## Test Conditions
DESIREE-FIRE Test Number Japanese 1 - Circuit Simulator Data Only
Test Date: | 2009-09-15
DCSim DAQ Start Time | 11:12
DCSim Time for Synchronization | 13:34
Heat Source Synchronization | 2:14 | minutes:seconds
Heat Source DAQ Start Time | 11:20
Heat Source Start Time | 13:39
DCSim Offset | 2:27 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 8850 | seconds
Heat Source Offset | 2:19 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 8323 | seconds
Heat Source Stop Time | 14:13
Test Duration | 0:34 | minutes:seconds
| 2040 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
SWGR Close | Mitsubishi, 6c, 14AWG |  | When looking into the opening of Penlight, Channel 3, Channel 4, and Channel 5 represent the left side, top, and right side of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | Mitsubishi, 6c, 14AWG |  | When looking into the opening of Penlight, Channel 3, Channel 4, and Channel 5 represent the left side, top, and right side of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1)
-0.26562 | 123.1293 | -60.7727 | 62.0178 | 0.081743 | 0.014181 | 0.014445 | -0.0018514 | 0.0027567 | -0.00095615 | -0.00042733 | -60.9421 | 62.0224 | -61.1435 | 0.041199 | 0.068665 | 0.086975 | -0.059509 | 0.27466 | 0.20142 | -0.23346 | -0.37079 | 0.004578 | -0.16937 | 60.8139 | -61.9492 | 60.5392 | -61.8164 | 0.20142
0.75 | 123.0377 | -60.8002 | 62.0316 | -0.18529 | 0.017812 | 0.015299 | 0.00413 | -2.0324e-05 | -0.00031535 | 0.0023499 | -60.9055 | 62.0773 | -61.116 | 0.036621 | 0.041199 | 0.050354 | 0.12817 | 0.2655 | 0.26093 | -0.1831 | -0.31586 | 0.045777 | -0.10529 | 60.8368 | -61.9904 | 60.6171 | -61.7706 | 0.21057
1.7344 | 123.111 | -60.7681 | 62.0361 | 0.10463 | 0.01653 | 0.014231 | -0.002065 | -0.00044752 | -0.00031535 | 0.00021367 | -60.9512 | 62.0087 | -61.1343 | 0.018311 | 0.045776 | 0.045776 | -0.059509 | 0.26093 | 0.19684 | -0.26093 | -0.36621 | -0.027466 | -0.18311 | 60.7864 | -61.9904 | 60.5072 | -61.8393 | 0.1831
2.7656 | 123.0103 | -60.8414 | 62.0453 | 0.1733 | 0.02123 | 0.016368 | 0.0094706 | 0.0016887 | -0.0013834 | -0.0023499 | -60.8917 | 62.1231 | -61.1023 | -0.036621 | -0.068665 | -0.082397 | 0 | 0.082397 | 0.21057 | -0.33875 | -0.26093 | 0.07782 | -0.050354 | 60.8047 | -62.114 | 60.5026 | -61.8347 | 0.21057
3.7344 | 123.1155 | -60.7864 | 62.0132 | 0.081743 | 0.016958 | 0.014872 | 7.12e-05 | 0.0014751 | -0.0018108 | 6.6667e-08 | -60.9375 | 61.9995 | -61.1572 | 0.009155 | 0.050354 | 0.022888 | -0.068665 | 0.21515 | 0.1831 | -0.28381 | -0.37079 | -0.013733 | -0.15106 | 60.7956 | -61.9629 | 60.5026 | -61.8301 | 0.21973
4.7656 | 123.056 | -60.8368 | 62.0407 | -0.15477 | 0.016744 | 0.019572 | 0.0081888 | 0.0033977 | -0.0026652 | -0.00021353 | -60.9009 | 62.1185 | -61.1435 | 0.1831 | 0.10986 | 0.004578 | 0.064087 | 0.29297 | 0.26093 | -0.18768 | -0.3067 | 0.07782 | -0.064087 | 61.0199 | -61.9308 | 60.6491 | -61.7798 | 0.24261
5.7344 | 123.0743 | -60.7773 | 62.0178 | 0.12752 | 0.018667 | 0.014659 | -0.002065 | 0.0023295 | -0.00031535 | -0.00064093 | -60.9467 | 62.0087 | -61.1435 | 0.036621 | 0.045776 | 0.036621 | -0.068665 | 0.24261 | 0.18768 | -0.2655 | -0.36621 | -0.009155 | -0.16937 | 60.8139 | -61.972 | 60.5118 | -61.8301 | 0.19684
6.7656 | 123.0652 | -60.8047 | 62.0407 | -0.0098092 | 0.021657 | 0.017008 | 0.0084026 | 0.0027567 | -0.00095615 | -0.0010681 | -60.8551 | 62.1414 | -61.1435 | 0.073242 | 0.032043 | 0.027466 | 0.013733 | 0.21973 | 0.2243 | -0.28381 | -0.33874 | 0.10071 | -0.050354 | 60.878 | -62.0087 | 60.5209 | -61.8164 | 0.28839
7.7344 | 123.1064 | -60.7956 | 61.972 | 0.10463 | 0.017812 | 0.020213 | -0.0012106 | 0.0021159 | -0.0037334 | -0.00085453 | -60.9375 | 62.0132 | -61.1343 | 0.018311 | 0.036621 | 0.041199 | -0.082397 | 0.2243 | 0.19226 | -0.27924 | -0.33875 | 0.041199 | -0.14191 | 60.8139 | -61.9354 | 60.5164 | -61.7798 | 0.19684
8.75 | 123.0148 | -60.8185 | 62.059 | -0.2158 | 0.017171 | 0.020426 | 0.0034892 | 0.00062048 | -0.0011698 | 0.00064087 | -60.9009 | 62.0453 | -61.1298 | 0.032043 | 0.045776 | 0.082397 | 0.10071 | 0.23804 | 0.24261 | -0.17853 | -0.31128 | -0.013733 | -0.082398 | 60.8505 | -62.0132 | 60.64 | -61.8164 | 0.22888
9.7344 | 123.1064 | -60.8047 | 61.9904 | 0.20381 | 0.016958 | 0.019786 | 0.0034892 | 0.0019023 | -0.00095615 | 0.0012817 | -60.8734 | 61.9858 | -61.1389 | 0.045776 | 0.054932 | 0.054932 | -0.17395 | 0.20599 | 0.16022 | -0.33875 | -0.33417 | -0.004577 | -0.068664 | 60.8505 | -61.9354 | 60.466 | -61.8301 | 0.2655
10.7656 | 123.0148 | -60.8139 | 61.9995 | 0.23433 | 0.021657 | 0.021708 | 0.0073344 | 0.0021159 | 0.0024618 | 0.00085447 | -60.9009 | 62.1323 | -61.1526 | -0.054932 | -0.068665 | -0.10071 | -0.013733 | 0.086975 | 0.20599 | -0.3479 | -0.33874 | 0.13275 | -0.086975 | 60.759 | -62.0682 | 60.466 | -61.7935 | 0.25177
11.7344 | 123.1155 | -60.7819 | 62.0041 | 0.15041 | 0.018239 | 0.016368 | 0.0004984 | 0.00062048 | -0.0015972 | -0.00042733 | -60.9421 | 62.0316 | -61.1252 | 0.013733 | 0.045776 | 0.027466 | -0.073242 | 0.20599 | 0.1831 | -0.28381 | -0.34332 | 0.027466 | -0.16022 | 60.7956 | -61.9583 | 60.498 | -61.821 | 0.1831
12.7656 | 123.056 | -60.8047 | 62.0361 | -0.11662 | 0.020376 | 0.022563 | 0.0081888 | 0.0014751 | -0.00010175 | 6.6667e-08 | -60.8505 | 62.1185 | -61.1206 | 0.07782 | 0.041199 | 0.036621 | 0.036621 | 0.2243 | 0.2243 | -0.26093 | -0.31586 | 0.082397 | -0.045776 | 60.8826 | -61.9949 | 60.5438 | -61.8118 | 0.27008
13.7344 | 123.0972 | -60.7727 | 61.9995 | 0.21144 | 0.018239 | 0.017863 | -0.0001424 | 0.0033977 | -0.0028788 | 0.00085447 | -60.9375 | 62.0087 | -61.1481 | 0 | 0.022888 | 0.018311 | -0.10529 | 0.19226 | 0.16937 | -0.28381 | -0.37537 | 0.009155 | -0.16479 | 60.7727 | -61.9766 | 60.4889 | -61.8301 | 0.21057
14.7656 | 123.024 | -60.8093 | 62.0636 | -0.12425 | 0.016744 | 0.017222 | 0.00413 | 0.0010477 | -0.0013834 | -0.00021353 | -60.9329 | 62.1048 | -61.1298 | 0.027466 | 0.036621 | 0.050354 | 0.14191 | 0.23804 | 0.2655 | -0.1831 | -0.32044 | 0.041198 | -0.1236 | 60.8368 | -62.027 | 60.6262 | -61.7981 | 0.19684
15.7344 | 123.1064 | -60.8047 | 62.0087 | 0.2267 | 0.016317 | 0.017222 | 0.0034892 | -0.00044752 | -0.0015972 | 0.0014953 | -60.8871 | 62.0224 | -61.1389 | -0.082397 | -0.07782 | 0 | -0.050354 | 0.17853 | 0.16937 | -0.32044 | -0.33417 | 0.013733 | -0.082397 | 60.7224 | -62.0865 | 60.4843 | -61.8393 | 0.25177
16.75 | 123.1613 | -60.759 | 62.0224 | -0.13951 | 0.016103 | 0.01594 | -0.0005696 | -0.00023392 | -0.003947 | -0.00042733 | -60.8505 | 61.9904 | -61.0931 | 0.1236 | 0.11902 | 0.16479 | -0.050354 | 0.35706 | 0.22888 | -0.21057 | -0.33417 | -0.032044 | -0.091553 | 60.8826 | -61.9034 | 60.5484 | -61.7935 | 0.24262
17.7344 | 123.143 | -60.7864 | 62.0041 | 0.31063 | 0.019307 | 0.016368 | 0.00648 | 0.0021159 | 0.00075285 | 6.6667e-08 | -60.8505 | 61.9904 | -61.1023 | 0.064087 | 0.032043 | 0.013733 | -0.20599 | 0.20142 | 0.15564 | -0.35706 | -0.31586 | -0.013733 | -0.064087 | 60.8505 | -61.972 | 60.4294 | -61.8484 | 0.25177
18.75 | 123.0377 | -60.8139 | 62.0682 | -0.19291 | 0.017385 | 0.017008 | 0.0034892 | 0.00062048 | -0.0024516 | 0.0010681 | -60.9375 | 62.0773 | -61.1343 | 0.032043 | 0.013733 | 0.041199 | 0.15106 | 0.23804 | 0.2655 | -0.16937 | -0.32043 | 0.009156 | -0.1236 | 60.8459 | -62.0544 | 60.6445 | -61.8027 | 0.19684
19.7344 | 123.1659 | -60.8002 | 62.0132 | 0.20381 | 0.01888 | 0.02064 | 0.0019938 | 0.0027567 | 0.00075285 | -0.0019225 | -60.8871 | 62.0224 | -61.116 | 0.050354 | 0.050354 | 0.036621 | -0.17395 | 0.21515 | 0.16022 | -0.32959 | -0.31586 | 0.009155 | -0.086975 | 60.8505 | -61.9629 | 60.4706 | -61.853 | 0.22888
20.75 | 123.1613 | -60.7681 | 61.9995 | -0.10899 | 0.015249 | 0.0080362 | -0.002065 | -0.0010885 | -0.002238 | 0.00021367 | -60.8643 | 61.9812 | -61.1023 | 0.1236 | 0.13275 | 0.17395 | -0.064087 | 0.38452 | 0.20142 | -0.19684 | -0.33417 | -0.018311 | -0.096131 | 60.8917 | -61.8668 | 60.5713 | -61.7981 | 0.23804
21.7344 | 123.1384 | -60.7727 | 62.0041 | 0.24959 | 0.017598 | 0.015513 | 0.003062 | 0.0036113 | -0.0018108 | -0.00042733 | -60.8551 | 62.0041 | -61.1206 | 0.059509 | 0.045776 | 0.041199 | -0.20142 | 0.21515 | 0.16022 | -0.35248 | -0.3479 | 0 | -0.082398 | 60.8322 | -61.9583 | 60.4202 | -61.8439 | 0.2655
22.7656 | 123.0148 | -60.8002 | 62.0316 | -0.14714 | 0.019735 | 0.015086 | 0.0049846 | 0.0019023 | -0.0020244 | 0.00085447 | -60.8963 | 62.1048 | -61.1298 | 0.036621 | 0.018311 | 0.032043 | 0.11444 | 0.23346 | 0.25635 | -0.21973 | -0.32959 | 0.073242 | -0.09613 | 60.8368 | -62.0132 | 60.5804 | -61.7752 | 0.23346
23.7344 | 123.111 | -60.791 | 62.0041 | 0.18855 | 0.019735 | 0.02064 | 0.0062662 | 0.0036113 | -0.0015972 | -0.0021361 | -60.9375 | 62.0728 | -61.1481 | 0.018311 | -0.004578 | 0.004578 | -0.12817 | 0.16022 | 0.16937 | -0.35706 | -0.35706 | 0.068665 | -0.14648 | 60.8093 | -62.0087 | 60.434 | -61.8347 | 0.21057
24.7656 | 123.0423 | -60.8322 | 62.0728 | -0.20054 | 0.018453 | 0.018077 | 0.0004984 | 0.0016887 | -0.00031535 | -0.00064093 | -60.9467 | 62.0682 | -61.1572 | 0.027466 | 0.032043 | 0.059509 | 0.15106 | 0.25177 | 0.27008 | -0.17395 | -0.32501 | -0.004578 | -0.11444 | 60.8597 | -62.0407 | 60.6583 | -61.8027 | 0.21057
25.7344 | 123.1247 | -60.8002 | 62.0041 | 0.23433 | 0.016958 | 0.018717 | 0.0039164 | 0.0036113 | -0.00031535 | 0.0014953 | -60.8414 | 62.0178 | -61.116 | 0.050354 | 0.036621 | 0.041199 | -0.17395 | 0.23346 | 0.15106 | -0.35706 | -0.31586 | 0.013733 | -0.041199 | 60.8505 | -61.9675 | 60.4431 | -61.853 | 0.27466
26.7656 | 123.0469 | -60.8459 | 62.0407 | -0.0021797 | 0.020376 | 0.01829 | 0.01118 | 0.0038249 | 0.00075285 | -0.0017089 | -60.8459 | 62.1414 | -61.1481 | 0.041199 | 0.018311 | 0.027466 | 0.009155 | 0.19684 | 0.21515 | -0.27924 | -0.30212 | 0.10071 | 0 | 60.8871 | -62.0224 | 60.5667 | -61.8256 | 0.30212
27.7344 | 123.1293 | -60.7956 | 61.9766 | 0.27248 | 0.019735 | 0.014231 | -0.0005696 | 0.0048931 | 0.00118 | -0.0017089 | -60.8551 | 62.0132 | -61.1343 | 0.041199 | 0.045776 | 0.045776 | -0.18768 | 0.21515 | 0.15106 | -0.3479 | -0.33875 | 0.036621 | -0.05951 | 60.8368 | -61.9308 | 60.4477 | -61.8256 | 0.27923
28.7656 | 123.1247 | -60.7819 | 62.0224 | -0.15477 | 0.01653 | 0.016795 | -0.0001424 | 0.0016887 | -0.00010175 | 6.6667e-08 | -60.8597 | 62.0499 | -61.1114 | 0.10529 | 0.11444 | 0.14648 | 0.013733 | 0.36163 | 0.21973 | -0.19684 | -0.32959 | 0.027466 | -0.07782 | 60.8871 | -61.908 | 60.585 | -61.8027 | 0.25177
29.7344 | 123.1384 | -60.7773 | 61.9675 | 0.21907 | 0.019948 | 0.016581 | 0.0049846 | 0.0046793 | -0.00052895 | 0.00042727 | -60.8734 | 62.0316 | -61.1252 | 0.054932 | 0.059509 | 0.032043 | -0.1831 | 0.21973 | 0.14648 | -0.3479 | -0.3479 | 0.064087 | -0.09613 | 60.8322 | -61.908 | 60.4294 | -61.821 | 0.25177
30.7656 | 123.0469 | -60.8185 | 62.0682 | -0.15477 | 0.019307 | 0.018717 | 0.004771 | 0.0012615 | -0.00010175 | -0.00021353 | -60.9146 | 62.1094 | -61.1481 | 0.022888 | 0.004578 | 0.022888 | 0.11902 | 0.22888 | 0.27008 | -0.19226 | -0.32959 | 0.041199 | -0.096131 | 60.8414 | -62.0636 | 60.6262 | -61.7981 | 0.23346
31.7344 | 123.0881 | -60.8093 | 61.9949 | 0.27248 | 0.02123 | 0.02299 | 0.0045574 | 0.0033977 | -0.00095615 | -0.00064093 | -60.91 | 62.0636 | -61.1481 | -0.018311 | -0.018311 | -0.027466 | -0.11902 | 0.15106 | 0.16479 | -0.32501 | -0.33875 | 0.068665 | -0.10071 | 60.791 | -62.0132 | 60.4843 | -61.8301 | 0.23804
32.7656 | 123.0652 | -60.8276 | 62.0407 | -0.070844 | 0.021016 | 0.018504 | 0.0062662 | 0.0048931 | -0.0020244 | -0.00064093 | -60.8597 | 62.1231 | -61.1343 | 0.022888 | -0.29755 | -0.2243 | 0.4303 | 0.45776 | 0.21973 | -0.25635 | -0.3067 | 0.082398 | -0.032043 | 60.8505 | -62.3383 | 60.5713 | -61.821 | 0.27466
33.7344 | 123.1201 | -60.7819 | 61.9858 | 0.51662 | 0.01888 | 0.020213 | 0.0009258 | 0.0046793 | -0.002238 | 0.0017091 | -60.8231 | 62.0224 | -61.1252 | 0.036621 | 0.068665 | 0.064087 | -0.19226 | 0.21973 | 0.15106 | -0.30212 | -0.34332 | 0.036621 | -0.041199 | 60.8185 | -61.9171 | 60.4797 | -61.8347 | 0.30212
34.7656 | 123.111 | -60.791 | 62.027 | -0.20054 | 0.017171 | 0.014872 | -0.0016378 | 0.0014751 | -0.0028788 | -0.0012817 | -60.8688 | 62.0544 | -61.1252 | 0.10071 | 0.10071 | 0.14191 | 0.059509 | 0.32959 | 0.23804 | -0.19226 | -0.33417 | 0.027465 | -0.077819 | 60.8917 | -61.9263 | 60.5988 | -61.7889 | 0.25635
35.75 | 123.0469 | -60.8139 | 62.0773 | -0.19291 | 0.014608 | 0.019999 | 0.000712 | 0.00083408 | -0.0013834 | -0.00042733 | -60.8917 | 62.059 | -61.1252 | 0.032043 | 0.045776 | 0.068665 | 0.13733 | 0.32044 | 0.25635 | -0.1831 | -0.31128 | -0.018311 | -0.07782 | 60.8459 | -62.0316 | 60.6308 | -61.821 | 0.23346
36.7656 | 123.0377 | -60.8047 | 62.0682 | -0.070844 | 0.020162 | 0.022135 | 0.0096842 | 0.0029705 | -0.0013834 | -0.00085453 | -60.8322 | 62.114 | -61.1206 | 0.054932 | 0.027466 | 0.045776 | 0.027466 | 0.24261 | 0.24719 | -0.2655 | -0.31586 | 0.045777 | -0.027465 | 60.8597 | -62.0407 | 60.5392 | -61.821 | 0.28839
37.7344 | 123.1567 | -60.7956 | 61.9812 | 0.24959 | 0.018667 | 0.019999 | 0.0019938 | 0.0038249 | -0.00095615 | -0.00042733 | -60.8734 | 62.0132 | -61.1343 | 0.041199 | 0.050354 | 0.022888 | -0.19226 | 0.20142 | 0.16022 | -0.36621 | -0.33875 | 0.032044 | -0.07782 | 60.8368 | -61.9308 | 60.4294 | -61.821 | 0.26093
38.7656 | 123.0789 | -60.8002 | 62.0361 | -0.055586 | 0.021657 | 0.017436 | 0.0049846 | 0.0053203 | 0.00032545 | 0.00085447 | -60.8551 | 62.1323 | -61.1252 | 0.059509 | 0.032043 | 0.036621 | 0.036621 | 0.22888 | 0.23346 | -0.2655 | -0.32501 | 0.09613 | -0.054932 | 60.8597 | -62.0041 | 60.5347 | -61.8027 | 0.27008
39.7344 | 123.0972 | -60.7773 | 62.0087 | 0.44032 | 0.019094 | 0.016581 | -0.0018514 | 0.0042521 | 0.00011185 | -0.00085453 | -60.8826 | 62.0041 | -61.1435 | 0.022888 | 0.050354 | 0.045776 | -0.14191 | 0.19684 | 0.16937 | -0.3067 | -0.36621 | -0.004578 | -0.10529 | 60.8002 | -61.9583 | 60.4706 | -61.8393 | 0.26093
40.7656 | 123.0881 | -60.7864 | 61.9858 | 0.097002 | 0.014394 | 0.015299 | -0.0029196 | 0.0016887 | 0.002248 | 0.0014953 | -60.9329 | 61.9949 | -61.1389 | 0.022888 | 0.059509 | 0.054932 | -0.059509 | 0.25177 | 0.20142 | -0.28381 | -0.35248 | 0.009155 | -0.14648 | 60.8093 | -61.9263 | 60.5026 | -61.7844 | 0.20599
41.7344 | 123.111 | -60.7864 | 61.9995 | 0.21144 | 0.017812 | 0.015727 | -0.0014242 | -0.00023392 | -0.0020244 | 0.0010681 | -60.8871 | 62.0087 | -61.1526 | 0.036621 | 0.091553 | 0.064087 | -0.16937 | 0.23346 | 0.17853 | -0.29755 | -0.36621 | 0.009155 | -0.10071 | 60.8231 | -61.908 | 60.4889 | -61.821 | 0.2655
42.7656 | 123.0606 | -60.8047 | 62.0544 | -0.10136 | 0.020803 | 0.022563 | 0.0077616 | 0.0019023 | 0.00053925 | 0.00064087 | -60.8368 | 62.1277 | -61.1023 | 0.059509 | 0.036621 | 0.045776 | 0.027466 | 0.23804 | 0.20142 | -0.27008 | -0.29755 | 0.073243 | -0.032043 | 60.8643 | -62.0178 | 60.5347 | -61.853 | 0.2655
43.7344 | 123.0972 | -60.7773 | 62.0224 | 0.27248 | 0.020589 | 0.017008 | 0.0009258 | 0.0025431 | -0.0015972 | 0.00021367 | -60.8734 | 62.0087 | -61.1526 | 0.027466 | -0.082397 | -0.15564 | 0.036621 | 0.46234 | 0.17395 | -0.3479 | -0.37537 | -0.013733 | -0.09613 | 60.8047 | -62.1048 | 60.4294 | -61.8484 | 0.27924
44.7656 | 123.0331 | -60.8139 | 62.0544 | -0.086103 | 0.014394 | 0.018504 | 0.0019938 | 0.0019023 | 0.00053925 | 0.00021367 | -60.91 | 62.0636 | -61.1435 | 0.022888 | 0.036621 | 0.050354 | 0.16937 | 0.35248 | 0.27008 | -0.16937 | -0.32959 | 0.009156 | -0.09613 | 60.8368 | -62.0178 | 60.6445 | -61.7844 | 0.23346
45.7344 | 123.1338 | -60.7681 | 62.0316 | -0.17003 | 0.016744 | 0.015727 | 0.0009258 | 0.0025431 | -0.0018108 | 6.6667e-08 | -60.8688 | 62.0178 | -61.1206 | 0.1236 | 0.10529 | 0.14648 | -0.022888 | 0.35248 | 0.20142 | -0.20599 | -0.35248 | -0.013733 | -0.10071 | 60.8917 | -61.9263 | 60.5621 | -61.8301 | 0.25177
46.75 | 123.0103 | -60.7864 | 62.0728 | -0.12425 | 0.019948 | 0.019786 | 0.0062662 | 0.00019328 | -0.002238 | 0.0014953 | -60.9375 | 62.0911 | -61.1435 | 0.027466 | 0.009155 | 0.036621 | 0.12817 | 0.25177 | 0.2655 | -0.17395 | -0.35706 | 0.01831 | -0.15106 | 60.8139 | -62.0636 | 60.6125 | -61.8073 | 0.20599
47.7344 | 123.1155 | -60.8231 | 62.0178 | 0.39455 | 0.017598 | 0.019786 | -0.002065 | 0.0033977 | 0.00011185 | 0.0017091 | -60.9009 | 61.9995 | -61.1389 | 0 | 0.027466 | 0.027466 | -0.1236 | 0.19226 | 0.17853 | -0.27924 | -0.31586 | -0.01831 | -0.07782 | 60.8231 | -61.9904 | 60.5438 | -61.8393 | 0.23804
48.7656 | 123.1155 | -60.7864 | 62.0087 | 0.058855 | 0.017385 | 0.015727 | -0.0007832 | 0.00040688 | 0.00118 | -0.0019225 | -60.9329 | 61.9812 | -61.1206 | 0.036621 | 0.041199 | 0.050354 | -0.064087 | 0.25635 | 0.20599 | -0.25635 | -0.33417 | -0.027466 | -0.14648 | 60.8231 | -61.9675 | 60.5301 | -61.8027 | 0.18768
49.7344 | 123.1201 | -60.8093 | 62.0224 | 0.19618 | 0.017385 | 0.017008 | 0.003062 | 0.00062048 | -0.0018108 | 6.6667e-08 | -60.8917 | 61.9995 | -61.116 | 0.16479 | 0.073242 | -0.059509 | -0.16022 | 0.25635 | 0.16937 | -0.31586 | -0.3067 | -0.022888 | -0.082398 | 60.9741 | -61.9492 | 60.4935 | -61.853 | 0.2243
50.7656 | 123.0515 | -60.8231 | 62.0682 | -0.15477 | 0.019735 | 0.013377 | 0.0034892 | -0.0010885 | -0.00052895 | -0.0021361 | -60.9375 | 62.1094 | -61.1389 | 0.027466 | -0.009155 | 0.022888 | 0.13733 | 0.23346 | 0.2655 | -0.18768 | -0.31586 | 0.041199 | -0.11444 | 60.8505 | -62.0773 | 60.6354 | -61.8027 | 0.20142
51.7344 | 123.1659 | -60.8047 | 61.9858 | 0.27248 | 0.018026 | 0.019572 | 0.0049846 | 0.0038249 | -0.00074255 | 0.00064087 | -60.8414 | 62.027 | -61.1435 | 0.064087 | 0.045776 | 0.032043 | -0.20599 | 0.21515 | 0.14648 | -0.36163 | -0.33874 | 0.041199 | -0.036621 | 60.8688 | -61.94 | 60.4431 | -61.8393 | 0.30212
52.7656 | 123.0515 | -60.7864 | 62.0224 | -0.23869 | 0.019735 | 0.017436 | 0.0071208 | 0.0036113 | 0.00053925 | -0.0010681 | -60.8734 | 62.1231 | -61.1389 | 0.064087 | 0.041199 | 0.050354 | 0.068665 | 0.24719 | 0.24719 | -0.24261 | -0.35248 | 0.10071 | -0.086975 | 60.8505 | -61.9812 | 60.5438 | -61.7752 | 0.2655
53.7344 | 123.1201 | -60.7864 | 61.9995 | 0.26485 | 0.017171 | 0.018077 | -0.0007832 | 0.0021159 | -0.00074255 | 0.00021367 | -60.8826 | 62.0132 | -61.1435 | 0.07782 | -0.032043 | -0.013733 | -0.064087 | 0.23346 | 0.16479 | -0.32501 | -0.35706 | 0.013733 | -0.09613 | 60.8643 | -62.0316 | 60.4614 | -61.8347 | 0.26093
54.7656 | 123.0743 | -60.8002 | 62.0316 | -0.086103 | 0.018667 | 0.02064 | 0.0060526 | 0.0027567 | 0.0020344 | 0.00021367 | -60.8734 | 62.1414 | -61.1526 | 0.064087 | 0.068665 | 0.09613 | 0.045776 | 0.22888 | 0.25635 | -0.2243 | -0.35248 | 0.10986 | -0.073242 | 60.8643 | -61.9629 | 60.5759 | -61.7752 | 0.27924
55.7344 | 123.1155 | -60.759 | 61.9766 | 0.24196 | 0.017812 | 0.01594 | 0.0037028 | 0.0044657 | 0.00011185 | 0.0019227 | -60.878 | 61.9812 | -61.1206 | 0.045776 | 0.050354 | 0.013733 | -0.19684 | 0.21973 | 0.15564 | -0.34332 | -0.36163 | 0.004577 | -0.11902 | 60.8047 | -61.9263 | 60.4156 | -61.821 | 0.24261
56.7656 | 123.0606 | -60.8047 | 62.0682 | -0.13188 | 0.018667 | 0.02064 | 0.0062662 | 0.0027567 | -0.00052895 | 0.00021367 | -60.8917 | 62.1323 | -61.1572 | 0 | 0.086975 | 0.07782 | 0.009155 | 0.21057 | 0.2655 | -0.21057 | -0.35248 | 0.064087 | -0.086975 | 60.8047 | -61.9812 | 60.5942 | -61.8027 | 0.2655
57.7344 | 123.1384 | -60.8047 | 62.0132 | 0.28774 | 0.02123 | 0.015727 | 0.001353 | 0.0040385 | 0.00053925 | -0.00064093 | -60.8505 | 62.027 | -61.1252 | 0.041199 | 0.050354 | 0.036621 | -0.20599 | 0.21515 | 0.16022 | -0.33875 | -0.32043 | 0.013733 | -0.045776 | 60.8459 | -61.9629 | 60.466 | -61.853 | 0.27466
58.7656 | 123.0698 | -60.791 | 62.0361 | 0.86757 | 0.018026 | 0.014659 | -0.0024922 | 0.0010477 | -0.0018108 | -0.00042733 | -60.9695 | 62.0407 | -61.1435 | 0.054932 | 0.068665 | 0.10986 | 0.059509 | 0.3067 | 0.23804 | -0.24719 | -0.35248 | 0.004577 | -0.17853 | 60.8459 | -61.9675 | 60.5438 | -61.7981 | 0.17395
59.7344 | 123.0469 | -60.8276 | 62.0224 | 0.21144 | 0.019948 | 0.02064 | 0.0098978 | 0.0044657 | -0.0030924 | -0.00042733 | -60.9192 | 62.0911 | -61.1618 | 0.21973 | -0.018311 | -0.1831 | 0.018311 | 0.25635 | 0.18768 | -0.32044 | -0.33417 | 0.068664 | -0.091552 | 61.0474 | -62.0407 | 60.5072 | -61.8347 | 0.24261
60.7656 | 123.056 | -60.759 | 61.9995 | -0.14714 | 0.016744 | 0.02064 | 0.0004984 | 0.0023295 | -0.00031535 | -0.0012817 | -60.8643 | 62.0316 | -61.1206 | 0.10071 | 0.1236 | 0.15564 | 0.009155 | 0.55847 | 0.23804 | -0.1831 | -0.36163 | 0.032043 | -0.10529 | 60.8597 | -61.8759 | 60.5759 | -61.7615 | 0.25635
61.7344 | 123.0972 | -60.7773 | 61.94 | 0.25722 | 0.017598 | 0.016368 | 0.0019938 | 0.0044657 | -0.00031535 | 0.00042727 | -60.8597 | 62.0041 | -61.1069 | 0.036621 | 0.032043 | 0.041199 | -0.1831 | 0.21057 | 0.14648 | -0.35248 | -0.32959 | 0.064087 | -0.082397 | 60.8139 | -61.908 | 60.4248 | -61.7935 | 0.24719
62.7656 | 123.1338 | -60.7819 | 62.0224 | -0.14714 | 0.017171 | 0.01829 | -0.0001424 | 0.00019328 | -0.002238 | 0.00042727 | -60.8597 | 62.0316 | -61.1206 | 0.12817 | 0.12817 | 0.16022 | -0.022888 | 0.36621 | 0.21973 | -0.20142 | -0.33874 | 0.009155 | -0.07782 | 60.91 | -61.8942 | 60.5804 | -61.8027 | 0.26093
63.7344 | 123.1155 | -60.8002 | 61.9949 | 0.24959 | 0.020803 | 0.014872 | 0.0073344 | 0.0038249 | -0.00074255 | 0.0014953 | -60.8917 | 62.0911 | -61.116 | 0.013733 | 0.013733 | -0.041199 | -0.13275 | 0.1831 | 0.16022 | -0.37537 | -0.31586 | 0.09613 | -0.091553 | 60.8139 | -61.9812 | 60.4248 | -61.8347 | 0.2243
64.75 | 123.143 | -60.7956 | 62.0132 | 0.13515 | 0.019521 | 0.019358 | -0.0016378 | -0.00044752 | 0.00032545 | 0.00064087 | -60.9238 | 62.0041 | -61.1572 | 0.059509 | 0.07782 | 0.086975 | -0.07782 | 0.29297 | 0.20599 | -0.25635 | -0.36163 | -0.009156 | -0.12817 | 60.8551 | -61.9354 | 60.5392 | -61.8073 | 0.23346
65.7344 | 123.024 | -60.8231 | 62.027 | 0.18855 | 0.019735 | 0.021708 | 0.0081888 | 0.0025431 | -0.00095615 | 0.00042727 | -60.9283 | 62.1094 | -61.1435 | -0.032043 | -0.068665 | -0.10986 | -0.018311 | 0.09613 | 0.20599 | -0.33875 | -0.32043 | 0.082397 | -0.10529 | 60.791 | -62.0956 | 60.4843 | -61.821 | 0.21515
66.7656 | 123.0698 | -60.7819 | 62.0453 | -0.19291 | 0.018453 | 0.017222 | 0.0009258 | 0.0014751 | -0.0020244 | 0.00042727 | -60.8871 | 62.0316 | -61.1114 | 0.073242 | 0.07782 | 0.082397 | 0.091553 | 0.30212 | 0.27008 | -0.19684 | -0.32959 | -0.013733 | -0.10529 | 60.8551 | -61.9675 | 60.585 | -61.7752 | 0.2243
67.7344 | 123.0698 | -60.8276 | 62.0361 | 0.15041 | 0.019307 | 0.018931 | 0.0071208 | 0.0029705 | -0.00052895 | 0.0019227 | -60.9055 | 62.0819 | -61.1526 | -0.018311 | -0.032043 | -0.059509 | -0.10071 | 0.12817 | 0.17395 | -0.3479 | -0.32501 | 0.045776 | -0.07782 | 60.8093 | -62.0682 | 60.4797 | -61.8622 | 0.24719
68.7656 | 123.1476 | -60.7727 | 62.0178 | -0.093733 | 0.015462 | 0.018077 | -0.0014242 | 0.0021159 | -0.0011698 | -0.00021353 | -60.8551 | 62.0132 | -61.1526 | 0.1236 | 0.13733 | 0.16479 | -0.036621 | 0.37079 | 0.22888 | -0.18768 | -0.37994 | -0.004577 | -0.082398 | 60.8963 | -61.8805 | 60.585 | -61.7889 | 0.29755
69.7344 | 123.0469 | -60.8185 | 62.0407 | 0.2267 | 0.021657 | 0.018504 | 0.0094706 | 0.0044657 | -0.00052895 | -0.0010681 | -60.9329 | 62.1323 | -61.1435 | -0.33875 | -0.49439 | -0.21057 | 0.64087 | 0.43488 | 0.17395 | -0.3479 | -0.32501 | 0.091553 | -0.11444 | 60.4797 | -62.5351 | 60.4706 | -61.8668 | 0.21057
70.75 | 123.1064 | -60.7819 | 62.0132 | 0.097002 | 0.017598 | 0.012309 | -0.0005696 | 0.0019023 | 0.00096645 | 0.00042727 | -60.9238 | 62.0178 | -61.1389 | -0.032043 | 0.036621 | 0.032043 | -0.07782 | 0.20599 | 0.17853 | -0.27924 | -0.35706 | 0.004577 | -0.14191 | 60.7498 | -61.9766 | 60.5026 | -61.8347 | 0.21515
71.7344 | 123.024 | -60.8414 | 62.0224 | 0.1733 | 0.022085 | 0.018077 | 0.010325 | 0.0023295 | 0.00075285 | 0.00064087 | -60.9146 | 62.1277 | -61.1389 | -0.050354 | -0.082397 | -0.086975 | 0.013733 | 0.068665 | 0.20142 | -0.37079 | -0.29755 | 0.10529 | -0.073242 | 60.791 | -62.1048 | 60.4706 | -61.821 | 0.2243
72.7656 | 123.1201 | -60.7681 | 62.0544 | -0.24632 | 0.016317 | 0.021708 | -0.0005696 | 0.0010477 | -0.0018108 | 6.6667e-08 | -60.8826 | 62.027 | -61.1389 | 0.10529 | 0.13733 | 0.13733 | 0.022888 | 0.3479 | 0.22888 | -0.18768 | -0.37079 | -0.027465 | -0.11444 | 60.8734 | -61.9171 | 60.5804 | -61.8256 | 0.25635
73.7344 | 123.0377 | -60.8185 | 62.0361 | 0.058855 | 0.023366 | 0.018931 | 0.0088298 | 0.0016887 | -0.0028788 | -0.00021353 | -60.8597 | 62.146 | -61.1298 | 0.004578 | -0.027466 | -0.036621 | 0.022888 | 0.14648 | 0.20599 | -0.3067 | -0.31128 | 0.10986 | -0.041199 | 60.8231 | -62.0636 | 60.5118 | -61.8301 | 0.27008
74.7656 | 123.111 | -60.7773 | 62.027 | -0.13188 | 0.017812 | 0.016368 | -0.0001424 | 0.0019023 | -0.0013834 | 6.6667e-08 | -60.8826 | 62.027 | -61.1343 | 0.10529 | 0.11902 | 0.15106 | 0.036621 | 0.3479 | 0.24261 | -0.18768 | -0.35706 | 0 | -0.10529 | 60.8826 | -61.908 | 60.5896 | -61.7844 | 0.25177
75.7344 | 123.0331 | -60.8185 | 62.027 | 0.10463 | 0.020376 | 0.021067 | 0.0077616 | 0.0027567 | 0.0016072 | 0.0014953 | -60.8597 | 62.114 | -61.1343 | -0.004578 | -0.027466 | -0.022888 | 0.027466 | 0.15564 | 0.21515 | -0.28839 | -0.31586 | 0.086975 | -0.041199 | 60.8139 | -62.0544 | 60.5301 | -61.8118 | 0.27466
76.7656 | 123.1522 | -60.759 | 62.0453 | -0.047956 | 0.01653 | 0.01594 | -0.0024922 | 0.00062048 | -0.0018108 | 0.0012817 | -60.9009 | 61.9949 | -61.1435 | 0.091553 | 0.10986 | 0.15106 | -0.091553 | 0.32044 | 0.21515 | -0.2243 | -0.38452 | -0.050354 | -0.14191 | 60.8505 | -61.9354 | 60.5347 | -61.8301 | 0.24261
77.7344 | 123.0194 | -60.8368 | 62.0453 | 0.10463 | 0.019521 | 0.018077 | 0.0069072 | 0.0029705 | -0.0011698 | 0.0014953 | -60.8826 | 62.1231 | -61.1343 | -0.004578 | -0.041199 | -0.041199 | 0.018311 | 0.16022 | 0.21973 | -0.3067 | -0.29755 | 0.07782 | -0.045776 | 60.8322 | -62.0865 | 60.5301 | -61.8256 | 0.25177
78.75 | 123.1293 | -60.7727 | 61.9858 | 0.19618 | 0.019094 | 0.021281 | 0.0039164 | 0.0038249 | 0.0016072 | 0.00064087 | -60.8414 | 62.0453 | -61.1252 | 0.041199 | 0.036621 | 0.027466 | -0.19226 | 0.20599 | 0.14191 | -0.36163 | -0.35248 | 0.059509 | -0.068665 | 60.8139 | -61.9492 | 60.4111 | -61.8439 | 0.28381
79.7344 | 123.0103 | -60.8322 | 62.0499 | -0.20817 | 0.020162 | 0.018931 | -0.0009968 | 0.0021159 | 0.0033162 | 0.0010681 | -60.9421 | 62.114 | -61.1298 | -0.13275 | 0.11444 | 0.20599 | 0.036621 | 0.13733 | 0.27466 | -0.19226 | -0.29755 | 0.064087 | -0.10986 | 60.6995 | -61.9354 | 60.64 | -61.7752 | 0.18768
80.7656 | 123.1476 | -60.7864 | 61.9995 | 0.097002 | 0.019094 | 0.018504 | 0.0004984 | 0.0027567 | -0.00052895 | 0.0012817 | -60.8871 | 62.0224 | -61.1389 | 0.050354 | 0.041199 | 0.027466 | -0.19226 | 0.21973 | 0.16937 | -0.32959 | -0.35248 | 0.022888 | -0.10071 | 60.8368 | -61.9583 | 60.4568 | -61.8301 | 0.25177
81.7344 | 123.0789 | -60.7956 | 62.0407 | -0.078474 | 0.020589 | 0.023204 | 0.004771 | 0.0025431 | 0.0013936 | 0.00021367 | -60.8643 | 62.146 | -61.116 | 0.064087 | 0.045776 | 0.045776 | 0.022888 | 0.23346 | 0.2243 | -0.25177 | -0.32044 | 0.10529 | -0.068665 | 60.8597 | -61.9949 | 60.5438 | -61.8164 | 0.25177
82.75 | 123.0469 | -60.8185 | 62.0178 | -0.49046 | 0.021871 | 0.014659 | 0.0051982 | 0.0042521 | 0.00032545 | 0.0012817 | -60.9238 | 62.114 | -61.1572 | -0.027466 | -0.068665 | -0.13275 | -0.068665 | 0.09613 | 0.2243 | -0.32044 | -0.33875 | 0.096131 | -0.10529 | 60.791 | -62.0865 | 60.498 | -61.7935 | 0.23346
83.7344 | 123.024 | -60.8276 | 62.0682 | -1.2381 | 0.019735 | 0.021067 | 0.001353 | 0.0042521 | -0.00010175 | 0.0010681 | -61.0382 | 62.114 | -61.1435 | 0.027466 | 0.013733 | -0.022888 | 0.17395 | 0.26093 | 0.25177 | -0.24719 | -0.31586 | 0.045777 | -0.21057 | 60.8551 | -62.0544 | 60.5804 | -61.8164 | 0.10529
84.7656 | 123.1064 | -60.8047 | 62.027 | 0.2267 | 0.016317 | 0.018931 | -0.0016378 | 0.0014751 | -0.0015972 | -0.0010681 | -60.9283 | 62.0087 | -61.1435 | 0.009155 | 0.022888 | 0.018311 | -0.1236 | 0.22888 | 0.16937 | -0.29755 | -0.33874 | -0.018311 | -0.1236 | 60.8139 | -62.0041 | 60.5072 | -61.8576 | 0.21515
85.7344 | 123.056 | -60.8093 | 62.0682 | -0.17766 | 0.018026 | 0.01594 | 0.0060526 | 0.0019023 | 0.00032545 | -0.00042733 | -60.91 | 62.1185 | -61.1298 | 0.027466 | 0.022888 | 0.045776 | 0.10071 | 0.24719 | 0.25635 | -0.19684 | -0.32044 | 0.050354 | -0.10071 | 60.8368 | -62.0453 | 60.6125 | -61.8118 | 0.21973
86.7656 | 123.1384 | -60.7956 | 61.9949 | 0.27248 | 0.018239 | 0.019999 | 7.12e-05 | 0.0040385 | 0.00053925 | 0.0034181 | -60.8826 | 62.027 | -61.1206 | 0.032043 | 0.050354 | 0.045776 | -0.17395 | 0.23346 | 0.14648 | -0.34332 | -0.32501 | 0.032044 | -0.086975 | 60.8276 | -61.9446 | 60.4523 | -61.8484 | 0.23804
87.7344 | 123.0377 | -60.8047 | 62.0636 | -0.27684 | 0.019094 | 0.018717 | 0.002421 | 0.00040688 | 0.00096645 | 0.00085447 | -60.9421 | 62.1277 | -61.1206 | 0.027466 | 0.009155 | 0.032043 | 0.13275 | 0.25635 | 0.27466 | -0.21973 | -0.31586 | 0.064087 | -0.13733 | 60.8322 | -62.0544 | 60.585 | -61.7889 | 0.17853
88.7656 | 123.0972 | -60.7819 | 62.0316 | 0.13515 | 0.015462 | 0.010813 | -0.0029196 | -2.0324e-05 | 0.00118 | 0.0021363 | -60.9146 | 62.0087 | -61.1206 | 0.009155 | 0.041199 | 0.064087 | -0.036621 | 0.24261 | 0.18768 | -0.27466 | -0.33874 | -0.022888 | -0.13275 | 60.791 | -61.9904 | 60.5072 | -61.8439 | 0.20599
89.7344 | 123.056 | -60.8139 | 62.1048 | -0.18529 | 0.018026 | 0.019786 | 0.0037028 | 0.00040688 | -0.0013834 | -0.0012817 | -60.9375 | 62.1048 | -61.116 | 0.018311 | 0.009155 | 0.032043 | 0.15564 | 0.23804 | 0.28381 | -0.1831 | -0.30212 | 0 | -0.1236 | 60.8322 | -62.0956 | 60.6308 | -61.821 | 0.17853
90.75 | 123.0377 | -60.8047 | 62.0361 | 0.020708 | 0.020162 | 0.023631 | 0.009257 | 0.0027567 | -0.00010175 | -0.0010681 | -60.8459 | 62.146 | -61.1298 | 0.022888 | -0.018311 | -0.018311 | -0.004578 | 0.16937 | 0.2243 | -0.29755 | -0.32501 | 0.10986 | -0.041198 | 60.8276 | -62.0544 | 60.5072 | -61.8118 | 0.28381
91.7344 | 123.0377 | -60.7864 | 62.0682 | -0.18529 | 0.01888 | 0.017436 | 0.0002848 | 0.0014751 | -0.0015972 | -0.0021361 | -60.9009 | 62.0819 | -61.1526 | 0.068665 | 0.050354 | 0.036621 | 0.12817 | 0.31586 | 0.25177 | -0.19684 | -0.36621 | 0.013733 | -0.11444 | 60.8551 | -62.0178 | 60.5896 | -61.8164 | 0.25177
92.75 | 123.024 | -60.8185 | 62.0407 | 0.10463 | 0.019521 | 0.019145 | 0.0086162 | 0.0036113 | 0.00075285 | -0.0012817 | -60.8826 | 62.1414 | -61.1389 | -0.004578 | -0.018311 | -0.045776 | 0.018311 | 0.14191 | 0.21515 | -0.3067 | -0.32044 | 0.10071 | -0.064087 | 60.8139 | -62.059 | 60.5118 | -61.8256 | 0.25635
93.7344 | 123.0927 | -60.7727 | 62.0407 | -0.20054 | 0.017385 | 0.01594 | -0.0022786 | 0.0016887 | -0.0015972 | -0.0010681 | -60.8643 | 62.0544 | -61.1114 | 0.082397 | 0.10071 | 0.12817 | 0.054932 | 0.33417 | 0.25177 | -0.20599 | -0.33874 | 0.013733 | -0.091553 | 60.8551 | -61.94 | 60.5667 | -61.7889 | 0.24719
94.75 | 123.0423 | -60.8185 | 62.0407 | 0.028338 | 0.021016 | 0.018717 | 0.0088298 | 0.0033977 | 0.00011185 | 0.00021367 | -60.8505 | 62.1323 | -61.1343 | 0.022888 | 0.013733 | -0.004578 | 0.013733 | 0.20599 | 0.21515 | -0.29755 | -0.31586 | 0.091553 | -0.032044 | 60.8414 | -62.027 | 60.5209 | -61.8256 | 0.28381
95.7344 | 123.1064 | -60.7773 | 62.0361 | 0.051226 | 0.01653 | 0.011454 | -0.0018514 | 0.0019023 | -0.00052895 | 0.0012817 | -60.8688 | 62.0087 | -61.1481 | 0.091553 | 0.11444 | 0.14648 | -0.041199 | 0.33875 | 0.22888 | -0.20599 | -0.37079 | -0.027466 | -0.091552 | 60.8688 | -61.9217 | 60.5713 | -61.8073 | 0.27924
96.7656 | 123.1384 | -60.791 | 61.9995 | 0.34877 | 0.018026 | 0.019145 | 0.0015666 | 0.0031841 | 0.00053925 | 0.0012817 | -60.8597 | 62.0132 | -61.1252 | 0.022888 | 0.059509 | 0.064087 | -0.20142 | 0.20142 | 0.14648 | -0.32959 | -0.33417 | 0.013733 | -0.068664 | 60.8139 | -61.94 | 60.4614 | -61.853 | 0.2655
97.7344 | 123.0881 | -60.759 | 62.0316 | -0.18529 | 0.016317 | 0.014659 | -0.0007832 | -0.00044752 | 0.00075285 | 0.00042727 | -60.8688 | 62.0499 | -61.1298 | 0.10071 | 0.09613 | 0.13733 | 0.045776 | 0.33875 | 0.25635 | -0.19684 | -0.37079 | 0.018311 | -0.10986 | 60.8597 | -61.9354 | 60.5621 | -61.7752 | 0.26093
98.7656 | 123.0057 | -60.8551 | 62.0453 | 0.24196 | 0.021657 | 0.016368 | 0.0096842 | 0.0033977 | 0.0033162 | 0.0017091 | -60.9375 | 62.114 | -61.1481 | -0.045776 | -0.064087 | -0.10071 | -0.022888 | 0.09613 | 0.19226 | -0.36621 | -0.29297 | 0.068665 | -0.082397 | 60.8093 | -62.1094 | 60.4889 | -61.853 | 0.21057
99.7344 | 123.1522 | -60.7636 | 62.0316 | -0.15477 | 0.017385 | 0.015727 | -0.0018514 | 0.00040688 | -0.00010175 | -0.0010681 | -60.8505 | 61.9995 | -61.1252 | 0.11902 | 0.1236 | 0.16022 | -0.054932 | 0.35706 | 0.21057 | -0.19684 | -0.36163 | -0.032043 | -0.086975 | 60.8826 | -61.908 | 60.5667 | -61.821 | 0.27466
100.7656 | 123.0652 | -60.8231 | 61.9995 | 0.27248 | 0.02123 | 0.016368 | 0.0056254 | 0.0036113 | -0.0015972 | -0.00042733 | -60.8963 | 62.0911 | -61.1298 | 0.009155 | -0.013733 | -0.036621 | -0.15106 | 0.15106 | 0.16937 | -0.34332 | -0.3067 | 0.091552 | -0.073242 | 60.8322 | -62.0132 | 60.4797 | -61.8301 | 0.23346
101.75 | 123.0331 | -60.8185 | 62.0361 | 0.21144 | 0.022298 | 0.016368 | 0.0088298 | 0.0025431 | 0.003957 | -0.00042733 | -60.9329 | 62.1048 | -61.1481 | -0.045776 | -0.073242 | -0.15564 | -0.81482 | -0.10986 | 0.13733 | -0.40283 | -0.32959 | 0.068664 | -0.11444 | 60.7727 | -62.1094 | 60.4156 | -61.8988 | 0.21515
102.7656 | 122.9965 | -60.8368 | 62.0316 | 0.14278 | 0.022939 | 0.018931 | 0.0081888 | 0.0048931 | 0.0013936 | 0.00064087 | -60.9146 | 62.1277 | -61.1664 | -0.064087 | -0.059509 | -0.073242 | 0.004578 | 0.10986 | 0.20599 | -0.33417 | -0.32959 | 0.096131 | -0.07782 | 60.7727 | -62.0911 | 60.5026 | -61.8256 | 0.25177
103.7344 | 123.056 | -60.8139 | 62.059 | -0.23106 | 0.018667 | 0.018504 | -0.0007832 | 0.0036113 | -0.002238 | -0.00021353 | -60.9283 | 62.1002 | -61.1389 | 0.027466 | 0.013733 | 0.027466 | 0.13275 | 0.27924 | 0.27008 | -0.17853 | -0.32501 | 0.041199 | -0.11444 | 60.8414 | -62.0453 | 60.6354 | -61.7889 | 0.21057
104.7656 | 123.0652 | -60.8597 | 62.0132 | 0.24959 | 0.018667 | 0.016154 | 0.004771 | 0.0025431 | -0.0018108 | -0.00021353 | -60.9238 | 62.1048 | -61.1572 | -0.054932 | -0.050354 | -0.068665 | -0.054932 | 0.086975 | 0.1831 | -0.33417 | -0.29755 | 0.091552 | -0.064087 | 60.8047 | -62.0636 | 60.5255 | -61.8301 | 0.23346
105.7344 | 123.1247 | -60.7819 | 62.0407 | -0.31499 | 0.015462 | 0.017649 | -0.0033468 | 0.00019328 | -0.00031535 | -0.0010681 | -60.878 | 62.0407 | -61.116 | 0.1236 | 0.12817 | 0.12817 | -0.041199 | 0.33875 | 0.21973 | -0.21057 | -0.33417 | 0 | -0.096131 | 60.9055 | -61.9125 | 60.5713 | -61.821 | 0.23804
106.7812 | 123.0011 | -60.8185 | 62.027 | 0.2267 | 0.021444 | 0.016154 | 0.0069072 | 0.0023295 | 0.00118 | 6.6667e-08 | -60.9421 | 62.114 | -61.1526 | -0.050354 | -0.068665 | -0.086975 | -0.004578 | 0.09613 | 0.20142 | -0.32501 | -0.33417 | 0.086975 | -0.1236 | 60.7681 | -62.0956 | 60.4935 | -61.8256 | 0.21057
107.7344 | 123.1705 | -60.7361 | 62.0087 | -0.078474 | 0.015676 | 0.016581 | -0.0033468 | -0.00023392 | 0.00096645 | 6.6667e-08 | -60.8826 | 62.0087 | -61.116 | 0.12817 | 0.13275 | 0.15564 | -0.059509 | 0.36163 | 0.21515 | -0.19684 | -0.37994 | 0 | -0.14648 | 60.8643 | -61.8759 | 60.5392 | -61.7935 | 0.23346
108.7656 | 123.1064 | -60.791 | 61.9949 | 0.23433 | 0.018026 | 0.016581 | 0.000712 | 0.0010477 | 0.0018208 | 0.0023499 | -60.91 | 61.9949 | -61.1252 | 0.027466 | 0.013733 | 0.022888 | -0.14191 | 0.18768 | 0.15564 | -0.33875 | -0.33417 | 0 | -0.11902 | 60.8185 | -61.9812 | 60.4523 | -61.8393 | 0.21515
109.7344 | 123.1018 | -60.7727 | 62.0361 | -0.18529 | 0.015889 | 0.014445 | 0.0019938 | -0.0021565 | -0.0018108 | 0.0027771 | -60.8826 | 62.027 | -61.1298 | 0.10071 | 0.10071 | 0.15106 | 0.027466 | 0.34332 | 0.25177 | -0.1831 | -0.35706 | -0.009155 | -0.10986 | 60.8734 | -61.9354 | 60.5896 | -61.7844 | 0.24719
110.75 | 123.0423 | -60.8139 | 62.0361 | -0.047956 | 0.020589 | 0.020213 | 0.0062662 | 0.0021159 | 0.002248 | -0.00042733 | -60.8505 | 62.1231 | -61.1298 | 0.050354 | 0.009155 | 0.022888 | 0.027466 | 0.21973 | 0.23346 | -0.2655 | -0.31586 | 0.086975 | -0.036621 | 60.8643 | -62.027 | 60.5484 | -61.8027 | 0.27924
111.7344 | 123.024 | -60.8276 | 62.0361 | 0.066485 | 0.020162 | 0.017222 | 0.007548 | 0.0031841 | -0.00031535 | 0.00021367 | -60.8963 | 62.1323 | -61.1572 | -0.004578 | -0.022888 | -0.045776 | 0.027466 | 0.15564 | 0.22888 | -0.28839 | -0.32959 | 0.09613 | -0.068664 | 60.8231 | -62.059 | 60.5392 | -61.8073 | 0.26093
112.7344 | 123.0972 | -60.7819 | 62.0224 | -0.18529 | 0.016744 | 0.01359 | -0.0029196 | 0.0016887 | -0.00095615 | 6.6667e-08 | -60.8505 | 62.059 | -61.1298 | 0.09613 | 0.11902 | 0.15106 | 0.009155 | 0.35248 | 0.23346 | -0.21057 | -0.3479 | 0.036621 | -0.068665 | 60.878 | -61.9034 | 60.5713 | -61.7889 | 0.27924
113.7656 | 123.024 | -60.8185 | 62.0361 | 0.10463 | 0.020162 | 0.017222 | 0.00648 | 0.0038249 | -0.00010175 | 0.00085447 | -60.8826 | 62.1414 | -61.1435 | -0.022888 | -0.054932 | -0.054932 | 0.022888 | 0.14648 | 0.21515 | -0.28839 | -0.32501 | 0.10529 | -0.064087 | 60.7956 | -62.0911 | 60.5301 | -61.821 | 0.26093
114.7344 | 123.056 | -60.8093 | 62.0407 | -0.18529 | 0.01354 | 0.015513 | 0.0017802 | 0.0019023 | -0.00031535 | -0.0012817 | -60.8871 | 62.0865 | -61.1343 | 0.064087 | 0.082397 | 0.10071 | 0.091553 | 0.30212 | 0.2655 | -0.19684 | -0.32501 | 0.045777 | -0.07782 | 60.8734 | -61.9583 | 60.6125 | -61.7752 | 0.24719
115.7656 | 123.111 | -60.8093 | 62.027 | 0.043596 | 0.013112 | 0.013377 | -0.0027058 | 0.0010477 | -0.00010175 | 0.00085447 | -60.9238 | 61.9858 | -61.1526 | 0.036621 | 0.07782 | 0.073242 | -0.059509 | 0.29297 | 0.21515 | -0.24261 | -0.34332 | -0.041199 | -0.11444 | 60.8459 | -61.9492 | 60.5667 | -61.8118 | 0.22888
116.7344 | 123.1338 | -60.7819 | 61.9904 | 0.23433 | 0.016103 | 0.017649 | 0.0019938 | 0.0014751 | 0.0013936 | 0.0012817 | -60.8688 | 62.0041 | -61.1069 | 0.045776 | 0.027466 | 0.027466 | -0.15564 | 0.22888 | 0.14648 | -0.33417 | -0.32501 | 0.013733 | -0.086975 | 60.8276 | -61.9629 | 60.4477 | -61.8439 | 0.23804
117.7656 | 123.1064 | -60.7864 | 61.9904 | 0.29537 | 0.019094 | 0.020854 | 0.0056254 | 0.0027567 | 0.00053925 | -0.00085453 | -60.8505 | 62.0682 | -61.1343 | 0.050354 | 0.013733 | 0.018311 | -0.1831 | 0.20599 | 0.14648 | -0.37079 | -0.3479 | 0.07782 | -0.064087 | 60.8368 | -61.9766 | 60.4156 | -61.8439 | 0.28381
118.7344 | 123.1018 | -60.7956 | 62.0316 | -0.14714 | 0.01653 | 0.018077 | -0.000356 | -2.0324e-05 | 0.00075285 | 6.6667e-08 | -60.8688 | 62.0316 | -61.1114 | 0.10529 | 0.082397 | 0.13733 | 0.032043 | 0.34332 | 0.26093 | -0.20142 | -0.31586 | 0 | -0.073242 | 60.9009 | -61.9492 | 60.5942 | -61.7706 | 0.24262
119.7656 | 123.0423 | -60.8276 | 62.0316 | 0.18855 | 0.020162 | 0.021922 | 0.0051982 | 0.0019023 | 0.00096645 | -0.0010681 | -60.91 | 62.0956 | -61.1298 | -0.036621 | -0.054932 | -0.086975 | -0.073242 | 0.11902 | 0.17853 | -0.34332 | -0.30212 | 0.064087 | -0.082397 | 60.791 | -62.0865 | 60.4843 | -61.853 | 0.21973
120.7344 | 123.143 | -60.759 | 61.9812 | -0.12425 | 0.018239 | 0.016795 | -0.0005696 | 0.00083408 | -0.0011698 | -0.0010681 | -60.8505 | 62.027 | -61.116 | 0.10986 | 0.1236 | 0.17853 | -0.041199 | 0.36163 | 0.21973 | -0.21057 | -0.35706 | 0.045777 | -0.091553 | 60.8688 | -61.8576 | 60.5484 | -61.7615 | 0.2655
121.7656 | 123.1293 | -60.7864 | 62.027 | 0.27248 | 0.017171 | 0.018717 | 0.0060526 | 0.0021159 | 0.00011185 | 0.00064087 | -60.8871 | 62.0773 | -61.1481 | 0.018311 | -0.013733 | -0.022888 | -0.15106 | 0.15106 | 0.17853 | -0.37079 | -0.36163 | 0.050354 | -0.10071 | 60.8047 | -62.0407 | 60.4156 | -61.8484 | 0.26093
122.7344 | 123.056 | -60.7956 | 62.0499 | -0.18529 | 0.019521 | 0.014445 | 0.0002848 | 0.0023295 | 0.00032545 | -0.00064093 | -60.8871 | 62.0544 | -61.1252 | 0.082397 | 0.073242 | 0.10071 | 0.068665 | 0.30212 | 0.24719 | -0.18768 | -0.32959 | 0.004577 | -0.091553 | 60.878 | -61.9766 | 60.6079 | -61.8027 | 0.23804
123.7656 | 123.0927 | -60.8002 | 62.0132 | 0.27248 | 0.021657 | 0.017008 | 0.0077616 | 0.0042521 | 0.00032545 | 0.00042727 | -60.9192 | 62.0773 | -61.1298 | -0.004578 | -0.032043 | -0.054932 | -0.10071 | 0.14191 | 0.17395 | -0.33417 | -0.32959 | 0.064087 | -0.11902 | 60.7956 | -62.0453 | 60.466 | -61.8393 | 0.21057
124.7344 | 123.0881 | -60.8047 | 62.0544 | -0.13951 | 0.016744 | 0.017863 | 7.12e-05 | 0.0012615 | -0.0020244 | 0.0010681 | -60.8643 | 62.0407 | -61.1206 | 0.11444 | 0.10071 | 0.11902 | 0.045776 | 0.33875 | 0.25177 | -0.18768 | -0.31586 | -0.013733 | -0.059509 | 60.9192 | -61.9537 | 60.6171 | -61.8027 | 0.25635
125.7656 | 123.0423 | -60.8047 | 62.027 | 0.29537 | 0.019735 | 0.018717 | 0.0066936 | 0.0033977 | -0.00031535 | 0.0017091 | -60.9192 | 62.0819 | -61.1481 | -0.036621 | -0.064087 | -0.082397 | -0.073242 | 0.11444 | 0.19226 | -0.33417 | -0.34332 | 0.054931 | -0.11444 | 60.7681 | -62.0911 | 60.4706 | -61.8347 | 0.22888
126.7344 | 123.1155 | -60.7636 | 62.027 | 0.043596 | 0.014821 | 0.014659 | -0.0012106 | 0.0021159 | -0.002238 | -0.00021353 | -60.8597 | 62.0132 | -61.1252 | 0.09613 | 0.10529 | 0.13733 | 0.004578 | 0.35706 | 0.2243 | -0.20142 | -0.36163 | -0.013733 | -0.09613 | 60.8597 | -61.9217 | 60.5621 | -61.8027 | 0.2655
127.75 | 123.0789 | -60.8093 | 62.027 | -0.0021797 | 0.020589 | 0.021281 | 0.0043436 | 0.0023295 | -0.00010175 | 0.0014953 | -60.8459 | 62.1277 | -61.1343 | 0.013733 | 0.027466 | 0.073242 | 0.004578 | 0.2243 | 0.23804 | -0.25635 | -0.32501 | 0.10071 | -0.036621 | 60.8231 | -61.9995 | 60.553 | -61.7889 | 0.28839
128.7344 | 123.143 | -60.7544 | 62.0178 | -0.10899 | 0.014821 | 0.018931 | 0.0017802 | 0.0033977 | -0.0020244 | -0.0012817 | -60.8597 | 62.0224 | -61.116 | 0.28381 | 0.16937 | -0.091553 | -0.086975 | 0.43945 | 0.21515 | -0.22888 | -0.36163 | 0.004578 | -0.10528 | 61.0382 | -61.8484 | 60.5255 | -61.8027 | 0.25635
129.7656 | 123.1018 | -60.8093 | 62.0316 | 1.1041 | 0.018667 | 0.018504 | -0.0027058 | 0.0021159 | -0.0011698 | 0.00042727 | -60.9741 | 62.0087 | -61.1526 | 0.041199 | 0.050354 | 0.041199 | -0.054932 | 0.24261 | 0.19226 | -0.2655 | -0.34332 | -0.022888 | -0.16479 | 60.8505 | -61.9812 | 60.5438 | -61.8393 | 0.17853
130.7344 | 123.0972 | -60.7864 | 62.027 | 0.028338 | 0.017385 | 0.014231 | 0.0002848 | -0.00087492 | 0.00096645 | -0.00085453 | -60.8551 | 62.027 | -61.1298 | 0.091553 | 0.10986 | 0.14191 | -0.004578 | 0.35248 | 0.23346 | -0.20142 | -0.34332 | 0 | -0.068665 | 60.878 | -61.9171 | 60.585 | -61.7935 | 0.27466
131.7656 | 123.056 | -60.8002 | 62.0453 | -0.0021797 | 0.02123 | 0.017222 | 0.010325 | 0.0023295 | -0.0011698 | -0.0021361 | -60.8185 | 62.1185 | -61.1252 | 0.091553 | -0.059509 | 0.009155 | 0.059509 | 0.21057 | 0.24261 | -0.27008 | -0.32501 | 0.073242 | -0.01831 | 60.8917 | -62.1048 | 60.5301 | -61.8027 | 0.3067
132.7344 | 123.111 | -60.7727 | 62.027 | -0.086103 | 0.017385 | 0.01594 | -0.0014242 | 0.0027567 | -0.0030924 | 0.00042727 | -60.8688 | 62.0178 | -61.1298 | 0.33417 | -0.27924 | -0.50354 | 0.036621 | 0.58136 | 0.22888 | -0.17395 | -0.35706 | -0.009156 | -0.09613 | 61.1069 | -62.3062 | 60.5988 | -61.7981 | 0.26093
133.7656 | 123.0103 | -60.8322 | 62.0682 | 0.13515 | 0.020589 | 0.015086 | 0.010112 | 0.0038249 | 0.00053925 | -0.0014953 | -60.878 | 62.1323 | -61.1481 | -0.013733 | -0.036621 | -0.054932 | 0.013733 | 0.12817 | 0.2243 | -0.31128 | -0.31586 | 0.064087 | -0.045777 | 60.8185 | -62.1048 | 60.5209 | -61.8439 | 0.27008
134.7344 | 123.1201 | -60.7819 | 61.9949 | -0.032697 | 0.016317 | 0.019572 | -0.0018514 | 0.0033977 | -0.00031535 | 0.00085447 | -60.9009 | 61.9995 | -61.1298 | 0.086975 | 0.09613 | 0.09613 | -0.068665 | 0.29297 | 0.20142 | -0.21515 | -0.3479 | 0.004578 | -0.11902 | 60.8688 | -61.8988 | 60.5667 | -61.7935 | 0.22888
135.7656 | 123.0057 | -60.8368 | 62.059 | 0.11226 | 0.022298 | 0.017008 | 0.009257 | 0.0040385 | -0.0011698 | -0.00042733 | -60.8917 | 62.1552 | -61.1618 | -0.032043 | -0.068665 | -0.10986 | 0.018311 | 0.10071 | 0.23346 | -0.3479 | -0.32501 | 0.09613 | -0.054932 | 60.8047 | -62.1277 | 60.4889 | -61.8256 | 0.27008
136.7344 | 123.1659 | -60.7681 | 62.0178 | -0.025068 | 0.016744 | 0.0097452 | -0.003774 | 0.0023295 | 0.00118 | 0.0010681 | -60.878 | 61.9995 | -61.1526 | 0.10529 | 0.11444 | 0.13275 | -0.068665 | 0.32044 | 0.20599 | -0.21057 | -0.38452 | -0.01831 | -0.10986 | 60.8734 | -61.9034 | 60.5576 | -61.8118 | 0.27466
137.7656 | 123.0469 | -60.8047 | 62.0087 | -0.8109 | 0.021444 | 0.016581 | 0.0066936 | 0.0044657 | 0.00032545 | 0.0019227 | -60.9879 | 62.1277 | -61.1435 | -0.018311 | -0.073242 | -0.10529 | -0.032043 | 0.10529 | 0.21515 | -0.33417 | -0.33874 | 0.11902 | -0.1831 | 60.7864 | -62.0819 | 60.4706 | -61.7935 | 0.15564
138.7344 | 123.1613 | -60.7452 | 62.027 | -0.063215 | 0.016744 | 0.010813 | -0.0044148 | 0.0019023 | -0.0013834 | 0.0014953 | -60.8826 | 62.0132 | -61.1252 | 0.11902 | 0.14191 | 0.17853 | -0.073242 | 0.35706 | 0.21057 | -0.19684 | -0.37994 | -0.013733 | -0.13733 | 60.8643 | -61.8851 | 60.5484 | -61.8164 | 0.24262
139.7656 | 123.0331 | -60.8459 | 62.0361 | 0.19618 | 0.02123 | 0.023631 | 0.0090434 | 0.0038249 | -0.00052895 | 0.00042727 | -60.9421 | 62.1094 | -61.1526 | -0.045776 | -0.073242 | -0.07782 | -0.004578 | 0.091553 | 0.1831 | -0.33875 | -0.3067 | 0.073242 | -0.096131 | 60.8002 | -62.1094 | 60.5072 | -61.853 | 0.21057
140.7344 | 123.1476 | -60.7864 | 62.0087 | -0.0098092 | 0.015249 | 0.017863 | -0.0016378 | 0.0042521 | -0.00010175 | 0.0014953 | -60.91 | 62.0041 | -61.1206 | 0.07782 | 0.10071 | 0.10529 | -0.091553 | 0.29297 | 0.20599 | -0.23804 | -0.33417 | -0.004578 | -0.1236 | 60.8643 | -61.908 | 60.5484 | -61.8027 | 0.21057
141.7656 | 123.0469 | -60.8276 | 62.0453 | 0.058855 | 0.019948 | 0.019999 | 0.0084026 | 0.0046793 | -0.0015972 | -0.0032043 | -60.8505 | 62.1277 | -61.0931 | 0.032043 | 0.004578 | 0 | 0.009155 | 0.1831 | 0.22888 | -0.29755 | -0.2655 | 0.082398 | -0.022888 | 60.8597 | -62.0407 | 60.5301 | -61.8164 | 0.24262
142.7344 | 123.111 | -60.7773 | 62.0178 | 0.32588 | 0.015889 | 0.014231 | -0.0024922 | 0.0042521 | 0.00053925 | 0.0023499 | -60.9055 | 62.0178 | -61.1343 | 0.032043 | 0.036621 | 0.041199 | -0.068665 | 0.25635 | 0.20599 | -0.25635 | -0.35706 | 0 | -0.12817 | 60.8093 | -61.9812 | 60.5209 | -61.8118 | 0.22888
143.75 | 123.0789 | -60.7773 | 62.0453 | -0.070844 | 0.021657 | 0.019358 | 0.0096842 | 0.0036113 | -0.0013834 | -0.00085453 | -60.8551 | 62.114 | -61.1572 | 0.050354 | 0.036621 | 0.050354 | 0.013733 | 0.24261 | 0.2243 | -0.2655 | -0.37994 | 0.068665 | -0.07782 | 60.8276 | -62.0087 | 60.5118 | -61.821 | 0.30212
144.7344 | 123.1155 | -60.7773 | 62.0361 | 0.11226 | 0.014608 | 0.017222 | -0.003774 | 0.0016887 | -0.00074255 | 0.00085447 | -60.9146 | 62.0178 | -61.1298 | 0.041199 | 0.050354 | 0.059509 | -0.064087 | 0.25177 | 0.19684 | -0.24719 | -0.35248 | -0.018311 | -0.13733 | 60.8185 | -61.9858 | 60.5301 | -61.8393 | 0.21515
145.75 | 123.0331 | -60.8185 | 62.0544 | -0.1624 | 0.019735 | 0.014659 | 0.0037028 | -2.0324e-05 | -0.00031535 | -0.00021353 | -60.8917 | 62.0682 | -61.116 | 0.036621 | 0.027466 | 0.068665 | 0.15106 | 0.29755 | 0.26093 | -0.16937 | -0.29755 | 0.013733 | -0.073243 | 60.8551 | -62.027 | 60.6491 | -61.7935 | 0.2243
146.7344 | 123.111 | -60.7956 | 62.0132 | 0.035967 | 0.015462 | 0.017649 | -0.0016378 | 0.0025431 | -0.00052895 | 0.0012817 | -60.9467 | 61.9995 | -61.1389 | 0.018311 | 0.041199 | 0.036621 | -0.068665 | 0.24261 | 0.19226 | -0.27008 | -0.34332 | -0.013733 | -0.15106 | 60.8139 | -61.972 | 60.5255 | -61.821 | 0.19226
147.7656 | 123.0148 | -60.8231 | 62.0728 | 0.10463 | 0.02123 | 0.022135 | 0.0088298 | 0.0019023 | -0.0018108 | -0.00042733 | -60.8734 | 62.1094 | -61.1343 | 0.009155 | -0.054932 | -0.045776 | 0.009155 | 0.13733 | 0.19684 | -0.31586 | -0.31128 | 0.036621 | -0.050354 | 60.8322 | -62.1277 | 60.5072 | -61.8759 | 0.26093
148.7344 | 123.143 | -60.791 | 61.972 | 0.28774 | 0.015676 | 0.015727 | 7.12e-05 | 0.0023295 | -0.0011698 | -0.00021353 | -60.8871 | 61.9949 | -61.1343 | 0.045776 | 0.041199 | 0.036621 | -0.16022 | 0.21057 | 0.16479 | -0.32501 | -0.34332 | 0.022888 | -0.09613 | 60.8368 | -61.9308 | 60.466 | -61.8073 | 0.24719
149.7656 | 123.0194 | -60.791 | 62.0499 | -1.9248 | 0.017598 | 0.017436 | 0.0054118 | 0.0016887 | 0.00011185 | -0.0029907 | -60.997 | 62.1368 | -61.1206 | 0.018311 | 0.027466 | 0.009155 | 0.15564 | 0.27924 | 0.27466 | -0.25177 | -0.32959 | 0.086975 | -0.20599 | 60.8093 | -62.0224 | 60.5392 | -61.7752 | 0.1236
150.7344 | 123.0927 | -60.8047 | 62.0316 | 0.21907 | 0.018667 | 0.019572 | -0.0031332 | 0.0029705 | -0.00031535 | -0.0010681 | -60.9467 | 62.0178 | -61.1435 | 0.018311 | 0.036621 | 0.027466 | -0.091553 | 0.21057 | 0.16937 | -0.28839 | -0.33874 | -0.013733 | -0.14191 | 60.8231 | -61.9949 | 60.5164 | -61.8622 | 0.19684
151.7656 | 122.9965 | -60.8002 | 62.0407 | 0.10463 | 0.021016 | 0.015513 | 0.0073344 | 0.0036113 | 0.00011185 | 0.00021367 | -60.8963 | 62.1323 | -61.1298 | -0.032043 | -0.059509 | -0.082397 | 0.032043 | 0.10529 | 0.21515 | -0.33417 | -0.32959 | 0.091553 | -0.09613 | 60.7681 | -62.1002 | 60.466 | -61.8256 | 0.23346
152.7344 | 123.1201 | -60.7819 | 61.9904 | 0.16567 | 0.018453 | 0.015513 | 0.0026346 | 0.0019023 | -0.002238 | -0.00042733 | -60.9055 | 62.0087 | -61.1526 | 0.041199 | 0.036621 | 0.004578 | -0.15564 | 0.21515 | 0.16937 | -0.33875 | -0.37079 | 0.018311 | -0.1236 | 60.8231 | -61.9537 | 60.4431 | -61.821 | 0.24719
153.7656 | 123.0423 | -60.8047 | 62.0636 | -0.20054 | 0.016317 | 0.015086 | 0.001353 | 0.00019328 | 0.00075285 | -0.00064093 | -60.8963 | 62.0911 | -61.1206 | 0.059509 | 0.068665 | 0.09613 | 0.09613 | 0.27924 | 0.25635 | -0.21057 | -0.31586 | 0.027465 | -0.091552 | 60.8643 | -61.9949 | 60.5942 | -61.8073 | 0.2243
154.7344 | 123.143 | -60.7819 | 61.9995 | -0.28447 | 0.017385 | 0.016795 | 0.0009258 | 0.0027567 | -0.00095615 | 0.00042727 | -60.7269 | 62.0453 | -61.1069 | 0.054932 | 0.064087 | 0.018311 | -0.22888 | 0.21057 | 0.15564 | -0.29755 | -0.32501 | 0.045776 | 0.054931 | 60.8368 | -61.9354 | 60.4843 | -61.8439 | 0.37994
155.75 | 123.1567 | -60.759 | 62.027 | -0.0098092 | 0.014608 | 0.01359 | -0.0001424 | 0.00040688 | 0.00096645 | 0.0017091 | -60.91 | 62.0087 | -61.1343 | 0.082397 | 0.10529 | 0.11902 | -0.07782 | 0.32501 | 0.21515 | -0.2243 | -0.37537 | -0.018311 | -0.15106 | 60.8414 | -61.9217 | 60.5347 | -61.8118 | 0.2243
156.7344 | 123.143 | -60.7864 | 61.9858 | 0.28011 | 0.019094 | 0.014018 | 0.0037028 | 0.00062048 | 0.00032545 | -0.00064093 | -60.8643 | 62.0132 | -61.1252 | 0.054932 | 0.041199 | 0.032043 | -0.20142 | 0.21973 | 0.14191 | -0.38452 | -0.33875 | 0.027466 | -0.07782 | 60.8414 | -61.9446 | 60.4019 | -61.8439 | 0.26093
157.7656 | 123.0789 | -60.7819 | 62.0728 | -0.19291 | 0.017598 | 0.014659 | 0.0015666 | -0.00087492 | -0.00031535 | -0.0012817 | -60.8734 | 62.0453 | -61.1298 | 0.091553 | 0.09613 | 0.14648 | 0.032043 | 0.34332 | 0.26093 | -0.20599 | -0.3479 | -0.027466 | -0.091553 | 60.8734 | -61.9766 | 60.5759 | -61.8118 | 0.25635
158.7344 | 123.1018 | -60.7864 | 62.0041 | 0.25722 | 0.020803 | 0.021495 | 0.005839 | 0.0014751 | -0.00074255 | -0.00042733 | -60.8963 | 62.0682 | -61.1435 | 0.041199 | 0.027466 | 0.009155 | -0.18768 | 0.15564 | 0.16479 | -0.36621 | -0.35706 | 0.064087 | -0.10986 | 60.8276 | -61.9766 | 60.4202 | -61.8393 | 0.24719
159.7656 | 123.0789 | -60.8002 | 62.027 | -0.17003 | 0.017171 | 0.013804 | 0.0009258 | 0.00040688 | 0.00053925 | 0.0010681 | -60.8826 | 62.0453 | -61.1252 | 0.10071 | 0.082397 | 0.10986 | 0.064087 | 0.29755 | 0.2655 | -0.20599 | -0.32501 | 0.01831 | -0.082397 | 60.9009 | -61.9446 | 60.5942 | -61.7615 | 0.24262
160.7344 | 123.1522 | -60.8002 | 61.9904 | 0.089373 | 0.018026 | 0.019145 | 0.004771 | 0.0019023 | -0.002238 | 0.00021367 | -60.8597 | 62.0499 | -61.1252 | 0.027466 | 0.027466 | 0.027466 | -0.17395 | 0.20142 | 0.16022 | -0.3479 | -0.32501 | 0.05951 | -0.059509 | 60.8276 | -61.9629 | 60.4523 | -61.8301 | 0.2655
161.7656 | 123.1201 | -60.7407 | 62.0361 | -0.3455 | 0.016103 | 0.01295 | 0.0009258 | -2.0324e-05 | -0.00052895 | 0.00085447 | -60.9009 | 62.0178 | -61.1298 | 0.12817 | 0.11444 | 0.10986 | -0.009155 | 0.36621 | 0.20599 | -0.21057 | -0.3891 | -0.018311 | -0.16022 | 60.8688 | -61.9217 | 60.5301 | -61.8301 | 0.22888
162.7344 | 122.9919 | -60.8322 | 62.0361 | 0.15804 | 0.021657 | 0.019572 | 0.0056254 | 0.0031841 | 0.00096645 | 6.6667e-08 | -60.9238 | 62.1048 | -61.1481 | -0.064087 | -0.091553 | -0.10986 | 0.009155 | 0.07782 | 0.20599 | -0.36163 | -0.31586 | 0.068664 | -0.091553 | 60.7681 | -62.1277 | 60.4706 | -61.8301 | 0.2243
163.7656 | 123.0835 | -60.8093 | 62.0453 | -0.093733 | 0.020803 | 0.023417 | 0.005839 | 0.0023295 | -0.0018108 | -0.00085453 | -60.9009 | 62.1597 | -61.1526 | 0.054932 | 0.045776 | 0.064087 | 0.10071 | 0.24719 | 0.27008 | -0.19226 | -0.34332 | 0.11444 | -0.091553 | 60.8643 | -61.9995 | 60.6171 | -61.7752 | 0.25177
164.7344 | 123.1293 | -60.7956 | 62.0041 | 0.25722 | 0.019307 | 0.018504 | 0.003062 | 0.0046793 | -0.00031535 | -0.00042733 | -60.8917 | 62.0865 | -61.1206 | 0.041199 | 0.027466 | -0.004578 | -0.2243 | 0.17853 | 0.15106 | -0.3891 | -0.32501 | 0.082398 | -0.096131 | 60.8368 | -61.9766 | 60.4065 | -61.853 | 0.22888
165.7656 | 123.175 | -60.7773 | 62.0316 | -0.047956 | 0.013967 | 0.014872 | -0.0016378 | -0.00044752 | -0.0013834 | 0.0027771 | -60.8734 | 62.0224 | -61.1069 | 0.15564 | 0.16022 | 0.19226 | -0.027466 | 0.36163 | 0.21515 | -0.1831 | -0.32959 | -0.009155 | -0.09613 | 60.9329 | -61.8713 | 60.5942 | -61.8164 | 0.23346
166.7344 | 123.0194 | -60.8368 | 62.0316 | 0.20381 | 0.022085 | 0.019786 | 0.004771 | -0.0019429 | 0.00032545 | 0.00042727 | -60.7636 | 62.114 | -61.1526 | -0.14648 | 0.050354 | 0.11444 | -0.082397 | 0.064087 | 0.20599 | -0.31586 | -0.31586 | 0.082398 | 0.073242 | 60.6903 | -61.9812 | 60.5209 | -61.8256 | 0.3891
167.7656 | 123.1613 | -60.7681 | 61.9949 | -0.040327 | 0.017385 | 0.01594 | -0.0039876 | 0.0012615 | 0.00053925 | 0.0010681 | -60.91 | 62.0132 | -61.1343 | 0.09613 | 0.11444 | 0.16022 | -0.064087 | 0.34332 | 0.21973 | -0.22888 | -0.36621 | 0.018311 | -0.14191 | 60.8643 | -61.8805 | 60.5392 | -61.7752 | 0.2243
168.7344 | 123.0698 | -60.8185 | 62.0132 | 0.31825 | 0.021871 | 0.020213 | 0.0071208 | 0.0016887 | 0.0013936 | 0.00064087 | -60.91 | 62.114 | -61.1572 | -0.027466 | -0.068665 | -0.082397 | -0.059509 | 0.09613 | 0.19226 | -0.34332 | -0.33875 | 0.10071 | -0.091553 | 60.791 | -62.0819 | 60.4752 | -61.821 | 0.24719
169.7656 | 122.9874 | -60.8414 | 62.0453 | 0.15804 | 0.020803 | 0.02299 | 0.0060526 | 0.0027567 | 0.0020344 | 0.00042727 | -60.9055 | 62.1323 | -61.1343 | -0.041199 | -0.073242 | -0.091553 | 0.018311 | 0.09613 | 0.20599 | -0.36163 | -0.29297 | 0.086975 | -0.064087 | 60.8002 | -62.1185 | 60.4797 | -61.8393 | 0.22888
170.7344 | 123.024 | -60.8322 | 62.0453 | 0.23433 | 0.023794 | 0.020426 | 0.00413 | 0.0055339 | 0.00053925 | -0.00064093 | -61.116 | 62.0773 | -61.1664 | 0.086975 | 0.050354 | -0.13733 | -0.027466 | 0.15106 | 0.21973 | -0.29297 | -0.33417 | 0.032044 | -0.28381 | 60.9192 | -61.9949 | 60.5392 | -61.8256 | 0.050354
171.7656 | 123.0103 | -60.8139 | 62.0361 | -0.20054 | 0.018239 | 0.019358 | 0.0004984 | 0.0023295 | -0.00095615 | -0.0019225 | -60.9375 | 62.1185 | -61.1435 | 0.009155 | 0.032043 | 0.054932 | 0.14648 | 0.24719 | 0.27924 | -0.16022 | -0.32959 | 0.082397 | -0.1236 | 60.8231 | -62.0041 | 60.6537 | -61.7569 | 0.20599
172.7344 | 123.056 | -60.8002 | 62.0316 | 0.19618 | 0.020589 | 0.017863 | 0.0056254 | 0.0031841 | -0.0013834 | 0.00085447 | -60.9055 | 62.1048 | -61.1526 | -0.036621 | -0.050354 | -0.068665 | -0.054932 | 0.10986 | 0.18768 | -0.35706 | -0.35248 | 0.073242 | -0.10529 | 60.7636 | -62.0819 | 60.4431 | -61.8439 | 0.24719
173.7656 | 123.0377 | -60.8047 | 62.0453 | -0.2158 | 0.016958 | 0.017863 | 0.0015666 | 0.0014751 | -0.00052895 | 0.00064087 | -60.9009 | 62.0773 | -61.1252 | 0.032043 | 0.027466 | 0.059509 | 0.15106 | 0.31128 | 0.25635 | -0.17395 | -0.32043 | 0.032044 | -0.09613 | 60.8368 | -62.0178 | 60.6308 | -61.7889 | 0.2243
174.7344 | 123.0881 | -60.8047 | 62.0224 | 0.23433 | 0.019094 | 0.020854 | 0.0011394 | 0.0023295 | 0.00118 | 0.00085447 | -60.9192 | 62.059 | -61.1252 | 0.004578 | 0.013733 | 0 | -0.11444 | 0.20142 | 0.16937 | -0.28381 | -0.32043 | 0.036621 | -0.11444 | 60.8093 | -62.0087 | 60.5209 | -61.853 | 0.20599
175.75 | 123.0972 | -60.7864 | 62.0407 | 0.18855 | 0.017385 | 0.016154 | -0.0016378 | -2.0324e-05 | 0.00096645 | 0.0025635 | -60.9467 | 62.0132 | -61.1572 | 0.018311 | 0.032043 | 0.018311 | -0.10529 | 0.21057 | 0.17395 | -0.28381 | -0.37079 | -0.027465 | -0.16022 | 60.8047 | -62.0087 | 60.5026 | -61.8668 | 0.21057
176.7344 | 122.9965 | -60.8047 | 62.059 | 0.10463 | 0.021871 | 0.020213 | 0.0094706 | -0.0010885 | 0.00011185 | -0.00064093 | -60.91 | 62.1277 | -61.1298 | -0.045776 | -0.054932 | -0.09613 | 0.013733 | 0.082397 | 0.21515 | -0.35706 | -0.32501 | 0.068665 | -0.10529 | 60.759 | -62.114 | 60.4477 | -61.8439 | 0.21973
177.7656 | 123.0148 | -60.8139 | 62.0544 | -0.17766 | 0.01888 | 0.010386 | 0.0051982 | 0.00062048 | -0.0011698 | -0.00085453 | -60.8963 | 62.1552 | -61.1481 | -0.018311 | -0.050354 | 0 | 0.12817 | 0.2243 | 0.26093 | -0.2243 | -0.33417 | 0.10071 | -0.082397 | 60.7956 | -62.1048 | 60.5896 | -61.7935 | 0.25177
178.7344 | 123.0652 | -60.8093 | 62.027 | 0.21907 | 0.02123 | 0.017222 | 0.0069072 | 0.0040385 | -0.00095615 | -0.00021353 | -60.9238 | 62.1185 | -61.1664 | -0.041199 | -0.032043 | -0.073242 | -0.082397 | 0.10986 | 0.19226 | -0.34332 | -0.35706 | 0.091552 | -0.11444 | 60.7681 | -62.059 | 60.466 | -61.8347 | 0.24262
179.7656 | 123.0148 | -60.8093 | 62.0728 | -0.093733 | 0.019735 | 0.0086772 | 0.0009258 | 0.00083408 | -0.002238 | 0.0014953 | -60.9421 | 62.0911 | -61.1481 | 0.022888 | 0.041199 | 0.059509 | 0.1236 | 0.25635 | 0.27466 | -0.16022 | -0.33875 | 0.01831 | -0.13275 | 60.8322 | -62.0316 | 60.6491 | -61.7981 | 0.20599
180.7344 | 123.0469 | -60.8185 | 62.0132 | 0.23433 | 0.022085 | 0.019145 | 0.00648 | 0.0042521 | -0.0024516 | 0.0014953 | -60.9283 | 62.1002 | -61.1435 | -0.045776 | -0.036621 | -0.068665 | -0.07782 | 0.10529 | 0.17853 | -0.34332 | -0.32501 | 0.086975 | -0.10986 | 60.7727 | -62.0499 | 60.4752 | -61.8347 | 0.21515
181.7656 | 123.0194 | -60.8002 | 62.0499 | -0.20054 | 0.017171 | 0.014872 | 0.0011394 | 0.0012615 | -0.00052895 | -0.0017089 | -60.9421 | 62.0956 | -61.116 | 0.022888 | 0.045776 | 0.07782 | 0.13733 | 0.24261 | 0.2655 | -0.17395 | -0.31586 | 0.045776 | -0.14191 | 60.8231 | -62.0041 | 60.6262 | -61.7844 | 0.17395
182.7344 | 123.1522 | -60.7819 | 62.0041 | -0.0021797 | 0.017598 | 0.011668 | -0.0029196 | -0.00044752 | 0.00075285 | 6.6667e-08 | -60.91 | 62.0224 | -61.1252 | 0.082397 | 0.086975 | 0.11444 | -0.068665 | 0.32044 | 0.21057 | -0.24261 | -0.34332 | 0.018311 | -0.12817 | 60.8643 | -61.9171 | 60.5392 | -61.7935 | 0.21515
183.7656 | 123.1522 | -60.7819 | 62.0087 | -0.14714 | 0.016317 | 0.011668 | -0.0005696 | 0.0012615 | -0.0020244 | 0.00064087 | -60.8688 | 62.0132 | -61.1114 | 0.086975 | 0.5127 | 0.75989 | -0.46692 | -0.31128 | 0.26093 | -0.1831 | -0.32959 | 0.004578 | -0.086975 | 60.8688 | -61.496 | 60.5988 | -61.7477 | 0.24262
184.7344 | 123.1522 | -60.8002 | 61.9904 | 0.46321 | 0.018667 | 0.019358 | 0.0062662 | 0.00083408 | -0.00031535 | -0.0012817 | -60.8322 | 62.0499 | -61.1343 | 0.045776 | 0.022888 | 0.004578 | -0.18768 | 0.21057 | 0.15106 | -0.37079 | -0.33417 | 0.05951 | -0.032043 | 60.8459 | -61.9675 | 60.4294 | -61.8393 | 0.30212
185.7656 | 123.1476 | -60.7773 | 62.0087 | -0.11662 | 0.014608 | 0.012309 | -0.0029196 | -0.0027975 | 0.0020344 | 0.00064087 | -60.8688 | 62.0361 | -61.1114 | -0.29755 | 0.045776 | 0.40283 | -0.07782 | 0.14648 | 0.22888 | -0.20599 | -0.33417 | 0.027466 | -0.091552 | 60.4797 | -61.9629 | 60.5713 | -61.7798 | 0.24262
186.7344 | 123.1018 | -60.8322 | 62.0178 | 0.24959 | 0.02123 | 0.019358 | 0.0084026 | 0.00083408 | 0.00118 | -0.00085453 | -60.8963 | 62.0773 | -61.1435 | -0.022888 | -0.036621 | -0.059509 | -0.11444 | 0.13733 | 0.16022 | -0.32959 | -0.31128 | 0.05951 | -0.064087 | 60.8093 | -62.0544 | 60.5026 | -61.8576 | 0.24719
187.7656 | 123.0881 | -60.7864 | 62.027 | 0.15804 | 0.018667 | 0.017436 | 0.0011394 | -0.00066112 | 0.0031026 | -0.00021353 | -60.9283 | 62.0728 | -61.116 | 0.022888 | 0.032043 | 0.032043 | -0.086975 | 0.23346 | 0.1831 | -0.28839 | -0.32959 | 0.045776 | -0.14191 | 60.8093 | -61.9949 | 60.498 | -61.8439 | 0.18768
188.7344 | 123.143 | -60.7819 | 61.9995 | 0.27248 | 0.017385 | 0.019358 | 0.005839 | 0.0019023 | -0.0015972 | 0.0023499 | -60.8505 | 62.0224 | -61.1526 | 0.054932 | 0.032043 | 0.009155 | -0.20599 | 0.20599 | 0.13275 | -0.36621 | -0.37079 | 0.022888 | -0.068665 | 60.8368 | -61.9675 | 60.4156 | -61.8668 | 0.30212
189.75 | 123.1293 | -60.7956 | 62.0316 | 0.028338 | 0.016958 | 0.017222 | -0.0024922 | 0.0010477 | 0.00011185 | 0.00085447 | -60.9329 | 62.0361 | -61.1572 | 0.086975 | 0.082397 | 0.091553 | -0.068665 | 0.31586 | 0.21973 | -0.25177 | -0.36163 | 0.004578 | -0.13733 | 60.8826 | -61.9492 | 60.5438 | -61.8118 | 0.22431
190.7344 | 123.0743 | -60.8231 | 62.0224 | 0.303 | 0.020162 | 0.015513 | 0.0088298 | 0.0012615 | -0.00010175 | 6.6667e-08 | -60.9055 | 62.1048 | -61.1481 | -0.004578 | -0.036621 | -0.045776 | -0.11902 | 0.13733 | 0.17853 | -0.32501 | -0.32501 | 0.082397 | -0.082398 | 60.8185 | -62.059 | 60.498 | -61.8439 | 0.24261
191.75 | 123.175 | -60.7544 | 62.0224 | -0.070844 | 0.015462 | 0.019358 | 0.000712 | -0.00044752 | 0.00032545 | 0.00085447 | -60.8734 | 61.9766 | -61.1114 | 0.13733 | 0.15106 | 0.17395 | -0.064087 | 0.3891 | 0.21973 | -0.19684 | -0.35705 | -0.045776 | -0.11902 | 60.8917 | -61.8713 | 60.5576 | -61.8027 | 0.23804
192.7344 | 123.1476 | -60.7864 | 62.0041 | -0.15477 | 0.016103 | 0.016795 | 0.0043436 | 0.00083408 | 0.0024618 | -0.00064093 | -60.8597 | 62.0224 | -61.0977 | 0.054932 | 0.027466 | 0.036621 | -0.19684 | 0.23804 | 0.15564 | -0.31586 | -0.31128 | 0.018311 | -0.073242 | 60.8414 | -61.9766 | 60.4706 | -61.8484 | 0.23804
193.7656 | 123.1293 | -60.7452 | 62.027 | -1.6654 | 0.016744 | 0.018717 | 0.0009258 | -2.0324e-05 | 0.0013936 | 0.00064087 | -60.7819 | 62.0499 | -61.084 | 0.11444 | 0.16937 | 0.12817 | -0.07782 | 0.37537 | 0.21515 | -0.24261 | -0.33875 | 0.022888 | -0.036621 | 60.8597 | -61.8576 | 60.5026 | -61.8118 | 0.30212
194.7344 | 123.143 | -60.7727 | 62.0224 | 0.089373 | 0.018453 | 0.016581 | 0.0026346 | 0.0023295 | -0.00010175 | -0.00042733 | -60.8231 | 62.0132 | -61.1206 | 0.054932 | 0.050354 | 0.022888 | -0.19684 | 0.23804 | 0.16937 | -0.32044 | -0.3479 | -0.009155 | -0.050354 | 60.8276 | -61.972 | 60.4523 | -61.853 | 0.29755
195.7656 | 123.0469 | -60.7956 | 62.0636 | -0.1624 | 0.020162 | 0.022776 | 0.0069072 | 0.00062048 | -0.0011698 | -0.0017089 | -60.8734 | 62.1552 | -61.116 | 0.064087 | 0.041199 | 0.059509 | 0.064087 | 0.25635 | 0.24719 | -0.21057 | -0.32044 | 0.091552 | -0.07782 | 60.8597 | -62.0224 | 60.585 | -61.8164 | 0.24262
196.7344 | 123.1247 | -60.7636 | 61.9858 | 0.28011 | 0.01888 | 0.017649 | 0.0037028 | 0.0019023 | -0.0015972 | 0.0010681 | -60.8643 | 62.0407 | -61.1389 | 0.059509 | 0.032043 | 0.027466 | -0.20142 | 0.2243 | 0.15564 | -0.35248 | -0.37537 | 0.054931 | -0.10071 | 60.8231 | -61.9537 | 60.4111 | -61.8301 | 0.27466
197.75 | 122.9965 | -60.8185 | 62.059 | -0.19291 | 0.019307 | 0.016154 | 0.001353 | 0.00040688 | -0.0011698 | 0.00042727 | -60.9558 | 62.1002 | -61.1481 | 0.30212 | 0.17853 | -0.37994 | -0.20142 | 0.27924 | 0.28839 | -0.14648 | -0.32959 | 0.041199 | -0.13733 | 61.1206 | -61.8805 | 60.672 | -61.7706 | 0.19226
198.7344 | 123.1018 | -60.8002 | 62.0132 | 0.24196 | 0.017598 | 0.018077 | 0.001353 | 0.0021159 | 0.00011185 | 0.0010681 | -60.9009 | 61.9949 | -61.116 | 0.027466 | 0.045776 | 0.009155 | -0.13733 | 0.19684 | 0.17853 | -0.32044 | -0.31586 | -0.018311 | -0.10071 | 60.8276 | -61.9675 | 60.4797 | -61.8347 | 0.21515
199.7656 | 123.056 | -60.8231 | 62.059 | -0.13951 | 0.017598 | 0.016154 | 0.0073344 | 0.0027567 | -0.00031535 | 0.0010681 | -60.8963 | 62.1323 | -61.1114 | 0.064087 | 0.050354 | 0.050354 | 0.091553 | 0.24261 | 0.26093 | -0.20599 | -0.28839 | 0.073242 | -0.073242 | 60.8871 | -62.0087 | 60.6171 | -61.7981 | 0.21515
200.7344 | 123.1018 | -60.8093 | 62.0041 | 0.21907 | 0.018453 | 0.017222 | 0.0004984 | 0.00083408 | -0.00031535 | 0.0014953 | -60.91 | 61.9858 | -61.1618 | 0.009155 | 0.032043 | 0.022888 | -0.15106 | 0.19684 | 0.16022 | -0.31128 | -0.35248 | -0.01831 | -0.10071 | 60.8185 | -61.972 | 60.498 | -61.8439 | 0.25177
201.7656 | 123.0606 | -60.8093 | 62.0361 | -0.055586 | 0.021871 | 0.02299 | 0.0073344 | 0.0036113 | -0.00031535 | 6.6667e-08 | -60.8551 | 62.1506 | -61.1069 | 0.054932 | 0.045776 | 0.036621 | 0.013733 | 0.22888 | 0.25635 | -0.27466 | -0.29755 | 0.11444 | -0.045777 | 60.8643 | -61.9904 | 60.5347 | -61.7798 | 0.25177
202.7344 | 123.1201 | -60.7681 | 62.0132 | 0.20381 | 0.019307 | 0.014872 | 0.000712 | 0.0019023 | 0.00075285 | 0.0023499 | -60.8963 | 61.9904 | -61.1435 | 0.032043 | 0.050354 | 0.032043 | -0.16022 | 0.19684 | 0.15564 | -0.32501 | -0.37537 | -0.022889 | -0.12817 | 60.8002 | -61.9629 | 60.4431 | -61.8576 | 0.24719
203.7656 | 123.0286 | -60.8368 | 62.0499 | -0.31499 | 0.015889 | 0.01295 | 0.0022074 | -0.00087492 | -0.0015972 | 0.0021363 | -60.9421 | 62.0819 | -61.1572 | 0.004578 | 0.032043 | 0.073242 | 0.13275 | 0.24261 | 0.2655 | -0.16022 | -0.32043 | 0.032043 | -0.10529 | 60.8414 | -62.0178 | 60.6766 | -61.7844 | 0.21515
204.7344 | 123.0972 | -60.7956 | 62.0224 | 0.18855 | 0.018667 | 0.015513 | 0.0017802 | -2.0324e-05 | 0.0013936 | 0.00021367 | -60.8917 | 61.9812 | -61.1526 | 0.036621 | 0.041199 | 0.036621 | -0.17853 | 0.21973 | 0.1831 | -0.35706 | -0.35706 | -0.041199 | -0.096131 | 60.8322 | -61.9812 | 60.4385 | -61.8393 | 0.26092
205.7656 | 123.0652 | -60.8276 | 62.0407 | -0.070844 | 0.019735 | 0.021708 | 0.0098978 | 0.00040688 | -0.00095615 | -0.0010681 | -60.8643 | 62.1414 | -61.1206 | 0.073242 | 0.041199 | 0.059509 | 0.059509 | 0.24261 | 0.23346 | -0.23346 | -0.29297 | 0.10071 | -0.036621 | 60.9009 | -61.9995 | 60.5942 | -61.8073 | 0.25635
206.7344 | 123.0972 | -60.8047 | 62.0178 | 0.15041 | 0.017171 | 0.014445 | -0.0007832 | 0.0021159 | 0.00032545 | 0.0010681 | -60.9192 | 62.0132 | -61.1435 | 0.009155 | 0.009155 | 0.013733 | -0.1236 | 0.17853 | 0.1831 | -0.28839 | -0.33874 | -0.004577 | -0.11444 | 60.8139 | -62.0087 | 60.5164 | -61.8347 | 0.2243
207.7656 | 123.0011 | -60.8322 | 62.0773 | -0.29973 | 0.016744 | 0.015299 | 0.004771 | 0.00019328 | -0.00095615 | 0.00064087 | -60.9375 | 62.0865 | -61.1023 | 0.036621 | 0.009155 | 0.032043 | 0.14648 | 0.24719 | 0.25635 | -0.17853 | -0.27008 | 0.009155 | -0.10529 | 60.8688 | -62.0682 | 60.6537 | -61.821 | 0.16479
208.7344 | 123.1476 | -60.8093 | 61.9858 | 0.26485 | 0.020803 | 0.017222 | 0.002421 | 0.0048931 | -0.0015972 | 0.00064087 | -60.965 | 62.0132 | -61.1435 | 0.10986 | 0.11902 | 0.050354 | -0.17853 | 0.24261 | 0.16937 | -0.3067 | -0.33417 | 0.027466 | -0.15564 | 60.9192 | -61.8668 | 60.5026 | -61.8164 | 0.17853
209.7656 | 123.0606 | -60.8047 | 62.0499 | -0.10899 | 0.022298 | 0.016581 | 0.0062662 | 0.0016887 | -0.002238 | -0.0010681 | -60.9009 | 62.114 | -61.1526 | 0.041199 | 0.027466 | 0.045776 | 0.1236 | 0.23346 | 0.24719 | -0.21057 | -0.3479 | 0.064087 | -0.09613 | 60.8459 | -62.0224 | 60.5942 | -61.8027 | 0.25177
210.7344 | 123.143 | -60.7864 | 61.9858 | 0.27248 | 0.018026 | 0.015299 | 0.0032756 | 0.0033977 | -0.00031535 | -0.00085453 | -60.8551 | 62.0316 | -61.1481 | 0.064087 | 0.036621 | 0.027466 | -0.20599 | 0.21973 | 0.15106 | -0.35706 | -0.36163 | 0.045776 | -0.068665 | 60.8505 | -61.9492 | 60.4294 | -61.8347 | 0.29297
211.7656 | 123.0148 | -60.8459 | 62.027 | 0.12752 | 0.019948 | 0.01829 | 0.010325 | 0.0029705 | -0.00031535 | 0.00064087 | -60.91 | 62.1277 | -61.1206 | -0.032043 | -0.064087 | -0.091553 | 0.022888 | 0.11444 | 0.21973 | -0.33417 | -0.27466 | 0.10071 | -0.064087 | 60.8139 | -62.0911 | 60.5118 | -61.8073 | 0.21057
212.7344 | 123.0972 | -60.7819 | 61.9949 | 0.18855 | 0.015889 | 0.019145 | -0.0014242 | 0.0044657 | -0.00010175 | 0.0019227 | -60.9009 | 62.0224 | -61.1435 | 0.027466 | 0.036621 | 0.027466 | -0.14648 | 0.18768 | 0.16022 | -0.33417 | -0.36163 | 0.027466 | -0.11902 | 60.8093 | -61.9583 | 60.4477 | -61.8347 | 0.24261
213.7656 | 122.9782 | -60.8139 | 62.0224 | 0.19618 | 0.022298 | 0.023204 | 0.009257 | 0.0044657 | 0.00053925 | 0.00042727 | -60.9192 | 62.1597 | -61.1252 | -0.064087 | -0.091553 | -0.10071 | -0.013733 | 0.10071 | 0.19684 | -0.3479 | -0.31128 | 0.13733 | -0.10529 | 60.7498 | -62.114 | 60.466 | -61.8256 | 0.20599
214.7344 | 123.1293 | -60.7773 | 61.9766 | 0.28774 | 0.017598 | 0.015727 | 0.0019938 | 0.0036113 | 0.00075285 | 0.0012817 | -60.8963 | 62.0407 | -61.1526 | 0.045776 | 0.045776 | 0.045776 | -0.15106 | 0.22888 | 0.16022 | -0.32501 | -0.37537 | 0.064086 | -0.11902 | 60.8231 | -61.9308 | 60.4523 | -61.8164 | 0.25635
215.7656 | 123.0469 | -60.8276 | 62.0636 | -0.22343 | 0.018239 | 0.015086 | 0.0032756 | 0.0012615 | 0.002248 | 0.00064087 | -60.8917 | 62.1506 | -61.1389 | 0.045776 | 0.068665 | 0.050354 | 0.1236 | 0.2243 | 0.26093 | -0.23804 | -0.31128 | 0.086975 | -0.064087 | 60.8734 | -61.9949 | 60.5896 | -61.8027 | 0.24719
216.7344 | 123.1613 | -60.7956 | 61.972 | 0.26485 | 0.020162 | 0.018931 | 0.0015666 | 0.0012615 | -0.00031535 | -0.00021353 | -60.8688 | 62.027 | -61.1298 | -0.068665 | 0.009155 | 0.17395 | -0.10529 | 0.22888 | 0.17395 | -0.32501 | -0.33417 | 0.054932 | -0.073242 | 60.7269 | -61.9629 | 60.4706 | -61.7981 | 0.26093
217.7656 | 123.056 | -60.8322 | 62.0682 | -0.19291 | 0.018026 | 0.015299 | 0.0051982 | 0.0010477 | -0.00031535 | -0.00021353 | -60.9512 | 62.1094 | -61.1389 | 0.027466 | -0.045776 | 0.29297 | 0.55389 | 0.054932 | 0.27924 | -0.1236 | -0.3067 | 0.041199 | -0.11902 | 60.8597 | -62.114 | 60.7086 | -61.7889 | 0.18768
218.7344 | 123.1613 | -60.7773 | 61.9949 | 0.28011 | 0.018026 | 0.015727 | 0.0011394 | 0.0023295 | -0.00010175 | -0.00042733 | -60.8643 | 62.0224 | -61.1435 | 0.045776 | 0.032043 | 0.027466 | -0.18768 | 0.20599 | 0.15564 | -0.35706 | -0.36621 | 0.027466 | -0.086975 | 60.8231 | -61.9629 | 60.4202 | -61.8393 | 0.27924
219.7656 | 123.0515 | -60.8047 | 62.0453 | -0.11662 | 0.017598 | 0.017436 | 0.00648 | 0.0016887 | -0.00074255 | 0.00042727 | -60.8871 | 62.1506 | -61.1481 | 0.073242 | 0.054932 | 0.064087 | 0.073242 | 0.27466 | 0.24261 | -0.25177 | -0.34332 | 0.10529 | -0.082397 | 60.878 | -61.9904 | 60.553 | -61.8027 | 0.26093
220.7344 | 123.1155 | -60.7864 | 61.9949 | -1.406 | 0.016103 | 0.01594 | 0.0019938 | 0.0048931 | -0.00074255 | 0.0014953 | -60.8505 | 62.027 | -61.1435 | 0.054932 | 0.027466 | 0.009155 | -0.19684 | 0.21973 | 0.16479 | -0.29755 | -0.35706 | 0.032044 | -0.064087 | 60.8414 | -61.9675 | 60.4889 | -61.8301 | 0.29297
221.7656 | 123.0515 | -60.8093 | 62.027 | 0.11226 | 0.022298 | 0.021067 | 0.007548 | 0.0027567 | 0.00011185 | -0.0014953 | -60.8414 | 62.1231 | -61.1069 | 0.036621 | -0.004578 | -0.004578 | 0.022888 | 0.20142 | 0.21515 | -0.27466 | -0.29755 | 0.09613 | -0.032044 | 60.8459 | -62.0316 | 60.5347 | -61.8118 | 0.2655
222.7344 | 123.1567 | -60.7864 | 61.9995 | 0.25722 | 0.018239 | 0.019358 | -0.0001424 | 0.0031841 | 0.00032545 | -0.00042733 | -60.8734 | 62.0224 | -61.1343 | -0.18768 | -0.23346 | 0.10071 | 0.3067 | 0.37079 | 0.14648 | -0.39825 | -0.3479 | 0.022888 | -0.086975 | 60.5988 | -62.233 | 60.3882 | -61.853 | 0.26093
223.7656 | 123.0331 | -60.7819 | 62.0728 | -0.15477 | 0.017598 | 0.012736 | 0.0015666 | 0.00040688 | -0.00074255 | 0.00064087 | -60.9146 | 62.0911 | -61.1572 | 0.050354 | 0.068665 | 0.09613 | 0.10071 | 0.23346 | 0.25177 | -0.17853 | -0.37537 | 0.01831 | -0.13275 | 60.8322 | -62.0041 | 60.6033 | -61.821 | 0.24262
224.7344 | 123.1384 | -60.7956 | 61.9995 | 0.303 | 0.021016 | 0.014231 | 0.0054118 | 0.0029705 | -0.002238 | -0.0019225 | -60.9055 | 62.0773 | -61.1572 | 0.018311 | -0.013733 | 0.004578 | -0.10986 | 0.17853 | 0.16479 | -0.36621 | -0.36163 | 0.07782 | -0.10986 | 60.8139 | -62.0132 | 60.4294 | -61.8347 | 0.25177
225.7656 | 123.0423 | -60.8139 | 62.0316 | -0.10136 | 0.018239 | 0.014659 | 0.0043436 | 0.0010477 | -0.0011698 | 0.0017091 | -60.9512 | 62.1231 | -61.1664 | 0.013733 | 0.032043 | 0.018311 | 0.13275 | 0.23346 | 0.25177 | -0.21057 | -0.35248 | 0.091553 | -0.13733 | 60.8276 | -61.9995 | 60.6033 | -61.7798 | 0.21515
226.7344 | 123.1247 | -60.7956 | 62.0132 | -0.070844 | 0.019521 | 0.02064 | 7.12e-05 | 0.0016887 | 0.00011185 | 0.0010681 | -60.8826 | 62.0316 | -61.1206 | 0.041199 | 0.045776 | 0.036621 | -0.16022 | 0.22888 | 0.15106 | -0.31586 | -0.32501 | 0.01831 | -0.086975 | 60.8368 | -61.9675 | 60.4797 | -61.8622 | 0.23804
227.7656 | 123.0331 | -60.8139 | 62.059 | -0.36076 | 0.019948 | 0.014018 | 0.00413 | 0.0016887 | 0.0018208 | -0.0012817 | -60.9695 | 62.1323 | -61.1298 | 0.022888 | 0.022888 | 0.027466 | 0.11902 | 0.23804 | 0.25635 | -0.24261 | -0.31586 | 0.073242 | -0.15564 | 60.8368 | -62.0361 | 60.5713 | -61.8027 | 0.16022
228.7344 | 123.1293 | -60.7681 | 62.0087 | -1.4975 | 0.016317 | 0.014659 | 0.0028484 | 0.0042521 | -0.00074255 | -0.00064093 | -60.8002 | 62.027 | -61.1481 | 0.045776 | 0.018311 | 0.004578 | -0.19684 | 0.21973 | 0.1831 | -0.30212 | -0.37994 | 0.018311 | -0.032044 | 60.8139 | -61.9904 | 60.466 | -61.8256 | 0.3479
229.7656 | 123.0652 | -60.791 | 62.0224 | -0.0098092 | 0.020589 | 0.016795 | 0.0094706 | 0.0029705 | -0.00074255 | -0.0012817 | -60.8505 | 62.1414 | -61.1481 | 0.050354 | 0.027466 | 0.036621 | 0.018311 | 0.24261 | 0.23346 | -0.27008 | -0.35706 | 0.11902 | -0.059509 | 60.8414 | -61.9949 | 60.5209 | -61.7889 | 0.29755
230.7344 | 123.1293 | -60.7773 | 61.972 | 0.25722 | 0.01888 | 0.018931 | 0.0026346 | 0.0029705 | 0.00118 | 0.00021367 | -61.0016 | 62.0224 | -61.1526 | 0.12817 | 0.091553 | 0.027466 | -0.17395 | 0.24261 | 0.17853 | -0.31128 | -0.37537 | 0.050354 | -0.2243 | 60.9055 | -61.8805 | 60.466 | -61.7935 | 0.15106
231.7656 | 123.0423 | -60.8002 | 62.0544 | -0.19291 | 0.019094 | 0.017436 | 0.0056254 | 0.0068157 | -0.00052895 | 0.00064087 | -60.9329 | 62.1277 | -61.1618 | 0.09613 | 0.10529 | -0.045776 | 0.018311 | 0.21515 | 0.23804 | -0.20599 | -0.36163 | 0.073243 | -0.13275 | 60.8963 | -61.9492 | 60.5942 | -61.8164 | 0.22888
232.7344 | 123.143 | -60.7727 | 61.9949 | 0.27248 | 0.017385 | 0.020213 | 0.0017802 | 0.0059611 | 0.00118 | 6.6667e-08 | -60.8643 | 62.0087 | -61.1481 | 0.32044 | 0.30212 | -0.018311 | -0.32959 | 0.28839 | 0.14648 | -0.37994 | -0.37537 | 0.013733 | -0.091553 | 61.0931 | -61.6928 | 60.3928 | -61.8484 | 0.28381
233.7656 | 123.0515 | -60.7864 | 62.0499 | -0.1624 | 0.019307 | 0.021708 | 0.0060526 | 0.0012615 | -0.00031535 | 6.6667e-08 | -60.8505 | 62.1368 | -61.1389 | 0.050354 | 0.032043 | 0.045776 | 0.032043 | 0.24719 | 0.24261 | -0.25177 | -0.35248 | 0.086975 | -0.064087 | 60.8368 | -62.0178 | 60.5347 | -61.8073 | 0.28839
234.7344 | 123.1018 | -60.8047 | 61.9812 | 0.2267 | 0.017171 | 0.013163 | 0.0019938 | 0.0033977 | 0.002248 | 0.00085447 | -60.8643 | 62.0316 | -61.1435 | 0.032043 | 0.041199 | 0.041199 | -0.16479 | 0.21515 | 0.1831 | -0.33417 | -0.33874 | 0.050354 | -0.059509 | 60.8368 | -61.94 | 60.4706 | -61.7981 | 0.27924
235.7656 | 123.0515 | -60.8322 | 62.0544 | -0.093733 | 0.021871 | 0.016795 | 0.0069072 | 0.0029705 | -0.0033062 | 0.00042727 | -60.8505 | 62.1552 | -61.116 | 0.073242 | 0.054932 | 0.045776 | 0.041199 | 0.26093 | 0.24261 | -0.25177 | -0.28381 | 0.10071 | -0.018311 | 60.9055 | -61.9995 | 60.5804 | -61.8118 | 0.2655
236.7344 | 123.111 | -60.7956 | 62.0132 | 0.14278 | 0.020589 | 0.017649 | 0.0004984 | 0.0044657 | -0.0033062 | 6.6667e-08 | -60.8734 | 62.0224 | -61.1298 | 0.045776 | 0.041199 | 0.041199 | -0.17853 | 0.21515 | 0.15564 | -0.32044 | -0.33417 | 0.009155 | -0.07782 | 60.8414 | -61.972 | 60.4752 | -61.8576 | 0.25635
237.7656 | 123.0286 | -60.8231 | 62.0865 | -0.17766 | 0.018239 | 0.014231 | 0.002421 | 0.0010477 | 0.00032545 | 0.00064087 | -60.9512 | 62.0956 | -61.1526 | 0.018311 | 0.018311 | 0.050354 | 0.14648 | 0.25177 | 0.27008 | -0.19226 | -0.32959 | 0.009155 | -0.12817 | 60.8414 | -62.0682 | 60.6308 | -61.8164 | 0.20142
238.75 | 123.0652 | -60.8139 | 62.0544 | -0.14714 | 0.022298 | 0.017863 | 0.0084026 | 0.0048931 | -0.00074255 | -0.00064093 | -60.8414 | 62.1277 | -61.1252 | 0.041199 | 0.009155 | 0.059509 | 0.041199 | 0.24261 | 0.26093 | -0.27008 | -0.31128 | 0.073243 | -0.027466 | 60.8551 | -62.0453 | 60.5438 | -61.7935 | 0.28381
239.7656 | 123.056 | -60.8139 | 62.0682 | 1.6534 | 0.02358 | 0.018717 | 0.0051982 | 0.0042521 | -0.00010175 | -0.00085453 | -60.8368 | 62.1231 | -61.1618 | 0.032043 | 0.036621 | 0.032043 | 0.018311 | 0.19684 | 0.2243 | -0.26093 | -0.3479 | 0.054932 | -0.022888 | 60.8459 | -62.0316 | 60.553 | -61.8439 | 0.32501
240.7344 | 123.1338 | -60.7864 | 62.0178 | 0.23433 | 0.019094 | 0.021067 | -0.0014242 | 0.0051067 | 0.00032545 | 0.0012817 | -60.8643 | 62.0361 | -61.1526 | 0.036621 | 0.032043 | 0.022888 | -0.16022 | 0.23804 | 0.15564 | -0.34332 | -0.36621 | 0.018311 | -0.07782 | 60.8231 | -61.9858 | 60.4431 | -61.8622 | 0.28839
241.7656 | 123.0606 | -60.7864 | 62.0499 | -0.1624 | 0.019948 | 0.015299 | 0.007548 | 0.0019023 | -0.0026652 | 0.00021367 | -60.878 | 62.1323 | -61.1389 | 0.059509 | 0.054932 | 0.059509 | 0.059509 | 0.2655 | 0.24261 | -0.23804 | -0.35248 | 0.082397 | -0.091553 | 60.8459 | -61.9949 | 60.5484 | -61.8073 | 0.26093
242.7344 | 123.1338 | -60.8002 | 62.0041 | 1.7297 | 0.018667 | 0.016795 | 0.0004984 | 0.0023295 | -0.00052895 | 0.0012817 | -60.8871 | 62.0407 | -61.1572 | 0.059509 | 0.036621 | 0.050354 | -0.18768 | 0.18768 | 0.15106 | -0.30212 | -0.35706 | 0.036621 | -0.086975 | 60.8597 | -61.9675 | 60.498 | -61.853 | 0.27008
243.7656 | 123.1384 | -60.791 | 61.9995 | 0.27248 | 0.019094 | 0.017649 | 0.0022074 | 0.0038249 | -0.0015972 | 0.00064087 | -60.8597 | 62.027 | -61.1435 | 0.059509 | 0.045776 | 0.032043 | -0.20142 | 0.21515 | 0.14648 | -0.35706 | -0.35248 | 0.027466 | -0.068664 | 60.8505 | -61.9537 | 60.434 | -61.853 | 0.28381
244.7344 | 123.1201 | -60.7773 | 61.9858 | 0.28774 | 0.019948 | 0.021067 | 0.0022074 | 0.0031841 | 0.00053925 | 0.0019227 | -60.8597 | 62.0316 | -61.1389 | 0.036621 | 0.032043 | 0.045776 | -0.20142 | 0.2243 | 0.17395 | -0.36163 | -0.36163 | 0.045776 | -0.082397 | 60.8139 | -61.9537 | 60.4156 | -61.8118 | 0.27924
245.7656 | 123.0515 | -60.8002 | 62.0316 | -0.15477 | 0.020376 | 0.019145 | 0.0066936 | 0.0014751 | -0.0020244 | -0.00064093 | -60.878 | 62.1368 | -61.1298 | 0.045776 | 0.041199 | 0.054932 | 0.068665 | 0.26093 | 0.26093 | -0.22888 | -0.32959 | 0.10529 | -0.07782 | 60.8459 | -61.9904 | 60.5713 | -61.7706 | 0.25177
246.7344 | 123.143 | -60.791 | 62.0087 | 0.45558 | 0.020589 | 0.021495 | 0.0039164 | 0.0048931 | -0.0011698 | -0.00064093 | -60.8734 | 62.0773 | -61.1481 | 0.050354 | 0.022888 | 0.018311 | -0.1831 | 0.20142 | 0.16022 | -0.36621 | -0.35706 | 0.068665 | -0.082397 | 60.8414 | -61.9858 | 60.4248 | -61.8484 | 0.27466
247.7656 | 123.111 | -60.7636 | 62.0224 | 0.058855 | 0.016744 | 0.01829 | -0.002065 | 0.0014751 | -0.00010175 | 0.00021367 | -60.8597 | 62.0407 | -61.1114 | 0.10071 | 0.1236 | 0.15564 | -0.032043 | 0.32959 | 0.21057 | -0.21057 | -0.3479 | 0.01831 | -0.09613 | 60.8643 | -61.8988 | 60.553 | -61.8118 | 0.25177
248.75 | 123.0972 | -60.791 | 62.0361 | -0.063215 | 0.017812 | 0.017436 | -0.0001424 | 0.00019328 | -0.0024516 | -0.00064093 | -60.8643 | 62.0453 | -61.1114 | 0.10529 | 0.09613 | 0.13275 | 0.027466 | 0.33875 | 0.25177 | -0.20599 | -0.32043 | 0.009155 | -0.073242 | 60.8963 | -61.94 | 60.585 | -61.7844 | 0.24719
249.7656 | 123.0103 | -60.8093 | 62.0728 | -0.13951 | 0.018239 | 0.021067 | 0.00413 | 0.0048931 | 0.00075285 | -0.00085453 | -60.9146 | 62.1368 | -61.1298 | 0.07782 | 0.11444 | -0.009155 | 0.009155 | 0.18768 | 0.2655 | -0.19684 | -0.32044 | 0.064087 | -0.10529 | 60.8871 | -61.9583 | 60.6125 | -61.8073 | 0.21515
250.7344 | 123.1476 | -60.8002 | 62.0041 | 0.24196 | 0.019735 | 0.014445 | 0.0045574 | 0.0040385 | -0.00074255 | -0.0014953 | -60.8826 | 62.0728 | -61.1252 | 0.032043 | -0.022888 | -0.045776 | -0.18768 | 0.21973 | 0.15564 | -0.36621 | -0.32501 | 0.068665 | -0.082397 | 60.8322 | -62.027 | 60.434 | -61.8484 | 0.24262
251.7656 | 123.143 | -60.7819 | 61.9995 | 0.21144 | 0.020376 | 0.02064 | 0.0073344 | 0.0023295 | -0.00031535 | 0.0010681 | -60.8597 | 62.059 | -61.1343 | 0.050354 | 0.045776 | 0.009155 | -0.20599 | 0.20142 | 0.15106 | -0.35248 | -0.35248 | 0.059509 | -0.07782 | 60.8322 | -61.9537 | 60.4294 | -61.8484 | 0.27466
252.7344 | 123.0698 | -60.8093 | 62.0132 | 0.23433 | 0.022298 | 0.016581 | 0.0043436 | 0.0033977 | -0.00095615 | 0.00064087 | -60.9055 | 62.1048 | -61.1847 | -0.018311 | -0.032043 | -0.050354 | -0.12817 | 0.12817 | 0.17853 | -0.32501 | -0.37537 | 0.091552 | -0.096131 | 60.791 | -62.0453 | 60.4843 | -61.8347 | 0.27923
253.7656 | 123.0972 | -60.7773 | 62.0132 | -0.093733 | 0.017171 | 0.015299 | -0.0009968 | 0.00040688 | -0.00010175 | 6.6667e-08 | -60.8871 | 62.0407 | -61.1298 | 0.10071 | 0.10529 | 0.14191 | 0.045776 | 0.3479 | 0.25177 | -0.21057 | -0.35248 | 0.027465 | -0.10986 | 60.878 | -61.908 | 60.5667 | -61.7615 | 0.24262
254.7344 | 123.0286 | -60.8368 | 62.0361 | 0.27248 | 0.022298 | 0.018717 | 0.0086162 | 0.0027567 | 0.00075285 | 0.0017091 | -60.9192 | 62.1277 | -61.1343 | -0.045776 | -0.045776 | -0.064087 | -0.059509 | 0.091553 | 0.18768 | -0.33417 | -0.29755 | 0.091553 | -0.082397 | 60.791 | -62.0819 | 60.5026 | -61.8484 | 0.21515
255.7656 | 123.1064 | -60.7636 | 62.0361 | 0.37166 | 0.016744 | 0.012522 | -0.0014242 | 0.00083408 | -0.00052895 | 0.00021367 | -60.8047 | 62.0453 | -61.1252 | 0.10986 | 0.15106 | 0.16937 | -0.036621 | 0.37079 | 0.2243 | -0.2243 | -0.36163 | 0.009155 | -0.041199 | 60.8734 | -61.8851 | 60.5392 | -61.8118 | 0.32043
256.7344 | 123.024 | -60.8459 | 62.0544 | 0.21144 | 0.02123 | 0.019358 | 0.010966 | 0.00019328 | 0.00032545 | -0.0012817 | -60.9238 | 62.1185 | -61.1526 | -0.018311 | -0.21973 | -0.10986 | 0.18768 | 0.13275 | 0.21973 | -0.32044 | -0.3067 | 0.064087 | -0.07782 | 60.8276 | -62.2742 | 60.5255 | -61.8347 | 0.22888
257.7656 | 123.1567 | -60.7819 | 61.9995 | -0.040327 | 0.013753 | 0.014231 | -0.0024922 | -2.0324e-05 | 0.00011185 | 6.6667e-08 | -60.91 | 62.0316 | -61.1343 | 0.09613 | 0.10071 | 0.15564 | -0.064087 | 0.32959 | 0.21515 | -0.2243 | -0.35248 | 0.032043 | -0.12817 | 60.878 | -61.8988 | 60.5576 | -61.7844 | 0.2243
258.7344 | 123.0606 | -60.8231 | 62.027 | 0.24959 | 0.022939 | 0.01829 | 0.009257 | 0.0021159 | 0.0016072 | -0.0014953 | -60.9238 | 62.1414 | -61.1618 | -0.036621 | -0.059509 | -0.082397 | -0.018311 | 0.10529 | 0.20599 | -0.33417 | -0.33874 | 0.11444 | -0.10071 | 60.7864 | -62.0865 | 60.4889 | -61.821 | 0.23804
259.7656 | 123.1338 | -60.7636 | 62.0499 | -0.0098092 | 0.017171 | 0.015727 | -0.0024922 | 0.00040688 | 0.00011185 | 0.0025635 | -60.9329 | 62.0224 | -61.1252 | 0.07782 | 0.086975 | 0.082397 | -0.059509 | 0.29755 | 0.20142 | -0.26093 | -0.36163 | -0.027466 | -0.16937 | 60.8414 | -61.9629 | 60.5026 | -61.8484 | 0.19226
260.7344 | 123.1338 | -60.8414 | 62.0544 | 0.2267 | 0.021016 | 0.019358 | 0.010325 | 0.0014751 | 0.00011185 | -0.00021353 | -60.9238 | 62.1277 | -61.1343 | -0.045776 | -0.059509 | -0.10529 | -0.022888 | -0.32959 | 0.1831 | -0.39368 | -0.29297 | 0.073243 | -0.082397 | 60.7956 | -62.114 | 60.4477 | -61.8713 | 0.21057
261.75 | 123.1613 | -60.7407 | 62.027 | -0.10899 | 0.017812 | 0.018931 | -0.0027058 | 0.00019328 | 0.00096645 | 0.00085447 | -60.8734 | 62.0087 | -61.116 | 0.13275 | 0.15106 | 0.18768 | -0.064087 | 0.37994 | 0.21973 | -0.20142 | -0.37537 | -0.018311 | -0.13275 | 60.8734 | -61.8759 | 60.5392 | -61.8073 | 0.24262
262.7344 | 123.024 | -60.8185 | 62.0453 | 0.21907 | 0.022939 | 0.020854 | 0.010112 | 0.0040385 | -0.00010175 | 0.00064087 | -61.1801 | 62.0865 | -61.1664 | 0.009155 | -0.068665 | -0.073242 | 0.009155 | 0.10071 | 0.22888 | -0.29755 | -0.3479 | 0.041199 | -0.36163 | 60.8276 | -62.114 | 60.5209 | -61.8164 | -0.013733
263.7656 | 123.1293 | -60.759 | 62.0361 | 0.020708 | 0.016103 | 0.015727 | -0.0035604 | 0.00062048 | 0.00053925 | 0.00042727 | -60.9467 | 62.0178 | -61.1389 | 0.054932 | 0.073242 | 0.10071 | -0.059509 | 0.27924 | 0.21515 | -0.24719 | -0.37994 | -0.018311 | -0.18768 | 60.8139 | -61.9629 | 60.5118 | -61.821 | 0.19226
264.7344 | 123.0148 | -60.8368 | 62.0316 | 0.24196 | 0.021444 | 0.017649 | 0.0081888 | 0.0033977 | 0.00011185 | -0.0027771 | -60.9375 | 62.114 | -61.1252 | -0.027466 | -0.068665 | -0.10071 | -0.022888 | 0.10071 | 0.21057 | -0.33417 | -0.28839 | 0.082398 | -0.10071 | 60.8093 | -62.1002 | 60.5026 | -61.821 | 0.18768
265.7656 | 123.175 | -60.7636 | 62.0178 | -0.11662 | 0.018026 | 0.012736 | -0.0009968 | 0.0010477 | -0.002238 | 0.00042727 | -60.8597 | 62.0087 | -61.1069 | 0.14648 | 0.13275 | 0.17395 | -0.027466 | 0.37079 | 0.21515 | -0.21057 | -0.34332 | -0.009155 | -0.09613 | 60.91 | -61.8851 | 60.553 | -61.8027 | 0.24719
266.7344 | 123.0194 | -60.8139 | 62.0407 | 0.028338 | 0.022085 | 0.020213 | 0.0084026 | 0.0040385 | 0.0020344 | 0.0017091 | -60.8597 | 62.146 | -61.1252 | -0.004578 | -0.041199 | -0.027466 | 0.004578 | 0.17395 | 0.20599 | -0.31128 | -0.31128 | 0.10529 | -0.045776 | 60.8093 | -62.0819 | 60.5026 | -61.8347 | 0.2655
267.75 | 123.1338 | -60.7773 | 62.0178 | -0.025068 | 0.015035 | 0.014659 | -0.003774 | -0.00066112 | -0.00031535 | 0.00085447 | -60.9055 | 62.0224 | -61.1435 | 0.07782 | 0.09613 | 0.1236 | -0.068665 | 0.3067 | 0.21057 | -0.22888 | -0.36621 | 0.004578 | -0.12817 | 60.8551 | -61.9217 | 60.5484 | -61.8073 | 0.23804
268.7344 | 123.024 | -60.8368 | 62.0453 | 0.21907 | 0.023794 | 0.024699 | 0.0088298 | 0.0033977 | 0.0018208 | -0.0017089 | -60.9238 | 62.1597 | -61.1526 | -0.036621 | -0.050354 | -0.082397 | 0 | 0.086975 | 0.20142 | -0.33875 | -0.31586 | 0.11444 | -0.086975 | 60.8002 | -62.0956 | 60.498 | -61.8439 | 0.22888
269.7656 | 123.0606 | -60.7819 | 62.0453 | -0.20054 | 0.018453 | 0.015727 | 0.0002848 | 0.0012615 | -0.0011698 | -0.00021353 | -60.91 | 62.0819 | -61.1389 | 0.07782 | 0.07782 | 0.11444 | 0.068665 | 0.29755 | 0.22888 | -0.21057 | -0.35706 | 0.036621 | -0.12817 | 60.8597 | -61.9675 | 60.5713 | -61.8164 | 0.22888
270.7344 | 122.9965 | -60.8322 | 62.0544 | 0.12752 | 0.021016 | 0.017649 | 0.010325 | 0.0033977 | 0.00096645 | -0.0010681 | -60.9055 | 62.1368 | -61.1526 | -0.041199 | -0.054932 | -0.09613 | -0.018311 | 0.059509 | 0.22888 | -0.34332 | -0.32043 | 0.082398 | -0.073243 | 60.791 | -62.1094 | 60.4889 | -61.8256 | 0.24719
271.7656 | 123.1293 | -60.759 | 62.0224 | 0.043596 | 0.016317 | 0.014872 | -0.0027058 | 0.0014751 | 0.0020344 | 0.0014953 | -60.9512 | 62.0041 | -61.1572 | 0.032043 | 0.07782 | 0.073242 | -0.064087 | 0.28839 | 0.20599 | -0.27466 | -0.39825 | -0.018311 | -0.19226 | 60.791 | -61.9446 | 60.4843 | -61.8164 | 0.20599
272.7344 | 123.0469 | -60.8322 | 62.027 | 0.1733 | 0.021444 | 0.016154 | 0.0060526 | 0.0033977 | 0.0016072 | 0.0012817 | -60.8414 | 62.1277 | -61.1114 | 0.041199 | 0.004578 | 0.018311 | 0.018311 | 0.21057 | 0.2243 | -0.27466 | -0.27924 | 0.10071 | -0.009156 | 60.8734 | -62.0224 | 60.5576 | -61.8027 | 0.27008
273.75 | 123.143 | -60.7956 | 61.9949 | 0.24959 | 0.019307 | 0.015513 | 0.0019938 | 0.00062048 | -0.00010175 | 0.0012817 | -60.8505 | 62.0499 | -61.1435 | -0.059509 | -0.25635 | -0.20142 | 0.26093 | 0.51727 | 0.14648 | -0.41199 | -0.3479 | 0.054932 | -0.054932 | 60.7361 | -62.2513 | 60.3836 | -61.8484 | 0.29297
274.7344 | 123.0103 | -60.8459 | 62.0407 | 0.11989 | 0.019735 | 0.021708 | 0.0079752 | 0.0033977 | 0.00032545 | -0.0021361 | -60.9283 | 62.1552 | -61.1801 | -0.050354 | -0.068665 | -0.10071 | 0.009155 | 0.07782 | 0.20599 | -0.33417 | -0.33417 | 0.11444 | -0.082398 | 60.7956 | -62.1094 | 60.5118 | -61.8347 | 0.25177
275.7656 | 123.1338 | -60.7773 | 61.9995 | -0.19291 | 0.015462 | 0.012522 | -0.0031332 | 0.0044657 | -0.0030924 | 0.00085447 | -60.878 | 62.0316 | -61.1298 | 0.10986 | -0.3067 | -0.30212 | 0.10529 | 0.44403 | 0.24261 | -0.20599 | -0.35248 | 0.032043 | -0.10071 | 60.8871 | -62.3062 | 60.5713 | -61.7569 | 0.25177
276.7344 | 123.0286 | -60.8551 | 62.0361 | 0.13515 | 0.02123 | 0.021281 | 0.010112 | 0.0021159 | -0.00052895 | -0.0025635 | -60.8917 | 62.1597 | -61.1252 | -0.041199 | -0.050354 | -0.07782 | 0.013733 | 0.10986 | 0.20599 | -0.35248 | -0.27008 | 0.1236 | -0.036621 | 60.8139 | -62.0865 | 60.5026 | -61.8301 | 0.23346
277.75 | 123.1476 | -60.7819 | 62.0041 | 1.7068 | 0.017598 | 0.02064 | 0.0019938 | 0.0029705 | -0.0011698 | 0.00021367 | -60.8459 | 62.0087 | -61.1481 | 0.045776 | 0.054932 | 0.059509 | -0.2243 | 0.18768 | 0.15564 | -0.28839 | -0.36621 | 0.004578 | -0.064087 | 60.8276 | -61.9492 | 60.4935 | -61.8484 | 0.30212
278.7344 | 123.0011 | -60.8231 | 62.0544 | 0.097002 | 0.021016 | 0.019145 | 0.009257 | 0.0027567 | 0.00118 | -0.00042733 | -60.8871 | 62.1368 | -61.1435 | -0.027466 | -0.027466 | -0.027466 | 0.018311 | 0.14191 | 0.21515 | -0.31128 | -0.32043 | 0.082398 | -0.064087 | 60.7956 | -62.0819 | 60.5118 | -61.8393 | 0.25635
279.7656 | 123.1247 | -60.7773 | 62.0087 | -0.017439 | 0.014821 | 0.014659 | -0.0027058 | 0.0027567 | -0.00010175 | 0.0021363 | -60.9146 | 62.0224 | -61.1481 | 0.073242 | 0.091553 | 0.10071 | -0.07782 | 0.3067 | 0.21515 | -0.23804 | -0.37079 | 0.013733 | -0.13733 | 60.8505 | -61.9171 | 60.5392 | -61.7935 | 0.23346
280.7344 | 123.0011 | -60.8414 | 62.0499 | 0.081743 | 0.022939 | 0.017863 | 0.0090434 | 0.0033977 | 0.00032545 | -0.0014953 | -60.8688 | 62.1368 | -61.1389 | 0.004578 | -0.018311 | -0.041199 | 0.032043 | 0.16022 | 0.20142 | -0.31586 | -0.29755 | 0.086975 | -0.027465 | 60.8459 | -62.0682 | 60.5255 | -61.8484 | 0.27008
281.7656 | 123.1705 | -60.7544 | 62.0132 | -0.047956 | 0.013967 | 0.017649 | -0.0027058 | -0.0017293 | 0.00011185 | 0.0021363 | -60.8917 | 62.027 | -61.1298 | 0.09613 | 0.14648 | 0.16937 | -0.041199 | 0.37537 | 0.21973 | -0.18768 | -0.37537 | 0.013733 | -0.13733 | 60.8505 | -61.8668 | 60.5667 | -61.7935 | 0.23804
282.7344 | 123.0148 | -60.8276 | 62.0361 | 0.081743 | 0.020589 | 0.020854 | 0.0077616 | 0.0027567 | 0.00075285 | -0.0010681 | -60.8917 | 62.1506 | -61.1389 | -0.054932 | -0.059509 | -0.086975 | 0.027466 | 0.086975 | 0.21515 | -0.34332 | -0.31128 | 0.11444 | -0.064087 | 60.7727 | -62.0956 | 60.4843 | -61.821 | 0.24719
283.7656 | 123.0835 | -60.7956 | 62.0178 | 0.21907 | 0.017385 | 0.016154 | -0.000356 | 0.0033977 | -0.00031535 | -0.00042733 | -60.9467 | 62.0132 | -61.1618 | -0.004578 | 0.009155 | 0.027466 | -0.11902 | 0.18768 | 0.16479 | -0.29755 | -0.36621 | -0.004577 | -0.15106 | 60.791 | -62.0087 | 60.498 | -61.853 | 0.21515
284.7344 | 123.0057 | -60.8322 | 62.027 | 0.11989 | 0.022298 | 0.019999 | 0.0081888 | 0.0021159 | -0.0026652 | -0.0017089 | -60.9055 | 62.1689 | -61.1298 | -0.045776 | -0.068665 | -0.064087 | 0.032043 | 0.10071 | 0.20599 | -0.32501 | -0.29755 | 0.14191 | -0.073243 | 60.7864 | -62.0956 | 60.5072 | -61.821 | 0.2243
285.75 | 123.1018 | -60.791 | 61.9949 | 0.2267 | 0.016744 | 0.018077 | -0.0035604 | 0.0014751 | 0.0024618 | 0.00021367 | -60.9283 | 62.0087 | -61.1389 | -0.009155 | 0.027466 | 0.013733 | -0.11902 | 0.20142 | 0.17395 | -0.3067 | -0.3479 | 0.013733 | -0.13733 | 60.7819 | -61.9675 | 60.4843 | -61.821 | 0.21057
286.7344 | 123.0469 | -60.8002 | 62.0407 | 0.020708 | 0.020589 | 0.017649 | 0.0081888 | 0.0025431 | 0.00011185 | -0.0010681 | -60.8597 | 62.1643 | -61.1069 | 0.036621 | 0.009155 | 0.009155 | 0.009155 | 0.21057 | 0.22888 | -0.31128 | -0.3067 | 0.1236 | -0.059509 | 60.8368 | -62.0316 | 60.4889 | -61.8118 | 0.24719
287.7656 | 123.1201 | -60.7773 | 62.027 | -0.086103 | 0.016958 | 0.01829 | -0.0009968 | 0.0027567 | 0.00096645 | -0.0032043 | -60.8917 | 62.0224 | -61.1389 | 0.10529 | 0.11902 | 0.15106 | 0.022888 | 0.34332 | 0.24719 | -0.19684 | -0.36163 | -0.004578 | -0.11444 | 60.8826 | -61.908 | 60.5804 | -61.7798 | 0.24719
288.7344 | 123.0194 | -60.8597 | 62.0316 | 0.24959 | 0.021871 | 0.015513 | 0.0084026 | 0.0027567 | 0.00118 | 0.00021367 | -60.9375 | 62.1231 | -61.1389 | -0.045776 | -0.068665 | -0.10071 | -0.004578 | 0.082397 | 0.20599 | -0.33875 | -0.27924 | 0.091553 | -0.07782 | 60.8139 | -62.1002 | 60.5209 | -61.8256 | 0.20142
289.7656 | 123.1522 | -60.7819 | 62.0041 | -0.13188 | 0.015889 | 0.013804 | -0.0024922 | 0.00019328 | -0.0013834 | 0.00042727 | -60.8643 | 62.0499 | -61.1343 | 0.11444 | 0.14191 | 0.15564 | -0.041199 | 0.35706 | 0.2243 | -0.19226 | -0.35248 | 0.045777 | -0.082398 | 60.8963 | -61.8622 | 60.5896 | -61.7798 | 0.27008
290.7344 | 123.0103 | -60.8322 | 62.0224 | 0.19618 | 0.02123 | 0.02534 | 0.009257 | 0.0036113 | -0.00095615 | -0.00085453 | -60.9329 | 62.1414 | -61.171 | -0.068665 | -0.091553 | -0.11444 | -0.018311 | 0.10071 | 0.17853 | -0.35248 | -0.33875 | 0.11902 | -0.10071 | 60.7635 | -62.114 | 60.4797 | -61.8439 | 0.23804
291.7656 | 123.1567 | -60.7956 | 62.0178 | -0.0098092 | 0.016744 | 0.01594 | -0.0042012 | 0.0023295 | -0.00074255 | -0.0017089 | -60.9329 | 62.027 | -61.1435 | 0.073242 | 0.091553 | 0.10529 | -0.068665 | 0.29297 | 0.20599 | -0.23346 | -0.3479 | 0.009156 | -0.13733 | 60.8688 | -61.9263 | 60.5621 | -61.8118 | 0.21057
292.7344 | 123.0011 | -60.8185 | 62.0316 | 0.11226 | 0.020589 | 0.019145 | 0.0079752 | 0.0019023 | -0.0011698 | -0.00085453 | -60.9146 | 62.1277 | -61.1343 | -0.054932 | -0.059509 | -0.09613 | 0.009155 | 0.07782 | 0.21057 | -0.36621 | -0.31586 | 0.096131 | -0.096131 | 60.7635 | -62.0911 | 60.4523 | -61.821 | 0.21973
293.7656 | 123.1338 | -60.7864 | 62.0224 | 0.11226 | 0.015889 | 0.014872 | -0.0024922 | 0.0010477 | 0.0013936 | 0.0010681 | -60.9375 | 62.0407 | -61.1801 | 0.013733 | 0.045776 | 0.045776 | -0.082397 | 0.24261 | 0.17395 | -0.27924 | -0.39368 | 0.01831 | -0.15106 | 60.8002 | -61.9766 | 60.5072 | -61.8484 | 0.24262
294.7344 | 123.0194 | -60.8093 | 62.0224 | 0.15804 | 0.021871 | 0.02064 | 0.0071208 | 0.0014751 | 0.00011185 | -0.0017089 | -60.91 | 62.1323 | -61.1389 | -0.027466 | -0.064087 | -0.073242 | 0.018311 | 0.10529 | 0.19684 | -0.31128 | -0.32959 | 0.10986 | -0.10071 | 60.7819 | -62.0865 | 60.498 | -61.8256 | 0.22888
295.7656 | 123.0927 | -60.7864 | 62.0361 | 0.23433 | 0.017598 | 0.018931 | -0.0007832 | -0.0010885 | -0.00052895 | 0.0012817 | -60.9512 | 62.0499 | -61.1481 | 0.018311 | 0.064087 | 0.050354 | -0.068665 | 0.25177 | 0.18768 | -0.26093 | -0.36163 | 0.013733 | -0.1648 | 60.8047 | -61.972 | 60.5255 | -61.8484 | 0.19684
296.7344 | 123.024 | -60.8276 | 62.0224 | 0.10463 | 0.022939 | 0.014872 | 0.0090434 | 0.0027567 | 0.0018208 | -0.00064093 | -60.8734 | 62.146 | -61.1435 | -0.004578 | -0.045776 | -0.050354 | 0.004578 | 0.15106 | 0.21057 | -0.30212 | -0.31586 | 0.1236 | -0.045776 | 60.8231 | -62.0682 | 60.5255 | -61.8118 | 0.27008
297.7656 | 123.0972 | -60.7773 | 62.0041 | 0.089373 | 0.014821 | 0.017008 | -0.0035604 | 0.00040688 | 0.00011185 | 0.0023499 | -60.9558 | 62.0132 | -61.1435 | -0.12817 | -0.036621 | 0.027466 | -0.054932 | 0.21973 | 0.21057 | -0.26093 | -0.36621 | 0.009156 | -0.17853 | 60.6491 | -62.0407 | 60.5164 | -61.7935 | 0.18768
298.7344 | 122.9919 | -60.8322 | 62.0453 | 0.11989 | 0.021871 | 0.019786 | 0.0051982 | 0.0031841 | 0.00053925 | 0.0010681 | -60.9146 | 62.1506 | -61.1343 | -0.050354 | -0.064087 | -0.10529 | 0.004578 | 0.073242 | 0.21057 | -0.3479 | -0.30212 | 0.10529 | -0.082398 | 60.7819 | -62.1094 | 60.4843 | -61.8347 | 0.21973
299.7656 | 123.0835 | -60.7864 | 61.9675 | 0.2267 | 0.019735 | 0.018717 | 0.0054118 | 0.0048931 | -0.0013834 | -0.0017089 | -60.8871 | 62.0819 | -61.1481 | 0.032043 | 0.009155 | 0.004578 | -0.15564 | 0.17853 | 0.16022 | -0.36163 | -0.36163 | 0.11444 | -0.10071 | 60.8185 | -61.9583 | 60.4248 | -61.8073 | 0.26093
300.7344 | 123.0515 | -60.8047 | 62.0407 | -0.025068 | 0.021871 | 0.020854 | 0.0062662 | 0.0046793 | -0.00031535 | -0.00042733 | -60.8505 | 62.1323 | -61.1526 | 0.032043 | 0.027466 | 0.004578 | 0.018311 | 0.21515 | 0.23346 | -0.26093 | -0.3479 | 0.091553 | -0.045776 | 60.8368 | -62.0132 | 60.5438 | -61.8073 | 0.30212
301.7656 | 123.143 | -60.7681 | 62.027 | 0.38692 | 0.014821 | 0.021708 | -0.0046284 | 0.0021159 | -0.0011698 | -0.00042733 | -60.8917 | 62.0178 | -61.1618 | 0.11902 | 0.13275 | 0.16022 | -0.013733 | 0.3479 | 0.22888 | -0.21515 | -0.39368 | -0.009156 | -0.1236 | 60.8871 | -61.8942 | 60.553 | -61.7981 | 0.27008
302.7344 | 122.9874 | -60.8368 | 62.0361 | 0.19618 | 0.020589 | 0.017436 | 0.0081888 | 0.0029705 | 0.0013936 | 0.0012817 | -60.9192 | 62.1231 | -61.1389 | -0.054932 | -0.07782 | -0.10529 | 0.022888 | 0.09613 | 0.21515 | -0.34332 | -0.30212 | 0.086975 | -0.082397 | 60.7819 | -62.114 | 60.4935 | -61.821 | 0.21973
303.7656 | 123.0927 | -60.759 | 62.0544 | -0.17003 | 0.016958 | 0.016581 | -0.0016378 | 0.0016887 | 0.00032545 | -0.00021353 | -60.878 | 62.027 | -61.1343 | 0.10529 | 0.10529 | 0.13733 | 0.045776 | 0.33875 | 0.2655 | -0.18768 | -0.37537 | -0.027465 | -0.11902 | 60.8643 | -61.9492 | 60.5713 | -61.7889 | 0.25635
304.7344 | 123.1018 | -60.7819 | 61.9949 | 0.2267 | 0.018026 | 0.016154 | -0.000356 | 0.0023295 | 0.00118 | 0.0014953 | -60.8826 | 62.0224 | -61.1343 | 0.027466 | 0.041199 | 0.018311 | -0.17853 | 0.19684 | 0.16479 | -0.34332 | -0.35248 | 0.027466 | -0.10071 | 60.8093 | -61.9537 | 60.4385 | -61.8301 | 0.25177
305.75 | 123.143 | -60.7636 | 61.9995 | 0.24959 | 0.018667 | 0.019786 | 0.0026346 | 0.0019023 | 0.00096645 | 0.00064087 | -60.8505 | 62.0132 | -61.1298 | -0.20142 | -0.009155 | 0.45776 | 0.018311 | 0.15106 | 0.15564 | -0.40741 | -0.36621 | 0.013733 | -0.086975 | 60.5621 | -62.0087 | 60.3561 | -61.8439 | 0.27924
306.7344 | 123.0331 | -60.8093 | 62.0224 | 0.089373 | 0.021016 | 0.019786 | 0.0088298 | 0.0033977 | -0.0018108 | -0.00085453 | -60.8597 | 62.146 | -61.1389 | 0.004578 | -0.032043 | -0.018311 | 0.004578 | 0.14191 | 0.21973 | -0.29755 | -0.32959 | 0.1236 | -0.050354 | 60.8139 | -62.0544 | 60.5118 | -61.8027 | 0.27924
307.7656 | 123.1201 | -60.8002 | 61.9995 | 0.074114 | 0.015889 | 0.016154 | -0.0050558 | 0.00062048 | 0.00032545 | -0.0021361 | -60.9467 | 62.0132 | -61.1526 | 0.073242 | 0.082397 | 0.10071 | -0.059509 | 0.28381 | 0.21515 | -0.24261 | -0.35248 | 0.013733 | -0.14648 | 60.8734 | -61.9171 | 60.5576 | -61.7844 | 0.20599
308.7344 | 123.0469 | -60.791 | 62.0407 | 0.020708 | 0.020162 | 0.016795 | 0.010752 | 0.0036113 | -0.0015972 | 0.00042727 | -60.8368 | 62.1414 | -61.1343 | 0.032043 | 0.018311 | 0.013733 | 0.018311 | 0.18768 | 0.2243 | -0.29297 | -0.34332 | 0.10071 | -0.045776 | 60.8231 | -62.0224 | 60.498 | -61.8164 | 0.29755
309.7656 | 123.1338 | -60.8139 | 61.9949 | 0.32588 | 0.01888 | 0.017649 | 0.0039164 | 0.0023295 | 0.00053925 | -0.0010681 | -60.8551 | 62.0499 | -61.1664 | 0.054932 | 0.032043 | 0.022888 | -0.20142 | 0.20142 | 0.14648 | -0.35706 | -0.35248 | 0.054932 | -0.041199 | 60.8688 | -61.9629 | 60.4568 | -61.8484 | 0.31128
310.7344 | 123.0423 | -60.8276 | 62.0407 | 0.11226 | 0.019735 | 0.018931 | 0.0086162 | 0.0040385 | -0.00031535 | -0.0014953 | -60.8826 | 62.1277 | -61.1572 | -0.004578 | -0.022888 | -0.027466 | 0.013733 | 0.14648 | 0.2243 | -0.30212 | -0.32959 | 0.086976 | -0.054931 | 60.8231 | -62.0636 | 60.5255 | -61.8164 | 0.27466
311.7656 | 123.0194 | -60.8047 | 62.0453 | -0.070844 | 0.016103 | 0.016368 | 0.0004984 | 0.0033977 | -0.0011698 | 0.00042727 | -60.9421 | 62.1185 | -61.1481 | 0.009155 | 0.027466 | 0.045776 | 0.14648 | 0.24261 | 0.29755 | -0.1831 | -0.34332 | 0.073242 | -0.13733 | 60.8139 | -62.0178 | 60.6216 | -61.7477 | 0.20599
312.7344 | 123.0469 | -60.8047 | 62.0499 | 0.089373 | 0.020162 | 0.02064 | 0.0066936 | 0.0059611 | -0.0024516 | 0.00021367 | -60.8551 | 62.1506 | -61.1572 | 0.022888 | 0.004578 | 0.004578 | 0 | 0.17853 | 0.23346 | -0.28381 | -0.35248 | 0.10071 | -0.050354 | 60.8276 | -62.0453 | 60.5209 | -61.8164 | 0.30212
313.7656 | 123.1155 | -60.7727 | 62.0361 | -0.025068 | 0.015676 | 0.015086 | -0.0018514 | 0.0027567 | -0.00052895 | 0.0012817 | -60.878 | 62.0636 | -61.1435 | 0.10071 | 0.10071 | 0.13733 | 0.009155 | 0.36621 | 0.21515 | -0.21057 | -0.37079 | 0.027466 | -0.10529 | 60.8734 | -61.9354 | 60.5621 | -61.821 | 0.2655
314.7344 | 123.0652 | -60.8002 | 62.0636 | -0.11662 | 0.021016 | 0.016795 | 0.00648 | 0.0023295 | -0.00010175 | 6.6667e-08 | -60.8551 | 62.1552 | -61.1252 | 0.054932 | 0.041199 | 0.041199 | 0.036621 | 0.22888 | 0.23346 | -0.27008 | -0.32501 | 0.091552 | -0.054932 | 60.8551 | -62.0224 | 60.5301 | -61.8301 | 0.27008
315.7656 | 123.175 | -60.759 | 62.0132 | -0.047956 | 0.014181 | 0.019145 | -0.0039876 | 0.00062048 | -0.00074255 | 0.00042727 | -60.8826 | 62.027 | -61.1343 | 0.11444 | 0.12817 | 0.17395 | -0.059509 | 0.37079 | 0.22888 | -0.1831 | -0.37537 | 0.013733 | -0.1236 | 60.8734 | -61.8851 | 60.5759 | -61.7844 | 0.25177
316.7344 | 123.0515 | -60.8002 | 62.059 | -0.040327 | 0.021657 | 0.021067 | 0.0062662 | 0.0040385 | -0.0020244 | 0.00064087 | -60.8459 | 62.146 | -61.1481 | 0.027466 | 0.004578 | 0.009155 | 0.013733 | 0.19684 | 0.2243 | -0.28839 | -0.3479 | 0.086975 | -0.045776 | 60.8276 | -62.0544 | 60.5118 | -61.8347 | 0.30212
317.7656 | 123.143 | -60.7819 | 62.0041 | -0.13188 | 0.015249 | 0.016154 | -0.0048422 | 0.0019023 | -0.0015972 | 0.0017091 | -60.8917 | 62.0224 | -61.116 | 0.10529 | 0.11902 | 0.15564 | -0.050354 | 0.36621 | 0.24261 | -0.19684 | -0.33417 | 0.018311 | -0.10986 | 60.8871 | -61.8851 | 60.585 | -61.7615 | 0.2243
318.7344 | 123.0469 | -60.8047 | 62.059 | -0.070844 | 0.019735 | 0.020854 | 0.0084026 | 0.0027567 | 0.00053925 | 0.00021367 | -60.8459 | 62.1231 | -61.1298 | 0.036621 | 0 | -0.35248 | 0.013733 | 0.43488 | 0.21515 | -0.29297 | -0.32501 | 0.064087 | -0.041198 | 60.8414 | -62.059 | 60.5118 | -61.8439 | 0.28381
319.7656 | 123.0881 | -60.791 | 62.0041 | 0.21144 | 0.01653 | 0.019572 | -0.0018514 | 0.0042521 | -0.00031535 | 0.00021367 | -60.9192 | 62.0178 | -61.1755 | 0 | 0 | 0.013733 | -0.11444 | 0.21515 | 0.15106 | -0.3067 | -0.38452 | 0.013733 | -0.12817 | 60.791 | -62.0041 | 60.4843 | -61.853 | 0.25635
320.7344 | 123.0423 | -60.8047 | 62.0407 | -0.063215 | 0.019521 | 0.015513 | 0.0077616 | 0.0036113 | -0.00074255 | -0.0021361 | -60.8505 | 62.146 | -61.1481 | 0.041199 | 0.018311 | 0.036621 | 0.036621 | 0.23804 | 0.23346 | -0.2655 | -0.34332 | 0.10529 | -0.045776 | 60.8459 | -62.0224 | 60.5392 | -61.8073 | 0.29755
321.7656 | 123.111 | -60.7773 | 62.0316 | 0.013079 | 0.015035 | 0.012522 | -0.0033468 | 0.0027567 | 0.0018208 | 0.0012817 | -60.6445 | 62.0819 | -61.1389 | 0.07782 | 0.14648 | 0.13733 | -0.054932 | 0.37537 | 0.21057 | -0.23346 | -0.36163 | 0.050354 | 0.13275 | 60.8551 | -61.8851 | 60.5438 | -61.821 | 0.49439
322.7344 | 123.0789 | -60.8139 | 62.0636 | -0.10899 | 0.021016 | 0.017649 | 0.00648 | 0.0029705 | -0.00095615 | -0.00085453 | -60.8597 | 62.1689 | -61.1298 | 0.068665 | 0.041199 | 0.059509 | 0.064087 | 0.25635 | 0.24719 | -0.24261 | -0.31586 | 0.10528 | -0.045776 | 60.8826 | -62.0224 | 60.5713 | -61.8164 | 0.27008
323.7656 | 123.1064 | -60.8047 | 62.0132 | 0.0054493 | 0.014181 | 0.015086 | -0.0029196 | 0.00083408 | 0.00032545 | 0.00021367 | -60.9329 | 62.0224 | -61.1618 | 0.032043 | 0.027466 | 0.068665 | -0.086975 | 0.25635 | 0.20599 | -0.26093 | -0.35705 | 0.009155 | -0.12817 | 60.8368 | -61.9858 | 60.5438 | -61.8073 | 0.22888
324.7344 | 123.056 | -60.8002 | 62.0407 | -0.070844 | 0.018026 | 0.019999 | 0.0073344 | 0.0021159 | -0.002238 | -0.0021361 | -60.8459 | 62.1277 | -61.1206 | 0.059509 | 0.050354 | 0.045776 | 0.022888 | 0.25177 | 0.24719 | -0.26093 | -0.32043 | 0.086976 | -0.045776 | 60.8597 | -61.9904 | 60.5392 | -61.7935 | 0.27466
325.7656 | 123.1476 | -60.7864 | 62.0132 | -0.13951 | 0.015035 | 0.014018 | 0.0004984 | 0.0014751 | -0.0013834 | 0.00042727 | -60.8276 | 62.0544 | -61.1023 | 0.050354 | 0.022888 | 0.13733 | -0.013733 | 0.32959 | 0.23346 | -0.2243 | -0.31586 | 0.041198 | -0.041199 | 60.8368 | -61.9904 | 60.5621 | -61.7798 | 0.27466
326.7344 | 123.0743 | -60.7956 | 62.0544 | -0.15477 | 0.021444 | 0.01829 | 0.007548 | 0.0033977 | -0.0011698 | -0.00042733 | -60.8734 | 62.1414 | -61.1343 | 0.073242 | 0.027466 | 0.054932 | 0.045776 | 0.27924 | 0.24261 | -0.24719 | -0.33875 | 0.086975 | -0.07782 | 60.8688 | -62.027 | 60.5484 | -61.8118 | 0.26093
327.7656 | 123.1842 | -60.7773 | 62.0178 | -0.040327 | 0.015035 | 0.016154 | -0.0014242 | 0.0010477 | -0.0015972 | -0.00085453 | -60.8963 | 62.0178 | -61.1252 | 0.086975 | 0.11444 | 0.12817 | -0.068665 | 0.32959 | 0.20599 | -0.22888 | -0.3479 | 0 | -0.11902 | 60.8643 | -61.9034 | 60.5484 | -61.8118 | 0.22888
328.7344 | 123.0194 | -60.8231 | 62.0636 | -0.19291 | 0.018239 | 0.015513 | 0.0043436 | -0.0030111 | 0.00053925 | -0.00021353 | -60.9192 | 62.1185 | -61.1343 | -0.22888 | -0.24261 | 0.027466 | 0.21057 | 0.20599 | 0.27466 | -0.17853 | -0.31128 | 0.054931 | -0.09613 | 60.5942 | -62.3062 | 60.6445 | -61.7889 | 0.21515
329.75 | 123.0515 | -60.8139 | 62.0224 | 0.11989 | 0.019948 | 0.020854 | 0.0051982 | 0.0046793 | -0.00031535 | -0.00021353 | -60.91 | 62.1323 | -61.171 | -0.036621 | -0.041199 | -0.064087 | -0.050354 | 0.09613 | 0.19684 | -0.32501 | -0.35706 | 0.10986 | -0.09613 | 60.7773 | -62.0636 | 60.4889 | -61.8256 | 0.26093
330.7344 | 123.0835 | -60.7956 | 62.0407 | -0.14714 | 0.020589 | 0.016368 | 0.0069072 | 0.0033977 | -0.00031535 | -0.0027771 | -60.8597 | 62.1506 | -61.1389 | 0.054932 | 0.045776 | 0.050354 | 0.054932 | 0.26093 | 0.24719 | -0.23804 | -0.34332 | 0.10986 | -0.064087 | 60.8505 | -61.9949 | 60.5576 | -61.7935 | 0.27924
331.7656 | 123.0972 | -60.8002 | 62.0087 | 0.066485 | 0.017171 | 0.017863 | -0.003774 | 0.00062048 | 0.00053925 | 0.0010681 | -60.9421 | 62.0132 | -61.1343 | 0.013733 | 0.045776 | 0.036621 | -0.073242 | 0.21515 | 0.19226 | -0.26093 | -0.33417 | 0.004578 | -0.14191 | 60.8139 | -61.9629 | 60.5392 | -61.8164 | 0.19226
332.7344 | 123.0515 | -60.791 | 62.0773 | -0.14714 | 0.018667 | 0.017649 | 0.0084026 | 0.0014751 | -0.00095615 | -0.0019225 | -60.8963 | 62.1506 | -61.1572 | 0.027466 | 0.027466 | 0.041199 | 0.09613 | 0.23346 | 0.26093 | -0.18768 | -0.36621 | 0.073242 | -0.10529 | 60.8185 | -62.0499 | 60.6033 | -61.8164 | 0.26093
333.7656 | 123.1476 | -60.8002 | 61.9904 | 0.27248 | 0.020803 | 0.015727 | 0.0056254 | 0.0063883 | -0.00095615 | -0.00042733 | -60.8871 | 62.0636 | -61.1572 | 0.018311 | -0.004578 | -0.022888 | -0.14191 | 0.17853 | 0.17853 | -0.35248 | -0.35706 | 0.073243 | -0.086975 | 60.8185 | -61.9949 | 60.4477 | -61.8118 | 0.27008
334.7344 | 123.0194 | -60.8047 | 62.0636 | -0.18529 | 0.016317 | 0.018717 | 0.000712 | 0.0031841 | 0.00032545 | -0.0014953 | -60.9375 | 62.0911 | -61.171 | 0.013733 | 0.032043 | 0.050354 | 0.14648 | 0.23804 | 0.27466 | -0.18768 | -0.36621 | 0.027465 | -0.13275 | 60.8185 | -62.0316 | 60.6171 | -61.7889 | 0.23346
335.75 | 123.0148 | -60.8322 | 62.0224 | 0.24196 | 0.021657 | 0.018931 | 0.0081888 | 0.0057475 | -0.0018108 | -0.0010681 | -60.91 | 62.114 | -61.1572 | -0.059509 | -0.059509 | -0.091553 | -0.018311 | 0.09613 | 0.20142 | -0.36621 | -0.32501 | 0.091553 | -0.07782 | 60.7727 | -62.0819 | 60.466 | -61.821 | 0.24719
336.7344 | 123.0606 | -60.8047 | 62.0407 | -0.15477 | 0.019521 | 0.016795 | 0.0032756 | 0.0038249 | -0.00095615 | -0.0010681 | -60.91 | 62.1277 | -61.1572 | 0.036621 | 0.022888 | 0.027466 | 0.1236 | 0.23346 | 0.25177 | -0.19226 | -0.35248 | 0.086976 | -0.10529 | 60.8414 | -62.0178 | 60.6125 | -61.7889 | 0.24719
337.7656 | 123.1705 | -60.7498 | 62.0316 | -0.070844 | 0.014394 | 0.017222 | -0.0050558 | 0.0031841 | -0.0013834 | 0.00085447 | -60.878 | 62.0178 | -61.1298 | 0.10529 | 0.10986 | 0.14191 | -0.064087 | 0.34332 | 0.18768 | -0.21057 | -0.37994 | -0.013733 | -0.12817 | 60.8551 | -61.9217 | 60.5392 | -61.8439 | 0.25177
338.7344 | 123.0469 | -60.8047 | 62.0682 | -0.18529 | 0.019521 | 0.019572 | 0.004771 | 0.0014751 | -0.0020244 | 0.00085447 | -60.7819 | 62.1185 | -61.1526 | -0.032043 | -0.009155 | 0.022888 | 0.1236 | 0.24719 | 0.25635 | -0.25635 | -0.3479 | 0.050354 | 0.022889 | 60.7727 | -62.0773 | 60.5484 | -61.8118 | 0.37079
339.7656 | 123.0652 | -60.8368 | 62.0224 | 0.23433 | 0.020589 | 0.019358 | 0.00648 | 0.0040385 | 0.00053925 | -0.0023499 | -60.8963 | 62.114 | -61.1572 | -0.041199 | -0.050354 | -0.07782 | -0.068665 | 0.11444 | 0.17395 | -0.3479 | -0.32043 | 0.091553 | -0.059509 | 60.7956 | -62.0728 | 60.4889 | -61.8484 | 0.26093
340.7344 | 123.0103 | -60.8093 | 62.0865 | -0.20817 | 0.019735 | 0.019358 | 0.0009258 | 0.0019023 | -0.0030924 | -0.0014953 | -60.9375 | 62.1002 | -61.1664 | 0.009155 | 0.009155 | 0.041199 | 0.15106 | 0.24261 | 0.25635 | -0.19226 | -0.35706 | 0.013733 | -0.12817 | 60.8185 | -62.0773 | 60.6171 | -61.8301 | 0.22888
341.7656 | 123.0927 | -60.8002 | 62.0178 | 0.21907 | 0.017171 | 0.012309 | -0.002065 | 0.0014751 | -0.0018108 | 0.0019227 | -60.91 | 61.9858 | -61.1343 | 0 | 0.022888 | 0.013733 | -0.10071 | 0.2243 | 0.16937 | -0.28839 | -0.33417 | -0.032043 | -0.10986 | 60.8002 | -61.9949 | 60.5118 | -61.8484 | 0.2243
342.7344 | 123.1018 | -60.7864 | 62.0773 | -0.23869 | 0.016103 | 0.010813 | -0.0014242 | -0.0015157 | -0.0020244 | -0.0010681 | -60.8551 | 62.059 | -61.1298 | 0.086975 | 0.082397 | 0.1236 | 0.045776 | 0.33417 | 0.23804 | -0.21057 | -0.34332 | -0.018311 | -0.068665 | 60.8734 | -61.9949 | 60.5759 | -61.8393 | 0.27466
343.7656 | 123.0972 | -60.7727 | 62.0132 | -0.0021797 | 0.018667 | 0.014445 | -0.0012106 | 0.00040688 | -0.0015972 | -0.0019225 | -60.8688 | 62.0178 | -61.1343 | 0.1236 | 0.11902 | 0.14648 | -0.018311 | 0.3479 | 0.22888 | -0.20599 | -0.36163 | 0.004577 | -0.09613 | 60.8963 | -61.8942 | 60.5667 | -61.7844 | 0.2655
344.7344 | 122.9462 | -60.8139 | 62.0682 | -0.17766 | 0.017812 | 0.014659 | 0.0043436 | -0.00044752 | -0.0011698 | -0.0017089 | -60.9283 | 62.1002 | -61.1664 | 0.004578 | 0.018311 | 0.027466 | 0.13733 | 0.56763 | 0.27008 | -0.15106 | -0.35248 | 0.032044 | -0.11444 | 60.8185 | -62.0499 | 60.6628 | -61.7981 | 0.23804
345.75 | 123.0469 | -60.8139 | 62.0544 | 0.10463 | 0.019948 | 0.019999 | 0.010112 | 0.0036113 | -0.00052895 | 6.6667e-08 | -60.878 | 62.1277 | -61.1389 | 0 | -0.054932 | -0.036621 | 0.022888 | 0.14191 | 0.23804 | -0.31128 | -0.32501 | 0.073243 | -0.064087 | 60.8139 | -62.1094 | 60.5026 | -61.8164 | 0.26093
346.7344 | 123.0103 | -60.7864 | 62.0682 | -0.18529 | 0.017385 | 0.015727 | 0.0009258 | 0.0012615 | -0.0026652 | -0.0014953 | -60.9421 | 62.1048 | -61.1755 | 0.018311 | 0.027466 | 0.050354 | 0.15564 | 0.26093 | 0.28381 | -0.16022 | -0.3891 | 0.036621 | -0.15564 | 60.8047 | -62.0407 | 60.6262 | -61.7844 | 0.23346
347.75 | 123.0011 | -60.8276 | 62.0407 | 0.15804 | 0.020803 | 0.021281 | 0.0094706 | 0.0038249 | 0.00075285 | -0.00021353 | -60.9055 | 62.1277 | -61.1389 | -0.027466 | -0.059509 | -0.09613 | 0.009155 | 0.091553 | 0.2243 | -0.35706 | -0.31128 | 0.086976 | -0.07782 | 60.8002 | -62.1002 | 60.4706 | -61.8164 | 0.23346
348.7344 | 123.0194 | -60.7956 | 62.0453 | -0.23106 | 0.017812 | 0.014231 | -0.000356 | 0.0033977 | -0.00095615 | 0.0014953 | -60.9192 | 62.0865 | -61.1572 | 0.027466 | 0.022888 | 0.064087 | 0.15106 | 0.28381 | 0.26093 | -0.16479 | -0.36163 | 0.041199 | -0.1236 | 60.8231 | -62.0224 | 60.6308 | -61.7844 | 0.23804
349.7656 | 123.0286 | -60.8185 | 62.0224 | 0.27248 | 0.021016 | 0.020426 | 0.0079752 | 0.0063883 | 0.00011185 | -0.0019225 | -60.9283 | 62.1414 | -61.1389 | -0.059509 | -0.045776 | -0.09613 | -0.022888 | 0.07782 | 0.19684 | -0.35248 | -0.32044 | 0.11902 | -0.10986 | 60.759 | -62.0682 | 60.466 | -61.8256 | 0.21057
350.7344 | 123.0286 | -60.8185 | 62.0499 | -0.19291 | 0.018239 | 0.017649 | -0.0007832 | 0.0053203 | -0.0011698 | -0.00064093 | -60.9329 | 62.114 | -61.1572 | 0.004578 | 0.022888 | 0.050354 | 0.15106 | 0.24261 | 0.29297 | -0.18768 | -0.33875 | 0.064087 | -0.11444 | 60.8231 | -62.027 | 60.6308 | -61.7569 | 0.22431
351.7656 | 123.111 | -60.8093 | 62.0224 | 0.21907 | 0.018239 | 0.01359 | -0.0016378 | 0.0042521 | -0.00052895 | 0.0017091 | -60.9055 | 61.9995 | -61.116 | 0.013733 | 0.027466 | 0 | -0.1236 | 0.20142 | 0.16937 | -0.3067 | -0.3067 | -0.022888 | -0.096131 | 60.8231 | -61.9949 | 60.5026 | -61.853 | 0.21057
352.7344 | 123.0423 | -60.8139 | 62.0316 | -0.14714 | 0.017385 | 0.015727 | 0.0017802 | 0.0023295 | -0.0011698 | 0.0014953 | -60.9055 | 62.0865 | -61.1481 | 0.022888 | 0.022888 | 0.050354 | 0.14191 | 0.24261 | 0.28381 | -0.17853 | -0.33417 | 0.054932 | -0.091553 | 60.8368 | -62.0087 | 60.6354 | -61.7477 | 0.24261
353.7656 | 123.0743 | -60.791 | 62.0224 | 0.18855 | 0.017171 | 0.014659 | -0.0001424 | 0.00083408 | -0.0013834 | -0.00064093 | -60.9375 | 61.9949 | -61.1526 | 0.018311 | 0.027466 | 0.032043 | -0.091553 | 0.21515 | 0.20142 | -0.27924 | -0.36163 | -0.027466 | -0.14648 | 60.8093 | -61.9949 | 60.5118 | -61.821 | 0.21515
354.7344 | 123.0515 | -60.8093 | 62.0453 | -0.17766 | 0.017812 | 0.016368 | 0.0022074 | -0.0017293 | -0.00074255 | -0.0021361 | -60.8917 | 62.0728 | -61.1389 | 0.041199 | 0.041199 | 0.086975 | 0.091553 | 0.24719 | 0.26093 | -0.1831 | -0.32959 | 0.027466 | -0.082398 | 60.8505 | -62.0041 | 60.6262 | -61.7844 | 0.24719
355.7656 | 123.1476 | -60.7956 | 61.9858 | 0.26485 | 0.020589 | 0.019786 | 0.00648 | 0.0010477 | 0.0016072 | 6.6667e-08 | -60.8414 | 62.0178 | -61.1435 | 0.045776 | 0.041199 | 0.018311 | -0.20142 | 0.2243 | 0.14648 | -0.35248 | -0.3479 | 0.032043 | -0.045777 | 60.8414 | -61.9446 | 60.4431 | -61.8393 | 0.30212
356.7344 | 123.1384 | -60.7681 | 62.0178 | -0.20054 | 0.015249 | 0.017008 | 7.12e-05 | 0.0046793 | 0.0013936 | 0.0012817 | -60.8551 | 62.0087 | -61.1343 | 0.19226 | 0.19226 | 0.027466 | -0.14191 | 0.36621 | 0.22888 | -0.2243 | -0.36621 | -0.009155 | -0.086976 | 60.9604 | -61.8256 | 60.5438 | -61.7889 | 0.27923
357.7656 | 123.1018 | -60.7819 | 62.0041 | 0.18855 | 0.018239 | 0.016795 | 0.001353 | 0.0010477 | -0.0015972 | 0.0021363 | -60.8871 | 62.0087 | -61.116 | 0.018311 | 0.027466 | 0.013733 | -0.13733 | 0.21515 | 0.15564 | -0.32959 | -0.33417 | 0.004578 | -0.10529 | 60.8002 | -61.9766 | 60.4523 | -61.8484 | 0.22888
358.7344 | 123.0011 | -60.8185 | 62.059 | -0.27684 | 0.018026 | 0.015299 | 0.002421 | -0.00023392 | -0.00074255 | -0.00042733 | -60.9055 | 62.0911 | -61.1389 | 0.022888 | 0.032043 | 0.068665 | 0.13733 | 0.24261 | 0.27466 | -0.17853 | -0.32044 | 0.032043 | -0.086976 | 60.8414 | -62.027 | 60.64 | -61.7844 | 0.23346
359.7656 | 123.1293 | -60.8002 | 61.9812 | 0.2267 | 0.018453 | 0.014018 | 0.002421 | 0.0012615 | 0.0013936 | 0.0014953 | -60.8597 | 62.0132 | -61.1618 | 0.036621 | 0.036621 | 0.032043 | -0.15564 | 0.21973 | 0.16479 | -0.33875 | -0.36163 | 0.032044 | -0.059509 | 60.8368 | -61.9446 | 60.4614 | -61.8164 | 0.30212
360.7344 | 123.0103 | -60.8322 | 62.027 | 0.16567 | 0.020803 | 0.01594 | 0.009257 | 0.0023295 | 0.0020344 | -0.00064093 | -60.9192 | 62.1277 | -61.1435 | -0.045776 | -0.07782 | -0.10986 | 0.009155 | 0.082397 | 0.21515 | -0.36163 | -0.31128 | 0.10071 | -0.086975 | 60.7864 | -62.1048 | 60.4706 | -61.8118 | 0.2243
361.7656 | 123.0606 | -60.8414 | 62.0087 | 2.0349 | 0.02123 | 0.014659 | 0.0086162 | 0.0038249 | 0.00096645 | -0.00021353 | -60.7819 | 62.1002 | -61.171 | -0.059509 | -0.036621 | -0.068665 | -0.041199 | 0.086975 | 0.21057 | -0.32044 | -0.32959 | 0.091553 | 0.05951 | 60.7819 | -62.0453 | 60.5209 | -61.7981 | 0.3891
362.7344 | 123.1659 | -60.759 | 61.9995 | -0.025068 | 0.017598 | 0.014231 | -0.0018514 | 0.0021159 | 0.00053925 | 0.0021363 | -60.8734 | 62.0132 | -61.1572 | 0.10986 | 0.12817 | 0.17853 | -0.032043 | 0.36621 | 0.21515 | -0.17853 | -0.39825 | 0.013733 | -0.11444 | 60.8688 | -61.8713 | 60.5804 | -61.7844 | 0.28381
363.75 | 123.0423 | -60.8047 | 62.0453 | 0.051226 | 0.022512 | 0.021708 | 0.0094706 | 0.0025431 | 0.0013936 | -0.00085453 | -60.8688 | 62.146 | -61.1206 | 0.013733 | -0.004578 | -0.027466 | 0 | 0.17853 | 0.20599 | -0.3067 | -0.31586 | 0.10071 | -0.064086 | 60.8185 | -62.0499 | 60.498 | -61.8393 | 0.25177
364.7344 | 122.9965 | -60.8047 | 62.059 | -0.2158 | 0.018667 | 0.01829 | 0.0004984 | 0.0010477 | -0.00031535 | 0.00064087 | -60.9146 | 62.0956 | -61.1435 | 0 | 0.032043 | 0.068665 | 0.13275 | 0.2655 | 0.27924 | -0.16937 | -0.33874 | 0.036621 | -0.10986 | 60.8047 | -62.027 | 60.6354 | -61.7798 | 0.22888
365.7656 | 123.143 | -60.7727 | 62.0316 | 2.1112 | 0.017171 | 0.016368 | -0.0014242 | 0.0038249 | -0.0011698 | 0.00042727 | -60.9329 | 62.0224 | -61.1389 | 0.082397 | 0.11902 | 0.16937 | -0.013733 | 0.35706 | 0.2243 | -0.21973 | -0.36621 | -0.009155 | -0.16022 | 60.8551 | -61.9125 | 60.553 | -61.8073 | 0.20599
366.7344 | 123.0423 | -60.7819 | 62.0636 | -0.19291 | 0.016744 | 0.019999 | 0.0026346 | 0.00040688 | -0.00074255 | -0.0029907 | -60.8917 | 62.0865 | -61.1389 | 0.068665 | 0.054932 | 0.091553 | 0.082397 | 0.25635 | 0.27008 | -0.19684 | -0.35706 | 0.022888 | -0.10986 | 60.8505 | -62.0087 | 60.585 | -61.7935 | 0.24719
367.7344 | 123.0698 | -60.7681 | 62.0544 | -0.2158 | 0.01653 | 0.018504 | 0.0022074 | 0.0014751 | -0.00052895 | 6.6667e-08 | -60.8734 | 62.059 | -61.1343 | 0.064087 | 0.073242 | 0.09613 | 0.10071 | 0.31128 | 0.24719 | -0.19226 | -0.36621 | 0.004578 | -0.10529 | 60.8322 | -61.9812 | 60.5759 | -61.8073 | 0.26093
368.7344 | 123.1155 | -60.7773 | 62.027 | -0.8643 | 0.017385 | 0.018504 | 0.0015666 | 0.00062048 | -0.002238 | -0.0025635 | -61.0382 | 62.0224 | -61.1206 | 0.10529 | 0.10986 | 0.15106 | -0.004578 | 0.37079 | 0.21057 | -0.23804 | -0.34332 | -0.004578 | -0.26093 | 60.8826 | -61.9171 | 60.5392 | -61.8164 | 0.082397
369.7656 | 123.1613 | -60.791 | 61.9995 | 0.19618 | 0.017598 | 0.019572 | 0.004771 | 0.0042521 | 0.00075285 | -0.0029907 | -60.8414 | 62.0499 | -61.1481 | 0.050354 | 0.036621 | 0.022888 | -0.19684 | 0.21057 | 0.16022 | -0.36621 | -0.35706 | 0.050354 | -0.050354 | 60.8414 | -61.9629 | 60.4248 | -61.8393 | 0.3067
370.7344 | 123.0515 | -60.8002 | 62.0544 | -0.025068 | 0.019948 | 0.018717 | 0.0066936 | 0.0029705 | -0.00031535 | -0.00064093 | -60.8414 | 62.114 | -61.1526 | 0.045776 | 0.018311 | 0.018311 | 0.004578 | 0.20599 | 0.22888 | -0.27466 | -0.35248 | 0.05951 | -0.041199 | 60.8459 | -62.0361 | 60.5255 | -61.8256 | 0.31128
371.7656 | 123.1476 | -60.7956 | 62.0041 | 0.40981 | 0.018667 | 0.016368 | 0.0037028 | 0.0051067 | -0.00095615 | -0.00064093 | -60.8459 | 62.0911 | -61.1618 | 0.054932 | 0.032043 | -0.004578 | -0.19684 | 0.19684 | 0.15564 | -0.38452 | -0.36621 | 0.086975 | -0.050354 | 60.8505 | -61.972 | 60.4111 | -61.8484 | 0.31586
372.7344 | 123.0331 | -60.8322 | 62.0682 | -0.1624 | 0.016744 | 0.019145 | -0.000356 | -0.00023392 | -0.0013834 | 0.00064087 | -60.9146 | 62.0911 | -61.1572 | 0.041199 | 0.059509 | 0.10071 | 0.10529 | 0.22888 | 0.2655 | -0.1831 | -0.32501 | 0.022888 | -0.082398 | 60.8734 | -62.0087 | 60.6491 | -61.8027 | 0.24262
373.7656 | 123.0881 | -60.7773 | 61.9675 | 0.27248 | 0.01653 | 0.017222 | 0.00413 | 0.0025431 | -0.0013834 | 6.6667e-08 | -60.8505 | 62.0224 | -61.1298 | 0.045776 | 0.050354 | 0.041199 | -0.17853 | 0.2243 | 0.13733 | -0.36621 | -0.35248 | 0.054932 | -0.073242 | 60.8231 | -61.9171 | 60.4111 | -61.8301 | 0.27924
374.7344 | 123.0606 | -60.791 | 62.0316 | -0.20054 | 0.016317 | 0.016795 | -0.0005696 | 0.0040385 | -0.00031535 | -0.00042733 | -60.9009 | 62.0682 | -61.1343 | 0.064087 | 0.073242 | 0.09613 | 0.086975 | 0.29297 | 0.25635 | -0.20142 | -0.34332 | 0.036621 | -0.10986 | 60.8551 | -61.9583 | 60.5896 | -61.7752 | 0.23346
375.7656 | 123.1201 | -60.7819 | 62.0407 | -0.1624 | 0.016958 | 0.016581 | 7.12e-05 | 0.0021159 | -0.0028788 | 0.00021367 | -60.8597 | 62.0361 | -61.1435 | 0.09613 | 0.09613 | 0.12817 | 0.032043 | 0.34332 | 0.25177 | -0.20142 | -0.36163 | -0.004577 | -0.07782 | 60.878 | -61.9446 | 60.5804 | -61.7889 | 0.28381
376.7344 | 123.1293 | -60.7636 | 62.0316 | -0.13188 | 0.015676 | 0.017008 | -0.002065 | -0.0045065 | -0.0011698 | 0.0010681 | -60.8643 | 62.0316 | -61.1252 | -0.27924 | -0.21515 | 0.2243 | 0.10529 | 0.24719 | 0.2243 | -0.21515 | -0.36163 | 0 | -0.10071 | 60.4843 | -62.2467 | 60.5484 | -61.8073 | 0.26093
377.7656 | 123.0835 | -60.8597 | 62.0773 | 0.1733 | 0.020803 | 0.023417 | 0.0081888 | 0.0019023 | 0.0016072 | -0.0017089 | -60.9055 | 62.1277 | -61.1481 | -0.041199 | -0.059509 | -0.09613 | -0.19684 | -0.54474 | 0.16937 | -0.3891 | -0.28839 | 0.050354 | -0.045777 | 60.8185 | -62.1368 | 60.4706 | -61.908 | 0.24261
378.7344 | 123.0286 | -60.8093 | 62.0544 | -0.17003 | 0.019735 | 0.019145 | 0.0032756 | 0.0025431 | -0.002238 | -0.00085453 | -60.9009 | 62.0773 | -61.1298 | 0.064087 | 0.064087 | 0.050354 | 0.086975 | 0.24261 | 0.2655 | -0.18768 | -0.32044 | 0.022889 | -0.091553 | 60.8734 | -61.9904 | 60.6216 | -61.7889 | 0.22888
379.7656 | 123.1155 | -60.7956 | 62.0041 | 0.31825 | 0.019307 | 0.019358 | 0.0028484 | 0.0057475 | -0.0011698 | -0.00042733 | -60.8231 | 62.0407 | -61.1206 | 0.059509 | 0.032043 | 0.027466 | -0.19684 | 0.23804 | 0.14648 | -0.3479 | -0.32501 | 0.036621 | -0.027466 | 60.8551 | -61.972 | 60.4477 | -61.8576 | 0.29755
380.7344 | 123.0515 | -60.7864 | 62.0499 | -0.17766 | 0.015035 | 0.016795 | 0.000712 | 0.0010477 | -0.0030924 | -0.00042733 | -60.8826 | 62.0636 | -61.1389 | 0.082397 | 0.054932 | 0.10071 | 0.073242 | 0.28381 | 0.24261 | -0.20599 | -0.35248 | 0.013733 | -0.09613 | 60.8688 | -61.9949 | 60.5804 | -61.8073 | 0.25635
381.7656 | 122.9919 | -60.8276 | 62.0178 | 0.10463 | 0.020376 | 0.020854 | 0.0066936 | 0.0038249 | -0.002238 | -0.0012817 | -60.91 | 62.1552 | -61.1618 | -0.050354 | -0.073242 | -0.10071 | 0 | 0.07782 | 0.20142 | -0.3479 | -0.33417 | 0.13733 | -0.082397 | 60.7773 | -62.0911 | 60.4797 | -61.8164 | 0.25177
382.7344 | 123.1293 | -60.7452 | 62.0224 | -0.093733 | 0.017171 | 0.011027 | -0.0018514 | 0.0014751 | -0.0020244 | -0.00042733 | -60.8688 | 62.0132 | -61.1114 | 0.13275 | 0.14191 | 0.09613 | 0.68207 | 0.71869 | 0.28839 | -0.15106 | -0.36621 | -0.009155 | -0.1236 | 60.878 | -61.8805 | 60.5942 | -61.734 | 0.24262
383.7656 | 122.9874 | -60.8368 | 62.0728 | 0.097002 | 0.020162 | 0.01829 | 0.0088298 | 0.0044657 | -0.0020244 | 0.00021367 | -60.8826 | 62.1506 | -61.1526 | -0.032043 | -0.022888 | -0.064087 | 0.027466 | 0.11902 | 0.2243 | -0.32959 | -0.31586 | 0.07782 | -0.045776 | 60.8047 | -62.0956 | 60.5072 | -61.8485 | 0.27008
384.7344 | 123.1293 | -60.791 | 62.0361 | -0.18529 | 0.017812 | 0.011881 | -0.0005696 | 0.0025431 | -0.0018108 | -0.0012817 | -60.8505 | 62.0728 | -61.1481 | 0.11444 | 0.11444 | 0.13733 | -0.027466 | 0.33875 | 0.22888 | -0.21515 | -0.35706 | 0.036621 | -0.059509 | 60.9055 | -61.9217 | 60.5759 | -61.8073 | 0.29755
385.75 | 123.0652 | -60.8185 | 62.0453 | -0.032697 | 0.019735 | 0.020213 | 0.0066936 | 0.0042521 | 0.00032545 | 6.6667e-08 | -60.8368 | 62.146 | -61.1343 | 0.13733 | 0.059509 | 0.022888 | 0.013733 | 0.20599 | 0.21973 | -0.28839 | -0.31586 | 0.10071 | -0.018311 | 60.9558 | -61.9858 | 60.5301 | -61.8256 | 0.29755
386.7344 | 123.0972 | -60.7819 | 62.0636 | -0.2158 | 0.01653 | 0.015513 | -0.0012106 | 0.0010477 | -0.00074255 | 0.00042727 | -60.878 | 62.059 | -61.1206 | 0.086975 | 0.086975 | 0.13733 | 0.050354 | 0.32959 | 0.27008 | -0.21057 | -0.33874 | -0.004578 | -0.096131 | 60.8688 | -61.9766 | 60.5713 | -61.7935 | 0.24261
387.7656 | 122.9645 | -60.8368 | 62.0132 | 0.18855 | 0.021016 | 0.018717 | 0.0079752 | 0.0025431 | -0.00074255 | -0.0010681 | -60.9283 | 62.1094 | -61.1755 | -0.059509 | -0.054932 | -0.09613 | -0.013733 | 0.086975 | 0.20599 | -0.35248 | -0.33874 | 0.09613 | -0.091553 | 60.7773 | -62.0682 | 60.4843 | -61.8073 | 0.24719
388.7344 | 123.143 | -60.7681 | 62.027 | -0.18529 | 0.015889 | 0.019145 | -0.0044148 | 0.0019023 | 0.00075285 | 6.6667e-08 | -60.8688 | 62.0224 | -61.1343 | 0.10529 | 0.12817 | 0.15564 | -0.045776 | 0.36163 | 0.21057 | -0.20599 | -0.36621 | -0.004578 | -0.10071 | 60.8734 | -61.8988 | 60.5621 | -61.8164 | 0.2655
389.75 | 123.0789 | -60.7773 | 62.0544 | 0.028338 | 0.020376 | 0.017222 | 0.0084026 | 0.0033977 | 0.002889 | 0.00064087 | -60.8368 | 62.1231 | -61.116 | -0.068665 | 0.054932 | 0.19226 | 0.054932 | 0.21515 | 0.21973 | -0.27466 | -0.33875 | 0.068665 | -0.059509 | 60.7086 | -61.9995 | 60.5026 | -61.8347 | 0.27924
390.7344 | 123.1338 | -60.7498 | 62.0178 | -0.078474 | 0.016958 | 0.019999 | -0.0046284 | 0.0031841 | -0.0018108 | -0.00042733 | -60.8826 | 62.0132 | -61.1343 | 0.12817 | 0.12817 | 0.15106 | -0.073242 | 0.37079 | 0.21515 | -0.1831 | -0.38452 | -0.004577 | -0.13275 | 60.878 | -61.8896 | 60.5667 | -61.8027 | 0.25177
391.7656 | 123.056 | -60.8276 | 62.0636 | -0.19291 | 0.016958 | 0.012095 | 0.0002848 | 0.0027567 | -0.00010175 | 6.6667e-08 | -60.8871 | 62.0407 | -61.1206 | 0.068665 | 0.054932 | 0.1236 | 0.086975 | 0.28381 | 0.25635 | -0.19226 | -0.29297 | -0.022889 | -0.059509 | 60.8963 | -62.0087 | 60.6354 | -61.8073 | 0.23346
392.7344 | 123.1522 | -60.7727 | 62.0453 | -2.3215 | 0.016317 | 0.016581 | -0.0005696 | 0.0010477 | 0.00075285 | -0.00042733 | -61.0016 | 62.0361 | -61.1343 | 0.13275 | 0.091553 | 0.11902 | -0.027466 | 0.37994 | 0.22888 | -0.23804 | -0.36163 | -0.009155 | -0.22888 | 60.9055 | -61.9537 | 60.5347 | -61.8164 | 0.13275
393.7656 | 123.0331 | -60.8139 | 62.0682 | 0.18855 | 0.021444 | 0.019999 | 0.0086162 | 0.0029705 | 0.0018208 | -0.00085453 | -60.9009 | 62.1597 | -61.1435 | -0.022888 | -0.054932 | -0.09613 | 0.009155 | 0.086975 | 0.21973 | -0.34332 | -0.32959 | 0.091553 | -0.086975 | 60.791 | -62.1231 | 60.4706 | -61.8484 | 0.24261
394.7344 | 123.1522 | -60.7544 | 62.0224 | -0.025068 | 0.015676 | 0.015086 | -0.0012106 | 0.00040688 | 0.00075285 | -0.0010681 | -60.9009 | 61.9995 | -61.1526 | 0.09613 | 0.10529 | 0.11444 | -0.07782 | 0.32044 | 0.19226 | -0.23346 | -0.39825 | -0.022888 | -0.14648 | 60.8505 | -61.9171 | 60.5209 | -61.8301 | 0.25177
395.7656 | 123.1338 | -60.8047 | 61.9995 | 0.27248 | 0.019307 | 0.018717 | 0.0054118 | 0.0027567 | -0.0011698 | 0.00021367 | -60.8505 | 62.0316 | -61.1435 | 0.064087 | 0.036621 | 0.013733 | -0.19684 | 0.2243 | 0.16479 | -0.35248 | -0.33874 | 0.032043 | -0.045776 | 60.8688 | -61.9629 | 60.4523 | -61.8347 | 0.29297
396.7344 | 123.1613 | -60.7544 | 62.0178 | -0.025068 | 0.01653 | 0.014872 | -0.0029196 | 0.00083408 | -0.00031535 | 0.0021363 | -60.8826 | 62.0178 | -61.116 | 0.091553 | 0.10529 | 0.12817 | -0.064087 | 0.35248 | 0.24261 | -0.2243 | -0.36163 | 0 | -0.12817 | 60.8459 | -61.9125 | 60.5301 | -61.7752 | 0.23346
397.7656 | 123.056 | -60.7956 | 62.059 | 0.043596 | 0.020803 | 0.018931 | 0.0077616 | 0.0025431 | -0.00010175 | -0.0019225 | -60.8459 | 62.1094 | -61.1481 | 0.045776 | 0.013733 | 0.018311 | 0.027466 | 0.21973 | 0.24261 | -0.27466 | -0.35248 | 0.050354 | -0.050354 | 60.8414 | -62.0453 | 60.5209 | -61.8164 | 0.30212
398.7344 | 123.143 | -60.7727 | 62.0132 | 0.028338 | 0.017171 | 0.017863 | -0.0012106 | 0.0029705 | 0.00118 | 0.0023499 | -60.9238 | 62.0132 | -61.1572 | 0.068665 | 0.082397 | 0.091553 | -0.054932 | 0.30212 | 0.2243 | -0.2243 | -0.38452 | 0 | -0.15106 | 60.8414 | -61.9308 | 60.5484 | -61.7889 | 0.23346
399.7344 | 123.1567 | -60.7727 | 62.0224 | 0.013079 | 0.01653 | 0.011241 | -0.0009968 | -0.0010885 | -0.002238 | -0.00042733 | -60.8826 | 62.0224 | -61.1481 | 0.10529 | 0.10071 | 0.1236 | -0.073242 | 0.32959 | 0.20599 | -0.24719 | -0.37537 | 0 | -0.10986 | 60.878 | -61.9217 | 60.5255 | -61.8164 | 0.2655
400.7344 | 123.1155 | -60.7681 | 62.0316 | 0.028338 | 0.015889 | 0.016154 | -0.002065 | -0.00066112 | 0.00011185 | -0.00085453 | -60.8917 | 62.0178 | -61.116 | 0.086975 | 0.07782 | 0.091553 | -0.091553 | 0.31128 | 0.21057 | -0.24261 | -0.3479 | -0.013733 | -0.1236 | 60.8551 | -61.9537 | 60.5255 | -61.821 | 0.2243
401.7344 | 123.1384 | -60.7727 | 62.0361 | 0.081743 | 0.016103 | 0.01295 | 0.0002848 | -0.0017293 | 0.00032545 | -0.00021353 | -60.9192 | 62.0132 | -61.1114 | 0.068665 | 0.059509 | 0.091553 | -0.064087 | 0.29755 | 0.19226 | -0.24719 | -0.33874 | -0.022888 | -0.14648 | 60.8414 | -61.9766 | 60.5255 | -61.8439 | 0.19226
402.7344 | 123.0927 | -60.7681 | 62.0361 | 0.097002 | 0.017385 | 0.017436 | 0.0002848 | -0.0038655 | 0.00075285 | 0.00064087 | -60.9238 | 62.0316 | -61.1298 | 0.032043 | 0.036621 | 0.041199 | -0.09613 | 0.19684 | 0.18768 | -0.27008 | -0.36163 | -0.004578 | -0.15564 | 60.8002 | -61.9995 | 60.498 | -61.8484 | 0.20599
403.7344 | 123.1201 | -60.7636 | 62.0041 | 0.020708 | 0.01653 | 0.014659 | -0.0012106 | -0.0017293 | 0.0016072 | -0.00085453 | -60.8871 | 62.0087 | -61.1298 | 0.082397 | 0.082397 | 0.10529 | -0.082397 | 0.29755 | 0.20599 | -0.23804 | -0.36621 | 0.004578 | -0.1236 | 60.8459 | -61.9217 | 60.5255 | -61.7981 | 0.24262
404.7656 | 123.0103 | -60.8276 | 62.0499 | 0.11226 | 0.022085 | 0.014872 | 0.010539 | 0.0014751 | -0.0011698 | -0.00042733 | -60.878 | 62.1552 | -61.1481 | -0.036621 | -0.064087 | -0.073242 | 0 | 0.10071 | 0.19684 | -0.33875 | -0.32043 | 0.10528 | -0.050354 | 60.791 | -62.114 | 60.4889 | -61.853 | 0.27008
405.7344 | 123.1247 | -60.7864 | 62.0132 | -0.10136 | 0.016744 | 0.016368 | -0.0024922 | -0.00066112 | -0.00095615 | -0.0012817 | -60.9512 | 62.027 | -61.1435 | 0.041199 | 0.059509 | 0.036621 | -0.07782 | 0.24261 | 0.20142 | -0.25635 | -0.35706 | 0.013733 | -0.1648 | 60.8276 | -61.9537 | 60.5301 | -61.8118 | 0.19226
406.75 | 123.0698 | -60.791 | 62.0499 | -0.10899 | 0.018239 | 0.018077 | 0.0096842 | 0.0019023 | -0.0030924 | -0.0010681 | -60.8871 | 62.1002 | -61.1664 | 0.073242 | 0.041199 | 0.059509 | 0.050354 | 0.24719 | 0.25177 | -0.25177 | -0.37537 | 0.050354 | -0.09613 | 60.8643 | -62.0087 | 60.5392 | -61.7981 | 0.27924
407.7344 | 123.0652 | -60.7956 | 62.0453 | 0.089373 | 0.015249 | 0.013804 | -0.0039876 | 0.0012615 | -0.00031535 | 0.00064087 | -60.9375 | 62.0132 | -61.1618 | 0.018311 | 0.059509 | 0.036621 | -0.082397 | 0.21973 | 0.20142 | -0.26093 | -0.36621 | -0.032043 | -0.14191 | 60.8139 | -61.9858 | 60.5347 | -61.8439 | 0.2243
408.7656 | 123.0698 | -60.7956 | 62.0544 | -0.025068 | 0.019735 | 0.020854 | 0.0088298 | 0.0029705 | 0.00011185 | -0.0010681 | -60.8505 | 62.146 | -61.1664 | 0.064087 | 0.036621 | 0.032043 | 0.027466 | 0.23346 | 0.22888 | -0.27924 | -0.37079 | 0.091553 | -0.054932 | 60.8597 | -62.0178 | 60.5164 | -61.8256 | 0.31586
409.7344 | 123.0972 | -60.7819 | 62.0087 | 0.18093 | 0.017385 | 0.016154 | -0.0012106 | 0.0036113 | 0.00096645 | -0.00042733 | -60.9329 | 62.0132 | -61.1389 | 0.022888 | 0.022888 | 0.022888 | -0.086975 | 0.21515 | 0.1831 | -0.28381 | -0.35706 | 0.004578 | -0.15106 | 60.8047 | -61.9858 | 60.498 | -61.8256 | 0.20599
410.7656 | 123.0423 | -60.8047 | 62.0544 | -0.10136 | 0.019948 | 0.014872 | 0.0062662 | 0.00040688 | -0.0020244 | -0.0012817 | -60.9329 | 62.1368 | -61.1435 | 0.045776 | 0.050354 | 0.045776 | 0.10529 | 0.21515 | 0.25177 | -0.2243 | -0.33874 | 0.082398 | -0.12817 | 60.8505 | -62.0041 | 60.5804 | -61.8027 | 0.21057
411.7344 | 123.1018 | -60.7636 | 61.9995 | 0.18855 | 0.013967 | 0.018717 | -0.0009968 | 0.0027567 | -0.00074255 | 0.0019227 | -60.8734 | 62.0087 | -61.1526 | 0.027466 | 0.032043 | 0.009155 | -0.15106 | 0.19684 | 0.16479 | -0.31586 | -0.3891 | 0.009155 | -0.10986 | 60.791 | -61.9675 | 60.4477 | -61.8347 | 0.27924
412.7656 | 123.0743 | -60.8047 | 62.0407 | -0.12425 | 0.020803 | 0.018931 | 0.0084026 | 0.0010477 | -0.0015972 | -0.0019225 | -60.8368 | 62.1277 | -61.1252 | 0.073242 | 0.041199 | 0.022888 | 0.036621 | 0.23804 | 0.23346 | -0.2655 | -0.32043 | 0.086976 | -0.032043 | 60.878 | -61.9995 | 60.5392 | -61.8073 | 0.28839
413.7344 | 123.143 | -60.7864 | 62.0407 | 0.12752 | 0.018026 | 0.015727 | -0.0016378 | 0.0021159 | 0.00075285 | 0.00021367 | -60.9375 | 62.0178 | -61.1389 | 0.032043 | 0.059509 | 0.045776 | -0.073242 | 0.23346 | 0.18768 | -0.26093 | -0.35248 | -0.022888 | -0.15106 | 60.8185 | -61.9812 | 60.5255 | -61.853 | 0.20142
414.7812 | 123.0881 | -60.791 | 62.0316 | 0.10463 | 0.016317 | 0.01594 | 0.0004984 | 0.00040688 | -0.0018108 | 0.0010681 | -60.9375 | 62.0087 | -61.1298 | 0.027466 | 0.050354 | 0.045776 | -0.068665 | 0.2243 | 0.18768 | -0.28381 | -0.33875 | -0.022888 | -0.14648 | 60.8185 | -61.9812 | 60.5072 | -61.8439 | 0.19226
416.1875 | 123.1155 | -60.7864 | 62.0041 | 0.303 | 0.019307 | 0.017436 | 0.005839 | 0.0014751 | 0.00096645 | -0.00042733 | -60.8871 | 62.0361 | -61.1435 | 0.022888 | 0.004578 | -0.027466 | -0.16479 | 0.23346 | 0.14648 | -0.35248 | -0.35706 | 0.032044 | -0.10071 | 60.8093 | -61.9995 | 60.434 | -61.8576 | 0.25635
416.9062 | 123.0423 | -60.8185 | 62.0407 | -0.2158 | 0.020589 | 0.016581 | 0.0062662 | 0.0019023 | -0.00095615 | -0.0019225 | -60.91 | 62.1368 | -61.1343 | 0.032043 | 0.022888 | 0.032043 | 0.1236 | 0.23804 | 0.2655 | -0.20142 | -0.31586 | 0.096131 | -0.091553 | 60.8505 | -62.0178 | 60.6171 | -61.7752 | 0.2243
418.1719 | 123.056 | -60.791 | 62.0453 | -0.12425 | 0.018239 | 0.013804 | 0.0077616 | 0.0046793 | -0.0020244 | -0.0027771 | -60.8459 | 62.1231 | -61.1435 | 0.091553 | 0.068665 | 0.064087 | 0.032043 | 0.23346 | 0.2655 | -0.24719 | -0.35248 | 0.07782 | -0.054931 | 60.8826 | -61.9766 | 60.5438 | -61.7798 | 0.29755
418.7344 | 123.1476 | -60.7819 | 61.9995 | 0.32588 | 0.01888 | 0.018931 | 0.004771 | 0.0053203 | -0.00031535 | 0.00064087 | -60.8505 | 62.0453 | -61.1481 | 0.041199 | 0.041199 | 0.027466 | -0.19226 | 0.20142 | 0.15564 | -0.36621 | -0.36621 | 0.045776 | -0.068665 | 60.8231 | -61.9583 | 60.4156 | -61.8439 | 0.29755
420.4688 | 123.1705 | -60.791 | 62.0132 | -0.032697 | 0.016317 | 0.013163 | -0.0027058 | -0.00044752 | -0.00031535 | 0.0021363 | -60.9009 | 62.0316 | -61.1435 | 0.09613 | 0.1236 | 0.13733 | -0.068665 | 0.3479 | 0.20599 | -0.2243 | -0.35248 | 0.01831 | -0.10986 | 60.8871 | -61.8896 | 60.5667 | -61.8073 | 0.24261
421.5781 | 123.0057 | -60.8231 | 62.059 | 0.1733 | 0.021016 | 0.01829 | 0.0069072 | 0.0068157 | -0.0028788 | 0.0019227 | -60.9375 | 62.1048 | -61.171 | -0.050354 | -0.059509 | -0.086975 | -0.004578 | 0.10529 | 0.20142 | -0.32501 | -0.3479 | 0.045776 | -0.11444 | 60.7727 | -62.1185 | 60.498 | -61.8576 | 0.23346
422.1406 | 123.0652 | -60.8231 | 62.027 | 0.28774 | 0.019307 | 0.016795 | 0.004771 | 0.0046793 | 0.0018208 | -0.00064093 | -60.9146 | 62.0728 | -61.1389 | -0.009155 | -0.032043 | -0.059509 | -0.09613 | 0.11444 | 0.17395 | -0.34332 | -0.31586 | 0.045776 | -0.091553 | 60.8139 | -62.059 | 60.4797 | -61.853 | 0.2243
423.1719 | 123.0881 | -60.7819 | 62.0728 | -0.14714 | 0.020376 | 0.015513 | 0.004771 | 0.0027567 | -0.0018108 | 6.6667e-08 | -60.8551 | 62.1552 | -61.1435 | 0.054932 | 0.050354 | 0.073242 | 0.07782 | 0.27466 | 0.24261 | -0.25635 | -0.36163 | 0.082397 | -0.073243 | 60.8368 | -62.0224 | 60.5255 | -61.8301 | 0.28839
427.2656 | 123.1293 | -60.791 | 62.059 | 0.058855 | 0.017598 | 0.01295 | -0.0009968 | 0.0016887 | -0.00052895 | -0.00085453 | -60.8551 | 62.0544 | -61.116 | 0.10071 | 0.13733 | 0.15564 | -0.018311 | 0.33875 | 0.21515 | -0.21973 | -0.32501 | -0.004578 | -0.064087 | 60.8917 | -61.9217 | 60.5713 | -61.8439 | 0.26093
427.7344 | 123.056 | -60.8047 | 62.0499 | -0.11662 | 0.021016 | 0.016154 | 0.0079752 | 0.0031841 | -0.0026652 | 0.00064087 | -60.8459 | 62.1323 | -61.1298 | 0.054932 | 0.036621 | 0.045776 | 0.027466 | 0.23346 | 0.23804 | -0.27924 | -0.32501 | 0.082397 | -0.041198 | 60.8597 | -62.0132 | 60.5255 | -61.8118 | 0.28381
428.2656 | 123.0927 | -60.7864 | 62.0407 | 0.5624 | 0.016317 | 0.014659 | -0.0016378 | 0.0055339 | -0.00095615 | 0.0032043 | -60.9375 | 62.0041 | -61.1572 | 0.032043 | 0.068665 | 0.068665 | -0.059509 | 0.25177 | 0.18768 | -0.27466 | -0.37079 | -0.036621 | -0.15106 | 60.8185 | -61.972 | 60.5118 | -61.853 | 0.21973
428.75 | 123.0331 | -60.8139 | 62.0636 | -0.22343 | 0.018667 | 0.016581 | 0.0022074 | -0.00087492 | -0.0018108 | -0.0010681 | -60.9146 | 62.1048 | -61.1343 | 0.013733 | 0.022888 | 0.082397 | 0.15106 | 0.27008 | 0.2655 | -0.1831 | -0.32043 | 0.041198 | -0.10071 | 60.8276 | -62.0407 | 60.6308 | -61.7981 | 0.21973
429.7344 | 123.1293 | -60.7773 | 61.9995 | 0.13515 | 0.021871 | 0.016795 | 0.0056254 | 0.0025431 | 0.00075285 | -0.00085453 | -60.8459 | 62.0499 | -61.1389 | 0.036621 | 0.022888 | 0.022888 | -0.18768 | 0.19684 | 0.15106 | -0.36621 | -0.36163 | 0.050354 | -0.068664 | 60.8139 | -61.9766 | 60.4111 | -61.8484 | 0.29297
430.7344 | 123.143 | -60.8002 | 61.9949 | 0.34114 | 0.019735 | 0.020213 | 0.0045574 | 0.0027567 | -0.00052895 | 0.0010681 | -60.8688 | 62.0865 | -61.1389 | 0.027466 | 0 | -0.018311 | -0.14191 | 0.24261 | 0.16479 | -0.36163 | -0.33875 | 0.091553 | -0.068664 | 60.8276 | -61.9949 | 60.4385 | -61.8301 | 0.27008
431.7344 | 123.1201 | -60.8093 | 61.9858 | 0.31063 | 0.021016 | 0.015086 | 0.0060526 | 0.0029705 | 0.002248 | 0.0012817 | -60.8917 | 62.0956 | -61.1664 | 0.018311 | 0.018311 | -0.009155 | -0.14648 | 0.20142 | 0.15564 | -0.37537 | -0.35706 | 0.10986 | -0.082398 | 60.8276 | -61.9675 | 60.434 | -61.8301 | 0.27466
432.7344 | 123.1293 | -60.8139 | 61.972 | 0.27248 | 0.018453 | 0.020426 | 0.0039164 | 0.0040385 | 0.00053925 | -0.00021353 | -60.8505 | 62.0453 | -61.1618 | 0.045776 | 0.045776 | 0.032043 | -0.18768 | 0.21515 | 0.15106 | -0.36163 | -0.3479 | 0.073242 | -0.036621 | 60.8597 | -61.9263 | 60.4523 | -61.821 | 0.31128
433.7656 | 123.1155 | -60.7864 | 62.0316 | -0.18529 | 0.019948 | 0.016368 | 0.0002848 | -0.00023392 | -0.0011698 | -0.00042733 | -60.8917 | 62.0773 | -61.1389 | 0.086975 | 0.09613 | 0.12817 | 0.045776 | 0.32501 | 0.24719 | -0.19684 | -0.35248 | 0.045777 | -0.10529 | 60.8734 | -61.9354 | 60.5896 | -61.7844 | 0.24719
434.7344 | 123.1384 | -60.791 | 62.0132 | 0.36403 | 0.01888 | 0.018504 | 0.0071208 | 0.0048931 | 0.0024618 | 0.00085447 | -60.8643 | 62.0728 | -61.1298 | 0.041199 | 0.018311 | 0 | -0.18768 | 0.21515 | 0.14648 | -0.37079 | -0.33875 | 0.059509 | -0.073242 | 60.8322 | -61.9949 | 60.4202 | -61.8668 | 0.2655
435.7656 | 123.1384 | -60.7681 | 62.0087 | 0.035967 | 0.019735 | 0.015086 | 0.0004984 | 0.0012615 | 0.002248 | 0.0012817 | -60.8688 | 62.0361 | -61.1252 | 0.050354 | 0.045776 | 0.032043 | -0.19226 | 0.2243 | 0.16022 | -0.33875 | -0.35706 | 0.027466 | -0.10071 | 60.8185 | -61.9629 | 60.4294 | -61.8484 | 0.25635
436.7344 | 123.111 | -60.7819 | 62.0087 | 0.24196 | 0.022298 | 0.023417 | 0.00648 | 0.0025431 | 0.0013936 | 0.00042727 | -60.8963 | 62.0865 | -61.1343 | 0.004578 | 0 | -0.018311 | -0.14648 | 0.16479 | 0.15564 | -0.3479 | -0.35248 | 0.07782 | -0.11444 | 60.7864 | -62.0087 | 60.434 | -61.853 | 0.23804
437.7344 | 123.1476 | -60.7727 | 62.0041 | -0.017439 | 0.017598 | 0.014018 | -0.0016378 | 0.00019328 | 0.0016072 | -0.0012817 | -60.8917 | 62.0178 | -61.1343 | 0.091553 | 0.11902 | 0.16937 | -0.068665 | 0.33875 | 0.21515 | -0.21057 | -0.36163 | 0.013733 | -0.11902 | 60.8643 | -61.8851 | 60.5621 | -61.7889 | 0.24261
438.7344 | 123.143 | -60.791 | 62.027 | 0.44032 | 0.020162 | 0.019145 | 0.0054118 | 0.0019023 | -0.00010175 | -0.0025635 | -60.8597 | 62.0865 | -61.1206 | 0.045776 | 0.018311 | 0.022888 | -0.18768 | 0.20599 | 0.14648 | -0.36621 | -0.32959 | 0.059509 | -0.068664 | 60.8368 | -62.0087 | 60.4248 | -61.8805 | 0.26093
439.7344 | 123.0331 | -60.8139 | 62.0316 | 0.31825 | 0.02123 | 0.016368 | 0.005839 | 0.0053203 | -0.00010175 | 0.00064087 | -60.9192 | 62.1048 | -61.1755 | -0.022888 | -0.059509 | -0.091553 | -0.07782 | 0.10529 | 0.18768 | -0.33875 | -0.36163 | 0.073242 | -0.10529 | 60.791 | -62.0911 | 60.4752 | -61.8439 | 0.25635
440.7344 | 123.056 | -60.8231 | 62.0087 | -1.0093 | 0.021444 | 0.018504 | 0.0051982 | 0.0021159 | -0.00010175 | 6.6667e-08 | -60.9467 | 62.1368 | -61.1481 | -0.032043 | -0.073242 | -0.10529 | -0.032043 | 0.10071 | 0.2243 | -0.32044 | -0.32501 | 0.12817 | -0.1236 | 60.791 | -62.0819 | 60.5026 | -61.7844 | 0.20142
441.7344 | 123.0927 | -60.7773 | 62.0224 | 0.2267 | 0.021871 | 0.015513 | 0.0049846 | 0.0031841 | 0.0016072 | -0.0021361 | -60.9192 | 62.1048 | -61.1801 | -0.022888 | -0.032043 | -0.050354 | -0.09613 | 0.12817 | 0.16479 | -0.35706 | -0.40283 | 0.082397 | -0.14191 | 60.7544 | -62.0544 | 60.4202 | -61.8576 | 0.26093
442.75 | 123.1338 | -60.7773 | 62.0178 | -0.093733 | 0.01354 | 0.011027 | -0.0018514 | 0.00040688 | -0.0015972 | 0.00042727 | -60.8551 | 62.0453 | -61.1069 | 0.11444 | 0.13275 | 0.16022 | -0.045776 | 0.36163 | 0.21973 | -0.21515 | -0.32959 | 0.027466 | -0.07782 | 60.8917 | -61.8851 | 60.5621 | -61.7981 | 0.25177
443.7344 | 123.0515 | -60.8414 | 62.0361 | -0.45231 | 0.021444 | 0.01829 | 0.0071208 | 0.0036113 | 0.0013936 | -0.0023499 | -60.965 | 62.1185 | -61.1526 | -0.041199 | -0.073242 | -0.091553 | -0.022888 | 0.10986 | 0.21515 | -0.34332 | -0.31128 | 0.082397 | -0.1236 | 60.8002 | -62.1094 | 60.498 | -61.821 | 0.18768
444.7344 | 122.9965 | -60.8276 | 62.0407 | 0.18093 | 0.02123 | 0.019999 | 0.0079752 | 0.0040385 | 0.0016072 | 0.00021367 | -60.8963 | 62.1506 | -61.1618 | -0.045776 | -0.07782 | -0.068665 | 0.013733 | 0.082397 | 0.21057 | -0.33417 | -0.33417 | 0.10986 | -0.068664 | 60.7819 | -62.1185 | 60.4935 | -61.8301 | 0.2655
445.7344 | 123.0057 | -60.8322 | 62.0361 | 0.14278 | 0.022939 | 0.021067 | 0.005839 | 0.0053203 | 0.00032545 | 0.00021367 | -60.8871 | 62.1552 | -61.1664 | -0.018311 | -0.045776 | -0.054932 | 0.018311 | 0.13275 | 0.23804 | -0.3067 | -0.33417 | 0.11902 | -0.054932 | 60.8139 | -62.0819 | 60.5255 | -61.7981 | 0.27924
446.7344 | 122.9965 | -60.8368 | 62.0407 | 0.19618 | 0.019948 | 0.022563 | 0.0056254 | 0.0042521 | -0.00031535 | -0.00021353 | -60.9375 | 62.146 | -61.1893 | -0.050354 | -0.059509 | -0.091553 | -0.004578 | 0.091553 | 0.19226 | -0.32959 | -0.35248 | 0.10529 | -0.10071 | 60.7864 | -62.1002 | 60.5072 | -61.8484 | 0.25177
447.7344 | 123.143 | -60.7636 | 61.9629 | 0.24196 | 0.018453 | 0.02299 | -0.000356 | 0.0063883 | -0.0011698 | 0.0010681 | -61.0062 | 62.0132 | -61.171 | 0.07782 | 0.064087 | 0.045776 | -0.14648 | 0.20599 | 0.15564 | -0.30212 | -0.40741 | 0.050354 | -0.24262 | 60.8414 | -61.8988 | 60.4614 | -61.8073 | 0.16479
448.7344 | 123.0286 | -60.8276 | 61.9995 | 0.1733 | 0.019948 | 0.021495 | 0.0045574 | 0.0019023 | -0.00095615 | 0.0014953 | -60.9283 | 62.1552 | -61.1481 | -0.054932 | -0.068665 | -0.10986 | -0.013733 | 0.082397 | 0.20142 | -0.35706 | -0.32043 | 0.15564 | -0.10071 | 60.7727 | -62.0682 | 60.4706 | -61.7981 | 0.21973
449.7656 | 123.0103 | -60.8322 | 62.0041 | 0.10463 | 0.02123 | 0.01829 | 0.0073344 | 0.0051067 | 0.00075285 | -0.00064093 | -60.9055 | 62.1597 | -61.1389 | -0.064087 | -0.073242 | -0.086975 | 0.013733 | 0.073242 | 0.20142 | -0.36163 | -0.3067 | 0.15564 | -0.073243 | 60.7681 | -62.0773 | 60.4706 | -61.8027 | 0.23346
450.7344 | 123.0103 | -60.8139 | 62.0544 | 0.089373 | 0.022725 | 0.021281 | 0.0060526 | 0.0055339 | -0.0024516 | -0.0010681 | -60.9055 | 62.1506 | -61.1481 | -0.064087 | -0.073242 | -0.091553 | 0.027466 | 0.091553 | 0.21973 | -0.36163 | -0.33417 | 0.096131 | -0.091553 | 60.7498 | -62.1277 | 60.4523 | -61.8347 | 0.24261
451.7812 | 123.0789 | -60.7956 | 62.0407 | -0.032697 | 0.019521 | 0.018931 | 0.005839 | 0.0051067 | -0.0011698 | 0.00042727 | -60.8597 | 62.1323 | -61.1481 | 0.032043 | 0.045776 | 0.054932 | 0.041199 | 0.24719 | 0.25177 | -0.27466 | -0.35248 | 0.091553 | -0.064087 | 60.8276 | -61.9949 | 60.5209 | -61.7889 | 0.28839
452.7344 | 122.9828 | -60.8139 | 62.0132 | 0.13515 | 0.020589 | 0.02064 | 0.0079752 | 0.0053203 | 0.00053925 | 0.00042727 | -60.9329 | 62.1552 | -61.1618 | -0.086975 | -0.068665 | -0.09613 | -0.004578 | 0.10529 | 0.20599 | -0.34332 | -0.3479 | 0.14191 | -0.11902 | 60.7269 | -62.0819 | 60.4706 | -61.8073 | 0.22888
453.7656 | 123.024 | -60.8139 | 62.027 | -0.25395 | 0.016958 | 0.014872 | -0.0012106 | 0.0021159 | 0.00075285 | 0.0023499 | -60.9512 | 62.1185 | -61.1801 | -0.009155 | 0.045776 | 0.050354 | 0.13733 | 0.24261 | 0.27924 | -0.19684 | -0.36621 | 0.091552 | -0.13733 | 60.8047 | -61.9812 | 60.6171 | -61.7477 | 0.22888
454.7344 | 123.024 | -60.8368 | 62.059 | 0.081743 | 0.019094 | 0.024272 | 0.0062662 | 0.0038249 | -0.00095615 | 6.6667e-08 | -60.8963 | 62.1506 | -61.1481 | -0.032043 | -0.032043 | -0.050354 | 0.018311 | 0.13733 | 0.22888 | -0.31128 | -0.31128 | 0.091553 | -0.059509 | 60.8047 | -62.0911 | 60.5255 | -61.8301 | 0.25177
455.7656 | 123.0469 | -60.8047 | 62.0636 | -0.39891 | 0.019735 | 0.015299 | 0.0011394 | 0.0014751 | 0.0018208 | -0.00042733 | -61.0428 | 62.1368 | -61.1755 | -0.004578 | 0 | 0.064087 | 0.17395 | 0.25635 | 0.27008 | -0.25177 | -0.37079 | 0.073242 | -0.23804 | 60.8002 | -62.0636 | 60.553 | -61.7935 | 0.13275
456.7344 | 123.0515 | -60.8185 | 62.0224 | 0.12752 | 0.021444 | 0.017436 | 0.0056254 | 0.0063883 | 0.00032545 | 0.00021367 | -60.8597 | 62.1368 | -61.1389 | 0.022888 | -0.004578 | 0.018311 | 0.027466 | 0.19684 | 0.23346 | -0.27466 | -0.32044 | 0.11444 | -0.041199 | 60.8414 | -62.027 | 60.5438 | -61.7889 | 0.27924
457.7656 | 123.0698 | -60.7864 | 62.0636 | -0.20817 | 0.018026 | 0.015086 | -0.002065 | 0.0031841 | 0.00032545 | 0.00042727 | -60.8963 | 62.0956 | -61.1435 | 0.064087 | 0.086975 | 0.1236 | 0.086975 | 0.29755 | 0.28839 | -0.19226 | -0.35706 | 0.032043 | -0.10986 | 60.8505 | -61.9766 | 60.5942 | -61.7752 | 0.24719
458.7344 | 123.0789 | -60.8002 | 62.0544 | -0.0098092 | 0.019094 | 0.017008 | 0.005839 | 0.0061747 | 0.0020344 | -0.0019225 | -60.8368 | 62.1368 | -61.116 | 0.041199 | 0.022888 | 0.036621 | 0.027466 | 0.2243 | 0.21973 | -0.2655 | -0.31586 | 0.082398 | -0.036621 | 60.8414 | -62.0316 | 60.5347 | -61.8347 | 0.27924
459.7656 | 123.1155 | -60.7864 | 62.0132 | 0.081743 | 0.015462 | 0.014018 | -0.0067648 | 0.0029705 | 0.0020344 | 0.00021367 | -60.9375 | 62.027 | -61.1481 | -0.018311 | 0.032043 | 0.064087 | -0.068665 | 0.25177 | 0.20599 | -0.27008 | -0.36163 | 0.013733 | -0.15106 | 60.7681 | -61.9812 | 60.5164 | -61.8073 | 0.21057
460.7344 | 123.0972 | -60.8231 | 62.0453 | -0.13188 | 0.019521 | 0.018931 | 0.0066936 | 0.0019023 | -0.00052895 | 0.00042727 | -60.8505 | 62.1506 | -61.1343 | 0.073242 | 0.022888 | 0.068665 | 0.068665 | 0.26093 | 0.25177 | -0.24719 | -0.31128 | 0.10529 | -0.027466 | 60.8963 | -62.0224 | 60.5759 | -61.7935 | 0.28381
461.7812 | 123.23 | -60.7407 | 62.0728 | -0.10899 | 0.015035 | 0.016795 | -0.0027058 | 0.0025431 | -0.00010175 | 6.6667e-08 | -60.8551 | 62.027 | -61.1114 | 0.10529 | 0.1236 | 0.16479 | -0.036621 | 0.37079 | 0.23346 | -0.19684 | -0.37079 | -0.045776 | -0.11444 | 60.8459 | -61.9492 | 60.5438 | -61.8393 | 0.25635
462.7344 | 123.0606 | -60.8047 | 62.0544 | -0.12425 | 0.019307 | 0.014445 | 0.0062662 | 0.0033977 | 0.00096645 | 0.00021367 | -60.8643 | 62.146 | -61.1298 | 0.050354 | 0.036621 | 0.086975 | 0.041199 | 0.24261 | 0.25635 | -0.25635 | -0.32501 | 0.091553 | -0.059509 | 60.8551 | -62.0178 | 60.5484 | -61.7981 | 0.2655
463.7656 | 123.143 | -60.8002 | 62.0087 | -0.22343 | 0.013326 | 0.017863 | -0.0009968 | 0.0012615 | -0.00074255 | -0.0010681 | -60.8643 | 62.0499 | -61.1298 | 0.10071 | 0.10071 | 0.15106 | 0.027466 | 0.35706 | 0.24261 | -0.19226 | -0.32959 | 0.041199 | -0.064087 | 60.9009 | -61.908 | 60.6079 | -61.7661 | 0.2655
464.7344 | 123.0515 | -60.8231 | 62.0636 | -0.15477 | 0.019307 | 0.014445 | 0.0043436 | 0.0014751 | -0.00031535 | -0.0021361 | -60.9055 | 62.1323 | -61.1206 | 0.032043 | 0.018311 | 0.050354 | 0.10071 | 0.2243 | 0.27924 | -0.20599 | -0.29755 | 0.068664 | -0.082398 | 60.8551 | -62.0453 | 60.6171 | -61.7844 | 0.21515
465.7656 | 123.0927 | -60.8047 | 62.0178 | 0.25722 | 0.018667 | 0.01594 | 0.005839 | 0.0042521 | 0.0020344 | -0.0017089 | -60.8963 | 62.0865 | -61.1618 | -0.022888 | -0.027466 | -0.045776 | -0.1236 | 0.13733 | 0.18768 | -0.32044 | -0.35705 | 0.068665 | -0.091552 | 60.7819 | -62.0453 | 60.4843 | -61.8301 | 0.2655
466.7344 | 123.0331 | -60.8093 | 62.0728 | -0.22343 | 0.017598 | 0.01829 | 0.0004984 | 0.0027567 | -0.00095615 | 0.00042727 | -60.8917 | 62.1048 | -61.1343 | 0.036621 | 0.018311 | 0.018311 | 0.14191 | 0.28839 | 0.28839 | -0.15564 | -0.32501 | 0.032043 | -0.082398 | 60.8459 | -62.0544 | 60.6537 | -61.7844 | 0.24261
467.7656 | 123.1338 | -60.7681 | 62.0087 | -0.14714 | 0.016317 | 0.016581 | -0.0033468 | 0.0021159 | -0.0020244 | 0.00085447 | -60.878 | 62.027 | -61.1069 | 0.32044 | 0.55389 | 0.42572 | -0.66376 | -0.018311 | 0.24261 | -0.16479 | -0.33875 | 0.018311 | -0.10986 | 61.0886 | -61.4548 | 60.6033 | -61.7661 | 0.22888
468.7344 | 123.0286 | -60.8139 | 62.0728 | -0.1624 | 0.019094 | 0.016581 | 0.00413 | 0.0029705 | 0.0018208 | -0.00042733 | -60.9055 | 62.1002 | -61.1526 | 0.050354 | 0.082397 | -0.004578 | 0.054932 | 0.21057 | 0.25635 | -0.21515 | -0.33874 | 0.027466 | -0.091553 | 60.8643 | -61.9904 | 60.5988 | -61.8164 | 0.24719
469.7656 | 123.1522 | -60.7773 | 61.9995 | 0.28011 | 0.021016 | 0.017436 | 0.0034892 | 0.0040385 | 0.00118 | -0.0014953 | -60.8322 | 62.0453 | -61.1343 | 0.045776 | 0.050354 | 0.032043 | -0.1831 | 0.21057 | 0.14191 | -0.35706 | -0.35706 | 0.045776 | -0.054931 | 60.8231 | -61.9492 | 60.4202 | -61.8576 | 0.30212
470.7344 | 123.0423 | -60.8231 | 62.0453 | -0.20054 | 0.018667 | 0.014872 | 0.0002848 | 0.0023295 | 0.00032545 | 0.00042727 | -60.9238 | 62.114 | -61.1664 | 0.027466 | 0.022888 | 0.027466 | 0.13733 | 0.24261 | 0.28839 | -0.17853 | -0.34332 | 0.068665 | -0.10071 | 60.8505 | -62.0224 | 60.6445 | -61.7569 | 0.24262
471.7812 | 123.143 | -60.7315 | 62.0178 | 0.013079 | 0.017598 | 0.014872 | -0.0024922 | -2.0324e-05 | -0.0033062 | 0.00021367 | -60.9009 | 62.0178 | -61.1435 | 0.10071 | 0.10529 | 0.12817 | -0.07782 | 0.33875 | 0.20142 | -0.23346 | -0.41199 | 0 | -0.16937 | 60.8322 | -61.9125 | 60.498 | -61.8164 | 0.24261
472.7344 | 123.056 | -60.7636 | 62.059 | -0.17766 | 0.017812 | 0.012736 | 0.0026346 | -2.0324e-05 | -0.00010175 | 0.0012817 | -60.878 | 62.0682 | -61.1343 | 0.059509 | 0.054932 | 0.091553 | 0.091553 | 0.31128 | 0.23804 | -0.21057 | -0.37079 | 0.009155 | -0.11444 | 60.8231 | -62.0041 | 60.553 | -61.821 | 0.25635
473.7656 | 123.1384 | -60.7773 | 62.0132 | 0.27248 | 0.01888 | 0.021708 | 0.0034892 | 0.0033977 | 0.00118 | -0.0014953 | -60.8322 | 62.0178 | -61.1206 | 0.082397 | 0.09613 | 0.068665 | -0.17395 | 0.23804 | 0.18768 | -0.31586 | -0.34332 | 0.004577 | -0.054931 | 60.8597 | -61.9171 | 60.4614 | -61.8256 | 0.28839
474.7344 | 123.1293 | -60.7819 | 62.0407 | -0.13951 | 0.017598 | 0.016581 | 0.0015666 | -0.00066112 | -0.00052895 | -0.00064093 | -60.8505 | 62.027 | -61.1435 | 0.10529 | 0.091553 | 0.1236 | 0 | 0.3479 | 0.23804 | -0.20599 | -0.36163 | -0.013732 | -0.068665 | 60.8871 | -61.9492 | 60.5759 | -61.8027 | 0.29297
475.7656 | 123.1064 | -60.7819 | 62.0178 | 0.20381 | 0.017171 | 0.017008 | 0.001353 | -0.0015157 | -0.0020244 | 0.00064087 | -60.8917 | 62.0087 | -61.116 | 0.004578 | 0.009155 | 0.013733 | -0.12817 | 0.19684 | 0.1831 | -0.29755 | -0.33417 | -0.009155 | -0.10986 | 60.7864 | -62.0087 | 60.4843 | -61.8347 | 0.2243
476.7344 | 123.0194 | -60.8093 | 62.0682 | -0.18529 | 0.018239 | 0.018077 | 0.0034892 | 0.00040688 | 0.0020344 | -0.0021361 | -60.9146 | 62.1323 | -61.1481 | -0.018311 | 0.091553 | 0.054932 | 0.027466 | 0.17853 | 0.27008 | -0.19226 | -0.33875 | 0.064087 | -0.10529 | 60.791 | -61.9766 | 60.6171 | -61.7981 | 0.23346
477.7656 | 123.0286 | -60.8276 | 62.059 | 0.20381 | 0.019948 | 0.015727 | 0.0086162 | 0.0046793 | 0.00011185 | 0.00085447 | -60.9238 | 62.1231 | -61.1618 | -0.041199 | -0.054932 | -0.091553 | -0.018311 | 0.07782 | 0.20142 | -0.34332 | -0.33417 | 0.064087 | -0.09613 | 60.7864 | -62.114 | 60.4843 | -61.8576 | 0.23804
478.7344 | 123.1201 | -60.7727 | 62.0178 | -0.11662 | 0.017385 | 0.01295 | -0.0005696 | 0.0019023 | -0.0020244 | 0.0010681 | -60.9787 | 62.027 | -61.116 | 0.19226 | 0.064087 | 0 | -0.032043 | 0.36163 | 0.22888 | -0.24719 | -0.34332 | 0.009156 | -0.20599 | 60.965 | -61.9537 | 60.5255 | -61.7889 | 0.13733
479.7656 | 123.0652 | -60.8185 | 62.0132 | 0.23433 | 0.020589 | 0.019999 | 0.0062662 | 0.0029705 | -0.0018108 | -0.0010681 | -60.9055 | 62.1277 | -61.1618 | -0.032043 | -0.054932 | -0.068665 | -0.086975 | 0.10071 | 0.17853 | -0.33875 | -0.34332 | 0.11444 | -0.086976 | 60.7864 | -62.0682 | 60.4797 | -61.8347 | 0.25635
480.7344 | 123.1613 | -60.7498 | 62.027 | -0.10136 | 0.015462 | 0.013377 | -0.0014242 | 0.0033977 | 0.00011185 | -0.00021353 | -60.8322 | 62.0316 | -61.1206 | 0.11902 | 0.11902 | 0.15106 | -0.045776 | 0.36621 | 0.22888 | -0.18768 | -0.37079 | 0.004577 | -0.082397 | 60.8688 | -61.908 | 60.5621 | -61.7981 | 0.28839
481.7812 | 123.0423 | -60.8185 | 62.0728 | -0.13951 | 0.01888 | 0.018077 | 0.0017802 | 0.00019328 | -0.0011698 | 0.00021367 | -60.9329 | 62.0911 | -61.1572 | 0.027466 | 0.036621 | 0.041199 | 0.13733 | 0.24719 | 0.2655 | -0.16937 | -0.33875 | 0.01831 | -0.11444 | 60.8459 | -62.0361 | 60.6491 | -61.8073 | 0.22431
482.7344 | 123.1476 | -60.7269 | 62.0499 | -0.13951 | 0.017171 | 0.014659 | -0.0014242 | -0.00044752 | -0.0018108 | -0.00085453 | -60.8414 | 62.027 | -61.1252 | 0.12817 | 0.11444 | 0.16937 | -0.041199 | 0.36621 | 0.24261 | -0.21515 | -0.39825 | -0.022888 | -0.11444 | 60.8551 | -61.9354 | 60.5118 | -61.8073 | 0.28381
483.7344 | 123.1567 | -60.7681 | 62.0544 | -0.078474 | 0.015676 | 0.017649 | -0.0039876 | 0.00062048 | -0.00095615 | 6.6667e-08 | -60.8276 | 62.0087 | -61.1481 | 0.14648 | 0.12817 | 0.16022 | -0.050354 | 0.35248 | 0.21515 | -0.20142 | -0.37994 | -0.045776 | -0.05951 | 60.9146 | -61.9263 | 60.5667 | -61.8393 | 0.32043
484.7344 | 123.143 | -60.7544 | 62.0407 | 0.074114 | 0.013753 | 0.011027 | -0.0009968 | -0.0015157 | -0.00010175 | 6.6667e-08 | -60.9009 | 62.0224 | -61.1343 | 0.068665 | 0.068665 | 0.09613 | -0.045776 | 0.28381 | 0.21515 | -0.24719 | -0.37994 | -0.01831 | -0.14648 | 60.8231 | -61.972 | 60.5072 | -61.8256 | 0.23346
485.7344 | 123.1338 | -60.7636 | 62.0544 | 0.081743 | 0.017598 | 0.015727 | 0.0002848 | -0.00087492 | 0.00075285 | -0.00085453 | -60.9192 | 62.0178 | -61.1481 | 0.059509 | 0.045776 | 0.050354 | -0.073242 | 0.25635 | 0.21973 | -0.25177 | -0.38452 | -0.036621 | -0.15564 | 60.8231 | -62.0087 | 60.5118 | -61.8347 | 0.22888
486.7812 | 123.1613 | -60.7681 | 61.9995 | 0.29537 | 0.018453 | 0.020213 | 0.0043436 | 0.0016887 | -0.00052895 | 6.6667e-08 | -60.8139 | 62.0544 | -61.1435 | 0.073242 | 0.045776 | 0.027466 | -0.54016 | -0.19226 | 0.1236 | -0.43488 | -0.37537 | 0.054931 | -0.045777 | 60.8414 | -61.9537 | 60.3333 | -61.8759 | 0.32959
487.7344 | 123.143 | -60.7773 | 62.0316 | 0.058855 | 0.016744 | 0.014872 | 7.12e-05 | -0.0045065 | 0.0024618 | -0.00064093 | -60.9146 | 62.0132 | -61.1481 | 0.068665 | 0.086975 | 0.091553 | -0.054932 | 0.27924 | 0.20599 | -0.23804 | -0.37079 | -0.01831 | -0.13733 | 60.8459 | -61.9446 | 60.5392 | -61.8256 | 0.23346
488.75 | 123.0423 | -60.8185 | 62.0819 | -0.17003 | 0.017598 | 0.020426 | 0.0090434 | 0.0016887 | -0.00031535 | -0.0012817 | -60.9741 | 62.1323 | -61.1298 | 0.09613 | -0.009155 | -0.059509 | 0.082397 | 0.20142 | 0.26093 | -0.21973 | -0.31128 | 0.050354 | -0.15564 | 60.9146 | -62.0911 | 60.5988 | -61.821 | 0.15564
489.7344 | 123.0881 | -60.7773 | 62.027 | 0.081743 | 0.018026 | 0.01594 | -0.0007832 | -0.0045065 | -0.00074255 | -0.0017089 | -60.9329 | 62.0361 | -61.1298 | -0.013733 | -0.07782 | -0.018311 | -0.07782 | 0.23346 | 0.20599 | -0.27008 | -0.35248 | 0.009155 | -0.15564 | 60.7635 | -62.1048 | 60.5072 | -61.821 | 0.19684
490.7656 | 123.0698 | -60.8139 | 62.0361 | 0.21144 | 0.02123 | 0.019358 | 0.010112 | 0.0019023 | 0.00096645 | -0.00085453 | -60.9009 | 62.1185 | -61.1526 | -0.032043 | -0.073242 | -0.068665 | -0.72327 | -0.3891 | 0.16022 | -0.3891 | -0.33874 | 0.082397 | -0.086975 | 60.7819 | -62.1094 | 60.4248 | -61.8759 | 0.25177
491.75 | 122.9965 | -60.8322 | 62.0316 | 0.18093 | 0.020589 | 0.019358 | 0.0051982 | 0.0033977 | 0.00053925 | 0.00021367 | -60.9146 | 62.1506 | -61.1343 | -0.036621 | -0.082397 | -0.10986 | -0.004578 | 0.073242 | 0.20599 | -0.33417 | -0.30212 | 0.11902 | -0.082398 | 60.7956 | -62.114 | 60.498 | -61.8256 | 0.21973
492.7656 | 123.0789 | -60.8093 | 62.027 | -0.0021797 | 0.017598 | 0.016368 | 0.0069072 | 0.0057475 | -0.00052895 | -0.0032043 | -60.8414 | 62.1506 | -61.1664 | 0.086975 | 0.018311 | -0.27008 | 0.13275 | 0.3479 | 0.21515 | -0.28839 | -0.35706 | 0.1236 | -0.032044 | 60.8963 | -62.0087 | 60.5209 | -61.8118 | 0.32501
493.7344 | 123.0972 | -60.7956 | 62.0087 | 0.12752 | 0.018026 | 0.018931 | -0.0046284 | 0.0025431 | -0.00010175 | 0.00064087 | -60.9283 | 62.0224 | -61.1435 | 0.041199 | 0.059509 | 0.054932 | -0.073242 | 0.2243 | 0.18768 | -0.27924 | -0.3479 | 0.013733 | -0.13275 | 60.8368 | -61.9492 | 60.5164 | -61.821 | 0.21515
494.7656 | 123.0103 | -60.8231 | 62.0544 | 0.081743 | 0.021016 | 0.018717 | 0.0094706 | 0.0042521 | -0.002238 | -0.00085453 | -60.878 | 62.1552 | -61.1252 | 0.004578 | -0.022888 | -0.032043 | -0.004578 | 0.11902 | 0.21515 | -0.31128 | -0.30212 | 0.10071 | -0.054932 | 60.8276 | -62.0773 | 60.5118 | -61.8393 | 0.24719
495.7344 | 123.0927 | -60.8002 | 62.0132 | 0.2267 | 0.017385 | 0.016368 | -0.0029196 | 0.0023295 | 0.00096645 | 6.6667e-08 | -60.9421 | 62.0453 | -61.1435 | 0 | 0.009155 | 0.041199 | -0.09613 | 0.21057 | 0.1831 | -0.29297 | -0.34332 | 0.032043 | -0.14191 | 60.8002 | -62.0041 | 60.5072 | -61.8301 | 0.20142
496.7812 | 123.0286 | -60.8185 | 62.0316 | 0.24959 | 0.022939 | 0.01829 | 0.0056254 | -0.00066112 | 0.00011185 | 0.00021367 | -60.91 | 62.146 | -61.1618 | -0.12817 | -0.1236 | 0.054932 | 0.07782 | 0.10071 | 0.20142 | -0.31128 | -0.34332 | 0.11444 | -0.091553 | 60.6903 | -62.1552 | 60.5072 | -61.8301 | 0.25177
497.7344 | 123.1705 | -60.7544 | 62.0132 | -0.047956 | 0.016317 | 0.014018 | -0.0009968 | 0.0019023 | 0.00053925 | 0.0014953 | -60.91 | 62.0453 | -61.1343 | 0.07782 | 0.091553 | 0.13275 | -0.068665 | 0.31586 | 0.20142 | -0.24261 | -0.37994 | 0.032043 | -0.15564 | 60.8322 | -61.9217 | 60.5118 | -61.8118 | 0.2243
498.7656 | 123.0698 | -60.8002 | 62.0132 | 0.2267 | 0.018667 | 0.01829 | -0.000356 | -0.00087492 | -0.00052895 | 6.6667e-08 | -60.9146 | 62.0087 | -61.1298 | 0.009155 | 0.027466 | 0.032043 | -0.11902 | 0.21057 | 0.16479 | -0.3067 | -0.32959 | -0.004578 | -0.11444 | 60.8093 | -61.9858 | 60.4935 | -61.8484 | 0.21515
499.7344 | 123.1064 | -60.7727 | 61.9995 | 0.21144 | 0.015889 | 0.01594 | 0.000712 | -0.0015157 | -0.00052895 | 0.0021363 | -60.91 | 62.0178 | -61.1572 | 0.022888 | 0.018311 | 0.009155 | -0.10071 | 0.20599 | 0.16479 | -0.29755 | -0.38452 | 0.01831 | -0.13733 | 60.7956 | -61.9812 | 60.4752 | -61.8347 | 0.24719
500.7656 | 123.0606 | -60.7956 | 62.0728 | -0.086103 | 0.018026 | 0.016581 | 0.0071208 | -0.00087492 | -0.00052895 | -0.0010681 | -60.8826 | 62.146 | -61.1435 | 0.041199 | 0.041199 | 0.068665 | 0.091553 | 0.24719 | 0.24719 | -0.19684 | -0.3479 | 0.073242 | -0.086975 | 60.8368 | -62.0316 | 60.5988 | -61.8256 | 0.26093
501.75 | 123.111 | -60.7727 | 62.027 | -0.032697 | 0.016317 | 0.01295 | -0.0022786 | 0.0019023 | 0.00032545 | -0.00064093 | -60.9329 | 62.0087 | -61.1298 | 0.032043 | 0.059509 | 0.073242 | -0.064087 | 0.27008 | 0.20142 | -0.27466 | -0.35706 | -0.018311 | -0.16022 | 60.8047 | -61.9675 | 60.498 | -61.8256 | 0.19684
502.7656 | 123.0927 | -60.8047 | 62.0407 | 0.27248 | 0.020803 | 0.016154 | 0.0084026 | 0.0012615 | 0.00053925 | -0.00042733 | -60.8917 | 62.1368 | -61.1435 | -0.004578 | -0.009155 | -0.054932 | -0.11444 | 0.11902 | 0.1831 | -0.35248 | -0.33874 | 0.096131 | -0.086975 | 60.8002 | -62.0499 | 60.4523 | -61.8576 | 0.25177
503.75 | 123.0469 | -60.8185 | 62.0773 | -0.12425 | 0.020589 | 0.017008 | 0.0056254 | 0.0025431 | -0.0024516 | -0.0012817 | -60.8963 | 62.1277 | -61.1526 | 0.050354 | 0.036621 | 0.036621 | 0.10529 | 0.23804 | 0.27008 | -0.21057 | -0.33417 | 0.050354 | -0.07782 | 60.8688 | -62.0407 | 60.6079 | -61.8073 | 0.25635
504.7656 | 123.0606 | -60.7956 | 62.059 | -0.032697 | 0.019948 | 0.015513 | 0.0086162 | 0.0051067 | -0.00010175 | -0.0012817 | -60.9283 | 62.1277 | -61.1343 | 0.041199 | 0.018311 | 0.027466 | 0.013733 | 0.19684 | 0.2243 | -0.27008 | -0.33875 | 0.068665 | -0.13275 | 60.8368 | -62.0407 | 60.5255 | -61.8347 | 0.20599
505.7344 | 123.1018 | -60.7361 | 61.9812 | 0.24196 | 0.018026 | 0.017008 | 0.0004984 | 0.0029705 | 0.00096645 | 0.0023499 | -60.8826 | 62.0316 | -61.1572 | 0.032043 | 0.041199 | 0.027466 | -0.16479 | 0.2243 | 0.18768 | -0.33417 | -0.42114 | 0.050354 | -0.14648 | 60.7681 | -61.94 | 60.4019 | -61.7935 | 0.27466
506.7812 | 123.1201 | -60.791 | 62.0041 | 0.26485 | 0.020162 | 0.020854 | 0.0049846 | 0.0051067 | 0.0033162 | 0.0017091 | -60.8917 | 62.1094 | -61.1572 | -0.004578 | -0.013733 | -0.032043 | -0.12817 | 0.15106 | 0.17395 | -0.35706 | -0.36621 | 0.10529 | -0.10071 | 60.7864 | -62.0178 | 60.434 | -61.8301 | 0.2655
507.7344 | 123.1018 | -60.7956 | 62.0087 | 0.18093 | 0.017598 | 0.018717 | -0.002065 | 0.0016887 | 0.00032545 | 0.00085447 | -60.8963 | 62.0361 | -61.1481 | 0.013733 | 0.009155 | 0.013733 | -0.14648 | 0.19226 | 0.16022 | -0.32501 | -0.35248 | 0.027466 | -0.10071 | 60.8093 | -61.9995 | 60.4706 | -61.8484 | 0.25177
508.7656 | 123.1476 | -60.791 | 61.9904 | 0.27248 | 0.017812 | 0.016795 | 0.0037028 | 0.0040385 | 0.0020344 | 0.0010681 | -60.8414 | 62.0453 | -61.1298 | 0.050354 | 0.045776 | 0.036621 | -0.20599 | 0.22888 | 0.16022 | -0.36621 | -0.33875 | 0.054932 | -0.050354 | 60.8414 | -61.9446 | 60.4248 | -61.8301 | 0.28839
509.7344 | 123.1064 | -60.7773 | 62.027 | 0.16567 | 0.01653 | 0.014018 | -0.0031332 | -2.0324e-05 | 0.00096645 | 0.00064087 | -60.9375 | 62.0041 | -61.1298 | -0.004578 | 0.036621 | 0.022888 | -0.09613 | 0.21973 | 0.18768 | -0.28839 | -0.35248 | -0.022889 | -0.16022 | 60.7727 | -61.9904 | 60.4889 | -61.8393 | 0.19226
510.7656 | 123.0103 | -60.8368 | 62.059 | 0.12752 | 0.020376 | 0.017436 | 0.0071208 | 0.0040385 | 0.00032545 | -0.0023499 | -60.878 | 62.1506 | -61.1298 | -0.045776 | -0.07782 | -0.086975 | 0.027466 | 0.10529 | 0.19684 | -0.34332 | -0.29297 | 0.091553 | -0.041199 | 60.791 | -62.1368 | 60.4935 | -61.8622 | 0.25177
511.75 | 122.9965 | -60.8231 | 62.0316 | 0.15804 | 0.021657 | 0.019358 | 0.0079752 | 0.0027567 | 0.00011185 | -0.0010681 | -60.9192 | 62.1414 | -61.1755 | -0.068665 | -0.09613 | -0.09613 | -0.004578 | 0.091553 | 0.20142 | -0.3479 | -0.35248 | 0.10986 | -0.09613 | 60.7544 | -62.1277 | 60.4752 | -61.8301 | 0.25635
512.7656 | 123.1567 | -60.7681 | 61.9904 | 0.31825 | 0.019094 | 0.019999 | 0.00413 | 0.0040385 | -0.0028788 | -0.00085453 | -60.8551 | 62.027 | -61.1343 | 0.036621 | 0.041199 | 0.032043 | -0.1831 | 0.21515 | 0.14191 | -0.36621 | -0.36621 | 0.036622 | -0.086976 | 60.8047 | -61.9492 | 60.4019 | -61.8484 | 0.27923
513.7344 | 123.143 | -60.7452 | 61.9949 | 0.23433 | 0.017812 | 0.016154 | 0.00413 | 0.0019023 | 0.00075285 | 0.0023499 | -60.8459 | 62.0636 | -61.1481 | 0.045776 | 0.041199 | 0.018311 | -0.20599 | 0.21515 | 0.16022 | -0.36163 | -0.40283 | 0.068665 | -0.10071 | 60.791 | -61.9537 | 60.3836 | -61.8347 | 0.30212
514.7656 | 122.9782 | -60.8231 | 62.0224 | 0.20381 | 0.020589 | 0.020426 | 0.0051982 | 0.0021159 | -0.0011698 | -0.00064093 | -60.9283 | 62.146 | -61.171 | -0.050354 | -0.07782 | -0.11444 | -0.009155 | 0.10071 | 0.19226 | -0.37537 | -0.3479 | 0.1236 | -0.10529 | 60.7727 | -62.1002 | 60.4477 | -61.8301 | 0.24261
515.7344 | 123.1338 | -60.7819 | 62.0132 | 0.25722 | 0.019948 | 0.016368 | 0.0037028 | 0.0046793 | -0.0011698 | 0.0014953 | -60.8734 | 62.0911 | -61.1572 | 0.027466 | 0.027466 | 0.022888 | -0.18768 | 0.19684 | 0.16937 | -0.37537 | -0.37537 | 0.077819 | -0.091553 | 60.8093 | -61.9858 | 60.4065 | -61.8439 | 0.28381
516.7812 | 123.1338 | -60.7636 | 62.0041 | 0.27248 | 0.017598 | 0.016795 | 0.0039164 | 0.0033977 | 0.00011185 | 0.0023499 | -60.878 | 62.059 | -61.1389 | 0.018311 | 0.027466 | 0.004578 | -0.20142 | 0.16479 | 0.14648 | -0.37537 | -0.37537 | 0.054932 | -0.11444 | 60.7819 | -61.9766 | 60.3882 | -61.8576 | 0.26093
517.7344 | 123.1064 | -60.791 | 62.0041 | 0.20381 | 0.015889 | 0.017008 | -0.0016378 | 0.0036113 | 0.0013936 | 0.0019227 | -60.9238 | 62.0224 | -61.1252 | 0.004578 | 0.018311 | 0.018311 | -0.13733 | 0.18768 | 0.16022 | -0.29297 | -0.33417 | 0.018311 | -0.13275 | 60.7956 | -61.9858 | 60.498 | -61.8439 | 0.20142
518.7656 | 123.0377 | -60.8322 | 62.0361 | 0.074114 | 0.02123 | 0.019358 | 0.0090434 | 0.0016887 | -0.00031535 | 6.6667e-08 | -60.8871 | 62.1414 | -61.1435 | -0.022888 | -0.059509 | -0.054932 | 0.032043 | 0.10529 | 0.21515 | -0.32044 | -0.31128 | 0.10529 | -0.054932 | 60.8093 | -62.0956 | 60.5118 | -61.821 | 0.25635
519.7344 | 123.1567 | -60.7773 | 62.0132 | 0.28774 | 0.019948 | 0.014872 | 0.0009258 | 0.0036113 | 0.0018208 | 0.0014953 | -60.8688 | 62.0911 | -61.1389 | 0.022888 | 0.036621 | 0.013733 | -0.18768 | 0.20599 | 0.15564 | -0.37079 | -0.36163 | 0.077819 | -0.091552 | 60.8002 | -61.9766 | 60.4065 | -61.8576 | 0.27008
520.7656 | 123.0972 | -60.7636 | 62.0407 | -0.11662 | 0.015035 | 0.011454 | -0.0007832 | 0.0021159 | 0.00032545 | -0.00085453 | -60.8643 | 62.0407 | -61.1389 | 0.091553 | 0.10986 | 0.16022 | 0.009155 | 0.36163 | 0.22888 | -0.20599 | -0.37537 | 0 | -0.10071 | 60.8551 | -61.9308 | 60.5576 | -61.8118 | 0.27466
521.7344 | 123.1064 | -60.7819 | 62.0316 | 0.15804 | 0.01888 | 0.015727 | 0.000712 | 0.0019023 | 0.00053925 | -0.00085453 | -60.9009 | 62.0087 | -61.1389 | -0.013733 | 0.013733 | -0.004578 | -0.091553 | 0.21973 | 0.18768 | -0.29297 | -0.35706 | -0.022888 | -0.11902 | 60.7681 | -62.0178 | 60.4889 | -61.8439 | 0.23804
522.7656 | 123.0606 | -60.7636 | 62.0544 | -0.20054 | 0.016744 | 0.01829 | 7.12e-05 | -0.00044752 | 0.00053925 | 0.0010681 | -60.8826 | 62.0544 | -61.1252 | 0.091553 | 0.082397 | 0.11902 | 0.07782 | 0.31128 | 0.26093 | -0.20599 | -0.36163 | 0 | -0.11902 | 60.8551 | -61.972 | 60.5576 | -61.7935 | 0.24262
523.7344 | 123.0698 | -60.7956 | 62.0132 | 0.24196 | 0.019948 | 0.015727 | 0.0077616 | 0.0010477 | -0.0026652 | 0.00021367 | -60.9055 | 62.1185 | -61.1252 | -0.027466 | -0.050354 | -0.064087 | -0.10071 | 0.12817 | 0.17395 | -0.35706 | -0.32959 | 0.10529 | -0.10986 | 60.7681 | -62.0636 | 60.4385 | -61.8393 | 0.21973
524.7656 | 123.111 | -60.7727 | 62.0316 | -0.13188 | 0.018239 | 0.017863 | 0.0002848 | 0.0012615 | -0.0011698 | -0.0053405 | -60.8505 | 62.0636 | -61.1069 | 0.10529 | 0.09613 | 0.14648 | 0.022888 | 0.35248 | 0.24261 | -0.20142 | -0.33417 | 0.032044 | -0.07782 | 60.878 | -61.9354 | 60.5713 | -61.7889 | 0.25635
525.7344 | 123.1476 | -60.7819 | 62.0224 | 0.24196 | 0.019094 | 0.018504 | 0.000712 | 0.0023295 | -0.0015972 | -0.00021353 | -60.8505 | 62.0316 | -61.1435 | 0.045776 | 0.041199 | 0.032043 | -0.16937 | 0.23804 | 0.16022 | -0.3479 | -0.36163 | 0.009155 | -0.068665 | 60.8276 | -61.9812 | 60.434 | -61.8622 | 0.29297
526.7812 | 123.0835 | -60.7956 | 62.0636 | -0.017439 | 0.020376 | 0.018077 | 0.0090434 | 0.0040385 | 0.00011185 | 0.0025635 | -60.8231 | 62.1368 | -61.1343 | -0.15106 | -0.17395 | 0.16479 | 0.18768 | 0.27008 | 0.21057 | -0.28839 | -0.33875 | 0.073242 | -0.027466 | 60.6445 | -62.2375 | 60.5072 | -61.853 | 0.31128
527.7344 | 123.0881 | -60.8139 | 62.027 | 0.2267 | 0.019307 | 0.019786 | 0.00648 | 0.0048931 | -0.0013834 | 6.6667e-08 | -60.9055 | 62.1185 | -61.1801 | -0.027466 | -0.036621 | -0.059509 | -0.091553 | 0.10529 | 0.1831 | -0.3479 | -0.36621 | 0.091552 | -0.091553 | 60.7864 | -62.0636 | 60.466 | -61.8439 | 0.27466
528.75 | 123.1155 | -60.7864 | 62.027 | -0.13951 | 0.018026 | 0.013163 | 7.12e-05 | 0.0012615 | -0.00095615 | 0.0010681 | -60.9329 | 62.0453 | -61.1618 | 0.041199 | 0.036621 | 0.045776 | -0.07782 | 0.23346 | 0.20599 | -0.29297 | -0.37537 | 0.01831 | -0.14648 | 60.8276 | -61.9904 | 60.4935 | -61.821 | 0.22888
529.7344 | 122.9736 | -60.8368 | 62.0682 | 0.15804 | 0.022512 | 0.019572 | 0.007548 | 0.0019023 | -0.00074255 | -0.0023499 | -60.9055 | 62.1414 | -61.1572 | -0.050354 | -0.086975 | -0.10071 | 0.022888 | 0.086975 | 0.20599 | -0.35248 | -0.32043 | 0.073242 | -0.068665 | 60.7864 | -62.1552 | 60.4843 | -61.8622 | 0.25177
530.7656 | 123.0469 | -60.8185 | 62.0361 | -0.040327 | 0.01888 | 0.019786 | 0.0071208 | 0.0040385 | -0.00052895 | -0.0014953 | -60.8414 | 62.1552 | -61.116 | 0.041199 | 0.036621 | 0.018311 | 0.032043 | 0.1831 | 0.23346 | -0.28381 | -0.29755 | 0.11902 | -0.022889 | 60.8597 | -61.9995 | 60.5347 | -61.8027 | 0.27466
531.7344 | 123.1064 | -60.759 | 62.0041 | 0.15804 | 0.018239 | 0.01594 | -0.002065 | 0.0033977 | -0.0026652 | 0.00085447 | -60.9375 | 62.0087 | -61.1572 | 0.022888 | 0.050354 | 0.027466 | -0.086975 | 0.21515 | 0.18768 | -0.29755 | -0.39825 | 0.004578 | -0.17853 | 60.7819 | -61.9537 | 60.4614 | -61.8164 | 0.21973
532.75 | 123.111 | -60.7819 | 62.0178 | 0.19618 | 0.015249 | 0.021922 | -0.0014242 | 0.0023295 | 0.0020344 | 0.00042727 | -60.9375 | 61.9995 | -61.1206 | 0.018311 | 0.027466 | 0.041199 | -0.086975 | 0.2243 | 0.17853 | -0.28381 | -0.33874 | -0.01831 | -0.15564 | 60.8002 | -61.9904 | 60.498 | -61.8393 | 0.1831
533.7344 | 123.0835 | -60.7864 | 62.027 | 0.28011 | 0.021016 | 0.017222 | 0.0073344 | 0.0025431 | -0.00095615 | -0.00042733 | -60.9055 | 62.1231 | -61.1481 | -0.013733 | -0.045776 | -0.059509 | -0.10071 | 0.1236 | 0.18768 | -0.3479 | -0.36163 | 0.09613 | -0.11902 | 60.7727 | -62.0728 | 60.4385 | -61.8393 | 0.24261
534.7656 | 123.1155 | -60.7452 | 62.0544 | -0.28447 | 0.015249 | 0.016795 | 7.12e-05 | 0.0014751 | -0.0033062 | -0.00042733 | -60.8734 | 62.0636 | -61.1114 | 0.11902 | 0.10986 | 0.14191 | 0.022888 | 0.36163 | 0.24719 | -0.20599 | -0.36621 | 0.009156 | -0.12817 | 60.8643 | -61.9446 | 60.5392 | -61.8073 | 0.23804
535.7344 | 123.0286 | -60.8093 | 62.0407 | 0.10463 | 0.021657 | 0.01829 | 0.0081888 | 0.0044657 | -0.00031535 | -0.00085453 | -60.8597 | 62.1323 | -61.1481 | 0 | -0.032043 | -0.027466 | 0.036621 | 0.1831 | 0.21973 | -0.32044 | -0.33875 | 0.091553 | -0.050354 | 60.8093 | -62.0728 | 60.4889 | -61.821 | 0.28839
536.7656 | 123.1934 | -60.759 | 62.0178 | 0.28774 | 0.017812 | 0.018504 | 0.0028484 | 0.0042521 | -0.0030924 | -0.0014953 | -60.8505 | 62.027 | -61.1664 | 0.054932 | 0.041199 | 0.027466 | -0.56763 | -0.20142 | 0.14191 | -0.41199 | -0.40741 | 0.009156 | -0.091553 | 60.8139 | -61.9766 | 60.347 | -61.8759 | 0.31586
537.7344 | 123.024 | -60.8093 | 62.0544 | 0.21907 | 0.021444 | 0.017863 | 0.0066936 | 0.0038249 | 0.00032545 | 0.0012817 | -60.9467 | 62.1368 | -61.1435 | -0.050354 | -0.068665 | -0.086975 | -0.013733 | 0.09613 | 0.20599 | -0.35706 | -0.33417 | 0.082398 | -0.13733 | 60.759 | -62.1231 | 60.4523 | -61.8484 | 0.19684
538.7656 | 123.1064 | -60.7819 | 62.0041 | 0.043596 | 0.01653 | 0.016154 | -0.0012106 | 0.0029705 | -0.00010175 | 0.00064087 | -60.9329 | 62.0407 | -61.1343 | 0.059509 | 0.059509 | 0.022888 | -0.059509 | 0.22888 | 0.20599 | -0.27008 | -0.35248 | 0.036621 | -0.15106 | 60.8414 | -61.9446 | 60.5118 | -61.7981 | 0.20142
539.7344 | 122.9874 | -60.8276 | 62.059 | 0.15804 | 0.020589 | 0.021281 | 0.007548 | 0.0029705 | -0.00010175 | 0.00042727 | -60.9055 | 62.146 | -61.1435 | -0.045776 | -0.082397 | -0.091553 | 0.027466 | 0.086975 | 0.21515 | -0.3479 | -0.31586 | 0.086975 | -0.07782 | 60.7819 | -62.1414 | 60.4797 | -61.8439 | 0.23804
540.75 | 123.1155 | -60.7681 | 62.0041 | 0.24959 | 0.021444 | 0.021281 | 0.0015666 | 0.0029705 | -0.0018108 | -0.00042733 | -61.0062 | 62.0087 | -61.1801 | 0.13275 | 0.082397 | 0.013733 | -0.16479 | 0.23804 | 0.16937 | -0.29297 | -0.41199 | 0.004578 | -0.23804 | 60.9009 | -61.9217 | 60.4752 | -61.8347 | 0.17395
541.7344 | 123.143 | -60.7681 | 62.0316 | 0.0054493 | 0.01653 | 0.014659 | -0.002065 | 0.0014751 | 0.0018208 | 0.0012817 | -60.8963 | 62.059 | -61.1618 | 0.091553 | 0.10986 | 0.11902 | -0.073242 | 0.33875 | 0.21515 | -0.23346 | -0.39368 | 0.027466 | -0.12817 | 60.8597 | -61.9217 | 60.5347 | -61.8164 | 0.2655
542.7656 | 123.1064 | -60.7773 | 61.9995 | 0.11989 | 0.016744 | 0.012522 | -0.0005696 | -0.00023392 | 0.0016072 | 0.00021367 | -60.9283 | 62.0132 | -61.1206 | 0.027466 | 0.036621 | 0.027466 | 0.027466 | 0.5127 | 0.20599 | -0.26093 | -0.34332 | 0.013733 | -0.15106 | 60.8047 | -61.9629 | 60.5164 | -61.7935 | 0.19226
543.7344 | 123.0331 | -60.8047 | 62.0544 | 0.020708 | 0.022725 | 0.017222 | 0.009257 | 0.0027567 | -0.00052895 | 0.00021367 | -60.8414 | 62.1414 | -61.1114 | 0.027466 | -0.022888 | -0.027466 | 0.009155 | 0.17853 | 0.2243 | -0.31128 | -0.3067 | 0.086975 | -0.036621 | 60.8322 | -62.0773 | 60.4935 | -61.8301 | 0.27008
544.7656 | 123.0377 | -60.7681 | 62.0728 | -0.15477 | 0.01653 | 0.017222 | 0.0045574 | 0.0014751 | -0.0020244 | 0.00042727 | -60.8963 | 62.0819 | -61.1618 | 0.022888 | 0.07782 | 0.10071 | 0.1236 | 0.23804 | 0.25177 | -0.17853 | -0.39368 | 0.009155 | -0.12817 | 60.791 | -61.9949 | 60.5896 | -61.821 | 0.2655
545.7344 | 123.0057 | -60.8139 | 62.0407 | 0.1733 | 0.020376 | 0.019999 | 0.0062662 | 0.0051067 | 0.00032545 | -0.0023499 | -60.91 | 62.1277 | -61.1435 | -0.041199 | -0.059509 | -0.086975 | -0.018311 | 0.10071 | 0.21057 | -0.35248 | -0.32959 | 0.086976 | -0.09613 | 60.7727 | -62.1002 | 60.4614 | -61.8301 | 0.23346
546.7656 | 123.0515 | -60.8139 | 62.0453 | 0.0054493 | 0.021444 | 0.019358 | 0.0088298 | 0.0031841 | -0.0030924 | 0.00042727 | -60.8322 | 62.1414 | -61.1298 | 0.032043 | 0.004578 | -0.009155 | 0.004578 | 0.18768 | 0.21515 | -0.27466 | -0.31586 | 0.09613 | -0.01831 | 60.8459 | -62.0407 | 60.5392 | -61.8301 | 0.29755
547.7344 | 123.0469 | -60.8093 | 62.0316 | 0.028338 | 0.021444 | 0.020854 | 0.0077616 | 0.0031841 | -0.0013834 | 0.00085447 | -60.8551 | 62.1368 | -61.1343 | 0.018311 | 0.013733 | -0.009155 | 0.009155 | 0.16022 | 0.21515 | -0.28381 | -0.32501 | 0.10529 | -0.045777 | 60.8276 | -62.0178 | 60.5255 | -61.8164 | 0.27923
548.7344 | 123.0423 | -60.8185 | 62.0453 | 0.074114 | 0.020162 | 0.021922 | 0.0066936 | 0.0038249 | -0.0024516 | -0.00064093 | -60.8963 | 62.1689 | -61.1435 | -0.018311 | -0.036621 | -0.050354 | 0.018311 | 0.13275 | 0.21515 | -0.3067 | -0.32501 | 0.1236 | -0.07782 | 60.8002 | -62.0819 | 60.5118 | -61.8301 | 0.24719
549.7344 | 122.9874 | -60.8139 | 62.0407 | 0.20381 | 0.021016 | 0.019572 | 0.0066936 | 0.0048931 | 0.00053925 | 0.00085447 | -60.9375 | 62.1414 | -61.1938 | -0.059509 | -0.064087 | -0.091553 | -0.022888 | 0.091553 | 0.20599 | -0.33417 | -0.37994 | 0.10071 | -0.1236 | 60.7544 | -62.1048 | 60.4797 | -61.8347 | 0.25635
550.7344 | 122.9965 | -60.8139 | 62.0361 | 0.1733 | 0.023794 | 0.01829 | 0.0054118 | 0.0059611 | 0.00053925 | 0.0021363 | -60.9238 | 62.1552 | -61.1664 | -0.054932 | -0.059509 | -0.082397 | 0.009155 | 0.064087 | 0.21515 | -0.35248 | -0.35248 | 0.11902 | -0.10986 | 60.759 | -62.0956 | 60.4614 | -61.821 | 0.24262
551.7344 | 123.0743 | -60.8322 | 62.027 | 0.27248 | 0.019735 | 0.017222 | 0.0034892 | 0.0046793 | 0.002248 | 0.0025635 | -60.9238 | 62.114 | -61.1664 | -0.041199 | -0.027466 | -0.054932 | -0.07782 | 0.1236 | 0.19684 | -0.3479 | -0.33417 | 0.086975 | -0.091553 | 60.791 | -62.0544 | 60.4843 | -61.8301 | 0.24262
552.7656 | 123.0835 | -60.7819 | 62.0041 | 0.11226 | 0.018239 | 0.016368 | -0.0042012 | 0.0021159 | -0.00031535 | 0.0014953 | -60.9329 | 62.027 | -61.1298 | 0 | 0.032043 | 0.041199 | -0.068665 | 0.23804 | 0.19684 | -0.24719 | -0.3479 | 0.022889 | -0.15106 | 60.7819 | -61.972 | 60.5347 | -61.8073 | 0.19684
553.7344 | 123.0286 | -60.8047 | 62.0499 | 0.12752 | 0.020803 | 0.019358 | 0.0079752 | 0.0025431 | 0.00032545 | -0.0014953 | -60.8734 | 62.1552 | -61.1206 | -0.027466 | -0.036621 | -0.032043 | 0.045776 | 0.15106 | 0.21515 | -0.31586 | -0.31586 | 0.10528 | -0.068664 | 60.7773 | -62.0865 | 60.4889 | -61.8347 | 0.24719
554.7656 | 123.0789 | -60.791 | 62.0499 | -0.14714 | 0.01653 | 0.019145 | 7.12e-05 | 0.0044657 | -0.0028788 | 0.0019227 | -60.8871 | 62.0911 | -61.1481 | 0.07782 | 0.073242 | 0.11902 | 0.073242 | 0.32501 | 0.25177 | -0.20599 | -0.35706 | 0.041198 | -0.09613 | 60.8688 | -61.9766 | 60.585 | -61.7981 | 0.26093
555.7344 | 123.0743 | -60.8093 | 62.0178 | -0.063215 | 0.019735 | 0.021495 | 0.0060526 | 0.0044657 | -0.0013834 | 0.0014953 | -60.8276 | 62.1552 | -61.1526 | 0.045776 | 0.009155 | 0.032043 | 0.004578 | 0.21973 | 0.22888 | -0.27008 | -0.34332 | 0.13733 | -0.018311 | 60.8551 | -62.0087 | 60.5392 | -61.7889 | 0.32501
556.7656 | 123.0469 | -60.8139 | 62.0544 | -0.17003 | 0.017812 | 0.014872 | 0.003062 | 0.0016887 | -0.00010175 | -0.0023499 | -60.9146 | 62.1231 | -61.1389 | 0.013733 | 0.16022 | 0.49439 | 0.064087 | -0.21515 | 0.29755 | -0.10071 | -0.32501 | 0.068665 | -0.10071 | 60.8276 | -61.8942 | 60.7132 | -61.7569 | 0.2243
557.7344 | 123.0606 | -60.8139 | 62.0636 | -0.49046 | 0.019735 | 0.022135 | 0.00648 | 0.0057475 | -0.00074255 | 0.00021367 | -60.8551 | 62.1277 | -61.1298 | 0.036621 | 0 | 0.004578 | 0.036621 | 0.20599 | 0.25177 | -0.27466 | -0.31586 | 0.064087 | -0.041199 | 60.8505 | -62.0636 | 60.5392 | -61.8118 | 0.27466
558.7656 | 123.1293 | -60.7773 | 62.0316 | -0.040327 | 0.015889 | 0.012309 | -0.0039876 | 0.0027567 | -0.00031535 | -0.0010681 | -60.91 | 62.0361 | -61.1389 | 0.073242 | 0.10071 | 0.10529 | -0.073242 | 0.29755 | 0.23346 | -0.23804 | -0.36163 | 0.004578 | -0.13275 | 60.8505 | -61.9308 | 60.5392 | -61.7981 | 0.22888
559.75 | 123.0972 | -60.7864 | 62.0132 | 0.21144 | 0.016103 | 0.017863 | -0.0009968 | 0.0019023 | -0.00010175 | -0.00042733 | -60.8963 | 62.0316 | -61.1389 | 0.018311 | 0.009155 | 0.013733 | -0.10529 | 0.21057 | 0.19226 | -0.31128 | -0.35248 | 0.01831 | -0.10986 | 60.8047 | -62.0041 | 60.4752 | -61.821 | 0.24262
560.7656 | 123.1338 | -60.7498 | 62.0132 | -0.1624 | 0.01653 | 0.016581 | -0.0056966 | -0.0025837 | -0.00010175 | -0.00064093 | -60.8597 | 62.0178 | -61.116 | -0.26093 | -0.073242 | 0.31128 | -0.11444 | 0.19684 | 0.2243 | -0.21515 | -0.36621 | 0.004577 | -0.10986 | 60.4889 | -62.0865 | 60.5347 | -61.7889 | 0.25635
561.7344 | 123.024 | -60.8322 | 62.0544 | 0.10463 | 0.021444 | 0.016795 | 0.0086162 | 0.0033977 | -0.0018108 | 0.0012817 | -60.878 | 62.1368 | -61.1618 | -0.050354 | -0.07782 | -0.09613 | 0.004578 | 0.091553 | 0.21515 | -0.33417 | -0.32959 | 0.082398 | -0.045777 | 60.7819 | -62.1323 | 60.498 | -61.8393 | 0.28381
562.7656 | 123.1567 | -60.7636 | 62.0316 | -0.0021797 | 0.014608 | 0.015727 | -0.0035604 | 0.0019023 | 0.00011185 | 0.0017091 | -60.8871 | 62.0224 | -61.1435 | 0.10529 | 0.086975 | 0.12817 | -0.054932 | 0.3479 | 0.21515 | -0.23804 | -0.37994 | -0.009155 | -0.1236 | 60.8688 | -61.9446 | 60.5255 | -61.8164 | 0.25635
563.7344 | 123.056 | -60.8002 | 62.0544 | -0.12425 | 0.018453 | 0.021281 | 0.0060526 | 0.0019023 | -0.0015972 | 6.6667e-08 | -60.8459 | 62.1643 | -61.1435 | 0.054932 | 0.032043 | 0.059509 | 0.09613 | 0.27008 | 0.24719 | -0.21973 | -0.34332 | 0.10986 | -0.045776 | 60.8551 | -62.0224 | 60.5804 | -61.8073 | 0.29755
564.7656 | 123.024 | -60.8047 | 62.0361 | 0.16567 | 0.022298 | 0.015727 | 0.0066936 | 0.0042521 | 0.00075285 | -0.0021361 | -60.8597 | 62.1231 | -61.1343 | 0 | -0.027466 | -0.041199 | 0.009155 | 0.16479 | 0.23804 | -0.32044 | -0.32959 | 0.086975 | -0.054931 | 60.8047 | -62.0636 | 60.4843 | -61.7981 | 0.27466
565.7344 | 123.0194 | -60.8093 | 62.0316 | 0.14278 | 0.020162 | 0.017649 | 0.0077616 | 0.0048931 | 0.00096645 | -0.00085453 | -60.8688 | 62.1277 | -61.1206 | -0.013733 | -0.045776 | -0.045776 | 0.032043 | 0.14648 | 0.22888 | -0.30212 | -0.31128 | 0.096131 | -0.059509 | 60.7956 | -62.0773 | 60.5072 | -61.8027 | 0.25177
566.7656 | 123.1705 | -60.7681 | 62.0224 | -0.13188 | 0.015889 | 0.01295 | -0.0048422 | 0.0029705 | -0.0011698 | -0.00085453 | -60.8597 | 62.0407 | -61.1343 | 0.15106 | 0.15564 | 0.1831 | -0.054932 | 0.37994 | 0.21057 | -0.17853 | -0.36621 | 0.01831 | -0.091553 | 60.9192 | -61.8668 | 60.5896 | -61.8118 | 0.27466
567.7344 | 123.0789 | -60.7819 | 62.059 | -0.0021797 | 0.020376 | 0.019572 | 0.0081888 | 0.0053203 | -0.00052895 | -0.00085453 | -60.8368 | 62.146 | -61.1298 | 0.022888 | 0.073242 | -0.073242 | -0.17395 | 0.28381 | 0.21515 | -0.29755 | -0.3479 | 0.086975 | -0.054932 | 60.8047 | -61.9858 | 60.4843 | -61.8439 | 0.29297
568.7656 | 123.1247 | -60.7361 | 62.027 | -0.13188 | 0.01653 | 0.011881 | -0.002065 | -0.00023392 | -0.0030924 | -0.0038451 | -60.8459 | 62.0361 | -61.0931 | 0.45319 | 0.48523 | 0.050354 | -0.57678 | 0.26093 | 0.27008 | -0.17395 | -0.35706 | 0.009155 | -0.10986 | 61.1893 | -61.5417 | 60.5621 | -61.7569 | 0.24719
569.7344 | 123.0606 | -60.8185 | 62.027 | 0.24196 | 0.021871 | 0.019999 | 0.0043436 | 0.0046793 | -0.00010175 | 6.6667e-08 | -60.8871 | 62.1414 | -61.1618 | -0.041199 | -0.050354 | -0.068665 | -0.086975 | 0.10986 | 0.17853 | -0.36163 | -0.34332 | 0.11444 | -0.068665 | 60.7773 | -62.0773 | 60.4568 | -61.8484 | 0.27466
570.75 | 123.1293 | -60.7727 | 61.9904 | 0.21144 | 0.020803 | 0.02064 | 0.0043436 | 0.0031841 | 0.00075285 | -0.0014953 | -60.8459 | 62.0544 | -61.1481 | 0.032043 | 0.027466 | 0.027466 | -0.1831 | 0.20599 | 0.15564 | -0.34332 | -0.37537 | 0.064087 | -0.073242 | 60.8047 | -61.9629 | 60.4294 | -61.8347 | 0.30212
571.7344 | 123.0148 | -60.8505 | 62.0178 | 0.18093 | 0.021444 | 0.018504 | 0.00648 | 0.0014751 | 0.00096645 | -0.0021361 | -60.9329 | 62.1414 | -61.1893 | -0.045776 | -0.059509 | -0.086975 | -0.013733 | 0.082397 | 0.21973 | -0.34332 | -0.33875 | 0.1236 | -0.082397 | 60.8047 | -62.0773 | 60.5072 | -61.7981 | 0.25635
572.7656 | 123.1247 | -60.7681 | 62.0132 | -0.92534 | 0.016958 | 0.017436 | -0.0014242 | 0.0029705 | -0.00074255 | -0.00085453 | -60.9329 | 62.0407 | -61.1389 | 0.11444 | 0.11444 | 0.15564 | 0.013733 | 0.35248 | 0.2243 | -0.2243 | -0.37079 | 0.027465 | -0.16479 | 60.8826 | -61.8988 | 60.5438 | -61.7889 | 0.20599
573.7344 | 123.024 | -60.8139 | 62.0499 | 0.066485 | 0.01888 | 0.017436 | 0.0069072 | 0.0029705 | -0.0015972 | 0.00021367 | -60.8643 | 62.1643 | -61.1343 | -0.004578 | -0.045776 | -0.045776 | 0.022888 | 0.15564 | 0.22888 | -0.29755 | -0.32043 | 0.11444 | -0.050354 | 60.8093 | -62.0956 | 60.5164 | -61.821 | 0.27008
574.7656 | 123.1201 | -60.791 | 62.0361 | 0.10463 | 0.018667 | 0.015513 | -0.003774 | 0.0027567 | 0.00053925 | 0.00042727 | -60.9238 | 62.0407 | -61.1481 | 0.027466 | 0.041199 | 0.041199 | -0.07782 | 0.26093 | 0.20599 | -0.26093 | -0.35706 | 0.004577 | -0.13275 | 60.8185 | -61.9949 | 60.5301 | -61.8301 | 0.2243
575.7344 | 123.0698 | -60.8002 | 62.0499 | -0.0021797 | 0.021657 | 0.017222 | 0.005839 | 0.0040385 | -0.00095615 | 0.0019227 | -60.8414 | 62.1368 | -61.1298 | 0.059509 | 0.022888 | 0.036621 | 0.004578 | 0.22888 | 0.23346 | -0.27924 | -0.32959 | 0.086975 | -0.041199 | 60.8597 | -62.027 | 60.5209 | -61.8164 | 0.28839
576.7656 | 123.1064 | -60.7498 | 62.0361 | -0.10899 | 0.015676 | 0.018504 | -0.0005696 | 0.0036113 | -0.002238 | 0.0014953 | -60.8643 | 62.0499 | -61.1206 | 0.086975 | 0.10986 | 0.15564 | 0.032043 | 0.35248 | 0.24719 | -0.21515 | -0.37079 | 0.013733 | -0.11444 | 60.8368 | -61.9263 | 60.5347 | -61.7889 | 0.25635
577.7344 | 123.0469 | -60.8093 | 62.0544 | -0.50572 | 0.021016 | 0.018717 | 0.0071208 | 0.0033977 | -0.0035198 | -0.0014953 | -60.791 | 62.1414 | -61.1298 | 0.032043 | 0.018311 | 0.022888 | 0.004578 | 0.21515 | 0.2243 | -0.27008 | -0.32044 | 0.086975 | 0.01831 | 60.8414 | -62.0361 | 60.5392 | -61.8301 | 0.33875
578.75 | 123.1155 | -60.7681 | 62.0041 | 0.20381 | 0.019948 | 0.01594 | -0.0001424 | 0.0038249 | -0.00095615 | -0.0010681 | -60.8917 | 62.0499 | -61.1343 | 0.004578 | 0.009155 | -0.004578 | -0.10529 | 0.20599 | 0.16479 | -0.30212 | -0.36621 | 0.045777 | -0.1236 | 60.7727 | -61.9949 | 60.466 | -61.8393 | 0.24261
579.7344 | 123.0698 | -60.7956 | 62.0636 | 0.081743 | 0.020589 | 0.015299 | 0.0096842 | 0.0048931 | -0.00095615 | 0.0017091 | -60.8368 | 62.1414 | -61.1343 | -0.10529 | 0.050354 | 0.18768 | 0.10071 | 0.24719 | 0.20142 | -0.29297 | -0.33875 | 0.077819 | -0.041199 | 60.6903 | -62.0132 | 60.5026 | -61.8622 | 0.29755
580.7656 | 123.1064 | -60.7819 | 62.0041 | 0.14278 | 0.017171 | 0.01594 | -0.0035604 | 0.0040385 | 0.00011185 | 0.00085447 | -60.9009 | 62.0316 | -61.1526 | -0.009155 | 0.013733 | 0.022888 | -0.07782 | 0.20599 | 0.17853 | -0.29755 | -0.37079 | 0.027466 | -0.11902 | 60.7727 | -61.9904 | 60.4843 | -61.8256 | 0.25177
581.7344 | 123.0927 | -60.8185 | 62.0224 | 0.24196 | 0.021016 | 0.020426 | 0.0043436 | 0.0029705 | -0.00010175 | 0.00085447 | -60.8963 | 62.1048 | -61.1435 | -0.027466 | -0.041199 | -0.068665 | -0.10529 | 0.12817 | 0.19684 | -0.3479 | -0.32501 | 0.082397 | -0.07782 | 60.791 | -62.0636 | 60.4706 | -61.8256 | 0.24719
582.7656 | 123.1201 | -60.7864 | 62.0224 | 0.11989 | 0.017385 | 0.012522 | -0.0022786 | 0.0023295 | 0.0018208 | 6.6667e-08 | -60.9192 | 62.059 | -61.1572 | 0.041199 | 0.050354 | 0.068665 | -0.045776 | 0.28381 | 0.20142 | -0.27008 | -0.37079 | 0.036621 | -0.13275 | 60.8276 | -61.972 | 60.5164 | -61.821 | 0.23804
583.7344 | 123.0743 | -60.7773 | 62.0544 | -0.063215 | 0.019735 | 0.016154 | 0.0084026 | 0.0023295 | 0.00011185 | 6.6667e-08 | -60.8368 | 62.146 | -61.116 | 0.054932 | 0.032043 | 0.027466 | 0.027466 | 0.24719 | 0.24261 | -0.27466 | -0.33875 | 0.091553 | -0.059509 | 60.8322 | -62.0224 | 60.5026 | -61.8118 | 0.27924
584.7656 | 123.0881 | -60.7727 | 62.0407 | 0.12752 | 0.017171 | 0.015513 | -0.0027058 | 0.0016887 | 0.0020344 | -0.00064093 | -60.91 | 62.0453 | -61.116 | 0.004578 | 0.027466 | 0.036621 | -0.073242 | 0.21973 | 0.18768 | -0.2655 | -0.34332 | 0.004578 | -0.13733 | 60.7773 | -62.0132 | 60.5072 | -61.853 | 0.20599
585.7344 | 123.0606 | -60.8093 | 62.0407 | 0.058855 | 0.023153 | 0.017863 | 0.010966 | 0.0055339 | -0.0015972 | 0.00021367 | -60.8093 | 62.178 | -61.116 | 0.13733 | 0.054932 | 0.059509 | 0.032043 | 0.19684 | 0.21973 | -0.26093 | -0.3067 | 0.13733 | 0 | 60.9467 | -61.9858 | 60.5484 | -61.821 | 0.3067
586.7656 | 123.111 | -60.7498 | 62.0453 | 0.043596 | 0.015462 | 0.019572 | -0.003774 | 0.0014751 | -0.00010175 | 0.0010681 | -60.8963 | 62.0361 | -61.1298 | 0.073242 | 0.07782 | 0.1236 | -0.064087 | 0.30212 | 0.21057 | -0.23804 | -0.37994 | -0.009155 | -0.14648 | 60.8231 | -61.9675 | 60.5118 | -61.8347 | 0.23346
587.7344 | 123.0698 | -60.7956 | 62.0682 | -0.047956 | 0.021657 | 0.020213 | 0.0086162 | 0.0014751 | 0.00075285 | 0.00021367 | -60.8185 | 62.146 | -61.1389 | 0.041199 | 0.009155 | 0.027466 | 0 | 0.21515 | 0.23804 | -0.28381 | -0.34332 | 0.07782 | -0.022888 | 60.8368 | -62.059 | 60.5118 | -61.8301 | 0.32044
588.75 | 123.024 | -60.8139 | 62.0682 | 0.25722 | 0.019948 | 0.018504 | 0.0045574 | 0.0051067 | -0.00031535 | -0.00085453 | -60.8963 | 62.1506 | -61.1801 | 0.32959 | 0.1831 | -0.22888 | 0.032043 | 0.28381 | 0.19684 | -0.32959 | -0.36621 | 0.082398 | -0.082397 | 61.1435 | -61.8851 | 60.4843 | -61.8713 | 0.28381
589.7344 | 123.0377 | -60.8093 | 62.0453 | -0.27684 | 0.019948 | 0.022349 | 0.0069072 | 0.0036113 | -0.0018108 | 0.00064087 | -60.8276 | 62.1368 | -61.1481 | 0.059509 | 0.018311 | 0.032043 | 0.018311 | 0.20142 | 0.23804 | -0.28839 | -0.33875 | 0.091553 | -0.018311 | 60.8688 | -62.027 | 60.5209 | -61.8073 | 0.32043
590.7656 | 123.1613 | -60.7773 | 62.0132 | 0.0054493 | 0.015889 | 0.014445 | -0.006551 | 0.0040385 | -0.0020244 | 0.00085447 | -60.9009 | 62.0178 | -61.1526 | 0.059509 | 0.07782 | 0.10071 | -0.068665 | 0.31128 | 0.20599 | -0.24719 | -0.37537 | 0.004577 | -0.1236 | 60.8368 | -61.9354 | 60.5301 | -61.8073 | 0.25177
591.7344 | 123.0011 | -60.8139 | 62.059 | 0.20381 | 0.019735 | 0.023844 | 0.0069072 | 0.0040385 | -0.00052895 | 0.00064087 | -60.9009 | 62.1506 | -61.1664 | -0.054932 | -0.082397 | -0.10529 | 0.022888 | 0.073242 | 0.21057 | -0.3479 | -0.35248 | 0.091553 | -0.086975 | 60.759 | -62.1414 | 60.466 | -61.8484 | 0.2655
592.7656 | 123.1064 | -60.7956 | 62.027 | 0.18093 | 0.017385 | 0.018717 | -0.0016378 | 0.00062048 | -0.00010175 | 0.0012817 | -60.9009 | 62.0499 | -61.1343 | 0.004578 | 0.018311 | 0.013733 | -0.11444 | 0.19226 | 0.17395 | -0.3067 | -0.33875 | 0.022888 | -0.10529 | 60.8002 | -62.0087 | 60.4889 | -61.853 | 0.23346
593.7344 | 123.0423 | -60.7864 | 62.0453 | 0.028338 | 0.021016 | 0.018504 | 0.0084026 | 0.0023295 | 0.0016072 | -0.0019225 | -60.8414 | 62.146 | -61.1435 | 0.027466 | 0 | 0.004578 | 0.018311 | 0.16479 | 0.21515 | -0.29297 | -0.35706 | 0.10071 | -0.054932 | 60.8139 | -62.0453 | 60.4935 | -61.8301 | 0.30212
594.7656 | 123.0515 | -60.8002 | 62.0728 | -0.032697 | 0.019307 | 0.020213 | 0.0060526 | 0.0042521 | 0.00053925 | 0.0023499 | -60.8185 | 62.1368 | -61.1481 | -0.018311 | 0.10986 | 0.1236 | 0.073242 | 0.23346 | 0.2243 | -0.27924 | -0.3479 | 0.064087 | -0.01831 | 60.7819 | -61.9629 | 60.5209 | -61.8485 | 0.32959
595.7344 | 123.0652 | -60.791 | 62.0453 | -0.20817 | 0.019948 | 0.018931 | 0.004771 | 0.0046793 | 0.00011185 | -0.0017089 | -60.8231 | 62.1552 | -61.1389 | 0.045776 | 0.041199 | 0.041199 | 0.022888 | 0.21973 | 0.23804 | -0.25635 | -0.3479 | 0.10986 | -0.032043 | 60.8368 | -62.0041 | 60.5347 | -61.8073 | 0.31586
596.7656 | 123.111 | -60.7773 | 62.0087 | 0.074114 | 0.01888 | 0.017436 | -0.0042012 | 0.0023295 | -0.0013834 | 6.6667e-08 | -60.9283 | 62.059 | -61.1481 | 0 | 0.045776 | 0.059509 | 0.20599 | 0.32959 | 0.22888 | -0.27008 | -0.37079 | 0.050354 | -0.15106 | 60.7773 | -61.9629 | 60.5072 | -61.7798 | 0.21973
597.7344 | 123.0606 | -60.7864 | 62.0407 | -0.0098092 | 0.019307 | 0.019358 | 0.0056254 | 0.0029705 | 0.00053925 | 0.00085447 | -60.8414 | 62.1323 | -61.1526 | 0.050354 | 0.018311 | 0.036621 | 0.009155 | 0.21057 | 0.22888 | -0.27466 | -0.36621 | 0.091553 | -0.054932 | 60.8368 | -62.0224 | 60.5118 | -61.8118 | 0.31128
598.7656 | 123.1064 | -60.7681 | 62.0773 | -0.10899 | 0.014821 | 0.014659 | 0.000712 | 0.0046793 | -0.0015972 | 0.00064087 | -60.8505 | 62.0682 | -61.1298 | 0.10071 | 0.10986 | 0.15106 | 0.018311 | 0.33417 | 0.23346 | -0.19684 | -0.36163 | -0.009156 | -0.082398 | 60.8688 | -61.9675 | 60.5713 | -61.8439 | 0.27924
599.7344 | 123.0652 | -60.8047 | 62.059 | -0.39891 | 0.020803 | 0.018504 | 0.0096842 | 0.0048931 | 0.00011185 | -0.0014953 | -60.8002 | 62.1231 | -61.116 | 0.050354 | 0.009155 | 0.013733 | 0.018311 | 0.20142 | 0.2243 | -0.26093 | -0.31128 | 0.064087 | 0.004578 | 60.8551 | -62.0499 | 60.5438 | -61.8347 | 0.31586
600.7656 | 123.1064 | -60.791 | 62.0361 | 0.21144 | 0.019521 | 0.016368 | -0.0018514 | 0.0023295 | -0.00010175 | 0.0012817 | -60.8688 | 62.0316 | -61.1435 | 0.022888 | 0.041199 | 0.050354 | -0.16022 | 0.21973 | 0.16937 | -0.32959 | -0.35248 | -0.004578 | -0.077819 | 60.8139 | -61.9949 | 60.4614 | -61.8668 | 0.27466
601.7344 | 123.0606 | -60.8276 | 62.0636 | 0.020708 | 0.019307 | 0.019572 | 0.0073344 | 0.0023295 | 0.00011185 | 0.0010681 | -60.8322 | 62.1735 | -61.1298 | 0.036621 | 0.018311 | -0.009155 | -0.27008 | 0.10986 | 0.21515 | -0.30212 | -0.30212 | 0.10986 | -0.004577 | 60.8643 | -62.0453 | 60.5255 | -61.8485 | 0.29755
602.7656 | 123.0972 | -60.7727 | 61.9995 | 0.21144 | 0.016958 | 0.017222 | -0.0009968 | 0.0029705 | 0.00032545 | 0.0032043 | -60.8963 | 62.0316 | -61.171 | 0.004578 | 0.018311 | 0.009155 | -0.11444 | 0.19684 | 0.19684 | -0.3067 | -0.39825 | 0.032043 | -0.1236 | 60.7773 | -61.9812 | 60.466 | -61.8027 | 0.27466
603.7344 | 123.0515 | -60.7819 | 62.059 | -0.13188 | 0.020589 | 0.020426 | 0.00648 | 0.0025431 | -0.00052895 | -0.0017089 | -60.8688 | 62.1368 | -61.1526 | 0.045776 | 0.032043 | 0.050354 | 0.09613 | 0.25177 | 0.2655 | -0.22888 | -0.37079 | 0.07782 | -0.086975 | 60.8276 | -62.027 | 60.553 | -61.7935 | 0.28381
604.7656 | 123.1201 | -60.7544 | 62.0087 | 0.26485 | 0.017598 | 0.014659 | 0.0039164 | 0.0059611 | -0.00031535 | 0.0023499 | -60.8322 | 62.0636 | -61.1252 | -0.013733 | 0.3479 | 0.28839 | -0.27466 | 0.25635 | 0.16937 | -0.37537 | -0.37079 | 0.054932 | -0.077819 | 60.7407 | -61.6608 | 60.379 | -61.8393 | 0.29297
605.7344 | 123.0515 | -60.8047 | 62.0773 | -0.13188 | 0.020589 | 0.016368 | 0.0039164 | 0.0031841 | 0.00118 | 0.00021367 | -60.8826 | 62.1597 | -61.1252 | 0.027466 | 0.013733 | 0.041199 | 0.10529 | 0.24719 | 0.24719 | -0.20142 | -0.32043 | 0.082397 | -0.077819 | 60.8322 | -62.0636 | 60.6033 | -61.8301 | 0.24262
606.7656 | 123.1796 | -60.7773 | 62.0453 | -0.070844 | 0.016317 | 0.012522 | -0.0016378 | 0.0019023 | -0.0020244 | 0.00064087 | -60.8505 | 62.0132 | -61.116 | 0.09613 | 0.11444 | 0.16937 | -0.054932 | 0.3891 | 0.2243 | -0.20142 | -0.33875 | -0.032043 | -0.073242 | 60.8734 | -61.9308 | 60.5759 | -61.821 | 0.2655
607.7344 | 123.0515 | -60.8002 | 62.0453 | -0.0098092 | 0.01888 | 0.018931 | 0.005839 | 0.0038249 | -0.0011698 | -0.00042733 | -60.8231 | 62.1552 | -61.1343 | 0.036621 | 0.013733 | 0.041199 | 0.018311 | 0.2243 | 0.2243 | -0.2655 | -0.33417 | 0.10986 | -0.022888 | 60.8368 | -62.0316 | 60.5347 | -61.821 | 0.31128
608.7656 | 123.1476 | -60.791 | 61.9995 | 0.24959 | 0.02123 | 0.018931 | -0.0001424 | 0.0029705 | 0.00053925 | -0.00064093 | -61.0245 | 62.0224 | -61.1526 | 0.027466 | 0.009155 | 0.086975 | -0.13275 | 0.21057 | 0.18768 | -0.30212 | -0.36163 | 0.022888 | -0.23346 | 60.8185 | -61.9904 | 60.4889 | -61.8118 | 0.12817
609.7344 | 123.0652 | -60.7864 | 62.0636 | -0.032697 | 0.019735 | 0.019145 | 0.0077616 | 0.0033977 | -0.0013834 | -0.0017089 | -60.8368 | 62.1597 | -61.1114 | 0.045776 | 0.036621 | 0.036621 | 0.027466 | 0.21515 | 0.25635 | -0.27924 | -0.32501 | 0.09613 | -0.050354 | 60.8322 | -62.027 | 60.5072 | -61.8073 | 0.27466
610.7656 | 123.111 | -60.791 | 62.0361 | 0.28774 | 0.018453 | 0.016581 | 0.003062 | 0.0051067 | 0.0035298 | 0.0014953 | -60.8551 | 62.114 | -61.1252 | 0.022888 | 0.027466 | -0.004578 | -0.21057 | 0.16022 | 0.14648 | -0.37079 | -0.33417 | 0.07782 | -0.064087 | 60.8139 | -62.0087 | 60.4202 | -61.8896 | 0.27008
611.7344 | 123.0606 | -60.8002 | 62.0499 | -0.0098092 | 0.02123 | 0.017649 | 0.0081888 | 0.0029705 | -0.00095615 | -0.00021353 | -60.8551 | 62.1689 | -61.1343 | -0.009155 | -0.018311 | -0.036621 | 0.018311 | 0.14191 | 0.23346 | -0.29297 | -0.33417 | 0.11902 | -0.054932 | 60.791 | -62.0682 | 60.5072 | -61.8164 | 0.27923
612.7656 | 123.1384 | -60.7498 | 62.0087 | 0.074114 | 0.019307 | 0.017863 | 7.12e-05 | 0.0021159 | -0.00095615 | -0.00042733 | -60.8551 | 62.0407 | -61.1252 | 0.018311 | 0.022888 | 0.027466 | -0.21057 | 0.20599 | 0.17853 | -0.28839 | -0.37537 | 0.032043 | -0.10529 | 60.7681 | -61.9858 | 60.4614 | -61.8301 | 0.27008
613.7344 | 123.0789 | -60.8002 | 62.0773 | -0.15477 | 0.021016 | 0.012309 | 0.0043436 | 0.0019023 | -0.00095615 | -0.00021353 | -60.8551 | 62.1643 | -61.1389 | 0.032043 | 0.045776 | 0.068665 | 0.082397 | 0.25635 | 0.26093 | -0.23346 | -0.33875 | 0.086975 | -0.054932 | 60.8322 | -62.0316 | 60.5667 | -61.8164 | 0.28381
614.7656 | 123.1338 | -60.7727 | 62.027 | 0.1733 | 0.017171 | 0.013804 | -0.0016378 | 0.0010477 | -0.0026652 | 0.0014953 | -60.9192 | 62.0407 | -61.1481 | -0.004578 | 0.045776 | 0.036621 | -0.068665 | 0.21515 | 0.19226 | -0.27924 | -0.37537 | 0.013732 | -0.14648 | 60.7681 | -61.9812 | 60.4935 | -61.8347 | 0.22888
615.7344 | 123.0698 | -60.7773 | 62.059 | 0.020708 | 0.020589 | 0.019999 | 0.0073344 | 0.0025431 | 0.0026754 | 0.00085447 | -60.8093 | 62.146 | -61.1252 | 0.068665 | 0.12817 | 0.064087 | 0.050354 | 0.23804 | 0.23346 | -0.28839 | -0.3479 | 0.086975 | -0.032043 | 60.8459 | -61.9308 | 60.4889 | -61.8256 | 0.31586
616.7656 | 123.1201 | -60.7727 | 62.0453 | 0.035967 | 0.015462 | 0.013377 | -0.0035604 | 0.0012615 | 0.00075285 | 0.0027771 | -60.9009 | 62.0361 | -61.116 | 0.059509 | 0.082397 | 0.09613 | -0.068665 | 0.28839 | 0.2243 | -0.23346 | -0.34332 | -0.009155 | -0.12817 | 60.8322 | -61.9629 | 60.5392 | -61.821 | 0.21515
617.7344 | 123.0469 | -60.7956 | 62.0773 | -0.31499 | 0.01888 | 0.014231 | 0.0066936 | 0.0016887 | -0.00031535 | -0.00042733 | -60.9467 | 62.1368 | -61.1252 | 0.036621 | 0.041199 | 0.054932 | 0.1236 | 0.21057 | 0.26093 | -0.23346 | -0.32959 | 0.059509 | -0.15106 | 60.8322 | -62.0361 | 60.5621 | -61.8164 | 0.17853
618.7656 | 123.1247 | -60.7681 | 62.0544 | 0.19618 | 0.016958 | 0.018504 | 0.0015666 | 0.0012615 | 0.0013936 | 6.6667e-08 | -60.8643 | 62.0544 | -61.1389 | 0.022888 | 0.036621 | 0.009155 | -0.13275 | 0.21973 | 0.16937 | -0.33417 | -0.37079 | 0 | -0.096131 | 60.791 | -62.0178 | 60.434 | -61.8851 | 0.27466
619.7344 | 123.0789 | -60.7956 | 62.0865 | -0.14714 | 0.020376 | 0.015513 | 0.0071208 | 0.0012615 | -0.0015972 | -0.00085453 | -60.8688 | 62.1689 | -61.1069 | 0.027466 | 0.022888 | 0.027466 | 0.10986 | 0.24261 | 0.26093 | -0.21057 | -0.31128 | 0.082397 | -0.073242 | 60.8231 | -62.0636 | 60.585 | -61.8256 | 0.23804
620.7656 | 123.1018 | -60.7727 | 62.0499 | 0.11989 | 0.016317 | 0.01359 | -0.0005696 | 0.0010477 | -0.00052895 | 0.00085447 | -60.91 | 62.0453 | -61.1343 | 0.018311 | 0.032043 | 0.036621 | -0.059509 | 0.25635 | 0.20599 | -0.25635 | -0.36163 | -0.004578 | -0.13733 | 60.791 | -62.0178 | 60.5164 | -61.8439 | 0.2243
621.7344 | 123.056 | -60.7956 | 62.0544 | -0.017439 | 0.020162 | 0.014659 | 0.009257 | 0.0042521 | -0.003947 | 0.0027771 | -60.8231 | 62.1506 | -61.1069 | 0.027466 | -0.004578 | 0.004578 | 0.018311 | 0.16937 | 0.22888 | -0.29297 | -0.31128 | 0.096131 | -0.027466 | 60.8231 | -62.059 | 60.5026 | -61.8256 | 0.28381
622.7656 | 123.143 | -60.7727 | 62.0361 | 0.24959 | 0.018026 | 0.019786 | 0.0022074 | 0.0021159 | 0.00032545 | 0.0010681 | -60.8459 | 62.0728 | -61.1343 | 0.18768 | 0.32959 | 0.1236 | -0.27008 | 0.29755 | 0.14191 | -0.3891 | -0.36163 | 0.036621 | -0.073242 | 60.9604 | -61.7065 | 60.3836 | -61.8942 | 0.28839
623.7344 | 123.0698 | -60.7819 | 62.0636 | -0.093733 | 0.020376 | 0.016154 | 0.0062662 | 0.00062048 | -0.00095615 | -0.00064093 | -60.8505 | 62.1506 | -61.1114 | 0.073242 | 0.045776 | 0.045776 | 0.050354 | 0.25177 | 0.25177 | -0.27008 | -0.32959 | 0.086975 | -0.068665 | 60.8551 | -62.0178 | 60.5118 | -61.8118 | 0.26093
624.7344 | 123.024 | -60.8047 | 62.0911 | -0.1624 | 0.018026 | 0.017436 | 0.0009258 | 0.0029705 | -0.0020244 | -0.00021353 | -60.9329 | 62.1094 | -61.1389 | 0.013733 | 0.027466 | 0.027466 | 0.15564 | 0.25177 | 0.27008 | -0.17853 | -0.33417 | 0.018311 | -0.12817 | 60.8185 | -62.0636 | 60.6262 | -61.821 | 0.20599
625.75 | 123.1201 | -60.7864 | 62.0224 | 0.21907 | 0.019521 | 0.017436 | 0.0056254 | 0.0040385 | 0.00011185 | -0.00042733 | -60.8734 | 62.0865 | -61.1389 | 0.027466 | 0.032043 | 0 | -0.16479 | 0.15564 | 0.16479 | -0.35706 | -0.35248 | 0.064087 | -0.086975 | 60.8139 | -61.9904 | 60.4294 | -61.8576 | 0.2655
626.75 | 123.0972 | -60.8139 | 61.9904 | 0.27248 | 0.019948 | 0.017008 | 0.005839 | 0.0061747 | 0.00075285 | -0.00042733 | -60.8688 | 62.1231 | -61.1298 | 0 | 0 | -0.022888 | -0.14648 | 0.14648 | 0.1831 | -0.35706 | -0.31586 | 0.13275 | -0.054931 | 60.8139 | -61.9904 | 60.4568 | -61.8073 | 0.26093
627.7344 | 123.0515 | -60.7819 | 62.0728 | -0.20054 | 0.019948 | 0.017649 | 0.0011394 | 0.0025431 | -0.0013834 | -0.0017089 | -60.91 | 62.1277 | -61.1435 | 0.022888 | 0.013733 | 0.041199 | 0.14648 | 0.24719 | 0.26093 | -0.17853 | -0.36163 | 0.054932 | -0.12817 | 60.8047 | -62.059 | 60.6033 | -61.8118 | 0.23346
628.75 | 123.056 | -60.8047 | 62.0361 | 0.26485 | 0.020803 | 0.015513 | 0.0043436 | 0.0036113 | 0.00096645 | 0.00021367 | -60.8734 | 62.1414 | -61.1389 | -0.036621 | -0.054932 | -0.082397 | -0.064087 | 0.11444 | 0.1831 | -0.36163 | -0.33417 | 0.10529 | -0.068664 | 60.7681 | -62.0911 | 60.4431 | -61.853 | 0.2655
629.7344 | 123.0423 | -60.7864 | 62.0819 | -0.24632 | 0.015676 | 0.017222 | 0.0028484 | 0.0019023 | 0.00011185 | -0.00064093 | -60.9009 | 62.1552 | -61.1389 | 0.022888 | 0.022888 | 0.045776 | 0.14648 | 0.25635 | 0.27008 | -0.17395 | -0.35248 | 0.073242 | -0.11444 | 60.8093 | -62.059 | 60.6125 | -61.8118 | 0.23804
630.7656 | 123.0606 | -60.7681 | 62.0773 | -0.20817 | 0.016744 | 0.013163 | 0.0019938 | 0.0019023 | -0.0013834 | 6.6667e-08 | -60.8551 | 62.1185 | -61.116 | 0.054932 | 0.068665 | 0.068665 | 0.086975 | 0.30212 | 0.24719 | -0.20599 | -0.3479 | 0.041198 | -0.086976 | 60.8231 | -62.0087 | 60.5621 | -61.8301 | 0.26093
631.7344 | 123.0789 | -60.7727 | 62.059 | -0.10899 | 0.019307 | 0.017649 | 0.0056254 | 0.0023295 | 0.00096645 | -0.0017089 | -60.8231 | 62.1597 | -61.1298 | 0.068665 | 0.041199 | 0.064087 | 0.045776 | 0.24261 | 0.25635 | -0.27008 | -0.35706 | 0.10071 | -0.050354 | 60.8414 | -62.0178 | 60.5026 | -61.8027 | 0.3067
632.7656 | 122.9828 | -60.7864 | 62.0728 | 0.1733 | 0.01888 | 0.02064 | 0.0079752 | 0.0042521 | -0.00074255 | -0.00021353 | -60.9055 | 62.1918 | -61.1481 | -0.082397 | -0.07782 | -0.11444 | -0.018311 | 0.082397 | 0.21973 | -0.35248 | -0.36163 | 0.11902 | -0.11902 | 60.704 | -62.1506 | 60.434 | -61.853 | 0.24261
633.7344 | 123.0972 | -60.7819 | 62.0819 | -0.15477 | 0.018239 | 0.016581 | -0.0018514 | 0.0016887 | 0.00096645 | 6.6667e-08 | -60.8551 | 62.1048 | -61.1526 | 0.073242 | 0.086975 | 0.1236 | 0.068665 | 0.31586 | 0.2655 | -0.20142 | -0.37079 | 0.022888 | -0.073243 | 60.8551 | -61.9949 | 60.5804 | -61.8164 | 0.29755
634.7656 | 123.143 | -60.7773 | 62.0224 | 0.4327 | 0.019521 | 0.016368 | 0.0049846 | 0.0042521 | -0.00052895 | -0.00042733 | -60.8093 | 62.1048 | -61.1389 | 0.041199 | 0.027466 | 0.032043 | -0.21057 | 0.20142 | 0.14191 | -0.35248 | -0.36163 | 0.082397 | -0.032043 | 60.8185 | -61.9949 | 60.4248 | -61.8805 | 0.32959
635.7344 | 123.0515 | -60.791 | 62.0361 | 0.028338 | 0.019307 | 0.019999 | 0.0045574 | 0.00083408 | -0.0015972 | -0.00021353 | -60.8505 | 62.1368 | -61.1526 | 0.050354 | 0 | 0 | 0.041199 | 0.2243 | 0.22888 | -0.27466 | -0.36163 | 0.10071 | -0.059509 | 60.8414 | -62.0361 | 60.5164 | -61.8073 | 0.30212
636.7656 | 123.1247 | -60.7681 | 62.027 | 0.28774 | 0.021444 | 0.014231 | 0.0034892 | 0.0044657 | 0.00118 | -0.00042733 | -60.8414 | 62.1185 | -61.1343 | 0.018311 | 0.009155 | 0.032043 | -0.14648 | 0.16022 | 0.17395 | -0.37537 | -0.36621 | 0.091552 | -0.073243 | 60.7864 | -62.0178 | 60.3928 | -61.853 | 0.29297
637.7344 | 123.0743 | -60.7864 | 62.1094 | -0.15477 | 0.017171 | 0.013377 | -0.0009968 | -0.00023392 | -0.0011698 | -0.0014953 | -60.878 | 62.0682 | -61.1343 | 0.073242 | 0.073242 | 0.10071 | 0.091553 | 0.30212 | 0.26093 | -0.20599 | -0.3479 | -0.041199 | -0.091553 | 60.8597 | -62.0361 | 60.5804 | -61.8484 | 0.25635
638.7656 | 123.1247 | -60.7773 | 62.059 | -0.13951 | 0.016744 | 0.015299 | 0.001353 | 0.00083408 | -0.0015972 | 6.6667e-08 | -60.8322 | 62.1048 | -61.1206 | 0.091553 | 0.09613 | 0.15106 | 0.022888 | 0.33875 | 0.24261 | -0.19226 | -0.34332 | 0.045776 | -0.054931 | 60.8688 | -61.9629 | 60.585 | -61.8164 | 0.28839
639.7344 | 123.0103 | -60.791 | 62.0865 | -0.13188 | 0.017812 | 0.01594 | 0.005839 | 0.0023295 | -0.0030924 | -0.0021361 | -60.9009 | 62.1277 | -61.1343 | 0.31586 | 0.12817 | -0.43488 | -0.018311 | 0.28839 | 0.27924 | -0.13275 | -0.34332 | 0.041199 | -0.10986 | 61.1069 | -61.9583 | 60.6583 | -61.8073 | 0.23346
640.7656 | 123.1842 | -60.7544 | 61.9949 | 0.27248 | 0.01888 | 0.019145 | 0.0037028 | 0.0016887 | 0.00075285 | -0.00064093 | -60.8322 | 62.059 | -61.1252 | 0.054932 | 0.050354 | 0.045776 | -0.20142 | 0.21973 | 0.17395 | -0.34332 | -0.37079 | 0.064087 | -0.077819 | 60.8093 | -61.9446 | 60.4111 | -61.821 | 0.29297
641.7344 | 123.0194 | -60.791 | 62.0956 | -0.18529 | 0.017812 | 0.019786 | 0.0039164 | 0.0010477 | -0.0013834 | -0.00064093 | -60.91 | 62.1231 | -61.1526 | 0.018311 | 0.013733 | 0.041199 | 0.15106 | 0.24261 | 0.28381 | -0.17395 | -0.36163 | 0.027466 | -0.11902 | 60.8093 | -62.0819 | 60.6171 | -61.8118 | 0.24261
642.7656 | 123.0789 | -60.8047 | 62.0636 | 0.28774 | 0.022725 | 0.017863 | 0.0071208 | 0.0048931 | -0.00095615 | 0.0012817 | -60.8963 | 62.1368 | -61.1389 | -0.018311 | -0.050354 | -0.068665 | -0.11444 | 0.1236 | 0.18768 | -0.33875 | -0.33417 | 0.073242 | -0.091552 | 60.7864 | -62.114 | 60.466 | -61.8759 | 0.24262
643.7344 | 123.0148 | -60.8002 | 62.0956 | -0.26921 | 0.017598 | 0.018717 | 0.003062 | 0.0016887 | 0.00032545 | -0.00085453 | -60.9009 | 62.1094 | -61.1298 | 0.013733 | -0.013733 | 0.032043 | 0.16479 | 0.27466 | 0.2655 | -0.17853 | -0.32959 | 0.013733 | -0.10071 | 60.8139 | -62.1094 | 60.6216 | -61.8301 | 0.22888
644.7656 | 123.0652 | -60.7956 | 62.0636 | -0.40654 | 0.019735 | 0.021281 | 0.0084026 | 0.0044657 | -0.0028788 | -0.0014953 | -60.8093 | 62.1597 | -61.1252 | 0.041199 | 0 | 0.018311 | 0.032043 | 0.20599 | 0.24261 | -0.27008 | -0.32959 | 0.09613 | -0.013733 | 60.8368 | -62.0636 | 60.5255 | -61.821 | 0.31586
645.7344 | 123.1338 | -60.7544 | 62.059 | -1.1695 | 0.015462 | 0.020426 | -0.0005696 | 0.0012615 | -0.0013834 | -0.00042733 | -60.9924 | 62.0682 | -61.1114 | 0.091553 | 0.059509 | 0.15564 | 0.013733 | 0.36163 | 0.2243 | -0.23346 | -0.35705 | 0.009155 | -0.23804 | 60.8459 | -61.9995 | 60.5209 | -61.8347 | 0.11902
646.7656 | 123.0011 | -60.8002 | 62.0682 | 0.11989 | 0.021871 | 0.020213 | 0.010325 | 0.0036113 | -0.00052895 | -0.00021353 | -60.8643 | 62.1689 | -61.1618 | -0.041199 | -0.068665 | -0.091553 | 0.027466 | 0.09613 | 0.21057 | -0.35248 | -0.36163 | 0.10071 | -0.064087 | 60.759 | -62.1368 | 60.4477 | -61.8576 | 0.29755
647.7344 | 123.1201 | -60.759 | 62.059 | -0.17003 | 0.015676 | 0.014445 | -0.0001424 | 0.0012615 | -0.00031535 | -0.0010681 | -60.8505 | 62.0911 | -61.1298 | 0.09613 | 0.10986 | 0.1236 | 0.022888 | 0.33875 | 0.24261 | -0.19226 | -0.37079 | 0.032043 | -0.091553 | 60.8551 | -61.9492 | 60.5667 | -61.8164 | 0.27924
648.7656 | 123.1064 | -60.7727 | 62.0453 | 0.24196 | 0.020162 | 0.019999 | 0.0060526 | 0.0027567 | -0.00074255 | -0.00021353 | -60.8505 | 62.0956 | -61.1435 | 0.041199 | 0.022888 | -0.013733 | -0.20142 | 0.14191 | 0.16937 | -0.37537 | -0.37079 | 0.050354 | -0.07782 | 60.8139 | -62.0224 | 60.3973 | -61.8759 | 0.29297
649.7344 | 123.1338 | -60.7498 | 62.0544 | 0.32588 | 0.016103 | 0.016154 | -0.0012106 | -0.00066112 | 0.00053925 | -0.0017089 | -60.8322 | 62.059 | -61.1298 | 0.13733 | 0.1236 | 0.13275 | -0.009155 | 0.37079 | 0.21515 | -0.2243 | -0.37994 | 0.004578 | -0.082397 | 60.8871 | -61.9308 | 60.5255 | -61.8393 | 0.29755
650.7656 | 123.1338 | -60.7773 | 62.0361 | 0.020708 | 0.018026 | 0.011241 | 0.0022074 | 0.00083408 | 0.0018208 | -0.0010681 | -60.8505 | 62.0636 | -61.116 | 0.018311 | 0.018311 | 0.022888 | -0.20599 | 0.20142 | 0.16479 | -0.31586 | -0.33875 | 0.027466 | -0.073242 | 60.7956 | -62.0178 | 60.4614 | -61.8713 | 0.2655
651.7344 | 123.0194 | -60.7773 | 62.0819 | -0.13951 | 0.016103 | 0.019358 | 0.002421 | 0.00040688 | -0.0013834 | -0.00064093 | -60.9009 | 62.1231 | -61.1252 | 0.022888 | 0.018311 | 0.050354 | 0.14648 | 0.26093 | 0.27924 | -0.17853 | -0.3479 | 0.041199 | -0.1236 | 60.8002 | -62.0636 | 60.5988 | -61.8027 | 0.2243
652.7656 | 123.1842 | -60.7269 | 62.0636 | -0.093733 | 0.017598 | 0.015727 | -0.0014242 | -0.00066112 | -0.00031535 | -0.00042733 | -60.8093 | 62.0544 | -61.0886 | 0.13733 | 0.15564 | 0.16937 | -0.036621 | 0.36163 | 0.21515 | -0.18768 | -0.36163 | -0.009156 | -0.082397 | 60.8643 | -61.908 | 60.5392 | -61.8485 | 0.27924
653.7344 | 123.1613 | -60.7498 | 62.0316 | -0.10899 | 0.014394 | 0.017436 | -0.0001424 | 0.00062048 | 0.00032545 | -0.00042733 | -60.8139 | 62.0316 | -61.084 | 0.12817 | 0.10986 | 0.16022 | -0.041199 | 0.37537 | 0.23346 | -0.20599 | -0.33417 | 0 | -0.064087 | 60.878 | -61.9217 | 60.5438 | -61.7981 | 0.27008
654.7656 | 122.9965 | -60.8002 | 62.0682 | 0.097002 | 0.019521 | 0.018931 | 0.0094706 | 0.00083408 | 0.00032545 | -0.0014953 | -60.8551 | 62.1506 | -61.1389 | -0.036621 | -0.064087 | -0.091553 | 0 | 0.082397 | 0.19684 | -0.36621 | -0.33875 | 0.082398 | -0.054932 | 60.7636 | -62.1323 | 60.434 | -61.8713 | 0.28381
655.7344 | 123.1293 | -60.7681 | 62.0499 | -0.15477 | 0.016103 | 0.016581 | -0.0005696 | 0.00040688 | -0.00095615 | 0.00021367 | -60.8551 | 62.0682 | -61.116 | 0.11444 | 0.11444 | 0.14648 | 0.013733 | 0.32501 | 0.23804 | -0.21057 | -0.3479 | 0.01831 | -0.086976 | 60.8826 | -61.9354 | 60.5576 | -61.8118 | 0.26093
656.7656 | 123.0515 | -60.8002 | 62.0636 | -0.40654 | 0.020803 | 0.021922 | 0.0081888 | 0.00040688 | -0.0020244 | -0.00064093 | -60.9146 | 62.1552 | -61.1389 | -0.022888 | -0.068665 | -0.082397 | -0.022888 | 0.11444 | 0.21515 | -0.35248 | -0.33875 | 0.091552 | -0.11444 | 60.7773 | -62.1323 | 60.4477 | -61.8485 | 0.2243
657.7344 | 123.1705 | -60.7315 | 62.059 | -0.032697 | 0.015462 | 0.015086 | -0.0014242 | -0.0010885 | 0.00075285 | 0.0029907 | -60.8551 | 62.0544 | -61.1298 | 0.13733 | 0.13733 | 0.16022 | -0.068665 | 0.37994 | 0.21515 | -0.1831 | -0.39825 | -0.004578 | -0.1236 | 60.8688 | -61.9217 | 60.5484 | -61.8439 | 0.27466
658.7656 | 123.0743 | -60.7956 | 62.0453 | 0.1733 | 0.02123 | 0.020854 | 0.0081888 | 0.0014751 | 0.00053925 | -0.0017089 | -60.8734 | 62.1323 | -61.1481 | -0.036621 | -0.041199 | -0.073242 | -0.086975 | 0.12817 | 0.18768 | -0.35706 | -0.35248 | 0.086975 | -0.07782 | 60.759 | -62.0865 | 60.4385 | -61.8576 | 0.27466
659.7344 | 123.1567 | -60.7544 | 62.0544 | -0.11662 | 0.014821 | 0.015727 | -0.0027058 | -0.00023392 | 0.00032545 | -0.00042733 | -60.8231 | 62.0224 | -61.1023 | 0.1236 | 0.13275 | 0.15564 | -0.041199 | 0.36621 | 0.2243 | -0.20599 | -0.3479 | -0.032043 | -0.068664 | 60.878 | -61.9217 | 60.5484 | -61.8301 | 0.27924
660.7656 | 123.0148 | -60.8093 | 62.0682 | 0.14278 | 0.021657 | 0.022563 | 0.0094706 | 0.0040385 | 0.0013936 | -0.0010681 | -60.8643 | 62.1826 | -61.1206 | -0.054932 | -0.07782 | -0.091553 | 0.018311 | 0.07782 | 0.21057 | -0.33417 | -0.31128 | 0.11444 | -0.054932 | 60.7544 | -62.146 | 60.4752 | -61.8576 | 0.25635
661.7344 | 123.2208 | -60.7361 | 62.1002 | -0.086103 | 0.015249 | 0.014018 | -0.0005696 | 0.00083408 | 0.00053925 | 0.00042727 | -60.8368 | 62.0773 | -61.1114 | 0.11902 | 0.12817 | 0.16937 | -0.036621 | 0.37537 | 0.23346 | -0.20599 | -0.37537 | -0.022888 | -0.10071 | 60.8551 | -61.972 | 60.5301 | -61.8668 | 0.27466
662.7656 | 123.0652 | -60.7819 | 62.0728 | 1.5084 | 0.016317 | 0.017222 | 0.0086162 | 0.0051067 | 0.00096645 | -0.0017089 | -60.8734 | 62.1414 | -61.1389 | 0.041199 | 0.041199 | 0.018311 | 0.004578 | 0.20599 | 0.21973 | -0.27466 | -0.35706 | 0.068664 | -0.091553 | 60.8231 | -62.0316 | 60.5072 | -61.853 | 0.2655
663.7344 | 123.1842 | -60.7407 | 62.0728 | -0.14714 | 0.015462 | 0.016368 | -0.0022786 | -0.00023392 | -0.00095615 | -0.0012817 | -60.8322 | 62.059 | -61.1206 | 0.12817 | 0.13733 | 0.1831 | -0.068665 | 0.38452 | 0.22888 | -0.19684 | -0.37994 | -0.013733 | -0.091552 | 60.8688 | -61.9354 | 60.5438 | -61.8439 | 0.28839
664.7656 | 123.0286 | -60.7864 | 62.0956 | -0.62779 | 0.016958 | 0.017649 | 0.0062662 | 0.00083408 | 0.00118 | 6.6667e-08 | -60.9055 | 62.146 | -61.1618 | 0.032043 | 0.036621 | 0.050354 | 0.13733 | 0.23346 | 0.26093 | -0.22888 | -0.37537 | 0.050354 | -0.11902 | 60.8185 | -62.059 | 60.5576 | -61.8347 | 0.25635
665.7344 | 123.1018 | -60.759 | 62.0453 | 0.11989 | 0.015249 | 0.014659 | -0.002065 | 0.00019328 | -0.00095615 | 0.0025635 | -60.9009 | 62.0407 | -61.1069 | 0.032043 | 0.041199 | 0.036621 | -0.086975 | 0.2243 | 0.18768 | -0.27008 | -0.3479 | -0.004578 | -0.14191 | 60.791 | -62.0041 | 60.4889 | -61.8576 | 0.20599
666.7656 | 123.0835 | -60.7681 | 62.0041 | 0.26485 | 0.019735 | 0.017863 | 0.0086162 | 0.0042521 | -0.0018108 | -0.0010681 | -60.8597 | 62.1094 | -61.1481 | 0.013733 | -0.013733 | -0.032043 | -0.13275 | 0.15106 | 0.16937 | -0.37079 | -0.37994 | 0.10529 | -0.091553 | 60.7819 | -62.0178 | 60.3973 | -61.8347 | 0.28839
667.7344 | 123.1613 | -60.759 | 62.0361 | 0.028338 | 0.015035 | 0.015513 | -0.0012106 | -0.00023392 | 0.00053925 | 0.00042727 | -60.91 | 62.0499 | -61.1206 | 0.027466 | 0.027466 | 0.032043 | -0.064087 | 0.24719 | 0.19684 | -0.2655 | -0.36163 | 0.013733 | -0.15106 | 60.7864 | -62.0087 | 60.4935 | -61.8393 | 0.21057
668.75 | 123.0698 | -60.7636 | 62.0819 | -0.070844 | 0.020589 | 0.01829 | 0.007548 | 0.0012615 | -0.0013834 | -0.0017089 | -60.8231 | 62.1552 | -61.1206 | 0.064087 | 0.045776 | 0.032043 | 0.027466 | 0.24719 | 0.24261 | -0.2655 | -0.35705 | 0.073242 | -0.059509 | 60.8276 | -62.0361 | 60.498 | -61.8393 | 0.29755
669.7344 | 123.1155 | -60.7681 | 62.0361 | 0.10463 | 0.015249 | 0.015299 | -0.0005696 | 0.0019023 | 0.00118 | -0.0012817 | -60.7727 | 62.0865 | -61.1206 | 0.050354 | 0.045776 | 0.018311 | -0.064087 | 0.25635 | 0.20142 | -0.27466 | -0.35248 | 0.050354 | -0.004578 | 60.8185 | -61.9904 | 60.4935 | -61.8347 | 0.3479
670.7656 | 123.0515 | -60.7727 | 62.0544 | 0.21907 | 0.019735 | 0.022135 | 0.0066936 | -0.0013021 | -0.00074255 | 0.00085447 | -60.8917 | 62.1597 | -61.1252 | -0.11444 | -0.022888 | 0.11902 | -0.036621 | 0.045776 | 0.19226 | -0.32044 | -0.35248 | 0.10529 | -0.11902 | 60.6583 | -62.0773 | 60.4523 | -61.8622 | 0.23346
671.7344 | 123.1705 | -60.7315 | 62.0728 | -0.11662 | 0.014608 | 0.020213 | -0.0027058 | 0.00083408 | 0.00075285 | -0.00021353 | -60.8459 | 62.0453 | -61.1206 | 0.13275 | 0.1236 | 0.15564 | -0.036621 | 0.39825 | 0.2243 | -0.17395 | -0.3891 | -0.027466 | -0.11444 | 60.8643 | -61.9492 | 60.5576 | -61.8485 | 0.27466
672.75 | 123.0148 | -60.8002 | 62.0911 | -0.093733 | 0.016317 | 0.017863 | 0.0034892 | -2.0324e-05 | -0.00052895 | 0.0010681 | -60.8871 | 62.114 | -61.1252 | 0.018311 | 0.027466 | 0.050354 | 0.14191 | 0.26093 | 0.25635 | -0.17395 | -0.32501 | 0.022889 | -0.086975 | 60.8185 | -62.0636 | 60.6262 | -61.8347 | 0.23804
673.7344 | 123.1064 | -60.7864 | 62.0682 | 0.2267 | 0.016317 | 0.014231 | -0.0007832 | -2.0324e-05 | -0.0015972 | -0.0012817 | -60.9009 | 62.0361 | -61.1389 | 0.009155 | 0.009155 | 0.032043 | -0.09613 | 0.23346 | 0.1831 | -0.27008 | -0.35248 | -0.032043 | -0.11444 | 60.7956 | -62.059 | 60.5164 | -61.8851 | 0.23804
674.7656 | 123.0331 | -60.8093 | 62.0911 | -0.23869 | 0.019094 | 0.014445 | 0.0062662 | 0.0023295 | 0.00032545 | -0.0025635 | -60.9283 | 62.1506 | -61.1481 | 0.036621 | 0.022888 | 0.064087 | 0.13733 | 0.2243 | 0.2655 | -0.21973 | -0.33875 | 0.05951 | -0.11902 | 60.8459 | -62.0682 | 60.5896 | -61.8256 | 0.21973
675.7344 | 123.111 | -60.7407 | 62.0453 | 0.097002 | 0.016958 | 0.014445 | -0.0001424 | 0.00040688 | -0.0018108 | -0.0021361 | -60.9055 | 62.0682 | -61.1389 | 0.018311 | 0.036621 | 0.041199 | -0.082397 | 0.22888 | 0.19684 | -0.27924 | -0.39825 | 0.022888 | -0.16479 | 60.759 | -62.0087 | 60.4614 | -61.8484 | 0.23346
676.7812 | 123.0743 | -60.8002 | 62.0453 | 0.29537 | 0.01888 | 0.014445 | 0.009257 | 0.0010477 | -0.00052895 | -0.00064093 | -60.8551 | 62.1414 | -61.1298 | -0.013733 | -0.045776 | -0.068665 | -0.064087 | 0.10986 | 0.19684 | -0.32044 | -0.32959 | 0.09613 | -0.054932 | 60.7864 | -62.0911 | 60.4797 | -61.8484 | 0.27466
677.7344 | 123.1018 | -60.7727 | 62.0224 | 0.23433 | 0.017171 | 0.015727 | -0.0001424 | 0.0027567 | 0.00096645 | -0.0010681 | -60.8734 | 62.0682 | -61.1114 | 0.013733 | 0.032043 | -0.004578 | -0.10986 | 0.19684 | 0.17395 | -0.30212 | -0.33874 | 0.045776 | -0.10071 | 60.7864 | -61.9904 | 60.4706 | -61.8484 | 0.23804
678.7656 | 123.0652 | -60.791 | 62.0819 | -0.070844 | 0.019521 | 0.019145 | 0.0084026 | 0.0019023 | 0.0016072 | 0.00021367 | -60.8002 | 62.1689 | -61.1343 | 0.064087 | 0.045776 | 0.032043 | 0.018311 | 0.23804 | 0.21973 | -0.26093 | -0.34332 | 0.086975 | -0.009155 | 60.8551 | -62.0361 | 60.5301 | -61.8622 | 0.33417
679.7344 | 123.0927 | -60.7681 | 62.0361 | 0.20381 | 0.016744 | 0.016795 | -0.0022786 | 0.0019023 | 0.00011185 | -0.00085453 | -60.9055 | 62.0361 | -61.1114 | 0.022888 | 0.041199 | 0.027466 | -0.091553 | 0.21973 | 0.20142 | -0.28839 | -0.34332 | 0 | -0.13733 | 60.791 | -61.9949 | 60.4797 | -61.8347 | 0.20599
680.7656 | 123.0652 | -60.7681 | 62.0819 | -0.10136 | 0.021444 | 0.014872 | 0.0086162 | 0.0019023 | -0.00095615 | -0.0025635 | -60.8139 | 62.178 | -61.1069 | 0.073242 | 0.041199 | 0.064087 | 0.082397 | 0.25177 | 0.25635 | -0.23346 | -0.33875 | 0.096131 | -0.045777 | 60.8414 | -62.0407 | 60.5347 | -61.8256 | 0.29297
681.7344 | 123.1888 | -60.7086 | 62.0636 | -0.13188 | 0.018667 | 0.012736 | -0.0014242 | 0.0021159 | -0.0026652 | -0.00021353 | -60.8185 | 62.0728 | -61.1023 | 0.13275 | 0.11444 | 0.15106 | -0.041199 | 0.37537 | 0.24719 | -0.18768 | -0.39368 | 0.009155 | -0.10986 | 60.8414 | -61.9492 | 60.5209 | -61.8164 | 0.28381
682.7344 | 123.1476 | -60.7452 | 62.0178 | 0.26485 | 0.016958 | 0.016581 | 0.00648 | 0.0053203 | 0.00118 | -0.0017089 | -60.8322 | 62.0636 | -61.1114 | 0.3067 | 0.091553 | -0.086975 | -0.10071 | 0.32959 | 0.15564 | -0.36163 | -0.36621 | 0.045777 | -0.086975 | 61.0519 | -61.9263 | 60.3836 | -61.8622 | 0.27924
683.7344 | 123.1064 | -60.7727 | 62.0224 | 0.1733 | 0.019521 | 0.016795 | 0.0032756 | -2.0324e-05 | -0.0015972 | -0.0010681 | -60.8322 | 62.0453 | -61.1298 | 0.045776 | 0.050354 | 0.045776 | -0.16479 | 0.23346 | 0.16022 | -0.3479 | -0.35706 | 0.022888 | -0.059509 | 60.8185 | -61.972 | 60.4248 | -61.8622 | 0.29755
684.7344 | 123.1384 | -60.7544 | 62.027 | 0.28011 | 0.01888 | 0.016795 | 0.0062662 | 0.0014751 | 0.00032545 | -0.0021361 | -60.8139 | 62.0728 | -61.116 | 0.041199 | 0.045776 | 0.013733 | -0.20599 | 0.21515 | 0.14648 | -0.36163 | -0.36163 | 0.045776 | -0.059509 | 60.7956 | -61.9812 | 60.3928 | -61.8805 | 0.30212
685.7344 | 123.1338 | -60.7544 | 62.027 | 0.27248 | 0.018239 | 0.020854 | 0.0034892 | 0.0027567 | -0.0013834 | 0.00021367 | -60.8917 | 62.0407 | -61.1389 | 0.11902 | 0.018311 | -0.022888 | -0.10529 | 0.26093 | 0.18768 | -0.31586 | -0.38452 | 0.013732 | -0.13733 | 60.8734 | -62.0087 | 60.4385 | -61.8393 | 0.24719
686.7344 | 123.0469 | -60.7498 | 62.059 | -0.055586 | 0.020376 | 0.01594 | 0.0060526 | 0.0019023 | -0.0015972 | -0.0027771 | -60.8368 | 62.1231 | -61.1664 | 0.050354 | 0.027466 | 0.032043 | 0.013733 | 0.23346 | 0.23804 | -0.27008 | -0.41656 | 0.064087 | -0.086975 | 60.8002 | -62.0316 | 60.4797 | -61.821 | 0.32959
687.7344 | 123.1567 | -60.7452 | 62.0178 | 0.28011 | 0.01888 | 0.019358 | 0.0056254 | 0.0033977 | -0.00031535 | 0.00064087 | -60.8093 | 62.0911 | -61.1481 | 0.059509 | 0.045776 | 0.032043 | -0.19226 | 0.22888 | 0.16022 | -0.37079 | -0.40283 | 0.073242 | -0.064087 | 60.8047 | -61.972 | 60.3744 | -61.8576 | 0.33875
688.7344 | 123.1476 | -60.7544 | 62.0178 | 0.23433 | 0.021444 | 0.021922 | 0.0019938 | 0.0021159 | -0.0013834 | -0.0012817 | -60.9879 | 62.0453 | -61.1298 | 0.050354 | -0.004578 | 0.064087 | -0.11902 | 0.20142 | 0.17853 | -0.31128 | -0.37537 | 0.027466 | -0.23346 | 60.8047 | -62.0224 | 60.4431 | -61.8393 | 0.14191
689.7344 | 123.111 | -60.759 | 62.0407 | 0.21144 | 0.01653 | 0.018504 | 0.002421 | 0.00040688 | 0.0018208 | -0.0014953 | -60.8505 | 62.0682 | -61.116 | 0.036621 | 0.041199 | 0.027466 | -0.16022 | 0.20599 | 0.15564 | -0.35248 | -0.35706 | 0.027466 | -0.091553 | 60.7956 | -61.9995 | 60.4065 | -61.8851 | 0.2655
690.7344 | 123.1476 | -60.7361 | 62.0316 | 0.29537 | 0.019307 | 0.017436 | 0.004771 | 0.0014751 | -0.00052895 | 0.0019227 | -60.8047 | 62.0682 | -61.1252 | 0.045776 | 0.041199 | 0.032043 | -0.20599 | 0.21973 | 0.12817 | -0.35706 | -0.3891 | 0.036621 | -0.068665 | 60.7819 | -61.9904 | 60.379 | -61.9034 | 0.32043
691.7344 | 123.0743 | -60.7681 | 62.1002 | -0.18529 | 0.020589 | 0.015727 | 0.00648 | 0.00019328 | -0.0028788 | -0.0012817 | -60.9009 | 62.1231 | -61.1343 | 0.032043 | 0.013733 | 0.027466 | 0.11902 | 0.22888 | 0.2655 | -0.2243 | -0.36621 | 0.022888 | -0.13275 | 60.8002 | -62.0865 | 60.5438 | -61.8347 | 0.23346
692.7344 | 123.1293 | -60.7544 | 62.0316 | 0.18093 | 0.017598 | 0.018931 | -0.0005696 | 0.0016887 | 0.00011185 | 0.0023499 | -60.8322 | 62.0911 | -61.1114 | 0.018311 | 0.027466 | 0.004578 | -0.15564 | 0.20142 | 0.15564 | -0.33417 | -0.35705 | 0.059509 | -0.077819 | 60.7727 | -62.0041 | 60.4202 | -61.8759 | 0.27924
693.7344 | 123.1155 | -60.7361 | 62.0544 | 0.28011 | 0.01888 | 0.018077 | 0.005839 | 0.0031841 | -0.0011698 | -0.0010681 | -60.8322 | 62.1048 | -61.1526 | 0.018311 | -0.018311 | 0.004578 | -0.13733 | 0.21515 | 0.16937 | -0.38452 | -0.41656 | 0.050354 | -0.09613 | 60.7544 | -62.0728 | 60.3516 | -61.8851 | 0.32043
694.7344 | 123.1201 | -60.7681 | 62.0224 | 0.26485 | 0.020589 | 0.021708 | 0.0060526 | 0.0023295 | 0.00075285 | 0.00021367 | -60.8459 | 62.1185 | -61.1206 | 0.027466 | 0.009155 | -0.018311 | -0.14191 | 0.19684 | 0.17853 | -0.38452 | -0.35248 | 0.09613 | -0.07782 | 60.7956 | -62.0132 | 60.3836 | -61.8439 | 0.27466
695.7344 | 123.1201 | -60.7773 | 62.027 | 0.28011 | 0.020162 | 0.018504 | 0.0060526 | 0.0023295 | 0.00075285 | 0.00064087 | -60.8826 | 62.1323 | -61.1526 | 0.004578 | -0.013733 | -0.041199 | -0.12817 | 0.16022 | 0.16022 | -0.35248 | -0.37537 | 0.10529 | -0.10529 | 60.7819 | -62.0407 | 60.4248 | -61.8668 | 0.27008
696.7812 | 123.1247 | -60.7407 | 62.0499 | -0.12425 | 0.016958 | 0.014018 | -0.000356 | 0.0010477 | -0.0013834 | -0.00064093 | -60.8139 | 62.059 | -61.1069 | 0.11902 | 0.13275 | 0.15564 | -0.036621 | 0.37079 | 0.21973 | -0.21973 | -0.36621 | 0.009155 | -0.073242 | 60.8597 | -61.9171 | 60.5209 | -61.8301 | 0.29297
697.7344 | 123.0789 | -60.7636 | 62.0636 | 0.25722 | 0.020162 | 0.015299 | 0.0071208 | 0.0016887 | -0.00074255 | 0.00085447 | -60.8643 | 62.1368 | -61.116 | -0.018311 | -0.045776 | -0.064087 | -0.10529 | 0.13275 | 0.18768 | -0.3479 | -0.35248 | 0.073242 | -0.10071 | 60.7452 | -62.1094 | 60.4156 | -61.8759 | 0.25177
698.7656 | 123.0515 | -60.7681 | 62.0728 | -0.13951 | 0.019094 | 0.019999 | 0.0049846 | 0.0010477 | 0.00032545 | -0.0012817 | -60.8551 | 62.1735 | -61.1435 | 0.045776 | 0.036621 | 0.054932 | 0.10071 | 0.24719 | 0.2655 | -0.19226 | -0.37537 | 0.10071 | -0.086976 | 60.8139 | -62.0361 | 60.5759 | -61.8073 | 0.28839
699.7344 | 123.1522 | -60.7773 | 62.0224 | 0.34877 | 0.021871 | 0.019145 | 0.004771 | 0.0036113 | -0.0011698 | 0.00064087 | -60.8231 | 62.1048 | -61.1114 | 0.036621 | 0.027466 | 0.013733 | -0.16022 | 0.21973 | 0.16022 | -0.36163 | -0.33417 | 0.082397 | -0.045776 | 60.8139 | -61.9949 | 60.4156 | -61.8622 | 0.28839
700.75 | 123.1567 | -60.7498 | 62.0407 | -0.047956 | 0.016958 | 0.015513 | -0.002065 | 0.00019328 | -0.002238 | 0.00064087 | -60.8551 | 62.059 | -61.116 | 0.09613 | 0.10986 | 0.1236 | -0.09613 | 0.33875 | 0.21515 | -0.22888 | -0.36621 | 0.018311 | -0.10529 | 60.8459 | -61.9308 | 60.5209 | -61.8256 | 0.26093
701.7344 | 123.0469 | -60.759 | 62.114 | -0.13951 | 0.015249 | 0.018504 | 0.00413 | 0.0016887 | -0.00095615 | 0.0025635 | -60.7315 | 62.1277 | -61.1435 | 0.059509 | 0.032043 | -0.027466 | 0.12817 | 0.2655 | 0.24719 | -0.2243 | -0.38452 | 0.013733 | 0.027466 | 60.8185 | -62.0819 | 60.5347 | -61.8668 | 0.41199
702.7656 | 123.0606 | -60.7864 | 62.0956 | -0.10899 | 0.017812 | 0.016368 | 0.0071208 | 0.0023295 | -0.0015972 | 0.00064087 | -60.8551 | 62.1735 | -61.0977 | 0.036621 | 0.027466 | 0.022888 | 0.10071 | 0.23346 | 0.25635 | -0.21057 | -0.31128 | 0.07782 | -0.068665 | 60.8231 | -62.0682 | 60.5759 | -61.8393 | 0.24261
703.7344 | 123.1155 | -60.7498 | 62.0087 | 0.28011 | 0.018667 | 0.01829 | 0.0039164 | 0.0029705 | -0.00052895 | 6.6667e-08 | -60.8093 | 62.0636 | -61.116 | 0.059509 | 0.032043 | 0.059509 | -0.17395 | 0.22888 | 0.16479 | -0.35248 | -0.36621 | 0.054932 | -0.059509 | 60.8093 | -61.9766 | 60.3973 | -61.8439 | 0.3067
704.7656 | 123.0148 | -60.8002 | 62.0773 | 0.074114 | 0.01888 | 0.020426 | 0.0079752 | 0.0048931 | -0.00010175 | -0.0014953 | -60.8139 | 62.1872 | -61.1023 | 0 | -0.013733 | -0.036621 | 0.022888 | 0.15564 | 0.22888 | -0.31128 | -0.30212 | 0.10986 | -0.013733 | 60.8002 | -62.0911 | 60.4889 | -61.8484 | 0.28839
705.7344 | 123.0972 | -60.7864 | 62.0407 | 0.14278 | 0.019521 | 0.020213 | -0.0007832 | 0.0029705 | 0.002248 | 0.00064087 | -60.8643 | 62.0865 | -61.1206 | 0.004578 | 0.041199 | 0.013733 | -0.12817 | 0.20599 | 0.19684 | -0.28839 | -0.33417 | 0.045777 | -0.07782 | 60.791 | -61.9995 | 60.498 | -61.8439 | 0.25635
706.7656 | 123.0789 | -60.759 | 62.0865 | -0.19291 | 0.018453 | 0.015086 | -0.0009968 | 0.0010477 | -0.00010175 | 0.00085447 | -60.8368 | 62.1552 | -61.0794 | 0.064087 | 0.082397 | 0.10986 | 0.064087 | 0.30212 | 0.26093 | -0.19684 | -0.32044 | 0.068664 | -0.07782 | 60.8231 | -62.0041 | 60.5621 | -61.8256 | 0.24262
707.7344 | 123.143 | -60.7269 | 62.0316 | 0.34114 | 0.018667 | 0.015086 | 0.0043436 | 0.0033977 | -0.00074255 | 0.0029907 | -60.8047 | 62.0956 | -61.1023 | 0.045776 | 0.036621 | 0.022888 | -0.20599 | 0.21973 | 0.15106 | -0.3479 | -0.37537 | 0.064087 | -0.07782 | 60.7727 | -61.9949 | 60.379 | -61.8805 | 0.29755
708.7656 | 123.0194 | -60.7819 | 62.1048 | -0.29973 | 0.015035 | 0.011881 | 0.0037028 | -2.0324e-05 | -0.00010175 | -0.00042733 | -60.8871 | 62.1185 | -61.1389 | 0.027466 | 0.022888 | 0.050354 | 0.14648 | 0.25177 | 0.27924 | -0.16479 | -0.35706 | 0.013733 | -0.10529 | 60.8093 | -62.0819 | 60.6171 | -61.8256 | 0.25177
709.7344 | 123.143 | -60.7544 | 61.9995 | 0.23433 | 0.01888 | 0.021708 | 0.0049846 | 0.0033977 | -0.002238 | -0.00021353 | -60.8185 | 62.0819 | -61.1298 | 0.027466 | 0.009155 | 0.013733 | -0.16022 | 0.21515 | 0.16022 | -0.36163 | -0.37537 | 0.082397 | -0.064086 | 60.7819 | -61.9904 | 60.3928 | -61.8393 | 0.31128
710.7656 | 123.0423 | -60.7636 | 62.0819 | -0.27684 | 0.019307 | 0.013163 | -0.0005696 | 0.0019023 | -0.00052895 | -0.00021353 | -60.8734 | 62.1048 | -61.1343 | 0.036621 | 0.050354 | 0.09613 | 0.16479 | 0.24719 | 0.27008 | -0.16479 | -0.37079 | 0.022888 | -0.10986 | 60.8002 | -62.0316 | 60.5988 | -61.8118 | 0.26093
711.7344 | 123.1659 | -60.7544 | 62.0407 | 0.24959 | 0.01653 | 0.018931 | 0.0049846 | 0.0038249 | 0.00053925 | -0.0010681 | -60.8047 | 62.0773 | -61.0886 | 0.045776 | 0.032043 | 0.041199 | -0.18768 | 0.21973 | 0.15564 | -0.37537 | -0.33417 | 0.036622 | -0.050354 | 60.8002 | -62.0087 | 60.379 | -61.8851 | 0.28381
712.7656 | 123.0469 | -60.759 | 62.0865 | -0.086103 | 0.020803 | 0.019572 | 0.0094706 | 0.0038249 | -0.00010175 | -0.0010681 | -60.8047 | 62.1826 | -61.1252 | 0.022888 | 0.004578 | 0.004578 | 0.013733 | 0.18768 | 0.22888 | -0.27924 | -0.36621 | 0.09613 | -0.045777 | 60.7819 | -62.0819 | 60.4797 | -61.8576 | 0.32043
713.7344 | 123.1293 | -60.7681 | 62.0178 | 0.24196 | 0.019521 | 0.017008 | 0.0043436 | 0.0040385 | 0.0020344 | -0.00085453 | -60.8139 | 62.1002 | -61.1114 | 0.013733 | 0.045776 | 0.036621 | -0.19226 | 0.20142 | 0.16937 | -0.35706 | -0.34332 | 0.082398 | -0.045777 | 60.7819 | -61.972 | 60.4111 | -61.8484 | 0.29755
714.7656 | 123.0469 | -60.7773 | 62.0911 | -0.23106 | 0.020803 | 0.018504 | 0.0056254 | 0.0036113 | -0.0018108 | 0.00042727 | -60.8688 | 62.1826 | -61.1023 | 0.032043 | 0.013733 | 0.032043 | 0.11444 | 0.2243 | 0.26093 | -0.2243 | -0.32501 | 0.091553 | -0.091552 | 60.8093 | -62.0773 | 60.553 | -61.8301 | 0.23346
715.7344 | 123.0927 | -60.7681 | 62.027 | 0.27248 | 0.020376 | 0.016581 | 0.0043436 | 0.0053203 | -0.00010175 | -0.0012817 | -60.8643 | 62.1048 | -61.1298 | -0.018311 | -0.018311 | -0.027466 | -0.11444 | 0.15106 | 0.17853 | -0.33417 | -0.36163 | 0.077819 | -0.096131 | 60.7498 | -62.0453 | 60.434 | -61.8484 | 0.2655
716.75 | 123.0652 | -60.759 | 62.0865 | -0.10899 | 0.019521 | 0.018077 | 0.0056254 | 0.0033977 | -0.00095615 | -0.0014953 | -60.8322 | 62.1231 | -61.1526 | 0.050354 | 0.045776 | 0.059509 | 0.036621 | 0.24719 | 0.26093 | -0.25177 | -0.39368 | 0.036621 | -0.073242 | 60.8093 | -62.0407 | 60.5072 | -61.8256 | 0.32043
717.7344 | 123.1155 | -60.7864 | 62.027 | 0.25722 | 0.020803 | 0.018504 | 0.0034892 | 0.0036113 | -0.00052895 | 0.00085447 | -60.8505 | 62.1002 | -61.1343 | 0.013733 | -0.009155 | -0.004578 | -0.1236 | 0.19226 | 0.14648 | -0.37994 | -0.3479 | 0.073242 | -0.064087 | 60.8002 | -62.0361 | 60.4065 | -61.8805 | 0.28381
718.7656 | 123.1338 | -60.7452 | 62.0453 | -0.19291 | 0.017385 | 0.021495 | -0.0050558 | -0.00023392 | 0.00053925 | 6.6667e-08 | -60.8368 | 62.0819 | -61.0931 | -0.23804 | 0.086975 | 0.30212 | -0.19684 | 0.23804 | 0.23804 | -0.21973 | -0.3479 | 0.036621 | -0.091553 | 60.5072 | -61.9583 | 60.5255 | -61.8073 | 0.25635
719.7344 | 123.1201 | -60.7407 | 62.027 | 0.24196 | 0.019094 | 0.016368 | 0.005839 | 0.0016887 | 0.00053925 | -0.00064093 | -60.8093 | 62.1048 | -61.1206 | -0.004578 | 0.022888 | 0.054932 | -0.16022 | 0.18768 | 0.15564 | -0.37079 | -0.37994 | 0.077819 | -0.068664 | 60.7361 | -62.0041 | 60.3699 | -61.8713 | 0.31128
720.75 | 123.1064 | -60.7498 | 62.0728 | 0.1733 | 0.016317 | 0.014445 | -0.000356 | 0.00062048 | 0.00075285 | 0.00042727 | -60.8871 | 62.0544 | -61.116 | 0.004578 | 0.018311 | 0.036621 | -0.082397 | 0.21973 | 0.19226 | -0.29297 | -0.36621 | -0.018311 | -0.13733 | 60.7544 | -62.0544 | 60.4568 | -61.8805 | 0.22888
721.7344 | 123.0286 | -60.7773 | 62.0865 | 0.11226 | 0.022298 | 0.017008 | 0.0094706 | 0.0031841 | -0.0013834 | 0.0017091 | -60.8597 | 62.178 | -61.1206 | -0.041199 | -0.07782 | -0.07782 | 0.036621 | 0.11444 | 0.21057 | -0.32959 | -0.34332 | 0.091553 | -0.082397 | 60.7361 | -62.1643 | 60.4477 | -61.8759 | 0.26093
722.75 | 123.1842 | -60.7361 | 62.0682 | -0.025068 | 0.017385 | 0.012736 | -0.003774 | 0.00083408 | -0.00010175 | -0.00042733 | -60.8322 | 62.0682 | -61.0931 | 0.11902 | 0.14191 | 0.15564 | -0.059509 | 0.38452 | 0.21515 | -0.1831 | -0.35706 | 0 | -0.09613 | 60.8551 | -61.9263 | 60.553 | -61.853 | 0.26093
723.7344 | 122.9828 | -60.8139 | 62.0819 | 0.11989 | 0.021871 | 0.019786 | 0.009257 | 0.0031841 | -0.00031535 | -0.0023499 | -60.8643 | 62.1964 | -61.1389 | -0.050354 | -0.07782 | -0.091553 | 0.018311 | 0.10071 | 0.20599 | -0.35248 | -0.32501 | 0.11444 | -0.050354 | 60.7636 | -62.1597 | 60.4614 | -61.8759 | 0.27466
724.7656 | 123.0606 | -60.7681 | 62.0819 | -0.078474 | 0.019948 | 0.021922 | 0.0034892 | 0.0027567 | -0.0020244 | 0.0012817 | -60.878 | 62.1826 | -61.1069 | 0.013733 | 0.009155 | 0.027466 | 0.12817 | 0.2243 | 0.27924 | -0.20599 | -0.33875 | 0.10071 | -0.10986 | 60.7819 | -62.0728 | 60.5621 | -61.8027 | 0.22888
725.7344 | 123.0331 | -60.7864 | 62.0773 | 0.16567 | 0.020803 | 0.021495 | 0.0073344 | 0.0048931 | -0.0011698 | 0.00085447 | -60.8597 | 62.1643 | -61.1206 | -0.064087 | -0.068665 | -0.10986 | 0.013733 | 0.059509 | 0.19226 | -0.37537 | -0.33417 | 0.086975 | -0.073242 | 60.7224 | -62.146 | 60.4111 | -61.8851 | 0.26093
726.7656 | 123.0194 | -60.7819 | 62.0865 | -0.18529 | 0.015249 | 0.016581 | -0.0005696 | 0.0019023 | 0.00053925 | 0.0014953 | -60.8917 | 62.1185 | -61.1298 | 0.009155 | 0.004578 | 0.045776 | 0.16022 | 0.27924 | 0.27924 | -0.16479 | -0.3479 | 0.032043 | -0.10986 | 60.791 | -62.0819 | 60.6171 | -61.8073 | 0.23804
727.7344 | 123.0377 | -60.7773 | 62.0819 | 0.12752 | 0.021871 | 0.017863 | 0.005839 | 0.0040385 | -0.0013834 | -0.0012817 | -60.8185 | 62.178 | -61.1114 | -0.018311 | -0.036621 | -0.045776 | 0.018311 | 0.13275 | 0.24261 | -0.30212 | -0.33417 | 0.096131 | -0.041198 | 60.759 | -62.1185 | 60.4752 | -61.8393 | 0.29297
728.7656 | 123.1659 | -60.7132 | 62.0728 | -0.025068 | 0.016744 | 0.015086 | -0.0031332 | 0.0027567 | 0.00032545 | -0.00042733 | -60.8322 | 62.0728 | -61.1023 | 0.11444 | 0.11902 | 0.16937 | -0.054932 | 0.36621 | 0.21515 | -0.18768 | -0.3891 | 0 | -0.11902 | 60.8276 | -61.9537 | 60.5255 | -61.8576 | 0.27008
729.7344 | 123.0652 | -60.7773 | 62.0819 | 0.16567 | 0.019735 | 0.017008 | 0.007548 | 0.0046793 | 0.00032545 | 0.00042727 | -60.7773 | 62.1964 | -61.1114 | 0.032043 | 0.009155 | 0.022888 | 0.013733 | 0.21057 | 0.24261 | -0.28839 | -0.33417 | 0.11444 | 0 | 60.8093 | -62.0728 | 60.4889 | -61.8393 | 0.33417
730.7656 | 123.1796 | -60.7407 | 62.0316 | -0.15477 | 0.01653 | 0.019572 | -0.0035604 | 0.0010477 | 0.0016072 | 0.0021363 | -60.8185 | 62.0636 | -61.0931 | 0.11902 | 0.14191 | 0.17853 | -0.059509 | 0.3891 | 0.22888 | -0.17853 | -0.35248 | 0.032044 | -0.077819 | 60.8597 | -61.8896 | 60.5621 | -61.8027 | 0.27466
731.7344 | 123.0377 | -60.7819 | 62.0819 | -0.086103 | 0.021016 | 0.01594 | 0.0060526 | 0.0029705 | -0.0015972 | 0.0010681 | -60.8002 | 62.1689 | -61.116 | 0.027466 | -0.013733 | -0.013733 | 0.004578 | 0.17853 | 0.22888 | -0.30212 | -0.33417 | 0.086975 | -0.018311 | 60.8093 | -62.0956 | 60.4797 | -61.853 | 0.31586
732.7656 | 123.1064 | -60.7361 | 62.0499 | 0.058855 | 0.015462 | 0.012309 | 0.0002848 | 0.0019023 | 0.00075285 | 0.0010681 | -60.8871 | 62.0773 | -61.1114 | 0 | 0.032043 | 0.064087 | -0.050354 | 0.23804 | 0.20599 | -0.27924 | -0.37537 | 0.027466 | -0.15106 | 60.7361 | -62.0178 | 60.4568 | -61.8439 | 0.2243
733.7344 | 123.0286 | -60.7773 | 62.0682 | -0.047956 | 0.019948 | 0.016368 | 0.007548 | 0.0027567 | 0.00118 | -0.0014953 | -60.7956 | 62.1506 | -61.116 | 0.054932 | 0.022888 | 0.022888 | 0 | 0.21973 | 0.21973 | -0.27008 | -0.33875 | 0.082398 | -0.01831 | 60.8322 | -62.0453 | 60.5072 | -61.8484 | 0.32044
734.7656 | 123.143 | -60.7407 | 62.0316 | 0.24959 | 0.019094 | 0.018931 | -0.0001424 | 0.00083408 | 0.00096645 | 6.6667e-08 | -60.8185 | 62.0682 | -61.1343 | 0.004578 | 0.091553 | 0.15564 | -0.23804 | 0.21515 | 0.16479 | -0.31586 | -0.39368 | 0.036621 | -0.077819 | 60.7452 | -61.94 | 60.4248 | -61.8668 | 0.31586
735.7344 | 123.0469 | -60.7773 | 62.0956 | -0.10136 | 0.018453 | 0.018504 | 0.0056254 | 0.0021159 | -0.00052895 | -0.0021361 | -60.7956 | 62.1826 | -61.1069 | 0.059509 | 0.041199 | 0.041199 | 0.036621 | 0.23804 | 0.27924 | -0.27008 | -0.32959 | 0.086975 | -0.01831 | 60.8368 | -62.0544 | 60.5072 | -61.8164 | 0.31128
736.7656 | 123.0835 | -60.7498 | 62.0544 | 0.21907 | 0.01888 | 0.017008 | 0.000712 | 0.0031841 | 0.0018208 | -0.00042733 | -60.8551 | 62.0453 | -61.1435 | 0 | 0.018311 | 0.022888 | -0.12817 | 0.20599 | 0.1831 | -0.28839 | -0.39368 | -0.009155 | -0.10529 | 60.7498 | -62.0361 | 60.4614 | -61.8713 | 0.28839
737.7344 | 123.0698 | -60.7819 | 62.1094 | -0.14714 | 0.020376 | 0.014445 | 0.0054118 | 0.0023295 | 0.00096645 | -0.0019225 | -60.8505 | 62.2101 | -61.1069 | 0.022888 | 0.013733 | 0.041199 | 0.11444 | 0.25635 | 0.2655 | -0.20142 | -0.32501 | 0.10071 | -0.068665 | 60.8047 | -62.0956 | 60.5804 | -61.8439 | 0.25635
738.7656 | 123.1247 | -60.7132 | 62.0819 | -0.20817 | 0.015035 | 0.011668 | -0.0056966 | -0.00066112 | -0.00031535 | 6.6667e-08 | -60.8185 | 62.059 | -61.0886 | -0.16022 | 0.17395 | 0.21057 | -0.21057 | 0.29297 | 0.22888 | -0.21515 | -0.37537 | -0.022888 | -0.10528 | 60.553 | -61.908 | 60.498 | -61.853 | 0.27008
739.7344 | 123.0698 | -60.759 | 62.0819 | -0.15477 | 0.018453 | 0.017008 | 0.007548 | 0.0025431 | -0.0011698 | -0.00021353 | -60.8185 | 62.2055 | -61.1114 | 0.064087 | 0.022888 | 0.064087 | 0.086975 | 0.25177 | 0.26093 | -0.21515 | -0.35248 | 0.1236 | -0.059509 | 60.8231 | -62.059 | 60.5438 | -61.821 | 0.29297
740.7656 | 123.1293 | -60.759 | 62.0544 | 0.24959 | 0.018026 | 0.021067 | 0.0054118 | 0.0042521 | 0.00053925 | -0.00021353 | -60.8185 | 62.1094 | -61.116 | 0.054932 | 0.050354 | 0 | -0.19684 | 0.20599 | 0.17395 | -0.37079 | -0.35706 | 0.054932 | -0.059509 | 60.8139 | -62.0041 | 60.3882 | -61.8805 | 0.29755
741.7344 | 123.0515 | -60.7773 | 62.114 | -0.1624 | 0.019307 | 0.014659 | 0.0026346 | 0.00083408 | -0.0013834 | -0.00042733 | -60.8505 | 62.2101 | -61.1114 | 0.027466 | 0.032043 | 0.032043 | 0.10986 | 0.23346 | 0.27466 | -0.19684 | -0.33417 | 0.09613 | -0.073242 | 60.8047 | -62.0819 | 60.5804 | -61.8393 | 0.26093
742.7656 | 123.1567 | -60.7498 | 62.0361 | 0.27248 | 0.020589 | 0.020854 | 0.0045574 | 0.0042521 | 0.0018208 | -0.0023499 | -60.7864 | 62.1185 | -61.1206 | 0.032043 | 0.045776 | 0.032043 | -0.20142 | 0.19226 | 0.16479 | -0.36163 | -0.37079 | 0.082397 | -0.036621 | 60.7819 | -61.9904 | 60.3882 | -61.8713 | 0.33417
743.7344 | 122.9965 | -60.7727 | 62.0956 | -0.20817 | 0.018667 | 0.015727 | 0.0026346 | 0.0023295 | -0.00031535 | 0.00021367 | -60.8871 | 62.1964 | -61.1069 | 0.013733 | 0.009155 | 0.032043 | 0.26093 | 0.65918 | 0.30212 | -0.12817 | -0.33417 | 0.10071 | -0.11444 | 60.7864 | -62.0865 | 60.6445 | -61.7935 | 0.21973
744.7656 | 123.0881 | -60.7498 | 62.0453 | 0.21907 | 0.018239 | 0.017649 | -0.000356 | 0.0021159 | 0.0018208 | 0.0017091 | -60.8597 | 62.0636 | -61.1435 | -0.009155 | 0.032043 | 0.013733 | -0.12817 | 0.20599 | 0.17853 | -0.28381 | -0.39368 | 0.018311 | -0.10986 | 60.7407 | -62.0132 | 60.466 | -61.8668 | 0.28381
745.7344 | 122.9828 | -60.7819 | 62.0911 | -0.19291 | 0.019521 | 0.014872 | 0.0034892 | -0.0030111 | -0.00074255 | 0.00085447 | -60.8505 | 62.1689 | -61.1252 | -0.23804 | -0.064087 | 0.14191 | 0.068665 | 0.12817 | 0.25635 | -0.18768 | -0.34332 | 0.07782 | -0.068665 | 60.5438 | -62.1552 | 60.5942 | -61.8347 | 0.27466
746.75 | 123.0743 | -60.7681 | 62.0361 | 0.28774 | 0.021871 | 0.021281 | 0.0054118 | 0.0036113 | -0.00031535 | -0.0012817 | -60.8459 | 62.1689 | -61.1023 | -0.022888 | -0.032043 | -0.054932 | -0.10529 | 0.13733 | 0.17395 | -0.36163 | -0.33417 | 0.13275 | -0.07782 | 60.7452 | -62.0682 | 60.4065 | -61.8622 | 0.25635
747.7344 | 123.0011 | -60.7681 | 62.1277 | -0.10899 | 0.017812 | 0.021067 | 0.0022074 | 0.0027567 | 0.00011185 | 0.00021367 | -60.8963 | 62.1643 | -61.1343 | 0.045776 | 0.032043 | 0.050354 | 0.15106 | 0.25635 | 0.2655 | -0.17395 | -0.36621 | 0.036621 | -0.12817 | 60.8139 | -62.0956 | 60.5942 | -61.8622 | 0.23804
748.7656 | 123.0743 | -60.7727 | 62.0316 | 0.10463 | 0.01653 | 0.013804 | -0.0033468 | 0.0010477 | 0.00096645 | -0.0010681 | -60.8643 | 62.0911 | -61.1206 | 0.018311 | 0.21057 | 0.28839 | -0.21515 | 0.13275 | 0.22888 | -0.25177 | -0.3479 | 0.059509 | -0.091553 | 60.791 | -61.821 | 60.5209 | -61.8027 | 0.25635
749.7344 | 123.0789 | -60.7407 | 62.114 | -0.17766 | 0.014394 | 0.018077 | 0.0022074 | -0.0013021 | -0.00052895 | -0.00085453 | -60.8368 | 62.0819 | -61.0977 | 0.059509 | 0.07782 | 0.11902 | 0.059509 | 0.31586 | 0.27008 | -0.19226 | -0.35706 | -0.032044 | -0.09613 | 60.8002 | -62.0361 | 60.5484 | -61.8439 | 0.26093
750.7656 | 123.175 | -60.7498 | 62.0453 | 0.303 | 0.019307 | 0.017863 | 0.0039164 | 0.00062048 | -0.00095615 | 0.00064087 | -60.8002 | 62.0911 | -61.1023 | 0.045776 | 0.036621 | 0.027466 | -0.55389 | -0.19226 | 0.13733 | -0.44861 | -0.35248 | 0.045776 | -0.050354 | 60.7956 | -62.0087 | 60.3012 | -61.908 | 0.30212
751.7344 | 123.1384 | -60.7452 | 62.0773 | -1.2534 | 0.015035 | 0.019145 | 0.002421 | -0.0023701 | 0.00011185 | 0.0017091 | -60.9558 | 62.114 | -61.0931 | 0.086975 | 0.059509 | 0.14191 | -0.004578 | 0.35248 | 0.21973 | -0.22888 | -0.3479 | 0.036621 | -0.21057 | 60.8322 | -62.0178 | 60.5164 | -61.8576 | 0.13733
752.75 | 123.0377 | -60.8047 | 62.0911 | 0.23433 | 0.019948 | 0.019572 | 0.010325 | 0.00062048 | -0.00052895 | -0.0029907 | -60.8688 | 62.1689 | -61.1481 | -0.050354 | -0.073242 | -0.10986 | -0.009155 | 0.09613 | 0.21057 | -0.3479 | -0.34332 | 0.07782 | -0.064086 | 60.7544 | -62.1643 | 60.4568 | -61.8805 | 0.27924
753.7344 | 123.1293 | -60.7361 | 62.0682 | -0.35313 | 0.01888 | 0.017649 | 0.0022074 | 0.00019328 | 0.00032545 | -0.0029907 | -60.8002 | 62.0865 | -61.1069 | 0.10529 | 0.09613 | 0.13275 | 0.004578 | 0.33417 | 0.23346 | -0.21515 | -0.37079 | 0.018311 | -0.064087 | 60.8414 | -61.972 | 60.5209 | -61.8347 | 0.3067
754.75 | 123.0515 | -60.7727 | 62.1002 | -0.10899 | 0.020162 | 0.01829 | 0.0066936 | 0.0021159 | -0.0024516 | -0.0014953 | -60.7636 | 62.1918 | -61.0886 | 0.064087 | 0.045776 | 0.045776 | 0.027466 | 0.23346 | 0.23804 | -0.25635 | -0.31586 | 0.091552 | 0.009155 | 60.8368 | -62.0544 | 60.5164 | -61.8622 | 0.32501
755.7344 | 123.0652 | -60.7224 | 62.059 | -0.13188 | 0.016317 | 0.016154 | -0.0009968 | 0.0016887 | 0.00011185 | -0.00085453 | -60.8139 | 62.0728 | -61.0886 | 0.11902 | 0.10986 | 0.15564 | -0.032043 | 0.74158 | 0.23346 | -0.16937 | -0.36621 | 0.013733 | -0.091553 | 60.8414 | -61.9492 | 60.553 | -61.8256 | 0.27466
756.7656 | 123.1293 | -60.7498 | 62.0682 | 0.27248 | 0.017598 | 0.018931 | 0.0051982 | 0.0044657 | 0.0016072 | 6.6667e-08 | -60.8231 | 62.1094 | -61.1069 | 0.054932 | 0.036621 | -0.045776 | -0.21973 | 0.20142 | 0.14191 | -0.37994 | -0.35706 | 0.041199 | -0.073242 | 60.8047 | -62.0316 | 60.3699 | -61.9263 | 0.28381
757.75 | 123.0148 | -60.791 | 62.0956 | 0.089373 | 0.021016 | 0.019999 | 0.0096842 | 0.0031841 | 0.00096645 | -0.00042733 | -60.8505 | 62.2009 | -61.116 | -0.045776 | -0.059509 | -0.09613 | 0.009155 | 0.10071 | 0.20599 | -0.33875 | -0.32501 | 0.10529 | -0.059509 | 60.7452 | -62.1552 | 60.4523 | -61.8896 | 0.2655
758.7656 | 123.0057 | -60.791 | 62.0819 | 0.097002 | 0.021871 | 0.019786 | 0.007548 | 0.0027567 | -0.0015972 | -0.0010681 | -60.8414 | 62.2055 | -61.1252 | -0.059509 | -0.082397 | -0.10071 | 0.018311 | 0.086975 | 0.2243 | -0.35248 | -0.33417 | 0.1236 | -0.050354 | 60.7315 | -62.1643 | 60.4385 | -61.8576 | 0.28381
759.7344 | 123.1293 | -60.7224 | 62.0956 | -0.13188 | 0.015889 | 0.017649 | -0.0035604 | 0.0031841 | -0.00010175 | 0.00021367 | -60.8139 | 62.0819 | -61.0931 | 0.11902 | 0.13275 | 0.16937 | -0.036621 | 0.37537 | 0.23346 | -0.19684 | -0.37079 | -0.013733 | -0.091553 | 60.8414 | -61.9629 | 60.5255 | -61.8622 | 0.27924
760.75 | 123.0103 | -60.7819 | 62.0773 | 0.051226 | 0.018667 | 0.021708 | 0.0088298 | 0.0019023 | 0.00011185 | -0.0019225 | -60.8185 | 62.2055 | -61.1252 | -0.009155 | -0.022888 | -0.022888 | 0.018311 | 0.16022 | 0.21515 | -0.32044 | -0.34332 | 0.12817 | -0.036621 | 60.7727 | -62.1002 | 60.4614 | -61.8622 | 0.3067
761.7344 | 123.1705 | -60.7361 | 62.0773 | -0.032697 | 0.016958 | 0.017008 | -0.0056966 | 0.0019023 | -0.0013834 | -0.00064093 | -60.7956 | 62.059 | -61.084 | 0.1236 | 0.15564 | 0.19226 | -0.050354 | 0.3891 | 0.23804 | -0.21057 | -0.3479 | -0.018311 | -0.059509 | 60.8597 | -61.9217 | 60.5255 | -61.8393 | 0.28839
762.7656 | 123.0789 | -60.7544 | 62.0682 | 0.23433 | 0.019307 | 0.018717 | 0.005839 | 0.0029705 | -0.00010175 | -0.00021353 | -60.8414 | 62.1231 | -61.116 | -0.032043 | -0.041199 | -0.059509 | -0.10529 | 0.14191 | 0.17853 | -0.35706 | -0.36163 | 0.054932 | -0.086975 | 60.7224 | -62.1094 | 60.3973 | -61.8896 | 0.27466
763.7344 | 123.1705 | -60.7178 | 62.0407 | 0.028338 | 0.015676 | 0.011668 | -0.0024922 | -0.00023392 | 0.0016072 | 0.00021367 | -60.8185 | 62.0773 | -61.0931 | 0.091553 | 0.1236 | 0.16022 | -0.068665 | 0.3479 | 0.21973 | -0.21973 | -0.37537 | 0.036622 | -0.10071 | 60.8093 | -61.9171 | 60.498 | -61.821 | 0.27466
764.75 | 123.0515 | -60.7498 | 62.1094 | -0.10899 | 0.020162 | 0.01829 | 0.0077616 | 0.0023295 | 0.00053925 | -0.0014953 | -60.8185 | 62.1872 | -61.116 | 0.041199 | 0.027466 | 0.050354 | 0.086975 | 0.27008 | 0.26093 | -0.20142 | -0.36621 | 0.07782 | -0.068664 | 60.791 | -62.0819 | 60.5484 | -61.8484 | 0.29755
765.7344 | 123.1201 | -60.7452 | 62.0773 | -0.0098092 | 0.016958 | 0.017008 | -0.0029196 | 0.0014751 | -0.00074255 | -0.00064093 | -60.7498 | 62.1002 | -61.0977 | 0.045776 | 0.022888 | 0.013733 | -0.059509 | 0.26093 | 0.21973 | -0.2655 | -0.35248 | 0.022888 | -0.004578 | 60.791 | -62.0544 | 60.4797 | -61.8576 | 0.3479
766.75 | 123.0606 | -60.8002 | 62.0865 | 0.020708 | 0.019521 | 0.021495 | 0.010112 | 0.0023295 | -0.0020244 | -0.00064093 | -60.7819 | 62.1918 | -61.0977 | 0.027466 | -0.022888 | -0.027466 | 0 | 0.15564 | 0.21515 | -0.29297 | -0.29755 | 0.10529 | 0.018311 | 60.8276 | -62.1094 | 60.5072 | -61.8713 | 0.31586
767.75 | 123.0331 | -60.7819 | 62.0911 | 0.051226 | 0.021657 | 0.017436 | 0.0069072 | 0.0031841 | 0.00118 | -0.0014953 | -60.8002 | 62.1872 | -61.1023 | 0.050354 | 0 | 0.009155 | 0.018311 | 0.19226 | 0.23804 | -0.28381 | -0.32043 | 0.096131 | -0.018311 | 60.8322 | -62.0911 | 60.498 | -61.853 | 0.30212
768.7656 | 123.1476 | -60.7269 | 62.0499 | -0.032697 | 0.016958 | 0.014659 | -0.0050558 | 0.00019328 | 0.00096645 | 6.6667e-08 | -60.8459 | 62.0865 | -61.1114 | 0.082397 | 0.11444 | 0.1236 | -0.082397 | 0.31586 | 0.21515 | -0.24261 | -0.38452 | 0.036621 | -0.11902 | 60.8093 | -61.9354 | 60.4843 | -61.8347 | 0.2655
769.7344 | 123.1522 | -60.7224 | 62.0728 | -0.055586 | 0.014181 | 0.014659 | -0.0018514 | 0.0010477 | -0.0015972 | 0.0012817 | -60.8276 | 62.1048 | -61.1023 | 0.086975 | 0.10986 | 0.11902 | -0.091553 | 0.32044 | 0.2243 | -0.2243 | -0.37994 | 0.032043 | -0.10529 | 60.8093 | -61.9629 | 60.498 | -61.8485 | 0.27466
770.7656 | 123.0423 | -60.7544 | 62.0956 | -0.69645 | 0.019735 | 0.023844 | 0.012034 | 0.00083408 | -0.00031535 | -0.0025635 | -60.7498 | 62.1735 | -61.0886 | 0.027466 | -0.009155 | 0.018311 | 0.013733 | 0.20599 | 0.2243 | -0.27924 | -0.33417 | 0.07782 | 0.004578 | 60.7819 | -62.1048 | 60.4752 | -61.8713 | 0.33875
771.7344 | 123.1476 | -60.704 | 62.0682 | -0.055586 | 0.016103 | 0.013377 | -0.0031332 | 0.0016887 | -0.00074255 | 0.0017091 | -60.8459 | 62.0636 | -61.1252 | 0.082397 | 0.10071 | 0.10529 | -0.082397 | 0.31586 | 0.21515 | -0.23804 | -0.42114 | -0.004577 | -0.14191 | 60.7864 | -61.9675 | 60.466 | -61.853 | 0.27924
772.7656 | 123.143 | -60.7498 | 62.0773 | 0.14278 | 0.01888 | 0.014231 | 0.0002848 | -0.0010885 | 0.00053925 | 0.00085447 | -60.8368 | 62.1368 | -61.084 | 0.045776 | 0.050354 | 0.07782 | -0.068665 | 0.2655 | 0.20142 | -0.25635 | -0.33417 | 0.059509 | -0.086975 | 60.7956 | -62.027 | 60.4935 | -61.8759 | 0.24719
773.7344 | 123.175 | -60.7269 | 62.0819 | -0.063215 | 0.015676 | 0.013163 | 0.0002848 | -0.00044752 | -0.00010175 | 6.6667e-08 | -60.8185 | 62.0865 | -61.0886 | 0.10986 | 0.11902 | 0.14191 | -0.091553 | 0.3479 | 0.21057 | -0.2243 | -0.36163 | 0.004578 | -0.091552 | 60.8368 | -61.9629 | 60.5026 | -61.8713 | 0.27008
774.75 | 123.0423 | -60.7361 | 62.1323 | -0.22343 | 0.017598 | 0.014231 | 0.0084026 | 0.00062048 | -0.00074255 | -0.00021353 | -60.9329 | 62.1643 | -61.0886 | -0.013733 | -0.07782 | 0.036621 | 0.15564 | 0.16479 | 0.26093 | -0.24261 | -0.35248 | 0.032044 | -0.19684 | 60.7224 | -62.2101 | 60.4935 | -61.8713 | 0.15564
775.7344 | 123.111 | -60.7636 | 62.0499 | 0.058855 | 0.016103 | 0.012309 | 0.0002848 | 0.0019023 | -0.00010175 | -0.00021353 | -60.8643 | 62.0773 | -61.116 | 0.009155 | 0.027466 | 0.064087 | -0.07782 | 0.21515 | 0.21515 | -0.2655 | -0.35248 | 0.027466 | -0.10071 | 60.7727 | -62.0224 | 60.498 | -61.8347 | 0.25177
776.7656 | 123.0423 | -60.7864 | 62.0911 | 0.058855 | 0.02123 | 0.018931 | 0.012034 | 0.0019023 | -0.00095615 | -0.0025635 | -60.7727 | 62.1872 | -61.1114 | 0.022888 | -0.032043 | -0.045776 | 0.009155 | 0.15564 | 0.21057 | -0.29755 | -0.32501 | 0.096131 | 0.013733 | 60.8093 | -62.1231 | 60.4889 | -61.8805 | 0.33874
777.7344 | 123.143 | -60.704 | 62.0773 | -0.0098092 | 0.016317 | 0.011668 | -0.0031332 | -0.00044752 | -0.0011698 | 0.00085447 | -60.8276 | 62.1002 | -61.1114 | 0.09613 | 0.11902 | 0.16022 | -0.082397 | 0.32501 | 0.21057 | -0.22888 | -0.40741 | 0.022888 | -0.1236 | 60.8002 | -61.9583 | 60.4752 | -61.8668 | 0.28381
778.7656 | 123.0972 | -60.7315 | 62.0728 | 0.081743 | 0.016317 | 0.012309 | 0.0004984 | -0.0021565 | -0.00095615 | 0.00085447 | -60.8551 | 62.0865 | -61.0977 | 0.064087 | 0.19226 | 0.25635 | -0.25635 | 0.12817 | 0.21057 | -0.25635 | -0.36621 | 0.013733 | -0.1236 | 60.7956 | -61.8805 | 60.4752 | -61.8622 | 0.24261
779.7344 | 123.0835 | -60.7361 | 62.0361 | 0.081743 | 0.015249 | 0.015299 | -0.0007832 | -0.00066112 | -0.0028788 | -0.0019225 | -60.8551 | 62.0499 | -61.1069 | 0.041199 | 0.032043 | 0.36163 | -0.10986 | 0.10071 | 0.20599 | -0.24261 | -0.37079 | 0.013733 | -0.11902 | 60.7773 | -62.0041 | 60.4935 | -61.8301 | 0.25177
780.7656 | 123.0148 | -60.7819 | 62.114 | 0.081743 | 0.022512 | 0.020213 | 0.009257 | 0.00019328 | -0.00010175 | -0.0027771 | -60.8093 | 62.1964 | -61.0748 | -0.013733 | -0.059509 | -0.082397 | 0.013733 | 0.11444 | 0.20142 | -0.32501 | -0.29297 | 0.082397 | -0.027466 | 60.7681 | -62.1735 | 60.4568 | -61.9125 | 0.2655
781.7344 | 123.1064 | -60.7544 | 62.0682 | -0.75749 | 0.017171 | 0.016581 | -0.0035604 | -0.0013021 | -0.00052895 | -0.00042733 | -60.9283 | 62.1002 | -61.0977 | 0.009155 | 0.032043 | 0.054932 | -0.068665 | 0.25177 | 0.18768 | -0.27008 | -0.34332 | 0.032044 | -0.17395 | 60.7636 | -62.0361 | 60.4843 | -61.8805 | 0.16937
782.7656 | 122.9828 | -60.7727 | 62.1094 | 0.089373 | 0.021016 | 0.01594 | 0.0090434 | 0.0033977 | -0.0015972 | -0.00085453 | -60.8597 | 62.2055 | -61.116 | -0.036621 | -0.082397 | -0.10529 | 0.013733 | 0.068665 | 0.20599 | -0.3479 | -0.34332 | 0.09613 | -0.086975 | 60.7361 | -62.1918 | 60.4248 | -61.9034 | 0.25635
783.7344 | 123.111 | -60.7269 | 62.0773 | 0.089373 | 0.014608 | 0.0106 | -0.002065 | -0.00066112 | 0.0013936 | 0.00042727 | -60.8734 | 62.0911 | -61.0931 | 0.009155 | 0.050354 | 0.041199 | -0.073242 | 0.24719 | 0.19684 | -0.2655 | -0.36621 | 0.013732 | -0.14648 | 60.7361 | -62.027 | 60.4614 | -61.8805 | 0.21973
784.75 | 123.1155 | -60.7361 | 62.0911 | -0.10899 | 0.016103 | 0.014872 | 0.0009258 | 0.00040688 | -0.0011698 | 0.0012817 | -60.791 | 62.114 | -61.1023 | 0.11902 | 0.13275 | 0.14191 | 0.018311 | 0.35706 | 0.24261 | -0.20599 | -0.36621 | 0.022889 | -0.054932 | 60.8551 | -61.9583 | 60.5301 | -61.8484 | 0.31128
785.7344 | 123.1064 | -60.7269 | 62.0544 | 0.028338 | 0.016317 | 0.016795 | 0.0037028 | 0.0012615 | -0.0015972 | -0.00042733 | -60.7819 | 62.0819 | -61.0794 | 0.054932 | 0.050354 | 0.009155 | -0.17395 | 0.21973 | 0.16022 | -0.32959 | -0.35248 | 0.027466 | -0.054931 | 60.7819 | -62.0041 | 60.3973 | -61.8942 | 0.29755
786.7656 | 123.0835 | -60.7498 | 62.1277 | -0.11662 | 0.01888 | 0.018504 | 0.0084026 | -0.00066112 | -0.002238 | -0.00085453 | -60.7956 | 62.2147 | -61.0611 | 0.073242 | 0.045776 | 0.054932 | 0.082397 | 0.26093 | 0.25177 | -0.20599 | -0.31128 | 0.086975 | -0.045776 | 60.8231 | -62.0819 | 60.5438 | -61.8759 | 0.2655
787.7344 | 123.1064 | -60.7544 | 62.0682 | 0.16567 | 0.016958 | 0.015086 | 0.0017802 | -0.00044752 | -0.00031535 | 6.6667e-08 | -60.8734 | 62.0728 | -61.1069 | 0.022888 | 0.022888 | 0.036621 | -0.082397 | 0.22888 | 0.19226 | -0.27008 | -0.35248 | 0.004578 | -0.11902 | 60.7773 | -62.0453 | 60.4843 | -61.8759 | 0.23346
788.7656 | 123.0789 | -60.7636 | 62.114 | -0.11662 | 0.01653 | 0.016368 | 0.0077616 | 0.0012615 | -0.00031535 | -0.0019225 | -60.7773 | 62.1964 | -61.084 | 0.07782 | 0.064087 | 0.054932 | 0.059509 | 0.25177 | 0.25177 | -0.24719 | -0.32043 | 0.082397 | -0.013733 | 60.8414 | -62.0499 | 60.5164 | -61.8622 | 0.3067
789.7344 | 123.1155 | -60.7498 | 62.059 | 0.11989 | 0.017812 | 0.020854 | 0.001353 | 0.0029705 | -0.00031535 | -0.00042733 | -60.8047 | 62.0956 | -61.0977 | 0.032043 | 0.041199 | 0.009155 | -0.14648 | 0.20142 | 0.17853 | -0.3479 | -0.3479 | 0.036621 | -0.054932 | 60.7819 | -62.0178 | 60.4019 | -61.8805 | 0.29297
790.7656 | 123.056 | -60.7498 | 62.1002 | 0.028338 | 0.020376 | 0.018717 | 0.0088298 | 0.0025431 | -0.0015972 | -0.0017089 | -60.7636 | 62.1964 | -61.084 | 0.059509 | 0.022888 | 0.018311 | 0 | 0.22888 | 0.21515 | -0.29297 | -0.33417 | 0.09613 | -0.013733 | 60.8093 | -62.0773 | 60.4568 | -61.8851 | 0.32043
791.7344 | 123.0835 | -60.7361 | 62.0407 | 0.18093 | 0.016744 | 0.014872 | -0.002065 | 0.0021159 | -0.0011698 | 0.0025635 | -60.8322 | 62.0865 | -61.1206 | 0.022888 | 0.036621 | 0.022888 | -0.14191 | 0.21057 | 0.16479 | -0.31128 | -0.38452 | 0.045777 | -0.09613 | 60.759 | -62.0041 | 60.4248 | -61.8759 | 0.28839
792.7656 | 123.0377 | -60.7681 | 62.1277 | -0.17766 | 0.017812 | 0.014659 | 0.0049846 | 0.0016887 | -0.0020244 | 0.00042727 | -60.8368 | 62.146 | -61.1114 | 0.054932 | 0.022888 | 0.073242 | 0.15564 | 0.30212 | 0.2655 | -0.16937 | -0.34332 | 0.01831 | -0.068665 | 60.8231 | -62.1048 | 60.5988 | -61.8622 | 0.27466
793.7344 | 123.1384 | -60.7407 | 62.059 | 1.7068 | 0.019735 | 0.01594 | 0.0026346 | 0.0023295 | 0.0018208 | -0.0019225 | -60.6674 | 62.0682 | -61.0886 | 0.036621 | 0.091553 | 0.091553 | -0.20142 | 0.19684 | 0.16937 | -0.27008 | -0.3479 | 0.009155 | 0.073243 | 60.7773 | -61.9675 | 60.4706 | -61.8896 | 0.42114
794.7656 | 123.1064 | -60.7132 | 62.0911 | -0.33787 | 0.016958 | 0.018077 | 0.002421 | 0.00062048 | -0.00052895 | -0.0021361 | -60.791 | 62.1048 | -61.0748 | 0.10529 | 0.10986 | 0.13275 | 0.041199 | 0.3479 | 0.25177 | -0.21057 | -0.36163 | 0.013733 | -0.07782 | 60.8185 | -61.9812 | 60.5026 | -61.8393 | 0.28381
795.7344 | 123.1522 | -60.7224 | 62.0499 | 0.28011 | 0.018453 | 0.017222 | 0.0051982 | 0.0038249 | 0.00053925 | -0.00021353 | -60.7544 | 62.0956 | -61.0794 | 0.045776 | 0.032043 | 0.045776 | -0.19684 | 0.21515 | 0.16479 | -0.37079 | -0.35706 | 0.045776 | -0.032044 | 60.7681 | -62.0178 | 60.3516 | -61.8851 | 0.32501
796.7656 | 123.0194 | -60.7452 | 62.1185 | -0.15477 | 0.018667 | 0.011027 | 0.0032756 | -0.00023392 | -0.002238 | -0.0019225 | -60.8414 | 62.1597 | -61.0931 | 0.027466 | 0.022888 | 0.045776 | 0.14648 | 0.26093 | 0.27008 | -0.18768 | -0.3479 | 0.041199 | -0.096131 | 60.7727 | -62.0956 | 60.5576 | -61.8484 | 0.25177
797.7344 | 123.1293 | -60.7498 | 62.0499 | 0.25722 | 0.019521 | 0.016368 | 0.0069072 | 0.0021159 | -0.00095615 | -0.0023499 | -60.8047 | 62.1552 | -61.0977 | 0.018311 | 0 | -0.041199 | -0.12817 | 0.20599 | 0.17395 | -0.37537 | -0.3479 | 0.10528 | -0.054932 | 60.7681 | -62.0499 | 60.3745 | -61.8759 | 0.29297
798.75 | 123.1201 | -60.704 | 62.1048 | 0.051226 | 0.015249 | 0.015299 | -0.0027058 | -0.0019429 | -0.002238 | -0.0021361 | -60.8414 | 62.0865 | -61.0977 | 0.068665 | 0.07782 | 0.10071 | -0.068665 | 0.29755 | 0.21057 | -0.24261 | -0.39368 | -0.01831 | -0.13733 | 60.7727 | -62.027 | 60.4614 | -61.8942 | 0.25635
799.7344 | 123.0148 | -60.7544 | 62.1002 | 0.2267 | 0.021657 | 0.019999 | 0.0088298 | 0.0021159 | 0.00053925 | -0.0029907 | -60.8597 | 62.1826 | -61.1069 | -0.041199 | -0.068665 | -0.09613 | -0.009155 | 0.11902 | 0.21057 | -0.33875 | -0.35248 | 0.082397 | -0.10528 | 60.7132 | -62.1689 | 60.4156 | -61.8896 | 0.24719
800.7656 | 123.0194 | -60.7407 | 62.1185 | -0.18529 | 0.016744 | 0.018077 | 0.0028484 | 0.0023295 | 0.00053925 | -0.00085453 | -60.8459 | 62.1826 | -61.1114 | 0.013733 | 0.036621 | 0.050354 | 0.15564 | 0.26093 | 0.28839 | -0.16937 | -0.37079 | 0.064087 | -0.10529 | 60.7544 | -62.0819 | 60.5713 | -61.8301 | 0.2655
801.7344 | 123.0698 | -60.759 | 62.0544 | 0.27248 | 0.019948 | 0.014231 | 0.0077616 | 0.0046793 | -0.00074255 | -0.00085453 | -60.8276 | 62.1689 | -61.0931 | -0.027466 | -0.036621 | -0.068665 | -0.068665 | 0.10986 | 0.18768 | -0.3479 | -0.33417 | 0.11444 | -0.068665 | 60.7315 | -62.0911 | 60.4111 | -61.8668 | 0.2655
802.7656 | 123.111 | -60.7132 | 62.059 | 0.035967 | 0.016744 | 0.014659 | 0.0004984 | -2.0324e-05 | -0.00031535 | 0.0032043 | -60.8551 | 62.1002 | -61.116 | -0.041199 | 0.022888 | 0.032043 | -0.073242 | 0.26093 | 0.21057 | -0.27924 | -0.40283 | 0.041199 | -0.14191 | 60.672 | -62.0361 | 60.434 | -61.8484 | 0.26093
803.7344 | 123.0331 | -60.7727 | 62.1094 | 0.24196 | 0.019094 | 0.018504 | 0.009257 | 0.0031841 | 0.00011185 | -0.0014953 | -60.8231 | 62.1964 | -61.1069 | -0.059509 | -0.21057 | -0.72327 | -0.045776 | 0.66376 | 0.17853 | -0.37994 | -0.33417 | 0.086975 | -0.050354 | 60.7132 | -62.3199 | 60.3928 | -61.9308 | 0.28381
804.7656 | 123.1201 | -60.7086 | 62.114 | 0.15041 | 0.018239 | 0.014445 | -0.0009968 | 0.00062048 | -0.0013834 | -0.00085453 | -60.791 | 62.1185 | -61.0794 | 0.09613 | 0.10529 | 0.15564 | 0.009155 | 0.36163 | 0.24719 | -0.21515 | -0.37079 | 0.004577 | -0.082398 | 60.8047 | -62.0087 | 60.4935 | -61.8668 | 0.28839
805.7344 | 122.9919 | -60.7864 | 62.1094 | 0.1733 | 0.017812 | 0.018504 | 0.0084026 | 0.0033977 | -0.0018108 | -0.00042733 | -60.8368 | 62.2055 | -61.1069 | -0.073242 | -0.091553 | -0.10986 | 0 | 0.091553 | 0.20142 | -0.35706 | -0.32044 | 0.09613 | -0.050354 | 60.7132 | -62.2009 | 60.4294 | -61.908 | 0.27008
806.7656 | 123.1659 | -60.6949 | 62.0636 | -0.047956 | 0.016103 | 0.017436 | -0.0029196 | 0.0010477 | -0.0020244 | 0.0014953 | -60.7956 | 62.0956 | -61.1069 | 0.10529 | 0.13275 | 0.16022 | -0.064087 | 0.35706 | 0.20599 | -0.18768 | -0.41199 | 0.032043 | -0.10071 | 60.8002 | -61.9308 | 60.5072 | -61.8576 | 0.31128
807.7344 | 123.0103 | -60.7727 | 62.1094 | 0.21907 | 0.022298 | 0.019358 | 0.0079752 | 0.0048931 | -0.00095615 | -0.0012817 | -60.8414 | 62.2055 | -61.0748 | -0.050354 | -0.073242 | -0.10071 | -0.004578 | 0.11444 | 0.20142 | -0.3479 | -0.30212 | 0.09613 | -0.068665 | 60.7224 | -62.1826 | 60.4248 | -61.908 | 0.23346
808.7656 | 123.143 | -60.7361 | 62.0911 | -0.0021797 | 0.013967 | 0.01295 | -0.0016378 | 0.00083408 | 0.00075285 | -0.00021353 | -60.8231 | 62.0865 | -61.0977 | 0.064087 | 0.086975 | 0.11902 | -0.045776 | 0.31128 | 0.21515 | -0.23804 | -0.36163 | -0.004577 | -0.086975 | 60.8002 | -62.0041 | 60.498 | -61.8759 | 0.27466
809.7344 | 123.0103 | -60.7727 | 62.1185 | 0.14278 | 0.019094 | 0.018077 | 0.0096842 | 0.0023295 | -0.0020244 | -0.0017089 | -60.7956 | 62.1918 | -61.0703 | -0.036621 | -0.050354 | -0.073242 | 0.022888 | 0.10071 | 0.21515 | -0.33417 | -0.29755 | 0.073242 | -0.022888 | 60.7361 | -62.1689 | 60.4385 | -61.9034 | 0.27466
810.7656 | 123.1522 | -60.7132 | 62.0728 | -0.14714 | 0.018026 | 0.015727 | -0.0022786 | 0.0010477 | -0.00010175 | -0.00042733 | -60.7773 | 62.0956 | -61.0703 | 0.11444 | 0.12817 | 0.16479 | -0.041199 | 0.36163 | 0.2243 | -0.1831 | -0.35705 | 0.022888 | -0.064087 | 60.8276 | -61.9446 | 60.5301 | -61.8485 | 0.29297
811.7344 | 123.0515 | -60.7681 | 62.114 | 0.089373 | 0.019094 | 0.015513 | 0.010325 | 0.0021159 | 0.00053925 | -0.0017089 | -60.7636 | 62.2238 | -61.0886 | 0.018311 | -0.022888 | -0.027466 | 0.013733 | 0.16479 | 0.21515 | -0.31128 | -0.32044 | 0.10986 | 0.004577 | 60.7864 | -62.1368 | 60.4568 | -61.8988 | 0.32501
812.75 | 123.111 | -60.7178 | 62.0728 | 0.69972 | 0.016744 | 0.014872 | 0.0009258 | 0.0040385 | 0.00011185 | -0.0010681 | -60.6674 | 62.0773 | -61.0886 | 0.082397 | 0.086975 | 0.022888 | -0.19684 | 0.21973 | 0.18768 | -0.29297 | -0.37079 | 0.004578 | 0.050354 | 60.8002 | -61.9858 | 60.4248 | -61.8851 | 0.42114
813.7344 | 123.0377 | -60.7498 | 62.1231 | -0.0098092 | 0.019735 | 0.019572 | 0.0073344 | 0.0036113 | -0.00074255 | -0.00064093 | -60.6628 | 62.2284 | -61.0931 | 0.050354 | 0.013733 | 0 | 0.027466 | 0.2243 | 0.23346 | -0.27008 | -0.34332 | 0.10529 | 0.086975 | 60.8002 | -62.1094 | 60.4797 | -61.8896 | 0.4303
814.7656 | 123.1567 | -60.7086 | 62.0865 | -0.040327 | 0.016103 | 0.013377 | -0.0050558 | 0.0021159 | 0.00096645 | -0.00064093 | -60.7956 | 62.0773 | -61.084 | 0.10071 | 0.1236 | 0.15564 | -0.054932 | 0.37537 | 0.20142 | -0.17395 | -0.37537 | -0.009155 | -0.086975 | 60.8093 | -61.9629 | 60.5347 | -61.8851 | 0.28839
815.7344 | 123.0469 | -60.7498 | 62.1277 | 0.058855 | 0.018239 | 0.021495 | 0.0079752 | 0.0038249 | -0.0026652 | -0.0014953 | -60.7727 | 62.2055 | -61.0794 | 0.032043 | 0.004578 | 0.022888 | 0.032043 | 0.21057 | 0.24719 | -0.2655 | -0.32959 | 0.077819 | -0.022888 | 60.7819 | -62.1231 | 60.4843 | -61.8805 | 0.3067
816.7656 | 123.111 | -60.7132 | 62.0682 | 0.21144 | 0.017598 | 0.014018 | -0.0005696 | 0.0046793 | -0.0011698 | 0.00021367 | -60.8047 | 62.0911 | -61.0886 | 0.022888 | 0.045776 | 0.041199 | -0.17853 | 0.21515 | 0.16937 | -0.34332 | -0.37537 | 0.022888 | -0.091553 | 60.7361 | -62.0224 | 60.3699 | -61.8988 | 0.28381
817.7344 | 123.0652 | -60.7224 | 62.0956 | -0.032697 | 0.019948 | 0.019145 | 0.0049846 | 0.0021159 | -0.00074255 | -0.00021353 | -60.759 | 62.1964 | -61.0886 | 0.050354 | 0.036621 | 0.022888 | 0.018311 | 0.22888 | 0.2243 | -0.26093 | -0.36621 | 0.10071 | -0.036621 | 60.7727 | -62.059 | 60.4614 | -61.8713 | 0.32959
818.7656 | 123.0698 | -60.7636 | 62.1094 | 0.0054493 | 0.019521 | 0.016795 | 0.0049846 | 0.0038249 | -0.0018108 | 0.00021367 | -60.7498 | 62.1964 | -61.0931 | 0.059509 | 0.041199 | 0.027466 | -0.009155 | 0.21973 | 0.23804 | -0.29755 | -0.32959 | 0.086975 | 0.013733 | 60.8231 | -62.0682 | 60.466 | -61.8713 | 0.34332
819.7344 | 123.0606 | -60.759 | 62.0865 | -0.10136 | 0.018453 | 0.021281 | 0.0088298 | 0.0057475 | -0.0013834 | -0.00042733 | -60.7544 | 62.2192 | -61.0611 | 0.041199 | 0.050354 | 0.050354 | 0.036621 | 0.24261 | 0.25177 | -0.25635 | -0.30212 | 0.13275 | 0.004577 | 60.8002 | -62.0361 | 60.5026 | -61.8347 | 0.3067
820.75 | 123.1293 | -60.7498 | 62.0911 | 0.24959 | 0.016103 | 0.016581 | -0.0029196 | 0.0038249 | 0.00096645 | 0.00085447 | -60.8231 | 62.114 | -61.0748 | 0.004578 | 0.027466 | 0.018311 | -0.11902 | 0.20142 | 0.17853 | -0.29755 | -0.32501 | 0.022889 | -0.073242 | 60.7544 | -62.0636 | 60.4523 | -61.9125 | 0.25177
821.7344 | 123.0515 | -60.7498 | 62.0911 | 0.028338 | 0.021016 | 0.018931 | 0.0073344 | 0.0046793 | -0.0011698 | 6.6667e-08 | -60.7727 | 62.2421 | -61.1069 | 0.050354 | 0.022888 | 0.027466 | 0.036621 | 0.21973 | 0.24261 | -0.27466 | -0.35706 | 0.15106 | -0.022888 | 60.8002 | -62.0682 | 60.4752 | -61.8484 | 0.33417
822.7656 | 123.1384 | -60.7086 | 62.1002 | -0.086103 | 0.01653 | 0.013163 | -0.0022786 | 0.0027567 | -0.00074255 | -0.00064093 | -60.791 | 62.1048 | -61.0703 | 0.091553 | 0.10071 | 0.15106 | -0.004578 | 0.35706 | 0.23346 | -0.21057 | -0.36163 | 0.004577 | -0.082398 | 60.8002 | -61.9995 | 60.498 | -61.8668 | 0.27923
823.7344 | 123.1338 | -60.7452 | 62.0682 | 0.303 | 0.020376 | 0.01594 | 0.0056254 | 0.0042521 | 0.00011185 | 0.00042727 | -60.7864 | 62.1506 | -61.0886 | -0.018311 | -0.004578 | -0.022888 | -0.12817 | 0.17853 | 0.17395 | -0.35248 | -0.34332 | 0.082398 | -0.041199 | 60.7269 | -62.0728 | 60.3928 | -61.8942 | 0.30212
824.7656 | 123.1064 | -60.7086 | 62.059 | 0.18855 | 0.015462 | 0.014231 | 0.0002848 | 0.00062048 | -0.00052895 | 0.00042727 | -60.7864 | 62.0911 | -61.0748 | 0.018311 | 0.032043 | 0.032043 | -0.16937 | 0.22888 | 0.17853 | -0.35248 | -0.36621 | 0.032043 | -0.07782 | 60.7269 | -62.027 | 60.3561 | -61.8805 | 0.28839
825.7344 | 123.1018 | -60.7498 | 62.1231 | -0.13188 | 0.019307 | 0.01594 | 0.0045574 | 0.0025431 | 0.0013936 | -0.0012817 | -60.7727 | 62.2101 | -61.0886 | 0.045776 | 0.045776 | 0.050354 | 0.059509 | 0.26093 | 0.25177 | -0.22888 | -0.33875 | 0.086975 | -0.022888 | 60.7956 | -62.0773 | 60.5209 | -61.8713 | 0.31586
826.7656 | 123.1064 | -60.7132 | 62.0499 | 0.24959 | 0.01888 | 0.019572 | -0.0005696 | 0.0012615 | -0.00031535 | 0.0017091 | -60.7864 | 62.0865 | -61.0931 | 0.009155 | 0.009155 | 0.022888 | -0.14648 | 0.21515 | 0.16937 | -0.33417 | -0.37994 | 0.036621 | -0.073242 | 60.7224 | -62.0407 | 60.379 | -61.8805 | 0.3067
827.7344 | 123.0789 | -60.7224 | 62.1368 | -0.047956 | 0.020162 | 0.015299 | 0.005839 | 0.0031841 | -0.002238 | -0.00085453 | -60.8047 | 62.2513 | -61.0794 | 0.027466 | 0.013733 | 0.027466 | 0.09613 | 0.23804 | 0.27466 | -0.21973 | -0.35706 | 0.11444 | -0.082398 | 60.7498 | -62.1231 | 60.5026 | -61.8622 | 0.27466
828.7656 | 123.1201 | -60.7132 | 62.0819 | 0.020708 | 0.016103 | 0.013804 | -0.0031332 | 0.0021159 | -0.0015972 | 0.0010681 | -60.8231 | 62.1185 | -61.0519 | 0.068665 | 0.07782 | 0.10071 | -0.054932 | 0.29755 | 0.20599 | -0.26093 | -0.33874 | 0.036621 | -0.10986 | 60.7819 | -62.0041 | 60.4523 | -61.8759 | 0.22888
829.7344 | 123.1018 | -60.7452 | 62.1323 | -0.18529 | 0.02123 | 0.016581 | 0.0054118 | 0.0029705 | -0.0033062 | -0.0010681 | -60.7681 | 62.2055 | -61.0565 | 0.073242 | 0.027466 | 0.054932 | 0.073242 | 0.24261 | 0.25635 | -0.25635 | -0.31128 | 0.073242 | -0.022888 | 60.8185 | -62.1048 | 60.4889 | -61.8759 | 0.28839
830.75 | 122.9965 | -60.7636 | 62.1048 | 0.18093 | 0.020803 | 0.016368 | 0.00648 | 0.0042521 | -0.0020244 | -0.00085453 | -60.8093 | 62.1964 | -61.1298 | -0.064087 | -0.07782 | -0.10986 | -0.018311 | 0.091553 | 0.2243 | -0.36163 | -0.36621 | 0.091553 | -0.045776 | 60.6995 | -62.1826 | 60.4019 | -61.8805 | 0.32044
831.7344 | 123.0652 | -60.7361 | 62.1323 | -0.11662 | 0.020162 | 0.016581 | 0.0039164 | 0.0023295 | -0.00095615 | -0.00021353 | -60.8139 | 62.2101 | -61.116 | 0.032043 | 0.036621 | 0.041199 | 0.11444 | 0.24261 | 0.26093 | -0.20599 | -0.37994 | 0.07782 | -0.07782 | 60.7681 | -62.0956 | 60.5301 | -61.8713 | 0.30212
832.7656 | 123.1155 | -60.7452 | 62.0773 | 0.26485 | 0.022298 | 0.018931 | 0.0028484 | 0.0033977 | 0.00118 | 6.6667e-08 | -60.7956 | 62.1872 | -61.0748 | 0 | -0.004578 | -0.009155 | -0.14648 | 0.16022 | 0.15564 | -0.37537 | -0.32959 | 0.10986 | -0.050354 | 60.7452 | -62.0819 | 60.3699 | -61.9217 | 0.27924
833.7344 | 123.056 | -60.7178 | 62.0956 | 0.013079 | 0.019521 | 0.021495 | 0.0077616 | 0.0055339 | -0.00095615 | -0.00042733 | -60.759 | 62.2467 | -61.116 | 0.018311 | -0.009155 | -0.018311 | 0.004578 | 0.15106 | 0.21515 | -0.28381 | -0.39825 | 0.15106 | -0.041199 | 60.7361 | -62.1048 | 60.434 | -61.8805 | 0.35706
834.7656 | 123.1064 | -60.7224 | 62.0865 | 0.12752 | 0.017385 | 0.01829 | -0.0033468 | 0.0010477 | 0.00011185 | -0.0010681 | -60.8231 | 62.1368 | -61.1023 | -0.004578 | 0.036621 | 0.041199 | -0.068665 | 0.22888 | 0.1831 | -0.29297 | -0.37994 | 0.050354 | -0.10071 | 60.7178 | -62.0499 | 60.4294 | -61.9034 | 0.27924
835.7344 | 123.0515 | -60.7544 | 62.1277 | -0.13188 | 0.017385 | 0.018931 | 0.0039164 | 0.0010477 | -0.0018108 | -0.00021353 | -60.7819 | 62.2284 | -61.084 | 0.041199 | 0.022888 | 0.054932 | 0.12817 | 0.25177 | 0.25177 | -0.20142 | -0.32959 | 0.10071 | -0.027465 | 60.7956 | -62.1048 | 60.553 | -61.8759 | 0.30212
836.7656 | 123.111 | -60.7224 | 62.0361 | 0.2267 | 0.018026 | 0.016581 | -0.000356 | 0.0016887 | 0.00011185 | 0.00085447 | -60.7636 | 62.114 | -61.0886 | 0.032043 | 0.027466 | 0.027466 | -0.17853 | 0.2243 | 0.16479 | -0.33417 | -0.36621 | 0.07782 | -0.041199 | 60.7544 | -62.0087 | 60.3882 | -61.8713 | 0.32501
837.7344 | 123.0331 | -60.7178 | 62.146 | -0.20817 | 0.019094 | 0.019572 | 0.0037028 | 0.00083408 | -0.00052895 | -0.0010681 | -60.8139 | 62.2147 | -61.0886 | 0.036621 | 0.022888 | 0.018311 | 0.1236 | 0.23346 | 0.24719 | -0.20599 | -0.37079 | 0.068665 | -0.096131 | 60.7544 | -62.1231 | 60.5118 | -61.8988 | 0.27466
838.7656 | 123.143 | -60.7132 | 62.1231 | 0.051226 | 0.015889 | 0.014445 | -0.0001424 | 0.0014751 | 0.00053925 | -0.0012817 | -60.8322 | 62.0911 | -61.0931 | 0.009155 | 0.036621 | 0.036621 | -0.073242 | 0.2243 | 0.21515 | -0.27466 | -0.37994 | -0.032044 | -0.11902 | 60.7224 | -62.0865 | 60.4385 | -61.908 | 0.26093
839.7344 | 123.0652 | -60.7315 | 62.1323 | -0.11662 | 0.019521 | 0.011454 | 0.007548 | 0.00040688 | -0.0013834 | -0.0021361 | -60.7407 | 62.2238 | -61.0474 | 0.045776 | 0.045776 | 0.054932 | 0.086975 | 0.26093 | 0.27008 | -0.21057 | -0.31586 | 0.091553 | -0.009156 | 60.7773 | -62.0865 | 60.5209 | -61.8622 | 0.3067
840.7656 | 123.143 | -60.7132 | 62.0865 | 0.28011 | 0.019948 | 0.01359 | -0.0009968 | 0.0038249 | 0.00096645 | -0.00064093 | -60.6812 | 62.114 | -61.0794 | 0.09613 | 0.11902 | -0.004578 | -0.1831 | 0.28839 | 0.17395 | -0.30212 | -0.36621 | 0.027466 | 0.032044 | 60.8093 | -61.9675 | 60.4111 | -61.9125 | 0.39826
841.7344 | 123.0286 | -60.7315 | 62.114 | -0.20817 | 0.017812 | 0.017222 | 0.0034892 | 0.0014751 | -0.00095615 | -0.0017089 | -60.8185 | 62.2284 | -61.0931 | 0.064087 | 0.29755 | 0.33417 | -0.27924 | 0.009155 | 0.3067 | -0.12817 | -0.36163 | 0.11444 | -0.086975 | 60.7956 | -61.8164 | 60.6033 | -61.8073 | 0.27466
842.7656 | 123.1018 | -60.7132 | 62.1048 | 0.18855 | 0.015889 | 0.017008 | -0.0007832 | 0.0012615 | -0.0013834 | 0.0010681 | -60.8185 | 62.114 | -61.0794 | -0.009155 | 0 | -0.009155 | -0.10071 | 0.21973 | 0.16937 | -0.28839 | -0.36621 | 0.009156 | -0.10528 | 60.704 | -62.1048 | 60.4248 | -61.9354 | 0.26093
843.7344 | 123.0469 | -60.7178 | 62.1231 | 0.051226 | 0.019094 | 0.011881 | 0.0045574 | -0.00044752 | -0.00052895 | -0.0027771 | -60.7773 | 62.2284 | -61.0886 | 0.041199 | 0.022888 | 0.009155 | 0.12817 | 0.25177 | 0.27466 | -0.23346 | -0.37079 | 0.10529 | -0.05951 | 60.759 | -62.1002 | 60.4843 | -61.8484 | 0.31128
844.7656 | 123.0743 | -60.7178 | 62.1002 | 0.15041 | 0.015889 | 0.01359 | -0.0001424 | 0.00019328 | -0.00010175 | -0.0021361 | -60.8185 | 62.0956 | -61.0794 | 0.018311 | 0.036621 | 0.027466 | -0.073242 | 0.23804 | 0.19226 | -0.27008 | -0.36163 | -0.004578 | -0.10071 | 60.7361 | -62.0636 | 60.4477 | -61.908 | 0.26093
845.7344 | 123.0469 | -60.7315 | 62.1506 | -0.17766 | 0.019307 | 0.015727 | 0.0069072 | 0.00040688 | -0.00031535 | 0.0021363 | -60.8093 | 62.2101 | -61.0703 | 0.018311 | 0.064087 | 0.45319 | 0.17395 | -0.17395 | 0.28839 | -0.13733 | -0.33874 | 0.059509 | -0.07782 | 60.7498 | -62.0865 | 60.5942 | -61.8622 | 0.26093
846.7656 | 123.1476 | -60.7132 | 62.0682 | 0.23433 | 0.01888 | 0.020854 | 0.0037028 | 0.0029705 | -0.00074255 | -0.0012817 | -60.7178 | 62.1277 | -61.0703 | 0.054932 | 0.045776 | 0.027466 | -0.21973 | 0.21057 | 0.16022 | -0.37537 | -0.35705 | 0.05951 | -0.004577 | 60.7681 | -62.0224 | 60.3378 | -61.908 | 0.35248
847.7344 | 123.024 | -60.7315 | 62.1643 | -0.19291 | 0.018667 | 0.015299 | 0.002421 | -0.00044752 | 0.00053925 | 0.00064087 | -60.8139 | 62.233 | -61.0703 | 0.036621 | 0.022888 | 0.022888 | 0.13275 | 0.25177 | 0.27466 | -0.18768 | -0.33874 | 0.068664 | -0.082398 | 60.7681 | -62.1414 | 60.5438 | -61.8896 | 0.25635
848.7656 | 123.1064 | -60.7132 | 62.0865 | 0.21144 | 0.017598 | 0.012309 | 0.0002848 | 0.0031841 | -0.00074255 | -0.0017089 | -60.7819 | 62.114 | -61.0703 | 0.018311 | 0.018311 | 0.018311 | -0.14191 | 0.20599 | 0.16937 | -0.3479 | -0.35705 | 0.027466 | -0.068664 | 60.7315 | -62.0682 | 60.3653 | -61.9171 | 0.28839
849.7344 | 123.0286 | -60.7407 | 62.1368 | -0.17766 | 0.017598 | 0.016368 | 0.0043436 | 0.0010477 | -0.0015972 | -0.0012817 | -60.8185 | 62.2147 | -61.0886 | 0.027466 | 0.10986 | 0.45319 | 0.086975 | -0.17853 | 0.29297 | -0.13733 | -0.3479 | 0.07782 | -0.077819 | 60.7681 | -62.027 | 60.6033 | -61.8439 | 0.27008
850.7656 | 123.1201 | -60.704 | 62.0819 | 0.23433 | 0.017171 | 0.016368 | 0.0026346 | 0.0014751 | 0.0016072 | -0.00042733 | -60.7407 | 62.1094 | -61.0703 | 0.054932 | 0.059509 | 0.050354 | -0.17853 | 0.21515 | 0.16479 | -0.32501 | -0.36621 | 0.027466 | -0.036621 | 60.759 | -62.0224 | 60.379 | -61.9171 | 0.32959
851.7344 | 123.024 | -60.7498 | 62.1597 | -0.20817 | 0.017385 | 0.016154 | 0.0019938 | -0.00023392 | -0.0013834 | 0.0010681 | -60.8093 | 62.178 | -61.0748 | 0.032043 | 0.027466 | 0.032043 | 0.14191 | 0.24261 | 0.27466 | -0.17395 | -0.32501 | 0.018311 | -0.059509 | 60.7819 | -62.1323 | 60.5759 | -61.8851 | 0.2655
852.7656 | 123.1018 | -60.7361 | 62.1002 | 0.21144 | 0.017171 | 0.01829 | 7.12e-05 | 0.00083408 | -0.00095615 | -0.0019225 | -60.8002 | 62.0819 | -61.0519 | 0.013733 | 0.032043 | 0.009155 | -0.14648 | 0.19226 | 0.16937 | -0.3067 | -0.31586 | -0.018311 | -0.064087 | 60.7498 | -62.0682 | 60.4294 | -61.9308 | 0.25177
853.7344 | 123.024 | -60.7269 | 62.1597 | -0.15477 | 0.017598 | 0.015299 | 0.0071208 | -0.0010885 | -0.0024516 | 0.00085447 | -60.8002 | 62.2147 | -61.0703 | -0.26093 | -0.13733 | 0.13275 | 0.11902 | 0.11444 | 0.27466 | -0.1831 | -0.34332 | 0.054932 | -0.073242 | 60.466 | -62.2971 | 60.5438 | -61.8851 | 0.27008
854.7656 | 123.1247 | -60.704 | 62.114 | 0.19618 | 0.017385 | 0.015086 | 0.0015666 | 0.00040688 | -0.00010175 | -0.00021353 | -60.7452 | 62.114 | -61.0703 | 0.022888 | 0.036621 | 0.027466 | -0.17853 | 0.2243 | 0.17853 | -0.32959 | -0.36621 | 0 | -0.041198 | 60.7269 | -62.0773 | 60.3745 | -61.9354 | 0.32501
855.7344 | 123.0515 | -60.7178 | 62.1323 | -0.17003 | 0.016317 | 0.014659 | 0.0011394 | -0.0013021 | -0.00031535 | -0.0017089 | -60.759 | 62.2009 | -61.0565 | 0.068665 | 0.064087 | 0.10071 | 0.086975 | 0.27466 | 0.27008 | -0.19684 | -0.33875 | 0.068665 | -0.041199 | 60.7864 | -62.0682 | 60.5209 | -61.8622 | 0.29755
856.7656 | 123.0377 | -60.7224 | 62.1323 | 0.26485 | 0.023153 | 0.016154 | 0.0084026 | 0.0023295 | -0.002238 | -0.0014953 | -60.9833 | 62.1918 | -61.1023 | -0.064087 | -0.082397 | -0.013733 | -0.022888 | 0.064087 | 0.21057 | -0.32044 | -0.37994 | 0.059509 | -0.26092 | 60.6583 | -62.2147 | 60.4019 | -61.9217 | 0.11902
857.7344 | 123.0377 | -60.7361 | 62.1826 | -0.24632 | 0.01653 | 0.013377 | 0.0037028 | 0.00062048 | -0.00052895 | -0.0023499 | -60.8093 | 62.2055 | -61.1069 | 0.032043 | 0.032043 | 0.045776 | 0.14648 | 0.25177 | 0.28839 | -0.17395 | -0.37079 | 0.022888 | -0.073242 | 60.7681 | -62.1506 | 60.5621 | -61.8942 | 0.29755
858.7656 | 123.0927 | -60.6857 | 62.1002 | 0.24959 | 0.015035 | 0.017863 | 0.001353 | 0.0012615 | 0.0024618 | -0.00085453 | -60.7773 | 62.1185 | -61.0794 | 0.032043 | 0.032043 | 0.013733 | -0.16479 | 0.19226 | 0.16479 | -0.34332 | -0.39368 | 0.01831 | -0.091553 | 60.7178 | -62.0682 | 60.3424 | -61.9354 | 0.30212
859.7344 | 123.0194 | -60.7178 | 62.1368 | -0.19291 | 0.017385 | 0.011881 | 0.0054118 | -0.00023392 | -0.0020244 | -0.00042733 | -60.791 | 62.2055 | -61.0657 | 0.013733 | -0.018311 | 0.041199 | 0.15106 | 0.2655 | 0.27924 | -0.17853 | -0.3479 | 0.068664 | -0.073243 | 60.7315 | -62.1552 | 60.5392 | -61.8576 | 0.27466
860.7656 | 123.0423 | -60.7315 | 62.178 | -0.17003 | 0.018239 | 0.018504 | 0.0028484 | -0.00023392 | 0.00011185 | 0.0017091 | -60.7956 | 62.2421 | -61.0748 | 0.022888 | 0.027466 | 0.041199 | 0.14191 | 0.23346 | 0.27008 | -0.17395 | -0.34332 | 0.064086 | -0.064087 | 60.7544 | -62.1506 | 60.5576 | -61.908 | 0.27924
861.7344 | 123.0606 | -60.7132 | 62.1643 | -0.22343 | 0.017385 | 0.019786 | 0.0039164 | 0.0016887 | -0.0030924 | -0.00042733 | -60.7498 | 62.1414 | -61.0474 | 0.073242 | 0.068665 | 0.082397 | 0.086975 | 0.29755 | 0.2655 | -0.20599 | -0.33417 | -0.022889 | -0.036621 | 60.7864 | -62.0956 | 60.5072 | -61.8988 | 0.29755
862.7656 | 123.0377 | -60.7269 | 62.1094 | 0.21907 | 0.019735 | 0.019145 | 0.0090434 | 0.0012615 | 0.00075285 | -0.0021361 | -60.7727 | 62.2284 | -61.0611 | -0.28839 | 0.11902 | 0.45319 | -0.013733 | 0.036621 | 0.18768 | -0.35248 | -0.33417 | 0.11902 | -0.045776 | 60.4385 | -61.9904 | 60.3745 | -61.9217 | 0.28839
863.7344 | 123.024 | -60.7132 | 62.1643 | -0.086103 | 0.018453 | 0.015513 | 0.0015666 | 0.0014751 | -0.00095615 | -0.00021353 | -60.7819 | 62.2192 | -61.0428 | 0.009155 | 0.009155 | 0.064087 | 0.12817 | 0.25635 | 0.2655 | -0.19226 | -0.32959 | 0.054931 | -0.068664 | 60.7224 | -62.1552 | 60.5209 | -61.8988 | 0.26093
864.7656 | 123.056 | -60.7224 | 62.1048 | -0.055586 | 0.019094 | 0.015299 | 0.00648 | 0.0048931 | 0.00096645 | 0.0012817 | -60.7956 | 62.2513 | -61.0657 | -0.036621 | -0.054932 | -0.073242 | -0.073242 | 0.082397 | 0.20142 | -0.33875 | -0.34332 | 0.14649 | -0.073242 | 60.6857 | -62.1597 | 60.3836 | -61.9034 | 0.27008
865.7344 | 123.0606 | -60.6995 | 62.1689 | -0.23106 | 0.017385 | 0.019786 | 0.000712 | 0.0012615 | -0.00052895 | -0.00042733 | -60.7636 | 62.2055 | -61.0382 | 0.045776 | 0.07782 | 0.091553 | 0.10071 | 0.29755 | 0.2655 | -0.18768 | -0.33874 | 0.036621 | -0.064087 | 60.7452 | -62.0911 | 60.5118 | -61.9034 | 0.27466
866.7656 | 122.9919 | -60.759 | 62.146 | 0.20381 | 0.020162 | 0.019999 | 0.0086162 | 0.0042521 | 0.00096645 | 0.00064087 | -60.7636 | 62.2513 | -61.0703 | -0.059509 | -0.073242 | -0.10529 | 0.009155 | 0.073242 | 0.19684 | -0.34332 | -0.31128 | 0.10529 | -0.004578 | 60.6995 | -62.2192 | 60.4156 | -61.9492 | 0.3067
867.7344 | 123.0148 | -60.7224 | 62.1735 | -0.23106 | 0.017598 | 0.017008 | 0.0017802 | 0.00040688 | -0.0013834 | -0.00064093 | -60.7956 | 62.2055 | -61.0657 | 0.004578 | 0.032043 | 0.036621 | 0.13733 | 0.26093 | 0.28839 | -0.17853 | -0.34332 | 0.032043 | -0.073242 | 60.7269 | -62.1414 | 60.5438 | -61.8851 | 0.27008
868.7656 | 123.0789 | -60.6903 | 62.1231 | 0.21144 | 0.015249 | 0.015727 | 0.0011394 | 0.0021159 | 0.00096645 | 0.00021367 | -60.7452 | 62.1277 | -61.0611 | 0.022888 | 0.050354 | 0.036621 | -0.16022 | 0.21973 | 0.16479 | -0.35248 | -0.37079 | 0.004578 | -0.054931 | 60.7132 | -62.0728 | 60.3378 | -61.9583 | 0.31586
869.7344 | 123.0698 | -60.6857 | 62.178 | -0.20817 | 0.017598 | 0.016795 | -0.0001424 | -0.0023701 | 0.00053925 | -0.00085453 | -60.7498 | 62.1964 | -61.0291 | 0.050354 | 0.068665 | 0.091553 | 0.10071 | 0.31128 | 0.27466 | -0.19226 | -0.34332 | 0.01831 | -0.064087 | 60.7361 | -62.1094 | 60.4935 | -61.9034 | 0.27924
870.7656 | 122.9874 | -60.7132 | 62.1368 | 0.11989 | 0.019307 | 0.018931 | 0.007548 | 0.0029705 | 0.00032545 | 0.00021367 | -60.7727 | 62.2375 | -61.0611 | -0.045776 | -0.073242 | -0.10071 | -0.004578 | 0.073242 | 0.20599 | -0.36163 | -0.3479 | 0.10071 | -0.059509 | 60.6674 | -62.2101 | 60.3516 | -61.9308 | 0.28839
871.7344 | 123.1064 | -60.6903 | 62.1552 | -0.11662 | 0.016958 | 0.017008 | 0.0011394 | 0.0019023 | 0.00075285 | -0.0014953 | -60.7132 | 62.178 | -61.0474 | 0.09613 | 0.09613 | 0.13733 | 0.032043 | 0.34332 | 0.25635 | -0.21515 | -0.35705 | 0.022889 | -0.022888 | 60.7864 | -62.059 | 60.4752 | -61.8988 | 0.33417
872.7656 | 123.0286 | -60.7086 | 62.1689 | 0.051226 | 0.019521 | 0.021281 | 0.009257 | 0.0053203 | -0.00074255 | -0.0017089 | -60.7269 | 62.2696 | -61.0519 | -0.027466 | -0.050354 | -0.054932 | 0.022888 | 0.12817 | 0.21973 | -0.3067 | -0.34332 | 0.10071 | -0.018311 | 60.6812 | -62.2192 | 60.4019 | -61.9492 | 0.32501
873.7344 | 123.1338 | -60.672 | 62.146 | 1.3101 | 0.015249 | 0.015727 | -0.0027058 | 0.0021159 | -0.0033062 | -0.0019225 | -60.8002 | 62.1506 | -61.0611 | 0.059509 | 0.13733 | 0.19684 | -0.027466 | 0.35706 | 0.2243 | -0.21057 | -0.3891 | 0.004578 | -0.12817 | 60.7315 | -62.0087 | 60.4614 | -61.9217 | 0.26093
874.7656 | 123.0286 | -60.7224 | 62.1506 | 0.24196 | 0.019948 | 0.018717 | 0.0066936 | 0.0025431 | 0.002248 | -0.00085453 | -60.7681 | 62.2467 | -61.0703 | -0.009155 | 0.35706 | 0.24261 | -0.16479 | 0.16022 | 0.19226 | -0.33417 | -0.3479 | 0.09613 | -0.045776 | 60.7132 | -61.7935 | 60.3882 | -61.9583 | 0.30212
875.7344 | 123.1247 | -60.6491 | 62.1552 | -0.1624 | 0.016744 | 0.013163 | -0.0014242 | 0.00062048 | -0.0011698 | 0.0019227 | -60.704 | 62.1643 | -61.0474 | 0.11444 | 0.12817 | 0.16937 | -0.032043 | 0.37079 | 0.2243 | -0.19684 | -0.39825 | 0.009156 | -0.054932 | 60.7636 | -62.027 | 60.4523 | -61.9308 | 0.34332
876.75 | 123.0057 | -60.7361 | 62.1506 | 0.11226 | 0.019735 | 0.021067 | 0.0084026 | 0.0016887 | 0.00096645 | -0.00064093 | -60.7544 | 62.2604 | -61.0382 | -0.050354 | -0.073242 | -0.10071 | 0.027466 | 0.068665 | 0.21057 | -0.36163 | -0.30212 | 0.10986 | -0.018311 | 60.6857 | -62.2238 | 60.3745 | -61.94 | 0.28381
877.7344 | 123.1293 | -60.6674 | 62.1506 | -0.14714 | 0.015676 | 0.01594 | -0.0059102 | -0.00087492 | 0.00032545 | -0.00085453 | -60.7132 | 62.178 | -61.0382 | -0.073242 | 0.22888 | 0.1831 | -0.21515 | 0.34332 | 0.24719 | -0.2243 | -0.37079 | 0.027466 | -0.045777 | 60.5942 | -61.9217 | 60.4431 | -61.9034 | 0.32501
878.7656 | 123.0606 | -60.704 | 62.1368 | 0.303 | 0.019948 | 0.017863 | 0.0081888 | 0.00083408 | -0.00010175 | 0.00021367 | -60.7407 | 62.2513 | -61.0611 | -0.032043 | -0.050354 | -0.07782 | -0.059509 | 0.1236 | 0.20142 | -0.33417 | -0.35706 | 0.11444 | -0.036621 | 60.672 | -62.1872 | 60.3699 | -61.9354 | 0.32043
879.7344 | 123.1384 | -60.672 | 62.1368 | -0.13188 | 0.014821 | 0.012736 | -0.0024922 | -0.00066112 | -0.00031535 | 0.0017091 | -60.6857 | 62.1231 | -61.0291 | 0.11444 | 0.1236 | 0.15564 | -0.045776 | 0.35706 | 0.23804 | -0.19684 | -0.35706 | -0.013733 | -0.013733 | 60.7864 | -62.0132 | 60.4752 | -61.8988 | 0.34332
880.7344 | 123.143 | -60.6766 | 62.146 | 0.0054493 | 0.014608 | 0.013804 | -0.0018514 | -0.0021565 | -0.00031535 | -0.00021353 | -60.7498 | 62.1277 | -61.0336 | 0.073242 | 0.068665 | 0.11444 | -0.07782 | 0.32044 | 0.21057 | -0.23346 | -0.35706 | -0.01831 | -0.073242 | 60.7498 | -62.0773 | 60.4431 | -61.9354 | 0.28381
881.7344 | 123.1659 | -60.64 | 62.1231 | -0.017439 | 0.013753 | 0.014018 | -0.0027058 | -0.00066112 | -0.00095615 | 0.00064087 | -60.7224 | 62.146 | -61.0245 | 0.11902 | 0.1236 | 0.14648 | -0.059509 | 0.37079 | 0.2243 | -0.20599 | -0.38452 | 0.022888 | -0.082397 | 60.759 | -61.9995 | 60.434 | -61.8988 | 0.30212
882.75 | 123.0698 | -60.672 | 62.1872 | -0.15477 | 0.019948 | 0.019145 | 0.0088298 | 0.0010477 | -0.0015972 | -0.00042733 | -60.704 | 62.2421 | -61.0199 | 0.045776 | 0.032043 | 0.036621 | 0.073242 | 0.25177 | 0.25635 | -0.20142 | -0.3479 | 0.054931 | -0.032044 | 60.7178 | -62.1552 | 60.4706 | -61.9308 | 0.31586
883.7344 | 123.1567 | -60.6674 | 62.1552 | -0.0021797 | 0.015035 | 0.015513 | -0.0007832 | -0.0017293 | -0.0013834 | -0.00085453 | -60.7315 | 62.1414 | -61.0245 | 0.086975 | 0.091553 | 0.10529 | -0.086975 | 0.3067 | 0.20599 | -0.25177 | -0.35706 | -0.013733 | -0.064087 | 60.7544 | -62.0636 | 60.4156 | -61.9492 | 0.29297
884.7656 | 123.1155 | -60.6583 | 62.1368 | 0.043596 | 0.016103 | 0.014018 | -0.000356 | -0.00044752 | -0.00031535 | 6.6667e-08 | -60.759 | 62.1597 | -61.0199 | 0.041199 | 0.059509 | 0.082397 | -0.064087 | 0.28839 | 0.20599 | -0.25177 | -0.36163 | 0.022888 | -0.10071 | 60.6995 | -62.0773 | 60.4065 | -61.9308 | 0.26093
885.7344 | 123.2025 | -60.6445 | 62.1368 | -0.047956 | 0.01653 | 0.015727 | -0.0012106 | -0.0023701 | 0.00011185 | -0.00064093 | -60.7086 | 62.114 | -61.0245 | 0.12817 | 0.11444 | 0.14648 | -0.064087 | 0.36163 | 0.22888 | -0.20142 | -0.37994 | -0.022888 | -0.064087 | 60.7727 | -62.0224 | 60.4431 | -61.908 | 0.31586
886.75 | 123.0331 | -60.6949 | 62.1918 | -1.139 | 0.01888 | 0.017649 | 0.0066936 | 0.00062048 | -0.00031535 | 0.00021367 | -60.8276 | 62.2513 | -61.0519 | 0.009155 | -0.036621 | 0.045776 | 0.14191 | 0.26093 | 0.2655 | -0.24719 | -0.35706 | 0.05951 | -0.13275 | 60.704 | -62.2284 | 60.4477 | -61.9263 | 0.2243
887.7344 | 123.1613 | -60.6445 | 62.1323 | -0.0098092 | 0.016744 | 0.013163 | -0.002065 | 0.0019023 | -0.00031535 | 0.00085447 | -60.7269 | 62.146 | -61.0153 | 0.09613 | 0.09613 | 0.091553 | -0.07782 | 0.32044 | 0.20599 | -0.23346 | -0.37079 | 0.013733 | -0.082398 | 60.7407 | -62.0361 | 60.4111 | -61.9263 | 0.28839
888.7656 | 123.0469 | -60.704 | 62.1826 | 1.5161 | 0.022085 | 0.016795 | 0.00648 | -0.00023392 | -0.00010175 | -0.00064093 | -60.8688 | 62.2192 | -61.0657 | -0.073242 | -0.073242 | -0.004578 | -0.054932 | 0.064087 | 0.21057 | -0.32044 | -0.36163 | 0.036621 | -0.16479 | 60.6308 | -62.2559 | 60.3836 | -61.972 | 0.19684
889.75 | 123.0652 | -60.6903 | 62.1872 | 0.14278 | 0.020376 | 0.017222 | 0.009257 | 0.0040385 | 0.0024618 | -0.0017089 | -60.6857 | 62.2421 | -61.0062 | 0.064087 | 0.018311 | 0.004578 | 0.018311 | 0.19684 | 0.22888 | -0.2655 | -0.31586 | 0.054931 | 0.004578 | 60.7544 | -62.1689 | 60.4248 | -61.9583 | 0.32044
890.75 | 123.056 | -60.6766 | 62.1506 | 0.051226 | 0.017385 | 0.020213 | 0.005839 | 0.0029705 | -0.00095615 | 6.6667e-08 | -60.7956 | 62.233 | -61.0703 | 0.018311 | 0.018311 | 0.059509 | 0.009155 | 0.18768 | 0.24719 | -0.27008 | -0.39368 | 0.082397 | -0.11902 | 60.6949 | -62.1323 | 60.4065 | -61.9034 | 0.27466
891.7344 | 123.1384 | -60.6491 | 62.1552 | 0.020708 | 0.015035 | 0.015513 | -0.0027058 | 0.0044657 | -0.00031535 | 0.0010681 | -60.7407 | 62.1597 | -61.0382 | 0.073242 | 0.11444 | 0.10986 | -0.07782 | 0.31128 | 0.19684 | -0.22888 | -0.3891 | 0.004578 | -0.091553 | 60.7224 | -62.0407 | 60.4202 | -61.9583 | 0.29755
892.7656 | 123.056 | -60.6812 | 62.2055 | -0.17766 | 0.021016 | 0.01295 | 0.0049846 | 0.0012615 | -0.00074255 | -0.0012817 | -60.7086 | 62.2971 | -61.0382 | 0.032043 | 0.009155 | 0.018311 | 0.10071 | 0.23346 | 0.2655 | -0.19684 | -0.35706 | 0.091553 | -0.027466 | 60.7132 | -62.1964 | 60.4843 | -61.94 | 0.32959
893.7344 | 123.1293 | -60.6537 | 62.1643 | 0.035967 | 0.014821 | 0.012095 | -0.0022786 | 0.0019023 | -0.00052895 | 0.0034181 | -60.7452 | 62.1506 | -61.0474 | 0.041199 | 0.07782 | 0.086975 | -0.036621 | 0.28839 | 0.20599 | -0.25177 | -0.39368 | -0.013733 | -0.091552 | 60.6949 | -62.0865 | 60.4019 | -61.9583 | 0.30212
894.7656 | 123.0011 | -60.7269 | 62.1689 | 0.18855 | 0.020803 | 0.017863 | 0.0081888 | 0.0027567 | 0.00032545 | -0.0010681 | -60.7498 | 62.2559 | -61.0428 | -0.045776 | -0.064087 | -0.07782 | -0.009155 | 0.10071 | 0.20142 | -0.34332 | -0.31586 | 0.086975 | -0.022888 | 60.6812 | -62.233 | 60.3836 | -61.9675 | 0.29297
895.7344 | 123.111 | -60.6766 | 62.1643 | 0.11989 | 0.01653 | 0.012095 | -0.0007832 | -0.00087492 | -0.0041606 | -0.00085453 | -60.7636 | 62.146 | -61.0519 | 0.022888 | -0.10986 | -0.018311 | -0.086975 | 0.20599 | 0.19684 | -0.28839 | -0.37537 | -0.018311 | -0.086975 | 60.6995 | -62.2742 | 60.3882 | -61.9675 | 0.28839
896.7656 | 123.0103 | -60.6949 | 62.1918 | 0.21144 | 0.020376 | 0.016368 | 0.0066936 | 0.00083408 | -0.0015972 | -0.00064093 | -60.7224 | 62.2971 | -61.0199 | -0.054932 | -0.068665 | -0.77362 | -0.38452 | 0.59052 | 0.16022 | -0.38452 | -0.32501 | 0.10529 | -0.027466 | 60.64 | -62.2604 | 60.3104 | -62.0316 | 0.29755
897.7344 | 123.1293 | -60.6766 | 62.1323 | 0.10463 | 0.016103 | 0.017222 | -0.0029196 | 0.00040688 | 0.00118 | 6.6667e-08 | -60.759 | 62.1689 | -61.0428 | 0.022888 | 0.054932 | 0.059509 | -0.054932 | 0.2655 | 0.19684 | -0.28381 | -0.36621 | 0.036621 | -0.082397 | 60.6995 | -62.0773 | 60.3928 | -61.9354 | 0.28381
898.7656 | 123.0377 | -60.6857 | 62.1826 | 0.11989 | 0.021657 | 0.016795 | 0.0090434 | 0.0023295 | 0.00053925 | -0.00021353 | -60.6766 | 62.3062 | -61.0199 | 0.009155 | -0.027466 | -0.041199 | -0.004578 | 0.13733 | 0.21515 | -0.32044 | -0.33417 | 0.1236 | 0.009155 | 60.6949 | -62.2101 | 60.3653 | -61.9675 | 0.34332
899.7344 | 123.1018 | -60.64 | 62.1368 | 0.058855 | 0.01653 | 0.014018 | -0.000356 | -0.00044752 | -0.00052895 | 6.6667e-08 | -60.759 | 62.1643 | -61.0016 | 0.018311 | 0.041199 | 0.050354 | 0.009155 | 0.53558 | 0.21057 | -0.24719 | -0.36163 | 0.027466 | -0.11902 | 60.6583 | -62.0956 | 60.3928 | -61.9263 | 0.24262
900.7656 | 123.0377 | -60.6812 | 62.1643 | 0.066485 | 0.020589 | 0.017436 | 0.0088298 | 0.0044657 | -0.0026652 | -0.0034179 | -60.6262 | 62.2971 | -61.0153 | 0.036621 | 0.004578 | -0.009155 | -0.004578 | 0.16937 | 0.22888 | -0.29755 | -0.33417 | 0.13275 | 0.054931 | 60.7178 | -62.1597 | 60.3836 | -61.9354 | 0.3891
901.7344 | 123.1155 | -60.6674 | 62.146 | 0.089373 | 0.016317 | 0.015299 | -0.0014242 | 0.0029705 | -0.0020244 | -0.0010681 | -60.7544 | 62.1918 | -61.0199 | 0.013733 | 0.045776 | 0.027466 | -0.07782 | 0.21515 | 0.20142 | -0.29297 | -0.35248 | 0.045776 | -0.086976 | 60.6812 | -62.1002 | 60.3745 | -61.9446 | 0.2655
902.75 | 123.0103 | -60.64 | 62.2055 | -0.14714 | 0.014608 | 0.01594 | 0.0019938 | 0.00040688 | 0.00053925 | 6.6667e-08 | -60.7086 | 62.2375 | -61.0062 | 0.027466 | 0.041199 | 0.073242 | 0.14191 | 0.24261 | 0.28839 | -0.1831 | -0.36621 | 0.032044 | -0.068664 | 60.6674 | -62.1643 | 60.4568 | -61.9171 | 0.29755
903.7344 | 123.111 | -60.6491 | 62.1597 | 0.20381 | 0.015462 | 0.011881 | 0.0028484 | 0.0029705 | -0.0013834 | 0.00042727 | -60.6766 | 62.1552 | -61.0382 | 0.027466 | 0.022888 | 0.036621 | -0.15564 | 0.2243 | 0.16022 | -0.32959 | -0.3891 | -0.004578 | -0.027466 | 60.6766 | -62.1368 | 60.3195 | -61.9995 | 0.36163
904.75 | 123.1064 | -60.672 | 62.1964 | -0.13188 | 0.019735 | 0.016368 | 0.0071208 | 0.00019328 | -0.0020244 | -0.0023499 | -60.6674 | 62.2696 | -61.0016 | 0.054932 | 0.036621 | 0.050354 | 0.082397 | 0.2655 | 0.2655 | -0.22888 | -0.32959 | 0.073242 | 0.004578 | 60.7269 | -62.1597 | 60.4431 | -61.9308 | 0.33417
905.7344 | 123.1201 | -60.6491 | 62.1597 | 0.15041 | 0.017385 | 0.011241 | -0.0001424 | 0.0010477 | 0.00032545 | 6.6667e-08 | -60.7269 | 62.1597 | -61.0336 | 0.018311 | 0.036621 | 0.027466 | -0.059509 | 0.25177 | 0.20599 | -0.27924 | -0.38452 | 0 | -0.07782 | 60.6674 | -62.1231 | 60.3699 | -61.9537 | 0.3067
906.75 | 123.0881 | -60.6354 | 62.1918 | -0.1624 | 0.018239 | 0.0097452 | 0.0022074 | -0.0019429 | 0.0016072 | 0.00021367 | -60.6537 | 62.2101 | -60.9695 | 0.091553 | 0.10071 | 0.1236 | 0.068665 | 0.33875 | 0.2655 | -0.19684 | -0.33417 | 0.018311 | -0.018311 | 60.7269 | -62.0911 | 60.4385 | -61.9263 | 0.31586
907.7344 | 123.1018 | -60.6079 | 62.1506 | 0.11989 | 0.01888 | 0.011027 | 0.0019938 | 0.00062048 | -0.00031535 | 0.00085447 | -60.704 | 62.1826 | -61.0153 | 0.027466 | 0.018311 | 0.032043 | -0.07782 | 0.21515 | 0.20599 | -0.27008 | -0.40741 | 0.032043 | -0.096131 | 60.6354 | -62.1323 | 60.3378 | -61.9446 | 0.31128
908.7656 | 123.0286 | -60.6949 | 62.1964 | 0.24959 | 0.020376 | 0.015299 | 0.011607 | 0.0016887 | -0.00052895 | -0.0025635 | -60.7086 | 62.3062 | -61.0245 | -0.045776 | -0.064087 | -0.091553 | -0.009155 | 0.09613 | 0.20599 | -0.3479 | -0.32959 | 0.10986 | -0.013733 | 60.6491 | -62.2604 | 60.347 | -61.9904 | 0.31586
909.7344 | 123.1064 | -60.6491 | 62.1735 | 0.1733 | 0.016958 | 0.016581 | 0.0002848 | 0.00062048 | -0.0013834 | -0.0023499 | -60.7224 | 62.1918 | -61.0291 | 0.013733 | 0.032043 | 0.032043 | -0.082397 | 0.21973 | 0.19226 | -0.28381 | -0.37994 | 0.01831 | -0.073242 | 60.6628 | -62.1414 | 60.3653 | -61.9812 | 0.3067
910.7656 | 123.0606 | -60.6628 | 62.2101 | -0.12425 | 0.020803 | 0.01829 | 0.0084026 | 0.00083408 | -0.00074255 | -0.0034179 | -60.6262 | 62.3062 | -61.0016 | 0.064087 | 0.032043 | 0.032043 | 0.027466 | 0.25177 | 0.23804 | -0.27924 | -0.33875 | 0.09613 | 0.036621 | 60.7269 | -62.178 | 60.3836 | -61.972 | 0.37537
911.7344 | 123.1064 | -60.6537 | 62.1689 | 0.081743 | 0.017385 | 0.011881 | -0.0027058 | -0.00023392 | 0.00118 | -0.0023499 | -60.7269 | 62.1872 | -61.0199 | -0.018311 | 0.19226 | 0.31586 | -0.21515 | 0.10986 | 0.21515 | -0.25635 | -0.36621 | 0.018311 | -0.073242 | 60.6354 | -61.9766 | 60.3973 | -61.9537 | 0.29297
912.7656 | 123.0331 | -60.6537 | 62.2192 | 0.058855 | 0.021871 | 0.020213 | 0.007548 | 0.0027567 | -0.00074255 | -0.0034179 | -60.6308 | 62.3154 | -61.0153 | 0.027466 | -0.022888 | -0.027466 | 0.022888 | 0.16022 | 0.20142 | -0.3067 | -0.36163 | 0.096131 | 0.022889 | 60.6812 | -62.2421 | 60.347 | -62.0178 | 0.38452
913.7344 | 123.0927 | -60.6216 | 62.1826 | 0.089373 | 0.018239 | 0.013163 | -0.0031332 | 0.0027567 | -0.00010175 | -0.00064093 | -60.7178 | 62.2101 | -61.0153 | 0.032043 | 0.041199 | 0.045776 | -0.068665 | 0.24719 | 0.1831 | -0.27924 | -0.39368 | 0.027466 | -0.09613 | 60.6537 | -62.1414 | 60.3424 | -61.9995 | 0.29755
914.7656 | 123.0286 | -60.64 | 62.2238 | 1.3635 | 0.019094 | 0.016581 | 0.0049846 | 0.0016887 | 0.00053925 | -0.0012817 | -60.6812 | 62.3062 | -61.0245 | 0.018311 | 0.036621 | 0.041199 | 0.13733 | 0.27466 | 0.27008 | -0.24261 | -0.38452 | 0.082397 | -0.041198 | 60.6583 | -62.1872 | 60.3973 | -61.9537 | 0.34332
915.7344 | 123.1018 | -60.6216 | 62.1826 | 0.12752 | 0.01354 | 0.014018 | -0.0024922 | -0.00023392 | -0.00031535 | -0.0012817 | -60.7086 | 62.1826 | -61.0245 | 0.045776 | 0.041199 | 0.059509 | -0.07782 | 0.2655 | 0.20142 | -0.24719 | -0.40283 | 0 | -0.086975 | 60.6674 | -62.1414 | 60.3745 | -61.9812 | 0.31586
916.7656 | 123.0194 | -60.6766 | 62.2101 | 0.23433 | 0.018667 | 0.016154 | 0.0066936 | 0.0046793 | -0.00095615 | 0.0012817 | -60.704 | 62.3154 | -61.0062 | -0.032043 | -0.086975 | -0.10529 | -0.013733 | 0.086975 | 0.19684 | -0.33417 | -0.32959 | 0.10529 | -0.027466 | 60.6445 | -62.2971 | 60.3424 | -62.0132 | 0.30212
917.7344 | 123.1064 | -60.6308 | 62.178 | 0.066485 | 0.019735 | 0.016154 | 0.0002848 | 0.00019328 | -0.00074255 | 0.0027771 | -60.7224 | 62.1826 | -61.0199 | 0.022888 | 0.032043 | 0.022888 | -0.07782 | 0.23346 | 0.19226 | -0.27924 | -0.3891 | 0.004577 | -0.091553 | 60.6537 | -62.146 | 60.3516 | -61.9858 | 0.29755
918.7656 | 123.1522 | -60.5988 | 62.1643 | -0.0021797 | 0.016744 | 0.011027 | -0.0022786 | 0.00019328 | -0.00074255 | 0.0014953 | -60.704 | 62.1872 | -60.9787 | 0.086975 | 0.07782 | 0.10529 | -0.064087 | 0.3067 | 0.21057 | -0.25635 | -0.37994 | 0.022888 | -0.10529 | 60.6857 | -62.0865 | 60.3424 | -61.9537 | 0.27466
919.7344 | 123.111 | -60.6171 | 62.1872 | 0.081743 | 0.015035 | 0.016581 | 0.0009258 | -0.0019429 | 0.00053925 | 0.0017091 | -60.6995 | 62.1735 | -60.9879 | 0.027466 | 0.09613 | 0.33417 | -0.082397 | 0.10529 | 0.21515 | -0.26093 | -0.37079 | -0.013733 | -0.082398 | 60.6445 | -62.0911 | 60.3561 | -61.972 | 0.28839
920.7656 | 123.0743 | -60.64 | 62.2009 | 0.28011 | 0.020376 | 0.020213 | 0.0096842 | 0.00062048 | 0.00011185 | -0.0017089 | -60.6583 | 62.265 | -60.9879 | 0 | -0.041199 | -0.041199 | -0.10986 | 0.14648 | 0.16479 | -0.34332 | -0.3479 | 0.064087 | -0.01831 | 60.64 | -62.2421 | 60.2966 | -62.0361 | 0.32959
921.7344 | 123.1064 | -60.6354 | 62.1552 | 0.066485 | 0.014181 | 0.012309 | 0.0002848 | -0.0017293 | 0.0013936 | 0.00021367 | -60.7132 | 62.1964 | -60.9833 | 0.041199 | 0.041199 | 0.036621 | -0.082397 | 0.22888 | 0.20599 | -0.27924 | -0.3479 | 0.041199 | -0.07782 | 60.6766 | -62.114 | 60.3561 | -61.9492 | 0.27008
922.7656 | 123.0698 | -60.64 | 62.1597 | 0.21144 | 0.022298 | 0.015727 | 0.0071208 | 0.0029705 | 0.00118 | -0.0010681 | -60.672 | 62.2833 | -61.0153 | -0.018311 | -0.032043 | -0.073242 | -0.10529 | 0.1236 | 0.1831 | -0.35248 | -0.37537 | 0.1236 | -0.032043 | 60.6216 | -62.1918 | 60.2875 | -61.9766 | 0.34332
923.7344 | 123.1018 | -60.6308 | 62.1826 | 0.11989 | 0.016744 | 0.017008 | -0.0007832 | -0.00044752 | 0.0024618 | 0.0019227 | -60.7132 | 62.1964 | -61.0016 | 0.027466 | 0.041199 | 0.032043 | -0.086975 | 0.23804 | 0.20599 | -0.28381 | -0.37079 | 0.013733 | -0.082398 | 60.6583 | -62.1414 | 60.347 | -61.9766 | 0.28839
924.7656 | 123.056 | -60.6674 | 62.178 | 0.24196 | 0.022939 | 0.018931 | 0.007548 | 0.0019023 | -0.0013834 | -0.0023499 | -60.672 | 62.3154 | -61.0016 | -0.027466 | -0.068665 | -0.10071 | -0.018311 | 0.082397 | 0.20142 | -0.3479 | -0.33417 | 0.13733 | -0.004578 | 60.64 | -62.2467 | 60.3195 | -61.9766 | 0.32959
925.7344 | 123.1201 | -60.6354 | 62.1918 | -0.063215 | 0.016958 | 0.015086 | -0.0031332 | -0.0015157 | 0.00053925 | 0.00085447 | -60.704 | 62.2055 | -61.0062 | 0.036621 | 0.054932 | 0.059509 | -0.073242 | 0.27924 | 0.20142 | -0.27924 | -0.37079 | 0.013733 | -0.068665 | 60.672 | -62.1368 | 60.3561 | -61.9904 | 0.30212
926.75 | 123.0927 | -60.6033 | 62.2101 | -0.15477 | 0.016317 | 0.01359 | 0.001353 | -0.0030111 | -0.00074255 | 6.6667e-08 | -60.6354 | 62.2375 | -60.9421 | 0.10529 | 0.10529 | 0.1236 | 0.036621 | 0.33417 | 0.23346 | -0.2243 | -0.33875 | 0.027466 | -0.032043 | 60.7086 | -62.1048 | 60.379 | -61.9766 | 0.3067
927.7344 | 123.1201 | -60.6079 | 62.2009 | -0.52098 | 0.018026 | 0.017436 | 0.001353 | -0.0019429 | -0.00031535 | -0.00042733 | -60.6857 | 62.2101 | -61.0016 | 0.036621 | 0.036621 | 0.045776 | -0.059509 | 0.24261 | 0.19226 | -0.27008 | -0.39368 | 0.009155 | -0.07782 | 60.6445 | -62.1643 | 60.3378 | -62.0087 | 0.31586
928.7656 | 123.0606 | -60.6445 | 62.2284 | 0.11226 | 0.021444 | 0.019999 | 0.0086162 | 0.0010477 | -0.0013834 | -0.0027771 | -60.6216 | 62.3199 | -60.9695 | 0.009155 | -0.027466 | -0.068665 | 0.009155 | 0.14648 | 0.2243 | -0.29297 | -0.32501 | 0.091552 | 0.022888 | 60.6537 | -62.2559 | 60.3516 | -62.0041 | 0.3479
929.7344 | 123.143 | -60.6216 | 62.2009 | -0.017439 | 0.016317 | 0.01594 | -0.0027058 | 0.0012615 | -0.0013834 | -0.0017089 | -60.6491 | 62.2192 | -60.997 | 0.082397 | 0.091553 | 0.10071 | -0.07782 | 0.31586 | 0.21973 | -0.24719 | -0.37537 | 0.01831 | -0.027466 | 60.704 | -62.1094 | 60.3745 | -61.9812 | 0.3479
930.7656 | 123.0606 | -60.6583 | 62.2192 | -0.070844 | 0.019307 | 0.014659 | 0.0096842 | 0.0021159 | -0.0015972 | -0.00064093 | -60.5896 | 62.3245 | -60.9558 | 0.082397 | 0.032043 | 0.045776 | 0.036621 | 0.22888 | 0.24719 | -0.2655 | -0.29755 | 0.10529 | 0.068664 | 60.7407 | -62.1872 | 60.3928 | -61.972 | 0.36621
931.7344 | 123.1293 | -60.6079 | 62.1689 | 0.11226 | 0.018239 | 0.014445 | -0.0014242 | 0.00019328 | 0.0013936 | -0.00042733 | -60.6812 | 62.1964 | -60.9924 | 0.022888 | 0.050354 | 0.045776 | -0.073242 | 0.23804 | 0.18768 | -0.2655 | -0.38452 | 0.027466 | -0.073242 | 60.6308 | -62.1185 | 60.3424 | -61.9812 | 0.31128
932.7656 | 123.0743 | -60.6262 | 62.1918 | 0.25722 | 0.020803 | 0.017436 | 0.0071208 | 0.00083408 | -0.00010175 | 0.0014953 | -60.6583 | 62.3016 | -61.0016 | -0.013733 | -0.036621 | -0.059509 | -0.11444 | 0.11444 | 0.19226 | -0.33875 | -0.37537 | 0.10986 | -0.032043 | 60.6125 | -62.2284 | 60.2875 | -61.9995 | 0.34332
933.7344 | 123.1247 | -60.6079 | 62.2284 | -0.017439 | 0.017171 | 0.012522 | -0.0022786 | -2.0324e-05 | 0.00053925 | -0.0025635 | -60.6995 | 62.2192 | -60.9741 | 0.050354 | 0.064087 | 0.068665 | -0.064087 | 0.28381 | 0.21515 | -0.27924 | -0.36621 | -0.009156 | -0.091553 | 60.6583 | -62.1643 | 60.3287 | -62.0132 | 0.27466
934.7656 | 123.0011 | -60.6628 | 62.2284 | 0.074114 | 0.019735 | 0.021067 | 0.010112 | 0.0016887 | -0.0018108 | -0.00021353 | -60.6354 | 62.3337 | -60.9558 | -0.004578 | -0.050354 | -0.045776 | 0.027466 | 0.1236 | 0.20599 | -0.32501 | -0.29297 | 0.10528 | 0.027466 | 60.6583 | -62.2787 | 60.3378 | -62.0224 | 0.32043
935.7344 | 123.1338 | -60.6171 | 62.2009 | 0.051226 | 0.018026 | 0.011454 | -0.0016378 | 0.00040688 | -0.00031535 | -0.0014953 | -60.5759 | 62.2421 | -60.965 | 0.054932 | 0.054932 | 0.041199 | -0.073242 | 0.25177 | 0.21057 | -0.27008 | -0.3479 | 0.041198 | 0.041198 | 60.672 | -62.146 | 60.347 | -61.9904 | 0.3891
936.7656 | 123.1613 | -60.5942 | 62.1689 | 0.28774 | 0.017171 | 0.017649 | 0.00648 | 0.0023295 | 0.00118 | -0.00021353 | -60.5667 | 62.2467 | -60.9787 | 0.050354 | 0.054932 | 0.032043 | -0.19684 | 0.22888 | 0.16022 | -0.36163 | -0.38452 | 0.07782 | 0.027466 | 60.6445 | -62.114 | 60.2325 | -62.0087 | 0.41199
937.7344 | 123.1064 | -60.6033 | 62.2101 | 0.10463 | 0.015249 | 0.013163 | -0.0022786 | -0.0010885 | 0.00075285 | -0.00021353 | -60.672 | 62.2009 | -60.9833 | 0.022888 | 0.050354 | 0.10529 | 0.13275 | 0.22888 | 0.22888 | -0.24719 | -0.37994 | -0.009155 | -0.068664 | 60.6262 | -62.1597 | 60.3561 | -61.9812 | 0.31128
938.7656 | 123.0789 | -60.6125 | 62.2238 | -0.10899 | 0.01888 | 0.014018 | 0.0071208 | -0.00044752 | 0.00032545 | 0.00042727 | -60.585 | 62.3383 | -60.9604 | 0.068665 | 0.050354 | 0.064087 | 0.073242 | 0.2655 | 0.24719 | -0.27008 | -0.3479 | 0.11444 | 0.027466 | 60.6812 | -62.1735 | 60.3424 | -61.9766 | 0.37537
939.7344 | 123.111 | -60.6033 | 62.2238 | 0.074114 | 0.015462 | 0.013804 | -0.0031332 | -0.00023392 | 0.0013936 | -0.0010681 | -60.6628 | 62.1918 | -60.9787 | 0.059509 | 0.07782 | 0.086975 | -0.050354 | 0.30212 | 0.20142 | -0.2655 | -0.37537 | -0.032044 | -0.059509 | 60.6628 | -62.146 | 60.3378 | -62.0224 | 0.31586
940.7656 | 123.111 | -60.5988 | 62.2101 | 0.013079 | 0.01653 | 0.012522 | 0.000712 | -0.0010885 | 0.00096645 | 0.00021367 | -60.6628 | 62.2101 | -60.9558 | 0.018311 | 0.018311 | 0.054932 | -0.036621 | 0.23804 | 0.20142 | -0.27466 | -0.35706 | 0 | -0.064087 | 60.6171 | -62.1918 | 60.3241 | -62.0087 | 0.29297
941.7344 | 123.1155 | -60.5896 | 62.178 | 0.49373 | 0.014608 | 0.016368 | -0.0016378 | -0.00066112 | -0.00010175 | 0.00042727 | -60.6674 | 62.2147 | -60.9512 | 0.041199 | 0.054932 | 0.059509 | -0.068665 | 0.26093 | 0.20599 | -0.27466 | -0.36163 | 0.036621 | -0.077819 | 60.6308 | -62.1231 | 60.3149 | -61.972 | 0.28381
942.7656 | 123.0881 | -60.6171 | 62.2787 | -0.13951 | 0.019521 | 0.016795 | 0.007548 | -2.0324e-05 | -0.00095615 | -0.00085453 | -60.6079 | 62.3199 | -60.965 | 0.045776 | 0.013733 | 0.036621 | 0.10529 | 0.24719 | 0.25635 | -0.17853 | -0.3479 | 0.041198 | 0.009155 | 60.6628 | -62.265 | 60.4385 | -62.0224 | 0.35706
943.7344 | 123.1384 | -60.5942 | 62.233 | 0.0054493 | 0.016958 | 0.016795 | -0.002065 | -0.00044752 | 0.00053925 | -0.00064093 | -60.6171 | 62.2055 | -60.9421 | 0.082397 | 0.082397 | 0.09613 | -0.068665 | 0.29297 | 0.21515 | -0.24719 | -0.3479 | -0.027466 | -0.022888 | 60.6766 | -62.1506 | 60.347 | -62.0178 | 0.32501
944.7656 | 123.0606 | -60.6216 | 62.2559 | -0.17003 | 0.018453 | 0.019145 | 0.0071208 | -0.00023392 | -0.00095615 | -0.0012817 | -60.6216 | 62.3199 | -60.9695 | 0.022888 | 0.013733 | 0.022888 | 0.11902 | 0.24261 | 0.27924 | -0.19684 | -0.3479 | 0.064087 | 0 | 60.6445 | -62.2421 | 60.4248 | -61.9766 | 0.3479
945.7344 | 123.0011 | -60.6216 | 62.2513 | -0.19291 | 0.016958 | 0.017863 | 0.002421 | 0.00040688 | -0.002238 | 0.0012817 | -60.6445 | 62.3154 | -60.9741 | 0.036621 | 0.036621 | 0.041199 | 0.13733 | 0.23804 | 0.28381 | -0.17395 | -0.35248 | 0.064087 | -0.022888 | 60.6583 | -62.2147 | 60.4477 | -61.9675 | 0.32959
946.7656 | 123.0286 | -60.64 | 62.2375 | 0.028338 | 0.01888 | 0.019145 | 0.0098978 | 0.0031841 | -0.0018108 | -0.0010681 | -60.5759 | 62.3245 | -60.9558 | 0.022888 | -0.013733 | -0.013733 | 0.004578 | 0.16022 | 0.2243 | -0.29297 | -0.31586 | 0.086975 | 0.064087 | 60.6628 | -62.2513 | 60.347 | -62.0132 | 0.37994
947.7344 | 123.111 | -60.5988 | 62.2055 | 0.18855 | 0.016744 | 0.015086 | -0.0007832 | 0.0029705 | -0.0011698 | 0.00021367 | -60.6537 | 62.2284 | -60.9787 | 0.027466 | 0.064087 | 0.07782 | -0.082397 | 0.25635 | 0.20599 | -0.2655 | -0.37994 | 0.022889 | -0.054932 | 60.6262 | -62.1414 | 60.3333 | -61.9995 | 0.32501
948.7656 | 123.0698 | -60.6262 | 62.233 | -0.070844 | 0.020376 | 0.024272 | 0.009257 | 0.0014751 | -0.00095615 | -0.00042733 | -60.5576 | 62.352 | -60.9695 | 0.059509 | 0.041199 | 0.027466 | 0.022888 | 0.24261 | 0.23346 | -0.26093 | -0.34332 | 0.11902 | 0.068665 | 60.6857 | -62.1918 | 60.3653 | -61.9995 | 0.41199
949.7344 | 123.1018 | -60.6033 | 62.1918 | 0.043596 | 0.016103 | 0.015513 | -0.0007832 | 0.00019328 | 0.0013936 | 0.00085447 | -60.6537 | 62.233 | -60.9604 | -0.004578 | 0.032043 | 0.064087 | -0.045776 | 0.21973 | 0.19226 | -0.28839 | -0.35706 | 0.041199 | -0.050354 | 60.5988 | -62.1597 | 60.3149 | -61.9995 | 0.3067
950.7656 | 123.1018 | -60.6033 | 62.2238 | -0.093733 | 0.016958 | 0.019145 | 0.0022074 | 0.00040688 | -0.0018108 | -0.0017089 | -60.5438 | 62.2696 | -60.9192 | 0.10986 | 0.10986 | 0.13275 | 0.041199 | 0.35706 | 0.22888 | -0.22888 | -0.31586 | 0.045776 | 0.05951 | 60.7132 | -62.114 | 60.3745 | -61.9949 | 0.37537
951.7344 | 123.1064 | -60.5713 | 62.2192 | 0.074114 | 0.015676 | 0.014659 | -0.0005696 | 0.00040688 | -0.00095615 | 6.6667e-08 | -60.6583 | 62.2375 | -60.9604 | 0.036621 | 0.036621 | 0.036621 | -0.068665 | 0.24261 | 0.20599 | -0.27924 | -0.3891 | 0.018311 | -0.086975 | 60.6079 | -62.1826 | 60.2921 | -62.0132 | 0.30212
952.7656 | 123.111 | -60.585 | 62.2284 | 0.081743 | 0.015889 | 0.011668 | 0.0002848 | -0.0017293 | -0.0011698 | 0.00042727 | -60.6079 | 62.2467 | -60.9375 | 0.018311 | 0.050354 | 0.068665 | -0.086975 | 0.21973 | 0.18768 | -0.27466 | -0.35248 | 0.01831 | -0.022888 | 60.6033 | -62.178 | 60.3104 | -62.0407 | 0.32959
953.7344 | 123.1155 | -60.5896 | 62.2009 | -0.4218 | 0.018239 | 0.020426 | 0.0015666 | -0.0010885 | 0.0013936 | -0.00042733 | -60.6812 | 62.233 | -60.965 | 0.018311 | 0.032043 | 0.059509 | -0.07782 | 0.25635 | 0.19684 | -0.28381 | -0.37537 | 0.032043 | -0.091552 | 60.6079 | -62.1689 | 60.3058 | -62.0041 | 0.28381
954.7656 | 123.0606 | -60.6125 | 62.2696 | -0.10136 | 0.021016 | 0.016368 | 0.004771 | 0.0016887 | -0.0011698 | -0.0014953 | -60.5942 | 62.3199 | -60.9604 | 0.045776 | 0.009155 | 0.022888 | 0.10986 | 0.25635 | 0.26093 | -0.19226 | -0.3479 | 0.050354 | 0.018311 | 60.6583 | -62.2604 | 60.4202 | -62.0087 | 0.36621
955.7344 | 123.1338 | -60.5667 | 62.2009 | 0.11989 | 0.016958 | 0.016368 | -0.0039876 | 0.00019328 | -0.0030924 | -0.00042733 | -60.64 | 62.2055 | -60.965 | 0.032043 | 0.041199 | 0.036621 | -0.059509 | 0.25635 | 0.19684 | -0.27466 | -0.39825 | 0.004577 | -0.073243 | 60.5988 | -62.1597 | 60.2921 | -62.0041 | 0.32501
956.7656 | 123.0698 | -60.5896 | 62.2787 | 0.028338 | 0.020803 | 0.021281 | 0.0098978 | 0.0027567 | -0.003947 | -0.0012817 | -60.5347 | 62.3291 | -60.9329 | 0.086975 | 0.018311 | 0.032043 | 0.027466 | 0.22888 | 0.23804 | -0.29297 | -0.34332 | 0.050354 | 0.054932 | 60.6766 | -62.2604 | 60.2966 | -62.0407 | 0.39825
957.7344 | 123.1064 | -60.5667 | 62.2147 | -1.4441 | 0.019094 | 0.01594 | 0.0002848 | 0.00062048 | -0.00074255 | 0.00085447 | -60.6262 | 62.2467 | -60.9695 | 0.027466 | 0.022888 | 0.041199 | -0.059509 | 0.25177 | 0.21515 | -0.28381 | -0.40283 | 0.032043 | -0.05951 | 60.5942 | -62.1918 | 60.2829 | -61.9995 | 0.34332
958.7656 | 123.056 | -60.6125 | 62.2604 | -0.20817 | 0.019521 | 0.022563 | 0.0069072 | -2.0324e-05 | -0.0011698 | -0.00085453 | -60.5988 | 62.3383 | -60.9558 | 0.032043 | 0.018311 | 0.036621 | 0.10529 | 0.23804 | 0.27924 | -0.21515 | -0.34332 | 0.07782 | 0.013733 | 60.6445 | -62.2421 | 60.3973 | -61.9812 | 0.35706
959.7344 | 123.0881 | -60.5804 | 62.2284 | 0.081743 | 0.016744 | 0.016581 | -0.0005696 | 0.0023295 | -0.00052895 | -0.00042733 | -60.6262 | 62.2375 | -60.9512 | 0.041199 | 0.041199 | 0.027466 | -0.082397 | 0.2243 | 0.19684 | -0.27924 | -0.37079 | 0.009155 | -0.045777 | 60.6216 | -62.1872 | 60.3012 | -62.0316 | 0.32501
960.7656 | 123.0377 | -60.6216 | 62.2192 | 0.21144 | 0.020589 | 0.015727 | 0.0081888 | 0.0023295 | -0.00052895 | 0.00042727 | -60.6308 | 62.3199 | -60.965 | -0.036621 | -0.059509 | -0.07782 | -0.068665 | 0.09613 | 0.1831 | -0.35248 | -0.34332 | 0.10071 | -0.009155 | 60.585 | -62.2787 | 60.2692 | -62.0361 | 0.33417
961.7344 | 123.1018 | -60.5667 | 62.2375 | 0.15804 | 0.016958 | 0.018077 | 0.0015666 | 0.00062048 | 0.00075285 | -0.0019225 | -60.6262 | 62.233 | -60.9467 | 0.009155 | 0.032043 | 0.022888 | -0.086975 | 0.20599 | 0.20599 | -0.30212 | -0.37994 | -0.004578 | -0.05951 | 60.5759 | -62.2055 | 60.2646 | -62.0316 | 0.32043
962.7656 | 123.0194 | -60.64 | 62.2513 | 0.10463 | 0.022085 | 0.016154 | 0.0088298 | 0.0031841 | 0.00011185 | -0.00064093 | -60.5942 | 62.3474 | -60.9375 | -0.041199 | -0.050354 | -0.073242 | 0.027466 | 0.09613 | 0.21973 | -0.34332 | -0.29755 | 0.09613 | 0.045777 | 60.5988 | -62.3016 | 60.2966 | -62.0316 | 0.34332
963.7344 | 123.0927 | -60.5942 | 62.2238 | 0.2267 | 0.016317 | 0.017008 | 0.0004984 | 0.00083408 | -0.00074255 | 0.0014953 | -60.5896 | 62.2604 | -60.9375 | 0.022888 | 0.013733 | 0 | -0.14191 | 0.21515 | 0.17395 | -0.35706 | -0.34332 | 0.036621 | 0.004577 | 60.6171 | -62.2101 | 60.2371 | -62.0499 | 0.3479
964.7656 | 123.0515 | -60.585 | 62.2375 | -0.10136 | 0.020803 | 0.018931 | 0.0081888 | 0.0023295 | -0.0011698 | -0.00021353 | -60.5438 | 62.3749 | -60.9467 | 0.064087 | 0.045776 | 0.050354 | 0.045776 | 0.25177 | 0.22888 | -0.26093 | -0.36163 | 0.13733 | 0.041199 | 60.6491 | -62.1918 | 60.3241 | -62.0087 | 0.40283
965.7344 | 123.1247 | -60.5759 | 62.1964 | 0.31063 | 0.019521 | 0.015086 | 0.0015666 | 0.0014751 | -0.0018108 | -0.00085453 | -60.5072 | 62.2375 | -60.9283 | 0.054932 | 0.036621 | 0.009155 | -0.17853 | 0.24261 | 0.16022 | -0.31586 | -0.35248 | 0.041199 | 0.068665 | 60.6308 | -62.1597 | 60.26 | -62.0361 | 0.42114
966.7656 | 123.0515 | -60.5988 | 62.2559 | 0.013079 | 0.021871 | 0.016368 | 0.012034 | 0.0040385 | 0.00011185 | 6.6667e-08 | -60.5942 | 62.3383 | -60.965 | 0.036621 | 0.041199 | 0.036621 | 0.018311 | 0.21973 | 0.23346 | -0.27008 | -0.36621 | 0.082398 | 0.004578 | 60.6354 | -62.2147 | 60.3287 | -62.0224 | 0.37079
967.7344 | 123.1293 | -60.5713 | 62.1918 | 0.33351 | 0.018026 | 0.01295 | 0.0037028 | 0.0038249 | -0.00095615 | 6.6667e-08 | -60.5713 | 62.233 | -60.9146 | 0.036621 | 0.050354 | 0.036621 | -0.16937 | 0.2243 | 0.17395 | -0.34332 | -0.34332 | 0.041199 | 0 | 60.6079 | -62.1414 | 60.228 | -62.0178 | 0.34332
968.7656 | 123.0698 | -60.5988 | 62.233 | -0.017439 | 0.020162 | 0.021281 | 0.0069072 | 0.0012615 | -0.0011698 | -0.00085453 | -60.5392 | 62.3886 | -60.9238 | 0.045776 | 0.032043 | 0.045776 | 0.027466 | 0.23346 | 0.23804 | -0.27008 | -0.32501 | 0.15564 | 0.059509 | 60.6445 | -62.2009 | 60.3287 | -61.9949 | 0.38452
969.7344 | 123.1476 | -60.5804 | 62.2009 | 0.26485 | 0.019094 | 0.017436 | 0.0037028 | 0.0048931 | -0.0011698 | -0.0014953 | -60.5438 | 62.2559 | -60.9421 | 0.032043 | 0.050354 | 0.073242 | -0.66834 | -0.018311 | 0.14191 | -0.44403 | -0.36163 | 0.054931 | 0.036621 | 60.6125 | -62.1506 | 60.1364 | -62.059 | 0.39825
970.7656 | 123.0743 | -60.5988 | 62.2467 | -0.12425 | 0.019948 | 0.01829 | 0.0077616 | 0.0023295 | 0.00011185 | 0.00042727 | -60.5347 | 62.384 | -60.9329 | 0.068665 | 0.050354 | 0.059509 | 0.082397 | 0.27924 | 0.24261 | -0.24719 | -0.33417 | 0.13733 | 0.064087 | 60.6674 | -62.1964 | 60.3516 | -62.0041 | 0.39825
971.7344 | 123.143 | -60.5667 | 62.1918 | 0.19618 | 0.016958 | 0.019786 | 0.0009258 | 0.0061747 | -0.00095615 | -0.00064093 | -60.5347 | 62.2787 | -60.9329 | 0.036621 | 0.036621 | 0.022888 | -0.19684 | 0.21057 | 0.16022 | -0.35248 | -0.36621 | 0.086976 | 0.032043 | 60.6033 | -62.1552 | 60.2142 | -62.0316 | 0.39825
972.75 | 123.056 | -60.5988 | 62.2421 | -0.17003 | 0.01653 | 0.015513 | -0.0009968 | 0.0010477 | -0.0024516 | 0.00021367 | -60.5759 | 62.2742 | -60.9421 | 0.050354 | 0.064087 | 0.091553 | 0.11444 | 0.3067 | 0.2655 | -0.17853 | -0.34332 | 0.032044 | 0.022888 | 60.6491 | -62.178 | 60.4202 | -61.9766 | 0.36621
973.7344 | 123.143 | -60.5576 | 62.2147 | 0.29537 | 0.017812 | 0.015086 | 0.0037028 | 0.0031841 | 0.00053925 | 6.6667e-08 | -60.5164 | 62.3016 | -60.9283 | 0.050354 | 0.054932 | 0.050354 | -0.18768 | 0.23346 | 0.16937 | -0.35706 | -0.37079 | 0.086975 | 0.041199 | 60.6079 | -62.1597 | 60.2005 | -62.0453 | 0.41199
974.7656 | 123.056 | -60.5804 | 62.2696 | -0.093733 | 0.022298 | 0.018077 | 0.0081888 | 0.0048931 | -0.00095615 | -0.0012817 | -60.5255 | 62.3749 | -60.9421 | 0.036621 | 0.009155 | 0.018311 | 0.022888 | 0.21057 | 0.22888 | -0.27924 | -0.36163 | 0.10529 | 0.054931 | 60.6171 | -62.2604 | 60.3012 | -62.0407 | 0.41657
975.7344 | 123.1476 | -60.5667 | 62.2147 | 0.303 | 0.019307 | 0.019786 | 0.0032756 | 0.0042521 | 0.00011185 | -0.0014953 | -60.5484 | 62.2925 | -60.9375 | -0.009155 | 0.013733 | 0.041199 | -0.14191 | 0.19684 | 0.16479 | -0.36163 | -0.37079 | 0.077819 | 0.01831 | 60.5576 | -62.2009 | 60.2051 | -62.0499 | 0.3891
976.75 | 123.0972 | -60.5621 | 62.2009 | 0.21907 | 0.019521 | 0.016368 | 0.0004984 | 0.0023295 | 0.0013936 | 6.6667e-08 | -60.5484 | 62.265 | -60.9192 | 0.032043 | 0.041199 | 0.022888 | -0.15106 | 0.21973 | 0.16937 | -0.35248 | -0.35706 | 0.064087 | 0.013733 | 60.5942 | -62.1597 | 60.2097 | -62.0316 | 0.37079
977.7344 | 123.0881 | -60.5896 | 62.2513 | 0.26485 | 0.020162 | 0.020213 | 0.0062662 | 0.0033977 | 0.0020344 | -0.00064093 | -60.5804 | 62.3428 | -60.9604 | -0.045776 | -0.027466 | -0.064087 | -0.09613 | 0.13733 | 0.18768 | -0.34332 | -0.37079 | 0.091552 | 0.009156 | 60.5438 | -62.2787 | 60.2463 | -62.0636 | 0.37994
978.7656 | 122.9965 | -60.5896 | 62.2696 | -0.19291 | 0.018239 | 0.017436 | 0.004771 | 0.00062048 | -0.0024516 | -0.00021353 | -60.5942 | 62.3428 | -60.9604 | 0.022888 | 0.022888 | 0.032043 | 0.32044 | 0.68665 | 0.28381 | -0.12817 | -0.37079 | 0.073242 | -0.004577 | 60.6125 | -62.2467 | 60.4614 | -61.9858 | 0.36621
979.7344 | 123.0469 | -60.5988 | 62.2421 | -2.1003 | 0.020589 | 0.024272 | 0.0071208 | 0.0044657 | -0.0024516 | -0.0010681 | -60.6079 | 62.3474 | -60.9329 | -0.036621 | -0.073242 | -0.091553 | -0.004578 | 0.091553 | 0.2243 | -0.32959 | -0.33417 | 0.10529 | -0.009155 | 60.5621 | -62.3154 | 60.2692 | -62.0178 | 0.32501
980.7656 | 123.1247 | -60.5347 | 62.2421 | -0.10136 | 0.017598 | 0.014659 | -0.0009968 | 0.0012615 | -0.0018108 | 0.00042727 | -60.5301 | 62.2879 | -60.9421 | 0.44403 | 0.48981 | 0.15106 | -0.62256 | 0.19684 | 0.28381 | -0.17395 | -0.40741 | 0.045777 | 0.004578 | 60.9787 | -61.7523 | 60.3607 | -61.9583 | 0.41199
981.7344 | 123.0606 | -60.5896 | 62.2467 | 0.24959 | 0.019948 | 0.01829 | 0.004771 | 0.0053203 | -0.00010175 | -0.00042733 | -60.5576 | 62.3428 | -60.9375 | -0.045776 | -0.059509 | -0.082397 | -0.068665 | 0.11444 | 0.17395 | -0.35248 | -0.3479 | 0.09613 | 0.032044 | 60.5438 | -62.3062 | 60.2371 | -62.0728 | 0.37994
982.7656 | 123.1705 | -60.5621 | 62.2467 | -0.12425 | 0.015249 | 0.012309 | -0.0022786 | 0.00083408 | -0.00010175 | 0.0014953 | -60.498 | 62.2421 | -60.9009 | 0.11902 | 0.14191 | 0.15564 | -0.045776 | 0.36163 | 0.24261 | -0.19684 | -0.33875 | -0.004578 | 0.064087 | 60.6812 | -62.1048 | 60.3653 | -62.0041 | 0.40283
983.7344 | 123.0331 | -60.6079 | 62.2833 | 0.21907 | 0.022725 | 0.021922 | 0.0062662 | 0.0057475 | 0.002248 | -0.0017089 | -60.5713 | 62.3886 | -60.9375 | 0.32959 | 0.16479 | -0.23346 | 0.013733 | 0.28381 | 0.21057 | -0.33875 | -0.32959 | 0.10529 | 0.036621 | 60.9375 | -62.1185 | 60.2692 | -62.0728 | 0.36621
984.75 | 123.1201 | -60.5621 | 62.2375 | 0.081743 | 0.017812 | 0.017008 | -0.0001424 | 0.0016887 | 0.00118 | -0.00042733 | -60.5988 | 62.2467 | -60.9329 | 0.018311 | 0.027466 | 0.022888 | -0.07782 | 0.22888 | 0.20142 | -0.28381 | -0.37079 | 0.009155 | -0.036621 | 60.5804 | -62.2101 | 60.2783 | -62.0361 | 0.33417
985.7344 | 123.024 | -60.5942 | 62.2787 | 0.11226 | 0.02123 | 0.017008 | 0.01118 | 0.0036113 | -0.0020244 | -0.00042733 | -60.5347 | 62.384 | -60.9146 | -0.027466 | -0.050354 | -0.073242 | 0.032043 | 0.14191 | 0.21057 | -0.29297 | -0.32043 | 0.10529 | 0.059509 | 60.5667 | -62.3291 | 60.3012 | -62.0682 | 0.37994
986.7656 | 123.1293 | -60.5255 | 62.2696 | 2.0272 | 0.016958 | 0.022563 | -0.000356 | -0.00087492 | -0.0026652 | 0.0010681 | -60.5713 | 62.2604 | -60.9329 | 0.082397 | 0.13275 | 0.17395 | -0.032043 | 0.35706 | 0.2243 | -0.23346 | -0.40741 | -0.009155 | -0.045776 | 60.6079 | -62.1368 | 60.2921 | -62.0453 | 0.36163
987.7344 | 123.0148 | -60.5942 | 62.2787 | 0.24196 | 0.021016 | 0.017008 | 0.009257 | 0.0072429 | -0.0011698 | -0.0021361 | -60.5621 | 62.3795 | -60.9467 | 0.21057 | 0.31586 | 0.013733 | -0.086975 | 0.23346 | 0.20599 | -0.34332 | -0.35248 | 0.10071 | 0.032043 | 60.8047 | -61.9629 | 60.2509 | -62.0728 | 0.38452
988.7656 | 123.0515 | -60.5759 | 62.2742 | -0.14714 | 0.018026 | 0.015513 | 0.0002848 | 0.0016887 | -0.0011698 | -0.0014953 | -60.5759 | 62.3383 | -60.9512 | 0 | 0.032043 | 0.059509 | 0.14191 | 0.26093 | 0.28839 | -0.17395 | -0.37537 | 0.064087 | 0 | 60.5759 | -62.2421 | 60.4019 | -61.9858 | 0.37537
989.7344 | 123.0377 | -60.5896 | 62.2925 | 0.21907 | 0.021016 | 0.020854 | 0.0090434 | 0.0061747 | -0.00052895 | -0.0019225 | -60.5713 | 62.3657 | -60.9329 | -0.050354 | -0.059509 | -0.09613 | -0.013733 | 0.086975 | 0.20142 | -0.32959 | -0.34332 | 0.073243 | 0.018311 | 60.5392 | -62.352 | 60.26 | -62.0911 | 0.36163
990.7656 | 123.1338 | -60.5392 | 62.2513 | -0.0021797 | 0.016103 | 0.01594 | -0.0035604 | 0.0021159 | -0.00052895 | 0.00064087 | -60.5621 | 62.2742 | -60.9238 | 0.064087 | 0.082397 | 0.10071 | -0.068665 | 0.31586 | 0.20142 | -0.2243 | -0.38452 | 0.022888 | -0.022888 | 60.6033 | -62.1689 | 60.3149 | -62.0499 | 0.36163
991.7344 | 123.0377 | -60.6171 | 62.2421 | 0.27248 | 0.020803 | 0.01594 | 0.0066936 | 0.0010477 | -0.0011698 | 0.0017091 | -60.5484 | 62.3795 | -60.9695 | -0.14191 | -0.054932 | 0.13275 | -0.004578 | 0.036621 | 0.21057 | -0.3479 | -0.35248 | 0.13733 | 0.068664 | 60.4752 | -62.2971 | 60.2692 | -62.0316 | 0.42114
992.7656 | 123.111 | -60.5576 | 62.2467 | 0.035967 | 0.015462 | 0.019358 | -0.0027058 | -0.00087492 | -0.00031535 | 6.6667e-08 | -60.585 | 62.2696 | -60.9238 | 0.054932 | 0.073242 | 0.086975 | -0.050354 | 0.29755 | 0.21057 | -0.25635 | -0.36621 | 0.022888 | -0.027466 | 60.6125 | -62.1735 | 60.3012 | -62.0361 | 0.33874
993.7344 | 123.0377 | -60.6125 | 62.2742 | 0.10463 | 0.020803 | 0.017649 | 0.0090434 | 0.0029705 | -0.00031535 | 0.00042727 | -60.5209 | 62.3795 | -60.9238 | -0.013733 | -0.050354 | -0.068665 | 0.018311 | 0.12817 | 0.2243 | -0.32044 | -0.31128 | 0.10529 | 0.091553 | 60.5988 | -62.3245 | 60.2921 | -62.0499 | 0.40283
994.75 | 123.1293 | -60.5804 | 62.233 | 0.18093 | 0.018453 | 0.016154 | 7.12e-05 | 0.0036113 | -0.00095615 | 6.6667e-08 | -60.5301 | 62.2467 | -60.9192 | 0.032043 | 0.032043 | 0.018311 | -0.16479 | 0.20599 | 0.17395 | -0.35706 | -0.33875 | 0.013733 | 0.050354 | 60.6125 | -62.2009 | 60.2234 | -62.059 | 0.3891
995.7344 | 123.0103 | -60.6033 | 62.2742 | 0.14278 | 0.01888 | 0.021281 | 0.007548 | 0.0025431 | 0.00032545 | 0.00021367 | -60.5576 | 62.3886 | -60.9512 | -0.073242 | -0.09613 | -0.11444 | 0.004578 | 0.082397 | 0.20599 | -0.3479 | -0.3479 | 0.11444 | 0.045777 | 60.5301 | -62.3703 | 60.2554 | -62.0682 | 0.39368
996.7656 | 123.0652 | -60.553 | 62.2742 | -0.17003 | 0.016958 | 0.018504 | 0.0009258 | 0.0023295 | -0.002238 | -0.0014953 | -60.5164 | 62.3154 | -60.8963 | 0.082397 | 0.082397 | 0.1236 | 0.059509 | 0.32959 | 0.2655 | -0.20142 | -0.34332 | 0.041199 | 0.036622 | 60.6354 | -62.1918 | 60.3516 | -62.0087 | 0.37994
997.7344 | 123.0286 | -60.585 | 62.265 | 0.13515 | 0.022725 | 0.01829 | 0.0096842 | 0.0033977 | -0.0020244 | -0.00042733 | -60.5347 | 62.4023 | -60.9192 | -0.036621 | -0.059509 | -0.07782 | 0.004578 | 0.068665 | 0.21515 | -0.33875 | -0.33417 | 0.13733 | 0.050354 | 60.5484 | -62.3245 | 60.2463 | -62.0499 | 0.38452
998.7656 | 123.1293 | -60.5621 | 62.2604 | 0.0054493 | 0.015035 | 0.015299 | -0.0044148 | -0.00066112 | 0.00096645 | 0.00042727 | -60.5713 | 62.265 | -60.9283 | 0.032043 | 0.059509 | 0.054932 | -0.073242 | 0.27924 | 0.21515 | -0.24261 | -0.36621 | 0.004578 | -0.009155 | 60.5942 | -62.2009 | 60.3195 | -62.0453 | 0.35706
999.7344 | 123.0057 | -60.585 | 62.3016 | 0.074114 | 0.022085 | 0.019999 | 0.01182 | 0.0014751 | -0.0013834 | 0.00085447 | -60.5347 | 62.3932 | -60.9146 | -0.027466 | -0.050354 | -0.064087 | 0.036621 | 0.14648 | 0.21973 | -0.31586 | -0.32959 | 0.091552 | 0.050354 | 60.5576 | -62.352 | 60.2692 | -62.0819 | 0.37994
1000.7656 | 123.0377 | -60.5804 | 62.2925 | 0.24196 | 0.021444 | 0.015513 | 0.007548 | 0.0098063 | -0.00052895 | -0.0032043 | -60.5576 | 62.3703 | -60.9375 | 0.31586 | 0.22888 | -0.20142 | -0.018311 | 0.27466 | 0.20599 | -0.33875 | -0.35706 | 0.07782 | 0.022888 | 60.8963 | -62.0636 | 60.2417 | -62.0865 | 0.37994
1001.7344 | 123.1155 | -60.5713 | 62.2421 | 0.18093 | 0.016317 | 0.019572 | -0.0001424 | 0.0031841 | -0.0015972 | 6.6667e-08 | -60.5301 | 62.265 | -60.9375 | 0.004578 | 0.036621 | 0.013733 | -0.11444 | 0.19226 | 0.18768 | -0.31128 | -0.36621 | 0.022889 | 0.041199 | 60.5759 | -62.2055 | 60.26 | -62.0544 | 0.40741
1002.7656 | 123.1247 | -60.5347 | 62.2742 | 0.066485 | 0.016317 | 0.012736 | -0.0029196 | 0.0010477 | -0.00095615 | 6.6667e-08 | -60.5484 | 62.2833 | -60.91 | 0.054932 | 0.064087 | 0.082397 | -0.064087 | 0.3067 | 0.21057 | -0.24719 | -0.37537 | 0.009155 | -0.013733 | 60.5896 | -62.2101 | 60.2875 | -62.0636 | 0.36163
1003.7344 | 123.0103 | -60.5988 | 62.3016 | 0.10463 | 0.020803 | 0.019786 | 0.0081888 | 0.0031841 | -0.00052895 | -0.0017089 | -60.5026 | 62.384 | -60.91 | -0.027466 | -0.068665 | -0.07782 | 0 | 0.1236 | 0.22888 | -0.32044 | -0.31128 | 0.082397 | 0.09613 | 60.5713 | -62.3703 | 60.2783 | -62.0728 | 0.40741
1004.7656 | 123.143 | -60.5209 | 62.265 | -0.063215 | 0.017171 | 0.015727 | -0.0001424 | 0.0010477 | -0.0011698 | -0.0023499 | -60.498 | 62.3016 | -60.8688 | 0.086975 | 0.10986 | 0.1236 | -0.018311 | 0.35248 | 0.24261 | -0.20599 | -0.3479 | 0.036621 | 0.022888 | 60.6079 | -62.1552 | 60.3149 | -62.0224 | 0.37079
1005.7344 | 123.0011 | -60.5759 | 62.2971 | 0.18093 | 0.022085 | 0.016154 | 0.007548 | 0.0019023 | -0.0015972 | 0.0010681 | -60.5392 | 62.4023 | -60.9329 | -0.073242 | -0.07782 | -0.09613 | -0.013733 | 0.086975 | 0.19684 | -0.33875 | -0.35705 | 0.10529 | 0.036621 | 60.5026 | -62.3749 | 60.2371 | -62.1002 | 0.39368
1006.7656 | 123.0743 | -60.5255 | 62.2925 | -0.20054 | 0.01653 | 0.020426 | 0.000712 | 0.0016887 | -0.002238 | -0.00085453 | -60.4935 | 62.3245 | -60.91 | 0.082397 | 0.07782 | 0.11902 | 0.068665 | 0.32501 | 0.27008 | -0.20599 | -0.38452 | 0.032044 | 0.032044 | 60.6079 | -62.2147 | 60.3195 | -62.0224 | 0.41657
1007.7344 | 123.0515 | -60.553 | 62.2833 | 0.035967 | 0.019094 | 0.019786 | 0.009257 | 0.0038249 | -0.0011698 | -0.0027771 | -60.4568 | 62.4023 | -60.8963 | 0.022888 | -0.018311 | -0.027466 | -0.009155 | 0.17395 | 0.22888 | -0.29297 | -0.34332 | 0.11902 | 0.096131 | 60.5759 | -62.3016 | 60.26 | -62.0544 | 0.43945
1008.7656 | 123.1338 | -60.5301 | 62.2696 | 0.44795 | 0.01653 | 0.012309 | -0.002065 | 0.0010477 | -0.00010175 | 0.00021367 | -60.585 | 62.2925 | -60.9055 | 0.027466 | 0.064087 | 0.064087 | -0.059509 | 0.26093 | 0.21515 | -0.27008 | -0.37537 | 0.022888 | -0.054932 | 60.5576 | -62.2055 | 60.26 | -62.0544 | 0.32043
1009.7344 | 123.0103 | -60.5896 | 62.2879 | 0.11989 | 0.023366 | 0.016581 | 0.0094706 | 0.0027567 | -0.00031535 | -0.00042733 | -60.466 | 62.4298 | -60.8917 | -0.004578 | -0.045776 | -0.036621 | 0.027466 | 0.13733 | 0.23346 | -0.32501 | -0.30212 | 0.14191 | 0.1236 | 60.585 | -62.3337 | 60.2646 | -62.0544 | 0.42572
1010.7656 | 123.1155 | -60.5347 | 62.2833 | 0.2267 | 0.019307 | 0.018504 | 7.12e-05 | 0.0033977 | -0.00095615 | 0.0014953 | -60.5072 | 62.2971 | -60.9238 | 0.032043 | 0.050354 | 0.032043 | -0.17395 | 0.23346 | 0.18768 | -0.33875 | -0.3891 | 0.013733 | 0.027466 | 60.5667 | -62.233 | 60.1959 | -62.0956 | 0.41656
1011.7344 | 123.0972 | -60.5484 | 62.2696 | 0.20381 | 0.016103 | 0.016795 | 7.12e-05 | 0.0010477 | -0.00010175 | 6.6667e-08 | -60.5072 | 62.3199 | -60.8963 | 0.013733 | 0.013733 | 0.027466 | -0.16022 | 0.20142 | 0.16022 | -0.34332 | -0.3479 | 0.050354 | 0.041199 | 60.5621 | -62.2559 | 60.2051 | -62.1094 | 0.3891
1012.7656 | 123.0972 | -60.5392 | 62.2742 | 0.18855 | 0.016744 | 0.018077 | 0.002421 | 0.00083408 | 0.00053925 | -0.00042733 | -60.5118 | 62.3062 | -60.8917 | 0.009155 | 0.009155 | 0.009155 | -0.13733 | 0.20142 | 0.17853 | -0.32044 | -0.35248 | 0.032043 | 0.027466 | 60.5484 | -62.265 | 60.2188 | -62.0956 | 0.37994
1013.7344 | 123.056 | -60.5347 | 62.3154 | 0.028338 | 0.021657 | 0.015299 | 0.010539 | 0.00040688 | -0.00052895 | -0.00042733 | -60.5209 | 62.3932 | -60.8963 | 0.032043 | 0.004578 | 0.009155 | 0.027466 | 0.20599 | 0.23804 | -0.27924 | -0.36163 | 0.077819 | 0.013733 | 60.5667 | -62.3108 | 60.2554 | -62.0773 | 0.37537
1014.7656 | 123.0972 | -60.5392 | 62.2742 | 0.081743 | 0.018453 | 0.014445 | -0.002065 | 0.00019328 | -0.00074255 | -0.0014953 | -60.5347 | 62.2879 | -60.9009 | 0.19226 | 0.14648 | -0.045776 | -0.14648 | 0.19226 | 0.21057 | -0.25635 | -0.36163 | 0.013733 | 0.004578 | 60.7315 | -62.1277 | 60.2829 | -62.0636 | 0.36621
1015.7344 | 123.0515 | -60.553 | 62.3245 | 0.020708 | 0.021444 | 0.021281 | 0.0081888 | 0.0023295 | -0.00095615 | 6.6667e-08 | -60.4568 | 62.439 | -60.9009 | 0.009155 | -0.022888 | -0.018311 | 0.018311 | 0.16937 | 0.21057 | -0.29755 | -0.3479 | 0.11444 | 0.096131 | 60.5621 | -62.3474 | 60.2554 | -62.114 | 0.44403
1016.7656 | 123.1338 | -60.5255 | 62.2925 | 0.020708 | 0.015462 | 0.010386 | -0.0009968 | 0.0025431 | -0.002238 | 0.00064087 | -60.5301 | 62.3016 | -60.9055 | 0.045776 | 0.064087 | 0.086975 | -0.045776 | 0.29297 | 0.21973 | -0.24719 | -0.37994 | 0.009156 | -0.004577 | 60.5713 | -62.2284 | 60.2783 | -62.0728 | 0.37537
1017.7344 | 123.056 | -60.5667 | 62.3154 | -0.14714 | 0.020803 | 0.017649 | 0.0086162 | 0.0033977 | -0.00052895 | -0.0012817 | -60.4202 | 62.4207 | -60.8688 | 0.036621 | -0.004578 | 0 | 0.022888 | 0.19684 | 0.22888 | -0.29297 | -0.30212 | 0.10529 | 0.14648 | 60.6033 | -62.3199 | 60.2737 | -62.0865 | 0.44861
1018.7656 | 123.1338 | -60.5118 | 62.3062 | 0.043596 | 0.018239 | 0.015513 | -0.0007832 | 0.0019023 | -0.0011698 | 0.0010681 | -60.5438 | 62.3016 | -60.8963 | 0.013733 | 0.059509 | 0.059509 | -0.10986 | 0.24719 | 0.18768 | -0.26093 | -0.38452 | -0.004577 | -0.032043 | 60.5255 | -62.2467 | 60.2509 | -62.1185 | 0.35248
1019.7344 | 123.0515 | -60.5392 | 62.3245 | 0.11226 | 0.020803 | 0.015513 | 0.0081888 | 0.0048931 | -0.0020244 | -0.0023499 | -60.4385 | 62.4252 | -60.878 | 0.009155 | -0.036621 | -0.045776 | 0.022888 | 0.15106 | 0.20599 | -0.31586 | -0.33875 | 0.10071 | 0.10071 | 60.5484 | -62.3611 | 60.2234 | -62.1185 | 0.43945
1020.7656 | 123.1384 | -60.5347 | 62.2971 | 0.089373 | 0.017812 | 0.015513 | -0.0029196 | 0.00083408 | -0.002238 | -0.00042733 | -60.5392 | 62.2925 | -60.8917 | 0.018311 | 0.036621 | 0.041199 | -0.068665 | 0.24719 | 0.19684 | -0.25177 | -0.35706 | -0.004578 | -0.004578 | 60.553 | -62.2604 | 60.2829 | -62.1002 | 0.35248
1021.7344 | 123.0698 | -60.5576 | 62.3062 | -0.025068 | 0.021871 | 0.014872 | 0.010112 | 0.0016887 | 0.00032545 | -0.0012817 | -60.434 | 62.4252 | -60.8688 | 0.050354 | 0.027466 | 0.032043 | 0.009155 | 0.22888 | 0.22888 | -0.27924 | -0.31128 | 0.11902 | 0.1236 | 60.6079 | -62.2787 | 60.2783 | -62.0773 | 0.43487
1022.7656 | 123.1155 | -60.5118 | 62.3016 | -0.17766 | 0.016103 | 0.017222 | -0.0027058 | 0.0016887 | 0.00118 | 0.00042727 | -60.466 | 62.3245 | -60.878 | 0.11902 | 0.1236 | 0.16937 | -0.045776 | 0.36621 | 0.23804 | -0.20142 | -0.36621 | 0.022888 | 0.045777 | 60.6308 | -62.178 | 60.3104 | -62.0636 | 0.41199
1023.7344 | 123.0606 | -60.5209 | 62.3199 | -0.093733 | 0.021871 | 0.019145 | 0.009257 | 0.0042521 | -0.0026652 | 0.00064087 | -60.4111 | 62.4252 | -60.8917 | 0.032043 | 0.009155 | 0.004578 | 0.027466 | 0.20142 | 0.23804 | -0.28839 | -0.37079 | 0.10529 | 0.10986 | 60.553 | -62.3108 | 60.2325 | -62.0819 | 0.48065
1024.7656 | 123.0927 | -60.5301 | 62.2879 | 0.15041 | 0.016958 | 0.018931 | -0.0029196 | 0.0033977 | -0.00052895 | 6.6667e-08 | -60.498 | 62.3062 | -60.8963 | 0 | 0.018311 | 0.050354 | -0.068665 | 0.22888 | 0.20142 | -0.27924 | -0.36621 | 0.01831 | 0.032043 | 60.5301 | -62.2696 | 60.2509 | -62.0865 | 0.39825
1025.7344 | 123.0698 | -60.5255 | 62.3337 | 0.035967 | 0.021871 | 0.017436 | 0.00648 | 0.0046793 | -0.00095615 | -0.0027771 | -60.4111 | 62.4069 | -60.8688 | 0.10986 | 0.036621 | 0.045776 | 0.027466 | 0.20599 | 0.25177 | -0.30212 | -0.34332 | 0.073242 | 0.11444 | 60.6354 | -62.2971 | 60.2234 | -62.0819 | 0.45776
1026.7656 | 123.0927 | -60.5301 | 62.2879 | 0.16567 | 0.017171 | 0.014231 | -0.0016378 | 0.0021159 | -0.00010175 | 6.6667e-08 | -60.5164 | 62.3016 | -60.9009 | 0 | 0.032043 | 0.027466 | -0.086975 | 0.21973 | 0.18768 | -0.30212 | -0.37079 | 0.013733 | 0.013733 | 60.5301 | -62.2559 | 60.228 | -62.1002 | 0.38452
1027.7344 | 123.0652 | -60.5209 | 62.3474 | -0.13188 | 0.018667 | 0.020426 | 0.0071208 | 0.0025431 | -0.0024516 | -0.0034179 | -60.4111 | 62.4344 | -60.8597 | 0.082397 | 0.050354 | 0.064087 | 0.041199 | 0.25635 | 0.27008 | -0.26093 | -0.33874 | 0.086975 | 0.10986 | 60.6033 | -62.2971 | 60.26 | -62.0773 | 0.44861
1028.7656 | 123.0881 | -60.4935 | 62.2879 | 0.21144 | 0.018453 | 0.015299 | -0.0007832 | 0.0029705 | 0.00053925 | 0.0023499 | -60.4889 | 62.2879 | -60.8688 | 0.004578 | 0.018311 | 0.018311 | -0.1236 | 0.18768 | 0.1831 | -0.30212 | -0.37537 | 0 | 0.004577 | 60.498 | -62.2696 | 60.1913 | -62.1048 | 0.37994
1029.7344 | 123.0652 | -60.5255 | 62.3108 | -0.0098092 | 0.022939 | 0.019145 | 0.0071208 | 0.0029705 | 0.00053925 | -0.00085453 | -60.4202 | 62.4435 | -60.8643 | 0.054932 | 0.027466 | 0.036621 | 0.022888 | 0.21057 | 0.26093 | -0.27924 | -0.33875 | 0.13275 | 0.10529 | 60.5804 | -62.2833 | 60.2463 | -62.0499 | 0.44403
1030.7656 | 123.1522 | -60.4614 | 62.3062 | -0.040327 | 0.016744 | 0.014872 | -0.0033468 | 0.0010477 | 0.00053925 | 6.6667e-08 | -60.466 | 62.2833 | -60.8688 | 0.09613 | 0.10986 | 0.11902 | -0.064087 | 0.33875 | 0.21515 | -0.2243 | -0.40741 | -0.022888 | -0.004577 | 60.5576 | -62.1964 | 60.2371 | -62.0911 | 0.40283
1031.7344 | 123.0743 | -60.5392 | 62.3245 | -0.032697 | 0.021444 | 0.019145 | 0.0084026 | 0.0027567 | -0.0026652 | -0.00021353 | -60.4248 | 62.4207 | -60.8551 | 0.045776 | 0.027466 | 0.036621 | 0.032043 | 0.22888 | 0.25635 | -0.27008 | -0.31586 | 0.09613 | 0.11444 | 60.585 | -62.2971 | 60.2692 | -62.0682 | 0.4303
1032.75 | 123.1018 | -60.4843 | 62.2925 | 0.23433 | 0.018667 | 0.017008 | 0.002421 | 0.0033977 | -0.0011698 | 0.00021367 | -60.4019 | 62.3291 | -60.8688 | 0.022888 | 0.36621 | 0.27466 | -0.27924 | 0.24719 | 0.14648 | -0.39825 | -0.38452 | 0.036622 | 0.082397 | 60.5072 | -61.9263 | 60.0861 | -62.146 | 0.46692
1033.7344 | 123.0469 | -60.5164 | 62.3428 | -0.13951 | 0.019948 | 0.015299 | 0.0077616 | 0.0031841 | -0.00010175 | 6.6667e-08 | -60.3973 | 62.4619 | -60.8414 | 0.068665 | 0.036621 | 0.018311 | 0.036621 | 0.24719 | 0.24719 | -0.28839 | -0.32501 | 0.11902 | 0.11902 | 60.585 | -62.3062 | 60.228 | -62.0956 | 0.44403
1034.7656 | 123.1155 | -60.5026 | 62.2696 | 0.21144 | 0.019735 | 0.015299 | 0.0028484 | -0.00023392 | -0.00095615 | 0.0014953 | -60.4568 | 62.3291 | -60.8826 | 0.022888 | 0.045776 | 0.050354 | -0.16479 | 0.21515 | 0.19226 | -0.33417 | -0.37994 | 0.05951 | 0.045777 | 60.5255 | -62.2238 | 60.1685 | -62.0773 | 0.42572
1035.7344 | 123.0286 | -60.5209 | 62.3474 | 0.074114 | 0.021871 | 0.017863 | 0.0079752 | 0.00019328 | -0.00052895 | -0.0010681 | -60.4385 | 62.4619 | -60.8871 | -0.009155 | -0.036621 | -0.032043 | 0.013733 | 0.13733 | 0.2243 | -0.30212 | -0.36621 | 0.11444 | 0.082397 | 60.5118 | -62.384 | 60.2188 | -62.1231 | 0.44861
1036.7656 | 123.1796 | -60.4797 | 62.3108 | -0.055586 | 0.014821 | 0.012309 | -0.0035604 | 0.0027567 | 0.00011185 | 6.6667e-08 | -60.4477 | 62.3337 | -60.8643 | 0.11902 | 0.14648 | 0.1831 | -0.050354 | 0.38452 | 0.23346 | -0.18768 | -0.38452 | 0.022888 | 0.032043 | 60.5988 | -62.1643 | 60.2921 | -62.0773 | 0.41656
1037.7344 | 123.0331 | -60.5347 | 62.3337 | 0.020708 | 0.020803 | 0.018504 | 0.0077616 | 0.0023295 | -0.00010175 | 0.00064087 | -60.434 | 62.4252 | -60.8505 | -0.004578 | -0.032043 | -0.045776 | 0.027466 | 0.16022 | 0.2243 | -0.31586 | -0.31586 | 0.091553 | 0.10071 | 60.5301 | -62.3657 | 60.2188 | -62.1094 | 0.41656
1038.75 | 123.143 | -60.4843 | 62.2787 | 0.24959 | 0.01888 | 0.016154 | 0.0032756 | 0.0036113 | -0.0030924 | -0.0012817 | -60.3928 | 62.3474 | -60.878 | 0.041199 | 0.041199 | 0.050354 | -0.18768 | 0.23346 | 0.15564 | -0.36163 | -0.39368 | 0.068664 | 0.091553 | 60.5255 | -62.2375 | 60.1227 | -62.1231 | 0.48523
1039.7344 | 123.0011 | -60.5392 | 62.3016 | 0.13515 | 0.020803 | 0.019358 | 0.0077616 | 0.0033977 | -0.0018108 | -0.0027771 | -60.4523 | 62.4573 | -60.878 | -0.032043 | -0.036621 | -0.082397 | 0.018311 | 0.09613 | 0.21973 | -0.36621 | -0.33875 | 0.15564 | 0.086975 | 60.5072 | -62.3383 | 60.173 | -62.0819 | 0.42572
1040.7656 | 123.1934 | -60.4752 | 62.3016 | -0.15477 | 0.016317 | 0.01359 | -0.0031332 | 0.0014751 | 0.00032545 | 0.0019227 | -60.4248 | 62.3428 | -60.8505 | 0.086975 | 0.10986 | 0.46234 | 0.63171 | 0.29755 | 0.2655 | -0.16937 | -0.37537 | 0.041198 | 0.050354 | 60.5621 | -62.1918 | 60.3058 | -62.0361 | 0.42572
1041.7344 | 123.056 | -60.498 | 62.3657 | 0.0054493 | 0.020803 | 0.016154 | 0.010112 | 0.0027567 | -0.0028788 | -0.00042733 | -60.3836 | 62.439 | -60.8231 | 0.022888 | 0 | -0.009155 | 0.018311 | 0.16022 | 0.22888 | -0.28381 | -0.32501 | 0.073242 | 0.11444 | 60.5209 | -62.3657 | 60.2142 | -62.1368 | 0.43945
1042.7656 | 123.0972 | -60.4843 | 62.3199 | 0.081743 | 0.015676 | 0.014231 | -0.0029196 | 0.0036113 | -0.00031535 | -0.00021353 | -60.4752 | 62.3474 | -60.8597 | 0.018311 | 0.041199 | 0.027466 | -0.073242 | 0.21057 | 0.20599 | -0.27466 | -0.37537 | 0.027466 | 0.009155 | 60.5026 | -62.2787 | 60.2097 | -62.114 | 0.38452
1043.7344 | 123.024 | -60.5072 | 62.352 | 0.081743 | 0.020803 | 0.017436 | 0.0084026 | 0.0010477 | -0.0020244 | -0.0027771 | -60.4202 | 62.4435 | -60.8597 | -0.027466 | -0.050354 | -0.054932 | 0.027466 | 0.14191 | 0.21515 | -0.32501 | -0.35248 | 0.091552 | 0.086975 | 60.4797 | -62.4023 | 60.1822 | -62.1368 | 0.43945
1044.7656 | 122.9874 | -60.5347 | 62.3337 | 0.1733 | 0.021657 | 0.021281 | 0.0084026 | 0.0036113 | -0.0024516 | 0.00064087 | -60.4614 | 62.4619 | -60.8643 | -0.064087 | -0.07782 | -0.11444 | 0.004578 | 0.068665 | 0.20599 | -0.3479 | -0.32959 | 0.12817 | 0.073242 | 60.4706 | -62.4115 | 60.1868 | -62.1277 | 0.40283
1045.7344 | 123.0423 | -60.5392 | 62.3428 | 0.081743 | 0.019735 | 0.022135 | 0.0081888 | 0.0046793 | -0.0018108 | 0.00064087 | -60.3973 | 62.4573 | -60.8414 | -0.018311 | -0.032043 | -0.036621 | 0.036621 | 0.15564 | 0.2243 | -0.31586 | -0.30212 | 0.11444 | 0.14191 | 60.5209 | -62.3749 | 60.2234 | -62.1185 | 0.44403
1046.7656 | 123.1155 | -60.466 | 62.3566 | 0.11226 | 0.015676 | 0.013804 | -0.0022786 | 0.0042521 | -0.00074255 | -0.0021361 | -60.3973 | 62.3566 | -60.8368 | 0.13275 | 0.13733 | 0.13275 | 0 | 0.35248 | 0.24261 | -0.21973 | -0.37079 | 0 | 0.068664 | 60.5988 | -62.2192 | 60.2463 | -62.114 | 0.43945
1047.7344 | 123.0331 | -60.5118 | 62.3199 | 0.043596 | 0.019307 | 0.019572 | 0.0069072 | 0.0040385 | -0.0018108 | -0.00085453 | -60.4019 | 62.4619 | -60.8322 | -0.004578 | -0.036621 | -0.041199 | 0.022888 | 0.16937 | 0.2243 | -0.3067 | -0.32043 | 0.14191 | 0.10986 | 60.5072 | -62.3566 | 60.2051 | -62.0956 | 0.4303
1048.75 | 123.1476 | -60.4935 | 62.352 | 0.035967 | 0.018453 | 0.014872 | -0.0044148 | 0.0025431 | -0.0020244 | 0.0012817 | -60.4523 | 62.3611 | -60.8505 | 0.018311 | 0.068665 | 0.091553 | -0.041199 | 0.29297 | 0.21515 | -0.2655 | -0.35706 | 0.009155 | 0.041198 | 60.5118 | -62.2833 | 60.228 | -62.1368 | 0.39825
1049.7344 | 123.0469 | -60.5301 | 62.3795 | 0.21907 | 0.022298 | 0.022135 | 0.0081888 | -0.00066112 | 0.00096645 | 0.00085447 | -60.434 | 62.4619 | -60.8551 | -0.1236 | -0.07782 | 0.10529 | 0.022888 | 0.041199 | 0.21973 | -0.31586 | -0.32501 | 0.082397 | 0.09613 | 60.4065 | -62.4573 | 60.2142 | -62.1597 | 0.42114
1050.75 | 123.1155 | -60.4752 | 62.3016 | 0.24959 | 0.016317 | 0.016368 | 0.0004984 | 0.0014751 | 0.00096645 | -0.00021353 | -60.3882 | 62.3657 | -60.8551 | 0.027466 | 0.036621 | 0.032043 | -0.16479 | 0.23346 | 0.15564 | -0.3479 | -0.37994 | 0.064087 | 0.086975 | 60.5026 | -62.265 | 60.1273 | -62.146 | 0.46692
1051.7344 | 123.0103 | -60.498 | 62.3703 | 0.23433 | 0.020162 | 0.018077 | 0.0084026 | 0.0040385 | 0.0013936 | 0.0019227 | -60.4385 | 62.4527 | -60.8826 | -0.045776 | -0.064087 | -0.6134 | -0.55389 | 0.39368 | 0.17395 | -0.41657 | -0.38452 | 0.082398 | 0.059509 | 60.4523 | -62.4344 | 60.0815 | -62.1964 | 0.44403
1052.75 | 123.1567 | -60.4614 | 62.3199 | 0.1733 | 0.017385 | 0.021281 | 0.0037028 | 0.0046793 | -0.0011698 | -0.0017089 | -60.3928 | 62.3932 | -60.8505 | 0.022888 | 0.032043 | 0.027466 | -0.17853 | 0.21057 | 0.14191 | -0.36163 | -0.3891 | 0.073242 | 0.068665 | 60.4843 | -62.2879 | 60.0998 | -62.178 | 0.45776
1053.7344 | 123.0423 | -60.5118 | 62.3291 | 0.24196 | 0.019735 | 0.021708 | 0.0073344 | 0.00083408 | -0.00031535 | 0.00064087 | -60.4523 | 62.4435 | -60.8597 | -0.054932 | -0.050354 | -0.073242 | -0.068665 | 0.10986 | 0.1831 | -0.36163 | -0.3479 | 0.11444 | 0.059509 | 60.4568 | -62.3795 | 60.1501 | -62.146 | 0.40741
1054.7656 | 123.0606 | -60.4752 | 62.384 | -0.24632 | 0.017598 | 0.015086 | 0.0009258 | 0.0014751 | -0.0015972 | 0.0014953 | -60.4065 | 62.4023 | -60.8459 | 0.054932 | 0.059509 | 0.082397 | 0.091553 | 0.28839 | 0.27924 | -0.2243 | -0.37079 | 0.018311 | 0.068665 | 60.5301 | -62.3245 | 60.2509 | -62.1048 | 0.43945
1055.7344 | 123.0331 | -60.5026 | 62.352 | 0.066485 | 0.021657 | 0.018077 | 0.007548 | 0.0016887 | -0.00010175 | -0.00064093 | -60.3745 | 62.4756 | -60.8276 | -0.009155 | -0.032043 | -0.036621 | 0.018311 | 0.16479 | 0.22888 | -0.32044 | -0.32501 | 0.1236 | 0.12817 | 60.4935 | -62.384 | 60.1822 | -62.1231 | 0.45319
1056.7656 | 123.0881 | -60.434 | 62.384 | -0.18529 | 0.016317 | 0.013804 | -0.0007832 | -0.00044752 | -0.0024516 | -0.0012817 | -60.3836 | 62.3749 | -60.8231 | 0.086975 | 0.091553 | 0.1236 | 0.064087 | 0.32959 | 0.25177 | -0.20599 | -0.3891 | -0.009155 | 0.050354 | 60.5209 | -62.2925 | 60.228 | -62.1323 | 0.43945
1057.7344 | 123.0331 | -60.5118 | 62.3657 | 0.058855 | 0.02123 | 0.019358 | 0.009257 | 0.0031841 | 0.00011185 | -0.0032043 | -60.3928 | 62.4847 | -60.8459 | -0.032043 | -0.064087 | -0.064087 | 0.018311 | 0.10986 | 0.22888 | -0.32501 | -0.33417 | 0.11902 | 0.11902 | 60.4797 | -62.4298 | 60.1868 | -62.1368 | 0.45319
1058.7656 | 123.056 | -60.5209 | 62.3795 | 0.051226 | 0.020589 | 0.017008 | 0.005839 | 0.0048931 | -0.00052895 | -0.0012817 | -60.379 | 62.471 | -60.8231 | -0.013733 | -0.027466 | -0.018311 | 0.009155 | 0.14648 | 0.2243 | -0.31128 | -0.30212 | 0.091552 | 0.14191 | 60.5072 | -62.4069 | 60.2097 | -62.1552 | 0.44403
1059.7344 | 123.0423 | -60.5118 | 62.3611 | 0.097002 | 0.023366 | 0.02064 | 0.0062662 | 0.0053203 | 0.00053925 | -0.00042733 | -60.3836 | 62.471 | -60.8643 | -0.027466 | -0.022888 | -0.036621 | 0.013733 | 0.14191 | 0.23346 | -0.32044 | -0.35248 | 0.10986 | 0.12817 | 60.4843 | -62.384 | 60.1913 | -62.1277 | 0.48065
1060.7656 | 123.1476 | -60.4294 | 62.352 | 0.11989 | 0.018026 | 0.01594 | -0.0046284 | 0.00062048 | -0.00052895 | -0.0014953 | -60.4477 | 62.3611 | -60.8459 | 0.022888 | 0.054932 | 0.041199 | -0.064087 | 0.23346 | 0.20599 | -0.27924 | -0.41657 | 0.009155 | -0.018311 | 60.4523 | -62.2971 | 60.1501 | -62.146 | 0.39825
1061.7344 | 123.0515 | -60.4797 | 62.3795 | 0.051226 | 0.021657 | 0.016795 | 0.0084026 | 0.0021159 | -0.0011698 | 6.6667e-08 | -60.3424 | 62.4847 | -60.8139 | 0.032043 | 0 | 0.013733 | 0.022888 | 0.21057 | 0.2243 | -0.28839 | -0.33417 | 0.10529 | 0.13733 | 60.5118 | -62.3795 | 60.1913 | -62.1552 | 0.4715
1062.7656 | 123.0057 | -60.5072 | 62.3886 | 0.14278 | 0.019735 | 0.017863 | 0.0066936 | 0.0063883 | 0.00096645 | -0.00021353 | -60.4156 | 62.4756 | -60.8459 | -0.073242 | -0.07782 | -0.086975 | 0.032043 | 0.073242 | 0.2243 | -0.35248 | -0.33875 | 0.086975 | 0.091553 | 60.434 | -62.4664 | 60.1547 | -62.1643 | 0.4303
1063.7344 | 123.024 | -60.466 | 62.3795 | 0.058855 | 0.020376 | 0.019786 | 0.0043436 | 0.0053203 | -0.0011698 | 0.00042727 | -60.3699 | 62.4893 | -60.8368 | -0.009155 | -0.018311 | -0.041199 | 0.041199 | 0.16937 | 0.21057 | -0.30212 | -0.37079 | 0.10986 | 0.09613 | 60.4568 | -62.3978 | 60.1639 | -62.1689 | 0.46692
1064.7656 | 123.1567 | -60.4477 | 62.352 | -0.017439 | 0.016317 | 0.01295 | -0.0044148 | 0.0031841 | -0.0015972 | 0.0017091 | -60.3973 | 62.3749 | -60.8231 | 0.073242 | 0.12817 | 0.15564 | -0.073242 | 0.34332 | 0.21057 | -0.22888 | -0.37537 | 0.022888 | 0.050354 | 60.5209 | -62.2238 | 60.2188 | -62.1414 | 0.42572
1065.7344 | 123.0606 | -60.466 | 62.3932 | -0.28447 | 0.019948 | 0.020854 | 0.0077616 | 0.0038249 | -0.0015972 | 0.00042727 | -60.3378 | 62.4802 | -60.8139 | 0.022888 | 0.009155 | 0.009155 | 0.027466 | 0.20599 | 0.24261 | -0.30212 | -0.3479 | 0.086976 | 0.12817 | 60.4889 | -62.384 | 60.1639 | -62.1506 | 0.47607
1066.7656 | 123.1247 | -60.434 | 62.3474 | -0.017439 | 0.017812 | 0.012095 | -0.0033468 | 0.0029705 | 0.002248 | 0.0025635 | -60.3973 | 62.3749 | -60.8276 | 0.068665 | 0.091553 | 0.10071 | -0.07782 | 0.30212 | 0.21973 | -0.25177 | -0.39368 | 0.027466 | 0.036621 | 60.5026 | -62.2559 | 60.1822 | -62.1277 | 0.4303
1067.7344 | 123.1338 | -60.4294 | 62.3383 | 0.2267 | 0.019094 | 0.016368 | 0.00413 | 0.00062048 | -0.00074255 | -0.0014953 | -60.5164 | 62.3886 | -60.8368 | 0.018311 | 0.009155 | 0.09613 | -0.13733 | 0.19226 | 0.16937 | -0.31128 | -0.40741 | 0.050354 | -0.086975 | 60.4477 | -62.3291 | 60.1181 | -62.1689 | 0.32044
1068.7656 | 123.1522 | -60.4294 | 62.3611 | 0.86757 | 0.016744 | 0.018504 | 0.0026346 | 0.00083408 | 0.00011185 | -0.00021353 | -60.2417 | 62.3978 | -60.8047 | 0.068665 | 0.064087 | 0.004578 | -0.21515 | 0.2243 | 0.16479 | -0.29755 | -0.37537 | 0.036621 | 0.18768 | 60.498 | -62.2971 | 60.1318 | -62.1964 | 0.56305
1069.7344 | 123.0515 | -60.4523 | 62.3749 | -0.10899 | 0.021444 | 0.017863 | 0.0081888 | 0.00040688 | -0.0015972 | -0.0021361 | -60.3195 | 62.471 | -60.8002 | 0.064087 | 0.018311 | 0.018311 | 0.013733 | 0.23804 | 0.22888 | -0.27924 | -0.3479 | 0.09613 | 0.13275 | 60.5164 | -62.3566 | 60.173 | -62.146 | 0.48065
1070.7656 | 123.111 | -60.4385 | 62.352 | 0.27248 | 0.018026 | 0.017649 | 0.0011394 | 0.0027567 | -0.00095615 | 6.6667e-08 | -60.3653 | 62.3703 | -60.8093 | 0.036621 | 0.027466 | 0.036621 | -0.17395 | 0.21515 | 0.16937 | -0.32501 | -0.37079 | 0.01831 | 0.073243 | 60.4752 | -62.3245 | 60.1135 | -62.1826 | 0.44403
1071.7344 | 123.0743 | -60.4568 | 62.3978 | -0.0098092 | 0.021444 | 0.017222 | 0.0088298 | 0.0021159 | -0.0020244 | 0.00021367 | -60.3195 | 62.5031 | -60.8231 | 0.036621 | 0.013733 | 0.027466 | 0.018311 | 0.21515 | 0.25635 | -0.28839 | -0.36621 | 0.10529 | 0.13733 | 60.4935 | -62.384 | 60.1685 | -62.1414 | 0.50354
1072.7656 | 123.0835 | -60.4752 | 62.4069 | -0.10136 | 0.019307 | 0.016795 | 0.0062662 | 0.0033977 | -0.0024516 | -0.0017089 | -60.3333 | 62.5076 | -60.8231 | 0.050354 | 0.036621 | 0.041199 | 0.032043 | 0.23346 | 0.24261 | -0.26093 | -0.3479 | 0.10071 | 0.14191 | 60.5255 | -62.3703 | 60.2142 | -62.1643 | 0.48981
1073.7344 | 123.0927 | -60.4706 | 62.384 | -0.14714 | 0.020162 | 0.016368 | 0.0062662 | 0.0055339 | -0.0011698 | -0.0017089 | -60.3104 | 62.5122 | -60.8139 | 0.045776 | 0.045776 | 0.041199 | 0.041199 | 0.23346 | 0.24261 | -0.2655 | -0.34332 | 0.12817 | 0.16022 | 60.5164 | -62.3383 | 60.2051 | -62.1414 | 0.50354
1074.7656 | 123.1293 | -60.4385 | 62.3337 | 0.097002 | 0.015462 | 0.017649 | 0.0004984 | 0.0027567 | -0.00010175 | 6.6667e-08 | -60.3607 | 62.3795 | -60.8276 | 0.036621 | 0.050354 | 0.045776 | -0.16479 | 0.22888 | 0.17395 | -0.34332 | -0.3891 | 0.045777 | 0.07782 | 60.4752 | -62.2833 | 60.0952 | -62.1597 | 0.46692
1075.7344 | 123.0835 | -60.4568 | 62.4023 | -0.19291 | 0.019521 | 0.022135 | 0.0049846 | 0.0021159 | -0.0013834 | -0.00064093 | -60.3378 | 62.5305 | -60.8139 | 0.054932 | 0.045776 | 0.041199 | 0.07782 | 0.26093 | 0.27008 | -0.2243 | -0.35706 | 0.12817 | 0.11902 | 60.5118 | -62.3566 | 60.2325 | -62.1323 | 0.47607
1076.7656 | 123.143 | -60.4294 | 62.384 | -0.025068 | 0.016317 | 0.017222 | -0.0048422 | -0.00044752 | -0.00095615 | -0.0019225 | -60.3836 | 62.3795 | -60.8185 | 0.073242 | 0.091553 | 0.10071 | -0.068665 | 0.32959 | 0.2243 | -0.24719 | -0.3891 | -0.004577 | 0.045776 | 60.5026 | -62.2925 | 60.1822 | -62.1597 | 0.43487
1077.7344 | 123.1567 | -60.4294 | 62.3611 | 0.25722 | 0.019735 | 0.018717 | 0.004771 | 0.0023295 | -0.00052895 | -0.0010681 | -60.2875 | 62.4207 | -60.7727 | 0.032043 | 0.041199 | 0.018311 | -0.2243 | 0.21057 | 0.15564 | -0.36163 | -0.34332 | 0.059509 | 0.14191 | 60.4614 | -62.3199 | 60.0677 | -62.2055 | 0.48523
1078.75 | 123.1522 | -60.4111 | 62.3474 | 0.24196 | 0.019521 | 0.020854 | 0.002421 | 0.0051067 | -0.00031535 | -0.0034179 | -60.3104 | 62.4023 | -60.8093 | 0.24261 | 0.29755 | 0.032043 | -0.2243 | 0.32959 | 0.15564 | -0.37994 | -0.39825 | 0.054932 | 0.10071 | 60.6537 | -62.0499 | 60.0311 | -62.1918 | 0.49896
1079.7344 | 123.0698 | -60.4385 | 62.4161 | -0.14714 | 0.019521 | 0.021281 | 0.0051982 | 0.00019328 | -0.00074255 | 0.00021367 | -60.3424 | 62.4847 | -60.8231 | 0.045776 | 0.027466 | 0.045776 | 0.086975 | 0.27466 | 0.2655 | -0.2243 | -0.38452 | 0.068664 | 0.096131 | 60.4843 | -62.3886 | 60.2142 | -62.1506 | 0.48065
1080.7656 | 123.1796 | -60.4065 | 62.3474 | 0.25722 | 0.018453 | 0.017222 | 0.001353 | 0.0031841 | 0.00053925 | 6.6667e-08 | -60.3012 | 62.4115 | -60.8093 | 0.036621 | 0.050354 | 0.041199 | -0.39825 | -0.19684 | 0.13733 | -0.41199 | -0.40283 | 0.064087 | 0.10529 | 60.4431 | -62.2971 | 59.9945 | -62.2101 | 0.50812
1081.7344 | 123.0835 | -60.4431 | 62.4207 | -0.10899 | 0.01888 | 0.01829 | 0.0066936 | 0.0029705 | -0.002238 | 0.0017091 | -60.3195 | 62.5122 | -60.8047 | 0.064087 | 0.032043 | 0.045776 | 0.036621 | 0.24261 | 0.25635 | -0.25177 | -0.36163 | 0.091553 | 0.1236 | 60.5072 | -62.3886 | 60.1913 | -62.1643 | 0.48523
1082.7656 | 123.1384 | -60.4156 | 62.3749 | 0.23433 | 0.020376 | 0.016154 | 0.0015666 | 0.0046793 | 0.00053925 | -0.00042733 | -60.3012 | 62.4344 | -60.8185 | 0.036621 | 0.050354 | 0.018311 | -0.2243 | 0.21057 | 0.16479 | -0.36621 | -0.40283 | 0.059509 | 0.11444 | 60.4523 | -62.3245 | 60.0494 | -62.2101 | 0.51727
1083.7344 | 123.0011 | -60.4477 | 62.4252 | -0.17766 | 0.021657 | 0.014018 | 0.001353 | -0.00087492 | 0.00011185 | 0.0017091 | -60.3607 | 62.5259 | -60.8093 | -0.19226 | 0.009155 | 0.10071 | 0.009155 | 0.15106 | 0.27008 | -0.19684 | -0.36163 | 0.10071 | 0.086975 | 60.2554 | -62.4161 | 60.2509 | -62.1552 | 0.44861
1084.7656 | 123.1155 | -60.434 | 62.3657 | 0.14278 | 0.016744 | 0.014018 | -0.0016378 | 0.0021159 | 0.00011185 | -0.0012817 | -60.3928 | 62.3749 | -60.7864 | 0.009155 | 0.027466 | 0.013733 | -0.07782 | 0.21973 | 0.20142 | -0.27924 | -0.35248 | 0.009155 | 0.041199 | 60.4431 | -62.3383 | 60.1547 | -62.1643 | 0.39368
1085.7344 | 123.0698 | -60.4568 | 62.4481 | -0.3455 | 0.021657 | 0.015299 | 0.0069072 | 0.00040688 | -0.00052895 | 0.00085447 | -60.3699 | 62.5214 | -60.8231 | 0.032043 | 0.004578 | 0.032043 | 0.10986 | 0.23804 | 0.27924 | -0.23346 | -0.36621 | 0.073242 | 0.086975 | 60.4889 | -62.4435 | 60.2234 | -62.1689 | 0.45319
1086.7656 | 123.0469 | -60.466 | 62.4252 | 0.20381 | 0.02123 | 0.016581 | 0.0088298 | 0.0027567 | 0.0060934 | 0.0021363 | -60.3607 | 62.4985 | -60.8139 | -0.40741 | -0.18768 | 0.50812 | 0.24261 | -0.004578 | 0.19226 | -0.35706 | -0.3479 | 0.073242 | 0.10529 | 60.0586 | -62.6129 | 60.1089 | -62.233 | 0.45319
1087.7344 | 123.0103 | -60.4614 | 62.4298 | -0.17766 | 0.018453 | 0.014659 | 0.0028484 | 0.0021159 | 0.00011185 | -0.00064093 | -60.3745 | 62.4939 | -60.8322 | 0.013733 | 0.11902 | 0.48065 | 0.07782 | -0.19226 | 0.28381 | -0.1236 | -0.37079 | 0.064086 | 0.086975 | 60.4752 | -62.3108 | 60.3378 | -62.146 | 0.45776
1088.7656 | 123.1293 | -60.4385 | 62.3795 | 0.26485 | 0.021871 | 0.016795 | 0.00413 | 0.0036113 | 0.00032545 | -0.00042733 | -60.3241 | 62.471 | -60.791 | -0.004578 | -0.013733 | -0.027466 | -0.16022 | 0.20142 | 0.17853 | -0.39368 | -0.35248 | 0.091552 | 0.11444 | 60.434 | -62.3932 | 60.0449 | -62.2009 | 0.46692
1089.7344 | 123.0469 | -60.4568 | 62.4207 | -0.19291 | 0.020162 | 0.013804 | 0.0011394 | 0.0019023 | -0.0024516 | 0.00021367 | -60.3607 | 62.4939 | -60.8047 | 0.009155 | 0.022888 | 0.050354 | 0.15106 | 0.25177 | 0.28381 | -0.19684 | -0.3479 | 0.073242 | 0.09613 | 60.466 | -62.3978 | 60.26 | -62.1368 | 0.44403
1090.7656 | 123.1384 | -60.3973 | 62.3978 | -0.093733 | 0.015676 | 0.019145 | -0.0022786 | -0.00023392 | 0.00096645 | -0.00085453 | -60.4111 | 62.4207 | -60.7864 | 0.009155 | 0.045776 | 0.059509 | -0.07782 | 0.24261 | 0.20599 | -0.27924 | -0.3891 | 0.022888 | -0.013733 | 60.4065 | -62.352 | 60.1181 | -62.1918 | 0.37537
1091.7344 | 123.0606 | -60.4202 | 62.4756 | -0.19291 | 0.018239 | 0.013804 | 0.0017802 | -0.00023392 | 0.0020344 | 6.6667e-08 | -60.3653 | 62.4985 | -60.7864 | 0.013733 | 0.022888 | 0.022888 | 0.15106 | 0.24261 | 0.27924 | -0.21057 | -0.36621 | 0.022888 | 0.054932 | 60.434 | -62.4527 | 60.2097 | -62.1964 | 0.42114
1092.7656 | 123.1476 | -60.4202 | 62.3795 | 0.29537 | 0.020803 | 0.018504 | 0.0034892 | 0.0021159 | 0.00053925 | 6.6667e-08 | -60.2646 | 62.4069 | -60.7544 | 0.036621 | 0.050354 | 0.036621 | -0.19684 | 0.21973 | 0.15564 | -0.37079 | -0.33417 | 0.027465 | 0.15564 | 60.4568 | -62.3291 | 60.0494 | -62.2238 | 0.48981
1093.7344 | 123.0148 | -60.4156 | 62.4481 | -0.2158 | 0.017812 | 0.017436 | 0.001353 | 0.00083408 | -0.0018108 | 0.00021367 | -60.3424 | 62.471 | -60.7864 | 0.027466 | 0.009155 | 0.036621 | 0.14648 | 0.25635 | 0.27008 | -0.1831 | -0.37079 | 0.022888 | 0.073242 | 60.4431 | -62.439 | 60.2325 | -62.178 | 0.44403
1094.75 | 123.0469 | -60.4477 | 62.4344 | 0.020708 | 0.021657 | 0.018717 | 0.009257 | 0.0025431 | -0.00031535 | -0.0019225 | -60.2646 | 62.5214 | -60.7819 | 0.032043 | -0.009155 | -0.022888 | -0.009155 | 0.16479 | 0.21973 | -0.30212 | -0.33417 | 0.086975 | 0.18311 | 60.4797 | -62.4435 | 60.1456 | -62.2147 | 0.51727
1095.7344 | 122.9736 | -60.4202 | 62.4344 | -0.19291 | 0.019307 | 0.016795 | 0.0037028 | 0.0036113 | -0.00052895 | -0.0036315 | -60.3516 | 62.4893 | -60.8047 | 0.022888 | 0.018311 | 0.032043 | 0.23346 | 0.69122 | 0.30212 | -0.12817 | -0.38452 | 0.054932 | 0.068665 | 60.4431 | -62.4161 | 60.2921 | -62.1323 | 0.45319
1096.7656 | 123.0331 | -60.4156 | 62.4252 | -0.0021797 | 0.020376 | 0.017649 | 0.0060526 | 0.0038249 | -0.00010175 | -0.00085453 | -60.3424 | 62.5214 | -60.8093 | -0.045776 | -0.054932 | -0.059509 | -0.036621 | 0.11902 | 0.21515 | -0.33417 | -0.39368 | 0.09613 | 0.073242 | 60.3699 | -62.4802 | 60.0815 | -62.2101 | 0.46692
1097.7344 | 123.0423 | -60.3973 | 62.4344 | -0.20817 | 0.017171 | 0.017863 | -0.0001424 | 0.0016887 | -0.0013834 | -0.0017089 | -60.2829 | 62.4939 | -60.7727 | 0.082397 | 0.064087 | 0.10529 | 0.086975 | 0.29755 | 0.2655 | -0.21057 | -0.37537 | 0.059509 | 0.11444 | 60.4797 | -62.3703 | 60.1868 | -62.1689 | 0.48981
1098.7656 | 123.111 | -60.3882 | 62.4252 | 0.066485 | 0.017171 | 0.01295 | -0.0014242 | 0.0012615 | -0.00031535 | -0.00064093 | -60.3424 | 62.4115 | -60.7773 | 0.009155 | 0.036621 | 0.027466 | -0.059509 | 0.22888 | 0.19226 | -0.28839 | -0.3891 | -0.013733 | 0.045777 | 60.3973 | -62.3886 | 60.0998 | -62.233 | 0.43488
1099.7344 | 123.0331 | -60.4294 | 62.4481 | -0.19291 | 0.017598 | 0.014872 | 0.003062 | -0.00087492 | -0.0026652 | 0.00021367 | -60.3516 | 62.4985 | -60.7636 | 0.018311 | 0.022888 | 0.050354 | 0.16022 | 0.25177 | 0.28839 | -0.1831 | -0.33417 | 0.050354 | 0.07782 | 60.4477 | -62.4252 | 60.2463 | -62.1597 | 0.41199
1100.7656 | 123.1293 | -60.3836 | 62.3886 | 0.15041 | 0.021016 | 0.019572 | 0.0049846 | 0.0038249 | 0.00032545 | 0.00042727 | -60.2554 | 62.4435 | -60.7773 | 0.027466 | 0.045776 | 0.032043 | -0.19684 | 0.20142 | 0.16937 | -0.37537 | -0.39368 | 0.054931 | 0.12817 | 60.4111 | -62.3428 | 60.0082 | -62.2192 | 0.52185
1101.7344 | 123.0377 | -60.4385 | 62.4481 | -0.20054 | 0.018026 | 0.012522 | 0.001353 | -0.0013021 | -0.00031535 | 0.00085447 | -60.3333 | 62.5259 | -60.7773 | -0.009155 | 0.027466 | 0.068665 | 0.14648 | 0.24719 | 0.27924 | -0.17395 | -0.33874 | 0.07782 | 0.10529 | 60.4294 | -62.4207 | 60.2646 | -62.1689 | 0.44403
1102.7656 | 123.0927 | -60.4111 | 62.4115 | 0.10463 | 0.016744 | 0.019145 | -0.0009968 | 0.00083408 | 0.00032545 | 6.6667e-08 | -60.3287 | 62.4344 | -60.7727 | -0.013733 | 0.018311 | 0.036621 | -0.059509 | 0.26093 | 0.21057 | -0.28381 | -0.36163 | 0.022888 | 0.082398 | 60.3973 | -62.3932 | 60.1273 | -62.2009 | 0.44403
1103.7344 | 123.0377 | -60.434 | 62.4619 | -0.2158 | 0.019521 | 0.014872 | 0.0028484 | -0.00044752 | -0.0015972 | -0.0027771 | -60.2737 | 62.4985 | -60.7452 | 0.064087 | 0.041199 | 0.091553 | 0.09613 | 0.23804 | 0.26093 | -0.16479 | -0.31128 | 0.036621 | 0.16022 | 60.498 | -62.4207 | 60.2692 | -62.2009 | 0.4715
1104.7656 | 123.1018 | -60.3928 | 62.4298 | 0.18855 | 0.015889 | 0.01594 | 0.000712 | -0.00087492 | -0.00095615 | -0.0014953 | -60.3149 | 62.3886 | -60.7956 | 0.013733 | 0.018311 | 0.018311 | -0.086975 | 0.21515 | 0.18768 | -0.29755 | -0.40283 | -0.041199 | 0.07782 | 60.4065 | -62.4115 | 60.0952 | -62.2421 | 0.48065
1105.7344 | 123.0377 | -60.4202 | 62.471 | -0.20817 | 0.018026 | 0.012736 | 0.0060526 | -0.0017293 | -0.00052895 | 0.0010681 | -60.3104 | 62.5305 | -60.7636 | 0.018311 | 0.013733 | 0.027466 | 0.14648 | 0.24261 | 0.27008 | -0.18768 | -0.34332 | 0.05951 | 0.10986 | 60.4385 | -62.4573 | 60.2325 | -62.2009 | 0.45319
1106.75 | 123.0652 | -60.4156 | 62.4573 | 0.013079 | 0.021871 | 0.019145 | 0.007548 | 0.0031841 | -0.0015972 | -0.0010681 | -60.2005 | 62.5168 | -60.7819 | 0.045776 | 0 | 0.009155 | 0.036621 | 0.20599 | 0.23804 | -0.27924 | -0.36621 | 0.05951 | 0.21515 | 60.4614 | -62.4573 | 60.1364 | -62.2192 | 0.58136
1107.7344 | 123.0057 | -60.3882 | 62.4573 | -0.19291 | 0.018026 | 0.016581 | 0.00413 | 0.0014751 | -0.0018108 | -0.0027771 | -60.2921 | 62.5259 | -60.8002 | 0.018311 | 0.027466 | 0.022888 | 0.13275 | 0.22888 | 0.28839 | -0.19226 | -0.41199 | 0.068665 | 0.096131 | 60.4065 | -62.4298 | 60.1959 | -62.1689 | 0.50812
1108.7656 | 123.1613 | -60.3699 | 62.3886 | 0.27248 | 0.018453 | 0.015513 | 0.0045574 | 0.0025431 | -0.0028788 | -0.0012817 | -60.2371 | 62.439 | -60.7498 | 0.054932 | 0.064087 | 0.036621 | -0.20142 | 0.22888 | 0.15106 | -0.33875 | -0.37994 | 0.050354 | 0.13275 | 60.4248 | -62.3245 | 60.0311 | -62.2375 | 0.5127
1109.7344 | 123.0286 | -60.4156 | 62.4756 | -0.19291 | 0.019521 | 0.015086 | 0.0054118 | 0.00083408 | -0.00052895 | -0.0019225 | -60.3058 | 62.5397 | -60.7498 | 0.032043 | 0.009155 | 0.032043 | 0.1236 | 0.23346 | 0.25635 | -0.21057 | -0.33417 | 0.064087 | 0.10986 | 60.4477 | -62.4664 | 60.2051 | -62.2192 | 0.44403
1110.7656 | 123.1293 | -60.3973 | 62.4023 | 0.10463 | 0.017812 | 0.01295 | -0.0001424 | 0.0016887 | -0.0011698 | 0.00064087 | -60.3012 | 62.4207 | -60.7727 | 0.013733 | 0.050354 | 0.050354 | -0.059509 | 0.24261 | 0.18768 | -0.27008 | -0.37537 | 0.01831 | 0.096131 | 60.4111 | -62.352 | 60.1273 | -62.2147 | 0.4715
1111.7344 | 123.024 | -60.3882 | 62.4481 | -0.20054 | 0.020162 | 0.015086 | 0.0032756 | -0.00066112 | -0.00031535 | -0.0010681 | -60.2966 | 62.5351 | -60.7636 | 0.027466 | 0.018311 | 0.041199 | 0.14648 | 0.24719 | 0.2655 | -0.1831 | -0.37537 | 0.086975 | 0.091553 | 60.4156 | -62.4298 | 60.2051 | -62.1826 | 0.46692
1112.7656 | 123.1064 | -60.3699 | 62.439 | 0.10463 | 0.015889 | 0.01594 | -0.0005696 | 0.00019328 | -0.00010175 | -0.00042733 | -60.3012 | 62.4527 | -60.759 | 0.018311 | 0.041199 | 0.032043 | -0.073242 | 0.23804 | 0.21057 | -0.28839 | -0.3891 | 0.013733 | 0.068665 | 60.3882 | -62.3978 | 60.0815 | -62.2284 | 0.45776
1113.7344 | 123.0286 | -60.4111 | 62.4756 | 0.020708 | 0.019735 | 0.019572 | 0.0060526 | 0.0025431 | -0.00095615 | -0.0012817 | -60.2417 | 62.5397 | -60.7544 | 0.050354 | 0.032043 | 0.041199 | 0.14648 | 0.25177 | 0.25635 | -0.27008 | -0.34332 | 0.064087 | 0.16937 | 60.4614 | -62.4435 | 60.141 | -62.2192 | 0.5127
1114.75 | 123.0103 | -60.4019 | 62.4573 | 0.13515 | 0.019307 | 0.021922 | 0.0086162 | 0.0016887 | -0.002238 | -0.00085453 | -60.2737 | 62.5671 | -60.759 | -0.059509 | -0.07782 | -0.09613 | 0.022888 | 0.07782 | 0.21515 | -0.37537 | -0.35706 | 0.10986 | 0.12817 | 60.3424 | -62.5351 | 60.0266 | -62.2421 | 0.48523
1115.7344 | 123.0652 | -60.4111 | 62.4527 | -0.093733 | 0.019948 | 0.017436 | 0.0060526 | 0.0023295 | -0.00074255 | -0.00042733 | -60.2463 | 62.5442 | -60.7727 | 0.054932 | 0.045776 | 0.041199 | 0.07782 | 0.24719 | 0.25635 | -0.21057 | -0.36163 | 0.091552 | 0.16479 | 60.466 | -62.4069 | 60.2005 | -62.1963 | 0.52643
1116.7656 | 123.1476 | -60.4019 | 62.4069 | 0.28774 | 0.021444 | 0.019999 | 0.004771 | 0.0016887 | 0.00096645 | 0.0014953 | -60.2097 | 62.4893 | -60.7681 | 0.041199 | 0.064087 | 0.032043 | -0.20599 | 0.20599 | 0.16022 | -0.3479 | -0.36621 | 0.082398 | 0.19226 | 60.4431 | -62.3428 | 60.054 | -62.2467 | 0.55847
1117.7344 | 123.0011 | -60.4294 | 62.4802 | -0.1624 | 0.019735 | 0.020426 | 0.003062 | 0.0012615 | 0.0016072 | -0.00042733 | -60.2829 | 62.5671 | -60.7727 | 0.3067 | 0.27466 | -0.31128 | -0.13733 | 0.27008 | 0.3067 | -0.13733 | -0.34332 | 0.086975 | 0.14648 | 60.7361 | -62.2055 | 60.2921 | -62.1735 | 0.48981
1118.7656 | 123.1201 | -60.3836 | 62.439 | 0.051226 | 0.018667 | 0.016368 | -0.0056966 | 0.0021159 | -0.00052895 | 0.00064087 | -60.2783 | 62.4527 | -60.7636 | -0.022888 | 0.004578 | 0.036621 | -0.059509 | 0.26093 | 0.19684 | -0.2655 | -0.37994 | 0.013733 | 0.10529 | 60.3607 | -62.4344 | 60.1181 | -62.2421 | 0.48523
1119.7344 | 123.0606 | -60.3928 | 62.4893 | -0.23106 | 0.019735 | 0.016368 | 0.00648 | 0.00062048 | -0.0013834 | -0.00064093 | -60.2509 | 62.5671 | -60.7407 | 0.018311 | 0 | 0.032043 | 0.11902 | 0.26093 | 0.25177 | -0.21973 | -0.3479 | 0.07782 | 0.14191 | 60.4111 | -62.4893 | 60.173 | -62.2375 | 0.48981
1120.7656 | 123.111 | -60.3836 | 62.439 | 0.31063 | 0.019948 | 0.016795 | 0.0066936 | 0.0042521 | 0.00096645 | -0.0025635 | -60.2417 | 62.5122 | -60.7498 | 0 | 0 | -0.027466 | -0.14648 | 0.16022 | 0.16479 | -0.36163 | -0.36621 | 0.073242 | 0.14191 | 60.3836 | -62.439 | 60.022 | -62.2742 | 0.50812
1121.7344 | 123.0469 | -60.3973 | 62.4802 | 0.79128 | 0.019735 | 0.017436 | 0.00413 | 0.0010477 | -0.00052895 | -0.00064093 | -60.2325 | 62.5488 | -60.7544 | 0.027466 | 0.041199 | 0.032043 | 0.16479 | 0.27008 | 0.25635 | -0.24261 | -0.35706 | 0.068664 | 0.1648 | 60.4248 | -62.439 | 60.1547 | -62.2238 | 0.52185
1122.75 | 123.0881 | -60.4202 | 62.4527 | 0.23433 | 0.019948 | 0.015513 | 0.007548 | 0.0038249 | 0.00032545 | -0.00064093 | -60.2417 | 62.5534 | -60.7544 | -0.059509 | -0.064087 | -0.09613 | -0.49439 | -0.49439 | 0.16479 | -0.39368 | -0.33417 | 0.10071 | 0.17853 | 60.3607 | -62.5168 | 60.0266 | -62.2879 | 0.5127
1123.7344 | 123.0331 | -60.3928 | 62.4527 | -0.20054 | 0.017812 | 0.011881 | -0.0012106 | 0.00083408 | -0.00052895 | -0.00021353 | -60.2371 | 62.5397 | -60.7407 | 0.050354 | 0.054932 | 0.091553 | 0.09613 | 0.2243 | 0.27466 | -0.19226 | -0.3479 | 0.086975 | 0.15564 | 60.4431 | -62.3978 | 60.2005 | -62.178 | 0.50354
1124.7656 | 123.1201 | -60.4065 | 62.4435 | 0.26485 | 0.019948 | 0.018717 | 0.0069072 | 0.0031841 | -0.0013834 | 0.00021367 | -60.228 | 62.5031 | -60.7452 | 0.004578 | 0.004578 | -0.013733 | -0.14648 | 0.18768 | 0.16937 | -0.37537 | -0.33874 | 0.05951 | 0.17853 | 60.4111 | -62.439 | 60.0311 | -62.2742 | 0.51727
1125.7344 | 123.0103 | -60.4111 | 62.4527 | 0.78365 | 0.022085 | 0.019786 | 0.0060526 | 0.0021159 | 0.00096645 | 0.00085447 | -60.2188 | 62.5534 | -60.7727 | 0.027466 | 0.022888 | 0.050354 | 0.14648 | 0.25635 | 0.27924 | -0.23804 | -0.36163 | 0.10071 | 0.19226 | 60.4385 | -62.4298 | 60.173 | -62.1735 | 0.55389
1126.7656 | 123.0972 | -60.3882 | 62.4573 | 0.21907 | 0.019948 | 0.019572 | 0.0060526 | 0.0055339 | 0.00118 | -0.0023499 | -60.2371 | 62.5351 | -60.7498 | -0.041199 | -0.032043 | -0.054932 | -0.091553 | 0.12817 | 0.16937 | -0.35248 | -0.36163 | 0.07782 | 0.15106 | 60.347 | -62.4893 | 60.0357 | -62.2879 | 0.5127
1127.7344 | 123.056 | -60.379 | 62.4802 | -0.18529 | 0.018026 | 0.016368 | 0.0022074 | -2.0324e-05 | -0.00052895 | -0.00021353 | -60.2554 | 62.5626 | -60.7452 | -0.004578 | 0.027466 | 0.032043 | 0.14191 | 0.24261 | 0.27924 | -0.17853 | -0.36621 | 0.082397 | 0.1236 | 60.3744 | -62.4527 | 60.2005 | -62.2009 | 0.48981
1128.7656 | 123.1705 | -60.3607 | 62.4298 | -0.040327 | 0.014821 | 0.016581 | -0.0024922 | -0.00023392 | -0.0013834 | 0.00085447 | -60.2005 | 62.4573 | -60.7269 | 0.09613 | 0.14191 | 0.16022 | -0.059509 | 0.37994 | 0.21515 | -0.17853 | -0.36621 | 0.027465 | 0.16022 | 60.4568 | -62.2879 | 60.1822 | -62.2147 | 0.52643
1129.7344 | 123.024 | -60.379 | 62.4802 | 0.33351 | 0.01888 | 0.016154 | 0.0054118 | -0.0010885 | 0.00118 | -0.0014953 | -60.3149 | 62.5488 | -60.7498 | -0.013733 | 0.022888 | 0.07782 | 0.13275 | 0.23346 | 0.25635 | -0.2655 | -0.37079 | 0.068664 | 0.064087 | 60.3653 | -62.4573 | 60.1135 | -62.2238 | 0.43488
1130.7656 | 123.1476 | -60.3424 | 62.439 | -0.025068 | 0.016958 | 0.014659 | -0.0005696 | 0.0023295 | -0.00052895 | -0.00021353 | -60.2097 | 62.439 | -60.7269 | 0.082397 | 0.10071 | 0.10529 | -0.059509 | 0.33875 | 0.19226 | -0.23804 | -0.38452 | 0 | 0.13275 | 60.4248 | -62.3383 | 60.1044 | -62.2467 | 0.51727
1131.7344 | 123.0286 | -60.3699 | 62.5076 | -0.18529 | 0.016958 | 0.018931 | 0.0037028 | -0.00066112 | -0.00052895 | -0.0010681 | -60.1913 | 62.4985 | -60.7086 | 0.032043 | 0.036621 | 0.045776 | 0.082397 | 0.28381 | 0.27466 | -0.1831 | -0.33875 | -0.009155 | 0.17853 | 60.4019 | -62.471 | 60.1868 | -62.233 | 0.51727
1132.7656 | 123.111 | -60.3699 | 62.4573 | 0.18855 | 0.017812 | 0.013377 | 0.001353 | 0.00083408 | -0.0013834 | -0.0012817 | -60.2097 | 62.471 | -60.6995 | -0.004578 | 0.004578 | 0.009155 | -0.1236 | 0.21057 | 0.16479 | -0.31128 | -0.32959 | 0.013733 | 0.16022 | 60.3653 | -62.4527 | 60.0586 | -62.2925 | 0.48981
1133.7344 | 123.0331 | -60.3928 | 62.4573 | 0.21907 | 0.021871 | 0.018931 | 0.0094706 | 0.0016887 | 0.0031026 | -0.0010681 | -60.2509 | 62.558 | -60.7407 | -0.041199 | -0.064087 | -0.10529 | -0.022888 | 0.086975 | 0.21057 | -0.33417 | -0.3479 | 0.10071 | 0.14191 | 60.3516 | -62.5214 | 60.0586 | -62.2467 | 0.48981
1134.7656 | 123.0515 | -60.4248 | 62.4527 | 0.21907 | 0.02123 | 0.017863 | 0.0051982 | 0.0029705 | 0.00011185 | -0.0012817 | -60.2417 | 62.5626 | -60.7819 | -0.032043 | -0.050354 | -0.10071 | -0.064087 | 0.11444 | 0.21515 | -0.36163 | -0.35706 | 0.10986 | 0.18311 | 60.3928 | -62.5031 | 60.0632 | -62.2375 | 0.54016
1135.7344 | 123.0698 | -60.3653 | 62.4527 | -0.17766 | 0.017171 | 0.015299 | 0.0002848 | 0.0021159 | -0.0030924 | 0.0021363 | -60.1913 | 62.5168 | -60.7224 | 0.068665 | 0.082397 | 0.10529 | 0.073242 | 0.31128 | 0.25635 | -0.20599 | -0.35706 | 0.064087 | 0.17395 | 60.434 | -62.3703 | 60.1593 | -62.1963 | 0.53101
1136.7344 | 123.1064 | -60.3561 | 62.4664 | -0.14714 | 0.016958 | 0.019999 | 0.0004984 | -0.0015157 | -0.00074255 | 6.6667e-08 | -60.1776 | 62.4619 | -60.7224 | 0.091553 | 0.10071 | 0.13275 | 0.032043 | 0.34332 | 0.25635 | -0.20599 | -0.36621 | -0.004578 | 0.17853 | 60.4477 | -62.3657 | 60.1501 | -62.2101 | 0.54474
1137.7344 | 123.1293 | -60.3516 | 62.4481 | 0.21907 | 0.018026 | 0.013163 | -0.0007832 | -0.0010885 | -0.0028788 | -0.0010681 | -60.1456 | 62.4847 | -60.7086 | 0.091553 | 0.11902 | 0.13275 | -0.018311 | 0.35248 | 0.23346 | -0.21515 | -0.35706 | 0.036621 | 0.20599 | 60.4431 | -62.3291 | 60.1364 | -62.2147 | 0.56305
1138.7656 | 123.0972 | -60.3333 | 62.4207 | -0.12425 | 0.015889 | 0.019999 | -0.000356 | -0.00023392 | 0.00075285 | -0.00042733 | -60.1501 | 62.4664 | -60.7132 | 0.13275 | 0.12817 | 0.15564 | -0.041199 | 0.5127 | 0.24719 | -0.17395 | -0.37994 | 0.045777 | 0.18311 | 60.466 | -62.2925 | 60.1593 | -62.1735 | 0.56305
1139.7344 | 123.1155 | -60.3516 | 62.4847 | -0.093733 | 0.018453 | 0.016581 | 0.0034892 | -0.00023392 | -0.0037334 | -0.00021353 | -60.141 | 62.4756 | -60.7086 | 0.11444 | 0.11902 | 0.14191 | 0.013733 | 0.3479 | 0.24719 | -0.22888 | -0.35706 | -0.009155 | 0.21057 | 60.466 | -62.3657 | 60.1227 | -62.2375 | 0.56763
1140.7656 | 123.0011 | -60.4202 | 62.4802 | 0.1733 | 0.021016 | 0.016795 | 0.009257 | 0.0010477 | 0.00011185 | -0.00085453 | -60.1959 | 62.5854 | -60.7361 | -0.064087 | -0.073242 | -0.091553 | -0.022888 | 0.086975 | 0.21515 | -0.36621 | -0.31586 | 0.10528 | 0.2243 | 60.3561 | -62.5534 | 60.054 | -62.265 | 0.54016
1141.7344 | 123.1613 | -60.3607 | 62.4481 | -0.13951 | 0.017812 | 0.012522 | 0.0004984 | -0.0051473 | -0.0037334 | -0.00042733 | -60.141 | 62.4619 | -60.7224 | 0 | -0.29297 | -0.10986 | 0.086975 | 0.25635 | 0.2243 | -0.21515 | -0.36163 | 0.013733 | 0.21973 | 60.3607 | -62.7411 | 60.1456 | -62.2238 | 0.58136
1142.7656 | 123.0515 | -60.4156 | 62.4573 | 0.0054493 | 0.02123 | 0.016795 | 0.010112 | 0.0021159 | -0.0011698 | -0.0017089 | -60.1318 | 62.558 | -60.7315 | 0.064087 | 0.004578 | 0.004578 | 0.022888 | 0.20599 | 0.23804 | -0.28839 | -0.31586 | 0.10071 | 0.28381 | 60.4797 | -62.4527 | 60.1273 | -62.2192 | 0.59967
1143.7344 | 123.1247 | -60.3378 | 62.4207 | -2.4512 | 0.016103 | 0.012736 | 0.0017802 | 0.0021159 | -0.0018108 | 0.00085447 | -59.9899 | 62.5305 | -60.7315 | 0.1831 | 0.13275 | 0.050354 | -0.032043 | 0.3891 | 0.20599 | -0.23346 | -0.39368 | 0.10986 | 0.3479 | 60.5209 | -62.2879 | 60.1044 | -62.2147 | 0.74158
1144.7656 | 123.1018 | -60.3745 | 62.4207 | 0.21144 | 0.014821 | 0.018931 | 0.0032756 | 0.0029705 | -0.0030924 | -0.00042733 | -60.1547 | 62.439 | -60.7269 | 0.041199 | 0.027466 | 0.032043 | -0.16022 | 0.20142 | 0.17853 | -0.33875 | -0.35248 | 0.018311 | 0.21973 | 60.4156 | -62.3932 | 60.0357 | -62.2421 | 0.5722
1145.7344 | 123.1613 | -60.3378 | 62.4435 | -0.017439 | 0.016744 | 0.016581 | -0.0016378 | -0.0023701 | 0.00011185 | -0.00085453 | -60.1547 | 62.4619 | -60.7132 | 0.086975 | 0.091553 | 0.11902 | -0.082397 | 0.3067 | 0.21057 | -0.24261 | -0.37537 | 0.018311 | 0.18311 | 60.4248 | -62.352 | 60.0952 | -62.233 | 0.55847
1146.7656 | 123.0652 | -60.4156 | 62.4664 | 0.058855 | 0.021444 | 0.019999 | 0.0088298 | 0.0014751 | 0.00118 | 0.00064087 | -60.0952 | 62.59 | -60.7315 | 0.004578 | -0.027466 | -0.036621 | 0.009155 | 0.16479 | 0.23346 | -0.3067 | -0.31586 | 0.1236 | 0.32043 | 60.4202 | -62.4939 | 60.1089 | -62.233 | 0.63629
1147.7344 | 123.1613 | -60.3241 | 62.4298 | -0.0021797 | 0.018239 | 0.015299 | -0.0027058 | -0.0013021 | -0.00052895 | 0.00021367 | -60.1501 | 62.471 | -60.7498 | 0.10986 | 0.1236 | 0.12817 | -0.064087 | 0.37994 | 0.21973 | -0.23346 | -0.42572 | 0.041198 | 0.17395 | 60.434 | -62.3062 | 60.0906 | -62.2101 | 0.59967
1148.7656 | 123.056 | -60.4111 | 62.4893 | -0.17003 | 0.019948 | 0.018717 | 0.0073344 | 0.0029705 | -0.0020244 | -0.0014953 | -60.141 | 62.5992 | -60.7407 | 0.045776 | 0.027466 | 0.041199 | 0.11444 | 0.24719 | 0.25177 | -0.21057 | -0.32959 | 0.10986 | 0.27008 | 60.4568 | -62.4619 | 60.2005 | -62.2375 | 0.59967
1149.7344 | 123.1293 | -60.3516 | 62.4481 | 0.028338 | 0.018026 | 0.018504 | -0.0033468 | -0.00087492 | 0.00032545 | -0.0023499 | -60.1685 | 62.4481 | -60.7407 | 0.073242 | 0.082397 | 0.10071 | -0.064087 | 0.29755 | 0.23346 | -0.25635 | -0.3891 | 0 | 0.18311 | 60.4248 | -62.3657 | 60.0952 | -62.2147 | 0.57221
1150.7656 | 123.0057 | -60.4065 | 62.4664 | 0.13515 | 0.021871 | 0.018931 | 0.010966 | 0.0014751 | -0.00031535 | -0.00064093 | -60.1318 | 62.5854 | -60.7452 | -0.009155 | -0.059509 | -0.068665 | 0.022888 | 0.12817 | 0.21973 | -0.34332 | -0.33874 | 0.11902 | 0.27466 | 60.3973 | -62.5259 | 60.0632 | -62.2467 | 0.6134
1151.7344 | 123.1064 | -60.3699 | 62.4619 | 0.020708 | 0.019521 | 0.014872 | -0.0022786 | -0.0013021 | 0.0013936 | 0.0010681 | -60.1822 | 62.4481 | -60.7452 | -0.059509 | 0.009155 | 0.027466 | -0.086975 | 0.27466 | 0.21057 | -0.28381 | -0.37537 | -0.013733 | 0.18768 | 60.3104 | -62.4527 | 60.0861 | -62.2513 | 0.56305
1152.7656 | 123.0606 | -60.4065 | 62.4344 | 0.20381 | 0.022085 | 0.018077 | 0.0077616 | 0.0031841 | 0.002248 | -0.0010681 | -60.1364 | 62.5442 | -60.7452 | -0.018311 | -0.041199 | -0.073242 | -0.086975 | 0.1236 | 0.20142 | -0.35706 | -0.33874 | 0.10986 | 0.27008 | 60.3882 | -62.4756 | 60.0494 | -62.233 | 0.60882
1153.7344 | 123.1064 | -60.3973 | 62.4298 | 0.46321 | 0.017598 | 0.013804 | 0.0004984 | -2.0324e-05 | -0.0020244 | -0.0012817 | -60.1776 | 62.439 | -60.7361 | 0.027466 | 0.054932 | 0.059509 | -0.07782 | 0.26093 | 0.20142 | -0.28381 | -0.33874 | 0.009155 | 0.21973 | 60.4248 | -62.3749 | 60.1135 | -62.2284 | 0.55847
1154.7656 | 123.0148 | -60.4111 | 62.4573 | 0.12752 | 0.022939 | 0.019786 | 0.012248 | 0.0016887 | -0.00010175 | -0.0017089 | -60.1456 | 62.5534 | -60.7681 | -0.054932 | -0.068665 | -0.11444 | 0.018311 | 0.07782 | 0.21515 | -0.35706 | -0.35706 | 0.096131 | 0.2655 | 60.3561 | -62.5259 | 60.054 | -62.2421 | 0.62256
1155.7344 | 123.1064 | -60.379 | 62.4298 | 0.10463 | 0.018453 | 0.014231 | -0.000356 | 0.0025431 | 0.00053925 | -0.00021353 | -60.1547 | 62.4481 | -60.7681 | 0.022888 | 0.036621 | 0.032043 | -0.09613 | 0.22888 | 0.20142 | -0.27008 | -0.3891 | 0.01831 | 0.2243 | 60.4019 | -62.3932 | 60.1089 | -62.2284 | 0.6134
1156.7656 | 122.9919 | -60.4065 | 62.4573 | 0.19618 | 0.021871 | 0.015086 | 0.0071208 | 0.0025431 | -0.0020244 | 6.6667e-08 | -60.1456 | 62.5671 | -60.7819 | -0.059509 | -0.082397 | -0.1236 | -0.004578 | 0.09613 | 0.19684 | -0.36621 | -0.37537 | 0.10986 | 0.26093 | 60.347 | -62.5397 | 60.0403 | -62.2604 | 0.63629
1157.7344 | 123.1201 | -60.3928 | 62.4115 | 0.13515 | 0.020162 | 0.016795 | -0.0012106 | -0.00044752 | 0.002248 | -0.0012817 | -60.1456 | 62.4527 | -60.7452 | 0.018311 | 0.054932 | 0.036621 | -0.064087 | 0.25177 | 0.21973 | -0.27924 | -0.35248 | 0.041199 | 0.24719 | 60.4111 | -62.3566 | 60.1135 | -62.1918 | 0.59967
1158.7656 | 123.0469 | -60.4111 | 62.4802 | -0.22343 | 0.019521 | 0.020854 | 0.0032756 | -0.00044752 | 0.00096645 | -0.00064093 | -60.1364 | 62.4847 | -60.7681 | 0.018311 | 0.036621 | 0.059509 | 0.11902 | 0.22888 | 0.28839 | -0.1831 | -0.35706 | 0.004577 | 0.27466 | 60.4294 | -62.4435 | 60.228 | -62.1918 | 0.63171
1159.7344 | 123.0972 | -60.3836 | 62.4023 | -0.025068 | 0.020162 | 0.017863 | 0.0019938 | 0.0023295 | -0.0013834 | 0.00042727 | -60.0632 | 62.439 | -60.7361 | 0.041199 | 0.045776 | 0.022888 | -0.16479 | 0.23346 | 0.17395 | -0.33417 | -0.35248 | 0.036621 | 0.32044 | 60.4248 | -62.3566 | 60.0494 | -62.2284 | 0.67291
1160.75 | 123.0835 | -60.3928 | 62.4847 | -0.17766 | 0.018453 | 0.016581 | 0.0045574 | -0.0010885 | 0.00032545 | -0.0023499 | -60.1364 | 62.5442 | -60.7681 | 0.022888 | 0.022888 | 0.018311 | 0.13733 | 0.24719 | 0.27924 | -0.18768 | -0.37537 | 0.059509 | 0.25635 | 60.4156 | -62.4619 | 60.2051 | -62.2055 | 0.63171
1161.7344 | 123.1384 | -60.3973 | 62.3978 | 0.19618 | 0.018239 | 0.017222 | 0.0022074 | -2.0324e-05 | -0.0013834 | -0.0010681 | -60.0632 | 62.4161 | -60.7315 | 0.054932 | 0.036621 | 0.036621 | -0.14648 | 0.21515 | 0.16479 | -0.33417 | -0.33417 | 0.018311 | 0.33417 | 60.4523 | -62.3611 | 60.0632 | -62.233 | 0.66834
1162.7656 | 123.0835 | -60.3928 | 62.4664 | -0.12425 | 0.019307 | 0.017222 | 0.0069072 | 0.00083408 | -0.0030924 | -0.0012817 | -60.054 | 62.5534 | -60.7407 | 0.054932 | 0.045776 | 0.059509 | 0.082397 | 0.26093 | 0.25177 | -0.2243 | -0.3479 | 0.086975 | 0.33875 | 60.4477 | -62.4207 | 60.1685 | -62.2147 | 0.68665
1163.7344 | 123.1247 | -60.4019 | 62.4115 | 0.29537 | 0.019307 | 0.014018 | 0.0011394 | 0.0021159 | -0.00010175 | 6.6667e-08 | -60.0357 | 62.4023 | -60.759 | 0.050354 | 0.045776 | 0.036621 | -0.16479 | 0.22888 | 0.17853 | -0.33875 | -0.35706 | -0.009155 | 0.36621 | 60.4523 | -62.3657 | 60.0632 | -62.233 | 0.72327
1164.7656 | 123.0286 | -60.4202 | 62.4435 | -0.23869 | 0.019307 | 0.01594 | 0.002421 | -0.00066112 | -0.00010175 | -0.00021353 | -60.1089 | 62.5168 | -60.7773 | 0.018311 | 0.018311 | 0.022888 | 0.14191 | 0.24719 | 0.28381 | -0.17853 | -0.35706 | 0.073243 | 0.31128 | 60.4385 | -62.4252 | 60.2417 | -62.1597 | 0.66833
1165.7344 | 123.1293 | -60.3928 | 62.4207 | 0.24196 | 0.018667 | 0.019786 | 0.00648 | 0.0029705 | 0.00011185 | -0.0017089 | -60.0311 | 62.4847 | -60.7773 | 0.045776 | -0.018311 | -0.045776 | -0.15106 | 0.23346 | 0.14191 | -0.38452 | -0.38452 | 0.064087 | 0.36163 | 60.4385 | -62.439 | 60.0082 | -62.2787 | 0.74615
1166.75 | 123.1064 | -60.3836 | 62.4298 | -0.093733 | 0.019735 | 0.016368 | 7.12e-05 | 0.0010477 | -0.00010175 | -0.0017089 | -60.0174 | 62.439 | -60.7361 | 0.10071 | 0.11902 | 0.12817 | 0.045776 | 0.33875 | 0.26093 | -0.19684 | -0.35248 | 0.009155 | 0.36621 | 60.4843 | -62.3108 | 60.1868 | -62.1689 | 0.71869
1167.7344 | 123.1476 | -60.3745 | 62.3978 | 0.28011 | 0.019094 | 0.017649 | 0.0073344 | 0.0031841 | -0.00074255 | 0.0025635 | -59.9899 | 62.4756 | -60.7544 | -0.004578 | 0.018311 | 0.041199 | -0.16479 | 0.19226 | 0.16022 | -0.3891 | -0.37994 | 0.07782 | 0.38452 | 60.3699 | -62.3795 | 59.9854 | -62.2375 | 0.76447
1168.7656 | 123.1476 | -60.3745 | 62.4252 | -0.13188 | 0.018026 | 0.012095 | 0.0004984 | -0.0013021 | -0.0011698 | 6.6667e-08 | -59.8526 | 62.4847 | -60.704 | 0.004578 | 0.11444 | 0.22888 | -0.086975 | 0.32044 | 0.23346 | -0.23346 | -0.32959 | 0.059509 | 0.52185 | 60.379 | -62.3108 | 60.141 | -62.1918 | 0.85144
1169.7344 | 123.0743 | -60.4523 | 62.4207 | 0.31825 | 0.021871 | 0.017649 | 0.0098978 | 0.0033977 | -0.0026652 | 0.00085447 | -60.0266 | 62.5397 | -60.7773 | -0.032043 | -0.059509 | -0.082397 | -0.068665 | 0.12817 | 0.19226 | -0.3479 | -0.32501 | 0.11902 | 0.42572 | 60.4202 | -62.4802 | 60.1044 | -62.2284 | 0.75073
1170.7656 | 123.1247 | -60.3882 | 62.4207 | 0.028338 | 0.017598 | 0.017222 | -0.0018514 | 0.00083408 | 0.00053925 | 0.0014953 | -60.022 | 62.4344 | -60.7544 | 0.068665 | 0.091553 | 0.10986 | -0.07782 | 0.29755 | 0.21973 | -0.23804 | -0.36621 | 0.013733 | 0.36621 | 60.4568 | -62.3291 | 60.1501 | -62.2009 | 0.73242
1171.7344 | 123.0606 | -60.4248 | 62.4298 | 0.23433 | 0.022512 | 0.022349 | 0.0096842 | 0.0012615 | 0.00053925 | -0.00085453 | -60.0082 | 62.5214 | -60.7636 | -0.022888 | -0.054932 | -0.064087 | -0.091553 | 0.11902 | 0.19226 | -0.3479 | -0.33875 | 0.091552 | 0.41656 | 60.4019 | -62.4847 | 60.0769 | -62.2375 | 0.75531
1172.7656 | 123.1293 | -60.3882 | 62.3795 | -0.0098092 | 0.017385 | 0.017863 | -0.0029196 | 0.00040688 | -0.0024516 | 6.6667e-08 | -60.0082 | 62.4298 | -60.759 | 0.082397 | 0.091553 | 0.10071 | -0.068665 | 0.3067 | 0.21057 | -0.23346 | -0.37079 | 0.050354 | 0.37994 | 60.4706 | -62.2879 | 60.1547 | -62.1689 | 0.75073
1173.7344 | 123.024 | -60.466 | 62.4344 | 0.097002 | 0.022085 | 0.024699 | 0.0086162 | 0.00040688 | -0.00031535 | -0.00021353 | -59.9716 | 62.5351 | -60.7636 | -0.022888 | -0.054932 | -0.064087 | 0.022888 | 0.091553 | 0.23346 | -0.34332 | -0.29755 | 0.10071 | 0.49438 | 60.4431 | -62.4893 | 60.1227 | -62.2009 | 0.79193
1174.7656 | 123.1018 | -60.3836 | 62.439 | -0.30736 | 0.015889 | 0.015727 | -0.000356 | 0.0014751 | -0.0015972 | -0.00042733 | -59.9442 | 62.4207 | -60.7636 | 0.1236 | 0.10529 | 0.13733 | -0.009155 | 0.3479 | 0.24261 | -0.21973 | -0.37994 | -0.018311 | 0.43945 | 60.5072 | -62.3337 | 60.1639 | -62.1964 | 0.8194
1175.7344 | 123.0148 | -60.466 | 62.4207 | 0.15041 | 0.022939 | 0.018717 | 0.0084026 | 0.0044657 | -0.0011698 | -0.0014953 | -59.9899 | 62.5122 | -60.7956 | -0.045776 | -0.09613 | -0.11902 | 0.018311 | 0.068665 | 0.21973 | -0.35706 | -0.32959 | 0.091553 | 0.47607 | 60.4202 | -62.5168 | 60.1089 | -62.2009 | 0.80566
1176.7656 | 123.1567 | -60.4156 | 62.3978 | 0.20381 | 0.018453 | 0.015299 | -0.0029196 | 0.0016887 | -0.0033062 | 0.00064087 | -59.9808 | 62.4023 | -60.8139 | 0.036621 | 0.068665 | 0.059509 | -0.07782 | 0.27466 | 0.18768 | -0.29297 | -0.39825 | 0.004578 | 0.43488 | 60.4523 | -62.3291 | 60.1227 | -62.2101 | 0.83313
1177.7344 | 123.0331 | -60.4706 | 62.4115 | 0.058855 | 0.022512 | 0.021495 | 0.0098978 | 0.0012615 | 0.00011185 | 0.00064087 | -59.9304 | 62.4985 | -60.7819 | -0.009155 | -0.022888 | -0.027466 | 0.027466 | 0.15106 | 0.2243 | -0.31128 | -0.31128 | 0.086975 | 0.54016 | 60.4614 | -62.4344 | 60.1593 | -62.1872 | 0.85144
1178.7656 | 123.1064 | -60.434 | 62.3932 | -0.13951 | 0.017171 | 0.01829 | -0.0016378 | 0.0019023 | -0.0026652 | 0.00042727 | -59.9304 | 62.4207 | -60.7956 | 0.086975 | 0.10529 | 0.14191 | 0.054932 | 0.33875 | 0.24261 | -0.20599 | -0.36163 | 0.027466 | 0.50354 | 60.5209 | -62.2879 | 60.228 | -62.1506 | 0.86517
1179.7344 | 123.0377 | -60.4568 | 62.3886 | -0.33024 | 0.023153 | 0.020854 | 0.007548 | 0.0036113 | -0.00031535 | -0.0014953 | -59.8526 | 62.4985 | -60.8185 | 0.036621 | 0.013733 | 0.004578 | 0.018311 | 0.20599 | 0.23804 | -0.28839 | -0.36163 | 0.10986 | 0.60425 | 60.4935 | -62.3749 | 60.1685 | -62.1506 | 0.96588
1180.75 | 123.1201 | -60.4385 | 62.3703 | 0.051226 | 0.020376 | 0.019572 | -0.0016378 | -2.0324e-05 | -0.0015972 | -0.0021361 | -59.9716 | 62.3749 | -60.8322 | 0.018311 | 0.045776 | 0.032043 | -0.050354 | 0.22888 | 0.20599 | -0.27924 | -0.39368 | 0.004578 | 0.46692 | 60.4568 | -62.3245 | 60.1593 | -62.1643 | 0.8606
1181.7344 | 123.0286 | -60.4935 | 62.3611 | 0.066485 | 0.022512 | 0.022135 | 0.004771 | 0.0036113 | -0.00095615 | -0.0021361 | -59.8663 | 62.5031 | -60.8139 | 0.018311 | 0.004578 | -0.041199 | 0.018311 | 0.1831 | 0.23346 | -0.29297 | -0.32044 | 0.14191 | 0.62714 | 60.5118 | -62.3566 | 60.2005 | -62.1277 | 0.94757
1182.7656 | 123.0927 | -60.466 | 62.3245 | 0.089373 | 0.017171 | 0.018504 | -0.0016378 | 0.0025431 | 0.00053925 | -0.00021353 | -59.9442 | 62.3566 | -60.8368 | 0.009155 | 0.032043 | 0.041199 | -0.07782 | 0.23346 | 0.20142 | -0.28381 | -0.37079 | 0.032043 | 0.52185 | 60.4752 | -62.2925 | 60.1822 | -62.1231 | 0.89264
1183.7344 | 123.0469 | -60.5026 | 62.3749 | -0.017439 | 0.022085 | 0.026408 | 0.010325 | 0.0029705 | 0.0035298 | -0.00064093 | -59.8389 | 62.4985 | -60.8139 | -0.068665 | 0.068665 | 0.15106 | 0.073242 | 0.24261 | 0.20599 | -0.30212 | -0.31128 | 0.1236 | 0.66376 | 60.434 | -62.3062 | 60.2005 | -62.1689 | 0.97504
1184.7656 | 123.0698 | -60.5072 | 62.3795 | -0.13188 | 0.018453 | 0.018077 | 0.0066936 | 0.0036113 | -0.0013834 | -0.0023499 | -59.8709 | 62.4664 | -60.8459 | 0.045776 | 0.045776 | 0.073242 | 0.10071 | 0.27924 | 0.27008 | -0.20599 | -0.33875 | 0.086975 | 0.63629 | 60.553 | -62.3337 | 60.3012 | -62.1094 | 0.97504
1185.7344 | 123.0606 | -60.4935 | 62.3291 | 0.051226 | 0.023153 | 0.02064 | 0.0062662 | 0.0038249 | -0.0011698 | -0.0012817 | -59.816 | 62.4756 | -60.8276 | 0.027466 | 0.018311 | 0.004578 | 0.004578 | 0.17395 | 0.23346 | -0.29755 | -0.33417 | 0.14648 | 0.67749 | 60.5209 | -62.3108 | 60.1959 | -62.0956 | 1.0117
1186.7656 | 123.1705 | -60.4523 | 62.3383 | -0.032697 | 0.019094 | 0.017008 | -0.0033468 | 0.0021159 | -0.0020244 | 0.00042727 | -59.8846 | 62.3566 | -60.8597 | 0.073242 | 0.11444 | 0.12817 | -0.064087 | 0.32959 | 0.20599 | -0.24261 | -0.40741 | 0.01831 | 0.56763 | 60.5255 | -62.2238 | 60.2097 | -62.1323 | 0.97504
1187.7344 | 123.0652 | -60.5072 | 62.352 | -0.086103 | 0.020376 | 0.019999 | 0.0062662 | 0.0025431 | -0.00095615 | -0.0010681 | -59.7794 | 62.4573 | -60.8459 | 0.036621 | 0.045776 | 0.027466 | 0.059509 | 0.23804 | 0.24719 | -0.27008 | -0.33875 | 0.10529 | 0.72784 | 60.5438 | -62.3062 | 60.2371 | -62.1048 | 1.0666
1188.7656 | 123.1064 | -60.4935 | 62.3016 | 0.31063 | 0.020589 | 0.019572 | 0.0028484 | 0.00062048 | -0.00074255 | -0.0012817 | -59.816 | 62.3428 | -60.878 | 0.027466 | 0.059509 | 0.032043 | -0.16479 | 0.25635 | 0.16479 | -0.33875 | -0.38452 | 0.041198 | 0.67749 | 60.5209 | -62.2421 | 60.1547 | -62.1368 | 1.062
1189.7344 | 123.0789 | -60.5255 | 62.3428 | -0.032697 | 0.022725 | 0.019572 | 0.0084026 | 0.0040385 | -0.00052895 | -0.00042733 | -59.8068 | 62.4573 | -60.8597 | 0.045776 | 0.018311 | 0.036621 | 0.013733 | 0.21973 | 0.24719 | -0.27466 | -0.33417 | 0.11444 | 0.71869 | 60.5713 | -62.3245 | 60.2509 | -62.0956 | 1.0529
1190.75 | 123.0194 | -60.5438 | 62.352 | 0.19618 | 0.022512 | 0.022349 | 0.0077616 | 0.0091655 | 0.00032545 | -0.0029907 | -59.8343 | 62.4161 | -60.8688 | 0.28839 | 0.27924 | -0.15564 | -0.036621 | 0.28381 | 0.20599 | -0.34332 | -0.32501 | 0.064087 | 0.70953 | 60.8322 | -62.0728 | 60.2005 | -62.146 | 1.0345
1191.7344 | 123.0698 | -60.4935 | 62.3337 | -0.46757 | 0.024648 | 0.024058 | 0.009257 | 0.0029705 | 0.00118 | -0.0021361 | -59.7519 | 62.4481 | -60.878 | 0.018311 | 0.009155 | 0.004578 | 0.018311 | 0.20599 | 0.22888 | -0.28839 | -0.38452 | 0.11444 | 0.74158 | 60.5118 | -62.3245 | 60.2051 | -62.1048 | 1.1261
1192.7656 | 123.1018 | -60.4935 | 62.3108 | 0.21144 | 0.019521 | 0.017436 | -0.0052694 | 0.0040385 | -0.00031535 | -0.00064093 | -59.8389 | 62.3337 | -60.8871 | 0.018311 | 0.045776 | 0.045776 | -0.073242 | 0.21515 | 0.20599 | -0.29755 | -0.39368 | 0.022888 | 0.6546 | 60.5118 | -62.265 | 60.1959 | -62.1048 | 1.0483
1193.7344 | 123.0835 | -60.5301 | 62.3337 | -0.11662 | 0.022298 | 0.019145 | 0.0049846 | 0.0031841 | 0.0013936 | -0.00021353 | -59.7107 | 62.471 | -60.8597 | 0.054932 | 0.054932 | 0.050354 | 0.041199 | 0.24261 | 0.25177 | -0.27008 | -0.32959 | 0.13733 | 0.8194 | 60.585 | -62.2787 | 60.26 | -62.0819 | 1.149
1194.7656 | 123.0286 | -60.5438 | 62.3337 | 0.081743 | 0.022939 | 0.022776 | 0.0073344 | 0.0038249 | -0.0033062 | 0.0012817 | -59.7519 | 62.4435 | -60.8917 | -0.013733 | -0.022888 | -0.054932 | 0.032043 | 0.12817 | 0.24261 | -0.31586 | -0.3479 | 0.10986 | 0.79193 | 60.5301 | -62.3566 | 60.228 | -62.0911 | 1.1398
1195.7344 | 123.0927 | -60.5164 | 62.3291 | -0.0098092 | 0.020589 | 0.022776 | 0.0054118 | 0.0040385 | -0.00074255 | 0.00042727 | -59.7015 | 62.439 | -60.8688 | 0.022888 | 0.027466 | 0.041199 | 0.022888 | 0.22888 | 0.24719 | -0.27924 | -0.35248 | 0.10986 | 0.81482 | 60.5392 | -62.3016 | 60.2371 | -62.0819 | 1.1673
1196.75 | 123.0698 | -60.5118 | 62.2742 | 0.21907 | 0.024007 | 0.020213 | 0.0043436 | 0.0051067 | 0.00053925 | 0.00021367 | -59.7565 | 62.4161 | -60.8963 | -0.050354 | -0.041199 | -0.054932 | -0.086975 | 0.11902 | 0.21057 | -0.3479 | -0.38452 | 0.14191 | 0.75531 | 60.4614 | -62.3154 | 60.1639 | -62.0636 | 1.1398
1197.7344 | 123.0606 | -60.5301 | 62.2971 | -0.10899 | 0.022298 | 0.019358 | 0.0062662 | 0.0031841 | 0.00032545 | 0.00021367 | -59.6649 | 62.4435 | -60.8734 | 0.059509 | 0.032043 | 0.041199 | 0.041199 | 0.24719 | 0.25177 | -0.27008 | -0.34332 | 0.14648 | 0.86517 | 60.5896 | -62.265 | 60.26 | -62.0453 | 1.2085
1198.7656 | 123.1384 | -60.5347 | 62.2742 | 0.10463 | 0.019521 | 0.020426 | -0.0009968 | 0.0051067 | -0.0026652 | 0.0023499 | -59.6466 | 62.3062 | -60.9009 | 0.041199 | 0.041199 | 0.032043 | -0.16022 | 0.21973 | 0.18768 | -0.32959 | -0.36621 | 0.032043 | 0.88806 | 60.5759 | -62.233 | 60.2051 | -62.0865 | 1.2543
1199.75 | 123.111 | -60.5392 | 62.2559 | 0.1733 | 0.019521 | 0.02064 | 0.000712 | 0.0023295 | 0.00075285 | -0.0017089 | -59.6512 | 62.3199 | -60.8963 | 0.009155 | 0.022888 | 0.027466 | -0.15106 | 0.20599 | 0.17853 | -0.35248 | -0.35706 | 0.064087 | 0.88806 | 60.5484 | -62.233 | 60.1868 | -62.0773 | 1.2451
1200.7656 | 123.1659 | -60.4935 | 62.265 | 0.27248 | 0.022298 | 0.02064 | 0.0009258 | 0.0019023 | 0.0018208 | 0.00042727 | -59.5871 | 62.3062 | -60.8871 | -0.24719 | -0.059509 | 0.48981 | -0.036621 | 0.15106 | 0.14191 | -0.4303 | -0.39368 | 0.041198 | 0.90637 | 60.2463 | -62.3245 | 60.0632 | -62.1231 | 1.3
1201.7344 | 123.056 | -60.5347 | 62.3016 | -0.10136 | 0.022725 | 0.024272 | 0.0056254 | 0.00083408 | -0.00074255 | 0.0010681 | -59.5642 | 62.4023 | -60.9009 | 0.054932 | 0.032043 | 0.054932 | 0.027466 | 0.23804 | 0.2655 | -0.2655 | -0.36621 | 0.10071 | 0.97046 | 60.5896 | -62.2696 | 60.2692 | -62.0361 | 1.3367
1202.7656 | 123.0927 | -60.5164 | 62.2787 | 0.11989 | 0.020589 | 0.020426 | -0.0018514 | 0.0031841 | -0.00031535 | 6.6667e-08 | -59.6146 | 62.2879 | -60.91 | 0.013733 | 0.032043 | 0.036621 | -0.073242 | 0.24261 | 0.21515 | -0.27008 | -0.39368 | 0.009155 | 0.90179 | 60.5301 | -62.2467 | 60.2463 | -62.0636 | 1.2955
1203.7344 | 123.0423 | -60.5576 | 62.3245 | -0.11662 | 0.022085 | 0.022349 | 0.0051982 | 0.00083408 | -0.002238 | -0.0012817 | -59.5413 | 62.3932 | -60.8871 | 0.032043 | 0.022888 | 0.059509 | 0.09613 | 0.27008 | 0.27008 | -0.20599 | -0.32959 | 0.068664 | 1.0162 | 60.5896 | -62.3016 | 60.3516 | -62.0544 | 1.3458
1204.7656 | 123.111 | -60.5438 | 62.2467 | 0.15041 | 0.022512 | 0.021067 | -0.000356 | 0.0031841 | -0.00010175 | 0.00085447 | -59.5001 | 62.2604 | -60.9329 | 0.022888 | 0.022888 | 0.013733 | -0.16479 | 0.23346 | 0.16479 | -0.33875 | -0.3891 | 0.013733 | 1.0437 | 60.5667 | -62.2238 | 60.2051 | -62.0819 | 1.4328
1205.7344 | 123.0515 | -60.5759 | 62.2971 | -0.11662 | 0.024862 | 0.024272 | 0.0084026 | 0.0040385 | -0.0015972 | -0.0014953 | -59.4315 | 62.384 | -60.9329 | 0.054932 | 0.032043 | 0.050354 | 0.073242 | 0.27924 | 0.25635 | -0.2655 | -0.35705 | 0.086975 | 1.1444 | 60.6308 | -62.265 | 60.3104 | -62.0407 | 1.5015
1206.7656 | 123.1201 | -60.585 | 62.2147 | 0.11989 | 0.018239 | 0.019145 | -0.0048422 | 0.0023295 | -0.002238 | -0.0010681 | -59.491 | 62.2742 | -60.9329 | 0.018311 | 0.032043 | 0.018311 | -0.064087 | 0.22888 | 0.21973 | -0.28381 | -0.3479 | 0.059509 | 1.0941 | 60.6033 | -62.1826 | 60.3012 | -61.9949 | 1.442
1207.7344 | 123.0331 | -60.6308 | 62.2513 | -0.18529 | 0.021871 | 0.022135 | 0.0039164 | 0.00019328 | -0.00031535 | -0.0010681 | -59.4727 | 62.3611 | -60.9787 | 0.16479 | -0.24261 | -0.32044 | 0.21515 | 0.24261 | 0.28839 | -0.16937 | -0.3479 | 0.10986 | 1.1581 | 60.7956 | -62.4939 | 60.4614 | -61.9629 | 1.506
1208.7656 | 123.1201 | -60.6125 | 62.178 | 0.28011 | 0.02358 | 0.022135 | 0.0056254 | 0.0027567 | -0.00010175 | 0.00064087 | -59.3994 | 62.2879 | -60.9695 | 0.045776 | 0.022888 | -0.041199 | -0.18768 | 0.17853 | 0.17853 | -0.37994 | -0.35706 | 0.10986 | 1.2131 | 60.6583 | -62.1552 | 60.2325 | -61.9995 | 1.5701
1209.7344 | 123.0377 | -60.6583 | 62.2559 | -0.14714 | 0.02358 | 0.025767 | 0.00648 | -0.00087492 | -0.0013834 | -0.00064093 | -59.4177 | 62.3199 | -60.9879 | 0.041199 | 0.032043 | 0.027466 | 0.11902 | 0.24261 | 0.28839 | -0.2243 | -0.32959 | 0.064087 | 1.2405 | 60.6995 | -62.2238 | 60.434 | -61.9675 | 1.5701
1210.7656 | 123.1064 | -60.6125 | 62.2101 | 0.051226 | 0.02123 | 0.019358 | -0.0033468 | 0.0012615 | -0.0020244 | -0.00085453 | -59.4223 | 62.2284 | -60.9695 | 0.018311 | 0.032043 | 0.032043 | -0.073242 | 0.23346 | 0.20142 | -0.27008 | -0.35706 | 0.018311 | 1.1902 | 60.6308 | -62.178 | 60.3424 | -62.0087 | 1.5472
1211.7344 | 123.024 | -60.6216 | 62.2284 | -0.17766 | 0.020803 | 0.023417 | 0.0049846 | 0.00019328 | -0.00052895 | 6.6667e-08 | -59.2438 | 62.3291 | -60.9879 | 0.041199 | 0.027466 | -0.050354 | 0.11444 | 0.27924 | 0.27466 | -0.24261 | -0.36621 | 0.10071 | 1.3779 | 60.6628 | -62.2009 | 60.379 | -61.9537 | 1.7441
1212.7656 | 123.143 | -60.6125 | 62.1643 | 0.16567 | 0.024221 | 0.019145 | 0.0056254 | 0.0014751 | 0.0013936 | -0.00064093 | -59.2896 | 62.2467 | -60.9741 | 0.036621 | 0.009155 | -0.004578 | -0.17395 | 0.21057 | 0.15564 | -0.37079 | -0.36163 | 0.082397 | 1.3229 | 60.6491 | -62.1552 | 60.2417 | -62.0087 | 1.6846
1213.7344 | 123.0469 | -60.6079 | 62.2238 | -0.19291 | 0.021444 | 0.019145 | 0.003062 | -0.00066112 | -0.0024516 | -0.0010681 | -59.3445 | 62.3199 | -60.9924 | 0.018311 | 0.013733 | 0.10071 | 0.63629 | 0.29755 | 0.32044 | -0.12817 | -0.38452 | 0.09613 | 1.2634 | 60.6262 | -62.2101 | 60.4797 | -61.9034 | 1.648
1214.7656 | 123.143 | -60.6079 | 62.178 | 0.29537 | 0.024434 | 0.023844 | 0.00413 | 0.0019023 | -0.00010175 | -0.0017089 | -59.2575 | 62.2147 | -60.9604 | 0.054932 | 0.041199 | 0.018311 | -0.19684 | 0.24719 | 0.16022 | -0.36621 | -0.35248 | 0.036621 | 1.3504 | 60.6628 | -62.1368 | 60.2417 | -62.0178 | 1.7029
1215.7344 | 123.0423 | -60.6262 | 62.2513 | 0.066485 | 0.024434 | 0.016795 | 0.0045574 | 0.0019023 | -0.00010175 | 0.0012817 | -59.2941 | 62.3428 | -60.9924 | 0.036621 | 0.018311 | 0.041199 | 0.11444 | 0.22888 | 0.28381 | -0.2243 | -0.36621 | 0.091552 | 1.3321 | 60.6628 | -62.233 | 60.4019 | -61.9675 | 1.6983
1216.7656 | 123.1155 | -60.6354 | 62.1964 | 0.14278 | 0.023153 | 0.015086 | -0.0016378 | 0.0021159 | 0.00118 | -0.0010681 | -59.3079 | 62.1872 | -61.0107 | 0.004578 | 0.032043 | 0.018311 | -0.064087 | 0.25177 | 0.19684 | -0.28381 | -0.37537 | -0.009155 | 1.3275 | 60.64 | -62.1643 | 60.3516 | -61.9995 | 1.7029
1217.7344 | 123.0469 | -60.6537 | 62.2284 | 1.6915 | 0.023794 | 0.018931 | 0.0034892 | 0.00040688 | -0.00095615 | -0.0032043 | -59.2621 | 62.2925 | -61.0153 | 0.022888 | 0.045776 | 0.032043 | 0.13275 | 0.2655 | 0.25635 | -0.25635 | -0.36163 | 0.064086 | 1.3916 | 60.6766 | -62.1826 | 60.3973 | -61.972 | 1.7532
1218.75 | 123.0103 | -60.6949 | 62.2055 | 0.12752 | 0.026784 | 0.02064 | 0.0088298 | 0.0031841 | 0.00011185 | -0.0010681 | -59.2117 | 62.3062 | -61.0291 | -0.050354 | -0.073242 | -0.091553 | 0.018311 | 0.10071 | 0.21515 | -0.36163 | -0.33417 | 0.10071 | 1.4832 | 60.6445 | -62.2787 | 60.3333 | -61.9904 | 1.8173
1219.7344 | 123.0194 | -60.64 | 62.2147 | -0.19291 | 0.024007 | 0.021281 | 0.002421 | 0.0021159 | 0.00011185 | 6.6667e-08 | -59.2209 | 62.2879 | -61.0153 | -0.13275 | 0.068665 | 0.07782 | 0.009155 | 0.20142 | 0.27466 | -0.19684 | -0.37537 | 0.073242 | 1.4191 | 60.5072 | -62.146 | 60.4431 | -61.94 | 1.7944
1220.7656 | 123.0927 | -60.6537 | 62.178 | 0.13515 | 0.021016 | 0.018931 | -0.0012106 | -2.0324e-05 | 0.00032545 | 0.00042727 | -59.2026 | 62.2055 | -61.0291 | 0.027466 | 0.045776 | 0.013733 | -0.086975 | 0.22888 | 0.20599 | -0.27008 | -0.37537 | 0.027465 | 1.4511 | 60.6812 | -62.1323 | 60.3836 | -61.972 | 1.8265
1221.7344 | 123.0011 | -60.6583 | 62.233 | -0.18529 | 0.021444 | 0.024058 | 0.00413 | 0.0014751 | -0.00074255 | -0.0017089 | -59.1843 | 62.2833 | -61.0062 | 0.036621 | 0.036621 | 0.045776 | 0.32959 | 0.67749 | 0.30212 | -0.12817 | -0.3479 | 0.050354 | 1.474 | 60.6949 | -62.1964 | 60.5301 | -61.9308 | 1.8219
1222.7656 | 123.1247 | -60.6445 | 62.178 | 0.28011 | 0.024648 | 0.021281 | 0.00648 | 0.0053203 | 0.0020344 | -0.0019225 | -59.1248 | 62.2192 | -61.0107 | 0.050354 | 0.041199 | 0 | -0.17395 | 0.16937 | 0.16479 | -0.37537 | -0.36621 | 0.041198 | 1.5198 | 60.6949 | -62.1368 | 60.2692 | -62.0132 | 1.886
1223.7344 | 123.0606 | -60.6583 | 62.2009 | -0.20054 | 0.022085 | 0.022776 | 0.0049846 | 0.0040385 | -0.00010175 | -0.00042733 | -59.1385 | 62.3154 | -61.0245 | 0.022888 | 0.013733 | 0.032043 | 0.11444 | 0.23346 | 0.27008 | -0.21515 | -0.36621 | 0.11444 | 1.5198 | 60.6812 | -62.1872 | 60.4431 | -61.9308 | 1.886
1224.7656 | 123.1384 | -60.64 | 62.1414 | 0.24959 | 0.025075 | 0.022563 | 0.0032756 | 0.0040385 | -0.00010175 | 0.00085447 | -59.0744 | 62.2147 | -61.0062 | 0.041199 | 0.032043 | 0.041199 | -0.18768 | 0.21515 | 0.15564 | -0.37537 | -0.36621 | 0.073243 | 1.5656 | 60.6812 | -62.1094 | 60.2646 | -61.9858 | 1.9318
1225.7344 | 123.0377 | -60.6445 | 62.2009 | -0.76512 | 0.02593 | 0.028117 | 0.003062 | -0.00087492 | -0.00074255 | 0.00085447 | -59.2346 | 62.2833 | -61.0336 | -0.032043 | -0.004578 | 0.064087 | 0.15106 | 0.23346 | 0.2655 | -0.25635 | -0.3891 | 0.082397 | 1.4099 | 60.6125 | -62.2055 | 60.3882 | -61.9354 | 1.799
1226.7656 | 123.1247 | -60.6216 | 62.1689 | 0.21907 | 0.024862 | 0.023204 | 0.003062 | 0.0040385 | 0.002248 | -0.00064093 | -59.0378 | 62.2375 | -61.0107 | 0.054932 | 0.032043 | 0.027466 | -0.20142 | 0.20599 | 0.15106 | -0.37079 | -0.3891 | 0.068665 | 1.5839 | 60.6766 | -62.1368 | 60.2509 | -62.0178 | 1.973
1227.7344 | 123.0148 | -60.6812 | 62.2101 | -0.18529 | 0.023794 | 0.020213 | 0.003062 | -0.0019429 | 0.00011185 | -0.00064093 | -59.0881 | 62.3291 | -61.0107 | 0.018311 | 0.018311 | -0.009155 | 0.54016 | 0.62714 | 0.30212 | -0.12817 | -0.32959 | 0.11902 | 1.593 | 60.6995 | -62.1918 | 60.553 | -61.908 | 1.9226
1228.7656 | 123.1705 | -60.6171 | 62.178 | -0.070844 | 0.024434 | 0.024912 | -0.002065 | -0.0017293 | 0.00011185 | -0.00085453 | -59.024 | 62.1872 | -60.9833 | 0.11444 | 0.14648 | 0.18768 | -0.050354 | 0.37994 | 0.23804 | -0.20142 | -0.36621 | 0.009155 | 1.593 | 60.7315 | -62.0316 | 60.4156 | -61.94 | 1.9592
1229.7344 | 123.0286 | -60.6445 | 62.2284 | 0.11989 | 0.02358 | 0.018077 | 0.0069072 | 0.00083408 | -0.00095615 | 0.00064087 | -59.0515 | 62.2879 | -61.0291 | 0.050354 | 0.022888 | 0.045776 | 0.10986 | 0.22888 | 0.28381 | -0.23346 | -0.38452 | 0.059509 | 1.593 | 60.6949 | -62.2055 | 60.4111 | -61.9446 | 1.9775
1230.7656 | 123.1338 | -60.6171 | 62.1506 | 0.24196 | 0.023794 | 0.02769 | 0.002421 | -0.00023392 | -0.0013834 | -0.0017089 | -58.9737 | 62.2009 | -60.997 | 0 | 0.068665 | 0.16937 | -0.21057 | 0.21515 | 0.18768 | -0.33417 | -0.37994 | 0.050354 | 1.6434 | 60.6171 | -62.0819 | 60.2829 | -61.9629 | 2.0233
1231.7344 | 122.9462 | -60.6216 | 62.233 | -0.17003 | 0.026143 | 0.022349 | 0.0045574 | 0.00019328 | 0.00032545 | -0.0019225 | -59.0378 | 62.2742 | -61.0245 | 0.013733 | 0.004578 | 0.032043 | 0.14648 | 0.37994 | 0.28839 | -0.13733 | -0.40283 | 0.041199 | 1.5839 | 60.6354 | -62.2284 | 60.4843 | -61.9446 | 1.9867
1232.7656 | 123.0881 | -60.6491 | 62.178 | 0.27248 | 0.025716 | 0.023631 | 0.007548 | 0.0040385 | -0.0015972 | -0.0023499 | -58.9737 | 62.233 | -61.0382 | -0.009155 | -0.027466 | -0.022888 | -0.12817 | 0.16479 | 0.16937 | -0.35248 | -0.3891 | 0.054931 | 1.6754 | 60.64 | -62.2055 | 60.2966 | -62.0087 | 2.0645
1233.7344 | 123.024 | -60.6812 | 62.2238 | -0.20054 | 0.024434 | 0.022135 | 0.0049846 | 0.0010477 | -0.0015972 | 6.6667e-08 | -59.0012 | 62.2971 | -61.0062 | 0.073242 | -0.013733 | -0.09613 | 0.17853 | 0.26093 | 0.26093 | -0.2243 | -0.32501 | 0.073242 | 1.68 | 60.7544 | -62.2375 | 60.4568 | -61.9629 | 2.005
1234.75 | 123.0148 | -60.6766 | 62.2192 | 0.074114 | 0.026998 | 0.025553 | 0.0081888 | 0.0027567 | -0.0020244 | -0.00085453 | -58.9417 | 62.3383 | -60.9924 | -0.009155 | -0.018311 | -0.064087 | 0.018311 | 0.13733 | 0.2243 | -0.31128 | -0.31586 | 0.11902 | 1.7349 | 60.6674 | -62.2375 | 60.3653 | -61.9949 | 2.0508
1235.7344 | 123.056 | -60.6262 | 62.2055 | -0.18529 | 0.023366 | 0.02769 | -0.0009968 | 0.00083408 | -0.0018108 | -0.0014953 | -58.9096 | 62.2192 | -60.9879 | 0.082397 | 0.091553 | 0.10529 | 0.082397 | 0.3067 | 0.27008 | -0.21515 | -0.36163 | 0.013733 | 1.7166 | 60.7086 | -62.114 | 60.4111 | -61.9354 | 2.0782
1236.7656 | 123.056 | -60.6445 | 62.1689 | 0.1733 | 0.025075 | 0.021708 | 0.0084026 | 0.0025431 | 0.00053925 | -0.00064093 | -58.9371 | 62.2742 | -61.0382 | -0.018311 | -0.045776 | -0.059509 | -0.09613 | 0.11444 | 0.1831 | -0.36163 | -0.39368 | 0.10529 | 1.7075 | 60.6262 | -62.2147 | 60.2829 | -61.9858 | 2.1011
1237.7344 | 123.0469 | -60.6491 | 62.2238 | -0.20817 | 0.022725 | 0.021281 | 0.000712 | 0.00083408 | -0.0013834 | -0.0010681 | -58.9142 | 62.2375 | -61.0016 | 0.036621 | 0.059509 | 0.086975 | 0.10986 | 0.2655 | 0.27008 | -0.19226 | -0.35248 | 0.013733 | 1.7349 | 60.6857 | -62.1643 | 60.4568 | -61.9537 | 2.0874
1238.75 | 123.0331 | -60.6674 | 62.2147 | 0.0054493 | 0.027639 | 0.025981 | 0.0079752 | 0.0025431 | -0.00052895 | -0.00085453 | -58.8455 | 62.3291 | -60.997 | 0.036621 | 0.022888 | 0.032043 | 0.004578 | 0.2243 | 0.24719 | -0.27466 | -0.32959 | 0.11444 | 1.8219 | 60.704 | -62.1918 | 60.3928 | -61.9675 | 2.1515
1239.7344 | 123.111 | -60.6445 | 62.1735 | -0.15477 | 0.024221 | 0.018077 | -0.0031332 | 0.00062048 | 0.002248 | 0.00021367 | -58.8959 | 62.2101 | -60.997 | 0.086975 | 0.1236 | 0.15564 | 0.027466 | 0.36163 | 0.25177 | -0.21057 | -0.35248 | 0.036621 | 1.7487 | 60.7315 | -62.0499 | 60.434 | -61.9217 | 2.1011
1240.7656 | 123.1384 | -60.6445 | 62.1323 | 0.28011 | 0.025075 | 0.02299 | 0.0039164 | 0.0031841 | 0.00096645 | -0.00064093 | -58.8501 | 62.1918 | -60.9787 | 0.041199 | 0.059509 | 0.036621 | -0.20142 | 0.21973 | 0.15564 | -0.36163 | -0.33417 | 0.059509 | 1.7944 | 60.6857 | -62.0728 | 60.2829 | -61.9766 | 2.1286
1241.7344 | 123.0698 | -60.6308 | 62.1826 | -0.14714 | 0.021871 | 0.026408 | -0.0029196 | -0.0023701 | 0.0016072 | -0.00021353 | -58.8501 | 62.1872 | -60.9924 | 0.1236 | 0.14191 | 0.17853 | -0.013733 | 0.58594 | 0.23804 | -0.17853 | -0.36163 | 0.004578 | 1.7807 | 60.7544 | -62.0407 | 60.4523 | -61.9446 | 2.1423
1242.7656 | 123.0423 | -60.6491 | 62.1826 | -0.32261 | 0.027639 | 0.024058 | 0.0077616 | 0.0012615 | -0.00010175 | 6.6667e-08 | -58.8593 | 62.2879 | -61.0199 | -0.050354 | -0.050354 | -0.091553 | -0.027466 | 0.11902 | 0.21057 | -0.32501 | -0.37079 | 0.10529 | 1.7899 | 60.5988 | -62.233 | 60.3241 | -61.972 | 2.1606
1243.7344 | 123.1155 | -60.6308 | 62.1552 | -0.13188 | 0.021871 | 0.019786 | -0.003774 | -0.0045065 | 0.0020344 | 0.0012817 | -58.8043 | 62.1964 | -61.0107 | -0.26093 | -0.1831 | 0.24261 | -0.041199 | 0.1831 | 0.22888 | -0.22888 | -0.37994 | 0.041199 | 1.8265 | 60.3699 | -62.3383 | 60.4019 | -61.9263 | 2.2064
1244.7656 | 123.1293 | -60.6583 | 62.1597 | 0.25722 | 0.026357 | 0.022776 | 0.004771 | -2.0324e-05 | 0.0031026 | -0.00064093 | -58.7677 | 62.1918 | -60.997 | 0.045776 | 0.050354 | -0.004578 | -0.68207 | 0.14648 | 0.13275 | -0.44403 | -0.33874 | 0.032043 | 1.8906 | 60.704 | -62.1094 | 60.2142 | -62.027 | 2.2293
1245.7344 | 123.1705 | -60.6171 | 62.1597 | -0.11662 | 0.022085 | 0.01594 | 0.001353 | -0.0010885 | -0.00010175 | -0.00021353 | -58.754 | 62.1872 | -60.9787 | 0.13733 | 0.12817 | 0.15564 | -0.036621 | 0.36163 | 0.25177 | -0.19684 | -0.36163 | 0.027466 | 1.8631 | 60.7544 | -62.0316 | 60.4202 | -61.908 | 2.2247
1246.7656 | 123.0423 | -60.6949 | 62.1826 | 0.013079 | 0.027212 | 0.028117 | 0.010539 | 0.0021159 | -0.00052895 | -0.0032043 | -58.7082 | 62.2971 | -61.0153 | 0.018311 | -0.027466 | -0.032043 | -0.004578 | 0.16022 | 0.22888 | -0.28381 | -0.32044 | 0.11444 | 1.9867 | 60.7132 | -62.2101 | 60.4111 | -61.9537 | 2.3071
1247.7344 | 123.1338 | -60.6125 | 62.1506 | -0.10899 | 0.022298 | 0.019999 | -0.0035604 | 0.00062048 | 0.00053925 | -0.0019225 | -58.699 | 62.1643 | -60.997 | 0.10071 | 0.12817 | 0.15564 | -0.050354 | 0.38452 | 0.23804 | -0.21057 | -0.38452 | 0.013733 | 1.9135 | 60.7132 | -62.0224 | 60.4019 | -61.9125 | 2.298
1248.7656 | 123.0286 | -60.6995 | 62.178 | 0.25722 | 0.02828 | 0.027049 | 0.0039164 | -2.0324e-05 | -0.0013834 | -0.0014953 | -58.6121 | 62.2559 | -61.0382 | 0.036621 | 0.068665 | -0.10986 | -0.064087 | 0.16479 | 0.23346 | -0.32044 | -0.33874 | 0.077819 | 2.0874 | 60.7361 | -62.1094 | 60.379 | -61.9446 | 2.4261
1249.7344 | 123.1201 | -60.6537 | 62.1597 | 0.058855 | 0.023794 | 0.020426 | -0.0014242 | -2.0324e-05 | -0.00095615 | -0.00085453 | -58.7311 | 62.1643 | -61.0199 | 0.050354 | 0.07782 | 0.07782 | -0.064087 | 0.29755 | 0.21973 | -0.2655 | -0.36621 | 0.004578 | 1.9226 | 60.704 | -62.0819 | 60.3882 | -61.94 | 2.2888
1250.7656 | 123.056 | -60.6857 | 62.1597 | -0.070844 | 0.030416 | 0.026835 | 0.0079752 | 0.0019023 | -0.0013834 | -0.00042733 | -58.6945 | 62.2696 | -61.0291 | -0.041199 | -0.041199 | -0.068665 | -0.027466 | 0.1236 | 0.21973 | -0.32959 | -0.34332 | 0.10986 | 1.9913 | 60.6445 | -62.2009 | 60.3561 | -61.94 | 2.3346
1251.7344 | 123.1338 | -60.6445 | 62.1368 | 0.028338 | 0.022939 | 0.022135 | -0.0001424 | -0.00087492 | -0.0015972 | -0.00064093 | -58.6716 | 62.146 | -61.0245 | 0.073242 | 0.09613 | 0.086975 | -0.073242 | 0.3067 | 0.22888 | -0.26093 | -0.37994 | 0.009155 | 1.973 | 60.7178 | -62.0407 | 60.3836 | -61.908 | 2.3529
1252.7656 | 123.056 | -60.6583 | 62.1826 | -0.0021797 | 0.027852 | 0.024699 | 0.0094706 | 0.0010477 | -0.0026652 | -0.00042733 | -58.5297 | 62.2559 | -61.0153 | 0.059509 | 0.018311 | 0.022888 | 0.027466 | 0.23346 | 0.23804 | -0.27924 | -0.35706 | 0.073242 | 2.1286 | 60.7178 | -62.1643 | 60.379 | -61.9446 | 2.4857
1253.7344 | 123.1064 | -60.6674 | 62.1506 | 0.074114 | 0.024648 | 0.02064 | 7.12e-05 | 0.0012615 | -0.0011698 | 0.0010681 | -58.6121 | 62.1597 | -61.0153 | 0.022888 | 0.059509 | 0.045776 | -0.073242 | 0.25635 | 0.21973 | -0.27924 | -0.3479 | 0.009155 | 2.0554 | 60.6903 | -62.0911 | 60.3882 | -61.9308 | 2.4033
1254.7656 | 123.0286 | -60.7086 | 62.146 | 0.27248 | 0.028493 | 0.024699 | 0.0049846 | 0.0025431 | 0.00118 | -0.0021361 | -58.5297 | 62.233 | -61.0886 | 0.068665 | 0.022888 | -0.15564 | -0.018311 | 0.16479 | 0.22888 | -0.32501 | -0.37994 | 0.086975 | 2.179 | 60.7773 | -62.1231 | 60.3836 | -61.9171 | 2.5589
1255.7344 | 123.0835 | -60.6766 | 62.1414 | 0.058855 | 0.02358 | 0.02299 | -0.0005696 | -2.0324e-05 | 0.00075285 | -0.0019225 | -58.5159 | 62.1597 | -61.0153 | 0.027466 | 0.027466 | 0.036621 | -0.064087 | 0.24719 | 0.20142 | -0.28839 | -0.33875 | 0.018311 | 2.1606 | 60.704 | -62.114 | 60.3882 | -61.94 | 2.4994
1256.7656 | 123.0148 | -60.6857 | 62.1506 | 0.18855 | 0.029775 | 0.027476 | 0.0088298 | 0.0014751 | -0.00010175 | -0.0017089 | -58.4747 | 62.2879 | -61.0519 | -0.041199 | -0.07782 | -0.10529 | -0.004578 | 0.09613 | 0.21057 | -0.36163 | -0.36621 | 0.13733 | 2.211 | 60.6445 | -62.2284 | 60.3241 | -61.94 | 2.5772
1257.7344 | 123.0972 | -60.6857 | 62.1231 | 0.074114 | 0.024648 | 0.022563 | -0.0027058 | -0.00023392 | -0.0048014 | -0.00085453 | -58.4335 | 62.1506 | -61.0291 | 0.20599 | 0.050354 | -0.14191 | -0.13733 | 0.21057 | 0.21515 | -0.2655 | -0.34332 | 0.027466 | 2.2522 | 60.8917 | -62.0728 | 60.4202 | -61.908 | 2.5955
1258.7656 | 123.0789 | -60.6995 | 62.1826 | 0.21144 | 0.030843 | 0.02534 | 0.0077616 | 0.0029705 | -0.00031535 | -0.0017089 | -58.3603 | 62.2742 | -61.0428 | -0.054932 | -0.064087 | -0.10529 | -0.34332 | -0.50354 | 0.1831 | -0.41199 | -0.34332 | 0.091553 | 2.3392 | 60.6445 | -62.2467 | 60.2875 | -61.9995 | 2.6825
1259.7344 | 123.0881 | -60.6628 | 62.1414 | 0.11226 | 0.025716 | 0.021708 | -0.000356 | -0.0010885 | -0.0013834 | 0.0021363 | -58.3328 | 62.1689 | -61.0336 | 0.013733 | 0.022888 | 0.022888 | -0.073242 | 0.23804 | 0.21057 | -0.27466 | -0.37079 | 0.027466 | 2.33 | 60.6766 | -62.1185 | 60.3882 | -61.9308 | 2.7008
1260.7656 | 123.1384 | -60.6445 | 62.1002 | -0.086103 | 0.026357 | 0.025126 | -0.0012106 | -0.0010885 | -0.0011698 | -0.0017089 | -58.2275 | 62.1506 | -61.0153 | 0.10529 | 0.1236 | 0.14648 | -0.086975 | 0.37537 | 0.20599 | -0.20142 | -0.37079 | 0.050354 | 2.417 | 60.7498 | -61.9766 | 60.4431 | -61.8942 | 2.7878
1261.7344 | 123.0927 | -60.6491 | 62.146 | 0.11989 | 0.027212 | 0.021708 | 0.0009258 | -2.0324e-05 | -0.0013834 | -0.0017089 | -58.2275 | 62.146 | -61.0107 | 0.013733 | 0.041199 | 0.041199 | -0.068665 | 0.23804 | 0.18768 | -0.27008 | -0.36163 | 0 | 2.4216 | 60.6628 | -62.1048 | 60.379 | -61.9583 | 2.7832
1262.7656 | 123.0194 | -60.6583 | 62.178 | -0.17003 | 0.025075 | 0.021495 | 0.0088298 | -0.0010885 | -0.0030924 | -0.0025635 | -58.168 | 62.2513 | -61.0291 | -0.054932 | -0.013733 | 0.086975 | 0.082397 | 0.17395 | 0.25177 | -0.23346 | -0.37079 | 0.073242 | 2.4902 | 60.6033 | -62.1918 | 60.4248 | -61.9263 | 2.861
1263.7344 | 123.111 | -60.672 | 62.1185 | 0.23433 | 0.026357 | 0.025553 | -0.0012106 | 0.0023295 | -0.0020244 | -0.00064093 | -58.049 | 62.1368 | -61.0245 | 0.045776 | 0.022888 | 0.018311 | -0.15106 | 0.23804 | 0.17395 | -0.33417 | -0.35248 | 0.018311 | 2.623 | 60.7178 | -62.0956 | 60.3378 | -61.9446 | 2.9755
1264.7656 | 123.0057 | -60.704 | 62.146 | 0.15041 | 0.030416 | 0.031321 | 0.010752 | 0.0023295 | -0.00095615 | -0.00064093 | -57.9987 | 62.233 | -61.0199 | -0.045776 | -0.068665 | -0.09613 | 0.004578 | 0.086975 | 0.21515 | -0.37079 | -0.31586 | 0.086975 | 2.7054 | 60.6583 | -62.2147 | 60.3333 | -61.9308 | 3.0212
1265.7344 | 123.0011 | -60.6903 | 62.1597 | -0.19291 | 0.02358 | 0.020854 | 0.0019938 | 0.0023295 | -0.0013834 | -0.0014953 | -57.9758 | 62.2192 | -61.0336 | 0.027466 | 0.018311 | 0.041199 | 0.15564 | 0.28839 | 0.27466 | -0.1831 | -0.34332 | 0.059509 | 2.7145 | 60.7178 | -62.1414 | 60.5072 | -61.8851 | 3.0579
1266.75 | 123.1522 | -60.6583 | 62.1368 | -0.1624 | 0.025075 | 0.02534 | 0.0004984 | 0.0014751 | -0.002238 | 0.00042727 | -57.8659 | 62.1643 | -61.0245 | 0.13733 | 0.13733 | 0.15106 | -0.059509 | 0.36621 | 0.23804 | -0.20599 | -0.36621 | 0.027466 | 2.7924 | 60.7956 | -61.9995 | 60.4523 | -61.8988 | 3.1586
1267.7344 | 123.1155 | -60.6583 | 62.1368 | 0.24196 | 0.029775 | 0.02534 | 0.0037028 | 0.0027567 | -0.00074255 | -0.00064093 | -57.7972 | 62.146 | -61.0107 | 0.032043 | 0.027466 | 0.041199 | -0.17395 | 0.24261 | 0.16479 | -0.33417 | -0.35248 | 0.009155 | 2.861 | 60.6903 | -62.1094 | 60.3241 | -61.972 | 3.2135
1268.7656 | 123.0148 | -60.6857 | 62.1735 | 1.4169 | 0.029775 | 0.025553 | 0.0079752 | 0.00019328 | -0.0013834 | -0.00064093 | -57.7927 | 62.233 | -61.0336 | 0.009155 | 0.054932 | 0.050354 | 0.14191 | 0.2655 | 0.2655 | -0.24719 | -0.3479 | 0.059509 | 2.8931 | 60.6949 | -62.1185 | 60.4385 | -61.908 | 3.241
1269.7344 | 123.143 | -60.6628 | 62.1414 | 0.26485 | 0.027212 | 0.024058 | 0.0054118 | 0.0038249 | -0.0028788 | -0.0023499 | -57.6462 | 62.146 | -61.0107 | 0.25635 | 0.027466 | -0.041199 | -0.054932 | 0.28839 | 0.16022 | -0.33417 | -0.3479 | 0.004578 | 3.0167 | 60.9192 | -62.114 | 60.3287 | -61.9812 | 3.3646
1270.7656 | 123.024 | -60.6903 | 62.1643 | 0.081743 | 0.03127 | 0.024058 | 0.0096842 | 0.0029705 | -0.0011698 | -0.00085453 | -57.5912 | 62.2101 | -61.0336 | 0 | -0.022888 | -0.027466 | 0.022888 | 0.14191 | 0.22888 | -0.3067 | -0.34332 | 0.045776 | 3.0991 | 60.6903 | -62.1872 | 60.3836 | -61.9354 | 3.4424
1271.7344 | 123.1247 | -60.6491 | 62.1048 | 0.29537 | 0.029989 | 0.030467 | 0.0011394 | 0.0040385 | -0.0035198 | -0.0017089 | -57.4905 | 62.1506 | -61.0153 | 0.045776 | 0.054932 | 0.032043 | -0.19684 | 0.2243 | 0.16022 | -0.33417 | -0.36621 | 0.045777 | 3.1586 | 60.6949 | -62.0499 | 60.3149 | -61.9446 | 3.5248
1272.7656 | 123.1247 | -60.6674 | 62.1185 | -0.1624 | 0.027639 | 0.025553 | -0.0009968 | -0.00066112 | 0.00032545 | -0.0019225 | -57.4402 | 62.1597 | -61.0153 | 0.35706 | -0.20142 | -0.41657 | 0.027466 | 0.41199 | 0.23804 | -0.20599 | -0.3479 | 0.041199 | 3.2272 | 61.0245 | -62.3199 | 60.4614 | -61.8805 | 3.5751
1273.7344 | 123.1201 | -60.6766 | 62.1323 | 0.28774 | 0.03127 | 0.030253 | 0.0056254 | 0.0016887 | 0.00053925 | 0.0012817 | -57.3669 | 62.1643 | -61.0291 | -0.10986 | 0.31128 | 0.39368 | -0.25635 | 0.21515 | 0.16022 | -0.40283 | -0.35248 | 0.032044 | 3.3096 | 60.5667 | -61.821 | 60.2737 | -61.972 | 3.6621
1274.7344 | 123.0515 | -60.6949 | 62.0728 | 0.31063 | 0.030629 | 0.027903 | 0.0073344 | 0.0038249 | -0.0015972 | -0.0012817 | -57.2845 | 62.178 | -61.0153 | 0.045776 | 0.045776 | 0.036621 | -0.19684 | 0.23346 | 0.16937 | -0.36621 | -0.32044 | 0.10529 | 3.4103 | 60.7407 | -62.027 | 60.3287 | -61.9034 | 3.7308
1275.7656 | 123.0148 | -60.6903 | 62.1597 | 0.035967 | 0.028493 | 0.025126 | 0.0060526 | 0.00019328 | -0.0013834 | 6.6667e-08 | -57.2983 | 62.2513 | -61.0703 | 0.022888 | 0.027466 | 0.041199 | 0.11444 | 0.21973 | 0.29297 | -0.21515 | -0.37994 | 0.091553 | 3.392 | 60.7132 | -62.1323 | 60.4752 | -61.8668 | 3.772
1276.7344 | 123.1155 | -60.6583 | 62.114 | 0.34114 | 0.031057 | 0.029185 | 0.0066936 | 0.0023295 | 0.00032545 | -0.00021353 | -57.1609 | 62.178 | -61.0519 | 0.054932 | 0.041199 | 0.032043 | -0.19226 | 0.21057 | 0.15564 | -0.36163 | -0.39368 | 0.064087 | 3.4973 | 60.7132 | -62.0728 | 60.2966 | -61.9583 | 3.891
1277.7656 | 122.9965 | -60.6995 | 62.1689 | -0.20054 | 0.03127 | 0.02833 | 0.0026346 | 0.0016887 | 0.0026754 | 0.0012817 | -57.1564 | 62.265 | -61.0519 | -0.045776 | 0.10529 | 0 | 0.018311 | 0.24719 | 0.2655 | -0.19684 | -0.35248 | 0.096131 | 3.5431 | 60.6537 | -62.0636 | 60.5026 | -61.9034 | 3.8956
1278.7344 | 123.1613 | -60.6812 | 62.1048 | 0.25722 | 0.030843 | 0.030253 | 0.0022074 | 0.0033977 | -0.0011698 | -0.00042733 | -57.1198 | 62.1506 | -61.0519 | 0.059509 | 0.041199 | 0.036621 | -0.28381 | -0.18768 | 0.14191 | -0.41657 | -0.37079 | 0.045777 | 3.5614 | 60.7407 | -62.0636 | 60.2646 | -61.9629 | 3.9322
1279.7656 | 123.0652 | -60.6857 | 62.1552 | -0.10899 | 0.030629 | 0.029185 | 0.0071208 | -2.0324e-05 | -0.002238 | -0.00042733 | -57.106 | 62.2421 | -61.0062 | 0.068665 | 0.054932 | 0.068665 | 0.050354 | 0.25177 | 0.25635 | -0.2655 | -0.32044 | 0.086975 | 3.5797 | 60.7544 | -62.1002 | 60.4202 | -61.8988 | 3.9001
1280.7344 | 123.1247 | -60.6583 | 62.1094 | 0.27248 | 0.031911 | 0.031321 | 0.0037028 | 0.0031841 | -0.00052895 | 0.00064087 | -57.0465 | 62.1643 | -61.0107 | 0.036621 | 0.041199 | 0.036621 | -0.19684 | 0.2243 | 0.15564 | -0.36163 | -0.35248 | 0.054932 | 3.6118 | 60.6949 | -62.0682 | 60.2966 | -61.9537 | 3.9642
1281.7656 | 123.111 | -60.6445 | 62.1323 | -0.070844 | 0.027425 | 0.02769 | 0.0002848 | -0.00023392 | -0.0013834 | 6.6667e-08 | -57.0099 | 62.1552 | -61.0565 | 0.45776 | 0.50812 | 0.14191 | -0.63171 | 0.19684 | 0.24719 | -0.19684 | -0.41199 | 0.022888 | 3.6346 | 61.1023 | -61.6241 | 60.4477 | -61.8851 | 4.0466
1282.7344 | 123.0652 | -60.704 | 62.1506 | 0.31063 | 0.033407 | 0.034098 | 0.0062662 | 0.0029705 | -0.0020244 | -0.00064093 | -56.9595 | 62.2284 | -61.0382 | -0.041199 | -0.041199 | -0.082397 | -0.07782 | 0.11444 | 0.19226 | -0.35706 | -0.33417 | 0.07782 | 3.7445 | 60.6628 | -62.1918 | 60.347 | -61.9583 | 4.0787
1283.7656 | 123.0331 | -60.6766 | 62.1689 | -0.20817 | 0.032338 | 0.028544 | 0.001353 | 0.0016887 | -0.0020244 | -0.0023499 | -56.8771 | 62.2055 | -61.0519 | 0.064087 | 0.064087 | 0.064087 | 0.10986 | 0.27008 | 0.27466 | -0.17395 | -0.37537 | 0.036621 | 3.7994 | 60.7407 | -62.1048 | 60.5026 | -61.8942 | 4.1748
1284.7344 | 123.1567 | -60.6628 | 62.1048 | 0.29537 | 0.031698 | 0.029612 | 0.003062 | 0.00083408 | -0.00031535 | -0.0017089 | -56.7444 | 62.1643 | -61.0199 | 0.041199 | 0.041199 | 0.032043 | -0.19684 | 0.21973 | 0.16479 | -0.37079 | -0.35706 | 0.05951 | 3.9185 | 60.704 | -62.0636 | 60.2921 | -61.94 | 4.2755
1285.7344 | 123.1201 | -60.6949 | 62.1002 | 0.11226 | 0.032125 | 0.030253 | 0.0056254 | 0.0027567 | -0.0011698 | 0.00064087 | -56.6711 | 62.1735 | -61.0336 | 0.036621 | 0.041199 | 0.032043 | -0.18768 | 0.21973 | 0.15106 | -0.37079 | -0.33875 | 0.073242 | 4.0237 | 60.7315 | -62.059 | 60.3241 | -61.9492 | 4.3625
1286.7656 | 123.1705 | -60.6216 | 62.1231 | -0.17003 | 0.030843 | 0.032817 | -0.0022786 | -0.00044752 | -0.0035198 | 6.6667e-08 | -56.6345 | 62.1368 | -61.0199 | 0.13275 | 0.14191 | 0.15564 | -0.041199 | 0.3891 | 0.23346 | -0.19226 | -0.39825 | 0.013733 | 3.9871 | 60.7544 | -61.9812 | 60.4294 | -61.8896 | 4.3854
1287.7344 | 123.1064 | -60.6674 | 62.1094 | 0.26485 | 0.035543 | 0.03303 | 0.0071208 | 0.0025431 | 0.00032545 | -0.00085453 | -56.5475 | 62.1918 | -61.0245 | 0.009155 | 0.036621 | 0.041199 | -0.17395 | 0.15106 | 0.16479 | -0.37537 | -0.35706 | 0.082397 | 4.1199 | 60.6766 | -62.0728 | 60.2921 | -61.9446 | 4.4769
1288.75 | 123.1247 | -60.672 | 62.1231 | -0.0098092 | 0.03127 | 0.028758 | -0.000356 | -0.00066112 | 0.00096645 | -0.00085453 | -56.5613 | 62.1277 | -61.0153 | 0.068665 | 0.10071 | 0.091553 | -0.068665 | 0.32501 | 0.20142 | -0.26093 | -0.34332 | 0.004578 | 4.1107 | 60.7407 | -62.0224 | 60.4111 | -61.9217 | 4.454
1289.7344 | 123.0743 | -60.7086 | 62.114 | 0.25722 | 0.035116 | 0.033671 | 0.0062662 | 0.0025431 | -0.00010175 | -0.00085453 | -56.4972 | 62.2284 | -61.0657 | -0.018311 | -0.032043 | -0.054932 | -0.11444 | 0.14191 | 0.19226 | -0.35248 | -0.35706 | 0.11444 | 4.2114 | 60.6903 | -62.146 | 60.3561 | -61.9217 | 4.5685
1290.7656 | 123.0515 | -60.6812 | 62.1735 | -0.14714 | 0.036611 | 0.031108 | 0.0060526 | 0.0025431 | -0.0015972 | -0.0017089 | -56.4011 | 62.2421 | -61.0565 | 0.041199 | 0.022888 | 0.036621 | 0.10986 | 0.26093 | 0.26093 | -0.20142 | -0.37537 | 0.068664 | 4.2801 | 60.7224 | -62.1506 | 60.4797 | -61.9125 | 4.6555
1291.7344 | 123.1155 | -60.6949 | 62.1002 | 0.31063 | 0.035329 | 0.038371 | 0.00413 | 0.0036113 | -0.0020244 | -0.00021353 | -56.3004 | 62.1964 | -61.0382 | 0.027466 | 0.032043 | 0 | -0.16479 | 0.16022 | 0.16937 | -0.3891 | -0.34332 | 0.09613 | 4.3945 | 60.7224 | -62.0682 | 60.3058 | -61.9308 | 4.7379
1292.7656 | 123.0652 | -60.6949 | 62.1277 | -0.078474 | 0.034047 | 0.031535 | 0.0084026 | 0.0023295 | -0.0011698 | 0.00021367 | -56.218 | 62.2513 | -61.0336 | 0.064087 | 0.050354 | 0.054932 | 0.068665 | 0.27466 | 0.27466 | -0.2655 | -0.33875 | 0.1236 | 4.4769 | 60.759 | -62.0773 | 60.4294 | -61.853 | 4.8157
1293.7344 | 123.0698 | -60.704 | 62.1002 | 0.25722 | 0.037893 | 0.038371 | 0.0056254 | 0.0053203 | -0.00010175 | -0.0012817 | -56.163 | 62.2421 | -61.0703 | -0.018311 | -0.022888 | -0.050354 | -0.10071 | 0.14648 | 0.17853 | -0.35248 | -0.36621 | 0.14191 | 4.541 | 60.6857 | -62.1231 | 60.3516 | -61.9217 | 4.9072
1294.7656 | 123.024 | -60.7178 | 62.1597 | -0.13951 | 0.035116 | 0.03068 | 0.0011394 | -2.0324e-05 | 0.0013936 | 0.00021367 | -56.0852 | 62.2009 | -61.0703 | 0.022888 | 0.041199 | 0.064087 | 0.11902 | 0.25635 | 0.27466 | -0.1831 | -0.35248 | 0.041199 | 4.6326 | 60.7407 | -62.1185 | 60.5347 | -61.8851 | 4.985
1295.7344 | 123.1064 | -60.6812 | 62.1002 | 0.24196 | 0.037465 | 0.031962 | 0.0056254 | 0.0016887 | -0.0015972 | -0.00021353 | -55.9387 | 62.1735 | -61.0474 | 0.036621 | 0.064087 | 0.004578 | -0.20599 | 0.16937 | 0.16937 | -0.37994 | -0.36621 | 0.073242 | 4.7424 | 60.7178 | -62.0361 | 60.3012 | -61.9308 | 5.1086
1296.7656 | 123.1384 | -60.6583 | 62.1048 | -0.093733 | 0.032552 | 0.027476 | -0.002065 | 0.0014751 | -0.0024516 | -0.00085453 | -55.838 | 62.114 | -61.0336 | 0.1236 | 0.13733 | 0.17395 | -0.032043 | 0.37079 | 0.21973 | -0.17853 | -0.37537 | 0.009156 | 4.8203 | 60.7819 | -61.9675 | 60.4797 | -61.8851 | 5.1956
1297.7344 | 122.9874 | -60.7224 | 62.1231 | 0.12752 | 0.040243 | 0.037089 | 0.0081888 | 0.0029705 | 0.00032545 | 0.00021367 | -55.7922 | 62.2513 | -61.0657 | -0.054932 | -0.082397 | -0.11444 | 0.009155 | 0.082397 | 0.21973 | -0.36621 | -0.34332 | 0.12817 | 4.9301 | 60.6674 | -62.2055 | 60.3561 | -61.9034 | 5.2734
1298.7656 | 123.1201 | -60.672 | 62.0956 | 0.0054493 | 0.034261 | 0.031108 | -0.0031332 | 0.0019023 | -0.0013834 | -0.0012817 | -55.6595 | 62.1277 | -61.0611 | 0.09613 | 0.1236 | 0.15564 | -0.064087 | 0.35248 | 0.21515 | -0.2243 | -0.3891 | 0.032044 | 5.0125 | 60.7681 | -61.972 | 60.4477 | -61.8805 | 5.4016
1299.7344 | 122.9919 | -60.7452 | 62.1368 | 0.2267 | 0.039388 | 0.041575 | 0.0066936 | 0.0031841 | -0.00052895 | -0.0010681 | -55.6183 | 62.233 | -61.0474 | -0.045776 | -0.064087 | -0.091553 | -0.009155 | 0.11444 | 0.21057 | -0.3479 | -0.30212 | 0.09613 | 5.127 | 60.6995 | -62.2009 | 60.3973 | -61.9263 | 5.4291
1300.75 | 123.0881 | -60.6857 | 62.0956 | 0.13515 | 0.034902 | 0.031748 | -0.0007832 | 0.0012615 | -0.00095615 | -0.0017089 | -55.545 | 62.1002 | -61.084 | 0.013733 | 0.027466 | 0.018311 | -0.091553 | 0.22888 | 0.21057 | -0.29297 | -0.39825 | 0.004578 | 5.1407 | 60.6995 | -62.0682 | 60.3928 | -61.8851 | 5.5389
1301.7344 | 123.0423 | -60.7178 | 62.1094 | 0.28011 | 0.040883 | 0.039652 | 0.0081888 | 0.0027567 | 0.0013936 | -0.00021353 | -55.4214 | 62.178 | -61.0519 | -0.027466 | -0.036621 | -0.054932 | -0.10071 | 0.13275 | 0.1831 | -0.35248 | -0.33417 | 0.068665 | 5.2963 | 60.6903 | -62.146 | 60.3653 | -61.9263 | 5.6305
1302.7656 | 123.0789 | -60.7132 | 62.0911 | 0.23433 | 0.041311 | 0.03303 | 0.005839 | 0.0038249 | -0.00052895 | -0.0010681 | -55.3116 | 62.1552 | -61.0794 | 0 | 0 | -0.013733 | -0.15106 | 0.16937 | 0.17853 | -0.36163 | -0.36621 | 0.064087 | 5.4016 | 60.7132 | -62.0911 | 60.3516 | -61.9125 | 5.7678
1303.7344 | 123.0011 | -60.7407 | 62.114 | 0.16567 | 0.040029 | 0.038584 | 0.007548 | 0.0044657 | -0.0011698 | 6.6667e-08 | -55.2612 | 62.2284 | -61.1114 | -0.054932 | -0.073242 | -0.09613 | -0.009155 | 0.10986 | 0.21515 | -0.35248 | -0.37079 | 0.11444 | 5.4794 | 60.6857 | -62.1872 | 60.3882 | -61.8988 | 5.8502
1304.7344 | 122.9874 | -60.7315 | 62.1094 | 0.11989 | 0.042592 | 0.039225 | 0.00648 | 0.0059611 | -0.0018108 | -0.0023499 | -55.1651 | 62.2421 | -61.1023 | -0.054932 | -0.068665 | -0.10071 | 0.009155 | 0.082397 | 0.21057 | -0.35248 | -0.37079 | 0.13275 | 5.5664 | 60.6766 | -62.178 | 60.379 | -61.8988 | 5.9372
1305.7656 | 123.1338 | -60.6628 | 62.0865 | -0.14714 | 0.036825 | 0.034953 | -0.0029196 | 0.0012615 | -0.00074255 | 0.00064087 | -55.0461 | 62.1323 | -61.084 | 0.10071 | 0.14648 | 0.16937 | -0.022888 | 0.35706 | 0.23804 | -0.1831 | -0.42114 | 0.045776 | 5.6168 | 60.7635 | -61.94 | 60.4797 | -61.8484 | 6.0379
1306.7344 | 123.0011 | -60.7407 | 62.0865 | 0.2267 | 0.042592 | 0.039866 | 0.0079752 | 0.00083408 | -0.00095615 | 0.0012817 | -54.9866 | 62.2192 | -61.084 | -0.064087 | -0.059509 | -0.10529 | -0.022888 | 0.10071 | 0.20599 | -0.36163 | -0.34332 | 0.13275 | 5.7541 | 60.6766 | -62.146 | 60.379 | -61.8805 | 6.0974
1307.7656 | 123.0652 | -60.704 | 62.1002 | -0.23869 | 0.038747 | 0.038371 | -0.0022786 | 0.00040688 | -0.0013834 | 0.0014953 | -54.863 | 62.1323 | -61.0611 | 0.073242 | 0.09613 | 0.1236 | 0.073242 | 0.31128 | 0.27924 | -0.2243 | -0.35706 | 0.032043 | 5.8411 | 60.7773 | -62.0041 | 60.4797 | -61.821 | 6.1981
1308.7344 | 122.9691 | -60.7361 | 62.1094 | 0.089373 | 0.04366 | 0.039225 | 0.009257 | 0.0029705 | -0.00052895 | 0.00085447 | -54.7806 | 62.233 | -61.0748 | -0.032043 | -0.082397 | -0.10071 | 0.032043 | 0.1236 | 0.21973 | -0.31586 | -0.33875 | 0.1236 | 5.9555 | 60.704 | -62.1918 | 60.4202 | -61.8896 | 6.2942
1309.75 | 123.0972 | -60.7178 | 62.0544 | 0.18855 | 0.04067 | 0.042857 | -0.0001424 | 0.0019023 | 0.0013936 | -0.0021361 | -54.6799 | 62.0911 | -61.0931 | 0.018311 | 0.032043 | 0.004578 | -0.15564 | 0.20599 | 0.17853 | -0.36163 | -0.37537 | 0.036621 | 6.0379 | 60.7361 | -62.0224 | 60.3561 | -61.8759 | 6.4133
1310.7344 | 122.9919 | -60.7544 | 62.0911 | 0.097002 | 0.045369 | 0.041575 | 0.0088298 | 0.0025431 | -0.0024516 | -0.00085453 | -54.57 | 62.2192 | -61.0382 | -0.004578 | -0.041199 | -0.036621 | 0.041199 | 0.15564 | 0.23346 | -0.31128 | -0.28381 | 0.12817 | 6.1844 | 60.7498 | -62.1323 | 60.4431 | -61.8576 | 6.4682
1311.7656 | 123.1338 | -60.6812 | 62.0819 | -0.055586 | 0.039815 | 0.038584 | -0.0016378 | -2.0324e-05 | 0.00075285 | -0.0029907 | -54.5105 | 62.1048 | -61.0886 | 0.09613 | 0.1236 | 0.15564 | -0.068665 | 0.37537 | 0.21973 | -0.21973 | -0.40741 | 0.022888 | 6.1707 | 60.7773 | -61.9583 | 60.4614 | -61.8622 | 6.5781
1312.7344 | 123.0011 | -60.7407 | 62.114 | 0.097002 | 0.047292 | 0.042857 | 0.0069072 | 0.0021159 | -0.0018108 | -0.0019225 | -54.3915 | 62.2101 | -61.0565 | -0.013733 | -0.022888 | -0.050354 | 0.022888 | 0.13275 | 0.21973 | -0.32044 | -0.31586 | 0.09613 | 6.3492 | 60.7269 | -62.1368 | 60.4202 | -61.8942 | 6.665
1313.7656 | 123.1155 | -60.6949 | 62.0865 | -0.17003 | 0.037465 | 0.039225 | -0.0001424 | 0.0010477 | -0.00095615 | -0.00042733 | -54.2221 | 62.1552 | -61.0794 | -0.013733 | 0.086975 | 0.21973 | -0.068665 | 0.29755 | 0.21973 | -0.23346 | -0.38452 | 0.068664 | 6.4728 | 60.6812 | -61.9995 | 60.4614 | -61.8668 | 6.8573
1314.7344 | 123.0148 | -60.7407 | 62.0956 | 0.066485 | 0.044942 | 0.044779 | 0.0079752 | 0.0019023 | -0.00095615 | -0.0014953 | -54.2038 | 62.2238 | -61.0474 | 0 | -0.041199 | -0.013733 | 0.009155 | 0.17395 | 0.24261 | -0.3067 | -0.3067 | 0.12817 | 6.5369 | 60.7407 | -62.1368 | 60.434 | -61.853 | 6.8436
1315.7656 | 123.1201 | -60.6812 | 62.0636 | -0.0098092 | 0.040456 | 0.042216 | -0.0016378 | -0.00044752 | -0.0015972 | 0.0012817 | -54.1306 | 62.1048 | -61.0703 | 0.091553 | 0.091553 | 0.1236 | -0.091553 | 0.32044 | 0.2243 | -0.23346 | -0.3891 | 0.041198 | 6.5506 | 60.7727 | -61.972 | 60.4477 | -61.8393 | 6.9397
1316.7344 | 122.9874 | -60.7315 | 62.1048 | 0.11989 | 0.047292 | 0.042216 | 0.0094706 | 0.0012615 | 0.00032545 | -0.0019225 | -54.0298 | 62.2055 | -61.0794 | -0.009155 | -0.045776 | -0.045776 | 0.032043 | 0.15106 | 0.22888 | -0.33417 | -0.3479 | 0.10071 | 6.7017 | 60.7224 | -62.1506 | 60.3973 | -61.8759 | 7.0496
1317.7656 | 123.0789 | -60.7086 | 62.0407 | 0.31825 | 0.045369 | 0.046275 | 0.0011394 | 0.0016887 | -0.00052895 | 0.00085447 | -53.9612 | 62.0773 | -61.0931 | 0.050354 | 0.068665 | 0.032043 | -0.17853 | 0.22888 | 0.16937 | -0.34332 | -0.38452 | 0.036622 | 6.7474 | 60.759 | -61.972 | 60.3653 | -61.8713 | 7.132
1318.7344 | 122.9736 | -60.7178 | 62.0728 | 0.028338 | 0.047506 | 0.045848 | 0.0084026 | 0.0029705 | -0.0011698 | -0.0014953 | -53.8239 | 62.2101 | -61.0931 | 0.045776 | 0.022888 | 0.036621 | 0.004578 | 0.2243 | 0.24719 | -0.27924 | -0.37537 | 0.13733 | 6.8939 | 60.7635 | -62.0499 | 60.4385 | -61.8256 | 7.2693
1319.7656 | 123.0789 | -60.7315 | 62.059 | 0.21907 | 0.044301 | 0.04307 | -0.0001424 | 0.00062048 | -0.0024516 | 0.0010681 | -53.8101 | 62.1094 | -61.0748 | 0.009155 | -0.004578 | 0.013733 | -0.12817 | 0.21057 | 0.16937 | -0.31128 | -0.34332 | 0.050354 | 6.9214 | 60.7407 | -62.0636 | 60.4202 | -61.8896 | 7.2647
1320.7344 | 123.0423 | -60.7452 | 62.114 | -0.032697 | 0.045797 | 0.043284 | 0.0088298 | 0.0023295 | 0.00075285 | 6.6667e-08 | -53.7598 | 62.1735 | -61.0977 | 0.027466 | -0.004578 | 0 | 0.041199 | 0.22888 | 0.24719 | -0.27008 | -0.35248 | 0.059509 | 6.9855 | 60.7727 | -62.1185 | 60.4752 | -61.8668 | 7.338
1321.7656 | 122.9965 | -60.7407 | 62.1048 | 0.013079 | 0.047292 | 0.044993 | 0.0034892 | 0.0019023 | 0.0016072 | -0.0012817 | -53.6316 | 62.2009 | -61.1206 | 0.041199 | 0.041199 | 0.041199 | 0.16479 | 0.24719 | 0.27466 | -0.25177 | -0.37994 | 0.096131 | 7.1091 | 60.7819 | -62.0636 | 60.4889 | -61.8301 | 7.489
1322.7344 | 123.0011 | -60.7361 | 62.1048 | 0.020708 | 0.048147 | 0.044566 | 0.0073344 | 0.0033977 | 0.00032545 | -0.0010681 | -53.5126 | 62.1872 | -61.0794 | 0.009155 | -0.004578 | -0.050354 | -0.004578 | 0.15564 | 0.20599 | -0.31586 | -0.34332 | 0.082398 | 7.2235 | 60.7452 | -62.1094 | 60.4202 | -61.8988 | 7.5668
1323.7656 | 123.1338 | -60.6949 | 62.0361 | -0.1624 | 0.042379 | 0.045848 | -0.0046284 | 0.0019023 | -0.00031535 | -0.00042733 | -53.4073 | 62.0773 | -61.084 | 0.10986 | 0.12817 | 0.15564 | -0.036621 | 0.36163 | 0.2243 | -0.20599 | -0.3891 | 0.041199 | 7.2876 | 60.8047 | -61.908 | 60.4889 | -61.8118 | 7.6767
1324.7344 | 123.0331 | -60.7315 | 62.0956 | -0.070844 | 0.047719 | 0.048838 | 0.0049846 | 0.0014751 | -0.0015972 | -0.0017089 | -53.3066 | 62.2192 | -61.0703 | 0.045776 | 0.032043 | 0.064087 | 0.013733 | 0.24261 | 0.24261 | -0.27924 | -0.33874 | 0.1236 | 7.4249 | 60.7773 | -62.0636 | 60.4523 | -61.853 | 7.7637
1325.75 | 123.1018 | -60.7544 | 62.0178 | 0.28011 | 0.048147 | 0.047129 | 0.00413 | 0.0027567 | 0.0020344 | -0.0014953 | -53.2654 | 62.1414 | -61.084 | 0.009155 | 0.013733 | 0.013733 | -0.13733 | 0.16479 | 0.17853 | -0.38452 | -0.32959 | 0.1236 | 7.489 | 60.7636 | -62.0041 | 60.3699 | -61.8393 | 7.8186
1326.7344 | 123.1018 | -60.7086 | 62.0087 | 0.23433 | 0.045797 | 0.044139 | 0.0028484 | 0.0059611 | -0.0013834 | -0.00085453 | -53.1967 | 62.1048 | -61.1023 | 0.054932 | 0.045776 | 0.013733 | -0.19226 | 0.20142 | 0.17395 | -0.37079 | -0.39368 | 0.09613 | 7.5119 | 60.7636 | -61.9629 | 60.3378 | -61.8347 | 7.9056
1327.75 | 123.0835 | -60.7224 | 62.0224 | 0.18093 | 0.046651 | 0.044779 | 0.0011394 | 0.0010477 | -0.00052895 | 0.00021367 | -53.1097 | 62.0819 | -61.0657 | 0.041199 | 0.032043 | 0.018311 | -0.16022 | 0.22888 | 0.17853 | -0.3479 | -0.34332 | 0.059509 | 7.6126 | 60.7636 | -61.9904 | 60.3745 | -61.8439 | 7.9559
1328.7344 | 123.0469 | -60.7452 | 62.0499 | -0.15477 | 0.049856 | 0.050547 | 0.0069072 | 0.0025431 | -0.0011698 | 6.6667e-08 | -52.9861 | 62.2101 | -61.0931 | 0.068665 | 0.032043 | 0.036621 | 0.032043 | 0.24261 | 0.23804 | -0.27008 | -0.3479 | 0.16022 | 7.7591 | 60.8139 | -62.0178 | 60.4752 | -61.8118 | 8.107
1329.75 | 123.1018 | -60.7361 | 62.0132 | 0.28774 | 0.049428 | 0.052043 | 0.0034892 | 0.0036113 | -0.00074255 | 0.00042727 | -52.9541 | 62.1185 | -61.1069 | 0.013733 | 0.004578 | -0.009155 | -0.13733 | 0.21057 | 0.17853 | -0.3891 | -0.37079 | 0.10529 | 7.782 | 60.7498 | -62.0087 | 60.347 | -61.8347 | 8.1528
1330.7344 | 123.0286 | -60.7269 | 62.0819 | -0.032697 | 0.051992 | 0.049906 | 0.0069072 | 0.0016887 | -0.00031535 | -0.00042733 | -52.8397 | 62.1689 | -61.1114 | 0.050354 | 0.041199 | 0.050354 | 0.018311 | 0.23346 | 0.24261 | -0.27924 | -0.38452 | 0.086975 | 7.8873 | 60.7773 | -62.0407 | 60.4477 | -61.8393 | 8.2718
1331.7656 | 123.0194 | -60.7224 | 62.0682 | -0.20054 | 0.047506 | 0.051402 | 0.0028484 | 0.0057475 | -0.0018108 | -0.00085453 | -52.8809 | 62.1506 | -61.1435 | 0.013733 | 0.013733 | 0.032043 | 0.14191 | 0.24719 | 0.2655 | -0.21057 | -0.42114 | 0.082398 | 7.8415 | 60.7361 | -62.0544 | 60.5118 | -61.8027 | 8.2626
1332.7344 | 123.0469 | -60.759 | 62.1094 | -0.10899 | 0.051137 | 0.04542 | 0.0049846 | 0.0031841 | 0.00032545 | 0.0014953 | -52.7573 | 62.1964 | -61.0931 | 0.036621 | 0.036621 | 0.041199 | 0.10529 | 0.23346 | 0.27466 | -0.21057 | -0.33417 | 0.086975 | 8.0017 | 60.7956 | -62.0728 | 60.5484 | -61.8347 | 8.3359
1333.7656 | 123.1293 | -60.7132 | 62.0453 | -0.14714 | 0.048574 | 0.049052 | -0.0031332 | 0.00062048 | -0.0069376 | -0.00064093 | -52.6474 | 62.0544 | -61.0565 | 0.34332 | -0.15564 | -0.40741 | 0.018311 | 0.40741 | 0.25177 | -0.21515 | -0.34332 | 0.009155 | 8.0658 | 61.0565 | -62.2009 | 60.498 | -61.7935 | 8.4091
1334.7344 | 123.0331 | -60.7407 | 62.0956 | -0.19291 | 0.051778 | 0.048411 | 0.0069072 | 0.0014751 | -0.002238 | -0.0010681 | -52.6062 | 62.1826 | -61.0703 | 0.050354 | 0.027466 | 0.064087 | 0.09613 | 0.2655 | 0.25635 | -0.2243 | -0.32959 | 0.086975 | 8.1345 | 60.791 | -62.0682 | 60.5164 | -61.8393 | 8.4641
1335.7656 | 123.0515 | -60.7224 | 62.0499 | 0.23433 | 0.050283 | 0.046275 | -0.002065 | 0.0019023 | -0.00095615 | -0.00042733 | -52.5604 | 62.059 | -61.0977 | 0.013733 | 0.027466 | 0.009155 | -0.14648 | 0.20142 | 0.1831 | -0.32044 | -0.37537 | 0.009155 | 8.1619 | 60.7361 | -62.0224 | 60.4019 | -61.8668 | 8.5373
1336.7344 | 123.0331 | -60.7315 | 62.059 | -0.093733 | 0.051992 | 0.046702 | 0.0084026 | 0.0036113 | -0.00074255 | -0.0012817 | -52.4506 | 62.1826 | -61.0794 | 0.054932 | 0.013733 | 0.036621 | 0.041199 | 0.23346 | 0.25177 | -0.27008 | -0.3479 | 0.1236 | 8.2809 | 60.7864 | -62.0453 | 60.4614 | -61.8073 | 8.6288
1337.7656 | 123.0698 | -60.7224 | 61.9995 | 0.34877 | 0.04836 | 0.047984 | -0.0007832 | 0.0038249 | 0.0013936 | 0.00085447 | -52.4231 | 62.0636 | -61.084 | 0.041199 | 0.045776 | 0.032043 | -0.16479 | 0.23346 | 0.1831 | -0.35706 | -0.36163 | 0.064087 | 8.2993 | 60.7636 | -61.9537 | 60.3653 | -61.8164 | 8.6609
1338.7344 | 122.9828 | -60.7407 | 62.0819 | 0.16567 | 0.051137 | 0.049052 | 0.0043436 | 0.00040688 | 0.0018208 | -0.00064093 | -52.3865 | 62.178 | -61.084 | 0.054932 | 0.045776 | 0.027466 | 0.11444 | 0.23346 | 0.2655 | -0.22888 | -0.34332 | 0.096131 | 8.3542 | 60.7956 | -62.0361 | 60.5118 | -61.8164 | 8.6975
1339.7656 | 123.0789 | -60.704 | 62.0178 | 1.6381 | 0.054342 | 0.050547 | 0.0015666 | 0.0016887 | -0.0015972 | -0.00085453 | -52.3682 | 62.0453 | -61.0977 | 0.004578 | 0.059509 | 0.10986 | -0.19684 | 0.19226 | 0.18768 | -0.31586 | -0.39368 | 0.027466 | 8.3359 | 60.7086 | -61.9583 | 60.3882 | -61.8301 | 8.7296
1340.7344 | 123.0057 | -60.7269 | 62.0636 | -0.13951 | 0.054555 | 0.049052 | 0.0066936 | 0.0014751 | -0.00031535 | -0.00064093 | -52.2949 | 62.1735 | -61.0703 | 0.041199 | 0.045776 | 0.041199 | 0.10986 | 0.26093 | 0.27924 | -0.21057 | -0.34332 | 0.10986 | 8.432 | 60.7681 | -62.0178 | 60.5164 | -61.7844 | 8.7753
1341.7656 | 123.0698 | -60.7178 | 62.0224 | 0.27248 | 0.052846 | 0.049052 | 0.0034892 | 0.0051067 | 0.00032545 | -0.0010681 | -52.1896 | 62.0636 | -61.0931 | 0.036621 | 0.086975 | -0.33875 | -0.46692 | 0.59967 | 0.15106 | -0.44403 | -0.37537 | 0.041199 | 8.5281 | 60.7544 | -61.9354 | 60.2737 | -61.8713 | 8.9035
1342.7344 | 123.0057 | -60.7315 | 62.1002 | -0.12425 | 0.051778 | 0.050761 | 0.0056254 | 0.0014751 | -0.00052895 | -0.0025635 | -52.1896 | 62.1735 | -61.1252 | 0.013733 | 0.013733 | 0.027466 | 0.10986 | 0.20599 | 0.27466 | -0.21515 | -0.39368 | 0.073242 | 8.5419 | 60.7452 | -62.0865 | 60.5164 | -61.8256 | 8.9355
1343.7656 | 123.111 | -60.7224 | 62.0132 | 0.32588 | 0.051351 | 0.05247 | 0.0034892 | 0.0023295 | -0.00010175 | 6.6667e-08 | -52.0844 | 62.0728 | -61.0657 | 0.050354 | 0.050354 | 0.032043 | -0.19226 | 0.21057 | 0.16479 | -0.37537 | -0.34332 | 0.059509 | 8.638 | 60.7727 | -61.9629 | 60.347 | -61.8484 | 8.9813
1344.7344 | 123.0331 | -60.7681 | 62.0682 | -0.14714 | 0.05541 | 0.052683 | 0.0066936 | 0.0016887 | -0.00010175 | -0.00042733 | -52.0523 | 62.1826 | -61.0886 | 0.050354 | 0.041199 | 0.068665 | 0.059509 | 0.27008 | 0.27924 | -0.25177 | -0.32044 | 0.11444 | 8.7158 | 60.8185 | -62.027 | 60.5164 | -61.7889 | 9.0363
1345.7656 | 123.0377 | -60.7544 | 62.0178 | 0.28774 | 0.053701 | 0.049266 | 0.0062662 | 0.0036113 | -0.00010175 | -0.0012817 | -52.0477 | 62.1414 | -61.1114 | -0.027466 | -0.022888 | -0.059509 | -0.10529 | 0.12817 | 0.17853 | -0.35706 | -0.35705 | 0.1236 | 8.7067 | 60.7269 | -62.0407 | 60.3973 | -61.8393 | 9.0637
1346.7344 | 122.9736 | -60.7544 | 62.0728 | -0.13951 | 0.055196 | 0.049266 | 0.0037028 | 0.0012615 | -0.00031535 | -0.0010681 | -51.9836 | 62.1872 | -61.0886 | -0.068665 | 0.004578 | 0.091553 | 0.086975 | 0.18768 | 0.25635 | -0.23346 | -0.33417 | 0.11444 | 8.7708 | 60.6857 | -62.0682 | 60.5209 | -61.8164 | 9.1049
1347.7656 | 123.1247 | -60.7224 | 62.0224 | 0.24959 | 0.054555 | 0.057597 | 0.0004984 | 0.0023295 | -0.00052895 | -0.0017089 | -51.9287 | 62.0636 | -61.0886 | -0.24261 | -0.17395 | 0.40741 | 0.064087 | 0.16479 | 0.15106 | -0.41657 | -0.36621 | 0.041199 | 8.7936 | 60.4797 | -62.1963 | 60.3058 | -61.8713 | 9.1599
1348.7344 | 122.9919 | -60.759 | 62.0728 | -0.11662 | 0.053274 | 0.049906 | 0.005839 | 0.0016887 | -0.00031535 | -0.00021353 | -51.9974 | 62.1689 | -61.1069 | 0.032043 | 0.032043 | 0.022888 | 0.11902 | 0.24261 | 0.27008 | -0.20599 | -0.3479 | 0.09613 | 8.7616 | 60.791 | -62.0407 | 60.553 | -61.8027 | 9.1095
1349.7656 | 123.0652 | -60.7407 | 62.027 | 0.26485 | 0.054769 | 0.055247 | 0.005839 | 0.0029705 | -0.0011698 | -0.0017089 | -51.9608 | 62.1094 | -61.1298 | -0.009155 | -0.004578 | -0.022888 | -0.15564 | 0.17395 | 0.17853 | -0.36621 | -0.3891 | 0.082397 | 8.7799 | 60.7315 | -62.0316 | 60.3745 | -61.8484 | 9.169
1350.7344 | 123.024 | -60.759 | 62.0636 | -0.13951 | 0.054555 | 0.058024 | 0.005839 | 0.0023295 | -0.0026652 | -0.00042733 | -51.8784 | 62.1735 | -61.1023 | 0.054932 | 0.045776 | 0.068665 | 0.073242 | 0.26093 | 0.27008 | -0.24261 | -0.34332 | 0.10986 | 8.8806 | 60.8139 | -62.0178 | 60.5164 | -61.7935 | 9.2239
1351.7656 | 123.0835 | -60.7498 | 62.0087 | 0.38692 | 0.05541 | 0.051188 | 0.0045574 | 0.0033977 | -0.00074255 | 0.00021367 | -51.828 | 62.059 | -61.0977 | 0.041199 | 0.032043 | 0.009155 | -0.20599 | 0.20599 | 0.16937 | -0.38452 | -0.3479 | 0.050354 | 8.9218 | 60.791 | -61.9766 | 60.3653 | -61.8393 | 9.2697
1352.7344 | 122.9919 | -60.759 | 62.0544 | -0.20817 | 0.05541 | 0.05247 | 0.0037028 | 0.0021159 | -0.0011698 | 0.0012817 | -51.86 | 62.1597 | -61.1069 | 0.19684 | -0.21057 | -0.33875 | 0.19684 | 0.27008 | 0.3067 | -0.16022 | -0.3479 | 0.10529 | 8.8989 | 60.9558 | -62.265 | 60.5988 | -61.7477 | 9.2468
1353.7656 | 123.0789 | -60.7132 | 62.0224 | 0.1733 | 0.05306 | 0.052897 | 0.0004984 | 0.0031841 | -0.00052895 | 0.0012817 | -51.7914 | 62.0544 | -61.0977 | 0.018311 | 0.032043 | 0.032043 | -0.15564 | 0.20599 | 0.17853 | -0.3479 | -0.38452 | 0.032043 | 8.9218 | 60.7315 | -61.9904 | 60.3653 | -61.8439 | 9.3063
1354.7344 | 123.0194 | -60.7636 | 62.0544 | -0.17003 | 0.055196 | 0.052897 | 0.0028484 | -0.00023392 | -0.0018108 | 0.0014953 | -51.7776 | 62.178 | -61.0977 | 0.032043 | 0.018311 | 0.036621 | 0.1236 | 0.23346 | 0.27924 | -0.21057 | -0.33417 | 0.1236 | 8.9859 | 60.7956 | -62.0361 | 60.553 | -61.7752 | 9.3201
1355.7656 | 122.9736 | -60.7452 | 62.0636 | 0.058855 | 0.053274 | 0.051615 | -0.0007832 | 0.0021159 | -0.00031535 | 6.6667e-08 | -51.7593 | 62.0407 | -61.1069 | 0.009155 | 0.032043 | 0.036621 | -0.064087 | 0.24719 | 0.22888 | -0.2655 | -0.36163 | -0.022889 | 8.9859 | 60.7544 | -62.0316 | 60.4797 | -61.8347 | 9.3475
1356.7344 | 122.9874 | -60.7361 | 62.0636 | -0.26158 | 0.054128 | 0.055033 | 0.0051982 | -0.0010885 | -0.0020244 | -0.00085453 | -51.6998 | 62.146 | -61.1023 | 0.041199 | 0.022888 | 0.027466 | 0.16022 | 0.25177 | 0.29297 | -0.25177 | -0.36621 | 0.082397 | 9.0363 | 60.7773 | -62.0407 | 60.4843 | -61.7706 | 9.4025
1357.7656 | 123.0881 | -60.7407 | 61.9812 | 0.28011 | 0.054342 | 0.059092 | 0.001353 | 0.0025431 | -0.00031535 | -0.00042733 | -51.6998 | 62.027 | -61.1114 | 0.1236 | 0.041199 | -0.013733 | -0.11902 | 0.27924 | 0.19226 | -0.32501 | -0.37079 | 0.045777 | 9.0408 | 60.8643 | -61.94 | 60.4156 | -61.7889 | 9.4116
1358.7344 | 123.0148 | -60.759 | 62.0728 | -0.12425 | 0.057546 | 0.048411 | 0.0088298 | 0.0031841 | -0.0020244 | -0.00064093 | -51.6129 | 62.1597 | -61.1069 | 0.036621 | 0.022888 | 0.036621 | 0.11902 | 0.2655 | 0.27008 | -0.1831 | -0.3479 | 0.086975 | 9.1461 | 60.7956 | -62.0499 | 60.5759 | -61.8027 | 9.494
1359.7656 | 123.0789 | -60.7315 | 61.9995 | 0.24196 | 0.05306 | 0.054606 | 0.000712 | 0.0019023 | 0.0016072 | 0.00042727 | -51.5762 | 62.0361 | -61.0977 | 0.032043 | 0.036621 | 0.027466 | -0.16937 | 0.22888 | 0.18768 | -0.33875 | -0.36621 | 0.036621 | 9.1553 | 60.7635 | -61.9629 | 60.3928 | -61.8118 | 9.5215
1360.7344 | 123.0011 | -60.7636 | 62.0682 | -0.15477 | 0.054128 | 0.052043 | 0.0066936 | 0.0016887 | -0.0011698 | 0.00064087 | -51.5625 | 62.1368 | -61.1023 | 0.036621 | 0.018311 | 0.032043 | 0.10986 | 0.24719 | 0.27466 | -0.21515 | -0.33874 | 0.068665 | 9.2011 | 60.8002 | -62.0499 | 60.5484 | -61.7935 | 9.5398
1361.75 | 123.111 | -60.7407 | 62.027 | 0.32588 | 0.056905 | 0.055461 | 0.0073344 | 0.0019023 | -0.0013834 | -0.00064093 | -51.535 | 62.0773 | -61.1023 | 0.059509 | 0.036621 | 0 | -0.18768 | 0.21515 | 0.16937 | -0.36163 | -0.36163 | 0.050354 | 9.2056 | 60.8002 | -61.9904 | 60.379 | -61.8576 | 9.5673
1362.7344 | 122.9828 | -60.7544 | 62.0544 | -1.4975 | 0.055196 | 0.053324 | 0.0043436 | 0.0033977 | -0.0013834 | -0.0012817 | -51.6907 | 62.1552 | -61.1206 | 0.022888 | -0.013733 | -0.004578 | 0.17395 | 0.24719 | 0.28839 | -0.24261 | -0.36621 | 0.10071 | 9.0637 | 60.7773 | -62.0682 | 60.5118 | -61.7661 | 9.4299
1363.75 | 122.9691 | -60.7864 | 62.0544 | 0.11226 | 0.060537 | 0.056529 | 0.0081888 | 0.0044657 | -0.003947 | -0.0025635 | -51.5213 | 62.1506 | -61.116 | -0.032043 | -0.054932 | -0.073242 | -0.004578 | 0.11444 | 0.24261 | -0.32501 | -0.32959 | 0.096131 | 9.2651 | 60.7544 | -62.1094 | 60.4614 | -61.8118 | 9.5947
1364.7344 | 122.9919 | -60.7636 | 62.0544 | -0.26158 | 0.053487 | 0.055674 | 0.0034892 | 0.0014751 | -0.0011698 | -0.0014953 | -51.5213 | 62.178 | -61.1114 | 0.013733 | 0.018311 | 0.032043 | 0.13275 | 0.23346 | 0.28381 | -0.20142 | -0.3479 | 0.1236 | 9.2422 | 60.7773 | -62.0361 | 60.5621 | -61.7706 | 9.5901
1365.7656 | 123.0377 | -60.7498 | 62.0087 | 0.2267 | 0.056264 | 0.050334 | -0.0016378 | 0.0036113 | -0.00031535 | -0.0010681 | -51.5121 | 62.0407 | -61.1023 | -0.013733 | 0.013733 | 0.013733 | -0.11444 | 0.20142 | 0.19684 | -0.3067 | -0.35248 | 0.032043 | 9.2377 | 60.7361 | -61.9949 | 60.4431 | -61.8118 | 9.5901
1366.7344 | 122.9828 | -60.7452 | 62.0819 | -0.24632 | 0.055837 | 0.053538 | 0.0022074 | 0.00019328 | -0.00031535 | 0.0014953 | -51.5121 | 62.1414 | -61.1069 | 0.022888 | 0.027466 | 0.036621 | 0.14648 | 0.25177 | 0.28839 | -0.1831 | -0.36163 | 0.059509 | 9.2331 | 60.7681 | -62.0544 | 60.5621 | -61.7935 | 9.5947
1367.75 | 123.056 | -60.7727 | 62.0178 | 0.26485 | 0.057546 | 0.053752 | 0.0071208 | 0.0042521 | -0.0018108 | -0.00064093 | -51.4435 | 62.114 | -61.1298 | 0 | 0.004578 | -0.009155 | -0.14191 | 0.15564 | 0.16479 | -0.37994 | -0.35706 | 0.096131 | 9.3292 | 60.7727 | -62.0132 | 60.3928 | -61.853 | 9.6863
1368.7344 | 122.9828 | -60.7773 | 62.0453 | -0.20817 | 0.056691 | 0.048838 | 0.0039164 | -2.0324e-05 | -0.00031535 | -0.0017089 | -51.4755 | 62.1277 | -61.1114 | 0.013733 | 0.018311 | 0.022888 | 0.14648 | 0.24719 | 0.28381 | -0.18768 | -0.33417 | 0.082398 | 9.3018 | 60.791 | -62.027 | 60.5896 | -61.7615 | 9.6359
1369.7656 | 123.0286 | -60.7361 | 62.0361 | 0.11989 | 0.055196 | 0.050975 | -0.0022786 | 0.0012615 | -0.00052895 | -0.0010681 | -51.4755 | 62.0361 | -61.1206 | 0.013733 | 0.032043 | 0.041199 | -0.054932 | 0.22888 | 0.20599 | -0.28839 | -0.38452 | 0 | 9.2606 | 60.7498 | -62.0041 | 60.4477 | -61.8301 | 9.6451
1370.7344 | 122.9736 | -60.7452 | 62.0499 | -0.2158 | 0.052633 | 0.052043 | 0.002421 | -0.0025837 | -0.0028788 | -0.0012817 | -51.4069 | 62.1048 | -61.0977 | 0.032043 | 0 | 0.013733 | 0.12817 | 0.28839 | 0.28381 | -0.18768 | -0.35248 | 0.054931 | 9.3384 | 60.7773 | -62.0499 | 60.5576 | -61.7661 | 9.6909
1371.7656 | 122.9691 | -60.7681 | 62.0361 | 0.2267 | 0.057973 | 0.055461 | 0.0077616 | 0.0010477 | -0.00074255 | -0.0014953 | -51.4252 | 62.1231 | -61.0977 | -0.068665 | -0.073242 | -0.064087 | -0.054932 | 0.10071 | 0.2243 | -0.34332 | -0.32959 | 0.086975 | 9.343 | 60.6995 | -62.1094 | 60.4248 | -61.8118 | 9.6725
1372.7344 | 123.0423 | -60.7498 | 62.0453 | -0.15477 | 0.054128 | 0.055888 | 7.12e-05 | 0.00040688 | -0.0020244 | -0.00021353 | -51.384 | 62.0636 | -61.0886 | 0.082397 | 0.091553 | 0.10986 | 0.050354 | 0.32501 | 0.27924 | -0.20599 | -0.33875 | 0.018311 | 9.3658 | 60.8322 | -61.9537 | 60.5438 | -61.7661 | 9.7046
1373.75 | 122.9828 | -60.759 | 62.0361 | 0.11226 | 0.057119 | 0.058024 | 0.0086162 | 0.0031841 | 0.00011185 | -0.0014953 | -51.4114 | 62.1597 | -61.1206 | -0.073242 | -0.068665 | -0.073242 | -0.054932 | 0.09613 | 0.24719 | -0.34332 | -0.36163 | 0.1236 | 9.3475 | 60.6857 | -62.1048 | 60.4156 | -61.7889 | 9.7092
1374.7344 | 123.0011 | -60.7224 | 62.0544 | -0.19291 | 0.053274 | 0.052683 | 0.0004984 | 0.0021159 | -0.0020244 | -0.0025635 | -51.4114 | 62.0773 | -61.1023 | 0.064087 | 0.068665 | 0.086975 | 0.09613 | 0.32044 | 0.28381 | -0.21515 | -0.37994 | 0.022889 | 9.3109 | 60.7864 | -61.9858 | 60.5072 | -61.7706 | 9.6909
1375.75 | 122.9782 | -60.7773 | 62.0544 | 0.24196 | 0.057973 | 0.055461 | 0.0069072 | 0.0040385 | -0.0015972 | -0.0034179 | -51.4709 | 62.1277 | -61.0977 | -0.045776 | -0.050354 | -0.10071 | -0.013733 | 0.09613 | 0.20599 | -0.35248 | -0.32043 | 0.073243 | 9.3063 | 60.7315 | -62.1048 | 60.4248 | -61.8484 | 9.6268
1376.7344 | 123.0606 | -60.7407 | 62.027 | -0.20817 | 0.051992 | 0.049693 | 0.0011394 | 0.0012615 | -0.0020244 | -0.00085453 | -51.416 | 62.0361 | -61.0931 | 0.09613 | 0.11902 | 0.14191 | 0.009155 | 0.36163 | 0.24261 | -0.20142 | -0.35248 | 0.009155 | 9.3246 | 60.8368 | -61.908 | 60.5392 | -61.7844 | 9.6771
1377.7656 | 123.0515 | -60.7452 | 62.0316 | -0.093733 | 0.054769 | 0.050975 | 0.000712 | 0.00062048 | -0.00074255 | -0.0012817 | -51.4526 | 62.0407 | -61.0977 | 0.091553 | 0.10071 | 0.13275 | 0.018311 | 0.33875 | 0.25635 | -0.2243 | -0.35248 | 0.009155 | 9.2926 | 60.8368 | -61.9308 | 60.5209 | -61.7752 | 9.6451
1378.7344 | 123.0606 | -60.704 | 62.0361 | -0.10136 | 0.054128 | 0.056101 | 0.0019938 | 0.00040688 | -0.002238 | -0.0014953 | -51.4526 | 62.0636 | -61.0977 | 0.10529 | 0.10986 | 0.1236 | 0.027466 | 0.33875 | 0.2655 | -0.21057 | -0.39368 | 0.027466 | 9.2514 | 60.8093 | -61.9263 | 60.4935 | -61.7706 | 9.6451
1379.7656 | 122.937 | -60.7544 | 62.0544 | 0.21907 | 0.05776 | 0.05717 | 0.009257 | 0.0031841 | -0.00074255 | -0.0012817 | -51.5305 | 62.1689 | -61.1252 | -0.054932 | -0.059509 | -0.10529 | -0.009155 | 0.086975 | 0.21057 | -0.3479 | -0.37079 | 0.11444 | 9.2239 | 60.6995 | -62.114 | 60.4065 | -61.8439 | 9.5947
1380.7344 | 123.0972 | -60.6903 | 61.9949 | -0.047956 | 0.054769 | 0.054392 | -0.0027058 | 0.00083408 | 0.00032545 | -0.0019225 | -51.5121 | 62.027 | -61.0931 | 0.10986 | 0.14191 | 0.14648 | -0.064087 | 0.37537 | 0.23346 | -0.19226 | -0.40283 | 0.032044 | 9.1782 | 60.8002 | -61.853 | 60.498 | -61.7615 | 9.581
1381.7656 | 123.0698 | -60.7361 | 62.0041 | 0.24959 | 0.058828 | 0.054606 | 0.005839 | 0.0012615 | 0.00053925 | -0.0034179 | -51.5213 | 62.0819 | -61.0703 | 0.041199 | 0.045776 | 0.009155 | -0.21057 | 0.14648 | 0.15564 | -0.39368 | -0.33417 | 0.07782 | 9.2148 | 60.7773 | -61.9583 | 60.3424 | -61.8484 | 9.5489
1382.7344 | 123.1155 | -60.7269 | 61.9995 | -0.17766 | 0.053487 | 0.049052 | -0.0012106 | -0.00044752 | -0.0033062 | 0.00021367 | -51.5671 | 62.027 | -61.1023 | 0.1236 | 0.15106 | 0.17395 | -0.059509 | 0.40283 | 0.23804 | -0.1831 | -0.37537 | 0.027466 | 9.1599 | 60.8505 | -61.8484 | 60.5438 | -61.7615 | 9.5352
1383.75 | 122.9736 | -60.759 | 62.0865 | -2.2147 | 0.057332 | 0.054606 | 0.0056254 | 0.0014751 | -0.0013834 | -0.00085453 | -51.7456 | 62.146 | -61.0931 | 0.054932 | -0.027466 | -0.013733 | 0.15564 | 0.23804 | 0.26093 | -0.24719 | -0.33417 | 0.059509 | 9.0134 | 60.8139 | -62.114 | 60.5118 | -61.8256 | 9.3475
1384.7344 | 123.0606 | -60.7361 | 62.0224 | -0.0021797 | 0.054983 | 0.049906 | -0.0039876 | -0.0030111 | -0.0020244 | -0.0017089 | -51.7136 | 62.0544 | -61.1069 | 0.059509 | 0.064087 | 0.10986 | -0.086975 | 0.30212 | 0.22888 | -0.24261 | -0.37079 | 0.032043 | 9.0225 | 60.7956 | -61.9583 | 60.4935 | -61.7935 | 9.3933
1385.7656 | 123.024 | -60.7361 | 62.0682 | -0.0098092 | 0.055196 | 0.057597 | 0.0088298 | 0.0025431 | -0.00074255 | -0.0014953 | -51.6998 | 62.1506 | -61.0886 | 0.054932 | 0.027466 | 0.018311 | 0.018311 | 0.22888 | 0.24719 | -0.28381 | -0.35248 | 0.082398 | 9.0363 | 60.791 | -62.0407 | 60.4523 | -61.821 | 9.3887
1386.7344 | 123.0423 | -60.7224 | 62.027 | 0.058855 | 0.053487 | 0.051615 | -0.0024922 | -0.00023392 | -0.0015972 | -0.0014953 | -51.9012 | 62.0544 | -61.1023 | 0.013733 | 0.054932 | 0.068665 | -0.073242 | 0.21973 | 0.20599 | -0.27466 | -0.37994 | 0.027465 | 8.8211 | 60.7361 | -61.972 | 60.4477 | -61.821 | 9.201
1387.7812 | 122.9919 | -60.7681 | 62.1002 | -0.20817 | 0.055837 | 0.05482 | 0.0049846 | -2.0324e-05 | 0.00118 | -0.00042733 | -51.8234 | 62.1506 | -61.0977 | 0.022888 | 0.018311 | 0.013733 | 0.13275 | 0.24261 | 0.27466 | -0.21515 | -0.32959 | 0.050354 | 8.9447 | 60.791 | -62.0819 | 60.553 | -61.8256 | 9.2743
1388.7344 | 123.0515 | -60.7361 | 62.0361 | 0.028338 | 0.053274 | 0.053538 | 0.0002848 | 0.00040688 | -0.0018108 | 0.00021367 | -51.7639 | 62.0636 | -61.0977 | 0.032043 | 0.068665 | 0.050354 | -0.09613 | 0.23804 | 0.19226 | -0.27466 | -0.36163 | 0.027466 | 8.9722 | 60.7681 | -61.9675 | 60.4614 | -61.8439 | 9.3338
1389.7656 | 122.9691 | -60.7544 | 62.0453 | -0.0021797 | 0.057332 | 0.052683 | 0.0090434 | 0.0029705 | -0.00095615 | -0.0019225 | -51.7868 | 62.1414 | -61.0886 | 0.004578 | -0.022888 | -0.032043 | 0.027466 | 0.17853 | 0.22888 | -0.32044 | -0.33417 | 0.09613 | 8.9676 | 60.759 | -62.0682 | 60.434 | -61.8164 | 9.3018
1390.7344 | 123.0423 | -60.7132 | 62.0316 | 0.15804 | 0.055196 | 0.051188 | -0.000356 | 0.00083408 | -0.0024516 | -0.0021361 | -51.9012 | 62.0499 | -61.1252 | 0.004578 | 0.032043 | 0.032043 | -0.086975 | 0.22888 | 0.20142 | -0.29297 | -0.41199 | 0.018311 | 8.812 | 60.7178 | -61.9995 | 60.4202 | -61.8301 | 9.2239
1391.7656 | 123.0331 | -60.7636 | 62.0178 | 0.303 | 0.056478 | 0.056101 | 0.0056254 | 0.0010477 | -0.0024516 | 0.00021367 | -51.915 | 62.1231 | -61.1069 | -0.013733 | -0.022888 | -0.050354 | -0.11902 | 0.14191 | 0.19226 | -0.36163 | -0.34332 | 0.10529 | 8.8486 | 60.7498 | -62.0407 | 60.4019 | -61.8256 | 9.1919
1392.7344 | 123.0423 | -60.7178 | 62.0453 | -0.15477 | 0.053274 | 0.053752 | 0.0017802 | -0.0010885 | -0.0018108 | -0.00085453 | -51.8829 | 62.059 | -61.0657 | 0.11444 | 0.11444 | 0.13733 | 0.032043 | 0.33875 | 0.2655 | -0.21515 | -0.3479 | 0.013733 | 8.8348 | 60.8322 | -61.9308 | 60.5026 | -61.7798 | 9.1827
1393.7344 | 123.0377 | -60.7224 | 62.0132 | 0.24959 | 0.054555 | 0.051829 | 0.0022074 | 0.00083408 | -0.00031535 | -0.0010681 | -51.9058 | 62.027 | -61.0977 | 0.036621 | 0.018311 | 0 | -0.15106 | 0.20599 | 0.16937 | -0.33417 | -0.37537 | 0.013733 | 8.8165 | 60.759 | -61.9949 | 60.3882 | -61.8439 | 9.1919
1394.7656 | 123.0515 | -60.7452 | 62.0407 | 0.28011 | 0.059041 | 0.053324 | 0.0088298 | 0.0029705 | -0.002238 | -0.00064093 | -51.9287 | 62.1094 | -61.1069 | 0 | -0.018311 | -0.050354 | -0.11444 | 0.15564 | 0.18768 | -0.3479 | -0.36163 | 0.068665 | 8.8165 | 60.7452 | -62.059 | 60.3973 | -61.853 | 9.1782
1395.7344 | 123.0286 | -60.7178 | 62.0041 | 0.18855 | 0.054555 | 0.053111 | 7.12e-05 | 0.0010477 | 0.002248 | -0.00064093 | -51.9745 | 62.0316 | -61.0886 | 0.018311 | 0.022888 | 0 | -0.13733 | 0.18768 | 0.16479 | -0.31128 | -0.37079 | 0.027466 | 8.7433 | 60.7361 | -61.9812 | 60.4065 | -61.8393 | 9.1141
1396.7656 | 122.9736 | -60.7361 | 62.0911 | -0.22343 | 0.054769 | 0.048411 | 0.0051982 | 0.0014751 | 0.0016072 | -0.00064093 | -51.9974 | 62.1231 | -61.084 | 0.027466 | 0.022888 | 0.022888 | 0.14191 | 0.25635 | 0.28381 | -0.17853 | -0.3479 | 0.032044 | 8.7387 | 60.7635 | -62.0682 | 60.5576 | -61.8073 | 9.0866
1397.7344 | 122.9736 | -60.7361 | 62.0819 | 0.18855 | 0.055196 | 0.054179 | 0.0049846 | 0.0021159 | -0.003947 | -0.00042733 | -51.9745 | 62.1231 | -61.1572 | 0.050354 | 0.032043 | 0.009155 | 0.13275 | 0.24261 | 0.27924 | -0.21973 | -0.42114 | 0.041199 | 8.7616 | 60.7864 | -62.0499 | 60.5164 | -61.8027 | 9.1827
1398.75 | 123.0469 | -60.7086 | 62.0499 | -0.22343 | 0.053487 | 0.049906 | 0.0017802 | -0.00023392 | 0.00053925 | 0.00064087 | -51.947 | 62.0682 | -61.0565 | 0.11902 | 0.10986 | 0.14648 | 0.022888 | 0.35706 | 0.25177 | -0.20599 | -0.3479 | 0.01831 | 8.7616 | 60.8276 | -61.94 | 60.5026 | -61.7981 | 9.1095
1399.7344 | 123.0423 | -60.7361 | 62.027 | 0.18093 | 0.053914 | 0.050334 | 0.0017802 | 0.0010477 | -0.00095615 | -0.0025635 | -52.0111 | 62.027 | -61.0794 | 0.013733 | 0.009155 | 0.027466 | -0.082397 | 0.21973 | 0.19684 | -0.30212 | -0.34332 | 0 | 8.725 | 60.7498 | -62.0178 | 60.434 | -61.8301 | 9.0683
1400.7656 | 123.0057 | -60.7452 | 62.0728 | -0.1624 | 0.0584 | 0.056956 | 0.0088298 | 0.00040688 | -0.002238 | -0.00085453 | -51.9974 | 62.1414 | -61.0748 | 0.036621 | 0.013733 | 0.032043 | 0.11444 | 0.21515 | 0.27924 | -0.21973 | -0.32959 | 0.068664 | 8.7479 | 60.7819 | -62.059 | 60.5255 | -61.7935 | 9.0775
1401.7344 | 123.0652 | -60.7132 | 62.027 | 0.41744 | 0.056905 | 0.055033 | 0.0015666 | 0.0021159 | 0.00011185 | -0.0010681 | -51.9287 | 62.0407 | -61.0657 | 0.036621 | 0.050354 | 0.059509 | -0.1831 | 0.22888 | 0.17853 | -0.33417 | -0.35248 | 0.013732 | 8.7845 | 60.7498 | -61.9766 | 60.379 | -61.8484 | 9.137
1402.7812 | 123.0148 | -60.7636 | 62.0499 | -0.055586 | 0.056478 | 0.05247 | 0.0098978 | 0.00019328 | -0.002238 | -0.00042733 | -51.915 | 62.146 | -61.0748 | 0.059509 | -0.018311 | -0.28381 | 0.004578 | 0.3479 | 0.24261 | -0.29755 | -0.31128 | 0.09613 | 8.8486 | 60.8231 | -62.0682 | 60.466 | -61.8073 | 9.1599
1403.7344 | 123.0423 | -60.7315 | 62.0224 | 0.21144 | 0.05306 | 0.053324 | 0.0022074 | -0.0015157 | -0.00074255 | -0.00064093 | -51.9699 | 62.059 | -61.0794 | 0.009155 | 0.022888 | 0.004578 | -0.1236 | 0.21973 | 0.16937 | -0.31128 | -0.3479 | 0.036621 | 8.7616 | 60.7407 | -61.9995 | 60.4202 | -61.853 | 9.1095
1404.7656 | 122.9553 | -60.7452 | 62.0773 | -0.20817 | 0.057546 | 0.055888 | 0.0034892 | -0.0015157 | -0.0030924 | -0.0012817 | -52.0248 | 62.146 | -61.084 | 0.027466 | 0.045776 | 0.036621 | 0.14191 | 0.26093 | 0.28381 | -0.20599 | -0.33875 | 0.068664 | 8.7204 | 60.7727 | -62.0316 | 60.5392 | -61.7935 | 9.0591
1405.7344 | 123.0423 | -60.7086 | 62.0316 | -0.45231 | 0.052419 | 0.048838 | -0.0007832 | -0.00023392 | 0.00032545 | -0.00021353 | -52.0294 | 62.0499 | -61.0519 | 0.018311 | 0.041199 | 0.082397 | -0.07782 | 0.25177 | 0.20599 | -0.2655 | -0.34332 | 0.018311 | 8.6792 | 60.7269 | -61.9904 | 60.4431 | -61.8256 | 9.0225
1406.7656 | 122.9691 | -60.7498 | 62.0865 | -0.17003 | 0.053914 | 0.05482 | 0.0049846 | -0.00066112 | 0.00075285 | 0.00042727 | -52.0157 | 62.1368 | -61.0886 | 0.032043 | 0.07782 | 0.49439 | 0.2243 | -0.1831 | 0.29297 | -0.13275 | -0.33875 | 0.050354 | 8.7341 | 60.7819 | -62.0087 | 60.6171 | -61.7935 | 9.0729
1407.7344 | 123.0515 | -60.704 | 62.0407 | 0.18093 | 0.052205 | 0.049479 | -0.0001424 | -0.00066112 | -0.002238 | -0.00021353 | -52.0615 | 62.0041 | -61.0931 | 0.013733 | 0.022888 | 0.022888 | -0.086975 | 0.22888 | 0.19226 | -0.27924 | -0.3891 | -0.036621 | 8.6426 | 60.7178 | -62.0178 | 60.4248 | -61.8484 | 9.0317
1408.7656 | 123.0148 | -60.7315 | 62.0544 | 0.013079 | 0.056478 | 0.057597 | 0.01182 | 0.0014751 | -0.0011698 | -0.0017089 | -52.0065 | 62.1597 | -61.084 | 0.059509 | 0.009155 | 0.032043 | -0.25177 | 0.14648 | 0.2243 | -0.29755 | -0.35248 | 0.10529 | 8.725 | 60.791 | -62.0453 | 60.434 | -61.8301 | 9.0775
1409.7344 | 123.056 | -60.7544 | 62.0361 | 0.2267 | 0.054128 | 0.050547 | -0.0009968 | 0.0012615 | -0.0015972 | 0.0017091 | -52.1713 | 62.0361 | -61.0931 | 0.018311 | 0.022888 | 0.018311 | -0.091553 | 0.21057 | 0.18768 | -0.27924 | -0.33874 | 0 | 8.5831 | 60.7727 | -62.0132 | 60.4752 | -61.8484 | 8.9218
1410.7656 | 122.9279 | -60.7819 | 62.0453 | 0.12752 | 0.056691 | 0.053752 | 0.011607 | 0.0016887 | -0.0011698 | -0.00085453 | -52.2171 | 62.1735 | -61.0886 | -0.032043 | -0.041199 | -0.082397 | 0.013733 | 0.09613 | 0.2243 | -0.36621 | -0.3067 | 0.12817 | 8.5648 | 60.7498 | -62.0865 | 60.4156 | -61.821 | 8.8715
1411.7344 | 123.0606 | -60.6949 | 62.0087 | 0.20381 | 0.054342 | 0.055461 | 0.0004984 | 0.00083408 | -0.0015972 | 0.00064087 | -52.1759 | 62.0178 | -61.0931 | 0.018311 | 0.022888 | 0.013733 | -0.13733 | 0.19684 | 0.17853 | -0.29755 | -0.39825 | 0.009155 | 8.519 | 60.7132 | -61.9858 | 60.3973 | -61.8301 | 8.9172
1412.7812 | 123.0743 | -60.7269 | 62.027 | -0.017439 | 0.050283 | 0.053538 | -0.0014242 | -0.00023392 | 0.0018208 | 0.0010681 | -52.1713 | 62.0453 | -61.1023 | 0.045776 | 0.064087 | 0.07782 | -0.082397 | 0.27924 | 0.20599 | -0.26093 | -0.37537 | 0.01831 | 8.5556 | 60.7727 | -61.9629 | 60.466 | -61.821 | 8.931
1413.7344 | 123.024 | -60.7452 | 62.0087 | 0.14278 | 0.053487 | 0.049479 | 7.12e-05 | -0.0013021 | -0.00010175 | -0.00085453 | -52.2263 | 62.0224 | -61.0977 | 0.041199 | 0.022888 | 0.018311 | -0.064087 | 0.23346 | 0.21057 | -0.28381 | -0.35248 | 0.013733 | 8.519 | 60.7864 | -61.9858 | 60.4614 | -61.7981 | 8.8715
1414.7656 | 123.0789 | -60.7361 | 61.9995 | 0.27248 | 0.055623 | 0.057597 | 0.0084026 | 0.0040385 | -0.00031535 | -0.0010681 | -52.1393 | 62.0728 | -61.1114 | 0.068665 | 0.018311 | -0.018311 | -0.20142 | 0.16479 | 0.15564 | -0.39368 | -0.37537 | 0.073242 | 8.5968 | 60.8047 | -61.9812 | 60.3424 | -61.8439 | 8.9722
1415.7344 | 123.0469 | -60.7224 | 61.9995 | 0.15041 | 0.053487 | 0.054392 | 0.0015666 | -2.0324e-05 | 0.00011185 | -0.00021353 | -52.1759 | 62.0087 | -61.0931 | 0.050354 | 0.027466 | 0.013733 | -0.15106 | 0.20142 | 0.17395 | -0.3479 | -0.37079 | 0.009155 | 8.5464 | 60.7727 | -61.972 | 60.3745 | -61.8256 | 8.9172
1416.7656 | 122.9782 | -60.7544 | 62.0178 | 2.4774 | 0.055196 | 0.056315 | 0.0079752 | 0.0019023 | -0.00052895 | -0.00042733 | -52.3453 | 62.1231 | -61.1435 | -0.059509 | -0.073242 | -0.009155 | -0.050354 | 0.068665 | 0.21057 | -0.32501 | -0.3891 | 0.10529 | 8.4091 | 60.6949 | -62.0911 | 60.4294 | -61.8073 | 8.7982
1417.7344 | 123.0515 | -60.7315 | 62.0178 | 0.1733 | 0.05306 | 0.048838 | 7.12e-05 | 0.00040688 | -0.00031535 | -0.00021353 | -52.2171 | 62.0453 | -61.0977 | 0.013733 | 0.027466 | 0.022888 | -0.082397 | 0.21973 | 0.1831 | -0.28839 | -0.36621 | 0.027466 | 8.5144 | 60.7452 | -61.9904 | 60.4431 | -61.8347 | 8.8806
1418.7656 | 123.0011 | -60.7681 | 62.0224 | 0.081743 | 0.054769 | 0.05247 | 0.0079752 | 0.0012615 | -0.0015972 | -0.0010681 | -52.1347 | 62.1643 | -61.0931 | 0.018311 | -0.036621 | -0.036621 | 0.018311 | 0.16479 | 0.21515 | -0.31128 | -0.32501 | 0.14191 | 8.6334 | 60.7864 | -62.059 | 60.4568 | -61.8073 | 8.9584
1419.7344 | 123.0652 | -60.7224 | 62.0041 | 0.0054493 | 0.049001 | 0.046061 | -0.002065 | 0.0016887 | -0.0018108 | 0.0014953 | -52.2034 | 62.0224 | -61.1114 | 0.050354 | 0.086975 | 0.10529 | -0.059509 | 0.27466 | 0.20599 | -0.26093 | -0.3891 | 0.018311 | 8.519 | 60.7727 | -61.9171 | 60.4614 | -61.7981 | 8.9081
1420.7656 | 122.9965 | -60.759 | 62.0087 | 0.27248 | 0.057973 | 0.05247 | 0.0049846 | 0.00062048 | -0.0011698 | -0.0025635 | -52.1622 | 62.114 | -61.116 | -0.013733 | -0.041199 | -0.045776 | -0.082397 | 0.1236 | 0.17395 | -0.35248 | -0.35706 | 0.10529 | 8.5968 | 60.7452 | -62.0499 | 60.4065 | -61.8347 | 8.9539
1421.7344 | 123.0286 | -60.7315 | 62.0132 | 0.18855 | 0.053274 | 0.052683 | 0.0002848 | 0.0019023 | -0.0013834 | -0.00085453 | -52.1576 | 62.0087 | -61.1069 | 0.013733 | 0.004578 | 0.022888 | -0.11444 | 0.21057 | 0.16937 | -0.32501 | -0.37537 | -0.004578 | 8.5739 | 60.7452 | -62.0087 | 60.4065 | -61.8439 | 8.9493
1422.7812 | 123.0103 | -60.7269 | 62.0178 | 0.20381 | 0.056051 | 0.056101 | 0.0062662 | 0.0012615 | 0.00075285 | -0.0012817 | -52.1713 | 62.0773 | -61.0977 | -0.013733 | -0.018311 | -0.059509 | -0.091553 | 0.11902 | 0.20142 | -0.3479 | -0.37079 | 0.05951 | 8.5556 | 60.7132 | -62.0361 | 60.379 | -61.8164 | 8.9264
1423.7344 | 123.0331 | -60.7224 | 62.0041 | 0.1733 | 0.050496 | 0.050334 | -0.0009968 | 0.00083408 | -0.00052895 | 0.0010681 | -52.1896 | 62.0178 | -61.1114 | 0.022888 | 0.036621 | 0.036621 | -0.086975 | 0.23346 | 0.20142 | -0.27466 | -0.3891 | 0.013733 | 8.5327 | 60.7452 | -61.9675 | 60.4477 | -61.8027 | 8.9218
1424.7656 | 122.9599 | -60.7681 | 62.0178 | 0.21907 | 0.056691 | 0.052043 | 0.009257 | 0.0019023 | -0.0015972 | -0.0027771 | -52.2034 | 62.146 | -61.1023 | -0.073242 | -0.091553 | -0.11444 | -0.018311 | 0.086975 | 0.20599 | -0.3479 | -0.33417 | 0.12817 | 8.5648 | 60.6949 | -62.1094 | 60.4202 | -61.8118 | 8.8989
1425.7344 | 123.0423 | -60.7315 | 62.0132 | 0.11989 | 0.052419 | 0.052043 | -0.000356 | -0.00023392 | 0.00118 | 0.0012817 | -52.1988 | 62.0361 | -61.0977 | 0.018311 | 0.027466 | 0.027466 | -0.10071 | 0.2243 | 0.19226 | -0.30212 | -0.36621 | 0.022888 | 8.5327 | 60.7498 | -61.9858 | 60.4294 | -61.821 | 8.8989
1426.7656 | 122.9645 | -60.7773 | 62.0544 | 0.028338 | 0.054983 | 0.051615 | 0.009257 | 0.0033977 | -0.0026652 | -0.0025635 | -52.1347 | 62.1552 | -61.0611 | 0 | -0.013733 | -0.022888 | 0.009155 | 0.16937 | 0.22888 | -0.3067 | -0.28381 | 0.10071 | 8.6426 | 60.7773 | -62.0682 | 60.4706 | -61.8256 | 8.9264
1427.7344 | 122.9645 | -60.7315 | 62.0773 | -0.1624 | 0.053274 | 0.050334 | 0.0034892 | 0.00040688 | -0.0018108 | -0.0010681 | -52.1942 | 62.1002 | -61.1069 | 0.027466 | 0.022888 | 0.036621 | 0.13733 | 0.2655 | 0.29755 | -0.16937 | -0.37537 | 0.022888 | 8.5373 | 60.759 | -62.0544 | 60.5621 | -61.7798 | 8.9127
1428.7656 | 122.9645 | -60.7956 | 62.0407 | 0.20381 | 0.054555 | 0.053752 | 0.0043436 | 0.0053203 | -0.0011698 | -0.0010681 | -52.2079 | 62.1597 | -61.1114 | -0.050354 | -0.068665 | -0.10529 | -0.009155 | 0.10071 | 0.20142 | -0.3479 | -0.31586 | 0.11902 | 8.5876 | 60.7452 | -62.1094 | 60.4477 | -61.8393 | 8.9035
1429.7344 | 123.0331 | -60.7315 | 62.0178 | 0.21907 | 0.051137 | 0.052256 | 0.001353 | 0.0023295 | -0.0011698 | -0.0010681 | -52.2217 | 62.0178 | -61.1023 | 0.022888 | 0.032043 | 0.009155 | -0.15564 | 0.21515 | 0.18768 | -0.35248 | -0.37079 | 0 | 8.5098 | 60.7544 | -61.9858 | 60.379 | -61.8301 | 8.8806
1430.7656 | 123.0194 | -60.7361 | 62.0453 | 0.0054493 | 0.057546 | 0.051615 | 0.0079752 | 0.0038249 | -0.0011698 | -0.0021361 | -52.1896 | 62.146 | -61.0931 | 0.12817 | 0.036621 | 0.059509 | 0.036621 | 0.21057 | 0.23804 | -0.3067 | -0.35706 | 0.10071 | 8.5464 | 60.8643 | -62.0087 | 60.4294 | -61.8073 | 8.9035
1431.7344 | 123.0469 | -60.7315 | 62.0316 | 0.19618 | 0.051351 | 0.048625 | -0.0018514 | 0.0027567 | -0.0011698 | -0.00064093 | -52.3087 | 62.0224 | -61.1206 | 0.004578 | 0.022888 | 0.027466 | -0.091553 | 0.21515 | 0.17853 | -0.27008 | -0.3891 | -0.009155 | 8.4229 | 60.7361 | -62.0087 | 60.4614 | -61.853 | 8.8119
1432.7812 | 122.9874 | -60.759 | 62.0407 | 0.089373 | 0.05776 | 0.053324 | 0.0071208 | 0.00040688 | -0.00010175 | 0.00064087 | -52.5009 | 62.1002 | -61.1206 | -0.064087 | -0.082397 | -0.009155 | -0.004578 | 0.073242 | 0.22888 | -0.33417 | -0.36163 | 0.05951 | 8.2581 | 60.6949 | -62.1231 | 60.4248 | -61.8118 | 8.6197
1433.7344 | 123.0377 | -60.7178 | 62.0316 | 0.089373 | 0.051778 | 0.049266 | -0.0027058 | 0.00040688 | 0.00053925 | 0.0029907 | -52.3315 | 62.0407 | -61.0931 | 0.009155 | 0.036621 | 0.022888 | -0.059509 | 0.2243 | 0.20599 | -0.28839 | -0.37537 | 0.009155 | 8.3862 | 60.7269 | -61.9949 | 60.4294 | -61.8256 | 8.7616
1434.7656 | 122.9736 | -60.7498 | 62.0544 | 0.28774 | 0.055196 | 0.051615 | 0.0062662 | 0.0021159 | -0.00052895 | 0.00085447 | -52.2858 | 62.1552 | -61.0931 | -0.041199 | -0.073242 | -0.10071 | -0.018311 | 0.091553 | 0.2243 | -0.35248 | -0.34332 | 0.10071 | 8.4641 | 60.7086 | -62.1277 | 60.3973 | -61.8301 | 8.8074
1435.75 | 122.9736 | -60.7498 | 62.0682 | -0.36076 | 0.055623 | 0.050547 | 0.0037028 | 0.00019328 | -0.00052895 | 6.6667e-08 | -52.3041 | 62.1552 | -61.1206 | 0.013733 | 0.018311 | 0.022888 | 0.12817 | 0.25177 | 0.27466 | -0.24261 | -0.37079 | 0.086975 | 8.4457 | 60.7636 | -62.0499 | 60.5072 | -61.7935 | 8.8165
1436.7656 | 122.9462 | -60.7636 | 62.059 | 0.24959 | 0.054769 | 0.056101 | 0.0073344 | 0.0066019 | 0.00075285 | -0.0012817 | -52.2675 | 62.1552 | -61.1206 | 0.022888 | 0.35706 | 0.24261 | -0.15564 | 0.17395 | 0.21057 | -0.33417 | -0.35705 | 0.09613 | 8.4961 | 60.7864 | -61.702 | 60.4294 | -61.8484 | 8.8531
1437.7344 | 123.056 | -60.7086 | 62.0453 | 0.066485 | 0.051992 | 0.054606 | -0.0014242 | 0.0016887 | 0.00032545 | -0.00064093 | -52.2766 | 62.059 | -61.0886 | 0.009155 | 0.032043 | 0.041199 | -0.064087 | 0.23346 | 0.19684 | -0.25635 | -0.37994 | 0.013733 | 8.432 | 60.7178 | -62.0132 | 60.4523 | -61.8484 | 8.812
1438.7656 | 123.0011 | -60.7361 | 62.0499 | -0.078474 | 0.055623 | 0.050975 | 0.0081888 | 0.0021159 | -0.00031535 | -0.00021353 | -52.1759 | 62.1552 | -61.0657 | 0.041199 | 0.018311 | 0.032043 | 0.022888 | 0.25177 | 0.23804 | -0.27924 | -0.32959 | 0.10528 | 8.5602 | 60.7773 | -62.0316 | 60.4568 | -61.8118 | 8.8898
1439.7344 | 123.0606 | -60.7361 | 62.0041 | 0.21144 | 0.051137 | 0.049906 | -0.0007832 | 0.0016887 | -0.002238 | 6.6667e-08 | -52.1988 | 62.0499 | -61.116 | 0.018311 | 0.027466 | 0.041199 | -0.16022 | 0.24261 | 0.17395 | -0.37079 | -0.37994 | 0.045777 | 8.5373 | 60.7544 | -61.9766 | 60.3653 | -61.8301 | 8.9172
1440.7656 | 123.0103 | -60.6995 | 62.0407 | -0.11662 | 0.054342 | 0.052043 | 0.0071208 | 0.0038249 | -0.0013834 | -0.0014953 | -52.1667 | 62.1597 | -61.1069 | 0.073242 | 0.045776 | 0.064087 | 0.086975 | 0.2655 | 0.25635 | -0.25177 | -0.40741 | 0.11902 | 8.5327 | 60.7727 | -61.9949 | 60.4477 | -61.7844 | 8.9401
1441.7344 | 123.0789 | -60.6949 | 62.0132 | 0.82942 | 0.052205 | 0.052683 | 0.0009258 | 0.0038249 | -0.0013834 | 0.0021363 | -52.0706 | 62.0407 | -61.1023 | 0.082397 | 0.068665 | 0.009155 | -0.18768 | 0.21515 | 0.18768 | -0.29755 | -0.40741 | 0.027465 | 8.6243 | 60.7773 | -61.9446 | 60.3973 | -61.8256 | 9.0317
1442.7812 | 123.0286 | -60.704 | 62.0041 | 0.19618 | 0.051778 | 0.052683 | 0.0022074 | 0.0021159 | -0.00095615 | -0.00021353 | -52.1759 | 62.027 | -61.084 | 0.032043 | 0.036621 | 0.013733 | -0.15564 | 0.2243 | 0.17395 | -0.34332 | -0.37994 | 0.022889 | 8.5281 | 60.7361 | -61.9675 | 60.3607 | -61.8301 | 8.9081
1443.7344 | 123.056 | -60.704 | 61.9949 | 0.28011 | 0.053274 | 0.049052 | 0.0015666 | -0.0017293 | -0.0015972 | 0.00042727 | -52.1576 | 62.0316 | -61.0886 | 0.045776 | 0.050354 | 0.041199 | -0.16937 | 0.21515 | 0.17853 | -0.3479 | -0.38452 | 0.036621 | 8.5464 | 60.7498 | -61.9446 | 60.3561 | -61.8164 | 8.931
1444.7656 | 123.0148 | -60.7224 | 62.0316 | -0.14714 | 0.054128 | 0.050547 | 0.0084026 | -0.00066112 | -0.0041606 | -0.00064093 | -52.1347 | 62.1735 | -61.0611 | 0.068665 | 0.041199 | 0.045776 | 0.059509 | 0.27008 | 0.2655 | -0.27008 | -0.33874 | 0.14191 | 8.5876 | 60.791 | -61.9904 | 60.4523 | -61.7661 | 8.9264
1445.7344 | 123.0927 | -60.7224 | 61.9858 | 0.24959 | 0.052846 | 0.051829 | 0.00413 | 0.0025431 | -0.0011698 | -0.00042733 | -52.1255 | 62.0316 | -61.0886 | -0.013733 | 0.022888 | 0.15564 | -0.13733 | 0.17853 | 0.1831 | -0.3479 | -0.36621 | 0.045776 | 8.5968 | 60.7086 | -61.9629 | 60.3745 | -61.8027 | 8.963
1446.7656 | 122.9507 | -60.7636 | 62.0361 | 0.15041 | 0.056478 | 0.052897 | 0.011607 | 0.0042521 | -0.002238 | -0.0012817 | -52.2079 | 62.1368 | -61.1252 | -0.064087 | -0.091553 | -0.11444 | -0.009155 | 0.086975 | 0.19226 | -0.36163 | -0.36163 | 0.10071 | 8.5556 | 60.6995 | -62.1277 | 60.4019 | -61.8439 | 8.9172
1447.7344 | 123.0469 | -60.6949 | 62.0132 | 0.028338 | 0.050924 | 0.051829 | -0.0009968 | 0.0023295 | -0.0020244 | -0.00021353 | -52.1988 | 62.0407 | -61.1023 | 0.050354 | 0.073242 | 0.10071 | -0.059509 | 0.29755 | 0.2243 | -0.23804 | -0.40741 | 0.027465 | 8.4961 | 60.7452 | -61.94 | 60.4568 | -61.7889 | 8.9035
1448.7656 | 123.0469 | -60.7407 | 62.0178 | 0.2267 | 0.051137 | 0.049479 | -0.0007832 | -0.0010885 | -0.0011698 | -0.00042733 | -52.1851 | 62.0316 | -61.0931 | 0.013733 | 0.027466 | 0.027466 | -0.086975 | 0.23346 | 0.18768 | -0.29755 | -0.35248 | 0.013733 | 8.5556 | 60.7544 | -61.9904 | 60.4431 | -61.8301 | 8.9081
1449.7344 | 123.0606 | -60.7086 | 62.0178 | 0.26485 | 0.053701 | 0.05012 | 0.00648 | 0.0016887 | -0.00052895 | 0.00085447 | -52.1072 | 62.0728 | -61.0977 | 0.036621 | 0.022888 | 0.004578 | -0.1831 | 0.2243 | 0.16937 | -0.39368 | -0.3891 | 0.054932 | 8.6014 | 60.7452 | -61.9949 | 60.3149 | -61.8484 | 8.9905
1450.7656 | 123.0469 | -60.704 | 61.9904 | 0.066485 | 0.048787 | 0.052043 | -0.0029196 | -0.0015157 | 0.00032545 | -0.0014953 | -52.1759 | 62.027 | -61.0886 | 0.050354 | 0.059509 | 0.09613 | -0.054932 | 0.29755 | 0.20599 | -0.26093 | -0.38452 | 0.036622 | 8.5281 | 60.7544 | -61.9308 | 60.4431 | -61.7844 | 8.9127
1451.7344 | 123.0698 | -60.7178 | 62.0178 | 0.27248 | 0.051351 | 0.052897 | 0.0056254 | 0.0012615 | 0.00096645 | 6.6667e-08 | -52.0706 | 62.0361 | -61.0748 | 0.054932 | 0.018311 | 0.036621 | -0.19226 | 0.2243 | 0.15106 | -0.37994 | -0.35706 | 0.018311 | 8.6472 | 60.7727 | -61.9995 | 60.3378 | -61.8668 | 9.0042
1452.7812 | 123.0698 | -60.7269 | 61.9904 | 1.0507 | 0.050924 | 0.05012 | 0.0028484 | 0.0010477 | -0.00031535 | -0.0023499 | -52.0157 | 62.0407 | -61.0886 | 0.073242 | 0.07782 | 0.027466 | -0.21057 | 0.22888 | 0.17853 | -0.30212 | -0.36163 | 0.050354 | 8.7112 | 60.8002 | -61.9125 | 60.4248 | -61.8118 | 9.0729
1453.75 | 122.9782 | -60.7315 | 62.0544 | -0.1624 | 0.053701 | 0.049266 | 0.0022074 | -0.0015157 | 0.00032545 | -0.00021353 | -52.1439 | 62.1094 | -61.084 | 0.050354 | 0.036621 | 0.068665 | 0.091553 | 0.31128 | 0.27924 | -0.18768 | -0.35248 | 0.054932 | 8.5876 | 60.7819 | -62.0178 | 60.5438 | -61.7752 | 8.9401
1454.7656 | 122.9462 | -60.7361 | 62.0544 | -0.17766 | 0.052846 | 0.049052 | 0.004771 | -0.00023392 | -0.0015972 | -0.00064093 | -52.2217 | 62.146 | -61.0886 | 0.022888 | 0.009155 | 0.018311 | 0.32044 | 0.68207 | 0.30212 | -0.14191 | -0.35248 | 0.091553 | 8.5144 | 60.759 | -62.0453 | 60.5942 | -61.7523 | 8.8669
1455.7344 | 123.0652 | -60.7361 | 62.0041 | 0.29537 | 0.055837 | 0.056529 | 0.0060526 | 0.0021159 | -0.00095615 | -0.0010681 | -52.1576 | 62.0911 | -61.116 | 0.018311 | -0.009155 | -0.027466 | -0.16022 | 0.21057 | 0.1831 | -0.37537 | -0.37994 | 0.086975 | 8.5785 | 60.7544 | -62.0132 | 60.3607 | -61.821 | 8.9584
1456.7656 | 122.9782 | -60.759 | 62.0544 | -0.1624 | 0.053487 | 0.054606 | 0.0032756 | 0.0023295 | -0.0015972 | -0.00042733 | -52.2263 | 62.0956 | -61.1069 | 0.027466 | 0.022888 | 0.045776 | 0.15564 | 0.25635 | 0.3067 | -0.20142 | -0.3479 | 0.041199 | 8.5327 | 60.7864 | -62.0316 | 60.5576 | -61.7477 | 8.8806
1457.75 | 122.9141 | -60.7407 | 62.059 | -0.2158 | 0.053487 | 0.048197 | 0.0054118 | 0.0033977 | -0.00010175 | -0.0027771 | -52.2171 | 62.1552 | -61.0657 | 0.018311 | 0.013733 | 0.027466 | 0.23346 | 0.67749 | 0.31586 | -0.13733 | -0.32501 | 0.09613 | 8.5236 | 60.759 | -62.0453 | 60.6033 | -61.7432 | 8.8486
1458.7656 | 123.0011 | -60.7498 | 62.0453 | 0.0054493 | 0.054342 | 0.055247 | 0.0071208 | 0.0040385 | -0.0045878 | -0.00021353 | -52.2171 | 62.0682 | -61.1389 | 0.036621 | -0.004578 | 0.036621 | 0.041199 | 0.21515 | 0.24261 | -0.27924 | -0.3891 | 0.022888 | 8.5327 | 60.7864 | -62.0499 | 60.4706 | -61.8027 | 8.9218
1459.7344 | 123.0881 | -60.7132 | 61.9949 | 0.24959 | 0.056264 | 0.052897 | 0.0051982 | 0.0031841 | -0.0018108 | -0.0010681 | -52.1347 | 62.1185 | -61.0977 | 0.036621 | 0.032043 | 0.009155 | -0.16479 | 0.15564 | 0.16479 | -0.40283 | -0.38452 | 0.1236 | 8.5785 | 60.7498 | -61.9629 | 60.3104 | -61.8301 | 8.963
1460.7656 | 123.0011 | -60.7361 | 61.9949 | -0.032697 | 0.056905 | 0.052256 | 0.0071208 | 0.0038249 | -0.0018108 | -0.00085453 | -52.1027 | 62.1368 | -61.0931 | 0.050354 | 0.032043 | 0.022888 | 0.018311 | 0.2243 | 0.23346 | -0.28381 | -0.35706 | 0.14191 | 8.6334 | 60.7864 | -61.9629 | 60.4523 | -61.7615 | 8.9905
1461.7344 | 123.0927 | -60.7269 | 61.9904 | 0.29537 | 0.054769 | 0.055674 | 0.00413 | 0.0027567 | 0.00075285 | -0.00021353 | -52.1164 | 62.0773 | -61.084 | 0.041199 | 0.045776 | 0.018311 | -0.17395 | 0.21515 | 0.14648 | -0.36621 | -0.35706 | 0.086976 | 8.6105 | 60.7681 | -61.9446 | 60.3607 | -61.8439 | 8.9676
1462.7812 | 123.0698 | -60.7407 | 61.9995 | 0.24959 | 0.052419 | 0.054606 | 0.0028484 | 0.0033977 | 0.0013936 | 0.00021367 | -52.0844 | 62.0407 | -61.0748 | -0.20142 | 0.16479 | 0.48065 | -0.19226 | 0.14648 | 0.15564 | -0.40283 | -0.33417 | 0.041198 | 8.6563 | 60.5392 | -61.8347 | 60.3378 | -61.8439 | 8.9905
1463.7344 | 123.1522 | -60.7452 | 61.9858 | 0.28774 | 0.053914 | 0.051402 | 0.0028484 | 0.0033977 | -0.00010175 | 0.00021367 | -52.0798 | 62.0316 | -61.0977 | 0.050354 | 0.036621 | 0.041199 | -0.1831 | 0.22888 | 0.15564 | -0.37079 | -0.35248 | 0.045776 | 8.6655 | 60.7956 | -61.9492 | 60.3744 | -61.8301 | 9.0179
1464.7656 | 123.0835 | -60.7269 | 61.9995 | 0.25722 | 0.054769 | 0.052683 | 0.0084026 | 0.0025431 | -0.00074255 | -0.00085453 | -52.0935 | 62.0682 | -61.0794 | 0.045776 | 0.059509 | 0.027466 | -0.19684 | 0.21057 | 0.17395 | -0.3891 | -0.35248 | 0.068664 | 8.6334 | 60.7727 | -61.94 | 60.3378 | -61.8256 | 8.9859
1465.7344 | 123.0148 | -60.759 | 62.0087 | 0.19618 | 0.0584 | 0.053324 | 0.00648 | 0.0016887 | 0.00118 | -0.00042733 | -52.1072 | 62.1231 | -61.1298 | -0.036621 | -0.036621 | -0.054932 | -0.10071 | 0.1236 | 0.17853 | -0.36163 | -0.37079 | 0.11444 | 8.6517 | 60.7224 | -62.0453 | 60.3973 | -61.8301 | 9.0225
1466.7656 | 123.0057 | -60.7636 | 62.0453 | -0.1624 | 0.051992 | 0.051402 | 0.0062662 | 0.0023295 | -0.0015972 | 0.00021367 | -52.0706 | 62.1323 | -61.0931 | 0.027466 | 0.032043 | 0.032043 | 0.11444 | 0.24719 | 0.27008 | -0.20142 | -0.32959 | 0.086975 | 8.6929 | 60.791 | -62.0132 | 60.5621 | -61.7752 | 9.0225
1467.75 | 122.9965 | -60.7452 | 62.0178 | 0.20381 | 0.05541 | 0.05482 | 0.0060526 | 0.0029705 | -0.00095615 | 0.0014953 | -52.0798 | 62.1185 | -61.1298 | -0.045776 | -0.045776 | -0.068665 | -0.064087 | 0.10529 | 0.2243 | -0.34332 | -0.38452 | 0.10071 | 8.6655 | 60.6995 | -62.0636 | 60.4019 | -61.7935 | 9.05
1468.7656 | 123.0927 | -60.7224 | 62.0178 | -0.12425 | 0.05071 | 0.050547 | -0.0033468 | 0.0027567 | -0.005015 | -0.0029907 | -52.0065 | 62.027 | -61.084 | 0.45776 | 0.09613 | -0.49896 | -0.16022 | 0.48065 | 0.25635 | -0.19684 | -0.36163 | 0.009156 | 8.7158 | 61.1801 | -61.9217 | 60.5255 | -61.7615 | 9.0775
1469.7344 | 122.9691 | -60.7956 | 62.0224 | 0.21907 | 0.054769 | 0.053965 | 0.0081888 | 0.0029705 | -0.00052895 | -0.0010681 | -52.066 | 62.1185 | -61.1114 | -0.059509 | -0.059509 | -0.091553 | -0.009155 | 0.09613 | 0.20142 | -0.33417 | -0.31586 | 0.09613 | 8.7296 | 60.7361 | -62.0819 | 60.4614 | -61.821 | 9.0454
1470.7656 | 123.024 | -60.759 | 62.0224 | -0.040327 | 0.054128 | 0.053752 | 0.00648 | 0.0042521 | -0.0015972 | -0.0023499 | -51.9836 | 62.1185 | -61.0748 | 0.041199 | 0.018311 | 0.036621 | 0.004578 | -0.036621 | 0.24719 | -0.3067 | -0.31586 | 0.09613 | 8.7753 | 60.8002 | -62.0041 | 60.4523 | -61.7752 | 9.0912
1471.7344 | 123.0652 | -60.7498 | 61.9858 | 0.32588 | 0.054342 | 0.054606 | 0.0032756 | 0.0040385 | -0.0020244 | 0.00021367 | -51.9699 | 62.0682 | -61.1023 | 0.032043 | 0.045776 | 0.036621 | -0.19226 | 0.21057 | 0.15564 | -0.36621 | -0.35248 | 0.082397 | 8.7799 | 60.7819 | -61.94 | 60.3836 | -61.8301 | 9.1324
1472.7812 | 122.937 | -60.791 | 62.0499 | 0.10463 | 0.056051 | 0.056956 | 0.0079752 | 0.0048931 | -0.00031535 | -0.00042733 | -52.0065 | 62.1597 | -61.1343 | -0.032043 | -0.064087 | -0.091553 | 0.036621 | 0.11444 | 0.2243 | -0.33875 | -0.34332 | 0.10986 | 8.7845 | 60.759 | -62.114 | 60.4523 | -61.8256 | 9.1278
1473.7344 | 122.9828 | -60.7773 | 61.9995 | 0.20381 | 0.054342 | 0.055461 | 0.007548 | 0.0057475 | 0.0024618 | -0.00042733 | -52.0248 | 62.146 | -61.1114 | -0.064087 | -0.050354 | -0.09613 | -0.004578 | 0.086975 | 0.21973 | -0.36163 | -0.33417 | 0.14648 | 8.7524 | 60.7132 | -62.0499 | 60.4156 | -61.7798 | 9.0866
1474.75 | 123.0698 | -60.7224 | 62.0087 | 0.20381 | 0.053914 | 0.049266 | -0.0035604 | 0.0036113 | 0.00032545 | 0.0014953 | -52.0157 | 62.0178 | -61.116 | 0 | 0.022888 | 0.027466 | -0.068665 | 0.22888 | 0.20142 | -0.27924 | -0.39368 | 0.009155 | 8.7067 | 60.7224 | -61.9858 | 60.4431 | -61.8073 | 9.1003
1475.7344 | 123.024 | -60.759 | 61.9949 | 0.32588 | 0.057546 | 0.051829 | 0.0054118 | 0.0033977 | -0.0011698 | -0.0010681 | -51.9699 | 62.1094 | -61.1114 | -0.022888 | -0.036621 | -0.032043 | -0.10529 | 0.14191 | 0.17395 | -0.36163 | -0.35248 | 0.11444 | 8.7891 | 60.7361 | -62.0316 | 60.3973 | -61.821 | 9.1415
1476.7656 | 122.9691 | -60.7773 | 62.0407 | -0.17003 | 0.056264 | 0.053965 | 0.0051982 | 0.0019023 | -0.0011698 | 0.00042727 | -51.9974 | 62.1323 | -61.116 | -0.11444 | -0.26093 | -0.064087 | 0.22888 | 0.18768 | 0.28381 | -0.17395 | -0.33875 | 0.091553 | 8.7799 | 60.6628 | -62.3016 | 60.6033 | -61.7569 | 9.1187
1477.75 | 123.0011 | -60.7636 | 62.0636 | -0.13951 | 0.054555 | 0.050975 | 0.0071208 | 0.0019023 | -0.0013834 | 0.0010681 | -51.9241 | 62.1185 | -61.084 | 0.045776 | 0.036621 | 0.073242 | 0.068665 | 0.25635 | 0.27924 | -0.24261 | -0.32043 | 0.054931 | 8.8394 | 60.8093 | -62.027 | 60.5209 | -61.7844 | 9.1599
1478.7656 | 123.0194 | -60.7544 | 62.0224 | -0.11662 | 0.055623 | 0.055461 | 0.0066936 | 0.0046793 | 0.0018208 | -0.0014953 | -51.9196 | 62.146 | -61.0977 | 0.054932 | 0.07782 | 0.07782 | 0.082397 | 0.27008 | 0.2655 | -0.26093 | -0.34332 | 0.1236 | 8.8348 | 60.8093 | -61.9446 | 60.4935 | -61.7569 | 9.1782
1479.7344 | 123.0789 | -60.7407 | 61.9812 | 0.303 | 0.053914 | 0.052683 | 0.0039164 | 0.0066019 | 0.00011185 | -0.0019225 | -51.9012 | 62.0544 | -61.0977 | 0.045776 | 0.050354 | 0.036621 | -0.20142 | 0.21515 | 0.15106 | -0.3891 | -0.35706 | 0.073242 | 8.8394 | 60.7864 | -61.9308 | 60.3516 | -61.8301 | 9.1965
1480.7656 | 123.0515 | -60.7132 | 61.9995 | 0.035967 | 0.052846 | 0.050761 | -0.0024922 | 0.0014751 | -0.0024516 | -0.00064093 | -51.9928 | 62.0132 | -61.1114 | -0.004578 | 0.045776 | 0.032043 | -0.059509 | 0.23804 | 0.20599 | -0.28839 | -0.39825 | 0.013733 | 8.7204 | 60.7086 | -61.9537 | 60.4248 | -61.7935 | 9.1187
1481.7344 | 122.9553 | -60.7956 | 62.0087 | 0.23433 | 0.058828 | 0.058238 | 0.009257 | 0.0010477 | 0.0024618 | -0.0014953 | -51.9882 | 62.1094 | -61.116 | -0.059509 | -0.073242 | -0.086975 | -0.022888 | 0.086975 | 0.23346 | -0.35706 | -0.32044 | 0.10071 | 8.8074 | 60.7361 | -62.0819 | 60.4385 | -61.7752 | 9.1278
1482.7812 | 122.9736 | -60.7727 | 62.0224 | 0.051226 | 0.056905 | 0.058665 | 0.0049846 | 0.0023295 | -0.00031535 | -0.0014953 | -51.9241 | 62.1185 | -61.1252 | 0.032043 | 0.013733 | 0.004578 | 0.045776 | 0.21515 | 0.25635 | -0.25177 | -0.35248 | 0.09613 | 8.8486 | 60.8047 | -62.0087 | 60.5209 | -61.7661 | 9.2011
1483.7344 | 122.937 | -60.791 | 62.0132 | 0.16567 | 0.056264 | 0.055033 | 0.0079752 | 0.0051067 | -0.0011698 | -0.0019225 | -51.9562 | 62.1368 | -61.1389 | -0.073242 | -0.07782 | -0.10529 | 0.013733 | 0.086975 | 0.21973 | -0.36163 | -0.3479 | 0.1236 | 8.8348 | 60.7178 | -62.0911 | 60.4294 | -61.7935 | 9.1827
1484.75 | 123.056 | -60.7269 | 61.9675 | 0.44795 | 0.054128 | 0.052683 | -0.0001424 | 0.0025431 | -0.00052895 | -0.00064093 | -51.9104 | 62.0178 | -61.1114 | 0.041199 | 0.059509 | 0.045776 | -0.16937 | 0.23804 | 0.16937 | -0.32959 | -0.38452 | 0.050354 | 8.8165 | 60.7681 | -61.908 | 60.3973 | -61.7981 | 9.201
1485.7344 | 122.9507 | -60.7819 | 62.0132 | 0.11989 | 0.057973 | 0.053538 | 0.0077616 | 0.0036113 | -0.00010175 | -0.0012817 | -51.9241 | 62.1277 | -61.1252 | -0.032043 | -0.059509 | -0.054932 | 0.032043 | 0.11444 | 0.21057 | -0.36163 | -0.34332 | 0.11444 | 8.8577 | 60.7498 | -62.0728 | 60.4202 | -61.8027 | 9.2011
1486.7656 | 123.0743 | -60.7269 | 62.0178 | -0.37602 | 0.051565 | 0.05012 | -0.002065 | 0.0012615 | -0.00031535 | -0.0012817 | -51.9196 | 62.0132 | -61.1206 | 0.086975 | 0.10986 | 0.13275 | -0.004578 | 0.35706 | 0.22888 | -0.2243 | -0.39368 | -0.004577 | 8.8074 | 60.8139 | -61.908 | 60.5026 | -61.7889 | 9.201
1487.7344 | 123.0423 | -60.7269 | 61.9904 | 0.23433 | 0.054769 | 0.049479 | -0.0001424 | 0.00062048 | -0.00031535 | 0.0010681 | -51.9241 | 62.0178 | -61.1206 | -0.009155 | 0.027466 | 0 | -0.11902 | 0.20599 | 0.17853 | -0.3067 | -0.39368 | 0.027466 | 8.8028 | 60.7178 | -61.9629 | 60.4202 | -61.8118 | 9.1965
1488.7656 | 123.0286 | -60.759 | 61.9675 | 0.19618 | 0.053914 | 0.05012 | 0.0002848 | -0.00087492 | -0.00052895 | 0.0014953 | -51.915 | 61.9949 | -61.1481 | 0 | -0.004578 | -0.022888 | -0.10986 | 0.21057 | 0.20142 | -0.31128 | -0.3891 | 0.027466 | 8.844 | 60.759 | -61.972 | 60.4477 | -61.7661 | 9.2331
1489.7344 | 122.9462 | -60.791 | 62.0316 | 0.18093 | 0.058187 | 0.049479 | 0.01118 | 0.00083408 | -0.00010175 | -0.00085453 | -51.8692 | 62.1185 | -61.1252 | -0.018311 | -0.068665 | -0.091553 | 0.013733 | 0.10071 | 0.2243 | -0.3479 | -0.33417 | 0.086975 | 8.9218 | 60.7727 | -62.1002 | 60.4431 | -61.8073 | 9.256
1490.7656 | 123.0835 | -60.7361 | 61.972 | 0.020708 | 0.049428 | 0.049693 | -0.002065 | -0.00023392 | -0.0015972 | -0.0017089 | -51.8967 | 62.0132 | -61.1206 | 0.073242 | 0.091553 | 0.1236 | -0.045776 | 0.34332 | 0.23346 | -0.23804 | -0.38452 | 0.041199 | 8.8394 | 60.8093 | -61.8805 | 60.498 | -61.7386 | 9.2239
1491.7344 | 122.9416 | -60.8002 | 62.0178 | 0.081743 | 0.057546 | 0.055247 | 0.0084026 | 0.0023295 | -0.0026652 | -0.00064093 | -51.8372 | 62.1597 | -61.0977 | -0.013733 | -0.050354 | -0.050354 | 0.032043 | 0.14648 | 0.22888 | -0.31586 | -0.29755 | 0.14191 | 8.963 | 60.7864 | -62.0682 | 60.4843 | -61.7889 | 9.2606
1492.7812 | 123.0469 | -60.7361 | 61.9949 | 0.38692 | 0.053274 | 0.052897 | -0.0014242 | 0.00062048 | 0.0016072 | 0.00042727 | -51.8829 | 61.9904 | -61.1114 | 0.022888 | 0.050354 | 0.050354 | -0.068665 | 0.25635 | 0.20142 | -0.28839 | -0.37537 | -0.004578 | 8.8531 | 60.759 | -61.9446 | 60.4477 | -61.7935 | 9.2285
1493.7344 | 122.9782 | -60.7544 | 62.0178 | 0.051226 | 0.055623 | 0.054392 | 0.0094706 | 0.0016887 | -0.002238 | -0.0038451 | -51.8143 | 62.1231 | -61.116 | 0.013733 | -0.027466 | -0.054932 | 0.009155 | 0.15106 | 0.21057 | -0.30212 | -0.36163 | 0.10529 | 8.9401 | 60.7681 | -62.0453 | 60.4523 | -61.8073 | 9.3018
1494.7656 | 123.0743 | -60.7727 | 61.9812 | 0.020708 | 0.050069 | 0.047984 | -0.0033468 | 0.00083408 | -0.0011698 | -0.00042733 | -51.8967 | 61.9949 | -61.1206 | 0.036621 | 0.068665 | 0.082397 | -0.050354 | 0.29297 | 0.23346 | -0.25635 | -0.3479 | 0.013733 | 8.876 | 60.8093 | -61.9125 | 60.5164 | -61.7477 | 9.2239
1495.75 | 123.0789 | -60.7361 | 61.9904 | 2.0425 | 0.05306 | 0.053324 | -0.0009968 | 0.0010477 | -0.0013834 | -0.0014953 | -51.7776 | 61.9949 | -61.0977 | 0.10071 | 0.13275 | 0.14191 | -0.027466 | 0.37994 | 0.21057 | -0.24719 | -0.36163 | 0.004578 | 8.9584 | 60.8368 | -61.8576 | 60.4889 | -61.7798 | 9.3201
1496.7656 | 122.9553 | -60.791 | 62.0499 | -0.20817 | 0.05306 | 0.050334 | 0.00413 | -0.0023701 | -0.00031535 | -0.0036315 | -51.8784 | 62.1231 | -61.1298 | 0.022888 | 0.009155 | 0.027466 | 0.13733 | 0.23804 | 0.29755 | -0.20599 | -0.33875 | 0.073242 | 8.9127 | 60.8139 | -62.0407 | 60.585 | -61.7523 | 9.2514
1497.7344 | 122.937 | -60.7956 | 62.0132 | 0.18855 | 0.056691 | 0.054606 | 0.0073344 | 0.0031841 | -0.00074255 | -0.0010681 | -51.8738 | 62.0773 | -61.1755 | -0.054932 | -0.073242 | -0.11444 | -0.013733 | 0.10071 | 0.19684 | -0.34332 | -0.37994 | 0.064087 | 8.9218 | 60.7407 | -62.0865 | 60.4523 | -61.8164 | 9.3018
1498.7656 | 123.0606 | -60.7498 | 61.9675 | -0.13188 | 0.052205 | 0.047984 | 0.0004984 | -2.0324e-05 | -0.00010175 | -0.00042733 | -51.7227 | 62.0361 | -61.1252 | 0 | 0.068665 | 0.21057 | -0.07782 | 0.30212 | 0.21973 | -0.25635 | -0.37537 | 0.068665 | 9.0271 | 60.7498 | -61.8988 | 60.4935 | -61.7477 | 9.4025
1499.7344 | 122.9416 | -60.8276 | 62.0087 | 0.14278 | 0.05541 | 0.05781 | 0.0090434 | 0.0029705 | -0.0020244 | -0.0012817 | -51.8509 | 62.0956 | -61.1526 | -0.068665 | -0.068665 | -0.091553 | 0.013733 | 0.086975 | 0.21973 | -0.36163 | -0.32501 | 0.086975 | 8.9767 | 60.759 | -62.0773 | 60.466 | -61.7889 | 9.3018
1500.7656 | 123.0377 | -60.7956 | 61.972 | 0.13515 | 0.053701 | 0.050547 | -0.0029196 | 0.0025431 | -0.00010175 | 0.00042727 | -51.8738 | 62.0178 | -61.1664 | 0.009155 | 0.032043 | 0.027466 | -0.073242 | 0.22888 | 0.20599 | -0.27466 | -0.37079 | 0.045776 | 8.9218 | 60.8047 | -61.94 | 60.5209 | -61.7661 | 9.2926
1501.7344 | 123.0057 | -60.8002 | 62.0041 | -0.032697 | 0.05776 | 0.055461 | 0.0088298 | 0.0036113 | -0.0015972 | -0.0017089 | -51.7914 | 62.1048 | -61.1069 | 0.027466 | 0.004578 | 0.013733 | 0.004578 | 0.16937 | 0.22888 | -0.28839 | -0.3067 | 0.10071 | 9.0088 | 60.8276 | -61.9995 | 60.5118 | -61.7752 | 9.3155
1502.7656 | 123.0331 | -60.7727 | 61.9675 | 0.2267 | 0.054342 | 0.052256 | 0.0004984 | 0.0010477 | 0.002248 | -0.00064093 | -51.8509 | 62.0087 | -61.1343 | 0.032043 | 0.036621 | -0.004578 | -0.15564 | 0.21057 | 0.1831 | -0.32501 | -0.36163 | 0.041199 | 8.9218 | 60.8047 | -61.9308 | 60.4477 | -61.7844 | 9.2834
1503.7344 | 122.9553 | -60.8322 | 61.9858 | 0.21907 | 0.057332 | 0.056101 | 0.009257 | 0.0042521 | 0.00053925 | 0.00021367 | -51.8784 | 62.0956 | -61.1938 | -0.027466 | -0.054932 | -0.082397 | -0.022888 | 0.10071 | 0.21057 | -0.35248 | -0.36163 | 0.10986 | 8.9539 | 60.8047 | -62.0407 | 60.4797 | -61.7752 | 9.3155
1504.7812 | 123.0606 | -60.759 | 61.9354 | 0.28011 | 0.052205 | 0.052897 | 0.0034892 | 0.0038249 | -0.0018108 | 0.0010681 | -51.7914 | 62.0041 | -61.1618 | 0.041199 | 0.059509 | 0.022888 | -0.20142 | 0.21057 | 0.16479 | -0.37537 | -0.40283 | 0.068664 | 8.9676 | 60.8002 | -61.8759 | 60.3836 | -61.7706 | 9.3704
1505.7344 | 122.9965 | -60.8002 | 61.9904 | -0.0021797 | 0.054342 | 0.054179 | 0.0066936 | 0.0040385 | -0.00031535 | -0.0014953 | -51.7868 | 62.1002 | -61.1298 | 0.050354 | 0.018311 | 0.009155 | 0.013733 | 0.24261 | 0.21973 | -0.2655 | -0.32959 | 0.10986 | 9.0134 | 60.8505 | -61.972 | 60.5347 | -61.7706 | 9.343
1506.7656 | 122.9691 | -60.7819 | 61.9904 | -0.20817 | 0.052633 | 0.053111 | 7.12e-05 | 0.00040688 | -0.0015972 | 0.0012817 | -51.8921 | 62.0773 | -61.1755 | 0.013733 | 0.032043 | 0.041199 | 0.15106 | 0.23346 | 0.29297 | -0.17395 | -0.39368 | 0.086976 | 8.8898 | 60.7956 | -61.9583 | 60.6079 | -61.6974 | 9.2834
1507.7344 | 122.9599 | -60.8231 | 61.972 | 0.23433 | 0.05776 | 0.056956 | 0.0045574 | 0.0046793 | 0.00032545 | 6.6667e-08 | -52.0844 | 62.0682 | -61.1572 | -0.064087 | -0.091553 | -0.004578 | 0.004578 | 0.064087 | 0.2243 | -0.31128 | -0.33417 | 0.09613 | 8.7387 | 60.759 | -62.0636 | 60.5118 | -61.7477 | 9.0729
1508.7656 | 122.9645 | -60.791 | 61.9675 | -0.055586 | 0.054983 | 0.051829 | 0.0073344 | 0.0029705 | -0.0015972 | -0.00085453 | -51.7822 | 62.0865 | -61.1435 | 0.054932 | 0.036621 | 0.036621 | 0.027466 | 0.23346 | 0.24719 | -0.27466 | -0.35248 | 0.11902 | 9.0088 | 60.8459 | -61.9308 | 60.5164 | -61.7203 | 9.3613
1509.7344 | 123.0743 | -60.7361 | 61.972 | -0.017439 | 0.051778 | 0.048625 | -0.0022786 | 0.0021159 | -0.0013834 | -0.00042733 | -51.8143 | 61.9766 | -61.1389 | 0.07782 | 0.11444 | 0.12817 | -0.054932 | 0.33417 | 0.22888 | -0.25635 | -0.40283 | 0.004578 | 8.9218 | 60.8139 | -61.8576 | 60.4797 | -61.7432 | 9.3246
1510.7656 | 122.9507 | -60.8093 | 62.027 | -0.17003 | 0.051565 | 0.047557 | 0.0028484 | -2.0324e-05 | -0.0024516 | -0.0014953 | -51.8738 | 62.0911 | -61.1389 | 0.009155 | -0.004578 | 0.036621 | 0.16479 | 0.26093 | 0.28381 | -0.19684 | -0.32959 | 0.064086 | 8.9355 | 60.8185 | -62.0316 | 60.6125 | -61.7432 | 9.2651
1511.7344 | 122.937 | -60.7956 | 61.9858 | 0.21144 | 0.057973 | 0.055461 | 0.0071208 | 0.0061747 | -0.0011698 | -0.0019225 | -51.828 | 62.0911 | -61.171 | -0.054932 | -0.073242 | -0.10529 | 0.009155 | 0.082397 | 0.21973 | -0.37994 | -0.37537 | 0.10529 | 8.9676 | 60.7407 | -62.059 | 60.4156 | -61.7661 | 9.343
1512.7656 | 123.0331 | -60.759 | 61.9766 | -0.11662 | 0.050924 | 0.050547 | -0.0027058 | 0.0031841 | -0.0015972 | 0.00042727 | -51.7776 | 62.0041 | -61.1343 | 0.050354 | 0.21973 | 0.086975 | -0.16479 | 0.3891 | 0.22888 | -0.21515 | -0.37537 | 0.027465 | 8.9813 | 60.8093 | -61.7569 | 60.5438 | -61.7477 | 9.3567
1513.7344 | 122.937 | -60.8139 | 62.0224 | 0.089373 | 0.056691 | 0.05717 | 0.0073344 | 0.0025431 | -0.00052895 | -0.0010681 | -51.8097 | 62.0865 | -61.1572 | -0.054932 | -0.068665 | -0.10529 | 0.004578 | 0.082397 | 0.21515 | -0.36621 | -0.34332 | 0.064087 | 9.0042 | 60.759 | -62.0911 | 60.4477 | -61.8073 | 9.3475
1514.7656 | 122.9828 | -60.8231 | 61.9904 | 0.2267 | 0.054342 | 0.048625 | 0.0062662 | 0.0033977 | -0.00031535 | -0.00064093 | -51.828 | 62.0544 | -61.1618 | -0.041199 | -0.059509 | -0.086975 | -0.073242 | 0.11902 | 0.19684 | -0.3479 | -0.33874 | 0.064087 | 8.9951 | 60.7819 | -62.0499 | 60.4752 | -61.7935 | 9.3338
1515.7344 | 122.9691 | -60.8047 | 61.9949 | 0.19618 | 0.055837 | 0.053324 | 0.0066936 | 0.0042521 | -0.0013834 | -0.0021361 | -51.8097 | 62.0819 | -61.1755 | -0.050354 | -0.50812 | -0.57678 | 0.4303 | 0.59509 | 0.17853 | -0.38452 | -0.37079 | 0.086975 | 8.9951 | 60.7544 | -62.5031 | 60.4202 | -61.8164 | 9.3658
1516.7656 | 123.0286 | -60.7956 | 61.9766 | -0.13951 | 0.051565 | 0.049266 | -0.0039876 | 0.0012615 | -0.00074255 | -0.00021353 | -51.7548 | 62.027 | -61.1206 | 0.091553 | 0.10071 | 0.15564 | 0.050354 | 0.34332 | 0.27008 | -0.20599 | -0.32501 | 0.050354 | 9.0408 | 60.8871 | -61.8759 | 60.5896 | -61.7065 | 9.3658
1517.7344 | 122.9874 | -60.8139 | 61.972 | 0.19618 | 0.055623 | 0.052256 | 0.0060526 | 0.0027567 | 0.00096645 | -0.00064093 | -51.7776 | 62.0728 | -61.1847 | -0.032043 | -0.050354 | -0.050354 | -0.073242 | 0.1236 | 0.19684 | -0.34332 | -0.37079 | 0.10071 | 9.0363 | 60.7819 | -62.0224 | 60.4706 | -61.7752 | 9.407
1518.7656 | 122.9965 | -60.8093 | 61.9949 | -0.13951 | 0.054555 | 0.048625 | 0.0045574 | 0.0033977 | -0.00010175 | -0.0012817 | -51.7685 | 62.0911 | -61.1847 | 0.022888 | 0.022888 | 0.045776 | 0.11444 | 0.24261 | 0.27924 | -0.20599 | -0.37537 | 0.09613 | 9.0408 | 60.8322 | -61.972 | 60.6033 | -61.7157 | 9.4162
1519.75 | 123.0652 | -60.8002 | 61.9583 | -0.0098092 | 0.053701 | 0.054606 | -0.0016378 | 0.0036113 | -0.00052895 | 0.00021367 | -51.6769 | 62.0453 | -61.1481 | 0.068665 | 0.10071 | 0.10986 | -0.064087 | 0.33417 | 0.24719 | -0.23804 | -0.3479 | 0.086975 | 9.1232 | 60.8688 | -61.8576 | 60.5621 | -61.7111 | 9.4711
1520.7656 | 123.0515 | -60.7864 | 61.9675 | 0.42507 | 0.05306 | 0.050975 | -0.0005696 | -0.00087492 | -0.00052895 | 0.00021367 | -51.7181 | 61.9675 | -61.1343 | 0.009155 | 0.064087 | 0.064087 | -0.059509 | 0.26093 | 0.21515 | -0.28839 | -0.3479 | 0 | 9.0683 | 60.7956 | -61.9034 | 60.498 | -61.7523 | 9.4162
1521.7344 | 122.9645 | -60.8185 | 61.9949 | 0.20381 | 0.05776 | 0.050547 | 0.010539 | 0.0021159 | -0.0011698 | -0.0036315 | -51.7136 | 62.0773 | -61.1984 | -0.059509 | -0.064087 | -0.10529 | -0.013733 | 0.10529 | 0.2243 | -0.35706 | -0.37994 | 0.082398 | 9.1049 | 60.759 | -62.059 | 60.4614 | -61.7706 | 9.4849
1522.7656 | 122.9507 | -60.8002 | 62.0041 | -0.23106 | 0.052846 | 0.051615 | 0.00413 | 0.0010477 | -0.0026652 | -0.0014953 | -51.7227 | 62.0865 | -61.1801 | 0.018311 | 0.027466 | 0.036621 | 0.16022 | 0.24261 | 0.29297 | -0.20599 | -0.37994 | 0.082398 | 9.0775 | 60.8185 | -61.9766 | 60.5942 | -61.7111 | 9.4574
1523.7344 | 123.0469 | -60.8002 | 61.94 | 0.29537 | 0.055837 | 0.049479 | 0.007548 | 0.0038249 | -0.00031535 | -0.0025635 | -51.6815 | 62.0636 | -61.171 | 0.004578 | -0.004578 | -0.022888 | -0.13275 | 0.16937 | 0.1831 | -0.37079 | -0.37079 | 0.1236 | 9.1187 | 60.8047 | -61.9446 | 60.4294 | -61.7569 | 9.4894
1524.7656 | 122.9645 | -60.791 | 62.0178 | -0.18529 | 0.05306 | 0.054392 | 0.0015666 | 0.00062048 | -0.002238 | -0.00021353 | -51.7502 | 62.0682 | -61.1526 | 0.027466 | 0.036621 | 0.045776 | 0.14648 | 0.24719 | 0.29297 | -0.20142 | -0.36163 | 0.050354 | 9.0408 | 60.8185 | -61.9812 | 60.5896 | -61.7249 | 9.4025
1525.7344 | 122.9462 | -60.8093 | 61.9675 | 0.15804 | 0.055196 | 0.054392 | 0.0071208 | 0.0027567 | 0.00011185 | -0.0017089 | -51.7136 | 62.0956 | -61.171 | -0.068665 | -0.086975 | -0.11444 | 0.009155 | 0.07782 | 0.23804 | -0.36163 | -0.36163 | 0.12817 | 9.0958 | 60.7407 | -62.0544 | 60.4477 | -61.7294 | 9.4574
1526.7656 | 123.0011 | -60.791 | 61.9812 | -0.18529 | 0.053701 | 0.051829 | -0.0016378 | 0.0016887 | -0.0026652 | -0.00021353 | -51.6861 | 62.0087 | -61.1618 | 0.07782 | 0.07782 | 0.11902 | 0.068665 | 0.31586 | 0.27924 | -0.21515 | -0.37079 | 0.027466 | 9.1049 | 60.8688 | -61.9034 | 60.5759 | -61.702 | 9.4757
1527.7344 | 123.0469 | -60.7681 | 61.9446 | 0.12752 | 0.050069 | 0.05247 | -0.0018514 | 0.0016887 | -0.0018108 | -0.0012817 | -51.7548 | 61.9675 | -61.1572 | 0.013733 | 0.018311 | 0.032043 | -0.059509 | 0.23804 | 0.21515 | -0.28381 | -0.3891 | 0.022888 | 9.0134 | 60.7819 | -61.9263 | 60.4843 | -61.7294 | 9.4025
1528.75 | 123.0194 | -60.8002 | 61.9583 | 0.18855 | 0.050496 | 0.046916 | -0.0005696 | 0.0025431 | 0.00096645 | -0.00042733 | -51.7044 | 61.9537 | -61.1435 | -0.009155 | 0.013733 | 0 | -0.1236 | 0.21057 | 0.18768 | -0.29755 | -0.34332 | -0.004578 | 9.0958 | 60.791 | -61.9446 | 60.5026 | -61.7706 | 9.4391
1529.7344 | 122.9645 | -60.8139 | 62.0041 | 0.24196 | 0.057546 | 0.046916 | 0.0098978 | 0.0016887 | 0.00053925 | -0.00021353 | -51.6861 | 62.0773 | -61.1618 | -0.018311 | -0.43488 | -0.63171 | 0.34332 | 0.65918 | 0.17853 | -0.37537 | -0.3479 | 0.073243 | 9.1278 | 60.7956 | -62.439 | 60.4385 | -61.8256 | 9.4757
1530.7656 | 123.0927 | -60.7681 | 61.9446 | -0.017439 | 0.051778 | 0.051188 | -0.0022786 | -0.00066112 | 0.00118 | -0.00042733 | -51.6449 | 61.9766 | -61.1252 | 0.10986 | 0.11444 | 0.16022 | -0.07782 | 0.36621 | 0.22888 | -0.22888 | -0.35706 | 0.032044 | 9.1232 | 60.878 | -61.8301 | 60.5392 | -61.7157 | 9.4803
1531.7344 | 122.8958 | -60.8551 | 61.9354 | 0.23433 | 0.056051 | 0.053752 | 0.010325 | 0.00062048 | -0.00095615 | -0.00042733 | -51.6632 | 62.0956 | -61.1664 | -0.054932 | -0.07782 | -0.086975 | -0.013733 | 0.091553 | 0.19684 | -0.36621 | -0.31128 | 0.16022 | 9.1919 | 60.8002 | -62.0132 | 60.4889 | -61.7386 | 9.5032
1532.7656 | 122.9736 | -60.7956 | 61.9995 | -0.20054 | 0.052633 | 0.054392 | 0.0039164 | 0.0021159 | -0.0028788 | -0.00064093 | -51.6724 | 62.0682 | -61.1755 | 0.009155 | 0.009155 | 0.11444 | 0.6134 | 0.26093 | 0.32044 | -0.1236 | -0.37994 | 0.068664 | 9.1232 | 60.8047 | -61.9904 | 60.672 | -61.6791 | 9.5032
1533.7344 | 122.9691 | -60.8276 | 61.9583 | -0.093733 | 0.056905 | 0.055461 | 0.0096842 | 0.0048931 | -0.0026652 | -0.0021361 | -51.6403 | 62.0728 | -61.1618 | -0.032043 | -0.032043 | -0.082397 | -0.045776 | 0.10529 | 0.20599 | -0.3479 | -0.33417 | 0.11444 | 9.1873 | 60.7956 | -61.9904 | 60.4797 | -61.7523 | 9.5215
1534.7656 | 123.0835 | -60.7864 | 61.9766 | -0.11662 | 0.054342 | 0.050547 | -0.0029196 | 0.0010477 | -0.0028788 | -0.00064093 | -51.5488 | 61.972 | -61.1572 | 0.11902 | 0.1236 | 0.16937 | -0.032043 | 0.36621 | 0.23804 | -0.20142 | -0.37079 | -0.004578 | 9.2377 | 60.9055 | -61.853 | 60.585 | -61.7386 | 9.6085
1535.7344 | 123.0286 | -60.7819 | 61.9308 | 0.303 | 0.055837 | 0.054392 | 0.00648 | 0.0029705 | -0.0013834 | -0.0021361 | -51.5671 | 62.0361 | -61.1526 | -0.004578 | -0.009155 | -0.036621 | -0.12817 | 0.16937 | 0.19684 | -0.35706 | -0.37079 | 0.10529 | 9.2148 | 60.7773 | -61.94 | 60.4248 | -61.734 | 9.5856
1536.7656 | 122.9507 | -60.8276 | 61.972 | 0.15041 | 0.054555 | 0.056742 | 0.0069072 | 0.0025431 | -0.00031535 | -0.00042733 | -51.59 | 62.1094 | -61.1481 | -0.022888 | -0.054932 | -0.082397 | 0.018311 | 0.12817 | 0.23804 | -0.32501 | -0.32043 | 0.13733 | 9.2377 | 60.8047 | -62.027 | 60.5026 | -61.734 | 9.5581
1537.7344 | 123.0423 | -60.791 | 61.9492 | 0.10463 | 0.051351 | 0.050334 | -0.0009968 | 0.0014751 | 0.00075285 | 6.6667e-08 | -51.6083 | 61.9537 | -61.116 | 0.018311 | 0.032043 | 0.032043 | -0.07782 | 0.23346 | 0.21973 | -0.28381 | -0.32501 | 0.004577 | 9.1827 | 60.8093 | -61.9171 | 60.5072 | -61.7294 | 9.5078
1538.7656 | 123.0103 | -60.7864 | 61.9995 | -0.070844 | 0.054128 | 0.050547 | 0.0071208 | 0.00019328 | -0.0033062 | -0.0025635 | -51.5671 | 62.0956 | -61.1481 | 0.036621 | 0.022888 | 0.041199 | 0.10986 | 0.26093 | 0.27466 | -0.21057 | -0.36163 | 0.09613 | 9.2194 | 60.8231 | -61.9766 | 60.5759 | -61.7249 | 9.581
1539.7344 | 122.9462 | -60.8368 | 61.9629 | 0.26485 | 0.053701 | 0.050334 | 0.0081888 | 0.0012615 | -0.0015972 | -0.0012817 | -51.6129 | 62.1002 | -61.1938 | -0.050354 | -0.059509 | -0.10071 | -0.009155 | 0.09613 | 0.2243 | -0.3479 | -0.35706 | 0.13733 | 9.2239 | 60.7864 | -62.0224 | 60.4889 | -61.7386 | 9.581
1540.7656 | 122.9736 | -60.7819 | 62.0041 | -0.18529 | 0.051137 | 0.050975 | -0.000356 | 0.0023295 | -0.0013834 | -0.00021353 | -51.5717 | 62.0224 | -61.1801 | 0.036621 | 0.050354 | 0.073242 | 0.073242 | 0.27924 | 0.26093 | -0.19684 | -0.39825 | 0.018311 | 9.2102 | 60.8185 | -61.9537 | 60.585 | -61.7432 | 9.6085
1541.7344 | 122.9691 | -60.8322 | 61.9858 | 0.26485 | 0.055623 | 0.049906 | 0.007548 | 0.0036113 | 0.00053925 | -0.0017089 | -51.4938 | 62.0728 | -61.1893 | -0.054932 | -0.050354 | -0.09613 | -0.022888 | 0.1236 | 0.2243 | -0.33875 | -0.35706 | 0.086975 | 9.3384 | 60.7773 | -62.0361 | 60.4935 | -61.7615 | 9.6954
1542.7656 | 123.0011 | -60.8002 | 61.9675 | -0.13951 | 0.05541 | 0.051615 | 0.007548 | 0.0033977 | -0.0026652 | 0.00042727 | -51.5213 | 62.1048 | -61.171 | 0.059509 | 0.041199 | 0.064087 | 0.073242 | 0.27008 | 0.27924 | -0.26093 | -0.37079 | 0.13733 | 9.2789 | 60.8597 | -61.9263 | 60.5392 | -61.6882 | 9.6497
1543.7344 | 123.0148 | -60.8002 | 61.94 | 0.303 | 0.056051 | 0.05482 | 0.0056254 | 0.0070293 | -0.0020244 | -0.0023499 | -51.5762 | 62.0407 | -61.1755 | -0.022888 | -0.018311 | -0.050354 | -0.10071 | 0.14191 | 0.19226 | -0.33875 | -0.37537 | 0.10071 | 9.2239 | 60.7773 | -61.9583 | 60.4614 | -61.7477 | 9.5993
1544.7656 | 122.9507 | -60.8231 | 61.9995 | -0.14714 | 0.049215 | 0.04777 | 0.002421 | 0.00040688 | 0.00011185 | 0.0017091 | -51.5854 | 62.0682 | -61.1572 | 0.018311 | 0.027466 | 0.041199 | 0.15564 | 0.27008 | 0.26093 | -0.19684 | -0.33417 | 0.068664 | 9.2377 | 60.8414 | -61.972 | 60.6262 | -61.7386 | 9.5718
1545.7344 | 122.9553 | -60.8276 | 61.9583 | 0.20381 | 0.055623 | 0.056529 | 0.0073344 | 0.0033977 | 0.00011185 | 0.00021367 | -51.5717 | 62.059 | -61.1801 | -0.054932 | -0.041199 | -0.10071 | -0.004578 | 0.086975 | 0.21057 | -0.35248 | -0.35248 | 0.10071 | 9.256 | 60.7727 | -61.9995 | 60.4752 | -61.7477 | 9.6085
1546.7656 | 123.0606 | -60.7773 | 61.9537 | -0.10136 | 0.050924 | 0.053538 | -0.0022786 | 0.0010477 | -0.0015972 | -0.0012817 | -51.5213 | 61.9675 | -61.1389 | 0.086975 | 0.10986 | 0.14191 | -0.009155 | 0.35706 | 0.24261 | -0.23804 | -0.36163 | 0.013733 | 9.256 | 60.8643 | -61.8439 | 60.5392 | -61.7111 | 9.6176
1547.7344 | 123.0652 | -60.7819 | 61.9583 | -0.040327 | 0.05306 | 0.055247 | 0.0011394 | 0.0019023 | -0.0011698 | 0.00042727 | -51.5167 | 61.94 | -61.1664 | 0.050354 | 0.036621 | 0.022888 | -0.14648 | 0.23346 | 0.16479 | -0.32959 | -0.38452 | -0.018311 | 9.2651 | 60.8322 | -61.9217 | 60.4523 | -61.7935 | 9.6497
1548.7656 | 123.0698 | -60.7864 | 61.9217 | -0.11662 | 0.050283 | 0.049052 | 0.0015666 | 0.00062048 | -0.0011698 | 0.00042727 | -51.5121 | 61.9995 | -61.1206 | 0.013733 | 0.036621 | 0.21057 | -0.027466 | 0.29755 | 0.23804 | -0.23346 | -0.33417 | 0.07782 | 9.2743 | 60.8002 | -61.8851 | 60.553 | -61.6837 | 9.6085
1549.7344 | 122.9645 | -60.8231 | 61.9949 | 0.23433 | 0.056264 | 0.051188 | 0.0086162 | 0.0029705 | -0.00095615 | -0.0012817 | -51.535 | 62.059 | -61.171 | -0.48981 | -0.32501 | 0.47607 | 0.41199 | 0.041199 | 0.19226 | -0.37537 | -0.3479 | 0.064087 | 9.288 | 60.3333 | -62.3199 | 60.4477 | -61.8027 | 9.6359
1550.7656 | 122.9736 | -60.7956 | 61.9675 | -0.063215 | 0.054342 | 0.053965 | 0.0081888 | 0.0055339 | 0.00032545 | -0.0017089 | -51.4847 | 62.0728 | -61.1481 | 0.050354 | 0.027466 | 0.045776 | 0.032043 | 0.23346 | 0.25635 | -0.27924 | -0.35248 | 0.10529 | 9.3109 | 60.8459 | -61.94 | 60.5164 | -61.7111 | 9.6634
1551.7344 | 122.9782 | -60.8322 | 61.9583 | -0.055586 | 0.05306 | 0.047984 | 0.0062662 | 0.0044657 | 0.00075285 | -0.00021353 | -51.5579 | 62.0636 | -61.2076 | -0.050354 | -0.054932 | -0.07782 | -0.050354 | 0.10071 | 0.21515 | -0.35248 | -0.37537 | 0.10529 | 9.2743 | 60.7819 | -62.0132 | 60.4797 | -61.7432 | 9.6497
1552.7656 | 122.9324 | -60.8368 | 61.972 | 0.19618 | 0.056478 | 0.049906 | 0.0069072 | 0.0070293 | 0.0031026 | -0.0010681 | -51.5625 | 62.0636 | -61.1938 | 0.013733 | 0.37994 | 0.25635 | -0.16479 | 0.16479 | 0.19226 | -0.3479 | -0.35706 | 0.091553 | 9.2743 | 60.8505 | -61.5921 | 60.4889 | -61.7798 | 9.6313
1553.7344 | 123.0103 | -60.8047 | 61.9354 | 0.24196 | 0.05541 | 0.049906 | 0.0045574 | 0.0033977 | 0.00032545 | -0.0010681 | -51.5442 | 62.0453 | -61.171 | -0.032043 | -0.013733 | -0.036621 | -0.10986 | 0.14191 | 0.16937 | -0.35248 | -0.36621 | 0.10986 | 9.2606 | 60.7727 | -61.9492 | 60.4523 | -61.7661 | 9.6268
1554.7656 | 123.0743 | -60.7498 | 61.9263 | -0.017439 | 0.05071 | 0.050334 | -0.0046284 | -0.0013021 | -0.00010175 | 0.00064087 | -51.5213 | 61.972 | -61.1389 | 0.10986 | 0.13733 | 0.13275 | -0.059509 | 0.37994 | 0.23346 | -0.19684 | -0.3891 | 0.045776 | 9.2285 | 60.8597 | -61.7889 | 60.553 | -61.6928 | 9.6176
1555.7344 | 123.0286 | -60.7864 | 61.9354 | 0.074114 | 0.050496 | 0.047129 | 0.0015666 | 0.0025431 | -0.0011698 | -0.00021353 | -51.5854 | 61.9812 | -61.1572 | 0.004578 | 0.018311 | 0.068665 | -0.059509 | 0.21057 | 0.20142 | -0.27924 | -0.37079 | 0.045776 | 9.201 | 60.791 | -61.9171 | 60.5072 | -61.734 | 9.5718
1556.7656 | 123.0652 | -60.7727 | 61.9537 | 0.020708 | 0.052419 | 0.049693 | -0.0031332 | -0.0025837 | -0.0024516 | 0.00064087 | -51.5488 | 61.9583 | -61.1343 | 0.07782 | 0.091553 | 0.11444 | -0.073242 | 0.32959 | 0.22888 | -0.24261 | -0.36163 | 0.004578 | 9.2239 | 60.8505 | -61.8622 | 60.5301 | -61.7249 | 9.5856
1557.7344 | 123.056 | -60.8002 | 61.9537 | -0.14714 | 0.050283 | 0.053752 | 0.0039164 | 0.0021159 | 0.00053925 | -0.0012817 | -51.4938 | 61.9675 | -61.1298 | 0.032043 | 0.004578 | 0.022888 | -0.15564 | 0.23804 | 0.16479 | -0.31586 | -0.32959 | 0.013733 | 9.3063 | 60.8322 | -61.9492 | 60.4843 | -61.7889 | 9.6359
1558.7656 | 122.9691 | -60.7956 | 61.9858 | -0.1624 | 0.05306 | 0.048197 | 0.0084026 | -0.0019429 | -0.00010175 | -0.0021361 | -51.384 | 62.1094 | -61.1435 | 0.004578 | 0.059509 | 0 | 0.064087 | 0.24719 | 0.2655 | -0.25635 | -0.3479 | 0.1236 | 9.4116 | 60.8002 | -61.9263 | 60.5392 | -61.7203 | 9.7595
1559.7344 | 122.9233 | -60.8505 | 61.972 | 0.11989 | 0.055623 | 0.053324 | 0.0088298 | 0.0027567 | -0.0037334 | -0.0012817 | -51.5213 | 62.0819 | -61.1435 | -0.036621 | -0.059509 | -0.086975 | 0.009155 | 0.10986 | 0.21515 | -0.34332 | -0.29297 | 0.10986 | 9.3292 | 60.8139 | -62.0316 | 60.5072 | -61.7569 | 9.6222
1560.7656 | 123.0652 | -60.7819 | 61.9629 | -0.36076 | 0.05071 | 0.053752 | 0.000712 | 0.0016887 | -0.0024516 | -0.00042733 | -51.5213 | 61.972 | -61.1526 | 0.10986 | 0.10529 | 0.1236 | 0 | 0.36163 | 0.24261 | -0.23346 | -0.37079 | 0.009155 | 9.2606 | 60.8917 | -61.8576 | 60.5484 | -61.7203 | 9.6313
1561.7344 | 123.0652 | -60.8002 | 61.9446 | 0.28011 | 0.055196 | 0.053111 | 0.0069072 | 0.0023295 | -0.0013834 | -0.00085453 | -51.503 | 62.0224 | -61.1893 | 0.013733 | 0 | -0.018311 | -0.15106 | 0.16937 | 0.17853 | -0.37994 | -0.3891 | 0.07782 | 9.2972 | 60.8139 | -61.9446 | 60.4202 | -61.7661 | 9.6863
1562.7656 | 122.9599 | -60.8231 | 62.0041 | -0.65831 | 0.054555 | 0.047343 | 0.0039164 | 0.00040688 | 0.00053925 | -0.00064093 | -51.6449 | 62.0682 | -61.1847 | -0.027466 | -0.018311 | 0.054932 | 0.15564 | 0.25635 | 0.27466 | -0.25635 | -0.36163 | 0.064087 | 9.1782 | 60.7956 | -62.0224 | 60.5667 | -61.7294 | 9.5398
1563.7344 | 123.0148 | -60.8322 | 61.9446 | 0.24196 | 0.054983 | 0.051188 | 0.0060526 | 0.0036113 | 0.002889 | -0.0014953 | -51.4847 | 62.0773 | -61.1755 | -0.054932 | -0.054932 | -0.086975 | -0.022888 | -0.018311 | 0.21973 | -0.39825 | -0.34332 | 0.13275 | 9.3475 | 60.7773 | -61.9995 | 60.434 | -61.7249 | 9.6909
1564.75 | 123.0469 | -60.8047 | 61.9217 | 0.20381 | 0.053274 | 0.052256 | -0.0005696 | 0.0029705 | -0.002238 | 6.6667e-08 | -51.4709 | 61.9217 | -61.1847 | 0.013733 | 0.027466 | 0.018311 | -0.13733 | 0.20142 | 0.17853 | -0.33875 | -0.37994 | 0 | 9.3338 | 60.8185 | -61.8942 | 60.466 | -61.7432 | 9.7137
1565.7344 | 122.9828 | -60.8231 | 61.9446 | -0.11662 | 0.053274 | 0.05482 | 0.0073344 | 0.0027567 | -0.0011698 | 0.00042727 | -51.4526 | 62.0728 | -61.1801 | -0.036621 | -0.059509 | -0.10529 | -0.041199 | 0.11902 | 0.22888 | -0.3479 | -0.35706 | 0.12817 | 9.3704 | 60.7864 | -62.0041 | 60.4752 | -61.7157 | 9.7275
1566.7656 | 123.024 | -60.8139 | 61.9354 | 0.14278 | 0.051565 | 0.05012 | -0.002065 | -0.00023392 | -0.00095615 | 0.0019227 | -51.4755 | 61.94 | -61.1755 | 0.018311 | 0.041199 | 0.022888 | -0.09613 | 0.21973 | 0.19226 | -0.30212 | -0.36163 | 0.004577 | 9.3384 | 60.8322 | -61.8942 | 60.5118 | -61.7432 | 9.7
1567.7344 | 122.9828 | -60.8231 | 61.9675 | 0.28774 | 0.054342 | 0.053111 | 0.0086162 | 0.0019023 | 0.00011185 | -0.0012817 | -51.6266 | 62.0544 | -61.203 | -0.027466 | -0.47607 | -0.55389 | 0.38452 | 0.58136 | 0.19684 | -0.37994 | -0.37994 | 0.086975 | 9.1965 | 60.7956 | -62.4435 | 60.4431 | -61.7706 | 9.5764
1568.7656 | 123.0011 | -60.8139 | 61.9629 | -0.1624 | 0.052419 | 0.048625 | 0.0062662 | 0.0014751 | -0.00052895 | 6.6667e-08 | -51.4435 | 62.0819 | -61.1618 | 0.036621 | 0.036621 | 0.041199 | 0.10986 | 0.27008 | 0.2655 | -0.21515 | -0.3479 | 0.11902 | 9.3704 | 60.8505 | -61.9263 | 60.5988 | -61.6974 | 9.7183
1569.7344 | 122.9874 | -60.8231 | 61.9537 | 0.63106 | 0.056478 | 0.051402 | 0.0049846 | 0.0044657 | -0.00010175 | -0.00042733 | -51.416 | 62.0499 | -61.1755 | -0.068665 | -0.050354 | -0.064087 | -0.07782 | 0.10529 | 0.21057 | -0.34332 | -0.35248 | 0.096131 | 9.407 | 60.7544 | -62.0041 | 60.4797 | -61.7432 | 9.7595
1570.7656 | 123.0194 | -60.8276 | 61.9354 | 0.23433 | 0.055837 | 0.052256 | 0.00648 | 0.0046793 | 0.00011185 | -0.0014953 | -51.4389 | 62.0911 | -61.2076 | -0.068665 | -0.045776 | -0.086975 | -0.009155 | 0.07782 | 0.20599 | -0.3479 | -0.37994 | 0.15564 | 9.3887 | 60.759 | -61.9812 | 60.4797 | -61.7294 | 9.7687
1571.7344 | 122.9416 | -60.8459 | 61.9492 | 0.074114 | 0.054769 | 0.055888 | 0.0069072 | 0.0048931 | -0.00095615 | -0.0019225 | -51.3748 | 62.1002 | -61.1893 | -0.041199 | -0.050354 | -0.086975 | 0.022888 | 0.10986 | 0.22888 | -0.32959 | -0.34332 | 0.15106 | 9.4711 | 60.8047 | -61.9995 | 60.5164 | -61.7203 | 9.8145
1572.7656 | 123.0377 | -60.8231 | 61.9537 | -1.1771 | 0.05071 | 0.047557 | -0.0067648 | 0.0038249 | -0.0018108 | 0.0010681 | -51.4938 | 61.9812 | -61.1664 | 0.009155 | 0.050354 | 0.07782 | -0.059509 | 0.27008 | 0.21973 | -0.27924 | -0.34332 | 0.027466 | 9.3292 | 60.8322 | -61.9034 | 60.5438 | -61.734 | 9.6725
1573.7344 | 122.9507 | -60.8093 | 61.9766 | 0.097002 | 0.054342 | 0.052043 | 0.007548 | 0.0029705 | -0.00031535 | -0.00085453 | -51.4206 | 62.0865 | -61.1618 | -0.013733 | -0.018311 | -0.027466 | 0.018311 | 0.15106 | 0.21515 | -0.31128 | -0.35248 | 0.10986 | 9.3887 | 60.7956 | -61.9949 | 60.498 | -61.7615 | 9.7412
1574.7656 | 123.0331 | -60.8185 | 61.9263 | 0.10463 | 0.053274 | 0.04777 | -0.0022786 | 0.0029705 | -0.00031535 | -0.0021361 | -51.3886 | 61.9492 | -61.1938 | 0.004578 | 0.045776 | 0.064087 | -0.073242 | 0.22888 | 0.20599 | -0.28839 | -0.37537 | 0.022888 | 9.4299 | 60.8231 | -61.8805 | 60.5301 | -61.7203 | 9.8053
1575.7344 | 123.0652 | -60.8002 | 61.9354 | 0.31825 | 0.055623 | 0.049906 | 0.0054118 | 0.0027567 | 0.0013936 | -0.0014953 | -51.5991 | 62.0178 | -61.1481 | 0.032043 | 0.022888 | -0.032043 | -0.1831 | 0.21515 | 0.17853 | -0.37537 | -0.3479 | 0.082397 | 9.2011 | 60.8322 | -61.9125 | 60.4248 | -61.7569 | 9.549
1576.7656 | 123.056 | -60.8093 | 61.9308 | 0.051226 | 0.051351 | 0.048625 | -0.0022786 | 0.0016887 | -0.0015972 | -0.0038451 | -51.4206 | 61.9766 | -61.1893 | -0.059509 | 0.004578 | -0.013733 | -0.091553 | 0.27008 | 0.21515 | -0.27924 | -0.37994 | 0.045777 | 9.3887 | 60.7498 | -61.9263 | 60.5301 | -61.7157 | 9.7687
1577.7344 | 123.0148 | -60.8139 | 61.9354 | 0.25722 | 0.054983 | 0.049693 | 0.0069072 | -2.0324e-05 | -0.00052895 | -0.00042733 | -51.384 | 62.027 | -61.1664 | -0.032043 | -0.045776 | -0.054932 | -0.09613 | 0.14191 | 0.19226 | -0.35248 | -0.35248 | 0.091553 | 9.4299 | 60.7819 | -61.9812 | 60.4614 | -61.7432 | 9.7824
1578.7656 | 123.024 | -60.8093 | 61.9308 | 0.21907 | 0.052419 | 0.053324 | 0.0011394 | 0.0021159 | -0.00031535 | 0.0014953 | -51.3474 | 61.94 | -61.1938 | 0.013733 | 0.013733 | 0.013733 | -0.10529 | 0.19684 | 0.1831 | -0.3067 | -0.38452 | 0.009155 | 9.462 | 60.8231 | -61.9171 | 60.5026 | -61.7477 | 9.8465
1579.7344 | 122.9919 | -60.8047 | 61.9583 | -0.55913 | 0.055837 | 0.059519 | 0.0088298 | 0.0025431 | -0.00052895 | 0.00085447 | -51.265 | 62.0819 | -61.1572 | 0.050354 | 0 | 0.018311 | 0.018311 | 0.2243 | 0.24261 | -0.28839 | -0.35248 | 0.1236 | 9.5398 | 60.8551 | -61.9583 | 60.5164 | -61.7157 | 9.8923
1580.7812 | 123.0286 | -60.8139 | 61.9217 | 0.21907 | 0.050069 | 0.055247 | 0.001353 | 0.0029705 | -0.00074255 | -0.00064093 | -51.3977 | 61.94 | -61.2122 | -0.009155 | 0.022888 | -0.022888 | -0.15106 | 0.19684 | 0.18768 | -0.34332 | -0.39825 | 0.01831 | 9.4162 | 60.8047 | -61.8988 | 60.4706 | -61.734 | 9.8145
1581.7344 | 122.9828 | -60.8505 | 61.9583 | 0.0054493 | 0.056691 | 0.049906 | 0.010112 | 0.0036113 | -0.0024516 | -0.0023499 | -51.2924 | 62.0911 | -61.1801 | 0.036621 | 0.013733 | 0.018311 | 0.018311 | 0.10071 | 0.23346 | -0.32501 | -0.32959 | 0.13275 | 9.5581 | 60.8871 | -61.9446 | 60.5255 | -61.7249 | 9.8877
1582.7656 | 122.9874 | -60.8185 | 61.9995 | -0.2158 | 0.054128 | 0.052897 | -0.0001424 | 0.00019328 | -0.0020244 | -0.0017089 | -51.3565 | 62.0361 | -61.1664 | 0.013733 | 0.041199 | 0.054932 | 0.1236 | 0.25177 | 0.27008 | -0.18768 | -0.3479 | 0.036621 | 9.462 | 60.8322 | -61.9583 | 60.6308 | -61.7294 | 9.8099
1583.7344 | 122.9828 | -60.8231 | 61.9675 | -0.055586 | 0.055837 | 0.055247 | 0.0069072 | 0.0029705 | -0.0011698 | -0.0019225 | -51.2604 | 62.0911 | -61.1618 | 0.041199 | 0.018311 | 0.027466 | 0.027466 | 0.23346 | 0.25635 | -0.27466 | -0.33874 | 0.1236 | 9.5627 | 60.8643 | -61.9492 | 60.5484 | -61.7111 | 9.9014
1584.7656 | 123.1018 | -60.7864 | 61.9446 | -0.20054 | 0.049215 | 0.047557 | -0.0029196 | 0.0029705 | -0.0011698 | -0.0010681 | -51.3016 | 61.9446 | -61.1481 | 0.1236 | 0.12817 | 0.17853 | -0.036621 | 0.37994 | 0.23346 | -0.19684 | -0.36163 | 0 | 9.4849 | 60.91 | -61.8164 | 60.5896 | -61.7111 | 9.8465
1585.7344 | 122.9599 | -60.8414 | 62.0041 | 0.074114 | 0.05541 | 0.053111 | 0.010325 | 0.0027567 | 0.00011185 | -0.0032043 | -51.2604 | 62.0499 | -61.1526 | -0.013733 | -0.036621 | -0.041199 | 0.018311 | 0.16479 | 0.25177 | -0.31586 | -0.31128 | 0.045777 | 9.581 | 60.8276 | -62.0407 | 60.5255 | -61.7523 | 9.8923
1586.7656 | 123.0469 | -60.7956 | 61.94 | 0.097002 | 0.052205 | 0.054606 | -0.0014242 | 0.00040688 | 0.00032545 | 6.6667e-08 | -51.384 | 61.9629 | -61.1847 | 0.022888 | 0.032043 | 0.041199 | -0.050354 | 0.24719 | 0.19226 | -0.27924 | -0.3891 | 0.022889 | 9.4116 | 60.8185 | -61.908 | 60.5164 | -61.7477 | 9.8007
1587.75 | 122.9919 | -60.8368 | 61.9583 | 0.2267 | 0.051565 | 0.053965 | 0.009257 | 0.0040385 | -0.00052895 | 0.00064087 | -51.3519 | 62.0361 | -61.1801 | -0.022888 | -0.036621 | -0.050354 | -0.10529 | 0.14191 | 0.1831 | -0.34332 | -0.34332 | 0.07782 | 9.4849 | 60.8139 | -61.9949 | 60.4935 | -61.7752 | 9.8282
1588.7656 | 123.0423 | -60.7819 | 61.9125 | -0.2158 | 0.05306 | 0.050334 | -0.0018514 | 0.0012615 | -0.00031535 | 0.00042727 | -51.4023 | 61.9492 | -61.1572 | 0.013733 | 0.054932 | 0.059509 | -0.068665 | 0.25177 | 0.19684 | -0.27466 | -0.37537 | 0.036621 | 9.3796 | 60.7956 | -61.8576 | 60.5072 | -61.7157 | 9.7549
1589.7344 | 122.9874 | -60.8276 | 61.9537 | 0.043596 | 0.054555 | 0.053752 | 0.007548 | 0.00062048 | -0.00010175 | -0.0023499 | -51.2878 | 62.0911 | -61.1664 | 0.045776 | 0.027466 | -0.009155 | 0 | 0.23804 | 0.21973 | -0.28381 | -0.33874 | 0.13733 | 9.5398 | 60.8734 | -61.9263 | 60.5438 | -61.734 | 9.8785
1590.7656 | 122.9736 | -60.8093 | 61.9263 | -0.040327 | 0.05306 | 0.05247 | 0.0077616 | 0.0025431 | -0.00010175 | -0.0010681 | -51.2924 | 62.0636 | -61.171 | 0.059509 | 0.022888 | 0.022888 | 0.018311 | 0.23346 | 0.24719 | -0.27924 | -0.36163 | 0.13733 | 9.5169 | 60.8688 | -61.9034 | 60.5301 | -61.6791 | 9.8785
1591.7344 | 122.9782 | -60.8414 | 61.9492 | 0.0054493 | 0.057546 | 0.051402 | 0.0069072 | 0.0046793 | -0.00095615 | -0.0027771 | -51.3107 | 62.0682 | -61.1755 | 0.050354 | 0.018311 | 0.018311 | 0.027466 | 0.24261 | 0.23346 | -0.29755 | -0.33417 | 0.11902 | 9.5306 | 60.8917 | -61.9308 | 60.5438 | -61.7157 | 9.8648
1592.7656 | 123.0835 | -60.791 | 61.94 | -0.017439 | 0.050924 | 0.050547 | -0.003774 | 0.0029705 | -0.00052895 | 6.6667e-08 | -51.3382 | 61.9492 | -61.1801 | 0.10986 | 0.13275 | 0.15564 | -0.082397 | 0.37079 | 0.21515 | -0.20599 | -0.3891 | 0.009156 | 9.4528 | 60.9009 | -61.8073 | 60.585 | -61.7249 | 9.8419
1593.7344 | 122.9965 | -60.8231 | 61.972 | -0.093733 | 0.054342 | 0.054392 | 0.0077616 | 0.0036113 | -0.0020244 | -0.0010681 | -51.3062 | 62.0819 | -61.1572 | 0.041199 | 0.013733 | 0.018311 | 0.027466 | 0.20142 | 0.24261 | -0.27466 | -0.33417 | 0.10986 | 9.5169 | 60.8643 | -61.9583 | 60.5484 | -61.7294 | 9.8511
1594.7656 | 123.0698 | -60.7864 | 61.9217 | -0.14714 | 0.049856 | 0.046916 | -0.002065 | 0.0016887 | -0.0011698 | 0.00064087 | -51.3153 | 61.9492 | -61.1389 | 0.11902 | 0.13275 | 0.16479 | -0.054932 | 0.35248 | 0.23346 | -0.21057 | -0.35248 | 0.027466 | 9.4711 | 60.9055 | -61.7889 | 60.5759 | -61.6882 | 9.8236
1595.7344 | 123.0057 | -60.8002 | 61.9812 | -0.070844 | 0.053914 | 0.049906 | 0.0094706 | 0.0038249 | -0.0013834 | -0.0019225 | -51.3016 | 62.0682 | -61.1435 | 0.059509 | 0.041199 | 0.041199 | 0.036621 | 0.24719 | 0.24719 | -0.27924 | -0.34332 | 0.086975 | 9.4986 | 60.8597 | -61.94 | 60.5209 | -61.734 | 9.8419
1596.75 | 123.0698 | -60.8002 | 61.8988 | 0.24196 | 0.053487 | 0.052043 | 0.003062 | 0.0038249 | -0.00074255 | -0.0017089 | -51.4618 | 61.9583 | -61.1755 | 0.018311 | 0.027466 | 0.10529 | -0.16022 | 0.20142 | 0.18768 | -0.31128 | -0.37537 | 0.059509 | 9.3384 | 60.8185 | -61.8713 | 60.4889 | -61.7111 | 9.7137
1597.7344 | 123.0011 | -60.8688 | 61.908 | 0.23433 | 0.05541 | 0.057383 | 0.0069072 | 0.0012615 | -0.00031535 | -0.0021361 | -51.3794 | 62.0911 | -61.1847 | -0.059509 | -0.054932 | -0.091553 | -0.013733 | 0.09613 | 0.21057 | -0.36163 | -0.31586 | 0.18311 | 9.4894 | 60.8093 | -61.9629 | 60.5072 | -61.6974 | 9.8053
1598.7656 | 123.0515 | -60.7773 | 61.9308 | -0.017439 | 0.047078 | 0.046916 | -0.0031332 | 0.0021159 | -0.0013834 | 0.0023499 | -51.3382 | 61.9858 | -61.1526 | 0.036621 | 0.032043 | 0.036621 | -0.050354 | 0.27924 | 0.21515 | -0.27466 | -0.37537 | 0.054932 | 9.4391 | 60.8139 | -61.8988 | 60.5026 | -61.7157 | 9.8145
1599.7344 | 122.9919 | -60.8276 | 61.9629 | -0.086103 | 0.054769 | 0.053965 | 0.0079752 | 0.0012615 | -0.00010175 | -0.00085453 | -51.3107 | 62.0544 | -61.1664 | 0.054932 | 0.036621 | 0.041199 | 0.036621 | 0.24261 | 0.24261 | -0.24719 | -0.33874 | 0.091552 | 9.5169 | 60.8826 | -61.9263 | 60.5804 | -61.7203 | 9.8557
1600.7656 | 123.0743 | -60.7819 | 61.9537 | 0.066485 | 0.049428 | 0.047557 | -0.0024922 | 0.0012615 | -0.00095615 | 0.00085447 | -51.3931 | 61.9583 | -61.1893 | 0.068665 | 0.086975 | 0.086975 | -0.068665 | 0.29297 | 0.21973 | -0.24719 | -0.40741 | 0.004578 | 9.3887 | 60.8505 | -61.8668 | 60.5347 | -61.734 | 9.7961
1601.7344 | 122.9782 | -60.7956 | 61.9675 | -0.12425 | 0.056051 | 0.053965 | 0.0079752 | 0.00083408 | -0.00052895 | -0.0019225 | -51.3336 | 62.0636 | -61.1389 | 0.050354 | 0.050354 | 0.050354 | 0.10071 | 0.27008 | 0.2655 | -0.20599 | -0.34332 | 0.096131 | 9.462 | 60.8459 | -61.9171 | 60.5896 | -61.702 | 9.8053
1602.7656 | 122.9645 | -60.8276 | 61.9446 | 0.066485 | 0.055623 | 0.047984 | 0.0077616 | 0.0040385 | 0.00032545 | -0.0014953 | -51.3199 | 62.0865 | -61.1755 | 0.013733 | -0.004578 | -0.032043 | 0.009155 | 0.16022 | 0.22888 | -0.31128 | -0.3479 | 0.14191 | 9.5078 | 60.8414 | -61.9492 | 60.5164 | -61.7157 | 9.8557
1603.7344 | 122.9828 | -60.8368 | 62.0087 | -0.24632 | 0.053274 | 0.049693 | 0.003062 | 0.0029705 | -0.0011698 | 0.00021367 | -51.3794 | 62.059 | -61.171 | 0.027466 | 0.013733 | 0.022888 | 0.10986 | 0.23346 | 0.27466 | -0.20599 | -0.33417 | 0.050354 | 9.4574 | 60.8643 | -61.9949 | 60.6308 | -61.734 | 9.7916
1604.7656 | 123.024 | -60.8231 | 61.9308 | 0.21144 | 0.05306 | 0.049052 | -0.0014242 | 0.0019023 | -0.00074255 | 0.0012817 | -51.384 | 61.9583 | -61.2076 | 0 | 0.018311 | 0 | -0.11444 | 0.19684 | 0.17395 | -0.30212 | -0.38452 | 0.027466 | 9.4391 | 60.8231 | -61.9125 | 60.5209 | -61.7569 | 9.8236
1605.7344 | 122.9782 | -60.8047 | 61.9995 | -0.17766 | 0.053274 | 0.051615 | 0.0073344 | 0.0033977 | -0.0013834 | -0.00042733 | -51.3931 | 62.0773 | -61.1847 | 0.050354 | 0.045776 | 0.054932 | 0.11444 | 0.25635 | 0.27466 | -0.20142 | -0.37994 | 0.07782 | 9.4116 | 60.8551 | -61.9537 | 60.6033 | -61.7249 | 9.7916
1606.7656 | 123.0286 | -60.7864 | 61.9583 | 0.035967 | 0.051137 | 0.049052 | -0.0012106 | 0.00019328 | 0.0020344 | 0.00042727 | -51.4755 | 61.9446 | -61.2076 | -0.036621 | -0.022888 | -0.004578 | -0.10071 | 0.24719 | 0.2243 | -0.27924 | -0.42114 | -0.013733 | 9.3109 | 60.7498 | -61.9812 | 60.5072 | -61.734 | 9.7321
1607.7344 | 122.9553 | -60.8139 | 61.9629 | 0.028338 | 0.054769 | 0.049906 | 0.0081888 | 0.0036113 | 0.00032545 | -0.0010681 | -51.3748 | 62.059 | -61.1481 | 0 | -0.027466 | -0.027466 | 0.018311 | 0.16022 | 0.23346 | -0.31586 | -0.33417 | 0.09613 | 9.4391 | 60.8139 | -61.9904 | 60.498 | -61.7294 | 9.7733
1608.7656 | 123.0331 | -60.7681 | 61.9354 | -0.13951 | 0.051137 | 0.044779 | -0.0022786 | 0.0012615 | -0.0013834 | 0.0017091 | -51.3519 | 61.9583 | -61.1847 | 0.1236 | 0.11444 | 0.086975 | 0.58136 | 0.89722 | 0.27924 | -0.16937 | -0.41656 | 0.022888 | 9.4162 | 60.8917 | -61.821 | 60.5988 | -61.6562 | 9.8328
1609.7344 | 122.9965 | -60.8047 | 61.9766 | -0.15477 | 0.052846 | 0.052043 | 0.0060526 | 0.0044657 | -0.0024516 | -0.0012817 | -51.3474 | 62.0728 | -61.1755 | 0.054932 | 0.022888 | 0.054932 | 0.091553 | 0.2655 | 0.27008 | -0.24261 | -0.37079 | 0.09613 | 9.4574 | 60.8597 | -61.9537 | 60.5621 | -61.7065 | 9.8282
1610.7656 | 123.0652 | -60.8093 | 61.9171 | 0.18093 | 0.053914 | 0.048838 | 0.0043436 | 0.0046793 | -0.0015972 | -0.00021353 | -51.3565 | 61.9675 | -61.1755 | 0.045776 | 0.032043 | 0.013733 | -0.19684 | 0.20599 | 0.15564 | -0.37994 | -0.36621 | 0.050354 | 9.4528 | 60.8551 | -61.8851 | 60.4294 | -61.7615 | 9.819
1611.7344 | 122.937 | -60.8368 | 61.972 | -0.17766 | 0.051778 | 0.049052 | 0.0051982 | 0.0023295 | -0.0013834 | -0.0014953 | -51.5305 | 62.0499 | -61.1893 | 0.27008 | 0.28381 | -0.21515 | -0.17853 | 0.24719 | 0.28381 | -0.15106 | -0.35248 | 0.07782 | 9.3063 | 61.1069 | -61.6882 | 60.6857 | -61.6882 | 9.6588
1612.7656 | 123.0331 | -60.8139 | 61.9629 | 0.066485 | 0.051351 | 0.046702 | -0.0018514 | -0.0010885 | -0.0024516 | -0.0010681 | -51.5533 | 61.9263 | -61.1755 | -0.004578 | 0.045776 | 0.013733 | -0.054932 | 0.26093 | 0.21057 | -0.27008 | -0.36163 | -0.036621 | 9.2606 | 60.8093 | -61.9171 | 60.5438 | -61.7523 | 9.6222
1613.7344 | 122.9874 | -60.8276 | 61.9995 | -0.12425 | 0.052846 | 0.048625 | 0.0069072 | -0.00066112 | -0.0024516 | -0.00042733 | -51.5121 | 62.0544 | -61.1847 | 0.022888 | 0.018311 | 0.027466 | 0.10529 | 0.23346 | 0.27466 | -0.21057 | -0.35705 | 0.054931 | 9.3155 | 60.8505 | -61.9812 | 60.6171 | -61.7249 | 9.6725
1614.7344 | 122.9645 | -60.8597 | 61.9492 | 0.12752 | 0.056478 | 0.048838 | 0.0090434 | 0.0016887 | -0.00031535 | -0.00085453 | -51.4664 | 62.0499 | -61.1893 | -0.009155 | -0.036621 | -0.036621 | 0.018311 | 0.17853 | 0.23804 | -0.32501 | -0.32959 | 0.10071 | 9.3933 | 60.8505 | -61.9858 | 60.5347 | -61.7111 | 9.7229
1615.7656 | 123.0743 | -60.7773 | 61.9308 | 0.028338 | 0.050283 | 0.043925 | -0.0035604 | 0.0021159 | 0.0016072 | 0.00064087 | -51.5121 | 61.9446 | -61.1755 | 0.07782 | 0.09613 | 0.10529 | -0.064087 | 0.29755 | 0.23804 | -0.2655 | -0.39825 | 0.013733 | 9.2651 | 60.8551 | -61.8347 | 60.5118 | -61.6928 | 9.6634
1616.7344 | 122.9919 | -60.8139 | 61.9492 | -0.040327 | 0.053914 | 0.049266 | 0.0079752 | 0.0010477 | -0.00074255 | -0.0025635 | -51.4847 | 62.0636 | -61.1618 | 0.050354 | 0.018311 | 0.082397 | -0.2655 | 0.07782 | 0.2243 | -0.29755 | -0.3479 | 0.11444 | 9.3292 | 60.8643 | -61.9308 | 60.5164 | -61.7249 | 9.6771
1617.7656 | 123.0148 | -60.8002 | 61.94 | 0.028338 | 0.049001 | 0.04777 | -0.0031332 | -0.00023392 | 0.00011185 | -0.00085453 | -51.535 | 61.9354 | -61.171 | 0.018311 | 0.050354 | 0.013733 | 0.17395 | 0.41657 | 0.21515 | -0.25635 | -0.37079 | -0.004577 | 9.2651 | 60.8185 | -61.8896 | 60.5438 | -61.7249 | 9.6359
1618.7344 | 122.9187 | -60.8368 | 61.9675 | 0.074114 | 0.05306 | 0.050761 | 0.0079752 | 0.0023295 | 0.00032545 | -0.0027771 | -51.5625 | 62.0819 | -61.1572 | -0.054932 | -0.07782 | -0.10071 | 0 | 0.10071 | 0.21973 | -0.36621 | -0.32043 | 0.11444 | 9.2743 | 60.7819 | -62.0453 | 60.4706 | -61.7477 | 9.5947
1619.7656 | 122.9507 | -60.8551 | 61.9583 | -0.36076 | 0.053701 | 0.053965 | 0.0062662 | 0.0044657 | 0.0024618 | -0.0019225 | -51.5533 | 62.0636 | -61.2213 | -0.027466 | -0.064087 | -0.07782 | -0.036621 | 0.10529 | 0.24719 | -0.35248 | -0.36621 | 0.10529 | 9.3018 | 60.8276 | -62.0224 | 60.5026 | -61.7111 | 9.668
1620.7344 | 122.9919 | -60.8276 | 61.9537 | -0.11662 | 0.053701 | 0.050547 | 0.004771 | 0.0016887 | -0.00095615 | -0.0023499 | -51.4893 | 62.0682 | -61.1618 | 0.082397 | 0.054932 | 0.036621 | 0.059509 | 0.2655 | 0.27924 | -0.26093 | -0.33417 | 0.11444 | 9.3384 | 60.91 | -61.8988 | 60.5667 | -61.6745 | 9.6725
1621.7656 | 123.0515 | -60.7864 | 61.8805 | 0.28011 | 0.05306 | 0.051829 | 0.0051982 | 0.0051067 | -0.00031535 | -0.00085453 | -51.503 | 62.027 | -61.1938 | 0.009155 | -0.009155 | 0 | -0.12817 | 0.20599 | 0.16479 | -0.37079 | -0.40741 | 0.14648 | 9.2834 | 60.7956 | -61.8896 | 60.4156 | -61.7157 | 9.6909
1622.7344 | 122.9782 | -60.8505 | 61.9308 | 0.19618 | 0.056051 | 0.06016 | 0.0051982 | 0.0044657 | -0.00052895 | -0.00085453 | -51.6998 | 62.0132 | -61.2305 | 0.054932 | -0.073242 | -0.15564 | 0.064087 | 0.12817 | 0.23346 | -0.32501 | -0.37994 | 0.082398 | 9.1507 | 60.9055 | -62.0041 | 60.5255 | -61.6974 | 9.5306
1623.7656 | 123.0286 | -60.8047 | 61.908 | 0.18093 | 0.05306 | 0.050334 | -0.0007832 | 0.0023295 | 0.00118 | -0.00021353 | -51.4618 | 61.9537 | -61.1481 | 0.027466 | 0.041199 | 0.036621 | -0.15106 | 0.23346 | 0.17853 | -0.35248 | -0.34332 | 0.045776 | 9.343 | 60.8322 | -61.8668 | 60.4523 | -61.7294 | 9.6863
1624.7344 | 122.9919 | -60.8185 | 61.9492 | -0.093733 | 0.054983 | 0.054392 | 0.0071208 | -0.00023392 | 0.00011185 | -0.0017089 | -51.4664 | 62.0773 | -61.1618 | 0.045776 | 0.050354 | 0.041199 | 0.027466 | 0.23804 | 0.26093 | -0.27466 | -0.34332 | 0.12817 | 9.3521 | 60.8643 | -61.8988 | 60.5438 | -61.6882 | 9.6954
1625.75 | 122.9462 | -60.8047 | 61.9263 | -0.070844 | 0.055196 | 0.055461 | 0.00648 | 0.0044657 | -0.0011698 | -0.0021361 | -51.5213 | 62.0407 | -61.1847 | -0.036621 | -0.041199 | -0.068665 | -0.041199 | 0.091553 | 0.21057 | -0.35706 | -0.37994 | 0.11444 | 9.2834 | 60.7681 | -61.9675 | 60.4477 | -61.7157 | 9.6634
1626.7344 | 122.9874 | -60.8414 | 61.9263 | 0.10463 | 0.053914 | 0.052043 | 0.0081888 | 0.0040385 | 0.00011185 | -0.00021353 | -51.4618 | 62.1002 | -61.171 | 0.004578 | -0.022888 | -0.022888 | 0.009155 | 0.16479 | 0.23346 | -0.32044 | -0.32959 | 0.17395 | 9.3796 | 60.8459 | -61.9492 | 60.5209 | -61.6928 | 9.7092
1627.7656 | 123.0881 | -60.791 | 61.9308 | -1.4518 | 0.051351 | 0.049052 | -0.0033468 | 0.0036113 | -0.00052895 | -0.0010681 | -51.297 | 61.9766 | -61.171 | 0.13275 | 0.10529 | 0.082397 | -0.004578 | 0.40283 | 0.21515 | -0.24261 | -0.37994 | 0.045777 | 9.494 | 60.9238 | -61.8256 | 60.5484 | -61.7157 | 9.874
1628.7344 | 122.9782 | -60.8322 | 61.9583 | -0.047956 | 0.056051 | 0.051402 | 0.0071208 | 0.0012615 | -0.0026652 | -0.00064093 | -51.3565 | 62.0499 | -61.1893 | 0.013733 | -0.15564 | -0.14648 | 0.16937 | 0.30212 | 0.21515 | -0.30212 | -0.35706 | 0.091553 | 9.4757 | 60.8459 | -62.114 | 60.5301 | -61.7432 | 9.8328
1629.7656 | 123.0286 | -60.8185 | 61.94 | 0.097002 | 0.052205 | 0.049266 | -0.0018514 | 0.0021159 | 0.00053925 | 6.6667e-08 | -51.5076 | 61.9354 | -61.1984 | 0.018311 | 0.059509 | 0.30212 | 0.009155 | 0.13275 | 0.21515 | -0.27466 | -0.37994 | -0.004577 | 9.3109 | 60.8368 | -61.8805 | 60.5438 | -61.7249 | 9.6909
1630.7344 | 122.9553 | -60.8459 | 61.9308 | 0.2267 | 0.056478 | 0.053324 | 0.0066936 | 0.0057475 | 0.0013936 | -0.0010681 | -51.4984 | 62.0453 | -61.1984 | 0.31128 | 0.28381 | -0.15564 | -0.036621 | 0.27008 | 0.21057 | -0.34332 | -0.35248 | 0.11444 | 9.3475 | 61.1572 | -61.647 | 60.5026 | -61.7203 | 9.7
1631.7656 | 123.0789 | -60.7864 | 61.9308 | -0.025068 | 0.050069 | 0.050334 | -0.0016378 | -0.0015157 | 0.00011185 | 0.00064087 | -51.5076 | 61.9446 | -61.1984 | 0.10986 | 0.11902 | 0.14191 | -0.07782 | 0.37537 | 0.22888 | -0.20142 | -0.41199 | 0.013733 | 9.2789 | 60.8963 | -61.8118 | 60.585 | -61.702 | 9.6909
1632.7344 | 123.0743 | -60.7956 | 61.8988 | 0.23433 | 0.053487 | 0.052043 | 0.0073344 | 0.0012615 | -0.00052895 | -0.00042733 | -51.4252 | 61.9812 | -61.1664 | 0.036621 | 0.054932 | 0 | -0.19684 | 0.19684 | 0.16479 | -0.37537 | -0.37079 | 0.082397 | 9.3704 | 60.8322 | -61.8439 | 60.4202 | -61.734 | 9.7412
1633.7656 | 123.0377 | -60.8185 | 61.9171 | 0.21907 | 0.051565 | 0.050334 | 0.0011394 | -0.00066112 | -0.00010175 | 6.6667e-08 | -51.3474 | 61.9354 | -61.1893 | 0.009155 | 0.009155 | -0.004578 | -0.10529 | 0.22888 | 0.18768 | -0.31586 | -0.37079 | 0.018311 | 9.4711 | 60.8276 | -61.908 | 60.5026 | -61.7294 | 9.8419
1634.7344 | 122.9874 | -60.8322 | 61.9263 | 0.24196 | 0.054769 | 0.055033 | 0.007548 | 0.00040688 | 0.00032545 | -0.0014953 | -51.3519 | 62.027 | -61.1893 | -0.045776 | -0.059509 | -0.086975 | -0.07782 | 0.11902 | 0.19684 | -0.35706 | -0.35706 | 0.10071 | 9.4803 | 60.7864 | -61.9858 | 60.4752 | -61.7294 | 9.8373
1635.7656 | 122.9233 | -60.8185 | 61.972 | -0.22343 | 0.052633 | 0.047984 | 0.0034892 | 0.00019328 | -0.0026652 | -0.0010681 | -51.3977 | 62.027 | -61.1938 | 0 | 0.022888 | 0.022888 | 0.14191 | 0.26093 | 0.29755 | -0.1831 | -0.37537 | 0.054932 | 9.4208 | 60.8185 | -61.9492 | 60.6354 | -61.6745 | 9.7961
1636.75 | 123.0377 | -60.8047 | 61.9446 | 0.11226 | 0.051137 | 0.045848 | -0.0016378 | -0.0013021 | 0.00096645 | -0.00042733 | -51.3977 | 61.9354 | -61.1893 | 0.036621 | 0.19226 | 0.21515 | -0.24261 | 0.14191 | 0.2243 | -0.26093 | -0.38452 | -0.009155 | 9.407 | 60.8414 | -61.7523 | 60.5438 | -61.7203 | 9.7916
1637.7656 | 122.9691 | -60.8368 | 61.9766 | -0.20817 | 0.053487 | 0.049479 | 0.0062662 | -0.0019429 | -0.0028788 | -0.0019225 | -51.3199 | 62.0819 | -61.1938 | 0.022888 | 0.032043 | 0.036621 | 0.13275 | 0.24719 | 0.29755 | -0.19226 | -0.35706 | 0.10529 | 9.5169 | 60.8597 | -61.9446 | 60.6445 | -61.6791 | 9.874
1638.7344 | 122.9736 | -60.8414 | 61.9263 | -2.1308 | 0.05306 | 0.049479 | 0.0066936 | -0.00066112 | 0.00011185 | -0.0010681 | -51.3245 | 62.0682 | -61.1801 | -0.036621 | -0.07782 | -0.12817 | -0.022888 | 0.11444 | 0.2243 | -0.32501 | -0.33875 | 0.14191 | 9.5169 | 60.8047 | -62.0041 | 60.5164 | -61.702 | 9.8557
1639.7656 | 123.0103 | -60.7956 | 61.9217 | 0.097002 | 0.050496 | 0.049052 | -0.0014242 | -0.00044752 | 0.00053925 | -0.00021353 | -51.2878 | 61.9354 | -61.1984 | 0.027466 | 0.17395 | 0.19684 | -0.22888 | 0.16022 | 0.23804 | -0.27924 | -0.40283 | 0.013733 | 9.5078 | 60.8231 | -61.7477 | 60.5164 | -61.6837 | 9.9106
1640.7344 | 122.9187 | -60.8459 | 61.9354 | 0.089373 | 0.056264 | 0.05247 | 0.0086162 | 0.00083408 | -0.00052895 | -0.0027771 | -51.3199 | 62.0636 | -61.1847 | -0.050354 | -0.09613 | -0.10529 | 0.013733 | 0.091553 | 0.23346 | -0.37079 | -0.33874 | 0.12817 | 9.5261 | 60.7956 | -62.0316 | 60.4752 | -61.702 | 9.8648
1641.7656 | 123.0423 | -60.8002 | 61.972 | -0.1624 | 0.051565 | 0.052683 | 0.0017802 | -0.00023392 | -0.0033062 | -0.0019225 | -51.2924 | 61.9858 | -61.1755 | 0.091553 | 0.10071 | 0.13275 | 0.036621 | 0.33875 | 0.27008 | -0.2243 | -0.37537 | 0.013733 | 9.5078 | 60.8917 | -61.8713 | 60.5759 | -61.702 | 9.8831
1642.7344 | 123.0652 | -60.8185 | 61.9217 | 0.028338 | 0.051137 | 0.049052 | -0.0016378 | -0.00066112 | -0.00010175 | -0.0029907 | -51.2878 | 62.0178 | -61.1481 | 0.064087 | 0.091553 | 0.10529 | -0.073242 | 0.29755 | 0.21515 | -0.2655 | -0.32959 | 0.09613 | 9.5306 | 60.8826 | -61.8301 | 60.553 | -61.7065 | 9.8602
1643.7656 | 123.0469 | -60.8047 | 61.9217 | 0.20381 | 0.051992 | 0.048838 | 0.0022074 | 0.00083408 | -0.00031535 | 0.00042727 | -51.2192 | 61.9217 | -61.1801 | 0.036621 | 0.027466 | 0.027466 | -0.15106 | 0.21057 | 0.17853 | -0.36621 | -0.37537 | 0 | 9.5856 | 60.8414 | -61.8942 | 60.4385 | -61.7432 | 9.9609
1644.7344 | 122.9141 | -60.8597 | 61.9446 | 0.18855 | 0.056691 | 0.047557 | 0.010966 | 0.0010477 | 0.00011185 | -0.00042733 | -51.3062 | 62.0636 | -61.203 | -0.064087 | -0.10529 | -0.10986 | 0 | 0.07782 | 0.21515 | -0.35248 | -0.34332 | 0.11902 | 9.5535 | 60.7956 | -62.0499 | 60.5072 | -61.7294 | 9.8969
1645.7656 | 123.0789 | -60.7773 | 61.94 | -0.070844 | 0.048147 | 0.049906 | -0.0014242 | 0.00040688 | 0.0016072 | -0.00085453 | -51.2329 | 61.94 | -61.1938 | 0.12817 | 0.13733 | 0.15106 | -0.054932 | 0.37994 | 0.2243 | -0.20599 | -0.41657 | 0 | 9.5444 | 60.9055 | -61.8027 | 60.5713 | -61.7157 | 9.9609
1646.75 | 122.9462 | -60.8688 | 61.9492 | 0.051226 | 0.05541 | 0.056101 | 0.0090434 | 0.00062048 | -0.0011698 | -0.0014953 | -51.2466 | 62.0087 | -61.2122 | 0.004578 | -0.022888 | -0.036621 | 0.018311 | 0.17853 | 0.24261 | -0.32501 | -0.34332 | 0.059509 | 9.6222 | 60.8734 | -61.972 | 60.5438 | -61.7065 | 9.9655
1647.7656 | 123.0423 | -60.7681 | 61.94 | -0.0021797 | 0.050496 | 0.052256 | -0.0009968 | 0.0012615 | -0.0035198 | -0.0014953 | -51.2146 | 61.9812 | -61.1801 | 0.10986 | 0.11902 | 0.15106 | 0 | 0.34332 | 0.23804 | -0.21515 | -0.41199 | 0.041199 | 9.5535 | 60.878 | -61.821 | 60.553 | -61.702 | 9.9655
1648.7344 | 122.9965 | -60.8047 | 61.9354 | -0.0098092 | 0.052419 | 0.048197 | 0.0094706 | 0.0019023 | -0.00074255 | -0.0010681 | -51.2054 | 62.059 | -61.1343 | 0.07782 | 0.045776 | 0.036621 | 0 | 0.19226 | 0.21973 | -0.28839 | -0.32959 | 0.1236 | 9.5993 | 60.8826 | -61.8896 | 60.5164 | -61.7157 | 9.9289
1649.7344 | 122.9874 | -60.8368 | 61.9629 | -0.10136 | 0.053701 | 0.056529 | 0.00648 | 0.0042521 | -0.002238 | -0.00042733 | -51.21 | 62.0728 | -61.1801 | 0.07782 | 0.068665 | 0.054932 | 0.041199 | 0.25177 | 0.26093 | -0.25177 | -0.34332 | 0.10986 | 9.6268 | 60.9146 | -61.8942 | 60.585 | -61.702 | 9.9701
1650.7344 | 122.9141 | -60.8597 | 61.9537 | 0.089373 | 0.054128 | 0.053965 | 0.007548 | 0.0038249 | -0.00052895 | 0.00042727 | -51.2878 | 62.0728 | -61.203 | -0.032043 | -0.064087 | -0.10071 | 0.036621 | 0.11902 | 0.2243 | -0.32044 | -0.34332 | 0.11902 | 9.5718 | 60.8276 | -62.0178 | 60.5392 | -61.7294 | 9.9152
1651.7656 | 122.9645 | -60.8551 | 61.9263 | 0.21144 | 0.053274 | 0.053965 | 0.0049846 | 0.0025431 | 0.00011185 | 0.0012817 | -51.2924 | 62.0453 | -61.2213 | -0.13733 | -0.045776 | 0.1236 | -0.004578 | 0.041199 | 0.21057 | -0.31586 | -0.36621 | 0.11902 | 9.5627 | 60.7178 | -61.972 | 60.5392 | -61.7157 | 9.9289
1652.7344 | 123.0331 | -60.8231 | 61.908 | 0.27248 | 0.053487 | 0.052043 | 0.005839 | 0.0038249 | 0.00075285 | -0.0014953 | -51.4252 | 62.027 | -61.203 | -0.009155 | -0.009155 | -0.036621 | -0.11444 | 0.15564 | 0.1831 | -0.34332 | -0.37994 | 0.11902 | 9.3979 | 60.8139 | -61.9171 | 60.4797 | -61.7249 | 9.7778
1653.7656 | 122.9691 | -60.8276 | 61.9492 | -0.040327 | 0.052633 | 0.053965 | 0.004771 | 0.0040385 | -0.00010175 | -0.0014953 | -51.3474 | 62.0728 | -61.171 | 0.041199 | 0.036621 | 0.036621 | 0.022888 | 0.22888 | 0.23346 | -0.29297 | -0.34332 | 0.1236 | 9.4803 | 60.8688 | -61.9125 | 60.5347 | -61.7157 | 9.8236
1654.7344 | 122.9324 | -60.8459 | 61.9446 | 0.11226 | 0.054555 | 0.05247 | 0.0094706 | 0.0051067 | -0.0018108 | -0.0010681 | -51.4435 | 62.0728 | -61.1984 | -0.027466 | -0.045776 | -0.050354 | 0.032043 | 0.13733 | 0.23804 | -0.3067 | -0.35248 | 0.12817 | 9.4025 | 60.8185 | -61.9904 | 60.5392 | -61.7065 | 9.7549
1655.7656 | 123.0377 | -60.8093 | 61.9217 | 0.035967 | 0.050069 | 0.047984 | -0.0044148 | 0.0023295 | -0.00010175 | 0.0010681 | -51.4481 | 61.9492 | -61.1664 | -0.009155 | 0.041199 | 0.059509 | -0.027466 | 0.24719 | 0.21515 | -0.27008 | -0.35706 | 0.027466 | 9.3613 | 60.8002 | -61.8805 | 60.5392 | -61.7065 | 9.7183
1656.7344 | 123.0011 | -60.8047 | 61.94 | -0.11662 | 0.051992 | 0.049266 | 0.0056254 | 0.00083408 | -0.00052895 | -0.0025635 | -51.4069 | 62.0682 | -61.1893 | 0.054932 | 0.041199 | 0.064087 | 0.050354 | 0.23804 | 0.25177 | -0.26093 | -0.38452 | 0.12817 | 9.3979 | 60.8597 | -61.8988 | 60.5438 | -61.6882 | 9.7824
1657.7656 | 123.0698 | -60.7864 | 61.9308 | -0.032697 | 0.050496 | 0.050761 | -0.0022786 | 0.00040688 | 0.00096645 | -0.0014953 | -51.3519 | 61.9675 | -61.1572 | 0.10986 | 0.12817 | 0.15106 | -0.054932 | 0.36621 | 0.21973 | -0.22888 | -0.37079 | 0.036621 | 9.4345 | 60.8963 | -61.8027 | 60.5576 | -61.7111 | 9.8053
1658.7344 | 122.9416 | -60.8643 | 61.9629 | 0.10463 | 0.05306 | 0.048411 | 0.0081888 | 0.0010477 | -0.00074255 | -0.0010681 | -51.5671 | 62.0453 | -61.1893 | -0.036621 | -0.059509 | -0.059509 | 0.032043 | 0.1236 | 0.22888 | -0.33417 | -0.32501 | 0.082397 | 9.2972 | 60.8276 | -62.0224 | 60.5301 | -61.734 | 9.6222
1659.75 | 122.8821 | -60.8597 | 61.8668 | 0.24959 | 0.055196 | 0.052256 | 0.0051982 | 0.0010477 | 0.0018208 | -0.00085453 | -51.4755 | 62.0544 | -61.1893 | -0.064087 | -0.059509 | -0.10529 | -0.009155 | 0.10529 | 0.21973 | -0.37537 | -0.32959 | 0.18768 | 9.3842 | 60.7956 | -61.9263 | 60.4843 | -61.647 | 9.7137
1660.7344 | 123.0011 | -60.8459 | 61.9583 | -0.040327 | 0.052205 | 0.051188 | 0.0060526 | 0.0021159 | -0.0020244 | -0.00042733 | -51.3474 | 62.0682 | -61.1938 | 0.041199 | 0.045776 | 0.054932 | 0.041199 | 0.24719 | 0.26093 | -0.26093 | -0.3479 | 0.10986 | 9.4986 | 60.8871 | -61.9125 | 60.585 | -61.6974 | 9.8465
1661.7656 | 123.0377 | -60.8139 | 61.9263 | -0.0098092 | 0.050069 | 0.050334 | -0.0024922 | 0.0027567 | -0.0024516 | -0.0017089 | -51.384 | 61.9354 | -61.171 | 0.054932 | 0.091553 | 0.091553 | -0.059509 | 0.31586 | 0.23346 | -0.24719 | -0.35706 | 0.009155 | 9.4299 | 60.8688 | -61.8347 | 60.5667 | -61.6928 | 9.787
1662.7344 | 122.9279 | -60.8414 | 61.9583 | 0.11226 | 0.052633 | 0.054392 | 0.0090434 | 0.0036113 | -0.0013834 | 0.0014953 | -51.1734 | 62.0636 | -61.1938 | -0.036621 | -0.073242 | -0.082397 | 0.022888 | 0.12817 | 0.22888 | -0.32044 | -0.35248 | 0.10529 | 9.668 | 60.8047 | -62.0316 | 60.5209 | -61.7294 | 10.0204
1663.7656 | 123.0331 | -60.8093 | 61.9034 | 0.15804 | 0.049215 | 0.04777 | -0.0033468 | 0.00062048 | -0.00031535 | 0.0010681 | -51.5488 | 61.9171 | -61.203 | 0 | 0.041199 | 0.036621 | -0.073242 | 0.21515 | 0.20142 | -0.27924 | -0.39368 | 0.013733 | 9.2606 | 60.8093 | -61.8622 | 60.5301 | -61.702 | 9.6542
1664.7344 | 122.9919 | -60.8322 | 61.9446 | -0.14714 | 0.054128 | 0.048838 | 0.0054118 | 0.0019023 | -0.00010175 | -0.00064093 | -51.2787 | 62.0728 | -61.1664 | 0.045776 | 0.036621 | 0.059509 | 0.10529 | 0.26093 | 0.2655 | -0.20142 | -0.33417 | 0.12817 | 9.5535 | 60.878 | -61.908 | 60.6308 | -61.6791 | 9.8877
1665.7656 | 123.0377 | -60.8047 | 61.8988 | 0.21144 | 0.052419 | 0.049906 | -0.0007832 | 0.0016887 | 0.00053925 | -0.00021353 | -51.4252 | 61.9446 | -61.171 | 0.036621 | 0.050354 | 0.041199 | -0.15106 | 0.2243 | 0.1831 | -0.35248 | -0.36621 | 0.045776 | 9.3796 | 60.8414 | -61.8484 | 60.4523 | -61.7157 | 9.7458
1666.7344 | 122.9874 | -60.8231 | 61.9583 | -0.032697 | 0.053487 | 0.051402 | 0.0096842 | 0.0040385 | -0.0024516 | 0.00064087 | -51.4938 | 62.0407 | -61.1801 | -0.14648 | -0.018311 | 0.1831 | 0.091553 | 0.25177 | 0.23804 | -0.29755 | -0.35706 | 0.082397 | 9.3292 | 60.6766 | -61.9766 | 60.5255 | -61.7203 | 9.6863
1667.7656 | 122.9965 | -60.8002 | 61.94 | -0.20054 | 0.049001 | 0.052256 | -0.0016378 | 0.0025431 | -0.0030924 | -0.0017089 | -51.3016 | 61.9675 | -61.1801 | 0.082397 | 0.086975 | 0.11444 | 0.064087 | 0.32959 | 0.2655 | -0.20142 | -0.37994 | 0.027466 | 9.4986 | 60.8826 | -61.853 | 60.5988 | -61.6745 | 9.8785
1668.7344 | 122.9141 | -60.8322 | 61.9629 | 0.21907 | 0.053914 | 0.054606 | 0.0081888 | 0.0029705 | -0.00010175 | -0.0010681 | -51.4984 | 62.0361 | -61.1847 | -0.050354 | -0.07782 | -0.75989 | -0.32501 | 0.58594 | 0.1831 | -0.39368 | -0.35248 | 0.073242 | 9.3338 | 60.7819 | -62.0407 | 60.4385 | -61.7798 | 9.6863
1669.7656 | 123.0515 | -60.8231 | 61.908 | -0.94822 | 0.051565 | 0.046702 | 7.12e-05 | 0.0029705 | -0.00095615 | 0.00021367 | -51.384 | 61.972 | -61.1481 | 0.022888 | 0.022888 | 0.018311 | -0.19226 | 0.21973 | 0.17395 | -0.30212 | -0.32501 | 0.064087 | 9.4391 | 60.8459 | -61.8851 | 60.5209 | -61.734 | 9.7641
1670.7344 | 123.0103 | -60.8459 | 61.94 | -0.12425 | 0.051992 | 0.051188 | 0.0084026 | 0.00083408 | -0.0011698 | -0.0014953 | -51.5396 | 62.0453 | -61.171 | 0.045776 | 0.045776 | 0.050354 | 0.082397 | 0.25635 | 0.27924 | -0.2243 | -0.32501 | 0.10529 | 9.3063 | 60.8917 | -61.8942 | 60.6216 | -61.6608 | 9.6313
1671.7656 | 123.0331 | -60.8139 | 61.9171 | 0.12752 | 0.050283 | 0.046275 | -0.0035604 | 0.0012615 | 0.00075285 | -0.0010681 | -51.6861 | 61.9492 | -61.1893 | 0.018311 | 0.036621 | 0.050354 | -0.068665 | 0.23346 | 0.20142 | -0.29755 | -0.37537 | 0.032044 | 9.1278 | 60.8322 | -61.8805 | 60.5164 | -61.7157 | 9.5032
1672.7344 | 122.9965 | -60.8047 | 61.9583 | -0.10899 | 0.052846 | 0.047984 | 0.0060526 | 0.0010477 | 0.00011185 | -0.0014953 | -51.1917 | 62.0361 | -61.1755 | 0.036621 | 0.027466 | 0.050354 | 0.11444 | 0.26093 | 0.26093 | -0.20142 | -0.37079 | 0.07782 | 9.613 | 60.8414 | -61.9308 | 60.6033 | -61.6974 | 9.9838
1673.7656 | 123.0377 | -60.7956 | 61.9537 | 0.089373 | 0.049856 | 0.046061 | -0.0005696 | 0.0021159 | 0.00075285 | -0.0019225 | -51.384 | 61.9446 | -61.2122 | 0.009155 | -0.027466 | 0.009155 | -0.10529 | 0.24261 | 0.21057 | -0.27924 | -0.41657 | -0.009155 | 9.4116 | 60.8047 | -61.9812 | 60.5164 | -61.7432 | 9.8282
1674.7344 | 122.9965 | -60.8459 | 61.9629 | -0.086103 | 0.051351 | 0.053752 | 0.0079752 | 0.00062048 | -0.0020244 | -0.0019225 | -51.5488 | 62.0682 | -61.1801 | 0.068665 | 0.036621 | 0.041199 | 0.022888 | 0.23804 | 0.2655 | -0.2655 | -0.33417 | 0.10529 | 9.2972 | 60.9146 | -61.9263 | 60.5804 | -61.6974 | 9.6313
1675.7656 | 123.056 | -60.7819 | 61.9171 | -0.063215 | 0.05071 | 0.049693 | 0.0002848 | 0.0010477 | -0.00031535 | -0.0023499 | -51.59 | 61.9583 | -61.1526 | 0.10986 | 0.1236 | 0.16022 | -0.07782 | 0.36621 | 0.20599 | -0.20142 | -0.37079 | 0.041199 | 9.1919 | 60.8917 | -61.7935 | 60.5804 | -61.7111 | 9.5627
1676.7344 | 122.9736 | -60.8322 | 61.9629 | -0.14714 | 0.052419 | 0.048838 | 0.005839 | 0.0012615 | -0.0024516 | -0.00085453 | -51.6266 | 62.059 | -61.1984 | 0.059509 | 0.041199 | 0.018311 | 0.064087 | 0.25635 | 0.27008 | -0.25177 | -0.36621 | 0.09613 | 9.2056 | 60.8917 | -61.9217 | 60.5804 | -61.6928 | 9.5718
1677.7656 | 123.0515 | -60.8002 | 61.9217 | -0.14714 | 0.05306 | 0.049693 | -0.0012106 | 0.0010477 | 0.00011185 | -0.0014953 | -51.6357 | 62.0041 | -61.1298 | 0.11902 | 0.1236 | 0.15564 | -0.036621 | 0.37994 | 0.23346 | -0.2243 | -0.32959 | 0.082397 | 9.1644 | 60.9192 | -61.7981 | 60.5759 | -61.6882 | 9.494
1678.7344 | 122.9645 | -60.8414 | 61.9583 | -0.13188 | 0.053274 | 0.054606 | 0.0090434 | 0.00083408 | -0.0011698 | -0.0014953 | -51.6357 | 62.0453 | -61.1755 | 0.054932 | 0.022888 | 0.032043 | 0.018311 | 0.23346 | 0.23804 | -0.27924 | -0.33417 | 0.086975 | 9.2056 | 60.8963 | -61.9354 | 60.5621 | -61.7203 | 9.5398
1679.75 | 123.056 | -60.7956 | 61.8896 | 0.29537 | 0.053701 | 0.049693 | 0.0034892 | 0.0036113 | -0.0020244 | -0.0023499 | -51.5762 | 61.9904 | -61.1755 | 0.041199 | 0.059509 | 0.036621 | -0.20599 | 0.21973 | 0.17395 | -0.37994 | -0.37994 | 0.10071 | 9.2194 | 60.8368 | -61.8301 | 60.4156 | -61.7157 | 9.5993
1680.7344 | 122.9828 | -60.8276 | 61.94 | -0.10136 | 0.054128 | 0.050975 | 0.0043436 | 0.0027567 | -0.0020244 | -0.00021353 | -51.6907 | 62.0682 | -61.203 | 0.032043 | 0.009155 | 0.045776 | 0.12817 | 0.24719 | 0.27008 | -0.2243 | -0.37537 | 0.12817 | 9.137 | 60.8597 | -61.9308 | 60.6033 | -61.6699 | 9.5123
1681.7656 | 123.0331 | -60.8093 | 61.9125 | 0.10463 | 0.049856 | 0.048625 | -0.0031332 | 0.0010477 | -0.0020244 | -0.0017089 | -51.6769 | 61.9446 | -61.1801 | 0.032043 | 0.059509 | 0.064087 | 0.25177 | 0.34332 | 0.22888 | -0.27466 | -0.37079 | 0.032043 | 9.1324 | 60.8414 | -61.853 | 60.5347 | -61.6837 | 9.5032
1682.7344 | 122.9691 | -60.8276 | 61.9537 | 0.013079 | 0.053274 | 0.055888 | 0.0090434 | 0.0023295 | 0.00075285 | -0.0025635 | -51.6037 | 62.0407 | -61.1618 | 0.018311 | 0 | -0.013733 | -0.004578 | 0.16937 | 0.22888 | -0.32044 | -0.33417 | 0.086975 | 9.2239 | 60.8459 | -61.9537 | 60.5072 | -61.7249 | 9.5581
1683.7656 | 123.0423 | -60.8002 | 61.9217 | 0.21907 | 0.05071 | 0.050761 | -0.0018514 | -0.0010885 | 0.002248 | -0.00021353 | -51.6357 | 61.9583 | -61.1938 | -0.004578 | 0.022888 | 0.009155 | -0.11444 | 0.21057 | 0.17853 | -0.32044 | -0.39368 | 0.036621 | 9.1644 | 60.7956 | -61.8988 | 60.4797 | -61.7432 | 9.5581
1684.7344 | 122.9874 | -60.8185 | 61.9492 | -0.017439 | 0.051565 | 0.050547 | 0.0079752 | 0.0014751 | -0.00052895 | -0.0025635 | -51.6129 | 62.0407 | -61.1755 | 0.068665 | 0.018311 | 0.032043 | 0.022888 | 0.24719 | 0.2243 | -0.28381 | -0.35706 | 0.091552 | 9.2056 | 60.8871 | -61.9308 | 60.5347 | -61.7249 | 9.5627
1685.7656 | 123.0606 | -60.8093 | 61.9171 | -0.0021797 | 0.05071 | 0.049052 | -0.0022786 | 0.0016887 | -0.0015972 | 0.0010681 | -51.6357 | 61.9446 | -61.1893 | 0.073242 | 0.10986 | 0.11444 | -0.059509 | 0.33417 | 0.2243 | -0.24719 | -0.37994 | 0.027466 | 9.1736 | 60.8826 | -61.8073 | 60.5621 | -61.6928 | 9.5535
1686.7344 | 122.9324 | -60.8414 | 61.9446 | 0.20381 | 0.052633 | 0.049052 | 0.010325 | 0.0016887 | -0.002238 | -0.0012817 | -51.6907 | 62.0316 | -61.203 | -0.059509 | -0.045776 | -0.091553 | -0.009155 | 0.082397 | 0.20142 | -0.36163 | -0.36163 | 0.086975 | 9.1507 | 60.7819 | -61.9904 | 60.4797 | -61.7432 | 9.5123
1687.75 | 123.0057 | -60.8185 | 61.8988 | 0.24959 | 0.050924 | 0.050547 | 0.001353 | 0.00083408 | -0.00010175 | 0.00042727 | -51.6632 | 61.9766 | -61.1618 | -0.004578 | 0.018311 | 0.018311 | -0.1236 | 0.20599 | 0.17395 | -0.31128 | -0.34332 | 0.07782 | 9.1553 | 60.8139 | -61.8805 | 60.5072 | -61.7249 | 9.4986
1688.7344 | 122.9645 | -60.8551 | 61.9583 | 0.21907 | 0.052846 | 0.05247 | 0.012248 | 0.0033977 | -0.0018108 | -0.00085453 | -51.709 | 62.0407 | -61.2259 | 0.2243 | -0.13733 | -0.1831 | 0.16022 | 0.1831 | 0.20599 | -0.34332 | -0.37079 | 0.082397 | 9.1461 | 61.0794 | -62.0956 | 60.5118 | -61.7523 | 9.5169
1689.7656 | 123.0331 | -60.7956 | 61.8851 | -0.12425 | 0.051137 | 0.05247 | 7.12e-05 | 0.0012615 | 0.0024618 | -0.00042733 | -51.7685 | 61.9492 | -61.1664 | 0.036621 | 0.045776 | 0.059509 | -0.16937 | 0.22888 | 0.1831 | -0.31586 | -0.37079 | 0.064087 | 9.0271 | 60.8322 | -61.8393 | 60.4797 | -61.702 | 9.3979
1690.7344 | 122.9233 | -60.8139 | 61.9904 | -0.39891 | 0.054342 | 0.050334 | 0.0062662 | -0.00023392 | -0.00074255 | 0.00042727 | -51.8829 | 62.059 | -61.203 | -0.013733 | 0.004578 | 0.073242 | 0.15106 | 0.25177 | 0.27466 | -0.28381 | -0.3891 | 0.068665 | 8.931 | 60.8002 | -61.9858 | 60.5301 | -61.7157 | 9.3201
1691.7656 | 123.0057 | -60.8231 | 61.9125 | 0.21907 | 0.053701 | 0.051188 | 0.0009258 | 0.0025431 | -0.00010175 | 6.6667e-08 | -51.8234 | 62.0087 | -61.1755 | 0.013733 | 0.018311 | 0 | -0.13733 | 0.19684 | 0.17853 | -0.35248 | -0.35248 | 0.09613 | 8.9996 | 60.8368 | -61.8942 | 60.4706 | -61.734 | 9.3521
1692.7344 | 122.9691 | -60.8276 | 61.9766 | -0.17003 | 0.051565 | 0.052256 | 0.00648 | 0.0010477 | -0.0013834 | 0.00085447 | -51.8921 | 62.0499 | -61.171 | 0.041199 | 0.036621 | 0.050354 | 0.1236 | 0.26093 | 0.27008 | -0.20599 | -0.34332 | 0.073242 | 8.9355 | 60.8688 | -61.94 | 60.6216 | -61.7065 | 9.2789
1693.7656 | 123.0377 | -60.8047 | 61.908 | 0.081743 | 0.049642 | 0.044779 | -0.0046284 | 0.0012615 | 0.00075285 | 0.00064087 | -51.8234 | 61.9675 | -61.1893 | -0.018311 | 0.041199 | 0.022888 | -0.059509 | 0.27466 | 0.20142 | -0.28381 | -0.38452 | 0.059509 | 8.9813 | 60.7864 | -61.8668 | 60.5209 | -61.7065 | 9.3658
1694.7344 | 122.9645 | -60.8185 | 61.9583 | -0.1624 | 0.050924 | 0.053111 | 0.007548 | 0.0010477 | -0.00031535 | -0.0012817 | -51.828 | 62.0728 | -61.1847 | 0.022888 | 0.013733 | 0.041199 | 0.11902 | 0.23804 | 0.27008 | -0.23346 | -0.36621 | 0.11444 | 8.9905 | 60.8414 | -61.9446 | 60.585 | -61.6882 | 9.3567
1695.7656 | 123.0698 | -60.7956 | 61.9171 | 0.013079 | 0.049428 | 0.051402 | -0.0007832 | -0.00066112 | -0.00031535 | -0.00085453 | -51.7639 | 61.9446 | -61.1664 | 0.059509 | 0.086975 | 0.082397 | -0.073242 | 0.3067 | 0.21973 | -0.25635 | -0.37079 | 0.027466 | 9.0317 | 60.8551 | -61.8301 | 60.5392 | -61.6974 | 9.4025
1696.7344 | 122.9919 | -60.8185 | 61.9583 | -0.13188 | 0.051778 | 0.047557 | 0.0069072 | 0.00040688 | -0.0024516 | -0.0017089 | -51.915 | 62.0499 | -61.1847 | 0.059509 | 0.032043 | 0.050354 | 0.086975 | 0.28381 | 0.26093 | -0.2655 | -0.36621 | 0.091553 | 8.9035 | 60.878 | -61.9263 | 60.553 | -61.6974 | 9.2697
1697.7656 | 123.024 | -60.8414 | 61.908 | 0.24196 | 0.055196 | 0.054392 | 0.0066936 | 0.0025431 | 0.0024618 | -0.0021361 | -51.915 | 62.0316 | -61.1938 | -0.013733 | -0.027466 | -0.059509 | -0.1236 | 0.15564 | 0.17395 | -0.37079 | -0.35248 | 0.1236 | 8.9264 | 60.8276 | -61.9354 | 60.4706 | -61.734 | 9.2789
1698.7344 | 122.9233 | -60.8276 | 61.9629 | -0.63542 | 0.053701 | 0.049479 | 0.005839 | 0.0014751 | -0.00010175 | -0.0012817 | -52.0203 | 62.0773 | -61.1847 | -0.013733 | -0.009155 | 0.054932 | 0.14191 | 0.24719 | 0.26093 | -0.2655 | -0.35705 | 0.11444 | 8.8074 | 60.8139 | -61.972 | 60.5621 | -61.702 | 9.1644
1699.7656 | 123.0652 | -60.7727 | 61.9171 | -0.10136 | 0.046651 | 0.049906 | -0.0018514 | -2.0324e-05 | -0.0013834 | -0.0014953 | -52.0981 | 61.9446 | -61.171 | 0.13275 | 0.12817 | 0.16022 | -0.036621 | 0.35248 | 0.24261 | -0.2243 | -0.39825 | 0.027466 | 8.6746 | 60.9055 | -61.7889 | 60.5484 | -61.6745 | 9.0729
1700.7344 | 122.9782 | -60.8231 | 61.9675 | -0.14714 | 0.052419 | 0.047984 | 0.0077616 | 0.00040688 | -0.0011698 | 6.6667e-08 | -52.1072 | 62.059 | -61.1664 | 0.059509 | 0.050354 | 0.064087 | 0.07782 | 0.26093 | 0.27924 | -0.23804 | -0.34332 | 0.091553 | 8.7158 | 60.8826 | -61.9171 | 60.585 | -61.6882 | 9.0591
1701.7656 | 123.056 | -60.8093 | 61.8988 | 0.23433 | 0.052846 | 0.046702 | 0.0011394 | -0.00066112 | 0.00096645 | -0.00042733 | -51.9928 | 61.94 | -61.1755 | 0 | 0.086975 | 0.16022 | -0.22888 | 0.21057 | 0.17853 | -0.3479 | -0.36621 | 0.041198 | 8.8165 | 60.8093 | -61.8118 | 60.4614 | -61.7203 | 9.1827
1702.7344 | 122.9736 | -60.8093 | 61.9583 | -0.047956 | 0.054342 | 0.050975 | 0.010112 | 0.0019023 | -0.0015972 | -0.0017089 | -52.034 | 62.0499 | -61.1801 | 0.050354 | 0.022888 | 0.032043 | 0.036621 | 0.23804 | 0.24719 | -0.28839 | -0.37079 | 0.091553 | 8.7753 | 60.8597 | -61.9354 | 60.5209 | -61.7111 | 9.1461
1703.75 | 122.9874 | -60.8368 | 61.9171 | 0.25722 | 0.053487 | 0.053111 | 0.0077616 | 0.00019328 | -0.00052895 | 6.6667e-08 | -52.0615 | 62.0499 | -61.2076 | -0.032043 | -0.036621 | -0.059509 | -0.07782 | 0.13275 | 0.20599 | -0.3479 | -0.37079 | 0.13275 | 8.7753 | 60.8047 | -61.9537 | 60.4889 | -61.7111 | 9.1461
1704.7344 | 122.9919 | -60.8276 | 61.9537 | -0.10899 | 0.054342 | 0.049693 | 0.0056254 | 0.0016887 | -0.0028788 | -0.0034179 | -52.1164 | 62.0728 | -61.1984 | 0.054932 | 0.045776 | 0.064087 | 0.10529 | 0.27466 | 0.27466 | -0.21973 | -0.37079 | 0.11902 | 8.7112 | 60.8826 | -61.908 | 60.6079 | -61.6791 | 9.082
1705.7656 | 123.0286 | -60.8047 | 61.9125 | 0.27248 | 0.047292 | 0.048411 | -0.0018514 | 0.00040688 | -0.0015972 | -0.0010681 | -52.0798 | 61.9675 | -61.171 | 0.10071 | 0.1236 | 0.13275 | 0 | 0.36163 | 0.23804 | -0.22888 | -0.36621 | 0.054931 | 8.725 | 60.9055 | -61.7889 | 60.5759 | -61.6745 | 9.0912
1706.7344 | 122.9828 | -60.8185 | 61.9354 | -0.025068 | 0.050283 | 0.050334 | 0.00648 | 0.0016887 | -0.0011698 | -0.0027771 | -52.1942 | 62.0453 | -61.171 | 0.059509 | 0.041199 | 0.041199 | 0.036621 | 0.25177 | 0.25635 | -0.27008 | -0.35248 | 0.10986 | 8.6243 | 60.878 | -61.8942 | 60.5484 | -61.6791 | 8.9767
1707.7656 | 123.056 | -60.8047 | 61.8805 | 0.23433 | 0.051137 | 0.049906 | 0.002421 | 0.0051067 | 0.00096645 | -0.0046997 | -52.1896 | 61.9858 | -61.171 | 0.32959 | 0.20599 | -0.054932 | -0.16937 | 0.35706 | 0.15564 | -0.3891 | -0.36621 | 0.10529 | 8.6151 | 61.1343 | -61.6745 | 60.4156 | -61.7249 | 8.9813
1708.7344 | 122.9919 | -60.8139 | 61.9263 | -0.032697 | 0.051778 | 0.052256 | 0.0079752 | 0.0016887 | 0.00011185 | -0.0012817 | -52.1622 | 62.0773 | -61.1847 | 0.059509 | 0.032043 | 0.032043 | 0.036621 | 0.23804 | 0.25635 | -0.27008 | -0.37079 | 0.15106 | 8.6517 | 60.8734 | -61.8942 | 60.5438 | -61.6699 | 9.0225
1709.7656 | 123.0194 | -60.8093 | 61.9125 | -0.6812 | 0.049215 | 0.045634 | -0.0029196 | 0.0033977 | 0.00075285 | -0.00021353 | -52.3453 | 61.972 | -61.1893 | 0 | 0.045776 | 0.064087 | -0.064087 | 0.2655 | 0.20599 | -0.2655 | -0.37994 | 0.059509 | 8.4641 | 60.8093 | -61.8668 | 60.5438 | -61.7065 | 8.844
1710.7344 | 122.9828 | -60.8459 | 61.94 | -0.26921 | 0.053701 | 0.047343 | 0.0077616 | 0.00062048 | 0.00053925 | -0.00085453 | -52.1713 | 62.0636 | -61.1618 | 0.027466 | 0.004578 | 0.009155 | 0.032043 | 0.22888 | 0.25177 | -0.30212 | -0.31586 | 0.1236 | 8.6746 | 60.8734 | -61.9354 | 60.5438 | -61.6882 | 8.9905
1711.7656 | 123.0377 | -60.8047 | 61.9034 | 0.46321 | 0.049856 | 0.043284 | -0.0009968 | -0.00044752 | -0.00010175 | 0.00085447 | -52.3361 | 61.9583 | -61.1847 | 0.027466 | 0.050354 | 0.054932 | -0.07782 | 0.25635 | 0.21515 | -0.27924 | -0.37994 | 0.054932 | 8.4686 | 60.8322 | -61.853 | 60.5255 | -61.6882 | 8.8486
1712.7344 | 123.0835 | -60.8368 | 61.8805 | 0.24959 | 0.051351 | 0.049906 | 0.0032756 | 0.0027567 | 0.0013936 | -0.00042733 | -52.2263 | 61.9537 | -61.1893 | 0.045776 | 0.045776 | 0.032043 | -0.18768 | 0.21973 | 0.15106 | -0.3891 | -0.35248 | 0.073242 | 8.6105 | 60.8826 | -61.8347 | 60.4477 | -61.7294 | 8.963
1713.7656 | 123.0789 | -60.791 | 61.9125 | -0.17766 | 0.047719 | 0.051829 | 0.0004984 | -0.00044752 | -0.0024516 | -0.0017089 | -52.2491 | 61.9537 | -61.1618 | 0.11444 | 0.1236 | 0.16479 | -0.045776 | 0.36163 | 0.23804 | -0.2243 | -0.37079 | 0.041198 | 8.5419 | 60.9055 | -61.7889 | 60.5667 | -61.6745 | 8.9127
1714.7344 | 122.9736 | -60.8276 | 61.9446 | -0.0098092 | 0.051565 | 0.047984 | 0.010752 | -2.0324e-05 | -0.0020244 | -0.0014953 | -52.2766 | 62.0453 | -61.1481 | 0.041199 | -0.009155 | 0.013733 | 0.027466 | 0.18768 | 0.24261 | -0.28839 | -0.32043 | 0.10071 | 8.551 | 60.8688 | -61.9537 | 60.5392 | -61.702 | 8.8715
1715.75 | 123.0881 | -60.8368 | 61.8805 | 0.34114 | 0.051137 | 0.05012 | 0.00413 | 0.0014751 | 0.00053925 | -0.0012817 | -52.2995 | 61.9675 | -61.1984 | 0.045776 | 0.027466 | 0.027466 | -0.1831 | 0.23346 | 0.16937 | -0.37994 | -0.36163 | 0.086975 | 8.5373 | 60.8826 | -61.853 | 60.4568 | -61.7111 | 8.8989
1716.7344 | 122.9324 | -60.8643 | 61.9492 | 0.15041 | 0.053274 | 0.053111 | 0.0071208 | 0.0023295 | -0.00010175 | -0.0017089 | -52.3819 | 62.0773 | -61.1755 | -0.027466 | -0.064087 | -0.064087 | 0.022888 | 0.10986 | 0.24261 | -0.33417 | -0.31128 | 0.12817 | 8.4824 | 60.8368 | -62.0132 | 60.5301 | -61.7065 | 8.7936
1717.7656 | 122.9919 | -60.8368 | 61.94 | -0.032697 | 0.052205 | 0.050334 | 0.0066936 | 0.0027567 | -0.0020244 | 0.00021367 | -52.3407 | 62.0132 | -61.2122 | 0.050354 | 0.032043 | 0.018311 | 0.032043 | 0.24719 | 0.25177 | -0.2655 | -0.37537 | 0.073243 | 8.4961 | 60.8871 | -61.908 | 60.5713 | -61.6882 | 8.8715
1718.7344 | 122.9736 | -60.8276 | 61.9446 | 0.028338 | 0.052846 | 0.044779 | 0.0073344 | 0.0031841 | -0.00031535 | -0.0019225 | -52.3727 | 62.059 | -61.1984 | -0.013733 | -0.018311 | -0.032043 | 0.009155 | 0.17395 | 0.24719 | -0.33417 | -0.37079 | 0.11444 | 8.4549 | 60.8139 | -61.9629 | 60.4935 | -61.6974 | 8.8257
1719.7656 | 123.0835 | -60.7773 | 61.908 | -0.070844 | 0.046651 | 0.049266 | -0.0024922 | 0.0016887 | -0.0028788 | -0.0010681 | -52.4185 | 61.94 | -61.2076 | 0.11444 | 0.13733 | 0.16479 | -0.07782 | 0.3479 | 0.21057 | -0.19684 | -0.4303 | 0.032043 | 8.3588 | 60.8917 | -61.7706 | 60.5804 | -61.6974 | 8.7891
1720.7344 | 122.9324 | -60.8688 | 61.9446 | 0.11989 | 0.05306 | 0.054392 | 0.0073344 | 0.0061747 | -0.00095615 | -0.0021361 | -52.4734 | 62.0636 | -61.2076 | -0.07782 | -0.068665 | -0.086975 | 0.027466 | 0.10986 | 0.22888 | -0.37079 | -0.33875 | 0.11902 | 8.3954 | 60.791 | -62.0132 | 60.498 | -61.7157 | 8.7341
1721.7656 | 123.0011 | -60.8093 | 61.9354 | -0.23869 | 0.048574 | 0.043498 | -0.0005696 | -0.00044752 | -0.0024516 | -0.0032043 | -52.4368 | 62.0041 | -61.1755 | 0.07782 | 0.10529 | 0.12817 | 0.036621 | 0.32501 | 0.24719 | -0.21515 | -0.36621 | 0.068664 | 8.3725 | 60.8871 | -61.8301 | 60.5942 | -61.6882 | 8.7387
1722.7344 | 122.937 | -60.8414 | 61.972 | 0.11989 | 0.051778 | 0.053111 | 0.0081888 | 0.0027567 | 0.00011185 | -0.00021353 | -52.4277 | 62.0544 | -61.1801 | -0.032043 | -0.054932 | -0.086975 | 0.013733 | 0.082397 | 0.2243 | -0.35706 | -0.33875 | 0.082397 | 8.4137 | 60.8093 | -62.027 | 60.4843 | -61.7477 | 8.7524
1723.7656 | 123.0148 | -60.791 | 61.8942 | 0.13515 | 0.049428 | 0.047557 | -0.0042012 | -0.00044752 | -0.0015972 | -0.0027771 | -52.4597 | 61.908 | -61.203 | 0.013733 | 0.036621 | 0.041199 | -0.07782 | 0.24261 | 0.20599 | -0.26093 | -0.41199 | 0.013733 | 8.3313 | 60.8047 | -61.8576 | 60.5301 | -61.6882 | 8.7433
1724.7344 | 122.9553 | -60.8597 | 61.9308 | 0.21907 | 0.05306 | 0.05012 | 0.0071208 | 0.0031841 | 0.0016072 | -0.0012817 | -52.4872 | 62.0544 | -61.1984 | -0.054932 | -0.068665 | -0.10071 | -0.013733 | 0.09613 | 0.2243 | -0.36621 | -0.33875 | 0.1236 | 8.3725 | 60.8047 | -61.9995 | 60.4935 | -61.7065 | 8.7112
1725.7656 | 123.024 | -60.8139 | 61.9308 | -0.063215 | 0.049001 | 0.048411 | -0.0029196 | -0.0010885 | 0.00032545 | -0.00042733 | -52.5055 | 61.9308 | -61.1893 | 0.027466 | 0.054932 | 0.050354 | -0.073242 | 0.24261 | 0.20142 | -0.28381 | -0.37537 | 0 | 8.3084 | 60.8414 | -61.8759 | 60.5301 | -61.7294 | 8.6838
1726.7344 | 122.9416 | -60.8505 | 61.94 | 0.058855 | 0.052419 | 0.051615 | 0.010325 | -2.0324e-05 | -0.0024516 | -0.0023499 | -52.4277 | 62.0728 | -61.1526 | -0.004578 | -0.027466 | -0.045776 | 0.022888 | 0.16022 | 0.2243 | -0.32959 | -0.30212 | 0.13275 | 8.4229 | 60.8459 | -61.9675 | 60.5209 | -61.7157 | 8.725
1727.7656 | 122.9919 | -60.8047 | 61.9354 | -0.2158 | 0.049428 | 0.047129 | 0.0015666 | -0.0010885 | 0.00096645 | 0.00042727 | -52.5513 | 62.0041 | -61.1847 | 0.073242 | 0.073242 | 0.086975 | 0.086975 | 0.30212 | 0.27924 | -0.21973 | -0.37994 | 0.068664 | 8.2535 | 60.878 | -61.8622 | 60.585 | -61.6562 | 8.6334
1728.7344 | 122.9324 | -60.8459 | 61.9537 | 0.1733 | 0.051778 | 0.052897 | 0.0073344 | 0.0016887 | -0.00095615 | -0.0032043 | -52.5558 | 62.0773 | -61.1893 | -0.050354 | -0.082397 | -0.11902 | 0.004578 | 0.064087 | 0.23804 | -0.37994 | -0.34332 | 0.1236 | 8.2901 | 60.7956 | -62.0361 | 60.466 | -61.7157 | 8.6334
1729.7656 | 123.024 | -60.8093 | 61.9308 | -0.20817 | 0.047719 | 0.048197 | 7.12e-05 | 0.0025431 | -0.00010175 | -0.00085453 | -52.5375 | 61.9812 | -61.1664 | 0.07782 | 0.10529 | 0.12817 | 0.041199 | 0.33875 | 0.24261 | -0.20599 | -0.35706 | 0.050354 | 8.2718 | 60.8871 | -61.8256 | 60.6033 | -61.6882 | 8.6288
1730.7344 | 122.937 | -60.8597 | 61.9629 | 0.2267 | 0.053914 | 0.051829 | 0.009257 | 0.0076701 | -0.00010175 | -0.0021361 | -52.6016 | 62.0636 | -61.2122 | -0.041199 | -0.073242 | -0.10529 | -0.013733 | 0.10071 | 0.21515 | -0.34332 | -0.35248 | 0.10071 | 8.2581 | 60.8185 | -62.0361 | 60.5164 | -61.7477 | 8.6105
1731.75 | 123.0286 | -60.8139 | 61.9125 | 0.20381 | 0.049642 | 0.046702 | -0.0001424 | -0.00023392 | -0.00031535 | -0.0017089 | -52.6108 | 61.9492 | -61.203 | 0.018311 | 0.018311 | 0.009155 | -0.12817 | 0.20142 | 0.17395 | -0.32501 | -0.3891 | 0.036621 | 8.2031 | 60.8322 | -61.8942 | 60.4889 | -61.7386 | 8.5922
1732.7344 | 122.9416 | -60.8414 | 61.9629 | 0.058855 | 0.052633 | 0.051829 | 0.009257 | 0.0019023 | -0.00031535 | -0.0012817 | -52.6108 | 62.0636 | -61.1755 | -0.018311 | -0.041199 | -0.059509 | 0.022888 | 0.14648 | 0.20599 | -0.32501 | -0.33417 | 0.10071 | 8.2306 | 60.8231 | -62.0041 | 60.5164 | -61.7569 | 8.5648
1733.7656 | 123.0286 | -60.7956 | 61.9354 | 0.089373 | 0.047719 | 0.046702 | -0.0044148 | -0.0010885 | -0.00074255 | -0.0012817 | -52.7298 | 61.9537 | -61.1618 | 0.022888 | 0.045776 | 0.050354 | -0.068665 | 0.24719 | 0.20599 | -0.28381 | -0.36621 | 0.01831 | 8.0658 | 60.8185 | -61.8896 | 60.5118 | -61.7294 | 8.432
1734.7344 | 122.9141 | -60.8551 | 61.9308 | 0.089373 | 0.054128 | 0.049266 | 0.0096842 | 0.0014751 | 0.00075285 | -0.0032043 | -52.7023 | 62.0911 | -61.1984 | -0.073242 | -0.07782 | -0.091553 | 0.027466 | 0.082397 | 0.21973 | -0.37079 | -0.34332 | 0.16022 | 8.1528 | 60.7819 | -62.0087 | 60.4843 | -61.7111 | 8.4961
1735.75 | 123.0423 | -60.8002 | 61.9125 | 0.24196 | 0.049856 | 0.044566 | 0.00413 | 0.00019328 | 0.00096645 | -0.0019225 | -52.6703 | 61.9354 | -61.1755 | 0.027466 | 0.041199 | 0.022888 | -0.18768 | 0.22888 | 0.17395 | -0.36621 | -0.37537 | 0.022888 | 8.1299 | 60.8276 | -61.8713 | 60.434 | -61.7386 | 8.5052
1736.7344 | 122.9324 | -60.8643 | 61.9583 | 0.21907 | 0.051992 | 0.050547 | 0.0077616 | 0.0023295 | 0.00096645 | -0.0025635 | -52.739 | 62.0682 | -61.203 | -0.059509 | -0.068665 | -0.054932 | -0.027466 | 0.07782 | 0.21515 | -0.33417 | -0.33875 | 0.10986 | 8.1253 | 60.8047 | -62.027 | 60.5301 | -61.7432 | 8.4641
1737.7656 | 122.9919 | -60.8185 | 61.9354 | 0.066485 | 0.04836 | 0.046488 | -0.0031332 | -2.0324e-05 | 0.00053925 | -0.00064093 | -52.7298 | 61.9583 | -61.171 | 0.018311 | 0.059509 | 0.050354 | -0.059509 | 0.26093 | 0.21973 | -0.30212 | -0.35248 | 0.022888 | 8.0887 | 60.8368 | -61.8759 | 60.5164 | -61.7157 | 8.4412
1738.7344 | 122.9462 | -60.8643 | 61.9812 | 0.24196 | 0.052846 | 0.050334 | 0.009257 | -0.00023392 | 0.00032545 | 0.0014953 | -52.7573 | 62.059 | -61.203 | -0.059509 | -0.07782 | -0.10071 | -0.013733 | 0.10529 | 0.2243 | -0.36163 | -0.33875 | 0.07782 | 8.107 | 60.8047 | -62.059 | 60.5026 | -61.7569 | 8.4457
1739.7656 | 122.9416 | -60.8414 | 61.9583 | -0.18529 | 0.05071 | 0.04777 | 0.003062 | -2.0324e-05 | 0.00075285 | -0.00021353 | -52.7298 | 62.059 | -61.1984 | 0.013733 | 0.018311 | 0.022888 | 0.14191 | 0.23804 | 0.27466 | -0.18768 | -0.35706 | 0.10071 | 8.1116 | 60.8551 | -61.94 | 60.6537 | -61.6837 | 8.4686
1740.7344 | 122.9462 | -60.8414 | 61.9766 | 0.035967 | 0.05306 | 0.047984 | 0.0081888 | 0.0016887 | 0.00011185 | 0.00042727 | -52.6978 | 62.0682 | -61.1893 | -0.032043 | -0.050354 | -0.054932 | 0.022888 | 0.13733 | 0.22888 | -0.33875 | -0.3479 | 0.091552 | 8.1436 | 60.8093 | -62.027 | 60.5026 | -61.7477 | 8.4915
1741.7656 | 123.0423 | -60.7956 | 61.9354 | -0.10899 | 0.04836 | 0.044139 | -0.0016378 | 0.0012615 | -0.0011698 | -0.00042733 | -52.6978 | 61.9583 | -61.1618 | 0.10071 | 0.13275 | 0.14648 | 0 | 0.37537 | 0.25635 | -0.21515 | -0.36621 | 0.022888 | 8.0978 | 60.8963 | -61.8027 | 60.5804 | -61.6791 | 8.464
1742.7344 | 122.9416 | -60.8322 | 61.9263 | 0.035967 | 0.050283 | 0.048411 | 0.0088298 | 0.0029705 | -0.00095615 | -0.0012817 | -52.7069 | 62.0682 | -61.1801 | 0.009155 | -0.018311 | -0.022888 | 0.022888 | 0.17853 | 0.23346 | -0.31586 | -0.3479 | 0.14191 | 8.1253 | 60.8414 | -61.9446 | 60.5164 | -61.6928 | 8.4732
1743.7344 | 122.9462 | -60.8459 | 61.9537 | 0.097002 | 0.051778 | 0.049266 | 0.0069072 | 0.0025431 | -0.00031535 | -0.0017089 | -52.7527 | 62.0819 | -61.1984 | -0.027466 | -0.045776 | -0.064087 | 0.027466 | 0.1236 | 0.22888 | -0.32959 | -0.35248 | 0.12817 | 8.0933 | 60.8185 | -61.9995 | 60.5164 | -61.7249 | 8.4457
1744.7656 | 123.0515 | -60.8093 | 61.9308 | -0.025068 | 0.045583 | 0.045634 | -0.0074056 | 0.00062048 | 0.00032545 | -0.00042733 | -52.771 | 61.9446 | -61.1984 | 0.073242 | 0.091553 | 0.10529 | -0.073242 | 0.32959 | 0.23346 | -0.25177 | -0.3891 | 0.013733 | 8.0383 | 60.8826 | -61.8393 | 60.5576 | -61.6974 | 8.4274
1745.7344 | 122.9736 | -60.8459 | 61.9537 | -0.017439 | 0.05306 | 0.050761 | 0.009257 | 0.0025431 | -0.002238 | -0.0034179 | -52.6794 | 62.0453 | -61.171 | 0.050354 | 0.013733 | 0.022888 | 0.022888 | 0.22888 | 0.24719 | -0.29297 | -0.32501 | 0.091553 | 8.1665 | 60.8963 | -61.94 | 60.553 | -61.7065 | 8.4915
1746.7656 | 122.9462 | -60.8597 | 61.972 | -0.36839 | 0.049642 | 0.045634 | 0.0039164 | 0.0010477 | -0.0013834 | -0.0025635 | -52.7847 | 62.0087 | -61.1938 | 0.004578 | 0.050354 | 0.050354 | 0.14648 | 0.25635 | 0.30212 | -0.19226 | -0.33417 | 0.036621 | 8.075 | 60.8643 | -61.9217 | 60.6674 | -61.6699 | 8.4091
1747.7344 | 122.937 | -60.8505 | 61.9583 | 0.058855 | 0.051565 | 0.049479 | 0.0081888 | 0.0040385 | 0.00053925 | 0.0010681 | -52.6886 | 62.0728 | -61.1755 | 0.018311 | 0.022888 | -0.018311 | 0.004578 | 0.1831 | 0.25635 | -0.30212 | -0.32501 | 0.11444 | 8.1619 | 60.8688 | -61.9354 | 60.5484 | -61.702 | 8.4869
1748.7656 | 123.0652 | -60.8185 | 61.9217 | -0.13951 | 0.044729 | 0.052897 | -0.0014242 | 0.0014751 | 0.00011185 | 0.00085447 | -52.739 | 61.9308 | -61.1755 | 0.10986 | 0.14648 | 0.16022 | 0.009155 | 0.36621 | 0.23804 | -0.2243 | -0.35706 | 0.009155 | 8.0795 | 60.9283 | -61.7752 | 60.5942 | -61.6837 | 8.4366
1749.7344 | 122.9736 | -60.8597 | 61.9217 | 0.028338 | 0.051992 | 0.049479 | 0.007548 | 0.0027567 | -0.00074255 | -0.0034179 | -52.7344 | 62.059 | -61.1572 | 0.041199 | 0.018311 | 0.032043 | 0.022888 | 0.21057 | 0.25177 | -0.27924 | -0.29755 | 0.13733 | 8.1253 | 60.9009 | -61.9034 | 60.5804 | -61.6699 | 8.4229
1750.7656 | 123.0606 | -60.7773 | 61.9034 | 0.26485 | 0.05071 | 0.04777 | 0.0037028 | 0.0057475 | 0.00011185 | -0.00085453 | -52.7435 | 61.9263 | -61.1984 | 0.036621 | 0.050354 | 0.027466 | -0.19684 | 0.21515 | 0.17853 | -0.36621 | -0.42114 | 0.022889 | 8.0338 | 60.8139 | -61.853 | 60.4111 | -61.7249 | 8.4549
1751.7344 | 122.9553 | -60.8368 | 61.9446 | 0.020708 | 0.054128 | 0.044352 | 0.0069072 | 0.0012615 | 0.00075285 | -0.00042733 | -52.7023 | 62.0728 | -61.1572 | 0 | -0.018311 | -0.027466 | 0.004578 | 0.15564 | 0.23346 | -0.32501 | -0.32043 | 0.12817 | 8.1345 | 60.8368 | -61.9629 | 60.5118 | -61.7111 | 8.4549
1752.7656 | 123.0331 | -60.7773 | 61.9217 | 0.097002 | 0.050069 | 0.046702 | -0.0035604 | 0.0031841 | -0.00052895 | 0.0012817 | -52.8214 | 61.9629 | -61.171 | 0.027466 | 0.064087 | 0.082397 | -0.050354 | 0.29297 | 0.21057 | -0.27924 | -0.39368 | 0.041199 | 7.9559 | 60.8047 | -61.8576 | 60.498 | -61.7111 | 8.3496
1753.7344 | 123.0011 | -60.8093 | 61.9537 | -0.10899 | 0.050496 | 0.046061 | 0.0084026 | 0.0025431 | -0.00095615 | -0.0027771 | -52.7298 | 62.0865 | -61.1801 | 0.041199 | 0.018311 | 0.036621 | 0.018311 | 0.23346 | 0.24261 | -0.29755 | -0.37079 | 0.13275 | 8.0795 | 60.8505 | -61.9354 | 60.5118 | -61.7111 | 8.4503
1754.75 | 123.0377 | -60.8093 | 61.9125 | 0.19618 | 0.050069 | 0.045848 | -0.0022786 | 0.00019328 | -0.00074255 | -0.0014953 | -52.8122 | 61.9583 | -61.171 | 0 | 0.027466 | 0.018311 | -0.13733 | 0.20142 | 0.20599 | -0.31586 | -0.36163 | 0.045776 | 7.9971 | 60.8093 | -61.8851 | 60.4935 | -61.7065 | 8.3588
1755.7344 | 123.0011 | -60.8276 | 61.9675 | -0.040327 | 0.05071 | 0.050761 | 0.007548 | 0.0033977 | -0.00031535 | -0.00064093 | -52.7344 | 62.0636 | -61.1572 | 0.032043 | 0.022888 | 0.032043 | 0.022888 | 0.2243 | 0.24261 | -0.27924 | -0.32959 | 0.096131 | 8.0933 | 60.8597 | -61.9446 | 60.5484 | -61.7249 | 8.4229
1756.7656 | 123.0469 | -60.8093 | 61.8851 | 0.23433 | 0.049428 | 0.046275 | 0.001353 | 0.0019023 | -0.0011698 | -0.0010681 | -52.771 | 61.9171 | -61.1847 | 0.050354 | 0.045776 | 0.050354 | -0.1831 | 0.21515 | 0.1831 | -0.36163 | -0.37537 | 0.032043 | 8.0383 | 60.8597 | -61.8393 | 60.4477 | -61.702 | 8.4137
1757.7344 | 122.9462 | -60.8368 | 61.94 | 0.020708 | 0.05306 | 0.051615 | 0.0077616 | 0.0036113 | -0.003947 | -0.0017089 | -52.7527 | 62.059 | -61.171 | 0.004578 | -0.018311 | -0.022888 | 0.022888 | 0.17395 | 0.23346 | -0.31586 | -0.33417 | 0.11902 | 8.0841 | 60.8414 | -61.9583 | 60.5209 | -61.7065 | 8.4183
1758.7656 | 123.0377 | -60.8002 | 61.908 | 0.24959 | 0.050069 | 0.048197 | 0.0043436 | 0.00083408 | 0.00053925 | -0.0019225 | -52.7527 | 61.9446 | -61.1984 | 0.041199 | 0.045776 | 0.027466 | -0.17853 | 0.23346 | 0.16937 | -0.3479 | -0.39825 | 0.036621 | 8.0475 | 60.8414 | -61.8622 | 60.4523 | -61.7386 | 8.4457
1759.7344 | 123.0057 | -60.8002 | 61.9492 | -0.032697 | 0.05306 | 0.048411 | 0.005839 | 0.0025431 | 0.00053925 | -0.0014953 | -52.7298 | 62.0636 | -61.1801 | 0.045776 | 0.027466 | 0.018311 | 0.018311 | 0.24261 | 0.23804 | -0.27466 | -0.37994 | 0.11444 | 8.0704 | 60.8459 | -61.9217 | 60.5255 | -61.7111 | 8.4503
1760.7656 | 123.0377 | -60.8231 | 61.9308 | 0.081743 | 0.049428 | 0.04542 | -0.0039876 | 0.00062048 | -0.0026652 | -0.0017089 | -52.858 | 61.9492 | -61.1938 | 0.013733 | 0.032043 | 0.045776 | -0.07782 | 0.23804 | 0.19684 | -0.28381 | -0.37079 | 0.018311 | 7.9651 | 60.8368 | -61.8988 | 60.5392 | -61.734 | 8.3359
1761.7344 | 122.9782 | -60.8231 | 61.9766 | 0.058855 | 0.053914 | 0.045848 | 0.0081888 | 0.0051067 | 0.0016072 | -0.0019225 | -52.7206 | 62.0636 | -61.171 | 0.045776 | 0.013733 | 0.027466 | 0.013733 | 0.21973 | 0.23346 | -0.28381 | -0.3479 | 0.086975 | 8.1024 | 60.8688 | -61.9629 | 60.5392 | -61.7432 | 8.4503
1762.7656 | 123.0698 | -60.791 | 61.9492 | -0.11662 | 0.046651 | 0.04307 | -0.0046284 | -0.00066112 | -0.0013834 | -0.00064093 | -52.7435 | 61.9492 | -61.1572 | 0.14191 | 0.16022 | 0.1831 | -0.07782 | 0.37994 | 0.23804 | -0.20599 | -0.36621 | 0 | 8.0475 | 60.9329 | -61.7889 | 60.585 | -61.7111 | 8.4137
1763.7344 | 122.9507 | -60.8322 | 61.9675 | 0.089373 | 0.05071 | 0.048838 | 0.0090434 | 0.0040385 | -0.00074255 | -0.0019225 | -52.7161 | 62.0544 | -61.1618 | -0.009155 | -0.032043 | -0.041199 | 0.013733 | 0.16479 | 0.23346 | -0.32959 | -0.32959 | 0.086975 | 8.1161 | 60.8231 | -61.9995 | 60.5026 | -61.734 | 8.4457
1764.7656 | 122.9324 | -60.8276 | 61.9766 | -0.15477 | 0.05071 | 0.051188 | 0.0043436 | 0.0036113 | -0.0011698 | -0.0019225 | -52.8076 | 62.0636 | -61.2122 | 0.032043 | 0.032043 | 0.036621 | 0.14648 | 0.24261 | 0.28839 | -0.19684 | -0.38452 | 0.086975 | 8.02 | 60.8597 | -61.9446 | 60.6308 | -61.6882 | 8.4045
1765.7344 | 122.9736 | -60.8368 | 61.9492 | 0.028338 | 0.053487 | 0.050334 | 0.0062662 | 0.0053203 | 0.00011185 | -0.0029907 | -52.6886 | 62.0682 | -61.2122 | 0.004578 | -0.022888 | -0.022888 | 0.018311 | 0.1831 | 0.26093 | -0.32044 | -0.37537 | 0.11902 | 8.1482 | 60.8414 | -61.972 | 60.5164 | -61.6882 | 8.5236
1766.7656 | 123.0606 | -60.8047 | 61.9217 | 0.043596 | 0.04601 | 0.047129 | -0.0063374 | 0.0016887 | -0.0037334 | -0.00085453 | -52.7481 | 61.94 | -61.1893 | 0.059509 | 0.082397 | 0.086975 | -0.050354 | 0.30212 | 0.20599 | -0.2655 | -0.38452 | 0.01831 | 8.0566 | 60.8643 | -61.8393 | 60.5392 | -61.7157 | 8.4412
1767.7344 | 122.9919 | -60.8139 | 61.9446 | -0.025068 | 0.049215 | 0.044779 | 0.0062662 | 0.0038249 | 0.00011185 | -0.00085453 | -52.6611 | 62.0773 | -61.1755 | 0.041199 | 0.036621 | 0.036621 | 0.009155 | 0.25177 | 0.24719 | -0.28381 | -0.36163 | 0.13275 | 8.1528 | 60.8551 | -61.908 | 60.5301 | -61.6974 | 8.5144
1768.7656 | 122.9691 | -60.8459 | 61.9583 | -0.078474 | 0.051137 | 0.051615 | 0.0066936 | 0.0023295 | -0.0015972 | -0.0029907 | -52.6886 | 62.0728 | -61.1755 | 0.059509 | 0.036621 | 0.041199 | 0.022888 | 0.24261 | 0.25177 | -0.26093 | -0.32959 | 0.11444 | 8.1573 | 60.9055 | -61.9217 | 60.585 | -61.7065 | 8.4869
1769.7344 | 122.9599 | -60.8185 | 61.9217 | -0.0021797 | 0.051992 | 0.052897 | 0.00648 | 0.0046793 | -0.00095615 | -0.0040589 | -52.7069 | 62.0499 | -61.1801 | 0.036621 | 0.027466 | 0.013733 | -0.036621 | 0.17395 | 0.24261 | -0.29755 | -0.36163 | 0.12817 | 8.1116 | 60.8551 | -61.8942 | 60.5209 | -61.6791 | 8.4732
1770.7656 | 123.0652 | -60.8093 | 61.8988 | 0.2267 | 0.051137 | 0.053538 | 0.0022074 | 0.0019023 | -0.0011698 | 0.00064087 | -52.6886 | 61.972 | -61.1801 | 0.050354 | 0.054932 | 0.036621 | -0.19226 | 0.2243 | 0.16937 | -0.36621 | -0.37079 | 0.073242 | 8.1207 | 60.8597 | -61.8439 | 60.4431 | -61.7294 | 8.4915
1771.7344 | 122.9462 | -60.8459 | 61.94 | 0.058855 | 0.050283 | 0.05012 | 0.0056254 | 0.0040385 | -0.00095615 | -0.0017089 | -52.6749 | 62.0819 | -61.203 | -0.009155 | -0.032043 | -0.018311 | 0.045776 | 0.15564 | 0.2243 | -0.31128 | -0.35706 | 0.14191 | 8.1711 | 60.8368 | -61.972 | 60.5347 | -61.7157 | 8.5281
1772.7656 | 122.9828 | -60.8368 | 61.9766 | -0.39128 | 0.049428 | 0.048197 | -0.0007832 | 0.0014751 | -0.00031535 | -0.0010681 | -52.6611 | 62.0132 | -61.1755 | 0.054932 | 0.068665 | 0.068665 | 0.082397 | 0.29755 | 0.27008 | -0.24261 | -0.33874 | 0.036621 | 8.1757 | 60.8917 | -61.908 | 60.5942 | -61.7065 | 8.5144
1773.75 | 123.056 | -60.7956 | 61.9308 | 0.043596 | 0.047292 | 0.044779 | -0.0009968 | 0.00040688 | -0.0013834 | -0.0025635 | -52.7069 | 61.9354 | -61.1801 | 0.054932 | 0.091553 | 0.10071 | 0.1236 | 0.48981 | 0.23346 | -0.23346 | -0.38452 | 0.004578 | 8.0887 | 60.8505 | -61.8393 | 60.5621 | -61.6974 | 8.4732
1774.7656 | 122.9416 | -60.8276 | 61.972 | -0.20817 | 0.050069 | 0.046916 | 0.0034892 | -0.0010885 | -0.0020244 | -0.0017089 | -52.7756 | 62.0407 | -61.1984 | 0.004578 | 0.009155 | 0.036621 | 0.15106 | 0.25177 | 0.28381 | -0.20599 | -0.37079 | 0.068664 | 8.0521 | 60.8322 | -61.9629 | 60.6216 | -61.6882 | 8.4229
1775.7344 | 122.9645 | -60.8414 | 61.9446 | -0.26921 | 0.052419 | 0.049693 | 0.009257 | 0.0023295 | -0.0015972 | -0.0017089 | -52.6749 | 62.0636 | -61.1847 | -0.018311 | -0.036621 | -0.022888 | 0.022888 | 0.16022 | 0.24719 | -0.31128 | -0.34332 | 0.11902 | 8.1665 | 60.8231 | -61.9812 | 60.5301 | -61.6974 | 8.5098
1776.7656 | 123.0515 | -60.7819 | 61.9354 | -0.14714 | 0.045797 | 0.042857 | -0.0018514 | 0.0012615 | 0.00011185 | -0.00085453 | -52.652 | 61.9629 | -61.1893 | 0.10529 | 0.10071 | 0.14191 | -0.018311 | 0.35248 | 0.24261 | -0.21515 | -0.40741 | 0.027466 | 8.1299 | 60.8871 | -61.8347 | 60.5667 | -61.6928 | 8.5373
1777.7344 | 122.9553 | -60.8414 | 61.94 | -0.093733 | 0.053701 | 0.052683 | 0.0096842 | 0.0038249 | -0.0018108 | 0.00042727 | -52.6611 | 62.0499 | -61.1984 | 0.013733 | -0.027466 | -0.041199 | 0.018311 | 0.15564 | 0.23346 | -0.32044 | -0.35706 | 0.10986 | 8.1802 | 60.8551 | -61.9675 | 60.5209 | -61.7065 | 8.5373
1778.7656 | 122.9645 | -60.8139 | 61.94 | -0.0021797 | 0.052419 | 0.052256 | 0.0060526 | 0.0033977 | -0.0011698 | -0.0025635 | -52.6382 | 62.0636 | -61.2122 | 0.036621 | 0.027466 | 0.036621 | 0.027466 | 0.23346 | 0.26093 | -0.27924 | -0.39825 | 0.1236 | 8.1757 | 60.8505 | -61.9125 | 60.5347 | -61.6791 | 8.5739
1779.7344 | 122.9233 | -60.8643 | 61.9675 | 0.089373 | 0.051565 | 0.05717 | 0.00648 | 0.0046793 | -0.0020244 | -0.0012817 | -52.7206 | 62.0728 | -61.1893 | -0.07782 | -0.082397 | -0.1236 | 0.022888 | 0.068665 | 0.2243 | -0.36163 | -0.32501 | 0.10529 | 8.1436 | 60.7864 | -62.0499 | 60.5026 | -61.7432 | 8.4686
1780.7656 | 123.0011 | -60.8276 | 61.9583 | -0.17766 | 0.048574 | 0.049479 | -0.0005696 | 0.0027567 | -0.00031535 | 0.00042727 | -52.6794 | 61.9858 | -61.1618 | 0.064087 | 0.086975 | 0.10529 | 0.068665 | 0.29755 | 0.27008 | -0.21057 | -0.33417 | 0.027466 | 8.1482 | 60.8917 | -61.8713 | 60.6171 | -61.6882 | 8.4824
1781.7344 | 122.937 | -60.8414 | 61.9583 | 0.058855 | 0.052205 | 0.046916 | 0.0054118 | 0.0044657 | -0.0018108 | -0.0010681 | -52.6428 | 62.0682 | -61.1572 | -0.004578 | -0.027466 | -0.027466 | 0.032043 | 0.16937 | 0.24719 | -0.32501 | -0.31586 | 0.10986 | 8.1985 | 60.8368 | -61.9858 | 60.5164 | -61.7111 | 8.5144
1782.7656 | 122.9782 | -60.8047 | 61.972 | -0.17766 | 0.047078 | 0.045848 | -0.0007832 | 0.0012615 | 0.00053925 | -0.00021353 | -52.739 | 61.9995 | -61.1755 | 0.064087 | 0.073242 | 0.10529 | 0.09613 | 0.30212 | 0.27008 | -0.22888 | -0.37079 | 0.027466 | 8.0658 | 60.8688 | -61.8988 | 60.5759 | -61.702 | 8.4366
1783.7344 | 122.9141 | -60.8643 | 61.9354 | 0.15041 | 0.053914 | 0.048838 | 0.00648 | 0.0053203 | -0.00031535 | -0.0017089 | -52.7435 | 62.0453 | -61.203 | -0.064087 | -0.07782 | -0.1236 | -0.018311 | 0.10986 | 0.2243 | -0.36163 | -0.33875 | 0.10986 | 8.1207 | 60.8002 | -62.0132 | 60.5026 | -61.7111 | 8.4595
1784.75 | 123.0377 | -60.8139 | 61.9034 | -0.070844 | 0.049428 | 0.052256 | -0.000356 | 0.0016887 | 0.0016072 | 0.00042727 | -52.7573 | 61.9446 | -61.1938 | 0.027466 | 0.050354 | 0.036621 | -0.15106 | 0.23346 | 0.17853 | -0.33417 | -0.37994 | 0.041199 | 8.0566 | 60.8414 | -61.853 | 60.4797 | -61.7249 | 8.4366
1785.7344 | 122.9416 | -60.8414 | 61.9583 | 0.19618 | 0.051778 | 0.051829 | 0.0077616 | 0.0040385 | 0.00011185 | -0.00064093 | -52.6474 | 62.0453 | -61.1893 | -0.25177 | 0.24261 | 0.44861 | -0.09613 | 0.073242 | 0.20142 | -0.36621 | -0.3479 | 0.086975 | 8.194 | 60.5896 | -61.7157 | 60.4752 | -61.7569 | 8.5419
1786.7656 | 123.0469 | -60.8093 | 61.8988 | 0.074114 | 0.049215 | 0.05247 | -0.0042012 | 0.0014751 | -0.0013834 | -0.0014953 | -52.6382 | 61.9675 | -61.203 | 0.027466 | 0.032043 | 0.032043 | -0.068665 | 0.24719 | 0.20599 | -0.27924 | -0.39368 | 0.068664 | 8.1711 | 60.8368 | -61.8668 | 60.5301 | -61.6928 | 8.5648
1787.7344 | 122.9095 | -60.8505 | 61.9675 | 0.13515 | 0.054769 | 0.048197 | 0.0098978 | 0.0023295 | -0.0015972 | -0.0017089 | -52.6199 | 62.0773 | -61.171 | -0.064087 | -0.073242 | -0.086975 | 0.009155 | 0.10529 | 0.23346 | -0.37537 | -0.32043 | 0.10986 | 8.2306 | 60.7864 | -62.0407 | 60.4752 | -61.734 | 8.551
1788.7656 | 123.0881 | -60.7773 | 61.9034 | -0.047956 | 0.050283 | 0.046061 | -0.0031332 | 0.00019328 | -0.0024516 | 0.00042727 | -52.4963 | 61.9537 | -61.1847 | 0.086975 | 0.14191 | 0.14191 | -0.086975 | 0.36621 | 0.23804 | -0.20142 | -0.40741 | 0.050354 | 8.2809 | 60.8643 | -61.7615 | 60.5759 | -61.6653 | 8.6884
1789.7344 | 122.9507 | -60.8414 | 61.9537 | 0.051226 | 0.054555 | 0.05247 | 0.0096842 | 0.0029705 | -0.0011698 | -0.0014953 | -52.739 | 62.0453 | -61.1893 | -0.036621 | -0.064087 | -0.09613 | 0.013733 | 0.11902 | 0.23804 | -0.35706 | -0.3479 | 0.091553 | 8.1024 | 60.8047 | -62.0178 | 60.4843 | -61.7157 | 8.4503
1790.7656 | 123.0286 | -60.7681 | 61.94 | -0.070844 | 0.04601 | 0.045207 | -0.0005696 | 0.0016887 | -0.0030924 | -0.0023499 | -52.8259 | 61.9675 | -61.171 | 0.086975 | 0.11902 | 0.13733 | 0.041199 | 0.36621 | 0.24719 | -0.21057 | -0.40283 | 0.027466 | 7.9422 | 60.8551 | -61.821 | 60.5576 | -61.6928 | 8.345
1791.7344 | 122.9736 | -60.8459 | 61.9354 | 0.15804 | 0.051778 | 0.051402 | 0.0071208 | 0.0036113 | -0.00074255 | 0.0012817 | -52.5879 | 62.0453 | -61.2122 | -0.036621 | -0.054932 | -0.07782 | -0.064087 | 0.10071 | 0.21515 | -0.36163 | -0.36621 | 0.10986 | 8.2581 | 60.8093 | -61.9904 | 60.4843 | -61.7203 | 8.6243
1792.7656 | 123.0743 | -60.8002 | 61.9446 | 0.043596 | 0.04601 | 0.052043 | -0.0007832 | 0.00019328 | -0.0015972 | 0.00064087 | -52.5879 | 61.94 | -61.1664 | 0.07782 | 0.10986 | 0.1236 | -0.082397 | 0.31586 | 0.21973 | -0.25635 | -0.36621 | -0.004578 | 8.2123 | 60.878 | -61.8347 | 60.5438 | -61.7249 | 8.5785
1793.7344 | 122.9507 | -60.8551 | 61.9354 | 0.4861 | 0.053701 | 0.048838 | 0.0071208 | 0.0029705 | -0.00010175 | -0.0023499 | -52.5467 | 62.0499 | -61.1847 | -0.050354 | -0.064087 | -0.082397 | -0.032043 | 0.1236 | 0.21057 | -0.34332 | -0.32959 | 0.11444 | 8.3084 | 60.8047 | -61.9995 | 60.5118 | -61.7249 | 8.638
1794.7656 | 123.0423 | -60.7636 | 61.9354 | -0.78801 | 0.04601 | 0.04542 | 0.0026346 | -0.0015157 | -0.002238 | -0.00021353 | -52.8442 | 61.9308 | -61.1572 | 0.09613 | 0.10529 | 0.16937 | -0.018311 | 0.36163 | 0.23804 | -0.24719 | -0.39368 | -0.004578 | 7.9193 | 60.8597 | -61.8301 | 60.5164 | -61.6974 | 8.313
1795.7344 | 122.9279 | -60.8459 | 61.9492 | 0.13515 | 0.052846 | 0.05482 | 0.0084026 | 0.0031841 | -0.0030924 | -0.0023499 | -52.7344 | 62.0682 | -61.1664 | -0.027466 | -0.082397 | -0.10071 | 0.013733 | 0.11902 | 0.23346 | -0.36621 | -0.32043 | 0.11902 | 8.1116 | 60.8185 | -62.0316 | 60.4797 | -61.7157 | 8.432
1796.7656 | 123.0698 | -60.7956 | 61.9125 | -0.025068 | 0.047292 | 0.047557 | -0.0029196 | -0.00066112 | -0.00052895 | -0.0017089 | -52.5284 | 61.9171 | -61.1801 | 0.09613 | 0.1236 | 0.13733 | -0.082397 | 0.33417 | 0.20599 | -0.23346 | -0.38452 | 0.004577 | 8.2672 | 60.8917 | -61.7889 | 60.5621 | -61.7065 | 8.6517
1797.7344 | 122.9324 | -60.8459 | 61.9583 | 0.2267 | 0.053701 | 0.050975 | 0.0079752 | 0.0029705 | 0.0035298 | 0.0038453 | -52.6337 | 62.0728 | -61.1938 | -0.48065 | -0.23804 | 0.64087 | 0.32044 | -0.013733 | 0.20142 | -0.3891 | -0.3479 | 0.11444 | 8.2123 | 60.3653 | -62.1963 | 60.4568 | -61.7569 | 8.5602
1798.7656 | 123.0743 | -60.7681 | 61.9171 | -0.0021797 | 0.049642 | 0.047984 | -0.0035604 | -0.0010885 | -0.00052895 | -0.00021353 | -52.6794 | 61.9492 | -61.1801 | 0.082397 | 0.086975 | 0.10986 | -0.068665 | 0.35706 | 0.2243 | -0.25177 | -0.41199 | 0.032044 | 8.0887 | 60.8505 | -61.8301 | 60.5164 | -61.6928 | 8.5007
1799.7344 | 122.9462 | -60.8185 | 61.9629 | 0.13515 | 0.051778 | 0.049266 | 0.0077616 | 0.0021159 | -0.00095615 | -0.00085453 | -52.6337 | 62.0544 | -61.171 | -0.032043 | -0.059509 | -0.086975 | -0.041199 | 0.10529 | 0.2243 | -0.35248 | -0.35248 | 0.091552 | 8.1848 | 60.7864 | -62.0224 | 60.466 | -61.7386 | 8.5373
1800.7656 | 122.9691 | -60.8231 | 61.9904 | -0.17003 | 0.050283 | 0.046061 | 0.0022074 | 0.0012615 | 0.00011185 | -0.0012817 | -52.6474 | 62.0041 | -61.1984 | 0.022888 | 0.022888 | 0.041199 | 0.15106 | 0.25177 | 0.29755 | -0.19684 | -0.37537 | 0.013733 | 8.1757 | 60.8459 | -61.9675 | 60.6262 | -61.6928 | 8.551
1801.7344 | 122.9233 | -60.8322 | 61.9354 | 0.11989 | 0.05071 | 0.049693 | 0.009257 | 0.0040385 | -0.002238 | -0.00064093 | -52.4826 | 62.059 | -61.203 | -0.036621 | -0.064087 | -0.091553 | 0.013733 | 0.09613 | 0.2243 | -0.35706 | -0.37079 | 0.1236 | 8.3496 | 60.7956 | -61.9995 | 60.4752 | -61.7111 | 8.7204
1802.7656 | 123.0743 | -60.7727 | 61.9217 | -0.040327 | 0.047506 | 0.04542 | -0.0029196 | -2.0324e-05 | -0.0020244 | -0.0014953 | -52.7756 | 61.9354 | -61.1938 | 0.082397 | 0.10529 | 0.1236 | -0.041199 | 0.35248 | 0.21057 | -0.22888 | -0.42114 | 0.013733 | 7.9971 | 60.8551 | -61.8164 | 60.5438 | -61.7111 | 8.4183
1803.7344 | 122.9233 | -60.8276 | 61.94 | 0.21144 | 0.051992 | 0.046916 | 0.0079752 | 0.0029705 | 0.0052388 | 0.00064087 | -52.6703 | 62.0407 | -61.1938 | -0.42572 | 0.068665 | 0.6546 | 0.050354 | -0.018311 | 0.20599 | -0.36621 | -0.36621 | 0.10071 | 8.1573 | 60.4019 | -61.8713 | 60.4614 | -61.734 | 8.5236
1804.7656 | 123.0194 | -60.8093 | 61.9217 | 0.15041 | 0.047506 | 0.050975 | -0.0033468 | 0.0014751 | -0.0013834 | -0.0017089 | -52.597 | 61.9354 | -61.1984 | 0.018311 | 0.027466 | 0.027466 | -0.07782 | 0.2243 | 0.19226 | -0.30212 | -0.3891 | 0.013733 | 8.2123 | 60.8276 | -61.8942 | 60.5072 | -61.7294 | 8.6014
1805.7344 | 122.9462 | -60.8505 | 61.9354 | 0.15804 | 0.053914 | 0.050334 | 0.0071208 | 0.0014751 | -0.00031535 | -0.0010681 | -52.6703 | 62.0499 | -61.1893 | -0.036621 | -0.068665 | -0.091553 | -0.032043 | 0.09613 | 0.19684 | -0.34332 | -0.33875 | 0.11444 | 8.1802 | 60.8139 | -62.0041 | 60.5072 | -61.7386 | 8.519
1806.7656 | 123.0194 | -60.7864 | 61.9034 | 0.57765 | 0.051992 | 0.044993 | -0.0024922 | 0.0010477 | -0.0018108 | -0.00085453 | -52.4231 | 61.9492 | -61.1938 | -0.004578 | 0.041199 | 0.045776 | -0.064087 | 0.26093 | 0.20142 | -0.27924 | -0.40741 | 0.045777 | 8.3633 | 60.7819 | -61.8622 | 60.5072 | -61.702 | 8.7708
1807.7344 | 122.937 | -60.8597 | 61.94 | -0.44468 | 0.05306 | 0.051615 | 0.0081888 | 0.00019328 | 0.00075285 | -0.00064093 | -52.7252 | 62.0499 | -61.1664 | -0.054932 | -0.07782 | -0.064087 | -0.032043 | 0.054932 | 0.21515 | -0.33417 | -0.3067 | 0.10986 | 8.1345 | 60.8047 | -62.0178 | 60.5255 | -61.7249 | 8.4412
1808.7656 | 122.9782 | -60.8047 | 61.9675 | -0.19291 | 0.051778 | 0.050975 | 0.0034892 | 0.00040688 | -0.00095615 | -0.0027771 | -52.7939 | 62.0178 | -61.1801 | 0.041199 | 0.036621 | 0.054932 | 0.10529 | 0.24261 | 0.27466 | -0.18768 | -0.37537 | 0.050354 | 8.0109 | 60.8459 | -61.9308 | 60.6171 | -61.6928 | 8.3862
1809.7344 | 122.9095 | -60.8414 | 61.94 | 0.28011 | 0.053487 | 0.050761 | 0.011393 | 0.0063883 | 0.0013936 | -0.0059815 | -52.597 | 62.0499 | -61.171 | 0.26093 | 0.39825 | -0.018311 | -0.086975 | 0.27008 | 0.19684 | -0.3479 | -0.32959 | 0.10986 | 8.2443 | 61.1023 | -61.5417 | 60.4935 | -61.7432 | 8.5739
1810.7656 | 123.0377 | -60.8185 | 61.9171 | 0.097002 | 0.048787 | 0.048197 | -0.0014242 | 0.0014751 | -0.00031535 | -0.00021353 | -52.8122 | 61.94 | -61.171 | 0.018311 | 0.059509 | 0.068665 | -0.064087 | 0.2655 | 0.22888 | -0.28839 | -0.35248 | 0.022888 | 8.0063 | 60.8368 | -61.8576 | 60.5301 | -61.6882 | 8.3588
1811.7344 | 122.7905 | -60.8551 | 61.8988 | 0.21144 | 0.051778 | 0.051188 | 0.0081888 | 0.0036113 | -0.00095615 | -0.0032043 | -52.5513 | 62.0682 | -61.1893 | -0.045776 | -0.059509 | -0.082397 | -0.009155 | 0.11902 | 0.21515 | -0.35706 | -0.33417 | 0.16937 | 8.3038 | 60.8093 | -61.9583 | 60.498 | -61.6837 | 8.638
1812.7656 | 123.0148 | -60.8322 | 61.9308 | 0.27248 | 0.050496 | 0.052683 | 0.0066936 | 0.0038249 | 0.00118 | 0.00064087 | -52.4963 | 62.027 | -61.235 | -0.036621 | -0.018311 | -0.045776 | -0.09613 | 0.13275 | 0.19684 | -0.3479 | -0.40283 | 0.096131 | 8.3359 | 60.7956 | -61.9492 | 60.4843 | -61.734 | 8.7387
1813.7344 | 122.9736 | -60.8414 | 61.9263 | 0.57002 | 0.053274 | 0.047129 | 0.0084026 | 0.0027567 | 0.0013936 | -0.0010681 | -52.9678 | 62.0682 | -61.2167 | -0.050354 | -0.050354 | -0.073242 | -0.022888 | 0.11444 | 0.21057 | -0.34332 | -0.37537 | 0.14191 | 7.8735 | 60.791 | -61.9766 | 60.498 | -61.7157 | 8.2489
1814.7656 | 123.0652 | -60.7773 | 61.9171 | -0.047956 | 0.046224 | 0.051829 | -0.0014242 | 0.0010477 | -0.00010175 | -0.00064093 | -52.5833 | 61.9308 | -61.1847 | 0.11444 | 0.14648 | 0.17853 | -0.064087 | 0.37537 | 0.23346 | -0.20142 | -0.40741 | 0.013733 | 8.194 | 60.8917 | -61.7706 | 60.5759 | -61.6837 | 8.6014
1815.7344 | 122.9141 | -60.8597 | 61.9583 | 0.089373 | 0.054983 | 0.049266 | 0.0090434 | 0.0021159 | -0.00074255 | -0.0027771 | -52.6337 | 62.0636 | -61.1893 | -0.054932 | -0.073242 | -0.068665 | 0.027466 | 0.10986 | 0.24261 | -0.3479 | -0.32959 | 0.10529 | 8.226 | 60.8047 | -62.0316 | 60.5118 | -61.7157 | 8.5556
1816.7656 | 122.9507 | -60.8322 | 61.9949 | -0.1624 | 0.051778 | 0.046916 | 0.0037028 | 0.0053203 | -0.0020244 | 0.00021367 | -52.8442 | 62.0361 | -61.1847 | 0.068665 | -0.032043 | -0.068665 | 0.19226 | 0.23804 | 0.27924 | -0.24719 | -0.35248 | 0.041199 | 7.988 | 60.9009 | -62.027 | 60.585 | -61.7157 | 8.3405
1817.7344 | 122.9233 | -60.8414 | 61.9354 | 0.21144 | 0.052846 | 0.050975 | 0.0081888 | 0.0051067 | -0.0011698 | -0.0029907 | -52.7115 | 62.0636 | -61.2076 | -0.050354 | -0.054932 | -0.091553 | -0.004578 | 0.10529 | 0.2243 | -0.33417 | -0.36621 | 0.12817 | 8.1299 | 60.791 | -61.9904 | 60.5072 | -61.7111 | 8.4961
1818.7656 | 123.0194 | -60.8047 | 61.9034 | 0.21144 | 0.048574 | 0.04307 | -0.0024922 | 0.0016887 | 0.00053925 | -0.00064093 | -52.7206 | 61.9308 | -61.1801 | 0.018311 | 0.041199 | 0.032043 | -0.086975 | 0.23804 | 0.18768 | -0.27924 | -0.37537 | 0.027466 | 8.0841 | 60.8231 | -61.8622 | 60.5255 | -61.7157 | 8.4595
1819.7344 | 122.9233 | -60.8551 | 61.9217 | 1.7144 | 0.054769 | 0.052683 | 0.0073344 | 0.0010477 | 0.00032545 | -0.0012817 | -52.9129 | 62.027 | -61.1938 | -0.09613 | -0.068665 | 0.018311 | -0.022888 | 0.064087 | 0.24261 | -0.32501 | -0.33875 | 0.10529 | 7.9422 | 60.759 | -61.9904 | 60.5301 | -61.6791 | 8.2809
1820.7656 | 123.0743 | -60.7727 | 61.9125 | -0.017439 | 0.04836 | 0.048197 | -0.005483 | 0.0010477 | -0.0013834 | -0.00021353 | -52.7527 | 61.9354 | -61.1526 | 0.10529 | 0.11902 | 0.16022 | -0.068665 | 0.33417 | 0.2243 | -0.21973 | -0.37994 | 0.022888 | 8.02 | 60.878 | -61.7935 | 60.553 | -61.6882 | 8.4
1821.7344 | 122.9462 | -60.8505 | 61.9675 | 0.066485 | 0.051778 | 0.049906 | 0.010112 | 0.0025431 | -0.00010175 | -0.0021361 | -52.6108 | 62.059 | -61.1801 | -0.018311 | -0.050354 | -0.059509 | 0.022888 | 0.14648 | 0.2243 | -0.33417 | -0.32959 | 0.091553 | 8.2397 | 60.8322 | -62.0178 | 60.5164 | -61.7432 | 8.5693
1822.7656 | 123.024 | -60.8002 | 61.908 | 0.081743 | 0.048147 | 0.046275 | -0.0033468 | 0.00062048 | -0.0011698 | 0.0012817 | -52.6199 | 61.9583 | -61.171 | 0.018311 | 0.073242 | 0.018311 | -0.09613 | 0.25177 | 0.21057 | -0.27924 | -0.37079 | 0.050354 | 8.1802 | 60.8185 | -61.8347 | 60.5209 | -61.6974 | 8.551
1823.7344 | 122.937 | -60.8505 | 61.9263 | 0.097002 | 0.052633 | 0.056101 | 0.010112 | 0.0027567 | 0.00011185 | -0.00042733 | -52.5513 | 62.0682 | -61.1664 | -0.050354 | -0.068665 | -0.10071 | 0.018311 | 0.091553 | 0.2243 | -0.38452 | -0.31586 | 0.14191 | 8.2993 | 60.8002 | -61.9949 | 60.466 | -61.702 | 8.6151
1824.75 | 123.024 | -60.8276 | 61.9263 | 0.64632 | 0.049856 | 0.047984 | -0.002065 | 0.0012615 | 0.00032545 | 0.00085447 | -52.6428 | 61.9675 | -61.1664 | 0.032043 | 0.054932 | 0.041199 | -0.059509 | 0.25635 | 0.19684 | -0.27008 | -0.33874 | 0.041198 | 8.1848 | 60.8597 | -61.8713 | 60.5576 | -61.7294 | 8.5236
1825.7344 | 122.9507 | -60.8322 | 61.9537 | 0.051226 | 0.053701 | 0.053965 | 0.0094706 | 0.00062048 | -0.0020244 | -0.0010681 | -52.7023 | 62.0453 | -61.1847 | -0.013733 | -0.022888 | -0.045776 | 0.018311 | 0.14648 | 0.24261 | -0.32501 | -0.35248 | 0.091553 | 8.1299 | 60.8185 | -61.9766 | 60.5072 | -61.7111 | 8.4824
1826.7656 | 123.1064 | -60.7773 | 61.9308 | -0.13188 | 0.046651 | 0.044139 | -0.003774 | -0.00087492 | 0.00011185 | -0.00021353 | -52.7069 | 61.9308 | -61.1572 | 0.12817 | 0.15106 | 0.17853 | -0.050354 | 0.39368 | 0.21973 | -0.20142 | -0.37994 | 0 | 8.0704 | 60.9055 | -61.7798 | 60.5759 | -61.7111 | 8.4503
1827.7344 | 122.937 | -60.8505 | 61.9583 | 0.18093 | 0.051778 | 0.053324 | 0.0090434 | 0.0027567 | -0.0015972 | -0.0014953 | -52.6108 | 62.0728 | -61.1893 | -0.032043 | -0.073242 | -0.09613 | 0.004578 | 0.10529 | 0.2243 | -0.37079 | -0.33875 | 0.11444 | 8.2397 | 60.8185 | -62.0316 | 60.4797 | -61.734 | 8.5785
1828.7656 | 123.0331 | -60.7956 | 61.9034 | -0.0021797 | 0.049001 | 0.047557 | -0.0016378 | 0.00019328 | -0.00031535 | 0.0012817 | -52.6245 | 61.9446 | -61.1801 | 0.027466 | 0.045776 | 0.050354 | -0.068665 | 0.28839 | 0.21973 | -0.27466 | -0.38452 | 0.041199 | 8.1711 | 60.8231 | -61.8576 | 60.5209 | -61.6837 | 8.5556
1829.7344 | 122.9553 | -60.8185 | 61.94 | 0.013079 | 0.056264 | 0.050547 | 0.0088298 | 0.0010477 | -0.0020244 | -0.0032043 | -52.5009 | 62.0361 | -61.1618 | 0.036621 | 0.032043 | 0.027466 | 0.009155 | 0.22888 | 0.25635 | -0.31128 | -0.34332 | 0.096131 | 8.3176 | 60.8551 | -61.908 | 60.5072 | -61.6837 | 8.6609
1830.7656 | 123.0606 | -60.791 | 61.9217 | 0.035967 | 0.048787 | 0.046275 | -0.003774 | 0.00019328 | 0.00011185 | -0.0027771 | -52.6703 | 61.9308 | -61.1893 | 0.059509 | 0.073242 | 0.091553 | -0.073242 | 0.31586 | 0.23346 | -0.26093 | -0.39825 | 0.009155 | 8.1207 | 60.8505 | -61.8484 | 60.5301 | -61.6882 | 8.519
1831.7344 | 122.9645 | -60.8368 | 61.9263 | -0.017439 | 0.052633 | 0.049906 | 0.0088298 | -0.00023392 | 0.00075285 | -0.0027771 | -52.5238 | 62.0499 | -61.1801 | 0.013733 | -0.009155 | -0.027466 | -0.004578 | 0.16479 | 0.25177 | -0.31128 | -0.34332 | 0.1236 | 8.313 | 60.8505 | -61.9354 | 60.5255 | -61.6745 | 8.6563
1832.7656 | 123.0286 | -60.7864 | 61.9354 | 0.13515 | 0.049428 | 0.047557 | -0.0007832 | -0.00044752 | 0.00075285 | -0.00042733 | -52.6245 | 61.9263 | -61.2167 | 0.013733 | 0.045776 | 0.022888 | -0.068665 | 0.23346 | 0.2243 | -0.28381 | -0.4303 | -0.009155 | 8.1619 | 60.8002 | -61.8896 | 60.5026 | -61.7111 | 8.5922
1833.7344 | 122.9462 | -60.8414 | 61.9583 | 0.11226 | 0.051992 | 0.05247 | 0.010539 | 0.0040385 | -0.0018108 | -0.0012817 | -52.7206 | 62.0407 | -61.1893 | 0.013733 | -0.032043 | -0.036621 | 0.004578 | 0.14648 | 0.23346 | -0.31586 | -0.3479 | 0.082397 | 8.1207 | 60.8551 | -61.9904 | 60.5255 | -61.7249 | 8.4686
1834.7656 | 122.9462 | -60.8551 | 61.9629 | 0.066485 | 0.051351 | 0.047984 | 0.0079752 | 0.0027567 | -0.00074255 | -0.0023499 | -52.6474 | 62.0544 | -61.2076 | -0.018311 | -0.050354 | -0.064087 | 0.018311 | 0.10529 | 0.24719 | -0.32501 | -0.35248 | 0.091552 | 8.2077 | 60.8368 | -62.0132 | 60.5301 | -61.7157 | 8.5602
1835.7344 | 122.9691 | -60.8231 | 61.9537 | -0.017439 | 0.052205 | 0.049266 | 0.005839 | 0.0029705 | -0.0028788 | 6.6667e-08 | -52.6703 | 62.0773 | -61.1755 | 0.054932 | 0.022888 | 0.032043 | 0.018311 | 0.21973 | 0.25177 | -0.28381 | -0.35248 | 0.1236 | 8.1528 | 60.878 | -61.9308 | 60.5392 | -61.702 | 8.5052
1836.7656 | 123.0286 | -60.8093 | 61.9263 | 0.051226 | 0.048147 | 0.046275 | -0.0056966 | 0.0010477 | 0.00011185 | 6.6667e-08 | -52.8488 | 61.9537 | -61.1847 | 0.013733 | 0.041199 | 0.059509 | -0.064087 | 0.26093 | 0.21973 | -0.27008 | -0.37537 | 0.027465 | 7.9605 | 60.8231 | -61.8851 | 60.5392 | -61.7065 | 8.3359
1837.7344 | 122.9691 | -60.8322 | 61.94 | -0.025068 | 0.053274 | 0.047343 | 0.0071208 | 0.0014751 | -0.00095615 | 0.00042727 | -52.565 | 62.0544 | -61.1984 | 0.064087 | 0.032043 | 0 | 0.027466 | 0.24719 | 0.24261 | -0.27924 | -0.36621 | 0.11444 | 8.2672 | 60.8963 | -61.908 | 60.553 | -61.6974 | 8.6334
1838.75 | 122.9965 | -60.8047 | 61.9308 | 0.21907 | 0.04836 | 0.049479 | 0.0002848 | 0.0036113 | -0.002238 | 0.00042727 | -52.6291 | 61.9629 | -61.171 | 0.004578 | 0.013733 | -0.004578 | -0.13733 | 0.2243 | 0.19226 | -0.33417 | -0.36621 | 0.032044 | 8.1757 | 60.8093 | -61.9171 | 60.4706 | -61.7386 | 8.5419
1839.7344 | 123.0743 | -60.7864 | 61.9034 | 0.26485 | 0.051565 | 0.048625 | 0.003062 | 0.0048931 | 0.00011185 | -0.0040589 | -52.5925 | 61.972 | -61.2076 | 0.31586 | 0.24719 | -0.027466 | -0.20142 | 0.33417 | 0.16937 | -0.3891 | -0.42114 | 0.068665 | 8.194 | 61.1023 | -61.6562 | 60.3973 | -61.734 | 8.6151
1840.7656 | 123.0652 | -60.7727 | 61.8988 | 0.24959 | 0.050924 | 0.052043 | -0.0007832 | -0.0017293 | 0.00011185 | 0.0010681 | -52.565 | 61.9583 | -61.1801 | -0.013733 | 0.091553 | 0.17395 | -0.22888 | 0.22888 | 0.16937 | -0.34332 | -0.40741 | 0.059509 | 8.2077 | 60.759 | -61.8073 | 60.4294 | -61.7294 | 8.6151
1841.7344 | 122.9874 | -60.8139 | 61.9171 | -0.0021797 | 0.054128 | 0.050761 | 0.0090434 | 0.00083408 | -0.00095615 | -0.0025635 | -52.5925 | 62.0728 | -61.1755 | 0.059509 | 0.027466 | -0.013733 | 0 | 0.27466 | 0.25177 | -0.28381 | -0.36163 | 0.15564 | 8.2214 | 60.8734 | -61.8896 | 60.5301 | -61.6653 | 8.5831
1842.7656 | 123.056 | -60.7864 | 61.9217 | 0.035967 | 0.047078 | 0.047557 | -0.0042012 | -0.00087492 | -0.0015972 | -0.00021353 | -52.6794 | 61.9354 | -61.1938 | 0.068665 | 0.082397 | 0.086975 | -0.064087 | 0.32044 | 0.22888 | -0.26093 | -0.40741 | 0.013733 | 8.107 | 60.8551 | -61.8393 | 60.5255 | -61.6928 | 8.5144
1843.7344 | 122.9874 | -60.8185 | 61.9492 | -0.13951 | 0.054555 | 0.051615 | 0.0069072 | 0.0014751 | -0.0011698 | -0.0055541 | -52.652 | 62.0728 | -61.1893 | 0.050354 | 0.022888 | 0.059509 | 0.068665 | 0.24261 | 0.2655 | -0.26093 | -0.37079 | 0.1236 | 8.1665 | 60.8688 | -61.9263 | 60.5576 | -61.6837 | 8.5373
1844.7656 | 123.0286 | -60.7727 | 61.9629 | -0.13188 | 0.047933 | 0.046702 | -0.000356 | 0.0010477 | -0.0026652 | 0.00021367 | -52.6566 | 61.9583 | -61.1343 | 0.10986 | 0.10986 | 0.13733 | 0.027466 | 0.35248 | 0.25177 | -0.22888 | -0.36163 | -0.004578 | 8.1162 | 60.8826 | -61.853 | 60.5438 | -61.7111 | 8.4778
1845.7344 | 123.0057 | -60.8231 | 61.9583 | -0.093733 | 0.050283 | 0.043925 | 0.0060526 | 0.0014751 | -0.0028788 | -0.0029907 | -52.6703 | 62.0499 | -61.1847 | 0.064087 | 0.022888 | 0.022888 | 0.036621 | 0.24719 | 0.25177 | -0.28381 | -0.36163 | 0.091553 | 8.1528 | 60.8871 | -61.9354 | 60.5392 | -61.7065 | 8.5144
1846.7656 | 123.0652 | -60.7819 | 61.908 | 0.19618 | 0.052205 | 0.048197 | 0.0037028 | 0.0042521 | -0.0018108 | -0.0025635 | -52.5146 | 61.9858 | -61.2122 | 0.004578 | -0.018311 | 0.013733 | -0.15564 | 0.19226 | 0.18768 | -0.37537 | -0.4303 | 0.07782 | 8.2672 | 60.7864 | -61.9263 | 60.4065 | -61.7203 | 8.6975
1847.7344 | 122.9919 | -60.8093 | 61.9537 | -0.0098092 | 0.051992 | 0.050975 | 0.0062662 | 0.0033977 | 0.00032545 | -0.00064093 | -52.684 | 62.059 | -61.1664 | -0.11902 | -0.091553 | 0.11444 | 0.11902 | 0.27466 | 0.2243 | -0.29297 | -0.35706 | 0.10529 | 8.1253 | 60.6903 | -62.0453 | 60.5164 | -61.7294 | 8.4824
1848.7656 | 123.024 | -60.8185 | 61.9171 | -0.025068 | 0.047078 | 0.045848 | -0.0039876 | 0.00083408 | -0.0015972 | 0.00064087 | -52.8214 | 61.9446 | -61.1618 | 0.054932 | 0.07782 | 0.086975 | -0.064087 | 0.31128 | 0.23804 | -0.2655 | -0.34332 | 0.027466 | 7.9971 | 60.8734 | -61.8393 | 60.553 | -61.6791 | 8.3405
1849.7344 | 123.0423 | -60.8139 | 61.8851 | 0.28011 | 0.052846 | 0.048625 | 0.0071208 | 0.00040688 | -0.00095615 | -0.00042733 | -52.6703 | 62.0178 | -61.1664 | 0.032043 | 0.013733 | 0.004578 | -0.16479 | 0.21973 | 0.16022 | -0.38452 | -0.35248 | 0.13275 | 8.1436 | 60.8459 | -61.8713 | 60.4294 | -61.7249 | 8.4961
1850.75 | 122.9736 | -60.8185 | 61.9217 | 0.31063 | 0.051992 | 0.051615 | 0.0060526 | 0.0014751 | 0.0020344 | -0.0014953 | -52.7344 | 62.0361 | -61.1801 | -0.027466 | -0.045776 | -0.073242 | -0.09613 | 0.13733 | 0.19684 | -0.35706 | -0.36163 | 0.11444 | 8.0841 | 60.791 | -61.9675 | 60.4614 | -61.7249 | 8.4457
1851.7344 | 122.9874 | -60.8368 | 61.94 | -0.055586 | 0.051992 | 0.048197 | 0.007548 | 0.0014751 | -0.00010175 | 0.00085447 | -52.7664 | 62.0728 | -61.1847 | 0.041199 | 0.027466 | 0.032043 | 0.032043 | 0.23804 | 0.25177 | -0.28839 | -0.3479 | 0.13275 | 8.0704 | 60.878 | -61.9125 | 60.5484 | -61.6882 | 8.4183
1852.7656 | 123.0011 | -60.8093 | 61.9171 | 0.10463 | 0.047506 | 0.046488 | -0.0033468 | 0.0021159 | -0.00052895 | -0.00021353 | -53.0502 | 61.9217 | -61.2122 | -0.10529 | 0 | -0.004578 | -0.09613 | 0.25177 | 0.20142 | -0.27466 | -0.40283 | 0.004578 | 7.7591 | 60.704 | -61.9171 | 60.5347 | -61.7157 | 8.1619
1853.7344 | 122.9874 | -60.8185 | 61.9446 | -0.10136 | 0.051778 | 0.051829 | 0.0049846 | 0.0019023 | -0.002238 | -0.00085453 | -52.6566 | 62.0544 | -61.1847 | 0.050354 | 0.045776 | 0.045776 | 0.068665 | 0.28839 | 0.27008 | -0.26093 | -0.36621 | 0.10986 | 8.1619 | 60.8688 | -61.8988 | 60.5576 | -61.6745 | 8.5281
1854.7656 | 123.0057 | -60.8368 | 61.9217 | 0.29537 | 0.053487 | 0.047984 | 0.005839 | 0.0048931 | 0.00032545 | -0.0014953 | -52.7756 | 62.0041 | -61.2122 | -0.013733 | -0.036621 | -0.054932 | -0.10529 | 0.13275 | 0.20142 | -0.35706 | -0.37537 | 0.082397 | 8.0612 | 60.8231 | -61.9583 | 60.4797 | -61.7203 | 8.4366
1855.7344 | 122.9691 | -60.8322 | 61.9766 | -0.025068 | 0.053487 | 0.05247 | 0.00648 | 0.0033977 | -0.0015972 | -0.0032043 | -52.6154 | 62.0682 | -61.1938 | 0.050354 | 0.041199 | 0.041199 | 0.027466 | 0.2243 | 0.25635 | -0.27466 | -0.36163 | 0.091552 | 8.2169 | 60.8826 | -61.9354 | 60.5576 | -61.7203 | 8.5785
1856.7656 | 122.9553 | -60.8459 | 61.9492 | -0.025068 | 0.054983 | 0.051402 | 0.0073344 | 0.0040385 | -0.00095615 | -0.0017089 | -52.684 | 62.0499 | -61.1893 | 0.013733 | 0.009155 | -0.032043 | 0.013733 | 0.16479 | 0.2243 | -0.31128 | -0.34332 | 0.10071 | 8.1619 | 60.8597 | -61.94 | 60.5347 | -61.7249 | 8.5052
1857.7344 | 122.9736 | -60.8551 | 61.9492 | -0.063215 | 0.053487 | 0.04777 | 0.0039164 | 0.00083408 | 0.00053925 | -0.00042733 | -52.6199 | 62.0544 | -61.2076 | 0.027466 | 0.045776 | 0.041199 | 0.13733 | 0.23804 | 0.28839 | -0.21057 | -0.35248 | 0.10529 | 8.2352 | 60.8826 | -61.9034 | 60.6445 | -61.6608 | 8.5876
1858.7656 | 123.0377 | -60.8231 | 61.9125 | 0.24196 | 0.049856 | 0.048411 | -0.0039876 | 0.0031841 | -0.00010175 | 0.00042727 | -52.6291 | 61.9354 | -61.1938 | 0.018311 | 0.068665 | 0.059509 | -0.064087 | 0.2655 | 0.20599 | -0.27008 | -0.37079 | 0.022888 | 8.194 | 60.8414 | -61.8439 | 60.553 | -61.7065 | 8.5648
1859.7344 | 122.9782 | -60.8185 | 61.9583 | -0.15477 | 0.051778 | 0.048411 | 0.0066936 | 0.0025431 | -0.0011698 | -0.0014953 | -52.3819 | 62.0453 | -61.1984 | 0.027466 | 0.022888 | 0.054932 | 0.10986 | 0.27008 | 0.28381 | -0.2243 | -0.37994 | 0.086975 | 8.4366 | 60.8459 | -61.9354 | 60.5942 | -61.6745 | 8.8165
1860.7656 | 122.9553 | -60.8139 | 61.9171 | -0.13188 | 0.053701 | 0.052043 | 0.0049846 | 0.0033977 | -0.00031535 | -0.00042733 | -52.7847 | 62.0453 | -61.1984 | -0.036621 | -0.059509 | -0.073242 | -0.045776 | 0.09613 | 0.21057 | -0.33875 | -0.38452 | 0.12817 | 8.0292 | 60.7773 | -61.9766 | 60.4752 | -61.7065 | 8.4137
1861.7344 | 122.9736 | -60.8276 | 61.9492 | -0.13188 | 0.052419 | 0.049052 | 0.005839 | 0.0036113 | -0.0028788 | -0.0019225 | -52.6474 | 62.059 | -61.1755 | 0.045776 | 0.050354 | 0.050354 | 0.07782 | 0.26093 | 0.27924 | -0.25177 | -0.3479 | 0.10986 | 8.1802 | 60.8734 | -61.8988 | 60.5759 | -61.6699 | 8.5281
1862.75 | 122.9416 | -60.8505 | 61.9308 | 0.23433 | 0.055196 | 0.050975 | 0.0056254 | 0.0031841 | 0.0024618 | 0.00021367 | -52.5009 | 62.0178 | -61.1984 | -0.35706 | 0.16937 | 0.56305 | -0.009155 | -0.004578 | 0.18768 | -0.35248 | -0.3479 | 0.086975 | 8.3496 | 60.4935 | -61.7615 | 60.498 | -61.7432 | 8.6975
1863.7344 | 122.9599 | -60.8368 | 61.9583 | -0.20817 | 0.049428 | 0.049693 | 0.0022074 | 0.0016887 | -0.00031535 | -0.00021353 | -52.5604 | 62.059 | -61.1893 | -0.036621 | 0.26093 | 0.45776 | -0.14191 | -0.14191 | 0.31586 | -0.14191 | -0.35248 | 0.10071 | 8.2764 | 60.8002 | -61.6974 | 60.6949 | -61.6425 | 8.6288
1864.75 | 122.9141 | -60.8688 | 61.9308 | 0.18093 | 0.054342 | 0.048625 | 0.0060526 | 0.0033977 | 0.00118 | -0.00064093 | -52.6337 | 62.0636 | -61.2122 | -0.07782 | -0.064087 | -0.10529 | -0.018311 | 0.09613 | 0.21057 | -0.35706 | -0.34332 | 0.13275 | 8.2352 | 60.791 | -61.9949 | 60.5118 | -61.7203 | 8.5785
1865.7344 | 122.9233 | -60.8414 | 61.9583 | -0.23869 | 0.053274 | 0.048197 | 0.003062 | 0.0014751 | 0.0020344 | -0.00021353 | -52.5513 | 62.0361 | -61.1938 | 0.050354 | 0.041199 | 0.032043 | 0.13733 | 0.25177 | 0.27924 | -0.25177 | -0.35248 | 0.07782 | 8.2901 | 60.8917 | -61.9171 | 60.5896 | -61.6791 | 8.6426
1866.7656 | 123.024 | -60.8047 | 61.9217 | 0.21907 | 0.051778 | 0.046275 | -0.0031332 | 0.00083408 | 0.00096645 | 0.00085447 | -52.7023 | 61.94 | -61.1801 | 0 | 0.050354 | 0.045776 | -0.082397 | 0.25177 | 0.21057 | -0.27924 | -0.37537 | 0.01831 | 8.1024 | 60.8047 | -61.8713 | 60.5255 | -61.7111 | 8.4778
1867.7344 | 122.9645 | -60.8322 | 61.9675 | -0.10136 | 0.053487 | 0.043925 | 0.00413 | 0.0012615 | -0.0013834 | -0.0034179 | -52.652 | 62.0407 | -61.1893 | 0.022888 | 0.018311 | 0.032043 | 0.10986 | 0.23346 | 0.29297 | -0.21515 | -0.35706 | 0.073242 | 8.1802 | 60.8551 | -61.9492 | 60.6171 | -61.6745 | 8.5373
1868.7656 | 123.0698 | -60.7956 | 61.9171 | 0.19618 | 0.051992 | 0.052256 | 0.0037028 | 0.0042521 | -0.00074255 | -0.00021353 | -52.7023 | 61.94 | -61.2122 | 0.041199 | 0.045776 | 0.009155 | -0.19684 | 0.20599 | 0.16479 | -0.3891 | -0.41657 | 0.022888 | 8.0933 | 60.8368 | -61.8713 | 60.4065 | -61.7523 | 8.5098
1869.7344 | 122.937 | -60.8459 | 61.9766 | -0.22343 | 0.051992 | 0.049693 | 0.0039164 | 0.00062048 | -0.00074255 | -0.0012817 | -52.9037 | 62.0728 | -61.1984 | -0.054932 | 0.013733 | 0.059509 | 0.054932 | 0.21515 | 0.27924 | -0.24261 | -0.35248 | 0.09613 | 7.9422 | 60.791 | -61.9629 | 60.6033 | -61.6974 | 8.2947
1870.7656 | 122.9279 | -60.8185 | 61.9629 | -0.2158 | 0.050069 | 0.048625 | 0.003062 | 0.0027567 | -0.00095615 | -0.00042733 | -52.6016 | 62.0132 | -61.203 | 0.018311 | 0.027466 | 0.045776 | 0.16022 | 0.25177 | 0.28381 | -0.17853 | -0.38452 | 0.050354 | 8.2169 | 60.8368 | -61.9354 | 60.64 | -61.6791 | 8.6014
1871.7344 | 122.9553 | -60.8185 | 61.94 | -0.2158 | 0.05071 | 0.050334 | 7.12e-05 | 0.0010477 | 0.00032545 | -0.0023499 | -53.0685 | 61.9995 | -61.1893 | 0.064087 | 0.073242 | 0.091553 | 0.07782 | 0.29755 | 0.28839 | -0.2243 | -0.37079 | 0.05951 | 7.7499 | 60.8826 | -61.8668 | 60.5942 | -61.6516 | 8.1207
1872.7656 | 122.9416 | -60.8505 | 61.9492 | 0.24196 | 0.053701 | 0.048838 | 0.0098978 | 0.0068157 | 0.00053925 | -0.0044861 | -52.5192 | 62.0224 | -61.1984 | 0.34332 | 0.14191 | -0.27008 | 0.059509 | 0.27466 | 0.21057 | -0.34332 | -0.3479 | 0.073242 | 8.3313 | 61.1938 | -61.8073 | 60.5072 | -61.7386 | 8.6792
1873.7344 | 122.9187 | -60.8505 | 61.9675 | -0.20054 | 0.052205 | 0.045634 | 7.12e-05 | 0.0025431 | -0.00074255 | -0.0014953 | -53.0594 | 62.0087 | -61.1984 | 0.054932 | 0.022888 | 0.018311 | 0.1236 | 0.30212 | 0.27924 | -0.19684 | -0.3479 | 0.041199 | 7.7911 | 60.9055 | -61.9446 | 60.6537 | -61.6882 | 8.139
1874.7656 | 123.0194 | -60.8276 | 61.908 | 0.24196 | 0.051565 | 0.042857 | 0.0054118 | 0.0016887 | -0.0011698 | -0.0012817 | -52.4734 | 62.0132 | -61.2076 | 0 | 0.004578 | -0.022888 | -0.15106 | 0.17853 | 0.18768 | -0.36163 | -0.37994 | 0.10529 | 8.3542 | 60.8276 | -61.9034 | 60.466 | -61.7203 | 8.7341
1875.7344 | 122.9507 | -60.8551 | 61.9766 | -0.047956 | 0.050069 | 0.049052 | 0.0032756 | -0.00044752 | -0.00052895 | -0.00042733 | -52.6016 | 62.0453 | -61.2076 | 0.018311 | 0.022888 | 0.041199 | 0.14648 | 0.24261 | 0.29755 | -0.21515 | -0.35248 | 0.068664 | 8.2535 | 60.8734 | -61.9537 | 60.64 | -61.6791 | 8.606
1876.75 | 122.9874 | -60.8551 | 61.94 | -0.12425 | 0.053274 | 0.047557 | 0.007548 | 0.0036113 | -0.00010175 | -0.0012817 | -52.4139 | 62.0407 | -61.1847 | 0.032043 | 0 | 0.004578 | 0.022888 | 0.18768 | 0.25635 | -0.31128 | -0.32959 | 0.10071 | 8.4412 | 60.8871 | -61.94 | 60.5438 | -61.6837 | 8.7708
1877.7344 | 123.0331 | -60.7956 | 61.9492 | 0.24959 | 0.049856 | 0.048197 | -0.0014242 | 0.0025431 | -0.0018108 | -0.00021353 | -52.5238 | 61.9583 | -61.171 | 0.10986 | 0.12817 | 0.1236 | -0.009155 | 0.3479 | 0.24719 | -0.21515 | -0.37537 | 0.009155 | 8.2718 | 60.9055 | -61.821 | 60.5804 | -61.702 | 8.6472
1878.7656 | 123.0743 | -60.8185 | 61.908 | 0.25722 | 0.050283 | 0.055888 | 0.002421 | 0.0025431 | -0.00031535 | 6.6667e-08 | -52.4597 | 61.9537 | -61.1847 | 0.041199 | 0.027466 | 0.009155 | -0.20142 | 0.2243 | 0.15564 | -0.3891 | -0.36621 | 0.045776 | 8.3588 | 60.8597 | -61.8805 | 60.4294 | -61.7523 | 8.725
1879.7344 | 123.024 | -60.7956 | 61.9492 | -0.20054 | 0.047933 | 0.048411 | 0.0043436 | -0.00066112 | -0.0013834 | -0.0010681 | -52.2629 | 61.9766 | -61.1847 | 0.11444 | 0.10071 | 0.11902 | 0.050354 | 0.33417 | 0.27466 | -0.2243 | -0.3891 | 0.027466 | 8.5327 | 60.91 | -61.8484 | 60.5713 | -61.6745 | 8.9218
1880.75 | 122.9691 | -60.8322 | 61.9537 | -0.047956 | 0.051992 | 0.053538 | 0.010112 | 0.0016887 | -0.0026652 | -0.0021361 | -52.5192 | 62.0453 | -61.1664 | 0.068665 | 0.022888 | 0.036621 | 0.022888 | 0.23346 | 0.26093 | -0.27008 | -0.33417 | 0.091553 | 8.313 | 60.9009 | -61.9308 | 60.5621 | -61.6928 | 8.6472
1881.7344 | 122.9507 | -60.791 | 61.9583 | -0.20054 | 0.049215 | 0.046702 | 0.0019938 | -0.00087492 | -0.0030924 | -0.00085453 | -52.6154 | 61.9766 | -61.1893 | 0.022888 | 0.041199 | 0.050354 | 0.15106 | 0.32501 | 0.27924 | -0.18768 | -0.39825 | 0.018311 | 8.1757 | 60.8139 | -61.9171 | 60.6033 | -61.6791 | 8.5739
1882.7656 | 122.9141 | -60.8459 | 61.9308 | 0.19618 | 0.054555 | 0.050334 | 0.010325 | 0.0025431 | 0.00075285 | -0.0019225 | -52.6062 | 62.059 | -61.2167 | -0.045776 | -0.054932 | -0.10529 | -0.027466 | 0.082397 | 0.21515 | -0.36621 | -0.37079 | 0.12817 | 8.2397 | 60.8002 | -61.9858 | 60.4797 | -61.7157 | 8.6105
1883.7344 | 122.9782 | -60.8185 | 61.9492 | -0.2158 | 0.049428 | 0.05012 | -0.0014242 | 0.0016887 | -0.00052895 | -0.0014953 | -52.4185 | 61.9583 | -61.1938 | 0.07782 | 0.091553 | 0.10529 | 0.07782 | 0.31128 | 0.2655 | -0.23346 | -0.37537 | 0.009155 | 8.4 | 60.8963 | -61.8576 | 60.585 | -61.6837 | 8.7753
1884.7656 | 123.0743 | -60.8139 | 61.8759 | 0.19618 | 0.049642 | 0.049266 | 0.0054118 | 0.0016887 | -0.0013834 | -0.0012817 | -52.4048 | 61.9812 | -61.1938 | 0.041199 | 0.045776 | 0.004578 | -0.20142 | 0.21973 | 0.15106 | -0.37537 | -0.37994 | 0.10529 | 8.4091 | 60.8551 | -61.8301 | 60.4385 | -61.7249 | 8.7891
1885.7344 | 123.0194 | -60.7864 | 61.9125 | -0.13951 | 0.046651 | 0.048197 | 0.0009258 | -0.0025837 | -0.0020244 | 0.00042727 | -52.4414 | 61.9812 | -61.1664 | 0.09613 | 0.10529 | 0.11902 | 0.032043 | 0.33875 | 0.26093 | -0.21057 | -0.37994 | 0.068664 | 8.345 | 60.8826 | -61.8073 | 60.5759 | -61.6516 | 8.725
1886.7656 | 122.9324 | -60.8368 | 61.9675 | 0.20381 | 0.051778 | 0.049266 | 0.0088298 | 0.00062048 | 0.00118 | -0.0012817 | -52.8717 | 62.0407 | -61.1984 | -0.050354 | -0.073242 | -0.086975 | -0.018311 | 0.082397 | 0.21973 | -0.3479 | -0.36163 | 0.073242 | 7.9651 | 60.7864 | -62.0407 | 60.4889 | -61.7477 | 8.3267
1887.7344 | 123.024 | -60.7864 | 61.9125 | -0.19291 | 0.049215 | 0.049693 | -0.000356 | -0.00023392 | 0.00032545 | -0.0021361 | -52.5696 | 61.9308 | -61.1618 | 0.11902 | 0.11444 | 0.13733 | -0.004578 | 0.33417 | 0.25177 | -0.23346 | -0.37537 | 0.01831 | 8.2169 | 60.9055 | -61.7981 | 60.553 | -61.6608 | 8.5922
1888.7656 | 123.024 | -60.8368 | 61.8942 | 0.25722 | 0.052846 | 0.053324 | 0.0077616 | 0.0023295 | -0.002238 | -0.0019225 | -52.6062 | 62.0087 | -61.2122 | 0.018311 | -0.009155 | -0.022888 | -0.14648 | 0.16022 | 0.16479 | -0.38452 | -0.37537 | 0.11444 | 8.2306 | 60.8551 | -61.9034 | 60.4523 | -61.7294 | 8.606
1889.7344 | 122.9965 | -60.7956 | 61.9537 | -0.1624 | 0.049642 | 0.048411 | 0.0011394 | -0.00087492 | -0.00010175 | -0.00085453 | -53.1418 | 61.9675 | -61.1755 | 0.07782 | 0.10529 | 0.11444 | 0.068665 | 0.32501 | 0.25635 | -0.22888 | -0.37994 | 0.013733 | 7.6538 | 60.8734 | -61.8484 | 60.5667 | -61.6974 | 8.0338
1890.7656 | 122.9416 | -60.8322 | 61.9492 | 0.0054493 | 0.054555 | 0.049266 | 0.0084026 | 0.0031841 | -0.00095615 | -0.0027771 | -52.9999 | 62.0499 | -61.171 | 0.013733 | -0.022888 | -0.022888 | 0.009155 | 0.17853 | 0.23346 | -0.31128 | -0.33875 | 0.10071 | 7.8323 | 60.8459 | -61.972 | 60.5209 | -61.7157 | 8.1711
1891.7344 | 123.0377 | -60.7864 | 61.972 | -0.12425 | 0.047078 | 0.047343 | -0.0016378 | 0.00040688 | -0.0020244 | 0.00021367 | -52.739 | 61.9492 | -61.1801 | 0.11902 | 0.13275 | 0.16937 | -0.045776 | 0.37537 | 0.23804 | -0.21515 | -0.39368 | -0.022888 | 8.0475 | 60.9055 | -61.8393 | 60.5713 | -61.734 | 8.4412
1892.7656 | 122.9233 | -60.8597 | 61.9354 | 0.2267 | 0.054983 | 0.051188 | 0.010112 | 0.0021159 | 0.00011185 | -0.0017089 | -52.8214 | 62.0407 | -61.1984 | -0.045776 | -0.059509 | -0.10071 | -0.009155 | 0.11444 | 0.23346 | -0.35248 | -0.33875 | 0.10528 | 8.0383 | 60.8139 | -61.9949 | 60.5072 | -61.702 | 8.3771
1893.7344 | 123.0377 | -60.8047 | 61.9446 | 0.91335 | 0.049001 | 0.048838 | -0.0016378 | -0.00087492 | -0.0011698 | -0.0017089 | -52.2858 | 61.9629 | -61.1755 | 0.1236 | 0.15106 | 0.15106 | -0.018311 | 0.37079 | 0.23804 | -0.24261 | -0.37079 | 0.018311 | 8.519 | 60.9283 | -61.7935 | 60.5621 | -61.7065 | 8.8898
1894.7656 | 122.9416 | -60.8459 | 61.972 | 0.11989 | 0.052846 | 0.05247 | 0.009257 | 0.0010477 | -0.00095615 | -0.0012817 | -53.4302 | 62.0544 | -61.1435 | -0.004578 | -0.032043 | -0.022888 | 0.013733 | 0.14648 | 0.2243 | -0.32044 | -0.29755 | 0.082397 | 7.4158 | 60.8414 | -62.0041 | 60.5255 | -61.7477 | 7.7133
1895.7344 | 123.0011 | -60.7864 | 61.9492 | -0.19291 | 0.050283 | 0.04243 | 0.0009258 | 0.00040688 | -0.00074255 | -0.00021353 | -52.3499 | 61.9492 | -61.1893 | 0.082397 | 0.09613 | 0.11902 | 0.054932 | 0.32501 | 0.25635 | -0.21057 | -0.40283 | 0 | 8.4366 | 60.8688 | -61.853 | 60.5759 | -61.6928 | 8.8394
1896.7656 | 123.0743 | -60.8093 | 61.9125 | 0.16567 | 0.051778 | 0.055888 | 0.0062662 | 0.0036113 | -0.00031535 | -0.00085453 | -52.4002 | 61.972 | -61.2076 | 0.022888 | 0.041199 | 0.041199 | -0.19226 | 0.19226 | 0.16479 | -0.38452 | -0.39825 | 0.059509 | 8.4091 | 60.8322 | -61.8713 | 60.4248 | -61.7477 | 8.8074
1897.7344 | 123.0698 | -60.7956 | 61.9125 | -0.14714 | 0.049428 | 0.044139 | -0.0014242 | -0.0010885 | 0.00011185 | -0.0023499 | -52.1622 | 61.972 | -61.1618 | 0.1236 | 0.13275 | 0.16479 | -0.045776 | 0.38452 | 0.23804 | -0.23346 | -0.36621 | 0.059509 | 8.6334 | 60.9192 | -61.7798 | 60.5621 | -61.6745 | 8.9996
1898.75 | 122.9187 | -60.8414 | 61.9446 | 0.12752 | 0.052419 | 0.051402 | 0.0088298 | 0.0012615 | -0.0020244 | 0.00042727 | -52.2583 | 62.0682 | -61.1893 | -0.054932 | -0.091553 | -0.1236 | 0.009155 | 0.059509 | 0.20142 | -0.36621 | -0.3479 | 0.1236 | 8.5831 | 60.7864 | -62.0361 | 60.4752 | -61.7432 | 8.931
1899.7344 | 123.056 | -60.8185 | 61.9354 | 2.0044 | 0.048574 | 0.049052 | -0.0014242 | 0.00019328 | 0.00075285 | 0.00064087 | -52.2446 | 61.9263 | -61.1938 | 0.086975 | 0.13733 | 0.19226 | -0.032043 | 0.35706 | 0.22888 | -0.23804 | -0.37537 | -0.009155 | 8.5739 | 60.9055 | -61.7981 | 60.5804 | -61.7065 | 8.9493
1900.7656 | 123.0057 | -60.7864 | 61.9217 | -0.1624 | 0.049856 | 0.04777 | -0.0009968 | 0.0014751 | 0.00032545 | -0.0010681 | -52.0294 | 61.9354 | -61.1847 | 0.11444 | 0.11902 | 0.14191 | 0.10529 | 0.99792 | 0.2655 | -0.16937 | -0.39825 | 0.013733 | 8.757 | 60.9009 | -61.8027 | 60.6171 | -61.6562 | 9.1553
1901.7344 | 123.0652 | -60.7956 | 61.8942 | -0.15477 | 0.048787 | 0.05012 | 0.0002848 | 0.00083408 | -0.0024516 | 0.00085447 | -52.153 | 61.9171 | -61.171 | -0.064087 | -0.29297 | -0.018311 | 0.086975 | 0.27008 | 0.25635 | -0.19684 | -0.37537 | 0.022888 | 8.6426 | 60.7315 | -62.1872 | 60.5988 | -61.6379 | 9.0179
1902.7656 | 122.9187 | -60.8688 | 61.9308 | 0.15804 | 0.054769 | 0.051829 | 0.0098978 | 0.0014751 | 0.0016072 | -0.0029907 | -52.3315 | 62.0407 | -61.1893 | -0.041199 | -0.10071 | -0.59509 | -0.54932 | 0.38452 | 0.1831 | -0.3891 | -0.32044 | 0.10986 | 8.5373 | 60.8276 | -62.0316 | 60.4797 | -61.7477 | 8.8577
1903.7344 | 123.0331 | -60.791 | 61.9171 | -0.13188 | 0.049215 | 0.049906 | 0.0009258 | 0.00040688 | -0.0028788 | -0.00064093 | -51.8967 | 61.9629 | -61.1893 | 0.10529 | 0.1236 | 0.13733 | 0.022888 | 0.3479 | 0.25635 | -0.21515 | -0.39825 | 0.045777 | 8.8943 | 60.8963 | -61.7935 | 60.5759 | -61.6608 | 9.2926
1904.7656 | 122.9507 | -60.8185 | 61.9217 | 0.081743 | 0.053274 | 0.051188 | 0.0098978 | 0.0019023 | -0.0028788 | -0.00042733 | -52.0248 | 62.0361 | -61.1801 | 0.041199 | 0.004578 | 0.013733 | 0.022888 | 0.20599 | 0.24261 | -0.28839 | -0.36163 | 0.11444 | 8.7936 | 60.8597 | -61.9171 | 60.5301 | -61.6791 | 9.1553
1905.7344 | 122.9919 | -60.8322 | 61.9354 | -0.10136 | 0.051992 | 0.053324 | 0.004771 | 0.0027567 | 0.0020344 | -0.0017089 | -52.4002 | 62.059 | -61.1938 | 0.068665 | 0.050354 | 0.032043 | 0.032043 | 0.24719 | 0.27008 | -0.26093 | -0.36163 | 0.1236 | 8.432 | 60.9009 | -61.8851 | 60.5713 | -61.6653 | 8.7936
1906.7344 | 123.0377 | -60.8093 | 61.9308 | 0.27248 | 0.050283 | 0.044352 | -0.0001424 | 0.0010477 | -0.00052895 | -0.00085453 | -51.7273 | 61.9217 | -61.1984 | 0.11444 | 0.11902 | 0.11902 | -0.013733 | 0.36163 | 0.22888 | -0.21515 | -0.3891 | -0.009155 | 9.082 | 60.9238 | -61.8118 | 60.5942 | -61.702 | 9.4711
1907.7656 | 122.9279 | -60.8459 | 61.9308 | 0.66158 | 0.054555 | 0.055888 | 0.0071208 | 0.0040385 | -0.0011698 | -0.0021361 | -52.1393 | 62.0407 | -61.2076 | -0.059509 | -0.064087 | -0.068665 | -0.041199 | 0.10529 | 0.21973 | -0.32044 | -0.36163 | 0.10986 | 8.7067 | 60.7864 | -61.9949 | 60.5255 | -61.7111 | 9.0683
1908.7344 | 123.0515 | -60.7864 | 61.9308 | 1.6305 | 0.049856 | 0.050547 | -0.0018514 | 0.0016887 | -0.0018108 | -0.0025635 | -52.1393 | 61.9446 | -61.2076 | 0.10529 | 0.15564 | 0.15106 | -0.022888 | 0.38452 | 0.22888 | -0.2243 | -0.42114 | 0.013733 | 8.6472 | 60.8917 | -61.7752 | 60.5621 | -61.702 | 9.0683
1909.7656 | 122.9645 | -60.8276 | 61.9217 | 0.020708 | 0.054342 | 0.050334 | 0.010966 | 0.0044657 | -0.00074255 | -0.0014953 | -52.0203 | 62.0636 | -61.1938 | 0.086975 | 0.054932 | 0.054932 | 0.018311 | 0.18768 | 0.22888 | -0.29755 | -0.36621 | 0.14191 | 8.8074 | 60.9146 | -61.8668 | 60.5301 | -61.6928 | 9.1736
1910.7344 | 122.9691 | -60.8368 | 61.94 | -0.0021797 | 0.054128 | 0.055033 | 0.0071208 | 0.0044657 | -0.0018108 | 6.6667e-08 | -52.066 | 62.0453 | -61.1893 | 0.022888 | 0 | -0.032043 | 0.004578 | 0.1831 | 0.24719 | -0.3067 | -0.35248 | 0.10529 | 8.7708 | 60.8597 | -61.94 | 60.5301 | -61.6928 | 9.1232
1911.7656 | 123.0103 | -60.8047 | 61.908 | 0.089373 | 0.049642 | 0.049693 | -0.0039876 | 0.0012615 | 0.00075285 | 0.00042727 | -52.2308 | 61.9354 | -61.1938 | 0.013733 | 0.054932 | 0.032043 | -0.073242 | 0.22888 | 0.20599 | -0.27924 | -0.3891 | 0.027466 | 8.5739 | 60.8185 | -61.853 | 60.5255 | -61.702 | 8.963
1912.7344 | 123.0515 | -60.8139 | 61.8988 | -2.2376 | 0.050283 | 0.046702 | -0.0001424 | 0.00083408 | 0.00011185 | -0.00042733 | -52.1713 | 61.972 | -61.1481 | 0.16022 | 0.11902 | 0.068665 | -0.018311 | 0.39825 | 0.21973 | -0.22888 | -0.33417 | 0.073242 | 8.6426 | 60.9741 | -61.7798 | 60.585 | -61.6791 | 8.9767
1913.7656 | 123.0469 | -60.8276 | 61.8851 | 0.24196 | 0.05306 | 0.047984 | 0.0049846 | 0.0025431 | -0.0011698 | 0.00064087 | -51.5762 | 61.9446 | -61.1664 | 0.036621 | 0.032043 | 0.032043 | -0.19684 | 0.21973 | 0.16479 | -0.37994 | -0.33874 | 0.059509 | 9.2514 | 60.8643 | -61.853 | 60.4477 | -61.7203 | 9.5901
1914.7344 | 123.0011 | -60.8276 | 61.9354 | -0.20054 | 0.050924 | 0.046275 | 0.0009258 | 0.00062048 | -0.0028788 | -0.0010681 | -51.8829 | 61.9858 | -61.1847 | 0.073242 | 0.07782 | 0.10529 | 0.064087 | 0.31128 | 0.27008 | -0.21057 | -0.35705 | 0.050354 | 8.9447 | 60.9009 | -61.8576 | 60.6171 | -61.6653 | 9.3018
1915.7656 | 123.0194 | -60.8002 | 61.9354 | -0.14714 | 0.049642 | 0.05012 | 0.0019938 | -0.0017293 | -0.0011698 | -0.0012817 | -51.7639 | 61.9354 | -61.1801 | 0.091553 | 0.10529 | 0.12817 | 0.041199 | 0.34332 | 0.27008 | -0.2243 | -0.37994 | 0 | 9.0363 | 60.8917 | -61.8301 | 60.5759 | -61.6653 | 9.4162
1916.7344 | 122.937 | -60.8276 | 61.9675 | -0.23869 | 0.052846 | 0.049693 | 0.004771 | -0.0010885 | -0.0033062 | -0.00085453 | -51.8097 | 62.0224 | -61.1938 | 0.009155 | 0.027466 | 0.045776 | 0.13733 | 0.25177 | 0.28839 | -0.17853 | -0.36621 | 0.054932 | 9.0179 | 60.8368 | -61.94 | 60.6491 | -61.6791 | 9.3842
1917.7656 | 122.9187 | -60.8459 | 61.9125 | 0.15804 | 0.05541 | 0.053324 | 0.010112 | 0.0046793 | -0.0018108 | -0.0025635 | -51.9653 | 62.0316 | -61.1938 | -0.059509 | -0.086975 | -0.10986 | 0.009155 | 0.07782 | 0.21973 | -0.36621 | -0.3479 | 0.11902 | 8.8806 | 60.7864 | -61.9995 | 60.4797 | -61.6928 | 9.2285
1918.7344 | 122.9874 | -60.7956 | 61.9675 | -0.18529 | 0.051992 | 0.045848 | -0.0007832 | 0.0025431 | -0.00031535 | 0.0010681 | -52.0752 | 61.972 | -61.1893 | 0.073242 | 0.082397 | 0.10529 | 0.059509 | 0.31586 | 0.26093 | -0.21515 | -0.39368 | 0.004578 | 8.7204 | 60.8688 | -61.8851 | 60.5804 | -61.7065 | 9.1141
1919.75 | 122.9599 | -60.8688 | 61.9034 | 0.18855 | 0.055623 | 0.055033 | 0.0088298 | 0.0025431 | -0.00031535 | -0.0010681 | -51.947 | 62.0316 | -61.1938 | -0.013733 | -0.045776 | -0.073242 | -0.082397 | 0.11902 | 0.19684 | -0.35706 | -0.32501 | 0.12817 | 8.9218 | 60.8551 | -61.9492 | 60.5118 | -61.7065 | 9.2468
1920.7344 | 122.9324 | -60.8322 | 61.9492 | -0.23106 | 0.052205 | 0.049266 | 0.0032756 | 0.00040688 | -0.0020244 | -0.0025635 | -51.9104 | 61.9995 | -61.2167 | 0.036621 | 0.032043 | 0.045776 | 0.14648 | 0.25635 | 0.28381 | -0.19226 | -0.38452 | 0.050354 | 8.9218 | 60.8688 | -61.9171 | 60.64 | -61.6653 | 9.3063
1921.7656 | 122.9324 | -60.8505 | 61.9308 | 0.19618 | 0.056691 | 0.049479 | 0.0069072 | 0.0014751 | 0.00096645 | -0.00064093 | -51.6678 | 62.027 | -61.2442 | -0.14648 | -0.032043 | 0.11902 | -0.022888 | 0.064087 | 0.21515 | -0.32501 | -0.39368 | 0.096131 | 9.1827 | 60.704 | -61.9629 | 60.5255 | -61.7157 | 9.5764
1922.7344 | 122.9416 | -60.8459 | 61.94 | -0.26921 | 0.05071 | 0.048411 | 0.0034892 | 0.00083408 | -0.0015972 | 6.6667e-08 | -51.8921 | 61.9949 | -61.2167 | 0.013733 | 0.041199 | 0.022888 | 0.15564 | 0.2655 | 0.28839 | -0.17853 | -0.37079 | 0.054932 | 8.9539 | 60.8597 | -61.8988 | 60.6674 | -61.6516 | 9.3246
1923.7656 | 123.0011 | -60.8002 | 61.8942 | 0.20381 | 0.052205 | 0.051402 | 0.0011394 | 0.0010477 | -0.0026652 | 0.0010681 | -51.8417 | 61.9034 | -61.1938 | 0.013733 | 0.036621 | 0.022888 | -0.17853 | 0.21973 | 0.1831 | -0.3479 | -0.39368 | 0.009155 | 8.9584 | 60.8139 | -61.8576 | 60.4523 | -61.7111 | 9.3521
1924.7344 | 122.9553 | -60.8643 | 61.9308 | -0.20054 | 0.052633 | 0.05012 | 0.0034892 | -0.00066112 | -0.0013834 | 0.0021363 | -51.9562 | 62.027 | -61.1893 | -0.21973 | -0.21057 | 0.059509 | 0.1831 | 0.14191 | 0.28381 | -0.18768 | -0.32501 | 0.096131 | 8.9081 | 60.6445 | -62.1414 | 60.6766 | -61.647 | 9.2331
1925.7656 | 123.0515 | -60.8002 | 61.8942 | 0.24959 | 0.054769 | 0.054606 | 0.0073344 | 0.0033977 | 0.00075285 | -0.00085453 | -51.8784 | 61.9904 | -61.171 | 0.036621 | 0.009155 | 0 | -0.20142 | 0.17395 | 0.17853 | -0.3891 | -0.37079 | 0.09613 | 8.9218 | 60.8368 | -61.8851 | 60.4111 | -61.7157 | 9.2926
1926.7344 | 122.9782 | -60.8414 | 61.94 | -0.19291 | 0.054769 | 0.047129 | 0.0009258 | 0.00040688 | -0.00010175 | 0.00064087 | -51.5396 | 61.9766 | -61.1938 | 0.059509 | 0.064087 | 0.09613 | 0.10986 | 0.28381 | 0.27466 | -0.18768 | -0.35248 | 0.036622 | 9.3018 | 60.9009 | -61.8759 | 60.6537 | -61.6653 | 9.6542
1927.7656 | 123.0606 | -60.8047 | 61.8851 | 0.29537 | 0.05306 | 0.053752 | 0.0051982 | 0.0029705 | -0.0024516 | -0.0023499 | -51.6449 | 61.9492 | -61.1847 | 0.036621 | 0.036621 | 0.027466 | -0.21057 | 0.22888 | 0.16937 | -0.37079 | -0.37994 | 0.064087 | 9.1599 | 60.8414 | -61.8485 | 60.434 | -61.7157 | 9.5398
1928.7344 | 122.9553 | -60.8322 | 61.9537 | -0.078474 | 0.053914 | 0.049052 | 0.0037028 | 0.0019023 | -0.0015972 | -0.0017089 | -51.8875 | 61.9995 | -61.1893 | 0.027466 | 0.045776 | 0.045776 | 0.15564 | 0.25177 | 0.29297 | -0.1831 | -0.35706 | 0.045777 | 8.9447 | 60.8597 | -61.908 | 60.6491 | -61.6608 | 9.3018
1929.75 | 122.9553 | -60.8551 | 61.9354 | 0.043596 | 0.056051 | 0.051188 | 0.0088298 | 0.0042521 | -0.0033062 | -0.0023499 | -52.0203 | 62.027 | -61.1801 | 0.013733 | -0.013733 | -0.027466 | -0.009155 | 0.17395 | 0.25177 | -0.32044 | -0.32501 | 0.091553 | 8.8348 | 60.8688 | -61.9492 | 60.5347 | -61.6837 | 9.1599
1930.7344 | 122.9507 | -60.8459 | 61.9354 | -0.1624 | 0.054128 | 0.050761 | 0.005839 | 0.0016887 | -0.0028788 | -0.00021353 | -51.8646 | 62.0453 | -61.1984 | 0.036621 | 0.027466 | 0.045776 | 0.12817 | 0.2655 | 0.27466 | -0.19684 | -0.35248 | 0.10986 | 8.9813 | 60.8826 | -61.908 | 60.6491 | -61.6608 | 9.3338
1931.7656 | 123.0057 | -60.8231 | 61.8759 | 0.24196 | 0.051992 | 0.049052 | 0.000712 | 0.0027567 | -0.0013834 | -0.00042733 | -51.5717 | 61.9171 | -61.2076 | 0.036621 | 0.054932 | 0.054932 | -0.16479 | 0.21973 | 0.16937 | -0.36621 | -0.38452 | 0.041198 | 9.2514 | 60.8597 | -61.821 | 60.4568 | -61.7065 | 9.6359
1932.7344 | 122.9691 | -60.8322 | 61.9492 | -0.20054 | 0.051137 | 0.051829 | 0.0002848 | -2.0324e-05 | 0.00011185 | -0.0012817 | -51.6678 | 61.9949 | -61.1847 | 0.064087 | 0.064087 | 0.09613 | 0.10529 | 0.31128 | 0.27924 | -0.21057 | -0.35248 | 0.045776 | 9.1644 | 60.8963 | -61.8851 | 60.6216 | -61.6699 | 9.5169
1933.7656 | 122.9507 | -60.8322 | 61.9446 | -0.1624 | 0.053487 | 0.052897 | 0.0034892 | 0.0025431 | -0.00095615 | -0.0017089 | -51.3977 | 62.0132 | -61.1847 | 0.032043 | 0.041199 | -0.041199 | 0.09613 | 0.25635 | 0.27466 | -0.25635 | -0.35248 | 0.068665 | 9.4345 | 60.8643 | -61.9034 | 60.5759 | -61.6699 | 9.787
1934.7344 | 122.9187 | -60.8459 | 61.9629 | -0.24632 | 0.051351 | 0.050334 | 0.0002848 | 0.00083408 | 0.00011185 | 0.00064087 | -51.9241 | 62.0316 | -61.1984 | 0.027466 | 0.013733 | 0.050354 | 0.14191 | 0.25635 | 0.29755 | -0.19226 | -0.35248 | 0.068664 | 8.9218 | 60.8734 | -61.9492 | 60.6537 | -61.6653 | 9.2743
1935.7656 | 123.0423 | -60.8231 | 61.908 | 0.11989 | 0.050496 | 0.048411 | -0.0024922 | 0.0012615 | -0.0020244 | 0.00042727 | -52.2125 | 61.9125 | -61.1938 | 0.027466 | 0.059509 | 0.073242 | -0.073242 | 0.27466 | 0.21515 | -0.27008 | -0.37079 | 0.004578 | 8.6105 | 60.8505 | -61.8484 | 60.553 | -61.6928 | 8.9813
1936.7344 | 122.9599 | -60.8505 | 61.9446 | -0.13188 | 0.052419 | 0.049052 | 0.0081888 | 0.0023295 | -0.0015972 | -0.00064093 | -51.5854 | 62.0224 | -61.1893 | 0.059509 | 0.032043 | 0.045776 | 0.10071 | 0.26093 | 0.27008 | -0.19684 | -0.33875 | 0.07782 | 9.2651 | 60.91 | -61.9125 | 60.6537 | -61.6745 | 9.6039
1937.7656 | 123.0103 | -60.8185 | 61.9171 | 0.13515 | 0.050924 | 0.052683 | -0.0014242 | -2.0324e-05 | -0.002238 | -0.00085453 | -51.3611 | 61.9217 | -61.2167 | 0.013733 | 0.027466 | 0.027466 | -0.082397 | 0.25177 | 0.21515 | -0.29297 | -0.39825 | 0.004578 | 9.4574 | 60.8322 | -61.8896 | 60.5255 | -61.702 | 9.8557
1938.7344 | 122.9782 | -60.8459 | 61.9492 | -0.10136 | 0.055837 | 0.051615 | 0.0066936 | 0.0021159 | -0.0015972 | -0.0012817 | -51.5854 | 62.0178 | -61.1893 | 0.022888 | 0.013733 | 0.036621 | 0.10986 | 0.27008 | 0.27466 | -0.21515 | -0.34332 | 0.068664 | 9.2606 | 60.8688 | -61.9354 | 60.6308 | -61.6745 | 9.6039
1939.7656 | 123.0286 | -60.8231 | 61.8988 | 0.18093 | 0.051351 | 0.050334 | -0.000356 | 0.0016887 | -0.0033062 | -0.0017089 | -50.9583 | 61.9308 | -61.1984 | 0.018311 | 0.041199 | 0.018311 | -0.082397 | 0.23804 | 0.19684 | -0.27924 | -0.37537 | 0.032043 | 9.8648 | 60.8414 | -61.8576 | 60.5438 | -61.702 | 10.2402
1940.7344 | 122.9004 | -60.8322 | 61.94 | -0.18529 | 0.053701 | 0.049906 | 0.0045574 | 0.00062048 | -0.00052895 | 6.6667e-08 | -51.6312 | 62.0316 | -61.1938 | 0.027466 | 0.022888 | 0.041199 | 0.36163 | 0.66834 | 0.3067 | -0.15106 | -0.36163 | 0.091553 | 9.201 | 60.8597 | -61.9171 | 60.6812 | -61.6333 | 9.5627
1941.7656 | 123.0057 | -60.8276 | 61.9263 | 0.12752 | 0.052419 | 0.050334 | -0.0005696 | 0.00040688 | -0.00095615 | -0.0017089 | -51.3336 | 61.9034 | -61.1755 | 0.23804 | 0.054932 | -0.1831 | -0.14191 | 0.20599 | 0.21515 | -0.27466 | -0.3479 | -0.022889 | 9.494 | 61.0657 | -61.8713 | 60.553 | -61.7111 | 9.8419
1942.7344 | 122.9233 | -60.8414 | 61.9492 | -0.22343 | 0.054342 | 0.052683 | 0.0043436 | -0.00023392 | -0.0011698 | -0.0014953 | -51.2787 | 61.9949 | -61.2076 | 0.022888 | 0.018311 | 0.027466 | 0.14191 | 0.24261 | 0.29755 | -0.20599 | -0.36621 | 0.045776 | 9.5627 | 60.8643 | -61.9308 | 60.6354 | -61.6516 | 9.9289
1943.7656 | 123.0057 | -60.8139 | 61.8988 | 0.27248 | 0.052419 | 0.051402 | 0.0066936 | 0.0027567 | -0.0020244 | -0.0019225 | -51.5076 | 61.9537 | -61.203 | 0 | -0.009155 | -0.054932 | -0.13275 | 0.16479 | 0.1831 | -0.35706 | -0.3891 | 0.054931 | 9.3063 | 60.8139 | -61.908 | 60.4568 | -61.7157 | 9.6954
1944.7344 | 122.937 | -60.8505 | 61.9354 | 0.013079 | 0.054128 | 0.052043 | 0.0060526 | 0.0027567 | -0.00052895 | -0.0019225 | -50.9399 | 62.0132 | -61.2167 | 0.036621 | 0.032043 | 0.054932 | 0.11444 | 0.2243 | 0.28381 | -0.25177 | -0.36621 | 0.07782 | 9.9106 | 60.8871 | -61.9034 | 60.5988 | -61.6516 | 10.2768
1945.7656 | 123.0286 | -60.8276 | 61.8942 | 0.028338 | 0.049001 | 0.048838 | -0.0018514 | 0.0010477 | 0.00032545 | -0.00042733 | -51.9836 | 61.8988 | -61.1938 | 0.027466 | 0.050354 | 0.050354 | -0.064087 | 0.27466 | 0.21515 | -0.28381 | -0.36621 | 0.004578 | 8.844 | 60.8551 | -61.8439 | 60.5438 | -61.6791 | 9.2102
1946.7344 | 122.8455 | -61.7798 | 60.9604 | -0.13188 | 1.2632 | 1.3028 | 0.00413 | -2.0324e-05 | -0.00095615 | -0.0023499 | 59.5596 | 60.878 | -62.0224 | 0.041199 | 0.027466 | 0.054932 | 0.11902 | 0.2655 | 0.27008 | -0.21057 | -0.24262 | -0.082397 | 121.3394 | 61.821 | -60.9329 | 61.5692 | -60.6903 | 121.582
1947.7656 | 122.8912 | -61.7432 | 60.8734 | 0.18855 | 1.181 | 1.2176 | -0.000356 | 0.0014751 | -0.00052895 | -0.0021361 | 59.6512 | 60.791 | -61.9812 | 0.027466 | 0.036621 | 0.022888 | -0.091553 | 0.2243 | 0.19684 | -0.30212 | -0.23804 | -0.082397 | 121.3943 | 61.7706 | -60.8368 | 61.441 | -60.6766 | 121.6324
1948.7344 | 122.8226 | -61.702 | 60.9512 | -0.1624 | 1.3414 | 1.3716 | 0.0071208 | -0.0017293 | -0.00074255 | -0.00085453 | 59.0652 | 60.8688 | -61.9629 | 0.036621 | 0.009155 | 0.022888 | 0.15106 | 0.26093 | 0.29297 | -0.20142 | -0.26093 | -0.082398 | 120.7672 | 61.7386 | -60.9421 | 61.5005 | -60.6583 | 121.0281
1949.75 | 122.7173 | -61.6928 | 60.8688 | 0.10463 | 1.2135 | 1.2261 | 0.010752 | 0.0033977 | -0.0018108 | -0.0017089 | 59.2621 | 60.878 | -61.9675 | 0 | -0.032043 | -0.041199 | 0.018311 | 0.15564 | 0.24261 | -0.31128 | -0.27466 | 0.009156 | 120.9549 | 61.6928 | -60.9009 | 61.3815 | -60.6262 | 121.2296
1950.7344 | 122.7356 | -61.6745 | 60.8917 | -0.50572 | 0.065236 | 0.063578 | 0.0060526 | 0.0038249 | -0.0015972 | -0.0023499 | 58.0856 | 60.9558 | -62.0682 | 0.054932 | 0.045776 | 0.050354 | 0.13275 | 0.23346 | 0.27466 | -0.24261 | -0.39368 | 0.064087 | 119.7601 | 61.7294 | -60.8459 | 61.4319 | -60.6171 | 120.1538
1951.7656 | 122.8226 | -61.6791 | 60.8459 | 0.081743 | 0.063527 | 0.063151 | 7.12e-05 | -0.00087492 | -0.0030924 | -0.0042725 | 58.2687 | 60.8963 | -62.0865 | 0.027466 | 0.045776 | 0.022888 | -0.07782 | 0.22888 | 0.21515 | -0.27466 | -0.40741 | 0.050354 | 119.9478 | 61.7065 | -60.8002 | 61.4044 | -60.6308 | 120.3552
1952.7344 | 122.7722 | -61.7294 | 60.8963 | -0.17003 | 0.06545 | 0.060374 | 0.0049846 | -0.00044752 | -0.0028788 | -0.00042733 | 58.0215 | 60.997 | -62.0544 | 0.14648 | 0.32501 | 0.1831 | -0.29297 | 0.073242 | 0.29755 | -0.14648 | -0.32501 | 0.10071 | 119.751 | 61.8759 | -60.5713 | 61.5829 | -60.5988 | 120.076
1953.7656 | 122.7676 | -61.7569 | 60.8734 | 0.2267 | 0.067159 | 0.062724 | 0.0081888 | 0.0042521 | -0.0011698 | -0.0036315 | 58.1955 | 61.0245 | -62.1002 | -0.027466 | -0.054932 | -0.086975 | -0.004578 | 0.10071 | 0.21515 | -0.36621 | -0.34332 | 0.15106 | 119.9524 | 61.7294 | -60.9283 | 61.3907 | -60.6583 | 120.2957
1954.7344 | 122.8455 | -61.7157 | 60.8963 | -0.2158 | 0.061391 | 0.063792 | -0.0009968 | 0.00083408 | -0.0041606 | -0.0012817 | 58.223 | 60.9421 | -62.0728 | 0.082397 | 0.086975 | 0.10071 | 0.068665 | 0.31586 | 0.2655 | -0.2243 | -0.35706 | 0.045777 | 119.9387 | 61.7981 | -60.8093 | 61.4914 | -60.6308 | 120.2957
1955.7656 | 122.937 | -61.6928 | 60.8643 | 1.333 | 0.063955 | 0.05781 | 0.0022074 | 0.00040688 | -0.00095615 | -0.00064093 | 58.5159 | 60.8826 | -62.0865 | 0.050354 | 0.07782 | 0.050354 | -0.2243 | 0.20599 | 0.18768 | -0.3067 | -0.39368 | 0.01831 | 120.2087 | 61.7432 | -60.7864 | 61.3861 | -60.6766 | 120.6024
1956.7344 | 122.8043 | -61.7386 | 60.9238 | -0.20054 | 0.06545 | 0.062297 | 0.0051982 | -0.0030111 | -0.0015972 | 0.00021367 | 59.5093 | 61.0336 | -62.1094 | -0.1831 | -0.22888 | 0.004578 | 0.21515 | 0.16479 | 0.30212 | -0.17853 | -0.37079 | 0.10986 | 121.2479 | 61.5555 | -61.1526 | 61.5601 | -60.6216 | 121.6187
1957.75 | 122.85 | -61.7523 | 60.8963 | 0.15804 | 0.066091 | 0.066355 | 0.0088298 | 0.0042521 | -0.00052895 | -0.0027771 | 59.6191 | 61.0245 | -62.114 | 0.050354 | 0.013733 | 0.013733 | 0.022888 | 0.21515 | 0.24719 | -0.28839 | -0.36163 | 0.12817 | 121.3715 | 61.8027 | -60.8826 | 61.4639 | -60.6491 | 121.7331
1958.7344 | 122.8363 | -61.7752 | 60.9055 | -0.24632 | 0.065664 | 0.060588 | 0.0039164 | 0.0012615 | -0.00074255 | -0.0023499 | 59.5184 | 60.9787 | -62.1048 | 0.032043 | 0.032043 | 0.022888 | 0.15106 | 0.25177 | 0.28381 | -0.19226 | -0.32959 | 0.073242 | 121.2936 | 61.8073 | -60.8734 | 61.5829 | -60.6216 | 121.6232
1959.7656 | 122.8134 | -61.7889 | 60.8871 | 0.11226 | 0.068868 | 0.069773 | 0.0077616 | 0.0046793 | -0.0035198 | -0.0023499 | 59.5825 | 61.0153 | -62.1323 | -0.054932 | -0.068665 | -0.10071 | 0.004578 | 0.086975 | 0.21515 | -0.35248 | -0.34332 | 0.12817 | 121.3715 | 61.734 | -60.9558 | 61.4365 | -60.672 | 121.7148
1960.7344 | 122.9141 | -61.7386 | 60.8871 | -0.093733 | 0.062459 | 0.059092 | -0.002065 | 0.0012615 | 0.00011185 | -0.00064093 | 59.6146 | 60.9467 | -62.0911 | 0.09613 | 0.11444 | 0.13275 | 0.036621 | 0.36163 | 0.26093 | -0.21515 | -0.35248 | 0.059509 | 121.3531 | 61.8347 | -60.7727 | 61.5234 | -60.6262 | 121.7056
1961.7656 | 122.9279 | -61.7386 | 60.8826 | 0.028338 | 0.0631 | 0.063365 | -0.002065 | 0.00062048 | -0.0035198 | -0.00085453 | 59.5779 | 60.9192 | -62.1185 | 0.07782 | 0.10071 | 0.09613 | -0.064087 | 0.32044 | 0.21515 | -0.25635 | -0.37994 | 0.036621 | 121.3165 | 61.8164 | -60.7819 | 61.4822 | -60.6674 | 121.6965
1962.7344 | 122.8821 | -61.734 | 60.9192 | -0.20817 | 0.0631 | 0.063365 | 0.00413 | -0.0010885 | -0.00010175 | -0.0017089 | 59.5963 | 60.9467 | -62.114 | 0.054932 | 0.041199 | 0.086975 | 0.14191 | 0.27924 | 0.28381 | -0.21973 | -0.37994 | 0.027466 | 121.3303 | 61.7889 | -60.878 | 61.5143 | -60.6354 | 121.7102
1963.7656 | 122.8134 | -61.7935 | 60.9055 | 0.15041 | 0.067373 | 0.065501 | 0.010325 | 0.0019023 | -0.0015972 | -0.00042733 | 59.5642 | 61.0428 | -62.1185 | -0.07782 | -0.086975 | -0.12817 | 0.013733 | 0.091553 | 0.20599 | -0.33875 | -0.32501 | 0.13733 | 121.3577 | 61.7157 | -60.9924 | 61.4548 | -60.6995 | 121.6827
1964.7344 | 122.8546 | -61.7661 | 60.9375 | -0.20817 | 0.065023 | 0.059519 | 0.0019938 | 0.00062048 | -0.0011698 | -0.0017089 | 59.5505 | 60.997 | -62.1231 | 0.018311 | 0.032043 | 0.045776 | 0.15564 | 0.27466 | 0.28839 | -0.20142 | -0.35706 | 0.059509 | 121.3165 | 61.7844 | -60.9055 | 61.5646 | -60.6491 | 121.6736
1965.7656 | 122.9645 | -61.7386 | 60.8871 | 0.3564 | 0.063527 | 0.064433 | 0.0062662 | 0.0031841 | -0.0015972 | -0.00064093 | 59.642 | 60.9512 | -62.146 | 0.045776 | 0.027466 | 0.013733 | -0.21057 | 0.21057 | 0.16937 | -0.38452 | -0.40741 | 0.064087 | 121.3806 | 61.7844 | -60.8597 | 61.3541 | -60.7178 | 121.788
1966.7344 | 122.8455 | -61.7477 | 60.9329 | -0.33024 | 0.063314 | 0.059519 | 7.12e-05 | 0.00019328 | 0.00011185 | -0.00042733 | 59.5779 | 60.9924 | -62.114 | 0.018311 | 0.022888 | 0.068665 | 0.15106 | 0.28381 | 0.28381 | -0.1831 | -0.36621 | 0.05951 | 121.3257 | 61.7661 | -60.91 | 61.5646 | -60.6491 | 121.6919
1967.7656 | 122.9736 | -61.734 | 60.8917 | -1.4441 | 0.062673 | 0.064219 | 0.0004984 | -0.00023392 | -0.0015972 | -0.0019225 | 59.5184 | 60.9146 | -62.1094 | 0.086975 | 0.050354 | 0.14191 | 0.013733 | 0.37079 | 0.21973 | -0.24261 | -0.37537 | 0.022888 | 121.2524 | 61.821 | -60.8414 | 61.4914 | -60.672 | 121.6278
1968.7344 | 122.8592 | -61.7615 | 60.9375 | -0.20817 | 0.065023 | 0.061869 | 0.0019938 | -0.00044752 | -0.00074255 | 6.6667e-08 | 59.6603 | 60.9375 | -62.1094 | 0.068665 | 0.068665 | 0.091553 | 0.082397 | 0.31128 | 0.27924 | -0.2243 | -0.3479 | 0 | 121.4218 | 61.8301 | -60.8688 | 61.5372 | -60.6583 | 121.7697
1969.75 | 122.937 | -61.7844 | 60.9192 | 0.23433 | 0.066945 | 0.061015 | 0.0090434 | 0.0023295 | -0.00095615 | -0.0027771 | 59.6283 | 61.0199 | -62.1231 | -0.041199 | -0.068665 | -0.10071 | -0.068665 | -0.52643 | 0.20142 | -0.40283 | -0.33875 | 0.10071 | 121.4127 | 61.7432 | -60.9879 | 61.3815 | -60.7178 | 121.7514
1970.7344 | 122.9416 | -61.7752 | 60.9146 | -0.17766 | 0.063741 | 0.062083 | -0.0022786 | 0.0010477 | -0.00031535 | -0.0019225 | 59.6649 | 60.9467 | -62.1231 | 0.10529 | 0.11444 | 0.13733 | 0.036621 | 0.3479 | 0.2655 | -0.21515 | -0.3479 | 0.032043 | 121.4401 | 61.8805 | -60.8002 | 61.5601 | -60.6491 | 121.788
1971.7656 | 123.0148 | -61.7065 | 60.9192 | -0.093733 | 0.061391 | 0.06016 | -0.0018514 | -0.00023392 | -0.0018108 | -0.0017089 | 59.7015 | 60.9009 | -62.1231 | 0.13733 | 0.13733 | 0.17853 | -0.036621 | 0.37537 | 0.24719 | -0.19684 | -0.41656 | -0.01831 | 121.4081 | 61.8439 | -60.7819 | 61.5097 | -60.672 | 121.8246
1972.7344 | 122.8821 | -61.7523 | 60.9146 | -0.20817 | 0.062887 | 0.060374 | 0.0009258 | -0.0010885 | -0.0015972 | -0.00064093 | 59.6741 | 60.9283 | -62.1048 | 0.059509 | 0.054932 | 0.068665 | 0.082397 | 0.27924 | 0.27924 | -0.16937 | -0.35248 | 0.013733 | 121.4264 | 61.8118 | -60.8597 | 61.5829 | -60.6354 | 121.7789
1973.7656 | 122.8546 | -61.8118 | 60.9283 | 0.18093 | 0.068868 | 0.064433 | 0.0094706 | 0.0029705 | -0.00031535 | -0.0034179 | 59.6695 | 61.0245 | -62.146 | -0.059509 | -0.086975 | -0.11902 | 0.004578 | 0.073242 | 0.22888 | -0.37079 | -0.33417 | 0.09613 | 121.4813 | 61.7523 | -61.0153 | 61.441 | -60.6995 | 121.8155
1974.7344 | 122.9599 | -61.7477 | 60.8871 | -0.12425 | 0.060964 | 0.059733 | -0.0009968 | -0.00066112 | -0.00031535 | -0.0021361 | 59.7061 | 60.9329 | -62.1185 | 0.24261 | 0.60425 | 0.54474 | -0.64545 | -0.045776 | 0.27466 | -0.18768 | -0.37079 | 0.045776 | 121.4539 | 61.9904 | -60.2829 | 61.5601 | -60.6125 | 121.8246
1975.7656 | 122.9599 | -61.7294 | 60.8688 | 0.26485 | 0.062887 | 0.058024 | 0.0051982 | 0.0012615 | -0.00052895 | 0.00021367 | 59.729 | 60.9512 | -62.1185 | 0.050354 | 0.059509 | -0.1831 | -0.63171 | 0.36621 | 0.13275 | -0.4303 | -0.3891 | 0.082398 | 121.4584 | 61.7798 | -60.8093 | 61.2991 | -60.7361 | 121.8475
1976.75 | 122.8317 | -61.8164 | 60.9375 | 0.2267 | 0.067586 | 0.063578 | 0.010752 | 0.0025431 | -0.0011698 | -0.0025635 | 59.6741 | 61.0107 | -62.1414 | -0.045776 | -0.068665 | -0.11444 | -0.013733 | 0.073242 | 0.2243 | -0.36163 | -0.32501 | 0.073242 | 121.4905 | 61.7706 | -61.0062 | 61.4548 | -60.7132 | 121.8155
1977.7656 | 122.9279 | -61.7477 | 60.8917 | 0.21144 | 0.064382 | 0.061228 | -0.0048422 | -0.00044752 | -0.00052895 | 0.0012817 | 59.6603 | 60.9009 | -62.1506 | 0.027466 | 0.022888 | 0.022888 | -0.11902 | 0.20142 | 0.18768 | -0.32044 | -0.40283 | 0.009155 | 121.4081 | 61.7752 | -60.8688 | 61.4273 | -60.704 | 121.8109
1978.7344 | 122.9233 | -61.7523 | 60.9375 | -0.20054 | 0.061391 | 0.055033 | -0.0001424 | -0.0027975 | -0.0015972 | 0.00042727 | 59.7015 | 60.9558 | -62.114 | 0.091553 | 0.10071 | 0.12817 | 0.059509 | 0.34332 | 0.27466 | -0.21515 | -0.36163 | 0.018311 | 121.4539 | 61.8439 | -60.8368 | 61.5372 | -60.6628 | 121.8155
1979.7656 | 122.8958 | -61.7844 | 60.8917 | 0.21907 | 0.066091 | 0.064006 | 0.0084026 | 0.0019023 | -0.0026652 | -0.0012817 | 59.6878 | 61.0016 | -62.1643 | -0.032043 | -0.027466 | -0.07782 | -0.086975 | 0.11902 | 0.19226 | -0.3479 | -0.37994 | 0.10986 | 121.4722 | 61.7523 | -60.9192 | 61.4365 | -60.6995 | 121.8521
1980.7344 | 122.9965 | -61.734 | 60.9192 | -0.13951 | 0.060964 | 0.061228 | -0.0014242 | 0.00019328 | -0.0020244 | -0.0010681 | 59.761 | 60.9375 | -62.1277 | 0.13275 | 0.12817 | 0.16022 | -0.041199 | 0.37537 | 0.23346 | -0.21973 | -0.39368 | 0.018311 | 121.4951 | 61.8668 | -60.791 | 61.5143 | -60.6857 | 121.8887
1981.7656 | 122.9324 | -61.7386 | 60.9421 | -0.1624 | 0.064382 | 0.058451 | 0.0022074 | 0.0010477 | -0.0015972 | -0.00021353 | 59.7427 | 60.9512 | -62.1185 | 0.10529 | 0.091553 | 0.10986 | 0.054932 | 0.32959 | 0.27008 | -0.20599 | -0.37994 | 0.009155 | 121.4813 | 61.8439 | -60.8505 | 61.5326 | -60.672 | 121.8613
1982.7344 | 122.9828 | -61.7523 | 60.9421 | -0.49046 | 0.062032 | 0.063578 | 0.000712 | -0.00044752 | -0.0013834 | -0.0017089 | 59.5917 | 60.9238 | -62.1185 | 0.082397 | 0.091553 | 0.20142 | -0.004578 | 0.3479 | 0.23346 | -0.24719 | -0.36621 | -0.018311 | 121.344 | 61.8347 | -60.8505 | 61.5051 | -60.7086 | 121.7102
1983.7656 | 122.9919 | -61.7752 | 60.8551 | 0.16567 | 0.064596 | 0.062724 | 0.0066936 | 0.0019023 | -0.00031535 | -0.0010681 | 59.7794 | 60.9329 | -62.1185 | 0.045776 | 0.018311 | 0.022888 | -0.20599 | 0.2243 | 0.17395 | -0.37079 | -0.34332 | 0.077819 | 121.5546 | 61.821 | -60.8368 | 61.4044 | -60.6812 | 121.8979
1984.7344 | 122.9828 | -61.7294 | 60.9329 | -0.12425 | 0.061818 | 0.058238 | 0.0009258 | -0.00066112 | -0.002238 | -0.0029907 | 59.7656 | 60.9283 | -62.0956 | 0.11902 | 0.09613 | 0.13275 | 0.036621 | 0.36163 | 0.27008 | -0.2243 | -0.36621 | -0.004577 | 121.4951 | 61.8484 | -60.8368 | 61.5051 | -60.6628 | 121.8613
1985.7656 | 122.8867 | -61.7935 | 60.9329 | 0.21907 | 0.066732 | 0.063792 | 0.0096842 | 0.0027567 | 0.0016072 | -0.0034179 | 59.7107 | 61.0153 | -62.178 | -0.045776 | -0.059509 | -0.086975 | -0.013733 | 0.11444 | 0.21973 | -0.34332 | -0.38452 | 0.082398 | 121.5042 | 61.7477 | -60.9924 | 61.4502 | -60.7132 | 121.8887
1986.75 | 122.85 | -61.8164 | 60.9146 | 0.14278 | 0.0631 | 0.066142 | 0.007548 | 0.0057475 | -0.003947 | -0.0023499 | 59.697 | 60.9924 | -62.178 | -0.054932 | -0.073242 | -0.091553 | 0.009155 | 0.073242 | 0.22888 | -0.34332 | -0.36163 | 0.07782 | 121.5134 | 61.7615 | -60.9879 | 61.4731 | -60.6857 | 121.875
1987.7656 | 123.0103 | -61.7661 | 60.8643 | 0.27248 | 0.064382 | 0.061656 | 0.0009258 | 0.0021159 | 0.0018208 | 0.00064087 | 59.7931 | 60.9283 | -62.1277 | 0.059509 | 0.050354 | 0.036621 | -0.1831 | 0.21515 | 0.18768 | -0.3479 | -0.36163 | 0.064087 | 121.5591 | 61.8256 | -60.8139 | 61.4182 | -60.6766 | 121.9208
1988.7344 | 123.0286 | -61.7294 | 60.9192 | -0.025068 | 0.0631 | 0.060801 | 0.000712 | -0.00066112 | -0.0028788 | -0.0019225 | 59.7748 | 60.9375 | -62.114 | 0.13275 | 0.13733 | 0.15564 | -0.073242 | 0.38452 | 0.23346 | -0.21515 | -0.38452 | 0.018311 | 121.5042 | 61.8622 | -60.7819 | 61.5143 | -60.6857 | 121.8887
1989.7656 | 122.9919 | -61.7661 | 60.8963 | 0.2267 | 0.066091 | 0.061656 | 0.0069072 | 0.0023295 | 0.00053925 | -0.0029907 | 59.7748 | 60.9787 | -62.1323 | 0.041199 | 0.050354 | 0.013733 | -0.20142 | 0.21515 | 0.17853 | -0.38452 | -0.36621 | 0.082398 | 121.5408 | 61.8073 | -60.8459 | 61.3815 | -60.7178 | 121.907
1990.7344 | 122.9233 | -61.7249 | 60.8826 | -0.17003 | 0.061818 | 0.059519 | -0.0001424 | -0.00087492 | -0.0018108 | 0.0021363 | 59.7794 | 60.9375 | -62.1277 | 0.1236 | 0.12817 | 0.17395 | -0.045776 | 0.70038 | 0.24719 | -0.17853 | -0.40283 | 0.054932 | 121.5042 | 61.8484 | -60.7544 | 61.5463 | -60.6354 | 121.907
1991.7656 | 122.9187 | -61.7706 | 60.9421 | 0.11989 | 0.064168 | 0.061442 | 0.0090434 | 0.0019023 | -0.00095615 | -0.0034179 | 59.8114 | 61.0382 | -62.1094 | 0.054932 | 0.018311 | 0.009155 | 0.013733 | 0.21057 | 0.24261 | -0.28381 | -0.33875 | 0.09613 | 121.582 | 61.8256 | -60.9238 | 61.4868 | -60.6995 | 121.9208
1992.7344 | 122.9782 | -61.7386 | 60.8963 | -0.23869 | 0.061391 | 0.057383 | 0.000712 | 0.00019328 | -0.0013834 | 0.00085447 | 59.7885 | 60.9375 | -62.1323 | 0.13275 | 0.11444 | 0.13275 | 0 | 0.34332 | 0.24261 | -0.22888 | -0.39368 | 0.041199 | 121.5271 | 61.8713 | -60.7819 | 61.5097 | -60.6537 | 121.9208
1993.7656 | 122.9553 | -61.7752 | 60.8917 | 0.25722 | 0.066945 | 0.061228 | 0.0073344 | 0.0031841 | -0.00052895 | -0.0027771 | 59.7839 | 61.0062 | -62.1414 | 0 | -0.018311 | -0.050354 | -0.11902 | 0.15106 | 0.19684 | -0.36163 | -0.36621 | 0.11444 | 121.5591 | 61.7752 | -60.91 | 61.4136 | -60.6949 | 121.9254
1994.7344 | 123.0423 | -61.7249 | 60.9283 | -0.040327 | 0.06075 | 0.061015 | -0.0031332 | 0.0010477 | -0.0011698 | -0.0010681 | 59.8068 | 60.9238 | -62.1414 | 0.11902 | 0.15564 | 0.16937 | -0.068665 | 0.3891 | 0.2243 | -0.19684 | -0.41656 | -0.004578 | 121.5317 | 61.8439 | -60.7727 | 61.528 | -60.704 | 121.9482
1995.7656 | 122.8729 | -61.8301 | 60.9375 | 0.11989 | 0.067586 | 0.062724 | 0.009257 | 0.0055339 | -0.0028788 | -0.0017089 | 59.7977 | 61.0703 | -62.1277 | -0.036621 | -0.059509 | -0.10071 | 0 | 0.10529 | 0.22888 | -0.37994 | -0.29755 | 0.13275 | 121.6278 | 61.7935 | -60.997 | 61.4502 | -60.7086 | 121.9254
1996.7344 | 123.0606 | -61.7523 | 60.9055 | -0.12425 | 0.058614 | 0.061015 | -0.0022786 | 0.00083408 | -0.0026652 | 0.00064087 | 59.8206 | 60.9238 | -62.1414 | 0.13275 | 0.11444 | 0.84228 | 0.36621 | -0.11444 | 0.29297 | -0.16479 | -0.3891 | 0.01831 | 121.5729 | 61.8851 | -60.791 | 61.5875 | -60.6125 | 121.962
1997.7656 | 122.8867 | -61.8027 | 60.9375 | 0.12752 | 0.068014 | 0.062937 | 0.0081888 | 0.0038249 | -0.003947 | -0.0017089 | 59.8297 | 61.0611 | -62.1368 | -0.009155 | -0.050354 | -0.073242 | 0.027466 | 0.13733 | 0.23346 | -0.33417 | -0.33417 | 0.1236 | 121.6324 | 61.7935 | -60.9879 | 61.4685 | -60.704 | 121.9666
1998.7344 | 123.0011 | -61.7477 | 60.9283 | -0.26158 | 0.062246 | 0.061656 | -0.000356 | 0.0010477 | -0.0028788 | -0.0017089 | 59.8389 | 60.9467 | -62.1231 | 0.10986 | 0.10986 | 0.14648 | 0 | 0.37079 | 0.24261 | -0.21973 | -0.37537 | 0.01831 | 121.5866 | 61.8576 | -60.8185 | 61.528 | -60.6857 | 121.962
1999.7656 | 122.9965 | -61.7615 | 60.8688 | 0.23433 | 0.063314 | 0.058024 | 0.0049846 | 0.0023295 | -0.0013834 | -0.00064093 | 59.8846 | 60.9512 | -62.146 | 0.041199 | 0.045776 | 0.027466 | -0.19684 | 0.2243 | 0.16022 | -0.37537 | -0.38452 | 0.082398 | 121.6461 | 61.8027 | -60.8231 | 61.3861 | -60.7086 | 122.0306
2000.7344 | 123.0011 | -61.7477 | 60.9421 | -2.3826 | 0.06075 | 0.060588 | -0.0005696 | 0.0010477 | -0.003947 | -0.00042733 | 59.7427 | 60.9558 | -62.1185 | 0.16022 | 0.059509 | 0.068665 | -0.009155 | 0.37537 | 0.22888 | -0.24719 | -0.37079 | 0.013733 | 121.4905 | 61.908 | -60.8826 | 61.5006 | -60.7132 | 121.8613
2001.7656 | 122.9187 | -61.7844 | 60.9238 | -0.017439 | 0.06545 | 0.065928 | 0.0096842 | 0.0025431 | -0.0024516 | -0.0014953 | 59.9075 | 61.0291 | -62.1277 | 0 | -0.018311 | -0.027466 | 0.004578 | 0.17395 | 0.24261 | -0.31128 | -0.34332 | 0.10529 | 121.6919 | 61.7844 | -60.9421 | 61.4731 | -60.6812 | 122.0352
2002.7344 | 123.0148 | -61.7661 | 60.9055 | -0.0098092 | 0.062032 | 0.059306 | -0.0022786 | -0.0017293 | -0.00010175 | -0.00085453 | 59.8434 | 60.9329 | -62.1643 | 0.10529 | 0.11902 | 0.11444 | -0.068665 | 0.34332 | 0.21515 | -0.25635 | -0.39825 | 0.027465 | 121.6095 | 61.8713 | -60.7864 | 61.5097 | -60.6903 | 122.0078
2003.7656 | 123.0011 | -61.7981 | 60.91 | 0.28011 | 0.06545 | 0.063578 | 0.0049846 | 0.00062048 | 0.00053925 | 0.0010681 | 59.8709 | 61.0107 | -62.1277 | 0.004578 | 0.009155 | 0 | -0.16022 | 0.19226 | 0.17395 | -0.37537 | -0.32959 | 0.10071 | 121.669 | 61.8027 | -60.9009 | 61.4227 | -60.7361 | 121.9986
2004.7344 | 123.0515 | -61.7615 | 60.8963 | -0.070844 | 0.061818 | 0.059733 | -0.0016378 | -0.00023392 | -0.0018108 | -0.0019225 | 59.8892 | 60.9329 | -62.1414 | 0.12817 | 0.15564 | 0.17853 | -0.050354 | 0.40283 | 0.22888 | -0.20142 | -0.37994 | 0.036621 | 121.6507 | 61.8896 | -60.7407 | 61.5601 | -60.6674 | 122.0306
2005.7656 | 122.8912 | -61.7889 | 60.9192 | 0.0054493 | 0.064382 | 0.062724 | 0.0090434 | 0.00083408 | -0.00010175 | -0.0017089 | 59.9075 | 61.0474 | -62.1323 | 0.032043 | -0.018311 | -0.036621 | 0.004578 | 0.16937 | 0.23346 | -0.31586 | -0.34332 | 0.12817 | 121.6965 | 61.821 | -60.9375 | 61.4731 | -60.6857 | 122.0398
2006.7344 | 123.0194 | -61.7569 | 60.9146 | -0.17766 | 0.062673 | 0.06251 | 0.0011394 | 0.0019023 | -0.0018108 | -0.0012817 | 59.9075 | 60.9192 | -62.1368 | 0.13275 | 0.13733 | 0.16022 | -0.050354 | 0.38452 | 0.25177 | -0.21973 | -0.37994 | 0.004577 | 121.6644 | 61.8896 | -60.7773 | 61.5372 | -60.6628 | 122.0444
2007.7656 | 122.9187 | -61.7798 | 60.9467 | -0.055586 | 0.065023 | 0.066355 | 0.0088298 | 0.0038249 | -0.0011698 | -0.0017089 | 59.9396 | 61.0703 | -62.146 | 0.1236 | 0.10071 | 0.054932 | 0.050354 | 0.2243 | 0.24719 | -0.28839 | -0.36621 | 0.1236 | 121.7194 | 61.9034 | -60.8459 | 61.4914 | -60.6995 | 122.0856
2008.7344 | 123.0103 | -61.7569 | 60.9055 | 0.028338 | 0.057332 | 0.055033 | -0.0018514 | 0.0025431 | -0.0020244 | -0.00021353 | 59.8343 | 60.9512 | -62.1643 | 0.054932 | 0.091553 | 0.09613 | -0.059509 | 0.3067 | 0.21973 | -0.25177 | -0.40741 | 0.045776 | 121.5912 | 61.8118 | -60.8139 | 61.5051 | -60.6857 | 121.9986
2009.75 | 122.8912 | -61.7889 | 60.965 | -0.22343 | 0.062887 | 0.062083 | 0.0026346 | -2.0324e-05 | -0.0011698 | -0.00085453 | 59.8526 | 61.0428 | -62.1414 | 0.032043 | 0.018311 | 0.022888 | 0.14648 | 0.23346 | 0.28839 | -0.20599 | -0.35248 | 0.07782 | 121.6415 | 61.821 | -60.9467 | 61.5829 | -60.6766 | 121.994
2010.7344 | 123.024 | -61.7615 | 60.91 | -0.0021797 | 0.062032 | 0.056742 | -0.0009968 | -0.00044752 | 0.0013936 | 0.00064087 | 59.8892 | 60.9238 | -62.1231 | 0.07782 | 0.082397 | 0.10986 | -0.082397 | 0.30212 | 0.23346 | -0.25635 | -0.36163 | 0.013733 | 121.6507 | 61.8393 | -60.8276 | 61.5051 | -60.6766 | 122.0123
2011.7656 | 122.8821 | -61.7981 | 60.9421 | 0.14278 | 0.064809 | 0.065074 | 0.010112 | 0.0025431 | -0.00095615 | -0.0042725 | 59.9304 | 61.0336 | -62.146 | 0.004578 | -0.068665 | -0.073242 | 0.032043 | 0.14191 | 0.22888 | -0.32044 | -0.3479 | 0.091552 | 121.7285 | 61.8027 | -61.0107 | 61.4777 | -60.7132 | 122.0764
2012.7344 | 123.0148 | -61.7752 | 60.9238 | -0.0098092 | 0.061818 | 0.056529 | -0.0005696 | 0.00062048 | -0.00074255 | -0.0027771 | 59.9121 | 60.9238 | -62.1368 | 0.086975 | 0.09613 | 0.10071 | -0.082397 | 0.32501 | 0.2243 | -0.24719 | -0.36163 | 0 | 121.6873 | 61.8622 | -60.8276 | 61.528 | -60.6995 | 122.0489
2013.7656 | 122.9095 | -61.8118 | 60.965 | -0.17766 | 0.065023 | 0.059733 | 0.0049846 | 0.0021159 | -0.0028788 | -0.0027771 | 59.9167 | 61.0657 | -62.1185 | 0.041199 | 0.018311 | 0.032043 | 0.12817 | 0.24719 | 0.27466 | -0.2243 | -0.3067 | 0.10071 | 121.7285 | 61.853 | -60.9467 | 61.5875 | -60.6903 | 122.0352
2014.7344 | 123.0011 | -61.7844 | 60.9192 | 0.11989 | 0.062246 | 0.056956 | -0.002065 | 0.00040688 | -0.0013834 | 0.00042727 | 59.8709 | 60.9421 | -62.178 | 0.045776 | 0.054932 | 0.068665 | -0.059509 | 0.2655 | 0.20599 | -0.27466 | -0.39368 | 0.022889 | 121.6553 | 61.8301 | -60.8643 | 61.5097 | -60.7132 | 122.049
2015.7656 | 123.0011 | -61.7569 | 60.9375 | 0.043596 | 0.058614 | 0.054179 | 0.000712 | -0.0021565 | -0.00052895 | -0.00064093 | 59.9121 | 60.9283 | -62.146 | 0.054932 | 0.07782 | 0.082397 | -0.045776 | 0.29755 | 0.21973 | -0.26093 | -0.3891 | -0.009155 | 121.669 | 61.8118 | -60.8597 | 61.496 | -60.7178 | 122.0581
2016.7344 | 122.9965 | -61.7752 | 60.9009 | 0.20381 | 0.060964 | 0.056529 | 0.0022074 | -0.0013021 | -0.00052895 | -0.00064093 | 59.9396 | 60.9329 | -62.1552 | 0.022888 | 0.027466 | -0.013733 | -0.13275 | 0.20599 | 0.17395 | -0.32959 | -0.37994 | 0.032043 | 121.7148 | 61.7981 | -60.8734 | 61.4456 | -60.7269 | 122.0947
2017.7656 | 122.9507 | -61.7889 | 60.9467 | -0.078474 | 0.062246 | 0.066996 | 0.0084026 | 0.0012615 | -0.0013834 | -0.0023499 | 60.0174 | 61.0748 | -62.1414 | 0.073242 | 0.022888 | 0.027466 | 0.027466 | 0.24719 | 0.25635 | -0.28839 | -0.35248 | 0.12817 | 121.8063 | 61.8622 | -60.9238 | 61.5005 | -60.6903 | 122.1588
2018.7344 | 122.9691 | -61.7798 | 60.9192 | 0.23433 | 0.063314 | 0.059306 | 7.12e-05 | 0.0021159 | -0.00052895 | -0.0014953 | 59.9579 | 60.91 | -62.1597 | 0.036621 | 0.032043 | 0.013733 | -0.1236 | 0.20599 | 0.19226 | -0.31586 | -0.37994 | -0.009155 | 121.7377 | 61.8164 | -60.8871 | 61.4639 | -60.7269 | 122.1176
2019.7656 | 122.9462 | -61.7889 | 60.9375 | -0.0021797 | 0.063955 | 0.06486 | 0.0086162 | 0.0057475 | -0.00095615 | -0.0025635 | 60.0174 | 61.0474 | -62.1368 | 0.059509 | 0.027466 | 0.004578 | 0.004578 | 0.21973 | 0.24261 | -0.30212 | -0.3479 | 0.10986 | 121.8063 | 61.8484 | -60.91 | 61.4868 | -60.6949 | 122.1542
2020.7344 | 122.9782 | -61.7889 | 60.9238 | 0.18855 | 0.063741 | 0.062297 | -0.0001424 | 0.0012615 | 0.00011185 | -0.0023499 | 59.935 | 60.9283 | -62.1643 | 0.009155 | 0.027466 | 0.009155 | -0.10071 | 0.21973 | 0.18768 | -0.29755 | -0.37537 | 0.004578 | 121.7239 | 61.7981 | -60.8963 | 61.4914 | -60.7361 | 122.0993
2021.7656 | 122.8912 | -61.7935 | 60.9512 | -0.15477 | 0.061605 | 0.05781 | 0.0051982 | 0.00062048 | 0.00075285 | -0.0014953 | 59.9258 | 61.0565 | -62.178 | 0.032043 | 0.022888 | 0.032043 | 0.13733 | 0.22888 | 0.29297 | -0.21057 | -0.38452 | 0.10529 | 121.7194 | 61.8256 | -60.9283 | 61.5829 | -60.6583 | 122.1039
2022.7344 | 122.9965 | -61.7615 | 60.8963 | 0.27248 | 0.064382 | 0.061015 | 0.0037028 | 0.0016887 | -0.00031535 | 0.00042727 | 60.0266 | 60.9283 | -62.1552 | 0.050354 | 0.050354 | 0.036621 | -0.19684 | 0.24261 | 0.1831 | -0.36163 | -0.39368 | 0.032044 | 121.788 | 61.8118 | -60.8459 | 61.3998 | -60.7132 | 122.1817
2023.7656 | 122.905 | -61.8073 | 60.965 | -0.15477 | 0.062673 | 0.059306 | 0.0032756 | -0.0025837 | -0.00052895 | -0.0014953 | 59.9442 | 61.0245 | -62.1597 | 0.027466 | 0.041199 | 0.041199 | 0.15564 | 0.2655 | 0.28839 | -0.20142 | -0.35248 | 0.059509 | 121.7514 | 61.8347 | -60.9238 | 61.6058 | -60.6766 | 122.1039
2024.7344 | 123.0011 | -61.7889 | 60.9192 | 0.29537 | 0.063955 | 0.062724 | 0.0034892 | 0.0019023 | -0.0030924 | -0.0012817 | 60.0311 | 60.9695 | -62.1323 | 0.07782 | 0.045776 | 0.041199 | -0.20599 | 0.25177 | 0.16022 | -0.37079 | -0.34332 | 0.050354 | 121.8201 | 61.8668 | -60.8734 | 61.4182 | -60.759 | 122.1634
2025.7656 | 122.937 | -61.7935 | 60.9375 | -0.2158 | 0.060323 | 0.059306 | 0.0032756 | -0.0013021 | -0.0015972 | -0.0025635 | 60.0037 | 60.965 | -62.1323 | 0.09613 | 0.07782 | 0.10071 | 0.082397 | 0.29755 | 0.27924 | -0.20599 | -0.33875 | 0.027466 | 121.7972 | 61.8896 | -60.8597 | 61.5875 | -60.6583 | 122.1359
2026.7344 | 123.0103 | -61.7844 | 60.9055 | 0.26485 | 0.061818 | 0.06251 | 0.0039164 | 0.0012615 | -0.00010175 | -0.00085453 | 60.0632 | 60.9421 | -62.1323 | 0.059509 | 0.050354 | 0.036621 | -0.20142 | 0.22888 | 0.17395 | -0.36163 | -0.3479 | 0.036621 | 121.8475 | 61.8439 | -60.8551 | 61.4227 | -60.7315 | 122.1954
2027.7656 | 123.0515 | -61.7386 | 60.91 | -0.19291 | 0.060964 | 0.059306 | 0.0011394 | -0.0023701 | -0.0013834 | -0.0021361 | 60.0632 | 60.9329 | -62.146 | 0.1236 | 0.10986 | 0.15564 | -0.022888 | 0.37537 | 0.23346 | -0.21973 | -0.40741 | 0.022888 | 121.8018 | 61.8622 | -60.8002 | 61.5189 | -60.6766 | 122.2092
2028.7344 | 123.0286 | -61.7615 | 60.91 | 0.27248 | 0.064809 | 0.063792 | 0.0062662 | 0.00083408 | 0.00032545 | -0.00064093 | 60.0769 | 60.9695 | -62.1368 | 0.054932 | 0.036621 | 0.018311 | -0.19684 | 0.21515 | 0.15564 | -0.3891 | -0.37537 | 0.059509 | 121.8384 | 61.8164 | -60.8734 | 61.3724 | -60.7544 | 122.2137
2029.7656 | 122.9828 | -61.7661 | 60.9467 | -0.1624 | 0.060109 | 0.059519 | -0.0001424 | -0.0013021 | -0.0020244 | -0.0010681 | 60.0586 | 60.9787 | -62.114 | 0.11902 | 0.10986 | 0.14191 | 0.022888 | 0.36163 | 0.25635 | -0.20142 | -0.3479 | 0.032044 | 121.8246 | 61.8851 | -60.8368 | 61.5646 | -60.6903 | 122.1725
2030.7344 | 122.9141 | -61.7981 | 60.9238 | 0.2267 | 0.064809 | 0.061656 | 0.0077616 | 0.0025431 | -0.00010175 | -0.0019225 | 60.0311 | 61.0382 | -62.1552 | -0.022888 | -0.050354 | -0.086975 | -0.036621 | 0.10529 | 0.21515 | -0.33417 | -0.35705 | 0.11444 | 121.8292 | 61.7752 | -60.9741 | 61.4639 | -60.7086 | 122.1863
2031.7656 | 123.0423 | -61.7523 | 60.9192 | -0.025068 | 0.059255 | 0.054392 | -0.0042012 | 0.00040688 | -0.00074255 | -0.0010681 | 60.0632 | 60.9421 | -62.1689 | 0.11902 | 0.13733 | 0.14648 | -0.091553 | 0.37079 | 0.21515 | -0.21057 | -0.41656 | 0.022889 | 121.8155 | 61.8713 | -60.7819 | 61.5417 | -60.704 | 122.2321
2032.7344 | 122.9462 | -61.7798 | 60.9238 | 0.28774 | 0.066518 | 0.059519 | 0.007548 | 0.0021159 | 0.0013936 | -0.0023499 | 60.0357 | 61.0199 | -62.1597 | -0.032043 | -0.064087 | -0.082397 | -0.073242 | 0.1236 | 0.20599 | -0.37537 | -0.37994 | 0.09613 | 121.8155 | 61.7477 | -60.9879 | 61.4044 | -60.7178 | 122.1954
2033.7656 | 122.9828 | -61.7523 | 60.9283 | -0.13188 | 0.059896 | 0.058451 | -0.000356 | -0.0015157 | -0.0011698 | -0.0010681 | 60.0952 | 60.9787 | -62.1323 | 0.1236 | 0.1236 | 0.14648 | -0.022888 | 0.37537 | 0.24261 | -0.2243 | -0.37994 | 0.050354 | 121.8475 | 61.8759 | -60.8047 | 61.528 | -60.6857 | 122.2275
2034.7344 | 122.9553 | -61.7935 | 60.9146 | 0.25722 | 0.061605 | 0.06251 | 0.0069072 | 0.0014751 | -0.0037334 | 0.00085447 | 60.0586 | 60.9924 | -62.1552 | -0.004578 | -0.027466 | -0.054932 | -0.11444 | 0.15564 | 0.17395 | -0.35706 | -0.36163 | 0.07782 | 121.8521 | 61.7889 | -60.9421 | 61.4365 | -60.7407 | 122.2137
2035.7656 | 122.9874 | -61.7844 | 60.9146 | -0.17766 | 0.059682 | 0.060801 | 0.0004984 | -0.0034383 | -0.003947 | -0.00042733 | 60.0861 | 60.965 | -62.1368 | 0.1236 | 0.10986 | 0.13275 | 0.027466 | 0.3479 | 0.26093 | -0.20599 | -0.35248 | 0.050354 | 121.8704 | 61.908 | -60.8047 | 61.5784 | -60.6537 | 122.2229
2036.7344 | 122.905 | -61.821 | 60.9283 | 0.21907 | 0.063955 | 0.063365 | 0.010112 | 0.0025431 | -0.0024516 | -0.0010681 | 60.0449 | 61.0703 | -62.1689 | -0.036621 | -0.059509 | -0.091553 | -0.018311 | 0.082397 | 0.21515 | -0.35248 | -0.3479 | 0.14191 | 121.8658 | 61.7844 | -60.9879 | 61.4685 | -60.7132 | 122.2137
2037.7656 | 122.937 | -61.7569 | 60.9421 | -0.18529 | 0.062673 | 0.058879 | 0.0004984 | -0.00044752 | -0.0018108 | -0.0012817 | 60.0998 | 60.9741 | -62.1552 | 0.068665 | 0.09613 | 0.09613 | 0.082397 | 0.33417 | 0.2655 | -0.21973 | -0.39825 | 0.032043 | 121.8567 | 61.8256 | -60.8459 | 61.5372 | -60.6766 | 122.2549
2038.7344 | 122.9095 | -61.8164 | 60.91 | 0.21907 | 0.065023 | 0.059947 | 0.0090434 | 0.00040688 | -0.0015972 | -0.0010681 | 60.0586 | 61.0657 | -62.1918 | -0.054932 | -0.068665 | -0.082397 | -0.013733 | 0.10071 | 0.22888 | -0.37079 | -0.37537 | 0.15564 | 121.875 | 61.7615 | -60.9787 | 61.4456 | -60.6812 | 122.2504
2039.7656 | 122.9691 | -61.7798 | 60.8963 | 0.097002 | 0.060323 | 0.060374 | -0.000356 | -0.00087492 | -0.0011698 | 6.6667e-08 | 60.0357 | 60.9329 | -62.1552 | 0.022888 | 0.041199 | 0.032043 | -0.073242 | 0.23804 | 0.20599 | -0.29755 | -0.37537 | 0.036621 | 121.8155 | 61.8027 | -60.8551 | 61.4822 | -60.6903 | 122.1909
2040.7344 | 122.9187 | -61.8164 | 60.9146 | 0.24959 | 0.06545 | 0.06251 | 0.0079752 | -0.0010885 | 0.0018208 | -0.0010681 | 60.0677 | 61.0474 | -62.1735 | -0.054932 | -0.054932 | -0.082397 | -0.036621 | 0.09613 | 0.23346 | -0.36163 | -0.35706 | 0.13275 | 121.8842 | 61.7615 | -60.9695 | 61.4548 | -60.6812 | 122.2412

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2 | Cable 3
-0.1052 | 21.0318 | 20.3992 | 20.575 | 20.6549
0.8948 | 21.0261 | 20.3956 | 20.5767 | 20.6643
1.8948 | 21.0305 | 20.3878 | 20.5774 | 20.6589
2.8948 | 21.0247 | 20.3799 | 20.5771 | 20.6574
3.8948 | 21.0317 | 20.3871 | 20.5828 | 20.6614
4.8948 | 21.3324 | 20.3959 | 20.5824 | 20.6589
5.8948 | 22.3506 | 20.3928 | 20.5795 | 20.666
6.8948 | 24.1453 | 20.3996 | 20.5838 | 20.6569
7.8948 | 26.6305 | 20.3893 | 20.5812 | 20.6644
8.8948 | 29.6785 | 20.3975 | 20.5849 | 20.6612
9.8948 | 33.1871 | 20.3794 | 20.5839 | 20.6559
10.8948 | 37.0803 | 20.3975 | 20.5781 | 20.657
11.8948 | 41.2928 | 20.3953 | 20.5802 | 20.6597
12.8948 | 45.7814 | 20.3917 | 20.5775 | 20.6559
13.9104 | 50.4926 | 20.3968 | 20.585 | 20.6684
14.8948 | 55.3629 | 20.3973 | 20.5817 | 20.6603
15.8948 | 60.3999 | 20.3986 | 20.5773 | 20.6561
16.8948 | 65.5329 | 20.404 | 20.5896 | 20.6682
17.8948 | 70.8039 | 20.394 | 20.5842 | 20.6702
18.8948 | 76.2801 | 20.3865 | 20.583 | 20.6652
19.8948 | 81.8515 | 20.403 | 20.5871 | 20.6653
20.8948 | 87.4937 | 20.4056 | 20.5905 | 20.6779
21.8948 | 93.1955 | 20.4037 | 20.5887 | 20.6695
22.8948 | 98.9772 | 20.4106 | 20.5966 | 20.6757
23.9104 | 104.8504 | 20.4149 | 20.5967 | 20.6796
24.8948 | 110.7857 | 20.4166 | 20.6017 | 20.6839
25.8948 | 116.7932 | 20.4333 | 20.6049 | 20.6849
26.8948 | 122.7997 | 20.4296 | 20.6112 | 20.6948
27.8948 | 128.75 | 20.4463 | 20.6143 | 20.7019
28.8948 | 134.7437 | 20.4598 | 20.6202 | 20.709
29.8948 | 140.7493 | 20.4703 | 20.6236 | 20.7122
30.8948 | 146.7845 | 20.4846 | 20.6326 | 20.7227
31.8948 | 152.8337 | 20.4962 | 20.6415 | 20.7353
32.8948 | 158.8405 | 20.516 | 20.6589 | 20.7463
33.8948 | 164.7803 | 20.5349 | 20.6644 | 20.7563
34.8948 | 170.749 | 20.5575 | 20.6795 | 20.7731
35.8948 | 176.722 | 20.5863 | 20.6974 | 20.7874
36.8948 | 182.6937 | 20.607 | 20.7084 | 20.811
37.8948 | 188.6796 | 20.6417 | 20.7296 | 20.8322
38.8948 | 194.6913 | 20.6764 | 20.7441 | 20.8531
39.8948 | 200.5473 | 20.7181 | 20.7786 | 20.8852
40.8948 | 206.4746 | 20.7604 | 20.8029 | 20.9071
41.8948 | 212.4487 | 20.8042 | 20.8282 | 20.9382
42.8948 | 218.3701 | 20.8557 | 20.8644 | 20.966
43.8948 | 224.165 | 20.8959 | 20.8941 | 21.0092
44.8948 | 229.9976 | 20.9634 | 20.931 | 21.049
45.8948 | 235.879 | 21.0349 | 20.9772 | 21.0949
46.8948 | 241.8189 | 21.0885 | 21.0151 | 21.1416
47.8948 | 247.5668 | 21.1673 | 21.0583 | 21.1995
48.8948 | 253.284 | 21.2488 | 21.1124 | 21.2548
49.8948 | 259.0413 | 21.3319 | 21.1682 | 21.3186
50.8948 | 264.6213 | 21.4176 | 21.23 | 21.3821
51.8948 | 270.2235 | 21.5014 | 21.3044 | 21.4503
52.8948 | 275.7992 | 21.6222 | 21.3718 | 21.5308
53.8948 | 281.427 | 21.7317 | 21.4504 | 21.6074
54.8948 | 286.6505 | 21.8452 | 21.5281 | 21.6986
55.8948 | 291.456 | 21.9706 | 21.6185 | 21.7857
56.9104 | 295.7779 | 22.095 | 21.7118 | 21.8885
57.8948 | 299.8544 | 22.23 | 21.8069 | 21.9933
58.8948 | 303.804 | 22.3802 | 21.9174 | 22.0976
59.8948 | 307.4735 | 22.5257 | 22.0257 | 22.2182
60.8948 | 310.707 | 22.6948 | 22.1483 | 22.3424
61.8948 | 313.8637 | 22.87 | 22.2679 | 22.4779
62.8948 | 317.075 | 23.0375 | 22.4 | 22.613
63.8948 | 319.8559 | 23.2314 | 22.5379 | 22.7597
64.8948 | 322.3855 | 23.4231 | 22.6816 | 22.9145
65.8948 | 324.7087 | 23.6399 | 22.8354 | 23.073
66.8948 | 326.5234 | 23.8521 | 23.0064 | 23.2468
67.8948 | 328.0876 | 24.0784 | 23.1686 | 23.4172
68.8948 | 329.2698 | 24.3069 | 23.3445 | 23.6061
69.8948 | 330.3266 | 24.526 | 23.5396 | 23.8029
70.8948 | 331.1234 | 24.7845 | 23.7343 | 24.0025
71.8948 | 331.83 | 25.0477 | 23.9393 | 24.2117
72.8948 | 332.2151 | 25.3195 | 24.1524 | 24.438
73.8948 | 332.5909 | 25.597 | 24.3711 | 24.6734
74.8948 | 332.7682 | 25.891 | 24.5936 | 24.902
75.8948 | 332.976 | 26.1746 | 24.8291 | 25.1462
76.8948 | 333.0462 | 26.4856 | 25.0758 | 25.4011
77.9104 | 333.0321 | 26.8154 | 25.3343 | 25.6697
78.8948 | 333.0597 | 27.1264 | 25.5954 | 25.9456
79.8948 | 332.9123 | 27.4627 | 25.8779 | 26.232
80.8948 | 332.7568 | 27.8011 | 26.1602 | 26.5147
81.8948 | 332.6225 | 28.1445 | 26.4502 | 26.8157
82.8948 | 332.3468 | 28.4952 | 26.7489 | 27.1329
83.8948 | 332.0992 | 28.8635 | 27.0636 | 27.4497
84.8948 | 331.9236 | 29.2299 | 27.3868 | 27.776
85.8948 | 331.528 | 29.613 | 27.7029 | 28.1072
86.8948 | 331.1484 | 29.9958 | 28.0426 | 28.4465
87.8948 | 330.7332 | 30.3877 | 28.3814 | 28.7938
88.8948 | 330.4442 | 30.7825 | 28.7311 | 29.1554
89.8948 | 330.0527 | 31.1821 | 29.0854 | 29.5133
90.8948 | 329.557 | 31.5873 | 29.4571 | 29.8966
91.8948 | 329.2328 | 32.0002 | 29.8254 | 30.2714
92.8948 | 328.9504 | 32.4159 | 30.2044 | 30.6549
93.8948 | 328.4921 | 32.8262 | 30.5884 | 31.0414
94.8948 | 327.9596 | 33.2454 | 30.9694 | 31.4338
95.8948 | 327.5158 | 33.6538 | 31.3706 | 31.8339
96.8948 | 327.1091 | 34.0993 | 31.7626 | 32.2442
97.8948 | 326.5272 | 34.5231 | 32.1735 | 32.6477
98.8948 | 325.9153 | 34.9644 | 32.5853 | 33.0645
99.8948 | 325.4939 | 35.4089 | 33.0002 | 33.4928
100.8948 | 325.0795 | 35.8511 | 33.4211 | 33.9105
101.8948 | 324.7211 | 36.307 | 33.8453 | 34.3446
102.8948 | 324.4622 | 36.7842 | 34.2735 | 34.7724
103.8948 | 324.0958 | 37.235 | 34.7067 | 35.2222
104.8948 | 323.7624 | 37.7022 | 35.1462 | 35.6564
105.8948 | 323.5466 | 38.1638 | 35.587 | 36.0993
106.8948 | 323.4414 | 38.6203 | 36.0275 | 36.5487
107.8948 | 323.1692 | 39.0981 | 36.4864 | 36.9969
108.8948 | 322.9861 | 39.5703 | 36.9345 | 37.4602
109.8948 | 322.9696 | 40.0389 | 37.3888 | 37.9076
110.8948 | 323.0219 | 40.5026 | 37.8485 | 38.3757
111.8948 | 322.9675 | 40.9851 | 38.3135 | 38.8312
112.8948 | 322.9162 | 41.4564 | 38.7796 | 39.315
113.8948 | 323.0251 | 41.919 | 39.2551 | 39.7828
114.8948 | 323.1405 | 42.4144 | 39.7209 | 40.2563
115.8948 | 323.3784 | 42.892 | 40.1931 | 40.7249
116.8948 | 323.5426 | 43.3731 | 40.6698 | 41.2029
117.8948 | 323.7559 | 43.8334 | 41.1506 | 41.6778
118.8948 | 323.9654 | 44.3206 | 41.6332 | 42.1685
119.8948 | 324.3185 | 44.8084 | 42.1095 | 42.6421
120.8948 | 324.5482 | 45.2954 | 42.5895 | 43.1254
121.8948 | 324.8142 | 45.7944 | 43.0687 | 43.6076
122.9104 | 325.0372 | 46.2873 | 43.5753 | 44.1025
123.8948 | 325.2602 | 46.7667 | 44.0465 | 44.582
124.8948 | 325.5103 | 47.2717 | 44.5379 | 45.0758
125.8948 | 325.8792 | 47.7668 | 45.0291 | 45.5593
126.8948 | 326.0851 | 48.2683 | 45.5188 | 46.0538
127.8948 | 326.3524 | 48.7862 | 46.0129 | 46.5485
128.8948 | 326.6879 | 49.278 | 46.5119 | 47.0416
129.8948 | 326.9538 | 49.7867 | 47.0048 | 47.5339
130.8948 | 327.1819 | 50.2705 | 47.505 | 48.0293
131.8948 | 327.2506 | 50.7726 | 48.0029 | 48.527
132.8948 | 327.3747 | 51.2695 | 48.504 | 49.034
133.8948 | 327.5462 | 51.7746 | 49.0091 | 49.5317
134.8948 | 327.6122 | 52.2466 | 49.5027 | 50.0281
135.8948 | 327.6573 | 52.7653 | 50.0071 | 50.5271
136.8948 | 327.8111 | 53.2516 | 50.51 | 51.0303
137.8948 | 327.9277 | 53.7621 | 51.0099 | 51.5277
138.8948 | 327.9376 | 54.2644 | 51.5129 | 52.0303
139.8948 | 328.0554 | 54.7532 | 52.0192 | 52.5334
140.8948 | 328.0379 | 55.2511 | 52.5156 | 53.0313
141.8948 | 328.1432 | 55.7834 | 53.0261 | 53.5288
142.8948 | 328.3157 | 56.2704 | 53.532 | 54.0469
143.8948 | 328.4073 | 56.7898 | 54.0314 | 54.5423
144.8948 | 328.4381 | 57.3075 | 54.5412 | 55.0455
145.8948 | 328.4972 | 57.8274 | 55.0457 | 55.5465
146.8948 | 328.5985 | 58.327 | 55.546 | 56.0483
147.8948 | 328.5382 | 58.8472 | 56.0548 | 56.551
148.8948 | 328.5132 | 59.3603 | 56.5689 | 57.0525
149.8948 | 328.4383 | 59.866 | 57.0676 | 57.5587
150.8948 | 328.2791 | 60.3758 | 57.5775 | 58.0648
151.8948 | 328.3194 | 60.8696 | 58.0963 | 58.5718
152.9104 | 328.2552 | 61.3927 | 58.5978 | 59.0762
153.8948 | 328.2072 | 61.8998 | 59.1053 | 59.5758
154.8948 | 328.2643 | 62.4153 | 59.6069 | 60.0764
155.8948 | 328.2454 | 62.9109 | 60.1166 | 60.5757
156.8948 | 328.2229 | 63.4164 | 60.6206 | 61.0794
157.8948 | 328.2362 | 63.9291 | 61.1309 | 61.5813
158.8948 | 328.2214 | 64.4381 | 61.6324 | 62.077
159.8948 | 328.1353 | 64.9333 | 62.1336 | 62.5885
160.8948 | 328.2554 | 65.4366 | 62.6353 | 63.0825
161.8948 | 328.2946 | 65.9493 | 63.1409 | 63.5764
162.8948 | 328.2539 | 66.4439 | 63.6509 | 64.0808
163.8948 | 328.3354 | 66.9639 | 64.1521 | 64.5805
164.8948 | 328.4144 | 67.4936 | 64.6636 | 65.0801
165.8948 | 328.4125 | 67.9831 | 65.165 | 65.585
166.8948 | 328.4736 | 68.4812 | 65.6712 | 66.0839
167.8948 | 328.6041 | 68.9871 | 66.1773 | 66.5844
168.8948 | 328.6771 | 69.5072 | 66.6754 | 67.0892
169.8948 | 328.7088 | 70.017 | 67.1945 | 67.5936
170.8948 | 328.8183 | 70.5211 | 67.706 | 68.1129
171.8948 | 328.8303 | 71.0555 | 68.2143 | 68.6154
172.8948 | 328.6721 | 71.5557 | 68.7251 | 69.1179
173.8948 | 328.6586 | 72.0741 | 69.2366 | 69.6212
174.8948 | 328.7275 | 72.6061 | 69.7498 | 70.1334
175.8948 | 328.7397 | 73.1333 | 70.2588 | 70.6385
176.8948 | 328.6972 | 73.658 | 70.7736 | 71.1446
177.8948 | 328.7341 | 74.1976 | 71.2832 | 71.6562
178.8948 | 328.771 | 74.7352 | 71.8097 | 72.1683
179.8948 | 328.7487 | 75.2844 | 72.3279 | 72.6876
180.8948 | 328.6794 | 75.8733 | 72.8536 | 73.2143
181.8948 | 328.681 | 76.4646 | 73.384 | 73.7417
182.9104 | 328.6233 | 77.1349 | 73.9308 | 74.2867
183.8948 | 328.6367 | 77.8327 | 74.4919 | 74.8351
184.8948 | 328.6037 | 78.5528 | 75.0659 | 75.4058
185.8948 | 328.4858 | 79.2947 | 75.6562 | 75.997
186.8948 | 328.4073 | 80.0833 | 76.26 | 76.5976
187.8948 | 328.4217 | 80.8582 | 76.8961 | 77.2223
188.8948 | 328.4735 | 81.6146 | 77.5276 | 77.8485
189.8948 | 328.524 | 82.36 | 78.165 | 78.488
190.8948 | 328.4678 | 83.1148 | 78.82 | 79.1291
191.8948 | 328.4007 | 83.8815 | 79.4858 | 79.7943
192.8948 | 328.4287 | 84.6328 | 80.1588 | 80.4592
193.8948 | 328.4515 | 85.3983 | 80.8487 | 81.1387
194.8948 | 328.3731 | 86.1273 | 81.5528 | 81.83
195.8948 | 328.2943 | 86.9071 | 82.2758 | 82.5239
196.8948 | 328.2647 | 87.6726 | 83.0075 | 83.241
197.8948 | 328.3269 | 88.4675 | 83.753 | 83.9744
198.8948 | 328.3428 | 89.2082 | 84.5096 | 84.7269
199.8948 | 328.3479 | 89.9222 | 85.2866 | 85.5012
200.8948 | 328.3478 | 90.5439 | 86.0748 | 86.2886
201.8948 | 328.3076 | 91.1036 | 86.8648 | 87.0974
202.8948 | 328.2834 | 91.6274 | 87.6554 | 87.9175
203.8948 | 328.2819 | 92.0997 | 88.4461 | 88.7436
204.8948 | 328.2345 | 92.5351 | 89.2408 | 89.5653
205.8948 | 328.2596 | 92.9399 | 90.0268 | 90.3838
206.8948 | 328.1198 | 93.3098 | 90.8146 | 91.1832
207.8948 | 328.1445 | 93.6604 | 91.5936 | 91.972
208.8948 | 328.1585 | 93.988 | 92.3719 | 92.7364
209.8948 | 328.2257 | 94.3111 | 93.1288 | 93.4456
210.8948 | 328.353 | 94.6108 | 93.8296 | 94.0913
211.8948 | 328.3477 | 94.8985 | 94.4629 | 94.6579
212.9104 | 328.446 | 95.1699 | 95.0024 | 95.1581
213.8948 | 328.4848 | 95.4568 | 95.4991 | 95.6263
214.8948 | 328.4495 | 95.724 | 95.8434 | 96.0589
215.8948 | 328.3954 | 95.9355 | 96.0868 | 96.3617
216.8948 | 328.3392 | 96.0946 | 96.2525 | 96.5632
217.8948 | 328.3242 | 96.1736 | 96.3702 | 96.7049
218.8948 | 328.2965 | 96.2432 | 96.456 | 96.8075
219.8948 | 328.2541 | 96.3134 | 96.5223 | 96.8876
220.8948 | 328.173 | 96.3929 | 96.5862 | 96.9685
221.8948 | 328.1698 | 96.4676 | 96.639 | 97.0251
222.8948 | 328.2369 | 96.5635 | 96.683 | 97.0841
223.8948 | 328.2498 | 96.6507 | 96.7272 | 97.1368
224.8948 | 328.2362 | 96.7729 | 96.7667 | 97.18
225.8948 | 328.2873 | 96.8815 | 96.8053 | 97.2174
226.8948 | 328.281 | 96.9892 | 96.84 | 97.2609
227.8948 | 328.2084 | 97.0928 | 96.8696 | 97.3046
228.8948 | 328.1806 | 97.2217 | 96.9099 | 97.3342
229.8948 | 328.1365 | 97.3496 | 96.94 | 97.3867
230.8948 | 328.0613 | 97.4553 | 96.9754 | 97.4238
231.8948 | 328.14 | 97.5965 | 97.0132 | 97.4615
232.8948 | 328.2665 | 97.7428 | 97.0452 | 97.4899
233.8948 | 328.3475 | 97.888 | 97.0759 | 97.5418
234.8948 | 328.3389 | 98.0324 | 97.1129 | 97.574
235.8948 | 328.314 | 98.1962 | 97.1569 | 97.6232
236.8948 | 328.2675 | 98.3362 | 97.1912 | 97.6638
237.8948 | 328.2296 | 98.4983 | 97.2379 | 97.7204
238.8948 | 328.1623 | 98.6607 | 97.2804 | 97.7705
239.8948 | 328.2398 | 98.8321 | 97.3244 | 97.8205
240.8948 | 328.3263 | 99.0066 | 97.3774 | 97.8758
241.8948 | 328.4741 | 99.1814 | 97.4313 | 97.9351
242.9104 | 328.4952 | 99.3832 | 97.4842 | 97.9926
243.8948 | 328.4889 | 99.5672 | 97.554 | 98.0624
244.8948 | 328.5238 | 99.7625 | 97.611 | 98.1323
245.8948 | 328.5042 | 99.9727 | 97.6803 | 98.2016
246.8948 | 328.5861 | 100.1703 | 97.7509 | 98.2725
247.8948 | 328.5622 | 100.3962 | 97.836 | 98.3539
248.8948 | 328.6579 | 100.6177 | 97.9134 | 98.4424
249.8948 | 328.7505 | 100.8371 | 97.9998 | 98.5201
250.8948 | 328.8446 | 101.0628 | 98.0932 | 98.61
251.8948 | 328.7189 | 101.2772 | 98.1895 | 98.7059
252.8948 | 328.6246 | 101.5131 | 98.2934 | 98.7997
253.8948 | 328.5846 | 101.7608 | 98.4013 | 98.9026
254.8948 | 328.5746 | 101.9967 | 98.5188 | 98.9996
255.8948 | 328.5513 | 102.2348 | 98.6353 | 99.1114
256.8948 | 328.5027 | 102.4801 | 98.7705 | 99.2282
257.8948 | 328.5298 | 102.7274 | 98.8988 | 99.3388
258.8948 | 328.5582 | 102.9713 | 99.0335 | 99.4668
259.8948 | 328.5303 | 103.2139 | 99.1808 | 99.5981
260.8948 | 328.4442 | 103.474 | 99.329 | 99.7198
261.8948 | 328.3396 | 103.7309 | 99.4882 | 99.86
262.8948 | 328.3497 | 103.9829 | 99.652 | 99.9935
263.8948 | 328.301 | 104.2467 | 99.8124 | 100.1405
264.8948 | 328.2052 | 104.5007 | 99.9952 | 100.2853
265.8948 | 328.1323 | 104.7635 | 100.1795 | 100.4472
266.8948 | 328.0483 | 105.0475 | 100.3736 | 100.6044
267.8948 | 327.9735 | 105.3109 | 100.563 | 100.7773
268.8948 | 327.9556 | 105.5771 | 100.7616 | 100.9454
269.8948 | 327.9364 | 105.8488 | 100.9602 | 101.1166
270.8948 | 327.894 | 106.1151 | 101.1726 | 101.2936
271.8948 | 327.8336 | 106.398 | 101.38 | 101.4851
272.9104 | 327.6866 | 106.662 | 101.5985 | 101.6704
273.8948 | 327.6091 | 106.942 | 101.8234 | 101.8598
274.8948 | 327.6091 | 107.2139 | 102.0519 | 102.0578
275.8948 | 327.5927 | 107.5006 | 102.2861 | 102.2613
276.8948 | 327.5711 | 107.7893 | 102.5159 | 102.4663
277.8948 | 327.6181 | 108.0796 | 102.7643 | 102.6824
278.8948 | 327.612 | 108.376 | 103.0063 | 102.8995
279.8948 | 327.552 | 108.6806 | 103.2601 | 103.1239
280.8948 | 327.5919 | 108.9776 | 103.5202 | 103.3549
281.8948 | 327.6641 | 109.2843 | 103.7785 | 103.5866
282.8948 | 327.6925 | 109.6053 | 104.0393 | 103.8238
283.8948 | 327.7136 | 109.912 | 104.3103 | 104.0691
284.8948 | 327.6688 | 110.222 | 104.5865 | 104.3152
285.8948 | 327.6033 | 110.5244 | 104.8619 | 104.5638
286.8948 | 327.5987 | 110.8612 | 105.1575 | 104.8272
287.8948 | 327.6173 | 111.1723 | 105.4387 | 105.0947
288.8948 | 327.6157 | 111.4979 | 105.727 | 105.3649
289.8948 | 327.5456 | 111.8261 | 106.0183 | 105.65
290.8948 | 327.5055 | 112.1537 | 106.3116 | 105.9251
291.8948 | 327.5312 | 112.4884 | 106.6093 | 106.2067
292.8948 | 327.5657 | 112.8104 | 106.9063 | 106.4894
293.8948 | 327.6344 | 113.1427 | 107.2127 | 106.7888
294.8948 | 327.6421 | 113.4764 | 107.5243 | 107.0839
295.8948 | 327.7038 | 113.8113 | 107.8419 | 107.3855
296.8948 | 327.7169 | 114.1443 | 108.1514 | 107.6916
297.8948 | 327.8328 | 114.5068 | 108.476 | 108.0003
298.8948 | 327.8869 | 114.8533 | 108.7973 | 108.3131
299.8948 | 327.9871 | 115.1856 | 109.1308 | 108.6326
300.8948 | 327.9578 | 115.5317 | 109.4533 | 108.956
301.8948 | 327.91 | 115.8749 | 109.7912 | 109.2896
302.9104 | 327.8579 | 116.2242 | 110.1282 | 109.6233
303.8948 | 327.7836 | 116.569 | 110.4634 | 109.9595
304.8948 | 327.7677 | 116.9177 | 110.8095 | 110.3017
305.8948 | 327.7643 | 117.2737 | 111.1513 | 110.6392
306.8948 | 327.7469 | 117.6128 | 111.5064 | 110.9884
307.8948 | 327.7769 | 117.964 | 111.8528 | 111.3384
308.8948 | 327.7182 | 118.316 | 112.2068 | 111.6969
309.8948 | 327.7696 | 118.6601 | 112.5662 | 112.0428
310.8948 | 327.8091 | 119.0311 | 112.928 | 112.4159
311.8948 | 327.7598 | 119.3698 | 113.2909 | 112.7752
312.8948 | 327.839 | 119.7245 | 113.6578 | 113.1427
313.8948 | 327.8106 | 120.0757 | 114.0239 | 113.5059
314.8948 | 327.7914 | 120.4423 | 114.3971 | 113.8881
315.8948 | 327.8174 | 120.8059 | 114.7781 | 114.2599
316.8948 | 327.8678 | 121.1639 | 115.1572 | 114.6426
317.8948 | 327.8375 | 121.5214 | 115.527 | 115.0268
318.8948 | 327.7823 | 121.8812 | 115.9042 | 115.4218
319.8948 | 327.8207 | 122.2402 | 116.2885 | 115.7978
320.8948 | 327.7709 | 122.6071 | 116.6658 | 116.1818
321.8948 | 327.6652 | 122.9699 | 117.0539 | 116.5723
322.8948 | 327.71 | 123.3366 | 117.4396 | 116.9589
323.8948 | 327.8152 | 123.698 | 117.8224 | 117.3555
324.8948 | 327.7987 | 124.0703 | 118.2102 | 117.7514
325.8948 | 327.757 | 124.4369 | 118.5971 | 118.1422
326.8948 | 327.8202 | 124.7894 | 118.9892 | 118.5432
327.8948 | 327.8387 | 125.1493 | 119.3768 | 118.9443
328.8948 | 327.8106 | 125.5131 | 119.7788 | 119.3395
329.8948 | 327.6895 | 125.8644 | 120.1654 | 119.7337
330.8948 | 327.7268 | 126.2401 | 120.552 | 120.1449
331.8948 | 327.752 | 126.595 | 120.9426 | 120.5385
332.9104 | 327.7704 | 126.966 | 121.3379 | 120.9386
333.8948 | 327.747 | 127.3106 | 121.7272 | 121.339
334.8948 | 327.741 | 127.6734 | 122.1227 | 121.7403
335.8948 | 327.6543 | 128.0338 | 122.5184 | 122.1465
336.8948 | 327.6828 | 128.3964 | 122.9079 | 122.5471
337.8948 | 327.8452 | 128.7493 | 123.3018 | 122.9465
338.8948 | 327.777 | 129.1141 | 123.702 | 123.3473
339.8948 | 327.7243 | 129.4669 | 124.1011 | 123.7543
340.8948 | 327.7681 | 129.8262 | 124.4917 | 124.1546
341.8948 | 327.7854 | 130.1936 | 124.8898 | 124.5646
342.8948 | 327.8723 | 130.541 | 125.2744 | 124.9564
343.8948 | 327.8809 | 130.8788 | 125.6656 | 125.3557
344.8948 | 327.8684 | 131.2396 | 126.0475 | 125.7537
345.8948 | 327.8576 | 131.5842 | 126.4421 | 126.1578
346.8948 | 327.8843 | 131.9303 | 126.8174 | 126.5547
347.8948 | 327.9889 | 132.2673 | 127.2038 | 126.9522
348.8948 | 327.8859 | 132.6178 | 127.5953 | 127.3465
349.8948 | 327.7909 | 132.9655 | 127.9814 | 127.7419
350.8948 | 327.7304 | 133.3189 | 128.361 | 128.1342
351.8948 | 327.6927 | 133.6784 | 128.745 | 128.5321
352.8948 | 327.6805 | 134.0276 | 129.1246 | 128.9232
353.8948 | 327.773 | 134.3817 | 129.5007 | 129.3106
354.8948 | 327.7453 | 134.7284 | 129.8834 | 129.6989
355.8948 | 327.6099 | 135.0798 | 130.2675 | 130.0892
356.8948 | 327.5131 | 135.4224 | 130.6389 | 130.4856
357.8948 | 327.6015 | 135.765 | 131.0225 | 130.8675
358.8948 | 327.5047 | 136.1108 | 131.4052 | 131.2518
359.9104 | 327.4594 | 136.4777 | 131.7844 | 131.6436
360.8948 | 327.4601 | 136.8161 | 132.1595 | 132.0291
361.8948 | 327.462 | 137.165 | 132.5365 | 132.4114
362.9104 | 327.4202 | 137.5206 | 132.9088 | 132.804
363.8948 | 327.3129 | 137.8557 | 133.2871 | 133.1754
364.8948 | 327.2963 | 138.2123 | 133.6704 | 133.5624
365.8948 | 327.2704 | 138.5456 | 134.0454 | 133.9415
366.8948 | 327.2804 | 138.8923 | 134.4205 | 134.3363
367.8948 | 327.2787 | 139.2371 | 134.7897 | 134.7175
368.8948 | 327.2409 | 139.6006 | 135.1644 | 135.0995
369.8948 | 327.1881 | 139.94 | 135.5329 | 135.4767
370.8948 | 327.1695 | 140.294 | 135.9043 | 135.8556
371.8948 | 327.1574 | 140.6445 | 136.2733 | 136.2348
372.8948 | 327.2115 | 140.9973 | 136.6433 | 136.6202
373.8948 | 327.2815 | 141.3556 | 137.0194 | 136.9853
374.8948 | 327.2906 | 141.7117 | 137.3816 | 137.365
375.8948 | 327.3518 | 142.0553 | 137.7544 | 137.742
376.8948 | 327.368 | 142.3975 | 138.1171 | 138.1155
377.8948 | 327.507 | 142.7459 | 138.4674 | 138.4861
378.8948 | 327.6414 | 143.0919 | 138.8415 | 138.8628
379.8948 | 327.5768 | 143.4557 | 139.2092 | 139.2282
380.8948 | 327.5464 | 143.7927 | 139.5784 | 139.5966
381.8948 | 327.523 | 144.1583 | 139.9303 | 139.9745
382.8948 | 327.4787 | 144.4946 | 140.2989 | 140.3377
383.8948 | 327.5144 | 144.8368 | 140.6577 | 140.7098
384.8948 | 327.6003 | 145.1742 | 141.0207 | 141.0772
385.8948 | 327.6485 | 145.5241 | 141.3888 | 141.4487
386.8948 | 327.6853 | 145.8828 | 141.747 | 141.8173
387.8948 | 327.7036 | 146.2209 | 142.1029 | 142.1834
388.8948 | 327.5325 | 146.5569 | 142.4641 | 142.5396
389.8948 | 327.3529 | 146.8939 | 142.8236 | 142.9067
390.8948 | 327.2443 | 147.2422 | 143.1802 | 143.2709
391.8948 | 327.168 | 147.578 | 143.5506 | 143.6326
392.9104 | 327.1551 | 147.9316 | 143.9119 | 144.0147
393.8948 | 327.1484 | 148.2638 | 144.2655 | 144.3729
394.8948 | 327.1693 | 148.6105 | 144.6204 | 144.7277
395.8948 | 327.1537 | 148.9528 | 144.9746 | 145.0969
396.8948 | 327.1543 | 149.2853 | 145.3276 | 145.4492
397.8948 | 327.1987 | 149.4342 | 145.6775 | 145.8004
398.8948 | 327.2054 | 149.7786 | 146.0268 | 146.1565
399.8948 | 327.242 | 150.1515 | 146.3774 | 146.5142
400.8948 | 327.2445 | 150.4913 | 146.7316 | 146.8739
401.8948 | 327.2657 | 150.8414 | 147.0821 | 147.2339
402.8948 | 327.2883 | 151.1814 | 147.4295 | 147.5804
403.8948 | 327.3071 | 151.5222 | 147.7851 | 147.9393
404.8948 | 327.3729 | 151.8767 | 148.1313 | 148.2906
405.8948 | 327.4114 | 152.2166 | 148.4823 | 148.643
406.8948 | 327.4956 | 152.5661 | 148.831 | 148.996
407.8948 | 327.5083 | 152.897 | 149.1717 | 149.3384
408.8948 | 327.5237 | 153.2385 | 149.5198 | 149.6963
409.8948 | 327.6092 | 153.575 | 149.8617 | 150.0396
410.8948 | 327.5518 | 153.9119 | 150.2155 | 150.3942
411.8948 | 327.7088 | 154.2622 | 150.5558 | 150.7426
412.8948 | 327.8623 | 154.6005 | 150.8979 | 151.089
413.8948 | 327.8483 | 154.9268 | 151.235 | 151.4441
414.8948 | 327.8481 | 155.2682 | 151.5811 | 151.7838
415.8948 | 327.8427 | 155.6007 | 151.9257 | 152.1261
416.8948 | 327.8504 | 155.9208 | 152.2651 | 152.472
417.8948 | 327.8099 | 156.2658 | 152.6049 | 152.8111
418.8948 | 327.7746 | 156.5908 | 152.9499 | 153.1614
419.8948 | 327.7874 | 156.9326 | 153.3033 | 153.509
420.8948 | 327.8073 | 157.2534 | 153.6445 | 153.8543
421.8948 | 327.7394 | 157.5938 | 153.9741 | 154.1951
422.9104 | 327.622 | 157.9231 | 154.3316 | 154.5444
423.8948 | 327.7801 | 158.2372 | 154.6585 | 154.8685
424.8948 | 327.667 | 158.573 | 154.9908 | 155.2108
425.8948 | 327.657 | 158.893 | 155.3235 | 155.548
426.8948 | 327.7061 | 159.219 | 155.661 | 155.8927
427.8948 | 327.6916 | 159.5443 | 156.0021 | 156.2215
428.8948 | 327.7135 | 159.8636 | 156.3365 | 156.5607
429.8948 | 327.6944 | 160.1875 | 156.661 | 156.9026
430.8948 | 327.7235 | 160.5121 | 156.996 | 157.2307
431.8948 | 327.6465 | 160.8286 | 157.3276 | 157.5612
432.8948 | 327.5984 | 161.1559 | 157.6582 | 157.8913
433.8948 | 327.5769 | 161.4822 | 157.9886 | 158.2265
434.8948 | 327.5385 | 161.8063 | 158.32 | 158.5584
435.8948 | 327.5282 | 162.128 | 158.6461 | 158.8917
436.8948 | 327.5392 | 162.4477 | 158.9789 | 159.2197
437.8948 | 327.5028 | 162.7578 | 159.3072 | 159.5511
438.8948 | 327.4846 | 163.1043 | 159.6316 | 159.8789
439.8948 | 327.4876 | 163.4165 | 159.9575 | 160.2001
440.8948 | 327.3782 | 163.7281 | 160.2886 | 160.5338
441.8948 | 327.352 | 164.0517 | 160.6086 | 160.8579
442.8948 | 327.3716 | 164.3672 | 160.9369 | 161.1829
443.8948 | 327.4204 | 164.6793 | 161.2625 | 161.5116
444.8948 | 327.359 | 164.993 | 161.5864 | 161.8385
445.8948 | 327.3047 | 165.3049 | 161.9026 | 162.1644
446.9104 | 327.3303 | 165.6346 | 162.2348 | 162.4841
447.8948 | 327.3186 | 165.9459 | 162.5509 | 162.8025
448.8948 | 327.4053 | 166.2621 | 162.8878 | 163.1278
449.8948 | 327.3697 | 166.5716 | 163.2056 | 163.455
450.8948 | 327.3334 | 166.8867 | 163.5238 | 163.7818
451.9104 | 327.4034 | 167.2018 | 163.8447 | 164.1031
452.8948 | 327.3687 | 167.5207 | 164.1607 | 164.4235
453.8948 | 327.2716 | 167.8132 | 164.484 | 164.7416
454.8948 | 327.297 | 168.1391 | 164.8021 | 165.064
455.8948 | 327.3388 | 168.4395 | 165.1153 | 165.3748
456.8948 | 327.3681 | 168.758 | 165.4348 | 165.6937
457.8948 | 327.3796 | 169.0608 | 165.7503 | 166.0179
458.8948 | 327.2551 | 169.3689 | 166.0674 | 166.333
459.8948 | 327.2998 | 169.6709 | 166.3814 | 166.6501
460.8948 | 327.3265 | 169.9752 | 166.6922 | 166.9603
461.8948 | 327.3328 | 170.1928 | 167.0042 | 167.273
462.8948 | 327.3852 | 170.4932 | 167.3176 | 167.5866
463.8948 | 327.392 | 170.815 | 167.6318 | 167.9016
464.8948 | 327.3976 | 171.123 | 167.9404 | 168.2121
465.8948 | 327.5331 | 171.4192 | 168.251 | 168.5206
466.8948 | 327.5697 | 171.7504 | 168.5589 | 168.8343
467.8948 | 327.6785 | 172.0473 | 168.8713 | 169.1465
468.8948 | 327.7251 | 172.348 | 169.1765 | 169.4518
469.8948 | 327.7304 | 172.6655 | 169.4834 | 169.7628
470.8948 | 327.6689 | 172.9727 | 169.7978 | 170.0697
471.8948 | 327.6478 | 173.2683 | 170.1009 | 170.3847
472.8948 | 327.6543 | 173.5733 | 170.4098 | 170.691
473.8948 | 327.6783 | 173.8715 | 170.7219 | 170.9974
474.8948 | 327.7378 | 174.1741 | 171.0258 | 171.3028
475.8948 | 327.642 | 174.4749 | 171.3286 | 171.6145
476.8948 | 327.6739 | 174.7719 | 171.632 | 171.9178
477.8948 | 327.6753 | 175.0725 | 171.9377 | 172.2243
478.8948 | 327.6821 | 175.3785 | 172.2419 | 172.5221
479.8948 | 327.6648 | 175.6689 | 172.5604 | 172.8334
480.8948 | 327.5328 | 175.9713 | 172.8555 | 173.146
481.8948 | 327.3894 | 176.2687 | 173.1604 | 173.4435
482.8948 | 327.3527 | 176.558 | 173.4623 | 173.7461
483.8948 | 327.2823 | 176.859 | 173.7622 | 174.0501
484.8948 | 327.1841 | 177.15 | 174.0587 | 174.3493
485.8948 | 327.1036 | 177.4458 | 174.3585 | 174.6455
486.8948 | 327.1546 | 177.7326 | 174.6554 | 174.9484
487.8948 | 327.1889 | 178.034 | 174.9512 | 175.2426
488.8948 | 327.136 | 178.3227 | 175.2542 | 175.5429
489.8948 | 327.1441 | 178.607 | 175.5435 | 175.831
490.8948 | 327.1304 | 178.8946 | 175.8436 | 176.1249
491.8948 | 327.0394 | 179.1945 | 176.1397 | 176.4239
492.8948 | 326.9382 | 179.4846 | 176.4283 | 176.7135
493.8948 | 326.8437 | 179.7794 | 176.7234 | 177.007
494.8948 | 326.8737 | 180.0666 | 177.013 | 177.3009
495.8948 | 326.8733 | 180.355 | 177.3038 | 177.5991
496.8948 | 326.9416 | 180.6236 | 177.5895 | 177.8905
497.8948 | 326.823 | 180.9276 | 177.8856 | 178.1764
498.8948 | 326.7888 | 181.2204 | 178.1764 | 178.4682
499.8948 | 326.7641 | 181.501 | 178.4651 | 178.7497
500.8948 | 326.6541 | 181.7796 | 178.7475 | 179.0429
501.8948 | 326.6031 | 182.0621 | 179.0412 | 179.3275
502.8948 | 326.4843 | 182.3582 | 179.3313 | 179.6171
503.8948 | 326.4394 | 182.6395 | 179.6185 | 179.8925
504.8948 | 326.5045 | 182.9236 | 179.9016 | 180.1944
505.8948 | 326.5598 | 183.1939 | 180.1812 | 180.4729
506.8948 | 326.5741 | 183.4804 | 180.4737 | 180.757
507.8948 | 326.5908 | 183.7603 | 180.7488 | 181.0349
508.8948 | 326.634 | 184.0478 | 181.0327 | 181.322
509.8948 | 326.7495 | 184.3253 | 181.3195 | 181.6031
510.8948 | 326.7818 | 184.6065 | 181.6034 | 181.8829
511.8948 | 326.897 | 184.8846 | 181.8735 | 182.1636
512.8948 | 326.8788 | 185.1571 | 182.16 | 182.4393
513.8948 | 326.8059 | 185.4244 | 182.4496 | 182.7369
514.8948 | 326.7793 | 185.6922 | 182.7323 | 183.0173
515.8948 | 326.6684 | 185.9643 | 183.0108 | 183.3016
516.8948 | 326.6497 | 186.2444 | 183.2837 | 183.5762
517.8948 | 326.7116 | 186.5063 | 183.5653 | 183.8635
518.8948 | 326.6617 | 186.7872 | 183.8383 | 184.136
519.8948 | 326.5708 | 187.0579 | 184.1193 | 184.4201
520.8948 | 326.6208 | 187.3134 | 184.4001 | 184.6905
521.8948 | 326.6852 | 187.5928 | 184.6695 | 184.9616
522.8948 | 326.8124 | 187.865 | 184.9429 | 185.2424
523.8948 | 326.7974 | 188.1197 | 185.2197 | 185.5141
524.8948 | 326.7606 | 188.3987 | 185.4903 | 185.7871
525.8948 | 326.6739 | 188.6552 | 185.7681 | 186.0509
526.8948 | 326.5939 | 188.9216 | 186.0362 | 186.3362
527.8948 | 326.5704 | 189.1697 | 186.3066 | 186.6049
528.8948 | 326.5396 | 189.4522 | 186.5762 | 186.8793
529.8948 | 326.596 | 189.7134 | 186.8527 | 187.1542
530.8948 | 326.606 | 189.9774 | 187.121 | 187.4267
531.8948 | 326.6199 | 190.2255 | 187.3929 | 187.6934
532.8948 | 326.5945 | 190.4927 | 187.6589 | 187.9601
533.8948 | 326.6307 | 190.7525 | 187.9206 | 188.2219
534.8948 | 326.588 | 191.0104 | 188.1912 | 188.4989
535.8948 | 326.5369 | 191.2536 | 188.4579 | 188.7577
536.8948 | 326.4517 | 191.5147 | 188.7269 | 189.0272
537.8948 | 326.4498 | 191.7707 | 188.9878 | 189.2848
538.8948 | 326.4158 | 192.044 | 189.2479 | 189.5428
539.8948 | 326.316 | 192.296 | 189.5163 | 189.8054
540.8948 | 326.3064 | 192.5396 | 189.7769 | 190.0667
541.8948 | 326.3304 | 192.8145 | 190.0377 | 190.328
542.8948 | 326.3256 | 193.0654 | 190.2952 | 190.5824
543.8948 | 326.2038 | 193.313 | 190.5608 | 190.847
544.8948 | 326.1193 | 193.5681 | 190.8149 | 191.1026
545.8948 | 326.0459 | 193.8119 | 191.0696 | 191.3627
546.8948 | 326.0381 | 194.0672 | 191.33 | 191.621
547.8948 | 326.1225 | 194.3398 | 191.5843 | 191.8627
548.8948 | 326.1597 | 194.5808 | 191.8458 | 192.1304
549.8948 | 326.2234 | 194.8332 | 192.1021 | 192.3793
550.8948 | 326.2305 | 195.0847 | 192.3635 | 192.6493
551.8948 | 326.1655 | 195.3339 | 192.616 | 192.8975
552.8948 | 326.2149 | 195.5864 | 192.8573 | 193.1491
553.8948 | 326.304 | 195.8406 | 193.1168 | 193.3978
554.8948 | 326.3361 | 196.0775 | 193.3708 | 193.6559
555.8948 | 326.3834 | 196.3297 | 193.6274 | 193.9103
556.8948 | 326.3674 | 196.5711 | 193.8759 | 194.1615
557.8948 | 326.38 | 196.8308 | 194.1207 | 194.4099
558.8948 | 326.4085 | 197.0601 | 194.3821 | 194.6615
559.8948 | 326.3877 | 197.3085 | 194.6373 | 194.9126
560.8948 | 326.3819 | 197.5435 | 194.8888 | 195.1627
561.8948 | 326.5432 | 197.7915 | 195.1357 | 195.4177
562.8948 | 326.5377 | 198.0212 | 195.3882 | 195.6585
563.8948 | 326.4878 | 198.2783 | 195.6316 | 195.9136
564.8948 | 326.5122 | 198.51 | 195.876 | 196.1568
565.8948 | 326.5356 | 198.7602 | 196.1234 | 196.3973
566.8948 | 326.6368 | 198.986 | 196.3665 | 196.6516
567.8948 | 326.656 | 199.2273 | 196.6206 | 196.8983
568.8948 | 326.6699 | 199.4548 | 196.8675 | 197.1421
569.8948 | 326.8274 | 199.6982 | 197.1101 | 197.3918
570.8948 | 326.8443 | 199.9353 | 197.3523 | 197.6274
571.8948 | 326.902 | 200.1623 | 197.5911 | 197.8683
572.8948 | 327.1165 | 200.4081 | 197.8277 | 198.1085
573.8948 | 327.3003 | 200.6476 | 198.0676 | 198.3493
574.8948 | 327.3084 | 200.8757 | 198.3119 | 198.5863
575.8948 | 327.3247 | 201.1217 | 198.5512 | 198.8251
576.8948 | 327.4033 | 201.3554 | 198.7911 | 199.0698
577.8948 | 327.4041 | 201.5962 | 199.0264 | 199.304
578.8948 | 327.3669 | 201.8393 | 199.2634 | 199.5378
579.8948 | 327.2829 | 202.0547 | 199.5015 | 199.7816
580.8948 | 327.1774 | 202.2921 | 199.7446 | 200.0242
581.8948 | 327.2105 | 202.5043 | 199.9793 | 200.2648
582.8948 | 327.2129 | 202.7368 | 200.2183 | 200.5079
583.8948 | 327.195 | 202.974 | 200.4563 | 200.7369
584.8948 | 327.1591 | 203.1953 | 200.6947 | 200.9826
585.8948 | 327.1278 | 203.4077 | 200.9308 | 201.2238
586.8948 | 327.0959 | 203.6254 | 201.1658 | 201.453
587.8948 | 327.047 | 203.8544 | 201.402 | 201.6866
588.8948 | 327.1219 | 204.0654 | 201.6389 | 201.9149
589.8948 | 327.1412 | 204.2832 | 201.8829 | 202.1579
590.8948 | 327.1988 | 204.5005 | 202.1148 | 202.402
591.8948 | 327.2132 | 204.7286 | 202.3389 | 202.6321
592.8948 | 327.1963 | 204.9581 | 202.5745 | 202.8622
593.8948 | 327.1343 | 205.1774 | 202.8023 | 203.0916
594.8948 | 327.0919 | 205.4037 | 203.0263 | 203.3235
595.8948 | 327.082 | 205.6228 | 203.2596 | 203.556
596.8948 | 327.0589 | 205.8389 | 203.4875 | 203.7746
597.8948 | 326.999 | 206.069 | 203.7092 | 204.0063
598.8948 | 326.9426 | 206.3071 | 203.8685 | 204.265
599.8948 | 326.9163 | 206.5217 | 204.1166 | 204.4781
600.8948 | 326.8977 | 206.7848 | 204.2388 | 204.7457
601.8948 | 326.8826 | 207.0034 | 204.472 | 204.9736
602.8948 | 326.8688 | 207.2117 | 204.705 | 205.1861
603.8948 | 326.8137 | 207.4023 | 204.9893 | 205.3846
604.8948 | 326.811 | 207.5949 | 205.2671 | 205.5711
605.8948 | 326.6709 | 207.8238 | 205.4757 | 205.8083
606.8948 | 326.6171 | 208.0191 | 205.7218 | 206.0099
607.8948 | 326.6008 | 208.2357 | 205.9495 | 206.2309
608.8948 | 326.6846 | 208.5262 | 206.0246 | 206.5182
609.8948 | 326.7967 | 208.7497 | 206.2509 | 206.7333
610.8948 | 326.793 | 208.9533 | 206.4703 | 206.9589
611.8948 | 326.8711 | 209.1576 | 206.6908 | 207.1727
612.8948 | 326.9383 | 209.3732 | 206.9044 | 207.3884
613.8948 | 326.9421 | 209.5922 | 207.128 | 207.6093
614.8948 | 326.9047 | 209.8 | 207.3449 | 207.8325
615.8948 | 326.8796 | 210.0121 | 207.5612 | 208.0438
616.8948 | 326.8838 | 210.2223 | 207.7809 | 208.2575
617.8948 | 326.9008 | 210.4304 | 207.9944 | 208.4769
618.8948 | 326.9523 | 210.6489 | 208.2154 | 208.6917
619.8948 | 326.9998 | 210.8509 | 208.4292 | 208.9054
620.8948 | 326.9437 | 211.056 | 208.6489 | 209.119
621.8948 | 326.8853 | 211.2731 | 208.8617 | 209.3294
622.8948 | 326.8486 | 211.4763 | 209.0676 | 209.5407
623.8948 | 326.8426 | 211.7047 | 209.2922 | 209.7603
624.8948 | 326.7832 | 211.9066 | 209.4985 | 209.9659
625.8948 | 326.6958 | 212.1053 | 209.7104 | 210.1819
626.8948 | 326.7145 | 212.3118 | 209.9232 | 210.3942
627.8948 | 326.6857 | 212.5154 | 210.137 | 210.5915
628.8948 | 326.6491 | 212.7275 | 210.3442 | 210.8003
629.8948 | 326.7124 | 212.937 | 210.5581 | 211.0119
630.8948 | 326.7414 | 213.138 | 210.7693 | 211.2076
631.8948 | 326.6746 | 213.3253 | 210.9862 | 211.4047
632.8948 | 326.5876 | 213.5343 | 211.2221 | 211.5989
633.8948 | 326.5363 | 213.7629 | 211.4106 | 211.7867
634.8948 | 326.5536 | 214.0969 | 211.6108 | 211.8671
635.8948 | 326.5695 | 214.3077 | 211.8166 | 212.0743
636.8948 | 326.6436 | 214.5116 | 212.0243 | 212.2847
637.8948 | 326.7978 | 214.7064 | 212.2233 | 212.4954
638.8948 | 326.9222 | 214.8971 | 212.4291 | 212.6969
639.8948 | 326.7697 | 215.1033 | 212.6335 | 212.901
640.8948 | 326.5798 | 215.2984 | 212.84 | 213.0997
641.8948 | 326.4812 | 215.4747 | 213.0408 | 213.3006
642.8948 | 326.4196 | 215.6803 | 213.2459 | 213.5039
643.8948 | 326.3942 | 215.8944 | 213.4414 | 213.7059
644.8948 | 326.4117 | 216.0712 | 213.6443 | 213.9087
645.8948 | 326.5227 | 216.2709 | 213.8467 | 214.0988
646.8948 | 326.5407 | 216.4383 | 214.0513 | 214.3284
647.8948 | 326.5506 | 216.6186 | 214.2479 | 214.5268
648.8948 | 326.4526 | 216.7028 | 214.4441 | 214.8455
649.8948 | 326.3096 | 216.8821 | 214.6362 | 215.0396
650.8948 | 326.233 | 217.0769 | 214.8447 | 215.2379
651.8948 | 326.2027 | 217.2598 | 215.0308 | 215.4364
652.8948 | 326.224 | 217.4639 | 215.236 | 215.6304
653.8948 | 326.1671 | 217.6541 | 215.4261 | 215.8253
654.8948 | 326.1814 | 217.8284 | 215.6167 | 216.02
655.8948 | 326.199 | 218.0125 | 215.8181 | 216.2153
656.8948 | 326.2282 | 218.2054 | 216.0033 | 216.4059
657.8948 | 326.1631 | 218.3961 | 216.2005 | 216.5984
658.8948 | 326.1177 | 218.5885 | 216.3983 | 216.7916
659.8948 | 326.1987 | 218.7636 | 216.5761 | 216.9832
660.8948 | 326.2487 | 218.9519 | 216.7767 | 217.1781
661.8948 | 326.1777 | 219.1213 | 216.9617 | 217.3756
662.8948 | 326.1502 | 219.31 | 217.1571 | 217.5606
663.8948 | 326.1516 | 219.488 | 217.3464 | 217.7544
664.8948 | 326.2293 | 219.6625 | 217.5349 | 217.9433
665.8948 | 326.1886 | 219.8534 | 217.7233 | 218.1376
666.8948 | 326.164 | 220.0227 | 217.9103 | 218.322
667.8948 | 326.183 | 220.2055 | 218.0965 | 218.5142
668.8948 | 326.2616 | 220.3923 | 218.2842 | 218.6957
669.8948 | 326.2322 | 220.5691 | 218.4697 | 218.8895
670.8948 | 326.2092 | 220.7471 | 218.6485 | 219.0728
671.8948 | 326.1464 | 220.9246 | 218.8421 | 219.2566
672.8948 | 326.1406 | 221.0991 | 219.0219 | 219.4431
673.8948 | 326.0582 | 221.2788 | 219.2111 | 219.6262
674.8948 | 326.0094 | 221.4594 | 219.3931 | 219.8066
675.8948 | 325.9731 | 221.635 | 219.5801 | 219.9855
676.8948 | 326.0019 | 221.8112 | 219.7536 | 220.1782
677.8948 | 326.0433 | 221.9849 | 219.9481 | 220.3549
678.8948 | 326.0013 | 222.1542 | 220.1217 | 220.5354
679.8948 | 325.9928 | 222.3349 | 220.303 | 220.721
680.8948 | 326.0835 | 222.5001 | 220.4855 | 220.8967
681.8948 | 326.1165 | 222.6669 | 220.6664 | 221.0791
682.8948 | 326.1747 | 222.8517 | 220.8485 | 221.259
683.8948 | 326.0886 | 223.0215 | 221.021 | 221.4341
684.8948 | 326.024 | 223.1858 | 221.2058 | 221.6158
685.8948 | 326.0419 | 223.3631 | 221.3914 | 221.7935
686.8948 | 326.0514 | 223.5226 | 221.5643 | 221.9842
687.8948 | 326.0868 | 223.6916 | 221.7402 | 222.1527
688.8948 | 325.9722 | 223.8571 | 221.9256 | 222.336
689.8948 | 325.9719 | 224.0339 | 222.0968 | 222.5195
690.8948 | 326.0234 | 224.1939 | 222.2736 | 222.6941
691.8948 | 326.0844 | 224.3519 | 222.4465 | 222.8616
692.8948 | 326.1399 | 224.5129 | 222.6153 | 223.036
693.8948 | 326.2815 | 224.6814 | 222.7867 | 223.2091
694.8948 | 326.2702 | 224.8461 | 222.962 | 223.3772
695.8948 | 326.2302 | 225.018 | 223.1416 | 223.5547
696.8948 | 326.1824 | 225.1816 | 223.3086 | 223.7222
697.8948 | 326.2403 | 225.3557 | 223.4824 | 223.8905
698.8948 | 326.2292 | 225.5138 | 223.6503 | 224.0674
699.8948 | 326.2929 | 225.6731 | 223.8171 | 224.2294
700.8948 | 326.4138 | 225.8313 | 223.9898 | 224.4102
701.8948 | 326.3506 | 226.0036 | 224.1623 | 224.5707
702.8948 | 326.3379 | 226.1569 | 224.3274 | 224.7472
703.8948 | 326.329 | 226.3128 | 224.4954 | 224.9209
704.8948 | 326.3667 | 226.4736 | 224.6655 | 225.0846
705.8948 | 326.3047 | 226.6293 | 224.8352 | 225.249
706.8948 | 326.258 | 226.7863 | 225.0041 | 225.4185
707.8948 | 326.3294 | 226.9362 | 225.162 | 225.5762
708.8948 | 326.2746 | 227.0907 | 225.3321 | 225.7443
709.8948 | 326.2586 | 227.2555 | 225.4909 | 225.9104
710.8948 | 326.3402 | 227.4107 | 225.6589 | 226.074
711.8948 | 326.3872 | 227.5621 | 225.825 | 226.248
712.8948 | 326.2971 | 227.7243 | 225.9845 | 226.4056
713.8948 | 326.186 | 227.8783 | 226.1487 | 226.5705
714.8948 | 326.0716 | 228.0293 | 226.3098 | 226.729
715.8948 | 326.0516 | 228.1868 | 226.4696 | 226.8873
716.8948 | 326.0299 | 228.3371 | 226.6318 | 227.0528
717.8948 | 325.9768 | 228.4958 | 226.7911 | 227.214
718.8948 | 325.9374 | 228.6452 | 226.9609 | 227.3778
719.8948 | 325.9212 | 228.7907 | 227.1175 | 227.5299
720.8948 | 326.1071 | 228.9501 | 227.2765 | 227.6931
721.8948 | 326.1899 | 229.0957 | 227.4302 | 227.8535
722.9104 | 326.1929 | 229.2441 | 227.5956 | 228.0079
723.8948 | 326.2342 | 229.4037 | 227.7534 | 228.1665
724.8948 | 326.2236 | 229.542 | 227.9112 | 228.3237
725.8948 | 326.1108 | 229.6918 | 228.0611 | 228.4861
726.8948 | 326.1932 | 229.8535 | 228.2281 | 228.6402
727.8948 | 326.1776 | 229.992 | 228.3887 | 228.8031
728.8948 | 326.1266 | 230.1541 | 228.5379 | 228.9579
729.8948 | 326.0417 | 230.2913 | 228.6948 | 229.1106
730.8948 | 325.9704 | 230.4174 | 228.8532 | 229.269
731.8948 | 325.9465 | 230.5768 | 229.0044 | 229.4325
732.8948 | 326.0062 | 230.7187 | 229.1627 | 229.5886
733.8948 | 326.0115 | 230.868 | 229.3188 | 229.7388
734.8948 | 325.9852 | 231.0021 | 229.4689 | 229.8888
735.8948 | 326.0512 | 231.1694 | 229.6255 | 230.0455
736.8948 | 326.1041 | 231.3061 | 229.7804 | 230.2007
737.8948 | 326.1891 | 231.4541 | 229.9277 | 230.3488
738.8948 | 326.1785 | 231.5892 | 230.0778 | 230.4991
739.8948 | 326.0567 | 231.7289 | 230.2323 | 230.6462
740.8948 | 326.1305 | 231.8717 | 230.3785 | 230.7974
741.8948 | 326.2543 | 232.0109 | 230.5318 | 230.9452
742.8948 | 326.3607 | 232.1544 | 230.6756 | 231.0994
743.8948 | 326.4257 | 232.2992 | 230.8323 | 231.2433
744.8948 | 326.4576 | 232.445 | 230.9862 | 231.3941
745.8948 | 326.4712 | 232.5767 | 231.1412 | 231.5472
746.8948 | 326.4369 | 232.7266 | 231.2871 | 231.7028
747.8948 | 326.4858 | 232.8725 | 231.4395 | 231.8469
748.8948 | 326.5084 | 233.0131 | 231.5762 | 231.9954
749.8948 | 326.5847 | 233.1449 | 231.7254 | 232.1301
750.8948 | 326.6182 | 233.2725 | 231.8731 | 232.2866
751.8948 | 326.6163 | 233.4284 | 232.0135 | 232.4341
752.8948 | 326.658 | 233.5776 | 232.165 | 232.5746
753.8948 | 326.7572 | 233.7056 | 232.3034 | 232.7157
754.8948 | 326.7173 | 233.85 | 232.4571 | 232.8625
755.8948 | 326.6477 | 233.9699 | 232.5977 | 233.0132
756.8948 | 326.5793 | 234.1187 | 232.7383 | 233.1545
757.8948 | 326.5017 | 234.2526 | 232.8818 | 233.2878
758.8948 | 326.4958 | 234.3816 | 233.0186 | 233.4357
759.8948 | 326.4351 | 234.5057 | 233.1588 | 233.566
760.8948 | 326.4368 | 234.6631 | 233.3068 | 233.714
761.8948 | 326.4978 | 234.7841 | 233.4496 | 233.853
762.8948 | 326.404 | 234.9243 | 233.594 | 233.9909
763.8948 | 326.2728 | 235.0556 | 233.7327 | 234.1306
764.8948 | 326.3059 | 235.183 | 233.8678 | 234.2687
765.8948 | 326.3208 | 235.3298 | 234.0025 | 234.4089
766.8948 | 326.3796 | 235.4519 | 234.1467 | 234.5401
767.8948 | 326.3717 | 235.6021 | 234.2828 | 234.6828
768.8948 | 326.4142 | 235.7143 | 234.4173 | 234.8154
769.8948 | 326.4401 | 235.8544 | 234.5608 | 234.9576
770.8948 | 326.4346 | 235.9764 | 234.702 | 235.0908
771.8948 | 326.4445 | 236.1096 | 234.8315 | 235.2245
772.8948 | 326.4447 | 236.2352 | 234.9735 | 235.3516
773.8948 | 326.5442 | 236.3601 | 235.1169 | 235.4808
774.8948 | 326.5241 | 236.4923 | 235.2442 | 235.6119
775.8948 | 326.4649 | 236.626 | 235.3791 | 235.752
776.8948 | 326.473 | 236.7567 | 235.5187 | 235.8857
777.8948 | 326.4441 | 236.8878 | 235.6458 | 236.0161
778.8948 | 326.4692 | 236.9976 | 235.7909 | 236.1526
779.8948 | 326.519 | 237.1491 | 235.9153 | 236.2975
780.8948 | 326.5397 | 237.2855 | 236.044 | 236.4291
781.8948 | 326.5438 | 237.3975 | 236.1782 | 236.551
782.8948 | 326.4771 | 237.5263 | 236.3056 | 236.6838
783.8948 | 326.4278 | 237.6576 | 236.442 | 236.8129
784.8948 | 326.4203 | 237.7788 | 236.568 | 236.9474
785.8948 | 326.5761 | 237.9063 | 236.7005 | 237.0803
786.8948 | 326.5584 | 238.0329 | 236.8362 | 237.204
787.8948 | 326.4838 | 238.1518 | 236.9634 | 237.3314
788.8948 | 326.4249 | 238.2953 | 237.0952 | 237.4592
789.8948 | 326.4324 | 238.4119 | 237.2312 | 237.5883
790.8948 | 326.3941 | 238.5251 | 237.3612 | 237.7188
791.8948 | 326.2052 | 238.6627 | 237.4864 | 237.851
792.8948 | 326.1048 | 238.7839 | 237.6124 | 237.9782
793.8948 | 326.0625 | 238.9067 | 237.7449 | 238.102
794.8948 | 325.9848 | 239.033 | 237.8699 | 238.2241
795.8948 | 325.9149 | 239.1525 | 237.9984 | 238.3569
796.8948 | 325.9482 | 239.2779 | 238.1245 | 238.4787
797.8948 | 325.9224 | 239.3989 | 238.2533 | 238.6153
798.8948 | 325.9784 | 239.5215 | 238.3784 | 238.7354
799.8948 | 325.9905 | 239.6423 | 238.5061 | 238.8635
800.8948 | 326.0037 | 239.7338 | 238.6349 | 238.9726
801.8948 | 326.0824 | 239.8675 | 238.7552 | 239.0966
802.8948 | 326.0432 | 239.9979 | 238.8847 | 239.2205
803.8948 | 326.0574 | 240.108 | 239.0061 | 239.3481
804.8948 | 326.0937 | 240.2403 | 239.1315 | 239.4689
805.8948 | 326.0534 | 240.3623 | 239.2652 | 239.59
806.8948 | 326.0714 | 240.4809 | 239.3784 | 239.7148
807.8948 | 326.0745 | 240.6159 | 239.5026 | 239.8562
808.8948 | 326.0651 | 240.7321 | 239.629 | 239.9746
809.8948 | 326.1031 | 240.8751 | 239.7586 | 240.0969
810.8948 | 326.0999 | 240.9879 | 239.8795 | 240.2267
811.8948 | 326.0178 | 241.1017 | 240.004 | 240.3462
812.8948 | 326.0267 | 241.2294 | 240.1226 | 240.4662
813.8948 | 326.0233 | 241.3472 | 240.2525 | 240.5836
814.8948 | 326.041 | 241.4633 | 240.3724 | 240.7122
815.8948 | 326.1096 | 241.5801 | 240.4872 | 240.8312
816.8948 | 326.247 | 241.6919 | 240.6122 | 240.9409
817.8948 | 326.3016 | 241.8156 | 240.7381 | 241.0678
818.8948 | 326.1936 | 241.9191 | 240.8667 | 241.1852
819.8948 | 326.1644 | 242.048 | 240.9871 | 241.324
820.8948 | 326.1247 | 242.1674 | 241.1068 | 241.4378
821.8948 | 326.166 | 242.2681 | 241.2295 | 241.5565
822.8948 | 326.1458 | 242.3936 | 241.3484 | 241.678
823.8948 | 326.133 | 242.5102 | 241.4625 | 241.7951
824.8948 | 326.0634 | 242.6291 | 241.5784 | 241.912
825.8948 | 326.0286 | 242.7252 | 241.7023 | 242.0187
826.8948 | 326.0049 | 242.845 | 241.8217 | 242.136
827.8948 | 325.9286 | 242.9359 | 241.9393 | 242.257
828.8948 | 325.8812 | 243.071 | 242.0601 | 242.3762
829.8948 | 325.8338 | 243.2198 | 242.1782 | 242.4366
830.8948 | 325.899 | 243.3541 | 242.2909 | 242.5542
831.8948 | 325.7877 | 243.4654 | 242.41 | 242.6721
832.8948 | 325.7256 | 243.5664 | 242.5242 | 242.788
833.8948 | 325.7477 | 243.6872 | 242.6401 | 242.8961
834.8948 | 325.6246 | 243.7965 | 242.7596 | 243.0165
835.8948 | 325.659 | 243.9068 | 242.8761 | 243.1363
836.8948 | 325.5558 | 244.0136 | 242.9876 | 243.2509
837.8948 | 325.5794 | 244.1334 | 243.1056 | 243.3578
838.8948 | 325.5716 | 244.2359 | 243.2209 | 243.4722
839.8948 | 325.5595 | 244.3625 | 243.3383 | 243.5946
840.8948 | 325.5335 | 244.4533 | 243.4488 | 243.6996
841.8948 | 325.3509 | 244.5742 | 243.5662 | 243.8132
842.8948 | 325.343 | 244.6876 | 243.6787 | 243.9264
843.8948 | 325.3612 | 244.7963 | 243.7863 | 244.0465
844.8948 | 325.2154 | 244.9065 | 243.9045 | 244.1586
845.8948 | 325.1303 | 245.014 | 244.0156 | 244.272
846.8948 | 325.0758 | 245.1283 | 244.137 | 244.3894
847.8948 | 325.0672 | 245.2451 | 244.2438 | 244.4978
848.8948 | 324.941 | 245.339 | 244.3533 | 244.6132
849.8948 | 324.8608 | 245.441 | 244.472 | 244.7213
850.8948 | 324.7908 | 245.5481 | 244.581 | 244.8364
851.8948 | 324.7811 | 245.6645 | 244.6968 | 244.9412
852.8948 | 324.7968 | 245.7735 | 244.8072 | 245.0547
853.8948 | 324.9027 | 245.8779 | 244.9133 | 245.1628
854.8948 | 324.843 | 245.9803 | 245.0231 | 245.2791
855.8948 | 324.8192 | 246.1182 | 245.1394 | 245.3819
856.8948 | 324.8825 | 246.2196 | 245.2498 | 245.4918
857.8948 | 324.8774 | 246.3141 | 245.3568 | 245.6073
858.8948 | 324.951 | 246.4005 | 245.4715 | 245.7108
859.8948 | 324.9696 | 246.5131 | 245.5792 | 245.8251
860.8948 | 324.9817 | 246.6155 | 245.6899 | 245.9332
861.8948 | 324.9448 | 246.7248 | 245.7975 | 246.0383
862.8948 | 324.9667 | 246.8286 | 245.9045 | 246.149
863.8948 | 325.0309 | 246.9216 | 246.0166 | 246.2571
864.8948 | 325.0807 | 247.0246 | 246.1203 | 246.3655
865.8948 | 324.9858 | 247.1332 | 246.2259 | 246.4739
866.8948 | 324.9478 | 247.2322 | 246.3388 | 246.5819
867.8948 | 324.9351 | 247.343 | 246.4449 | 246.688
868.8948 | 324.926 | 247.4399 | 246.5534 | 246.7944
869.8948 | 324.9016 | 247.5484 | 246.6669 | 246.8944
870.8948 | 324.84 | 247.6576 | 246.7689 | 247.0058
871.8948 | 324.9073 | 247.7578 | 246.8712 | 247.1117
872.8948 | 324.9084 | 247.8594 | 246.9858 | 247.2114
873.8948 | 324.8486 | 247.957 | 247.0853 | 247.3145
874.8948 | 324.8491 | 248.0651 | 247.1937 | 247.4198
875.8948 | 324.9241 | 248.1598 | 247.3044 | 247.5204
876.8948 | 324.9893 | 248.2569 | 247.4058 | 247.634
877.8948 | 325.1427 | 248.3678 | 247.5085 | 247.7365
878.8948 | 325.2283 | 248.4703 | 247.6104 | 247.8411
879.8948 | 325.331 | 248.561 | 247.7197 | 247.9401
880.8948 | 325.3644 | 248.6655 | 247.8207 | 248.0512
881.8948 | 325.5241 | 248.7626 | 247.9265 | 248.1422
882.8948 | 325.6603 | 248.8611 | 248.0316 | 248.2572
883.8948 | 325.6962 | 248.9691 | 248.1375 | 248.3537
884.8948 | 325.7353 | 249.0624 | 248.2422 | 248.4564
885.8948 | 325.7645 | 249.1608 | 248.3446 | 248.5556
886.8948 | 325.8222 | 249.2582 | 248.4411 | 248.6547
887.8948 | 325.9285 | 249.3562 | 248.5528 | 248.7542
888.8948 | 325.972 | 249.4557 | 248.6575 | 248.865
889.8948 | 326.0282 | 249.5389 | 248.7557 | 248.9583
890.8948 | 326.102 | 249.6541 | 248.8523 | 249.0571
891.8948 | 326.0966 | 249.7385 | 248.9576 | 249.1592
892.8948 | 326.1271 | 249.8369 | 249.0555 | 249.2578
893.8948 | 326.0769 | 249.9209 | 249.1647 | 249.3564
894.8948 | 326.0073 | 250.0322 | 249.2654 | 249.4529
895.8948 | 326.033 | 250.1219 | 249.3634 | 249.5553
896.8948 | 326.0286 | 250.2071 | 249.4596 | 249.6492
897.8948 | 325.9484 | 250.3028 | 249.566 | 249.7593
898.8948 | 325.9417 | 250.4119 | 249.6641 | 249.856
899.8948 | 325.8554 | 250.5022 | 249.7596 | 249.9457
900.8948 | 325.7793 | 250.5937 | 249.8584 | 250.0489
901.8948 | 325.659 | 250.7031 | 249.9544 | 250.1402
902.8948 | 325.6359 | 250.7932 | 250.0554 | 250.2426
903.8948 | 325.6748 | 250.8769 | 250.1463 | 250.3342
904.8948 | 325.6897 | 250.9714 | 250.247 | 250.434
905.8948 | 325.709 | 251.0599 | 250.3426 | 250.53
906.8948 | 325.6798 | 251.1541 | 250.4446 | 250.6339
907.8948 | 325.6349 | 251.2414 | 250.554 | 250.7135
908.8948 | 325.5641 | 251.3364 | 250.641 | 250.8101
909.8948 | 325.4824 | 251.4223 | 250.7391 | 250.9087
910.8948 | 325.4995 | 251.5056 | 250.8281 | 251.0078
911.8948 | 325.4687 | 251.6087 | 250.9341 | 251.1055
912.8948 | 325.4988 | 251.708 | 251.0231 | 251.2009
913.8948 | 325.477 | 251.7947 | 251.1192 | 251.2934
914.8948 | 325.5519 | 251.8805 | 251.2213 | 251.396
915.8948 | 325.5549 | 251.9838 | 251.3056 | 251.4857
916.8948 | 325.5942 | 252.0654 | 251.4104 | 251.5795
917.8948 | 325.5584 | 252.1632 | 251.5017 | 251.672
918.8948 | 325.5847 | 252.2486 | 251.5904 | 251.7632
919.8948 | 325.5939 | 252.3386 | 251.6924 | 251.8561
920.8948 | 325.5368 | 252.4115 | 251.7852 | 251.9482
921.8948 | 325.4562 | 252.5125 | 251.8762 | 252.0464
922.8948 | 325.4898 | 252.605 | 251.9663 | 252.1335
923.8948 | 325.4909 | 252.6891 | 252.0622 | 252.2242
924.8948 | 325.4314 | 252.7756 | 252.1574 | 252.3154
925.8948 | 325.4962 | 252.8703 | 252.2531 | 252.4104
926.8948 | 325.5569 | 252.9603 | 252.3314 | 252.4993
927.8948 | 325.6005 | 253.0411 | 252.4315 | 252.5956
928.8948 | 325.6195 | 253.1263 | 252.5217 | 252.6783
929.8948 | 325.7201 | 253.2154 | 252.6156 | 252.779
930.8948 | 325.7435 | 253.3077 | 252.7049 | 252.8596
931.8948 | 325.6397 | 253.3845 | 252.7942 | 252.9464
932.8948 | 325.6241 | 253.4663 | 252.8821 | 253.0404
933.8948 | 325.7549 | 253.5562 | 252.9758 | 253.131
934.8948 | 325.8926 | 253.6379 | 253.0618 | 253.2226
935.8948 | 325.8618 | 253.7173 | 253.1576 | 253.31
936.8948 | 325.8878 | 253.7977 | 253.2466 | 253.3946
937.8948 | 325.9262 | 253.8847 | 253.3424 | 253.4804
938.8948 | 325.874 | 253.9789 | 253.4284 | 253.5751
939.8948 | 325.9185 | 254.0316 | 253.5165 | 253.6621
940.8948 | 325.9954 | 254.1252 | 253.6094 | 253.7538
941.8948 | 325.9798 | 254.2229 | 253.6926 | 253.8415
942.8948 | 325.9575 | 254.3083 | 253.7841 | 253.9304
943.8948 | 325.903 | 254.3811 | 253.8764 | 254.014
944.8948 | 325.8547 | 254.4543 | 253.9648 | 254.0991
945.8948 | 325.8211 | 254.5455 | 254.0467 | 254.1862
946.8948 | 325.8317 | 254.6392 | 254.1367 | 254.2769
947.8948 | 325.8483 | 254.7183 | 254.2203 | 254.3621
948.8948 | 325.834 | 254.7901 | 254.3083 | 254.4463
949.8948 | 325.7542 | 254.8774 | 254.4 | 254.5355
950.8948 | 325.7365 | 255.0169 | 254.4807 | 254.615
951.8948 | 325.7557 | 255.0702 | 254.5678 | 254.6942
952.8948 | 325.7357 | 255.1133 | 254.6507 | 254.7838
953.8948 | 325.663 | 255.2133 | 254.7393 | 254.8719
954.8948 | 325.5645 | 255.2969 | 254.8288 | 254.9556
955.8948 | 325.6241 | 255.3717 | 254.9186 | 255.0421
956.8948 | 325.6604 | 255.4477 | 255.0084 | 255.127
957.8948 | 325.7728 | 255.5299 | 255.0918 | 255.2118
958.8948 | 325.7572 | 255.6065 | 255.1701 | 255.2938
959.8948 | 325.697 | 255.7395 | 255.2623 | 255.3788
960.8948 | 325.6256 | 255.8226 | 255.35 | 255.4604
961.8948 | 325.6123 | 255.9021 | 255.4372 | 255.552
962.8948 | 325.5898 | 255.9801 | 255.5169 | 255.6291
963.8948 | 325.5436 | 256.0603 | 255.5963 | 255.7084
964.8948 | 325.4697 | 256.1309 | 255.6773 | 255.8055
965.8948 | 325.5175 | 256.2188 | 255.7633 | 255.8892
966.8948 | 325.5513 | 256.3238 | 255.8464 | 255.9622
967.8948 | 325.5887 | 256.3034 | 255.9322 | 256.0534
968.8948 | 325.4806 | 256.4732 | 256.0117 | 256.1228
969.8948 | 325.4205 | 256.5401 | 256.0952 | 256.2051
970.8948 | 325.3194 | 256.6093 | 256.1741 | 256.2833
971.8948 | 325.2134 | 256.6931 | 256.2532 | 256.3613
972.8948 | 325.1613 | 256.7665 | 256.331 | 256.4461
973.8948 | 325.2037 | 256.8463 | 256.4093 | 256.5202
974.8948 | 325.1854 | 256.909 | 256.4954 | 256.6007
975.8948 | 325.2874 | 256.9919 | 256.5765 | 256.6826
976.8948 | 325.3153 | 257.0705 | 256.6567 | 256.7599
977.8948 | 325.2456 | 257.1438 | 256.7385 | 256.8402
978.8948 | 325.168 | 257.2173 | 256.8156 | 256.9148
979.8948 | 325.1546 | 257.2853 | 256.8966 | 256.9972
980.8948 | 325.1859 | 257.3724 | 256.9641 | 257.0679
981.8948 | 325.245 | 257.4528 | 257.0512 | 257.152
982.8948 | 325.3059 | 257.5175 | 257.1221 | 257.2247
983.8948 | 325.3191 | 257.5948 | 257.2045 | 257.3074
984.8948 | 325.3259 | 257.6754 | 257.283 | 257.3855
985.8948 | 325.3557 | 257.7503 | 257.365 | 257.4601
986.8948 | 325.3469 | 257.8266 | 257.4427 | 257.5325
987.8948 | 325.3653 | 257.8969 | 257.5196 | 257.6068
988.8948 | 325.402 | 257.9788 | 257.5991 | 257.6781
989.8948 | 325.3857 | 258.0462 | 257.6789 | 257.7575
990.8948 | 325.4368 | 258.0075 | 257.7611 | 257.8502
991.8948 | 325.3942 | 258.0771 | 257.8443 | 257.9247
992.8948 | 325.4204 | 258.152 | 257.9136 | 258.0062
993.8948 | 325.3829 | 258.2339 | 257.9922 | 258.0774
994.8948 | 325.3707 | 258.2979 | 258.0804 | 258.1547
995.8948 | 325.4247 | 258.4902 | 258.1317 | 258.2147
996.8948 | 325.4775 | 258.4383 | 258.2233 | 258.3135
997.8948 | 325.482 | 258.4997 | 258.3058 | 258.3822
998.8948 | 325.5251 | 258.6964 | 258.3618 | 258.4355
999.8948 | 325.5272 | 258.7668 | 258.4341 | 258.5124
1000.8948 | 325.6069 | 258.8261 | 258.5091 | 258.5811
1001.8948 | 325.635 | 258.8942 | 258.5833 | 258.6588
1002.8948 | 325.6602 | 258.9629 | 258.6543 | 258.727
1003.8948 | 325.7156 | 259.0304 | 258.7373 | 258.8096
1004.8948 | 325.6521 | 259.1144 | 258.8012 | 258.8814
1005.8948 | 325.663 | 259.179 | 258.8749 | 258.947
1006.8948 | 325.7547 | 259.2499 | 258.9497 | 259.0243
1007.8948 | 325.7171 | 259.3215 | 259.0284 | 259.0986
1008.8948 | 325.5985 | 259.3906 | 259.1022 | 259.1679
1009.8948 | 325.4552 | 259.4654 | 259.1747 | 259.2381
1010.8948 | 325.5705 | 259.5282 | 259.2441 | 259.3116
1011.8948 | 325.5667 | 259.5952 | 259.3143 | 259.3835
1012.8948 | 325.5066 | 259.6732 | 259.383 | 259.4578
1013.8948 | 325.4792 | 259.7453 | 259.4615 | 259.5279
1014.8948 | 325.5189 | 259.6657 | 259.5533 | 259.6171
1015.8948 | 325.4961 | 259.7477 | 259.6257 | 259.6924
1016.8948 | 325.5097 | 259.8223 | 259.6931 | 259.7613
1017.8948 | 325.4562 | 259.8898 | 259.7674 | 259.834
1018.8948 | 325.4219 | 259.9738 | 259.8376 | 259.9028
1019.8948 | 325.4383 | 260.0481 | 259.9152 | 259.9706
1020.8948 | 325.5398 | 260.1276 | 259.9884 | 260.0438
1021.8948 | 325.6044 | 260.191 | 260.0614 | 260.119
1022.8948 | 325.6236 | 260.2486 | 260.1367 | 260.1868
1023.8948 | 325.6567 | 260.3247 | 260.2105 | 260.2641
1024.8948 | 325.7586 | 260.3845 | 260.2829 | 260.3286
1025.8948 | 325.8944 | 260.4593 | 260.3505 | 260.3959
1026.8948 | 325.8433 | 260.531 | 260.414 | 260.4637
1027.8948 | 325.8067 | 260.5834 | 260.4879 | 260.5405
1028.8948 | 325.8614 | 260.6592 | 260.5632 | 260.6175
1029.8948 | 325.8738 | 260.725 | 260.6244 | 260.6826
1030.8948 | 325.9101 | 260.7926 | 260.6959 | 260.7486
1031.8948 | 325.9742 | 260.8618 | 260.7626 | 260.8199
1032.8948 | 325.983 | 260.9301 | 260.8323 | 260.8861
1033.8948 | 326.0241 | 260.993 | 260.9027 | 260.9542
1034.8948 | 325.9958 | 261.0553 | 260.9727 | 261.031
1035.8948 | 325.9667 | 261.1209 | 261.0393 | 261.0964
1036.8948 | 325.8636 | 261.1917 | 261.1138 | 261.1658
1037.8948 | 325.798 | 261.2458 | 261.1796 | 261.2278
1038.8948 | 325.701 | 261.3081 | 261.2484 | 261.2975
1039.8948 | 325.661 | 261.3713 | 261.3103 | 261.3611
1040.8948 | 325.7493 | 261.4424 | 261.3818 | 261.4384
1041.8948 | 325.8403 | 261.5086 | 261.4473 | 261.5005
1042.8948 | 325.8048 | 261.5725 | 261.5156 | 261.5697
1043.8948 | 325.8277 | 261.6154 | 261.5869 | 261.6372
1044.8948 | 325.8209 | 261.6849 | 261.6451 | 261.6987
1045.8948 | 325.8856 | 261.7576 | 261.7155 | 261.7721
1046.8948 | 325.8748 | 261.8259 | 261.7822 | 261.8339
1047.8948 | 325.7806 | 261.8801 | 261.849 | 261.9014
1048.8948 | 325.6957 | 261.9486 | 261.9182 | 261.9605
1049.8948 | 325.6908 | 262.0046 | 261.9793 | 262.0299
1050.8948 | 325.7039 | 262.0654 | 262.0415 | 262.0939
1051.8948 | 325.6832 | 262.1191 | 262.1053 | 262.1586
1052.8948 | 325.5792 | 262.1741 | 262.1746 | 262.2239
1053.8948 | 325.6188 | 262.2453 | 262.2345 | 262.285
1054.8948 | 325.6247 | 262.3024 | 262.3028 | 262.3506
1055.8948 | 325.6435 | 262.3468 | 262.3591 | 262.408
1056.8948 | 325.5586 | 262.4145 | 262.4233 | 262.4685
1057.8948 | 325.4541 | 262.4682 | 262.4826 | 262.5332
1058.8948 | 325.5237 | 262.5302 | 262.5462 | 262.5907
1059.8948 | 325.4913 | 262.5888 | 262.6065 | 262.6438
1060.8948 | 325.4073 | 262.6373 | 262.6676 | 262.7159
1061.8948 | 325.3411 | 262.7001 | 262.7239 | 262.7726
1062.8948 | 325.2478 | 262.7638 | 262.7887 | 262.8288
1063.8948 | 325.2274 | 262.826 | 262.85 | 262.8889
1064.8948 | 325.2202 | 262.8783 | 262.9051 | 262.9559
1065.8948 | 325.1059 | 262.9311 | 262.9659 | 263.0169
1066.8948 | 325.1369 | 262.9855 | 263.0304 | 263.0742
1067.8948 | 325.1217 | 263.0503 | 263.0925 | 263.1352
1068.8948 | 325.0238 | 263.0972 | 263.149 | 263.1956
1069.8948 | 325.0047 | 263.1544 | 263.213 | 263.2533
1070.8948 | 325.0032 | 263.2065 | 263.2693 | 263.3147
1071.8948 | 325.0361 | 263.2625 | 263.3291 | 263.3708
1072.8948 | 325.1153 | 263.318 | 263.3901 | 263.4332
1073.8948 | 325.1349 | 263.3858 | 263.4434 | 263.4947
1074.8948 | 325.0641 | 263.4309 | 263.5063 | 263.5419
1075.8948 | 325.06 | 263.4931 | 263.5624 | 263.6065
1076.8948 | 325.1542 | 263.5413 | 263.6186 | 263.6598
1077.8948 | 325.1818 | 263.5888 | 263.6773 | 263.7257
1078.8948 | 325.2891 | 263.6483 | 263.7281 | 263.7801
1079.8948 | 325.301 | 263.6998 | 263.7929 | 263.836
1080.8948 | 325.3309 | 263.7552 | 263.8495 | 263.8868
1081.8948 | 325.384 | 263.811 | 263.9032 | 263.95
1082.8948 | 325.4927 | 263.8622 | 263.9504 | 264.011
1083.8948 | 325.4774 | 263.8991 | 264.008 | 264.0642
1084.8948 | 325.5311 | 263.9624 | 264.0716 | 264.1187
1085.8948 | 325.4535 | 264.0284 | 264.1273 | 264.1719
1086.8948 | 325.4859 | 264.0705 | 264.1791 | 264.2313
1087.8948 | 325.5889 | 264.1263 | 264.236 | 264.2814
1088.8948 | 325.6489 | 264.3505 | 264.2676 | 264.3221
1089.8948 | 325.6757 | 264.4546 | 264.323 | 264.3711
1090.8948 | 325.7058 | 264.4864 | 264.3751 | 264.4299
1091.8948 | 325.8183 | 264.5482 | 264.4255 | 264.4882
1092.8948 | 325.8991 | 264.5951 | 264.4871 | 264.5384
1093.8948 | 325.8488 | 264.4235 | 264.5581 | 264.608
1094.8948 | 325.8653 | 264.4883 | 264.6176 | 264.6696
1095.8948 | 325.8207 | 264.5352 | 264.6708 | 264.7202
1096.8948 | 325.8311 | 264.5844 | 264.7161 | 264.7802
1097.8948 | 325.8684 | 264.6499 | 264.7745 | 264.8335
1098.8948 | 325.8607 | 264.7019 | 264.8331 | 264.886
1099.8948 | 325.867 | 264.7493 | 264.8873 | 264.9483
1100.8948 | 325.8534 | 264.8105 | 264.9391 | 264.9969
1101.8948 | 325.804 | 264.872 | 264.9941 | 265.0571
1102.8948 | 325.7726 | 264.9116 | 265.0481 | 265.1087
1103.8948 | 325.7873 | 264.9565 | 265.1012 | 265.1602
1104.8948 | 325.8183 | 265.0144 | 265.1577 | 265.216
1105.8948 | 325.8152 | 265.0679 | 265.215 | 265.2651
1106.8948 | 325.68 | 265.1243 | 265.2625 | 265.3299
1107.8948 | 325.6148 | 265.176 | 265.3186 | 265.3806
1108.8948 | 325.548 | 265.2245 | 265.3694 | 265.431
1109.8948 | 325.577 | 265.2673 | 265.4239 | 265.4915
1110.8948 | 325.6396 | 265.3391 | 265.4805 | 265.5453
1111.8948 | 325.749 | 265.3928 | 265.5319 | 265.5888
1112.8948 | 325.5865 | 265.4417 | 265.5838 | 265.6528
1113.8948 | 325.518 | 265.4933 | 265.632 | 265.7022
1114.8948 | 325.4796 | 265.5466 | 265.6932 | 265.7599
1115.8948 | 325.396 | 265.5908 | 265.7393 | 265.8043
1116.8948 | 325.4058 | 265.6412 | 265.7936 | 265.8654
1117.8948 | 325.3656 | 265.6993 | 265.8501 | 265.9156
1118.8948 | 325.4035 | 265.746 | 265.9054 | 265.9653
1119.8948 | 325.3859 | 265.79 | 265.9592 | 266.0238
1120.8948 | 325.3827 | 265.8518 | 266.0161 | 266.0769
1121.8948 | 325.4646 | 265.9017 | 266.0618 | 266.1399
1122.8948 | 325.334 | 265.9599 | 266.1221 | 266.1906
1123.8948 | 325.2175 | 266.0125 | 266.1763 | 266.2439
1124.8948 | 325.1986 | 266.0541 | 266.2252 | 266.2986
1125.8948 | 325.1779 | 266.3183 | 266.2603 | 266.331
1126.8948 | 325.1444 | 266.3831 | 266.3096 | 266.3837
1127.8948 | 325.1368 | 266.4302 | 266.3657 | 266.4385
1128.8948 | 325.0993 | 266.4859 | 266.4177 | 266.4956
1129.8948 | 325.0706 | 266.534 | 266.4731 | 266.5433
1130.8948 | 325.0352 | 266.5966 | 266.5275 | 266.6017
1131.8948 | 325.0121 | 266.6381 | 266.5805 | 266.6562
1132.8948 | 325.1001 | 266.6905 | 266.6371 | 266.7091
1133.8948 | 324.9726 | 266.7516 | 266.6895 | 266.7653
1134.8948 | 324.8933 | 266.8026 | 266.7448 | 266.821
1135.8948 | 324.8108 | 266.855 | 266.7951 | 266.8701
1136.8948 | 324.7994 | 266.9163 | 266.8522 | 266.9326
1137.8948 | 324.7783 | 266.9672 | 266.9054 | 266.9816
1138.8948 | 324.7726 | 267.0216 | 266.9554 | 267.0326
1139.8948 | 324.769 | 267.0768 | 267.0134 | 267.0938
1140.8948 | 324.6589 | 267.1104 | 267.0647 | 267.1446
1141.8948 | 324.6513 | 267.1715 | 267.1135 | 267.2009
1142.8948 | 324.6097 | 267.2174 | 267.1743 | 267.258
1143.8948 | 324.5594 | 267.275 | 267.2231 | 267.3137
1144.8948 | 324.5401 | 267.3258 | 267.281 | 267.3649
1145.8948 | 324.5008 | 267.365 | 267.3366 | 267.4219
1146.8948 | 324.445 | 267.4227 | 267.3915 | 267.4763
1147.8948 | 324.3475 | 267.4618 | 267.438 | 267.5294
1148.8948 | 324.3229 | 267.5147 | 267.4877 | 267.5802
1149.8948 | 324.2709 | 267.5512 | 267.5362 | 267.6332
1150.8948 | 324.2976 | 267.5965 | 267.5862 | 267.6808
1151.8948 | 324.3502 | 267.6624 | 267.6377 | 267.7338
1152.8948 | 324.4015 | 267.7048 | 267.6866 | 267.7917
1153.8948 | 324.4177 | 267.7387 | 267.7386 | 267.8374
1154.8948 | 324.4821 | 267.7926 | 267.784 | 267.8907
1155.8948 | 324.354 | 267.838 | 267.8308 | 267.9412
1156.8948 | 324.2174 | 267.8827 | 267.8876 | 267.9908
1157.8948 | 324.1415 | 267.9129 | 267.9348 | 268.0527
1158.8948 | 324.1401 | 267.9759 | 267.9824 | 268.0991
1159.8948 | 324.0454 | 268.0121 | 268.03 | 268.1484
1160.8948 | 324.0281 | 268.0609 | 268.0812 | 268.1947
1161.8948 | 324.0788 | 268.1011 | 268.127 | 268.2374
1162.8948 | 324.0351 | 268.1472 | 268.1756 | 268.2921
1163.8948 | 323.9847 | 268.2005 | 268.2278 | 268.3431
1164.8948 | 323.9844 | 268.2433 | 268.2713 | 268.3924
1165.8948 | 323.9852 | 268.2808 | 268.3214 | 268.439
1166.8948 | 323.9925 | 268.3223 | 268.3666 | 268.4926
1167.8948 | 324.0017 | 268.3742 | 268.4136 | 268.5415
1168.8948 | 324.0238 | 268.4138 | 268.462 | 268.5853
1169.8948 | 324.0892 | 268.4523 | 268.5052 | 268.6354
1170.8948 | 324.141 | 268.497 | 268.5534 | 268.6867
1171.8948 | 324.1961 | 268.5422 | 268.6004 | 268.7367
1172.8948 | 324.3364 | 268.5703 | 268.6458 | 268.7885
1173.8948 | 324.439 | 268.619 | 268.6868 | 268.8342
1174.8948 | 324.5988 | 268.6759 | 268.7321 | 268.873
1175.8948 | 324.6233 | 268.7226 | 268.7851 | 268.929
1176.8948 | 324.6197 | 268.7656 | 268.8346 | 268.969
1177.8948 | 324.8173 | 268.8072 | 268.8787 | 269.0203
1178.8948 | 324.8567 | 268.8588 | 268.9257 | 269.0673
1179.8948 | 324.8763 | 268.886 | 268.9722 | 269.1228
1180.8948 | 324.9009 | 268.9389 | 269.0172 | 269.166
1181.8948 | 324.9481 | 268.9835 | 269.0644 | 269.222
1182.8948 | 324.9286 | 269.0288 | 269.1043 | 269.2624
1183.8948 | 324.9164 | 269.0714 | 269.1537 | 269.3134
1184.8948 | 324.9991 | 269.1082 | 269.1977 | 269.3626
1185.8948 | 325.1192 | 269.1711 | 269.2397 | 269.4006
1186.8948 | 325.1185 | 269.2099 | 269.291 | 269.4538
1187.8948 | 325.1664 | 269.2474 | 269.336 | 269.5048
1188.8948 | 325.1439 | 269.2995 | 269.378 | 269.5471
1189.8948 | 325.1286 | 269.3536 | 269.4247 | 269.5963
1190.8948 | 325.1439 | 269.3939 | 269.4729 | 269.6438
1191.8948 | 325.222 | 269.4194 | 269.5181 | 269.6963
1192.8948 | 325.2578 | 269.4523 | 269.5574 | 269.7443
1193.8948 | 325.2002 | 269.505 | 269.6036 | 269.7882
1194.8948 | 325.2234 | 269.5453 | 269.6485 | 269.8336
1195.8948 | 325.1684 | 269.5874 | 269.6958 | 269.8823
1196.8948 | 325.1405 | 269.6494 | 269.7445 | 269.9347
1197.8948 | 325.1446 | 269.687 | 269.7823 | 269.9765
1198.8948 | 325.0551 | 269.7364 | 269.8215 | 270.0275
1199.8948 | 325.075 | 269.7792 | 269.8703 | 270.0733
1200.8948 | 325.0449 | 269.8129 | 269.9071 | 270.1231
1201.8948 | 325.0591 | 269.8663 | 269.9453 | 270.1743
1202.8948 | 325.09 | 269.9192 | 269.9871 | 270.2268
1203.8948 | 325.14 | 269.9464 | 270.0294 | 270.2754
1204.8948 | 325.2038 | 270.0046 | 270.079 | 270.318
1205.8948 | 325.1307 | 270.0556 | 270.1184 | 270.3741
1206.8948 | 325.0575 | 270.1106 | 270.1571 | 270.4215
1207.8948 | 325.0132 | 270.1474 | 270.1944 | 270.4762
1208.8948 | 325.0051 | 270.193 | 270.2323 | 270.5234
1209.8948 | 324.9555 | 270.2382 | 270.2736 | 270.5693
1210.8948 | 325.0134 | 270.3037 | 270.3235 | 270.6155
1211.8948 | 325.0592 | 270.3431 | 270.3638 | 270.6709
1212.8948 | 324.9854 | 270.3962 | 270.4041 | 270.7147
1213.8948 | 324.964 | 270.4576 | 270.4511 | 270.7655
1214.8948 | 324.9714 | 270.5145 | 270.4887 | 270.8132
1215.8948 | 324.9686 | 270.5535 | 270.5337 | 270.8652
1216.8948 | 324.991 | 270.6238 | 270.5718 | 270.9119
1217.8948 | 324.9468 | 270.7244 | 270.6216 | 270.9636
1218.8948 | 325.0588 | 270.7709 | 270.654 | 271.0088
1219.8948 | 325.1109 | 270.8339 | 270.6933 | 271.0471
1220.8948 | 325.0646 | 270.8769 | 270.734 | 271.0934
1221.8948 | 325.1018 | 270.9222 | 270.7584 | 271.1285
1222.8948 | 325.1405 | 270.967 | 270.7947 | 271.1679
1223.8948 | 325.184 | 270.998 | 270.8197 | 271.2052
1224.8948 | 325.1901 | 271.0494 | 270.856 | 271.2403
1225.8948 | 325.1793 | 271.0739 | 270.8877 | 271.2738
1226.8948 | 325.2033 | 271.127 | 270.9209 | 271.3075
1227.8948 | 325.2842 | 271.1644 | 270.9487 | 271.3432
1228.8948 | 325.2431 | 271.1998 | 270.979 | 271.38
1229.8948 | 325.2081 | 271.2395 | 271.0113 | 271.4127
1230.8948 | 325.2796 | 271.2743 | 271.0368 | 271.4518
1231.8948 | 325.3645 | 271.3037 | 271.0713 | 271.48
1232.8948 | 325.3277 | 271.3382 | 271.1007 | 271.524
1233.9104 | 325.379 | 271.3818 | 271.1285 | 271.5564
1234.8948 | 325.3134 | 271.4175 | 271.1694 | 271.5943
1235.8948 | 325.2366 | 271.4465 | 271.1968 | 271.6309
1236.8948 | 325.2107 | 271.4814 | 271.2334 | 271.6681
1237.8948 | 325.2128 | 271.525 | 271.2578 | 271.7019
1238.8948 | 325.1913 | 271.555 | 271.2864 | 271.7327
1239.8948 | 325.0409 | 271.5908 | 271.3129 | 271.7622
1240.8948 | 324.9737 | 271.6285 | 271.3515 | 271.798
1241.8948 | 324.9771 | 271.6644 | 271.3796 | 271.8244
1242.8948 | 324.9861 | 271.5989 | 271.4612 | 271.8798
1243.8948 | 324.9864 | 271.6292 | 271.4849 | 271.9019
1244.8948 | 324.9417 | 271.6559 | 271.5149 | 271.9342
1245.8948 | 324.8909 | 271.6955 | 271.5443 | 271.9601
1246.8948 | 324.8756 | 271.7328 | 271.5711 | 271.9883
1247.8948 | 324.8891 | 271.789 | 271.6007 | 271.9988
1248.8948 | 324.8426 | 271.8292 | 271.6332 | 272.0087
1249.8948 | 324.8935 | 271.8618 | 271.6523 | 272.0309
1250.8948 | 324.9678 | 271.9114 | 271.6845 | 272.0528
1251.8948 | 324.9301 | 271.9454 | 271.7027 | 272.0794
1252.8948 | 325.0919 | 271.9709 | 271.7279 | 272.0909
1253.8948 | 325.1182 | 272.0153 | 271.7549 | 272.1091
1254.8948 | 325.1686 | 272.0313 | 271.7835 | 272.127
1255.8948 | 325.1938 | 272.0773 | 271.8088 | 272.1349
1256.8948 | 325.1784 | 272.1024 | 271.8288 | 272.1421
1257.8948 | 325.0972 | 272.1467 | 271.8499 | 272.1594
1258.8948 | 324.9613 | 272.1528 | 271.8746 | 272.1567
1259.8948 | 324.9217 | 272.1728 | 271.8971 | 272.1678
1260.8948 | 324.9882 | 272.1732 | 271.9265 | 272.1678
1261.8948 | 325.0422 | 272.1977 | 271.9434 | 272.1686
1262.8948 | 325.0178 | 272.2063 | 271.9602 | 272.1691
1263.9104 | 325.0181 | 272.2392 | 271.9816 | 272.1636
1264.8948 | 325.0794 | 272.2459 | 271.9996 | 272.1657
1265.8948 | 325.0409 | 272.246 | 272.0152 | 272.1609
1266.8948 | 324.9986 | 272.2514 | 272.0271 | 272.1568
1267.8948 | 325.0565 | 272.2584 | 272.0425 | 272.1587
1268.8948 | 325.0698 | 272.2627 | 272.0607 | 272.1539
1269.8948 | 325.0071 | 272.2795 | 272.072 | 272.1628
1270.8948 | 324.9602 | 272.2888 | 272.0835 | 272.16
1271.8948 | 324.9128 | 272.292 | 272.1056 | 272.1651
1272.8948 | 324.8829 | 272.3038 | 272.1134 | 272.1696
1273.8948 | 324.8975 | 272.3099 | 272.1282 | 272.1751
1274.8948 | 324.8705 | 272.3116 | 272.1396 | 272.1842
1275.8948 | 324.819 | 272.3139 | 272.1475 | 272.1756
1276.8948 | 324.7679 | 272.324 | 272.1657 | 272.1762
1277.8948 | 324.8198 | 272.3264 | 272.173 | 272.1748
1278.8948 | 324.839 | 272.3247 | 272.1831 | 272.1799
1279.8948 | 324.9057 | 272.317 | 272.1996 | 272.1815
1280.8948 | 324.8737 | 272.3252 | 272.2074 | 272.1862
1281.8948 | 324.9387 | 272.3063 | 272.218 | 272.1866
1282.8948 | 324.9007 | 272.3024 | 272.2252 | 272.1949
1283.8948 | 324.8855 | 272.3042 | 272.2409 | 272.1942
1284.8948 | 324.8115 | 272.2904 | 272.2503 | 272.1955
1285.8948 | 324.74 | 272.2781 | 272.2669 | 272.1918
1286.8948 | 324.7055 | 272.2726 | 272.2749 | 272.1819
1287.8948 | 324.7413 | 272.27 | 272.2783 | 272.1956
1288.8948 | 324.806 | 272.2457 | 272.2973 | 272.1897
1289.8948 | 324.7918 | 272.2308 | 272.3084 | 272.1887
1290.8948 | 324.7904 | 272.221 | 272.3227 | 272.1898
1291.8948 | 324.7539 | 272.2085 | 272.3283 | 272.1903
1292.8948 | 324.7134 | 272.1903 | 272.3459 | 272.1835
1293.9104 | 324.6684 | 272.1705 | 272.3536 | 272.1937
1294.8948 | 324.7109 | 272.1666 | 272.3687 | 272.1991
1295.8948 | 324.8166 | 272.1532 | 272.3748 | 272.1912
1296.8948 | 324.7587 | 272.1388 | 272.3901 | 272.1952
1297.8948 | 324.7874 | 272.1331 | 272.397 | 272.193
1298.8948 | 324.7745 | 272.1156 | 272.4035 | 272.1895
1299.8948 | 324.7379 | 272.0973 | 272.4118 | 272.2004
1300.8948 | 324.8627 | 272.0823 | 272.4269 | 272.1978
1301.8948 | 324.855 | 272.0808 | 272.4286 | 272.1936
1302.8948 | 324.7336 | 272.0691 | 272.4295 | 272.1943
1303.8948 | 324.568 | 272.0542 | 272.4408 | 272.1905
1304.8948 | 324.5348 | 272.048 | 272.4416 | 272.1885
1305.8948 | 324.5205 | 272.0483 | 272.4519 | 272.1872
1306.8948 | 324.5875 | 272.0373 | 272.4448 | 272.1834
1307.8948 | 324.5913 | 272.0312 | 272.4601 | 272.1875
1308.8948 | 324.5284 | 272.0121 | 272.4656 | 272.1798
1309.8948 | 324.5302 | 272.0154 | 272.459 | 272.1799
1310.8948 | 324.5088 | 272.0162 | 272.466 | 272.1798
1311.8948 | 324.4996 | 272.0049 | 272.4649 | 272.1708
1312.8948 | 324.5114 | 271.9928 | 272.4674 | 272.1697
1313.8948 | 324.5725 | 271.9953 | 272.4758 | 272.1679
1314.8948 | 324.6213 | 271.993 | 272.4772 | 272.1623
1315.8948 | 324.6737 | 271.9839 | 272.476 | 272.157
1316.8948 | 324.663 | 271.9872 | 272.4854 | 272.1573
1317.8948 | 324.607 | 271.9751 | 272.4791 | 272.1538
1318.8948 | 324.7564 | 271.9741 | 272.4892 | 272.1472
1319.8948 | 324.7618 | 271.9642 | 272.487 | 272.1433
1320.8948 | 324.7479 | 271.9638 | 272.488 | 272.1348
1321.8948 | 324.8647 | 271.9636 | 272.4896 | 272.136
1322.8948 | 324.793 | 271.9624 | 272.4935 | 272.1277
1323.9104 | 324.7296 | 271.9484 | 272.4928 | 272.1236
1324.8948 | 324.837 | 271.9607 | 272.4955 | 272.117
1325.8948 | 324.9035 | 271.959 | 272.5018 | 272.1067
1326.8948 | 324.9755 | 271.9604 | 272.4899 | 272.1032
1327.8948 | 324.9532 | 271.9614 | 272.4981 | 272.1015
1328.8948 | 324.9549 | 271.9567 | 272.4953 | 272.09
1329.8948 | 324.9804 | 271.9578 | 272.5047 | 272.0788
1330.8948 | 324.9923 | 271.9474 | 272.4973 | 272.0783
1331.8948 | 324.9721 | 271.9403 | 272.4988 | 272.0768
1332.8948 | 325.0014 | 271.938 | 272.5005 | 272.0615
1333.8948 | 325.0038 | 271.944 | 272.5034 | 272.0633
1334.8948 | 325.0559 | 271.9479 | 272.5032 | 272.0533
1335.8948 | 325.0568 | 271.9353 | 272.5034 | 272.0477
1336.8948 | 325.0665 | 271.9384 | 272.5058 | 272.0436
1337.8948 | 325.1619 | 271.935 | 272.5102 | 272.0411
1338.8948 | 325.2593 | 271.9401 | 272.503 | 272.0336
1339.8948 | 325.2802 | 271.9285 | 272.506 | 272.0274
1340.8948 | 325.3305 | 271.9449 | 272.5113 | 272.0192
1341.8948 | 325.3314 | 271.9356 | 272.5136 | 272.0171
1342.8948 | 325.3457 | 271.9377 | 272.5125 | 272.0094
1343.8948 | 325.3492 | 271.9382 | 272.5163 | 272.0111
1344.8948 | 325.3588 | 271.9277 | 272.5184 | 272.0099
1345.8948 | 325.3989 | 271.9278 | 272.5226 | 272.0014
1346.8948 | 325.3881 | 271.9262 | 272.5275 | 272.0049
1347.8948 | 325.4325 | 271.9288 | 272.531 | 271.9896
1348.8948 | 325.43 | 271.9344 | 272.5341 | 272.0003
1349.8948 | 325.3318 | 271.9473 | 272.5372 | 272.0011
1350.8948 | 325.2655 | 271.9452 | 272.5379 | 271.9946
1351.8948 | 325.2826 | 271.946 | 272.5429 | 272
1352.8948 | 325.3067 | 271.9442 | 272.545 | 271.9999
1353.9104 | 325.3238 | 271.9397 | 272.5579 | 271.9991
1354.8948 | 325.2086 | 271.938 | 272.5632 | 271.9999
1355.8948 | 325.1609 | 271.9555 | 272.5656 | 272.0014
1356.8948 | 325.1211 | 271.9581 | 272.5719 | 272.0017
1357.8948 | 325.1529 | 271.9549 | 272.5811 | 272.0043
1358.8948 | 325.1538 | 271.9714 | 272.5843 | 272.0098
1359.8948 | 325.2057 | 271.9702 | 272.5887 | 272.018
1360.8948 | 325.1284 | 271.9885 | 272.5995 | 272.023
1361.8948 | 325.1771 | 271.9834 | 272.6088 | 272.0267
1362.8948 | 325.1673 | 271.9862 | 272.6163 | 272.0405
1363.8948 | 325.2071 | 271.9993 | 272.6266 | 272.0434
1364.8948 | 325.1969 | 272.0097 | 272.6321 | 272.0521
1365.8948 | 325.1593 | 272.0145 | 272.6458 | 272.0598
1366.8948 | 325.0948 | 272.0214 | 272.6478 | 272.0715
1367.8948 | 325.087 | 272.0247 | 272.6606 | 272.0811
1368.8948 | 325.0232 | 272.0369 | 272.6767 | 272.0974
1369.8948 | 325.0179 | 272.0445 | 272.6757 | 272.096
1370.8948 | 324.913 | 272.0699 | 272.6946 | 272.1107
1371.8948 | 324.8534 | 272.0774 | 272.7096 | 272.1217
1372.8948 | 324.9107 | 272.0887 | 272.7157 | 272.1402
1373.8948 | 325.0126 | 272.0952 | 272.7329 | 272.1432
1374.8948 | 324.9729 | 272.1088 | 272.7445 | 272.1661
1375.8948 | 324.905 | 272.1208 | 272.7616 | 272.1802
1376.8948 | 324.927 | 272.1301 | 272.7755 | 272.1963
1377.8948 | 324.9617 | 272.136 | 272.7865 | 272.2142
1378.8948 | 324.9401 | 272.1548 | 272.8 | 272.2295
1379.8948 | 324.8947 | 272.1619 | 272.8149 | 272.2459
1380.8948 | 324.8573 | 272.1795 | 272.8275 | 272.2656
1381.8948 | 324.7972 | 272.1907 | 272.8431 | 272.2836
1382.8948 | 324.7004 | 272.1902 | 272.8569 | 272.2979
1383.9104 | 324.6937 | 272.2153 | 272.8756 | 272.3117
1384.8948 | 324.7761 | 272.2289 | 272.8936 | 272.3385
1385.8948 | 324.7677 | 272.236 | 272.9125 | 272.3587
1386.8948 | 324.934 | 272.2509 | 272.9225 | 272.3835
1387.8948 | 325.0255 | 272.2763 | 272.9354 | 272.3994
1388.8948 | 325.0885 | 272.2947 | 272.9526 | 272.4211
1389.8948 | 325.2067 | 272.3019 | 272.9751 | 272.4417
1390.8948 | 325.194 | 272.3139 | 272.9909 | 272.4577
1391.8948 | 325.2219 | 272.3341 | 273.0106 | 272.4823
1392.8948 | 325.2589 | 272.3562 | 273.0327 | 272.5061
1393.8948 | 325.3231 | 272.3739 | 273.0518 | 272.5319
1394.8948 | 325.3352 | 272.3928 | 273.0698 | 272.5499
1395.8948 | 325.3223 | 272.4143 | 273.0845 | 272.576
1396.8948 | 325.3489 | 272.4327 | 273.1108 | 272.6063
1397.8948 | 325.3084 | 272.4571 | 273.1285 | 272.6279
1398.8948 | 325.3026 | 272.4737 | 273.1456 | 272.658
1399.8948 | 325.348 | 272.4996 | 273.1653 | 272.6766
1400.8948 | 325.3749 | 272.5146 | 273.189 | 272.7
1401.8948 | 325.3744 | 272.5307 | 273.2097 | 272.7323
1402.8948 | 325.4264 | 272.5488 | 273.2294 | 272.7592
1403.8948 | 325.447 | 272.5764 | 273.2505 | 272.7876
1404.8948 | 325.5781 | 272.5988 | 273.2757 | 272.8142
1405.8948 | 325.5907 | 272.6285 | 273.2971 | 272.8443
1406.8948 | 325.6234 | 272.6325 | 273.3176 | 272.8714
1407.8948 | 325.6206 | 272.6719 | 273.3495 | 272.9
1408.8948 | 325.5568 | 272.6745 | 273.3646 | 272.93
1409.8948 | 325.5102 | 272.7162 | 273.3819 | 272.9634
1410.8948 | 325.6863 | 272.7485 | 273.4089 | 272.9904
1411.8948 | 325.7551 | 272.7601 | 273.4302 | 273.0158
1412.8948 | 325.7971 | 272.7764 | 273.4563 | 273.0457
1413.9104 | 325.7708 | 272.8084 | 273.469 | 273.0756
1414.8948 | 325.6604 | 272.8301 | 273.4907 | 273.1047
1415.8948 | 325.6107 | 272.8575 | 273.5244 | 273.1363
1416.8948 | 325.62 | 272.8852 | 273.5377 | 273.1698
1417.8948 | 325.6034 | 272.9263 | 273.5702 | 273.2016
1418.8948 | 325.6746 | 272.9477 | 273.5825 | 273.236
1419.8948 | 325.8048 | 272.9729 | 273.6179 | 273.2726
1420.8948 | 325.8337 | 272.9896 | 273.6404 | 273.2992
1421.8948 | 325.9582 | 273.0178 | 273.667 | 273.3343
1422.8948 | 325.9652 | 273.0523 | 273.6961 | 273.3648
1423.9104 | 326.0125 | 273.0735 | 273.7146 | 273.3943
1424.8948 | 325.9993 | 273.0918 | 273.7361 | 273.4172
1425.8948 | 325.9638 | 273.1173 | 273.7616 | 273.4509
1426.8948 | 325.9001 | 273.1472 | 273.7945 | 273.4871
1427.8948 | 325.8937 | 273.1724 | 273.8157 | 273.5152
1428.8948 | 325.8834 | 273.2126 | 273.8383 | 273.5548
1429.8948 | 325.8883 | 273.2343 | 273.861 | 273.5898
1430.8948 | 325.9131 | 273.2673 | 273.8884 | 273.623
1431.8948 | 325.878 | 273.2912 | 273.903 | 273.6506
1432.8948 | 325.8899 | 273.34 | 273.9371 | 273.6817
1433.8948 | 325.9707 | 273.3583 | 273.9605 | 273.7172
1434.8948 | 326.0318 | 273.3903 | 273.9879 | 273.7483
1435.8948 | 326.016 | 273.4142 | 274.0092 | 273.777
1436.8948 | 325.9997 | 273.449 | 274.025 | 273.8068
1437.8948 | 325.9931 | 273.4761 | 274.0551 | 273.8529
1438.8948 | 326.0208 | 273.4978 | 274.0749 | 273.879
1439.8948 | 326.0887 | 273.52 | 274.1006 | 273.9093
1440.8948 | 326.058 | 273.5475 | 274.1225 | 273.9389
1441.8948 | 326.0834 | 273.579 | 274.1431 | 273.9697
1442.8948 | 326.1075 | 273.6138 | 274.1666 | 274.0027
1443.9104 | 326.0844 | 273.6335 | 274.195 | 274.0346
1444.8948 | 326.1324 | 273.6638 | 274.2212 | 274.0629
1445.8948 | 326.0926 | 273.6989 | 274.2502 | 274.0956
1446.8948 | 326.0308 | 273.7229 | 274.2742 | 274.1231
1447.8948 | 326.0232 | 273.7524 | 274.2928 | 274.1538
1448.8948 | 326.0508 | 273.7903 | 274.3186 | 274.1815
1449.8948 | 326.0617 | 273.8097 | 274.342 | 274.2146
1450.8948 | 326.019 | 273.8337 | 274.3616 | 274.2363
1451.8948 | 326.0521 | 273.8549 | 274.3893 | 274.2661
1452.8948 | 326.0127 | 273.883 | 274.4123 | 274.3069
1453.8948 | 325.9559 | 273.9165 | 274.4355 | 274.3374
1454.8948 | 325.9024 | 273.9399 | 274.4631 | 274.3654
1455.8948 | 325.8657 | 273.9717 | 274.4907 | 274.3898
1456.8948 | 325.8025 | 274.0087 | 274.5189 | 274.4163
1457.8948 | 325.6933 | 274.0304 | 274.539 | 274.4527
1458.8948 | 325.5932 | 274.0503 | 274.554 | 274.4926
1459.8948 | 325.5223 | 274.0711 | 274.5771 | 274.515
1460.8948 | 325.4576 | 274.1096 | 274.5931 | 274.5409
1461.8948 | 325.3164 | 274.1217 | 274.622 | 274.5689
1462.8948 | 325.337 | 274.1566 | 274.6443 | 274.6051
1463.8948 | 325.4478 | 274.179 | 274.6713 | 274.6321
1464.8948 | 325.3329 | 274.2138 | 274.6917 | 274.6632
1465.8948 | 325.219 | 274.244 | 274.7147 | 274.6906
1466.8948 | 325.1826 | 274.2605 | 274.7373 | 274.7241
1467.8948 | 325.1092 | 274.2983 | 274.7553 | 274.7503
1468.8948 | 325.0383 | 274.3148 | 274.7783 | 274.7779
1469.8948 | 324.9417 | 274.3451 | 274.8056 | 274.8031
1470.8948 | 324.7721 | 274.3783 | 274.8256 | 274.8317
1471.8948 | 324.6856 | 274.3957 | 274.849 | 274.8616
1472.8948 | 324.7034 | 274.435 | 274.8681 | 274.8949
1473.9104 | 324.7343 | 274.4548 | 274.8949 | 274.9121
1474.8948 | 324.8345 | 274.4636 | 274.9186 | 274.9344
1475.8948 | 324.9281 | 274.5009 | 274.9422 | 274.9643
1476.8948 | 325.0187 | 274.5288 | 274.9723 | 274.9879
1477.8948 | 325.0701 | 274.54 | 274.9923 | 275.014
1478.8948 | 325.0976 | 274.5753 | 275.0089 | 275.0451
1479.8948 | 325.0618 | 274.6045 | 275.0315 | 275.0669
1480.8948 | 325.0413 | 274.6222 | 275.056 | 275.0932
1481.8948 | 324.9756 | 274.6468 | 275.0764 | 275.1204
1482.8948 | 324.8879 | 274.6747 | 275.0943 | 275.1496
1483.8948 | 324.8218 | 274.7012 | 275.1256 | 275.1717
1484.8948 | 324.7883 | 274.7354 | 275.1401 | 275.1978
1485.8948 | 324.7627 | 274.7442 | 275.1614 | 275.2182
1486.8948 | 324.8088 | 274.7807 | 275.1833 | 275.2552
1487.8948 | 324.9073 | 274.7974 | 275.2067 | 275.2744
1488.8948 | 324.9576 | 274.8229 | 275.224 | 275.2979
1489.8948 | 325.0224 | 274.8539 | 275.244 | 275.3235
1490.8948 | 325.0165 | 274.8681 | 275.264 | 275.3474
1491.8948 | 324.9858 | 274.891 | 275.2839 | 275.3743
1492.8948 | 324.9357 | 274.9131 | 275.3039 | 275.4007
1493.8948 | 324.8504 | 274.9432 | 275.3265 | 275.4202
1494.8948 | 324.912 | 274.9546 | 275.3468 | 275.4372
1495.8948 | 324.9418 | 274.9903 | 275.3609 | 275.4703
1496.8948 | 324.9667 | 275.0072 | 275.3778 | 275.4888
1497.8948 | 324.9779 | 275.035 | 275.3989 | 275.5076
1498.8948 | 325.0524 | 275.0538 | 275.4154 | 275.5404
1499.8948 | 325.1226 | 275.0847 | 275.4348 | 275.5633
1500.8948 | 325.1204 | 275.0957 | 275.4578 | 275.5776
1501.8948 | 325.0888 | 275.1261 | 275.4731 | 275.6031
1502.8948 | 325.0874 | 275.1435 | 275.4925 | 275.6249
1503.9104 | 325.1373 | 275.168 | 275.5164 | 275.6518
1504.8948 | 325.2125 | 275.1859 | 275.5382 | 275.6685
1505.8948 | 325.1857 | 275.209 | 275.5531 | 275.6906
1506.8948 | 325.2122 | 275.226 | 275.5653 | 275.7127
1507.8948 | 325.2249 | 275.2506 | 275.587 | 275.734
1508.8948 | 325.1462 | 275.2682 | 275.6072 | 275.7577
1509.8948 | 325.0736 | 275.2902 | 275.6198 | 275.7793
1510.8948 | 325.0413 | 275.3035 | 275.6384 | 275.7889
1511.8948 | 325.1025 | 275.3264 | 275.6578 | 275.8131
1512.8948 | 325.1534 | 275.3475 | 275.6729 | 275.8324
1513.8948 | 325.2779 | 275.3782 | 275.6854 | 275.8493
1514.8948 | 325.3176 | 275.3822 | 275.7066 | 275.8743
1515.8948 | 325.2708 | 275.4087 | 275.7227 | 275.8922
1516.8948 | 325.2863 | 275.4287 | 275.7406 | 275.9094
1517.8948 | 325.2771 | 275.4477 | 275.7568 | 275.9328
1518.8948 | 325.2798 | 275.4696 | 275.7708 | 275.9445
1519.8948 | 325.2422 | 275.4824 | 275.7915 | 275.9687
1520.8948 | 325.2261 | 275.514 | 275.8043 | 275.9898
1521.8948 | 325.2164 | 275.5204 | 275.8214 | 276.0062
1522.9104 | 325.2097 | 275.557 | 275.8357 | 276.0263
1523.8948 | 325.2384 | 275.5693 | 275.8534 | 276.0421
1524.8948 | 325.2696 | 275.5878 | 275.8679 | 276.0592
1525.8948 | 325.2242 | 275.6122 | 275.8802 | 276.0741
1526.8948 | 325.1761 | 275.6334 | 275.8968 | 276.0953
1527.8948 | 325.1072 | 275.6421 | 275.9146 | 276.1114
1528.8948 | 325.0018 | 275.6659 | 275.9323 | 276.1324
1529.8948 | 324.9402 | 275.6774 | 275.9491 | 276.1534
1530.8948 | 324.9338 | 275.695 | 275.9639 | 276.1673
1531.8948 | 324.9078 | 275.716 | 275.9773 | 276.1846
1532.8948 | 324.9466 | 275.7333 | 275.9939 | 276.1991
1533.9104 | 324.9725 | 275.7559 | 276.013 | 276.2176
1534.8948 | 325.0207 | 275.773 | 276.0271 | 276.2379
1535.9104 | 325.0027 | 275.7958 | 276.0445 | 276.2483
1536.8948 | 324.9589 | 275.8158 | 276.0597 | 276.2753
1537.8948 | 325.0283 | 275.8375 | 276.0725 | 276.2907
1538.8948 | 324.9801 | 275.8418 | 276.0866 | 276.305
1539.8948 | 324.9233 | 275.8655 | 276.1025 | 276.3269
1540.8948 | 324.8931 | 275.8952 | 276.1205 | 276.3406
1541.8948 | 324.9013 | 275.8935 | 276.1336 | 276.36
1542.8948 | 325.0417 | 275.9165 | 276.1525 | 276.371
1543.8948 | 325.1001 | 275.9412 | 276.1667 | 276.3914
1544.8948 | 325.0775 | 275.9576 | 276.1834 | 276.3999
1545.8948 | 325.0358 | 275.9727 | 276.1908 | 276.4185
1546.9104 | 325.016 | 275.989 | 276.2104 | 276.43
1547.8948 | 325.0946 | 275.9975 | 276.2208 | 276.4464
1548.8948 | 325.1441 | 276.0221 | 276.2351 | 276.4633
1549.8948 | 325.1342 | 276.0339 | 276.2569 | 276.48
1550.8948 | 325.1556 | 276.0469 | 276.268 | 276.4983
1551.9104 | 325.1818 | 276.0658 | 276.2842 | 276.5107
1552.8948 | 325.1271 | 276.0914 | 276.2937 | 276.5284
1553.8948 | 325.1141 | 276.102 | 276.3048 | 276.5455
1554.8948 | 325.1069 | 276.1151 | 276.3281 | 276.5614
1555.8948 | 325.0828 | 276.1327 | 276.3358 | 276.5809
1556.8948 | 325.0835 | 276.1559 | 276.3492 | 276.5952
1557.8948 | 325.0461 | 276.1625 | 276.363 | 276.5996
1558.8948 | 325.0136 | 276.1741 | 276.379 | 276.6216
1559.8948 | 324.9741 | 276.1923 | 276.3953 | 276.629
1560.8948 | 325.0115 | 276.2171 | 276.4078 | 276.643
1561.8948 | 325.0744 | 276.2305 | 276.4201 | 276.6576
1562.8948 | 325.0442 | 276.2384 | 276.4403 | 276.6731
1563.9104 | 324.968 | 276.2521 | 276.4463 | 276.6858
1564.8948 | 325.0064 | 276.2811 | 276.4614 | 276.6963
1565.8948 | 324.9868 | 276.2827 | 276.4677 | 276.7123
1566.8948 | 324.9277 | 276.3028 | 276.4845 | 276.7252
1567.8948 | 324.8376 | 276.3181 | 276.4958 | 276.7363
1568.8948 | 324.7768 | 276.3327 | 276.5144 | 276.7511
1569.8948 | 324.9057 | 276.3458 | 276.5249 | 276.7707
1570.8948 | 324.9332 | 276.3625 | 276.5473 | 276.7784
1571.8948 | 324.9408 | 276.383 | 276.5601 | 276.7948
1572.8948 | 324.968 | 276.3767 | 276.5675 | 276.8023
1573.8948 | 324.9611 | 276.4187 | 276.5777 | 276.8135
1574.8948 | 325.0936 | 276.4065 | 276.5906 | 276.8282
1575.8948 | 325.1019 | 276.4368 | 276.6046 | 276.8414
1576.8948 | 325.159 | 276.4508 | 276.6181 | 276.8511
1577.8948 | 325.2253 | 276.4542 | 276.6259 | 276.8654
1578.8948 | 325.3147 | 276.4757 | 276.6419 | 276.8784
1579.8948 | 325.4007 | 276.4962 | 276.6608 | 276.8917
1580.8948 | 325.4324 | 276.5057 | 276.6643 | 276.8989
1581.8948 | 325.4528 | 276.5157 | 276.6803 | 276.9147
1582.9104 | 325.5331 | 276.5295 | 276.6887 | 276.9227
1583.8948 | 325.6077 | 276.5405 | 276.703 | 276.9383
1584.8948 | 325.7122 | 276.5543 | 276.7078 | 276.941
1585.8948 | 325.788 | 276.5683 | 276.7236 | 276.9614
1586.8948 | 325.7591 | 276.574 | 276.7307 | 276.9684
1587.8948 | 325.7664 | 276.5969 | 276.7471 | 276.9792
1588.8948 | 325.7718 | 276.6091 | 276.7544 | 276.9867
1589.8948 | 325.7559 | 276.6279 | 276.7737 | 276.9981
1590.8948 | 325.8376 | 276.6347 | 276.78 | 277.0118
1591.8948 | 325.7868 | 276.6525 | 276.7978 | 277.0257
1592.8948 | 325.769 | 276.6523 | 276.8125 | 277.0348
1593.9104 | 325.8105 | 276.6746 | 276.8128 | 277.0469
1594.8948 | 325.7815 | 276.6862 | 276.834 | 277.0585
1595.8948 | 325.7228 | 276.7007 | 276.8488 | 277.0753
1596.8948 | 325.7972 | 276.7118 | 276.858 | 277.082
1597.8948 | 325.8158 | 276.726 | 276.8681 | 277.1018
1598.8948 | 325.6116 | 276.7396 | 276.8828 | 277.1107
1599.8948 | 325.5781 | 276.7481 | 276.8936 | 277.1236
1600.8948 | 325.5366 | 276.7717 | 276.9082 | 277.1344
1601.8948 | 325.526 | 276.7723 | 276.9296 | 277.1497
1602.8948 | 325.5425 | 276.7919 | 276.943 | 277.1577
1603.8948 | 325.5214 | 276.7996 | 276.9464 | 277.1763
1604.8948 | 325.4003 | 276.8233 | 276.9616 | 277.1835
1605.8948 | 325.3209 | 276.8325 | 276.9744 | 277.2011
1606.8948 | 325.2244 | 276.8466 | 276.988 | 277.2113
1607.8948 | 325.1885 | 276.862 | 276.9992 | 277.2236
1608.8948 | 325.0929 | 276.8768 | 277.0142 | 277.2389
1609.8948 | 325.0751 | 276.9037 | 277.0249 | 277.2535
1610.8948 | 324.9752 | 276.9097 | 277.0444 | 277.2697
1611.8948 | 325.0127 | 276.9187 | 277.0559 | 277.2747
1612.8948 | 325.038 | 276.9335 | 277.0714 | 277.2879
1613.8948 | 324.9241 | 276.9511 | 277.0913 | 277.3006
1614.8948 | 324.9357 | 276.9598 | 277.0987 | 277.3191
1615.8948 | 324.9378 | 276.9646 | 277.1102 | 277.3304
1616.8948 | 324.9746 | 276.991 | 277.1264 | 277.3434
1617.8948 | 325.0209 | 277.0017 | 277.1449 | 277.357
1618.8948 | 325.0864 | 277.0175 | 277.1594 | 277.3678
1619.8948 | 325.0864 | 277.0248 | 277.1794 | 277.381
1620.8948 | 325.1068 | 277.0492 | 277.1861 | 277.3899
1621.8948 | 325.1781 | 277.0698 | 277.2003 | 277.4092
1622.8948 | 325.1615 | 277.0742 | 277.21 | 277.4224
1623.8948 | 325.1909 | 277.0846 | 277.2248 | 277.4355
1624.8948 | 325.2461 | 277.1077 | 277.2433 | 277.4503
1625.8948 | 325.24 | 277.1201 | 277.2557 | 277.465
1626.8948 | 325.1958 | 277.1352 | 277.2731 | 277.4776
1627.8948 | 325.228 | 277.1499 | 277.2859 | 277.4946
1628.8948 | 325.2476 | 277.1721 | 277.3045 | 277.5087
1629.8948 | 325.2206 | 277.1762 | 277.3174 | 277.5279
1630.8948 | 325.16 | 277.1917 | 277.3261 | 277.5317
1631.8948 | 325.1694 | 277.2101 | 277.3459 | 277.5506
1632.8948 | 325.1742 | 277.2279 | 277.358 | 277.5671
1633.8948 | 325.1175 | 277.2255 | 277.3711 | 277.5753
1634.8948 | 325.1645 | 277.2591 | 277.3862 | 277.5871
1635.8948 | 325.1479 | 277.2687 | 277.4017 | 277.5976
1636.8948 | 325.1095 | 277.2769 | 277.415 | 277.6204
1637.8948 | 325.0349 | 277.2815 | 277.4342 | 277.6231
1638.8948 | 325.0152 | 277.3151 | 277.44 | 277.6403
1639.8948 | 325.0329 | 277.3332 | 277.4576 | 277.6586
1640.8948 | 325.1002 | 277.3352 | 277.4752 | 277.6718
1641.8948 | 325.1557 | 277.3524 | 277.4883 | 277.6834
1642.8948 | 325.1161 | 277.3555 | 277.5039 | 277.6916
1643.8948 | 325.1706 | 277.3751 | 277.5192 | 277.7077
1644.8948 | 325.1627 | 277.3912 | 277.5319 | 277.7231
1645.8948 | 325.1235 | 277.4054 | 277.5389 | 277.7355
1646.8948 | 325.1377 | 277.4271 | 277.562 | 277.7511
1647.8948 | 325.1744 | 277.4304 | 277.5762 | 277.7655
1648.8948 | 325.2344 | 277.4492 | 277.5853 | 277.7835
1649.8948 | 325.3066 | 277.4655 | 277.6007 | 277.7924
1650.8948 | 325.3486 | 277.4855 | 277.6181 | 277.8102
1651.8948 | 325.3232 | 277.4937 | 277.6284 | 277.8231
1652.8948 | 325.4078 | 277.5007 | 277.6412 | 277.8387
1653.8948 | 325.4657 | 277.5301 | 277.6631 | 277.8499
1654.8948 | 325.4547 | 277.5442 | 277.6708 | 277.862
1655.8948 | 325.5071 | 277.5466 | 277.6884 | 277.8745
1656.8948 | 325.594 | 277.5662 | 277.6997 | 277.8851
1657.8948 | 325.6504 | 277.5744 | 277.7174 | 277.9036
1658.8948 | 325.6542 | 277.5838 | 277.731 | 277.9165
1659.8948 | 325.6136 | 277.6064 | 277.7468 | 277.9313
1660.8948 | 325.558 | 277.6223 | 277.7604 | 277.9424
1661.8948 | 325.5017 | 277.6279 | 277.7702 | 277.9552
1662.8948 | 325.5546 | 277.6535 | 277.7836 | 277.9697
1663.8948 | 325.623 | 277.6642 | 277.8031 | 277.9806
1664.8948 | 325.6836 | 277.677 | 277.807 | 278.0013
1665.8948 | 325.7327 | 277.699 | 277.8254 | 278.0112
1666.8948 | 325.7448 | 277.6959 | 277.841 | 278.0269
1667.8948 | 325.7274 | 277.722 | 277.856 | 278.0326
1668.8948 | 325.7576 | 277.7405 | 277.8717 | 278.0499
1669.8948 | 325.7644 | 277.7503 | 277.8862 | 278.0623
1670.8948 | 325.7592 | 277.7693 | 277.8986 | 278.0743
1671.8948 | 325.793 | 277.7759 | 277.9141 | 278.0935
1672.8948 | 325.7329 | 277.7914 | 277.9307 | 278.1038
1673.8948 | 325.7737 | 277.8086 | 277.9409 | 278.112
1674.8948 | 325.729 | 277.8318 | 277.951 | 278.1315
1675.8948 | 325.7121 | 277.8191 | 277.97 | 278.1457
1676.8948 | 325.7545 | 277.8382 | 277.9833 | 278.1572
1677.8948 | 325.78 | 277.8593 | 277.9989 | 278.1727
1678.8948 | 325.8172 | 277.8715 | 278.0083 | 278.1882
1679.8948 | 325.7744 | 277.8938 | 278.0285 | 278.203
1680.8948 | 325.8284 | 277.9012 | 278.0389 | 278.2187
1681.8948 | 325.8897 | 277.9206 | 278.0555 | 278.2298
1682.8948 | 325.9342 | 277.9422 | 278.0671 | 278.2423
1683.8948 | 325.953 | 277.9511 | 278.081 | 278.2499
1684.8948 | 325.9437 | 277.9715 | 278.0985 | 278.2693
1685.8948 | 325.907 | 277.9819 | 278.1099 | 278.2839
1686.8948 | 325.8756 | 278.0092 | 278.1195 | 278.2924
1687.8948 | 325.9048 | 278.0114 | 278.1452 | 278.3116
1688.8948 | 325.9268 | 278.0304 | 278.1596 | 278.3283
1689.8948 | 325.9439 | 278.0401 | 278.1748 | 278.3421
1690.8948 | 325.9047 | 278.06 | 278.1931 | 278.3585
1691.8948 | 325.8085 | 278.0743 | 278.2116 | 278.3768
1692.8948 | 325.752 | 278.0684 | 278.226 | 278.3917
1693.8948 | 325.7535 | 278.0896 | 278.2375 | 278.4069
1694.8948 | 325.7524 | 278.1163 | 278.2577 | 278.4213
1695.8948 | 325.7434 | 278.1273 | 278.2678 | 278.4406
1696.8948 | 325.7463 | 278.1495 | 278.2854 | 278.4559
1697.8948 | 325.7238 | 278.1583 | 278.3073 | 278.4654
1698.8948 | 325.8181 | 278.1768 | 278.3185 | 278.4863
1699.8948 | 325.8877 | 278.1911 | 278.3369 | 278.4959
1700.8948 | 325.8278 | 278.2096 | 278.3434 | 278.5151
1701.8948 | 325.7986 | 278.2097 | 278.3692 | 278.5279
1702.8948 | 325.7382 | 278.2412 | 278.3759 | 278.5492
1703.8948 | 325.7717 | 278.2476 | 278.4017 | 278.5544
1704.8948 | 325.8188 | 278.2598 | 278.4186 | 278.5755
1705.8948 | 325.8608 | 278.2787 | 278.4262 | 278.587
1706.8948 | 325.8937 | 278.2871 | 278.4431 | 278.5996
1707.8948 | 325.8621 | 278.3069 | 278.4555 | 278.6214
1708.8948 | 325.8551 | 278.3255 | 278.4732 | 278.6398
1709.8948 | 325.7844 | 278.3194 | 278.4958 | 278.6554
1710.8948 | 325.7685 | 278.3463 | 278.5058 | 278.6674
1711.8948 | 325.8262 | 278.3653 | 278.5213 | 278.6838
1712.8948 | 325.8098 | 278.3735 | 278.5384 | 278.7073
1713.9104 | 325.9116 | 278.3962 | 278.5532 | 278.7073
1714.8948 | 325.9523 | 278.4144 | 278.5704 | 278.7273
1715.8948 | 325.9619 | 278.4206 | 278.5891 | 278.7441
1716.8948 | 326.0381 | 278.4406 | 278.6009 | 278.7652
1717.8948 | 326.1852 | 278.4468 | 278.6158 | 278.778
1718.8948 | 326.1705 | 278.4768 | 278.6354 | 278.7902
1719.8948 | 326.1177 | 278.4836 | 278.6516 | 278.803
1720.8948 | 326.1229 | 278.4927 | 278.6682 | 278.8218
1721.8948 | 326.1326 | 278.5167 | 278.6862 | 278.841
1722.8948 | 326.1752 | 278.5321 | 278.7034 | 278.8612
1723.8948 | 326.2248 | 278.5559 | 278.7233 | 278.8711
1724.8948 | 326.2127 | 278.5534 | 278.7384 | 278.8888
1725.8948 | 326.1915 | 278.5839 | 278.7523 | 278.905
1726.8948 | 326.2099 | 278.6033 | 278.7665 | 278.9186
1727.8948 | 326.2003 | 278.6167 | 278.7867 | 278.9343
1728.8948 | 326.107 | 278.628 | 278.8014 | 278.9511
1729.8948 | 326.0738 | 278.6484 | 278.817 | 278.9734
1730.8948 | 326.0142 | 278.6633 | 278.8328 | 278.986
1731.8948 | 326.0089 | 278.6807 | 278.8522 | 279.0012
1732.8948 | 326.0049 | 278.6968 | 278.8665 | 279.0178
1733.8948 | 325.9841 | 278.7167 | 278.8823 | 279.0322
1734.8948 | 325.95 | 278.7294 | 278.9019 | 279.0492
1735.8948 | 325.9607 | 278.7397 | 278.9133 | 279.0656
1736.8948 | 325.958 | 278.7637 | 278.9314 | 279.079
1737.8948 | 325.9026 | 278.7721 | 278.951 | 279.101
1738.8948 | 325.8766 | 278.7919 | 278.9649 | 279.115
1739.8948 | 325.8405 | 278.815 | 278.9821 | 279.1302
1740.8948 | 325.7982 | 278.8237 | 278.9939 | 279.1489
1741.8948 | 325.8244 | 278.8429 | 279.0168 | 279.1637
1742.8948 | 325.8213 | 278.851 | 279.0286 | 279.1762
1743.8948 | 325.8163 | 278.8784 | 279.0447 | 279.1934
1744.8948 | 325.7522 | 278.8898 | 279.063 | 279.2079
1745.8948 | 325.637 | 278.8992 | 279.0806 | 279.2231
1746.8948 | 325.5606 | 278.9207 | 279.0943 | 279.2477
1747.8948 | 325.5061 | 278.944 | 279.1103 | 279.2555
1748.8948 | 325.4215 | 278.9646 | 279.1274 | 279.2763
1749.8948 | 325.35 | 278.9756 | 279.1474 | 279.2957
1750.8948 | 325.3924 | 278.9871 | 279.1561 | 279.313
1751.8948 | 325.4383 | 279.01 | 279.1757 | 279.3277
1752.8948 | 325.4881 | 279.025 | 279.1969 | 279.3495
1753.8948 | 325.551 | 279.0446 | 279.2076 | 279.3591
1754.8948 | 325.6366 | 279.0752 | 279.2239 | 279.3777
1755.8948 | 325.7021 | 279.0768 | 279.2419 | 279.3922
1756.8948 | 325.6088 | 279.0989 | 279.2554 | 279.4092
1757.8948 | 325.4553 | 279.1181 | 279.2681 | 279.4296
1758.9104 | 325.4515 | 279.1356 | 279.2916 | 279.4443
1759.8948 | 325.5038 | 279.1514 | 279.3037 | 279.4662
1760.8948 | 325.589 | 279.1676 | 279.3222 | 279.4789
1761.8948 | 325.6383 | 279.185 | 279.3362 | 279.4875
1762.8948 | 325.6206 | 279.2018 | 279.3551 | 279.5085
1763.8948 | 325.6416 | 279.2103 | 279.3719 | 279.5246
1764.8948 | 326.1982 | 279.2429 | 279.3911 | 279.547
1765.8948 | 327.6658 | 279.2494 | 279.4059 | 279.5595
1766.8948 | 329.8683 | 279.2749 | 279.4296 | 279.5818
1767.8948 | 332.6981 | 279.2868 | 279.4464 | 279.6027
1768.8948 | 335.8832 | 279.3022 | 279.4634 | 279.6086
1769.8948 | 339.267 | 279.3244 | 279.4782 | 279.6309
1770.8948 | 342.816 | 279.3385 | 279.5006 | 279.6472
1771.8948 | 346.2984 | 279.3536 | 279.509 | 279.667
1772.8948 | 349.3183 | 279.385 | 279.5344 | 279.681
1773.8948 | 352.0324 | 279.3976 | 279.5491 | 279.6971
1774.8948 | 354.4776 | 279.4196 | 279.5662 | 279.713
1775.8948 | 356.4347 | 279.4459 | 279.5902 | 279.7296
1776.8948 | 358.1088 | 279.4558 | 279.6033 | 279.7509
1777.8948 | 359.4785 | 279.4825 | 279.6203 | 279.7699
1778.8948 | 360.5478 | 279.4954 | 279.6415 | 279.7877
1779.8948 | 361.383 | 279.5133 | 279.6643 | 279.8065
1780.8948 | 361.9889 | 279.5409 | 279.6701 | 279.8255
1781.8948 | 362.4766 | 279.5622 | 279.6953 | 279.8468
1782.8948 | 362.7765 | 279.5845 | 279.7116 | 279.8645
1783.8948 | 363.0769 | 279.5984 | 279.726 | 279.8965
1784.8948 | 363.2464 | 279.6279 | 279.7444 | 279.9174
1785.8948 | 363.1373 | 279.6515 | 279.7717 | 279.9461
1786.8948 | 362.9528 | 279.6868 | 279.7898 | 279.9641
1787.8948 | 362.8843 | 279.7123 | 279.8179 | 280.0021
1788.8948 | 362.7978 | 279.7357 | 279.8354 | 280.0275
1789.8948 | 362.5928 | 279.7669 | 279.8597 | 280.0569
1790.8948 | 362.1902 | 279.8056 | 279.885 | 280.0891
1791.8948 | 361.8121 | 279.8398 | 279.9169 | 280.114
1792.8948 | 361.4564 | 279.8836 | 279.9486 | 280.1476
1793.8948 | 361.0075 | 279.9101 | 279.9819 | 280.1772
1794.8948 | 360.6182 | 279.9526 | 280.0088 | 280.2231
1795.8948 | 360.1998 | 279.9911 | 280.0485 | 280.2593
1796.8948 | 359.7816 | 280.0328 | 280.0825 | 280.2994
1797.8948 | 359.2466 | 280.0857 | 280.1149 | 280.3435
1798.8948 | 358.8121 | 280.1321 | 280.1559 | 280.3827
1799.8948 | 358.3704 | 280.1676 | 280.1959 | 280.4275
1800.8948 | 357.878 | 280.2275 | 280.2363 | 280.4756
1801.8948 | 357.2835 | 280.2845 | 280.2791 | 280.5284
1802.8948 | 356.785 | 280.3316 | 280.3308 | 280.5741
1803.8948 | 356.2634 | 280.3815 | 280.3824 | 280.6319
1804.8948 | 355.7883 | 280.4385 | 280.4246 | 280.6863
1805.8948 | 355.2648 | 280.508 | 280.4847 | 280.7445
1806.8948 | 354.7299 | 280.5684 | 280.5388 | 280.7977
1807.8948 | 354.1943 | 280.6365 | 280.5964 | 280.86
1808.8948 | 353.586 | 280.6933 | 280.653 | 280.9233
1809.8948 | 352.9968 | 280.7757 | 280.7123 | 280.9907
1810.8948 | 352.5157 | 280.8311 | 280.7774 | 281.0612
1811.8948 | 352.019 | 280.9106 | 280.8358 | 281.126
1812.8948 | 351.581 | 280.975 | 280.8995 | 281.1899
1813.8948 | 351.1458 | 281.0446 | 280.9724 | 281.2616
1814.8948 | 350.7776 | 281.1242 | 281.0375 | 281.3371
1815.8948 | 350.414 | 281.1987 | 281.1094 | 281.4063
1816.8948 | 349.9642 | 281.2807 | 281.1801 | 281.4823
1817.8948 | 349.5198 | 281.358 | 281.2546 | 281.5621
1818.9104 | 349.1439 | 281.4328 | 281.3275 | 281.6487
1819.8948 | 348.7724 | 281.5269 | 281.3929 | 281.7171
1820.8948 | 348.3546 | 281.6074 | 281.4727 | 281.8059
1821.8948 | 347.9438 | 281.6845 | 281.5535 | 281.8837
1822.9417 | 347.7387 | 281.7718 | 281.639 | 281.9622
1823.8948 | 347.5262 | 281.8555 | 281.7146 | 282.0508
1824.8948 | 347.3267 | 281.9401 | 281.7946 | 282.1301
1825.8948 | 347.1252 | 282.0268 | 281.8742 | 282.2177
1826.8948 | 347.0251 | 282.1218 | 281.9618 | 282.3047
1827.8948 | 346.8802 | 282.2023 | 282.0458 | 282.3868
1828.8948 | 346.7884 | 282.2967 | 282.1346 | 282.4733
1829.9104 | 346.8078 | 282.3939 | 282.2161 | 282.5668
1830.8948 | 346.8855 | 282.4705 | 282.3054 | 282.6534
1831.8948 | 346.8732 | 282.5701 | 282.3963 | 282.74
1832.8948 | 346.9214 | 282.6586 | 282.4804 | 282.826
1833.8948 | 347.0748 | 282.7438 | 282.5666 | 282.9235
1834.8948 | 347.1524 | 282.831 | 282.6567 | 283.0079
1835.8948 | 347.2964 | 282.93 | 282.7511 | 283.0953
1836.8948 | 347.462 | 283.0168 | 282.8368 | 283.1926
1837.8948 | 347.6254 | 283.1071 | 282.9271 | 283.2836
1838.926 | 347.9015 | 283.1981 | 283.0234 | 283.3678
1839.8948 | 348.0781 | 283.2976 | 283.1049 | 283.4581
1840.8948 | 348.3043 | 283.3787 | 283.1941 | 283.5517
1841.8948 | 348.5597 | 283.4733 | 283.2787 | 283.6442
1842.8948 | 348.7432 | 283.5721 | 283.3688 | 283.7271
1843.8948 | 348.9955 | 283.6633 | 283.4639 | 283.836
1844.8948 | 349.2207 | 283.7586 | 283.5525 | 283.9195
1845.8948 | 349.4709 | 283.837 | 283.6423 | 284.0097
1846.8948 | 349.6909 | 283.9296 | 283.735 | 284.1024
1847.8948 | 349.9299 | 284.0274 | 283.8253 | 284.1895
1848.8948 | 350.1077 | 284.122 | 283.9239 | 284.2877
1849.8948 | 350.3645 | 284.2125 | 284.018 | 284.3799
1850.8948 | 350.6648 | 284.302 | 284.1081 | 284.4685
1851.8948 | 350.8006 | 284.4045 | 284.1939 | 284.5632
1852.8948 | 350.8715 | 284.4873 | 284.2925 | 284.6497
1853.8948 | 351.0322 | 284.5804 | 284.3763 | 284.7534
1854.8948 | 351.2493 | 284.6632 | 284.4663 | 284.8422
1855.9104 | 351.3894 | 284.7695 | 284.5678 | 284.9319
1856.8948 | 351.4859 | 284.8576 | 284.6504 | 285.0261
1857.8948 | 351.5945 | 284.9433 | 284.7481 | 285.1157
1858.8948 | 351.6036 | 285.0409 | 284.8381 | 285.2103
1859.8948 | 351.5971 | 285.1341 | 284.928 | 285.2954
1860.8948 | 351.6645 | 285.2183 | 285.0167 | 285.3914
1861.8948 | 351.7558 | 285.3095 | 285.1088 | 285.4877
1862.8948 | 351.7666 | 285.4013 | 285.1997 | 285.5751
1863.8948 | 351.7291 | 285.4998 | 285.2862 | 285.6644
1864.8948 | 351.7347 | 285.5847 | 285.3766 | 285.755
1865.8948 | 351.6893 | 285.6817 | 285.4679 | 285.8541
1866.8948 | 351.6161 | 285.7741 | 285.5579 | 285.9442
1867.8948 | 351.5508 | 285.8586 | 285.6471 | 286.034
1868.8948 | 351.5051 | 285.9568 | 285.7451 | 286.1207
1869.8948 | 351.4169 | 286.0437 | 285.8349 | 286.2164
1870.8948 | 351.4989 | 286.1395 | 285.9221 | 286.3073
1871.8948 | 351.525 | 286.229 | 286.0178 | 286.4035
1872.8948 | 351.514 | 286.3225 | 286.1114 | 286.4915
1873.8948 | 351.5743 | 286.4078 | 286.1964 | 286.58
1874.8948 | 351.6018 | 286.5057 | 286.2853 | 286.6719
1875.8948 | 351.5615 | 286.5868 | 286.3833 | 286.7595
1876.8948 | 351.5815 | 286.6836 | 286.4737 | 286.851
1877.8948 | 351.5911 | 286.7651 | 286.5611 | 286.9422
1878.9104 | 351.635 | 286.8606 | 286.6502 | 287.0321
1879.8948 | 351.6547 | 286.9511 | 286.7393 | 287.121
1880.8948 | 351.6015 | 287.0455 | 286.8239 | 287.2146
1881.8948 | 351.688 | 287.1296 | 286.9206 | 287.2949
1882.8948 | 351.6952 | 287.2162 | 287.0135 | 287.388
1883.8948 | 351.654 | 287.3041 | 287.0989 | 287.4833
1884.8948 | 351.5848 | 287.3931 | 287.1851 | 287.5716
1885.8948 | 351.5717 | 287.4761 | 287.273 | 287.66
1886.8948 | 351.521 | 287.5615 | 287.3577 | 287.7467
1887.8948 | 351.4838 | 287.6573 | 287.4496 | 287.839
1888.8948 | 351.5252 | 287.7531 | 287.5285 | 287.9138
1889.8948 | 351.601 | 287.8475 | 287.6255 | 288.0096
1890.8948 | 351.5757 | 287.9292 | 287.7132 | 288.0946
1891.8948 | 351.5044 | 288.0122 | 287.8018 | 288.1762
1892.8948 | 351.4988 | 288.0992 | 287.8904 | 288.268
1893.8948 | 351.5096 | 288.1786 | 287.9797 | 288.3594
1894.8948 | 351.5466 | 288.2605 | 288.0615 | 288.4391
1895.8948 | 351.5433 | 288.3525 | 288.1482 | 288.5313
1896.8948 | 351.6172 | 288.4417 | 288.2381 | 288.6138
1897.8948 | 351.6035 | 288.5216 | 288.3237 | 288.702
1898.8948 | 351.6817 | 288.6095 | 288.4061 | 288.7858
1899.8948 | 351.7634 | 288.6973 | 288.4965 | 288.8713
1900.8948 | 351.6873 | 288.7743 | 288.5804 | 288.9635
1901.8948 | 351.6329 | 288.8632 | 288.6624 | 289.0429
1902.8948 | 351.5349 | 288.9497 | 288.7514 | 289.1207
1903.8948 | 351.5429 | 289.0405 | 288.8361 | 289.2104
1904.8948 | 351.5864 | 289.1238 | 288.9149 | 289.289
1905.8948 | 351.6391 | 289.1959 | 289.0131 | 289.38
1906.8948 | 351.7272 | 289.2793 | 289.097 | 289.4715
1907.8948 | 351.668 | 289.3746 | 289.1768 | 289.559
1908.8948 | 351.595 | 289.4432 | 289.2605 | 289.642
1909.8948 | 351.5759 | 289.5405 | 289.3458 | 289.716
1910.8948 | 351.5292 | 289.6223 | 289.4299 | 289.8001
1911.8948 | 351.5683 | 289.6856 | 289.5115 | 289.8853
1912.8948 | 351.5929 | 289.7769 | 289.5921 | 289.9627
1913.8948 | 351.5941 | 289.8537 | 289.6722 | 290.045
1914.8948 | 351.5557 | 289.9427 | 289.7516 | 290.1152
1915.8948 | 351.3924 | 290.0156 | 289.834 | 290.201
1916.8948 | 351.2453 | 290.0895 | 289.9209 | 290.285
1917.8948 | 351.1223 | 290.1756 | 289.9988 | 290.3677
1918.8948 | 351.0676 | 290.2561 | 290.0798 | 290.4443
1919.8948 | 351.0198 | 290.3291 | 290.1613 | 290.5295
1920.8948 | 350.9391 | 290.4123 | 290.2369 | 290.5988
1921.8948 | 350.925 | 290.4916 | 290.315 | 290.6858
1922.8948 | 350.8668 | 290.5736 | 290.3932 | 290.7694
1923.8948 | 350.9349 | 290.651 | 290.4668 | 290.8433
1924.8948 | 350.9207 | 290.72 | 290.552 | 290.9227
1925.8948 | 350.9266 | 290.7917 | 290.6236 | 290.9945
1926.8948 | 350.8218 | 290.8517 | 290.7101 | 291.0741
1927.8948 | 350.8169 | 290.9518 | 290.7818 | 291.1495
1928.8948 | 350.7757 | 291.0276 | 290.8624 | 291.2248
1929.8948 | 350.6903 | 291.0964 | 290.9345 | 291.3017
1930.8948 | 350.6582 | 291.1814 | 291.0124 | 291.377
1931.8948 | 350.5596 | 291.249 | 291.091 | 291.4469
1932.8948 | 350.5405 | 291.3266 | 291.1648 | 291.5315
1933.8948 | 350.5076 | 291.4003 | 291.2458 | 291.6047
1934.8948 | 350.4441 | 291.4663 | 291.3213 | 291.6809
1935.8948 | 350.4034 | 291.5511 | 291.3955 | 291.7576
1936.8948 | 350.3349 | 291.6185 | 291.4619 | 291.8282
1937.8948 | 350.2524 | 291.6881 | 291.5353 | 291.8987
1938.8948 | 350.1564 | 291.7563 | 291.6104 | 291.9835
1939.8948 | 350.0716 | 291.8337 | 291.6896 | 292.0441
1940.8948 | 350.0027 | 291.9103 | 291.7674 | 292.1239
1941.8948 | 349.8649 | 291.9765 | 291.8385 | 292.1925
1942.8948 | 349.7673 | 292.0437 | 291.9073 | 292.2654
1943.8948 | 349.7802 | 292.1268 | 291.9837 | 292.3344
1944.8948 | 349.7671 | 292.1818 | 292.0552 | 292.4112
1945.8948 | 349.8498 | 292.2698 | 292.1247 | 292.4791
1946.8948 | 349.9671 | 292.3325 | 292.1984 | 292.5491
1947.8948 | 350.0012 | 292.3964 | 292.2658 | 292.6159
1948.8948 | 350.0018 | 292.4684 | 292.3394 | 292.6825
1949.8948 | 350.0577 | 292.5412 | 292.41 | 292.762
1950.8948 | 350.0062 | 292.6137 | 292.4765 | 292.8253
1951.8948 | 349.9799 | 292.6725 | 292.5447 | 292.9005
1952.8948 | 349.8822 | 292.7356 | 292.6092 | 292.9539
1953.8948 | 349.8742 | 292.809 | 292.679 | 293.0322
1954.8948 | 349.9155 | 292.8734 | 292.7475 | 293.0904
1955.8948 | 349.9656 | 292.9343 | 292.8211 | 293.1694
1956.8948 | 349.9946 | 293.0017 | 292.8842 | 293.2297
1957.8948 | 350.0112 | 293.0802 | 292.9483 | 293.2913
1958.8948 | 349.9891 | 293.1303 | 293.024 | 293.3578
1959.8948 | 349.9828 | 293.1909 | 293.0828 | 293.4239
1960.8948 | 350.0202 | 293.2644 | 293.154 | 293.491
1961.8948 | 349.9765 | 293.3213 | 293.2203 | 293.5569
1962.8948 | 349.9409 | 293.398 | 293.2759 | 293.6226
1963.8948 | 349.8685 | 293.4574 | 293.3452 | 293.6806
1964.8948 | 350.0276 | 293.5078 | 293.4046 | 293.7492
1965.8948 | 350.0787 | 293.5757 | 293.4796 | 293.8106
1966.8948 | 350.1731 | 293.6335 | 293.5379 | 293.8744
1967.8948 | 350.2917 | 293.7071 | 293.6141 | 293.9441
1968.8948 | 350.4149 | 293.7683 | 293.6715 | 294.0018
1969.8948 | 350.4201 | 293.8288 | 293.7309 | 294.0656
1970.8948 | 350.3884 | 293.8878 | 293.7941 | 294.1276
1971.8948 | 350.4568 | 293.9426 | 293.8505 | 294.1875
1972.8948 | 350.5156 | 294.0108 | 293.92 | 294.2459
1973.8948 | 350.5667 | 294.0708 | 293.9782 | 294.3066
1974.9104 | 350.5857 | 294.1329 | 294.0365 | 294.3702
1975.8948 | 350.6602 | 294.1929 | 294.099 | 294.4264
1976.8948 | 350.6849 | 294.2462 | 294.1604 | 294.483
1977.8948 | 350.7226 | 294.3106 | 294.2292 | 294.5484
1978.8948 | 350.824 | 294.3678 | 294.2797 | 294.6081
1979.8948 | 350.7737 | 294.4305 | 294.3442 | 294.6668
1980.8948 | 350.8134 | 294.488 | 294.4012 | 294.728
1981.8948 | 350.8194 | 294.5512 | 294.4587 | 294.7811
1982.8948 | 350.8823 | 294.6047 | 294.5156 | 294.8401
1983.8948 | 350.9044 | 294.6563 | 294.5774 | 294.895
1984.8948 | 350.9609 | 294.7114 | 294.633 | 294.9581
1985.8948 | 350.9891 | 294.7813 | 294.6992 | 295.01
1986.8948 | 351.0475 | 294.839 | 294.7516 | 295.068
1987.8948 | 351.0797 | 294.8893 | 294.8114 | 295.1273
1988.8948 | 351.0217 | 294.9421 | 294.8651 | 295.1831
1989.8948 | 351.009 | 294.9924 | 294.9318 | 295.2426
1990.8948 | 351.0212 | 295.0556 | 294.9825 | 295.2966
1991.8948 | 351.0893 | 295.1197 | 295.0402 | 295.3499
1992.8948 | 351.1244 | 295.173 | 295.0944 | 295.4126
1993.8948 | 351.1701 | 295.2105 | 295.1515 | 295.4718
1994.8948 | 351.193 | 295.2808 | 295.1985 | 295.5151
1995.8948 | 351.1998 | 295.3372 | 295.2582 | 295.5729
1996.8948 | 351.1756 | 295.3897 | 295.3233 | 295.6302
1997.8948 | 351.0955 | 295.4374 | 295.374 | 295.6828
1998.9104 | 351.0621 | 295.4964 | 295.4232 | 295.7349
1999.8948 | 351.0507 | 295.5471 | 295.483 | 295.7929
2000.8948 | 350.9528 | 295.5928 | 295.5403 | 295.8467
2001.8948 | 350.813 | 295.6481 | 295.6004 | 295.8995
2002.8948 | 350.8645 | 295.7026 | 295.6409 | 295.9492
2003.8948 | 350.8788 | 295.7536 | 295.7048 | 296.0059
2004.8948 | 350.8814 | 295.8187 | 295.7538 | 296.0552
2005.8948 | 350.9198 | 295.8687 | 295.8086 | 296.1072
2006.8948 | 350.9124 | 295.9181 | 295.861 | 296.1615
2007.8948 | 350.9019 | 295.9662 | 295.9126 | 296.2158
2008.8948 | 350.8946 | 296.02 | 295.9667 | 296.2675
2009.8948 | 350.9184 | 296.0776 | 296.0205 | 296.3172
2010.8948 | 350.9448 | 296.1183 | 296.0688 | 296.3711
2011.8948 | 351.0582 | 296.1752 | 296.128 | 296.4252
2012.8948 | 351.0908 | 296.2295 | 296.1743 | 296.4786
2013.8948 | 351.0493 | 296.2757 | 296.226 | 296.5289
2014.8948 | 351.0767 | 296.3353 | 296.2801 | 296.5821
2015.8948 | 351.1376 | 296.3823 | 296.3391 | 296.6376
2016.8948 | 351.1099 | 296.4355 | 296.3819 | 296.6805
2017.8948 | 350.9401 | 296.4851 | 296.4346 | 296.7356
2018.8948 | 350.9576 | 296.5353 | 296.4829 | 296.7905
2019.8948 | 351.1388 | 296.5822 | 296.5353 | 296.8348
2020.8948 | 351.1576 | 296.6359 | 296.5914 | 296.8851
2021.8948 | 351.1098 | 296.6904 | 296.6449 | 296.9409
2022.8948 | 351.1245 | 296.741 | 296.6866 | 296.9909
2023.8948 | 351.1948 | 296.7911 | 296.738 | 297.0439
2024.8948 | 351.2606 | 296.8404 | 296.7866 | 297.0897
2025.8948 | 351.1892 | 296.8899 | 296.839 | 297.1386
2026.8948 | 351.1668 | 296.9274 | 296.8854 | 297.1851
2027.8948 | 351.144 | 296.9898 | 296.9379 | 297.2403
2028.8948 | 351.1955 | 297.0469 | 296.9929 | 297.2871
2029.8948 | 351.2447 | 297.0865 | 297.045 | 297.3354
2030.8948 | 351.1996 | 297.1432 | 297.098 | 297.39
2031.8948 | 351.129 | 297.1916 | 297.1418 | 297.4378
2032.8948 | 351.1899 | 297.2384 | 297.196 | 297.485
2033.8948 | 351.2429 | 297.2834 | 297.2451 | 297.5332
2034.8948 | 351.1854 | 297.338 | 297.2975 | 297.5897
2035.8948 | 351.2981 | 297.3809 | 297.347 | 297.636
2036.8948 | 351.3554 | 297.4366 | 297.3898 | 297.6814
2037.8948 | 351.3835 | 297.4715 | 297.4411 | 297.7266
2038.8948 | 351.4567 | 297.5333 | 297.4872 | 297.7786
2039.8948 | 351.4743 | 297.5729 | 297.5402 | 297.8283
2040.8948 | 351.5144 | 297.6345 | 297.5868 | 297.8802