## Test Conditions
DESIREE-FIRE Test Number 4 - Circuit Simulator Data Only
Test Date: | 2009-07-30
DCSim DAQ Start Time | 8:20
DCSim Time for Synchronization | 8:28
Heat Source Synchronization | 1:19 | minutes:seconds
Heat Source DAQ Start Time | 8:27
Heat Source Start Time | 8:31
DCSim Offset | 0:11 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 635 | seconds
Heat Source Offset | 0:04 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 220 | seconds
Heat Source Stop Time | 8:58
Test Duration | 0:27 | minutes:seconds
| 1637 | seconds
CT500 Turns | 2 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 5
Pre-Test Baseline: | Yes
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | XLPE/CSPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-1.0156 | 122.9782 | -60.8643 | 61.9308 | 0.19836 | 0.015381 | 0.016876 | 0.0061952 | 0.062805 | -0.0008544 | 0.070068 | -60.9558 | 61.8347 | -60.8231 | -61.0703 | 61.7432 | 0.041199 | 0.036621 | -0.036621 | 61.7889 | -61.0153 | 0.041199 | -0.09613 | -0.091553 | -0.20599 | -0.18768 | -0.15106 | -0.14191 | -0.13275 | 60.9009 | 60.8276 | 122.6074 | 122.699 | -0.091553 | 122.6532 | 60.9055 | -0.15106 | 122.699 | -0.091553 | 60.9055 | 122.6074 | 122.6532 | -122.7539 | -122.9462
0.03125 | 122.9828 | -60.8643 | 61.9308 | -0.0076295 | 0.017517 | 0.013672 | 0.0042726 | 0.062805 | -0.0014954 | 0.069855 | -61.0062 | 61.8759 | -60.8643 | -61.0886 | 61.7294 | -0.059509 | 0.50812 | 0.17853 | 61.8805 | -60.9329 | 0 | -0.054931 | -0.14191 | -0.2243 | -0.20142 | -0.068664 | -0.050354 | -0.14191 | 61.3724 | 61.0428 | 122.5937 | 122.7402 | -0.14191 | 122.7448 | 60.8047 | -0.068664 | 122.7402 | -0.14191 | 60.8047 | 122.5937 | 122.7448 | -122.7951 | -122.8638
0.98438 | 122.9691 | -60.8597 | 61.972 | -0.015259 | 0.014313 | 0.01709 | 0.0049134 | 0.063873 | -0.0014954 | 0.07135 | -60.9833 | 61.8484 | -60.878 | -61.1618 | 61.3678 | -0.21973 | 0.48065 | 0.013733 | 61.853 | -60.9604 | -0.018311 | -0.1236 | -0.1236 | -0.30212 | -0.60425 | -0.10071 | -0.11902 | -0.10528 | 61.3403 | 60.8734 | 122.2275 | 122.7081 | -0.1236 | 122.7127 | 60.64 | -0.10071 | 122.7081 | -0.1236 | 60.64 | 122.2275 | 122.7127 | -122.85 | -122.9324
2.0312 | 123.0469 | -60.8276 | 61.8988 | 0.34332 | 0.014313 | 0.016876 | -0.0008544 | 0.066009 | -0.003418 | 0.072632 | -60.9375 | 61.7386 | -60.8505 | -61.0519 | 61.7661 | 0.054932 | -0.13275 | 0.004578 | 61.7706 | -60.9238 | -0.022888 | -0.16022 | -0.10986 | -0.2243 | -0.13275 | -0.09613 | -0.12817 | -0.086975 | 60.6949 | 60.8322 | 122.5937 | 122.5662 | -0.10986 | 122.5983 | 60.8826 | -0.09613 | 122.5662 | -0.10986 | 60.8826 | 122.5937 | 122.5983 | -122.7493 | -122.8226
2.9844 | 123.0652 | -60.8597 | 61.9675 | 0.068664 | 0.01709 | 0.013886 | 0.0081178 | 0.064514 | -0.0040588 | 0.070923 | -60.9512 | 61.8393 | -60.8322 | -60.9924 | 61.8164 | 0.11902 | 0.10071 | 0.064087 | 61.821 | -60.9512 | 0.027466 | -0.12817 | -0.091553 | -0.13275 | -0.15106 | -0.091553 | -0.14648 | -0.11902 | 60.9604 | 60.9238 | 122.6761 | 122.699 | -0.091553 | 122.6807 | 60.9787 | -0.091553 | 122.699 | -0.091553 | 60.9787 | 122.6761 | 122.6807 | -122.7997 | -122.9187
4.0312 | 122.9874 | -60.8551 | 61.9217 | -0.038147 | 0.015595 | 0.016876 | 0.0025636 | 0.063019 | -0.0025634 | 0.070923 | -60.9467 | 61.8027 | -60.8185 | -61.0062 | 61.7889 | 0.14191 | 0.086975 | 0.10529 | 61.8164 | -60.9558 | 0.036622 | -0.11902 | -0.091552 | -0.15106 | -0.13275 | -0.10071 | -0.10529 | -0.12817 | 60.9421 | 60.9604 | 122.644 | 122.6578 | -0.091552 | 122.6715 | 60.997 | -0.10071 | 122.6578 | -0.091552 | 60.997 | 122.644 | 122.6715 | -122.7402 | -122.8775
4.9844 | 123.0881 | -60.8185 | 61.9354 | -0.045776 | 0.013458 | 0.018372 | 0.0012818 | 0.062591 | -0.0029906 | 0.071777 | -60.9009 | 61.7569 | -60.8139 | -60.965 | 61.8439 | 0.17395 | -0.009155 | 0.15106 | 61.7661 | -60.9146 | 0.004577 | -0.17853 | -0.082398 | -0.14648 | -0.091553 | -0.096131 | -0.16937 | -0.086975 | 60.8093 | 60.9695 | 122.6624 | 122.5754 | -0.082398 | 122.5845 | 60.9924 | -0.096131 | 122.5754 | -0.082398 | 60.9924 | 122.6624 | 122.5845 | -122.7493 | -122.85
5.9844 | 123.0331 | -60.878 | 61.9492 | 0.099182 | 0.017731 | 0.016663 | 0.006836 | 0.064728 | -0.0002136 | 0.071136 | -60.9421 | 61.853 | -60.8276 | -61.0245 | 61.7706 | 0.09613 | 0.059509 | 0.032043 | 61.8301 | -60.9833 | 0.050354 | -0.096131 | -0.064087 | -0.14648 | -0.17853 | -0.10528 | -0.11902 | -0.11444 | 60.9375 | 60.91 | 122.6486 | 122.731 | -0.064087 | 122.7081 | 60.9741 | -0.10528 | 122.731 | -0.064087 | 60.9741 | 122.6486 | 122.7081 | -122.7768 | -122.9324
7.0312 | 122.9782 | -60.8734 | 61.972 | -0.030518 | 0.017944 | 0.013245 | 0.0021362 | 0.063232 | -0.001709 | 0.071564 | -61.0107 | 61.8347 | -60.8597 | -61.0794 | 61.7294 | 0.073242 | 0.16937 | 0.032043 | 61.8622 | -60.9375 | 0.013733 | -0.13733 | -0.13733 | -0.20599 | -0.24262 | -0.064087 | -0.10986 | -0.15106 | 61.0428 | 60.9055 | 122.6028 | 122.7081 | -0.13733 | 122.7356 | 60.9467 | -0.064087 | 122.7081 | -0.13733 | 60.9467 | 122.6028 | 122.7356 | -122.8317 | -122.9095
7.9844 | 122.9828 | -60.8414 | 61.9492 | -0.053406 | 0.015595 | 0.013245 | 0.0029908 | 0.063446 | -0.003418 | 0.070068 | -60.997 | 61.8484 | -60.8643 | -61.0748 | 61.7386 | 0.073242 | 0.17853 | 0.041199 | 61.8484 | -60.9467 | -0.022888 | -0.10071 | -0.15564 | -0.23346 | -0.21057 | -0.10529 | -0.10071 | -0.13275 | 61.0199 | 60.8826 | 122.58 | 122.6898 | -0.15564 | 122.6898 | 60.9146 | -0.10529 | 122.6898 | -0.15564 | 60.9146 | 122.58 | 122.6898 | -122.8134 | -122.8958
8.9844 | 122.9691 | -60.8459 | 61.972 | 0 | 0.016449 | 0.01004 | 0.0057678 | 0.06366 | -0.0019226 | 0.071777 | -61.0016 | 61.8576 | -60.8368 | -61.0886 | 61.7477 | 0.064087 | 0.17395 | 0.009155 | 61.8484 | -60.9467 | 0.009155 | -0.11444 | -0.15564 | -0.24262 | -0.2243 | -0.10071 | -0.1236 | -0.16479 | 61.0199 | 60.8551 | 122.5937 | 122.7036 | -0.15564 | 122.6944 | 60.91 | -0.10071 | 122.7036 | -0.15564 | 60.91 | 122.5937 | 122.6944 | -122.8088 | -122.9187
10.0156 | 123.0606 | -60.8597 | 61.8988 | 0.39673 | 0.016022 | 0.015167 | -0.0002136 | 0.065796 | -0.0023498 | 0.071564 | -60.9924 | 61.7935 | -60.8551 | -61.0703 | 61.7523 | 0 | -0.13733 | -0.041199 | 61.7569 | -60.9695 | 0.004577 | -0.10529 | -0.13275 | -0.21057 | -0.14648 | -0.10986 | -0.14191 | -0.13733 | 60.7224 | 60.8185 | 122.612 | 122.6532 | -0.13275 | 122.6166 | 60.8597 | -0.10986 | 122.6532 | -0.13275 | 60.8597 | 122.612 | 122.6166 | -122.7539 | -122.8683
10.9844 | 123.0469 | -60.8734 | 61.9629 | 0.091552 | 0.018799 | 0.02243 | 0.0046998 | 0.065155 | -0.0023498 | 0.071777 | -60.9467 | 61.8713 | -60.8459 | -61.0291 | 61.7844 | 0.086975 | 0.064087 | 0.036621 | 61.821 | -60.9787 | 0.027466 | -0.091553 | -0.073242 | -0.15564 | -0.17853 | -0.10529 | -0.14191 | -0.10071 | 60.9375 | 60.91 | 122.6578 | 122.7448 | -0.073242 | 122.6944 | 60.9604 | -0.10529 | 122.7448 | -0.073242 | 60.9604 | 122.6578 | 122.6944 | -122.8088 | -122.9416
12.0312 | 123.0103 | -60.8734 | 61.9446 | 0.045776 | 0.016876 | 0.017517 | 0.0057678 | 0.063873 | -0.0006408 | 0.070709 | -60.9879 | 61.8668 | -60.8597 | -61.0519 | 61.7477 | 0.07782 | 0.13733 | 0 | 61.8576 | -60.9421 | 0.013733 | -0.07782 | -0.11444 | -0.17853 | -0.19684 | -0.068665 | -0.086975 | -0.12817 | 61.0107 | 60.8734 | 122.6212 | 122.7402 | -0.11444 | 122.731 | 60.9512 | -0.068665 | 122.7402 | -0.11444 | 60.9512 | 122.6212 | 122.731 | -122.8043 | -122.8867
12.9844 | 122.9965 | -60.8643 | 61.9583 | -0.015259 | 0.017944 | 0.013031 | 0.0021362 | 0.065796 | -0.001709 | 0.071991 | -61.0062 | 61.8393 | -60.8734 | -61.0794 | 61.7523 | 0.07782 | 0.16479 | 0.027466 | 61.8439 | -60.9787 | -0.009155 | -0.11902 | -0.14191 | -0.21515 | -0.20599 | -0.11444 | -0.11444 | -0.13275 | 61.0291 | 60.8917 | 122.6166 | 122.7036 | -0.14191 | 122.7081 | 60.9421 | -0.11444 | 122.7036 | -0.14191 | 60.9421 | 122.6166 | 122.7081 | -122.8317 | -122.937
14.0312 | 123.1247 | -60.8322 | 61.9217 | 0.030518 | 0.01474 | 0.013031 | -0.0014952 | 0.062378 | -0.0019226 | 0.070923 | -60.9192 | 61.7706 | -60.8231 | -60.9787 | 61.8622 | 0.18768 | 0.004578 | 0.15564 | 61.8027 | -60.9055 | 0.009155 | -0.15106 | -0.086975 | -0.14648 | -0.059509 | -0.073243 | -0.11902 | -0.09613 | 60.8368 | 60.9879 | 122.6944 | 122.6028 | -0.086975 | 122.6349 | 61.0199 | -0.073243 | 122.6028 | -0.086975 | 61.0199 | 122.6944 | 122.6349 | -122.7448 | -122.8271
14.9844 | 122.9599 | -60.8734 | 61.9354 | -0.022889 | 0.016449 | 0.017517 | 0.0019226 | 0.062805 | -0.0023498 | 0.070496 | -61.0062 | 61.8301 | -60.8688 | -61.0657 | 61.7477 | 0.07782 | 0.17395 | 0.027466 | 61.8439 | -60.965 | 0.004578 | -0.10529 | -0.13275 | -0.19226 | -0.18768 | -0.091553 | -0.091553 | -0.13733 | 61.0474 | 60.9009 | 122.6212 | 122.7036 | -0.13275 | 122.7173 | 60.9512 | -0.091553 | 122.7036 | -0.13275 | 60.9512 | 122.6212 | 122.7173 | -122.8043 | -122.9004
16.0156 | 123.0103 | -60.8551 | 61.908 | 0.43488 | 0.015167 | 0.015595 | 0.004059 | 0.064941 | -0.0023498 | 0.07135 | -61.0107 | 61.7752 | -60.8826 | -61.0977 | 61.734 | -0.004578 | -0.07782 | 0.009155 | 61.8164 | -60.9695 | -0.027465 | -0.13275 | -0.15564 | -0.24261 | -0.17395 | -0.11444 | -0.091553 | -0.12817 | 60.7773 | 60.8643 | 122.5891 | 122.6303 | -0.15564 | 122.6715 | 60.8505 | -0.11444 | 122.6303 | -0.15564 | 60.8505 | 122.5891 | 122.6715 | -122.7905 | -122.8775
16.9844 | 123.0606 | -60.8093 | 61.94 | 0.045776 | 0.012604 | 0.015167 | 0.0010682 | 0.0643 | -0.0036316 | 0.07135 | -60.9238 | 61.7615 | -60.8093 | -60.9787 | 61.8301 | 0.16022 | 0.022888 | 0.15106 | 61.8073 | -60.9375 | 0 | -0.17853 | -0.11444 | -0.16937 | -0.10986 | -0.12817 | -0.13275 | -0.11444 | 60.8322 | 60.9604 | 122.6395 | 122.5708 | -0.11444 | 122.6166 | 60.9695 | -0.12817 | 122.5708 | -0.11444 | 60.9695 | 122.6395 | 122.6166 | -122.7493 | -122.8775
18.0312 | 123.0881 | -60.8093 | 61.9171 | 0.015259 | 0.015381 | 0.015595 | -0.0008544 | 0.062378 | -0.0038452 | 0.071136 | -60.9192 | 61.7523 | -60.8002 | -60.9741 | 61.8484 | 0.17395 | 0.009155 | 0.15564 | 61.7752 | -60.9238 | 0.009155 | -0.16479 | -0.10986 | -0.16479 | -0.068664 | -0.11444 | -0.14191 | -0.11902 | 60.8185 | 60.965 | 122.6578 | 122.5616 | -0.10986 | 122.5845 | 60.9833 | -0.11444 | 122.5616 | -0.10986 | 60.9833 | 122.6578 | 122.5845 | -122.7173 | -122.8409
18.9844 | 122.9919 | -60.8459 | 61.972 | -0.022889 | 0.015167 | 0.015381 | 0.0046998 | 0.061737 | -0.002777 | 0.071136 | -60.997 | 61.8073 | -60.8459 | -61.0794 | 61.7477 | 0.082397 | 0.16937 | 0.022888 | 61.8347 | -60.9512 | 0 | -0.16479 | -0.15106 | -0.23346 | -0.2243 | -0.10529 | -0.13733 | -0.15106 | 61.0153 | 60.8688 | 122.5937 | 122.6532 | -0.15106 | 122.6807 | 60.9283 | -0.10529 | 122.6532 | -0.15106 | 60.9283 | 122.5937 | 122.6807 | -122.818 | -122.9233
20.0312 | 123.0698 | -60.8276 | 61.9308 | -0.015259 | 0.014954 | 0.018372 | 0.0019226 | 0.06366 | -0.0023498 | 0.070709 | -60.9283 | 61.7935 | -60.7956 | -60.9787 | 61.8301 | 0.16022 | 0.050354 | 0.12817 | 61.7935 | -60.9375 | 0.032044 | -0.13733 | -0.10071 | -0.15106 | -0.10071 | -0.10986 | -0.13733 | -0.13275 | 60.878 | 60.9558 | 122.6578 | 122.6212 | -0.10071 | 122.6212 | 60.9879 | -0.10986 | 122.6212 | -0.10071 | 60.9879 | 122.6578 | 122.6212 | -122.7264 | -122.8683
20.9844 | 123.1155 | -60.7956 | 61.9125 | 0.022888 | 0.014526 | 0.016449 | 0.0002136 | 0.061737 | -0.0006408 | 0.071991 | -60.8917 | 61.7386 | -60.8276 | -60.965 | 61.8484 | 0.1831 | -0.013733 | 0.15564 | 61.7615 | -60.9283 | -0.032044 | -0.17395 | -0.096131 | -0.16937 | -0.064087 | -0.13275 | -0.15106 | -0.064087 | 60.7819 | 60.9512 | 122.644 | 122.5342 | -0.096131 | 122.5571 | 60.9787 | -0.13275 | 122.5342 | -0.096131 | 60.9787 | 122.644 | 122.5571 | -122.7402 | -122.8409
22.0312 | 123.1018 | -60.8414 | 61.9125 | 0.40436 | 0.016022 | 0.016022 | 0.0025636 | 0.063232 | -0.002777 | 0.071777 | -60.9512 | 61.7157 | -60.8414 | -61.0107 | 61.8118 | 0.073242 | -0.16937 | 0.027466 | 61.7615 | -60.9421 | 0 | -0.19684 | -0.10986 | -0.16937 | -0.10071 | -0.10071 | -0.15106 | -0.10986 | 60.672 | 60.8688 | 122.6532 | 122.5571 | -0.10986 | 122.6028 | 60.9146 | -0.10071 | 122.5571 | -0.10986 | 60.9146 | 122.6532 | 122.6028 | -122.7539 | -122.8546
22.9844 | 123.0789 | -60.8002 | 61.9308 | -0.0076295 | 0.016663 | 0.017304 | 0.0019226 | 0.063019 | -0.0021362 | 0.07135 | -60.9146 | 61.7523 | -60.8276 | -60.9558 | 61.8439 | 0.17395 | -0.027466 | 0.14191 | 61.7661 | -60.9421 | -0.027466 | -0.17853 | -0.11444 | -0.15564 | -0.086975 | -0.14191 | -0.16479 | -0.086975 | 60.7727 | 60.9421 | 122.644 | 122.5525 | -0.11444 | 122.5662 | 60.9741 | -0.14191 | 122.5525 | -0.11444 | 60.9741 | 122.644 | 122.5662 | -122.7585 | -122.8729
24.0312 | 122.9874 | -60.8505 | 61.9583 | -0.022889 | 0.017304 | 0.009613 | 0.0049134 | 0.062805 | -0.002777 | 0.071991 | -61.0199 | 61.8393 | -60.8551 | -61.0794 | 61.7294 | 0.064087 | 0.16022 | 0.009155 | 61.8439 | -60.9741 | -0.004578 | -0.11902 | -0.16937 | -0.22888 | -0.22888 | -0.1236 | -0.11444 | -0.16479 | 61.0107 | 60.8597 | 122.58 | 122.6898 | -0.16937 | 122.6944 | 60.9146 | -0.1236 | 122.6898 | -0.16937 | 60.9146 | 122.58 | 122.6944 | -122.8134 | -122.9324
24.9844 | 123.0789 | -60.8139 | 61.8988 | 0.19836 | 0.014526 | 0.01474 | -0.0004272 | 0.0643 | -0.0021362 | 0.069 | -60.9879 | 61.7432 | -60.8597 | -61.0382 | 61.7889 | 0.07782 | -0.045776 | 0.041199 | 61.7844 | -60.9192 | -0.045776 | -0.15564 | -0.17395 | -0.2243 | -0.10986 | -0.10529 | -0.11444 | -0.12817 | 60.7681 | 60.8551 | 122.6028 | 122.5571 | -0.17395 | 122.5983 | 60.8917 | -0.10529 | 122.5571 | -0.17395 | 60.8917 | 122.6028 | 122.5983 | -122.7585 | -122.818
25.9844 | 123.1293 | -60.8002 | 61.9034 | 0.076294 | 0.013458 | 0.015381 | 0.0025636 | 0.062164 | -0.0021362 | 0.070923 | -60.9146 | 61.734 | -60.8414 | -60.9467 | 61.8713 | 0.1831 | -0.041199 | 0.16022 | 61.7706 | -60.91 | -0.041199 | -0.16937 | -0.11444 | -0.14648 | -0.032043 | -0.10986 | -0.13275 | -0.073242 | 60.759 | 60.9604 | 122.6715 | 122.5342 | -0.11444 | 122.5708 | 60.9833 | -0.10986 | 122.5342 | -0.11444 | 60.9833 | 122.6715 | 122.5708 | -122.7448 | -122.8134
26.9844 | 123.0743 | -60.8414 | 61.9583 | -0.030518 | 0.016876 | 0.015595 | 0.001709 | 0.062805 | -0.0038452 | 0.071777 | -60.9329 | 61.8073 | -60.8093 | -60.9833 | 61.7981 | 0.12817 | 0.07782 | 0.032043 | 61.7752 | -60.9741 | 0.032044 | -0.15106 | -0.091552 | -0.14191 | -0.16022 | -0.13275 | -0.1831 | -0.1236 | 60.9192 | 60.8734 | 122.6395 | 122.6486 | -0.091552 | 122.6166 | 60.9695 | -0.13275 | 122.6486 | -0.091552 | 60.9695 | 122.6395 | 122.6166 | -122.7676 | -122.9324
28.0312 | 123.1018 | -60.8368 | 61.908 | 0.17548 | 0.014954 | 0.0089722 | 0.0036316 | 0.062591 | -0.0046996 | 0.072418 | -60.9741 | 61.7523 | -60.8459 | -61.0199 | 61.7981 | 0.10529 | -0.032043 | 0.068665 | 61.7752 | -60.9421 | -0.009155 | -0.15564 | -0.13733 | -0.1831 | -0.10986 | -0.10529 | -0.13275 | -0.12817 | 60.8047 | 60.9055 | 122.6349 | 122.5891 | -0.13733 | 122.612 | 60.9421 | -0.10529 | 122.5891 | -0.13733 | 60.9421 | 122.6349 | 122.612 | -122.7539 | -122.85
28.9844 | 123.024 | -60.8322 | 61.9858 | 0.045776 | 0.016022 | 0.017304 | 0.0072632 | 0.06131 | -0.0019226 | 0.069 | -60.9833 | 61.8347 | -60.8734 | -61.0611 | 61.7432 | 0.07782 | 0.14648 | 0.013733 | 61.8256 | -60.965 | -0.041199 | -0.15106 | -0.15106 | -0.22888 | -0.24262 | -0.13275 | -0.16022 | -0.10986 | 60.9787 | 60.8459 | 122.5754 | 122.6669 | -0.15106 | 122.6578 | 60.91 | -0.13275 | 122.6669 | -0.15106 | 60.91 | 122.5754 | 122.6578 | -122.8592 | -122.9507
30.0312 | 123.0835 | -60.8185 | 61.94 | 0.053405 | 0.014099 | 0.015167 | 0.003418 | 0.062805 | -0.0014954 | 0.069214 | -60.8963 | 61.7935 | -60.8002 | -60.965 | 61.8484 | 0.16937 | 0.004578 | 0.12817 | 61.7889 | -60.9375 | 0.01831 | -0.14648 | -0.07782 | -0.14648 | -0.091552 | -0.11902 | -0.15106 | -0.09613 | 60.8231 | 60.9467 | 122.6669 | 122.612 | -0.07782 | 122.6074 | 60.9879 | -0.11902 | 122.612 | -0.07782 | 60.9879 | 122.6669 | 122.6074 | -122.7402 | -122.8775
30.9844 | 123.056 | -60.8276 | 61.9537 | -0.030518 | 0.014313 | 0.014526 | 0.003418 | 0.063019 | -0.0032044 | 0.07135 | -60.9375 | 61.7889 | -60.8322 | -61.0016 | 61.8988 | 0.013733 | 0.032043 | 0.20599 | 61.7844 | -60.9329 | -0.004577 | -0.1648 | -0.10986 | -0.17395 | -0.054931 | -0.10528 | -0.16937 | -0.10529 | 60.8597 | 61.0336 | 122.7264 | 122.6166 | -0.10986 | 122.612 | 60.8414 | -0.10528 | 122.6166 | -0.10986 | 60.8414 | 122.7264 | 122.612 | -122.7859 | -122.8867
32.0312 | 123.1201 | -60.8093 | 61.9125 | 0.022888 | 0.015595 | 0.012177 | 0.0002136 | 0.0643 | -0.0040588 | 0.069214 | -60.91 | 61.7432 | -60.8276 | -60.9695 | 61.8622 | 0.17853 | -0.022888 | 0.15106 | 61.7661 | -60.9192 | -0.018311 | -0.16937 | -0.10071 | -0.16022 | -0.050354 | -0.10986 | -0.14648 | -0.082397 | 60.7864 | 60.9604 | 122.6715 | 122.5525 | -0.10071 | 122.5754 | 60.9879 | -0.10986 | 122.5525 | -0.10071 | 60.9879 | 122.6715 | 122.5754 | -122.7402 | -122.8317
32.9844 | 123.0423 | -60.8276 | 61.8851 | 0.30518 | 0.014099 | 0.016235 | 0.00235 | 0.061523 | -0.0025634 | 0.071991 | -60.9787 | 61.7523 | -60.8688 | -61.0611 | 61.7569 | 0.054932 | -0.054932 | 0.013733 | 61.7752 | -60.9512 | -0.041198 | -0.13275 | -0.15106 | -0.23346 | -0.12817 | -0.1236 | -0.10986 | -0.10986 | 60.7727 | 60.8414 | 122.5845 | 122.58 | -0.15106 | 122.6028 | 60.8826 | -0.1236 | 122.58 | -0.15106 | 60.8826 | 122.5845 | 122.6028 | -122.7539 | -122.8363
33.9844 | 123.0927 | -60.8093 | 61.9263 | 0.022888 | 0.015167 | 0.016663 | 0.0029908 | 0.062164 | -0.0040588 | 0.069855 | -60.8917 | 61.7569 | -60.8505 | -60.9512 | 61.8393 | 0.16022 | 0.004578 | 0.16479 | 61.7798 | -60.9421 | -0.041199 | -0.16937 | -0.082398 | -0.14191 | -0.086976 | -0.13275 | -0.14649 | -0.041199 | 60.8139 | 60.9741 | 122.6486 | 122.5662 | -0.082398 | 122.5891 | 60.9695 | -0.13275 | 122.5662 | -0.082398 | 60.9695 | 122.6486 | 122.5891 | -122.7768 | -122.8683
35.0312 | 123.1384 | -60.8047 | 61.9308 | 0.11444 | 0.014099 | 0.013672 | 0.0014954 | 0.062591 | -0.001709 | 0.069855 | -60.91 | 61.7523 | -60.8093 | -60.9512 | 61.8668 | 0.17853 | -0.059509 | 0.14648 | 61.7661 | -60.9329 | -0.004577 | -0.17853 | -0.10529 | -0.14648 | -0.064087 | -0.12817 | -0.16479 | -0.10071 | 60.7452 | 60.9512 | 122.6715 | 122.5571 | -0.10529 | 122.5708 | 60.9833 | -0.12817 | 122.5571 | -0.10529 | 60.9833 | 122.6715 | 122.5708 | -122.7402 | -122.8638
35.9844 | 123.0698 | -60.8093 | 61.9492 | 0.007629 | 0.016235 | 0.015167 | 0.0042726 | 0.060669 | -0.005127 | 0.070923 | -60.9329 | 61.7889 | -60.8276 | -60.9787 | 61.8164 | 0.15564 | 0.059509 | 0.10529 | 61.7889 | -60.9146 | -0.018311 | -0.16022 | -0.1236 | -0.16937 | -0.13275 | -0.10529 | -0.16022 | -0.10528 | 60.8688 | 60.9146 | 122.6257 | 122.5983 | -0.1236 | 122.5983 | 60.965 | -0.10529 | 122.5983 | -0.1236 | 60.965 | 122.6257 | 122.5983 | -122.7768 | -122.8638
37.0156 | 122.9965 | -60.8643 | 61.9537 | 0.35858 | 0.018158 | 0.019226 | 0.0093994 | 0.064087 | -0.0040588 | 0.07135 | -61.0245 | 61.7935 | -60.8963 | -61.1114 | 61.6974 | -0.054932 | 0.018311 | -0.10986 | 61.7981 | -60.9879 | -0.032043 | -0.16022 | -0.16022 | -0.24719 | -0.25635 | -0.1236 | -0.15564 | -0.12817 | 60.8826 | 60.7544 | 122.5616 | 122.6578 | -0.16022 | 122.6624 | 60.8093 | -0.1236 | 122.6578 | -0.16022 | 60.8093 | 122.5616 | 122.6624 | -122.85 | -122.9416
37.9844 | 123.0743 | -60.8231 | 61.9034 | 0.22888 | 0.016022 | 0.014526 | -0.001068 | 0.063446 | -0.0023498 | 0.071991 | -61.0016 | 61.7569 | -60.8597 | -61.0382 | 61.7935 | 0.082397 | -0.036621 | 0.027466 | 61.7661 | -60.9329 | -0.036621 | -0.14648 | -0.17853 | -0.21515 | -0.10986 | -0.10986 | -0.13733 | -0.14191 | 60.7864 | 60.8505 | 122.6166 | 122.58 | -0.17853 | 122.5891 | 60.9055 | -0.10986 | 122.58 | -0.17853 | 60.9055 | 122.6166 | 122.5891 | -122.7631 | -122.8363
39.0312 | 123.0743 | -60.8322 | 61.8988 | 0.21362 | 0.013672 | 0.017304 | 0.0027772 | 0.060882 | -0.0046996 | 0.069855 | -60.9512 | 61.7477 | -60.8505 | -61.0199 | 61.8347 | 0.11444 | -0.045776 | 0.086975 | 61.7661 | -60.9421 | -0.018311 | -0.15106 | -0.11902 | -0.18768 | -0.064087 | -0.10986 | -0.13275 | -0.10071 | 60.7864 | 60.9192 | 122.6669 | 122.58 | -0.11902 | 122.5983 | 60.9467 | -0.10986 | 122.58 | -0.11902 | 60.9467 | 122.6669 | 122.5983 | -122.7493 | -122.8409
39.9844 | 123.0469 | -60.8368 | 61.9308 | 0.3891 | 0.015808 | 0.016663 | 0.0049134 | 0.061096 | -0.0040588 | 0.070282 | -60.9512 | 61.7523 | -60.8505 | -61.0428 | 61.7569 | 0.027466 | -0.1236 | -0.009155 | 61.7249 | -60.9467 | -0.013733 | -0.17853 | -0.11444 | -0.20599 | -0.17395 | -0.10986 | -0.20599 | -0.10071 | 60.7132 | 60.8276 | 122.5937 | 122.5891 | -0.11444 | 122.5616 | 60.8643 | -0.10986 | 122.5891 | -0.11444 | 60.8643 | 122.5937 | 122.5616 | -122.7814 | -122.8775
41.0312 | 123.0927 | -60.8185 | 61.908 | 0.091552 | 0.01474 | 0.011963 | 0.0038452 | 0.061737 | -0.002777 | 0.070282 | -60.9467 | 61.7661 | -60.8459 | -60.9741 | 61.8439 | 0.15106 | -0.059509 | 0.10529 | 61.734 | -60.9421 | -0.027466 | -0.14191 | -0.12817 | -0.15564 | -0.064087 | -0.1236 | -0.17395 | -0.10071 | 60.759 | 60.9238 | 122.6624 | 122.5845 | -0.12817 | 122.5525 | 60.9695 | -0.1236 | 122.5845 | -0.12817 | 60.9695 | 122.6624 | 122.5525 | -122.7539 | -122.85
41.9844 | 123.0789 | -60.8093 | 61.8942 | 0.24414 | 0.015381 | 0.017731 | 0.004059 | 0.061523 | -0.0042724 | 0.070709 | -60.9924 | 61.7249 | -60.8597 | -61.0245 | 61.7889 | 0.045776 | -0.054932 | 0.022888 | 61.734 | -60.9421 | -0.050354 | -0.16937 | -0.18311 | -0.21515 | -0.10529 | -0.13275 | -0.16022 | -0.13275 | 60.7544 | 60.8322 | 122.5983 | 122.5342 | -0.18311 | 122.5433 | 60.8551 | -0.13275 | 122.5342 | -0.18311 | 60.8551 | 122.5983 | 122.5433 | -122.7539 | -122.8363
43.0312 | 123.1201 | -60.8185 | 61.908 | 0.14496 | 0.014313 | 0.014526 | 0.0025636 | 0.06131 | -0.0038452 | 0.070496 | -60.9375 | 61.7661 | -60.8505 | -61.0016 | 61.821 | 0.12817 | -0.045776 | 0.09613 | 61.7569 | -60.9192 | -0.032044 | -0.14191 | -0.11902 | -0.18311 | -0.086975 | -0.10071 | -0.15106 | -0.086975 | 60.7727 | 60.9146 | 122.6395 | 122.5845 | -0.11902 | 122.5754 | 60.9467 | -0.10071 | 122.5845 | -0.11902 | 60.9467 | 122.6395 | 122.5754 | -122.7585 | -122.8271
43.9844 | 123.1155 | -60.8093 | 61.9263 | 0 | 0.015167 | 0.01474 | 0.0044862 | 0.06131 | -0.004486 | 0.068573 | -60.9238 | 61.7569 | -60.8231 | -60.9558 | 61.8622 | 0.17853 | -0.018311 | 0.16022 | 61.7615 | -60.9238 | -0.013733 | -0.16937 | -0.11444 | -0.14648 | -0.064087 | -0.11444 | -0.1648 | -0.10071 | 60.791 | 60.9695 | 122.6715 | 122.5662 | -0.11444 | 122.5708 | 60.9879 | -0.11444 | 122.5662 | -0.11444 | 60.9879 | 122.6715 | 122.5708 | -122.7493 | -122.85
45.0312 | 123.0835 | -60.8093 | 61.9354 | -0.038147 | 0.016663 | 0.01239 | 0.004059 | 0.059174 | -0.0029906 | 0.070496 | -60.9146 | 61.7661 | -60.8414 | -60.9283 | 61.853 | 0.16937 | -0.013733 | 0.14191 | 61.7706 | -60.9146 | -0.032044 | -0.16937 | -0.10529 | -0.11902 | -0.082398 | -0.10529 | -0.1648 | -0.073242 | 60.7956 | 60.9512 | 122.6624 | 122.5754 | -0.10529 | 122.58 | 60.9787 | -0.10529 | 122.5754 | -0.10529 | 60.9787 | 122.6624 | 122.58 | -122.7768 | -122.85
45.9844 | 123.0515 | -60.8368 | 61.9125 | 0.38147 | 0.015595 | 0.019653 | 0.0019226 | 0.063019 | -0.0021362 | 0.070923 | -60.965 | 61.7294 | -60.878 | -61.0611 | 61.7249 | 0.036621 | -0.10986 | -0.018311 | 61.7203 | -60.9421 | -0.041199 | -0.18311 | -0.12817 | -0.2243 | -0.18768 | -0.10529 | -0.19226 | -0.086975 | 60.7269 | 60.8185 | 122.5616 | 122.5662 | -0.12817 | 122.5571 | 60.8734 | -0.10529 | 122.5662 | -0.12817 | 60.8734 | 122.5616 | 122.5571 | -122.7905 | -122.8546
46.9844 | 123.0469 | -60.8505 | 61.9354 | 0.26703 | 0.013672 | 0.014099 | 0.004059 | 0.062164 | -0.0032044 | 0.071136 | -60.9604 | 61.7615 | -60.8597 | -61.0428 | 61.7661 | 0.059509 | -0.050354 | 0.004578 | 61.7661 | -60.9375 | -0.009155 | -0.17395 | -0.10986 | -0.19226 | -0.16937 | -0.086975 | -0.16937 | -0.10071 | 60.8002 | 60.8551 | 122.6166 | 122.612 | -0.10986 | 122.6166 | 60.91 | -0.086975 | 122.612 | -0.10986 | 60.91 | 122.6166 | 122.6166 | -122.7951 | -122.8729
48.0312 | 123.111 | -60.8276 | 61.9171 | 0.15259 | 0.015167 | 0.014313 | 0.0038452 | 0.060028 | -0.0023498 | 0.069427 | -60.9375 | 61.7615 | -60.8276 | -60.9695 | 61.8301 | 0.12817 | -0.064087 | 0.10071 | 61.7706 | -60.9375 | 0 | -0.15564 | -0.10986 | -0.14191 | -0.086975 | -0.10986 | -0.14648 | -0.10986 | 60.7636 | 60.9283 | 122.6578 | 122.5891 | -0.10986 | 122.5983 | 60.9558 | -0.10986 | 122.5891 | -0.10986 | 60.9558 | 122.6578 | 122.5983 | -122.7448 | -122.8546
48.9844 | 123.0881 | -60.8047 | 61.9308 | 0.076294 | 0.015808 | 0.016876 | 0.0042726 | 0.062805 | -0.0019226 | 0.071564 | -60.91 | 61.7569 | -60.8368 | -60.9512 | 61.8668 | 0.17853 | -0.018311 | 0.16022 | 61.7477 | -60.9238 | -0.032043 | -0.17395 | -0.10529 | -0.14648 | -0.064087 | -0.11902 | -0.1831 | -0.073242 | 60.7864 | 60.965 | 122.6715 | 122.5616 | -0.10529 | 122.5525 | 60.9833 | -0.11902 | 122.5616 | -0.10529 | 60.9833 | 122.6715 | 122.5525 | -122.7676 | -122.8546
49.9844 | 123.0606 | -60.8551 | 61.9217 | -0.54932 | 0.014313 | 0.018372 | 0.003418 | 0.062591 | -0.0049134 | 0.070496 | -61.0016 | 61.7523 | -60.8551 | -61.0565 | 61.7615 | 0.041199 | -0.086975 | -0.013733 | 61.7432 | -60.9329 | 0 | -0.16937 | -0.14648 | -0.20142 | -0.16022 | -0.077819 | -0.17853 | -0.14648 | 60.7681 | 60.8414 | 122.6166 | 122.6074 | -0.14648 | 122.5983 | 60.8963 | -0.077819 | 122.6074 | -0.14648 | 60.8963 | 122.6166 | 122.5983 | -122.7768 | -122.8546
51.0312 | 123.1338 | -60.7819 | 61.9125 | 0.007629 | 0.014313 | 0.016876 | 0.0008546 | 0.061096 | -0.0023498 | 0.070496 | -60.8963 | 61.7661 | -60.8368 | -60.9421 | 61.8713 | 0.20599 | -0.032043 | 0.16479 | 61.7386 | -60.9009 | -0.054932 | -0.14648 | -0.11444 | -0.16022 | -0.041199 | -0.11902 | -0.17395 | -0.059509 | 60.7498 | 60.9467 | 122.6532 | 122.5479 | -0.11444 | 122.5204 | 60.9879 | -0.11902 | 122.5479 | -0.11444 | 60.9879 | 122.6532 | 122.5204 | -122.7493 | -122.8134
51.9844 | 123.1293 | -60.8002 | 61.9263 | 0.053405 | 0.014954 | 0.013886 | 0.00235 | 0.061951 | -0.0042724 | 0.071564 | -60.9009 | 61.7798 | -60.8322 | -60.9329 | 61.853 | 0.19226 | -0.027466 | 0.16479 | 61.7569 | -60.9055 | -0.032043 | -0.14649 | -0.10071 | -0.13275 | -0.073243 | -0.10529 | -0.16937 | -0.068665 | 60.7727 | 60.965 | 122.6532 | 122.58 | -0.10071 | 122.5571 | 60.9924 | -0.10529 | 122.58 | -0.10071 | 60.9924 | 122.6532 | 122.5571 | -122.7585 | -122.8317
53.0156 | 122.9691 | -60.8551 | 61.94 | 0.32806 | 0.016663 | 0.013672 | 0.0079042 | 0.062378 | -0.006195 | 0.070709 | -61.0474 | 61.7935 | -60.8917 | -61.1069 | 61.6974 | -0.050354 | 0.027466 | -0.09613 | 61.7661 | -60.997 | -0.036621 | -0.14648 | -0.19226 | -0.25177 | -0.24261 | -0.14191 | -0.17395 | -0.15564 | 60.8826 | 60.759 | 122.5525 | 122.6486 | -0.19226 | 122.6212 | 60.8047 | -0.14191 | 122.6486 | -0.19226 | 60.8047 | 122.5525 | 122.6212 | -122.8317 | -122.937
53.9844 | 123.0148 | -60.8551 | 61.9308 | 0.099182 | 0.018799 | 0.016663 | 0.0076904 | 0.062591 | -0.002777 | 0.071991 | -60.9375 | 61.8713 | -60.8414 | -61.0107 | 61.7798 | 0.082397 | 0.054932 | 0.032043 | 61.7981 | -60.9695 | 0.013733 | -0.059509 | -0.082397 | -0.15564 | -0.15106 | -0.11444 | -0.13275 | -0.09613 | 60.91 | 60.8871 | 122.6349 | 122.7264 | -0.082397 | 122.6532 | 60.9375 | -0.11444 | 122.7264 | -0.082397 | 60.9375 | 122.6349 | 122.6532 | -122.7722 | -122.9004
55.0312 | 123.0789 | -60.8231 | 61.8851 | -0.0076295 | 0.016022 | 0.015167 | 0.0019226 | 0.062591 | -0.0042724 | 0.070068 | -60.9421 | 61.7203 | -60.8643 | -60.9787 | 61.8393 | 0.16022 | -0.045776 | 0.1236 | 61.7615 | -60.9283 | -0.041199 | -0.1648 | -0.11902 | -0.15564 | -0.045777 | -0.10529 | -0.1236 | -0.07782 | 60.7773 | 60.9467 | 122.6624 | 122.5433 | -0.11902 | 122.5845 | 60.9833 | -0.10529 | 122.5433 | -0.11902 | 60.9833 | 122.6624 | 122.5845 | -122.7493 | -122.8134
55.9844 | 123.0652 | -60.8414 | 61.8942 | 0.17548 | 0.01474 | 0.016022 | 0.00235 | 0.062591 | -0.0038452 | 0.072845 | -60.9924 | 61.7523 | -60.8322 | -61.0428 | 61.7844 | 0.07782 | -0.041199 | 0.027466 | 61.7432 | -60.9329 | 0.009156 | -0.14191 | -0.15106 | -0.20142 | -0.10986 | -0.091552 | -0.15106 | -0.16022 | 60.8002 | 60.8688 | 122.6257 | 122.5937 | -0.15106 | 122.5845 | 60.9192 | -0.091552 | 122.5937 | -0.15106 | 60.9192 | 122.6257 | 122.5845 | -122.7264 | -122.8271
57.0312 | 123.0881 | -60.8093 | 61.9125 | 0.13733 | 0.014313 | 0.015381 | 0.001709 | 0.059601 | -0.0021362 | 0.072205 | -60.965 | 61.7706 | -60.8414 | -60.9879 | 61.8118 | 0.14648 | -0.054932 | 0.068665 | 61.7477 | -60.9375 | -0.032044 | -0.14191 | -0.15564 | -0.17853 | -0.10071 | -0.12817 | -0.16479 | -0.1236 | 60.7544 | 60.878 | 122.6212 | 122.58 | -0.15564 | 122.5571 | 60.9558 | -0.12817 | 122.58 | -0.15564 | 60.9558 | 122.6212 | 122.5571 | -122.7539 | -122.85
57.9844 | 123.111 | -60.7956 | 61.8851 | 0.39673 | 0.016449 | 0.016235 | 0.0044862 | 0.062591 | -0.0014954 | 0.069 | -60.9421 | 61.7661 | -60.8551 | -60.9924 | 61.8027 | 0.086975 | -0.15106 | 0.018311 | 61.7249 | -60.9512 | -0.05951 | -0.11902 | -0.14649 | -0.19684 | -0.082398 | -0.15564 | -0.16022 | -0.086975 | 60.6445 | 60.8139 | 122.5983 | 122.5616 | -0.14649 | 122.5204 | 60.8826 | -0.15564 | 122.5616 | -0.14649 | 60.8826 | 122.5983 | 122.5204 | -122.7402 | -122.8363
59.0312 | 123.1338 | -60.8093 | 61.9034 | 0.045776 | 0.015808 | 0.016449 | 0.0025636 | 0.063232 | -0.0040588 | 0.069855 | -60.8917 | 61.7935 | -60.8047 | -60.9695 | 61.8668 | 0.18768 | -0.022888 | 0.17395 | 61.7523 | -60.9329 | 0.004577 | -0.10986 | -0.082398 | -0.16022 | -0.036621 | -0.1236 | -0.15106 | -0.086975 | 60.7864 | 60.9833 | 122.6761 | 122.6028 | -0.082398 | 122.5616 | 60.997 | -0.1236 | 122.6028 | -0.082398 | 60.997 | 122.6761 | 122.5616 | -122.7081 | -122.8363
59.9844 | 123.056 | -60.8231 | 61.9171 | 0.19836 | 0.013886 | 0.013245 | 0.001709 | 0.062164 | -0.002777 | 0.072418 | -61.0062 | 61.7523 | -60.8688 | -61.0565 | 61.7798 | 0.073242 | -0.032043 | 0.027466 | 61.7569 | -60.9192 | -0.045776 | -0.16479 | -0.18311 | -0.23346 | -0.13733 | -0.09613 | -0.16022 | -0.13733 | 60.791 | 60.8505 | 122.6028 | 122.5754 | -0.18311 | 122.58 | 60.8963 | -0.09613 | 122.5754 | -0.18311 | 60.8963 | 122.6028 | 122.58 | -122.7859 | -122.8363
60.9844 | 123.0743 | -60.8597 | 61.9125 | 0.21362 | 0.014313 | 0.014954 | 0.000641 | 0.061737 | -0.0038452 | 0.069855 | -60.9833 | 61.7661 | -60.878 | -61.0382 | 61.7706 | 0.07782 | -0.041199 | 0.013733 | 61.7615 | -60.9467 | -0.018311 | -0.14648 | -0.1236 | -0.17853 | -0.14191 | -0.086975 | -0.15106 | -0.10528 | 60.8185 | 60.8734 | 122.6303 | 122.6257 | -0.1236 | 122.6212 | 60.9375 | -0.086975 | 122.6257 | -0.1236 | 60.9375 | 122.6303 | 122.6212 | -122.7905 | -122.8592
62.0312 | 123.1293 | -60.7956 | 61.9308 | 0.022888 | 0.015595 | 0.016663 | 0.005127 | 0.060882 | -0.0049134 | 0.070709 | -60.9146 | 61.7569 | -60.8231 | -60.9421 | 61.8713 | 0.17395 | -0.027466 | 0.15564 | 61.7569 | -60.9329 | -0.027466 | -0.17395 | -0.11902 | -0.14649 | -0.059509 | -0.13733 | -0.17395 | -0.091553 | 60.7681 | 60.9512 | 122.6669 | 122.5525 | -0.11902 | 122.5525 | 60.9695 | -0.13733 | 122.5525 | -0.11902 | 60.9695 | 122.6669 | 122.5525 | -122.7539 | -122.8638
62.9844 | 123.0469 | -60.8414 | 61.9171 | 0.20599 | 0.014526 | 0.015167 | 0.0014954 | 0.062164 | -0.003418 | 0.067718 | -60.997 | 61.7752 | -60.8551 | -61.0245 | 61.7935 | 0.086975 | -0.036621 | 0.045776 | 61.7477 | -60.9512 | -0.013733 | -0.14191 | -0.15564 | -0.18311 | -0.1236 | -0.10986 | -0.16937 | -0.14191 | 60.8047 | 60.8871 | 122.6349 | 122.6166 | -0.15564 | 122.5891 | 60.9283 | -0.10986 | 122.6166 | -0.15564 | 60.9283 | 122.6349 | 122.5891 | -122.7722 | -122.8683
64.0469 | 123.0011 | -60.8551 | 61.9629 | 0.22888 | 0.015381 | 0.01474 | 0.0079042 | 0.063019 | -0.0046996 | 0.071777 | -60.9467 | 61.8347 | -60.8505 | -61.0519 | 61.734 | 0.032043 | 0.027466 | -0.027466 | 61.7935 | -60.9833 | 0.004578 | -0.12817 | -0.091552 | -0.19684 | -0.22888 | -0.12817 | -0.16937 | -0.09613 | 60.8826 | 60.8276 | 122.5891 | 122.6898 | -0.091552 | 122.6486 | 60.8871 | -0.12817 | 122.6898 | -0.091552 | 60.8871 | 122.5891 | 122.6486 | -122.8134 | -122.9462
64.9844 | 123.143 | -60.8002 | 61.8805 | 0.19836 | 0.013886 | 0.015595 | 0.0027772 | 0.063873 | -0.005127 | 0.072845 | -60.9192 | 61.7615 | -60.8368 | -60.9604 | 61.8393 | 0.16022 | -0.064087 | 0.13275 | 61.7889 | -60.91 | -0.036621 | -0.11902 | -0.11902 | -0.16022 | -0.041199 | -0.10986 | -0.091553 | -0.082397 | 60.7361 | 60.9329 | 122.6395 | 122.5616 | -0.11902 | 122.5891 | 60.9604 | -0.10986 | 122.5616 | -0.11902 | 60.9604 | 122.6395 | 122.5891 | -122.7173 | -122.7905
66.0156 | 122.9919 | -60.8414 | 61.9171 | 0.18311 | 0.016235 | 0.015808 | 0.0096132 | 0.060242 | -0.0042724 | 0.071564 | -60.9787 | 61.8301 | -60.9055 | -61.0657 | 61.7432 | 0.009155 | 0.022888 | -0.041199 | 61.7706 | -60.9695 | -0.064087 | -0.086975 | -0.13733 | -0.2243 | -0.17395 | -0.12817 | -0.14648 | -0.073242 | 60.8643 | 60.8002 | 122.5845 | 122.6715 | -0.13733 | 122.612 | 60.8505 | -0.12817 | 122.6715 | -0.13733 | 60.8505 | 122.5845 | 122.612 | -122.8226 | -122.8867
66.9844 | 123.0743 | -60.8185 | 61.8988 | 0.35095 | 0.015808 | 0.016235 | 0.005127 | 0.065796 | -0.005127 | 0.071991 | -60.9467 | 61.7706 | -60.8688 | -61.0016 | 61.7752 | 0.059509 | -0.15106 | 0.004578 | 61.702 | -60.965 | -0.050354 | -0.12817 | -0.12817 | -0.18311 | -0.1236 | -0.14648 | -0.19684 | -0.07782 | 60.6674 | 60.8231 | 122.5937 | 122.5891 | -0.12817 | 122.5204 | 60.878 | -0.14648 | 122.5891 | -0.12817 | 60.878 | 122.5937 | 122.5204 | -122.7676 | -122.8638
68.0156 | 123.0148 | -60.8459 | 61.9308 | 0.16022 | 0.015808 | 0.01709 | 0.0079042 | 0.063873 | -0.0057678 | 0.072205 | -60.9558 | 61.8118 | -60.8597 | -61.0245 | 61.7615 | 0.064087 | 0.041199 | 0.009155 | 61.8164 | -60.9833 | -0.013733 | -0.11902 | -0.10986 | -0.17853 | -0.16937 | -0.13733 | -0.11444 | -0.096131 | 60.8871 | 60.8551 | 122.6074 | 122.6578 | -0.10986 | 122.6624 | 60.91 | -0.13733 | 122.6578 | -0.10986 | 60.91 | 122.6074 | 122.6624 | -122.7905 | -122.9141
68.9844 | 122.9874 | -60.8734 | 61.94 | 0.2594 | 0.016235 | 0.016022 | 0.006836 | 0.065582 | -0.004486 | 0.070068 | -61.0062 | 61.8622 | -60.8597 | -61.0886 | 61.7203 | 0.009155 | 0.059509 | -0.07782 | 61.7981 | -60.9879 | 0.013733 | -0.077819 | -0.13275 | -0.21515 | -0.21973 | -0.11444 | -0.14191 | -0.14649 | 60.9329 | 60.7956 | 122.5937 | 122.7356 | -0.13275 | 122.6715 | 60.8826 | -0.11444 | 122.7356 | -0.13275 | 60.8826 | 122.5937 | 122.6715 | -122.7997 | -122.9279
70.0312 | 123.0652 | -60.8231 | 61.9263 | 0.022888 | 0.01474 | 0.018585 | 0.0019226 | 0.0643 | -0.0049134 | 0.070709 | -60.9375 | 61.7981 | -60.8414 | -60.9741 | 61.8576 | 0.17395 | 0.045776 | 0.13733 | 61.8164 | -60.91 | -0.018311 | -0.12817 | -0.11444 | -0.15106 | -0.068665 | -0.086975 | -0.10986 | -0.09613 | 60.8688 | 60.9604 | 122.6807 | 122.6212 | -0.11444 | 122.6395 | 60.997 | -0.086975 | 122.6212 | -0.11444 | 60.997 | 122.6807 | 122.6395 | -122.7676 | -122.8363
70.9844 | 123.1155 | -60.8414 | 61.8896 | 0.41199 | 0.013886 | 0.015808 | 0.0012818 | 0.066437 | -0.0055542 | 0.072845 | -60.9238 | 61.7569 | -60.8505 | -61.0016 | 61.8118 | 0.07782 | -0.16022 | 0.032043 | 61.7523 | -60.9329 | -0.009155 | -0.13275 | -0.082397 | -0.16022 | -0.077819 | -0.091552 | -0.13733 | -0.073242 | 60.6812 | 60.8734 | 122.6532 | 122.5983 | -0.082397 | 122.5937 | 60.9192 | -0.091552 | 122.5983 | -0.082397 | 60.9192 | 122.6532 | 122.5937 | -122.7402 | -122.8226
71.9844 | 123.0789 | -60.8459 | 61.8668 | 0.38147 | 0.016235 | 0.015595 | 0.0012818 | 0.064514 | -0.004486 | 0.071564 | -60.9421 | 61.7432 | -60.8551 | -61.0199 | 61.8027 | 0.082397 | -0.14191 | 0.041199 | 61.7615 | -60.9512 | -0.009156 | -0.1236 | -0.096131 | -0.17395 | -0.064087 | -0.10529 | -0.10529 | -0.086975 | 60.704 | 60.8871 | 122.6486 | 122.5891 | -0.096131 | 122.6074 | 60.9283 | -0.10529 | 122.5891 | -0.096131 | 60.9283 | 122.6486 | 122.6074 | -122.7219 | -122.818
73.0312 | 123.1384 | -60.8231 | 61.908 | 0.022888 | 0.015808 | 0.014099 | 0.0010682 | 0.061096 | -0.0046996 | 0.069855 | -60.9512 | 61.7569 | -60.8368 | -60.9787 | 61.8439 | 0.16937 | -0.064087 | 0.11902 | 61.7523 | -60.9238 | -0.013733 | -0.15106 | -0.12817 | -0.15564 | -0.064087 | -0.10071 | -0.15564 | -0.11444 | 60.759 | 60.9421 | 122.6669 | 122.58 | -0.12817 | 122.5754 | 60.9924 | -0.10071 | 122.58 | -0.12817 | 60.9924 | 122.6669 | 122.5754 | -122.7448 | -122.8317
73.9844 | 123.1201 | -60.8322 | 61.9263 | 0.13733 | 0.015808 | 0.012817 | 0.0032044 | 0.063446 | -0.0021362 | 0.069214 | -60.8871 | 61.7981 | -60.8002 | -60.9238 | 61.8759 | 0.1831 | -0.022888 | 0.16022 | 61.7569 | -60.9558 | 0.032043 | -0.12817 | -0.054932 | -0.091553 | -0.050354 | -0.1236 | -0.16937 | -0.086975 | 60.8093 | 60.9924 | 122.7081 | 122.6303 | -0.054932 | 122.5891 | 61.0153 | -0.1236 | 122.6303 | -0.054932 | 61.0153 | 122.7081 | 122.5891 | -122.7264 | -122.8821
75.0156 | 123.0057 | -60.8322 | 61.9492 | 0.068664 | 0.015808 | 0.014954 | 0.0089722 | 0.06366 | -0.0036316 | 0.073273 | -60.9329 | 61.8347 | -60.8459 | -61.0291 | 61.7752 | 0.082397 | 0.059509 | 0.041199 | 61.8256 | -60.9558 | -0.013733 | -0.11444 | -0.10071 | -0.19684 | -0.17395 | -0.1236 | -0.1236 | -0.086975 | 60.8917 | 60.8734 | 122.6074 | 122.6669 | -0.10071 | 122.6578 | 60.9146 | -0.1236 | 122.6669 | -0.10071 | 60.9146 | 122.6074 | 122.6578 | -122.7951 | -122.905
75.9844 | 123.0789 | -60.8414 | 61.9034 | 0.3891 | 0.016449 | 0.01239 | 0.0044862 | 0.06366 | -0.0036316 | 0.071564 | -60.9375 | 61.7844 | -60.8643 | -61.0245 | 61.7981 | 0.086975 | -0.15564 | 0.045776 | 61.7661 | -60.9604 | -0.022888 | -0.11902 | -0.09613 | -0.18311 | -0.10529 | -0.11902 | -0.13733 | -0.073242 | 60.6857 | 60.8871 | 122.6395 | 122.6257 | -0.09613 | 122.6074 | 60.9283 | -0.11902 | 122.6257 | -0.09613 | 60.9283 | 122.6395 | 122.6074 | -122.7676 | -122.8638
77.0312 | 122.9965 | -60.8871 | 61.908 | 0.35095 | 0.018372 | 0.016235 | 0.0064088 | 0.063873 | -0.0032044 | 0.071777 | -61.0245 | 61.8073 | -60.9192 | -61.1023 | 61.6974 | -0.027466 | -0.018311 | -0.086975 | 61.7935 | -60.9833 | -0.032043 | -0.10071 | -0.13733 | -0.21515 | -0.21057 | -0.09613 | -0.11444 | -0.10529 | 60.8688 | 60.8002 | 122.5845 | 122.6944 | -0.13733 | 122.6807 | 60.8597 | -0.09613 | 122.6944 | -0.13733 | 60.8597 | 122.5845 | 122.6807 | -122.8271 | -122.8912
77.9844 | 123.0286 | -60.8414 | 61.8942 | 0.4425 | 0.014954 | 0.014526 | 0.000641 | 0.064087 | -0.0040588 | 0.072205 | -60.9741 | 61.7477 | -60.878 | -61.0657 | 61.7798 | 0.050354 | -0.086975 | -0.004578 | 61.7798 | -60.9604 | -0.036621 | -0.14648 | -0.13275 | -0.2243 | -0.11444 | -0.11902 | -0.11444 | -0.09613 | 60.7544 | 60.8368 | 122.6212 | 122.5891 | -0.13275 | 122.6212 | 60.8917 | -0.11902 | 122.5891 | -0.13275 | 60.8917 | 122.6212 | 122.6212 | -122.7722 | -122.8546
79.0312 | 123.1018 | -60.8414 | 61.8988 | 0.45013 | 0.017304 | 0.018585 | 0.0064088 | 0.064728 | -0.0038452 | 0.069855 | -60.9558 | 61.8256 | -60.8551 | -61.0062 | 61.7935 | 0.054932 | -0.14191 | 0 | 61.7523 | -60.9879 | -0.013733 | -0.073242 | -0.11444 | -0.1648 | -0.10529 | -0.14648 | -0.14648 | -0.10071 | 60.6995 | 60.8414 | 122.6349 | 122.6669 | -0.11444 | 122.5937 | 60.8963 | -0.14648 | 122.6669 | -0.11444 | 60.8963 | 122.6349 | 122.5937 | -122.7539 | -122.8867
79.9844 | 123.0606 | -60.8643 | 61.8759 | 0.67139 | 0.018372 | 0.018372 | 0.0042726 | 0.064728 | -0.0002136 | 0.071777 | -61.0153 | 61.8347 | -60.8643 | -61.0565 | 61.7661 | 0.018311 | -0.11444 | -0.054932 | 61.7432 | -60.9741 | 0 | -0.041199 | -0.15106 | -0.19226 | -0.10986 | -0.10986 | -0.13275 | -0.15106 | 60.7498 | 60.8093 | 122.6303 | 122.699 | -0.15106 | 122.6074 | 60.8826 | -0.10986 | 122.699 | -0.15106 | 60.8826 | 122.6303 | 122.6074 | -122.7402 | -122.85
81.0312 | 122.9645 | -60.8917 | 61.9263 | 0.40436 | 0.016876 | 0.014954 | 0.0064088 | 0.066437 | -0.0004272 | 0.073059 | -61.0062 | 61.8073 | -60.8826 | -61.0428 | 61.8027 | -0.086975 | -0.10529 | 0.086975 | 61.7661 | -60.9924 | 0.009156 | -0.11902 | -0.11444 | -0.15106 | -0.1236 | -0.10071 | -0.16022 | -0.1236 | 60.7864 | 60.9787 | 122.6944 | 122.699 | -0.11444 | 122.6578 | 60.8047 | -0.10071 | 122.699 | -0.11444 | 60.8047 | 122.6944 | 122.6578 | -122.8088 | -122.9187
81.9844 | 122.9874 | -60.878 | 61.908 | -0.80109 | 0.013458 | 0.017731 | 0.008545 | 0.066437 | -0.002777 | 0.070282 | -60.91 | 61.8668 | -60.8643 | -61.1023 | 61.734 | 0.027466 | 0.050354 | -0.045776 | 61.7935 | -60.9924 | 0.013733 | -0.041199 | -0.032043 | -0.2243 | -0.17395 | -0.11444 | -0.11444 | -0.045776 | 60.9283 | 60.8322 | 122.612 | 122.7448 | -0.032043 | 122.6715 | 60.9055 | -0.11444 | 122.7448 | -0.032043 | 60.9055 | 122.612 | 122.6715 | -122.7722 | -122.9004
83.0156 | 122.9645 | -60.8368 | 61.94 | -0.0076295 | 0.015808 | 0.013672 | 0.0032044 | 0.062591 | -0.0023498 | 0.071136 | -60.997 | 61.8851 | -60.878 | -61.0703 | 61.7477 | 0.07782 | 0.16937 | 0.032043 | 61.8347 | -60.9604 | -0.041199 | -0.054931 | -0.16022 | -0.23346 | -0.19226 | -0.1236 | -0.10529 | -0.11902 | 61.0062 | 60.8688 | 122.5845 | 122.7219 | -0.16022 | 122.6715 | 60.9146 | -0.1236 | 122.7219 | -0.16022 | 60.9146 | 122.5845 | 122.6715 | -122.818 | -122.9004
83.9688 | 123.0606 | -60.8597 | 61.8988 | 0.26703 | 0.015808 | 0.015381 | 0.0004274 | 0.065155 | -0.0021362 | 0.070496 | -60.9741 | 61.8073 | -60.8459 | -61.0428 | 61.7615 | 0.064087 | -0.022888 | 0.018311 | 61.7935 | -60.9421 | 0.013733 | -0.091553 | -0.11444 | -0.18311 | -0.13733 | -0.082398 | -0.10529 | -0.12817 | 60.8368 | 60.878 | 122.6212 | 122.6669 | -0.11444 | 122.6532 | 60.9238 | -0.082398 | 122.6669 | -0.11444 | 60.9238 | 122.6212 | 122.6532 | -122.7448 | -122.8409
85.0312 | 122.9645 | -60.8917 | 61.9446 | 0.21362 | 0.017944 | 0.017731 | 0.0083314 | 0.066009 | -0.0029906 | 0.072418 | -60.9924 | 61.8668 | -60.8917 | -61.1206 | 61.6791 | -0.036621 | 0.059509 | -0.10529 | 61.8393 | -61.0062 | 0 | -0.07782 | -0.10071 | -0.22888 | -0.2655 | -0.11444 | -0.10529 | -0.10071 | 60.9512 | 60.7864 | 122.5708 | 122.7585 | -0.10071 | 122.731 | 60.8551 | -0.11444 | 122.7585 | -0.10071 | 60.8551 | 122.5708 | 122.731 | -122.8363 | -122.9507
85.9844 | 122.9874 | -60.8871 | 61.9629 | 0.19836 | 0.016449 | 0.016663 | 0.0053406 | 0.065796 | -0.002777 | 0.071564 | -60.9512 | 61.853 | -60.8734 | -61.0428 | 61.7569 | 0.11444 | -0.3479 | -0.22888 | 61.7706 | -61.0062 | 0.013733 | -0.10986 | -0.064087 | -0.15564 | -0.20599 | -0.11902 | -0.19226 | -0.07782 | 60.5392 | 60.6583 | 122.644 | 122.7402 | -0.064087 | 122.6578 | 61.0016 | -0.11902 | 122.7402 | -0.064087 | 61.0016 | 122.644 | 122.6578 | -122.8363 | -122.9691
87.0156 | 123.0789 | -60.8231 | 61.94 | 0 | 0.012604 | 0.01239 | 0.0002136 | 0.063873 | -0.0032044 | 0.07135 | -60.9283 | 61.8301 | -60.8231 | -60.9741 | 61.8576 | 0.16479 | 0.041199 | 0.10529 | 61.8347 | -60.9467 | 0 | -0.10986 | -0.10529 | -0.15106 | -0.082397 | -0.1236 | -0.10529 | -0.10529 | 60.8643 | 60.9283 | 122.6807 | 122.6532 | -0.10529 | 122.6578 | 60.9879 | -0.1236 | 122.6532 | -0.10529 | 60.9879 | 122.6807 | 122.6578 | -122.7631 | -122.8867
87.9844 | 122.9736 | -60.8826 | 61.9354 | 0.33569 | 0.017304 | 0.018585 | 0.0074768 | 0.066223 | -0.0055542 | 0.070923 | -60.9924 | 61.8668 | -60.878 | -61.1023 | 61.7065 | -0.004578 | 0.050354 | -0.091553 | 61.8439 | -60.9695 | 0.004577 | -0.068665 | -0.10986 | -0.21973 | -0.22888 | -0.086975 | -0.091553 | -0.11444 | 60.9329 | 60.791 | 122.5891 | 122.7493 | -0.10986 | 122.7264 | 60.878 | -0.086975 | 122.7493 | -0.10986 | 60.878 | 122.5891 | 122.7264 | -122.8134 | -122.905
89.0312 | 123.0148 | -60.8917 | 61.9217 | 0.35858 | 0.018158 | 0.017517 | 0.0029908 | 0.067718 | -0.002777 | 0.071777 | -61.0291 | 61.8484 | -60.9009 | -61.116 | 61.7111 | -0.018311 | -0.018311 | -0.09613 | 61.8118 | -60.9879 | -0.009155 | -0.073242 | -0.13733 | -0.2243 | -0.21057 | -0.09613 | -0.10986 | -0.12817 | 60.8734 | 60.7956 | 122.6028 | 122.7402 | -0.13733 | 122.7036 | 60.8734 | -0.09613 | 122.7402 | -0.13733 | 60.8734 | 122.6028 | 122.7036 | -122.8226 | -122.9095
89.9844 | 123.0286 | -60.8551 | 61.908 | 0.26703 | 0.015167 | 0.017944 | -0.0014952 | 0.063232 | -0.0025634 | 0.073914 | -60.9924 | 61.8073 | -60.8826 | -61.0611 | 61.7615 | 0.064087 | -0.041199 | 0.013733 | 61.7798 | -60.9741 | -0.027465 | -0.10071 | -0.13733 | -0.20599 | -0.14648 | -0.11902 | -0.12817 | -0.10986 | 60.8139 | 60.8688 | 122.6166 | 122.6624 | -0.13733 | 122.6349 | 60.9192 | -0.11902 | 122.6624 | -0.13733 | 60.9192 | 122.6166 | 122.6349 | -122.7905 | -122.8821
91.0312 | 123.0011 | -60.8414 | 61.9492 | 0.16785 | 0.015167 | 0.015808 | 0.0076904 | 0.065582 | -0.0040588 | 0.072845 | -60.9512 | 61.8484 | -60.8734 | -61.0153 | 61.7798 | 0.091553 | 0.050354 | 0.041199 | 61.8073 | -60.9695 | -0.032043 | -0.10071 | -0.10986 | -0.17395 | -0.16937 | -0.12817 | -0.14191 | -0.07782 | 60.8917 | 60.8826 | 122.6212 | 122.6898 | -0.10986 | 122.6486 | 60.9329 | -0.12817 | 122.6898 | -0.10986 | 60.9329 | 122.6212 | 122.6486 | -122.8226 | -122.9187
91.9844 | 122.9919 | -60.878 | 61.9354 | 0.28992 | 0.014954 | 0.015381 | 0.0064088 | 0.067718 | -0.0023498 | 0.072845 | -61.0107 | 61.8484 | -60.9009 | -61.0977 | 61.7203 | -0.013733 | 0.068665 | -0.054932 | 61.821 | -60.997 | -0.022888 | -0.086975 | -0.13275 | -0.21973 | -0.21515 | -0.11902 | -0.11444 | -0.10986 | 60.9467 | 60.8231 | 122.5983 | 122.7264 | -0.13275 | 122.699 | 60.8643 | -0.11902 | 122.7264 | -0.13275 | 60.8643 | 122.5983 | 122.699 | -122.8363 | -122.9324
93.0312 | 123.0789 | -60.8093 | 61.9171 | 0.038147 | 0.014526 | 0.01709 | -0.001068 | 0.0643 | -0.0032044 | 0.069855 | -60.9238 | 61.8164 | -60.8093 | -60.9833 | 61.8393 | 0.17853 | 0.018311 | 0.14191 | 61.8301 | -60.9329 | 0 | -0.10071 | -0.11444 | -0.17395 | -0.07782 | -0.1236 | -0.086975 | -0.11444 | 60.8276 | 60.9512 | 122.6486 | 122.6257 | -0.11444 | 122.6395 | 60.9879 | -0.1236 | 122.6257 | -0.11444 | 60.9879 | 122.6486 | 122.6395 | -122.7264 | -122.85
93.9844 | 122.937 | -60.8826 | 61.9217 | 0.26703 | 0.015167 | 0.017304 | 0.0074768 | 0.066437 | -0.004486 | 0.07135 | -60.9924 | 61.853 | -60.878 | -61.1023 | 61.702 | -0.009155 | 0.068665 | -0.086975 | 61.8347 | -60.9879 | 0.004577 | -0.068665 | -0.10986 | -0.21973 | -0.21973 | -0.10529 | -0.086975 | -0.11444 | 60.9512 | 60.7956 | 122.5845 | 122.7356 | -0.10986 | 122.7173 | 60.8734 | -0.10529 | 122.7356 | -0.10986 | 60.8734 | 122.5845 | 122.7173 | -122.7997 | -122.9095
95.0156 | 123.056 | -60.8551 | 61.9217 | -1.9684 | 0.016022 | 0.016663 | -0.0019226 | 0.0643 | -0.002777 | 0.07135 | -61.0657 | 61.8118 | -60.8368 | -61.0886 | 61.7569 | 0.041199 | -0.041199 | 0 | 61.7798 | -60.9329 | 0.018311 | -0.10986 | -0.21057 | -0.23346 | -0.16479 | -0.077819 | -0.14191 | -0.22888 | 60.8139 | 60.8551 | 122.612 | 122.6669 | -0.21057 | 122.6349 | 60.8963 | -0.077819 | 122.6669 | -0.21057 | 60.8963 | 122.612 | 122.6349 | -122.7585 | -122.8546
95.9844 | 122.9828 | -60.8734 | 61.94 | 0.26703 | 0.01474 | 0.013672 | 0.0076904 | 0.06665 | -0.003418 | 0.072205 | -60.9741 | 61.8393 | -60.8917 | -61.0794 | 61.7111 | 0.018311 | 0.036621 | -0.050354 | 61.8073 | -60.9879 | -0.018311 | -0.10071 | -0.10071 | -0.20599 | -0.22888 | -0.11444 | -0.13275 | -0.082397 | 60.91 | 60.8231 | 122.5845 | 122.7127 | -0.10071 | 122.6807 | 60.8917 | -0.11444 | 122.7127 | -0.10071 | 60.8917 | 122.5845 | 122.6807 | -122.8317 | -122.9279
97.0156 | 123.0698 | -60.8368 | 61.908 | 0.16022 | 0.015808 | 0.013458 | 0 | 0.064087 | -0.003418 | 0.069641 | -60.9467 | 61.7844 | -60.8322 | -61.0107 | 61.8118 | 0.11902 | -0.054932 | 0.11902 | 61.7981 | -60.9238 | 0.004578 | -0.1236 | -0.10986 | -0.17395 | -0.09613 | -0.086975 | -0.10986 | -0.11444 | 60.7819 | 60.9558 | 122.6486 | 122.6212 | -0.10986 | 122.6349 | 60.9558 | -0.086975 | 122.6212 | -0.10986 | 60.9558 | 122.6486 | 122.6349 | -122.7402 | -122.8317
97.9844 | 122.9919 | -60.8871 | 61.9492 | 0.32043 | 0.014954 | 0.018372 | 0.013458 | 0.066009 | -0.0029906 | 0.069855 | -61.0428 | 61.8576 | -60.8643 | -61.0153 | 61.7065 | -0.009155 | 0.004578 | -0.10071 | 61.8393 | -60.997 | 0.022888 | -0.091553 | -0.15564 | -0.12817 | -0.24261 | -0.10986 | -0.10986 | -0.17853 | 60.8917 | 60.7864 | 122.5937 | 122.7448 | -0.15564 | 122.7264 | 60.878 | -0.10986 | 122.7448 | -0.15564 | 60.878 | 122.5937 | 122.7264 | -122.8134 | -122.9462
99.0312 | 123.0881 | -60.8231 | 61.94 | 0.045776 | 0.013886 | 0.01239 | 0.000641 | 0.064941 | -0.0059814 | 0.070068 | -60.91 | 61.8027 | -60.8643 | -60.9833 | 61.8301 | 0.16937 | 0.036621 | 0.14648 | 61.8118 | -60.9192 | -0.041199 | -0.13733 | -0.086975 | -0.16022 | -0.10986 | -0.09613 | -0.12817 | -0.045776 | 60.8597 | 60.9695 | 122.6532 | 122.6257 | -0.086975 | 122.6349 | 60.9924 | -0.09613 | 122.6257 | -0.086975 | 60.9924 | 122.6532 | 122.6349 | -122.8043 | -122.8592
99.9844 | 123.0194 | -60.878 | 61.9217 | 0.19836 | 0.01474 | 0.01944 | 0.0055542 | 0.063446 | -0.0042724 | 0.073914 | -60.965 | 61.7844 | -60.8917 | -61.0748 | 61.7203 | 0.036621 | 0.036621 | -0.027466 | 61.8118 | -60.965 | -0.013733 | -0.13733 | -0.086975 | -0.19684 | -0.20142 | -0.086975 | -0.10986 | -0.073242 | 60.9146 | 60.8505 | 122.5983 | 122.6624 | -0.086975 | 122.6898 | 60.9146 | -0.086975 | 122.6624 | -0.086975 | 60.9146 | 122.5983 | 122.6898 | -122.8134 | -122.8867
101.0312 | 123.0652 | -60.791 | 61.908 | 0.79346 | 0.014099 | 0.013031 | -0.0014952 | 0.065369 | -0.0042724 | 0.071136 | -60.878 | 61.7615 | -60.8597 | -60.9604 | 61.853 | 0.17853 | -0.018311 | 0.15564 | 61.8256 | -60.9283 | -0.068664 | -0.14648 | -0.086975 | -0.16937 | -0.054932 | -0.13733 | -0.082397 | -0.018311 | 60.7727 | 60.9467 | 122.644 | 122.5525 | -0.086975 | 122.6166 | 60.9695 | -0.13733 | 122.5525 | -0.086975 | 60.9695 | 122.644 | 122.6166 | -122.7676 | -122.8363
101.9844 | 122.937 | -60.8734 | 61.9217 | 0.28992 | 0.015167 | 0.015808 | 0.0072632 | 0.066223 | -0.0057678 | 0.071991 | -61.0245 | 61.8118 | -60.8871 | -61.1618 | 61.6562 | -0.032043 | 0.032043 | -0.09613 | 61.8256 | -60.9833 | -0.013733 | -0.10986 | -0.15106 | -0.28839 | -0.2655 | -0.10986 | -0.09613 | -0.13733 | 60.9055 | 60.7773 | 122.5296 | 122.6852 | -0.15106 | 122.699 | 60.8414 | -0.10986 | 122.6852 | -0.15106 | 60.8414 | 122.5296 | 122.699 | -122.8088 | -122.905
103.0312 | 123.0698 | -60.8231 | 61.8988 | 0.39673 | 0.013672 | 0.016663 | -0.0014952 | 0.064087 | -0.0029906 | 0.072205 | -60.9604 | 61.7798 | -60.8597 | -61.0474 | 61.7661 | 0.064087 | -0.10986 | 0 | 61.7844 | -60.965 | -0.036621 | -0.11902 | -0.13733 | -0.2243 | -0.13275 | -0.14191 | -0.11444 | -0.10071 | 60.7132 | 60.8231 | 122.5891 | 122.6028 | -0.13733 | 122.6074 | 60.8871 | -0.14191 | 122.6028 | -0.13733 | 60.8871 | 122.5891 | 122.6074 | -122.7585 | -122.8638
103.9844 | 122.9919 | -60.8368 | 61.94 | 0.16785 | 0.01709 | 0.015595 | 0.0087586 | 0.063873 | -0.0055542 | 0.072845 | -60.9512 | 61.8073 | -60.8826 | -61.0474 | 61.7569 | 0.064087 | 0.050354 | 0.004578 | 61.8118 | -60.9695 | -0.045776 | -0.13275 | -0.11444 | -0.21057 | -0.1831 | -0.13275 | -0.12817 | -0.068665 | 60.8871 | 60.8414 | 122.5937 | 122.644 | -0.11444 | 122.6486 | 60.9009 | -0.13275 | 122.644 | -0.11444 | 60.9009 | 122.5937 | 122.6486 | -122.8226 | -122.9095
104.9688 | 123.0835 | -60.8459 | 61.8896 | 0.21362 | 0.013886 | 0.015595 | 0.0027772 | 0.065796 | -0.0059814 | 0.070923 | -60.9421 | 61.7432 | -60.8276 | -60.997 | 61.8073 | 0.073242 | -0.15106 | 0.027466 | 61.7752 | -60.9421 | 0.01831 | -0.14648 | -0.096131 | -0.15106 | -0.082397 | -0.096131 | -0.11444 | -0.11444 | 60.6949 | 60.8734 | 122.6532 | 122.5891 | -0.096131 | 122.6212 | 60.9192 | -0.096131 | 122.5891 | -0.096131 | 60.9192 | 122.6532 | 122.6212 | -122.7173 | -122.8317
106.0312 | 122.9553 | -60.8597 | 61.9354 | 0.030518 | 0.01474 | 0.015595 | 0.004059 | 0.064514 | -0.0021362 | 0.071564 | -60.997 | 61.8576 | -60.8688 | -61.0794 | 61.734 | 0.050354 | 0.14191 | 0.009155 | 61.8301 | -60.9375 | -0.009155 | -0.07782 | -0.13733 | -0.21973 | -0.20142 | -0.07782 | -0.10529 | -0.12817 | 61.0016 | 60.8688 | 122.5937 | 122.7173 | -0.13733 | 122.6898 | 60.91 | -0.07782 | 122.7173 | -0.13733 | 60.91 | 122.5937 | 122.6898 | -122.8043 | -122.8729
106.9688 | 122.9279 | -60.8551 | 61.9217 | 0.32043 | 0.016022 | 0.016449 | 0.0061952 | 0.065369 | -0.0055542 | 0.07135 | -61.0474 | 61.8164 | -60.9146 | -61.1618 | 61.6745 | -0.036621 | 0.032043 | -0.10071 | 61.8439 | -60.9741 | -0.059509 | -0.10529 | -0.19226 | -0.3067 | -0.24719 | -0.11902 | -0.07782 | -0.13275 | 60.8871 | 60.7544 | 122.5296 | 122.6715 | -0.19226 | 122.699 | 60.8185 | -0.11902 | 122.6715 | -0.19226 | 60.8185 | 122.5296 | 122.699 | -122.8363 | -122.8958
108.0312 | 122.9919 | -60.8597 | 61.9675 | 0.030518 | 0.012604 | 0.01239 | 0.0029908 | 0.063019 | -0.0053406 | 0.071991 | -60.9879 | 61.8301 | -60.8643 | -61.0657 | 61.7432 | 0.07782 | 0.14648 | 0.032043 | 61.8439 | -60.9512 | -0.004578 | -0.13733 | -0.12817 | -0.20599 | -0.2243 | -0.091553 | -0.1236 | -0.1236 | 61.0062 | 60.8917 | 122.6028 | 122.6898 | -0.12817 | 122.7036 | 60.9375 | -0.091553 | 122.6898 | -0.12817 | 60.9375 | 122.6028 | 122.7036 | -122.8317 | -122.9187
108.9688 | 123.0331 | -60.8414 | 61.9446 | 0.17548 | 0.013458 | 0.016876 | 0.0038452 | 0.065155 | -0.0046996 | 0.072845 | -60.9604 | 61.8164 | -60.8643 | -61.0428 | 61.7706 | -0.13733 | 0.10986 | 0.082397 | 61.8118 | -60.9467 | -0.022888 | -0.12817 | -0.11902 | -0.20142 | -0.17395 | -0.10529 | -0.13275 | -0.09613 | 60.9512 | 60.9238 | 122.612 | 122.6578 | -0.11902 | 122.6532 | 60.704 | -0.10529 | 122.6578 | -0.11902 | 60.704 | 122.612 | 122.6532 | -122.8088 | -122.8912
110.0312 | 123.0057 | -60.8368 | 61.9263 | 0.14496 | 0.014526 | 0.017517 | 0.0042726 | 0.066009 | -0.0036316 | 0.076263 | -60.9512 | 61.8164 | -60.878 | -61.2259 | 61.702 | 0.17395 | 0.10986 | 0.073242 | 61.8484 | -60.9512 | -0.041199 | -0.10986 | -0.11444 | -0.3891 | -0.22431 | -0.11444 | -0.07782 | -0.073242 | 60.9467 | 60.91 | 122.5388 | 122.6532 | -0.11444 | 122.6852 | 61.0107 | -0.11444 | 122.6532 | -0.11444 | 61.0107 | 122.5388 | 122.6852 | -122.8043 | -122.8775
110.9844 | 122.9645 | -60.8505 | 61.9446 | 0.3128 | 0.016235 | 0.018799 | 0.0046998 | 0.0643 | -0.0057678 | 0.071564 | -61.0291 | 61.8118 | -60.9146 | -61.4044 | 61.2808 | -0.21515 | 0.27008 | -0.064087 | 61.821 | -60.9741 | -0.064087 | -0.13275 | -0.17853 | -0.55389 | -0.66376 | -0.1236 | -0.1236 | -0.11444 | 61.1206 | 60.7864 | 122.1313 | 122.6624 | -0.17853 | 122.6715 | 60.6354 | -0.1236 | 122.6624 | -0.17853 | 60.6354 | 122.1313 | 122.6715 | -122.8592 | -122.9187
112.0312 | 122.9965 | -60.8231 | 61.9354 | 0.030518 | 0.016876 | 0.012817 | 0.0008546 | 0.064514 | -0.005127 | 0.070923 | -60.9512 | 61.8164 | -60.8597 | -61.0336 | 61.7752 | 0.091553 | 0.086975 | 0.07782 | 61.8439 | -60.9558 | -0.036621 | -0.11902 | -0.12817 | -0.21057 | -0.16022 | -0.13275 | -0.091553 | -0.091553 | 60.91 | 60.9009 | 122.5983 | 122.6395 | -0.12817 | 122.6669 | 60.9146 | -0.13275 | 122.6395 | -0.12817 | 60.9146 | 122.5983 | 122.6669 | -122.7951 | -122.8912
112.9688 | 122.9736 | -60.8643 | 61.908 | 0.32806 | 0.015595 | 0.014526 | 0.0036316 | 0.065796 | -0.0023498 | 0.070496 | -61.0199 | 61.8027 | -60.8963 | -61.1389 | 61.6882 | -0.036621 | 0.009155 | -0.091553 | 61.8073 | -60.9695 | -0.032043 | -0.10529 | -0.15564 | -0.27466 | -0.21973 | -0.10529 | -0.10071 | -0.1236 | 60.8734 | 60.7727 | 122.5525 | 122.6669 | -0.15564 | 122.6715 | 60.8276 | -0.10529 | 122.6669 | -0.15564 | 60.8276 | 122.5525 | 122.6715 | -122.8043 | -122.8775
114.0312 | 123.0423 | -60.8459 | 61.9446 | 0.022888 | 0.014954 | 0.017304 | 0 | 0.064941 | -0.0040588 | 0.071564 | -60.9192 | 61.7706 | -60.8505 | -60.997 | 61.8393 | 0.16479 | 0.041199 | 0.13275 | 61.8164 | -60.9329 | -0.004578 | -0.17395 | -0.073242 | -0.15106 | -0.10529 | -0.086975 | -0.12817 | -0.068664 | 60.8871 | 60.9787 | 122.6852 | 122.6166 | -0.073242 | 122.6624 | 61.0107 | -0.086975 | 122.6166 | -0.073242 | 61.0107 | 122.6852 | 122.6624 | -122.7951 | -122.8775
114.9688 | 123.0194 | -60.8505 | 61.94 | -0.015259 | 0.01474 | 0.013672 | 0.004059 | 0.063019 | -0.0064086 | 0.070923 | -60.9695 | 61.8484 | -60.8734 | -61.0382 | 61.7569 | 0.082397 | 0.09613 | 0.045776 | 61.8347 | -60.9512 | -0.022888 | -0.091552 | -0.11902 | -0.18768 | -0.1831 | -0.10071 | -0.10529 | -0.09613 | 60.9467 | 60.8963 | 122.6074 | 122.699 | -0.11902 | 122.6852 | 60.9329 | -0.10071 | 122.699 | -0.11902 | 60.9329 | 122.6074 | 122.6852 | -122.8134 | -122.8912
116.0312 | 123.0286 | -60.8368 | 61.9125 | 0.36621 | 0.012604 | 0.010681 | -0.001068 | 0.062591 | -0.0046996 | 0.071777 | -60.9879 | 61.7294 | -60.8643 | -61.0794 | 61.7569 | 0.059509 | -0.041199 | 0.022888 | 61.8073 | -60.9283 | -0.027466 | -0.18311 | -0.15106 | -0.24262 | -0.15564 | -0.091553 | -0.10529 | -0.1236 | 60.7956 | 60.8597 | 122.5937 | 122.5662 | -0.15106 | 122.644 | 60.8963 | -0.091553 | 122.5662 | -0.15106 | 60.8963 | 122.5937 | 122.644 | -122.7768 | -122.8409
116.9688 | 123.0331 | -60.8231 | 61.9263 | 0.11444 | 0.01474 | 0.012177 | 0.0066224 | 0.0643 | -0.0076904 | 0.0737 | -60.9375 | 61.7981 | -60.8688 | -61.0428 | 61.7752 | 0.068665 | 0.045776 | 0.032043 | 61.8484 | -60.9558 | -0.045776 | -0.12817 | -0.11444 | -0.21973 | -0.15106 | -0.13275 | -0.07782 | -0.068665 | 60.8688 | 60.8551 | 122.5983 | 122.6212 | -0.11444 | 122.6715 | 60.8917 | -0.13275 | 122.6212 | -0.11444 | 60.8917 | 122.5983 | 122.6715 | -122.7951 | -122.8821
118.0312 | 123.0331 | -60.8047 | 61.9308 | 0.20599 | 0.014526 | 0.014313 | -0.0019226 | 0.063446 | -0.0036316 | 0.071991 | -61.0016 | 61.7615 | -60.8643 | -61.0519 | 61.7661 | 0.068665 | -0.036621 | 0.041199 | 61.8073 | -60.9375 | -0.059509 | -0.16937 | -0.19684 | -0.24719 | -0.16479 | -0.13275 | -0.1236 | -0.13733 | 60.7681 | 60.8459 | 122.5708 | 122.5662 | -0.19684 | 122.612 | 60.8734 | -0.13275 | 122.5662 | -0.19684 | 60.8734 | 122.5708 | 122.612 | -122.7951 | -122.8683
118.9688 | 123.0286 | -60.8139 | 61.9537 | -0.015259 | 0.014099 | 0.01239 | 0.000641 | 0.064087 | -0.0046996 | 0.071991 | -60.9146 | 61.7844 | -60.8459 | -60.9787 | 61.8164 | 0.16022 | 0.036621 | 0.14648 | 61.8256 | -60.9329 | -0.032043 | -0.16937 | -0.10071 | -0.16479 | -0.13733 | -0.11902 | -0.12817 | -0.068665 | 60.8505 | 60.9604 | 122.6303 | 122.5983 | -0.10071 | 122.6395 | 60.9741 | -0.11902 | 122.5983 | -0.10071 | 60.9741 | 122.6303 | 122.6395 | -122.7997 | -122.8867
120.0312 | 123.0423 | -60.8459 | 61.9446 | 0.2594 | 0.0093994 | 0.016022 | 0.0014954 | 0.06366 | -0.0040588 | 0.070923 | -60.8322 | 61.7752 | -60.8322 | -61.0703 | 61.7294 | 0.041199 | -0.050354 | 0.004578 | 61.8164 | -60.9375 | 0.013733 | -0.16937 | 0.013733 | -0.2243 | -0.21515 | -0.091553 | -0.12817 | 0 | 60.7956 | 60.8505 | 122.5754 | 122.6212 | 0.013733 | 122.6624 | 60.8871 | -0.091553 | 122.6212 | 0.013733 | 60.8871 | 122.5754 | 122.6624 | -122.7768 | -122.8821
120.9688 | 123.1064 | -60.7956 | 61.9125 | -0.045776 | 0.015595 | 0.014954 | 0.0012818 | 0.062591 | -0.0055542 | 0.070923 | -60.9009 | 61.7203 | -60.8551 | -60.9741 | 61.8439 | 0.16937 | -0.022888 | 0.15564 | 61.8439 | -60.9146 | -0.05951 | -0.19226 | -0.10529 | -0.17853 | -0.068665 | -0.11902 | -0.068665 | -0.045776 | 60.7727 | 60.9512 | 122.6395 | 122.5159 | -0.10529 | 122.6395 | 60.965 | -0.11902 | 122.5159 | -0.10529 | 60.965 | 122.6395 | 122.6395 | -122.7676 | -122.8271
122.0156 | 123.0881 | -60.8231 | 61.8851 | 0.38147 | 0.014526 | 0.018158 | 0.0044862 | 0.06366 | -0.0046996 | 0.070923 | -60.9375 | 61.7249 | -60.8643 | -61.0107 | 61.8027 | 0.073242 | -0.15564 | 0.041199 | 61.7706 | -60.9375 | -0.041199 | -0.16022 | -0.11444 | -0.18768 | -0.082398 | -0.11444 | -0.11444 | -0.073242 | 60.6674 | 60.8643 | 122.6257 | 122.5479 | -0.11444 | 122.5937 | 60.8963 | -0.11444 | 122.5479 | -0.11444 | 60.8963 | 122.6257 | 122.5937 | -122.7493 | -122.8226
122.9688 | 123.0698 | -60.8185 | 61.908 | 0.25177 | 0.01474 | 0.01239 | 0.0021362 | 0.064087 | -0.0040588 | 0.072418 | -60.9787 | 61.7432 | -60.8597 | -61.0428 | 61.7889 | 0.09613 | -0.036621 | 0.073242 | 61.8073 | -60.9421 | -0.041199 | -0.16479 | -0.16022 | -0.22431 | -0.11902 | -0.1236 | -0.10071 | -0.11902 | 60.7819 | 60.8917 | 122.6074 | 122.5616 | -0.16022 | 122.6257 | 60.9146 | -0.1236 | 122.5616 | -0.16022 | 60.9146 | 122.6074 | 122.6257 | -122.7676 | -122.85
124.0312 | 123.0606 | -60.8551 | 61.9217 | 0.19836 | 0.015595 | 0.015167 | 0.0032044 | 0.060882 | -0.002777 | 0.070496 | -60.9741 | 61.7615 | -60.8459 | -61.0474 | 61.7798 | 0.068665 | -0.036621 | 0.041199 | 61.7752 | -60.9375 | 0.009156 | -0.16022 | -0.11902 | -0.19226 | -0.14191 | -0.082397 | -0.14648 | -0.12817 | 60.8185 | 60.8963 | 122.6349 | 122.6166 | -0.11902 | 122.6303 | 60.9238 | -0.082397 | 122.6166 | -0.11902 | 60.9238 | 122.6349 | 122.6303 | -122.7676 | -122.8592
124.9688 | 123.0606 | -60.8002 | 61.9354 | 0.015259 | 0.015595 | 0.011749 | 0.004059 | 0.063019 | -0.004486 | 0.071777 | -60.9192 | 61.7661 | -60.8643 | -60.9695 | 61.8256 | 0.15564 | 0.027466 | 0.14191 | 61.8256 | -60.9283 | -0.064087 | -0.16937 | -0.11902 | -0.16937 | -0.10986 | -0.12817 | -0.10986 | -0.054931 | 60.8276 | 60.9421 | 122.6257 | 122.5662 | -0.11902 | 122.6257 | 60.9558 | -0.12817 | 122.5662 | -0.11902 | 60.9558 | 122.6257 | 122.6257 | -122.7997 | -122.8638
126.0156 | 123.0331 | -60.8459 | 61.908 | 0.4425 | 0.016235 | 0.016449 | 0.010468 | 0.0643 | -0.0055542 | 0.07135 | -61.0016 | 61.7935 | -60.8917 | -61.0657 | 61.7203 | -0.022888 | -0.073242 | -0.068665 | 61.7844 | -60.965 | -0.045777 | -0.11444 | -0.15564 | -0.21973 | -0.18768 | -0.11902 | -0.1236 | -0.10986 | 60.7727 | 60.7773 | 122.5662 | 122.6395 | -0.15564 | 122.6303 | 60.8231 | -0.11902 | 122.6395 | -0.15564 | 60.8231 | 122.5662 | 122.6303 | -122.7997 | -122.8729
126.9688 | 123.056 | -60.8093 | 61.9492 | 0 | 0.015808 | 0.011749 | 0.0027772 | 0.061951 | -0.0036316 | 0.071136 | -60.9238 | 61.7889 | -60.8322 | -60.9879 | 61.8027 | 0.12817 | 0.068665 | 0.12817 | 61.8027 | -60.9467 | -0.022888 | -0.16022 | -0.11444 | -0.17853 | -0.14648 | -0.13733 | -0.14648 | -0.091553 | 60.878 | 60.9375 | 122.612 | 122.5983 | -0.11444 | 122.612 | 60.9375 | -0.13733 | 122.5983 | -0.11444 | 60.9375 | 122.612 | 122.612 | -122.7814 | -122.8958
128.0156 | 122.9736 | -60.878 | 61.9263 | 0.34332 | 0.016449 | 0.01474 | 0.0079042 | 0.064941 | -0.0057678 | 0.070282 | -61.0199 | 61.8073 | -60.9009 | -61.1069 | 61.6974 | -0.041199 | 0.004578 | -0.10071 | 61.8073 | -60.9787 | -0.022888 | -0.11902 | -0.14191 | -0.22888 | -0.22888 | -0.10071 | -0.11902 | -0.11902 | 60.8826 | 60.7773 | 122.5754 | 122.6852 | -0.14191 | 122.6852 | 60.8368 | -0.10071 | 122.6852 | -0.14191 | 60.8368 | 122.5754 | 122.6852 | -122.8271 | -122.905
128.9688 | 123.0469 | -60.8368 | 61.8988 | 0.28229 | 0.014099 | 0.01239 | 0 | 0.062591 | -0.0038452 | 0.070496 | -60.9695 | 61.7798 | -60.8597 | -61.0657 | 61.734 | 0.013733 | -0.045776 | -0.018311 | 61.7615 | -60.9695 | -0.022888 | -0.11902 | -0.13275 | -0.22888 | -0.16479 | -0.13275 | -0.13733 | -0.10986 | 60.791 | 60.8185 | 122.5708 | 122.6166 | -0.13275 | 122.5983 | 60.8505 | -0.13275 | 122.6166 | -0.13275 | 60.8505 | 122.5708 | 122.5983 | -122.7585 | -122.8683
130.0156 | 123.0881 | -60.8414 | 61.8988 | 0.43488 | 0.017304 | 0.016235 | 0.0055542 | 0.065582 | -0.0046996 | 0.071564 | -60.9741 | 61.7889 | -60.878 | -61.0428 | 61.7752 | 0.050354 | -0.15106 | -0.013733 | 61.7477 | -60.9741 | -0.036621 | -0.10986 | -0.13275 | -0.20142 | -0.1236 | -0.13275 | -0.15106 | -0.09613 | 60.6903 | 60.8276 | 122.6166 | 122.6303 | -0.13275 | 122.5891 | 60.8917 | -0.13275 | 122.6303 | -0.13275 | 60.8917 | 122.6166 | 122.5891 | -122.7768 | -122.8729
130.9844 | 123.1293 | -60.8047 | 61.908 | 0.11444 | 0.016022 | 0.013886 | 0 | 0.062805 | -0.0023498 | 0.071991 | -60.9009 | 61.7661 | -60.8459 | -60.9695 | 61.8484 | 0.16022 | -0.068665 | 0.14191 | 61.7798 | -60.9192 | -0.041198 | -0.14191 | -0.09613 | -0.16479 | -0.059509 | -0.11444 | -0.12817 | -0.054932 | 60.7361 | 60.9467 | 122.6532 | 122.5708 | -0.09613 | 122.5845 | 60.965 | -0.11444 | 122.5708 | -0.09613 | 60.965 | 122.6532 | 122.5845 | -122.7539 | -122.8271
132.0312 | 123.0789 | -60.8231 | 61.8851 | 0.35858 | 0.015167 | 0.01474 | 0.004059 | 0.0643 | -0.0053406 | 0.071991 | -60.9329 | 61.7706 | -60.8551 | -61.0062 | 61.8027 | 0.073242 | -0.16479 | 0.036621 | 61.7661 | -60.9375 | -0.032044 | -0.11444 | -0.10986 | -0.18311 | -0.082398 | -0.11444 | -0.11902 | -0.077819 | 60.6583 | 60.8597 | 122.6257 | 122.5937 | -0.10986 | 122.5891 | 60.8963 | -0.11444 | 122.5937 | -0.10986 | 60.8963 | 122.6257 | 122.5891 | -122.7402 | -122.8226
132.9844 | 123.0881 | -60.791 | 61.94 | -0.015259 | 0.013245 | 0.012817 | 0.0021362 | 0.06366 | -0.0008544 | 0.071777 | -60.9055 | 61.7889 | -60.8276 | -60.9467 | 61.8347 | 0.1831 | -0.045776 | 0.16022 | 61.8027 | -60.9192 | -0.036621 | -0.15106 | -0.11444 | -0.15564 | -0.10529 | -0.12817 | -0.13733 | -0.07782 | 60.7452 | 60.9512 | 122.6257 | 122.58 | -0.11444 | 122.5937 | 60.9741 | -0.12817 | 122.58 | -0.11444 | 60.9741 | 122.6257 | 122.5937 | -122.7676 | -122.8592
134.0312 | 123.0835 | -60.8093 | 61.9354 | 0.37384 | 0.013458 | 0.01709 | 0.0066224 | 0.063019 | -0.0046996 | 0.068359 | -60.9421 | 61.7432 | -60.8734 | -60.9924 | 61.7249 | -0.13733 | -0.068665 | 0.16022 | 61.7432 | -60.9375 | -0.064087 | -0.19226 | -0.13275 | -0.18311 | -0.21057 | -0.12817 | -0.19226 | -0.068665 | 60.7407 | 60.9695 | 122.5342 | 122.5525 | -0.13275 | 122.5525 | 60.672 | -0.12817 | 122.5525 | -0.13275 | 60.672 | 122.5342 | 122.5525 | -122.8088 | -122.8729
134.9688 | 123.1247 | -60.8276 | 61.8896 | 0.48828 | 0.014313 | 0.01944 | 0.0046998 | 0.0643 | -0.002777 | 0.070282 | -60.9329 | 61.7661 | -60.8734 | -60.9924 | 61.8073 | 0.068665 | -0.17395 | 0.022888 | 61.7706 | -60.9558 | -0.045776 | -0.1236 | -0.10528 | -0.16479 | -0.082397 | -0.12817 | -0.11902 | -0.059509 | 60.6537 | 60.8505 | 122.6349 | 122.5937 | -0.10528 | 122.5983 | 60.8963 | -0.12817 | 122.5937 | -0.10528 | 60.8963 | 122.6349 | 122.5983 | -122.7631 | -122.8455
136.0156 | 122.9691 | -60.8505 | 61.9263 | 0.27466 | 0.015808 | 0.016663 | 0.0072632 | 0.064514 | -0.0036316 | 0.071136 | -60.9787 | 61.8393 | -60.8826 | -61.0611 | 61.7065 | 0.013733 | 0.050354 | -0.054932 | 61.8118 | -61.0016 | -0.032043 | -0.086976 | -0.12817 | -0.21057 | -0.21973 | -0.15106 | -0.11444 | -0.096131 | 60.9009 | 60.7956 | 122.5571 | 122.6898 | -0.12817 | 122.6624 | 60.8643 | -0.15106 | 122.6898 | -0.12817 | 60.8643 | 122.5571 | 122.6624 | -122.8088 | -122.9279
136.9688 | 123.0286 | -60.8871 | 61.8988 | 0.3891 | 0.017731 | 0.014313 | 0.0053406 | 0.067291 | -0.0014954 | 0.072845 | -61.0016 | 61.8484 | -60.878 | -61.0886 | 61.7294 | -0.018311 | -0.054932 | -0.082397 | 61.7798 | -61.0153 | 0.009155 | -0.050354 | -0.11444 | -0.20142 | -0.16937 | -0.12817 | -0.11902 | -0.1236 | 60.8322 | 60.8047 | 122.6166 | 122.7356 | -0.11444 | 122.6669 | 60.8688 | -0.12817 | 122.7356 | -0.11444 | 60.8688 | 122.6166 | 122.6669 | -122.7768 | -122.9141
137.9688 | 123.0972 | -60.8368 | 61.8942 | 0.35095 | 0.012817 | 0.017304 | 0.0014954 | 0.063232 | -0.0012818 | 0.0737 | -60.9375 | 61.7844 | -60.8459 | -61.0291 | 61.7981 | 0.073242 | -0.14191 | 0.027466 | 61.734 | -60.9695 | -0.009155 | -0.10986 | -0.10071 | -0.19226 | -0.09613 | -0.13275 | -0.16022 | -0.091553 | 60.6949 | 60.8643 | 122.6349 | 122.6212 | -0.10071 | 122.5708 | 60.91 | -0.13275 | 122.6212 | -0.10071 | 60.91 | 122.6349 | 122.5708 | -122.7402 | -122.8638
139.0156 | 122.9645 | -60.8459 | 61.9446 | 0.23651 | 0.016876 | 0.015595 | 0.0059816 | 0.06131 | -0.004486 | 0.070496 | -60.9741 | 61.8576 | -60.8963 | -61.0611 | 61.7249 | 0.032043 | 0.032043 | -0.032043 | 61.8027 | -61.0062 | -0.050354 | -0.086975 | -0.12817 | -0.21515 | -0.21973 | -0.16022 | -0.14191 | -0.07782 | 60.878 | 60.8139 | 122.5708 | 122.7036 | -0.12817 | 122.6486 | 60.878 | -0.16022 | 122.7036 | -0.12817 | 60.878 | 122.5708 | 122.6486 | -122.8409 | -122.9507
139.9844 | 123.0194 | -60.8322 | 61.9354 | -0.68665 | 0.016449 | 0.013886 | 0.0036316 | 0.064728 | -0.004486 | 0.070923 | -60.9924 | 61.8347 | -60.9146 | -61.0336 | 61.7706 | 0.082397 | 0.027466 | 0.036621 | 61.8118 | -60.9558 | -0.082398 | -0.10071 | -0.16022 | -0.20142 | -0.1648 | -0.1236 | -0.1236 | -0.07782 | 60.8597 | 60.8688 | 122.6028 | 122.6669 | -0.16022 | 122.644 | 60.9146 | -0.1236 | 122.6669 | -0.16022 | 60.9146 | 122.6028 | 122.644 | -122.85 | -122.8912
141.0156 | 122.8683 | -60.9146 | 61.9171 | 0.35858 | 0.016449 | 0.012817 | 0.004059 | 0.066223 | -0.0023498 | 0.073914 | -61.0153 | 61.8851 | -60.8963 | -61.1252 | 61.6791 | -0.050354 | 0.059509 | -0.12817 | 61.8027 | -60.997 | 0.018311 | -0.032043 | -0.10071 | -0.21057 | -0.23804 | -0.082397 | -0.11444 | -0.11902 | 60.9741 | 60.7864 | 122.5937 | 122.7997 | -0.10071 | 122.7173 | 60.8643 | -0.082397 | 122.7997 | -0.10071 | 60.8643 | 122.5937 | 122.7173 | -122.8134 | -122.9141
141.9844 | 123.0377 | -60.8322 | 61.9171 | 0.3128 | 0.014313 | 0.016022 | -0.0006408 | 0.0643 | -0.0023498 | 0.071991 | -60.9741 | 61.8164 | -60.8505 | -61.0565 | 61.7661 | 0.064087 | -0.054932 | 0.20599 | 61.8118 | -60.9604 | -0.018311 | -0.10071 | -0.14191 | -0.22431 | -0.15106 | -0.12817 | -0.10528 | -0.1236 | 60.7773 | 61.0382 | 122.5983 | 122.6486 | -0.14191 | 122.644 | 60.8963 | -0.12817 | 122.6486 | -0.14191 | 60.8963 | 122.5983 | 122.644 | -122.7676 | -122.8775
143.0156 | 122.9919 | -60.8597 | 61.94 | 0.25177 | 0.014313 | 0.016663 | 0.0070496 | 0.064087 | -0.0023498 | 0.070923 | -60.9741 | 61.8759 | -60.8826 | -61.0657 | 61.7111 | 0.004578 | 0.050354 | -0.050354 | 61.8164 | -61.0016 | -0.022888 | -0.064086 | -0.11444 | -0.20599 | -0.22888 | -0.14191 | -0.1236 | -0.091553 | 60.91 | 60.8093 | 122.5708 | 122.7356 | -0.11444 | 122.6761 | 60.8643 | -0.14191 | 122.7356 | -0.11444 | 60.8643 | 122.5708 | 122.6761 | -122.8226 | -122.9416
143.9688 | 122.9965 | -60.8414 | 61.9034 | 0.40436 | 0.016876 | 0.013672 | 0.0053406 | 0.065582 | -0.001068 | 0.071136 | -61.0153 | 61.8622 | -60.8871 | -61.1069 | 61.7294 | -0.018311 | -0.064087 | -0.068665 | 61.7844 | -61.0107 | -0.045776 | -0.041198 | -0.17395 | -0.2655 | -0.17395 | -0.16937 | -0.11902 | -0.12817 | 60.7773 | 60.7727 | 122.5708 | 122.7036 | -0.17395 | 122.6257 | 60.8231 | -0.16937 | 122.7036 | -0.17395 | 60.8231 | 122.5708 | 122.6257 | -122.7905 | -122.9141
145.0312 | 123.1064 | -60.8276 | 61.8942 | -0.32043 | 0.012604 | 0.010254 | 0.000641 | 0.064728 | -0.0036316 | 0.073059 | -60.8185 | 61.7661 | -60.8643 | -61.0107 | 61.8256 | 0.07782 | -0.16937 | 0.027466 | 61.7523 | -60.9604 | -0.036621 | -0.12817 | 0.009156 | -0.1831 | -0.068664 | -0.13275 | -0.14191 | 0.045777 | 60.6583 | 60.8551 | 122.6532 | 122.5937 | 0.009156 | 122.58 | 60.9055 | -0.13275 | 122.5937 | 0.009156 | 60.9055 | 122.6532 | 122.58 | -122.7585 | -122.8546
145.9688 | 123.0881 | -60.8505 | 61.8896 | 0.40436 | 0.01474 | 0.014954 | 0.0027772 | 0.063232 | -0.0042724 | 0.072418 | -60.9238 | 61.8118 | -60.8688 | -61.0016 | 61.8118 | 0.068665 | -0.16937 | 0.036621 | 61.7661 | -60.9741 | -0.01831 | -0.077819 | -0.073242 | -0.15106 | -0.077819 | -0.1236 | -0.1236 | -0.054932 | 60.6812 | 60.8871 | 122.6624 | 122.6624 | -0.073242 | 122.6166 | 60.9192 | -0.1236 | 122.6624 | -0.073242 | 60.9192 | 122.6624 | 122.6166 | -122.7585 | -122.8638
147.0156 | 123.0011 | -60.8414 | 61.9675 | 0.13733 | 0.01709 | 0.014313 | 0.0055542 | 0.065582 | -0.0032044 | 0.073059 | -60.9421 | 61.8896 | -60.8826 | -61.0977 | 61.8622 | 0.10071 | 0.11902 | 0.09613 | 61.8164 | -61.0062 | -0.041198 | -0.07782 | -0.10071 | -0.25635 | -0.10528 | -0.1648 | -0.15106 | -0.05951 | 60.9604 | 60.9375 | 122.7036 | 122.731 | -0.10071 | 122.6578 | 60.9421 | -0.1648 | 122.731 | -0.10071 | 60.9421 | 122.7036 | 122.6578 | -122.85 | -122.9736
147.9688 | 123.0057 | -60.8551 | 61.9263 | 0.25177 | 0.017944 | 0.018158 | 0.0070496 | 0.064728 | -0.0029906 | 0.071777 | -60.9833 | 61.8896 | -60.8643 | -61.0886 | 61.7386 | 0 | 0.050354 | -0.045776 | 61.8301 | -61.0199 | -0.009155 | -0.036622 | -0.12817 | -0.23346 | -0.18768 | -0.16479 | -0.096131 | -0.11902 | 60.9055 | 60.8093 | 122.5937 | 122.7448 | -0.12817 | 122.6852 | 60.8551 | -0.16479 | 122.7448 | -0.12817 | 60.8551 | 122.5937 | 122.6852 | -122.7905 | -122.9462
149.0156 | 123.0194 | -60.8276 | 61.9217 | 0.1297 | 0.017731 | 0.017517 | 0.0053406 | 0.065796 | -0.0036316 | 0.070923 | -60.9009 | 61.853 | -60.8734 | -61.0519 | 61.8301 | 0.091553 | 0.07782 | 0.064087 | 61.8301 | -60.9879 | -0.045776 | -0.068665 | -0.073242 | -0.2243 | -0.091553 | -0.16022 | -0.091553 | -0.027466 | 60.9055 | 60.8917 | 122.6578 | 122.6807 | -0.073242 | 122.6578 | 60.9192 | -0.16022 | 122.6807 | -0.073242 | 60.9192 | 122.6578 | 122.6578 | -122.7951 | -122.9095
149.9844 | 123.0423 | -60.8414 | 61.8896 | 0.3128 | 0.014313 | 0.010895 | -0.0014952 | 0.0643 | -0.0012818 | 0.073486 | -61.0062 | 61.7889 | -60.878 | -61.0703 | 61.7477 | 0.054932 | -0.07782 | 0.004578 | 61.7844 | -60.965 | -0.036621 | -0.10071 | -0.1648 | -0.22888 | -0.14191 | -0.1236 | -0.10529 | -0.12817 | 60.7635 | 60.8459 | 122.5891 | 122.6303 | -0.1648 | 122.6257 | 60.8963 | -0.1236 | 122.6303 | -0.1648 | 60.8963 | 122.5891 | 122.6257 | -122.7676 | -122.8546
151.0156 | 123.024 | -60.8368 | 61.9583 | 0.068664 | 0.016235 | 0.017517 | 0.005127 | 0.064728 | -0.005127 | 0.070496 | -60.9558 | 61.8713 | -60.8643 | -61.0291 | 61.7798 | 0.091553 | 0.091553 | 0.054932 | 61.8439 | -60.965 | -0.027466 | -0.086975 | -0.11902 | -0.19226 | -0.17853 | -0.12817 | -0.11444 | -0.091553 | 60.9283 | 60.8917 | 122.6166 | 122.7081 | -0.11902 | 122.6807 | 60.9283 | -0.12817 | 122.7081 | -0.11902 | 60.9283 | 122.6166 | 122.6807 | -122.8226 | -122.9233
151.9688 | 122.9736 | -60.8505 | 61.9308 | 0.22888 | 0.017731 | 0.016876 | 0.0057678 | 0.064941 | -0.002777 | 0.071777 | -60.9924 | 61.8851 | -60.8871 | -61.0977 | 61.702 | -0.004578 | 0.059509 | -0.054932 | 61.8393 | -61.0245 | -0.036621 | -0.045776 | -0.14191 | -0.24719 | -0.22888 | -0.17395 | -0.091553 | -0.10529 | 60.91 | 60.7956 | 122.5525 | 122.7356 | -0.14191 | 122.6898 | 60.8459 | -0.17395 | 122.7356 | -0.14191 | 60.8459 | 122.5525 | 122.6898 | -122.818 | -122.9553
153.0156 | 123.0057 | -60.8322 | 61.9492 | 0.061035 | 0.017304 | 0.01239 | 0.0066224 | 0.065369 | -0.0025634 | 0.071564 | -60.9467 | 61.908 | -60.8734 | -61.0153 | 61.7935 | 0.10071 | 0.086975 | 0.064087 | 61.8347 | -61.0016 | -0.041199 | -0.041199 | -0.11444 | -0.18311 | -0.15564 | -0.16937 | -0.11444 | -0.073242 | 60.9192 | 60.8963 | 122.6257 | 122.7402 | -0.11444 | 122.6669 | 60.9329 | -0.16937 | 122.7402 | -0.11444 | 60.9329 | 122.6257 | 122.6669 | -122.8226 | -122.9507
153.9688 | 123.0057 | -60.8597 | 61.9492 | 0.14496 | 0.015595 | 0.013031 | 0.004059 | 0.064941 | -0.0032044 | 0.072845 | -60.9421 | 61.8942 | -60.8917 | -61.0611 | 61.7477 | 0.050354 | 0.041199 | 0.022888 | 61.821 | -61.0199 | -0.032044 | -0.054932 | -0.082398 | -0.20142 | -0.20142 | -0.16022 | -0.12817 | -0.050354 | 60.9009 | 60.8826 | 122.6074 | 122.7539 | -0.082398 | 122.6807 | 60.91 | -0.16022 | 122.7539 | -0.082398 | 60.91 | 122.6074 | 122.6807 | -122.8409 | -122.9691
155.0469 | 123.0057 | -60.8505 | 61.9308 | 0.16785 | 0.017304 | 0.015167 | 0.0049134 | 0.064087 | -0.0029906 | 0.071777 | -60.965 | 61.8942 | -60.9055 | -61.0748 | 61.7569 | 0.068665 | 0.045776 | 0.022888 | 61.821 | -61.0016 | -0.054932 | -0.036621 | -0.11444 | -0.2243 | -0.17395 | -0.15106 | -0.10986 | -0.059509 | 60.8963 | 60.8734 | 122.6074 | 122.7448 | -0.11444 | 122.6715 | 60.9192 | -0.15106 | 122.7448 | -0.11444 | 60.9192 | 122.6074 | 122.6715 | -122.8363 | -122.9324
155.9688 | 123.0286 | -60.8688 | 61.9354 | 0.068664 | 0.018585 | 0.011749 | 0.0027772 | 0.065796 | -0.002777 | 0.071136 | -61.0931 | 61.8439 | -60.8917 | -61.0382 | 61.7844 | 0.10986 | 0.054932 | 0.064087 | 61.8347 | -60.9924 | -0.022889 | -0.091553 | -0.22431 | -0.16937 | -0.15106 | -0.1236 | -0.10071 | -0.20142 | 60.9238 | 60.9329 | 122.6532 | 122.7127 | -0.22431 | 122.7036 | 60.9787 | -0.1236 | 122.7127 | -0.22431 | 60.9787 | 122.6532 | 122.7036 | -122.8271 | -122.9279
157.0156 | 122.9874 | -60.8551 | 61.9492 | 0.091552 | 0.015808 | 0.01474 | 0.0019226 | 0.064514 | -0.0023498 | 0.07135 | -61.0062 | 61.908 | -60.8688 | -61.0748 | 61.7249 | 0.064087 | 0.16937 | 0.022888 | 61.8622 | -61.0153 | -0.013732 | -0.041199 | -0.15106 | -0.21973 | -0.2243 | -0.16022 | -0.086975 | -0.13733 | 61.0245 | 60.878 | 122.58 | 122.7631 | -0.15106 | 122.7173 | 60.9192 | -0.16022 | 122.7631 | -0.15106 | 60.9192 | 122.58 | 122.7173 | -122.818 | -122.9645
157.9688 | 122.9828 | -60.8322 | 61.9171 | 0.25177 | 0.019653 | 0.016449 | 0.0066224 | 0.065796 | -0.0040588 | 0.072205 | -60.9512 | 61.908 | -60.8734 | -61.0245 | 61.7798 | 0.086975 | 0.054932 | 0.050354 | 61.8256 | -60.997 | -0.041199 | -0.009155 | -0.11902 | -0.19226 | -0.13733 | -0.16479 | -0.091552 | -0.07782 | 60.8871 | 60.8826 | 122.612 | 122.7402 | -0.11902 | 122.6578 | 60.9192 | -0.16479 | 122.7402 | -0.11902 | 60.9192 | 122.612 | 122.6578 | -122.7905 | -122.9141
159.0156 | 122.9919 | -60.8459 | 62.0087 | -0.13733 | 0.01709 | 0.014526 | 0.0002136 | 0.06366 | -0.003418 | 0.071136 | -60.9924 | 61.8759 | -60.8597 | -61.0748 | 61.7615 | 0.091553 | 0.15564 | 0.036621 | 61.853 | -61.0245 | -0.013733 | -0.13275 | -0.14648 | -0.22888 | -0.24719 | -0.17853 | -0.15564 | -0.13275 | 61.0016 | 60.8826 | 122.6074 | 122.7219 | -0.14648 | 122.699 | 60.9375 | -0.17853 | 122.7219 | -0.14648 | 60.9375 | 122.6074 | 122.699 | -122.8683 | -123.0331
159.9688 | 123.0377 | -60.8551 | 61.9263 | 0.015259 | 0.016449 | 0.013672 | 0.005127 | 0.062164 | -0.0029906 | 0.0737 | -60.9467 | 61.8942 | -60.8871 | -61.0382 | 61.7752 | 0.09613 | 0.086975 | 0.050354 | 61.8439 | -61.0107 | -0.032043 | -0.032044 | -0.091552 | -0.1831 | -0.15106 | -0.15564 | -0.082398 | -0.059509 | 60.9421 | 60.9055 | 122.6303 | 122.7493 | -0.091552 | 122.699 | 60.9512 | -0.15564 | 122.7493 | -0.091552 | 60.9512 | 122.6303 | 122.699 | -122.8134 | -122.937
161.0156 | 123.0927 | -60.8231 | 61.9263 | 0.061035 | 0.014099 | 0.012604 | -0.0023498 | 0.063232 | -0.002777 | 0.069855 | -60.9192 | 61.821 | -60.8414 | -60.9879 | 61.853 | 0.1831 | -0.013733 | 0.16479 | 61.8118 | -60.9512 | -0.018311 | -0.10529 | -0.09613 | -0.16479 | -0.073243 | -0.12817 | -0.11444 | -0.077819 | 60.8093 | 60.9879 | 122.6761 | 122.644 | -0.09613 | 122.6349 | 61.0062 | -0.12817 | 122.644 | -0.09613 | 61.0062 | 122.6761 | 122.6349 | -122.7676 | -122.8775
161.9688 | 122.9507 | -60.8871 | 61.9034 | 0.2594 | 0.016876 | 0.014954 | 0.004059 | 0.064514 | -0.0019226 | 0.068787 | -61.0245 | 61.8668 | -60.8963 | -61.1252 | 61.6745 | -0.041199 | 0.054932 | -0.10986 | 61.8073 | -61.0199 | -0.009155 | -0.036621 | -0.13733 | -0.23804 | -0.22888 | -0.13275 | -0.09613 | -0.12817 | 60.9421 | 60.7773 | 122.5616 | 122.7539 | -0.13733 | 122.6944 | 60.8459 | -0.13275 | 122.7539 | -0.13733 | 60.8459 | 122.5616 | 122.6944 | -122.7997 | -122.9233
163.0156 | 122.9874 | -60.8368 | 61.9354 | -0.030518 | 0.015381 | 0.01709 | -0.0002136 | 0.063873 | -0.0019226 | 0.070709 | -60.9558 | 61.853 | -60.8643 | -61.0428 | 61.7752 | 0.11902 | 0.11444 | 0.07782 | 61.8347 | -60.9833 | -0.027466 | -0.082398 | -0.11902 | -0.20599 | -0.16022 | -0.14648 | -0.10071 | -0.091553 | 60.9512 | 60.9146 | 122.612 | 122.6898 | -0.11902 | 122.6715 | 60.9558 | -0.14648 | 122.6898 | -0.11902 | 60.9558 | 122.612 | 122.6715 | -122.7997 | -122.9187
163.9688 | 122.9828 | -60.8505 | 61.9446 | 0 | 0.016022 | 0.014313 | 0.0025636 | 0.062591 | -0.0025634 | 0.069855 | -61.0062 | 61.8668 | -60.8597 | -61.084 | 61.7432 | 0.068665 | 0.39368 | 0.23804 | 61.8988 | -60.9833 | -0.009155 | -0.07782 | -0.15564 | -0.23346 | -0.20142 | -0.13275 | -0.045776 | -0.14649 | 61.2442 | 61.0886 | 122.5937 | 122.7173 | -0.15564 | 122.7493 | 60.9192 | -0.13275 | 122.7173 | -0.15564 | 60.9192 | 122.5937 | 122.7493 | -122.8043 | -122.9279
165.0156 | 123.1018 | -60.8231 | 61.94 | -0.0076295 | 0.014099 | 0.012177 | 0.00235 | 0.064514 | -0.0032044 | 0.071564 | -60.9009 | 61.821 | -60.8414 | -60.9833 | 61.8347 | 0.16479 | 0.036621 | 0.16937 | 61.8118 | -60.9604 | -0.018311 | -0.11902 | -0.07782 | -0.16022 | -0.10529 | -0.13733 | -0.12817 | -0.059509 | 60.8597 | 60.9924 | 122.6578 | 122.644 | -0.07782 | 122.6349 | 60.9879 | -0.13733 | 122.644 | -0.07782 | 60.9879 | 122.6578 | 122.6349 | -122.7814 | -122.9004
165.9688 | 122.9874 | -60.8459 | 61.972 | 0.022888 | 0.014954 | 0.013245 | 0.0064088 | 0.062378 | -0.0046996 | 0.071564 | -60.9741 | 61.9034 | -60.8688 | -61.0748 | 61.7432 | 0.059509 | 0.14191 | 0.032043 | 61.8622 | -60.9833 | -0.022888 | -0.068665 | -0.12817 | -0.22888 | -0.22888 | -0.13733 | -0.10986 | -0.10529 | 60.9879 | 60.878 | 122.5891 | 122.7493 | -0.12817 | 122.7081 | 60.9055 | -0.13733 | 122.7493 | -0.12817 | 60.9055 | 122.5891 | 122.7081 | -122.8409 | -122.9553
166.9688 | 122.9736 | -60.8414 | 61.9537 | 0 | 0.015381 | 0.015167 | 0.004059 | 0.064087 | -0.004486 | 0.070282 | -60.9741 | 61.8576 | -60.8871 | -61.084 | 61.734 | 0.086975 | 0.16022 | 0.009155 | 61.8576 | -60.9558 | -0.045776 | -0.09613 | -0.13275 | -0.24261 | -0.21973 | -0.11444 | -0.09613 | -0.086975 | 61.0016 | 60.8505 | 122.5754 | 122.699 | -0.13275 | 122.699 | 60.9283 | -0.11444 | 122.699 | -0.13275 | 60.9283 | 122.5754 | 122.699 | -122.8409 | -122.9095
168.0312 | 122.9828 | -60.8368 | 61.972 | 0.038147 | 0.014954 | 0.012817 | 0.0021362 | 0.064941 | -0.001709 | 0.071564 | -60.9787 | 61.853 | -60.8688 | -61.0565 | 61.7615 | 0.073242 | 0.16937 | 0.050354 | 61.8759 | -60.9604 | -0.032043 | -0.11902 | -0.14191 | -0.21973 | -0.21057 | -0.1236 | -0.09613 | -0.10986 | 61.0062 | 60.8871 | 122.5983 | 122.6898 | -0.14191 | 122.7127 | 60.91 | -0.1236 | 122.6898 | -0.14191 | 60.91 | 122.5983 | 122.7127 | -122.8409 | -122.9324
168.9688 | 123.0103 | -60.878 | 61.9492 | -0.045776 | 0.015167 | 0.011963 | 0.0019226 | 0.064728 | -0.0046996 | 0.071136 | -60.965 | 61.8393 | -60.8871 | -61.0519 | 61.7523 | 0.091553 | 0.12817 | 0.064087 | 61.8622 | -60.9558 | -0.009155 | -0.10986 | -0.086975 | -0.17395 | -0.19684 | -0.07782 | -0.086975 | -0.07782 | 61.0062 | 60.9421 | 122.6303 | 122.7173 | -0.086975 | 122.7402 | 60.9695 | -0.07782 | 122.7173 | -0.086975 | 60.9695 | 122.6303 | 122.7402 | -122.8363 | -122.905
169.9688 | 122.9919 | -60.8322 | 61.94 | -0.068665 | 0.014313 | 0.012817 | 0.0002136 | 0.065155 | -0.0036316 | 0.071777 | -60.9375 | 61.8027 | -60.8505 | -61.0336 | 61.7661 | 0.11444 | 0.13275 | 0.082397 | 61.8713 | -60.9467 | -0.018311 | -0.13733 | -0.10529 | -0.20142 | -0.17395 | -0.11444 | -0.068664 | -0.086975 | 60.965 | 60.9146 | 122.5983 | 122.6349 | -0.10529 | 122.7036 | 60.9467 | -0.11444 | 122.6349 | -0.10529 | 60.9467 | 122.5983 | 122.7036 | -122.7905 | -122.8867
171.0312 | 123.0331 | -60.8505 | 61.9446 | -0.068665 | 0.014954 | 0.013245 | 0.0029908 | 0.063232 | -0.002777 | 0.073273 | -60.9192 | 61.8073 | -60.8368 | -61.0245 | 61.7844 | 0.14191 | 0.09613 | 0.10986 | 61.8896 | -60.9421 | 0.013733 | -0.13733 | -0.068664 | -0.17395 | -0.16022 | -0.091553 | -0.054932 | -0.082397 | 60.9467 | 60.9604 | 122.6349 | 122.6578 | -0.068664 | 122.7402 | 60.9924 | -0.091553 | 122.6578 | -0.068664 | 60.9924 | 122.6349 | 122.7402 | -122.7814 | -122.8867
171.9688 | 123.024 | -60.8551 | 61.94 | 0.13733 | 0.016449 | 0.014099 | 0.0089722 | 0.064514 | -0.0038452 | 0.070709 | -60.9421 | 61.8484 | -60.8871 | -61.0336 | 61.7432 | 0.068665 | 0.027466 | 0.027466 | 61.8301 | -61.0016 | -0.032043 | -0.091552 | -0.086975 | -0.17853 | -0.19684 | -0.14648 | -0.10986 | -0.054932 | 60.8826 | 60.8826 | 122.5983 | 122.7036 | -0.086975 | 122.6852 | 60.9238 | -0.14648 | 122.7036 | -0.086975 | 60.9238 | 122.5983 | 122.6852 | -122.8271 | -122.9416
173.0156 | 123.056 | -60.8276 | 61.8988 | 0.21362 | 0.014313 | 0.01239 | 0.0002136 | 0.06366 | -0.0021362 | 0.070709 | -60.9924 | 61.7935 | -60.8688 | -61.0336 | 61.7935 | 0.09613 | -0.032043 | 0.07782 | 61.7798 | -60.9467 | -0.041198 | -0.10529 | -0.16479 | -0.20599 | -0.10529 | -0.11902 | -0.11902 | -0.1236 | 60.7956 | 60.9055 | 122.6212 | 122.6212 | -0.16479 | 122.6074 | 60.9238 | -0.11902 | 122.6212 | -0.16479 | 60.9238 | 122.6212 | 122.6074 | -122.7676 | -122.8455
173.9688 | 122.9691 | -60.8459 | 61.9492 | -0.061036 | 0.015808 | 0.01474 | 0.0025636 | 0.063019 | -0.0029906 | 0.070068 | -61.0016 | 61.8759 | -60.9055 | -61.0657 | 61.734 | 0.059509 | 0.16937 | 0.041199 | 61.8896 | -60.9833 | -0.05951 | -0.073242 | -0.15564 | -0.21973 | -0.21515 | -0.13733 | -0.05951 | -0.09613 | 61.0153 | 60.8871 | 122.58 | 122.7219 | -0.15564 | 122.7356 | 60.9055 | -0.13733 | 122.7219 | -0.15564 | 60.9055 | 122.58 | 122.7356 | -122.8546 | -122.9324
175.0156 | 123.1155 | -60.8139 | 61.972 | 0.068664 | 0.014954 | 0.014313 | 0.000641 | 0.064087 | -0.0040588 | 0.070709 | -60.9192 | 61.7889 | -60.8185 | -60.9695 | 61.8301 | 0.16479 | 0.009155 | 0.16022 | 61.7706 | -60.9375 | -0.004577 | -0.18311 | -0.10529 | -0.15564 | -0.14191 | -0.1236 | -0.20142 | -0.10071 | 60.8231 | 60.9741 | 122.644 | 122.6028 | -0.10529 | 122.5845 | 60.9787 | -0.1236 | 122.6028 | -0.10529 | 60.9787 | 122.644 | 122.5845 | -122.7905 | -122.9095
175.9688 | 122.9416 | -60.8688 | 61.9766 | 0 | 0.013886 | 0.015595 | 0.0064088 | 0.062591 | -0.0036316 | 0.069855 | -60.9879 | 61.853 | -60.8963 | -61.0519 | 61.7249 | 0.036621 | 0.17395 | 0.045776 | 61.8576 | -60.9512 | -0.027466 | -0.1236 | -0.11902 | -0.18311 | -0.25177 | -0.082398 | -0.11902 | -0.091553 | 61.0428 | 60.9146 | 122.5937 | 122.7219 | -0.11902 | 122.7264 | 60.9055 | -0.082398 | 122.7219 | -0.11902 | 60.9055 | 122.5937 | 122.7264 | -122.8729 | -122.9279
176.9688 | 123.0011 | -60.8643 | 61.9675 | -0.015259 | 0.015808 | 0.012177 | 0.005127 | 0.062591 | -0.0042724 | 0.070709 | -60.9924 | 61.8759 | -60.8826 | -61.0703 | 61.6653 | 0.14191 | 0.35706 | -0.13275 | 61.8713 | -60.9695 | -0.01831 | -0.091552 | -0.12817 | -0.20599 | -0.30212 | -0.10529 | -0.09613 | -0.10986 | 61.2213 | 60.7315 | 122.5296 | 122.7402 | -0.12817 | 122.7356 | 61.0062 | -0.10529 | 122.7402 | -0.12817 | 61.0062 | 122.5296 | 122.7356 | -122.85 | -122.937
177.9688 | 122.9874 | -60.8505 | 61.972 | -0.061036 | 0.016876 | 0.011749 | 0.004059 | 0.064728 | -0.0036316 | 0.07135 | -60.9924 | 61.8256 | -60.8963 | -61.0794 | 61.7386 | 0.059509 | 0.16937 | 0.054932 | 61.8622 | -60.9604 | -0.045776 | -0.14648 | -0.14191 | -0.22888 | -0.23346 | -0.10986 | -0.10986 | -0.096131 | 61.0199 | 60.9055 | 122.5891 | 122.6761 | -0.14191 | 122.7127 | 60.91 | -0.10986 | 122.6761 | -0.14191 | 60.91 | 122.5891 | 122.7127 | -122.8683 | -122.9324
179.0156 | 123.0881 | -60.8093 | 61.8988 | 0.15259 | 0.014954 | 0.012604 | -0.001068 | 0.066009 | -0.0023498 | 0.068787 | -60.9192 | 61.7981 | -60.8414 | -60.9741 | 61.8301 | 0.15106 | -0.050354 | 0.14648 | 61.8027 | -60.9238 | -0.032044 | -0.10071 | -0.10986 | -0.16479 | -0.068665 | -0.11444 | -0.096131 | -0.077819 | 60.759 | 60.9558 | 122.6395 | 122.6074 | -0.10986 | 122.612 | 60.9604 | -0.11444 | 122.6074 | -0.10986 | 60.9604 | 122.6395 | 122.612 | -122.7402 | -122.8226
179.9688 | 123.0148 | -60.8368 | 61.9354 | 0.2594 | 0.014954 | 0.016449 | 0.0061952 | 0.064728 | -0.0038452 | 0.071777 | -60.9238 | 61.8576 | -60.878 | -61.0153 | 61.7981 | 0.082397 | 0.036621 | 0.036621 | 61.8393 | -60.9833 | -0.041199 | -0.07782 | -0.086975 | -0.17853 | -0.13733 | -0.14648 | -0.096131 | -0.045776 | 60.8734 | 60.8734 | 122.6349 | 122.6944 | -0.086975 | 122.6761 | 60.9192 | -0.14648 | 122.6944 | -0.086975 | 60.9192 | 122.6349 | 122.6761 | -122.8134 | -122.9187
181.0156 | 123.111 | -60.8231 | 61.8942 | 0.053405 | 0.013672 | 0.011322 | -0.0019226 | 0.0643 | -0.0014954 | 0.07135 | -60.878 | 61.8118 | -60.8368 | -60.9879 | 61.7844 | 0.14648 | -0.032043 | 0.09613 | 61.8027 | -60.9467 | -0.013733 | -0.082397 | -0.054932 | -0.16479 | -0.10986 | -0.1236 | -0.091553 | -0.041199 | 60.791 | 60.9192 | 122.6074 | 122.6349 | -0.054932 | 122.6257 | 60.9695 | -0.1236 | 122.6349 | -0.054932 | 60.9695 | 122.6074 | 122.6257 | -122.731 | -122.8409
181.9688 | 123.024 | -60.8368 | 61.9446 | -0.038147 | 0.014954 | 0.010254 | 0.0025636 | 0.06366 | -0.005127 | 0.07135 | -60.9558 | 61.8301 | -60.8551 | -61.0519 | 61.7615 | 0.091553 | 0.15106 | 0.091553 | 61.8576 | -60.9421 | -0.018311 | -0.11444 | -0.11902 | -0.21515 | -0.18311 | -0.10529 | -0.086975 | -0.10071 | 60.9879 | 60.9283 | 122.5983 | 122.6669 | -0.11902 | 122.6944 | 60.9283 | -0.10529 | 122.6669 | -0.11902 | 60.9283 | 122.5983 | 122.6944 | -122.7997 | -122.8867
182.9688 | 122.9828 | -60.8368 | 61.9812 | -1.8616 | 0.015808 | 0.015595 | 0.0038452 | 0.06366 | -0.0040588 | 0.071991 | -61.0611 | 61.8668 | -60.8871 | -61.0931 | 61.7065 | 0.064087 | 0.17853 | 0.045776 | 61.8851 | -60.9558 | -0.050354 | -0.11444 | -0.2243 | -0.25635 | -0.27466 | -0.11902 | -0.09613 | -0.17395 | 61.0153 | 60.8826 | 122.5433 | 122.7036 | -0.2243 | 122.7219 | 60.9009 | -0.11902 | 122.7036 | -0.2243 | 60.9009 | 122.5433 | 122.7219 | -122.8683 | -122.937
184.0156 | 123.0515 | -60.8322 | 61.9263 | 0.26703 | 0.014526 | 0.015381 | 0.0021362 | 0.062805 | -0.0032044 | 0.072418 | -60.9833 | 61.7935 | -60.8643 | -61.0291 | 61.7889 | 0.064087 | -0.022888 | 0.050354 | 61.8027 | -60.9238 | -0.032044 | -0.13275 | -0.15106 | -0.19684 | -0.13733 | -0.091553 | -0.1236 | -0.11902 | 60.8093 | 60.8826 | 122.6212 | 122.6257 | -0.15106 | 122.6349 | 60.8963 | -0.091553 | 122.6257 | -0.15106 | 60.8963 | 122.6212 | 122.6349 | -122.7905 | -122.85
184.9688 | 122.9736 | -60.8643 | 61.9537 | -1.9836 | 0.015381 | 0.016449 | 0.0066224 | 0.064728 | -0.002777 | 0.070282 | -61.0107 | 61.8759 | -60.8826 | -61.0611 | 61.702 | 0.050354 | 0.16937 | 0.032043 | 61.8805 | -60.9741 | -0.01831 | -0.077819 | -0.14648 | -0.19684 | -0.25177 | -0.10986 | -0.073242 | -0.12817 | 61.0336 | 60.8963 | 122.5662 | 122.7402 | -0.14648 | 122.7448 | 60.9146 | -0.10986 | 122.7402 | -0.14648 | 60.9146 | 122.5662 | 122.7448 | -122.8363 | -122.9279
186.0156 | 123.0743 | -60.8276 | 61.9125 | 0.061035 | 0.012817 | 0.011536 | 0.0021362 | 0.06366 | -0.005127 | 0.070068 | -60.8917 | 61.7981 | -60.8505 | -60.9741 | 61.8301 | 0.18768 | 0 | 0.16479 | 61.8164 | -60.9375 | -0.022888 | -0.11444 | -0.064087 | -0.14648 | -0.082398 | -0.10986 | -0.096131 | -0.041199 | 60.8276 | 60.9924 | 122.6578 | 122.6257 | -0.064087 | 122.644 | 61.0153 | -0.10986 | 122.6257 | -0.064087 | 61.0153 | 122.6578 | 122.644 | -122.7631 | -122.85
186.9688 | 123.0011 | -60.8231 | 61.9354 | 0.038147 | 0.015381 | 0.013886 | 0.0074768 | 0.062805 | -0.0036316 | 0.070923 | -60.9695 | 61.8851 | -60.8871 | -61.0611 | 61.7386 | 0.068665 | 0.14191 | 0.027466 | 61.8576 | -60.9879 | -0.064087 | -0.050354 | -0.14648 | -0.23804 | -0.19684 | -0.16479 | -0.07782 | -0.082397 | 60.965 | 60.8505 | 122.5616 | 122.7081 | -0.14648 | 122.6807 | 60.8917 | -0.16479 | 122.7081 | -0.14648 | 60.8917 | 122.5616 | 122.6807 | -122.8226 | -122.9233
188.0156 | 123.0743 | -60.8276 | 61.908 | 0.33569 | 0.013886 | 0.013031 | -0.0019226 | 0.063446 | -0.0012818 | 0.070496 | -60.965 | 61.8027 | -60.878 | -61.0611 | 61.7615 | 0.064087 | -0.068665 | 0.018311 | 61.8118 | -60.9238 | -0.050354 | -0.10529 | -0.13733 | -0.23346 | -0.14648 | -0.09613 | -0.09613 | -0.086975 | 60.759 | 60.8459 | 122.5891 | 122.6303 | -0.13733 | 122.6395 | 60.8917 | -0.09613 | 122.6303 | -0.13733 | 60.8917 | 122.5891 | 122.6395 | -122.7859 | -122.8317
188.9688 | 122.9965 | -60.8597 | 61.9583 | -0.022889 | 0.015381 | 0.014099 | 0.0038452 | 0.062164 | -0.0057678 | 0.073059 | -60.9192 | 61.8759 | -60.8505 | -61.0794 | 61.7386 | 0.073242 | 0.14648 | 0.032043 | 61.8713 | -60.965 | 0.009155 | -0.082397 | -0.059509 | -0.21973 | -0.21973 | -0.10529 | -0.086975 | -0.068664 | 61.0062 | 60.8917 | 122.5983 | 122.7356 | -0.059509 | 122.731 | 60.9329 | -0.10529 | 122.7356 | -0.059509 | 60.9329 | 122.5983 | 122.731 | -122.8088 | -122.9233
190.0156 | 123.056 | -60.8505 | 61.9217 | 0.18311 | 0.012177 | 0.014954 | 0.001709 | 0.064941 | -0.0038452 | 0.071991 | -60.9741 | 61.8027 | -60.8734 | -61.0474 | 61.7706 | 0.068665 | -0.045776 | 0.036621 | 61.8256 | -60.9558 | -0.022888 | -0.11902 | -0.1236 | -0.19684 | -0.15106 | -0.10529 | -0.09613 | -0.10071 | 60.8047 | 60.8871 | 122.6212 | 122.6532 | -0.1236 | 122.6761 | 60.9192 | -0.10529 | 122.6532 | -0.1236 | 60.9192 | 122.6212 | 122.6761 | -122.7951 | -122.8775
190.9688 | 122.9782 | -60.8505 | 61.9629 | 0.068664 | 0.016022 | 0.014954 | 0.005127 | 0.064728 | -0.0036316 | 0.072418 | -60.9879 | 61.8439 | -60.9055 | -61.0657 | 61.7294 | 0.068665 | 0.14191 | 0.018311 | 61.8622 | -60.9558 | -0.054932 | -0.11902 | -0.13733 | -0.21515 | -0.23346 | -0.10529 | -0.10071 | -0.082397 | 60.9924 | 60.8688 | 122.58 | 122.6944 | -0.13733 | 122.7127 | 60.9192 | -0.10529 | 122.6944 | -0.13733 | 60.9192 | 122.58 | 122.7127 | -122.8683 | -122.9187
192.0156 | 123.0469 | -60.8368 | 61.9034 | 0.42725 | 0.016022 | 0.017304 | -0.0002136 | 0.063873 | -0.004486 | 0.071777 | -60.965 | 61.7981 | -60.8688 | -61.0611 | 61.7752 | 0.068665 | -0.045776 | 0.036621 | 61.7981 | -60.9558 | -0.032043 | -0.10529 | -0.12817 | -0.2243 | -0.12817 | -0.11902 | -0.10529 | -0.096131 | 60.791 | 60.8734 | 122.612 | 122.6349 | -0.12817 | 122.6349 | 60.9055 | -0.11902 | 122.6349 | -0.12817 | 60.9055 | 122.612 | 122.6349 | -122.7722 | -122.8592
192.9688 | 122.9782 | -60.8597 | 61.9354 | 0.25177 | 0.016022 | 0.01474 | 0.0087586 | 0.0643 | -0.0046996 | 0.070068 | -60.9558 | 61.8759 | -60.9055 | -61.0886 | 61.7203 | 0 | 0.059509 | -0.050354 | 61.8668 | -60.997 | -0.045777 | -0.059509 | -0.096131 | -0.22888 | -0.21515 | -0.13733 | -0.068665 | -0.050354 | 60.9192 | 60.8093 | 122.58 | 122.7356 | -0.096131 | 122.7264 | 60.8597 | -0.13733 | 122.7356 | -0.096131 | 60.8597 | 122.58 | 122.7264 | -122.8409 | -122.9324
194.0156 | 123.0515 | -60.8505 | 61.8988 | 0.30518 | 0.015167 | 0.015808 | 0.0012818 | 0.064087 | -0.0038452 | 0.070923 | -60.9695 | 61.7798 | -60.8643 | -61.0474 | 61.7798 | 0.050354 | -0.09613 | 0.009155 | 61.8027 | -60.9879 | -0.013733 | -0.11902 | -0.11902 | -0.19684 | -0.11902 | -0.13733 | -0.096131 | -0.10529 | 60.7544 | 60.8597 | 122.6303 | 122.6303 | -0.11902 | 122.6532 | 60.9009 | -0.13733 | 122.6303 | -0.11902 | 60.9009 | 122.6303 | 122.6532 | -122.7631 | -122.8867
194.9688 | 122.9691 | -60.8551 | 61.9629 | -0.083923 | 0.013672 | 0.011322 | 0.0059816 | 0.064087 | -0.003418 | 0.070709 | -61.0016 | 61.8759 | -60.8734 | -61.0703 | 61.734 | 0.07782 | 0.15106 | 0.032043 | 61.8622 | -60.9558 | -0.01831 | -0.086975 | -0.14648 | -0.21515 | -0.22888 | -0.10071 | -0.10071 | -0.12817 | 61.0062 | 60.8871 | 122.5891 | 122.731 | -0.14648 | 122.7173 | 60.9329 | -0.10071 | 122.731 | -0.14648 | 60.9329 | 122.5891 | 122.7173 | -122.8363 | -122.9187
196.0156 | 123.0652 | -60.8459 | 61.8988 | 0.33569 | 0.014526 | 0.016663 | -0.0012816 | 0.065796 | -0.0023498 | 0.070282 | -60.9467 | 61.7752 | -60.878 | -61.0336 | 61.7798 | 0.045776 | -0.10071 | 0.022888 | 61.7798 | -60.9695 | -0.032044 | -0.1236 | -0.10071 | -0.18768 | -0.11902 | -0.1236 | -0.11902 | -0.068664 | 60.7452 | 60.8688 | 122.6257 | 122.6212 | -0.10071 | 122.6257 | 60.8917 | -0.1236 | 122.6212 | -0.10071 | 60.8917 | 122.6257 | 122.6257 | -122.7768 | -122.8683
196.9688 | 123.0194 | -60.8231 | 61.9629 | 0.053405 | 0.015808 | 0.015808 | 0.0076904 | 0.062591 | -0.0038452 | 0.07135 | -60.9695 | 61.8759 | -60.8688 | -61.0519 | 61.7386 | 0.082397 | 0.13733 | 0.041199 | 61.8759 | -60.9695 | -0.045776 | -0.086975 | -0.14648 | -0.22888 | -0.22431 | -0.14648 | -0.086975 | -0.10071 | 60.9604 | 60.8643 | 122.5616 | 122.699 | -0.14648 | 122.699 | 60.9055 | -0.14648 | 122.699 | -0.14648 | 60.9055 | 122.5616 | 122.699 | -122.8317 | -122.9324
198.0156 | 123.056 | -60.8459 | 61.9308 | 0.24414 | 0.015167 | 0.01004 | 0.0025636 | 0.064728 | -0.001709 | 0.071777 | -60.9833 | 61.8118 | -60.8734 | -61.0565 | 61.7615 | 0.054932 | -0.045776 | 0.036621 | 61.8073 | -60.9604 | -0.027466 | -0.11902 | -0.13733 | -0.21057 | -0.16937 | -0.11444 | -0.1236 | -0.10986 | 60.8002 | 60.8826 | 122.6074 | 122.6578 | -0.13733 | 122.6532 | 60.9009 | -0.11444 | 122.6578 | -0.13733 | 60.9009 | 122.6074 | 122.6532 | -122.8043 | -122.8912
198.9688 | 122.9736 | -60.8688 | 61.9904 | 0.038147 | 0.016663 | 0.013245 | 0.0027772 | 0.065796 | -0.0029906 | 0.070068 | -60.9833 | 61.8622 | -60.8826 | -61.0611 | 61.734 | 0.073242 | 0.15106 | 0.041199 | 61.853 | -60.9787 | -0.013733 | -0.12817 | -0.11444 | -0.19226 | -0.25635 | -0.10986 | -0.13733 | -0.10071 | 61.0199 | 60.91 | 122.6028 | 122.731 | -0.11444 | 122.7219 | 60.9421 | -0.10986 | 122.731 | -0.11444 | 60.9421 | 122.6028 | 122.7219 | -122.8729 | -122.9691
200.0156 | 123.0286 | -60.8368 | 61.9125 | 0.30518 | 0.015808 | 0.015167 | 0.000641 | 0.063873 | -0.0066222 | 0.07135 | -60.9512 | 61.8027 | -60.8688 | -61.0519 | 61.7615 | 0.027466 | -0.07782 | 0.004578 | 61.8118 | -60.9741 | -0.032043 | -0.10986 | -0.11444 | -0.21515 | -0.15106 | -0.13733 | -0.10071 | -0.082398 | 60.759 | 60.8414 | 122.5983 | 122.6395 | -0.11444 | 122.6486 | 60.8643 | -0.13733 | 122.6395 | -0.11444 | 60.8643 | 122.5983 | 122.6486 | -122.7814 | -122.8867
200.9688 | 122.9691 | -60.8597 | 61.9492 | 0.16022 | 0.013886 | 0.012177 | 0.0036316 | 0.066009 | -0.0042724 | 0.073486 | -60.9833 | 61.8576 | -60.9375 | -61.0794 | 61.7203 | 0.064087 | 0.16022 | 0.022888 | 61.8713 | -60.9787 | -0.07782 | -0.091553 | -0.1236 | -0.21973 | -0.22888 | -0.11902 | -0.07782 | -0.045776 | 61.0199 | 60.8826 | 122.58 | 122.7173 | -0.1236 | 122.731 | 60.9238 | -0.11902 | 122.7173 | -0.1236 | 60.9238 | 122.58 | 122.731 | -122.8867 | -122.9279
201.9688 | 123.0148 | -60.8643 | 61.9354 | 0.022888 | 0.014313 | 0.017731 | 0.0057678 | 0.063873 | -0.0059814 | 0.070923 | -60.9741 | 61.8622 | -60.9009 | -61.0611 | 61.7523 | 0.073242 | 0.14648 | 0.032043 | 61.8713 | -60.9695 | -0.036621 | -0.073242 | -0.10986 | -0.19684 | -0.18311 | -0.10529 | -0.064087 | -0.073242 | 61.0107 | 60.8963 | 122.6166 | 122.7264 | -0.10986 | 122.7356 | 60.9375 | -0.10529 | 122.7264 | -0.10986 | 60.9375 | 122.6166 | 122.7356 | -122.8363 | -122.905
202.9688 | 122.9691 | -60.8643 | 61.972 | 0 | 0.015808 | 0.014099 | 0.0008546 | 0.064941 | -0.0040588 | 0.071564 | -60.997 | 61.908 | -60.8871 | -61.0565 | 61.7386 | 0.059509 | 0.15106 | 0.027466 | 61.8668 | -60.9558 | -0.022888 | -0.064087 | -0.13275 | -0.19226 | -0.23346 | -0.091553 | -0.10529 | -0.10986 | 61.0153 | 60.8917 | 122.6028 | 122.7722 | -0.13275 | 122.731 | 60.9238 | -0.091553 | 122.7722 | -0.13275 | 60.9238 | 122.6028 | 122.731 | -122.8592 | -122.9279
204.0156 | 123.0881 | -60.8231 | 61.908 | 0.36621 | 0.015167 | 0.017304 | 0.000641 | 0.067932 | -0.0023498 | 0.071777 | -60.9329 | 61.8027 | -60.8643 | -61.0016 | 61.7981 | 0.064087 | -0.13733 | 0.032043 | 61.7844 | -60.9695 | -0.041199 | -0.10529 | -0.10986 | -0.17853 | -0.10986 | -0.14648 | -0.1236 | -0.068664 | 60.6857 | 60.8551 | 122.6212 | 122.6257 | -0.10986 | 122.6074 | 60.8871 | -0.14648 | 122.6257 | -0.10986 | 60.8871 | 122.6212 | 122.6074 | -122.7722 | -122.8775
204.9688 | 123.0515 | -60.8276 | 61.9446 | 0.022888 | 0.015595 | 0.015808 | 0.0029908 | 0.066009 | -0.004486 | 0.07135 | -60.9055 | 61.7889 | -60.8597 | -60.9695 | 61.8347 | 0.16479 | 0.022888 | 0.15564 | 61.8347 | -60.9283 | -0.032043 | -0.15564 | -0.07782 | -0.14191 | -0.10986 | -0.10071 | -0.10986 | -0.045777 | 60.8505 | 60.9833 | 122.6624 | 122.6166 | -0.07782 | 122.6624 | 60.9924 | -0.10071 | 122.6166 | -0.07782 | 60.9924 | 122.6624 | 122.6624 | -122.8043 | -122.8729
206.0156 | 123.0789 | -60.8276 | 61.9446 | 0.32043 | 0.016449 | 0.012604 | -0.0002136 | 0.06366 | -0.0029906 | 0.072418 | -60.9695 | 61.7935 | -60.8551 | -61.0611 | 61.7432 | 0.059509 | -0.059509 | 0.032043 | 61.8164 | -60.9604 | -0.027466 | -0.15106 | -0.14191 | -0.23346 | -0.20142 | -0.13275 | -0.12817 | -0.11444 | 60.7681 | 60.8597 | 122.5708 | 122.6212 | -0.14191 | 122.644 | 60.8871 | -0.13275 | 122.6212 | -0.14191 | 60.8871 | 122.5708 | 122.644 | -122.7997 | -122.905
206.9688 | 123.0103 | -60.8505 | 61.9492 | 0.14496 | 0.016022 | 0.01709 | 0.0061952 | 0.06366 | -0.006195 | 0.069855 | -60.9238 | 61.8393 | -60.8688 | -61.0245 | 61.7523 | 0.050354 | 0.054932 | 0.022888 | 61.8393 | -60.9741 | -0.01831 | -0.10986 | -0.073242 | -0.17395 | -0.19684 | -0.1236 | -0.10986 | -0.054932 | 60.9055 | 60.8734 | 122.6028 | 122.6898 | -0.073242 | 122.6898 | 60.9009 | -0.1236 | 122.6898 | -0.073242 | 60.9009 | 122.6028 | 122.6898 | -122.818 | -122.9233
208.0156 | 123.0606 | -60.8139 | 61.9034 | 0.23651 | 0.014526 | 0.01239 | -0.0014952 | 0.063873 | -0.0019226 | 0.072418 | -60.9558 | 61.7935 | -60.8917 | -61.0153 | 61.8073 | 0.1236 | -0.022888 | 0.091553 | 61.8164 | -60.9695 | -0.07782 | -0.10986 | -0.14191 | -0.20142 | -0.09613 | -0.15564 | -0.086975 | -0.064087 | 60.791 | 60.9055 | 122.6212 | 122.6074 | -0.14191 | 122.6303 | 60.9375 | -0.15564 | 122.6074 | -0.14191 | 60.9375 | 122.6212 | 122.6303 | -122.7951 | -122.8729
208.9688 | 122.9691 | -60.8459 | 61.94 | -0.091553 | 0.016022 | 0.017517 | 0.0042726 | 0.062164 | -0.005127 | 0.071991 | -60.997 | 61.8759 | -60.8917 | -61.0703 | 61.734 | 0.068665 | 0.16937 | 0.022888 | 61.853 | -60.9695 | -0.045777 | -0.064086 | -0.15106 | -0.2243 | -0.20599 | -0.1236 | -0.086975 | -0.10528 | 61.0153 | 60.8688 | 122.58 | 122.7219 | -0.15106 | 122.699 | 60.9146 | -0.1236 | 122.7219 | -0.15106 | 60.9146 | 122.58 | 122.699 | -122.8317 | -122.9095
209.9688 | 122.9782 | -60.8459 | 61.9766 | 1.3809 | 0.017517 | 0.012604 | 0.006836 | 0.066223 | -0.0057678 | 0.070068 | -61.0519 | 61.853 | -60.91 | -61.0931 | 61.7294 | 0.07782 | 0.16937 | 0.032043 | 61.8759 | -60.9833 | -0.064087 | -0.1236 | -0.20599 | -0.24719 | -0.24719 | -0.13733 | -0.10071 | -0.14191 | 61.0153 | 60.878 | 122.5754 | 122.699 | -0.20599 | 122.7219 | 60.9238 | -0.13733 | 122.699 | -0.20599 | 60.9238 | 122.5754 | 122.7219 | -122.8867 | -122.9599
210.9688 | 123.0972 | -60.7956 | 61.9308 | 0.053405 | 0.013031 | 0.014313 | 0.0014954 | 0.061737 | -0.0046996 | 0.071991 | -60.9146 | 61.7935 | -60.8734 | -60.9787 | 61.8439 | 0.17395 | -0.009155 | 0.16479 | 61.7798 | -60.9421 | -0.07782 | -0.13733 | -0.11902 | -0.18311 | -0.086975 | -0.14649 | -0.15106 | -0.041199 | 60.7864 | 60.9604 | 122.6395 | 122.5891 | -0.11902 | 122.5754 | 60.9695 | -0.14649 | 122.5891 | -0.11902 | 60.9695 | 122.6395 | 122.5754 | -122.8043 | -122.8729
212.0156 | 123.0469 | -60.8551 | 61.8805 | 0.34332 | 0.011322 | 0.013458 | 0.0036316 | 0.0643 | -0.0036316 | 0.073059 | -60.9375 | 61.7569 | -60.8688 | -61.0291 | 61.7889 | 0.068665 | -0.16479 | 0.036621 | 61.7661 | -60.9512 | -0.013732 | -0.1236 | -0.082397 | -0.17395 | -0.091553 | -0.09613 | -0.11444 | -0.068665 | 60.6903 | 60.8917 | 122.644 | 122.612 | -0.082397 | 122.6212 | 60.9238 | -0.09613 | 122.612 | -0.082397 | 60.9238 | 122.644 | 122.6212 | -122.7493 | -122.8317
212.9688 | 122.8958 | -60.8322 | 62.0132 | -0.061036 | 0.014526 | 0.016449 | 0.005127 | 0.061523 | -0.002777 | 0.069641 | -60.997 | 61.8439 | -60.8551 | -61.0748 | 61.7432 | 0.059509 | 0.15564 | 0.045776 | 61.8668 | -60.9512 | -0.022889 | -0.16937 | -0.16479 | -0.24262 | -0.27008 | -0.11902 | -0.14648 | -0.14191 | 60.9879 | 60.878 | 122.5754 | 122.6761 | -0.16479 | 122.699 | 60.8917 | -0.11902 | 122.6761 | -0.16479 | 60.8917 | 122.5754 | 122.699 | -122.8683 | -122.9645
214.0156 | 123.0469 | -60.8597 | 61.8988 | 0.28229 | 0.014954 | 0.0076904 | 0.005127 | 0.062164 | -0.003418 | 0.070282 | -61.0382 | 61.8164 | -60.8459 | -61.0794 | 61.7477 | 0.050354 | -0.041199 | 0.004578 | 61.7981 | -60.9833 | 0.013733 | -0.082398 | -0.17853 | -0.21973 | -0.15106 | -0.1236 | -0.10071 | -0.19226 | 60.8185 | 60.8643 | 122.6074 | 122.6761 | -0.17853 | 122.6578 | 60.91 | -0.1236 | 122.6761 | -0.17853 | 60.91 | 122.6074 | 122.6578 | -122.7448 | -122.8821
214.9688 | 123.0148 | -60.8414 | 61.9537 | -0.038147 | 0.013672 | 0.015808 | 0.0053406 | 0.062164 | -0.0038452 | 0.068787 | -60.9741 | 61.8256 | -60.8643 | -61.0382 | 61.7569 | 0.082397 | 0.14648 | 0.064087 | 61.8851 | -60.9512 | -0.022888 | -0.12817 | -0.13275 | -0.19684 | -0.19684 | -0.10986 | -0.068664 | -0.10986 | 60.9879 | 60.9055 | 122.5983 | 122.6669 | -0.13275 | 122.7264 | 60.9238 | -0.10986 | 122.6669 | -0.13275 | 60.9238 | 122.5983 | 122.7264 | -122.818 | -122.905
216.0156 | 123.0789 | -60.8459 | 61.8942 | 0.34332 | 0.016022 | 0.013245 | 0.0029908 | 0.065369 | -0.0053406 | 0.070709 | -60.9421 | 61.7661 | -60.8734 | -61.0336 | 61.7615 | 0.050354 | -0.12817 | 0.027466 | 61.7981 | -60.9421 | -0.027466 | -0.12817 | -0.096131 | -0.18768 | -0.13275 | -0.096131 | -0.09613 | -0.068665 | 60.7178 | 60.8734 | 122.6074 | 122.612 | -0.096131 | 122.644 | 60.8963 | -0.096131 | 122.612 | -0.096131 | 60.8963 | 122.6074 | 122.644 | -122.7676 | -122.8363
216.9688 | 122.9828 | -60.8643 | 61.9537 | -0.022889 | 0.013886 | 0.013245 | 0.0061952 | 0.063019 | -0.0040588 | 0.070709 | -60.9879 | 61.8301 | -60.8826 | -61.0657 | 61.6745 | 0.041199 | 0.18768 | 0.032043 | 61.8759 | -60.9879 | -0.01831 | -0.1236 | -0.1236 | -0.20142 | -0.27923 | -0.1236 | -0.077819 | -0.10529 | 61.0519 | 60.8963 | 122.5388 | 122.6944 | -0.1236 | 122.7402 | 60.9055 | -0.1236 | 122.6944 | -0.1236 | 60.9055 | 122.5388 | 122.7402 | -122.8363 | -122.9416
218.0156 | 123.0331 | -60.8459 | 61.9125 | 0.32806 | 0.014313 | 0.012177 | 0.0008546 | 0.063873 | -0.006195 | 0.070282 | -60.9833 | 61.7981 | -60.8688 | -61.0565 | 61.7798 | 0.050354 | -0.073242 | 0.004578 | 61.8164 | -60.9604 | -0.022888 | -0.11444 | -0.13733 | -0.21057 | -0.13275 | -0.11444 | -0.096131 | -0.11444 | 60.7727 | 60.8505 | 122.6257 | 122.644 | -0.13733 | 122.6624 | 60.8963 | -0.11444 | 122.644 | -0.13733 | 60.8963 | 122.6257 | 122.6624 | -122.7814 | -122.8729
218.9688 | 123.0103 | -60.8185 | 62.0178 | 0 | 0.013886 | 0.013458 | 0.0061952 | 0.062378 | -0.0029906 | 0.070496 | -60.997 | 61.853 | -60.8826 | -61.0565 | 61.7294 | 0.064087 | 0.16937 | 0.054932 | 61.8713 | -60.9787 | -0.064087 | -0.1648 | -0.17853 | -0.23804 | -0.28839 | -0.16022 | -0.14648 | -0.11444 | 60.9879 | 60.8734 | 122.5479 | 122.6715 | -0.17853 | 122.6898 | 60.8826 | -0.16022 | 122.6715 | -0.17853 | 60.8826 | 122.5479 | 122.6898 | -122.9004 | -122.9965
219.9688 | 122.9874 | -60.8551 | 61.9629 | 0.030518 | 0.015808 | 0.012604 | 0.0053406 | 0.064087 | -0.0042724 | 0.069427 | -60.9924 | 61.8713 | -60.8917 | -61.0703 | 61.734 | 0.059509 | 0.16937 | 0.032043 | 61.8576 | -60.9695 | -0.036621 | -0.091553 | -0.13733 | -0.21515 | -0.22888 | -0.11444 | -0.10529 | -0.10071 | 61.0245 | 60.8871 | 122.5891 | 122.7264 | -0.13733 | 122.7127 | 60.9146 | -0.11444 | 122.7264 | -0.13733 | 60.9146 | 122.5891 | 122.7127 | -122.8546 | -122.9324
221.0156 | 123.0606 | -60.8276 | 61.8896 | 0.36621 | 0.016235 | 0.014099 | 0.0010682 | 0.061096 | -0.0049134 | 0.072632 | -60.9467 | 61.7615 | -60.878 | -61.0474 | 61.7752 | 0.041199 | -0.10529 | 0.027466 | 61.8027 | -60.9741 | -0.050354 | -0.12817 | -0.11902 | -0.21973 | -0.11444 | -0.14648 | -0.086975 | -0.068664 | 60.7224 | 60.8551 | 122.6028 | 122.5891 | -0.11902 | 122.6303 | 60.8688 | -0.14648 | 122.5891 | -0.11902 | 60.8688 | 122.6028 | 122.6303 | -122.7676 | -122.8638
221.9688 | 122.9691 | -60.8688 | 61.9812 | -0.19073 | 0.017944 | 0.016449 | 0.0055542 | 0.064087 | -0.0059814 | 0.070709 | -61.1298 | 61.8713 | -60.91 | -61.0794 | 61.7203 | 0.07782 | 0.16937 | 0.022888 | 61.8942 | -60.9558 | -0.041199 | -0.10986 | -0.26093 | -0.21057 | -0.26093 | -0.086976 | -0.086975 | -0.21973 | 61.0382 | 60.8917 | 122.5891 | 122.7402 | -0.26093 | 122.7631 | 60.9467 | -0.086976 | 122.7402 | -0.26093 | 60.9467 | 122.5891 | 122.7631 | -122.8912 | -122.937
222.9688 | 122.9553 | -60.8505 | 61.972 | -0.022889 | 0.015808 | 0.016449 | 0.0042726 | 0.063232 | -0.0042724 | 0.071777 | -60.9924 | 61.8851 | -60.9009 | -61.1023 | 61.7706 | 0.068665 | 0.16937 | 0.050354 | 61.8668 | -60.9741 | -0.050354 | -0.086975 | -0.14191 | -0.25177 | -0.20142 | -0.1236 | -0.10529 | -0.091553 | 61.0199 | 60.9009 | 122.6212 | 122.7356 | -0.14191 | 122.7173 | 60.9192 | -0.1236 | 122.7356 | -0.14191 | 60.9192 | 122.6212 | 122.7173 | -122.8729 | -122.9462
224.0156 | 123.0743 | -60.8505 | 61.8759 | 0.45776 | 0.014526 | 0.013886 | 0.0083314 | 0.064087 | -0.002777 | 0.070496 | -60.9512 | 61.7844 | -60.9146 | -61.0428 | 61.7706 | 0.041199 | -0.13275 | -0.022888 | 61.8073 | -60.9879 | -0.064087 | -0.091553 | -0.10071 | -0.19226 | -0.10529 | -0.13733 | -0.068665 | -0.036621 | 60.7178 | 60.8276 | 122.6212 | 122.6349 | -0.10071 | 122.6578 | 60.8917 | -0.13733 | 122.6349 | -0.10071 | 60.8917 | 122.6212 | 122.6578 | -122.7905 | -122.8638
224.9688 | 123.0331 | -60.8414 | 61.94 | -0.030518 | 0.013886 | 0.011536 | -0.0004272 | 0.063019 | -0.0036316 | 0.070923 | -60.9329 | 61.8164 | -60.8643 | -61.0062 | 61.8164 | 0.14648 | 0.068665 | 0.14191 | 61.8118 | -60.9192 | -0.022888 | -0.1236 | -0.091552 | -0.1648 | -0.1236 | -0.077819 | -0.12817 | -0.068664 | 60.91 | 60.9833 | 122.6578 | 122.6578 | -0.091552 | 122.6532 | 60.9879 | -0.077819 | 122.6578 | -0.091552 | 60.9879 | 122.6578 | 122.6532 | -122.8043 | -122.8592
226.0156 | 123.024 | -60.8551 | 61.908 | 0.27466 | 0.014313 | 0.014099 | 0.0029908 | 0.063232 | -0.002777 | 0.071991 | -60.9695 | 61.7615 | -60.8643 | -61.0748 | 61.7523 | 0.068665 | -0.059509 | 0.013733 | 61.821 | -60.9512 | -0.009155 | -0.14648 | -0.11444 | -0.21973 | -0.15564 | -0.09613 | -0.086975 | -0.10529 | 60.7956 | 60.8688 | 122.6074 | 122.6166 | -0.11444 | 122.6761 | 60.9238 | -0.09613 | 122.6166 | -0.11444 | 60.9238 | 122.6074 | 122.6761 | -122.7722 | -122.8592
226.9688 | 123.0927 | -60.8047 | 61.9537 | 0.015259 | 0.014954 | 0.012604 | 0.00235 | 0.063232 | -0.0038452 | 0.070496 | -60.91 | 61.7706 | -60.8551 | -60.9512 | 61.8439 | 0.16022 | 0.022888 | 0.17853 | 61.8256 | -60.9283 | -0.050354 | -0.18311 | -0.10529 | -0.14648 | -0.10986 | -0.1236 | -0.12817 | -0.054931 | 60.8276 | 60.9833 | 122.6486 | 122.5754 | -0.10529 | 122.6303 | 60.965 | -0.1236 | 122.5754 | -0.10529 | 60.965 | 122.6486 | 122.6303 | -122.8088 | -122.8821
228.0156 | 122.9782 | -60.8185 | 61.9125 | 0.26703 | 0.016022 | 0.015381 | 0.003418 | 0.062805 | -0.0074768 | 0.070923 | -60.9604 | 61.7889 | -60.8688 | -61.0565 | 61.7615 | 0.050354 | -0.059509 | 0.027466 | 61.821 | -60.9695 | -0.050354 | -0.1236 | -0.14191 | -0.23804 | -0.15106 | -0.15106 | -0.091553 | -0.091553 | 60.759 | 60.8459 | 122.58 | 122.6074 | -0.14191 | 122.6395 | 60.8688 | -0.15106 | 122.6074 | -0.14191 | 60.8688 | 122.58 | 122.6395 | -122.7814 | -122.8821
228.9688 | 123.0194 | -60.8688 | 61.94 | 0.14496 | 0.017731 | 0.01944 | 0.010468 | 0.064941 | -0.0055542 | 0.071564 | -60.9421 | 61.8301 | -60.8917 | -61.0199 | 61.7523 | 0.054932 | 0.032043 | 0.013733 | 61.8439 | -60.9604 | -0.022889 | -0.10986 | -0.073243 | -0.15106 | -0.18768 | -0.091553 | -0.09613 | -0.050354 | 60.9009 | 60.8826 | 122.6212 | 122.699 | -0.073243 | 122.7127 | 60.9238 | -0.091553 | 122.699 | -0.073243 | 60.9238 | 122.6212 | 122.7127 | -122.8317 | -122.9004
230.0156 | 123.0789 | -60.8459 | 61.8988 | 0.41962 | 0.014954 | 0.015167 | 0.0025636 | 0.063446 | -0.0055542 | 0.073059 | -60.8047 | 61.7889 | -60.8917 | -60.9695 | 61.8164 | 0.068665 | -0.17853 | 0.050354 | 61.7615 | -60.9558 | -0.045777 | -0.10986 | 0.041198 | -0.1236 | -0.082398 | -0.10986 | -0.13733 | 0.086975 | 60.6674 | 60.8963 | 122.6624 | 122.6349 | 0.041198 | 122.6074 | 60.9146 | -0.10986 | 122.6349 | 0.041198 | 60.9146 | 122.6624 | 122.6074 | -122.7905 | -122.8546
230.9844 | 122.9736 | -60.878 | 61.9629 | 0.32043 | 0.014313 | 0.015167 | 0.008545 | 0.067291 | -0.0021362 | 0.067718 | -61.0474 | 61.8622 | -60.8871 | -60.8871 | 61.734 | -0.036621 | 0.050354 | -0.10071 | 61.8484 | -61.0199 | -0.009155 | -0.10071 | -0.16937 | -0.009155 | -0.22888 | -0.14191 | -0.11444 | -0.16022 | 60.9283 | 60.7773 | 122.612 | 122.7402 | -0.16937 | 122.7264 | 60.8414 | -0.14191 | 122.7402 | -0.16937 | 60.8414 | 122.612 | 122.7264 | -122.85 | -122.9828
232.0156 | 123.0972 | -60.8414 | 61.8851 | 0.34332 | 0.015167 | 0.015808 | 0.0044862 | 0.063232 | -0.003418 | 0.072632 | -60.9375 | 61.7935 | -60.9055 | -61.0062 | 61.7935 | 0.07782 | -0.15106 | 0.018311 | 61.7706 | -60.9558 | -0.064087 | -0.091553 | -0.09613 | -0.1648 | -0.091553 | -0.11444 | -0.11444 | -0.032043 | 60.6903 | 60.8597 | 122.6349 | 122.6349 | -0.09613 | 122.612 | 60.9192 | -0.11444 | 122.6349 | -0.09613 | 60.9192 | 122.6349 | 122.612 | -122.7905 | -122.8409
232.9688 | 123.0972 | -60.8139 | 61.9308 | 0.053405 | 0.012817 | 0.011536 | 0.0008546 | 0.063446 | -0.0040588 | 0.072205 | -60.8917 | 61.8118 | -60.8505 | -60.9695 | 61.8393 | 0.16937 | 0.004578 | 0.16937 | 61.8027 | -60.9421 | -0.036621 | -0.11902 | -0.07782 | -0.15564 | -0.091553 | -0.12817 | -0.12817 | -0.041199 | 60.8185 | 60.9833 | 122.6532 | 122.6257 | -0.07782 | 122.6166 | 60.9833 | -0.12817 | 122.6257 | -0.07782 | 60.9833 | 122.6532 | 122.6166 | -122.7814 | -122.8729
234.0156 | 123.0331 | -60.8505 | 61.9171 | 0.32043 | 0.015381 | 0.014099 | 0.001709 | 0.066437 | -0.0036316 | 0.070068 | -60.9833 | 61.7706 | -60.8551 | -61.0565 | 61.7706 | 0.045776 | -0.07782 | 0.018311 | 61.8164 | -60.9695 | -0.004578 | -0.14648 | -0.13275 | -0.20599 | -0.14648 | -0.11902 | -0.10071 | -0.12817 | 60.7727 | 60.8688 | 122.6212 | 122.6212 | -0.13275 | 122.6669 | 60.8963 | -0.11902 | 122.6212 | -0.13275 | 60.8963 | 122.6212 | 122.6669 | -122.7722 | -122.8867
234.9688 | 123.111 | -60.791 | 61.9263 | 2.2354 | 0.014313 | 0.01004 | 0.0029908 | 0.061523 | -0.0042724 | 0.070709 | -60.8826 | 61.7294 | -60.8734 | -60.9512 | 61.8759 | 0.19226 | -0.032043 | 0.17853 | 61.8439 | -60.9055 | -0.082397 | -0.19684 | -0.091552 | -0.16022 | -0.050354 | -0.11444 | -0.082398 | -0.009155 | 60.759 | 60.9695 | 122.6669 | 122.5204 | -0.091552 | 122.6349 | 60.9833 | -0.11444 | 122.5204 | -0.091552 | 60.9833 | 122.6669 | 122.6349 | -122.7997 | -122.8317
236.0312 | 123.0194 | -60.8459 | 61.9858 | 0.007629 | 0.016663 | 0.013458 | 0.0066224 | 0.063446 | -0.006195 | 0.068359 | -60.9604 | 61.8759 | -60.8917 | -61.0382 | 61.7432 | 0.073242 | 0.14648 | 0.050354 | 61.8896 | -60.965 | -0.045777 | -0.10986 | -0.11444 | -0.19226 | -0.24262 | -0.11902 | -0.096131 | -0.068664 | 60.9924 | 60.8963 | 122.5891 | 122.7219 | -0.11444 | 122.7356 | 60.9192 | -0.11902 | 122.7219 | -0.11444 | 60.9192 | 122.5891 | 122.7356 | -122.8775 | -122.9507
236.9688 | 122.9919 | -60.8414 | 61.9583 | 0 | 0.016449 | 0.013886 | 0.0066224 | 0.065796 | -0.0057678 | 0.07135 | -60.9879 | 61.853 | -60.8963 | -61.0245 | 61.7569 | 0.068665 | 0.13733 | 0.050354 | 61.8393 | -60.9833 | -0.054931 | -0.10529 | -0.14648 | -0.18311 | -0.20142 | -0.14191 | -0.11902 | -0.091553 | 60.9787 | 60.8917 | 122.5983 | 122.6944 | -0.14648 | 122.6807 | 60.91 | -0.14191 | 122.6944 | -0.14648 | 60.91 | 122.5983 | 122.6807 | -122.8546 | -122.9416
238.0156 | 123.0331 | -60.8505 | 61.9034 | 0.41962 | 0.01709 | 0.016449 | 0.0057678 | 0.065796 | -0.0036316 | 0.068787 | -61.0016 | 61.8027 | -60.9375 | -61.0657 | 61.7432 | 0 | -0.082397 | -0.018311 | 61.8073 | -60.9467 | -0.086975 | -0.10071 | -0.15106 | -0.21515 | -0.16022 | -0.09613 | -0.09613 | -0.064087 | 60.7681 | 60.8322 | 122.5937 | 122.6532 | -0.15106 | 122.6578 | 60.8505 | -0.09613 | 122.6532 | -0.15106 | 60.8505 | 122.5937 | 122.6578 | -122.8409 | -122.85
238.9688 | 123.1155 | -60.8093 | 61.9125 | 0.015259 | 0.011749 | 0.014099 | 0.0012818 | 0.056824 | -0.005127 | 0.071777 | -60.8963 | 61.8073 | -60.8688 | -61.0931 | 61.5921 | 0.09613 | -0.14648 | 0.16022 | 61.7798 | -60.9375 | -0.059509 | -0.10529 | -0.086975 | -0.28381 | -0.32044 | -0.12817 | -0.13275 | -0.027466 | 60.6628 | 60.9695 | 122.4014 | 122.6166 | -0.086975 | 122.5891 | 60.9055 | -0.12817 | 122.6166 | -0.086975 | 60.9055 | 122.4014 | 122.5891 | -122.7814 | -122.85
240.0156 | 123.0698 | -60.8505 | 61.8942 | 0.4425 | 0.013886 | 0.016449 | 0.0042726 | 0.063873 | -0.0057678 | 0.072205 | -61.1389 | 61.7249 | -60.91 | -61.0199 | 61.7844 | 0.068665 | -0.15106 | 0.050354 | 61.7752 | -60.9421 | -0.059509 | -0.16937 | -0.28839 | -0.16937 | -0.10986 | -0.091553 | -0.11902 | -0.22888 | 60.6995 | 60.9009 | 122.6349 | 122.5754 | -0.28839 | 122.6257 | 60.9192 | -0.091553 | 122.5754 | -0.28839 | 60.9192 | 122.6349 | 122.6257 | -122.8043 | -122.8363
240.9844 | 123.0011 | -60.8414 | 61.9446 | 0.13733 | 0.014099 | 0.01944 | 0.010254 | 0.06366 | -0.0029906 | 0.069 | -60.9283 | 61.8805 | -60.8734 | -61.0291 | 61.7523 | 0.073242 | 0.027466 | 0.018311 | 61.8347 | -61.0016 | -0.032043 | -0.064087 | -0.086975 | -0.18768 | -0.19226 | -0.16022 | -0.10986 | -0.054932 | 60.8688 | 60.8597 | 122.5937 | 122.7219 | -0.086975 | 122.6761 | 60.9146 | -0.16022 | 122.7219 | -0.086975 | 60.9146 | 122.5937 | 122.6761 | -122.818 | -122.9462
242.0156 | 123.0881 | -60.8459 | 61.8942 | 0.43488 | 0.01474 | 0.013245 | 0.004059 | 0.065369 | -0.0040588 | 0.072632 | -60.9558 | 61.7798 | -60.9192 | -61.0291 | 61.7889 | 0.059509 | -0.13733 | 0.032043 | 61.8073 | -60.9512 | -0.073242 | -0.11444 | -0.10986 | -0.18311 | -0.10529 | -0.10529 | -0.086975 | -0.036622 | 60.7086 | 60.878 | 122.6349 | 122.6257 | -0.10986 | 122.6532 | 60.9055 | -0.10529 | 122.6257 | -0.10986 | 60.9055 | 122.6349 | 122.6532 | -122.8134 | -122.8455
242.9688 | 123.111 | -60.7864 | 61.908 | 0.12207 | 0.012817 | 0.013458 | -0.0002136 | 0.064514 | -0.0046996 | 0.070282 | -60.9192 | 61.7615 | -60.8688 | -60.9741 | 61.8622 | 0.16479 | -0.045776 | 0.17853 | 61.8073 | -60.8963 | -0.082397 | -0.14648 | -0.13275 | -0.18768 | -0.045776 | -0.10986 | -0.10071 | -0.050354 | 60.7407 | 60.965 | 122.6486 | 122.5479 | -0.13275 | 122.5937 | 60.9512 | -0.10986 | 122.5479 | -0.13275 | 60.9512 | 122.6486 | 122.5937 | -122.7768 | -122.8043
244.0156 | 123.0789 | -60.8093 | 61.8576 | 0.41962 | 0.013031 | 0.013458 | 0.0032044 | 0.063232 | -0.0053406 | 0.071564 | -60.9512 | 61.7889 | -60.8917 | -61.0062 | 61.7798 | 0.059509 | -0.15106 | 0.013733 | 61.8027 | -60.9467 | -0.082398 | -0.068665 | -0.14191 | -0.19684 | -0.07782 | -0.13733 | -0.054932 | -0.059509 | 60.6583 | 60.8231 | 122.5891 | 122.5983 | -0.14191 | 122.612 | 60.8688 | -0.13733 | 122.5983 | -0.14191 | 60.8688 | 122.5891 | 122.612 | -122.7493 | -122.8043
244.9688 | 122.9874 | -60.8505 | 61.9629 | 0.030518 | 0.014526 | 0.010254 | 0.0044862 | 0.063019 | -0.0055542 | 0.071564 | -60.997 | 61.8256 | -60.8826 | -61.0519 | 61.734 | 0.082397 | 0.16022 | 0.064087 | 61.8622 | -60.965 | -0.032043 | -0.13733 | -0.14648 | -0.20142 | -0.22888 | -0.11444 | -0.10071 | -0.11444 | 61.0107 | 60.9146 | 122.5845 | 122.6761 | -0.14648 | 122.7127 | 60.9329 | -0.11444 | 122.6761 | -0.14648 | 60.9329 | 122.5845 | 122.7127 | -122.8455 | -122.9279
246.0312 | 123.0148 | -60.8322 | 61.9537 | 0.19836 | 0.016449 | 0.013245 | 0.0064088 | 0.064941 | -0.0074768 | 0.070496 | -60.9375 | 61.8118 | -60.8871 | -61.0153 | 61.7615 | 0.073242 | 0.036621 | 0.032043 | 61.8759 | -60.9512 | -0.054932 | -0.14191 | -0.10529 | -0.18311 | -0.19226 | -0.11902 | -0.077819 | -0.050354 | 60.8688 | 60.8643 | 122.5937 | 122.644 | -0.10529 | 122.7081 | 60.9055 | -0.11902 | 122.644 | -0.10529 | 60.9055 | 122.5937 | 122.7081 | -122.8409 | -122.905
246.9688 | 123.0423 | -60.8414 | 61.9034 | 0.34332 | 0.015595 | 0.014313 | -0.0002136 | 0.064728 | -0.0012818 | 0.070496 | -60.9787 | 61.7798 | -60.878 | -61.0611 | 61.7661 | 0.050354 | -0.045776 | 0.027466 | 61.8164 | -60.9604 | -0.036621 | -0.1236 | -0.13733 | -0.21973 | -0.13733 | -0.11902 | -0.086975 | -0.10071 | 60.7956 | 60.8688 | 122.6074 | 122.6212 | -0.13733 | 122.6578 | 60.8917 | -0.11902 | 122.6212 | -0.13733 | 60.8917 | 122.6074 | 122.6578 | -122.7814 | -122.8638
248.0156 | 122.9279 | -60.8505 | 61.9217 | 0.23651 | 0.012817 | 0.017944 | 0.0074768 | 0.064087 | -0.0042724 | 0.070282 | -61.0199 | 61.8164 | -60.9283 | -61.116 | 61.6882 | -0.045776 | 0.054932 | -0.09613 | 61.8301 | -60.9833 | -0.07782 | -0.10529 | -0.16937 | -0.2655 | -0.23346 | -0.13275 | -0.091553 | -0.091552 | 60.9055 | 60.7544 | 122.5388 | 122.6669 | -0.16937 | 122.6807 | 60.8047 | -0.13275 | 122.6669 | -0.16937 | 60.8047 | 122.5388 | 122.6807 | -122.85 | -122.905
248.9688 | 123.0927 | -60.8047 | 61.9263 | 0.13733 | 0.012177 | 0.015167 | 0.0002136 | 0.060882 | -0.0023498 | 0.069855 | -60.9604 | 61.7798 | -60.8688 | -61.0016 | 61.821 | 0.1236 | -0.054932 | 0.11444 | 61.7844 | -60.9512 | -0.064086 | -0.14649 | -0.15564 | -0.19684 | -0.10529 | -0.14648 | -0.14191 | -0.091553 | 60.7498 | 60.9192 | 122.6257 | 122.5845 | -0.15564 | 122.5891 | 60.9283 | -0.14648 | 122.5845 | -0.15564 | 60.9283 | 122.6257 | 122.5891 | -122.7951 | -122.8775
249.9688 | 123.0881 | -60.8368 | 61.9217 | 0.16022 | 0.015167 | 0.012604 | -0.0006408 | 0.062591 | -0.0023498 | 0.072205 | -60.9741 | 61.7661 | -60.8505 | -61.0199 | 61.8027 | 0.1236 | -0.041199 | 0.09613 | 61.7981 | -60.9421 | -0.013733 | -0.15564 | -0.13733 | -0.1831 | -0.11902 | -0.10529 | -0.1236 | -0.1236 | 60.7956 | 60.9329 | 122.6395 | 122.6028 | -0.13733 | 122.6349 | 60.9604 | -0.10529 | 122.6028 | -0.13733 | 60.9604 | 122.6395 | 122.6349 | -122.7722 | -122.8638
251.0312 | 123.1155 | -60.7864 | 61.9034 | 0.038147 | 0.011536 | 0.0091858 | 0.005127 | 0.06131 | -0.0053406 | 0.067291 | -60.8871 | 61.7615 | -60.8688 | -60.6812 | 61.8256 | -0.07782 | -0.050354 | 0.10071 | 61.7889 | -60.91 | -0.082397 | -0.14191 | -0.10071 | 0.10529 | -0.077819 | -0.1236 | -0.11444 | -0.018311 | 60.7361 | 60.8871 | 122.612 | 122.5479 | -0.10071 | 122.5754 | 60.7086 | -0.1236 | 122.5479 | -0.10071 | 60.7086 | 122.612 | 122.5754 | -122.7722 | -122.8134
251.9688 | 123.1018 | -60.8093 | 61.9308 | -0.030518 | 0.01474 | 0.013458 | 0.0029908 | 0.060242 | -0.0040588 | 0.071136 | -60.997 | 61.7661 | -60.8871 | -60.9695 | 61.853 | 0.19226 | -0.032043 | 0.16937 | 61.8073 | -60.9421 | -0.07782 | -0.16479 | -0.18768 | -0.16022 | -0.07782 | -0.13275 | -0.1236 | -0.10986 | 60.7773 | 60.9787 | 122.6624 | 122.5754 | -0.18768 | 122.6166 | 61.0016 | -0.13275 | 122.5754 | -0.18768 | 61.0016 | 122.6624 | 122.6166 | -122.818 | -122.8729
253.0156 | 122.9965 | -60.8322 | 61.9537 | 0.21362 | 0.016663 | 0.015595 | 0.0087586 | 0.06366 | -0.007904 | 0.071991 | -60.9695 | 61.8164 | -60.8826 | -61.0519 | 61.7157 | 0.018311 | 0.036621 | -0.013733 | 61.8439 | -60.9787 | -0.050354 | -0.13733 | -0.13733 | -0.21973 | -0.23804 | -0.14648 | -0.10986 | -0.086975 | 60.8688 | 60.8185 | 122.5479 | 122.6486 | -0.13733 | 122.6761 | 60.8505 | -0.14648 | 122.6486 | -0.13733 | 60.8505 | 122.5479 | 122.6761 | -122.8363 | -122.9324
253.9688 | 123.0606 | -60.8185 | 61.8942 | 0.36621 | 0.014099 | 0.014954 | 0.0025636 | 0.061523 | -0.0049134 | 0.073914 | -60.9467 | 61.7798 | -60.8826 | -61.0199 | 61.7889 | 0.054932 | -0.13733 | 0.032043 | 61.7706 | -60.9787 | -0.064087 | -0.11444 | -0.12817 | -0.20142 | -0.10529 | -0.16022 | -0.1236 | -0.064087 | 60.6812 | 60.8505 | 122.6074 | 122.5983 | -0.12817 | 122.5891 | 60.8734 | -0.16022 | 122.5983 | -0.12817 | 60.8734 | 122.6074 | 122.5891 | -122.7768 | -122.8729
255.0156 | 122.9233 | -60.8871 | 61.9492 | 0.25177 | 0.01474 | 0.016022 | 0.0072632 | 0.062378 | -0.0046996 | 0.071777 | -61.0199 | 61.8439 | -60.9146 | -61.1343 | 61.6608 | -0.050354 | 0.054932 | -0.086975 | 61.8393 | -61.0016 | -0.027466 | -0.10529 | -0.13275 | -0.24719 | -0.28839 | -0.11444 | -0.10986 | -0.10529 | 60.9421 | 60.8002 | 122.5479 | 122.731 | -0.13275 | 122.7264 | 60.8368 | -0.11444 | 122.731 | -0.13275 | 60.8368 | 122.5479 | 122.7264 | -122.8638 | -122.9507
255.9688 | 123.1796 | -60.8139 | 61.9354 | 0.26703 | 0.012817 | 0.01239 | 0.0032044 | 0.061737 | -0.0040588 | 0.068787 | -60.9787 | 61.7889 | -60.8826 | -61.0519 | 61.7661 | 0.045776 | -0.054932 | 0.027466 | 61.7844 | -60.9467 | -0.068664 | -0.14649 | -0.16479 | -0.23804 | -0.16937 | -0.13275 | -0.15106 | -0.096131 | 60.759 | 60.8414 | 122.58 | 122.6028 | -0.16479 | 122.5983 | 60.8597 | -0.13275 | 122.6028 | -0.16479 | 60.8597 | 122.58 | 122.5983 | -122.818 | -122.8821
257.0156 | 123.0148 | -60.8139 | 61.9171 | 0.1297 | 0.015808 | 0.015167 | 0.01004 | 0.062591 | -0.006836 | 0.071777 | -60.9329 | 61.8347 | -60.8734 | -61.0382 | 61.7477 | 0.082397 | 0.032043 | 0.027466 | 61.8484 | -60.9741 | -0.059509 | -0.082397 | -0.11902 | -0.2243 | -0.16937 | -0.16022 | -0.068664 | -0.059509 | 60.8459 | 60.8414 | 122.5616 | 122.6486 | -0.11902 | 122.6624 | 60.8963 | -0.16022 | 122.6486 | -0.11902 | 60.8963 | 122.5616 | 122.6624 | -122.7905 | -122.8912
257.9688 | 123.0652 | -60.8093 | 61.8896 | 0.045776 | 0.015595 | 0.012177 | 0.003418 | 0.061096 | -0.004486 | 0.070282 | -60.8917 | 61.7889 | -60.8597 | -60.9375 | 61.8576 | 0.32959 | 0.21057 | -0.15106 | 61.8256 | -60.9238 | -0.050354 | -0.10071 | -0.082398 | -0.12817 | -0.032043 | -0.11444 | -0.064086 | -0.032044 | 61.0199 | 60.6583 | 122.6669 | 122.5983 | -0.082398 | 122.6349 | 61.1389 | -0.11444 | 122.5983 | -0.082398 | 61.1389 | 122.6669 | 122.6349 | -122.7493 | -122.8134
259.0156 | 123.0194 | -60.8231 | 61.9354 | 0.20599 | 0.01709 | 0.015381 | 0.008545 | 0.064087 | -0.0040588 | 0.069855 | -60.9512 | 61.8347 | -60.8963 | -61.0474 | 61.7523 | 0.050354 | 0.032043 | 0.009155 | 61.8439 | -60.9879 | -0.073242 | -0.10071 | -0.12817 | -0.2243 | -0.18311 | -0.16479 | -0.091553 | -0.054932 | 60.8551 | 60.8322 | 122.5754 | 122.6578 | -0.12817 | 122.6669 | 60.8734 | -0.16479 | 122.6578 | -0.12817 | 60.8734 | 122.5754 | 122.6669 | -122.8317 | -122.9233
259.9688 | 123.0652 | -60.8139 | 61.8896 | 0.42725 | 0.015167 | 0.013458 | 0.0070496 | 0.067505 | -0.003418 | 0.070923 | -60.9146 | 61.7889 | -60.8826 | -60.9009 | 61.9125 | 0.073242 | -0.15564 | 0.054932 | 61.7844 | -60.9695 | -0.068664 | -0.10071 | -0.10071 | -0.086975 | 0.022889 | -0.15564 | -0.10529 | -0.032044 | 60.6583 | 60.8688 | 122.7264 | 122.6028 | -0.10071 | 122.5983 | 60.8871 | -0.15564 | 122.6028 | -0.10071 | 60.8871 | 122.7264 | 122.5983 | -122.7722 | -122.8592
261.0156 | 123.0286 | -60.8414 | 61.9583 | 0.2594 | 0.019013 | 0.014526 | 0.006836 | 0.063019 | -0.0040588 | 0.070282 | -61.0291 | 61.8576 | -60.8917 | -61.0199 | 61.7889 | 0.09613 | 0.041199 | 0.059509 | 61.8027 | -60.965 | -0.050354 | -0.10071 | -0.18768 | -0.17853 | -0.16937 | -0.1236 | -0.15564 | -0.13733 | 60.8826 | 60.9009 | 122.6303 | 122.699 | -0.18768 | 122.644 | 60.9375 | -0.1236 | 122.699 | -0.18768 | 60.9375 | 122.6303 | 122.644 | -122.85 | -122.9233
261.9688 | 123.0881 | -60.8047 | 61.9171 | 0.15259 | 0.014954 | 0.0098268 | 0.0004274 | 0.062164 | -0.0025634 | 0.071564 | -60.9787 | 61.7889 | -60.8551 | -61.0062 | 61.8027 | 0.10529 | -0.036621 | 0.10071 | 61.821 | -60.9375 | -0.050354 | -0.12817 | -0.17395 | -0.20142 | -0.11444 | -0.13275 | -0.09613 | -0.1236 | 60.7681 | 60.9055 | 122.6074 | 122.5937 | -0.17395 | 122.6257 | 60.91 | -0.13275 | 122.5937 | -0.17395 | 60.91 | 122.6074 | 122.6257 | -122.7722 | -122.8546
263.0156 | 122.9507 | -60.8643 | 61.94 | 0.22888 | 0.016235 | 0.014313 | 0.01004 | 0.065582 | -0.0055542 | 0.071136 | -60.9695 | 61.8256 | -60.91 | -61.0565 | 61.7294 | 0.027466 | 0.036621 | -0.018311 | 61.8484 | -60.9787 | -0.045776 | -0.11444 | -0.10529 | -0.19226 | -0.21057 | -0.11444 | -0.091552 | -0.059509 | 60.9009 | 60.8459 | 122.5937 | 122.6898 | -0.10529 | 122.7127 | 60.8917 | -0.11444 | 122.6898 | -0.10529 | 60.8917 | 122.5937 | 122.7127 | -122.85 | -122.9187
263.9688 | 123.0789 | -60.8276 | 61.8942 | 0.71716 | 0.014954 | 0.016663 | 0.0044862 | 0.06366 | -0.0023498 | 0.071777 | -60.8871 | 61.8027 | -60.8688 | -61.0153 | 61.7935 | 0.064087 | -0.14648 | 0.054932 | 61.7752 | -61.0062 | -0.041198 | -0.091553 | -0.059509 | -0.18768 | -0.10071 | -0.17853 | -0.11902 | -0.018311 | 60.6812 | 60.8826 | 122.6212 | 122.6303 | -0.059509 | 122.6028 | 60.8917 | -0.17853 | 122.6303 | -0.059509 | 60.8917 | 122.6212 | 122.6028 | -122.7631 | -122.9004
265.0156 | 123.0331 | -60.8231 | 61.94 | 0.1297 | 0.014526 | 0.014313 | 0.0072632 | 0.061951 | -0.0046996 | 0.0737 | -60.9421 | 61.8759 | -60.9055 | -61.0107 | 61.7661 | 0.082397 | 0.068665 | 0.073242 | 61.8622 | -60.9695 | -0.082398 | -0.064086 | -0.11902 | -0.18768 | -0.17395 | -0.14648 | -0.077819 | -0.036621 | 60.8917 | 60.8963 | 122.5891 | 122.699 | -0.11902 | 122.6852 | 60.9055 | -0.14648 | 122.699 | -0.11902 | 60.9055 | 122.5891 | 122.6852 | -122.8455 | -122.9095
265.9688 | 123.0652 | -60.8231 | 61.8942 | 0.43488 | 0.014313 | 0.015808 | 0.0057678 | 0.0643 | -0.0038452 | 0.07135 | -60.9512 | 61.8347 | -60.9009 | -61.0382 | 61.7889 | 0.064087 | -0.15564 | 0.004578 | 61.7661 | -60.9833 | -0.07782 | -0.059509 | -0.12817 | -0.21515 | -0.10529 | -0.16022 | -0.12817 | -0.050354 | 60.6674 | 60.8276 | 122.612 | 122.6578 | -0.12817 | 122.5891 | 60.8871 | -0.16022 | 122.6578 | -0.12817 | 60.8871 | 122.612 | 122.5891 | -122.7951 | -122.8775
267.0156 | 123.0606 | -60.7956 | 61.9171 | -0.0076295 | 0.013886 | 0.013031 | 0.0019226 | 0.064514 | -0.0040588 | 0.071777 | -60.9009 | 61.8347 | -60.8688 | -60.9604 | 61.8393 | 0.17395 | 0 | 0.16937 | 61.8027 | -60.9604 | -0.073242 | -0.082397 | -0.10529 | -0.1648 | -0.07782 | -0.1648 | -0.11444 | -0.032044 | 60.7956 | 60.965 | 122.6349 | 122.6303 | -0.10529 | 122.5983 | 60.9695 | -0.1648 | 122.6303 | -0.10529 | 60.9695 | 122.6349 | 122.5983 | -122.7859 | -122.8775
267.9688 | 123.0469 | -60.8505 | 61.908 | 0.20599 | 0.01474 | 0.013245 | 0.0008546 | 0.062164 | -0.0038452 | 0.071777 | -60.8643 | 61.8439 | -60.8643 | -61.0611 | 61.7477 | 0.036621 | -0.032043 | 0.022888 | 61.821 | -60.9741 | -0.013733 | -0.064087 | -0.013733 | -0.21057 | -0.16022 | -0.1236 | -0.086975 | 0 | 60.8185 | 60.8734 | 122.5983 | 122.6944 | -0.013733 | 122.6715 | 60.8871 | -0.1236 | 122.6944 | -0.013733 | 60.8871 | 122.5983 | 122.6715 | -122.7722 | -122.8821
269.0156 | 123.0743 | -60.791 | 61.9263 | 0.083923 | 0.013245 | 0.013458 | 0.0044862 | 0.062378 | -0.004486 | 0.070923 | -60.91 | 61.821 | -60.8505 | -60.9512 | 61.8393 | 0.16937 | 0 | 0.1831 | 61.7981 | -60.9741 | -0.059509 | -0.10529 | -0.11902 | -0.16022 | -0.086976 | -0.1831 | -0.12817 | -0.059509 | 60.791 | 60.9741 | 122.6303 | 122.612 | -0.11902 | 122.5891 | 60.9604 | -0.1831 | 122.612 | -0.11902 | 60.9604 | 122.6303 | 122.5891 | -122.7768 | -122.9004
269.9688 | 123.0377 | -60.8231 | 61.8851 | 0.35095 | 0.015167 | 0.011536 | 0.0019226 | 0.063019 | -0.0012818 | 0.071991 | -60.9467 | 61.8073 | -60.8871 | -61.0382 | 61.7569 | 0.027466 | -0.091553 | 0.013733 | 61.7752 | -61.0062 | -0.064087 | -0.07782 | -0.1236 | -0.21515 | -0.12817 | -0.18311 | -0.10986 | -0.059509 | 60.7315 | 60.8368 | 122.58 | 122.6303 | -0.1236 | 122.5983 | 60.8505 | -0.18311 | 122.6303 | -0.1236 | 60.8505 | 122.58 | 122.5983 | -122.7722 | -122.8912
271.0156 | 123.262 | -60.7773 | 61.9766 | 0.061035 | 0.017304 | 0.014526 | 0.003418 | 0.063019 | -0.0053406 | 0.070496 | -60.8871 | 61.8118 | -60.8459 | -60.9375 | 61.8622 | 0.1831 | -0.032043 | 0.17853 | 61.8073 | -60.965 | -0.068664 | -0.16479 | -0.10986 | -0.16022 | -0.11444 | -0.18768 | -0.16937 | -0.041199 | 60.7452 | 60.9558 | 122.6395 | 122.5891 | -0.10986 | 122.5845 | 60.9604 | -0.18768 | 122.5891 | -0.10986 | 60.9604 | 122.6395 | 122.5845 | -122.8226 | -122.9416
271.9688 | 122.9645 | -60.8597 | 61.9583 | 0.25177 | 0.013886 | 0.013672 | 0.0081178 | 0.063232 | -0.0055542 | 0.072205 | -60.965 | 61.8988 | -60.91 | -61.0657 | 61.7203 | 0.004578 | 0.036621 | -0.045776 | 61.8347 | -61.0336 | -0.050354 | -0.059509 | -0.10529 | -0.20599 | -0.23804 | -0.17395 | -0.1236 | -0.054932 | 60.8963 | 60.8139 | 122.58 | 122.7585 | -0.10529 | 122.6944 | 60.8643 | -0.17395 | 122.7585 | -0.10529 | 60.8643 | 122.58 | 122.6944 | -122.8683 | -122.9919
273.0156 | 122.9645 | -60.8688 | 61.9583 | -0.061036 | 0.013245 | 0.014313 | 0.0064088 | 0.061737 | -0.0029906 | 0.072418 | -60.9879 | 61.8942 | -60.8826 | -61.0611 | 61.7432 | 0 | 0.47607 | 0.091553 | 61.9034 | -60.9879 | -0.013733 | -0.064087 | -0.11902 | -0.19226 | -0.21515 | -0.11902 | -0.054932 | -0.10529 | 61.3449 | 60.9604 | 122.612 | 122.7631 | -0.11902 | 122.7722 | 60.8688 | -0.11902 | 122.7631 | -0.11902 | 60.8688 | 122.612 | 122.7722 | -122.8409 | -122.9462
273.9688 | 123.0103 | -60.8505 | 61.9446 | 0.23651 | 0.018372 | 0.017304 | 0.0083314 | 0.066009 | -0.0053406 | 0.071564 | -60.9146 | 61.9171 | -60.8826 | -61.0336 | 61.7706 | 0.054932 | 0.041199 | 0.036621 | 61.853 | -60.997 | -0.032043 | -0.027466 | -0.064087 | -0.18311 | -0.17395 | -0.14648 | -0.091553 | -0.032044 | 60.8917 | 60.8871 | 122.6212 | 122.7676 | -0.064087 | 122.7036 | 60.9055 | -0.14648 | 122.7676 | -0.064087 | 60.9055 | 122.6212 | 122.7036 | -122.8271 | -122.9416
274.9688 | 122.9782 | -60.8505 | 61.9354 | 0.19836 | 0.016022 | 0.016235 | 0.0074768 | 0.064941 | -0.0038452 | 0.071991 | -60.9421 | 61.8713 | -60.8963 | -61.0382 | 61.734 | 0.027466 | 0.041199 | 0.009155 | 61.8256 | -61.0336 | -0.045776 | -0.064087 | -0.091553 | -0.18768 | -0.20142 | -0.18311 | -0.10986 | -0.045777 | 60.8917 | 60.8597 | 122.5845 | 122.7219 | -0.091553 | 122.6761 | 60.878 | -0.18311 | 122.7219 | -0.091553 | 60.878 | 122.5845 | 122.6761 | -122.8317 | -122.9691
276.0156 | 123.0515 | -60.8322 | 61.9263 | 0.21362 | 0.015808 | 0.013031 | 0.0014954 | 0.064728 | -0.0006408 | 0.072205 | -60.9879 | 61.8622 | -60.8643 | -61.0428 | 61.7706 | 0.082397 | -0.036621 | 0.064087 | 61.821 | -61.0153 | -0.032044 | -0.064087 | -0.15564 | -0.21057 | -0.15564 | -0.18311 | -0.10529 | -0.1236 | 60.7956 | 60.8963 | 122.6028 | 122.6944 | -0.15564 | 122.6532 | 60.9146 | -0.18311 | 122.6944 | -0.15564 | 60.9146 | 122.6028 | 122.6532 | -122.7905 | -122.9416
276.9688 | 122.9691 | -60.9055 | 61.908 | 0.32806 | 0.014313 | 0.016449 | 0.0066224 | 0.063019 | -0.0040588 | 0.071136 | -61.0107 | 61.8851 | -60.9146 | -61.1252 | 61.6928 | -0.027466 | 0.013733 | -0.082397 | 61.8393 | -61.0199 | -0.009155 | -0.022888 | -0.10529 | -0.21973 | -0.21515 | -0.11444 | -0.068665 | -0.09613 | 60.9192 | 60.8231 | 122.5983 | 122.7905 | -0.10529 | 122.7448 | 60.878 | -0.11444 | 122.7905 | -0.10529 | 60.878 | 122.5983 | 122.7448 | -122.8226 | -122.9279
277.9688 | 123.0331 | -60.8597 | 61.9446 | 0.2594 | 0.017731 | 0.014313 | 0.0087586 | 0.063446 | -0.002777 | 0.072632 | -60.9329 | 61.908 | -60.8963 | -61.0199 | 61.7569 | 0.082397 | 0.032043 | 0.041199 | 61.8301 | -60.997 | -0.036621 | -0.036621 | -0.073242 | -0.16022 | -0.18768 | -0.13733 | -0.11444 | -0.036621 | 60.8917 | 60.9009 | 122.6166 | 122.7676 | -0.073242 | 122.6898 | 60.9421 | -0.13733 | 122.7676 | -0.073242 | 60.9421 | 122.6166 | 122.6898 | -122.8409 | -122.9416
279.0156 | 123.0331 | -60.8322 | 61.9263 | 0.2594 | 0.014526 | 0.012177 | -0.0002136 | 0.064087 | -0.001068 | 0.073059 | -60.9695 | 61.8301 | -60.8643 | -61.0794 | 61.7844 | 0.045776 | -0.022888 | 0.013733 | 61.7935 | -61.0062 | -0.032044 | -0.096131 | -0.13733 | -0.24719 | -0.14191 | -0.17395 | -0.13275 | -0.10529 | 60.8093 | 60.8459 | 122.6166 | 122.6624 | -0.13733 | 122.6257 | 60.878 | -0.17395 | 122.6624 | -0.13733 | 60.878 | 122.6166 | 122.6257 | -122.7905 | -122.9324
279.9688 | 123.0103 | -60.8597 | 61.9308 | 0.045776 | 0.01709 | 0.016022 | 0.0064088 | 0.061951 | -0.002777 | 0.070282 | -60.9833 | 61.9034 | -60.91 | -61.0611 | 61.7386 | 0.064087 | 0.14648 | 0.032043 | 61.8622 | -60.9787 | -0.050354 | -0.027466 | -0.1236 | -0.20142 | -0.19226 | -0.11902 | -0.068664 | -0.073242 | 61.0062 | 60.8917 | 122.5983 | 122.7631 | -0.1236 | 122.7219 | 60.9238 | -0.11902 | 122.7631 | -0.1236 | 60.9238 | 122.5983 | 122.7219 | -122.8409 | -122.9095
281.0156 | 123.056 | -60.8505 | 61.8988 | 0.40436 | 0.01474 | 0.012177 | 0.0008546 | 0.063232 | -0.0025634 | 0.071991 | -60.9604 | 61.821 | -60.8826 | -61.0703 | 61.7706 | 0.045776 | -0.082397 | 0.018311 | 61.8301 | -60.9924 | -0.032043 | -0.07782 | -0.10986 | -0.21973 | -0.12817 | -0.14191 | -0.068665 | -0.07782 | 60.7681 | 60.8688 | 122.6212 | 122.6715 | -0.10986 | 122.6807 | 60.8963 | -0.14191 | 122.6715 | -0.10986 | 60.8963 | 122.6212 | 122.6807 | -122.7814 | -122.8912
281.9688 | 122.9599 | -60.8597 | 61.9492 | 0.21362 | 0.015595 | 0.014099 | 0.008545 | 0.065369 | -0.0049134 | 0.073059 | -60.9833 | 61.8759 | -60.8963 | -61.0931 | 61.6928 | -0.013733 | 0.07782 | -0.068665 | 61.8622 | -60.9879 | -0.036621 | -0.073242 | -0.1236 | -0.23346 | -0.25635 | -0.12817 | -0.086975 | -0.086975 | 60.9375 | 60.791 | 122.5525 | 122.7356 | -0.1236 | 122.7219 | 60.8459 | -0.12817 | 122.7356 | -0.1236 | 60.8459 | 122.5525 | 122.7219 | -122.8455 | -122.937
283.0156 | 123.0377 | -60.8459 | 61.9125 | 0.34332 | 0.013458 | 0.014099 | 0.0002136 | 0.062378 | -0.001709 | 0.075623 | -60.9558 | 61.7935 | -60.8917 | -61.0519 | 61.7569 | 0.059509 | -0.10071 | 0.022888 | 61.7889 | -61.0016 | -0.045777 | -0.11902 | -0.10986 | -0.20599 | -0.15564 | -0.15564 | -0.1236 | -0.064087 | 60.7452 | 60.8688 | 122.6028 | 122.6395 | -0.10986 | 122.6349 | 60.9055 | -0.15564 | 122.6395 | -0.10986 | 60.9055 | 122.6028 | 122.6349 | -122.8043 | -122.9141
283.9688 | 122.9736 | -60.8505 | 61.972 | 0.022888 | 0.016449 | 0.01474 | 0.0049134 | 0.062805 | -0.0040588 | 0.071564 | -60.997 | 61.8942 | -60.8963 | -61.0657 | 61.7294 | 0.073242 | 0.15106 | 0.027466 | 61.8576 | -60.997 | -0.045776 | -0.07782 | -0.14648 | -0.21515 | -0.24262 | -0.14648 | -0.11444 | -0.10071 | 61.0016 | 60.878 | 122.58 | 122.7448 | -0.14648 | 122.7081 | 60.9238 | -0.14648 | 122.7448 | -0.14648 | 60.9238 | 122.58 | 122.7081 | -122.8683 | -122.9691
285.0156 | 123.0698 | -60.8368 | 61.8851 | 0.38147 | 0.01474 | 0.020721 | 0.0044862 | 0.063232 | -0.0038452 | 0.071777 | -60.9283 | 61.7981 | -60.8963 | -61.0245 | 61.821 | 0.059509 | -0.15564 | 0.045776 | 61.7706 | -60.9787 | -0.059509 | -0.086975 | -0.091553 | -0.18768 | -0.064087 | -0.14191 | -0.11444 | -0.032044 | 60.6812 | 60.8826 | 122.6578 | 122.6349 | -0.091553 | 122.6074 | 60.8963 | -0.14191 | 122.6349 | -0.091553 | 60.8963 | 122.6578 | 122.6074 | -122.7814 | -122.8638
285.9688 | 122.9462 | -60.8459 | 61.9766 | 0.007629 | 0.015595 | 0.012604 | 0.0038452 | 0.062591 | -0.0055542 | 0.071136 | -60.9924 | 61.8622 | -60.9009 | -61.0245 | 61.6013 | -0.027466 | 0.15106 | 0.050354 | 61.8896 | -60.9741 | -0.054932 | -0.11444 | -0.14648 | -0.17853 | -0.37537 | -0.12817 | -0.086976 | -0.091553 | 60.997 | 60.8963 | 122.4472 | 122.7081 | -0.14648 | 122.7356 | 60.8185 | -0.12817 | 122.7081 | -0.14648 | 60.8185 | 122.4472 | 122.7356 | -122.8775 | -122.9507
287.0156 | 123.0286 | -60.8459 | 61.9217 | 0.43488 | 0.016876 | 0.012177 | 0.0042726 | 0.065369 | -0.0040588 | 0.070496 | -60.9787 | 61.8439 | -60.9192 | -61.0886 | 61.734 | -0.009155 | -0.07782 | -0.045776 | 61.8576 | -60.9833 | -0.073242 | -0.07782 | -0.13275 | -0.24262 | -0.18768 | -0.13733 | -0.064087 | -0.05951 | 60.7681 | 60.8002 | 122.58 | 122.6898 | -0.13275 | 122.7036 | 60.8368 | -0.13733 | 122.6898 | -0.13275 | 60.8368 | 122.58 | 122.7036 | -122.8409 | -122.905
287.9688 | 123.0103 | -60.8322 | 61.9492 | -0.038147 | 0.015381 | 0.01474 | 0.0019226 | 0.061523 | -0.0055542 | 0.071991 | -60.9375 | 61.8484 | -60.8597 | -61.0107 | 61.7752 | 0.13733 | 0.091553 | 0.12817 | 61.853 | -60.9695 | -0.027466 | -0.10071 | -0.10529 | -0.17853 | -0.17395 | -0.13733 | -0.096131 | -0.07782 | 60.9238 | 60.9604 | 122.6074 | 122.6807 | -0.10529 | 122.6852 | 60.9695 | -0.13733 | 122.6807 | -0.10529 | 60.9695 | 122.6074 | 122.6852 | -122.8088 | -122.9187
289.0156 | 123.0972 | -60.8139 | 61.8988 | 0.39673 | 0.013031 | 0.01239 | 0.0038452 | 0.064941 | -0.0036316 | 0.071564 | -60.9283 | 61.7569 | -60.8826 | -61.0245 | 61.7935 | 0.073242 | -0.15106 | 0.050354 | 61.7752 | -60.9375 | -0.068664 | -0.14191 | -0.11444 | -0.21057 | -0.10529 | -0.1236 | -0.1236 | -0.045777 | 60.6628 | 60.8643 | 122.6074 | 122.5708 | -0.11444 | 122.5891 | 60.8871 | -0.1236 | 122.5708 | -0.11444 | 60.8871 | 122.6074 | 122.5891 | -122.7814 | -122.8363
289.9688 | 123.0194 | -60.8185 | 61.9629 | 0.038147 | 0.016449 | 0.01474 | 0.0070496 | 0.063019 | -0.0042724 | 0.072632 | -60.9604 | 61.8347 | -60.8871 | -61.0291 | 61.7523 | 0.082397 | 0.10986 | 0.054932 | 61.8439 | -60.9421 | -0.068665 | -0.12817 | -0.14191 | -0.21057 | -0.21057 | -0.1236 | -0.11902 | -0.073242 | 60.9283 | 60.8734 | 122.5708 | 122.6532 | -0.14191 | 122.6624 | 60.9009 | -0.1236 | 122.6532 | -0.14191 | 60.9009 | 122.5708 | 122.6624 | -122.85 | -122.905
291.0156 | 123.0469 | -60.8505 | 61.853 | 0.43488 | 0.014526 | 0.013031 | 0.0055542 | 0.064728 | -0.003418 | 0.07135 | -60.9238 | 61.7661 | -60.9055 | -61.0245 | 61.7889 | 0.059509 | -0.16479 | 0.027466 | 61.7661 | -60.965 | -0.054932 | -0.086975 | -0.073242 | -0.17395 | -0.064087 | -0.11444 | -0.086975 | -0.01831 | 60.6857 | 60.878 | 122.6395 | 122.6166 | -0.073242 | 122.6166 | 60.91 | -0.11444 | 122.6166 | -0.073242 | 60.91 | 122.6395 | 122.6166 | -122.7585 | -122.818
291.9688 | 123.0927 | -60.8093 | 61.9263 | -0.0076295 | 0.012604 | 0.013672 | 0.001709 | 0.061737 | -0.005127 | 0.069427 | -60.8963 | 61.7935 | -60.8643 | -60.965 | 61.8393 | 0.16022 | -0.018311 | 0.1831 | 61.8164 | -60.9375 | -0.054932 | -0.13275 | -0.086975 | -0.15564 | -0.086976 | -0.12817 | -0.10986 | -0.032043 | 60.791 | 60.9924 | 122.6486 | 122.6028 | -0.086975 | 122.6257 | 60.9695 | -0.12817 | 122.6028 | -0.086975 | 60.9695 | 122.6486 | 122.6257 | -122.7905 | -122.8638
292.9688 | 123.1018 | -60.7956 | 61.9263 | -0.45776 | 0.011749 | 0.01239 | 0.001709 | 0.058533 | -0.003418 | 0.07135 | -60.9695 | 61.7752 | -60.878 | -60.9512 | 61.8347 | 0.1831 | -0.041199 | 0.18768 | 61.8256 | -60.9238 | -0.082398 | -0.15106 | -0.17395 | -0.15564 | -0.091553 | -0.12817 | -0.10071 | -0.091552 | 60.7544 | 60.9833 | 122.6303 | 122.5708 | -0.17395 | 122.6212 | 60.9787 | -0.12817 | 122.5708 | -0.17395 | 60.9787 | 122.6303 | 122.6212 | -122.8043 | -122.85
294.0156 | 122.9599 | -60.8688 | 61.9492 | 0.26703 | 0.014526 | 0.016876 | 0.0074768 | 0.063873 | -0.0070496 | 0.072205 | -60.997 | 61.8301 | -60.9375 | -61.0977 | 61.6837 | -0.018311 | 0.059509 | -0.07782 | 61.853 | -60.9787 | -0.068665 | -0.11902 | -0.12817 | -0.22888 | -0.2655 | -0.10986 | -0.096131 | -0.059509 | 60.9283 | 60.791 | 122.5525 | 122.699 | -0.12817 | 122.7219 | 60.8505 | -0.10986 | 122.699 | -0.12817 | 60.8505 | 122.5525 | 122.7219 | -122.8867 | -122.9279
294.9688 | 123.0377 | -60.8414 | 61.9034 | 0.14496 | 0.015167 | 0.012817 | -0.001068 | 0.061951 | -0.003418 | 0.072418 | -60.9924 | 61.7844 | -60.8917 | -61.0657 | 61.7569 | 0.064087 | -0.045776 | 0.022888 | 61.8393 | -60.9375 | -0.050354 | -0.11902 | -0.15106 | -0.2243 | -0.14648 | -0.09613 | -0.064087 | -0.10071 | 60.7956 | 60.8643 | 122.5983 | 122.6257 | -0.15106 | 122.6807 | 60.9055 | -0.09613 | 122.6257 | -0.15106 | 60.9055 | 122.5983 | 122.6807 | -122.7951 | -122.8409
296.0156 | 122.9965 | -60.8688 | 61.94 | 0.65613 | 0.017731 | 0.015595 | 0.0079042 | 0.063232 | -0.0040588 | 0.071136 | -60.9604 | 61.8256 | -60.9055 | -61.1252 | 61.6837 | -0.045776 | 0.036621 | -0.10986 | 61.8256 | -60.997 | -0.036622 | -0.11444 | -0.091553 | -0.25635 | -0.25635 | -0.12817 | -0.11444 | -0.054931 | 60.9055 | 60.759 | 122.5525 | 122.6944 | -0.091553 | 122.6944 | 60.8231 | -0.12817 | 122.6944 | -0.091553 | 60.8231 | 122.5525 | 122.6944 | -122.8455 | -122.937
296.9688 | 123.1293 | -60.7864 | 61.9583 | 0.12207 | 0.014099 | 0.012177 | 0 | 0.061096 | -0.0023498 | 0.071991 | -60.9055 | 61.7752 | -60.8688 | -60.9558 | 61.853 | 0.17853 | -0.050354 | 0.17853 | 61.7798 | -60.9192 | -0.082397 | -0.1831 | -0.11902 | -0.16937 | -0.10529 | -0.13275 | -0.17853 | -0.036622 | 60.7361 | 60.965 | 122.6395 | 122.5616 | -0.11902 | 122.5662 | 60.965 | -0.13275 | 122.5616 | -0.11902 | 60.965 | 122.6395 | 122.5662 | -122.8271 | -122.8775
298.0156 | 122.9965 | -60.8597 | 61.9171 | 0.40436 | 0.016235 | 0.013245 | 0.0055542 | 0.063446 | -0.006195 | 0.070496 | -61.0199 | 61.821 | -60.9512 | -61.084 | 61.7111 | -0.013733 | -0.059509 | -0.068665 | 61.7981 | -60.997 | -0.091553 | -0.09613 | -0.16022 | -0.2243 | -0.20599 | -0.13733 | -0.11902 | -0.068664 | 60.8002 | 60.791 | 122.5708 | 122.6807 | -0.16022 | 122.6578 | 60.8459 | -0.13733 | 122.6807 | -0.16022 | 60.8459 | 122.5708 | 122.6578 | -122.8683 | -122.9141
298.9688 | 123.0743 | -60.8414 | 61.9217 | 0.14496 | 0.013672 | 0.010254 | 0.001709 | 0.061096 | -0.0023498 | 0.071564 | -60.9695 | 61.7706 | -60.8734 | -61.0062 | 61.7935 | 0.10529 | -0.027466 | 0.10529 | 61.8027 | -60.9329 | -0.032043 | -0.15106 | -0.12817 | -0.1648 | -0.12817 | -0.091552 | -0.11902 | -0.09613 | 60.8139 | 60.9467 | 122.6349 | 122.612 | -0.12817 | 122.644 | 60.9467 | -0.091552 | 122.612 | -0.12817 | 60.9467 | 122.6349 | 122.644 | -122.7951 | -122.8546
300.0156 | 122.9691 | -60.8597 | 61.9446 | 0.76294 | 0.016663 | 0.015595 | 0.0089722 | 0.064941 | -0.0038452 | 0.071136 | -60.9879 | 61.8347 | -60.9238 | -61.1114 | 61.6653 | -0.036621 | 0 | -0.091553 | 61.8393 | -60.9787 | -0.064087 | -0.10986 | -0.12817 | -0.25177 | -0.27924 | -0.11902 | -0.10529 | -0.064087 | 60.8597 | 60.7681 | 122.525 | 122.6944 | -0.12817 | 122.699 | 60.8231 | -0.11902 | 122.6944 | -0.12817 | 60.8231 | 122.525 | 122.699 | -122.8683 | -122.9233
300.9688 | 123.0423 | -60.8185 | 61.9034 | -0.21362 | 0.013886 | 0.008545 | 0.0012818 | 0.062591 | -0.0053406 | 0.070282 | -60.9879 | 61.7752 | -60.878 | -61.0657 | 61.7661 | 0.059509 | -0.050354 | 0.036621 | 61.7981 | -60.9375 | -0.05951 | -0.12817 | -0.16937 | -0.24719 | -0.13733 | -0.11902 | -0.10529 | -0.10986 | 60.7681 | 60.8551 | 122.5845 | 122.5937 | -0.16937 | 122.6166 | 60.878 | -0.11902 | 122.5937 | -0.16937 | 60.878 | 122.5845 | 122.6166 | -122.7814 | -122.8409
302.0156 | 123.0057 | -60.8231 | 61.9537 | 1.6785 | 0.014099 | 0.0091858 | 0.0087586 | 0.062378 | -0.005127 | 0.069641 | -60.8643 | 61.821 | -60.9329 | -61.0062 | 61.7798 | 0.064087 | 0.022888 | 0.050354 | 61.8484 | -60.9604 | -0.10986 | -0.13275 | -0.041199 | -0.18311 | -0.17395 | -0.13733 | -0.10529 | 0.068664 | 60.8459 | 60.8734 | 122.6028 | 122.644 | -0.041199 | 122.6715 | 60.8871 | -0.13733 | 122.644 | -0.041199 | 60.8871 | 122.6028 | 122.6715 | -122.8867 | -122.9141
302.9688 | 123.0194 | -60.8505 | 61.9125 | 0.30518 | 0.012817 | 0.015167 | 0.0002136 | 0.062805 | -0.0008544 | 0.072632 | -60.9879 | 61.7706 | -60.8688 | -61.0657 | 61.7523 | 0.045776 | -0.068665 | 0.013733 | 61.7752 | -61.0016 | -0.01831 | -0.14191 | -0.13733 | -0.21515 | -0.16022 | -0.15106 | -0.13733 | -0.11902 | 60.7819 | 60.8643 | 122.6028 | 122.6212 | -0.13733 | 122.6257 | 60.8963 | -0.15106 | 122.6212 | -0.13733 | 60.8963 | 122.6028 | 122.6257 | -122.7814 | -122.9141
304.0156 | 122.9462 | -60.8322 | 61.9766 | 0.25177 | 0.01474 | 0.012177 | 0.011108 | 0.062591 | -0.0042724 | 0.071564 | -61.0107 | 61.8301 | -60.9192 | -61.1114 | 61.6882 | -0.032043 | 0.050354 | -0.082397 | 61.8393 | -60.997 | -0.086975 | -0.14648 | -0.17853 | -0.27924 | -0.28839 | -0.16479 | -0.13733 | -0.091553 | 60.8826 | 60.7498 | 122.5204 | 122.6624 | -0.17853 | 122.6715 | 60.8002 | -0.16479 | 122.6624 | -0.17853 | 60.8002 | 122.5204 | 122.6715 | -122.8958 | -122.9736
304.9688 | 123.0927 | -60.8093 | 61.9263 | -0.022889 | 0.01474 | 0.017944 | 0.0019226 | 0.063873 | -0.0059814 | 0.071136 | -60.9146 | 61.7981 | -60.8643 | -60.9695 | 61.7706 | 0.16022 | -0.07782 | 0.11444 | 61.8027 | -60.9558 | -0.054932 | -0.12817 | -0.10529 | -0.16022 | -0.15564 | -0.14648 | -0.1236 | -0.050354 | 60.7315 | 60.9238 | 122.58 | 122.6074 | -0.10529 | 122.612 | 60.9695 | -0.14648 | 122.6074 | -0.10529 | 60.9695 | 122.58 | 122.612 | -122.7905 | -122.8821
306.0156 | 122.9965 | -60.8322 | 61.9308 | 0.16785 | 0.015808 | 0.012177 | 0.0093994 | 0.062378 | -0.005127 | 0.071136 | -60.9604 | 61.7981 | -60.8826 | -61.0519 | 61.7294 | 0.027466 | 0.022888 | -0.018311 | 61.8576 | -60.9787 | -0.050354 | -0.13275 | -0.12817 | -0.21973 | -0.20142 | -0.14648 | -0.073242 | -0.07782 | 60.8551 | 60.8139 | 122.5616 | 122.6303 | -0.12817 | 122.6898 | 60.8597 | -0.14648 | 122.6303 | -0.12817 | 60.8597 | 122.5616 | 122.6898 | -122.8134 | -122.9095
306.9688 | 123.0652 | -60.8414 | 61.9125 | 0.40436 | 0.014099 | 0.015167 | 0.0014954 | 0.063873 | -0.003418 | 0.071991 | -60.9329 | 61.7889 | -60.8917 | -61.0291 | 61.7981 | 0.068665 | -0.14648 | 0.041199 | 61.7752 | -60.9879 | -0.050354 | -0.1236 | -0.091552 | -0.18768 | -0.11444 | -0.14648 | -0.13733 | -0.041198 | 60.6949 | 60.8826 | 122.6395 | 122.6303 | -0.091552 | 122.6166 | 60.91 | -0.14648 | 122.6303 | -0.091552 | 60.91 | 122.6395 | 122.6166 | -122.8043 | -122.9004
307.9688 | 123.0743 | -60.8047 | 61.9034 | 0.42725 | 0.015167 | 0.014954 | 0.0027772 | 0.061951 | -0.0053406 | 0.071991 | -60.9192 | 61.7889 | -60.8826 | -61.1526 | 61.6653 | 0.10529 | -0.086975 | 0.064087 | 61.7935 | -60.9558 | -0.077819 | -0.11444 | -0.11444 | -0.3479 | -0.23804 | -0.15106 | -0.10986 | -0.036621 | 60.7178 | 60.8688 | 122.4701 | 122.5937 | -0.11444 | 122.5983 | 60.91 | -0.15106 | 122.5937 | -0.11444 | 60.91 | 122.4701 | 122.5983 | -122.7859 | -122.8592
309.0156 | 123.0011 | -60.8276 | 61.9766 | -0.053406 | 0.014954 | 0.011749 | 0.0061952 | 0.063019 | -0.0064086 | 0.071136 | -60.9604 | 61.8896 | -60.8826 | -61.0519 | 61.7386 | 0.068665 | 0.1236 | 0.045776 | 61.8622 | -60.9833 | -0.054931 | -0.086976 | -0.13275 | -0.2243 | -0.23804 | -0.15564 | -0.11444 | -0.07782 | 60.9512 | 60.8734 | 122.5662 | 122.7173 | -0.13275 | 122.6898 | 60.8963 | -0.15564 | 122.7173 | -0.13275 | 60.8963 | 122.5662 | 122.6898 | -122.8592 | -122.9599
309.9688 | 123.0423 | -60.8231 | 61.8988 | 0.39673 | 0.016022 | 0.014099 | 0.0044862 | 0.064514 | -0.002777 | 0.070496 | -60.9604 | 61.7981 | -60.9146 | -61.0336 | 61.7569 | 0.041199 | -0.13275 | 0.009155 | 61.7798 | -60.9833 | -0.091553 | -0.10071 | -0.13733 | -0.21057 | -0.14191 | -0.16022 | -0.11902 | -0.045776 | 60.6903 | 60.8322 | 122.58 | 122.6212 | -0.13733 | 122.6028 | 60.8643 | -0.16022 | 122.6212 | -0.13733 | 60.8643 | 122.58 | 122.6028 | -122.8134 | -122.8821
311.0156 | 122.9919 | -60.8551 | 61.9766 | 1.0529 | 0.017304 | 0.015167 | 0.0036316 | 0.063019 | -0.004486 | 0.070923 | -61.0382 | 61.8759 | -60.8917 | -61.0611 | 61.7523 | 0.082397 | 0.13733 | 0.036621 | 61.8347 | -60.9787 | -0.036621 | -0.10071 | -0.1831 | -0.20599 | -0.22431 | -0.1236 | -0.14191 | -0.14648 | 60.9924 | 60.8917 | 122.6074 | 122.731 | -0.1831 | 122.6898 | 60.9375 | -0.1236 | 122.731 | -0.1831 | 60.9375 | 122.6074 | 122.6898 | -122.8683 | -122.9553
311.9688 | 123.0743 | -60.8276 | 61.9034 | 0.41962 | 0.016876 | 0.016663 | 0.005127 | 0.063232 | -0.0023498 | 0.073486 | -60.9879 | 61.8484 | -60.9192 | -61.0611 | 61.7386 | 0.041199 | -0.13275 | -0.009155 | 61.7935 | -61.0016 | -0.091552 | -0.054931 | -0.16022 | -0.23346 | -0.1648 | -0.17395 | -0.10986 | -0.068665 | 60.6949 | 60.8185 | 122.5662 | 122.6761 | -0.16022 | 122.6212 | 60.8688 | -0.17395 | 122.6761 | -0.16022 | 60.8688 | 122.5662 | 122.6212 | -122.8226 | -122.905
313.0156 | 123.0057 | -60.8047 | 61.9583 | -0.015259 | 0.016663 | 0.011749 | 0.0021362 | 0.06131 | -0.0021362 | 0.070496 | -60.9238 | 61.8759 | -60.8551 | -61.0199 | 61.7981 | 0.14191 | 0.07782 | 0.13733 | 61.8347 | -61.0016 | -0.050354 | -0.082397 | -0.11902 | -0.21515 | -0.16022 | -0.19684 | -0.1236 | -0.068664 | 60.8826 | 60.9421 | 122.6028 | 122.6807 | -0.11902 | 122.6395 | 60.9467 | -0.19684 | 122.6807 | -0.11902 | 60.9467 | 122.6028 | 122.6395 | -122.8134 | -122.9599
313.9688 | 122.9645 | -60.8459 | 61.9537 | 0.3891 | 0.015808 | 0.014099 | 0.0061952 | 0.064087 | -0.003418 | 0.071136 | -61.0016 | 61.8759 | -60.9192 | -61.1252 | 61.6974 | -0.041199 | -0.30212 | -0.27008 | 61.7752 | -61.0474 | -0.073242 | -0.077819 | -0.15564 | -0.27924 | -0.25635 | -0.20142 | -0.17853 | -0.082398 | 60.5438 | 60.5759 | 122.5433 | 122.7219 | -0.15564 | 122.6212 | 60.8047 | -0.20142 | 122.7219 | -0.15564 | 60.8047 | 122.5433 | 122.6212 | -122.8729 | -123.0011
315.0156 | 122.9874 | -60.8368 | 61.9583 | -0.038147 | 0.015808 | 0.011536 | 0.0021362 | 0.061951 | -0.0049134 | 0.071777 | -60.9192 | 61.8668 | -60.8597 | -60.9741 | 61.8118 | 0.15564 | 0.045776 | 0.11902 | 61.8439 | -60.9787 | -0.022888 | -0.091553 | -0.082397 | -0.13733 | -0.14648 | -0.14191 | -0.11444 | -0.059509 | 60.8826 | 60.9558 | 122.6486 | 122.7036 | -0.082397 | 122.6807 | 60.9924 | -0.14191 | 122.7036 | -0.082397 | 60.9924 | 122.6486 | 122.6807 | -122.818 | -122.937
315.9688 | 123.0148 | -60.8414 | 61.9446 | 0.17548 | 0.01709 | 0.016663 | 0.0081178 | 0.062378 | -0.0049134 | 0.070709 | -60.9375 | 61.9125 | -60.9009 | -61.0291 | 61.7569 | 0.082397 | 0.036621 | 0.050354 | 61.8622 | -61.0062 | -0.059509 | -0.032043 | -0.09613 | -0.18768 | -0.18768 | -0.1648 | -0.082397 | -0.036621 | 60.878 | 60.8917 | 122.5983 | 122.7539 | -0.09613 | 122.7036 | 60.9238 | -0.1648 | 122.7539 | -0.09613 | 60.9238 | 122.5983 | 122.7036 | -122.8455 | -122.9507
317.0156 | 123.0606 | -60.7956 | 61.8988 | 0.007629 | 0.01474 | 0.012604 | 0.0010682 | 0.062378 | -0.0025634 | 0.071136 | -60.8917 | 61.8393 | -60.8459 | -60.9421 | 61.8576 | 0.17853 | -0.022888 | 0.17395 | 61.8256 | -60.9787 | -0.050354 | -0.05951 | -0.096131 | -0.14649 | -0.041199 | -0.18311 | -0.073242 | -0.045777 | 60.7727 | 60.9695 | 122.6532 | 122.6349 | -0.096131 | 122.6212 | 60.9741 | -0.18311 | 122.6349 | -0.096131 | 60.9741 | 122.6532 | 122.6212 | -122.7448 | -122.8775
317.9688 | 123.0789 | -60.8414 | 61.8988 | 0.41962 | 0.016022 | 0.015808 | 0.0053406 | 0.064728 | -0.0049134 | 0.070923 | -60.9238 | 61.821 | -60.9009 | -60.9924 | 61.8118 | 0.082397 | -0.18768 | 0.050354 | 61.7798 | -61.0107 | -0.059509 | -0.07782 | -0.082397 | -0.15106 | -0.086975 | -0.16937 | -0.11902 | -0.022888 | 60.6537 | 60.8917 | 122.6532 | 122.6624 | -0.082397 | 122.6212 | 60.9238 | -0.16937 | 122.6624 | -0.082397 | 60.9238 | 122.6532 | 122.6212 | -122.7997 | -122.9095
319.0156 | 123.056 | -60.8231 | 61.9354 | -0.0076295 | 0.014526 | 0.016022 | 0.0004274 | 0.063019 | -0.0008544 | 0.070068 | -60.91 | 61.8805 | -60.8414 | -60.965 | 61.8073 | 0.11902 | 0.013733 | 0.10986 | 61.8393 | -60.997 | -0.018311 | -0.054932 | -0.086975 | -0.14191 | -0.12817 | -0.17395 | -0.096131 | -0.068664 | 60.8368 | 60.9329 | 122.6303 | 122.7036 | -0.086975 | 122.6624 | 60.9421 | -0.17395 | 122.7036 | -0.086975 | 60.9421 | 122.6303 | 122.6624 | -122.7768 | -122.9324
319.9688 | 123.0011 | -60.8414 | 61.94 | 0.13733 | 0.01709 | 0.01709 | 0.0083314 | 0.065369 | -0.0032044 | 0.07135 | -60.9192 | 61.8942 | -60.8734 | -61.0199 | 61.7661 | 0.086975 | 0.054932 | 0.054932 | 61.8439 | -61.0245 | -0.032043 | -0.045776 | -0.077819 | -0.17853 | -0.17395 | -0.18311 | -0.09613 | -0.045776 | 60.8963 | 60.8963 | 122.6074 | 122.7356 | -0.077819 | 122.6852 | 60.9283 | -0.18311 | 122.7356 | -0.077819 | 60.9283 | 122.6074 | 122.6852 | -122.8134 | -122.9645
321.0156 | 123.1247 | -60.8276 | 61.9034 | 0.16785 | 0.013672 | 0.013886 | -0.001068 | 0.06366 | -0.003418 | 0.07135 | -60.9283 | 61.853 | -60.8643 | -60.9833 | 61.8256 | 0.14648 | -0.07782 | 0.1236 | 61.8347 | -60.9741 | -0.036621 | -0.050354 | -0.10071 | -0.15564 | -0.077819 | -0.14648 | -0.068664 | -0.064087 | 60.7498 | 60.9512 | 122.6532 | 122.6807 | -0.10071 | 122.6624 | 60.9741 | -0.14648 | 122.6807 | -0.10071 | 60.9741 | 122.6532 | 122.6624 | -122.7676 | -122.8775
321.9688 | 123.0331 | -60.8414 | 61.9308 | 0.1297 | 0.015167 | 0.015381 | 0.006836 | 0.064728 | -0.006836 | 0.068787 | -60.9375 | 61.8988 | -60.8917 | -61.0245 | 61.7661 | 0.091553 | 0.036621 | 0.050354 | 61.8576 | -60.9924 | -0.050354 | -0.032043 | -0.09613 | -0.18311 | -0.16479 | -0.15106 | -0.073242 | -0.045776 | 60.878 | 60.8917 | 122.6074 | 122.7402 | -0.09613 | 122.699 | 60.9329 | -0.15106 | 122.7402 | -0.09613 | 60.9329 | 122.6074 | 122.699 | -122.8226 | -122.9233
323.0156 | 123.1293 | -60.8322 | 61.908 | 0.11444 | 0.01474 | 0.011963 | 0.0008546 | 0.065155 | -0.0042724 | 0.072418 | -60.9375 | 61.8439 | -60.8871 | -60.9787 | 61.8256 | 0.15106 | -0.073242 | 0.1236 | 61.8256 | -60.9421 | -0.054932 | -0.064087 | -0.10529 | -0.14648 | -0.082397 | -0.10986 | -0.082397 | -0.050354 | 60.759 | 60.9558 | 122.6578 | 122.6761 | -0.10529 | 122.6578 | 60.9833 | -0.10986 | 122.6761 | -0.10529 | 60.9833 | 122.6578 | 122.6578 | -122.7951 | -122.85
323.9688 | 123.0057 | -60.8368 | 61.9263 | 0.15259 | 0.015381 | 0.014954 | 0.0091858 | 0.06366 | -0.0036316 | 0.071777 | -60.9192 | 61.8851 | -60.9146 | -61.0107 | 61.7889 | 0.068665 | 0.027466 | 0.059509 | 61.8622 | -61.0107 | -0.07782 | -0.041199 | -0.082397 | -0.17395 | -0.13733 | -0.17395 | -0.064087 | -0.004577 | 60.8643 | 60.8963 | 122.6257 | 122.7219 | -0.082397 | 122.699 | 60.9055 | -0.17395 | 122.7219 | -0.082397 | 60.9055 | 122.6257 | 122.699 | -122.8409 | -122.937
325.0156 | 123.0652 | -60.8093 | 61.9125 | 0.22888 | 0.013672 | 0.011322 | 0.0019226 | 0.06366 | -0.001709 | 0.070923 | -60.9695 | 61.8576 | -60.8826 | -61.0657 | 61.7752 | 0.050354 | -0.064087 | 0.036621 | 61.8439 | -60.9558 | -0.073242 | -0.054932 | -0.16022 | -0.25635 | -0.13733 | -0.14648 | -0.068665 | -0.086975 | 60.7452 | 60.8459 | 122.5845 | 122.6669 | -0.16022 | 122.6532 | 60.8597 | -0.14648 | 122.6669 | -0.16022 | 60.8597 | 122.5845 | 122.6532 | -122.7951 | -122.8683
325.9688 | 122.9736 | -60.8597 | 61.94 | 0.27466 | 0.016449 | 0.016022 | 0.0070496 | 0.064087 | -0.005127 | 0.071564 | -60.9741 | 61.8805 | -60.9329 | -61.0703 | 61.7065 | 0.009155 | 0.050354 | -0.032043 | 61.8668 | -61.0062 | -0.073242 | -0.059509 | -0.11444 | -0.21057 | -0.23346 | -0.14649 | -0.073242 | -0.041199 | 60.91 | 60.8276 | 122.5662 | 122.7402 | -0.11444 | 122.7264 | 60.8688 | -0.14649 | 122.7402 | -0.11444 | 60.8688 | 122.5662 | 122.7264 | -122.8729 | -122.9462
326.9844 | 123.0698 | -60.8871 | 61.8896 | 0.41199 | 0.015808 | 0.012604 | 0.0046998 | 0.065796 | -0.004486 | 0.071777 | -60.9787 | 61.8576 | -60.9283 | -61.0519 | 61.7615 | 0.018311 | -0.10986 | -0.004578 | 61.8347 | -60.9604 | -0.041199 | -0.032043 | -0.091553 | -0.16479 | -0.12817 | -0.073242 | -0.054931 | -0.050354 | 60.7773 | 60.8826 | 122.6486 | 122.7448 | -0.091553 | 122.7219 | 60.9055 | -0.073242 | 122.7448 | -0.091553 | 60.9055 | 122.6486 | 122.7219 | -122.818 | -122.85
328.0156 | 123.0469 | -60.8551 | 61.9034 | 0.33569 | 0.014954 | 0.011536 | 0 | 0.06366 | -0.0029906 | 0.070709 | -60.9787 | 61.8164 | -60.9055 | -61.0703 | 61.7798 | 0.050354 | -0.068665 | 0.032043 | 61.8027 | -60.9695 | -0.050354 | -0.086975 | -0.1236 | -0.21515 | -0.1236 | -0.11444 | -0.10071 | -0.073242 | 60.7864 | 60.8871 | 122.6349 | 122.6715 | -0.1236 | 122.6578 | 60.9055 | -0.11444 | 122.6715 | -0.1236 | 60.9055 | 122.6349 | 122.6578 | -122.8088 | -122.8729
328.9688 | 122.9782 | -60.8322 | 61.9766 | -0.11444 | 0.018158 | 0.013886 | 0.0064088 | 0.06131 | -0.0029906 | 0.070923 | -60.9695 | 61.8713 | -60.8826 | -61.0611 | 61.7432 | 0.07782 | 0.14191 | 0.068665 | 61.8713 | -60.9695 | -0.050354 | -0.10529 | -0.13733 | -0.22888 | -0.23346 | -0.13733 | -0.10529 | -0.086975 | 60.9741 | 60.9009 | 122.5754 | 122.7036 | -0.13733 | 122.7036 | 60.91 | -0.13733 | 122.7036 | -0.13733 | 60.91 | 122.5754 | 122.7036 | -122.8592 | -122.9462
330.0156 | 123.0331 | -60.8505 | 61.9034 | 0.24414 | 0.012817 | 0.013672 | 0.00235 | 0.061737 | -0.0025634 | 0.073059 | -60.965 | 61.8027 | -60.8917 | -61.0565 | 61.7569 | 0.054932 | -0.045776 | 0.032043 | 61.821 | -60.9741 | -0.041199 | -0.10071 | -0.11444 | -0.20599 | -0.14648 | -0.1236 | -0.082397 | -0.073242 | 60.8047 | 60.8826 | 122.6074 | 122.6532 | -0.11444 | 122.6715 | 60.9055 | -0.1236 | 122.6532 | -0.11444 | 60.9055 | 122.6074 | 122.6715 | -122.7951 | -122.8775
330.9688 | 122.937 | -60.8597 | 61.94 | 0.28992 | 0.015595 | 0.012604 | 0.0087586 | 0.063873 | -0.006195 | 0.071991 | -60.9833 | 61.8988 | -60.9009 | -61.0886 | 61.7065 | 0.013733 | 0.041199 | -0.041199 | 61.8484 | -61.0291 | -0.041199 | -0.041198 | -0.1236 | -0.22888 | -0.23346 | -0.16937 | -0.091552 | -0.082397 | 60.9009 | 60.8185 | 122.5662 | 122.7585 | -0.1236 | 122.7081 | 60.8734 | -0.16937 | 122.7585 | -0.1236 | 60.8734 | 122.5662 | 122.7081 | -122.8409 | -122.9691
332.0312 | 122.9599 | -60.878 | 61.9446 | 0.38147 | 0.01709 | 0.016449 | 0.008545 | 0.065582 | -0.006195 | 0.070068 | -61.0199 | 61.8439 | -60.9283 | -61.1298 | 61.6791 | -0.036621 | 0.027466 | -0.082397 | 61.8484 | -61.0107 | -0.050354 | -0.10071 | -0.14191 | -0.25177 | -0.2655 | -0.13275 | -0.09613 | -0.091552 | 60.9055 | 60.7956 | 122.5571 | 122.7219 | -0.14191 | 122.7264 | 60.8414 | -0.13275 | 122.7219 | -0.14191 | 60.8414 | 122.5571 | 122.7264 | -122.8729 | -122.9553
332.9688 | 123.024 | -60.8322 | 61.908 | 0.16022 | 0.01474 | 0.012604 | 0.0057678 | 0.063232 | -0.0055542 | 0.072418 | -60.9283 | 61.8576 | -60.9146 | -61.0016 | 61.7706 | 0.09613 | 0.027466 | 0.050354 | 61.8439 | -60.9924 | -0.082398 | -0.050354 | -0.096131 | -0.16937 | -0.13733 | -0.16022 | -0.064087 | -0.013733 | 60.8597 | 60.8826 | 122.6028 | 122.6898 | -0.096131 | 122.6761 | 60.9283 | -0.16022 | 122.6898 | -0.096131 | 60.9283 | 122.6028 | 122.6761 | -122.8226 | -122.9004
334.0156 | 123.056 | -60.8368 | 61.908 | 0.24414 | 0.014954 | 0.011322 | -0.0019226 | 0.062164 | -0.0040588 | 0.073486 | -60.9833 | 61.821 | -60.878 | -61.0428 | 61.7661 | 0.050354 | -0.022888 | 0.050354 | 61.8256 | -60.9879 | -0.041199 | -0.086975 | -0.14648 | -0.20599 | -0.14191 | -0.15106 | -0.082397 | -0.10528 | 60.8139 | 60.8871 | 122.6028 | 122.6578 | -0.14648 | 122.6624 | 60.8871 | -0.15106 | 122.6578 | -0.14648 | 60.8871 | 122.6028 | 122.6624 | -122.7859 | -122.8958
334.9688 | 122.9645 | -60.8322 | 61.9766 | -0.022889 | 0.015167 | 0.012604 | 0.0032044 | 0.06131 | -0.0049134 | 0.070923 | -60.9604 | 61.8576 | -60.8963 | -61.0336 | 61.7752 | 0.07782 | 0.14648 | 0.07782 | 61.8805 | -60.9879 | -0.064087 | -0.11902 | -0.12817 | -0.20142 | -0.20142 | -0.15564 | -0.096131 | -0.064087 | 60.9787 | 60.91 | 122.6074 | 122.6898 | -0.12817 | 122.7127 | 60.91 | -0.15564 | 122.6898 | -0.12817 | 60.91 | 122.6074 | 122.7127 | -122.8729 | -122.9645
336.0156 | 123.0743 | -60.8826 | 61.8805 | 0.40436 | 0.015595 | 0.016449 | 0.006836 | 0.064087 | -0.0046996 | 0.072205 | -61.0153 | 61.8484 | -60.9283 | -61.116 | 61.702 | -0.013733 | -0.022888 | -0.07782 | 61.8393 | -61.0062 | -0.045777 | -0.032043 | -0.13275 | -0.23346 | -0.17853 | -0.1236 | -0.041199 | -0.086975 | 60.8597 | 60.8047 | 122.5845 | 122.731 | -0.13275 | 122.7219 | 60.8688 | -0.1236 | 122.731 | -0.13275 | 60.8688 | 122.5845 | 122.7219 | -122.8088 | -122.8867
336.9844 | 123.0789 | -60.8185 | 61.9125 | 0.39673 | 0.018372 | 0.014526 | 0.0072632 | 0.0643 | -0.0046996 | 0.071136 | -60.965 | 61.8393 | -60.8963 | -61.0336 | 61.7615 | 0.054932 | -0.11444 | 0.004578 | 61.8027 | -60.997 | -0.07782 | -0.073243 | -0.14648 | -0.21515 | -0.15106 | -0.17853 | -0.10986 | -0.068665 | 60.704 | 60.8231 | 122.58 | 122.6578 | -0.14648 | 122.6212 | 60.8734 | -0.17853 | 122.6578 | -0.14648 | 60.8734 | 122.58 | 122.6212 | -122.8088 | -122.9095
338.0156 | 123.0972 | -60.8231 | 61.9217 | 0.41199 | 0.014099 | 0.016663 | 0.004059 | 0.0643 | -0.0038452 | 0.073273 | -60.965 | 61.8118 | -60.91 | -61.0382 | 61.7889 | 0.07782 | -0.15564 | 0.036621 | 61.7798 | -60.997 | -0.086975 | -0.10986 | -0.14191 | -0.21515 | -0.13275 | -0.17395 | -0.14191 | -0.054932 | 60.6674 | 60.8597 | 122.612 | 122.6349 | -0.14191 | 122.6028 | 60.9009 | -0.17395 | 122.6349 | -0.14191 | 60.9009 | 122.612 | 122.6028 | -122.8317 | -122.9187
338.9688 | 123.0103 | -60.8093 | 61.9492 | 0.091552 | 0.015167 | 0.014954 | 0.0066224 | 0.0643 | -0.0064086 | 0.070496 | -60.9329 | 61.8622 | -60.9055 | -61.0336 | 61.7706 | 0.10071 | 0.059509 | 0.059509 | 61.853 | -60.9421 | -0.096131 | -0.086975 | -0.1236 | -0.2243 | -0.17853 | -0.13275 | -0.096131 | -0.027465 | 60.8688 | 60.8688 | 122.58 | 122.6715 | -0.1236 | 122.6624 | 60.91 | -0.13275 | 122.6715 | -0.1236 | 60.91 | 122.58 | 122.6624 | -122.8546 | -122.8912
340.0156 | 123.0927 | -60.7956 | 61.8942 | 0.39673 | 0.015595 | 0.012604 | 0.0055542 | 0.065369 | -0.0023498 | 0.07135 | -60.9283 | 61.8027 | -60.9192 | -61.0199 | 61.7981 | 0.064087 | -0.16022 | 0.041199 | 61.8118 | -60.965 | -0.1236 | -0.091553 | -0.13275 | -0.2243 | -0.09613 | -0.16937 | -0.082397 | -0.009156 | 60.6354 | 60.8368 | 122.5937 | 122.5983 | -0.13275 | 122.6074 | 60.8597 | -0.16937 | 122.5983 | -0.13275 | 60.8597 | 122.5937 | 122.6074 | -122.8134 | -122.8592
340.9688 | 123.0835 | -60.8139 | 61.9583 | 0.030518 | 0.013458 | 0.013672 | 0.0010682 | 0.064087 | -0.003418 | 0.07135 | -60.91 | 61.8073 | -60.8643 | -60.9787 | 61.8484 | 0.17395 | -0.022888 | 0.17853 | 61.7935 | -60.9238 | -0.050354 | -0.15106 | -0.09613 | -0.16479 | -0.10986 | -0.10986 | -0.16479 | -0.045776 | 60.791 | 60.9924 | 122.6624 | 122.6212 | -0.09613 | 122.6074 | 60.9879 | -0.10986 | 122.6212 | -0.09613 | 60.9879 | 122.6624 | 122.6074 | -122.8226 | -122.8821
342.0312 | 122.9691 | -60.8414 | 61.9995 | -0.015259 | 0.017304 | 0.010895 | 0.0046998 | 0.061523 | -0.002777 | 0.072205 | -60.9833 | 61.8942 | -60.8688 | -61.0794 | 61.7157 | 0.073242 | 0.15106 | 0.022888 | 61.8942 | -61.0062 | -0.027465 | -0.10529 | -0.14191 | -0.23804 | -0.28381 | -0.1648 | -0.10529 | -0.11444 | 60.9924 | 60.8643 | 122.5571 | 122.7356 | -0.14191 | 122.7356 | 60.9146 | -0.1648 | 122.7356 | -0.14191 | 60.9146 | 122.5571 | 122.7356 | -122.8683 | -123.0057
342.9688 | 123.1064 | -60.8093 | 61.94 | 0.1297 | 0.013245 | 0.012177 | -0.0012816 | 0.062164 | -0.0029906 | 0.073914 | -60.9421 | 61.7935 | -60.9009 | -60.9924 | 61.8164 | 0.13733 | -0.054932 | 0.11902 | 61.8576 | -60.9375 | -0.091553 | -0.14648 | -0.13275 | -0.18311 | -0.1236 | -0.12817 | -0.082397 | -0.041199 | 60.7544 | 60.9283 | 122.6257 | 122.6028 | -0.13275 | 122.6669 | 60.9467 | -0.12817 | 122.6028 | -0.13275 | 60.9467 | 122.6257 | 122.6669 | -122.8409 | -122.8775
344.0156 | 122.9416 | -60.878 | 61.9217 | 0.35095 | 0.01474 | 0.015595 | 0.0070496 | 0.059601 | -0.0053406 | 0.072418 | -61.0245 | 61.821 | -60.9467 | -61.116 | 61.6837 | -0.041199 | 0 | -0.086975 | 61.8301 | -60.9924 | -0.068664 | -0.10071 | -0.14648 | -0.23804 | -0.23804 | -0.11444 | -0.091553 | -0.07782 | 60.878 | 60.791 | 122.5616 | 122.699 | -0.14648 | 122.7081 | 60.8368 | -0.11444 | 122.699 | -0.14648 | 60.8368 | 122.5616 | 122.7081 | -122.8683 | -122.9141
344.9688 | 123.0606 | -60.8093 | 61.94 | 0.20599 | 0.011749 | 0.014099 | 0.0002136 | 0.060882 | -0.0046996 | 0.073273 | -60.9741 | 61.7844 | -60.8963 | -61.0428 | 61.9125 | 0.16022 | -0.07782 | 0.059509 | 61.8439 | -60.9421 | -0.086975 | -0.15564 | -0.16479 | -0.23346 | -0.027465 | -0.13275 | -0.09613 | -0.07782 | 60.7315 | 60.8688 | 122.7219 | 122.5937 | -0.16479 | 122.6532 | 60.9695 | -0.13275 | 122.5937 | -0.16479 | 60.9695 | 122.7219 | 122.6532 | -122.8363 | -122.8821
346.0156 | 122.9645 | -60.8414 | 61.9171 | 0.32806 | 0.016663 | 0.013886 | 0.0074768 | 0.064087 | -0.003418 | 0.071777 | -61.0245 | 61.8439 | -60.9238 | -61.1343 | 61.6653 | -0.036621 | 0.022888 | -0.10986 | 61.8393 | -60.997 | -0.082397 | -0.073242 | -0.18311 | -0.29297 | -0.25177 | -0.15564 | -0.07782 | -0.10071 | 60.8643 | 60.7315 | 122.5067 | 122.6852 | -0.18311 | 122.6807 | 60.8047 | -0.15564 | 122.6852 | -0.18311 | 60.8047 | 122.5067 | 122.6807 | -122.8409 | -122.9141
346.9688 | 123.0972 | -60.8093 | 61.94 | 0.10681 | 0.010895 | 0.013245 | 0.0019226 | 0.061096 | -0.002777 | 0.070923 | -60.9238 | 61.8073 | -60.8963 | -60.997 | 61.8164 | 0.15564 | -0.059509 | 0.16479 | 61.7981 | -60.9558 | -0.086975 | -0.13275 | -0.11444 | -0.18768 | -0.1236 | -0.14648 | -0.14191 | -0.027466 | 60.7498 | 60.9741 | 122.6257 | 122.6166 | -0.11444 | 122.6074 | 60.965 | -0.14648 | 122.6166 | -0.11444 | 60.965 | 122.6257 | 122.6074 | -122.8363 | -122.8958
348.0156 | 123.0148 | -60.8231 | 61.9537 | 0.18311 | 0.016663 | 0.010254 | 0.0081178 | 0.060882 | -0.005127 | 0.072845 | -61.0519 | 61.8073 | -60.9238 | -61.0336 | 61.734 | 0.054932 | 0.041199 | 0.036621 | 61.8347 | -60.9375 | -0.10071 | -0.14648 | -0.22888 | -0.21057 | -0.21973 | -0.11444 | -0.11902 | -0.12817 | 60.8643 | 60.8597 | 122.5571 | 122.6303 | -0.22888 | 122.6578 | 60.878 | -0.11444 | 122.6303 | -0.22888 | 60.878 | 122.5571 | 122.6578 | -122.8775 | -122.8912
348.9688 | 123.0743 | -60.7819 | 61.9537 | 0.45776 | 0.01239 | 0.01474 | 0.0019226 | 0.059174 | -0.002777 | 0.069855 | -60.9238 | 61.7935 | -60.9009 | -60.9741 | 61.8301 | 0.16479 | 0 | 0.16022 | 61.8164 | -60.9467 | -0.11902 | -0.16022 | -0.14191 | -0.19226 | -0.1236 | -0.16479 | -0.13733 | -0.022888 | 60.7819 | 60.9421 | 122.612 | 122.5754 | -0.14191 | 122.5983 | 60.9467 | -0.16479 | 122.5754 | -0.14191 | 60.9467 | 122.612 | 122.5983 | -122.8546 | -122.9004
350.0156 | 122.9095 | -60.8505 | 61.908 | 0.3891 | 0.014526 | 0.014313 | 0.0066224 | 0.061737 | -0.0040588 | 0.070923 | -61.0153 | 61.8301 | -60.9375 | -61.1206 | 61.6837 | -0.032043 | 0.009155 | -0.09613 | 61.821 | -60.9879 | -0.086975 | -0.07782 | -0.1648 | -0.27008 | -0.2243 | -0.13733 | -0.086975 | -0.07782 | 60.8597 | 60.7544 | 122.5342 | 122.6807 | -0.1648 | 122.6715 | 60.8185 | -0.13733 | 122.6807 | -0.1648 | 60.8185 | 122.5342 | 122.6715 | -122.8455 | -122.8958
350.9688 | 123.0469 | -60.8231 | 61.8988 | 0.29755 | 0.013886 | 0.012177 | 0.0002136 | 0.058105 | -0.003418 | 0.071777 | -60.9787 | 61.7752 | -60.9055 | -61.0611 | 61.7477 | 0.054932 | -0.068665 | 0.022888 | 61.8118 | -60.9787 | -0.082398 | -0.1236 | -0.15564 | -0.23804 | -0.15106 | -0.15564 | -0.086975 | -0.073242 | 60.7544 | 60.8459 | 122.5708 | 122.5983 | -0.15564 | 122.6349 | 60.878 | -0.15564 | 122.5983 | -0.15564 | 60.878 | 122.5708 | 122.6349 | -122.8043 | -122.8775
352.0156 | 122.9507 | -60.8322 | 61.9583 | 0.25177 | 0.01709 | 0.015808 | 0.0076904 | 0.061951 | -0.002777 | 0.070923 | -60.9787 | 61.8301 | -60.9146 | -61.0565 | 61.7157 | 0.013733 | 0.032043 | -0.041199 | 61.8301 | -60.9833 | -0.082398 | -0.12817 | -0.14648 | -0.22431 | -0.24261 | -0.15106 | -0.12817 | -0.064087 | 60.8643 | 60.791 | 122.5479 | 122.6624 | -0.14648 | 122.6624 | 60.8459 | -0.15106 | 122.6624 | -0.14648 | 60.8459 | 122.5479 | 122.6624 | -122.8729 | -122.9416
352.9688 | 123.0698 | -60.8047 | 61.9217 | 0.022888 | 0.016022 | 0.01004 | -0.0002136 | 0.059387 | -0.0046996 | 0.072632 | -60.9421 | 61.821 | -60.8826 | -61.0291 | 61.7706 | 0.086975 | -0.054932 | 0.045776 | 61.8118 | -60.9467 | -0.077819 | -0.10071 | -0.13733 | -0.2243 | -0.15106 | -0.14191 | -0.10986 | -0.05951 | 60.7498 | 60.8505 | 122.5754 | 122.6257 | -0.13733 | 122.6166 | 60.8917 | -0.14191 | 122.6257 | -0.13733 | 60.8917 | 122.5754 | 122.6166 | -122.8043 | -122.8683
354.0156 | 123.0057 | -60.8414 | 61.9492 | 0.86975 | 0.016663 | 0.011322 | 0.0074768 | 0.063019 | -0.0057678 | 0.072205 | -60.9421 | 61.821 | -60.91 | -61.0291 | 61.7615 | 0.054932 | 0.032043 | 0.027466 | 61.8439 | -60.9741 | -0.068664 | -0.12817 | -0.10071 | -0.18768 | -0.18768 | -0.13275 | -0.10529 | -0.032044 | 60.8734 | 60.8688 | 122.6028 | 122.6624 | -0.10071 | 122.6852 | 60.8963 | -0.13275 | 122.6624 | -0.10071 | 60.8963 | 122.6028 | 122.6852 | -122.8592 | -122.9233
354.9688 | 123.0515 | -60.8276 | 61.9034 | 0.36621 | 0.011108 | 0.015595 | 0.0010682 | 0.062805 | -0.0036316 | 0.070068 | -60.9879 | 61.7752 | -60.8826 | -61.0657 | 61.7523 | 0.041199 | -0.10529 | 0.013733 | 61.7844 | -60.965 | -0.054931 | -0.12817 | -0.16022 | -0.23804 | -0.15106 | -0.13733 | -0.11902 | -0.10529 | 60.7224 | 60.8414 | 122.58 | 122.6028 | -0.16022 | 122.612 | 60.8688 | -0.13733 | 122.6028 | -0.16022 | 60.8688 | 122.58 | 122.612 | -122.7859 | -122.8683
356.0156 | 122.9599 | -60.8414 | 61.9492 | 0.19073 | 0.015381 | 0.014954 | 0.0079042 | 0.062805 | -0.0046996 | 0.070923 | -60.9375 | 61.8759 | -60.91 | -61.0428 | 61.7157 | 0.013733 | 0.018311 | -0.027466 | 61.8576 | -60.9833 | -0.068664 | -0.073242 | -0.09613 | -0.20142 | -0.23346 | -0.14191 | -0.091553 | -0.027466 | 60.8597 | 60.8139 | 122.5571 | 122.7173 | -0.09613 | 122.699 | 60.8551 | -0.14191 | 122.7173 | -0.09613 | 60.8551 | 122.5571 | 122.699 | -122.8592 | -122.9324
356.9688 | 123.0286 | -60.8002 | 61.9171 | 0.36621 | 0.013031 | 0.010681 | 0.0004274 | 0.061096 | -0.004486 | 0.071564 | -60.9924 | 61.7981 | -60.8826 | -61.0428 | 61.7661 | 0.054932 | -0.068665 | 0.013733 | 61.8256 | -60.9467 | -0.082397 | -0.11902 | -0.19226 | -0.24262 | -0.15106 | -0.14648 | -0.091552 | -0.10986 | 60.7315 | 60.8139 | 122.5662 | 122.5983 | -0.19226 | 122.6257 | 60.8551 | -0.14648 | 122.5983 | -0.19226 | 60.8551 | 122.5662 | 122.6257 | -122.7997 | -122.8638
358.0156 | 123.0148 | -60.8093 | 61.9446 | -0.0076295 | 0.015808 | 0.014313 | 0.0089722 | 0.060669 | -0.0042724 | 0.070923 | -60.9375 | 61.8759 | -60.8917 | -61.0245 | 61.7706 | 0.091553 | 0.041199 | 0.054932 | 61.8393 | -60.9467 | -0.082398 | -0.068664 | -0.12817 | -0.21515 | -0.17395 | -0.13733 | -0.10529 | -0.045776 | 60.8505 | 60.8643 | 122.58 | 122.6852 | -0.12817 | 122.6486 | 60.9009 | -0.13733 | 122.6852 | -0.12817 | 60.9009 | 122.58 | 122.6486 | -122.8363 | -122.8912
358.9688 | 123.0881 | -60.791 | 61.9492 | 0.10681 | 0.014313 | 0.01004 | 0.0008546 | 0.062805 | -0.003418 | 0.071136 | -60.8963 | 61.8118 | -60.8826 | -60.9283 | 61.8805 | 0.17395 | -0.045776 | 0.16937 | 61.8073 | -60.965 | -0.091552 | -0.13733 | -0.10529 | -0.13733 | -0.068665 | -0.17395 | -0.14191 | -0.013733 | 60.7452 | 60.9604 | 122.6715 | 122.6028 | -0.10529 | 122.5983 | 60.965 | -0.17395 | 122.6028 | -0.10529 | 60.965 | 122.6715 | 122.5983 | -122.8317 | -122.9141
360.0156 | 122.9874 | -60.8231 | 61.9583 | 0.27466 | 0.015381 | 0.012817 | 0.0072632 | 0.062805 | -0.0066222 | 0.071564 | -60.9833 | 61.8622 | -60.9192 | -61.0748 | 61.6928 | -0.004578 | 0.036621 | -0.059509 | 61.821 | -60.9924 | -0.09613 | -0.09613 | -0.16022 | -0.25177 | -0.2655 | -0.16937 | -0.13733 | -0.064087 | 60.8597 | 60.7636 | 122.5159 | 122.6852 | -0.16022 | 122.644 | 60.8185 | -0.16937 | 122.6852 | -0.16022 | 60.8185 | 122.5159 | 122.644 | -122.8775 | -122.9507
360.9688 | 123.111 | -60.7819 | 61.9446 | 0.17548 | 0.013458 | 0.012604 | 0.0027772 | 0.060028 | -0.0040588 | 0.072632 | -60.9146 | 61.8439 | -60.8505 | -60.9924 | 61.8347 | 0.16022 | -0.073242 | 0.13275 | 61.8164 | -60.9512 | -0.068665 | -0.10071 | -0.13275 | -0.21057 | -0.10986 | -0.16937 | -0.12817 | -0.064087 | 60.7086 | 60.9146 | 122.6166 | 122.6257 | -0.13275 | 122.5983 | 60.9421 | -0.16937 | 122.6257 | -0.13275 | 60.9421 | 122.6166 | 122.5983 | -122.7951 | -122.8958
362.0156 | 122.9691 | -60.8185 | 61.972 | 0.17548 | 0.015381 | 0.013245 | 0.008545 | 0.062805 | -0.0064086 | 0.071777 | -60.9375 | 61.8439 | -60.9146 | -61.0474 | 61.7432 | 0.050354 | 0.009155 | -0.009155 | 61.853 | -60.9879 | -0.096131 | -0.12817 | -0.11902 | -0.22888 | -0.22888 | -0.16937 | -0.11902 | -0.022888 | 60.8276 | 60.8093 | 122.5616 | 122.6624 | -0.11902 | 122.6715 | 60.8688 | -0.16937 | 122.6624 | -0.11902 | 60.8688 | 122.5616 | 122.6715 | -122.8867 | -122.9599
362.9688 | 123.0698 | -60.8322 | 61.908 | 0.35858 | 0.013886 | 0.014954 | 0.0012818 | 0.060669 | -0.0055542 | 0.070496 | -60.9238 | 61.8027 | -60.8734 | -61.0016 | 61.8027 | 0.082397 | -0.16022 | 0.041199 | 61.7889 | -60.9604 | -0.041199 | -0.10529 | -0.091553 | -0.16937 | -0.10529 | -0.12817 | -0.11902 | -0.050354 | 60.672 | 60.8734 | 122.6349 | 122.6349 | -0.091553 | 122.6212 | 60.9146 | -0.12817 | 122.6349 | -0.091553 | 60.9146 | 122.6349 | 122.6212 | -122.7814 | -122.8683
364.0156 | 123.0011 | -60.8276 | 61.9629 | 0.053405 | 0.016449 | 0.01474 | 0.0076904 | 0.062164 | -0.0032044 | 0.070923 | -60.9329 | 61.8805 | -60.878 | -61.0199 | 61.7615 | 0.09613 | 0.059509 | 0.059509 | 61.8622 | -60.965 | -0.050354 | -0.082398 | -0.10528 | -0.19226 | -0.20142 | -0.13733 | -0.10071 | -0.054931 | 60.8871 | 60.8871 | 122.5891 | 122.7081 | -0.10528 | 122.6898 | 60.9238 | -0.13733 | 122.7081 | -0.10528 | 60.9238 | 122.5891 | 122.6898 | -122.8409 | -122.9279
364.9688 | 123.0606 | -60.8002 | 61.9492 | 0.20599 | 0.014526 | 0.014313 | -0.0004272 | 0.059601 | -0.003418 | 0.071991 | -60.965 | 61.821 | -60.8551 | -61.0062 | 61.821 | 0.11444 | -0.050354 | 0.086975 | 61.821 | -60.9833 | -0.054932 | -0.12817 | -0.16479 | -0.20599 | -0.12817 | -0.1831 | -0.12817 | -0.10986 | 60.7498 | 60.8871 | 122.6212 | 122.6212 | -0.16479 | 122.6212 | 60.9146 | -0.1831 | 122.6212 | -0.16479 | 60.9146 | 122.6212 | 122.6212 | -122.8043 | -122.9324
366.0156 | 122.9599 | -60.8459 | 62.0041 | 0.038147 | 0.015808 | 0.012177 | 0.0074768 | 0.062378 | -0.004486 | 0.071564 | -60.9741 | 61.908 | -60.9146 | -61.0474 | 61.734 | 0.082397 | 0.10986 | 0.027466 | 61.8484 | -60.9879 | -0.068665 | -0.09613 | -0.12817 | -0.20142 | -0.27008 | -0.14191 | -0.15564 | -0.059509 | 60.9558 | 60.8734 | 122.58 | 122.7539 | -0.12817 | 122.6944 | 60.9283 | -0.14191 | 122.7539 | -0.12817 | 60.9283 | 122.58 | 122.6944 | -122.9187 | -122.9919
366.9688 | 123.0331 | -60.8231 | 61.9308 | 0.22888 | 0.014099 | 0.016449 | 0.0021362 | 0.060242 | -0.0025634 | 0.070923 | -60.9695 | 61.853 | -60.8963 | -60.9879 | 61.908 | 0.15564 | -0.12817 | 0.022888 | 61.8164 | -60.9558 | -0.073242 | -0.07782 | -0.14648 | -0.16479 | -0.022888 | -0.13275 | -0.11444 | -0.073242 | 60.6949 | 60.8459 | 122.731 | 122.6761 | -0.14648 | 122.6395 | 60.9787 | -0.13275 | 122.6761 | -0.14648 | 60.9787 | 122.731 | 122.6395 | -122.8271 | -122.8867
368.0156 | 123.0286 | -60.8276 | 61.9812 | 0.061035 | 0.014313 | 0.013031 | 0.0070496 | 0.060242 | -0.006195 | 0.070496 | -60.9695 | 61.9125 | -60.9055 | -61.0336 | 61.7523 | 0.086975 | 0.10529 | 0.050354 | 61.8622 | -60.9833 | -0.07782 | -0.068664 | -0.14191 | -0.20599 | -0.22888 | -0.15564 | -0.11902 | -0.064086 | 60.9329 | 60.878 | 122.58 | 122.7402 | -0.14191 | 122.6898 | 60.9146 | -0.15564 | 122.7402 | -0.14191 | 60.9146 | 122.58 | 122.6898 | -122.8867 | -122.9645
368.9688 | 123.0835 | -60.8047 | 61.9034 | 0.54169 | 0.015595 | 0.010681 | 0.0053406 | 0.064514 | -0.0036316 | 0.073273 | -60.9329 | 61.8622 | -60.8826 | -61.0016 | 61.7844 | 0.086975 | -0.18768 | 0.013733 | 61.7889 | -60.9787 | -0.077819 | -0.041198 | -0.12817 | -0.19684 | -0.11902 | -0.17395 | -0.11444 | -0.050354 | 60.6171 | 60.8185 | 122.5891 | 122.6669 | -0.12817 | 122.5937 | 60.8917 | -0.17395 | 122.6669 | -0.12817 | 60.8917 | 122.5891 | 122.5937 | -122.7859 | -122.8821
369.9688 | 123.0881 | -60.8414 | 61.8942 | 0.42725 | 0.016235 | 0.008545 | 0.0070496 | 0.065369 | -0.0029906 | 0.071991 | -60.9558 | 61.8484 | -60.9055 | -61.0336 | 61.7569 | 0.041199 | -0.14648 | -0.027466 | 61.821 | -60.9924 | -0.064087 | -0.045776 | -0.11444 | -0.19226 | -0.13733 | -0.15106 | -0.073242 | -0.050354 | 60.6949 | 60.8139 | 122.5983 | 122.6898 | -0.11444 | 122.6624 | 60.8826 | -0.15106 | 122.6898 | -0.11444 | 60.8826 | 122.5983 | 122.6624 | -122.7997 | -122.8867
371.0156 | 123.0011 | -60.8276 | 61.9492 | -0.045776 | 0.016022 | 0.01709 | 0.0046998 | 0.060028 | -0.0025634 | 0.071564 | -60.9329 | 61.9034 | -60.8643 | -61.0245 | 61.8073 | 0.1236 | 0.09613 | 0.086975 | 61.8896 | -60.9695 | -0.036621 | -0.045777 | -0.10528 | -0.19684 | -0.14191 | -0.14191 | -0.05951 | -0.068664 | 60.9238 | 60.9146 | 122.6349 | 122.731 | -0.10528 | 122.7173 | 60.9512 | -0.14191 | 122.731 | -0.10528 | 60.9512 | 122.6349 | 122.7173 | -122.8134 | -122.9187
371.9688 | 123.0057 | -60.8322 | 61.9263 | 0.34332 | 0.016876 | 0.013245 | 0.006836 | 0.063873 | -0.0046996 | 0.072632 | -61.0153 | 61.908 | -60.9009 | -61.0886 | 61.6928 | -0.013733 | -0.059509 | -0.10071 | 61.8256 | -61.0062 | -0.068665 | -0.018311 | -0.18311 | -0.25635 | -0.23346 | -0.17395 | -0.10071 | -0.11444 | 60.7727 | 60.7315 | 122.525 | 122.7402 | -0.18311 | 122.6578 | 60.8185 | -0.17395 | 122.7402 | -0.18311 | 60.8185 | 122.525 | 122.6578 | -122.8271 | -122.9324
372.9844 | 123.0881 | -60.8093 | 61.8851 | 0.48065 | 0.015808 | 0.015167 | 0.0038452 | 0.063232 | -0.0029906 | 0.073486 | -60.9055 | 61.8164 | -60.91 | -61.0107 | 61.7935 | 0.073242 | -0.18768 | 0.022888 | 61.7935 | -60.9833 | -0.10071 | -0.068665 | -0.096131 | -0.20142 | -0.091553 | -0.17395 | -0.091553 | 0.004577 | 60.6216 | 60.8322 | 122.6028 | 122.6257 | -0.096131 | 122.6028 | 60.8826 | -0.17395 | 122.6257 | -0.096131 | 60.8826 | 122.6028 | 122.6028 | -122.7951 | -122.8683
374.0156 | 122.9507 | -60.8276 | 61.9949 | -0.015259 | 0.016663 | 0.016235 | 0.0032044 | 0.060882 | -0.0049134 | 0.071136 | -60.9741 | 61.9034 | -60.8826 | -61.0474 | 61.7477 | 0.086975 | 0.14191 | 0.041199 | 61.9034 | -60.997 | -0.054931 | -0.091553 | -0.14648 | -0.21973 | -0.24719 | -0.16937 | -0.091553 | -0.091553 | 60.9695 | 60.8688 | 122.5754 | 122.731 | -0.14648 | 122.731 | 60.9146 | -0.16937 | 122.731 | -0.14648 | 60.9146 | 122.5754 | 122.731 | -122.8775 | -122.9919
374.9688 | 122.9874 | -60.8597 | 61.9537 | 0.28992 | 0.01944 | 0.017304 | 0.0070496 | 0.065155 | -0.0040588 | 0.071136 | -61.0062 | 61.908 | -60.9055 | -61.0794 | 61.6791 | -0.009155 | -0.013733 | -0.091553 | 61.8668 | -61.0107 | -0.045777 | -0.045776 | -0.14649 | -0.21973 | -0.27466 | -0.15106 | -0.086975 | -0.10071 | 60.8459 | 60.7681 | 122.5388 | 122.7676 | -0.14649 | 122.7264 | 60.8505 | -0.15106 | 122.7676 | -0.14649 | 60.8505 | 122.5388 | 122.7264 | -122.8592 | -122.9645
376.0156 | 122.9919 | -60.791 | 61.9446 | -0.053406 | 0.015808 | 0.014954 | 0.0025636 | 0.06131 | -0.0064086 | 0.07135 | -60.8963 | 61.9263 | -60.8688 | -60.9879 | 61.8118 | 0.16479 | 0.054932 | 0.11902 | 61.8713 | -60.9695 | -0.077819 | -0.01831 | -0.10529 | -0.19684 | -0.13275 | -0.17853 | -0.073242 | -0.027466 | 60.8459 | 60.91 | 122.6028 | 122.7173 | -0.10529 | 122.6624 | 60.9558 | -0.17853 | 122.7173 | -0.10529 | 60.9558 | 122.6028 | 122.6624 | -122.8134 | -122.9141
376.9688 | 122.9141 | -60.8734 | 61.9629 | 0.27466 | 0.015808 | 0.015167 | 0.0046998 | 0.065155 | -0.0036316 | 0.073486 | -60.9879 | 61.9171 | -60.9329 | -61.1252 | 61.6791 | -0.027466 | 0.009155 | -0.086975 | 61.8713 | -61.0062 | -0.059509 | -0.045777 | -0.11444 | -0.25177 | -0.28381 | -0.13275 | -0.091553 | -0.054932 | 60.8826 | 60.7864 | 122.5525 | 122.7905 | -0.11444 | 122.7448 | 60.8459 | -0.13275 | 122.7905 | -0.11444 | 60.8459 | 122.5525 | 122.7448 | -122.8958 | -122.9691
378.0156 | 123.056 | -60.8093 | 61.9263 | 0.10681 | 0.016235 | 0.015808 | -0.0014952 | 0.063019 | -0.0021362 | 0.070709 | -60.9329 | 61.8713 | -60.8871 | -60.997 | 61.8256 | 0.14648 | -0.064087 | 0.10071 | 61.853 | -60.965 | -0.07782 | -0.054932 | -0.1236 | -0.18768 | -0.10071 | -0.15564 | -0.073243 | -0.045776 | 60.7452 | 60.91 | 122.6349 | 122.6807 | -0.1236 | 122.6624 | 60.9558 | -0.15564 | 122.6807 | -0.1236 | 60.9558 | 122.6349 | 122.6624 | -122.8134 | -122.8912
378.9688 | 123.0057 | -60.8276 | 61.9583 | 0.2594 | 0.014313 | 0.013886 | 0.0076904 | 0.06366 | -0.0049134 | 0.069 | -60.8871 | 61.8851 | -60.91 | -60.9924 | 61.7798 | 0.10986 | 0.027466 | 0.045776 | 61.8805 | -60.997 | -0.082397 | -0.073242 | -0.059509 | -0.16479 | -0.17853 | -0.16937 | -0.07782 | 0.022888 | 60.8551 | 60.8734 | 122.6074 | 122.7127 | -0.059509 | 122.7081 | 60.9375 | -0.16937 | 122.7127 | -0.059509 | 60.9375 | 122.6074 | 122.7081 | -122.8683 | -122.9553
379.9688 | 123.0469 | -60.8414 | 61.8988 | 0.4425 | 0.016235 | 0.010468 | 0.0057678 | 0.067718 | -0.0036316 | 0.072205 | -60.9421 | 61.8805 | -60.8826 | -61.0336 | 61.7706 | 0.050354 | -0.14191 | 0 | 61.8164 | -61.0016 | -0.041198 | -0.018311 | -0.10071 | -0.19226 | -0.12817 | -0.16022 | -0.082398 | -0.05951 | 60.6995 | 60.8414 | 122.612 | 122.7219 | -0.10071 | 122.6578 | 60.8917 | -0.16022 | 122.7219 | -0.10071 | 60.8917 | 122.612 | 122.6578 | -122.7814 | -122.9004
381.0156 | 123.0011 | -60.8459 | 61.9766 | -0.053406 | 0.015595 | 0.011108 | 0.0010682 | 0.06366 | -0.0049134 | 0.071777 | -60.9283 | 61.9171 | -60.878 | -61.0428 | 61.7798 | 0.11444 | 0.12817 | 0.091553 | 61.9125 | -60.9879 | -0.032044 | -0.05951 | -0.082398 | -0.19684 | -0.19684 | -0.14191 | -0.064087 | -0.050354 | 60.9741 | 60.9375 | 122.6257 | 122.7631 | -0.082398 | 122.7585 | 60.9604 | -0.14191 | 122.7631 | -0.082398 | 60.9604 | 122.6257 | 122.7585 | -122.8546 | -122.9645
381.9688 | 122.9599 | -60.8459 | 61.9446 | 0.35858 | 0.015595 | 0.013031 | 0.0070496 | 0.066437 | -0.0042724 | 0.070923 | -61.0062 | 61.8896 | -60.9055 | -61.0886 | 61.6974 | -0.004578 | 0 | -0.09613 | 61.8851 | -61.0107 | -0.05951 | -0.054932 | -0.16022 | -0.24262 | -0.24719 | -0.16479 | -0.059509 | -0.10071 | 60.8459 | 60.7498 | 122.5433 | 122.7356 | -0.16022 | 122.731 | 60.8414 | -0.16479 | 122.7356 | -0.16022 | 60.8414 | 122.5433 | 122.731 | -122.85 | -122.9553
383.0156 | 123.024 | -60.8414 | 61.9446 | 0.27466 | 0.015808 | 0.01239 | 0.0012818 | 0.064728 | -0.0032044 | 0.071777 | -60.9375 | 61.8668 | -60.8917 | -61.0428 | 61.7661 | 0.086975 | -0.07782 | 0.022888 | 61.8393 | -60.9879 | -0.050354 | -0.07782 | -0.09613 | -0.20142 | -0.17853 | -0.14648 | -0.10529 | -0.045776 | 60.7635 | 60.8643 | 122.6074 | 122.7081 | -0.09613 | 122.6807 | 60.9283 | -0.14648 | 122.7081 | -0.09613 | 60.9283 | 122.6074 | 122.6807 | -122.8363 | -122.9324
383.9688 | 122.937 | -60.8551 | 61.972 | 0.29755 | 0.013458 | 0.014313 | 0.0087586 | 0.063019 | -0.0040588 | 0.073059 | -61.0062 | 61.9263 | -60.9238 | -61.1252 | 61.6791 | -0.004578 | 0.013733 | -0.09613 | 61.8576 | -61.0336 | -0.068664 | -0.045776 | -0.15106 | -0.27008 | -0.29297 | -0.17853 | -0.11444 | -0.082398 | 60.8688 | 60.759 | 122.5342 | 122.7814 | -0.15106 | 122.7127 | 60.8505 | -0.17853 | 122.7814 | -0.15106 | 60.8505 | 122.5342 | 122.7127 | -122.8958 | -123.0057
385.0156 | 123.0286 | -60.8231 | 61.9354 | 0.3128 | 0.014313 | 0.015167 | -0.002777 | 0.063019 | -0.002777 | 0.072205 | -60.965 | 61.8668 | -60.8688 | -61.0519 | 61.7661 | 0.07782 | -0.086975 | 0.022888 | 61.8301 | -60.9879 | -0.045776 | -0.068665 | -0.14191 | -0.22888 | -0.16937 | -0.16479 | -0.10529 | -0.096131 | 60.7361 | 60.8459 | 122.5891 | 122.6898 | -0.14191 | 122.6532 | 60.9009 | -0.16479 | 122.6898 | -0.14191 | 60.9009 | 122.5891 | 122.6532 | -122.8043 | -122.9233
385.9688 | 122.9691 | -60.8276 | 61.9904 | -1.7166 | 0.013245 | 0.015595 | 0.0076904 | 0.062164 | -0.0029906 | 0.070709 | -61.0519 | 61.9812 | -60.9009 | -61.0657 | 61.7111 | 0.07782 | 0.15106 | 0.041199 | 61.8851 | -61.0107 | -0.073242 | -0.009155 | -0.2243 | -0.23804 | -0.27923 | -0.1831 | -0.10528 | -0.15106 | 60.9787 | 60.8688 | 122.5388 | 122.8088 | -0.2243 | 122.7127 | 60.9055 | -0.1831 | 122.8088 | -0.2243 | 60.9055 | 122.5388 | 122.7127 | -122.8912 | -123.0011
386.9688 | 122.9919 | -60.8139 | 62.0041 | 0.045776 | 0.016876 | 0.013672 | 0.0057678 | 0.064514 | -0.005127 | 0.069855 | -60.965 | 61.9217 | -60.9009 | -61.0474 | 61.7523 | 0.086975 | 0.10986 | 0.032043 | 61.908 | -60.9924 | -0.086975 | -0.082397 | -0.15106 | -0.23346 | -0.25177 | -0.17853 | -0.09613 | -0.064087 | 60.9238 | 60.8459 | 122.5662 | 122.7356 | -0.15106 | 122.7219 | 60.9009 | -0.17853 | 122.7356 | -0.15106 | 60.9009 | 122.5662 | 122.7219 | -122.905 | -122.9965
388.0156 | 123.0515 | -60.8139 | 61.9263 | 0.38147 | 0.014526 | 0.013458 | 0.000641 | 0.063446 | -0.0029906 | 0.070496 | -60.9421 | 61.8393 | -60.8734 | -61.0519 | 61.7569 | 0.086975 | -0.11902 | 0.018311 | 61.8118 | -60.9741 | -0.059509 | -0.086976 | -0.12817 | -0.23804 | -0.16937 | -0.16022 | -0.11444 | -0.068665 | 60.6949 | 60.8322 | 122.5708 | 122.6532 | -0.12817 | 122.6257 | 60.9009 | -0.16022 | 122.6532 | -0.12817 | 60.9009 | 122.5708 | 122.6257 | -122.7997 | -122.9004
388.9688 | 122.9645 | -60.8505 | 61.9858 | 0.24414 | 0.016663 | 0.014954 | 0.0076904 | 0.063446 | -0.006836 | 0.070496 | -60.9833 | 61.8805 | -60.91 | -61.0748 | 61.7065 | 0.018311 | 0.036621 | -0.050354 | 61.8713 | -61.0199 | -0.059509 | -0.10529 | -0.13275 | -0.2243 | -0.27924 | -0.16937 | -0.11444 | -0.073242 | 60.8871 | 60.8002 | 122.5571 | 122.731 | -0.13275 | 122.7219 | 60.8688 | -0.16937 | 122.731 | -0.13275 | 60.8688 | 122.5571 | 122.7219 | -122.8958 | -123.0057
390.0156 | 123.0972 | -60.8047 | 61.8942 | 0.47302 | 0.013886 | 0.013458 | 0 | 0.063019 | -0.0019226 | 0.071777 | -60.9238 | 61.8164 | -60.8917 | -60.9787 | 61.7981 | 0.10071 | -0.17395 | 0.054932 | 61.8256 | -60.9467 | -0.086975 | -0.07782 | -0.11902 | -0.17395 | -0.09613 | -0.14191 | -0.068664 | -0.032043 | 60.6308 | 60.8597 | 122.6028 | 122.6212 | -0.11902 | 122.6303 | 60.9055 | -0.14191 | 122.6212 | -0.11902 | 60.9055 | 122.6028 | 122.6303 | -122.786 | -122.8409
390.9688 | 123.0148 | -60.8276 | 61.94 | 0.076294 | 0.015595 | 0.013031 | 0.0064088 | 0.06366 | -0.003418 | 0.070923 | -60.9283 | 61.9034 | -60.9055 | -60.9833 | 61.7661 | 0.1236 | 0.013733 | 0.054932 | 61.8301 | -60.9787 | -0.07782 | -0.036621 | -0.10071 | -0.15564 | -0.17395 | -0.15106 | -0.10986 | -0.022888 | 60.8414 | 60.8826 | 122.5937 | 122.731 | -0.10071 | 122.6578 | 60.9512 | -0.15106 | 122.731 | -0.10071 | 60.9512 | 122.5937 | 122.6578 | -122.8455 | -122.9187
392.0156 | 123.0469 | -60.8093 | 61.853 | 0.48065 | 0.014954 | 0.012177 | 0.003418 | 0.063446 | -0.004486 | 0.071136 | -60.9009 | 61.8256 | -60.9238 | -61.0062 | 61.8027 | 0.11902 | -0.20142 | 0.036621 | 61.821 | -60.9695 | -0.11444 | -0.027465 | -0.091553 | -0.19684 | -0.050354 | -0.16022 | -0.032043 | 0.022888 | 60.6079 | 60.8459 | 122.612 | 122.6349 | -0.091553 | 122.6303 | 60.9283 | -0.16022 | 122.6349 | -0.091553 | 60.9283 | 122.612 | 122.6303 | -122.7768 | -122.8226
392.9688 | 123.0789 | -60.7773 | 61.9675 | 0.068664 | 0.011963 | 0.010681 | -0.0004272 | 0.060455 | -0.0036316 | 0.070923 | -60.91 | 61.8668 | -60.8597 | -60.9604 | 61.8301 | 0.21515 | 0.004578 | 0.16022 | 61.8576 | -60.9283 | -0.082397 | -0.10071 | -0.13275 | -0.18311 | -0.13733 | -0.15106 | -0.10986 | -0.050354 | 60.7819 | 60.9375 | 122.6074 | 122.644 | -0.13275 | 122.6349 | 60.9924 | -0.15106 | 122.644 | -0.13275 | 60.9924 | 122.6074 | 122.6349 | -122.8271 | -122.8958
393.9688 | 122.9599 | -60.8002 | 61.972 | 0 | 0.014099 | 0.011749 | 0.0042726 | 0.06131 | -0.0042724 | 0.069855 | -60.9833 | 61.8713 | -60.9009 | -61.0519 | 61.734 | 0.12817 | 0.14648 | 0.064087 | 61.8896 | -60.9741 | -0.10071 | -0.10071 | -0.1831 | -0.25177 | -0.23804 | -0.17395 | -0.082398 | -0.082397 | 60.9467 | 60.8643 | 122.5342 | 122.6715 | -0.1831 | 122.6898 | 60.9283 | -0.17395 | 122.6715 | -0.1831 | 60.9283 | 122.5342 | 122.6898 | -122.8729 | -122.9462
395.0156 | 123.0789 | -60.8139 | 61.9171 | 0.36621 | 0.01474 | 0.011963 | 0.0061952 | 0.062164 | -0.0036316 | 0.072418 | -60.91 | 61.8027 | -60.8917 | -61.0199 | 61.7844 | 0.13275 | -0.1831 | 0.036621 | 61.8027 | -60.9512 | -0.07782 | -0.11444 | -0.09613 | -0.20599 | -0.13275 | -0.13733 | -0.11444 | -0.01831 | 60.6308 | 60.8505 | 122.5983 | 122.6166 | -0.09613 | 122.6166 | 60.9467 | -0.13733 | 122.6166 | -0.09613 | 60.9467 | 122.5983 | 122.6166 | -122.8088 | -122.8683
395.9688 | 123.0057 | -60.8093 | 61.9675 | 0.030518 | 0.013245 | 0.012177 | 0.0046998 | 0.0643 | -0.0032044 | 0.070923 | -60.9375 | 61.9125 | -60.8871 | -61.0245 | 61.7661 | 0.15564 | 0.068665 | 0.068665 | 61.8851 | -60.9741 | -0.07782 | -0.054931 | -0.12817 | -0.21515 | -0.20142 | -0.16479 | -0.082397 | -0.050354 | 60.878 | 60.878 | 122.5754 | 122.7219 | -0.12817 | 122.6944 | 60.965 | -0.16479 | 122.7219 | -0.12817 | 60.965 | 122.5754 | 122.6944 | -122.8546 | -122.9416
397.0156 | 123.0515 | -60.8002 | 61.9263 | 0.3891 | 0.016663 | 0.017944 | 0.0055542 | 0.065369 | -0.0042724 | 0.071564 | -60.965 | 61.8393 | -60.9192 | -61.0565 | 61.7386 | 0.091553 | -0.15564 | 0 | 61.8164 | -60.965 | -0.11902 | -0.086976 | -0.16479 | -0.25635 | -0.18768 | -0.16479 | -0.10986 | -0.045777 | 60.6445 | 60.8002 | 122.5388 | 122.6395 | -0.16479 | 122.6166 | 60.8917 | -0.16479 | 122.6395 | -0.16479 | 60.8917 | 122.5388 | 122.6166 | -122.8455 | -122.8912
397.9688 | 122.9691 | -60.8185 | 61.9858 | 0.045776 | 0.014099 | 0.015808 | 0.0032044 | 0.060455 | -0.0040588 | 0.069855 | -60.9879 | 61.908 | -60.9055 | -61.0748 | 61.7386 | 0.13275 | 0.086975 | 0.036621 | 61.8759 | -60.9833 | -0.086976 | -0.07782 | -0.16937 | -0.25635 | -0.24719 | -0.16479 | -0.10986 | -0.082397 | 60.9055 | 60.8551 | 122.5571 | 122.7264 | -0.16937 | 122.6944 | 60.9512 | -0.16479 | 122.7264 | -0.16937 | 60.9512 | 122.5571 | 122.6944 | -122.8912 | -122.9691
399.0156 | 122.9782 | -60.8459 | 61.908 | 0.34332 | 0.015381 | 0.012817 | 0.0053406 | 0.066223 | -0.004486 | 0.072845 | -60.9879 | 61.8393 | -60.9375 | -61.0931 | 61.6745 | 0.054932 | -0.086975 | -0.07782 | 61.8576 | -60.965 | -0.091553 | -0.068665 | -0.14191 | -0.24719 | -0.23346 | -0.11902 | -0.050354 | -0.050354 | 60.759 | 60.7681 | 122.5204 | 122.6852 | -0.14191 | 122.7036 | 60.9009 | -0.11902 | 122.6852 | -0.14191 | 60.9009 | 122.5204 | 122.7036 | -122.8455 | -122.8729
399.9688 | 123.1018 | -60.7636 | 61.908 | 0.015259 | 0.014099 | 0.0091858 | 0.000641 | 0.062378 | -0.0053406 | 0.069855 | -60.6216 | 61.8988 | -60.8322 | -60.997 | 61.821 | 0.23804 | -0.12817 | 0.19226 | 61.8393 | -60.9558 | -0.068664 | -0.009155 | 0.14191 | -0.23346 | -0.086975 | -0.19226 | -0.068665 | 0.21057 | 60.6354 | 60.9558 | 122.5845 | 122.6624 | 0.14191 | 122.6028 | 61.0016 | -0.19226 | 122.6624 | 0.14191 | 61.0016 | 122.5845 | 122.6028 | -122.7402 | -122.8638
401.0156 | 123.0103 | -60.8276 | 61.9217 | 0.40436 | 0.014099 | 0.016449 | 0.0044862 | 0.061951 | -0.0021362 | 0.07135 | -60.9787 | 61.8301 | -60.9421 | -61.0565 | 61.7065 | 0.064087 | -0.14191 | -0.054932 | 61.8484 | -60.9741 | -0.11444 | -0.091553 | -0.15106 | -0.22888 | -0.21515 | -0.14648 | -0.073242 | -0.036621 | 60.6857 | 60.7727 | 122.5342 | 122.6578 | -0.15106 | 122.6761 | 60.8917 | -0.14648 | 122.6578 | -0.15106 | 60.8917 | 122.5342 | 122.6761 | -122.8638 | -122.8958
401.9844 | 123.0331 | -60.8047 | 62.0224 | -0.045776 | 0.013458 | 0.014099 | 0.001709 | 0.059814 | -0.0038452 | 0.070496 | -60.9833 | 61.8988 | -60.8917 | -61.0611 | 61.7203 | 0.15106 | 0.07782 | 0.013733 | 61.8988 | -60.9787 | -0.086975 | -0.1236 | -0.17853 | -0.25635 | -0.30212 | -0.17395 | -0.1236 | -0.091552 | 60.8826 | 60.8185 | 122.525 | 122.7036 | -0.17853 | 122.7036 | 60.9558 | -0.17395 | 122.7036 | -0.17853 | 60.9558 | 122.525 | 122.7036 | -122.9141 | -123.0011
403.0156 | 123.1293 | -60.8139 | 61.9446 | 0.41199 | 0.015167 | 0.014313 | 0.00235 | 0.064087 | -0.0053406 | 0.071777 | -60.91 | 61.7981 | -60.878 | -60.9924 | 61.7981 | 0.16937 | -0.28839 | -0.17395 | 61.7889 | -60.965 | -0.064087 | -0.14648 | -0.09613 | -0.17853 | -0.14648 | -0.15106 | -0.15564 | -0.032043 | 60.5255 | 60.64 | 122.612 | 122.612 | -0.09613 | 122.6028 | 60.9833 | -0.15106 | 122.612 | -0.09613 | 60.9833 | 122.612 | 122.6028 | -122.8226 | -122.9095
403.9688 | 122.9782 | -60.8276 | 61.9537 | -0.022889 | 0.014526 | 0.011963 | 0.0046998 | 0.060242 | -0.0040588 | 0.070923 | -60.9787 | 61.9034 | -60.8688 | -61.0519 | 61.7569 | 0.3479 | 0.032043 | -0.11444 | 61.9171 | -60.965 | -0.041198 | -0.050354 | -0.15106 | -0.2243 | -0.19684 | -0.13733 | -0.036621 | -0.10986 | 60.8597 | 60.7132 | 122.5845 | 122.731 | -0.15106 | 122.7448 | 61.1755 | -0.13733 | 122.731 | -0.15106 | 61.1755 | 122.5845 | 122.7448 | -122.8226 | -122.9187
404.9688 | 123.2483 | -60.7452 | 62.0132 | 0.030518 | 0.012604 | 0.012177 | 0.000641 | 0.060669 | -0.006195 | 0.072418 | -60.8688 | 61.8484 | -60.8414 | -60.9329 | 61.8439 | 0.31128 | -0.20599 | 0.13733 | 61.8805 | -60.9238 | -0.096131 | -0.16479 | -0.1236 | -0.18768 | -0.16937 | -0.17853 | -0.13275 | -0.027465 | 60.5392 | 60.8826 | 122.5891 | 122.5937 | -0.1236 | 122.6257 | 61.0565 | -0.17853 | 122.5937 | -0.1236 | 61.0565 | 122.5891 | 122.6257 | -122.8546 | -122.937
406.0156 | 122.9507 | -60.8139 | 61.972 | 0.25177 | 0.014099 | 0.014954 | 0.0083314 | 0.061951 | -0.0059814 | 0.071777 | -60.9558 | 61.8942 | -60.9192 | -61.0565 | 61.6974 | 0.16022 | -0.16022 | -0.10529 | 61.8622 | -60.9741 | -0.10529 | -0.07782 | -0.14191 | -0.24262 | -0.27466 | -0.16022 | -0.10986 | -0.036622 | 60.6537 | 60.7086 | 122.5113 | 122.7081 | -0.14191 | 122.6761 | 60.9741 | -0.16022 | 122.7081 | -0.14191 | 60.9741 | 122.5113 | 122.6761 | -122.8912 | -122.9462
406.9688 | 123.1155 | -60.7544 | 61.9354 | -0.030518 | 0.013458 | 0.0087586 | 0.0010682 | 0.061096 | -0.0032044 | 0.071777 | -60.8917 | 61.8256 | -60.8459 | -60.9421 | 61.8484 | 0.34332 | -0.31128 | 0.086975 | 61.8439 | -60.9238 | -0.091552 | -0.10986 | -0.13733 | -0.18768 | -0.086975 | -0.16937 | -0.091553 | -0.045777 | 60.4431 | 60.8414 | 122.6028 | 122.58 | -0.13733 | 122.5983 | 61.0977 | -0.16937 | 122.58 | -0.13733 | 61.0977 | 122.6028 | 122.5983 | -122.7814 | -122.8592
408.0156 | 123.0881 | -60.7727 | 61.9263 | 0.39673 | 0.013458 | 0.011963 | 0.0072632 | 0.060028 | -0.0053406 | 0.073273 | -60.9192 | 61.8118 | -60.8871 | -60.9787 | 61.7935 | 0.27924 | -0.4715 | -0.073242 | 61.8164 | -60.9421 | -0.11444 | -0.11444 | -0.14648 | -0.20599 | -0.13275 | -0.16937 | -0.10986 | -0.032043 | 60.3012 | 60.6995 | 122.5662 | 122.5845 | -0.14648 | 122.5891 | 61.0519 | -0.16937 | 122.5845 | -0.14648 | 61.0519 | 122.5662 | 122.5891 | -122.8134 | -122.8683
408.9688 | 123.0057 | -60.8047 | 62.0224 | 0.076294 | 0.014526 | 0.0093994 | 0.005127 | 0.061096 | -0.0040588 | 0.070923 | -60.9787 | 61.9034 | -60.8963 | -61.0107 | 61.7477 | 0.31128 | -0.24261 | -0.16479 | 61.9171 | -60.9604 | -0.091552 | -0.11902 | -0.17395 | -0.20599 | -0.27466 | -0.15564 | -0.10529 | -0.082398 | 60.5621 | 60.64 | 122.5525 | 122.7081 | -0.17395 | 122.7219 | 61.116 | -0.15564 | 122.7081 | -0.17395 | 61.116 | 122.5525 | 122.7219 | -122.9187 | -122.9828
410.0156 | 123.0011 | -60.8139 | 62.0224 | 0.36621 | 0.014313 | 0.01474 | 0.0057678 | 0.063232 | -0.004486 | 0.072205 | -60.9467 | 61.9171 | -60.9009 | -61.0382 | 61.702 | 0.23346 | -0.45319 | -0.36163 | 61.8988 | -60.9512 | -0.086975 | -0.10529 | -0.13275 | -0.2243 | -0.32043 | -0.13733 | -0.1236 | -0.045776 | 60.3607 | 60.4523 | 122.5159 | 122.731 | -0.13275 | 122.7127 | 61.0474 | -0.13733 | 122.731 | -0.13275 | 61.0474 | 122.5159 | 122.7127 | -122.9233 | -122.9736
410.9688 | 123.0423 | -60.7544 | 62.0132 | -0.053406 | 0.01474 | 0.0098268 | 0.0021362 | 0.060669 | -0.005127 | 0.07135 | -60.8643 | 61.8988 | -60.8414 | -60.965 | 61.8347 | 0.43488 | -0.48523 | -0.24261 | 61.9125 | -60.8963 | -0.086975 | -0.11444 | -0.10986 | -0.21057 | -0.17853 | -0.14191 | -0.10071 | -0.022888 | 60.2692 | 60.5118 | 122.5891 | 122.6532 | -0.10986 | 122.6669 | 61.1893 | -0.14191 | 122.6532 | -0.10986 | 61.1893 | 122.5891 | 122.6669 | -122.8546 | -122.9095
411.9688 | 123.0835 | -60.7407 | 61.9904 | 0.19836 | 0.014954 | 0.01239 | 0.0008546 | 0.060242 | -0.0042724 | 0.071564 | -60.9009 | 61.8805 | -60.8414 | -60.9512 | 61.853 | 0.46692 | -0.68665 | -0.37994 | 61.8988 | -60.8871 | -0.10071 | -0.10986 | -0.16022 | -0.21057 | -0.13733 | -0.14648 | -0.091552 | -0.059509 | 60.054 | 60.3607 | 122.5937 | 122.6212 | -0.16022 | 122.6395 | 61.2076 | -0.14648 | 122.6212 | -0.16022 | 61.2076 | 122.5937 | 122.6395 | -122.8317 | -122.8775
413.0156 | 122.9553 | -60.7773 | 62.0316 | 0.38147 | 0.01239 | 0.01944 | 0.0087586 | 0.06131 | -0.0053406 | 0.070923 | -61.2167 | 61.8622 | -60.8917 | -61.0062 | 61.7477 | 0.3479 | -0.68665 | -0.67749 | 61.908 | -60.9375 | -0.11444 | -0.16937 | -0.43945 | -0.22888 | -0.28381 | -0.16022 | -0.1236 | -0.32501 | 60.0906 | 60.0998 | 122.525 | 122.6395 | -0.43945 | 122.6852 | 61.1252 | -0.16022 | 122.6395 | -0.43945 | 61.1252 | 122.525 | 122.6852 | -122.9233 | -122.9691
413.9688 | 123.0469 | -60.7315 | 61.9858 | 0.24414 | 0.01239 | 0.014526 | 0.001709 | 0.059814 | -0.0040588 | 0.071777 | -60.8185 | 61.908 | -60.7819 | -60.965 | 61.8027 | 0.45776 | -0.89722 | -0.70038 | 61.8713 | -60.8826 | -0.050354 | -0.07782 | -0.086975 | -0.23346 | -0.18311 | -0.15106 | -0.11444 | -0.036621 | 59.8343 | 60.0311 | 122.5342 | 122.6395 | -0.086975 | 122.6028 | 61.1893 | -0.15106 | 122.6395 | -0.086975 | 61.1893 | 122.5342 | 122.6028 | -122.7676 | -122.8683
414.9688 | 123.0652 | -60.6949 | 62.027 | 0.053405 | 0.012604 | 0.010895 | 0.0019226 | 0.05896 | -0.0036316 | 0.072205 | -60.8093 | 61.8988 | -60.7819 | -60.878 | 61.8759 | 0.59052 | -0.97961 | -0.71869 | 61.9263 | -60.8459 | -0.086975 | -0.12817 | -0.11444 | -0.18311 | -0.15106 | -0.15106 | -0.10071 | -0.027466 | 59.7153 | 59.9762 | 122.5708 | 122.5937 | -0.11444 | 122.6212 | 61.2854 | -0.15106 | 122.5937 | -0.11444 | 61.2854 | 122.5708 | 122.6212 | -122.8088 | -122.8729
416.0156 | 123.0103 | -60.7269 | 62.0636 | 0.21362 | 0.014526 | 0.013672 | 0.011322 | 0.06131 | -0.006195 | 0.070496 | -60.8231 | 61.9675 | -60.7864 | -60.9192 | 61.8027 | 0.5127 | -1.0712 | -1.0162 | 61.9492 | -60.8917 | -0.059509 | -0.096131 | -0.09613 | -0.19226 | -0.26093 | -0.1648 | -0.11444 | -0.036621 | 59.6558 | 59.7107 | 122.5296 | 122.6944 | -0.09613 | 122.6761 | 61.2396 | -0.1648 | 122.6944 | -0.09613 | 61.2396 | 122.5296 | 122.6761 | -122.85 | -122.9553
416.9688 | 123.0606 | -60.6445 | 62.0544 | 0.022888 | 0.011108 | 0.017304 | 0.0027772 | 0.061096 | -0.0023498 | 0.070282 | -60.7956 | 61.9171 | -60.7681 | -60.8414 | 61.908 | 0.65918 | -1.1856 | -1.0208 | 61.9629 | -60.8368 | -0.1236 | -0.13733 | -0.15106 | -0.19684 | -0.14648 | -0.19226 | -0.091552 | -0.027466 | 59.4589 | 59.6237 | 122.5525 | 122.5616 | -0.15106 | 122.6074 | 61.3037 | -0.19226 | 122.5616 | -0.15106 | 61.3037 | 122.5525 | 122.6074 | -122.8226 | -122.8912
418.0156 | 122.9874 | -60.7132 | 62.0865 | 0.19836 | 0.012817 | 0.013031 | 0.0083314 | 0.063232 | -0.0049134 | 0.070709 | -60.8231 | 61.972 | -60.8139 | -60.9055 | 61.8027 | 0.54474 | -1.2863 | -1.3504 | 61.9949 | -60.8322 | -0.10071 | -0.11444 | -0.10986 | -0.19226 | -0.28381 | -0.11902 | -0.091553 | -0.009155 | 59.4269 | 59.3628 | 122.5159 | 122.6852 | -0.10986 | 122.7081 | 61.2579 | -0.11902 | 122.6852 | -0.10986 | 61.2579 | 122.5159 | 122.7081 | -122.9004 | -122.9187
418.9688 | 123.1155 | -60.64 | 62.059 | 0.091552 | 0.013031 | 0.010468 | 0.0004274 | 0.060028 | -0.0046996 | 0.071136 | -60.7727 | 61.94 | -60.7315 | -60.8688 | 61.9217 | 0.6958 | -1.4603 | -1.3367 | 61.9629 | -60.8322 | -0.091552 | -0.11902 | -0.13275 | -0.22888 | -0.13733 | -0.19226 | -0.09613 | -0.041199 | 59.1797 | 59.3033 | 122.5616 | 122.58 | -0.13275 | 122.6028 | 61.3358 | -0.19226 | 122.58 | -0.13275 | 61.3358 | 122.5616 | 122.6028 | -122.7905 | -122.8912
420.0156 | 123.0331 | -60.6674 | 62.0911 | 0.11444 | 0.017517 | 0.015381 | 0.0083314 | 0.063019 | -0.0021362 | 0.071136 | -60.7773 | 62.0087 | -60.7452 | -60.9329 | 61.8576 | 0.6958 | -1.4557 | -1.5976 | 62.0087 | -60.8505 | -0.07782 | -0.082397 | -0.10986 | -0.2655 | -0.23346 | -0.18311 | -0.082397 | -0.032044 | 59.2117 | 59.0698 | 122.525 | 122.6761 | -0.10986 | 122.6761 | 61.3632 | -0.18311 | 122.6761 | -0.10986 | 61.3632 | 122.525 | 122.6761 | -122.8363 | -122.9416
420.9688 | 123.0377 | -60.6583 | 62.0728 | 0.32806 | 0.014526 | 0.015595 | 0.0032044 | 0.061951 | -0.002777 | 0.071564 | -60.8047 | 61.9675 | -60.7315 | -60.8917 | 61.8484 | 0.6958 | -1.7578 | -1.8082 | 61.9949 | -60.8276 | -0.073242 | -0.10529 | -0.14648 | -0.23346 | -0.2243 | -0.16937 | -0.07782 | -0.073243 | 58.9005 | 58.8501 | 122.5067 | 122.6257 | -0.14648 | 122.6532 | 61.3541 | -0.16937 | 122.6257 | -0.14648 | 61.3541 | 122.5067 | 122.6532 | -122.8043 | -122.9004
422.0156 | 122.9965 | -60.6583 | 62.1094 | 0.16022 | 0.015167 | 0.018158 | 0.0093994 | 0.062805 | -0.0025634 | 0.07135 | -60.9192 | 62.0178 | -60.759 | -60.8276 | 61.8347 | 0.74158 | -1.7853 | -1.9592 | 62.0178 | -60.8322 | -0.10071 | -0.091553 | -0.26093 | -0.16937 | -0.27466 | -0.17395 | -0.091553 | -0.16022 | 58.873 | 58.699 | 122.493 | 122.6761 | -0.26093 | 122.6761 | 61.3998 | -0.17395 | 122.6761 | -0.26093 | 61.3998 | 122.493 | 122.6761 | -122.8683 | -122.9416
422.9844 | 122.9187 | -60.6354 | 62.146 | -0.061036 | 0.012604 | 0.012177 | 0.004059 | 0.063019 | -0.0029906 | 0.069855 | -60.8139 | 62.0865 | -60.7132 | -60.8688 | 61.8439 | 0.74158 | -1.7761 | -1.9272 | 62.0911 | -60.7956 | -0.07782 | -0.059509 | -0.17853 | -0.23346 | -0.30212 | -0.16022 | -0.054932 | -0.10071 | 58.8593 | 58.7082 | 122.4792 | 122.7219 | -0.17853 | 122.7264 | 61.377 | -0.16022 | 122.7219 | -0.17853 | 61.377 | 122.4792 | 122.7264 | -122.8592 | -122.9416
424.0156 | 122.9965 | -60.6125 | 62.1552 | 0.091552 | 0.015167 | 0.011536 | 0.008545 | 0.063446 | -0.0049134 | 0.069855 | -60.704 | 62.0911 | -60.6949 | -60.8139 | 61.8896 | 0.64087 | -2.2385 | -2.33 | 62.0773 | -60.7819 | -0.082397 | -0.064087 | -0.091553 | -0.20142 | -0.2655 | -0.16937 | -0.077819 | -0.009156 | 58.374 | 58.2825 | 122.5021 | 122.7036 | -0.091553 | 122.6898 | 61.2534 | -0.16937 | 122.7036 | -0.091553 | 61.2534 | 122.5021 | 122.6898 | -122.85 | -122.937
424.9688 | 123.0423 | -60.5988 | 62.1552 | 0.22888 | 0.015167 | 0.0057678 | -0.001068 | 0.063019 | -0.0040588 | 0.070496 | -60.5896 | 62.0911 | -60.64 | -60.8368 | 61.9171 | 0.61798 | -2.5269 | -2.4948 | 62.0773 | -60.7544 | -0.041199 | -0.064087 | 0.009155 | -0.23804 | -0.23804 | -0.15564 | -0.077819 | 0.050354 | 58.0719 | 58.1039 | 122.5159 | 122.6898 | 0.009155 | 122.6761 | 61.2167 | -0.15564 | 122.6898 | 0.009155 | 61.2167 | 122.5159 | 122.6761 | -122.7951 | -122.9095
425.9688 | 123.0698 | -60.5804 | 62.1506 | 0.41199 | 0.016022 | 0.013031 | 0.0064088 | 0.061951 | -0.0053406 | 0.072205 | -60.7269 | 62.0819 | -60.6812 | -60.7956 | 61.9034 | 0.63629 | -2.7832 | -2.6825 | 62.0544 | -60.7773 | -0.10071 | -0.068665 | -0.14648 | -0.21515 | -0.24719 | -0.19684 | -0.096131 | -0.045777 | 57.7972 | 57.8979 | 122.4838 | 122.6624 | -0.14648 | 122.6349 | 61.2167 | -0.19684 | 122.6624 | -0.14648 | 61.2167 | 122.4838 | 122.6349 | -122.8317 | -122.9279
427.0156 | 122.9874 | -60.5576 | 62.2238 | 0.015259 | 0.013245 | 0.013458 | 0.0079042 | 0.062164 | -0.0032044 | 0.069855 | -60.6674 | 62.1368 | -60.6445 | -60.7498 | 61.9308 | 0.68207 | -2.8015 | -2.8061 | 62.1414 | -60.7086 | -0.086975 | -0.086975 | -0.10986 | -0.19226 | -0.29297 | -0.15106 | -0.082398 | -0.022888 | 57.756 | 57.7515 | 122.4884 | 122.6944 | -0.10986 | 122.699 | 61.2396 | -0.15106 | 122.6944 | -0.10986 | 61.2396 | 122.4884 | 122.699 | -122.8683 | -122.9324
427.9844 | 123.1338 | -60.5164 | 62.2192 | 0.10681 | 0.010895 | 0.016235 | 0.0012818 | 0.060455 | -0.0032044 | 0.070709 | -60.6033 | 62.0865 | -60.5988 | -60.6628 | 62.0453 | 0.81024 | -3.1128 | -2.8152 | 62.1094 | -60.6537 | -0.082398 | -0.13275 | -0.086976 | -0.14648 | -0.17395 | -0.13733 | -0.10986 | -0.004578 | 57.4036 | 57.7011 | 122.5616 | 122.6028 | -0.086976 | 122.6257 | 61.3266 | -0.13733 | 122.6028 | -0.086976 | 61.3266 | 122.5616 | 122.6257 | -122.818 | -122.8729
429.0156 | 122.9919 | -60.5164 | 62.2787 | 0.015259 | 0.016876 | 0.012817 | 0.0066224 | 0.06131 | -0.004486 | 0.07135 | -60.6491 | 62.2009 | -60.585 | -60.7544 | 61.9308 | 0.72327 | -3.1036 | -3.1174 | 62.178 | -60.704 | -0.068665 | -0.07782 | -0.13275 | -0.23804 | -0.3479 | -0.18768 | -0.10071 | -0.064087 | 57.4127 | 57.399 | 122.4472 | 122.7173 | -0.13275 | 122.6944 | 61.2396 | -0.18768 | 122.7173 | -0.13275 | 61.2396 | 122.4472 | 122.6944 | -122.8638 | -122.9828
429.9688 | 123.0423 | -60.4935 | 62.2559 | 0.25177 | 0.014954 | 0.011322 | 0.0021362 | 0.063232 | -0.0021362 | 0.071991 | -60.6354 | 62.1643 | -60.5347 | -60.7315 | 61.9629 | 0.71411 | -3.4378 | -3.2547 | 62.1597 | -60.6583 | -0.041199 | -0.091552 | -0.14191 | -0.23804 | -0.29297 | -0.1648 | -0.09613 | -0.10071 | 57.0557 | 57.2388 | 122.4564 | 122.6578 | -0.14191 | 122.6532 | 61.2076 | -0.1648 | 122.6578 | -0.14191 | 61.2076 | 122.4564 | 122.6532 | -122.7905 | -122.9141
431.0156 | 123.0469 | -60.4523 | 62.2742 | 0.030518 | 0.014313 | 0.014526 | 0.0029908 | 0.06131 | -0.0032044 | 0.070709 | -60.5484 | 62.1964 | -60.5209 | -60.6216 | 62.0407 | 0.81024 | -3.5614 | -3.2913 | 62.1735 | -60.6216 | -0.068664 | -0.07782 | -0.09613 | -0.16937 | -0.23346 | -0.16937 | -0.10071 | -0.027466 | 56.8909 | 57.1609 | 122.493 | 122.6486 | -0.09613 | 122.6257 | 61.2625 | -0.16937 | 122.6486 | -0.09613 | 61.2625 | 122.493 | 122.6257 | -122.7951 | -122.8958
431.9688 | 123.024 | -60.4568 | 62.2925 | 0.4425 | 0.016449 | 0.017731 | 0.0079042 | 0.063446 | -0.0040588 | 0.072418 | -60.6171 | 62.2192 | -60.585 | -60.7132 | 61.9537 | 0.69122 | -3.8177 | -3.6163 | 62.2101 | -60.6308 | -0.12817 | -0.073242 | -0.16022 | -0.25635 | -0.33874 | -0.17395 | -0.082397 | -0.032043 | 56.6391 | 56.8405 | 122.4106 | 122.6761 | -0.16022 | 122.6669 | 61.1481 | -0.17395 | 122.6761 | -0.16022 | 61.1481 | 122.4106 | 122.6669 | -122.8775 | -122.9233
432.9844 | 123.1064 | -60.4248 | 62.3062 | 0.14496 | 0.014954 | 0.014099 | 0 | 0.061951 | -0.0053406 | 0.071136 | -60.5438 | 62.1964 | -60.5026 | -60.5988 | 62.059 | 0.78735 | -3.9688 | -3.6209 | 62.2375 | -60.5621 | -0.07782 | -0.10986 | -0.11902 | -0.17395 | -0.24719 | -0.13733 | -0.068664 | -0.041198 | 56.456 | 56.8039 | 122.4838 | 122.6212 | -0.11902 | 122.6624 | 61.2122 | -0.13733 | 122.6212 | -0.11902 | 61.2122 | 122.4838 | 122.6624 | -122.8088 | -122.8683
433.9688 | 122.9828 | -60.466 | 62.352 | 0.38147 | 0.015595 | 0.018372 | 0.0066224 | 0.062591 | -0.0029906 | 0.071991 | -60.585 | 62.3154 | -60.5026 | -60.6949 | 61.94 | 0.60883 | -4.0695 | -3.9688 | 62.2375 | -60.6354 | -0.036622 | -0.036621 | -0.11902 | -0.22888 | -0.41199 | -0.16937 | -0.11444 | -0.082397 | 56.3965 | 56.4972 | 122.406 | 122.7814 | -0.11902 | 122.7036 | 61.0748 | -0.16937 | 122.7814 | -0.11902 | 61.0748 | 122.406 | 122.7036 | -122.8546 | -122.9874
435.0156 | 122.9599 | -60.3836 | 62.3978 | -0.022889 | 0.016235 | 0.010468 | 0.0064088 | 0.061737 | -0.0042724 | 0.071564 | -60.5301 | 62.3566 | -60.4797 | -60.6308 | 62.0041 | 0.68207 | -4.0878 | -4.0009 | 62.3245 | -60.5621 | -0.09613 | -0.041199 | -0.14648 | -0.24719 | -0.39368 | -0.17853 | -0.073242 | -0.050354 | 56.2958 | 56.3828 | 122.3877 | 122.7402 | -0.14648 | 122.7081 | 61.0657 | -0.17853 | 122.7402 | -0.14648 | 61.0657 | 122.3877 | 122.7081 | -122.8775 | -122.9599
435.9688 | 122.9645 | -60.4202 | 62.3383 | 0.32043 | 0.016235 | 0.015381 | 0.010254 | 0.065582 | -0.003418 | 0.074127 | -60.5438 | 62.3657 | -60.4752 | -60.6583 | 61.9492 | 0.60425 | -4.4312 | -4.2938 | 62.3154 | -60.5667 | -0.054932 | 0.027466 | -0.1236 | -0.23804 | -0.3891 | -0.14648 | -0.022888 | -0.068664 | 55.9891 | 56.1264 | 122.3694 | 122.7859 | -0.1236 | 122.7356 | 61.0245 | -0.14648 | 122.7859 | -0.1236 | 61.0245 | 122.3694 | 122.7356 | -122.8134 | -122.905
437.0156 | 123.0011 | -60.3516 | 62.439 | -0.022889 | 0.014526 | 0.009613 | 0.0032044 | 0.063446 | -0.0053406 | 0.071136 | -60.4294 | 62.384 | -60.4156 | -60.5392 | 62.0865 | 0.72784 | -4.4952 | -4.2892 | 62.3749 | -60.5026 | -0.064087 | -0.054932 | -0.07782 | -0.18768 | -0.35248 | -0.15106 | -0.064087 | -0.013733 | 55.8563 | 56.0623 | 122.438 | 122.7356 | -0.07782 | 122.7264 | 61.0794 | -0.15106 | 122.7356 | -0.07782 | 61.0794 | 122.438 | 122.7264 | -122.8546 | -122.9416
437.9688 | 122.9828 | -60.347 | 62.4802 | 0.015259 | 0.016663 | 0.011108 | 0.0027772 | 0.063019 | -0.005127 | 0.071777 | -60.4614 | 62.4298 | -60.4019 | -60.5576 | 62.0636 | 0.74616 | -4.6143 | -4.4403 | 62.3886 | -60.4889 | -0.054932 | -0.050354 | -0.11444 | -0.21057 | -0.41656 | -0.14191 | -0.091553 | -0.059509 | 55.7327 | 55.9067 | 122.4106 | 122.7768 | -0.11444 | 122.7356 | 61.0931 | -0.14191 | 122.7768 | -0.11444 | 61.0931 | 122.4106 | 122.7356 | -122.8821 | -122.9691
439.0156 | 123.0698 | -60.2737 | 62.5031 | 0.015259 | 0.015167 | 0.016663 | 0.0025636 | 0.063019 | -0.003418 | 0.070068 | -60.3607 | 62.3978 | -60.3424 | -60.4294 | 62.1689 | 0.86975 | -4.9026 | -4.4632 | 62.384 | -60.4431 | -0.068664 | -0.10529 | -0.086975 | -0.15564 | -0.33417 | -0.16937 | -0.11902 | -0.018311 | 55.3711 | 55.8105 | 122.4426 | 122.6715 | -0.086975 | 122.6578 | 61.1435 | -0.16937 | 122.6715 | -0.086975 | 61.1435 | 122.4426 | 122.6578 | -122.8455 | -122.9462
439.9688 | 123.1018 | -60.2829 | 62.471 | 0.40436 | 0.015595 | 0.016449 | 0.0061952 | 0.064087 | -0.004486 | 0.072418 | -60.3333 | 62.4069 | -60.347 | -60.466 | 62.146 | 0.62256 | -5.191 | -4.5593 | 62.3428 | -60.4614 | -0.064087 | -0.064087 | -0.050354 | -0.1831 | -0.32501 | -0.17853 | -0.12817 | 0.013733 | 55.0919 | 55.7236 | 122.4289 | 122.6898 | -0.050354 | 122.6257 | 60.9055 | -0.17853 | 122.6898 | -0.050354 | 60.9055 | 122.4289 | 122.6257 | -122.818 | -122.9324
441.0156 | 123.0286 | -60.26 | 62.471 | 0.030518 | 0.014526 | 0.011749 | 0.005127 | 0.061951 | -0.002777 | 0.071564 | -60.3333 | 62.4069 | -60.347 | -60.434 | 62.1506 | 1.2726 | -5.1041 | -4.5914 | 62.3978 | -60.4431 | -0.086975 | -0.064087 | -0.073242 | -0.17395 | -0.32043 | -0.1831 | -0.073242 | 0.013733 | 55.1559 | 55.6686 | 122.4106 | 122.6669 | -0.073242 | 122.6578 | 61.5326 | -0.1831 | 122.6669 | -0.073242 | 61.5326 | 122.4106 | 122.6578 | -122.818 | -122.9141
441.9688 | 122.9645 | -60.2692 | 62.4939 | 0.21362 | 0.018158 | 0.013031 | 0.0093994 | 0.0643 | -0.0042724 | 0.070496 | -60.3607 | 62.4481 | -60.3378 | -60.5072 | 62.0361 | 1.2589 | -5.1636 | -4.8111 | 62.439 | -60.4477 | -0.068665 | -0.045776 | -0.091553 | -0.23804 | -0.45776 | -0.17853 | -0.054931 | -0.022888 | 55.1056 | 55.4581 | 122.3053 | 122.7173 | -0.091553 | 122.7081 | 61.528 | -0.17853 | 122.7173 | -0.091553 | 61.528 | 122.3053 | 122.7081 | -122.8317 | -122.9416
443.0156 | 123.1018 | -60.2509 | 62.4802 | 0.038147 | 0.014526 | 0.012817 | 0.0010682 | 0.063873 | -0.0023498 | 0.070068 | -60.2921 | 62.4298 | -60.2966 | -60.3195 | 62.5122 | 1.7395 | -5.6671 | -4.7104 | 62.4161 | -60.4156 | -0.045777 | -0.050354 | -0.041199 | -0.068665 | 0.032043 | -0.1648 | -0.064087 | 0.004578 | 54.5837 | 55.5405 | 122.7631 | 122.6807 | -0.041199 | 122.6669 | 61.9904 | -0.1648 | 122.6807 | -0.041199 | 61.9904 | 122.7631 | 122.6669 | -122.7768 | -122.8958
443.9688 | 123.0057 | -60.2829 | 62.5168 | 0.13733 | 0.017731 | 0.015381 | 0.0089722 | 0.064941 | -0.0042724 | 0.073486 | -60.3149 | 62.4893 | -60.3287 | -60.4477 | 61.8668 | 1.4282 | -5.2048 | -4.7882 | 62.4481 | -60.4385 | -0.045776 | -0.027466 | -0.032043 | -0.16479 | -0.65002 | -0.15564 | -0.068665 | 0.013733 | 55.0781 | 55.4947 | 122.1497 | 122.7722 | -0.032043 | 122.731 | 61.7111 | -0.15564 | 122.7722 | -0.032043 | 61.7111 | 122.1497 | 122.731 | -122.8455 | -122.9553
445.0156 | 123.1018 | -60.2325 | 62.5168 | 0.12207 | 0.01239 | 0.01239 | -0.0019226 | 0.0643 | -0.0023498 | 0.070068 | -60.3058 | 62.4573 | -60.2921 | -60.3928 | 62.1597 | 1.7624 | -5.452 | -4.6967 | 62.4207 | -60.3882 | -0.059509 | -0.05951 | -0.073242 | -0.16022 | -0.35706 | -0.15564 | -0.096131 | -0.013733 | 54.7806 | 55.5359 | 122.3923 | 122.6898 | -0.073242 | 122.6532 | 61.9949 | -0.15564 | 122.6898 | -0.073242 | 61.9949 | 122.3923 | 122.6532 | -122.8088 | -122.905
445.9688 | 122.9095 | -60.2875 | 62.5397 | 0.35858 | 0.016663 | 0.011963 | 0.0066224 | 0.0643 | -0.0021362 | 0.071136 | -60.4019 | 62.5168 | -60.3378 | -60.5209 | 61.972 | 1.7166 | -5.3879 | -4.953 | 62.4847 | -60.4202 | -0.050354 | -0.022888 | -0.11444 | -0.23346 | -0.56763 | -0.13275 | -0.054932 | -0.064087 | 54.8996 | 55.3345 | 122.2595 | 122.8043 | -0.11444 | 122.7722 | 62.0041 | -0.13275 | 122.8043 | -0.11444 | 62.0041 | 122.2595 | 122.7722 | -122.8775 | -122.9599
447.0156 | 123.1247 | -60.173 | 62.5351 | 0.1297 | 0.014313 | 0.01474 | 0.001709 | 0.061737 | -0.001068 | 0.072418 | -60.2783 | 62.4847 | -60.2509 | -60.3836 | 62.1689 | 1.9867 | -5.5206 | -4.747 | 62.471 | -60.3424 | -0.077819 | -0.050354 | -0.10529 | -0.21057 | -0.36621 | -0.16937 | -0.064087 | -0.027466 | 54.6524 | 55.426 | 122.3419 | 122.6578 | -0.10529 | 122.644 | 62.1597 | -0.16937 | 122.6578 | -0.10529 | 62.1597 | 122.3419 | 122.644 | -122.7859 | -122.8775
447.9688 | 122.937 | -60.2097 | 62.6266 | -0.0076295 | 0.015381 | 0.014526 | 0.008545 | 0.063446 | -0.0029906 | 0.070496 | -60.3104 | 62.5626 | -60.2875 | -60.4477 | 62.0407 | 1.8997 | -5.4062 | -4.8843 | 62.5031 | -60.3607 | -0.07782 | -0.064087 | -0.10071 | -0.23804 | -0.58594 | -0.15106 | -0.1236 | -0.022888 | 54.8035 | 55.3253 | 122.2504 | 122.7722 | -0.10071 | 122.7127 | 62.1094 | -0.15106 | 122.7722 | -0.10071 | 62.1094 | 122.2504 | 122.7127 | -122.9141 | -122.9874
449.0156 | 123.0606 | -60.2005 | 62.5671 | 0.20599 | 0.015381 | 0.011536 | 0.0021362 | 0.060882 | -0.0029906 | 0.074341 | -60.2921 | 62.4802 | -60.26 | -60.3973 | 62.0819 | 2.092 | -5.6351 | -4.8935 | 62.4573 | -60.3378 | -0.05951 | -0.086975 | -0.091553 | -0.19684 | -0.48523 | -0.13733 | -0.10986 | -0.032043 | 54.5654 | 55.307 | 122.2824 | 122.6807 | -0.091553 | 122.6578 | 62.2925 | -0.13733 | 122.6807 | -0.091553 | 62.2925 | 122.2824 | 122.6578 | -122.8271 | -122.905
449.9688 | 122.9965 | -60.1913 | 62.6358 | 0.30518 | 0.016876 | 0.009613 | 0.0064088 | 0.061951 | -0.0025634 | 0.071777 | -60.3058 | 62.5626 | -60.2509 | -60.3973 | 62.0361 | 2.1423 | -5.4932 | -4.953 | 62.5488 | -60.3333 | -0.059509 | -0.073242 | -0.11444 | -0.20599 | -0.59967 | -0.14191 | -0.086975 | -0.054932 | 54.6982 | 55.2383 | 122.2275 | 122.7539 | -0.11444 | 122.7402 | 62.3337 | -0.14191 | 122.7539 | -0.11444 | 62.3337 | 122.2275 | 122.7402 | -122.8867 | -122.9691
451.0156 | 123.0881 | -60.1089 | 62.5671 | 0.40436 | 0.014954 | 0.012817 | 0.0055542 | 0.062805 | -0.0059814 | 0.073914 | -60.1913 | 62.5168 | -60.2188 | -60.2966 | 62.1277 | 2.3483 | -5.896 | -4.953 | 62.4756 | -60.3058 | -0.10986 | -0.050354 | -0.082397 | -0.18768 | -0.43945 | -0.19684 | -0.091553 | 0.027466 | 54.213 | 55.1559 | 122.2366 | 122.6257 | -0.082397 | 122.5845 | 62.4573 | -0.19684 | 122.6257 | -0.082397 | 62.4573 | 122.2366 | 122.5845 | -122.7859 | -122.8729
451.9688 | 122.9782 | -60.1501 | 62.677 | -0.0076295 | 0.014954 | 0.0089722 | 0.0049134 | 0.061523 | -0.0036316 | 0.072418 | -60.0815 | 62.6633 | -60.1776 | -60.3653 | 62.0682 | 2.3621 | -5.7404 | -5.1086 | 62.5992 | -60.2921 | -0.027466 | -0.013733 | 0.068664 | -0.21515 | -0.60883 | -0.14191 | -0.07782 | 0.09613 | 54.4098 | 55.0415 | 122.2183 | 122.8134 | 0.068664 | 122.7493 | 62.5122 | -0.14191 | 122.8134 | 0.068664 | 62.5122 | 122.2183 | 122.7493 | -122.8546 | -122.9691
452.9688 | 122.9416 | -60.1181 | 62.7136 | -0.038147 | 0.013886 | 0.010681 | 0.0025636 | 0.061951 | -0.0032044 | 0.070496 | -60.2463 | 62.6038 | -60.2005 | -60.347 | 62.0773 | 2.3438 | -5.9143 | -5.2551 | 62.6404 | -60.2692 | -0.082397 | -0.10986 | -0.12817 | -0.22888 | -0.63629 | -0.15106 | -0.073242 | -0.045777 | 54.2038 | 54.863 | 122.1954 | 122.7219 | -0.12817 | 122.7585 | 62.4619 | -0.15106 | 122.7219 | -0.12817 | 62.4619 | 122.1954 | 122.7585 | -122.9141 | -122.9828
454.0156 | 123.0652 | -60.0952 | 62.6724 | 0.35858 | 0.016235 | 0.013886 | 0.0021362 | 0.063446 | -0.0040588 | 0.070709 | -60.1593 | 62.5397 | -60.1822 | -60.3058 | 62.1185 | 2.4857 | -6.221 | -5.3055 | 62.5717 | -60.2097 | -0.086975 | -0.13275 | -0.064087 | -0.21057 | -0.55389 | -0.11444 | -0.10071 | 0.022888 | 53.8742 | 54.7897 | 122.2137 | 122.6349 | -0.064087 | 122.6669 | 62.5809 | -0.11444 | 122.6349 | -0.064087 | 62.5809 | 122.2137 | 122.6669 | -122.8546 | -122.8821
454.9688 | 123.056 | -60.054 | 62.7136 | -0.068665 | 0.012177 | 0.013245 | 0.0027772 | 0.06131 | -0.0042724 | 0.072632 | -60.1135 | 62.5992 | -60.1135 | -60.2371 | 62.1506 | 2.4948 | -6.2988 | -5.3787 | 62.6404 | -60.2051 | -0.059509 | -0.11444 | -0.059509 | -0.18311 | -0.56305 | -0.15106 | -0.073242 | 0 | 53.7552 | 54.6753 | 122.2046 | 122.6532 | -0.059509 | 122.6944 | 62.5488 | -0.15106 | 122.6532 | -0.059509 | 62.5488 | 122.2046 | 122.6944 | -122.8271 | -122.9187
456.0156 | 123.0972 | -60.0174 | 62.6999 | 0.45013 | 0.016022 | 0.011322 | 0.0074768 | 0.062591 | -0.002777 | 0.074341 | -60.1089 | 62.6083 | -60.1181 | -60.2234 | 62.114 | 2.4857 | -6.6696 | -5.603 | 62.6221 | -60.1685 | -0.10071 | -0.091553 | -0.091553 | -0.20599 | -0.58594 | -0.15106 | -0.07782 | 0.009155 | 53.3478 | 54.4144 | 122.1313 | 122.6257 | -0.091553 | 122.6395 | 62.5031 | -0.15106 | 122.6257 | -0.091553 | 62.5031 | 122.1313 | 122.6395 | -122.818 | -122.8683
456.9688 | 123.0972 | -59.9899 | 62.7502 | -0.015259 | 0.013672 | 0.013458 | -0.0038452 | 0.058533 | -0.0049134 | 0.0737 | -60.0357 | 62.6495 | -60.0632 | -60.3287 | 62.1643 | 2.5635 | -6.6238 | -5.5893 | 62.6404 | -60.1456 | -0.073242 | -0.10071 | -0.045777 | -0.33875 | -0.58594 | -0.15564 | -0.10986 | 0.027465 | 53.3661 | 54.4006 | 122.1542 | 122.6395 | -0.045777 | 122.6303 | 62.5534 | -0.15564 | 122.6395 | -0.045777 | 62.5534 | 122.1542 | 122.6303 | -122.8134 | -122.8958
458.0156 | 123.0927 | -59.9304 | 62.764 | 0.41962 | 0.012604 | 0.013886 | 0.0074768 | 0.062378 | -0.0049134 | 0.0737 | -60.0311 | 62.6175 | -60.0723 | -60.0998 | 62.1643 | 2.5543 | -6.6605 | -5.7404 | 62.645 | -60.1227 | -0.14191 | -0.14648 | -0.10071 | -0.16937 | -0.59967 | -0.19226 | -0.11902 | 0.041199 | 53.27 | 54.1901 | 122.0947 | 122.5479 | -0.10071 | 122.5754 | 62.4847 | -0.19226 | 122.5479 | -0.10071 | 62.4847 | 122.0947 | 122.5754 | -122.8363 | -122.8867
458.9688 | 123.0057 | -59.9579 | 62.8418 | -0.0076295 | 0.016876 | 0.012177 | 0.0042726 | 0.061951 | -0.004486 | 0.072205 | -60.0632 | 62.7731 | -60.022 | -60.1593 | 62.1094 | 2.3254 | -6.6605 | -5.9372 | 62.796 | -60.0769 | -0.064087 | -0.068665 | -0.10528 | -0.20142 | -0.73242 | -0.11902 | -0.045776 | -0.041198 | 53.2974 | 54.0207 | 122.0673 | 122.731 | -0.10528 | 122.7539 | 62.2833 | -0.11902 | 122.731 | -0.10528 | 62.2833 | 122.0673 | 122.7539 | -122.8638 | -122.9187
460.0156 | 122.9507 | -59.8938 | 62.8693 | 0.25177 | 0.014954 | 0.016235 | 0.0072632 | 0.062805 | -0.0066222 | 0.070709 | -60.0266 | 62.7777 | -59.9808 | -60.1639 | 62.0636 | 2.1149 | -6.8619 | -6.1981 | 62.8189 | -60.0266 | -0.086975 | -0.091553 | -0.13275 | -0.27008 | -0.80566 | -0.13275 | -0.050354 | -0.045776 | 53.0319 | 53.6957 | 121.9574 | 122.6715 | -0.13275 | 122.7127 | 62.0087 | -0.13275 | 122.6715 | -0.13275 | 62.0087 | 121.9574 | 122.7127 | -122.85 | -122.8958
460.9688 | 123.1018 | -59.8389 | 62.9059 | 0.20599 | 0.011749 | 0.010254 | -0.0008544 | 0.061096 | -0.006195 | 0.071136 | -59.9533 | 62.7731 | -59.9167 | -60.0403 | 62.2009 | 2.1011 | -7.1411 | -6.2119 | 62.796 | -59.9899 | -0.07782 | -0.13275 | -0.11444 | -0.20142 | -0.70496 | -0.15106 | -0.10986 | -0.036621 | 52.6978 | 53.627 | 122.0398 | 122.612 | -0.11444 | 122.6349 | 61.94 | -0.15106 | 122.612 | -0.11444 | 61.94 | 122.0398 | 122.6349 | -122.8226 | -122.8958
462.0156 | 122.9462 | -59.8206 | 62.9608 | 0.28992 | 0.016022 | 0.016022 | 0.0079042 | 0.061096 | -0.0057678 | 0.071991 | -59.9487 | 62.8876 | -59.9396 | -60.0952 | 62.1002 | 1.8631 | -7.3563 | -6.6742 | 62.8647 | -60.0037 | -0.11902 | -0.073242 | -0.12817 | -0.27466 | -0.86059 | -0.1831 | -0.09613 | -0.009155 | 52.4643 | 53.1464 | 121.9208 | 122.7081 | -0.12817 | 122.6852 | 61.6837 | -0.1831 | 122.7081 | -0.12817 | 61.6837 | 121.9208 | 122.6852 | -122.9004 | -122.9645
462.9688 | 123.056 | -59.7565 | 62.9837 | 0.11444 | 0.015595 | 0.01004 | 0 | 0.060242 | -0.0046996 | 0.070068 | -59.8526 | 62.8647 | -59.8526 | -59.9533 | 62.2147 | 1.9501 | -7.5806 | -6.6238 | 62.8647 | -59.8846 | -0.09613 | -0.11902 | -0.09613 | -0.19684 | -0.76904 | -0.12817 | -0.11902 | 0 | 52.1759 | 53.1326 | 121.9711 | 122.6212 | -0.09613 | 122.6212 | 61.7065 | -0.12817 | 122.6212 | -0.09613 | 61.7065 | 121.9711 | 122.6212 | -122.8363 | -122.8683
464.0156 | 122.9462 | -59.729 | 63.0295 | 0.35095 | 0.014313 | 0.014954 | 0.0036316 | 0.062164 | -0.0038452 | 0.071564 | -59.8755 | 62.9059 | -59.8618 | -60.0174 | 62.1185 | 1.7029 | -7.5943 | -6.9214 | 62.9608 | -59.9304 | -0.13275 | -0.1236 | -0.14648 | -0.28839 | -0.91095 | -0.20142 | -0.068665 | -0.013733 | 52.1347 | 52.8076 | 121.8475 | 122.6349 | -0.14648 | 122.6898 | 61.4319 | -0.20142 | 122.6349 | -0.14648 | 61.4319 | 121.8475 | 122.6898 | -122.8912 | -122.9599
464.9688 | 122.9599 | -59.6695 | 63.1348 | -0.0076295 | 0.015381 | 0.012817 | 0.0044862 | 0.060455 | -0.0025634 | 0.072205 | -59.8114 | 63.0203 | -59.7702 | -59.9167 | 62.1872 | 1.6022 | -7.8461 | -7.1548 | 63.0341 | -59.8297 | -0.10071 | -0.11444 | -0.14191 | -0.24719 | -0.94757 | -0.16022 | -0.10071 | -0.041198 | 51.8234 | 52.5146 | 121.8567 | 122.6898 | -0.14191 | 122.7036 | 61.2717 | -0.16022 | 122.6898 | -0.14191 | 61.2717 | 121.8567 | 122.7036 | -122.905 | -122.9645
466.0156 | 122.9965 | -59.6237 | 63.1805 | -0.45776 | 0.014954 | 0.013458 | 0.0061952 | 0.061951 | -0.0042724 | 0.073486 | -59.6832 | 63.0844 | -59.697 | -59.8572 | 62.1597 | 1.3184 | -8.1482 | -7.4661 | 63.0981 | -59.761 | -0.073242 | -0.09613 | -0.05951 | -0.23346 | -1.0208 | -0.13733 | -0.082397 | 0.013732 | 51.4755 | 52.1576 | 121.7834 | 122.7081 | -0.05951 | 122.7219 | 60.9421 | -0.13733 | 122.7081 | -0.05951 | 60.9421 | 121.7834 | 122.7219 | -122.8775 | -122.9416
466.9688 | 123.0606 | -59.5139 | 63.2217 | 0.48828 | 0.015167 | 0.012177 | 0.0010682 | 0.062164 | -0.0032044 | 0.07135 | -59.6466 | 63.1073 | -59.5871 | -59.7656 | 62.2879 | 1.2314 | -8.3954 | -7.5211 | 63.1439 | -59.6695 | -0.073242 | -0.11444 | -0.13275 | -0.25177 | -0.93384 | -0.15564 | -0.07782 | -0.059509 | 51.1185 | 51.9928 | 121.8018 | 122.6212 | -0.13275 | 122.6578 | 60.7452 | -0.15564 | 122.6212 | -0.13275 | 60.7452 | 121.8018 | 122.6578 | -122.8088 | -122.8912
467.9688 | 123.0331 | -59.4406 | 63.2812 | 0.28229 | 0.01474 | 0.011749 | 0.0019226 | 0.060242 | -0.0025634 | 0.07135 | -59.5551 | 63.1897 | -59.523 | -59.697 | 62.2787 | 1.1719 | -8.4595 | -7.6401 | 63.1851 | -59.61 | -0.082397 | -0.091553 | -0.11444 | -0.25635 | -1.0025 | -0.16937 | -0.09613 | -0.032044 | 50.9811 | 51.8005 | 121.7194 | 122.6303 | -0.11444 | 122.6257 | 60.6125 | -0.16937 | 122.6303 | -0.11444 | 60.6125 | 121.7194 | 122.6257 | -122.8043 | -122.8912
469.0156 | 122.9874 | -59.3994 | 63.4094 | 0.17548 | 0.017304 | 0.013886 | 0.010468 | 0.060242 | -0.004486 | 0.070709 | -59.4452 | 63.3179 | -59.4772 | -59.5917 | 62.2925 | 1.1353 | -8.6517 | -8.0063 | 63.3133 | -59.5642 | -0.07782 | -0.091553 | -0.045776 | -0.19226 | -1.1169 | -0.16479 | -0.096131 | 0.032044 | 50.7477 | 51.3931 | 121.6919 | 122.7173 | -0.045776 | 122.7127 | 60.5347 | -0.16479 | 122.7173 | -0.045776 | 60.5347 | 121.6919 | 122.7127 | -122.8867 | -122.9736
469.9688 | 123.0377 | -59.3033 | 63.4415 | 0.3128 | 0.013245 | 0.015167 | 0.0036316 | 0.061951 | -0.0040588 | 0.072632 | -59.3903 | 63.3453 | -59.404 | -59.523 | 62.3337 | 1.03 | -9.0317 | -8.2306 | 63.3362 | -59.4543 | -0.10071 | -0.09613 | -0.086975 | -0.21973 | -1.1078 | -0.15106 | -0.10529 | 0.013733 | 50.2716 | 51.0727 | 121.637 | 122.6486 | -0.086975 | 122.6395 | 60.3333 | -0.15106 | 122.6486 | -0.086975 | 60.3333 | 121.637 | 122.6395 | -122.8455 | -122.8958
471.0156 | 122.9462 | -59.2117 | 63.5513 | 0.25177 | 0.015808 | 0.013031 | 0.0087586 | 0.063232 | -0.0040588 | 0.069855 | -59.3353 | 63.4598 | -59.3216 | -59.5276 | 62.2787 | 0.87891 | -9.0866 | -8.6105 | 63.4644 | -59.4086 | -0.10986 | -0.091553 | -0.1236 | -0.31586 | -1.2726 | -0.19684 | -0.086976 | -0.013733 | 50.1251 | 50.6012 | 121.4905 | 122.6715 | -0.1236 | 122.6761 | 60.0906 | -0.19684 | 122.6715 | -0.1236 | 60.0906 | 121.4905 | 122.6761 | -122.8729 | -122.9599
471.9688 | 123.0927 | -59.0836 | 63.6154 | 0.030518 | 0.013672 | 0.021362 | 0.0025636 | 0.06131 | -0.0059814 | 0.072205 | -59.1385 | 63.5147 | -59.1522 | -59.2072 | 62.2009 | 0.7782 | -9.5169 | -8.6426 | 63.5147 | -59.2346 | -0.068665 | -0.10071 | -0.054932 | -0.1236 | -1.4145 | -0.15106 | -0.10071 | 0.013733 | 49.5666 | 50.441 | 121.2845 | 122.5983 | -0.054932 | 122.5983 | 59.8618 | -0.15106 | 122.5983 | -0.054932 | 59.8618 | 121.2845 | 122.5983 | -122.7676 | -122.85
473.0156 | 122.9736 | -59.0652 | 63.739 | 0.27466 | 0.016022 | 0.014526 | 0.0070496 | 0.061951 | -0.0040588 | 0.074127 | -59.1156 | 63.6246 | -59.1385 | -59.3124 | 62.3703 | 0.36163 | -9.7824 | -9.1187 | 63.6154 | -59.2346 | -0.073242 | -0.11444 | -0.050354 | -0.24719 | -1.3687 | -0.16937 | -0.1236 | 0.022888 | 49.2828 | 49.9466 | 121.4355 | 122.6898 | -0.050354 | 122.6807 | 59.4269 | -0.16937 | 122.6898 | -0.050354 | 59.4269 | 121.4355 | 122.6807 | -122.8775 | -122.9736
473.9688 | 123.0515 | -58.9645 | 63.7665 | 0.30518 | 0.015595 | 0.012817 | 0.0032044 | 0.061096 | -0.0040588 | 0.072205 | -58.9966 | 63.6612 | -59.0515 | -59.1843 | 62.4435 | 0.28381 | -10.2768 | -9.2697 | 63.6841 | -59.1156 | -0.086975 | -0.10528 | -0.032043 | -0.21973 | -1.3229 | -0.15106 | -0.082397 | 0.054932 | 48.6877 | 49.6948 | 121.4081 | 122.6257 | -0.032043 | 122.6486 | 59.2484 | -0.15106 | 122.6257 | -0.032043 | 59.2484 | 121.4081 | 122.6486 | -122.818 | -122.8821
475.0156 | 122.9874 | -58.8593 | 63.9267 | 0.19073 | 0.016022 | 0.019013 | 0.0081178 | 0.061096 | -0.0025634 | 0.071564 | -58.96 | 63.8168 | -58.9417 | -59.0652 | 62.4573 | -0.16937 | -10.318 | -9.4894 | 63.8443 | -59.0195 | -0.082397 | -0.10986 | -0.10071 | -0.20599 | -1.4694 | -0.16022 | -0.082398 | -0.018311 | 48.5413 | 49.3698 | 121.3165 | 122.6761 | -0.10071 | 122.7036 | 58.6899 | -0.16022 | 122.6761 | -0.10071 | 58.6899 | 121.3165 | 122.7036 | -122.8683 | -122.9462
475.9688 | 123.1064 | -58.7402 | 63.9542 | 0.56458 | 0.015167 | 0.015167 | 0.0044862 | 0.062591 | -0.002777 | 0.073486 | -58.7952 | 63.8718 | -58.8547 | -58.9188 | 62.5626 | -0.35248 | -10.8307 | -9.7504 | 63.8901 | -58.9005 | -0.11444 | -0.082398 | -0.054932 | -0.17853 | -1.3916 | -0.16022 | -0.064087 | 0.059509 | 47.9095 | 48.9899 | 121.3028 | 122.612 | -0.054932 | 122.6303 | 58.3878 | -0.16022 | 122.612 | -0.054932 | 58.3878 | 121.3028 | 122.6303 | -122.8088 | -122.8546
476.9688 | 123.1201 | -58.6441 | 64.0732 | 0.41962 | 0.014313 | 0.015167 | 0.005127 | 0.063446 | -0.0042724 | 0.073059 | -58.6441 | 63.9954 | -58.7036 | -58.8364 | 62.5717 | -0.74616 | -11.0184 | -10.0983 | 63.9771 | -58.8272 | -0.059509 | -0.07782 | 0 | -0.19226 | -1.5015 | -0.18311 | -0.09613 | 0.059509 | 47.6257 | 48.5458 | 121.2158 | 122.6395 | 0 | 122.6212 | 57.8979 | -0.18311 | 122.6395 | 0 | 57.8979 | 121.2158 | 122.6212 | -122.7768 | -122.9004
478.0156 | 123.0103 | -58.5754 | 64.2334 | -0.0076295 | 0.016876 | 0.011536 | 0.0061952 | 0.063019 | -0.003418 | 0.071777 | -58.6304 | 64.1647 | -58.6304 | -58.786 | 62.5122 | -1.1719 | -10.9909 | -10.1532 | 64.1602 | -58.7082 | -0.054932 | -0.068664 | -0.054932 | -0.21057 | -1.7212 | -0.13275 | -0.073242 | 0 | 47.5845 | 48.4222 | 121.0876 | 122.7402 | -0.054932 | 122.7356 | 57.4036 | -0.13275 | 122.7402 | -0.054932 | 57.4036 | 121.0876 | 122.7356 | -122.8638 | -122.9416
478.9688 | 123.1064 | -58.4244 | 64.3295 | 0.41199 | 0.016235 | 0.010254 | 0.0057678 | 0.066437 | -0.0042724 | 0.073059 | -58.4198 | 64.2197 | -58.5251 | -58.5297 | 62.6175 | -1.3 | -11.4716 | -10.2768 | 64.2197 | -58.5342 | -0.10071 | -0.10986 | 0.004577 | -0.10529 | -1.712 | -0.10986 | -0.10986 | 0.10528 | 46.9528 | 48.1476 | 121.0419 | 122.644 | 0.004577 | 122.644 | 57.1243 | -0.10986 | 122.644 | 0.004577 | 57.1243 | 121.0419 | 122.644 | -122.8546 | -122.8638
480.0156 | 122.9965 | -58.2504 | 64.563 | 0.015259 | 0.016022 | 0.013886 | 0.0087586 | 0.063019 | -0.0032044 | 0.0737 | -58.2916 | 64.4806 | -58.3466 | -58.4656 | 62.6221 | -1.561 | -11.3388 | -10.4828 | 64.476 | -58.4061 | -0.096131 | -0.082397 | -0.041199 | -0.21515 | -1.9409 | -0.15564 | -0.086975 | 0.054932 | 46.9116 | 47.7676 | 120.8725 | 122.731 | -0.041199 | 122.7264 | 56.6895 | -0.15564 | 122.731 | -0.041199 | 56.6895 | 120.8725 | 122.7264 | -122.9095 | -122.9691
480.9688 | 123.0789 | -58.1268 | 64.595 | 0.42725 | 0.016449 | 0.012817 | 0.003418 | 0.064941 | -0.0055542 | 0.074341 | -58.1131 | 64.5447 | -58.2001 | -58.3237 | 62.677 | -1.5701 | -11.7371 | -10.5835 | 64.5035 | -58.2733 | -0.073242 | -0.050354 | 0.013733 | -0.19684 | -1.918 | -0.14648 | -0.091553 | 0.086975 | 46.3898 | 47.5433 | 120.8038 | 122.6715 | 0.013733 | 122.6303 | 56.5567 | -0.14648 | 122.6715 | 0.013733 | 56.5567 | 120.8038 | 122.6303 | -122.7951 | -122.8683
482.0156 | 122.9782 | -58.0078 | 64.8148 | 0.076294 | 0.015595 | 0.011749 | 0.0036316 | 0.060882 | -0.0029906 | 0.072205 | -58.0307 | 64.7507 | -58.0673 | -58.2275 | 62.6678 | -1.918 | -11.7325 | -10.9314 | 64.7278 | -58.1451 | -0.05951 | -0.064087 | -0.022889 | -0.21973 | -2.1469 | -0.13733 | -0.086975 | 0.036621 | 46.2753 | 47.0764 | 120.6757 | 122.7585 | -0.022889 | 122.7356 | 56.0898 | -0.13733 | 122.7585 | -0.022889 | 56.0898 | 120.6757 | 122.7356 | -122.8821 | -122.9599
482.9688 | 123.0743 | -57.811 | 64.9292 | 0.43488 | 0.015381 | 0.019013 | 0.005127 | 0.063873 | -0.003418 | 0.072418 | -57.8293 | 64.8926 | -57.9117 | -58.049 | 62.7457 | -2.1332 | -12.1628 | -11.1374 | 64.8468 | -57.9803 | -0.10071 | -0.036621 | -0.018311 | -0.23804 | -2.1835 | -0.16937 | -0.082397 | 0.082397 | 45.6482 | 46.6736 | 120.5566 | 122.7036 | -0.018311 | 122.6578 | 55.6778 | -0.16937 | 122.7036 | -0.018311 | 55.6778 | 120.5566 | 122.6578 | -122.8409 | -122.9095
484.0156 | 123.0011 | -57.6141 | 65.181 | -0.030518 | 0.015167 | 0.016022 | 0.005127 | 0.061737 | -0.002777 | 0.072632 | -57.605 | 65.1123 | -57.6691 | -57.8293 | 62.8601 | -2.3392 | -12.2635 | -11.2564 | 65.0848 | -57.7744 | -0.054931 | -0.068664 | 0.009156 | -0.21515 | -2.3209 | -0.16022 | -0.09613 | 0.064087 | 45.3506 | 46.3577 | 120.4742 | 122.7264 | 0.009156 | 122.699 | 55.275 | -0.16022 | 122.7264 | 0.009156 | 55.275 | 120.4742 | 122.699 | -122.85 | -122.9553
484.9688 | 123.024 | -57.4951 | 65.2771 | 0.35858 | 0.014099 | 0.016022 | 0.00235 | 0.061523 | -0.001068 | 0.072205 | -57.5089 | 65.1764 | -57.5912 | -57.7377 | 62.8464 | -2.5543 | -12.561 | -11.412 | 65.1718 | -57.6553 | -0.096131 | -0.10071 | -0.013733 | -0.24262 | -2.4307 | -0.16022 | -0.10529 | 0.082398 | 44.9341 | 46.0831 | 120.3415 | 122.6715 | -0.013733 | 122.6669 | 54.9408 | -0.16022 | 122.6715 | -0.013733 | 54.9408 | 120.3415 | 122.6669 | -122.8683 | -122.9324
486.0156 | 123.0286 | -57.312 | 65.5151 | 0.022888 | 0.016235 | 0.012604 | 0.0081178 | 0.060242 | -0.0032044 | 0.072845 | -57.312 | 65.4877 | -57.3898 | -57.5089 | 62.9013 | -2.7557 | -12.735 | -11.6455 | 65.4282 | -57.4585 | -0.07782 | -0.027466 | 0 | -0.19684 | -2.6138 | -0.14648 | -0.086975 | 0.07782 | 44.577 | 45.6665 | 120.2133 | 122.7997 | 0 | 122.7402 | 54.5563 | -0.14648 | 122.7997 | 0 | 54.5563 | 120.2133 | 122.7402 | -122.905 | -122.9736
486.9688 | 122.9965 | -57.1152 | 65.6433 | 0.41199 | 0.016876 | 0.011963 | 0.0072632 | 0.06366 | -0.0021362 | 0.074554 | -57.1381 | 65.5975 | -57.2159 | -57.3715 | 62.9517 | -3.0441 | -13.1561 | -11.911 | 65.5701 | -57.28 | -0.10071 | -0.045777 | -0.022889 | -0.25635 | -2.6917 | -0.16479 | -0.073243 | 0.077819 | 43.959 | 45.2042 | 120.0668 | 122.7127 | -0.022889 | 122.6852 | 54.071 | -0.16479 | 122.7127 | -0.022889 | 54.071 | 120.0668 | 122.6852 | -122.8592 | -122.9233
488.0156 | 122.9736 | -56.9046 | 65.8859 | -0.15259 | 0.017304 | 0.013458 | 0.00235 | 0.060669 | -0.0021362 | 0.071136 | -56.9138 | 65.8447 | -56.987 | -57.1609 | 63.0112 | -3.3142 | -13.4079 | -12.0209 | 65.8173 | -57.0602 | -0.082398 | -0.041198 | -0.009155 | -0.25635 | -2.8748 | -0.15564 | -0.068664 | 0.073243 | 43.4967 | 44.8837 | 119.9158 | 122.7493 | -0.009155 | 122.7219 | 53.5904 | -0.15564 | 122.7493 | -0.009155 | 53.5904 | 119.9158 | 122.7219 | -122.8729 | -122.9462
488.9688 | 122.9919 | -56.7902 | 66.0141 | 0.38147 | 0.017517 | 0.012604 | 0.0081178 | 0.063873 | -0.001709 | 0.073914 | -56.9733 | 65.95 | -56.8954 | -57.0374 | 63.0066 | -3.4561 | -13.591 | -12.1582 | 65.9775 | -56.9321 | -0.10529 | -0.064087 | -0.18311 | -0.24719 | -3.0075 | -0.14191 | -0.036621 | -0.07782 | 43.1992 | 44.632 | 119.7968 | 122.7402 | -0.18311 | 122.7676 | 53.334 | -0.14191 | 122.7402 | -0.18311 | 53.334 | 119.7968 | 122.7676 | -122.9095 | -122.9462
490.0156 | 123.0423 | -56.543 | 66.2247 | -0.015259 | 0.014313 | 0.016022 | 0.0029908 | 0.061737 | -0.0002136 | 0.073486 | -56.4789 | 66.1743 | -56.6071 | -56.7307 | 63.1485 | -3.4607 | -13.7192 | -12.1078 | 66.1652 | -56.7078 | -0.064087 | -0.050354 | 0.064087 | -0.18768 | -3.0762 | -0.16479 | -0.059509 | 0.12817 | 42.8238 | 44.4351 | 119.6915 | 122.7173 | 0.064087 | 122.7081 | 53.0823 | -0.16479 | 122.7173 | 0.064087 | 53.0823 | 119.6915 | 122.7081 | -122.8317 | -122.9324
490.9688 | 123.0148 | -56.4194 | 66.3803 | 0.23651 | 0.016235 | 0.0098268 | 0.0089722 | 0.066009 | -0.0036316 | 0.074768 | -56.3782 | 66.3574 | -56.5201 | -56.7032 | 63.0157 | -3.6621 | -13.8199 | -12.4603 | 66.3162 | -56.5842 | -0.10071 | -0.022888 | 0.041199 | -0.28381 | -3.3646 | -0.16479 | -0.064087 | 0.14191 | 42.5995 | 43.959 | 119.4351 | 122.7768 | 0.041199 | 122.7356 | 52.7573 | -0.16479 | 122.7768 | 0.041199 | 52.7573 | 119.4351 | 122.7356 | -122.9004 | -122.9645
492.0156 | 123.0194 | -56.1722 | 66.6183 | -0.038147 | 0.016022 | 0.01004 | 0.0038452 | 0.062591 | -0.0042724 | 0.074768 | -56.0898 | 66.5634 | -56.2271 | -56.3507 | 63.2172 | -3.5751 | -13.8016 | -12.3688 | 66.5222 | -56.3004 | -0.054932 | -0.054931 | 0.082397 | -0.17853 | -3.4012 | -0.12817 | -0.09613 | 0.13733 | 42.3706 | 43.8034 | 119.3893 | 122.7356 | 0.082397 | 122.6944 | 52.597 | -0.12817 | 122.7356 | 0.082397 | 52.597 | 119.3893 | 122.6944 | -122.8455 | -122.9187
492.9688 | 123.0652 | -56.0257 | 66.7007 | -0.3891 | 0.014099 | 0.016022 | 0.0044862 | 0.064087 | -0.0008544 | 0.07605 | -55.9021 | 66.6641 | -56.1127 | -56.2225 | 63.1439 | -3.6621 | -14.0167 | -12.3459 | 66.6092 | -56.2042 | -0.086975 | -0.036621 | 0.1236 | -0.19684 | -3.5568 | -0.17853 | -0.091553 | 0.21057 | 42.009 | 43.6798 | 119.1696 | 122.6898 | 0.1236 | 122.6349 | 52.3636 | -0.17853 | 122.6898 | 0.1236 | 52.3636 | 119.1696 | 122.6349 | -122.8134 | -122.905
494.0156 | 123.0881 | -55.8334 | 66.893 | -1.297 | 0.012817 | 0.013458 | 0.0038452 | 0.061523 | -0.0038452 | 0.074768 | -55.6778 | 66.8747 | -55.9067 | -56.0715 | 63.1805 | -3.8589 | -14.0579 | -12.3413 | 66.7969 | -56.0303 | -0.073242 | -0.01831 | 0.15564 | -0.23804 | -3.7125 | -0.19684 | -0.09613 | 0.22888 | 41.7755 | 43.4921 | 119.014 | 122.7081 | 0.15564 | 122.6303 | 51.9745 | -0.19684 | 122.7081 | 0.15564 | 51.9745 | 119.014 | 122.6303 | -122.7997 | -122.9233
494.9688 | 122.9782 | -55.6961 | 67.099 | 0.26703 | 0.016876 | 0.016022 | 0.0098268 | 0.062164 | -0.0021362 | 0.074768 | -55.6183 | 67.0761 | -55.7785 | -55.9341 | 63.0524 | -4.0237 | -13.8794 | -12.3642 | 67.0303 | -55.8517 | -0.082397 | -0.022888 | 0.07782 | -0.23804 | -4.0466 | -0.15564 | -0.068665 | 0.16022 | 41.8167 | 43.3319 | 118.7485 | 122.7722 | 0.07782 | 122.7264 | 51.6724 | -0.15564 | 122.7722 | 0.07782 | 51.6724 | 118.7485 | 122.7264 | -122.8775 | -122.9507
495.9688 | 123.0286 | -55.5771 | 67.2318 | 0.076294 | 0.014099 | 0.015808 | 0.0072632 | 0.063446 | -0.0023498 | 0.073059 | -55.4626 | 67.1951 | -55.6366 | -55.7556 | 63.0112 | -3.9963 | -14.1495 | -12.4329 | 67.1906 | -55.7236 | -0.05951 | -0.036621 | 0.11444 | -0.17853 | -4.2206 | -0.14648 | -0.041198 | 0.17395 | 41.4276 | 43.1442 | 118.5883 | 122.7722 | 0.11444 | 122.7676 | 51.5808 | -0.14648 | 122.7722 | 0.11444 | 51.5808 | 118.5883 | 122.7676 | -122.8683 | -122.9553
497.0156 | 123.0515 | -55.3436 | 67.4149 | 0.24414 | 0.015808 | 0.012604 | 0.0012818 | 0.063873 | -0.001709 | 0.074341 | -55.2567 | 67.3599 | -55.4123 | -55.5725 | 63.0157 | -4.335 | -14.2822 | -12.5839 | 67.3599 | -55.4901 | -0.068664 | -0.054932 | 0.086975 | -0.22888 | -4.3991 | -0.14648 | -0.054932 | 0.15564 | 41.0614 | 42.7597 | 118.3594 | 122.7036 | 0.086975 | 122.7036 | 51.0086 | -0.14648 | 122.7036 | 0.086975 | 51.0086 | 118.3594 | 122.7036 | -122.8271 | -122.905
497.9688 | 122.9645 | -55.101 | 67.6941 | 0.17548 | 0.016235 | 0.014313 | 0.0096132 | 0.065155 | -0.0019226 | 0.07605 | -54.9957 | 67.6575 | -55.1971 | -55.3482 | 63.0386 | -4.3579 | -14.0945 | -12.5793 | 67.5842 | -55.2887 | -0.096131 | -0.036621 | 0.10529 | -0.24719 | -4.6555 | -0.18768 | -0.10986 | 0.20142 | 41.0065 | 42.5217 | 118.1396 | 122.7585 | 0.10529 | 122.6852 | 50.7431 | -0.18768 | 122.7585 | 0.10529 | 50.7431 | 118.1396 | 122.6852 | -122.8912 | -122.9828
499.0156 | 123.0743 | -54.9774 | 67.7765 | 0.14496 | 0.01474 | 0.015381 | 0.0025636 | 0.062591 | -0.0008544 | 0.074127 | -54.8538 | 67.7124 | -55.0415 | -55.1697 | 63.002 | -4.2755 | -14.3921 | -12.5793 | 67.6987 | -55.1514 | -0.064087 | -0.064087 | 0.1236 | -0.19226 | -4.7745 | -0.17395 | -0.07782 | 0.18768 | 40.5853 | 42.3981 | 117.9794 | 122.6898 | 0.1236 | 122.6761 | 50.7019 | -0.17395 | 122.6898 | 0.1236 | 50.7019 | 117.9794 | 122.6761 | -122.818 | -122.9279
499.9688 | 123.0057 | -54.8126 | 67.9916 | 0.14496 | 0.016022 | 0.017517 | 0.0081178 | 0.063232 | -0.0023498 | 0.076263 | -54.6524 | 67.9871 | -54.8859 | -54.9911 | 62.8967 | -4.4952 | -14.4516 | -12.7441 | 67.9138 | -54.982 | -0.073242 | -0.004577 | 0.16022 | -0.17853 | -5.0949 | -0.16937 | -0.07782 | 0.23346 | 40.361 | 42.0685 | 117.7094 | 122.7997 | 0.16022 | 122.7264 | 50.3174 | -0.16937 | 122.7997 | 0.16022 | 50.3174 | 117.7094 | 122.7264 | -122.8775 | -122.9736
501.0156 | 123.0789 | -54.6387 | 68.1244 | 0.16022 | 0.014099 | 0.01239 | 0.0008546 | 0.062164 | -0.0006408 | 0.076263 | -54.5654 | 68.0603 | -54.7256 | -54.8767 | 62.796 | -4.6005 | -14.502 | -12.7304 | 68.042 | -54.7897 | -0.086975 | -0.064087 | 0.073242 | -0.23804 | -5.3284 | -0.15106 | -0.082398 | 0.16022 | 40.1367 | 41.9083 | 117.4347 | 122.699 | 0.073242 | 122.6807 | 50.0381 | -0.15106 | 122.699 | 0.073242 | 50.0381 | 117.4347 | 122.6807 | -122.85 | -122.9141
501.9688 | 123.0103 | -54.5105 | 68.3075 | 0.015259 | 0.015595 | 0.015167 | 0.0064088 | 0.063873 | -0.0014954 | 0.075623 | -54.3732 | 68.2755 | -54.6112 | -54.7119 | 62.6358 | -4.7791 | -14.8041 | -12.9822 | 68.2114 | -54.657 | -0.10071 | -0.032043 | 0.13733 | -0.20142 | -5.6717 | -0.14648 | -0.09613 | 0.23804 | 39.7064 | 41.5283 | 117.1463 | 122.7859 | 0.13733 | 122.7219 | 49.7314 | -0.14648 | 122.7859 | 0.13733 | 49.7314 | 117.1463 | 122.7219 | -122.9187 | -122.9645
502.9688 | 122.9691 | -54.3503 | 68.4769 | -0.015259 | 0.015595 | 0.013245 | 0.0046998 | 0.062591 | 0 | 0.076904 | -54.2404 | 68.4174 | -54.4327 | -54.6021 | 62.59 | -4.5822 | -14.9506 | -13.1287 | 68.4128 | -54.483 | -0.082397 | -0.05951 | 0.10986 | -0.25177 | -5.8868 | -0.13275 | -0.064087 | 0.19226 | 39.3997 | 41.2216 | 116.9403 | 122.7676 | 0.10986 | 122.7631 | 49.7681 | -0.13275 | 122.7676 | 0.10986 | 49.7681 | 116.9403 | 122.7631 | -122.9095 | -122.9599
504.0156 | 123.0331 | -54.2542 | 68.5364 | 0.35858 | 0.013672 | 0.010468 | 0.0032044 | 0.06366 | 0.0010682 | 0.076691 | -54.1122 | 68.4128 | -54.3091 | -54.4876 | 62.2559 | -4.6875 | -15.1749 | -12.9868 | 68.4586 | -54.3777 | -0.054932 | -0.1236 | 0.14191 | -0.23346 | -6.2805 | -0.1236 | -0.07782 | 0.19684 | 39.0793 | 41.2674 | 116.51 | 122.6669 | 0.14191 | 122.7127 | 49.5667 | -0.1236 | 122.6669 | 0.14191 | 49.5667 | 116.51 | 122.7127 | -122.8455 | -122.9141
504.9688 | 122.9782 | -54.0253 | 68.7607 | 0.19836 | 0.016235 | 0.013886 | 0.010681 | 0.062164 | -0.001068 | 0.077545 | -53.8605 | 68.6874 | -54.1077 | -54.2725 | 62.1506 | -4.8889 | -15.0055 | -13.0051 | 68.6829 | -54.1946 | -0.082397 | -0.073242 | 0.16479 | -0.24719 | -6.6101 | -0.16937 | -0.07782 | 0.24719 | 39.0198 | 41.0202 | 116.1758 | 122.7127 | 0.16479 | 122.7081 | 49.1364 | -0.16937 | 122.7127 | 0.16479 | 49.1364 | 116.1758 | 122.7081 | -122.8683 | -122.9553
506.0156 | 123.0606 | -53.8422 | 68.8934 | 0.29755 | 0.014526 | 0.012177 | 0.0032044 | 0.063019 | 0.0010682 | 0.077759 | -53.6407 | 68.8248 | -53.9291 | -54.0482 | 62.0499 | -5.0079 | -15.3442 | -13.028 | 68.7927 | -54.0115 | -0.086975 | -0.068665 | 0.20142 | -0.20599 | -6.8436 | -0.16937 | -0.10071 | 0.28839 | 38.4979 | 40.8142 | 115.892 | 122.6669 | 0.20142 | 122.6349 | 48.8342 | -0.16937 | 122.6669 | 0.20142 | 48.8342 | 115.892 | 122.6349 | -122.8226 | -122.905
506.9688 | 122.9828 | -53.595 | 69.1681 | 0.17548 | 0.017517 | 0.014099 | 0.010895 | 0.065155 | -0.001709 | 0.077332 | -53.4256 | 69.1132 | -53.7277 | -53.8513 | 61.8896 | -5.0812 | -15.152 | -13.0554 | 69.1086 | -53.7689 | -0.13275 | -0.054932 | 0.16937 | -0.25635 | -7.2784 | -0.17395 | -0.059509 | 0.30212 | 38.443 | 40.5396 | 115.4846 | 122.7081 | 0.16937 | 122.7036 | 48.5138 | -0.17395 | 122.7081 | 0.16937 | 48.5138 | 115.4846 | 122.7036 | -122.8958 | -122.937
508.0156 | 123.0469 | -52.6978 | 70.0653 | 0.34332 | 0.013458 | 0.013886 | 0.000641 | 0.062591 | 0.0006408 | 0.077972 | -52.5284 | 69.9509 | -52.7618 | -52.9221 | 62.1689 | -8.5144 | -16.0995 | -14.7217 | 69.9646 | -52.8305 | -0.064087 | -0.11444 | 0.16937 | -0.2243 | -7.8964 | -0.13275 | -0.10071 | 0.23346 | 36.5982 | 37.9761 | 114.8666 | 122.6486 | 0.16937 | 122.6624 | 44.1834 | -0.13275 | 122.6486 | 0.16937 | 44.1834 | 114.8666 | 122.6624 | -122.8271 | -122.8958
508.9688 | 122.9553 | -52.2995 | 70.5185 | -0.045776 | 0.016235 | 0.014526 | 0.0025636 | 0.060242 | -0.0006408 | 0.077545 | -52.1118 | 70.4041 | -52.359 | -52.5375 | 62.1735 | -9.2972 | -16.3742 | -15.0467 | 70.4178 | -52.446 | -0.059509 | -0.11444 | 0.18768 | -0.23804 | -8.345 | -0.14648 | -0.10071 | 0.24719 | 35.9253 | 37.2528 | 114.473 | 122.7036 | 0.18768 | 122.7173 | 43.0023 | -0.14648 | 122.7036 | 0.18768 | 43.0023 | 114.473 | 122.7173 | -122.8775 | -122.9645
509.9688 | 123.1064 | -51.9562 | 70.8252 | -0.0076295 | 0.01474 | 0.01004 | 0.0019226 | 0.063232 | -0.0006408 | 0.077332 | -51.709 | 70.7245 | -52.0203 | -52.1164 | 62.0132 | -9.6954 | -16.658 | -15.1108 | 70.7291 | -52.0752 | -0.064087 | -0.10071 | 0.24719 | -0.16022 | -8.8119 | -0.11902 | -0.09613 | 0.31128 | 35.2982 | 36.8454 | 113.9694 | 122.6807 | 0.24719 | 122.6852 | 42.2607 | -0.11902 | 122.6807 | 0.24719 | 42.2607 | 113.9694 | 122.6852 | -122.8455 | -122.9004
511.0156 | 123.0789 | -51.8051 | 70.9579 | 0.39673 | 0.015808 | 0.01239 | 0.010254 | 0.061523 | -0.0021362 | 0.07904 | -51.5488 | 70.7703 | -51.9196 | -52.0477 | 60.7178 | -6.5735 | -16.7908 | -15.1154 | 70.7291 | -52.0203 | -0.11444 | -0.18768 | 0.25635 | -0.24261 | -10.2402 | -0.21515 | -0.22888 | 0.37079 | 35.0143 | 36.6898 | 112.5229 | 122.5754 | 0.25635 | 122.5342 | 45.2316 | -0.21515 | 122.5754 | 0.25635 | 45.2316 | 112.5229 | 122.5342 | -122.8775 | -122.9782
511.9688 | 123.0103 | -51.796 | 70.9991 | 0.038147 | 0.014099 | 0.013458 | 0.0066224 | 0.060882 | 0.0014954 | 0.079681 | -51.6037 | 70.903 | -51.915 | -52.0477 | 60.9238 | -8.1528 | -16.3467 | -14.8773 | 70.9305 | -51.9836 | -0.11902 | -0.096131 | 0.19226 | -0.25177 | -10.0754 | -0.18768 | -0.068665 | 0.31128 | 35.4492 | 36.9186 | 112.7197 | 122.699 | 0.19226 | 122.7264 | 43.6432 | -0.18768 | 122.699 | 0.19226 | 43.6432 | 112.7197 | 122.7264 | -122.9141 | -122.9828
513.0156 | 123.0011 | -51.6815 | 71.109 | 0.28992 | 0.015167 | 0.011322 | 0.0061952 | 0.063446 | 0.0021362 | 0.079254 | -51.4664 | 71.0449 | -51.8005 | -51.9608 | 60.553 | -9.4711 | -16.5527 | -15.033 | 71.0266 | -51.8463 | -0.11902 | -0.064087 | 0.21515 | -0.27923 | -10.556 | -0.16479 | -0.082398 | 0.33417 | 35.1288 | 36.6486 | 112.2345 | 122.7264 | 0.21515 | 122.7081 | 42.2104 | -0.16479 | 122.7264 | 0.21515 | 42.2104 | 112.2345 | 122.7081 | -122.9095 | -122.9553
513.9844 | 122.9599 | -51.5488 | 71.2326 | 0.2594 | 0.016876 | 0.016022 | 0.0098268 | 0.062164 | 0.0025634 | 0.077972 | -51.2878 | 71.2326 | -51.6174 | -51.8372 | 60.3699 | -8.8348 | -16.3467 | -14.8636 | 71.1777 | -51.7548 | -0.068665 | 0 | 0.26093 | -0.28839 | -10.8627 | -0.20599 | -0.054932 | 0.32959 | 35.202 | 36.6852 | 111.9186 | 122.7814 | 0.26093 | 122.7264 | 42.7139 | -0.20599 | 122.7814 | 0.26093 | 42.7139 | 111.9186 | 122.7264 | -122.85 | -122.9874
515.0156 | 122.9553 | -51.6953 | 71.0953 | 0.39673 | 0.016663 | 0.011963 | 0.0066224 | 0.063232 | 0.0008546 | 0.080322 | -51.4389 | 71.022 | -51.796 | -51.9882 | 59.0652 | -8.844 | -16.2918 | -14.1678 | 71.0175 | -51.8188 | -0.10071 | -0.073242 | 0.25635 | -0.29297 | -12.03 | -0.1236 | -0.07782 | 0.35706 | 35.4034 | 37.5275 | 110.7605 | 122.7173 | 0.25635 | 122.7127 | 42.8513 | -0.1236 | 122.7173 | 0.25635 | 42.8513 | 110.7605 | 122.7127 | -122.8912 | -122.9141
515.9688 | 123.0789 | -51.503 | 71.1823 | 0.13733 | 0.015595 | 0.014954 | -0.0004272 | 0.059601 | 0.001709 | 0.082886 | -51.2238 | 71.0815 | -51.6357 | -51.7273 | 58.6716 | -6.0654 | -16.3147 | -14.1953 | 71.0999 | -51.6495 | -0.13275 | -0.10071 | 0.27924 | -0.2243 | -12.5107 | -0.14648 | -0.082397 | 0.41199 | 35.1883 | 37.3077 | 110.1746 | 122.5845 | 0.27924 | 122.6028 | 45.4376 | -0.14648 | 122.5845 | 0.27924 | 45.4376 | 110.1746 | 122.6028 | -122.818 | -122.8317
517.0156 | 123.0148 | -52.0477 | 70.7245 | 0.37384 | 0.016022 | 0.015595 | 0.0083314 | 0.060882 | 0.0046998 | 0.082672 | -51.7502 | 70.6375 | -52.1484 | -52.327 | 56.0211 | -4.9026 | -15.5594 | -13.6597 | 70.6238 | -52.2171 | -0.10071 | -0.086975 | 0.29755 | -0.27924 | -14.7034 | -0.16937 | -0.10071 | 0.39825 | 36.4883 | 38.3881 | 108.0688 | 122.6852 | 0.29755 | 122.6715 | 47.1451 | -0.16937 | 122.6852 | 0.29755 | 47.1451 | 108.0688 | 122.6715 | -122.8729 | -122.9416
517.9688 | 123.1018 | -52.1118 | 70.6467 | 0.12207 | 0.013458 | 0.010468 | 0.0019226 | 0.059601 | 0.0046998 | 0.084808 | -51.7868 | 70.491 | -52.2079 | -52.3361 | 54.3274 | -5.9601 | -15.4449 | -13.1699 | 70.5368 | -52.2308 | -0.096131 | -0.15564 | 0.32501 | -0.22431 | -16.3193 | -0.11902 | -0.10986 | 0.42114 | 36.6669 | 38.942 | 106.4392 | 122.6028 | 0.32501 | 122.6486 | 46.1517 | -0.11902 | 122.6028 | 0.32501 | 46.1517 | 106.4392 | 122.6486 | -122.8546 | -122.8775
519.0312 | 123.024 | -51.4618 | 71.3791 | 0.045776 | 0.015595 | 0.015595 | 0.0093994 | 0.061096 | 0.0049134 | 0.083527 | -51.0727 | 71.3608 | -51.4847 | -51.6907 | 53.2928 | -6.2714 | -15.9164 | -13.8657 | 71.2738 | -51.6129 | -0.022888 | -0.01831 | 0.3891 | -0.22888 | -18.0862 | -0.15106 | -0.10528 | 0.41199 | 35.5453 | 37.5961 | 104.7546 | 122.8226 | 0.3891 | 122.7356 | 45.1904 | -0.15106 | 122.8226 | 0.3891 | 45.1904 | 104.7546 | 122.7356 | -122.8638 | -122.9919
519.9688 | 123.056 | -51.4572 | 71.2784 | 0.22888 | 0.010681 | 0.014313 | 0.003418 | 0.060242 | 0.006836 | 0.085449 | -51.1093 | 71.1639 | -51.5945 | -51.7181 | 52.3224 | -7.5027 | -15.8524 | -13.2889 | 71.2051 | -51.6037 | -0.13733 | -0.11444 | 0.3479 | -0.26093 | -18.956 | -0.14648 | -0.073242 | 0.48523 | 35.6049 | 38.1683 | 103.7796 | 122.6212 | 0.3479 | 122.6624 | 43.9545 | -0.14648 | 122.6212 | 0.3479 | 43.9545 | 103.7796 | 122.6624 | -122.8729 | -122.8821
521.0156 | 122.9828 | -51.4252 | 71.3745 | 0.27466 | 0.016663 | 0.013458 | 0.011749 | 0.06131 | 0.0072632 | 0.08609 | -50.9995 | 71.3013 | -51.503 | -51.6586 | 50.2762 | -3.9322 | -15.6006 | -13.2156 | 71.2555 | -51.5625 | -0.07782 | -0.073242 | 0.42572 | -0.23346 | -21.0983 | -0.13733 | -0.11902 | 0.50354 | 35.8246 | 38.2095 | 101.7014 | 122.7264 | 0.42572 | 122.6807 | 47.493 | -0.13733 | 122.7264 | 0.42572 | 47.493 | 101.7014 | 122.6807 | -122.8775 | -122.937
521.9688 | 123.0652 | -51.4572 | 71.2921 | 0.1297 | 0.013672 | 0.01709 | 0.0021362 | 0.060455 | 0.010468 | 0.08844 | -51.1139 | 71.1365 | -51.5945 | -51.709 | 48.6603 | -7.2235 | -15.8295 | -13.2477 | 71.2006 | -51.59 | -0.13733 | -0.15564 | 0.34332 | -0.25177 | -22.6318 | -0.13275 | -0.091552 | 0.48065 | 35.6277 | 38.2095 | 100.1175 | 122.5937 | 0.34332 | 122.6578 | 44.2337 | -0.13275 | 122.5937 | 0.34332 | 44.2337 | 100.1175 | 122.6578 | -122.8867 | -122.8821
523.0156 | 122.9507 | -51.3748 | 71.3791 | 0.27466 | 0.015167 | 0.013672 | 0.0098268 | 0.06131 | 0.006836 | 0.089294 | -50.9033 | 71.3562 | -51.4755 | -51.6266 | 47.699 | -6.2759 | -15.4633 | -13.1561 | 71.3287 | -51.5167 | -0.10071 | -0.022888 | 0.4715 | -0.25177 | -23.6801 | -0.14191 | -0.050354 | 0.5722 | 35.9116 | 38.2187 | 99.0738 | 122.731 | 0.4715 | 122.7036 | 45.0989 | -0.14191 | 122.731 | 0.4715 | 45.0989 | 99.0738 | 122.7036 | -122.8546 | -122.8958
523.9844 | 122.9874 | -51.1414 | 71.6537 | 0.053405 | 0.017944 | 0.014526 | 0.011536 | 0.061737 | 0.010468 | 0.087585 | -50.5966 | 71.6171 | -51.2054 | -51.3336 | 45.813 | -5.5069 | -15.7608 | -13.829 | 71.5851 | -51.297 | -0.064087 | -0.036622 | 0.54474 | -0.19226 | -25.8408 | -0.15564 | -0.068665 | 0.60883 | 35.3806 | 37.3123 | 96.9543 | 122.7585 | 0.54474 | 122.7264 | 45.6345 | -0.15564 | 122.7585 | 0.54474 | 45.6345 | 96.9543 | 122.7264 | -122.8592 | -122.9507
525.0156 | 122.9691 | -51.6907 | 71.1044 | 0.2594 | 0.015381 | 0.013458 | 0.011108 | 0.063019 | 0.0093994 | 0.091217 | -51.1688 | 71.0129 | -51.8051 | -51.9608 | 42.7505 | -4.7791 | -15.6692 | -13.7741 | 71.0129 | -51.8234 | -0.11444 | -0.091553 | 0.52185 | -0.27008 | -28.3539 | -0.13275 | -0.091553 | 0.63629 | 36.0214 | 37.9166 | 94.4412 | 122.7036 | 0.52185 | 122.7036 | 46.9116 | -0.13275 | 122.7036 | 0.52185 | 46.9116 | 94.4412 | 122.7036 | -122.9095 | -122.9279
525.9688 | 123.1155 | -51.5488 | 71.1502 | 0.16022 | 0.013245 | 0.013031 | 0.0029908 | 0.061096 | 0.013458 | 0.091003 | -50.9766 | 71.0632 | -51.6495 | -51.7593 | 41.2125 | -5.3055 | -15.6509 | -13.9343 | 71.0815 | -51.709 | -0.10071 | -0.086976 | 0.5722 | -0.21057 | -29.9377 | -0.16022 | -0.068665 | 0.67291 | 35.8978 | 37.6144 | 92.7612 | 122.612 | 0.5722 | 122.6303 | 46.2433 | -0.16022 | 122.612 | 0.5722 | 46.2433 | 92.7612 | 122.6303 | -122.7997 | -122.8592
527.0156 | 123.0148 | -51.1597 | 71.6171 | 0.18311 | 0.015595 | 0.018585 | 0.010895 | 0.061096 | 0.011963 | 0.092712 | -50.6149 | 71.5164 | -51.2924 | -51.3977 | 40.1001 | -5.3238 | -16.4612 | -14.6072 | 71.5164 | -51.329 | -0.13275 | -0.10071 | 0.54474 | -0.23804 | -31.517 | -0.16937 | -0.10071 | 0.67749 | 34.6985 | 36.5524 | 91.2598 | 122.6761 | 0.54474 | 122.6761 | 45.8359 | -0.16937 | 122.6761 | 0.54474 | 45.8359 | 91.2598 | 122.6761 | -122.9095 | -122.9462
527.9688 | 123.0606 | -50.8621 | 71.846 | 0.13733 | 0.015167 | 0.010895 | 0.000641 | 0.060028 | 0.012604 | 0.092071 | -50.2716 | 71.7545 | -50.9583 | -51.1276 | 39.4592 | -5.2872 | -16.6672 | -14.1815 | 71.7453 | -51.0315 | -0.09613 | -0.091552 | 0.59052 | -0.2655 | -32.3868 | -0.16937 | -0.10071 | 0.68665 | 34.1949 | 36.6806 | 90.3214 | 122.6166 | 0.59052 | 122.6074 | 45.575 | -0.16937 | 122.6166 | 0.59052 | 45.575 | 90.3214 | 122.6074 | -122.8043 | -122.8775
529.0312 | 123.0652 | -50.4776 | 72.2763 | 0.16785 | 0.015808 | 0.01944 | 0.005127 | 0.059174 | 0.014526 | 0.093994 | -49.8596 | 72.1664 | -50.5829 | -50.7156 | 38.7131 | 0.45776 | -17.9855 | -15.564 | 72.1573 | -50.647 | -0.10529 | -0.10986 | 0.61798 | -0.23804 | -33.5632 | -0.16937 | -0.11902 | 0.72327 | 32.4921 | 34.9136 | 89.1907 | 122.644 | 0.61798 | 122.6349 | 50.9354 | -0.16937 | 122.644 | 0.61798 | 50.9354 | 89.1907 | 122.6349 | -122.8592 | -122.9233
529.9688 | 123.0835 | -49.823 | 72.8668 | 0.45776 | 0.016235 | 0.016022 | 0.010681 | 0.063446 | 0.014313 | 0.095276 | -49.1455 | 72.7936 | -49.9466 | -50.0656 | 36.5891 | 0.10986 | -18.2602 | -16.3834 | 72.7753 | -50.0015 | -0.1236 | -0.073242 | 0.67749 | -0.24262 | -36.2778 | -0.17853 | -0.091552 | 0.80109 | 31.5628 | 33.4396 | 86.412 | 122.6166 | 0.67749 | 122.5983 | 49.9329 | -0.17853 | 122.6166 | 0.67749 | 49.9329 | 86.412 | 122.5983 | -122.8134 | -122.8683
531.0156 | 123.0377 | -50.1251 | 72.6517 | 0.015259 | 0.017944 | 0.016449 | 0.011963 | 0.063232 | 0.015381 | 0.097626 | -49.3286 | 72.6288 | -50.1984 | -50.3403 | 33.6639 | 3.923 | -16.8182 | -14.3234 | 72.6059 | -50.2625 | -0.073242 | -0.022888 | 0.79651 | -0.21515 | -38.9877 | -0.13733 | -0.045776 | 0.86975 | 33.3069 | 35.8017 | 83.7891 | 122.7539 | 0.79651 | 122.731 | 54.0482 | -0.13733 | 122.7539 | 0.79651 | 54.0482 | 83.7891 | 122.731 | -122.85 | -122.9141
531.9688 | 123.0698 | -49.4522 | 73.2605 | 0.3891 | 0.017731 | 0.014526 | 0.0055542 | 0.063873 | 0.018372 | 0.097198 | -48.5413 | 73.201 | -49.5392 | -49.6307 | 33.1284 | -0.65918 | -17.5186 | -14.8453 | 73.2422 | -49.6262 | -0.086976 | -0.059509 | 0.91095 | -0.17853 | -40.1321 | -0.17395 | -0.018311 | 0.99793 | 31.9336 | 34.6069 | 82.5806 | 122.6532 | 0.91095 | 122.6944 | 48.793 | -0.17395 | 122.6532 | 0.91095 | 48.793 | 82.5806 | 122.6944 | -122.7997 | -122.8867
533.0156 | 122.9874 | -48.2529 | 74.5926 | -0.038147 | 0.018372 | 0.016449 | 0.010895 | 0.060455 | 0.018585 | 0.1004 | -47.4014 | 74.556 | -48.3215 | -48.6282 | 32.2357 | 1.2268 | -19.0384 | -18.512 | 74.437 | -48.4497 | -0.068664 | -0.036621 | 0.85144 | -0.37537 | -42.3569 | -0.19684 | -0.15564 | 0.9201 | 29.2145 | 29.7409 | 80.4886 | 122.8088 | 0.85144 | 122.6898 | 49.4797 | -0.19684 | 122.8088 | 0.85144 | 49.4797 | 80.4886 | 122.6898 | -122.9141 | -123.0423
533.9688 | 123.0698 | -48.4726 | 74.2905 | 0.24414 | 0.016449 | 0.016022 | 0.0046998 | 0.061096 | 0.019226 | 0.10275 | -47.6074 | 74.231 | -48.5321 | -48.7289 | 31.2057 | 2.4948 | -18.5806 | -18.0725 | 74.1623 | -48.6053 | -0.059509 | -0.059509 | 0.86517 | -0.25635 | -43.0847 | -0.13275 | -0.12817 | 0.92468 | 29.892 | 30.4001 | 79.6783 | 122.7036 | 0.86517 | 122.6349 | 50.9674 | -0.13275 | 122.7036 | 0.86517 | 50.9674 | 79.6783 | 122.6349 | -122.8226 | -122.8958
535.0156 | 122.9233 | -48.1018 | 74.7025 | -0.0076295 | 0.019867 | 0.019226 | 0.01004 | 0.059174 | 0.019867 | 0.10382 | -47.2824 | 74.6155 | -48.2162 | -48.3765 | 29.7226 | 3.1677 | -18.1412 | -17.8391 | 74.675 | -48.2117 | -0.11444 | -0.086975 | 0.8194 | -0.27466 | -44.9799 | -0.10986 | -0.027466 | 0.93384 | 29.9606 | 30.2628 | 77.8244 | 122.7173 | 0.8194 | 122.7768 | 51.2695 | -0.10986 | 122.7173 | 0.8194 | 51.2695 | 77.8244 | 122.7768 | -122.9187 | -122.9141
535.9688 | 122.9965 | -47.8317 | 74.9451 | 0.37384 | 0.01944 | 0.019653 | 0.011749 | 0.063019 | 0.020935 | 0.10062 | -46.8933 | 74.8901 | -47.9095 | -48.1155 | 29.1504 | 2.2659 | -18.7775 | -17.8482 | 74.8718 | -48.0057 | -0.07782 | -0.054931 | 0.93842 | -0.28381 | -45.7947 | -0.17395 | -0.073242 | 1.0162 | 29.0543 | 29.9835 | 76.9821 | 122.7219 | 0.93842 | 122.7036 | 50.0977 | -0.17395 | 122.7219 | 0.93842 | 50.0977 | 76.9821 | 122.7036 | -122.8546 | -122.9507
537.0156 | 122.8958 | -48.0927 | 74.6841 | -0.015259 | 0.018799 | 0.018585 | 0.0098268 | 0.060455 | 0.01944 | 0.10083 | -47.1405 | 74.6201 | -48.2025 | -48.4222 | 28.4637 | 0.37537 | -17.0471 | -15.097 | 74.5972 | -48.2803 | -0.10986 | -0.064087 | 0.95215 | -0.32959 | -46.2204 | -0.18768 | -0.086975 | 1.062 | 31.0455 | 32.9956 | 76.5564 | 122.7127 | 0.95215 | 122.6898 | 48.468 | -0.18768 | 122.7127 | 0.95215 | 48.468 | 76.5564 | 122.6898 | -122.8867 | -122.9645
537.9688 | 122.9828 | -47.168 | 75.6271 | 0.22888 | 0.017731 | 0.019013 | 0.013458 | 0.06366 | 0.022644 | 0.10468 | -46.0602 | 75.5676 | -47.2733 | -47.4792 | 27.9327 | 1.4969 | -18.4662 | -16.2735 | 75.5585 | -47.3602 | -0.10529 | -0.059509 | 1.1078 | -0.31128 | -47.6944 | -0.19226 | -0.068664 | 1.2131 | 28.7018 | 30.8945 | 75.1007 | 122.7356 | 1.1078 | 122.7264 | 48.6649 | -0.19226 | 122.7356 | 1.1078 | 48.6649 | 75.1007 | 122.7264 | -122.9004 | -122.9874
539.0156 | 123.0789 | -46.7926 | 75.9613 | -0.015259 | 0.017944 | 0.013886 | 0.0055542 | 0.06366 | 0.023285 | 0.10297 | -45.5154 | 75.8881 | -46.8979 | -46.9803 | 27.3468 | -1.7715 | -17.8345 | -16.4337 | 75.8743 | -46.9437 | -0.10529 | -0.073242 | 1.2772 | -0.18768 | -48.6145 | -0.15106 | -0.086975 | 1.3824 | 28.9581 | 30.3589 | 74.1394 | 122.6807 | 1.2772 | 122.6669 | 45.0211 | -0.15106 | 122.6807 | 1.2772 | 45.0211 | 74.1394 | 122.6669 | -122.8592 | -122.905
539.9688 | 122.9279 | -46.2158 | 76.6022 | 0.28229 | 0.020081 | 0.019867 | 0.012604 | 0.062591 | 0.02179 | 0.10468 | -42.2241 | 77.2705 | -45.6619 | -46.3577 | 26.8387 | -3.511 | -17.2714 | -16.4062 | 76.6205 | -46.3165 | 0.55389 | 0.66834 | 3.9917 | -0.14191 | -49.7635 | -0.10071 | 0.01831 | 3.4378 | 28.9444 | 29.8096 | 73.0545 | 123.4863 | 3.9917 | 122.8363 | 42.7048 | -0.10071 | 123.4863 | 3.9917 | 42.7048 | 73.0545 | 122.8363 | -122.2641 | -122.9187
541.0156 | 123.0331 | -45.0302 | 77.7191 | 0.053405 | 0.017304 | 0.018585 | 0.0057678 | 0.062378 | 0.024567 | 0.10532 | -43.3182 | 77.6596 | -45.1355 | -45.2499 | 27.5208 | -2.5864 | -17.1616 | -16.0767 | 77.655 | -45.1996 | -0.10529 | -0.059509 | 1.712 | -0.21973 | -50.1984 | -0.16937 | -0.064087 | 1.8173 | 27.8687 | 28.9536 | 72.551 | 122.6898 | 1.712 | 122.6852 | 42.4438 | -0.16937 | 122.6898 | 1.712 | 42.4438 | 72.551 | 122.6852 | -122.8546 | -122.9187
541.9688 | 123.1018 | -44.371 | 78.3508 | 0.42725 | 0.017517 | 0.019653 | 0.011963 | 0.065582 | 0.023285 | 0.10446 | -42.485 | 78.3463 | -44.4122 | -44.6732 | 27.2461 | -6.871 | -17.0197 | -17.0609 | 78.2272 | -44.5633 | -0.041198 | -0.004578 | 1.886 | -0.30212 | -51.1047 | -0.19226 | -0.1236 | 1.9272 | 27.3514 | 27.3102 | 71.6171 | 122.7173 | 1.886 | 122.5983 | 37.5 | -0.19226 | 122.7173 | 1.886 | 37.5 | 71.6171 | 122.5983 | -122.7631 | -122.9141
543.0156 | 122.9462 | -44.0964 | 78.717 | 0.053405 | 0.019013 | 0.020294 | 0.011322 | 0.062164 | 0.025421 | 0.10703 | -42.4576 | 78.6667 | -44.1513 | -44.371 | 26.7975 | -5.246 | -17.9352 | -17.7017 | 78.6163 | -44.2703 | -0.054931 | -0.050354 | 1.6388 | -0.27466 | -51.9196 | -0.17395 | -0.10071 | 1.6937 | 26.1612 | 26.3947 | 70.8939 | 122.7631 | 1.6388 | 122.7127 | 38.8504 | -0.17395 | 122.7631 | 1.6388 | 38.8504 | 70.8939 | 122.7127 | -122.8683 | -122.9874
543.9688 | 123.0011 | -42.6453 | 80.1361 | 0.11444 | 0.019653 | 0.021149 | 0.014526 | 0.064728 | 0.023285 | 0.10574 | -42.5949 | 80.1773 | -42.7002 | -42.9794 | 25.2731 | -8.8211 | -19.3497 | -19.5602 | 80.0674 | -42.8055 | -0.054931 | 0.041199 | 0.050354 | -0.33417 | -54.863 | -0.16022 | -0.068664 | 0.10529 | 23.2956 | 23.085 | 67.9184 | 122.8226 | 0.050354 | 122.7127 | 33.8242 | -0.16022 | 122.8226 | 0.050354 | 33.8242 | 67.9184 | 122.7127 | -122.8363 | -122.9416
544.9688 | 123.0469 | -41.7023 | 81.0242 | 0.43488 | 0.01944 | 0.018158 | 0.01004 | 0.064728 | 0.029053 | 0.1098 | -39.8209 | 81.0242 | -41.803 | -41.9861 | 24.1058 | -7.5577 | -19.3222 | -19.4778 | 80.9647 | -41.8442 | -0.10071 | 0 | 1.8814 | -0.28381 | -56.9183 | -0.14191 | -0.059509 | 1.9821 | 22.3801 | 22.2244 | 65.8081 | 122.7264 | 1.8814 | 122.6669 | 34.1446 | -0.14191 | 122.7264 | 1.8814 | 34.1446 | 65.8081 | 122.6669 | -122.8271 | -122.8683
546.0156 | 123.0194 | -41.3361 | 81.3858 | 0.10681 | 0.019653 | 0.016022 | 0.0074768 | 0.063446 | 0.027344 | 0.11044 | -39.3539 | 81.3446 | -41.4276 | -41.5695 | 23.0484 | -9.3109 | -18.9972 | -19.2352 | 81.3263 | -41.5009 | -0.091552 | -0.041199 | 1.9821 | -0.23346 | -58.3374 | -0.16479 | -0.059509 | 2.0737 | 22.3389 | 22.1008 | 64.3845 | 122.6807 | 1.9821 | 122.6624 | 32.0251 | -0.16479 | 122.6807 | 1.9821 | 32.0251 | 64.3845 | 122.6624 | -122.8134 | -122.8867
546.9688 | 122.9874 | -41.6153 | 81.1798 | 0.35095 | 0.021149 | 0.01474 | 0.013031 | 0.066223 | 0.02713 | 0.11365 | -39.6698 | 81.1752 | -41.716 | -41.9312 | 22.3206 | -9.2011 | -18.4799 | -18.5852 | 81.1066 | -41.7801 | -0.10071 | -0.004578 | 1.9455 | -0.31586 | -58.8593 | -0.16479 | -0.073243 | 2.0462 | 23.1354 | 23.0301 | 63.9359 | 122.7905 | 1.9455 | 122.7219 | 32.4142 | -0.16479 | 122.7905 | 1.9455 | 32.4142 | 63.9359 | 122.7219 | -122.8958 | -122.9599
548.0156 | 123.0789 | -41.2445 | 81.4774 | 0.12207 | 0.019867 | 0.019013 | 0.0070496 | 0.06366 | 0.029907 | 0.11151 | -39.1983 | 81.4636 | -41.2766 | -41.4322 | 21.3364 | -6.3354 | -18.0862 | -17.9718 | 81.4087 | -41.3956 | -0.032043 | -0.013733 | 2.0462 | -0.18768 | -60.141 | -0.15106 | -0.068665 | 2.0782 | 23.1583 | 23.2727 | 62.5809 | 122.7081 | 2.0462 | 122.6532 | 34.9091 | -0.15106 | 122.7081 | 2.0462 | 34.9091 | 62.5809 | 122.6532 | -122.7539 | -122.8729
548.9688 | 122.9645 | -40.947 | 81.8665 | 0.37384 | 0.022217 | 0.026276 | 0.012604 | 0.065155 | 0.026703 | 0.11066 | -38.5208 | 81.8298 | -41.0614 | -41.2033 | 20.5215 | -5.3787 | -17.1158 | -17.2348 | 81.8207 | -41.1118 | -0.11444 | -0.036621 | 2.4261 | -0.25635 | -61.3449 | -0.1648 | -0.045776 | 2.5406 | 23.8312 | 23.7122 | 61.4685 | 122.7768 | 2.4261 | 122.7676 | 35.5682 | -0.1648 | 122.7768 | 2.4261 | 35.5682 | 61.4685 | 122.7676 | -122.9279 | -122.9782
550.0156 | 123.0469 | -40.7913 | 81.9809 | 0.87738 | 0.019226 | 0.026276 | 0.008545 | 0.062164 | 0.032257 | 0.11578 | -38.443 | 81.8665 | -40.9058 | -41.0614 | 17.0929 | -1.9226 | -17.3126 | -17.2531 | 81.8756 | -40.9332 | -0.11444 | -0.11444 | 2.3483 | -0.27008 | -64.888 | -0.14191 | -0.10529 | 2.4628 | 23.4787 | 23.5382 | 57.8842 | 122.6578 | 2.3483 | 122.6669 | 38.8687 | -0.14191 | 122.6578 | 2.3483 | 38.8687 | 57.8842 | 122.6669 | -122.8867 | -122.9141
550.9688 | 122.9965 | -39.9307 | 82.8644 | 0.14496 | 0.019653 | 0.022003 | 0.015808 | 0.064728 | 0.032257 | 0.11707 | -37.5687 | 82.8369 | -40.0177 | -40.1459 | 12.9593 | -0.086975 | -17.7612 | -17.7109 | 82.8049 | -40.0543 | -0.086975 | -0.027466 | 2.3621 | -0.21515 | -69.9051 | -0.1236 | -0.059509 | 2.449 | 22.1695 | 22.2198 | 52.89 | 122.7676 | 2.3621 | 122.7356 | 39.8438 | -0.1236 | 122.7676 | 2.3621 | 39.8438 | 52.89 | 122.7356 | -122.8821 | -122.9187
552.0156 | 123.0927 | -40.654 | 82.0999 | 0.16785 | 0.017731 | 0.022217 | 0.0076904 | 0.06366 | 0.032898 | 0.11792 | -38.2233 | 82.0084 | -40.7822 | -40.8325 | 12.8769 | 2.8519 | -15.3763 | -15.097 | 82.0404 | -40.7867 | -0.12817 | -0.091553 | 2.4307 | -0.17853 | -69.223 | -0.13275 | -0.05951 | 2.5589 | 25.2777 | 25.5569 | 53.5309 | 122.6624 | 2.4307 | 122.6944 | 43.5059 | -0.13275 | 122.6624 | 2.4307 | 43.5059 | 53.5309 | 122.6944 | -122.8821 | -122.8867
552.9688 | 122.9874 | -39.4958 | 83.2626 | 0.11444 | 0.022858 | 0.025421 | 0.016876 | 0.063232 | 0.037811 | 0.12048 | -36.9965 | 83.313 | -39.5691 | -39.7202 | 10.7574 | 2.6688 | -16.5573 | -16.5985 | 83.2352 | -39.6698 | -0.073242 | 0.050354 | 2.4994 | -0.2243 | -72.5052 | -0.17395 | -0.027466 | 2.5726 | 22.9385 | 22.8973 | 50.2533 | 122.8088 | 2.4994 | 122.731 | 42.1646 | -0.17395 | 122.8088 | 2.4994 | 42.1646 | 50.2533 | 122.731 | -122.8317 | -122.9324
554.0156 | 123.0286 | -38.3652 | 84.4391 | 0.25177 | 0.019226 | 0.018585 | 0.0091858 | 0.063019 | 0.036957 | 0.12219 | -35.8429 | 84.3292 | -38.4476 | -38.6444 | 9.1873 | 3.4012 | -17.8116 | -17.7658 | 84.3109 | -38.5025 | -0.082398 | -0.10986 | 2.5223 | -0.27924 | -75.2518 | -0.13733 | -0.12817 | 2.6047 | 20.5536 | 20.5994 | 47.5525 | 122.6944 | 2.5223 | 122.6761 | 41.7664 | -0.13733 | 122.6944 | 2.5223 | 41.7664 | 47.5525 | 122.6761 | -122.8867 | -122.9416
554.9688 | 122.9828 | -37.8204 | 85.0021 | 0.39673 | 0.023071 | 0.024994 | 0.016663 | 0.063232 | 0.039093 | 0.12518 | -35.2112 | 84.9884 | -37.9166 | -38.1317 | 7.8003 | 1.4694 | -17.1936 | -17.0883 | 84.938 | -37.9715 | -0.09613 | -0.013733 | 2.6093 | -0.31128 | -77.2018 | -0.15106 | -0.064087 | 2.7054 | 20.6268 | 20.7321 | 45.6207 | 122.8088 | 2.6093 | 122.7585 | 39.2899 | -0.15106 | 122.8088 | 2.6093 | 39.2899 | 45.6207 | 122.7585 | -122.9187 | -122.9736
556.0156 | 123.0515 | -36.9873 | 85.7391 | 0.16785 | 0.022217 | 0.020935 | 0.0083314 | 0.063232 | 0.041016 | 0.12732 | -34.2545 | 85.6979 | -37.088 | -37.2528 | 5.9235 | 1.3321 | -17.5232 | -17.363 | 85.643 | -37.1704 | -0.10071 | -0.041199 | 2.7328 | -0.2655 | -79.8157 | -0.1831 | -0.096131 | 2.8336 | 19.4641 | 19.6243 | 42.9108 | 122.6852 | 2.7328 | 122.6303 | 38.3194 | -0.1831 | 122.6852 | 2.7328 | 38.3194 | 42.9108 | 122.6303 | -122.8271 | -122.9095
556.9688 | 122.9507 | -35.6827 | 87.1445 | 0.16785 | 0.023071 | 0.023926 | 0.016876 | 0.062591 | 0.041016 | 0.12625 | -32.6019 | 87.085 | -35.7605 | -35.939 | 5.2917 | -1.8448 | -17.6971 | -17.6834 | 87.0346 | -35.8383 | -0.07782 | -0.059509 | 3.0807 | -0.25635 | -81.8527 | -0.15564 | -0.10986 | 3.1586 | 17.9855 | 17.9993 | 40.9744 | 122.7676 | 3.0807 | 122.7173 | 33.8379 | -0.15564 | 122.7676 | 3.0807 | 33.8379 | 40.9744 | 122.7173 | -122.905 | -122.9828
558.0156 | 122.9965 | -35.2753 | 87.6663 | 0.24414 | 0.020081 | 0.021362 | 0.0093994 | 0.059814 | 0.038025 | 0.12796 | -32.3181 | 87.3093 | -35.4858 | -35.733 | 6.7703 | -0.41199 | -18.2144 | -18.3243 | 87.291 | -35.5179 | -0.21057 | -0.35706 | 2.9572 | -0.45776 | -80.896 | -0.24261 | -0.37537 | 3.1677 | 17.0609 | 16.951 | 42.0456 | 122.5845 | 2.9572 | 122.5662 | 34.8633 | -0.24261 | 122.5845 | 2.9572 | 34.8633 | 42.0456 | 122.5662 | -123.1522 | -123.1842
558.9688 | 122.9416 | -34.8999 | 87.9272 | 0.46539 | 0.023285 | 0.019013 | 0.015595 | 0.061951 | 0.040375 | 0.12582 | -31.7322 | 87.9593 | -34.9503 | -35.1608 | 6.8527 | -1.2405 | -17.0151 | -16.9785 | 87.8769 | -35.0143 | -0.050354 | 0.032044 | 3.1677 | -0.26093 | -81.0745 | -0.11444 | -0.050354 | 3.2181 | 17.8848 | 17.9214 | 41.7526 | 122.8592 | 3.1677 | 122.7768 | 33.6594 | -0.11444 | 122.8592 | 3.1677 | 33.6594 | 41.7526 | 122.7768 | -122.8775 | -122.9416
560.0156 | 123.056 | -33.7509 | 88.9618 | 0.21362 | 0.021149 | 0.018585 | 0.011536 | 0.061737 | 0.041229 | 0.12839 | -30.5603 | 89.0625 | -33.7555 | -34.0256 | 8.0521 | -2.2064 | -18.0771 | -17.9123 | 88.916 | -33.8837 | -0.004577 | 0.10071 | 3.1906 | -0.27466 | -80.9097 | -0.13275 | -0.045776 | 3.1952 | 15.6738 | 15.8386 | 41.803 | 122.8134 | 3.1906 | 122.6669 | 31.5445 | -0.13275 | 122.8134 | 3.1906 | 31.5445 | 41.803 | 122.6669 | -122.7173 | -122.8455
560.9688 | 122.9965 | -34.1995 | 88.5956 | -0.22125 | 0.020935 | 0.021149 | 0.017731 | 0.06366 | 0.038239 | 0.12646 | -30.986 | 88.5635 | -34.3185 | -34.4788 | 9.0088 | -2.2659 | -17.0563 | -17.0105 | 88.4857 | -34.3689 | -0.11902 | -0.032043 | 3.2135 | -0.27924 | -79.5868 | -0.16937 | -0.10986 | 3.3325 | 17.1432 | 17.189 | 43.2083 | 122.7631 | 3.2135 | 122.6852 | 31.9336 | -0.16937 | 122.7631 | 3.2135 | 31.9336 | 43.2083 | 122.6852 | -122.9141 | -122.9645
562.0156 | 123.0423 | -33.5449 | 89.1678 | 0.083923 | 0.021362 | 0.019226 | 0.010254 | 0.063019 | 0.03952 | 0.12732 | -30.4092 | 89.122 | -33.6685 | -33.9066 | 10.2264 | -2.5223 | -18.1686 | -18.2465 | 89.0991 | -33.7189 | -0.1236 | -0.045777 | 3.1357 | -0.36163 | -78.9413 | -0.17395 | -0.068665 | 3.2593 | 15.3763 | 15.2985 | 43.7714 | 122.6669 | 3.1357 | 122.644 | 31.0226 | -0.17395 | 122.6669 | 3.1357 | 31.0226 | 43.7714 | 122.644 | -122.8363 | -122.8867
562.9688 | 122.9553 | -32.8125 | 90.0101 | 0.38147 | 0.024353 | 0.026489 | 0.017944 | 0.06366 | 0.03952 | 0.13074 | -29.5944 | 89.9826 | -32.9041 | -33.1284 | 9.4711 | -2.4673 | -18.9148 | -18.8278 | 89.9139 | -32.9773 | -0.091553 | -0.027466 | 3.2181 | -0.31586 | -80.5389 | -0.16479 | -0.096131 | 3.3096 | 13.8977 | 13.9847 | 42.2836 | 122.7951 | 3.2181 | 122.7264 | 30.3452 | -0.16479 | 122.7951 | 3.2181 | 30.3452 | 42.2836 | 122.7264 | -122.9141 | -122.9874
564.0156 | 123.0698 | -32.8995 | 89.8361 | 0.083923 | 0.021149 | 0.020294 | 0.014526 | 0.064087 | 0.040588 | 0.13202 | -29.5853 | 89.8178 | -32.9636 | -33.1375 | 9.4986 | -3.154 | -17.8619 | -17.6376 | 89.7995 | -33.0185 | -0.064087 | -0.018311 | 3.3142 | -0.23804 | -80.3375 | -0.11902 | -0.036621 | 3.3783 | 15.0375 | 15.2618 | 42.3981 | 122.7173 | 3.3142 | 122.699 | 29.7455 | -0.11902 | 122.7173 | 3.3142 | 29.7455 | 42.3981 | 122.699 | -122.7997 | -122.8546
564.9688 | 122.9874 | -30.6335 | 92.1661 | 0.053405 | 0.023285 | 0.022858 | 0.02243 | 0.06366 | 0.04187 | 0.13309 | -27.475 | 92.1158 | -31.1325 | -30.8395 | 8.6517 | -4.9988 | -21.666 | -21.8765 | 92.1066 | -30.7114 | -0.49896 | -0.050354 | 3.1586 | -0.20599 | -83.5144 | -0.07782 | -0.05951 | 3.6575 | 8.9676 | 8.757 | 39.2853 | 122.7493 | 3.1586 | 122.7402 | 25.6348 | -0.07782 | 122.7493 | 3.1586 | 25.6348 | 39.2853 | 122.7402 | -123.2986 | -122.8775
566.0156 | 123.0286 | -46.5134 | 76.2039 | 0.20599 | 0.019653 | 0.022858 | 0.25699 | 0.06131 | 0.030548 | 0.367 | -42.7551 | 76.1765 | -46.5454 | -46.6919 | 13.2889 | -0.93384 | 76.1719 | 26.8936 | 76.1261 | -46.6415 | -0.032043 | -0.027465 | 3.7582 | -0.17853 | -62.915 | -0.12817 | -0.077819 | 3.7903 | 122.6852 | 73.407 | 59.8022 | 122.6898 | 3.7582 | 122.6395 | 45.5795 | -0.12817 | 122.6898 | 3.7582 | 45.5795 | 59.8022 | 122.6395 | -122.7493 | -122.8455
566.9688 | 122.5388 | -39.18 | 83.1345 | 0.099182 | 0.020935 | 0.02243 | 1.7365 | 0.0643 | 0.036102 | 1.6733 | -34.8175 | 83.1162 | -39.3036 | -38.9969 | 6.5689 | -9.6268 | 65.6937 | -13.7421 | 82.9926 | -39.1296 | -0.1236 | -0.01831 | 4.3625 | 0.18311 | -76.5656 | 0.050354 | -0.14191 | 4.4861 | 104.8737 | 25.4379 | 45.7489 | 122.2961 | 4.3625 | 122.1725 | 29.5532 | 0.050354 | 122.2961 | 4.3625 | 29.5532 | 45.7489 | 122.1725 | -122.438 | -122.2641
568.0156 | 122.4426 | -44.0781 | 78.035 | 0.099182 | 0.016663 | 0.021149 | 0.079681 | 0.001068 | 0.032684 | 0.11792 | -40.4709 | 77.9617 | -44.1788 | 64.9887 | 18.869 | 13.6642 | 77.6825 | -42.3752 | 77.9663 | -44.2062 | -0.10071 | -0.073242 | 3.6072 | 109.0668 | -59.166 | -0.12817 | -0.068664 | 3.7079 | 121.7606 | 1.7029 | 62.9471 | 122.0398 | 3.6072 | 122.0444 | 57.7423 | -0.12817 | 122.0398 | 3.6072 | 57.7423 | 62.9471 | 122.0444 | -122.2137 | -122.2412
568.9688 | 122.2778 | -37.3856 | 84.7275 | 0.099182 | 0.020294 | 0.021576 | 0.10959 | 0.013672 | 0.064728 | 0.1897 | -33.8379 | 84.7366 | -37.4405 | 57.7011 | -37.5183 | -37.619 | 83.4869 | -37.5595 | 84.6725 | -37.5 | -0.054932 | 0.009155 | 3.5477 | 95.0867 | -122.2458 | -0.11444 | -0.054932 | 3.6026 | 120.8725 | -0.17395 | -0.13275 | 122.1222 | 3.5477 | 122.0581 | -0.23346 | -0.11444 | 122.1222 | 3.5477 | -0.23346 | -0.13275 | 122.0581 | -122.168 | -122.2275
570.0156 | 122.3557 | -39.2578 | 82.8644 | 0.068664 | 0.018585 | 0.016235 | 0.1019 | 0.008972 | 0.063446 | 0.17624 | -35.7925 | 82.869 | -39.2624 | 58.9096 | -39.1937 | -39.2532 | 82.8278 | 78.8498 | 82.8186 | -39.3814 | -0.004578 | 0.004578 | 3.4653 | 98.1674 | -122.0581 | -0.1236 | -0.045776 | 3.4698 | 122.0856 | 118.1076 | 0.064086 | 122.1268 | 3.4653 | 122.0764 | 0.004577 | -0.1236 | 122.1268 | 3.4653 | 0.004577 | 0.064086 | 122.0764 | -122.1268 | -122.2458
570.9688 | 122.4747 | -35.527 | 86.7645 | 0.045776 | 0.019867 | 0.023071 | 0.15167 | 0.010681 | 0.065796 | 0.22943 | -32.4738 | 86.7096 | -35.614 | 61.9583 | -35.6964 | -35.7925 | 86.7416 | 9.4116 | 86.6821 | -35.6552 | -0.086975 | -0.054931 | 3.0533 | 97.4854 | -122.4609 | -0.12817 | -0.082397 | 3.1403 | 122.2687 | 44.9387 | -0.16937 | 122.2366 | 3.0533 | 122.2092 | -0.2655 | -0.12817 | 122.2366 | 3.0533 | -0.2655 | -0.16937 | 122.2092 | -122.3785 | -122.4197
572.0156 | 122.5571 | -39.6011 | 82.6675 | 0.14496 | 0.018158 | 0.022217 | 0.055328 | 0.010467 | 0.065582 | 0.13992 | -36.058 | 82.663 | -39.6103 | 57.2983 | -39.6881 | -39.7934 | 82.6126 | 82.2647 | 82.6309 | -39.7018 | -0.009156 | -0.004578 | 3.5431 | 96.8994 | -122.3557 | -0.10071 | -0.036622 | 3.5522 | 122.2137 | 121.8658 | -0.086975 | 122.2641 | 3.5431 | 122.2321 | -0.19226 | -0.10071 | 122.2641 | 3.5431 | -0.19226 | -0.086975 | 122.2321 | -122.2778 | -122.3694
572.9688 | 122.4609 | -39.2487 | 83.0978 | 0.007629 | 0.017944 | 0.024139 | 0.067719 | 0.011108 | 0.065155 | 0.14676 | -35.9619 | 83.0521 | -39.3265 | 56.7719 | -39.4363 | -39.5508 | 83.1802 | 82.7271 | 83.0795 | -39.3677 | -0.07782 | -0.045776 | 3.2867 | 96.0205 | -122.5342 | -0.11902 | -0.01831 | 3.3646 | 122.4289 | 121.9757 | -0.18768 | 122.3007 | 3.2867 | 122.3282 | -0.30212 | -0.11902 | 122.3007 | 3.2867 | -0.30212 | -0.18768 | 122.3282 | -122.4243 | -122.4655
573.9688 | 122.4655 | -39.1205 | 83.2581 | 0.29755 | 0.019226 | 0.025421 | 0.093353 | 0.013885 | 0.065155 | 0.17773 | -35.5545 | 83.2397 | -39.18 | 53.4302 | -39.3494 | -39.4272 | 83.3359 | 82.7682 | 83.2352 | -39.2212 | -0.05951 | -0.018311 | 3.566 | 92.5507 | -122.6074 | -0.10071 | -0.022889 | 3.6255 | 122.4564 | 121.8887 | -0.22888 | 122.3602 | 3.566 | 122.3557 | -0.3067 | -0.10071 | 122.3602 | 3.566 | -0.3067 | -0.22888 | 122.3557 | -122.4381 | -122.4792
575.0156 | 121.9162 | -38.2416 | 83.4183 | 0.34332 | 0.01709 | 0.023499 | 0.062378 | 0.013245 | 0.063019 | 0.14697 | -34.6848 | 83.3954 | -38.324 | 55.4214 | -38.4064 | -38.4842 | 83.4274 | 83.1024 | 83.345 | -38.3789 | -0.082398 | -0.022888 | 3.5568 | 93.663 | -121.8246 | -0.13733 | -0.073242 | 3.6392 | 121.669 | 121.344 | -0.16479 | 121.637 | 3.5568 | 121.5866 | -0.24262 | -0.13733 | 121.637 | 3.5568 | -0.24262 | -0.16479 | 121.5866 | -121.7422 | -121.7972
575.9688 | 122.4335 | -39.4547 | 82.8094 | 0.37384 | 0.020294 | 0.024994 | 0.077972 | 0.010467 | 0.061951 | 0.1521 | -36.1267 | 82.8415 | -39.5279 | 56.3553 | -39.7064 | -39.7797 | 82.8918 | 81.0974 | 82.7774 | -39.6149 | -0.073242 | 0.032044 | 3.3279 | 95.8099 | -122.5159 | -0.16022 | -0.032043 | 3.4012 | 122.3465 | 120.5521 | -0.25177 | 122.2961 | 3.3279 | 122.2321 | -0.32501 | -0.16022 | 122.2961 | 3.3279 | -0.32501 | -0.25177 | 122.2321 | -122.3373 | -122.4243
577.0156 | 122.6166 | -40.0269 | 82.2418 | 0.068664 | 0.016022 | 0.021149 | 0.068573 | 0.009613 | 0.067291 | 0.1506 | -36.5707 | 82.2144 | -40.0681 | 56.4331 | -40.1276 | -40.2328 | 82.196 | 79.2252 | 82.2052 | -40.1505 | -0.041199 | -0.027466 | 3.4561 | 96.46 | -122.3694 | -0.1236 | -0.036621 | 3.4973 | 122.2229 | 119.252 | -0.10071 | 122.2412 | 3.4561 | 122.2321 | -0.20599 | -0.1236 | 122.2412 | 3.4561 | -0.20599 | -0.10071 | 122.2321 | -122.3099 | -122.3923
577.9688 | 122.4609 | -36.3052 | 86.0596 | 0.27466 | 0.022858 | 0.024567 | 1.9348 | -0.0010682 | 0.064301 | 2.0213 | -33.2932 | 85.9497 | -36.4334 | 81.7474 | -36.3144 | -36.4334 | 85.849 | 85.3455 | 85.8215 | -36.3052 | -0.12817 | -0.10986 | 3.0121 | 118.0527 | -122.374 | 0 | -0.23804 | 3.1403 | 122.1542 | 121.6507 | -0.009155 | 122.2549 | 3.0121 | 122.1268 | -0.12817 | 0 | 122.2549 | 3.0121 | -0.12817 | -0.009155 | 122.1268 | -122.493 | -122.3648
579.0156 | 122.3282 | -52.0386 | 69.9738 | 0.35095 | 0.017517 | 0.027344 | 0.099762 | -0.0044862 | 0.064514 | 0.16919 | -48.2117 | 69.9509 | -52.121 | 68.9896 | -52.1805 | -52.2995 | 69.9829 | 70.0287 | 69.9326 | -52.153 | -0.082398 | -0.022888 | 3.8269 | 121.0281 | -122.1542 | -0.11444 | -0.041199 | 3.9093 | 122.0215 | 122.0673 | -0.14191 | 121.9894 | 3.8269 | 121.9711 | -0.26093 | -0.11444 | 121.9894 | 3.8269 | -0.26093 | -0.14191 | 121.9711 | -122.0947 | -122.1268
579.9688 | 121.8475 | -31.8558 | 89.9368 | -0.030518 | 0.021362 | 0.023071 | 0.076477 | -0.00235 | 0.062378 | 0.14548 | -24.5361 | 97.0047 | -25.9918 | 85.0159 | -32.6706 | -32.4921 | 8.2901 | 6.3171 | 89.8453 | -32.0526 | 5.864 | 7.0679 | 7.3196 | 116.8716 | -122.6074 | -0.19684 | -0.091553 | 1.4557 | 40.1459 | 38.1729 | -0.81482 | 128.8605 | 7.3196 | 121.701 | -0.63629 | -0.19684 | 128.8605 | 7.3196 | -0.63629 | -0.81482 | 121.701 | -115.9287 | -121.9894
581.0156 | 121.9803 | -43.4006 | 78.2181 | 0.17548 | 0.019013 | 0.027985 | 0.1192 | 0.016022 | 0.065369 | 0.20166 | -40.1688 | 78.1357 | -43.5013 | 41.9907 | -43.4143 | -43.4875 | 66.774 | 67.0486 | 78.1494 | -43.515 | -0.10071 | -0.082398 | 3.2318 | 85.3912 | -121.6324 | -0.11444 | -0.068665 | 3.3325 | 110.1746 | 110.4492 | -0.013733 | 121.5363 | 3.2318 | 121.55 | -0.086975 | -0.11444 | 121.5363 | 3.2318 | -0.086975 | -0.013733 | 121.55 | -121.7194 | -121.7331
581.9688 | 121.8842 | -25.9232 | 95.7687 | 0.076294 | 0.019013 | 0.022644 | 0.023712 | 0.059601 | 0.06665 | 0.15103 | -23.1674 | 95.8237 | -25.9369 | -18.5394 | -25.3738 | -25.4379 | -18.5211 | -22.8973 | 95.7825 | -25.9827 | -0.013733 | 0.054931 | 2.7557 | 7.3837 | -121.1426 | -0.059509 | 0.013733 | 2.7695 | 7.402 | 3.0258 | 0.54932 | 121.7468 | 2.7557 | 121.7056 | 0.48523 | -0.059509 | 121.7468 | 2.7557 | 0.48523 | 0.54932 | 121.7056 | -121.7056 | -121.7514
582.9688 | 121.5454 | -32.2769 | 89.09 | 0.24414 | 0.02179 | 0.026703 | 0.032257 | 0.048065 | 0.049774 | 0.1286 | -29.3518 | 89.2136 | -32.2586 | -2.8748 | -6.9305 | -7.0358 | -2.8656 | -2.8656 | 89.1449 | -32.341 | 0.018311 | 0.1236 | 2.9251 | 29.4022 | -96.0205 | -0.064086 | 0.054931 | 2.9068 | 29.4113 | 29.4113 | 25.3464 | 121.4905 | 2.9251 | 121.4218 | 25.2411 | -0.064086 | 121.4905 | 2.9251 | 25.2411 | 25.3464 | 121.4218 | -121.3486 | -121.431
584.0156 | 121.9208 | -24.9023 | 96.8124 | 0.25177 | 0.020508 | 0.028198 | 0.024353 | 0.060669 | 0.065155 | 0.16193 | -22.2931 | 96.7896 | -24.9527 | -22.2702 | -23.1171 | -23.14 | -22.3022 | -22.1695 | 96.7575 | -25.0076 | -0.050354 | -0.022888 | 2.6093 | 2.6321 | -119.9295 | -0.10529 | -0.054932 | 2.6596 | 2.6001 | 2.7328 | 1.7853 | 121.6919 | 2.6093 | 121.6599 | 1.7624 | -0.10529 | 121.6919 | 2.6093 | 1.7624 | 1.7853 | 121.6599 | -121.7651 | -121.8201
584.9688 | 121.8979 | -24.6826 | 97.1191 | 0.26703 | 0.020508 | 0.022644 | 0.034607 | 0.064514 | 0.062805 | 0.16492 | -22.1787 | 97.0688 | -24.7879 | -22.9889 | -23.7534 | -23.7854 | -22.9385 | -22.9248 | 97.0139 | -24.8154 | -0.10529 | -0.050354 | 2.504 | 1.6937 | -120.8725 | -0.13275 | -0.10529 | 2.6093 | 1.7441 | 1.7578 | 0.92926 | 121.7514 | 2.504 | 121.6965 | 0.89722 | -0.13275 | 121.7514 | 2.504 | 0.89722 | 0.92926 | 121.6965 | -121.907 | -121.9345
586.0156 | 121.9986 | -25.4013 | 96.2677 | 0.38147 | 0.019653 | 0.023071 | 0.019226 | 0.063446 | 0.064301 | 0.15424 | -22.7783 | 96.2219 | -25.4608 | -21.3272 | -22.5128 | -22.5494 | -21.5103 | -21.6293 | 96.167 | -25.4929 | -0.059509 | -0.045776 | 2.623 | 4.0741 | -118.7805 | -0.091553 | -0.10071 | 2.6825 | 3.891 | 3.772 | 2.8885 | 121.6232 | 2.623 | 121.5683 | 2.8519 | -0.091553 | 121.6232 | 2.623 | 2.8519 | 2.8885 | 121.5683 | -121.7285 | -121.7606
586.9688 | 121.9162 | -24.8611 | 96.9498 | -0.64087 | 0.021149 | 0.019867 | 0.029694 | 0.060882 | 0.063019 | 0.15808 | -22.4167 | 96.9772 | -24.8611 | -22.5586 | -24.3484 | -24.4125 | -22.1603 | -22.1375 | 96.8353 | -24.9939 | 0 | 0.027466 | 2.4445 | 2.3026 | -121.2982 | -0.13275 | -0.11444 | 2.4445 | 2.7008 | 2.7237 | 0.5127 | 121.8384 | 2.4445 | 121.6965 | 0.44861 | -0.13275 | 121.8384 | 2.4445 | 0.44861 | 0.5127 | 121.6965 | -121.8109 | -121.9437
588.0156 | 122.0581 | -24.2477 | 97.5311 | 0.5722 | 0.020935 | 0.026062 | 0.052338 | 0.062378 | 0.065369 | 0.18906 | -21.6385 | 97.4442 | -24.353 | -22.0551 | -24.0463 | -24.0738 | -22.261 | -21.9727 | 97.3938 | -24.3484 | -0.10529 | -0.086975 | 2.6093 | 2.1927 | -121.5775 | -0.10071 | -0.13733 | 2.7145 | 1.9867 | 2.2751 | 0.20142 | 121.6919 | 2.6093 | 121.6415 | 0.17395 | -0.10071 | 121.6919 | 2.6093 | 0.17395 | 0.20142 | 121.6415 | -121.8842 | -121.8796
588.9688 | 121.7926 | -59.3399 | 62.2147 | 0.030518 | 0.020935 | 0.033112 | 0.047852 | -0.0044862 | -0.0040588 | 0.030762 | -55.2933 | 62.1231 | -59.4955 | 61.1984 | 61.0565 | 61.1618 | 61.1389 | 60.9924 | 62.1506 | -59.523 | -0.15564 | -0.091553 | 4.0466 | 120.5383 | -1.1581 | -0.1831 | -0.064087 | 4.2023 | 120.4788 | 120.3323 | 120.3964 | 121.463 | 4.0466 | 121.4905 | 120.5017 | -0.1831 | 121.463 | 4.0466 | 120.5017 | 120.3964 | 121.4905 | -121.7102 | -121.7377
589.9688 | 121.8658 | -60.3378 | 61.3312 | 0.23651 | 0.021362 | 0.033325 | 0.048279 | -0.0025636 | -0.0040588 | 0.027985 | -56.0806 | 61.3312 | -60.4431 | 60.8139 | 60.7086 | 60.8185 | 60.8414 | 60.6766 | 61.3083 | -60.5072 | -0.10529 | 0 | 4.2572 | 121.1517 | -0.62256 | -0.16937 | -0.022888 | 4.3625 | 121.1792 | 121.0144 | 121.0464 | 121.669 | 4.2572 | 121.6461 | 121.1563 | -0.16937 | 121.669 | 4.2572 | 121.1563 | 121.0464 | 121.6461 | -121.7743 | -121.8384
591.0156 | 121.7651 | -22.3618 | 99.2203 | 0.2594 | 0.019867 | 0.026489 | 0.018585 | 0.061737 | 0.064301 | 0.17133 | -19.9127 | 99.0372 | -22.4945 | -20.2103 | -20.1645 | -20.3247 | -20.4849 | -20.4758 | 99.1058 | -22.4716 | -0.13275 | -0.18311 | 2.449 | 2.1515 | -119.3848 | -0.10986 | -0.11444 | 2.5818 | 1.8768 | 1.886 | 2.1973 | 121.3989 | 2.449 | 121.4676 | 2.037 | -0.10986 | 121.3989 | 2.449 | 2.037 | 2.1973 | 121.4676 | -121.7148 | -121.6919
591.9688 | 121.7377 | -22.0184 | 99.6918 | 0.007629 | 0.023712 | 0.027771 | 0.067291 | 0.060882 | 0.06366 | 0.17773 | -19.6289 | 99.4766 | -22.229 | -21.1029 | -21.0297 | -21.0754 | -20.9885 | -21.0892 | 99.5407 | -22.1695 | -0.21057 | -0.21515 | 2.3895 | 0.91553 | -120.7214 | -0.15106 | -0.15106 | 2.6001 | 1.03 | 0.92926 | 0.98877 | 121.4951 | 2.3895 | 121.5591 | 0.94299 | -0.15106 | 121.4951 | 2.3895 | 0.94299 | 0.98877 | 121.5591 | -121.9208 | -121.8613
593.0156 | 121.4447 | -53.5995 | 67.5385 | 0.38147 | 0.019867 | 0.033966 | 0.0093994 | 0.0055542 | 0.0070496 | 0.011536 | -49.4843 | 67.4194 | -53.7918 | 51.503 | 51.3107 | 51.5579 | 51.4069 | 51.4389 | 67.4377 | -53.833 | -0.19226 | -0.11902 | 4.1153 | 105.1025 | -16.2277 | -0.23346 | -0.10071 | 4.3076 | 105.0064 | 105.0385 | 104.9103 | 121.019 | 4.1153 | 121.0373 | 105.1575 | -0.23346 | 121.019 | 4.1153 | 105.1575 | 104.9103 | 121.0373 | -121.3303 | -121.3715
593.9688 | 121.6415 | -29.6036 | 91.9006 | 0.18311 | 0.026276 | 0.028839 | 0.021149 | 0.050629 | 0.046997 | 0.11792 | -26.7975 | 91.8777 | -29.6402 | -2.3163 | -2.3438 | -2.3438 | -2.3117 | -2.3071 | 91.8045 | -29.718 | -0.036621 | -0.022888 | 2.8061 | 27.2873 | -94.2444 | -0.11444 | -0.096131 | 2.8427 | 27.2919 | 27.2964 | 27.2598 | 121.4813 | 2.8061 | 121.4081 | 27.2598 | -0.11444 | 121.4813 | 2.8061 | 27.2598 | 27.2598 | 121.4081 | -121.5408 | -121.6187
595.0156 | 121.7606 | -21.08 | 100.502 | 0.27466 | 0.02243 | 0.025421 | 0.012604 | 0.060882 | 0.061951 | 0.1489 | -18.4616 | 100.415 | -21.1395 | -18.2831 | -18.2098 | -18.2373 | -18.338 | -18.1686 | 100.4196 | -21.1716 | -0.059509 | -0.086975 | 2.6184 | 2.7969 | -118.7119 | -0.091553 | -0.082397 | 2.6779 | 2.742 | 2.9114 | 2.8702 | 121.4951 | 2.6184 | 121.4996 | 2.8427 | -0.091553 | 121.4951 | 2.6184 | 2.8427 | 2.8702 | 121.4996 | -121.6415 | -121.6736
595.9688 | 121.7285 | -20.5215 | 101.2207 | 0 | 0.023712 | 0.027771 | 0.2775 | 0.059174 | 0.061096 | 0.4187 | -18.3563 | 100.5936 | -21.0938 | -17.4637 | -17.6559 | -18.6996 | -18.8553 | -19.0201 | 100.9323 | -20.755 | -0.57221 | -0.62714 | 2.1652 | 3.0579 | -118.8766 | -0.23346 | -0.28839 | 2.7374 | 1.6663 | 1.5015 | 2.8656 | 121.1151 | 2.1652 | 121.4539 | 1.8219 | -0.23346 | 121.1151 | 2.1652 | 1.8219 | 2.8656 | 121.4539 | -122.3145 | -121.9757
596.9688 | 121.0693 | -56.9458 | 63.9221 | -0.022889 | 0.02179 | 0.036316 | 0.061524 | -0.0027772 | -0.0002136 | 0.046143 | -52.4918 | 63.8809 | -57.0923 | 60.9787 | 60.7407 | 60.9695 | 61.0199 | -57.225 | 63.8626 | -57.1609 | -0.14648 | -0.041199 | 4.454 | 117.9245 | -3.1815 | -0.21515 | -0.059509 | 4.6005 | 117.9657 | -0.27924 | 117.6865 | 120.8267 | 4.454 | 120.8084 | 117.9153 | -0.21515 | 120.8267 | 4.454 | 117.9153 | 117.6865 | 120.8084 | -121.0144 | -121.0831
598.0156 | 121.637 | -56.543 | 64.8239 | 0.24414 | 0.024353 | 0.040161 | 0.068359 | -0.003418 | -0.0021362 | 0.059387 | -52.0203 | 64.8376 | -56.5384 | 62.0911 | 62.059 | 62.0682 | 61.9949 | -56.7581 | 64.7507 | -56.6895 | 0.004578 | 0.013732 | 4.5227 | 118.634 | -2.7649 | -0.14648 | -0.073243 | 4.5181 | 118.5379 | -0.21515 | 118.602 | 121.3806 | 4.5227 | 121.2936 | 118.6111 | -0.14648 | 121.3806 | 4.5227 | 118.6111 | 118.602 | 121.2936 | -121.3623 | -121.5134
598.9688 | 121.3165 | -59.2117 | 61.8759 | 0.15259 | 0.025208 | 0.043152 | 0.047852 | -0.0038452 | -0.0046996 | 0.022644 | -54.332 | 61.8301 | -59.317 | 62.0499 | 61.9171 | 62.0453 | 1.1856 | -8.8303 | 61.821 | -59.3628 | -0.10529 | -0.045777 | 4.8798 | 121.2616 | 0.041198 | -0.15106 | -0.054932 | 4.985 | 60.3973 | 50.3815 | 121.1288 | 121.0419 | 4.8798 | 121.0327 | 121.257 | -0.15106 | 121.0419 | 4.8798 | 121.257 | 121.1288 | 121.0327 | -121.1929 | -121.2387
600.0312 | 121.4676 | -58.6441 | 62.6633 | 0.40436 | 0.025421 | 0.048065 | 0.050842 | -0.0004274 | -0.001068 | 0.023712 | -53.627 | 62.6358 | -58.6945 | 62.764 | 62.6266 | 62.7594 | -6.8344 | -26.0101 | 62.6312 | -58.8043 | -0.050354 | -0.027466 | 5.0171 | 121.4081 | -0.036621 | -0.16022 | -0.032043 | 5.0674 | 51.8097 | 32.634 | 121.2708 | 121.2799 | 5.0171 | 121.2753 | 121.4035 | -0.16022 | 121.2799 | 5.0171 | 121.4035 | 121.2708 | 121.2753 | -121.3577 | -121.4676
600.9688 | 121.6461 | -60.997 | 60.3699 | -0.015259 | 0.023071 | 0.041016 | 0.047211 | -0.0029908 | -0.0046996 | 0.023071 | -55.4855 | 60.26 | -61.0886 | 60.5759 | 60.4523 | 60.5713 | -10.4095 | -32.4005 | 60.2966 | -61.1069 | -0.091553 | -0.10986 | 5.5115 | 121.5729 | 0.082398 | -0.10986 | -0.073242 | 5.603 | 50.5875 | 28.5965 | 121.4493 | 121.257 | 5.5115 | 121.2936 | 121.5683 | -0.10986 | 121.257 | 5.5115 | 121.5683 | 121.4493 | 121.2936 | -121.4584 | -121.4767
602.0156 | 121.6141 | -73.4848 | 47.7448 | 0.41962 | 0.023926 | 0.047638 | 0.048706 | -0.0032044 | -0.0021362 | 0.015594 | -67.3782 | 47.6944 | -73.5992 | 48.0057 | 47.905 | 48.0606 | -63.2217 | -71.0312 | 47.7081 | -73.6359 | -0.11444 | -0.050354 | 6.1066 | 121.4905 | 0.16022 | -0.15106 | -0.036621 | 6.221 | 10.2631 | 2.4536 | 121.3898 | 121.1792 | 6.1066 | 121.1929 | 121.5454 | -0.15106 | 121.1792 | 6.1066 | 121.5454 | 121.3898 | 121.1929 | -121.344 | -121.3806
602.9688 | 121.6187 | -72.9446 | 48.4772 | 0.099182 | 0.025635 | 0.053192 | 0.062164 | -0.0025636 | -0.0038452 | 0.016235 | -65.4419 | 48.5092 | -72.9446 | 48.4863 | 48.5229 | 48.642 | -66.5817 | -72.4319 | 48.3353 | -73.1644 | 0 | 0.032043 | 7.5027 | 121.431 | 0.045776 | -0.21973 | -0.14191 | 7.5027 | 6.3629 | 0.5127 | 121.4676 | 121.4539 | 7.5027 | 121.2799 | 121.5866 | -0.21973 | 121.4539 | 7.5027 | 121.5866 | 121.4676 | 121.2799 | -121.4218 | -121.6415
604.0156 | 121.7514 | -78.8956 | 42.453 | 0.45776 | 0.022858 | 0.058319 | 0.06601 | -0.00235 | -0.0014954 | 0.021149 | -70.9534 | 42.3569 | -79.0237 | 42.6956 | 42.5903 | 42.7551 | -78.5889 | -78.9001 | 42.4072 | -79.0375 | -0.12817 | -0.09613 | 7.9422 | 121.5912 | 0.13733 | -0.14191 | -0.045776 | 8.0704 | 0.3067 | -0.004577 | 121.4859 | 121.2524 | 7.9422 | 121.3028 | 121.6507 | -0.14191 | 121.2524 | 7.9422 | 121.6507 | 121.4859 | 121.3028 | -121.4767 | -121.4905
604.9844 | 121.5958 | -82.8415 | 38.6673 | 0.3128 | 0.028198 | 0.061737 | 0.074555 | -0.0036316 | -0.0025634 | 0.023071 | -75.9521 | 38.6078 | -82.9376 | 38.7222 | 38.5941 | 38.6856 | -82.5989 | -83.02 | 38.5254 | -83.075 | -0.09613 | -0.059509 | 6.8893 | 121.5637 | -0.073242 | -0.23346 | -0.14191 | 6.9855 | 0.24262 | -0.17853 | 121.4355 | 121.4493 | 6.8893 | 121.3669 | 121.5271 | -0.23346 | 121.4493 | 6.8893 | 121.5271 | 121.4355 | 121.3669 | -121.6049 | -121.7422
606.0156 | 121.7331 | -60.3012 | 61.203 | 0.35095 | 0.024353 | 0.053192 | 0.050842 | -0.0038452 | -0.001068 | 0.026916 | -54.0115 | 61.1252 | -60.3058 | 61.3586 | 61.235 | 61.409 | -60.3745 | -60.4019 | 61.1069 | -60.3928 | -0.004578 | -0.07782 | 6.2897 | 121.6599 | 0.032043 | -0.091553 | -0.09613 | 6.2942 | -0.073243 | -0.10071 | 121.5363 | 121.4264 | 6.2897 | 121.4081 | 121.7102 | -0.091553 | 121.4264 | 6.2897 | 121.7102 | 121.5363 | 121.4081 | -121.5088 | -121.5958
606.9688 | 121.7743 | -62.8601 | 58.5983 | 0.061035 | 0.023712 | 0.053833 | 0.055969 | -0.0055542 | -0.0023498 | 0.023071 | -56.9183 | 58.493 | -62.9379 | 58.8501 | 58.7494 | 58.8409 | -63.0569 | -62.9196 | 58.5205 | -63.002 | -0.07782 | -0.10529 | 5.9418 | 121.7102 | 0.15106 | -0.14191 | -0.07782 | 6.0196 | -0.19684 | -0.05951 | 121.6095 | 121.3531 | 5.9418 | 121.3806 | 121.701 | -0.14191 | 121.3531 | 5.9418 | 121.701 | 121.6095 | 121.3806 | -121.5363 | -121.6003
607.9688 | 121.7926 | -64.6225 | 56.8771 | 0.61798 | 0.024994 | 0.055969 | 0.061524 | -0.0074768 | -0.0049134 | 0.025207 | -58.374 | 56.7947 | -64.7003 | 57.074 | 56.9412 | 57.074 | -64.7507 | -64.7278 | 56.7856 | -64.8102 | -0.077819 | -0.082397 | 6.2485 | 121.6965 | 0.064087 | -0.18768 | -0.091553 | 6.3263 | -0.12817 | -0.10529 | 121.5637 | 121.4172 | 6.2485 | 121.4081 | 121.6965 | -0.18768 | 121.4172 | 6.2485 | 121.6965 | 121.5637 | 121.4081 | -121.5775 | -121.6873
608.9688 | 121.6736 | -66.9891 | 54.3594 | -0.022889 | 0.026062 | 0.054474 | 0.060455 | -0.0042726 | -0.003418 | 0.02713 | -60.7132 | 54.2496 | -67.1082 | 54.5609 | 54.4052 | 54.538 | -67.2867 | -67.1127 | 54.2404 | -67.1677 | -0.11902 | -0.10986 | 6.2759 | 121.55 | 0.045776 | -0.17853 | -0.11902 | 6.395 | -0.29755 | -0.1236 | 121.3943 | 121.2387 | 6.2759 | 121.2296 | 121.5271 | -0.17853 | 121.2387 | 6.2759 | 121.5271 | 121.3943 | 121.2296 | -121.4676 | -121.5271
610.0312 | 121.6782 | -69.6396 | 51.8509 | 0.22125 | 0.027344 | 0.060028 | 0.071777 | -0.0029908 | -0.001068 | 0.02478 | -63.4827 | 51.7639 | -69.7357 | 51.9974 | 51.8509 | 51.9608 | -69.8227 | -69.8318 | 51.7456 | -69.8135 | -0.096131 | -0.086975 | 6.1569 | 121.637 | 0 | -0.17395 | -0.10529 | 6.2531 | -0.18311 | -0.19226 | 121.4905 | 121.4035 | 6.1569 | 121.3852 | 121.6003 | -0.17395 | 121.4035 | 6.1569 | 121.6003 | 121.4905 | 121.3852 | -121.5866 | -121.6644
610.9688 | 121.8704 | -70.8572 | 50.647 | 0.038147 | 0.026489 | 0.061737 | 0.067291 | -0.005127 | -0.003418 | 0.026703 | -65.5243 | 50.5508 | -70.9213 | 50.9079 | 50.7797 | 50.8713 | -71.1273 | -70.8801 | 50.5463 | -70.9808 | -0.064087 | -0.096131 | 5.3329 | 121.7651 | 0.13275 | -0.1236 | -0.10071 | 5.397 | -0.27008 | -0.022888 | 121.637 | 121.4081 | 5.3329 | 121.4035 | 121.7285 | -0.1236 | 121.4081 | 5.3329 | 121.7285 | 121.637 | 121.4035 | -121.5683 | -121.6278
612.0156 | 121.8338 | -71.2601 | 50.1938 | 0.39673 | 0.028626 | 0.069641 | 0.079041 | -0.0049134 | -0.002777 | 0.03183 | -66.5131 | 50.0977 | -71.3745 | 50.4318 | 50.322 | 50.4547 | -71.6263 | -71.347 | 50.1022 | -71.434 | -0.11444 | -0.096131 | 4.747 | 121.6919 | 0.12817 | -0.17395 | -0.091553 | 4.8614 | -0.36621 | -0.086975 | 121.582 | 121.3577 | 4.747 | 121.3623 | 121.7148 | -0.17395 | 121.3577 | 4.747 | 121.7148 | 121.582 | 121.3623 | -121.5683 | -121.6278
612.9688 | 121.8063 | -76.9501 | 44.5908 | 0.053405 | 0.029053 | 0.072846 | 0.1004 | -0.005127 | -0.0029906 | 0.039093 | -71.8964 | 44.5541 | -77.0462 | 44.7876 | 44.6411 | 44.7418 | -77.0554 | -76.9821 | 44.5312 | -77.1286 | -0.096131 | -0.036621 | 5.0537 | 121.7377 | 0.050354 | -0.17853 | -0.059509 | 5.1498 | -0.10529 | -0.032044 | 121.5912 | 121.5042 | 5.0537 | 121.4813 | 121.6919 | -0.17853 | 121.5042 | 5.0537 | 121.6919 | 121.5912 | 121.4813 | -121.637 | -121.7194
614.0156 | 121.8338 | -68.779 | 52.684 | 0.40436 | 0.028626 | 0.06665 | 0.085022 | -0.0032044 | -0.0029906 | 0.037811 | -63.9862 | 52.6199 | -68.8797 | 52.9037 | 52.7893 | 52.9221 | -69.1818 | -68.9255 | 52.6199 | -68.9438 | -0.10071 | -0.064087 | 4.7928 | 121.6827 | 0.10529 | -0.16479 | -0.064087 | 4.8935 | -0.40283 | -0.14648 | 121.5683 | 121.3989 | 4.7928 | 121.3989 | 121.7011 | -0.16479 | 121.3989 | 4.7928 | 121.7011 | 121.5683 | 121.3989 | -121.5637 | -121.6278
614.9688 | 121.756 | -73.8647 | 47.6395 | 0.045776 | 0.02948 | 0.075623 | 0.095276 | -0.0081178 | -0.0012818 | 0.046783 | -69.1223 | 47.5708 | -73.9243 | 47.9187 | 47.8088 | 47.9233 | -74.1302 | -73.819 | 47.5891 | -74.0387 | -0.059509 | -0.068664 | 4.7424 | 121.7834 | 0.16937 | -0.17395 | -0.050354 | 4.8019 | -0.2655 | 0.045776 | 121.6736 | 121.4355 | 4.7424 | 121.4539 | 121.788 | -0.17395 | 121.4355 | 4.7424 | 121.788 | 121.6736 | 121.4539 | -121.5637 | -121.6782
616.0156 | 121.7651 | -91.1819 | 30.3726 | 0.37384 | 0.03183 | 0.086517 | 0.12027 | -0.003418 | -0.0023498 | 0.044861 | -85.8261 | 30.3177 | -91.3147 | 30.423 | 30.2261 | 30.4138 | -91.1774 | -91.4062 | 30.3223 | -91.3605 | -0.13275 | -0.054932 | 5.3558 | 121.6049 | -0.14649 | -0.17853 | -0.050354 | 5.4886 | 0.004578 | -0.2243 | 121.4081 | 121.4996 | 5.3558 | 121.5042 | 121.5958 | -0.17853 | 121.4996 | 5.3558 | 121.5958 | 121.4081 | 121.5042 | -121.6873 | -121.7331
616.9688 | 121.8338 | -77.6733 | 43.9316 | 0.091552 | 0.032898 | 0.081818 | 0.098694 | -0.0089722 | -0.0032044 | 0.041656 | -72.8027 | 43.8263 | -77.7466 | 44.0918 | 43.9774 | 44.1101 | -77.8336 | -77.7557 | 43.8354 | -77.8519 | -0.073242 | -0.10529 | 4.8706 | 121.7651 | 0.045776 | -0.17853 | -0.096131 | 4.9438 | -0.16022 | -0.082397 | 121.6507 | 121.4996 | 4.8706 | 121.5088 | 121.7834 | -0.17853 | 121.4996 | 4.8706 | 121.7834 | 121.6507 | 121.5088 | -121.6782 | -121.7834
617.9688 | 121.8063 | -81.1569 | 40.4205 | 0.015259 | 0.031403 | 0.08844 | 0.15402 | -0.0053406 | -0.0036316 | 0.085876 | -75.6271 | 40.3976 | -81.3217 | 40.5716 | 40.5121 | 40.5945 | -81.2393 | -81.2897 | 40.3885 | -81.3446 | -0.16479 | -0.022888 | 5.5298 | 121.7285 | 0.091553 | -0.18768 | -0.032043 | 5.6946 | -0.082398 | -0.13275 | 121.669 | 121.5546 | 5.5298 | 121.5454 | 121.7514 | -0.18768 | 121.5546 | 5.5298 | 121.7514 | 121.669 | 121.5454 | -121.7422 | -121.7651
619.0156 | 121.7514 | -84.3704 | 37.2162 | 0.39673 | 0.03183 | 0.088867 | 0.15189 | -0.0032044 | -0.0040588 | 0.082245 | -79.5822 | 37.0422 | -84.6268 | 37.3169 | 37.1933 | 37.3169 | -84.5169 | -84.5764 | 37.175 | -84.5398 | -0.25635 | -0.17395 | 4.7882 | 121.6873 | -0.022889 | -0.16937 | -0.041199 | 5.0446 | -0.14648 | -0.20599 | 121.5637 | 121.4127 | 4.7882 | 121.5454 | 121.6873 | -0.16937 | 121.4127 | 4.7882 | 121.6873 | 121.5637 | 121.5454 | -121.843 | -121.756
619.9688 | 121.9254 | -101.8753 | 19.7021 | 0.030518 | 0.030121 | 0.10617 | 0.12198 | -0.006836 | -0.0042724 | 0.037811 | -95.9885 | 19.6106 | -101.9714 | 19.9036 | 19.8349 | 19.9219 | -102.0996 | -101.8662 | 19.6106 | -102.0676 | -0.096131 | -0.091552 | 5.8868 | 121.7789 | 0.13275 | -0.19226 | -0.091552 | 5.983 | -0.2243 | 0.009155 | 121.7102 | 121.4859 | 5.8868 | 121.4859 | 121.7972 | -0.19226 | 121.4859 | 5.8868 | 121.7972 | 121.7102 | 121.4859 | -121.6736 | -121.7697
621.0156 | 121.8521 | -104.068 | 17.5552 | 0.37384 | 0.033325 | 0.10959 | 0.13031 | -0.0055542 | -0.0036316 | 0.030975 | -98.0484 | 17.4728 | -104.2145 | 17.5232 | 17.4774 | 17.7246 | -104.2374 | -104.2282 | 17.4912 | -104.2328 | -0.14648 | -0.082398 | 6.0196 | 121.5912 | -0.07782 | -0.16479 | -0.064087 | 6.1661 | -0.16937 | -0.16022 | 121.5454 | 121.5408 | 6.0196 | 121.5591 | 121.7926 | -0.16479 | 121.5408 | 6.0196 | 121.7926 | 121.5454 | 121.5591 | -121.7697 | -121.788
621.9688 | 121.8933 | -107.3868 | 14.296 | 0.18311 | 0.03418 | 0.11472 | 0.1333 | -0.004059 | -0.0046996 | 0.036316 | -101.1566 | 14.241 | -107.4783 | 14.3188 | 14.241 | 14.3188 | -107.46 | -107.4554 | 14.2319 | -107.579 | -0.091553 | -0.054931 | 6.2302 | 121.7056 | -0.054931 | -0.19226 | -0.064086 | 6.3217 | -0.073242 | -0.068664 | 121.6278 | 121.6278 | 6.2302 | 121.6187 | 121.7056 | -0.19226 | 121.6278 | 6.2302 | 121.7056 | 121.6278 | 121.6187 | -121.7743 | -121.875
623.0156 | 121.9803 | -112.4405 | 9.1461 | 0.37384 | 0.33176 | 0.37149 | 0.10574 | -0.0038452 | -0.0025634 | 0.041229 | -72.6242 | 9.082 | -112.5458 | 9.2056 | 9.1599 | 9.2606 | -112.7014 | -112.532 | 9.0958 | -112.6648 | -0.10529 | -0.064087 | 39.8163 | 121.6461 | 0.013733 | -0.2243 | -0.050354 | 39.9216 | -0.26093 | -0.091552 | 121.6003 | 121.5225 | 39.8163 | 121.5363 | 121.701 | -0.2243 | 121.5225 | 39.8163 | 121.701 | 121.6003 | 121.5363 | -121.6919 | -121.8109
623.9688 | 121.875 | -115.5624 | 6.2027 | 0.015259 | 0.32022 | 0.3606 | 0.10638 | -0.0046998 | -0.0021362 | 0.04422 | -62.7136 | 6.0883 | -115.6311 | 6.0791 | 6.0516 | 6.1752 | -115.5075 | -115.6631 | 6.1295 | -115.7272 | -0.068665 | -0.11444 | 52.8488 | 121.6415 | -0.15106 | -0.16479 | -0.073242 | 52.9175 | 0.054932 | -0.10071 | 121.6141 | 121.6507 | 52.8488 | 121.6919 | 121.7377 | -0.16479 | 121.6507 | 52.8488 | 121.7377 | 121.6141 | 121.6919 | -121.8338 | -121.9299
625.0156 | 121.7972 | -117.9611 | 3.6301 | 0.38147 | 2.0247 | 2.0745 | 0.072846 | -0.0038452 | -0.0036316 | 0.03653 | -9.5718 | 3.4287 | -117.897 | 3.5522 | 3.5248 | 3.5843 | -118.1442 | -118.0664 | 3.566 | -118.1763 | 0.064087 | -0.20142 | 108.3893 | 121.5134 | -0.10529 | -0.21515 | -0.064087 | 108.3252 | -0.1831 | -0.10528 | 121.4859 | 121.3898 | 108.3893 | 121.5271 | 121.5454 | -0.21515 | 121.3898 | 108.3893 | 121.5454 | 121.4859 | 121.5271 | -121.5271 | -121.8063
625.9688 | 121.8796 | -118.4875 | 3.0991 | 0.030518 | 1.3535 | 1.3753 | 0.06366 | -0.0059816 | -0.0049134 | 0.033966 | -8.4457 | 2.9388 | -118.5196 | 3.1174 | 3.1357 | 3.1586 | -118.7027 | -118.5104 | 3.0533 | -118.7119 | -0.032043 | -0.16022 | 110.0418 | 121.6049 | 0.036621 | -0.2243 | -0.045776 | 110.0739 | -0.21515 | -0.022888 | 121.6232 | 121.4264 | 110.0418 | 121.5408 | 121.6461 | -0.2243 | 121.4264 | 110.0418 | 121.6461 | 121.6232 | 121.5408 | -121.6187 | -121.8109
626.9688 | 121.8246 | -116.629 | 4.9393 | 0.022888 | 0.01239 | 0.10938 | 0.16684 | -0.0055542 | -0.0038452 | 0.033966 | -111.5341 | -9.1095 | -116.8579 | 4.7516 | 4.7562 | 4.8157 | -116.7847 | -116.8625 | 4.8386 | -116.9998 | -0.22888 | -14.0488 | 5.0949 | 121.3806 | -0.1831 | -0.37079 | -0.10071 | 5.3238 | -0.15564 | -0.23346 | 121.3852 | 107.5195 | 5.0949 | 121.4676 | 121.4447 | -0.37079 | 107.5195 | 5.0949 | 121.4447 | 121.3852 | 121.4676 | -121.7972 | -121.9391
628.0156 | 121.7926 | -91.4749 | 30.011 | 0.37384 | 0.0091858 | 0.19333 | 0.46548 | -0.003418 | -0.0046996 | 0.047211 | -28.8574 | -9.082 | -91.4474 | 29.7958 | 29.8187 | 30.1025 | -91.6351 | -91.5344 | 29.9423 | -91.6672 | 0.027466 | -39.093 | 62.6175 | 121.2708 | -0.19226 | -0.19226 | -0.068664 | 62.59 | -0.16022 | -0.059509 | 121.2936 | 82.3929 | 62.6175 | 121.4172 | 121.5775 | -0.19226 | 82.3929 | 62.6175 | 121.5775 | 121.2936 | 121.4172 | -121.4584 | -121.6782
628.9688 | 121.9391 | -88.0508 | 33.5175 | -0.015259 | 0.0091858 | 0.2384 | 0.32129 | -0.0061952 | -0.0053406 | 0.073273 | -15.7516 | -9.0775 | -88.1058 | 33.6273 | 33.5083 | 33.696 | -88.4171 | -88.092 | 33.3481 | -88.2614 | -0.054932 | -42.5949 | 72.2992 | 121.6782 | -0.009155 | -0.21057 | -0.16937 | 72.3541 | -0.36621 | -0.041199 | 121.5591 | 78.9734 | 72.2992 | 121.3989 | 121.7468 | -0.21057 | 78.9734 | 72.2992 | 121.7468 | 121.5591 | 121.3989 | -121.6232 | -121.7789
629.9688 | 121.8613 | -82.608 | 38.8962 | -0.25177 | 0.0091858 | 0.42148 | 0.4736 | -0.0038452 | -0.0029906 | 0.055542 | -17.0609 | -9.082 | -82.2372 | 39.4867 | 38.8458 | 39.0839 | -82.8094 | -82.8598 | 38.8687 | -82.8278 | 0.37079 | -47.9782 | 65.5472 | 122.0947 | -0.050354 | -0.21973 | -0.027466 | 65.1764 | -0.20142 | -0.25177 | 121.4539 | 73.526 | 65.5472 | 121.4767 | 121.6919 | -0.21973 | 73.526 | 65.5472 | 121.6919 | 121.4539 | 121.4767 | -121.1334 | -121.7239
631.0156 | 121.9666 | -98.703 | 22.7463 | 0.56458 | 0.010468 | 0.31039 | 0.37555 | -0.0042726 | -0.001709 | 0.048706 | -14.4928 | -9.0775 | -98.6847 | 23.4879 | 23.3917 | 23.4421 | -98.8861 | -98.9456 | 23.0484 | -98.8632 | 0.018311 | -31.8237 | 84.2102 | 122.1909 | 0.64545 | -0.16022 | 0.30212 | 84.1919 | -0.1831 | -0.24262 | 122.0947 | 89.6255 | 84.2102 | 121.7514 | 122.1451 | -0.16022 | 89.6255 | 84.2102 | 122.1451 | 122.0947 | 121.7514 | -121.431 | -121.6095
631.9688 | 121.8979 | -116.922 | 4.8523 | 0.16022 | 0.010681 | 0.32257 | 0.4328 | -0.0072632 | -0.0053406 | 0.096344 | -17.7933 | -9.082 | -116.9357 | 4.7836 | 4.7516 | 4.8065 | -116.8945 | -116.89 | 4.7928 | -117.0456 | -0.013733 | -13.9343 | 99.1287 | 121.7056 | -0.10071 | -0.1236 | -0.059509 | 99.1425 | 0.027466 | 0.032043 | 121.6736 | 107.84 | 99.1287 | 121.7148 | 121.7285 | -0.1236 | 107.84 | 99.1287 | 121.7285 | 121.6736 | 121.7148 | -121.788 | -121.8979
633.0156 | 121.7377 | -117.3065 | 4.4266 | 0.38147 | 0.0098268 | 0.3623 | 0.42276 | -0.0053406 | -0.0019226 | 0.047424 | -17.0563 | -9.082 | -117.2882 | 4.39 | 4.3991 | 4.422 | -117.4759 | -117.3019 | 4.3579 | -117.4301 | 0.018311 | -13.5086 | 100.2502 | 121.6965 | -0.027466 | -0.1236 | -0.068665 | 100.2319 | -0.16937 | 0.004578 | 121.7056 | 108.2245 | 100.2502 | 121.6644 | 121.7285 | -0.1236 | 108.2245 | 100.2502 | 121.7285 | 121.7056 | 121.6644 | -121.7148 | -121.8567
633.9688 | 121.9345 | -117.2058 | 4.4998 | 0.11444 | 0.0087586 | 0.38815 | 0.44904 | -0.0076904 | -0.0042724 | 0.049774 | -16.5756 | -9.0866 | -117.2791 | 4.4678 | 4.4632 | 4.5227 | -117.3981 | -117.1509 | 4.39 | -117.3798 | -0.073242 | -13.5864 | 100.6302 | 121.6736 | -0.036621 | -0.17395 | -0.10986 | 100.7034 | -0.19226 | 0.054932 | 121.669 | 108.1192 | 100.6302 | 121.5958 | 121.7285 | -0.17395 | 108.1192 | 100.6302 | 121.7285 | 121.669 | 121.5958 | -121.7789 | -121.8796
635.0156 | 121.6278 | -83.5739 | 38.118 | 0.36621 | 0.012177 | 2.8805 | 2.8489 | -0.0074768 | -0.0032044 | 0.056183 | -30.1117 | -9.082 | -83.757 | 37.6923 | 37.6602 | 37.7747 | -83.876 | -83.876 | 37.6694 | -83.8531 | -0.1831 | -47.2 | 53.4622 | 121.2662 | -0.45776 | -0.27923 | -0.44861 | 53.6453 | -0.30212 | -0.30212 | 121.2341 | 74.4919 | 53.4622 | 121.2433 | 121.3486 | -0.27923 | 74.4919 | 53.4622 | 121.3486 | 121.2341 | 121.2433 | -121.875 | -121.9711
635.9688 | 121.8109 | -76.3412 | 45.6848 | -0.038147 | 0.006836 | 0.88419 | 0.86389 | -0.01004 | -0.0049134 | 0.047424 | -34.0851 | -9.0912 | -74.7849 | 44.9799 | 47.1588 | 48.23 | -75.8377 | -76.5656 | 45.9137 | -76.1353 | 1.5564 | -54.776 | 42.2562 | 121.3211 | 1.474 | 0.20599 | 0.22888 | 40.6998 | 0.50354 | -0.2243 | 123.5001 | 67.2501 | 42.2562 | 122.2549 | 124.5712 | 0.20599 | 67.2501 | 42.2562 | 124.5712 | 123.5001 | 122.2549 | -120.4697 | -121.8201
636.9688 | 121.8613 | -89.328 | 32.1625 | 0.061035 | 0.0059814 | 3.685 | 3.7183 | -0.0064088 | -0.0023498 | 0.058105 | -29.567 | -9.0912 | -89.9918 | 31.3705 | 31.485 | 31.8283 | -89.6255 | -89.6255 | 31.5262 | -89.6393 | -0.66376 | -41.2537 | 59.761 | 120.6985 | -0.67749 | -0.31128 | -0.63629 | 60.4248 | -0.29755 | -0.29755 | 120.813 | 80.2368 | 59.761 | 120.8542 | 121.1563 | -0.31128 | 80.2368 | 59.761 | 121.1563 | 120.813 | 120.8542 | -122.1542 | -121.8018
638.0156 | 121.0373 | -118.1671 | 2.536 | -0.083923 | 0.011108 | 1.1529 | 1.0784 | -0.005127 | -0.003418 | 0.067932 | -56.9504 | -9.1095 | -118.0573 | 2.1606 | 2.3758 | 2.3621 | -118.4189 | -118.4052 | 2.1927 | -118.4601 | 0.10986 | -11.6455 | 61.2167 | 120.3278 | -0.16022 | -0.29297 | -0.34332 | 61.1069 | -0.25177 | -0.23804 | 120.5429 | 109.0576 | 61.2167 | 120.3598 | 120.5292 | -0.29297 | 109.0576 | 61.2167 | 120.5292 | 120.5429 | 120.3598 | -120.5933 | -120.9961
638.9688 | 121.1929 | -0.99792 | 120.0027 | -0.0076295 | 0.013031 | 0.027985 | 0.057037 | -0.0053406 | -0.0029906 | 0.053406 | -0.21515 | -0.92926 | -1.0483 | 120.2408 | 120.108 | 120.108 | 120.1904 | 115.9103 | 120.163 | -1.0941 | -0.050354 | -120.932 | 0.78278 | 121.2387 | 0.10528 | -0.09613 | 0.16022 | 0.83313 | 121.1884 | 116.9083 | 121.106 | 0.068665 | 0.78278 | 121.1609 | 121.106 | -0.09613 | 0.068665 | 0.78278 | 121.106 | 121.106 | 121.1609 | -121.051 | -121.0968
640.0156 | 121.5363 | -0.28839 | 121.0373 | 0.40436 | 0.0091858 | 0.024353 | 0.082886 | -0.005127 | -0.0053406 | 0.077759 | -0.050354 | -0.29755 | -0.32501 | 121.2341 | 121.0831 | 121.1334 | 120.8542 | 120.0256 | 120.9778 | -0.3891 | -0.036621 | -121.3348 | 0.23804 | 121.5225 | 0.045777 | -0.10071 | -0.059509 | 0.27466 | 121.1426 | 120.314 | 121.3715 | -0.009155 | 0.23804 | 121.2662 | 121.4218 | -0.10071 | -0.009155 | 0.23804 | 121.4218 | 121.3715 | 121.2662 | -121.3623 | -121.4264
640.9688 | 121.5363 | -0.086975 | 121.0556 | 0.21362 | 0.009613 | 0.023712 | 0.207 | -0.0093994 | -0.005127 | 0.046997 | -0.11902 | -0.26093 | -0.28839 | 121.2845 | 121.1609 | 121.2021 | 121.0419 | 120.9 | 121.0739 | 2.1835 | -0.20142 | -121.3165 | -0.032044 | 121.3715 | 0.10529 | 2.2705 | 0.018311 | 0.16937 | 121.1288 | 120.9869 | 121.2479 | -0.17395 | -0.032044 | 121.1609 | 121.2891 | 2.2705 | -0.17395 | -0.032044 | 121.2891 | 121.2479 | 121.1609 | -121.344 | -118.8721
642.0156 | 121.5225 | -0.3067 | 121.2204 | 0.26703 | 0.010895 | 0.026917 | 0.3559 | -0.0087586 | -0.0057678 | 0.33881 | -0.12817 | -0.23804 | -0.3479 | 121.1975 | 121.051 | 121.0831 | 121.1517 | 95.6085 | 121.1243 | -0.37079 | -0.041198 | -121.4584 | 0.17853 | 121.5042 | -0.16937 | -0.064087 | -0.09613 | 0.21973 | 121.4584 | 95.9152 | 121.3577 | 0.068665 | 0.17853 | 121.431 | 121.3898 | -0.064087 | 0.068665 | 0.17853 | 121.3898 | 121.3577 | 121.431 | -121.5683 | -121.5912
642.9688 | 121.3669 | -0.27466 | 121.2204 | 0.068664 | 0.01004 | 0.026062 | 0.87137 | -0.008545 | -0.0049134 | 0.86774 | -0.16479 | -0.20142 | -0.31128 | 121.1838 | 121.0922 | 121.0236 | 121.1655 | 120.9503 | 121.1334 | -0.21057 | -0.036621 | -121.4218 | 0.10986 | 121.4584 | -0.12817 | 0.064087 | -0.086975 | 0.14648 | 121.4401 | 121.225 | 121.3669 | 0.073242 | 0.10986 | 121.4081 | 121.2982 | 0.064087 | 0.073242 | 0.10986 | 121.2982 | 121.3669 | 121.4081 | -121.5317 | -121.431
644.0156 | 121.582 | -0.27008 | 121.1655 | 0.45013 | 0.010895 | 0.026703 | 0.028839 | -0.0008546 | -0.0025634 | 0.020081 | -0.09613 | -0.22888 | -0.31586 | 121.3028 | 121.1746 | 121.1884 | 121.0876 | 88.9252 | 121.1472 | -0.38452 | -0.045776 | -121.3943 | 0.17395 | 121.5729 | 0.009156 | -0.11444 | -0.01831 | 0.21973 | 121.3577 | 89.1953 | 121.4447 | 0.041199 | 0.17395 | 121.4172 | 121.4584 | -0.11444 | 0.041199 | 0.17395 | 121.4584 | 121.4447 | 121.4172 | -121.4813 | -121.55
644.9688 | 121.5408 | -0.28839 | 121.2982 | -0.038147 | 0.0093994 | 0.026489 | 0.030975 | -0.0044862 | -0.0040588 | 0.026062 | -0.15564 | -0.21973 | -0.3479 | 121.3531 | 121.1929 | 121.2112 | 121.2982 | 112.7655 | 121.2341 | -0.39825 | -0.059509 | -121.5179 | 0.13275 | 121.6415 | -0.10529 | -0.10986 | -0.064087 | 0.19226 | 121.5866 | 113.0539 | 121.4813 | 0.068664 | 0.13275 | 121.5225 | 121.4996 | -0.10986 | 0.068664 | 0.13275 | 121.4996 | 121.4813 | 121.5225 | -121.6461 | -121.6965
646.0156 | 121.6278 | -0.29755 | 121.2891 | 0.39673 | 0.009613 | 0.026703 | 0.038025 | -0.0038452 | -0.005127 | 0.028412 | -0.14648 | -0.19684 | -0.32959 | 121.3623 | 121.2112 | 121.2296 | 121.2753 | 116.0477 | 121.2708 | -0.3891 | -0.032044 | -121.4859 | 0.15106 | 121.6599 | -0.077819 | -0.091553 | -0.01831 | 0.18311 | 121.5729 | 116.3452 | 121.5088 | 0.10071 | 0.15106 | 121.5683 | 121.5271 | -0.091553 | 0.10071 | 0.15106 | 121.5271 | 121.5088 | 121.5683 | -121.6187 | -121.6782
646.9688 | 121.6827 | -0.26093 | 121.3165 | -0.053406 | 0.01004 | 0.021362 | 0.036743 | -0.0076904 | -0.0036316 | 0.033539 | 0.064087 | -0.25635 | -0.32044 | 121.4722 | 121.344 | 121.3577 | 121.2524 | 114.5782 | 121.2708 | -0.37537 | -0.05951 | -121.5729 | 0.32501 | 121.7331 | 0.027466 | -0.11444 | -0.045776 | 0.38452 | 121.5134 | 114.8392 | 121.6049 | 0.004577 | 0.32501 | 121.5317 | 121.6187 | -0.11444 | 0.004577 | 0.32501 | 121.6187 | 121.6049 | 121.5317 | -121.637 | -121.6919
648.0156 | 121.6415 | -0.28839 | 121.3623 | 0.27466 | 0.009613 | 0.026703 | 0.037384 | -0.0055542 | -0.0046996 | 0.027771 | -0.15106 | -0.21057 | -0.32501 | 121.3989 | 121.2479 | 121.2662 | 121.3715 | 92.8619 | 121.3257 | -0.37994 | -0.036621 | -121.5729 | 0.13733 | 121.6873 | -0.11444 | -0.091553 | -0.036621 | 0.17395 | 121.6599 | 93.1503 | 121.5363 | 0.07782 | 0.13733 | 121.6141 | 121.5546 | -0.091553 | 0.07782 | 0.13733 | 121.5546 | 121.5363 | 121.6141 | -121.6873 | -121.7422
648.9688 | 121.7377 | -0.24719 | 121.3577 | 0.24414 | 0.006836 | 0.026062 | 0.029907 | -0.0070496 | -0.0029906 | 0.029907 | -0.10529 | -0.25177 | -0.28839 | 121.4813 | 121.3577 | 121.3898 | 121.2662 | 88.1195 | 121.2799 | -0.33875 | -0.041199 | -121.6095 | 0.14191 | 121.7285 | 0 | -0.091553 | -0.07782 | 0.18311 | 121.5134 | 88.3667 | 121.6049 | -0.004578 | 0.14191 | 121.5271 | 121.637 | -0.091553 | -0.004578 | 0.14191 | 121.637 | 121.6049 | 121.5271 | -121.6461 | -121.6965
650.0156 | 121.7422 | -0.28381 | 121.3943 | 0.1297 | 0.011322 | 0.030335 | 0.055328 | -0.0061952 | -0.0040588 | 0.041656 | -0.064087 | -0.23346 | -0.32501 | 121.5225 | 121.3623 | 121.3715 | 121.3257 | 91.8777 | 121.2936 | -0.37994 | -0.041199 | -121.6278 | 0.21973 | 121.8063 | -0.032043 | -0.096131 | -0.10071 | 0.26093 | 121.6095 | 92.1616 | 121.6461 | 0.050354 | 0.21973 | 121.5775 | 121.6553 | -0.096131 | 0.050354 | 0.21973 | 121.6553 | 121.6461 | 121.5775 | -121.7194 | -121.7743
650.9688 | 121.756 | -0.28839 | 121.3989 | 0.045776 | 0.0098268 | 0.026489 | 0.036957 | -0.0064088 | -0.005127 | 0.030121 | -0.082397 | -0.27008 | -0.29755 | 121.5134 | 121.3852 | 121.3943 | 121.3394 | 89.6713 | 121.344 | -0.3891 | -0.009155 | -121.669 | 0.20599 | 121.8018 | -0.013733 | -0.10071 | -0.054932 | 0.21515 | 121.6278 | 89.9597 | 121.6736 | 0.01831 | 0.20599 | 121.6324 | 121.6827 | -0.10071 | 0.01831 | 0.20599 | 121.6827 | 121.6736 | 121.6324 | -121.6965 | -121.788
652.0156 | 121.7331 | -0.33417 | 121.4127 | 0.40436 | 0.011322 | 0.026489 | 0.042938 | -0.0038452 | -0.005127 | 0.028839 | -0.12817 | -0.24719 | -0.37079 | 121.4355 | 121.2936 | 121.3074 | 121.3623 | 90.802 | 121.3623 | -0.42114 | -0.036622 | -121.6599 | 0.20599 | 121.7697 | -0.11902 | -0.086976 | -0.050354 | 0.24261 | 121.6965 | 91.1362 | 121.6278 | 0.086975 | 0.20599 | 121.6965 | 121.6415 | -0.086976 | 0.086975 | 0.20599 | 121.6415 | 121.6278 | 121.6965 | -121.7834 | -121.8338
652.9688 | 121.8567 | -0.27924 | 121.4081 | 0.15259 | 0.0081178 | 0.025208 | 0.037384 | -0.0072632 | -0.0032044 | 0.034607 | -0.09613 | -0.3479 | -0.36163 | 121.5591 | 121.431 | 121.4676 | 121.3028 | 92.1936 | 121.3394 | -0.37537 | -0.082397 | -121.756 | 0.18311 | 121.8384 | 0.022888 | -0.09613 | -0.068664 | 0.2655 | 121.582 | 92.4728 | 121.7102 | -0.068664 | 0.18311 | 121.6187 | 121.7468 | -0.09613 | -0.068664 | 0.18311 | 121.7468 | 121.7102 | 121.6187 | -121.7697 | -121.7834
654.0156 | 121.7651 | -0.32044 | 121.431 | 0.24414 | 0.013245 | 0.025208 | 0.11151 | -0.0055542 | -0.004486 | 0.1004 | -0.10529 | -0.24719 | -0.34332 | 121.5042 | 121.3211 | 121.3303 | 121.3806 | 14.3829 | 121.3165 | -0.4303 | -0.022888 | -121.6782 | 0.21515 | 121.8246 | -0.10986 | -0.10986 | -0.11444 | 0.23804 | 121.7011 | 14.7034 | 121.6415 | 0.073243 | 0.21515 | 121.637 | 121.6507 | -0.10986 | 0.073243 | 0.21515 | 121.6507 | 121.6415 | 121.637 | -121.7743 | -121.8613
654.9688 | 121.875 | -0.29755 | 121.4127 | 0.22888 | 0.011108 | 0.023712 | 0.039093 | -0.0081178 | -0.005127 | 0.031189 | -0.091553 | -0.29297 | -0.33417 | 121.5317 | 121.4172 | 121.4401 | 121.312 | 96.7392 | 121.3623 | -0.39368 | -0.036621 | -121.7056 | 0.20599 | 121.8292 | 0.004577 | -0.096131 | -0.050354 | 0.24261 | 121.6095 | 97.0367 | 121.7148 | 0.004577 | 0.20599 | 121.6599 | 121.7377 | -0.096131 | 0.004577 | 0.20599 | 121.7377 | 121.7148 | 121.6599 | -121.7468 | -121.8063
655.9688 | 121.8887 | -0.34332 | 121.4218 | 0.20599 | 0.010681 | 0.023071 | 0.034821 | -0.0076904 | -0.0023498 | 0.033539 | -0.10986 | -0.25177 | -0.32501 | 121.5591 | 121.431 | 121.4722 | 121.3257 | 88.9114 | 121.3257 | -0.44861 | 0.018311 | -121.6736 | 0.23346 | 121.9025 | 0.009155 | -0.10529 | -0.09613 | 0.21515 | 121.669 | 89.2548 | 121.7743 | 0.091553 | 0.23346 | 121.669 | 121.8155 | -0.10529 | 0.091553 | 0.23346 | 121.8155 | 121.7743 | 121.669 | -121.7468 | -121.8704
657.0156 | 121.7926 | -0.33875 | 121.4218 | 0.35095 | 0.0091858 | 0.024994 | 0.20529 | -0.0057678 | -0.003418 | 0.19183 | -0.13275 | -0.25635 | -0.33417 | 121.4951 | 121.344 | 121.3531 | 121.4081 | 114.4363 | 121.4127 | -0.40741 | 0.004578 | -121.6782 | 0.20599 | 121.8338 | -0.07782 | -0.068665 | -0.009155 | 0.20142 | 121.7468 | 114.7751 | 121.6827 | 0.082397 | 0.20599 | 121.7514 | 121.6919 | -0.068665 | 0.082397 | 0.20599 | 121.6919 | 121.6827 | 121.7514 | -121.756 | -121.8292
657.9688 | 121.907 | -0.27924 | 121.4539 | 0.1297 | 0.010468 | 0.024353 | 0.069855 | -0.0055542 | -0.0014954 | 0.064301 | -0.059509 | -0.27008 | -0.31128 | 121.6507 | 121.5179 | 121.55 | 121.3531 | 78.511 | 121.3989 | -0.36621 | -0.032043 | -121.7239 | 0.21973 | 121.9299 | 0.064087 | -0.086975 | -0.054931 | 0.25177 | 121.6324 | 78.7903 | 121.7972 | 0.009155 | 0.21973 | 121.6782 | 121.8292 | -0.086975 | 0.009155 | 0.21973 | 121.8292 | 121.7972 | 121.6782 | -121.7651 | -121.8201
659.0156 | 121.8338 | -0.32959 | 121.4951 | 0.3128 | 0.011749 | 0.024353 | 0.040802 | -0.0064088 | -0.0029906 | 0.027344 | -0.15106 | -0.24261 | -0.36163 | 121.5546 | 121.3943 | 121.3943 | 121.4676 | 92.6651 | 121.4218 | -0.41657 | -0.032043 | -121.7377 | 0.17853 | 121.8842 | -0.10071 | -0.086975 | -0.073242 | 0.21057 | 121.7972 | 92.9947 | 121.7239 | 0.086975 | 0.17853 | 121.7514 | 121.7239 | -0.086975 | 0.086975 | 0.17853 | 121.7239 | 121.7239 | 121.7514 | -121.8567 | -121.9116
659.9688 | 121.9162 | -0.25635 | 121.4539 | 0.19836 | 0.0087586 | 0.026703 | 0.02948 | -0.006836 | -0.0040588 | 0.024353 | -0.064087 | -0.30212 | -0.31586 | 121.6461 | 121.5225 | 121.55 | 121.376 | 104.1962 | 121.4218 | -0.29297 | -0.059509 | -121.756 | 0.19226 | 121.9025 | 0.068665 | -0.036621 | -0.032043 | 0.25177 | 121.6324 | 104.4525 | 121.7789 | -0.045776 | 0.19226 | 121.6782 | 121.8063 | -0.036621 | -0.045776 | 0.19226 | 121.8063 | 121.7789 | 121.6782 | -121.7697 | -121.7468
661.0156 | 121.4859 | -0.3067 | 121.1334 | 0.32806 | 0.010254 | 0.026489 | 0.024353 | -0.0038452 | -0.0004272 | 0.015381 | -0.13275 | -0.25635 | -0.36621 | 121.1929 | 121.2112 | 121.1884 | 121.0602 | 121.106 | 121.1151 | -0.41199 | -0.059509 | -121.3898 | 0.17395 | 121.4996 | 0.07782 | -0.10529 | -0.018311 | 0.23346 | 121.3669 | 121.4127 | 121.5179 | 0.050354 | 0.17395 | 121.4218 | 121.4951 | -0.10529 | 0.050354 | 0.17395 | 121.4951 | 121.5179 | 121.4218 | -121.4996 | -121.5454
661.9688 | 121.6507 | -0.29755 | 121.2341 | 0.20599 | 0.010681 | 0.023712 | 0.018372 | -0.0049134 | 0.0006408 | 0.013031 | -0.11444 | -0.30212 | -0.3479 | 121.3623 | 121.2341 | 121.2662 | 121.1655 | 121.2067 | 121.1929 | -0.3891 | -0.050354 | -121.5363 | 0.1831 | 121.6599 | 0 | -0.091553 | -0.041199 | 0.23346 | 121.463 | 121.5042 | 121.5317 | -0.004578 | 0.1831 | 121.4905 | 121.5637 | -0.091553 | -0.004578 | 0.1831 | 121.5637 | 121.5317 | 121.4905 | -121.582 | -121.6232
663.0156 | 121.6324 | -0.33417 | 121.3303 | 0.36621 | 0.0098268 | 0.026489 | 0.02478 | -0.0053406 | -0.001709 | 0.013245 | -0.14191 | -0.25177 | -0.36621 | 121.3806 | 121.2204 | 121.2524 | 121.2845 | 121.1792 | 121.2982 | -0.43488 | -0.032044 | -121.582 | 0.19226 | 121.7148 | -0.10986 | -0.10071 | -0.032043 | 0.2243 | 121.6187 | 121.5134 | 121.5546 | 0.082397 | 0.19226 | 121.6324 | 121.5866 | -0.10071 | 0.082397 | 0.19226 | 121.5866 | 121.5546 | 121.6324 | -121.6965 | -121.7651
663.9688 | 121.7926 | -0.38452 | 121.257 | 0.21362 | 0.0074768 | 0.02478 | 0.018799 | -0.0093994 | -0.0021362 | 0.015381 | -0.11444 | -0.29297 | -0.33417 | 121.4813 | 121.3348 | 121.3623 | 121.0968 | 121.17 | 121.1517 | -0.44403 | 0.050354 | -121.55 | 0.27008 | 121.8658 | 0.07782 | -0.05951 | -0.10529 | 0.21973 | 121.4813 | 121.5546 | 121.7194 | 0.091552 | 0.27008 | 121.5363 | 121.7468 | -0.05951 | 0.091552 | 0.27008 | 121.7468 | 121.7194 | 121.5363 | -121.5912 | -121.701
665.0156 | 121.7285 | -0.33875 | 121.3669 | 0.35095 | 0.011536 | 0.027771 | 0.029053 | -0.0061952 | -0.0038452 | 0.016235 | -0.054932 | -0.2655 | -0.37994 | 121.4447 | 121.3028 | 121.3211 | 121.312 | 121.2524 | 121.3348 | -0.42572 | -0.041199 | -121.6324 | 0.28381 | 121.7834 | -0.064087 | -0.086975 | -0.032043 | 0.32501 | 121.6507 | 121.5912 | 121.6415 | 0.073242 | 0.28381 | 121.6736 | 121.6599 | -0.086975 | 0.073242 | 0.28381 | 121.6599 | 121.6415 | 121.6736 | -121.7468 | -121.7926
665.9688 | 121.7697 | -0.35248 | 121.3898 | -0.045776 | 0.0093994 | 0.028198 | 0.026062 | -0.0057678 | -0.0032044 | 0.016876 | -0.11444 | -0.28839 | -0.35248 | 121.5179 | 121.3531 | 121.3623 | 121.3898 | 121.3531 | 121.3303 | -0.4303 | 0 | -121.6782 | 0.23804 | 121.8704 | -0.036622 | -0.07782 | -0.05951 | 0.23804 | 121.7422 | 121.7056 | 121.7056 | 0.064087 | 0.23804 | 121.6827 | 121.7148 | -0.07782 | 0.064087 | 0.23804 | 121.7148 | 121.7056 | 121.6827 | -121.7422 | -121.8201
667.0156 | 121.7331 | -0.24719 | 121.582 | 0.22888 | 0.011108 | 0.029694 | 0.038239 | -0.0074768 | -0.007904 | 0.025848 | -0.1236 | -0.1831 | -0.2655 | 121.5958 | 121.431 | 121.463 | 121.5271 | 121.4035 | 121.5088 | -0.34332 | -0.018311 | -121.7651 | 0.1236 | 121.843 | -0.15106 | -0.096131 | -0.073242 | 0.14191 | 121.7743 | 121.6507 | 121.6782 | 0.064087 | 0.1236 | 121.756 | 121.7102 | -0.096131 | 0.064087 | 0.1236 | 121.7102 | 121.6782 | 121.756 | -121.8475 | -121.9254
667.9688 | 121.8933 | -0.1831 | 121.4905 | 0.20599 | 0.0091858 | 0.027985 | 0.024139 | -0.0070496 | -0.001709 | 0.016235 | -0.082397 | -0.11902 | -0.14648 | 121.7148 | 121.5912 | 121.6232 | 121.4996 | 121.5775 | 121.5363 | -0.23804 | 0.036621 | -121.6095 | 0.10071 | 121.8979 | 0.10071 | -0.054932 | 0.045776 | 0.064087 | 121.6827 | 121.7606 | 121.7743 | 0.064086 | 0.10071 | 121.7194 | 121.8063 | -0.054932 | 0.064086 | 0.10071 | 121.8063 | 121.7743 | 121.7194 | -121.637 | -121.7285
669.0156 | 121.7926 | -0.16937 | 121.637 | 0.22125 | 0.010468 | 0.025208 | 0.08609 | -0.006836 | -0.0046996 | 0.072632 | -0.14191 | -0.10071 | -0.17853 | 121.669 | 121.5179 | 121.5271 | 121.6095 | 121.4539 | 121.5958 | -0.054932 | -0.009155 | -121.7377 | 0.027466 | 121.8384 | -0.11902 | 0.11444 | -0.041199 | 0.036621 | 121.7789 | 121.6232 | 121.6873 | 0.068665 | 0.027466 | 121.7651 | 121.6965 | 0.11444 | 0.068665 | 0.027466 | 121.6965 | 121.6873 | 121.7651 | -121.8155 | -121.6919
669.9688 | 121.9345 | -0.11902 | 121.6415 | 0.28992 | 0.010254 | 0.026276 | 0.033966 | -0.006836 | -0.0032044 | 0.021576 | -0.059509 | -0.1236 | -0.14648 | 121.788 | 121.6599 | 121.6736 | 121.4859 | 121.6324 | 121.5591 | -0.20599 | -0.027465 | -121.7651 | 0.05951 | 121.907 | 0.01831 | -0.086975 | -0.082398 | 0.086975 | 121.6049 | 121.7514 | 121.7789 | -0.004577 | 0.05951 | 121.6782 | 121.7926 | -0.086975 | -0.004577 | 0.05951 | 121.7926 | 121.7789 | 121.6782 | -121.788 | -121.8475
671.0156 | 121.8155 | -0.20142 | 121.6461 | 0.28229 | 0.012177 | 0.023285 | 0.045075 | -0.0046998 | -0.002777 | 0.032471 | -0.11444 | -0.10071 | -0.19226 | 121.7239 | 121.5591 | 121.5683 | 121.6141 | 121.5225 | 121.582 | -0.27008 | 0.009155 | -121.7468 | 0.086975 | 121.9254 | -0.086975 | -0.068665 | -0.064087 | 0.07782 | 121.8155 | 121.7239 | 121.7606 | 0.10071 | 0.086975 | 121.7834 | 121.7697 | -0.068665 | 0.10071 | 0.086975 | 121.7697 | 121.7606 | 121.7834 | -121.8384 | -121.9162
671.9688 | 121.8979 | -0.13275 | 121.6507 | 0.16022 | 0.0072632 | 0.023285 | 0.036316 | -0.0064088 | -0.0023498 | 0.014954 | -0.11902 | -0.12817 | -0.16479 | 121.7834 | 121.6461 | 121.6644 | 121.5546 | 121.6232 | 121.6003 | -0.21057 | -0.032044 | -121.7789 | 0.013732 | 121.9162 | -0.004578 | -0.07782 | -0.050354 | 0.045776 | 121.6873 | 121.756 | 121.7789 | 0.004577 | 0.013732 | 121.7331 | 121.7972 | -0.07782 | 0.004577 | 0.013732 | 121.7972 | 121.7789 | 121.7331 | -121.8155 | -121.8613
673.0156 | 121.907 | -0.17853 | 121.6873 | 0.015259 | 0.010254 | 0.029266 | 0.02948 | -0.0074768 | -0.0046996 | 0.017731 | -0.11902 | -0.09613 | -0.1831 | 121.7697 | 121.6232 | 121.6324 | 121.6507 | 121.6095 | 121.5958 | -0.25635 | -0.004577 | -121.7834 | 0.059509 | 121.9482 | -0.064087 | -0.07782 | -0.091553 | 0.064086 | 121.8292 | 121.788 | 121.8018 | 0.082398 | 0.059509 | 121.7743 | 121.8109 | -0.07782 | 0.082398 | 0.059509 | 121.8109 | 121.8018 | 121.7743 | -121.8704 | -121.9437
673.9688 | 121.9528 | -0.15564 | 121.637 | 0 | 0.0079042 | 0.023499 | 0.040802 | -0.0079042 | -0.0053406 | 0.030548 | -0.041199 | -0.13275 | -0.15564 | 121.9849 | 121.7697 | 121.5912 | 121.5454 | 121.7377 | 121.5866 | -0.25177 | 0 | -121.7697 | 0.11444 | 122.1405 | 0.13275 | -0.09613 | -0.050354 | 0.11444 | 121.7011 | 121.8933 | 121.9254 | 0.022889 | 0.11444 | 121.7422 | 121.7468 | -0.09613 | 0.022889 | 0.11444 | 121.7468 | 121.9254 | 121.7422 | -121.7926 | -121.8887
675.0156 | 121.8979 | -0.17395 | 121.701 | 0.26703 | 0.010254 | 0.030975 | 0.047424 | -0.004059 | -0.005127 | 0.036102 | -0.10071 | -0.1236 | -0.17853 | 121.7697 | 121.6141 | 121.6187 | 121.6599 | 121.582 | 121.6324 | -0.19684 | -0.004578 | -121.8246 | 0.073242 | 121.9437 | -0.086975 | -0.022888 | -0.068665 | 0.07782 | 121.8338 | 121.756 | 121.788 | 0.050354 | 0.073242 | 121.8063 | 121.7926 | -0.022888 | 0.050354 | 0.073242 | 121.7926 | 121.788 | 121.8063 | -121.8796 | -121.8979
675.9688 | 121.9574 | -0.13733 | 121.6736 | 0.053405 | 0.011749 | 0.026703 | 0.043579 | -0.005127 | -0.0038452 | 0.032257 | -0.059509 | -0.19684 | -0.17395 | 121.8613 | 121.7102 | 121.756 | 121.5088 | 121.701 | 121.6232 | -0.21057 | -0.036621 | -121.8704 | 0.07782 | 121.9986 | 0.036621 | -0.073242 | -0.050354 | 0.11444 | 121.6461 | 121.8384 | 121.8475 | -0.059509 | 0.07782 | 121.7606 | 121.8933 | -0.073242 | -0.059509 | 0.07782 | 121.8933 | 121.8475 | 121.7606 | -121.8475 | -121.8842
677.0156 | 121.9162 | -0.1831 | 121.6873 | 0.022888 | 0.013245 | 0.02243 | 0.19824 | -0.0066224 | -0.0025634 | 0.18115 | -0.12817 | -0.10071 | -0.2243 | 121.7743 | 121.6049 | 121.637 | 121.6278 | 121.6324 | 121.6599 | -0.21973 | -0.041199 | -121.788 | 0.054931 | 121.9574 | -0.082398 | -0.036622 | -0.027466 | 0.09613 | 121.8109 | 121.8155 | 121.788 | 0.082397 | 0.054931 | 121.843 | 121.8201 | -0.036622 | 0.082397 | 0.054931 | 121.8201 | 121.788 | 121.843 | -121.9116 | -121.907
677.9688 | 121.9528 | -0.11902 | 121.6782 | 0.34332 | 0.010254 | 0.029694 | 0.032684 | -0.0046998 | -0.0038452 | 0.022644 | -0.050354 | -0.15106 | -0.14648 | 121.8796 | 121.7377 | 121.7651 | 121.5179 | 121.7102 | 121.6553 | -0.21973 | -0.027465 | -121.8292 | 0.068665 | 121.9986 | 0.059509 | -0.10071 | -0.022889 | 0.09613 | 121.637 | 121.8292 | 121.8567 | -0.032043 | 0.068665 | 121.7743 | 121.8842 | -0.10071 | -0.032043 | 0.068665 | 121.8842 | 121.8567 | 121.7743 | -121.8246 | -121.8979
679.0156 | 121.9025 | -0.1831 | 121.7056 | 0.24414 | 0.012177 | 0.027557 | 0.035248 | -0.0038452 | -0.0059814 | 0.023498 | -0.10071 | -0.11902 | -0.18768 | 121.8155 | 121.6507 | 121.6324 | 121.6736 | 121.6095 | 121.6599 | -0.27008 | -0.004578 | -121.8246 | 0.082397 | 121.9986 | -0.054931 | -0.086976 | -0.045776 | 0.086975 | 121.8567 | 121.7926 | 121.8338 | 0.064086 | 0.082397 | 121.843 | 121.8155 | -0.086976 | 0.064086 | 0.082397 | 121.8155 | 121.8338 | 121.843 | -121.8933 | -121.9757
679.9688 | 121.9666 | -0.10529 | 121.701 | 0.34332 | 0.0083314 | 0.02713 | 0.033112 | -0.0049134 | -0.001709 | 0.026489 | -0.064087 | -0.14191 | -0.16022 | 121.8567 | 121.7239 | 121.756 | 121.5866 | 121.701 | 121.669 | -0.23346 | -0.054931 | -121.843 | 0.041199 | 121.962 | 0.022888 | -0.12817 | -0.032044 | 0.09613 | 121.6919 | 121.8063 | 121.8292 | -0.036621 | 0.041199 | 121.7743 | 121.8613 | -0.12817 | -0.036621 | 0.041199 | 121.8613 | 121.8292 | 121.7743 | -121.8613 | -121.9345
680.9844 | 121.9437 | -0.17395 | 121.7148 | 0.022888 | 0.010681 | 0.025848 | 0.038666 | -0.0036316 | -0.0036316 | 0.024567 | -0.11444 | -0.10071 | -0.20142 | 121.8521 | 121.6873 | 121.6965 | 121.6919 | 121.6873 | 121.6827 | -0.26093 | -0.027466 | -121.8155 | 0.059509 | 122.0261 | -0.027466 | -0.086975 | -0.032044 | 0.086975 | 121.8658 | 121.8613 | 121.8613 | 0.073242 | 0.059509 | 121.8567 | 121.8704 | -0.086975 | 0.073242 | 0.059509 | 121.8704 | 121.8613 | 121.8567 | -121.9162 | -121.9757
682.0156 | 121.9299 | -0.20599 | 121.7468 | 0.045776 | 0.010681 | 0.021576 | 0.033112 | -0.0059816 | -0.0057678 | 0.021576 | -0.14648 | -0.10986 | -0.20599 | 121.8338 | 121.6827 | 121.6827 | 121.7148 | 121.6782 | 121.6965 | -0.2655 | 0 | -121.8567 | 0.05951 | 122.0398 | -0.064087 | -0.059509 | -0.050354 | 0.05951 | 121.9208 | 121.8842 | 121.8887 | 0.096131 | 0.05951 | 121.9025 | 121.8887 | -0.059509 | 0.096131 | 0.05951 | 121.8887 | 121.8887 | 121.9025 | -121.9528 | -122.0123
682.9688 | 122.0444 | -0.13733 | 121.7148 | 0.36621 | 0.011322 | 0.028626 | 0.035034 | -0.0025636 | -0.0053406 | 0.027771 | -0.050354 | -0.16479 | -0.15106 | 121.907 | 121.7697 | 121.788 | 121.5637 | 121.7377 | 121.6782 | -0.23346 | -0.013733 | -121.8796 | 0.086975 | 122.0444 | 0.054931 | -0.09613 | -0.036621 | 0.10071 | 121.701 | 121.875 | 121.907 | -0.027466 | 0.086975 | 121.8155 | 121.9254 | -0.09613 | -0.027466 | 0.086975 | 121.9254 | 121.907 | 121.8155 | -121.8658 | -121.9482
684.0156 | 121.9437 | -0.19226 | 121.7148 | 0.22888 | 0.012604 | 0.02713 | 0.049561 | -0.0055542 | -0.0046996 | 0.032043 | -0.10071 | -0.1236 | -0.17853 | 121.8475 | 121.6736 | 121.6736 | 121.7056 | 121.6461 | 121.701 | -0.23346 | 0.013733 | -121.8384 | 0.091553 | 122.0398 | -0.041199 | -0.041198 | -0.013733 | 0.07782 | 121.8979 | 121.8384 | 121.8658 | 0.068665 | 0.091553 | 121.8933 | 121.8658 | -0.041198 | 0.068665 | 0.091553 | 121.8658 | 121.8658 | 121.8933 | -121.8933 | -121.9482
684.9688 | 122.0581 | -0.14648 | 121.7514 | 0.14496 | 0.012604 | 0.028839 | 0.038452 | -0.0042726 | -0.002777 | 0.032898 | -0.068665 | -0.11902 | -0.17395 | 121.9116 | 121.7651 | 121.7972 | 121.637 | 121.7834 | 121.7102 | -0.17395 | -0.027466 | -121.8704 | 0.077819 | 122.0581 | 0.013733 | -0.027466 | -0.041199 | 0.10528 | 121.7834 | 121.9299 | 121.9116 | 0.027465 | 0.077819 | 121.8567 | 121.9437 | -0.027466 | 0.027465 | 0.077819 | 121.9437 | 121.9116 | 121.8567 | -121.9254 | -121.9254
686.0469 | 122.0352 | -0.13275 | 121.7422 | 0.37384 | 0.0089722 | 0.025208 | 0.035889 | -0.0049134 | -0.0036316 | 0.026276 | -0.064087 | -0.14648 | -0.15106 | 121.907 | 121.7422 | 121.7972 | 121.6278 | 121.7651 | 121.6919 | -0.22888 | -0.018311 | -121.8887 | 0.068664 | 122.0398 | 0 | -0.096131 | -0.050354 | 0.086975 | 121.7606 | 121.8979 | 121.875 | -0.013733 | 0.068664 | 121.8246 | 121.9299 | -0.096131 | -0.013733 | 0.068664 | 121.9299 | 121.875 | 121.8246 | -121.8933 | -121.9711
686.9688 | 122.0993 | -0.13733 | 121.7422 | 0.3891 | 0.009613 | 0.027557 | 0.046784 | -0.0057678 | -0.0036316 | 0.035889 | -0.054932 | -0.16022 | -0.15564 | 121.9437 | 121.7697 | 121.8155 | 121.5912 | 121.7743 | 121.669 | -0.21515 | -0.018311 | -121.9025 | 0.082397 | 122.081 | 0.027465 | -0.07782 | -0.073243 | 0.10071 | 121.7285 | 121.9116 | 121.907 | -0.022888 | 0.082397 | 121.8063 | 121.9528 | -0.07782 | -0.022888 | 0.082397 | 121.9528 | 121.907 | 121.8063 | -121.8979 | -121.9574
687.9688 | 122.0856 | -0.13733 | 121.7606 | 0.41199 | 0.01004 | 0.026703 | 0.038025 | -0.0053406 | -0.0040588 | 0.025207 | -0.041199 | -0.17853 | -0.17395 | 121.9437 | 121.8018 | 121.8109 | 121.5958 | 121.7834 | 121.6782 | -0.22888 | -0.036621 | -121.9391 | 0.09613 | 122.081 | 0.041199 | -0.091553 | -0.082397 | 0.13275 | 121.7331 | 121.9208 | 121.9391 | -0.041199 | 0.09613 | 121.8155 | 121.9482 | -0.091553 | -0.041199 | 0.09613 | 121.9482 | 121.9391 | 121.8155 | -121.9345 | -121.9894
688.9688 | 122.1085 | -0.14191 | 121.7514 | 0.3891 | 0.011108 | 0.024994 | 0.036957 | -0.0072632 | -0.0042724 | 0.027771 | -0.054932 | -0.21057 | -0.1831 | 121.962 | 121.788 | 121.8292 | 121.582 | 121.7926 | 121.7148 | -0.25177 | -0.041198 | -121.962 | 0.086975 | 122.1039 | 0.036621 | -0.10986 | -0.036621 | 0.12817 | 121.7239 | 121.9345 | 121.9299 | -0.068664 | 0.086975 | 121.8567 | 121.9711 | -0.10986 | -0.068664 | 0.086975 | 121.9711 | 121.9299 | 121.8567 | -121.9345 | -122.0032
689.9688 | 122.081 | -0.15564 | 121.7514 | 0.37384 | 0.011322 | 0.026062 | 0.047211 | -0.0064088 | -0.0042724 | 0.026062 | -0.082397 | -0.15106 | -0.1831 | 121.9437 | 121.8063 | 121.8201 | 121.6049 | 121.7697 | 121.7148 | -0.25635 | -0.027465 | -121.9025 | 0.073243 | 122.0993 | 0.054931 | -0.10071 | -0.036621 | 0.10071 | 121.7606 | 121.9254 | 121.962 | 0.004578 | 0.073243 | 121.8704 | 121.9757 | -0.10071 | 0.004578 | 0.073243 | 121.9757 | 121.962 | 121.8704 | -121.9345 | -122.0078
690.9844 | 122.1313 | -0.14648 | 121.7834 | 0.11444 | 0.009613 | 0.026062 | 0.046356 | -0.006836 | -0.0049134 | 0.048279 | -0.10071 | -0.15106 | -0.16022 | 121.9803 | 121.8018 | 121.8338 | 121.669 | 121.8201 | 121.7285 | -0.19684 | -0.013733 | -121.9345 | 0.045776 | 122.1268 | 0.018311 | -0.050354 | -0.054931 | 0.059509 | 121.8155 | 121.9666 | 121.9482 | -0.004578 | 0.045776 | 121.875 | 121.9803 | -0.050354 | -0.004578 | 0.045776 | 121.9803 | 121.9482 | 121.875 | -121.9437 | -121.9803
692.0156 | 122.0078 | -0.21515 | 121.788 | 0.061035 | 0.011749 | 0.025848 | 0.040802 | -0.0079042 | -0.0057678 | 0.023712 | -0.13275 | -0.11444 | -0.21515 | 121.8796 | 121.7148 | 121.7148 | 121.7972 | 121.7194 | 121.756 | -0.30212 | 0 | -121.9025 | 0.082398 | 122.0947 | -0.073242 | -0.086975 | -0.032044 | 0.082398 | 122.0123 | 121.9345 | 121.9299 | 0.10071 | 0.082398 | 121.9711 | 121.9299 | -0.086975 | 0.10071 | 0.082398 | 121.9299 | 121.9299 | 121.9711 | -122.0032 | -122.0901
692.9688 | 122.1039 | -0.15564 | 121.788 | 0.15259 | 0.0091858 | 0.026276 | 0.037384 | -0.006836 | -0.0019226 | 0.028625 | -0.054932 | -0.20142 | -0.20142 | 121.9849 | 121.8246 | 121.8658 | 121.5958 | 121.8109 | 121.7422 | -0.25635 | -0.045776 | -121.9894 | 0.10071 | 122.1405 | 0.036621 | -0.10071 | -0.045776 | 0.14648 | 121.7514 | 121.9666 | 121.9803 | -0.045776 | 0.10071 | 121.8979 | 122.0215 | -0.10071 | -0.045776 | 0.10071 | 122.0215 | 121.9803 | 121.8979 | -121.9894 | -122.0444
694.0156 | 121.9666 | -0.21057 | 121.8063 | -0.038147 | 0.011963 | 0.025848 | 0.10873 | -0.005127 | -0.0029906 | 0.096985 | -0.15564 | -0.11902 | -0.20142 | 121.8704 | 121.6827 | 121.7148 | 121.8292 | 121.7056 | 121.7789 | -0.27008 | 0.009155 | -121.9254 | 0.054931 | 122.081 | -0.1236 | -0.05951 | -0.027465 | 0.045776 | 122.0398 | 121.9162 | 121.8933 | 0.091552 | 0.054931 | 121.9894 | 121.9254 | -0.05951 | 0.091552 | 0.054931 | 121.9254 | 121.8933 | 121.9894 | -122.0078 | -122.0764
694.9688 | 122.0901 | -0.24261 | 121.7239 | 0.26703 | 0.01239 | 0.026703 | 0.039093 | -0.0072632 | -0.0038452 | 0.032043 | -0.11444 | -0.14191 | -0.19226 | 121.9254 | 121.7789 | 121.7697 | 121.5729 | 121.6095 | 121.6461 | -0.24719 | 0.050354 | -121.8658 | 0.12817 | 122.168 | 0.054932 | -0.004577 | -0.07782 | 0.07782 | 121.8155 | 121.8521 | 122.0215 | 0.10071 | 0.12817 | 121.8887 | 122.0123 | -0.004577 | 0.10071 | 0.12817 | 122.0123 | 122.0215 | 121.8887 | -121.9162 | -121.9711
696.0156 | 121.9894 | -0.19684 | 121.8475 | -0.51117 | 0.010681 | 0.029266 | 0.049988 | -0.004059 | -0.0042724 | 0.038025 | -0.19226 | -0.1236 | -0.20142 | 121.8842 | 121.7056 | 121.7331 | 121.7789 | 121.6827 | 121.7926 | -0.29755 | -0.004578 | -121.9711 | 0.004577 | 122.081 | -0.14191 | -0.10071 | -0.054931 | 0.009155 | 121.9757 | 121.8796 | 121.9025 | 0.073242 | 0.004577 | 121.9894 | 121.9299 | -0.10071 | 0.073242 | 0.004577 | 121.9299 | 121.9025 | 121.9894 | -122.0489 | -122.1451
696.9688 | 115.9744 | -0.18768 | 115.6769 | 0.36621 | 0.011749 | 0.027985 | 6.9417 | 0 | 0.0008546 | 7.015 | -0.12817 | -0.10071 | -0.18768 | 75.4303 | 62.2055 | 75.1602 | 75.2197 | 75.3067 | 91.951 | 8.9035 | 0 | -115.7776 | 0.059509 | 75.618 | -53.4714 | 9.0912 | -23.7259 | 0.059509 | 75.4074 | 75.4944 | 62.3932 | 0.086975 | 0.059509 | 92.1387 | 75.3479 | 9.0912 | 0.086975 | 0.059509 | 75.3479 | 62.3932 | 92.1387 | -115.8646 | -106.7734
697.9688 | 121.3806 | -0.17853 | 121.0968 | 0.40436 | 0.011749 | 0.026276 | 0.027557 | -0.0014954 | 0 | 0.019867 | -0.11444 | -0.15106 | -0.20142 | 116.8076 | 116.7435 | 116.2445 | 115.5121 | 116.0248 | 121.0785 | -0.2655 | -0.022888 | -121.2479 | 0.064087 | 116.9861 | -4.3533 | -0.086975 | -0.018311 | 0.086975 | 115.6906 | 116.2033 | 116.922 | 0.027466 | 0.064087 | 121.257 | 116.423 | -0.086975 | 0.027466 | 0.064087 | 116.423 | 116.922 | 121.257 | -121.2982 | -121.3623
698.9688 | 121.5042 | -0.16937 | 121.2524 | 0.4425 | 0.01239 | 0.031189 | 0.022217 | 0.034607 | 0.033112 | 0.084381 | -0.10986 | -0.1236 | -0.19684 | 54.0985 | 53.801 | 54.0665 | 53.8971 | 53.9612 | 121.2524 | -0.26093 | -0.027465 | -121.376 | 0.05951 | 54.2679 | -67.4515 | -0.091552 | 0 | 0.086975 | 54.0665 | 54.1306 | 53.9703 | 0.045777 | 0.05951 | 121.4218 | 54.2358 | -0.091552 | 0.045777 | 0.05951 | 54.2358 | 53.9703 | 121.4218 | -121.4493 | -121.5134
699.9688 | 121.6415 | -0.13733 | 121.2982 | 0.43488 | 0.011108 | 0.02478 | 0.02243 | 0.061096 | 0.060883 | 0.14206 | -0.059509 | -0.13733 | -0.16937 | 5.5435 | 5.5023 | 5.5664 | 5.3741 | 5.7175 | 121.2708 | -0.22888 | -0.032044 | -121.4355 | 0.07782 | 5.6808 | -115.7959 | -0.091553 | -0.027466 | 0.10986 | 5.5115 | 5.8548 | 5.6396 | 0 | 0.07782 | 121.4081 | 5.7037 | -0.091553 | 0 | 0.07782 | 5.7037 | 5.6396 | 121.4081 | -121.4676 | -121.5271
700.9688 | 121.7148 | -0.14191 | 121.3394 | 0.007629 | 0.010895 | 0.022858 | 0.019653 | 0.057037 | 0.060242 | 0.14014 | -0.041199 | -0.13275 | -0.15106 | 6.3217 | 6.2805 | 6.1249 | 6.3538 | 6.1432 | 121.2845 | -0.24719 | -0.009155 | -121.4722 | 0.10071 | 6.4636 | -115.0589 | -0.10528 | -0.054932 | 0.10986 | 6.4957 | 6.2851 | 6.4224 | 0.009156 | 0.10071 | 121.4264 | 6.2668 | -0.10528 | 0.009156 | 0.10071 | 6.2668 | 6.4224 | 121.4264 | -121.4905 | -121.5866
701.9688 | 121.6599 | -0.17395 | 121.4264 | 0.39673 | 0.015167 | 0.027344 | 0.039093 | 0.058105 | 0.057678 | 0.15189 | -0.12817 | -0.1236 | -0.21057 | 5.2917 | 5.2414 | 5.2826 | 5.1636 | 7.0496 | 121.3577 | -0.23804 | -0.036621 | -121.55 | 0.045776 | 5.4657 | -116.185 | -0.064087 | -0.068665 | 0.082397 | 5.3375 | 7.2235 | 5.4153 | 0.050354 | 0.045776 | 121.5317 | 5.4565 | -0.064087 | 0.050354 | 0.045776 | 5.4565 | 5.4153 | 121.5317 | -121.637 | -121.6644
703.0156 | 121.701 | -0.21515 | 121.4218 | 0.045776 | 0.011322 | 0.028198 | 0.039093 | 0.04187 | 0.043366 | 0.12326 | -0.14191 | -0.10529 | -0.21057 | 34.7809 | 34.7168 | 34.8816 | 34.8907 | 43.6707 | 121.4264 | -0.2655 | 0.004578 | -121.5271 | 0.073242 | 34.996 | -86.705 | -0.050354 | 0.004578 | 0.068664 | 35.1059 | 43.8858 | 34.9319 | 0.10986 | 0.073242 | 121.6415 | 35.0967 | -0.050354 | 0.10986 | 0.073242 | 35.0967 | 34.9319 | 121.6415 | -121.6324 | -121.6873
703.9688 | 121.6461 | -0.19226 | 121.4859 | 0.32806 | 0.012604 | 0.028839 | 0.036316 | 0.060028 | 0.059601 | 0.15338 | -0.14648 | -0.11444 | -0.21515 | 6.6376 | 6.7886 | 6.7017 | 6.6605 | 19.9539 | 121.4722 | -0.2655 | -0.022888 | -121.6003 | 0.045777 | 6.8298 | -114.6973 | -0.073242 | -0.013733 | 0.068665 | 6.8527 | 20.1462 | 6.9809 | 0.07782 | 0.045777 | 121.6644 | 6.8939 | -0.073242 | 0.07782 | 0.045777 | 6.8939 | 6.9809 | 121.6644 | -121.701 | -121.7514
705.0156 | 121.7926 | -0.15564 | 121.4767 | -3.7231 | 0.012177 | 0.027344 | 0.1004 | 0.055328 | 0.056183 | 0.21918 | -0.11444 | -0.16022 | -0.1831 | 8.8806 | 8.8669 | 8.9172 | 8.8028 | 90.1337 | 121.4539 | -0.2243 | -0.027465 | -121.637 | 0.041199 | 9.0363 | -112.6099 | -0.068664 | -0.022889 | 0.068664 | 8.9584 | 90.2893 | 9.0225 | -0.004577 | 0.041199 | 121.6095 | 9.0729 | -0.068664 | -0.004577 | 0.041199 | 9.0729 | 9.0225 | 121.6095 | -121.6599 | -121.7011
705.9688 | 121.8155 | -0.16937 | 121.4996 | 0.22888 | 0.0098268 | 0.025208 | 0.12518 | 0.04892 | 0.051056 | 0.22324 | -0.059509 | -0.21057 | -0.21515 | 25.4883 | 25.3967 | 25.5249 | 25.2411 | 114.537 | 121.4539 | -0.22888 | -0.045776 | -121.7102 | 0.10986 | 25.6577 | -96.1029 | -0.059509 | -0.045777 | 0.15564 | 25.4105 | 114.7064 | 25.5661 | -0.041198 | 0.10986 | 121.6232 | 25.6943 | -0.059509 | -0.041198 | 0.10986 | 25.6943 | 25.5661 | 121.6232 | -121.7148 | -121.7285
707.0156 | 121.7285 | -0.19226 | 121.5775 | 0 | 0.011536 | 0.024994 | 0.028626 | 0.059174 | 0.060669 | 0.14612 | -0.15564 | -0.064087 | -0.17395 | 3.3737 | 3.3783 | 3.3737 | 3.4927 | 5.0858 | 121.5088 | -0.27466 | 0.018311 | -121.6415 | 0.036621 | 3.566 | -118.1992 | -0.082397 | -0.068665 | 0.01831 | 3.685 | 5.278 | 3.5706 | 0.12817 | 0.036621 | 121.701 | 3.566 | -0.082397 | 0.12817 | 0.036621 | 3.566 | 3.5706 | 121.701 | -121.7514 | -121.8521
707.9688 | 121.7194 | -0.20142 | 121.5546 | 0.27466 | 0.013031 | 0.022858 | 0.34564 | 0.059814 | 0.059387 | 0.4595 | -0.16937 | -0.10529 | -0.2243 | 9.1919 | 9.1599 | 9.1965 | 9.2789 | 88.9893 | 121.4996 | -0.25635 | -0.022888 | -121.6599 | 0.032043 | 9.3933 | -112.3947 | -0.054932 | -0.054931 | 0.054931 | 9.4803 | 89.1907 | 9.3613 | 0.09613 | 0.032043 | 121.701 | 9.3979 | -0.054932 | 0.09613 | 0.032043 | 9.3979 | 9.3613 | 121.701 | -121.7789 | -121.8109
709.0156 | 121.8658 | -0.16937 | 121.4859 | 0.11444 | 0.010468 | 0.026917 | 1.1371 | 0.029694 | 0.02948 | 1.2044 | -0.059509 | -0.16479 | -0.16937 | 59.5413 | 59.4269 | 59.5184 | 59.2163 | 111.5387 | 121.3669 | -0.16479 | 0 | -121.6507 | 0.10986 | 59.7107 | -62.059 | 0.004578 | -0.11902 | 0.10986 | 59.3857 | 111.7081 | 59.5963 | 0.004578 | 0.10986 | 121.5363 | 59.6878 | 0.004578 | 0.004578 | 0.10986 | 59.6878 | 59.5963 | 121.5363 | -121.6553 | -121.6507
709.9688 | 121.7834 | -0.20142 | 121.5225 | 0.43488 | 0.010681 | 0.026062 | 0.4328 | 0.035248 | 0.034607 | 0.50009 | -0.15564 | -0.14648 | -0.22888 | 51.9745 | 51.86 | 52.0065 | 51.8921 | 108.6227 | 121.4539 | -0.24719 | -0.027466 | -121.669 | 0.045776 | 52.1759 | -69.6625 | -0.045776 | -0.068665 | 0.073242 | 52.0935 | 108.8242 | 52.0615 | 0.054932 | 0.045776 | 121.6553 | 52.2079 | -0.045776 | 0.054932 | 0.045776 | 52.2079 | 52.0615 | 121.6553 | -121.7514 | -121.7697
711.0156 | 121.8796 | -0.17853 | 121.5408 | -2.0142 | 0.011536 | 0.030548 | 0.031403 | 0.0072632 | 0.0012818 | 0.020508 | -0.26093 | -0.20599 | -0.2243 | 114.6378 | 115.0131 | 110.5179 | 96.4233 | 90.5777 | 121.4951 | -0.23346 | -0.045776 | -121.7468 | -0.082397 | 114.8163 | -6.5277 | -0.054931 | -0.045777 | -0.036621 | 96.6019 | 90.7562 | 115.1917 | -0.027466 | -0.082397 | 121.6736 | 110.6964 | -0.054931 | -0.027466 | -0.082397 | 110.6964 | 115.1917 | 121.6736 | -121.7651 | -121.7743
711.9688 | 121.8475 | -0.21973 | 121.55 | 0.022888 | 0.01004 | 0.030121 | 0.030975 | 0.010681 | 0.013031 | 0.051269 | -0.13733 | -0.15564 | -0.23346 | 91.1133 | 90.2893 | 89.1037 | 90.097 | 91.0995 | 121.5408 | -0.27466 | -0.013732 | -121.7056 | 0.082398 | 91.333 | -31.2607 | -0.054931 | -0.009155 | 0.09613 | 90.3168 | 91.3193 | 90.509 | 0.064087 | 0.082398 | 121.7606 | 89.3234 | -0.054931 | 0.064087 | 0.082398 | 89.3234 | 90.509 | 121.7606 | -121.7834 | -121.8246
712.9688 | 121.5134 | -0.23346 | 121.6644 | 0.14496 | 0.011322 | 0.029053 | 0.029694 | 0.0021362 | -0.0025634 | 0.02179 | -0.13733 | -0.16937 | -0.26093 | 115.9515 | 115.8051 | 115.8005 | 115.7913 | 115.5945 | 121.55 | -0.32959 | -0.027466 | -121.8338 | 0.09613 | 116.185 | -5.8594 | -0.096131 | -0.11444 | 0.1236 | 116.0248 | 115.8279 | 116.0385 | 0.064086 | 0.09613 | 121.7834 | 116.0339 | -0.096131 | 0.064086 | 0.09613 | 116.0339 | 116.0385 | 121.7834 | -121.9254 | -121.994
714.0156 | 121.3028 | -0.1831 | 120.9869 | 0.22888 | 0.0098268 | 0.02243 | 0.01239 | 0.02948 | 0.033325 | 0.075836 | -0.13275 | -0.15106 | -0.18768 | 58.3099 | 58.2092 | 58.2092 | 50.5142 | -0.07782 | 120.9686 | -0.27466 | -0.004578 | -121.138 | 0.050354 | 58.493 | -62.7777 | -0.091553 | -0.01831 | 0.054932 | 50.6973 | 0.10528 | 58.3923 | 0.032043 | 0.050354 | 121.1517 | 58.3923 | -0.091553 | 0.032043 | 0.050354 | 58.3923 | 58.3923 | 121.1517 | -121.1746 | -121.2616
714.9688 | 121.3577 | -0.21057 | 121.1929 | 0.34332 | 0.009613 | 0.027985 | 0.02243 | 0.053833 | 0.055969 | 0.12476 | -0.17853 | -0.1236 | -0.22888 | 14.9551 | 14.8865 | 15.0146 | 1.5656 | -0.16937 | 121.138 | -0.28839 | -0.018311 | -121.3165 | 0.032043 | 15.1657 | -106.3065 | -0.07782 | -0.054932 | 0.050354 | 1.7761 | 0.041198 | 15.097 | 0.086975 | 0.032043 | 121.3486 | 15.2252 | -0.07782 | 0.086975 | 0.032043 | 15.2252 | 15.097 | 121.3486 | -121.4218 | -121.4813
716.0156 | 121.5363 | -0.16479 | 121.2158 | 0.27466 | 0.012604 | 0.021576 | 0.013245 | 0.055756 | 0.057251 | 0.12454 | -0.14648 | -0.21057 | -0.20599 | 13.6826 | 13.6414 | 13.9206 | 0.64087 | -0.036621 | 121.1929 | -0.26093 | -0.041199 | -121.4264 | 0.018311 | 13.8474 | -107.5745 | -0.09613 | -0.022888 | 0.05951 | 0.80566 | 0.12817 | 13.8062 | -0.045776 | 0.018311 | 121.3577 | 14.0854 | -0.09613 | -0.045776 | 0.018311 | 14.0854 | 13.8062 | 121.3577 | -121.4218 | -121.4767
716.9688 | 121.5179 | -0.2243 | 121.3028 | 0.2594 | 0.01239 | 0.024994 | 0.019653 | 0.055542 | 0.055756 | 0.12924 | -0.14191 | -0.07782 | -0.18768 | 11.6913 | 11.6089 | 11.998 | 0.55389 | -0.11444 | 121.2936 | -0.28839 | 0.036621 | -121.3806 | 0.082397 | 11.9156 | -109.6939 | -0.064087 | -0.009155 | 0.045776 | 0.7782 | 0.10986 | 11.8332 | 0.14648 | 0.082397 | 121.5179 | 12.2223 | -0.064087 | 0.14648 | 0.082397 | 12.2223 | 11.8332 | 121.5179 | -121.4905 | -121.5912
718.0156 | 121.6141 | -0.16022 | 121.3211 | 0.32806 | 0.009613 | 0.028198 | 0.017944 | 0.056824 | 0.057892 | 0.13458 | -0.07782 | -0.17395 | -0.16937 | 11.2427 | 11.2061 | 16.4291 | 0.2655 | -0.045776 | 121.2936 | -0.24719 | -0.009156 | -121.4951 | 0.082397 | 11.4029 | -110.1151 | -0.086975 | -0.027466 | 0.091553 | 0.42572 | 0.11444 | 11.3663 | -0.013733 | 0.082397 | 121.4539 | 16.5894 | -0.086975 | -0.013733 | 0.082397 | 16.5894 | 11.3663 | 121.4539 | -121.4905 | -121.5683
718.9688 | 121.5408 | -0.23804 | 121.3623 | 0.26703 | 0.011536 | 0.025848 | 0.074555 | 0.054474 | 0.056183 | 0.18137 | -0.17853 | -0.16937 | -0.24261 | 12.822 | 12.7396 | 118.1763 | 0.40741 | -0.14648 | 121.2845 | -0.31586 | -0.004578 | -121.5317 | 0.059509 | 13.06 | -108.6227 | -0.07782 | -0.07782 | 0.064087 | 0.64545 | 0.091553 | 12.9776 | 0.068664 | 0.059509 | 121.5225 | 118.4143 | -0.07782 | 0.068664 | 0.059509 | 118.4143 | 12.9776 | 121.5225 | -121.6049 | -121.6782
720.0156 | 121.6415 | -0.19684 | 121.3486 | 0.32043 | 0.010254 | 0.024567 | 0.072846 | 0.056396 | 0.057037 | 0.18713 | -0.10986 | -0.21057 | -0.21057 | 12.2452 | 12.2086 | 118.1351 | 0.32959 | -0.045776 | 121.2982 | -0.2655 | -0.013733 | -121.5591 | 0.086975 | 12.442 | -109.14 | -0.068665 | -0.050354 | 0.10071 | 0.52643 | 0.15106 | 12.4054 | -0.013733 | 0.086975 | 121.4951 | 118.3319 | -0.068665 | -0.013733 | 0.086975 | 118.3319 | 12.4054 | 121.4951 | -121.5591 | -121.6141
720.9688 | 121.637 | -0.24261 | 121.3943 | -0.022889 | 0.011108 | 0.02243 | 0.089508 | 0.05426 | 0.05661 | 0.19931 | -0.059509 | -0.14191 | -0.21515 | 12.0117 | 11.9293 | 119.2703 | 0.58136 | -0.13733 | 121.3669 | -0.30212 | 0.027466 | -121.5363 | 0.18311 | 12.2543 | -109.465 | -0.059509 | -0.027466 | 0.15564 | 0.82398 | 0.10529 | 12.1719 | 0.10071 | 0.18311 | 121.6095 | 119.5129 | -0.059509 | 0.10071 | 0.18311 | 119.5129 | 12.1719 | 121.6095 | -121.6095 | -121.6965
722.0156 | 121.6782 | -0.23346 | 121.3486 | 0.28992 | 0.0074768 | 0.025848 | 0.77225 | 0.030762 | 0.032043 | 0.84189 | -0.17853 | -0.20599 | -0.23804 | 52.7893 | 52.6657 | 114.9307 | 1.6708 | 0.009155 | 121.257 | -0.23804 | -0.004578 | -121.5546 | 0.054931 | 53.0228 | -68.6829 | -0.004578 | -0.091553 | 0.059509 | 1.9043 | 0.24261 | 52.8992 | 0.027465 | 0.054931 | 121.4905 | 115.1642 | -0.004578 | 0.027465 | 0.054931 | 115.1642 | 52.8992 | 121.4905 | -121.5866 | -121.5866
722.9688 | 121.5683 | -0.25177 | 121.3623 | -0.022889 | 0.009613 | 0.023712 | 1.1687 | 0.034607 | 0.034393 | 1.2463 | -0.24261 | -0.17395 | -0.28381 | 50.4456 | 50.3311 | 115.3198 | 2.3026 | -0.004578 | 121.2433 | -0.25635 | -0.032043 | -121.5363 | 0.009155 | 50.6973 | -71.0312 | -0.004578 | -0.11902 | 0.041198 | 2.5543 | 0.24719 | 50.5829 | 0.07782 | 0.009155 | 121.4951 | 115.5716 | -0.004578 | 0.07782 | 0.009155 | 115.5716 | 50.5829 | 121.4951 | -121.6461 | -121.6187
724.0156 | 121.6965 | -0.2243 | 121.3303 | 0.14496 | 0.009613 | 0.026276 | 1.5421 | 0.029694 | 0.030548 | 1.6116 | -0.14191 | -0.27466 | -0.27924 | 59.8572 | 59.7015 | 115.2191 | 2.4994 | 0.14191 | 121.1655 | -0.1831 | -0.054932 | -121.6049 | 0.082397 | 60.0815 | -61.6287 | 0.041199 | -0.16479 | 0.13733 | 2.7237 | 0.36621 | 59.9258 | -0.050354 | 0.082397 | 121.3898 | 115.4434 | 0.041199 | -0.050354 | 0.082397 | 115.4434 | 59.9258 | 121.3898 | -121.6095 | -121.5134
724.9688 | 121.7102 | -0.23346 | 121.3577 | -0.11444 | 0.0091858 | 0.02478 | 1.6754 | 0.016876 | 0.021362 | 1.7239 | -0.16022 | -0.25635 | -0.25177 | 76.886 | 76.8173 | 116.1713 | 2.6093 | 0.1831 | 121.17 | -0.16937 | -0.018311 | -121.6141 | 0.073242 | 77.1194 | -44.5404 | 0.064086 | -0.18768 | 0.091553 | 2.8427 | 0.41656 | 77.0508 | -0.022889 | 0.073242 | 121.4035 | 116.4047 | 0.064086 | -0.022889 | 0.073242 | 116.4047 | 77.0508 | 121.4035 | -121.6095 | -121.5271
726.0156 | 121.7651 | -0.21973 | 121.3852 | 0.35095 | 0.0079042 | 0.02478 | 0.90704 | 0.019867 | 0.025208 | 0.95853 | -0.16479 | -0.21515 | -0.2243 | 71.8872 | 71.6125 | 118.3731 | 1.4191 | 0.018311 | 121.2662 | -0.1831 | -0.004577 | -121.6003 | 0.054932 | 72.1069 | -49.7726 | 0.036622 | -0.11902 | 0.059509 | 1.6388 | 0.23804 | 71.8323 | 0.004578 | 0.054932 | 121.4859 | 118.5928 | 0.036622 | 0.004578 | 0.054932 | 118.5928 | 71.8323 | 121.4859 | -121.6095 | -121.5683
727.4062 | 121.7743 | -0.23804 | 121.376 | 2.4719 | 0.010681 | 0.027344 | 1.2115 | 0.022858 | 0.023926 | 1.2732 | -0.12817 | -0.24719 | -0.23346 | 70.134 | 69.4839 | 117.6453 | 1.8082 | 0.12817 | 121.2296 | -0.2243 | 0.004578 | -121.6232 | 0.10986 | 70.372 | -51.8921 | 0.013733 | -0.14648 | 0.10528 | 2.0462 | 0.36621 | 69.722 | -0.009155 | 0.10986 | 121.4676 | 117.8833 | 0.013733 | -0.009155 | 0.10986 | 117.8833 | 69.722 | 121.4676 | -121.6095 | -121.6003
727.9688 | 121.8109 | -0.28381 | 121.3577 | 0.007629 | 0.01004 | 0.029053 | 1.7509 | 0.010467 | 0.012817 | 1.6267 | -0.21973 | -0.21057 | -0.30212 | 87.4695 | 87.1033 | 115.9927 | 2.6871 | 0.12817 | 121.1609 | -0.15564 | -0.018311 | -121.5683 | 0.064086 | 87.7533 | -34.2545 | 0.12817 | -0.19684 | 0.082397 | 2.9709 | 0.41199 | 87.3871 | 0.073242 | 0.064086 | 121.4447 | 116.2766 | 0.12817 | 0.073242 | 0.064086 | 116.2766 | 87.3871 | 121.4447 | -121.6599 | -121.5134
728.9688 | 121.6553 | -0.23804 | 121.3531 | -0.083923 | 0.011322 | 0.023499 | 0.80707 | 0.016235 | 0.01709 | 0.84616 | -0.16022 | -0.2243 | -0.25177 | 81.9214 | 81.9397 | 119.2291 | 1.1627 | 0.004578 | 121.2936 | -0.27466 | -0.013733 | -121.5775 | 0.07782 | 82.1594 | -39.4135 | -0.036621 | -0.059509 | 0.091553 | 1.4008 | 0.24261 | 82.1777 | 0.013733 | 0.07782 | 121.5317 | 119.4672 | -0.036621 | 0.013733 | 0.07782 | 119.4672 | 82.1777 | 121.5317 | -121.6049 | -121.6278
729.9688 | 121.6873 | -0.25635 | 121.3898 | 0.053405 | 0.008545 | 0.02478 | 0.71094 | 0.0055542 | 0.006195 | 0.70453 | -0.16022 | -0.24719 | -0.25635 | 97.4854 | 97.3618 | 119.4855 | 0.99335 | 0.013733 | 121.2936 | -0.27008 | 0 | -121.637 | 0.096131 | 97.7417 | -24.028 | -0.013733 | -0.096131 | 0.096131 | 1.2497 | 0.27008 | 97.6181 | 0.009156 | 0.096131 | 121.55 | 119.7418 | -0.013733 | 0.009156 | 0.096131 | 119.7418 | 97.6181 | 121.55 | -121.6461 | -121.6599
730.9688 | 121.637 | -0.24719 | 121.2296 | 0.083923 | 0.0091858 | 0.02478 | 4.9059 | 0.0098266 | 0.011536 | 4.9439 | -0.15106 | -0.26093 | -0.2655 | 91.7999 | 91.6672 | 112.5366 | 12.323 | 0.60425 | 120.7581 | 0.15564 | -0.018311 | -121.4905 | 0.09613 | 92.0471 | -29.5624 | 0.40283 | -0.4715 | 0.11444 | 12.5702 | 0.85144 | 91.9144 | -0.013733 | 0.09613 | 121.0052 | 112.7838 | 0.40283 | -0.013733 | 0.09613 | 112.7838 | 91.9144 | 121.0052 | -121.4951 | -121.0739
732.0156 | 121.8109 | -0.24719 | 121.4172 | 0.41199 | 0.011749 | 0.02713 | 0.036743 | 0.045288 | 0.045288 | 0.12476 | -0.17395 | -0.23804 | -0.27466 | 31.636 | 31.5262 | 31.6498 | -0.28839 | -0.1236 | 121.376 | -0.32501 | -0.027466 | -121.6553 | 0.073242 | 31.8832 | -89.8911 | -0.07782 | -0.041198 | 0.10071 | -0.041199 | 0.1236 | 31.7734 | 0.009155 | 0.073242 | 121.6232 | 31.897 | -0.07782 | 0.009155 | 0.073242 | 31.897 | 31.7734 | 121.6232 | -121.6919 | -121.7422
732.9688 | 121.8613 | -0.23346 | 121.4355 | -0.045776 | 0.0076904 | 0.021149 | 0.03183 | 0.053619 | 0.055756 | 0.14954 | -0.14191 | -0.24719 | -0.24719 | 11.055 | 11.1008 | 11.2564 | -0.29755 | -0.032043 | 121.376 | -0.3479 | -0.013733 | -121.6827 | 0.091552 | 11.2885 | -110.3348 | -0.11444 | -0.059509 | 0.10528 | -0.064087 | 0.20142 | 11.3342 | -0.013733 | 0.091552 | 121.6095 | 11.4899 | -0.11444 | -0.013733 | 0.091552 | 11.4899 | 11.3342 | 121.6095 | -121.6827 | -121.7834
734.0312 | 121.788 | -0.23804 | 121.4905 | 0.18311 | 0.01239 | 0.027771 | 0.036957 | 0.056824 | 0.057892 | 0.14911 | -0.086975 | -0.17853 | -0.21515 | 9.7458 | 9.6588 | 9.7137 | -0.10071 | -0.13733 | 121.4584 | -0.29755 | 0.022888 | -121.669 | 0.15106 | 9.9838 | -111.8317 | -0.059509 | -0.032044 | 0.12817 | 0.13733 | 0.10071 | 9.8969 | 0.059509 | 0.15106 | 121.6965 | 9.9518 | -0.059509 | 0.059509 | 0.15106 | 9.9518 | 9.8969 | 121.6965 | -121.7056 | -121.788
735.5469 | 121.8521 | -0.27466 | 121.4539 | 0.47302 | 0.0089722 | 0.025421 | 0.036316 | 0.056824 | 0.05896 | 0.14996 | -0.20599 | -0.23804 | -0.3067 | 9.0134 | 8.9767 | 9.0363 | -0.24261 | -0.16022 | 121.4401 | -0.33875 | -0.032044 | -121.6919 | 0.068664 | 9.288 | -112.4771 | -0.064087 | -0.013732 | 0.10071 | 0.032043 | 0.11444 | 9.2514 | 0.036621 | 0.068664 | 121.7148 | 9.3109 | -0.064087 | 0.036621 | 0.068664 | 9.3109 | 9.2514 | 121.7148 | -121.7606 | -121.7926
736.2188 | 121.7697 | -0.26093 | 121.5134 | -0.015259 | 0.01004 | 0.023071 | 0.032257 | 0.056183 | 0.059387 | 0.15125 | -0.27924 | -0.21515 | -0.32501 | 8.8028 | 8.7616 | 8.7982 | -0.054932 | -0.21057 | 121.4767 | -0.3479 | -0.064087 | -121.7285 | -0.018311 | 9.0637 | -112.7518 | -0.086975 | -0.036621 | 0.045776 | 0.20599 | 0.050354 | 9.0225 | 0.045776 | -0.018311 | 121.7377 | 9.0591 | -0.086975 | 0.045776 | -0.018311 | 9.0591 | 9.0225 | 121.7377 | -121.8384 | -121.8613
737.5625 | 121.8018 | -0.33875 | 121.4905 | 0.045776 | 0.0093994 | 0.025848 | 0.035889 | 0.057892 | 0.05896 | 0.15125 | -0.2655 | -0.2655 | -0.33417 | 8.3176 | 8.2809 | 8.3176 | -0.10071 | -0.22888 | 121.463 | -0.40741 | 0.004578 | -121.756 | 0.073242 | 8.6563 | -113.2095 | -0.068665 | -0.027466 | 0.068664 | 0.23804 | 0.10986 | 8.6197 | 0.073242 | 0.073242 | 121.8018 | 8.6563 | -0.068665 | 0.073242 | 0.073242 | 8.6563 | 8.6197 | 121.8018 | -121.8246 | -121.8979
738.0625 | 121.8704 | -0.30212 | 121.4127 | 0.3128 | 0.010895 | 0.024994 | 0.027985 | 0.057037 | 0.059601 | 0.1506 | -0.23804 | -0.27008 | -0.27924 | 8.2397 | 8.2214 | 8.2809 | -0.23346 | -0.19226 | 121.431 | -0.38452 | 0.022888 | -121.6827 | 0.064087 | 8.5419 | -113.1912 | -0.082397 | 0.01831 | 0.041199 | 0.068665 | 0.10986 | 8.5236 | 0.032043 | 0.064087 | 121.7331 | 8.5831 | -0.082397 | 0.032043 | 0.064087 | 8.5831 | 8.5236 | 121.7331 | -121.6919 | -121.7972
739.9375 | 121.9208 | -0.29755 | 121.4767 | 0.25177 | 0.01004 | 0.025848 | 0.031403 | 0.052978 | 0.058533 | 0.15167 | -0.28839 | -0.34332 | -0.32959 | 7.988 | 7.9514 | 8.0109 | -0.25177 | -0.16937 | 121.4218 | -0.38452 | -0.032044 | -121.8201 | 0.009155 | 8.2855 | -113.5254 | -0.086975 | -0.054932 | 0.041199 | 0.045776 | 0.12817 | 8.2489 | -0.045777 | 0.009155 | 121.7194 | 8.3084 | -0.086975 | -0.045777 | 0.009155 | 8.3084 | 8.2489 | 121.7194 | -121.8063 | -121.8613
740.9844 | 121.9482 | -0.33875 | 121.4447 | 0.4425 | 0.011963 | 0.025421 | 0.03717 | 0.05661 | 0.057037 | 0.15295 | -0.19226 | -0.31128 | -0.3067 | 7.9559 | 7.7225 | 7.8781 | -0.2243 | -0.10529 | 121.3623 | -0.41657 | 0.032043 | -121.756 | 0.14648 | 8.2947 | -113.7222 | -0.07782 | -0.082397 | 0.11444 | 0.11444 | 0.23346 | 8.0612 | 0.027466 | 0.14648 | 121.7011 | 8.2169 | -0.07782 | 0.027466 | 0.14648 | 8.2169 | 8.0612 | 121.7011 | -121.7514 | -121.8613
741.5781 | 121.9528 | -0.3067 | 121.4676 | -0.038147 | 0.0091858 | 0.026703 | 0.033753 | 0.055969 | 0.059814 | 0.15274 | -0.1831 | -0.30212 | -0.3067 | 7.8827 | 8.0978 | 8.107 | -0.58136 | -0.10529 | 121.4401 | -0.39368 | 0 | -121.7697 | 0.1236 | 8.1894 | -113.3698 | -0.086975 | -0.027465 | 0.1236 | -0.27466 | 0.20142 | 8.4045 | 0.004578 | 0.1236 | 121.7468 | 8.4137 | -0.086975 | 0.004578 | 0.1236 | 8.4137 | 8.4045 | 121.7468 | -121.7743 | -121.8613
742.4219 | 121.8201 | -0.33417 | 121.5546 | 0.22888 | 0.011963 | 0.031616 | 0.041016 | 0.059174 | 0.05661 | 0.15103 | -0.25177 | -0.23804 | -0.34332 | 7.988 | 7.9147 | 7.9742 | -0.10071 | -0.27924 | 121.5179 | -0.40741 | -0.009156 | -121.7926 | 0.082397 | 8.3221 | -113.6398 | -0.073243 | -0.036621 | 0.091553 | 0.23346 | 0.054931 | 8.2489 | 0.09613 | 0.082397 | 121.8521 | 8.3084 | -0.073243 | 0.09613 | 0.082397 | 8.3084 | 8.2489 | 121.8521 | -121.8979 | -121.962
746.7188 | 121.8933 | -0.32959 | 121.5729 | 0.5722 | 0.0083314 | 0.027985 | 0.037384 | 0.057251 | 0.057678 | 0.15338 | -0.2655 | -0.2243 | -0.32044 | 7.7408 | 7.7087 | 7.7637 | -0.1236 | -0.25635 | 121.5408 | -0.37537 | 0.009155 | -121.7972 | 0.064087 | 8.0704 | -113.8641 | -0.045776 | -0.032043 | 0.054932 | 0.20599 | 0.073242 | 8.0383 | 0.10529 | 0.064087 | 121.8704 | 8.0933 | -0.045776 | 0.10529 | 0.064087 | 8.0933 | 8.0383 | 121.8704 | -121.8933 | -121.9482
747.1562 | 122.0169 | -0.25635 | 121.5637 | 0.022888 | 0.0091858 | 0.023926 | 0.031189 | 0.057892 | 0.056824 | 0.15039 | -0.16022 | -0.28381 | -0.29755 | 7.9422 | 7.8964 | 7.9605 | -0.21973 | -0.064087 | 121.5088 | -0.33417 | -0.041198 | -121.8475 | 0.096131 | 8.1985 | -113.6673 | -0.077819 | -0.054932 | 0.13733 | 0.036621 | 0.19226 | 8.1528 | -0.027465 | 0.096131 | 121.7651 | 8.2169 | -0.077819 | -0.027465 | 0.096131 | 8.2169 | 8.1528 | 121.7651 | -121.8613 | -121.8979
748.0312 | 121.907 | -0.3067 | 121.6187 | -0.038147 | 0.0081178 | 0.025635 | 0.034393 | 0.054474 | 0.057465 | 0.15274 | -0.24261 | -0.24261 | -0.29755 | 7.8049 | 7.7728 | 7.7866 | -0.07782 | -0.18768 | 121.5408 | -0.37079 | 0.009156 | -121.8613 | 0.064087 | 8.1116 | -113.8458 | -0.064087 | -0.077819 | 0.054931 | 0.22888 | 0.11902 | 8.0795 | 0.064087 | 0.064087 | 121.8475 | 8.0933 | -0.064087 | 0.064087 | 0.064087 | 8.0933 | 8.0795 | 121.8475 | -121.9162 | -121.9894
748.9688 | 121.9894 | -0.24261 | 121.6049 | 0.076294 | 0.0087586 | 0.02243 | 0.030548 | 0.054687 | 0.05661 | 0.15359 | -0.13733 | -0.28381 | -0.27008 | 7.8735 | 7.8461 | 7.8964 | -0.20142 | -0.045776 | 121.5637 | -0.32959 | -0.027466 | -121.8887 | 0.10529 | 8.1162 | -113.7588 | -0.086975 | -0.041198 | 0.13275 | 0.041199 | 0.19684 | 8.0887 | -0.041198 | 0.10529 | 121.8063 | 8.139 | -0.086975 | -0.041198 | 0.10529 | 8.139 | 8.0887 | 121.8063 | -121.875 | -121.9345
750.0156 | 122.0169 | -0.29755 | 121.5637 | 0.45013 | 0.0083314 | 0.022644 | 0.035889 | 0.055115 | 0.056397 | 0.15338 | -0.16479 | -0.28839 | -0.27466 | 7.7225 | 7.8918 | 7.9285 | -0.33875 | -0.10986 | 121.4813 | -0.39368 | 0.022888 | -121.8521 | 0.13275 | 8.02 | -113.6719 | -0.096131 | -0.082398 | 0.10986 | -0.041199 | 0.18768 | 8.1894 | 0.009155 | 0.13275 | 121.7789 | 8.226 | -0.096131 | 0.009155 | 0.13275 | 8.226 | 8.1894 | 121.7789 | -121.8384 | -121.9574
750.9688 | 122.0535 | -0.23346 | 121.5866 | 0.099182 | 0.0074768 | 0.025208 | 0.032684 | 0.054047 | 0.060669 | 0.1521 | -0.16937 | -0.25177 | -0.25177 | 7.9102 | 7.8873 | 7.9376 | -0.24719 | -0.054932 | 121.5637 | -0.32501 | -0.018311 | -121.8384 | 0.064086 | 8.1436 | -113.6993 | -0.091553 | -0.022888 | 0.082397 | -0.013733 | 0.17853 | 8.1207 | -0.018311 | 0.064086 | 121.7972 | 8.1711 | -0.091553 | -0.018311 | 0.064086 | 8.1711 | 8.1207 | 121.7972 | -121.8384 | -121.9116
752.0156 | 122.0215 | -0.25635 | 121.5958 | 0.39673 | 0.010468 | 0.02179 | 0.040161 | 0.054047 | 0.060883 | 0.1521 | -0.16022 | -0.28839 | -0.27924 | 7.8781 | 7.814 | 7.901 | -0.29755 | -0.13275 | 121.5179 | -0.33417 | -0.022888 | -121.8842 | 0.096131 | 8.1345 | -113.7817 | -0.077819 | -0.07782 | 0.11902 | -0.041198 | 0.1236 | 8.0704 | -0.032043 | 0.096131 | 121.7743 | 8.1573 | -0.077819 | -0.032043 | 0.096131 | 8.1573 | 8.0704 | 121.7743 | -121.875 | -121.9299
752.9844 | 121.962 | -0.28381 | 121.637 | 1.6785 | 0.01474 | 0.024353 | 0.039948 | 0.057678 | 0.057892 | 0.14996 | -0.10986 | -0.17395 | -0.23804 | 7.8415 | 7.7728 | 7.8094 | -0.14191 | -0.16937 | 121.5912 | -0.37537 | 0.045776 | -121.8109 | 0.17395 | 8.1253 | -113.8641 | -0.091553 | -0.045776 | 0.12817 | 0.14191 | 0.11444 | 8.0566 | 0.10986 | 0.17395 | 121.875 | 8.0933 | -0.091553 | 0.10986 | 0.17395 | 8.0933 | 8.0566 | 121.875 | -121.875 | -122.0123
754.0156 | 121.9437 | -0.40283 | 121.5179 | 0.35095 | 0.014313 | 0.029053 | 0.03653 | 0.057465 | 0.059174 | 0.15295 | -0.36621 | -0.34332 | -0.4303 | 7.5851 | 7.5394 | 7.5989 | -0.27466 | -0.35248 | 121.4951 | -0.48065 | -0.027466 | -121.8613 | 0.036621 | 7.988 | -113.9786 | -0.07782 | -0.022888 | 0.064087 | 0.12817 | 0.050354 | 7.9422 | 0.059509 | 0.036621 | 121.8979 | 8.0017 | -0.07782 | 0.059509 | 0.036621 | 8.0017 | 7.9422 | 121.8979 | -121.9482 | -121.9986
754.9688 | 122.0673 | -0.38452 | 121.5088 | 0.099182 | 0.0074768 | 0.017944 | 0.031189 | 0.054687 | 0.057251 | 0.15274 | -0.30212 | -0.3891 | -0.38452 | 7.6355 | 7.6218 | 7.663 | -0.36163 | -0.17853 | 121.431 | -0.46234 | 0 | -121.8979 | 0.082397 | 8.02 | -113.887 | -0.07782 | -0.07782 | 0.082397 | 0.022888 | 0.20599 | 8.0063 | -0.004578 | 0.082397 | 121.8155 | 8.0475 | -0.07782 | -0.004578 | 0.082397 | 8.0475 | 8.0063 | 121.8155 | -121.8933 | -121.9711
756.0156 | 121.9254 | -0.44403 | 121.5179 | 0.3128 | 0.01004 | 0.025635 | 0.039948 | 0.055756 | 0.058319 | 0.15381 | -0.41657 | -0.37537 | -0.45319 | 7.5348 | 7.4707 | 7.5348 | -0.2243 | -0.39825 | 121.4539 | -0.51727 | -0.009155 | -121.8933 | 0.027466 | 7.9788 | -114.0472 | -0.073242 | -0.064087 | 0.036621 | 0.21973 | 0.045777 | 7.9147 | 0.068665 | 0.027466 | 121.8979 | 7.9788 | -0.073242 | 0.068665 | 0.027466 | 7.9788 | 7.9147 | 121.8979 | -121.9711 | -122.0352
756.9688 | 122.0718 | -0.40283 | 121.5408 | 0.099182 | 0.0098268 | 0.023071 | 0.029907 | 0.052978 | 0.06131 | 0.1506 | -0.3067 | -0.3891 | -0.3891 | 7.6035 | 7.5897 | 7.6447 | -0.33417 | -0.1831 | 121.4722 | -0.46234 | 0.013733 | -121.9299 | 0.09613 | 8.0063 | -113.9511 | -0.059509 | -0.068665 | 0.082397 | 0.068665 | 0.21973 | 7.9926 | 0.013733 | 0.09613 | 121.875 | 8.0475 | -0.059509 | 0.013733 | 0.09613 | 8.0475 | 7.9926 | 121.875 | -121.9299 | -122.0032
757.9844 | 122.0123 | -0.36163 | 121.5637 | 0.16785 | 0.013245 | 0.028198 | 0.038025 | 0.054901 | 0.059601 | 0.15295 | -0.3067 | -0.35706 | -0.44403 | 7.4982 | 7.4524 | 7.4844 | -0.23804 | -0.27924 | 121.5225 | -0.44861 | -0.082398 | -121.9208 | 0.054931 | 7.8598 | -114.1113 | -0.086975 | -0.041199 | 0.13733 | 0.1236 | 0.082397 | 7.814 | 0.004577 | 0.054931 | 121.8842 | 7.8461 | -0.086975 | 0.004577 | 0.054931 | 7.8461 | 7.814 | 121.8842 | -122.0078 | -122.0123
758.9688 | 122.0352 | -0.42572 | 121.5454 | 0.24414 | 0.0076904 | 0.018799 | 0.02948 | 0.055756 | 0.060028 | 0.15424 | -0.48523 | -0.41199 | -0.44861 | 7.402 | 7.3929 | 7.4753 | -0.32959 | -0.28381 | 121.4905 | -0.48523 | -0.022888 | -121.9574 | -0.059509 | 7.8278 | -114.1525 | -0.059509 | -0.054931 | -0.036621 | 0.09613 | 0.14191 | 7.8186 | 0.013733 | -0.059509 | 121.9162 | 7.901 | -0.059509 | 0.013733 | -0.059509 | 7.901 | 7.8186 | 121.9162 | -121.994 | -122.0306
759.9688 | 122.0535 | -0.43945 | 121.5271 | 0.22888 | 0.009613 | 0.021362 | 0.031189 | 0.054687 | 0.057465 | 0.15167 | -0.35248 | -0.37537 | -0.40741 | 7.2922 | 7.2922 | 7.3746 | -0.3479 | -0.31586 | 121.4218 | -0.53101 | 0.032043 | -121.9025 | 0.086975 | 7.7316 | -114.2349 | -0.091553 | -0.10529 | 0.054932 | 0.091553 | 0.1236 | 7.7316 | 0.064087 | 0.086975 | 121.8613 | 7.814 | -0.091553 | 0.064087 | 0.086975 | 7.814 | 7.7316 | 121.8613 | -121.9345 | -122.0581
760.9688 | 122.0718 | -0.38452 | 121.5546 | 0.22125 | 0.0091858 | 0.021149 | 0.032898 | 0.052551 | 0.059174 | 0.15338 | -0.34332 | -0.38452 | -0.4303 | 7.1548 | 7.132 | 7.1915 | -0.31586 | -0.21973 | 121.4859 | -0.45776 | -0.045777 | -121.9391 | 0.041198 | 7.5394 | -114.4226 | -0.073243 | -0.068664 | 0.086975 | 0.068664 | 0.16479 | 7.5165 | 0 | 0.041198 | 121.8704 | 7.576 | -0.073243 | 0 | 0.041198 | 7.576 | 7.5165 | 121.8704 | -121.9849 | -122.0123
762.0156 | 121.9757 | -0.43945 | 121.5912 | 0.27466 | 0.0089722 | 0.025421 | 0.039093 | 0.055115 | 0.057251 | 0.15466 | -0.40283 | -0.36621 | -0.44861 | 6.9534 | 6.8848 | 6.9489 | -0.20142 | -0.37079 | 121.5225 | -0.50354 | -0.009155 | -121.9574 | 0.036621 | 7.3929 | -114.7064 | -0.064087 | -0.068665 | 0.045776 | 0.23804 | 0.068664 | 7.3242 | 0.073242 | 0.036621 | 121.962 | 7.3883 | -0.064087 | 0.073242 | 0.036621 | 7.3883 | 7.3242 | 121.962 | -122.0398 | -122.0947
762.9844 | 122.0535 | -0.42572 | 121.6003 | 0.045776 | 0.012817 | 0.024139 | 0.040802 | 0.057251 | 0.060669 | 0.15317 | -0.33417 | -0.36621 | -0.43488 | 6.958 | 6.926 | 6.958 | -0.24261 | -0.28381 | 121.5363 | -0.51727 | -0.009155 | -121.9666 | 0.091553 | 7.3837 | -114.6744 | -0.091553 | -0.064087 | 0.10071 | 0.1831 | 0.14191 | 7.3517 | 0.059509 | 0.091553 | 121.962 | 7.3837 | -0.091553 | 0.059509 | 0.091553 | 7.3837 | 7.3517 | 121.962 | -122.0352 | -122.1176
764.0156 | 122.0993 | -0.33875 | 121.582 | 0.36621 | 0.0091858 | 0.023285 | 0.035889 | 0.059174 | 0.058319 | 0.15552 | -0.28381 | -0.39825 | -0.39825 | 6.9351 | 6.8985 | 6.9672 | -0.36621 | -0.22888 | 121.5225 | -0.44861 | -0.059509 | -121.9803 | 0.054932 | 7.2739 | -114.6835 | -0.10986 | -0.059509 | 0.11444 | -0.027466 | 0.10986 | 7.2372 | -0.059509 | 0.054932 | 121.8613 | 7.3059 | -0.10986 | -0.059509 | 0.054932 | 7.3059 | 7.2372 | 121.8613 | -121.9803 | -122.0306
764.9688 | 122.0444 | -0.40741 | 121.6095 | -0.061036 | 0.0093994 | 0.02478 | 0.035889 | 0.055969 | 0.05661 | 0.15466 | -0.33875 | -0.37537 | -0.42114 | 6.8527 | 6.8207 | 6.8436 | -0.18768 | -0.28381 | 121.5775 | -0.48065 | -0.013733 | -121.9849 | 0.068665 | 7.2601 | -114.7888 | -0.073242 | -0.032043 | 0.082398 | 0.21973 | 0.1236 | 7.2281 | 0.032044 | 0.068665 | 121.9849 | 7.251 | -0.073242 | 0.032044 | 0.068665 | 7.251 | 7.2281 | 121.9849 | -122.0306 | -122.0901
765.9688 | 122.0901 | -0.37994 | 121.6049 | 0.25177 | 0.0087586 | 0.021362 | 0.032684 | 0.055756 | 0.05896 | 0.15253 | -0.34332 | -0.40283 | -0.38452 | 6.8619 | 6.8481 | 6.8939 | -0.31586 | -0.27008 | 121.5546 | -0.45319 | -0.004577 | -122.0078 | 0.036621 | 7.2418 | -114.7568 | -0.073242 | -0.050354 | 0.041198 | 0.064087 | 0.10986 | 7.2281 | -0.022888 | 0.036621 | 121.9345 | 7.2739 | -0.073242 | -0.022888 | 0.036621 | 7.2739 | 7.2281 | 121.9345 | -121.9894 | -122.0581
766.9844 | 122.0856 | -0.37537 | 121.6415 | -0.030518 | 0.01004 | 0.024994 | 0.034821 | 0.054047 | 0.060028 | 0.15466 | -0.31586 | -0.35706 | -0.39368 | 6.839 | 6.7841 | 6.8207 | -0.2243 | -0.24719 | 121.5775 | -0.48523 | -0.018311 | -121.9986 | 0.059509 | 7.2144 | -114.8575 | -0.10986 | -0.064087 | 0.07782 | 0.15106 | 0.12817 | 7.1594 | 0.01831 | 0.059509 | 121.9528 | 7.196 | -0.10986 | 0.01831 | 0.059509 | 7.196 | 7.1594 | 121.9528 | -122.0352 | -122.1268
767.9844 | 122.0993 | -0.37994 | 121.6095 | -0.038147 | 0.010681 | 0.025208 | 0.035675 | 0.057251 | 0.057251 | 0.15381 | -0.29297 | -0.35706 | -0.39368 | 6.8619 | 6.8253 | 6.8527 | -0.23804 | -0.24261 | 121.5546 | -0.46692 | -0.013733 | -121.9666 | 0.086975 | 7.2418 | -114.7842 | -0.086975 | -0.054932 | 0.10071 | 0.14191 | 0.13733 | 7.2052 | 0.022888 | 0.086975 | 121.9345 | 7.2327 | -0.086975 | 0.022888 | 0.086975 | 7.2327 | 7.2052 | 121.9345 | -122.0032 | -122.0764
768.9688 | 122.1542 | -0.36163 | 121.637 | -0.038147 | 0.0087586 | 0.02179 | 0.033539 | 0.056824 | 0.058533 | 0.15424 | -0.29755 | -0.37537 | -0.38452 | 7.0267 | 6.9809 | 7.0175 | -0.29755 | -0.17395 | 121.582 | -0.43488 | -0.022888 | -122.0123 | 0.064087 | 7.3883 | -114.6561 | -0.073242 | -0.054932 | 0.086975 | 0.064087 | 0.18768 | 7.3425 | -0.013733 | 0.064087 | 121.9437 | 7.3792 | -0.073242 | -0.013733 | 0.064087 | 7.3792 | 7.3425 | 121.9437 | -122.0215 | -122.0718
770.0156 | 122.0261 | -0.37994 | 121.6644 | 0.37384 | 0.012817 | 0.025635 | 0.03952 | 0.058746 | 0.059387 | 0.15509 | -0.37079 | -0.35248 | -0.43945 | 7.0633 | 7.045 | 6.9443 | -0.12817 | -0.36621 | 121.6095 | -0.45319 | -0.059509 | -122.0169 | 0.009155 | 7.4432 | -114.6194 | -0.073242 | -0.054932 | 0.068664 | 0.25177 | 0.013733 | 7.4249 | 0.027466 | 0.009155 | 121.9894 | 7.3242 | -0.073242 | 0.027466 | 0.009155 | 7.3242 | 7.4249 | 121.9894 | -122.1039 | -122.1176
770.9688 | 122.0306 | -0.42114 | 121.6599 | 0.007629 | 0.009613 | 0.022217 | 0.03653 | 0.05661 | 0.058746 | 0.15231 | -0.37079 | -0.3479 | -0.42572 | 6.9122 | 6.8802 | 6.9214 | -0.16479 | -0.30212 | 121.5958 | -0.49439 | -0.004577 | -122.0078 | 0.050354 | 7.3334 | -114.7797 | -0.073242 | -0.064087 | 0.054931 | 0.25635 | 0.11902 | 7.3013 | 0.073243 | 0.050354 | 122.0169 | 7.3425 | -0.073242 | 0.073243 | 0.050354 | 7.3425 | 7.3013 | 122.0169 | -122.0856 | -122.1542
772.0156 | 122.0856 | -0.39825 | 121.6553 | -0.083923 | 0.0098268 | 0.024353 | 0.040161 | 0.057037 | 0.057037 | 0.15231 | -0.29297 | -0.30212 | -0.34332 | 6.9809 | 6.9168 | 6.9443 | -0.25177 | -0.29755 | 121.5958 | -0.46692 | 0.054931 | -121.9574 | 0.10529 | 7.3792 | -114.7385 | -0.068665 | -0.059509 | 0.050354 | 0.14648 | 0.10071 | 7.3151 | 0.09613 | 0.10529 | 121.994 | 7.3425 | -0.068665 | 0.09613 | 0.10529 | 7.3425 | 7.3151 | 121.994 | -121.9986 | -122.1222
772.9688 | 122.0856 | -0.39368 | 121.5134 | 0.28992 | 0.010468 | 0.019653 | 0.033753 | 0.054687 | 0.060455 | 0.15338 | -0.32959 | -0.37079 | -0.37537 | 7.077 | 7.0679 | 7.1136 | -0.29297 | -0.26093 | 121.582 | -0.46234 | 0.018311 | -121.8842 | 0.064087 | 7.4707 | -114.4455 | -0.068664 | 0.068664 | 0.045776 | 0.10071 | 0.13275 | 7.4615 | 0.022888 | 0.064087 | 121.9757 | 7.5073 | -0.068664 | 0.022888 | 0.064087 | 7.5073 | 7.4615 | 121.9757 | -121.8887 | -121.9757
774.0156 | 122.1176 | -0.43945 | 121.6461 | 0.068664 | 0.011322 | 0.02713 | 0.040375 | 0.056396 | 0.058533 | 0.15317 | -0.37537 | -0.36163 | -0.44861 | 7.077 | 7.045 | 7.0633 | -0.23346 | -0.31128 | 121.5958 | -0.52643 | -0.009155 | -122.0078 | 0.064087 | 7.5165 | -114.6011 | -0.086975 | -0.050354 | 0.073242 | 0.20599 | 0.12817 | 7.4844 | 0.07782 | 0.064087 | 122.0352 | 7.5027 | -0.086975 | 0.07782 | 0.064087 | 7.5027 | 7.4844 | 122.0352 | -122.0947 | -122.1725
774.9688 | 122.1909 | -0.38452 | 121.6232 | -0.022889 | 0.0093994 | 0.020508 | 0.035248 | 0.057037 | 0.059601 | 0.15295 | -0.45319 | -0.3891 | -0.39825 | 7.0862 | 7.0953 | 7.1228 | -0.32959 | -0.18768 | 121.5775 | -0.46692 | -0.013733 | -122.0123 | -0.068665 | 7.4707 | -114.5279 | -0.082398 | -0.045776 | -0.054932 | 0.054931 | 0.19684 | 7.4799 | -0.004578 | -0.068665 | 121.962 | 7.5073 | -0.082398 | -0.004578 | -0.068665 | 7.5073 | 7.4799 | 121.962 | -122.0215 | -122.0901
776.0156 | 122.0901 | -0.39368 | 121.7056 | -0.3891 | 0.0098268 | 0.028198 | 0.038239 | 0.057037 | 0.057678 | 0.15445 | -0.28381 | -0.29297 | -0.32959 | 7.0541 | 6.9946 | 7.0312 | -0.2243 | -0.27466 | 121.6278 | -0.46234 | 0.064087 | -121.9986 | 0.10986 | 7.4478 | -114.711 | -0.068664 | -0.077819 | 0.045777 | 0.16937 | 0.11902 | 7.3883 | 0.10071 | 0.10986 | 122.0215 | 7.4249 | -0.068664 | 0.10071 | 0.10986 | 7.4249 | 7.3883 | 122.0215 | -122.0352 | -122.168
776.9688 | 122.2183 | -0.40283 | 121.5225 | 0.27466 | 0.0070496 | 0.019653 | 0.030762 | 0.055115 | 0.058319 | 0.15466 | -0.35706 | -0.39368 | -0.39368 | 6.9855 | 6.9672 | 7.0129 | -0.29297 | -0.25177 | 121.582 | -0.46234 | 0.009155 | -121.9162 | 0.045776 | 7.3883 | -114.5554 | -0.059509 | 0.059509 | 0.036621 | 0.10986 | 0.15106 | 7.37 | 0.009155 | 0.045776 | 121.9849 | 7.4158 | -0.059509 | 0.009155 | 0.045776 | 7.4158 | 7.37 | 121.9849 | -121.9162 | -121.9849
778.0156 | 122.0718 | -0.41657 | 121.6873 | 0.28992 | 0.01004 | 0.028626 | 0.039948 | 0.054687 | 0.058319 | 0.15466 | -0.3891 | -0.36621 | -0.4303 | 6.9809 | 6.9214 | 6.9672 | -0.17853 | -0.37537 | 121.637 | -0.50354 | -0.013733 | -122.0535 | 0.027466 | 7.3975 | -114.7659 | -0.086975 | -0.050354 | 0.041199 | 0.23804 | 0.041199 | 7.338 | 0.050354 | 0.027466 | 122.0535 | 7.3837 | -0.086975 | 0.050354 | 0.027466 | 7.3837 | 7.338 | 122.0535 | -122.1176 | -122.1909
778.9688 | 122.2321 | -0.37079 | 121.6507 | 0.10681 | 0.0057678 | 0.023285 | 0.031616 | 0.052978 | 0.059814 | 0.15317 | -0.26093 | -0.35248 | -0.33417 | 7.1045 | 7.1091 | 7.1365 | -0.32044 | -0.13733 | 121.6187 | -0.42114 | 0.036622 | -122.0032 | 0.10986 | 7.4753 | -114.5416 | -0.050354 | -0.032044 | 0.073242 | 0.050354 | 0.23346 | 7.4799 | 0.018311 | 0.10986 | 121.9894 | 7.5073 | -0.050354 | 0.018311 | 0.10986 | 7.5073 | 7.4799 | 121.9894 | -121.9849 | -122.0718
780.0156 | 122.0856 | -0.39368 | 121.7056 | 0.2594 | 0.011536 | 0.026489 | 0.041016 | 0.056824 | 0.060669 | 0.15359 | -0.33417 | -0.35248 | -0.40741 | 6.9809 | 6.9214 | 6.9717 | -0.18768 | -0.31586 | 121.669 | -0.48065 | -0.013733 | -122.0581 | 0.05951 | 7.3746 | -114.7842 | -0.086975 | -0.036621 | 0.073243 | 0.20599 | 0.07782 | 7.3151 | 0.041199 | 0.05951 | 122.0627 | 7.3654 | -0.086975 | 0.041199 | 0.05951 | 7.3654 | 7.3151 | 122.0627 | -122.113 | -122.1863
780.9688 | 122.1725 | -0.33875 | 121.701 | 0.34332 | 0.0098268 | 0.026276 | 0.031403 | 0.056824 | 0.06131 | 0.15488 | -0.27466 | -0.32959 | -0.36163 | 7.0404 | 7.0221 | 7.0816 | -0.27924 | -0.23346 | 121.6599 | -0.41199 | -0.022888 | -122.0306 | 0.064087 | 7.3792 | -114.679 | -0.073242 | -0.041199 | 0.086975 | 0.059509 | 0.10529 | 7.3608 | 0.009155 | 0.064087 | 121.9986 | 7.4203 | -0.073242 | 0.009155 | 0.064087 | 7.4203 | 7.3608 | 121.9986 | -122.0627 | -122.113
782.0156 | 122.1039 | -0.39368 | 121.7285 | 0.16785 | 0.010468 | 0.027771 | 0.040802 | 0.057892 | 0.059387 | 0.15359 | -0.3067 | -0.32044 | -0.40741 | 7.0038 | 6.9489 | 6.9992 | -0.20142 | -0.3067 | 121.6873 | -0.46692 | -0.013733 | -122.049 | 0.086975 | 7.3975 | -114.7797 | -0.073242 | -0.041199 | 0.10071 | 0.19226 | 0.086975 | 7.3425 | 0.073242 | 0.086975 | 122.081 | 7.3929 | -0.073242 | 0.073242 | 0.086975 | 7.3929 | 7.3425 | 122.081 | -122.1359 | -122.1954
782.9688 | 122.2595 | -0.35706 | 121.6965 | 0.12207 | 0.010254 | 0.023285 | 0.031616 | 0.05426 | 0.057892 | 0.15402 | -0.23804 | -0.33875 | -0.34332 | 7.0862 | 7.0724 | 7.1091 | -0.31128 | -0.10529 | 121.6736 | -0.42114 | 0.013733 | -122.0352 | 0.11902 | 7.4432 | -114.624 | -0.064087 | -0.022888 | 0.10529 | 0.045777 | 0.25177 | 7.4295 | 0.018311 | 0.11902 | 122.0306 | 7.4661 | -0.064087 | 0.018311 | 0.11902 | 7.4661 | 7.4295 | 122.0306 | -122.0398 | -122.1176
784.0156 | 122.1222 | -0.36621 | 121.7377 | -0.045776 | 0.01239 | 0.024567 | 0.039948 | 0.056824 | 0.058105 | 0.15359 | -0.2655 | -0.27008 | -0.33417 | 7.0267 | 6.9763 | 7.0129 | -0.20599 | -0.26093 | 121.7239 | -0.45319 | 0.032044 | -122.0078 | 0.10071 | 7.3929 | -114.7614 | -0.086975 | -0.013733 | 0.068664 | 0.16022 | 0.10529 | 7.3425 | 0.09613 | 0.10071 | 122.0901 | 7.3792 | -0.086975 | 0.09613 | 0.10071 | 7.3792 | 7.3425 | 122.0901 | -122.0718 | -122.1909
784.9688 | 122.2321 | -0.31586 | 121.7239 | 0.16785 | 0.0089722 | 0.025208 | 0.02948 | 0.057678 | 0.060455 | 0.15359 | -0.25177 | -0.32044 | -0.34332 | 7.0908 | 7.0679 | 7.1274 | -0.28839 | -0.15106 | 121.7056 | -0.40283 | -0.027466 | -122.0444 | 0.064087 | 7.4066 | -114.6561 | -0.086975 | -0.018311 | 0.091553 | 0.027466 | 0.16479 | 7.3837 | -0.004578 | 0.064087 | 122.0215 | 7.4432 | -0.086975 | -0.004578 | 0.064087 | 7.4432 | 7.3837 | 122.0215 | -122.0673 | -122.1268
785.9688 | 122.2137 | -0.33417 | 121.7468 | 0.35095 | 0.0091858 | 0.025421 | 0.036957 | 0.054687 | 0.060455 | 0.15659 | -0.25635 | -0.34332 | -0.35248 | 7.2006 | 7.1594 | 7.2372 | -0.27924 | -0.21057 | 121.6644 | -0.40283 | -0.018311 | -122.0901 | 0.077819 | 7.5348 | -114.5874 | -0.068665 | -0.082397 | 0.09613 | 0.054931 | 0.1236 | 7.4936 | -0.009156 | 0.077819 | 121.9986 | 7.5714 | -0.068665 | -0.009156 | 0.077819 | 7.5714 | 7.4936 | 121.9986 | -122.0993 | -122.1497
786.9688 | 122.2183 | -0.35248 | 121.7377 | 1.8768 | 0.01004 | 0.026276 | 0.037811 | 0.058105 | 0.059601 | 0.15466 | -0.21515 | -0.3891 | -0.37537 | 7.1091 | 7.077 | 7.1228 | -0.3479 | -0.19226 | 121.6736 | -0.43945 | -0.022888 | -122.1268 | 0.13733 | 7.4615 | -114.6606 | -0.086975 | -0.064087 | 0.16022 | 0.004578 | 0.16022 | 7.4295 | -0.036621 | 0.13733 | 122.0261 | 7.4753 | -0.086975 | -0.036621 | 0.13733 | 7.4753 | 7.4295 | 122.0261 | -122.113 | -122.1771
787.9688 | 122.2 | -0.32044 | 121.7285 | 0.35858 | 0.0098268 | 0.024994 | 0.037811 | 0.055115 | 0.059174 | 0.15573 | -0.25177 | -0.35248 | -0.3479 | 7.077 | 7.0358 | 7.1091 | -0.30212 | -0.18768 | 121.6873 | -0.41657 | -0.027465 | -122.081 | 0.068665 | 7.3975 | -114.6927 | -0.09613 | -0.041199 | 0.09613 | 0.018311 | 0.13275 | 7.3563 | -0.032043 | 0.068665 | 122.0078 | 7.4295 | -0.09613 | -0.032043 | 0.068665 | 7.4295 | 7.3563 | 122.0078 | -122.0764 | -122.1451
788.9688 | 122.2183 | -0.32044 | 121.7606 | 0.38147 | 0.0081178 | 0.02243 | 0.035248 | 0.056824 | 0.05896 | 0.1568 | -0.24261 | -0.3479 | -0.36621 | 7.0953 | 7.0633 | 7.1274 | -0.30212 | -0.17853 | 121.6919 | -0.4303 | -0.045776 | -122.1085 | 0.07782 | 7.4158 | -114.6973 | -0.10986 | -0.068664 | 0.1236 | 0.018311 | 0.14191 | 7.3837 | -0.027465 | 0.07782 | 122.0123 | 7.4478 | -0.10986 | -0.027465 | 0.07782 | 7.4478 | 7.3837 | 122.0123 | -122.1268 | -122.1909
789.9688 | 122.2092 | -0.32959 | 121.7606 | 0.37384 | 0.009613 | 0.022003 | 0.035675 | 0.054901 | 0.060883 | 0.1568 | -0.2655 | -0.33417 | -0.35248 | 7.0587 | 7.0038 | 7.0724 | -0.27008 | -0.20142 | 121.7148 | -0.39368 | -0.022888 | -122.0947 | 0.064087 | 7.3883 | -114.7568 | -0.064087 | -0.045776 | 0.086975 | 0.059509 | 0.12817 | 7.3334 | -0.004577 | 0.064087 | 122.0444 | 7.402 | -0.064087 | -0.004577 | 0.064087 | 7.402 | 7.3334 | 122.0444 | -122.113 | -122.1542
790.9688 | 122.2137 | -0.31586 | 121.7606 | 0.35858 | 0.011108 | 0.02478 | 0.03653 | 0.054901 | 0.060455 | 0.15594 | -0.24719 | -0.34332 | -0.33875 | 7.045 | 6.9992 | 7.0724 | -0.28839 | -0.20142 | 121.7239 | -0.40283 | -0.022888 | -122.1039 | 0.068665 | 7.3608 | -114.7614 | -0.086975 | -0.036621 | 0.091553 | 0.027466 | 0.11444 | 7.3151 | -0.027466 | 0.068665 | 122.0398 | 7.3883 | -0.086975 | -0.027466 | 0.068665 | 7.3883 | 7.3151 | 122.0398 | -122.0993 | -122.1634
791.9688 | 122.2549 | -0.34332 | 121.7789 | 0.20599 | 0.009613 | 0.022644 | 0.035461 | 0.053619 | 0.057678 | 0.15637 | -0.29297 | -0.32044 | -0.35706 | 7.0084 | 6.9809 | 7.0633 | -0.26093 | -0.17395 | 121.7056 | -0.41657 | -0.013733 | -122.0993 | 0.050354 | 7.3517 | -114.798 | -0.073242 | -0.073243 | 0.064087 | 0.082398 | 0.16937 | 7.3242 | 0.022888 | 0.050354 | 122.049 | 7.4066 | -0.073242 | 0.022888 | 0.050354 | 7.4066 | 7.3242 | 122.049 | -122.1359 | -122.1954
793.0156 | 122.1909 | -0.37079 | 121.7834 | 0.091552 | 0.0098268 | 0.024353 | 0.043152 | 0.055328 | 0.057678 | 0.15488 | -0.27924 | -0.3067 | -0.3891 | 6.9855 | 6.9122 | 6.9443 | -0.1831 | -0.24719 | 121.7468 | -0.45319 | -0.01831 | -122.0901 | 0.091553 | 7.3563 | -114.8712 | -0.082397 | -0.036621 | 0.10986 | 0.18768 | 0.1236 | 7.283 | 0.064087 | 0.091553 | 122.1176 | 7.3151 | -0.082397 | 0.064087 | 0.091553 | 7.3151 | 7.283 | 122.1176 | -122.1725 | -122.2366
793.9688 | 122.2641 | -0.3479 | 121.7606 | 0.40436 | 0.01004 | 0.02478 | 0.037384 | 0.055969 | 0.059174 | 0.15488 | -0.25635 | -0.33875 | -0.36621 | 7.0312 | 6.9763 | 7.045 | -0.33417 | -0.19684 | 121.6873 | -0.41199 | -0.018311 | -122.0993 | 0.091552 | 7.3792 | -114.7842 | -0.064087 | -0.073242 | 0.10986 | 0.013733 | 0.15106 | 7.3242 | 0.009155 | 0.091552 | 122.0352 | 7.3929 | -0.064087 | 0.009155 | 0.091552 | 7.3929 | 7.3242 | 122.0352 | -122.1268 | -122.1725
795.0156 | 122.2092 | -0.37537 | 121.843 | 0.16785 | 0.012604 | 0.024994 | 0.041229 | 0.059174 | 0.05896 | 0.15573 | -0.27924 | -0.32044 | -0.38452 | 6.9534 | 6.9031 | 6.9214 | -0.19684 | -0.24719 | 121.7377 | -0.46234 | -0.009155 | -122.1634 | 0.09613 | 7.3288 | -114.9399 | -0.086975 | -0.10529 | 0.10529 | 0.17853 | 0.12817 | 7.2784 | 0.054931 | 0.09613 | 122.113 | 7.2968 | -0.086975 | 0.054931 | 0.09613 | 7.2968 | 7.2784 | 122.113 | -122.2275 | -122.3053
795.9688 | 122.3557 | -0.4303 | 121.669 | 0.41962 | 0.01004 | 0.025421 | 0.035461 | 0.059387 | 0.059601 | 0.15723 | -0.27924 | -0.40741 | -0.41657 | 6.9489 | 6.9122 | 6.9763 | -0.38452 | -0.30212 | 121.6553 | -0.47607 | 0.013733 | -122.0764 | 0.15106 | 7.3792 | -114.7568 | -0.045776 | -0.013733 | 0.13733 | 0.045777 | 0.12817 | 7.3425 | 0.022888 | 0.15106 | 122.0856 | 7.4066 | -0.045776 | 0.022888 | 0.15106 | 7.4066 | 7.3425 | 122.0856 | -122.0856 | -122.1451
797.0156 | 122.2046 | -0.42114 | 121.7377 | 0.061035 | 0.010895 | 0.022858 | 0.038879 | 0.059601 | 0.057678 | 0.15488 | -0.34332 | -0.37994 | -0.44403 | 6.9214 | 6.8802 | 6.9077 | -0.20599 | -0.28839 | 121.7285 | -0.50812 | -0.022888 | -122.1176 | 0.07782 | 7.3425 | -114.8575 | -0.086975 | -0.009155 | 0.10071 | 0.21515 | 0.13275 | 7.3013 | 0.041199 | 0.07782 | 122.1497 | 7.3288 | -0.086975 | 0.041199 | 0.07782 | 7.3288 | 7.3013 | 122.1497 | -122.1817 | -122.2458
797.9688 | 122.2824 | -0.37994 | 121.7789 | 0.19836 | 0.0098268 | 0.024567 | 0.030335 | 0.058319 | 0.061096 | 0.15359 | -0.30212 | -0.37079 | -0.3891 | 6.9855 | 6.9717 | 7.0221 | -0.27008 | -0.19684 | 121.7331 | -0.43945 | -0.009155 | -122.1497 | 0.07782 | 7.3654 | -114.8071 | -0.059509 | -0.045777 | 0.086975 | 0.10986 | 0.18311 | 7.3517 | 0.009155 | 0.07782 | 122.113 | 7.402 | -0.059509 | 0.009155 | 0.07782 | 7.402 | 7.3517 | 122.113 | -122.168 | -122.2183
799.0156 | 122.1954 | -0.41657 | 121.7651 | 0.038147 | 0.011536 | 0.02478 | 0.03653 | 0.055756 | 0.060028 | 0.15445 | -0.35706 | -0.32044 | -0.40741 | 6.9122 | 6.8756 | 6.8848 | -0.13733 | -0.29297 | 121.7285 | -0.50812 | 0.009155 | -122.0856 | 0.059509 | 7.3288 | -114.8895 | -0.091553 | -0.036621 | 0.050354 | 0.27924 | 0.1236 | 7.2922 | 0.09613 | 0.059509 | 122.1451 | 7.3013 | -0.091553 | 0.09613 | 0.059509 | 7.3013 | 7.2922 | 122.1451 | -122.1725 | -122.2733
799.9688 | 122.2412 | -0.36621 | 121.7697 | 0.38147 | 0.0079042 | 0.023285 | 0.034607 | 0.057037 | 0.059814 | 0.15402 | -0.31586 | -0.33417 | -0.37537 | 6.9626 | 6.9443 | 6.9992 | -0.25635 | -0.24261 | 121.7514 | -0.45319 | -0.009155 | -122.1039 | 0.050354 | 7.3288 | -114.8254 | -0.086975 | -0.01831 | 0.059509 | 0.10986 | 0.1236 | 7.3105 | 0.032044 | 0.050354 | 122.1176 | 7.3654 | -0.086975 | 0.032044 | 0.050354 | 7.3654 | 7.3105 | 122.1176 | -122.1451 | -122.2229
801.0156 | 122.1771 | -0.40283 | 121.8201 | -0.076294 | 0.010681 | 0.017517 | 0.036316 | 0.056824 | 0.060883 | 0.15573 | -0.34332 | -0.30212 | -0.40741 | 7.0358 | 7.0038 | 7.0312 | -0.10986 | -0.27924 | 121.7697 | -0.47607 | -0.004578 | -122.1222 | 0.059509 | 7.4387 | -114.8163 | -0.073242 | -0.050354 | 0.064087 | 0.29297 | 0.1236 | 7.4066 | 0.10071 | 0.059509 | 122.1725 | 7.4341 | -0.073242 | 0.10071 | 0.059509 | 7.4341 | 7.4066 | 122.1725 | -122.2275 | -122.2961
801.9688 | 122.319 | -0.34332 | 121.7789 | 0.40436 | 0.0098268 | 0.030762 | 0.041443 | 0.061523 | 0.060669 | 0.15616 | -0.22888 | -0.3479 | -0.35706 | 7.1457 | 7.0816 | 7.1594 | -0.34332 | -0.17853 | 121.7697 | -0.43488 | -0.013733 | -122.1268 | 0.11444 | 7.489 | -114.6973 | -0.091552 | -0.009156 | 0.12817 | 0 | 0.16479 | 7.4249 | -0.004577 | 0.11444 | 122.113 | 7.5027 | -0.091552 | -0.004577 | 0.11444 | 7.5027 | 7.4249 | 122.113 | -122.1359 | -122.2137
803.0156 | 122.1909 | -0.38452 | 121.8613 | -0.045776 | 0.011536 | 0.024139 | 0.036743 | 0.055969 | 0.058319 | 0.15359 | -0.33417 | -0.29755 | -0.39368 | 7.0129 | 6.9901 | 7.0129 | -0.086975 | -0.27924 | 121.8063 | -0.47607 | -0.009156 | -122.1588 | 0.050354 | 7.3975 | -114.8712 | -0.091553 | -0.054932 | 0.05951 | 0.29755 | 0.10529 | 7.3746 | 0.086975 | 0.050354 | 122.1909 | 7.3975 | -0.091553 | 0.086975 | 0.050354 | 7.3975 | 7.3746 | 122.1909 | -122.2549 | -122.3373
803.9688 | 122.3099 | -0.33417 | 121.7926 | 0.40436 | 0.011536 | 0.024353 | 0.038452 | 0.061096 | 0.055969 | 0.15488 | -0.29755 | -0.34332 | -0.36621 | 7.077 | 7.045 | 7.1228 | -0.30212 | -0.2243 | 121.7743 | -0.43488 | -0.032044 | -122.1359 | 0.036621 | 7.4112 | -114.7476 | -0.10071 | -0.018311 | 0.068665 | 0.032043 | 0.10986 | 7.3792 | -0.009156 | 0.036621 | 122.1085 | 7.457 | -0.10071 | -0.009156 | 0.036621 | 7.457 | 7.3792 | 122.1085 | -122.1588 | -122.2275
804.9688 | 122.2733 | -0.37537 | 121.8063 | 0.41199 | 0.011749 | 0.02179 | 0.035889 | 0.060669 | 0.060028 | 0.15359 | -0.30212 | -0.31586 | -0.39825 | 7.0587 | 7.0221 | 7.0679 | -0.24719 | -0.24719 | 121.788 | -0.43945 | -0.022888 | -122.1222 | 0.073242 | 7.4341 | -114.7842 | -0.064087 | -0.01831 | 0.09613 | 0.12817 | 0.12817 | 7.3975 | 0.059509 | 0.073242 | 122.1634 | 7.4432 | -0.064087 | 0.059509 | 0.073242 | 7.4432 | 7.3975 | 122.1634 | -122.2046 | -122.2458
806.0156 | 122.2275 | -0.37994 | 121.8246 | 0.038147 | 0.012604 | 0.025635 | 0.03717 | 0.05661 | 0.059601 | 0.15338 | -0.31128 | -0.27466 | -0.37537 | 7.0679 | 7.0496 | 7.0679 | -0.086975 | -0.27924 | 121.8201 | -0.46234 | 0.004578 | -122.0993 | 0.068665 | 7.4478 | -114.7751 | -0.082397 | -0.004578 | 0.064087 | 0.29297 | 0.10071 | 7.4295 | 0.10529 | 0.068665 | 122.2 | 7.4478 | -0.082397 | 0.10529 | 0.068665 | 7.4478 | 7.4295 | 122.2 | -122.2 | -122.287
806.9688 | 122.1817 | -0.38452 | 121.8887 | 0.33569 | 0.011749 | 0.026062 | 0.040161 | 0.059814 | 0.057678 | 0.15466 | -0.31586 | -0.27008 | -0.3891 | 7.0908 | 7.0541 | 7.0862 | -0.1236 | -0.32959 | 121.875 | -0.45319 | -0.004578 | -122.1588 | 0.068664 | 7.4753 | -114.8346 | -0.068665 | -0.013733 | 0.073242 | 0.26093 | 0.054931 | 7.4387 | 0.11444 | 0.068664 | 122.2595 | 7.4707 | -0.068665 | 0.11444 | 0.068664 | 7.4707 | 7.4387 | 122.2595 | -122.2778 | -122.3419
808.0156 | 122.3053 | -0.31586 | 121.843 | 0.068664 | 0.0098268 | 0.024994 | 0.032044 | 0.05896 | 0.059174 | 0.15445 | -0.21057 | -0.31128 | -0.32959 | 7.2144 | 7.2006 | 7.2327 | -0.21057 | -0.11444 | 121.8384 | -0.39825 | -0.013733 | -122.1542 | 0.10529 | 7.5302 | -114.6423 | -0.082397 | -0.004578 | 0.11902 | 0.10529 | 0.20142 | 7.5165 | 0.004578 | 0.10529 | 122.1542 | 7.5485 | -0.082397 | 0.004578 | 0.10529 | 7.5485 | 7.5165 | 122.1542 | -122.1725 | -122.2412
808.9688 | 122.2366 | -0.34332 | 121.8842 | 0.35858 | 0.013458 | 0.024994 | 0.036957 | 0.059601 | 0.061737 | 0.15573 | -0.28839 | -0.25635 | -0.36163 | 7.1548 | 7.1182 | 7.1686 | -0.16937 | -0.27924 | 121.8521 | -0.41657 | -0.01831 | -122.1405 | 0.054932 | 7.4982 | -114.7659 | -0.073242 | -0.032043 | 0.073242 | 0.17395 | 0.064087 | 7.4615 | 0.086975 | 0.054932 | 122.1954 | 7.5119 | -0.073242 | 0.086975 | 0.054932 | 7.5119 | 7.4615 | 122.1954 | -122.2458 | -122.3007
810.0156 | 122.2275 | -0.33875 | 121.8887 | -0.030518 | 0.009613 | 0.024567 | 0.03418 | 0.058105 | 0.05896 | 0.15488 | -0.25635 | -0.27466 | -0.34332 | 7.2144 | 7.1823 | 7.2052 | -0.07782 | -0.2243 | 121.8658 | -0.40741 | -0.004578 | -122.1634 | 0.082397 | 7.5531 | -114.7064 | -0.068665 | -0.022888 | 0.086975 | 0.26093 | 0.11444 | 7.5211 | 0.064087 | 0.082397 | 122.2046 | 7.5439 | -0.068665 | 0.064087 | 0.082397 | 7.5439 | 7.5211 | 122.2046 | -122.2321 | -122.2961
810.9688 | 122.3282 | -0.31586 | 121.8658 | 0.40436 | 0.011749 | 0.026917 | 0.03418 | 0.060455 | 0.060669 | 0.15552 | -0.14648 | -0.31586 | -0.32501 | 7.2601 | 7.2327 | 7.2968 | -0.27466 | -0.14191 | 121.8475 | -0.39825 | -0.009155 | -122.1817 | 0.16937 | 7.576 | -114.6332 | -0.082397 | -0.018311 | 0.17853 | 0.041199 | 0.17395 | 7.5485 | 0 | 0.16937 | 122.1634 | 7.6126 | -0.082397 | 0 | 0.16937 | 7.6126 | 7.5485 | 122.1634 | -122.1909 | -122.2641
812.0156 | 122.3557 | -0.27008 | 121.9116 | 0.015259 | 0.0055542 | 0.02243 | 0.033325 | 0.057251 | 0.06131 | 0.15359 | -0.054932 | -0.27924 | -0.3067 | 7.3425 | 7.3013 | 7.3654 | -0.21057 | -0.068665 | 121.907 | -0.36163 | -0.036621 | -122.1909 | 0.21515 | 7.6126 | -114.6103 | -0.091552 | -0.004578 | 0.25177 | 0.05951 | 0.20142 | 7.5714 | -0.009155 | 0.21515 | 122.1771 | 7.6355 | -0.091552 | -0.009155 | 0.21515 | 7.6355 | 7.5714 | 122.1771 | -122.2183 | -122.2733
812.9688 | 122.1954 | -0.30212 | 121.9482 | 0.3128 | 0.012817 | 0.02243 | 0.040375 | 0.059814 | 0.058746 | 0.1553 | -0.27466 | -0.22888 | -0.34332 | 7.2372 | 7.1777 | 7.2098 | -0.045776 | -0.27466 | 121.9391 | -0.40741 | -0.041199 | -122.1771 | 0.027466 | 7.5394 | -114.7705 | -0.10529 | -0.009155 | 0.068665 | 0.25635 | 0.027466 | 7.4799 | 0.073242 | 0.027466 | 122.2412 | 7.5119 | -0.10529 | 0.073242 | 0.027466 | 7.5119 | 7.4799 | 122.2412 | -122.2916 | -122.3557
814.0156 | 122.2733 | -0.29297 | 121.9299 | -0.038147 | 0.009613 | 0.021149 | 0.034821 | 0.057892 | 0.058533 | 0.15488 | -0.18768 | -0.25635 | -0.31128 | 7.3517 | 7.3196 | 7.3654 | -0.10071 | -0.1236 | 121.9345 | -0.36163 | -0.01831 | -122.1863 | 0.10529 | 7.6447 | -114.6103 | -0.068664 | 0.004577 | 0.1236 | 0.19226 | 0.16937 | 7.6126 | 0.036621 | 0.10529 | 122.2275 | 7.6584 | -0.068664 | 0.036621 | 0.10529 | 7.6584 | 7.6126 | 122.2275 | -122.2412 | -122.2916
814.9688 | 122.3465 | -0.27924 | 121.9116 | 0.42725 | 0.010895 | 0.027344 | 0.034821 | 0.059601 | 0.060028 | 0.15359 | -0.14648 | -0.27008 | -0.29297 | 7.3792 | 7.3334 | 7.4295 | -0.25177 | -0.11902 | 121.8887 | -0.3479 | -0.013733 | -122.1817 | 0.13275 | 7.6584 | -114.5782 | -0.068664 | -0.022888 | 0.14648 | 0.027466 | 0.16022 | 7.6126 | 0.009155 | 0.13275 | 122.168 | 7.7087 | -0.068664 | 0.009155 | 0.13275 | 7.7087 | 7.6126 | 122.168 | -122.2046 | -122.2595
816.0156 | 122.2733 | -0.32044 | 121.9345 | 0.19073 | 0.012817 | 0.025421 | 0.039734 | 0.058105 | 0.060242 | 0.15338 | -0.19684 | -0.21057 | -0.28381 | 7.4341 | 7.37 | 7.4066 | -0.10071 | -0.20142 | 121.9299 | -0.39368 | 0.036622 | -122.1451 | 0.1236 | 7.7545 | -114.5645 | -0.073242 | -0.004577 | 0.086975 | 0.21973 | 0.11902 | 7.6904 | 0.10986 | 0.1236 | 122.2504 | 7.7271 | -0.073242 | 0.10986 | 0.1236 | 7.7271 | 7.6904 | 122.2504 | -122.2183 | -122.3282
816.9688 | 122.2549 | -0.33417 | 121.9437 | 0.21362 | 0.013031 | 0.02713 | 0.038239 | 0.060882 | 0.059601 | 0.15552 | -0.26093 | -0.23346 | -0.33417 | 7.4615 | 7.3975 | 7.4524 | -0.09613 | -0.26093 | 121.9391 | -0.41199 | 0 | -122.1771 | 0.073242 | 7.7957 | -114.5462 | -0.07782 | -0.004578 | 0.073242 | 0.23804 | 0.073242 | 7.7316 | 0.10071 | 0.073242 | 122.2733 | 7.7866 | -0.07782 | 0.10071 | 0.073242 | 7.7866 | 7.7316 | 122.2733 | -122.2778 | -122.3557
818.0156 | 122.3557 | -0.2655 | 121.9254 | 0.038147 | 0.0093994 | 0.023071 | 0.031616 | 0.058105 | 0.060242 | 0.1553 | -0.16022 | -0.27466 | -0.2655 | 7.6172 | 7.6035 | 7.6447 | -0.19684 | -0.064087 | 121.9254 | -0.35248 | 0 | -122.2 | 0.10529 | 7.8827 | -114.3219 | -0.086975 | 0 | 0.10529 | 0.068665 | 0.20142 | 7.869 | -0.009155 | 0.10529 | 122.1909 | 7.9102 | -0.086975 | -0.009155 | 0.10529 | 7.9102 | 7.869 | 122.1909 | -122.1909 | -122.2778
818.9688 | 122.2778 | -0.31586 | 121.9666 | 0.16785 | 0.011749 | 0.025208 | 0.037811 | 0.061523 | 0.059814 | 0.15488 | -0.21515 | -0.21973 | -0.3067 | 7.5943 | 7.5531 | 7.5714 | -0.11902 | -0.20142 | 121.9391 | -0.40283 | 0.009155 | -122.1863 | 0.10071 | 7.9102 | -114.4135 | -0.086975 | -0.027466 | 0.091553 | 0.19684 | 0.11444 | 7.869 | 0.09613 | 0.10071 | 122.2549 | 7.8873 | -0.086975 | 0.09613 | 0.10071 | 7.8873 | 7.869 | 122.2549 | -122.2733 | -122.3694
820.0156 | 122.2549 | -0.35706 | 121.756 | 0 | 0.010895 | 0.030121 | 2.644 | 0.006195 | 0.0091858 | 2.6709 | -0.23346 | -0.33875 | -0.35706 | 100.0763 | 99.9893 | 102.4109 | 0.87891 | 0.19684 | 121.5363 | -0.23804 | 0 | -122.0947 | 0.1236 | 100.4334 | -21.7667 | 0.11902 | -0.21973 | 0.1236 | 1.236 | 0.55389 | 100.3464 | 0.018311 | 0.1236 | 121.8933 | 102.7679 | 0.11902 | 0.018311 | 0.1236 | 102.7679 | 100.3464 | 121.8933 | -122.113 | -121.994
820.9688 | 122.2778 | -0.34332 | 121.9345 | 0.038147 | 0.014313 | 0.027557 | 0.036957 | 0.055542 | 0.059601 | 0.15167 | -0.25177 | -0.27466 | -0.35248 | 9.0912 | 9.0363 | 9.0729 | -0.13733 | -0.21515 | 121.9116 | -0.41199 | -0.009155 | -122.2092 | 0.091553 | 9.4345 | -112.8983 | -0.068664 | -0.022888 | 0.10071 | 0.20599 | 0.12817 | 9.3796 | 0.068665 | 0.091553 | 122.2549 | 9.4162 | -0.068664 | 0.068665 | 0.091553 | 9.4162 | 9.3796 | 122.2549 | -122.287 | -122.3465
822.0156 | 122.3328 | -0.29297 | 121.9254 | 0.18311 | 0.0091858 | 0.029694 | 0.031616 | 0.056183 | 0.062378 | 0.15167 | -0.25177 | -0.29755 | -0.32044 | 8.9996 | 8.9996 | 9.05 | -0.20599 | -0.13733 | 121.9162 | -0.37537 | -0.027466 | -122.2229 | 0.041199 | 9.2926 | -112.9257 | -0.082397 | -0.009155 | 0.068665 | 0.086975 | 0.15564 | 9.2926 | -0.004577 | 0.041199 | 122.2092 | 9.343 | -0.082397 | -0.004577 | 0.041199 | 9.343 | 9.2926 | 122.2092 | -122.2458 | -122.3007
822.9688 | 122.319 | -0.26093 | 121.9757 | 0.11444 | 0.0098268 | 0.022858 | 0.042511 | 0.057678 | 0.057037 | 0.14932 | -0.21973 | -0.25635 | -0.34332 | 9.9335 | 10.0891 | 10.025 | 0.12817 | -0.17395 | 122.0169 | -0.32959 | -0.082398 | -122.2321 | 0.041198 | 10.1944 | -111.8866 | -0.068665 | 0.041199 | 0.1236 | 0.3891 | 0.086975 | 10.35 | 0.004577 | 0.041198 | 122.2778 | 10.2859 | -0.068665 | 0.004577 | 0.041198 | 10.2859 | 10.35 | 122.2778 | -122.319 | -122.3053
824.0156 | 122.3877 | -0.3067 | 121.9299 | -0.0076295 | 0.010468 | 0.02179 | 0.025421 | 0.055115 | 0.057892 | 0.15103 | -0.18768 | -0.27466 | -0.29755 | 10.3455 | 10.3226 | 10.3043 | -0.13733 | -0.13275 | 121.8979 | -0.39368 | 0.009156 | -122.2046 | 0.11902 | 10.6522 | -111.6074 | -0.086975 | -0.032044 | 0.10986 | 0.16937 | 0.17395 | 10.6293 | 0.032044 | 0.11902 | 122.2046 | 10.611 | -0.086975 | 0.032044 | 0.11902 | 10.611 | 10.6293 | 122.2046 | -122.2275 | -122.3236
824.9688 | 122.2504 | -0.33875 | 121.9574 | 0.2594 | 0.013672 | 0.025848 | 0.041443 | 0.056396 | 0.057037 | 0.14847 | -0.30212 | -0.27924 | -0.35248 | 12.0026 | 11.9385 | 11.9888 | -0.018311 | -0.29755 | 121.9666 | -0.42572 | -0.013733 | -122.2366 | 0.036621 | 12.3413 | -110.0189 | -0.086975 | 0.009156 | 0.050354 | 0.32043 | 0.041199 | 12.2772 | 0.059509 | 0.036621 | 122.3053 | 12.3276 | -0.086975 | 0.059509 | 0.036621 | 12.3276 | 12.2772 | 122.3053 | -122.3099 | -122.3831
826.0156 | 122.3602 | -0.28839 | 121.9437 | 0.32806 | 0.008545 | 0.023499 | 0.031616 | 0.054687 | 0.057037 | 0.1474 | -0.23804 | -0.27924 | -0.30212 | 12.7991 | 12.7533 | 12.8311 | -0.27008 | -0.18768 | 121.9482 | -0.37537 | -0.013733 | -122.2229 | 0.050354 | 13.0875 | -109.1904 | -0.086975 | 0.004577 | 0.064087 | 0.01831 | 0.10071 | 13.0417 | 0.009155 | 0.050354 | 122.2366 | 13.1195 | -0.086975 | 0.009155 | 0.050354 | 13.1195 | 13.0417 | 122.2366 | -122.2458 | -122.319
826.9688 | 122.2824 | -0.3479 | 121.9666 | 0.20599 | 0.011749 | 0.024994 | 0.038879 | 0.055115 | 0.057892 | 0.14996 | -0.25635 | -0.26093 | -0.32501 | 12.6801 | 12.5977 | 12.6526 | -0.19226 | -0.23804 | 121.9528 | -0.42114 | 0.022888 | -122.2275 | 0.091552 | 13.028 | -109.3689 | -0.073243 | -0.013733 | 0.068664 | 0.15564 | 0.10986 | 12.9456 | 0.086975 | 0.091552 | 122.3007 | 13.0005 | -0.073243 | 0.086975 | 0.091552 | 13.0005 | 12.9456 | 122.3007 | -122.2916 | -122.3877
828.0156 | 122.3602 | -0.3067 | 121.9254 | -0.74005 | 0.0081178 | 0.025208 | 0.030335 | 0.054687 | 0.056183 | 0.14911 | -0.34332 | -0.32959 | -0.36163 | 12.9089 | 12.8586 | 12.941 | -0.2243 | -0.17395 | 121.9299 | -0.39368 | -0.054931 | -122.2549 | -0.036621 | 13.2156 | -109.0668 | -0.086975 | 0.004578 | 0.01831 | 0.082398 | 0.13275 | 13.1653 | -0.022888 | -0.036621 | 122.2366 | 13.2477 | -0.086975 | -0.022888 | -0.036621 | 13.2477 | 13.1653 | 122.2366 | -122.287 | -122.319
828.9688 | 122.2824 | -0.34332 | 121.9757 | 0.26703 | 0.0081178 | 0.025208 | 0.038239 | 0.054474 | 0.054901 | 0.14761 | -0.25635 | -0.2655 | -0.35248 | 12.8586 | 12.767 | 12.8448 | -0.19684 | -0.27008 | 121.9482 | -0.42572 | -0.009155 | -122.2412 | 0.086975 | 13.2019 | -109.2087 | -0.082397 | -0.027466 | 0.09613 | 0.14648 | 0.073242 | 13.1104 | 0.07782 | 0.086975 | 122.2916 | 13.1882 | -0.082397 | 0.07782 | 0.086975 | 13.1882 | 13.1104 | 122.2916 | -122.3282 | -122.4014
830.0156 | 122.3557 | -0.29755 | 121.9391 | 0.32043 | 0.0087586 | 0.026062 | 0.03183 | 0.053833 | 0.059601 | 0.14804 | -0.25177 | -0.28839 | -0.29755 | 12.9456 | 12.9227 | 12.9822 | -0.26093 | -0.17395 | 121.962 | -0.36621 | 0 | -122.2275 | 0.045776 | 13.2431 | -109.0164 | -0.068665 | 0.022888 | 0.045776 | 0.036621 | 0.1236 | 13.2202 | 0.009155 | 0.045776 | 122.2595 | 13.2797 | -0.068665 | 0.009155 | 0.045776 | 13.2797 | 13.2202 | 122.2595 | -122.2366 | -122.3053
830.9688 | 122.2824 | -0.32959 | 121.9757 | 0.030518 | 0.01239 | 0.023712 | 0.040161 | 0.053192 | 0.055969 | 0.1474 | -0.27008 | -0.22888 | -0.32501 | 12.9913 | 12.9227 | 12.9684 | -0.11444 | -0.21973 | 121.9849 | -0.41657 | 0.004578 | -122.2046 | 0.059509 | 13.3209 | -109.053 | -0.086975 | 0.009155 | 0.054931 | 0.21515 | 0.10986 | 13.2523 | 0.10071 | 0.059509 | 122.3145 | 13.298 | -0.086975 | 0.10071 | 0.059509 | 13.298 | 13.2523 | 122.3145 | -122.3007 | -122.3923
832.0156 | 122.3877 | -0.2655 | 121.9757 | 0.11444 | 0.0087586 | 0.026276 | 0.03653 | 0.055542 | 0.056183 | 0.14996 | -0.19226 | -0.32044 | -0.3067 | 12.8036 | 12.7441 | 12.822 | -0.31128 | -0.10529 | 121.9574 | -0.35248 | -0.041199 | -122.2961 | 0.073242 | 13.0692 | -109.2316 | -0.086975 | -0.018311 | 0.11444 | -0.045776 | 0.16022 | 13.0096 | -0.054932 | 0.073242 | 122.2229 | 13.0875 | -0.086975 | -0.054932 | 0.073242 | 13.0875 | 13.0096 | 122.2229 | -122.2824 | -122.3282
832.9688 | 122.319 | -0.3479 | 121.9757 | 0.17548 | 0.011108 | 0.02948 | 0.040161 | 0.054474 | 0.056824 | 0.14996 | -0.22888 | -0.25635 | -0.33875 | 13.1287 | 13.0508 | 13.0966 | -0.20142 | -0.21973 | 121.9482 | -0.41657 | 0.009155 | -122.2321 | 0.11902 | 13.4766 | -108.9249 | -0.068665 | -0.027466 | 0.10986 | 0.14648 | 0.12817 | 13.3987 | 0.091552 | 0.11902 | 122.2961 | 13.4445 | -0.068665 | 0.091552 | 0.11902 | 13.4445 | 13.3987 | 122.2961 | -122.3145 | -122.3923
834.0156 | 122.3602 | -0.27466 | 121.9803 | 0.3891 | 0.0091858 | 0.023285 | 0.029266 | 0.053406 | 0.057892 | 0.14911 | -0.20599 | -0.24719 | -0.29755 | 12.7762 | 12.7396 | 12.822 | -0.25635 | -0.16479 | 122.0078 | -0.33875 | -0.022888 | -122.2275 | 0.068664 | 13.0508 | -109.2407 | -0.064087 | 0.027465 | 0.091552 | 0.01831 | 0.10986 | 13.0142 | 0.027466 | 0.068664 | 122.2824 | 13.0966 | -0.064087 | 0.027466 | 0.068664 | 13.0966 | 13.0142 | 122.2824 | -122.2778 | -122.319
834.9688 | 122.4197 | -0.25177 | 122.0169 | 0.038147 | 0.0074768 | 0.022003 | 0.034821 | 0.054047 | 0.057037 | 0.14697 | -0.16479 | -0.26093 | -0.27924 | 12.767 | 12.7258 | 12.7808 | -0.21057 | -0.054932 | 121.9894 | -0.32959 | -0.027466 | -122.2778 | 0.086975 | 13.0188 | -109.2911 | -0.07782 | -0.027466 | 0.11444 | 0.041199 | 0.19684 | 12.9776 | -0.009155 | 0.086975 | 122.2412 | 13.0325 | -0.07782 | -0.009155 | 0.086975 | 13.0325 | 12.9776 | 122.2412 | -122.2961 | -122.3465
836.0156 | 122.3785 | -0.23346 | 122.0215 | 0.38147 | 0.008545 | 0.025635 | 0.035034 | 0.054047 | 0.056824 | 0.14847 | -0.16937 | -0.25177 | -0.27924 | 13.1149 | 13.0463 | 13.1378 | -0.29297 | -0.10071 | 121.9757 | -0.3479 | -0.045777 | -122.2733 | 0.064086 | 13.3484 | -108.9752 | -0.11444 | -0.045776 | 0.10986 | -0.05951 | 0.13275 | 13.2797 | -0.018311 | 0.064086 | 122.2092 | 13.3713 | -0.11444 | -0.018311 | 0.064086 | 13.3713 | 13.2797 | 122.2092 | -122.3007 | -122.3694
836.9688 | 122.3511 | -0.3067 | 122.0306 | 0.045776 | 0.0076904 | 0.022003 | 0.037384 | 0.033325 | 0.035889 | 0.10468 | -0.22888 | -0.27924 | -0.32044 | 51.4526 | 51.3245 | 51.3977 | 0 | -0.16937 | 121.994 | -0.39368 | -0.013733 | -122.3099 | 0.07782 | 51.7593 | -70.7062 | -0.086975 | -0.036621 | 0.091553 | 0.3067 | 0.13733 | 51.6312 | 0.027466 | 0.07782 | 122.3007 | 51.7044 | -0.086975 | 0.027466 | 0.07782 | 51.7044 | 51.6312 | 122.3007 | -122.3511 | -122.4243
838.0156 | 122.3831 | -0.27924 | 122.0261 | 0.28229 | 0.0059814 | 0.02179 | 0.033112 | 0.039734 | 0.040588 | 0.11642 | -0.2243 | -0.26093 | -0.27466 | 41.2491 | 41.1575 | 41.3773 | -0.018311 | -0.15106 | 121.994 | -0.35706 | 0.004578 | -122.287 | 0.054932 | 41.5283 | -80.8685 | -0.07782 | -0.032043 | 0.050354 | 0.26092 | 0.12817 | 41.4368 | 0.018311 | 0.054932 | 122.2733 | 41.6565 | -0.07782 | 0.018311 | 0.054932 | 41.6565 | 41.4368 | 122.2733 | -122.3007 | -122.3831
838.9688 | 122.3785 | -0.27008 | 122.0444 | -0.045776 | 0.008545 | 0.024994 | 0.033539 | 0.039307 | 0.044861 | 0.12155 | -0.19684 | -0.25635 | -0.27008 | 36.3007 | 36.2091 | 36.2823 | 0.054932 | -0.11444 | 122.0215 | -0.36163 | 0 | -122.3007 | 0.073243 | 36.5707 | -85.8353 | -0.091552 | -0.022889 | 0.073243 | 0.32501 | 0.15564 | 36.4792 | 0.013733 | 0.073243 | 122.2916 | 36.5524 | -0.091552 | 0.013733 | 0.073243 | 36.5524 | 36.4792 | 122.2916 | -122.3145 | -122.406
839.9688 | 122.3877 | -0.27008 | 122.0535 | -0.022889 | 0.009613 | 0.019013 | 0.034393 | 0.040802 | 0.045715 | 0.12476 | -0.16937 | -0.25635 | -0.27924 | 33.1924 | 33.0917 | 33.1558 | 0.036621 | -0.086975 | 121.9894 | -0.34332 | -0.009155 | -122.3099 | 0.10071 | 33.4625 | -88.9618 | -0.073242 | -0.064087 | 0.10986 | 0.3067 | 0.18311 | 33.3618 | 0.013733 | 0.10071 | 122.2595 | 33.4259 | -0.073242 | 0.013733 | 0.10071 | 33.4259 | 33.3618 | 122.2595 | -122.3328 | -122.3969
840.9688 | 122.3282 | -0.3067 | 122.0627 | 0.038147 | 0.010254 | 0.021362 | 0.037598 | 0.043152 | 0.047638 | 0.12903 | -0.24719 | -0.18768 | -0.29297 | 30.1392 | 30.0568 | 30.1254 | 0.17395 | -0.19226 | 122.0535 | -0.39825 | 0.013733 | -122.2504 | 0.05951 | 30.4459 | -92.0059 | -0.091552 | -0.009155 | 0.045777 | 0.48065 | 0.11444 | 30.3635 | 0.11902 | 0.05951 | 122.3602 | 30.4321 | -0.091552 | 0.11902 | 0.05951 | 30.4321 | 30.3635 | 122.3602 | -122.3557 | -122.4609
842.0156 | 122.3923 | -0.26093 | 122.0352 | 0.41962 | 0.0093994 | 0.022217 | 0.03717 | 0.053833 | 0.055328 | 0.14441 | -0.21057 | -0.24261 | -0.28839 | 16.008 | 15.9393 | 16.0172 | 0.068665 | -0.15106 | 122.0352 | -0.33875 | -0.027466 | -122.2778 | 0.050354 | 16.2689 | -106.0959 | -0.07782 | 0 | 0.07782 | 0.32959 | 0.10986 | 16.2003 | 0.01831 | 0.050354 | 122.2961 | 16.2781 | -0.07782 | 0.01831 | 0.050354 | 16.2781 | 16.2003 | 122.2961 | -122.3236 | -122.374
842.9688 | 122.438 | -0.21057 | 122.0627 | 0.11444 | 0.0091858 | 0.021149 | 0.032471 | 0.05661 | 0.057037 | 0.1521 | -0.16479 | -0.2243 | -0.25177 | 11.0321 | 10.9772 | 11.0229 | 0.10071 | -0.041199 | 122.0169 | -0.30212 | -0.041199 | -122.287 | 0.045776 | 11.2427 | -111.0855 | -0.091553 | -0.045776 | 0.086975 | 0.31128 | 0.16937 | 11.1877 | -0.013733 | 0.045776 | 122.2275 | 11.2335 | -0.091553 | -0.013733 | 0.045776 | 11.2335 | 11.1877 | 122.2275 | -122.3145 | -122.3648
844.0312 | 122.3602 | -0.28381 | 122.049 | 0.045776 | 0.012817 | 0.025421 | 0.039948 | 0.054047 | 0.058319 | 0.15317 | -0.1831 | -0.19684 | -0.29297 | 9.787 | 9.7321 | 9.7549 | 0.20599 | -0.14191 | 122.0627 | -0.37079 | -0.009156 | -122.2458 | 0.10071 | 10.0708 | -112.3169 | -0.086976 | 0.013733 | 0.10986 | 0.48981 | 0.14191 | 10.0159 | 0.086975 | 0.10071 | 122.3465 | 10.0388 | -0.086976 | 0.086975 | 0.10071 | 10.0388 | 10.0159 | 122.3465 | -122.3419 | -122.4197
844.9688 | 122.4335 | -0.23346 | 122.0535 | -0.015259 | 0.0076904 | 0.020721 | 0.033966 | 0.056183 | 0.059387 | 0.15125 | -0.07782 | -0.24719 | -0.2655 | 9.6085 | 9.5215 | 9.6085 | 0.086975 | -0.013733 | 122.0261 | -0.31128 | -0.032044 | -122.3007 | 0.15564 | 9.8419 | -112.532 | -0.07782 | -0.027466 | 0.18768 | 0.32043 | 0.21973 | 9.7549 | -0.013733 | 0.15564 | 122.2595 | 9.8419 | -0.07782 | -0.013733 | 0.15564 | 9.8419 | 9.7549 | 122.2595 | -122.319 | -122.3648
846.0156 | 122.3602 | -0.24719 | 122.0535 | 0.37384 | 0.009613 | 0.022858 | 0.039948 | 0.056183 | 0.058319 | 0.15274 | -0.22888 | -0.21057 | -0.28381 | 9.0271 | 8.9767 | 9.0317 | 0.14648 | -0.19684 | 122.0306 | -0.33875 | -0.036621 | -122.2641 | 0.01831 | 9.2743 | -113.0768 | -0.091553 | -0.022888 | 0.054931 | 0.39368 | 0.050354 | 9.2239 | 0.036621 | 0.01831 | 122.2778 | 9.2789 | -0.091553 | 0.036621 | 0.01831 | 9.2789 | 9.2239 | 122.2778 | -122.3373 | -122.3923
846.9688 | 122.4792 | -0.20599 | 122.0581 | 0.030518 | 0.0079042 | 0.022217 | 0.032257 | 0.054047 | 0.059814 | 0.15466 | -0.1236 | -0.2243 | -0.2243 | 8.8028 | 8.7753 | 8.8211 | 0.07782 | -0.004578 | 122.0078 | -0.29755 | -0.01831 | -122.2824 | 0.082398 | 9.0088 | -113.2828 | -0.091552 | -0.050354 | 0.10071 | 0.28381 | 0.20142 | 8.9813 | -0.01831 | 0.082398 | 122.2137 | 9.0271 | -0.091552 | -0.01831 | 0.082398 | 9.0271 | 8.9813 | 122.2137 | -122.2824 | -122.3557
848.0156 | 122.3053 | -0.26093 | 122.113 | 0.2594 | 0.013245 | 0.025208 | 0.040161 | 0.054047 | 0.059387 | 0.15274 | -0.21973 | -0.21973 | -0.28381 | 9.7 | 9.6542 | 9.7046 | 0.21515 | -0.23346 | 122.0856 | -0.35248 | -0.022888 | -122.3328 | 0.041198 | 9.9609 | -112.4588 | -0.091553 | -0.027466 | 0.064086 | 0.47607 | 0.027466 | 9.9152 | 0.041198 | 0.041198 | 122.3465 | 9.9655 | -0.091553 | 0.041198 | 0.041198 | 9.9655 | 9.9152 | 122.3465 | -122.3969 | -122.4655
848.9844 | 122.2824 | -0.24261 | 122.1268 | -0.015259 | 0.0089722 | 0.019653 | 0.035461 | 0.054474 | 0.057892 | 0.14996 | -0.23346 | -0.19684 | -0.28381 | 9.2514 | 9.2011 | 9.2239 | 0.28839 | 0.022888 | 122.113 | -0.33875 | -0.041198 | -122.3236 | 0.009156 | 9.494 | -112.9257 | -0.09613 | -0.013733 | 0.050354 | 0.53101 | 0.2655 | 9.4437 | 0.045777 | 0.009156 | 122.3557 | 9.4666 | -0.09613 | 0.045777 | 0.009156 | 9.4666 | 9.4437 | 122.3557 | -122.4106 | -122.4655
850.0156 | 122.3602 | -0.27008 | 122.081 | 0.3128 | 0.010895 | 0.023285 | 0.03717 | 0.057892 | 0.056824 | 0.15317 | -0.23804 | -0.19684 | -0.29297 | 8.9218 | 8.8806 | 8.9401 | 0.19684 | -0.20599 | 122.0718 | -0.35248 | -0.022888 | -122.2778 | 0.032044 | 9.1919 | -113.2004 | -0.082397 | -0.009156 | 0.054932 | 0.46692 | 0.064087 | 9.1507 | 0.073243 | 0.032044 | 122.3419 | 9.2102 | -0.082397 | 0.073243 | 0.032044 | 9.2102 | 9.1507 | 122.3419 | -122.374 | -122.4335
850.9688 | 122.438 | -0.24261 | 122.1085 | 0.21362 | 0.010468 | 0.023285 | 0.030121 | 0.055328 | 0.060242 | 0.15488 | -0.19226 | -0.23804 | -0.24261 | 8.7936 | 8.7845 | 8.8303 | 0.14648 | -0.09613 | 122.0627 | -0.28839 | 0 | -122.3465 | 0.050354 | 9.0363 | -113.324 | -0.045776 | -0.045776 | 0.050354 | 0.3891 | 0.14649 | 9.0271 | 0.004578 | 0.050354 | 122.3053 | 9.0729 | -0.045776 | 0.004578 | 0.050354 | 9.0729 | 9.0271 | 122.3053 | -122.3511 | -122.3969
852.0156 | 122.3282 | -0.2655 | 122.1222 | 0.27466 | 0.0098268 | 0.026917 | 0.03952 | 0.054901 | 0.057465 | 0.15445 | -0.23804 | -0.2243 | -0.29755 | 8.5785 | 8.5144 | 8.551 | 0.2243 | -0.2243 | 122.0718 | -0.35706 | -0.032043 | -122.3465 | 0.027466 | 8.844 | -113.6078 | -0.091553 | -0.050354 | 0.059509 | 0.48981 | 0.041199 | 8.7799 | 0.041199 | 0.027466 | 122.3373 | 8.8165 | -0.091553 | 0.041199 | 0.027466 | 8.8165 | 8.7799 | 122.3373 | -122.4197 | -122.4792
852.9688 | 122.438 | -0.24261 | 122.0718 | 0.16022 | 0.0079042 | 0.020935 | 0.030548 | 0.053192 | 0.058533 | 0.15424 | -0.19684 | -0.22888 | -0.24719 | 8.4824 | 8.4641 | 8.5098 | 0.14648 | -0.07782 | 122.0673 | -0.29755 | -0.004577 | -122.3007 | 0.045777 | 8.725 | -113.6078 | -0.054931 | -0.004577 | 0.050354 | 0.3891 | 0.16479 | 8.7067 | 0.013733 | 0.045777 | 122.3099 | 8.7524 | -0.054931 | 0.013733 | 0.045777 | 8.7524 | 8.7067 | 122.3099 | -122.319 | -122.3694
854.0312 | 122.4106 | -0.25635 | 122.0993 | 0.54932 | 0.012817 | 0.024994 | 0.041016 | 0.055969 | 0.061523 | 0.15295 | -0.11444 | -0.13275 | -0.20142 | 8.3496 | 8.2764 | 8.3267 | 0.25177 | -0.14191 | 122.0673 | -0.34332 | 0.054932 | -122.2321 | 0.14191 | 8.606 | -113.8229 | -0.086975 | -0.032043 | 0.086975 | 0.50812 | 0.11444 | 8.5327 | 0.1236 | 0.14191 | 122.3236 | 8.5831 | -0.086975 | 0.1236 | 0.14191 | 8.5831 | 8.5327 | 122.3236 | -122.3007 | -122.4426
854.9688 | 122.4335 | -0.25177 | 122.0901 | -0.045776 | 0.008545 | 0.02243 | 0.031189 | 0.057678 | 0.058533 | 0.1521 | -0.27008 | -0.3067 | -0.29755 | 8.1894 | 8.1482 | 8.2077 | 0.16022 | -0.13733 | 122.0718 | -0.34332 | -0.045776 | -122.3969 | -0.018311 | 8.4412 | -113.942 | -0.091553 | -0.018311 | 0.027465 | 0.41199 | 0.11444 | 8.4 | -0.054932 | -0.018311 | 122.3236 | 8.4595 | -0.091553 | -0.054932 | -0.018311 | 8.4595 | 8.4 | 122.3236 | -122.3877 | -122.4335
856.0156 | 122.4106 | -0.25177 | 122.1039 | 0.16022 | 0.011536 | 0.021576 | 0.03952 | 0.056824 | 0.057678 | 0.15445 | -0.13733 | -0.15564 | -0.20599 | 8.0292 | 7.9605 | 8.0017 | 0.13733 | -0.1236 | 122.0718 | -0.32959 | 0.045776 | -122.2595 | 0.11444 | 8.2809 | -114.1434 | -0.07782 | -0.032044 | 0.068665 | 0.3891 | 0.12817 | 8.2123 | 0.09613 | 0.11444 | 122.3236 | 8.2535 | -0.07782 | 0.09613 | 0.11444 | 8.2535 | 8.2123 | 122.3236 | -122.3099 | -122.4335
856.9688 | 122.4106 | -0.25177 | 122.0901 | -0.038147 | 0.0087586 | 0.024139 | 0.033325 | 0.054047 | 0.060883 | 0.15466 | -0.17853 | -0.21973 | -0.26093 | 7.8735 | 7.8278 | 7.8644 | 0.15106 | -0.10986 | 122.0764 | -0.32501 | -0.009155 | -122.3099 | 0.073242 | 8.1253 | -114.2624 | -0.073242 | -0.013733 | 0.082397 | 0.40283 | 0.14191 | 8.0795 | 0.032043 | 0.073242 | 122.3282 | 8.1161 | -0.073242 | 0.032043 | 0.073242 | 8.1161 | 8.0795 | 122.3282 | -122.3511 | -122.4152
857.9688 | 122.4564 | -0.24719 | 122.0947 | 0.32043 | 0.0089722 | 0.023499 | 0.032898 | 0.053833 | 0.061096 | 0.15723 | -0.19226 | -0.23346 | -0.22888 | 7.6859 | 7.663 | 7.7133 | -0.009155 | -0.11902 | 122.0673 | -0.31586 | 0.01831 | -122.3282 | 0.054931 | 7.933 | -114.4318 | -0.068665 | -0.027466 | 0.036621 | 0.23804 | 0.12817 | 7.9102 | 0.013733 | 0.054931 | 122.3145 | 7.9605 | -0.068665 | 0.013733 | 0.054931 | 7.9605 | 7.9102 | 122.3145 | -122.3236 | -122.4106
859.0312 | 122.3923 | -0.25635 | 122.1268 | 0.19836 | 0.011322 | 0.024567 | 0.040375 | 0.056824 | 0.059814 | 0.15509 | -0.16937 | -0.20599 | -0.27924 | 7.5302 | 7.4844 | 7.5302 | 0.009155 | -0.12817 | 122.081 | -0.3479 | -0.022888 | -122.3328 | 0.086975 | 7.7866 | -114.6423 | -0.091552 | -0.045776 | 0.10986 | 0.2655 | 0.12817 | 7.7408 | 0.050354 | 0.086975 | 122.3373 | 7.7866 | -0.091552 | 0.050354 | 0.086975 | 7.7866 | 7.7408 | 122.3373 | -122.406 | -122.4747
859.9688 | 122.4426 | -0.23346 | 122.1085 | 0.35095 | 0.011322 | 0.024353 | 0.032257 | 0.056183 | 0.060883 | 0.15573 | -0.21057 | -0.21973 | -0.24261 | 7.3929 | 7.3563 | 7.4341 | -0.091553 | -0.10529 | 122.0856 | -0.30212 | -0.009156 | -122.3282 | 0.022888 | 7.6263 | -114.7522 | -0.068665 | -0.022888 | 0.032044 | 0.14191 | 0.12817 | 7.5897 | 0.013732 | 0.022888 | 122.319 | 7.6675 | -0.068665 | 0.013732 | 0.022888 | 7.6675 | 7.5897 | 122.319 | -122.3511 | -122.4106
861.0156 | 122.438 | -0.2655 | 122.1405 | 0.13733 | 0.0098268 | 0.023712 | 0.03952 | 0.056396 | 0.05896 | 0.15509 | -0.17395 | -0.21057 | -0.27924 | 7.3517 | 7.2784 | 7.3105 | -0.032043 | -0.13733 | 122.081 | -0.3479 | -0.013733 | -122.3511 | 0.091553 | 7.6172 | -114.8621 | -0.082397 | -0.059509 | 0.10529 | 0.23346 | 0.12817 | 7.5439 | 0.054932 | 0.091553 | 122.3465 | 7.576 | -0.082397 | 0.054932 | 0.091553 | 7.576 | 7.5439 | 122.3465 | -122.4197 | -122.4884
861.9688 | 122.4655 | -0.22888 | 122.0993 | 0.38147 | 0.008545 | 0.023499 | 0.038666 | 0.057465 | 0.058746 | 0.1553 | -0.15106 | -0.23346 | -0.22888 | 7.3105 | 7.2693 | 7.3425 | -0.13275 | -0.09613 | 122.0993 | -0.29755 | 0 | -122.3328 | 0.07782 | 7.5394 | -114.83 | -0.068664 | 0 | 0.07782 | 0.096131 | 0.13275 | 7.4982 | -0.004577 | 0.07782 | 122.3282 | 7.5714 | -0.068664 | -0.004577 | 0.07782 | 7.5714 | 7.4982 | 122.3282 | -122.3282 | -122.3969
863.0156 | 122.4014 | -0.28839 | 122.113 | 0.038147 | 0.010895 | 0.026489 | 0.039734 | 0.056396 | 0.059601 | 0.15552 | -0.20142 | -0.19226 | -0.28381 | 7.1594 | 7.1091 | 7.1548 | -0.027466 | -0.15106 | 122.081 | -0.33875 | 0.004578 | -122.3053 | 0.086975 | 7.4478 | -115.004 | -0.050354 | -0.032043 | 0.082397 | 0.26093 | 0.13733 | 7.3975 | 0.09613 | 0.086975 | 122.3694 | 7.4432 | -0.050354 | 0.09613 | 0.086975 | 7.4432 | 7.3975 | 122.3694 | -122.3969 | -122.4518
863.9688 | 122.4564 | -0.23804 | 122.1268 | 0.37384 | 0.01004 | 0.023712 | 0.031189 | 0.057678 | 0.060028 | 0.1553 | -0.14191 | -0.20599 | -0.23346 | 7.1228 | 7.0953 | 7.164 | -0.16479 | -0.10529 | 122.1085 | -0.30212 | 0.004578 | -122.3328 | 0.09613 | 7.3608 | -115.0314 | -0.064087 | -0.018311 | 0.091552 | 0.073242 | 0.13275 | 7.3334 | 0.032043 | 0.09613 | 122.3465 | 7.402 | -0.064087 | 0.032043 | 0.09613 | 7.402 | 7.3334 | 122.3465 | -122.3602 | -122.4289
865.0156 | 122.4335 | -0.21973 | 122.2458 | 0.10681 | 0.011536 | 0.024567 | 0.039948 | 0.05896 | 0.058105 | 0.15552 | -0.17395 | -0.20142 | -0.2655 | 7.0267 | 6.9901 | 7.0175 | -0.073242 | -0.10986 | 122.1039 | -0.33417 | -0.045776 | -122.4472 | 0.045777 | 7.2464 | -115.2557 | -0.11444 | -0.14191 | 0.091553 | 0.14649 | 0.10986 | 7.2098 | 0.018311 | 0.045777 | 122.3236 | 7.2372 | -0.11444 | 0.018311 | 0.045777 | 7.2372 | 7.2098 | 122.3236 | -122.5113 | -122.58
865.9688 | 122.5204 | -0.21515 | 122.0993 | 0.061035 | 0.0091858 | 0.018585 | 0.032257 | 0.057678 | 0.060883 | 0.15445 | -0.14191 | -0.21973 | -0.23346 | 7.0221 | 6.9992 | 7.0541 | -0.19684 | -0.013733 | 122.0993 | -0.29755 | -0.01831 | -122.319 | 0.073242 | 7.2372 | -115.1001 | -0.082397 | 0 | 0.091552 | 0.018311 | 0.20142 | 7.2144 | -0.004578 | 0.073242 | 122.3145 | 7.2693 | -0.082397 | -0.004578 | 0.073242 | 7.2693 | 7.2144 | 122.3145 | -122.3328 | -122.3969
867.0156 | 122.4106 | -0.26093 | 122.1313 | 0.061035 | 0.01004 | 0.020935 | 0.038666 | 0.057251 | 0.059387 | 0.15659 | -0.18768 | -0.19684 | -0.28839 | 6.9031 | 6.8665 | 6.8893 | -0.10529 | -0.13733 | 122.1268 | -0.32959 | -0.027466 | -122.3282 | 0.073242 | 7.164 | -115.2649 | -0.068665 | -0.004578 | 0.10071 | 0.15564 | 0.1236 | 7.1274 | 0.064087 | 0.073242 | 122.3877 | 7.1503 | -0.068665 | 0.064087 | 0.073242 | 7.1503 | 7.1274 | 122.3877 | -122.4197 | -122.4609
867.9688 | 122.525 | -0.2243 | 122.0993 | 1.8921 | 0.010681 | 0.022003 | 0.035675 | 0.05896 | 0.058533 | 0.15701 | -0.091553 | -0.27008 | -0.28381 | 6.9214 | 6.9168 | 6.9534 | -0.28839 | -0.073242 | 122.081 | -0.32501 | -0.059509 | -122.3694 | 0.13275 | 7.1457 | -115.1825 | -0.10071 | -0.01831 | 0.19226 | -0.064087 | 0.15106 | 7.1411 | -0.045777 | 0.13275 | 122.3053 | 7.1777 | -0.10071 | -0.045777 | 0.13275 | 7.1777 | 7.1411 | 122.3053 | -122.3831 | -122.4243
869.0156 | 122.3877 | -0.2655 | 122.1634 | -0.045776 | 0.011108 | 0.020081 | 0.035034 | 0.057037 | 0.059601 | 0.15488 | -0.27008 | -0.14648 | -0.25177 | 6.8024 | 6.7703 | 6.7978 | -0.009155 | -0.16937 | 122.1497 | -0.32959 | 0.013733 | -122.3099 | -0.004578 | 7.0679 | -115.3931 | -0.064087 | -0.013733 | -0.018311 | 0.25635 | 0.09613 | 7.0358 | 0.11902 | -0.004578 | 122.4152 | 7.0633 | -0.064087 | 0.11902 | -0.004578 | 7.0633 | 7.0358 | 122.4152 | -122.4152 | -122.493
869.9688 | 122.5067 | -0.20599 | 122.1313 | 0.46539 | 0.0098268 | 0.02713 | 0.038025 | 0.058533 | 0.060028 | 0.1568 | -0.10986 | -0.22888 | -0.21515 | 6.8939 | 6.8481 | 6.9122 | -0.26093 | -0.064087 | 122.0856 | -0.31586 | -0.009155 | -122.3602 | 0.096131 | 7.0999 | -115.2832 | -0.10986 | -0.045777 | 0.10529 | -0.054931 | 0.14191 | 7.0541 | -0.022888 | 0.096131 | 122.2916 | 7.1182 | -0.10986 | -0.022888 | 0.096131 | 7.1182 | 7.0541 | 122.2916 | -122.3465 | -122.4472
871.0312 | 122.406 | -0.23804 | 122.1542 | -0.0076295 | 0.0091858 | 0.021362 | 0.033753 | 0.056824 | 0.059814 | 0.15659 | -0.17853 | -0.1831 | -0.24719 | 6.752 | 6.7154 | 6.7429 | -0.041199 | -0.1236 | 122.1268 | -0.35248 | -0.009155 | -122.3373 | 0.059509 | 6.9901 | -115.4388 | -0.11444 | -0.027466 | 0.068664 | 0.19684 | 0.11444 | 6.9534 | 0.054932 | 0.059509 | 122.3648 | 6.9809 | -0.11444 | 0.054932 | 0.059509 | 6.9809 | 6.9534 | 122.3648 | -122.4014 | -122.5067
871.9688 | 122.5113 | -0.21057 | 122.1771 | 0.21362 | 0.0093994 | 0.022003 | 0.032044 | 0.056183 | 0.060883 | 0.15723 | -0.15106 | -0.19684 | -0.21057 | 6.7383 | 6.7245 | 6.7795 | -0.18768 | -0.045776 | 122.1222 | -0.28839 | 0 | -122.374 | 0.059509 | 6.9489 | -115.4526 | -0.07782 | -0.054932 | 0.059509 | 0.022888 | 0.1648 | 6.9351 | 0.013733 | 0.059509 | 122.3328 | 6.9901 | -0.07782 | 0.013733 | 0.059509 | 6.9901 | 6.9351 | 122.3328 | -122.3877 | -122.4655
873.0156 | 122.4426 | -0.26093 | 122.1909 | 0.068664 | 0.011749 | 0.024353 | 0.038666 | 0.055756 | 0.059601 | 0.1553 | -0.19684 | -0.16937 | -0.27008 | 6.6284 | 6.5781 | 6.6147 | -0.045776 | -0.15106 | 122.1405 | -0.33875 | -0.009156 | -122.3602 | 0.064087 | 6.8893 | -115.6128 | -0.07782 | -0.050354 | 0.073243 | 0.21515 | 0.10986 | 6.839 | 0.091552 | 0.064087 | 122.4014 | 6.8756 | -0.07782 | 0.091552 | 0.064087 | 6.8756 | 6.839 | 122.4014 | -122.4609 | -122.5296
873.9688 | 122.5021 | -0.21057 | 122.168 | 0.5722 | 0.0091858 | 0.02478 | 0.030548 | 0.057678 | 0.059174 | 0.15509 | -0.17853 | -0.27008 | -0.27466 | 6.6284 | 6.5964 | 6.665 | -0.1831 | -0.091553 | 122.1359 | -0.29755 | -0.064087 | -122.4381 | 0.032043 | 6.839 | -115.5716 | -0.086975 | -0.032044 | 0.09613 | 0.027466 | 0.11902 | 6.8069 | -0.05951 | 0.032043 | 122.3465 | 6.8756 | -0.086975 | -0.05951 | 0.032043 | 6.8756 | 6.8069 | 122.3465 | -122.4426 | -122.4655
875.0156 | 122.3969 | -0.22888 | 122.2092 | 0.007629 | 0.011963 | 0.024567 | 0.038025 | 0.058105 | 0.059387 | 0.15445 | -0.20142 | -0.14648 | -0.2655 | 6.5552 | 6.5048 | 6.5414 | -0.045776 | -0.14648 | 122.1863 | -0.32501 | -0.036621 | -122.3557 | 0.027466 | 6.7841 | -115.7043 | -0.09613 | -0.022888 | 0.064087 | 0.18311 | 0.082398 | 6.7337 | 0.082398 | 0.027466 | 122.4152 | 6.7703 | -0.09613 | 0.082398 | 0.027466 | 6.7703 | 6.7337 | 122.4152 | -122.4747 | -122.5342
875.9688 | 122.493 | -0.29755 | 122.1176 | 0.22888 | 0.008545 | 0.023926 | 0.033325 | 0.057251 | 0.05896 | 0.15659 | -0.16479 | -0.21515 | -0.21515 | 6.5277 | 6.5277 | 6.5506 | -0.22888 | -0.29297 | 122.0352 | -0.33417 | 0.082397 | -122.3328 | 0.13275 | 6.8253 | -115.5899 | -0.036621 | -0.082398 | 0.050354 | 0.068664 | 0.004577 | 6.8253 | 0.082397 | 0.13275 | 122.3328 | 6.8481 | -0.036621 | 0.082397 | 0.13275 | 6.8481 | 6.8253 | 122.3328 | -122.3328 | -122.4518
877.0156 | 122.3923 | -0.2243 | 122.1954 | -0.022889 | 0.010254 | 0.026703 | 0.037811 | 0.055969 | 0.059601 | 0.15616 | -0.20599 | -0.16937 | -0.27466 | 6.7154 | 6.5872 | 6.4316 | -0.059509 | -0.13733 | 122.2092 | -0.28839 | -0.050354 | -122.3648 | 0.01831 | 6.9397 | -115.6082 | -0.064087 | 0.013732 | 0.068664 | 0.16479 | 0.086975 | 6.8115 | 0.054931 | 0.01831 | 122.4335 | 6.6559 | -0.064087 | 0.054931 | 0.01831 | 6.6559 | 6.8115 | 122.4335 | -122.4701 | -122.4838
877.9688 | 122.4472 | -0.24261 | 122.1817 | 0.37384 | 0.011108 | 0.025635 | 0.039093 | 0.059814 | 0.060883 | 0.15594 | -0.17395 | -0.16022 | -0.27466 | 6.4224 | 6.3858 | 6.4407 | -0.16479 | -0.15564 | 122.1634 | -0.31586 | -0.032043 | -122.3419 | 0.068665 | 6.665 | -115.7959 | -0.073242 | -0.018311 | 0.10071 | 0.07782 | 0.086975 | 6.6284 | 0.082398 | 0.068665 | 122.406 | 6.6833 | -0.073242 | 0.082398 | 0.068665 | 6.6833 | 6.6284 | 122.406 | -122.4564 | -122.4976
879.0156 | 122.4838 | -0.20599 | 122.1771 | -0.022889 | 0.0098268 | 0.022858 | 0.034393 | 0.057892 | 0.05896 | 0.15659 | -0.1236 | -0.18768 | -0.21057 | 6.4545 | 6.4133 | 6.4407 | -0.15106 | -0.027466 | 122.1497 | -0.28839 | -0.004577 | -122.3648 | 0.082398 | 6.6605 | -115.7639 | -0.082397 | -0.027466 | 0.086975 | 0.054932 | 0.17853 | 6.6193 | 0.018311 | 0.082398 | 122.3557 | 6.6467 | -0.082397 | 0.018311 | 0.082398 | 6.6467 | 6.6193 | 122.3557 | -122.3877 | -122.4655
879.9688 | 122.5021 | -0.23804 | 122.1405 | 0.41962 | 0.012604 | 0.026703 | 0.036102 | 0.058319 | 0.060455 | 0.15808 | -0.15106 | -0.19226 | -0.25635 | 6.4087 | 6.3629 | 6.4087 | -0.21973 | -0.11444 | 122.1497 | -0.28381 | -0.018311 | -122.3328 | 0.086975 | 6.6467 | -115.7776 | -0.045776 | 0.009155 | 0.10529 | 0.01831 | 0.1236 | 6.601 | 0.045776 | 0.086975 | 122.3877 | 6.6467 | -0.045776 | 0.045776 | 0.086975 | 6.6467 | 6.601 | 122.3877 | -122.3969 | -122.4243
881.0312 | 122.5067 | -0.19684 | 122.1634 | 0.37384 | 0.011322 | 0.020935 | 0.032471 | 0.057251 | 0.060669 | 0.15552 | -0.14648 | -0.21515 | -0.23346 | 6.4316 | 6.395 | 6.4453 | -0.2243 | -0.064087 | 122.1359 | -0.29755 | -0.036621 | -122.3785 | 0.050354 | 6.6284 | -115.7684 | -0.10071 | -0.027466 | 0.086975 | -0.027466 | 0.13275 | 6.5918 | -0.018311 | 0.050354 | 122.3328 | 6.6421 | -0.10071 | -0.018311 | 0.050354 | 6.6421 | 6.5918 | 122.3328 | -122.3969 | -122.4609
881.9688 | 122.525 | -0.19226 | 122.1909 | 0.36621 | 0.0074768 | 0.024994 | 0.033112 | 0.055328 | 0.060028 | 0.15659 | -0.086975 | -0.21057 | -0.21515 | 6.4041 | 6.3721 | 6.4316 | -0.24719 | -0.041199 | 122.1542 | -0.29755 | -0.022888 | -122.4014 | 0.10529 | 6.5964 | -115.8188 | -0.10528 | -0.036621 | 0.12817 | -0.054931 | 0.15106 | 6.5643 | -0.01831 | 0.10529 | 122.3465 | 6.6238 | -0.10528 | -0.01831 | 0.10529 | 6.6238 | 6.5643 | 122.3465 | -122.406 | -122.4884
883.0156 | 122.4655 | -0.26093 | 122.2137 | -0.022889 | 0.011963 | 0.023926 | 0.037811 | 0.058746 | 0.060028 | 0.15787 | -0.17853 | -0.16479 | -0.2655 | 6.2576 | 6.2119 | 6.2485 | -0.091553 | -0.1236 | 122.1817 | -0.32044 | -0.004578 | -122.3785 | 0.082397 | 6.5186 | -116.0019 | -0.05951 | -0.032043 | 0.086975 | 0.16937 | 0.13733 | 6.4728 | 0.09613 | 0.082397 | 122.4426 | 6.5094 | -0.05951 | 0.09613 | 0.082397 | 6.5094 | 6.4728 | 122.4426 | -122.4792 | -122.5342
883.9688 | 122.4426 | -0.24719 | 122.1817 | 0.23651 | 0.012177 | 0.026062 | 0.037811 | 0.059601 | 0.062164 | 0.15851 | -0.1831 | -0.13733 | -0.25635 | 6.221 | 6.1752 | 6.2347 | -0.1236 | -0.18768 | 122.2 | -0.32501 | -0.009156 | -122.319 | 0.064087 | 6.4682 | -116.0065 | -0.07782 | 0.01831 | 0.073243 | 0.1236 | 0.059509 | 6.4224 | 0.10986 | 0.064087 | 122.4472 | 6.4819 | -0.07782 | 0.10986 | 0.064087 | 6.4819 | 6.4224 | 122.4472 | -122.4381 | -122.5067
885.0156 | 122.5342 | -0.20142 | 122.1725 | 0.022888 | 0.009613 | 0.022217 | 0.033539 | 0.058533 | 0.059387 | 0.15701 | -0.10986 | -0.21057 | -0.22888 | 6.3309 | 6.3309 | 6.3492 | -0.18768 | -0.013733 | 122.1863 | -0.30212 | -0.027466 | -122.3831 | 0.091553 | 6.5323 | -115.8417 | -0.10071 | 0.013733 | 0.11902 | 0.013733 | 0.18768 | 6.5323 | -0.009155 | 0.091553 | 122.3877 | 6.5506 | -0.10071 | -0.009155 | 0.091553 | 6.5506 | 6.5323 | 122.3877 | -122.4014 | -122.4747
885.9844 | 122.58 | -0.18768 | 122.1954 | 0.1297 | 0.0066224 | 0.023071 | 0.030975 | 0.057465 | 0.058746 | 0.1568 | -0.11902 | -0.20142 | -0.20142 | 6.2897 | 6.2714 | 6.3354 | -0.20599 | 0.004578 | 122.1954 | -0.25177 | -0.013733 | -122.3969 | 0.068664 | 6.4774 | -115.9241 | -0.064087 | 0 | 0.082397 | -0.018311 | 0.19226 | 6.459 | -0.013733 | 0.068664 | 122.3831 | 6.5231 | -0.064087 | -0.013733 | 0.068664 | 6.5231 | 6.459 | 122.3831 | -122.3969 | -122.4472
887.0156 | 122.5616 | -0.20599 | 122.2 | -0.030518 | 0.011963 | 0.026276 | 0.034821 | 0.057037 | 0.060242 | 0.15787 | -0.16937 | -0.20142 | -0.24719 | 6.2942 | 6.2531 | 6.3034 | -0.22888 | 0.004578 | 122.1405 | -0.28839 | -0.041198 | -122.4014 | 0.036621 | 6.5002 | -115.947 | -0.082397 | -0.059509 | 0.077819 | -0.022888 | 0.21057 | 6.459 | 0.004578 | 0.036621 | 122.3465 | 6.5094 | -0.082397 | 0.004578 | 0.036621 | 6.5094 | 6.459 | 122.3465 | -122.4472 | -122.4884
887.9688 | 122.4609 | -0.26093 | 122.2046 | 0.32806 | 0.010254 | 0.027344 | 0.03952 | 0.057465 | 0.059814 | 0.15573 | -0.1831 | -0.15564 | -0.27466 | 6.1432 | 6.0974 | 6.1523 | -0.13275 | -0.17853 | 122.2092 | -0.32044 | -0.013733 | -122.3602 | 0.07782 | 6.4041 | -116.1072 | -0.05951 | 0.004577 | 0.091553 | 0.12817 | 0.082397 | 6.3583 | 0.10529 | 0.07782 | 122.4701 | 6.4133 | -0.05951 | 0.10529 | 0.07782 | 6.4133 | 6.3583 | 122.4701 | -122.4792 | -122.525
888.9688 | 122.4472 | -0.25635 | 122.2183 | 0.3891 | 0.012817 | 0.025635 | 0.039948 | 0.05896 | 0.059387 | 0.15723 | -0.1831 | -0.16479 | -0.25177 | 6.1386 | 6.0883 | 6.134 | -0.11444 | -0.1831 | 122.1909 | -0.32044 | 0.004578 | -122.3831 | 0.073243 | 6.395 | -116.1301 | -0.064087 | -0.027466 | 0.068665 | 0.14191 | 0.073243 | 6.3446 | 0.091553 | 0.073243 | 122.4472 | 6.3904 | -0.064087 | 0.091553 | 0.073243 | 6.3904 | 6.3446 | 122.4472 | -122.4701 | -122.5388
890.0156 | 122.4655 | -0.24719 | 122.2137 | 0.030518 | 0.0098268 | 0.027771 | 0.037598 | 0.059601 | 0.060455 | 0.15808 | -0.18768 | -0.16022 | -0.27466 | 6.1203 | 6.0791 | 6.1066 | -0.068665 | -0.15106 | 122.2092 | -0.3067 | -0.027466 | -122.374 | 0.059509 | 6.3675 | -116.1346 | -0.05951 | -0.004578 | 0.086975 | 0.17853 | 0.09613 | 6.3263 | 0.086975 | 0.059509 | 122.4564 | 6.3538 | -0.05951 | 0.086975 | 0.059509 | 6.3538 | 6.3263 | 122.4564 | -122.4884 | -122.5204
890.9844 | 122.5662 | -0.19226 | 122.2 | 0.11444 | 0.0089722 | 0.023071 | 0.032044 | 0.059814 | 0.060242 | 0.15829 | -0.1236 | -0.19226 | -0.20142 | 6.1935 | 6.1798 | 6.2073 | -0.2243 | -0.013733 | 122.1863 | -0.27924 | -0.009155 | -122.3923 | 0.068665 | 6.3858 | -116.0202 | -0.086975 | -0.013733 | 0.07782 | -0.032043 | 0.17853 | 6.3721 | 0 | 0.068665 | 122.3785 | 6.3995 | -0.086975 | 0 | 0.068665 | 6.3995 | 6.3721 | 122.3785 | -122.4014 | -122.4792
892.0156 | 122.5616 | -0.20599 | 122.1863 | -2.2049 | 0.010468 | 0.025421 | 0.032898 | 0.056183 | 0.062164 | 0.1568 | -0.26093 | -0.21973 | -0.22888 | 6.1752 | 6.1478 | 6.189 | -0.21057 | -0.004578 | 122.1588 | -0.28381 | -0.022888 | -122.406 | -0.054931 | 6.3812 | -116.0385 | -0.077819 | -0.027466 | -0.032043 | -0.004577 | 0.20142 | 6.3538 | -0.013733 | -0.054931 | 122.3648 | 6.395 | -0.077819 | -0.013733 | -0.054931 | 6.395 | 6.3538 | 122.3648 | -122.4152 | -122.4701
892.9688 | 122.5662 | -0.20142 | 122.2 | 0.40436 | 0.011963 | 0.023285 | 0.035034 | 0.059174 | 0.060455 | 0.15851 | -0.086975 | -0.23346 | -0.2243 | 6.1569 | 6.1066 | 6.1752 | -0.27924 | -0.036621 | 122.1909 | -0.27008 | -0.022888 | -122.4335 | 0.11444 | 6.3583 | -116.0934 | -0.068665 | -0.009155 | 0.13733 | -0.07782 | 0.1648 | 6.308 | -0.032043 | 0.11444 | 122.3923 | 6.3766 | -0.068665 | -0.032043 | 0.11444 | 6.3766 | 6.308 | 122.3923 | -122.4243 | -122.4701
894.0156 | 122.4472 | -0.21973 | 122.2412 | -0.053406 | 0.01004 | 0.024353 | 0.038666 | 0.059174 | 0.062164 | 0.15594 | -0.20599 | -0.16022 | -0.24719 | 6.0287 | 5.9738 | 6.0287 | -0.036621 | -0.15564 | 122.2275 | -0.31128 | -0.027465 | -122.4014 | 0.013733 | 6.2485 | -116.2674 | -0.091552 | -0.013733 | 0.041198 | 0.18311 | 0.064087 | 6.1935 | 0.05951 | 0.013733 | 122.4472 | 6.2485 | -0.091552 | 0.05951 | 0.013733 | 6.2485 | 6.1935 | 122.4472 | -122.4884 | -122.5525
894.9688 | 122.4564 | -0.21973 | 122.2229 | 0.30518 | 0.010468 | 0.02713 | 0.039093 | 0.059814 | 0.062805 | 0.15851 | -0.18768 | -0.14648 | -0.23346 | 6.0059 | 5.9784 | 6.0104 | -0.11444 | -0.16937 | 122.2092 | -0.33417 | -0.013732 | -122.3694 | 0.032044 | 6.2256 | -116.2445 | -0.11444 | -0.013733 | 0.045776 | 0.10529 | 0.050354 | 6.1981 | 0.073243 | 0.032044 | 122.4289 | 6.2302 | -0.11444 | 0.073243 | 0.032044 | 6.2302 | 6.1981 | 122.4289 | -122.4564 | -122.5571
895.9844 | 122.5937 | -0.17395 | 122.1817 | 0.20599 | 0.010895 | 0.022644 | 0.030762 | 0.058746 | 0.05896 | 0.15488 | -0.10986 | -0.18768 | -0.19684 | 6.102 | 6.0837 | 6.1386 | -0.21973 | 0.009155 | 122.2366 | -0.25177 | -0.022888 | -122.3694 | 0.064087 | 6.2759 | -116.098 | -0.07782 | 0.054931 | 0.086975 | -0.045777 | 0.1831 | 6.2576 | -0.013733 | 0.064087 | 122.4106 | 6.3126 | -0.07782 | -0.013733 | 0.064087 | 6.3126 | 6.2576 | 122.4106 | -122.3785 | -122.4335
897.0156 | 122.3877 | -0.24261 | 122.3328 | -0.022889 | 0.011536 | 0.023926 | 0.03653 | 0.057892 | 0.059601 | 0.15808 | -0.18768 | -0.15564 | -0.25635 | 5.9875 | 5.9601 | 5.9784 | -0.054932 | -0.14648 | 122.2046 | -0.32959 | -0.013733 | -122.4884 | 0.054932 | 6.2302 | -116.3727 | -0.086975 | -0.12817 | 0.068665 | 0.18768 | 0.096131 | 6.2027 | 0.086975 | 0.054932 | 122.4472 | 6.221 | -0.086975 | 0.086975 | 0.054932 | 6.221 | 6.2027 | 122.4472 | -122.5891 | -122.6624
897.9688 | 122.5662 | -0.1831 | 122.2092 | 0.36621 | 0.010895 | 0.023926 | 0.03418 | 0.059174 | 0.062805 | 0.15552 | -0.10071 | -0.20599 | -0.21057 | 5.9738 | 5.9463 | 6.0059 | -0.2655 | -0.045776 | 122.1725 | -0.2655 | -0.027466 | -122.4152 | 0.082397 | 6.1569 | -116.2628 | -0.082398 | -0.036621 | 0.10986 | -0.082398 | 0.13733 | 6.1295 | -0.022889 | 0.082397 | 122.3557 | 6.189 | -0.082398 | -0.022889 | 0.082397 | 6.189 | 6.1295 | 122.3557 | -122.4197 | -122.4747
899.0156 | 122.5342 | -0.22888 | 122.2183 | -0.030518 | 0.010254 | 0.025208 | 0.035675 | 0.05661 | 0.060028 | 0.15723 | -0.11444 | -0.17395 | -0.23346 | 5.983 | 5.9555 | 5.9738 | -0.14191 | -0.050354 | 122.2046 | -0.32044 | -0.004577 | -122.3923 | 0.11444 | 6.2119 | -116.2628 | -0.091553 | -0.013733 | 0.11902 | 0.086975 | 0.17853 | 6.1844 | 0.054932 | 0.11444 | 122.4335 | 6.2027 | -0.091553 | 0.054932 | 0.11444 | 6.2027 | 6.1844 | 122.4335 | -122.4518 | -122.5388
899.9688 | 122.58 | -0.18768 | 122.2137 | 0.35095 | 0.011749 | 0.025635 | 0.035675 | 0.059814 | 0.059601 | 0.15573 | -0.09613 | -0.21515 | -0.21515 | 5.983 | 5.9372 | 5.9967 | -0.27008 | -0.041199 | 122.2046 | -0.28839 | -0.027466 | -122.4289 | 0.091553 | 6.1707 | -116.2766 | -0.10071 | -0.009155 | 0.11902 | -0.082398 | 0.14648 | 6.1249 | -0.027466 | 0.091553 | 122.3923 | 6.1844 | -0.10071 | -0.027466 | 0.091553 | 6.1844 | 6.1249 | 122.3923 | -122.4289 | -122.5021
901.0469 | 122.5525 | -0.21515 | 122.2092 | 0.17548 | 0.0089722 | 0.026489 | 0.032257 | 0.055969 | 0.061096 | 0.15723 | -0.16479 | -0.2243 | -0.24261 | 5.9097 | 5.8823 | 5.9418 | -0.19684 | -0.068665 | 122.2 | -0.30212 | -0.027466 | -122.4335 | 0.050354 | 6.1249 | -116.3269 | -0.086975 | -0.009155 | 0.07782 | 0.018311 | 0.14648 | 6.0974 | -0.009155 | 0.050354 | 122.4152 | 6.1569 | -0.086975 | -0.009155 | 0.050354 | 6.1569 | 6.0974 | 122.4152 | -122.4518 | -122.5113
901.9688 | 122.493 | -0.24719 | 122.2366 | 0.3891 | 0.013886 | 0.025848 | 0.039307 | 0.056824 | 0.062378 | 0.15936 | -0.1831 | -0.15564 | -0.2655 | 5.8273 | 5.777 | 5.8136 | -0.13275 | -0.16937 | 122.2092 | -0.34332 | -0.018311 | -122.3923 | 0.064087 | 6.0745 | -116.4597 | -0.096131 | -0.027466 | 0.082398 | 0.11444 | 0.077819 | 6.0242 | 0.091552 | 0.064087 | 122.4564 | 6.0608 | -0.096131 | 0.091552 | 0.064087 | 6.0608 | 6.0242 | 122.4564 | -122.5021 | -122.58
903.0156 | 122.4976 | -0.22888 | 122.2549 | 0 | 0.010468 | 0.021362 | 0.03717 | 0.059601 | 0.058533 | 0.15616 | -0.11902 | -0.15564 | -0.25635 | 5.8868 | 5.8594 | 5.8548 | -0.13275 | -0.10529 | 122.2458 | -0.32959 | -0.027466 | -122.4106 | 0.10986 | 6.1157 | -116.3956 | -0.10071 | -0.009155 | 0.13733 | 0.096131 | 0.1236 | 6.0883 | 0.073242 | 0.10986 | 122.4747 | 6.0837 | -0.10071 | 0.073242 | 0.10986 | 6.0837 | 6.0883 | 122.4747 | -122.5113 | -122.5845
903.9688 | 122.6028 | -0.20599 | 122.2092 | -0.091553 | 0.0091858 | 0.027771 | 0.035461 | 0.059814 | 0.062164 | 0.15723 | -0.054932 | -0.23804 | -0.23804 | 5.9006 | 5.9006 | 5.928 | -0.28381 | -0.027466 | 122.2 | -0.30212 | -0.032043 | -122.4472 | 0.15106 | 6.1066 | -116.3086 | -0.09613 | -0.009155 | 0.1831 | -0.077819 | 0.17853 | 6.1066 | -0.032043 | 0.15106 | 122.406 | 6.134 | -0.09613 | -0.032043 | 0.15106 | 6.134 | 6.1066 | 122.406 | -122.4472 | -122.5113
905.0156 | 122.5159 | -0.23346 | 122.2366 | -0.030518 | 0.010254 | 0.023926 | 0.034393 | 0.057037 | 0.060883 | 0.15808 | -0.12817 | -0.17395 | -0.2243 | 5.8365 | 5.7999 | 5.8365 | -0.10986 | -0.059509 | 122.2458 | -0.31586 | 0.009155 | -122.4106 | 0.10528 | 6.0699 | -116.4368 | -0.082398 | 0.009156 | 0.09613 | 0.1236 | 0.17395 | 6.0333 | 0.059509 | 0.10528 | 122.4792 | 6.0699 | -0.082398 | 0.059509 | 0.10528 | 6.0699 | 6.0333 | 122.4792 | -122.4609 | -122.5525
905.9844 | 122.5891 | -0.18768 | 122.2229 | 0.41962 | 0.01004 | 0.028839 | 0.037598 | 0.060242 | 0.060242 | 0.15872 | -0.11902 | -0.1831 | -0.24261 | 5.8319 | 5.7907 | 5.8502 | -0.26093 | -0.068665 | 122.2321 | -0.27924 | -0.054932 | -122.406 | 0.068664 | 6.0196 | -116.4322 | -0.091553 | 0.009156 | 0.1236 | -0.073242 | 0.11902 | 5.9784 | 0.004578 | 0.068664 | 122.4197 | 6.0379 | -0.091553 | 0.004578 | 0.068664 | 6.0379 | 5.9784 | 122.4197 | -122.4655 | -122.5021
906.9844 | 122.612 | -0.2243 | 122.2137 | 0.43488 | 0.011322 | 0.022644 | 0.03952 | 0.059387 | 0.060028 | 0.15765 | -0.082397 | -0.21057 | -0.20142 | 5.8594 | 5.7907 | 5.8228 | -0.28839 | -0.064087 | 122.1771 | -0.32501 | 0.022888 | -122.4243 | 0.14191 | 6.0837 | -116.423 | -0.10071 | -0.036621 | 0.11902 | -0.064087 | 0.16022 | 6.015 | 0.013733 | 0.14191 | 122.4014 | 6.0471 | -0.10071 | 0.013733 | 0.14191 | 6.0471 | 6.015 | 122.4014 | -122.4152 | -122.5388
907.9844 | 122.5342 | -0.20142 | 122.2321 | 0.32806 | 0.010468 | 0.020721 | 0.034821 | 0.057892 | 0.06131 | 0.15829 | -0.14191 | -0.18768 | -0.20599 | 5.7678 | 5.7358 | 5.7861 | -0.21515 | -0.086975 | 122.2321 | -0.28381 | -0.004578 | -122.4197 | 0.059509 | 5.9692 | -116.4963 | -0.082397 | 0 | 0.064087 | -0.013733 | 0.11444 | 5.9372 | 0.013733 | 0.059509 | 122.4335 | 5.9875 | -0.082397 | 0.013733 | 0.059509 | 5.9875 | 5.9372 | 122.4335 | -122.4381 | -122.5159
908.9844 | 122.5983 | -0.21515 | 122.2275 | 0.38147 | 0.0098268 | 0.023712 | 0.036102 | 0.055328 | 0.060669 | 0.15979 | -0.10529 | -0.21973 | -0.23346 | 5.7861 | 5.7541 | 5.8182 | -0.27924 | -0.036621 | 122.1634 | -0.28839 | -0.01831 | -122.4472 | 0.10986 | 6.0013 | -116.4734 | -0.073242 | -0.064087 | 0.12817 | -0.064087 | 0.17853 | 5.9692 | -0.004578 | 0.10986 | 122.3785 | 6.0333 | -0.073242 | -0.004578 | 0.10986 | 6.0333 | 5.9692 | 122.3785 | -122.4609 | -122.5159
910.0312 | 122.4838 | -0.24261 | 122.2549 | 0.16785 | 0.0089722 | 0.02243 | 0.040375 | 0.058533 | 0.056183 | 0.15765 | -0.15106 | -0.17395 | -0.27466 | 5.7449 | 5.69 | 5.7083 | -0.15106 | -0.13275 | 122.2092 | -0.33875 | -0.032043 | -122.4289 | 0.091553 | 5.9875 | -116.5649 | -0.09613 | -0.045777 | 0.1236 | 0.091553 | 0.10986 | 5.9326 | 0.068665 | 0.091553 | 122.4518 | 5.9509 | -0.09613 | 0.068665 | 0.091553 | 5.9509 | 5.9326 | 122.4518 | -122.5296 | -122.5937
911 | 122.5479 | -0.17395 | 122.2183 | 0.35858 | 0.0089722 | 0.020508 | 0.034393 | 0.057251 | 0.061737 | 0.1568 | -0.10986 | -0.21973 | -0.2243 | 5.7861 | 5.7678 | 5.809 | -0.24261 | -0.054932 | 122.2229 | -0.28381 | -0.050354 | -122.4381 | 0.064087 | 5.9601 | -116.4505 | -0.10986 | 0.004577 | 0.11444 | -0.068665 | 0.11902 | 5.9418 | -0.045777 | 0.064087 | 122.3969 | 5.983 | -0.10986 | -0.045777 | 0.064087 | 5.983 | 5.9418 | 122.3969 | -122.4426 | -122.5021
912.0312 | 122.5891 | -0.21515 | 122.2595 | 0.22888 | 0.0089722 | 0.020294 | 0.032257 | 0.057037 | 0.059174 | 0.15829 | -0.15564 | -0.19684 | -0.2243 | 5.7083 | 5.6854 | 5.7541 | -0.18768 | -0.027466 | 122.2229 | -0.28381 | -0.009155 | -122.4564 | 0.059509 | 5.9235 | -116.5741 | -0.068664 | -0.036621 | 0.068664 | 0.027466 | 0.18768 | 5.9006 | 0.018311 | 0.059509 | 122.438 | 5.9692 | -0.068664 | 0.018311 | 0.059509 | 5.9692 | 5.9006 | 122.438 | -122.4838 | -122.5433
912.9844 | 122.5754 | -0.22888 | 122.2366 | 0.015259 | 0.0083314 | 0.022644 | 0.033753 | 0.056824 | 0.059387 | 0.15616 | -0.10986 | -0.21515 | -0.23346 | 5.7632 | 5.7404 | 5.7724 | -0.15106 | 0.21515 | 122.1771 | -0.31128 | -0.004577 | -122.4518 | 0.11902 | 5.9921 | -116.4963 | -0.082397 | -0.059509 | 0.1236 | 0.07782 | 0.44403 | 5.9692 | 0.013733 | 0.11902 | 122.406 | 6.0013 | -0.082397 | 0.013733 | 0.11902 | 6.0013 | 5.9692 | 122.406 | -122.4701 | -122.5479
914.0312 | 122.4838 | -0.23346 | 122.2778 | 0.19073 | 0.010895 | 0.020508 | 0.041657 | 0.059387 | 0.060242 | 0.15851 | -0.12817 | -0.16937 | -0.23804 | 5.7083 | 5.6213 | 5.6671 | -0.14648 | -0.1236 | 122.2458 | -0.32959 | -0.004578 | -122.4472 | 0.10528 | 5.9418 | -116.6565 | -0.096131 | -0.032043 | 0.10986 | 0.086975 | 0.10986 | 5.8548 | 0.064086 | 0.10528 | 122.4792 | 5.9006 | -0.096131 | 0.064086 | 0.10528 | 5.9006 | 5.8548 | 122.4792 | -122.5159 | -122.6074
914.9844 | 122.5891 | -0.19226 | 122.2412 | 0.15259 | 0.0089722 | 0.02179 | 0.032471 | 0.057465 | 0.060669 | 0.15894 | -0.14648 | -0.19226 | -0.21057 | 5.722 | 5.722 | 5.7541 | -0.18768 | -0.022888 | 122.2549 | -0.27466 | -0.01831 | -122.4335 | 0.045777 | 5.9143 | -116.5192 | -0.082397 | 0.013733 | 0.064087 | 0.004578 | 0.16937 | 5.9143 | 0 | 0.045777 | 122.4472 | 5.9463 | -0.082397 | 0 | 0.045777 | 5.9463 | 5.9143 | 122.4472 | -122.4518 | -122.5159
916 | 122.5845 | -0.2243 | 122.2687 | 0.39673 | 0.011322 | 0.025421 | 0.039307 | 0.059174 | 0.057892 | 0.15808 | -0.13275 | -0.18768 | -0.24261 | 5.6808 | 5.6442 | 5.6808 | -0.24261 | -0.082397 | 122.2092 | -0.3067 | -0.018311 | -122.4564 | 0.091553 | 5.9052 | -116.6245 | -0.082398 | -0.05951 | 0.10986 | -0.018311 | 0.14191 | 5.8685 | 0.036621 | 0.091553 | 122.4335 | 5.9052 | -0.082398 | 0.036621 | 0.091553 | 5.9052 | 5.8685 | 122.4335 | -122.5113 | -122.5754
917.0312 | 122.5754 | -0.19226 | 122.2504 | 0.26703 | 0.0081178 | 0.020508 | 0.033753 | 0.05661 | 0.060455 | 0.15808 | -0.18768 | -0.23346 | -0.24261 | 5.6442 | 5.6488 | 5.6992 | -0.21057 | -0.073242 | 122.2412 | -0.28381 | -0.050354 | -122.4838 | 0.004578 | 5.8365 | -116.6016 | -0.091552 | -0.009155 | 0.054932 | -0.01831 | 0.11902 | 5.8411 | -0.041198 | 0.004578 | 122.4335 | 5.8914 | -0.091552 | -0.041198 | 0.004578 | 5.8914 | 5.8411 | 122.4335 | -122.493 | -122.5342
917.9844 | 122.644 | -0.20599 | 122.2549 | 0.091552 | 0.0072632 | 0.022858 | 0.033966 | 0.055328 | 0.063232 | 0.15744 | -0.10529 | -0.21057 | -0.20142 | 5.7266 | 5.6992 | 5.7129 | -0.23804 | 0.027466 | 122.2092 | -0.27008 | 0.004578 | -122.4655 | 0.10071 | 5.9326 | -116.5558 | -0.064087 | -0.045777 | 0.09613 | -0.032043 | 0.23346 | 5.9052 | -0.004577 | 0.10071 | 122.4152 | 5.9189 | -0.064087 | -0.004577 | 0.10071 | 5.9189 | 5.9052 | 122.4152 | -122.4564 | -122.525
919.0469 | 122.5708 | -0.16479 | 122.2824 | 0.38147 | 0.0081178 | 0.02243 | 0.035461 | 0.057678 | 0.05896 | 0.15851 | -0.1236 | -0.22888 | -0.22888 | 5.6717 | 5.6534 | 5.6992 | -0.25177 | -0.027466 | 122.2229 | -0.28839 | -0.064087 | -122.5113 | 0.041199 | 5.8365 | -116.629 | -0.1236 | -0.05951 | 0.10529 | -0.086975 | 0.13733 | 5.8182 | -0.064087 | 0.041199 | 122.3877 | 5.864 | -0.1236 | -0.064087 | 0.041199 | 5.864 | 5.8182 | 122.3877 | -122.5113 | -122.5708
919.9844 | 122.6257 | -0.17853 | 122.2824 | 0.099182 | 0.0098268 | 0.021576 | 0.033753 | 0.055115 | 0.060455 | 0.15894 | -0.11444 | -0.20599 | -0.18768 | 5.6671 | 5.6442 | 5.6946 | -0.21973 | -0.009155 | 122.2412 | -0.26093 | -0.009155 | -122.4884 | 0.064087 | 5.8456 | -116.6382 | -0.082397 | -0.041199 | 0.073242 | -0.041199 | 0.16937 | 5.8228 | -0.027466 | 0.064087 | 122.4197 | 5.8731 | -0.082397 | -0.027466 | 0.064087 | 5.8731 | 5.8228 | 122.4197 | -122.4701 | -122.5433
921.0469 | 122.5159 | -0.23346 | 122.2733 | 0.19073 | 0.01474 | 0.019867 | 0.042511 | 0.058105 | 0.059601 | 0.15787 | -0.11444 | -0.16937 | -0.23804 | 5.5756 | 5.5206 | 5.5573 | -0.13733 | -0.13733 | 122.2275 | -0.32501 | -0.004578 | -122.4426 | 0.11902 | 5.809 | -116.7526 | -0.091553 | -0.045776 | 0.1236 | 0.09613 | 0.09613 | 5.7541 | 0.064086 | 0.11902 | 122.4609 | 5.7907 | -0.091553 | 0.064086 | 0.11902 | 5.7907 | 5.7541 | 122.4609 | -122.5113 | -122.5983
921.9844 | 122.5388 | -0.25635 | 122.2046 | 0.22125 | 0.011536 | 0.023071 | 0.032044 | 0.059601 | 0.057892 | 0.15723 | -0.17395 | -0.20142 | -0.21057 | 5.5527 | 5.5298 | 5.5847 | -0.16937 | -0.16937 | 122.2 | -0.3067 | 0.045777 | -122.406 | 0.082398 | 5.809 | -116.6748 | -0.050354 | -0.004578 | 0.036621 | 0.086975 | 0.086975 | 5.7861 | 0.054932 | 0.082398 | 122.4564 | 5.8411 | -0.050354 | 0.054932 | 0.082398 | 5.8411 | 5.7861 | 122.4564 | -122.4152 | -122.5113
923.0312 | 122.5983 | -0.21057 | 122.2458 | 0.36621 | 0.0089722 | 0.02478 | 0.038879 | 0.058105 | 0.059601 | 0.15894 | -0.12817 | -0.19226 | -0.23346 | 5.571 | 5.5481 | 5.5893 | -0.2655 | -0.07782 | 122.1863 | -0.29297 | -0.022888 | -122.4381 | 0.082397 | 5.7816 | -116.6977 | -0.082398 | -0.05951 | 0.10528 | -0.054932 | 0.13275 | 5.7587 | 0.01831 | 0.082397 | 122.3969 | 5.7999 | -0.082398 | 0.01831 | 0.082397 | 5.7999 | 5.7587 | 122.3969 | -122.4792 | -122.5388
923.9844 | 122.612 | -0.20599 | 122.2916 | 0.16785 | 0.0081178 | 0.022644 | 0.031403 | 0.055328 | 0.05896 | 0.15808 | -0.15106 | -0.20599 | -0.20599 | 5.5573 | 5.5298 | 5.5756 | -0.20142 | -0.027466 | 122.2412 | -0.29297 | 0 | -122.4976 | 0.054932 | 5.7632 | -116.7618 | -0.086975 | -0.050354 | 0.054932 | 0.004578 | 0.17853 | 5.7358 | 0 | 0.054932 | 122.4472 | 5.7816 | -0.086975 | 0 | 0.054932 | 5.7816 | 5.7358 | 122.4472 | -122.4976 | -122.5845
925.0156 | 122.525 | -0.24719 | 122.2824 | 0.045776 | 0.010681 | 0.022644 | 0.036957 | 0.056183 | 0.060242 | 0.15958 | -0.17853 | -0.16479 | -0.26093 | 5.4565 | 5.4245 | 5.4474 | -0.054932 | -0.15106 | 122.2549 | -0.32501 | -0.013733 | -122.4472 | 0.068664 | 5.7037 | -116.8579 | -0.07782 | -0.027466 | 0.082397 | 0.19226 | 0.09613 | 5.6717 | 0.082397 | 0.068664 | 122.5021 | 5.6946 | -0.07782 | 0.082397 | 0.068664 | 5.6946 | 5.6717 | 122.5021 | -122.5433 | -122.6074
926 | 122.5479 | -0.2243 | 122.2412 | 0.38147 | 0.013245 | 0.026276 | 0.038879 | 0.059174 | 0.060242 | 0.15872 | -0.16937 | -0.18768 | -0.25177 | 5.4245 | 5.397 | 5.4428 | -0.16937 | -0.14191 | 122.2321 | -0.32044 | -0.027466 | -122.4289 | 0.054931 | 5.6488 | -116.8442 | -0.096131 | -0.009155 | 0.082397 | 0.054931 | 0.082397 | 5.6213 | 0.036621 | 0.054931 | 122.4564 | 5.6671 | -0.096131 | 0.036621 | 0.054931 | 5.6671 | 5.6213 | 122.4564 | -122.493 | -122.5616
926.9844 | 122.5708 | -0.20599 | 122.2733 | 0.34332 | 0.011749 | 0.026276 | 0.032257 | 0.05896 | 0.060883 | 0.15872 | -0.13733 | -0.21057 | -0.2243 | 5.4932 | 5.4886 | 5.5298 | -0.20599 | -0.07782 | 122.2275 | -0.2655 | -0.01831 | -122.4838 | 0.068665 | 5.6992 | -116.7847 | -0.059509 | -0.045776 | 0.086975 | 0 | 0.12817 | 5.6946 | -0.004577 | 0.068665 | 122.4335 | 5.7358 | -0.059509 | -0.004577 | 0.068665 | 5.7358 | 5.6946 | 122.4335 | -122.4976 | -122.5388
928.0469 | 122.6303 | -0.19684 | 122.2504 | 0.14496 | 0.009613 | 0.024567 | 0.033539 | 0.056396 | 0.059601 | 0.15808 | -0.11444 | -0.19226 | -0.20599 | 5.5527 | 5.5389 | 5.5573 | -0.21515 | 0.009155 | 122.2229 | -0.28381 | -0.009156 | -122.4426 | 0.082397 | 5.7495 | -116.7114 | -0.086975 | -0.027466 | 0.091553 | -0.018311 | 0.20599 | 5.7358 | 0.004577 | 0.082397 | 122.4197 | 5.7541 | -0.086975 | 0.004577 | 0.082397 | 5.7541 | 5.7358 | 122.4197 | -122.4564 | -122.5342
928.9844 | 122.6395 | -0.19684 | 122.2549 | 0.099182 | 0.0098268 | 0.022003 | 0.032898 | 0.057037 | 0.059814 | 0.15851 | -0.13275 | -0.19684 | -0.21515 | 5.5069 | 5.4932 | 5.5664 | -0.16937 | -0.009155 | 122.2183 | -0.27008 | -0.018311 | -122.4518 | 0.064087 | 5.7037 | -116.7618 | -0.073243 | -0.036621 | 0.082398 | 0.027465 | 0.18768 | 5.69 | 0 | 0.064087 | 122.4152 | 5.7632 | -0.073243 | 0 | 0.064087 | 5.7632 | 5.69 | 122.4152 | -122.4701 | -122.525
930.0312 | 122.5845 | -0.20142 | 122.2641 | 0.33569 | 0.0098268 | 0.023285 | 0.032684 | 0.055115 | 0.062592 | 0.15915 | -0.14191 | -0.20599 | -0.2243 | 5.5481 | 5.5298 | 5.571 | -0.13733 | -0.07782 | 122.2275 | -0.29297 | -0.022888 | -122.4701 | 0.059509 | 5.7495 | -116.7343 | -0.091553 | -0.036621 | 0.082397 | 0.064087 | 0.1236 | 5.7312 | -0.004578 | 0.059509 | 122.4289 | 5.7724 | -0.091553 | -0.004578 | 0.059509 | 5.7724 | 5.7312 | 122.4289 | -122.4884 | -122.5571
931 | 122.6349 | -0.20142 | 122.2687 | 0.36621 | 0.010468 | 0.02243 | 0.037384 | 0.057465 | 0.05896 | 0.15808 | -0.11902 | -0.21515 | -0.22888 | 5.6122 | 5.5756 | 5.6305 | -0.17853 | -0.036621 | 122.2229 | -0.27008 | -0.027466 | -122.4838 | 0.082397 | 5.8136 | -116.6931 | -0.068665 | -0.045777 | 0.10986 | 0.022888 | 0.1648 | 5.777 | -0.013733 | 0.082397 | 122.4243 | 5.8319 | -0.068665 | -0.013733 | 0.082397 | 5.8319 | 5.777 | 122.4243 | -122.4976 | -122.5388
932.0312 | 122.6166 | -0.17853 | 122.2641 | 0.38147 | 0.0083314 | 0.019867 | 0.037384 | 0.056183 | 0.060669 | 0.15872 | -0.1236 | -0.21057 | -0.22888 | 5.5298 | 5.5023 | 5.571 | -0.19226 | -0.050354 | 122.2275 | -0.29755 | -0.050354 | -122.4747 | 0.054932 | 5.7083 | -116.7618 | -0.11902 | -0.036621 | 0.10529 | -0.013733 | 0.12817 | 5.6808 | -0.032043 | 0.054932 | 122.406 | 5.7495 | -0.11902 | -0.032043 | 0.054932 | 5.7495 | 5.6808 | 122.406 | -122.493 | -122.5616
932.9844 | 122.58 | -0.20599 | 122.2778 | -0.068665 | 0.0079042 | 0.023926 | 0.035675 | 0.055328 | 0.060669 | 0.15851 | -0.1236 | -0.21057 | -0.23346 | 5.8731 | 5.8319 | 5.8594 | 0.29755 | -0.050354 | 122.2458 | -0.29755 | -0.027465 | -122.4884 | 0.082398 | 6.0791 | -116.4459 | -0.091552 | -0.032043 | 0.10986 | 0.50354 | 0.15564 | 6.0379 | -0.004577 | 0.082398 | 122.4518 | 6.0654 | -0.091552 | -0.004577 | 0.082398 | 6.0654 | 6.0379 | 122.4518 | -122.5113 | -122.5754
934.0469 | 122.6852 | -0.24719 | 122.2092 | 0.43488 | 0.01004 | 0.024353 | 0.039307 | 0.057892 | 0.059814 | 0.15851 | -0.10529 | -0.21057 | -0.2243 | 5.8868 | 5.8456 | 5.9006 | -0.032043 | -0.35706 | 122.1405 | -0.29297 | 0.022888 | -122.4197 | 0.14191 | 6.134 | -116.3635 | -0.045777 | -0.068664 | 0.11902 | 0.21515 | -0.10986 | 6.0928 | 0.036621 | 0.14191 | 122.3877 | 6.1478 | -0.045777 | 0.036621 | 0.14191 | 6.1478 | 6.0928 | 122.3877 | -122.4335 | -122.5021
935 | 122.5479 | -0.27466 | 122.2961 | 0.030518 | 0.011322 | 0.025208 | 0.037811 | 0.058746 | 0.06131 | 0.15787 | -0.1831 | -0.14648 | -0.25177 | 5.9372 | 5.9006 | 5.9235 | 0.55389 | -0.14648 | 122.2641 | -0.35706 | 0.022888 | -122.4426 | 0.091553 | 6.2119 | -116.3956 | -0.082398 | -0.032044 | 0.068665 | 0.82855 | 0.12817 | 6.1752 | 0.12817 | 0.091553 | 122.5388 | 6.1981 | -0.082398 | 0.12817 | 0.091553 | 6.1981 | 6.1752 | 122.5388 | -122.5479 | -122.6532
936.0469 | 122.58 | -0.22888 | 122.2778 | 0.26703 | 0.0089722 | 0.022217 | 0.033112 | 0.057251 | 0.059174 | 0.15851 | -0.16022 | -0.18768 | -0.2243 | 5.7632 | 5.7404 | 5.777 | 0.21057 | -0.086975 | 122.2641 | -0.3067 | 0.004578 | -122.4655 | 0.068665 | 5.9921 | -116.5375 | -0.07782 | -0.013733 | 0.064087 | 0.43945 | 0.14191 | 5.9692 | 0.041199 | 0.068665 | 122.493 | 6.0059 | -0.07782 | 0.041199 | 0.068665 | 6.0059 | 5.9692 | 122.493 | -122.5021 | -122.5845
936.9844 | 122.6028 | -0.2243 | 122.2778 | 0.35095 | 0.0089722 | 0.020721 | 0.034393 | 0.054687 | 0.058319 | 0.15381 | -0.14191 | -0.19226 | -0.22888 | 11.348 | 11.2885 | 11.3617 | 6.0562 | -0.091553 | 122.2229 | -0.28839 | -0.004578 | -122.4701 | 0.082397 | 11.5723 | -110.9894 | -0.064087 | -0.054932 | 0.086975 | 6.2805 | 0.13275 | 11.5128 | 0.032043 | 0.082397 | 122.4472 | 11.586 | -0.064087 | 0.032043 | 0.082397 | 11.586 | 11.5128 | 122.4472 | -122.5067 | -122.5662
938.0156 | 122.6212 | -0.2243 | 122.2733 | 0.94605 | 0.0098268 | 0.023499 | 0.036316 | 0.056824 | 0.062164 | 0.16129 | -0.1831 | -0.26093 | -0.24719 | 5.4611 | 5.452 | 5.5069 | -0.10071 | -0.091553 | 122.2183 | -0.32501 | -0.022888 | -122.5342 | 0.041199 | 5.6854 | -116.8213 | -0.10071 | -0.054931 | 0.064087 | 0.1236 | 0.13275 | 5.6763 | -0.036621 | 0.041199 | 122.4426 | 5.7312 | -0.10071 | -0.036621 | 0.041199 | 5.7312 | 5.6763 | 122.4426 | -122.5204 | -122.5983
938.9844 | 122.525 | -0.25177 | 122.3145 | 0.30518 | 0.0098268 | 0.023926 | 0.043152 | 0.05896 | 0.061523 | 0.15808 | -0.19226 | -0.17853 | -0.27924 | 5.3329 | 5.3055 | 5.3421 | -0.027466 | -0.1831 | 122.2824 | -0.33875 | -0.027466 | -122.493 | 0.059509 | 5.5847 | -117.009 | -0.086975 | -0.032043 | 0.086975 | 0.2243 | 0.068665 | 5.5573 | 0.073242 | 0.059509 | 122.5342 | 5.5939 | -0.086975 | 0.073242 | 0.059509 | 5.5939 | 5.5573 | 122.5342 | -122.5937 | -122.6532
940.0312 | 122.6166 | -0.21057 | 122.2595 | 0.39673 | 0.011108 | 0.02478 | 0.033753 | 0.060028 | 0.06131 | 0.15936 | -0.13733 | -0.21515 | -0.21973 | 5.4337 | 5.4108 | 5.4657 | -0.19684 | -0.045776 | 122.2595 | -0.28839 | -0.009156 | -122.4747 | 0.073242 | 5.6442 | -116.8488 | -0.07782 | 0 | 0.082398 | 0.013733 | 0.1648 | 5.6213 | -0.004578 | 0.073242 | 122.4701 | 5.6763 | -0.07782 | -0.004578 | 0.073242 | 5.6763 | 5.6213 | 122.4701 | -122.4792 | -122.5479
940.9844 | 122.6486 | -0.21973 | 122.3007 | 0.32806 | 0.0081178 | 0.022217 | 0.036102 | 0.058533 | 0.060242 | 0.16086 | -0.12817 | -0.21973 | -0.22888 | 5.4565 | 5.4382 | 5.4977 | -0.1831 | -0.054932 | 122.2412 | -0.28839 | -0.009155 | -122.5204 | 0.091553 | 5.6763 | -116.8625 | -0.068664 | -0.059509 | 0.10071 | 0.036622 | 0.16479 | 5.658 | 0 | 0.091553 | 122.4609 | 5.7175 | -0.068664 | 0 | 0.091553 | 5.7175 | 5.658 | 122.4609 | -122.5296 | -122.5891
942.0156 | 122.6486 | -0.21973 | 122.287 | 0.015259 | 0.0079042 | 0.02243 | 0.033325 | 0.055328 | 0.061096 | 0.15829 | -0.091553 | -0.21057 | -0.21057 | 5.5664 | 5.5435 | 5.5801 | -0.032043 | 0 | 122.2412 | -0.29297 | 0.009156 | -122.4976 | 0.12817 | 5.7861 | -116.7435 | -0.073242 | -0.045776 | 0.11902 | 0.18768 | 0.21973 | 5.7632 | 0.009156 | 0.12817 | 122.4609 | 5.7999 | -0.073242 | 0.009156 | 0.12817 | 5.7999 | 5.7632 | 122.4609 | -122.4976 | -122.58
942.9844 | 122.5845 | -0.2243 | 122.2916 | 0.39673 | 0.010681 | 0.02243 | 0.039948 | 0.059387 | 0.059601 | 0.15808 | -0.17395 | -0.19684 | -0.27924 | 5.4153 | 5.3925 | 5.4108 | -0.013733 | -0.15106 | 122.2916 | -0.32959 | -0.054932 | -122.4884 | 0.050354 | 5.6396 | -116.8991 | -0.10529 | 0 | 0.10529 | 0.21057 | 0.073242 | 5.6168 | 0.027466 | 0.050354 | 122.5159 | 5.6351 | -0.10529 | 0.027466 | 0.050354 | 5.6351 | 5.6168 | 122.5159 | -122.5708 | -122.6212
944.0312 | 122.5616 | -0.23804 | 122.2824 | 0.15259 | 0.012177 | 0.025848 | 0.041229 | 0.060669 | 0.05896 | 0.15723 | -0.13275 | -0.16022 | -0.26093 | 5.4977 | 5.452 | 5.4611 | 0.082397 | -0.13733 | 122.2961 | -0.33875 | -0.022888 | -122.4426 | 0.10529 | 5.7358 | -116.8304 | -0.10071 | 0.013733 | 0.12817 | 0.32043 | 0.10071 | 5.69 | 0.07782 | 0.10529 | 122.5342 | 5.6992 | -0.10071 | 0.07782 | 0.10529 | 5.6992 | 5.69 | 122.5342 | -122.5433 | -122.6212
944.9844 | 122.5891 | -0.23346 | 122.3007 | -0.045776 | 0.010895 | 0.021149 | 0.033966 | 0.058319 | 0.06131 | 0.16107 | -0.14648 | -0.21057 | -0.25635 | 5.5298 | 5.5252 | 5.5435 | 0.10986 | -0.059509 | 122.3053 | -0.3067 | -0.022889 | -122.5113 | 0.086975 | 5.7632 | -116.7755 | -0.073243 | 0.004578 | 0.10986 | 0.34332 | 0.17395 | 5.7587 | 0.022888 | 0.086975 | 122.5388 | 5.777 | -0.073243 | 0.022888 | 0.086975 | 5.777 | 5.7587 | 122.5388 | -122.5571 | -122.6074
945.9844 | 122.5616 | -0.27008 | 122.2961 | 0.23651 | 0.010681 | 0.022644 | 0.041443 | 0.058319 | 0.058319 | 0.15317 | -0.17395 | -0.17395 | -0.2655 | 9.2194 | 8.9493 | 8.9401 | 3.9963 | -0.16937 | 122.2824 | -0.35248 | 0.004578 | -122.4701 | 0.096131 | 9.4894 | -113.3469 | -0.082397 | -0.013733 | 0.091553 | 4.2664 | 0.10071 | 9.2194 | 0.096131 | 0.096131 | 122.5525 | 9.2102 | -0.082397 | 0.096131 | 0.096131 | 9.2102 | 9.2194 | 122.5525 | -122.5616 | -122.6486
946.9844 | 122.525 | -0.19226 | 122.3099 | 0.15259 | 0.012177 | 0.024994 | 0.038452 | 0.059601 | 0.063232 | 0.16043 | -0.14191 | -0.17395 | -0.2655 | 5.3879 | 5.3421 | 5.3329 | -0.10071 | -0.068665 | 122.3328 | -0.25635 | -0.073242 | -122.4838 | 0.050354 | 5.5801 | -116.9678 | -0.064087 | 0.022889 | 0.1236 | 0.091553 | 0.1236 | 5.5344 | 0.018311 | 0.050354 | 122.525 | 5.5252 | -0.064087 | 0.018311 | 0.050354 | 5.5252 | 5.5344 | 122.525 | -122.5754 | -122.5662
948.0312 | 122.5571 | -0.25177 | 122.287 | 0.17548 | 0.010681 | 0.023499 | 0.036957 | 0.061737 | 0.060242 | 0.15872 | -0.14648 | -0.17395 | -0.27466 | 5.2002 | 5.1682 | 5.2002 | -0.11902 | -0.14191 | 122.3053 | -0.31586 | -0.022888 | -122.4609 | 0.10529 | 5.452 | -117.1188 | -0.064087 | 0.018311 | 0.12817 | 0.13275 | 0.10986 | 5.4199 | 0.07782 | 0.10529 | 122.5571 | 5.452 | -0.064087 | 0.07782 | 0.10529 | 5.452 | 5.4199 | 122.5571 | -122.5616 | -122.6028
948.9844 | 122.6257 | -0.23346 | 122.287 | 0.32043 | 0.010468 | 0.018372 | 0.028839 | 0.060028 | 0.06131 | 0.15915 | -0.16022 | -0.19684 | -0.20599 | 5.1773 | 5.1956 | 5.2505 | -0.16937 | -0.11444 | 122.3099 | -0.28839 | 0.027465 | -122.4838 | 0.073242 | 5.4108 | -117.0914 | -0.054932 | 0.022888 | 0.045777 | 0.064086 | 0.11902 | 5.4291 | 0.036621 | 0.073242 | 122.5433 | 5.484 | -0.054932 | 0.036621 | 0.073242 | 5.484 | 5.4291 | 122.5433 | -122.493 | -122.5754
950.0312 | 122.5388 | -0.26093 | 122.3099 | 0.41199 | 0.0093994 | 0.022003 | 0.034821 | 0.058746 | 0.060242 | 0.15979 | -0.2243 | -0.15106 | -0.26093 | 5.1224 | 5.1178 | 5.159 | -0.10529 | -0.19226 | 122.319 | -0.32501 | 0 | -122.4609 | 0.036621 | 5.3833 | -117.1921 | -0.064087 | 0.009156 | 0.036621 | 0.15564 | 0.068664 | 5.3787 | 0.10986 | 0.036621 | 122.58 | 5.4199 | -0.064087 | 0.10986 | 0.036621 | 5.4199 | 5.3787 | 122.58 | -122.5708 | -122.6349
950.9844 | 122.6669 | -0.19684 | 122.2824 | 0.40436 | 0.011963 | 0.022644 | 0.035034 | 0.059387 | 0.058319 | 0.15808 | -0.10529 | -0.21057 | -0.22888 | 5.2368 | 5.2505 | 5.2826 | -0.22888 | -0.059509 | 122.2824 | -0.27466 | -0.032044 | -122.493 | 0.091552 | 5.4337 | -117.0319 | -0.07782 | 0 | 0.1236 | -0.032044 | 0.13733 | 5.4474 | -0.013733 | 0.091552 | 122.4792 | 5.4794 | -0.07782 | -0.013733 | 0.091552 | 5.4794 | 5.4474 | 122.4792 | -122.5113 | -122.5571
952.0312 | 122.5891 | -0.23804 | 122.2824 | 0.16785 | 0.011108 | 0.02713 | 0.039093 | 0.059814 | 0.060455 | 0.15936 | -0.13733 | -0.1831 | -0.24719 | 5.191 | 5.1727 | 5.1865 | -0.068665 | -0.15106 | 122.2778 | -0.33417 | -0.009155 | -122.4655 | 0.10071 | 5.4291 | -117.1097 | -0.09613 | -0.004578 | 0.10986 | 0.16937 | 0.086975 | 5.4108 | 0.054932 | 0.10071 | 122.5159 | 5.4245 | -0.09613 | 0.054932 | 0.10071 | 5.4245 | 5.4108 | 122.5159 | -122.5296 | -122.6166
952.9844 | 122.5662 | -0.25177 | 122.3099 | 0.36621 | 0.01239 | 0.025635 | 0.035034 | 0.060669 | 0.062805 | 0.15936 | -0.19684 | -0.1831 | -0.27008 | 5.2872 | 5.2826 | 5.3192 | 0.086975 | -0.16479 | 122.2916 | -0.32044 | -0.018311 | -122.493 | 0.054932 | 5.5389 | -117.0273 | -0.068665 | -0.01831 | 0.073243 | 0.33874 | 0.086975 | 5.5344 | 0.068665 | 0.054932 | 122.5433 | 5.571 | -0.068665 | 0.068665 | 0.054932 | 5.571 | 5.5344 | 122.5433 | -122.58 | -122.6303
954.0312 | 122.4747 | -0.23804 | 122.3465 | 0.33569 | 0.011108 | 0.025848 | 0.039307 | 0.059174 | 0.062164 | 0.15894 | -0.21973 | -0.16937 | -0.28381 | 5.191 | 5.1819 | 5.2139 | 0.045776 | -0.20142 | 122.319 | -0.33875 | -0.045776 | -122.5159 | 0.01831 | 5.4291 | -117.1646 | -0.10071 | -0.027466 | 0.064086 | 0.28381 | 0.036621 | 5.4199 | 0.068664 | 0.01831 | 122.5571 | 5.452 | -0.10071 | 0.068664 | 0.01831 | 5.452 | 5.4199 | 122.5571 | -122.6303 | -122.6852
954.9844 | 122.5571 | -0.27466 | 122.3099 | 0.25177 | 0.011749 | 0.026917 | 0.035889 | 0.058533 | 0.056397 | 0.15146 | -0.16937 | -0.17395 | -0.28381 | 11.5219 | 11.4761 | 11.8515 | 7.0724 | -0.19226 | 122.3465 | -0.35706 | -0.009155 | -122.4838 | 0.10529 | 11.7966 | -110.8337 | -0.082398 | 0.036622 | 0.11444 | 7.3471 | 0.082397 | 11.7508 | 0.10071 | 0.10529 | 122.6212 | 12.1262 | -0.082398 | 0.10071 | 0.10529 | 12.1262 | 11.7508 | 122.6212 | -122.5937 | -122.6669
956.0312 | 122.6715 | -0.23804 | 122.3099 | 0.015259 | 0.0076904 | 0.023926 | 0.029907 | 0.055542 | 0.058746 | 0.15082 | -0.13275 | -0.2243 | -0.24261 | 10.6796 | 9.9197 | 9.8053 | 4.6829 | -0.009155 | 122.2733 | -0.31128 | -0.004578 | -122.5342 | 0.10529 | 10.9177 | -112.3901 | -0.073242 | -0.036621 | 0.10986 | 4.921 | 0.22888 | 10.1578 | 0.013733 | 0.10529 | 122.5113 | 10.0433 | -0.073242 | 0.013733 | 0.10529 | 10.0433 | 10.1578 | 122.5113 | -122.5525 | -122.6212
956.9844 | 122.6715 | -0.21057 | 122.2916 | 0.39673 | 0.0098268 | 0.025421 | 0.034393 | 0.059174 | 0.060883 | 0.15808 | -0.10071 | -0.2655 | -0.25177 | 5.3696 | 5.3604 | 5.4153 | -0.13275 | -0.041199 | 122.287 | -0.28839 | -0.041199 | -122.5571 | 0.10986 | 5.5801 | -116.9312 | -0.07782 | -0.004578 | 0.15106 | 0.07782 | 0.16937 | 5.571 | -0.054932 | 0.10986 | 122.4976 | 5.6259 | -0.07782 | -0.054932 | 0.10986 | 5.6259 | 5.571 | 122.4976 | -122.5433 | -122.58
957.9844 | 122.5525 | -0.25635 | 122.3282 | 0.27466 | 0.012177 | 0.024994 | 0.038025 | 0.059601 | 0.060669 | 0.16043 | -0.19684 | -0.17853 | -0.27466 | 5.2597 | 5.2414 | 5.2597 | 0.10529 | -0.18768 | 122.3282 | -0.36621 | -0.01831 | -122.5067 | 0.05951 | 5.5161 | -117.0868 | -0.10986 | 0 | 0.07782 | 0.36163 | 0.068665 | 5.4977 | 0.07782 | 0.05951 | 122.5845 | 5.5161 | -0.10986 | 0.07782 | 0.05951 | 5.5161 | 5.4977 | 122.5845 | -122.6028 | -122.6944
958.9844 | 122.5754 | -0.25635 | 122.3099 | 0.16022 | 0.013031 | 0.026062 | 0.040161 | 0.060455 | 0.060883 | 0.15808 | -0.15106 | -0.16479 | -0.27008 | 5.4382 | 5.4108 | 5.4428 | 0.21973 | -0.11902 | 122.3328 | -0.34332 | -0.013733 | -122.4747 | 0.10529 | 5.6946 | -116.8991 | -0.086975 | 0.022889 | 0.11902 | 0.47608 | 0.13733 | 5.6671 | 0.091553 | 0.10529 | 122.5891 | 5.6992 | -0.086975 | 0.091553 | 0.10529 | 5.6992 | 5.6671 | 122.5891 | -122.58 | -122.6532
959.9844 | 122.5388 | -0.27924 | 122.3282 | 0.30518 | 0.012177 | 0.023712 | 0.036102 | 0.063873 | 0.060883 | 0.16043 | -0.19226 | -0.1831 | -0.27008 | 5.2414 | 5.2231 | 5.2368 | 0.09613 | -0.20142 | 122.3465 | -0.35248 | 0.009155 | -122.5113 | 0.086975 | 5.5206 | -117.1051 | -0.073242 | 0.018311 | 0.07782 | 0.37537 | 0.07782 | 5.5023 | 0.096131 | 0.086975 | 122.6257 | 5.5161 | -0.073242 | 0.096131 | 0.086975 | 5.5161 | 5.5023 | 122.6257 | -122.5983 | -122.6807
960.9844 | 122.644 | -0.2243 | 122.2916 | 0.32806 | 0.008545 | 0.026917 | 0.028198 | 0.060028 | 0.059814 | 0.15915 | -0.1831 | -0.20599 | -0.2243 | 5.2826 | 5.2917 | 5.3467 | 0.018311 | -0.091553 | 122.2916 | -0.29297 | 0 | -122.4976 | 0.041199 | 5.5069 | -116.9998 | -0.068665 | 0 | 0.041199 | 0.24261 | 0.13275 | 5.5161 | 0.01831 | 0.041199 | 122.5159 | 5.571 | -0.068665 | 0.01831 | 0.041199 | 5.571 | 5.5161 | 122.5159 | -122.5159 | -122.5845
962.0312 | 122.5937 | -0.25635 | 122.3007 | 0.16785 | 0.011536 | 0.024567 | 0.037598 | 0.058319 | 0.061096 | 0.15701 | -0.11902 | -0.14191 | -0.20142 | 5.3558 | 5.3146 | 5.3421 | 0.10529 | -0.11444 | 122.3145 | -0.36163 | 0.054932 | -122.4426 | 0.13733 | 5.6122 | -116.9861 | -0.10528 | 0.013733 | 0.082397 | 0.36163 | 0.14191 | 5.571 | 0.11444 | 0.13733 | 122.5708 | 5.5984 | -0.10528 | 0.11444 | 0.13733 | 5.5984 | 5.571 | 122.5708 | -122.5021 | -122.6624
962.9844 | 122.7081 | -0.24261 | 122.2366 | 0.39673 | 0.0089722 | 0.023071 | 0.035248 | 0.060882 | 0.060455 | 0.15701 | -0.091553 | -0.19684 | -0.23804 | 5.3558 | 5.3375 | 5.4062 | -0.44403 | -0.19684 | 122.2092 | -0.32044 | 0.004578 | -122.4335 | 0.15106 | 5.5984 | -116.8991 | -0.07782 | -0.027466 | 0.14648 | -0.20142 | 0.045777 | 5.5801 | 0.045777 | 0.15106 | 122.4518 | 5.6488 | -0.07782 | 0.045777 | 0.15106 | 5.6488 | 5.5801 | 122.4518 | -122.4747 | -122.5571
964.0312 | 122.6074 | -0.21973 | 122.3236 | 0.045776 | 0.012177 | 0.02243 | 0.03653 | 0.05896 | 0.06131 | 0.15808 | -0.16022 | -0.1831 | -0.27466 | 5.3421 | 5.3055 | 5.3375 | 0.09613 | -0.10529 | 122.3099 | -0.33875 | -0.054931 | -122.5067 | 0.05951 | 5.5618 | -117.0181 | -0.11902 | -0.013733 | 0.11444 | 0.31586 | 0.11444 | 5.5252 | 0.036622 | 0.05951 | 122.5296 | 5.5573 | -0.11902 | 0.036622 | 0.05951 | 5.5573 | 5.5252 | 122.5296 | -122.5983 | -122.6624
964.9844 | 122.5708 | -0.24719 | 122.319 | 0.26703 | 0.014313 | 0.026062 | 0.034607 | 0.05896 | 0.061096 | 0.16043 | -0.17395 | -0.16022 | -0.27008 | 5.2917 | 5.2689 | 5.3055 | 0.10071 | -0.16022 | 122.3373 | -0.35248 | -0.022889 | -122.4792 | 0.073242 | 5.5389 | -117.0502 | -0.10529 | 0.01831 | 0.096131 | 0.3479 | 0.086975 | 5.5161 | 0.086975 | 0.073242 | 122.5845 | 5.5527 | -0.10529 | 0.086975 | 0.073242 | 5.5527 | 5.5161 | 122.5845 | -122.5891 | -122.6715
966.0156 | 122.6669 | -0.21515 | 122.3236 | 0.030518 | 0.010895 | 0.020721 | 0.030762 | 0.058319 | 0.062592 | 0.15851 | -0.11444 | -0.19684 | -0.22888 | 5.4657 | 5.4565 | 5.4703 | 0.10986 | -0.013733 | 122.3007 | -0.28839 | -0.013733 | -122.5204 | 0.10071 | 5.6808 | -116.8671 | -0.073242 | -0.022888 | 0.11444 | 0.32501 | 0.20142 | 5.6717 | 0.018311 | 0.10071 | 122.5159 | 5.6854 | -0.073242 | 0.018311 | 0.10071 | 5.6854 | 5.6717 | 122.5159 | -122.5525 | -122.612
966.9844 | 122.5616 | -0.26093 | 122.3282 | 0.72479 | 0.011536 | 0.020935 | 0.038025 | 0.060455 | 0.06131 | 0.15787 | -0.15564 | -0.15564 | -0.2655 | 5.4932 | 5.4932 | 5.5389 | 0.2243 | -0.17853 | 122.3145 | -0.35706 | -0.004578 | -122.4838 | 0.10529 | 5.7541 | -116.835 | -0.096131 | -0.013733 | 0.10986 | 0.48523 | 0.082397 | 5.7541 | 0.10529 | 0.10529 | 122.5754 | 5.7999 | -0.096131 | 0.10529 | 0.10529 | 5.7999 | 5.7541 | 122.5754 | -122.5937 | -122.6852
968.0156 | 122.6898 | -0.22888 | 122.3282 | -0.11444 | 0.011108 | 0.019867 | 0.030762 | 0.059387 | 0.061096 | 0.16 | -0.11444 | -0.21973 | -0.25177 | 5.8548 | 5.8228 | 5.8594 | 0.16022 | -0.009155 | 122.319 | -0.29755 | -0.022888 | -122.5479 | 0.11444 | 6.0837 | -116.5054 | -0.068664 | -0.009155 | 0.13733 | 0.3891 | 0.21973 | 6.0516 | 0.009155 | 0.11444 | 122.5479 | 6.0883 | -0.068664 | 0.009155 | 0.11444 | 6.0883 | 6.0516 | 122.5479 | -122.58 | -122.6257
968.9844 | 122.5616 | -0.2655 | 122.3511 | 0.41199 | 0.010895 | 0.024139 | 0.038452 | 0.058533 | 0.061096 | 0.15765 | -0.37537 | -0.15106 | -0.24261 | 5.8502 | 5.7266 | 5.7358 | 0.3067 | -0.19226 | 122.3602 | -0.32501 | 0.022888 | -122.5021 | -0.10986 | 6.1157 | -116.6244 | -0.059509 | 0.009155 | -0.13275 | 0.5722 | 0.073242 | 5.9921 | 0.11444 | -0.10986 | 122.6257 | 6.0013 | -0.059509 | 0.11444 | -0.10986 | 6.0013 | 5.9921 | 122.6257 | -122.5937 | -122.6761
970.0312 | 122.5571 | -0.25177 | 122.3145 | 0.36621 | 0.013245 | 0.023499 | 0.033112 | 0.059601 | 0.059814 | 0.15829 | -0.091553 | -0.16022 | -0.25177 | 5.5618 | 5.4932 | 5.5618 | 0.16022 | -0.19226 | 122.374 | -0.33875 | 0 | -122.4747 | 0.16022 | 5.8136 | -116.8213 | -0.086975 | 0.059509 | 0.16022 | 0.41199 | 0.059509 | 5.7449 | 0.091553 | 0.16022 | 122.6257 | 5.8136 | -0.086975 | 0.091553 | 0.16022 | 5.8136 | 5.7449 | 122.6257 | -122.5662 | -122.6532
970.9844 | 122.6715 | -0.23804 | 122.3145 | 0.28229 | 0.0098268 | 0.023071 | 0.029694 | 0.057465 | 0.063446 | 0.15808 | -0.17853 | -0.20599 | -0.2243 | 5.6946 | 5.6992 | 5.7541 | 0.18768 | -0.082397 | 122.3236 | -0.29755 | 0.013733 | -122.5204 | 0.059509 | 5.9326 | -116.6153 | -0.059509 | 0.009155 | 0.045776 | 0.42572 | 0.15564 | 5.9372 | 0.032043 | 0.059509 | 122.5616 | 5.9921 | -0.059509 | 0.032043 | 0.059509 | 5.9921 | 5.9372 | 122.5616 | -122.5388 | -122.612
971.9844 | 122.6807 | -0.18768 | 122.3099 | 0.38147 | 0.0089722 | 0.024567 | 0.035248 | 0.058105 | 0.061523 | 0.15787 | -0.13275 | -0.20599 | -0.24261 | 5.864 | 5.8411 | 5.9052 | 0.25635 | -0.064087 | 122.3053 | -0.30212 | -0.054932 | -122.5159 | 0.054932 | 6.0516 | -116.4688 | -0.11444 | -0.004577 | 0.10986 | 0.44403 | 0.1236 | 6.0287 | -0.018311 | 0.054932 | 122.493 | 6.0928 | -0.11444 | -0.018311 | 0.054932 | 6.0928 | 6.0287 | 122.493 | -122.5525 | -122.612
973.0312 | 122.6669 | -0.19226 | 122.319 | 0.38147 | 0.0089722 | 0.027344 | 0.030762 | 0.058746 | 0.061096 | 0.15744 | -0.1236 | -0.21515 | -0.23346 | 6.0104 | 6.0013 | 6.0562 | 0.46692 | -0.059509 | 122.319 | -0.28839 | -0.041198 | -122.5342 | 0.068665 | 6.2027 | -116.3177 | -0.09613 | 0 | 0.10986 | 0.65918 | 0.13275 | 6.1935 | -0.022888 | 0.068665 | 122.5113 | 6.2485 | -0.09613 | -0.022888 | 0.068665 | 6.2485 | 6.1935 | 122.5113 | -122.5525 | -122.6074
973.9844 | 122.5754 | -0.27466 | 122.3602 | 0.2594 | 0.011749 | 0.022858 | 0.03952 | 0.058533 | 0.061096 | 0.15765 | -0.1831 | -0.16022 | -0.27924 | 5.571 | 5.5252 | 5.5573 | 0.24261 | -0.17395 | 122.3511 | -0.35706 | -0.004578 | -122.5204 | 0.091553 | 5.8456 | -116.835 | -0.082398 | -0.009155 | 0.096131 | 0.51727 | 0.10071 | 5.7999 | 0.11444 | 0.091553 | 122.6257 | 5.8319 | -0.082398 | 0.11444 | 0.091553 | 5.8319 | 5.7999 | 122.6257 | -122.6395 | -122.7173
974.9844 | 122.58 | -0.25177 | 122.3373 | 0.17548 | 0.013031 | 0.022217 | 0.038239 | 0.06131 | 0.061523 | 0.15744 | -0.13733 | -0.17395 | -0.26093 | 5.5344 | 5.484 | 5.5115 | 0.13733 | -0.14191 | 122.3557 | -0.33417 | -0.009155 | -122.5113 | 0.11444 | 5.7861 | -116.8533 | -0.082397 | 0.018311 | 0.1236 | 0.3891 | 0.10986 | 5.7358 | 0.07782 | 0.11444 | 122.6074 | 5.7632 | -0.082397 | 0.07782 | 0.11444 | 5.7632 | 5.7358 | 122.6074 | -122.5983 | -122.6715
976.0156 | 122.6212 | -0.25177 | 122.3511 | -0.015259 | 0.010681 | 0.024139 | 0.030762 | 0.059814 | 0.063232 | 0.15872 | -0.13275 | -0.18768 | -0.2243 | 5.5344 | 5.5023 | 5.5298 | 0.10986 | -0.059509 | 122.3465 | -0.30212 | 0.027466 | -122.5388 | 0.11902 | 5.7861 | -116.8488 | -0.050354 | -0.004577 | 0.091553 | 0.36163 | 0.19226 | 5.7541 | 0.064087 | 0.11902 | 122.5983 | 5.7816 | -0.050354 | 0.064087 | 0.11902 | 5.7816 | 5.7541 | 122.5983 | -122.5754 | -122.6532
976.9844 | 122.7036 | -0.19684 | 122.3328 | 0.17548 | 0.011108 | 0.024994 | 0.03418 | 0.058746 | 0.059814 | 0.15637 | -0.10986 | -0.24719 | -0.27466 | 5.5298 | 5.4886 | 5.5481 | -0.036621 | -0.045776 | 122.3328 | -0.29755 | -0.07782 | -122.58 | 0.086975 | 5.7266 | -116.8442 | -0.10071 | 0 | 0.1648 | 0.16022 | 0.15106 | 5.6854 | -0.050354 | 0.086975 | 122.5296 | 5.7449 | -0.10071 | -0.050354 | 0.086975 | 5.7449 | 5.6854 | 122.5296 | -122.6074 | -122.6303
978.0156 | 122.7264 | -0.20599 | 122.3099 | 0.16022 | 0.0089722 | 0.025421 | 0.029053 | 0.055542 | 0.061951 | 0.15958 | -0.086975 | -0.17853 | -0.2243 | 5.5664 | 5.5435 | 5.5984 | 0 | 0.036621 | 122.3282 | -0.30212 | -0.01831 | -122.4884 | 0.11902 | 5.7724 | -116.7664 | -0.09613 | 0.018311 | 0.13733 | 0.20599 | 0.24262 | 5.7495 | 0.027466 | 0.11902 | 122.5342 | 5.8044 | -0.09613 | 0.027466 | 0.11902 | 5.8044 | 5.7495 | 122.5342 | -122.5342 | -122.612
978.9844 | 122.5754 | -0.2655 | 122.3694 | 2.1667 | 0.013458 | 0.024994 | 0.041229 | 0.057892 | 0.061951 | 0.15616 | -0.20599 | -0.16022 | -0.22888 | 5.452 | 5.4245 | 5.4703 | 0.15564 | -0.18768 | 122.3648 | -0.32501 | 0.036621 | -122.5296 | 0.059509 | 5.7175 | -116.9449 | -0.059509 | -0.004578 | 0.022888 | 0.42114 | 0.07782 | 5.69 | 0.10529 | 0.059509 | 122.6303 | 5.7358 | -0.059509 | 0.10529 | 0.059509 | 5.7358 | 5.69 | 122.6303 | -122.5983 | -122.6944
980.0312 | 122.6898 | -0.19684 | 122.319 | 0.34332 | 0.010468 | 0.026703 | 0.033966 | 0.060455 | 0.061523 | 0.15723 | -0.09613 | -0.21057 | -0.24261 | 5.5023 | 5.4611 | 5.5206 | -0.041199 | -0.064087 | 122.319 | -0.30212 | -0.045777 | -122.5296 | 0.10071 | 5.6992 | -116.8579 | -0.10529 | 0 | 0.14649 | 0.15564 | 0.13275 | 5.658 | -0.013733 | 0.10071 | 122.5159 | 5.7175 | -0.10529 | -0.013733 | 0.10071 | 5.7175 | 5.658 | 122.5159 | -122.5616 | -122.6212
980.9844 | 122.7127 | -0.21057 | 122.319 | 0.10681 | 0.0079042 | 0.02179 | 0.029694 | 0.057465 | 0.061951 | 0.15894 | -0.11902 | -0.20599 | -0.21515 | 5.5206 | 5.4932 | 5.5435 | 0.064087 | 0.009155 | 122.3557 | -0.27466 | -0.004578 | -122.525 | 0.091552 | 5.7312 | -116.8259 | -0.064087 | 0.036621 | 0.09613 | 0.27466 | 0.21973 | 5.7037 | 0.004577 | 0.091552 | 122.5662 | 5.7541 | -0.064087 | 0.004577 | 0.091552 | 5.7541 | 5.7037 | 122.5662 | -122.5342 | -122.5937
982.0312 | 122.5754 | -0.23804 | 122.3694 | 0.2594 | 0.014313 | 0.026917 | 0.03717 | 0.060242 | 0.060455 | 0.16 | -0.19226 | -0.17395 | -0.27924 | 5.3787 | 5.3375 | 5.3513 | 0.21515 | -0.19684 | 122.3557 | -0.33875 | -0.041199 | -122.5433 | 0.045776 | 5.6168 | -117.0319 | -0.10071 | -0.013733 | 0.086975 | 0.45319 | 0.041199 | 5.5756 | 0.064087 | 0.045776 | 122.5937 | 5.5893 | -0.10071 | 0.064087 | 0.045776 | 5.5893 | 5.5756 | 122.5937 | -122.6486 | -122.7081
982.9844 | 122.6395 | -0.27924 | 122.287 | 0.27466 | 0.009613 | 0.021576 | 0.028839 | 0.058319 | 0.060883 | 0.16 | -0.16937 | -0.21515 | -0.23346 | 5.397 | 5.4016 | 5.452 | 0.027466 | -0.082397 | 122.319 | -0.32501 | 0.045777 | -122.5021 | 0.10986 | 5.6763 | -116.8854 | -0.045776 | 0.032044 | 0.064086 | 0.3067 | 0.19684 | 5.6808 | 0.064087 | 0.10986 | 122.5983 | 5.7312 | -0.045776 | 0.064087 | 0.10986 | 5.7312 | 5.6808 | 122.5983 | -122.5204 | -122.612
984.0312 | 122.6715 | -0.20599 | 122.3419 | 0.37384 | 0.0083314 | 0.020721 | 0.031616 | 0.057678 | 0.06131 | 0.16 | -0.12817 | -0.21515 | -0.2243 | 5.3604 | 5.3421 | 5.397 | 0.027466 | -0.068665 | 122.3282 | -0.28839 | -0.01831 | -122.5571 | 0.07782 | 5.5664 | -116.9998 | -0.082397 | -0.013733 | 0.09613 | 0.23346 | 0.13733 | 5.5481 | -0.009155 | 0.07782 | 122.5342 | 5.603 | -0.082397 | -0.009155 | 0.07782 | 5.603 | 5.5481 | 122.5342 | -122.5662 | -122.6303
984.9844 | 122.6715 | -0.21057 | 122.3648 | 0.22125 | 0.0093994 | 0.023285 | 0.030548 | 0.055969 | 0.059601 | 0.15723 | -0.16937 | -0.21057 | -0.2243 | 5.2872 | 5.278 | 5.3055 | -0.009155 | -0.054932 | 122.3053 | -0.29755 | -0.013733 | -122.5754 | 0.041198 | 5.4977 | -117.0868 | -0.086975 | -0.059509 | 0.054931 | 0.20142 | 0.15564 | 5.4886 | 0 | 0.041198 | 122.5159 | 5.5161 | -0.086975 | 0 | 0.041198 | 5.5161 | 5.4886 | 122.5159 | -122.5891 | -122.6624
986.0469 | 122.58 | -0.2655 | 122.3694 | 0.26703 | 0.011963 | 0.022217 | 0.038666 | 0.057251 | 0.059601 | 0.15701 | -0.17853 | -0.19226 | -0.2655 | 5.2048 | 5.1498 | 5.1727 | 0.036621 | -0.17395 | 122.3328 | -0.3479 | 0 | -122.5616 | 0.086975 | 5.4703 | -117.2195 | -0.082397 | -0.036621 | 0.086975 | 0.30212 | 0.091553 | 5.4153 | 0.073242 | 0.086975 | 122.5983 | 5.4382 | -0.082397 | 0.073242 | 0.086975 | 5.4382 | 5.4153 | 122.5983 | -122.6349 | -122.7173
986.9844 | 122.7127 | -0.20142 | 122.319 | 0.17548 | 0.009613 | 0.023285 | 0.034607 | 0.057465 | 0.061951 | 0.15659 | -0.10986 | -0.26093 | -0.25177 | 5.3009 | 5.2551 | 5.3101 | -0.11444 | -0.050354 | 122.3465 | -0.3067 | -0.050354 | -122.58 | 0.091553 | 5.5023 | -117.0639 | -0.10529 | 0.027466 | 0.14191 | 0.086975 | 0.15106 | 5.4565 | -0.059509 | 0.091553 | 122.5479 | 5.5115 | -0.10529 | -0.059509 | 0.091553 | 5.5115 | 5.4565 | 122.5479 | -122.5708 | -122.6257
988.0156 | 122.5983 | -0.24261 | 122.3648 | -0.022889 | 0.0091858 | 0.022003 | 0.033966 | 0.056396 | 0.059387 | 0.15829 | -0.14191 | -0.17853 | -0.24719 | 5.2597 | 5.2185 | 5.2505 | 0.07782 | -0.10071 | 122.3465 | -0.31128 | -0.004577 | -122.5433 | 0.10071 | 5.5023 | -117.1463 | -0.068664 | -0.01831 | 0.10528 | 0.32044 | 0.14191 | 5.4611 | 0.064087 | 0.10071 | 122.5891 | 5.4932 | -0.068664 | 0.064087 | 0.10071 | 5.4932 | 5.4611 | 122.5891 | -122.612 | -122.6761
988.9844 | 122.7356 | -0.24719 | 122.2366 | 0.26703 | 0.0081178 | 0.022003 | 0.031403 | 0.05661 | 0.059174 | 0.15829 | -0.16937 | -0.21515 | -0.2243 | 5.2734 | 5.2551 | 5.3055 | 0 | -0.086975 | 122.3557 | -0.31128 | 0.022888 | -122.4518 | 0.077819 | 5.5206 | -116.9815 | -0.064087 | 0.11902 | 0.054931 | 0.24719 | 0.16022 | 5.5023 | 0.032043 | 0.077819 | 122.6028 | 5.5527 | -0.064087 | 0.032043 | 0.077819 | 5.5527 | 5.5023 | 122.6028 | -122.4609 | -122.5479
989.9844 | 122.6715 | -0.20142 | 122.3602 | 0.35095 | 0.0079042 | 0.025421 | 0.034821 | 0.055542 | 0.058105 | 0.1568 | -0.11444 | -0.19684 | -0.21973 | 5.3009 | 5.2826 | 5.3101 | -0.004578 | -0.068665 | 122.3145 | -0.29755 | -0.018311 | -122.5571 | 0.086975 | 5.5023 | -117.0776 | -0.09613 | -0.045776 | 0.10529 | 0.19684 | 0.13275 | 5.484 | 0.004578 | 0.086975 | 122.5159 | 5.5115 | -0.09613 | 0.004578 | 0.086975 | 5.5115 | 5.484 | 122.5159 | -122.58 | -122.6578
991.0469 | 122.7081 | -0.21057 | 122.3694 | 0.32806 | 0.011749 | 0.024139 | 0.034607 | 0.057465 | 0.060669 | 0.16214 | -0.10071 | -0.22888 | -0.21973 | 5.4474 | 5.397 | 5.4657 | 0.091553 | -0.036621 | 122.319 | -0.31586 | -0.009156 | -122.5983 | 0.10986 | 5.658 | -116.9724 | -0.10529 | -0.050354 | 0.11902 | 0.30212 | 0.17395 | 5.6076 | -0.018311 | 0.10986 | 122.5296 | 5.6763 | -0.10529 | -0.018311 | 0.10986 | 5.6763 | 5.6076 | 122.5296 | -122.5891 | -122.6852
991.9844 | 122.7081 | -0.22888 | 122.3328 | 0.48828 | 0.011322 | 0.023712 | 0.038879 | 0.058105 | 0.061737 | 0.15872 | -0.09613 | -0.2243 | -0.24719 | 5.4886 | 5.4428 | 5.5023 | 0.11902 | -0.059509 | 122.3373 | -0.30212 | -0.01831 | -122.5571 | 0.13275 | 5.7175 | -116.89 | -0.073242 | 0.004577 | 0.15106 | 0.3479 | 0.16937 | 5.6717 | 0.004578 | 0.13275 | 122.5662 | 5.7312 | -0.073242 | 0.004578 | 0.13275 | 5.7312 | 5.6717 | 122.5662 | -122.58 | -122.6349
993.0156 | 122.644 | -0.24719 | 122.4335 | -0.076294 | 0.010895 | 0.024353 | 0.035889 | 0.054047 | 0.058533 | 0.15509 | -0.20599 | -0.16937 | -0.28839 | 9.2697 | 9.2422 | 9.2285 | 4.4769 | -0.14191 | 122.3923 | -0.34332 | -0.041199 | -122.6028 | 0.041198 | 9.5169 | -113.1912 | -0.096131 | -0.041199 | 0.082397 | 4.7241 | 0.10528 | 9.4894 | 0.077819 | 0.041198 | 122.6395 | 9.4757 | -0.096131 | 0.077819 | 0.041198 | 9.4757 | 9.4894 | 122.6395 | -122.7219 | -122.7768
993.9844 | 122.6257 | -0.23346 | 122.3511 | 0.43488 | 0.010681 | 0.026062 | 0.036957 | 0.061096 | 0.063019 | 0.15894 | -0.16479 | -0.16937 | -0.26093 | 5.2963 | 5.2689 | 5.3009 | 0.09613 | -0.15106 | 122.374 | -0.31586 | -0.027466 | -122.5204 | 0.068664 | 5.5298 | -117.0822 | -0.082398 | 0.022888 | 0.09613 | 0.32959 | 0.082397 | 5.5023 | 0.064086 | 0.068664 | 122.6074 | 5.5344 | -0.082398 | 0.064086 | 0.068664 | 5.5344 | 5.5023 | 122.6074 | -122.612 | -122.6669
995.0156 | 122.5983 | -0.26093 | 122.3694 | -0.061036 | 0.010681 | 0.025635 | 0.033753 | 0.058319 | 0.06131 | 0.15894 | -0.19226 | -0.16479 | -0.25177 | 5.2551 | 5.2322 | 5.2414 | 0.21973 | -0.13733 | 122.406 | -0.34332 | 0.009155 | -122.5342 | 0.068664 | 5.5161 | -117.1371 | -0.082398 | 0.036621 | 0.059509 | 0.48065 | 0.1236 | 5.4932 | 0.09613 | 0.068664 | 122.6669 | 5.5023 | -0.082398 | 0.09613 | 0.068664 | 5.5023 | 5.4932 | 122.6669 | -122.6212 | -122.7127
995.9844 | 122.7264 | -0.20599 | 122.3602 | 0.14496 | 0.009613 | 0.021576 | 0.030335 | 0.058533 | 0.059387 | 0.15851 | -0.13275 | -0.17853 | -0.19684 | 5.4337 | 5.4199 | 5.4382 | 0.16022 | -0.004578 | 122.3648 | -0.25635 | 0.009156 | -122.5388 | 0.073243 | 5.6396 | -116.9403 | -0.050354 | 0.004578 | 0.064087 | 0.36621 | 0.20142 | 5.6259 | 0.027466 | 0.073243 | 122.5708 | 5.6442 | -0.050354 | 0.027466 | 0.073243 | 5.6442 | 5.6259 | 122.5708 | -122.5571 | -122.6166
997.0312 | 122.7036 | -0.19684 | 122.3602 | 0.36621 | 0.0083314 | 0.023712 | 0.034821 | 0.057465 | 0.063019 | 0.15829 | -0.10071 | -0.2243 | -0.21515 | 5.5389 | 5.5161 | 5.5664 | 0.25635 | -0.045776 | 122.3465 | -0.28839 | -0.018311 | -122.5845 | 0.09613 | 5.7358 | -116.8442 | -0.091553 | -0.013732 | 0.11444 | 0.45319 | 0.15106 | 5.7129 | -0.027466 | 0.09613 | 122.5433 | 5.7632 | -0.091553 | -0.027466 | 0.09613 | 5.7632 | 5.7129 | 122.5433 | -122.5754 | -122.6486
997.9844 | 122.7036 | -0.20142 | 122.3648 | 0.21362 | 0.010468 | 0.022644 | 0.032898 | 0.056396 | 0.060669 | 0.15765 | -0.16479 | -0.21057 | -0.22888 | 5.4245 | 5.4291 | 5.4474 | 0.23804 | -0.050354 | 122.319 | -0.29755 | -0.027466 | -122.5754 | 0.036621 | 5.6259 | -116.9357 | -0.09613 | -0.045776 | 0.064087 | 0.43945 | 0.15106 | 5.6305 | -0.009155 | 0.036621 | 122.5204 | 5.6488 | -0.09613 | -0.009155 | 0.036621 | 5.6488 | 5.6305 | 122.5204 | -122.5937 | -122.6624
999.0312 | 122.6532 | -0.2243 | 122.3694 | 0.40436 | 0.01239 | 0.026703 | 0.038239 | 0.057678 | 0.062378 | 0.15958 | -0.15564 | -0.18768 | -0.27008 | 5.397 | 5.3558 | 5.4108 | 0.27466 | -0.13733 | 122.3557 | -0.33417 | -0.045777 | -122.5571 | 0.068664 | 5.6213 | -117.0135 | -0.10986 | -0.013733 | 0.11444 | 0.49896 | 0.086975 | 5.5801 | 0.036621 | 0.068664 | 122.58 | 5.6351 | -0.10986 | 0.036621 | 0.068664 | 5.6351 | 5.5801 | 122.58 | -122.6395 | -122.7036
999.9844 | 122.7127 | -0.18768 | 122.3465 | 0.41199 | 0.010681 | 0.021149 | 0.037598 | 0.058533 | 0.061096 | 0.15936 | -0.10986 | -0.18768 | -0.24719 | 5.2277 | 5.1819 | 5.2322 | -0.073242 | -0.050354 | 122.3419 | -0.30212 | -0.059509 | -122.5342 | 0.07782 | 5.4153 | -117.1646 | -0.11444 | -0.004578 | 0.13733 | 0.11444 | 0.13733 | 5.3696 | 0 | 0.07782 | 122.5296 | 5.4199 | -0.11444 | 0 | 0.07782 | 5.4199 | 5.3696 | 122.5296 | -122.5937 | -122.6486
1001.0312 | 122.7173 | -0.20142 | 122.3602 | 0.19073 | 0.0076904 | 0.026703 | 0.029907 | 0.057892 | 0.061096 | 0.15894 | -0.14191 | -0.19226 | -0.24261 | 5.1773 | 5.1819 | 5.2139 | -0.004578 | -0.022888 | 122.3648 | -0.29297 | -0.041199 | -122.5525 | 0.059509 | 5.3787 | -117.1783 | -0.091553 | 0.004578 | 0.10071 | 0.19684 | 0.17853 | 5.3833 | 0.009155 | 0.059509 | 122.5662 | 5.4153 | -0.091553 | 0.009155 | 0.059509 | 5.4153 | 5.3833 | 122.5662 | -122.6028 | -122.6532
1001.9844 | 122.612 | -0.27466 | 122.374 | 0.24414 | 0.011749 | 0.02713 | 0.039948 | 0.057678 | 0.059601 | 0.15829 | -0.15106 | -0.18768 | -0.26093 | 5.0995 | 5.0583 | 5.0812 | 0.086975 | -0.15106 | 122.3694 | -0.3479 | 0.013733 | -122.5616 | 0.1236 | 5.3741 | -117.3157 | -0.073242 | -0.004577 | 0.10986 | 0.36163 | 0.1236 | 5.3329 | 0.086975 | 0.1236 | 122.644 | 5.3558 | -0.073242 | 0.086975 | 0.1236 | 5.3558 | 5.3329 | 122.644 | -122.6349 | -122.7219
1003.0312 | 122.6898 | -0.21057 | 122.3419 | 0.3128 | 0.0079042 | 0.023285 | 0.032044 | 0.060028 | 0.060669 | 0.16 | -0.15564 | -0.19684 | -0.23346 | 5.1224 | 5.127 | 5.1682 | 0.027466 | -0.082397 | 122.3602 | -0.30212 | -0.022888 | -122.5388 | 0.054931 | 5.3329 | -117.215 | -0.091553 | 0.01831 | 0.077819 | 0.23804 | 0.12817 | 5.3375 | 0.013733 | 0.054931 | 122.5708 | 5.3787 | -0.091553 | 0.013733 | 0.054931 | 5.3787 | 5.3375 | 122.5708 | -122.5754 | -122.644
1003.9844 | 122.7219 | -0.21515 | 122.3511 | 0.41199 | 0.01004 | 0.026062 | 0.039093 | 0.057251 | 0.060242 | 0.15765 | -0.12817 | -0.19226 | -0.24261 | 5.1865 | 5.1453 | 5.1956 | -0.018311 | -0.068665 | 122.3373 | -0.29297 | -0.027466 | -122.5433 | 0.086975 | 5.4016 | -117.2058 | -0.07782 | -0.013733 | 0.11444 | 0.19684 | 0.14648 | 5.3604 | 0.022888 | 0.086975 | 122.5525 | 5.4108 | -0.07782 | 0.022888 | 0.086975 | 5.4108 | 5.3604 | 122.5525 | -122.5937 | -122.644
1005.0312 | 122.6944 | -0.18768 | 122.3602 | 0.34332 | 0.010681 | 0.024139 | 0.030548 | 0.056824 | 0.060883 | 0.16086 | -0.12817 | -0.19226 | -0.22888 | 5.2048 | 5.2002 | 5.2505 | 0.10986 | -0.064087 | 122.3648 | -0.29755 | -0.041199 | -122.5525 | 0.059509 | 5.3925 | -117.16 | -0.10986 | 0.004578 | 0.10071 | 0.29755 | 0.1236 | 5.3879 | -0.004578 | 0.059509 | 122.5525 | 5.4382 | -0.10986 | -0.004578 | 0.059509 | 5.4382 | 5.3879 | 122.5525 | -122.5891 | -122.6578
1005.9844 | 122.7081 | -0.20142 | 122.3419 | 0.33569 | 0.011749 | 0.023071 | 0.036957 | 0.058746 | 0.06131 | 0.15851 | -0.11444 | -0.25635 | -0.24261 | 5.5664 | 5.5252 | 5.571 | 0.33417 | -0.036621 | 122.3282 | -0.27466 | -0.041199 | -122.5983 | 0.086975 | 5.7678 | -116.8167 | -0.073242 | -0.013733 | 0.12817 | 0.53558 | 0.1648 | 5.7266 | -0.054932 | 0.086975 | 122.5296 | 5.7724 | -0.073242 | -0.054932 | 0.086975 | 5.7724 | 5.7266 | 122.5296 | -122.5845 | -122.6166
1007.0156 | 122.6166 | -0.26093 | 122.4106 | -0.12207 | 0.0093994 | 0.018799 | 0.035034 | 0.057251 | 0.062805 | 0.15701 | -0.17853 | -0.16022 | -0.24261 | 5.0812 | 5.0537 | 5.0766 | 0.12817 | -0.13275 | 122.3831 | -0.35248 | 0.01831 | -122.5708 | 0.082397 | 5.3421 | -117.3569 | -0.091553 | -0.027465 | 0.064087 | 0.3891 | 0.12817 | 5.3146 | 0.10071 | 0.082397 | 122.644 | 5.3375 | -0.091553 | 0.10071 | 0.082397 | 5.3375 | 5.3146 | 122.644 | -122.6532 | -122.7631
1007.9844 | 122.6212 | -0.2655 | 122.3648 | 0.28229 | 0.013458 | 0.020935 | 0.03717 | 0.060669 | 0.060028 | 0.16 | -0.17853 | -0.14191 | -0.24719 | 5.0858 | 5.0354 | 5.0629 | 0.073242 | -0.17853 | 122.3969 | -0.3479 | 0.018311 | -122.5067 | 0.086975 | 5.3513 | -117.3294 | -0.082397 | 0.032044 | 0.068664 | 0.33874 | 0.086975 | 5.3009 | 0.1236 | 0.086975 | 122.6624 | 5.3284 | -0.082397 | 0.1236 | 0.086975 | 5.3284 | 5.3009 | 122.6624 | -122.612 | -122.7127
1008.9844 | 122.6852 | -0.1831 | 122.3785 | 0.37384 | 0.008545 | 0.02478 | 0.033539 | 0.059174 | 0.061096 | 0.15808 | -0.11444 | -0.19684 | -0.22888 | 5.1498 | 5.1178 | 5.1544 | -0.050354 | -0.059509 | 122.3831 | -0.28381 | -0.045777 | -122.5754 | 0.068664 | 5.3329 | -117.2607 | -0.10071 | 0.004578 | 0.11444 | 0.13275 | 0.1236 | 5.3009 | -0.013733 | 0.068664 | 122.5662 | 5.3375 | -0.10071 | -0.013733 | 0.068664 | 5.3375 | 5.3009 | 122.5662 | -122.6074 | -122.6624
1010.0156 | 122.731 | -0.19684 | 122.3648 | -1.1978 | 0.008545 | 0.020508 | 0.032257 | 0.057251 | 0.060883 | 0.15915 | -0.082397 | -0.20142 | -0.24261 | 5.1498 | 5.1453 | 5.1636 | -0.022888 | 0.009155 | 122.3602 | -0.3067 | -0.045777 | -122.5662 | 0.11444 | 5.3467 | -117.2195 | -0.10986 | -0.004578 | 0.16022 | 0.17395 | 0.20599 | 5.3421 | -0.004578 | 0.11444 | 122.5571 | 5.3604 | -0.10986 | -0.004578 | 0.11444 | 5.3604 | 5.3421 | 122.5571 | -122.6074 | -122.6715
1010.9844 | 122.6852 | -0.20142 | 122.4014 | 0.35095 | 0.0091858 | 0.021149 | 0.033112 | 0.055969 | 0.059814 | 0.15765 | -0.1236 | -0.19684 | -0.21515 | 5.1041 | 5.0949 | 5.1453 | -0.004578 | -0.073242 | 122.3969 | -0.28839 | -0.013733 | -122.5983 | 0.07782 | 5.3055 | -117.3065 | -0.086975 | -0.004577 | 0.091553 | 0.19684 | 0.12817 | 5.2963 | 0.004578 | 0.07782 | 122.5983 | 5.3467 | -0.086975 | 0.004578 | 0.07782 | 5.3467 | 5.2963 | 122.5983 | -122.6166 | -122.6898
1012.0156 | 122.6761 | -0.21515 | 122.3969 | -0.030518 | 0.011749 | 0.022217 | 0.035675 | 0.057678 | 0.061951 | 0.15829 | -0.11444 | -0.18768 | -0.23346 | 5.1361 | 5.0995 | 5.1132 | 0.068665 | -0.059509 | 122.3785 | -0.32044 | -0.01831 | -122.5845 | 0.10071 | 5.3513 | -117.2974 | -0.10529 | -0.018311 | 0.11902 | 0.28381 | 0.15564 | 5.3146 | 0.027466 | 0.10071 | 122.5937 | 5.3284 | -0.10529 | 0.027466 | 0.10071 | 5.3284 | 5.3146 | 122.5937 | -122.6303 | -122.7173
1012.9844 | 122.6395 | -0.24261 | 122.4014 | 0.36621 | 0.011322 | 0.022858 | 0.039734 | 0.058533 | 0.060883 | 0.16 | -0.1831 | -0.15106 | -0.27008 | 5.072 | 5.0446 | 5.0674 | 0.082397 | -0.16022 | 122.3877 | -0.3479 | -0.027466 | -122.5525 | 0.05951 | 5.3146 | -117.3569 | -0.10528 | -0.013733 | 0.086976 | 0.32501 | 0.082398 | 5.2872 | 0.091553 | 0.05951 | 122.6303 | 5.3101 | -0.10528 | 0.091553 | 0.05951 | 5.3101 | 5.2872 | 122.6303 | -122.6715 | -122.7493
1014.0156 | 122.6303 | -0.23346 | 122.4014 | -0.068665 | 0.010468 | 0.020294 | 0.033966 | 0.056824 | 0.061096 | 0.15744 | -0.14191 | -0.17395 | -0.2243 | 5.1407 | 5.1361 | 5.1361 | 0.17395 | -0.09613 | 122.3923 | -0.32044 | 0.009155 | -122.5754 | 0.091552 | 5.3741 | -117.2653 | -0.086976 | -0.009155 | 0.082397 | 0.40741 | 0.13733 | 5.3696 | 0.059509 | 0.091552 | 122.6257 | 5.3696 | -0.086976 | 0.059509 | 0.091552 | 5.3696 | 5.3696 | 122.6257 | -122.6257 | -122.7219
1014.9844 | 122.6212 | -0.24261 | 122.4197 | 0.36621 | 0.011963 | 0.025635 | 0.042297 | 0.061096 | 0.057892 | 0.15958 | -0.1831 | -0.16022 | -0.28381 | 5.2231 | 5.1453 | 5.2048 | 0.26093 | -0.15106 | 122.4426 | -0.31128 | -0.041198 | -122.58 | 0.05951 | 5.4657 | -117.2745 | -0.068664 | 0.022888 | 0.10071 | 0.50354 | 0.091553 | 5.3879 | 0.082398 | 0.05951 | 122.6852 | 5.4474 | -0.068664 | 0.082398 | 0.05951 | 5.4474 | 5.3879 | 122.6852 | -122.7036 | -122.731
1016.0312 | 122.7264 | -0.22888 | 122.3602 | 0.41962 | 0.011322 | 0.02179 | 0.033539 | 0.061951 | 0.060455 | 0.15936 | -0.14191 | -0.18768 | -0.24719 | 5.0858 | 5.0674 | 5.0949 | 0.004578 | -0.091553 | 122.3511 | -0.3067 | -0.01831 | -122.5479 | 0.086975 | 5.3146 | -117.2928 | -0.07782 | -0.009155 | 0.10528 | 0.23346 | 0.13733 | 5.2963 | 0.041199 | 0.086975 | 122.58 | 5.3238 | -0.07782 | 0.041199 | 0.086975 | 5.3238 | 5.2963 | 122.58 | -122.6074 | -122.6669
1016.9844 | 122.5937 | -0.24719 | 122.4106 | 0.28992 | 0.010895 | 0.028412 | 0.037811 | 0.060028 | 0.060669 | 0.16193 | -0.21515 | -0.17853 | -0.27924 | 5.0583 | 5.0079 | 5.0354 | 0.20142 | -0.20142 | 122.4152 | -0.33875 | -0.032044 | -122.5891 | 0.032043 | 5.3055 | -117.4026 | -0.091553 | 0.004578 | 0.064087 | 0.44861 | 0.045776 | 5.2551 | 0.068664 | 0.032043 | 122.6624 | 5.2826 | -0.091553 | 0.068664 | 0.032043 | 5.2826 | 5.2551 | 122.6624 | -122.6898 | -122.7493
1018.0312 | 122.7173 | -0.21973 | 122.3694 | 0.3891 | 0.011963 | 0.024353 | 0.03418 | 0.060028 | 0.060455 | 0.1553 | -0.10986 | -0.18768 | -0.24719 | 8.9676 | 8.963 | 9.0042 | 4.1245 | -0.054932 | 122.3602 | -0.29297 | -0.027465 | -122.5571 | 0.10986 | 9.1873 | -113.4064 | -0.073242 | -0.009156 | 0.13733 | 4.3442 | 0.16479 | 9.1827 | 0.032044 | 0.10986 | 122.58 | 9.2239 | -0.073242 | 0.032044 | 0.10986 | 9.2239 | 9.1827 | 122.58 | -122.6166 | -122.6624
1018.9844 | 122.6624 | -0.24261 | 122.4197 | 0.16785 | 0.010468 | 0.020508 | 0.03717 | 0.059814 | 0.060883 | 0.16193 | -0.09613 | -0.11902 | -0.21515 | 5.0079 | 4.9622 | 4.9942 | 0.013733 | -0.09613 | 122.4289 | -0.33417 | 0.027466 | -122.5388 | 0.14649 | 5.2505 | -117.4576 | -0.091552 | 0.009155 | 0.11902 | 0.25635 | 0.14649 | 5.2048 | 0.1236 | 0.14649 | 122.6715 | 5.2368 | -0.091552 | 0.1236 | 0.14649 | 5.2368 | 5.2048 | 122.6715 | -122.6349 | -122.7539
1020.0312 | 122.7356 | -0.20599 | 122.3877 | 0.030518 | 0.011322 | 0.020508 | 0.032684 | 0.059814 | 0.06131 | 0.15872 | -0.10071 | -0.18768 | -0.21973 | 5.0491 | 5.0491 | 5.0629 | 0.004578 | 0 | 122.3877 | -0.28381 | -0.013733 | -122.5754 | 0.10529 | 5.2551 | -117.3386 | -0.077819 | 0 | 0.11902 | 0.21057 | 0.20599 | 5.2551 | 0.018311 | 0.10529 | 122.5937 | 5.2689 | -0.077819 | 0.018311 | 0.10529 | 5.2689 | 5.2551 | 122.5937 | -122.6074 | -122.6715
1020.9844 | 122.612 | -0.25177 | 122.4197 | 0.27466 | 0.012817 | 0.030335 | 0.040161 | 0.063446 | 0.060028 | 0.15723 | -0.17395 | -0.16937 | -0.25635 | 4.9118 | 4.9026 | 4.9026 | 0.07782 | -0.1831 | 122.4197 | -0.32044 | -0.004578 | -122.5891 | 0.07782 | 5.1636 | -117.5171 | -0.068665 | 0 | 0.082398 | 0.32959 | 0.068665 | 5.1544 | 0.082397 | 0.07782 | 122.6715 | 5.1544 | -0.068665 | 0.082397 | 0.07782 | 5.1544 | 5.1544 | 122.6715 | -122.6761 | -122.7402
1022.0312 | 122.7264 | -0.19684 | 122.406 | 0.39673 | 0.011963 | 0.02179 | 0.035248 | 0.062164 | 0.060883 | 0.16193 | -0.12817 | -0.19226 | -0.25635 | 4.985 | 4.9805 | 5.0262 | -0.045776 | -0.07782 | 122.3923 | -0.3067 | -0.05951 | -122.5983 | 0.068664 | 5.1819 | -117.4255 | -0.10986 | -0.013733 | 0.12817 | 0.15106 | 0.11902 | 5.1773 | 0.004577 | 0.068664 | 122.5891 | 5.2231 | -0.10986 | 0.004577 | 0.068664 | 5.2231 | 5.1773 | 122.5891 | -122.6624 | -122.7127
1022.9844 | 122.6715 | -0.23804 | 122.3969 | 0.083923 | 0.011322 | 0.022003 | 0.035889 | 0.061523 | 0.061951 | 0.15915 | -0.15564 | -0.15106 | -0.27466 | 5.0034 | 4.9942 | 5.0125 | 0.073242 | -0.091553 | 122.3923 | -0.32044 | -0.036621 | -122.5479 | 0.082397 | 5.2414 | -117.4026 | -0.082398 | -0.004578 | 0.11902 | 0.31128 | 0.14648 | 5.2322 | 0.086975 | 0.082397 | 122.6303 | 5.2505 | -0.082398 | 0.086975 | 0.082397 | 5.2505 | 5.2322 | 122.6303 | -122.6715 | -122.7173
1024.0312 | 122.6852 | -0.16937 | 122.438 | 0.11444 | 0.011108 | 0.026703 | 0.036957 | 0.06131 | 0.061096 | 0.16257 | -0.11902 | -0.16937 | -0.26093 | 5.1682 | 5.0812 | 5.0903 | 0.15106 | -0.036621 | 122.4747 | -0.24261 | -0.091552 | -122.6074 | 0.050354 | 5.3375 | -117.3569 | -0.073242 | 0.036621 | 0.14191 | 0.32044 | 0.13275 | 5.2506 | 0 | 0.050354 | 122.644 | 5.2597 | -0.073242 | 0 | 0.050354 | 5.2597 | 5.2506 | 122.644 | -122.699 | -122.6807
1024.9844 | 122.6578 | -0.22888 | 122.4106 | 0.17548 | 0.011536 | 0.025635 | 0.035461 | 0.06131 | 0.061523 | 0.15894 | -0.10071 | -0.13275 | -0.24719 | 5.0217 | 5.0125 | 5.0034 | 0.10986 | -0.10986 | 122.438 | -0.32501 | -0.01831 | -122.5433 | 0.12817 | 5.2505 | -117.3981 | -0.09613 | 0.027466 | 0.14648 | 0.33875 | 0.11902 | 5.2414 | 0.096131 | 0.12817 | 122.6669 | 5.2322 | -0.09613 | 0.096131 | 0.12817 | 5.2322 | 5.2414 | 122.6669 | -122.6578 | -122.7356
1026.0469 | 122.7081 | -0.19226 | 122.3923 | 0.38147 | 0.012604 | 0.020294 | 0.02948 | 0.059387 | 0.059601 | 0.15915 | -0.10529 | -0.20142 | -0.21973 | 5.0674 | 5.0858 | 5.1224 | 0.013733 | -0.032043 | 122.4197 | -0.27466 | -0.027466 | -122.5937 | 0.086975 | 5.2597 | -117.3065 | -0.082397 | 0.027466 | 0.11444 | 0.20599 | 0.16022 | 5.278 | -0.009155 | 0.086975 | 122.612 | 5.3146 | -0.082397 | -0.009155 | 0.086975 | 5.3146 | 5.278 | 122.612 | -122.612 | -122.6669
1026.9844 | 122.6761 | -0.2243 | 122.3923 | 0.083923 | 0.010895 | 0.02243 | 0.037811 | 0.060455 | 0.062164 | 0.15915 | -0.14648 | -0.15564 | -0.25635 | 5.1315 | 5.1041 | 5.1315 | 0.25177 | -0.09613 | 122.4335 | -0.31586 | -0.032044 | -122.5479 | 0.07782 | 5.3558 | -117.2882 | -0.091553 | 0.041199 | 0.10986 | 0.47607 | 0.12817 | 5.3284 | 0.068664 | 0.07782 | 122.6578 | 5.3558 | -0.091553 | 0.068664 | 0.07782 | 5.3558 | 5.3284 | 122.6578 | -122.6486 | -122.7081
1028.0156 | 122.699 | -0.19226 | 122.3923 | 0.3128 | 0.0093994 | 0.023285 | 0.031616 | 0.059814 | 0.062164 | 0.15915 | -0.14191 | -0.16479 | -0.20142 | 5.0812 | 5.0949 | 5.1453 | 0.17395 | -0.064087 | 122.3923 | -0.29755 | -0.009155 | -122.5571 | 0.050354 | 5.2734 | -117.2974 | -0.10528 | 0 | 0.059509 | 0.36621 | 0.12817 | 5.2872 | 0.027466 | 0.050354 | 122.5845 | 5.3375 | -0.10528 | 0.027466 | 0.050354 | 5.3375 | 5.2872 | 122.5845 | -122.5937 | -122.6898
1028.9844 | 122.6624 | -0.23346 | 122.4472 | 0.18311 | 0.011749 | 0.024139 | 0.036957 | 0.060882 | 0.060669 | 0.15701 | -0.11444 | -0.13275 | -0.21973 | 7.2647 | 7.1869 | 7.2098 | 2.5131 | -0.091553 | 122.4106 | -0.3067 | 0.013732 | -122.58 | 0.11902 | 7.4982 | -115.2603 | -0.073243 | -0.036622 | 0.10529 | 2.7466 | 0.14191 | 7.4203 | 0.10071 | 0.11902 | 122.644 | 7.4432 | -0.073243 | 0.10071 | 0.11902 | 7.4432 | 7.4203 | 122.644 | -122.6669 | -122.7539
1030.0312 | 122.731 | -0.19226 | 122.4014 | 0.053405 | 0.010895 | 0.020081 | 0.030762 | 0.059387 | 0.060883 | 0.15872 | -0.091553 | -0.19226 | -0.20599 | 4.9484 | 4.9484 | 4.9713 | 0.004578 | 0 | 122.438 | -0.28839 | -0.013733 | -122.5937 | 0.10071 | 5.1407 | -117.453 | -0.09613 | 0.036621 | 0.11444 | 0.19684 | 0.19226 | 5.1407 | 0 | 0.10071 | 122.6303 | 5.1636 | -0.09613 | 0 | 0.10071 | 5.1636 | 5.1407 | 122.6303 | -122.6074 | -122.6898
1030.9844 | 122.7219 | -0.21057 | 122.2778 | 0.25177 | 0.0079042 | 0.020935 | 0.030548 | 0.060242 | 0.061523 | 0.15958 | -0.16479 | -0.21515 | -0.22888 | 4.8706 | 4.8614 | 4.9118 | -0.018311 | -0.068665 | 122.4243 | -0.29297 | -0.018311 | -122.493 | 0.045776 | 5.0812 | -117.4164 | -0.082398 | 0.14648 | 0.064087 | 0.19226 | 0.14191 | 5.072 | -0.004578 | 0.045776 | 122.6349 | 5.1224 | -0.082398 | -0.004578 | 0.045776 | 5.1224 | 5.072 | 122.6349 | -122.5067 | -122.5708
1032.0312 | 122.7173 | -0.19684 | 122.5296 | 0.083923 | 0.013031 | 0.025635 | 0.036743 | 0.060669 | 0.061737 | 0.15979 | -0.11444 | -0.16479 | -0.23346 | 4.8843 | 4.8523 | 4.8569 | 0.036621 | -0.09613 | 122.4609 | -0.30212 | -0.036621 | -122.6944 | 0.082397 | 5.0812 | -117.6773 | -0.10529 | -0.068665 | 0.11902 | 0.23346 | 0.10071 | 5.0491 | 0.032043 | 0.082397 | 122.6578 | 5.0537 | -0.10529 | 0.032043 | 0.082397 | 5.0537 | 5.0491 | 122.6578 | -122.7631 | -122.8317
1032.9844 | 122.6486 | -0.24261 | 122.4289 | 0.29755 | 0.011749 | 0.020294 | 0.036957 | 0.060028 | 0.06131 | 0.15872 | -0.17853 | -0.14648 | -0.25635 | 4.7882 | 4.7836 | 4.7699 | 0.022888 | -0.15106 | 122.4655 | -0.32959 | -0.013733 | -122.5754 | 0.064087 | 5.0308 | -117.6453 | -0.086975 | 0.036621 | 0.07782 | 0.2655 | 0.091553 | 5.0262 | 0.096131 | 0.064087 | 122.7081 | 5.0125 | -0.086975 | 0.096131 | 0.064087 | 5.0125 | 5.0262 | 122.7081 | -122.6852 | -122.7585
1034.0312 | 122.6212 | -0.25177 | 122.4243 | 0.25177 | 0.012817 | 0.02478 | 0.038025 | 0.060669 | 0.060455 | 0.15958 | -0.15106 | -0.15564 | -0.25177 | 4.8248 | 4.8111 | 4.7928 | 0.059509 | -0.13275 | 122.4426 | -0.31586 | 0 | -122.58 | 0.10071 | 5.0766 | -117.6132 | -0.064087 | 0.018311 | 0.10071 | 0.31128 | 0.11902 | 5.0629 | 0.09613 | 0.10071 | 122.6944 | 5.0446 | -0.064087 | 0.09613 | 0.10071 | 5.0446 | 5.0629 | 122.6944 | -122.6761 | -122.7402
1034.9844 | 122.6761 | -0.25177 | 122.4426 | 0.007629 | 0.011108 | 0.023926 | 0.033753 | 0.05896 | 0.061737 | 0.16086 | -0.1831 | -0.14648 | -0.26093 | 4.8523 | 4.8477 | 4.8569 | 0.12817 | -0.1236 | 122.4701 | -0.31128 | -0.009155 | -122.5891 | 0.068665 | 5.1041 | -117.5949 | -0.059509 | 0.027466 | 0.07782 | 0.37994 | 0.12817 | 5.0995 | 0.10529 | 0.068665 | 122.7219 | 5.1086 | -0.059509 | 0.10529 | 0.068665 | 5.1086 | 5.0995 | 122.7219 | -122.7036 | -122.7539
1035.9844 | 122.7676 | -0.18768 | 122.406 | 0.1297 | 0.0079042 | 0.023712 | 0.030335 | 0.060882 | 0.060455 | 0.15894 | -0.09613 | -0.25177 | -0.26093 | 5.0262 | 5.0262 | 5.072 | 0.004578 | -0.036621 | 122.4152 | -0.25635 | -0.073242 | -122.6578 | 0.091553 | 5.2139 | -117.3798 | -0.068665 | 0.009155 | 0.1648 | 0.19226 | 0.15106 | 5.2139 | -0.064087 | 0.091553 | 122.6028 | 5.2597 | -0.068665 | -0.064087 | 0.091553 | 5.2597 | 5.2139 | 122.6028 | -122.6669 | -122.6624
1037.0156 | 122.7402 | -0.20599 | 122.3923 | 0.37384 | 0.0091858 | 0.024353 | 0.030975 | 0.058746 | 0.062378 | 0.15979 | -0.10529 | -0.20599 | -0.21057 | 4.9026 | 4.8981 | 4.9255 | -0.022888 | -0.027466 | 122.4152 | -0.29755 | -0.004577 | -122.5983 | 0.10071 | 5.1086 | -117.4942 | -0.091552 | 0.022888 | 0.10529 | 0.18311 | 0.17853 | 5.1041 | 0 | 0.10071 | 122.6212 | 5.1315 | -0.091552 | 0 | 0.10071 | 5.1315 | 5.1041 | 122.6212 | -122.6028 | -122.6898
1037.9844 | 122.6761 | -0.25177 | 122.4289 | -0.0076295 | 0.011322 | 0.025208 | 0.033539 | 0.057465 | 0.062164 | 0.15872 | -0.17853 | -0.15106 | -0.2655 | 4.8431 | 4.8111 | 4.8294 | 0.16937 | -0.11902 | 122.4197 | -0.32501 | -0.013733 | -122.58 | 0.073242 | 5.0949 | -117.6178 | -0.073242 | -0.009155 | 0.086975 | 0.42114 | 0.13275 | 5.0629 | 0.10071 | 0.073242 | 122.6715 | 5.0812 | -0.073242 | 0.10071 | 0.073242 | 5.0812 | 5.0629 | 122.6715 | -122.6944 | -122.7539
1039.0156 | 122.7631 | -0.1831 | 122.4152 | 0.091552 | 0.010254 | 0.026276 | 0.033112 | 0.058533 | 0.060669 | 0.15851 | -0.10986 | -0.23346 | -0.25177 | 5.0217 | 5.0125 | 5.04 | 0.064087 | -0.022888 | 122.4243 | -0.28839 | -0.068665 | -122.6486 | 0.073242 | 5.2048 | -117.4026 | -0.10529 | 0.009155 | 0.14191 | 0.24719 | 0.16022 | 5.1956 | -0.050354 | 0.073242 | 122.6074 | 5.2231 | -0.10529 | -0.050354 | 0.073242 | 5.2231 | 5.1956 | 122.6074 | -122.6669 | -122.7036
1039.9844 | 122.699 | -0.17395 | 122.4243 | 0.11444 | 0.011749 | 0.024994 | 0.038879 | 0.059601 | 0.061737 | 0.15958 | 0.21057 | -0.13733 | -0.19684 | 4.8523 | 4.8248 | 4.8248 | 0.059509 | -0.059509 | 122.4426 | -0.27924 | -0.022888 | -122.5616 | 0.38452 | 5.0262 | -117.5995 | -0.10529 | 0.018311 | 0.40741 | 0.23346 | 0.11444 | 4.9988 | 0.036621 | 0.38452 | 122.6166 | 4.9988 | -0.10529 | 0.036621 | 0.38452 | 4.9988 | 4.9988 | 122.6166 | -122.6212 | -122.7036
1041.0469 | 122.7219 | -0.21515 | 122.4152 | 0.25177 | 0.0074768 | 0.020935 | 0.02948 | 0.058533 | 0.062592 | 0.16086 | -0.14648 | -0.20599 | -0.2243 | 4.8935 | 4.8752 | 4.9072 | 0.032043 | -0.041199 | 122.4426 | -0.29755 | -0.009155 | -122.6212 | 0.068665 | 5.1086 | -117.54 | -0.082397 | 0.027466 | 0.07782 | 0.24719 | 0.17395 | 5.0903 | 0.009155 | 0.068665 | 122.6578 | 5.1224 | -0.082397 | 0.009155 | 0.068665 | 5.1224 | 5.0903 | 122.6578 | -122.6395 | -122.7127
1041.9844 | 122.6807 | -0.17395 | 122.5433 | 0.11444 | 0.011749 | 0.024994 | 0.041443 | 0.059387 | 0.060455 | 0.15765 | -0.1236 | -0.14648 | -0.23804 | 4.8248 | 4.8019 | 4.7928 | 0.036621 | -0.086975 | 122.4472 | -0.3067 | -0.064087 | -122.6898 | 0.050354 | 4.9988 | -117.7414 | -0.13275 | -0.09613 | 0.11444 | 0.21057 | 0.086975 | 4.9759 | 0.027466 | 0.050354 | 122.6212 | 4.9667 | -0.13275 | 0.027466 | 0.050354 | 4.9667 | 4.9759 | 122.6212 | -122.7814 | -122.85
1043.0156 | 122.7676 | -0.19684 | 122.4106 | 0.32043 | 0.008545 | 0.022858 | 0.032471 | 0.058746 | 0.061951 | 0.16171 | -0.10071 | -0.21057 | -0.21515 | 4.8935 | 4.8706 | 4.9026 | -0.091553 | -0.009155 | 122.4472 | -0.2655 | -0.018311 | -122.6212 | 0.09613 | 5.0903 | -117.54 | -0.068665 | 0.036622 | 0.11444 | 0.10529 | 0.18768 | 5.0674 | -0.013733 | 0.09613 | 122.644 | 5.0995 | -0.068665 | -0.013733 | 0.09613 | 5.0995 | 5.0674 | 122.644 | -122.6257 | -122.6761
1043.9844 | 122.6898 | -0.24261 | 122.4426 | 0.045776 | 0.011749 | 0.024139 | 0.037598 | 0.057678 | 0.061951 | 0.15616 | -0.17395 | -0.13275 | -0.25177 | 4.7791 | 4.7562 | 4.7562 | 0.10986 | -0.13275 | 122.4747 | -0.32959 | -0.009155 | -122.5754 | 0.068665 | 5.0217 | -117.6865 | -0.086975 | 0.032043 | 0.07782 | 0.35248 | 0.10986 | 4.9988 | 0.10986 | 0.068665 | 122.7173 | 4.9988 | -0.086975 | 0.10986 | 0.068665 | 4.9988 | 4.9988 | 122.7173 | -122.6944 | -122.7722
1045.0312 | 122.6852 | -0.21057 | 122.438 | 0.14496 | 0.009613 | 0.022644 | 0.037384 | 0.059814 | 0.062164 | 0.16043 | -0.07782 | -0.09613 | -0.16022 | 4.866 | 4.8294 | 4.8248 | 0.045776 | -0.07782 | 122.4426 | -0.28839 | 0.050354 | -122.5342 | 0.13275 | 5.0766 | -117.6086 | -0.07782 | 0.004578 | 0.082397 | 0.25635 | 0.13275 | 5.04 | 0.11444 | 0.13275 | 122.6532 | 5.0354 | -0.07782 | 0.11444 | 0.13275 | 5.0354 | 5.04 | 122.6532 | -122.5983 | -122.7264
1045.9844 | 122.6578 | -0.25177 | 122.4289 | 0.21362 | 0.011749 | 0.021576 | 0.038025 | 0.061951 | 0.061951 | 0.15872 | -0.14191 | -0.16022 | -0.25177 | 4.8294 | 4.8111 | 4.7882 | 0.054932 | -0.13275 | 122.4701 | -0.32501 | 0 | -122.5891 | 0.10986 | 5.0812 | -117.6178 | -0.073242 | 0.041199 | 0.10986 | 0.3067 | 0.11902 | 5.0629 | 0.091553 | 0.10986 | 122.7219 | 5.04 | -0.073242 | 0.091553 | 0.10986 | 5.04 | 5.0629 | 122.7219 | -122.6807 | -122.7539
1047.0156 | 122.7264 | -0.20142 | 122.438 | 0.32043 | 0.008545 | 0.026062 | 0.029053 | 0.059601 | 0.062378 | 0.15979 | -0.09613 | -0.19226 | -0.20599 | 4.8843 | 4.8981 | 4.8935 | -0.041199 | -0.013733 | 122.406 | -0.2655 | -0.004578 | -122.6303 | 0.10529 | 5.0858 | -117.54 | -0.064087 | -0.032043 | 0.10986 | 0.16022 | 0.18768 | 5.0995 | 0.009155 | 0.10529 | 122.6074 | 5.0949 | -0.064087 | 0.009155 | 0.10529 | 5.0949 | 5.0995 | 122.6074 | -122.644 | -122.7036
1047.9844 | 122.6669 | -0.16022 | 122.4792 | 0.15259 | 0.011536 | 0.029053 | 0.03717 | 0.057465 | 0.062378 | 0.15958 | -0.11902 | -0.14648 | -0.2243 | 4.9393 | 5.0308 | 4.9438 | 0.28839 | -0.073242 | 122.525 | -0.25177 | -0.064087 | -122.6257 | 0.041198 | 5.0995 | -117.4484 | -0.091553 | 0.045776 | 0.10529 | 0.44861 | 0.086975 | 5.191 | 0.013733 | 0.041198 | 122.6852 | 5.1041 | -0.091553 | 0.013733 | 0.041198 | 5.1041 | 5.191 | 122.6852 | -122.7036 | -122.731
1049.0312 | 122.6624 | -0.24261 | 122.4564 | -0.030518 | 0.011108 | 0.022858 | 0.035461 | 0.060455 | 0.061951 | 0.15894 | -0.19226 | -0.11902 | -0.24261 | 4.866 | 4.8431 | 4.834 | 0.26093 | -0.12817 | 122.493 | -0.33417 | 0 | -122.5754 | 0.050354 | 5.1086 | -117.6132 | -0.091552 | 0.036621 | 0.050354 | 0.50354 | 0.11444 | 5.0858 | 0.1236 | 0.050354 | 122.7356 | 5.0766 | -0.091552 | 0.1236 | 0.050354 | 5.0766 | 5.0858 | 122.7356 | -122.699 | -122.7905
1049.9844 | 122.6074 | -0.20142 | 122.5708 | 0.14496 | 0.010468 | 0.025208 | 0.034607 | 0.05896 | 0.062805 | 0.15808 | -0.11444 | -0.15106 | -0.22888 | 4.8614 | 4.8477 | 4.8111 | 0.10529 | -0.082397 | 122.4701 | -0.31128 | -0.027466 | -122.7219 | 0.086975 | 5.0629 | -117.7231 | -0.10986 | -0.10071 | 0.11444 | 0.3067 | 0.11902 | 5.0491 | 0.050354 | 0.086975 | 122.6715 | 5.0125 | -0.10986 | 0.050354 | 0.086975 | 5.0125 | 5.0491 | 122.6715 | -122.7997 | -122.8821
1051.0469 | 122.6257 | -0.23804 | 122.4609 | 0.19836 | 0.011536 | 0.020721 | 0.036102 | 0.060455 | 0.060883 | 0.15979 | -0.20142 | -0.1831 | -0.27008 | 4.715 | 4.7104 | 4.7058 | 0.11444 | -0.17395 | 122.4792 | -0.3067 | -0.032044 | -122.644 | 0.036621 | 4.953 | -117.7505 | -0.068665 | 0.018311 | 0.068665 | 0.35248 | 0.064087 | 4.9484 | 0.054932 | 0.036621 | 122.7173 | 4.9438 | -0.068665 | 0.054932 | 0.036621 | 4.9438 | 4.9484 | 122.7173 | -122.731 | -122.7676
1051.9844 | 122.6944 | -0.24261 | 122.4609 | 0.045776 | 0.010895 | 0.023926 | 0.035675 | 0.060455 | 0.062164 | 0.15829 | -0.16479 | -0.15106 | -0.25635 | 4.7607 | 4.7516 | 4.7058 | 0.11902 | -0.10071 | 122.4609 | -0.33875 | -0.013733 | -122.612 | 0.07782 | 5.0034 | -117.7094 | -0.09613 | 0 | 0.091553 | 0.36163 | 0.14191 | 4.9942 | 0.091553 | 0.07782 | 122.7036 | 4.9484 | -0.09613 | 0.091553 | 0.07782 | 4.9484 | 4.9942 | 122.7036 | -122.7173 | -122.7997
1053.0312 | 122.6898 | -0.16937 | 122.5388 | 0.1297 | 0.013031 | 0.018799 | 0.033753 | 0.062164 | 0.061737 | 0.15915 | -0.11444 | -0.14648 | -0.23804 | 4.7653 | 4.7653 | 4.7241 | 0.07782 | -0.082397 | 122.5021 | -0.30212 | -0.068664 | -122.6852 | 0.054932 | 4.9347 | -117.7734 | -0.13275 | -0.036621 | 0.1236 | 0.24719 | 0.086976 | 4.9347 | 0.022889 | 0.054932 | 122.6715 | 4.8935 | -0.13275 | 0.022889 | 0.054932 | 4.8935 | 4.9347 | 122.6715 | -122.7768 | -122.8409
1053.9844 | 122.6349 | -0.24719 | 122.4609 | 0.2594 | 0.011322 | 0.026062 | 0.033325 | 0.063446 | 0.060455 | 0.15894 | -0.17853 | -0.16937 | -0.25177 | 4.7012 | 4.6829 | 4.6875 | 0.10986 | -0.16937 | 122.4976 | -0.33875 | -0.004578 | -122.6303 | 0.068664 | 4.9484 | -117.778 | -0.091553 | 0.036622 | 0.073242 | 0.35706 | 0.077819 | 4.9301 | 0.077819 | 0.068664 | 122.7448 | 4.9347 | -0.091553 | 0.077819 | 0.068664 | 4.9347 | 4.9301 | 122.7448 | -122.7127 | -122.7997
1055.0312 | 122.6715 | -0.24261 | 122.4701 | 0.068664 | 0.009613 | 0.024139 | 0.033325 | 0.062591 | 0.061523 | 0.15936 | -0.1831 | -0.12817 | -0.25177 | 4.7379 | 4.7333 | 4.7058 | 0.15106 | -0.1236 | 122.4838 | -0.31586 | -0.009155 | -122.5983 | 0.05951 | 4.9805 | -117.7368 | -0.073242 | 0.013733 | 0.068665 | 0.39368 | 0.11902 | 4.9759 | 0.11444 | 0.05951 | 122.7264 | 4.9484 | -0.073242 | 0.11444 | 0.05951 | 4.9484 | 4.9759 | 122.7264 | -122.7219 | -122.7859
1055.9844 | 122.6715 | -0.23804 | 122.438 | 0.20599 | 0.01239 | 0.028412 | 0.034607 | 0.060028 | 0.063446 | 0.15936 | -0.13275 | -0.14648 | -0.24719 | 4.7516 | 4.7241 | 4.7379 | 0.09613 | -0.14648 | 122.4655 | -0.3067 | -0.009155 | -122.5845 | 0.10529 | 4.9896 | -117.7139 | -0.068665 | 0.027466 | 0.11444 | 0.33417 | 0.091553 | 4.9622 | 0.091553 | 0.10529 | 122.7036 | 4.9759 | -0.068665 | 0.091553 | 0.10529 | 4.9759 | 4.9622 | 122.7036 | -122.6852 | -122.7448
1057.0156 | 122.7722 | -0.18768 | 122.4701 | 0.12207 | 0.0074768 | 0.021576 | 0.026276 | 0.057892 | 0.061951 | 0.16022 | -0.10071 | -0.16479 | -0.1831 | 4.8614 | 4.8569 | 4.8843 | 0.027466 | 0.032043 | 122.4564 | -0.26093 | 0.004578 | -122.6349 | 0.086975 | 5.0491 | -117.6132 | -0.073242 | -0.013733 | 0.082397 | 0.21515 | 0.21973 | 5.0446 | 0.022888 | 0.086975 | 122.644 | 5.072 | -0.073242 | 0.022888 | 0.086975 | 5.072 | 5.0446 | 122.644 | -122.6532 | -122.731
1057.9844 | 122.6761 | -0.2243 | 122.4518 | 0.20599 | 0.011322 | 0.023499 | 0.03717 | 0.061096 | 0.061523 | 0.16043 | -0.14648 | -0.14191 | -0.25635 | 4.7745 | 4.7562 | 4.7333 | 0.12817 | -0.13275 | 122.4792 | -0.32501 | -0.032044 | -122.5937 | 0.07782 | 4.9988 | -117.6956 | -0.10071 | 0.027466 | 0.10986 | 0.35248 | 0.091553 | 4.9805 | 0.082397 | 0.07782 | 122.7036 | 4.9576 | -0.10071 | 0.082397 | 0.07782 | 4.9576 | 4.9805 | 122.7036 | -122.7081 | -122.7768
1059.0312 | 122.7036 | -0.18768 | 122.4472 | 0.12207 | 0.011749 | 0.024994 | 0.034607 | 0.061737 | 0.061951 | 0.1568 | -0.068665 | -0.10529 | -0.16022 | 4.9393 | 4.9072 | 4.9026 | 0.23346 | -0.068665 | 122.5159 | -0.27466 | 0.027466 | -122.5525 | 0.11902 | 5.127 | -117.54 | -0.086975 | 0.068664 | 0.091552 | 0.42114 | 0.11902 | 5.0949 | 0.082397 | 0.11902 | 122.7036 | 5.0903 | -0.086975 | 0.082397 | 0.11902 | 5.0903 | 5.0949 | 122.7036 | -122.6074 | -122.7219
1059.9844 | 122.6532 | -0.23804 | 122.4335 | 0.24414 | 0.014526 | 0.024353 | 0.035034 | 0.063232 | 0.059814 | 0.16064 | -0.13733 | -0.1236 | -0.25177 | 4.9576 | 4.9301 | 4.9118 | 0.32501 | -0.14191 | 122.4976 | -0.32044 | -0.013733 | -122.5571 | 0.10071 | 5.1956 | -117.5034 | -0.082398 | 0.064087 | 0.11444 | 0.56305 | 0.09613 | 5.1682 | 0.11444 | 0.10071 | 122.7356 | 5.1498 | -0.082398 | 0.11444 | 0.10071 | 5.1498 | 5.1682 | 122.7356 | -122.6852 | -122.7539
1060.9844 | 122.6715 | -0.23346 | 122.4564 | 0.3891 | 0.010254 | 0.022217 | 0.034393 | 0.062591 | 0.062378 | 0.15915 | -0.1831 | -0.12817 | -0.23804 | 4.6875 | 4.7104 | 4.715 | 0.091553 | -0.16479 | 122.5067 | -0.32959 | -0.004578 | -122.5845 | 0.050354 | 4.921 | -117.746 | -0.096131 | 0.050354 | 0.054932 | 0.32501 | 0.068664 | 4.9438 | 0.10528 | 0.050354 | 122.7402 | 4.9484 | -0.096131 | 0.10528 | 0.050354 | 4.9484 | 4.9438 | 122.7402 | -122.6944 | -122.7859
1062.0156 | 122.7539 | -0.20142 | 122.4152 | 0.053405 | 0.0093994 | 0.023285 | 0.027985 | 0.060882 | 0.062805 | 0.16022 | -0.073242 | -0.17853 | -0.21515 | 4.8065 | 4.66 | 4.8935 | -0.16937 | -0.21515 | 122.4335 | -0.29297 | -0.013733 | -122.5937 | 0.12817 | 5.0079 | -117.7551 | -0.091553 | 0.018311 | 0.14191 | 0.032043 | -0.013733 | 4.8614 | 0.022888 | 0.12817 | 122.6349 | 5.0949 | -0.091553 | 0.022888 | 0.12817 | 5.0949 | 4.8614 | 122.6349 | -122.6303 | -122.7081
1062.9844 | 122.699 | -0.19684 | 122.4609 | 0.13733 | 0.013245 | 0.027771 | 0.039307 | 0.061096 | 0.060242 | 0.15808 | -0.068665 | -0.091553 | -0.16479 | 4.7287 | 4.7104 | 4.6921 | 0.054932 | -0.07782 | 122.5067 | -0.29755 | 0.032043 | -122.5525 | 0.12817 | 4.9255 | -117.7505 | -0.10071 | 0.045777 | 0.09613 | 0.25177 | 0.11902 | 4.9072 | 0.10529 | 0.12817 | 122.7036 | 4.8889 | -0.10071 | 0.10529 | 0.12817 | 4.8889 | 4.9072 | 122.7036 | -122.6257 | -122.7585
1064.0312 | 122.699 | -0.21057 | 122.493 | 0.30518 | 0.011963 | 0.02713 | 0.035034 | 0.063019 | 0.060883 | 0.15936 | -0.07782 | -0.10529 | -0.16937 | 4.7653 | 4.7379 | 4.7241 | 0.059509 | -0.064087 | 122.5021 | -0.32044 | 0.041198 | -122.5983 | 0.13275 | 4.9759 | -117.7551 | -0.10986 | 0.009155 | 0.091553 | 0.27008 | 0.14648 | 4.9484 | 0.10529 | 0.13275 | 122.7127 | 4.9347 | -0.10986 | 0.10529 | 0.13275 | 4.9347 | 4.9484 | 122.7127 | -122.6624 | -122.8134
1064.9844 | 122.6212 | -0.21973 | 122.4564 | 0.33569 | 0.011536 | 0.022858 | 0.036743 | 0.060669 | 0.063446 | 0.16129 | -0.16937 | -0.11902 | -0.24261 | 4.6463 | 4.66 | 4.66 | 0.073242 | -0.16937 | 122.5067 | -0.31586 | -0.022888 | -122.5754 | 0.050354 | 4.866 | -117.7963 | -0.09613 | 0.050354 | 0.073242 | 0.29297 | 0.050354 | 4.8798 | 0.10071 | 0.050354 | 122.7264 | 4.8798 | -0.09613 | 0.10071 | 0.050354 | 4.8798 | 4.8798 | 122.7264 | -122.699 | -122.7722
1066.0312 | 122.6624 | -0.2243 | 122.4884 | 0.16785 | 0.013458 | 0.026917 | 0.032898 | 0.062378 | 0.064728 | 0.15808 | -0.16479 | -0.13275 | -0.25635 | 4.7195 | 4.6967 | 4.6829 | 0.082397 | -0.15564 | 122.525 | -0.32044 | -0.032044 | -122.6212 | 0.059509 | 4.9438 | -117.7917 | -0.096131 | 0.036621 | 0.091553 | 0.3067 | 0.068664 | 4.921 | 0.091553 | 0.059509 | 122.7493 | 4.9072 | -0.096131 | 0.091553 | 0.059509 | 4.9072 | 4.921 | 122.7493 | -122.7448 | -122.8088
1067.0469 | 122.7264 | -0.20599 | 122.4564 | 0.12207 | 0.010895 | 0.023712 | 0.035248 | 0.061523 | 0.061951 | 0.16043 | -0.12817 | -0.15564 | -0.24261 | 4.7928 | 4.7653 | 4.7195 | 0.068665 | -0.073242 | 122.4792 | -0.28381 | -0.036621 | -122.612 | 0.07782 | 4.9988 | -117.691 | -0.077819 | 0.022888 | 0.11444 | 0.27466 | 0.13275 | 4.9713 | 0.050354 | 0.07782 | 122.6852 | 4.9255 | -0.077819 | 0.050354 | 0.07782 | 4.9255 | 4.9713 | 122.6852 | -122.699 | -122.7402
1068.0156 | 122.7951 | -0.16937 | 122.4655 | 0.15259 | 0.0089722 | 0.022217 | 0.027557 | 0.060455 | 0.063873 | 0.15915 | -0.091553 | -0.14648 | -0.18768 | 4.8569 | 4.866 | 4.8523 | -0.013733 | 0.036621 | 122.4564 | -0.28381 | -0.01831 | -122.612 | 0.07782 | 5.0262 | -117.5995 | -0.11444 | -0.009155 | 0.09613 | 0.15564 | 0.20599 | 5.0354 | 0.022889 | 0.07782 | 122.6257 | 5.0217 | -0.11444 | 0.022889 | 0.07782 | 5.0217 | 5.0354 | 122.6257 | -122.6532 | -122.7493
1068.9844 | 122.6669 | -0.2243 | 122.4884 | 0.74005 | 0.015167 | 0.023712 | 0.036102 | 0.06131 | 0.061737 | 0.16022 | -0.14191 | -0.12817 | -0.22888 | 4.7516 | 4.7195 | 4.6967 | 0.13733 | -0.15106 | 122.5159 | -0.3067 | -0.004578 | -122.6166 | 0.082397 | 4.9759 | -117.7689 | -0.082398 | 0.027466 | 0.086975 | 0.36163 | 0.073242 | 4.9438 | 0.09613 | 0.082397 | 122.7402 | 4.921 | -0.082398 | 0.09613 | 0.082397 | 4.921 | 4.9438 | 122.7402 | -122.7173 | -122.7951
1070.0312 | 122.644 | -0.18768 | 122.5159 | -0.0076295 | 0.013031 | 0.021149 | 0.033539 | 0.058746 | 0.063019 | 0.15872 | -0.17395 | -0.13275 | -0.26093 | 4.8889 | 5.0537 | 4.9393 | 0.14648 | -0.13733 | 122.5571 | -0.28381 | -0.073242 | -122.6486 | 0.013733 | 5.0766 | -117.4622 | -0.09613 | 0.041199 | 0.086975 | 0.33417 | 0.050354 | 5.2414 | 0.054932 | 0.013733 | 122.7448 | 5.127 | -0.09613 | 0.054932 | 0.013733 | 5.127 | 5.2414 | 122.7448 | -122.7768 | -122.7997
1070.9844 | 122.7448 | -0.19684 | 122.4564 | 0.4425 | 0.01239 | 0.024994 | 0.037384 | 0.061096 | 0.061951 | 0.15936 | -0.15106 | -0.16479 | -0.24261 | 6.3492 | 6.2988 | 6.3354 | 1.712 | -0.09613 | 122.4838 | -0.28839 | -0.045777 | -122.6212 | 0.045776 | 6.546 | -116.1575 | -0.091553 | 0.027466 | 0.091553 | 1.9089 | 0.10071 | 6.4957 | 0.032043 | 0.045776 | 122.6807 | 6.5323 | -0.091553 | 0.032043 | 0.045776 | 6.5323 | 6.4957 | 122.6807 | -122.699 | -122.7448
1072.0312 | 122.644 | -0.21515 | 122.4472 | 0.3128 | 0.011536 | 0.026276 | 0.03653 | 0.061523 | 0.062164 | 0.15787 | -0.15564 | -0.13733 | -0.26093 | 4.7012 | 4.66 | 4.6188 | 0.09613 | -0.16937 | 122.5113 | -0.32044 | -0.045776 | -122.5845 | 0.059509 | 4.9164 | -117.7872 | -0.10529 | 0.064087 | 0.10529 | 0.31128 | 0.045776 | 4.8752 | 0.07782 | 0.059509 | 122.7264 | 4.834 | -0.10529 | 0.07782 | 0.059509 | 4.834 | 4.8752 | 122.7264 | -122.7081 | -122.7676
1072.9844 | 122.7402 | -0.16479 | 122.4564 | 0.38147 | 0.010254 | 0.02179 | 0.027557 | 0.059174 | 0.063232 | 0.16043 | -0.091553 | -0.16022 | -0.20142 | 4.7699 | 4.7745 | 4.7333 | -0.041199 | -0.027466 | 122.5067 | -0.25635 | -0.036621 | -122.6166 | 0.073242 | 4.9347 | -117.6819 | -0.091553 | 0.050354 | 0.10986 | 0.1236 | 0.13733 | 4.9393 | 0.004578 | 0.073242 | 122.6715 | 4.8981 | -0.091553 | 0.004578 | 0.073242 | 4.8981 | 4.9393 | 122.6715 | -122.6578 | -122.7127
1074.0156 | 122.731 | -0.21515 | 122.4564 | -0.038147 | 0.011536 | 0.022858 | 0.031616 | 0.057251 | 0.058533 | 0.15808 | -0.10071 | -0.15564 | -0.21515 | 4.8019 | 4.7882 | 4.715 | 0.068665 | -0.041199 | 122.4655 | -0.29297 | 0 | -122.612 | 0.11444 | 5.0171 | -117.6682 | -0.07782 | 0.009155 | 0.11444 | 0.28381 | 0.17395 | 5.0034 | 0.059509 | 0.11444 | 122.6807 | 4.9301 | -0.07782 | 0.059509 | 0.11444 | 4.9301 | 5.0034 | 122.6807 | -122.6715 | -122.7493
1074.9844 | 122.7951 | -0.17395 | 122.4747 | 0.41199 | 0.0098268 | 0.023926 | 0.034821 | 0.06131 | 0.060455 | 0.15851 | -0.082397 | -0.16479 | -0.21973 | 4.8386 | 4.7882 | 4.7974 | -0.050354 | -0.032043 | 122.493 | -0.2655 | -0.045777 | -122.6395 | 0.091553 | 5.0125 | -117.6865 | -0.091553 | 0.018311 | 0.13733 | 0.1236 | 0.14191 | 4.9622 | 0.009155 | 0.091553 | 122.6669 | 4.9713 | -0.091553 | 0.009155 | 0.091553 | 4.9713 | 4.9622 | 122.6669 | -122.6944 | -122.7402
1075.9844 | 122.7539 | -0.16937 | 122.4472 | 0.32043 | 0.011108 | 0.02179 | 0.032471 | 0.05896 | 0.063019 | 0.15958 | -0.07782 | -0.1831 | -0.20142 | 4.8569 | 4.8477 | 4.8203 | -0.059509 | -0.004578 | 122.4747 | -0.2655 | -0.032043 | -122.6303 | 0.091553 | 5.0262 | -117.5995 | -0.09613 | 0.027465 | 0.1236 | 0.10986 | 0.16479 | 5.0171 | -0.013732 | 0.091553 | 122.644 | 4.9896 | -0.09613 | -0.013732 | 0.091553 | 4.9896 | 5.0171 | 122.644 | -122.6486 | -122.7127
1076.9844 | 122.5159 | -0.21515 | 122.5159 | 0.32806 | 0.01239 | 0.02948 | 0.037598 | 0.060242 | 0.062592 | 0.15958 | -0.18768 | -0.1236 | -0.24261 | 4.7836 | 4.7424 | 4.7012 | 0.13275 | -0.16479 | 122.5021 | -0.33417 | -0.027466 | -122.6395 | 0.027466 | 4.9988 | -117.7734 | -0.11902 | -0.013733 | 0.054932 | 0.3479 | 0.050354 | 4.9576 | 0.091553 | 0.027466 | 122.7173 | 4.9164 | -0.11902 | 0.091553 | 0.027466 | 4.9164 | 4.9576 | 122.7173 | -122.7585 | -122.85
1078.0156 | 122.7676 | -0.17395 | 122.4609 | 0.061035 | 0.0079042 | 0.019013 | 0.029907 | 0.057037 | 0.063873 | 0.15872 | -0.07782 | -0.16479 | -0.19684 | 4.9484 | 4.9301 | 4.866 | 0.07782 | 0.022888 | 122.493 | -0.28381 | -0.022888 | -122.6257 | 0.09613 | 5.1224 | -117.5308 | -0.10986 | 0.032044 | 0.11902 | 0.25177 | 0.19684 | 5.1041 | 0.009155 | 0.09613 | 122.6669 | 5.04 | -0.10986 | 0.009155 | 0.09613 | 5.04 | 5.1041 | 122.6669 | -122.6578 | -122.7447
1078.9844 | 122.6944 | -0.14648 | 122.4884 | 0.13733 | 0.010895 | 0.024353 | 0.037384 | 0.05896 | 0.062164 | 0.15787 | -0.10986 | -0.13275 | -0.22888 | 4.9347 | 4.9026 | 4.7836 | 0.18768 | -0.045776 | 122.5662 | -0.22888 | -0.082398 | -122.6212 | 0.036621 | 5.0812 | -117.5858 | -0.082398 | 0.07782 | 0.11902 | 0.33417 | 0.10071 | 5.0491 | 0.013733 | 0.036621 | 122.7127 | 4.9301 | -0.082398 | 0.013733 | 0.036621 | 4.9301 | 5.0491 | 122.7127 | -122.7173 | -122.7173
1080.0156 | 122.8134 | -0.16022 | 122.4335 | 0.14496 | 0.0098268 | 0.020935 | 0.028198 | 0.059814 | 0.06131 | 0.1568 | -0.059509 | -0.15106 | -0.18768 | 5.0674 | 5.0537 | 4.9942 | 0.13733 | 0.050354 | 122.4884 | -0.26093 | -0.027466 | -122.5845 | 0.10071 | 5.2277 | -117.3798 | -0.10071 | 0.054931 | 0.12817 | 0.29755 | 0.21057 | 5.2139 | 0.009155 | 0.10071 | 122.6486 | 5.1544 | -0.10071 | 0.009155 | 0.10071 | 5.1544 | 5.2139 | 122.6486 | -122.6212 | -122.6944
1080.9844 | 122.7402 | -0.17395 | 122.4792 | 0.34332 | 0.01004 | 0.020081 | 0.032684 | 0.060242 | 0.062592 | 0.15958 | -0.073242 | -0.17853 | -0.19226 | 4.9072 | 4.8889 | 4.8111 | -0.009155 | 0 | 122.493 | -0.26093 | -0.018311 | -122.6578 | 0.10071 | 5.0812 | -117.5903 | -0.086975 | 0.013733 | 0.11902 | 0.16479 | 0.17395 | 5.0629 | -0.004578 | 0.10071 | 122.6669 | 4.985 | -0.086975 | -0.004578 | 0.10071 | 4.985 | 5.0629 | 122.6669 | -122.6715 | -122.7402
1082.0312 | 122.6761 | -0.21057 | 122.493 | -0.030518 | 0.011963 | 0.022644 | 0.035889 | 0.057465 | 0.061523 | 0.15915 | -0.09613 | -0.10071 | -0.21515 | 4.8203 | 4.8294 | 4.7699 | 0.19684 | -0.11444 | 122.5342 | -0.27924 | -0.004578 | -122.5937 | 0.11444 | 5.0308 | -117.6636 | -0.068665 | 0.041199 | 0.11902 | 0.40741 | 0.09613 | 5.04 | 0.10986 | 0.11444 | 122.7448 | 4.9805 | -0.068665 | 0.10986 | 0.11444 | 4.9805 | 5.04 | 122.7448 | -122.7081 | -122.7722
1082.9844 | 122.7356 | -0.20599 | 122.4472 | 0.4425 | 0.011322 | 0.024994 | 0.036957 | 0.060455 | 0.063019 | 0.15744 | -0.14648 | -0.14191 | -0.22888 | 4.9713 | 4.9301 | 4.8935 | 0.15564 | -0.10071 | 122.5067 | -0.29297 | -0.022888 | -122.5891 | 0.05951 | 5.1773 | -117.5171 | -0.086975 | 0.059509 | 0.082398 | 0.36163 | 0.10529 | 5.1361 | 0.064087 | 0.05951 | 122.7127 | 5.0995 | -0.086975 | 0.064087 | 0.05951 | 5.0995 | 5.1361 | 122.7127 | -122.6761 | -122.7402
1084.0312 | 122.6669 | -0.2243 | 122.4838 | 0.28229 | 0.010895 | 0.024139 | 0.03653 | 0.062805 | 0.062592 | 0.15787 | -0.16022 | -0.13733 | -0.23346 | 4.7745 | 4.7607 | 4.6783 | 0.11444 | -0.15106 | 122.5433 | -0.32044 | -0.009155 | -122.6212 | 0.064087 | 4.9988 | -117.7231 | -0.096131 | 0.059509 | 0.073242 | 0.33875 | 0.073242 | 4.985 | 0.086975 | 0.064087 | 122.7676 | 4.9026 | -0.096131 | 0.086975 | 0.064087 | 4.9026 | 4.985 | 122.7676 | -122.7173 | -122.8043
1084.9844 | 122.6624 | -0.23346 | 122.493 | 0.22125 | 0.011108 | 0.023712 | 0.03653 | 0.060669 | 0.062805 | 0.15915 | -0.15106 | -0.15564 | -0.25635 | 4.7974 | 4.7745 | 4.6829 | 0.10071 | -0.13733 | 122.5113 | -0.32501 | -0.022889 | -122.6486 | 0.082397 | 5.0308 | -117.7185 | -0.091553 | 0.018311 | 0.10529 | 0.33417 | 0.09613 | 5.0079 | 0.077819 | 0.082397 | 122.7448 | 4.9164 | -0.091553 | 0.077819 | 0.082397 | 4.9164 | 5.0079 | 122.7448 | -122.7493 | -122.818
1086.0312 | 122.6761 | -0.2243 | 122.5021 | 0.022888 | 0.009613 | 0.019013 | 0.032898 | 0.061096 | 0.062164 | 0.15958 | -0.14648 | -0.11902 | -0.2243 | 4.8111 | 4.8111 | 4.7516 | 0.14191 | -0.10529 | 122.5296 | -0.28839 | 0 | -122.6212 | 0.07782 | 5.0354 | -117.691 | -0.064087 | 0.027466 | 0.07782 | 0.36621 | 0.11902 | 5.0354 | 0.10529 | 0.07782 | 122.7539 | 4.9759 | -0.064087 | 0.10529 | 0.07782 | 4.9759 | 5.0354 | 122.7539 | -122.7264 | -122.7905
1086.9844 | 122.6852 | -0.21973 | 122.4884 | 0.49591 | 0.011322 | 0.025635 | 0.034821 | 0.05896 | 0.063019 | 0.15829 | -0.16479 | -0.09613 | -0.21973 | 4.8203 | 4.7928 | 4.747 | 0.11444 | -0.15106 | 122.5021 | -0.29755 | 0 | -122.5845 | 0.054932 | 5.04 | -117.6956 | -0.077819 | 0.013733 | 0.054932 | 0.33417 | 0.068665 | 5.0125 | 0.1236 | 0.054932 | 122.7219 | 4.9667 | -0.077819 | 0.1236 | 0.054932 | 4.9667 | 5.0125 | 122.7219 | -122.7081 | -122.7859
1088.0156 | 122.7951 | -0.16937 | 122.4655 | 0.030518 | 0.011322 | 0.021576 | 0.028198 | 0.058319 | 0.060883 | 0.15765 | -0.068665 | -0.17395 | -0.18768 | 4.9713 | 4.9622 | 4.8843 | 0.004578 | 0.032043 | 122.4976 | -0.27924 | -0.01831 | -122.6395 | 0.10071 | 5.1407 | -117.5034 | -0.10986 | 0.032044 | 0.11902 | 0.17395 | 0.20142 | 5.1315 | -0.004577 | 0.10071 | 122.6669 | 5.0537 | -0.10986 | -0.004577 | 0.10071 | 5.0537 | 5.1315 | 122.6669 | -122.6532 | -122.7448
1088.9844 | 122.7173 | -0.22888 | 122.4884 | 0.19073 | 0.011749 | 0.023712 | 0.036102 | 0.061523 | 0.063446 | 0.15829 | -0.10071 | -0.14648 | -0.23346 | 4.9438 | 4.9118 | 4.8386 | 0.11444 | -0.10071 | 122.5296 | -0.29297 | -0.004577 | -122.6349 | 0.12817 | 5.1727 | -117.5766 | -0.064087 | 0.041199 | 0.13275 | 0.34332 | 0.12817 | 5.1407 | 0.082398 | 0.12817 | 122.7585 | 5.0674 | -0.064087 | 0.082398 | 0.12817 | 5.0674 | 5.1407 | 122.7585 | -122.7219 | -122.7814
1089.9844 | 122.6761 | -0.20142 | 122.493 | 0.38147 | 0.011322 | 0.024994 | 0.042511 | 0.063873 | 0.057892 | 0.15765 | -0.15106 | -0.1236 | -0.22888 | 5.1086 | 4.9622 | 4.8294 | 0.19684 | -0.16479 | 122.5845 | -0.28839 | -0.027466 | -122.6166 | 0.050354 | 5.3101 | -117.5308 | -0.086975 | 0.091553 | 0.07782 | 0.39825 | 0.036621 | 5.1636 | 0.07782 | 0.050354 | 122.7859 | 5.0308 | -0.086975 | 0.07782 | 0.050354 | 5.0308 | 5.1636 | 122.7859 | -122.7219 | -122.7814
1091.0312 | 122.7173 | -0.21973 | 122.5067 | 0.13733 | 0.010681 | 0.024139 | 0.036957 | 0.062378 | 0.058319 | 0.15851 | -0.086975 | -0.09613 | -0.20142 | 5.0491 | 5.0217 | 4.9347 | 0.13275 | -0.082397 | 122.5204 | -0.28839 | 0.018311 | -122.6028 | 0.13275 | 5.2689 | -117.485 | -0.068664 | 0.013733 | 0.11444 | 0.35248 | 0.13733 | 5.2414 | 0.1236 | 0.13275 | 122.7402 | 5.1544 | -0.068664 | 0.1236 | 0.13275 | 5.1544 | 5.2414 | 122.7402 | -122.7081 | -122.7951
1091.9844 | 122.6898 | -0.21973 | 122.493 | 0.24414 | 0.010895 | 0.025848 | 0.036743 | 0.060882 | 0.061096 | 0.16086 | -0.14648 | -0.14648 | -0.22888 | 5.0583 | 5.0446 | 4.9484 | 0.21057 | -0.13275 | 122.5204 | -0.31128 | -0.009155 | -122.6395 | 0.073243 | 5.278 | -117.4484 | -0.091552 | 0.027466 | 0.082398 | 0.4303 | 0.086976 | 5.2643 | 0.073243 | 0.073243 | 122.7402 | 5.1682 | -0.091552 | 0.073243 | 0.073243 | 5.1682 | 5.2643 | 122.7402 | -122.7219 | -122.8043
1093.0312 | 122.7402 | -0.19684 | 122.4792 | 0.4425 | 0.011108 | 0.024567 | 0.034821 | 0.063019 | 0.061523 | 0.1615 | -0.15564 | -0.15106 | -0.24719 | 5.0629 | 5.0812 | 5.0308 | 0.14648 | -0.09613 | 122.5113 | -0.29755 | -0.050354 | -122.6303 | 0.041198 | 5.2597 | -117.3981 | -0.10071 | 0.032044 | 0.091552 | 0.34332 | 0.10071 | 5.278 | 0.045776 | 0.041198 | 122.7081 | 5.2277 | -0.10071 | 0.045776 | 0.041198 | 5.2277 | 5.278 | 122.7081 | -122.7264 | -122.7768
1093.9844 | 122.6624 | -0.22888 | 122.5067 | 0.24414 | 0.011963 | 0.026489 | 0.035461 | 0.061523 | 0.06366 | 0.15851 | -0.16022 | -0.1236 | -0.24719 | 5.1819 | 5.1727 | 5.0949 | 0.37537 | -0.15106 | 122.5342 | -0.31586 | -0.01831 | -122.6303 | 0.068665 | 5.4108 | -117.334 | -0.086975 | 0.027466 | 0.086975 | 0.60425 | 0.07782 | 5.4016 | 0.10529 | 0.068665 | 122.7631 | 5.3238 | -0.086975 | 0.10529 | 0.068665 | 5.3238 | 5.4016 | 122.7631 | -122.7539 | -122.8226
1095.0312 | 122.6807 | -0.23346 | 122.4838 | 0.007629 | 0.011749 | 0.017517 | 0.030975 | 0.060242 | 0.062592 | 0.15958 | -0.15106 | -0.13275 | -0.23804 | 5.0354 | 5.04 | 4.9576 | 0.24261 | -0.10071 | 122.5662 | -0.32501 | -0.004578 | -122.6166 | 0.082397 | 5.2689 | -117.4438 | -0.091553 | 0.082397 | 0.086975 | 0.47607 | 0.13275 | 5.2734 | 0.10071 | 0.082397 | 122.7997 | 5.191 | -0.091553 | 0.10071 | 0.082397 | 5.191 | 5.2734 | 122.7997 | -122.7219 | -122.8088
1095.9844 | 122.6944 | -0.23346 | 122.4838 | 0.23651 | 0.009613 | 0.025208 | 0.035675 | 0.06131 | 0.061523 | 0.15851 | -0.14191 | -0.13733 | -0.25177 | 4.9713 | 4.9576 | 4.8843 | 0.09613 | -0.14648 | 122.525 | -0.31128 | -0.018311 | -122.6212 | 0.091552 | 5.2048 | -117.5262 | -0.07782 | 0.041198 | 0.10986 | 0.32959 | 0.086975 | 5.191 | 0.09613 | 0.091552 | 122.7585 | 5.1178 | -0.07782 | 0.09613 | 0.091552 | 5.1178 | 5.191 | 122.7585 | -122.7356 | -122.7951
1097.0312 | 122.7036 | -0.21515 | 122.5113 | 0.45776 | 0.010254 | 0.02243 | 0.033325 | 0.061523 | 0.059601 | 0.15765 | -0.1236 | -0.11444 | -0.21973 | 7.2189 | 7.196 | 7.1091 | 0.064087 | -0.14191 | 122.5571 | -0.3067 | -0.004578 | -122.6257 | 0.091553 | 7.4341 | -115.3152 | -0.091553 | 0.045776 | 0.096131 | 0.27924 | 0.073242 | 7.4112 | 0.10071 | 0.091553 | 122.7722 | 7.3242 | -0.091553 | 0.10071 | 0.091553 | 7.3242 | 7.4112 | 122.7722 | -122.731 | -122.818
1097.9844 | 122.6624 | -0.22888 | 122.5067 | 0.22888 | 0.013245 | 0.023499 | 0.036316 | 0.061096 | 0.059387 | 0.1568 | -0.17395 | -0.15564 | -0.26093 | 6.5735 | 6.5552 | 6.4682 | 0.073242 | -0.15106 | 122.5159 | -0.32044 | -0.032043 | -122.6624 | 0.054932 | 6.8024 | -115.9515 | -0.091553 | 0.009155 | 0.086975 | 0.30212 | 0.07782 | 6.7841 | 0.073242 | 0.054932 | 122.7448 | 6.6971 | -0.091553 | 0.073242 | 0.054932 | 6.6971 | 6.7841 | 122.7448 | -122.7676 | -122.8271
1098.9844 | 122.699 | -0.21515 | 122.5067 | 0.16785 | 0.010468 | 0.026276 | 0.035675 | 0.060455 | 0.059814 | 0.15787 | -0.091553 | -0.1236 | -0.20142 | 6.4774 | 6.4407 | 6.3034 | 0.041199 | -0.086975 | 122.5388 | -0.29755 | 0.013733 | -122.6303 | 0.1236 | 6.6925 | -116.066 | -0.082397 | 0.032043 | 0.10986 | 0.25635 | 0.12817 | 6.6559 | 0.091553 | 0.1236 | 122.7539 | 6.5186 | -0.082397 | 0.091553 | 0.1236 | 6.5186 | 6.6559 | 122.7539 | -122.7081 | -122.8043
1099.9844 | 122.7173 | -0.21973 | 122.4884 | 0.045776 | 0.010254 | 0.02243 | 0.033966 | 0.061737 | 0.060883 | 0.1568 | -0.16479 | -0.12817 | -0.24719 | 6.4041 | 6.4041 | 6.3171 | 0.11902 | -0.10529 | 122.5342 | -0.31586 | -0.027465 | -122.6166 | 0.054932 | 6.6238 | -116.0843 | -0.09613 | 0.045777 | 0.082397 | 0.33875 | 0.11444 | 6.6238 | 0.091553 | 0.054932 | 122.7539 | 6.5369 | -0.09613 | 0.091553 | 0.054932 | 6.5369 | 6.6238 | 122.7539 | -122.7356 | -122.8043
1101.0312 | 122.7219 | -0.21973 | 122.5067 | 0.007629 | 0.008545 | 0.019653 | 0.031616 | 0.060028 | 0.06131 | 0.15936 | -0.16022 | -0.14648 | -0.23804 | 6.2759 | 6.2668 | 6.1752 | 0.14191 | -0.091553 | 122.5525 | -0.32044 | -0.01831 | -122.6532 | 0.05951 | 6.4957 | -116.2399 | -0.10071 | 0.045776 | 0.07782 | 0.36163 | 0.12817 | 6.4865 | 0.073243 | 0.05951 | 122.7722 | 6.395 | -0.10071 | 0.073243 | 0.05951 | 6.395 | 6.4865 | 122.7722 | -122.7448 | -122.8271
1101.9844 | 122.6807 | -0.21057 | 122.5204 | 0.40436 | 0.01239 | 0.025421 | 0.033325 | 0.05896 | 0.062164 | 0.15808 | -0.35248 | -0.13275 | -0.21515 | 6.221 | 6.1935 | 6.0928 | 0.10071 | -0.15106 | 122.525 | -0.29755 | -0.004578 | -122.6532 | -0.14191 | 6.4316 | -116.3269 | -0.086975 | 0.004577 | -0.13733 | 0.31128 | 0.059509 | 6.4041 | 0.07782 | -0.14191 | 122.7356 | 6.3034 | -0.086975 | 0.07782 | -0.14191 | 6.3034 | 6.4041 | 122.7356 | -122.7356 | -122.818
1103.0469 | 122.8271 | -0.17395 | 122.5113 | 0.11444 | 0.0089722 | 0.021362 | 0.027557 | 0.057678 | 0.062805 | 0.15765 | -0.082397 | -0.13275 | -0.20142 | 6.2805 | 6.2805 | 6.2119 | 0.041199 | 0.022888 | 122.5204 | -0.23346 | -0.027466 | -122.644 | 0.091553 | 6.4545 | -116.2308 | -0.059509 | 0.009155 | 0.11902 | 0.21515 | 0.19684 | 6.4545 | 0.041199 | 0.091553 | 122.6944 | 6.3858 | -0.059509 | 0.041199 | 0.091553 | 6.3858 | 6.4545 | 122.6944 | -122.7127 | -122.7448
1103.9688 | 122.7493 | -0.20599 | 122.5021 | 0.38147 | 0.011963 | 0.023071 | 0.036316 | 0.058319 | 0.058533 | 0.15787 | -0.13733 | -0.15106 | -0.23346 | 6.2851 | 6.2485 | 6.1844 | 0.12817 | -0.073242 | 122.493 | -0.27008 | -0.027465 | -122.6532 | 0.068665 | 6.4911 | -116.2537 | -0.064087 | -0.009155 | 0.09613 | 0.33417 | 0.13275 | 6.4545 | 0.054932 | 0.068665 | 122.699 | 6.3904 | -0.064087 | 0.054932 | 0.068665 | 6.3904 | 6.4545 | 122.699 | -122.7356 | -122.7722
1105.0312 | 122.7448 | -0.21515 | 122.5388 | 0.053405 | 0.009613 | 0.02478 | 0.035889 | 0.057892 | 0.060028 | 0.15701 | -0.10986 | -0.15564 | -0.23346 | 6.1981 | 6.1432 | 6.0471 | 0.14191 | -0.068665 | 122.5342 | -0.29297 | -0.01831 | -122.6944 | 0.10529 | 6.4133 | -116.3956 | -0.07782 | -0.004577 | 0.1236 | 0.35706 | 0.14648 | 6.3583 | 0.059509 | 0.10529 | 122.7493 | 6.2622 | -0.07782 | 0.059509 | 0.10529 | 6.2622 | 6.3583 | 122.7493 | -122.7722 | -122.8317
1105.9688 | 122.7036 | -0.2243 | 122.4747 | 0.19836 | 0.012177 | 0.020508 | 0.035675 | 0.059174 | 0.060455 | 0.15808 | -0.13275 | -0.15106 | -0.23804 | 6.1707 | 6.1203 | 6.0196 | 0.19684 | -0.11902 | 122.5433 | -0.30212 | -0.013733 | -122.6257 | 0.091553 | 6.395 | -116.3544 | -0.07782 | 0.068665 | 0.10529 | 0.42114 | 0.10529 | 6.3446 | 0.073242 | 0.091553 | 122.7676 | 6.2439 | -0.07782 | 0.073242 | 0.091553 | 6.2439 | 6.3446 | 122.7676 | -122.7127 | -122.7768
1107.0312 | 122.6669 | -0.2243 | 122.525 | 0.2594 | 0.011749 | 0.024567 | 0.035675 | 0.059601 | 0.060242 | 0.15851 | -0.18768 | -0.16479 | -0.24719 | 6.1707 | 6.1432 | 6.0333 | 0.33417 | -0.16937 | 122.5479 | -0.30212 | -0.022888 | -122.6898 | 0.036621 | 6.395 | -116.3818 | -0.07782 | 0.022889 | 0.059509 | 0.55847 | 0.054931 | 6.3675 | 0.059509 | 0.036621 | 122.7722 | 6.2576 | -0.07782 | 0.059509 | 0.036621 | 6.2576 | 6.3675 | 122.7722 | -122.7722 | -122.8271
1107.9844 | 122.8088 | -0.16937 | 122.4609 | 0.42725 | 0.01004 | 0.017731 | 0.028839 | 0.058746 | 0.063446 | 0.15958 | -0.086975 | -0.2243 | -0.2243 | 6.1935 | 6.1844 | 6.0883 | 0.041199 | 0 | 122.4884 | -0.25177 | -0.054931 | -122.6852 | 0.082398 | 6.3629 | -116.2766 | -0.082397 | 0.027466 | 0.13733 | 0.21057 | 0.16937 | 6.3538 | -0.054931 | 0.082398 | 122.6578 | 6.2576 | -0.082397 | -0.054931 | 0.082398 | 6.2576 | 6.3538 | 122.6578 | -122.6852 | -122.7127
1109.0312 | 122.699 | -0.21057 | 122.525 | 0.19073 | 0.010468 | 0.019653 | 0.034393 | 0.055328 | 0.063019 | 0.15787 | -0.16022 | -0.10529 | -0.23346 | 5.9875 | 5.9875 | 5.8548 | 0.16937 | -0.091553 | 122.5479 | -0.3067 | -0.022888 | -122.6303 | 0.050354 | 6.1981 | -116.5375 | -0.096131 | 0.022889 | 0.073242 | 0.37994 | 0.11902 | 6.1981 | 0.10529 | 0.050354 | 122.7585 | 6.0654 | -0.096131 | 0.10529 | 0.050354 | 6.0654 | 6.1981 | 122.7585 | -122.7585 | -122.8317
1109.9688 | 122.8729 | -0.17853 | 122.3877 | 0.3891 | 0.010254 | 0.023926 | 0.033539 | 0.057892 | 0.059814 | 0.1568 | -0.059509 | -0.17395 | -0.1831 | 6.0425 | 6.015 | 5.928 | -0.07782 | -0.004578 | 122.5021 | -0.25177 | -0.004577 | -122.5616 | 0.11902 | 6.221 | -116.3727 | -0.073242 | 0.11444 | 0.1236 | 0.10071 | 0.17395 | 6.1935 | 0.004578 | 0.11902 | 122.6807 | 6.1066 | -0.073242 | 0.004578 | 0.11902 | 6.1066 | 6.1935 | 122.6807 | -122.5708 | -122.6395
1111.0312 | 122.7905 | -0.19226 | 122.4838 | 0.40436 | 0.011322 | 0.021576 | 0.03418 | 0.057678 | 0.06131 | 0.15915 | -0.12817 | -0.14648 | -0.21515 | 6.0333 | 6.0059 | 5.9372 | -0.022888 | -0.054932 | 122.5204 | -0.27466 | -0.022888 | -122.6303 | 0.064087 | 6.2256 | -116.478 | -0.082397 | 0.036621 | 0.086975 | 0.16937 | 0.13733 | 6.1981 | 0.045777 | 0.064087 | 122.7127 | 6.1295 | -0.082397 | 0.045777 | 0.064087 | 6.1295 | 6.1981 | 122.7127 | -122.699 | -122.7585
1111.9844 | 122.7356 | -0.1831 | 122.3923 | 0.42725 | 0.011749 | 0.02179 | 0.035461 | 0.059814 | 0.060669 | 0.15659 | -0.050354 | -0.16479 | -0.19684 | 6.0654 | 6.0242 | 5.9463 | -0.059509 | -0.004578 | 122.5479 | -0.24719 | -0.013733 | -122.5571 | 0.13275 | 6.2485 | -116.3681 | -0.064087 | 0.15564 | 0.14648 | 0.1236 | 0.17853 | 6.2073 | 0.01831 | 0.13275 | 122.731 | 6.1295 | -0.064087 | 0.01831 | 0.13275 | 6.1295 | 6.2073 | 122.731 | -122.5891 | -122.6395
1113.0312 | 122.7448 | -0.20599 | 122.4976 | 0.091552 | 0.010895 | 0.022003 | 0.036957 | 0.059814 | 0.060669 | 0.1553 | -0.10986 | -0.1236 | -0.24261 | 6.0699 | 6.0242 | 5.9326 | 0.10986 | -0.054932 | 122.5433 | -0.27924 | -0.036621 | -122.6212 | 0.096131 | 6.2759 | -116.4734 | -0.073242 | 0.045776 | 0.13275 | 0.31586 | 0.15106 | 6.2302 | 0.082398 | 0.096131 | 122.7493 | 6.1386 | -0.073242 | 0.082398 | 0.096131 | 6.1386 | 6.2302 | 122.7493 | -122.7402 | -122.7768
1113.9688 | 122.699 | -0.19226 | 122.5067 | 0.38147 | 0.010681 | 0.026703 | 0.036102 | 0.058533 | 0.059174 | 0.15829 | -0.16937 | -0.11902 | -0.23804 | 5.9784 | 6.2988 | 5.8456 | 0.14191 | 0.1831 | 122.5891 | -0.27924 | -0.045776 | -122.6257 | 0.022888 | 6.1707 | -116.2079 | -0.086975 | 0.082397 | 0.068664 | 0.33417 | 0.37537 | 6.4911 | 0.073242 | 0.022888 | 122.7814 | 6.0379 | -0.086975 | 0.073242 | 0.022888 | 6.0379 | 6.4911 | 122.7814 | -122.7448 | -122.7859
1115.0312 | 122.7081 | -0.20142 | 122.5296 | 0.35095 | 0.011963 | 0.021149 | 0.038666 | 0.062591 | 0.058319 | 0.1553 | -0.17395 | -0.12817 | -0.25177 | 6.2027 | 6.0196 | 5.9006 | 0.22888 | -0.15564 | 122.5845 | -0.27466 | -0.050354 | -122.6578 | 0.027466 | 6.4041 | -116.51 | -0.073242 | 0.054932 | 0.07782 | 0.4303 | 0.045776 | 6.221 | 0.073242 | 0.027466 | 122.7859 | 6.102 | -0.073242 | 0.073242 | 0.027466 | 6.102 | 6.221 | 122.7859 | -122.7814 | -122.8043
1115.9688 | 122.6486 | -0.23804 | 122.5204 | 0.30518 | 0.010254 | 0.026917 | 0.034393 | 0.057678 | 0.060883 | 0.1615 | -0.1831 | -0.11902 | -0.23346 | 6.1523 | 6.1203 | 6.0242 | 0.37994 | -0.13275 | 122.5525 | -0.29755 | 0.004578 | -122.6395 | 0.054932 | 6.3904 | -116.4001 | -0.059509 | 0.032043 | 0.050354 | 0.61798 | 0.10529 | 6.3583 | 0.11902 | 0.054932 | 122.7905 | 6.2622 | -0.059509 | 0.11902 | 0.054932 | 6.2622 | 6.3583 | 122.7905 | -122.7539 | -122.818
1117.0469 | 122.7127 | -0.20142 | 122.5342 | -0.030518 | 0.013031 | 0.021149 | 0.034393 | 0.05896 | 0.061096 | 0.15552 | -0.16479 | -0.11444 | -0.2243 | 6.0333 | 6.015 | 5.9052 | 0.25177 | -0.10071 | 122.5342 | -0.3067 | -0.022888 | -122.6486 | 0.036621 | 6.2347 | -116.5192 | -0.10529 | 0 | 0.059509 | 0.45319 | 0.10071 | 6.2164 | 0.086975 | 0.036621 | 122.7356 | 6.1066 | -0.10529 | 0.086975 | 0.036621 | 6.1066 | 6.2164 | 122.7356 | -122.7585 | -122.8409
1117.9688 | 122.6807 | -0.2243 | 122.5159 | 0.25177 | 0.012604 | 0.022858 | 0.034821 | 0.05896 | 0.061737 | 0.15552 | -0.1831 | -0.14191 | -0.23346 | 5.9967 | 5.9418 | 5.8548 | 0.2243 | -0.14648 | 122.5479 | -0.29297 | -0.009155 | -122.6578 | 0.041199 | 6.221 | -116.5741 | -0.068665 | 0.032044 | 0.050354 | 0.44861 | 0.07782 | 6.1661 | 0.082397 | 0.041199 | 122.7722 | 6.0791 | -0.068665 | 0.082397 | 0.041199 | 6.0791 | 6.1661 | 122.7722 | -122.7493 | -122.8088
1118.9688 | 122.7264 | -0.18768 | 122.5113 | 0.38147 | 0.011963 | 0.023712 | 0.033539 | 0.060028 | 0.062592 | 0.15915 | -0.15564 | -0.15564 | -0.25177 | 6.2027 | 6.1844 | 6.0837 | 0.34332 | -0.10529 | 122.5433 | -0.28839 | -0.064087 | -122.6669 | 0.032043 | 6.3904 | -116.3269 | -0.10071 | 0.032043 | 0.09613 | 0.53101 | 0.082397 | 6.3721 | 0.032043 | 0.032043 | 122.731 | 6.2714 | -0.10071 | 0.032043 | 0.032043 | 6.2714 | 6.3721 | 122.731 | -122.7631 | -122.7997
1120.0312 | 122.8317 | -0.17853 | 122.4884 | -0.1297 | 0.0072632 | 0.020081 | 0.030548 | 0.057251 | 0.058533 | 0.15723 | -0.07782 | -0.1831 | -0.19226 | 6.2531 | 6.2302 | 6.1752 | 0.23804 | 0.041199 | 122.5388 | -0.26093 | -0.013733 | -122.6715 | 0.10071 | 6.4316 | -116.2582 | -0.082397 | 0.050354 | 0.11444 | 0.41656 | 0.21973 | 6.4087 | -0.004577 | 0.10071 | 122.7173 | 6.3538 | -0.082397 | -0.004577 | 0.10071 | 6.3538 | 6.4087 | 122.7173 | -122.6807 | -122.7493
1120.9688 | 122.7036 | -0.21057 | 122.5296 | -0.022889 | 0.0087586 | 0.023285 | 0.034607 | 0.059601 | 0.059174 | 0.1568 | -0.17395 | -0.10986 | -0.22888 | 6.0974 | 6.0791 | 5.928 | 0.32959 | -0.091553 | 122.5937 | -0.30212 | -0.018311 | -122.6395 | 0.036621 | 6.308 | -116.4505 | -0.091553 | 0.064087 | 0.054932 | 0.54016 | 0.11902 | 6.2897 | 0.10071 | 0.036621 | 122.8043 | 6.1386 | -0.091553 | 0.10071 | 0.036621 | 6.1386 | 6.2897 | 122.8043 | -122.7585 | -122.8317
1122.0312 | 122.7905 | -0.15106 | 122.493 | 0.33569 | 0.01004 | 0.023285 | 0.031189 | 0.056183 | 0.06131 | 0.15894 | -0.054932 | -0.16479 | -0.18768 | 6.102 | 6.0883 | 6.0287 | 0.086975 | 0.004578 | 122.5388 | -0.23804 | -0.036621 | -122.6578 | 0.09613 | 6.2531 | -116.4047 | -0.086975 | 0.045776 | 0.13275 | 0.23804 | 0.15564 | 6.2393 | -0.013733 | 0.09613 | 122.6898 | 6.1798 | -0.086975 | -0.013733 | 0.09613 | 6.1798 | 6.2393 | 122.6898 | -122.6807 | -122.731
1122.9688 | 122.7036 | -0.21973 | 122.5204 | 0.30518 | 0.010681 | 0.025848 | 0.038666 | 0.058319 | 0.060669 | 0.15488 | -0.1236 | -0.14191 | -0.23346 | 6.1249 | 6.0837 | 5.9601 | 0.32501 | -0.11444 | 122.5342 | -0.29755 | -0.013732 | -122.6624 | 0.096131 | 6.3446 | -116.4368 | -0.077819 | 0.013733 | 0.10986 | 0.54474 | 0.10529 | 6.3034 | 0.07782 | 0.096131 | 122.7539 | 6.1798 | -0.077819 | 0.07782 | 0.096131 | 6.1798 | 6.3034 | 122.7539 | -122.7539 | -122.818
1124.0312 | 122.8455 | -0.19684 | 122.4838 | 0.038147 | 0.0091858 | 0.020935 | 0.02948 | 0.057465 | 0.059814 | 0.15787 | -0.064087 | -0.16479 | -0.18768 | 6.3675 | 6.3538 | 6.1432 | 0.71411 | -0.009155 | 122.4884 | -0.28381 | 0.009155 | -122.6486 | 0.13275 | 6.5643 | -116.1301 | -0.086975 | 0.004577 | 0.1236 | 0.91095 | 0.18768 | 6.5506 | 0.032043 | 0.13275 | 122.6852 | 6.34 | -0.086975 | 0.032043 | 0.13275 | 6.34 | 6.5506 | 122.6852 | -122.6715 | -122.7676
1124.9688 | 122.7585 | -0.19226 | 122.5204 | 0.030518 | 0.0087586 | 0.022217 | 0.035034 | 0.059814 | 0.057892 | 0.15659 | -0.13733 | -0.11902 | -0.23804 | 6.134 | 6.0974 | 5.9601 | 0.3067 | -0.064087 | 122.5479 | -0.30212 | -0.045776 | -122.6395 | 0.054932 | 6.3263 | -116.423 | -0.10986 | 0.027466 | 0.10071 | 0.49896 | 0.12817 | 6.2897 | 0.073242 | 0.054932 | 122.7402 | 6.1523 | -0.10986 | 0.073242 | 0.054932 | 6.1523 | 6.2897 | 122.7402 | -122.7585 | -122.8226
1126.0156 | 122.8271 | -0.15106 | 122.5067 | 0.068664 | 0.0089722 | 0.022003 | 0.02948 | 0.056824 | 0.060242 | 0.15402 | -0.050354 | -0.15564 | -0.17853 | 8.3588 | 8.3267 | 8.1253 | 2.1194 | 0.068665 | 122.5159 | -0.24719 | -0.027466 | -122.6624 | 0.10071 | 8.5098 | -114.18 | -0.09613 | 0.009155 | 0.12817 | 2.2705 | 0.21973 | 8.4778 | -0.004578 | 0.10071 | 122.6669 | 8.2764 | -0.09613 | -0.004578 | 0.10071 | 8.2764 | 8.4778 | 122.6669 | -122.6852 | -122.7539
1126.9844 | 122.6944 | -0.23346 | 122.5388 | 0.27466 | 0.011749 | 0.026062 | 0.038025 | 0.058105 | 0.063019 | 0.15723 | -0.13275 | -0.13733 | -0.23346 | 5.8731 | 5.8594 | 5.7083 | 0.1236 | -0.13275 | 122.5616 | -0.31128 | 0 | -122.6761 | 0.10071 | 6.1066 | -116.6794 | -0.07782 | 0.022889 | 0.10071 | 0.35706 | 0.10071 | 6.0928 | 0.09613 | 0.10071 | 122.7951 | 5.9418 | -0.07782 | 0.09613 | 0.10071 | 5.9418 | 6.0928 | 122.7951 | -122.7722 | -122.85
1128.0156 | 122.8043 | -0.16937 | 122.5296 | 0.22888 | 0.0081178 | 0.020721 | 0.028198 | 0.057037 | 0.061523 | 0.15829 | -0.12817 | -0.15564 | -0.1831 | 5.9784 | 5.9647 | 5.8868 | 0.064087 | 0.009155 | 122.5525 | -0.24261 | -0.013732 | -122.6852 | 0.041199 | 6.1478 | -116.5649 | -0.073242 | 0.022888 | 0.054931 | 0.23346 | 0.17853 | 6.134 | 0.013733 | 0.041199 | 122.7219 | 6.0562 | -0.073242 | 0.013733 | 0.041199 | 6.0562 | 6.134 | 122.7219 | -122.7127 | -122.7722
1128.9688 | 122.6944 | -0.17395 | 122.5388 | -0.022889 | 0.009613 | 0.020935 | 0.033539 | 0.059387 | 0.060883 | 0.15637 | -0.16022 | -0.11902 | -0.21515 | 5.9097 | 5.864 | 5.7541 | 0.18768 | -0.091553 | 122.6074 | -0.24261 | -0.041199 | -122.6578 | 0.013733 | 6.0837 | -116.6748 | -0.068665 | 0.068665 | 0.054932 | 0.36163 | 0.082397 | 6.0379 | 0.054931 | 0.013733 | 122.7814 | 5.928 | -0.068665 | 0.054931 | 0.013733 | 5.928 | 6.0379 | 122.7814 | -122.7539 | -122.7814
1129.9688 | 122.7631 | -0.20142 | 122.5433 | 0.015259 | 0.010895 | 0.02478 | 0.03653 | 0.059387 | 0.059814 | 0.15659 | -0.13733 | -0.13275 | -0.23804 | 5.928 | 5.8868 | 5.7861 | 0.11902 | -0.064087 | 122.5342 | -0.28381 | -0.036621 | -122.6761 | 0.064087 | 6.1295 | -116.6565 | -0.082397 | -0.009155 | 0.10071 | 0.32044 | 0.13733 | 6.0883 | 0.068665 | 0.064087 | 122.7356 | 5.9875 | -0.082397 | 0.068665 | 0.064087 | 5.9875 | 6.0883 | 122.7356 | -122.7814 | -122.8271
1131.0312 | 122.7997 | -0.17395 | 122.5067 | 0.053405 | 0.010895 | 0.025635 | 0.029266 | 0.058105 | 0.061737 | 0.15573 | -0.064087 | -0.16479 | -0.18768 | 6.0287 | 6.0013 | 5.8914 | 0.027466 | 0.050354 | 122.5479 | -0.23804 | -0.013733 | -122.6715 | 0.10986 | 6.2027 | -116.5054 | -0.064087 | 0.041199 | 0.1236 | 0.20142 | 0.2243 | 6.1752 | 0.009155 | 0.10986 | 122.7219 | 6.0654 | -0.064087 | 0.009155 | 0.10986 | 6.0654 | 6.1752 | 122.7219 | -122.6944 | -122.7448
1131.9844 | 122.7722 | -0.19226 | 122.5296 | 0.13733 | 0.010254 | 0.021362 | 0.037384 | 0.057678 | 0.057892 | 0.15765 | -0.09613 | -0.14191 | -0.21515 | 5.9738 | 5.9418 | 5.809 | 0.11444 | -0.045776 | 122.5525 | -0.27008 | -0.022888 | -122.6715 | 0.096131 | 6.1661 | -116.5878 | -0.07782 | 0.022888 | 0.11902 | 0.3067 | 0.14648 | 6.134 | 0.050354 | 0.096131 | 122.7448 | 6.0013 | -0.07782 | 0.050354 | 0.096131 | 6.0013 | 6.134 | 122.7448 | -122.7448 | -122.7997
1133.0156 | 122.8226 | -0.16937 | 122.5388 | 0.22888 | 0.008545 | 0.020081 | 0.026917 | 0.058746 | 0.062378 | 0.15744 | -0.1236 | -0.15106 | -0.17853 | 5.9784 | 5.9647 | 5.8319 | 0.068665 | -0.009155 | 122.5571 | -0.24719 | -0.009155 | -122.6898 | 0.045777 | 6.1478 | -116.5741 | -0.077819 | 0.018311 | 0.054932 | 0.23804 | 0.16022 | 6.134 | 0.018311 | 0.045777 | 122.7264 | 6.0013 | -0.077819 | 0.018311 | 0.045777 | 6.0013 | 6.134 | 122.7264 | -122.7173 | -122.7859
1133.9844 | 122.7676 | -0.1831 | 122.5296 | 1.6785 | 0.0091858 | 0.024994 | 0.038452 | 0.05896 | 0.057251 | 0.15915 | -0.032043 | -0.09613 | -0.13733 | 6.0287 | 5.983 | 5.8273 | 0.16937 | -0.036621 | 122.5891 | -0.23346 | 0.045776 | -122.6257 | 0.15106 | 6.2119 | -116.5466 | -0.050354 | 0.059509 | 0.10529 | 0.35248 | 0.14648 | 6.1661 | 0.086975 | 0.15106 | 122.7722 | 6.0104 | -0.050354 | 0.086975 | 0.15106 | 6.0104 | 6.1661 | 122.7722 | -122.6669 | -122.7631
1135.0312 | 122.8271 | -0.15106 | 122.5159 | 0.50354 | 0.010254 | 0.02243 | 0.02948 | 0.059387 | 0.060455 | 0.1553 | -0.064087 | -0.17853 | -0.1831 | 6.2393 | 6.2164 | 6.134 | 0.25177 | 0.041199 | 122.5342 | -0.23804 | -0.032043 | -122.6944 | 0.086975 | 6.3904 | -116.2994 | -0.086975 | 0.018311 | 0.11902 | 0.40283 | 0.19226 | 6.3675 | -0.027466 | 0.086975 | 122.6852 | 6.2851 | -0.086975 | -0.027466 | 0.086975 | 6.2851 | 6.3675 | 122.6852 | -122.699 | -122.7539
1135.9688 | 122.7356 | -0.20599 | 122.5296 | 0.053405 | 0.011108 | 0.020294 | 0.033966 | 0.058746 | 0.058746 | 0.15723 | -0.15106 | -0.11902 | -0.23804 | 6.0196 | 6.0059 | 5.8868 | 0.3067 | -0.09613 | 122.5891 | -0.31128 | -0.032043 | -122.6486 | 0.054932 | 6.2256 | -116.5237 | -0.10528 | 0.059509 | 0.086975 | 0.5127 | 0.10986 | 6.2119 | 0.086975 | 0.054932 | 122.7951 | 6.0928 | -0.10528 | 0.086975 | 0.054932 | 6.0928 | 6.2119 | 122.7951 | -122.7676 | -122.8409
1137.0156 | 122.8043 | -0.16937 | 122.5296 | 0.18311 | 0.0074768 | 0.021149 | 0.02948 | 0.057678 | 0.060669 | 0.15872 | -0.1236 | -0.16022 | -0.17395 | 6.0333 | 6.0287 | 5.9143 | 0.1236 | 0 | 122.5754 | -0.25177 | -0.004577 | -122.6898 | 0.045777 | 6.2027 | -116.5009 | -0.082397 | 0.045776 | 0.050354 | 0.29297 | 0.16937 | 6.1981 | 0.009156 | 0.045777 | 122.7448 | 6.0837 | -0.082397 | 0.009156 | 0.045777 | 6.0837 | 6.1981 | 122.7448 | -122.7036 | -122.7814
1137.9688 | 122.8317 | -0.14191 | 122.5525 | 0.007629 | 0.0074768 | 0.023712 | 0.032684 | 0.055969 | 0.058746 | 0.15744 | -0.064087 | -0.16479 | -0.17853 | 6.2347 | 6.2073 | 6.0562 | 0.25635 | 0.064087 | 122.5296 | -0.25177 | -0.036621 | -122.7173 | 0.07782 | 6.3766 | -116.3452 | -0.10986 | -0.022888 | 0.11444 | 0.39826 | 0.20599 | 6.3492 | -0.022888 | 0.07782 | 122.6715 | 6.1981 | -0.10986 | -0.022888 | 0.07782 | 6.1981 | 6.3492 | 122.6715 | -122.731 | -122.8043
1139.0156 | 122.8226 | -0.15564 | 122.5342 | 0.17548 | 0.0083314 | 0.020508 | 0.030975 | 0.058105 | 0.05896 | 0.15958 | -0.10071 | -0.15106 | -0.16937 | 6.1569 | 6.1295 | 6.0104 | 0.22888 | 0.027466 | 122.5571 | -0.24719 | -0.013733 | -122.6852 | 0.054932 | 6.3126 | -116.4047 | -0.091552 | 0.022888 | 0.068665 | 0.38452 | 0.18311 | 6.2851 | 0.004578 | 0.054932 | 122.7127 | 6.1661 | -0.091552 | 0.004578 | 0.054932 | 6.1661 | 6.2851 | 122.7127 | -122.7036 | -122.7814
1139.9688 | 122.7997 | -0.17853 | 122.5433 | 0.007629 | 0.0083314 | 0.020508 | 0.033325 | 0.056824 | 0.059174 | 0.15552 | -0.050354 | -0.15106 | -0.17395 | 6.3309 | 6.2759 | 6.1615 | 0.40741 | 0.027466 | 122.5662 | -0.25635 | 0.004578 | -122.6944 | 0.12817 | 6.5094 | -116.2674 | -0.07782 | 0.022888 | 0.1236 | 0.58594 | 0.20599 | 6.4545 | 0.027466 | 0.12817 | 122.7448 | 6.34 | -0.07782 | 0.027466 | 0.12817 | 6.34 | 6.4545 | 122.7448 | -122.7173 | -122.7997
1141.0156 | 122.7905 | -0.17395 | 122.5159 | 0.24414 | 0.0087586 | 0.019653 | 0.033539 | 0.054901 | 0.057678 | 0.15765 | -0.10986 | -0.15564 | -0.19226 | 6.2302 | 6.2119 | 6.1203 | 0.33417 | -0.027466 | 122.5525 | -0.23346 | -0.018311 | -122.6715 | 0.064087 | 6.4041 | -116.304 | -0.059509 | 0.036621 | 0.082398 | 0.50812 | 0.14648 | 6.3858 | 0.01831 | 0.064087 | 122.7264 | 6.2942 | -0.059509 | 0.01831 | 0.064087 | 6.2942 | 6.3858 | 122.7264 | -122.7081 | -122.7493
1141.9844 | 122.7585 | -0.16022 | 122.5479 | -0.030518 | 0.010254 | 0.023712 | 0.035675 | 0.056183 | 0.057037 | 0.15808 | -0.091553 | -0.12817 | -0.20142 | 6.2302 | 6.189 | 6.0745 | 0.39825 | -0.009155 | 122.5845 | -0.25635 | -0.041199 | -122.6761 | 0.068664 | 6.3904 | -116.3589 | -0.096131 | 0.036621 | 0.10986 | 0.55847 | 0.15106 | 6.3492 | 0.032043 | 0.068664 | 122.7448 | 6.2347 | -0.096131 | 0.032043 | 0.068664 | 6.2347 | 6.3492 | 122.7448 | -122.7493 | -122.8043
1143.0156 | 122.818 | -0.16022 | 122.5342 | 0.16022 | 0.0072632 | 0.021149 | 0.031189 | 0.055115 | 0.059387 | 0.15701 | -0.10071 | -0.16022 | -0.1831 | 6.2759 | 6.2485 | 6.1249 | 0.36163 | 0.036621 | 122.5433 | -0.23346 | -0.022888 | -122.6944 | 0.059509 | 6.4362 | -116.2857 | -0.073242 | 0.009155 | 0.082397 | 0.52185 | 0.19684 | 6.4087 | 0 | 0.059509 | 122.7036 | 6.2851 | -0.073242 | 0 | 0.059509 | 6.2851 | 6.4087 | 122.7036 | -122.7173 | -122.7676
1143.9688 | 122.8134 | -0.1831 | 122.5204 | 0.053405 | 0.0070496 | 0.020935 | 0.033966 | 0.054901 | 0.05191 | 0.15359 | -0.041199 | -0.16022 | -0.18768 | 8.9264 | 8.7067 | 8.8211 | 3.1265 | 0.041199 | 122.525 | -0.26093 | -0.004578 | -122.6807 | 0.14191 | 9.1095 | -113.8138 | -0.07782 | 0.004577 | 0.14648 | 3.3096 | 0.2243 | 8.8898 | 0.022888 | 0.14191 | 122.7081 | 9.0042 | -0.07782 | 0.022888 | 0.14191 | 9.0042 | 8.8898 | 122.7081 | -122.7081 | -122.7814
1145.0312 | 122.8546 | -0.15106 | 122.5479 | 0.16022 | 0.0066224 | 0.019867 | 0.03183 | 0.054474 | 0.061096 | 0.15936 | -0.068665 | -0.14191 | -0.1831 | 5.9784 | 5.9372 | 5.8502 | 0.018311 | 0.050354 | 122.5571 | -0.21515 | -0.032043 | -122.6898 | 0.082397 | 6.1295 | -116.6107 | -0.064087 | 0.009155 | 0.11444 | 0.16937 | 0.20142 | 6.0883 | 0.009155 | 0.082397 | 122.7081 | 6.0013 | -0.064087 | 0.009155 | 0.082397 | 6.0013 | 6.0883 | 122.7081 | -122.731 | -122.7631
1145.9688 | 122.8821 | -0.15106 | 122.525 | 0.091552 | 0.0093994 | 0.016663 | 0.034393 | 0.054901 | 0.061737 | 0.15765 | -0.036621 | -0.15564 | -0.16479 | 6.0104 | 5.983 | 5.8777 | -0.018311 | 0.068665 | 122.5525 | -0.23346 | -0.013733 | -122.6807 | 0.11444 | 6.1615 | -116.5421 | -0.082397 | 0.027466 | 0.12817 | 0.13275 | 0.21973 | 6.134 | -0.004578 | 0.11444 | 122.7036 | 6.0287 | -0.082397 | -0.004578 | 0.11444 | 6.0287 | 6.134 | 122.7036 | -122.6898 | -122.7585
1146.9688 | 122.8134 | -0.13275 | 122.5342 | 0.22125 | 0.0070496 | 0.02243 | 0.032898 | 0.054047 | 0.059814 | 0.15787 | -0.086975 | -0.15564 | -0.17395 | 5.9738 | 5.9372 | 5.8365 | 0.045776 | 0.018311 | 122.5662 | -0.23804 | -0.041199 | -122.6898 | 0.045776 | 6.1066 | -116.597 | -0.10529 | 0.032043 | 0.086975 | 0.17853 | 0.15106 | 6.0699 | -0.022889 | 0.045776 | 122.699 | 5.9692 | -0.10529 | -0.022889 | 0.045776 | 5.9692 | 6.0699 | 122.699 | -122.7081 | -122.7722
1148.0156 | 122.7997 | -0.13733 | 122.525 | 0.38147 | 0.0076904 | 0.017944 | 0.034393 | 0.057251 | 0.060883 | 0.15594 | -0.036621 | -0.16479 | -0.17395 | 5.983 | 5.928 | 5.8273 | 0.041199 | 0 | 122.5388 | -0.23804 | -0.036621 | -122.6898 | 0.10071 | 6.1203 | -116.597 | -0.10071 | 0.013733 | 0.13733 | 0.17853 | 0.13733 | 6.0654 | -0.027466 | 0.10071 | 122.6761 | 5.9647 | -0.10071 | -0.027466 | 0.10071 | 5.9647 | 6.0654 | 122.6761 | -122.699 | -122.7631
1148.9688 | 122.6898 | -0.21973 | 122.5479 | -0.030518 | 0.009613 | 0.022644 | 0.038025 | 0.057037 | 0.058746 | 0.15851 | -0.15564 | -0.11444 | -0.2243 | 5.9235 | 5.8731 | 5.6625 | 0.22888 | -0.068665 | 122.5891 | -0.27924 | -0.004577 | -122.6624 | 0.064087 | 6.1432 | -116.6748 | -0.059509 | 0.041198 | 0.068664 | 0.44861 | 0.15106 | 6.0928 | 0.10529 | 0.064087 | 122.8088 | 5.8823 | -0.059509 | 0.10529 | 0.064087 | 5.8823 | 6.0928 | 122.8088 | -122.7722 | -122.8271
1150.0156 | 122.7905 | -0.18768 | 122.5388 | 0.34332 | 0.0055542 | 0.022003 | 0.032257 | 0.05896 | 0.058533 | 0.15851 | -0.086975 | -0.14191 | -0.16479 | 6.0471 | 6.0104 | 5.9006 | 0.10986 | -0.032043 | 122.5708 | -0.22888 | 0.022888 | -122.6807 | 0.10071 | 6.2347 | -116.5283 | -0.041199 | 0.032044 | 0.07782 | 0.29755 | 0.15564 | 6.1981 | 0.045776 | 0.10071 | 122.7585 | 6.0883 | -0.041199 | 0.045776 | 0.10071 | 6.0883 | 6.1981 | 122.7585 | -122.7036 | -122.7676
1150.9688 | 122.7219 | -0.18768 | 122.5708 | 0 | 0.01004 | 0.023712 | 0.036316 | 0.05661 | 0.055328 | 0.15701 | -0.091553 | -0.13275 | -0.20142 | 6.0883 | 6.0562 | 5.9052 | 0.36621 | -0.059509 | 122.5891 | -0.27924 | -0.013733 | -122.7036 | 0.09613 | 6.2759 | -116.5146 | -0.091553 | 0.01831 | 0.10986 | 0.55389 | 0.12817 | 6.2439 | 0.054932 | 0.09613 | 122.7768 | 6.0928 | -0.091553 | 0.054932 | 0.09613 | 6.0928 | 6.2439 | 122.7768 | -122.7722 | -122.85
1152.0156 | 122.8226 | -0.14191 | 122.5204 | 0.38147 | 0.0087586 | 0.021362 | 0.035034 | 0.057892 | 0.060028 | 0.15851 | -0.050354 | -0.17395 | -0.17853 | 6.3675 | 6.3263 | 6.1935 | 0.34332 | 0.018311 | 122.5571 | -0.23346 | -0.036621 | -122.6944 | 0.091553 | 6.5094 | -116.1942 | -0.091552 | 0.036621 | 0.12817 | 0.48523 | 0.16022 | 6.4682 | -0.032043 | 0.091553 | 122.699 | 6.3354 | -0.091552 | -0.032043 | 0.091553 | 6.3354 | 6.4682 | 122.699 | -122.699 | -122.7539
1152.9688 | 122.8363 | -0.12817 | 122.525 | 0.16022 | 0.0081178 | 0.022644 | 0.031403 | 0.054687 | 0.058533 | 0.15594 | -0.036621 | -0.13275 | -0.15564 | 6.3766 | 6.3309 | 6.2119 | 0.35706 | 0.068665 | 122.5479 | -0.22888 | -0.027466 | -122.6578 | 0.091553 | 6.5048 | -116.1942 | -0.10071 | 0.022889 | 0.11902 | 0.48523 | 0.19684 | 6.459 | -0.004577 | 0.091553 | 122.6761 | 6.34 | -0.10071 | -0.004577 | 0.091553 | 6.34 | 6.459 | 122.6761 | -122.6807 | -122.7539
1154.0156 | 122.8088 | -0.16479 | 122.5433 | 0.26703 | 0.0076904 | 0.022644 | 0.032257 | 0.057678 | 0.059387 | 0.15723 | -0.10986 | -0.1236 | -0.16022 | 6.221 | 6.1981 | 6.0654 | 0.31128 | -0.018311 | 122.5662 | -0.24261 | 0.004578 | -122.6669 | 0.054932 | 6.3858 | -116.3452 | -0.07782 | 0.022888 | 0.050354 | 0.47607 | 0.14648 | 6.3629 | 0.041199 | 0.054932 | 122.731 | 6.2302 | -0.07782 | 0.041199 | 0.054932 | 6.2302 | 6.3629 | 122.731 | -122.7036 | -122.7859
1154.9688 | 122.7127 | -0.19226 | 122.58 | -0.0076295 | 0.0093994 | 0.025635 | 0.036316 | 0.057251 | 0.059174 | 0.15829 | -0.14191 | -0.1236 | -0.20599 | 6.1981 | 6.1432 | 5.9601 | 0.45319 | -0.073242 | 122.6074 | -0.27924 | -0.013733 | -122.7036 | 0.050354 | 6.3904 | -116.4368 | -0.086975 | 0.027466 | 0.064087 | 0.64545 | 0.11902 | 6.3354 | 0.068665 | 0.050354 | 122.7997 | 6.1523 | -0.086975 | 0.068665 | 0.050354 | 6.1523 | 6.3354 | 122.7997 | -122.7859 | -122.8592
1156.0156 | 122.7997 | -0.17395 | 122.5388 | 0.16022 | 0.0076904 | 0.02478 | 0.031189 | 0.056183 | 0.058533 | 0.1568 | -0.15106 | -0.20142 | -0.23804 | 6.3538 | 6.3309 | 6.2759 | 0.4303 | -0.027466 | 122.5616 | -0.25177 | -0.064087 | -122.7402 | 0.022888 | 6.5277 | -116.2079 | -0.07782 | 0.022889 | 0.086975 | 0.60425 | 0.14648 | 6.5048 | -0.027466 | 0.022888 | 122.7356 | 6.4499 | -0.07782 | -0.027466 | 0.022888 | 6.4499 | 6.5048 | 122.7356 | -122.7768 | -122.7905
1156.9688 | 122.8638 | -0.14191 | 122.5204 | 0.038147 | 0.008545 | 0.020508 | 0.03183 | 0.052338 | 0.06131 | 0.15659 | -0.050354 | -0.12817 | -0.16479 | 6.2851 | 6.2485 | 6.134 | 0.2243 | 0.082397 | 122.5296 | -0.22888 | -0.022888 | -122.6486 | 0.091553 | 6.427 | -116.272 | -0.086975 | 0.009155 | 0.11444 | 0.36621 | 0.2243 | 6.3904 | 0.013733 | 0.091553 | 122.6715 | 6.2759 | -0.086975 | 0.013733 | 0.091553 | 6.2759 | 6.3904 | 122.6715 | -122.6852 | -122.7493
1158.0312 | 122.8546 | -0.13275 | 122.5525 | 0.12207 | 0.0070496 | 0.022644 | 0.03183 | 0.053833 | 0.060669 | 0.15723 | -0.050354 | -0.13275 | -0.16937 | 6.2942 | 6.2485 | 6.1295 | 0.2655 | 0.073242 | 122.5479 | -0.24261 | -0.036622 | -122.6852 | 0.082397 | 6.427 | -116.304 | -0.10986 | -0.004577 | 0.11902 | 0.39825 | 0.20599 | 6.3812 | 0 | 0.082397 | 122.6807 | 6.2622 | -0.10986 | 0 | 0.082397 | 6.2622 | 6.3812 | 122.6807 | -122.7219 | -122.7951
1158.9688 | 122.8775 | -0.12817 | 122.5204 | 0.091552 | 0.0064088 | 0.018799 | 0.03183 | 0.05661 | 0.05896 | 0.16 | -0.059509 | -0.14191 | -0.15564 | 6.4041 | 6.3675 | 6.308 | 0.37994 | 0.068665 | 122.5754 | -0.22888 | -0.027466 | -122.6624 | 0.068665 | 6.5323 | -116.153 | -0.10071 | 0.054931 | 0.096131 | 0.50812 | 0.19684 | 6.4957 | -0.013733 | 0.068665 | 122.7036 | 6.4362 | -0.10071 | -0.013733 | 0.068665 | 6.4362 | 6.4957 | 122.7036 | -122.6761 | -122.7493
1160.0156 | 122.8043 | -0.15564 | 122.5754 | 0.2594 | 0.0061952 | 0.022217 | 0.032471 | 0.056824 | 0.05896 | 0.15894 | -0.10071 | -0.13733 | -0.16022 | 6.1615 | 6.1295 | 6.0242 | 0.26093 | -0.018311 | 122.5571 | -0.24719 | -0.004577 | -122.7127 | 0.054932 | 6.3171 | -116.4459 | -0.091552 | -0.01831 | 0.059509 | 0.41657 | 0.13733 | 6.2851 | 0.018311 | 0.054932 | 122.7127 | 6.1798 | -0.091552 | 0.018311 | 0.054932 | 6.1798 | 6.2851 | 122.7127 | -122.7356 | -122.8226
1160.9688 | 122.8546 | -0.14191 | 122.5433 | 0.16785 | 0.0053406 | 0.018158 | 0.032684 | 0.053833 | 0.06131 | 0.1568 | -0.064087 | -0.13733 | -0.16022 | 6.2988 | 6.2439 | 6.1478 | 0.29297 | 0.032043 | 122.58 | -0.21515 | -0.01831 | -122.6807 | 0.07782 | 6.4407 | -116.2994 | -0.073242 | 0.036621 | 0.09613 | 0.43488 | 0.17395 | 6.3858 | 0.004578 | 0.07782 | 122.7219 | 6.2897 | -0.073242 | 0.004578 | 0.07782 | 6.2897 | 6.3858 | 122.7219 | -122.7036 | -122.7585
1162.0156 | 122.8683 | -0.1831 | 122.5113 | 0.38147 | 0.0089722 | 0.019226 | 0.035889 | 0.057892 | 0.060883 | 0.15637 | -0.022888 | -0.16479 | -0.16937 | 6.1203 | 6.0791 | 5.9692 | -0.27466 | -0.15106 | 122.4701 | -0.27008 | 0.013732 | -122.6761 | 0.16022 | 6.3034 | -116.4322 | -0.086976 | -0.041199 | 0.14649 | -0.091553 | 0.032043 | 6.2622 | 0.01831 | 0.16022 | 122.6532 | 6.1523 | -0.086976 | 0.01831 | 0.16022 | 6.1523 | 6.2622 | 122.6532 | -122.6807 | -122.7814
1162.9688 | 122.7264 | -0.1831 | 122.5937 | -0.022889 | 0.009613 | 0.022003 | 0.034607 | 0.056183 | 0.060028 | 0.15851 | -0.082397 | -0.13275 | -0.19684 | 6.2851 | 6.2576 | 6.0608 | 0.49439 | -0.032043 | 122.5845 | -0.24719 | -0.013733 | -122.7264 | 0.10071 | 6.4682 | -116.3361 | -0.064087 | -0.009155 | 0.11444 | 0.67749 | 0.15106 | 6.4407 | 0.050354 | 0.10071 | 122.7676 | 6.2439 | -0.064087 | 0.050354 | 0.10071 | 6.2439 | 6.4407 | 122.7676 | -122.7905 | -122.8409
1164.0312 | 122.85 | -0.12817 | 122.5616 | 0.12207 | 0.0081178 | 0.018799 | 0.032684 | 0.055969 | 0.060242 | 0.15552 | -0.027466 | -0.13275 | -0.16022 | 6.3446 | 6.3171 | 6.2302 | 0.33417 | 0.073242 | 122.5891 | -0.22888 | -0.032043 | -122.6944 | 0.10071 | 6.4728 | -116.2445 | -0.10071 | 0.027465 | 0.13275 | 0.46234 | 0.20142 | 6.4453 | -0.004577 | 0.10071 | 122.7173 | 6.3583 | -0.10071 | -0.004577 | 0.10071 | 6.3583 | 6.4453 | 122.7173 | -122.7219 | -122.7905
1164.9688 | 122.85 | -0.12817 | 122.5571 | 0.11444 | 0.0076904 | 0.022003 | 0.030335 | 0.054687 | 0.058746 | 0.15765 | -0.059509 | -0.13275 | -0.17395 | 6.4316 | 6.4224 | 6.3034 | 0.41657 | 0.059509 | 122.5662 | -0.22888 | -0.045776 | -122.6898 | 0.068665 | 6.5598 | -116.1346 | -0.10071 | 0.009155 | 0.11444 | 0.54474 | 0.18768 | 6.5506 | -0.004577 | 0.068665 | 122.6944 | 6.4316 | -0.10071 | -0.004577 | 0.068665 | 6.4316 | 6.5506 | 122.6944 | -122.731 | -122.7859
1166.0156 | 122.8134 | -0.12817 | 122.5479 | 0.37384 | 0.0072632 | 0.023071 | 0.034393 | 0.056824 | 0.059387 | 0.15701 | -0.045776 | -0.15564 | -0.18768 | 6.3721 | 6.3354 | 6.2164 | 0.30212 | 0.022888 | 122.5616 | -0.24261 | -0.059509 | -122.7036 | 0.082398 | 6.5002 | -116.2125 | -0.11444 | 0.013733 | 0.14191 | 0.4303 | 0.15106 | 6.4636 | -0.027466 | 0.082398 | 122.6898 | 6.3446 | -0.11444 | -0.027466 | 0.082398 | 6.3446 | 6.4636 | 122.6898 | -122.7356 | -122.7905
1166.9688 | 122.8455 | -0.12817 | 122.5754 | 0.16785 | 0.0066224 | 0.019653 | 0.030548 | 0.056183 | 0.060028 | 0.15637 | -0.086975 | -0.12817 | -0.17853 | 6.4865 | 6.4545 | 6.3538 | 0.44861 | 0.041199 | 122.5662 | -0.21057 | -0.050354 | -122.7036 | 0.041199 | 6.6147 | -116.1209 | -0.082397 | -0.009155 | 0.091553 | 0.57678 | 0.16937 | 6.5826 | 0 | 0.041199 | 122.6944 | 6.4819 | -0.082397 | 0 | 0.041199 | 6.4819 | 6.5826 | 122.6944 | -122.7539 | -122.7859
1168.0312 | 122.7768 | -0.21515 | 122.5708 | 0.22125 | 0.0079042 | 0.025848 | 0.032471 | 0.054901 | 0.061951 | 0.15359 | -0.10529 | -0.15106 | -0.18768 | 6.5094 | 6.514 | 6.4957 | 0.56763 | -0.022888 | 122.5067 | -0.31128 | 0.027466 | -122.7219 | 0.10986 | 6.7245 | -116.0568 | -0.09613 | -0.064087 | 0.082397 | 0.78278 | 0.19226 | 6.7291 | 0.064087 | 0.10986 | 122.7219 | 6.7108 | -0.09613 | 0.064087 | 0.10986 | 6.7108 | 6.7291 | 122.7219 | -122.7585 | -122.8821
1168.9688 | 122.8088 | -0.15564 | 122.5983 | 0.22125 | 0.0076904 | 0.020081 | 0.032684 | 0.056824 | 0.059387 | 0.15701 | -0.086975 | -0.14191 | -0.17395 | 6.5918 | 6.5598 | 6.3721 | 0.55847 | 0.041199 | 122.5571 | -0.22888 | -0.01831 | -122.7402 | 0.068665 | 6.7474 | -116.0385 | -0.073242 | -0.041199 | 0.086975 | 0.71411 | 0.19684 | 6.7154 | 0.013733 | 0.068665 | 122.7127 | 6.5277 | -0.073242 | 0.013733 | 0.068665 | 6.5277 | 6.7154 | 122.7127 | -122.7722 | -122.8271
1170.0156 | 122.7814 | -0.20599 | 122.4792 | 0.27466 | 0.0089722 | 0.018799 | 0.030762 | 0.055542 | 0.057892 | 0.15659 | -0.10986 | -0.13275 | -0.17395 | 6.6422 | 6.6055 | 6.4774 | 0.70038 | -0.045776 | 122.5342 | -0.28381 | 0.032044 | -122.612 | 0.096131 | 6.8481 | -115.8737 | -0.077819 | 0.054932 | 0.064087 | 0.90637 | 0.16022 | 6.8115 | 0.073243 | 0.096131 | 122.7402 | 6.6834 | -0.077819 | 0.073243 | 0.096131 | 6.6834 | 6.8115 | 122.7402 | -122.6532 | -122.7631
1170.9688 | 122.7585 | -0.16022 | 122.5754 | -0.045776 | 0.0081178 | 0.020081 | 0.035248 | 0.057037 | 0.058746 | 0.15552 | -0.050354 | -0.11444 | -0.1831 | 6.2347 | 6.1981 | 5.9509 | 0.14191 | 0.009155 | 122.6166 | -0.26093 | -0.022888 | -122.6898 | 0.10986 | 6.395 | -116.3773 | -0.10071 | 0.041199 | 0.13275 | 0.30212 | 0.16937 | 6.3583 | 0.045776 | 0.10986 | 122.7768 | 6.1111 | -0.10071 | 0.045776 | 0.10986 | 6.1111 | 6.3583 | 122.7768 | -122.7585 | -122.8363
1172.0156 | 122.818 | -0.14191 | 122.5845 | 0.37384 | 0.0081178 | 0.024353 | 0.033539 | 0.055542 | 0.056824 | 0.15829 | -0.041199 | -0.14648 | -0.16937 | 6.2759 | 6.2439 | 6.1432 | -0.004578 | 0.018311 | 122.5388 | -0.21973 | -0.027466 | -122.731 | 0.10071 | 6.4178 | -116.3406 | -0.07782 | -0.045777 | 0.12817 | 0.13733 | 0.16022 | 6.3858 | -0.004577 | 0.10071 | 122.6807 | 6.2851 | -0.07782 | -0.004577 | 0.10071 | 6.2851 | 6.3858 | 122.6807 | -122.7539 | -122.8043
1172.9688 | 122.85 | -0.12817 | 122.5983 | 0.16022 | 0.0074768 | 0.023926 | 0.033325 | 0.054047 | 0.058746 | 0.15659 | -0.059509 | -0.12817 | -0.16479 | 6.5048 | 6.4682 | 6.3904 | 0.041199 | 0.059509 | 122.5937 | -0.2243 | -0.036621 | -122.7264 | 0.068665 | 6.633 | -116.1301 | -0.09613 | -0.004578 | 0.10529 | 0.16937 | 0.18768 | 6.5964 | 0 | 0.068665 | 122.7219 | 6.5186 | -0.09613 | 0 | 0.068665 | 6.5186 | 6.5964 | 122.7219 | -122.7631 | -122.8226
1174.0156 | 122.8317 | -0.12817 | 122.58 | 0.34332 | 0.010254 | 0.02243 | 0.032898 | 0.05426 | 0.059601 | 0.15659 | -0.050354 | -0.16479 | -0.17395 | 6.7886 | 6.7474 | 6.6467 | 0.004578 | 0.032043 | 122.5616 | -0.21973 | -0.045776 | -122.7448 | 0.07782 | 6.9168 | -115.8325 | -0.091553 | -0.01831 | 0.1236 | 0.13275 | 0.16022 | 6.8756 | -0.036621 | 0.07782 | 122.6898 | 6.7749 | -0.091553 | -0.036621 | 0.07782 | 6.7749 | 6.8756 | 122.6898 | -122.7539 | -122.7997
1174.9688 | 122.7356 | -0.17853 | 122.6074 | 0.038147 | 0.0072632 | 0.019867 | 0.033966 | 0.057892 | 0.059174 | 0.15701 | -0.12817 | -0.11902 | -0.21057 | 6.5598 | 6.5277 | 6.3583 | 0.19684 | -0.064087 | 122.612 | -0.2655 | -0.032043 | -122.7264 | 0.050354 | 6.7383 | -116.0797 | -0.086975 | 0.004578 | 0.082397 | 0.37537 | 0.11444 | 6.7062 | 0.059509 | 0.050354 | 122.7905 | 6.5369 | -0.086975 | 0.059509 | 0.050354 | 6.5369 | 6.7062 | 122.7905 | -122.818 | -122.8729
1176.0156 | 122.8271 | -0.13275 | 122.5571 | 0.37384 | 0.0098268 | 0.019013 | 0.034393 | 0.058105 | 0.058746 | 0.15616 | -0.045776 | -0.16479 | -0.15564 | 6.5689 | 6.5369 | 6.4133 | 0 | 0.022888 | 122.5937 | -0.22888 | -0.022889 | -122.7219 | 0.086975 | 6.7017 | -116.0202 | -0.096131 | 0.036621 | 0.10986 | 0.13275 | 0.15564 | 6.6696 | -0.032044 | 0.086975 | 122.7264 | 6.546 | -0.096131 | -0.032044 | 0.086975 | 6.546 | 6.6696 | 122.7264 | -122.7127 | -122.7859
1176.9688 | 122.8683 | -0.14648 | 122.5662 | 0.083923 | 0.0074768 | 0.023926 | 0.032471 | 0.056396 | 0.060242 | 0.15723 | -0.036621 | -0.16022 | -0.17853 | 6.5231 | 6.4774 | 6.3354 | 0.013733 | 0.086975 | 122.5708 | -0.21515 | -0.032044 | -122.7264 | 0.10986 | 6.6696 | -116.0889 | -0.068665 | 0.004578 | 0.14191 | 0.16022 | 0.23346 | 6.6238 | -0.013733 | 0.10986 | 122.7173 | 6.4819 | -0.068665 | -0.013733 | 0.10986 | 6.4819 | 6.6238 | 122.7173 | -122.7448 | -122.7814
1178.0156 | 122.8638 | -0.15564 | 122.5571 | 0.42725 | 0.0072632 | 0.024353 | 0.035461 | 0.058319 | 0.058746 | 0.15659 | -0.2243 | -0.16937 | -0.19684 | 6.5002 | 6.4362 | 6.2942 | -0.027466 | 0.032043 | 122.5296 | -0.23804 | -0.041198 | -122.7264 | -0.068664 | 6.6559 | -116.1209 | -0.082397 | -0.027466 | -0.027466 | 0.12817 | 0.18768 | 6.5918 | -0.013733 | -0.068664 | 122.6852 | 6.4499 | -0.082397 | -0.013733 | -0.068664 | 6.4499 | 6.5918 | 122.6852 | -122.7539 | -122.7951
1178.9688 | 122.7402 | -0.19684 | 122.5937 | 0.045776 | 0.011749 | 0.020294 | 0.035675 | 0.056396 | 0.060242 | 0.1568 | -0.14191 | -0.10986 | -0.21973 | 6.4224 | 6.3812 | 6.221 | 0.19684 | -0.059509 | 122.6212 | -0.26093 | -0.022889 | -122.7036 | 0.054931 | 6.6193 | -116.2125 | -0.064087 | 0.027466 | 0.07782 | 0.39368 | 0.13733 | 6.5781 | 0.086975 | 0.054931 | 122.818 | 6.4178 | -0.064087 | 0.086975 | 0.054931 | 6.4178 | 6.5781 | 122.818 | -122.8134 | -122.8546
1180.0156 | 122.8455 | -0.12817 | 122.5754 | 0.43488 | 0.006836 | 0.025848 | 0.036102 | 0.058105 | 0.060455 | 0.15659 | -0.054932 | -0.11902 | -0.20599 | 6.5689 | 6.5231 | 6.2759 | 0.027466 | 0.022888 | 122.58 | -0.2243 | -0.07782 | -122.6944 | 0.073242 | 6.6971 | -116.0522 | -0.09613 | 0.004578 | 0.15106 | 0.15564 | 0.15106 | 6.6513 | 0.009155 | 0.073242 | 122.7081 | 6.4041 | -0.09613 | 0.009155 | 0.073242 | 6.4041 | 6.6513 | 122.7081 | -122.7814 | -122.7997
1180.9688 | 122.7585 | -0.19684 | 122.6028 | -0.030518 | 0.010681 | 0.023926 | 0.036957 | 0.058319 | 0.058105 | 0.15509 | -0.13733 | -0.086975 | -0.20599 | 6.4865 | 6.4682 | 6.2393 | 0.20142 | -0.073242 | 122.6212 | -0.2655 | -0.009156 | -122.6898 | 0.059509 | 6.6833 | -116.1346 | -0.068665 | 0.018311 | 0.068665 | 0.39825 | 0.1236 | 6.665 | 0.10986 | 0.059509 | 122.818 | 6.4362 | -0.068665 | 0.10986 | 0.059509 | 6.4362 | 6.665 | 122.818 | -122.8088 | -122.8683
1182.0156 | 122.8363 | -0.11902 | 122.5891 | 0.35095 | 0.0070496 | 0.022217 | 0.032684 | 0.058105 | 0.059174 | 0.15573 | -0.041199 | -0.15564 | -0.16937 | 6.6376 | 6.6284 | 6.4499 | 0.004578 | 0.009155 | 122.5845 | -0.21973 | -0.050354 | -122.7448 | 0.07782 | 6.7566 | -115.9607 | -0.10071 | -0.004577 | 0.12817 | 0.1236 | 0.12817 | 6.7474 | -0.036621 | 0.07782 | 122.7036 | 6.5689 | -0.10071 | -0.036621 | 0.07782 | 6.5689 | 6.7474 | 122.7036 | -122.7585 | -122.8088
1182.9688 | 122.9965 | -0.15106 | 122.5204 | 0 | 0.0070496 | 0.019653 | 0.030335 | 0.057465 | 0.057892 | 0.15723 | -0.022888 | -0.15106 | -0.16937 | 6.6696 | 6.6376 | 6.4911 | 0.032043 | 0.091553 | 122.58 | -0.21515 | -0.018311 | -122.6715 | 0.12817 | 6.8207 | -115.8829 | -0.064087 | 0.059509 | 0.14649 | 0.18311 | 0.24261 | 6.7886 | 0 | 0.12817 | 122.731 | 6.6422 | -0.064087 | 0 | 0.12817 | 6.6422 | 6.7886 | 122.731 | -122.6898 | -122.7356
1184.0156 | 122.8729 | -0.14191 | 122.5571 | -0.59509 | 0.0074768 | 0.018799 | 0.035889 | 0.058533 | 0.058533 | 0.15744 | -0.064087 | -0.21057 | -0.20599 | 6.7337 | 6.6925 | 6.5277 | -0.032043 | 0.027466 | 122.5616 | -0.24261 | -0.064087 | -122.7676 | 0.07782 | 6.8756 | -115.8646 | -0.10071 | 0.004578 | 0.14191 | 0.10986 | 0.16937 | 6.8344 | -0.068664 | 0.07782 | 122.7036 | 6.6696 | -0.10071 | -0.068664 | 0.07782 | 6.6696 | 6.8344 | 122.7036 | -122.7631 | -122.7997
1184.9688 | 122.7448 | -0.1831 | 122.6212 | -0.022889 | 0.009613 | 0.022217 | 0.036957 | 0.056396 | 0.057892 | 0.15659 | -0.14191 | -0.09613 | -0.21515 | 6.6101 | 6.5598 | 6.4636 | 0.19684 | -0.082397 | 122.6349 | -0.27466 | -0.032044 | -122.7173 | 0.041198 | 6.7932 | -116.0614 | -0.091553 | 0.013733 | 0.073242 | 0.37994 | 0.10071 | 6.7429 | 0.086975 | 0.041198 | 122.818 | 6.6467 | -0.091553 | 0.086975 | 0.041198 | 6.6467 | 6.7429 | 122.818 | -122.8363 | -122.8958
1186.0156 | 122.8226 | -0.13733 | 122.5662 | 0.43488 | 0.0083314 | 0.02243 | 0.02948 | 0.054901 | 0.058746 | 0.15637 | -0.11902 | -0.16937 | -0.20599 | 6.7062 | 6.7017 | 6.459 | 0.064087 | 0.004578 | 122.5845 | -0.23346 | -0.068665 | -122.7356 | 0.01831 | 6.8436 | -115.8646 | -0.09613 | 0.018311 | 0.086975 | 0.20142 | 0.14191 | 6.839 | -0.032044 | 0.01831 | 122.7219 | 6.5964 | -0.09613 | -0.032044 | 0.01831 | 6.5964 | 6.839 | 122.7219 | -122.7722 | -122.7997
1186.9688 | 122.8546 | -0.16022 | 122.5708 | 0.022888 | 0.006836 | 0.01709 | 0.03183 | 0.056396 | 0.057465 | 0.15659 | -0.036621 | -0.12817 | -0.16479 | 6.8253 | 6.8069 | 6.514 | 0.068665 | 0.073242 | 122.5662 | -0.22888 | -0.004578 | -122.699 | 0.1236 | 6.9855 | -115.7639 | -0.068665 | -0.004578 | 0.12817 | 0.22888 | 0.23346 | 6.9672 | 0.032043 | 0.1236 | 122.7264 | 6.6742 | -0.068665 | 0.032043 | 0.1236 | 6.6742 | 6.9672 | 122.7264 | -122.7356 | -122.7997
1188.0156 | 122.7585 | -0.16479 | 122.5937 | 0.38147 | 0.009613 | 0.021149 | 0.038879 | 0.057251 | 0.063446 | 0.15552 | -0.14648 | -0.10529 | -0.21515 | 6.7154 | 6.9397 | 6.6284 | 0.16479 | -0.054932 | 122.6532 | -0.23346 | -0.050354 | -122.699 | 0.018311 | 6.8802 | -115.654 | -0.068664 | 0.059509 | 0.068665 | 0.32959 | 0.10986 | 7.1045 | 0.059509 | 0.018311 | 122.818 | 6.7932 | -0.068664 | 0.059509 | 0.018311 | 6.7932 | 7.1045 | 122.818 | -122.8088 | -122.8271
1188.9688 | 122.7722 | -0.20599 | 122.6166 | 0.022888 | 0.0089722 | 0.022003 | 0.037598 | 0.057678 | 0.059174 | 0.15723 | -0.13275 | -0.11902 | -0.2243 | 6.9443 | 6.8756 | 6.6422 | 0.18768 | -0.045776 | 122.5891 | -0.27924 | -0.01831 | -122.7356 | 0.073243 | 7.1503 | -115.741 | -0.073242 | -0.027466 | 0.091553 | 0.39368 | 0.16022 | 7.0816 | 0.086975 | 0.073243 | 122.7951 | 6.8481 | -0.073242 | 0.086975 | 0.073243 | 6.8481 | 7.0816 | 122.7951 | -122.8409 | -122.8958
1190.0156 | 122.8317 | -0.1831 | 122.5433 | 0.41199 | 0.01004 | 0.020721 | 0.035675 | 0.057037 | 0.057251 | 0.15424 | -0.036621 | -0.16022 | -0.19684 | 8.0017 | 7.9559 | 7.8781 | -0.032043 | 0.009155 | 122.5342 | -0.28381 | -0.013733 | -122.7036 | 0.14648 | 8.1848 | -114.5874 | -0.10071 | -0.009155 | 0.16022 | 0.15106 | 0.19226 | 8.139 | 0.022888 | 0.14648 | 122.7173 | 8.0612 | -0.10071 | 0.022888 | 0.14648 | 8.0612 | 8.139 | 122.7173 | -122.7402 | -122.8271
1190.9688 | 122.7814 | -0.17853 | 122.5845 | -0.061036 | 0.008545 | 0.021362 | 0.032898 | 0.056396 | 0.057892 | 0.15573 | -0.068665 | -0.13275 | -0.19684 | 7.988 | 7.9468 | 7.6813 | 0.16479 | 0.004578 | 122.5983 | -0.24719 | -0.01831 | -122.7173 | 0.10986 | 8.1665 | -114.6378 | -0.068664 | 0.013733 | 0.12817 | 0.34332 | 0.18311 | 8.1253 | 0.045777 | 0.10986 | 122.7768 | 7.8598 | -0.068664 | 0.045777 | 0.10986 | 7.8598 | 8.1253 | 122.7768 | -122.7814 | -122.8317
1191.9688 | 122.7905 | -0.16022 | 122.5662 | -0.061036 | 0.0079042 | 0.023712 | 0.033966 | 0.056396 | 0.059814 | 0.15573 | -0.068665 | -0.14648 | -0.18768 | 7.3334 | 7.3105 | 7.0679 | 0.17853 | 0.032043 | 122.6257 | -0.25635 | -0.027466 | -122.7127 | 0.091552 | 7.4936 | -115.2557 | -0.096131 | 0.059509 | 0.11902 | 0.33874 | 0.19226 | 7.4707 | 0.013733 | 0.091552 | 122.7859 | 7.2281 | -0.096131 | 0.013733 | 0.091552 | 7.2281 | 7.4707 | 122.7859 | -122.7539 | -122.8226
1193.0156 | 122.7951 | -0.14191 | 122.5754 | 0.36621 | 0.0093994 | 0.01944 | 0.032898 | 0.057465 | 0.05896 | 0.15616 | -0.073242 | -0.14191 | -0.18768 | 7.2601 | 7.2372 | 7.0999 | 0.10071 | -0.009155 | 122.6166 | -0.19684 | -0.045776 | -122.7173 | 0.068665 | 7.402 | -115.3381 | -0.054931 | 0.041199 | 0.11444 | 0.24262 | 0.13275 | 7.3792 | 0 | 0.068665 | 122.7585 | 7.2418 | -0.054931 | 0 | 0.068665 | 7.2418 | 7.3792 | 122.7585 | -122.7631 | -122.7722
1193.9688 | 122.8043 | -0.16022 | 122.5754 | 0.038147 | 0.0055542 | 0.022644 | 0.031616 | 0.057251 | 0.059814 | 0.15616 | -0.064087 | -0.14648 | -0.19226 | 7.3608 | 7.338 | 7.1457 | 0.16479 | 0.036621 | 122.5754 | -0.24261 | -0.032044 | -122.7219 | 0.09613 | 7.5211 | -115.2374 | -0.082398 | 0 | 0.12817 | 0.32501 | 0.19684 | 7.4982 | 0.013733 | 0.09613 | 122.7356 | 7.3059 | -0.082398 | 0.013733 | 0.09613 | 7.3059 | 7.4982 | 122.7356 | -122.7676 | -122.818
1195.0156 | 122.8683 | -0.14648 | 122.5388 | 0.54169 | 0.0089722 | 0.019653 | 0.03653 | 0.05896 | 0.058746 | 0.15509 | -0.022888 | -0.14648 | -0.1831 | 7.1182 | 7.0862 | 6.9077 | 0.050354 | 0.018311 | 122.58 | -0.21057 | -0.036621 | -122.6852 | 0.1236 | 7.2647 | -115.4526 | -0.064087 | 0.041199 | 0.16022 | 0.19684 | 0.16479 | 7.2327 | 0 | 0.1236 | 122.7264 | 7.0541 | -0.064087 | 0 | 0.1236 | 7.0541 | 7.2327 | 122.7264 | -122.7219 | -122.7493
1195.9688 | 122.8683 | -0.13275 | 122.5891 | 0.13733 | 0.0066224 | 0.017304 | 0.030335 | 0.055542 | 0.058533 | 0.15787 | -0.059509 | -0.13275 | -0.16022 | 7.7225 | 7.6859 | 7.5256 | 0.16937 | 0.068665 | 122.5983 | -0.21515 | -0.027466 | -122.7219 | 0.073242 | 7.8552 | -114.9033 | -0.082398 | 0.009156 | 0.10071 | 0.30212 | 0.20142 | 7.8186 | 0 | 0.073242 | 122.731 | 7.6584 | -0.082398 | 0 | 0.073242 | 7.6584 | 7.8186 | 122.731 | -122.7493 | -122.8043
1196.9688 | 122.85 | -0.15106 | 122.5616 | 0.11444 | 0.0074768 | 0.019867 | 0.033539 | 0.058746 | 0.057892 | 0.15274 | -0.045776 | -0.16022 | -0.1831 | 7.8506 | 7.8232 | 7.6447 | 0.21515 | 0.073242 | 122.5891 | -0.23346 | -0.032043 | -122.7219 | 0.10529 | 8.0017 | -114.7385 | -0.082397 | 0.027465 | 0.13733 | 0.36621 | 0.2243 | 7.9742 | -0.009155 | 0.10529 | 122.7402 | 7.7957 | -0.082397 | -0.009155 | 0.10529 | 7.7957 | 7.9742 | 122.7402 | -122.7448 | -122.7951
1198.0156 | 122.8317 | -0.13733 | 122.5571 | 0.35858 | 0.0089722 | 0.026062 | 0.035675 | 0.056183 | 0.059174 | 0.15594 | -0.041199 | -0.16937 | -0.18768 | 7.782 | 7.7499 | 7.608 | 0.3067 | 0.022888 | 122.6074 | -0.22888 | -0.050354 | -122.7264 | 0.09613 | 7.9193 | -114.8071 | -0.091553 | 0.050354 | 0.14648 | 0.44403 | 0.16022 | 7.8873 | -0.032044 | 0.09613 | 122.7448 | 7.7454 | -0.091553 | -0.032044 | 0.09613 | 7.7454 | 7.8873 | 122.7448 | -122.7448 | -122.7859
1198.9688 | 122.7676 | -0.21515 | 122.5845 | 0.038147 | 0.01004 | 0.024139 | 0.037598 | 0.058319 | 0.05661 | 0.15402 | -0.1236 | -0.11902 | -0.21515 | 7.814 | 7.7591 | 7.5668 | 0.33417 | -0.068665 | 122.6303 | -0.28839 | 0 | -122.7036 | 0.091553 | 8.0292 | -114.8254 | -0.073242 | 0.045776 | 0.091553 | 0.54932 | 0.14648 | 7.9742 | 0.09613 | 0.091553 | 122.8455 | 7.782 | -0.073242 | 0.09613 | 0.091553 | 7.782 | 7.9742 | 122.8455 | -122.7997 | -122.8729
1200.0156 | 122.8729 | -0.17395 | 122.5616 | 0.41199 | 0.0089722 | 0.01944 | 0.033966 | 0.057678 | 0.059174 | 0.15723 | -0.045776 | -0.17395 | -0.19226 | 7.2876 | 7.4203 | 7.3654 | 0.11444 | 0.004578 | 122.5113 | -0.28839 | -0.018311 | -122.7356 | 0.12817 | 7.4615 | -115.1413 | -0.11444 | -0.050354 | 0.14648 | 0.28839 | 0.17853 | 7.5943 | 0 | 0.12817 | 122.6852 | 7.5394 | -0.11444 | 0 | 0.12817 | 7.5394 | 7.5943 | 122.6852 | -122.7539 | -122.85
1200.9688 | 122.8043 | -0.16022 | 122.6028 | -0.022889 | 0.0081178 | 0.017731 | 0.032684 | 0.055328 | 0.057037 | 0.15552 | -0.07782 | -0.1236 | -0.17395 | 7.9056 | 7.8644 | 7.5394 | 0.21973 | 0.018311 | 122.612 | -0.25635 | -0.013733 | -122.7264 | 0.082397 | 8.0658 | -114.7385 | -0.096131 | 0.009156 | 0.09613 | 0.37994 | 0.17853 | 8.0246 | 0.036621 | 0.082397 | 122.7722 | 7.6996 | -0.096131 | 0.036621 | 0.082397 | 7.6996 | 8.0246 | 122.7722 | -122.7768 | -122.8592
1201.9688 | 122.8363 | -0.16022 | 122.5708 | 2.6245 | 0.0089722 | 0.026489 | 0.033325 | 0.055115 | 0.059601 | 0.15466 | -0.004578 | -0.16022 | -0.20142 | 8.2306 | 8.1985 | 8.0063 | 0.20142 | 0.07782 | 122.5845 | -0.21515 | -0.041199 | -122.731 | 0.15564 | 8.3908 | -114.3723 | -0.054932 | 0.013733 | 0.19684 | 0.36163 | 0.23804 | 8.3588 | 0 | 0.15564 | 122.7448 | 8.1665 | -0.054932 | 0 | 0.15564 | 8.1665 | 8.3588 | 122.7448 | -122.7722 | -122.7859
1202.9844 | 122.7585 | -0.1831 | 122.5754 | 0.18311 | 0.013886 | 0.024139 | 0.041229 | 0.060455 | 0.058105 | 0.15744 | -0.050354 | -0.091553 | -0.21057 | 7.5256 | 7.4615 | 7.3242 | 0.29755 | -0.059509 | 122.6212 | -0.28381 | -0.027466 | -122.6669 | 0.13275 | 7.7087 | -115.1138 | -0.10071 | 0.045777 | 0.16022 | 0.48065 | 0.1236 | 7.6447 | 0.091552 | 0.13275 | 122.8043 | 7.5073 | -0.10071 | 0.091552 | 0.13275 | 7.5073 | 7.6447 | 122.8043 | -122.7859 | -122.8592
1204.0156 | 122.8134 | -0.13733 | 122.5662 | 0.35858 | 0.0087586 | 0.019653 | 0.032257 | 0.056824 | 0.059814 | 0.15744 | -0.10071 | -0.1236 | -0.18768 | 7.7454 | 7.7316 | 7.5577 | 0.39825 | -0.009155 | 122.5983 | -0.23804 | -0.050354 | -122.6898 | 0.036621 | 7.8827 | -114.8346 | -0.10071 | 0.032044 | 0.086975 | 0.53558 | 0.12817 | 7.869 | 0.013733 | 0.036621 | 122.7356 | 7.695 | -0.10071 | 0.013733 | 0.036621 | 7.695 | 7.869 | 122.7356 | -122.7539 | -122.8043
1204.9688 | 122.7356 | -0.19226 | 122.5983 | -0.083923 | 0.009613 | 0.020081 | 0.034393 | 0.054901 | 0.05896 | 0.15488 | -0.12817 | -0.10986 | -0.23346 | 7.6584 | 7.6218 | 7.3975 | 0.41657 | -0.073242 | 122.644 | -0.27466 | -0.041198 | -122.7081 | 0.064087 | 7.8506 | -114.9765 | -0.082397 | 0.045776 | 0.10528 | 0.60883 | 0.11902 | 7.814 | 0.082398 | 0.064087 | 122.8363 | 7.5897 | -0.082397 | 0.082398 | 0.064087 | 7.5897 | 7.814 | 122.8363 | -122.8317 | -122.8729
1206.0156 | 122.8638 | -0.16479 | 122.4747 | 0.39673 | 0.0079042 | 0.023071 | 0.035034 | 0.057465 | 0.058319 | 0.15701 | -0.050354 | -0.15106 | -0.19226 | 7.9468 | 7.901 | 7.7683 | 0.43945 | 0.036621 | 122.5845 | -0.24261 | -0.027466 | -122.6257 | 0.11444 | 8.1116 | -114.5737 | -0.07782 | 0.10986 | 0.14191 | 0.60425 | 0.20142 | 8.0658 | 0.013733 | 0.11444 | 122.7493 | 7.933 | -0.07782 | 0.013733 | 0.11444 | 7.933 | 8.0658 | 122.7493 | -122.6669 | -122.7173
1206.9688 | 122.7951 | -0.17395 | 122.58 | 0.068664 | 0.0089722 | 0.023071 | 0.040161 | 0.058746 | 0.058746 | 0.1553 | -0.10529 | -0.11902 | -0.23346 | 8.107 | 8.0521 | 7.8644 | 0.76904 | -0.032043 | 122.6349 | -0.27466 | -0.059509 | -122.699 | 0.068664 | 8.2809 | -114.5279 | -0.10071 | 0.054932 | 0.12817 | 0.94299 | 0.14191 | 8.226 | 0.054931 | 0.068664 | 122.8088 | 8.0383 | -0.10071 | 0.054931 | 0.068664 | 8.0383 | 8.226 | 122.8088 | -122.8134 | -122.8546
1208.0312 | 122.8134 | -0.17853 | 122.58 | 0.10681 | 0.01239 | 0.02478 | 0.037811 | 0.057892 | 0.061523 | 0.1568 | -0.082397 | -0.12817 | -0.21515 | 7.5851 | 7.5348 | 7.338 | 0.16479 | -0.036621 | 122.6349 | -0.27008 | -0.036621 | -122.7081 | 0.096131 | 7.7637 | -115.0452 | -0.091553 | 0.054932 | 0.13275 | 0.34332 | 0.14191 | 7.7133 | 0.050354 | 0.096131 | 122.8134 | 7.5165 | -0.091553 | 0.050354 | 0.096131 | 7.5165 | 7.7133 | 122.8134 | -122.7951 | -122.85
1208.9688 | 122.7905 | -0.17395 | 122.5754 | 0.74768 | 0.011108 | 0.025208 | 0.03717 | 0.058533 | 0.05896 | 0.15616 | -0.018311 | -0.059509 | -0.1236 | 7.6584 | 7.6309 | 7.338 | 0.17395 | -0.027466 | 122.6349 | -0.22888 | 0.050354 | -122.6349 | 0.15564 | 7.8323 | -114.9445 | -0.054932 | 0.05951 | 0.10528 | 0.3479 | 0.14648 | 7.8049 | 0.11444 | 0.15564 | 122.8088 | 7.5119 | -0.054932 | 0.11444 | 0.15564 | 7.5119 | 7.8049 | 122.8088 | -122.699 | -122.8043
1210.0156 | 122.818 | -0.14648 | 122.5708 | 0.37384 | 0.0093994 | 0.023285 | 0.030121 | 0.056824 | 0.062164 | 0.15488 | -0.07782 | -0.13275 | -0.1831 | 8.7616 | 8.725 | 8.5144 | 0.11902 | 0 | 122.5845 | -0.21973 | -0.036621 | -122.7036 | 0.068664 | 8.9081 | -113.8458 | -0.073243 | 0.013733 | 0.10528 | 0.2655 | 0.14648 | 8.8715 | 0.013733 | 0.068664 | 122.731 | 8.6609 | -0.073243 | 0.013733 | 0.068664 | 8.6609 | 8.8715 | 122.731 | -122.7539 | -122.7905
1210.9688 | 122.8455 | -0.15564 | 122.5616 | 0.038147 | 0.0074768 | 0.020935 | 0.03183 | 0.056396 | 0.055969 | 0.15317 | -0.068665 | -0.13275 | -0.16022 | 9.6542 | 9.6359 | 9.3704 | 0.26093 | 0.054932 | 122.6166 | -0.23804 | -0.004577 | -122.6944 | 0.086975 | 9.8099 | -112.9257 | -0.082397 | 0.054931 | 0.091552 | 0.41657 | 0.21057 | 9.7916 | 0.022889 | 0.086975 | 122.7722 | 9.5261 | -0.082397 | 0.022889 | 0.086975 | 9.5261 | 9.7916 | 122.7722 | -122.7219 | -122.7997
1211.9688 | 122.7585 | -0.20142 | 122.5983 | 0.20599 | 0.01239 | 0.022003 | 0.038666 | 0.057465 | 0.056397 | 0.15167 | -0.086975 | -0.10986 | -0.21973 | 10.3363 | 10.2814 | 9.9197 | 0.30212 | -0.082397 | 122.6486 | -0.28381 | -0.018311 | -122.7081 | 0.11444 | 10.5377 | -112.3169 | -0.082397 | 0.050354 | 0.13275 | 0.50354 | 0.11902 | 10.4828 | 0.091553 | 0.11444 | 122.85 | 10.1212 | -0.082397 | 0.091553 | 0.11444 | 10.1212 | 10.4828 | 122.85 | -122.818 | -122.8821
1213.0312 | 122.7585 | -0.18768 | 122.58 | 0.25177 | 0.011963 | 0.024353 | 0.037598 | 0.05661 | 0.057251 | 0.15103 | -0.11444 | -0.10071 | -0.21057 | 12.4786 | 12.4054 | 12.2086 | 0.43945 | -0.10529 | 122.6166 | -0.30212 | -0.022888 | -122.6807 | 0.073242 | 12.6663 | -110.1746 | -0.11444 | 0.036621 | 0.09613 | 0.62714 | 0.082397 | 12.5931 | 0.086975 | 0.073242 | 122.8043 | 12.3962 | -0.11444 | 0.086975 | 0.073242 | 12.3962 | 12.5931 | 122.8043 | -122.7905 | -122.8821
1213.9688 | 122.7676 | -0.15564 | 122.6028 | -0.061036 | 0.0098268 | 0.01944 | 0.032471 | 0.054901 | 0.058533 | 0.15295 | -0.16479 | -0.082397 | -0.21973 | 12.0712 | 12.0621 | 11.6776 | 0.41657 | -0.045776 | 122.6669 | -0.23804 | -0.064087 | -122.6852 | -0.009155 | 12.2269 | -110.5408 | -0.082397 | 0.064087 | 0.054932 | 0.57221 | 0.10986 | 12.2177 | 0.073243 | -0.009155 | 122.8226 | 11.8332 | -0.082397 | 0.073243 | -0.009155 | 11.8332 | 12.2177 | 122.8226 | -122.8226 | -122.8409
1214.9688 | 122.7631 | -0.16022 | 122.6074 | -0.083923 | 0.0089722 | 0.019653 | 0.033753 | 0.053192 | 0.057678 | 0.1521 | -0.16937 | -0.10071 | -0.22888 | 11.1969 | 11.1557 | 10.9726 | 0.37079 | -0.10529 | 122.6761 | -0.24719 | -0.068665 | -122.7081 | -0.009156 | 11.3571 | -111.4517 | -0.086975 | 0.068664 | 0.059509 | 0.53101 | 0.054931 | 11.3159 | 0.059509 | -0.009156 | 122.8363 | 11.1328 | -0.086975 | 0.059509 | -0.009156 | 11.1328 | 11.3159 | 122.8363 | -122.8363 | -122.8546
1215.9688 | 122.7768 | -0.1831 | 122.58 | -0.015259 | 0.010681 | 0.023926 | 0.030335 | 0.055328 | 0.058105 | 0.15274 | -0.09613 | -0.13275 | -0.18768 | 9.137 | 9.1049 | 8.9676 | 0.30212 | -0.022888 | 122.6532 | -0.27008 | -0.004578 | -122.7127 | 0.086975 | 9.3201 | -113.475 | -0.086976 | 0.073242 | 0.091553 | 0.48523 | 0.16022 | 9.288 | 0.050354 | 0.086975 | 122.8363 | 9.1507 | -0.086976 | 0.050354 | 0.086975 | 9.1507 | 9.288 | 122.8363 | -122.7676 | -122.85
1216.9688 | 122.7722 | -0.1831 | 122.5937 | -0.038147 | 0.0091858 | 0.023285 | 0.030335 | 0.054901 | 0.060242 | 0.15317 | -0.086975 | -0.1236 | -0.19684 | 8.7708 | 8.7341 | 8.5373 | 0.28381 | -0.018311 | 122.6761 | -0.27924 | -0.013733 | -122.7173 | 0.09613 | 8.9539 | -113.8596 | -0.096131 | 0.082397 | 0.10986 | 0.46692 | 0.16479 | 8.9172 | 0.059509 | 0.09613 | 122.8592 | 8.7204 | -0.096131 | 0.059509 | 0.09613 | 8.7204 | 8.9172 | 122.8592 | -122.7905 | -122.8729
1217.9844 | 122.7448 | -0.20599 | 122.5983 | 0.30518 | 0.011108 | 0.02243 | 0.03717 | 0.056824 | 0.056824 | 0.15295 | -0.14648 | -0.10071 | -0.22888 | 10.0433 | 9.9884 | 9.7366 | 0.29755 | -0.1236 | 122.6624 | -0.29297 | -0.022888 | -122.699 | 0.05951 | 10.2493 | -112.6099 | -0.086975 | 0.064087 | 0.082398 | 0.50354 | 0.082398 | 10.1944 | 0.10529 | 0.05951 | 122.8683 | 9.9426 | -0.086975 | 0.10529 | 0.05951 | 9.9426 | 10.1944 | 122.8683 | -122.8271 | -122.8912
1218.9688 | 122.7676 | -0.21057 | 122.5983 | 0.061035 | 0.0089722 | 0.023285 | 0.036316 | 0.05661 | 0.058533 | 0.15317 | -0.15106 | -0.09613 | -0.23804 | 9.9518 | 9.9152 | 9.6863 | 0.36163 | -0.073242 | 122.6349 | -0.29755 | -0.027466 | -122.6944 | 0.059509 | 10.1624 | -112.6831 | -0.086975 | 0.036621 | 0.086975 | 0.5722 | 0.13733 | 10.1257 | 0.11444 | 0.059509 | 122.8455 | 9.8969 | -0.086975 | 0.11444 | 0.059509 | 9.8969 | 10.1257 | 122.8455 | -122.8363 | -122.8958
1219.9688 | 122.7539 | -0.19684 | 122.5937 | 0.28992 | 0.011108 | 0.021149 | 0.036316 | 0.057892 | 0.058746 | 0.15231 | -0.13275 | -0.10986 | -0.2243 | 9.8511 | 9.8007 | 9.6222 | 0.32501 | -0.10071 | 122.6212 | -0.30212 | -0.027466 | -122.7036 | 0.064087 | 10.0479 | -112.793 | -0.10529 | 0.027466 | 0.091553 | 0.52185 | 0.09613 | 9.9976 | 0.086975 | 0.064087 | 122.818 | 9.819 | -0.10529 | 0.086975 | 0.064087 | 9.819 | 9.9976 | 122.818 | -122.818 | -122.8958
1221.0156 | 122.8317 | -0.15564 | 122.5754 | 0.29755 | 0.0081178 | 0.026276 | 0.027557 | 0.055756 | 0.060242 | 0.15466 | -0.11444 | -0.12817 | -0.17853 | 9.8328 | 9.8145 | 9.613 | 0.33417 | -0.018311 | 122.5983 | -0.25177 | -0.022888 | -122.7036 | 0.041199 | 9.9884 | -112.7609 | -0.09613 | 0.022889 | 0.064087 | 0.48981 | 0.13733 | 9.9701 | 0.027466 | 0.041199 | 122.7539 | 9.7687 | -0.09613 | 0.027466 | 0.041199 | 9.7687 | 9.9701 | 122.7539 | -122.7539 | -122.8271
1221.9688 | 122.7036 | -0.17853 | 122.6669 | -0.022889 | 0.009613 | 0.021149 | 0.034607 | 0.054901 | 0.057678 | 0.1553 | -0.14648 | -0.091553 | -0.22888 | 9.6039 | 9.581 | 9.3246 | 0.41657 | -0.07782 | 122.7081 | -0.27008 | -0.050354 | -122.7585 | 0.032044 | 9.7824 | -113.0859 | -0.091553 | 0.041199 | 0.082398 | 0.59509 | 0.10071 | 9.7595 | 0.086975 | 0.032044 | 122.8867 | 9.5032 | -0.091553 | 0.086975 | 0.032044 | 9.5032 | 9.7595 | 122.8867 | -122.8958 | -122.937
1223.0312 | 122.7951 | -0.1236 | 122.6212 | 0.18311 | 0.011108 | 0.02478 | 0.036316 | 0.055542 | 0.060028 | 0.15295 | -0.086975 | -0.10986 | -0.20599 | 9.6771 | 9.5535 | 9.343 | 0.35706 | -0.004578 | 122.7127 | -0.20142 | -0.082398 | -122.731 | 0.036621 | 9.8007 | -113.0676 | -0.07782 | 0.091553 | 0.11902 | 0.48065 | 0.11902 | 9.6771 | 0.013733 | 0.036621 | 122.8363 | 9.4666 | -0.07782 | 0.013733 | 0.036621 | 9.4666 | 9.6771 | 122.8363 | -122.8271 | -122.8226
1223.9688 | 122.7356 | -0.22888 | 122.612 | 0.26703 | 0.0087586 | 0.027344 | 0.03418 | 0.058319 | 0.055756 | 0.15338 | -0.16022 | -0.10529 | -0.24719 | 9.6634 | 9.6085 | 9.3933 | 0.3891 | -0.12817 | 122.5983 | -0.29755 | -0.01831 | -122.7173 | 0.068665 | 9.8923 | -113.0035 | -0.068664 | -0.013733 | 0.086975 | 0.61798 | 0.10071 | 9.8373 | 0.1236 | 0.068665 | 122.8271 | 9.6222 | -0.068664 | 0.1236 | 0.068665 | 9.6222 | 9.8373 | 122.8271 | -122.8592 | -122.9095
1225.0156 | 122.8409 | -0.17395 | 122.58 | 0.29755 | 0.0098268 | 0.023712 | 0.028412 | 0.055969 | 0.060883 | 0.15295 | -0.10529 | -0.12817 | -0.17853 | 9.9335 | 9.9197 | 9.6909 | 0.35706 | -0.018311 | 122.6028 | -0.2655 | -0.004578 | -122.7081 | 0.068664 | 10.1074 | -112.6602 | -0.091553 | 0.022888 | 0.073242 | 0.53101 | 0.15564 | 10.0937 | 0.045776 | 0.068664 | 122.7768 | 9.8648 | -0.091553 | 0.045776 | 0.068664 | 9.8648 | 10.0937 | 122.7768 | -122.7585 | -122.8455
1225.9688 | 122.7631 | -0.1831 | 122.5845 | 0.022888 | 0.0098268 | 0.02179 | 0.035461 | 0.057037 | 0.058319 | 0.15381 | -0.15106 | -0.086975 | -0.23346 | 9.3063 | 9.2789 | 9.0408 | 0.55389 | -0.082397 | 122.6715 | -0.29297 | -0.050354 | -122.6715 | 0.032043 | 9.4894 | -113.3057 | -0.10986 | 0.086975 | 0.082397 | 0.737 | 0.10071 | 9.462 | 0.09613 | 0.032043 | 122.8546 | 9.2239 | -0.10986 | 0.09613 | 0.032043 | 9.2239 | 9.462 | 122.8546 | -122.818 | -122.8775
1227.0156 | 122.8271 | -0.16022 | 122.5754 | 0.28992 | 0.011108 | 0.021362 | 0.030975 | 0.056824 | 0.060455 | 0.15253 | -0.10529 | -0.13275 | -0.17853 | 9.462 | 9.4391 | 9.2011 | 0.59509 | -0.022888 | 122.6257 | -0.26093 | -0.018311 | -122.7081 | 0.054931 | 9.6222 | -113.1363 | -0.10071 | 0.050354 | 0.073242 | 0.75531 | 0.13733 | 9.5993 | 0.027466 | 0.054931 | 122.7859 | 9.3613 | -0.10071 | 0.027466 | 0.054931 | 9.3613 | 9.5993 | 122.7859 | -122.7539 | -122.8363
1227.9688 | 122.7493 | -0.20599 | 122.5983 | 0.25177 | 0.011749 | 0.020294 | 0.037598 | 0.05661 | 0.056397 | 0.15424 | -0.12817 | -0.11444 | -0.22888 | 9.5627 | 9.494 | 9.3063 | 0.75073 | -0.12817 | 122.6486 | -0.3067 | -0.022888 | -122.7127 | 0.07782 | 9.7687 | -113.1042 | -0.10071 | 0.050354 | 0.10071 | 0.95673 | 0.07782 | 9.7 | 0.091553 | 0.07782 | 122.8546 | 9.5123 | -0.10071 | 0.091553 | 0.07782 | 9.5123 | 9.7 | 122.8546 | -122.8271 | -122.905
1229.0156 | 122.8271 | -0.17395 | 122.5891 | 0.40436 | 0.0091858 | 0.022644 | 0.027985 | 0.054687 | 0.060883 | 0.15381 | -0.14191 | -0.14648 | -0.21515 | 8.8898 | 8.8715 | 8.6655 | 0.091553 | -0.004578 | 122.612 | -0.27008 | -0.041199 | -122.7356 | 0.032043 | 9.0637 | -113.7177 | -0.096131 | 0.022889 | 0.073242 | 0.2655 | 0.16937 | 9.0454 | 0.027466 | 0.032043 | 122.7859 | 8.8394 | -0.096131 | 0.027466 | 0.032043 | 8.8394 | 9.0454 | 122.7859 | -122.8043 | -122.8592
1229.9688 | 122.7905 | -0.18768 | 122.58 | 0.038147 | 0.010895 | 0.023285 | 0.038239 | 0.05896 | 0.057465 | 0.15317 | -0.10071 | -0.10071 | -0.23804 | 8.8303 | 8.7524 | 8.5281 | 0.14191 | -0.036621 | 122.6532 | -0.28839 | -0.050354 | -122.6807 | 0.086975 | 9.0179 | -113.8275 | -0.10071 | 0.073242 | 0.13733 | 0.32959 | 0.15106 | 8.9401 | 0.086975 | 0.086975 | 122.8409 | 8.7158 | -0.10071 | 0.086975 | 0.086975 | 8.7158 | 8.9401 | 122.8409 | -122.818 | -122.8683
1231.0156 | 122.8271 | -0.16479 | 122.5662 | 0.2594 | 0.0089722 | 0.023712 | 0.030335 | 0.054901 | 0.060242 | 0.15594 | -0.11444 | -0.13275 | -0.17853 | 8.6517 | 8.6243 | 8.4412 | 0.064087 | -0.018311 | 122.6486 | -0.25635 | -0.013733 | -122.699 | 0.050354 | 8.8165 | -113.942 | -0.091553 | 0.082398 | 0.064087 | 0.22888 | 0.14648 | 8.7891 | 0.032044 | 0.050354 | 122.8134 | 8.606 | -0.091553 | 0.032044 | 0.050354 | 8.606 | 8.7891 | 122.8134 | -122.7448 | -122.8226
1231.9688 | 122.7905 | -0.19226 | 122.6166 | 0.23651 | 0.0093994 | 0.025208 | 0.038239 | 0.056824 | 0.059601 | 0.15317 | -0.036621 | -0.036621 | -0.13275 | 8.6838 | 8.6151 | 8.3588 | 0.13275 | -0.032043 | 122.6486 | -0.27924 | 0.05951 | -122.6532 | 0.15564 | 8.876 | -114.0015 | -0.086975 | 0.032044 | 0.09613 | 0.32501 | 0.16022 | 8.8074 | 0.15564 | 0.15564 | 122.8409 | 8.551 | -0.086975 | 0.15564 | 0.15564 | 8.551 | 8.8074 | 122.8409 | -122.7493 | -122.8958
1233.0156 | 122.8226 | -0.15564 | 122.5754 | 0.37384 | 0.012604 | 0.022858 | 0.03183 | 0.057465 | 0.059174 | 0.15659 | -0.07782 | -0.13275 | -0.18768 | 8.6655 | 8.6288 | 8.4961 | 0.059509 | 0 | 122.6212 | -0.23804 | -0.032043 | -122.7081 | 0.07782 | 8.8211 | -113.9465 | -0.082397 | 0.045777 | 0.10986 | 0.21515 | 0.15564 | 8.7845 | 0.022889 | 0.07782 | 122.7768 | 8.6517 | -0.082397 | 0.022889 | 0.07782 | 8.6517 | 8.7845 | 122.7768 | -122.7631 | -122.8134
1233.9688 | 122.7676 | -0.20142 | 122.5891 | 0.20599 | 0.010895 | 0.023071 | 0.037811 | 0.057465 | 0.060028 | 0.15445 | -0.15106 | -0.09613 | -0.2243 | 8.5922 | 8.5327 | 8.4274 | 0.20142 | -0.12817 | 122.644 | -0.29297 | -0.022888 | -122.6852 | 0.050354 | 8.7936 | -114.0564 | -0.091553 | 0.054932 | 0.073242 | 0.40283 | 0.073242 | 8.7341 | 0.10529 | 0.050354 | 122.8455 | 8.6288 | -0.091553 | 0.10529 | 0.050354 | 8.6288 | 8.7341 | 122.8455 | -122.8134 | -122.8821
1235.0156 | 122.8821 | -0.15106 | 122.5708 | 0.20599 | 0.010895 | 0.021362 | 0.028839 | 0.055115 | 0.060669 | 0.15659 | -0.1236 | -0.14191 | -0.17853 | 8.7616 | 8.7524 | 8.6151 | 0.19684 | 0.032043 | 122.5983 | -0.26093 | -0.027466 | -122.7127 | 0.027466 | 8.9127 | -113.8184 | -0.10986 | 0.027466 | 0.054932 | 0.3479 | 0.18311 | 8.9035 | 0.009155 | 0.027466 | 122.7493 | 8.7662 | -0.10986 | 0.009155 | 0.027466 | 8.7662 | 8.9035 | 122.7493 | -122.7493 | -122.8317
1235.9688 | 122.8226 | -0.1831 | 122.58 | 0.16022 | 0.0098268 | 0.025421 | 0.038452 | 0.057892 | 0.060455 | 0.15167 | -0.073242 | -0.09613 | -0.21057 | 8.8669 | 8.7799 | 8.638 | 0.37537 | -0.054932 | 122.6486 | -0.28381 | -0.027466 | -122.6761 | 0.10986 | 9.05 | -113.8 | -0.10071 | 0.068665 | 0.13733 | 0.55847 | 0.12817 | 8.963 | 0.086975 | 0.10986 | 122.8317 | 8.8211 | -0.10071 | 0.086975 | 0.10986 | 8.8211 | 8.963 | 122.8317 | -122.7905 | -122.8638
1237.0156 | 122.9004 | -0.14191 | 122.5616 | 0.12207 | 0.008545 | 0.022644 | 0.028626 | 0.054687 | 0.059601 | 0.15402 | -0.054932 | -0.12817 | -0.16937 | 8.7753 | 8.7662 | 8.5693 | 0.068665 | 0.07782 | 122.6074 | -0.27008 | -0.027466 | -122.6898 | 0.086975 | 8.9172 | -113.7955 | -0.12817 | 0.045776 | 0.11444 | 0.21057 | 0.21973 | 8.9081 | 0.013733 | 0.086975 | 122.7493 | 8.7112 | -0.12817 | 0.013733 | 0.086975 | 8.7112 | 8.9081 | 122.7493 | -122.731 | -122.8317
1237.9688 | 122.85 | -0.17395 | 122.5479 | 0.40436 | 0.013886 | 0.020081 | 0.035248 | 0.057037 | 0.058319 | 0.15253 | -0.10071 | -0.13275 | -0.23804 | 8.7616 | 8.7067 | 8.5281 | 0.10529 | -0.041199 | 122.6486 | -0.28381 | -0.064087 | -122.6807 | 0.073242 | 8.9355 | -113.8412 | -0.10986 | 0.10071 | 0.13733 | 0.27924 | 0.13275 | 8.8806 | 0.041199 | 0.073242 | 122.8226 | 8.7021 | -0.10986 | 0.041199 | 0.073242 | 8.7021 | 8.8806 | 122.8226 | -122.7859 | -122.8317
1239.0156 | 122.818 | -0.16479 | 122.5891 | -0.083923 | 0.008545 | 0.024353 | 0.030975 | 0.05661 | 0.05661 | 0.1521 | -0.086975 | -0.12817 | -0.19226 | 8.8486 | 8.7982 | 8.5785 | 0.26093 | 0.004578 | 122.644 | -0.27466 | -0.027466 | -122.7173 | 0.07782 | 9.0134 | -113.7909 | -0.10986 | 0.054932 | 0.10529 | 0.42572 | 0.16937 | 8.963 | 0.036621 | 0.07782 | 122.8088 | 8.7433 | -0.10986 | 0.036621 | 0.07782 | 8.7433 | 8.963 | 122.8088 | -122.7814 | -122.8638
1239.9688 | 122.7814 | -0.20142 | 122.5571 | 0.16785 | 0.013031 | 0.025635 | 0.035248 | 0.057892 | 0.057465 | 0.15338 | -0.09613 | -0.10986 | -0.21973 | 8.8898 | 8.844 | 8.5739 | 0.24719 | -0.086975 | 122.6532 | -0.29755 | -0.018311 | -122.6669 | 0.10529 | 9.0912 | -113.7131 | -0.09613 | 0.09613 | 0.1236 | 0.44861 | 0.11444 | 9.0454 | 0.091553 | 0.10529 | 122.8546 | 8.7753 | -0.09613 | 0.091553 | 0.10529 | 8.7753 | 9.0454 | 122.8546 | -122.7768 | -122.8546
1240.9688 | 122.8729 | -0.15106 | 122.5754 | 0.41199 | 0.011536 | 0.021362 | 0.034821 | 0.059174 | 0.059814 | 0.15424 | -0.086975 | -0.13733 | -0.20599 | 9.0912 | 9.0591 | 8.8623 | 0.21973 | -0.009155 | 122.6212 | -0.27008 | -0.054932 | -122.7127 | 0.064087 | 9.2422 | -113.5162 | -0.11902 | 0.045777 | 0.11902 | 0.37079 | 0.14191 | 9.2102 | 0.013733 | 0.064087 | 122.7722 | 9.0134 | -0.11902 | 0.013733 | 0.064087 | 9.0134 | 9.2102 | 122.7722 | -122.7814 | -122.8455
1242.0156 | 122.9416 | -0.16479 | 122.5388 | 0.083923 | 0.0087586 | 0.021362 | 0.028412 | 0.054901 | 0.057678 | 0.15317 | -0.045776 | -0.13733 | -0.16937 | 9.4803 | 9.4391 | 9.2194 | 0.1831 | 0.082397 | 122.6074 | -0.2655 | -0.004578 | -122.6761 | 0.11902 | 9.6451 | -113.0997 | -0.10071 | 0.068665 | 0.1236 | 0.3479 | 0.24719 | 9.6039 | 0.027466 | 0.11902 | 122.7722 | 9.3842 | -0.10071 | 0.027466 | 0.11902 | 9.3842 | 9.6039 | 122.7722 | -122.7081 | -122.8043
1242.9688 | 122.8729 | -0.15564 | 122.5754 | 0.33569 | 0.010254 | 0.023285 | 0.036743 | 0.05896 | 0.061737 | 0.15402 | -0.045776 | -0.14191 | -0.19226 | 9.4437 | 9.4025 | 9.1965 | 0.3067 | 0 | 122.6028 | -0.2655 | -0.036621 | -122.7173 | 0.10986 | 9.5993 | -113.1729 | -0.10986 | 0.027466 | 0.14648 | 0.46234 | 0.15564 | 9.5581 | 0.013733 | 0.10986 | 122.7585 | 9.3521 | -0.10986 | 0.013733 | 0.10986 | 9.3521 | 9.5581 | 122.7585 | -122.7676 | -122.8409
1244.0156 | 122.7493 | -0.18768 | 122.6166 | -0.030518 | 0.011536 | 0.02243 | 0.037598 | 0.055542 | 0.061096 | 0.15317 | -0.19684 | -0.086975 | -0.21973 | 9.4254 | 9.3842 | 9.1736 | 0.36163 | -0.09613 | 122.6807 | -0.28381 | -0.032044 | -122.7036 | -0.009155 | 9.613 | -113.2324 | -0.09613 | 0.064087 | 0.022889 | 0.54932 | 0.091553 | 9.5718 | 0.10071 | -0.009155 | 122.8683 | 9.3613 | -0.09613 | 0.10071 | -0.009155 | 9.3613 | 9.5718 | 122.8683 | -122.8363 | -122.9004
1244.9688 | 122.7539 | -0.21057 | 122.5891 | 0.24414 | 0.011108 | 0.025208 | 0.038666 | 0.052978 | 0.055115 | 0.1459 | -0.13275 | -0.09613 | -0.22888 | 16.983 | 16.8961 | 16.6763 | 8.7662 | -0.11902 | 122.6395 | -0.32501 | -0.018311 | -122.6852 | 0.07782 | 17.1936 | -105.6931 | -0.11444 | 0.050354 | 0.096131 | 8.9767 | 0.091552 | 17.1066 | 0.11444 | 0.07782 | 122.85 | 16.8869 | -0.11444 | 0.11444 | 0.07782 | 16.8869 | 17.1066 | 122.85 | -122.818 | -122.9141
1246.0156 | 122.7722 | -0.18768 | 122.6074 | 0.27466 | 0.010254 | 0.025208 | 0.032898 | 0.055328 | 0.059814 | 0.15488 | -0.1236 | -0.059509 | -0.17395 | 8.6975 | 8.67 | 8.3817 | 0.25635 | -0.086975 | 122.6715 | -0.28839 | 0.013733 | -122.6669 | 0.064087 | 8.8852 | -113.9374 | -0.10071 | 0.064087 | 0.050354 | 0.44403 | 0.10071 | 8.8577 | 0.12817 | 0.064087 | 122.8592 | 8.5693 | -0.10071 | 0.12817 | 0.064087 | 8.5693 | 8.8577 | 122.8592 | -122.7814 | -122.8958
1246.9688 | 122.7814 | -0.16937 | 122.6028 | 0.29755 | 0.01239 | 0.023071 | 0.034607 | 0.058533 | 0.05896 | 0.15637 | -0.1831 | -0.086975 | -0.24719 | 8.67 | 8.6472 | 8.3588 | -0.10529 | -0.21515 | 122.6578 | -0.28381 | -0.077819 | -122.6898 | -0.013732 | 8.8394 | -113.9557 | -0.11444 | 0.054932 | 0.064087 | 0.064087 | -0.045776 | 8.8165 | 0.082398 | -0.013732 | 122.8271 | 8.5281 | -0.11444 | 0.082398 | -0.013732 | 8.5281 | 8.8165 | 122.8271 | -122.85 | -122.8867
1248.0156 | 122.818 | -0.15564 | 122.6074 | -0.0076295 | 0.008545 | 0.022644 | 0.029907 | 0.055756 | 0.060028 | 0.15317 | -0.073242 | -0.1236 | -0.1831 | 8.6792 | 8.6472 | 8.3862 | 0.13733 | 0.018311 | 122.6212 | -0.28381 | -0.027465 | -122.731 | 0.082398 | 8.8348 | -113.9603 | -0.12817 | 0.013733 | 0.10986 | 0.29297 | 0.17395 | 8.8028 | 0.032044 | 0.082398 | 122.7768 | 8.5419 | -0.12817 | 0.032044 | 0.082398 | 8.5419 | 8.8028 | 122.7768 | -122.7905 | -122.8912
1248.9688 | 122.8409 | -0.15564 | 122.5983 | 0.35095 | 0.011963 | 0.01944 | 0.02948 | 0.055756 | 0.058105 | 0.15594 | -0.09613 | -0.1236 | -0.16937 | 8.5602 | 8.5327 | 8.4091 | 0.082397 | -0.022888 | 122.6166 | -0.25635 | -0.013733 | -122.7219 | 0.05951 | 8.7158 | -114.0656 | -0.10071 | 0.01831 | 0.073243 | 0.23804 | 0.13275 | 8.6884 | 0.032044 | 0.05951 | 122.7722 | 8.5648 | -0.10071 | 0.032044 | 0.05951 | 8.5648 | 8.6884 | 122.7722 | -122.7676 | -122.8546
1250.0156 | 122.8043 | -0.21057 | 122.6074 | 0 | 0.010681 | 0.02243 | 0.035461 | 0.056396 | 0.059601 | 0.15253 | -0.12817 | -0.09613 | -0.21973 | 8.4686 | 8.4183 | 8.1573 | 0.18768 | -0.041199 | 122.6257 | -0.28839 | -0.009156 | -122.7036 | 0.082397 | 8.6792 | -114.1891 | -0.07782 | 0.01831 | 0.091553 | 0.39825 | 0.16937 | 8.6288 | 0.11444 | 0.082397 | 122.8363 | 8.3679 | -0.07782 | 0.11444 | 0.082397 | 8.3679 | 8.6288 | 122.8363 | -122.8271 | -122.8958
1250.9688 | 122.7631 | -0.20599 | 122.6074 | 0.34332 | 0.014526 | 0.026062 | 0.033112 | 0.057037 | 0.058746 | 0.15573 | -0.21973 | -0.10529 | -0.19226 | 8.4091 | 8.4045 | 8.1207 | 0.21973 | -0.13275 | 122.644 | -0.29755 | 0.013733 | -122.7127 | -0.013733 | 8.6151 | -114.2029 | -0.091552 | 0.036621 | -0.027466 | 0.42572 | 0.073243 | 8.6105 | 0.10071 | -0.013733 | 122.85 | 8.3267 | -0.091552 | 0.10071 | -0.013733 | 8.3267 | 8.6105 | 122.85 | -122.7997 | -122.905
1252.0156 | 122.6898 | -0.17853 | 122.6807 | -0.0076295 | 0.009613 | 0.02179 | 0.032471 | 0.055328 | 0.06131 | 0.15466 | -0.16479 | -0.09613 | -0.22888 | 8.4183 | 8.3954 | 8.1619 | 0.31586 | 0.054932 | 122.6669 | -0.28839 | -0.050354 | -122.7768 | 0.013733 | 8.5968 | -114.2853 | -0.10986 | -0.013733 | 0.064087 | 0.49438 | 0.23346 | 8.5739 | 0.082398 | 0.013733 | 122.8455 | 8.3405 | -0.10986 | 0.082398 | 0.013733 | 8.3405 | 8.5739 | 122.8455 | -122.9095 | -122.9691
1252.9688 | 122.8912 | -0.15106 | 122.5616 | 0.36621 | 0.011749 | 0.026917 | 0.034607 | 0.05896 | 0.061737 | 0.15445 | -0.064087 | -0.15564 | -0.19684 | 8.4732 | 8.4503 | 8.2947 | 0.10071 | 0.018311 | 122.6166 | -0.26093 | -0.045776 | -122.7173 | 0.086975 | 8.6243 | -114.1113 | -0.10986 | 0.054931 | 0.13275 | 0.25177 | 0.16937 | 8.6014 | -0.004578 | 0.086975 | 122.7676 | 8.4457 | -0.10986 | -0.004578 | 0.086975 | 8.4457 | 8.6014 | 122.7676 | -122.7585 | -122.8226
1254.0156 | 122.8043 | -0.18768 | 122.6212 | 0.061035 | 0.011108 | 0.023285 | 0.034607 | 0.057465 | 0.059601 | 0.15509 | -0.10986 | -0.12817 | -0.22888 | 8.4366 | 8.3817 | 8.1619 | 0.27466 | -0.036621 | 122.6715 | -0.29755 | -0.041199 | -122.7493 | 0.07782 | 8.6243 | -114.2395 | -0.10986 | 0.050354 | 0.11902 | 0.46234 | 0.15106 | 8.5693 | 0.059509 | 0.07782 | 122.8592 | 8.3496 | -0.10986 | 0.059509 | 0.07782 | 8.3496 | 8.5693 | 122.8592 | -122.85 | -122.9187
1254.9688 | 122.8729 | -0.16022 | 122.5891 | 0.24414 | 0.0091858 | 0.023285 | 0.028626 | 0.05426 | 0.060669 | 0.15445 | -0.14191 | -0.15106 | -0.20599 | 8.3954 | 8.3771 | 8.1894 | 0.23804 | -0.004578 | 122.612 | -0.27008 | -0.045777 | -122.7402 | 0.01831 | 8.5556 | -114.212 | -0.10986 | 0.022889 | 0.064087 | 0.39825 | 0.15564 | 8.5373 | 0.009155 | 0.01831 | 122.7722 | 8.3496 | -0.10986 | 0.009155 | 0.01831 | 8.3496 | 8.5373 | 122.7722 | -122.7951 | -122.8592
1256.0156 | 122.8043 | -0.19226 | 122.6212 | 0.061035 | 0.011108 | 0.02478 | 0.035675 | 0.055756 | 0.057037 | 0.15381 | -0.10071 | -0.10071 | -0.22888 | 8.4961 | 8.4457 | 8.1757 | 0.39368 | -0.036621 | 122.6624 | -0.29755 | -0.036621 | -122.7219 | 0.091553 | 8.6884 | -114.1754 | -0.10528 | 0.041199 | 0.12817 | 0.58594 | 0.15564 | 8.638 | 0.091553 | 0.091553 | 122.8546 | 8.3679 | -0.10528 | 0.091553 | 0.091553 | 8.3679 | 8.638 | 122.8546 | -122.85 | -122.9187
1256.9688 | 122.8958 | -0.19226 | 122.5571 | 0.43488 | 0.010468 | 0.023926 | 0.034393 | 0.056183 | 0.060242 | 0.15445 | -0.045776 | -0.15106 | -0.20599 | 8.3679 | 8.5556 | 8.4183 | 0.24719 | 0.018311 | 122.612 | -0.29755 | -0.013733 | -122.7081 | 0.14648 | 8.5602 | -114.0015 | -0.10528 | 0.054932 | 0.16022 | 0.43945 | 0.21057 | 8.7479 | 0.041199 | 0.14648 | 122.8043 | 8.6105 | -0.10528 | 0.041199 | 0.14648 | 8.6105 | 8.7479 | 122.8043 | -122.7631 | -122.8546
1258.0156 | 122.818 | -0.21057 | 122.6166 | 0.053405 | 0.011322 | 0.025848 | 0.035461 | 0.057678 | 0.05896 | 0.15445 | -0.13733 | -0.10986 | -0.23346 | 8.5373 | 8.4915 | 8.3588 | 0.58594 | -0.068665 | 122.644 | -0.29755 | -0.022888 | -122.7264 | 0.073242 | 8.7479 | -114.1251 | -0.086975 | 0.027466 | 0.09613 | 0.79651 | 0.14191 | 8.7021 | 0.10071 | 0.073242 | 122.8546 | 8.5693 | -0.086975 | 0.10071 | 0.073242 | 8.5693 | 8.7021 | 122.8546 | -122.85 | -122.9141
1258.9688 | 122.905 | -0.14191 | 122.5891 | 0.42725 | 0.0087586 | 0.022858 | 0.032044 | 0.051269 | 0.055969 | 0.14996 | 0.013733 | -0.20142 | -0.23804 | 14.1037 | 13.9481 | 13.7604 | 6.1203 | 0.022888 | 122.5845 | -0.25635 | -0.09613 | -122.7905 | 0.15564 | 14.2456 | -108.6411 | -0.11444 | -0.004577 | 0.25177 | 6.2622 | 0.16479 | 14.09 | -0.059509 | 0.15564 | 122.7264 | 13.9023 | -0.11444 | -0.059509 | 0.15564 | 13.9023 | 14.09 | 122.7264 | -122.8271 | -122.8455
1260.0156 | 122.8317 | -0.11444 | 122.6395 | 0.14496 | 0.010681 | 0.02243 | 0.033753 | 0.05661 | 0.06131 | 0.15659 | -0.10071 | -0.11902 | -0.2243 | 8.4274 | 8.3176 | 8.075 | 0.32959 | -0.009155 | 122.7173 | -0.20599 | -0.10986 | -122.7585 | 0.013733 | 8.5419 | -114.3219 | -0.091553 | 0.07782 | 0.1236 | 0.44403 | 0.10529 | 8.432 | -0.004578 | 0.013733 | 122.8317 | 8.1894 | -0.091553 | -0.004578 | 0.013733 | 8.1894 | 8.432 | 122.8317 | -122.8638 | -122.8455
1260.9688 | 122.9004 | -0.13733 | 122.5983 | 0.14496 | 0.0072632 | 0.020508 | 0.026917 | 0.055969 | 0.060242 | 0.15637 | -0.091553 | -0.14191 | -0.16937 | 8.194 | 8.194 | 7.9559 | 0.14191 | 0.050354 | 122.6486 | -0.25177 | -0.032044 | -122.7402 | 0.045776 | 8.3313 | -114.4043 | -0.11444 | 0.050354 | 0.07782 | 0.27924 | 0.18768 | 8.3313 | -0.004578 | 0.045776 | 122.7859 | 8.0933 | -0.11444 | -0.004578 | 0.045776 | 8.0933 | 8.3313 | 122.7859 | -122.7676 | -122.85
1262.0156 | 122.7997 | -0.18768 | 122.6028 | 0.1297 | 0.011108 | 0.02179 | 0.036316 | 0.058319 | 0.055756 | 0.15338 | -0.11902 | -0.12817 | -0.23804 | 8.2443 | 8.1848 | 7.988 | 0.25177 | -0.036621 | 122.6852 | -0.27466 | -0.050354 | -122.731 | 0.068664 | 8.432 | -114.418 | -0.086975 | 0.082398 | 0.11902 | 0.43945 | 0.15106 | 8.3725 | 0.059509 | 0.068664 | 122.8729 | 8.1757 | -0.086975 | 0.059509 | 0.068664 | 8.1757 | 8.3725 | 122.8729 | -122.8409 | -122.8775
1262.9688 | 122.85 | -0.14648 | 122.6212 | 0.3891 | 0.0098268 | 0.024139 | 0.029694 | 0.054687 | 0.058319 | 0.1553 | -0.10071 | -0.13275 | -0.17853 | 8.2077 | 8.1619 | 7.9788 | 0.16022 | -0.004578 | 122.6074 | -0.2655 | -0.032044 | -122.7539 | 0.045776 | 8.3542 | -114.4592 | -0.11902 | -0.013733 | 0.07782 | 0.3067 | 0.14191 | 8.3084 | 0.013733 | 0.045776 | 122.7539 | 8.1253 | -0.11902 | 0.013733 | 0.045776 | 8.1253 | 8.3084 | 122.7539 | -122.7997 | -122.8867
1263.9688 | 122.8317 | -0.15564 | 122.5983 | 0.34332 | 0.010468 | 0.018158 | 0.030335 | 0.053192 | 0.057892 | 0.15659 | -0.09613 | -0.13733 | -0.17853 | 8.2123 | 8.1665 | 8.075 | 0.20599 | -0.013733 | 122.6212 | -0.25177 | -0.022888 | -122.7356 | 0.05951 | 8.3679 | -114.4318 | -0.09613 | 0.022888 | 0.082398 | 0.36163 | 0.14191 | 8.3221 | 0.018311 | 0.05951 | 122.7768 | 8.2306 | -0.09613 | 0.018311 | 0.05951 | 8.2306 | 8.3221 | 122.7768 | -122.7768 | -122.85
1265.0156 | 122.7585 | -0.21057 | 122.6212 | 0.32043 | 0.010895 | 0.023285 | 0.038879 | 0.057465 | 0.057251 | 0.15594 | -0.16022 | -0.13275 | -0.23804 | 8.1528 | 8.075 | 7.8003 | 0.31128 | -0.11902 | 122.6578 | -0.28839 | -0.027466 | -122.7539 | 0.050354 | 8.3633 | -114.5462 | -0.07782 | 0.036621 | 0.07782 | 0.52185 | 0.091552 | 8.2855 | 0.07782 | 0.050354 | 122.8683 | 8.0109 | -0.07782 | 0.07782 | 0.050354 | 8.0109 | 8.2855 | 122.8683 | -122.8592 | -122.9095
1265.9688 | 122.8455 | -0.17853 | 122.6166 | 0.29755 | 0.0087586 | 0.022217 | 0.028626 | 0.055969 | 0.061737 | 0.15594 | -0.11444 | -0.14191 | -0.20142 | 8.2169 | 8.1848 | 7.9376 | 0.27008 | -0.036621 | 122.6074 | -0.26093 | -0.022888 | -122.7585 | 0.064087 | 8.3954 | -114.4318 | -0.082397 | -0.009155 | 0.086975 | 0.44861 | 0.14191 | 8.3633 | 0.036621 | 0.064087 | 122.7859 | 8.1161 | -0.082397 | 0.036621 | 0.064087 | 8.1161 | 8.3633 | 122.7859 | -122.818 | -122.8775
1267.0156 | 122.7905 | -0.19684 | 122.5937 | 0.20599 | 0.0091858 | 0.019867 | 0.038452 | 0.054474 | 0.058319 | 0.15573 | -0.11902 | -0.11902 | -0.22888 | 8.2077 | 8.1345 | 7.8735 | 0.34332 | -0.07782 | 122.6624 | -0.27466 | -0.032044 | -122.7127 | 0.077819 | 8.4045 | -114.4592 | -0.07782 | 0.068665 | 0.10986 | 0.54016 | 0.11902 | 8.3313 | 0.077819 | 0.077819 | 122.8592 | 8.0704 | -0.07782 | 0.077819 | 0.077819 | 8.0704 | 8.3313 | 122.8592 | -122.8226 | -122.8683
1267.9688 | 122.9004 | -0.16022 | 122.6074 | 0.43488 | 0.008545 | 0.021149 | 0.02948 | 0.054901 | 0.059387 | 0.15552 | -0.07782 | -0.15564 | -0.19684 | 8.3725 | 8.345 | 8.0978 | 0.37079 | 0.068665 | 122.6028 | -0.25177 | -0.036621 | -122.7631 | 0.082397 | 8.5327 | -114.2624 | -0.091553 | -0.004578 | 0.11902 | 0.53101 | 0.22888 | 8.5052 | 0.004577 | 0.082397 | 122.7631 | 8.2581 | -0.091553 | 0.004577 | 0.082397 | 8.2581 | 8.5052 | 122.7631 | -122.8043 | -122.8592
1269.0156 | 122.8409 | -0.10529 | 122.6624 | 0.17548 | 0.012177 | 0.022858 | 0.03653 | 0.055542 | 0.057251 | 0.15445 | -0.10986 | -0.13733 | -0.21973 | 8.3038 | 8.2397 | 8.2489 | 0.63171 | 0.15106 | 122.7905 | -0.23346 | -0.11444 | -122.7997 | -0.004577 | 8.4091 | -114.4226 | -0.12817 | 0.12817 | 0.10986 | 0.737 | 0.25635 | 8.345 | -0.032043 | -0.004577 | 122.8958 | 8.3542 | -0.12817 | -0.032043 | -0.004577 | 8.3542 | 8.345 | 122.8958 | -122.8821 | -122.8958
1269.9688 | 122.8546 | -0.16937 | 122.58 | 0.23651 | 0.0081178 | 0.016876 | 0.028626 | 0.053192 | 0.06131 | 0.15445 | -0.14648 | -0.17853 | -0.21057 | 8.4091 | 8.3817 | 8.194 | 0.47607 | 0.004578 | 122.6349 | -0.25177 | -0.041198 | -122.7585 | 0.022889 | 8.5785 | -114.1983 | -0.082397 | 0.054932 | 0.064087 | 0.64545 | 0.17395 | 8.551 | -0.009155 | 0.022889 | 122.8043 | 8.3633 | -0.082397 | -0.009155 | 0.022889 | 8.3633 | 8.551 | 122.8043 | -122.7905 | -122.8317
1271.0156 | 122.7493 | -0.21057 | 122.6395 | 0.22125 | 0.010681 | 0.02713 | 0.03717 | 0.055756 | 0.057037 | 0.15402 | -0.17395 | -0.14191 | -0.2243 | 8.2764 | 8.2214 | 7.9697 | 0.54932 | -0.13733 | 122.6486 | -0.29755 | -0.013733 | -122.7814 | 0.036621 | 8.4869 | -114.418 | -0.086975 | 0.009156 | 0.050354 | 0.75989 | 0.073242 | 8.432 | 0.068664 | 0.036621 | 122.8592 | 8.1802 | -0.086975 | 0.068664 | 0.036621 | 8.1802 | 8.432 | 122.8592 | -122.8638 | -122.937
1271.9688 | 122.8638 | -0.16022 | 122.5891 | 0.32043 | 0.009613 | 0.017731 | 0.028412 | 0.054687 | 0.060028 | 0.15445 | -0.12817 | -0.13733 | -0.18768 | 8.4229 | 8.4091 | 8.1802 | 0.53101 | -0.022888 | 122.6303 | -0.26093 | -0.027466 | -122.7264 | 0.032043 | 8.5831 | -114.18 | -0.10071 | 0.041199 | 0.059509 | 0.69122 | 0.13733 | 8.5693 | 0.022888 | 0.032043 | 122.7905 | 8.3405 | -0.10071 | 0.022888 | 0.032043 | 8.3405 | 8.5693 | 122.7905 | -122.7768 | -122.85
1273.0156 | 122.7585 | -0.1831 | 122.6532 | 0.35858 | 0.009613 | 0.01944 | 0.03653 | 0.061523 | 0.05896 | 0.15295 | -0.16022 | -0.11444 | -0.21973 | 8.5236 | 8.3221 | 8.0246 | 0.67749 | -0.14648 | 122.6761 | -0.2655 | -0.036622 | -122.7676 | 0.022888 | 8.7067 | -114.3311 | -0.082398 | 0.022888 | 0.05951 | 0.86059 | 0.036621 | 8.5052 | 0.068664 | 0.022888 | 122.8592 | 8.2077 | -0.082398 | 0.068664 | 0.022888 | 8.2077 | 8.5052 | 122.8592 | -122.8729 | -122.9187
1273.9688 | 122.8958 | -0.17395 | 122.6074 | 0.1297 | 0.0079042 | 0.019013 | 0.028412 | 0.053619 | 0.059601 | 0.15445 | -0.10071 | -0.1236 | -0.17853 | 8.4641 | 8.432 | 8.3313 | 0.52643 | 0.050354 | 122.6303 | -0.24261 | -0.004578 | -122.731 | 0.073242 | 8.638 | -114.1754 | -0.068665 | 0.022888 | 0.07782 | 0.70038 | 0.2243 | 8.606 | 0.050354 | 0.073242 | 122.8043 | 8.5052 | -0.068665 | 0.050354 | 0.073242 | 8.5052 | 8.606 | 122.8043 | -122.7859 | -122.85
1275.0156 | 122.8043 | -0.20599 | 122.612 | 0.36621 | 0.010895 | 0.024139 | 0.037384 | 0.056183 | 0.055969 | 0.14996 | -0.17395 | -0.13733 | -0.2655 | 12.8128 | 12.7716 | 12.4832 | 0.55847 | -0.10071 | 122.6532 | -0.28381 | -0.059509 | -122.7493 | 0.032044 | 13.0188 | -109.8404 | -0.077819 | 0.041198 | 0.091553 | 0.76447 | 0.10529 | 12.9776 | 0.068665 | 0.032044 | 122.8592 | 12.6892 | -0.077819 | 0.068665 | 0.032044 | 12.6892 | 12.9776 | 122.8592 | -122.8775 | -122.8958
1275.9688 | 122.8409 | -0.16022 | 122.612 | 0 | 0.0083314 | 0.023285 | 0.030121 | 0.054901 | 0.056824 | 0.15189 | -0.073242 | -0.15106 | -0.20599 | 11.2244 | 11.1649 | 10.8719 | 0.67749 | 0.018311 | 122.6349 | -0.26093 | -0.045777 | -122.7631 | 0.086975 | 11.3846 | -111.4471 | -0.10071 | 0.022888 | 0.13275 | 0.83771 | 0.17853 | 11.3251 | 0.009155 | 0.086975 | 122.7951 | 11.0321 | -0.10071 | 0.009155 | 0.086975 | 11.0321 | 11.3251 | 122.7951 | -122.818 | -122.8729
1277.0156 | 122.7722 | -0.21515 | 122.612 | 0.2594 | 0.01004 | 0.022858 | 0.037598 | 0.056396 | 0.058105 | 0.1506 | -0.14648 | -0.13275 | -0.24719 | 10.5972 | 10.5011 | 10.3592 | 0.69122 | -0.13733 | 122.6486 | -0.30212 | -0.032043 | -122.7448 | 0.068665 | 10.8124 | -112.1109 | -0.086975 | 0.036621 | 0.10071 | 0.90637 | 0.07782 | 10.7162 | 0.082398 | 0.068665 | 122.8638 | 10.5743 | -0.086975 | 0.082398 | 0.068665 | 10.5743 | 10.7162 | 122.8638 | -122.8592 | -122.9141
1277.9688 | 122.8638 | -0.15564 | 122.6074 | 0.12207 | 0.0089722 | 0.020935 | 0.028839 | 0.054901 | 0.059174 | 0.15146 | -0.1236 | -0.13733 | -0.19226 | 10.5377 | 10.4828 | 10.2997 | 0.64545 | 0.041199 | 122.6212 | -0.23804 | -0.036621 | -122.7448 | 0.032044 | 10.6934 | -112.1246 | -0.082397 | 0.013733 | 0.068665 | 0.80109 | 0.19684 | 10.6384 | 0.018311 | 0.032044 | 122.7768 | 10.4553 | -0.082397 | 0.018311 | 0.032044 | 10.4553 | 10.6384 | 122.7768 | -122.7997 | -122.8455
1279.0156 | 122.7951 | -0.20599 | 122.6028 | 0.3891 | 0.0098268 | 0.026703 | 0.036102 | 0.056183 | 0.058319 | 0.1521 | -0.16479 | -0.10529 | -0.24261 | 9.9243 | 9.8694 | 9.6359 | 0.17853 | -0.10529 | 122.6303 | -0.29297 | -0.036621 | -122.7081 | 0.041199 | 10.1303 | -112.7335 | -0.086975 | 0.027466 | 0.07782 | 0.38452 | 0.10071 | 10.0754 | 0.10071 | 0.041199 | 122.8363 | 9.8419 | -0.086975 | 0.10071 | 0.041199 | 9.8419 | 10.0754 | 122.8363 | -122.8455 | -122.8958
1279.9688 | 122.8638 | -0.20142 | 122.6028 | 0.26703 | 0.011963 | 0.021362 | 0.02948 | 0.052765 | 0.060455 | 0.15295 | -0.21973 | -0.16937 | -0.2243 | 9.8785 | 9.8785 | 9.6725 | 0.10986 | -0.018311 | 122.612 | -0.27466 | -0.022888 | -122.7722 | -0.018311 | 10.08 | -112.7243 | -0.073242 | 0.009156 | 0.004577 | 0.31128 | 0.18311 | 10.08 | 0.032043 | -0.018311 | 122.8134 | 9.874 | -0.073242 | 0.032043 | -0.018311 | 9.874 | 10.08 | 122.8134 | -122.8271 | -122.8775
1281.0156 | 122.7722 | -0.20142 | 122.6349 | 0.34332 | 0.0093994 | 0.018585 | 0.033966 | 0.053192 | 0.057465 | 0.15082 | -0.16022 | -0.11444 | -0.22888 | 10.2356 | 10.1578 | 9.8969 | 0.17853 | -0.10986 | 122.6578 | -0.27466 | -0.027466 | -122.7493 | 0.041199 | 10.437 | -112.4771 | -0.073242 | 0.022888 | 0.068665 | 0.37994 | 0.091553 | 10.3592 | 0.086975 | 0.041199 | 122.8592 | 10.0983 | -0.073242 | 0.086975 | 0.041199 | 10.0983 | 10.3592 | 122.8592 | -122.8638 | -122.9095
1281.9688 | 122.8912 | -0.14648 | 122.612 | 0.19073 | 0.0083314 | 0.021149 | 0.026703 | 0.052978 | 0.055756 | 0.15146 | -0.10529 | -0.14648 | -0.16937 | 11.9202 | 11.8607 | 11.6455 | 0.13733 | 0.036621 | 122.6486 | -0.25177 | -0.022889 | -122.7585 | 0.041198 | 12.0666 | -110.7513 | -0.10529 | 0.036621 | 0.064087 | 0.28381 | 0.18311 | 12.0071 | 0 | 0.041198 | 122.7951 | 11.792 | -0.10529 | 0 | 0.041198 | 11.792 | 12.0071 | 122.7951 | -122.7814 | -122.8638
1283.0156 | 122.8546 | -0.20142 | 122.6028 | 0.4425 | 0.009613 | 0.022644 | 0.03418 | 0.045715 | 0.046356 | 0.13031 | -0.12817 | -0.13275 | -0.21973 | 31.485 | 31.3522 | 30.78 | 0.068665 | -0.045776 | 122.6303 | -0.28381 | -0.018311 | -122.7356 | 0.073242 | 31.6864 | -91.2506 | -0.082397 | 0.027466 | 0.091553 | 0.27008 | 0.15564 | 31.5536 | 0.068665 | 0.073242 | 122.8317 | 30.9814 | -0.082397 | 0.068665 | 0.073242 | 30.9814 | 31.5536 | 122.8317 | -122.8226 | -122.8867
1283.9688 | 122.9004 | -0.16937 | 122.5983 | 0.21362 | 0.0087586 | 0.017731 | 0.02713 | 0.040802 | 0.045288 | 0.13223 | -0.1236 | -0.13733 | -0.19226 | 29.631 | 29.567 | 29.0405 | 0.12817 | 0.013733 | 122.644 | -0.27008 | -0.022888 | -122.7356 | 0.045777 | 29.8004 | -93.0313 | -0.10071 | 0.045776 | 0.068665 | 0.29755 | 0.18311 | 29.7363 | 0.032044 | 0.045777 | 122.8134 | 29.2099 | -0.10071 | 0.032044 | 0.045777 | 29.2099 | 29.7363 | 122.8134 | -122.7905 | -122.8683
1285.0156 | 122.8729 | -0.16022 | 122.4976 | 0.43488 | 0.0098268 | 0.024353 | 0.035461 | 0.040588 | 0.044861 | 0.12796 | -0.073242 | -0.16937 | -0.21515 | 33.6823 | 33.5861 | 33.0139 | 0.045776 | 0.009155 | 122.612 | -0.23346 | -0.054932 | -122.6669 | 0.086975 | 33.8425 | -88.9114 | -0.073242 | 0.11444 | 0.14191 | 0.20599 | 0.16937 | 33.7463 | -0.009156 | 0.086975 | 122.7722 | 33.1741 | -0.073242 | -0.009156 | 0.086975 | 33.1741 | 33.7463 | 122.7722 | -122.7127 | -122.731
1285.9688 | 122.9004 | -0.14191 | 122.612 | 0.19836 | 0.0070496 | 0.016876 | 0.030548 | 0.043152 | 0.045715 | 0.13138 | -0.11444 | -0.12817 | -0.20599 | 28.1387 | 28.0746 | 27.6352 | 0.15564 | 0.013733 | 122.6578 | -0.26093 | -0.064087 | -122.7402 | 0.027466 | 28.2806 | -94.5374 | -0.11902 | 0.045776 | 0.091553 | 0.29755 | 0.15564 | 28.2166 | 0.013733 | 0.027466 | 122.7997 | 27.7771 | -0.11902 | 0.013733 | 0.027466 | 27.7771 | 28.2166 | 122.7997 | -122.818 | -122.8729
1287.0156 | 122.7905 | -0.21515 | 122.612 | 0.20599 | 0.010468 | 0.022644 | 0.036957 | 0.045074 | 0.044647 | 0.13202 | -0.17395 | -0.10986 | -0.20142 | 28.0563 | 27.9282 | 27.3148 | 0.23804 | -0.12817 | 122.6852 | -0.31586 | 0.013733 | -122.7219 | 0.041199 | 28.2715 | -94.6838 | -0.10071 | 0.073242 | 0.027466 | 0.45319 | 0.086975 | 28.1433 | 0.10529 | 0.041199 | 122.9004 | 27.5299 | -0.10071 | 0.10529 | 0.041199 | 27.5299 | 28.1433 | 122.9004 | -122.8134 | -122.9279
1287.9688 | 122.7859 | -0.16479 | 122.6715 | -0.015259 | 0.012177 | 0.022858 | 0.033753 | 0.03952 | 0.045288 | 0.12646 | -0.16937 | -0.12817 | -0.24261 | 33.1924 | 33.0643 | 31.3797 | 0.59052 | -0.19226 | 122.7402 | -0.28381 | -0.07782 | -122.7997 | -0.004578 | 33.3572 | -89.6072 | -0.11902 | 0.068664 | 0.073242 | 0.75531 | -0.027466 | 33.2291 | 0.036621 | -0.004578 | 122.905 | 31.5445 | -0.11902 | 0.036621 | -0.004578 | 31.5445 | 33.2291 | 122.905 | -122.9141 | -122.9553
1289.0156 | 122.905 | -0.14191 | 122.5845 | 0.30518 | 0.0087586 | 0.024353 | 0.03653 | 0.044006 | 0.045288 | 0.12903 | -0.068665 | -0.15564 | -0.21973 | 31.3385 | 31.2515 | 29.3015 | 0.16479 | 0.004578 | 122.6166 | -0.25177 | -0.07782 | -122.7402 | 0.073242 | 31.4804 | -91.333 | -0.10986 | 0.032043 | 0.15106 | 0.3067 | 0.14649 | 31.3934 | -0.013733 | 0.073242 | 122.7585 | 29.4434 | -0.10986 | -0.013733 | 0.073242 | 29.4434 | 31.3934 | 122.7585 | -122.8043 | -122.8363
1289.9688 | 122.7768 | -0.21057 | 122.6303 | 0.015259 | 0.0091858 | 0.022003 | 0.033539 | 0.043365 | 0.045288 | 0.12753 | -0.15106 | -0.11444 | -0.22888 | 31.6818 | 31.5674 | 29.599 | 0.43488 | -0.09613 | 122.6761 | -0.28381 | -0.018311 | -122.7448 | 0.059509 | 31.8924 | -91.0629 | -0.073242 | 0.045776 | 0.07782 | 0.64545 | 0.11444 | 31.778 | 0.09613 | 0.059509 | 122.8867 | 29.8096 | -0.073242 | 0.09613 | 0.059509 | 29.8096 | 31.778 | 122.8867 | -122.8592 | -122.9141
1291.0156 | 122.7814 | -0.20599 | 122.6257 | 0.23651 | 0.010681 | 0.022003 | 0.035889 | 0.044861 | 0.044647 | 0.12711 | -0.15564 | -0.13275 | -0.25635 | 31.4758 | 31.3431 | 28.8254 | 0.25177 | -0.14648 | 122.6669 | -0.29297 | -0.050354 | -122.7585 | 0.050354 | 31.6818 | -91.2827 | -0.086975 | 0.041199 | 0.10071 | 0.45776 | 0.05951 | 31.5491 | 0.073243 | 0.050354 | 122.8729 | 29.0314 | -0.086975 | 0.073243 | 0.050354 | 29.0314 | 31.5491 | 122.8729 | -122.8821 | -122.9187
1291.9688 | 122.9233 | -0.15106 | 122.5983 | 0.17548 | 0.006836 | 0.019013 | 0.02713 | 0.042725 | 0.046143 | 0.12753 | -0.07782 | -0.14648 | -0.18768 | 31.3293 | 31.2515 | 28.7659 | 0.09613 | 0.045776 | 122.6852 | -0.25635 | -0.036621 | -122.7448 | 0.073242 | 31.4804 | -91.3467 | -0.10529 | 0.086975 | 0.10986 | 0.24719 | 0.19684 | 31.4026 | 0.004578 | 0.073242 | 122.8363 | 28.9169 | -0.10529 | 0.004578 | 0.073242 | 28.9169 | 31.4026 | 122.8363 | -122.786 | -122.8546
1293.0156 | 122.7722 | -0.21515 | 122.6257 | 0.39673 | 0.0083314 | 0.023499 | 0.035461 | 0.044434 | 0.045288 | 0.12817 | -0.31128 | -0.1236 | -0.21515 | 31.0089 | 30.867 | 28.2669 | 0.27008 | -0.12817 | 122.6898 | -0.28839 | 0 | -122.7493 | -0.09613 | 31.2241 | -91.7587 | -0.073242 | 0.064087 | -0.09613 | 0.48523 | 0.086975 | 31.0822 | 0.091553 | -0.09613 | 122.905 | 28.4821 | -0.073242 | 0.091553 | -0.09613 | 28.4821 | 31.0822 | 122.905 | -122.8409 | -122.9141
1293.9688 | 122.7905 | -0.20142 | 122.6395 | 0.053405 | 0.008545 | 0.016663 | 0.03418 | 0.04422 | 0.044006 | 0.12839 | -0.16479 | -0.09613 | -0.23346 | 30.5099 | 30.4047 | 27.5299 | 0.36163 | -0.086975 | 122.6532 | -0.29297 | -0.032043 | -122.7356 | 0.036621 | 30.7114 | -92.2348 | -0.091553 | 0.013733 | 0.068664 | 0.56305 | 0.11444 | 30.6061 | 0.10529 | 0.036621 | 122.8546 | 27.7313 | -0.091553 | 0.10529 | 0.036621 | 27.7313 | 30.6061 | 122.8546 | -122.8729 | -122.9324
1295.0156 | 122.8226 | -0.19684 | 122.5937 | 0.36621 | 0.010254 | 0.020935 | 0.03418 | 0.045074 | 0.046997 | 0.13095 | -0.16022 | -0.12817 | -0.24719 | 29.8187 | 29.7318 | 26.6327 | 0.19226 | -0.09613 | 122.6624 | -0.30212 | -0.050354 | -122.7219 | 0.036621 | 30.0156 | -92.8619 | -0.10529 | 0.068665 | 0.086975 | 0.3891 | 0.10071 | 29.9286 | 0.068664 | 0.036621 | 122.8592 | 26.8295 | -0.10529 | 0.068664 | 0.036621 | 26.8295 | 29.9286 | 122.8592 | -122.8409 | -122.8958
1295.9688 | 122.7905 | -0.20142 | 122.6532 | -0.053406 | 0.010681 | 0.020081 | 0.033753 | 0.045288 | 0.045502 | 0.13266 | -0.16937 | -0.091553 | -0.24719 | 29.1733 | 29.0771 | 25.9415 | 0.36163 | -0.09613 | 122.6944 | -0.29297 | -0.045776 | -122.7448 | 0.032043 | 29.3747 | -93.5761 | -0.091553 | 0.041199 | 0.077819 | 0.56305 | 0.10529 | 29.2786 | 0.10986 | 0.032043 | 122.8958 | 26.1429 | -0.091553 | 0.10986 | 0.032043 | 26.1429 | 29.2786 | 122.8958 | -122.9004 | -122.9462
1297.0156 | 122.8271 | -0.19226 | 122.6212 | 0.32043 | 0.010681 | 0.02179 | 0.03418 | 0.046997 | 0.045502 | 0.13052 | -0.15564 | -0.11902 | -0.23346 | 28.4454 | 28.3585 | 25.0443 | 0.28381 | -0.11444 | 122.6852 | -0.28839 | -0.041198 | -122.7402 | 0.036621 | 28.6377 | -94.2627 | -0.09613 | 0.064087 | 0.077819 | 0.47607 | 0.07782 | 28.5507 | 0.073242 | 0.036621 | 122.8775 | 25.2365 | -0.09613 | 0.073242 | 0.036621 | 25.2365 | 28.5507 | 122.8775 | -122.8546 | -122.9095
1297.9688 | 122.8867 | -0.16479 | 122.6028 | -0.14496 | 0.0074768 | 0.018799 | 0.029266 | 0.043365 | 0.048492 | 0.13052 | -0.082397 | -0.17395 | -0.20599 | 28.8574 | 28.8116 | 25.6027 | 0.15564 | 0.059509 | 122.6166 | -0.27008 | -0.041199 | -122.7768 | 0.082398 | 29.0222 | -93.7912 | -0.10529 | 0.013733 | 0.1236 | 0.32044 | 0.2243 | 28.9764 | -0.009155 | 0.082398 | 122.7814 | 25.7675 | -0.10529 | -0.009155 | 0.082398 | 25.7675 | 28.9764 | 122.7814 | -122.8088 | -122.8729
1299.0312 | 122.7814 | -0.2243 | 122.6212 | 3.8147 | 0.010468 | 0.017304 | 0.035461 | 0.042725 | 0.044434 | 0.12604 | 0.054932 | -0.091553 | -0.2243 | 33.5083 | 33.4076 | 29.6036 | 0.26093 | -0.12817 | 122.6852 | -0.29297 | 0 | -122.7127 | 0.27924 | 33.7326 | -89.2136 | -0.068665 | 0.064087 | 0.27924 | 0.48523 | 0.09613 | 33.6319 | 0.13275 | 0.27924 | 122.9095 | 29.8279 | -0.068665 | 0.13275 | 0.27924 | 29.8279 | 33.6319 | 122.9095 | -122.8455 | -122.9141
1299.9688 | 122.937 | -0.15564 | 122.5891 | 0.14496 | 0.0076904 | 0.02243 | 0.029907 | 0.043579 | 0.046783 | 0.12881 | -0.082397 | -0.14648 | -0.21057 | 30.5008 | 30.4276 | 26.944 | 0.3067 | 0.059509 | 122.6532 | -0.2655 | -0.054931 | -122.7356 | 0.073243 | 30.6564 | -92.1616 | -0.10986 | 0.064087 | 0.12817 | 0.46234 | 0.21515 | 30.5832 | 0.009156 | 0.073243 | 122.8088 | 27.0996 | -0.10986 | 0.009156 | 0.073243 | 27.0996 | 30.5832 | 122.8088 | -122.7997 | -122.8546
1301.0156 | 122.905 | -0.15564 | 122.5983 | 0.41962 | 0.0091858 | 0.020935 | 0.036743 | 0.047638 | 0.048279 | 0.13565 | -0.11444 | -0.16937 | -0.21515 | 25.9323 | 25.827 | 22.6776 | 0.10986 | -0.013733 | 122.6578 | -0.27008 | -0.059509 | -122.7676 | 0.041199 | 26.088 | -96.7712 | -0.11444 | 0.059509 | 0.10071 | 0.2655 | 0.14191 | 25.9827 | -0.013733 | 0.041199 | 122.8134 | 22.8333 | -0.11444 | -0.013733 | 0.041199 | 22.8333 | 25.9827 | 122.8134 | -122.8134 | -122.8683
1301.9688 | 122.8271 | -0.19684 | 122.6349 | -0.030518 | 0.0072632 | 0.020508 | 0.033112 | 0.046997 | 0.04892 | 0.13458 | -0.091553 | -0.15564 | -0.22888 | 24.1745 | 24.0784 | 21.0022 | 0.2655 | -0.022888 | 122.6715 | -0.28839 | -0.032044 | -122.7905 | 0.10529 | 24.3713 | -98.5565 | -0.091553 | 0.036621 | 0.13733 | 0.46234 | 0.17395 | 24.2752 | 0.041198 | 0.10529 | 122.8683 | 21.199 | -0.091553 | 0.041198 | 0.10529 | 21.199 | 24.2752 | 122.8683 | -122.8638 | -122.9233
1303.0156 | 122.8775 | -0.15106 | 122.612 | 0.33569 | 0.0074768 | 0.023499 | 0.032684 | 0.042297 | 0.044006 | 0.12454 | -0.082397 | -0.16479 | -0.21057 | 35.527 | 35.4309 | 31.4621 | 0.086975 | 0 | 122.6486 | -0.2655 | -0.059509 | -122.7768 | 0.068665 | 35.6781 | -87.1811 | -0.11444 | 0.036621 | 0.12817 | 0.23804 | 0.15106 | 35.582 | -0.013733 | 0.068665 | 122.7997 | 31.6132 | -0.11444 | -0.013733 | 0.068665 | 31.6132 | 35.582 | 122.7997 | -122.8226 | -122.8775
1303.9844 | 122.7768 | -0.21057 | 122.5937 | 0.19073 | 0.010895 | 0.025208 | 0.038452 | 0.043793 | 0.043366 | 0.1239 | -0.11444 | -0.13275 | -0.21973 | 35.0601 | 34.9136 | 30.8304 | 0.20142 | -0.09613 | 122.699 | -0.32501 | -0.009156 | -122.7264 | 0.09613 | 35.2707 | -87.6801 | -0.11444 | 0.10529 | 0.10529 | 0.41199 | 0.11444 | 35.1242 | 0.07782 | 0.09613 | 122.9095 | 31.041 | -0.11444 | 0.07782 | 0.09613 | 31.041 | 35.1242 | 122.9095 | -122.8134 | -122.9187
1305.0156 | 122.9095 | -0.17395 | 122.5662 | 0.41962 | 0.0076904 | 0.026489 | 0.030121 | 0.042511 | 0.043579 | 0.12219 | -0.24719 | -0.1831 | -0.21973 | 36.5067 | 36.3739 | 31.4896 | 0.073242 | 0.009155 | 122.612 | -0.29755 | -0.045777 | -122.7493 | -0.073242 | 36.6806 | -86.1923 | -0.1236 | 0.045777 | -0.027465 | 0.24719 | 0.1831 | 36.5479 | -0.009155 | -0.073242 | 122.7859 | 31.6635 | -0.1236 | -0.009155 | -0.073242 | 31.6635 | 36.5479 | 122.7859 | -122.7859 | -122.8638
1305.9688 | 122.9187 | -0.16022 | 122.6028 | 0.022888 | 0.006836 | 0.020935 | 0.030762 | 0.040588 | 0.045074 | 0.12326 | -0.086975 | -0.16937 | -0.22888 | 34.8907 | 34.7946 | 30.0201 | 0.16022 | 0.054932 | 122.6166 | -0.25635 | -0.068665 | -122.7722 | 0.073242 | 35.051 | -87.8082 | -0.096131 | 0.013733 | 0.14191 | 0.32043 | 0.21515 | 34.9548 | -0.009156 | 0.073242 | 122.7768 | 30.1804 | -0.096131 | -0.009156 | 0.073242 | 30.1804 | 34.9548 | 122.7768 | -122.8317 | -122.8592
1307.0156 | 122.9324 | -0.19684 | 122.5891 | 0.41199 | 0.008545 | 0.020294 | 0.03183 | 0.040588 | 0.044647 | 0.12433 | -0.059509 | -0.15106 | -0.21515 | 34.7305 | 34.6344 | 30.0476 | 0.20142 | 0 | 122.644 | -0.27924 | -0.018311 | -122.7402 | 0.13733 | 34.9274 | -87.9547 | -0.082398 | 0.054932 | 0.15564 | 0.39825 | 0.19684 | 34.8312 | 0.045776 | 0.13733 | 122.8409 | 30.2444 | -0.082398 | 0.045776 | 0.13733 | 30.2444 | 34.8312 | 122.8409 | -122.8043 | -122.8683
1307.9688 | 122.85 | -0.19226 | 122.6349 | -0.030518 | 0.0061952 | 0.020081 | 0.030762 | 0.040588 | 0.045288 | 0.12561 | -0.10071 | -0.14648 | -0.20599 | 34.2865 | 34.1858 | 29.6494 | 0.49439 | -0.013733 | 122.6578 | -0.27924 | -0.013733 | -122.7814 | 0.091553 | 34.4788 | -88.4491 | -0.086975 | 0.022888 | 0.10529 | 0.68665 | 0.17853 | 34.3781 | 0.045777 | 0.091553 | 122.85 | 29.8416 | -0.086975 | 0.045777 | 0.091553 | 29.8416 | 34.3781 | 122.85 | -122.8409 | -122.9141
1308.9844 | 122.9095 | -0.17853 | 122.5845 | 0.36621 | 0.011108 | 0.024353 | 0.036957 | 0.044647 | 0.046143 | 0.12732 | -0.07782 | -0.15564 | -0.21515 | 34.0851 | 33.989 | 29.5853 | 0.25635 | -0.013733 | 122.6898 | -0.27008 | -0.036621 | -122.7402 | 0.10071 | 34.2636 | -88.5956 | -0.091553 | 0.10528 | 0.13733 | 0.43488 | 0.16479 | 34.1675 | 0.022888 | 0.10071 | 122.8683 | 29.7638 | -0.091553 | 0.022888 | 0.10071 | 29.7638 | 34.1675 | 122.8683 | -122.7997 | -122.8546
1310.0156 | 122.8821 | -0.2243 | 122.612 | 0.28229 | 0.0098268 | 0.020721 | 0.030762 | 0.041656 | 0.044647 | 0.12753 | -0.23804 | -0.16022 | -0.22888 | 33.4534 | 33.3664 | 28.9581 | 0.33417 | -0.068665 | 122.6028 | -0.33875 | -0.004578 | -122.7722 | -0.013733 | 33.6777 | -89.2456 | -0.11444 | -0.009156 | -0.009155 | 0.55847 | 0.15564 | 33.5907 | 0.064087 | -0.013733 | 122.8271 | 29.1824 | -0.11444 | 0.064087 | -0.013733 | 29.1824 | 33.5907 | 122.8271 | -122.8409 | -122.9507
1310.9688 | 122.8546 | -0.21515 | 122.6395 | 0.091552 | 0.0093994 | 0.02243 | 0.039734 | 0.041016 | 0.040375 | 0.11963 | -0.10529 | -0.12817 | -0.24719 | 38.5574 | 38.4155 | 33.5358 | 0.32044 | -0.050354 | 122.6761 | -0.28839 | -0.032043 | -122.7676 | 0.10986 | 38.7726 | -84.2239 | -0.073242 | 0.036621 | 0.14191 | 0.53558 | 0.16479 | 38.6307 | 0.086975 | 0.10986 | 122.8912 | 33.7509 | -0.073242 | 0.086975 | 0.10986 | 33.7509 | 38.6307 | 122.8912 | -122.8867 | -122.9279
1312.0156 | 122.8912 | -0.17853 | 122.6028 | 0.35858 | 0.0081178 | 0.022858 | 0.030548 | 0.041656 | 0.043152 | 0.12454 | -0.10071 | -0.14191 | -0.19684 | 35.495 | 35.3897 | 30.8762 | 0.15564 | -0.022888 | 122.6715 | -0.25635 | -0.01831 | -122.7448 | 0.07782 | 35.6735 | -87.2131 | -0.07782 | 0.068665 | 0.09613 | 0.33417 | 0.15564 | 35.5682 | 0.036621 | 0.07782 | 122.85 | 31.0547 | -0.07782 | 0.036621 | 0.07782 | 31.0547 | 35.5682 | 122.85 | -122.7997 | -122.8592
1313.25 | 122.8088 | -0.20142 | 122.731 | -0.030518 | 0.010254 | 0.020294 | 0.032684 | 0.039734 | 0.041443 | 0.12262 | -0.1831 | -0.1236 | -0.23804 | 35.3302 | 35.2432 | 30.5969 | 0.3067 | -0.091553 | 122.7173 | -0.31128 | -0.036621 | -122.8546 | 0.018311 | 35.5316 | -87.4878 | -0.10986 | -0.013733 | 0.054932 | 0.50812 | 0.10986 | 35.4446 | 0.07782 | 0.018311 | 122.9187 | 30.7983 | -0.10986 | 0.07782 | 0.018311 | 30.7983 | 35.4446 | 122.9187 | -122.9691 | -123.0423
1315.0469 | 122.9187 | -0.14191 | 122.6166 | 0.091552 | 0.008545 | 0.024353 | 0.028839 | 0.041229 | 0.043793 | 0.12497 | -0.091553 | -0.13275 | -0.19684 | 34.9045 | 34.8267 | 30.4276 | 0.1236 | 0.054932 | 122.6624 | -0.2655 | -0.054931 | -122.7493 | 0.050354 | 35.0464 | -87.7899 | -0.1236 | 0.045777 | 0.10529 | 0.2655 | 0.19684 | 34.9686 | 0.009156 | 0.050354 | 122.8043 | 30.5695 | -0.1236 | 0.009156 | 0.050354 | 30.5695 | 34.9686 | 122.8043 | -122.8134 | -122.8821
1315.8281 | 122.7081 | -0.19226 | 122.6669 | 0.34332 | 0.010468 | 0.020508 | 0.038452 | 0.042938 | 0.041229 | 0.1239 | -0.16937 | -0.11444 | -0.24719 | 34.4559 | 34.346 | 30.0385 | 0.2243 | -0.13275 | 122.7036 | -0.31128 | -0.054931 | -122.7814 | 0.022888 | 34.6481 | -88.3209 | -0.11902 | 0.036621 | 0.077819 | 0.41656 | 0.05951 | 34.5383 | 0.07782 | 0.022888 | 122.8958 | 30.2307 | -0.11902 | 0.07782 | 0.022888 | 30.2307 | 34.5383 | 122.8958 | -122.9141 | -122.9782
1317.125 | 122.8775 | -0.26093 | 122.5388 | 0.28992 | 0.006836 | 0.020081 | 0.028626 | 0.041229 | 0.044647 | 0.12561 | -0.14191 | -0.14648 | -0.21057 | 34.1858 | 34.108 | 29.9286 | 0.10529 | -0.15106 | 122.5479 | -0.32959 | 0.050354 | -122.6852 | 0.11902 | 34.4467 | -88.4308 | -0.068665 | 0.009156 | 0.068664 | 0.36621 | 0.10986 | 34.3689 | 0.11444 | 0.11902 | 122.8088 | 30.1895 | -0.068665 | 0.11444 | 0.11902 | 30.1895 | 34.3689 | 122.8088 | -122.7493 | -122.8683
1317.9062 | 122.818 | -0.22888 | 122.6074 | -0.0076295 | 0.010468 | 0.021149 | 0.035889 | 0.044006 | 0.046783 | 0.12967 | -0.16937 | -0.10986 | -0.26093 | 29.4983 | 29.3976 | 25.7217 | 0.31128 | -0.082397 | 122.6578 | -0.31128 | -0.032043 | -122.7173 | 0.059509 | 29.7272 | -93.2098 | -0.082397 | 0.050354 | 0.091552 | 0.54016 | 0.14649 | 29.6265 | 0.11902 | 0.059509 | 122.8867 | 25.9506 | -0.082397 | 0.11902 | 0.059509 | 25.9506 | 29.6265 | 122.8867 | -122.8683 | -122.9187
1318.4688 | 122.8683 | -0.19684 | 122.5937 | 0.42725 | 0.0098268 | 0.02243 | 0.035889 | 0.049988 | 0.05127 | 0.14014 | -0.16937 | -0.15106 | -0.24719 | 21.0159 | 20.9244 | 18.457 | 0.19684 | -0.082397 | 122.6395 | -0.29297 | -0.050354 | -122.7448 | 0.027465 | 21.2128 | -101.6693 | -0.096131 | 0.045776 | 0.077819 | 0.39368 | 0.11444 | 21.1212 | 0.045776 | 0.027465 | 122.8363 | 18.6539 | -0.096131 | 0.045776 | 0.027465 | 18.6539 | 21.1212 | 122.8363 | -122.8409 | -122.8867
1318.9688 | 122.7814 | -0.19684 | 122.6624 | -1.7929 | 0.011108 | 0.023071 | 0.033539 | 0.055969 | 0.054688 | 0.1489 | -0.16479 | -0.068665 | -0.20599 | 13.3804 | 13.3072 | 11.8011 | 0.37994 | -0.086975 | 122.6852 | -0.3067 | -0.009156 | -122.731 | 0.032043 | 13.5773 | -109.3552 | -0.10986 | 0.022888 | 0.041199 | 0.57678 | 0.10986 | 13.504 | 0.12817 | 0.032043 | 122.8821 | 11.998 | -0.10986 | 0.12817 | 0.032043 | 11.998 | 13.504 | 122.8821 | -122.8683 | -122.9691
1319.9688 | 122.8226 | -0.20599 | 122.6257 | 0.030518 | 0.01004 | 0.018799 | 0.032471 | 0.052978 | 0.056824 | 0.15082 | -0.13275 | -0.12817 | -0.23346 | 11.1099 | 11.0779 | 9.8602 | 0.35706 | -0.054932 | 122.6715 | -0.31586 | -0.027465 | -122.7539 | 0.073243 | 11.3159 | -111.5479 | -0.10986 | 0.045777 | 0.10071 | 0.56305 | 0.15106 | 11.2839 | 0.07782 | 0.073243 | 122.8775 | 10.0662 | -0.10986 | 0.07782 | 0.073243 | 10.0662 | 11.2839 | 122.8775 | -122.8592 | -122.9416
1320.9688 | 122.8043 | -0.2243 | 122.6257 | 0.015259 | 0.0089722 | 0.018372 | 0.031189 | 0.058533 | 0.057251 | 0.15189 | -0.12817 | -0.11902 | -0.23804 | 10.2448 | 10.2036 | 9.0958 | 0.39368 | -0.064087 | 122.7036 | -0.32044 | -0.013733 | -122.7448 | 0.09613 | 10.4691 | -112.4222 | -0.096131 | 0.07782 | 0.10986 | 0.61798 | 0.16022 | 10.4279 | 0.10529 | 0.09613 | 122.9279 | 9.3201 | -0.096131 | 0.10529 | 0.09613 | 9.3201 | 10.4279 | 122.9279 | -122.8638 | -122.9462
1321.9688 | 122.8271 | -0.21973 | 122.6349 | 0.038147 | 0.0087586 | 0.020294 | 0.034821 | 0.055756 | 0.058105 | 0.15082 | -0.15564 | -0.10986 | -0.2655 | 10.0296 | 9.9747 | 8.9172 | 0.41657 | -0.09613 | 122.6715 | -0.32959 | -0.045776 | -122.7448 | 0.064087 | 10.2493 | -112.6602 | -0.10986 | 0.036621 | 0.10986 | 0.63629 | 0.1236 | 10.1944 | 0.10986 | 0.064087 | 122.8912 | 9.137 | -0.10986 | 0.10986 | 0.064087 | 9.137 | 10.1944 | 122.8912 | -122.9004 | -122.9645
1322.9844 | 122.8592 | -0.21057 | 122.6257 | 0.10681 | 0.011536 | 0.019653 | 0.035248 | 0.054047 | 0.056824 | 0.15295 | -0.10986 | -0.12817 | -0.23804 | 9.906 | 9.819 | 8.8348 | 0.47607 | -0.054932 | 122.7127 | -0.29297 | -0.027466 | -122.7539 | 0.10071 | 10.1166 | -112.8067 | -0.082398 | 0.086976 | 0.12817 | 0.68664 | 0.15564 | 10.0296 | 0.082397 | 0.10071 | 122.9233 | 9.0454 | -0.082398 | 0.082397 | 0.10071 | 9.0454 | 10.0296 | 122.9233 | -122.8638 | -122.9187
1323.9688 | 122.8363 | -0.19684 | 122.612 | 0.030518 | 0.0098268 | 0.023499 | 0.034393 | 0.057037 | 0.057678 | 0.1506 | -0.15564 | -0.10071 | -0.24719 | 9.6588 | 9.613 | 8.6563 | 0.61798 | -0.07782 | 122.7036 | -0.32044 | -0.050354 | -122.7127 | 0.041198 | 9.8557 | -112.999 | -0.1236 | 0.091552 | 0.091552 | 0.81482 | 0.11902 | 9.8099 | 0.09613 | 0.041198 | 122.9004 | 8.8531 | -0.1236 | 0.09613 | 0.041198 | 8.8531 | 9.8099 | 122.9004 | -122.8592 | -122.9324
1325.0469 | 122.7905 | -0.21057 | 122.6944 | -0.030518 | 0.010681 | 0.018799 | 0.031616 | 0.054474 | 0.057892 | 0.15381 | -0.19226 | -0.10071 | -0.23346 | 9.5261 | 9.4986 | 8.5876 | 0.76446 | -0.086975 | 122.6852 | -0.31128 | -0.022888 | -122.7951 | 0.01831 | 9.7366 | -113.1958 | -0.10071 | -0.009155 | 0.041198 | 0.97504 | 0.1236 | 9.7092 | 0.10986 | 0.01831 | 122.8958 | 8.7982 | -0.10071 | 0.10986 | 0.01831 | 8.7982 | 9.7092 | 122.8958 | -122.9279 | -123.0057
1325.9688 | 122.8409 | -0.22888 | 122.5937 | -0.0076295 | 0.0093994 | 0.020081 | 0.033112 | 0.057892 | 0.054474 | 0.15359 | -0.13733 | -0.11444 | -0.25635 | 9.3979 | 9.3567 | 8.4961 | 0.73242 | -0.07782 | 122.7081 | -0.31586 | -0.027466 | -122.7081 | 0.091553 | 9.6268 | -113.237 | -0.086975 | 0.11444 | 0.11902 | 0.9613 | 0.15106 | 9.5856 | 0.11444 | 0.091553 | 122.937 | 8.725 | -0.086975 | 0.11444 | 0.091553 | 8.725 | 9.5856 | 122.937 | -122.85 | -122.9095
1326.9688 | 122.7905 | -0.21057 | 122.6212 | 0.20599 | 0.011536 | 0.018585 | 0.033112 | 0.054687 | 0.055756 | 0.14719 | -0.16022 | -0.07782 | -0.20142 | 13.8977 | 13.8153 | 12.9547 | 5.5939 | -0.091553 | 122.699 | -0.31128 | 0.009155 | -122.699 | 0.050354 | 14.1083 | -108.8058 | -0.10071 | 0.07782 | 0.041199 | 5.8044 | 0.11902 | 14.0259 | 0.13275 | 0.050354 | 122.9095 | 13.1653 | -0.10071 | 0.13275 | 0.050354 | 13.1653 | 14.0259 | 122.9095 | -122.8226 | -122.9324
1327.9688 | 122.8363 | -0.23804 | 122.6166 | 0.007629 | 0.012604 | 0.02179 | 0.034393 | 0.058105 | 0.058105 | 0.15445 | -0.15564 | -0.1236 | -0.24261 | 8.5785 | 8.5281 | 7.6767 | 0.18768 | -0.073242 | 122.6944 | -0.3067 | -0.004578 | -122.7402 | 0.082397 | 8.8165 | -114.0884 | -0.068665 | 0.07782 | 0.086975 | 0.42572 | 0.16479 | 8.7662 | 0.11444 | 0.082397 | 122.9324 | 7.9147 | -0.068665 | 0.11444 | 0.082397 | 7.9147 | 8.7662 | 122.9324 | -122.8592 | -122.9233
1329.0469 | 122.8134 | -0.21973 | 122.612 | 0.038147 | 0.011749 | 0.02243 | 0.034607 | 0.057892 | 0.057892 | 0.15488 | -0.17395 | -0.10071 | -0.24719 | 8.4183 | 8.3908 | 7.5897 | 0.2243 | -0.09613 | 122.7081 | -0.30212 | -0.027465 | -122.7127 | 0.045777 | 8.638 | -114.2212 | -0.082397 | 0.09613 | 0.073242 | 0.44403 | 0.1236 | 8.6105 | 0.11902 | 0.045777 | 122.9279 | 7.8094 | -0.082397 | 0.11902 | 0.045777 | 7.8094 | 8.6105 | 122.9279 | -122.8592 | -122.9141
1329.9688 | 122.8455 | -0.20142 | 122.6349 | 0.13733 | 0.011108 | 0.023712 | 0.034607 | 0.057037 | 0.059814 | 0.15424 | -0.10071 | -0.11902 | -0.23804 | 8.3862 | 8.3313 | 7.5668 | 0.16937 | -0.045776 | 122.6944 | -0.3067 | -0.036621 | -122.7539 | 0.10071 | 8.5876 | -114.3036 | -0.10529 | 0.059509 | 0.13733 | 0.37079 | 0.15564 | 8.5327 | 0.082397 | 0.10071 | 122.8958 | 7.7682 | -0.10529 | 0.082397 | 0.10071 | 7.7682 | 8.5327 | 122.8958 | -122.8729 | -122.9416
1330.9688 | 122.8455 | -0.19226 | 122.5845 | 0.11444 | 0.011108 | 0.021576 | 0.034607 | 0.058746 | 0.059601 | 0.15381 | -0.10529 | -0.1236 | -0.25177 | 8.2581 | 8.2214 | 7.4387 | 0.15106 | -0.045776 | 122.7036 | -0.29755 | -0.059509 | -122.7081 | 0.086975 | 8.4503 | -114.3631 | -0.10528 | 0.11902 | 0.14648 | 0.34332 | 0.14648 | 8.4137 | 0.068665 | 0.086975 | 122.8958 | 7.6309 | -0.10528 | 0.068665 | 0.086975 | 7.6309 | 8.4137 | 122.8958 | -122.8363 | -122.8821
1332.0312 | 122.8455 | -0.20142 | 122.6166 | -0.038147 | 0.0081178 | 0.01944 | 0.029907 | 0.056396 | 0.057892 | 0.1568 | -0.11444 | -0.15564 | -0.2243 | 8.1161 | 8.0933 | 7.37 | 0.13733 | -0.004578 | 122.6715 | -0.27924 | -0.022888 | -122.7722 | 0.086975 | 8.3176 | -114.5233 | -0.07782 | 0.054932 | 0.10986 | 0.33875 | 0.19684 | 8.2947 | 0.045776 | 0.086975 | 122.8729 | 7.5714 | -0.07782 | 0.045776 | 0.086975 | 7.5714 | 8.2947 | 122.8729 | -122.8409 | -122.8958
1332.9688 | 122.8455 | -0.22888 | 122.6303 | 0.022888 | 0.010681 | 0.019013 | 0.033539 | 0.058533 | 0.061096 | 0.15253 | -0.16022 | -0.10529 | -0.24719 | 7.9605 | 7.9056 | 7.196 | 0.19226 | -0.07782 | 122.7127 | -0.31128 | -0.01831 | -122.7356 | 0.068665 | 8.1894 | -114.7247 | -0.082397 | 0.082398 | 0.086975 | 0.42114 | 0.15106 | 8.1345 | 0.1236 | 0.068665 | 122.9416 | 7.4249 | -0.082397 | 0.1236 | 0.068665 | 7.4249 | 8.1345 | 122.9416 | -122.8775 | -122.9416
1333.9688 | 122.8455 | -0.2243 | 122.6395 | 0.10681 | 0.011322 | 0.021576 | 0.034393 | 0.058533 | 0.058533 | 0.15402 | -0.14191 | -0.10071 | -0.25635 | 7.8598 | 7.8278 | 7.1228 | 0.21515 | -0.091553 | 122.6898 | -0.31586 | -0.032044 | -122.7402 | 0.082397 | 8.0841 | -114.8117 | -0.091553 | 0.050354 | 0.11444 | 0.43945 | 0.13275 | 8.0521 | 0.1236 | 0.082397 | 122.9141 | 7.3471 | -0.091553 | 0.1236 | 0.082397 | 7.3471 | 8.0521 | 122.9141 | -122.8958 | -122.9553
1334.9688 | 122.8363 | -0.21057 | 122.644 | 0.10681 | 0.011108 | 0.024567 | 0.032898 | 0.057465 | 0.058746 | 0.15488 | -0.10071 | -0.13733 | -0.25635 | 7.814 | 7.7637 | 7.0862 | 0.15564 | -0.045776 | 122.7127 | -0.3067 | -0.045777 | -122.7814 | 0.10986 | 8.0246 | -114.8804 | -0.096131 | 0.068665 | 0.15564 | 0.36621 | 0.1648 | 7.9742 | 0.073242 | 0.10986 | 122.9233 | 7.2968 | -0.096131 | 0.073242 | 0.10986 | 7.2968 | 7.9742 | 122.9233 | -122.9004 | -122.9507
1335.9688 | 122.8455 | -0.1831 | 122.6486 | 0.18311 | 0.011749 | 0.026489 | 0.03717 | 0.061096 | 0.058319 | 0.1553 | -0.086975 | -0.068665 | -0.16479 | 7.7362 | 7.6859 | 7.0038 | 0.14191 | -0.045776 | 122.731 | -0.27466 | 0.01831 | -122.7173 | 0.09613 | 7.9193 | -114.9628 | -0.091553 | 0.082397 | 0.07782 | 0.32501 | 0.13733 | 7.869 | 0.11444 | 0.09613 | 122.9141 | 7.1869 | -0.091553 | 0.11444 | 0.09613 | 7.1869 | 7.869 | 122.9141 | -122.8134 | -122.9233
1336.9688 | 122.85 | -0.16937 | 122.6395 | 0.11444 | 0.012177 | 0.027985 | 0.034607 | 0.058319 | 0.059601 | 0.15573 | 0.022888 | -0.07782 | -0.1831 | 7.7087 | 7.6584 | 6.9443 | 0.1831 | -0.032043 | 122.7219 | -0.26093 | -0.013732 | -122.7173 | 0.19226 | 7.8781 | -114.9811 | -0.091552 | 0.082398 | 0.20599 | 0.35248 | 0.13733 | 7.8278 | 0.091553 | 0.19226 | 122.8912 | 7.1136 | -0.091552 | 0.091553 | 0.19226 | 7.1136 | 7.8278 | 122.8912 | -122.8226 | -122.9004
1337.9688 | 122.8683 | -0.14191 | 122.6486 | 0.18311 | 0.011749 | 0.020721 | 0.037598 | 0.057892 | 0.058319 | 0.15488 | -0.086975 | -0.09613 | -0.24261 | 7.6263 | 7.608 | 6.9717 | 0.21515 | -0.013733 | 122.7631 | -0.22888 | -0.10071 | -122.7448 | 0.054932 | 7.7683 | -115.0406 | -0.086975 | 0.11444 | 0.15564 | 0.35706 | 0.12817 | 7.7499 | 0.045777 | 0.054932 | 122.905 | 7.1136 | -0.086975 | 0.045777 | 0.054932 | 7.1136 | 7.7499 | 122.905 | -122.8912 | -122.8775
1338.9688 | 122.8271 | -0.11902 | 122.6761 | 0.17548 | 0.011963 | 0.023926 | 0.032898 | 0.059387 | 0.059174 | 0.15659 | -0.10529 | -0.09613 | -0.23346 | 7.7408 | 7.6218 | 6.9901 | 0.28839 | 0.004578 | 122.8043 | -0.22888 | -0.11444 | -122.7722 | 0.013733 | 7.8598 | -115.0543 | -0.10986 | 0.12817 | 0.12817 | 0.40741 | 0.1236 | 7.7408 | 0.022889 | 0.013733 | 122.9233 | 7.1091 | -0.10986 | 0.022889 | 0.013733 | 7.1091 | 7.7408 | 122.9233 | -122.9095 | -122.905
1339.9688 | 122.8134 | -0.16022 | 122.7631 | 0.12207 | 0.01004 | 0.02243 | 0.03418 | 0.060242 | 0.060028 | 0.1568 | -0.09613 | -0.10529 | -0.2243 | 7.489 | 7.4615 | 6.8436 | 0.17395 | -0.041199 | 122.6944 | -0.30212 | -0.064087 | -122.8683 | 0.064087 | 7.6492 | -115.3015 | -0.14191 | -0.068665 | 0.12817 | 0.33417 | 0.11902 | 7.6218 | 0.054931 | 0.064087 | 122.8546 | 7.0038 | -0.14191 | 0.054931 | 0.064087 | 7.0038 | 7.6218 | 122.8546 | -122.9874 | -123.0652
1340.9688 | 122.8546 | -0.21057 | 122.6212 | -0.022889 | 0.011749 | 0.023499 | 0.034393 | 0.057678 | 0.057678 | 0.15594 | -0.15564 | -0.09613 | -0.26093 | 7.4341 | 7.4112 | 6.7886 | 0.23346 | -0.059509 | 122.7127 | -0.29755 | -0.050354 | -122.7173 | 0.054931 | 7.6447 | -115.21 | -0.086975 | 0.091553 | 0.10529 | 0.44403 | 0.15106 | 7.6218 | 0.11444 | 0.054931 | 122.9233 | 6.9992 | -0.086975 | 0.11444 | 0.054931 | 6.9992 | 7.6218 | 122.9233 | -122.8821 | -122.9187
1341.9688 | 122.8317 | -0.19684 | 122.6074 | 0.091552 | 0.012177 | 0.02179 | 0.033325 | 0.060455 | 0.060883 | 0.15552 | -0.10529 | -0.09613 | -0.24261 | 7.4615 | 7.4432 | 6.8344 | 0.21515 | -0.045776 | 122.7081 | -0.30212 | -0.045777 | -122.7036 | 0.091552 | 7.6584 | -115.1642 | -0.10529 | 0.10071 | 0.13733 | 0.41199 | 0.15106 | 7.6401 | 0.10071 | 0.091552 | 122.905 | 7.0312 | -0.10529 | 0.10071 | 0.091552 | 7.0312 | 7.6401 | 122.905 | -122.85 | -122.9095
1342.9688 | 122.8455 | -0.18768 | 122.6486 | 0.16785 | 0.015167 | 0.02478 | 0.032898 | 0.06131 | 0.060028 | 0.15659 | -0.009155 | -0.064087 | -0.16479 | 7.489 | 7.4295 | 6.8344 | 0.21973 | -0.036621 | 122.7493 | -0.27008 | 0.022888 | -122.7127 | 0.17853 | 7.6767 | -115.2191 | -0.082398 | 0.10071 | 0.15564 | 0.40741 | 0.15106 | 7.6172 | 0.1236 | 0.17853 | 122.937 | 7.0221 | -0.082398 | 0.1236 | 0.17853 | 7.0221 | 7.6172 | 122.937 | -122.8134 | -122.9187
1344.3125 | 122.9141 | -0.14191 | 122.6303 | 0.12207 | 0.008545 | 0.020508 | 0.025208 | 0.058533 | 0.059601 | 0.15637 | -0.11444 | -0.15106 | -0.19684 | 7.457 | 7.4524 | 6.8802 | 0.19226 | 0.045776 | 122.7081 | -0.26093 | -0.054931 | -122.7814 | 0.027466 | 7.5989 | -115.1779 | -0.11902 | 0.07782 | 0.082397 | 0.33417 | 0.18768 | 7.5943 | -0.009155 | 0.027466 | 122.85 | 7.0221 | -0.11902 | -0.009155 | 0.027466 | 7.0221 | 7.5943 | 122.85 | -122.8271 | -122.8912
1345.0469 | 122.937 | -0.15564 | 122.6166 | 0.42725 | 0.008545 | 0.025635 | 0.032257 | 0.055328 | 0.060455 | 0.15509 | -0.064087 | -0.13733 | -0.20599 | 7.4661 | 7.4387 | 6.8619 | 0.11444 | 0.009155 | 122.6624 | -0.26093 | -0.050354 | -122.7539 | 0.091553 | 7.6218 | -115.1779 | -0.10529 | 0.045777 | 0.14191 | 0.27008 | 0.16479 | 7.5943 | 0.018311 | 0.091553 | 122.818 | 7.0175 | -0.10529 | 0.018311 | 0.091553 | 7.0175 | 7.5943 | 122.818 | -122.8226 | -122.8775
1345.9688 | 122.8455 | -0.17853 | 122.6349 | 0.1297 | 0.0098268 | 0.024139 | 0.03717 | 0.058105 | 0.060669 | 0.15488 | -0.10071 | -0.11444 | -0.21973 | 7.4478 | 7.3883 | 6.7978 | 0.27466 | -0.032043 | 122.6898 | -0.3067 | -0.041199 | -122.7493 | 0.07782 | 7.6263 | -115.2466 | -0.12817 | 0.054931 | 0.11902 | 0.45319 | 0.14648 | 7.5668 | 0.064087 | 0.07782 | 122.8683 | 6.9763 | -0.12817 | 0.064087 | 0.07782 | 6.9763 | 7.5668 | 122.8683 | -122.8546 | -122.9416
1346.9688 | 122.8455 | -0.18768 | 122.612 | 0.091552 | 0.012604 | 0.023499 | 0.035889 | 0.057251 | 0.057678 | 0.15466 | -0.10529 | -0.1236 | -0.25177 | 7.4707 | 7.4066 | 6.8298 | 0.30212 | -0.036621 | 122.7173 | -0.29297 | -0.064087 | -122.7356 | 0.082397 | 7.6584 | -115.2054 | -0.10529 | 0.10529 | 0.14648 | 0.48981 | 0.15106 | 7.5943 | 0.064087 | 0.082397 | 122.905 | 7.0175 | -0.10529 | 0.064087 | 0.082397 | 7.0175 | 7.5943 | 122.905 | -122.8638 | -122.905
1347.9688 | 122.8134 | -0.20142 | 122.6486 | 0.022888 | 0.013031 | 0.021362 | 0.03183 | 0.059601 | 0.060883 | 0.15381 | -0.16022 | -0.091553 | -0.24261 | 7.3563 | 7.3105 | 6.7337 | 0.35706 | -0.073242 | 122.7264 | -0.29755 | -0.041199 | -122.7402 | 0.041199 | 7.5577 | -115.3381 | -0.09613 | 0.077819 | 0.082398 | 0.55847 | 0.12817 | 7.5119 | 0.10986 | 0.041199 | 122.9279 | 6.9351 | -0.09613 | 0.10986 | 0.041199 | 6.9351 | 7.5119 | 122.9279 | -122.8912 | -122.9462
1348.9688 | 122.8363 | -0.21057 | 122.6532 | 0.015259 | 0.010254 | 0.020081 | 0.033325 | 0.059814 | 0.057892 | 0.15402 | -0.13733 | -0.11444 | -0.23804 | 7.3929 | 7.3608 | 6.7749 | 0.29755 | -0.045776 | 122.7402 | -0.30212 | -0.027466 | -122.7676 | 0.073242 | 7.6035 | -115.2924 | -0.091553 | 0.086975 | 0.10071 | 0.50812 | 0.1648 | 7.5714 | 0.09613 | 0.073242 | 122.9507 | 6.9855 | -0.091553 | 0.09613 | 0.073242 | 6.9855 | 7.5714 | 122.9507 | -122.8912 | -122.9553
1349.9844 | 122.8363 | -0.2243 | 122.6212 | 0.36621 | 0.010895 | 0.022003 | 0.03183 | 0.06131 | 0.058533 | 0.15445 | -0.16022 | -0.11444 | -0.24719 | 7.3837 | 7.3517 | 6.7978 | 0.27008 | -0.11444 | 122.7264 | -0.30212 | -0.022888 | -122.7356 | 0.064087 | 7.608 | -115.2695 | -0.07782 | 0.10528 | 0.086975 | 0.49439 | 0.10986 | 7.576 | 0.10986 | 0.064087 | 122.9507 | 7.0221 | -0.07782 | 0.10986 | 0.064087 | 7.0221 | 7.576 | 122.9507 | -122.8683 | -122.9233
1351.0469 | 122.8088 | -0.22888 | 122.6349 | -0.038147 | 0.013458 | 0.020508 | 0.030762 | 0.058746 | 0.057892 | 0.15594 | -0.16479 | -0.086975 | -0.24719 | 7.4203 | 7.3975 | 6.8298 | 0.41657 | -0.082397 | 122.7264 | -0.3067 | -0.01831 | -122.7219 | 0.064087 | 7.6492 | -115.2374 | -0.07782 | 0.091552 | 0.082397 | 0.64545 | 0.14649 | 7.6263 | 0.14191 | 0.064087 | 122.9553 | 7.0587 | -0.07782 | 0.14191 | 0.064087 | 7.0587 | 7.6263 | 122.9553 | -122.8821 | -122.9416
1351.9688 | 122.8455 | -0.19684 | 122.6166 | 0.1297 | 0.010681 | 0.023926 | 0.035461 | 0.058533 | 0.061096 | 0.15402 | -0.10986 | -0.13275 | -0.23804 | 7.576 | 7.5165 | 6.9443 | 0.41199 | -0.036621 | 122.7356 | -0.31128 | -0.041199 | -122.7493 | 0.086975 | 7.7728 | -115.1001 | -0.11444 | 0.11902 | 0.12817 | 0.60882 | 0.16022 | 7.7133 | 0.064087 | 0.086975 | 122.9324 | 7.1411 | -0.11444 | 0.064087 | 0.086975 | 7.1411 | 7.7133 | 122.9324 | -122.8546 | -122.9279
1352.9688 | 122.8409 | -0.19226 | 122.644 | 0.038147 | 0.012177 | 0.021362 | 0.033966 | 0.059174 | 0.059387 | 0.15573 | -0.11902 | -0.11902 | -0.24261 | 7.6447 | 7.6309 | 7.0633 | 0.51727 | -0.045776 | 122.7356 | -0.3067 | -0.050354 | -122.7631 | 0.073242 | 7.8369 | -115.0131 | -0.11444 | 0.091553 | 0.1236 | 0.70953 | 0.14648 | 7.8232 | 0.073242 | 0.073242 | 122.9279 | 7.2556 | -0.11444 | 0.073242 | 0.073242 | 7.2556 | 7.8232 | 122.9279 | -122.8867 | -122.9507
1353.9688 | 122.8363 | -0.21057 | 122.6349 | 0.045776 | 0.011108 | 0.023499 | 0.032044 | 0.058746 | 0.057892 | 0.15723 | -0.14191 | -0.10986 | -0.24261 | 7.7087 | 7.6767 | 7.0953 | 0.55389 | -0.050354 | 122.7219 | -0.3067 | -0.032044 | -122.7448 | 0.068664 | 7.9193 | -114.9582 | -0.096131 | 0.086975 | 0.10071 | 0.76446 | 0.16022 | 7.8873 | 0.10071 | 0.068664 | 122.9324 | 7.3059 | -0.096131 | 0.10071 | 0.068664 | 7.3059 | 7.8873 | 122.9324 | -122.8775 | -122.9416
1354.9844 | 122.7997 | -0.21057 | 122.6257 | 0.39673 | 0.011322 | 0.023712 | 0.033966 | 0.064514 | 0.060455 | 0.15338 | -0.16479 | -0.11902 | -0.24719 | 7.8186 | 7.6355 | 7.0084 | 0.54932 | -0.15106 | 122.7585 | -0.28381 | -0.036621 | -122.7448 | 0.045776 | 8.0292 | -114.9902 | -0.073242 | 0.13275 | 0.082397 | 0.75989 | 0.059509 | 7.8461 | 0.091552 | 0.045776 | 122.9691 | 7.2189 | -0.073242 | 0.091552 | 0.045776 | 7.2189 | 7.8461 | 122.9691 | -122.8729 | -122.9095
1355.9688 | 122.8409 | -0.2243 | 122.6257 | 0.045776 | 0.0083314 | 0.023499 | 0.033539 | 0.058319 | 0.058105 | 0.15466 | -0.15564 | -0.10071 | -0.24261 | 7.8598 | 7.8369 | 7.251 | 0.56763 | -0.07782 | 122.7219 | -0.31128 | -0.018311 | -122.7264 | 0.068664 | 8.0841 | -114.7888 | -0.086975 | 0.096131 | 0.086975 | 0.79193 | 0.14648 | 8.0612 | 0.1236 | 0.068664 | 122.9462 | 7.4753 | -0.086975 | 0.1236 | 0.068664 | 7.4753 | 8.0612 | 122.9462 | -122.8683 | -122.937
1356.9688 | 122.8409 | -0.18768 | 122.6303 | 0.13733 | 0.011536 | 0.022217 | 0.034393 | 0.059814 | 0.061096 | 0.15295 | -0.10529 | -0.10529 | -0.24719 | 8.0338 | 7.9971 | 7.3883 | 0.50354 | -0.022888 | 122.7356 | -0.28839 | -0.059509 | -122.7356 | 0.082397 | 8.2214 | -114.6332 | -0.10071 | 0.10529 | 0.14191 | 0.69122 | 0.16479 | 8.1848 | 0.082397 | 0.082397 | 122.9233 | 7.576 | -0.10071 | 0.082397 | 0.082397 | 7.576 | 8.1848 | 122.9233 | -122.8775 | -122.9187
1357.9688 | 122.8638 | -0.19684 | 122.6486 | 0.045776 | 0.01239 | 0.023926 | 0.032257 | 0.057678 | 0.057251 | 0.15146 | -0.10071 | -0.11444 | -0.2243 | 10.4828 | 10.4279 | 9.819 | 3.2593 | -0.045776 | 122.7264 | -0.30212 | -0.027466 | -122.7631 | 0.09613 | 10.6796 | -112.2208 | -0.10529 | 0.077819 | 0.1236 | 3.4561 | 0.15106 | 10.6247 | 0.082397 | 0.09613 | 122.9233 | 10.0159 | -0.10529 | 0.082397 | 0.09613 | 10.0159 | 10.6247 | 122.9233 | -122.8729 | -122.9507
1358.9688 | 122.8546 | -0.19684 | 122.6486 | 0.053405 | 0.01239 | 0.020508 | 0.033539 | 0.061096 | 0.060669 | 0.15445 | -0.10986 | -0.10986 | -0.25177 | 7.5531 | 7.5119 | 6.958 | 0.28839 | -0.045776 | 122.731 | -0.3067 | -0.054932 | -122.7585 | 0.086975 | 7.7499 | -115.1367 | -0.10986 | 0.082397 | 0.14191 | 0.48523 | 0.15106 | 7.7087 | 0.086975 | 0.086975 | 122.9279 | 7.1548 | -0.10986 | 0.086975 | 0.086975 | 7.1548 | 7.7087 | 122.9279 | -122.9004 | -122.9553
1359.9688 | 122.8546 | -0.19684 | 122.6166 | 0.038147 | 0.010254 | 0.023499 | 0.032044 | 0.05896 | 0.059387 | 0.15573 | -0.10986 | -0.11444 | -0.23804 | 7.5211 | 7.4707 | 6.926 | 0.2655 | -0.027466 | 122.7539 | -0.3067 | -0.041199 | -122.731 | 0.086975 | 7.7179 | -115.1459 | -0.10986 | 0.13733 | 0.12817 | 0.46234 | 0.16937 | 7.6675 | 0.082397 | 0.086975 | 122.9507 | 7.1228 | -0.10986 | 0.082397 | 0.086975 | 7.1228 | 7.6675 | 122.9507 | -122.8546 | -122.9233
1360.9688 | 122.8409 | -0.1831 | 122.6349 | 0.038147 | 0.012177 | 0.023285 | 0.034393 | 0.060242 | 0.060028 | 0.15338 | -0.12817 | -0.11444 | -0.25177 | 7.6035 | 7.5851 | 7.0312 | 0.31128 | -0.027466 | 122.7264 | -0.31586 | -0.068665 | -122.7493 | 0.054931 | 7.7866 | -115.0497 | -0.13275 | 0.091552 | 0.1236 | 0.49438 | 0.15564 | 7.7682 | 0.068664 | 0.054931 | 122.9095 | 7.2144 | -0.13275 | 0.068664 | 0.054931 | 7.2144 | 7.7682 | 122.9095 | -122.8867 | -122.9507
1361.9688 | 122.8226 | -0.22888 | 122.6349 | -0.0076295 | 0.012604 | 0.014954 | 0.032257 | 0.056824 | 0.059814 | 0.15659 | -0.14191 | -0.091553 | -0.25635 | 7.6538 | 7.6263 | 7.0816 | 0.43945 | -0.082397 | 122.7402 | -0.30212 | -0.027466 | -122.7264 | 0.086975 | 7.8827 | -115.0085 | -0.073242 | 0.10528 | 0.11444 | 0.66834 | 0.14649 | 7.8552 | 0.13733 | 0.086975 | 122.9691 | 7.3105 | -0.073242 | 0.13733 | 0.086975 | 7.3105 | 7.8552 | 122.9691 | -122.8912 | -122.937
1362.9688 | 122.8546 | -0.20142 | 122.6303 | 0.030518 | 0.009613 | 0.01944 | 0.033325 | 0.057892 | 0.06131 | 0.15488 | -0.11902 | -0.11444 | -0.25177 | 7.8232 | 7.782 | 7.2189 | 0.41199 | -0.032043 | 122.7127 | -0.29755 | -0.050354 | -122.7448 | 0.082397 | 8.0246 | -114.8483 | -0.09613 | 0.082398 | 0.13275 | 0.6134 | 0.16937 | 7.9834 | 0.086975 | 0.082397 | 122.9141 | 7.4203 | -0.09613 | 0.086975 | 0.082397 | 7.4203 | 7.9834 | 122.9141 | -122.8821 | -122.9279
1363.9688 | 122.8638 | -0.15564 | 122.6624 | 0.16785 | 0.011749 | 0.019867 | 0.032257 | 0.057678 | 0.058319 | 0.15424 | -0.091553 | -0.10986 | -0.23804 | 8.0933 | 8.0292 | 7.4661 | 0.5722 | -0.018311 | 122.7676 | -0.25177 | -0.082397 | -122.7722 | 0.064087 | 8.2489 | -114.6332 | -0.09613 | 0.10529 | 0.14648 | 0.72784 | 0.13733 | 8.1848 | 0.045777 | 0.064087 | 122.9233 | 7.6218 | -0.09613 | 0.045777 | 0.064087 | 7.6218 | 8.1848 | 122.9233 | -122.9004 | -122.9141
1364.9688 | 122.8455 | -0.15106 | 122.6624 | 0.083923 | 0.011322 | 0.023712 | 0.035034 | 0.058319 | 0.058533 | 0.15146 | -0.091553 | -0.10071 | -0.2243 | 10.6796 | 10.5881 | 10.0525 | 2.9846 | -0.009155 | 122.7539 | -0.26093 | -0.073242 | -122.7631 | 0.059509 | 10.8307 | -112.0743 | -0.10986 | 0.091552 | 0.13275 | 3.1357 | 0.14191 | 10.7391 | 0.050354 | 0.059509 | 122.905 | 10.2036 | -0.10986 | 0.050354 | 0.059509 | 10.2036 | 10.7391 | 122.905 | -122.8867 | -122.9233
1365.9688 | 122.8683 | -0.15106 | 122.6395 | 0.15259 | 0.012177 | 0.02478 | 0.033966 | 0.058319 | 0.057465 | 0.15125 | -0.013733 | -0.091553 | -0.17395 | 10.7986 | 10.7483 | 9.8923 | 0.21515 | -0.032043 | 122.7539 | -0.26093 | -0.022888 | -122.731 | 0.13733 | 10.9497 | -111.8912 | -0.10986 | 0.11444 | 0.16022 | 0.36621 | 0.11902 | 10.8994 | 0.059509 | 0.13733 | 122.905 | 10.0433 | -0.10986 | 0.059509 | 0.13733 | 10.0433 | 10.8994 | 122.905 | -122.8134 | -122.9004
1366.9688 | 122.8546 | -0.17853 | 122.6349 | 2.2812 | 0.010254 | 0.01944 | 0.035675 | 0.060242 | 0.058319 | 0.15402 | 0 | -0.045776 | -0.15564 | 8.8715 | 8.8303 | 8.1573 | 0.17395 | -0.050354 | 122.7448 | -0.27008 | 0.022888 | -122.6807 | 0.17853 | 9.05 | -113.8046 | -0.091553 | 0.10986 | 0.15564 | 0.35248 | 0.12817 | 9.0088 | 0.13275 | 0.17853 | 122.9233 | 8.3359 | -0.091553 | 0.13275 | 0.17853 | 8.3359 | 9.0088 | 122.9233 | -122.7905 | -122.905
1367.9688 | 122.85 | -0.21057 | 122.6578 | 0.099182 | 0.011322 | 0.020508 | 0.032898 | 0.05896 | 0.057678 | 0.15189 | -0.10529 | -0.11902 | -0.24719 | 8.606 | 8.5693 | 7.9239 | 0.17853 | -0.054932 | 122.7264 | -0.3067 | -0.036621 | -122.7768 | 0.10529 | 8.8165 | -114.0884 | -0.096131 | 0.068664 | 0.14191 | 0.3891 | 0.15564 | 8.7799 | 0.091552 | 0.10529 | 122.937 | 8.1345 | -0.096131 | 0.091552 | 0.10529 | 8.1345 | 8.7799 | 122.937 | -122.905 | -122.9645
1368.9688 | 122.8409 | -0.19226 | 122.6212 | 0.083923 | 0.010895 | 0.026489 | 0.032471 | 0.058105 | 0.058105 | 0.15381 | -0.11444 | -0.091553 | -0.24261 | 8.5785 | 8.5281 | 7.901 | 0.1831 | -0.027466 | 122.7173 | -0.29755 | -0.050354 | -122.7127 | 0.07782 | 8.7708 | -114.093 | -0.10528 | 0.09613 | 0.12817 | 0.37537 | 0.16479 | 8.7204 | 0.10071 | 0.07782 | 122.9095 | 8.0933 | -0.10528 | 0.10071 | 0.07782 | 8.0933 | 8.7204 | 122.9095 | -122.8638 | -122.9187
1369.9688 | 122.8546 | -0.19226 | 122.6349 | 0.18311 | 0.010681 | 0.023712 | 0.033539 | 0.059814 | 0.058105 | 0.15552 | -0.07782 | -0.059509 | -0.16937 | 8.5785 | 8.551 | 7.9147 | 0.17853 | -0.036621 | 122.7585 | -0.3067 | 0.022888 | -122.6944 | 0.11444 | 8.7708 | -114.0839 | -0.11444 | 0.1236 | 0.091553 | 0.37079 | 0.15564 | 8.7433 | 0.13275 | 0.11444 | 122.9507 | 8.107 | -0.11444 | 0.13275 | 0.11444 | 8.107 | 8.7433 | 122.9507 | -122.8043 | -122.9416
1370.9688 | 122.8226 | -0.20599 | 122.612 | 0.25177 | 0.011108 | 0.022217 | 0.03418 | 0.059174 | 0.060883 | 0.15424 | -0.14191 | -0.10986 | -0.22888 | 8.5236 | 8.4915 | 7.8186 | 0.25635 | -0.10529 | 122.699 | -0.32501 | -0.022888 | -122.7219 | 0.064087 | 8.7296 | -114.1205 | -0.11902 | 0.086975 | 0.086975 | 0.46234 | 0.10071 | 8.6975 | 0.096131 | 0.064087 | 122.905 | 8.0246 | -0.11902 | 0.096131 | 0.064087 | 8.0246 | 8.6975 | 122.905 | -122.8409 | -122.937
1371.9688 | 122.8043 | -0.21973 | 122.644 | 0.22888 | 0.011322 | 0.022003 | 0.03418 | 0.060242 | 0.059814 | 0.15359 | -0.13275 | -0.10529 | -0.24261 | 8.4686 | 8.4183 | 7.7499 | 0.27008 | -0.11444 | 122.7081 | -0.33875 | -0.022888 | -122.7493 | 0.086976 | 8.6884 | -114.2258 | -0.11902 | 0.064087 | 0.10986 | 0.48981 | 0.10529 | 8.638 | 0.11444 | 0.086976 | 122.9279 | 7.9697 | -0.11902 | 0.11444 | 0.086976 | 7.9697 | 8.638 | 122.9279 | -122.8867 | -122.9828
1372.9688 | 122.7905 | -0.23346 | 122.6303 | 0.27466 | 0.011749 | 0.024994 | 0.033539 | 0.058533 | 0.058533 | 0.15509 | -0.16479 | -0.11902 | -0.23804 | 8.4412 | 8.4045 | 7.7545 | 0.27008 | -0.11902 | 122.7448 | -0.32501 | -0.004578 | -122.7493 | 0.068664 | 8.6746 | -114.2258 | -0.091553 | 0.11444 | 0.073242 | 0.50354 | 0.11444 | 8.638 | 0.11444 | 0.068664 | 122.9782 | 7.988 | -0.091553 | 0.11444 | 0.068664 | 7.988 | 8.638 | 122.9782 | -122.8683 | -122.9553
1373.9688 | 122.7951 | -0.22888 | 122.6395 | 0.23651 | 0.010254 | 0.021362 | 0.034821 | 0.060455 | 0.059387 | 0.15466 | -0.14648 | -0.10529 | -0.25635 | 8.4732 | 8.4503 | 7.8323 | 0.29755 | -0.10986 | 122.7539 | -0.32501 | -0.027466 | -122.7448 | 0.082398 | 8.7021 | -114.1891 | -0.09613 | 0.11444 | 0.10986 | 0.52643 | 0.11902 | 8.6792 | 0.1236 | 0.082398 | 122.9828 | 8.0612 | -0.09613 | 0.1236 | 0.082398 | 8.0612 | 8.6792 | 122.9828 | -122.8958 | -122.9645
1374.9688 | 122.8134 | -0.19226 | 122.6257 | 0.21362 | 0.010681 | 0.026703 | 0.033753 | 0.059814 | 0.061096 | 0.15338 | -0.11444 | -0.10986 | -0.23346 | 8.551 | 8.5052 | 7.8964 | 0.28381 | -0.073242 | 122.731 | -0.3067 | -0.041198 | -122.7356 | 0.07782 | 8.7433 | -114.1205 | -0.11444 | 0.10529 | 0.11902 | 0.47607 | 0.11902 | 8.6975 | 0.082398 | 0.07782 | 122.9233 | 8.0887 | -0.11444 | 0.082398 | 0.07782 | 8.0887 | 8.6975 | 122.9233 | -122.8592 | -122.9324
1375.9688 | 122.818 | -0.21057 | 122.6074 | 0.19836 | 0.013458 | 0.025421 | 0.035034 | 0.060455 | 0.059814 | 0.15509 | -0.11444 | -0.10529 | -0.24261 | 8.4778 | 8.4457 | 7.8323 | 0.2243 | -0.09613 | 122.6944 | -0.3067 | -0.032044 | -122.7127 | 0.09613 | 8.6884 | -114.1617 | -0.096131 | 0.086975 | 0.12817 | 0.43488 | 0.11444 | 8.6563 | 0.10529 | 0.09613 | 122.905 | 8.0429 | -0.096131 | 0.10529 | 0.09613 | 8.0429 | 8.6563 | 122.905 | -122.85 | -122.9141
1376.9688 | 122.8134 | -0.20599 | 122.6349 | 0.26703 | 0.012604 | 0.023712 | 0.034393 | 0.061096 | 0.056824 | 0.15402 | -0.17395 | -0.10071 | -0.24719 | 8.4549 | 8.4366 | 7.814 | 0.25635 | -0.13733 | 122.7264 | -0.3067 | -0.041198 | -122.7356 | 0.032044 | 8.6609 | -114.1983 | -0.10071 | 0.091552 | 0.073242 | 0.46234 | 0.068665 | 8.6426 | 0.10529 | 0.032044 | 122.9324 | 8.02 | -0.10071 | 0.10529 | 0.032044 | 8.02 | 8.6426 | 122.9324 | -122.8821 | -122.9416
1377.9688 | 122.8271 | -0.21973 | 122.6257 | 0.061035 | 0.012604 | 0.025208 | 0.032471 | 0.060669 | 0.060883 | 0.15552 | -0.16022 | -0.091553 | -0.23804 | 8.5098 | 8.4732 | 7.8918 | 0.2655 | -0.12817 | 122.7676 | -0.3067 | -0.01831 | -122.7173 | 0.05951 | 8.7296 | -114.1525 | -0.086975 | 0.14191 | 0.07782 | 0.48523 | 0.091553 | 8.6929 | 0.12817 | 0.05951 | 122.9874 | 8.1116 | -0.086975 | 0.12817 | 0.05951 | 8.1116 | 8.6929 | 122.9874 | -122.8638 | -122.9324
1378.9688 | 122.8271 | -0.20599 | 122.6349 | 0.5188 | 0.011108 | 0.022644 | 0.033112 | 0.059387 | 0.058746 | 0.15552 | -0.15106 | -0.09613 | -0.24719 | 8.5327 | 8.5281 | 7.9239 | 0.23804 | -0.1236 | 122.7448 | -0.31586 | -0.041198 | -122.731 | 0.054932 | 8.7387 | -114.1068 | -0.10986 | 0.10986 | 0.09613 | 0.44403 | 0.082398 | 8.7341 | 0.10986 | 0.054932 | 122.9507 | 8.1299 | -0.10986 | 0.10986 | 0.054932 | 8.1299 | 8.7341 | 122.9507 | -122.8821 | -122.9507
1379.9688 | 122.818 | -0.20599 | 122.644 | 0.33569 | 0.010681 | 0.020508 | 0.031189 | 0.058746 | 0.06131 | 0.15253 | -0.16022 | -0.10529 | -0.24261 | 8.6563 | 8.6334 | 8.0429 | 0.21973 | -0.11902 | 122.7448 | -0.31586 | -0.036621 | -122.7493 | 0.045777 | 8.8623 | -114.0106 | -0.10986 | 0.10071 | 0.082398 | 0.42572 | 0.086975 | 8.8394 | 0.10071 | 0.045777 | 122.9507 | 8.2489 | -0.10986 | 0.10071 | 0.045777 | 8.2489 | 8.8394 | 122.9507 | -122.8867 | -122.9599
1380.9688 | 122.8088 | -0.22888 | 122.6624 | 0.41962 | 0.011963 | 0.026489 | 0.033753 | 0.059174 | 0.061523 | 0.15424 | -0.17395 | -0.10529 | -0.23346 | 9.0088 | 8.963 | 8.345 | 0.21973 | -0.11902 | 122.7081 | -0.32044 | -0.004577 | -122.7676 | 0.054932 | 9.2377 | -113.6993 | -0.091553 | 0.045776 | 0.059509 | 0.44861 | 0.10986 | 9.1919 | 0.1236 | 0.054932 | 122.937 | 8.5739 | -0.091553 | 0.1236 | 0.054932 | 8.5739 | 9.1919 | 122.937 | -122.8958 | -122.9828
1381.9688 | 122.7768 | -0.21515 | 122.6669 | 0.3891 | 0.011963 | 0.021149 | 0.032898 | 0.043365 | 0.045074 | 0.12369 | -0.16937 | -0.1236 | -0.25635 | 36.4151 | 37.1063 | 34.4467 | 0.16022 | -0.15106 | 122.731 | -0.31128 | -0.041199 | -122.7905 | 0.045776 | 36.6302 | -85.5606 | -0.09613 | 0.064087 | 0.086975 | 0.37537 | 0.064087 | 37.3215 | 0.091553 | 0.045776 | 122.9462 | 34.6619 | -0.09613 | 0.091553 | 0.045776 | 34.6619 | 37.3215 | 122.9462 | -122.9233 | -122.9782
1382.9688 | 122.8043 | -0.21515 | 122.6486 | 0.2594 | 0.013458 | 0.024994 | 0.033966 | 0.049988 | 0.049133 | 0.13608 | -0.16937 | -0.1236 | -0.25635 | 25.1083 | 25.0259 | 23.0713 | 0.23804 | -0.13275 | 122.7539 | -0.32501 | -0.041199 | -122.7722 | 0.045776 | 25.3235 | -97.6227 | -0.10986 | 0.10528 | 0.086975 | 0.45319 | 0.082398 | 25.2411 | 0.091553 | 0.045776 | 122.9691 | 23.2864 | -0.10986 | 0.091553 | 0.045776 | 23.2864 | 25.2411 | 122.9691 | -122.905 | -122.9736
1383.9688 | 122.8729 | -0.20599 | 122.6395 | 0.46539 | 0.012177 | 0.020508 | 0.031616 | 0.054687 | 0.053192 | 0.14569 | -0.15106 | -0.10986 | -0.25177 | 16.9785 | 16.9189 | 15.1703 | 0.23346 | -0.059509 | 122.7356 | -0.28839 | -0.045776 | -122.7493 | 0.054932 | 17.1844 | -105.7205 | -0.082397 | 0.096131 | 0.10071 | 0.43945 | 0.14649 | 17.1249 | 0.096131 | 0.054932 | 122.9416 | 15.3763 | -0.082397 | 0.096131 | 0.054932 | 15.3763 | 17.1249 | 122.9416 | -122.8912 | -122.9279
1384.9688 | 122.8592 | -0.18768 | 122.6303 | 0.3891 | 0.011536 | 0.021362 | 0.03183 | 0.036743 | 0.036743 | 0.10916 | -0.14648 | -0.11902 | -0.25177 | 48.6511 | 48.5001 | 43.2404 | 0.10986 | -0.10071 | 122.7356 | -0.31586 | -0.064087 | -122.7493 | 0.041199 | 48.8388 | -74.1302 | -0.12817 | 0.10529 | 0.10529 | 0.29755 | 0.086975 | 48.6877 | 0.068664 | 0.041199 | 122.9233 | 43.428 | -0.12817 | 0.068664 | 0.041199 | 43.428 | 48.6877 | 122.9233 | -122.8821 | -122.9462
1385.9688 | 122.8409 | -0.19684 | 122.6395 | 0.40436 | 0.013031 | 0.026489 | 0.033112 | 0.042297 | 0.042938 | 0.11877 | -0.15564 | -0.11444 | -0.24261 | 39.798 | 39.6194 | 35.1288 | 0.13275 | -0.082397 | 122.7448 | -0.31586 | -0.045777 | -122.7539 | 0.041198 | 39.9948 | -83.02 | -0.11902 | 0.10529 | 0.086975 | 0.32959 | 0.11444 | 39.8163 | 0.082397 | 0.041198 | 122.9416 | 35.3256 | -0.11902 | 0.082397 | 0.041198 | 35.3256 | 39.8163 | 122.9416 | -122.8821 | -122.9553
1386.9688 | 122.8546 | -0.18768 | 122.6578 | 0.37384 | 0.012177 | 0.019226 | 0.032898 | 0.01004 | 0.0081176 | 0.055756 | -0.16479 | -0.12817 | -0.25635 | 97.11 | 96.9177 | 87.7533 | -0.082397 | -0.11902 | 122.7219 | -0.30212 | -0.068665 | -122.7859 | 0.022888 | 97.2977 | -25.7401 | -0.11444 | 0.064087 | 0.091553 | 0.10529 | 0.068664 | 97.1054 | 0.059509 | 0.022888 | 122.9095 | 87.941 | -0.11444 | 0.059509 | 0.022888 | 87.941 | 97.1054 | 122.9095 | -122.9141 | -122.9599
1387.9688 | 122.818 | -0.21973 | 122.6349 | 0.37384 | 0.011963 | 0.025208 | 0.033753 | 0.041229 | 0.042511 | 0.11877 | -0.16937 | -0.10529 | -0.25177 | 41.1163 | 41.011 | 36.5479 | 0.19684 | -0.10071 | 122.7448 | -0.29755 | -0.032043 | -122.7402 | 0.050354 | 41.3361 | -81.6238 | -0.077819 | 0.10986 | 0.082397 | 0.41657 | 0.11902 | 41.2308 | 0.11444 | 0.050354 | 122.9645 | 36.7676 | -0.077819 | 0.11444 | 0.050354 | 36.7676 | 41.2308 | 122.9645 | -122.8867 | -122.9324
1388.9688 | 122.8363 | -0.19226 | 122.6669 | 0.35095 | 0.012177 | 0.022003 | 0.033966 | 0.030975 | 0.033112 | 0.099762 | -0.16479 | -0.091553 | -0.24719 | 58.0994 | 57.843 | 50.9491 | 0.37994 | -0.17395 | 122.7814 | -0.27924 | -0.054931 | -122.7585 | 0.027466 | 58.2916 | -64.8239 | -0.086975 | 0.11444 | 0.082397 | 0.5722 | 0.018311 | 58.0353 | 0.10071 | 0.027466 | 122.9736 | 51.1414 | -0.086975 | 0.10071 | 0.027466 | 51.1414 | 58.0353 | 122.9736 | -122.9141 | -122.9462
1389.9688 | 122.8134 | -0.18768 | 122.6669 | 0.34332 | 0.012604 | 0.027771 | 0.033966 | 0.031616 | 0.032684 | 0.099121 | -0.17395 | -0.10529 | -0.25177 | 57.0557 | 56.9595 | 49.8276 | -0.11444 | -0.21973 | 122.7768 | -0.29297 | -0.064087 | -122.7722 | 0.013733 | 57.2433 | -65.7074 | -0.10529 | 0.10986 | 0.07782 | 0.073242 | -0.032044 | 57.1472 | 0.082397 | 0.013733 | 122.9645 | 50.0153 | -0.10529 | 0.082397 | 0.013733 | 50.0153 | 57.1472 | 122.9645 | -122.9187 | -122.9599
1390.9688 | 122.937 | -0.17853 | 122.6303 | 0.39673 | 0.011963 | 0.020081 | 0.032257 | 0.0098266 | 0.011536 | 0.05426 | -0.13275 | -0.14648 | -0.24719 | 97.7875 | 97.5677 | 89.0488 | -0.15106 | -0.045776 | 122.7081 | -0.29755 | -0.068664 | -122.7768 | 0.045777 | 97.966 | -25.0626 | -0.11902 | 0.07782 | 0.11444 | 0.027466 | 0.13275 | 97.7463 | 0.032044 | 0.045777 | 122.8867 | 89.2273 | -0.11902 | 0.032044 | 0.045777 | 89.2273 | 97.7463 | 122.8867 | -122.8775 | -122.9279
1391.9688 | 122.937 | -0.19226 | 122.6028 | 0.45013 | 0.010254 | 0.023712 | 0.030975 | 0.0098266 | 0.012177 | 0.06131 | -0.13733 | -0.13275 | -0.23346 | 93.3975 | 93.2236 | 85.0754 | -0.1236 | -0.064087 | 122.7081 | -0.32501 | -0.041198 | -122.7356 | 0.054932 | 93.5898 | -29.3793 | -0.13275 | 0.10529 | 0.09613 | 0.068665 | 0.12817 | 93.4158 | 0.05951 | 0.054932 | 122.9004 | 85.2676 | -0.13275 | 0.05951 | 0.054932 | 85.2676 | 93.4158 | 122.9004 | -122.8363 | -122.9279
1392.9688 | 122.9279 | -0.16937 | 122.612 | 0.43488 | 0.010895 | 0.023712 | 0.03183 | 0.017731 | 0.015381 | 0.067078 | -0.14191 | -0.13733 | -0.24261 | 86.8195 | 86.6501 | 77.916 | -0.10071 | -0.054932 | 122.7264 | -0.30212 | -0.073242 | -122.7493 | 0.027466 | 86.9888 | -35.9619 | -0.13275 | 0.11444 | 0.10071 | 0.068665 | 0.11444 | 86.8195 | 0.032044 | 0.027466 | 122.8958 | 78.0853 | -0.13275 | 0.032044 | 0.027466 | 78.0853 | 86.8195 | 122.8958 | -122.8546 | -122.9141
1393.9688 | 122.905 | -0.17853 | 122.6166 | 0.43488 | 0.011322 | 0.023071 | 0.03418 | 0.019653 | 0.020721 | 0.081604 | -0.14191 | -0.15564 | -0.24719 | 74.1257 | 73.9655 | 67.3737 | -0.032043 | -0.064087 | 122.7402 | -0.30212 | -0.068664 | -122.7722 | 0.036621 | 74.3042 | -48.6511 | -0.1236 | 0.1236 | 0.10528 | 0.14648 | 0.11444 | 74.144 | 0.022888 | 0.036621 | 122.9187 | 67.5522 | -0.1236 | 0.022888 | 0.036621 | 67.5522 | 74.144 | 122.9187 | -122.8638 | -122.9187
1394.9688 | 122.905 | -0.20599 | 122.6257 | 0.41962 | 0.010468 | 0.025848 | 0.033753 | 0.031189 | 0.032898 | 0.098694 | -0.14648 | -0.14648 | -0.23346 | 58.9966 | 58.8684 | 52.8671 | 0.054932 | -0.068665 | 122.7356 | -0.30212 | -0.027465 | -122.7722 | 0.05951 | 59.2026 | -63.7573 | -0.09613 | 0.10986 | 0.086975 | 0.26093 | 0.13733 | 59.0744 | 0.05951 | 0.05951 | 122.9416 | 53.0731 | -0.09613 | 0.05951 | 0.05951 | 53.0731 | 59.0744 | 122.9416 | -122.8592 | -122.9279
1395.9688 | 122.8363 | -0.21057 | 122.6624 | -0.022889 | 0.011749 | 0.022858 | 0.032471 | 0.035248 | 0.03653 | 0.10596 | -0.17395 | -0.10071 | -0.26093 | 51.1139 | 50.9857 | 45.7306 | 0.20142 | -0.14648 | 122.7676 | -0.31128 | -0.050354 | -122.7631 | 0.036621 | 51.3245 | -71.6766 | -0.10071 | 0.10529 | 0.086975 | 0.41199 | 0.064087 | 51.1963 | 0.10986 | 0.036621 | 122.9782 | 45.9412 | -0.10071 | 0.10986 | 0.036621 | 45.9412 | 51.1963 | 122.9782 | -122.9233 | -122.9736
1396.9688 | 122.8226 | -0.2243 | 122.6669 | 0.42725 | 0.011749 | 0.021362 | 0.034393 | 0.025635 | 0.026062 | 0.085022 | -0.15564 | -0.11444 | -0.24719 | 70.1752 | 70.0104 | 63.9221 | 0.11902 | -0.14648 | 122.7539 | -0.32501 | -0.022888 | -122.7814 | 0.068664 | 70.3995 | -52.6566 | -0.10071 | 0.086975 | 0.091552 | 0.34332 | 0.07782 | 70.2347 | 0.10986 | 0.068664 | 122.9782 | 64.1464 | -0.10071 | 0.10986 | 0.068664 | 64.1464 | 70.2347 | 122.9782 | -122.9141 | -122.9919
1397.9688 | 122.9553 | -0.18768 | 122.5983 | 0.40436 | 0.0089722 | 0.023926 | 0.029907 | 0.033752 | 0.036102 | 0.11279 | -0.07782 | -0.15564 | -0.22888 | 47.168 | 47.0489 | 42.8055 | 0.068665 | 0.004578 | 122.7356 | -0.27466 | -0.041199 | -122.7539 | 0.10986 | 47.3557 | -75.5493 | -0.086975 | 0.13733 | 0.15106 | 0.25635 | 0.19226 | 47.2366 | 0.032043 | 0.10986 | 122.9233 | 42.9932 | -0.086975 | 0.032043 | 0.10986 | 42.9932 | 47.2366 | 122.9233 | -122.8271 | -122.8729
1398.9688 | 122.9462 | -0.14648 | 122.6303 | 0.39673 | 0.011108 | 0.022003 | 0.032044 | 0.037811 | 0.041229 | 0.11642 | -0.07782 | -0.15106 | -0.21973 | 42.1738 | 42.0547 | 38.3652 | 0.14648 | 0 | 122.7036 | -0.28839 | -0.073243 | -122.7814 | 0.068664 | 42.3203 | -80.5756 | -0.14191 | 0.073242 | 0.14191 | 0.29297 | 0.14648 | 42.2012 | -0.004578 | 0.068664 | 122.85 | 38.5117 | -0.14191 | -0.004578 | 0.068664 | 38.5117 | 42.2012 | 122.85 | -122.85 | -122.9187
1399.9688 | 122.9462 | -0.15564 | 122.6303 | 0.39673 | 0.010895 | 0.024139 | 0.034821 | 0.04187 | 0.044861 | 0.12198 | -0.07782 | -0.16479 | -0.21057 | 37.0239 | 36.9186 | 33.7463 | 0.20142 | -0.004578 | 122.7036 | -0.27466 | -0.054931 | -122.7951 | 0.07782 | 37.1796 | -85.7117 | -0.11902 | 0.073242 | 0.13275 | 0.35706 | 0.15106 | 37.0743 | -0.009155 | 0.07782 | 122.8592 | 33.902 | -0.11902 | -0.009155 | 0.07782 | 33.902 | 37.0743 | 122.8592 | -122.8409 | -122.905
1400.9688 | 122.9279 | -0.16022 | 122.6212 | 0.4425 | 0.010895 | 0.022217 | 0.03418 | 0.04422 | 0.045074 | 0.12604 | -0.068665 | -0.15106 | -0.21973 | 32.9086 | 32.7942 | 29.9149 | 0.26093 | -0.018311 | 122.6669 | -0.28381 | -0.05951 | -122.7722 | 0.091552 | 33.0688 | -89.827 | -0.1236 | 0.045776 | 0.15106 | 0.42114 | 0.14191 | 32.9544 | 0.009155 | 0.091552 | 122.8271 | 30.0751 | -0.1236 | 0.009155 | 0.091552 | 30.0751 | 32.9544 | 122.8271 | -122.8409 | -122.905
1401.9688 | 122.9553 | -0.16479 | 122.6257 | 0.42725 | 0.009613 | 0.023499 | 0.034393 | 0.040588 | 0.044647 | 0.12326 | -0.064087 | -0.15564 | -0.22888 | 35.2753 | 35.17 | 32.2266 | 0.27924 | -0.009155 | 122.6944 | -0.28839 | -0.064087 | -122.7814 | 0.10071 | 35.4401 | -87.4557 | -0.1236 | 0.068665 | 0.16479 | 0.44403 | 0.15564 | 35.3348 | 0.009155 | 0.10071 | 122.8592 | 32.3914 | -0.1236 | 0.009155 | 0.10071 | 32.3914 | 35.3348 | 122.8592 | -122.8546 | -122.9141
1402.9688 | 122.8912 | -0.20142 | 122.6212 | 0.3891 | 0.011963 | 0.02179 | 0.036102 | 0.045074 | 0.049133 | 0.12967 | -0.15106 | -0.13733 | -0.22888 | 29.4937 | 29.393 | 26.8936 | 0.47607 | -0.09613 | 122.6944 | -0.29755 | -0.027466 | -122.7585 | 0.050354 | 29.6951 | -93.2281 | -0.09613 | 0.073242 | 0.07782 | 0.67749 | 0.10529 | 29.5944 | 0.064087 | 0.050354 | 122.8958 | 27.095 | -0.09613 | 0.064087 | 0.050354 | 27.095 | 29.5944 | 122.8958 | -122.85 | -122.9187
1403.9688 | 122.8958 | -0.1831 | 122.644 | 0.41962 | 0.010895 | 0.026703 | 0.035034 | 0.045929 | 0.049133 | 0.13223 | -0.13733 | -0.12817 | -0.24719 | 27.4017 | 27.2964 | 24.9939 | 0.31586 | -0.07782 | 122.7127 | -0.31128 | -0.064087 | -122.7722 | 0.045776 | 27.5848 | -95.3476 | -0.12817 | 0.068665 | 0.10986 | 0.49896 | 0.10528 | 27.4796 | 0.054931 | 0.045776 | 122.8958 | 25.177 | -0.12817 | 0.054931 | 0.045776 | 25.177 | 27.4796 | 122.8958 | -122.8912 | -122.9553
1404.9688 | 122.937 | -0.14648 | 122.6349 | 0.3891 | 0.0087586 | 0.021576 | 0.031189 | 0.045502 | 0.050629 | 0.13437 | -0.082397 | -0.17395 | -0.21515 | 26.0056 | 25.9003 | 23.7534 | 0.32044 | 0.004578 | 122.6807 | -0.28381 | -0.068665 | -122.8088 | 0.064087 | 26.152 | -96.7346 | -0.13733 | 0.045776 | 0.13275 | 0.46692 | 0.15106 | 26.0468 | -0.027466 | 0.064087 | 122.8271 | 23.8998 | -0.13733 | -0.027466 | 0.064087 | 23.8998 | 26.0468 | 122.8271 | -122.85 | -122.9187
1405.9688 | 122.9324 | -0.16937 | 122.6303 | 0.40436 | 0.010895 | 0.023712 | 0.031189 | 0.045074 | 0.049561 | 0.13565 | -0.091553 | -0.14648 | -0.20599 | 25.5798 | 25.4929 | 23.3826 | 0.054932 | 0.018311 | 122.6852 | -0.27008 | -0.036621 | -122.7768 | 0.07782 | 25.7492 | -97.1375 | -0.10071 | 0.054932 | 0.11444 | 0.22431 | 0.18768 | 25.6622 | 0.022889 | 0.07782 | 122.8546 | 23.5519 | -0.10071 | 0.022889 | 0.07782 | 23.5519 | 25.6622 | 122.8546 | -122.8363 | -122.9004
1406.9688 | 122.9553 | -0.16937 | 122.612 | 0.35858 | 0.010681 | 0.019867 | 0.028839 | 0.046356 | 0.05127 | 0.13629 | -0.082397 | -0.16937 | -0.21515 | 24.3942 | 24.3027 | 22.2794 | 0.018311 | 0 | 122.6761 | -0.28381 | -0.045776 | -122.7814 | 0.086976 | 24.5636 | -98.3093 | -0.11444 | 0.064086 | 0.13275 | 0.18768 | 0.16937 | 24.472 | 0 | 0.086976 | 122.8455 | 22.4487 | -0.11444 | 0 | 0.086976 | 22.4487 | 24.472 | 122.8455 | -122.8271 | -122.8958
1407.9688 | 122.937 | -0.16937 | 122.6349 | 0.34332 | 0.0089722 | 0.023285 | 0.033112 | 0.046783 | 0.052338 | 0.13928 | -0.082397 | -0.16022 | -0.21057 | 22.0825 | 21.9818 | 20.2103 | -0.10071 | 0.004578 | 122.6852 | -0.28381 | -0.041198 | -122.7951 | 0.086976 | 22.2519 | -100.6531 | -0.11444 | 0.050354 | 0.12817 | 0.068665 | 0.17395 | 22.1512 | 0.009156 | 0.086976 | 122.8546 | 20.3796 | -0.11444 | 0.009156 | 0.086976 | 20.3796 | 22.1512 | 122.8546 | -122.8455 | -122.9187
1408.9688 | 122.9233 | -0.15564 | 122.6395 | 0.33569 | 0.0087586 | 0.023499 | 0.032684 | 0.04657 | 0.050629 | 0.138 | -0.07782 | -0.14648 | -0.22888 | 21.7484 | 21.6705 | 19.9448 | -0.07782 | -0.004578 | 122.6578 | -0.27466 | -0.073242 | -122.7859 | 0.07782 | 21.904 | -100.9689 | -0.11902 | 0.018311 | 0.15106 | 0.07782 | 0.15106 | 21.8262 | 0.009156 | 0.07782 | 122.8134 | 20.1004 | -0.11902 | 0.009156 | 0.07782 | 20.1004 | 21.8262 | 122.8134 | -122.8683 | -122.9141
1409.9688 | 122.9416 | -0.1831 | 122.6303 | 0.41962 | 0.010468 | 0.022217 | 0.035034 | 0.047424 | 0.052124 | 0.13886 | -0.30212 | -0.20599 | -0.25177 | 22.2153 | 22.1146 | 20.256 | -0.10529 | 0.004578 | 122.6486 | -0.3067 | -0.068665 | -122.8363 | -0.11902 | 22.3984 | -100.5157 | -0.1236 | 0.018311 | -0.050354 | 0.077819 | 0.18768 | 22.2977 | -0.022889 | -0.11902 | 122.8317 | 20.4391 | -0.1236 | -0.022889 | -0.11902 | 20.4391 | 22.2977 | 122.8317 | -122.8821 | -122.937
1410.9688 | 122.9553 | -0.19684 | 122.612 | 1.9684 | 0.008545 | 0.020508 | 0.034607 | 0.047851 | 0.050201 | 0.13907 | -0.064087 | -0.20599 | -0.24261 | 21.8353 | 21.7484 | 19.8944 | -0.11444 | -0.013733 | 122.6898 | -0.29297 | -0.045777 | -122.818 | 0.13275 | 22.0322 | -100.8636 | -0.096131 | 0.077819 | 0.17853 | 0.082397 | 0.18311 | 21.9452 | -0.009156 | 0.13275 | 122.8867 | 20.0912 | -0.096131 | -0.009156 | 0.13275 | 20.0912 | 21.9452 | 122.8867 | -122.8546 | -122.905
1411.9688 | 122.8958 | -0.17395 | 122.6486 | 0.32806 | 0.0076904 | 0.017944 | 0.029053 | 0.04657 | 0.052979 | 0.14056 | -0.13275 | -0.14648 | -0.18768 | 21.4005 | 21.3364 | 19.5236 | -0.013733 | -0.022888 | 122.6898 | -0.29297 | -0.013733 | -122.7951 | 0.041199 | 21.5744 | -101.3123 | -0.11902 | 0.041198 | 0.054932 | 0.16022 | 0.15106 | 21.5103 | 0.027466 | 0.041199 | 122.8638 | 19.6976 | -0.11902 | 0.027466 | 0.041199 | 19.6976 | 21.5103 | 122.8638 | -122.8363 | -122.9416
1412.9688 | 122.905 | -0.16937 | 122.6257 | 0.28229 | 0.008545 | 0.022003 | 0.030121 | 0.045074 | 0.052979 | 0.13757 | -0.13733 | -0.16479 | -0.21057 | 21.1945 | 21.0983 | 19.313 | 0.009155 | -0.027466 | 122.6578 | -0.27008 | -0.041198 | -122.7905 | 0.032044 | 21.3638 | -101.5274 | -0.10071 | 0.032044 | 0.073242 | 0.17853 | 0.14191 | 21.2677 | 0.004578 | 0.032044 | 122.8271 | 19.4824 | -0.10071 | 0.004578 | 0.032044 | 19.4824 | 21.2677 | 122.8271 | -122.8363 | -122.8958
1413.9688 | 123.1384 | -0.20142 | 122.5433 | 0.27466 | 0.010254 | 0.019013 | 0.030975 | 0.04657 | 0.051483 | 0.13864 | -0.14191 | -0.14191 | -0.21057 | 21.08 | 20.9976 | 19.2169 | -0.013733 | -0.041199 | 122.6761 | -0.27466 | -0.009155 | -122.6852 | 0.059509 | 21.2814 | -101.5457 | -0.073242 | 0.13275 | 0.068664 | 0.18768 | 0.16022 | 21.199 | 0.059509 | 0.059509 | 122.8775 | 19.4183 | -0.073242 | 0.059509 | 0.059509 | 19.4183 | 21.199 | 122.8775 | -122.7539 | -122.818
1414.9688 | 122.9691 | -0.21973 | 122.5342 | 0.30518 | 0.0081178 | 0.023071 | 0.031189 | 0.047211 | 0.052979 | 0.1395 | -0.13275 | -0.15106 | -0.21515 | 20.9244 | 20.8511 | 19.0659 | 0 | -0.036621 | 122.6852 | -0.27466 | 0.004578 | -122.6852 | 0.086976 | 21.1441 | -101.683 | -0.054931 | 0.15106 | 0.082398 | 0.21973 | 0.18311 | 21.0709 | 0.068665 | 0.086976 | 122.905 | 19.2856 | -0.054931 | 0.068665 | 0.086976 | 19.2856 | 21.0709 | 122.905 | -122.7493 | -122.8088
1415.9688 | 122.9279 | -0.25635 | 122.5891 | 0.30518 | 0.010681 | 0.02243 | 0.031403 | 0.045502 | 0.050842 | 0.14206 | -0.14191 | -0.15106 | -0.21057 | 20.8145 | 20.7413 | 18.9651 | -0.013733 | -0.13275 | 122.5616 | -0.32501 | 0.045777 | -122.7402 | 0.11444 | 21.0709 | -101.8478 | -0.068664 | -0.027465 | 0.068664 | 0.24262 | 0.1236 | 20.9976 | 0.10529 | 0.11444 | 122.818 | 19.2215 | -0.068664 | 0.10529 | 0.11444 | 19.2215 | 20.9976 | 122.818 | -122.7997 | -122.9141
1416.9688 | 122.8912 | -0.15564 | 122.6532 | 0.37384 | 0.010254 | 0.017517 | 0.031189 | 0.044434 | 0.053619 | 0.1395 | -0.082397 | -0.14648 | -0.2243 | 20.7092 | 20.6223 | 18.8141 | -0.041199 | -0.013733 | 122.6807 | -0.26093 | -0.068664 | -122.7997 | 0.073243 | 20.8649 | -102.0309 | -0.10529 | 0.027466 | 0.14191 | 0.11444 | 0.14191 | 20.7779 | 0.009156 | 0.073243 | 122.8363 | 18.9697 | -0.10529 | 0.009156 | 0.073243 | 18.9697 | 20.7779 | 122.8363 | -122.8775 | -122.9141
1417.9688 | 122.8958 | -0.16479 | 122.6395 | 0.35858 | 0.0089722 | 0.021576 | 0.030548 | 0.047851 | 0.053192 | 0.14035 | -0.10071 | -0.14648 | -0.21973 | 20.5261 | 20.4437 | 18.6401 | -0.027466 | -0.022888 | 122.6624 | -0.27466 | -0.054932 | -122.7859 | 0.064087 | 20.6909 | -102.1957 | -0.10986 | 0.022889 | 0.11902 | 0.13733 | 0.14191 | 20.6085 | 0.018311 | 0.064087 | 122.8271 | 18.8049 | -0.10986 | 0.018311 | 0.064087 | 18.8049 | 20.6085 | 122.8271 | -122.8592 | -122.9141
1418.9688 | 122.9416 | -0.17395 | 122.644 | 0.26703 | 0.0070496 | 0.019226 | 0.030762 | 0.045929 | 0.054474 | 0.14014 | -0.12817 | -0.15564 | -0.21973 | 20.5444 | 20.4666 | 18.6584 | 0.004578 | 0.004578 | 122.6898 | -0.2655 | -0.045777 | -122.7997 | 0.045776 | 20.7184 | -102.1774 | -0.091553 | 0.045776 | 0.091553 | 0.17853 | 0.17853 | 20.6406 | 0.01831 | 0.045776 | 122.8638 | 18.8324 | -0.091553 | 0.01831 | 0.045776 | 18.8324 | 20.6406 | 122.8638 | -122.8638 | -122.9095
1419.9688 | 122.9324 | -0.1831 | 122.6578 | 0.21362 | 0.008545 | 0.017304 | 0.032044 | 0.045502 | 0.051483 | 0.13971 | -0.15106 | -0.14191 | -0.2243 | 20.5811 | 20.5124 | 18.6813 | -0.004578 | -0.004578 | 122.6624 | -0.27924 | -0.041199 | -122.7997 | 0.032043 | 20.7642 | -102.1454 | -0.096131 | 0.004578 | 0.073242 | 0.17853 | 0.17853 | 20.6955 | 0.041198 | 0.032043 | 122.8455 | 18.8644 | -0.096131 | 0.041198 | 0.032043 | 18.8644 | 20.6955 | 122.8455 | -122.8821 | -122.937
1420.9688 | 122.9324 | -0.16937 | 122.6578 | 0.19073 | 0.0087586 | 0.020294 | 0.029907 | 0.045502 | 0.049988 | 0.14227 | -0.13733 | -0.14648 | -0.21973 | 20.6268 | 20.5536 | 18.6264 | 0.009155 | -0.013733 | 122.6578 | -0.28839 | -0.050354 | -122.8043 | 0.032044 | 20.7962 | -102.1042 | -0.11902 | 0 | 0.082398 | 0.17853 | 0.15564 | 20.723 | 0.022889 | 0.032044 | 122.8271 | 18.7958 | -0.11902 | 0.022889 | 0.032044 | 18.7958 | 20.723 | 122.8271 | -122.8775 | -122.9462
1421.9688 | 122.9004 | -0.16937 | 122.6395 | 0.21362 | 0.0079042 | 0.019013 | 0.029694 | 0.046783 | 0.05191 | 0.13907 | -0.16479 | -0.14648 | -0.21057 | 20.9747 | 20.8786 | 18.9011 | 0 | -0.013733 | 122.644 | -0.27466 | -0.041198 | -122.7859 | 0.004578 | 21.1441 | -101.7609 | -0.10529 | 0.004578 | 0.045776 | 0.16937 | 0.15564 | 21.048 | 0.022889 | 0.004578 | 122.8134 | 19.0704 | -0.10529 | 0.022889 | 0.004578 | 19.0704 | 21.048 | 122.8134 | -122.85 | -122.9141
1422.9688 | 122.9187 | -0.19226 | 122.6532 | 0.19073 | 0.0074768 | 0.019226 | 0.030121 | 0.044647 | 0.051056 | 0.13672 | -0.15564 | -0.15106 | -0.21973 | 21.9223 | 21.8124 | 19.1895 | -0.009155 | -0.009155 | 122.6807 | -0.27924 | -0.027466 | -122.8043 | 0.036621 | 22.1146 | -100.8408 | -0.086975 | 0.027466 | 0.064087 | 0.18311 | 0.18311 | 22.0047 | 0.041199 | 0.036621 | 122.8729 | 19.3817 | -0.086975 | 0.041199 | 0.036621 | 19.3817 | 22.0047 | 122.8729 | -122.8729 | -122.9324
1423.9688 | 122.8958 | -0.16479 | 122.5525 | 0.29755 | 0.0074768 | 0.022217 | 0.028626 | 0.044006 | 0.052979 | 0.14056 | -0.14648 | -0.16022 | -0.21973 | 21.3638 | 21.286 | 18.8919 | 0.027466 | -0.022888 | 122.6395 | -0.27924 | -0.054932 | -122.7127 | 0.018311 | 21.5286 | -101.2665 | -0.11444 | 0.086975 | 0.073243 | 0.19226 | 0.14191 | 21.4508 | 0.004578 | 0.018311 | 122.8043 | 19.0567 | -0.11444 | 0.004578 | 0.018311 | 19.0567 | 21.4508 | 122.8043 | -122.7722 | -122.8317
1424.9688 | 122.8958 | -0.19226 | 122.6486 | 0.32043 | 0.0089722 | 0.019653 | 0.030548 | 0.046356 | 0.050842 | 0.14035 | -0.13275 | -0.14191 | -0.2243 | 21.5195 | 21.4416 | 19.0613 | 0.027466 | -0.036621 | 122.6578 | -0.27008 | -0.032043 | -122.7905 | 0.05951 | 21.7117 | -101.207 | -0.07782 | 0.009155 | 0.091553 | 0.21973 | 0.15564 | 21.6339 | 0.050354 | 0.05951 | 122.85 | 19.2535 | -0.07782 | 0.050354 | 0.05951 | 19.2535 | 21.6339 | 122.85 | -122.8729 | -122.9187
1425.9688 | 122.9645 | -0.16022 | 122.6349 | 0.11444 | 0.0083314 | 0.020721 | 0.029907 | 0.044006 | 0.052979 | 0.13651 | -0.09613 | -0.12817 | -0.21057 | 21.73 | 21.6431 | 19.2719 | 0.032043 | 0.045776 | 122.6898 | -0.2655 | -0.050354 | -122.7631 | 0.064087 | 21.8903 | -100.9918 | -0.10529 | 0.054931 | 0.11444 | 0.19226 | 0.20599 | 21.8033 | 0.032043 | 0.064087 | 122.85 | 19.4321 | -0.10529 | 0.032043 | 0.064087 | 19.4321 | 21.8033 | 122.85 | -122.8455 | -122.9004
1426.9688 | 122.9599 | -0.15106 | 122.6486 | 0.18311 | 0.0079042 | 0.018799 | 0.031616 | 0.030975 | 0.036102 | 0.10831 | -0.10071 | -0.14648 | -0.20142 | 49.5621 | 49.4247 | 46.5729 | -0.041199 | 0.041199 | 122.6715 | -0.27466 | -0.050354 | -122.7951 | 0.050354 | 49.7131 | -73.2239 | -0.1236 | 0.022888 | 0.10071 | 0.10986 | 0.19226 | 49.5758 | 0.004578 | 0.050354 | 122.8226 | 46.7239 | -0.1236 | 0.004578 | 0.050354 | 46.7239 | 49.5758 | 122.8226 | -122.85 | -122.9233
1427.9688 | 122.9462 | -0.17853 | 122.6303 | 0.10681 | 0.006836 | 0.017517 | 0.030548 | 0.022644 | 0.029053 | 0.093353 | -0.091553 | -0.16022 | -0.21057 | 63.0569 | 62.8922 | 59.3308 | -0.07782 | 0.032043 | 122.6715 | -0.25635 | -0.032043 | -122.7905 | 0.086975 | 63.2355 | -59.7382 | -0.07782 | 0.041199 | 0.11902 | 0.10071 | 0.21057 | 63.0707 | 0.018311 | 0.086975 | 122.85 | 59.5093 | -0.07782 | 0.018311 | 0.086975 | 59.5093 | 63.0707 | 122.85 | -122.8409 | -122.8867
1428.9688 | 122.9462 | -0.15106 | 122.6532 | 0.083923 | 0.0081178 | 0.020935 | 0.031189 | 0.010254 | 0.015595 | 0.068573 | -0.11444 | -0.16479 | -0.21515 | 83.6105 | 83.4412 | 80.5389 | -0.10986 | 0.036621 | 122.6807 | -0.27466 | -0.064087 | -122.818 | 0.036621 | 83.7616 | -39.212 | -0.1236 | 0.027466 | 0.10071 | 0.041199 | 0.18768 | 83.5922 | -0.013733 | 0.036621 | 122.8317 | 80.69 | -0.1236 | -0.013733 | 0.036621 | 80.69 | 83.5922 | 122.8317 | -122.8683 | -122.9279
1429.9688 | 122.9553 | -0.16937 | 122.6624 | 0.17548 | 0.0074768 | 0.018158 | 0.030335 | 0.016663 | 0.022003 | 0.080536 | -0.10986 | -0.14191 | -0.2243 | 74.025 | 73.8464 | 71.0815 | -0.068665 | 0.022888 | 122.6807 | -0.24719 | -0.054931 | -122.8043 | 0.05951 | 74.1943 | -48.8159 | -0.077819 | 0.01831 | 0.11444 | 0.10071 | 0.19226 | 74.0158 | 0.027466 | 0.05951 | 122.85 | 71.2509 | -0.077819 | 0.027466 | 0.05951 | 71.2509 | 74.0158 | 122.85 | -122.8867 | -122.9095
1430.9688 | 122.9141 | -0.17853 | 122.6669 | 0.20599 | 0.0091858 | 0.019653 | 0.031189 | 0.021576 | 0.028839 | 0.094635 | -0.17853 | -0.21057 | -0.27008 | 60.9421 | 60.7819 | 58.4885 | 0.032043 | -0.050354 | 122.6486 | -0.28839 | -0.091553 | -122.8775 | 0 | 61.1206 | -61.8851 | -0.10986 | -0.01831 | 0.091553 | 0.21057 | 0.12817 | 60.9604 | -0.032043 | 0 | 122.8271 | 58.667 | -0.10986 | -0.032043 | 0 | 58.667 | 60.9604 | 122.8271 | -122.937 | -122.9553
1431.9688 | 122.9233 | -0.19226 | 122.6486 | 0.26703 | 0.008545 | 0.01944 | 0.029266 | 0.02948 | 0.03418 | 0.10361 | -0.17853 | -0.21057 | -0.27008 | 52.1667 | 52.0432 | 50.0656 | 0.17853 | -0.032043 | 122.6532 | -0.29755 | -0.07782 | -122.8592 | 0.013733 | 52.359 | -70.6055 | -0.10528 | 0.004577 | 0.091553 | 0.37079 | 0.16022 | 52.2354 | -0.01831 | 0.013733 | 122.8455 | 50.2579 | -0.10528 | -0.01831 | 0.013733 | 50.2579 | 52.2354 | 122.8455 | -122.9187 | -122.9462
1432.9688 | 122.9782 | -0.16937 | 122.6303 | 0.16785 | 0.0081178 | 0.01709 | 0.030121 | 0.030975 | 0.03717 | 0.11258 | -0.07782 | -0.14191 | -0.20599 | 46.5775 | 46.4584 | 44.6503 | 0.1236 | 0.064087 | 122.6624 | -0.25177 | -0.036621 | -122.7722 | 0.091553 | 46.7468 | -76.1719 | -0.082397 | 0.032044 | 0.12817 | 0.29297 | 0.23346 | 46.6278 | 0.027466 | 0.091553 | 122.8317 | 44.8196 | -0.082397 | 0.027466 | 0.091553 | 44.8196 | 46.6278 | 122.8317 | -122.8363 | -122.8821
1433.9688 | 122.9965 | -0.15564 | 122.6349 | 0.10681 | 0.0089722 | 0.017304 | 0.030762 | 0.0070494 | 0.013245 | 0.058319 | -0.068665 | -0.15106 | -0.20599 | 92.7612 | 92.5964 | 87.9135 | -0.1236 | 0.041199 | 122.6578 | -0.28839 | -0.050354 | -122.7859 | 0.086975 | 92.9169 | -30.0385 | -0.13275 | 0.022888 | 0.13733 | 0.032044 | 0.19684 | 92.7521 | 0.004578 | 0.086975 | 122.8134 | 88.0692 | -0.13275 | 0.004578 | 0.086975 | 88.0692 | 92.7521 | 122.8134 | -122.8409 | -122.9233
1434.9688 | 122.9828 | -0.15106 | 122.6578 | 0.21362 | 0.0076904 | 0.023285 | 0.027985 | 0.035248 | 0.042084 | 0.11407 | -0.086975 | -0.12817 | -0.19684 | 43.1305 | 42.9886 | 41.3269 | 0.20142 | 0.050354 | 122.6669 | -0.25635 | -0.045776 | -122.7859 | 0.064087 | 43.2816 | -79.6692 | -0.10529 | 0.009155 | 0.10986 | 0.35248 | 0.20142 | 43.1396 | 0.022888 | 0.064087 | 122.818 | 41.478 | -0.10529 | 0.022888 | 0.064087 | 41.478 | 43.1396 | 122.818 | -122.8546 | -122.9141
1435.9688 | 122.9828 | -0.16022 | 122.6578 | 0.13733 | 0.006836 | 0.017731 | 0.030121 | 0.035675 | 0.042297 | 0.12006 | -0.091553 | -0.15564 | -0.19684 | 40.1321 | 39.9994 | 38.4384 | 0.24719 | 0.050354 | 122.6807 | -0.27008 | -0.036621 | -122.8134 | 0.068664 | 40.2924 | -82.6584 | -0.10986 | 0.022888 | 0.10529 | 0.40741 | 0.21057 | 40.1596 | 0.004577 | 0.068664 | 122.8409 | 38.5986 | -0.10986 | 0.004577 | 0.068664 | 38.5986 | 40.1596 | 122.8409 | -122.8546 | -122.9279
1436.9688 | 122.9645 | -0.15564 | 122.6578 | 0.17548 | 0.006836 | 0.018585 | 0.028626 | 0.035889 | 0.04422 | 0.11877 | -0.086975 | -0.11902 | -0.20142 | 38.1912 | 38.063 | 36.5662 | 0.19684 | 0.054932 | 122.6715 | -0.24719 | -0.045776 | -122.7768 | 0.068665 | 38.3469 | -84.5947 | -0.091552 | 0.013733 | 0.11444 | 0.35248 | 0.21057 | 38.2187 | 0.036621 | 0.068665 | 122.8271 | 36.7218 | -0.091552 | 0.036621 | 0.068665 | 36.7218 | 38.2187 | 122.8271 | -122.8592 | -122.905
1437.9688 | 122.9279 | -0.16022 | 122.6807 | 0.18311 | 0.011108 | 0.019867 | 0.029053 | 0.037384 | 0.043152 | 0.1192 | -0.13733 | -0.17853 | -0.22888 | 36.8774 | 36.7676 | 35.3577 | 0.24719 | -0.004578 | 122.6669 | -0.26093 | -0.068665 | -122.8592 | 0.022888 | 37.0377 | -85.9131 | -0.10071 | -0.013733 | 0.091553 | 0.40741 | 0.15564 | 36.9278 | -0.018311 | 0.022888 | 122.8271 | 35.5179 | -0.10071 | -0.018311 | 0.022888 | 35.5179 | 36.9278 | 122.8271 | -122.9095 | -122.9416
1438.9688 | 122.9736 | -0.15564 | 122.6395 | 0.030518 | 0.0070496 | 0.020081 | 0.031189 | 0.03418 | 0.039307 | 0.11365 | -0.050354 | -0.15106 | -0.20599 | 43.1534 | 42.9703 | 41.1621 | 0.068665 | 0.059509 | 122.6624 | -0.27466 | -0.050354 | -122.7905 | 0.10529 | 43.309 | -79.6692 | -0.11902 | 0.022889 | 0.15564 | 0.22431 | 0.21515 | 43.1259 | 0.004578 | 0.10529 | 122.818 | 41.3177 | -0.11902 | 0.004578 | 0.10529 | 41.3177 | 43.1259 | 122.818 | -122.8455 | -122.9141
1439.9688 | 122.9691 | -0.16479 | 122.6532 | 0.1297 | 0.0061952 | 0.024353 | 0.028626 | -0.0044862 | 0.0010682 | 0.034607 | -0.068665 | -0.1831 | -0.21057 | 114.4959 | 114.3173 | 108.7784 | -0.21515 | 0.045776 | 122.6486 | -0.28839 | -0.045776 | -122.8363 | 0.09613 | 114.6606 | -8.3359 | -0.1236 | -0.004577 | 0.14191 | -0.050354 | 0.21057 | 114.4821 | -0.01831 | 0.09613 | 122.8134 | 108.9432 | -0.1236 | -0.01831 | 0.09613 | 108.9432 | 114.4821 | 122.8134 | -122.8638 | -122.9416
1440.9688 | 122.9782 | -0.14191 | 122.6807 | 0.076294 | 0.0079042 | 0.020508 | 0.028839 | -0.003418 | -0.0004272 | 0.03717 | -0.07782 | -0.16479 | -0.21057 | 113.8 | 113.6261 | 108.1284 | -0.21057 | 0.064087 | 122.6624 | -0.27924 | -0.068664 | -122.8455 | 0.064087 | 113.942 | -9.0546 | -0.13733 | -0.01831 | 0.13275 | -0.068664 | 0.20599 | 113.768 | -0.022888 | 0.064087 | 122.8043 | 108.2703 | -0.13733 | -0.022888 | 0.064087 | 108.2703 | 113.768 | 122.8043 | -122.8912 | -122.9599
1441.9688 | 122.9782 | -0.16022 | 122.6578 | 0.083923 | 0.0083314 | 0.020294 | 0.029053 | -0.0036316 | 0.0019226 | 0.040161 | -0.068665 | -0.16479 | -0.21057 | 108.7692 | 108.5541 | 103.1204 | -0.21515 | 0.064087 | 122.6532 | -0.29297 | -0.050354 | -122.8226 | 0.091552 | 108.9294 | -14.1037 | -0.13275 | -0.004578 | 0.14191 | -0.054932 | 0.2243 | 108.7143 | -0.004578 | 0.091552 | 122.8134 | 103.2806 | -0.13275 | -0.004578 | 0.091552 | 103.2806 | 108.7143 | 122.8134 | -122.8683 | -122.9507
1442.9688 | 123.0148 | -0.16479 | 122.6578 | 0.10681 | 0.0072632 | 0.01944 | 0.028198 | -0.0042726 | 0.0004272 | 0.036102 | -0.082397 | -0.15564 | -0.20142 | 111.4975 | 111.3007 | 105.9402 | -0.23346 | 0.07782 | 122.6715 | -0.28381 | -0.036621 | -122.8134 | 0.082398 | 111.6623 | -11.3571 | -0.11902 | 0.013733 | 0.11902 | -0.068664 | 0.24261 | 111.4655 | 0.009155 | 0.082398 | 122.8363 | 106.105 | -0.11902 | 0.009155 | 0.082398 | 106.105 | 111.4655 | 122.8363 | -122.8592 | -122.9416
1443.9688 | 123.024 | -0.16479 | 122.6395 | 0.14496 | 0.008545 | 0.021576 | 0.032044 | 0.0036316 | 0.0089722 | 0.054901 | -0.073242 | -0.15564 | -0.19226 | 98.0576 | 97.8745 | 93.0679 | -0.13733 | 0.091553 | 122.6898 | -0.27466 | -0.027466 | -122.7951 | 0.091553 | 98.2224 | -24.765 | -0.10986 | 0.050354 | 0.11902 | 0.027466 | 0.25635 | 98.0392 | 0.009155 | 0.091553 | 122.8546 | 93.2327 | -0.10986 | 0.009155 | 0.091553 | 93.2327 | 98.0392 | 122.8546 | -122.8317 | -122.9141
1444.9688 | 122.9645 | -0.17395 | 122.6852 | 0.099182 | 0.0057678 | 0.020508 | 0.028839 | -0.0049134 | 0 | 0.03653 | -0.11902 | -0.14648 | -0.20599 | 113.5574 | 113.3743 | 107.5012 | -0.17395 | 0.022888 | 122.6807 | -0.25177 | -0.032044 | -122.8317 | 0.054931 | 113.7314 | -9.3109 | -0.07782 | -0.004578 | 0.086975 | 0 | 0.19684 | 113.5483 | 0.027466 | 0.054931 | 122.8546 | 107.6752 | -0.07782 | 0.027466 | 0.054931 | 107.6752 | 113.5483 | 122.8546 | -122.8912 | -122.937
1445.9688 | 123.0011 | -0.16022 | 122.6807 | 0.11444 | 0.006836 | 0.017944 | 0.02948 | -0.0059816 | 0.0006408 | 0.035461 | -0.091553 | -0.15106 | -0.21057 | 114.9124 | 114.7293 | 108.8196 | -0.19684 | 0.073242 | 122.6486 | -0.28381 | -0.050354 | -122.8317 | 0.068664 | 115.0726 | -7.9514 | -0.1236 | -0.032043 | 0.11902 | -0.036621 | 0.23346 | 114.8895 | 0.009155 | 0.068664 | 122.8088 | 108.9798 | -0.1236 | 0.009155 | 0.068664 | 108.9798 | 114.8895 | 122.8088 | -122.8912 | -122.9645
1446.9688 | 122.9599 | -0.15564 | 122.6715 | -0.1297 | 0.0091858 | 0.018585 | 0.029053 | 0.0021362 | 0.0074768 | 0.053619 | -0.10071 | -0.16937 | -0.22888 | 98.8037 | 98.6206 | 93.8141 | -0.086975 | 0.045776 | 122.6669 | -0.2655 | -0.073242 | -122.8409 | 0.054932 | 98.9594 | -24.0509 | -0.10986 | -0.004578 | 0.12817 | 0.068665 | 0.20142 | 98.7762 | -0.013733 | 0.054932 | 122.8226 | 93.9697 | -0.10986 | -0.013733 | 0.054932 | 93.9697 | 98.7762 | 122.8226 | -122.9004 | -122.937
1447.9688 | 122.9645 | -0.16479 | 122.6852 | -0.045776 | 0.0093994 | 0.020081 | 0.031616 | 0.0042724 | 0.0089722 | 0.054901 | -0.091553 | -0.17853 | -0.23804 | 97.4854 | 97.2931 | 92.6514 | -0.086975 | 0.041199 | 122.7036 | -0.27924 | -0.073242 | -122.8638 | 0.073242 | 97.6501 | -25.3922 | -0.11444 | 0.01831 | 0.14648 | 0.07782 | 0.20599 | 97.4579 | -0.013733 | 0.073242 | 122.8683 | 92.8162 | -0.11444 | -0.013733 | 0.073242 | 92.8162 | 97.4579 | 122.8683 | -122.9233 | -122.9645
1448.9688 | 122.9599 | -0.17395 | 122.6715 | 0.56458 | 0.0081178 | 0.019013 | 0.031616 | 0.0057678 | 0.010681 | 0.054687 | -0.082397 | -0.1831 | -0.2243 | 95.4163 | 95.2377 | 90.7059 | -0.036621 | 0.054932 | 122.6944 | -0.26093 | -0.050354 | -122.8546 | 0.091553 | 95.5902 | -27.4338 | -0.086975 | 0.022888 | 0.14191 | 0.13733 | 0.22888 | 95.4117 | -0.009155 | 0.091553 | 122.8683 | 90.8798 | -0.086975 | -0.009155 | 0.091553 | 90.8798 | 95.4117 | 122.8683 | -122.8958 | -122.9324
1449.9688 | 122.9599 | -0.17395 | 122.6532 | 0.33569 | 0.005127 | 0.020081 | 0.03418 | -0.0055542 | -0.0032044 | 0.030975 | -0.091553 | -0.19684 | -0.22888 | 117.8375 | 117.6407 | 111.4151 | -0.19684 | 0.032043 | 122.7127 | -0.28839 | -0.054932 | -122.85 | 0.082397 | 118.0115 | -5.0125 | -0.11444 | 0.05951 | 0.13733 | -0.022888 | 0.20599 | 117.8146 | -0.022888 | 0.082397 | 122.8867 | 111.5891 | -0.11444 | -0.022888 | 0.082397 | 111.5891 | 117.8146 | 122.8867 | -122.8821 | -122.9416
1450.9844 | 122.8592 | -0.22888 | 122.7127 | 0.28992 | 0.010468 | 0.023712 | 0.035675 | -0.0032044 | -0.001068 | 0.030334 | -0.16479 | -0.1236 | -0.2655 | 117.7872 | 117.5949 | 111.4243 | -0.064087 | -0.13733 | 122.7356 | -0.34332 | -0.036621 | -122.8363 | 0.064087 | 118.0161 | -5.1178 | -0.11444 | 0.022888 | 0.10071 | 0.16479 | 0.091553 | 117.8238 | 0.10529 | 0.064087 | 122.9645 | 111.6531 | -0.11444 | 0.10529 | 0.064087 | 111.6531 | 117.8238 | 122.9645 | -122.9782 | -123.056
1451.9688 | 123.0148 | -0.16937 | 122.644 | 0.12207 | 0.0081178 | 0.023712 | 0.029053 | -0.0053406 | -0.003418 | 0.032257 | -0.091553 | -0.15564 | -0.20142 | 117.9703 | 117.7917 | 111.6028 | -0.16937 | 0.068665 | 122.6898 | -0.25635 | -0.032043 | -122.7997 | 0.07782 | 118.1396 | -4.8523 | -0.086975 | 0.045776 | 0.10986 | 0 | 0.23804 | 117.9611 | 0.013733 | 0.07782 | 122.8592 | 111.7722 | -0.086975 | 0.013733 | 0.07782 | 111.7722 | 117.9611 | 122.8592 | -122.8455 | -122.9004
1452.9688 | 122.9691 | -0.15564 | 122.6852 | 0.72479 | 0.0059814 | 0.015595 | 0.030335 | -0.0061952 | -0.003418 | 0.030548 | -0.082397 | -0.1831 | -0.21973 | 117.9565 | 117.7734 | 111.5433 | -0.14648 | 0.050354 | 122.7081 | -0.27008 | -0.064087 | -122.8683 | 0.073243 | 118.1122 | -4.9118 | -0.11444 | 0.022888 | 0.13733 | 0.009156 | 0.20599 | 117.9291 | -0.027465 | 0.073243 | 122.8638 | 111.6989 | -0.11444 | -0.027465 | 0.073243 | 111.6989 | 117.9291 | 122.8638 | -122.905 | -122.9553
1453.9688 | 122.9324 | -0.18768 | 122.6807 | -0.022889 | 0.006836 | 0.023712 | 0.032471 | -0.0079042 | -0.0049134 | 0.030975 | -0.10071 | -0.14648 | -0.21973 | 117.9703 | 117.7734 | 111.5295 | -0.086975 | -0.004578 | 122.7081 | -0.28839 | -0.032044 | -122.8271 | 0.086975 | 118.158 | -4.9072 | -0.10071 | 0.027466 | 0.11902 | 0.10071 | 0.1831 | 117.9611 | 0.041199 | 0.086975 | 122.8958 | 111.7172 | -0.10071 | 0.041199 | 0.086975 | 111.7172 | 117.9611 | 122.8958 | -122.9004 | -122.9691
1454.9688 | 122.9233 | -0.20142 | 122.7036 | 0.007629 | 0.0083314 | 0.01944 | 0.031189 | -0.0076904 | -0.0046996 | 0.031189 | -0.10529 | -0.13275 | -0.21515 | 118.0115 | 117.8375 | 111.5616 | -0.036621 | -0.013733 | 122.7081 | -0.29755 | -0.013733 | -122.8363 | 0.09613 | 118.2129 | -4.866 | -0.09613 | 0.004578 | 0.10986 | 0.1648 | 0.18768 | 118.0389 | 0.068665 | 0.09613 | 122.9095 | 111.763 | -0.09613 | 0.068665 | 0.09613 | 111.763 | 118.0389 | 122.9095 | -122.9187 | -123.0011
1455.9844 | 122.8867 | -0.19684 | 122.7173 | 0.41199 | 0.012604 | 0.023926 | 0.03717 | -0.0042726 | -0.0049134 | 0.032043 | -0.17853 | -0.11902 | -0.25635 | 117.9016 | 117.6865 | 111.4838 | 0.30212 | 0.004578 | 122.7585 | -0.31128 | -0.05951 | -122.8363 | 0.01831 | 118.0984 | -5.0308 | -0.11444 | 0.041199 | 0.07782 | 0.49896 | 0.20142 | 117.8833 | 0.077819 | 0.01831 | 122.9553 | 111.6806 | -0.11444 | 0.077819 | 0.01831 | 111.6806 | 117.8833 | 122.9553 | -122.9736 | -123.0286
1456.9688 | 122.9279 | -0.19684 | 122.6532 | 0.007629 | 0.0074768 | 0.024353 | 0.029907 | -0.004059 | -0.0040588 | 0.031403 | -0.10529 | -0.15106 | -0.2243 | 118.0344 | 117.8467 | 111.5112 | -0.022888 | 0.009155 | 122.7493 | -0.3067 | -0.027466 | -122.8043 | 0.091552 | 118.2312 | -4.8065 | -0.10986 | 0.096131 | 0.11902 | 0.17395 | 0.20599 | 118.0435 | 0.045776 | 0.091552 | 122.9462 | 111.7081 | -0.10986 | 0.045776 | 0.091552 | 111.7081 | 118.0435 | 122.9462 | -122.8775 | -122.9599
1457.9688 | 122.9965 | -0.1831 | 122.6715 | -0.0076295 | 0.006836 | 0.020935 | 0.034821 | -0.0049134 | -0.0014954 | 0.032471 | -0.082397 | -0.17853 | -0.21515 | 117.9108 | 117.8101 | 111.8912 | -0.1831 | 0.045776 | 122.6852 | -0.3067 | -0.032044 | -122.85 | 0.10071 | 118.0939 | -4.8615 | -0.1236 | 0.013733 | 0.13275 | 0 | 0.22888 | 117.9932 | 0.004577 | 0.10071 | 122.8683 | 112.0743 | -0.1236 | 0.004577 | 0.10071 | 112.0743 | 117.9932 | 122.8683 | -122.8867 | -122.9782
1458.9688 | 122.9874 | -0.18768 | 122.6761 | 0.030518 | 0.0070496 | 0.020081 | 0.032471 | -0.0059816 | -0.0049134 | 0.031403 | -0.09613 | -0.16937 | -0.21973 | 117.9977 | 117.6041 | 111.5479 | 0.050354 | -0.004578 | 122.6715 | -0.3067 | -0.032044 | -122.8455 | 0.091553 | 118.1854 | -5.072 | -0.11902 | -0.004577 | 0.1236 | 0.23804 | 0.1831 | 117.7917 | 0.01831 | 0.091553 | 122.8592 | 111.7355 | -0.11902 | 0.01831 | 0.091553 | 111.7355 | 117.7917 | 122.8592 | -122.8958 | -122.9828
1459.9688 | 122.8683 | -0.20599 | 122.7173 | -0.061036 | 0.0066224 | 0.019653 | 0.033112 | -0.0074768 | -0.002777 | 0.031616 | -0.12817 | -0.14191 | -0.22888 | 117.9703 | 117.7689 | 111.5433 | 0.09613 | -0.045776 | 122.7036 | -0.32501 | -0.022888 | -122.8592 | 0.07782 | 118.1763 | -4.9484 | -0.11902 | -0.013733 | 0.10071 | 0.30212 | 0.16022 | 117.9749 | 0.064087 | 0.07782 | 122.9095 | 111.7493 | -0.11902 | 0.064087 | 0.07782 | 111.7493 | 117.9749 | 122.9095 | -122.9462 | -123.0423
1460.9844 | 122.8409 | -0.2243 | 122.6852 | 0.26703 | 0.01004 | 0.024567 | 0.039307 | -0.0049134 | -0.002777 | 0.027771 | -0.16479 | -0.10986 | -0.2655 | 117.9977 | 117.8009 | 111.5982 | 0.032043 | -0.16937 | 122.7219 | -0.32044 | -0.041199 | -122.7951 | 0.059509 | 118.222 | -4.8843 | -0.096131 | 0.036621 | 0.10071 | 0.25635 | 0.054931 | 118.0252 | 0.11444 | 0.059509 | 122.9462 | 111.8225 | -0.096131 | 0.11444 | 0.059509 | 111.8225 | 118.0252 | 122.9462 | -122.9507 | -123.0057
1461.9688 | 122.9187 | -0.19684 | 122.6944 | -0.045776 | 0.0091858 | 0.018372 | 0.030975 | -0.005127 | -0.002777 | 0.03183 | -0.1236 | -0.14191 | -0.25177 | 117.9291 | 117.7505 | 111.5616 | 0.036621 | -0.041199 | 122.7493 | -0.33417 | -0.054932 | -122.8363 | 0.073242 | 118.1259 | -4.9438 | -0.13733 | 0.054932 | 0.12817 | 0.23346 | 0.15564 | 117.9474 | 0.054931 | 0.073242 | 122.9462 | 111.7584 | -0.13733 | 0.054931 | 0.073242 | 111.7584 | 117.9474 | 122.9462 | -122.9462 | -123.0286
1462.9688 | 122.937 | -0.19226 | 122.7036 | -0.045776 | 0.0087586 | 0.018585 | 0.033325 | -0.0061952 | -0.0036316 | 0.03183 | -0.12817 | -0.15106 | -0.22888 | 118.1168 | 117.952 | 111.795 | 0.013733 | -0.036621 | 122.7402 | -0.29755 | -0.036621 | -122.8546 | 0.064087 | 118.309 | -4.7516 | -0.10528 | 0.036621 | 0.10071 | 0.20599 | 0.15564 | 118.1442 | 0.041199 | 0.064087 | 122.9324 | 111.9873 | -0.10528 | 0.041199 | 0.064087 | 111.9873 | 118.1442 | 122.9324 | -122.9324 | -123.0011
1463.9688 | 122.9279 | -0.17853 | 122.7036 | -0.045776 | 0.008545 | 0.020294 | 0.029694 | 0.0083312 | 0.013672 | 0.063019 | -0.11902 | -0.13733 | -0.23346 | 91.0446 | 90.8615 | 86.1832 | 0.35248 | -0.022888 | 122.7493 | -0.29297 | -0.054931 | -122.8409 | 0.059509 | 91.2231 | -31.842 | -0.11444 | 0.045777 | 0.11444 | 0.53101 | 0.15564 | 91.04 | 0.041199 | 0.059509 | 122.9279 | 86.3617 | -0.11444 | 0.041199 | 0.059509 | 86.3617 | 91.04 | 122.9279 | -122.937 | -122.9965
1464.9688 | 122.9874 | -0.16479 | 122.6715 | -0.20599 | 0.0087586 | 0.020081 | 0.029053 | -0.0061952 | -0.0036316 | 0.030762 | -0.09613 | -0.1831 | -0.24719 | 118.3044 | 118.1305 | 112.3215 | -0.13275 | 0.045776 | 122.7127 | -0.29297 | -0.082397 | -122.8546 | 0.068665 | 118.4692 | -4.541 | -0.12817 | 0.041199 | 0.15106 | 0.032044 | 0.21057 | 118.2953 | -0.01831 | 0.068665 | 122.8775 | 112.4863 | -0.12817 | -0.01831 | 0.068665 | 112.4863 | 118.2953 | 122.8775 | -122.9187 | -122.9645
1465.9844 | 122.85 | -0.19226 | 122.818 | 0.11444 | 0.009613 | 0.021149 | 0.038025 | -0.0046998 | -0.002777 | 0.031189 | -0.11444 | -0.1236 | -0.2655 | 118.2083 | 118.0023 | 111.9736 | 0.036621 | -0.073242 | 122.7539 | -0.31586 | -0.073242 | -122.9416 | 0.07782 | 118.4006 | -4.8157 | -0.1236 | -0.064087 | 0.15106 | 0.22888 | 0.11902 | 118.1946 | 0.068665 | 0.07782 | 122.9462 | 112.1658 | -0.1236 | 0.068665 | 0.07782 | 112.1658 | 118.1946 | 122.9462 | -123.0835 | -123.1338
1466.9688 | 122.8546 | -0.23804 | 122.6898 | 0.022888 | 0.0079042 | 0.021149 | 0.03183 | -0.0072632 | -0.005127 | 0.032043 | -0.16022 | -0.1236 | -0.26093 | 118.0847 | 117.9199 | 112.0102 | 0.086975 | -0.086975 | 122.7676 | -0.33875 | -0.022888 | -122.8134 | 0.07782 | 118.3228 | -4.7699 | -0.10071 | 0.07782 | 0.10071 | 0.32501 | 0.15106 | 118.158 | 0.11444 | 0.07782 | 123.0057 | 112.2482 | -0.10071 | 0.11444 | 0.07782 | 112.2482 | 118.158 | 123.0057 | -122.9507 | -123.0286
1467.9688 | 122.8867 | -0.21515 | 122.7036 | 0 | 0.0093994 | 0.017731 | 0.033753 | -0.0059816 | -0.0023498 | 0.030762 | -0.1831 | -0.13275 | -0.24719 | 118.1992 | 118.0344 | 112.2025 | 0.07782 | -0.082397 | 122.7676 | -0.33417 | -0.032043 | -122.8363 | 0.032044 | 118.4143 | -4.6692 | -0.11902 | 0.064087 | 0.064087 | 0.29297 | 0.13275 | 118.2495 | 0.082398 | 0.032044 | 122.9828 | 112.4176 | -0.11902 | 0.082398 | 0.032044 | 112.4176 | 118.2495 | 122.9828 | -122.9507 | -123.0377
1468.9688 | 122.8683 | -0.23346 | 122.7036 | -0.030518 | 0.008545 | 0.023071 | 0.031403 | -0.005127 | -0.0019226 | 0.030121 | -0.17395 | -0.13275 | -0.26093 | 118.1671 | 117.9977 | 112.0331 | 0.21973 | -0.10529 | 122.7768 | -0.32501 | -0.027466 | -122.8363 | 0.059509 | 118.4006 | -4.7058 | -0.091553 | 0.073242 | 0.086975 | 0.45319 | 0.12817 | 118.2312 | 0.10071 | 0.059509 | 123.0103 | 112.2665 | -0.091553 | 0.10071 | 0.059509 | 112.2665 | 118.2312 | 123.0103 | -122.9645 | -123.0286
1470.0469 | 122.9965 | -0.18768 | 122.699 | 0.13733 | 0.0070496 | 0.01944 | 0.029694 | -0.0053406 | -0.0029906 | 0.030121 | -0.10986 | -0.15106 | -0.21057 | 118.158 | 117.9794 | 112.0285 | 0.07782 | 0.009155 | 122.7402 | -0.27924 | -0.022888 | -122.85 | 0.07782 | 118.3456 | -4.7195 | -0.091553 | 0.041198 | 0.10071 | 0.2655 | 0.19684 | 118.1671 | 0.036621 | 0.07782 | 122.9279 | 112.2162 | -0.091553 | 0.036621 | 0.07782 | 112.2162 | 118.1671 | 122.9279 | -122.9095 | -122.9782
1470.9844 | 122.8821 | -0.20142 | 122.699 | 0.32806 | 0.0098268 | 0.023071 | 0.033966 | -0.0038452 | -0.0023498 | 0.030548 | -0.16937 | -0.11444 | -0.2655 | 117.9611 | 117.7368 | 111.8362 | 0.068665 | -0.13733 | 122.7493 | -0.3479 | -0.064087 | -122.8134 | 0.032043 | 118.1625 | -4.9622 | -0.14648 | 0.050354 | 0.09613 | 0.27008 | 0.064087 | 117.9382 | 0.086975 | 0.032043 | 122.9507 | 112.0377 | -0.14648 | 0.086975 | 0.032043 | 112.0377 | 117.9382 | 122.9507 | -122.9645 | -123.0469
1471.9688 | 122.9553 | -0.17853 | 122.7036 | 0.007629 | 0.0070496 | 0.019867 | 0.030548 | -0.0061952 | -0.001068 | 0.030975 | -0.09613 | -0.13275 | -0.2243 | 118.3273 | 118.1213 | 112.1338 | 0.13275 | 0.018311 | 122.7448 | -0.29297 | -0.045776 | -122.8363 | 0.082398 | 118.5059 | -4.5822 | -0.11444 | 0.041199 | 0.12817 | 0.31128 | 0.19684 | 118.2999 | 0.045777 | 0.082398 | 122.9233 | 112.3123 | -0.11444 | 0.045777 | 0.082398 | 112.3123 | 118.2999 | 122.9233 | -122.9279 | -122.9965
1472.9688 | 122.9462 | -0.19226 | 122.6761 | 0.007629 | 0.0083314 | 0.020935 | 0.032471 | -0.0061952 | -0.003418 | 0.030121 | -0.091553 | -0.17395 | -0.2243 | 118.2358 | 118.0618 | 112.1246 | 0.1236 | 0.013733 | 122.7264 | -0.30212 | -0.032043 | -122.85 | 0.10071 | 118.428 | -4.6143 | -0.10986 | 0.050354 | 0.13275 | 0.31586 | 0.20599 | 118.2541 | 0.018311 | 0.10071 | 122.9187 | 112.3169 | -0.10986 | 0.018311 | 0.10071 | 112.3169 | 118.2541 | 122.9187 | -122.9004 | -122.9782
1473.9688 | 122.8867 | -0.21515 | 122.7219 | -0.099183 | 0.010895 | 0.017731 | 0.033966 | -0.0055542 | -0.0025634 | 0.03183 | -0.19226 | -0.064087 | -0.21515 | 118.2587 | 118.0847 | 112.1521 | 0.21973 | -0.10071 | 122.7905 | -0.33417 | 0 | -122.7859 | 0.022888 | 118.4738 | -4.6371 | -0.11902 | 0.068664 | 0.022888 | 0.43488 | 0.11444 | 118.2999 | 0.15106 | 0.022888 | 123.0057 | 112.3672 | -0.11902 | 0.15106 | 0.022888 | 112.3672 | 118.2999 | 123.0057 | -122.937 | -123.056
1474.9688 | 122.8912 | -0.21515 | 122.7173 | -0.2594 | 0.010254 | 0.020721 | 0.035461 | -0.0046998 | -0.0038452 | 0.030121 | -0.16479 | -0.068665 | -0.2243 | 118.3456 | 118.1534 | 112.1338 | 0.29297 | -0.09613 | 122.7859 | -0.34332 | -0.009155 | -122.7859 | 0.050354 | 118.5608 | -4.5639 | -0.12817 | 0.068665 | 0.059509 | 0.50812 | 0.11902 | 118.3685 | 0.14648 | 0.050354 | 123.0011 | 112.3489 | -0.12817 | 0.14648 | 0.050354 | 112.3489 | 118.3685 | 123.0011 | -122.9416 | -123.0606
1475.9688 | 122.8867 | -0.21515 | 122.7219 | -0.23651 | 0.009613 | 0.023712 | 0.035034 | -0.0046998 | -0.001709 | 0.030975 | -0.15564 | -0.073242 | -0.22888 | 118.3594 | 118.158 | 112.1658 | 0.42114 | -0.091553 | 122.8043 | -0.32501 | -0.013733 | -122.7951 | 0.059509 | 118.5745 | -4.5639 | -0.10986 | 0.082397 | 0.073242 | 0.63629 | 0.1236 | 118.3731 | 0.14191 | 0.059509 | 123.0194 | 112.381 | -0.10986 | 0.14191 | 0.059509 | 112.381 | 118.3731 | 123.0194 | -122.9507 | -123.0469
1476.9688 | 122.8775 | -0.20599 | 122.6898 | 0.29755 | 0.0089722 | 0.020721 | 0.03183 | -0.0042726 | -0.0023498 | 0.030121 | -0.14191 | -0.064087 | -0.21515 | 118.3273 | 118.1168 | 112.1841 | 0.35248 | -0.091553 | 122.8043 | -0.33417 | -0.009155 | -122.7539 | 0.064087 | 118.5333 | -4.5731 | -0.12817 | 0.11444 | 0.073242 | 0.55847 | 0.11444 | 118.3228 | 0.14191 | 0.064087 | 123.0103 | 112.3901 | -0.12817 | 0.14191 | 0.064087 | 112.3901 | 118.3228 | 123.0103 | -122.905 | -123.024
1477.9688 | 122.85 | -0.2243 | 122.7264 | -0.015259 | 0.011749 | 0.023712 | 0.033539 | -0.0061952 | -0.0040588 | 0.030334 | -0.16937 | -0.073242 | -0.21515 | 118.4006 | 118.2129 | 112.3169 | 0.45776 | -0.10529 | 122.7814 | -0.32501 | 0.009155 | -122.7997 | 0.054931 | 118.6249 | -4.5135 | -0.10071 | 0.054932 | 0.045776 | 0.68207 | 0.11902 | 118.4372 | 0.15106 | 0.054931 | 123.0057 | 112.5412 | -0.10071 | 0.15106 | 0.054931 | 112.5412 | 118.4372 | 123.0057 | -122.9416 | -123.0515
1478.9688 | 122.8912 | -0.21973 | 122.7264 | -0.045776 | 0.009613 | 0.018799 | 0.029694 | -0.0053406 | -0.0038452 | 0.030762 | -0.16479 | -0.1236 | -0.24719 | 118.2266 | 118.0298 | 112.1109 | 0.40283 | -0.091553 | 122.7905 | -0.32959 | -0.027465 | -122.85 | 0.054932 | 118.4464 | -4.6967 | -0.10986 | 0.064087 | 0.082397 | 0.62256 | 0.12817 | 118.2495 | 0.096131 | 0.054932 | 123.0103 | 112.3306 | -0.10986 | 0.096131 | 0.054932 | 112.3306 | 118.2495 | 123.0103 | -122.9736 | -123.056
1479.9688 | 122.8912 | -0.21973 | 122.731 | -0.015259 | 0.009613 | 0.022217 | 0.031403 | -0.0053406 | -0.002777 | 0.03183 | -0.15106 | -0.12817 | -0.24261 | 118.4143 | 118.2495 | 112.2849 | 0.49896 | -0.082397 | 122.7997 | -0.32959 | -0.022888 | -122.8592 | 0.068665 | 118.634 | -4.4815 | -0.10986 | 0.068665 | 0.091553 | 0.71869 | 0.13733 | 118.4692 | 0.091553 | 0.068665 | 123.0194 | 112.5046 | -0.10986 | 0.091553 | 0.068665 | 112.5046 | 118.4692 | 123.0194 | -122.9736 | -123.0606
1480.9688 | 122.9004 | -0.22888 | 122.7081 | 0.076294 | 0.010468 | 0.023285 | 0.033753 | -0.0042726 | -0.0021362 | 0.032471 | -0.15106 | -0.11902 | -0.2655 | 118.4189 | 118.2358 | 112.2528 | 0.63171 | -0.09613 | 122.7539 | -0.32959 | -0.036621 | -122.8271 | 0.07782 | 118.6478 | -4.4724 | -0.10071 | 0.045776 | 0.11444 | 0.8606 | 0.13275 | 118.4647 | 0.10986 | 0.07782 | 122.9828 | 112.4817 | -0.10071 | 0.10986 | 0.07782 | 112.4817 | 118.4647 | 122.9828 | -122.9736 | -123.0377
1481.9688 | 122.9141 | -0.23804 | 122.6761 | 0.045776 | 0.010895 | 0.020294 | 0.032257 | -0.004059 | -0.0036316 | 0.029266 | -0.16022 | -0.10986 | -0.24261 | 118.4738 | 118.2678 | 112.3032 | 0.64545 | -0.09613 | 122.7768 | -0.34332 | -0.004578 | -122.7859 | 0.07782 | 118.7119 | -4.4083 | -0.10529 | 0.10071 | 0.082398 | 0.88348 | 0.14191 | 118.5059 | 0.12817 | 0.07782 | 123.0148 | 112.5412 | -0.10529 | 0.12817 | 0.07782 | 112.5412 | 118.5059 | 123.0148 | -122.9187 | -123.0194
1482.9688 | 122.9187 | -0.22888 | 122.6944 | 0.015259 | 0.011536 | 0.025208 | 0.033112 | -0.0038452 | -0.0025634 | 0.029907 | -0.16937 | -0.11444 | -0.2655 | 118.5013 | 118.2999 | 112.3032 | 0.61798 | -0.091553 | 122.7859 | -0.34332 | -0.036621 | -122.8088 | 0.059509 | 118.7302 | -4.3945 | -0.11444 | 0.091553 | 0.09613 | 0.84686 | 0.13733 | 118.5287 | 0.11444 | 0.059509 | 123.0148 | 112.532 | -0.11444 | 0.11444 | 0.059509 | 112.532 | 118.5287 | 123.0148 | -122.9599 | -123.0377
1483.9688 | 122.9233 | -0.24719 | 122.699 | 0.007629 | 0.009613 | 0.020294 | 0.034393 | -0.0027772 | -0.0049134 | 0.029694 | -0.16937 | -0.11902 | -0.27924 | 118.4784 | 118.309 | 112.3032 | 0.50354 | -0.10529 | 122.7859 | -0.32044 | -0.032044 | -122.818 | 0.077819 | 118.7256 | -4.39 | -0.073243 | 0.086975 | 0.10986 | 0.75073 | 0.14191 | 118.5562 | 0.12817 | 0.077819 | 123.0331 | 112.5504 | -0.073243 | 0.12817 | 0.077819 | 112.5504 | 118.5562 | 123.0331 | -122.9782 | -123.0194
1484.9688 | 122.9141 | -0.22888 | 122.7402 | 0.022888 | 0.0093994 | 0.021576 | 0.032898 | -0.003418 | -0.0042724 | 0.030975 | -0.16022 | -0.11444 | -0.27466 | 118.4784 | 118.277 | 112.2894 | 0.58136 | -0.10071 | 122.7997 | -0.3479 | -0.045776 | -122.8546 | 0.068665 | 118.7073 | -4.4632 | -0.11902 | 0.05951 | 0.11444 | 0.81024 | 0.12817 | 118.5059 | 0.11444 | 0.068665 | 123.0286 | 112.5183 | -0.11902 | 0.11444 | 0.068665 | 112.5183 | 118.5059 | 123.0286 | -123.0148 | -123.0881
1485.9688 | 122.8775 | -0.19684 | 122.7127 | -0.053406 | 0.011108 | 0.024567 | 0.032044 | -0.0032044 | -0.0023498 | 0.030121 | -0.19226 | -0.10071 | -0.27924 | 118.4463 | 118.2404 | 112.2803 | 0.94299 | -0.13275 | 122.8455 | -0.3067 | -0.082398 | -122.8134 | 0.004577 | 118.6432 | -4.4724 | -0.10986 | 0.13275 | 0.086975 | 1.1398 | 0.064087 | 118.4372 | 0.09613 | 0.004577 | 123.0423 | 112.4771 | -0.10986 | 0.09613 | 0.004577 | 112.4771 | 118.4372 | 123.0423 | -122.9919 | -123.0194
1486.9688 | 122.8729 | -0.18768 | 122.7219 | -0.030518 | 0.011108 | 0.019226 | 0.028198 | -0.0038452 | -0.002777 | 0.032043 | -0.17853 | -0.10071 | -0.28839 | 118.4418 | 118.3685 | 112.3627 | 0.76446 | -0.073242 | 122.8317 | -0.29297 | -0.10071 | -122.8226 | 0.009155 | 118.6295 | -4.3533 | -0.10529 | 0.10986 | 0.10986 | 0.95215 | 0.11444 | 118.5562 | 0.086975 | 0.009155 | 123.0194 | 112.5504 | -0.10529 | 0.086975 | 0.009155 | 112.5504 | 118.5562 | 123.0194 | -123.0103 | -123.0148
1487.9688 | 122.9187 | -0.22888 | 122.6944 | 0.045776 | 0.011322 | 0.024139 | 0.034393 | -0.0029908 | -0.002777 | 0.030121 | -0.11902 | -0.1236 | -0.2655 | 118.5608 | 118.3685 | 112.4451 | 0.88806 | -0.064087 | 122.7951 | -0.33417 | -0.036621 | -122.818 | 0.10986 | 118.7897 | -4.3259 | -0.10528 | 0.10071 | 0.14648 | 1.1169 | 0.16479 | 118.5974 | 0.10529 | 0.10986 | 123.024 | 112.674 | -0.10528 | 0.10529 | 0.10986 | 112.674 | 118.5974 | 123.024 | -122.9599 | -123.0286
1488.9688 | 122.9324 | -0.22888 | 122.7081 | 0 | 0.011749 | 0.022003 | 0.034607 | -0.0021364 | -0.0040588 | 0.030121 | -0.13275 | -0.1236 | -0.27924 | 118.5791 | 118.3914 | 112.6694 | 1.0345 | -0.050354 | 122.8088 | -0.32959 | -0.050354 | -122.8317 | 0.096131 | 118.808 | -4.3167 | -0.10071 | 0.10071 | 0.14648 | 1.2634 | 0.17853 | 118.6203 | 0.10529 | 0.096131 | 123.0377 | 112.8983 | -0.10071 | 0.10529 | 0.096131 | 112.8983 | 118.6203 | 123.0377 | -122.9874 | -123.0377
1489.9688 | 122.9187 | -0.22888 | 122.6898 | 0.030518 | 0.010254 | 0.022003 | 0.032257 | -0.0008546 | -0.0025634 | 0.029266 | -0.14648 | -0.11902 | -0.27924 | 118.5608 | 118.3823 | 112.5275 | 0.6958 | -0.073242 | 122.7768 | -0.3479 | -0.050354 | -122.8088 | 0.082398 | 118.7897 | -4.3076 | -0.11902 | 0.086975 | 0.13275 | 0.92468 | 0.15564 | 118.6111 | 0.10986 | 0.082398 | 123.0057 | 112.7563 | -0.11902 | 0.10986 | 0.082398 | 112.7563 | 118.6111 | 123.0057 | -122.9691 | -123.0377
1490.9688 | 122.937 | -0.22888 | 122.699 | 0.053405 | 0.012604 | 0.024139 | 0.033112 | -0.0038452 | -0.0029906 | 0.03183 | -0.14191 | -0.10986 | -0.26093 | 118.5516 | 118.3456 | 112.5 | 1.1261 | -0.07782 | 122.7997 | -0.3479 | -0.032043 | -122.8088 | 0.086975 | 118.7805 | -4.3533 | -0.11902 | 0.10071 | 0.11902 | 1.355 | 0.15106 | 118.5745 | 0.11902 | 0.086975 | 123.0286 | 112.7289 | -0.11902 | 0.11902 | 0.086975 | 112.7289 | 118.5745 | 123.0286 | -122.9599 | -123.0469
1491.9688 | 122.9187 | -0.23804 | 122.6807 | 0.022888 | 0.010895 | 0.021576 | 0.033966 | 0 | -0.0012818 | 0.029053 | -0.15564 | -0.1236 | -0.27924 | 118.6111 | 118.4143 | 112.5412 | 0.97504 | -0.07782 | 122.7905 | -0.3479 | -0.041199 | -122.8043 | 0.082397 | 118.8492 | -4.2664 | -0.10986 | 0.10986 | 0.1236 | 1.2131 | 0.16022 | 118.6523 | 0.11444 | 0.082397 | 123.0286 | 112.7792 | -0.10986 | 0.11444 | 0.082397 | 112.7792 | 118.6523 | 123.0286 | -122.9599 | -123.0286
1492.9688 | 122.8958 | -0.22888 | 122.7448 | -0.038147 | 0.01239 | 0.019653 | 0.02948 | -0.003418 | -0.003418 | 0.030334 | -0.19226 | -0.07782 | -0.25177 | 118.5242 | 118.3411 | 112.5046 | 0.86975 | -0.10986 | 122.7997 | -0.33875 | -0.022888 | -122.8226 | 0.036621 | 118.7531 | -4.4037 | -0.10986 | 0.054932 | 0.059509 | 1.0986 | 0.11902 | 118.5699 | 0.15106 | 0.036621 | 123.0286 | 112.7335 | -0.10986 | 0.15106 | 0.036621 | 112.7335 | 118.5699 | 123.0286 | -122.9965 | -123.0835
1493.9688 | 122.8867 | -0.23346 | 122.7173 | 0.16785 | 0.0091858 | 0.016663 | 0.032684 | -0.0038452 | -0.0023498 | 0.031616 | -0.17853 | -0.068665 | -0.23346 | 118.5837 | 118.4006 | 112.5366 | 1.1307 | -0.10529 | 122.7905 | -0.33417 | 0 | -122.7859 | 0.054931 | 118.8171 | -4.3167 | -0.10071 | 0.073242 | 0.054931 | 1.3641 | 0.12817 | 118.634 | 0.16479 | 0.054931 | 123.024 | 112.7701 | -0.10071 | 0.16479 | 0.054931 | 112.7701 | 118.634 | 123.024 | -122.9507 | -123.0515
1494.9688 | 122.9462 | -0.20599 | 122.6898 | 0.022888 | 0.0087586 | 0.019653 | 0.033539 | 0.0040588 | 0.0036316 | 0.044434 | -0.1236 | -0.10529 | -0.27008 | 107.3135 | 107.1442 | 102.3331 | 1.9913 | -0.054932 | 122.818 | -0.31586 | -0.064087 | -122.7951 | 0.082398 | 107.5195 | -15.5457 | -0.10986 | 0.12817 | 0.14649 | 2.1973 | 0.15106 | 107.3502 | 0.10071 | 0.082398 | 123.024 | 102.5391 | -0.10986 | 0.10071 | 0.082398 | 102.5391 | 107.3502 | 123.024 | -122.9599 | -123.0057
1495.9688 | 122.9324 | -0.23346 | 122.6944 | 0.083923 | 0.013031 | 0.020721 | 0.033966 | -0.0025636 | -0.0025634 | 0.02948 | -0.1236 | -0.1236 | -0.27008 | 118.4601 | 118.2632 | 112.4405 | 0.75073 | -0.073242 | 122.7859 | -0.32959 | -0.036622 | -122.818 | 0.10986 | 118.6935 | -4.4312 | -0.096131 | 0.091553 | 0.14649 | 0.98419 | 0.16022 | 118.4967 | 0.10986 | 0.10986 | 123.0194 | 112.6739 | -0.096131 | 0.10986 | 0.10986 | 112.6739 | 118.4967 | 123.0194 | -122.9645 | -123.024
1496.9688 | 122.9279 | -0.23804 | 122.7036 | 0.045776 | 0.0093994 | 0.02179 | 0.033325 | -0.0012818 | -0.0029906 | 0.032043 | -0.1236 | -0.1236 | -0.27466 | 118.5242 | 118.3411 | 112.5412 | 0.79193 | -0.07782 | 122.8226 | -0.32959 | -0.036621 | -122.8271 | 0.11444 | 118.7622 | -4.3625 | -0.091553 | 0.11902 | 0.15106 | 1.03 | 0.16022 | 118.5791 | 0.11444 | 0.11444 | 123.0606 | 112.7792 | -0.091553 | 0.11444 | 0.11444 | 112.7792 | 118.5791 | 123.0606 | -122.9782 | -123.0331
1497.9688 | 122.9233 | -0.21515 | 122.6898 | 0.038147 | 0.0081178 | 0.023071 | 0.033753 | -0.0010682 | -0.002777 | 0.030975 | -0.15106 | -0.1236 | -0.28839 | 118.5242 | 118.3456 | 112.5687 | 1.1581 | -0.068665 | 122.7722 | -0.35706 | -0.073242 | -122.8134 | 0.064087 | 118.7393 | -4.3442 | -0.14191 | 0.082398 | 0.13733 | 1.3733 | 0.14648 | 118.5608 | 0.091553 | 0.064087 | 122.9874 | 112.7838 | -0.14191 | 0.091553 | 0.064087 | 112.7838 | 118.5608 | 122.9874 | -122.9782 | -123.0469
1498.9688 | 122.9324 | -0.24719 | 122.6852 | 0.030518 | 0.010468 | 0.023926 | 0.03183 | -0.00235 | -0.001068 | 0.029053 | -0.16022 | -0.14648 | -0.28381 | 118.5333 | 118.4967 | 112.7792 | 1.2085 | -0.07782 | 122.7859 | -0.35248 | -0.036621 | -122.8317 | 0.086975 | 118.7805 | -4.1885 | -0.10529 | 0.10071 | 0.1236 | 1.4557 | 0.16937 | 118.7439 | 0.10071 | 0.086975 | 123.0331 | 113.0264 | -0.10529 | 0.10071 | 0.086975 | 113.0264 | 118.7439 | 123.0331 | -122.9691 | -123.0377
1499.9688 | 122.905 | -0.24261 | 122.699 | -0.045776 | 0.010468 | 0.021149 | 0.029266 | -0.0032044 | -0.004486 | 0.030334 | -0.18768 | -0.09613 | -0.26093 | 118.5287 | 118.3777 | 112.6602 | 1.2039 | -0.10071 | 122.8271 | -0.34332 | -0.01831 | -122.7951 | 0.054932 | 118.7714 | -4.3213 | -0.10071 | 0.12817 | 0.073242 | 1.4465 | 0.14191 | 118.6203 | 0.14649 | 0.054932 | 123.0698 | 112.9028 | -0.10071 | 0.14649 | 0.054932 | 112.9028 | 118.6203 | 123.0698 | -122.9599 | -123.0423
1500.9688 | 122.9141 | -0.22888 | 122.7219 | 1.2894 | 0.012177 | 0.023499 | 0.031189 | -0.0027772 | -0.0049134 | 0.02948 | -0.16937 | -0.068665 | -0.24719 | 118.5837 | 118.3868 | 112.7197 | 1.2405 | -0.11902 | 122.8363 | -0.33875 | -0.01831 | -122.7905 | 0.059509 | 118.8126 | -4.335 | -0.10986 | 0.11444 | 0.077819 | 1.4694 | 0.10986 | 118.6157 | 0.16022 | 0.059509 | 123.0652 | 112.9486 | -0.10986 | 0.16022 | 0.059509 | 112.9486 | 118.6157 | 123.0652 | -122.9691 | -123.0606
1501.9688 | 122.937 | -0.19684 | 122.6852 | 0.091552 | 0.010681 | 0.024139 | 0.032684 | -0.00235 | -0.001709 | 0.029694 | -0.13733 | -0.1236 | -0.27924 | 118.6111 | 118.4143 | 112.8845 | 1.5518 | -0.086975 | 122.7997 | -0.34332 | -0.082398 | -122.8088 | 0.059509 | 118.808 | -4.2709 | -0.14648 | 0.11444 | 0.14191 | 1.7487 | 0.10986 | 118.6111 | 0.073242 | 0.059509 | 122.9965 | 113.0814 | -0.14648 | 0.073242 | 0.059509 | 113.0814 | 118.6111 | 122.9965 | -122.9645 | -123.0286
1502.9688 | 122.9462 | -0.24261 | 122.6761 | 0.030518 | 0.011749 | 0.023712 | 0.032684 | -0.0012818 | -0.0021362 | 0.030121 | -0.14648 | -0.15564 | -0.27466 | 118.6523 | 118.4463 | 112.8433 | 1.5747 | -0.073242 | 122.8043 | -0.32959 | -0.032043 | -122.8317 | 0.096131 | 118.895 | -4.2297 | -0.086975 | 0.12817 | 0.12817 | 1.8173 | 0.16937 | 118.689 | 0.086975 | 0.096131 | 123.0469 | 113.0859 | -0.086975 | 0.086975 | 0.096131 | 113.0859 | 118.689 | 123.0469 | -122.9507 | -123.0057
1503.9688 | 122.9416 | -0.25177 | 122.6852 | 0.061035 | 0.01004 | 0.022858 | 0.032684 | -0.0025636 | -0.0029906 | 0.02948 | -0.16479 | -0.1236 | -0.2655 | 118.689 | 118.4967 | 112.8571 | 1.4282 | -0.09613 | 122.7951 | -0.3479 | -0.013733 | -122.8088 | 0.086975 | 118.9407 | -4.1885 | -0.09613 | 0.10986 | 0.10071 | 1.68 | 0.15564 | 118.7485 | 0.12817 | 0.086975 | 123.0469 | 113.1088 | -0.09613 | 0.12817 | 0.086975 | 113.1088 | 118.7485 | 123.0469 | -122.9507 | -123.0331
1504.9688 | 122.9279 | -0.24261 | 122.6761 | 0.022888 | 0.01004 | 0.023926 | 0.032044 | -0.0029908 | -0.0023498 | 0.031403 | -0.17853 | -0.13733 | -0.27924 | 118.6752 | 118.483 | 112.8525 | 1.6159 | -0.10071 | 122.7997 | -0.35706 | -0.036621 | -122.8134 | 0.064087 | 118.9178 | -4.1931 | -0.11444 | 0.1236 | 0.10071 | 1.8585 | 0.14191 | 118.7256 | 0.10529 | 0.064087 | 123.0423 | 113.0951 | -0.11444 | 0.10529 | 0.064087 | 113.0951 | 118.7256 | 123.0423 | -122.9553 | -123.0331
1505.9688 | 122.937 | -0.24261 | 122.6944 | 0.007629 | 0.0093994 | 0.022217 | 0.031189 | -0.0032044 | -0.0032044 | 0.030548 | -0.1831 | -0.13275 | -0.27008 | 118.634 | 118.4692 | 112.8937 | 1.8723 | -0.091553 | 122.8043 | -0.37079 | -0.027466 | -122.8271 | 0.05951 | 118.8766 | -4.2252 | -0.12817 | 0.10986 | 0.086976 | 2.1149 | 0.15106 | 118.7119 | 0.10986 | 0.05951 | 123.0469 | 113.1363 | -0.12817 | 0.10986 | 0.05951 | 113.1363 | 118.7119 | 123.0469 | -122.9645 | -123.0652
1506.9688 | 122.8912 | -0.2243 | 122.731 | 0.23651 | 0.0093994 | 0.021362 | 0.03183 | -0.0055542 | -0.0019226 | 0.030975 | -0.17853 | -0.07782 | -0.20599 | 118.5974 | 118.4189 | 112.8571 | 1.767 | -0.10071 | 122.8226 | -0.34332 | 0.01831 | -122.8088 | 0.045776 | 118.8217 | -4.3121 | -0.11902 | 0.091553 | 0.027466 | 1.9913 | 0.1236 | 118.6432 | 0.14648 | 0.045776 | 123.0469 | 113.0814 | -0.11902 | 0.14648 | 0.045776 | 113.0814 | 118.6432 | 123.0469 | -122.937 | -123.0743
1507.9688 | 122.905 | -0.24261 | 122.7402 | 1.3657 | 0.01239 | 0.016876 | 0.030335 | -0.0042726 | -0.001068 | 0.030762 | -0.16022 | -0.086975 | -0.23346 | 118.4509 | 118.2861 | 112.7792 | 2.3849 | -0.1236 | 122.8088 | -0.36621 | 0.009156 | -122.8271 | 0.082398 | 118.6935 | -4.454 | -0.1236 | 0.068665 | 0.073242 | 2.6276 | 0.11902 | 118.5287 | 0.15564 | 0.082398 | 123.0515 | 113.0219 | -0.1236 | 0.15564 | 0.082398 | 113.0219 | 118.5287 | 123.0515 | -122.9736 | -123.1064
1508.9688 | 122.937 | -0.23346 | 122.7081 | 0.099182 | 0.0098268 | 0.022858 | 0.032898 | -0.0032044 | -0.0029906 | 0.030334 | -0.13275 | -0.1236 | -0.25177 | 118.7347 | 118.5471 | 113.0859 | 2.536 | -0.054932 | 122.8088 | -0.34332 | -0.018311 | -122.8317 | 0.10071 | 118.9682 | -4.1611 | -0.10986 | 0.10071 | 0.11902 | 2.7695 | 0.17853 | 118.7805 | 0.10986 | 0.10071 | 123.0423 | 113.3194 | -0.10986 | 0.10986 | 0.10071 | 113.3194 | 118.7805 | 123.0423 | -122.9599 | -123.0515
1509.9688 | 122.9553 | -0.21973 | 122.7081 | 0.068664 | 0.010895 | 0.027344 | 0.033325 | -0.0021364 | -0.0014954 | 0.030548 | -0.1236 | -0.14191 | -0.27466 | 118.6615 | 118.4921 | 113.0127 | 2.655 | -0.073242 | 122.8088 | -0.32959 | -0.054931 | -122.85 | 0.096131 | 118.8812 | -4.216 | -0.10986 | 0.10071 | 0.15106 | 2.8748 | 0.14649 | 118.7119 | 0.07782 | 0.096131 | 123.0286 | 113.2324 | -0.10986 | 0.07782 | 0.096131 | 113.2324 | 118.7119 | 123.0286 | -122.9828 | -123.0377
1510.9688 | 122.9095 | -0.2243 | 122.7081 | 0.076294 | 0.011749 | 0.023071 | 0.03418 | -0.0008546 | -0.0006408 | 0.030548 | -0.13733 | -0.13733 | -0.2655 | 118.5379 | 118.364 | 112.912 | 2.5772 | -0.082397 | 122.7997 | -0.34332 | -0.041199 | -122.8455 | 0.086975 | 118.7622 | -4.3442 | -0.11902 | 0.091553 | 0.12817 | 2.8015 | 0.14191 | 118.5883 | 0.086975 | 0.086975 | 123.024 | 113.1363 | -0.11902 | 0.086975 | 0.086975 | 113.1363 | 118.5883 | 123.024 | -122.9736 | -123.0515
1511.9688 | 122.9416 | -0.24719 | 122.6807 | 0.076294 | 0.0098268 | 0.021576 | 0.033325 | -0.0002136 | -0.003418 | 0.031403 | -0.13275 | -0.14648 | -0.28381 | 118.6752 | 118.4875 | 113.0768 | 3.2318 | -0.086975 | 122.7951 | -0.33875 | -0.036621 | -122.8271 | 0.11444 | 118.9224 | -4.1931 | -0.091553 | 0.11444 | 0.15106 | 3.479 | 0.16022 | 118.7347 | 0.10071 | 0.11444 | 123.0423 | 113.324 | -0.091553 | 0.10071 | 0.11444 | 113.324 | 118.7347 | 123.0423 | -122.9645 | -123.0194
1512.9688 | 122.9599 | -0.2243 | 122.7036 | 0.045776 | 0.011108 | 0.020721 | 0.034607 | -0.0021364 | -0.0014954 | 0.031189 | -0.14191 | -0.14191 | -0.27466 | 118.7851 | 118.5745 | 113.1226 | 2.7695 | -0.082397 | 122.8134 | -0.35248 | -0.050354 | -122.8455 | 0.082397 | 119.0094 | -4.129 | -0.12817 | 0.10986 | 0.13275 | 2.9938 | 0.14191 | 118.7988 | 0.082397 | 0.082397 | 123.0377 | 113.3469 | -0.12817 | 0.082397 | 0.082397 | 113.3469 | 118.7988 | 123.0377 | -122.9782 | -123.056
1513.9688 | 122.9141 | -0.2655 | 122.7081 | 0 | 0.0098268 | 0.023926 | 0.030121 | -0.001709 | -0.002777 | 0.028625 | -0.17853 | -0.12817 | -0.28381 | 118.5196 | 118.3411 | 112.999 | 3.4378 | -0.1236 | 122.818 | -0.35706 | -0.01831 | -122.8363 | 0.086975 | 118.7851 | -4.3671 | -0.091553 | 0.10986 | 0.10528 | 3.7033 | 0.14191 | 118.6066 | 0.13733 | 0.086975 | 123.0835 | 113.2645 | -0.091553 | 0.13733 | 0.086975 | 113.2645 | 118.6066 | 123.0835 | -122.9919 | -123.0652
1514.9688 | 122.9233 | -0.27924 | 122.7036 | 0.068664 | 0.0070496 | 0.020721 | 0.03183 | -0.0032044 | -0.0002136 | 0.030975 | -0.16479 | -0.12817 | -0.28839 | 118.4555 | 118.2587 | 112.9257 | 3.9825 | -0.13733 | 122.8317 | -0.37079 | -0.009155 | -122.8317 | 0.11444 | 118.7347 | -4.4449 | -0.091553 | 0.12817 | 0.1236 | 4.2618 | 0.14191 | 118.5379 | 0.15106 | 0.11444 | 123.111 | 113.205 | -0.091553 | 0.15106 | 0.11444 | 113.205 | 118.5379 | 123.111 | -122.9919 | -123.0743
1515.9688 | 122.9324 | -0.21973 | 122.7081 | -0.38147 | 0.011536 | 0.025421 | 0.035034 | -0.003418 | -0.0023498 | 0.032043 | -0.11902 | -0.073242 | -0.19684 | 118.428 | 118.2175 | 112.9166 | 3.9871 | -0.064087 | 122.8134 | -0.33417 | 0.022889 | -122.7814 | 0.10071 | 118.6478 | -4.4907 | -0.11444 | 0.10529 | 0.077819 | 4.2068 | 0.15564 | 118.4372 | 0.14649 | 0.10071 | 123.0331 | 113.1363 | -0.11444 | 0.14649 | 0.10071 | 113.1363 | 118.4372 | 123.0331 | -122.905 | -123.0423
1516.9688 | 122.9553 | -0.2243 | 122.7036 | -0.57983 | 0.009613 | 0.021576 | 0.033966 | -0.0010682 | -0.0021362 | 0.030762 | -0.11902 | -0.068665 | -0.17853 | 118.634 | 118.4463 | 113.15 | 4.0558 | -0.082397 | 122.8271 | -0.34332 | 0.045776 | -122.7722 | 0.10529 | 118.8583 | -4.2572 | -0.11902 | 0.1236 | 0.059509 | 4.2801 | 0.14191 | 118.6707 | 0.15564 | 0.10529 | 123.0515 | 113.3743 | -0.11902 | 0.15564 | 0.10529 | 113.3743 | 118.6707 | 123.0515 | -122.8821 | -123.0469
1517.9688 | 122.9187 | -0.21515 | 122.699 | -0.45776 | 0.012177 | 0.021362 | 0.033753 | -0.0021364 | -0.002777 | 0.030762 | -0.10071 | -0.073242 | -0.19226 | 118.6478 | 118.428 | 113.1912 | 4.4952 | -0.091553 | 122.8088 | -0.35248 | 0.022888 | -122.7722 | 0.11444 | 118.8629 | -4.2709 | -0.13733 | 0.10986 | 0.091553 | 4.7104 | 0.1236 | 118.6432 | 0.14191 | 0.11444 | 123.024 | 113.4064 | -0.13733 | 0.14191 | 0.11444 | 113.4064 | 118.6432 | 123.024 | -122.8912 | -123.0515
1518.9688 | 122.9416 | -0.2243 | 122.7173 | -0.4425 | 0.011322 | 0.020508 | 0.033325 | -0.0004274 | -0.0025634 | 0.033325 | -0.09613 | -0.045776 | -0.17395 | 118.6111 | 118.4372 | 113.2278 | 4.8294 | -0.07782 | 122.8043 | -0.34332 | 0.050354 | -122.7631 | 0.12817 | 118.8354 | -4.2801 | -0.11902 | 0.086975 | 0.07782 | 5.0537 | 0.14648 | 118.6615 | 0.17853 | 0.12817 | 123.0286 | 113.4521 | -0.11902 | 0.17853 | 0.12817 | 113.4521 | 118.6615 | 123.0286 | -122.8912 | -123.0606
1519.9688 | 122.9233 | -0.2243 | 122.6852 | -0.0076295 | 0.010681 | 0.022217 | 0.032898 | -0.0027772 | -0.0023498 | 0.032471 | -0.11444 | -0.064087 | -0.17853 | 118.602 | 118.4097 | 113.237 | 4.6829 | -0.07782 | 122.8271 | -0.33417 | 0.045776 | -122.7493 | 0.10986 | 118.8263 | -4.2755 | -0.10986 | 0.14191 | 0.064087 | 4.9072 | 0.14648 | 118.634 | 0.16022 | 0.10986 | 123.0515 | 113.4613 | -0.10986 | 0.16022 | 0.10986 | 113.4613 | 118.634 | 123.0515 | -122.8638 | -123.0194
1520.9688 | 122.9507 | -0.25177 | 122.6852 | 0.11444 | 0.01239 | 0.019226 | 0.032257 | -0.0027772 | -0.0014954 | 0.030975 | -0.13733 | -0.14648 | -0.3067 | 118.7393 | 118.5379 | 113.3789 | 4.7562 | -0.082397 | 122.8271 | -0.36163 | -0.054932 | -122.8317 | 0.11444 | 118.9911 | -4.1473 | -0.10986 | 0.14191 | 0.16937 | 5.0079 | 0.16937 | 118.7897 | 0.10529 | 0.11444 | 123.0789 | 113.6307 | -0.10986 | 0.10529 | 0.11444 | 113.6307 | 118.7897 | 123.0789 | -122.9919 | -123.0469
1521.9688 | 122.9462 | -0.23346 | 122.7219 | 0.1297 | 0.011108 | 0.020508 | 0.033112 | 0 | -0.0014954 | 0.030762 | -0.1236 | -0.12817 | -0.30212 | 118.6661 | 118.4967 | 113.3148 | 5.2826 | -0.07782 | 122.7997 | -0.34332 | -0.068665 | -122.85 | 0.10986 | 118.8995 | -4.2252 | -0.10986 | 0.07782 | 0.17853 | 5.5161 | 0.15564 | 118.7302 | 0.10528 | 0.10986 | 123.0331 | 113.5483 | -0.10986 | 0.10528 | 0.10986 | 113.5483 | 118.7302 | 123.0331 | -123.024 | -123.0652
1522.9688 | 122.9095 | -0.2655 | 122.6944 | 0.25177 | 0.01239 | 0.027771 | 0.033753 | -0.0019226 | -0.0038452 | 0.02948 | -0.16479 | -0.13275 | -0.29297 | 118.6157 | 118.4189 | 113.3514 | 5.5801 | -0.15106 | 122.818 | -0.39368 | -0.027466 | -122.8271 | 0.10071 | 118.8812 | -4.2755 | -0.12817 | 0.1236 | 0.12817 | 5.8456 | 0.11444 | 118.6844 | 0.13275 | 0.10071 | 123.0835 | 113.6169 | -0.12817 | 0.13275 | 0.10071 | 113.6169 | 118.6844 | 123.0835 | -122.9874 | -123.0881
1523.9688 | 122.9324 | -0.23346 | 122.699 | 0.24414 | 0.010895 | 0.02243 | 0.034393 | 0.0002136 | -0.004486 | 0.028412 | -0.15564 | -0.15106 | -0.28839 | 118.6432 | 118.4647 | 113.3102 | 5.3055 | -0.15106 | 122.8409 | -0.37537 | -0.054932 | -122.85 | 0.077819 | 118.8766 | -4.2343 | -0.14191 | 0.14191 | 0.13275 | 5.5389 | 0.082397 | 118.6981 | 0.082397 | 0.077819 | 123.0743 | 113.5437 | -0.14191 | 0.082397 | 0.077819 | 113.5437 | 118.6981 | 123.0743 | -122.9874 | -123.0743
1524.9688 | 122.9187 | -0.24719 | 122.6944 | 0.22888 | 0.010895 | 0.024353 | 0.034393 | -0.0008546 | -0.0029906 | 0.029907 | -0.16479 | -0.14191 | -0.30212 | 118.5837 | 118.3868 | 113.2599 | 5.6076 | -0.12817 | 122.8134 | -0.37079 | -0.054932 | -122.8363 | 0.082397 | 118.8309 | -4.3076 | -0.1236 | 0.11902 | 0.13733 | 5.8548 | 0.11902 | 118.634 | 0.10528 | 0.082397 | 123.0606 | 113.5071 | -0.1236 | 0.10528 | 0.082397 | 113.5071 | 118.634 | 123.0606 | -122.9965 | -123.0652
1525.9688 | 122.9095 | -0.26093 | 122.6944 | 0.3128 | 0.011536 | 0.023071 | 0.032684 | 0.0002136 | -0.0012818 | 0.030334 | -0.16479 | -0.15106 | -0.27466 | 118.5654 | 118.3731 | 113.3102 | 5.6808 | -0.16479 | 122.8363 | -0.3891 | -0.013733 | -122.8455 | 0.09613 | 118.8263 | -4.3213 | -0.12817 | 0.14191 | 0.10986 | 5.9418 | 0.09613 | 118.634 | 0.10986 | 0.09613 | 123.0972 | 113.5712 | -0.12817 | 0.10986 | 0.09613 | 113.5712 | 118.634 | 123.0972 | -122.9691 | -123.0835
1526.9688 | 122.8912 | -0.25635 | 122.6898 | 0.22125 | 0.012817 | 0.024139 | 0.035034 | -0.0008546 | -0.005127 | 0.029266 | -0.16479 | -0.13733 | -0.29297 | 118.5013 | 118.3044 | 113.3011 | 6.0654 | -0.16022 | 122.818 | -0.36621 | -0.036621 | -122.8271 | 0.091553 | 118.7576 | -4.3854 | -0.10986 | 0.12817 | 0.12817 | 6.3217 | 0.096131 | 118.5608 | 0.11902 | 0.091553 | 123.0743 | 113.5574 | -0.10986 | 0.11902 | 0.091553 | 113.5574 | 118.5608 | 123.0743 | -122.9828 | -123.056
1527.9688 | 122.9462 | -0.23804 | 122.6944 | -0.076294 | 0.011963 | 0.026917 | 0.032898 | -0.0019226 | -0.001068 | 0.030975 | -0.086975 | -0.073242 | -0.20599 | 118.5013 | 118.3273 | 113.3286 | 6.1615 | -0.07782 | 122.8134 | -0.3479 | 0.032043 | -122.7676 | 0.15106 | 118.7393 | -4.3671 | -0.10986 | 0.11902 | 0.11902 | 6.3995 | 0.16022 | 118.5654 | 0.16479 | 0.15106 | 123.0515 | 113.5666 | -0.10986 | 0.16479 | 0.15106 | 113.5666 | 118.5654 | 123.0515 | -122.9004 | -123.0423
1528.9688 | 122.9095 | -0.24719 | 122.6944 | 0.25177 | 0.011963 | 0.020935 | 0.033112 | -0.003418 | -0.0040588 | 0.03183 | -0.18768 | -0.12817 | -0.27924 | 118.5974 | 118.3914 | 113.4521 | 6.0745 | -0.15564 | 122.7951 | -0.37994 | -0.032044 | -122.8226 | 0.059509 | 118.8446 | -4.303 | -0.13275 | 0.10071 | 0.091553 | 6.3217 | 0.091552 | 118.6386 | 0.11902 | 0.059509 | 123.0423 | 113.6993 | -0.13275 | 0.11902 | 0.059509 | 113.6993 | 118.6386 | 123.0423 | -122.9736 | -123.0743
1529.9688 | 122.8592 | -0.2655 | 122.6898 | 0.28229 | 0.012604 | 0.022217 | 0.033966 | -0.0029908 | -0.002777 | 0.030975 | -0.20142 | -0.14191 | -0.28381 | 118.5471 | 118.3685 | 113.4247 | 6.0287 | -0.20599 | 122.85 | -0.37994 | -0.01831 | -122.8317 | 0.064087 | 118.8126 | -4.3213 | -0.11444 | 0.16022 | 0.082397 | 6.2943 | 0.059509 | 118.634 | 0.1236 | 0.064087 | 123.1155 | 113.6902 | -0.11444 | 0.1236 | 0.064087 | 113.6902 | 118.634 | 123.1155 | -122.9736 | -123.0698
1530.9688 | 122.8958 | -0.2655 | 122.699 | 0.27466 | 0.013886 | 0.023499 | 0.033539 | -0.0008546 | -0.0014954 | 0.032898 | -0.20142 | -0.13733 | -0.29755 | 118.5608 | 118.3823 | 113.4476 | 6.0013 | -0.20142 | 122.8134 | -0.36621 | -0.032043 | -122.8363 | 0.064087 | 118.8263 | -4.3167 | -0.10071 | 0.11444 | 0.09613 | 6.2668 | 0.064087 | 118.6478 | 0.12817 | 0.064087 | 123.0789 | 113.7131 | -0.10071 | 0.12817 | 0.064087 | 113.7131 | 118.6478 | 123.0789 | -122.9965 | -123.0652
1531.9688 | 122.8683 | -0.25177 | 122.699 | 0.32043 | 0.011108 | 0.025208 | 0.033325 | -0.001709 | -0.0036316 | 0.030548 | -0.19226 | -0.12817 | -0.30212 | 118.5974 | 118.4189 | 113.4155 | 5.9189 | -0.20142 | 122.8409 | -0.35706 | -0.050354 | -122.8271 | 0.059509 | 118.8492 | -4.2801 | -0.10529 | 0.14191 | 0.10986 | 6.1707 | 0.050354 | 118.6707 | 0.1236 | 0.059509 | 123.0927 | 113.6673 | -0.10529 | 0.1236 | 0.059509 | 113.6673 | 118.6707 | 123.0927 | -123.0011 | -123.056
1532.9688 | 122.8775 | -0.2655 | 122.7036 | 0.32806 | 0.012817 | 0.023071 | 0.033753 | -0.0027772 | -0.0019226 | 0.02948 | -0.19226 | -0.15106 | -0.31586 | 118.6249 | 118.4143 | 113.4201 | 5.7587 | -0.19226 | 122.8317 | -0.37537 | -0.050354 | -122.8546 | 0.073242 | 118.8904 | -4.2892 | -0.10986 | 0.12817 | 0.1236 | 6.0242 | 0.073242 | 118.6798 | 0.11444 | 0.073242 | 123.0972 | 113.6856 | -0.10986 | 0.11444 | 0.073242 | 113.6856 | 118.6798 | 123.0972 | -123.0194 | -123.0789
1533.9688 | 122.8592 | -0.27466 | 122.7127 | 0.28992 | 0.01239 | 0.025208 | 0.033325 | 0.0070494 | 0.0040588 | 0.04657 | -0.21057 | -0.13733 | -0.32044 | 103.0426 | 102.8503 | 98.822 | 15.0009 | -0.21057 | 122.8363 | -0.38452 | -0.045777 | -122.85 | 0.064087 | 103.3173 | -19.8624 | -0.10986 | 0.1236 | 0.10986 | 15.2756 | 0.064087 | 103.125 | 0.13733 | 0.064087 | 123.111 | 99.0967 | -0.10986 | 0.13733 | 0.064087 | 99.0967 | 103.125 | 123.111 | -123.0331 | -123.0972
1534.9688 | 122.9187 | -0.25177 | 122.7036 | 0.26703 | 0.011749 | 0.025848 | 0.033112 | -0.001709 | -0.003418 | 0.02948 | -0.16937 | -0.14648 | -0.30212 | 118.7027 | 118.5242 | 113.5162 | 4.9576 | -0.15106 | 122.7905 | -0.37079 | -0.050354 | -122.85 | 0.082397 | 118.9545 | -4.1794 | -0.11902 | 0.086975 | 0.13275 | 5.2094 | 0.10071 | 118.7759 | 0.10529 | 0.082397 | 123.0423 | 113.768 | -0.11902 | 0.10529 | 0.082397 | 113.768 | 118.7759 | 123.0423 | -123.0057 | -123.0743
1535.9688 | 122.8638 | -0.2655 | 122.6807 | 0.19836 | 0.013245 | 0.023285 | 0.032044 | -0.0014954 | -0.001709 | 0.029694 | -0.20142 | -0.14648 | -0.29755 | 118.602 | 118.428 | 113.4888 | 5.1086 | -0.20142 | 122.8363 | -0.39368 | -0.032043 | -122.8271 | 0.064087 | 118.8675 | -4.2526 | -0.12817 | 0.15564 | 0.09613 | 5.3741 | 0.064087 | 118.6935 | 0.11902 | 0.064087 | 123.1018 | 113.7543 | -0.12817 | 0.11902 | 0.064087 | 113.7543 | 118.6935 | 123.1018 | -122.9782 | -123.0743
1536.9688 | 122.9004 | -0.27008 | 122.6852 | -0.54932 | 0.012817 | 0.024139 | 0.033966 | -0.004059 | -0.001709 | 0.032471 | -0.18768 | -0.13275 | -0.27466 | 118.5425 | 118.3548 | 113.4201 | 4.8706 | -0.1831 | 122.8317 | -0.38452 | -0.004577 | -122.818 | 0.082398 | 118.8126 | -4.3304 | -0.11444 | 0.14648 | 0.086975 | 5.1407 | 0.086976 | 118.6249 | 0.13733 | 0.082398 | 123.1018 | 113.6902 | -0.11444 | 0.13733 | 0.082398 | 113.6902 | 118.6249 | 123.1018 | -122.9599 | -123.0698
1537.9688 | 122.9279 | -0.2655 | 122.7127 | 0.23651 | 0.013031 | 0.020721 | 0.033539 | -0.001709 | -0.001068 | 0.031403 | -0.33417 | -0.13733 | -0.3067 | 118.5196 | 118.3182 | 113.3972 | 4.8752 | -0.20142 | 122.8088 | -0.37994 | -0.041199 | -122.85 | -0.068664 | 118.7851 | -4.3945 | -0.11444 | 0.09613 | -0.027465 | 5.1407 | 0.064087 | 118.5837 | 0.12817 | -0.068664 | 123.0743 | 113.6627 | -0.11444 | 0.12817 | -0.068664 | 113.6627 | 118.5837 | 123.0743 | -123.0194 | -123.0927
1538.9688 | 122.9004 | -0.27924 | 122.6807 | 0.32806 | 0.010895 | 0.026489 | 0.02948 | -0.0008546 | -0.0021362 | 0.031189 | -0.21515 | -0.15106 | -0.28839 | 118.6981 | 118.4647 | 113.5941 | 4.5593 | -0.21515 | 122.8088 | -0.3891 | -0.009155 | -122.8317 | 0.064087 | 118.9774 | -4.216 | -0.10986 | 0.12817 | 0.073242 | 4.8386 | 0.064087 | 118.7439 | 0.12817 | 0.064087 | 123.0881 | 113.8733 | -0.10986 | 0.12817 | 0.064087 | 113.8733 | 118.7439 | 123.0881 | -122.9691 | -123.0698
1539.9688 | 122.9279 | -0.26093 | 122.6807 | 0.36621 | 0.012177 | 0.025848 | 0.038025 | -0.0029908 | -0.004486 | 0.03418 | -0.20142 | -0.15106 | -0.32501 | 118.5928 | 118.3777 | 113.5666 | 4.6921 | -0.16022 | 122.818 | -0.36621 | -0.064087 | -122.8317 | 0.059509 | 118.8538 | -4.303 | -0.10529 | 0.13733 | 0.1236 | 4.953 | 0.10071 | 118.6386 | 0.10986 | 0.059509 | 123.0789 | 113.8275 | -0.10529 | 0.10986 | 0.059509 | 113.8275 | 118.6386 | 123.0789 | -123.0057 | -123.0469
1540.9688 | 122.9324 | -0.25635 | 122.699 | 0.38147 | 0.013031 | 0.022003 | 0.032471 | -0.0021364 | -0.0006408 | 0.031616 | -0.21515 | -0.16022 | -0.3067 | 118.6111 | 118.6386 | 113.5071 | 4.8065 | -0.17853 | 122.8134 | -0.35706 | -0.050354 | -122.8592 | 0.041199 | 118.8675 | -4.0604 | -0.10071 | 0.11444 | 0.091553 | 5.0629 | 0.07782 | 118.895 | 0.096131 | 0.041199 | 123.0698 | 113.7634 | -0.10071 | 0.096131 | 0.041199 | 113.7634 | 118.895 | 123.0698 | -123.0057 | -123.056
1541.9688 | 122.8867 | -0.28839 | 122.6898 | 0.29755 | 0.011749 | 0.023926 | 0.033112 | -0.001709 | -0.001068 | 0.030762 | -0.20599 | -0.15564 | -0.31586 | 118.6066 | 118.4097 | 113.53 | 4.6738 | -0.18768 | 122.7814 | -0.40741 | -0.027466 | -122.8455 | 0.082397 | 118.895 | -4.2801 | -0.11902 | 0.091553 | 0.10986 | 4.9622 | 0.10071 | 118.6981 | 0.13275 | 0.082397 | 123.0698 | 113.8184 | -0.11902 | 0.13275 | 0.082397 | 113.8184 | 118.6981 | 123.0698 | -123.0057 | -123.0972
1542.9688 | 122.9233 | -0.24261 | 122.7036 | 0.33569 | 0.011108 | 0.022003 | 0.033112 | -0.0004274 | -0.001068 | 0.032898 | -0.24719 | -0.16479 | -0.32501 | 118.5516 | 118.3594 | 113.5025 | 4.4998 | -0.36163 | 122.8088 | -0.34332 | -0.082397 | -122.8683 | -0.004577 | 118.7943 | -4.3442 | -0.10071 | 0.10529 | 0.07782 | 4.7424 | -0.11902 | 118.602 | 0.07782 | -0.004577 | 123.0515 | 113.7451 | -0.10071 | 0.07782 | -0.004577 | 113.7451 | 118.602 | 123.0515 | -123.0286 | -123.0469
1543.9688 | 122.9141 | -0.28839 | 122.6807 | 0.36621 | 0.012817 | 0.026276 | 0.030975 | -0.001709 | -0.001068 | 0.030334 | -0.2243 | -0.17395 | -0.32044 | 118.5974 | 118.396 | 113.681 | 4.5181 | -0.20599 | 122.8363 | -0.40741 | -0.032044 | -122.8546 | 0.064087 | 118.8858 | -4.2847 | -0.11902 | 0.15564 | 0.096131 | 4.8065 | 0.082397 | 118.6844 | 0.11444 | 0.064087 | 123.1247 | 113.9694 | -0.11902 | 0.11444 | 0.064087 | 113.9694 | 118.6844 | 123.1247 | -123.0011 | -123.0881
1544.9688 | 122.9141 | -0.27924 | 122.6898 | 0.33569 | 0.010681 | 0.02478 | 0.03183 | -0.0012818 | -0.0025634 | 0.032684 | -0.2243 | -0.16022 | -0.32501 | 118.6661 | 118.4967 | 113.8687 | 4.4815 | -0.20599 | 122.7951 | -0.39368 | -0.045776 | -122.85 | 0.054932 | 118.9453 | -4.1931 | -0.11444 | 0.10529 | 0.10071 | 4.7607 | 0.073242 | 118.7759 | 0.11902 | 0.054932 | 123.0743 | 114.1479 | -0.11444 | 0.11902 | 0.054932 | 114.1479 | 118.7759 | 123.0743 | -123.0148 | -123.0835
1545.9688 | 122.9187 | -0.29297 | 122.6807 | 0.33569 | 0.0091858 | 0.023499 | 0.031403 | -0.0014954 | -0.0040588 | 0.029694 | -0.21973 | -0.16479 | -0.31586 | 118.7164 | 118.5196 | 113.8458 | 4.3762 | -0.20599 | 122.7997 | -0.39368 | -0.022888 | -122.8455 | 0.073242 | 119.0094 | -4.1611 | -0.10071 | 0.11902 | 0.09613 | 4.6692 | 0.086975 | 118.8126 | 0.12817 | 0.073242 | 123.0927 | 114.1388 | -0.10071 | 0.12817 | 0.073242 | 114.1388 | 118.8126 | 123.0927 | -122.9965 | -123.0743
1546.9688 | 122.937 | -0.28381 | 122.6807 | 0.46539 | 0.011963 | 0.01944 | 0.031403 | -0.0010682 | -0.001068 | 0.031403 | -0.2243 | -0.16022 | -0.31128 | 118.634 | 118.4418 | 113.7405 | 4.5868 | -0.20599 | 122.7676 | -0.39825 | -0.027466 | -122.8409 | 0.059509 | 118.9178 | -4.2389 | -0.11444 | 0.086975 | 0.086975 | 4.8706 | 0.077819 | 118.7256 | 0.1236 | 0.059509 | 123.0515 | 114.0244 | -0.11444 | 0.1236 | 0.059509 | 114.0244 | 118.7256 | 123.0515 | -122.9919 | -123.0789
1547.9688 | 122.8775 | -0.28839 | 122.699 | 0.2594 | 0.014099 | 0.02713 | 0.033325 | -0.0021364 | -0.0023498 | 0.033112 | -0.24261 | -0.17395 | -0.32044 | 118.6066 | 118.4006 | 113.7405 | 4.628 | -0.23804 | 122.7905 | -0.41657 | -0.032044 | -122.8729 | 0.045776 | 118.895 | -4.2984 | -0.12817 | 0.091552 | 0.07782 | 4.9164 | 0.050354 | 118.689 | 0.11444 | 0.045776 | 123.0789 | 114.0289 | -0.12817 | 0.11444 | 0.045776 | 114.0289 | 118.689 | 123.0789 | -123.0194 | -123.1155
1548.9688 | 122.8912 | -0.28381 | 122.7081 | 0.2594 | 0.011322 | 0.023071 | 0.035461 | -0.001709 | -0.0038452 | 0.031189 | -0.2243 | -0.16937 | -0.33417 | 118.602 | 118.4235 | 113.7909 | 4.628 | -0.23804 | 122.8088 | -0.3891 | -0.050354 | -122.8775 | 0.059509 | 118.8858 | -4.2847 | -0.10529 | 0.10071 | 0.10986 | 4.9118 | 0.045776 | 118.7073 | 0.11444 | 0.059509 | 123.0927 | 114.0747 | -0.10529 | 0.11444 | 0.059509 | 114.0747 | 118.7073 | 123.0927 | -123.0423 | -123.0972
1549.9688 | 122.9462 | -0.27924 | 122.6898 | 0.50354 | 0.011963 | 0.024994 | 0.031616 | -0.0019226 | -0.0036316 | 0.03183 | -0.21973 | -0.15564 | -0.32959 | 118.8126 | 118.6066 | 113.9832 | 4.4083 | -0.21057 | 122.8409 | -0.39368 | -0.050354 | -122.8455 | 0.059509 | 119.0918 | -4.0833 | -0.11444 | 0.15106 | 0.10986 | 4.6875 | 0.068665 | 118.8858 | 0.1236 | 0.059509 | 123.1201 | 114.2624 | -0.11444 | 0.1236 | 0.059509 | 114.2624 | 118.8858 | 123.1201 | -123.0194 | -123.0835
1550.9688 | 123.0057 | -0.26093 | 122.6486 | 0.38147 | 0.0098268 | 0.026489 | 0.032044 | -0.001709 | 0.0004272 | 0.030121 | -0.21057 | -0.1831 | -0.32044 | 118.7073 | 118.5059 | 113.8504 | 4.4724 | -0.13733 | 122.7859 | -0.3891 | -0.05951 | -122.8317 | 0.050354 | 118.9682 | -4.1428 | -0.12817 | 0.13733 | 0.10986 | 4.7333 | 0.1236 | 118.7668 | 0.07782 | 0.050354 | 123.0469 | 114.1113 | -0.12817 | 0.07782 | 0.050354 | 114.1113 | 118.7668 | 123.0469 | -122.9691 | -123.0377
1551.9688 | 122.9919 | -0.25177 | 122.644 | 0.3891 | 0.010895 | 0.020935 | 0.031189 | -0.0010682 | -0.0019226 | 0.029053 | -0.21515 | -0.1831 | -0.32501 | 118.7347 | 118.5516 | 113.9374 | 4.3808 | -0.14648 | 122.7676 | -0.38452 | -0.073242 | -122.8271 | 0.036621 | 118.9865 | -4.0924 | -0.13275 | 0.1236 | 0.10986 | 4.6326 | 0.10529 | 118.8034 | 0.068665 | 0.036621 | 123.0194 | 114.1891 | -0.13275 | 0.068665 | 0.036621 | 114.1891 | 118.8034 | 123.0194 | -122.9691 | -123.0286
1552.9688 | 122.9645 | -0.27466 | 122.644 | 0.42725 | 0.013245 | 0.023499 | 0.032471 | -0.0027772 | -0.001709 | 0.031403 | -0.20599 | -0.18768 | -0.32501 | 118.7668 | 118.5699 | 113.9282 | 4.454 | -0.15106 | 122.7859 | -0.37994 | -0.050354 | -122.8317 | 0.068664 | 119.0414 | -4.0741 | -0.10529 | 0.14191 | 0.11902 | 4.7287 | 0.1236 | 118.8446 | 0.086975 | 0.068664 | 123.0606 | 114.2029 | -0.10529 | 0.086975 | 0.068664 | 114.2029 | 118.8446 | 123.0606 | -122.9691 | -123.024
1553.9688 | 122.9736 | -0.27466 | 122.6624 | 0.40436 | 0.011749 | 0.025208 | 0.033112 | -0.0032044 | -0.0025634 | 0.029694 | -0.21973 | -0.17395 | -0.32501 | 118.6478 | 118.4601 | 113.8138 | 4.5547 | -0.15564 | 122.7722 | -0.38452 | -0.050354 | -122.8363 | 0.054931 | 118.9224 | -4.2023 | -0.10986 | 0.10986 | 0.10529 | 4.8294 | 0.11902 | 118.7347 | 0.10071 | 0.054931 | 123.0469 | 114.0884 | -0.10986 | 0.10071 | 0.054931 | 114.0884 | 118.7347 | 123.0469 | -122.9874 | -123.0469
1554.9688 | 122.9187 | -0.29297 | 122.6715 | -1.9608 | 0.009613 | 0.022644 | 0.031189 | -0.00235 | -0.001068 | 0.030334 | -0.27466 | -0.17395 | -0.29755 | 118.5745 | 118.3731 | 113.7268 | 4.6417 | -0.19684 | 122.7859 | -0.40283 | -0.004577 | -122.8455 | 0.018311 | 118.8675 | -4.2984 | -0.10986 | 0.11444 | 0.022888 | 4.9347 | 0.096131 | 118.6661 | 0.11902 | 0.018311 | 123.0789 | 114.0198 | -0.10986 | 0.11902 | 0.018311 | 114.0198 | 118.6661 | 123.0789 | -122.9691 | -123.0743
1555.9688 | 122.9233 | -0.28381 | 122.6898 | 1.9379 | 0.010254 | 0.021576 | 0.034607 | -0.0038452 | -0.002777 | 0.02948 | -0.059509 | -0.16937 | -0.30212 | 118.5425 | 118.3685 | 113.7543 | 4.7424 | -0.20142 | 122.8043 | -0.39368 | -0.018311 | -122.8592 | 0.2243 | 118.8263 | -4.3213 | -0.10986 | 0.11444 | 0.24261 | 5.0262 | 0.082397 | 118.6523 | 0.11444 | 0.2243 | 123.0881 | 114.0381 | -0.10986 | 0.11444 | 0.2243 | 114.0381 | 118.6523 | 123.0881 | -122.9919 | -123.0835
1556.9844 | 123.0331 | -0.2243 | 122.6578 | 0.083923 | 0.009613 | 0.020294 | 0.024353 | -0.0053406 | -0.0029906 | 0.032257 | -0.18768 | -0.20599 | -0.27924 | 118.7851 | 118.5883 | 113.9923 | 4.5181 | -0.013733 | 122.7493 | -0.33417 | -0.054932 | -122.8638 | 0.036621 | 119.0094 | -4.0695 | -0.10986 | 0.091553 | 0.091553 | 4.7424 | 0.21057 | 118.8126 | 0.01831 | 0.036621 | 122.9736 | 114.2166 | -0.10986 | 0.01831 | 0.036621 | 114.2166 | 118.8126 | 122.9736 | -122.937 | -122.9919
1557.9688 | 123.0423 | -0.23346 | 122.6624 | 0.48828 | 0.010895 | 0.022217 | 0.033966 | -0.004059 | -0.002777 | 0.031189 | -0.15106 | -0.21973 | -0.29755 | 118.8034 | 118.6111 | 114.0472 | 4.5456 | -0.086975 | 122.731 | -0.35706 | -0.064087 | -122.8821 | 0.082397 | 119.0369 | -4.0512 | -0.1236 | 0.068664 | 0.14648 | 4.7791 | 0.14648 | 118.8446 | 0.013732 | 0.082397 | 122.9645 | 114.2807 | -0.1236 | 0.013732 | 0.082397 | 114.2807 | 118.8446 | 122.9645 | -122.9599 | -123.0194
1558.9688 | 123.0515 | -0.22888 | 122.6532 | 0.49591 | 0.0089722 | 0.019867 | 0.033539 | -0.0057678 | -0.0032044 | 0.031189 | -0.15564 | -0.21057 | -0.30212 | 118.7119 | 118.5196 | 114.006 | 4.4724 | -0.073242 | 122.7173 | -0.37994 | -0.073242 | -122.8638 | 0.073242 | 118.9407 | -4.1336 | -0.15106 | 0.064087 | 0.14648 | 4.7012 | 0.15564 | 118.7485 | 0.018311 | 0.073242 | 122.9462 | 114.2349 | -0.15106 | 0.018311 | 0.073242 | 114.2349 | 118.7485 | 122.9462 | -122.9553 | -123.0331
1559.9688 | 123.0469 | -0.23804 | 122.6395 | 0.50354 | 0.01239 | 0.023285 | 0.033753 | -0.0061952 | -0.0021362 | 0.028839 | -0.14648 | -0.20599 | -0.29755 | 118.7119 | 118.5104 | 113.9603 | 4.5685 | -0.091553 | 122.7219 | -0.35706 | -0.059509 | -122.8455 | 0.091553 | 118.9499 | -4.129 | -0.11902 | 0.082398 | 0.15106 | 4.8065 | 0.14648 | 118.7485 | 0.032043 | 0.091553 | 122.9599 | 114.1983 | -0.11902 | 0.032043 | 0.091553 | 114.1983 | 118.7485 | 122.9599 | -122.937 | -122.9965
1560.9688 | 123.056 | -0.23804 | 122.6532 | 0.46539 | 0.010468 | 0.02179 | 0.032684 | -0.0053406 | -0.001709 | 0.031616 | -0.14648 | -0.21515 | -0.28381 | 118.7897 | 118.5745 | 113.9923 | 4.2801 | -0.073242 | 122.7402 | -0.37079 | -0.045776 | -122.8683 | 0.091553 | 119.0277 | -4.0787 | -0.13275 | 0.086975 | 0.13733 | 4.5181 | 0.16479 | 118.8126 | 0.022888 | 0.091553 | 122.9782 | 114.2303 | -0.13275 | 0.022888 | 0.091553 | 114.2303 | 118.8126 | 122.9782 | -122.937 | -123.024
1561.9844 | 123.0423 | -0.21973 | 122.644 | 0.091552 | 0.0070496 | 0.022217 | 0.02478 | -0.0079042 | -0.003418 | 0.029053 | -0.17395 | -0.20599 | -0.27924 | 118.7576 | 118.5562 | 114.0244 | 4.5136 | -0.032043 | 122.7448 | -0.34332 | -0.059509 | -122.85 | 0.045777 | 118.9774 | -4.0878 | -0.1236 | 0.10071 | 0.10529 | 4.7333 | 0.18768 | 118.7759 | 0.013733 | 0.045777 | 122.9645 | 114.2441 | -0.1236 | 0.013733 | 0.045777 | 114.2441 | 118.7759 | 122.9645 | -122.9233 | -122.9874
1562.9688 | 122.9691 | -0.27008 | 122.6578 | 0.41199 | 0.012604 | 0.021576 | 0.034607 | -0.0042726 | -0.0019226 | 0.031616 | -0.22888 | -0.19684 | -0.32501 | 118.6752 | 118.4784 | 113.9191 | 4.541 | -0.16937 | 122.7402 | -0.38452 | -0.054931 | -122.8546 | 0.041199 | 118.9453 | -4.1794 | -0.11444 | 0.082397 | 0.09613 | 4.8111 | 0.10071 | 118.7485 | 0.073243 | 0.041199 | 123.0103 | 114.1891 | -0.11444 | 0.073243 | 0.041199 | 114.1891 | 118.7485 | 123.0103 | -122.9828 | -123.0423
1563.9688 | 123.024 | -0.25635 | 122.6257 | 0.43488 | 0.011749 | 0.02179 | 0.032044 | -0.0055542 | -0.0029906 | 0.032684 | -0.15564 | -0.23804 | -0.28839 | 118.7759 | 118.5745 | 114.0701 | 4.422 | -0.073242 | 122.7036 | -0.35706 | -0.032043 | -122.8638 | 0.10071 | 119.0323 | -4.0512 | -0.10071 | 0.07782 | 0.13275 | 4.6783 | 0.18311 | 118.8309 | 0.018311 | 0.10071 | 122.9599 | 114.3265 | -0.10071 | 0.018311 | 0.10071 | 114.3265 | 118.8309 | 122.9599 | -122.9141 | -122.9828
1564.9688 | 123.0377 | -0.24261 | 122.612 | 0.37384 | 0.0098268 | 0.019226 | 0.030548 | -0.0072632 | -0.001068 | 0.032898 | -0.16022 | -0.25177 | -0.3067 | 118.6111 | 118.4052 | 113.8641 | 4.2938 | -0.068665 | 122.7036 | -0.37994 | -0.064087 | -122.8638 | 0.082398 | 118.8538 | -4.2068 | -0.13733 | 0.091552 | 0.14648 | 4.5364 | 0.17395 | 118.6478 | -0.009155 | 0.082398 | 122.9462 | 114.1068 | -0.13733 | -0.009155 | 0.082398 | 114.1068 | 118.6478 | 122.9462 | -122.9187 | -122.9919
1565.9688 | 123.0148 | -0.24261 | 122.6669 | 0.37384 | 0.0091858 | 0.022644 | 0.032898 | -0.0049134 | -0.0032044 | 0.030975 | -0.16022 | -0.24261 | -0.30212 | 118.6066 | 118.4052 | 113.8458 | 4.303 | -0.073242 | 122.7219 | -0.37079 | -0.059509 | -122.9095 | 0.082398 | 118.8492 | -4.2618 | -0.12817 | 0.054932 | 0.14191 | 4.5456 | 0.16937 | 118.6478 | 0 | 0.082398 | 122.9645 | 114.0884 | -0.12817 | 0 | 0.082398 | 114.0884 | 118.6478 | 122.9645 | -122.9691 | -123.0377
1566.9844 | 122.9233 | -0.28839 | 122.6761 | 0.16785 | 0.0083314 | 0.01944 | 0.03418 | 0 | 0.0023498 | 0.042084 | -0.24261 | -0.13733 | -0.34332 | 108.1329 | 107.9315 | 103.9124 | 9.6725 | -0.16479 | 122.7814 | -0.42114 | -0.054932 | -122.8134 | 0.045776 | 108.4213 | -14.7446 | -0.13275 | 0.10529 | 0.10071 | 9.9609 | 0.1236 | 108.2199 | 0.15106 | 0.045776 | 123.0698 | 104.2007 | -0.13275 | 0.15106 | 0.045776 | 104.2007 | 108.2199 | 123.0698 | -123.0194 | -123.0972
1567.9688 | 123.0331 | -0.25177 | 122.6624 | 0.38147 | 0.009613 | 0.025848 | 0.031189 | -0.004059 | -0.0023498 | 0.030121 | -0.16937 | -0.24261 | -0.30212 | 118.689 | 118.4921 | 114.0244 | 4.6692 | -0.07782 | 122.7264 | -0.36621 | -0.050354 | -122.905 | 0.082397 | 118.9407 | -4.1702 | -0.11444 | 0.064086 | 0.13275 | 4.921 | 0.17395 | 118.7439 | 0.009155 | 0.082397 | 122.9782 | 114.2761 | -0.11444 | 0.009155 | 0.082397 | 114.2761 | 118.7439 | 122.9782 | -122.9645 | -123.0286
1568.9688 | 123.0698 | -0.27466 | 122.6349 | 0.45776 | 0.0087586 | 0.022217 | 0.030121 | -0.0042726 | 0.0006408 | 0.030121 | -0.14648 | -0.25635 | -0.31128 | 118.8675 | 118.6798 | 114.1617 | 3.8452 | -0.064087 | 122.6807 | -0.40741 | -0.036621 | -122.8912 | 0.12817 | 119.1422 | -3.9551 | -0.13275 | 0.045776 | 0.16479 | 4.1199 | 0.21057 | 118.9545 | 0.01831 | 0.12817 | 122.9553 | 114.4363 | -0.13275 | 0.01831 | 0.12817 | 114.4363 | 118.9545 | 122.9553 | -122.9462 | -123.0423
1569.9688 | 123.0515 | -0.26093 | 122.6212 | 0.22125 | 0.009613 | 0.017304 | 0.031403 | -0.0044862 | -0.0019226 | 0.02948 | -0.091553 | -0.27466 | -0.35706 | 118.5654 | 118.3594 | 113.8 | 3.8223 | -0.07782 | 122.6852 | -0.35706 | -0.096131 | -122.8958 | 0.16937 | 118.8263 | -4.2618 | -0.096131 | 0.064087 | 0.2655 | 4.0833 | 0.18311 | 118.6203 | -0.013733 | 0.16937 | 122.9462 | 114.061 | -0.096131 | -0.013733 | 0.16937 | 114.061 | 118.6203 | 122.9462 | -122.9782 | -122.9782
1570.9688 | 122.9828 | -0.27466 | 122.6578 | 0.28992 | 0.0070496 | 0.020508 | 0.027344 | -0.0083314 | -0.0008544 | 0.031189 | -0.22888 | -0.21515 | -0.28839 | 118.9316 | 118.7576 | 114.3219 | 3.9368 | -0.10986 | 122.7264 | -0.37537 | -0.013733 | -122.8729 | 0.045776 | 119.2062 | -3.9001 | -0.10071 | 0.068664 | 0.059509 | 4.2114 | 0.1648 | 119.0323 | 0.059509 | 0.045776 | 123.0011 | 114.5966 | -0.10071 | 0.059509 | 0.045776 | 114.5966 | 119.0323 | 123.0011 | -122.9462 | -123.0331
1571.9844 | 122.9553 | -0.29755 | 122.6898 | 0.038147 | 0.0098268 | 0.023071 | 0.035248 | -0.0055542 | -0.003418 | 0.029907 | -0.23804 | -0.1831 | -0.33417 | 118.689 | 118.4601 | 113.9969 | 4.2435 | -0.16937 | 122.7264 | -0.42114 | -0.036621 | -122.8729 | 0.059509 | 118.9865 | -4.2297 | -0.1236 | 0.036621 | 0.09613 | 4.541 | 0.12817 | 118.7576 | 0.11444 | 0.059509 | 123.024 | 114.2944 | -0.1236 | 0.11444 | 0.059509 | 114.2944 | 118.7576 | 123.024 | -123.024 | -123.111
1572.9688 | 122.9691 | -0.32501 | 122.5937 | 0.2594 | 0.0066224 | 0.020508 | 0.027985 | -0.0049134 | -0.0042724 | 0.030975 | -0.2243 | -0.22888 | -0.31586 | 118.8034 | 118.6249 | 114.1846 | 3.7262 | -0.33417 | 122.6074 | -0.41657 | 0.009155 | -122.8226 | 0.10071 | 119.1284 | -3.9688 | -0.091553 | 0.013733 | 0.091553 | 4.0512 | -0.009155 | 118.9499 | 0.09613 | 0.10071 | 122.9324 | 114.5096 | -0.091553 | 0.09613 | 0.10071 | 114.5096 | 118.9499 | 122.9324 | -122.9095 | -123.0103
1573.9688 | 123.0057 | -0.32959 | 122.6303 | 0.23651 | 0.0081178 | 0.017304 | 0.029907 | -0.0079042 | -0.0032044 | 0.026062 | -0.23346 | -0.21973 | -0.3067 | 118.4326 | 118.2907 | 113.9053 | 3.8406 | -0.15564 | 122.6486 | -0.44403 | 0.022888 | -122.85 | 0.096131 | 118.7622 | -4.3396 | -0.11444 | 0.018311 | 0.073243 | 4.1702 | 0.17395 | 118.6203 | 0.10986 | 0.096131 | 122.9782 | 114.2349 | -0.11444 | 0.10986 | 0.096131 | 114.2349 | 118.6203 | 122.9782 | -122.937 | -123.0743
1574.9688 | 123.0057 | -0.31128 | 122.6669 | 0.19073 | 0.0072632 | 0.020294 | 0.026917 | -0.008545 | -0.0008544 | 0.032043 | -0.21973 | -0.23346 | -0.31128 | 118.602 | 118.4006 | 113.9145 | 3.7949 | -0.16479 | 122.6715 | -0.43488 | 0 | -122.9004 | 0.091552 | 118.9133 | -4.2664 | -0.1236 | 0.004578 | 0.091552 | 4.1061 | 0.14648 | 118.7119 | 0.07782 | 0.091552 | 122.9828 | 114.2258 | -0.1236 | 0.07782 | 0.091552 | 114.2258 | 118.7119 | 122.9828 | -122.9782 | -123.1018
1575.9688 | 122.9874 | -0.23346 | 122.6898 | 0.35095 | 0.0070496 | 0.020081 | 0.031189 | -0.0079042 | -0.0012818 | 0.030121 | -0.21057 | -0.2243 | -0.29297 | 118.6752 | 118.4738 | 114.093 | 3.772 | -0.12817 | 122.6898 | -0.36621 | -0.05951 | -122.9141 | 0.022888 | 118.9087 | -4.216 | -0.13275 | 0 | 0.082398 | 4.0054 | 0.10528 | 118.7073 | 0.009155 | 0.022888 | 122.9233 | 114.3265 | -0.13275 | 0.009155 | 0.022888 | 114.3265 | 118.7073 | 122.9233 | -122.9828 | -123.056
1576.9844 | 122.937 | -0.29297 | 122.6761 | -0.030518 | 0.01239 | 0.021576 | 0.035248 | -0.0072632 | -0.0002136 | 0.030975 | -0.22888 | -0.16022 | -0.3067 | 118.5699 | 118.364 | 113.7955 | 3.9688 | -0.16479 | 122.7493 | -0.40283 | -0.013733 | -122.8363 | 0.064087 | 118.8629 | -4.3121 | -0.10986 | 0.073243 | 0.07782 | 4.2618 | 0.12817 | 118.6569 | 0.13275 | 0.064087 | 123.0423 | 114.0884 | -0.10986 | 0.13275 | 0.064087 | 114.0884 | 118.6569 | 123.0423 | -122.9828 | -123.0789
1577.9688 | 123.0377 | -0.23346 | 122.7081 | 0.13733 | 0.008545 | 0.019226 | 0.030121 | -0.0079042 | -0.0029906 | 0.029907 | -0.17395 | -0.20142 | -0.28839 | 118.483 | 118.309 | 113.8 | 4.0192 | -0.050354 | 122.7493 | -0.34332 | -0.054932 | -122.9095 | 0.059509 | 118.7164 | -4.3991 | -0.10986 | 0.041199 | 0.11444 | 4.2526 | 0.1831 | 118.5425 | 0.032043 | 0.059509 | 122.9828 | 114.0335 | -0.10986 | 0.032043 | 0.059509 | 114.0335 | 118.5425 | 122.9828 | -122.9965 | -123.0515
1578.9688 | 123.0515 | -0.22888 | 122.6852 | 0.14496 | 0.0072632 | 0.02243 | 0.03183 | -0.0089722 | -0.004486 | 0.030334 | -0.17853 | -0.21973 | -0.27924 | 118.3228 | 118.1305 | 113.7314 | 4.097 | -0.045776 | 122.7219 | -0.36163 | -0.050354 | -122.905 | 0.050354 | 118.5516 | -4.5547 | -0.13275 | 0.036621 | 0.10071 | 4.3259 | 0.18311 | 118.3594 | 0.009155 | 0.050354 | 122.9507 | 113.9603 | -0.13275 | 0.009155 | 0.050354 | 113.9603 | 118.3594 | 122.9507 | -122.9645 | -123.0469
1579.9688 | 123.0423 | -0.24719 | 122.6898 | 0.12207 | 0.0079042 | 0.020508 | 0.027557 | -0.006836 | -0.0029906 | 0.032043 | -0.19226 | -0.21057 | -0.29297 | 118.4143 | 118.2266 | 113.7634 | 4.01 | -0.041199 | 122.7219 | -0.35706 | -0.045777 | -122.9004 | 0.054931 | 118.6615 | -4.4632 | -0.10986 | 0.032044 | 0.10071 | 4.2572 | 0.20599 | 118.4738 | 0.036621 | 0.054931 | 122.9691 | 114.0106 | -0.10986 | 0.036621 | 0.054931 | 114.0106 | 118.4738 | 122.9691 | -122.9828 | -123.0469
1580.9688 | 123.0331 | -0.24719 | 122.6852 | 0.15259 | 0.008545 | 0.016022 | 0.029053 | -0.0096132 | -0.0002136 | 0.029907 | -0.17395 | -0.21973 | -0.30212 | 119.133 | 118.9499 | 114.5004 | 3.4012 | -0.050354 | 122.7127 | -0.3479 | -0.054932 | -122.905 | 0.073242 | 119.3802 | -3.7354 | -0.10071 | 0.027466 | 0.12817 | 3.6484 | 0.19684 | 119.1971 | 0.027465 | 0.073242 | 122.9599 | 114.7476 | -0.10071 | 0.027465 | 0.073242 | 114.7476 | 119.1971 | 122.9599 | -122.9874 | -123.0331
1581.9688 | 123.056 | -0.21515 | 122.699 | 0.11444 | 0.0074768 | 0.019013 | 0.028198 | -0.0098268 | -0.001709 | 0.030762 | -0.17395 | -0.2243 | -0.29755 | 119.2108 | 119.0002 | 114.5691 | 3.4012 | -0.050354 | 122.731 | -0.33875 | -0.082397 | -122.9233 | 0.041199 | 119.426 | -3.6987 | -0.1236 | 0.032043 | 0.1236 | 3.6163 | 0.16479 | 119.2154 | -0.009155 | 0.041199 | 122.9462 | 114.7842 | -0.1236 | -0.009155 | 0.041199 | 114.7842 | 119.2154 | 122.9462 | -122.9965 | -123.0377
1582.9688 | 123.0194 | -0.26093 | 122.6852 | 0.2594 | 0.0089722 | 0.017944 | 0.030335 | -0.0091858 | -0.001709 | 0.029694 | -0.24261 | -0.2655 | -0.33417 | 119.0598 | 118.8583 | 114.4959 | 3.2822 | -0.10986 | 122.7081 | -0.36621 | -0.073242 | -122.9507 | 0.01831 | 119.3207 | -3.8269 | -0.10529 | 0.022888 | 0.091552 | 3.5431 | 0.15106 | 119.1193 | -0.004578 | 0.01831 | 122.9691 | 114.7568 | -0.10529 | -0.004578 | 0.01831 | 114.7568 | 119.1193 | 122.9691 | -123.0194 | -123.0515
1583.9688 | 122.9965 | -0.24719 | 122.6715 | 0.20599 | 0.0081178 | 0.020935 | 0.029694 | -0.0096132 | -0.001709 | 0.030334 | -0.22888 | -0.27008 | -0.33417 | 119.1055 | 118.9224 | 114.5279 | 3.4332 | -0.10986 | 122.7081 | -0.37537 | -0.086975 | -122.9416 | 0.01831 | 119.3527 | -3.7491 | -0.12817 | 0.036621 | 0.10528 | 3.6804 | 0.13733 | 119.1696 | -0.022889 | 0.01831 | 122.9553 | 114.7751 | -0.12817 | -0.022889 | 0.01831 | 114.7751 | 119.1696 | 122.9553 | -123.0057 | -123.0469
1584.9688 | 123.0835 | -0.24261 | 122.6532 | 0.045776 | 0.0049134 | 0.019226 | 0.031403 | -0.0091858 | -0.0014954 | 0.030121 | -0.13733 | -0.21973 | -0.28381 | 118.895 | 118.6523 | 114.3036 | 3.6713 | -0.032043 | 122.6944 | -0.35248 | -0.041198 | -122.8729 | 0.10529 | 119.1376 | -4.0009 | -0.10986 | 0.041199 | 0.14648 | 3.9139 | 0.21057 | 118.895 | 0.022888 | 0.10529 | 122.937 | 114.5462 | -0.10986 | 0.022888 | 0.10529 | 114.5462 | 118.895 | 122.937 | -122.937 | -123.0057
1585.9688 | 123.0972 | -0.22888 | 122.6807 | 0.076294 | 0.0070496 | 0.019867 | 0.031403 | -0.0087586 | -0.0029906 | 0.030548 | -0.13733 | -0.23346 | -0.3067 | 118.7622 | 118.4463 | 114.0106 | 3.9459 | -0.027466 | 122.7081 | -0.35248 | -0.07782 | -122.9141 | 0.091553 | 118.9911 | -4.2343 | -0.1236 | 0.027466 | 0.16937 | 4.1748 | 0.20142 | 118.6752 | -0.004577 | 0.091553 | 122.937 | 114.2395 | -0.1236 | -0.004577 | 0.091553 | 114.2395 | 118.6752 | 122.937 | -122.9874 | -123.0331
1586.9688 | 123.0881 | -0.25177 | 122.6669 | 0.083923 | 0.0074768 | 0.01944 | 0.030121 | -0.0089722 | -0.0008544 | 0.028839 | -0.15106 | -0.22888 | -0.28839 | 119.2062 | 118.9957 | 114.6057 | 3.3737 | -0.013733 | 122.6669 | -0.36621 | -0.036621 | -122.8958 | 0.10071 | 119.458 | -3.6713 | -0.11444 | 0 | 0.13733 | 3.6255 | 0.23804 | 119.2474 | 0.022888 | 0.10071 | 122.9187 | 114.8575 | -0.11444 | 0.022888 | 0.10071 | 114.8575 | 119.2474 | 122.9187 | -122.9553 | -123.0331
1587.9688 | 123.0789 | -0.24719 | 122.6532 | 0.11444 | 0.0079042 | 0.017517 | 0.02948 | -0.006836 | -0.002777 | 0.028625 | -0.15106 | -0.21973 | -0.29297 | 118.8583 | 118.6295 | 114.18 | 3.7537 | -0.009155 | 122.6944 | -0.36621 | -0.045777 | -122.8729 | 0.09613 | 119.1055 | -4.0237 | -0.11902 | 0.041199 | 0.14191 | 4.0009 | 0.23804 | 118.8766 | 0.027465 | 0.09613 | 122.9416 | 114.4272 | -0.11902 | 0.027465 | 0.09613 | 114.4272 | 118.8766 | 122.9416 | -122.9462 | -123.0194
1588.9688 | 123.0698 | -0.23804 | 122.6486 | 0.1297 | 0.0081178 | 0.016876 | 0.030121 | -0.0066224 | -0.0025634 | 0.02948 | -0.15564 | -0.23346 | -0.30212 | 119.165 | 118.9911 | 114.5508 | 3.3783 | -0.013733 | 122.7081 | -0.36621 | -0.064087 | -122.8821 | 0.082397 | 119.4031 | -3.6575 | -0.12817 | 0.059509 | 0.14648 | 3.6163 | 0.2243 | 119.2291 | 0.004578 | 0.082397 | 122.9462 | 114.7888 | -0.12817 | 0.004578 | 0.082397 | 114.7888 | 119.2291 | 122.9462 | -122.9507 | -123.0148
1589.9688 | 123.0515 | -0.2243 | 122.6852 | 0.091552 | 0.0076904 | 0.017304 | 0.031403 | -0.0074768 | -0.0023498 | 0.028412 | -0.19226 | -0.21973 | -0.31586 | 119.2291 | 119.0231 | 114.6103 | 3.36 | -0.059509 | 122.7127 | -0.36163 | -0.091553 | -122.905 | 0.032043 | 119.4534 | -3.6621 | -0.13733 | 0.027466 | 0.1236 | 3.5843 | 0.16479 | 119.2474 | 0.004577 | 0.032043 | 122.937 | 114.8346 | -0.13733 | 0.004577 | 0.032043 | 114.8346 | 119.2474 | 122.937 | -123.0011 | -123.0469
1590.9688 | 123.0606 | -0.23346 | 122.6898 | 0.14496 | 0.0081178 | 0.018372 | 0.028412 | -0.0091858 | -0.0032044 | 0.030334 | -0.19226 | -0.2243 | -0.30212 | 119.2978 | 119.0918 | 114.7385 | 3.2867 | -0.054932 | 122.7036 | -0.37994 | -0.068665 | -122.9141 | 0.041198 | 119.5312 | -3.598 | -0.14649 | 0.013733 | 0.10986 | 3.5202 | 0.17853 | 119.3253 | 0.009155 | 0.041198 | 122.937 | 114.9719 | -0.14649 | 0.009155 | 0.041198 | 114.9719 | 119.3253 | 122.937 | -122.9919 | -123.0698
1591.9688 | 123.0469 | -0.25177 | 122.6486 | -0.25177 | 0.0083314 | 0.021362 | 0.028198 | -0.0083314 | -0.0046996 | 0.029694 | -0.19684 | -0.23804 | -0.29297 | 119.3069 | 119.0918 | 114.6469 | 3.511 | -0.036621 | 122.6761 | -0.36163 | -0.041199 | -122.8867 | 0.054932 | 119.5587 | -3.5568 | -0.10986 | 0.027465 | 0.096131 | 3.7628 | 0.21515 | 119.3436 | 0.013733 | 0.054932 | 122.9279 | 114.8987 | -0.10986 | 0.013733 | 0.054932 | 114.8987 | 119.3436 | 122.9279 | -122.9416 | -123.0103
1592.9688 | 123.056 | -0.26093 | 122.6852 | 0.58746 | 0.005127 | 0.018585 | 0.030975 | -0.0074768 | -0.003418 | 0.029694 | -0.15564 | -0.26093 | -0.32959 | 119.2841 | 119.0552 | 114.743 | 3.3691 | -0.050354 | 122.7127 | -0.36621 | -0.068665 | -122.9462 | 0.10529 | 119.545 | -3.6301 | -0.10529 | 0.027466 | 0.17395 | 3.6301 | 0.21057 | 119.3161 | 0 | 0.10529 | 122.9736 | 115.004 | -0.10529 | 0 | 0.10529 | 115.004 | 119.3161 | 122.9736 | -123.0148 | -123.0515
1593.9688 | 123.0469 | -0.24261 | 122.6395 | -0.11444 | 0.0089722 | 0.016449 | 0.032044 | -0.0076904 | -0.0029906 | 0.030121 | -0.20142 | -0.26093 | -0.3479 | 119.3298 | 119.1284 | 114.798 | 3.4241 | -0.050354 | 122.699 | -0.3891 | -0.10528 | -122.9004 | 0.041199 | 119.5724 | -3.511 | -0.14648 | 0.05951 | 0.14648 | 3.6667 | 0.19226 | 119.371 | -0.01831 | 0.041199 | 122.9416 | 115.0406 | -0.14648 | -0.01831 | 0.041199 | 115.0406 | 119.371 | 122.9416 | -122.9874 | -123.0286
1594.9688 | 123.056 | -0.24719 | 122.6303 | 0.68665 | 0.006836 | 0.016449 | 0.031616 | -0.0061952 | -0.0014954 | 0.029053 | -0.12817 | -0.24719 | -0.32044 | 119.3436 | 119.1467 | 114.8849 | 3.6392 | -0.036621 | 122.7036 | -0.36621 | -0.073243 | -122.8775 | 0.11902 | 119.5908 | -3.4836 | -0.11902 | 0.073242 | 0.19226 | 3.8864 | 0.21057 | 119.3939 | 0 | 0.11902 | 122.9507 | 115.1321 | -0.11902 | 0 | 0.11902 | 115.1321 | 119.3939 | 122.9507 | -122.9507 | -122.9965
1595.9688 | 123.0698 | -0.25635 | 122.6669 | -0.16785 | 0.009613 | 0.018585 | 0.031616 | -0.0083314 | -0.0040588 | 0.02948 | -0.19226 | -0.23804 | -0.33417 | 119.3756 | 119.1605 | 114.9765 | 3.3279 | -0.036621 | 122.7081 | -0.36621 | -0.077819 | -122.905 | 0.064087 | 119.632 | -3.5065 | -0.10986 | 0.041199 | 0.14191 | 3.5843 | 0.21973 | 119.4168 | 0.018311 | 0.064087 | 122.9645 | 115.2328 | -0.10986 | 0.018311 | 0.064087 | 115.2328 | 119.4168 | 122.9645 | -123.0011 | -123.0331
1596.9688 | 123.0743 | -0.24719 | 122.6395 | 0.13733 | 0.0066224 | 0.017517 | 0.030975 | -0.0093994 | -0.002777 | 0.030121 | -0.16479 | -0.2243 | -0.28839 | 119.252 | 119.0552 | 114.9033 | 3.804 | -0.041199 | 122.6669 | -0.3891 | -0.041199 | -122.8638 | 0.082397 | 119.4992 | -3.5843 | -0.14191 | 0.027466 | 0.1236 | 4.0512 | 0.20599 | 119.3024 | 0.022888 | 0.082397 | 122.9141 | 115.1505 | -0.14191 | 0.022888 | 0.082397 | 115.1505 | 119.3024 | 122.9141 | -122.9279 | -123.0286
1597.9688 | 123.0652 | -0.24719 | 122.6624 | 0.11444 | 0.0074768 | 0.019013 | 0.029907 | -0.0081178 | -0.0049134 | 0.029053 | -0.15564 | -0.23346 | -0.29297 | 119.252 | 119.0323 | 114.8438 | 3.3234 | -0.032043 | 122.7173 | -0.36163 | -0.045777 | -122.8958 | 0.091552 | 119.4992 | -3.6301 | -0.11444 | 0.054931 | 0.13733 | 3.5706 | 0.21515 | 119.2795 | 0.013733 | 0.091552 | 122.9645 | 115.0909 | -0.11444 | 0.013733 | 0.091552 | 115.0909 | 119.2795 | 122.9645 | -122.9553 | -123.024
1598.9688 | 123.0331 | -0.2655 | 122.6761 | -0.022889 | 0.0087586 | 0.020081 | 0.030975 | -0.0042726 | -0.0040588 | 0.027344 | -0.17853 | -0.21973 | -0.31128 | 118.9316 | 118.6935 | 114.4867 | 3.8635 | -0.07782 | 122.7081 | -0.38452 | -0.045776 | -122.8958 | 0.086975 | 119.1971 | -3.9825 | -0.11902 | 0.032044 | 0.13275 | 4.129 | 0.18768 | 118.959 | 0.045776 | 0.086975 | 122.9736 | 114.7522 | -0.11902 | 0.045776 | 0.086975 | 114.7522 | 118.959 | 122.9736 | -122.9874 | -123.0606
1599.9688 | 123.024 | -0.26093 | 122.6807 | 0.030518 | 0.0076904 | 0.019013 | 0.03183 | -0.0079042 | -0.004486 | 0.030334 | -0.17853 | -0.24719 | -0.3067 | 119.252 | 119.0323 | 114.7751 | 3.3325 | -0.07782 | 122.6944 | -0.38452 | -0.045777 | -122.9279 | 0.082397 | 119.5129 | -3.6484 | -0.1236 | 0.013733 | 0.12817 | 3.5934 | 0.18311 | 119.2932 | 0.013733 | 0.082397 | 122.9553 | 115.036 | -0.1236 | 0.013733 | 0.082397 | 115.036 | 119.2932 | 122.9553 | -122.9874 | -123.0652
1600.9688 | 123.0331 | -0.26093 | 122.6807 | 0.030518 | 0.0074768 | 0.016663 | 0.030548 | -0.0081178 | -0.002777 | 0.027557 | -0.19226 | -0.24261 | -0.32501 | 119.3756 | 119.1513 | 114.917 | 3.3691 | -0.054932 | 122.7036 | -0.38452 | -0.064087 | -122.9233 | 0.068664 | 119.6365 | -3.5294 | -0.1236 | 0.022888 | 0.13275 | 3.6301 | 0.20599 | 119.4122 | 0.01831 | 0.068664 | 122.9645 | 115.1779 | -0.1236 | 0.01831 | 0.068664 | 115.1779 | 119.4122 | 122.9645 | -123.0057 | -123.0652
1601.9688 | 123.0377 | -0.26093 | 122.6715 | 0.045776 | 0.0089722 | 0.01474 | 0.031403 | -0.0070496 | -0.003418 | 0.029907 | -0.1831 | -0.24719 | -0.3067 | 118.9545 | 118.7668 | 114.5462 | 3.8315 | -0.054932 | 122.6898 | -0.39825 | -0.045777 | -122.9187 | 0.07782 | 119.2154 | -3.9047 | -0.13733 | 0.01831 | 0.1236 | 4.0924 | 0.20599 | 119.0277 | 0.013733 | 0.07782 | 122.9507 | 114.8071 | -0.13733 | 0.013733 | 0.07782 | 114.8071 | 119.0277 | 122.9507 | -122.9782 | -123.0698
1602.9688 | 123.0743 | -0.27008 | 122.6669 | 0.022888 | 0.0057678 | 0.022217 | 0.02948 | -0.0061952 | -0.0032044 | 0.028412 | -0.17853 | -0.24261 | -0.32044 | 119.1101 | 118.9178 | 114.6515 | 3.5614 | -0.054932 | 122.7219 | -0.37537 | -0.050354 | -122.9095 | 0.091553 | 119.3802 | -3.7491 | -0.10528 | 0.054932 | 0.14191 | 3.8315 | 0.21515 | 119.1879 | 0.027466 | 0.091553 | 122.9919 | 114.9216 | -0.10528 | 0.027466 | 0.091553 | 114.9216 | 119.1879 | 122.9919 | -122.9874 | -123.0423
1603.9688 | 123.0972 | -0.27466 | 122.6624 | 0.007629 | 0.009613 | 0.019013 | 0.029053 | -0.0083314 | -0.0036316 | 0.02948 | -0.18768 | -0.2243 | -0.31586 | 119.0552 | 118.8583 | 114.6423 | 3.6026 | -0.022888 | 122.6761 | -0.37537 | -0.041199 | -122.8867 | 0.086975 | 119.3298 | -3.804 | -0.10071 | 0.013732 | 0.12817 | 3.8773 | 0.25177 | 119.133 | 0.050354 | 0.086975 | 122.9507 | 114.917 | -0.10071 | 0.050354 | 0.086975 | 114.917 | 119.133 | 122.9507 | -122.9782 | -123.0377
1604.9688 | 123.0835 | -0.27008 | 122.644 | 0.083923 | 0.0087586 | 0.018585 | 0.030121 | -0.0089722 | -0.0021362 | 0.030548 | -0.17853 | -0.25635 | -0.31128 | 118.9682 | 118.7531 | 114.5691 | 3.5843 | -0.009155 | 122.6761 | -0.37537 | -0.041198 | -122.9004 | 0.091553 | 119.2383 | -3.891 | -0.10528 | 0.032043 | 0.13275 | 3.8544 | 0.26093 | 119.0231 | 0.013733 | 0.091553 | 122.9462 | 114.8392 | -0.10528 | 0.013733 | 0.091553 | 114.8392 | 119.0231 | 122.9462 | -122.9553 | -123.0194
1605.9688 | 123.0148 | -0.27008 | 122.6761 | -0.076294 | 0.0070496 | 0.019653 | 0.030548 | -0.0079042 | -0.0040588 | 0.029907 | -0.19684 | -0.24261 | -0.33417 | 119.0826 | 118.8812 | 114.679 | 3.6804 | -0.091553 | 122.6807 | -0.39825 | -0.064086 | -122.9187 | 0.073243 | 119.3527 | -3.7949 | -0.12817 | 0.004578 | 0.13733 | 3.9505 | 0.17853 | 119.1513 | 0.027466 | 0.073243 | 122.9507 | 114.949 | -0.12817 | 0.027466 | 0.073243 | 114.949 | 119.1513 | 122.9507 | -123.0103 | -123.0743
1606.9688 | 123.0194 | -0.27466 | 122.6669 | 0.022888 | 0.0089722 | 0.017517 | 0.033112 | -0.0076904 | -0.0036316 | 0.030334 | -0.18768 | -0.25177 | -0.35706 | 118.9453 | 118.7531 | 114.5691 | 3.7674 | -0.09613 | 122.6898 | -0.3891 | -0.082398 | -122.9187 | 0.086975 | 119.22 | -3.9139 | -0.11444 | 0.022888 | 0.16937 | 4.0421 | 0.17853 | 119.0277 | 0.022888 | 0.086975 | 122.9645 | 114.8438 | -0.11444 | 0.022888 | 0.086975 | 114.8438 | 119.0277 | 122.9645 | -123.024 | -123.056
1607.9688 | 123.0377 | -0.2655 | 122.6532 | 0 | 0.008545 | 0.020935 | 0.032684 | -0.0083314 | -0.0025634 | 0.029694 | -0.1831 | -0.25177 | -0.33417 | 119.2108 | 119.0186 | 114.8575 | 3.5751 | -0.068665 | 122.6898 | -0.39825 | -0.068664 | -122.905 | 0.082398 | 119.4763 | -3.6346 | -0.13275 | 0.036621 | 0.15106 | 3.8406 | 0.19684 | 119.2841 | 0.013733 | 0.082398 | 122.9553 | 115.123 | -0.13275 | 0.013733 | 0.082398 | 115.123 | 119.2841 | 122.9553 | -122.9874 | -123.0515
1608.9688 | 123.0423 | -0.27466 | 122.6852 | 0.045776 | 0.0076904 | 0.020935 | 0.031616 | -0.0059816 | -0.0042724 | 0.029907 | -0.18768 | -0.2655 | -0.34332 | 119.3481 | 119.1376 | 114.9857 | 3.3463 | -0.064087 | 122.6852 | -0.40283 | -0.068665 | -122.9507 | 0.086975 | 119.6228 | -3.5477 | -0.12817 | 0 | 0.15564 | 3.6209 | 0.21057 | 119.4122 | 0.009155 | 0.086975 | 122.9599 | 115.2603 | -0.12817 | 0.009155 | 0.086975 | 115.2603 | 119.4122 | 122.9599 | -123.0286 | -123.0881
1609.9688 | 123.0423 | -0.27924 | 122.6669 | 0.015259 | 0.0057678 | 0.016876 | 0.031189 | -0.0083314 | -0.0021362 | 0.029266 | -0.18768 | -0.24719 | -0.33875 | 119.4901 | 119.2749 | 115.1505 | 3.3005 | -0.054932 | 122.7036 | -0.39825 | -0.059509 | -122.9141 | 0.091553 | 119.7693 | -3.392 | -0.11902 | 0.036621 | 0.15106 | 3.5797 | 0.2243 | 119.5541 | 0.032044 | 0.091553 | 122.9828 | 115.4297 | -0.11902 | 0.032044 | 0.091553 | 115.4297 | 119.5541 | 122.9828 | -123.0057 | -123.0652
1610.9688 | 123.0789 | -0.27008 | 122.6395 | 0.11444 | 0.0064088 | 0.019013 | 0.029053 | -0.0083314 | -0.004486 | 0.029694 | -0.17853 | -0.25635 | -0.33417 | 119.4672 | 119.2612 | 115.1276 | 3.273 | -0.050354 | 122.6761 | -0.38452 | -0.064086 | -122.8958 | 0.091553 | 119.7372 | -3.3783 | -0.11444 | 0.036621 | 0.15564 | 3.5431 | 0.21973 | 119.5312 | 0.013733 | 0.091553 | 122.9462 | 115.3976 | -0.11444 | 0.013733 | 0.091553 | 115.3976 | 119.5312 | 122.9462 | -122.9736 | -123.024
1611.9688 | 123.0972 | -0.28381 | 122.6578 | 0.19836 | 0.0081178 | 0.017517 | 0.028839 | -0.0091858 | -0.0025634 | 0.029907 | -0.16937 | -0.2655 | -0.32044 | 119.5129 | 119.3253 | 115.1642 | 3.3646 | -0.036621 | 122.6486 | -0.40283 | -0.036622 | -122.9233 | 0.11444 | 119.7968 | -3.3325 | -0.11902 | -0.009155 | 0.15106 | 3.6484 | 0.24719 | 119.6091 | 0.01831 | 0.11444 | 122.9324 | 115.448 | -0.11902 | 0.01831 | 0.11444 | 115.448 | 119.6091 | 122.9324 | -122.9782 | -123.0606
1612.9688 | 122.9736 | -0.29755 | 122.6761 | -0.053406 | 0.0093994 | 0.020294 | 0.031616 | -0.006836 | -0.0014954 | 0.029907 | -0.21057 | -0.22888 | -0.35248 | 119.3756 | 119.165 | 115.0589 | 3.5568 | -0.1236 | 122.6807 | -0.42572 | -0.054932 | -122.905 | 0.086975 | 119.6732 | -3.511 | -0.12817 | 0.004578 | 0.14191 | 3.8544 | 0.17395 | 119.4626 | 0.068664 | 0.086975 | 122.9782 | 115.3564 | -0.12817 | 0.068664 | 0.086975 | 115.3564 | 119.4626 | 122.9782 | -123.0286 | -123.1018
1613.9688 | 123.0103 | -0.3067 | 122.6898 | -0.022889 | 0.0093994 | 0.018372 | 0.031403 | -0.0081178 | -0.0032044 | 0.029266 | -0.20599 | -0.24261 | -0.33417 | 119.3344 | 119.1284 | 114.9582 | 3.6713 | -0.11902 | 122.7219 | -0.40741 | -0.027465 | -122.9324 | 0.10071 | 119.6411 | -3.5614 | -0.10071 | 0.032044 | 0.12817 | 3.978 | 0.18768 | 119.4351 | 0.064087 | 0.10071 | 123.0286 | 115.2649 | -0.10071 | 0.064087 | 0.10071 | 115.2649 | 119.4351 | 123.0286 | -123.024 | -123.0972
1614.9688 | 122.9919 | -0.31128 | 122.6624 | -0.038147 | 0.0074768 | 0.02179 | 0.032471 | -0.0083314 | -0.0057678 | 0.027557 | -0.21057 | -0.25177 | -0.33417 | 119.4214 | 119.2108 | 115.0772 | 3.5934 | -0.1236 | 122.6898 | -0.42572 | -0.022888 | -122.9141 | 0.10071 | 119.7327 | -3.4515 | -0.11444 | 0.027465 | 0.1236 | 3.9047 | 0.18768 | 119.5221 | 0.059509 | 0.10071 | 123.0011 | 115.3885 | -0.11444 | 0.059509 | 0.10071 | 115.3885 | 119.5221 | 123.0011 | -122.9965 | -123.0881
1615.9688 | 123.0103 | -0.27924 | 122.6807 | -0.030518 | 0.008545 | 0.020081 | 0.030975 | -0.0074768 | -0.001709 | 0.029053 | -0.21973 | -0.25177 | -0.35248 | 119.5084 | 119.3024 | 115.1138 | 3.479 | -0.10986 | 122.6807 | -0.41199 | -0.073242 | -122.9324 | 0.059509 | 119.7876 | -3.3783 | -0.13275 | 0 | 0.13275 | 3.7582 | 0.16937 | 119.5816 | 0.027466 | 0.059509 | 122.9599 | 115.3931 | -0.13275 | 0.027466 | 0.059509 | 115.3931 | 119.5816 | 122.9599 | -123.0331 | -123.0927
1616.9688 | 123.0286 | -0.30212 | 122.6532 | -0.053406 | 0.008545 | 0.018372 | 0.030548 | -0.0093994 | -0.0042724 | 0.029266 | -0.2243 | -0.24719 | -0.3479 | 119.4946 | 119.3024 | 115.155 | 3.4607 | -0.10986 | 122.7264 | -0.41657 | -0.045776 | -122.9004 | 0.07782 | 119.7968 | -3.3508 | -0.11444 | 0.073242 | 0.1236 | 3.7628 | 0.19226 | 119.6045 | 0.054932 | 0.07782 | 123.0286 | 115.4572 | -0.11444 | 0.054932 | 0.07782 | 115.4572 | 119.6045 | 123.0286 | -123.0011 | -123.0698
1617.9688 | 123.0972 | -0.28381 | 122.6532 | -0.24414 | 0.0091858 | 0.020935 | 0.03183 | -0.0087586 | -0.0025634 | 0.028198 | -0.23804 | -0.28839 | -0.36163 | 119.4534 | 119.2657 | 115.1367 | 3.6713 | -0.073242 | 122.6807 | -0.40283 | -0.07782 | -122.9416 | 0.045776 | 119.7372 | -3.3875 | -0.11902 | 0.027466 | 0.1236 | 3.9551 | 0.21057 | 119.5496 | -0.004578 | 0.045776 | 122.9645 | 115.4205 | -0.11902 | -0.004578 | 0.045776 | 115.4205 | 119.5496 | 122.9645 | -123.0148 | -123.056
1618.9688 | 123.0331 | -0.30212 | 122.6852 | -0.038147 | 0.0083314 | 0.022003 | 0.033539 | -0.01004 | -0.0049134 | 0.029053 | -0.21973 | -0.23346 | -0.33875 | 119.545 | 119.3161 | 115.2603 | 3.5934 | -0.1236 | 122.7081 | -0.43945 | -0.036621 | -122.9187 | 0.082397 | 119.8471 | -3.3691 | -0.13733 | 0.022888 | 0.11902 | 3.8956 | 0.17853 | 119.6182 | 0.068665 | 0.082397 | 123.0103 | 115.5624 | -0.13733 | 0.068665 | 0.082397 | 115.5624 | 119.6182 | 123.0103 | -123.024 | -123.1247
1619.9688 | 122.9599 | -0.32501 | 122.6578 | -0.015259 | 0.0066224 | 0.015808 | 0.033325 | -0.0076904 | -0.0036316 | 0.02713 | -0.30212 | -0.21515 | -0.39368 | 119.3481 | 119.1238 | 115.0223 | 3.8361 | -0.20599 | 122.7081 | -0.45776 | -0.068665 | -122.8729 | 0.022888 | 119.6732 | -3.5339 | -0.13275 | 0.050354 | 0.091553 | 4.1611 | 0.11902 | 119.4489 | 0.10986 | 0.022888 | 123.0331 | 115.3473 | -0.13275 | 0.10986 | 0.022888 | 115.3473 | 119.4489 | 123.0331 | -123.0515 | -123.1155
1620.9688 | 122.9645 | -0.34332 | 122.6944 | 0 | 0.010895 | 0.021362 | 0.029694 | -0.0087586 | -0.006195 | 0.028412 | -0.29755 | -0.21973 | -0.38452 | 119.3024 | 119.101 | 115.0314 | 3.8452 | -0.21057 | 122.7081 | -0.45776 | -0.041198 | -122.9141 | 0.045777 | 119.6457 | -3.5934 | -0.11444 | 0.013733 | 0.086975 | 4.1885 | 0.13275 | 119.4443 | 0.1236 | 0.045777 | 123.0515 | 115.3748 | -0.11444 | 0.1236 | 0.045777 | 115.3748 | 119.4443 | 123.0515 | -123.0789 | -123.1522
1621.9688 | 122.9279 | -0.32959 | 122.6761 | -0.022889 | 0.0074768 | 0.019226 | 0.032684 | -0.0070496 | -0.004486 | 0.030334 | -0.3067 | -0.25177 | -0.38452 | 119.4351 | 119.2154 | 115.1093 | 3.7354 | -0.20142 | 122.7219 | -0.46234 | -0.054931 | -122.9279 | 0.022888 | 119.7647 | -3.4607 | -0.13275 | 0.045777 | 0.077819 | 4.0649 | 0.12817 | 119.545 | 0.07782 | 0.022888 | 123.0515 | 115.4388 | -0.13275 | 0.07782 | 0.022888 | 115.4388 | 119.545 | 123.0515 | -123.0606 | -123.1384
1622.9688 | 122.9553 | -0.3479 | 122.6761 | 0.053405 | 0.0074768 | 0.02179 | 0.031616 | -0.0076904 | -0.0049134 | 0.029266 | -0.31128 | -0.24261 | -0.3891 | 119.4489 | 119.2429 | 115.1642 | 3.8589 | -0.19226 | 122.7173 | -0.45776 | -0.041199 | -122.9187 | 0.036621 | 119.7968 | -3.4332 | -0.10986 | 0.041199 | 0.07782 | 4.2068 | 0.15564 | 119.5908 | 0.10528 | 0.036621 | 123.0652 | 115.5121 | -0.10986 | 0.10528 | 0.036621 | 115.5121 | 119.5908 | 123.0652 | -123.0652 | -123.1338
1623.9688 | 122.9553 | -0.3479 | 122.6624 | -0.14496 | 0.0066224 | 0.019867 | 0.033753 | -0.0057678 | -0.0049134 | 0.028412 | -0.29297 | -0.23804 | -0.39368 | 119.4992 | 119.2978 | 115.2283 | 3.7491 | -0.21973 | 122.7127 | -0.46234 | -0.045777 | -122.9004 | 0.054931 | 119.8471 | -3.3646 | -0.11444 | 0.050354 | 0.10071 | 4.097 | 0.12817 | 119.6457 | 0.10986 | 0.054931 | 123.0606 | 115.5762 | -0.11444 | 0.10986 | 0.054931 | 115.5762 | 119.6457 | 123.0606 | -123.056 | -123.1247
1624.9688 | 123.0515 | -0.3067 | 122.644 | -0.015259 | 0.0061952 | 0.02179 | 0.029907 | -0.006836 | -0.0049134 | 0.029694 | -0.2243 | -0.2655 | -0.36163 | 119.5129 | 119.3436 | 115.2832 | 3.6667 | -0.10529 | 122.7219 | -0.43488 | -0.054931 | -122.9095 | 0.082398 | 119.8196 | -3.3005 | -0.12817 | 0.07782 | 0.13733 | 3.9734 | 0.20142 | 119.6503 | 0.041199 | 0.082398 | 123.0286 | 115.5899 | -0.12817 | 0.041199 | 0.082398 | 115.5899 | 119.6503 | 123.0286 | -123.0057 | -123.0789
1625.9688 | 122.9645 | -0.35248 | 122.6715 | -0.23651 | 0.011536 | 0.019867 | 0.033325 | -0.0070496 | -0.0032044 | 0.030334 | -0.31586 | -0.19226 | -0.33875 | 119.4214 | 119.2337 | 115.1413 | 3.7949 | -0.2243 | 122.7036 | -0.48523 | 0.013733 | -122.8638 | 0.036621 | 119.7739 | -3.4378 | -0.13275 | 0.032043 | 0.022888 | 4.1473 | 0.12817 | 119.5862 | 0.16022 | 0.036621 | 123.056 | 115.4938 | -0.13275 | 0.16022 | 0.036621 | 115.4938 | 119.5862 | 123.056 | -123.0103 | -123.1567
1626.9688 | 122.9599 | -0.3479 | 122.6578 | -0.7019 | 0.010895 | 0.020935 | 0.033966 | -0.0074768 | -0.0059814 | 0.029694 | -0.35248 | -0.20142 | -0.37079 | 119.4305 | 119.2108 | 115.1962 | 3.7903 | -0.21973 | 122.7493 | -0.4715 | -0.022889 | -122.8592 | -0.004578 | 119.7784 | -3.447 | -0.1236 | 0.091553 | 0.018311 | 4.1382 | 0.12817 | 119.5587 | 0.14648 | -0.004578 | 123.0972 | 115.5441 | -0.1236 | 0.14648 | -0.004578 | 115.5441 | 119.5587 | 123.0972 | -123.0286 | -123.1293
1627.9688 | 122.9874 | -0.33875 | 122.6669 | -0.015259 | 0.0093994 | 0.018372 | 0.033539 | -0.0061952 | -0.0032044 | 0.029053 | -0.32044 | -0.23346 | -0.42114 | 119.4534 | 119.2429 | 115.2237 | 4.0237 | -0.2243 | 122.7722 | -0.4303 | -0.082398 | -122.9004 | 0.01831 | 119.7922 | -3.4241 | -0.091553 | 0.10529 | 0.10071 | 4.3625 | 0.11444 | 119.5816 | 0.10529 | 0.01831 | 123.111 | 115.5624 | -0.091553 | 0.10529 | 0.01831 | 115.5624 | 119.5816 | 123.111 | -123.0881 | -123.0972
1628.9688 | 122.9553 | -0.31586 | 122.7127 | 0 | 0.0098268 | 0.02179 | 0.032257 | -0.0055542 | -0.0023498 | 0.025421 | -0.33417 | -0.24261 | -0.41199 | 119.7189 | 119.4717 | 115.274 | 3.7445 | -0.18768 | 122.7814 | -0.43488 | -0.09613 | -122.9553 | -0.01831 | 120.0348 | -3.241 | -0.11902 | 0.068664 | 0.07782 | 4.0604 | 0.12817 | 119.7876 | 0.073242 | -0.01831 | 123.0972 | 115.5899 | -0.11902 | 0.073242 | -0.01831 | 115.5899 | 119.7876 | 123.0972 | -123.1247 | -123.1476
1629.9688 | 122.905 | -0.32044 | 122.7173 | -0.045776 | 0.010895 | 0.019653 | 0.03418 | -0.0059816 | -0.0049134 | 0.027771 | -0.31128 | -0.22888 | -0.41657 | 118.9453 | 118.7531 | 114.8346 | 3.8544 | -0.15106 | 122.7722 | -0.4715 | -0.09613 | -122.9462 | 0.009156 | 119.2657 | -3.9642 | -0.15106 | 0.054932 | 0.10529 | 4.1748 | 0.16937 | 119.0735 | 0.091553 | 0.009156 | 123.0927 | 115.155 | -0.15106 | 0.091553 | 0.009156 | 115.155 | 119.0735 | 123.0927 | -123.1339 | -123.1888
1630.9688 | 122.9462 | -0.37079 | 122.6578 | 0.038147 | 0.0076904 | 0.018585 | 0.032257 | -0.0070496 | -0.0036316 | 0.029694 | -0.33417 | -0.25177 | -0.42114 | 119.4901 | 119.2978 | 115.3564 | 3.7399 | -0.22888 | 122.7173 | -0.47607 | -0.050354 | -122.9095 | 0.036622 | 119.8608 | -3.36 | -0.10529 | 0.059509 | 0.086976 | 4.1107 | 0.14191 | 119.6686 | 0.11902 | 0.036622 | 123.0881 | 115.7272 | -0.10529 | 0.11902 | 0.036622 | 115.7272 | 119.6686 | 123.0881 | -123.0789 | -123.1338
1631.9688 | 123.0057 | -0.32959 | 122.644 | 0.022888 | 0.0070496 | 0.019226 | 0.031403 | -0.0074768 | -0.0057678 | 0.027344 | -0.23804 | -0.27924 | -0.37994 | 119.5496 | 119.3436 | 115.3931 | 3.7811 | -0.12817 | 122.7036 | -0.4303 | -0.050354 | -122.9233 | 0.091553 | 119.8792 | -3.3005 | -0.10071 | 0.059509 | 0.14191 | 4.1107 | 0.20142 | 119.6732 | 0.050354 | 0.091553 | 123.0331 | 115.7227 | -0.10071 | 0.050354 | 0.091553 | 115.7227 | 119.6732 | 123.0331 | -123.024 | -123.0743
1632.9688 | 122.9462 | -0.37537 | 122.6669 | -0.0076295 | 0.0091858 | 0.023071 | 0.030975 | -0.0074768 | -0.004486 | 0.028625 | -0.28381 | -0.26093 | -0.40741 | 119.4855 | 119.2749 | 115.3885 | 3.9001 | -0.20599 | 122.6944 | -0.4715 | -0.032044 | -122.9279 | 0.091553 | 119.8608 | -3.392 | -0.096131 | 0.027466 | 0.1236 | 4.2755 | 0.16937 | 119.6503 | 0.11444 | 0.091553 | 123.0698 | 115.7639 | -0.096131 | 0.11444 | 0.091553 | 115.7639 | 119.6503 | 123.0698 | -123.0743 | -123.1384
1633.9688 | 122.9416 | -0.33875 | 122.6532 | -0.022889 | 0.0093994 | 0.023712 | 0.02948 | -0.0059816 | -0.0038452 | 0.02948 | -0.32959 | -0.25635 | -0.42572 | 119.4672 | 119.3527 | 115.4114 | 3.8956 | -0.21057 | 122.7402 | -0.43488 | -0.086975 | -122.9095 | 0.009155 | 119.8059 | -3.3005 | -0.09613 | 0.086975 | 0.09613 | 4.2343 | 0.12817 | 119.6915 | 0.082397 | 0.009155 | 123.0789 | 115.7501 | -0.09613 | 0.082397 | 0.009155 | 115.7501 | 119.6915 | 123.0789 | -123.0789 | -123.0881
1634.9688 | 122.9553 | -0.31128 | 122.6669 | -0.030518 | 0.010254 | 0.017944 | 0.033753 | -0.0064088 | -0.003418 | 0.030975 | -0.33875 | -0.24719 | -0.43488 | 119.3069 | 119.1147 | 115.3061 | 4.6326 | -0.14648 | 122.8134 | -0.43945 | -0.1236 | -122.9141 | -0.027466 | 119.6182 | -3.5522 | -0.12817 | 0.14648 | 0.09613 | 4.9438 | 0.16479 | 119.426 | 0.064087 | -0.027466 | 123.1247 | 115.6174 | -0.12817 | 0.064087 | -0.027466 | 115.6174 | 119.426 | 123.1247 | -123.1018 | -123.1064
1635.9688 | 122.9462 | -0.37537 | 122.6395 | -0.045776 | 0.0093994 | 0.021576 | 0.029266 | -0.0081178 | -0.0019226 | 0.031189 | -0.34332 | -0.27466 | -0.42572 | 119.3893 | 119.1605 | 115.2786 | 4.1382 | -0.24719 | 122.7402 | -0.49896 | -0.050354 | -122.9141 | 0.032043 | 119.7647 | -3.479 | -0.1236 | 0.10071 | 0.082397 | 4.5135 | 0.12817 | 119.5358 | 0.10071 | 0.032043 | 123.1155 | 115.654 | -0.1236 | 0.10071 | 0.032043 | 115.654 | 119.5358 | 123.1155 | -123.0652 | -123.1384
1636.9688 | 122.9553 | -0.36621 | 122.6532 | -0.061036 | 0.0089722 | 0.019867 | 0.031189 | -0.0066224 | -0.0049134 | 0.029053 | -0.33875 | -0.27008 | -0.4303 | 119.4626 | 119.2566 | 115.3885 | 3.8406 | -0.24261 | 122.7264 | -0.47607 | -0.064087 | -122.9233 | 0.027466 | 119.8288 | -3.3966 | -0.10986 | 0.073242 | 0.091553 | 4.2068 | 0.1236 | 119.6228 | 0.09613 | 0.027466 | 123.0927 | 115.7547 | -0.10986 | 0.09613 | 0.027466 | 115.7547 | 119.6228 | 123.0927 | -123.0835 | -123.1293
1637.9688 | 123.0194 | -0.34332 | 122.6349 | -0.053406 | 0.0091858 | 0.02243 | 0.030975 | -0.0059816 | -0.0040588 | 0.028198 | -0.27008 | -0.29297 | -0.3891 | 119.5404 | 119.3481 | 115.535 | 3.9185 | -0.14191 | 122.6669 | -0.4715 | -0.045776 | -122.9279 | 0.073242 | 119.8837 | -3.2867 | -0.12817 | 0.032043 | 0.11902 | 4.2618 | 0.20142 | 119.6915 | 0.050354 | 0.073242 | 123.0103 | 115.8783 | -0.12817 | 0.050354 | 0.073242 | 115.8783 | 119.6915 | 123.0103 | -123.024 | -123.1064

## Thermal Data
Fire Time | North 25C | Cable 1 | Cable 2
-0.0583 | 20.5668 | 19.819 | 19.9549
0.9417 | 20.5665 | 19.8282 | 19.9532
1.9417 | 20.5674 | 19.8197 | 19.9527
2.9417 | 20.5619 | 19.8272 | 19.9515
3.9417 | 20.5737 | 19.8313 | 19.9537
4.9417 | 20.662 | 19.8275 | 19.9625
5.9417 | 21.2451 | 19.827 | 19.951
6.9417 | 22.5662 | 19.8291 | 19.957
7.9417 | 24.5708 | 19.8209 | 19.9564
8.9417 | 27.2074 | 19.8248 | 19.954
9.9417 | 30.3694 | 19.8296 | 19.9496
10.9417 | 33.9419 | 19.8452 | 19.951
11.9417 | 37.8915 | 19.8541 | 19.9447
12.9417 | 42.1381 | 19.86 | 19.9487
13.9417 | 46.6399 | 19.8807 | 19.9521
14.9417 | 51.3174 | 19.9022 | 19.9441
15.9417 | 56.1941 | 19.9224 | 19.9477
16.9417 | 61.2274 | 19.9664 | 19.9442
17.9417 | 66.5005 | 20.002 | 19.9543
18.9417 | 71.8995 | 20.0431 | 19.9567
19.9417 | 77.3754 | 20.0939 | 19.9622
20.9417 | 82.9451 | 20.1493 | 19.9753
21.9417 | 88.6187 | 20.2069 | 19.9795
22.9417 | 94.3852 | 20.3052 | 19.9858
23.9417 | 100.2066 | 20.3995 | 20.0146
24.9417 | 106.0767 | 20.4969 | 20.0056
25.9417 | 112.0304 | 20.6062 | 20.0228
26.9417 | 118.0829 | 20.7373 | 20.0374
27.9417 | 124.1461 | 20.8686 | 20.0566
28.9417 | 130.1518 | 21.021 | 20.0687
29.9417 | 136.2009 | 21.1688 | 20.0883
30.9417 | 142.2897 | 21.3422 | 20.1154
31.9417 | 148.3629 | 21.5404 | 20.1364
32.9417 | 154.4211 | 21.7553 | 20.1691
33.9417 | 160.3903 | 21.979 | 20.2031
34.9417 | 166.3026 | 22.2119 | 20.2362
35.9417 | 172.2496 | 22.4725 | 20.2851
36.9417 | 178.2586 | 22.7298 | 20.3259
37.9417 | 184.2637 | 23.0193 | 20.3767
38.9417 | 190.2291 | 23.3326 | 20.4379
39.9417 | 196.1674 | 23.6467 | 20.4937
40.9417 | 202.1443 | 23.9941 | 20.5699
41.9417 | 208.1624 | 24.3575 | 20.6378
42.9417 | 214.1104 | 24.7343 | 20.7301
43.9417 | 219.9205 | 25.1473 | 20.8081
44.9417 | 225.725 | 25.5505 | 20.901
45.9417 | 231.6072 | 25.9806 | 20.9955
46.9417 | 237.4393 | 26.4394 | 21.1042
47.9417 | 243.2089 | 26.9041 | 21.201
48.9417 | 249.1429 | 27.3863 | 21.3195
49.9417 | 255.0451 | 27.8901 | 21.4425
50.9417 | 260.8239 | 28.4195 | 21.5863
51.9417 | 266.4923 | 28.9554 | 21.7294
52.9417 | 272.1162 | 29.5173 | 21.901
53.9417 | 277.7154 | 30.0897 | 22.0929
54.9417 | 283.2911 | 30.6858 | 22.2834
55.9417 | 288.8938 | 31.3056 | 22.4687
56.9417 | 294.5501 | 31.9408 | 22.6769
57.9417 | 300.12 | 32.608 | 22.9159
58.9417 | 305.5974 | 33.2885 | 23.1342
59.9417 | 310.9267 | 33.9901 | 23.3748
60.9417 | 316.3575 | 34.7338 | 23.61
61.9417 | 321.7856 | 35.4708 | 23.8859
62.9417 | 326.9971 | 36.2427 | 24.1445
63.9417 | 332.2066 | 37.0366 | 24.4423
64.9417 | 337.5645 | 37.8577 | 24.7258
65.9417 | 342.9293 | 38.7078 | 25.0882
66.9417 | 348.2035 | 39.5625 | 25.3638
67.9417 | 353.4015 | 40.4489 | 25.683
68.9417 | 358.6701 | 41.3549 | 26.0621
69.9417 | 363.7996 | 42.2822 | 26.4167
70.9417 | 369.0122 | 43.2327 | 26.8003
71.9417 | 374.2961 | 44.2103 | 27.1947
72.9417 | 379.3667 | 45.2035 | 27.6101
73.9417 | 384.5426 | 46.2308 | 28.035
74.9417 | 389.7307 | 47.2851 | 28.5274
75.9417 | 394.5355 | 48.3667 | 29.042
76.9417 | 399.4692 | 49.4897 | 29.5334
77.9417 | 404.318 | 50.6512 | 30.0588
78.9417 | 409.0708 | 51.8688 | 30.6098
79.9417 | 413.9161 | 53.1137 | 31.1658
80.9417 | 418.7643 | 54.4137 | 31.6849
81.9417 | 423.5377 | 55.711 | 32.2776
82.9417 | 427.9636 | 57.0564 | 32.8541
83.9417 | 431.6623 | 58.4212 | 33.4784
84.9417 | 435.1678 | 59.8206 | 34.063
85.9417 | 438.3764 | 61.2422 | 34.7328
86.9417 | 441.6311 | 62.6932 | 35.4231
87.9417 | 444.5967 | 64.1699 | 36.1623
88.9417 | 447.3951 | 65.6519 | 36.8935
89.9417 | 450.0965 | 67.1252 | 37.4805
90.9417 | 452.8987 | 68.6381 | 38.3444
91.9417 | 455.575 | 70.1438 | 39.1719
92.9417 | 458.0823 | 71.6667 | 40.0145
93.9417 | 460.2989 | 73.2055 | 41.113
94.9417 | 462.3065 | 74.7374 | 42.1204
95.9417 | 464.0399 | 76.2889 | 42.9648
96.9417 | 465.6367 | 77.8457 | 43.7408
97.9417 | 466.9899 | 79.4047 | 44.6224
98.9417 | 468.187 | 80.9637 | 45.3307
99.9417 | 469.1889 | 82.5523 | 46.419
100.9417 | 469.8131 | 84.1204 | 47.4033
101.9417 | 470.2039 | 85.6794 | 48.3248
102.9417 | 470.5865 | 87.2314 | 49.2169
103.9417 | 470.8816 | 88.7907 | 50.4097
104.9417 | 471.1329 | 90.3499 | 51.4668
105.9417 | 471.2718 | 91.9039 | 52.4301
106.9417 | 471.1336 | 93.4274 | 53.3985
107.9417 | 471.0012 | 94.9429 | 54.392
108.9417 | 470.8278 | 96.4604 | 55.5048
109.9417 | 470.5487 | 97.9439 | 56.6698
110.9417 | 470.2763 | 99.4162 | 57.8879
111.9417 | 470.1183 | 100.8889 | 59.0971
112.9417 | 469.8421 | 102.3296 | 60.2592
113.9417 | 469.6784 | 103.7661 | 61.3342
114.9417 | 469.477 | 105.1729 | 62.3835
115.9417 | 469.5549 | 106.5854 | 63.4653
116.9417 | 469.5844 | 107.9702 | 64.4674
117.9417 | 469.755 | 109.3367 | 65.5023
118.9417 | 469.8427 | 110.7029 | 66.5192
119.9417 | 469.9552 | 112.0519 | 67.4951
120.9417 | 469.907 | 113.3736 | 68.4991
121.9417 | 469.9118 | 114.685 | 69.4374
122.9417 | 470.1365 | 115.9814 | 70.3348
123.9417 | 470.3077 | 117.2764 | 71.1654
124.9417 | 470.5085 | 118.5554 | 71.9347
125.9417 | 470.6877 | 119.8375 | 72.7205
126.9417 | 470.7901 | 121.085 | 73.5979
127.9417 | 470.8315 | 122.3273 | 74.4933
128.9417 | 470.942 | 123.5409 | 75.3726
129.9417 | 471.0219 | 124.7466 | 76.2341
130.9417 | 470.9863 | 125.9507 | 77.0638
131.9417 | 471.081 | 127.1397 | 77.8601
132.9417 | 471.0356 | 128.3137 | 78.5481
133.9417 | 471.0317 | 129.4832 | 79.1088
134.9417 | 471.1851 | 130.6413 | 79.4436
135.9417 | 471.376 | 131.7905 | 79.7408
136.9417 | 471.6201 | 132.9251 | 80.4131
137.9417 | 471.9801 | 134.0675 | 81.1347
138.9417 | 472.3068 | 135.1846 | 81.978
139.9417 | 472.5658 | 136.3134 | 82.83
140.9417 | 472.6787 | 137.4352 | 83.7188
141.9417 | 472.8242 | 138.5622 | 84.6383
142.9417 | 473.1332 | 139.6795 | 85.5794
143.9417 | 473.1317 | 140.7657 | 86.7683
144.9417 | 473.2932 | 141.8553 | 87.8544
145.9417 | 473.2104 | 142.9475 | 88.9175
146.9417 | 473.1381 | 144.0128 | 90
147.9417 | 473.0576 | 145.0757 | 91.1054
148.9417 | 473.2201 | 146.1278 | 92.302
149.9417 | 473.2669 | 147.1703 | 93.4413
150.9417 | 473.1185 | 148.2106 | 94.4313
151.9417 | 473.1679 | 149.2557 | 95.4614
152.9417 | 473.2815 | 150.2812 | 96.5622
153.9417 | 473.3573 | 151.3211 | 97.7381
154.9417 | 473.6022 | 152.326 | 98.777
155.9417 | 473.604 | 153.3314 | 99.9064
156.9417 | 473.6472 | 154.3244 | 101.0365
157.9417 | 473.772 | 155.2992 | 102.1379
158.9417 | 473.9412 | 156.2845 | 103.237
159.9417 | 474.0074 | 157.2818 | 104.2924
160.9417 | 473.8659 | 158.2535 | 105.2848
161.9417 | 473.8723 | 159.2098 | 106.244
162.9417 | 474.0506 | 160.152 | 107.2082
163.9417 | 474.053 | 161.0874 | 108.2522
164.9417 | 474.2045 | 162.0111 | 109.2624
165.9417 | 474.2384 | 162.9334 | 110.2539
166.9417 | 474.3367 | 163.8427 | 111.2259
167.9417 | 474.4692 | 164.735 | 112.201
168.9417 | 474.4699 | 165.6486 | 113.1578
169.9417 | 474.5316 | 166.5323 | 114.1195
170.9417 | 474.5863 | 167.4067 | 115.0721
171.9417 | 474.6283 | 168.2651 | 116.0101
172.9417 | 474.5962 | 169.1243 | 116.9387
173.9417 | 474.6902 | 169.9684 | 117.8483
174.9417 | 474.601 | 170.8167 | 118.7614
175.9417 | 474.6744 | 171.6489 | 119.7149
176.9417 | 474.8015 | 172.48 | 120.6499
177.9417 | 474.9357 | 173.3069 | 121.6025
178.9417 | 475.0949 | 174.1408 | 122.526
179.9417 | 475.1201 | 174.9419 | 123.4149
180.9417 | 475.4118 | 175.7777 | 124.283
181.9417 | 475.5025 | 176.5909 | 125.1571
182.9417 | 475.4464 | 177.4145 | 126.0117
183.9417 | 475.451 | 178.252 | 126.8798
184.9417 | 475.1852 | 179.0622 | 127.6719
185.9417 | 475.1894 | 179.8751 | 128.5599
186.9417 | 475.3066 | 180.6808 | 129.3842
187.9417 | 475.2332 | 181.4746 | 130.26
188.9417 | 475.1964 | 182.2704 | 131.1127
189.9417 | 475.2611 | 183.0611 | 131.9294
190.9417 | 475.1048 | 183.8234 | 132.7825
191.9417 | 474.9793 | 184.5743 | 133.5856
192.9417 | 474.8709 | 185.3286 | 134.3062
193.9417 | 474.8798 | 186.0758 | 135.2445
194.9417 | 474.9754 | 186.7947 | 135.4922
195.9417 | 475.1116 | 187.5271 | 135.4471
196.9417 | 475.1382 | 188.2596 | 136.4471
197.9417 | 475.2489 | 188.9842 | 138.0948
198.9417 | 475.2359 | 189.7053 | 139.3367
199.9417 | 475.2196 | 190.4342 | 140.4005
200.9417 | 475.3003 | 191.1657 | 141.6168
201.9417 | 475.2426 | 191.9049 | 142.5756
202.9417 | 475.259 | 192.6498 | 143.6476
203.9417 | 475.3923 | 193.4023 | 144.7659
204.9417 | 475.3346 | 194.1447 | 145.8877
205.9417 | 475.4438 | 194.9067 | 146.9861
206.9417 | 475.6139 | 195.6817 | 148.1216
207.9417 | 475.6844 | 196.4601 | 149.2226
208.9417 | 475.5564 | 197.225 | 150.2629
209.9417 | 475.5117 | 198.0097 | 151.3097
210.9417 | 475.5553 | 198.7753 | 152.2978
211.9417 | 475.5769 | 199.5201 | 153.2966
212.9417 | 475.6849 | 200.2736 | 154.2488
213.9417 | 475.6024 | 201.025 | 155.1713
214.9417 | 475.6644 | 201.7767 | 156.1311
215.9417 | 475.7928 | 202.5419 | 157.0018
216.9417 | 475.822 | 203.2882 | 157.9425
217.9417 | 475.8001 | 204.0376 | 158.8558
218.9417 | 475.7966 | 204.7922 | 159.7363
219.9417 | 475.7763 | 205.5433 | 160.6121
220.9417 | 475.6607 | 206.2897 | 161.4711
221.9417 | 475.7325 | 207.0394 | 162.3297
222.9417 | 475.7493 | 207.7856 | 163.1659
223.9417 | 475.8381 | 208.5346 | 164.0173
224.9417 | 475.9047 | 209.2703 | 164.8655
225.9417 | 476.0743 | 210.0147 | 165.7088
226.9417 | 476.2152 | 210.7311 | 166.5281
227.9417 | 476.1284 | 211.457 | 167.3674
228.9417 | 475.9901 | 212.1908 | 168.1891
229.9417 | 476.0069 | 212.8894 | 169.0278
230.9417 | 476.145 | 213.5871 | 169.8637
231.9417 | 476.0423 | 214.3247 | 170.6893
232.9417 | 475.9987 | 215.0642 | 171.5423
233.9417 | 476.0402 | 215.8056 | 172.373
234.9417 | 476.1012 | 216.5612 | 173.204
235.9417 | 476.143 | 217.3255 | 174.0423
236.9417 | 476.3068 | 218.0422 | 174.9086
237.9417 | 476.2544 | 218.7705 | 175.7547
238.9417 | 476.1793 | 219.4823 | 176.6044
239.9417 | 476.1861 | 220.1959 | 177.4305
240.9417 | 476.2534 | 220.9502 | 178.2715
241.9417 | 476.1572 | 221.7374 | 179.0582
242.9417 | 476.2713 | 222.5606 | 179.5389
243.9417 | 476.2841 | 223.3423 | 180.1467
244.9417 | 476.3493 | 224.0956 | 180.7505
245.9417 | 476.4405 | 224.8271 | 181.4727
246.9417 | 476.3345 | 225.5868 | 182.2675
247.9417 | 476.306 | 226.4108 | 183.0128
248.9417 | 476.3757 | 227.2055 | 183.5489
249.9417 | 476.376 | 227.9764 | 183.9062
250.9417 | 476.2961 | 228.7123 | 184.4913
251.9417 | 476.1131 | 229.3501 | 185.0791
252.9417 | 476.094 | 229.9587 | 185.7492
253.9417 | 476.1667 | 230.5361 | 186.4882
254.9417 | 476.3072 | 231.0525 | 187.0581
255.9417 | 476.3568 | 231.4912 | 187.6635
256.9417 | 476.274 | 231.9359 | 188.3657
257.9417 | 476.2801 | 232.3172 | 189.0535
258.9417 | 476.0371 | 232.6375 | 189.5427
259.9417 | 475.7959 | 232.9802 | 190.0419
260.9417 | 475.7939 | 233.2508 | 190.3972
261.9417 | 475.9404 | 233.4807 | 191.1509
262.9417 | 475.8969 | 233.6553 | 191.3319
263.9417 | 475.9582 | 233.9494 | 191.559
264.9417 | 475.8052 | 234.1203 | 189.9683
265.9417 | 475.7845 | 234.2366 | 190.0756
266.9417 | 475.8041 | 234.3216 | 190.3924
267.9417 | 475.8268 | 234.1853 | 191.3972
268.9417 | 475.6641 | 234.2013 | 190.6957
269.9417 | 475.5562 | 234.094 | 191.1567
270.9417 | 475.4115 | 233.9499 | 190.7938
271.9417 | 475.3927 | 233.7537 | 190.0792
272.9417 | 475.4828 | 233.5627 | 190.1911
273.9417 | 475.4613 | 233.3733 | 189.5827
274.9417 | 475.482 | 233.2256 | 187.3085
275.9417 | 475.5997 | 233.0712 | 175.2453
276.9417 | 475.711 | 232.9111 | 175.9539
277.9417 | 475.6664 | 232.7939 | 176.6792
278.9417 | 475.6759 | 232.7031 | 177.4219
279.9417 | 475.5363 | 232.6577 | 178.1759
280.9417 | 475.4567 | 232.6096 | 178.9254
281.9417 | 475.3893 | 232.5775 | 179.6758
282.9417 | 475.3 | 232.566 | 180.4307
283.9417 | 475.2461 | 232.589 | 181.1869
284.9417 | 475.2384 | 232.6895 | 181.9471
285.9417 | 475.2048 | 232.7793 | 182.7042
286.9417 | 475.1553 | 232.9292 | 183.4537
287.9417 | 475.0588 | 233.1156 | 184.2018
288.9417 | 475.0841 | 233.3372 | 184.9567
289.9417 | 475.0345 | 233.5615 | 185.7007
290.9417 | 474.9795 | 233.8679 | 186.4423
291.9417 | 474.8252 | 235.4845 | 187.1776
292.9417 | 474.9224 | 237.8037 | 187.9137
293.9417 | 474.9929 | 239.0435 | 188.6375
294.9417 | 474.911 | 239.8745 | 189.3486
295.9417 | 474.887 | 240.4915 | 190.057
296.9417 | 474.7806 | 240.9968 | 190.7518
297.9417 | 474.7239 | 241.3817 | 191.4442
298.9417 | 474.6357 | 241.6994 | 192.1332
299.9417 | 474.7803 | 241.999 | 192.8052
300.9417 | 474.8544 | 242.3124 | 193.4793
301.9417 | 474.9947 | 242.6549 | 194.1435
302.9417 | 475.1994 | 243.0712 | 194.8089
303.9417 | 475.3752 | 243.4784 | 195.5214
304.9417 | 475.6875 | 243.9748 | 196.2278
305.9417 | 476.0519 | 244.4834 | 196.9614
306.9417 | 476.7184 | 245.1333 | 197.7492
307.9417 | 477.2814 | 246.3473 | 198.4861
308.9417 | 477.71 | 247.8792 | 199.1606
309.9417 | 477.9676 | 249.5384 | 199.8393
310.9417 | 478.1838 | 251.8991 | 200.4849
311.9417 | 478.4836 | 253.8667 | 201.1434
312.9417 | 478.6007 | 255.711 | 201.7996
313.9417 | 478.6971 | 257.3102 | 202.457
314.9417 | 478.5932 | 258.8197 | 203.1137
315.9417 | 478.3384 | 260.4219 | 203.7594
316.9417 | 478.2766 | 262.2585 | 204.4119
317.9417 | 478.2441 | 264.2269 | 205.0488
318.9417 | 478.0541 | 266.1653 | 205.7169
319.9417 | 477.9449 | 268.8016 | 206.375
320.9417 | 477.8253 | 271.0169 | 207.0517
321.9417 | 477.6834 | 273.1143 | 207.7247
322.9417 | 477.472 | 274.9979 | 208.4028
323.9417 | 477.3962 | 276.792 | 209.1418
324.9417 | 477.2794 | 277.9065 | 209.927
325.9417 | 477.2967 | 279.4654 | 210.6978
326.9417 | 477.1959 | 279.7897 | 211.5227
327.9417 | 477.0965 | 279.9501 | 212.3751
328.9417 | 477.0134 | 280.6284 | 213.5603
329.9417 | 476.6884 | 280.799 | 214.7456
330.9417 | 476.439 | 281.2922 | 215.9702
331.9417 | 476.0029 | 281.4164 | 217.305
332.9417 | 475.6772 | 281.0919 | 218.4203
333.9417 | 475.4729 | 280.4592 | 219.6409
334.9417 | 475.1223 | 281.0848 | 221.529
335.9417 | 475.0551 | 282.306 | 222.5493
336.9417 | 474.8693 | 285.6942 | 223.9599
337.9417 | 474.6849 | 288.1861 | 225.3396
338.9417 | 474.3101 | 290.6173 | 226.8112
339.9417 | 473.8948 | 292.701 | 228.5764
340.9417 | 473.5763 | 294.7662 | 230.0295
341.9417 | 473.3316 | 297.7134 | 233.6776
342.9417 | 473.1596 | 300.6192 | 234.1397
343.9417 | 472.823 | 303.7585 | 235.7026
344.9417 | 472.3519 | 306.6787 | 236.3096
345.9417 | 471.8886 | 310.4398 | 238.0636
346.9417 | 471.5593 | 312.257 | 239.0427
347.9417 | 471.1349 | 314.5185 | 240.8159
348.9417 | 470.8679 | 316.5138 | 242.3764
349.9417 | 470.6901 | 318.7839 | 244.3809
350.9417 | 470.2991 | 321.3529 | 247.7181
351.9417 | 469.9352 | 324.9698 | 250.986
352.9417 | 469.6141 | 323.9144 | 250.3402
353.9417 | 469.2884 | 324.6039 | 252.345
354.9417 | 468.9154 | 325.9907 | 253.7987
355.9417 | 468.7629 | 326.7647 | 255.6075
356.9417 | 468.4202 | 328.2262 | 257.3754
357.9417 | 468.2926 | 329.642 | 259.6188
358.9417 | 468.3411 | 330.9519 | 264.2919
359.9417 | 468.1274 | 333.0932 | 263.9803
360.9417 | 467.932 | 333.3923 | 265.8587
361.9417 | 467.7607 | 331.8644 | 267.6049
362.9417 | 467.5126 | 332.2955 | 269.471
363.9573 | 467.4306 | 334.515 | 272.0783
364.9417 | 467.2368 | 334.7316 | 274.0953
365.9417 | 467.12 | 335.9441 | 276.7301
366.9417 | 466.972 | 336.2246 | 279.9287
367.9417 | 466.7598 | 337.9763 | 280.5902
368.9417 | 466.6272 | 339.5687 | 283.9552
369.9417 | 466.6277 | 339.9182 | 286.0232
370.9417 | 466.5921 | 340.3523 | 287.2895
371.9417 | 466.2656 | 342.2624 | 289.8053
372.9417 | 466.1025 | 342.2146 | 291.6654
373.9417 | 466.1625 | 343.6103 | 293.9737
374.9417 | 466.1599 | 344.2786 | 295.8464
375.9885 | 466.2489 | 345.5254 | 298.4115
376.9417 | 466.1395 | 346.3582 | 299.9241
377.9417 | 466.0607 | 347.6588 | 302.1924
378.9417 | 466.0877 | 347.5791 | 303.9278
380.051 | 466.1084 | 348.8807 | 305.5259
380.9417 | 466.2339 | 349.9207 | 306.9226
381.9573 | 466.2751 | 350.8944 | 308.5555
382.9417 | 466.2954 | 351.3104 | 310.2784
383.9417 | 466.2368 | 352.4219 | 311.6272
384.9417 | 466.2511 | 353.7239 | 312.9691
385.9417 | 466.2533 | 354.2305 | 314.5054
386.9417 | 466.1839 | 356.1729 | 315.6546
387.9417 | 466.0949 | 357.6483 | 317.9464
388.9417 | 465.9967 | 359.0089 | 319.1941
390.301 | 465.9384 | 361.2423 | 321.0445
390.9417 | 465.9308 | 362.7797 | 322.262
391.9417 | 465.8719 | 365.9686 | 324.002
392.9417 | 465.8565 | 366.4905 | 325.5763
393.9417 | 465.8265 | 368.2818 | 327.0842
395.0354 | 465.7488 | 371.9129 | 327.9907
395.9885 | 465.7094 | 373.3781 | 328.9914
397.0354 | 465.653 | 373.4129 | 330.5535
398.1448 | 465.608 | 376.9538 | 332.4624
398.9417 | 465.5532 | 378.9643 | 333.302
399.9417 | 465.5061 | 379.8819 | 334.7964
400.9417 | 465.5988 | 380.8836 | 336.576
401.9417 | 465.6482 | 383.5186 | 338.287
402.9417 | 465.6742 | 383.6958 | 339.6501
403.9417 | 465.7473 | 385.5509 | 340.9436
404.9417 | 465.6039 | 386.0797 | 342.4191
405.9417 | 465.5256 | 387.092 | 343.8383
406.9417 | 465.5133 | 388.1089 | 344.9537
407.9417 | 465.4869 | 388.4492 | 346.0973
408.9417 | 465.5669 | 390.0806 | 347.7732
409.9417 | 465.6681 | 390.0248 | 348.2097
410.9417 | 465.7636 | 391.2016 | 348.814
411.9417 | 465.7892 | 392.3898 | 351.5819
412.9417 | 465.8516 | 392.9041 | 351.5629
413.9417 | 465.9446 | 393.3282 | 352.1266
414.9417 | 466.0078 | 393.9163 | 352.9925
415.9417 | 466.0545 | 394.3584 | 352.9837
416.9417 | 466.0673 | 394.9307 | 353.5195
417.9417 | 466.1281 | 395.6082 | 354.2893
418.9417 | 466.1914 | 395.8081 | 357.2749
419.9417 | 466.3041 | 396.7124 | 356.1464
420.9417 | 466.3528 | 396.8608 | 357.2286
421.9417 | 466.393 | 397.0275 | 358.3182
422.9417 | 466.4075 | 397.2611 | 359.7767
423.9417 | 466.4295 | 397.6373 | 359.7437
424.9417 | 466.4875 | 397.382 | 361.5342
425.9417 | 466.7223 | 397.9445 | 361.1859
426.9417 | 466.7394 | 398.0429 | 362.0501
427.9417 | 466.7259 | 398.106 | 363.2725
428.9417 | 466.7907 | 397.8733 | 363.861
429.9417 | 466.8397 | 398.0843 | 364.6861
430.9417 | 466.9681 | 397.4197 | 364.9964
431.9417 | 467.0098 | 397.4534 | 364.851
432.9417 | 467.1409 | 397.2473 | 365.2662
433.9417 | 467.2543 | 397.6099 | 365.7291
434.9417 | 467.3842 | 397.5921 | 366.3311
435.9417 | 467.5119 | 397.6102 | 366.9485
436.9417 | 467.6122 | 398.2419 | 367.6088
437.9417 | 467.7667 | 398.239 | 367.3492
438.9417 | 467.796 | 398.9184 | 368.6066
439.9417 | 467.8518 | 399.2374 | 368.5273
440.9417 | 467.9336 | 399.1966 | 369.914
441.9417 | 468.069 | 399.5667 | 369.9754
442.9417 | 468.2143 | 399.608 | 369.7054
443.9417 | 468.221 | 400.2253 | 370.0511
444.9417 | 468.3462 | 399.7722 | 369.7825
445.9417 | 468.3619 | 400.3949 | 370.1983
446.9417 | 468.2997 | 400.4041 | 370.0771
447.9417 | 468.1834 | 400.7774 | 370.1774
448.9417 | 468.1747 | 400.8151 | 370.7402
449.9417 | 468.1809 | 400.9065 | 370.5169
450.9417 | 468.2699 | 401.3059 | 370.16
451.9417 | 468.2389 | 401.2468 | 369.4332
452.9417 | 468.1967 | 401.4465 | 369.5653
453.9417 | 468.174 | 401.4697 | 369.2031
454.9417 | 468.3596 | 401.6317 | 368.5842
455.9417 | 468.5469 | 402.0486 | 367.9196
456.9417 | 468.4619 | 402.2785 | 367.6572
457.9417 | 468.4997 | 402.4206 | 367.0427
458.9417 | 468.6224 | 403.0309 | 366.5674
459.9417 | 468.6011 | 402.5969 | 366.172
460.9417 | 468.6886 | 402.8232 | 365.6493
461.9417 | 468.5612 | 403.2485 | 365.2348
462.9417 | 468.4875 | 403.2779 | 364.9506
463.9417 | 468.4774 | 403.8965 | 364.9088
464.9417 | 468.5382 | 404.4932 | 364.9794
465.9417 | 468.5086 | 405.3144 | 364.7353
466.9417 | 468.4798 | 405.5918 | 364.6233
467.9417 | 468.4234 | 406.3598 | 364.6796
468.9417 | 468.4453 | 406.2549 | 364.6113
469.9417 | 468.3326 | 406.6955 | 364.4402
470.9417 | 468.2713 | 407.6936 | 364.6086
471.9417 | 468.2306 | 407.3038 | 364.6676
472.9417 | 468.1497 | 407.8075 | 364.8256
473.9417 | 468.1905 | 409.7456 | 365.0652
474.9417 | 468.133 | 409.6394 | 365.1454
475.9417 | 468.1601 | 410.5661 | 365.3342
476.9417 | 468.0997 | 411.2784 | 365.8388
477.9417 | 468.0738 | 411.9272 | 365.9644
478.9417 | 468.1147 | 412.361 | 366.5308
479.9417 | 467.9872 | 413.6633 | 367.0276
480.9417 | 467.8855 | 413.8533 | 367.8124
481.9417 | 467.847 | 414.8173 | 368.4198
482.9417 | 467.7297 | 414.9487 | 368.7465
483.9417 | 467.5527 | 415.7596 | 369.5545
484.9417 | 467.6284 | 415.7702 | 370.135
485.9417 | 467.6222 | 416.8565 | 370.8569
486.9417 | 467.6099 | 418.3009 | 371.6597
487.9417 | 467.4951 | 417.8362 | 372.2867
488.9417 | 467.3392 | 419.3486 | 373.042
489.9417 | 467.3023 | 419.5926 | 373.7819
490.9417 | 467.2576 | 419.9058 | 374.546
491.9417 | 467.2021 | 420.5262 | 375.3963
492.9417 | 467.0816 | 420.9528 | 376.0882
493.9417 | 466.9648 | 421.6759 | 376.9393
494.9417 | 466.8256 | 422.0464 | 377.8763
495.9417 | 466.735 | 422.2186 | 378.627
496.9417 | 466.6262 | 423.3047 | 379.4262
497.9417 | 466.5416 | 423.3237 | 380.3081
498.9417 | 466.5597 | 423.3146 | 381.1404
499.9417 | 466.3796 | 423.5669 | 381.9245
500.9417 | 466.3546 | 424.0643 | 382.9916
501.9417 | 466.2891 | 424.0679 | 383.7588
502.9417 | 466.0382 | 424.9633 | 384.721
503.9417 | 465.9798 | 424.9548 | 385.7721
504.9417 | 465.9569 | 424.7712 | 386.3019
505.9417 | 466.0015 | 425.458 | 387.4859
506.9417 | 465.9096 | 425.4151 | 388.319
507.9417 | 465.8397 | 425.7289 | 389.2916
508.9417 | 465.6946 | 426.2803 | 390.1532
509.9417 | 465.6211 | 426.8885 | 390.6972
510.9417 | 465.7284 | 426.9277 | 391.5644
511.9417 | 465.6528 | 426.9337 | 392.4671
512.9417 | 465.6821 | 427.1632 | 393.3238
513.9417 | 465.8353 | 427.4274 | 394.1629
514.9417 | 466.0201 | 427.991 | 395.0314
515.9417 | 466.0418 | 428.7973 | 395.7419
516.9417 | 466.037 | 428.4817 | 396.7602
517.9417 | 466.0897 | 428.1235 | 397.218
518.9417 | 466.1356 | 428.136 | 398.1796
519.9417 | 466.0934 | 428.3252 | 398.9649
520.9417 | 466.0602 | 428.3812 | 399.6603
521.9417 | 466.0173 | 428.6172 | 400.5545
522.9417 | 466.0726 | 428.5678 | 401.2935
523.9417 | 466.1253 | 429.0716 | 401.977
524.9417 | 466.1125 | 429.3042 | 402.8189
525.9417 | 466.2606 | 429.4506 | 403.8078
526.9417 | 466.3409 | 429.5519 | 404.5154
527.9417 | 466.3936 | 429.0563 | 405.3061
528.9417 | 466.3886 | 429.1456 | 406.1491
529.9417 | 466.4456 | 429.5796 | 406.8841
530.9417 | 466.4559 | 429.6966 | 407.7314
531.9417 | 466.5079 | 429.964 | 408.5757
532.9417 | 466.5393 | 430.2076 | 409.2912
533.9417 | 466.5311 | 430.3297 | 410.1139
534.9417 | 466.5677 | 431.0596 | 410.9136
535.9417 | 466.5551 | 432.2216 | 411.6415
536.9417 | 466.6008 | 432.2804 | 412.3697
537.9417 | 466.6783 | 433.182 | 413.1503
538.9417 | 466.6366 | 432.1271 | 413.8485
539.9417 | 466.5076 | 431.7199 | 414.5475
540.9417 | 466.374 | 430.5993 | 414.7054
541.9417 | 466.3309 | 429.3929 | 415.0853
542.9417 | 466.256 | 428.7774 | 415.6072
543.9417 | 466.3003 | 421.0882 | 415.4373
544.9417 | 466.3136 | 419.6003 | 416.0527
545.9417 | 466.2853 | 424.2352 | 418.3939
546.9417 | 466.2307 | 422.0412 | 418.8038
547.9417 | 466.1917 | 419.4179 | 419.7854
548.9417 | 466.1929 | 423.2118 | 420.6112
549.9417 | 466.0603 | 427.3922 | 421.7677
550.9417 | 466.029 | 424.6296 | 422.4673
551.9417 | 466.095 | 423.6324 | 423.3566
552.9417 | 466.0786 | 419.753 | 424.2153
553.9417 | 465.9782 | 421.3068 | 425.3079
554.9417 | 465.9543 | 420.5453 | 425.8914
555.9417 | 465.8718 | 419.0768 | 426.7178
556.9417 | 465.8086 | 415.5057 | 427.5985
557.9417 | 465.8336 | 413.7269 | 428.296
558.9417 | 465.7431 | 414.6546 | 429.3314
559.9417 | 465.7585 | 413.8782 | 428.6914
560.9417 | 465.7294 | 412.2762 | 428.5752
561.9417 | 465.7449 | 411.4266 | 428.8728
562.9417 | 465.8426 | 411.6295 | 430.2743
563.9417 | 465.8623 | 410.3003 | 430.9016
564.9417 | 465.8333 | 415.3286 | 431.6287
565.9417 | 465.8145 | 415.2495 | 432.6223
566.9417 | 465.7051 | 411.0155 | 433.3535
567.9417 | 465.7434 | 412.1099 | 433.9136
568.9417 | 465.6748 | 355.3467 | 428.6915
569.9417 | 465.6416 | 383.818 | 432.9914
570.9417 | 465.7363 | 349.8532 | 430.554
571.9417 | 465.8382 | 369.6673 | 433.3573
572.9417 | 465.961 | 354.6155 | 432.4249
573.9417 | 465.965 | 366.3192 | 434.4217
574.9417 | 465.8741 | 342.5355 | 430.7507
575.9417 | 465.8106 | 341.3928 | 431.6488
576.9417 | 465.7806 | 338.9526 | 433.6151
577.9417 | 465.6243 | 345.633 | 434.6307
578.9417 | 465.7275 | 348.2916 | 435.0671
579.9417 | 465.6916 | 339.6877 | 430.0405
580.9417 | 465.6397 | 332.7351 | 427.1247
581.9417 | 465.6993 | 273.7485 | 401.6795
582.9417 | 465.7465 | 395.1113 | 433.7122
583.9417 | 465.6703 | 315.645 | 408.936
584.9417 | 465.7415 | 389.5476 | 429.7711
585.9417 | 465.7844 | 317.3368 | 405.5834
586.9417 | 465.9566 | 394.9968 | 427.3924
587.9417 | 466.1403 | 392.6622 | 429.7875
588.9417 | 466.5907 | 379.0761 | 425.3814
589.9417 | 466.8995 | 383.0828 | 425.1611
590.9417 | 466.8367 | 388.8104 | 422.3223
591.9417 | 466.6595 | 189.3151 | 356.5114
592.9417 | 466.4835 | 239.4337 | 373.7321
593.9417 | 466.3164 | 382.3113 | 422.9716
594.9417 | 466.15 | 392.607 | 425.7167
595.9417 | 466.0799 | 192.6769 | 356.2931
596.9417 | 465.9869 | 373.1541 | 418.9798
597.9417 | 465.8022 | 392.8285 | 425.2823
598.9417 | 465.71 | 401.6835 | 427.3156
599.9417 | 465.5684 | 161.4455 | 352.4876
600.9417 | 465.4122 | 154.7377 | 344.2812
601.9417 | 465.184 | 84.1767 | 335.3117
602.9417 | 465.3025 | NaN | 336.6849
603.9417 | 465.4014 | NaN | 327.4292
604.9417 | 465.4139 | NaN | 300.4096
605.9417 | 465.3346 | 1326.94 | 297.4787
606.9417 | 465.1762 | NaN | 277.7098
607.9417 | 465.0242 | NaN | 267.4698
608.9417 | 465.0081 | 289.8308 | 326.5521
609.9417 | 464.9453 | 976.1413 | 313.0136
610.9417 | 464.8512 | NaN | 296.3779
611.9417 | 464.7102 | NaN | 285.4425
612.9417 | 464.5453 | NaN | 270.983
613.9417 | 464.7215 | NaN | 260.9483
614.9417 | 464.8721 | NaN | 247.6423
615.9417 | 464.9063 | NaN | 216.6688
616.9417 | 464.8758 | NaN | 244.0145
617.9417 | 464.8121 | NaN | 222.9423
618.9417 | 464.7255 | NaN | 145.9318
619.9417 | 464.749 | NaN | 194.7378
620.9417 | 464.8176 | NaN | 171.339
621.9417 | 464.9322 | NaN | 136.3845
622.9417 | 464.8586 | NaN | 40.8313
623.9417 | 464.8118 | NaN | 22.1709
624.9417 | 464.7079 | NaN | 9.189
625.9417 | 464.5723 | NaN | 248.2071
626.9417 | 464.3836 | NaN | 331.6115
627.9417 | 464.2325 | NaN | 450.2562
628.9417 | 463.9661 | 109.9887 | 463.6081
629.9417 | 463.7106 | NaN | 10.201
630.9417 | 463.6163 | NaN | 380.1371
631.9417 | 463.4739 | 111.1559 | 437.2979
632.9417 | 463.4359 | 156.1075 | 434.2027
633.9417 | 463.2567 | 123.0345 | 434.6227
634.9417 | 463.0647 | 59.7447 | 437.7492
635.9417 | 462.9577 | -3.5559 | 437.7884
636.9417 | 462.8368 | NaN | 438.2529
637.9417 | 462.6777 | NaN | 386.7782
638.9417 | 462.5592 | NaN | 333.6316
639.9417 | 462.3144 | NaN | 316.9787
640.9417 | 461.9632 | NaN | 256.9336
641.9417 | 461.8218 | 495.5467 | 500.0432
642.9417 | 461.7641 | 498.7903 | 501.2296
643.9417 | 461.6254 | 498.8667 | 502.7881
644.9417 | 461.3605 | 498.9805 | 503.7746
645.9417 | 461.2905 | 498.7693 | 504.7784
646.9417 | 461.263 | 498.9681 | 506.2825
647.9417 | 461.1991 | 498.915 | 507.6222
648.9417 | 460.9788 | 498.8717 | 508.6755
649.9417 | 460.7474 | 498.0591 | 509.4546
650.9417 | 460.8532 | 497.6977 | 510.7768
651.9417 | 460.7384 | 497.5223 | 511.2162
652.9417 | 460.4925 | 497.6964 | 512.3163
653.9417 | 460.3791 | 498.0244 | 513.172
654.9417 | 460.1773 | 498.3503 | 513.6094
655.9417 | 460.0583 | 498.3673 | 514.6772
656.9417 | 459.8458 | 498.7042 | 515.2332
657.9417 | 459.7781 | 498.8093 | 515.8846
658.9417 | 459.7334 | 499.2884 | 516.999
659.9417 | 459.5305 | 499.3722 | 517.501
660.9417 | 459.298 | 499.3387 | 518.3089
661.9417 | 459.1259 | 498.8755 | 519.1436
662.9417 | 459.015 | 498.9127 | 519.7038
663.9417 | 458.9391 | 499.1631 | 520.4403
664.9417 | 458.8913 | 499.281 | 521.1335
665.9417 | 458.8724 | 499.1913 | 522.0121
666.9417 | 458.6719 | 499.444 | 522.2747
667.9417 | 458.4944 | 499.7544 | 522.8523
668.9417 | 458.3955 | 500.0258 | 523.9429
669.9417 | 458.4408 | 501.7021 | 524.6174
670.9417 | 458.4066 | 502.6414 | 524.8452
671.9417 | 458.3556 | 503.3388 | 525.8177
672.9417 | 458.2865 | 503.9281 | 526.2454
673.9417 | 458.3532 | 504.3845 | 526.8393
674.9417 | 458.2565 | 505.1281 | 527.2782
675.9417 | 458.1791 | 505.7787 | 527.9691
676.9417 | 458.2153 | 506.6945 | 528.4461
677.9417 | 458.2076 | 507.3661 | 529.0251
678.9417 | 458.3501 | 508.2396 | 529.7052
679.9417 | 458.454 | 508.9124 | 530.3938
680.9417 | 458.4542 | 509.6517 | 530.7906
681.9417 | 458.4121 | 510.3434 | 531.2759
682.9417 | 458.3817 | 510.7961 | 531.7299
683.9417 | 458.3818 | 511.2294 | 532.3857
684.9417 | 458.5246 | 511.7148 | 532.6541
685.9417 | 458.6609 | 512.3496 | 533.1624
686.9417 | 458.7939 | 512.6873 | 534.0689
687.9417 | 459.0136 | 513.3858 | 534.2311
688.9417 | 459.1948 | 514.1896 | 534.8915
689.9417 | 459.3091 | 513.9892 | 535.6619
690.9417 | 459.4766 | 515.0181 | 535.8115
691.9417 | 459.6937 | 515.8277 | 535.9223
692.9417 | 459.9574 | 516.5111 | 536.8039
693.9417 | 460.2147 | 517.5356 | 537.0653
694.9417 | 460.4104 | 518.1081 | 537.4048
695.9417 | 460.6263 | 519.3146 | 537.7365
696.9417 | 460.7458 | 519.8455 | 538.3541
697.9417 | 460.9182 | 520.6544 | 538.679
698.9417 | 461.1557 | 521.3173 | 538.9283
699.9417 | 461.4751 | 523.6402 | 549.5405
700.9417 | 461.8151 | 523.9089 | 540.7146
701.9417 | 462.2573 | 523.8945 | 540.1196
702.9417 | 462.4922 | 525.561 | 539.5631
703.9417 | 462.6301 | 526.1816 | 539.8512
704.9417 | 462.8097 | 527.1088 | 540.1042
705.9417 | 463.096 | 528.0864 | 540.6723
706.9417 | 463.3109 | 528.6802 | 540.6136
707.9417 | 463.5284 | 529.8473 | 540.9629
708.9417 | 463.6825 | 530.0276 | 541.3016
709.9417 | 463.816 | 530.8691 | 541.2879
710.9417 | 463.933 | 531.8332 | 541.6553
711.9417 | 464.059 | 532.697 | 542.4358
712.9417 | 464.115 | 533.1883 | 542.466
713.9417 | 464.2346 | 533.6523 | 543.2134
714.9417 | 464.3601 | 534.4475 | 543.4539
715.9417 | 464.3885 | 534.5892 | 543.6826
716.9417 | 464.4612 | 536.1276 | 543.6981
717.9417 | 464.6141 | 537.0341 | 543.653
718.9417 | 464.6671 | 537.6755 | 543.9641
719.9417 | 464.711 | 538.1932 | 544.2165
720.9417 | 464.7027 | 538.6451 | 544.5129
721.9417 | 464.6737 | 539.0945 | 544.7759
722.9417 | 464.5935 | 539.6775 | 545.0063
723.9417 | 464.5869 | 540.2088 | 545.2509
724.9417 | 464.5337 | 540.9986 | 545.4965
725.9417 | 464.5908 | 541.5259 | 545.7305
726.9417 | 464.5899 | 542.3501 | 546.0832
727.9417 | 464.5314 | 542.3656 | 546.1253
728.9417 | 464.471 | 542.8422 | 546.1651
729.9417 | 464.467 | 543.6172 | 546.4296
730.9417 | 464.3909 | 544.0966 | 546.4374
731.9417 | 464.3372 | 544.4299 | 546.4024
732.9417 | 464.353 | 545.2019 | 546.5707
733.9417 | 464.3621 | 545.5946 | 546.6837
734.9417 | 464.4573 | 546.7969 | 546.7191
735.9417 | 464.4624 | 547.3972 | 546.8639
736.9417 | 464.4143 | 548.0645 | 546.972
737.9417 | 464.3917 | 547.8499 | 547.0308
738.9417 | 464.3395 | 548.0815 | 547.0477
739.9417 | 464.3436 | 548.4014 | 547.0985
740.9417 | 464.3426 | 548.665 | 547.1826
741.9417 | 464.344 | 548.412 | 547.296
742.9417 | 464.432 | 549.5189 | 547.5301
743.9417 | 464.4918 | 549.737 | 547.6713
744.9417 | 464.4709 | 550.9221 | 547.8522
745.9417 | 464.4314 | 551.7601 | 548.0447
746.9417 | 464.4563 | 552.7262 | 548.3062
747.9417 | 464.4114 | 553.5912 | 548.5356
748.9417 | 464.3694 | 553.4179 | 548.7027
749.9417 | 464.3651 | 554.1205 | 548.7016
750.9417 | 464.3456 | 554.6115 | 549.36
751.9417 | 464.3717 | 556.2627 | 549.6442
752.9417 | 464.3273 | 557.1476 | 549.8177
753.9417 | 464.3168 | 557.8319 | 549.9961
754.9417 | 464.3496 | 558.0234 | 550.3235
755.9417 | 464.3402 | 558.2703 | 550.3575
756.9417 | 464.4417 | 555.6817 | 550.5552
757.9417 | 464.5218 | 555.482 | 550.8048
758.9417 | 464.5901 | 557.6452 | 551.1341
759.9417 | 464.6281 | 558.2317 | 551.1975
760.9417 | 464.6317 | 558.7478 | 551.7357
761.9417 | 464.639 | 560.0442 | 551.9373
762.9417 | 464.6665 | 561.0848 | 552.1553
763.9417 | 464.7259 | 561.6083 | 552.4206
764.9417 | 464.7927 | 562.7992 | 552.6851
765.9417 | 464.8652 | 565.2309 | 553.0159
766.9417 | 464.8516 | 565.6865 | 553.2918
767.9417 | 464.8281 | 566.0965 | 553.5507
768.9417 | 464.855 | 566.0302 | 553.7847
769.9417 | 464.8623 | 567.0319 | 554.0593
770.9417 | 464.9506 | 567.1788 | 554.3084
771.9417 | 464.999 | 567.5036 | 554.5673
772.9417 | 465.0425 | 567.9105 | 554.9673
773.9417 | 465.0624 | 568.193 | 555.1647
774.9417 | 465.0976 | 568.8861 | 555.4336
775.9417 | 465.1176 | 568.7106 | 555.7583
776.9417 | 465.1954 | 568.5492 | 556.1463
777.9417 | 465.2355 | 568.9618 | 556.3187
778.9417 | 465.3041 | 569.4877 | 556.6797
779.9417 | 465.2953 | 569.4867 | 556.9019
780.9417 | 465.3934 | 569.9957 | 557.2373
781.9417 | 465.5664 | 570.7381 | 557.483
782.9417 | 465.579 | 571.4624 | 557.8782
783.9417 | 465.5939 | 571.5093 | 558.085
784.9417 | 465.6556 | 571.4183 | 558.3821
785.9417 | 465.6634 | 571.9859 | 558.6683
786.9417 | 465.6333 | 572.1966 | 558.8571
787.9417 | 465.6313 | 571.7754 | 559.1226
788.9417 | 465.6851 | 571.9956 | 559.4755
789.9417 | 465.7318 | 572.1402 | 559.7532
790.9417 | 465.7211 | 572.5869 | 560.0154
791.9417 | 465.7127 | 572.8049 | 560.2691
792.9417 | 465.7592 | 573.276 | 560.4604
793.9417 | 465.8017 | 573.4082 | 560.7657
794.9417 | 465.876 | 573.8941 | 560.9471
795.9417 | 465.9899 | 574.361 | 561.3156
796.9417 | 466.0557 | 574.4499 | 561.5732
797.9417 | 466.1095 | 574.567 | 562.0998
798.9417 | 466.0723 | 572.1402 | 561.9752
799.9417 | 466.0672 | 573.0981 | 562.5765
800.9417 | 466.0765 | 573.937 | 562.6827
801.9417 | 466.1309 | 574.8123 | 563.385
802.9417 | 466.1376 | 575.2483 | 563.6169
803.9417 | 466.0935 | 576.0356 | 564.1903
804.9417 | 466.0933 | 576.2077 | 564.5029
805.9417 | 466.1398 | 576.791 | 564.701
806.9417 | 466.0849 | 576.5308 | 565.0525
807.9417 | 466.0692 | 577.1841 | 565.4511
808.9417 | 466.0822 | 577.4673 | 565.8269
809.9417 | 466.1146 | 578.6899 | 566.128
810.9417 | 466.1332 | 579.6455 | 566.6006
811.9417 | 466.1518 | 580.5422 | 566.8851
812.9417 | 466.2273 | 581.1278 | 567.3596
813.9417 | 466.2695 | 581.8838 | 567.6315
814.9417 | 466.2846 | 583.5147 | 568.2978
815.9417 | 466.2859 | 584.2395 | 568.6814
816.9417 | 466.2846 | 584.5263 | 568.878
817.9417 | 466.3379 | 585.2245 | 569.2843
818.9417 | 466.4053 | 585.5434 | 569.9671
819.9417 | 466.4219 | 585.8061 | 570.1275
820.9417 | 466.5531 | 586.2185 | 570.8047
821.9417 | 466.6097 | 586.2938 | 570.9404
822.9417 | 466.6548 | 581.5118 | 570.9054
823.9417 | 466.7548 | 585.4183 | 571.7877
824.9417 | 466.942 | 585.7464 | 572.096
825.9417 | 466.971 | 585.7309 | 572.5046
826.9417 | 467.077 | 585.6891 | 573.1107
827.9417 | 467.2863 | 585.6003 | 573.399
828.9417 | 467.2786 | 586.1781 | 574.6864
829.9417 | 467.2034 | 586.7624 | 574.7882
830.9417 | 467.2267 | 586.7151 | 574.9212
831.9417 | 467.1857 | 587.0185 | 575.2177
832.9417 | 467.1109 | 587.8109 | 575.8
833.9417 | 467.0224 | 586.4155 | 581.7534
834.9417 | 466.9911 | 587.6394 | 581.931
835.9417 | 467.0276 | 585.8554 | 582.0859
836.9417 | 467.0184 | 588.1015 | 582.9117
837.9417 | 467.0201 | 589.6675 | 583.3553
838.9417 | 466.9578 | 589.7934 | 583.6686
839.9417 | 466.9956 | 588.1598 | 584.151
840.9417 | 466.9518 | 589.1758 | 584.175
841.9417 | 466.8444 | 589.6639 | 584.7632
842.9417 | 466.826 | 590.3705 | 585.5249
843.9417 | 466.8863 | 590.9326 | 585.7887
844.9417 | 466.9517 | 591.5903 | 585.6618
845.9417 | 466.8832 | 591.7647 | 586.4957
846.9417 | 466.8848 | 592.8825 | 587.0167
847.9417 | 467.0139 | 593.4015 | 587.229
848.9417 | 467.1076 | 593.698 | 587.6036
849.9417 | 467.1847 | 593.6663 | 588.107
850.9417 | 467.1764 | 593.9379 | 589.2374
851.9417 | 467.1733 | 593.7858 | 589.6769
852.9417 | 467.2292 | 593.9564 | 590.2543
853.9417 | 467.3164 | 594.748 | 590.3167
854.9417 | 467.3402 | 594.4808 | 591.1739
855.9417 | 467.3323 | 594.739 | 591.3966
856.9417 | 467.3625 | 594.6721 | 592.1721
857.9417 | 467.4586 | 595.2178 | 591.9704
858.9417 | 467.472 | 594.6715 | 592.3716
859.9417 | 467.4314 | 594.9887 | 592.3676
860.9417 | 467.4553 | 595.2117 | 592.9764
861.9417 | 467.4844 | 595.8508 | 592.853
862.9417 | 467.4722 | 596.259 | 593.0849
863.9417 | 467.4935 | 596.7772 | 592.8346
864.9417 | 467.5775 | 597.3849 | 592.1733
865.9417 | 467.6057 | 598.292 | 591.8017
866.9417 | 467.6977 | 598.503 | 591.9095
867.9417 | 467.7394 | 598.7699 | 592.0622
868.9417 | 467.7473 | 598.6035 | 592.0826
869.9417 | 467.6735 | 599.4127 | 592.5437
870.9417 | 467.6749 | 599.9279 | 592.9561
871.9417 | 467.7068 | 600.7022 | 593.3444
872.9417 | 467.7587 | 601.1048 | 593.7873
873.9417 | 467.8227 | 601.4189 | 594.4602
874.9417 | 467.8247 | 601.7341 | 594.744
875.9417 | 467.9373 | 602.3918 | 595.1619
876.9417 | 467.9742 | 602.9889 | 595.5999
877.9417 | 467.9648 | 603.3148 | 595.8988
878.9417 | 468.0229 | 603.3475 | 596.1148
879.9417 | 467.9852 | 603.9743 | 596.6563
880.9417 | 467.9383 | 604.0111 | 597.1084
881.9417 | 467.933 | 604.651 | 597.4858
882.9417 | 467.895 | 604.9472 | 598.0452
883.9417 | 467.9371 | 605.2533 | 598.3804
884.9417 | 468.0645 | 605.2959 | 598.8563
885.9417 | 468.0865 | 605.6211 | 599.1364
886.9417 | 468.0386 | 605.5697 | 599.2907
887.9417 | 468.0557 | 605.9777 | 599.5413
888.9417 | 468.0661 | 606.3318 | 599.7265
889.9417 | 468.0324 | 606.0915 | 600.1816
890.9417 | 468.0019 | 606.4273 | 600.4783
891.9417 | 467.9351 | 606.768 | 600.8455
892.9417 | 467.8507 | 607.113 | 601.0862
893.9417 | 467.8113 | 607.6296 | 601.2948
894.9417 | 467.9157 | 608.3802 | 601.507
895.9417 | 467.8806 | 608.9508 | 601.863
896.9417 | 467.815 | 609.0261 | 602.1344
897.9417 | 467.7654 | 609.3402 | 602.335
898.9417 | 467.7376 | 610.1983 | 602.5767
899.9417 | 467.8145 | 610.9047 | 602.9692
900.9417 | 467.9416 | 611.0303 | 603.309
901.9417 | 467.9466 | 611.284 | 603.6599
902.9417 | 468.0792 | 611.3863 | 603.8675
903.9417 | 468.1979 | 611.7772 | 604.5306
904.9417 | 468.2351 | 612.2537 | 604.6962
905.9417 | 468.2166 | 612.9348 | 605.2805
906.9417 | 468.2512 | 613.4647 | 605.7337
907.9417 | 468.3973 | 614.1367 | 606.1651
908.9417 | 468.3274 | 614.5278 | 606.2648
909.9417 | 468.286 | 614.9102 | 606.1893
910.9417 | 468.2142 | 615.7107 | 606.4942
911.9417 | 468.1824 | 614.9497 | 606.6107
912.9417 | 468.2016 | 615.6372 | 606.3838
913.9417 | 468.319 | 616.375 | 607.0232
914.9417 | 468.4496 | 617.215 | 607.3082
915.9417 | 468.5141 | 617.7837 | 607.7215
916.9417 | 468.5784 | 618.1619 | 607.876
917.9417 | 468.7132 | 619.1778 | 607.9958
918.9417 | 468.8171 | 620.2267 | 608.2688
919.9417 | 468.9308 | 620.7534 | 608.4661
920.9417 | 468.8391 | 621.4806 | 608.7952
921.9417 | 468.7114 | 621.8009 | 609.0502
922.9417 | 468.6159 | 621.933 | 609.2203
923.9417 | 468.5785 | 623.047 | 609.5981
924.9417 | 468.6356 | 623.0304 | 609.6442
925.9417 | 468.7205 | 623.9007 | 609.9907
926.9417 | 468.6939 | 626.4032 | 606.7966
927.9417 | 468.6171 | 625.1408 | 610.7538
928.9417 | 468.7004 | 625.7036 | 611.0215
929.9417 | 468.7085 | 626.129 | 611.2775
930.9417 | 468.7242 | 626.8928 | 611.5058
931.9417 | 468.7344 | 627.4249 | 611.695
932.9417 | 468.7761 | 628.0133 | 611.8968
933.9417 | 468.6919 | 628.5113 | 612.2503
934.9417 | 468.5728 | 629.4161 | 612.368
935.9417 | 468.5308 | 629.4411 | 612.074
936.9417 | 468.5633 | 630.2712 | 612.6726
937.9417 | 468.6314 | 631.1244 | 612.4133
938.9417 | 468.6501 | 631.6886 | 612.2838
939.9417 | 468.5826 | 632.2433 | 612.0492
940.9417 | 468.441 | 632.8351 | 612.3964
941.9417 | 468.2419 | 633.5774 | 612.7739
942.9417 | 468.0957 | 635.1249 | 610.7739
943.9417 | 468.0818 | 635.7397 | 610.6473
944.9417 | 468.0061 | 634.933 | 613.3473
945.9417 | 468.0755 | 635.6259 | 613.4445
946.9417 | 468.0163 | 636.73 | 613.6368
947.9417 | 467.8482 | 637.1496 | 613.6681
948.9417 | 467.7537 | 637.0683 | 613.4204
949.9417 | 467.7016 | 640.0221 | 609.5984
950.9417 | 467.6124 | 641.0443 | 608.7975
951.9417 | 467.53 | 642.4552 | 607.1108
952.9417 | 467.4198 | 642.1487 | 608.396
953.9417 | 467.4026 | 642.1401 | 608.0763
954.9417 | 467.4442 | 642.8574 | 607.6946
955.9417 | 467.4383 | 643.8197 | 607.329
956.9417 | 467.4564 | 644.5218 | 607.0703
957.9417 | 467.4579 | 644.6974 | 606.9937
958.9417 | 467.454 | 645.3019 | 607.3167
959.9417 | 467.4733 | 645.7564 | 607.5859
960.9417 | 467.6065 | 646.1263 | 607.8795
961.9417 | 467.6352 | 646.8748 | 608.3817
962.9417 | 467.6773 | 647.2689 | 608.8822
963.9417 | 467.6642 | 647.6951 | 608.8789
964.9417 | 467.6759 | 648.136 | 608.575
965.9417 | 467.662 | 648.91 | 608.7539
966.9417 | 467.6383 | 649.4645 | 609.268
967.9417 | 467.7686 | 650.4206 | 609.5451
968.9417 | 467.7634 | 650.7219 | 609.8634
969.9417 | 467.7779 | 651.4432 | 610.0098
970.9417 | 467.7571 | 651.9725 | 610.7843
971.9417 | 467.8001 | 652.9211 | 611.4953
972.9417 | 467.8107 | 653.6498 | 611.9114
973.9417 | 467.8219 | 653.6849 | 612.1626
974.9417 | 467.9159 | 654.4328 | 612.4348
975.9417 | 467.9863 | 655.1349 | 613.0094
976.9417 | 468.032 | 655.7484 | 613.4828
977.9417 | 468.1597 | 656.2958 | 613.5751
978.9417 | 468.2037 | 656.6124 | 613.8565
979.9417 | 468.2322 | 656.754 | 614.1769
980.9417 | 468.2047 | 657.2754 | 614.8403
981.9417 | 468.1947 | 657.9216 | 615.3241
982.9729 | 468.2559 | 658.3892 | 615.4634
983.9417 | 468.2862 | 658.7902 | 615.5461
984.9417 | 468.2864 | 659.3863 | 615.8023
985.9417 | 468.3508 | 659.8689 | 616.1716
986.9417 | 468.4442 | 660.4226 | 616.5561
987.9417 | 468.4488 | 661.0194 | 616.9065
988.9417 | 468.4926 | 661.5568 | 617.1804
989.9417 | 468.4119 | 661.9481 | 617.3521
990.9417 | 468.3681 | 662.9842 | 617.7699
991.9417 | 468.4184 | 664.0325 | 618.219
992.9417 | 468.3872 | 664.9663 | 618.5047
993.9417 | 468.4362 | 665.5241 | 618.5121
994.9417 | 468.388 | 666.1792 | 618.6504
995.9417 | 468.3911 | 666.7441 | 619.3212
996.9417 | 468.5529 | 667.3972 | 619.6116
997.9417 | 468.5788 | 668.1493 | 619.876
998.9417 | 468.6571 | 668.5611 | 619.7506
999.9417 | 468.7159 | 668.8953 | 620.1368
1000.9417 | 468.7987 | 669.8314 | 620.6086
1001.9417 | 468.692 | 670.1051 | 621.0305
1002.9417 | 468.6495 | 670.3763 | 620.9623
1003.9417 | 468.6196 | 670.6635 | 621.1055
1004.9417 | 468.661 | 671.3399 | 621.495
1005.9417 | 468.6702 | 671.558 | 621.907
1006.9417 | 468.6618 | 671.8579 | 622.0419
1007.9417 | 468.6157 | 672.1381 | 622.181
1008.9417 | 468.5315 | 672.4004 | 622.0077
1009.9417 | 468.5067 | 673.0997 | 622.2585
1010.9417 | 468.4406 | 674.0809 | 622.8087
1011.9417 | 468.5902 | 674.8028 | 623.1461
1012.9417 | 468.7467 | 675.6259 | 623.3895
1013.9417 | 468.9163 | 676.3589 | 623.4399
1014.9417 | 469.0099 | 676.9864 | 623.7497
1015.9417 | 468.9746 | 677.6677 | 624.1756
1016.9417 | 469.0765 | 677.9232 | 624.5359
1017.9417 | 469.0254 | 678.1249 | 624.5587
1018.9417 | 468.9972 | 677.8232 | 624.5785
1019.9417 | 468.9605 | 677.5159 | 624.72
1020.9417 | 468.8835 | 677.6866 | 625.2208
1021.9417 | 468.9135 | 677.7593 | 625.4225
1022.9417 | 469.0004 | 677.7672 | 625.6008
1023.9417 | 469.026 | 677.7739 | 625.4333
1024.9417 | 469.0002 | 678.3583 | 625.9125
1025.9417 | 469.0038 | 678.5364 | 625.9595
1026.9417 | 469.0068 | 678.7494 | 626.5098
1027.9417 | 469.1711 | 678.9709 | 626.6497
1028.9417 | 469.2157 | 679.6647 | 627.3958
1029.9417 | 469.2181 | 679.6674 | 626.9451
1030.9417 | 469.277 | 679.897 | 627.6386
1031.9417 | 469.4011 | 679.7188 | 627.8534
1032.9417 | 469.4985 | 679.8204 | 627.8975
1033.9417 | 469.4768 | 679.3787 | 627.8292
1034.9417 | 469.3893 | 679.3451 | 628.3341
1035.9417 | 469.5025 | 679.1225 | 628.132
1036.9417 | 469.5179 | 679.0682 | 628.5142
1037.9417 | 469.5009 | 679.0036 | 628.7991
1038.9417 | 469.4459 | 678.9576 | 628.8731
1039.9417 | 469.3936 | 679.188 | 628.7842
1040.9417 | 469.4621 | 679.4885 | 629.0455
1041.9417 | 469.5726 | 679.5617 | 629.179
1042.9417 | 469.5622 | 679.5848 | 629.4295
1043.9417 | 469.5177 | 679.4626 | 629.6737
1044.9417 | 469.5106 | 679.8005 | 629.9658
1045.9417 | 469.4771 | 680.1038 | 630.2958
1046.9417 | 469.4085 | 680.5254 | 630.5481
1047.9417 | 469.3474 | 680.9733 | 630.9233
1048.9417 | 469.3595 | 681.101 | 631.0878
1049.9417 | 469.3908 | 681.1287 | 631.3422
1050.9417 | 469.3947 | 681.5419 | 631.374
1051.9417 | 469.3673 | 681.9202 | 631.5554
1052.9417 | 469.2995 | 682.2577 | 631.6606
1053.9417 | 469.2439 | 682.8294 | 631.7753
1054.9417 | 469.222 | 682.8798 | 631.6382
1055.9417 | 469.1739 | 683.021 | 631.7276
1056.9417 | 469.2242 | 683.3291 | 631.8398
1057.9417 | 469.1883 | 683.3859 | 632.0071
1058.9417 | 469.151 | 683.4804 | 632.0416
1059.9417 | 469.0953 | 683.6532 | 632.1326
1060.9417 | 468.993 | 683.794 | 632.1977
1061.9417 | 468.9228 | 684.2249 | 632.5301
1062.9417 | 468.9247 | 684.4148 | 632.7531
1063.9417 | 468.9275 | 684.6449 | 632.7097
1064.9417 | 468.8213 | 684.9854 | 632.8329
1065.9417 | 468.7814 | 685.1124 | 632.8454
1066.9417 | 468.7734 | 685.5607 | 633.1136
1067.9417 | 468.6622 | 685.669 | 633.1559
1068.9417 | 468.7226 | 685.788 | 633.1992
1069.9417 | 468.8146 | 685.7428 | 633.0982
1070.9417 | 468.7192 | 685.7243 | 633.3181
1071.9417 | 468.5736 | 685.8443 | 633.5697
1072.9417 | 468.5243 | 685.8454 | 633.5513
1073.9417 | 468.5466 | 685.7317 | 633.7696
1074.9417 | 468.4771 | 685.7142 | 633.9021
1075.9417 | 468.5162 | 685.6773 | 634.0408
1076.9417 | 468.6292 | 685.8622 | 634.2876
1077.9417 | 468.6824 | 685.7994 | 634.6242
1078.9417 | 468.5726 | 685.8644 | 634.5706
1079.9417 | 468.5957 | 685.5861 | 634.7446
1080.9417 | 468.6138 | 685.7028 | 634.9425
1081.9417 | 468.5173 | 685.8372 | 634.7118
1082.9417 | 468.6048 | 685.9349 | 634.8509
1083.9417 | 468.6635 | 686.0387 | 634.423
1084.9417 | 468.7342 | 686.1668 | 634.7777
1085.9417 | 468.7152 | 686.2196 | 634.7584
1086.9417 | 468.7043 | 686.3865 | 634.739
1087.9417 | 468.7241 | 686.3419 | 634.6911
1088.9417 | 468.6894 | 686.4213 | 634.8684
1089.9417 | 468.6489 | 686.7593 | 635.0082
1090.9417 | 468.8289 | 687.3068 | 634.9076
1091.9417 | 469.0956 | 687.0368 | 634.9392
1092.9417 | 469.0877 | 687.4049 | 634.9296
1093.9417 | 469.1449 | 687.6389 | 634.9555
1094.9417 | 469.0979 | 687.7413 | 634.2107
1095.9417 | 469.1026 | 687.7781 | 634.6462
1096.9417 | 469.173 | 688.264 | 634.4104
1097.9417 | 469.3451 | 688.5555 | 634.489
1098.9417 | 469.448 | 688.5504 | 634.5425
1099.9417 | 469.3331 | 688.5973 | 634.7973
1100.9417 | 469.3745 | 688.8904 | 634.9339
1101.9417 | 469.3485 | 689.4775 | 635.0107
1102.9417 | 469.1906 | 689.5327 | 635.2739
1103.9417 | 469.0935 | 689.6418 | 635.5899
1104.9417 | 469.0903 | 689.7042 | 635.8727
1105.9417 | 469.1235 | 689.8225 | 636.1024
1106.9417 | 469.1528 | 689.588 | 636.2234
1107.9417 | 469.1122 | 689.8777 | 636.2278
1108.9417 | 469.1594 | 689.6612 | 636.4025
1109.9417 | 469.1561 | 689.7306 | 636.7146
1110.9417 | 469.1641 | 689.5897 | 636.5837
1111.9417 | 469.1303 | 689.5678 | 636.9064
1112.9417 | 468.9774 | 689.6935 | 636.8456
1113.9417 | 468.9802 | 689.6985 | 637.3111
1114.9417 | 469.0174 | 689.0611 | 637.0518
1115.9417 | 468.9957 | 689.1119 | 637.4901
1116.9417 | 468.9263 | 689.0445 | 637.8318
1117.9417 | 468.839 | 688.8295 | 638.4239
1118.9417 | 468.7623 | 687.4704 | 639.088
1119.9417 | 468.7454 | 687.1794 | 639.4089
1120.9417 | 468.7634 | 687.0336 | 639.4982
1121.9417 | 468.8099 | 687.4658 | 639.7857
1122.9417 | 468.8099 | 688.0235 | 640.013
1123.9417 | 468.8032 | 688.1317 | 640.0011
1124.9417 | 468.7609 | 687.8753 | 639.9087
1125.9417 | 468.6107 | 687.7191 | 640.0266
1126.9417 | 468.4611 | 687.6366 | 639.9847
1127.9417 | 468.3283 | 687.4724 | 640.1062
1128.9417 | 468.2569 | 687.7113 | 640.3808
1129.9417 | 468.195 | 687.5374 | 640.6467
1130.9417 | 468.2207 | 687.8941 | 640.8359
1131.9417 | 468.1592 | 687.98 | 640.6702
1132.9417 | 468.1743 | 687.716 | 640.7091
1133.9417 | 468.1825 | 687.7763 | 640.8479
1134.9417 | 468.2204 | 687.6972 | 640.8089
1135.9417 | 468.1583 | 687.5748 | 640.9742
1136.9417 | 468.1097 | 687.272 | 640.9147
1137.9417 | 468.1332 | 687.272 | 640.9839
1138.9417 | 468.1175 | 687.2631 | 640.6453
1139.9417 | 468.1651 | 687.5785 | 641.0862
1140.9417 | 468.1178 | 687.7632 | 640.9902
1142.1292 | 468.1283 | 687.1831 | 640.4665
1143.051 | 468.3027 | 687.1811 | 640.5436
1144.051 | 468.347 | 687.171 | 640.6233
1144.9417 | 468.3861 | 686.309 | 639.3483
1145.9417 | 468.2987 | 687.1692 | 640.7103
1146.9417 | 468.2606 | 687.1806 | 640.7771
1147.9573 | 468.3252 | 686.9735 | 640.8468
1148.9417 | 468.4088 | 687.0924 | 640.7705
1149.9417 | 468.5592 | 687.1875 | 640.197
1150.9417 | 468.6885 | 687.4698 | 639.723
1151.9417 | 468.8494 | 687.5001 | 639.5779
1152.9417 | 468.8118 | 687.2311 | 639.4686
1153.9417 | 468.7817 | 687.0154 | 639.4898
1154.9417 | 468.8275 | 687.0734 | 639.51
1155.9417 | 468.8493 | 687.0791 | 639.1848
1156.9417 | 468.8788 | 687.1815 | 639.1007
1158.0354 | 468.8995 | 686.8209 | 638.2366
1158.9417 | 468.8986 | 687.2689 | 638.8518
1159.9417 | 468.7588 | 686.8797 | 638.4331
1160.9417 | 468.8737 | 686.9851 | 638.3497
1161.9729 | 468.9236 | 686.4896 | 637.1025
1162.9417 | 468.8908 | 686.7269 | 637.7318
1163.9417 | 468.8548 | 686.5785 | 637.4012
1164.9417 | 468.8285 | 686.6212 | 637.2018
1165.9417 | 468.8905 | 686.2804 | 637.0214
1166.9417 | 468.7904 | 684.2876 | 633.7205
1167.9417 | 468.7046 | 685.5775 | 636.5778
1168.9417 | 468.6518 | 685.4662 | 636.5711
1169.9417 | 468.6741 | 685.3179 | 636.2581
1170.9417 | 468.6911 | 685.1418 | 636.0898
1171.9885 | 468.6186 | 685.123 | 636.0324
1172.9417 | 468.4636 | 685.2058 | 636.0697
1173.9417 | 468.65 | 684.9555 | 635.9714
1174.9417 | 468.88 | 684.9 | 635.9556
1175.9885 | 468.93 | 684.2344 | 635.5946
1176.9417 | 468.9928 | 684.1634 | 635.754
1178.051 | 469.003 | 683.3233 | 634.9758
1179.0823 | 468.8293 | 683.15 | 633.8655
1179.9885 | 468.7896 | 683.4151 | 634.946
1180.9417 | 468.7658 | 682.959 | 635.1421
1181.9417 | 468.7499 | 682.9634 | 634.8895
1182.9417 | 468.7412 | 682.8039 | 634.679
1183.9417 | 468.6595 | 682.5418 | 633.8368
1184.9417 | 468.5856 | 682.5309 | 633.8341
1185.9417 | 468.5205 | 682.3884 | 633.6553
1186.9417 | 468.6093 | 682.022 | 633.5347
1187.9417 | 468.7828 | 681.5751 | 633.073
1188.9417 | 468.9634 | 680.7375 | 633.1774
1189.9417 | 469.0946 | 680.2105 | 633.04
1190.9417 | 469.185 | 679.822 | 632.7731
1191.9417 | 469.2148 | 679.28 | 632.5681
1192.9417 | 469.1818 | 678.8705 | 632.4473
1193.9417 | 469.3013 | 678.3052 | 632.1561
1194.9417 | 469.2911 | 677.658 | 631.6552
1195.9417 | 469.3126 | 677.2155 | 632.1036
1196.9417 | 469.43 | 676.4753 | 632.1491
1197.9417 | 469.5493 | 675.7018 | 632.248
1198.9417 | 469.4314 | 675.1441 | 631.8577
1199.9417 | 469.2945 | 674.4914 | 631.7461
1200.9417 | 469.187 | 673.6754 | 631.9519
1201.9417 | 469.0609 | 672.8734 | 631.552
1202.9417 | 468.9176 | 672.0358 | 631.1662
1203.9417 | 468.7676 | 671.5182 | 630.7797
1204.9417 | 468.6708 | 670.3523 | 630.3285
1205.9417 | 468.6731 | 669.4364 | 629.7161
1206.9417 | 468.7583 | 668.7287 | 629.8994
1207.9417 | 468.6847 | 667.7136 | 629.7387
1208.9417 | 468.6009 | 666.928 | 629.6035
1209.9417 | 468.576 | 665.8963 | 629.1895
1210.9417 | 468.6934 | 665.0436 | 629.1519
1211.9417 | 468.746 | 664.1815 | 628.8941
1212.9417 | 468.6707 | 663.5568 | 628.8802
1213.9417 | 468.7963 | 662.8473 | 628.6181
1214.9417 | 468.8742 | 662.1183 | 628.1724
1215.9417 | 468.8788 | 661.5741 | 627.9573
1216.9417 | 468.9691 | 660.874 | 627.6845
1217.9417 | 469.1306 | 660.3944 | 627.5465
1218.9417 | 469.2281 | 659.6857 | 627.5153
1219.9417 | 469.2499 | 659.2 | 627.0533
1220.9417 | 469.2855 | 658.9278 | 626.8316
1221.9417 | 469.3774 | 658.3822 | 626.603
1222.9417 | 469.4257 | 657.8259 | 626.3678
1223.9417 | 469.5541 | 657.4489 | 626.2432
1224.9417 | 469.6166 | 656.9051 | 625.8729
1225.9417 | 469.6233 | 656.5994 | 625.9013
1226.9417 | 469.6643 | 656.2528 | 625.7436
1227.9417 | 469.5672 | 655.7402 | 625.6635
1228.9417 | 469.41 | 655.1373 | 625.1152
1229.9417 | 469.4348 | 654.8841 | 625.2896
1230.9417 | 469.4987 | 654.2647 | 625.1075
1231.9417 | 469.5059 | 653.7024 | 625.0837
1232.9417 | 469.4579 | 653.2816 | 624.9538
1233.9417 | 469.5593 | 652.948 | 624.9175
1234.9417 | 469.5996 | 652.5137 | 624.3633
1235.9417 | 469.5709 | 652.2814 | 624.1374
1236.9417 | 469.6323 | 651.9444 | 623.8309
1237.9417 | 469.6072 | 651.2988 | 624.0581
1238.9417 | 469.6681 | 651.0305 | 623.378
1239.9417 | 469.6263 | 650.6085 | 623.2831
1240.9417 | 469.742 | 650.2086 | 621.8692
1241.9417 | 469.7978 | 649.9584 | 622.0165
1242.9417 | 469.8324 | 649.6108 | 621.5489
1243.9417 | 469.7967 | 649.2446 | 621.417
1244.9417 | 469.8301 | 649.0905 | 621.0957
1245.9417 | 469.8287 | 648.7864 | 620.5184
1246.9417 | 469.8232 | 648.5488 | 620.1261
1247.9417 | 469.951 | 648.164 | 620.142
1248.9417 | 470.013 | 647.7192 | 619.5811
1249.9417 | 469.9172 | 647.3851 | 619.2542
1250.9417 | 469.8518 | 647.2566 | 619.5866
1251.9417 | 469.8852 | 646.7513 | 618.7112
1252.9417 | 469.9013 | 646.0784 | 618.1334
1253.9417 | 469.9058 | 645.5865 | 617.4737
1254.9417 | 469.9528 | 645.1697 | 617.0518
1255.9417 | 470.105 | 644.7518 | 616.4067
1256.9417 | 470.0839 | 644.3172 | 616.1424
1257.9417 | 470.0794 | 643.919 | 615.7472
1258.9417 | 470.1012 | 643.559 | 615.6051
1259.9417 | 470.133 | 643.0748 | 615.2537
1260.9417 | 470.0789 | 642.7003 | 614.9722
1261.9417 | 470.0677 | 642.0791 | 614.6479
1262.9417 | 470.0393 | 641.5836 | 614.4524
1263.9417 | 469.9894 | 641.1187 | 614.0555
1264.9417 | 470.061 | 640.7406 | 613.8181
1265.9417 | 470.0565 | 640.2856 | 613.3983
1266.9417 | 470.0186 | 639.7555 | 613.1504
1267.9417 | 469.9683 | 639.1777 | 612.9832
1268.9417 | 470.0273 | 638.6692 | 612.856
1269.9417 | 470.0718 | 638.2199 | 611.8103
1270.9417 | 470.161 | 637.7422 | 611.7112
1271.9417 | 470.1295 | 637.3204 | 611.0518
1272.9417 | 470.0647 | 636.7901 | 610.5645
1273.9417 | 469.9549 | 636.2655 | 610.3843
1274.9417 | 470.0607 | 635.5305 | 609.5544
1275.9417 | 470.0909 | 635.0845 | 609.7732
1276.9417 | 470.1395 | 634.3643 | 609.5922
1277.9417 | 470.0669 | 633.6671 | 609.5227
1278.9417 | 470.0548 | 632.9487 | 609.2587
1279.9417 | 469.9747 | 632.3081 | 609.1284
1280.9417 | 470.0349 | 631.8052 | 608.5789
1281.9417 | 469.8964 | 631.3337 | 608.0918
1282.9417 | 469.7656 | 630.7902 | 607.4961
1283.9417 | 469.7033 | 630.3692 | 607.096
1284.9417 | 469.7757 | 629.7266 | 606.6681
1285.9417 | 469.7741 | 629.2186 | 606.4967
1286.9417 | 469.7507 | 628.6978 | 606.3101
1287.9417 | 469.728 | 628.1478 | 606.2245
1288.9417 | 469.7624 | 627.4787 | 605.7218
1289.9417 | 469.8133 | 627.1152 | 605.9216
1290.9417 | 469.8739 | 626.5637 | 605.8458
1291.9417 | 469.8831 | 626.0647 | 605.6536
1292.9417 | 469.9126 | 625.587 | 605.2666
1293.9417 | 469.9662 | 625.1427 | 604.6621
1294.9417 | 470.1014 | 624.8108 | 604.5935
1295.9417 | 470.0185 | 624.333 | 604.2083
1296.9417 | 469.8562 | 623.8341 | 603.7574
1297.9417 | 469.7609 | 623.4474 | 603.5039
1298.9417 | 469.7565 | 622.9818 | 602.9139
1299.9417 | 469.723 | 622.5885 | 602.4831
1300.9417 | 469.7181 | 622.1863 | 602.1189
1301.9417 | 469.7925 | 621.7582 | 601.823
1302.9417 | 469.7343 | 621.2497 | 601.3429
1303.9417 | 469.6662 | 620.7006 | 600.9976
1304.9417 | 469.654 | 620.3862 | 600.9381
1305.9417 | 469.667 | 619.8077 | 600.645
1306.9417 | 469.6338 | 619.2009 | 599.9847
1307.9417 | 469.5653 | 618.7717 | 599.521
1308.9417 | 469.5149 | 618.1863 | 598.5396
1309.9417 | 469.4837 | 617.7977 | 598.4774
1310.9417 | 469.4377 | 617.2429 | 597.6588
1311.9417 | 469.3726 | 616.8896 | 597.1033
1312.9417 | 469.2444 | 616.4805 | 596.5033
1313.9417 | 469.1193 | 615.9586 | 595.6811
1314.9417 | 469.0735 | 615.5858 | 595.0763
1315.9417 | 469.0039 | 615.3026 | 594.5472
1316.9417 | 469.0369 | 614.9148 | 593.9464
1317.9417 | 469.1377 | 614.5372 | 593.7027
1318.9417 | 469.3485 | 614.1251 | 592.7487
1319.9417 | 469.395 | 613.7937 | 592.064
1320.9417 | 469.4496 | 613.4998 | 591.564
1321.9417 | 469.4547 | 613.1742 | 590.5087
1322.9417 | 469.5119 | 612.8561 | 589.7663
1323.9417 | 469.6817 | 612.4186 | 589.276
1324.9417 | 469.5997 | 611.9482 | 588.7698
1325.9417 | 469.574 | 611.4616 | 588.3684
1326.9417 | 469.566 | 610.8803 | 587.8929
1327.9417 | 469.4416 | 610.3943 | 587.4317
1328.9417 | 469.51 | 609.9736 | 586.7792
1329.9417 | 469.5376 | 609.4652 | 586.1213
1330.9417 | 469.6467 | 608.8916 | 585.7159
1331.9417 | 469.759 | 608.36 | 585.2886
1332.9417 | 469.9132 | 607.8493 | 584.8891
1333.9417 | 470.0501 | 607.278 | 583.8406
1334.9417 | 470.1787 | 606.7222 | 583.3406
1335.9417 | 470.2602 | 606.2091 | 583.0607
1336.9417 | 470.2331 | 605.8157 | 582.5102
1337.9417 | 470.1858 | 605.2688 | 582.1917
1338.9417 | 470.163 | 604.7169 | 581.7253
1339.9417 | 470.1738 | 604.2144 | 581.204
1340.9417 | 470.2002 | 603.6702 | 580.6345
1341.9417 | 470.091 | 603.0722 | 580.3121
1342.9417 | 470.1105 | 602.5389 | 579.7756
1343.9417 | 470.0976 | 602.0149 | 579.3827
1344.9417 | 470.0693 | 601.4503 | 578.9506
1345.9417 | 470.1218 | 600.9656 | 578.5675
1346.9417 | 470.164 | 600.4441 | 578.1708
1347.9417 | 470.0941 | 599.9405 | 577.5462
1348.9417 | 470.1261 | 599.3782 | 576.9615
1349.9417 | 470.1916 | 598.9175 | 577.0011
1350.9417 | 470.2191 | 598.3823 | 576.5075
1351.9417 | 470.2788 | 597.8287 | 576.1347
1352.9417 | 470.3435 | 597.296 | 575.6907
1353.9417 | 470.2978 | 596.705 | 574.8598
1354.9417 | 470.4029 | 596.2096 | 574.6146
1355.9417 | 470.4657 | 595.6482 | 574.0232
1356.9417 | 470.506 | 595.0662 | 573.5107
1357.9417 | 470.4443 | 594.4972 | 572.9356
1358.9417 | 470.3312 | 593.9043 | 572.3886
1359.9417 | 470.2702 | 593.2674 | 571.9491
1360.9417 | 470.2115 | 592.6477 | 571.312
1361.9417 | 470.0196 | 592.0147 | 570.8772
1362.9417 | 469.9522 | 591.409 | 570.4728
1363.9417 | 470.0594 | 590.7626 | 570.0249
1364.9417 | 470.0612 | 590.1042 | 569.652
1365.9417 | 470.0987 | 589.4067 | 568.6933
1366.9417 | 470.1439 | 588.7715 | 568.2663
1367.9417 | 470.0644 | 588.0798 | 567.6266
1368.9417 | 469.9432 | 587.4271 | 567.0963
1369.9417 | 469.8961 | 586.7938 | 566.418
1370.9417 | 470.0156 | 586.1467 | 565.7236
1371.9417 | 470.1519 | 585.5546 | 565.3135
1372.9417 | 470.2682 | 584.9588 | 564.7648
1373.9417 | 470.2739 | 584.327 | 564.1989
1374.9417 | 470.1117 | 583.7976 | 563.6616
1375.9417 | 470.1312 | 583.1624 | 563.0713
1376.9417 | 470.066 | 582.5886 | 562.6342
1377.9417 | 470.1583 | 581.999 | 562.1424
1378.9417 | 470.2585 | 581.3489 | 561.5946
1379.9417 | 470.3202 | 580.7976 | 561.1562
1380.9417 | 470.3261 | 580.2165 | 560.515
1381.9417 | 470.3802 | 579.6333 | 560.0395
1382.9417 | 470.4813 | 579.0417 | 559.3178
1383.9417 | 470.4625 | 578.4433 | 558.9199
1384.9417 | 470.5235 | 577.8843 | 558.649
1385.9417 | 470.4989 | 577.3263 | 558.076
1386.9417 | 470.6097 | 576.7936 | 557.6419
1387.9417 | 470.6461 | 576.2645 | 557.0079
1388.9417 | 470.654 | 575.7274 | 556.0805
1389.9417 | 470.5552 | 575.2371 | 555.8684
1390.9417 | 470.4584 | 574.6829 | 555.3138
1391.9417 | 470.4458 | 574.0891 | 555.036
1392.9417 | 470.385 | 573.5329 | 554.4851
1393.9417 | 470.2459 | 572.723 | 554.1759
1394.9417 | 470.1248 | 572.1625 | 553.6601
1395.9417 | 470.0986 | 571.6885 | 553.2261
1396.9417 | 470.0633 | 571.2149 | 552.6986
1397.9417 | 469.9676 | 570.7317 | 552.2867
1398.9417 | 469.922 | 570.2318 | 551.8169
1399.9417 | 469.8663 | 569.7183 | 551.2706
1400.9417 | 469.7659 | 569.3082 | 550.7246
1401.9417 | 469.6599 | 569.0173 | 549.9844
1402.9417 | 469.6211 | 568.5898 | 549.5467
1403.9417 | 469.5877 | 568.0908 | 549.148
1404.9417 | 469.6206 | 567.6361 | 548.6348
1405.9417 | 469.6066 | 567.1752 | 548.2941
1406.9417 | 469.4744 | 566.7249 | 547.9674
1407.9417 | 469.3676 | 566.2027 | 547.44
1408.9417 | 469.3573 | 565.7613 | 547.007
1409.9417 | 469.4578 | 565.3548 | 546.5154
1410.9417 | 469.4879 | 564.9509 | 545.8207
1411.9417 | 469.6164 | 564.5126 | 545.3605
1412.9417 | 469.6817 | 564.0988 | 544.9986
1413.9417 | 469.8264 | 563.6951 | 544.6623
1414.9417 | 469.8037 | 563.2593 | 544.3077
1415.9417 | 469.8594 | 562.8015 | 543.8713
1416.9417 | 470.0171 | 562.4089 | 543.5004
1417.9417 | 470.1701 | 561.9326 | 543.0664
1418.9417 | 470.1933 | 561.5347 | 542.5585
1419.9417 | 470.3907 | 561.0835 | 542.2221
1420.9417 | 470.3423 | 560.6357 | 541.8249
1421.9417 | 470.3593 | 560.1839 | 541.1709
1422.9417 | 470.3661 | 559.7695 | 540.7064
1423.9417 | 470.392 | 559.3441 | 540.3374
1424.9417 | 470.4303 | 558.901 | 539.8326
1425.9417 | 470.3567 | 558.4962 | 539.3223
1426.9417 | 470.3409 | 558.0884 | 538.9301
1427.9417 | 470.3283 | 557.6807 | 538.5324
1428.9417 | 470.3783 | 557.2181 | 537.9843
1429.9417 | 470.438 | 556.8093 | 537.5483
1430.9417 | 470.4878 | 556.4033 | 537.2127
1431.9417 | 470.653 | 556.0192 | 536.8003
1432.9417 | 470.6951 | 555.5932 | 536.3869
1433.9417 | 470.5638 | 555.2044 | 535.7328
1434.9417 | 470.5144 | 554.8204 | 535.8323
1435.9417 | 470.6179 | 554.4294 | 535.5378
1436.9417 | 470.6478 | 554.0616 | 535.2985
1437.9417 | 470.6639 | 553.6664 | 535.2177
1438.9417 | 470.7021 | 553.2886 | 534.83
1439.9417 | 470.6758 | 552.9163 | 534.5134
1440.9417 | 470.4953 | 552.5562 | 534.0145
1441.9417 | 470.4348 | 552.1794 | 533.6478
1442.9417 | 470.5656 | 551.8071 | 533.2177
1443.9417 | 470.5933 | 551.4441 | 532.7632
1444.9417 | 470.5586 | 551.0198 | 532.402
1445.9417 | 470.4935 | 550.6716 | 532.0646
1446.9417 | 470.3705 | 550.2582 | 531.7779
1447.9417 | 470.4342 | 549.9164 | 531.5078
1448.9417 | 470.3977 | 549.5175 | 531.5116
1449.9417 | 470.3735 | 549.1462 | 531.0973
1450.9417 | 470.3308 | 548.7859 | 530.6757
1451.9417 | 470.2481 | 548.346 | 530.334
1452.9417 | 470.096 | 547.9747 | 530.0234
1453.9417 | 470.1591 | 547.5769 | 529.5888
1454.9417 | 470.0507 | 547.1701 | 529.1978
1455.9417 | 469.9071 | 546.7765 | 528.8799
1456.9417 | 469.8599 | 546.4244 | 528.5759
1457.9417 | 469.9056 | 546.0347 | 528.3952
1458.9417 | 469.8603 | 545.6233 | 528.0615
1459.9417 | 469.7206 | 545.31 | 527.7809
1460.9417 | 469.6488 | 544.956 | 527.4241
1461.9417 | 469.7648 | 544.6272 | 527.1291
1462.9417 | 469.7428 | 544.2509 | 526.7099
1463.9417 | 469.8802 | 543.8558 | 526.1951
1464.9417 | 470.0014 | 543.5041 | 525.8588
1465.9417 | 469.9912 | 543.1309 | 525.2918
1466.9417 | 469.924 | 542.7756 | 525.0548
1467.9417 | 469.8756 | 542.4305 | 524.582
1468.9417 | 469.8677 | 542.0985 | 524.3198
1469.9417 | 469.856 | 541.7751 | 524.0486
1470.9417 | 469.8663 | 541.4212 | 523.8506
1471.9417 | 469.9815 | 541.0896 | 523.5205
1472.9417 | 470.004 | 540.7901 | 523.1716
1473.9417 | 469.9908 | 540.4487 | 522.8996
1474.9417 | 469.9447 | 540.1802 | 522.6427
1475.9573 | 470.0506 | 539.8371 | 522.3707
1476.9417 | 470.1387 | 539.4777 | 522.177
1477.9417 | 470.1314 | 539.2233 | 522.0052
1478.9417 | 470.1105 | 538.8764 | 521.358
1479.9417 | 470.0777 | 538.5895 | 521.4346
1480.9417 | 470.043 | 538.2897 | 521.2413
1481.9417 | 470.0364 | 537.9561 | 520.9463
1482.9417 | 470.0747 | 537.6763 | 520.7606
1483.9417 | 470.0695 | 537.3743 | 520.4818
1484.9417 | 470.2428 | 537.1086 | 520.2556
1485.9417 | 470.3457 | 536.8523 | 519.9616
1486.9417 | 470.4251 | 536.5711 | 519.6823
1487.9417 | 470.383 | 536.2853 | 519.4155
1488.9417 | 470.4286 | 535.9765 | 519.1808
1489.9417 | 470.6113 | 535.6741 | 518.934
1490.9417 | 470.6362 | 535.4116 | 518.3223
1491.9417 | 470.603 | 535.0935 | 518.2396
1492.9417 | 470.7097 | 534.8143 | 517.8422
1493.9417 | 470.7199 | 534.5368 | 517.7203
1494.9417 | 470.6558 | 534.214 | 517.4812
1495.9417 | 470.6251 | 533.9613 | 517.24
1496.9417 | 470.756 | 533.6773 | 517.1359
1497.9417 | 470.7598 | 533.4016 | 516.8928
1498.9417 | 470.7441 | 533.1034 | 516.5276
1499.9417 | 470.7018 | 532.8228 | 516.3395
1500.9417 | 470.7994 | 532.5785 | 516.1025
1501.9417 | 470.9841 | 532.2903 | 515.735
1502.9417 | 471.0399 | 532.0629 | 515.6682
1503.9417 | 471.0371 | 531.8045 | 515.3746
1504.9417 | 470.9545 | 531.5333 | 515.102
1505.9417 | 470.9091 | 531.2537 | 514.8825
1506.9417 | 470.8379 | 530.95 | 514.6755
1507.9417 | 470.7258 | 530.7167 | 514.5763
1508.9417 | 470.724 | 530.3889 | 514.3615
1509.9417 | 470.776 | 530.1349 | 514.0329
1510.9417 | 470.7649 | 529.8541 | 513.8211
1511.9417 | 470.7365 | 529.5811 | 513.7793
1512.9417 | 470.632 | 529.2766 | 513.4235
1513.9417 | 470.5602 | 529.0175 | 512.995
1514.9417 | 470.5604 | 528.7675 | 513.074
1515.9417 | 470.6731 | 528.4753 | 512.8455
1516.9417 | 470.8757 | 528.2022 | 512.5492
1517.9417 | 470.9855 | 527.9041 | 512.4415
1518.9417 | 470.9827 | 527.6319 | 512.1819
1519.9417 | 470.9911 | 527.304 | 511.9991
1520.9417 | 471.1199 | 527.0496 | 511.8533
1521.9417 | 471.1851 | 526.7503 | 511.6908
1522.9417 | 471.1432 | 526.4589 | 511.3555
1523.9417 | 471.2334 | 526.1333 | 511.2205
1524.9417 | 471.277 | 525.8794 | 511.1079
1525.9417 | 471.3813 | 525.558 | 510.9032
1526.9417 | 471.4181 | 525.2644 | 510.6938
1527.9417 | 471.5847 | 525.0249 | 510.5594
1528.9417 | 471.7471 | 524.7401 | 510.1983
1529.9417 | 471.852 | 524.5067 | 510.0883
1530.9417 | 471.7137 | 524.2157 | 509.8611
1531.9417 | 471.5813 | 523.9405 | 509.649
1532.9417 | 471.5442 | 523.7132 | 509.5245
1533.9417 | 471.5295 | 523.468 | 509.2848
1534.9417 | 471.5812 | 523.2033 | 509.0235
1535.9417 | 471.5586 | 522.9483 | 508.1378
1536.9417 | 471.5591 | 522.66 | 508.3622
1537.9417 | 471.4866 | 522.3866 | 508.2386
1538.9417 | 471.2938 | 522.1121 | 507.9815
1539.9417 | 471.2924 | 521.8368 | 507.7058
1540.9417 | 471.3059 | 521.5766 | 507.6224
1541.9417 | 471.2711 | 521.3117 | 507.2734
1542.9417 | 471.1642 | 521.0453 | 507.183
1543.9417 | 471.1349 | 520.8209 | 507.0354
1544.9417 | 471.0578 | 520.5515 | 506.6853
1545.9417 | 470.9688 | 520.2755 | 506.5574
1546.9417 | 470.9883 | 519.994 | 506.3823
1547.9417 | 471.0268 | 519.7384 | 506.015
1548.9417 | 471.0565 | 519.4914 | 505.9204
1549.9417 | 471.0186 | 519.1698 | 505.877
1550.9417 | 470.9862 | 518.9352 | 505.9749
1551.9417 | 470.9279 | 518.6391 | 506.165
1552.9417 | 470.8736 | 518.3533 | 506.0588
1553.9417 | 470.851 | 518.073 | 506.2127
1554.9417 | 471.0063 | 517.8202 | 506.0709
1555.9417 | 471.0201 | 517.5423 | 505.9721
1556.9417 | 471.0269 | 517.2693 | 505.49
1557.9417 | 471.074 | 516.9761 | 505.1269
1558.9417 | 471.1422 | 516.6932 | 504.5797
1559.9417 | 471.1124 | 516.3743 | 504.7816
1560.9417 | 471.0146 | 516.086 | 504.8008
1561.9417 | 470.9627 | 515.7981 | 504.7198
1562.9417 | 470.8157 | 515.5023 | 504.603
1563.9417 | 470.6542 | 515.229 | 504.2084
1564.9417 | 470.5537 | 514.9685 | 503.9351
1565.9417 | 470.5745 | 514.6801 | 503.519
1566.9417 | 470.5056 | 514.3596 | 503.4642
1567.9417 | 470.4145 | 514.0529 | 503.3354
1568.9417 | 470.2541 | 513.7547 | 503.3458
1569.9417 | 470.1665 | 513.4421 | 502.8898
1570.9417 | 470.05 | 513.173 | 502.9342
1571.9417 | 470.0266 | 512.8558 | 502.8111
1572.9417 | 469.9695 | 512.556 | 502.7792
1573.9417 | 469.8594 | 512.2454 | 502.495
1574.9417 | 469.769 | 511.9426 | 502.2975
1575.9417 | 469.7866 | 511.6676 | 502.0112
1576.9417 | 469.8579 | 511.3873 | 501.8147
1577.9417 | 469.9048 | 511.1082 | 501.7779
1578.9417 | 469.832 | 510.7962 | 501.7518
1579.9417 | 469.8218 | 510.5151 | 501.8348
1580.9417 | 469.9406 | 510.2399 | 501.6318
1581.9417 | 469.9844 | 509.9307 | 501.4257
1582.9573 | 470.0272 | 509.6398 | 500.1069
1583.9417 | 470.0916 | 509.3618 | 500.861
1584.9417 | 470.0578 | 509.086 | 500.6945
1585.9417 | 469.9744 | 508.7918 | 500.2135
1586.9417 | 470.0823 | 508.5046 | 500.1234
1587.9417 | 470.2639 | 508.1488 | 500.3385
1588.9417 | 470.3532 | 507.8295 | 500.0305
1589.9417 | 470.3697 | 507.4499 | 502.786
1590.9417 | 470.4236 | 507.0854 | 503.4297
1591.9417 | 470.5098 | 506.7226 | 503.4203
1592.9417 | 470.4259 | 506.19 | 513.6399
1593.9417 | 470.344 | 505.9419 | 510.1231
1594.9417 | 470.3238 | 505.4627 | 517.0283
1595.9417 | 470.4387 | 505.2252 | 514.2073
1596.9417 | 470.5099 | 505.1538 | 503.2528
1597.9417 | 470.4095 | 504.8767 | 501.1037
1598.9417 | 470.4874 | 504.5293 | 502.6864
1599.9417 | 470.4939 | 504.244 | 502.8785
1600.9417 | 470.4432 | 503.8739 | 505.6336
1601.9417 | 470.3647 | 503.6287 | 502.6868
1602.9417 | 470.3495 | 503.3957 | 498.3193
1603.9417 | 470.2833 | 503.0788 | 496.9767
1604.9417 | 470.3639 | 502.7873 | 496.6655
1605.9417 | 470.2771 | 502.4417 | 497.5791
1606.9417 | 470.1953 | 502.1406 | 496.48
1607.9417 | 470.2005 | 501.7923 | 496.5409
1608.9417 | 470.2479 | 501.4398 | 496.1993
1609.9417 | 470.2821 | 501.1158 | 495.1856
1610.9417 | 470.3119 | 500.785 | 494.7428
1611.9417 | 470.2991 | 500.4338 | 495.0424
1612.9417 | 470.3393 | 500.0459 | 494.6081
1613.9417 | 470.1827 | 499.9036 | 494.2984
1614.9417 | 470.2184 | 499.4538 | 497.2194
1615.9417 | 470.3466 | 498.9924 | 502.6734
1616.9417 | 470.437 | 498.6768 | 501.0428
1617.9417 | 470.4443 | 498.2182 | 505.0869
1618.9417 | 470.4215 | 498.005 | 498.5484
1619.9417 | 470.3173 | 497.6952 | 495.5225
1620.9417 | 470.1756 | 497.2287 | 500.7361
1621.9417 | 470.0953 | 496.8731 | 499.2088
1622.9417 | 470.1466 | 496.5586 | 498.5336
1623.9417 | 470.2912 | 496.3821 | 488.8197
1624.9417 | 470.395 | 496.0201 | 489.2526
1625.9417 | 470.423 | 495.6712 | 489.1103
1626.9417 | 470.3889 | 495.3014 | 490.0459
1627.9417 | 470.4155 | 494.9558 | 489.996
1628.9417 | 470.5524 | 494.6325 | 489.3944
1629.9417 | 470.6273 | 494.3307 | 487.5041
1630.9417 | 470.6513 | 493.9485 | 487.7861
1631.9417 | 470.5863 | 493.6057 | 487.6431
1632.9417 | 470.5503 | 493.2767 | 486.4355
1633.9417 | 470.5736 | 492.9256 | 486.3018
1634.9417 | 470.5532 | 492.561 | 485.1416
1635.9417 | 470.618 | 492.1565 | 486.2681
1636.9417 | 470.5736 | 491.7753 | 486.4326
1637.9417 | 470.5978 | 491.4296 | 485.6194