## Test Conditions
DESIREE-FIRE Test Number 3 - Circuit Simulator Data Only
Test Date: | 2009-07-21
DCSim DAQ Start Time | 10:28
DCSim Time for Synchronization | 10:40
Heat Source Synchronization | 4:47 | minutes:seconds
Heat Source DAQ Start Time | 10:35
Heat Source Start Time | 10:40
DCSim Offset | 0:13 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 750 | seconds
Heat Source Offset | 0:06 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 343 | seconds
Heat Source Stop Time | 10:56
Test Duration | 0:15 | minutes:seconds
| 912 | seconds
CT500 Turns | 1 |  | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 Turns | 1
Pre-Test Baseline: | Partially Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SWGR Close | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SWGR Trip | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SWGR_CT500 | SWGR-a_CT35_1_PC | SWGR-a_CT35_2_N1 | SWGR-b_CT35_1_PT | SWGR-b_CT35_2_G | SWGR-b_CT35_3_R | SWGR-b_CT35_4_N2 | SWGR-a_VT7_1_C1 | SWGR-a_VTU_1_PC | SWGR-a_VTU_2_N1 | SWGR-b_VT7_1_G | SWGR-b_VT7_2_R | SWGR-b_VT7_3_T | SWGR-b_VT7_4_SP | SWGR-b_VT7_5_SP | SWGR-b_VTU_1_PT | SWGR-b_VTU_2_N2 | {SWGR-C} V(N1) - V(Batt -) | {SWGR-C} V(PC) - V(Batt +) | {SWGR-C} V(C1) - V(Batt +) | {SWGR-T} V(G) - V(Batt -) | {SWGR-T} V(R) - V(Batt +) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-T} V(PT) - V(Batt +) | {SWGR-C} V(C1) - V(N1) | {SWGR-T} V(SP1) - V(Batt -) | {SWGR-T} V(SP2) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PC) - V(Batt -) | {SWGR-T} V(C1) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(N2) - V(Batt -) | {SWGR-C} V(PC) - V(Batt -) | {SWGR-C} V(C1) - V(Batt -) | {SWGR-T} V(T) - V(Batt -) | {SWGR-T} V(R) - V(Batt -) | {SWGR-T} V(PT) - V(Batt -) | {SWGR-C} V(N1) - V(Batt +) | {SWGR-T} V(N2) - V(Batt +)
-0.34375 | 123.4772 | -61.084 | 62.1552 | 0.55012 | -0.046983 | -0.075141 | 0.095187 | -0.0073727 | -0.076888 | 0.047815 | -61.203 | 62.1414 | -61.1664 | -61.2534 | 62.0224 | 0.050354 | -0.004578 | 0.054932 | 62.059 | -61.2076 | -0.082398 | -0.013733 | -0.11902 | -0.16937 | -0.13275 | -0.1236 | -0.09613 | -0.036621 | 61.0794 | 61.1389 | 123.1064 | 123.2254 | -0.11902 | 123.143 | 61.1343 | -0.1236 | 123.2254 | -0.11902 | 61.1343 | 123.1064 | 123.143 | -123.3215 | -123.3627
0.65625 | 123.5413 | -61.0336 | 62.1643 | 0.3365 | -0.052323 | -0.076209 | 0.096255 | -0.01485 | -0.086501 | 0.046747 | -61.2122 | 62.0911 | -61.1572 | -61.3312 | 61.9766 | -0.018311 | 0.068665 | -0.022888 | 62.0773 | -61.2076 | -0.1236 | -0.073243 | -0.17853 | -0.29755 | -0.18768 | -0.17395 | -0.086975 | -0.054931 | 61.1023 | 61.0107 | 123.0103 | 123.1247 | -0.17853 | 123.111 | 61.0153 | -0.17395 | 123.1247 | -0.17853 | 61.0153 | 123.0103 | 123.111 | -123.3215 | -123.3719
1.6562 | 123.5184 | -61.0291 | 62.1277 | 0.5959 | -0.046983 | -0.058051 | 0.088778 | -0.0095097 | -0.076888 | 0.045679 | -61.1526 | 62.0773 | -61.1435 | -61.3403 | 61.9446 | -0.022888 | 0.086975 | -0.036621 | 62.0636 | -61.2122 | -0.11444 | -0.050354 | -0.1236 | -0.31128 | -0.18311 | -0.18311 | -0.064087 | -0.009155 | 61.116 | 60.9924 | 122.9736 | 123.1064 | -0.1236 | 123.0927 | 61.0062 | -0.18311 | 123.1064 | -0.1236 | 61.0062 | 122.9736 | 123.0927 | -123.2712 | -123.3398
2.6562 | 123.5001 | -61.084 | 62.1552 | 0.5196 | -0.043778 | -0.097572 | 0.091982 | -0.01485 | -0.069411 | 0.046747 | -61.1847 | 62.1094 | -61.1343 | -61.2946 | 61.9812 | 0.018311 | 0.045776 | 0.009155 | 62.0544 | -61.2305 | -0.050354 | -0.045776 | -0.10071 | -0.21057 | -0.17395 | -0.14648 | -0.10071 | -0.050354 | 61.1298 | 61.0931 | 123.0652 | 123.1934 | -0.10071 | 123.1384 | 61.1023 | -0.14648 | 123.1934 | -0.10071 | 61.1023 | 123.0652 | 123.1384 | -123.2895 | -123.3856
3.7188 | 123.4085 | -61.0703 | 62.178 | 0.092359 | -0.040574 | -0.066596 | 0.11014 | -0.0063047 | -0.071547 | 0.048883 | -61.1435 | 62.1826 | -61.1343 | -61.2167 | 62.027 | 0.10071 | -0.036621 | 0.082397 | 62.0636 | -61.1893 | -0.064087 | 0.004577 | -0.073243 | -0.14648 | -0.15106 | -0.11902 | -0.11444 | -0.009156 | 61.0336 | 61.1526 | 123.0972 | 123.2529 | -0.073243 | 123.1338 | 61.171 | -0.11902 | 123.2529 | -0.073243 | 61.171 | 123.0972 | 123.1338 | -123.3124 | -123.3673
4.6562 | 123.3948 | -61.0703 | 62.1735 | -0.1823 | -0.043778 | -0.068732 | 0.10694 | 0.00010333 | -0.080092 | 0.051019 | -61.1755 | 62.1735 | -61.1252 | -61.171 | 62.0865 | 0.1236 | -0.086975 | 0.13275 | 62.0453 | -61.1847 | -0.054932 | 0 | -0.10529 | -0.10071 | -0.086975 | -0.11444 | -0.12817 | -0.050354 | 60.9833 | 61.203 | 123.1567 | 123.2437 | -0.10529 | 123.1155 | 61.1938 | -0.11444 | 123.2437 | -0.10529 | 61.1938 | 123.1567 | 123.1155 | -123.2986 | -123.3582
5.6562 | 123.5001 | -61.0565 | 62.1552 | 0.5196 | -0.045914 | -0.085822 | 0.082369 | 0.0075803 | -0.071547 | 0.043542 | -61.1801 | 62.1323 | -61.1526 | -61.2854 | 61.9995 | 0.036621 | 0.045776 | -0.045776 | 62.0728 | -61.2213 | -0.09613 | -0.022888 | -0.1236 | -0.22888 | -0.15564 | -0.16479 | -0.082397 | -0.027466 | 61.1023 | 61.0107 | 123.056 | 123.1888 | -0.1236 | 123.1293 | 61.0931 | -0.16479 | 123.1888 | -0.1236 | 61.0931 | 123.056 | 123.1293 | -123.3078 | -123.3765
6.6562 | 123.4177 | -61.0977 | 62.1689 | 0.58064 | -0.043778 | -0.062324 | 0.097323 | -0.0073727 | -0.082229 | 0.049951 | -61.2305 | 62.1506 | -61.171 | -61.1893 | 62.0773 | 0.091553 | -0.059509 | 0.10529 | 62.0453 | -61.1801 | -0.073242 | -0.01831 | -0.13275 | -0.091553 | -0.091552 | -0.082398 | -0.1236 | -0.05951 | 61.0382 | 61.203 | 123.175 | 123.2483 | -0.13275 | 123.143 | 61.1893 | -0.082398 | 123.2483 | -0.13275 | 61.1893 | 123.175 | 123.143 | -123.3398 | -123.349
7.6562 | 123.4726 | -61.0794 | 62.1689 | 0.61116 | -0.053391 | -0.055915 | 0.099459 | -0.01485 | -0.068343 | 0.053156 | -61.2259 | 62.1185 | -61.1664 | -61.2305 | 62.0178 | 0.073242 | -0.036621 | 0.082397 | 62.0407 | -61.171 | -0.086975 | -0.050354 | -0.14648 | -0.15106 | -0.15106 | -0.091552 | -0.12817 | -0.059509 | 61.0428 | 61.1618 | 123.0972 | 123.1979 | -0.14648 | 123.1201 | 61.1526 | -0.091552 | 123.1979 | -0.14648 | 61.1526 | 123.0972 | 123.1201 | -123.3353 | -123.3398
8.6562 | 123.4131 | -61.0886 | 62.1552 | 0.56538 | -0.048051 | -0.071937 | 0.086642 | -0.010578 | -0.076888 | 0.053156 | -61.2167 | 62.1597 | -61.171 | -61.1984 | 62.0316 | 0.09613 | -0.054932 | 0.086975 | 62.0316 | -61.203 | -0.082397 | 0.004578 | -0.12817 | -0.10986 | -0.1236 | -0.11444 | -0.1236 | -0.045777 | 61.0336 | 61.1755 | 123.1201 | 123.2483 | -0.12817 | 123.1201 | 61.1847 | -0.11444 | 123.2483 | -0.12817 | 61.1847 | 123.1201 | 123.1201 | -123.3261 | -123.3582
9.6562 | 123.4268 | -61.1023 | 62.1414 | 0.45857 | -0.048051 | -0.068732 | 0.097323 | 0.0022403 | -0.066207 | 0.048883 | -61.235 | 62.1735 | -61.1572 | -61.1984 | 62.0544 | 0.09613 | -0.059509 | 0.11444 | 62.0361 | -61.1664 | -0.054932 | 0.032044 | -0.13275 | -0.09613 | -0.086975 | -0.064087 | -0.10529 | -0.077819 | 61.0428 | 61.2167 | 123.1567 | 123.2758 | -0.13275 | 123.1384 | 61.1984 | -0.064087 | 123.2758 | -0.13275 | 61.1984 | 123.1567 | 123.1384 | -123.2986 | -123.3078
10.7188 | 123.4543 | -61.0794 | 62.1918 | 0.0771 | -0.052323 | -0.076209 | 0.094119 | -0.0041687 | -0.059798 | 0.043542 | -61.1343 | 62.1643 | -61.1343 | -61.2305 | 62.0224 | 0.10071 | -0.032043 | 0.07782 | 62.059 | -61.171 | -0.054931 | -0.027465 | -0.054931 | -0.15106 | -0.16937 | -0.091552 | -0.13275 | 0 | 61.0474 | 61.1572 | 123.1018 | 123.2437 | -0.054931 | 123.1384 | 61.1801 | -0.091552 | 123.2437 | -0.054931 | 61.1801 | 123.1018 | 123.1384 | -123.3261 | -123.3627
11.6562 | 123.3902 | -61.0748 | 62.178 | 0.29072 | -0.049119 | -0.087958 | 0.108 | -0.00096467 | -0.079024 | 0.043542 | -61.2076 | 62.1826 | -61.1389 | -61.1618 | 62.0728 | 0.14191 | -0.086975 | 0.1236 | 62.059 | -61.1618 | -0.064087 | 0.004577 | -0.13275 | -0.086975 | -0.10529 | -0.086975 | -0.11902 | -0.068665 | 60.9879 | 61.1984 | 123.1476 | 123.2574 | -0.13275 | 123.1338 | 61.2167 | -0.086975 | 123.2574 | -0.13275 | 61.2167 | 123.1476 | 123.1338 | -123.317 | -123.3398
12.6562 | 123.3856 | -61.0886 | 62.1918 | 0.50435 | -0.036301 | -0.093299 | 0.094119 | 0.0075803 | -0.071547 | 0.042474 | -61.2442 | 62.1918 | -61.1664 | -61.1481 | 62.0819 | 0.14191 | -0.091553 | 0.13733 | 62.0316 | -61.171 | -0.07782 | 0 | -0.15564 | -0.059509 | -0.10986 | -0.082397 | -0.16022 | -0.07782 | 60.997 | 61.2259 | 123.1705 | 123.2803 | -0.15564 | 123.1201 | 61.2305 | -0.082397 | 123.2803 | -0.15564 | 61.2305 | 123.1705 | 123.1201 | -123.3582 | -123.3627
13.6562 | 123.381 | -61.0657 | 62.1826 | 0.15339 | -0.052323 | -0.08155 | 0.10907 | 0.0054443 | -0.061934 | 0.049951 | -61.2396 | 62.1872 | -61.1526 | -61.1664 | 62.1094 | 0.14648 | -0.10986 | 0.12817 | 62.0499 | -61.1893 | -0.086975 | 0.004578 | -0.17395 | -0.10071 | -0.073242 | -0.1236 | -0.13275 | -0.086975 | 60.9558 | 61.1938 | 123.175 | 123.2529 | -0.17395 | 123.1155 | 61.2122 | -0.1236 | 123.2529 | -0.17395 | 61.2122 | 123.175 | 123.1155 | -123.3353 | -123.3719
14.6562 | 123.4085 | -61.0977 | 62.1552 | 0.47383 | -0.043778 | -0.074073 | 0.090914 | -0.023395 | -0.083297 | 0.042474 | -61.2442 | 62.1735 | -61.1618 | -61.1755 | 62.0911 | 0.12817 | -0.086975 | 0.12817 | 62.0361 | -61.1984 | -0.064087 | 0.018311 | -0.14648 | -0.07782 | -0.064087 | -0.10071 | -0.11902 | -0.082398 | 61.0107 | 61.2259 | 123.1888 | 123.2712 | -0.14648 | 123.1338 | 61.2259 | -0.10071 | 123.2712 | -0.14648 | 61.2259 | 123.1888 | 123.1338 | -123.317 | -123.3536
15.6562 | 123.4039 | -61.1206 | 62.1735 | 0.41279 | -0.046983 | -0.083686 | 0.09305 | 0.0033083 | -0.063003 | 0.047815 | -61.235 | 62.1964 | -61.1481 | -61.1893 | 62.0865 | 0.1236 | -0.09613 | 0.13733 | 62.0544 | -61.1847 | -0.027466 | 0.022888 | -0.11444 | -0.068665 | -0.086975 | -0.064087 | -0.11902 | -0.086975 | 61.0245 | 61.2579 | 123.2071 | 123.317 | -0.11444 | 123.175 | 61.2442 | -0.064087 | 123.317 | -0.11444 | 61.2442 | 123.2071 | 123.175 | -123.3215 | -123.3582
16.6562 | 123.3719 | -61.1023 | 62.1506 | 0.26021 | -0.037369 | -0.065528 | 0.097323 | -0.0031007 | -0.07582 | 0.052087 | -61.2442 | 62.1918 | -61.1572 | -61.1618 | 62.0911 | 0.14191 | -0.10986 | 0.16479 | 62.0544 | -61.1618 | -0.054932 | 0.041198 | -0.14191 | -0.059509 | -0.05951 | -0.059509 | -0.096131 | -0.086975 | 60.9924 | 61.2671 | 123.1934 | 123.2941 | -0.14191 | 123.1567 | 61.2442 | -0.059509 | 123.2941 | -0.14191 | 61.2442 | 123.1934 | 123.1567 | -123.3078 | -123.3124
17.7188 | 123.3948 | -61.0794 | 62.2192 | -0.28911 | -0.054459 | -0.077277 | 0.091982 | 0.0043763 | -0.086501 | 0.047815 | -61.2167 | 62.1689 | -61.1664 | -61.1984 | 62.0728 | 0.15564 | -0.07782 | 0.15564 | 62.0956 | -61.1252 | -0.086975 | -0.050354 | -0.13733 | -0.11902 | -0.14648 | -0.045776 | -0.1236 | -0.050354 | 61.0016 | 61.235 | 123.1522 | 123.2483 | -0.13733 | 123.175 | 61.235 | -0.045776 | 123.2483 | -0.13733 | 61.235 | 123.1522 | 123.175 | -123.3856 | -123.3444
18.6562 | 123.4451 | -61.084 | 62.1964 | 0.092359 | -0.034165 | -0.059119 | 0.11334 | 0.0065123 | -0.070479 | 0.049951 | -61.1481 | 62.1735 | -61.1206 | -61.2122 | 62.0361 | 0.10529 | -0.041199 | 0.09613 | 62.0773 | -61.1938 | -0.036621 | -0.022888 | -0.064087 | -0.12817 | -0.16022 | -0.10986 | -0.11902 | -0.027466 | 61.0428 | 61.1801 | 123.1201 | 123.2574 | -0.064087 | 123.1613 | 61.1893 | -0.10986 | 123.2574 | -0.064087 | 61.1893 | 123.1201 | 123.1613 | -123.317 | -123.3902
19.7188 | 123.3765 | -61.0748 | 62.2055 | -0.67058 | -0.052323 | -0.090095 | 0.08771 | -0.0095097 | -0.079024 | 0.045679 | -61.2076 | 62.1735 | -61.1526 | -61.1984 | 62.0453 | 0.15106 | -0.068665 | 0.15106 | 62.0865 | -61.1526 | -0.07782 | -0.032043 | -0.13275 | -0.1236 | -0.16022 | -0.07782 | -0.11902 | -0.054932 | 61.0062 | 61.2259 | 123.1201 | 123.2483 | -0.13275 | 123.1613 | 61.2259 | -0.07782 | 123.2483 | -0.13275 | 61.2259 | 123.1201 | 123.1613 | -123.3582 | -123.3582
20.6562 | 123.4222 | -61.0748 | 62.1918 | 0.26021 | -0.053391 | -0.075141 | 0.10907 | 0.0054443 | -0.064071 | 0.036066 | -61.171 | 62.178 | -61.1206 | -61.2213 | 62.0407 | 0.12817 | -0.064087 | 0.10071 | 62.0544 | -61.1893 | -0.045776 | -0.013732 | -0.09613 | -0.14648 | -0.15106 | -0.11444 | -0.13733 | -0.050354 | 61.0107 | 61.1755 | 123.1155 | 123.2529 | -0.09613 | 123.1293 | 61.203 | -0.11444 | 123.2529 | -0.09613 | 61.203 | 123.1155 | 123.1293 | -123.3124 | -123.381
21.6562 | 123.3673 | -61.1023 | 62.2009 | 0.27546 | -0.050187 | -0.050574 | 0.089846 | -0.0020327 | -0.071547 | 0.057428 | -61.1893 | 62.1735 | -61.1526 | -61.1847 | 62.0499 | 0.13733 | -0.10529 | 0.1236 | 62.0865 | -61.1893 | -0.050354 | -0.027466 | -0.086975 | -0.082397 | -0.15106 | -0.086975 | -0.11444 | -0.036621 | 60.997 | 61.2259 | 123.1522 | 123.2758 | -0.086975 | 123.1888 | 61.2396 | -0.086975 | 123.2758 | -0.086975 | 61.2396 | 123.1522 | 123.1888 | -123.3536 | -123.3902
22.6562 | 123.3948 | -61.0703 | 62.2101 | 0.30598 | -0.039506 | -0.065528 | 0.10907 | 0.0011723 | -0.07582 | 0.047815 | -61.1938 | 62.2009 | -61.1389 | -61.2076 | 62.0453 | 0.10986 | -0.059509 | 0.11902 | 62.0728 | -61.1755 | -0.068665 | -0.009155 | -0.1236 | -0.13733 | -0.16479 | -0.10529 | -0.13733 | -0.054932 | 61.0107 | 61.1893 | 123.1155 | 123.2712 | -0.1236 | 123.143 | 61.1801 | -0.10529 | 123.2712 | -0.1236 | 61.1801 | 123.1155 | 123.143 | -123.349 | -123.3856
23.6562 | 123.4268 | -61.0931 | 62.1918 | 0.19917 | -0.038438 | -0.06446 | 0.090914 | 0.0022403 | -0.072616 | 0.049951 | -61.1801 | 62.1826 | -61.1526 | -61.2167 | 62.0499 | 0.1236 | -0.059509 | 0.11444 | 62.0911 | -61.1801 | -0.059509 | -0.009155 | -0.086975 | -0.1236 | -0.14191 | -0.086975 | -0.10071 | -0.027466 | 61.0336 | 61.2076 | 123.143 | 123.2758 | -0.086975 | 123.1842 | 61.2167 | -0.086975 | 123.2758 | -0.086975 | 61.2167 | 123.143 | 123.1842 | -123.3444 | -123.3719
24.7188 | 123.4131 | -61.0703 | 62.1872 | -0.21282 | -0.055527 | -0.08689 | 0.083437 | -0.00096467 | -0.08116 | 0.055292 | -61.2259 | 62.1689 | -61.1526 | -61.1984 | 62.0773 | 0.15106 | -0.068665 | 0.13733 | 62.0911 | -61.203 | -0.082398 | -0.018311 | -0.15564 | -0.12817 | -0.10986 | -0.13275 | -0.096131 | -0.073242 | 61.0016 | 61.2076 | 123.1476 | 123.2391 | -0.15564 | 123.1613 | 61.2213 | -0.13275 | 123.2391 | -0.15564 | 61.2213 | 123.1476 | 123.1613 | -123.3398 | -123.3902
25.6562 | 123.4314 | -61.0794 | 62.1872 | -0.029711 | -0.046983 | -0.070869 | 0.098391 | -0.0084417 | -0.071547 | 0.036066 | -61.1664 | 62.1643 | -61.1206 | -61.2259 | 62.0132 | 0.091553 | -0.027466 | 0.064087 | 62.0865 | -61.1984 | -0.041198 | -0.022888 | -0.086975 | -0.14648 | -0.17395 | -0.11902 | -0.10071 | -0.045777 | 61.0519 | 61.1435 | 123.0927 | 123.2437 | -0.086975 | 123.1659 | 61.171 | -0.11902 | 123.2437 | -0.086975 | 61.171 | 123.0927 | 123.1659 | -123.3078 | -123.3856
26.6562 | 123.468 | -61.0703 | 62.1918 | 0.061841 | -0.052323 | -0.068732 | 0.085574 | -0.0052367 | -0.068343 | 0.041406 | -61.1343 | 62.1872 | -61.1252 | -61.2213 | 62.0087 | 0.10071 | -0.022888 | 0.086975 | 62.1048 | -61.1984 | -0.054932 | -0.004577 | -0.064087 | -0.15106 | -0.1831 | -0.12817 | -0.086975 | -0.009155 | 61.0474 | 61.1572 | 123.0789 | 123.2574 | -0.064087 | 123.175 | 61.171 | -0.12817 | 123.2574 | -0.064087 | 61.171 | 123.0789 | 123.175 | -123.317 | -123.3902
27.6562 | 123.4497 | -61.084 | 62.2009 | -0.014452 | -0.054459 | -0.075141 | 0.090914 | 0.0097163 | -0.065139 | 0.037134 | -61.1252 | 62.1735 | -61.1252 | -61.2305 | 62.027 | 0.09613 | -0.018311 | 0.064087 | 62.1094 | -61.171 | -0.041199 | -0.027466 | -0.041199 | -0.14648 | -0.17395 | -0.086975 | -0.091553 | 0 | 61.0657 | 61.1481 | 123.111 | 123.2574 | -0.041199 | 123.1934 | 61.1801 | -0.086975 | 123.2574 | -0.041199 | 61.1801 | 123.111 | 123.1934 | -123.3261 | -123.3719
28.6562 | 123.381 | -61.0931 | 62.1872 | 0.15339 | -0.049119 | -0.074073 | 0.099459 | 0.0075803 | -0.065139 | 0.053156 | -61.2167 | 62.1872 | -61.171 | -61.1893 | 62.0453 | 0.10986 | -0.07782 | 0.10071 | 62.0911 | -61.203 | -0.077819 | 0 | -0.1236 | -0.09613 | -0.14191 | -0.10986 | -0.096131 | -0.045777 | 61.0153 | 61.1938 | 123.1384 | 123.2803 | -0.1236 | 123.1842 | 61.203 | -0.10986 | 123.2803 | -0.1236 | 61.203 | 123.1384 | 123.1842 | -123.3582 | -123.3902
29.6562 | 123.4634 | -61.0794 | 62.1918 | 0.046583 | -0.048051 | -0.078345 | 0.096255 | -0.0031007 | -0.055526 | 0.054224 | -61.1526 | 62.1826 | -61.1389 | -61.2305 | 62.0224 | 0.086975 | -0.013733 | 0.068665 | 62.1048 | -61.1893 | -0.059509 | -0.009155 | -0.073242 | -0.15106 | -0.16937 | -0.10986 | -0.086975 | -0.013733 | 61.0657 | 61.1481 | 123.1018 | 123.262 | -0.073242 | 123.1842 | 61.1664 | -0.10986 | 123.262 | -0.073242 | 61.1664 | 123.1018 | 123.1842 | -123.3307 | -123.381
30.6562 | 123.4726 | -61.0565 | 62.2284 | 0.031324 | -0.039506 | -0.060187 | 0.090914 | -0.0052367 | -0.071547 | 0.053156 | -61.1526 | 62.1872 | -61.1389 | -61.235 | 62.0178 | 0.086975 | -0.027466 | 0.086975 | 62.1002 | -61.1801 | -0.082397 | -0.041199 | -0.09613 | -0.17853 | -0.21057 | -0.1236 | -0.12817 | -0.013733 | 61.0291 | 61.1435 | 123.0743 | 123.2437 | -0.09613 | 123.1567 | 61.1435 | -0.1236 | 123.2437 | -0.09613 | 61.1435 | 123.0743 | 123.1567 | -123.3673 | -123.4085
31.6562 | 123.4634 | -61.0611 | 62.1872 | -0.12126 | -0.050187 | -0.074073 | 0.08771 | 0.0065123 | -0.067275 | 0.051019 | -61.171 | 62.1964 | -61.1526 | -61.2213 | 62.0453 | 0.11444 | -0.027466 | 0.086975 | 62.114 | -61.1893 | -0.091553 | 0.009155 | -0.10986 | -0.16022 | -0.14191 | -0.12817 | -0.073242 | -0.01831 | 61.0336 | 61.1481 | 123.1064 | 123.2574 | -0.10986 | 123.175 | 61.1755 | -0.12817 | 123.2574 | -0.10986 | 61.1755 | 123.1064 | 123.175 | -123.3398 | -123.3765
32.6562 | 123.3948 | -61.0794 | 62.2009 | -0.25859 | -0.06514 | -0.078345 | 0.084505 | 0.0011723 | -0.074752 | 0.041406 | -61.2167 | 62.1872 | -61.1481 | -61.1664 | 62.0682 | 0.15564 | -0.07782 | 0.14648 | 62.114 | -61.1618 | -0.068664 | -0.013733 | -0.13733 | -0.086975 | -0.13275 | -0.082397 | -0.086975 | -0.068665 | 61.0016 | 61.2259 | 123.1476 | 123.2666 | -0.13733 | 123.1934 | 61.235 | -0.082397 | 123.2666 | -0.13733 | 61.235 | 123.1476 | 123.1934 | -123.349 | -123.3627
33.6562 | 123.4406 | -61.0703 | 62.233 | -0.1823 | -0.049119 | -0.097572 | 0.10694 | 0.016125 | -0.079024 | 0.052087 | -61.203 | 62.1964 | -61.1298 | -61.2259 | 62.0636 | 0.16022 | -0.07782 | 0.15106 | 62.0956 | -61.1938 | -0.05951 | -0.036621 | -0.13275 | -0.15564 | -0.16937 | -0.1236 | -0.13733 | -0.073242 | 60.9924 | 61.2213 | 123.1338 | 123.2666 | -0.13275 | 123.1659 | 61.2305 | -0.1236 | 123.2666 | -0.13275 | 61.2305 | 123.1338 | 123.1659 | -123.3627 | -123.4268
34.7188 | 123.4909 | -61.0703 | 62.178 | 0.32124 | -0.057664 | -0.063392 | 0.067416 | -0.016986 | -0.090773 | 0.037134 | -61.203 | 62.0499 | -61.1389 | -61.3129 | 61.972 | 0.045776 | 0.009155 | 0.054932 | 62.114 | -61.203 | -0.068665 | -0.12817 | -0.13275 | -0.24262 | -0.20599 | -0.13275 | -0.064087 | -0.064087 | 61.0794 | 61.1252 | 123.0423 | 123.1201 | -0.13275 | 123.1842 | 61.116 | -0.13275 | 123.1201 | -0.13275 | 61.116 | 123.0423 | 123.1842 | -123.317 | -123.381
35.6562 | 123.436 | -61.0931 | 62.2055 | -0.24333 | -0.053391 | -0.087958 | 0.10373 | -0.0084417 | -0.069411 | 0.049951 | -61.1618 | 62.1872 | -61.1343 | -61.2076 | 62.0407 | 0.13275 | -0.068665 | 0.1236 | 62.1048 | -61.203 | -0.041198 | -0.01831 | -0.068664 | -0.11444 | -0.1648 | -0.10986 | -0.10071 | -0.027466 | 61.0245 | 61.2167 | 123.1338 | 123.2803 | -0.068664 | 123.1979 | 61.2259 | -0.10986 | 123.2803 | -0.068664 | 61.2259 | 123.1338 | 123.1979 | -123.3398 | -123.4085
36.6562 | 123.4314 | -61.0748 | 62.2238 | -0.1823 | -0.041642 | -0.080482 | 0.10159 | -0.010578 | -0.066207 | 0.054224 | -61.203 | 62.1735 | -61.1389 | -61.1801 | 62.0544 | 0.14648 | -0.032043 | 0.10529 | 62.0956 | -61.1938 | -0.064087 | -0.050354 | -0.12817 | -0.10529 | -0.16937 | -0.11902 | -0.12817 | -0.064087 | 61.0428 | 61.1801 | 123.1293 | 123.2483 | -0.12817 | 123.1705 | 61.2213 | -0.11902 | 123.2483 | -0.12817 | 61.2213 | 123.1293 | 123.1705 | -123.3627 | -123.4177
37.6562 | 123.4131 | -61.0657 | 62.2055 | -0.21282 | -0.041642 | -0.071937 | 0.097323 | -0.0052367 | -0.065139 | 0.046747 | -61.2259 | 62.1735 | -61.1343 | -61.1801 | 62.0728 | 0.16022 | -0.07782 | 0.15106 | 62.1277 | -61.1755 | -0.068664 | -0.032043 | -0.16022 | -0.11444 | -0.13275 | -0.10986 | -0.077819 | -0.091553 | 60.9879 | 61.2167 | 123.1384 | 123.2391 | -0.16022 | 123.1934 | 61.2259 | -0.10986 | 123.2391 | -0.16022 | 61.2259 | 123.1384 | 123.1934 | -123.3398 | -123.381
38.6562 | 123.4268 | -61.0703 | 62.2284 | -0.25859 | -0.0598 | -0.079414 | 0.08771 | -0.0052367 | -0.090773 | 0.05636 | -61.1664 | 62.1277 | -61.1252 | -61.235 | 62.0316 | 0.10529 | -0.068665 | 0.11444 | 62.1185 | -61.1801 | -0.054932 | -0.10071 | -0.096131 | -0.16479 | -0.19684 | -0.10986 | -0.10986 | -0.041199 | 61.0016 | 61.1847 | 123.1018 | 123.1979 | -0.096131 | 123.1888 | 61.1755 | -0.10986 | 123.1979 | -0.096131 | 61.1755 | 123.1018 | 123.1888 | -123.3536 | -123.4085
39.6562 | 123.3948 | -61.0703 | 62.2467 | -0.36541 | -0.057664 | -0.093299 | 0.094119 | -0.0052367 | -0.072616 | 0.054224 | -61.203 | 62.1597 | -61.1618 | -61.1893 | 62.0773 | 0.15106 | -0.068665 | 0.13275 | 62.1368 | -61.1664 | -0.091553 | -0.086975 | -0.13275 | -0.11902 | -0.16937 | -0.096131 | -0.10986 | -0.041199 | 61.0016 | 61.203 | 123.1476 | 123.23 | -0.13275 | 123.2071 | 61.2213 | -0.096131 | 123.23 | -0.13275 | 61.2213 | 123.1476 | 123.2071 | -123.4085 | -123.4131
40.6562 | 123.4039 | -61.0611 | 62.2147 | -0.22808 | -0.054459 | -0.10078 | 0.085574 | -0.0052367 | -0.074752 | 0.048883 | -61.1984 | 62.1323 | -61.1618 | -61.2259 | 62.0224 | 0.13275 | -0.082397 | 0.12817 | 62.1277 | -61.171 | -0.10071 | -0.082398 | -0.13733 | -0.16479 | -0.19226 | -0.10986 | -0.086975 | -0.036621 | 60.9787 | 61.1893 | 123.0835 | 123.1934 | -0.13733 | 123.1888 | 61.1938 | -0.10986 | 123.1934 | -0.13733 | 61.1938 | 123.0835 | 123.1888 | -123.3765 | -123.3856
41.6562 | 123.436 | -61.0748 | 62.2055 | -0.19756 | -0.0598 | -0.097572 | 0.094119 | -0.0073727 | -0.086501 | 0.041406 | -61.1618 | 62.1094 | -61.1069 | -61.2305 | 62.0132 | 0.086975 | -0.032043 | 0.091553 | 62.1094 | -61.1664 | -0.032044 | -0.09613 | -0.086975 | -0.15564 | -0.19226 | -0.091553 | -0.09613 | -0.054931 | 61.0428 | 61.1664 | 123.0881 | 123.1842 | -0.086975 | 123.1842 | 61.1618 | -0.091553 | 123.1842 | -0.086975 | 61.1618 | 123.0881 | 123.1842 | -123.3124 | -123.3719
42.7188 | 123.4909 | -61.0565 | 62.1872 | 0.24495 | -0.068345 | -0.084754 | 0.075961 | -0.023395 | -0.090773 | 0.047815 | -61.2122 | 62.0636 | -61.1481 | -61.3083 | 61.972 | 0.036621 | 0.036621 | 0.027466 | 62.114 | -61.1847 | -0.091552 | -0.1236 | -0.15564 | -0.25177 | -0.21515 | -0.12817 | -0.073242 | -0.064087 | 61.0931 | 61.084 | 123.0286 | 123.1201 | -0.15564 | 123.1705 | 61.0931 | -0.12817 | 123.1201 | -0.15564 | 61.0931 | 123.0286 | 123.1705 | -123.3353 | -123.3719
43.6562 | 123.4039 | -61.0748 | 62.2101 | -0.35015 | -0.048051 | -0.090095 | 0.095187 | -0.015918 | -0.08116 | 0.046747 | -61.1801 | 62.1323 | -61.1526 | -61.2396 | 62.0178 | 0.15106 | -0.036621 | 0.10071 | 62.1231 | -61.1984 | -0.07782 | -0.07782 | -0.10529 | -0.16479 | -0.19226 | -0.1236 | -0.086975 | -0.027466 | 61.0382 | 61.1755 | 123.0927 | 123.2071 | -0.10529 | 123.1979 | 61.2259 | -0.1236 | 123.2071 | -0.10529 | 61.2259 | 123.0927 | 123.1979 | -123.3627 | -123.4085
44.6562 | 123.4314 | -61.0519 | 62.2238 | -0.30437 | -0.070481 | -0.094367 | 0.099459 | -0.010578 | -0.086501 | 0.054224 | -61.1435 | 62.114 | -61.1206 | -61.2442 | 61.9904 | 0.086975 | -0.032043 | 0.091553 | 62.1277 | -61.171 | -0.068664 | -0.10986 | -0.091553 | -0.19226 | -0.23346 | -0.11902 | -0.09613 | -0.022889 | 61.0199 | 61.1435 | 123.0423 | 123.1659 | -0.091553 | 123.1796 | 61.1389 | -0.11902 | 123.1659 | -0.091553 | 61.1389 | 123.0423 | 123.1796 | -123.3444 | -123.3948
45.6562 | 123.5138 | -61.0153 | 62.2009 | -0.1823 | -0.058732 | -0.092231 | 0.08771 | -0.013782 | -0.086501 | 0.043542 | -61.1343 | 62.0819 | -61.1206 | -61.3312 | 61.908 | 0.004578 | 0.068665 | -0.009155 | 62.1368 | -61.203 | -0.10528 | -0.11902 | -0.11902 | -0.31586 | -0.29297 | -0.18768 | -0.064087 | -0.013733 | 61.084 | 61.0062 | 122.9233 | 123.0972 | -0.11902 | 123.1522 | 61.0199 | -0.18768 | 123.0972 | -0.11902 | 61.0199 | 122.9233 | 123.1522 | -123.3215 | -123.4039
46.7188 | 123.5001 | -61.0657 | 62.1735 | 0.47383 | -0.0598 | -0.08155 | 0.08771 | -0.013782 | -0.095046 | 0.038202 | -61.1984 | 62.0499 | -61.1755 | -61.3037 | 61.9629 | 0.018311 | 0.036621 | 0.018311 | 62.0911 | -61.1984 | -0.10986 | -0.1236 | -0.13275 | -0.23804 | -0.21057 | -0.13275 | -0.082398 | -0.022888 | 61.1023 | 61.084 | 123.0286 | 123.1155 | -0.13275 | 123.1567 | 61.084 | -0.13275 | 123.1155 | -0.13275 | 61.084 | 123.0286 | 123.1567 | -123.349 | -123.3719
47.6562 | 123.5229 | -61.0519 | 62.1735 | -0.090746 | -0.069413 | -0.10078 | 0.091982 | -0.020191 | -0.090773 | 0.064905 | -61.1343 | 62.0544 | -61.116 | -61.3174 | 61.9308 | 0.027466 | 0.068665 | 0.013733 | 62.1185 | -61.203 | -0.064087 | -0.11902 | -0.082397 | -0.2655 | -0.24262 | -0.15106 | -0.054932 | -0.01831 | 61.1206 | 61.0657 | 122.9828 | 123.1064 | -0.082397 | 123.1705 | 61.0794 | -0.15106 | 123.1064 | -0.082397 | 61.0794 | 122.9828 | 123.1705 | -123.2895 | -123.3765
48.6562 | 123.5275 | -61.0245 | 62.1689 | -0.04497 | -0.067277 | -0.094367 | 0.084505 | -0.020191 | -0.095046 | 0.051019 | -61.1252 | 62.0773 | -61.0977 | -61.322 | 61.9263 | -0.004578 | 0.073242 | -0.018311 | 62.1323 | -61.203 | -0.073242 | -0.091552 | -0.10071 | -0.29755 | -0.24261 | -0.17853 | -0.036621 | -0.027466 | 61.0977 | 61.0062 | 122.9507 | 123.1018 | -0.10071 | 123.1567 | 61.0199 | -0.17853 | 123.1018 | -0.10071 | 61.0199 | 122.9507 | 123.1567 | -123.2666 | -123.3719
49.6562 | 123.4589 | -61.0474 | 62.1964 | -0.1823 | -0.053391 | -0.096503 | 0.08771 | -0.016986 | -0.088637 | 0.042474 | -61.1252 | 62.1048 | -61.1206 | -61.2991 | 61.9537 | 0.027466 | 0.036621 | 0.022888 | 62.1231 | -61.2076 | -0.073242 | -0.091553 | -0.07782 | -0.25177 | -0.24262 | -0.16022 | -0.073242 | -0.004578 | 61.084 | 61.0703 | 123.0011 | 123.1522 | -0.07782 | 123.1705 | 61.0748 | -0.16022 | 123.1522 | -0.07782 | 61.0748 | 123.0011 | 123.1705 | -123.317 | -123.4039
50.6562 | 123.5275 | -61.0199 | 62.1872 | -0.22808 | -0.0598 | -0.083686 | 0.096255 | -0.020191 | -0.084365 | 0.043542 | -61.116 | 62.0728 | -61.0931 | -61.3174 | 61.9446 | 0.036621 | 0.064087 | 0.009155 | 62.1368 | -61.203 | -0.073243 | -0.11444 | -0.096131 | -0.29755 | -0.24262 | -0.18311 | -0.050354 | -0.022888 | 61.084 | 61.0291 | 122.9645 | 123.0927 | -0.096131 | 123.1567 | 61.0565 | -0.18311 | 123.0927 | -0.096131 | 61.0565 | 122.9645 | 123.1567 | -123.2803 | -123.3902
51.7188 | 123.5184 | -61.0519 | 62.1506 | 0.5959 | -0.061936 | -0.068732 | 0.10266 | -0.024463 | -0.07582 | 0.037134 | -61.1389 | 62.0682 | -61.1298 | -61.3403 | 61.9263 | -0.036621 | 0.068665 | -0.032043 | 62.0865 | -61.235 | -0.07782 | -0.082398 | -0.086975 | -0.28839 | -0.2243 | -0.1831 | -0.064087 | -0.009155 | 61.1206 | 61.0199 | 122.9782 | 123.1201 | -0.086975 | 123.1384 | 61.0153 | -0.1831 | 123.1201 | -0.086975 | 61.0153 | 122.9782 | 123.1384 | -123.2803 | -123.3856
52.6562 | 123.4863 | -61.0565 | 62.2009 | -0.25859 | -0.070481 | -0.096503 | 0.082369 | -0.01485 | -0.080092 | 0.043542 | -61.1114 | 62.0911 | -61.1298 | -61.29 | 61.9446 | 0.013733 | 0.054932 | 0.004578 | 62.1414 | -61.1801 | -0.073242 | -0.10986 | -0.054931 | -0.23346 | -0.25635 | -0.1236 | -0.05951 | 0.018311 | 61.1115 | 61.0611 | 123.0011 | 123.1476 | -0.054931 | 123.1979 | 61.0703 | -0.1236 | 123.1476 | -0.054931 | 61.0703 | 123.0011 | 123.1979 | -123.3307 | -123.381
53.6562 | 123.5275 | -61.0565 | 62.178 | 0.15339 | -0.075822 | -0.08155 | 0.081301 | -0.026599 | -0.089705 | 0.047815 | -61.116 | 62.0636 | -61.1343 | -61.3358 | 61.94 | -0.018311 | 0.10071 | -0.032043 | 62.114 | -61.1984 | -0.077819 | -0.11444 | -0.059509 | -0.27923 | -0.23804 | -0.14191 | -0.064087 | 0.01831 | 61.1572 | 61.0245 | 122.9965 | 123.1201 | -0.059509 | 123.1705 | 61.0382 | -0.14191 | 123.1201 | -0.059509 | 61.0382 | 122.9965 | 123.1705 | -123.3124 | -123.3765
54.7188 | 123.5275 | -61.0382 | 62.1414 | 0.48909 | -0.060868 | -0.079414 | 0.099459 | -0.015918 | -0.080092 | 0.041406 | -61.1298 | 62.0499 | -61.116 | -61.322 | 61.94 | -0.036621 | 0.068665 | -0.013733 | 62.0728 | -61.2167 | -0.07782 | -0.091552 | -0.091553 | -0.28381 | -0.20142 | -0.17853 | -0.068664 | -0.013733 | 61.1069 | 61.0245 | 122.9782 | 123.0881 | -0.091553 | 123.111 | 61.0016 | -0.17853 | 123.0881 | -0.091553 | 61.0016 | 122.9782 | 123.111 | -123.2574 | -123.3582
55.6562 | 123.5275 | -61.0153 | 62.1735 | -0.15178 | -0.064072 | -0.058051 | 0.089846 | -0.01485 | -0.090773 | 0.043542 | -61.116 | 62.0728 | -61.1114 | -61.3449 | 61.9217 | 0.009155 | 0.07782 | -0.004578 | 62.1185 | -61.203 | -0.09613 | -0.10071 | -0.10071 | -0.32959 | -0.25177 | -0.18768 | -0.054932 | -0.004578 | 61.0931 | 61.0107 | 122.937 | 123.0881 | -0.10071 | 123.1338 | 61.0245 | -0.18768 | 123.0881 | -0.10071 | 61.0245 | 122.937 | 123.1338 | -123.2849 | -123.3765
56.6562 | 123.5779 | -61.0428 | 62.178 | 0.0771 | -0.056596 | -0.078345 | 0.079165 | -0.015918 | -0.099318 | 0.054224 | -61.1526 | 62.0636 | -61.1435 | -61.3586 | 61.9125 | 0.018311 | 0.10529 | -0.013733 | 62.1231 | -61.1984 | -0.10071 | -0.11444 | -0.10986 | -0.31586 | -0.2655 | -0.15564 | -0.054932 | -0.009155 | 61.1481 | 61.0291 | 122.9553 | 123.1064 | -0.10986 | 123.1659 | 61.0611 | -0.15564 | 123.1064 | -0.10986 | 61.0611 | 122.9553 | 123.1659 | -123.3215 | -123.3765
57.6562 | 123.5458 | -61.0336 | 62.1643 | 0.046583 | -0.068345 | -0.08689 | 0.089846 | -0.018055 | -0.09825 | 0.045679 | -61.1526 | 62.0728 | -61.1206 | -61.3266 | 61.9308 | -0.013733 | 0.07782 | -0.018311 | 62.1048 | -61.1755 | -0.086975 | -0.091553 | -0.11902 | -0.29297 | -0.23346 | -0.14191 | -0.05951 | -0.032044 | 61.1115 | 61.0153 | 122.9645 | 123.1064 | -0.11902 | 123.1384 | 61.0199 | -0.14191 | 123.1064 | -0.11902 | 61.0199 | 122.9645 | 123.1384 | -123.2849 | -123.3398
58.6562 | 123.5001 | -61.0474 | 62.1552 | 0.16865 | -0.063004 | -0.090095 | 0.088778 | -0.018055 | -0.091842 | 0.054224 | -61.1893 | 62.0682 | -61.1252 | -61.2946 | 61.9949 | 0.022888 | 0.036621 | 0.022888 | 62.0865 | -61.1938 | -0.07782 | -0.086975 | -0.14191 | -0.24719 | -0.16022 | -0.14649 | -0.068664 | -0.064087 | 61.084 | 61.0703 | 123.0423 | 123.1155 | -0.14191 | 123.1338 | 61.0703 | -0.14649 | 123.1155 | -0.14191 | 61.0703 | 123.0423 | 123.1338 | -123.2803 | -123.349
59.6562 | 123.4909 | -61.0291 | 62.1643 | 0.18391 | -0.066209 | -0.099708 | 0.081301 | -0.021259 | -0.1132 | 0.045679 | -61.1893 | 62.0636 | -61.1343 | -61.2946 | 61.9904 | 0.036621 | 0.009155 | 0.041199 | 62.0865 | -61.2076 | -0.10529 | -0.10071 | -0.16022 | -0.2655 | -0.17395 | -0.17853 | -0.07782 | -0.054932 | 61.0382 | 61.0703 | 123.0194 | 123.0927 | -0.16022 | 123.1155 | 61.0657 | -0.17853 | 123.0927 | -0.16022 | 61.0657 | 123.0194 | 123.1155 | -123.2986 | -123.3719
60.7188 | 123.4222 | -61.1023 | 62.1872 | 0.50435 | -0.051255 | -0.056983 | 0.11975 | -0.019123 | -0.086501 | 0.041406 | -61.2213 | 62.1506 | -61.1572 | -61.1664 | 62.0407 | 0.11444 | -0.082397 | 0.10529 | 62.0316 | -61.171 | -0.054932 | -0.036621 | -0.11902 | -0.064087 | -0.14649 | -0.068664 | -0.15564 | -0.064086 | 61.0199 | 61.2076 | 123.143 | 123.2529 | -0.11902 | 123.1338 | 61.2167 | -0.068664 | 123.2529 | -0.11902 | 61.2167 | 123.143 | 123.1338 | -123.3444 | -123.3582
61.6562 | 123.5046 | -61.0748 | 62.146 | 0.092359 | -0.064072 | -0.077277 | 0.089846 | -0.021259 | -0.10786 | 0.048883 | -61.2122 | 62.0682 | -61.1343 | -61.2854 | 61.9949 | 0.027466 | 0.018311 | 0.022888 | 62.0865 | -61.1572 | -0.059509 | -0.07782 | -0.13733 | -0.21057 | -0.15106 | -0.082398 | -0.059509 | -0.07782 | 61.0931 | 61.0977 | 123.0698 | 123.143 | -0.13733 | 123.1613 | 61.1023 | -0.082398 | 123.143 | -0.13733 | 61.1023 | 123.0698 | 123.1613 | -123.2803 | -123.3032
62.6562 | 123.4955 | -61.0474 | 62.1735 | 0.18391 | -0.060868 | -0.083686 | 0.09305 | -0.019123 | -0.09825 | 0.036066 | -61.1801 | 62.0819 | -61.1481 | -61.2808 | 61.9492 | 0.004578 | 0.045776 | 0 | 62.0682 | -61.1847 | -0.10071 | -0.091553 | -0.13275 | -0.23346 | -0.2243 | -0.13733 | -0.10529 | -0.032044 | 61.0931 | 61.0474 | 122.9965 | 123.1293 | -0.13275 | 123.1155 | 61.0519 | -0.13733 | 123.1293 | -0.13275 | 61.0519 | 122.9965 | 123.1155 | -123.3215 | -123.3582
63.7344 | 123.5321 | -61.0565 | 62.1552 | 0.62642 | -0.06514 | -0.08689 | 0.094119 | -0.025531 | -0.093978 | 0.049951 | -61.1572 | 62.027 | -61.1298 | -61.3266 | 61.9263 | -0.022888 | 0.068665 | -0.022888 | 62.0911 | -61.203 | -0.073242 | -0.12817 | -0.10071 | -0.27008 | -0.22888 | -0.14648 | -0.064087 | -0.027466 | 61.1252 | 61.0336 | 122.9828 | 123.0835 | -0.10071 | 123.1476 | 61.0336 | -0.14648 | 123.0835 | -0.10071 | 61.0336 | 122.9828 | 123.1476 | -123.2849 | -123.3582
64.6719 | 123.3994 | -61.0703 | 62.2192 | -0.30437 | -0.049119 | -0.077277 | 0.1048 | -0.023395 | -0.086501 | 0.049951 | -61.2122 | 62.1643 | -61.1252 | -61.1526 | 62.0453 | 0.16937 | -0.09613 | 0.13733 | 62.0728 | -61.1435 | -0.054932 | -0.054931 | -0.14191 | -0.082398 | -0.17395 | -0.073243 | -0.14648 | -0.086975 | 60.9741 | 61.2076 | 123.1155 | 123.2346 | -0.14191 | 123.143 | 61.2396 | -0.073243 | 123.2346 | -0.14191 | 61.2396 | 123.1155 | 123.143 | -123.3444 | -123.3627
65.6562 | 123.4909 | -61.0474 | 62.1643 | 0.41279 | -0.056596 | -0.097572 | 0.09305 | -0.020191 | -0.086501 | 0.042474 | -61.1801 | 62.0407 | -61.1206 | -61.3037 | 61.972 | 0.036621 | 0.032043 | 0.027466 | 62.0728 | -61.203 | -0.073242 | -0.1236 | -0.13275 | -0.25635 | -0.19226 | -0.15564 | -0.091553 | -0.05951 | 61.0794 | 61.0748 | 123.0194 | 123.0881 | -0.13275 | 123.1201 | 61.084 | -0.15564 | 123.0881 | -0.13275 | 61.084 | 123.0194 | 123.1201 | -123.2849 | -123.3673
66.6562 | 123.4863 | -61.0245 | 62.178 | 0.15339 | -0.0598 | -0.084754 | 0.083437 | -0.026599 | -0.096114 | 0.042474 | -61.1893 | 62.0728 | -61.1435 | -61.2946 | 61.972 | 0.022888 | 0.013733 | 0.018311 | 62.0636 | -61.1938 | -0.11902 | -0.10529 | -0.16479 | -0.27008 | -0.20599 | -0.16937 | -0.11444 | -0.045776 | 61.0382 | 61.0428 | 122.9965 | 123.0972 | -0.16479 | 123.0881 | 61.0474 | -0.16937 | 123.0972 | -0.16479 | 61.0474 | 122.9965 | 123.0881 | -123.3215 | -123.3719
67.7188 | 123.4772 | -61.0519 | 62.1506 | 0.35176 | -0.056596 | -0.087958 | 0.099459 | -0.015918 | -0.088637 | 0.048883 | -61.2167 | 62.0865 | -61.1252 | -61.2579 | 61.9812 | 0.045776 | 0.027466 | 0.041199 | 62.0728 | -61.1847 | -0.073242 | -0.064087 | -0.16479 | -0.20599 | -0.16937 | -0.13275 | -0.07782 | -0.091553 | 61.0794 | 61.0931 | 123.0331 | 123.1384 | -0.16479 | 123.1247 | 61.0977 | -0.13275 | 123.1384 | -0.16479 | 61.0977 | 123.0331 | 123.1247 | -123.2758 | -123.3353
68.6562 | 123.4955 | -61.0519 | 62.1597 | 0.39753 | -0.061936 | -0.054847 | 0.086642 | -0.019123 | -0.095046 | 0.043542 | -61.1893 | 62.059 | -61.1389 | -61.2671 | 61.9858 | 0.013733 | 0.013733 | 0.036621 | 62.0636 | -61.1893 | -0.086975 | -0.10071 | -0.13733 | -0.21515 | -0.17395 | -0.13733 | -0.09613 | -0.050354 | 61.0657 | 61.0886 | 123.0377 | 123.111 | -0.13733 | 123.1155 | 61.0657 | -0.13733 | 123.111 | -0.13733 | 61.0657 | 123.0377 | 123.1155 | -123.2986 | -123.349
69.7344 | 123.5321 | -61.0565 | 62.1414 | 0.56538 | -0.068345 | -0.080482 | 0.108 | -0.030872 | -0.082229 | 0.041406 | -61.1298 | 62.0682 | -61.1252 | -61.322 | 61.9354 | -0.032043 | 0.086975 | -0.027466 | 62.0819 | -61.2167 | -0.068664 | -0.073242 | -0.073242 | -0.2655 | -0.20599 | -0.16022 | -0.059509 | -0.004578 | 61.1435 | 61.0291 | 122.9919 | 123.1247 | -0.073242 | 123.1384 | 61.0245 | -0.16022 | 123.1247 | -0.073242 | 61.0245 | 122.9919 | 123.1384 | -123.2666 | -123.3582
70.6562 | 123.468 | -61.0565 | 62.1872 | 0.26021 | -0.067277 | -0.074073 | 0.086642 | -0.022327 | -0.096114 | 0.046747 | -61.1984 | 62.0453 | -61.1526 | -61.2762 | 61.972 | 0.022888 | 0.013733 | 0.041199 | 62.0682 | -61.1618 | -0.09613 | -0.14191 | -0.14191 | -0.21973 | -0.21515 | -0.10528 | -0.11902 | -0.045776 | 61.0703 | 61.0977 | 123.0286 | 123.1018 | -0.14191 | 123.1247 | 61.0794 | -0.10528 | 123.1018 | -0.14191 | 61.0794 | 123.0286 | 123.1247 | -123.3398 | -123.349
71.6562 | 123.4863 | -61.0657 | 62.1506 | 0.38228 | -0.054459 | -0.063392 | 0.09305 | -0.020191 | -0.09825 | 0.058496 | -61.1847 | 62.0407 | -61.1389 | -61.2946 | 61.9766 | 0.032043 | 0 | 0.032043 | 62.0773 | -61.1893 | -0.073242 | -0.10986 | -0.11902 | -0.22888 | -0.17395 | -0.1236 | -0.073242 | -0.045776 | 61.0657 | 61.0977 | 123.0423 | 123.1064 | -0.11902 | 123.143 | 61.0977 | -0.1236 | 123.1064 | -0.11902 | 61.0977 | 123.0423 | 123.143 | -123.2895 | -123.3398
72.6562 | 123.5138 | -61.0336 | 62.1552 | 0.55012 | -0.060868 | -0.094367 | 0.097323 | -0.020191 | -0.088637 | 0.041406 | -61.1526 | 62.0682 | -61.1343 | -61.3495 | 61.9446 | -0.032043 | 0.068665 | -0.018311 | 62.0636 | -61.2122 | -0.10071 | -0.086975 | -0.11902 | -0.31586 | -0.21057 | -0.17853 | -0.091552 | -0.018311 | 61.1023 | 61.0153 | 122.9782 | 123.1018 | -0.11902 | 123.0972 | 61.0016 | -0.17853 | 123.1018 | -0.11902 | 61.0016 | 122.9782 | 123.0972 | -123.2895 | -123.3673
73.6562 | 123.5138 | -61.0474 | 62.1597 | 0.53486 | -0.0598 | -0.074073 | 0.099459 | -0.019123 | -0.083297 | 0.040338 | -61.1343 | 62.0499 | -61.1343 | -61.3266 | 61.9354 | -0.027466 | 0.082397 | -0.018311 | 62.0819 | -61.2259 | -0.086975 | -0.10986 | -0.086975 | -0.27924 | -0.2243 | -0.17853 | -0.07782 | 0 | 61.1298 | 61.0291 | 122.9828 | 123.0972 | -0.086975 | 123.1293 | 61.0199 | -0.17853 | 123.0972 | -0.086975 | 61.0199 | 122.9828 | 123.1293 | -123.2941 | -123.3856
74.6719 | 123.5733 | -61.0245 | 62.1597 | -0.04497 | -0.071549 | -0.089027 | 0.084505 | -0.020191 | -0.10252 | 0.048883 | -61.1252 | 62.0911 | -61.1206 | -61.3495 | 61.9171 | 0.004578 | 0.10529 | -0.032043 | 62.0819 | -61.1938 | -0.09613 | -0.068665 | -0.10071 | -0.32501 | -0.24262 | -0.16937 | -0.07782 | -0.004578 | 61.1298 | 60.9924 | 122.9416 | 123.1155 | -0.10071 | 123.1064 | 61.0291 | -0.16937 | 123.1155 | -0.10071 | 61.0291 | 122.9416 | 123.1064 | -123.2803 | -123.3536
75.6562 | 123.5001 | -61.0428 | 62.1323 | 0.55012 | -0.063004 | -0.06446 | 0.091982 | -0.018055 | -0.090773 | 0.051019 | -61.1755 | 62.0911 | -61.1343 | -61.3312 | 61.9263 | -0.032043 | 0.086975 | -0.027466 | 62.0728 | -61.2167 | -0.091552 | -0.041199 | -0.13275 | -0.28839 | -0.20599 | -0.17395 | -0.059509 | -0.041199 | 61.1298 | 61.0153 | 122.9691 | 123.1338 | -0.13275 | 123.1155 | 61.0107 | -0.17395 | 123.1338 | -0.13275 | 61.0107 | 122.9691 | 123.1155 | -123.2666 | -123.349
76.6562 | 123.4589 | -61.0336 | 62.1918 | 0.50435 | -0.072617 | -0.063392 | 0.082369 | -0.012714 | -0.091842 | 0.043542 | -61.1893 | 62.0407 | -61.1389 | -61.2991 | 61.9583 | -0.004578 | 0.050354 | 0.013733 | 62.0499 | -61.2076 | -0.10529 | -0.15106 | -0.15564 | -0.2655 | -0.23346 | -0.17395 | -0.14191 | -0.050354 | 61.084 | 61.0474 | 122.9919 | 123.0743 | -0.15564 | 123.0835 | 61.0291 | -0.17395 | 123.0743 | -0.15564 | 61.0291 | 122.9919 | 123.0835 | -123.3307 | -123.3994
77.6562 | 123.4863 | -61.0519 | 62.1414 | 0.38228 | -0.069413 | -0.078345 | 0.10053 | -0.028736 | -0.083297 | 0.042474 | -61.1572 | 62.0773 | -61.1481 | -61.3037 | 62.0132 | -0.004578 | 0.059509 | -0.036621 | 62.0865 | -61.2076 | -0.09613 | -0.064086 | -0.10529 | -0.25177 | -0.12817 | -0.15564 | -0.054931 | -0.009156 | 61.1114 | 61.0153 | 123.0652 | 123.1293 | -0.10529 | 123.1384 | 61.0474 | -0.15564 | 123.1293 | -0.10529 | 61.0474 | 123.0652 | 123.1384 | -123.2895 | -123.349
78.6562 | 123.555 | -61.0245 | 62.1506 | 0.58064 | -0.057664 | -0.08155 | 0.089846 | -0.024463 | -0.08116 | 0.03927 | -61.1252 | 62.0865 | -61.1252 | -61.3266 | 61.9492 | -0.022888 | 0.073242 | -0.022888 | 62.0819 | -61.1984 | -0.10071 | -0.064087 | -0.10071 | -0.30212 | -0.20142 | -0.17395 | -0.068665 | 0 | 61.0977 | 61.0016 | 122.9736 | 123.111 | -0.10071 | 123.1064 | 61.0016 | -0.17395 | 123.111 | -0.10071 | 61.0016 | 122.9736 | 123.1064 | -123.2758 | -123.349
79.6719 | 123.4589 | -61.0657 | 62.1643 | -0.30437 | -0.053391 | -0.06446 | 0.094119 | -0.025531 | -0.097182 | 0.047815 | -61.1526 | 62.1277 | -61.1343 | -61.2167 | 62.0178 | 0.1236 | -0.041199 | 0.091553 | 62.0636 | -61.1435 | -0.068664 | -0.036621 | -0.086975 | -0.15106 | -0.14648 | -0.07782 | -0.10071 | -0.018311 | 61.0245 | 61.1572 | 123.0835 | 123.1934 | -0.086975 | 123.1293 | 61.1893 | -0.07782 | 123.1934 | -0.086975 | 61.1893 | 123.0835 | 123.1293 | -123.2986 | -123.3078
80.6562 | 123.5321 | -61.0336 | 62.1552 | 0.56538 | -0.067277 | -0.069801 | 0.088778 | -0.023395 | -0.073684 | 0.043542 | -61.1481 | 62.0636 | -61.1435 | -61.3174 | 61.94 | -0.018311 | 0.07782 | -0.027466 | 62.0636 | -61.2167 | -0.10986 | -0.091552 | -0.11444 | -0.28381 | -0.21515 | -0.18311 | -0.091552 | -0.004577 | 61.1115 | 61.0062 | 122.9736 | 123.0972 | -0.11444 | 123.0972 | 61.0153 | -0.18311 | 123.0972 | -0.11444 | 61.0153 | 122.9736 | 123.0972 | -123.2986 | -123.3719
81.6562 | 123.4772 | -61.0474 | 62.1368 | 1.2215 | -0.0598 | -0.071937 | 0.09305 | -0.018055 | -0.10252 | 0.038202 | -61.1664 | 62.059 | -61.1481 | -61.3266 | 61.9629 | 0.022888 | 0.050354 | 0 | 62.0636 | -61.2122 | -0.10071 | -0.07782 | -0.11902 | -0.27924 | -0.17395 | -0.1648 | -0.073242 | -0.018311 | 61.0977 | 61.0474 | 123.0103 | 123.1064 | -0.11902 | 123.111 | 61.0703 | -0.1648 | 123.1064 | -0.11902 | 61.0703 | 123.0103 | 123.111 | -123.2849 | -123.349
82.6562 | 123.4863 | -61.0428 | 62.1597 | 0.62642 | -0.048051 | -0.091163 | 0.10694 | -0.027668 | -0.07582 | 0.046747 | -61.1893 | 62.1597 | -61.1343 | -61.2579 | 61.9995 | 0.004578 | 0.027466 | 0.022888 | 62.0728 | -61.203 | -0.091552 | 0 | -0.14648 | -0.21515 | -0.16022 | -0.16022 | -0.086975 | -0.054932 | 61.0703 | 61.0657 | 123.0423 | 123.2025 | -0.14648 | 123.1155 | 61.0474 | -0.16022 | 123.2025 | -0.14648 | 61.0474 | 123.0423 | 123.1155 | -123.2941 | -123.3627
83.6562 | 123.5275 | -61.0245 | 62.1414 | 0.16865 | -0.046983 | -0.061256 | 0.10587 | -0.013782 | -0.083297 | 0.051019 | -61.1618 | 62.114 | -61.1572 | -61.3083 | 61.9537 | -0.013733 | 0.059509 | -0.004578 | 62.0911 | -61.2076 | -0.13275 | -0.027465 | -0.13733 | -0.28381 | -0.18768 | -0.18311 | -0.050354 | -0.004577 | 61.084 | 61.0199 | 122.9782 | 123.1384 | -0.13733 | 123.1155 | 61.0107 | -0.18311 | 123.1384 | -0.13733 | 61.0107 | 122.9782 | 123.1155 | -123.2986 | -123.349
84.6562 | 123.5184 | -61.0519 | 62.1597 | -0.075488 | -0.060868 | -0.073005 | 0.085574 | -0.013782 | -0.088637 | 0.052087 | -61.1252 | 62.1231 | -61.0977 | -61.3358 | 61.9583 | 0.018311 | 0.091553 | -0.018311 | 62.1231 | -61.1984 | -0.045776 | -0.036621 | -0.073242 | -0.28381 | -0.20142 | -0.14648 | -0.036621 | -0.027466 | 61.1435 | 61.0336 | 123.0103 | 123.175 | -0.073242 | 123.175 | 61.0703 | -0.14648 | 123.175 | -0.073242 | 61.0703 | 123.0103 | 123.175 | -123.2574 | -123.3582
85.6562 | 123.4543 | -61.0657 | 62.1414 | 0.55012 | -0.051255 | -0.089027 | 0.10694 | -0.013782 | -0.070479 | 0.052087 | -61.203 | 62.1323 | -61.1526 | -61.2076 | 61.9537 | 0.045776 | 0.004578 | 0.032043 | 62.0682 | -61.1984 | -0.086975 | -0.009155 | -0.13733 | -0.14191 | -0.18768 | -0.13275 | -0.073242 | -0.050354 | 61.0703 | 61.0977 | 123.0194 | 123.1979 | -0.13733 | 123.1338 | 61.1114 | -0.13275 | 123.1979 | -0.13733 | 61.1114 | 123.0194 | 123.1338 | -123.2941 | -123.3398
86.6562 | 123.3994 | -61.0977 | 62.1872 | 0.45857 | -0.041642 | -0.090095 | 0.11655 | -0.018055 | -0.070479 | 0.051019 | -61.235 | 62.1689 | -61.1755 | -61.1572 | 62.0911 | 0.12817 | -0.086975 | 0.1236 | 62.0316 | -61.1664 | -0.07782 | -0.018311 | -0.13733 | -0.05951 | -0.096131 | -0.068665 | -0.15564 | -0.059509 | 61.0107 | 61.2213 | 123.1888 | 123.2666 | -0.13733 | 123.1293 | 61.2259 | -0.068665 | 123.2666 | -0.13733 | 61.2259 | 123.1888 | 123.1293 | -123.3627 | -123.3536
87.6562 | 123.3856 | -61.1069 | 62.1964 | 0.45857 | -0.041642 | -0.085822 | 0.11014 | -0.0052367 | -0.07582 | 0.058496 | -61.2167 | 62.1689 | -61.1526 | -61.1526 | 62.0911 | 0.16479 | -0.091553 | 0.15106 | 62.027 | -61.1618 | -0.045776 | -0.027466 | -0.10986 | -0.045776 | -0.10529 | -0.054931 | -0.16937 | -0.064087 | 61.0153 | 61.2579 | 123.1979 | 123.2758 | -0.10986 | 123.1339 | 61.2717 | -0.054931 | 123.2758 | -0.10986 | 61.2717 | 123.1979 | 123.1339 | -123.349 | -123.3582
88.6719 | 123.5229 | -61.0703 | 62.146 | 0.29072 | -0.058732 | -0.085822 | 0.082369 | -0.018055 | -0.09291 | 0.052087 | -61.2122 | 62.0773 | -61.1252 | -61.322 | 61.9858 | 0.045776 | 0.027466 | 0.045776 | 62.0819 | -61.2076 | -0.054932 | -0.068664 | -0.14191 | -0.25177 | -0.16022 | -0.13733 | -0.064087 | -0.086975 | 61.0977 | 61.116 | 123.056 | 123.1476 | -0.14191 | 123.1522 | 61.116 | -0.13733 | 123.1476 | -0.14191 | 61.116 | 123.056 | 123.1522 | -123.2712 | -123.3536
89.6562 | 123.3994 | -61.0931 | 62.1964 | 0.42805 | -0.048051 | -0.090095 | 0.10587 | -0.016986 | -0.069411 | 0.044611 | -61.2396 | 62.1826 | -61.1618 | -61.1343 | 62.1094 | 0.10986 | -0.07782 | 0.13275 | 62.0316 | -61.1801 | -0.068664 | -0.013733 | -0.14648 | -0.041198 | -0.086975 | -0.086975 | -0.1648 | -0.07782 | 61.0153 | 61.2259 | 123.2025 | 123.2758 | -0.14648 | 123.1247 | 61.203 | -0.086975 | 123.2758 | -0.14648 | 61.203 | 123.2025 | 123.1247 | -123.3582 | -123.3765
90.6562 | 123.3994 | -61.0977 | 62.178 | 0.44331 | -0.049119 | -0.068732 | 0.10373 | -0.018055 | -0.076888 | 0.044611 | -61.235 | 62.1735 | -61.1664 | -61.1618 | 62.0728 | 0.11902 | -0.082397 | 0.14191 | 62.0041 | -61.1755 | -0.068665 | -0.004578 | -0.13733 | -0.064087 | -0.10529 | -0.07782 | -0.17395 | -0.068664 | 61.0153 | 61.2396 | 123.1705 | 123.2712 | -0.13733 | 123.1018 | 61.2167 | -0.07782 | 123.2712 | -0.13733 | 61.2167 | 123.1705 | 123.1018 | -123.3444 | -123.3536
91.6562 | 123.3994 | -61.1023 | 62.1872 | 0.47383 | -0.046983 | -0.080482 | 0.099459 | -0.0063047 | -0.079024 | 0.052087 | -61.2442 | 62.1918 | -61.1847 | -61.1755 | 62.0636 | 0.12817 | -0.07782 | 0.11902 | 62.0499 | -61.1801 | -0.082397 | 0.004577 | -0.14191 | -0.073242 | -0.1236 | -0.07782 | -0.13733 | -0.05951 | 61.0245 | 61.2213 | 123.1659 | 123.2941 | -0.14191 | 123.1522 | 61.2305 | -0.07782 | 123.2941 | -0.14191 | 61.2305 | 123.1659 | 123.1522 | -123.3719 | -123.3673
92.6562 | 123.381 | -61.1114 | 62.1735 | 0.38228 | -0.041642 | -0.066596 | 0.098391 | -0.0063047 | -0.074752 | 0.040338 | -61.235 | 62.1964 | -61.1572 | -61.1664 | 62.0773 | 0.13733 | -0.10071 | 0.15106 | 62.0361 | -61.171 | -0.045777 | 0.022888 | -0.1236 | -0.054932 | -0.09613 | -0.059509 | -0.13733 | -0.077819 | 61.0107 | 61.2625 | 123.1888 | 123.3078 | -0.1236 | 123.1476 | 61.2488 | -0.059509 | 123.3078 | -0.1236 | 61.2488 | 123.1888 | 123.1476 | -123.3307 | -123.3444
93.6562 | 123.436 | -61.0519 | 62.2055 | 0.27546 | -0.0598 | -0.074073 | 0.10373 | -0.0052367 | -0.069411 | 0.048883 | -61.0199 | 62.1826 | -61.1526 | -61.171 | 62.0819 | 0.10986 | -0.082397 | 0.11902 | 62.0499 | -61.1938 | -0.10071 | -0.022888 | 0.032044 | -0.11902 | -0.1236 | -0.14191 | -0.15564 | 0.13275 | 60.9695 | 61.171 | 123.1338 | 123.2346 | 0.032044 | 123.1018 | 61.1618 | -0.14191 | 123.2346 | 0.032044 | 61.1618 | 123.1338 | 123.1018 | -123.3582 | -123.3994
94.6562 | 123.3719 | -61.0886 | 62.1735 | 0.53486 | -0.04271 | -0.069801 | 0.098391 | -0.0020327 | -0.072616 | 0.049951 | -61.2167 | 62.1918 | -61.1664 | -61.1572 | 62.1231 | 0.15564 | -0.10529 | 0.14648 | 62.0544 | -61.1938 | -0.07782 | 0.01831 | -0.12817 | -0.068665 | -0.050354 | -0.10529 | -0.11902 | -0.050354 | 60.9833 | 61.235 | 123.2117 | 123.2803 | -0.12817 | 123.143 | 61.2442 | -0.10529 | 123.2803 | -0.12817 | 61.2442 | 123.2117 | 123.143 | -123.3398 | -123.3673
95.6562 | 123.4177 | -61.0977 | 62.2009 | 0.13813 | -0.043778 | -0.082618 | 0.094119 | -0.0041687 | -0.066207 | 0.041406 | -61.1664 | 62.2055 | -61.1435 | -61.2076 | 62.0544 | 0.10986 | -0.027466 | 0.09613 | 62.0544 | -61.171 | -0.045777 | 0.004577 | -0.068665 | -0.10986 | -0.14648 | -0.073242 | -0.14648 | -0.022888 | 61.0703 | 61.1938 | 123.1522 | 123.3032 | -0.068665 | 123.1522 | 61.2076 | -0.073242 | 123.3032 | -0.068665 | 61.2076 | 123.1522 | 123.1522 | -123.3444 | -123.3719
96.6562 | 123.3719 | -61.0977 | 62.1826 | 0.19917 | -0.041642 | -0.091163 | 0.10053 | -0.0041687 | -0.080092 | 0.044611 | -61.1847 | 62.2009 | -61.1572 | -61.1984 | 62.0636 | 0.12817 | -0.054932 | 0.11444 | 62.0636 | -61.1938 | -0.05951 | 0.018311 | -0.086975 | -0.10071 | -0.11902 | -0.096131 | -0.11902 | -0.027465 | 61.0428 | 61.2122 | 123.1613 | 123.2986 | -0.086975 | 123.1613 | 61.2259 | -0.096131 | 123.2986 | -0.086975 | 61.2259 | 123.1613 | 123.1613 | -123.3398 | -123.3765
97.6562 | 123.4268 | -61.0565 | 62.1735 | 0.22969 | -0.049119 | -0.090095 | 0.10053 | -0.0063047 | -0.066207 | 0.047815 | -61.1664 | 62.2055 | -61.1389 | -61.1984 | 62.0499 | 0.13275 | -0.045776 | 0.10529 | 62.0682 | -61.1801 | -0.082397 | 0.032043 | -0.10986 | -0.14191 | -0.1236 | -0.1236 | -0.10529 | -0.027466 | 61.0107 | 61.1618 | 123.1064 | 123.262 | -0.10986 | 123.1247 | 61.1893 | -0.1236 | 123.262 | -0.10986 | 61.1893 | 123.1064 | 123.1247 | -123.3124 | -123.3536
98.6562 | 123.4406 | -61.084 | 62.1918 | 0.16865 | -0.053391 | -0.079414 | 0.10266 | 0.0075803 | -0.07582 | 0.052087 | -61.1435 | 62.1826 | -61.1389 | -61.2305 | 62.0316 | 0.091553 | -0.009155 | 0.086975 | 62.0773 | -61.1984 | -0.054932 | -0.009155 | -0.05951 | -0.14648 | -0.16022 | -0.11444 | -0.11444 | -0.004578 | 61.0748 | 61.171 | 123.1155 | 123.2666 | -0.05951 | 123.1613 | 61.1755 | -0.11444 | 123.2666 | -0.05951 | 61.1755 | 123.1155 | 123.1613 | -123.3307 | -123.3902
99.6562 | 123.4222 | -61.0474 | 62.2101 | 0.031324 | -0.032029 | -0.092231 | 0.09305 | -0.0052367 | -0.070479 | 0.042474 | -61.1572 | 62.1918 | -61.1664 | -61.1847 | 62.0224 | 0.091553 | -0.004578 | 0.068665 | 62.0911 | -61.203 | -0.11902 | -0.018311 | -0.10986 | -0.13733 | -0.18768 | -0.15564 | -0.11902 | 0.009155 | 61.0428 | 61.116 | 123.0698 | 123.2391 | -0.10986 | 123.1384 | 61.1389 | -0.15564 | 123.2391 | -0.10986 | 61.1389 | 123.0698 | 123.1384 | -123.3765 | -123.4131
100.6562 | 123.4314 | -61.0748 | 62.2055 | -0.075488 | -0.052323 | -0.076209 | 0.098391 | -0.0031007 | -0.080092 | 0.044611 | -61.2213 | 62.2192 | -61.1435 | -61.1893 | 62.0453 | 0.15106 | -0.064087 | 0.14191 | 62.0819 | -61.171 | -0.068665 | 0.013733 | -0.14648 | -0.11444 | -0.16022 | -0.09613 | -0.1236 | -0.077819 | 61.0107 | 61.2167 | 123.1201 | 123.2941 | -0.14648 | 123.1567 | 61.2259 | -0.09613 | 123.2941 | -0.14648 | 61.2259 | 123.1201 | 123.1567 | -123.349 | -123.3765
101.6562 | 123.4085 | -61.1069 | 62.2147 | -0.19756 | -0.058732 | -0.092231 | 0.10266 | 0.0043763 | -0.077956 | 0.053156 | -61.2213 | 62.2238 | -61.1526 | -61.1664 | 62.0636 | 0.16022 | -0.064087 | 0.14191 | 62.0865 | -61.1801 | -0.045776 | 0.009155 | -0.11444 | -0.059509 | -0.15106 | -0.073242 | -0.12817 | -0.068664 | 61.0428 | 61.2488 | 123.1705 | 123.3307 | -0.11444 | 123.1934 | 61.2671 | -0.073242 | 123.3307 | -0.11444 | 61.2671 | 123.1705 | 123.1934 | -123.3673 | -123.3948
102.6562 | 123.4268 | -61.084 | 62.1964 | 0.031324 | -0.050187 | -0.083686 | 0.09305 | -0.0052367 | -0.069411 | 0.048883 | -61.1343 | 62.178 | -61.1526 | -61.2534 | 62.027 | 0.10071 | -0.032043 | 0.091553 | 62.0956 | -61.1801 | -0.068665 | -0.01831 | -0.050354 | -0.16937 | -0.16937 | -0.096131 | -0.10071 | 0.018311 | 61.0519 | 61.1755 | 123.111 | 123.262 | -0.050354 | 123.1796 | 61.1847 | -0.096131 | 123.262 | -0.050354 | 61.1847 | 123.111 | 123.1796 | -123.349 | -123.3765
103.6562 | 123.3994 | -61.0748 | 62.1918 | -0.22808 | -0.056596 | -0.095435 | 0.1048 | -0.0031007 | -0.076888 | 0.058496 | -61.2213 | 62.1826 | -61.1893 | -61.1893 | 62.0544 | 0.16022 | -0.07782 | 0.15564 | 62.1094 | -61.1893 | -0.11444 | -0.009155 | -0.14648 | -0.11444 | -0.13733 | -0.11444 | -0.082397 | -0.032043 | 60.997 | 61.2305 | 123.1293 | 123.2574 | -0.14648 | 123.1842 | 61.235 | -0.11444 | 123.2574 | -0.14648 | 61.235 | 123.1293 | 123.1842 | -123.381 | -123.381
104.6562 | 123.4543 | -61.0748 | 62.2238 | -0.1823 | -0.064072 | -0.058051 | 0.08771 | -0.0052367 | -0.087569 | 0.049951 | -61.1847 | 62.2009 | -61.1572 | -61.2076 | 62.0636 | 0.14648 | -0.054932 | 0.14191 | 62.1094 | -61.1664 | -0.082398 | -0.022888 | -0.10986 | -0.13275 | -0.16022 | -0.091553 | -0.11444 | -0.027465 | 61.0199 | 61.2167 | 123.1384 | 123.2758 | -0.10986 | 123.1842 | 61.2213 | -0.091553 | 123.2758 | -0.10986 | 61.2213 | 123.1384 | 123.1842 | -123.381 | -123.3902
105.6562 | 123.4497 | -61.0657 | 62.2101 | -0.10601 | -0.051255 | -0.076209 | 0.085574 | -0.0084417 | -0.088637 | 0.032861 | -61.1572 | 62.1643 | -61.1481 | -61.2213 | 62.0178 | 0.10071 | -0.045776 | 0.10071 | 62.1002 | -61.1893 | -0.082397 | -0.045776 | -0.091553 | -0.15564 | -0.19226 | -0.1236 | -0.10986 | -0.009156 | 61.0199 | 61.1664 | 123.0835 | 123.23 | -0.091553 | 123.1659 | 61.1664 | -0.1236 | 123.23 | -0.091553 | 61.1664 | 123.0835 | 123.1659 | -123.3582 | -123.3994
106.6562 | 123.4039 | -61.084 | 62.2055 | 0.70271 | -0.049119 | -0.092231 | 0.080233 | -0.0084417 | -0.091842 | 0.042474 | -61.2213 | 62.1964 | -61.1664 | -61.1938 | 62.0453 | 0.13275 | -0.07782 | 0.14648 | 62.1002 | -61.1664 | -0.082398 | -0.009155 | -0.13733 | -0.10986 | -0.16022 | -0.082398 | -0.10529 | -0.054931 | 61.0062 | 61.2305 | 123.1293 | 123.2803 | -0.13733 | 123.1842 | 61.2167 | -0.082398 | 123.2803 | -0.13733 | 61.2167 | 123.1293 | 123.1842 | -123.3719 | -123.3719
107.6562 | 123.4177 | -61.0931 | 62.2238 | -0.22808 | -0.070481 | -0.089027 | 0.089846 | -0.0020327 | -0.09291 | 0.054224 | -61.1801 | 62.1368 | -61.1435 | -61.2442 | 62.0224 | 0.086975 | -0.068665 | 0.16937 | 62.1414 | -61.1801 | -0.050354 | -0.086975 | -0.086975 | -0.15106 | -0.20142 | -0.086975 | -0.082398 | -0.036621 | 61.0245 | 61.2625 | 123.1155 | 123.23 | -0.086975 | 123.2346 | 61.1801 | -0.086975 | 123.23 | -0.086975 | 61.1801 | 123.1155 | 123.2346 | -123.3673 | -123.4039
108.6562 | 123.3994 | -61.0519 | 62.2375 | -0.36541 | -0.055527 | -0.10184 | 0.099459 | -0.0041687 | -0.086501 | 0.054224 | -61.2167 | 62.1689 | -61.1664 | -61.1984 | 62.0544 | 0.16022 | -0.07782 | 0.14191 | 62.1002 | -61.1664 | -0.11444 | -0.068665 | -0.16479 | -0.14648 | -0.18311 | -0.11444 | -0.13733 | -0.050354 | 60.9741 | 61.1938 | 123.1064 | 123.2208 | -0.16479 | 123.1522 | 61.2122 | -0.11444 | 123.2208 | -0.16479 | 61.2122 | 123.1064 | 123.1522 | -123.4039 | -123.4039
109.6562 | 123.3902 | -61.0474 | 62.2192 | -1.1283 | -0.061936 | -0.092231 | 0.090914 | -0.0063047 | -0.085433 | 0.043542 | -61.2259 | 62.1552 | -61.1435 | -61.2076 | 62.0499 | 0.15564 | -0.068665 | 0.14648 | 62.0865 | -61.1755 | -0.096131 | -0.064087 | -0.17853 | -0.16022 | -0.16937 | -0.12817 | -0.13275 | -0.082397 | 60.9787 | 61.1938 | 123.0972 | 123.2025 | -0.17853 | 123.1338 | 61.203 | -0.12817 | 123.2025 | -0.17853 | 61.203 | 123.0972 | 123.1338 | -123.3627 | -123.3948
110.6562 | 123.4177 | -61.0474 | 62.233 | -4.058 | -0.057664 | -0.08155 | 0.084505 | -0.020191 | -0.090773 | 0.048883 | -61.2625 | 62.1735 | -61.1526 | -61.1801 | 62.0361 | 0.16022 | -0.059509 | 0.16937 | 62.1094 | -61.1618 | -0.10529 | -0.059509 | -0.21515 | -0.13275 | -0.19684 | -0.11444 | -0.1236 | -0.10986 | 60.9879 | 61.2167 | 123.0835 | 123.2208 | -0.21515 | 123.1567 | 61.2076 | -0.11444 | 123.2208 | -0.21515 | 61.2076 | 123.0835 | 123.1567 | -123.3856 | -123.3948
111.6562 | 123.3673 | -61.0703 | 62.2238 | -0.24333 | -0.054459 | -0.10932 | 0.096255 | -0.018055 | -0.080092 | 0.037134 | -61.2259 | 62.178 | -61.1481 | -61.084 | 62.2925 | 0.19226 | -0.16937 | 0.07782 | 62.0865 | -61.1893 | -0.07782 | -0.045776 | -0.15564 | -0.013733 | 0.068664 | -0.11902 | -0.13733 | -0.07782 | 60.9009 | 61.1481 | 123.3627 | 123.2483 | -0.15564 | 123.1567 | 61.2625 | -0.11902 | 123.2483 | -0.15564 | 61.2625 | 123.3627 | 123.1567 | -123.3719 | -123.4131
112.6562 | 123.3856 | -61.0703 | 62.2375 | -0.19756 | -0.060868 | -0.083686 | 0.095187 | 0.00010333 | -0.085433 | 0.051019 | -61.2213 | 62.1643 | -61.171 | -61.2122 | 62.059 | 0.16479 | -0.064087 | 0.14191 | 62.146 | -61.1938 | -0.10071 | -0.073242 | -0.15106 | -0.14191 | -0.17853 | -0.1236 | -0.091553 | -0.050354 | 61.0062 | 61.2122 | 123.1293 | 123.2346 | -0.15106 | 123.2162 | 61.235 | -0.1236 | 123.2346 | -0.15106 | 61.235 | 123.1293 | 123.2162 | -123.4085 | -123.4314
113.6562 | 123.4085 | -61.0794 | 62.2284 | -0.22808 | -0.054459 | -0.097572 | 0.081301 | -0.015918 | -0.089705 | 0.052087 | -61.1847 | 62.146 | -61.1481 | -61.1481 | 62.059 | 0.10071 | -0.091553 | 0.13733 | 62.1048 | -61.171 | -0.068664 | -0.082398 | -0.10528 | -0.068664 | -0.16937 | -0.091552 | -0.1236 | -0.036621 | 60.9879 | 61.2167 | 123.1384 | 123.2254 | -0.10528 | 123.1842 | 61.1801 | -0.091552 | 123.2254 | -0.10528 | 61.1801 | 123.1384 | 123.1842 | -123.3765 | -123.3994
114.6562 | 123.5367 | -61.0336 | 62.178 | -0.13652 | -0.06514 | -0.093299 | 0.078097 | -0.0095097 | -0.091842 | 0.046747 | -61.1343 | 62.0682 | -61.1252 | -61.3129 | 61.9217 | 0.018311 | 0.059509 | 0.018311 | 62.1414 | -61.2076 | -0.091553 | -0.10986 | -0.10071 | -0.27924 | -0.25635 | -0.17395 | -0.036622 | -0.009155 | 61.0931 | 61.0519 | 122.9553 | 123.1018 | -0.10071 | 123.175 | 61.0519 | -0.17395 | 123.1018 | -0.10071 | 61.0519 | 122.9553 | 123.175 | -123.3032 | -123.3856
115.6562 | 123.5413 | -61.0336 | 62.1964 | 0.19917 | -0.055527 | -0.09864 | 0.089846 | -0.020191 | -0.095046 | 0.045679 | -61.1252 | 62.0911 | -61.1206 | -61.3449 | 61.9171 | 0.018311 | 0.082397 | -0.018311 | 62.1368 | -61.203 | -0.086975 | -0.10529 | -0.091553 | -0.31128 | -0.27924 | -0.16937 | -0.059509 | -0.004578 | 61.116 | 61.0153 | 122.9507 | 123.1247 | -0.091553 | 123.1705 | 61.0519 | -0.16937 | 123.1247 | -0.091553 | 61.0519 | 122.9507 | 123.1705 | -123.317 | -123.3994
116.8281 | 123.4863 | -61.0428 | 62.1643 | -3.3714 | -0.054459 | -0.080482 | 0.073824 | -0.024463 | -0.090773 | 0.046747 | -61.2762 | 62.0865 | -61.1435 | -61.2808 | 61.9537 | 0.013733 | 0 | 0.041199 | 62.0911 | -61.2122 | -0.10071 | -0.07782 | -0.23346 | -0.23804 | -0.21057 | -0.16937 | -0.073243 | -0.13275 | 61.0428 | 61.084 | 122.9965 | 123.1293 | -0.23346 | 123.1338 | 61.0565 | -0.16937 | 123.1293 | -0.23346 | 61.0565 | 122.9965 | 123.1338 | -123.3078 | -123.3765
118.5938 | 123.3994 | -61.0886 | 62.2101 | 0.19917 | -0.045914 | -0.093299 | 0.11121 | -0.015918 | -0.082229 | 0.044611 | -61.1801 | 62.1506 | -61.1389 | -61.1572 | 62.0682 | 0.09613 | -0.082397 | 0.10071 | 62.0544 | -61.1893 | -0.050354 | -0.059509 | -0.091553 | -0.068665 | -0.14191 | -0.10071 | -0.15564 | -0.041199 | 61.0062 | 61.1893 | 123.1567 | 123.2391 | -0.091553 | 123.143 | 61.1847 | -0.10071 | 123.2391 | -0.091553 | 61.1847 | 123.1567 | 123.143 | -123.349 | -123.3994
119.2812 | 123.4085 | -61.0794 | 62.1964 | -0.22808 | -0.055527 | -0.076209 | 0.10266 | -0.016986 | -0.096114 | 0.049951 | -61.2259 | 62.146 | -61.1664 | -61.1435 | 62.059 | 0.15106 | -0.082397 | 0.13733 | 62.1002 | -61.1755 | -0.086975 | -0.050354 | -0.14648 | -0.064087 | -0.13733 | -0.09613 | -0.09613 | -0.059509 | 60.997 | 61.2167 | 123.1384 | 123.2254 | -0.14648 | 123.1796 | 61.2305 | -0.09613 | 123.2254 | -0.14648 | 61.2305 | 123.1384 | 123.1796 | -123.3627 | -123.3719
120.5156 | 123.4543 | -61.0748 | 62.1918 | -0.13652 | -0.050187 | -0.092231 | 0.096255 | -0.0073727 | -0.07582 | 0.055292 | -61.171 | 62.1918 | -61.1755 | -61.1984 | 62.0087 | 0.11444 | -0.041199 | 0.086975 | 62.1048 | -61.1618 | -0.10071 | 0 | -0.09613 | -0.1236 | -0.1831 | -0.086975 | -0.086975 | 0.004578 | 61.0336 | 61.1618 | 123.0835 | 123.2666 | -0.09613 | 123.1796 | 61.1893 | -0.086975 | 123.2666 | -0.09613 | 61.1893 | 123.0835 | 123.1796 | -123.3673 | -123.3536
121.1562 | 123.4909 | -61.0474 | 62.1918 | 0.16865 | -0.058732 | -0.099708 | 0.08771 | -0.012714 | -0.087569 | 0.048883 | -61.1618 | 62.1414 | -61.1298 | -61.3266 | 61.9537 | 0.013733 | 0.041199 | 0.032043 | 62.0911 | -61.2259 | -0.082398 | -0.050354 | -0.11444 | -0.27924 | -0.23804 | -0.17853 | -0.10071 | -0.032043 | 61.0886 | 61.0794 | 123.0011 | 123.1888 | -0.11444 | 123.1384 | 61.0611 | -0.17853 | 123.1888 | -0.11444 | 61.0611 | 123.0011 | 123.1384 | -123.3215 | -123.4177
121.6719 | 123.3994 | -61.0657 | 62.2238 | -0.27385 | -0.0598 | -0.089027 | 0.1048 | -0.021259 | -0.096114 | 0.048883 | -61.1938 | 62.1506 | -61.1526 | -61.1847 | 62.1048 | 0.14648 | -0.07782 | 0.10529 | 62.1048 | -61.1618 | -0.086975 | -0.073242 | -0.12817 | -0.11902 | -0.11902 | -0.09613 | -0.11902 | -0.041199 | 60.9879 | 61.171 | 123.1705 | 123.2162 | -0.12817 | 123.1705 | 61.2122 | -0.09613 | 123.2162 | -0.12817 | 61.2122 | 123.1705 | 123.1705 | -123.3765 | -123.3856
122.7188 | 123.5092 | -61.0382 | 62.178 | -0.090746 | -0.063004 | -0.093299 | 0.088778 | -0.01485 | -0.096114 | 0.060632 | -61.1069 | 62.0865 | -61.1343 | -61.3495 | 61.94 | 0.004578 | 0.07782 | -0.013733 | 62.1277 | -61.2122 | -0.09613 | -0.091553 | -0.068665 | -0.31128 | -0.23804 | -0.17395 | -0.050354 | 0.027465 | 61.116 | 61.0245 | 122.9782 | 123.1247 | -0.068665 | 123.1659 | 61.0428 | -0.17395 | 123.1247 | -0.068665 | 61.0428 | 122.9782 | 123.1659 | -123.3124 | -123.3902
123.6562 | 123.4863 | -61.0107 | 62.1643 | 0.00080561 | -0.0598 | -0.096503 | 0.094119 | -0.027668 | -0.082229 | 0.049951 | -61.1114 | 62.1094 | -61.1343 | -61.3449 | 61.9308 | -0.009155 | 0.073242 | -0.013733 | 62.1414 | -61.2213 | -0.1236 | -0.054932 | -0.10071 | -0.33417 | -0.23346 | -0.21057 | -0.022889 | 0.022888 | 61.084 | 60.997 | 122.9416 | 123.1201 | -0.10071 | 123.1522 | 61.0016 | -0.21057 | 123.1201 | -0.10071 | 61.0016 | 122.9416 | 123.1522 | -123.2986 | -123.3856
124.7188 | 123.5229 | -61.0336 | 62.1735 | -0.12126 | -0.056596 | -0.10612 | 0.089846 | -0.01485 | -0.099318 | 0.044611 | -60.7178 | 62.1368 | -61.1023 | -61.3266 | 61.8851 | -0.027466 | 0.082397 | -0.022888 | 62.1231 | -61.2122 | -0.068665 | -0.036621 | 0.31586 | -0.29297 | -0.28839 | -0.17853 | -0.050354 | 0.38452 | 61.116 | 61.0107 | 122.9187 | 123.1705 | 0.31586 | 123.1567 | 61.0062 | -0.17853 | 123.1705 | 0.31586 | 61.0062 | 122.9187 | 123.1567 | -123.2758 | -123.3856
125.6562 | 123.3994 | -61.0474 | 62.2375 | -0.19756 | -0.066209 | -0.071937 | 0.108 | -0.016986 | -0.073684 | 0.037134 | -61.2259 | 62.1506 | -61.1984 | -61.1435 | 62.0453 | 0.15106 | -0.064087 | 0.13733 | 62.1002 | -61.171 | -0.15106 | -0.086975 | -0.17853 | -0.096131 | -0.19226 | -0.1236 | -0.13733 | -0.027466 | 60.9833 | 61.1847 | 123.0927 | 123.1979 | -0.17853 | 123.1476 | 61.1984 | -0.1236 | 123.1979 | -0.17853 | 61.1984 | 123.0927 | 123.1476 | -123.436 | -123.4085
126.6719 | 123.4726 | -61.0565 | 62.233 | -0.1823 | -0.0598 | -0.080482 | 0.09305 | -0.016986 | -0.09291 | 0.045679 | -61.2076 | 62.146 | -61.171 | -61.2122 | 62.0682 | 0.14648 | -0.064087 | 0.13275 | 62.1048 | -61.1526 | -0.11444 | -0.086975 | -0.15106 | -0.15564 | -0.16479 | -0.09613 | -0.12817 | -0.036622 | 60.9924 | 61.1893 | 123.1247 | 123.2025 | -0.15106 | 123.1613 | 61.203 | -0.09613 | 123.2025 | -0.15106 | 61.203 | 123.1247 | 123.1613 | -123.4039 | -123.3856
127.6719 | 123.4634 | -61.084 | 62.2055 | -0.10601 | -0.056596 | -0.083686 | 0.10159 | -0.015918 | -0.084365 | 0.048883 | -61.1526 | 62.1597 | -61.1664 | -61.2076 | 62.0178 | 0.11444 | -0.022888 | 0.082397 | 62.0865 | -61.1847 | -0.082398 | -0.045776 | -0.068665 | -0.1236 | -0.18768 | -0.10071 | -0.11902 | 0.013733 | 61.0611 | 61.1664 | 123.1018 | 123.2437 | -0.068665 | 123.1705 | 61.1984 | -0.10071 | 123.2437 | -0.068665 | 61.1984 | 123.1018 | 123.1705 | -123.3719 | -123.3902
128.6562 | 123.587 | -61.0794 | 62.1368 | 0.15339 | -0.0598 | -0.11466 | 0.077029 | -0.0084417 | -0.09825 | 0.048883 | -61.1069 | 62.0773 | -61.1343 | -61.3358 | 61.9125 | -0.14191 | 0.07782 | 0.16022 | 62.2055 | -61.1801 | -0.054931 | -0.059509 | -0.027466 | -0.25635 | -0.2243 | -0.10071 | 0.068664 | 0.027465 | 61.1572 | 61.2396 | 122.9919 | 123.1567 | -0.027466 | 123.2849 | 60.9375 | -0.10071 | 123.1567 | -0.027466 | 60.9375 | 122.9919 | 123.2849 | -123.2712 | -123.317
129.6562 | 123.4955 | -61.0336 | 62.178 | 0.16865 | -0.06514 | -0.10398 | 0.080233 | -0.029804 | -0.1068 | 0.046747 | -61.1847 | 62.0911 | -61.1252 | -61.3083 | 61.9629 | 0.022888 | 0.032043 | 0.018311 | 62.114 | -61.203 | -0.091553 | -0.086976 | -0.15106 | -0.27466 | -0.21515 | -0.16937 | -0.064087 | -0.059509 | 61.0657 | 61.0519 | 122.9965 | 123.1247 | -0.15106 | 123.1476 | 61.0565 | -0.16937 | 123.1247 | -0.15106 | 61.0565 | 122.9965 | 123.1476 | -123.3032 | -123.381
130.6719 | 123.4314 | -61.1069 | 62.2238 | -0.24333 | -0.058732 | -0.055915 | 0.11228 | -0.021259 | -0.083297 | 0.043542 | -61.1938 | 62.178 | -61.1572 | -61.1526 | 62.0636 | 0.14648 | -0.073242 | 0.13733 | 62.0911 | -61.1526 | -0.050354 | -0.045776 | -0.086975 | -0.045776 | -0.16022 | -0.045776 | -0.13275 | -0.036621 | 61.0336 | 61.2442 | 123.1705 | 123.2849 | -0.086975 | 123.1979 | 61.2534 | -0.045776 | 123.2849 | -0.086975 | 61.2534 | 123.1705 | 123.1979 | -123.381 | -123.3765
131.6562 | 123.5687 | -61.0291 | 62.1643 | -0.014452 | -0.064072 | -0.097572 | 0.085574 | -0.025531 | -0.088637 | 0.069177 | -61.1343 | 62.0819 | -61.1298 | -61.2991 | 62.2833 | 0.068665 | -0.09613 | -0.091553 | 62.0956 | -61.2259 | -0.10071 | -0.082398 | -0.10529 | -0.27008 | 0.11902 | -0.19684 | -0.068665 | -0.004577 | 60.9329 | 60.9375 | 123.3124 | 123.111 | -0.10529 | 123.1247 | 61.0977 | -0.19684 | 123.111 | -0.10529 | 61.0977 | 123.3124 | 123.1247 | -123.2941 | -123.3902
132.7031 | 123.5046 | -61.0519 | 62.1368 | 0.48909 | -0.055527 | -0.067664 | 0.095187 | -0.020191 | -0.087569 | 0.040338 | -61.3403 | 62.0499 | -61.1481 | -61.3174 | 61.9171 | -0.013733 | 0.07782 | -0.036621 | 62.0819 | -61.2534 | -0.09613 | -0.086975 | -0.28839 | -0.2655 | -0.21973 | -0.20142 | -0.054932 | -0.19226 | 61.1298 | 61.0153 | 122.9691 | 123.1018 | -0.28839 | 123.1338 | 61.0382 | -0.20142 | 123.1018 | -0.28839 | 61.0382 | 122.9691 | 123.1338 | -123.2849 | -123.3902
133.6562 | 123.5046 | -61.0336 | 62.1735 | 0.13813 | -0.0598 | -0.094367 | 0.084505 | -0.027668 | -0.10359 | 0.046747 | -61.1389 | 62.0773 | -61.1206 | -61.322 | 61.94 | 0 | 0.086975 | -0.004578 | 62.114 | -61.2259 | -0.086975 | -0.09613 | -0.10529 | -0.28839 | -0.23346 | -0.19226 | -0.059509 | -0.018311 | 61.1206 | 61.0291 | 122.9736 | 123.111 | -0.10529 | 123.1476 | 61.0336 | -0.19226 | 123.111 | -0.10529 | 61.0336 | 122.9736 | 123.1476 | -123.2941 | -123.3994
134.7188 | 123.5367 | -61.0245 | 62.178 | -0.19756 | -0.056596 | -0.069801 | 0.082369 | -0.021259 | -0.097182 | 0.052087 | -61.1252 | 62.0819 | -61.1298 | -61.4136 | 61.9217 | 0.022888 | 0.13733 | 0.009155 | 62.1277 | -61.2076 | -0.10529 | -0.096131 | -0.10071 | -0.3891 | -0.25635 | -0.18311 | -0.050354 | 0.004578 | 61.1618 | 61.0336 | 122.9462 | 123.1064 | -0.10071 | 123.1522 | 61.0474 | -0.18311 | 123.1064 | -0.10071 | 61.0474 | 122.9462 | 123.1522 | -123.3078 | -123.3856
135.6719 | 123.4726 | -61.0245 | 62.2009 | -0.30437 | -0.064072 | -0.083686 | 0.090914 | -0.027668 | -0.085433 | 0.042474 | -61.1343 | 62.1323 | -61.0886 | -61.2396 | 61.9812 | 0.082397 | 0.018311 | 0.059509 | 62.1048 | -61.1893 | -0.064087 | -0.068665 | -0.10986 | -0.21515 | -0.21973 | -0.16479 | -0.096131 | -0.045776 | 61.0428 | 61.084 | 123.0057 | 123.1567 | -0.10986 | 123.1293 | 61.1069 | -0.16479 | 123.1567 | -0.10986 | 61.1069 | 123.0057 | 123.1293 | -123.2895 | -123.3902
136.6562 | 123.5138 | -61.0428 | 62.1918 | 0.19917 | -0.0598 | -0.10291 | 0.095187 | -0.028736 | -0.10039 | 0.044611 | -61.1984 | 62.0636 | -61.1343 | -61.3037 | 61.9492 | 0.013733 | 0.045776 | 0.013733 | 62.1094 | -61.203 | -0.091552 | -0.12817 | -0.15564 | -0.26093 | -0.24261 | -0.16022 | -0.082397 | -0.064087 | 61.0886 | 61.0565 | 122.9919 | 123.1064 | -0.15564 | 123.1522 | 61.0565 | -0.16022 | 123.1064 | -0.15564 | 61.0565 | 122.9919 | 123.1522 | -123.3261 | -123.3948
137.6562 | 123.5001 | -61.0428 | 62.2009 | 0.15339 | -0.061936 | -0.092231 | 0.08771 | -0.024463 | -0.10039 | 0.041406 | -61.1801 | 62.0819 | -61.1298 | -61.29 | 61.9675 | 0.041199 | 0.027466 | 0.036621 | 62.114 | -61.1984 | -0.086975 | -0.11902 | -0.13733 | -0.24719 | -0.23346 | -0.15564 | -0.086975 | -0.050354 | 61.0703 | 61.0794 | 123.0103 | 123.1247 | -0.13733 | 123.1567 | 61.084 | -0.15564 | 123.1247 | -0.13733 | 61.084 | 123.0103 | 123.1567 | -123.3307 | -123.3994
138.6562 | 123.5001 | -61.0245 | 62.178 | 0.031324 | -0.069413 | -0.066596 | 0.088778 | -0.024463 | -0.10252 | 0.041406 | -61.1526 | 62.0682 | -61.1389 | -61.3083 | 61.9492 | 0.009155 | 0.07782 | -0.013733 | 62.0956 | -61.2122 | -0.11444 | -0.10986 | -0.12817 | -0.28381 | -0.22888 | -0.18768 | -0.082398 | -0.013733 | 61.1023 | 61.0107 | 122.9736 | 123.0927 | -0.12817 | 123.1201 | 61.0336 | -0.18768 | 123.0927 | -0.12817 | 61.0336 | 122.9736 | 123.1201 | -123.317 | -123.3902
139.6562 | 123.4909 | -61.0428 | 62.2009 | 0.046583 | -0.06514 | -0.074073 | 0.099459 | -0.026599 | -0.10039 | 0.044611 | -61.1618 | 62.0728 | -61.1481 | -61.3037 | 61.9537 | 0.027466 | 0.059509 | 0 | 62.1002 | -61.1893 | -0.10529 | -0.12817 | -0.11902 | -0.26093 | -0.24719 | -0.14648 | -0.10071 | -0.013733 | 61.1023 | 61.0428 | 122.9965 | 123.1155 | -0.11902 | 123.143 | 61.0703 | -0.14648 | 123.1155 | -0.11902 | 61.0703 | 122.9965 | 123.143 | -123.349 | -123.3902
140.6719 | 123.4589 | -61.0565 | 62.2101 | -0.060229 | -0.051255 | -0.051643 | 0.11975 | -0.023395 | -0.079024 | 0.042474 | -61.1572 | 62.1826 | -61.1618 | -61.1938 | 62.0819 | 0.086975 | -0.022888 | 0.068665 | 62.0728 | -61.1938 | -0.10528 | -0.027466 | -0.10071 | -0.13733 | -0.12817 | -0.13733 | -0.13733 | 0.004577 | 61.0336 | 61.1252 | 123.1384 | 123.2391 | -0.10071 | 123.1293 | 61.1435 | -0.13733 | 123.2391 | -0.10071 | 61.1435 | 123.1384 | 123.1293 | -123.3719 | -123.4039
141.6562 | 123.4909 | -61.0474 | 62.178 | 0.22969 | -0.069413 | -0.10291 | 0.090914 | -0.027668 | -0.09825 | 0.046747 | -61.1755 | 62.0819 | -61.171 | -61.29 | 61.9629 | 0.022888 | 0.041199 | 0.036621 | 62.1094 | -61.1847 | -0.1236 | -0.096131 | -0.12817 | -0.24262 | -0.21515 | -0.13733 | -0.068665 | -0.004578 | 61.0886 | 61.084 | 123.0103 | 123.1293 | -0.12817 | 123.1567 | 61.0703 | -0.13733 | 123.1293 | -0.12817 | 61.0703 | 123.0103 | 123.1567 | -123.349 | -123.3627
142.6562 | 123.4543 | -61.0474 | 62.1643 | 0.13813 | -0.066209 | -0.1168 | 0.08771 | -0.019123 | -0.10893 | 0.033929 | -61.1984 | 62.0682 | -61.1298 | -61.2534 | 62.0682 | 0.018311 | 0.013733 | 0.07782 | 62.1002 | -61.1938 | -0.082398 | -0.096131 | -0.15106 | -0.20599 | -0.096131 | -0.14649 | -0.064087 | -0.068664 | 61.0611 | 61.1252 | 123.1155 | 123.1155 | -0.15106 | 123.1476 | 61.0657 | -0.14649 | 123.1155 | -0.15106 | 61.0657 | 123.1155 | 123.1476 | -123.2941 | -123.3582
143.6562 | 123.5046 | -61.0382 | 62.1552 | 0.10762 | -0.061936 | -0.074073 | 0.08771 | -0.028736 | -0.093978 | 0.049951 | -61.1801 | 62.0956 | -61.1435 | -61.2717 | 61.9766 | 0.036621 | 0.013733 | 0.032043 | 62.0911 | -61.2076 | -0.10529 | -0.059509 | -0.14191 | -0.23346 | -0.17853 | -0.16937 | -0.064087 | -0.036621 | 61.0519 | 61.0703 | 123.0148 | 123.1338 | -0.14191 | 123.1293 | 61.0748 | -0.16937 | 123.1338 | -0.14191 | 61.0748 | 123.0148 | 123.1293 | -123.2986 | -123.3627
144.7031 | 123.3902 | -61.1069 | 62.2009 | 0.18391 | -0.0598 | -0.085822 | 0.11762 | -0.025531 | -0.085433 | 0.047815 | -61.2076 | 62.1506 | -61.1618 | -61.1252 | 62.059 | 0.10986 | -0.073242 | 0.10986 | 62.059 | -61.203 | -0.054931 | -0.050354 | -0.10071 | -0.01831 | -0.14191 | -0.09613 | -0.14191 | -0.045777 | 61.0336 | 61.2167 | 123.1659 | 123.2574 | -0.10071 | 123.1659 | 61.2167 | -0.09613 | 123.2574 | -0.10071 | 61.2167 | 123.1659 | 123.1659 | -123.3627 | -123.4039
145.6719 | 123.4543 | -61.0611 | 62.1964 | 0.016065 | -0.049119 | -0.065528 | 0.11548 | -0.010578 | -0.071547 | 0.071313 | -61.1435 | 62.1826 | -61.1664 | -61.1664 | 61.9308 | 0.054932 | 0.004578 | 0.036621 | 62.0544 | -61.1755 | -0.10529 | -0.013733 | -0.082398 | -0.10529 | -0.2655 | -0.11444 | -0.14191 | 0.022888 | 61.0657 | 61.0977 | 122.9919 | 123.2437 | -0.082398 | 123.1155 | 61.116 | -0.11444 | 123.2437 | -0.082398 | 61.116 | 122.9919 | 123.1155 | -123.3627 | -123.3719
146.6562 | 123.5138 | -61.0382 | 62.1735 | 0.21443 | -0.068345 | -0.10718 | 0.079165 | -0.012714 | -0.089705 | 0.054224 | -61.2076 | 62.0636 | -61.1435 | -61.3037 | 61.9858 | 0.032043 | 0.036621 | 0.032043 | 62.0956 | -61.1618 | -0.10529 | -0.10986 | -0.16937 | -0.2655 | -0.18768 | -0.1236 | -0.07782 | -0.064087 | 61.0748 | 61.0703 | 123.024 | 123.1018 | -0.16937 | 123.1338 | 61.0703 | -0.1236 | 123.1018 | -0.16937 | 61.0703 | 123.024 | 123.1338 | -123.317 | -123.3353
147.6562 | 123.4909 | -61.0428 | 62.146 | 0.16865 | -0.073685 | -0.10078 | 0.079165 | -0.025531 | -0.09825 | 0.047815 | -61.2122 | 62.0819 | -61.1801 | -61.29 | 61.9766 | 0.022888 | 0.027466 | 0.032043 | 62.0819 | -61.1938 | -0.13733 | -0.064087 | -0.16937 | -0.24719 | -0.16937 | -0.15106 | -0.064087 | -0.032043 | 61.0703 | 61.0748 | 123.0194 | 123.1247 | -0.16937 | 123.1247 | 61.0657 | -0.15106 | 123.1247 | -0.16937 | 61.0657 | 123.0194 | 123.1247 | -123.3261 | -123.3398
148.6719 | 123.555 | -61.0931 | 62.1231 | 0.031324 | -0.064072 | -0.096503 | 0.084505 | -0.023395 | -0.088637 | 0.055292 | -61.0977 | 62.0865 | -61.1481 | -61.3403 | 61.908 | -0.036621 | 0.036621 | 0.23804 | 62.178 | -61.1664 | -0.054931 | -0.036621 | -0.004577 | -0.24719 | -0.21515 | -0.073242 | 0.054932 | 0.050354 | 61.1298 | 61.3312 | 123.0011 | 123.1796 | -0.004577 | 123.2712 | 61.0565 | -0.073242 | 123.1796 | -0.004577 | 61.0565 | 123.0011 | 123.2712 | -123.2712 | -123.2895
149.7188 | 123.4772 | -61.0474 | 62.1872 | 0.8553 | -0.064072 | -0.087958 | 0.089846 | -0.021259 | -0.089705 | 0.054224 | -61.203 | 62.0819 | -61.1298 | -61.2762 | 61.972 | 0.059509 | 0.027466 | 0.068665 | 62.0636 | -61.1893 | -0.082398 | -0.10529 | -0.15564 | -0.22888 | -0.21515 | -0.14191 | -0.1236 | -0.073242 | 61.0748 | 61.116 | 123.0194 | 123.1293 | -0.15564 | 123.111 | 61.1069 | -0.14191 | 123.1293 | -0.15564 | 61.1069 | 123.0194 | 123.111 | -123.317 | -123.3765
150.6562 | 123.468 | -61.0657 | 62.1323 | 0.26021 | -0.068345 | -0.10078 | 0.10053 | -0.033008 | -0.095046 | 0.049951 | -61.203 | 62.0773 | -61.1481 | -61.3403 | 62.027 | 0.032043 | 0.004578 | 0.036621 | 62.0819 | -61.1893 | -0.082397 | -0.054931 | -0.13733 | -0.27466 | -0.10529 | -0.1236 | -0.050354 | -0.054932 | 61.0703 | 61.1023 | 123.0927 | 123.143 | -0.13733 | 123.1476 | 61.0977 | -0.1236 | 123.143 | -0.13733 | 61.0977 | 123.0927 | 123.1476 | -123.2803 | -123.3215
151.7031 | 123.4131 | -61.0886 | 62.1964 | -0.80791 | -0.037369 | -0.06446 | 0.11762 | -0.024463 | -0.084365 | 0.030725 | -61.2671 | 62.1689 | -61.1618 | -61.1389 | 62.0499 | 0.14191 | -0.091553 | 0.12817 | 62.0178 | -61.1801 | -0.073242 | -0.027466 | -0.17853 | -0.050354 | -0.14648 | -0.091553 | -0.17853 | -0.10529 | 60.997 | 61.2167 | 123.1384 | 123.2574 | -0.17853 | 123.1064 | 61.2305 | -0.091553 | 123.2574 | -0.17853 | 61.2305 | 123.1384 | 123.1064 | -123.3582 | -123.3765
152.6562 | 123.4726 | -61.0794 | 62.1552 | 0.26021 | -0.066209 | -0.090095 | 0.082369 | -0.010578 | -0.10039 | 0.048883 | -61.2259 | 62.059 | -61.171 | -61.2717 | 61.9904 | 0.027466 | 0.027466 | 0.045776 | 62.1185 | -61.1755 | -0.091552 | -0.09613 | -0.14648 | -0.19226 | -0.16479 | -0.09613 | -0.036621 | -0.054932 | 61.1069 | 61.1252 | 123.0698 | 123.1384 | -0.14648 | 123.1979 | 61.1069 | -0.09613 | 123.1384 | -0.14648 | 61.1069 | 123.0698 | 123.1979 | -123.3261 | -123.3307
153.7031 | 123.381 | -61.084 | 62.1735 | 0.39753 | -0.044846 | -0.061256 | 0.11334 | -0.01485 | -0.079024 | 0.049951 | -61.2076 | 62.1597 | -61.1481 | -61.1435 | 62.0728 | 0.10529 | -0.082397 | 0.13275 | 62.0316 | -61.1847 | -0.064087 | -0.013733 | -0.1236 | -0.05951 | -0.10071 | -0.10071 | -0.14191 | -0.05951 | 61.0016 | 61.2167 | 123.1567 | 123.2437 | -0.1236 | 123.1155 | 61.1893 | -0.10071 | 123.2437 | -0.1236 | 61.1893 | 123.1567 | 123.1155 | -123.3215 | -123.3582
154.6562 | 123.4543 | -61.0474 | 62.1597 | 0.30598 | -0.06514 | -0.11039 | 0.078097 | -0.025531 | -0.096114 | 0.047815 | -61.1984 | 62.0682 | -61.1435 | -61.235 | 62.0773 | 0.045776 | 0.013733 | 0.064087 | 62.1094 | -61.1801 | -0.096131 | -0.091553 | -0.15106 | -0.18768 | -0.082397 | -0.13275 | -0.050354 | -0.054931 | 61.0611 | 61.1114 | 123.1247 | 123.1155 | -0.15106 | 123.1567 | 61.0931 | -0.13275 | 123.1155 | -0.15106 | 61.0931 | 123.1247 | 123.1567 | -123.3032 | -123.3398
155.6562 | 123.4818 | -61.0611 | 62.1277 | 0.5196 | -0.061936 | -0.10825 | 0.095187 | -0.023395 | -0.093978 | 0.045679 | -61.1572 | 62.0682 | -61.1572 | -61.3266 | 61.9354 | -0.009155 | 0.054932 | 0.013733 | 62.0956 | -61.203 | -0.096131 | -0.05951 | -0.096131 | -0.2655 | -0.19226 | -0.14191 | -0.032044 | 0 | 61.116 | 61.0748 | 122.9965 | 123.1293 | -0.096131 | 123.1567 | 61.0519 | -0.14191 | 123.1293 | -0.096131 | 61.0519 | 122.9965 | 123.1567 | -123.2849 | -123.3307
156.7031 | 123.3765 | -61.0748 | 62.1918 | 0.21443 | -0.050187 | -0.097572 | 0.11548 | -0.01485 | -0.072616 | 0.045679 | -61.1984 | 62.1826 | -61.1435 | -61.1343 | 62.0499 | 0.1236 | -0.091553 | 0.11902 | 62.0499 | -61.1618 | -0.068665 | -0.009155 | -0.1236 | -0.059509 | -0.14191 | -0.086975 | -0.14191 | -0.054931 | 60.9833 | 61.1938 | 123.1247 | 123.2574 | -0.1236 | 123.1247 | 61.1984 | -0.086975 | 123.2574 | -0.1236 | 61.1984 | 123.1247 | 123.1247 | -123.3353 | -123.3536
157.6562 | 123.4818 | -61.0336 | 62.1506 | 0.47383 | -0.064072 | -0.075141 | 0.089846 | -0.019123 | -0.096114 | 0.051019 | -61.1893 | 62.0956 | -61.1572 | -61.3083 | 61.972 | 0.027466 | 0.041199 | 0.032043 | 62.1048 | -61.2076 | -0.1236 | -0.054932 | -0.15564 | -0.27466 | -0.17853 | -0.17395 | -0.045777 | -0.032043 | 61.0748 | 61.0657 | 123.0057 | 123.1293 | -0.15564 | 123.1384 | 61.0611 | -0.17395 | 123.1293 | -0.15564 | 61.0611 | 123.0057 | 123.1384 | -123.3078 | -123.3582
158.7031 | 123.4497 | -61.0931 | 62.1643 | 0.45857 | -0.035233 | -0.078345 | 0.11121 | -0.019123 | -0.084365 | 0.047815 | -61.2122 | 62.1689 | -61.1847 | -61.1984 | 62.0728 | 0.068665 | -0.059509 | 0.086975 | 62.0178 | -61.203 | -0.091552 | 0.004577 | -0.11902 | -0.10529 | -0.091553 | -0.10986 | -0.14648 | -0.027466 | 61.0336 | 61.1801 | 123.1659 | 123.262 | -0.11902 | 123.111 | 61.1618 | -0.10986 | 123.262 | -0.11902 | 61.1618 | 123.1659 | 123.111 | -123.349 | -123.3673
159.6562 | 123.4818 | -61.0474 | 62.1689 | 0.41279 | -0.056596 | -0.08689 | 0.099459 | -0.016986 | -0.099318 | 0.045679 | -61.1893 | 62.0865 | -61.1618 | -61.2946 | 61.9675 | 0.027466 | 0.009155 | 0.045776 | 62.0956 | -61.1984 | -0.11444 | -0.082397 | -0.14191 | -0.24719 | -0.20142 | -0.15106 | -0.073242 | -0.027466 | 61.0565 | 61.0931 | 123.0148 | 123.1338 | -0.14191 | 123.143 | 61.0748 | -0.15106 | 123.1338 | -0.14191 | 61.0748 | 123.0148 | 123.143 | -123.3307 | -123.3673
160.6562 | 123.5046 | -61.0474 | 62.1414 | 0.5196 | -0.068345 | -0.071937 | 0.094119 | -0.016986 | -0.09825 | 0.053156 | -61.1618 | 62.0636 | -61.1526 | -61.2991 | 61.9766 | 0.018311 | 0.045776 | 0.018311 | 62.0911 | -61.2167 | -0.10529 | -0.077819 | -0.11444 | -0.25177 | -0.16479 | -0.16937 | -0.050354 | -0.009155 | 61.0931 | 61.0657 | 123.024 | 123.111 | -0.11444 | 123.1384 | 61.0657 | -0.16937 | 123.111 | -0.11444 | 61.0657 | 123.024 | 123.1384 | -123.2941 | -123.3582
161.6562 | 123.4634 | -61.0428 | 62.146 | 0.42805 | -0.06514 | -0.095435 | 0.10266 | -0.020191 | -0.088637 | 0.03927 | -61.1343 | 62.0682 | -61.1435 | -61.3266 | 61.9308 | 0 | 0.064087 | 0 | 62.0956 | -61.2305 | -0.10071 | -0.07782 | -0.091552 | -0.28381 | -0.21515 | -0.18768 | -0.050354 | 0.009156 | 61.1069 | 61.0428 | 122.9736 | 123.111 | -0.091552 | 123.1384 | 61.0428 | -0.18768 | 123.111 | -0.091552 | 61.0428 | 122.9736 | 123.1384 | -123.2895 | -123.3765
162.6562 | 123.5184 | -61.0519 | 62.1506 | 0.50435 | -0.055527 | -0.079414 | 0.10053 | -0.027668 | -0.089705 | 0.055292 | -61.1343 | 62.0773 | -61.1572 | -61.4319 | 61.7111 | -0.073242 | 0.16022 | 0.064087 | 62.0956 | -61.1984 | -0.10529 | -0.073242 | -0.082397 | -0.37994 | -0.43945 | -0.14648 | -0.054932 | 0.022889 | 61.2122 | 61.116 | 122.7631 | 123.1293 | -0.082397 | 123.1476 | 60.9787 | -0.14648 | 123.1293 | -0.082397 | 60.9787 | 122.7631 | 123.1476 | -123.3078 | -123.349
163.6562 | 123.5092 | -61.0336 | 62.1231 | 0.24495 | -0.055527 | -0.066596 | 0.097323 | -0.021259 | -0.086501 | 0.040338 | -61.1847 | 62.1094 | -61.1435 | -61.3083 | 61.9308 | -0.013733 | 0.073242 | 0 | 62.0911 | -61.1893 | -0.10986 | -0.013733 | -0.15106 | -0.27466 | -0.19226 | -0.15564 | -0.032044 | -0.041198 | 61.1069 | 61.0336 | 122.9645 | 123.143 | -0.15106 | 123.1247 | 61.0199 | -0.15564 | 123.143 | -0.15106 | 61.0199 | 122.9645 | 123.1247 | -123.2666 | -123.3124
164.7188 | 123.5229 | -61.0428 | 62.146 | -0.92998 | -0.061936 | -0.095435 | 0.08771 | -0.012714 | -0.085433 | 0.052087 | -61.1298 | 62.0865 | -61.1252 | -61.3541 | 61.9217 | -0.045776 | 0.086975 | -0.013733 | 62.1048 | -61.2167 | -0.082397 | -0.059509 | -0.086975 | -0.31128 | -0.2243 | -0.17395 | -0.041199 | -0.004578 | 61.1298 | 61.0291 | 122.9645 | 123.1293 | -0.086975 | 123.1476 | 60.997 | -0.17395 | 123.1293 | -0.086975 | 60.997 | 122.9645 | 123.1476 | -123.2712 | -123.3627
165.6562 | 123.5092 | -61.0199 | 62.1414 | 0.53486 | -0.055527 | -0.091163 | 0.098391 | -0.016986 | -0.072616 | 0.043542 | -61.1343 | 62.1094 | -61.1389 | -61.3312 | 62.0956 | 0.022888 | 0.050354 | -0.036621 | 62.1277 | -61.2213 | -0.11902 | -0.032043 | -0.11444 | -0.31128 | -0.045776 | -0.20142 | -0.013732 | 0.004578 | 61.0703 | 60.9833 | 123.1155 | 123.1293 | -0.11444 | 123.1476 | 61.0428 | -0.20142 | 123.1293 | -0.11444 | 61.0428 | 123.1155 | 123.1476 | -123.2803 | -123.3627
166.6562 | 123.5458 | -61.0428 | 62.1552 | 0.48909 | -0.06514 | -0.071937 | 0.10159 | -0.026599 | -0.085433 | 0.049951 | -61.1389 | 62.0911 | -61.1435 | -61.3403 | 61.9308 | -0.036621 | 0.064087 | -0.022888 | 62.0865 | -61.2122 | -0.10071 | -0.064087 | -0.09613 | -0.29755 | -0.2243 | -0.16937 | -0.068664 | 0.004578 | 61.1069 | 61.0199 | 122.9736 | 123.1338 | -0.09613 | 123.1293 | 61.0062 | -0.16937 | 123.1338 | -0.09613 | 61.0062 | 122.9736 | 123.1293 | -123.2986 | -123.3673
167.7031 | 123.4543 | -61.0657 | 62.1689 | 0.016065 | -0.050187 | -0.059119 | 0.11014 | -0.01485 | -0.07582 | 0.034998 | -61.1572 | 62.1872 | -61.1389 | -61.2488 | 61.9766 | 0.091553 | -0.059509 | 0.09613 | 62.0682 | -61.1938 | -0.073242 | 0.018311 | -0.091553 | -0.1831 | -0.19226 | -0.12817 | -0.10071 | -0.018311 | 61.0062 | 61.1618 | 123.0423 | 123.2529 | -0.091553 | 123.1338 | 61.1572 | -0.12817 | 123.2529 | -0.091553 | 61.1572 | 123.0423 | 123.1338 | -123.3078 | -123.3627
168.6562 | 123.5184 | -61.0519 | 62.1277 | 0.50435 | -0.068345 | -0.08689 | 0.083437 | -0.024463 | -0.09291 | 0.048883 | -61.1847 | 62.0773 | -61.1618 | -61.3586 | 61.9354 | -0.022888 | 0.091553 | -0.032043 | 62.0956 | -61.2259 | -0.10986 | -0.050354 | -0.13275 | -0.3067 | -0.19226 | -0.17395 | -0.032044 | -0.022888 | 61.1435 | 61.0199 | 122.9874 | 123.1293 | -0.13275 | 123.1476 | 61.0291 | -0.17395 | 123.1293 | -0.13275 | 61.0291 | 122.9874 | 123.1476 | -123.2895 | -123.3536
169.7031 | 123.3627 | -61.1114 | 62.1964 | 0.42805 | -0.045914 | -0.067664 | 0.10266 | -0.013782 | -0.071547 | 0.051019 | -61.2259 | 62.2238 | -61.1755 | -61.1389 | 62.0773 | 0.13733 | -0.10986 | 0.15564 | 62.0178 | -61.1801 | -0.064087 | 0.027466 | -0.11444 | -0.027466 | -0.11902 | -0.068665 | -0.17853 | -0.050354 | 61.0016 | 61.2671 | 123.1888 | 123.3353 | -0.11444 | 123.1293 | 61.2488 | -0.068665 | 123.3353 | -0.11444 | 61.2488 | 123.1888 | 123.1293 | -123.3719 | -123.3765
170.6562 | 123.4406 | -61.0931 | 62.1918 | 0.55012 | -0.046983 | -0.074073 | 0.10053 | -0.013782 | -0.087569 | 0.047815 | -61.2259 | 62.1552 | -61.1893 | -61.1938 | 62.0499 | 0.073242 | -0.027466 | 0.082397 | 62.0453 | -61.1755 | -0.09613 | -0.036621 | -0.13275 | -0.10071 | -0.14191 | -0.082397 | -0.14648 | -0.036621 | 61.0657 | 61.1755 | 123.143 | 123.2483 | -0.13275 | 123.1384 | 61.1664 | -0.082397 | 123.2483 | -0.13275 | 61.1664 | 123.143 | 123.1384 | -123.381 | -123.3673
171.7031 | 123.4131 | -61.084 | 62.1826 | 0.00080561 | -0.045914 | -0.10505 | 0.10907 | -0.016986 | -0.076888 | 0.040338 | -61.1526 | 62.2009 | -61.1572 | -61.1938 | 62.0316 | 0.10071 | -0.027466 | 0.09613 | 62.0728 | -61.1893 | -0.073243 | 0.018311 | -0.068665 | -0.10986 | -0.15106 | -0.10529 | -0.10986 | 0.004578 | 61.0565 | 61.1801 | 123.1155 | 123.2849 | -0.068665 | 123.1567 | 61.1847 | -0.10529 | 123.2849 | -0.068665 | 61.1847 | 123.1155 | 123.1567 | -123.3398 | -123.3719
172.6562 | 123.4039 | -61.0886 | 62.1643 | 0.29072 | -0.039506 | -0.059119 | 0.11014 | -0.0063047 | -0.072616 | 0.055292 | -61.2259 | 62.1872 | -61.1938 | -61.1618 | 62.0865 | 0.11902 | -0.082397 | 0.14191 | 62.0544 | -61.1893 | -0.10529 | 0.022888 | -0.13733 | -0.073242 | -0.07782 | -0.10071 | -0.10986 | -0.032043 | 61.0062 | 61.2305 | 123.175 | 123.2758 | -0.13733 | 123.143 | 61.2076 | -0.10071 | 123.2758 | -0.13733 | 61.2076 | 123.175 | 123.143 | -123.3582 | -123.3536
173.6562 | 123.436 | -61.084 | 62.1918 | 0.53486 | -0.050187 | -0.075141 | 0.098391 | -0.013782 | -0.068343 | 0.048883 | -61.235 | 62.1735 | -61.1755 | -61.2122 | 62.059 | 0.091553 | -0.068665 | 0.091553 | 62.0636 | -61.1984 | -0.091553 | -0.01831 | -0.15106 | -0.12817 | -0.13275 | -0.11444 | -0.12817 | -0.059509 | 61.0153 | 61.1755 | 123.143 | 123.2574 | -0.15106 | 123.1476 | 61.1755 | -0.11444 | 123.2574 | -0.15106 | 61.1755 | 123.143 | 123.1476 | -123.3673 | -123.3902
174.6562 | 123.4177 | -61.084 | 62.1643 | 0.47383 | -0.051255 | -0.079414 | 0.090914 | -0.0095097 | -0.079024 | 0.042474 | -61.2259 | 62.1735 | -61.1801 | -61.1847 | 62.0773 | 0.1236 | -0.073242 | 0.1236 | 62.0407 | -61.1893 | -0.096131 | 0.009155 | -0.14191 | -0.10071 | -0.086975 | -0.10529 | -0.1236 | -0.045776 | 61.0107 | 61.2076 | 123.1613 | 123.2574 | -0.14191 | 123.1247 | 61.2076 | -0.10529 | 123.2574 | -0.14191 | 61.2076 | 123.1613 | 123.1247 | -123.3444 | -123.3536
175.7188 | 123.4497 | -61.0748 | 62.1872 | 0.44331 | -0.046983 | -0.094367 | 0.10266 | -0.0052367 | -0.072616 | 0.052087 | -61.2213 | 62.1735 | -61.1984 | -61.2396 | 62.0361 | 0.064087 | -0.027466 | 0.07782 | 62.0544 | -61.2122 | -0.1236 | -0.013733 | -0.14648 | -0.16479 | -0.15106 | -0.13733 | -0.13275 | -0.022888 | 61.0474 | 61.1526 | 123.111 | 123.2483 | -0.14648 | 123.1293 | 61.1389 | -0.13733 | 123.2483 | -0.14648 | 61.1389 | 123.111 | 123.1293 | -123.3856 | -123.3994
176.6562 | 123.4039 | -61.0977 | 62.1872 | 0.19917 | -0.046983 | -0.090095 | 0.11121 | -0.0063047 | -0.061934 | 0.049951 | -61.203 | 62.2009 | -61.1847 | -61.171 | 62.059 | 0.13733 | -0.082397 | 0.15564 | 62.0682 | -61.171 | -0.086975 | 0.013733 | -0.10529 | -0.073242 | -0.12817 | -0.073242 | -0.11902 | -0.018311 | 61.0153 | 61.2534 | 123.1567 | 123.2986 | -0.10529 | 123.1659 | 61.235 | -0.073242 | 123.2986 | -0.10529 | 61.235 | 123.1567 | 123.1659 | -123.3719 | -123.3582
177.6562 | 123.4131 | -61.0794 | 62.1918 | 0.10762 | -0.045914 | -0.079414 | 0.108 | -0.0063047 | -0.070479 | 0.051019 | -61.1664 | 62.1872 | -61.171 | -61.203 | 62.0499 | 0.13733 | -0.041199 | 0.13275 | 62.0911 | -61.1755 | -0.091552 | -0.004577 | -0.086975 | -0.1236 | -0.14191 | -0.09613 | -0.10071 | 0.004577 | 61.0382 | 61.2122 | 123.1293 | 123.2666 | -0.086975 | 123.1705 | 61.2167 | -0.09613 | 123.2666 | -0.086975 | 61.2167 | 123.1293 | 123.1705 | -123.3627 | -123.3673
178.7031 | 123.4314 | -61.0611 | 62.2055 | -0.1823 | -0.039506 | -0.08689 | 0.09305 | -0.0052367 | -0.083297 | 0.059564 | -61.1526 | 62.2101 | -61.1435 | -61.2122 | 62.0361 | 0.11444 | -0.022888 | 0.10071 | 62.0819 | -61.1755 | -0.082398 | 0.004578 | -0.091553 | -0.15106 | -0.16937 | -0.11444 | -0.1236 | -0.009155 | 61.0382 | 61.1618 | 123.0972 | 123.2712 | -0.091553 | 123.143 | 61.1755 | -0.11444 | 123.2712 | -0.091553 | 61.1755 | 123.0972 | 123.143 | -123.349 | -123.381
179.6562 | 123.3856 | -61.0748 | 62.1643 | 0.44331 | -0.048051 | -0.090095 | 0.10587 | -0.0063047 | -0.068343 | 0.049951 | -61.1893 | 62.1964 | -61.1664 | -61.1755 | 62.0773 | 0.13733 | -0.082397 | 0.13275 | 62.0499 | -61.1938 | -0.091553 | 0.032043 | -0.11444 | -0.10071 | -0.086975 | -0.11902 | -0.11444 | -0.022888 | 60.9924 | 61.2076 | 123.1522 | 123.2712 | -0.11444 | 123.1247 | 61.2122 | -0.11902 | 123.2712 | -0.11444 | 61.2122 | 123.1522 | 123.1247 | -123.3307 | -123.3582
180.6562 | 123.3948 | -61.0977 | 62.2009 | 0.22969 | -0.046983 | -0.083686 | 0.1048 | -0.013782 | -0.069411 | 0.045679 | -61.203 | 62.1964 | -61.1847 | -61.1618 | 62.0682 | 0.13733 | -0.10529 | 0.14648 | 62.0819 | -61.2076 | -0.086975 | -0.004578 | -0.10529 | -0.064087 | -0.13275 | -0.10986 | -0.11902 | -0.018311 | 60.9924 | 61.2442 | 123.1659 | 123.2941 | -0.10529 | 123.1796 | 61.235 | -0.10986 | 123.2941 | -0.10529 | 61.235 | 123.1659 | 123.1796 | -123.3856 | -123.4085
181.6562 | 123.3536 | -61.1114 | 62.1826 | 0.22969 | -0.041642 | -0.10825 | 0.094119 | -0.0052367 | -0.068343 | 0.047815 | -61.1893 | 62.1918 | -61.171 | -61.171 | 62.1002 | 0.14648 | -0.091553 | 0.14648 | 62.0773 | -61.203 | -0.059509 | 0.009155 | -0.07782 | -0.059509 | -0.082397 | -0.091553 | -0.10529 | -0.018311 | 61.0199 | 61.2579 | 123.2117 | 123.3032 | -0.07782 | 123.1888 | 61.2579 | -0.091553 | 123.3032 | -0.07782 | 61.2579 | 123.2117 | 123.1888 | -123.3536 | -123.3856
182.6562 | 123.3902 | -61.1114 | 62.2147 | 0.22969 | -0.045914 | -0.079414 | 0.095187 | -0.0095097 | -0.071547 | 0.041406 | -61.1755 | 62.1872 | -61.1801 | -61.1984 | 62.0499 | 0.10529 | -0.086975 | 0.12817 | 62.0728 | -61.1893 | -0.068665 | -0.027466 | -0.064087 | -0.086975 | -0.16479 | -0.07782 | -0.14191 | 0.004578 | 61.0245 | 61.2396 | 123.1613 | 123.2986 | -0.064087 | 123.1842 | 61.2167 | -0.07782 | 123.2986 | -0.064087 | 61.2167 | 123.1613 | 123.1842 | -123.3948 | -123.4039
183.7188 | 123.4131 | -61.0703 | 62.178 | 0.0771 | -0.036301 | -0.079414 | 0.108 | 0.0033083 | -0.069411 | 0.052087 | -61.1801 | 62.1826 | -61.1572 | -61.1938 | 62.0453 | 0.1236 | -0.059509 | 0.10071 | 62.0728 | -61.1938 | -0.086976 | 0.004577 | -0.10986 | -0.1236 | -0.13275 | -0.1236 | -0.10529 | -0.022888 | 61.0107 | 61.171 | 123.1155 | 123.2529 | -0.10986 | 123.143 | 61.1938 | -0.1236 | 123.2529 | -0.10986 | 61.1938 | 123.1155 | 123.143 | -123.3353 | -123.3719
184.6562 | 123.468 | -61.0931 | 62.2009 | -0.090746 | -0.044846 | -0.096503 | 0.091982 | -0.012714 | -0.068343 | 0.046747 | -61.1526 | 62.2101 | -61.1755 | -61.2213 | 62.0132 | 0.10071 | 0.022888 | 0.073242 | 62.0956 | -61.2213 | -0.082397 | 0.009155 | -0.059509 | -0.12817 | -0.18768 | -0.12817 | -0.10529 | 0.022888 | 61.116 | 61.1664 | 123.1064 | 123.3032 | -0.059509 | 123.1888 | 61.1938 | -0.12817 | 123.3032 | -0.059509 | 61.1938 | 123.1064 | 123.1888 | -123.3765 | -123.4222
185.6562 | 123.4406 | -61.0611 | 62.1552 | -0.21282 | -0.040574 | -0.077277 | 0.091982 | -0.0073727 | -0.079024 | 0.042474 | -61.1572 | 62.1872 | -61.1618 | -61.2396 | 62.0041 | 0.082397 | 0 | 0.07782 | 62.1185 | -61.1893 | -0.10071 | 0.032044 | -0.096131 | -0.17853 | -0.15106 | -0.12817 | -0.036621 | 0.004577 | 61.0611 | 61.1389 | 123.0652 | 123.2483 | -0.096131 | 123.1796 | 61.1435 | -0.12817 | 123.2483 | -0.096131 | 61.1435 | 123.0652 | 123.1796 | -123.317 | -123.3444
186.7188 | 123.4451 | -61.0611 | 62.1735 | 0.0771 | -0.054459 | -0.069801 | 0.095187 | -0.0073727 | -0.069411 | 0.042474 | -61.2167 | 62.1964 | -61.1572 | -61.2488 | 61.9904 | 0.10529 | 0.009155 | 0.086975 | 62.1231 | -61.1984 | -0.096131 | 0.022888 | -0.15564 | -0.18768 | -0.18311 | -0.13733 | -0.050354 | -0.059509 | 61.0703 | 61.1481 | 123.0515 | 123.2574 | -0.15564 | 123.1842 | 61.1664 | -0.13733 | 123.2574 | -0.15564 | 61.1664 | 123.0515 | 123.1842 | -123.3307 | -123.3719
187.6562 | 123.4314 | -61.084 | 62.2009 | 0.016065 | -0.048051 | -0.095435 | 0.099459 | -0.0073727 | -0.070479 | 0.045679 | -61.1526 | 62.1964 | -61.1481 | -61.235 | 62.0224 | 0.10986 | -0.018311 | 0.10071 | 62.114 | -61.2167 | -0.064087 | -0.004578 | -0.068665 | -0.15106 | -0.17853 | -0.13275 | -0.086975 | -0.004578 | 61.0657 | 61.1847 | 123.1064 | 123.2803 | -0.068665 | 123.1979 | 61.1938 | -0.13275 | 123.2803 | -0.068665 | 61.1938 | 123.1064 | 123.1979 | -123.349 | -123.4177
188.6562 | 123.4314 | -61.0703 | 62.1689 | 0.13813 | -0.050187 | -0.091163 | 0.10159 | -0.0052367 | -0.070479 | 0.048883 | -61.1343 | 62.2147 | -61.1389 | -61.2305 | 62.0087 | 0.082397 | -0.013733 | 0.09613 | 62.1002 | -61.1938 | -0.068665 | 0.045777 | -0.064087 | -0.16022 | -0.16022 | -0.1236 | -0.068664 | 0.004578 | 61.0565 | 61.1664 | 123.0789 | 123.2849 | -0.064087 | 123.1705 | 61.1526 | -0.1236 | 123.2849 | -0.064087 | 61.1526 | 123.0789 | 123.1705 | -123.3078 | -123.3627
189.7031 | 123.3673 | -61.0107 | 62.1506 | -0.1823 | -0.066209 | -0.10078 | 0.065279 | -0.0084417 | -0.087569 | 0.051019 | -61.1023 | 62.0773 | -61.1526 | -61.3907 | 61.9171 | -0.009155 | 0.091553 | -0.07782 | 62.1689 | -61.1893 | -0.14191 | -0.073242 | -0.091553 | -0.37994 | -0.23346 | -0.17853 | 0.01831 | 0.050354 | 61.1023 | 60.9329 | 122.9279 | 123.0881 | -0.091553 | 123.1796 | 61.0016 | -0.17853 | 123.0881 | -0.091553 | 61.0016 | 122.9279 | 123.1796 | -123.3032 | -123.3398
190.6562 | 123.4589 | -61.0474 | 62.2192 | -0.16704 | -0.049119 | -0.11039 | 0.095187 | -0.0052367 | -0.068343 | 0.048883 | -61.1893 | 62.2055 | -61.1435 | -61.1984 | 62.0132 | 0.11902 | -0.036621 | 0.1236 | 62.1094 | -61.1893 | -0.096131 | -0.013733 | -0.14191 | -0.15106 | -0.20599 | -0.14191 | -0.10986 | -0.045776 | 61.0107 | 61.171 | 123.0606 | 123.2529 | -0.14191 | 123.1567 | 61.1664 | -0.14191 | 123.2529 | -0.14191 | 61.1664 | 123.0606 | 123.1567 | -123.3627 | -123.4085
191.7188 | 123.4268 | -61.0748 | 62.2101 | -0.10601 | -0.057664 | -0.10612 | 0.096255 | -0.016986 | -0.083297 | 0.041406 | -61.1801 | 62.2009 | -61.1618 | -61.1755 | 62.0728 | 0.15106 | -0.064087 | 0.13275 | 62.1048 | -61.1847 | -0.086975 | -0.009155 | -0.10529 | -0.10071 | -0.13733 | -0.10986 | -0.10529 | -0.018311 | 61.0107 | 61.2076 | 123.1476 | 123.2758 | -0.10529 | 123.1796 | 61.2259 | -0.10986 | 123.2758 | -0.10529 | 61.2259 | 123.1476 | 123.1796 | -123.3719 | -123.3948
192.6562 | 123.4314 | -61.0794 | 62.2147 | -0.15178 | -0.054459 | -0.099708 | 0.1048 | -0.0095097 | -0.072616 | 0.05636 | -61.1664 | 62.178 | -61.1526 | -61.2213 | 62.0178 | 0.10071 | -0.036621 | 0.09613 | 62.1185 | -61.1847 | -0.073242 | -0.036621 | -0.086975 | -0.14191 | -0.19684 | -0.10528 | -0.096131 | -0.013733 | 61.0428 | 61.1755 | 123.0972 | 123.2574 | -0.086975 | 123.1979 | 61.1801 | -0.10528 | 123.2574 | -0.086975 | 61.1801 | 123.0972 | 123.1979 | -123.3673 | -123.3994
193.6562 | 123.4543 | -61.0931 | 62.2147 | -0.075488 | -0.046983 | -0.091163 | 0.10159 | -0.0073727 | -0.069411 | 0.049951 | -61.1389 | 62.1826 | -61.171 | -61.2167 | 62.0224 | 0.09613 | -0.027466 | 0.10986 | 62.1094 | -61.2167 | -0.077819 | -0.032044 | -0.045776 | -0.1236 | -0.19226 | -0.1236 | -0.10529 | 0.032043 | 61.0657 | 61.203 | 123.1155 | 123.2758 | -0.045776 | 123.2025 | 61.1893 | -0.1236 | 123.2758 | -0.045776 | 61.1893 | 123.1155 | 123.2025 | -123.3856 | -123.4314
194.6562 | 123.4314 | -61.0474 | 62.2055 | -0.15178 | -0.050187 | -0.067664 | 0.089846 | -0.018055 | -0.073684 | 0.042474 | -61.1435 | 62.1964 | -61.1755 | -61.2122 | 62.0224 | 0.10529 | -0.032043 | 0.082397 | 62.1368 | -61.1893 | -0.12817 | -0.009155 | -0.096131 | -0.1648 | -0.18311 | -0.14191 | -0.068664 | 0.032043 | 61.0153 | 61.1298 | 123.0698 | 123.2437 | -0.096131 | 123.1842 | 61.1526 | -0.14191 | 123.2437 | -0.096131 | 61.1526 | 123.0698 | 123.1842 | -123.381 | -123.3948
195.7031 | 123.4589 | -61.0428 | 62.2009 | -0.31963 | -0.056596 | -0.10078 | 0.069552 | -0.011646 | -0.090773 | 0.057428 | -61.1526 | 62.1002 | -61.1664 | -61.2717 | 61.972 | 0.064087 | 0.018311 | 0.07782 | 62.178 | -61.2259 | -0.1236 | -0.10071 | -0.10986 | -0.22888 | -0.22888 | -0.1831 | -0.022888 | 0.013733 | 61.0611 | 61.1206 | 123.0148 | 123.143 | -0.10986 | 123.2208 | 61.1069 | -0.1831 | 123.143 | -0.10986 | 61.1069 | 123.0148 | 123.2208 | -123.3673 | -123.4268
196.6562 | 123.4131 | -61.0886 | 62.2192 | -0.21282 | -0.04271 | -0.10398 | 0.096255 | -0.0095097 | -0.08116 | 0.055292 | -61.1847 | 62.2147 | -61.1801 | -61.1893 | 62.0361 | 0.14191 | -0.064087 | 0.14648 | 62.1368 | -61.1847 | -0.091553 | -0.004577 | -0.09613 | -0.10071 | -0.1831 | -0.09613 | -0.082397 | -0.004577 | 61.0245 | 61.235 | 123.1247 | 123.3032 | -0.09613 | 123.2254 | 61.2305 | -0.09613 | 123.3032 | -0.09613 | 61.2305 | 123.1247 | 123.2254 | -123.3994 | -123.4039
197.6562 | 123.4177 | -61.1069 | 62.2009 | -0.25859 | -0.055527 | -0.094367 | 0.096255 | -0.020191 | -0.07582 | 0.049951 | -61.2167 | 62.1872 | -61.171 | -61.1572 | 61.9034 | 0.059509 | -0.07782 | 0.15564 | 62.1002 | -61.1755 | -0.064086 | -0.013733 | -0.10986 | -0.050354 | -0.29755 | -0.068664 | -0.10071 | -0.045777 | 61.0291 | 61.2625 | 123.0103 | 123.2941 | -0.10986 | 123.2071 | 61.1664 | -0.068664 | 123.2941 | -0.10986 | 61.1664 | 123.0103 | 123.2071 | -123.3719 | -123.3765
198.7188 | 123.3765 | -61.0748 | 62.2467 | -0.04497 | -0.057664 | -0.10078 | 0.098391 | -0.015918 | -0.077956 | 0.046747 | -61.1526 | 62.1918 | -61.1481 | -61.1893 | 62.0407 | 0.14648 | -0.07782 | 0.15106 | 62.114 | -61.1938 | -0.073242 | -0.054932 | -0.07782 | -0.11444 | -0.20599 | -0.11902 | -0.13275 | -0.004578 | 60.997 | 61.2259 | 123.1155 | 123.2666 | -0.07782 | 123.1888 | 61.2213 | -0.11902 | 123.2666 | -0.07782 | 61.2213 | 123.1155 | 123.1888 | -123.3948 | -123.4406
199.6562 | 123.3902 | -61.0657 | 62.2238 | -3.0052 | -0.063004 | -0.069801 | 0.10159 | -0.012714 | -0.079024 | 0.054224 | -61.2396 | 62.1735 | -61.1526 | -61.171 | 62.0361 | 0.14648 | -0.068665 | 0.17853 | 62.1094 | -61.171 | -0.086975 | -0.050354 | -0.17395 | -0.10529 | -0.18768 | -0.10529 | -0.11444 | -0.086975 | 60.997 | 61.2442 | 123.1018 | 123.2391 | -0.17395 | 123.175 | 61.2122 | -0.10529 | 123.2391 | -0.17395 | 61.2122 | 123.1018 | 123.175 | -123.3765 | -123.3948
200.6562 | 123.3948 | -61.0977 | 62.2375 | -0.24333 | -0.061936 | -0.099708 | 0.10053 | -0.0084417 | -0.08116 | 0.046747 | -61.1984 | 62.1735 | -61.1526 | -61.171 | 62.0499 | 0.15106 | -0.073242 | 0.13275 | 62.1231 | -61.1664 | -0.054932 | -0.064087 | -0.10071 | -0.073242 | -0.18768 | -0.068665 | -0.11444 | -0.045776 | 61.0245 | 61.2305 | 123.1476 | 123.2712 | -0.10071 | 123.2208 | 61.2488 | -0.068665 | 123.2712 | -0.10071 | 61.2488 | 123.1476 | 123.2208 | -123.3902 | -123.4039
201.7031 | 123.5458 | -61.0107 | 62.1689 | -0.04497 | -0.06514 | -0.096503 | 0.083437 | -0.018055 | -0.096114 | 0.058496 | -61.1435 | 62.059 | -61.1526 | -61.3678 | 61.9171 | -0.009155 | 0.082397 | -0.027466 | 62.178 | -61.2167 | -0.14191 | -0.10986 | -0.13275 | -0.35706 | -0.25177 | -0.20599 | 0.009156 | 0.009155 | 61.0931 | 60.9833 | 122.9279 | 123.0698 | -0.13275 | 123.1888 | 61.0016 | -0.20599 | 123.0698 | -0.13275 | 61.0016 | 122.9279 | 123.1888 | -123.3215 | -123.3856
202.6562 | 123.4406 | -61.0382 | 62.2055 | -0.13652 | -0.048051 | -0.11466 | 0.099459 | -0.021259 | -0.083297 | 0.058496 | -61.1801 | 62.1964 | -61.1618 | -61.1893 | 62.059 | 0.13275 | -0.091553 | 0.15106 | 62.1094 | -61.1984 | -0.1236 | -0.009155 | -0.14191 | -0.15106 | -0.14648 | -0.16022 | -0.09613 | -0.018311 | 60.9467 | 61.1893 | 123.0972 | 123.2346 | -0.14191 | 123.1476 | 61.171 | -0.16022 | 123.2346 | -0.14191 | 61.171 | 123.0972 | 123.1476 | -123.3673 | -123.4039
203.6562 | 123.3948 | -61.0657 | 62.2284 | -0.19756 | -0.052323 | -0.095435 | 0.10266 | -0.020191 | -0.084365 | 0.046747 | -61.2076 | 62.1735 | -61.1801 | -61.084 | 62.2833 | 0.18768 | -0.16937 | 0.07782 | 62.0956 | -61.2122 | -0.11444 | -0.054932 | -0.14191 | -0.01831 | 0.054931 | -0.14648 | -0.13275 | -0.027466 | 60.8963 | 61.1435 | 123.349 | 123.2391 | -0.14191 | 123.1613 | 61.2534 | -0.14648 | 123.2391 | -0.14191 | 61.2534 | 123.349 | 123.1613 | -123.4085 | -123.4406
204.6562 | 123.436 | -61.0474 | 62.1872 | -0.24333 | -0.070481 | -0.10825 | 0.083437 | -0.015918 | -0.093978 | 0.041406 | -61.1435 | 62.1185 | -61.1526 | -61.2671 | 61.9583 | 0.059509 | 0.018311 | 0.082397 | 62.1597 | -61.1984 | -0.10529 | -0.068665 | -0.096131 | -0.21973 | -0.22888 | -0.15106 | -0.027466 | 0.009155 | 61.0657 | 61.1298 | 123.0057 | 123.1659 | -0.096131 | 123.2071 | 61.1069 | -0.15106 | 123.1659 | -0.096131 | 61.1069 | 123.0057 | 123.2071 | -123.3398 | -123.3856
205.7031 | 123.5733 | -61.0519 | 62.1689 | 0.092359 | -0.07689 | -0.099708 | 0.083437 | -0.023395 | -0.10252 | 0.055292 | -61.1481 | 62.0682 | -61.1618 | -61.3449 | 61.9308 | -0.018311 | 0.086975 | -0.018311 | 62.1643 | -61.2076 | -0.10986 | -0.10071 | -0.09613 | -0.29297 | -0.23804 | -0.15564 | -0.004577 | 0.013733 | 61.1389 | 61.0336 | 122.9828 | 123.1201 | -0.09613 | 123.2162 | 61.0336 | -0.15564 | 123.1201 | -0.09613 | 61.0336 | 122.9828 | 123.2162 | -123.3307 | -123.3765
206.6562 | 123.3948 | -61.0519 | 62.2375 | -0.28911 | -0.066209 | -0.10612 | 0.10373 | -0.0073727 | -0.079024 | 0.044611 | -60.9833 | 62.2101 | -61.1618 | -61.1526 | 62.059 | 0.14191 | -0.10529 | 0.16022 | 62.1185 | -61.1618 | -0.10986 | -0.027466 | 0.068665 | -0.10071 | -0.17853 | -0.10986 | -0.11902 | 0.17853 | 60.9467 | 61.2122 | 123.111 | 123.262 | 0.068665 | 123.1705 | 61.1938 | -0.10986 | 123.262 | 0.068665 | 61.1938 | 123.111 | 123.1705 | -123.3994 | -123.3994
207.7031 | 123.5092 | -61.0519 | 62.1826 | -0.090746 | -0.068345 | -0.08689 | 0.086642 | -0.020191 | -0.095046 | 0.0617 | -61.1206 | 62.1094 | -61.1435 | -61.322 | 61.9171 | 0.004578 | 0.064087 | 0.013733 | 62.1735 | -61.2213 | -0.091553 | -0.073242 | -0.068664 | -0.27008 | -0.2655 | -0.16937 | -0.009155 | 0.022889 | 61.116 | 61.0657 | 122.9691 | 123.1613 | -0.068664 | 123.2254 | 61.0565 | -0.16937 | 123.1613 | -0.068664 | 61.0565 | 122.9691 | 123.2254 | -123.3261 | -123.4039
208.6719 | 123.3902 | -61.1069 | 62.1643 | 0.53486 | -0.017075 | -0.067664 | 0.11228 | -0.019123 | -0.082229 | 0.045679 | -61.5051 | 62.1277 | -61.2213 | -61.1893 | 62.0773 | 0.13275 | -0.091553 | 0.13733 | 62.0682 | -61.2213 | -0.11444 | -0.036621 | -0.39825 | -0.082397 | -0.086975 | -0.11444 | -0.096131 | -0.28381 | 61.0153 | 61.2442 | 123.1842 | 123.2346 | -0.39825 | 123.175 | 61.2396 | -0.11444 | 123.2346 | -0.39825 | 61.2396 | 123.1842 | 123.175 | -123.3856 | -123.3856
209.7031 | 123.4772 | -61.0611 | 62.1597 | 0.21443 | -0.066209 | -0.082618 | 0.075961 | -0.011646 | -0.097182 | 0.045679 | -61.1755 | 62.0773 | -61.1664 | -61.2305 | 61.9949 | 0.004578 | 0.018311 | 0.054932 | 62.1368 | -61.2076 | -0.10529 | -0.082397 | -0.11444 | -0.16937 | -0.16479 | -0.14648 | -0.022888 | -0.009155 | 61.0794 | 61.116 | 123.056 | 123.1384 | -0.11444 | 123.1979 | 61.0657 | -0.14648 | 123.1384 | -0.11444 | 61.0657 | 123.056 | 123.1979 | -123.3261 | -123.3673
210.6562 | 123.3902 | -61.0611 | 62.2101 | 1.4504 | -0.068345 | -0.10291 | 0.10907 | -0.013782 | -0.089705 | 0.03927 | -61.1801 | 62.1506 | -61.1893 | -61.1389 | 62.0819 | 0.16022 | -0.09613 | 0.13275 | 62.1323 | -61.1984 | -0.12817 | -0.059509 | -0.11902 | -0.07782 | -0.12817 | -0.13733 | -0.07782 | 0.009155 | 60.965 | 61.1938 | 123.143 | 123.2117 | -0.11902 | 123.1934 | 61.2213 | -0.13733 | 123.2117 | -0.11902 | 61.2213 | 123.143 | 123.1934 | -123.3994 | -123.4085
211.7031 | 123.5138 | -61.0565 | 62.1872 | 0.046583 | -0.068345 | -0.09864 | 0.085574 | -0.020191 | -0.099318 | 0.043542 | -61.1435 | 62.0865 | -61.1572 | -61.3266 | 61.9308 | -0.004578 | 0.054932 | 0 | 62.1506 | -61.2167 | -0.10071 | -0.10071 | -0.086975 | -0.27008 | -0.25635 | -0.16022 | -0.036621 | 0.013733 | 61.1115 | 61.0565 | 122.9874 | 123.143 | -0.086975 | 123.2071 | 61.0519 | -0.16022 | 123.143 | -0.086975 | 61.0519 | 122.9874 | 123.2071 | -123.3444 | -123.4039
212.6562 | 123.3902 | -61.0565 | 62.2192 | -0.27385 | -0.053391 | -0.077277 | 0.108 | -0.018055 | -0.09825 | 0.041406 | -61.2076 | 62.1643 | -61.1664 | -61.2259 | 62.2101 | 0.23804 | -0.09613 | 0.059509 | 62.1094 | -61.1801 | -0.10986 | -0.054931 | -0.15106 | -0.16937 | -0.009155 | -0.1236 | -0.10986 | -0.041199 | 60.9604 | 61.116 | 123.2666 | 123.2208 | -0.15106 | 123.1659 | 61.2946 | -0.1236 | 123.2208 | -0.15106 | 61.2946 | 123.2666 | 123.1659 | -123.3856 | -123.3994
213.7188 | 123.4497 | -61.0474 | 62.2009 | -0.24333 | -0.068345 | -0.10184 | 0.09305 | -0.0095097 | -0.089705 | 0.051019 | -61.1389 | 62.1414 | -61.116 | -61.2534 | 61.9904 | 0.07782 | 0.009155 | 0.059509 | 62.1368 | -61.2122 | -0.068665 | -0.05951 | -0.091553 | -0.20599 | -0.21057 | -0.1648 | -0.064087 | -0.022888 | 61.0565 | 61.1069 | 123.0377 | 123.1888 | -0.091553 | 123.1842 | 61.1252 | -0.1648 | 123.1888 | -0.091553 | 61.1252 | 123.0377 | 123.1842 | -123.317 | -123.4131
214.6562 | 123.3856 | -61.0748 | 62.2192 | -0.24333 | -0.0598 | -0.090095 | 0.10373 | -0.018055 | -0.091842 | 0.051019 | -61.1984 | 62.1506 | -61.1755 | -61.1618 | 62.059 | 0.12817 | -0.07782 | 0.14191 | 62.0911 | -61.1618 | -0.10071 | -0.068664 | -0.1236 | -0.086975 | -0.16022 | -0.086975 | -0.12817 | -0.022888 | 60.997 | 61.2167 | 123.1338 | 123.2254 | -0.1236 | 123.1659 | 61.203 | -0.086975 | 123.2254 | -0.1236 | 61.203 | 123.1338 | 123.1659 | -123.3948 | -123.381
215.7031 | 123.5275 | -61.0382 | 62.1872 | 0.18391 | -0.057664 | -0.10291 | 0.095187 | -0.013782 | -0.10146 | 0.048883 | -61.1801 | 62.0773 | -61.1664 | -61.2946 | 61.9629 | 0.013733 | 0.022888 | 0.018311 | 62.1048 | -61.2167 | -0.12817 | -0.10986 | -0.14191 | -0.25635 | -0.2243 | -0.17853 | -0.082398 | -0.013733 | 61.0611 | 61.0565 | 123.0011 | 123.1155 | -0.14191 | 123.143 | 61.0519 | -0.17853 | 123.1155 | -0.14191 | 61.0519 | 123.0011 | 123.143 | -123.3536 | -123.4039
216.6562 | 123.3948 | -61.0794 | 62.2009 | 1.1452 | -0.060868 | -0.092231 | 0.10907 | -0.018055 | -0.086501 | 0.047815 | -61.3266 | 62.1552 | -61.1847 | -61.1481 | 62.0911 | 0.1831 | -0.068665 | 0.16022 | 62.1323 | -61.1664 | -0.10528 | -0.045777 | -0.24719 | -0.068664 | -0.10986 | -0.086975 | -0.068665 | -0.14191 | 61.0107 | 61.2396 | 123.1705 | 123.2346 | -0.24719 | 123.2117 | 61.2625 | -0.086975 | 123.2346 | -0.24719 | 61.2625 | 123.1705 | 123.2117 | -123.3856 | -123.3673
217.6562 | 123.4909 | -61.0336 | 62.1964 | -0.12126 | -0.067277 | -0.077277 | 0.089846 | -0.015918 | -0.090773 | 0.0617 | -61.116 | 62.1094 | -61.116 | -61.2991 | 61.9354 | 0.018311 | 0.054932 | 0.013733 | 62.1323 | -61.2167 | -0.082398 | -0.086975 | -0.082398 | -0.2655 | -0.26093 | -0.18311 | -0.064087 | 0 | 61.0886 | 61.0474 | 122.9691 | 123.143 | -0.082398 | 123.1659 | 61.0519 | -0.18311 | 123.143 | -0.082398 | 61.0519 | 122.9691 | 123.1659 | -123.3124 | -123.4131
218.7188 | 123.4589 | -61.0474 | 62.2238 | -0.075488 | -0.046983 | -0.06446 | 0.11121 | -0.0084417 | -0.074752 | 0.045679 | -61.1572 | 62.2009 | -61.1435 | -61.1755 | 62.0132 | 0.091553 | -0.041199 | 0.10071 | 62.0911 | -61.1938 | -0.096131 | -0.022888 | -0.10986 | -0.12817 | -0.21057 | -0.14649 | -0.13275 | -0.013733 | 61.0062 | 61.1481 | 123.0606 | 123.2483 | -0.10986 | 123.1384 | 61.1389 | -0.14649 | 123.2483 | -0.10986 | 61.1389 | 123.0606 | 123.1384 | -123.3673 | -123.4177
219.6562 | 123.4497 | -61.0428 | 62.2101 | -0.24333 | -0.067277 | -0.10825 | 0.08771 | -0.016986 | -0.10252 | 0.034998 | -61.1435 | 62.114 | -61.1435 | -61.2442 | 61.9995 | 0.086975 | -0.004578 | 0.068665 | 62.1277 | -61.1893 | -0.10071 | -0.09613 | -0.10071 | -0.20142 | -0.21057 | -0.14648 | -0.082397 | 0 | 61.0382 | 61.1115 | 123.0423 | 123.1567 | -0.10071 | 123.1705 | 61.1298 | -0.14648 | 123.1567 | -0.10071 | 61.1298 | 123.0423 | 123.1705 | -123.3536 | -123.3994
220.6562 | 123.468 | -61.0519 | 62.2055 | -0.25859 | -0.057664 | -0.091163 | 0.088778 | -0.025531 | -0.095046 | 0.043542 | -61.1435 | 62.114 | -61.1526 | -61.2717 | 61.9766 | 0.059509 | 0.013733 | 0.059509 | 62.1368 | -61.1893 | -0.10071 | -0.091552 | -0.091553 | -0.21973 | -0.22888 | -0.13733 | -0.068664 | 0.009155 | 61.0657 | 61.1114 | 123.0286 | 123.1659 | -0.091553 | 123.1888 | 61.1114 | -0.13733 | 123.1659 | -0.091553 | 61.1114 | 123.0286 | 123.1888 | -123.3582 | -123.3948
221.6562 | 123.4085 | -61.1023 | 62.2147 | -0.12126 | -0.066209 | -0.10291 | 0.097323 | -0.022327 | -0.086501 | 0.046747 | -61.1938 | 62.146 | -61.1481 | -61.171 | 62.0544 | 0.13733 | -0.068665 | 0.13733 | 62.0865 | -61.1526 | -0.045776 | -0.068665 | -0.091553 | -0.068664 | -0.16022 | -0.050354 | -0.12817 | -0.045777 | 61.0336 | 61.2396 | 123.1567 | 123.2483 | -0.091553 | 123.1888 | 61.2396 | -0.050354 | 123.2483 | -0.091553 | 61.2396 | 123.1567 | 123.1888 | -123.3627 | -123.3673
222.6562 | 123.4131 | -61.0794 | 62.2284 | -0.28911 | -0.056596 | -0.08689 | 0.090914 | -0.021259 | -0.095046 | 0.03927 | -61.1847 | 62.1689 | -61.1618 | -61.1847 | 62.059 | 0.14648 | -0.07782 | 0.11444 | 62.1231 | -61.171 | -0.082397 | -0.05951 | -0.10528 | -0.10528 | -0.16937 | -0.091552 | -0.10529 | -0.022888 | 61.0016 | 61.1938 | 123.1384 | 123.2483 | -0.10528 | 123.2025 | 61.2259 | -0.091552 | 123.2483 | -0.10528 | 61.2259 | 123.1384 | 123.2025 | -123.3902 | -123.3994
223.6562 | 123.4177 | -61.0611 | 62.2147 | -0.36541 | -0.075822 | -0.10825 | 0.10053 | -0.018055 | -0.095046 | 0.048883 | -61.1664 | 62.1414 | -61.1343 | -61.2167 | 62.0361 | 0.1236 | -0.041199 | 0.10986 | 62.114 | -61.1847 | -0.073242 | -0.073243 | -0.10529 | -0.15564 | -0.17853 | -0.1236 | -0.10071 | -0.032044 | 61.0199 | 61.171 | 123.0972 | 123.2025 | -0.10529 | 123.175 | 61.1847 | -0.1236 | 123.2025 | -0.10529 | 61.1847 | 123.0972 | 123.175 | -123.349 | -123.3994
224.7031 | 123.6282 | -61.0291 | 62.2604 | -0.060229 | -0.060868 | -0.11252 | 0.094119 | -0.024463 | -0.099318 | 0.055292 | -61.1114 | 62.059 | -61.1252 | -61.3632 | 61.9034 | 0 | 0.082397 | -0.009155 | 62.1277 | -61.2122 | -0.09613 | -0.20142 | -0.082397 | -0.33417 | -0.35706 | -0.18311 | -0.13275 | 0.013733 | 61.1114 | 61.0199 | 122.9324 | 123.0881 | -0.082397 | 123.1567 | 61.0291 | -0.18311 | 123.0881 | -0.082397 | 61.0291 | 122.9324 | 123.1567 | -123.3856 | -123.4726
225.6562 | 123.5367 | -61.0336 | 62.2101 | -0.51799 | -0.070481 | -0.082618 | 0.097323 | -0.01485 | -0.091842 | 0.037134 | -61.1069 | 62.0911 | -61.1252 | -61.3174 | 61.908 | 0.004578 | 0.068665 | -0.009155 | 62.1323 | -61.2122 | -0.091553 | -0.11902 | -0.073243 | -0.28381 | -0.30212 | -0.17853 | -0.07782 | 0.01831 | 61.1023 | 61.0245 | 122.9416 | 123.1247 | -0.073243 | 123.1659 | 61.0382 | -0.17853 | 123.1247 | -0.073243 | 61.0382 | 122.9416 | 123.1659 | -123.3353 | -123.4222
226.7031 | 123.4955 | -61.0428 | 62.1826 | 0.16865 | -0.072617 | -0.12214 | 0.090914 | -0.021259 | -0.10786 | 0.043542 | -61.1984 | 62.0911 | -61.1526 | -61.2946 | 61.972 | 0.004578 | 0.050354 | 0.027466 | 62.1277 | -61.1984 | -0.10986 | -0.091553 | -0.15564 | -0.25177 | -0.21057 | -0.15564 | -0.054931 | -0.045776 | 61.0931 | 61.0703 | 123.0148 | 123.1338 | -0.15564 | 123.1705 | 61.0474 | -0.15564 | 123.1338 | -0.15564 | 61.0474 | 123.0148 | 123.1705 | -123.3353 | -123.381
227.6562 | 123.5138 | -61.0245 | 62.1872 | -0.16704 | -0.051255 | -0.12321 | 0.085574 | -0.022327 | -0.086501 | 0.054224 | -61.1343 | 62.1185 | -61.1389 | -61.3037 | 61.9537 | 0.041199 | 0.050354 | 0.032043 | 62.1048 | -61.2076 | -0.11444 | -0.068665 | -0.10986 | -0.27924 | -0.23346 | -0.18311 | -0.082398 | 0.004578 | 61.0748 | 61.0565 | 122.9782 | 123.143 | -0.10986 | 123.1293 | 61.0657 | -0.18311 | 123.143 | -0.10986 | 61.0657 | 122.9782 | 123.1293 | -123.3261 | -123.3948
228.6562 | 123.4268 | -61.084 | 62.2101 | -0.39592 | -0.069413 | -0.084754 | 0.096255 | -0.024463 | -0.095046 | 0.03927 | -61.1572 | 62.1231 | -61.1481 | -61.2122 | 62.0132 | 0.10071 | -0.041199 | 0.09613 | 62.1094 | -61.171 | -0.064087 | -0.086975 | -0.073243 | -0.12817 | -0.19684 | -0.086975 | -0.10071 | -0.009156 | 61.0428 | 61.1801 | 123.0972 | 123.2071 | -0.073243 | 123.1934 | 61.1847 | -0.086975 | 123.2071 | -0.073243 | 61.1847 | 123.0972 | 123.1934 | -123.3582 | -123.381
229.6562 | 123.4543 | -61.0565 | 62.2238 | -0.22808 | -0.060868 | -0.09864 | 0.10053 | -0.025531 | -0.10146 | 0.038202 | -61.1526 | 62.1368 | -61.1389 | -61.2534 | 61.9766 | 0.064087 | -0.004578 | 0.073242 | 62.0911 | -61.203 | -0.082397 | -0.086975 | -0.09613 | -0.19684 | -0.24719 | -0.14648 | -0.13275 | -0.013733 | 61.0519 | 61.1298 | 123.0331 | 123.1934 | -0.09613 | 123.1476 | 61.1206 | -0.14648 | 123.1934 | -0.09613 | 61.1206 | 123.0331 | 123.1476 | -123.3627 | -123.4268
230.7031 | 123.468 | -61.0611 | 62.1689 | 0.41279 | -0.060868 | -0.080482 | 0.090914 | -0.029804 | -0.10786 | 0.046747 | -61.1847 | 62.0728 | -61.1481 | -61.2808 | 61.9766 | 0.009155 | 0.027466 | 0.032043 | 62.1231 | -61.2076 | -0.086975 | -0.09613 | -0.1236 | -0.21973 | -0.19226 | -0.14648 | -0.045776 | -0.036621 | 61.0886 | 61.0931 | 123.0377 | 123.1338 | -0.1236 | 123.1842 | 61.0703 | -0.14648 | 123.1338 | -0.1236 | 61.0703 | 123.0377 | 123.1842 | -123.317 | -123.3765
231.6719 | 123.4039 | -61.0611 | 62.1918 | 0.27546 | -0.043778 | -0.084754 | 0.11975 | -0.018055 | -0.080092 | 0.031793 | -61.1664 | 62.1872 | -61.171 | -61.1298 | 62.0544 | 0.10986 | -0.07782 | 0.11444 | 62.0636 | -61.2122 | -0.10986 | -0.004577 | -0.10529 | -0.068665 | -0.13733 | -0.15106 | -0.12817 | 0.004577 | 60.9833 | 61.1755 | 123.1155 | 123.2483 | -0.10529 | 123.1247 | 61.171 | -0.15106 | 123.2483 | -0.10529 | 61.171 | 123.1155 | 123.1247 | -123.3627 | -123.4039
232.7188 | 123.5046 | -61.0199 | 62.1689 | -0.090746 | -0.068345 | -0.10078 | 0.096255 | -0.0095097 | -0.10039 | 0.055292 | -61.1389 | 62.1002 | -61.1664 | -61.3083 | 61.9446 | 0.022888 | 0.068665 | 0.013733 | 62.1277 | -61.2167 | -0.14648 | -0.068664 | -0.11902 | -0.28839 | -0.2243 | -0.19684 | -0.041198 | 0.027466 | 61.0886 | 61.0336 | 122.9645 | 123.1201 | -0.11902 | 123.1476 | 61.0428 | -0.19684 | 123.1201 | -0.11902 | 61.0428 | 122.9645 | 123.1476 | -123.3353 | -123.3856
233.6562 | 123.5229 | -61.0336 | 62.1735 | -0.24333 | -0.067277 | -0.097572 | 0.09305 | -0.023395 | -0.093978 | 0.049951 | -61.1252 | 62.0819 | -61.1481 | -61.3083 | 61.9217 | 0.004578 | 0.059509 | -0.013733 | 62.1368 | -61.203 | -0.11444 | -0.091553 | -0.091553 | -0.27466 | -0.25177 | -0.16937 | -0.036621 | 0.022888 | 61.0931 | 61.0199 | 122.9553 | 123.1155 | -0.091553 | 123.1705 | 61.0382 | -0.16937 | 123.1155 | -0.091553 | 61.0382 | 122.9553 | 123.1705 | -123.3215 | -123.3765
234.6562 | 123.5229 | -61.0245 | 62.2055 | -0.25859 | -0.0598 | -0.11252 | 0.098391 | -0.013782 | -0.10039 | 0.059564 | -60.8688 | 62.1506 | -61.116 | -61.2717 | 61.9034 | -0.027466 | 0.064087 | -0.018311 | 62.1414 | -61.1801 | -0.091553 | -0.054931 | 0.15564 | -0.24719 | -0.30212 | -0.15564 | -0.064087 | 0.24719 | 61.0886 | 61.0062 | 122.9279 | 123.175 | 0.15564 | 123.1659 | 60.997 | -0.15564 | 123.175 | 0.15564 | 60.997 | 122.9279 | 123.1659 | -123.3215 | -123.3856
235.7031 | 123.5092 | -61.0428 | 62.1597 | 0.24495 | -0.063004 | -0.094367 | 0.10159 | -0.028736 | -0.084365 | 0.038202 | -61.1435 | 62.0819 | -61.1435 | -61.322 | 61.9217 | -0.018311 | 0.09613 | -0.018311 | 62.0956 | -61.235 | -0.10071 | -0.07782 | -0.10071 | -0.27923 | -0.23804 | -0.19226 | -0.064087 | 0 | 61.1389 | 61.0245 | 122.9645 | 123.1247 | -0.10071 | 123.1384 | 61.0245 | -0.19226 | 123.1247 | -0.10071 | 61.0245 | 122.9645 | 123.1384 | -123.3032 | -123.3948
236.6719 | 123.4543 | -61.0474 | 62.2055 | 0.10762 | -0.045914 | -0.073005 | 0.11762 | -0.0084417 | -0.067275 | 0.033929 | -61.1298 | 62.1872 | -61.1435 | -61.2488 | 62.0407 | 0.082397 | -0.068665 | 0.11902 | 62.0819 | -61.203 | -0.096131 | -0.01831 | -0.082398 | -0.20142 | -0.1648 | -0.15564 | -0.1236 | 0.013733 | 60.9787 | 61.1664 | 123.0881 | 123.2346 | -0.082398 | 123.1293 | 61.1298 | -0.15564 | 123.2346 | -0.082398 | 61.1298 | 123.0881 | 123.1293 | -123.349 | -123.4085
237.7188 | 123.4406 | -61.0977 | 62.2101 | -0.19756 | -0.052323 | -0.10184 | 0.1048 | -0.021259 | -0.077956 | 0.042474 | -61.1893 | 62.2055 | -61.1664 | -61.1526 | 62.059 | 0.14648 | -0.073242 | 0.13733 | 62.1094 | -61.1526 | -0.068665 | -0.004578 | -0.091553 | -0.054932 | -0.15106 | -0.054932 | -0.10071 | -0.022888 | 61.0245 | 61.235 | 123.1567 | 123.3032 | -0.091553 | 123.2071 | 61.2442 | -0.054932 | 123.3032 | -0.091553 | 61.2442 | 123.1567 | 123.2071 | -123.3765 | -123.3627
238.6562 | 123.5321 | -61.0291 | 62.1643 | 0.15339 | -0.061936 | -0.11039 | 0.079165 | -0.023395 | -0.10359 | 0.055292 | -61.1572 | 62.0773 | -61.1481 | -61.3083 | 61.9583 | -0.004578 | 0.068665 | 0.018311 | 62.1643 | -61.203 | -0.11902 | -0.086975 | -0.12817 | -0.27924 | -0.20599 | -0.17395 | 0 | -0.009156 | 61.0977 | 61.0474 | 122.9874 | 123.1064 | -0.12817 | 123.1934 | 61.0245 | -0.17395 | 123.1064 | -0.12817 | 61.0245 | 122.9874 | 123.1934 | -123.3124 | -123.3673
239.6562 | 123.5229 | -61.0611 | 62.1643 | -0.029711 | -0.064072 | -0.090095 | 0.08771 | -0.025531 | -0.11641 | 0.0617 | -61.1755 | 62.1048 | -61.1435 | -61.3129 | 61.9537 | 0.013733 | 0.064087 | 0.032043 | 62.146 | -61.2122 | -0.082398 | -0.05951 | -0.11444 | -0.25177 | -0.21057 | -0.15106 | -0.018311 | -0.032043 | 61.1252 | 61.0931 | 123.0148 | 123.1659 | -0.11444 | 123.2071 | 61.0748 | -0.15106 | 123.1659 | -0.11444 | 61.0748 | 123.0148 | 123.2071 | -123.3078 | -123.3765
240.6562 | 123.5138 | -61.0245 | 62.178 | -0.04497 | -0.066209 | -0.094367 | 0.095187 | -0.034076 | -0.10573 | 0.048883 | -61.1343 | 62.0773 | -61.1206 | -61.3312 | 61.908 | -0.004578 | 0.091553 | -0.018311 | 62.1231 | -61.203 | -0.09613 | -0.10071 | -0.10986 | -0.3067 | -0.27008 | -0.17853 | -0.054932 | -0.013733 | 61.116 | 61.0062 | 122.9324 | 123.1018 | -0.10986 | 123.1476 | 61.0199 | -0.17853 | 123.1018 | -0.10986 | 61.0199 | 122.9324 | 123.1476 | -123.2986 | -123.381
241.7188 | 123.3948 | -61.084 | 62.1552 | 0.45857 | -0.052323 | -0.076209 | 0.11975 | -0.027668 | -0.080092 | 0.046747 | -61.203 | 62.178 | -61.1847 | -61.1618 | 62.0453 | 0.10986 | -0.082397 | 0.12817 | 62.0636 | -61.171 | -0.10071 | 0.022889 | -0.11902 | -0.07782 | -0.10986 | -0.086975 | -0.091552 | -0.018311 | 61.0016 | 61.2122 | 123.1293 | 123.262 | -0.11902 | 123.1476 | 61.1938 | -0.086975 | 123.262 | -0.11902 | 61.1938 | 123.1293 | 123.1476 | -123.3398 | -123.3261
242.6562 | 123.5275 | -61.0336 | 62.1735 | -0.10601 | -0.079026 | -0.10078 | 0.090914 | -0.027668 | -0.1068 | 0.049951 | -61.1298 | 62.059 | -61.1435 | -61.3541 | 61.9125 | -0.018311 | 0.10529 | -0.022888 | 62.114 | -61.2259 | -0.10986 | -0.11444 | -0.096131 | -0.32043 | -0.26093 | -0.19226 | -0.059509 | 0.013733 | 61.1389 | 61.0107 | 122.9462 | 123.0927 | -0.096131 | 123.1476 | 61.0153 | -0.19226 | 123.0927 | -0.096131 | 61.0153 | 122.9462 | 123.1476 | -123.317 | -123.3994
243.7031 | 123.4909 | -61.0336 | 62.1643 | 0.36702 | -0.068345 | -0.10184 | 0.088778 | -0.034076 | -0.09825 | 0.046747 | -61.2076 | 62.0911 | -61.171 | -61.3129 | 62.0041 | 0.059509 | -0.036621 | 0.059509 | 62.1277 | -61.2122 | -0.13733 | -0.073243 | -0.17395 | -0.27924 | -0.16022 | -0.17853 | -0.036621 | -0.036622 | 60.997 | 61.0931 | 123.0377 | 123.1247 | -0.17395 | 123.1613 | 61.0931 | -0.17853 | 123.1247 | -0.17395 | 61.0931 | 123.0377 | 123.1613 | -123.3353 | -123.3765
244.6562 | 123.4955 | -61.0107 | 62.1918 | 0.00080561 | -0.070481 | -0.11359 | 0.096255 | -0.027668 | -0.099318 | 0.052087 | -61.1572 | 62.1002 | -61.1618 | -61.3083 | 61.9354 | 0.018311 | 0.064087 | 0 | 62.1277 | -61.203 | -0.15106 | -0.091552 | -0.14648 | -0.29755 | -0.25635 | -0.19226 | -0.064086 | 0.004577 | 61.0748 | 61.0107 | 122.9462 | 123.111 | -0.14648 | 123.1384 | 61.0291 | -0.19226 | 123.111 | -0.14648 | 61.0291 | 122.9462 | 123.1384 | -123.3536 | -123.3948
245.7031 | 123.5138 | -61.0245 | 62.146 | 0.41279 | -0.0598 | -0.083686 | 0.098391 | -0.027668 | -0.096114 | 0.048883 | -61.1206 | 62.0819 | -61.1481 | -61.322 | 61.94 | -0.022888 | 0.073242 | -0.009155 | 62.0911 | -61.2305 | -0.1236 | -0.064087 | -0.09613 | -0.29755 | -0.20599 | -0.20599 | -0.054932 | 0.027466 | 61.0977 | 61.0153 | 122.9645 | 123.1064 | -0.09613 | 123.1155 | 61.0016 | -0.20599 | 123.1064 | -0.09613 | 61.0016 | 122.9645 | 123.1155 | -123.2941 | -123.3765
246.6719 | 123.4222 | -61.0657 | 62.2101 | 1.5267 | -0.073685 | -0.08155 | 0.11014 | -0.022327 | -0.079024 | 0.044611 | -61.2122 | 62.1735 | -61.1847 | -61.1114 | 62.0728 | 0.17853 | -0.10529 | 0.15564 | 62.0773 | -61.1938 | -0.11902 | -0.036621 | -0.14648 | -0.045776 | -0.13733 | -0.12817 | -0.13275 | -0.027466 | 60.9604 | 61.2213 | 123.1384 | 123.2391 | -0.14648 | 123.143 | 61.2442 | -0.12817 | 123.2391 | -0.14648 | 61.2442 | 123.1384 | 123.143 | -123.3948 | -123.4039
247.7031 | 123.4955 | -61.0565 | 62.1643 | 0.53486 | -0.064072 | -0.094367 | 0.10907 | -0.023395 | -0.079024 | 0.043542 | -61.171 | 62.1277 | -61.1847 | -61.2762 | 61.972 | 0.018311 | 0.041199 | -0.004578 | 62.0819 | -61.2259 | -0.12817 | -0.036621 | -0.11444 | -0.21973 | -0.19226 | -0.16937 | -0.082398 | 0.013733 | 61.0977 | 61.0519 | 123.0286 | 123.1842 | -0.11444 | 123.1384 | 61.0748 | -0.16937 | 123.1842 | -0.11444 | 61.0748 | 123.0286 | 123.1384 | -123.349 | -123.3902
248.6562 | 123.468 | -61.0336 | 62.1597 | 0.30598 | -0.068345 | -0.10932 | 0.08771 | -0.033008 | -0.10252 | 0.053156 | -61.2167 | 62.1048 | -61.1618 | -61.2991 | 62.0132 | 0.032043 | -0.041199 | 0.059509 | 62.1094 | -61.2167 | -0.12817 | -0.054932 | -0.18311 | -0.2655 | -0.14648 | -0.18311 | -0.050354 | -0.054932 | 60.9924 | 61.0931 | 123.0469 | 123.1384 | -0.18311 | 123.143 | 61.0657 | -0.18311 | 123.1384 | -0.18311 | 61.0657 | 123.0469 | 123.143 | -123.3215 | -123.3765
249.7031 | 123.3994 | -61.0977 | 62.1964 | 0.35176 | -0.058732 | -0.08689 | 0.12082 | -0.026599 | -0.073684 | 0.041406 | -61.203 | 62.2009 | -61.171 | -61.1435 | 62.0773 | 0.1236 | -0.09613 | 0.1236 | 62.0636 | -61.2122 | -0.073242 | 0.004578 | -0.10529 | -0.045777 | -0.11902 | -0.11444 | -0.13275 | -0.032044 | 61.0016 | 61.2213 | 123.175 | 123.2986 | -0.10529 | 123.1613 | 61.2213 | -0.11444 | 123.2986 | -0.10529 | 61.2213 | 123.175 | 123.1613 | -123.3673 | -123.4085
250.6562 | 123.4497 | -61.0428 | 62.1506 | 0.19917 | -0.066209 | -0.10718 | 0.080233 | -0.012714 | -0.093978 | 0.042474 | -61.0977 | 62.1094 | -61.1435 | -61.2625 | 61.9904 | 0.054932 | 0 | 0.022888 | 62.0956 | -61.203 | -0.10071 | -0.041199 | -0.054931 | -0.21973 | -0.16022 | -0.16022 | -0.054932 | 0.045777 | 61.0428 | 61.0657 | 123.0331 | 123.1522 | -0.054931 | 123.1384 | 61.0977 | -0.16022 | 123.1522 | -0.054931 | 61.0977 | 123.0331 | 123.1384 | -123.2941 | -123.3536
251.7188 | 123.381 | -61.0565 | 62.2055 | -0.27385 | -0.063004 | -0.10932 | 0.10907 | -0.023395 | -0.079024 | 0.0617 | -61.0428 | 62.2238 | -61.1618 | -61.1526 | 62.0819 | 0.16022 | -0.091553 | 0.16022 | 62.0956 | -61.1572 | -0.10528 | 0.018311 | 0.013733 | -0.09613 | -0.1236 | -0.10071 | -0.10986 | 0.11902 | 60.965 | 61.2167 | 123.1384 | 123.2803 | 0.013733 | 123.1522 | 61.2167 | -0.10071 | 123.2803 | 0.013733 | 61.2167 | 123.1384 | 123.1522 | -123.3673 | -123.3627
252.6562 | 123.5001 | -61.0382 | 62.1506 | 0.48909 | -0.067277 | -0.10184 | 0.090914 | -0.020191 | -0.096114 | 0.042474 | -61.1526 | 62.0819 | -61.171 | -61.3174 | 61.9308 | -0.032043 | 0.068665 | -0.013733 | 62.1002 | -61.2122 | -0.13275 | -0.068665 | -0.11444 | -0.27924 | -0.21973 | -0.17395 | -0.050354 | 0.01831 | 61.1069 | 61.0245 | 122.9691 | 123.1201 | -0.11444 | 123.1384 | 61.0062 | -0.17395 | 123.1201 | -0.11444 | 61.0062 | 122.9691 | 123.1384 | -123.3215 | -123.3627
253.6562 | 123.5321 | -61.0474 | 62.1368 | 0.53486 | -0.051255 | -0.10184 | 0.091982 | -0.023395 | -0.090773 | 0.053156 | -61.1343 | 62.0819 | -61.1435 | -61.3266 | 61.9217 | -0.032043 | 0.064087 | -0.013733 | 62.0819 | -61.2259 | -0.096131 | -0.054932 | -0.086975 | -0.27924 | -0.21515 | -0.17853 | -0.054932 | 0.009156 | 61.1114 | 61.0336 | 122.9691 | 123.1293 | -0.086975 | 123.1293 | 61.0153 | -0.17853 | 123.1293 | -0.086975 | 61.0153 | 122.9691 | 123.1293 | -123.2803 | -123.3627
254.7188 | 123.4634 | -61.0245 | 62.1689 | -0.1823 | -0.066209 | -0.097572 | 0.080233 | -0.029804 | -0.096114 | 0.040338 | -61.2488 | 62.0682 | -61.1664 | -61.2671 | 61.9858 | 0.045776 | 0.018311 | 0.064087 | 62.1094 | -61.1984 | -0.14191 | -0.10071 | -0.2243 | -0.24262 | -0.1831 | -0.17395 | -0.059509 | -0.082397 | 61.0428 | 61.0886 | 123.0103 | 123.0927 | -0.2243 | 123.1338 | 61.0703 | -0.17395 | 123.0927 | -0.2243 | 61.0703 | 123.0103 | 123.1338 | -123.3353 | -123.3673
255.6562 | 123.5138 | -61.0428 | 62.1323 | 0.48909 | -0.06514 | -0.08155 | 0.10266 | -0.036213 | -0.091842 | 0.040338 | -61.1572 | 62.1002 | -61.1481 | -61.3129 | 61.9263 | -0.022888 | 0.054932 | -0.004578 | 62.1185 | -61.2534 | -0.10529 | -0.032043 | -0.11444 | -0.27008 | -0.20599 | -0.21057 | -0.013733 | -0.009156 | 61.0977 | 61.0382 | 122.9691 | 123.143 | -0.11444 | 123.1613 | 61.0199 | -0.21057 | 123.143 | -0.11444 | 61.0199 | 122.9691 | 123.1613 | -123.2803 | -123.3856
256.6562 | 123.4634 | -61.0428 | 62.1643 | 0.42805 | -0.0598 | -0.10612 | 0.10159 | -0.040485 | -0.084365 | 0.045679 | -61.1664 | 62.0865 | -61.1664 | -61.29 | 61.9675 | 0.004578 | 0.032043 | 0.027466 | 62.0956 | -61.2122 | -0.1236 | -0.07782 | -0.1236 | -0.24719 | -0.19684 | -0.16937 | -0.068665 | 0 | 61.0748 | 61.0703 | 123.0103 | 123.1293 | -0.1236 | 123.1384 | 61.0474 | -0.16937 | 123.1293 | -0.1236 | 61.0474 | 123.0103 | 123.1384 | -123.3307 | -123.3765
257.6562 | 123.5001 | -61.0428 | 62.1872 | 0.39753 | -0.057664 | -0.099708 | 0.10373 | -0.024463 | -0.096114 | 0.040338 | -61.1481 | 62.0865 | -61.1435 | -61.3174 | 61.9263 | -0.013733 | 0.064087 | -0.009155 | 62.1094 | -61.2167 | -0.10071 | -0.10071 | -0.10529 | -0.27466 | -0.26093 | -0.17395 | -0.07782 | -0.004577 | 61.1069 | 61.0336 | 122.9691 | 123.1293 | -0.10529 | 123.1522 | 61.0291 | -0.17395 | 123.1293 | -0.10529 | 61.0291 | 122.9691 | 123.1522 | -123.3307 | -123.4039
258.6562 | 123.5046 | -61.0474 | 62.146 | 0.5196 | -0.0598 | -0.11252 | 0.10159 | -0.022327 | -0.085433 | 0.042474 | -61.1343 | 62.0911 | -61.1343 | -61.3266 | 61.9217 | -0.036621 | 0.07782 | -0.018311 | 62.1002 | -61.2305 | -0.086975 | -0.054932 | -0.086975 | -0.27924 | -0.2243 | -0.18311 | -0.045776 | 0 | 61.1252 | 61.0291 | 122.9691 | 123.1384 | -0.086975 | 123.1476 | 61.0107 | -0.18311 | 123.1384 | -0.086975 | 61.0107 | 122.9691 | 123.1476 | -123.2803 | -123.3765
259.6562 | 123.5138 | -61.0382 | 62.1506 | 0.55012 | -0.048051 | -0.080482 | 0.12082 | -0.028736 | -0.090773 | 0.043542 | -61.1618 | 62.1048 | -61.1755 | -61.2762 | 61.94 | -0.013733 | 0.059509 | -0.004578 | 62.0911 | -61.2259 | -0.13733 | -0.045777 | -0.1236 | -0.23804 | -0.21057 | -0.18768 | -0.05951 | 0.013733 | 61.0977 | 61.0336 | 122.9782 | 123.143 | -0.1236 | 123.1293 | 61.0245 | -0.18768 | 123.143 | -0.1236 | 61.0245 | 122.9782 | 123.1293 | -123.3261 | -123.3765
260.7031 | 123.4222 | -61.0703 | 62.178 | 0.42805 | -0.051255 | -0.091163 | 0.11548 | -0.018055 | -0.07582 | 0.034998 | -61.1984 | 62.1735 | -61.1893 | -61.1481 | 62.0682 | 0.09613 | -0.09613 | 0.13275 | 62.0544 | -61.1938 | -0.11902 | -0.004578 | -0.12817 | -0.07782 | -0.10986 | -0.1236 | -0.1236 | -0.009155 | 60.9741 | 61.203 | 123.1384 | 123.2437 | -0.12817 | 123.1247 | 61.1664 | -0.1236 | 123.2437 | -0.12817 | 61.1664 | 123.1384 | 123.1247 | -123.3673 | -123.3719
261.6562 | 123.5092 | -61.0428 | 62.1231 | 0.56538 | -0.0598 | -0.099708 | 0.10053 | -0.025531 | -0.09291 | 0.040338 | -61.1389 | 62.1002 | -61.1526 | -61.3129 | 61.9492 | -0.036621 | 0.064087 | 0.004578 | 62.1094 | -61.2167 | -0.10986 | -0.022888 | -0.09613 | -0.27008 | -0.17395 | -0.17395 | -0.013733 | 0.013733 | 61.1069 | 61.0474 | 122.9919 | 123.143 | -0.09613 | 123.1522 | 61.0062 | -0.17395 | 123.143 | -0.09613 | 61.0062 | 122.9919 | 123.1522 | -123.2758 | -123.3398
262.6562 | 123.4955 | -61.0336 | 62.1506 | 0.55012 | -0.043778 | -0.08155 | 0.096255 | -0.027668 | -0.070479 | 0.045679 | -61.171 | 62.1368 | -61.171 | -61.2991 | 61.9492 | -0.009155 | 0.045776 | 0.009155 | 62.114 | -61.2167 | -0.13733 | -0.013733 | -0.13733 | -0.2655 | -0.20142 | -0.18311 | -0.036621 | 0 | 61.0794 | 61.0428 | 122.9828 | 123.1705 | -0.13733 | 123.1476 | 61.0245 | -0.18311 | 123.1705 | -0.13733 | 61.0245 | 122.9828 | 123.1476 | -123.3215 | -123.3673
263.6562 | 123.5275 | -61.0199 | 62.1185 | 0.61116 | -0.052323 | -0.068732 | 0.094119 | -0.015918 | -0.085433 | 0.027521 | -61.1252 | 62.0956 | -61.1618 | -61.2808 | 61.7294 | -0.09613 | 0.086975 | 0.091553 | 62.1231 | -61.2076 | -0.14191 | -0.022888 | -0.10529 | -0.26093 | -0.3891 | -0.18768 | 0.004578 | 0.036621 | 61.1069 | 61.1114 | 122.7493 | 123.1155 | -0.10529 | 123.143 | 60.9238 | -0.18768 | 123.1155 | -0.10529 | 60.9238 | 122.7493 | 123.143 | -123.2803 | -123.3261
264.7031 | 123.3673 | -61.0703 | 62.1872 | 0.36702 | -0.041642 | -0.084754 | 0.11548 | -0.030872 | -0.079024 | 0.051019 | -61.2076 | 62.2238 | -61.1664 | -61.1343 | 62.1002 | 0.12817 | -0.11444 | 0.15106 | 62.0407 | -61.203 | -0.096131 | 0.036621 | -0.13733 | -0.064087 | -0.086975 | -0.13275 | -0.14649 | -0.041199 | 60.9558 | 61.2213 | 123.1705 | 123.2941 | -0.13733 | 123.111 | 61.1984 | -0.13275 | 123.2941 | -0.13733 | 61.1984 | 123.1705 | 123.111 | -123.3536 | -123.3902
265.6562 | 123.5046 | -61.0336 | 62.1414 | 0.53486 | -0.056596 | -0.096503 | 0.099459 | -0.013782 | -0.087569 | 0.048883 | -61.1755 | 62.1185 | -61.1801 | -61.29 | 61.9583 | -0.004578 | 0.036621 | 0.009155 | 62.114 | -61.2122 | -0.14648 | -0.022888 | -0.14191 | -0.25635 | -0.18311 | -0.17853 | -0.027465 | 0.004578 | 61.0703 | 61.0428 | 122.9919 | 123.1522 | -0.14191 | 123.1476 | 61.0291 | -0.17853 | 123.1522 | -0.14191 | 61.0291 | 122.9919 | 123.1476 | -123.3215 | -123.3536
266.7031 | 123.5138 | -61.1114 | 62.1918 | 0.3365 | -0.045914 | -0.079414 | 0.10907 | -0.018055 | -0.083297 | 0.046747 | -61.2396 | 62.2147 | -61.1984 | -61.1389 | 62.0956 | 0.14191 | -0.091553 | 0.19226 | 62.0636 | -61.2076 | -0.086975 | 0.022889 | -0.12817 | -0.027466 | -0.09613 | -0.096131 | -0.12817 | -0.041199 | 61.0199 | 61.3037 | 123.2071 | 123.3261 | -0.12817 | 123.175 | 61.2534 | -0.096131 | 123.3261 | -0.12817 | 61.2534 | 123.2071 | 123.175 | -123.3902 | -123.3994
267.6562 | 123.4039 | -61.1069 | 62.1597 | 0.67219 | -0.044846 | -0.080482 | 0.10266 | -0.015918 | -0.074752 | 0.037134 | -61.2625 | 62.1872 | -61.2122 | -61.1481 | 62.0728 | 0.12817 | -0.09613 | 0.14648 | 62.0636 | -61.1755 | -0.10529 | 0.027466 | -0.15564 | -0.041198 | -0.086975 | -0.068664 | -0.09613 | -0.050354 | 61.0107 | 61.2534 | 123.1796 | 123.2941 | -0.15564 | 123.1705 | 61.235 | -0.068664 | 123.2941 | -0.15564 | 61.235 | 123.1796 | 123.1705 | -123.3719 | -123.3353
268.6562 | 123.4085 | -61.0703 | 62.1735 | 0.55012 | -0.056596 | -0.091163 | 0.10159 | -0.0095097 | -0.07582 | 0.038202 | -61.2167 | 62.1643 | -61.1984 | -61.2167 | 62.0407 | 0.07782 | -0.045776 | 0.09613 | 62.0819 | -61.1984 | -0.12817 | -0.009155 | -0.14648 | -0.14648 | -0.13275 | -0.12817 | -0.091553 | -0.018311 | 61.0245 | 61.1664 | 123.111 | 123.2346 | -0.14648 | 123.1522 | 61.1481 | -0.12817 | 123.2346 | -0.14648 | 61.1481 | 123.111 | 123.1522 | -123.3719 | -123.3719
269.6562 | 123.4863 | -61.0428 | 62.1597 | 0.58064 | -0.049119 | -0.08689 | 0.099459 | -0.021259 | -0.080092 | 0.042474 | -61.1893 | 62.1414 | -61.1847 | -61.29 | 61.9766 | 0.009155 | 0.041199 | 0.004578 | 62.1185 | -61.2396 | -0.14191 | -0.018311 | -0.14648 | -0.24719 | -0.1831 | -0.19684 | -0.041199 | -0.004578 | 61.084 | 61.0474 | 123.0194 | 123.1842 | -0.14648 | 123.1613 | 61.0519 | -0.19684 | 123.1842 | -0.14648 | 61.0519 | 123.0194 | 123.1613 | -123.3444 | -123.3994
270.6562 | 123.4863 | -61.0565 | 62.1689 | 0.58064 | -0.064072 | -0.093299 | 0.098391 | -0.033008 | -0.071547 | 0.047815 | -61.203 | 62.1597 | -61.1893 | -61.2579 | 61.9995 | 0.036621 | 0.022888 | 0.036621 | 62.1002 | -61.2122 | -0.13275 | -0.009155 | -0.14648 | -0.20142 | -0.16937 | -0.15564 | -0.068664 | -0.013733 | 61.0794 | 61.0931 | 123.056 | 123.2162 | -0.14648 | 123.1567 | 61.0931 | -0.15564 | 123.2162 | -0.14648 | 61.0931 | 123.056 | 123.1567 | -123.3582 | -123.381
271.7031 | 123.4314 | -61.0657 | 62.1872 | -0.12126 | -0.04271 | -0.10505 | 0.11121 | -0.016986 | -0.077956 | 0.048883 | -61.1572 | 62.2101 | -61.1893 | -61.1938 | 62.0361 | 0.10529 | -0.032043 | 0.10986 | 62.114 | -61.2167 | -0.1236 | 0.022888 | -0.091553 | -0.12817 | -0.15106 | -0.15106 | -0.073242 | 0.032043 | 61.0336 | 61.1755 | 123.1018 | 123.2758 | -0.091553 | 123.1796 | 61.171 | -0.15106 | 123.2758 | -0.091553 | 61.171 | 123.1018 | 123.1796 | -123.3765 | -123.4039
272.6562 | 123.4268 | -61.0794 | 62.1689 | 0.50435 | -0.057664 | -0.084754 | 0.090914 | -0.012714 | -0.085433 | 0.045679 | -61.235 | 62.2101 | -61.1893 | -61.1984 | 62.0316 | 0.07782 | -0.050354 | 0.11444 | 62.0773 | -61.2167 | -0.10986 | 0.041199 | -0.15564 | -0.11902 | -0.13733 | -0.13733 | -0.091552 | -0.045776 | 61.0291 | 61.1938 | 123.111 | 123.2895 | -0.15564 | 123.1567 | 61.1572 | -0.13733 | 123.2895 | -0.15564 | 61.1572 | 123.111 | 123.1567 | -123.3582 | -123.3856
273.6562 | 123.4131 | -61.084 | 62.2238 | 0.32124 | -0.048051 | -0.08689 | 0.11548 | -0.015918 | -0.079024 | 0.046747 | -61.2442 | 62.2009 | -61.1893 | -61.1526 | 62.2421 | 0.10071 | -0.23346 | -0.027466 | 62.0499 | -61.203 | -0.10529 | -0.022888 | -0.16022 | -0.068665 | 0.01831 | -0.11902 | -0.17395 | -0.054932 | 60.8505 | 61.0565 | 123.3261 | 123.2849 | -0.16022 | 123.1338 | 61.1847 | -0.11902 | 123.2849 | -0.16022 | 61.1847 | 123.3261 | 123.1338 | -123.4131 | -123.4268
274.6562 | 123.381 | -61.116 | 62.1735 | 0.24495 | -0.054459 | -0.078345 | 0.10694 | -0.0095097 | -0.082229 | 0.053156 | -61.2167 | 62.2147 | -61.1893 | -61.1481 | 62.0911 | 0.14191 | -0.11444 | 0.16937 | 62.0636 | -61.1847 | -0.073242 | 0.041199 | -0.10071 | -0.032043 | -0.082398 | -0.068664 | -0.10986 | -0.027466 | 61.0016 | 61.2854 | 123.2071 | 123.3307 | -0.10071 | 123.1796 | 61.2579 | -0.068664 | 123.3307 | -0.10071 | 61.2579 | 123.2071 | 123.1796 | -123.3627 | -123.3582
275.6562 | 123.3673 | -61.0886 | 62.2055 | -3.0967 | -0.055527 | -0.080482 | 0.08771 | -0.015918 | -0.084365 | 0.042474 | -61.1847 | 62.2147 | -61.1938 | -61.1664 | 62.0316 | 0.10986 | -0.082397 | 0.15564 | 62.1002 | -61.1938 | -0.10529 | 0.009156 | -0.09613 | -0.07782 | -0.17395 | -0.10529 | -0.10529 | 0.009156 | 61.0062 | 61.2442 | 123.1201 | 123.3032 | -0.09613 | 123.1888 | 61.1984 | -0.10529 | 123.3032 | -0.09613 | 61.1984 | 123.1201 | 123.1888 | -123.3994 | -123.3994
276.7188 | 123.4863 | -61.0474 | 62.1323 | 0.55012 | -0.063004 | -0.092231 | 0.084505 | -0.021259 | -0.10252 | 0.051019 | -61.1755 | 62.059 | -61.1755 | -61.3495 | 61.94 | -0.009155 | 0.068665 | 0.018311 | 62.1231 | -61.2259 | -0.12817 | -0.073242 | -0.12817 | -0.30212 | -0.19226 | -0.17853 | -0.009155 | 0 | 61.116 | 61.0657 | 122.9874 | 123.1064 | -0.12817 | 123.1705 | 61.0382 | -0.17853 | 123.1064 | -0.12817 | 61.0382 | 122.9874 | 123.1705 | -123.3078 | -123.3582
277.6562 | 123.3948 | -61.1023 | 62.1872 | 0.64167 | -0.041642 | -0.090095 | 0.1048 | -0.015918 | -0.072616 | 0.047815 | -61.2259 | 62.2147 | -61.1755 | -61.1755 | 62.0499 | 0.11902 | -0.086975 | 0.14648 | 62.0819 | -61.1938 | -0.073242 | 0.027466 | -0.1236 | -0.073242 | -0.13733 | -0.091553 | -0.10529 | -0.050354 | 61.0153 | 61.2488 | 123.1522 | 123.317 | -0.1236 | 123.1842 | 61.2213 | -0.091553 | 123.317 | -0.1236 | 61.2213 | 123.1522 | 123.1842 | -123.3627 | -123.381
278.6562 | 123.3856 | -61.0794 | 62.2055 | 0.50435 | -0.044846 | -0.060187 | 0.095187 | -0.019123 | -0.086501 | 0.047815 | -61.5555 | 62.1323 | -61.203 | -61.1801 | 62.0911 | 0.14648 | -0.086975 | 0.16022 | 62.0865 | -61.2167 | -0.1236 | -0.073242 | -0.47607 | -0.10071 | -0.11444 | -0.13733 | -0.11902 | -0.35248 | 60.9924 | 61.2396 | 123.1705 | 123.2117 | -0.47607 | 123.1659 | 61.2259 | -0.13733 | 123.2117 | -0.47607 | 61.2259 | 123.1705 | 123.1659 | -123.4085 | -123.4222
279.7031 | 123.4085 | -61.0977 | 62.2101 | 0.93159 | -0.06514 | -0.078345 | 0.10159 | -0.022327 | -0.09291 | 0.046747 | -61.2122 | 62.1872 | -61.1938 | -61.1435 | 62.0865 | 0.17395 | -0.073242 | 0.15106 | 62.1368 | -61.171 | -0.096131 | -0.022888 | -0.11444 | -0.045777 | -0.1236 | -0.073242 | -0.073242 | -0.01831 | 61.0245 | 61.2488 | 123.1842 | 123.2849 | -0.11444 | 123.2346 | 61.2717 | -0.073242 | 123.2849 | -0.11444 | 61.2717 | 123.1842 | 123.2346 | -123.4039 | -123.381
280.6562 | 123.4222 | -61.0703 | 62.2055 | 0.15339 | -0.046983 | -0.10718 | 0.11014 | -0.016986 | -0.079024 | 0.040338 | -61.1481 | 62.2101 | -61.1572 | -61.1893 | 62.0544 | 0.091553 | -0.045776 | 0.11444 | 62.0911 | -61.1984 | -0.086976 | 0.004578 | -0.07782 | -0.11902 | -0.15106 | -0.12817 | -0.11444 | 0.009156 | 61.0245 | 61.1847 | 123.1247 | 123.2803 | -0.07782 | 123.1613 | 61.1618 | -0.12817 | 123.2803 | -0.07782 | 61.1618 | 123.1247 | 123.1613 | -123.3627 | -123.4039
281.7188 | 123.4039 | -61.0886 | 62.1552 | 0.42805 | -0.048051 | -0.074073 | 0.10159 | -0.018055 | -0.087569 | 0.049951 | -61.2213 | 62.1643 | -61.1847 | -61.1984 | 62.0499 | 0.09613 | -0.068665 | 0.13275 | 62.0773 | -61.1893 | -0.09613 | 0.009156 | -0.13275 | -0.10986 | -0.10528 | -0.10071 | -0.077819 | -0.036621 | 61.0199 | 61.2213 | 123.1384 | 123.2529 | -0.13275 | 123.1659 | 61.1847 | -0.10071 | 123.2529 | -0.13275 | 61.1847 | 123.1384 | 123.1659 | -123.3398 | -123.3444
282.6562 | 123.3902 | -61.0657 | 62.1918 | 0.30598 | -0.045914 | -0.065528 | 0.099459 | 0.00010333 | -0.079024 | 0.049951 | -61.1664 | 62.1826 | -61.1618 | -61.1984 | 62.0544 | 0.12817 | -0.059509 | 0.11444 | 62.0865 | -61.1938 | -0.09613 | -0.009155 | -0.10071 | -0.13275 | -0.13733 | -0.12817 | -0.10529 | -0.004578 | 61.0062 | 61.1801 | 123.1201 | 123.2483 | -0.10071 | 123.1522 | 61.1938 | -0.12817 | 123.2483 | -0.10071 | 61.1938 | 123.1201 | 123.1522 | -123.3536 | -123.3856
283.7188 | 123.4177 | -61.1069 | 62.1735 | 0.30598 | -0.052323 | -0.084754 | 0.10053 | -0.016986 | -0.072616 | 0.049951 | -61.1893 | 62.1964 | -61.171 | -61.1572 | 62.059 | 0.13733 | -0.091553 | 0.13275 | 62.1002 | -61.1984 | -0.064086 | 0.022888 | -0.082397 | -0.050354 | -0.11444 | -0.091552 | -0.073242 | -0.018311 | 61.0153 | 61.2396 | 123.1659 | 123.3032 | -0.082397 | 123.2071 | 61.2442 | -0.091552 | 123.3032 | -0.082397 | 61.2442 | 123.1659 | 123.2071 | -123.3444 | -123.3719
284.6562 | 123.3765 | -61.0703 | 62.1735 | 0.18391 | -0.046983 | -0.071937 | 0.10587 | -0.01485 | -0.069411 | 0.045679 | -61.1893 | 62.2284 | -61.1618 | -61.1984 | 62.0544 | 0.10986 | -0.073242 | 0.13733 | 62.1048 | -61.2213 | -0.091553 | 0.054932 | -0.11902 | -0.12817 | -0.11902 | -0.15106 | -0.068665 | -0.027466 | 60.997 | 61.2076 | 123.1247 | 123.2986 | -0.11902 | 123.175 | 61.1801 | -0.15106 | 123.2986 | -0.11902 | 61.1801 | 123.1247 | 123.175 | -123.3353 | -123.3948
285.6562 | 123.4177 | -61.0748 | 62.1964 | 0.10762 | -0.054459 | -0.079414 | 0.10373 | -0.0084417 | -0.071547 | 0.046747 | -61.1481 | 62.2147 | -61.1801 | -61.203 | 62.0407 | 0.10986 | -0.041199 | 0.1236 | 62.1048 | -61.2259 | -0.10529 | 0.018311 | -0.073242 | -0.12817 | -0.15564 | -0.15106 | -0.091553 | 0.032044 | 61.0336 | 61.1984 | 123.1155 | 123.2895 | -0.073242 | 123.1796 | 61.1847 | -0.15106 | 123.2895 | -0.073242 | 61.1847 | 123.1155 | 123.1796 | -123.3765 | -123.4222
286.7031 | 123.3765 | -61.0977 | 62.2055 | -0.39592 | -0.052323 | -0.096503 | 0.10053 | -0.0095097 | -0.085433 | 0.051019 | -61.235 | 62.1689 | -61.2122 | -61.1481 | 62.0682 | 0.15106 | -0.09613 | 0.16022 | 62.1185 | -61.1755 | -0.11444 | -0.036621 | -0.13733 | -0.050354 | -0.13733 | -0.07782 | -0.086975 | -0.022888 | 61.0016 | 61.2579 | 123.1659 | 123.2666 | -0.13733 | 123.2162 | 61.2488 | -0.07782 | 123.2666 | -0.13733 | 61.2488 | 123.1659 | 123.2162 | -123.4177 | -123.381
287.6562 | 123.436 | -61.0886 | 62.2009 | -0.060229 | -0.056596 | -0.10825 | 0.10053 | -0.01485 | -0.072616 | 0.051019 | -61.1481 | 62.2284 | -61.1481 | -61.2167 | 62.0087 | 0.11444 | -0.032043 | 0.09613 | 62.1323 | -61.2122 | -0.059509 | 0.027466 | -0.059509 | -0.12817 | -0.19226 | -0.1236 | -0.068665 | 0 | 61.0565 | 61.1847 | 123.0972 | 123.317 | -0.059509 | 123.2208 | 61.203 | -0.1236 | 123.317 | -0.059509 | 61.203 | 123.0972 | 123.2208 | -123.349 | -123.4131
288.7031 | 123.4039 | -61.0657 | 62.233 | -0.21282 | -0.060868 | -0.10078 | 0.099459 | -0.0041687 | -0.087569 | 0.043542 | -61.2167 | 62.2055 | -61.1755 | -61.1893 | 62.0499 | 0.16022 | -0.07782 | 0.14648 | 62.1414 | -61.1847 | -0.10986 | -0.027466 | -0.15106 | -0.1236 | -0.1831 | -0.11902 | -0.091553 | -0.041199 | 60.9879 | 61.2122 | 123.1155 | 123.2712 | -0.15106 | 123.2071 | 61.2259 | -0.11902 | 123.2712 | -0.15106 | 61.2259 | 123.1155 | 123.2071 | -123.4085 | -123.4177
289.6562 | 123.4543 | -61.0611 | 62.178 | 0.00080561 | -0.056596 | -0.08689 | 0.10053 | -0.018055 | -0.083297 | 0.037134 | -61.1481 | 62.1918 | -61.1755 | -61.2213 | 62.0224 | 0.091553 | -0.027466 | 0.10071 | 62.1506 | -61.2076 | -0.11444 | 0.013732 | -0.086975 | -0.16022 | -0.15564 | -0.14648 | -0.027466 | 0.027466 | 61.0336 | 61.1618 | 123.0835 | 123.2529 | -0.086975 | 123.2117 | 61.1526 | -0.14648 | 123.2529 | -0.086975 | 61.1526 | 123.0835 | 123.2117 | -123.3536 | -123.3856
290.6562 | 123.4451 | -61.0474 | 62.1872 | -0.075488 | -0.055527 | -0.090095 | 0.1283 | -0.018055 | -0.079024 | 0.043542 | -61.1343 | 62.2055 | -61.1481 | -61.2534 | 61.9858 | 0.11444 | -0.041199 | 0.073242 | 62.114 | -61.2259 | -0.10071 | 0.01831 | -0.086975 | -0.20599 | -0.20142 | -0.17853 | -0.073242 | 0.013733 | 61.0062 | 61.1206 | 123.0331 | 123.2529 | -0.086975 | 123.1613 | 61.1618 | -0.17853 | 123.2529 | -0.086975 | 61.1618 | 123.0331 | 123.1613 | -123.3353 | -123.4131
291.7188 | 123.4497 | -61.0748 | 62.1918 | 0.046583 | -0.048051 | -0.087958 | 0.097323 | -0.0095097 | -0.08116 | 0.046747 | -61.1526 | 62.1964 | -61.1618 | -61.2167 | 62.0041 | 0.09613 | -0.022888 | 0.10071 | 62.1414 | -61.2076 | -0.086975 | 0.004578 | -0.07782 | -0.14191 | -0.18768 | -0.13275 | -0.050354 | 0.009155 | 61.0519 | 61.1755 | 123.0789 | 123.2712 | -0.07782 | 123.2162 | 61.171 | -0.13275 | 123.2712 | -0.07782 | 61.171 | 123.0789 | 123.2162 | -123.3536 | -123.3994
292.6562 | 123.4497 | -61.0703 | 62.2009 | -0.04497 | -0.051255 | -0.10505 | 0.094119 | -0.0052367 | -0.083297 | 0.049951 | -61.1618 | 62.2147 | -61.1618 | -61.1984 | 62.0041 | 0.09613 | -0.036621 | 0.082397 | 62.1323 | -61.1938 | -0.091553 | 0.013733 | -0.091553 | -0.12817 | -0.19684 | -0.1236 | -0.068665 | 0 | 61.0336 | 61.1526 | 123.0743 | 123.2849 | -0.091553 | 123.2025 | 61.1664 | -0.1236 | 123.2849 | -0.091553 | 61.1664 | 123.0743 | 123.2025 | -123.3627 | -123.3948
293.6562 | 123.4268 | -61.0565 | 62.2284 | -0.15178 | -0.061936 | -0.097572 | 0.096255 | -0.020191 | -0.086501 | 0.052087 | -61.2213 | 62.1918 | -61.1755 | -61.171 | 62.0636 | 0.15106 | -0.07782 | 0.14648 | 62.1368 | -61.1801 | -0.11902 | -0.036622 | -0.16479 | -0.11444 | -0.16479 | -0.1236 | -0.091553 | -0.045776 | 60.9787 | 61.203 | 123.1201 | 123.2483 | -0.16479 | 123.1934 | 61.2076 | -0.1236 | 123.2483 | -0.16479 | 61.2076 | 123.1201 | 123.1934 | -123.4039 | -123.4085
294.6562 | 123.3948 | -61.0611 | 62.2101 | 2.015 | -0.046983 | -0.08689 | 0.086642 | -0.0084417 | -0.089705 | 0.043542 | -61.235 | 62.178 | -61.203 | -61.171 | 62.0728 | 0.19226 | -0.073242 | 0.15564 | 62.1368 | -61.2076 | -0.14191 | -0.032043 | -0.17395 | -0.10986 | -0.13733 | -0.14648 | -0.073242 | -0.032043 | 60.9879 | 61.2167 | 123.1338 | 123.2391 | -0.17395 | 123.1979 | 61.2534 | -0.14648 | 123.2391 | -0.17395 | 61.2534 | 123.1338 | 123.1979 | -123.4131 | -123.4177
295.7188 | 123.4222 | -61.0886 | 62.1964 | -0.35015 | -0.060868 | -0.084754 | 0.091982 | -0.0063047 | -0.087569 | 0.046747 | -61.2213 | 62.1918 | -61.1938 | -61.1801 | 62.059 | 0.11444 | -0.07782 | 0.32959 | 62.1689 | -61.1847 | -0.10529 | -0.004578 | -0.13275 | -0.091553 | -0.13733 | -0.09613 | -0.027466 | -0.027465 | 61.0107 | 61.4182 | 123.1476 | 123.2803 | -0.13275 | 123.2574 | 61.203 | -0.09613 | 123.2803 | -0.13275 | 61.203 | 123.1476 | 123.2574 | -123.3902 | -123.381
296.6562 | 123.4177 | -61.0611 | 62.1918 | -0.060229 | -0.063004 | -0.10398 | 0.10159 | -0.025531 | -0.076888 | 0.045679 | -61.1893 | 62.1872 | -61.1801 | -61.1847 | 62.0544 | 0.15564 | -0.10529 | 0.16022 | 62.1277 | -61.171 | -0.11902 | -0.004577 | -0.12817 | -0.1236 | -0.13733 | -0.10986 | -0.064086 | -0.009155 | 60.9558 | 61.2213 | 123.1155 | 123.2483 | -0.12817 | 123.1888 | 61.2167 | -0.10986 | 123.2483 | -0.12817 | 61.2167 | 123.1155 | 123.1888 | -123.3719 | -123.3627
297.6562 | 123.4039 | -61.0565 | 62.2192 | -0.15178 | -0.052323 | -0.084754 | 0.10907 | -0.016986 | -0.080092 | 0.053156 | -61.1984 | 62.2147 | -61.1847 | -61.171 | 62.0499 | 0.13733 | -0.059509 | 0.15106 | 62.1277 | -61.1755 | -0.12817 | -0.004577 | -0.14191 | -0.11444 | -0.16937 | -0.11902 | -0.091552 | -0.013733 | 60.997 | 61.2076 | 123.1064 | 123.2712 | -0.14191 | 123.1842 | 61.1938 | -0.11902 | 123.2712 | -0.14191 | 61.1938 | 123.1064 | 123.1842 | -123.4039 | -123.3948
298.7188 | 123.436 | -61.0794 | 62.1872 | 0.061841 | -0.046983 | -0.089027 | 0.10907 | -0.0095097 | -0.079024 | 0.038202 | -61.1481 | 62.1964 | -61.2076 | -61.2625 | 61.9766 | 0.091553 | -0.068665 | 0.10071 | 62.1094 | -61.2213 | -0.12817 | 0.009155 | -0.068664 | -0.1831 | -0.21057 | -0.14191 | -0.07782 | 0.05951 | 61.0107 | 61.1801 | 123.056 | 123.2758 | -0.068664 | 123.1888 | 61.171 | -0.14191 | 123.2758 | -0.068664 | 61.171 | 123.056 | 123.1888 | -123.3948 | -123.4085
299.6562 | 123.3856 | -61.1114 | 62.2055 | 0.18391 | -0.053391 | -0.084754 | 0.099459 | -0.01485 | -0.084365 | 0.040338 | -61.2167 | 62.1872 | -61.1847 | -61.1801 | 62.0499 | 0.13275 | -0.086975 | 0.16022 | 62.1231 | -61.1984 | -0.073242 | -0.01831 | -0.10529 | -0.068665 | -0.15564 | -0.086975 | -0.082397 | -0.032044 | 61.0245 | 61.2717 | 123.1613 | 123.2986 | -0.10529 | 123.2346 | 61.2442 | -0.086975 | 123.2986 | -0.10529 | 61.2442 | 123.1613 | 123.2346 | -123.3902 | -123.4039
300.6562 | 123.4222 | -61.0657 | 62.2147 | -0.30437 | -0.074754 | -0.097572 | 0.088778 | -0.025531 | -0.083297 | 0.047815 | -61.1481 | 62.1414 | -61.1526 | -61.2534 | 61.9949 | 0.10986 | -0.022888 | 0.10529 | 62.1368 | -61.2076 | -0.086975 | -0.073243 | -0.082397 | -0.18768 | -0.21973 | -0.14191 | -0.07782 | 0.004578 | 61.0428 | 61.171 | 123.0606 | 123.2071 | -0.082397 | 123.2025 | 61.1755 | -0.14191 | 123.2071 | -0.082397 | 61.1755 | 123.0606 | 123.2025 | -123.3673 | -123.4222
301.7031 | 123.468 | -61.0245 | 62.178 | 0.18391 | -0.071549 | -0.10398 | 0.079165 | -0.023395 | -0.10466 | 0.059564 | -61.1847 | 62.0956 | -61.1572 | -61.3312 | 61.9537 | 0.018311 | 0.045776 | 0.032043 | 62.1597 | -61.235 | -0.13275 | -0.082398 | -0.16022 | -0.3067 | -0.22431 | -0.21057 | -0.018311 | -0.027465 | 61.0703 | 61.0565 | 122.9782 | 123.1201 | -0.16022 | 123.1842 | 61.0428 | -0.21057 | 123.1201 | -0.16022 | 61.0428 | 122.9782 | 123.1842 | -123.3353 | -123.4131
302.6562 | 123.3948 | -61.0657 | 62.2101 | -0.24333 | -0.056596 | -0.10184 | 0.096255 | -0.028736 | -0.082229 | 0.044611 | -61.1847 | 62.1506 | -61.1618 | -61.1984 | 62.0499 | 0.16022 | -0.064087 | 0.12817 | 62.1323 | -61.2076 | -0.09613 | -0.059509 | -0.11902 | -0.13275 | -0.16022 | -0.14191 | -0.07782 | -0.022888 | 61.0016 | 61.1938 | 123.1155 | 123.2162 | -0.11902 | 123.1979 | 61.2259 | -0.14191 | 123.2162 | -0.11902 | 61.2259 | 123.1155 | 123.1979 | -123.3719 | -123.4177
303.7031 | 123.4543 | -61.0519 | 62.1643 | 0.27546 | -0.067277 | -0.090095 | 0.088778 | -0.028736 | -0.10039 | 0.044611 | -61.1938 | 62.0956 | -61.171 | -61.29 | 61.972 | 0.018311 | 0.009155 | 0.036621 | 62.1597 | -61.2076 | -0.11902 | -0.068665 | -0.14191 | -0.23804 | -0.19226 | -0.15564 | -0.004578 | -0.022889 | 61.0611 | 61.0886 | 123.024 | 123.1476 | -0.14191 | 123.2117 | 61.0703 | -0.15564 | 123.1476 | -0.14191 | 61.0703 | 123.024 | 123.2117 | -123.3353 | -123.3719
304.6562 | 123.3902 | -61.0657 | 62.2147 | -0.7011 | -0.054459 | -0.094367 | 0.1048 | -0.015918 | -0.088637 | 0.037134 | -61.2213 | 62.1826 | -61.171 | -61.1755 | 62.0224 | 0.13733 | -0.082397 | 0.15106 | 62.1323 | -61.1893 | -0.10529 | -0.032044 | -0.15564 | -0.10986 | -0.19226 | -0.1236 | -0.082398 | -0.050354 | 60.9833 | 61.2167 | 123.0881 | 123.2483 | -0.15564 | 123.1979 | 61.203 | -0.1236 | 123.2483 | -0.15564 | 61.203 | 123.0881 | 123.1979 | -123.3856 | -123.4039
305.7031 | 123.5321 | -61.0382 | 62.1643 | -0.12126 | -0.075822 | -0.10718 | 0.096255 | -0.020191 | -0.090773 | 0.058496 | -61.1069 | 62.114 | -61.1664 | -61.4456 | 61.8851 | 0.17853 | 0.2655 | -0.10071 | 62.1597 | -61.2579 | -0.12817 | -0.050354 | -0.068665 | -0.40741 | -0.27924 | -0.21973 | -0.004578 | 0.059509 | 61.3037 | 60.9375 | 122.9233 | 123.1522 | -0.068665 | 123.1979 | 61.2167 | -0.21973 | 123.1522 | -0.068665 | 61.2167 | 122.9233 | 123.1979 | -123.3307 | -123.4222
306.6562 | 123.436 | -61.0565 | 62.2284 | -0.28911 | -0.066209 | -0.12107 | 0.099459 | -0.020191 | -0.10252 | 0.047815 | -61.1435 | 62.1277 | -61.1572 | -61.2213 | 61.9812 | 0.086975 | -0.022888 | 0.091553 | 62.1506 | -61.1938 | -0.10071 | -0.10071 | -0.086975 | -0.16479 | -0.24719 | -0.13733 | -0.07782 | 0.013733 | 61.0336 | 61.1481 | 123.0377 | 123.1842 | -0.086975 | 123.2071 | 61.1435 | -0.13733 | 123.1842 | -0.086975 | 61.1435 | 123.0377 | 123.2071 | -123.3856 | -123.4222
307.7031 | 123.4222 | -61.0382 | 62.2238 | -0.21282 | -0.075822 | -0.10505 | 0.096255 | -0.021259 | -0.10252 | 0.048883 | -61.1664 | 62.1414 | -61.1618 | -61.2167 | 62.027 | 0.10071 | -0.07782 | 0.16022 | 62.1323 | -61.1664 | -0.1236 | -0.082398 | -0.12817 | -0.17853 | -0.19684 | -0.12817 | -0.091553 | -0.004578 | 60.9604 | 61.1984 | 123.0652 | 123.1796 | -0.12817 | 123.1705 | 61.1389 | -0.12817 | 123.1796 | -0.12817 | 61.1389 | 123.0652 | 123.1705 | -123.3856 | -123.3902
308.6562 | 123.5229 | -61.0199 | 62.1872 | -0.21282 | -0.056596 | -0.11466 | 0.078097 | -0.024463 | -0.095046 | 0.043542 | -61.116 | 62.0865 | -61.1435 | -61.322 | 61.9171 | -0.004578 | 0.07782 | 0 | 62.178 | -61.2442 | -0.1236 | -0.10071 | -0.096131 | -0.30212 | -0.27008 | -0.22431 | -0.009155 | 0.027466 | 61.0977 | 61.0199 | 122.937 | 123.1064 | -0.096131 | 123.1979 | 61.0153 | -0.22431 | 123.1064 | -0.096131 | 61.0153 | 122.937 | 123.1979 | -123.3307 | -123.4314
309.7188 | 123.5229 | -61.0153 | 62.1872 | -0.12126 | -0.060868 | -0.11039 | 0.097323 | -0.03194 | -0.10252 | 0.049951 | -60.9238 | 62.146 | -61.1069 | -61.2488 | 61.8942 | -0.027466 | 0.045776 | -0.013733 | 62.146 | -61.2259 | -0.091553 | -0.041199 | 0.091553 | -0.23346 | -0.29297 | -0.21057 | -0.041199 | 0.18311 | 61.0611 | 61.0016 | 122.9095 | 123.1613 | 0.091553 | 123.1613 | 60.9879 | -0.21057 | 123.1613 | 0.091553 | 60.9879 | 122.9095 | 123.1613 | -123.2941 | -123.4131
310.6562 | 123.5596 | -61.0153 | 62.2284 | -0.24333 | -0.073685 | -0.087958 | 0.084505 | -0.021259 | -0.09825 | 0.037134 | -61.1114 | 62.1048 | -61.1481 | -61.3174 | 61.9263 | -0.009155 | 0.068665 | 0 | 62.1735 | -61.2076 | -0.13275 | -0.1236 | -0.09613 | -0.30212 | -0.30212 | -0.19226 | -0.054932 | 0.036621 | 61.084 | 61.0153 | 122.9416 | 123.1201 | -0.09613 | 123.1888 | 61.0062 | -0.19226 | 123.1201 | -0.09613 | 61.0062 | 122.9416 | 123.1888 | -123.3765 | -123.436
311.6562 | 123.4818 | -61.0199 | 62.1918 | -1.6319 | -0.053391 | -0.10612 | 0.089846 | -0.020191 | -0.090773 | 0.044611 | -61.2808 | 62.1231 | -61.1526 | -61.3403 | 61.9171 | 0.022888 | 0.064087 | 0.009155 | 62.1689 | -61.2488 | -0.13275 | -0.068664 | -0.26093 | -0.32043 | -0.27466 | -0.22888 | -0.022888 | -0.12817 | 61.084 | 61.0291 | 122.937 | 123.143 | -0.26093 | 123.1888 | 61.0428 | -0.22888 | 123.143 | -0.26093 | 61.0428 | 122.937 | 123.1888 | -123.3444 | -123.4406
312.6562 | 123.4909 | -61.0016 | 62.2009 | -0.25859 | -0.071549 | -0.092231 | 0.091982 | -0.03194 | -0.10252 | 0.047815 | -61.1069 | 62.0956 | -61.1343 | -61.3174 | 61.9171 | 0 | 0.068665 | 0.009155 | 62.1506 | -61.2076 | -0.13275 | -0.10529 | -0.10529 | -0.31586 | -0.28381 | -0.20599 | -0.050354 | 0.027465 | 61.0703 | 61.0107 | 122.9187 | 123.0972 | -0.10529 | 123.1522 | 61.0016 | -0.20599 | 123.0972 | -0.10529 | 61.0016 | 122.9187 | 123.1522 | -123.3353 | -123.4085
313.7188 | 123.4818 | -61.0336 | 62.2009 | -0.79265 | -0.051255 | -0.10718 | 0.091982 | -0.021259 | -0.099318 | 0.054224 | -61.29 | 62.0956 | -61.1893 | -61.3174 | 61.9217 | 0.013733 | 0.068665 | 0.004578 | 62.1643 | -61.2167 | -0.15564 | -0.10529 | -0.25635 | -0.28381 | -0.27924 | -0.18311 | -0.036621 | -0.10071 | 61.1023 | 61.0382 | 122.9553 | 123.1293 | -0.25635 | 123.1979 | 61.0474 | -0.18311 | 123.1293 | -0.25635 | 61.0474 | 122.9553 | 123.1979 | -123.3902 | -123.4177
314.6562 | 123.5138 | -61.0428 | 62.1735 | 0.18391 | -0.061936 | -0.10184 | 0.084505 | -0.036213 | -0.10252 | 0.040338 | -61.1893 | 62.0728 | -61.1618 | -61.2808 | 61.9629 | 0.013733 | 0.036621 | 0.018311 | 62.1323 | -61.2076 | -0.11902 | -0.10071 | -0.14648 | -0.23804 | -0.21057 | -0.16479 | -0.041199 | -0.027466 | 61.0794 | 61.0611 | 123.0057 | 123.1155 | -0.14648 | 123.175 | 61.0565 | -0.16479 | 123.1155 | -0.14648 | 61.0565 | 123.0057 | 123.175 | -123.3353 | -123.381
315.6562 | 123.4863 | -61.0382 | 62.178 | 0.27546 | -0.073685 | -0.09864 | 0.095187 | -0.025531 | -0.10146 | 0.058496 | -61.1938 | 62.0865 | -61.1801 | -61.2488 | 61.9492 | 0.018311 | 0.022888 | 0.032043 | 62.1277 | -61.171 | -0.14191 | -0.091553 | -0.15564 | -0.21057 | -0.22888 | -0.13275 | -0.050354 | -0.013733 | 61.0611 | 61.0703 | 122.9874 | 123.1247 | -0.15564 | 123.1659 | 61.0565 | -0.13275 | 123.1247 | -0.15564 | 61.0565 | 122.9874 | 123.1659 | -123.3582 | -123.349
316.6562 | 123.4955 | -61.0245 | 62.1689 | 0.13813 | -0.067277 | -0.11146 | 0.094119 | -0.038349 | -0.1068 | 0.051019 | -61.1938 | 62.0682 | -61.171 | -61.2808 | 61.9583 | 0.018311 | 0.045776 | 0.027466 | 62.1552 | -61.2122 | -0.14648 | -0.10071 | -0.16937 | -0.25635 | -0.21057 | -0.18768 | -0.013733 | -0.022889 | 61.0703 | 61.0519 | 122.9828 | 123.0927 | -0.16937 | 123.1796 | 61.0428 | -0.18768 | 123.0927 | -0.16937 | 61.0428 | 122.9828 | 123.1796 | -123.3398 | -123.381
317.7031 | 123.4772 | -61.0428 | 62.1597 | 0.5196 | -0.063004 | -0.089027 | 0.1048 | -0.021259 | -0.096114 | 0.043542 | -61.1298 | 62.0911 | -61.1572 | -61.29 | 61.8484 | -0.11902 | 0.068665 | 0.059509 | 62.1368 | -61.2305 | -0.11444 | -0.068665 | -0.086975 | -0.24719 | -0.31128 | -0.18768 | -0.022888 | 0.027466 | 61.1115 | 61.1023 | 122.8912 | 123.1338 | -0.086975 | 123.1796 | 60.9238 | -0.18768 | 123.1338 | -0.086975 | 60.9238 | 122.8912 | 123.1796 | -123.317 | -123.3902
318.6562 | 123.5275 | -61.0062 | 62.1964 | -0.12126 | -0.073685 | -0.11146 | 0.091982 | -0.027668 | -0.093978 | 0.051019 | -61.1206 | 62.0865 | -61.1572 | -61.3266 | 61.908 | -0.018311 | 0.07782 | -0.004578 | 62.146 | -61.2213 | -0.15106 | -0.10986 | -0.11444 | -0.32043 | -0.28839 | -0.21515 | -0.050354 | 0.036622 | 61.084 | 61.0016 | 122.9141 | 123.0927 | -0.11444 | 123.1522 | 60.9879 | -0.21515 | 123.0927 | -0.11444 | 60.9879 | 122.9141 | 123.1522 | -123.3536 | -123.4177
319.7031 | 123.4589 | -61.0474 | 62.1597 | 0.39753 | -0.067277 | -0.10078 | 0.099459 | -0.037281 | -0.093978 | 0.033929 | -61.1801 | 62.059 | -61.171 | -61.2717 | 61.9583 | 0.022888 | 0.032043 | 0.027466 | 62.1368 | -61.203 | -0.1236 | -0.10071 | -0.13275 | -0.2243 | -0.20142 | -0.15564 | -0.022888 | -0.009156 | 61.0794 | 61.0748 | 123.0057 | 123.1064 | -0.13275 | 123.1842 | 61.0703 | -0.15564 | 123.1064 | -0.13275 | 61.0703 | 123.0057 | 123.1842 | -123.3307 | -123.3627
320.6562 | 123.4772 | -61.0474 | 62.1872 | 0.29072 | -0.06514 | -0.10612 | 0.091982 | -0.03194 | -0.10039 | 0.041406 | -61.2122 | 62.0865 | -61.1664 | -61.2717 | 61.9171 | 0.018311 | 0.07782 | 0.045776 | 62.1231 | -61.1938 | -0.11902 | -0.10071 | -0.1648 | -0.2243 | -0.27008 | -0.14649 | -0.064087 | -0.045776 | 61.1252 | 61.0931 | 122.9645 | 123.1338 | -0.1648 | 123.1705 | 61.0657 | -0.14649 | 123.1338 | -0.1648 | 61.0657 | 122.9645 | 123.1705 | -123.3536 | -123.381
321.6562 | 123.4589 | -61.0474 | 62.1826 | 0.42805 | -0.070481 | -0.075141 | 0.095187 | -0.029804 | -0.099318 | 0.040338 | -61.1984 | 62.0636 | -61.1618 | -61.2671 | 61.9766 | 0.009155 | 0.009155 | 0.041199 | 62.1048 | -61.2259 | -0.11444 | -0.11902 | -0.15106 | -0.21973 | -0.20599 | -0.17853 | -0.07782 | -0.036621 | 61.0565 | 61.0886 | 123.024 | 123.111 | -0.15106 | 123.1522 | 61.0565 | -0.17853 | 123.111 | -0.15106 | 61.0565 | 123.024 | 123.1522 | -123.3444 | -123.4085
322.7031 | 123.4909 | -61.0382 | 62.1094 | 0.71797 | -0.051255 | -0.082618 | 0.11121 | -0.030872 | -0.083297 | 0.040338 | -61.1298 | 62.1323 | -61.1893 | -61.29 | 61.94 | -0.022888 | 0.054932 | -0.013733 | 62.1048 | -61.2259 | -0.15106 | 0.022888 | -0.091553 | -0.25177 | -0.16937 | -0.18768 | -0.004578 | 0.059509 | 61.0931 | 61.0245 | 122.9782 | 123.1705 | -0.091553 | 123.143 | 61.0153 | -0.18768 | 123.1705 | -0.091553 | 61.0153 | 122.9782 | 123.143 | -123.2986 | -123.3353
323.6562 | 123.4497 | -61.0382 | 62.1277 | 0.35176 | -0.060868 | -0.12321 | 0.098391 | -0.037281 | -0.10252 | 0.034998 | -61.203 | 62.0773 | -61.1664 | -61.2396 | 61.9904 | 0.013733 | 0.013733 | 0.032043 | 62.114 | -61.203 | -0.12817 | -0.050354 | -0.1648 | -0.20142 | -0.13733 | -0.1648 | -0.013733 | -0.036621 | 61.0519 | 61.0703 | 123.0286 | 123.1155 | -0.1648 | 123.1522 | 61.0519 | -0.1648 | 123.1155 | -0.1648 | 61.0519 | 123.0286 | 123.1522 | -123.2941 | -123.3307
324.7031 | 123.3948 | -61.0703 | 62.2009 | 0.45857 | -0.035233 | -0.094367 | 0.11762 | -0.025531 | -0.08116 | 0.030725 | -61.2167 | 62.2009 | -61.1938 | -61.1526 | 61.7798 | 0.004578 | 0.013733 | 0.21057 | 62.0865 | -61.1847 | -0.1236 | 0 | -0.14648 | -0.082398 | -0.42114 | -0.11444 | -0.11444 | -0.022888 | 61.084 | 61.2808 | 122.85 | 123.2712 | -0.14648 | 123.1567 | 61.0748 | -0.11444 | 123.2712 | -0.14648 | 61.0748 | 122.85 | 123.1567 | -123.3948 | -123.3856
325.6562 | 123.4589 | -61.0428 | 62.1643 | 0.36702 | -0.069413 | -0.094367 | 0.086642 | -0.034076 | -0.11107 | 0.054224 | -61.1801 | 62.0956 | -61.1801 | -61.2579 | 61.9904 | 0.032043 | 0.018311 | 0.045776 | 62.1185 | -61.1847 | -0.13733 | -0.068665 | -0.13733 | -0.21515 | -0.17395 | -0.14191 | -0.045777 | 0 | 61.0611 | 61.0886 | 123.0331 | 123.1384 | -0.13733 | 123.1613 | 61.0748 | -0.14191 | 123.1384 | -0.13733 | 61.0748 | 123.0331 | 123.1613 | -123.3444 | -123.349
326.6562 | 123.4589 | -61.0382 | 62.1689 | 0.35176 | -0.069413 | -0.10505 | 0.098391 | -0.036213 | -0.10466 | 0.047815 | -61.1984 | 62.1002 | -61.171 | -61.2671 | 61.9949 | 0.045776 | 0.013733 | 0.050354 | 62.0819 | -61.2213 | -0.13275 | -0.068664 | -0.16022 | -0.22888 | -0.17395 | -0.18311 | -0.086975 | -0.027466 | 61.0519 | 61.0886 | 123.0331 | 123.1384 | -0.16022 | 123.1201 | 61.084 | -0.18311 | 123.1384 | -0.16022 | 61.084 | 123.0331 | 123.1201 | -123.3398 | -123.3902
327.7188 | 123.4497 | -61.0382 | 62.1918 | -0.13652 | -0.068345 | -0.11573 | 0.10907 | -0.020191 | -0.10146 | 0.059564 | -61.1481 | 62.1002 | -61.1435 | -61.2579 | 61.9675 | 0.041199 | 0.027466 | 0.064087 | 62.1368 | -61.1938 | -0.10529 | -0.091552 | -0.10986 | -0.21973 | -0.2243 | -0.15564 | -0.054931 | -0.004577 | 61.0657 | 61.1023 | 123.0057 | 123.1384 | -0.10986 | 123.175 | 61.0794 | -0.15564 | 123.1384 | -0.10986 | 61.0794 | 123.0057 | 123.175 | -123.3353 | -123.3856
328.6562 | 123.5092 | -61.0245 | 62.1872 | 0.53486 | -0.056596 | -0.062324 | 0.095187 | -0.030872 | -0.09291 | 0.049951 | -61.1435 | 62.0865 | -61.1481 | -61.3129 | 61.9217 | -0.018311 | 0.050354 | -0.17395 | 62.0911 | -61.2534 | -0.1236 | -0.10071 | -0.11902 | -0.28839 | -0.2655 | -0.22888 | -0.096131 | 0.004577 | 61.0748 | 60.8505 | 122.9462 | 123.111 | -0.11902 | 123.1155 | 61.0062 | -0.22888 | 123.111 | -0.11902 | 61.0062 | 122.9462 | 123.1155 | -123.3353 | -123.4406
329.7031 | 123.5046 | -61.0382 | 62.1506 | 0.58064 | -0.061936 | -0.090095 | 0.097323 | -0.028736 | -0.09291 | 0.051019 | -61.1618 | 62.146 | -61.1618 | -61.2579 | 61.972 | -0.018311 | 0.036621 | 0.004578 | 62.0682 | -61.2442 | -0.1236 | -0.004578 | -0.1236 | -0.21973 | -0.17853 | -0.20599 | -0.082398 | 0 | 61.0748 | 61.0428 | 123.0103 | 123.1842 | -0.1236 | 123.1064 | 61.0199 | -0.20599 | 123.1842 | -0.1236 | 61.0199 | 123.0103 | 123.1064 | -123.3124 | -123.3948
330.6562 | 123.5092 | -61.0062 | 62.1506 | -1.6929 | -0.06514 | -0.095435 | 0.097323 | -0.041553 | -0.09291 | 0.043542 | -61.0977 | 62.1368 | -61.1114 | -61.3449 | 61.9308 | -0.036621 | 0.064087 | 0.004578 | 62.1048 | -61.2213 | -0.10528 | -0.013733 | -0.091552 | -0.33874 | -0.21973 | -0.21515 | -0.045777 | 0.013733 | 61.0703 | 61.0107 | 122.937 | 123.143 | -0.091552 | 123.111 | 60.9695 | -0.21515 | 123.143 | -0.091552 | 60.9695 | 122.937 | 123.111 | -123.262 | -123.3719
331.6562 | 123.5184 | -61.0245 | 62.1414 | 0.53486 | -0.054459 | -0.08689 | 0.10694 | -0.035144 | -0.086501 | 0.042474 | -61.1435 | 62.114 | -61.1526 | -61.3174 | 62.027 | 0.036621 | 0.068665 | -0.009155 | 62.1414 | -61.2076 | -0.12817 | -0.027465 | -0.11902 | -0.29297 | -0.11444 | -0.18311 | 0 | 0.009155 | 61.0931 | 61.0153 | 123.0515 | 123.1384 | -0.11902 | 123.1659 | 61.0611 | -0.18311 | 123.1384 | -0.11902 | 61.0611 | 123.0515 | 123.1659 | -123.2941 | -123.349
332.7188 | 123.4772 | -61.0107 | 62.1643 | -0.16704 | -0.075822 | -0.1168 | 0.10373 | -0.020191 | -0.09825 | 0.049951 | -60.9055 | 62.1552 | -61.116 | -61.2808 | 61.9125 | 0.009155 | 0.059509 | 0.004578 | 62.1506 | -61.1984 | -0.10529 | -0.009156 | 0.10529 | -0.27008 | -0.25177 | -0.18768 | -0.013733 | 0.21057 | 61.0703 | 61.0153 | 122.9233 | 123.1659 | 0.10529 | 123.1613 | 61.0199 | -0.18768 | 123.1659 | 0.10529 | 61.0199 | 122.9233 | 123.1613 | -123.2803 | -123.3627
333.7188 | 123.4131 | -61.0611 | 62.2101 | 0.36702 | -0.049119 | -0.083686 | 0.12189 | -0.0095097 | -0.089705 | 0.041406 | -61.171 | 62.1918 | -61.1435 | -61.1343 | 62.0316 | 0.10529 | -0.050354 | 0.09613 | 62.1002 | -61.2076 | -0.082398 | -0.018311 | -0.10986 | -0.073242 | -0.17853 | -0.14648 | -0.10986 | -0.027465 | 61.0107 | 61.1572 | 123.0927 | 123.2529 | -0.10986 | 123.1613 | 61.1664 | -0.14648 | 123.2529 | -0.10986 | 61.1664 | 123.0927 | 123.1613 | -123.3536 | -123.4177
334.6562 | 123.4863 | -61.0428 | 62.1643 | 0.45857 | -0.063004 | -0.10184 | 0.085574 | -0.013782 | -0.10466 | 0.046747 | -61.1893 | 62.0819 | -61.171 | -61.2991 | 61.9858 | 0.036621 | 0.036621 | 0.045776 | 62.1277 | -61.2076 | -0.12817 | -0.082398 | -0.14648 | -0.25635 | -0.17853 | -0.16479 | -0.036621 | -0.018311 | 61.0794 | 61.0886 | 123.0286 | 123.1247 | -0.14648 | 123.1705 | 61.0794 | -0.16479 | 123.1247 | -0.14648 | 61.0794 | 123.0286 | 123.1705 | -123.3353 | -123.3719
335.6562 | 123.5184 | -61.0199 | 62.1597 | 0.55012 | -0.057664 | -0.089027 | 0.094119 | -0.026599 | -0.10573 | 0.042474 | -61.1526 | 62.0865 | -61.1618 | -61.2808 | 61.9308 | -0.027466 | 0.059509 | -0.022888 | 62.1231 | -61.2396 | -0.14191 | -0.073242 | -0.13275 | -0.26093 | -0.22888 | -0.21973 | -0.036621 | 0.009155 | 61.0794 | 60.997 | 122.9507 | 123.1064 | -0.13275 | 123.143 | 60.9924 | -0.21973 | 123.1064 | -0.13275 | 60.9924 | 122.9507 | 123.143 | -123.3215 | -123.3994
336.6562 | 123.5138 | -61.0016 | 62.1643 | 0.53486 | -0.061936 | -0.073005 | 0.097323 | -0.034076 | -0.088637 | 0.044611 | -61.1206 | 62.0819 | -61.1664 | -61.2717 | 61.8484 | -0.12817 | 0.073242 | 0.073242 | 62.1185 | -61.171 | -0.16479 | -0.082398 | -0.11902 | -0.27008 | -0.31586 | -0.16937 | -0.045777 | 0.045777 | 61.0748 | 61.0748 | 122.85 | 123.0835 | -0.11902 | 123.1201 | 60.8734 | -0.16937 | 123.0835 | -0.11902 | 60.8734 | 122.85 | 123.1201 | -123.3307 | -123.3353
337.7188 | 123.5092 | -61.0245 | 62.1506 | 0.092359 | -0.060868 | -0.092231 | 0.094119 | -0.037281 | -0.10466 | 0.045679 | -61.1618 | 62.114 | -61.1206 | -61.3129 | 61.9492 | 0.013733 | 0.068665 | 0.013733 | 62.146 | -61.2167 | -0.09613 | -0.036621 | -0.13733 | -0.28839 | -0.20142 | -0.19226 | -0.004578 | -0.041199 | 61.0931 | 61.0382 | 122.9736 | 123.1384 | -0.13733 | 123.1705 | 61.0382 | -0.19226 | 123.1384 | -0.13733 | 61.0382 | 122.9736 | 123.1705 | -123.2712 | -123.3673
338.6562 | 123.5092 | -61.0474 | 62.1506 | 0.55012 | -0.056596 | -0.10078 | 0.10907 | -0.041553 | -0.096114 | 0.049951 | -61.1389 | 62.0956 | -61.1481 | -61.3174 | 61.9354 | -0.018311 | 0.068665 | 0 | 62.1185 | -61.235 | -0.10071 | -0.054932 | -0.091553 | -0.27008 | -0.21515 | -0.18768 | -0.032044 | 0.009155 | 61.116 | 61.0474 | 122.9828 | 123.143 | -0.091553 | 123.1659 | 61.0291 | -0.18768 | 123.143 | -0.091553 | 61.0291 | 122.9828 | 123.1659 | -123.2986 | -123.3856
339.7031 | 123.3856 | -61.0657 | 62.178 | 0.44331 | -0.049119 | -0.085822 | 0.12403 | -0.03194 | -0.080092 | 0.043542 | -61.2305 | 62.2101 | -61.1984 | -61.1389 | 62.0499 | 0.1236 | -0.086975 | 0.14191 | 62.0499 | -61.1938 | -0.13275 | 0.032043 | -0.16479 | -0.073242 | -0.12817 | -0.12817 | -0.12817 | -0.032044 | 60.9787 | 61.2076 | 123.1155 | 123.2758 | -0.16479 | 123.1155 | 61.1893 | -0.12817 | 123.2758 | -0.16479 | 61.1893 | 123.1155 | 123.1155 | -123.3765 | -123.3719
340.6562 | 123.4772 | -61.0428 | 62.1414 | 0.47383 | -0.072617 | -0.12 | 0.091982 | -0.039417 | -0.097182 | 0.047815 | -61.1893 | 62.0956 | -61.1664 | -61.2854 | 61.9858 | 0.027466 | 0.018311 | 0.050354 | 62.1185 | -61.2213 | -0.1236 | -0.045776 | -0.14648 | -0.24261 | -0.15564 | -0.17853 | -0.022888 | -0.022888 | 61.0611 | 61.0931 | 123.0286 | 123.1384 | -0.14648 | 123.1613 | 61.0703 | -0.17853 | 123.1384 | -0.14648 | 61.0703 | 123.0286 | 123.1613 | -123.3078 | -123.3627
341.7031 | 123.3948 | -61.0794 | 62.2055 | 0.16865 | -0.038438 | -0.075141 | 0.11762 | -0.021259 | -0.074752 | 0.042474 | -61.1847 | 62.2009 | -61.1572 | -61.1435 | 62.059 | 0.13275 | -0.050354 | 0.10529 | 62.0956 | -61.203 | -0.07782 | -0.004577 | -0.10528 | -0.064087 | -0.14648 | -0.1236 | -0.10986 | -0.027465 | 61.0291 | 61.1847 | 123.1384 | 123.2803 | -0.10528 | 123.175 | 61.2122 | -0.1236 | 123.2803 | -0.10528 | 61.2122 | 123.1384 | 123.175 | -123.3627 | -123.4085
342.6562 | 123.5229 | -61.0336 | 62.146 | 0.61116 | -0.060868 | -0.074073 | 0.11121 | -0.026599 | -0.095046 | 0.054224 | -61.1481 | 62.1414 | -61.1801 | -61.3083 | 61.9308 | 0 | 0.068665 | -0.027466 | 62.1185 | -61.2213 | -0.14648 | -0.004578 | -0.11444 | -0.27466 | -0.21515 | -0.18768 | -0.027466 | 0.032044 | 61.1023 | 61.0062 | 122.9645 | 123.175 | -0.11444 | 123.1522 | 61.0336 | -0.18768 | 123.175 | -0.11444 | 61.0336 | 122.9645 | 123.1522 | -123.3261 | -123.3673
343.6562 | 123.5229 | -61.0382 | 62.1597 | 0.779 | -0.0598 | -0.096503 | 0.081301 | -0.025531 | -0.10252 | 0.049951 | -61.2396 | 62.0773 | -61.1847 | -61.3266 | 61.9446 | -0.013733 | 0.068665 | -0.032043 | 62.114 | -61.2579 | -0.14648 | -0.082397 | -0.20142 | -0.28839 | -0.21515 | -0.21973 | -0.045776 | -0.054932 | 61.1069 | 61.0062 | 122.9828 | 123.1155 | -0.20142 | 123.1522 | 61.0245 | -0.21973 | 123.1155 | -0.20142 | 61.0245 | 122.9828 | 123.1522 | -123.3444 | -123.4177
344.6562 | 123.4726 | -61.0611 | 62.1506 | 0.36702 | -0.052323 | -0.083686 | 0.088778 | -0.029804 | -0.09291 | 0.046747 | -61.1664 | 62.1094 | -61.1893 | -61.3083 | 61.9537 | 0.009155 | 0.041199 | 0.027466 | 62.1185 | -61.2122 | -0.12817 | -0.041199 | -0.10529 | -0.24719 | -0.19684 | -0.15106 | -0.032044 | 0.022888 | 61.1023 | 61.0886 | 123.0148 | 123.1705 | -0.10529 | 123.1796 | 61.0703 | -0.15106 | 123.1705 | -0.10529 | 61.0703 | 123.0148 | 123.1796 | -123.3398 | -123.3627
345.7031 | 123.3261 | -61.116 | 62.1597 | 0.39753 | -0.053391 | -0.091163 | 0.12082 | -0.026599 | -0.072616 | 0.036066 | -61.2213 | 62.1872 | -61.1984 | -61.1572 | 62.0544 | 0.1236 | -0.10529 | 0.14191 | 62.0728 | -61.2122 | -0.082397 | 0.027466 | -0.10529 | -0.041199 | -0.10529 | -0.09613 | -0.086975 | -0.022888 | 61.0107 | 61.2579 | 123.1705 | 123.3032 | -0.10529 | 123.1888 | 61.2396 | -0.09613 | 123.3032 | -0.10529 | 61.2396 | 123.1705 | 123.1888 | -123.3582 | -123.3719
346.6562 | 123.5092 | -61.0428 | 62.1506 | 0.50435 | -0.056596 | -0.099708 | 0.097323 | -0.030872 | -0.093978 | 0.048883 | -61.1755 | 62.1094 | -61.1664 | -61.3174 | 61.9537 | -0.013733 | 0.064087 | 0.009155 | 62.1048 | -61.2442 | -0.1236 | -0.041199 | -0.13275 | -0.27466 | -0.19684 | -0.20142 | -0.045777 | -0.009155 | 61.1069 | 61.0519 | 122.9965 | 123.1522 | -0.13275 | 123.1476 | 61.0291 | -0.20142 | 123.1522 | -0.13275 | 61.0291 | 122.9965 | 123.1476 | -123.317 | -123.3948
347.7031 | 123.4772 | -61.0474 | 62.1597 | 0.41279 | -0.057664 | -0.11146 | 0.095187 | -0.034076 | -0.085433 | 0.041406 | -61.1847 | 62.1094 | -61.1801 | -61.2808 | 61.9583 | 0.018311 | 0.022888 | 0.036621 | 62.1231 | -61.235 | -0.13275 | -0.050354 | -0.13733 | -0.23346 | -0.20142 | -0.18768 | -0.036621 | -0.004577 | 61.0703 | 61.084 | 123.0057 | 123.1567 | -0.13733 | 123.1705 | 61.0657 | -0.18768 | 123.1567 | -0.13733 | 61.0657 | 123.0057 | 123.1705 | -123.3398 | -123.3948
348.6562 | 123.468 | -61.0107 | 62.1689 | 0.3365 | -0.0598 | -0.12641 | 0.097323 | -0.030872 | -0.10359 | 0.045679 | -61.1938 | 62.0956 | -61.1755 | -61.2808 | 61.9904 | 0.027466 | 0.018311 | 0.050354 | 62.1094 | -61.2076 | -0.16479 | -0.073242 | -0.18311 | -0.27008 | -0.17853 | -0.19684 | -0.059509 | -0.018311 | 61.0291 | 61.0611 | 123.0011 | 123.1064 | -0.18311 | 123.1201 | 61.0382 | -0.19684 | 123.1064 | -0.18311 | 61.0382 | 123.0011 | 123.1201 | -123.3444 | -123.3765
349.7188 | 123.5092 | -61.0245 | 62.1597 | 0.73323 | -0.064072 | -0.092231 | 0.10266 | -0.042621 | -0.090773 | 0.046747 | -61.1526 | 62.0865 | -61.1664 | -61.3174 | 61.9492 | -0.027466 | 0.054932 | -0.004578 | 62.1185 | -61.235 | -0.14191 | -0.073242 | -0.12817 | -0.29297 | -0.21057 | -0.21057 | -0.041199 | 0.013733 | 61.0794 | 61.0199 | 122.9736 | 123.111 | -0.12817 | 123.143 | 60.997 | -0.21057 | 123.111 | -0.12817 | 60.997 | 122.9736 | 123.143 | -123.3261 | -123.3948
350.6562 | 123.4863 | -61.0382 | 62.1323 | 0.19917 | -0.075822 | -0.091163 | 0.096255 | -0.035144 | -0.099318 | 0.048883 | -61.1572 | 62.0728 | -61.1893 | -61.322 | 61.9446 | -0.009155 | 0.064087 | -0.009155 | 62.1277 | -61.235 | -0.15106 | -0.059509 | -0.11902 | -0.28381 | -0.18768 | -0.19684 | -0.004577 | 0.032043 | 61.1023 | 61.0291 | 122.9828 | 123.111 | -0.11902 | 123.1659 | 61.0291 | -0.19684 | 123.111 | -0.11902 | 61.0291 | 122.9828 | 123.1659 | -123.3215 | -123.3673
351.7188 | 123.4589 | -61.0565 | 62.1735 | 0.50435 | -0.064072 | -0.10184 | 0.085574 | -0.034076 | -0.10359 | 0.046747 | -61.1893 | 62.1002 | -61.171 | -61.2946 | 61.9492 | 0.013733 | 0.022888 | 0.041199 | 62.1094 | -61.203 | -0.11444 | -0.073242 | -0.13275 | -0.23804 | -0.2243 | -0.14648 | -0.064087 | -0.018311 | 61.0794 | 61.0977 | 123.0057 | 123.1567 | -0.13275 | 123.1659 | 61.0703 | -0.14648 | 123.1567 | -0.13275 | 61.0703 | 123.0057 | 123.1659 | -123.3444 | -123.3765
352.6562 | 123.4589 | -61.0519 | 62.1689 | 0.44331 | -0.064072 | -0.085822 | 0.098391 | -0.036213 | -0.10146 | 0.046747 | -61.1618 | 62.0819 | -61.171 | -61.2808 | 61.9537 | 0 | 0.041199 | 0.045776 | 62.1048 | -61.2076 | -0.11902 | -0.086975 | -0.10986 | -0.22888 | -0.21515 | -0.15564 | -0.064087 | 0.009155 | 61.0931 | 61.0977 | 123.0057 | 123.1338 | -0.10986 | 123.1567 | 61.0519 | -0.15564 | 123.1338 | -0.10986 | 61.0519 | 123.0057 | 123.1567 | -123.3398 | -123.3765
353.6562 | 123.4726 | -61.0474 | 62.1597 | 0.15339 | -0.061936 | -0.095435 | 0.095187 | -0.034076 | -0.097182 | 0.047815 | -61.1755 | 62.1185 | -61.1847 | -61.2808 | 61.972 | 0.027466 | 0.018311 | 0.064087 | 62.1231 | -61.2167 | -0.13733 | -0.041199 | -0.12817 | -0.23346 | -0.18768 | -0.16937 | -0.036621 | 0.009155 | 61.0657 | 61.1114 | 123.0194 | 123.1659 | -0.12817 | 123.1705 | 61.0748 | -0.16937 | 123.1659 | -0.12817 | 61.0748 | 123.0194 | 123.1705 | -123.3444 | -123.3765
354.6562 | 123.4909 | -61.0428 | 62.1414 | 0.12288 | -0.06514 | -0.10718 | 0.1048 | -0.030872 | -0.10252 | 0.048883 | -61.1847 | 62.0773 | -61.1893 | -61.2808 | 61.9766 | 0.022888 | 0.013733 | 0.045776 | 62.1506 | -61.2076 | -0.14648 | -0.064086 | -0.14191 | -0.23804 | -0.16479 | -0.16479 | 0.009156 | 0.004578 | 61.0565 | 61.0886 | 123.0194 | 123.1201 | -0.14191 | 123.1934 | 61.0657 | -0.16479 | 123.1201 | -0.14191 | 61.0657 | 123.0194 | 123.1934 | -123.3307 | -123.349
355.6562 | 123.4634 | -61.0336 | 62.1597 | 0.41279 | -0.079026 | -0.08689 | 0.094119 | -0.045826 | -0.10039 | 0.033929 | -61.1893 | 62.0911 | -61.1664 | -61.2579 | 61.9766 | 0.027466 | 0.009155 | 0.050354 | 62.114 | -61.2076 | -0.13275 | -0.068665 | -0.15564 | -0.22431 | -0.1831 | -0.17395 | -0.045776 | -0.022888 | 61.0428 | 61.084 | 123.0103 | 123.1247 | -0.15564 | 123.1476 | 61.0611 | -0.17395 | 123.1247 | -0.15564 | 61.0611 | 123.0103 | 123.1476 | -123.3261 | -123.3673
356.6562 | 123.4909 | -61.0245 | 62.1643 | 0.36702 | -0.063004 | -0.10718 | 0.1048 | -0.033008 | -0.10466 | 0.03927 | -61.1526 | 62.0819 | -61.1618 | -61.2946 | 61.9492 | -0.004578 | 0.050354 | 0.009155 | 62.1002 | -61.2305 | -0.13733 | -0.082398 | -0.12817 | -0.27008 | -0.21515 | -0.20599 | -0.064087 | 0.009155 | 61.0748 | 61.0336 | 122.9736 | 123.1064 | -0.12817 | 123.1247 | 61.0199 | -0.20599 | 123.1064 | -0.12817 | 61.0199 | 122.9736 | 123.1247 | -123.3261 | -123.3948
357.7031 | 123.381 | -61.1023 | 62.1826 | 0.22969 | -0.052323 | -0.10184 | 0.13043 | -0.03194 | -0.076888 | 0.043542 | -61.1801 | 62.2147 | -61.1755 | -61.1298 | 62.0544 | 0.1236 | -0.091553 | 0.15106 | 62.0819 | -61.1847 | -0.073242 | 0.032044 | -0.07782 | -0.027466 | -0.12817 | -0.082397 | -0.10071 | -0.004578 | 61.0107 | 61.2534 | 123.1567 | 123.317 | -0.07782 | 123.1842 | 61.2259 | -0.082397 | 123.317 | -0.07782 | 61.2259 | 123.1567 | 123.1842 | -123.3582 | -123.3673
358.6562 | 123.4772 | -61.0474 | 62.1826 | 0.32124 | -0.063004 | -0.11146 | 0.09305 | -0.026599 | -0.095046 | 0.054224 | -61.2076 | 62.0956 | -61.1801 | -61.2625 | 61.9766 | 0.032043 | 0.013733 | 0.041199 | 62.1094 | -61.2122 | -0.13275 | -0.086975 | -0.16022 | -0.21515 | -0.20599 | -0.1648 | -0.073242 | -0.027466 | 61.0611 | 61.0886 | 123.024 | 123.143 | -0.16022 | 123.1567 | 61.0794 | -0.1648 | 123.143 | -0.16022 | 61.0794 | 123.024 | 123.1567 | -123.3627 | -123.3948
359.6562 | 123.4818 | -61.0519 | 62.1689 | 0.24495 | -0.067277 | -0.11787 | 0.10053 | -0.035144 | -0.11107 | 0.046747 | -61.1664 | 62.1414 | -61.1801 | -61.2579 | 61.9858 | 0.032043 | -0.004578 | 0.027466 | 62.1231 | -61.2259 | -0.12817 | -0.027466 | -0.11444 | -0.20599 | -0.1831 | -0.17395 | -0.045776 | 0.013733 | 61.0474 | 61.0794 | 123.0377 | 123.1934 | -0.11444 | 123.175 | 61.084 | -0.17395 | 123.1934 | -0.11444 | 61.084 | 123.0377 | 123.175 | -123.349 | -123.3948
360.6562 | 123.4726 | -61.0519 | 62.1826 | 0.15339 | -0.054459 | -0.11466 | 0.094119 | -0.037281 | -0.1132 | 0.053156 | -61.1618 | 62.1185 | -61.1526 | -61.2625 | 61.9995 | 0.054932 | -0.009155 | 0.027466 | 62.1277 | -61.1938 | -0.10071 | -0.064087 | -0.10986 | -0.21057 | -0.1831 | -0.14191 | -0.054931 | -0.009155 | 61.0428 | 61.0794 | 123.0515 | 123.1705 | -0.10986 | 123.1796 | 61.1069 | -0.14191 | 123.1705 | -0.10986 | 61.1069 | 123.0515 | 123.1796 | -123.3353 | -123.3765
361.7031 | 123.436 | -61.0519 | 62.1689 | 0.27546 | -0.058732 | -0.085822 | 0.10587 | -0.036213 | -0.1068 | 0.036066 | -61.1938 | 62.1323 | -61.1481 | -61.2625 | 61.9766 | 0.045776 | 0.009155 | 0.059509 | 62.1277 | -61.2076 | -0.09613 | -0.036621 | -0.14191 | -0.21057 | -0.19226 | -0.15564 | -0.041198 | -0.045777 | 61.0611 | 61.1114 | 123.0286 | 123.1842 | -0.14191 | 123.1796 | 61.0977 | -0.15564 | 123.1842 | -0.14191 | 61.0977 | 123.0286 | 123.1796 | -123.317 | -123.3765
362.6562 | 123.4909 | -61.0428 | 62.1597 | 0.21443 | -0.06514 | -0.097572 | 0.094119 | -0.033008 | -0.1068 | 0.048883 | -61.2076 | 62.0911 | -61.1572 | -61.3037 | 61.9629 | 0.059509 | 0.018311 | 0.041199 | 62.1231 | -61.1984 | -0.11444 | -0.068665 | -0.16479 | -0.26093 | -0.19684 | -0.15564 | -0.036621 | -0.050354 | 61.0611 | 61.084 | 123.0057 | 123.1338 | -0.16479 | 123.1659 | 61.1023 | -0.15564 | 123.1338 | -0.16479 | 61.1023 | 123.0057 | 123.1659 | -123.317 | -123.3582
363.6562 | 123.4772 | -61.0474 | 62.1826 | 0.41279 | -0.054459 | -0.10078 | 0.097323 | -0.03194 | -0.096114 | 0.048883 | -61.1938 | 62.1185 | -61.1847 | -61.2625 | 61.9812 | 0.022888 | 0.018311 | 0.032043 | 62.1185 | -61.203 | -0.13733 | -0.064087 | -0.14649 | -0.21515 | -0.20142 | -0.15564 | -0.064087 | -0.009156 | 61.0657 | 61.0794 | 123.0286 | 123.1659 | -0.14649 | 123.1659 | 61.0703 | -0.15564 | 123.1659 | -0.14649 | 61.0703 | 123.0286 | 123.1659 | -123.3673 | -123.3856
364.7031 | 123.468 | -61.0062 | 62.146 | 0.62642 | -0.053391 | -0.093299 | 0.108 | -0.039417 | -0.089705 | 0.025385 | -61.1664 | 62.1323 | -61.1801 | -61.2579 | 61.9675 | 0.018311 | 0.041199 | 0.009155 | 62.0911 | -61.2259 | -0.17395 | -0.013733 | -0.16022 | -0.25177 | -0.17853 | -0.21973 | -0.054932 | 0.013733 | 61.0474 | 61.0153 | 122.9736 | 123.1384 | -0.16022 | 123.0972 | 61.0245 | -0.21973 | 123.1384 | -0.16022 | 61.0245 | 122.9736 | 123.0972 | -123.3261 | -123.3719
365.6562 | 123.4543 | -61.0245 | 62.1689 | 0.30598 | -0.068345 | -0.08155 | 0.09305 | -0.036213 | -0.10039 | 0.051019 | -61.1984 | 62.114 | -61.1847 | -61.2854 | 61.9949 | 0.073242 | 0.054932 | 0.059509 | 62.1597 | -61.1938 | -0.16022 | -0.054931 | -0.17395 | -0.26093 | -0.17395 | -0.16937 | -0.009155 | -0.013733 | 61.0794 | 61.084 | 123.0194 | 123.1384 | -0.17395 | 123.1842 | 61.0977 | -0.16937 | 123.1384 | -0.17395 | 61.0977 | 123.0194 | 123.1842 | -123.3536 | -123.3627
366.7188 | 123.4726 | -61.0382 | 62.178 | 0.24495 | -0.080094 | -0.079414 | 0.094119 | -0.037281 | -0.1132 | 0.051019 | -61.1984 | 62.0911 | -61.1755 | -61.2579 | 62.0773 | 0.091553 | 0.022888 | 0.054932 | 62.1185 | -61.2167 | -0.13733 | -0.086976 | -0.16022 | -0.21973 | -0.10071 | -0.17853 | -0.05951 | -0.022888 | 61.0611 | 61.0931 | 123.1155 | 123.1293 | -0.16022 | 123.1567 | 61.1298 | -0.17853 | 123.1293 | -0.16022 | 61.1298 | 123.1155 | 123.1567 | -123.3536 | -123.3948
367.6562 | 123.5184 | -61.0382 | 62.178 | 0.16865 | -0.067277 | -0.097572 | 0.099459 | -0.035144 | -0.10786 | 0.057428 | -61.1847 | 62.114 | -61.1572 | -61.2854 | 61.9492 | 0.013733 | 0.045776 | 0.045776 | 62.1323 | -61.1938 | -0.11902 | -0.064087 | -0.14648 | -0.24719 | -0.22888 | -0.15564 | -0.045777 | -0.027465 | 61.084 | 61.084 | 122.9874 | 123.1522 | -0.14648 | 123.1705 | 61.0519 | -0.15564 | 123.1522 | -0.14648 | 61.0519 | 122.9874 | 123.1705 | -123.3353 | -123.3719
368.7031 | 123.4863 | -61.0474 | 62.1597 | 0.48909 | -0.064072 | -0.11466 | 0.10053 | -0.03194 | -0.09291 | 0.044611 | -61.1252 | 62.1002 | -61.1572 | -61.2991 | 61.9446 | -0.013733 | 0.054932 | -0.009155 | 62.114 | -61.2442 | -0.10986 | -0.059509 | -0.07782 | -0.25177 | -0.21515 | -0.19684 | -0.045776 | 0.032044 | 61.1023 | 61.0382 | 122.9919 | 123.1476 | -0.07782 | 123.1613 | 61.0336 | -0.19684 | 123.1476 | -0.07782 | 61.0336 | 122.9919 | 123.1613 | -123.317 | -123.4039
369.6562 | 123.4589 | -61.0336 | 62.1689 | 0.26021 | -0.063004 | -0.058051 | 0.095187 | -0.028736 | -0.10146 | 0.042474 | -61.203 | 62.0911 | -61.1664 | -61.2625 | 61.972 | 0.032043 | -0.004578 | 0.054932 | 62.1048 | -61.1938 | -0.13275 | -0.07782 | -0.16937 | -0.22888 | -0.19684 | -0.16022 | -0.064087 | -0.036621 | 61.0291 | 61.0886 | 123.0057 | 123.1247 | -0.16937 | 123.1384 | 61.0657 | -0.16022 | 123.1247 | -0.16937 | 61.0657 | 123.0057 | 123.1384 | -123.3353 | -123.3627
370.6562 | 123.4497 | -61.0428 | 62.1918 | 0.41279 | -0.067277 | -0.12534 | 0.098391 | -0.034076 | -0.11534 | 0.045679 | -61.1801 | 62.1048 | -61.1847 | -61.2579 | 61.972 | 0.027466 | -0.009155 | 0.050354 | 62.1231 | -61.1847 | -0.14191 | -0.086975 | -0.13733 | -0.21515 | -0.21973 | -0.14191 | -0.068664 | 0.004577 | 61.0336 | 61.0931 | 123.0148 | 123.1476 | -0.13733 | 123.1659 | 61.0703 | -0.14191 | 123.1476 | -0.13733 | 61.0703 | 123.0148 | 123.1659 | -123.3765 | -123.3765
371.6562 | 123.4863 | -61.0382 | 62.1597 | 0.41279 | -0.064072 | -0.097572 | 0.096255 | -0.039417 | -0.11534 | 0.049951 | -61.203 | 62.0682 | -61.1664 | -61.2717 | 61.972 | 0.045776 | 0.013733 | 0.045776 | 62.1185 | -61.1893 | -0.12817 | -0.091553 | -0.1648 | -0.23346 | -0.18768 | -0.15106 | -0.041199 | -0.036621 | 61.0519 | 61.084 | 123.0103 | 123.1064 | -0.1648 | 123.1567 | 61.084 | -0.15106 | 123.1064 | -0.1648 | 61.084 | 123.0103 | 123.1567 | -123.3261 | -123.349
372.7031 | 123.3856 | -61.0794 | 62.1964 | 0.21443 | -0.046983 | -0.087958 | 0.1283 | -0.024463 | -0.08116 | 0.041406 | -61.1755 | 62.2009 | -61.1801 | -61.1252 | 62.0499 | 0.11444 | -0.073242 | 0.11444 | 62.0773 | -61.1893 | -0.10071 | 0.004578 | -0.09613 | -0.045776 | -0.14648 | -0.10986 | -0.11902 | 0.004578 | 61.0062 | 61.1938 | 123.1293 | 123.2803 | -0.09613 | 123.1567 | 61.1938 | -0.10986 | 123.2803 | -0.09613 | 61.1938 | 123.1293 | 123.1567 | -123.3765 | -123.3856
373.6562 | 123.4863 | -61.0291 | 62.178 | 0.16865 | -0.063004 | -0.10932 | 0.096255 | -0.035144 | -0.1068 | 0.048883 | -61.1847 | 62.1002 | -61.1801 | -61.2808 | 61.9629 | 0.027466 | 0.027466 | 0.027466 | 62.1048 | -61.1984 | -0.15106 | -0.07782 | -0.15564 | -0.25177 | -0.21515 | -0.16937 | -0.073243 | -0.004577 | 61.0565 | 61.0565 | 122.9919 | 123.1293 | -0.15564 | 123.1338 | 61.0565 | -0.16937 | 123.1293 | -0.15564 | 61.0565 | 122.9919 | 123.1338 | -123.3582 | -123.3765
374.6562 | 123.4818 | -61.0199 | 62.1735 | 0.44331 | -0.057664 | -0.12107 | 0.10159 | -0.022327 | -0.097182 | 0.047815 | -61.1755 | 62.1231 | -61.1755 | -61.2625 | 61.9812 | 0.054932 | 0.027466 | 0.054932 | 62.1185 | -61.1664 | -0.15564 | -0.050354 | -0.15564 | -0.24262 | -0.19226 | -0.14648 | -0.054932 | 0 | 61.0474 | 61.0748 | 123.0011 | 123.143 | -0.15564 | 123.1384 | 61.0748 | -0.14648 | 123.143 | -0.15564 | 61.0748 | 123.0011 | 123.1384 | -123.349 | -123.3398
375.6562 | 123.5001 | -61.0291 | 62.1689 | 0.12288 | -0.071549 | -0.099708 | 0.097323 | -0.040485 | -0.11 | 0.048883 | -61.1023 | 62.114 | -61.1801 | -61.2579 | 61.9995 | 0.068665 | -0.013733 | 0.022888 | 62.114 | -61.2213 | -0.15106 | -0.054931 | -0.073242 | -0.22888 | -0.16937 | -0.19226 | -0.054931 | 0.07782 | 61.0153 | 61.0519 | 123.0286 | 123.143 | -0.073242 | 123.143 | 61.0977 | -0.19226 | 123.143 | -0.073242 | 61.0977 | 123.0286 | 123.143 | -123.349 | -123.3902
376.6562 | 123.4772 | -61.0291 | 62.1689 | 0.26021 | -0.071549 | -0.10825 | 0.10053 | -0.034076 | -0.10359 | 0.046747 | -61.1938 | 62.1277 | -61.1526 | -61.2488 | 61.9217 | 0.059509 | 0.036621 | 0.064087 | 62.1185 | -61.1893 | -0.1236 | -0.041198 | -0.1648 | -0.21973 | -0.24719 | -0.16022 | -0.050354 | -0.041199 | 61.0657 | 61.0931 | 122.9507 | 123.1567 | -0.1648 | 123.1476 | 61.0886 | -0.16022 | 123.1567 | -0.1648 | 61.0886 | 122.9507 | 123.1476 | -123.3215 | -123.3582
377.7031 | 123.3719 | -61.0748 | 62.2055 | 0.29072 | -0.049119 | -0.089027 | 0.12403 | -0.023395 | -0.084365 | 0.041406 | -61.2122 | 62.1964 | -61.1664 | -61.116 | 62.0773 | 0.15106 | -0.10529 | 0.16022 | 62.0773 | -61.1847 | -0.091553 | -0.009155 | -0.13733 | -0.041199 | -0.12817 | -0.10986 | -0.12817 | -0.045776 | 60.9695 | 61.235 | 123.1522 | 123.2712 | -0.13733 | 123.1522 | 61.2259 | -0.10986 | 123.2712 | -0.13733 | 61.2259 | 123.1522 | 123.1522 | -123.3719 | -123.3902
378.6562 | 123.4589 | -61.0382 | 62.1597 | 0.30598 | -0.063004 | -0.087958 | 0.091982 | -0.037281 | -0.10039 | 0.049951 | -61.1893 | 62.0773 | -61.1664 | -61.2625 | 61.9812 | 0.041199 | 0 | 0.041199 | 62.114 | -61.1984 | -0.12817 | -0.082397 | -0.15106 | -0.2243 | -0.17853 | -0.16022 | -0.045776 | -0.022888 | 61.0382 | 61.0794 | 123.0194 | 123.1155 | -0.15106 | 123.1522 | 61.0794 | -0.16022 | 123.1155 | -0.15106 | 61.0794 | 123.0194 | 123.1522 | -123.3261 | -123.3582
379.6562 | 123.4909 | -61.0291 | 62.1826 | 0.44331 | -0.070481 | -0.12534 | 0.089846 | -0.037281 | -0.10252 | 0.05636 | -61.1893 | 62.1185 | -61.1664 | -61.2534 | 61.9766 | 0.041199 | 0.013733 | 0.041199 | 62.1185 | -61.1984 | -0.13733 | -0.064087 | -0.16022 | -0.2243 | -0.20599 | -0.16937 | -0.064087 | -0.022888 | 61.0428 | 61.0703 | 123.0057 | 123.1476 | -0.16022 | 123.1476 | 61.0703 | -0.16937 | 123.1476 | -0.16022 | 61.0703 | 123.0057 | 123.1476 | -123.349 | -123.381
380.7188 | 123.5001 | -61.0382 | 62.146 | 0.5196 | -0.056596 | -0.083686 | 0.097323 | -0.039417 | -0.10466 | 0.045679 | -61.1572 | 62.1002 | -61.1526 | -61.2946 | 61.9217 | -0.009155 | 0.064087 | -0.018311 | 62.114 | -61.2305 | -0.11444 | -0.045776 | -0.11902 | -0.25635 | -0.2243 | -0.19226 | -0.032043 | -0.004578 | 61.1023 | 61.0199 | 122.9599 | 123.1384 | -0.11902 | 123.1522 | 61.0291 | -0.19226 | 123.1384 | -0.11902 | 61.0291 | 122.9599 | 123.1522 | -123.2986 | -123.3765
381.6562 | 123.5001 | -61.0428 | 62.1643 | 0.38228 | -0.063004 | -0.11146 | 0.096255 | -0.037281 | -0.099318 | 0.054224 | -61.1847 | 62.114 | -61.171 | -61.2717 | 61.9766 | 0.050354 | -0.004578 | 0.059509 | 62.1002 | -61.2213 | -0.12817 | -0.050354 | -0.14191 | -0.22888 | -0.18768 | -0.17853 | -0.064087 | -0.013733 | 61.0382 | 61.1023 | 123.0194 | 123.1567 | -0.14191 | 123.143 | 61.0931 | -0.17853 | 123.1567 | -0.14191 | 61.0931 | 123.0194 | 123.143 | -123.3353 | -123.3856
382.6562 | 123.468 | -61.0519 | 62.1643 | 0.3365 | -0.063004 | -0.10932 | 0.10373 | -0.029804 | -0.10146 | 0.054224 | -61.1847 | 62.1094 | -61.1755 | -61.2762 | 61.9858 | 0.027466 | 0.009155 | 0.041199 | 62.1368 | -61.1893 | -0.1236 | -0.054932 | -0.13275 | -0.2243 | -0.17853 | -0.13733 | -0.027466 | -0.009155 | 61.0611 | 61.0931 | 123.0377 | 123.1613 | -0.13275 | 123.1888 | 61.0794 | -0.13733 | 123.1613 | -0.13275 | 61.0794 | 123.0377 | 123.1888 | -123.3398 | -123.3536
383.7031 | 123.4772 | -61.0474 | 62.1689 | 0.64167 | -0.048051 | -0.062324 | 0.11975 | -0.035144 | -0.084365 | 0.043542 | -61.1755 | 62.1689 | -61.1481 | -61.2076 | 62.0041 | 0.036621 | 0 | 0.045776 | 62.0773 | -61.2076 | -0.10071 | 0 | -0.12817 | -0.16022 | -0.16479 | -0.16022 | -0.091552 | -0.027466 | 61.0474 | 61.0931 | 123.0515 | 123.2162 | -0.12817 | 123.1247 | 61.084 | -0.16022 | 123.2162 | -0.12817 | 61.084 | 123.0515 | 123.1247 | -123.317 | -123.3765
384.6562 | 123.5184 | -61.0016 | 62.1552 | -0.65532 | -0.0598 | -0.094367 | 0.11334 | -0.024463 | -0.099318 | 0.042474 | -61.116 | 62.1185 | -61.1526 | -61.322 | 61.9171 | -0.032043 | 0.050354 | -0.004578 | 62.1368 | -61.2076 | -0.15106 | -0.036621 | -0.11444 | -0.32043 | -0.23804 | -0.20599 | -0.01831 | 0.036621 | 61.0519 | 60.997 | 122.9187 | 123.1201 | -0.11444 | 123.1384 | 60.9695 | -0.20599 | 123.1201 | -0.11444 | 60.9695 | 122.9187 | 123.1384 | -123.3078 | -123.3627
385.7188 | 123.4726 | -61.0245 | 62.1368 | 0.42805 | -0.051255 | -0.10612 | 0.098391 | -0.028736 | -0.11107 | 0.044611 | -61.1481 | 62.1094 | -61.1893 | -61.3129 | 61.9537 | -0.004578 | 0.045776 | -0.009155 | 62.1231 | -61.2259 | -0.16479 | -0.027466 | -0.1236 | -0.28839 | -0.18311 | -0.20142 | -0.013733 | 0.041199 | 61.0703 | 61.0153 | 122.9782 | 123.1338 | -0.1236 | 123.1476 | 61.0199 | -0.20142 | 123.1338 | -0.1236 | 61.0199 | 122.9782 | 123.1476 | -123.3261 | -123.3627
386.6562 | 123.5138 | -61.0107 | 62.1323 | 0.38228 | -0.064072 | -0.087958 | 0.096255 | -0.028736 | -0.10573 | 0.048883 | -61.1252 | 62.114 | -61.1526 | -61.2991 | 61.9446 | -0.004578 | 0.045776 | -0.004578 | 62.1048 | -61.2167 | -0.14191 | -0.01831 | -0.11444 | -0.28839 | -0.18768 | -0.20599 | -0.027466 | 0.027466 | 61.0565 | 61.0062 | 122.9553 | 123.1247 | -0.11444 | 123.1155 | 61.0062 | -0.20599 | 123.1247 | -0.11444 | 61.0062 | 122.9553 | 123.1155 | -123.2849 | -123.349
387.6562 | 123.4726 | -61.0519 | 62.1735 | 0.48909 | -0.056596 | -0.092231 | 0.08771 | -0.03194 | -0.11 | 0.044611 | -61.1847 | 62.1048 | -61.1572 | -61.2671 | 61.9858 | 0.041199 | 0.018311 | 0.032043 | 62.1094 | -61.2213 | -0.10529 | -0.068665 | -0.13275 | -0.21515 | -0.18768 | -0.16937 | -0.064087 | -0.027465 | 61.0703 | 61.084 | 123.0377 | 123.1567 | -0.13275 | 123.1613 | 61.0931 | -0.16937 | 123.1567 | -0.13275 | 61.0931 | 123.0377 | 123.1613 | -123.3307 | -123.3948
388.6562 | 123.4406 | -61.0428 | 62.1689 | 0.42805 | -0.061936 | -0.10291 | 0.099459 | -0.034076 | -0.1068 | 0.036066 | -61.1526 | 62.114 | -61.1481 | -61.2671 | 61.9492 | 0.004578 | 0.022888 | 0.022888 | 62.1048 | -61.1984 | -0.10529 | -0.054931 | -0.10986 | -0.2243 | -0.21973 | -0.15564 | -0.064087 | -0.004578 | 61.0657 | 61.0657 | 122.9919 | 123.1567 | -0.10986 | 123.1476 | 61.0474 | -0.15564 | 123.1567 | -0.10986 | 61.0474 | 122.9919 | 123.1476 | -123.317 | -123.3673
389.7031 | 123.4222 | -61.0565 | 62.1689 | 0.38228 | -0.056596 | -0.10398 | 0.12403 | -0.036213 | -0.084365 | 0.042474 | -61.203 | 62.2147 | -61.1984 | -61.1572 | 62.0499 | 0.10071 | -0.073242 | 0.09613 | 62.0865 | -61.1984 | -0.14191 | 0.045777 | -0.14648 | -0.10071 | -0.11902 | -0.14191 | -0.082397 | -0.004578 | 60.9833 | 61.1526 | 123.1064 | 123.2712 | -0.14648 | 123.143 | 61.1572 | -0.14191 | 123.2712 | -0.14648 | 61.1572 | 123.1064 | 123.143 | -123.3673 | -123.3673
390.6562 | 123.5367 | -61.0107 | 62.1368 | 0.5959 | -0.051255 | -0.083686 | 0.10053 | -0.030872 | -0.099318 | 0.048883 | -61.1343 | 62.1231 | -61.1801 | -61.3037 | 61.9354 | -0.018311 | 0.059509 | -0.045776 | 62.1368 | -61.2396 | -0.16937 | -0.013733 | -0.1236 | -0.29297 | -0.20142 | -0.22888 | 0 | 0.045777 | 61.0703 | 60.965 | 122.9462 | 123.1338 | -0.1236 | 123.1476 | 60.9924 | -0.22888 | 123.1338 | -0.1236 | 60.9924 | 122.9462 | 123.1476 | -123.317 | -123.3765
391.6562 | 123.5321 | -61.0382 | 62.1689 | 0.58064 | -0.064072 | -0.097572 | 0.10266 | -0.037281 | -0.10252 | 0.046747 | -61.1252 | 62.1414 | -61.171 | -61.29 | 61.9492 | -0.018311 | 0.050354 | -0.009155 | 62.1094 | -61.2076 | -0.13275 | -0.027466 | -0.086975 | -0.25177 | -0.21973 | -0.16937 | -0.059509 | 0.045776 | 61.0886 | 61.0291 | 122.9874 | 123.1796 | -0.086975 | 123.1476 | 61.0199 | -0.16937 | 123.1796 | -0.086975 | 61.0199 | 122.9874 | 123.1476 | -123.3398 | -123.3765
392.7031 | 123.4634 | -61.0382 | 62.2238 | -0.075488 | -0.057664 | -0.095435 | 0.12189 | -0.012714 | -0.069411 | 0.058496 | -61.1526 | 62.2421 | -61.171 | -61.1801 | 62.0361 | 0.12817 | -0.059509 | 0.086975 | 62.1094 | -61.1847 | -0.13275 | 0.01831 | -0.11444 | -0.14191 | -0.18768 | -0.14648 | -0.11444 | 0.01831 | 60.9787 | 61.1252 | 123.0743 | 123.2803 | -0.11444 | 123.1476 | 61.1664 | -0.14648 | 123.2803 | -0.11444 | 61.1664 | 123.0743 | 123.1476 | -123.3948 | -123.4085
393.6562 | 123.5275 | -61.0062 | 62.1826 | 0.53486 | -0.067277 | -0.10612 | 0.10159 | -0.021259 | -0.093978 | 0.053156 | -61.1252 | 62.1277 | -61.1618 | -61.2396 | 62.0499 | -0.14191 | -0.073242 | -0.009155 | 62.1368 | -61.203 | -0.15564 | -0.054931 | -0.11902 | -0.23346 | -0.13275 | -0.19684 | -0.045776 | 0.036621 | 60.9329 | 60.997 | 123.056 | 123.1339 | -0.11902 | 123.143 | 60.8643 | -0.19684 | 123.1339 | -0.11902 | 60.8643 | 123.056 | 123.143 | -123.3444 | -123.3856
394.6562 | 123.4955 | -61.0474 | 62.1506 | 0.65693 | -0.071549 | -0.090095 | 0.099459 | -0.03194 | -0.089705 | 0.042474 | -61.1526 | 62.1002 | -61.171 | -61.3083 | 61.94 | -0.009155 | 0.050354 | -0.027466 | 62.1506 | -61.2122 | -0.1236 | -0.050354 | -0.10529 | -0.26093 | -0.21057 | -0.1648 | 0 | 0.01831 | 61.0977 | 61.0199 | 122.9874 | 123.1476 | -0.10529 | 123.1979 | 61.0382 | -0.1648 | 123.1476 | -0.10529 | 61.0382 | 122.9874 | 123.1979 | -123.3215 | -123.3627
395.6562 | 123.5046 | -61.0199 | 62.1689 | -2.4559 | -0.066209 | -0.097572 | 0.099459 | -0.023395 | -0.099318 | 0.049951 | -61.0794 | 62.1368 | -61.1481 | -61.3358 | 61.9308 | -0.045776 | 0.036621 | -0.027466 | 62.1185 | -61.2167 | -0.12817 | -0.032043 | -0.05951 | -0.31586 | -0.23804 | -0.19684 | -0.050354 | 0.068664 | 61.0565 | 60.9924 | 122.9507 | 123.1567 | -0.05951 | 123.1384 | 60.9741 | -0.19684 | 123.1567 | -0.05951 | 60.9741 | 122.9507 | 123.1384 | -123.317 | -123.3856
396.6562 | 123.5367 | -61.0016 | 62.1735 | 0.5196 | -0.057664 | -0.11359 | 0.10587 | -0.035144 | -0.095046 | 0.049951 | -61.116 | 62.114 | -61.1481 | -61.3541 | 61.6882 | -0.045776 | 0.10986 | 0.041199 | 62.1552 | -61.203 | -0.14648 | -0.059509 | -0.11444 | -0.35248 | -0.48523 | -0.20142 | -0.018311 | 0.032043 | 61.1114 | 61.0428 | 122.6898 | 123.1155 | -0.11444 | 123.1567 | 60.9558 | -0.20142 | 123.1155 | -0.11444 | 60.9558 | 122.6898 | 123.1567 | -123.3215 | -123.3765
397.7031 | 123.3856 | -61.0703 | 62.2192 | 0.24495 | -0.048051 | -0.085822 | 0.12082 | -0.020191 | -0.084365 | 0.042474 | -61.1801 | 62.2284 | -61.1755 | -61.1481 | 62.059 | 0.12817 | -0.09613 | 0.11444 | 62.0956 | -61.1893 | -0.10529 | 0.009156 | -0.10986 | -0.07782 | -0.16022 | -0.11902 | -0.1236 | -0.004578 | 60.9741 | 61.1847 | 123.1293 | 123.2986 | -0.10986 | 123.1659 | 61.1984 | -0.11902 | 123.2986 | -0.10986 | 61.1984 | 123.1293 | 123.1659 | -123.3948 | -123.4085
398.6562 | 123.381 | -61.0611 | 62.2055 | 0.48909 | -0.052323 | -0.076209 | 0.11655 | -0.020191 | -0.087569 | 0.047815 | -61.2076 | 62.2009 | -61.1984 | -61.1252 | 62.0728 | 0.10986 | -0.15106 | 0.15564 | 62.0819 | -61.1893 | -0.13733 | -0.004577 | -0.14648 | -0.064087 | -0.13275 | -0.12817 | -0.1236 | -0.009156 | 60.91 | 61.2167 | 123.1338 | 123.262 | -0.14648 | 123.143 | 61.171 | -0.12817 | 123.262 | -0.14648 | 61.171 | 123.1338 | 123.143 | -123.4039 | -123.3948
399.6562 | 123.5413 | -61.0428 | 62.146 | 0.55012 | -0.046983 | -0.094367 | 0.10053 | -0.028736 | -0.093978 | 0.044611 | -61.1572 | 62.1597 | -61.1526 | -61.2762 | 61.9583 | 0.013733 | 0.045776 | 0.009155 | 62.1277 | -61.2076 | -0.10986 | 0.013733 | -0.11444 | -0.23346 | -0.18768 | -0.16479 | -0.01831 | -0.004578 | 61.0886 | 61.0519 | 123.0011 | 123.2025 | -0.11444 | 123.1705 | 61.0565 | -0.16479 | 123.2025 | -0.11444 | 61.0565 | 123.0011 | 123.1705 | -123.2986 | -123.3536
400.7031 | 123.3536 | -61.0703 | 62.1735 | 0.41279 | -0.043778 | -0.063392 | 0.11014 | -0.022327 | -0.082229 | 0.044611 | -61.2213 | 62.2421 | -61.1984 | -61.116 | 62.1094 | 0.16479 | -0.11902 | 0.13733 | 62.0911 | -61.1801 | -0.12817 | 0.068664 | -0.15106 | -0.045777 | -0.064087 | -0.10986 | -0.082398 | -0.022888 | 60.9512 | 61.2076 | 123.1796 | 123.3124 | -0.15106 | 123.1613 | 61.235 | -0.10986 | 123.3124 | -0.15106 | 61.235 | 123.1796 | 123.1613 | -123.3719 | -123.3536
401.6562 | 123.4772 | -61.0519 | 62.1552 | 0.55012 | -0.058732 | -0.099708 | 0.10053 | -0.030872 | -0.083297 | 0.047815 | -61.1938 | 62.1872 | -61.1755 | -61.1984 | 62.0361 | 0.086975 | -0.054932 | 0.07782 | 62.114 | -61.1847 | -0.1236 | 0.032044 | -0.14191 | -0.14648 | -0.11902 | -0.13275 | -0.041198 | -0.018311 | 60.997 | 61.1298 | 123.0881 | 123.2391 | -0.14191 | 123.1659 | 61.1389 | -0.13275 | 123.2391 | -0.14191 | 61.1389 | 123.0881 | 123.1659 | -123.3307 | -123.3398
402.7188 | 123.4222 | -61.084 | 62.1872 | 0.47383 | -0.049119 | -0.11146 | 0.097323 | -0.019123 | -0.070479 | 0.048883 | -61.1984 | 62.2055 | -61.203 | -61.1618 | 62.059 | 0.11444 | -0.073242 | 0.10529 | 62.1094 | -61.171 | -0.11902 | 0.01831 | -0.11444 | -0.07782 | -0.12817 | -0.086975 | -0.07782 | 0.004578 | 61.0107 | 61.1893 | 123.143 | 123.2895 | -0.11444 | 123.1934 | 61.1984 | -0.086975 | 123.2895 | -0.11444 | 61.1984 | 123.143 | 123.1934 | -123.3902 | -123.3582
403.6562 | 123.4863 | -61.0519 | 62.1414 | 0.5959 | -0.049119 | -0.083686 | 0.10266 | -0.020191 | -0.080092 | 0.036066 | -61.1938 | 62.1964 | -61.1938 | -61.2534 | 62.0178 | 0.054932 | 0 | 0.022888 | 62.114 | -61.2259 | -0.14191 | 0.054932 | -0.14191 | -0.20142 | -0.1236 | -0.17395 | -0.027465 | 0 | 61.0519 | 61.0748 | 123.0698 | 123.2483 | -0.14191 | 123.1659 | 61.1069 | -0.17395 | 123.2483 | -0.14191 | 61.1069 | 123.0698 | 123.1659 | -123.3353 | -123.3673
404.7188 | 123.4726 | -61.0199 | 62.1872 | 0.35176 | -0.068345 | -0.099708 | 0.082369 | -0.034076 | -0.10359 | 0.042474 | -61.2122 | 62.1277 | -61.1847 | -61.2991 | 61.9904 | 0.068665 | -0.009155 | 0.054932 | 62.1597 | -61.1984 | -0.16479 | -0.059509 | -0.19226 | -0.27924 | -0.19684 | -0.17853 | -0.027466 | -0.027466 | 61.0107 | 61.0748 | 123.0103 | 123.1476 | -0.19226 | 123.1796 | 61.0886 | -0.17853 | 123.1476 | -0.19226 | 61.0886 | 123.0103 | 123.1796 | -123.3719 | -123.3856
405.6562 | 123.3444 | -61.0794 | 62.1414 | 0.48909 | -0.046983 | -0.078345 | 0.1048 | -0.021259 | -0.080092 | 0.047815 | -61.2167 | 62.2238 | -61.1755 | -61.1389 | 62.0865 | 0.13733 | -0.10529 | 0.14648 | 62.0819 | -61.1893 | -0.09613 | 0.082398 | -0.13733 | -0.059509 | -0.054931 | -0.10986 | -0.059509 | -0.041199 | 60.9741 | 61.2259 | 123.1659 | 123.3032 | -0.13733 | 123.1613 | 61.2167 | -0.10986 | 123.3032 | -0.13733 | 61.2167 | 123.1659 | 123.1613 | -123.317 | -123.3307
406.6562 | 123.4131 | -61.0657 | 62.1918 | 0.47383 | -0.053391 | -0.092231 | 0.10053 | -0.021259 | -0.076888 | 0.043542 | -61.1938 | 62.2147 | -61.1893 | -61.1343 | 62.0773 | 0.13733 | -0.09613 | 0.13733 | 62.1048 | -61.203 | -0.1236 | 0.022889 | -0.12817 | -0.068664 | -0.11444 | -0.13733 | -0.086975 | -0.004578 | 60.9695 | 61.203 | 123.143 | 123.2803 | -0.12817 | 123.1705 | 61.203 | -0.13733 | 123.2803 | -0.12817 | 61.203 | 123.143 | 123.1705 | -123.381 | -123.3948
407.6562 | 123.3948 | -61.0565 | 62.2055 | 0.53486 | -0.048051 | -0.10184 | 0.1048 | -0.018055 | -0.1068 | 0.040338 | -61.2122 | 62.2238 | -61.1893 | -61.0153 | 62.1094 | 0.16937 | -0.09613 | 0.10071 | 62.114 | -61.1893 | -0.13275 | 0.018311 | -0.15564 | 0.041199 | -0.09613 | -0.13275 | -0.091552 | -0.022888 | 60.9604 | 61.1572 | 123.1659 | 123.2803 | -0.15564 | 123.1705 | 61.2259 | -0.13275 | 123.2803 | -0.15564 | 61.2259 | 123.1659 | 123.1705 | -123.3948 | -123.3948
408.6562 | 123.4131 | -61.084 | 62.1872 | 0.44331 | -0.041642 | -0.083686 | 0.11228 | -0.012714 | -0.083297 | 0.051019 | -61.1984 | 62.233 | -61.1984 | -61.1755 | 62.0499 | 0.11444 | -0.07782 | 0.11902 | 62.1094 | -61.203 | -0.11444 | 0.045776 | -0.11444 | -0.091553 | -0.13733 | -0.11902 | -0.07782 | 0 | 61.0062 | 61.203 | 123.1338 | 123.317 | -0.11444 | 123.1934 | 61.1984 | -0.11902 | 123.317 | -0.11444 | 61.1984 | 123.1338 | 123.1934 | -123.3856 | -123.3902
409.6562 | 123.4177 | -61.0657 | 62.1964 | -3.8292 | -0.054459 | -0.084754 | 0.10587 | -0.016986 | -0.079024 | 0.03927 | -61.1755 | 62.2375 | -61.1572 | -61.1618 | 62.0544 | 0.12817 | -0.082397 | 0.1236 | 62.1048 | -61.203 | -0.091553 | 0.041199 | -0.10986 | -0.09613 | -0.14191 | -0.13733 | -0.091553 | -0.01831 | 60.9833 | 61.1893 | 123.1201 | 123.3032 | -0.10986 | 123.1705 | 61.1938 | -0.13733 | 123.3032 | -0.10986 | 61.1938 | 123.1201 | 123.1705 | -123.3536 | -123.3994
410.7188 | 123.4634 | -61.0428 | 62.1735 | 0.48909 | -0.063004 | -0.096503 | 0.084505 | -0.023395 | -0.09825 | 0.037134 | -61.1481 | 62.1414 | -61.1801 | -61.3174 | 61.972 | 0.022888 | 0.018311 | 0.009155 | 62.1231 | -61.235 | -0.13733 | -0.032044 | -0.10529 | -0.27466 | -0.20142 | -0.19226 | -0.050354 | 0.032044 | 61.0611 | 61.0519 | 123.0148 | 123.1842 | -0.10529 | 123.1659 | 61.0657 | -0.19226 | 123.1842 | -0.10529 | 61.0657 | 123.0148 | 123.1659 | -123.3536 | -123.4085
411.6562 | 123.3994 | -61.0474 | 62.2147 | 0.24495 | -0.046983 | -0.078345 | 0.108 | -0.015918 | -0.080092 | 0.052087 | -61.1801 | 62.2192 | -61.1893 | -61.1572 | 62.0544 | 0.16022 | -0.091553 | 0.14191 | 62.1277 | -61.1984 | -0.14191 | 0.004577 | -0.13275 | -0.10986 | -0.16022 | -0.15106 | -0.086975 | 0.009155 | 60.9558 | 61.1893 | 123.1018 | 123.2666 | -0.13275 | 123.175 | 61.2076 | -0.15106 | 123.2666 | -0.13275 | 61.2076 | 123.1018 | 123.175 | -123.4039 | -123.4131
412.6562 | 123.3902 | -61.0565 | 62.2055 | 0.13813 | -0.053391 | -0.087958 | 0.10694 | -0.021259 | -0.074752 | 0.045679 | -61.1435 | 62.2192 | -61.1801 | -61.1618 | 62.0361 | 0.13275 | -0.07782 | 0.10986 | 62.146 | -61.1984 | -0.1236 | 0.013733 | -0.086975 | -0.10528 | -0.16937 | -0.14191 | -0.059509 | 0.036621 | 60.9787 | 61.1664 | 123.0927 | 123.2758 | -0.086975 | 123.2025 | 61.1893 | -0.14191 | 123.2758 | -0.086975 | 61.1893 | 123.0927 | 123.2025 | -123.3856 | -123.4039
413.6562 | 123.3902 | -61.0611 | 62.1964 | 0.18391 | -0.050187 | -0.10398 | 0.11228 | -0.010578 | -0.086501 | 0.045679 | -61.1801 | 62.2467 | -61.1618 | -61.1664 | 62.0728 | 0.16479 | -0.10986 | 0.14648 | 62.1094 | -61.1847 | -0.10071 | 0.050354 | -0.11902 | -0.10529 | -0.1236 | -0.1236 | -0.086975 | -0.018311 | 60.9512 | 61.2076 | 123.1338 | 123.3078 | -0.11902 | 123.1705 | 61.2259 | -0.1236 | 123.3078 | -0.11902 | 61.2259 | 123.1338 | 123.1705 | -123.3582 | -123.381
414.6562 | 123.4222 | -61.0611 | 62.1918 | 0.21443 | -0.048051 | -0.087958 | 0.10373 | -0.0063047 | -0.074752 | 0.044611 | -61.171 | 62.2375 | -61.1481 | -61.1664 | 62.0499 | 0.16479 | -0.082397 | 0.15106 | 62.1185 | -61.1893 | -0.086975 | 0.045777 | -0.10986 | -0.10529 | -0.14191 | -0.12817 | -0.073242 | -0.022888 | 60.9787 | 61.2122 | 123.111 | 123.2986 | -0.10986 | 123.1796 | 61.2259 | -0.12817 | 123.2986 | -0.10986 | 61.2259 | 123.111 | 123.1796 | -123.3398 | -123.381
415.6562 | 123.381 | -61.0611 | 62.1918 | 0.22969 | -0.032029 | -0.10612 | 0.10587 | -0.020191 | -0.080092 | 0.047815 | -61.1984 | 62.233 | -61.1755 | -61.1389 | 62.0773 | 0.16937 | -0.1236 | 0.16022 | 62.1048 | -61.1801 | -0.11444 | 0.041199 | -0.13733 | -0.07782 | -0.11444 | -0.11902 | -0.086975 | -0.022888 | 60.9375 | 61.2213 | 123.1384 | 123.2941 | -0.13733 | 123.1659 | 61.2305 | -0.11902 | 123.2941 | -0.13733 | 61.2305 | 123.1384 | 123.1659 | -123.3673 | -123.3719
416.7188 | 123.4451 | -61.0336 | 62.1964 | 0.16865 | -0.040574 | -0.094367 | 0.108 | -0.020191 | -0.079024 | 0.048883 | -61.1252 | 62.2696 | -61.1801 | -61.1938 | 62.0499 | 0.11444 | -0.059509 | 0.10986 | 62.1231 | -61.203 | -0.14648 | 0.073242 | -0.091553 | -0.16022 | -0.14648 | -0.16937 | -0.073242 | 0.054932 | 60.9741 | 61.1435 | 123.0835 | 123.3032 | -0.091553 | 123.1567 | 61.1481 | -0.16937 | 123.3032 | -0.091553 | 61.1481 | 123.0835 | 123.1567 | -123.3765 | -123.3994
417.6562 | 123.3948 | -61.0565 | 62.2147 | 0.21443 | -0.04271 | -0.090095 | 0.10694 | -0.016986 | -0.070479 | 0.058496 | -61.171 | 62.2284 | -61.1938 | -61.1755 | 62.0682 | 0.16479 | -0.086975 | 0.13733 | 62.1323 | -61.1893 | -0.13733 | 0.013733 | -0.11444 | -0.11902 | -0.14648 | -0.13275 | -0.082398 | 0.022889 | 60.9695 | 61.1938 | 123.1247 | 123.2849 | -0.11444 | 123.1888 | 61.2213 | -0.13275 | 123.2849 | -0.11444 | 61.2213 | 123.1247 | 123.1888 | -123.4085 | -123.4039
418.6719 | 123.5229 | -61.0245 | 62.1826 | 0.15339 | -0.054459 | -0.082618 | 0.082369 | -0.0095097 | -0.085433 | 0.049951 | -61.116 | 62.1414 | -61.1801 | -61.3358 | 61.9583 | 0.013733 | 0.07782 | 0.004578 | 62.1735 | -61.2213 | -0.15564 | -0.041199 | -0.091553 | -0.31128 | -0.2243 | -0.19684 | -0.009155 | 0.064087 | 61.1023 | 61.0291 | 122.9828 | 123.1659 | -0.091553 | 123.1979 | 61.0382 | -0.19684 | 123.1659 | -0.091553 | 61.0382 | 122.9828 | 123.1979 | -123.3627 | -123.4039
419.6562 | 123.4177 | -61.0474 | 62.2055 | 0.061841 | -0.036301 | -0.060187 | 0.11334 | -0.012714 | -0.079024 | 0.052087 | -61.1252 | 62.2696 | -61.171 | -61.203 | 62.0178 | 0.1236 | -0.022888 | 0.10071 | 62.1414 | -61.1984 | -0.1236 | 0.064087 | -0.07782 | -0.15564 | -0.18768 | -0.15106 | -0.064087 | 0.045776 | 61.0245 | 61.1481 | 123.0652 | 123.317 | -0.07782 | 123.1888 | 61.171 | -0.15106 | 123.317 | -0.07782 | 61.171 | 123.0652 | 123.1888 | -123.3765 | -123.4039
420.7031 | 123.4039 | -61.0565 | 62.2375 | -0.13652 | -0.067277 | -0.082618 | 0.10587 | -0.013782 | -0.080092 | 0.044611 | -61.0657 | 62.2421 | -61.1801 | -61.1618 | 62.0819 | 0.17853 | -0.07782 | 0.18768 | 62.1643 | -61.1618 | -0.1236 | 0.004577 | -0.009155 | -0.10528 | -0.15564 | -0.10528 | -0.073242 | 0.11444 | 60.9787 | 61.2442 | 123.1384 | 123.2986 | -0.009155 | 123.2208 | 61.235 | -0.10528 | 123.2986 | -0.009155 | 61.235 | 123.1384 | 123.2208 | -123.4177 | -123.3994
421.6562 | 123.3902 | -61.0611 | 62.2055 | 0.32124 | -0.041642 | -0.10078 | 0.098391 | -0.023395 | -0.082229 | 0.058496 | -61.171 | 62.2284 | -61.171 | -61.171 | 62.0361 | 0.14191 | -0.068665 | 0.13733 | 62.1368 | -61.2213 | -0.10986 | 0.022889 | -0.10986 | -0.10986 | -0.16937 | -0.16022 | -0.068664 | 0 | 60.9924 | 61.1984 | 123.0972 | 123.2895 | -0.10986 | 123.1979 | 61.203 | -0.16022 | 123.2895 | -0.10986 | 61.203 | 123.0972 | 123.1979 | -123.3765 | -123.4268
422.6562 | 123.4085 | -61.0474 | 62.178 | 0.18391 | -0.04271 | -0.089027 | 0.11334 | -0.016986 | -0.076888 | 0.047815 | -61.1435 | 62.2375 | -61.1847 | -61.171 | 62.059 | 0.14191 | -0.054932 | 0.12817 | 62.1368 | -61.2259 | -0.13733 | 0.059509 | -0.096131 | -0.1236 | -0.11902 | -0.17853 | -0.041199 | 0.041198 | 60.9924 | 61.1755 | 123.1064 | 123.2849 | -0.096131 | 123.1842 | 61.1893 | -0.17853 | 123.2849 | -0.096131 | 61.1893 | 123.1064 | 123.1842 | -123.3627 | -123.4039
423.7188 | 123.4497 | -61.0291 | 62.1826 | 0.41279 | -0.06514 | -0.13709 | 0.077029 | -0.029804 | -0.099318 | 0.042474 | -61.1481 | 62.1277 | -61.1938 | -61.3174 | 61.9766 | 0.032043 | 0.032043 | 0.027466 | 62.1735 | -61.2396 | -0.1648 | -0.054931 | -0.11902 | -0.28839 | -0.20599 | -0.21057 | -0.009155 | 0.045777 | 61.0611 | 61.0565 | 123.0057 | 123.1567 | -0.11902 | 123.2025 | 61.0611 | -0.21057 | 123.1567 | -0.11902 | 61.0611 | 123.0057 | 123.2025 | -123.3765 | -123.4222
424.6562 | 123.4314 | -61.0428 | 62.2055 | 0.19917 | -0.04271 | -0.091163 | 0.10053 | -0.016986 | -0.079024 | 0.049951 | -61.1069 | 62.2467 | -61.1343 | -61.1893 | 62.0224 | 0.12817 | -0.036621 | 0.11444 | 62.1414 | -61.2076 | -0.091552 | 0.041199 | -0.064087 | -0.14648 | -0.18311 | -0.16479 | -0.064087 | 0.027465 | 61.0062 | 61.1572 | 123.0652 | 123.2895 | -0.064087 | 123.1842 | 61.171 | -0.16479 | 123.2895 | -0.064087 | 61.171 | 123.0652 | 123.1842 | -123.3398 | -123.4131
425.6562 | 123.4177 | -61.0703 | 62.2147 | -0.13652 | -0.048051 | -0.091163 | 0.099459 | -0.019123 | -0.083297 | 0.05636 | -61.1252 | 62.2192 | -61.1664 | -61.1801 | 62.0178 | 0.12817 | -0.013733 | 0.10071 | 62.146 | -61.203 | -0.096131 | 0.004577 | -0.054932 | -0.10986 | -0.19684 | -0.13275 | -0.068665 | 0.041199 | 61.0565 | 61.171 | 123.0881 | 123.2895 | -0.054932 | 123.2162 | 61.1984 | -0.13275 | 123.2895 | -0.054932 | 61.1984 | 123.0881 | 123.2162 | -123.381 | -123.4177
426.6562 | 123.436 | -61.0565 | 62.2055 | -0.090746 | -0.050187 | -0.10291 | 0.10159 | -0.036213 | -0.088637 | 0.045679 | -61.1206 | 62.2604 | -61.1618 | -61.1893 | 62.027 | 0.14191 | -0.018311 | 0.09613 | 62.1506 | -61.1984 | -0.10528 | 0.054932 | -0.064086 | -0.13275 | -0.17853 | -0.14191 | -0.054931 | 0.041199 | 61.0382 | 61.1526 | 123.0835 | 123.317 | -0.064086 | 123.2071 | 61.1984 | -0.14191 | 123.317 | -0.064086 | 61.1984 | 123.0835 | 123.2071 | -123.3673 | -123.4039
427.7188 | 123.4406 | -61.0428 | 62.2192 | 0.00080561 | -0.052323 | -0.09864 | 0.097323 | -0.021259 | -0.086501 | 0.031793 | -61.1252 | 62.2513 | -61.1801 | -61.1893 | 62.0544 | 0.10986 | -0.091553 | 0.11444 | 62.146 | -61.2305 | -0.13733 | 0.032044 | -0.082397 | -0.14648 | -0.16479 | -0.18768 | -0.073242 | 0.054932 | 60.9512 | 61.1572 | 123.0972 | 123.2941 | -0.082397 | 123.1888 | 61.1526 | -0.18768 | 123.2941 | -0.082397 | 61.1526 | 123.0972 | 123.1888 | -123.3994 | -123.4497
428.6719 | 123.4772 | -61.0291 | 62.1552 | 0.22969 | -0.0598 | -0.12534 | 0.086642 | -0.026599 | -0.10146 | 0.041406 | -61.1847 | 62.1368 | -61.1572 | -61.2854 | 61.9812 | 0.082397 | 0.013733 | 0.054932 | 62.1643 | -61.2213 | -0.12817 | -0.01831 | -0.15564 | -0.25635 | -0.17395 | -0.19226 | 0.009156 | -0.027465 | 61.0428 | 61.084 | 123.0103 | 123.1659 | -0.15564 | 123.1934 | 61.1114 | -0.19226 | 123.1659 | -0.15564 | 61.1114 | 123.0103 | 123.1934 | -123.3124 | -123.3765
429.7031 | 123.5001 | -61.0016 | 62.1872 | -0.22808 | -0.069413 | -0.095435 | 0.079165 | -0.028736 | -0.10252 | 0.053156 | -61.1252 | 62.1231 | -61.1618 | -61.3358 | 61.9125 | 0.086975 | 0.1236 | -0.022888 | 62.2101 | -61.2167 | -0.16022 | -0.064087 | -0.1236 | -0.33417 | -0.27466 | -0.21515 | 0.022888 | 0.036621 | 61.1252 | 60.9787 | 122.9141 | 123.1247 | -0.1236 | 123.2117 | 61.0886 | -0.21515 | 123.1247 | -0.1236 | 61.0886 | 122.9141 | 123.2117 | -123.349 | -123.4039
430.6562 | 123.436 | -61.0474 | 62.2009 | -0.029711 | -0.044846 | -0.097572 | 0.10907 | -0.03194 | -0.083297 | 0.052087 | -61.1114 | 62.2238 | -61.1526 | -61.1801 | 62.0224 | 0.13733 | -0.036621 | 0.09613 | 62.1643 | -61.2122 | -0.10529 | 0.022888 | -0.064087 | -0.13275 | -0.17853 | -0.1648 | -0.036621 | 0.041199 | 61.0107 | 61.1435 | 123.0698 | 123.2712 | -0.064087 | 123.2117 | 61.1847 | -0.1648 | 123.2712 | -0.064087 | 61.1847 | 123.0698 | 123.2117 | -123.3536 | -123.4131
431.7031 | 123.4314 | -61.0474 | 62.2467 | -0.33489 | -0.064072 | -0.12 | 0.096255 | -0.01485 | -0.10466 | 0.052087 | -61.1938 | 62.1918 | -61.1801 | -60.9512 | 62.1323 | 0.16479 | -0.16022 | 0.14648 | 62.1735 | -61.1847 | -0.13275 | -0.054932 | -0.14649 | 0.09613 | -0.11444 | -0.13733 | -0.073242 | -0.013733 | 60.8871 | 61.1938 | 123.1796 | 123.2391 | -0.14649 | 123.2208 | 61.2122 | -0.13733 | 123.2391 | -0.14649 | 61.2122 | 123.1796 | 123.2208 | -123.4268 | -123.4314
432.6562 | 123.4543 | -61.0428 | 62.2147 | -0.10601 | -0.043778 | -0.10291 | 0.11228 | -0.013782 | -0.07582 | 0.043542 | -61.1298 | 62.2513 | -61.1618 | -61.1755 | 62.0132 | 0.13733 | -0.045776 | 0.086975 | 62.1872 | -61.1801 | -0.11902 | 0.036621 | -0.086975 | -0.13275 | -0.20142 | -0.13733 | -0.027466 | 0.032043 | 60.997 | 61.1298 | 123.056 | 123.2941 | -0.086975 | 123.23 | 61.1801 | -0.13733 | 123.2941 | -0.086975 | 61.1801 | 123.056 | 123.23 | -123.3765 | -123.3948
433.6719 | 123.468 | -61.0611 | 62.1872 | 0.58064 | -0.050187 | -0.092231 | 0.094119 | -0.01485 | -0.082229 | 0.03927 | -61.1847 | 62.2055 | -61.1481 | -61.1938 | 62.027 | 0.10986 | -0.036621 | 0.068665 | 62.1552 | -61.2213 | -0.086975 | 0.01831 | -0.1236 | -0.13275 | -0.16022 | -0.16022 | -0.032044 | -0.036621 | 61.0245 | 61.1298 | 123.0881 | 123.2666 | -0.1236 | 123.2162 | 61.171 | -0.16022 | 123.2666 | -0.1236 | 61.171 | 123.0881 | 123.2162 | -123.3353 | -123.4085
434.6562 | 123.468 | -61.0703 | 62.2055 | 0.031324 | -0.040574 | -0.082618 | 0.11121 | -0.0073727 | -0.07582 | 0.043542 | -61.1069 | 62.2238 | -61.1664 | -61.1847 | 62.0178 | 0.14191 | -0.036621 | 0.07782 | 62.1368 | -61.1984 | -0.096131 | 0.018311 | -0.036622 | -0.11444 | -0.18768 | -0.12817 | -0.068664 | 0.059509 | 61.0336 | 61.1481 | 123.0881 | 123.2941 | -0.036622 | 123.2071 | 61.2122 | -0.12817 | 123.2941 | -0.036622 | 61.2122 | 123.0881 | 123.2071 | -123.3719 | -123.4039
435.7031 | 123.3948 | -61.0474 | 62.233 | -0.25859 | -0.067277 | -0.085822 | 0.099459 | -0.0084417 | -0.088637 | 0.05636 | -61.1893 | 62.2055 | -61.1618 | -61.1526 | 62.0407 | 0.22888 | -0.082397 | 0.14191 | 62.1918 | -61.1755 | -0.11444 | -0.027466 | -0.14191 | -0.10529 | -0.19226 | -0.12817 | -0.041199 | -0.027466 | 60.965 | 61.1893 | 123.0881 | 123.2529 | -0.14191 | 123.2391 | 61.2762 | -0.12817 | 123.2529 | -0.14191 | 61.2762 | 123.0881 | 123.2391 | -123.3948 | -123.4085
436.6562 | 123.4268 | -61.0382 | 62.2192 | 0.12288 | -0.056596 | -0.096503 | 0.1048 | -0.012714 | -0.07582 | 0.046747 | -61.0977 | 62.2375 | -61.1435 | -61.1664 | 62.0316 | 0.19226 | -0.073242 | 0.091553 | 62.1506 | -61.2076 | -0.10529 | 0.018311 | -0.059509 | -0.12817 | -0.18768 | -0.16937 | -0.068664 | 0.045777 | 60.965 | 61.1298 | 123.0698 | 123.2758 | -0.059509 | 123.1888 | 61.2305 | -0.16937 | 123.2758 | -0.059509 | 61.2305 | 123.0698 | 123.1888 | -123.3627 | -123.4268
437.6562 | 123.3948 | -61.0428 | 62.2192 | 0.092359 | -0.04271 | -0.09864 | 0.11121 | -0.012714 | -0.079024 | 0.040338 | -61.1114 | 62.2513 | -61.1526 | -61.1938 | 62.0132 | 0.19226 | -0.068665 | 0.068665 | 62.1597 | -61.2305 | -0.10986 | 0.032044 | -0.068664 | -0.15106 | -0.20599 | -0.18768 | -0.059509 | 0.041199 | 60.9741 | 61.1115 | 123.056 | 123.2941 | -0.068664 | 123.2025 | 61.235 | -0.18768 | 123.2941 | -0.068664 | 61.235 | 123.056 | 123.2025 | -123.3719 | -123.4497
438.6562 | 123.4131 | -61.0245 | 62.2238 | 0.35176 | -0.041642 | -0.087958 | 0.108 | -0.010578 | -0.069411 | 0.042474 | -61.1252 | 62.233 | -61.1801 | -61.1755 | 62.0224 | 0.19684 | -0.09613 | 0.036621 | 62.1643 | -61.2259 | -0.15564 | 0.009155 | -0.10071 | -0.15106 | -0.20142 | -0.20142 | -0.059509 | 0.054932 | 60.9283 | 61.0611 | 123.0469 | 123.2574 | -0.10071 | 123.1888 | 61.2213 | -0.20142 | 123.2574 | -0.10071 | 61.2213 | 123.0469 | 123.1888 | -123.4039 | -123.4497
439.7188 | 123.4177 | -61.0428 | 62.2101 | 0.32124 | -0.056596 | -0.087958 | 0.11548 | -0.022327 | -0.083297 | 0.052087 | -61.0886 | 62.2421 | -61.171 | -61.1755 | 62.0361 | 0.24261 | -0.09613 | 0.022888 | 62.178 | -61.1801 | -0.12817 | 0.032043 | -0.045776 | -0.13275 | -0.17395 | -0.13733 | -0.032043 | 0.082397 | 60.9467 | 61.0657 | 123.0789 | 123.2849 | -0.045776 | 123.2208 | 61.2854 | -0.13733 | 123.2849 | -0.045776 | 61.2854 | 123.0789 | 123.2208 | -123.381 | -123.3902
440.6562 | 123.4406 | -61.0107 | 62.1918 | 0.13813 | -0.051255 | -0.079414 | 0.098391 | -0.020191 | -0.074752 | 0.046747 | -61.0977 | 62.2604 | -61.1618 | -61.1755 | 62.0178 | 0.2655 | -0.13275 | 0.013733 | 62.1735 | -61.2122 | -0.15106 | 0.068665 | -0.086975 | -0.16479 | -0.17395 | -0.20142 | -0.01831 | 0.064087 | 60.878 | 61.0245 | 123.0286 | 123.2712 | -0.086975 | 123.1842 | 61.2762 | -0.20142 | 123.2712 | -0.086975 | 61.2762 | 123.0286 | 123.1842 | -123.3536 | -123.4039
441.6562 | 123.4222 | -61.0107 | 62.2147 | 0.031324 | -0.053391 | -0.077277 | 0.098391 | -0.022327 | -0.076888 | 0.051019 | -61.1114 | 62.2375 | -61.1481 | -61.1481 | 61.9949 | 0.2655 | -0.17395 | -0.013733 | 62.1689 | -61.2122 | -0.13733 | 0.022888 | -0.10071 | -0.13733 | -0.21973 | -0.20142 | -0.045777 | 0.036621 | 60.8368 | 60.997 | 123.0057 | 123.2483 | -0.10071 | 123.1796 | 61.2762 | -0.20142 | 123.2483 | -0.10071 | 61.2762 | 123.0057 | 123.1796 | -123.3627 | -123.4268
442.7188 | 123.4634 | -61.0291 | 62.2238 | -0.029711 | -0.061936 | -0.082618 | 0.094119 | -0.011646 | -0.077956 | 0.044611 | -61.1114 | 62.265 | -61.1618 | -61.1801 | 61.9995 | 0.33875 | -0.20142 | -0.041199 | 62.1964 | -61.2122 | -0.13275 | 0.041199 | -0.082397 | -0.15106 | -0.2243 | -0.18311 | -0.027466 | 0.050354 | 60.8276 | 60.9879 | 123.0286 | 123.2941 | -0.082397 | 123.2254 | 61.3678 | -0.18311 | 123.2941 | -0.082397 | 61.3678 | 123.0286 | 123.2254 | -123.3856 | -123.436
443.6562 | 123.3994 | -61.0382 | 62.2147 | 0.16865 | -0.053391 | -0.094367 | 0.099459 | -0.024463 | -0.091842 | 0.03927 | -61.1114 | 62.2375 | -61.1526 | -61.1526 | 62.0544 | 0.37994 | -0.27466 | -0.059509 | 62.1872 | -61.1984 | -0.11444 | 0.022888 | -0.073242 | -0.11444 | -0.16022 | -0.16022 | -0.027466 | 0.041199 | 60.7635 | 60.9787 | 123.0927 | 123.2758 | -0.073242 | 123.2254 | 61.4182 | -0.16022 | 123.2758 | -0.073242 | 61.4182 | 123.0927 | 123.2254 | -123.3673 | -123.4131
444.6562 | 123.4085 | -61.0245 | 62.2284 | 0.092359 | -0.049119 | -0.092231 | 0.10373 | -0.021259 | -0.083297 | 0.052087 | -61.1069 | 62.2559 | -61.171 | -61.171 | 62.0453 | 0.41199 | -0.33417 | -0.10529 | 62.1689 | -61.203 | -0.14648 | 0.027465 | -0.082398 | -0.14648 | -0.18311 | -0.17853 | -0.05951 | 0.064086 | 60.6903 | 60.9192 | 123.0698 | 123.2803 | -0.082398 | 123.1934 | 61.4365 | -0.17853 | 123.2803 | -0.082398 | 61.4365 | 123.0698 | 123.1934 | -123.3994 | -123.4314
445.6562 | 123.4039 | -61.0336 | 62.2284 | 0.15339 | -0.052323 | -0.094367 | 0.11121 | -0.020191 | -0.061934 | 0.045679 | -61.1252 | 62.2604 | -61.1618 | -61.1435 | 62.0316 | 0.44861 | -0.37079 | -0.17395 | 62.1643 | -61.1755 | -0.12817 | 0.032043 | -0.091553 | -0.10986 | -0.19684 | -0.14191 | -0.064087 | 0.036621 | 60.6628 | 60.8597 | 123.0652 | 123.2941 | -0.091553 | 123.1979 | 61.4822 | -0.14191 | 123.2941 | -0.091553 | 61.4822 | 123.0652 | 123.1979 | -123.3902 | -123.4039
446.6562 | 123.4039 | -61.0062 | 62.2421 | -0.04497 | -0.044846 | -0.10932 | 0.094119 | -0.01485 | -0.08116 | 0.054224 | -61.0886 | 62.2833 | -61.1343 | -61.1847 | 62.0178 | 0.48065 | -0.42572 | -0.25635 | 62.1918 | -61.1984 | -0.12817 | 0.041199 | -0.082397 | -0.17853 | -0.2243 | -0.19226 | -0.050354 | 0.045776 | 60.5804 | 60.7498 | 123.024 | 123.2895 | -0.082397 | 123.1979 | 61.4868 | -0.19226 | 123.2895 | -0.082397 | 61.4868 | 123.024 | 123.1979 | -123.3765 | -123.4406
447.6562 | 123.4406 | -60.997 | 62.2513 | -0.029711 | -0.056596 | -0.091163 | 0.10159 | -0.012714 | -0.090773 | 0.057428 | -61.0794 | 62.2971 | -61.1481 | -61.1618 | 62.0087 | 0.50354 | -0.54016 | -0.32044 | 62.1918 | -61.1572 | -0.15106 | 0.045776 | -0.082398 | -0.16479 | -0.24262 | -0.16022 | -0.05951 | 0.068664 | 60.4568 | 60.6766 | 123.0057 | 123.2941 | -0.082398 | 123.1888 | 61.5005 | -0.16022 | 123.2941 | -0.082398 | 61.5005 | 123.0057 | 123.1888 | -123.3994 | -123.4085
448.6562 | 123.436 | -61.0199 | 62.2604 | 0.031324 | -0.049119 | -0.11146 | 0.10266 | -0.015918 | -0.084365 | 0.041406 | -61.0703 | 62.2879 | -61.1252 | -61.1481 | 62.0087 | 0.52185 | -0.63629 | -0.39825 | 62.2101 | -61.1572 | -0.10529 | 0.027466 | -0.050354 | -0.12817 | -0.25177 | -0.13733 | -0.050354 | 0.054932 | 60.3836 | 60.6216 | 123.0286 | 123.3078 | -0.050354 | 123.23 | 61.5417 | -0.13733 | 123.3078 | -0.050354 | 61.5417 | 123.0286 | 123.23 | -123.3856 | -123.4177
449.7031 | 123.4451 | -60.997 | 62.2742 | -0.13652 | -0.057664 | -0.084754 | 0.095187 | -0.021259 | -0.072616 | 0.051019 | -61.116 | 62.3108 | -61.1114 | -61.1252 | 62.0544 | 0.5722 | -0.80566 | -0.42114 | 62.2284 | -61.1343 | -0.11444 | 0.036621 | -0.11902 | -0.12817 | -0.21973 | -0.13733 | -0.045776 | -0.004578 | 60.1913 | 60.5759 | 123.0515 | 123.3078 | -0.11902 | 123.2254 | 61.5692 | -0.13733 | 123.3078 | -0.11902 | 61.5692 | 123.0515 | 123.2254 | -123.3856 | -123.4085
450.6562 | 123.436 | -60.9833 | 62.2742 | -1.2046 | -0.055527 | -0.080482 | 0.098391 | -0.013782 | -0.082229 | 0.037134 | -61.1114 | 62.2787 | -61.1252 | -61.1069 | 62.0316 | 0.56305 | -0.88806 | -0.54932 | 62.2513 | -61.1389 | -0.14191 | 0.004578 | -0.12817 | -0.1236 | -0.24262 | -0.15564 | -0.022888 | 0.013733 | 60.0952 | 60.434 | 123.0148 | 123.262 | -0.12817 | 123.2346 | 61.5463 | -0.15564 | 123.262 | -0.12817 | 61.5463 | 123.0148 | 123.2346 | -123.3994 | -123.4131
451.6562 | 123.4268 | -60.9512 | 62.2833 | 0.046583 | -0.055527 | -0.12214 | 0.11014 | -0.0073727 | -0.074752 | 0.043542 | -61.0611 | 62.3108 | -61.0931 | -61.1389 | 62.0407 | 0.58136 | -0.98419 | -0.62256 | 62.2467 | -61.1206 | -0.14191 | 0.027466 | -0.10986 | -0.18768 | -0.24262 | -0.16937 | -0.036621 | 0.032044 | 59.967 | 60.3287 | 122.9919 | 123.262 | -0.10986 | 123.1979 | 61.5326 | -0.16937 | 123.262 | -0.10986 | 61.5326 | 122.9919 | 123.1979 | -123.3765 | -123.4039
452.6562 | 123.436 | -60.9695 | 62.3016 | -0.029711 | -0.063004 | -0.089027 | 0.10266 | -0.013782 | -0.07582 | 0.048883 | -61.0611 | 62.3291 | -61.084 | -61.1206 | 62.0316 | 0.54474 | -1.1627 | -0.74158 | 62.2284 | -61.1114 | -0.11444 | 0.027466 | -0.091553 | -0.15106 | -0.27008 | -0.14191 | -0.073242 | 0.022888 | 59.8068 | 60.228 | 123.0011 | 123.2986 | -0.091553 | 123.1979 | 61.5143 | -0.14191 | 123.2986 | -0.091553 | 61.5143 | 123.0011 | 123.1979 | -123.3856 | -123.4131
453.6562 | 123.436 | -60.9467 | 62.3154 | -0.014452 | -0.055527 | -0.076209 | 0.099459 | -0.012714 | -0.079024 | 0.046747 | -61.0336 | 62.3245 | -61.1023 | -61.1069 | 62.0361 | 0.55847 | -1.3184 | -0.83313 | 62.2559 | -61.1298 | -0.15564 | 0.009155 | -0.086975 | -0.16022 | -0.27924 | -0.18311 | -0.05951 | 0.068665 | 59.6283 | 60.1135 | 122.9828 | 123.2712 | -0.086975 | 123.2025 | 61.5051 | -0.18311 | 123.2712 | -0.086975 | 61.5051 | 122.9828 | 123.2025 | -123.4177 | -123.4451
454.7031 | 123.5229 | -60.9009 | 62.2787 | -0.04497 | -0.06514 | -0.11252 | 0.074892 | -0.027668 | -0.10146 | 0.048883 | -61.0382 | 62.2467 | -61.0703 | -61.2488 | 61.9766 | 0.48065 | -1.4099 | -1.0071 | 62.3016 | -61.1206 | -0.16937 | -0.032044 | -0.13733 | -0.3479 | -0.30212 | -0.21973 | 0.022888 | 0.032043 | 59.491 | 59.8938 | 122.8775 | 123.1476 | -0.13733 | 123.2025 | 61.3815 | -0.21973 | 123.1476 | -0.13733 | 61.3815 | 122.8775 | 123.2025 | -123.349 | -123.3994
455.6562 | 123.4268 | -60.9329 | 62.3245 | 0.016065 | -0.052323 | -0.095435 | 0.10053 | -0.022327 | -0.072616 | 0.05636 | -61.0062 | 62.3383 | -61.0611 | -61.0794 | 62.1872 | 0.53101 | -1.6525 | -1.0117 | 62.2925 | -61.1252 | -0.12817 | 0.013733 | -0.073243 | -0.14649 | -0.13733 | -0.19226 | -0.032044 | 0.054931 | 59.2804 | 59.9213 | 123.1201 | 123.2712 | -0.073243 | 123.2254 | 61.4639 | -0.19226 | 123.2712 | -0.073243 | 61.4639 | 123.1201 | 123.2254 | -123.3856 | -123.4497
456.6562 | 123.3994 | -60.9375 | 62.3566 | 0.16865 | -0.053391 | -0.074073 | 0.10159 | -0.020191 | -0.074752 | 0.043542 | -61.0199 | 62.3657 | -61.0611 | -61.0428 | 62.0865 | 0.53558 | -1.8127 | -1.0849 | 62.2879 | -61.0794 | -0.1236 | 0.009156 | -0.082397 | -0.10529 | -0.27008 | -0.14191 | -0.068664 | 0.041199 | 59.1248 | 59.8526 | 123.024 | 123.3032 | -0.082397 | 123.2254 | 61.4731 | -0.14191 | 123.3032 | -0.082397 | 61.4731 | 123.024 | 123.2254 | -123.4177 | -123.436
457.7031 | 123.4955 | -60.878 | 62.3199 | 4.5021 | -0.056596 | -0.10825 | 0.073824 | -0.015918 | -0.096114 | 0.05636 | -60.9924 | 62.2513 | -61.0565 | -61.2167 | 61.9904 | 0.42114 | -1.8723 | -1.2955 | 62.352 | -61.0977 | -0.17853 | -0.068664 | -0.11444 | -0.33874 | -0.32959 | -0.21973 | 0.032044 | 0.064087 | 59.0057 | 59.5825 | 122.8683 | 123.1293 | -0.11444 | 123.23 | 61.2991 | -0.21973 | 123.1293 | -0.11444 | 61.2991 | 122.8683 | 123.23 | -123.3765 | -123.4177
458.6562 | 123.3673 | -60.9055 | 62.3657 | 0.29072 | -0.049119 | -0.075141 | 0.11548 | -0.022327 | -0.072616 | 0.052087 | -61.0016 | 62.4161 | -61.0245 | -61.0016 | 62.1185 | 0.53101 | -2.1881 | -1.2451 | 62.2925 | -61.0428 | -0.11902 | 0.050354 | -0.09613 | -0.09613 | -0.24719 | -0.13733 | -0.073243 | 0.022888 | 58.7173 | 59.6603 | 123.024 | 123.3215 | -0.09613 | 123.1979 | 61.4365 | -0.13733 | 123.3215 | -0.09613 | 61.4365 | 123.024 | 123.1979 | -123.3902 | -123.4085
459.7031 | 123.4543 | -60.8505 | 62.3657 | -0.30437 | -0.061936 | -0.12427 | 0.094119 | -0.023395 | -0.09291 | 0.048883 | -60.9421 | 62.2925 | -60.997 | -61.116 | 62.0316 | 0.43488 | -2.2751 | -1.4557 | 62.3703 | -61.0428 | -0.14648 | -0.073243 | -0.091553 | -0.2655 | -0.33417 | -0.19226 | 0.004577 | 0.054931 | 58.5754 | 59.3948 | 122.8821 | 123.143 | -0.091553 | 123.2208 | 61.2854 | -0.19226 | 123.143 | -0.091553 | 61.2854 | 122.8821 | 123.2208 | -123.3627 | -123.4085
460.6562 | 123.4222 | -60.8734 | 62.3795 | 0.5196 | -0.040574 | -0.090095 | 0.10907 | -0.027668 | -0.074752 | 0.045679 | -60.9604 | 62.3749 | -61.0062 | -60.9924 | 62.0865 | 0.45776 | -2.504 | -1.5518 | 62.3291 | -61.0291 | -0.13275 | -0.004578 | -0.086975 | -0.11902 | -0.29297 | -0.15564 | -0.050354 | 0.045777 | 58.3694 | 59.3216 | 122.9599 | 123.2483 | -0.086975 | 123.2025 | 61.3312 | -0.15564 | 123.2483 | -0.086975 | 61.3312 | 122.9599 | 123.2025 | -123.3856 | -123.4085
461.6562 | 123.3856 | -60.9009 | 62.3795 | 0.15339 | -0.051255 | -0.092231 | 0.11121 | -0.019123 | -0.079024 | 0.057428 | -60.9741 | 62.4207 | -61.0062 | -60.9879 | 62.114 | 0.48981 | -2.7008 | -1.6525 | 62.3245 | -61.0153 | -0.10529 | 0.041198 | -0.073242 | -0.086975 | -0.2655 | -0.11444 | -0.054932 | 0.032044 | 58.2001 | 59.2484 | 123.0148 | 123.3215 | -0.073242 | 123.2254 | 61.3907 | -0.11444 | 123.3215 | -0.073242 | 61.3907 | 123.0148 | 123.2254 | -123.3856 | -123.3948
462.7031 | 123.4085 | -60.878 | 62.4252 | -0.22808 | -0.052323 | -0.093299 | 0.10373 | -0.019123 | -0.076888 | 0.043542 | -60.9787 | 62.4298 | -61.0107 | -60.9558 | 62.1368 | 0.52643 | -2.8427 | -1.7853 | 62.3657 | -60.9695 | -0.13275 | 0.004578 | -0.10071 | -0.07782 | -0.28839 | -0.091552 | -0.059509 | 0.032043 | 58.0353 | 59.0927 | 123.0148 | 123.3078 | -0.10071 | 123.2437 | 61.4044 | -0.091552 | 123.3078 | -0.10071 | 61.4044 | 123.0148 | 123.2437 | -123.436 | -123.3948
463.6562 | 123.381 | -60.8688 | 62.4069 | 0.36702 | -0.041642 | -0.10078 | 0.10266 | -0.01485 | -0.082229 | 0.042474 | -60.9879 | 62.4435 | -60.997 | -60.9283 | 62.1643 | 0.54474 | -3.0396 | -1.886 | 62.3428 | -60.9924 | -0.12817 | 0.036621 | -0.11902 | -0.05951 | -0.24261 | -0.1236 | -0.064087 | 0.009155 | 57.8293 | 58.9828 | 123.0331 | 123.3124 | -0.11902 | 123.2117 | 61.4136 | -0.1236 | 123.3124 | -0.11902 | 61.4136 | 123.0331 | 123.2117 | -123.4039 | -123.3994
464.7188 | 123.4039 | -60.8368 | 62.4252 | 0.0771 | -0.038438 | -0.092231 | 0.10694 | -0.015918 | -0.074752 | 0.042474 | -60.9283 | 62.4435 | -60.9741 | -60.9421 | 62.1185 | 0.55389 | -3.1311 | -2.0645 | 62.3428 | -60.997 | -0.13733 | 0.01831 | -0.091553 | -0.10529 | -0.3067 | -0.16022 | -0.082398 | 0.045776 | 57.7057 | 58.7723 | 122.9553 | 123.2803 | -0.091553 | 123.1796 | 61.3907 | -0.16022 | 123.2803 | -0.091553 | 61.3907 | 122.9553 | 123.1796 | -123.3994 | -123.4222
465.6562 | 123.381 | -60.8643 | 62.4344 | 0.27546 | -0.048051 | -0.090095 | 0.095187 | -0.01485 | -0.088637 | 0.044611 | -60.9558 | 62.471 | -60.9467 | -60.9146 | 62.1872 | 0.62256 | -3.2867 | -2.1149 | 62.3566 | -60.9741 | -0.082397 | 0.036621 | -0.091553 | -0.050354 | -0.24719 | -0.10986 | -0.07782 | -0.009156 | 57.5775 | 58.7494 | 123.0515 | 123.3353 | -0.091553 | 123.2208 | 61.4868 | -0.10986 | 123.3353 | -0.091553 | 61.4868 | 123.0515 | 123.2208 | -123.381 | -123.4085
466.6562 | 123.4177 | -60.7956 | 62.4527 | 0.12288 | -0.045914 | -0.091163 | 0.10266 | -0.0041687 | -0.082229 | 0.048883 | -60.8734 | 62.4847 | -60.9375 | -60.9558 | 62.1277 | 0.61798 | -3.4103 | -2.3392 | 62.3703 | -60.9512 | -0.14191 | 0.032043 | -0.07782 | -0.16022 | -0.32501 | -0.15564 | -0.082398 | 0.064087 | 57.3853 | 58.4564 | 122.9233 | 123.2803 | -0.07782 | 123.1659 | 61.4136 | -0.15564 | 123.2803 | -0.07782 | 61.4136 | 122.9233 | 123.1659 | -123.3902 | -123.4039
467.6562 | 123.4039 | -60.8093 | 62.4298 | -0.24333 | -0.052323 | -0.080482 | 0.10159 | -0.012714 | -0.072616 | 0.045679 | -60.8734 | 62.4893 | -60.9146 | -60.965 | 62.114 | 0.70038 | -3.6346 | -2.5909 | 62.3795 | -60.965 | -0.10529 | 0.059509 | -0.064087 | -0.15564 | -0.31586 | -0.15564 | -0.050354 | 0.041199 | 57.1747 | 58.2184 | 122.9233 | 123.2986 | -0.064087 | 123.1888 | 61.5097 | -0.15564 | 123.2986 | -0.064087 | 61.5097 | 122.9233 | 123.1888 | -123.3444 | -123.3948
468.6562 | 123.4268 | -60.8185 | 62.4802 | 0.30598 | -0.0598 | -0.096503 | 0.1048 | -0.023395 | -0.087569 | 0.047815 | -60.878 | 62.5214 | -60.9375 | -60.9283 | 62.1643 | 0.79193 | -3.8315 | -2.6779 | 62.3932 | -60.9604 | -0.11902 | 0.041198 | -0.05951 | -0.10986 | -0.31586 | -0.14191 | -0.086976 | 0.059509 | 56.987 | 58.1406 | 122.9828 | 123.3398 | -0.05951 | 123.2117 | 61.6104 | -0.14191 | 123.3398 | -0.05951 | 61.6104 | 122.9828 | 123.2117 | -123.4177 | -123.4406
469.7188 | 123.436 | -60.7773 | 62.4619 | 0.031324 | -0.054459 | -0.080482 | 0.11228 | -0.010578 | -0.087569 | 0.049951 | -60.8505 | 62.5122 | -60.9238 | -60.9421 | 62.0728 | 0.89264 | -3.8635 | -2.8336 | 62.4298 | -60.9375 | -0.14648 | 0.050354 | -0.073242 | -0.1648 | -0.3891 | -0.16022 | -0.032043 | 0.073242 | 56.9138 | 57.9437 | 122.85 | 123.2895 | -0.073242 | 123.2071 | 61.6699 | -0.16022 | 123.2895 | -0.073242 | 61.6699 | 122.85 | 123.2071 | -123.3856 | -123.3994
470.6562 | 123.381 | -60.8093 | 62.4664 | 0.26021 | -0.045914 | -0.084754 | 0.10266 | -0.016986 | -0.074752 | 0.041406 | -60.9009 | 62.4985 | -60.9283 | -60.878 | 62.2009 | 0.98419 | -4.0833 | -2.9022 | 62.4069 | -60.9421 | -0.11902 | 0.032043 | -0.091553 | -0.068665 | -0.2655 | -0.13275 | -0.05951 | 0.027466 | 56.7261 | 57.9071 | 123.0103 | 123.3078 | -0.091553 | 123.2162 | 61.7935 | -0.13275 | 123.3078 | -0.091553 | 61.7935 | 123.0103 | 123.2162 | -123.3948 | -123.4085
471.7031 | 123.3948 | -60.7681 | 62.5168 | 0.13813 | -0.053391 | -0.10825 | 0.10587 | -0.016986 | -0.097182 | 0.047815 | -60.91 | 62.5031 | -60.91 | -60.91 | 62.1918 | 1.1444 | -4.1336 | -2.9709 | 62.4573 | -60.91 | -0.14191 | -0.013733 | -0.14191 | -0.14191 | -0.32501 | -0.14191 | -0.05951 | 0 | 56.6345 | 57.7972 | 122.9599 | 123.2712 | -0.14191 | 123.2254 | 61.9125 | -0.14191 | 123.2712 | -0.14191 | 61.9125 | 122.9599 | 123.2254 | -123.4268 | -123.4268
472.6562 | 123.3948 | -60.7544 | 62.5076 | 0.26021 | -0.050187 | -0.073005 | 0.108 | -0.019123 | -0.066207 | 0.054224 | -60.8643 | 62.5122 | -60.8871 | -60.878 | 62.2009 | 1.2039 | -4.1885 | -3.0762 | 62.4435 | -60.9329 | -0.13275 | 0.004578 | -0.10986 | -0.1236 | -0.3067 | -0.17853 | -0.064087 | 0.022888 | 56.5659 | 57.6782 | 122.9553 | 123.2666 | -0.10986 | 123.1979 | 61.9583 | -0.17853 | 123.2666 | -0.10986 | 61.9583 | 122.9553 | 123.1979 | -123.3948 | -123.4406
473.6562 | 123.4451 | -60.7544 | 62.5168 | 0.12288 | -0.045914 | -0.092231 | 0.10907 | -0.019123 | -0.089705 | 0.03927 | -60.8963 | 62.5442 | -60.8688 | -60.9146 | 62.1323 | 1.2543 | -4.2068 | -3.154 | 62.4893 | -60.9146 | -0.11444 | 0.027465 | -0.14191 | -0.16022 | -0.38452 | -0.16022 | -0.027466 | -0.027466 | 56.5475 | 57.6004 | 122.8867 | 123.2986 | -0.14191 | 123.2437 | 62.0087 | -0.16022 | 123.2986 | -0.14191 | 62.0087 | 122.8867 | 123.2437 | -123.3856 | -123.4314
474.6562 | 123.4222 | -60.7681 | 62.4939 | 0.00080561 | -0.04271 | -0.084754 | 0.1048 | -0.0052367 | -0.074752 | 0.062769 | -60.8047 | 62.5214 | -60.8734 | -60.9146 | 62.1094 | 1.3824 | -4.2252 | -3.241 | 62.439 | -60.9146 | -0.10529 | 0.027466 | -0.036622 | -0.14648 | -0.38452 | -0.14648 | -0.054931 | 0.068664 | 56.543 | 57.5272 | 122.8775 | 123.2895 | -0.036622 | 123.2071 | 62.1506 | -0.14648 | 123.2895 | -0.036622 | 62.1506 | 122.8775 | 123.2071 | -123.3673 | -123.4085
475.6562 | 123.3948 | -60.7361 | 62.5168 | 0.046583 | -0.057664 | -0.12641 | 0.11334 | -0.012714 | -0.085433 | 0.048883 | -60.8322 | 62.5259 | -60.8917 | -60.8597 | 62.1643 | 1.6113 | -4.2389 | -3.154 | 62.4893 | -60.9238 | -0.15564 | 0.009155 | -0.09613 | -0.1236 | -0.35248 | -0.18768 | -0.027466 | 0.05951 | 56.4972 | 57.5821 | 122.9004 | 123.262 | -0.09613 | 123.2254 | 62.3474 | -0.18768 | 123.262 | -0.09613 | 62.3474 | 122.9004 | 123.2254 | -123.4085 | -123.4406
476.7188 | 123.4406 | -60.7315 | 62.5259 | -0.060229 | -0.049119 | -0.08689 | 0.11228 | -0.016986 | -0.085433 | 0.041406 | -60.8002 | 62.5626 | -60.8688 | -60.8734 | 62.1368 | 1.8036 | -4.1794 | -3.0945 | 62.4893 | -60.9375 | -0.13733 | 0.036621 | -0.068665 | -0.14191 | -0.3891 | -0.20599 | -0.036621 | 0.068664 | 56.5521 | 57.637 | 122.8683 | 123.2941 | -0.068665 | 123.2208 | 62.5351 | -0.20599 | 123.2941 | -0.068665 | 62.5351 | 122.8683 | 123.2208 | -123.3948 | -123.4634
477.6562 | 123.3856 | -60.7544 | 62.5351 | 0.24495 | -0.064072 | -0.075141 | 0.10053 | -0.015918 | -0.073684 | 0.048883 | -60.8414 | 62.5534 | -60.8734 | -60.8505 | 62.1918 | 2.0233 | -4.216 | -3.0258 | 62.471 | -60.8871 | -0.11902 | 0.018311 | -0.086975 | -0.09613 | -0.34332 | -0.13275 | -0.064087 | 0.032043 | 56.5384 | 57.7286 | 122.9462 | 123.3078 | -0.086975 | 123.2254 | 62.7777 | -0.13275 | 123.3078 | -0.086975 | 62.7777 | 122.9462 | 123.2254 | -123.4085 | -123.4222
478.6562 | 123.3994 | -60.7544 | 62.4939 | 0.19917 | -0.04271 | -0.077277 | 0.10907 | -0.013782 | -0.071547 | 0.042474 | -60.8414 | 62.5717 | -60.8688 | -60.8643 | 62.178 | 2.1698 | -4.184 | -2.9892 | 62.439 | -60.91 | -0.11444 | 0.07782 | -0.086975 | -0.10986 | -0.31586 | -0.15564 | -0.054931 | 0.027465 | 56.5704 | 57.7652 | 122.9324 | 123.3261 | -0.086975 | 123.1934 | 62.9242 | -0.15564 | 123.3261 | -0.086975 | 62.9242 | 122.9324 | 123.1934 | -123.3627 | -123.4039
479.7031 | 123.4039 | -60.7315 | 62.5076 | -0.27385 | -0.061936 | -0.12107 | 0.089846 | -0.011646 | -0.09825 | 0.0617 | -60.8597 | 62.4939 | -60.8871 | -60.91 | 62.1643 | 2.417 | -4.1428 | -2.9343 | 62.5122 | -60.8688 | -0.15564 | -0.013733 | -0.12817 | -0.17853 | -0.34332 | -0.13733 | 0.004578 | 0.027466 | 56.5887 | 57.7972 | 122.8958 | 123.2254 | -0.12817 | 123.2437 | 63.1485 | -0.13733 | 123.2254 | -0.12817 | 63.1485 | 122.8958 | 123.2437 | -123.3948 | -123.3765
480.6562 | 123.4543 | -60.7132 | 62.5168 | 0.13813 | -0.058732 | -0.09864 | 0.11868 | -0.027668 | -0.085433 | 0.045679 | -60.8047 | 62.5534 | -60.8917 | -60.8826 | 62.1185 | 2.5864 | -4.0833 | -2.8839 | 62.4893 | -60.9192 | -0.17853 | 0.036621 | -0.091553 | -0.16937 | -0.39825 | -0.20599 | -0.027466 | 0.086975 | 56.6299 | 57.8293 | 122.8317 | 123.2666 | -0.091553 | 123.2025 | 63.2996 | -0.20599 | 123.2666 | -0.091553 | 63.2996 | 122.8317 | 123.2025 | -123.4085 | -123.436
481.7188 | 123.5229 | -60.7132 | 62.4664 | 0.5196 | -0.054459 | -0.083686 | 0.090914 | -0.016986 | -0.088637 | 0.048883 | -60.8047 | 62.4573 | -60.8643 | -61.0199 | 62.0224 | 2.7054 | -3.923 | -2.916 | 62.4802 | -60.9467 | -0.15106 | -0.009156 | -0.091553 | -0.3067 | -0.44403 | -0.23346 | 0.013733 | 0.059509 | 56.7902 | 57.7972 | 122.7356 | 123.1705 | -0.091553 | 123.1934 | 63.4186 | -0.23346 | 123.1705 | -0.091553 | 63.4186 | 122.7356 | 123.1934 | -123.3307 | -123.4131
482.6562 | 123.3765 | -60.7361 | 62.5442 | 0.16865 | -0.051255 | -0.065528 | 0.11334 | -0.022327 | -0.076888 | 0.045679 | -60.8002 | 62.5854 | -60.8368 | -60.8414 | 62.1597 | 2.7374 | -4.3625 | -2.9068 | 62.4664 | -60.8917 | -0.10071 | 0.041199 | -0.064087 | -0.10529 | -0.38452 | -0.15564 | -0.077819 | 0.036621 | 56.3736 | 57.8293 | 122.8958 | 123.3215 | -0.064087 | 123.2025 | 63.4735 | -0.15564 | 123.3215 | -0.064087 | 63.4735 | 122.8958 | 123.2025 | -123.381 | -123.436
483.6562 | 123.3765 | -60.7269 | 62.5442 | 0.41279 | -0.056596 | -0.085822 | 0.10694 | -0.024463 | -0.083297 | 0.045679 | -60.8505 | 62.5717 | -60.8643 | -60.8139 | 62.1826 | 2.9205 | -4.4769 | -2.8656 | 62.4802 | -60.8871 | -0.13733 | 0.027466 | -0.1236 | -0.086975 | -0.36163 | -0.16022 | -0.064086 | 0.013733 | 56.25 | 57.8613 | 122.9095 | 123.2986 | -0.1236 | 123.2071 | 63.6475 | -0.16022 | 123.2986 | -0.1236 | 63.6475 | 122.9095 | 123.2071 | -123.4085 | -123.4314
484.6562 | 123.349 | -60.7178 | 62.5397 | 0.24495 | -0.051255 | -0.097572 | 0.10694 | -0.024463 | -0.070479 | 0.059564 | -60.8231 | 62.5992 | -60.8688 | -60.8047 | 62.1964 | 3.035 | -4.5181 | -2.9984 | 62.4802 | -60.8734 | -0.15106 | 0.059509 | -0.10529 | -0.086976 | -0.34332 | -0.15564 | -0.059509 | 0.045776 | 56.1996 | 57.7194 | 122.9141 | 123.317 | -0.10529 | 123.1979 | 63.7527 | -0.15564 | 123.317 | -0.10529 | 63.7527 | 122.9141 | 123.1979 | -123.4085 | -123.4131
485.7188 | 123.4222 | -60.7224 | 62.5397 | 0.00080561 | -0.050187 | -0.091163 | 0.108 | -0.012714 | -0.07582 | 0.041406 | -60.7681 | 62.6129 | -60.8459 | -60.8551 | 62.1323 | 3.0487 | -4.4815 | -3.1311 | 62.5031 | -60.8871 | -0.1236 | 0.073242 | -0.045776 | -0.13275 | -0.40741 | -0.16479 | -0.036621 | 0.07782 | 56.2408 | 57.5912 | 122.8546 | 123.3353 | -0.045776 | 123.2254 | 63.7711 | -0.16479 | 123.3353 | -0.045776 | 63.7711 | 122.8546 | 123.2254 | -123.3856 | -123.4268
486.6562 | 123.3902 | -60.7269 | 62.5534 | 0.29072 | -0.045914 | -0.093299 | 0.108 | -0.011646 | -0.077956 | 0.05636 | -60.8185 | 62.5763 | -60.8688 | -60.8231 | 62.1597 | 3.2089 | -4.5776 | -3.1174 | 62.4939 | -60.8871 | -0.14191 | 0.022888 | -0.091552 | -0.09613 | -0.39368 | -0.16022 | -0.05951 | 0.050354 | 56.1493 | 57.6096 | 122.8867 | 123.3032 | -0.091552 | 123.2208 | 63.9359 | -0.16022 | 123.3032 | -0.091552 | 63.9359 | 122.8867 | 123.2208 | -123.4222 | -123.4406
487.7031 | 123.5321 | -60.6995 | 62.5397 | -0.029711 | -0.067277 | -0.097572 | 0.081301 | -0.020191 | -0.099318 | 0.047815 | -60.7773 | 62.4619 | -60.8276 | -61.0107 | 62.027 | 3.2272 | -4.4403 | -3.3005 | 62.5626 | -60.8826 | -0.12817 | -0.07782 | -0.07782 | -0.31128 | -0.5127 | -0.1831 | 0.022888 | 0.050354 | 56.2592 | 57.399 | 122.7264 | 123.1613 | -0.07782 | 123.262 | 63.9267 | -0.1831 | 123.1613 | -0.07782 | 63.9267 | 122.7264 | 123.262 | -123.3673 | -123.4222
488.6562 | 123.4268 | -60.6812 | 62.5717 | 0.12288 | -0.053391 | -0.083686 | 0.095187 | -0.018055 | -0.073684 | 0.047815 | -60.7498 | 62.5992 | -60.8368 | -60.9009 | 62.1368 | 3.4195 | -4.6097 | -3.2684 | 62.5168 | -60.8871 | -0.15564 | 0.027466 | -0.068665 | -0.21973 | -0.43488 | -0.20599 | -0.054931 | 0.086975 | 56.0715 | 57.4127 | 122.818 | 123.2803 | -0.068665 | 123.1979 | 64.1006 | -0.20599 | 123.2803 | -0.068665 | 64.1006 | 122.818 | 123.1979 | -123.4085 | -123.4589
489.6562 | 123.4039 | -60.7224 | 62.5351 | 0.10762 | -0.041642 | -0.099708 | 0.11441 | -0.010578 | -0.074752 | 0.044611 | -60.7773 | 62.5763 | -60.8276 | -60.8231 | 62.1231 | 3.5019 | -4.6783 | -3.2959 | 62.4985 | -60.8551 | -0.10529 | 0.041199 | -0.054932 | -0.10071 | -0.41199 | -0.13275 | -0.036621 | 0.050354 | 56.044 | 57.4265 | 122.8455 | 123.2986 | -0.054932 | 123.2208 | 64.2242 | -0.13275 | 123.2986 | -0.054932 | 64.2242 | 122.8455 | 123.2208 | -123.3627 | -123.3902
490.6562 | 123.3994 | -60.704 | 62.558 | 0.16865 | -0.050187 | -0.10078 | 0.10694 | -0.018055 | -0.08116 | 0.054224 | -60.759 | 62.6083 | -60.8414 | -60.8459 | 62.114 | 3.5522 | -4.7699 | -3.3875 | 62.4802 | -60.8826 | -0.13733 | 0.050354 | -0.054931 | -0.14191 | -0.44403 | -0.17853 | -0.077819 | 0.082398 | 55.9341 | 57.3166 | 122.818 | 123.3124 | -0.054931 | 123.1842 | 64.2563 | -0.17853 | 123.3124 | -0.054931 | 64.2563 | 122.818 | 123.1842 | -123.3994 | -123.4406
491.7031 | 123.4543 | -60.7086 | 62.558 | -0.15178 | -0.0598 | -0.095435 | 0.097323 | -0.019123 | -0.088637 | 0.051019 | -60.7864 | 62.6175 | -60.8276 | -60.8093 | 62.1277 | 3.7079 | -4.7974 | -3.5248 | 62.5442 | -60.8459 | -0.11902 | 0.05951 | -0.07782 | -0.10071 | -0.4303 | -0.13733 | -0.013733 | 0.041199 | 55.9113 | 57.1838 | 122.8363 | 123.3261 | -0.07782 | 123.2529 | 64.4165 | -0.13733 | 123.3261 | -0.07782 | 64.4165 | 122.8363 | 123.2529 | -123.3856 | -123.4039
492.6562 | 123.468 | -60.6903 | 62.5809 | 0.031324 | -0.054459 | -0.076209 | 0.099459 | -0.021259 | -0.074752 | 0.03927 | -60.7224 | 62.5717 | -60.7956 | -60.8643 | 62.0956 | 3.8406 | -4.9255 | -4.01 | 62.5351 | -60.8414 | -0.10528 | -0.009156 | -0.032043 | -0.17395 | -0.48523 | -0.15106 | -0.045777 | 0.073242 | 55.7648 | 56.6803 | 122.7859 | 123.262 | -0.032043 | 123.2254 | 64.5309 | -0.15106 | 123.262 | -0.032043 | 64.5309 | 122.7859 | 123.2254 | -123.3765 | -123.4222
493.6562 | 123.436 | -60.704 | 62.5488 | -0.014452 | -0.043778 | -0.089027 | 0.1048 | -0.01485 | -0.067275 | 0.042474 | -60.7498 | 62.6038 | -60.8414 | -60.8688 | 62.027 | 4.2801 | -4.8523 | -3.9276 | 62.5168 | -60.8688 | -0.13733 | 0.054932 | -0.045776 | -0.16479 | -0.52185 | -0.16479 | -0.032043 | 0.091553 | 55.8517 | 56.7764 | 122.731 | 123.3078 | -0.045776 | 123.2208 | 64.9841 | -0.16479 | 123.3078 | -0.045776 | 64.9841 | 122.731 | 123.2208 | -123.3902 | -123.4177
494.6562 | 123.4131 | -60.7086 | 62.5946 | -0.16704 | -0.052323 | -0.10505 | 0.088778 | -0.021259 | -0.083297 | 0.060632 | -60.7819 | 62.6038 | -60.8185 | -60.8368 | 62.0544 | 4.4174 | -4.9164 | -3.9459 | 62.5214 | -60.8505 | -0.10986 | 0.009156 | -0.073242 | -0.12817 | -0.54016 | -0.14191 | -0.073242 | 0.036621 | 55.7922 | 56.7627 | 122.7631 | 123.3124 | -0.073242 | 123.23 | 65.126 | -0.14191 | 123.3124 | -0.073242 | 65.126 | 122.7631 | 123.23 | -123.4131 | -123.4451
495.7188 | 123.4268 | -60.6995 | 62.5809 | -0.12126 | -0.049119 | -0.096503 | 0.096255 | -0.018055 | -0.080092 | 0.047815 | -60.7544 | 62.5992 | -60.8459 | -60.8368 | 62.0087 | 4.4632 | -4.9438 | -4.0878 | 62.5305 | -60.8963 | -0.14648 | 0.01831 | -0.054932 | -0.13733 | -0.5722 | -0.19684 | -0.050354 | 0.091552 | 55.7556 | 56.6116 | 122.7081 | 123.2986 | -0.054932 | 123.23 | 65.1627 | -0.19684 | 123.2986 | -0.054932 | 65.1627 | 122.7081 | 123.23 | -123.4268 | -123.4772
496.6562 | 123.4314 | -60.7269 | 62.5671 | -0.090746 | -0.051255 | -0.093299 | 0.10053 | -0.0041687 | -0.080092 | 0.046747 | -60.7819 | 62.5946 | -60.8414 | -60.8643 | 62.0224 | 4.5136 | -4.9942 | -4.1428 | 62.5168 | -60.8643 | -0.11444 | 0.027465 | -0.054931 | -0.13733 | -0.54474 | -0.13733 | -0.050354 | 0.05951 | 55.7327 | 56.5842 | 122.7493 | 123.3215 | -0.054931 | 123.2437 | 65.2405 | -0.13733 | 123.3215 | -0.054931 | 65.2405 | 122.7493 | 123.2437 | -123.4085 | -123.4314
497.6562 | 123.4177 | -60.7086 | 62.5488 | 0.092359 | -0.049119 | -0.10825 | 0.10053 | -0.013782 | -0.07582 | 0.047815 | -60.7544 | 62.6038 | -60.8368 | -60.8597 | 61.9949 | 4.5822 | -5.0858 | -4.2892 | 62.5168 | -60.8505 | -0.12817 | 0.054932 | -0.045777 | -0.15106 | -0.55389 | -0.14191 | -0.032043 | 0.082397 | 55.6229 | 56.4194 | 122.7036 | 123.3124 | -0.045777 | 123.2254 | 65.2908 | -0.14191 | 123.3124 | -0.045777 | 65.2908 | 122.7036 | 123.2254 | -123.3856 | -123.3994
498.6562 | 123.4268 | -60.6812 | 62.558 | -0.12126 | -0.055527 | -0.10505 | 0.1048 | -0.015918 | -0.087569 | 0.038202 | -60.7407 | 62.6083 | -60.8597 | -60.8551 | 61.9629 | 4.6509 | -5.1636 | -4.3762 | 62.5305 | -60.8597 | -0.17853 | 0.050354 | -0.05951 | -0.17395 | -0.59509 | -0.17853 | -0.027465 | 0.11902 | 55.5176 | 56.3049 | 122.644 | 123.2895 | -0.05951 | 123.2117 | 65.332 | -0.17853 | 123.2895 | -0.05951 | 65.332 | 122.644 | 123.2117 | -123.4177 | -123.4177
499.6562 | 123.4268 | -60.6903 | 62.5717 | -0.21282 | -0.048051 | -0.097572 | 0.097323 | -0.0073727 | -0.088637 | 0.060632 | -60.7452 | 62.6038 | -60.8414 | -60.8322 | 61.972 | 4.7104 | -5.2322 | -4.454 | 62.5351 | -60.8459 | -0.15106 | 0.032044 | -0.054931 | -0.14191 | -0.59967 | -0.15564 | -0.036621 | 0.096131 | 55.4581 | 56.2363 | 122.6624 | 123.2941 | -0.054931 | 123.2254 | 65.4007 | -0.15564 | 123.2941 | -0.054931 | 65.4007 | 122.6624 | 123.2254 | -123.4131 | -123.4177
500.6562 | 123.4268 | -60.6903 | 62.5671 | -0.13652 | -0.056596 | -0.09864 | 0.094119 | -0.013782 | -0.077956 | 0.049951 | -60.7361 | 62.6083 | -60.8368 | -60.8276 | 61.94 | 4.7653 | -5.3604 | -4.6234 | 62.5351 | -60.8459 | -0.14648 | 0.041198 | -0.045776 | -0.13733 | -0.62714 | -0.15564 | -0.032044 | 0.10071 | 55.3299 | 56.0669 | 122.6303 | 123.2986 | -0.045776 | 123.2254 | 65.4556 | -0.15564 | 123.2986 | -0.045776 | 65.4556 | 122.6303 | 123.2254 | -123.4039 | -123.4131
501.6562 | 123.3948 | -60.7132 | 62.5809 | -0.27385 | -0.051255 | -0.095435 | 0.11441 | -0.016986 | -0.08116 | 0.043542 | -60.7773 | 62.6358 | -60.8231 | -60.8093 | 61.9629 | 4.8614 | -5.5801 | -4.747 | 62.5259 | -60.8322 | -0.10986 | 0.054931 | -0.064087 | -0.09613 | -0.61798 | -0.11902 | -0.054932 | 0.045776 | 55.1331 | 55.9662 | 122.6761 | 123.349 | -0.064087 | 123.2391 | 65.5746 | -0.11902 | 123.349 | -0.064087 | 65.5746 | 122.6761 | 123.2391 | -123.4039 | -123.4131
502.7031 | 123.5138 | -60.6125 | 62.5717 | 0.031324 | -0.074754 | -0.10825 | 0.064211 | -0.026599 | -0.10252 | 0.048883 | -60.7224 | 62.5031 | -60.8093 | -61.0062 | 61.8439 | 4.7287 | -5.4703 | -5.0491 | 62.5809 | -60.8551 | -0.19684 | -0.068664 | -0.10986 | -0.39368 | -0.72784 | -0.24262 | 0.009156 | 0.086975 | 55.1422 | 55.5634 | 122.4564 | 123.1155 | -0.10986 | 123.1934 | 65.3412 | -0.24262 | 123.1155 | -0.10986 | 65.3412 | 122.4564 | 123.1934 | -123.381 | -123.4268
503.6562 | 123.3902 | -60.6308 | 62.6404 | -0.13652 | -0.067277 | -0.10291 | 0.11014 | -0.03194 | -0.087569 | 0.053156 | -60.7407 | 62.6358 | -60.7956 | -60.7544 | 61.9675 | 4.953 | -6.2714 | -5.1636 | 62.5717 | -60.8002 | -0.16479 | -0.004578 | -0.10986 | -0.1236 | -0.67291 | -0.16937 | -0.068665 | 0.054931 | 54.3594 | 55.4672 | 122.5983 | 123.2666 | -0.10986 | 123.2025 | 65.5838 | -0.16937 | 123.2666 | -0.10986 | 65.5838 | 122.5983 | 123.2025 | -123.436 | -123.4406
504.6562 | 123.4131 | -60.6308 | 62.6221 | -0.16704 | -0.057664 | -0.089027 | 0.11441 | -0.020191 | -0.072616 | 0.041406 | -60.6995 | 62.6541 | -60.7498 | -60.7681 | 61.9217 | 4.8889 | -6.4911 | -5.4016 | 62.59 | -60.8139 | -0.11902 | 0.032044 | -0.068665 | -0.13733 | -0.70038 | -0.18311 | -0.032043 | 0.050354 | 54.1397 | 55.2292 | 122.5525 | 123.2849 | -0.068665 | 123.2208 | 65.5197 | -0.18311 | 123.2849 | -0.068665 | 65.5197 | 122.5525 | 123.2208 | -123.3719 | -123.436
505.7188 | 123.3902 | -60.6628 | 62.645 | -0.24333 | -0.051255 | -0.10505 | 0.10053 | -0.018055 | -0.085433 | 0.046747 | -60.7224 | 62.6633 | -60.7956 | -60.8139 | 62.0499 | 5.1086 | -6.7154 | -5.6717 | 62.5992 | -60.7819 | -0.13275 | 0.018311 | -0.059509 | -0.15106 | -0.59509 | -0.11902 | -0.045776 | 0.073242 | 53.9474 | 54.9911 | 122.7127 | 123.3261 | -0.059509 | 123.262 | 65.7715 | -0.11902 | 123.3261 | -0.059509 | 65.7715 | 122.7127 | 123.262 | -123.4406 | -123.4268
506.6562 | 123.3994 | -60.5896 | 62.677 | -0.014452 | -0.054459 | -0.09864 | 0.10694 | -0.018055 | -0.083297 | 0.051019 | -60.6583 | 62.6907 | -60.7544 | -60.7132 | 61.94 | 4.921 | -7.0312 | -5.8456 | 62.5992 | -60.7452 | -0.1648 | 0.013733 | -0.068664 | -0.1236 | -0.737 | -0.15564 | -0.07782 | 0.096131 | 53.5583 | 54.744 | 122.5296 | 123.2803 | -0.068664 | 123.1888 | 65.5106 | -0.15564 | 123.2803 | -0.068664 | 65.5106 | 122.5296 | 123.1888 | -123.4314 | -123.4222
507.7031 | 123.5321 | -60.5576 | 62.645 | -0.12126 | -0.072617 | -0.090095 | 0.088778 | -0.015918 | -0.10359 | 0.0082954 | -60.5942 | 62.5809 | -60.704 | -60.9238 | 61.9858 | 4.9484 | -7.2739 | -6.3858 | 62.6495 | -60.7681 | -0.14648 | -0.064086 | -0.036621 | -0.36621 | -0.65918 | -0.21057 | 0.004578 | 0.10986 | 53.2837 | 54.1718 | 122.5433 | 123.1384 | -0.036621 | 123.2071 | 65.506 | -0.21057 | 123.1384 | -0.036621 | 65.506 | 122.5433 | 123.2071 | -123.349 | -123.4131
508.6562 | 123.3902 | -60.5667 | 62.7136 | -0.22808 | -0.060868 | -0.089027 | 0.096255 | -0.016986 | -0.093978 | 0.042474 | -60.6033 | 62.6907 | -60.6812 | -60.7224 | 61.8988 | 4.8706 | -7.663 | -6.4499 | 62.6404 | -60.7407 | -0.11444 | -0.022888 | -0.036622 | -0.15564 | -0.81482 | -0.17395 | -0.073242 | 0.077819 | 52.9037 | 54.1168 | 122.4655 | 123.2574 | -0.036622 | 123.2071 | 65.4373 | -0.17395 | 123.2574 | -0.036622 | 65.4373 | 122.4655 | 123.2071 | -123.3948 | -123.4543
509.6719 | 123.5321 | -60.5255 | 62.6999 | 0.016065 | -0.072617 | -0.12321 | 0.077029 | -0.034076 | -0.10359 | 0.053156 | -60.5576 | 62.6083 | -60.6903 | -60.8459 | 61.7706 | 4.6371 | -7.8644 | -6.8573 | 62.7182 | -60.759 | -0.1648 | -0.091553 | -0.032043 | -0.32043 | -0.92926 | -0.23346 | 0.018311 | 0.13275 | 52.6611 | 53.6682 | 122.2961 | 123.1338 | -0.032043 | 123.2437 | 65.1627 | -0.23346 | 123.1338 | -0.032043 | 65.1627 | 122.2961 | 123.2437 | -123.3902 | -123.4589
510.7188 | 123.3902 | -60.5392 | 62.7502 | -2.5779 | -0.061936 | -0.10078 | 0.1048 | -0.026599 | -0.087569 | 0.032861 | -60.6308 | 62.7686 | -60.6583 | -60.6262 | 61.9034 | 4.7287 | -8.3725 | -7.0267 | 62.7045 | -60.672 | -0.11902 | 0.018311 | -0.091552 | -0.086975 | -0.84686 | -0.13275 | -0.045776 | 0.027466 | 52.1667 | 53.5126 | 122.4426 | 123.3078 | -0.091552 | 123.2437 | 65.2679 | -0.13275 | 123.3078 | -0.091552 | 65.2679 | 122.4426 | 123.2437 | -123.4085 | -123.4222
511.6562 | 123.4039 | -60.5392 | 62.764 | -0.33489 | -0.049119 | -0.10932 | 0.11548 | -0.033008 | -0.10146 | 0.036066 | -60.6079 | 62.7548 | -60.6445 | -60.6079 | 62.114 | 4.6829 | -8.7936 | -7.4524 | 62.6724 | -60.6766 | -0.10529 | -0.009155 | -0.068664 | -0.068664 | -0.65002 | -0.13733 | -0.091553 | 0.036621 | 51.7456 | 53.0869 | 122.6532 | 123.2941 | -0.068664 | 123.2117 | 65.2222 | -0.13733 | 123.2941 | -0.068664 | 65.2222 | 122.6532 | 123.2117 | -123.4085 | -123.4406
512.6562 | 123.3994 | -60.4935 | 62.7777 | -0.27385 | -0.068345 | -0.082618 | 0.098391 | -0.025531 | -0.088637 | 0.046747 | -60.5988 | 62.7777 | -60.6354 | -60.6033 | 61.8759 | 4.1977 | -9.2239 | -7.8232 | 62.7182 | -60.6491 | -0.14191 | 0 | -0.10529 | -0.10986 | -0.90179 | -0.15564 | -0.059509 | 0.036621 | 51.2695 | 52.6703 | 122.3694 | 123.2712 | -0.10529 | 123.2117 | 64.6912 | -0.15564 | 123.2712 | -0.10529 | 64.6912 | 122.3694 | 123.2117 | -123.4131 | -123.4268
513.6562 | 123.4085 | -60.4294 | 62.8326 | -0.19756 | -0.039506 | -0.10505 | 0.094119 | -0.023395 | -0.096114 | 0.051019 | -60.553 | 62.8098 | -60.6262 | -60.5896 | 61.8759 | 4.0924 | -9.5078 | -8.0612 | 62.7365 | -60.6079 | -0.19684 | -0.022889 | -0.1236 | -0.16022 | -0.95673 | -0.17853 | -0.096131 | 0.073242 | 50.9216 | 52.3682 | 122.3053 | 123.2391 | -0.1236 | 123.1659 | 64.5218 | -0.17853 | 123.2391 | -0.1236 | 64.5218 | 122.3053 | 123.1659 | -123.4589 | -123.4406
514.6719 | 123.4268 | -60.4294 | 62.8326 | 0.016065 | -0.055527 | -0.092231 | 0.11762 | -0.021259 | -0.083297 | 0.040338 | -60.4477 | 62.8555 | -60.5621 | -60.5713 | 61.8073 | 3.6942 | -9.8969 | -8.551 | 62.7594 | -60.585 | -0.13275 | 0.022888 | -0.018311 | -0.14191 | -1.0254 | -0.15564 | -0.073243 | 0.11444 | 50.5325 | 51.8784 | 122.2366 | 123.2849 | -0.018311 | 123.1888 | 64.1235 | -0.15564 | 123.2849 | -0.018311 | 64.1235 | 122.2366 | 123.1888 | -123.3948 | -123.4177
515.6562 | 123.5046 | -60.3561 | 62.8372 | 0.12288 | -0.064072 | -0.089027 | 0.082369 | -0.024463 | -0.10359 | 0.052087 | -60.379 | 62.796 | -60.5209 | -60.6628 | 61.7294 | 3.5019 | -10.2402 | -9.0225 | 62.8418 | -60.5804 | -0.16479 | -0.041198 | -0.022888 | -0.3067 | -1.1078 | -0.2243 | 0.004578 | 0.14191 | 50.116 | 51.3336 | 122.0856 | 123.1522 | -0.022888 | 123.1979 | 63.858 | -0.2243 | 123.1522 | -0.022888 | 63.858 | 122.0856 | 123.1979 | -123.3582 | -123.4177
516.6562 | 123.4772 | -60.3287 | 62.883 | 3.9681 | -0.067277 | -0.10612 | 0.094119 | -0.026599 | -0.09291 | 0.053156 | -60.3973 | 62.8143 | -60.4797 | -60.6445 | 61.7294 | 3.3508 | -10.6659 | -9.4254 | 62.883 | -60.5392 | -0.15106 | -0.068665 | -0.068665 | -0.31586 | -1.1536 | -0.21057 | 0 | 0.082397 | 49.6628 | 50.9033 | 122.0581 | 123.143 | -0.068665 | 123.2117 | 63.6795 | -0.21057 | 123.143 | -0.068665 | 63.6795 | 122.0581 | 123.2117 | -123.3627 | -123.4222
517.6562 | 123.4726 | -60.3104 | 62.9105 | -0.22808 | -0.068345 | -0.11146 | 0.09305 | -0.027668 | -0.091842 | 0.048883 | -60.3561 | 62.8738 | -60.466 | -60.5576 | 61.7294 | 3.1769 | -11.3388 | -9.9152 | 62.883 | -60.5255 | -0.15564 | -0.036621 | -0.045776 | -0.24719 | -1.181 | -0.21515 | -0.027465 | 0.10986 | 48.9716 | 50.3952 | 122.0398 | 123.1842 | -0.045776 | 123.1934 | 63.4872 | -0.21515 | 123.1842 | -0.045776 | 63.4872 | 122.0398 | 123.1934 | -123.3765 | -123.436
518.6562 | 123.3948 | -60.3012 | 62.9791 | -0.33489 | -0.06514 | -0.10718 | 0.10373 | -0.029804 | -0.091842 | 0.052087 | -60.3745 | 62.9471 | -60.4294 | -60.4385 | 61.7752 | 3.2043 | -11.8195 | -10.2127 | 62.8876 | -60.4431 | -0.12817 | -0.032043 | -0.073243 | -0.13733 | -1.2039 | -0.14191 | -0.091553 | 0.054931 | 48.4818 | 50.0885 | 122.0764 | 123.2483 | -0.073243 | 123.1888 | 63.5056 | -0.14191 | 123.2483 | -0.073243 | 63.5056 | 122.0764 | 123.1888 | -123.4085 | -123.4222
519.6719 | 123.5046 | -60.2463 | 62.9425 | 0.58064 | -0.044846 | -0.093299 | 0.10373 | -0.03194 | -0.090773 | 0.045679 | -60.2737 | 62.9013 | -60.4065 | -60.5209 | 61.6516 | 2.8702 | -12.1124 | -10.7483 | 62.9517 | -60.466 | -0.16022 | -0.041199 | -0.027466 | -0.27466 | -1.2909 | -0.21973 | 0.009155 | 0.13275 | 48.1338 | 49.498 | 121.8979 | 123.1476 | -0.027466 | 123.1979 | 63.1165 | -0.21973 | 123.1476 | -0.027466 | 63.1165 | 121.8979 | 123.1979 | -123.349 | -123.4085
520.6562 | 123.5046 | -60.1959 | 63.0066 | 0.76375 | -0.072617 | -0.11252 | 0.08771 | -0.035144 | -0.097182 | 0.049951 | -60.2325 | 62.9333 | -60.3836 | -60.4797 | 61.6562 | 2.7924 | -12.4832 | -11.0321 | 63.0249 | -60.4111 | -0.18768 | -0.073242 | -0.036621 | -0.28381 | -1.3504 | -0.21515 | 0.01831 | 0.15106 | 47.7127 | 49.1638 | 121.8521 | 123.1293 | -0.036621 | 123.2208 | 62.9883 | -0.21515 | 123.1293 | -0.036621 | 62.9883 | 121.8521 | 123.2208 | -123.3902 | -123.4177
521.6562 | 123.5046 | -60.1685 | 63.0249 | -0.65532 | -0.071549 | -0.12 | 0.086642 | -0.043689 | -0.10466 | 0.057428 | -60.3195 | 62.9791 | -60.3378 | -60.4889 | 61.615 | 2.7283 | -12.9044 | -11.4532 | 63.0386 | -60.3836 | -0.16937 | -0.045776 | -0.15106 | -0.32044 | -1.4099 | -0.21515 | 0.013733 | 0.018311 | 47.2641 | 48.7152 | 121.7834 | 123.1476 | -0.15106 | 123.2071 | 62.8967 | -0.21515 | 123.1476 | -0.15106 | 62.8967 | 121.7834 | 123.2071 | -123.3627 | -123.4085
522.6562 | 123.5367 | -60.141 | 63.0707 | -0.029711 | -0.069413 | -0.11573 | 0.089846 | -0.042621 | -0.10039 | 0.048883 | -60.1776 | 62.9837 | -60.3058 | -60.4614 | 61.5784 | 2.5085 | -13.1332 | -11.7737 | 63.0753 | -60.3424 | -0.16479 | -0.086975 | -0.036621 | -0.32044 | -1.4923 | -0.20142 | 0.004577 | 0.12817 | 47.0078 | 48.3673 | 121.7194 | 123.1247 | -0.036621 | 123.2162 | 62.6495 | -0.20142 | 123.1247 | -0.036621 | 62.6495 | 121.7194 | 123.2162 | -123.3765 | -123.4131
523.6562 | 123.5184 | -60.1227 | 63.0524 | -0.21282 | -0.058732 | -0.11146 | 0.091982 | -0.037281 | -0.10466 | 0.046747 | -60.1089 | 63.0341 | -60.2371 | -60.4202 | 61.5555 | 2.4216 | -13.3896 | -11.7645 | 63.1531 | -60.2692 | -0.11444 | -0.01831 | 0.013733 | -0.29755 | -1.4969 | -0.14648 | 0.10071 | 0.12817 | 46.7331 | 48.3582 | 121.6782 | 123.1567 | 0.013733 | 123.2758 | 62.5443 | -0.14648 | 123.1567 | 0.013733 | 62.5443 | 121.6782 | 123.2758 | -123.2895 | -123.3215
524.6719 | 123.4863 | -60.0815 | 63.1439 | 0.5959 | -0.051255 | -0.10398 | 0.11548 | -0.036213 | -0.085433 | 0.044611 | -60.1547 | 63.1348 | -60.2371 | -60.2554 | 61.6104 | 2.4948 | -13.7466 | -12.1811 | 63.0569 | -60.2966 | -0.15564 | -0.009155 | -0.073242 | -0.17395 | -1.5335 | -0.21515 | -0.086975 | 0.082398 | 46.3348 | 47.9004 | 121.6919 | 123.2162 | -0.073242 | 123.1384 | 62.5763 | -0.21515 | 123.2162 | -0.073242 | 62.5763 | 121.6919 | 123.1384 | -123.381 | -123.4406
525.6562 | 123.5229 | -60.054 | 63.1393 | -0.31963 | -0.069413 | -0.11359 | 0.094119 | -0.035144 | -0.099318 | 0.042474 | -60.0357 | 63.0661 | -60.2097 | -60.3149 | 61.5051 | 2.2751 | -14.1495 | -12.6251 | 63.1577 | -60.2371 | -0.15564 | -0.073242 | 0.01831 | -0.26093 | -1.6342 | -0.18311 | 0.018311 | 0.17395 | 45.9045 | 47.4289 | 121.5591 | 123.1201 | 0.01831 | 123.2117 | 62.3291 | -0.18311 | 123.1201 | 0.01831 | 62.3291 | 121.5591 | 123.2117 | -123.349 | -123.3765
526.6562 | 123.5001 | -60.0357 | 63.1851 | -0.28911 | -0.067277 | -0.10078 | 0.090914 | -0.035144 | -0.10466 | 0.049951 | -60.0494 | 63.1073 | -60.1639 | -60.3104 | 61.4868 | 2.211 | -14.3967 | -12.9501 | 63.1714 | -60.2005 | -0.12817 | -0.07782 | -0.013732 | -0.27466 | -1.6983 | -0.16479 | -0.013733 | 0.11444 | 45.639 | 47.0856 | 121.5225 | 123.143 | -0.013732 | 123.2071 | 62.2467 | -0.16479 | 123.143 | -0.013732 | 62.2467 | 121.5225 | 123.2071 | -123.349 | -123.3856
527.6562 | 123.4772 | -59.9579 | 63.2309 | -0.19756 | -0.061936 | -0.14243 | 0.097323 | -0.033008 | -0.09825 | 0.059564 | -59.7748 | 63.208 | -60.0632 | -60.2142 | 61.4777 | 2.179 | -14.7263 | -13.2706 | 63.2126 | -60.1639 | -0.10528 | -0.022888 | 0.18311 | -0.25635 | -1.7532 | -0.20599 | -0.018311 | 0.28839 | 45.2316 | 46.6873 | 121.4355 | 123.1659 | 0.18311 | 123.1705 | 62.1368 | -0.20599 | 123.1659 | 0.18311 | 62.1368 | 121.4355 | 123.1705 | -123.2941 | -123.3948
528.6562 | 123.5367 | -59.9396 | 63.2767 | -0.16704 | -0.068345 | -0.11466 | 0.12296 | -0.050098 | -0.10466 | 0.063837 | -59.9396 | 63.1943 | -60.0769 | -60.3241 | 61.3266 | 2.1835 | -15.0101 | -13.5544 | 63.2492 | -60.1364 | -0.13733 | -0.082397 | 0 | -0.38452 | -1.9501 | -0.19684 | -0.027465 | 0.13733 | 44.9295 | 46.3852 | 121.2662 | 123.1338 | 0 | 123.1888 | 62.1231 | -0.19684 | 123.1338 | 0 | 62.1231 | 121.2662 | 123.1888 | -123.3536 | -123.4131
529.6719 | 123.4863 | -59.9258 | 63.2721 | 0.38228 | -0.058732 | -0.099708 | 0.099459 | -0.035144 | -0.11 | 0.047815 | -59.9762 | 63.2263 | -60.0952 | -60.1776 | 61.4227 | 2.1103 | -15.4633 | -13.9114 | 63.2492 | -60.1135 | -0.16937 | -0.045777 | -0.050354 | -0.25177 | -1.8494 | -0.18768 | -0.022888 | 0.11902 | 44.4626 | 46.0144 | 121.3486 | 123.1522 | -0.050354 | 123.175 | 62.0361 | -0.18768 | 123.1522 | -0.050354 | 62.0361 | 121.3486 | 123.175 | -123.3673 | -123.3856
530.6562 | 123.6328 | -59.8434 | 63.3636 | -0.21282 | -0.066209 | -0.096503 | 0.10587 | -0.041553 | -0.10573 | 0.055292 | -59.8434 | 63.2721 | -60.022 | -60.1776 | 61.3495 | 2.1286 | -15.6052 | -14.1815 | 63.327 | -60.0952 | -0.17853 | -0.091552 | 0 | -0.33417 | -2.0142 | -0.25177 | -0.036621 | 0.17853 | 44.2383 | 45.6619 | 121.1929 | 123.1155 | 0 | 123.1705 | 61.972 | -0.25177 | 123.1155 | 0 | 61.972 | 121.1929 | 123.1705 | -123.3856 | -123.4589
531.6562 | 123.4909 | -59.8114 | 63.382 | -0.10601 | -0.058732 | -0.090095 | 0.11441 | -0.028736 | -0.10359 | 0.047815 | -59.7931 | 63.3133 | -59.9899 | -60.1227 | 61.3037 | 2.0416 | -15.889 | -14.4516 | 63.3774 | -60.0311 | -0.17853 | -0.068665 | 0.01831 | -0.31128 | -2.0782 | -0.21973 | -0.004578 | 0.19684 | 43.9224 | 45.3598 | 121.1151 | 123.1247 | 0.01831 | 123.1888 | 61.853 | -0.21973 | 123.1247 | 0.01831 | 61.853 | 121.1151 | 123.1888 | -123.3719 | -123.4131
532.6562 | 123.5001 | -59.7794 | 63.4048 | 0.56538 | -0.068345 | -0.11893 | 0.097323 | -0.037281 | -0.1068 | 0.046747 | -59.7794 | 63.327 | -59.967 | -60.0586 | 61.322 | 1.9867 | -16.1179 | -14.6301 | 63.4003 | -59.9991 | -0.18768 | -0.07782 | 0 | -0.27924 | -2.0828 | -0.21973 | -0.004577 | 0.18768 | 43.6615 | 45.1492 | 121.1014 | 123.1064 | 0 | 123.1796 | 61.7661 | -0.21973 | 123.1064 | 0 | 61.7661 | 121.1014 | 123.1796 | -123.3719 | -123.4039
533.6562 | 123.5092 | -59.7473 | 63.446 | 1.191 | -0.08223 | -0.10291 | 0.1048 | -0.035144 | -0.10252 | 0.051019 | -59.6878 | 63.382 | -59.903 | -60.0494 | 61.2259 | 1.9501 | -16.301 | -14.7995 | 63.4186 | -59.967 | -0.15564 | -0.064087 | 0.059509 | -0.30212 | -2.2202 | -0.21973 | -0.027466 | 0.21515 | 43.4464 | 44.9478 | 120.9732 | 123.1293 | 0.059509 | 123.1659 | 61.6974 | -0.21973 | 123.1293 | 0.059509 | 61.6974 | 120.9732 | 123.1659 | -123.349 | -123.4131
534.6719 | 123.4726 | -59.7061 | 63.5193 | -0.45696 | -0.061936 | -0.09864 | 0.10587 | -0.039417 | -0.10039 | 0.047815 | -59.7519 | 63.5284 | -59.8206 | -59.935 | 61.2579 | 2.0325 | -16.5115 | -14.9094 | 63.4735 | -59.8618 | -0.11444 | 0.009155 | -0.045776 | -0.22888 | -2.2614 | -0.15564 | -0.045776 | 0.068665 | 43.1946 | 44.7968 | 120.9641 | 123.2346 | -0.045776 | 123.1796 | 61.7386 | -0.15564 | 123.2346 | -0.045776 | 61.7386 | 120.9641 | 123.1796 | -123.3398 | -123.381
535.6562 | 123.5321 | -59.6649 | 63.5376 | -0.10601 | -0.075822 | -0.1168 | 0.10694 | -0.040485 | -0.10359 | 0.041406 | -59.6512 | 63.4689 | -59.8343 | -59.9487 | 61.171 | 1.9501 | -16.6489 | -15.2206 | 63.5651 | -59.8709 | -0.16937 | -0.068665 | 0.013733 | -0.28381 | -2.3666 | -0.20599 | 0.027465 | 0.18311 | 43.0161 | 44.4443 | 120.8359 | 123.1338 | 0.013733 | 123.23 | 61.615 | -0.20599 | 123.1338 | 0.013733 | 61.615 | 120.8359 | 123.23 | -123.3719 | -123.4085
536.6562 | 123.5092 | -59.6008 | 63.5925 | -0.075488 | -0.072617 | -0.10718 | 0.10587 | -0.047962 | -0.10466 | 0.053156 | -59.5871 | 63.5559 | -59.7473 | -59.8801 | 61.1618 | 1.9272 | -16.8869 | -15.4633 | 63.5742 | -59.7656 | -0.14648 | -0.036621 | 0.013733 | -0.27924 | -2.4307 | -0.16479 | -0.01831 | 0.16022 | 42.7139 | 44.1376 | 120.7626 | 123.1567 | 0.013733 | 123.175 | 61.528 | -0.16479 | 123.1567 | 0.013733 | 61.528 | 120.7626 | 123.175 | -123.3398 | -123.3582
537.6562 | 123.5413 | -59.5596 | 63.6475 | 0.031324 | -0.069413 | -0.11146 | 0.1048 | -0.040485 | -0.12495 | 0.044611 | -59.523 | 63.5605 | -59.729 | -59.8663 | 61.0703 | 1.7715 | -17.1844 | -15.8066 | 63.6108 | -59.7656 | -0.16937 | -0.086975 | 0.036621 | -0.3067 | -2.5772 | -0.20599 | -0.036621 | 0.20599 | 42.3752 | 43.7531 | 120.6299 | 123.1201 | 0.036621 | 123.1705 | 61.3312 | -0.20599 | 123.1201 | 0.036621 | 61.3312 | 120.6299 | 123.1705 | -123.3765 | -123.4131
538.6562 | 123.5275 | -59.4772 | 63.6932 | -0.10601 | -0.070481 | -0.11146 | 0.098391 | -0.045826 | -0.11 | 0.052087 | -59.4452 | 63.5971 | -59.642 | -59.8343 | 61.0336 | 1.7899 | -17.276 | -15.8936 | 63.6658 | -59.7198 | -0.16479 | -0.09613 | 0.032044 | -0.35706 | -2.6596 | -0.24262 | -0.027466 | 0.19684 | 42.2012 | 43.5837 | 120.5109 | 123.0743 | 0.032044 | 123.143 | 61.2671 | -0.24262 | 123.0743 | 0.032044 | 61.2671 | 120.5109 | 123.143 | -123.3353 | -123.4131
539.6719 | 123.5001 | -59.4955 | 63.6703 | 0.53486 | -0.06514 | -0.099708 | 0.10907 | -0.033008 | -0.099318 | 0.047815 | -59.3262 | 63.652 | -59.6741 | -59.7794 | 60.9604 | 1.6434 | -17.4683 | -16.0675 | 63.6658 | -59.6786 | -0.17853 | -0.01831 | 0.16937 | -0.28381 | -2.71 | -0.18311 | -0.004578 | 0.3479 | 42.0273 | 43.428 | 120.4559 | 123.1476 | 0.16937 | 123.1613 | 61.1389 | -0.18311 | 123.1476 | 0.16937 | 61.1389 | 120.4559 | 123.1613 | -123.3444 | -123.349
540.6562 | 123.5275 | -59.4086 | 63.7802 | -0.19756 | -0.0598 | -0.099708 | 0.10266 | -0.057575 | -0.12389 | 0.060632 | -59.3765 | 63.7253 | -59.5642 | -59.5047 | 60.8551 | 1.6525 | -17.4316 | -16.0538 | 63.7527 | -59.5963 | -0.15564 | -0.054931 | 0.032043 | -0.096131 | -2.9251 | -0.18768 | -0.027465 | 0.18768 | 41.9769 | 43.3548 | 120.2637 | 123.1338 | 0.032043 | 123.1613 | 61.0611 | -0.18768 | 123.1338 | 0.032043 | 61.0611 | 120.2637 | 123.1613 | -123.3444 | -123.3765
541.6562 | 123.6145 | -59.3628 | 63.8809 | -0.014452 | -0.070481 | -0.12427 | 0.094119 | -0.040485 | -0.10252 | 0.043542 | -59.3124 | 63.739 | -59.5367 | -59.6786 | 60.8826 | 1.7715 | -17.5507 | -16.1728 | 63.7939 | -59.5779 | -0.17395 | -0.14191 | 0.050354 | -0.31586 | -2.9984 | -0.21515 | -0.086975 | 0.2243 | 41.8121 | 43.19 | 120.2454 | 123.1018 | 0.050354 | 123.1567 | 61.1343 | -0.21515 | 123.1018 | 0.050354 | 61.1343 | 120.2454 | 123.1567 | -123.4177 | -123.4589
542.6562 | 123.5138 | -59.3491 | 63.8306 | 0.10762 | -0.056596 | -0.12961 | 0.11121 | -0.042621 | -0.11 | 0.048883 | -59.3308 | 63.7848 | -59.5184 | -59.6283 | 60.8047 | 1.8036 | -17.4225 | -16.0584 | 63.8031 | -59.5551 | -0.16937 | -0.045776 | 0.01831 | -0.27924 | -3.0258 | -0.20599 | -0.027465 | 0.18768 | 41.9266 | 43.2907 | 120.1538 | 123.1338 | 0.01831 | 123.1522 | 61.1526 | -0.20599 | 123.1338 | 0.01831 | 61.1526 | 120.1538 | 123.1522 | -123.349 | -123.3856
543.6562 | 123.5413 | -59.3124 | 63.8855 | 0.046583 | -0.069413 | -0.10612 | 0.099459 | -0.041553 | -0.10252 | 0.053156 | -59.2575 | 63.8306 | -59.4772 | -59.6466 | 60.7086 | 1.6846 | -17.45 | -16.1774 | 63.8809 | -59.5001 | -0.1648 | -0.054932 | 0.054932 | -0.33417 | -3.1769 | -0.18768 | -0.004578 | 0.21973 | 41.8625 | 43.1351 | 120.0211 | 123.143 | 0.054932 | 123.1934 | 60.997 | -0.18768 | 123.143 | 0.054932 | 60.997 | 120.0211 | 123.1934 | -123.3627 | -123.3856
544.6719 | 123.4863 | -59.317 | 63.913 | -2.8068 | -0.06514 | -0.12107 | 0.095187 | -0.047962 | -0.11107 | 0.048883 | -59.3216 | 63.858 | -59.4131 | -59.5093 | 60.6903 | 1.7532 | -17.5095 | -16.0584 | 63.8626 | -59.4818 | -0.09613 | -0.054932 | -0.004577 | -0.19226 | -3.2227 | -0.16479 | -0.050354 | 0.091553 | 41.8076 | 43.2587 | 120.0073 | 123.175 | -0.004577 | 123.1796 | 61.0703 | -0.16479 | 123.175 | -0.004577 | 61.0703 | 120.0073 | 123.1796 | -123.3261 | -123.3948
545.6719 | 123.3765 | -59.2621 | 64.0137 | -0.19756 | -0.066209 | -0.10932 | 0.11014 | -0.038349 | -0.10039 | 0.046747 | -59.2209 | 63.9679 | -59.3857 | -59.3765 | 60.7086 | 1.8448 | -17.5232 | -15.8798 | 63.913 | -59.404 | -0.1236 | -0.045776 | 0.041199 | -0.11444 | -3.3051 | -0.14191 | -0.10071 | 0.16479 | 41.7389 | 43.3823 | 119.9707 | 123.23 | 0.041199 | 123.175 | 61.1069 | -0.14191 | 123.23 | 0.041199 | 61.1069 | 119.9707 | 123.175 | -123.3994 | -123.4177
546.6719 | 123.3215 | -59.2346 | 64.0182 | -0.24333 | -0.063004 | -0.10078 | 0.11868 | -0.021259 | -0.10252 | 0.048883 | -59.2026 | 64.032 | -59.3948 | -59.3308 | 60.5988 | 1.9775 | -17.6193 | -15.8798 | 63.9496 | -59.3308 | -0.16022 | 0.013732 | 0.032043 | -0.096131 | -3.4195 | -0.096131 | -0.068665 | 0.19226 | 41.6153 | 43.3548 | 119.8334 | 123.2666 | 0.032043 | 123.1842 | 61.2122 | -0.096131 | 123.2666 | 0.032043 | 61.2122 | 119.8334 | 123.1842 | -123.4131 | -123.349
547.6719 | 123.4085 | -59.2484 | 64.0457 | -0.33489 | -0.060868 | -0.10184 | 0.11121 | -0.019123 | -0.097182 | 0.03927 | -59.1568 | 64.0503 | -59.3674 | -59.3308 | 60.4614 | 2.0508 | -17.5232 | -15.834 | 63.9221 | -59.3536 | -0.11902 | 0.004578 | 0.091553 | -0.082398 | -3.5843 | -0.10529 | -0.1236 | 0.21057 | 41.7252 | 43.4143 | 119.7098 | 123.2986 | 0.091553 | 123.1705 | 61.2991 | -0.10529 | 123.2986 | 0.091553 | 61.2991 | 119.7098 | 123.1705 | -123.4131 | -123.3994
548.6562 | 123.5321 | -59.1934 | 64.0091 | -0.16704 | -0.060868 | -0.099708 | 0.10373 | -0.026599 | -0.10786 | 0.058496 | -59.1614 | 63.9771 | -59.3399 | -59.4681 | 60.2875 | 1.9913 | -17.3126 | -15.8981 | 63.9679 | -59.3811 | -0.14648 | -0.032043 | 0.032043 | -0.27466 | -3.7216 | -0.18768 | -0.041198 | 0.17853 | 41.8808 | 43.2953 | 119.4809 | 123.1705 | 0.032043 | 123.1613 | 61.1847 | -0.18768 | 123.1705 | 0.032043 | 61.1847 | 119.4809 | 123.1613 | -123.349 | -123.3902
549.6875 | 123.4543 | -59.1797 | 64.0594 | -0.22808 | -0.068345 | -0.10825 | 0.099459 | -0.036213 | -0.10039 | 0.046747 | -59.0881 | 64.0045 | -59.3079 | -59.4131 | 60.141 | 1.9775 | -17.4133 | -15.834 | 63.9862 | -59.3445 | -0.12817 | -0.054931 | 0.091552 | -0.23346 | -3.9185 | -0.16479 | -0.073242 | 0.21973 | 41.7664 | 43.3456 | 119.3207 | 123.1842 | 0.091552 | 123.1659 | 61.1572 | -0.16479 | 123.1842 | 0.091552 | 61.1572 | 119.3207 | 123.1659 | -123.3673 | -123.4039
550.6562 | 123.5504 | -59.1476 | 64.0732 | -0.16704 | -0.069413 | -0.092231 | 0.08771 | -0.039417 | -0.10573 | 0.048883 | -59.0469 | 63.9771 | -59.3399 | -59.4589 | 59.9258 | 1.8997 | -17.244 | -15.8249 | 63.9999 | -59.3719 | -0.19226 | -0.09613 | 0.10071 | -0.31128 | -4.1473 | -0.2243 | -0.073242 | 0.29297 | 41.9037 | 43.3228 | 119.0735 | 123.1247 | 0.10071 | 123.1476 | 61.0474 | -0.2243 | 123.1247 | 0.10071 | 61.0474 | 119.0735 | 123.1476 | -123.4131 | -123.4451
551.6562 | 123.5138 | -59.1843 | 63.9862 | 0.10762 | -0.069413 | -0.10932 | 0.091982 | -0.041553 | -0.11 | 0.042474 | -59.0561 | 63.9542 | -59.3399 | -59.5139 | 59.697 | 1.9043 | -17.2119 | -15.7333 | 63.9771 | -59.3948 | -0.15564 | -0.032043 | 0.12817 | -0.32959 | -4.2892 | -0.21057 | -0.009155 | 0.28381 | 41.9724 | 43.4509 | 118.8812 | 123.1384 | 0.12817 | 123.1613 | 61.0886 | -0.21057 | 123.1384 | 0.12817 | 61.0886 | 118.8812 | 123.1613 | -123.3261 | -123.381
552.6562 | 123.5367 | -59.2072 | 63.9954 | -0.029711 | -0.06514 | -0.11146 | 0.098391 | -0.039417 | -0.11 | 0.059564 | -59.0561 | 63.9175 | -59.3536 | -59.5184 | 59.5139 | 1.8906 | -17.1661 | -15.6647 | 63.9908 | -59.3857 | -0.14648 | -0.077819 | 0.15106 | -0.31128 | -4.4815 | -0.17853 | -0.004577 | 0.29755 | 42.041 | 43.5425 | 118.721 | 123.1247 | 0.15106 | 123.1979 | 61.0977 | -0.17853 | 123.1247 | 0.15106 | 61.0977 | 118.721 | 123.1979 | -123.349 | -123.381
553.6719 | 123.4726 | -59.23 | 64.0182 | -0.25859 | -0.06514 | -0.085822 | 0.099459 | -0.034076 | -0.09825 | 0.043542 | -59.0973 | 63.9313 | -59.3903 | -59.4818 | 59.317 | 2.1652 | -17.0288 | -15.3946 | 63.9221 | -59.3948 | -0.16022 | -0.086976 | 0.13275 | -0.25177 | -4.7012 | -0.16479 | -0.096131 | 0.29297 | 42.2012 | 43.8354 | 118.5471 | 123.1613 | 0.13275 | 123.1522 | 61.3953 | -0.16479 | 123.1613 | 0.13275 | 61.3953 | 118.5471 | 123.1522 | -123.4085 | -123.4131
554.6875 | 123.4497 | -59.1843 | 64.0686 | -0.25859 | -0.072617 | -0.10825 | 0.10159 | -0.044757 | -0.090773 | 0.048883 | -59.0378 | 63.9999 | -59.3308 | -59.3857 | 59.1888 | 2.4261 | -16.8091 | -15.0421 | 64.0274 | -59.3582 | -0.14648 | -0.068665 | 0.14648 | -0.20142 | -4.8798 | -0.17395 | -0.041199 | 0.29297 | 42.3752 | 44.1422 | 118.3731 | 123.1842 | 0.14648 | 123.2117 | 61.6104 | -0.17395 | 123.1842 | 0.14648 | 61.6104 | 118.3731 | 123.2117 | -123.3994 | -123.4268
555.6719 | 123.3765 | -59.2255 | 64.0778 | -0.28911 | -0.055527 | -0.092231 | 0.1048 | -0.035144 | -0.097182 | 0.045679 | -59.0744 | 64.0823 | -59.3445 | -59.2941 | 58.9371 | 2.9526 | -16.6214 | -14.7171 | 63.9633 | -59.3079 | -0.11902 | 0.004577 | 0.15106 | -0.068664 | -5.1407 | -0.082397 | -0.11444 | 0.27008 | 42.6041 | 44.5084 | 118.1625 | 123.3078 | 0.15106 | 123.1888 | 62.178 | -0.082397 | 123.3078 | 0.15106 | 62.178 | 118.1625 | 123.1888 | -123.4222 | -123.3856
556.6562 | 123.5229 | -59.1751 | 64.0274 | 0.00080561 | -0.063004 | -0.12214 | 0.091982 | -0.043689 | -0.10146 | 0.053156 | -59.0469 | 63.9908 | -59.317 | -59.4818 | 58.6899 | 2.9984 | -16.2689 | -14.5386 | 64.0091 | -59.3582 | -0.14191 | -0.036621 | 0.12817 | -0.3067 | -5.3375 | -0.18311 | -0.018311 | 0.27008 | 42.9062 | 44.6365 | 117.865 | 123.1659 | 0.12817 | 123.1842 | 62.1735 | -0.18311 | 123.1659 | 0.12817 | 62.1735 | 117.865 | 123.1842 | -123.3444 | -123.3856
557.6562 | 123.5092 | -59.1797 | 64.0274 | -0.090746 | -0.071549 | -0.12748 | 0.098391 | -0.041553 | -0.10893 | 0.054224 | -59.024 | 63.9633 | -59.317 | -59.4772 | 58.3969 | 3.2364 | -15.7928 | -13.9389 | 64.0045 | -59.3674 | -0.13733 | -0.064087 | 0.15564 | -0.29755 | -5.6305 | -0.18768 | -0.022888 | 0.29297 | 43.3868 | 45.2408 | 117.5766 | 123.143 | 0.15564 | 123.1842 | 62.4161 | -0.18768 | 123.143 | 0.15564 | 62.4161 | 117.5766 | 123.1842 | -123.3444 | -123.3948
558.6562 | 123.5184 | -59.1476 | 64.0686 | -0.54851 | -0.06514 | -0.12641 | 0.098391 | -0.043689 | -0.10786 | 0.059564 | -59.1248 | 63.9954 | -59.3308 | -59.4543 | 58.136 | 3.392 | -15.564 | -13.6917 | 64.0045 | -59.3124 | -0.18311 | -0.073243 | 0.022888 | -0.3067 | -5.9326 | -0.16479 | -0.064087 | 0.20599 | 43.5837 | 45.4559 | 117.2836 | 123.143 | 0.022888 | 123.1522 | 62.5397 | -0.16479 | 123.143 | 0.022888 | 62.5397 | 117.2836 | 123.1522 | -123.3994 | -123.381
559.6875 | 123.5046 | -59.166 | 64.0274 | -0.13652 | -0.068345 | -0.12321 | 0.088778 | -0.037281 | -0.10359 | 0.047815 | -58.9554 | 63.9816 | -59.2941 | -59.4864 | 57.8979 | 3.3554 | -15.4816 | -13.4995 | 64.0137 | -59.3628 | -0.12817 | -0.045777 | 0.21057 | -0.32043 | -6.1295 | -0.19684 | -0.013733 | 0.33875 | 43.6844 | 45.6665 | 117.0639 | 123.1476 | 0.21057 | 123.1796 | 62.5214 | -0.19684 | 123.1476 | 0.21057 | 62.5214 | 117.0639 | 123.1796 | -123.3215 | -123.3902
560.6562 | 123.4085 | -59.0149 | 64.1647 | -0.1823 | -0.066209 | -0.10718 | 0.11548 | -0.038349 | -0.10252 | 0.041406 | -58.7997 | 64.1052 | -59.1797 | -59.3353 | 57.9895 | 2.8702 | -15.8478 | -13.9664 | 64.1785 | -59.2209 | -0.16479 | -0.059509 | 0.21515 | -0.32043 | -6.1752 | -0.20599 | 0.013733 | 0.37994 | 43.1671 | 45.0485 | 117.0044 | 123.1201 | 0.21515 | 123.1934 | 61.8851 | -0.20599 | 123.1201 | 0.21515 | 61.8851 | 117.0044 | 123.1934 | -123.3444 | -123.3856
561.6719 | 123.4222 | -58.9371 | 64.3204 | -0.28911 | -0.061936 | -0.10078 | 0.108 | -0.041553 | -0.10039 | 0.046747 | -58.7219 | 64.2838 | -59.0836 | -59.0927 | 58.1039 | 2.7237 | -16.0812 | -13.9664 | 64.2197 | -59.0744 | -0.14648 | -0.036622 | 0.21515 | -0.15564 | -6.2164 | -0.13733 | -0.10071 | 0.36163 | 42.8558 | 44.9707 | 117.041 | 123.2208 | 0.21515 | 123.1567 | 61.6608 | -0.13733 | 123.2208 | 0.21515 | 61.6608 | 117.041 | 123.1567 | -123.4039 | -123.3948
562.6719 | 123.4497 | -59.2987 | 63.9587 | -0.30437 | -0.069413 | -0.11146 | 0.10694 | -0.03194 | -0.097182 | 0.053156 | -59.0561 | 63.8901 | -59.4315 | -59.4864 | 56.7673 | 6.2393 | -14.3738 | -11.9202 | 63.9038 | -59.4452 | -0.13275 | -0.068664 | 0.24262 | -0.18768 | -7.1915 | -0.14648 | -0.054931 | 0.37537 | 44.9249 | 47.3785 | 116.066 | 123.1888 | 0.24262 | 123.2025 | 65.538 | -0.14648 | 123.1888 | 0.24262 | 65.538 | 116.066 | 123.2025 | -123.3902 | -123.4039
563.6719 | 123.4268 | -58.8821 | 64.3662 | -0.19756 | -0.045914 | -0.096503 | 0.11868 | -0.030872 | -0.089705 | 0.055292 | -58.6487 | 64.4211 | -59.0195 | -58.9828 | 57.6187 | 3.6804 | -15.3168 | -13.0417 | 64.2929 | -59.0424 | -0.13733 | 0.054932 | 0.23346 | -0.10071 | -6.7474 | -0.16022 | -0.073242 | 0.37079 | 43.5654 | 45.8405 | 116.5009 | 123.3032 | 0.23346 | 123.175 | 62.5626 | -0.16022 | 123.3032 | 0.23346 | 62.5626 | 116.5009 | 123.175 | -123.3856 | -123.4085
564.6719 | 123.642 | -59.0195 | 64.2654 | -0.19756 | -0.077958 | -0.1168 | 0.091982 | -0.023395 | -0.10466 | 0.055292 | -58.7173 | 64.1464 | -59.1568 | -59.3079 | 56.8634 | 4.7424 | -14.2319 | -12.204 | 64.183 | -59.1934 | -0.13733 | -0.11902 | 0.30212 | -0.28839 | -7.402 | -0.17395 | -0.082398 | 0.43945 | 44.7876 | 46.8155 | 115.8829 | 123.1659 | 0.30212 | 123.2025 | 63.7619 | -0.17395 | 123.1659 | 0.30212 | 63.7619 | 115.8829 | 123.2025 | -123.4222 | -123.4589
565.6719 | 123.5046 | -59.1843 | 64.0366 | 0.41279 | -0.075822 | -0.091163 | 0.099459 | -0.030872 | -0.10466 | 0.059564 | -58.9005 | 63.9359 | -59.3491 | -59.491 | 55.8929 | 7.4936 | -13.0875 | -10.8444 | 63.9954 | -59.3628 | -0.16479 | -0.10071 | 0.28381 | -0.3067 | -8.1436 | -0.17853 | -0.041199 | 0.44861 | 46.0968 | 48.3398 | 115.0772 | 123.1201 | 0.28381 | 123.1796 | 66.6779 | -0.17853 | 123.1201 | 0.28381 | 66.6779 | 115.0772 | 123.1796 | -123.3856 | -123.3994
566.6562 | 123.5184 | -59.0012 | 64.1922 | 0.031324 | -0.061936 | -0.10291 | 0.10159 | -0.030872 | -0.11107 | 0.064905 | -58.7173 | 64.119 | -59.1568 | -59.3079 | 56.1127 | 6.1111 | -13.5773 | -11.4258 | 64.1602 | -59.2072 | -0.15564 | -0.073242 | 0.28381 | -0.3067 | -8.0795 | -0.20599 | -0.032044 | 0.43945 | 45.4239 | 47.5754 | 115.1138 | 123.1201 | 0.28381 | 123.1613 | 65.1123 | -0.20599 | 123.1201 | 0.28381 | 65.1123 | 115.1138 | 123.1613 | -123.349 | -123.3994
567.6719 | 123.5184 | -58.9645 | 64.2242 | -0.029711 | -0.066209 | -0.11039 | 0.10053 | -0.033008 | -0.10573 | 0.05636 | -58.6395 | 64.1647 | -59.1385 | -59.2804 | 55.8334 | 6.3492 | -13.2385 | -11.1374 | 64.2151 | -59.1568 | -0.17395 | -0.059509 | 0.32501 | -0.31586 | -8.3908 | -0.19226 | -0.009155 | 0.49896 | 45.726 | 47.8271 | 114.798 | 123.1293 | 0.32501 | 123.1796 | 65.3137 | -0.19226 | 123.1293 | 0.32501 | 65.3137 | 114.798 | 123.1796 | -123.3627 | -123.381
568.6562 | 123.4909 | -58.6761 | 64.5401 | 0.12288 | -0.074754 | -0.10718 | 0.097323 | -0.040485 | -0.096114 | 0.062769 | -58.4015 | 64.4669 | -58.8455 | -58.9737 | 56.2912 | 4.7791 | -13.7878 | -11.7599 | 64.4852 | -58.8684 | -0.16937 | -0.073242 | 0.27466 | -0.29755 | -8.2489 | -0.19226 | -0.054932 | 0.44403 | 44.8883 | 46.9162 | 114.9673 | 123.143 | 0.27466 | 123.1613 | 63.4552 | -0.19226 | 123.143 | 0.27466 | 63.4552 | 114.9673 | 123.1613 | -123.3856 | -123.4085
569.6719 | 123.3994 | -58.9142 | 64.389 | -0.25859 | -0.055527 | -0.11252 | 0.11228 | -0.029804 | -0.096114 | 0.05636 | -58.5709 | 64.3524 | -59.0424 | -59.0424 | 55.6091 | 6.3492 | -13.2202 | -10.8765 | 64.3021 | -59.0149 | -0.12817 | -0.036621 | 0.34332 | -0.12817 | -8.7799 | -0.10071 | -0.086975 | 0.4715 | 45.694 | 48.0377 | 114.5233 | 123.2666 | 0.34332 | 123.2162 | 65.2634 | -0.10071 | 123.2666 | 0.34332 | 65.2634 | 114.5233 | 123.2162 | -123.4314 | -123.4039
570.6562 | 123.4772 | -58.8867 | 64.3662 | 0.29072 | -0.069413 | -0.10078 | 0.10694 | -0.039417 | -0.11 | 0.05636 | -58.5297 | 64.2792 | -59.0332 | -59.0927 | 55.2109 | 6.4865 | -13.2248 | -10.8994 | 64.2975 | -59.0561 | -0.14648 | -0.086975 | 0.35706 | -0.20599 | -9.1553 | -0.16937 | -0.068665 | 0.50354 | 45.6619 | 47.9874 | 114.0976 | 123.1659 | 0.35706 | 123.1842 | 65.3732 | -0.16937 | 123.1659 | 0.35706 | 65.3732 | 114.0976 | 123.1842 | -123.3994 | -123.4222
571.6719 | 123.5001 | -58.7448 | 64.4119 | -0.30437 | -0.058732 | -0.087958 | 0.10373 | -0.043689 | -0.12602 | 0.049951 | -58.3923 | 64.3478 | -58.9325 | -58.9417 | 55.3024 | 6.1295 | -13.385 | -11.0687 | 64.3753 | -58.9966 | -0.18768 | -0.064087 | 0.35248 | -0.19684 | -9.1095 | -0.25177 | -0.036621 | 0.54016 | 45.3598 | 47.6761 | 114.0472 | 123.0927 | 0.35248 | 123.1201 | 64.8743 | -0.25177 | 123.0927 | 0.35248 | 64.8743 | 114.0472 | 123.1201 | -123.3444 | -123.4085
572.6562 | 123.468 | -58.8821 | 64.3433 | 0.19917 | -0.069413 | -0.10078 | 0.097323 | -0.037281 | -0.096114 | 0.047815 | -58.5022 | 64.2975 | -59.0378 | -59.111 | 54.4922 | 7.1915 | -12.7945 | -10.4919 | 64.2975 | -59.0332 | -0.15564 | -0.045777 | 0.37994 | -0.22888 | -9.8511 | -0.15106 | -0.045777 | 0.53558 | 46.0876 | 48.3902 | 113.3743 | 123.1796 | 0.37994 | 123.1796 | 66.0736 | -0.15106 | 123.1796 | 0.37994 | 66.0736 | 113.3743 | 123.1796 | -123.381 | -123.3765
573.6719 | 123.5092 | -58.7402 | 64.4897 | 0.15339 | -0.051255 | -0.10932 | 0.097323 | -0.038349 | -0.10573 | 0.048883 | -58.3466 | 64.3982 | -58.8776 | -59.0057 | 54.4373 | 6.2759 | -12.8998 | -10.8765 | 64.4531 | -58.8959 | -0.13733 | -0.091553 | 0.39368 | -0.2655 | -10.0525 | -0.15564 | -0.036621 | 0.53101 | 45.8405 | 47.8638 | 113.1775 | 123.1384 | 0.39368 | 123.1934 | 65.0162 | -0.15564 | 123.1384 | 0.39368 | 65.0162 | 113.1775 | 123.1934 | -123.3673 | -123.3856
574.6719 | 123.5001 | -58.8135 | 64.3982 | -0.12126 | -0.072617 | -0.10398 | 0.11228 | -0.042621 | -0.099318 | 0.055292 | -58.3328 | 64.3616 | -58.9417 | -59.0836 | 53.4897 | 7.4432 | -12.3047 | -10.5698 | 64.3936 | -59.0195 | -0.12817 | -0.036621 | 0.48065 | -0.27008 | -10.9085 | -0.20599 | -0.004577 | 0.60883 | 46.5088 | 48.2437 | 112.3032 | 123.175 | 0.48065 | 123.2071 | 66.2567 | -0.20599 | 123.175 | 0.48065 | 66.2567 | 112.3032 | 123.2071 | -123.3398 | -123.4177
575.6719 | 123.5138 | -58.699 | 64.476 | -0.04497 | -0.060868 | -0.11466 | 0.089846 | -0.034076 | -0.10786 | 0.0617 | -58.2321 | 64.4211 | -58.8684 | -59.0469 | 53.3844 | 6.871 | -12.5198 | -10.5698 | 64.4394 | -58.8959 | -0.16937 | -0.054931 | 0.46692 | -0.3479 | -11.0916 | -0.19684 | -0.036621 | 0.63629 | 46.1792 | 48.1293 | 112.0834 | 123.1201 | 0.46692 | 123.1384 | 65.5701 | -0.19684 | 123.1201 | 0.46692 | 65.5701 | 112.0834 | 123.1384 | -123.3444 | -123.3719
576.6562 | 123.4314 | -58.7997 | 64.4302 | 0.44331 | -0.055527 | -0.10612 | 0.098391 | -0.050098 | -0.10252 | 0.047815 | -58.3145 | 64.3616 | -58.9279 | -59.0149 | 52.6703 | 8.0246 | -12.0575 | -9.9609 | 64.3845 | -58.9691 | -0.12817 | -0.068665 | 0.48523 | -0.21515 | -11.7599 | -0.16937 | -0.045777 | 0.6134 | 46.7422 | 48.8388 | 111.47 | 123.1613 | 0.48523 | 123.1842 | 66.8243 | -0.16937 | 123.1613 | 0.48523 | 66.8243 | 111.47 | 123.1842 | -123.3582 | -123.3994
577.6562 | 123.4863 | -58.6075 | 64.5859 | 0.5196 | -0.056596 | -0.11573 | 0.11441 | -0.035144 | -0.10252 | 0.053156 | -58.1131 | 64.5264 | -58.754 | -58.8409 | 52.7023 | 6.9672 | -12.5702 | -10.4645 | 64.5538 | -58.7769 | -0.14648 | -0.059509 | 0.49439 | -0.23346 | -11.8835 | -0.16937 | -0.032043 | 0.64087 | 46.0373 | 48.143 | 111.3098 | 123.1338 | 0.49439 | 123.1613 | 65.5746 | -0.16937 | 123.1338 | 0.49439 | 65.5746 | 111.3098 | 123.1613 | -123.3398 | -123.3627
578.6562 | 123.5046 | -58.5617 | 64.6133 | 0.56538 | -0.055527 | -0.08689 | 0.11228 | -0.035144 | -0.091842 | 0.052087 | -58.0078 | 64.5813 | -58.7173 | -59.0103 | 52.034 | 7.782 | -12.9181 | -11.0458 | 64.6042 | -58.7723 | -0.15564 | -0.032043 | 0.55389 | -0.44861 | -12.5793 | -0.21057 | -0.009155 | 0.70953 | 45.6436 | 47.5159 | 110.5957 | 123.143 | 0.55389 | 123.1659 | 66.3437 | -0.21057 | 123.143 | 0.55389 | 66.3437 | 110.5957 | 123.1659 | -123.3307 | -123.3856
579.6719 | 123.4818 | -58.5526 | 64.6317 | 0.15339 | -0.063004 | -0.09864 | 0.10694 | -0.041553 | -0.10573 | 0.063837 | -58.0124 | 64.5996 | -58.7173 | -58.8043 | 51.7181 | 8.7479 | -13.0875 | -11.0962 | 64.6317 | -58.7219 | -0.16479 | -0.032044 | 0.54016 | -0.25177 | -12.9135 | -0.16937 | 0 | 0.70496 | 45.4651 | 47.4564 | 110.2707 | 123.1522 | 0.54016 | 123.1842 | 67.3004 | -0.16937 | 123.1522 | 0.54016 | 67.3004 | 110.2707 | 123.1842 | -123.349 | -123.3536
580.6719 | 123.4634 | -58.4885 | 64.7232 | -0.04497 | -0.070481 | -0.10184 | 0.10266 | -0.043689 | -0.1068 | 0.054224 | -57.9483 | 64.6637 | -58.6716 | -58.7494 | 50.8713 | 8.9813 | -13.4216 | -11.3937 | 64.6729 | -58.6807 | -0.18311 | -0.05951 | 0.54016 | -0.26093 | -13.8519 | -0.19226 | -0.050354 | 0.72327 | 45.0668 | 47.0947 | 109.3597 | 123.1522 | 0.54016 | 123.1613 | 67.4698 | -0.19226 | 123.1522 | 0.54016 | 67.4698 | 109.3597 | 123.1613 | -123.3948 | -123.4039
581.6719 | 123.4726 | -58.8043 | 64.3936 | 0.32124 | -0.0598 | -0.094367 | 0.11762 | -0.042621 | -0.090773 | 0.054224 | -58.1909 | 64.3616 | -58.9462 | -59.0149 | 48.9166 | 11.2244 | -12.5244 | -10.5286 | 64.3936 | -58.9737 | -0.14191 | -0.032044 | 0.6134 | -0.21057 | -15.477 | -0.16937 | 0 | 0.75531 | 46.2799 | 48.2758 | 107.7209 | 123.1659 | 0.6134 | 123.1979 | 70.0287 | -0.16937 | 123.1659 | 0.6134 | 70.0287 | 107.7209 | 123.1979 | -123.3398 | -123.3673
582.6562 | 123.5184 | -58.9188 | 64.27 | 0.44331 | -0.061936 | -0.094367 | 0.11548 | -0.037281 | -0.096114 | 0.075586 | -58.1955 | 64.2792 | -59.0378 | -59.1522 | 47.6074 | 11.6638 | -12.4329 | -10.2722 | 64.2334 | -59.1248 | -0.11902 | 0.009155 | 0.72327 | -0.23346 | -16.6626 | -0.20599 | -0.036622 | 0.84229 | 46.4859 | 48.6465 | 106.5262 | 123.1979 | 0.72327 | 123.1522 | 70.5826 | -0.20599 | 123.1979 | 0.72327 | 70.5826 | 106.5262 | 123.1522 | -123.3078 | -123.3948
583.6719 | 123.4589 | -59.2575 | 63.9313 | -0.029711 | -0.061936 | -0.10718 | 0.099459 | -0.040485 | -0.096114 | 0.065973 | -58.6487 | 63.8855 | -59.4269 | -59.4681 | 45.4056 | 14.6255 | -11.9339 | -9.0637 | 63.8901 | -59.4406 | -0.16937 | -0.045776 | 0.60882 | -0.21057 | -18.5257 | -0.18311 | -0.041198 | 0.7782 | 47.3236 | 50.1938 | 104.6631 | 123.143 | 0.60882 | 123.1476 | 73.8831 | -0.18311 | 123.143 | 0.60882 | 73.8831 | 104.6631 | 123.1476 | -123.3582 | -123.3719
584.6719 | 123.5001 | -59.1751 | 64.032 | -0.21282 | -0.06514 | -0.092231 | 0.09305 | -0.030872 | -0.093978 | 0.07345 | -58.429 | 64.0045 | -59.2896 | -59.5276 | 44.6274 | 13.0737 | -12.3917 | -9.4391 | 64.0366 | -59.3353 | -0.11444 | -0.027465 | 0.74615 | -0.35248 | -19.4046 | -0.16022 | 0.004578 | 0.8606 | 46.7834 | 49.736 | 103.8025 | 123.1796 | 0.74615 | 123.2117 | 72.2488 | -0.16022 | 123.1796 | 0.74615 | 72.2488 | 103.8025 | 123.2117 | -123.3215 | -123.3673
585.6562 | 123.5138 | -58.7173 | 64.4714 | 0.42805 | -0.061936 | -0.10505 | 0.108 | -0.037281 | -0.076888 | 0.058496 | -57.9803 | 64.4485 | -58.8821 | -58.9371 | 41.9998 | 17.2943 | -14.0305 | -10.1257 | 64.4531 | -58.8867 | -0.16479 | -0.022889 | 0.737 | -0.21973 | -22.4716 | -0.16937 | -0.018311 | 0.90179 | 44.6869 | 48.5916 | 100.7172 | 123.1659 | 0.737 | 123.1705 | 76.0117 | -0.16937 | 123.1659 | 0.737 | 76.0117 | 100.7172 | 123.1705 | -123.3536 | -123.3582
586.6562 | 123.4955 | -58.6533 | 64.5401 | 0.58064 | -0.063004 | -0.08155 | 0.12403 | -0.030872 | -0.077956 | 0.063837 | -57.8613 | 64.5676 | -58.7952 | -58.8364 | 41.7526 | 15.9943 | -14.2548 | -10.4828 | 64.4943 | -58.8226 | -0.14191 | 0.027466 | 0.79193 | -0.18311 | -22.7875 | -0.16937 | -0.045776 | 0.93384 | 44.3985 | 48.1705 | 100.4059 | 123.2208 | 0.79193 | 123.1476 | 74.6475 | -0.16937 | 123.2208 | 0.79193 | 74.6475 | 100.4059 | 123.1476 | -123.3353 | -123.3627
587.6719 | 123.4726 | -58.5388 | 64.6774 | 0.36702 | -0.06514 | -0.10612 | 0.08771 | -0.035144 | -0.087569 | 0.063837 | -57.7835 | 64.595 | -58.7082 | -58.7448 | 40.8417 | 16.4612 | -14.6164 | -10.643 | 64.6454 | -58.6899 | -0.16937 | -0.082397 | 0.75531 | -0.20599 | -23.8358 | -0.15106 | -0.032043 | 0.92468 | 43.9224 | 47.8958 | 99.3805 | 123.1338 | 0.75531 | 123.1842 | 75 | -0.15106 | 123.1338 | 0.75531 | 75 | 99.3805 | 123.1842 | -123.3856 | -123.3673
588.6719 | 123.4634 | -58.2825 | 64.8972 | 0.45857 | -0.061936 | -0.085822 | 0.11228 | -0.039417 | -0.087569 | 0.070245 | -57.4265 | 64.856 | -58.4518 | -58.5663 | 38.8962 | 14.8499 | -15.0833 | -11.2518 | 64.8422 | -58.4564 | -0.16937 | -0.041199 | 0.85602 | -0.28381 | -26.001 | -0.17395 | -0.054932 | 1.0254 | 43.1992 | 47.0306 | 97.1787 | 123.1384 | 0.85602 | 123.1247 | 73.1323 | -0.17395 | 123.1384 | 0.85602 | 73.1323 | 97.1787 | 123.1247 | -123.349 | -123.3536
589.6719 | 123.4451 | -57.9666 | 65.2084 | 0.27546 | -0.064072 | -0.096503 | 0.10373 | -0.042621 | -0.10252 | 0.069177 | -57.1655 | 65.1901 | -58.0948 | -58.1909 | 39.5187 | 10.35 | -15.8707 | -11.7096 | 65.2039 | -58.1406 | -0.12817 | -0.01831 | 0.80109 | -0.2243 | -25.6897 | -0.17395 | -0.004578 | 0.92926 | 42.0959 | 46.257 | 97.4854 | 123.1567 | 0.80109 | 123.1705 | 68.3167 | -0.17395 | 123.1567 | 0.80109 | 68.3167 | 97.4854 | 123.1705 | -123.3032 | -123.349
590.6562 | 123.4543 | -58.168 | 65.0482 | 0.47383 | -0.048051 | -0.087958 | 0.13257 | -0.03194 | -0.073684 | 0.057428 | -57.2937 | 65.1031 | -58.3008 | -58.2687 | 39.093 | 10.5881 | -16.1957 | -12.0483 | 64.9979 | -58.2962 | -0.13275 | 0.054931 | 0.87433 | -0.10071 | -25.9552 | -0.12817 | -0.050354 | 1.0071 | 41.9724 | 46.1197 | 97.261 | 123.2712 | 0.87433 | 123.1659 | 68.7561 | -0.12817 | 123.2712 | 0.87433 | 68.7561 | 97.261 | 123.1659 | -123.349 | -123.3444
591.6719 | 123.4634 | -58.1726 | 64.9979 | 0.47383 | -0.045914 | -0.08689 | 0.10694 | -0.029804 | -0.086501 | 0.064905 | -57.2571 | 64.9658 | -58.3328 | -58.4381 | 38.0997 | 9.906 | -16.2964 | -12.2131 | 65.0024 | -58.3603 | -0.16022 | -0.032044 | 0.91553 | -0.2655 | -26.8982 | -0.18768 | 0.004577 | 1.0757 | 41.8762 | 45.9595 | 96.2723 | 123.1384 | 0.91553 | 123.175 | 68.0786 | -0.18768 | 123.1384 | 0.91553 | 68.0786 | 96.2723 | 123.175 | -123.3307 | -123.3582
592.6562 | 123.3536 | -58.2413 | 65.007 | 0.58064 | -0.035233 | -0.075141 | 0.13471 | -0.03194 | -0.070479 | 0.074518 | -57.2845 | 65.0574 | -58.3694 | -58.2687 | 37.0148 | 10.2768 | -16.3834 | -11.6776 | 64.8972 | -58.3557 | -0.12817 | 0.050354 | 0.95673 | -0.027466 | -27.9922 | -0.11444 | -0.10986 | 1.0849 | 41.8579 | 46.5637 | 95.256 | 123.2986 | 0.95673 | 123.1384 | 68.5181 | -0.11444 | 123.2986 | 0.95673 | 68.5181 | 95.256 | 123.1384 | -123.3765 | -123.3627
593.6562 | 123.4314 | -57.9666 | 65.2313 | 0.50435 | -0.06514 | -0.099708 | 0.11121 | -0.037281 | -0.074752 | 0.059564 | -57.0328 | 65.2817 | -58.1451 | -58.1039 | 35.4584 | 10.0342 | -16.8594 | -12.735 | 65.1947 | -58.1268 | -0.17853 | 0.050354 | 0.93384 | -0.13733 | -29.7729 | -0.16022 | -0.036621 | 1.1124 | 41.1072 | 45.2316 | 93.425 | 123.2483 | 0.93384 | 123.1613 | 68.0008 | -0.16022 | 123.2483 | 0.93384 | 68.0008 | 93.425 | 123.1613 | -123.3765 | -123.3582
594.6719 | 123.4863 | -57.1884 | 65.9912 | -1.4183 | -0.068345 | -0.11039 | 0.1048 | -0.025531 | -0.086501 | 0.079858 | -56.2271 | 65.9454 | -57.3395 | -57.4539 | 32.8217 | 6.9397 | -17.8894 | -14.502 | 65.9683 | -57.3898 | -0.15106 | -0.045776 | 0.9613 | -0.2655 | -33.1696 | -0.20142 | -0.022888 | 1.1124 | 39.299 | 42.6865 | 90.0101 | 123.1339 | 0.9613 | 123.1567 | 64.1281 | -0.20142 | 123.1339 | 0.9613 | 64.1281 | 90.0101 | 123.1567 | -123.3307 | -123.381
595.6719 | 123.4726 | -56.987 | 66.1972 | 0.50435 | -0.064072 | -0.089027 | 0.10587 | -0.026599 | -0.088637 | 0.067041 | -55.9891 | 66.1514 | -57.1701 | -57.2891 | 33.11 | 7.6355 | -18.0588 | -14.8544 | 66.1972 | -57.1838 | -0.1831 | -0.045777 | 0.99793 | -0.30212 | -33.0872 | -0.19684 | 0 | 1.181 | 38.9282 | 42.1326 | 90.097 | 123.1384 | 0.99793 | 123.1842 | 64.6225 | -0.19684 | 123.1384 | 0.99793 | 64.6225 | 90.097 | 123.1842 | -123.3673 | -123.381
596.6719 | 123.4818 | -57.0602 | 66.1011 | 0.5196 | -0.048051 | -0.087958 | 0.11121 | -0.043689 | -0.063003 | 0.069177 | -56.0074 | 66.124 | -57.2205 | -57.3624 | 32.2769 | 6.1707 | -17.2256 | -11.8515 | 66.0919 | -57.2937 | -0.16022 | 0.022888 | 1.0529 | -0.30212 | -33.8242 | -0.23346 | -0.009155 | 1.2131 | 39.8346 | 45.2087 | 89.3372 | 123.1842 | 1.0529 | 123.1522 | 63.2309 | -0.23346 | 123.1842 | 1.0529 | 63.2309 | 89.3372 | 123.1522 | -123.3215 | -123.3948
597.6562 | 123.5184 | -56.781 | 66.4124 | 0.58064 | -0.044846 | -0.10718 | 0.11228 | -0.039417 | -0.066207 | 0.067041 | -55.6824 | 66.4398 | -56.9 | -57.0602 | 30.8533 | -4.9805 | -17.7979 | -12.9089 | 66.3391 | -56.9962 | -0.11902 | 0.027465 | 1.0986 | -0.27924 | -35.5591 | -0.21515 | -0.073243 | 1.2177 | 38.9832 | 43.8721 | 87.6343 | 123.2208 | 1.0986 | 123.1201 | 51.8005 | -0.21515 | 123.2208 | 1.0986 | 51.8005 | 87.6343 | 123.1201 | -123.3124 | -123.4085
598.6562 | 123.349 | -57.2021 | 66.0278 | 0.35176 | -0.052323 | -0.083686 | 0.12189 | -0.026599 | -0.069411 | 0.064905 | -56.1035 | 66.1102 | -57.3303 | -57.2708 | 29.5029 | 4.303 | -17.6239 | -12.0438 | 65.9637 | -57.3303 | -0.12817 | 0.082397 | 1.0986 | -0.068665 | -36.525 | -0.12817 | -0.064087 | 1.2268 | 39.5782 | 45.1584 | 86.705 | 123.3124 | 1.0986 | 123.1659 | 61.5051 | -0.12817 | 123.3124 | 1.0986 | 61.5051 | 86.705 | 123.1659 | -123.3582 | -123.3582
599.6719 | 123.4726 | -56.8863 | 66.2613 | -0.22808 | -0.063004 | -0.092231 | 0.098391 | -0.028736 | -0.083297 | 0.074518 | -55.6229 | 66.2613 | -57.0969 | -57.2617 | 28.4409 | 2.5681 | -17.6971 | -12.3825 | 66.2704 | -57.1335 | -0.21057 | 0 | 1.2634 | -0.37537 | -37.8204 | -0.24719 | 0.009155 | 1.474 | 39.1891 | 44.5038 | 85.3271 | 123.1476 | 1.2634 | 123.1567 | 59.4543 | -0.24719 | 123.1476 | 1.2634 | 59.4543 | 85.3271 | 123.1567 | -123.3582 | -123.3948
600.6562 | 123.3627 | -56.2454 | 67.0029 | 0.50435 | -0.048051 | -0.10718 | 0.13257 | -0.020191 | -0.071547 | 0.069177 | -55.1285 | 67.0807 | -56.3873 | -56.282 | 27.6077 | -7.2968 | -18.7317 | -14.1724 | 66.9479 | -56.3553 | -0.14191 | 0.077819 | 1.1169 | -0.036621 | -39.3951 | -0.10986 | -0.054932 | 1.2589 | 37.5137 | 42.0731 | 83.8531 | 123.3261 | 1.1169 | 123.1934 | 48.9487 | -0.10986 | 123.3261 | 1.1169 | 48.9487 | 83.8531 | 123.1934 | -123.3902 | -123.3582
601.6562 | 123.3765 | -56.2363 | 67.012 | 4.9141 | -0.041642 | -0.10718 | 0.12403 | -0.021259 | -0.07582 | 0.062769 | -54.9271 | 67.0761 | -56.3828 | -56.282 | 27.6398 | 2.71 | -19.455 | -14.5111 | 66.9479 | -56.337 | -0.14648 | 0.064087 | 1.3092 | -0.045776 | -39.3723 | -0.10071 | -0.064087 | 1.4557 | 36.7813 | 41.7252 | 83.876 | 123.3124 | 1.3092 | 123.1842 | 58.9462 | -0.10071 | 123.3124 | 1.3092 | 58.9462 | 83.876 | 123.1842 | -123.3948 | -123.349
602.6562 | 123.3627 | -56.4651 | 66.7923 | 0.50435 | -0.051255 | -0.097572 | 0.11868 | -0.029804 | -0.074752 | 0.072382 | -55.3299 | 66.8243 | -56.6345 | -56.5796 | 26.1612 | 1.7258 | -18.6813 | -11.9751 | 66.687 | -56.5796 | -0.16937 | 0.032044 | 1.1353 | -0.11444 | -40.6311 | -0.11444 | -0.10529 | 1.3046 | 37.7838 | 44.4901 | 82.6263 | 123.2895 | 1.1353 | 123.1522 | 58.1909 | -0.11444 | 123.2895 | 1.1353 | 58.1909 | 82.6263 | 123.1522 | -123.4268 | -123.3719
603.6719 | 123.4634 | -56.3599 | 66.8106 | 0.53486 | -0.060868 | -0.061256 | 0.098391 | -0.035144 | -0.074752 | 0.07879 | -55.3482 | 66.7877 | -56.543 | -56.6528 | 23.7854 | -10.4324 | -20.2103 | -15.6326 | 66.8289 | -56.5659 | -0.18311 | -0.022888 | 1.0117 | -0.29297 | -43.0252 | -0.20599 | 0.01831 | 1.1948 | 36.1496 | 40.7272 | 80.1453 | 123.1476 | 1.0117 | 123.1888 | 45.9274 | -0.20599 | 123.1476 | 1.0117 | 45.9274 | 80.1453 | 123.1888 | -123.3536 | -123.3765
604.6719 | 123.5138 | -57.0465 | 66.1148 | 0.092359 | -0.064072 | -0.10078 | 0.094119 | -0.039417 | -0.074752 | 0.084131 | -55.8517 | 66.1194 | -57.2296 | -57.3715 | 24.7513 | 0.26093 | -18.9651 | -14.4745 | 66.1011 | -57.2571 | -0.1831 | 0.004578 | 1.1948 | -0.32501 | -41.3635 | -0.21057 | -0.013733 | 1.3779 | 38.0814 | 42.572 | 81.7978 | 123.1659 | 1.1948 | 123.1476 | 57.3074 | -0.21057 | 123.1659 | 1.1948 | 57.3074 | 81.7978 | 123.1476 | -123.3444 | -123.3719
605.6562 | 123.4177 | -56.8039 | 66.4124 | 0.56538 | -0.057664 | -0.079414 | 0.12296 | -0.029804 | -0.063003 | 0.079858 | -55.6 | 66.4856 | -56.955 | -56.8726 | 24.6094 | -0.20599 | -18.3517 | -15.1611 | 66.3528 | -56.9183 | -0.15106 | 0.073242 | 1.2039 | -0.068665 | -41.803 | -0.11444 | -0.05951 | 1.355 | 38.4521 | 41.6428 | 81.4133 | 123.2895 | 1.2039 | 123.1567 | 56.5979 | -0.11444 | 123.2895 | 1.2039 | 56.5979 | 81.4133 | 123.1567 | -123.3673 | -123.3307
606.6562 | 123.3582 | -55.307 | 67.9321 | 0.30598 | -0.058732 | -0.096503 | 0.12296 | -0.029804 | -0.069411 | 0.077722 | -54.0939 | 67.9459 | -55.4901 | -55.426 | 23.7808 | -1.4969 | -20.3339 | -15.7608 | 67.836 | -55.4764 | -0.18311 | 0.013733 | 1.2131 | -0.11902 | -44.1513 | -0.16937 | -0.09613 | 1.3962 | 34.9731 | 39.5462 | 79.0878 | 123.2529 | 1.2131 | 123.143 | 53.8101 | -0.16937 | 123.2529 | 1.2131 | 53.8101 | 79.0878 | 123.143 | -123.4222 | -123.4085
607.6719 | 123.4543 | -55.0598 | 68.0786 | 0.53486 | -0.055527 | -0.083686 | 0.10266 | -0.028736 | -0.064071 | 0.074518 | -53.714 | 68.1427 | -55.1926 | -55.3482 | 23.7991 | -4.5822 | -24.4995 | -17.6147 | 68.1427 | -55.2383 | -0.13275 | 0.064087 | 1.3458 | -0.28839 | -44.2795 | -0.17853 | 0.064087 | 1.4786 | 30.5603 | 37.4451 | 78.8589 | 123.2025 | 1.3458 | 123.2025 | 50.4776 | -0.17853 | 123.2025 | 1.3458 | 50.4776 | 78.8589 | 123.2025 | -123.2712 | -123.317
608.6719 | 123.4818 | -54.0344 | 69.1498 | 0.56538 | -0.055527 | -0.073005 | 0.11334 | -0.029804 | -0.066207 | 0.083063 | -52.7206 | 69.2596 | -54.1489 | -54.1992 | 24.6963 | -4.9622 | -31.2241 | -21.8994 | 69.1635 | -54.1763 | -0.11444 | 0.10986 | 1.3138 | -0.16479 | -44.4534 | -0.14191 | 0.013733 | 1.4282 | 22.8104 | 32.135 | 78.7308 | 123.2941 | 1.3138 | 123.1979 | 49.0723 | -0.14191 | 123.2941 | 1.3138 | 49.0723 | 78.7308 | 123.1979 | -123.2986 | -123.3261
609.6719 | 123.4818 | -53.7781 | 69.4244 | -0.21282 | -0.056596 | -0.099708 | 0.10373 | -0.029804 | -0.088637 | 0.081995 | -52.3865 | 69.4061 | -53.9108 | -54.2404 | 23.5291 | -5.983 | -32.4509 | -22.3389 | 69.429 | -54.007 | -0.13275 | -0.01831 | 1.3916 | -0.46234 | -45.8954 | -0.22888 | 0.004578 | 1.5244 | 21.3272 | 31.4392 | 77.3071 | 123.1842 | 1.3916 | 123.2071 | 47.7951 | -0.22888 | 123.1842 | 1.3916 | 47.7951 | 77.3071 | 123.2071 | -123.3353 | -123.4314
610.6562 | 123.3948 | -53.7506 | 69.5343 | 0.56538 | -0.040574 | -0.080482 | 0.11868 | -0.030872 | -0.071547 | 0.074518 | -52.5787 | 69.5114 | -53.8879 | -53.8879 | 22.3526 | -5.9097 | -36.2045 | -29.5807 | 69.4382 | -53.8971 | -0.13733 | -0.022888 | 1.1719 | -0.13733 | -47.1817 | -0.14648 | -0.096131 | 1.3092 | 17.5461 | 24.1699 | 76.1032 | 123.262 | 1.1719 | 123.1888 | 47.8409 | -0.14648 | 123.262 | 1.1719 | 47.8409 | 76.1032 | 123.1888 | -123.4222 | -123.4314
611.6719 | 123.4818 | -53.2837 | 69.9005 | 1.0842 | -0.060868 | -0.083686 | 0.10159 | -0.036213 | -0.087569 | 0.076654 | -51.7639 | 69.9005 | -53.4302 | -53.5858 | 19.812 | -13.7192 | -37.7747 | -31.2332 | 69.8822 | -53.4943 | -0.14649 | 0 | 1.5198 | -0.30212 | -50.0885 | -0.21057 | -0.018311 | 1.6663 | 15.509 | 22.0505 | 73.0957 | 123.1842 | 1.5198 | 123.1659 | 39.5645 | -0.21057 | 123.1842 | 1.5198 | 39.5645 | 73.0957 | 123.1659 | -123.3307 | -123.3948
612.6719 | 123.3902 | -52.8671 | 70.3445 | 0.48909 | -0.045914 | -0.093299 | 0.11548 | -0.034076 | -0.068343 | 0.089471 | -51.5121 | 70.3857 | -53.0319 | -53.0182 | 19.0613 | -12.0987 | -41.4413 | -29.8462 | 70.3033 | -53.009 | -0.16479 | 0.041199 | 1.355 | -0.15106 | -51.2833 | -0.14191 | -0.041198 | 1.5198 | 11.4258 | 23.0209 | 71.9284 | 123.2529 | 1.355 | 123.1705 | 40.7684 | -0.14191 | 123.2529 | 1.355 | 40.7684 | 71.9284 | 123.1705 | -123.3765 | -123.3536
613.6562 | 123.4039 | -52.7527 | 70.5276 | 0.47383 | -0.041642 | -0.079414 | 0.11762 | -0.030872 | -0.061934 | 0.093744 | -51.3336 | 70.5597 | -52.8763 | -52.8168 | 18.576 | -9.6497 | -41.5054 | -30.574 | 70.4315 | -52.858 | -0.1236 | 0.032043 | 1.4191 | -0.064086 | -51.9516 | -0.10529 | -0.09613 | 1.5427 | 11.2473 | 22.1786 | 71.3287 | 123.3124 | 1.4191 | 123.1842 | 43.103 | -0.10529 | 123.3124 | 1.4191 | 43.103 | 71.3287 | 123.1842 | -123.4039 | -123.3856
614.6719 | 123.4772 | -52.8671 | 70.3262 | 0.061841 | -0.0598 | -0.12 | 0.096255 | -0.033008 | -0.079024 | 0.091608 | -51.4297 | 70.2942 | -53.0365 | -53.1647 | 16.9739 | -10.0616 | -43.277 | -32.0892 | 70.3308 | -53.0502 | -0.16937 | -0.032044 | 1.4374 | -0.29755 | -53.3524 | -0.18311 | 0.004578 | 1.6067 | 9.5901 | 20.7779 | 69.841 | 123.1613 | 1.4374 | 123.1979 | 42.8055 | -0.18311 | 123.1613 | 1.4374 | 42.8055 | 69.841 | 123.1979 | -123.3627 | -123.3765
615.6719 | 123.3902 | -52.7161 | 70.5231 | -0.27385 | -0.048051 | -0.11252 | 0.12616 | -0.024463 | -0.052321 | 0.087335 | -51.2695 | 70.5276 | -52.9083 | -52.8442 | 15.7059 | -9.8557 | -43.1534 | -32.4188 | 70.4544 | -52.9083 | -0.19226 | 0.004578 | 1.4465 | -0.12817 | -54.8172 | -0.19226 | -0.068664 | 1.6388 | 9.5627 | 20.2972 | 68.4219 | 123.2437 | 1.4465 | 123.1705 | 42.8604 | -0.19226 | 123.2437 | 1.4465 | 42.8604 | 68.4219 | 123.1705 | -123.4314 | -123.4314
616.6562 | 123.5138 | -52.0889 | 71.0632 | 0.32124 | -0.061936 | -0.068732 | 0.10694 | -0.043689 | -0.056594 | 0.080927 | -50.6012 | 71.0678 | -52.2629 | -52.4139 | 15.8844 | -11.3663 | -42.8879 | -36.4197 | 71.1044 | -52.3178 | -0.17395 | 0.004578 | 1.4877 | -0.32501 | -55.1788 | -0.22888 | 0.041199 | 1.6617 | 9.2011 | 15.6693 | 67.9733 | 123.1567 | 1.4877 | 123.1934 | 40.7227 | -0.22888 | 123.1567 | 1.4877 | 40.7227 | 67.9733 | 123.1934 | -123.3261 | -123.381
617.6562 | 123.4589 | -52.5009 | 70.6879 | 0.45857 | -0.048051 | -0.096503 | 0.10694 | -0.038349 | -0.063003 | 0.075586 | -50.9445 | 70.7062 | -52.6291 | -52.7847 | 16.008 | -8.9218 | -44.7235 | -33.4625 | 70.665 | -52.7069 | -0.12817 | 0.018311 | 1.5564 | -0.28381 | -54.6799 | -0.20599 | -0.022888 | 1.6846 | 7.7774 | 19.0384 | 68.5089 | 123.2071 | 1.5564 | 123.1659 | 43.5791 | -0.20599 | 123.2071 | 1.5564 | 43.5791 | 68.5089 | 123.1659 | -123.317 | -123.3948
618.6562 | 123.3673 | -52.2583 | 71.0129 | 0.38228 | -0.038438 | -0.077277 | 0.13257 | -0.033008 | -0.05873 | 0.092676 | -50.7156 | 71.0495 | -52.4185 | -52.3544 | 15.6097 | -9.0088 | -44.4214 | -37.5687 | 70.9259 | -52.3773 | -0.16022 | 0.036622 | 1.5427 | -0.09613 | -55.4031 | -0.11902 | -0.086975 | 1.7029 | 7.8369 | 14.6896 | 67.868 | 123.3078 | 1.5427 | 123.1842 | 43.2495 | -0.11902 | 123.3078 | 1.5427 | 43.2495 | 67.868 | 123.1842 | -123.4314 | -123.3902
619.6719 | 123.5092 | -52.327 | 70.8298 | -0.060229 | -0.070481 | -0.080482 | 0.1048 | -0.03194 | -0.061934 | 0.092676 | -50.7156 | 70.7977 | -52.5101 | -52.6932 | 14.3234 | -7.2327 | -44.3985 | -38.3835 | 70.8572 | -52.565 | -0.18311 | -0.032044 | 1.6113 | -0.36621 | -56.5063 | -0.23804 | 0.027466 | 1.7944 | 7.9285 | 13.9435 | 66.6504 | 123.1247 | 1.6113 | 123.1842 | 45.0943 | -0.23804 | 123.1247 | 1.6113 | 45.0943 | 66.6504 | 123.1842 | -123.3398 | -123.3948
620.6719 | 123.3765 | -51.6815 | 71.4981 | -0.21282 | -0.060868 | -0.099708 | 0.10694 | -0.028736 | -0.061934 | 0.087335 | -50.061 | 71.5302 | -51.8646 | -51.9012 | 13.1195 | -6.0654 | -44.0689 | -39.3997 | 71.4661 | -51.8692 | -0.1831 | 0.032043 | 1.6205 | -0.21973 | -58.3786 | -0.18768 | -0.032044 | 1.8036 | 7.6126 | 12.2818 | 64.801 | 123.2117 | 1.6205 | 123.1476 | 45.6162 | -0.18768 | 123.2117 | 1.6205 | 45.6162 | 64.801 | 123.1476 | -123.3627 | -123.3673
621.6562 | 123.4772 | -50.9995 | 72.1848 | 0.45857 | -0.053391 | -0.09864 | 0.12509 | -0.037281 | -0.068343 | 0.09054 | -49.3698 | 72.2168 | -51.1642 | -51.2329 | 12.2635 | -9.5032 | -43.9911 | -39.5828 | 72.1664 | -51.2054 | -0.16479 | 0.032044 | 1.6296 | -0.23346 | -59.9213 | -0.20599 | -0.01831 | 1.7944 | 7.0084 | 11.4166 | 63.2629 | 123.2162 | 1.6296 | 123.1659 | 41.4963 | -0.20599 | 123.2162 | 1.6296 | 41.4963 | 63.2629 | 123.1659 | -123.349 | -123.3902
622.6562 | 123.468 | -50.4456 | 72.757 | 0.55012 | -0.051255 | -0.099708 | 0.11655 | -0.042621 | -0.046981 | 0.093744 | -48.7976 | 72.7661 | -50.6332 | -50.6699 | 10.437 | -9.0088 | -44.0231 | -39.5004 | 72.7386 | -50.6287 | -0.18768 | 0.009155 | 1.648 | -0.2243 | -62.3199 | -0.1831 | -0.018311 | 1.8356 | 6.4224 | 10.9451 | 60.8826 | 123.2117 | 1.648 | 123.1842 | 41.4368 | -0.1831 | 123.2117 | 1.648 | 41.4368 | 60.8826 | 123.1842 | -123.3902 | -123.3856
623.6719 | 123.4451 | -50.2487 | 72.9034 | 0.48909 | -0.049119 | -0.11146 | 0.11014 | -0.036213 | -0.076888 | 0.10015 | -48.5413 | 72.8943 | -50.4227 | -50.5783 | 9.8282 | -8.2306 | -44.0048 | -40.416 | 72.9034 | -50.4822 | -0.17395 | -0.009155 | 1.7075 | -0.32959 | -63.0753 | -0.23346 | 0 | 1.8814 | 6.2439 | 9.8328 | 60.0769 | 123.143 | 1.7075 | 123.1522 | 42.0181 | -0.23346 | 123.143 | 1.7075 | 42.0181 | 60.0769 | 123.1522 | -123.3261 | -123.3856
624.6719 | 123.4314 | -50.7156 | 72.4686 | 0.41279 | -0.056596 | -0.10078 | 0.098391 | -0.035144 | -0.068343 | 0.083063 | -49.0402 | 72.4228 | -50.8896 | -50.9766 | 9.6222 | -8.0383 | -44.3527 | -40.5716 | 72.4411 | -50.8896 | -0.17395 | -0.045776 | 1.6754 | -0.26093 | -62.8464 | -0.17395 | -0.027466 | 1.8494 | 6.3629 | 10.144 | 60.3378 | 123.1384 | 1.6754 | 123.1567 | 42.6773 | -0.17395 | 123.1384 | 1.6754 | 42.6773 | 60.3378 | 123.1567 | -123.3582 | -123.3582
625.6719 | 123.349 | -50.6149 | 72.6517 | -0.13652 | -0.064072 | -0.10078 | 0.11975 | -0.026599 | -0.052321 | 0.10122 | -48.8663 | 72.67 | -50.7294 | -50.6973 | 7.0816 | -1.7715 | -44.5633 | -40.4114 | 72.6059 | -50.7294 | -0.11444 | 0.018311 | 1.7487 | -0.082398 | -65.5701 | -0.11444 | -0.045776 | 1.8631 | 6.0516 | 10.2036 | 57.6965 | 123.2849 | 1.7487 | 123.2208 | 48.8434 | -0.11444 | 123.2849 | 1.7487 | 48.8434 | 57.6965 | 123.2208 | -123.381 | -123.381
626.6562 | 123.3902 | -50.56 | 72.6837 | 0.12288 | -0.040574 | -0.090095 | 0.13364 | -0.037281 | -0.059798 | 0.088403 | -48.7885 | 72.7341 | -50.679 | -50.6699 | 7.9376 | -0.91095 | -45.0439 | -40.654 | 72.5922 | -50.6836 | -0.11902 | 0.050354 | 1.7715 | -0.10986 | -64.7461 | -0.1236 | -0.091553 | 1.8906 | 5.5161 | 9.906 | 58.4976 | 123.2941 | 1.7715 | 123.1522 | 49.649 | -0.1236 | 123.2941 | 1.7715 | 49.649 | 58.4976 | 123.1522 | -123.3627 | -123.3673
627.6719 | 123.4818 | -50.9766 | 72.2031 | 0.45857 | -0.045914 | -0.075141 | 0.11441 | -0.033008 | -0.05873 | 0.10015 | -49.1364 | 72.2031 | -51.1505 | -51.265 | 7.6584 | -0.64545 | -45.0348 | -40.9927 | 72.171 | -51.178 | -0.17395 | 0 | 1.8402 | -0.28839 | -64.5447 | -0.20142 | -0.032043 | 2.0142 | 5.9418 | 9.9838 | 58.6349 | 123.1796 | 1.8402 | 123.1476 | 50.3311 | -0.20142 | 123.1796 | 1.8402 | 50.3311 | 58.6349 | 123.1476 | -123.3536 | -123.381
628.6719 | 123.4222 | -51.2924 | 71.9055 | 0.39753 | -0.045914 | -0.11893 | 0.11334 | -0.019123 | -0.068343 | 0.092676 | -49.4385 | 71.8506 | -51.4206 | -51.5259 | 7.9605 | 1.1627 | -45.2591 | -41.0202 | 71.9147 | -51.4481 | -0.12817 | -0.054932 | 1.8539 | -0.23346 | -63.945 | -0.15564 | 0.009155 | 1.9821 | 6.0333 | 10.2722 | 59.2529 | 123.143 | 1.8539 | 123.2071 | 52.4551 | -0.15564 | 123.143 | 1.8539 | 52.4551 | 59.2529 | 123.2071 | -123.3261 | -123.3536
629.6719 | 123.5184 | -50.8804 | 72.2992 | -0.1823 | -0.06514 | -0.092231 | 0.09305 | -0.033008 | -0.05873 | 0.098016 | -48.9761 | 72.2992 | -51.0269 | -51.1871 | 8.0063 | 1.3641 | -44.9753 | -40.8005 | 72.345 | -51.059 | -0.14648 | 0 | 1.9043 | -0.3067 | -64.2929 | -0.17853 | 0.045777 | 2.0508 | 5.9052 | 10.08 | 58.8867 | 123.1796 | 1.9043 | 123.2254 | 52.2446 | -0.17853 | 123.1796 | 1.9043 | 52.2446 | 58.8867 | 123.2254 | -123.3261 | -123.3582
630.6719 | 123.4543 | -50.8118 | 72.3816 | -0.16704 | -0.054459 | -0.090095 | 0.10266 | -0.036213 | -0.068343 | 0.087335 | -48.9075 | 72.3404 | -50.9766 | -51.1002 | 6.926 | 0.88806 | -44.9844 | -40.9332 | 72.3495 | -51.0132 | -0.16479 | -0.041199 | 1.9043 | -0.28839 | -65.4556 | -0.20142 | -0.032044 | 2.0691 | 5.8273 | 9.8785 | 57.7377 | 123.1522 | 1.9043 | 123.1613 | 51.6998 | -0.20142 | 123.1522 | 1.9043 | 51.6998 | 57.7377 | 123.1613 | -123.3582 | -123.3948
631.6719 | 123.4177 | -50.2579 | 72.9126 | 0.44331 | -0.0598 | -0.10398 | 0.10694 | -0.040485 | -0.070479 | 0.096948 | -48.3627 | 72.8348 | -50.4501 | -50.5463 | 4.5456 | 1.6708 | -45.0531 | -41.5329 | 72.8989 | -50.4822 | -0.19226 | -0.07782 | 1.8951 | -0.28839 | -68.367 | -0.2243 | -0.013733 | 2.0874 | 5.2048 | 8.725 | 54.8035 | 123.0927 | 1.8951 | 123.1567 | 51.9287 | -0.2243 | 123.0927 | 1.8951 | 51.9287 | 54.8035 | 123.1567 | -123.3627 | -123.3948
632.6562 | 123.4772 | -49.8825 | 73.3154 | 0.65693 | -0.058732 | -0.075141 | 0.11975 | -0.043689 | -0.057662 | 0.092676 | -47.8867 | 73.288 | -50.0336 | -50.1434 | 3.0121 | 0.25635 | -44.4901 | -41.1667 | 73.2788 | -50.0702 | -0.15106 | -0.027466 | 1.9958 | -0.26093 | -70.3033 | -0.18768 | -0.036621 | 2.1469 | 5.3925 | 8.7158 | 52.8946 | 123.1705 | 1.9958 | 123.1613 | 50.1389 | -0.18768 | 123.1705 | 1.9958 | 50.1389 | 52.8946 | 123.1613 | -123.349 | -123.3856
633.6562 | 123.4863 | -50.1205 | 73.027 | 0.96211 | -0.04271 | -0.10505 | 0.11548 | -0.03194 | -0.053389 | 0.081995 | -48.0515 | 73.0682 | -50.2899 | -50.3815 | 2.5955 | -0.11444 | -45.1492 | -42.8696 | 73.0408 | -50.3448 | -0.16937 | 0.041198 | 2.0691 | -0.26093 | -70.4315 | -0.22431 | 0.013732 | 2.2385 | 4.9713 | 7.251 | 52.7161 | 123.1888 | 2.0691 | 123.1613 | 50.0061 | -0.22431 | 123.1888 | 2.0691 | 50.0061 | 52.7161 | 123.1613 | -123.317 | -123.3719
634.6719 | 123.4406 | -49.205 | 73.9838 | -0.30437 | -0.063004 | -0.082618 | 0.095187 | -0.037281 | -0.068343 | 0.098016 | -47.2687 | 73.9014 | -49.3973 | -49.4705 | -1.4923 | -3.5065 | -44.3024 | -42.485 | 73.9792 | -49.3973 | -0.19226 | -0.082398 | 1.9363 | -0.2655 | -75.4761 | -0.19226 | -0.004578 | 2.1286 | 4.9026 | 6.72 | 47.7127 | 123.1064 | 1.9363 | 123.1842 | 45.6985 | -0.19226 | 123.1064 | 1.9363 | 45.6985 | 47.7127 | 123.1842 | -123.381 | -123.381
635.6719 | 123.436 | -48.9304 | 74.263 | 0.30598 | -0.057664 | -0.093299 | 0.10159 | -0.036213 | -0.055526 | 0.10336 | -46.8338 | 74.231 | -49.0448 | -49.173 | -3.0304 | -5.0629 | -42.897 | -40.7318 | 74.2493 | -49.0997 | -0.11444 | -0.032043 | 2.0966 | -0.24262 | -77.2934 | -0.16937 | -0.013732 | 2.211 | 6.0333 | 8.1985 | 45.9 | 123.1613 | 2.0966 | 123.1796 | 43.8675 | -0.16937 | 123.1613 | 2.0966 | 43.8675 | 45.9 | 123.1796 | -123.3078 | -123.3627
636.6562 | 123.5229 | -48.9853 | 74.2172 | 0.5959 | -0.058732 | -0.10184 | 0.11548 | -0.039417 | -0.053389 | 0.098016 | -46.582 | 74.2218 | -49.0814 | -49.2233 | -3.5522 | -5.5435 | -43.3273 | -42.0502 | 74.2035 | -49.1821 | -0.09613 | 0.004578 | 2.4033 | -0.23804 | -77.7695 | -0.19684 | -0.013733 | 2.4994 | 5.658 | 6.9351 | 45.433 | 123.2071 | 2.4033 | 123.1888 | 43.4418 | -0.19684 | 123.2071 | 2.4033 | 43.4418 | 45.433 | 123.1888 | -123.2986 | -123.3994
637.6719 | 123.4497 | -48.3078 | 74.8764 | 0.031324 | -0.06514 | -0.11252 | 0.108 | -0.040485 | -0.07582 | 0.10656 | -45.9869 | 74.8215 | -48.4634 | -48.6145 | -4.2892 | -6.3309 | -42.9108 | -41.5787 | 74.8535 | -48.5046 | -0.15564 | -0.054932 | 2.3209 | -0.3067 | -79.1656 | -0.19684 | -0.022888 | 2.4765 | 5.397 | 6.7291 | 44.0186 | 123.1293 | 2.3209 | 123.1613 | 41.9769 | -0.19684 | 123.1293 | 2.3209 | 41.9769 | 44.0186 | 123.1613 | -123.3398 | -123.381
638.6562 | 123.436 | -47.8775 | 75.3113 | 0.64167 | -0.046983 | -0.090095 | 0.12296 | -0.04903 | -0.046981 | 0.088403 | -45.3918 | 75.325 | -48.0286 | -48.0789 | -4.3121 | -5.9235 | -42.0822 | -40.5533 | 75.2838 | -48.0698 | -0.15106 | 0.013733 | 2.4857 | -0.20142 | -79.6234 | -0.19226 | -0.027466 | 2.6367 | 5.7953 | 7.3242 | 43.5654 | 123.2025 | 2.4857 | 123.1613 | 41.954 | -0.19226 | 123.2025 | 2.4857 | 41.954 | 43.5654 | 123.1613 | -123.3398 | -123.381
639.6719 | 123.4589 | -47.0947 | 76.0666 | 0.12288 | -0.064072 | -0.10291 | 0.10694 | -0.044757 | -0.055526 | 0.10549 | -44.6732 | 76.0437 | -47.2549 | -47.374 | -6.3263 | -8.0154 | -42.3431 | -40.741 | 76.0666 | -47.2641 | -0.16022 | -0.022888 | 2.4216 | -0.27923 | -82.3929 | -0.16937 | 0 | 2.5818 | 4.7516 | 6.3538 | 40.7684 | 123.1384 | 2.4216 | 123.1613 | 39.0793 | -0.16937 | 123.1384 | 2.4216 | 39.0793 | 40.7684 | 123.1613 | -123.3215 | -123.3307
640.6562 | 123.4818 | -46.8658 | 76.3092 | 0.55012 | -0.050187 | -0.085822 | 0.12082 | -0.035144 | -0.051253 | 0.11083 | -44.2886 | 76.3138 | -46.9986 | -47.0993 | -7.6126 | -9.2743 | -41.2445 | -40.0223 | 76.3046 | -47.0673 | -0.13275 | 0.004578 | 2.5772 | -0.23346 | -83.9218 | -0.20142 | -0.004578 | 2.71 | 5.6213 | 6.8436 | 39.2532 | 123.1796 | 2.5772 | 123.1705 | 37.5916 | -0.20142 | 123.1796 | 2.5772 | 37.5916 | 39.2532 | 123.1705 | -123.3078 | -123.3765
641.6562 | 123.4497 | -46.3257 | 76.8356 | 0.53486 | -0.050187 | -0.089027 | 0.11014 | -0.040485 | -0.051253 | 0.10336 | -43.8858 | 76.8997 | -46.4127 | -46.6278 | -9.5718 | -11.174 | -41.0889 | -39.8346 | 76.8036 | -46.5363 | -0.086975 | 0.064087 | 2.4399 | -0.30212 | -86.4075 | -0.21057 | -0.032043 | 2.5269 | 5.2368 | 6.4911 | 36.7538 | 123.2254 | 2.4399 | 123.1293 | 35.1517 | -0.21057 | 123.2254 | 2.4399 | 35.1517 | 36.7538 | 123.1293 | -123.2483 | -123.3719
642.6562 | 123.4589 | -46.7422 | 76.4008 | 0.5959 | -0.061936 | -0.10612 | 0.12616 | -0.041553 | -0.059798 | 0.10443 | -44.0552 | 76.4008 | -46.8933 | -47.0535 | -8.2581 | -9.8145 | -40.5075 | -39.473 | 76.4191 | -46.9574 | -0.15106 | 0 | 2.6871 | -0.31128 | -84.6588 | -0.21515 | 0.01831 | 2.8381 | 6.2347 | 7.2693 | 38.4842 | 123.143 | 2.6871 | 123.1613 | 36.9278 | -0.21515 | 123.143 | 2.6871 | 36.9278 | 38.4842 | 123.1613 | -123.2941 | -123.3582
643.6719 | 123.4268 | -46.9208 | 76.2588 | 0.27546 | -0.053391 | -0.11787 | 0.10373 | -0.030872 | -0.08116 | 0.10763 | -44.22 | 76.2863 | -47.0398 | -47.2229 | -7.5211 | -8.8028 | -40.3976 | -39.3951 | 76.2405 | -47.0993 | -0.11902 | 0.027466 | 2.7008 | -0.30212 | -83.7799 | -0.17853 | -0.01831 | 2.8198 | 6.5231 | 7.5256 | 39.3997 | 123.2071 | 2.7008 | 123.1613 | 38.118 | -0.17853 | 123.2071 | 2.7008 | 38.118 | 39.3997 | 123.1613 | -123.2986 | -123.3582
644.6719 | 123.3902 | -46.9574 | 76.2314 | 0.24495 | -0.054459 | -0.10612 | 0.11548 | -0.041553 | -0.070479 | 0.10122 | -44.458 | 76.2131 | -47.1085 | -47.1909 | -7.5302 | -8.6929 | -40.1642 | -39.1205 | 76.2039 | -47.1497 | -0.15106 | -0.01831 | 2.4994 | -0.23346 | -83.7616 | -0.19226 | -0.027466 | 2.6505 | 6.7932 | 7.8369 | 39.4272 | 123.1705 | 2.4994 | 123.1613 | 38.2645 | -0.19226 | 123.1705 | 2.4994 | 38.2645 | 39.4272 | 123.1613 | -123.3398 | -123.381
645.6719 | 123.436 | -46.5729 | 76.6205 | 0.18391 | -0.055527 | -0.087958 | 0.12082 | -0.051166 | -0.067275 | 0.10015 | -44.0414 | 76.4694 | -46.8338 | -46.9482 | -7.2739 | -8.2993 | -39.6973 | -38.6032 | 76.5747 | -46.756 | -0.26093 | -0.15106 | 2.5314 | -0.37537 | -83.8943 | -0.1831 | -0.045776 | 2.7924 | 6.8756 | 7.9697 | 39.299 | 123.0423 | 2.5314 | 123.1476 | 38.2736 | -0.1831 | 123.0423 | 2.5314 | 38.2736 | 39.299 | 123.1476 | -123.4543 | -123.3765
646.6562 | 123.436 | -46.5775 | 76.5976 | 0.45857 | -0.046983 | -0.090095 | 0.12616 | -0.041553 | -0.049117 | 0.098016 | -43.9087 | 76.6251 | -46.756 | -46.7743 | -7.9376 | -8.8852 | -39.7156 | -38.5757 | 76.5564 | -46.7377 | -0.17853 | 0.027466 | 2.6688 | -0.19684 | -84.5352 | -0.16022 | -0.041199 | 2.8473 | 6.8619 | 8.0017 | 38.6398 | 123.2025 | 2.6688 | 123.1339 | 37.6923 | -0.16022 | 123.2025 | 2.6688 | 37.6923 | 38.6398 | 123.1339 | -123.3536 | -123.3353
647.6719 | 123.4131 | -45.0256 | 78.1357 | 0.45857 | -0.060868 | -0.090095 | 0.11975 | -0.044757 | -0.060866 | 0.10763 | -41.6885 | 78.1174 | -45.1401 | -45.2545 | -10.5789 | -11.6089 | -38.2507 | -37.2849 | 78.1631 | -45.1859 | -0.11444 | -0.01831 | 3.3371 | -0.22888 | -88.7146 | -0.16022 | 0.027466 | 3.4515 | 6.7749 | 7.7408 | 34.4467 | 123.143 | 3.3371 | 123.1888 | 33.4167 | -0.16022 | 123.143 | 3.3371 | 33.4167 | 34.4467 | 123.1888 | -123.2758 | -123.3215
648.6562 | 123.5046 | -44.6732 | 78.5065 | 0.58064 | -0.053391 | -0.11146 | 0.11762 | -0.035144 | -0.035232 | 0.10549 | -41.2262 | 78.4744 | -44.8471 | -44.9982 | -12.5244 | -13.4216 | -38.1958 | -37.5458 | 78.4378 | -44.9112 | -0.17395 | -0.032044 | 3.447 | -0.32501 | -91.0309 | -0.23804 | -0.068665 | 3.6209 | 6.4774 | 7.1274 | 32.1487 | 123.1476 | 3.447 | 123.111 | 31.2515 | -0.23804 | 123.1476 | 3.447 | 31.2515 | 32.1487 | 123.111 | -123.3536 | -123.4177
649.6719 | 123.5001 | -44.5724 | 78.5706 | -0.075488 | -0.057664 | -0.10291 | 0.11975 | -0.04903 | -0.059798 | 0.11404 | -40.9286 | 78.5706 | -44.7327 | -44.9203 | -12.1307 | -13.0508 | -39.0747 | -38.2462 | 78.5797 | -44.7739 | -0.16022 | 0 | 3.6438 | -0.3479 | -90.7013 | -0.20142 | 0.009155 | 3.804 | 5.4977 | 6.3263 | 32.4417 | 123.143 | 3.6438 | 123.1522 | 31.5216 | -0.20142 | 123.143 | 3.6438 | 31.5216 | 32.4417 | 123.1522 | -123.3032 | -123.3444
650.6562 | 123.4543 | -44.5358 | 78.653 | 0.5196 | -0.041642 | -0.084754 | 0.11868 | -0.03194 | -0.046981 | 0.11404 | -41.9815 | 78.6987 | -44.6915 | -44.7647 | -12.0987 | -13.0783 | -37.0102 | -36.1313 | 78.5934 | -44.7235 | -0.15564 | 0.045776 | 2.5543 | -0.22888 | -90.7516 | -0.18768 | -0.059509 | 2.71 | 7.5256 | 8.4045 | 32.4371 | 123.2346 | 2.5543 | 123.1293 | 31.4575 | -0.18768 | 123.2346 | 2.5543 | 31.4575 | 32.4371 | 123.1293 | -123.3444 | -123.3765
651.6562 | 123.4268 | -44.783 | 78.3966 | 0.3365 | -0.056596 | -0.080482 | 0.11441 | -0.033008 | -0.059798 | 0.12045 | -42.2379 | 78.36 | -44.9661 | -44.8517 | -12.085 | -13.1332 | -29.4571 | -29.1687 | 78.447 | -44.9066 | -0.1831 | -0.036621 | 2.5452 | -0.068665 | -90.4816 | -0.1236 | 0.050354 | 2.7283 | 15.3259 | 15.6143 | 32.6981 | 123.143 | 2.5452 | 123.23 | 31.6498 | -0.1236 | 123.143 | 2.5452 | 31.6498 | 32.6981 | 123.23 | -123.3627 | -123.3032
652.6562 | 123.4772 | -44.1467 | 79.01 | 0.48909 | -0.052323 | -0.077277 | 0.1283 | -0.037281 | -0.040572 | 0.10549 | -41.3773 | 79.0558 | -44.2886 | -44.4214 | -12.355 | -13.5223 | -28.9993 | -28.6606 | 78.9917 | -44.3619 | -0.14191 | 0.045776 | 2.7695 | -0.27466 | -91.3651 | -0.21515 | -0.018311 | 2.9114 | 15.1474 | 15.4861 | 31.7917 | 123.2025 | 2.7695 | 123.1384 | 30.6244 | -0.21515 | 123.2025 | 2.7695 | 30.6244 | 31.7917 | 123.1384 | -123.2986 | -123.3719
653.6719 | 123.4589 | -42.3431 | 80.7678 | 0.55012 | -0.053391 | -0.059119 | 0.11334 | -0.04903 | -0.035232 | 0.11404 | -39.1983 | 80.777 | -42.5308 | -42.659 | -12.8952 | -14.0854 | -28.6743 | -28.5965 | 80.8228 | -42.5537 | -0.18768 | 0.009156 | 3.1448 | -0.31586 | -93.663 | -0.21057 | 0.054932 | 3.3325 | 13.6688 | 13.7466 | 29.4479 | 123.1201 | 3.1448 | 123.1659 | 28.2578 | -0.21057 | 123.1201 | 3.1448 | 28.2578 | 29.4479 | 123.1659 | -123.2986 | -123.3215
654.6719 | 123.381 | -42.4667 | 80.7312 | 0.35176 | -0.061936 | -0.097572 | 0.12082 | -0.028736 | -0.054458 | 0.10549 | -39.6515 | 80.6717 | -42.6224 | -42.7322 | -13.0417 | -14.2914 | -29.7363 | -29.3884 | 80.6534 | -42.6544 | -0.15564 | -0.059509 | 2.8152 | -0.2655 | -93.7729 | -0.18768 | -0.07782 | 2.9709 | 12.7304 | 13.0783 | 29.425 | 123.1384 | 2.8152 | 123.1201 | 28.1754 | -0.18768 | 123.1384 | 2.8152 | 28.1754 | 29.425 | 123.1201 | -123.3536 | -123.3856
655.6719 | 123.436 | -42.215 | 80.928 | 0.5196 | -0.034165 | -0.082618 | 0.12616 | -0.039417 | -0.045913 | 0.10763 | -39.4547 | 80.896 | -42.4072 | -42.5262 | -13.4399 | -14.1586 | -29.9469 | -29.7134 | 80.9509 | -42.4347 | -0.19226 | -0.032044 | 2.7603 | -0.31128 | -94.368 | -0.21973 | 0.022888 | 2.9526 | 12.2681 | 12.5015 | 28.775 | 123.111 | 2.7603 | 123.1659 | 28.0563 | -0.21973 | 123.111 | 2.7603 | 28.0563 | 28.775 | 123.1659 | -123.3353 | -123.3627
656.6562 | 123.4451 | -42.1783 | 80.9875 | 0.45857 | -0.043778 | -0.08155 | 0.12082 | -0.039417 | -0.044845 | 0.11938 | -39.2075 | 80.983 | -42.3294 | -42.4713 | -13.0966 | -13.6047 | -29.6539 | -29.4525 | 80.9692 | -42.3798 | -0.15106 | -0.004578 | 2.9709 | -0.29297 | -94.0842 | -0.20142 | -0.018311 | 3.1219 | 12.5244 | 12.7258 | 29.0817 | 123.1613 | 2.9709 | 123.1476 | 28.5736 | -0.20142 | 123.1613 | 2.9709 | 28.5736 | 29.0817 | 123.1476 | -123.317 | -123.3673
657.6719 | 123.4314 | -41.8808 | 81.2943 | 0.092359 | -0.053391 | -0.073005 | 0.11334 | -0.028736 | -0.064071 | 0.12258 | -39.0793 | 81.2988 | -42.0319 | -42.1326 | -13.4445 | -13.9252 | -30.1712 | -29.837 | 81.2576 | -42.0639 | -0.15106 | 0.004578 | 2.8015 | -0.25177 | -94.7388 | -0.18311 | -0.036621 | 2.9526 | 11.7096 | 12.0438 | 28.4363 | 123.1796 | 2.8015 | 123.1384 | 27.9556 | -0.18311 | 123.1796 | 2.8015 | 27.9556 | 28.4363 | 123.1384 | -123.3261 | -123.3582
658.7188 | 123.4451 | -42.2607 | 80.8731 | 0.5196 | -0.037369 | -0.095435 | 0.12937 | -0.036213 | -0.034163 | 0.11724 | -39.3494 | 80.8868 | -42.453 | -42.5858 | -10.5698 | -11.0184 | -28.9444 | -28.7109 | 80.8594 | -42.4942 | -0.19226 | 0.013733 | 2.9114 | -0.32501 | -91.4429 | -0.23346 | -0.013733 | 3.1036 | 13.3163 | 13.5498 | 31.691 | 123.1476 | 2.9114 | 123.1201 | 31.2424 | -0.23346 | 123.1476 | 2.9114 | 31.2424 | 31.691 | 123.1201 | -123.3261 | -123.3673
659.6719 | 123.4131 | -41.9952 | 81.1569 | 0.24495 | -0.050187 | -0.089027 | 0.12509 | -0.050098 | -0.046981 | 0.11938 | -39.1983 | 81.1249 | -42.1646 | -42.2836 | -10.9314 | -11.3159 | -28.8437 | -28.3951 | 81.1249 | -42.1646 | -0.16937 | -0.032043 | 2.7969 | -0.28839 | -92.0883 | -0.16937 | -0.032043 | 2.9663 | 13.1515 | 13.6002 | 31.0638 | 123.1201 | 2.7969 | 123.1201 | 30.6793 | -0.16937 | 123.1201 | 2.7969 | 30.6793 | 31.0638 | 123.1201 | -123.3215 | -123.3215
660.6562 | 123.3261 | -41.7892 | 81.4545 | 0.45857 | -0.038438 | -0.087958 | 0.14432 | -0.035144 | -0.040572 | 0.11724 | -39.1296 | 81.5186 | -41.9037 | -41.8579 | -11.3617 | -11.792 | -29.3472 | -28.7842 | 81.3538 | -41.9037 | -0.11444 | 0.064087 | 2.6596 | -0.068664 | -92.8162 | -0.11444 | -0.10071 | 2.774 | 12.442 | 13.0051 | 30.4276 | 123.3078 | 2.6596 | 123.143 | 29.9973 | -0.11444 | 123.3078 | 2.6596 | 29.9973 | 30.4276 | 123.143 | -123.3582 | -123.3582
661.6719 | 123.4406 | -41.4276 | 81.7566 | 0.41279 | -0.051255 | -0.074073 | 0.12723 | -0.044757 | -0.052321 | 0.11617 | -38.9328 | 81.72 | -41.6153 | -41.7389 | -11.3251 | -11.8057 | -28.7201 | -28.4271 | 81.7291 | -41.6061 | -0.18768 | -0.036621 | 2.4948 | -0.31128 | -93.0817 | -0.17853 | -0.027466 | 2.6825 | 12.7075 | 13.0005 | 30.1025 | 123.1476 | 2.4948 | 123.1567 | 29.6219 | -0.17853 | 123.1476 | 2.4948 | 29.6219 | 30.1025 | 123.1567 | -123.3719 | -123.3627
662.6562 | 123.3536 | -40.7089 | 82.4982 | 3.3883 | -0.041642 | -0.08689 | 0.14005 | -0.03194 | -0.044845 | 0.12686 | -38.2782 | 82.5943 | -40.86 | -40.8142 | -12.5336 | -12.9639 | -29.3655 | -28.8528 | 82.3929 | -40.8554 | -0.15106 | 0.09613 | 2.4307 | -0.10529 | -95.0317 | -0.14648 | -0.10529 | 2.5818 | 11.3434 | 11.8561 | 28.1754 | 123.3032 | 2.4307 | 123.1018 | 27.7451 | -0.14648 | 123.3032 | 2.4307 | 27.7451 | 28.1754 | 123.1018 | -123.3582 | -123.3536
663.7031 | 123.3902 | -39.7614 | 83.4412 | 0.016065 | -0.044846 | -0.060187 | 0.14218 | -0.029804 | -0.042708 | 0.11724 | -36.0214 | 83.5007 | -39.9033 | -39.9078 | -12.767 | -13.1973 | -28.6148 | -28.093 | 83.3817 | -39.9124 | -0.14191 | 0.059509 | 3.7399 | -0.14648 | -96.2082 | -0.15106 | -0.059509 | 3.8818 | 11.1465 | 11.6684 | 26.9943 | 123.262 | 3.7399 | 123.143 | 26.564 | -0.15106 | 123.262 | 3.7399 | 26.564 | 26.9943 | 123.143 | -123.3444 | -123.3536
664.6719 | 123.4039 | -39.5554 | 83.5876 | 0.45857 | -0.049119 | -0.10505 | 0.12403 | -0.035144 | -0.054458 | 0.12899 | -35.8749 | 83.606 | -39.7202 | -39.8254 | -13.0829 | -13.4995 | -28.4225 | -28.0884 | 83.5922 | -39.7339 | -0.16479 | 0.018311 | 3.6804 | -0.27008 | -96.6705 | -0.17853 | 0.004578 | 3.8452 | 11.1328 | 11.467 | 26.4725 | 123.1613 | 3.6804 | 123.1476 | 26.0559 | -0.17853 | 123.1613 | 3.6804 | 26.0559 | 26.4725 | 123.1476 | -123.3078 | -123.3215
665.6719 | 123.4589 | -39.473 | 83.7067 | 0.30598 | -0.051255 | -0.10505 | 0.15073 | -0.035144 | -0.055526 | 0.14715 | -35.9894 | 83.7067 | -39.6469 | -39.6973 | -13.6322 | -13.9938 | -28.45 | -28.125 | 83.6746 | -39.6423 | -0.17395 | 0 | 3.4836 | -0.22431 | -97.3389 | -0.16937 | -0.032043 | 3.6575 | 11.0229 | 11.348 | 25.8408 | 123.1796 | 3.4836 | 123.1476 | 25.4791 | -0.16937 | 123.1796 | 3.4836 | 25.4791 | 25.8408 | 123.1476 | -123.3536 | -123.349
666.6562 | 122.9507 | -55.6961 | 67.1265 | 0.5196 | -0.035233 | -0.069801 | 0.37717 | -0.091755 | -0.076888 | 0.27319 | -51.3931 | 67.1814 | -55.8746 | 20.0729 | 57.0328 | 56.3828 | -51.2329 | -55.4672 | 67.0349 | -55.806 | -0.17853 | 0.054931 | 4.303 | 75.769 | -10.0937 | -0.10986 | -0.091553 | 4.4815 | 4.4632 | 0.22888 | 112.7289 | 122.8775 | 4.303 | 122.731 | 112.0789 | -0.10986 | 122.8775 | 4.303 | 112.0789 | 112.7289 | 122.731 | -123.0011 | -122.9324
667.7188 | 123.1384 | -61.9263 | 60.965 | 0.36702 | -0.051255 | -0.087958 | 0.33765 | -0.11632 | -0.096114 | 0.26251 | -57.4951 | 60.9375 | -62.1323 | 59.1614 | 56.9275 | 56.8954 | -41.6748 | -62.0178 | 60.9329 | -62.114 | -0.20599 | -0.027466 | 4.4312 | 121.0876 | -4.0375 | -0.18768 | -0.032044 | 4.6371 | 20.2515 | -0.091552 | 118.8538 | 122.8638 | 4.4312 | 122.8592 | 118.8217 | -0.18768 | 122.8638 | 4.4312 | 118.8217 | 118.8538 | 122.8592 | -123.0972 | -123.0789
668.6562 | 123.1018 | -62.4481 | 60.5255 | 0.38228 | -0.032029 | -0.071937 | 0.34726 | -0.10457 | -0.079024 | 0.24221 | -57.962 | 60.5896 | -62.6266 | 58.9783 | 55.9616 | 55.957 | -29.7501 | -62.4069 | 60.4614 | -62.5626 | -0.17853 | 0.064087 | 4.4861 | 121.4264 | -4.5639 | -0.11444 | -0.064087 | 4.6646 | 32.6981 | 0.041199 | 118.4097 | 123.0377 | 4.4861 | 122.9095 | 118.4052 | -0.11444 | 123.0377 | 4.4861 | 118.4052 | 118.4097 | 122.9095 | -123.1522 | -123.0881
669.6719 | 123.2117 | -62.6953 | 60.2646 | 0.35176 | -0.04271 | -0.092231 | 0.32056 | -0.11312 | -0.11427 | 0.24328 | -58.2458 | 60.2509 | -62.8464 | 58.4656 | 54.9866 | 54.982 | -26.2299 | -62.8281 | 60.2509 | -62.8738 | -0.15106 | -0.013733 | 4.4495 | 121.1609 | -5.278 | -0.17853 | -0.013733 | 4.6005 | 36.4655 | -0.13275 | 117.6819 | 122.9462 | 4.4495 | 122.9462 | 117.6773 | -0.17853 | 122.9462 | 4.4495 | 117.6773 | 117.6819 | 122.9462 | -123.111 | -123.1384
670.7188 | 123.1522 | -64.6957 | 58.3099 | 0.53486 | -0.036301 | -0.10398 | 0.41669 | -0.11418 | -0.080092 | 0.31484 | -60.434 | 58.3923 | -64.801 | 56.6483 | 54.1489 | 54.1534 | 40.8691 | -64.6362 | 58.255 | -64.801 | -0.10528 | 0.082397 | 4.2618 | 121.344 | -4.1611 | -0.10528 | -0.054932 | 4.3671 | 105.5649 | 0.05951 | 118.8446 | 123.0881 | 4.2618 | 122.9507 | 118.8492 | -0.10528 | 123.0881 | 4.2618 | 118.8492 | 118.8446 | 122.9507 | -123.111 | -123.111
671.6562 | 123.0331 | -71.6858 | 51.0773 | 0.45857 | -0.053391 | -0.080482 | 0.28424 | -0.10778 | -0.093978 | 0.19842 | -67.1951 | 51.1047 | -71.8048 | 50.7797 | 49.5758 | 49.6811 | 50.0885 | 47.2687 | 51.123 | -71.8552 | -0.11902 | 0.027465 | 4.4907 | 122.4655 | -1.5015 | -0.16937 | 0.045776 | 4.6097 | 121.7743 | 118.9545 | 121.2616 | 122.7905 | 4.4907 | 122.8088 | 121.3669 | -0.16937 | 122.7905 | 4.4907 | 121.3669 | 121.2616 | 122.8088 | -122.8821 | -122.9324
672.7031 | 123.0011 | -72.1848 | 50.7431 | 0.0771 | -0.045914 | -0.078345 | 0.3056 | -0.097095 | -0.084365 | 0.20269 | -67.4515 | 50.7797 | -72.345 | 50.4272 | 49.1867 | 49.3423 | 49.7452 | 49.617 | 50.679 | -72.3221 | -0.16022 | 0.036621 | 4.7333 | 122.612 | -1.5564 | -0.13733 | -0.064087 | 4.8935 | 121.9299 | 121.8018 | 121.3715 | 122.9645 | 4.7333 | 122.8638 | 121.5271 | -0.13733 | 122.9645 | 4.7333 | 121.5271 | 121.3715 | 122.8638 | -123.0881 | -123.0652
673.6719 | 122.5937 | -69.4473 | 52.9037 | 0.27546 | -0.049119 | -0.091163 | 0.26608 | -0.10457 | -0.10466 | 0.19308 | -64.7369 | 52.8259 | -69.6213 | 46.9025 | 47.9553 | 47.6624 | 46.5958 | 46.6507 | 52.8763 | -69.6213 | -0.17395 | -0.07782 | 4.7104 | 116.3498 | -4.9484 | -0.17395 | -0.027466 | 4.8843 | 116.0431 | 116.098 | 117.4026 | 122.2733 | 4.7104 | 122.3236 | 117.1097 | -0.17395 | 122.2733 | 4.7104 | 117.1097 | 117.4026 | 122.3236 | -122.525 | -122.525
674.7188 | 122.818 | -70.0287 | 52.6611 | 0.53486 | -0.028825 | -0.070869 | 0.30347 | -0.11952 | -0.085433 | 0.18026 | -64.8651 | 52.7115 | -70.1843 | 49.379 | 49.6811 | 49.4888 | 48.9349 | 49.1409 | 52.5879 | -70.1477 | -0.15564 | 0.050354 | 5.1636 | 119.4077 | -2.98 | -0.11902 | -0.073242 | 5.3192 | 118.9636 | 119.1696 | 119.7098 | 122.7402 | 5.1636 | 122.6166 | 119.5175 | -0.11902 | 122.7402 | 5.1636 | 119.5175 | 119.7098 | 122.6166 | -122.8455 | -122.8088
675.6562 | 122.8775 | -69.7403 | 52.9633 | 1.5877 | -0.029893 | -0.073005 | 0.29065 | -0.10244 | -0.088637 | 0.18667 | -64.5309 | 52.977 | -69.9509 | 49.5071 | 49.7314 | 49.5392 | 49.1776 | 49.2691 | 52.8992 | -69.9188 | -0.21057 | 0.013733 | 5.2094 | 119.2474 | -3.2318 | -0.17853 | -0.064087 | 5.4199 | 118.9178 | 119.0094 | 119.4717 | 122.7173 | 5.2094 | 122.6395 | 119.2795 | -0.17853 | 122.7173 | 5.2094 | 119.2795 | 119.4717 | 122.6395 | -122.9141 | -122.8821
676.6562 | 122.8271 | -67.1173 | 55.4169 | 0.5959 | -0.029893 | -0.071937 | 0.26715 | -0.10884 | -0.089705 | 0.1557 | -62.0178 | 55.3116 | -67.4149 | 43.721 | 43.5837 | 43.515 | 43.3731 | 43.3044 | 55.4581 | -67.3141 | -0.29755 | -0.10529 | 5.0995 | 110.8383 | -11.8332 | -0.19684 | 0.041199 | 5.397 | 110.4904 | 110.4218 | 110.701 | 122.4289 | 5.0995 | 122.5754 | 110.6323 | -0.19684 | 122.4289 | 5.0995 | 110.6323 | 110.701 | 122.5754 | -122.8317 | -122.731
677.6719 | 122.9324 | -69.2871 | 53.4073 | 0.39753 | -0.032029 | -0.079414 | 0.26288 | -0.11098 | -0.10359 | 0.17813 | -63.9771 | 53.3615 | -69.4702 | 48.1888 | 48.3032 | 48.3032 | 47.9095 | 47.9279 | 53.3981 | -69.5023 | -0.18311 | -0.045777 | 5.3101 | 117.4759 | -5.1041 | -0.21515 | -0.009156 | 5.4932 | 117.1967 | 117.215 | 117.5903 | 122.6486 | 5.3101 | 122.6852 | 117.5903 | -0.21515 | 122.6486 | 5.3101 | 117.5903 | 117.5903 | 122.6852 | -122.8775 | -122.9095
678.7188 | 122.9736 | -69.2001 | 53.5126 | 0.38228 | -0.049119 | -0.08689 | 0.25861 | -0.12273 | -0.1068 | 0.17172 | -63.8397 | 53.4668 | -69.3558 | 47.9965 | 48.912 | 48.8388 | 47.3373 | 47.3145 | 53.508 | -69.4107 | -0.15564 | -0.045776 | 5.3604 | 117.1967 | -4.6005 | -0.21057 | -0.004577 | 5.5161 | 116.5375 | 116.5146 | 118.1122 | 122.6669 | 5.3604 | 122.7081 | 118.0389 | -0.21057 | 122.6669 | 5.3604 | 118.0389 | 118.1122 | 122.7081 | -122.8683 | -122.9233
679.6719 | 122.6898 | -69.928 | 52.4872 | 0.41279 | -0.053391 | -0.08689 | 0.29813 | -0.11846 | -0.093978 | 0.20376 | -64.357 | 52.4551 | -70.079 | 51.8555 | 52.0111 | 51.9836 | 51.8509 | 51.6357 | 52.4963 | -70.1294 | -0.15106 | -0.032044 | 5.571 | 121.7834 | -0.47608 | -0.20142 | 0.009155 | 5.722 | 121.7789 | 121.5637 | 121.9391 | 122.3831 | 5.571 | 122.4243 | 121.9116 | -0.20142 | 122.3831 | 5.571 | 121.9116 | 121.9391 | 122.4243 | -122.5662 | -122.6166
680.6562 | 122.7127 | -69.342 | 53.2288 | 0.99263 | -0.040574 | -0.055915 | 0.30774 | -0.10991 | -0.082229 | 0.19201 | -63.6383 | 53.2974 | -69.429 | 52.6062 | 52.6978 | 52.6703 | 52.4597 | 52.327 | 53.215 | -69.4885 | -0.086975 | 0.068664 | 5.7037 | 121.9482 | -0.53101 | -0.14648 | -0.013733 | 5.7907 | 121.8018 | 121.669 | 122.0398 | 122.6395 | 5.7037 | 122.5571 | 122.0123 | -0.14648 | 122.6395 | 5.7037 | 122.0123 | 122.0398 | 122.5571 | -122.6578 | -122.7173
681.6719 | 122.8729 | -69.3695 | 53.215 | 0.61116 | -0.035233 | -0.087958 | 0.30347 | -0.12273 | -0.096114 | 0.20376 | -63.739 | 53.1052 | -69.6075 | 52.3544 | 52.478 | 52.4734 | 52.359 | 52.1255 | 53.2288 | -69.5526 | -0.23804 | -0.10986 | 5.6305 | 121.7239 | -0.737 | -0.1831 | 0.013733 | 5.8685 | 121.7285 | 121.4951 | 121.8475 | 122.4747 | 5.6305 | 122.5983 | 121.843 | -0.1831 | 122.4747 | 5.6305 | 121.843 | 121.8475 | 122.5983 | -122.8226 | -122.7676
682.7031 | 122.7951 | -69.2871 | 53.3432 | 0.00080561 | -0.032029 | -0.078345 | 0.33658 | -0.11846 | -0.09291 | 0.21551 | -63.7939 | 53.3981 | -69.4473 | 51.9608 | 52.6794 | 52.5879 | 51.8188 | 51.2741 | 53.3249 | -69.4336 | -0.16022 | 0.054931 | 5.4932 | 121.2479 | -0.66376 | -0.14648 | -0.018311 | 5.6534 | 121.106 | 120.5612 | 121.9666 | 122.6852 | 5.4932 | 122.612 | 121.875 | -0.14648 | 122.6852 | 5.4932 | 121.875 | 121.9666 | 122.612 | -122.7905 | -122.7768
683.6719 | 122.8867 | -69.8135 | 52.771 | 0.58064 | -0.033097 | -0.076209 | 0.32697 | -0.12059 | -0.096114 | 0.21765 | -64.1922 | 52.8809 | -69.9005 | 50.8759 | 52.1988 | 52.0981 | 51.2924 | 50.1434 | 52.771 | -70.0195 | -0.086975 | 0.10986 | 5.6213 | 120.6894 | -0.5722 | -0.20599 | 0 | 5.7083 | 121.106 | 119.957 | 122.0123 | 122.6944 | 5.6213 | 122.5845 | 121.9116 | -0.20599 | 122.6944 | 5.6213 | 121.9116 | 122.0123 | 122.5845 | -122.6715 | -122.7905
684.6719 | 122.9279 | -69.8776 | 52.7298 | 0.50435 | -0.043778 | -0.063392 | 0.31842 | -0.1238 | -0.090773 | 0.2091 | -64.3341 | 52.7893 | -69.9738 | 49.942 | 51.9608 | 51.6586 | 48.88 | 48.8388 | 52.7435 | -70.0928 | -0.09613 | 0.05951 | 5.5435 | 119.8196 | -0.76904 | -0.21515 | 0.013733 | 5.6396 | 118.7576 | 118.7164 | 121.8384 | 122.6669 | 5.5435 | 122.6212 | 121.5363 | -0.21515 | 122.6669 | 5.5435 | 121.5363 | 121.8384 | 122.6212 | -122.7036 | -122.8226
685.6719 | 122.9187 | -68.9713 | 53.6133 | 0.55012 | -0.04271 | -0.056983 | 0.31949 | -0.11205 | -0.096114 | 0.23046 | -63.7756 | 53.4531 | -69.3146 | 46.3394 | 53.0548 | 52.771 | 45.6482 | 45.9183 | 53.6499 | -69.223 | -0.34332 | -0.16022 | 5.1956 | 115.3107 | -0.55847 | -0.25177 | 0.036621 | 5.5389 | 114.6194 | 114.8895 | 122.0261 | 122.4243 | 5.1956 | 122.6212 | 121.7422 | -0.25177 | 122.4243 | 5.1956 | 121.7422 | 122.0261 | 122.6212 | -122.9279 | -122.8363
686.7031 | 122.8867 | -52.9358 | 69.8044 | -0.27385 | -0.027756 | -0.092231 | 0.77664 | -0.074665 | -0.10039 | 0.73995 | -48.3353 | 69.7678 | -53.096 | -4.8386 | 66.8472 | 5.5344 | 66.8198 | -7.0587 | 69.6808 | -53.0457 | -0.16022 | -0.036621 | 4.6005 | 48.0972 | -2.9572 | -0.10986 | -0.1236 | 4.7607 | 119.7556 | 45.8771 | 119.783 | 122.7036 | 4.6005 | 122.6166 | 58.4702 | -0.10986 | 122.7036 | 4.6005 | 58.4702 | 119.783 | 122.6166 | -122.9004 | -122.85
687.6719 | 123.0011 | -68.4586 | 54.1809 | 0.58064 | -0.032029 | -0.071937 | 0.35474 | -0.11952 | -0.089705 | 0.24862 | -63.176 | 54.2999 | -68.5684 | 45.7306 | 53.6179 | 47.4335 | 51.6266 | 45.0577 | 54.1901 | -68.6554 | -0.10986 | 0.11902 | 5.2826 | 114.1891 | -0.56305 | -0.19684 | 0.009155 | 5.3925 | 120.0851 | 113.5162 | 122.0764 | 122.7585 | 5.2826 | 122.6486 | 115.892 | -0.19684 | 122.7585 | 5.2826 | 115.892 | 122.0764 | 122.6486 | -122.7493 | -122.8363
688.6719 | 122.4838 | -69.9966 | 52.2858 | -0.04497 | -0.021348 | -0.070869 | 0.30454 | -0.10778 | -0.083297 | 0.16851 | -64.5126 | 52.2812 | -70.1981 | 52.5055 | 52.2446 | 52.2629 | 51.8372 | 50.8667 | 52.2263 | -70.1843 | -0.20142 | -0.004578 | 5.484 | 122.5021 | -0.041199 | -0.18768 | -0.05951 | 5.6854 | 121.8338 | 120.8633 | 122.2412 | 122.2778 | 5.484 | 122.2229 | 122.2595 | -0.18768 | 122.2778 | 5.484 | 122.2595 | 122.2412 | 122.2229 | -122.4838 | -122.4701
689.7188 | 122.6944 | -69.7495 | 52.6199 | 0.61116 | -0.040574 | -0.055915 | 0.3024 | -0.11205 | -0.083297 | 0.17172 | -63.8031 | 52.6154 | -69.9417 | 52.7756 | 52.6016 | 52.5742 | 52.3819 | 52.2903 | 52.6337 | -69.9738 | -0.19226 | -0.004578 | 5.9463 | 122.525 | -0.01831 | -0.2243 | 0.013733 | 6.1386 | 122.1313 | 122.0398 | 122.3511 | 122.3648 | 5.9463 | 122.3831 | 122.3236 | -0.2243 | 122.3648 | 5.9463 | 122.3236 | 122.3511 | 122.3831 | -122.5616 | -122.5937
690.6562 | 122.612 | -70.4315 | 52.0706 | 0.45857 | -0.02028 | -0.058051 | 0.3259 | -0.11098 | -0.086501 | 0.18026 | -64.801 | 52.1027 | -70.5872 | 52.3361 | 52.2171 | 52.1027 | 51.5991 | 51.7776 | 52.0203 | -70.6009 | -0.15564 | 0.032043 | 5.6305 | 122.7676 | 0.14648 | -0.16937 | -0.050354 | 5.7861 | 122.0306 | 122.2092 | 122.6486 | 122.5342 | 5.6305 | 122.4518 | 122.5342 | -0.16937 | 122.5342 | 5.6305 | 122.5342 | 122.6486 | 122.4518 | -122.6578 | -122.6715
691.7031 | 122.7036 | -70.6787 | 51.8509 | -0.090746 | -0.023484 | -0.060187 | 0.31949 | -0.11418 | -0.083297 | 0.18347 | -64.7049 | 51.86 | -70.8298 | 52.0523 | 51.8417 | 51.8509 | 51.3748 | 51.4435 | 51.8051 | -70.8344 | -0.15106 | 0.009155 | 5.9738 | 122.731 | -0.009155 | -0.15564 | -0.045776 | 6.1249 | 122.0535 | 122.1222 | 122.5204 | 122.5388 | 5.9738 | 122.4838 | 122.5296 | -0.15564 | 122.5388 | 5.9738 | 122.5296 | 122.5204 | 122.4838 | -122.6807 | -122.6852
692.6562 | 122.406 | -69.9966 | 52.0752 | 0.56538 | -0.029893 | -0.083686 | 0.28317 | -0.11418 | -0.084365 | 0.16744 | -64.032 | 52.1072 | -70.1248 | 52.2079 | 51.7593 | 52.002 | 52.2263 | 52.1027 | 52.1255 | -70.2164 | -0.12817 | 0.032044 | 5.9647 | 122.2046 | -0.31586 | -0.21973 | 0.050354 | 6.0928 | 122.2229 | 122.0993 | 121.756 | 122.1039 | 5.9647 | 122.1222 | 121.9986 | -0.21973 | 122.1039 | 5.9647 | 121.9986 | 121.756 | 122.1222 | -122.2 | -122.2916
693.7188 | 122.6257 | -70.4636 | 51.8188 | 0.47383 | -0.037369 | -0.071937 | 0.28104 | -0.11739 | -0.097182 | 0.17919 | -64.2746 | 51.7822 | -70.6467 | 51.9379 | 51.6769 | 51.8875 | 51.9424 | 51.8188 | 51.8417 | -70.7016 | -0.1831 | -0.036621 | 6.189 | 122.4014 | -0.14191 | -0.23804 | 0.022888 | 6.3721 | 122.406 | 122.2824 | 122.1405 | 122.2458 | 6.189 | 122.3053 | 122.3511 | -0.23804 | 122.2458 | 6.189 | 122.3511 | 122.1405 | 122.3053 | -122.4655 | -122.5204
694.6719 | 122.6532 | -70.3812 | 51.9516 | 0.61116 | -0.033097 | -0.059119 | 0.30454 | -0.12487 | -0.093978 | 0.19201 | -64.2288 | 51.9745 | -70.546 | 52.1347 | 51.7548 | 52.0523 | 52.0889 | 52.0065 | 51.9608 | -70.5872 | -0.16479 | 0.022888 | 6.1523 | 122.5159 | -0.19684 | -0.20599 | 0.009155 | 6.3171 | 122.4701 | 122.3877 | 122.1359 | 122.3557 | 6.1523 | 122.3419 | 122.4335 | -0.20599 | 122.3557 | 6.1523 | 122.4335 | 122.1359 | 122.3419 | -122.4976 | -122.5388
695.6719 | 122.6028 | -70.6833 | 51.7456 | 0.47383 | -0.028825 | -0.062324 | 0.31415 | -0.11739 | -0.091842 | 0.18774 | -64.5813 | 51.7502 | -70.8939 | 51.9562 | 51.7227 | 51.915 | 51.7273 | 51.7227 | 51.6815 | -70.8618 | -0.21057 | 0.004578 | 6.102 | 122.6395 | -0.022888 | -0.17853 | -0.064086 | 6.3126 | 122.4106 | 122.406 | 122.406 | 122.4335 | 6.102 | 122.3648 | 122.5983 | -0.17853 | 122.4335 | 6.102 | 122.5983 | 122.406 | 122.3648 | -122.6395 | -122.6074
696.7031 | 122.5983 | -70.6055 | 51.8509 | -0.15178 | -0.044846 | -0.090095 | 0.31735 | -0.10991 | -0.089705 | 0.19522 | -64.4531 | 51.8875 | -70.7748 | 52.1164 | 51.8875 | 52.0294 | 51.7731 | 51.9745 | 51.8097 | -70.7565 | -0.16937 | 0.036621 | 6.1523 | 122.7219 | 0.036621 | -0.15106 | -0.041199 | 6.3217 | 122.3785 | 122.58 | 122.493 | 122.493 | 6.1523 | 122.4152 | 122.6349 | -0.15106 | 122.493 | 6.1523 | 122.6349 | 122.493 | 122.4152 | -122.6257 | -122.6074
697.6719 | 122.6944 | -70.665 | 51.7731 | 0.64167 | -0.043778 | -0.076209 | 0.33231 | -0.10778 | -0.09825 | 0.19415 | -64.6408 | 51.7731 | -70.7886 | 51.9104 | 51.828 | 51.8875 | 51.8326 | 51.8097 | 51.7685 | -70.8435 | -0.1236 | 0 | 6.0242 | 122.5754 | 0.054932 | -0.17853 | -0.004577 | 6.1478 | 122.4976 | 122.4747 | 122.493 | 122.438 | 6.0242 | 122.4335 | 122.5525 | -0.17853 | 122.438 | 6.0242 | 122.5525 | 122.493 | 122.4335 | -122.5616 | -122.6166
698.6562 | 122.5891 | -70.5414 | 51.9562 | 0.36702 | -0.02028 | -0.059119 | 0.34299 | -0.10671 | -0.085433 | 0.20483 | -64.3845 | 52.002 | -70.6741 | 52.3819 | 52.0844 | 52.2446 | 52.0157 | 52.1896 | 51.9882 | -70.5597 | -0.13275 | 0.045776 | 6.1569 | 122.9233 | 0.12817 | -0.01831 | 0.032043 | 6.2897 | 122.5571 | 122.731 | 122.6257 | 122.5433 | 6.1569 | 122.5296 | 122.7859 | -0.01831 | 122.5433 | 6.1569 | 122.7859 | 122.6257 | 122.5296 | -122.6303 | -122.5159
699.6719 | 117.0456 | -56.0715 | 60.6995 | 0.44331 | -0.043778 | -0.078345 | 34.7545 | -0.063984 | -0.1132 | 35.1493 | -50.9995 | 60.6537 | -56.3187 | 29.2099 | 20.9976 | 29.4022 | 29.1733 | -0.90637 | 42.7185 | -38.2233 | -0.24719 | -0.045776 | 5.072 | 85.2814 | -39.7018 | 17.8482 | -17.981 | 5.3192 | 85.2448 | 55.1651 | 77.0691 | 116.7252 | 5.072 | 98.79 | 85.4736 | 17.8482 | 116.7252 | 5.072 | 85.4736 | 77.0691 | 98.79 | -117.0181 | -98.9227
700.6562 | 121.6827 | -34.2545 | 87.3825 | 0.41279 | -0.014939 | -0.077277 | 0.26395 | -0.11632 | -0.082229 | 0.17065 | -29.4525 | 87.4146 | -34.3643 | -20.8786 | -20.8511 | -20.9061 | -21.0342 | -20.7596 | -8.7891 | -34.3643 | -0.10986 | 0.032044 | 4.8019 | 13.3759 | -108.2336 | -0.10986 | -96.1716 | 4.9118 | 13.2202 | 13.4949 | 13.4033 | 121.669 | 4.8019 | 25.4654 | 13.3484 | -0.10986 | 121.669 | 4.8019 | 13.3484 | 13.4033 | 25.4654 | -121.7468 | -121.7468
701.7188 | 122.0261 | -35.0418 | 86.9522 | 0.3365 | -0.016007 | -0.054847 | 0.25968 | -0.10564 | -0.083297 | 0.16851 | -30.0476 | 86.9797 | -35.1837 | -19.6976 | -19.6747 | -19.725 | -19.9265 | -19.5786 | -8.7936 | -35.1608 | -0.14191 | 0.027466 | 4.9942 | 15.3442 | -106.6269 | -0.11902 | -95.7458 | 5.1361 | 15.1154 | 15.4633 | 15.3671 | 122.0215 | 4.9942 | 26.2482 | 15.3168 | -0.11902 | 122.0215 | 4.9942 | 15.3168 | 15.3671 | 26.2482 | -122.1359 | -122.113
702.6562 | 122.1359 | -34.996 | 87.0071 | 0.046583 | -0.018143 | -0.053779 | 0.25647 | -0.10671 | -0.079024 | 0.1824 | -30.1163 | 87.085 | -35.1746 | -19.4046 | -19.3405 | -19.3405 | -19.5831 | -19.2764 | -8.8028 | -35.1471 | -0.17853 | 0.07782 | 4.8798 | 15.5914 | -106.3477 | -0.15106 | -95.8099 | 5.0583 | 15.4129 | 15.7196 | 15.6555 | 122.081 | 4.8798 | 26.1932 | 15.6555 | -0.15106 | 122.081 | 4.8798 | 15.6555 | 15.6555 | 26.1932 | -122.1817 | -122.1542
703.6719 | 122.1954 | -33.4076 | 88.6597 | 0.42805 | -0.018143 | -0.056983 | 0.25113 | -0.11525 | -0.070479 | 0.17278 | -28.2761 | 88.7283 | -33.5953 | -21.5286 | -21.4828 | -21.5195 | -21.5652 | -21.5652 | -8.8028 | -33.5678 | -0.18768 | 0.068665 | 5.1315 | 11.879 | -110.1425 | -0.16022 | -97.4625 | 5.3192 | 11.8423 | 11.8423 | 11.9247 | 122.1359 | 5.1315 | 24.6048 | 11.8881 | -0.16022 | 122.1359 | 5.1315 | 11.8881 | 11.9247 | 24.6048 | -122.2549 | -122.2275
704.6719 | 122.2916 | -29.0451 | 93.0176 | 0.44331 | -0.023484 | -0.071937 | 0.24899 | -0.10564 | -0.068343 | 0.17919 | -24.2477 | 93.1046 | -29.1824 | -27.8595 | -27.7908 | -27.8915 | -27.8824 | -27.7817 | -8.8028 | -29.1962 | -0.13733 | 0.086975 | 4.7974 | 1.1856 | -120.8084 | -0.15106 | -101.8204 | 4.9347 | 1.1627 | 1.2634 | 1.2543 | 122.1497 | 4.7974 | 20.2423 | 1.1536 | -0.15106 | 122.1497 | 4.7974 | 1.1536 | 1.2543 | 20.2423 | -122.2 | -122.2137
705.6719 | 122.3282 | -28.0792 | 93.9789 | 0.55012 | -0.035233 | -0.077277 | 0.24793 | -0.11846 | -0.10039 | 0.17599 | -23.3002 | 94.0063 | -28.244 | -28.093 | -27.9739 | -28.0563 | -27.951 | -27.9648 | -8.8028 | -28.2761 | -0.1648 | 0.027466 | 4.7791 | -0.013733 | -121.9528 | -0.19684 | -102.7817 | 4.9438 | 0.12817 | 0.11444 | 0.10529 | 122.0856 | 4.7791 | 19.2764 | 0.022889 | -0.19684 | 122.0856 | 4.7791 | 0.022889 | 0.10529 | 19.2764 | -122.2229 | -122.2549
706.6562 | 122.2733 | -27.5253 | 94.6518 | 0.0771 | -0.016007 | -0.054847 | 0.26822 | -0.096027 | -0.067275 | 0.17278 | -22.4854 | 94.7159 | -27.6627 | -27.4429 | -27.388 | -27.4567 | -27.5848 | -27.3651 | -8.8028 | -27.6672 | -0.13733 | 0.064087 | 5.04 | 0.082398 | -122.0398 | -0.14191 | -103.4546 | 5.1773 | -0.059509 | 0.16022 | 0.13733 | 122.2412 | 5.04 | 18.7225 | 0.068665 | -0.14191 | 122.2412 | 5.04 | 0.068665 | 0.13733 | 18.7225 | -122.3145 | -122.319
707.7188 | 122.3877 | -26.8662 | 95.2011 | 0.74849 | -0.026688 | -0.087958 | 0.24045 | -0.11952 | -0.10039 | 0.17919 | -22.1466 | 95.2377 | -27.063 | -27.0447 | -26.9669 | -27.0401 | -26.9028 | -26.9348 | -8.7982 | -27.0721 | -0.19684 | 0.036621 | 4.7195 | -0.17853 | -122.168 | -0.20599 | -103.9993 | 4.9164 | -0.036621 | -0.068664 | -0.10071 | 122.1039 | 4.7195 | 18.0679 | -0.17395 | -0.20599 | 122.1039 | 4.7195 | -0.17395 | -0.10071 | 18.0679 | -122.2641 | -122.2733
708.6562 | 122.2824 | -26.4587 | 95.7504 | 0.27546 | -0.019212 | -0.067664 | 0.26502 | -0.11312 | -0.076888 | 0.17706 | -21.8628 | 95.8237 | -26.5961 | -26.3901 | -26.3626 | -26.4038 | -26.5869 | -26.3031 | -8.8028 | -26.5869 | -0.13733 | 0.073242 | 4.5959 | 0.068664 | -122.113 | -0.12817 | -104.5532 | 4.7333 | -0.12817 | 0.15564 | 0.09613 | 122.2824 | 4.5959 | 17.6559 | 0.054931 | -0.12817 | 122.2824 | 4.5959 | 0.054931 | 0.09613 | 17.6559 | -122.3465 | -122.3373
709.7188 | 122.2595 | -26.12 | 96.1212 | 0.27546 | -0.013871 | -0.065528 | 0.26822 | -0.11739 | -0.07582 | 0.18347 | -21.4462 | 96.1807 | -26.2619 | -26.0239 | -25.9872 | -26.0468 | -26.2482 | -25.9003 | -8.8028 | -26.2344 | -0.14191 | 0.059509 | 4.6738 | 0.09613 | -122.1085 | -0.11444 | -104.924 | 4.8157 | -0.12817 | 0.21973 | 0.13275 | 122.3007 | 4.6738 | 17.3172 | 0.073242 | -0.11444 | 122.3007 | 4.6738 | 0.073242 | 0.13275 | 17.3172 | -122.3831 | -122.3557
710.6562 | 122.3465 | -25.6302 | 96.5881 | 0.031324 | -0.021348 | -0.048438 | 0.26074 | -0.1003 | -0.083297 | 0.17813 | -20.9885 | 96.7072 | -25.708 | -25.5844 | -25.5386 | -25.589 | -25.6943 | -25.4608 | -8.8028 | -25.7538 | -0.07782 | 0.11902 | 4.6417 | 0.045776 | -122.1268 | -0.1236 | -105.3909 | 4.7195 | -0.064087 | 0.16937 | 0.091553 | 122.3373 | 4.6417 | 16.8274 | 0.041199 | -0.1236 | 122.3373 | 4.6417 | 0.041199 | 0.091553 | 16.8274 | -122.2961 | -122.3419
711.7188 | 122.3923 | -25.3189 | 96.8811 | 0.24495 | -0.04271 | -0.082618 | 0.2255 | -0.10991 | -0.11427 | 0.19308 | -20.8054 | 96.8719 | -25.4883 | -25.3738 | -25.264 | -25.3235 | -25.3326 | -25.1907 | -8.8074 | -25.4837 | -0.16937 | -0.009156 | 4.5136 | -0.054931 | -122.1451 | -0.16479 | -105.6885 | 4.6829 | -0.013733 | 0.12817 | 0.054932 | 122.1909 | 4.5136 | 16.5115 | -0.004577 | -0.16479 | 122.1909 | 4.5136 | -0.004577 | 0.054932 | 16.5115 | -122.3694 | -122.3648
712.6719 | 122.287 | -24.9481 | 97.3297 | 0.22969 | -0.021348 | -0.08155 | 0.25968 | -0.11098 | -0.072616 | 0.18987 | -20.4849 | 97.3709 | -25.0992 | -24.8337 | -24.8154 | -24.8611 | -25.0854 | -24.7238 | -8.8028 | -25.0763 | -0.15106 | 0.041199 | 4.4632 | 0.11444 | -122.1451 | -0.12817 | -106.1325 | 4.6143 | -0.13733 | 0.2243 | 0.13275 | 122.319 | 4.4632 | 16.1453 | 0.086975 | -0.12817 | 122.319 | 4.4632 | 0.086975 | 0.13275 | 16.1453 | -122.4289 | -122.406
713.6719 | 122.4426 | -24.4858 | 97.7051 | 0.5959 | -0.026688 | -0.068732 | 0.25113 | -0.10778 | -0.090773 | 0.18347 | -20.2148 | 97.7646 | -24.646 | -24.5682 | -24.5132 | -24.5773 | -24.4812 | -24.4537 | -8.7982 | -24.6643 | -0.16022 | 0.059509 | 4.2709 | -0.082397 | -122.2183 | -0.17853 | -106.5033 | 4.4312 | 0.004578 | 0.032044 | -0.027466 | 122.2504 | 4.2709 | 15.6876 | -0.091553 | -0.17853 | 122.2504 | 4.2709 | -0.091553 | -0.027466 | 15.6876 | -122.3511 | -122.3694
714.7031 | 122.4014 | -23.9868 | 98.2635 | 0.016065 | -0.02562 | -0.069801 | 0.26715 | -0.10778 | -0.079024 | 0.1856 | -19.6564 | 98.3093 | -24.1562 | -24.0097 | -23.9777 | -24.028 | -24.0967 | -23.909 | -8.8028 | -24.1287 | -0.16937 | 0.045776 | 4.3304 | -0.022889 | -122.2412 | -0.14191 | -107.0663 | 4.4998 | -0.10986 | 0.077819 | 0.009155 | 122.2961 | 4.3304 | 15.184 | -0.041199 | -0.14191 | 122.2961 | 4.3304 | -0.041199 | 0.009155 | 15.184 | -122.4197 | -122.3923
715.6719 | 122.319 | -23.4695 | 98.8358 | 0.3365 | -0.026688 | -0.070869 | 0.27249 | -0.11205 | -0.084365 | 0.17385 | -19.3314 | 98.8815 | -23.6023 | -23.3917 | -23.3551 | -23.3963 | -23.6298 | -23.2773 | -8.812 | -23.5977 | -0.13275 | 0.045777 | 4.1382 | 0.077819 | -122.1909 | -0.12817 | -107.6477 | 4.2709 | -0.16022 | 0.19226 | 0.11444 | 122.3511 | 4.1382 | 14.6576 | 0.073242 | -0.12817 | 122.3511 | 4.1382 | 0.073242 | 0.11444 | 14.6576 | -122.438 | -122.4335
716.7188 | 122.4518 | -23.0576 | 99.1653 | 0.62642 | -0.018143 | -0.066596 | 0.25006 | -0.11525 | -0.088637 | 0.1856 | -18.7912 | 99.2157 | -23.2178 | -23.2544 | -23.1857 | -23.2544 | -23.1537 | -23.1216 | -8.7982 | -23.2315 | -0.16022 | 0.050354 | 4.2664 | -0.19684 | -122.3511 | -0.17395 | -107.9636 | 4.4266 | -0.096131 | -0.064087 | -0.12817 | 122.2733 | 4.2664 | 14.2593 | -0.19684 | -0.17395 | 122.2733 | 4.2664 | -0.19684 | -0.12817 | 14.2593 | -122.3831 | -122.3969
717.6562 | 122.3969 | -22.5677 | 99.733 | 0.12288 | -0.010667 | -0.071937 | 0.27143 | -0.10457 | -0.082229 | 0.17599 | -17.7933 | 99.8611 | -22.6227 | -22.6273 | -22.5906 | -22.6044 | -22.7417 | -22.5037 | -8.8028 | -22.6776 | -0.054932 | 0.12817 | 4.7745 | -0.059509 | -122.3236 | -0.10986 | -108.5358 | 4.8294 | -0.17395 | 0.064087 | -0.022888 | 122.4289 | 4.7745 | 13.765 | -0.036621 | -0.10986 | 122.4289 | 4.7745 | -0.036621 | -0.022888 | 13.765 | -122.3557 | -122.4106
718.6562 | 122.3923 | -26.7746 | 95.3979 | 0.092359 | 0.17625 | 0.11498 | 0.26715 | -0.11739 | -0.082229 | 0.1856 | 13.4033 | 96.4416 | -26.1246 | -26.4084 | -26.3031 | -26.4496 | -26.8112 | -26.7929 | -8.8028 | -26.7792 | 0.65002 | 1.0437 | 40.1779 | 0.36621 | -121.701 | -0.004578 | -104.2007 | 39.5279 | -0.036621 | -0.018311 | 0.4715 | 123.2162 | 40.1779 | 17.9718 | 0.32501 | -0.004578 | 123.2162 | 40.1779 | 0.32501 | 0.4715 | 17.9718 | -121.5225 | -122.1771
719.6719 | 122.4655 | -32.1899 | 90.0055 | 0.44331 | 0.30443 | 0.25704 | 0.25754 | -0.10991 | -0.08116 | 0.19094 | 47.0261 | 90.0146 | -32.3868 | -32.3593 | -32.2906 | -32.3822 | -32.2815 | -32.2632 | -8.7982 | -32.3822 | -0.19684 | 0.009155 | 79.216 | -0.16937 | -122.2961 | -0.19226 | -98.8037 | 79.4128 | -0.091553 | -0.073243 | -0.10071 | 122.2046 | 79.216 | 23.3917 | -0.19226 | -0.19226 | 122.2046 | 79.216 | -0.19226 | -0.10071 | 23.3917 | -122.3923 | -122.3877
720.6562 | 122.2778 | -32.9453 | 89.3097 | 0.38228 | 1.1472 | 1.1318 | 0.26715 | -0.10564 | -0.074752 | 0.1824 | 78.3737 | 89.2868 | -33.0368 | -32.8857 | -32.8308 | -32.8995 | -33.0643 | -32.7621 | -8.7982 | -33.0551 | -0.091553 | -0.022888 | 111.319 | 0.059509 | -122.1405 | -0.10986 | -98.1079 | 111.4105 | -0.11902 | 0.1831 | 0.11444 | 122.2321 | 111.319 | 24.147 | 0.045776 | -0.10986 | 122.2321 | 111.319 | 0.045776 | 0.11444 | 24.147 | -122.3465 | -122.3648
721.7188 | 122.3877 | -32.0755 | 90.0925 | 0.24495 | 1.631 | 1.5409 | 0.24793 | -0.1035 | -0.11641 | 0.19628 | 79.2252 | 89.9963 | -32.0892 | -32.2449 | -32.1762 | -32.2449 | -32.1991 | -32.1075 | -8.8074 | -32.2357 | -0.013733 | -0.09613 | 111.3007 | -0.16937 | -122.2687 | -0.16022 | -98.8998 | 111.3144 | -0.1236 | -0.032044 | -0.10071 | 122.0718 | 111.3007 | 23.2681 | -0.16937 | -0.16022 | 122.0718 | 111.3007 | -0.16937 | -0.10071 | 23.2681 | -122.1817 | -122.3282
722.6562 | 122.3785 | -30.7343 | 91.4612 | -0.15178 | 1.3181 | 1.2643 | 0.26715 | -0.11739 | -0.08116 | 0.19415 | 78.8498 | 91.4658 | -30.7755 | -30.8029 | -30.7892 | -30.8304 | -30.9311 | -30.7114 | -8.8074 | -30.8945 | -0.041199 | 0.004577 | 109.584 | -0.068664 | -122.2504 | -0.16022 | -100.2686 | 109.6252 | -0.19684 | 0.022888 | -0.054932 | 122.2 | 109.584 | 21.9269 | -0.09613 | -0.16022 | 122.2 | 109.584 | -0.09613 | -0.054932 | 21.9269 | -122.2366 | -122.3557
723.7188 | 122.2961 | -29.7226 | 92.5049 | 0.56538 | 1.536 | 1.5174 | 0.27463 | -0.11525 | -0.087569 | 0.19415 | 79.6829 | 92.4454 | -29.7318 | -29.6585 | -29.6265 | -29.6906 | -29.8965 | -29.5441 | -8.812 | -29.8416 | -0.009155 | -0.059509 | 109.4055 | 0.064087 | -122.1313 | -0.11902 | -101.3168 | 109.4147 | -0.17395 | 0.17853 | 0.09613 | 122.168 | 109.4055 | 20.9106 | 0.032043 | -0.11902 | 122.168 | 109.4055 | 0.032043 | 0.09613 | 20.9106 | -122.2366 | -122.3465
724.6719 | 122.3648 | -28.949 | 93.3014 | 0.45857 | 0.13246 | 0.085076 | 0.26181 | -0.11312 | -0.084365 | 0.18774 | 81.1615 | 93.3792 | -29.1092 | -28.8712 | -28.8528 | -28.9673 | -29.1092 | -28.8254 | -8.7982 | -29.1046 | -0.16022 | 0.077819 | 110.1105 | 0.07782 | -122.1542 | -0.15564 | -102.0996 | 110.2707 | -0.16022 | 0.1236 | 0.096131 | 122.3282 | 110.1105 | 20.1508 | -0.01831 | -0.15564 | 122.3282 | 110.1105 | -0.01831 | 0.096131 | 20.1508 | -122.4106 | -122.406
725.7031 | 122.4976 | -28.2211 | 94.043 | -0.35015 | 0.15062 | 0.08294 | 0.24472 | -0.10457 | -0.10039 | 0.19842 | 77.1332 | 94.043 | -28.3493 | -28.3859 | -28.3035 | -28.363 | -28.3813 | -28.2211 | -8.8165 | -28.3585 | -0.12817 | 0 | 105.3543 | -0.1648 | -122.3465 | -0.13733 | -102.8595 | 105.4825 | -0.16022 | 0 | -0.082398 | 122.2641 | 105.3543 | 19.4046 | -0.14191 | -0.13733 | 122.2641 | 105.3543 | -0.14191 | -0.082398 | 19.4046 | -122.3923 | -122.4014
726.6719 | 122.4243 | -28.2211 | 94.0292 | 0.32124 | 0.15596 | 0.10003 | 0.24579 | -0.12059 | -0.10786 | 0.18987 | 89.9551 | 94.0247 | -28.3539 | -28.3859 | -28.2761 | -28.3493 | -28.331 | -28.2028 | -8.812 | -28.3905 | -0.13275 | -0.004578 | 118.1763 | -0.1648 | -122.3053 | -0.16937 | -102.8412 | 118.309 | -0.10986 | 0.01831 | -0.054932 | 122.2458 | 118.1763 | 19.4092 | -0.12817 | -0.16937 | 122.2458 | 118.1763 | -0.12817 | -0.054932 | 19.4092 | -122.3831 | -122.4197
727.7031 | 122.4792 | -27.2003 | 95.018 | -0.21282 | 0.15275 | 0.088281 | 0.23297 | -0.12593 | -0.11748 | 0.20376 | 91.5802 | 95.0546 | -27.2964 | -27.4429 | -27.3651 | -27.3926 | -27.2644 | -27.2919 | -8.8211 | -27.3834 | -0.096131 | 0.036621 | 118.7805 | -0.24262 | -122.3831 | -0.18311 | -103.8391 | 118.8766 | -0.064087 | -0.091553 | -0.1648 | 122.2549 | 118.7805 | 18.3792 | -0.19226 | -0.18311 | 122.2549 | 118.7805 | -0.19226 | -0.1648 | 18.3792 | -122.3145 | -122.4014
728.6562 | 122.3877 | -26.77 | 95.5582 | 0.3365 | 0.1848 | 0.1043 | 0.26822 | -0.11418 | -0.070479 | 0.19308 | 92.482 | 95.5673 | -26.9119 | -26.7609 | -26.7334 | -26.7975 | -27.0035 | -26.6418 | -8.812 | -26.8845 | -0.14191 | 0.009155 | 119.252 | 0.009156 | -122.2916 | -0.11444 | -104.3701 | 119.3939 | -0.23346 | 0.12817 | 0.036622 | 122.3373 | 119.252 | 17.9581 | -0.027465 | -0.11444 | 122.3373 | 119.252 | -0.027465 | 0.036622 | 17.9581 | -122.4701 | -122.4426
729.7188 | 122.3877 | -26.1703 | 96.1441 | -0.15178 | 0.14955 | 0.093621 | 0.27677 | -0.11418 | -0.079024 | 0.18881 | 93.0771 | 96.2311 | -26.2802 | -26.2527 | -26.2436 | -26.2665 | -26.3718 | -26.1383 | -8.8074 | -26.2802 | -0.10986 | 0.086975 | 119.2474 | -0.082398 | -122.3877 | -0.10986 | -104.9515 | 119.3573 | -0.20142 | 0.032043 | -0.073242 | 122.4014 | 119.2474 | 17.363 | -0.09613 | -0.10986 | 122.4014 | 119.2474 | -0.09613 | -0.073242 | 17.363 | -122.4243 | -122.4243
730.6562 | 122.4106 | -26.4359 | 95.8694 | -0.12126 | 0.38667 | 0.30618 | 0.25754 | -0.11846 | -0.096114 | 0.19094 | 93.338 | 95.9198 | -26.5732 | -26.4954 | -26.4816 | -26.5182 | -26.7105 | -26.3947 | -8.812 | -26.5411 | -0.13733 | 0.050354 | 119.7739 | -0.059509 | -122.3511 | -0.10529 | -104.6814 | 119.9112 | -0.27466 | 0.041199 | -0.045776 | 122.3557 | 119.7739 | 17.6239 | -0.082398 | -0.10529 | 122.3557 | 119.7739 | -0.082398 | -0.045776 | 17.6239 | -122.4426 | -122.4106
731.7188 | 122.2824 | -17.9306 | 104.3198 | 0.44331 | 3.0057 | 2.9081 | 0.23297 | -0.11205 | -0.087569 | 0.18774 | 16.4612 | 104.0405 | -17.7521 | -18.1778 | -18.1274 | -18.1778 | -18.1229 | -17.9489 | -8.8074 | -18.1183 | 0.17853 | -0.27924 | 34.3918 | -0.24719 | -122.4472 | -0.18768 | -113.1271 | 34.2133 | -0.19226 | -0.018311 | -0.19684 | 121.9711 | 34.3918 | 9.1232 | -0.24719 | -0.18768 | 121.9711 | 34.3918 | -0.24719 | -0.19684 | 9.1232 | -122.0718 | -122.438
732.6719 | 122.4289 | -14.9231 | 107.5836 | -0.10601 | 0.18587 | 0.14916 | 0.26822 | -0.1238 | -0.077956 | 0.18987 | 103.1937 | 107.7301 | -14.8224 | -15.2161 | -14.7995 | -14.9094 | -15.3168 | -14.8773 | -8.7982 | -15.0787 | 0.10071 | 0.14648 | 118.1168 | -0.29297 | -122.3831 | -0.15564 | -116.3818 | 118.0161 | -0.39368 | 0.045777 | 0.1236 | 122.6532 | 118.1168 | 6.1249 | 0.013733 | -0.15564 | 122.6532 | 118.1168 | 0.013733 | 0.1236 | 6.1249 | -122.406 | -122.6624
733.7188 | 122.113 | -12.5336 | 111.0809 | -0.15178 | 0.27986 | 0.21645 | 0.25754 | -0.11952 | -0.090773 | 0.19201 | 108.0048 | 111.0077 | -11.5494 | -10.1532 | -10.5377 | -13.6459 | -15.3168 | -14.6393 | -8.7845 | -12.7396 | 0.98419 | -0.073243 | 120.5383 | 2.3804 | -121.6187 | -0.20599 | -119.8654 | 119.5541 | -2.7832 | -2.1057 | 1.9958 | 123.5413 | 120.5383 | 3.7491 | -1.1124 | -0.20599 | 123.5413 | 120.5383 | -1.1124 | 1.9958 | 3.7491 | -122.6303 | -123.8205
734.6719 | 115.2878 | -13.0463 | 109.2865 | -0.59429 | 0.089736 | 0.0060365 | 0.26502 | -0.11952 | -0.08116 | 0.17706 | -3.1128 | -2.5497 | -0.059509 | -13.0234 | -13.028 | -13.0508 | -13.1744 | -12.886 | -8.8074 | -13.1332 | 12.9868 | -111.8362 | 9.9335 | 0.022889 | -122.3145 | -0.086975 | -118.0939 | -3.0533 | -0.12817 | 0.16022 | 0.018311 | 10.4965 | 9.9335 | 4.2389 | -0.004577 | -0.086975 | 10.4965 | 9.9335 | -0.004577 | 0.018311 | 4.2389 | -109.346 | -122.4197
735.7031 | 122.5021 | -12.6526 | 109.6939 | -0.13652 | 0.057693 | 0.019921 | 0.24045 | -0.11312 | -0.10252 | 0.19522 | -0.059509 | -0.022888 | -0.24261 | -12.8632 | -12.822 | -12.8357 | -12.6892 | -12.6846 | -8.8028 | -12.8174 | 12.41 | -109.7168 | 12.5931 | -0.21057 | -122.5159 | -0.16479 | -118.4967 | 0.18311 | -0.036621 | -0.032043 | -0.16937 | 12.6297 | 12.5931 | 3.8498 | -0.1831 | -0.16479 | 12.6297 | 12.5931 | -0.1831 | -0.16937 | 3.8498 | -109.9365 | -122.5113
736.6562 | 122.4838 | -12.355 | 110.0372 | -0.029711 | 0.067306 | 0.029534 | 0.25434 | -0.10457 | -0.083297 | 0.1824 | -0.086975 | -0.022888 | -0.28839 | -12.4008 | -12.4054 | -12.4054 | -12.4878 | -12.2818 | -8.7936 | -12.4878 | 12.0667 | -110.0601 | 12.2681 | -0.045776 | -122.4426 | -0.13275 | -118.8309 | 0.20142 | -0.13275 | 0.073243 | -0.050354 | 12.3322 | 12.2681 | 3.5614 | -0.050354 | -0.13275 | 12.3322 | 12.2681 | -0.050354 | -0.050354 | 3.5614 | -110.3256 | -122.525
737.6719 | 122.4152 | -12.2223 | 110.202 | 0.22969 | 0.080123 | 0.016717 | 0.26395 | -0.11418 | -0.083297 | 0.18774 | -0.1831 | -0.027466 | -0.3067 | -12.1628 | -12.1536 | -12.1719 | -12.3688 | -12.0483 | -8.7891 | -12.2818 | 11.9156 | -110.2295 | 12.0392 | 0.059509 | -122.3557 | -0.059509 | -118.9911 | 0.1236 | -0.14648 | 0.17395 | 0.068665 | 12.1948 | 12.0392 | 3.4332 | 0.050354 | -0.059509 | 12.1948 | 12.0392 | 0.050354 | 0.068665 | 3.4332 | -110.5087 | -122.4838
738.7188 | 122.493 | -11.9568 | 110.4263 | 0.00080561 | 0.077987 | 0.033807 | 0.26822 | -0.12059 | -0.085433 | 0.18774 | -0.073242 | 0 | -0.27924 | -12.0071 | -12.0117 | -12.0346 | -12.0987 | -11.8881 | -8.7891 | -12.0941 | 11.6776 | -110.4263 | 11.8835 | -0.050354 | -122.4381 | -0.13733 | -119.2154 | 0.20599 | -0.14191 | 0.068664 | -0.054932 | 11.9568 | 11.8835 | 3.1677 | -0.07782 | -0.13733 | 11.9568 | 11.8835 | -0.07782 | -0.054932 | 3.1677 | -110.7056 | -122.5204
739.6562 | 122.5204 | -11.5906 | 110.8109 | 0.24495 | 0.07051 | 0.03167 | 0.23938 | -0.11418 | -0.099318 | 0.18667 | -0.20599 | -0.082397 | -0.21515 | -11.7279 | -11.6638 | -11.6867 | -11.6592 | -11.5448 | -8.7753 | -11.7188 | 11.3754 | -110.8932 | 11.3846 | -0.13733 | -122.4747 | -0.12817 | -119.5862 | 0.009155 | -0.068665 | 0.045776 | -0.073242 | 11.5082 | 11.3846 | 2.8152 | -0.096131 | -0.12817 | 11.5082 | 11.3846 | -0.096131 | -0.073242 | 2.8152 | -111.026 | -122.5296
740.6562 | 122.4655 | -11.4395 | 110.994 | 0.47383 | 0.082259 | 0.023126 | 0.26502 | -0.12059 | -0.057662 | 0.1856 | -0.24719 | -0.086975 | -0.24719 | -11.5814 | -11.4212 | -11.3846 | -11.5997 | -11.3022 | -8.7662 | -11.499 | 11.1923 | -111.0809 | 11.1923 | -0.14191 | -122.4152 | -0.059509 | -119.7601 | 0 | -0.16022 | 0.13733 | 0.01831 | 11.3525 | 11.1923 | 2.6733 | 0.054931 | -0.059509 | 11.3525 | 11.1923 | 0.054931 | 0.01831 | 2.6733 | -111.2412 | -122.493
741.6562 | 122.5662 | -10.9406 | 111.3922 | 2.5032 | 0.064101 | 0.025262 | 0.2522 | -0.11205 | -0.086501 | 0.18026 | -0.1236 | -0.19684 | -0.23804 | -11.142 | -11.0825 | -11.1328 | -10.9909 | -11.0001 | -8.7387 | -11.1282 | 10.7025 | -111.5891 | 10.817 | -0.20142 | -122.4747 | -0.18768 | -120.1309 | 0.11444 | -0.050354 | -0.059509 | -0.14191 | 10.7437 | 10.817 | 2.2018 | -0.19226 | -0.18768 | 10.7437 | 10.817 | -0.19226 | -0.14191 | 2.2018 | -111.6302 | -122.5204
742.7188 | 122.4609 | -10.5972 | 111.8958 | 0.3365 | 0.082259 | 0.03167 | 0.27677 | -0.10884 | -0.067275 | 0.1824 | -0.23804 | -0.12817 | -0.24261 | -10.556 | -10.5469 | -10.5743 | -10.73 | -10.4324 | -8.6929 | -10.6705 | 10.3546 | -112.0239 | 10.3592 | 0.041199 | -122.4426 | -0.073242 | -120.5887 | 0.004578 | -0.13275 | 0.16479 | 0.050354 | 10.4691 | 10.3592 | 1.9043 | 0.022888 | -0.073242 | 10.4691 | 10.3592 | 0.022888 | 0.050354 | 1.9043 | -112.1384 | -122.5662
743.6562 | 122.5113 | -10.3821 | 112.0651 | 0.50435 | 0.089736 | 0.025262 | 0.26288 | -0.11418 | -0.083297 | 0.18987 | -0.10529 | 0.013733 | -0.24719 | -10.3821 | -10.3729 | -10.4141 | -10.4553 | -10.2768 | -8.67 | -10.4782 | 10.1349 | -112.0514 | 10.2768 | 0 | -122.438 | -0.09613 | -120.7352 | 0.14191 | -0.073242 | 0.10529 | 0.009155 | 10.3958 | 10.2768 | 1.712 | -0.032044 | -0.09613 | 10.3958 | 10.2768 | -0.032044 | 0.009155 | 1.712 | -112.3123 | -122.5433
744.7188 | 122.5021 | -9.9701 | 112.4725 | 0.031324 | 0.085464 | 0.020989 | 0.26715 | -0.11098 | -0.083297 | 0.19094 | -0.050354 | 0.013733 | -0.22888 | -9.9792 | -9.9838 | -9.993 | -10.0662 | -9.8694 | -8.6014 | -10.0937 | 9.7412 | -112.4588 | 9.9197 | -0.009155 | -122.4564 | -0.1236 | -121.0739 | 0.17853 | -0.09613 | 0.10071 | -0.013733 | 9.9838 | 9.9197 | 1.3687 | -0.022888 | -0.1236 | 9.9838 | 9.9197 | -0.022888 | -0.013733 | 1.3687 | -112.7014 | -122.5662
745.6562 | 122.5983 | -9.6817 | 112.6923 | 0.76375 | 0.081191 | 0.012444 | 0.25434 | -0.11952 | -0.088637 | 0.18987 | -0.16479 | -0.16022 | -0.19226 | -9.8236 | -9.7733 | -9.8145 | -9.6909 | -9.6909 | -8.5281 | -9.8557 | 9.4894 | -112.8525 | 9.5169 | -0.14191 | -122.4655 | -0.17395 | -121.2204 | 0.027466 | -0.009155 | -0.009155 | -0.091552 | 9.5215 | 9.5169 | 1.1536 | -0.13275 | -0.17395 | 9.5215 | 9.5169 | -0.13275 | -0.091552 | 1.1536 | -112.8845 | -122.5479
746.7031 | 122.4792 | -9.343 | 113.1226 | -0.27385 | 0.084396 | 0.041283 | 0.25434 | -0.11525 | -0.09291 | 0.18453 | -0.2243 | -0.059509 | -0.24719 | -9.343 | -9.3292 | -9.3201 | -9.5169 | -9.1919 | -8.4274 | -9.4482 | 9.0958 | -113.1821 | 9.1187 | 0 | -122.4518 | -0.10529 | -121.55 | 0.022888 | -0.17395 | 0.15106 | 0.013733 | 9.2834 | 9.1187 | 0.91553 | 0.022889 | -0.10529 | 9.2834 | 9.1187 | 0.022889 | 0.013733 | 0.91553 | -113.3698 | -122.5708
747.6562 | 122.525 | -9.0042 | 113.4109 | 0.45857 | 0.0876 | 0.032739 | 0.26074 | -0.11525 | -0.085433 | 0.18026 | -0.16022 | -0.032043 | -0.23346 | -8.9813 | -8.9859 | -9.0088 | -9.0912 | -8.8669 | -8.2718 | -9.1187 | 8.7708 | -113.443 | 8.844 | 0.022888 | -122.3969 | -0.11444 | -121.6827 | 0.073242 | -0.086976 | 0.13733 | 0.01831 | 8.9722 | 8.844 | 0.73242 | -0.004578 | -0.11444 | 8.9722 | 8.844 | -0.004578 | 0.01831 | 0.73242 | -113.6444 | -122.5296
748.6562 | 122.4976 | -8.7112 | 113.768 | 0.092359 | 0.077987 | 0.04342 | 0.26395 | -0.11312 | -0.082229 | 0.18133 | -0.14191 | -0.059509 | -0.21973 | -8.6426 | -8.638 | -8.6472 | -8.7845 | -8.5236 | -8.075 | -8.7845 | 8.4915 | -113.8275 | 8.5693 | 0.068665 | -122.406 | -0.073242 | -121.843 | 0.07782 | -0.073242 | 0.18768 | 0.073243 | 8.6517 | 8.5693 | 0.63629 | 0.064087 | -0.073242 | 8.6517 | 8.5693 | 0.064087 | 0.073243 | 0.63629 | -113.9877 | -122.5525
749.6562 | 122.5845 | -8.5144 | 113.9145 | 0.47383 | 0.061965 | 0.030602 | 0.23831 | -0.12059 | -0.085433 | 0.17919 | -0.022888 | -0.009155 | -0.14648 | -8.6288 | -8.5739 | -8.5876 | -8.5098 | -8.4595 | -7.9788 | -8.6472 | 8.3679 | -113.9236 | 8.4915 | -0.11444 | -122.4884 | -0.13275 | -121.8933 | 0.1236 | 0.004577 | 0.054931 | -0.05951 | 8.5052 | 8.4915 | 0.53558 | -0.073242 | -0.13275 | 8.5052 | 8.4915 | -0.073242 | -0.05951 | 0.53558 | -114.061 | -122.5616
750.7031 | 122.6257 | -8.2443 | 114.1891 | 0.046583 | 0.055557 | 0.023126 | 0.22977 | -0.11739 | -0.10466 | 0.19522 | -0.045776 | -0.004578 | -0.16479 | -8.3725 | -8.3313 | -8.3496 | -8.2581 | -8.2077 | -7.7957 | -8.3908 | 8.0795 | -114.1937 | 8.1985 | -0.12817 | -122.5204 | -0.14648 | -121.9849 | 0.11902 | -0.013733 | 0.036621 | -0.086975 | 8.2397 | 8.1985 | 0.44861 | -0.10528 | -0.14648 | 8.2397 | 8.1985 | -0.10528 | -0.086975 | 0.44861 | -114.3539 | -122.58
751.6562 | 122.5891 | -7.7911 | 114.6606 | 0.55012 | 0.074783 | 0.033807 | 0.25861 | -0.1238 | -0.080092 | 0.1824 | -0.004578 | 0.041199 | -0.16022 | -7.8461 | -7.7866 | -7.8644 | -7.7866 | -7.7362 | -7.4249 | -7.9285 | 7.6309 | -114.6194 | 7.7866 | -0.054931 | -122.4472 | -0.13733 | -122.0856 | 0.15564 | 0.004578 | 0.054932 | 0.004578 | 7.8323 | 7.7866 | 0.36621 | -0.073242 | -0.13733 | 7.8323 | 7.7866 | -0.073242 | 0.004578 | 0.36621 | -114.8209 | -122.5891
752.7031 | 122.5296 | -7.8049 | 114.711 | -0.15178 | 0.071578 | 0.032739 | 0.27143 | -0.11525 | -0.084365 | 0.19522 | -0.036621 | 0.064087 | -0.21515 | -7.7499 | -7.7683 | -7.7591 | -7.8506 | -7.6447 | -7.4249 | -7.8735 | 7.5897 | -114.6469 | 7.7683 | 0.054932 | -122.4792 | -0.068664 | -122.1359 | 0.17853 | -0.045776 | 0.16022 | 0.036621 | 7.869 | 7.7683 | 0.37994 | 0.045777 | -0.068664 | 7.869 | 7.7683 | 0.045777 | 0.036621 | 0.37994 | -114.9261 | -122.5845
753.6562 | 122.6166 | -7.6859 | 114.743 | 0.44331 | 0.080123 | 0.018853 | 0.24579 | -0.11205 | -0.087569 | 0.17278 | 0.009155 | 0.018311 | -0.16022 | -7.7774 | -7.7316 | -7.7637 | -7.6492 | -7.6401 | -7.3334 | -7.8278 | 7.5256 | -114.7247 | 7.695 | -0.091553 | -122.4747 | -0.14191 | -122.0764 | 0.16937 | 0.036621 | 0.045776 | -0.045776 | 7.7042 | 7.695 | 0.35248 | -0.07782 | -0.14191 | 7.7042 | 7.695 | -0.07782 | -0.045776 | 0.35248 | -114.9033 | -122.5708
754.7188 | 122.493 | -7.4112 | 115.1093 | 0.41279 | 0.0876 | 0.029534 | 0.27036 | -0.11418 | -0.088637 | 0.17919 | -0.07782 | 0.07782 | -0.20142 | -7.2922 | -7.3105 | -7.3242 | -7.5027 | -7.1869 | -7.0999 | -7.4799 | 7.2098 | -115.0314 | 7.3334 | 0.11902 | -122.4197 | -0.068664 | -122.2092 | 0.1236 | -0.091553 | 0.2243 | 0.10071 | 7.489 | 7.3334 | 0.31128 | 0.086975 | -0.068664 | 7.489 | 7.3334 | 0.086975 | 0.10071 | 0.31128 | -115.3107 | -122.5891
755.6562 | 122.5296 | -7.2922 | 115.2328 | 0.36702 | 0.090804 | 0.024194 | 0.26715 | -0.11739 | -0.087569 | 0.18347 | -0.041199 | 0.059509 | -0.21057 | -7.1732 | -7.196 | -7.2144 | -7.3563 | -7.0816 | -6.9489 | -7.3517 | 7.0816 | -115.1733 | 7.251 | 0.11902 | -122.4289 | -0.05951 | -122.1817 | 0.16937 | -0.064087 | 0.21057 | 0.09613 | 7.3517 | 7.251 | 0.34332 | 0.07782 | -0.05951 | 7.3517 | 7.251 | 0.07782 | 0.09613 | 0.34332 | -115.4434 | -122.5845
756.6562 | 122.525 | -7.1182 | 115.448 | 0.061841 | 0.090804 | 0.038079 | 0.26929 | -0.10564 | -0.082229 | 0.18347 | -0.018311 | 0.064087 | -0.19226 | -7.0221 | -7.0267 | -7.0221 | -7.1777 | -6.9168 | -6.7978 | -7.1915 | 6.926 | -115.3839 | 7.0999 | 0.09613 | -122.4747 | -0.073242 | -122.2458 | 0.17395 | -0.059509 | 0.20142 | 0.091553 | 7.1823 | 7.0999 | 0.32043 | 0.09613 | -0.073242 | 7.1823 | 7.0999 | 0.09613 | 0.091553 | 0.32043 | -115.6403 | -122.6395
757.7188 | 122.4655 | -6.8207 | 115.7318 | 0.41279 | 0.079055 | 0.045556 | 0.25968 | -0.10991 | -0.091842 | 0.18667 | -0.064087 | 0.068665 | -0.19684 | -6.7108 | -6.7154 | -6.7383 | -6.9122 | -6.5964 | -6.5689 | -6.9122 | 6.6238 | -115.6631 | 6.7566 | 0.10986 | -122.4472 | -0.091552 | -122.3007 | 0.13275 | -0.091552 | 0.2243 | 0.10529 | 6.8893 | 6.7566 | 0.25177 | 0.082398 | -0.091552 | 6.8893 | 6.7566 | 0.082398 | 0.10529 | 0.25177 | -115.9287 | -122.644
758.6562 | 122.5708 | -6.6376 | 115.8417 | -0.60955 | 0.089736 | 0.024194 | 0.2522 | -0.11205 | -0.07582 | 0.18881 | -0.013733 | 0.1236 | -0.16022 | -6.5598 | -6.5643 | -6.5872 | -6.6833 | -6.459 | -6.34 | -6.7429 | 6.4774 | -115.7181 | 6.6238 | 0.07782 | -122.406 | -0.10529 | -122.1817 | 0.14648 | -0.045777 | 0.17853 | 0.073242 | 6.7612 | 6.6238 | 0.29755 | 0.050354 | -0.10529 | 6.7612 | 6.6238 | 0.050354 | 0.073242 | 0.29755 | -116.0019 | -122.5845
759.6562 | 122.5754 | -6.4224 | 116.0797 | 0.10762 | 0.077987 | 0.02633 | 0.2554 | -0.11846 | -0.071547 | 0.17599 | 0 | 0.07782 | -0.17853 | -6.3446 | -6.395 | -6.3858 | -6.459 | -6.2759 | -6.1707 | -6.4819 | 6.2439 | -116.0019 | 6.4224 | 0.07782 | -122.4747 | -0.05951 | -122.2504 | 0.17853 | -0.036621 | 0.14648 | 0.027466 | 6.5002 | 6.4224 | 0.25177 | 0.036621 | -0.05951 | 6.5002 | 6.4224 | 0.036621 | 0.027466 | 0.25177 | -116.2582 | -122.5616
760.6562 | 122.525 | -6.34 | 116.2079 | 0.12288 | 0.089736 | 0.041283 | 0.2554 | -0.10564 | -0.080092 | 0.18667 | 0 | 0.082397 | -0.19226 | -6.2302 | -6.2302 | -6.2347 | -6.3766 | -6.1295 | -6.0608 | -6.4087 | 6.1478 | -116.1255 | 6.34 | 0.10986 | -122.4381 | -0.068664 | -122.2687 | 0.19226 | -0.036621 | 0.21057 | 0.10986 | 6.4224 | 6.34 | 0.27924 | 0.10529 | -0.068664 | 6.4224 | 6.34 | 0.10529 | 0.10986 | 0.27924 | -116.4001 | -122.6166
761.6562 | 122.5708 | -6.0928 | 116.4688 | 0.061841 | 0.086532 | 0.019921 | 0.26502 | -0.10564 | -0.086501 | 0.19308 | -0.013733 | 0.082397 | -0.15564 | -5.9967 | -5.9921 | -5.983 | -6.1157 | -5.8868 | -5.8273 | -6.1661 | 5.9372 | -116.3864 | 6.0791 | 0.09613 | -122.4609 | -0.073243 | -122.2961 | 0.14191 | -0.022889 | 0.20599 | 0.10071 | 6.1752 | 6.0791 | 0.2655 | 0.10986 | -0.073243 | 6.1752 | 6.0791 | 0.10986 | 0.10071 | 0.2655 | -116.6245 | -122.6349
762.7188 | 122.5525 | -5.8365 | 116.6794 | -0.1823 | 0.073715 | 0.035943 | 0.25434 | -0.097095 | -0.085433 | 0.17919 | 0.009155 | 0.10529 | -0.11902 | -5.7907 | -5.7724 | -5.7678 | -5.8868 | -5.6717 | -5.5939 | -5.9418 | 5.7175 | -116.5741 | 5.8456 | 0.045777 | -122.4518 | -0.10529 | -122.2733 | 0.12817 | -0.050354 | 0.16479 | 0.064087 | 5.9418 | 5.8456 | 0.24261 | 0.068665 | -0.10529 | 5.9418 | 5.8456 | 0.068665 | 0.064087 | 0.24261 | -116.7984 | -122.6212
763.6562 | 122.5891 | -5.7632 | 116.7755 | -0.014452 | 0.089736 | 0.017785 | 0.26181 | -0.1035 | -0.089705 | 0.18881 | 0.091553 | 0.09613 | -0.11444 | -5.6808 | -5.6946 | -5.6808 | -5.7861 | -5.6168 | -5.5115 | -5.8411 | 5.6488 | -116.6794 | 5.8548 | 0.082398 | -122.4701 | -0.077819 | -122.287 | 0.20599 | -0.022888 | 0.14649 | 0.068665 | 5.8594 | 5.8548 | 0.25177 | 0.082398 | -0.077819 | 5.8594 | 5.8548 | 0.082398 | 0.068665 | 0.25177 | -116.89 | -122.6166
764.6719 | 122.5296 | -5.6351 | 116.9312 | 0.21443 | 0.084396 | 0.040215 | 0.24686 | -0.10564 | -0.073684 | 0.19308 | -0.064087 | 0.073242 | -0.2243 | -5.4977 | -5.4749 | -5.4749 | -5.722 | -5.3833 | -5.4245 | -5.6992 | 5.4108 | -116.8579 | 5.571 | 0.13733 | -122.406 | -0.064087 | -122.3557 | 0.16022 | -0.086975 | 0.25177 | 0.16022 | 5.7083 | 5.571 | 0.21057 | 0.16022 | -0.064087 | 5.7083 | 5.571 | 0.16022 | 0.16022 | 0.21057 | -117.1555 | -122.6303
765.7188 | 122.6761 | -5.5023 | 117.009 | -0.014452 | 0.059829 | 0.038079 | 0.22443 | -0.10778 | -0.11 | 0.18987 | -0.018311 | 0.032043 | -0.13733 | -5.5893 | -5.5389 | -5.5344 | -5.4382 | -5.4428 | -5.278 | -5.6168 | 5.365 | -116.9769 | 5.484 | -0.086975 | -122.5479 | -0.11444 | -122.287 | 0.11902 | 0.064087 | 0.059509 | -0.036621 | 5.5344 | 5.484 | 0.2243 | -0.032044 | -0.11444 | 5.5344 | 5.484 | -0.032044 | -0.036621 | 0.2243 | -117.1463 | -122.6257
766.6562 | 122.5662 | -5.4291 | 117.16 | 0.10762 | 0.092941 | 0.034875 | 0.26395 | -0.11952 | -0.084365 | 0.18133 | 0.009155 | 0.10529 | -0.16937 | -5.3284 | -5.3284 | -5.3284 | -5.4428 | -5.2231 | -5.2002 | -5.5023 | 5.2597 | -117.0547 | 5.4382 | 0.10071 | -122.4884 | -0.073242 | -122.3602 | 0.17853 | -0.013733 | 0.20599 | 0.10071 | 5.5344 | 5.4382 | 0.22888 | 0.10071 | -0.073242 | 5.5344 | 5.4382 | 0.10071 | 0.10071 | 0.22888 | -117.3294 | -122.6624
767.6719 | 122.5571 | -5.0491 | 117.5446 | 0.35176 | 0.083328 | 0.02633 | 0.26822 | -0.10778 | -0.083297 | 0.18133 | -0.032043 | 0.064087 | -0.19226 | -4.9118 | -4.9026 | -4.9072 | -5.0903 | -4.8065 | -4.8386 | -5.1132 | 4.8569 | -117.4805 | 5.0171 | 0.13733 | -122.4472 | -0.064087 | -122.3831 | 0.16022 | -0.041199 | 0.24261 | 0.14648 | 5.1132 | 5.0171 | 0.21057 | 0.14191 | -0.064087 | 5.1132 | 5.0171 | 0.14191 | 0.14648 | 0.21057 | -117.7368 | -122.6578
768.6562 | 122.6028 | -5.0079 | 117.572 | 0.15339 | 0.081191 | 0.025262 | 0.27143 | -0.11525 | -0.072616 | 0.18347 | 0.013733 | 0.068665 | -0.16022 | -4.9438 | -4.921 | -4.921 | -5.0354 | -4.8203 | -4.7791 | -5.0949 | 4.8477 | -117.5034 | 5.0217 | 0.064087 | -122.493 | -0.086975 | -122.3511 | 0.17395 | -0.027465 | 0.18768 | 0.086976 | 5.0766 | 5.0217 | 0.22888 | 0.086976 | -0.086975 | 5.0766 | 5.0217 | 0.086976 | 0.086976 | 0.22888 | -117.7322 | -122.6669
769.6719 | 122.612 | -4.9347 | 117.6315 | 0.5196 | 0.080123 | 0.035943 | 0.25327 | -0.11632 | -0.083297 | 0.17919 | -0.036621 | 0.082397 | -0.17853 | -4.866 | -4.8431 | -4.8569 | -4.9347 | -4.7699 | -4.7333 | -5.0491 | 4.7562 | -117.5491 | 4.8981 | 0.068664 | -122.4747 | -0.11444 | -122.3648 | 0.14191 | 0 | 0.16479 | 0.091552 | 5.0171 | 4.8981 | 0.20142 | 0.077819 | -0.11444 | 5.0171 | 4.8981 | 0.077819 | 0.091552 | 0.20142 | -117.8101 | -122.6807
770.6562 | 122.612 | -4.7287 | 117.8238 | -0.15178 | 0.083328 | 0.016717 | 0.26502 | -0.11952 | -0.086501 | 0.18453 | -0.032043 | 0.086975 | -0.1831 | -4.628 | -4.6509 | -4.6371 | -4.7607 | -4.541 | -4.5136 | -4.8157 | 4.5456 | -117.7368 | 4.6967 | 0.10071 | -122.4747 | -0.086975 | -122.3373 | 0.15106 | -0.032043 | 0.18768 | 0.07782 | 4.8157 | 4.6967 | 0.21515 | 0.091553 | -0.086975 | 4.8157 | 4.6967 | 0.091553 | 0.07782 | 0.21515 | -118.0069 | -122.6395
771.7188 | 122.5891 | -4.5639 | 118.0344 | -0.029711 | 0.081191 | 0.042352 | 0.26074 | -0.11846 | -0.091842 | 0.18987 | -0.041199 | 0.086975 | -0.18768 | -4.454 | -4.4769 | -4.454 | -4.628 | -4.3625 | -4.3625 | -4.6463 | 4.3762 | -117.9474 | 4.5227 | 0.10986 | -122.5113 | -0.082397 | -122.3969 | 0.14648 | -0.064087 | 0.20142 | 0.086975 | 4.6509 | 4.5227 | 0.20142 | 0.10986 | -0.082397 | 4.6509 | 4.5227 | 0.10986 | 0.086975 | 0.20142 | -118.222 | -122.6807
772.6562 | 122.6303 | -4.5044 | 118.0939 | -0.060229 | 0.080123 | 0.025262 | 0.25113 | -0.10137 | -0.086501 | 0.19522 | -0.009155 | 0.07782 | -0.18768 | -4.4128 | -4.4449 | -4.4174 | -4.5273 | -4.3396 | -4.2938 | -4.5959 | 4.3167 | -118.0161 | 4.4952 | 0.091553 | -122.5388 | -0.091552 | -122.3877 | 0.17853 | -0.022888 | 0.16479 | 0.05951 | 4.5822 | 4.4952 | 0.21057 | 0.086976 | -0.091552 | 4.5822 | 4.4952 | 0.086976 | 0.05951 | 0.21057 | -118.2816 | -122.6898
773.7188 | 122.5845 | -4.2938 | 118.3182 | 0.21443 | 0.07051 | 0.034875 | 0.26181 | -0.10457 | -0.082229 | 0.1824 | 0.009155 | 0.09613 | -0.16937 | -4.1794 | -4.1748 | -4.1794 | -4.2938 | -4.0878 | -4.0787 | -4.3808 | 4.1244 | -118.222 | 4.303 | 0.11444 | -122.493 | -0.086975 | -122.3969 | 0.17853 | 0 | 0.20599 | 0.11902 | 4.39 | 4.303 | 0.21515 | 0.11444 | -0.086975 | 4.39 | 4.303 | 0.11444 | 0.11902 | 0.21515 | -118.4875 | -122.699
774.6562 | 122.6257 | -4.2526 | 118.3273 | 0.046583 | 0.071578 | 0.022057 | 0.25006 | -0.11952 | -0.07582 | 0.19094 | 0.004578 | 0.086975 | -0.17395 | -4.1702 | -4.1748 | -4.1748 | -4.248 | -4.0741 | -4.0512 | -4.3304 | 4.0787 | -118.2404 | 4.2572 | 0.082398 | -122.5021 | -0.077819 | -122.3785 | 0.17853 | 0.004578 | 0.17853 | 0.07782 | 4.3396 | 4.2572 | 0.20142 | 0.07782 | -0.077819 | 4.3396 | 4.2572 | 0.07782 | 0.07782 | 0.20142 | -118.5013 | -122.6578
775.6562 | 122.6212 | -4.1977 | 118.4052 | -0.014452 | 0.077987 | 0.042352 | 0.25754 | -0.10778 | -0.087569 | 0.19628 | 0.013733 | 0.073242 | -0.16479 | -4.1016 | -4.1153 | -4.1016 | -4.2023 | -4.0192 | -3.9825 | -4.2847 | 4.0329 | -118.3319 | 4.2114 | 0.096131 | -122.5204 | -0.086975 | -122.3877 | 0.17853 | -0.004578 | 0.17853 | 0.082398 | 4.2709 | 4.2114 | 0.21515 | 0.096131 | -0.086975 | 4.2709 | 4.2114 | 0.096131 | 0.082398 | 0.21515 | -118.5699 | -122.6898
776.6562 | 122.6257 | -4.129 | 118.4692 | -0.12126 | 0.084396 | 0.025262 | 0.25113 | -0.10991 | -0.079024 | 0.18453 | 0 | 0.091553 | -0.17395 | -4.0375 | -4.0421 | -4.0146 | -4.1107 | -3.9322 | -3.9139 | -4.1931 | 3.9551 | -118.3777 | 4.129 | 0.091552 | -122.5113 | -0.064087 | -122.3831 | 0.17395 | 0.01831 | 0.19684 | 0.086975 | 4.2206 | 4.129 | 0.21515 | 0.11444 | -0.064087 | 4.2206 | 4.129 | 0.11444 | 0.086975 | 0.21515 | -118.6432 | -122.6624
777.7188 | 122.6166 | -3.7308 | 118.8904 | 0.39753 | 0.079055 | 0.038079 | 0.25754 | -0.11312 | -0.08116 | 0.18881 | -0.041199 | 0.086975 | -0.16937 | -3.6209 | -3.6072 | -3.6209 | -3.7354 | -3.5294 | -3.5431 | -3.7994 | 3.5614 | -118.8034 | 3.6896 | 0.10986 | -122.4976 | -0.068664 | -122.4335 | 0.12817 | -0.004578 | 0.20142 | 0.1236 | 3.8177 | 3.6896 | 0.18768 | 0.10986 | -0.068664 | 3.8177 | 3.6896 | 0.10986 | 0.1236 | 0.18768 | -119.0598 | -122.6898
778.6562 | 122.5983 | -3.8223 | 118.808 | -0.28911 | 0.091872 | 0.014581 | 0.2522 | -0.11632 | -0.08116 | 0.18667 | -0.050354 | 0.086975 | -0.17395 | -3.6987 | -3.6804 | -3.6758 | -3.8956 | -3.6072 | -3.6209 | -3.8818 | 3.6484 | -118.721 | 3.772 | 0.1236 | -122.4884 | -0.059509 | -122.4289 | 0.1236 | -0.073242 | 0.21515 | 0.14191 | 3.9093 | 3.772 | 0.20142 | 0.14649 | -0.059509 | 3.9093 | 3.772 | 0.14649 | 0.14191 | 0.20142 | -118.9819 | -122.6898
779.7188 | 122.6715 | -3.8086 | 118.8126 | -0.090746 | 0.073715 | 0.051965 | 0.26074 | -0.10564 | -0.090773 | 0.19201 | -0.013733 | 0.068665 | -0.17395 | -3.7079 | -3.717 | -3.717 | -3.8132 | -3.6209 | -3.6026 | -3.891 | 3.6346 | -118.7439 | 3.7949 | 0.10071 | -122.5296 | -0.082397 | -122.4152 | 0.16022 | -0.004577 | 0.18768 | 0.091553 | 3.8773 | 3.7949 | 0.20599 | 0.091553 | -0.082397 | 3.8773 | 3.7949 | 0.091553 | 0.091553 | 0.20599 | -118.9865 | -122.7036
780.6562 | 122.6578 | -3.5202 | 119.1101 | -0.13652 | 0.084396 | 0.0071045 | 0.25968 | -0.1035 | -0.085433 | 0.18347 | 0.009155 | 0.082397 | -0.16937 | -3.4287 | -3.4332 | -3.4058 | -3.5202 | -3.3188 | -3.3188 | -3.5934 | 3.3508 | -119.0277 | 3.5294 | 0.091553 | -122.5433 | -0.073242 | -122.4289 | 0.17853 | 0 | 0.20142 | 0.086975 | 3.6026 | 3.5294 | 0.20142 | 0.11444 | -0.073242 | 3.6026 | 3.5294 | 0.11444 | 0.086975 | 0.20142 | -119.2795 | -122.7036
781.6562 | 122.6486 | -3.3508 | 119.2566 | -0.15178 | 0.071578 | 0.020989 | 0.25968 | -0.11632 | -0.097182 | 0.18774 | -0.013733 | 0.091553 | -0.18768 | -3.2501 | -3.2684 | -3.2455 | -3.3737 | -3.1631 | -3.1677 | -3.447 | 3.1631 | -119.165 | 3.3371 | 0.10071 | -122.525 | -0.09613 | -122.4243 | 0.17395 | -0.022888 | 0.18768 | 0.082397 | 3.4424 | 3.3371 | 0.18311 | 0.10529 | -0.09613 | 3.4424 | 3.3371 | 0.10529 | 0.082397 | 0.18311 | -119.4443 | -122.7036
782.6562 | 122.6028 | -3.3234 | 119.3298 | -2.3948 | 0.080123 | 0.03167 | 0.2554 | -0.10564 | -0.096114 | 0.18881 | -0.068665 | 0.13733 | -0.14191 | -3.1723 | -3.2043 | -3.1631 | -3.3691 | -3.0716 | -3.1036 | -3.3737 | 3.1815 | -119.1925 | 3.2547 | 0.15106 | -122.5342 | -0.050354 | -122.4335 | 0.073242 | -0.045777 | 0.25177 | 0.11902 | 3.4607 | 3.2547 | 0.21973 | 0.16022 | -0.050354 | 3.4607 | 3.2547 | 0.16022 | 0.11902 | 0.21973 | -119.4717 | -122.7036
783.7188 | 122.6349 | -3.3051 | 119.3344 | -0.53325 | 0.0876 | 0.027398 | 0.25861 | -0.10991 | -0.090773 | 0.1856 | 0.041199 | 0.14191 | -0.091553 | -3.1952 | -3.2227 | -3.2135 | -3.3279 | -3.1265 | -3.0808 | -3.3966 | 3.2135 | -119.1925 | 3.3463 | 0.10986 | -122.5571 | -0.091552 | -122.4152 | 0.13275 | -0.022888 | 0.17853 | 0.082398 | 3.447 | 3.3463 | 0.2243 | 0.091553 | -0.091552 | 3.447 | 3.3463 | 0.091553 | 0.082398 | 0.2243 | -119.426 | -122.731
784.6562 | 122.5937 | -3.1586 | 119.4534 | -0.27385 | 0.082259 | -0.00037251 | 0.2522 | -0.10778 | -0.095046 | 0.18987 | -0.064087 | 0.082397 | -0.1831 | -2.9846 | -2.8748 | -2.9068 | -3.2089 | -2.9663 | -2.9938 | -3.2364 | 2.9755 | -119.371 | 3.0945 | 0.17395 | -122.3282 | -0.07782 | -122.4472 | 0.11902 | -0.050354 | 0.19226 | 0.28381 | 3.241 | 3.0945 | 0.16479 | 0.25177 | -0.07782 | 3.241 | 3.0945 | 0.25177 | 0.28381 | 0.16479 | -119.6365 | -122.6898
785.6562 | 122.5754 | -3.2272 | 119.3985 | -0.30437 | 0.071578 | 0.023126 | 0.25861 | -0.10884 | -0.099318 | 0.19201 | -0.045776 | 0.11444 | -0.17853 | -3.1311 | -3.1448 | -3.1174 | -3.3096 | -2.8793 | -3.0716 | -3.3051 | 3.0487 | -119.2841 | 3.1815 | 0.09613 | -122.5433 | -0.07782 | -122.4701 | 0.13275 | -0.082397 | 0.3479 | 0.082398 | 3.3417 | 3.1815 | 0.15564 | 0.10986 | -0.07782 | 3.3417 | 3.1815 | 0.10986 | 0.082398 | 0.15564 | -119.577 | -122.7036
786.7188 | 122.6532 | -2.9984 | 119.7235 | -0.30437 | 0.083328 | 0.020989 | 0.25647 | -0.11739 | -0.096114 | 0.18453 | -0.050354 | 0.09613 | -0.16022 | -2.8931 | -2.8976 | -2.8656 | -3.0945 | -2.8015 | -2.8473 | -3.0945 | 2.8381 | -119.6274 | 2.948 | 0.10529 | -122.6212 | -0.09613 | -122.5708 | 0.10986 | -0.09613 | 0.19684 | 0.10071 | 3.0945 | 2.948 | 0.15106 | 0.13275 | -0.09613 | 3.0945 | 2.948 | 0.13275 | 0.10071 | 0.15106 | -119.8837 | -122.818
787.6562 | 122.6532 | -2.9297 | 119.7189 | -0.075488 | 0.075851 | 0.012444 | 0.26181 | -0.10244 | -0.076888 | 0.18347 | 0.027466 | 0.091553 | -0.17395 | -2.8564 | -2.8748 | -2.8564 | -2.9572 | -2.774 | -2.7649 | -3.0396 | 2.7557 | -119.6274 | 2.9572 | 0.073242 | -122.5937 | -0.10986 | -122.4838 | 0.20142 | -0.027466 | 0.15564 | 0.054931 | 3.0212 | 2.9572 | 0.16479 | 0.073242 | -0.10986 | 3.0212 | 2.9572 | 0.073242 | 0.054931 | 0.16479 | -119.8929 | -122.7585
788.6562 | 122.6486 | -2.8381 | 119.8059 | -0.19756 | 0.0876 | 0.016717 | 0.26502 | -0.11205 | -0.086501 | 0.19094 | 0.022888 | 0.10529 | -0.16022 | -2.7603 | -2.7786 | -2.7512 | -2.8473 | -2.6733 | -2.6779 | -2.9343 | 2.6779 | -119.7006 | 2.861 | 0.07782 | -122.5845 | -0.09613 | -122.4838 | 0.1831 | -0.009155 | 0.16479 | 0.05951 | 2.9434 | 2.861 | 0.16022 | 0.086975 | -0.09613 | 2.9434 | 2.861 | 0.086975 | 0.05951 | 0.16022 | -119.9661 | -122.7402
789.6562 | 122.644 | -2.8427 | 119.8242 | -0.19756 | 0.079055 | 0.033807 | 0.25434 | -0.11418 | -0.097182 | 0.19094 | 0.013733 | 0.10986 | -0.16479 | -2.7374 | -2.7466 | -2.7374 | -2.8473 | -2.6642 | -2.6642 | -2.9205 | 2.6779 | -119.7144 | 2.8564 | 0.10529 | -122.5708 | -0.07782 | -122.4884 | 0.17853 | -0.004578 | 0.17853 | 0.09613 | 2.9526 | 2.8564 | 0.17853 | 0.10529 | -0.07782 | 2.9526 | 2.8564 | 0.10529 | 0.09613 | 0.17853 | -119.989 | -122.7448
790.7031 | 122.7631 | -2.829 | 119.7418 | -0.060229 | 0.054488 | 0.015649 | 0.23511 | -0.11846 | -0.096114 | 0.19842 | 0.059509 | 0.045776 | -0.11902 | -2.948 | -2.8931 | -2.8656 | -2.7695 | -2.7786 | -2.6688 | -2.9709 | 2.71 | -119.696 | 2.8885 | -0.11902 | -122.6349 | -0.14191 | -122.4106 | 0.17853 | 0.059509 | 0.050354 | -0.064087 | 2.8748 | 2.8885 | 0.16022 | -0.036622 | -0.14191 | 2.8748 | 2.8885 | -0.036622 | -0.064087 | 0.16022 | -119.8608 | -122.7127
791.6562 | 122.644 | -2.7649 | 119.9112 | -0.13652 | 0.085464 | 0.023126 | 0.25861 | -0.11098 | -0.089705 | 0.1856 | -0.018311 | 0.11902 | -0.13733 | -2.6047 | -2.6321 | -2.6001 | -2.8198 | -2.5406 | -2.5635 | -2.8244 | 2.6276 | -119.7922 | 2.7466 | 0.16022 | -122.5433 | -0.059509 | -122.4747 | 0.11902 | -0.054931 | 0.2243 | 0.13275 | 2.8839 | 2.7466 | 0.20142 | 0.16479 | -0.059509 | 2.8839 | 2.7466 | 0.16479 | 0.13275 | 0.20142 | -120.0485 | -122.7356
792.6562 | 122.6303 | -2.7283 | 119.9432 | -0.04497 | 0.071578 | 0.014581 | 0.27036 | -0.11632 | -0.087569 | 0.17813 | -0.041199 | 0.12817 | -0.13733 | -2.5864 | -2.6047 | -2.5864 | -2.7924 | -2.4948 | -2.5543 | -2.8015 | 2.5909 | -119.8151 | 2.6871 | 0.14191 | -122.5479 | -0.073243 | -122.4976 | 0.09613 | -0.064087 | 0.23346 | 0.1236 | 2.8564 | 2.6871 | 0.17395 | 0.14191 | -0.073243 | 2.8564 | 2.6871 | 0.14191 | 0.1236 | 0.17395 | -120.0806 | -122.7448
793.7031 | 122.6578 | -2.5955 | 120.0623 | -0.45696 | 0.067306 | 0.034875 | 0.25861 | -0.11418 | -0.091842 | 0.18987 | 0 | 0.13733 | -0.10986 | -2.4811 | -2.5131 | -2.504 | -2.623 | -2.4353 | -2.4078 | -2.7054 | 2.4857 | -119.9249 | 2.5955 | 0.11444 | -122.5754 | -0.10986 | -122.4701 | 0.10986 | -0.027466 | 0.16022 | 0.082397 | 2.7328 | 2.5955 | 0.18768 | 0.091553 | -0.10986 | 2.7328 | 2.5955 | 0.091553 | 0.082397 | 0.18768 | -120.1721 | -122.7676
794.6562 | 122.6852 | -2.5864 | 120.0714 | 0.031324 | 0.074783 | 0.029534 | 0.26502 | -0.10457 | -0.085433 | 0.17599 | 0.054932 | 0.09613 | -0.12817 | -2.4719 | -2.4994 | -2.4765 | -2.5772 | -2.4078 | -2.3987 | -2.6642 | 2.4582 | -119.9753 | 2.6413 | 0.11444 | -122.5708 | -0.07782 | -122.4701 | 0.18311 | 0.009156 | 0.17853 | 0.086975 | 2.6825 | 2.6413 | 0.18768 | 0.10986 | -0.07782 | 2.6825 | 2.6413 | 0.10986 | 0.086975 | 0.18768 | -120.1996 | -122.7356
795.6562 | 122.6715 | -2.6276 | 120.0439 | -0.014452 | 0.085464 | 0.034875 | 0.25861 | -0.11098 | -0.079024 | 0.1856 | 0.036621 | 0.086975 | -0.14648 | -2.5177 | -2.5177 | -2.5223 | -2.6321 | -2.4445 | -2.449 | -2.7008 | 2.4811 | -119.957 | 2.6642 | 0.10986 | -122.5616 | -0.073243 | -122.493 | 0.18311 | -0.004578 | 0.1831 | 0.10986 | 2.7145 | 2.6642 | 0.17853 | 0.10528 | -0.073243 | 2.7145 | 2.6642 | 0.10528 | 0.10986 | 0.17853 | -120.1904 | -122.7448
796.6562 | 122.6944 | -2.5177 | 120.1355 | -0.075488 | 0.082259 | 0.040215 | 0.26502 | -0.11205 | -0.072616 | 0.18881 | 0.027466 | 0.10071 | -0.14648 | -2.417 | -2.4399 | -2.4124 | -2.5269 | -2.3438 | -2.3392 | -2.6093 | 2.3712 | -120.0348 | 2.5452 | 0.10071 | -122.5754 | -0.091553 | -122.4747 | 0.17395 | -0.009155 | 0.17395 | 0.07782 | 2.6184 | 2.5452 | 0.17853 | 0.10528 | -0.091553 | 2.6184 | 2.5452 | 0.10528 | 0.07782 | 0.17853 | -120.282 | -122.7448
797.6562 | 122.699 | -2.4994 | 120.1767 | -0.15178 | 0.085464 | 0.04342 | 0.27036 | -0.10884 | -0.077956 | 0.18987 | 0.032043 | 0.09613 | -0.16022 | -2.3895 | -2.3941 | -2.3804 | -2.4811 | -2.3026 | -2.33 | -2.5681 | 2.3392 | -120.0806 | 2.5314 | 0.10986 | -122.5708 | -0.068664 | -122.5067 | 0.19226 | 0.018311 | 0.19684 | 0.10529 | 2.5955 | 2.5314 | 0.16937 | 0.11902 | -0.068664 | 2.5955 | 2.5314 | 0.11902 | 0.10529 | 0.16937 | -120.3369 | -122.7448
798.6562 | 122.6669 | -2.4765 | 120.2133 | -2.9899 | 0.07051 | 0.037011 | 0.25113 | -0.11525 | -0.085433 | 0.18774 | -0.022888 | 0.13275 | -0.11902 | -2.33 | -2.3438 | -2.3483 | -2.5497 | -2.2614 | -2.2842 | -2.5406 | 2.3575 | -120.0806 | 2.4536 | 0.14648 | -122.5571 | -0.064087 | -122.4976 | 0.096131 | -0.073243 | 0.21515 | 0.13275 | 2.6093 | 2.4536 | 0.19226 | 0.12817 | -0.064087 | 2.6093 | 2.4536 | 0.12817 | 0.13275 | 0.19226 | -120.3323 | -122.7539
799.7031 | 122.7859 | -2.3712 | 120.2591 | -0.04497 | 0.064101 | 0.0092405 | 0.23297 | -0.12059 | -0.11534 | 0.1824 | 0.050354 | 0.064087 | -0.11444 | -2.4582 | -2.4078 | -2.3941 | -2.2797 | -2.3209 | -2.2018 | -2.4857 | 2.2568 | -120.195 | 2.4216 | -0.086975 | -122.6669 | -0.11444 | -122.4609 | 0.16479 | 0.091553 | 0.050354 | -0.036621 | 2.4353 | 2.4216 | 0.16937 | -0.022888 | -0.11444 | 2.4353 | 2.4216 | -0.022888 | -0.036621 | 0.16937 | -120.3735 | -122.7448
800.6562 | 122.7173 | -2.3529 | 120.314 | 0.0771 | 0.084396 | 0.023126 | 0.26074 | -0.11632 | -0.082229 | 0.18133 | 0.041199 | 0.09613 | -0.15564 | -2.2476 | -2.2614 | -2.243 | -2.3483 | -2.1698 | -2.1652 | -2.4124 | 2.1973 | -120.2179 | 2.3941 | 0.10528 | -122.5754 | -0.05951 | -122.4792 | 0.19684 | 0.004577 | 0.1831 | 0.091552 | 2.449 | 2.3941 | 0.18768 | 0.10986 | -0.05951 | 2.449 | 2.3941 | 0.10986 | 0.091552 | 0.18768 | -120.4697 | -122.7264
801.6562 | 122.6852 | -2.3254 | 120.3598 | 0.26021 | 0.082259 | 0.044488 | 0.26715 | -0.10991 | -0.079024 | 0.1824 | 0.036621 | 0.1236 | -0.13733 | -2.1835 | -2.1973 | -2.179 | -2.3254 | -2.1194 | -2.1469 | -2.4078 | 2.1881 | -120.2362 | 2.3621 | 0.14191 | -122.5571 | -0.082398 | -122.5067 | 0.17395 | 0 | 0.20599 | 0.12817 | 2.449 | 2.3621 | 0.17853 | 0.14648 | -0.082398 | 2.449 | 2.3621 | 0.14648 | 0.12817 | 0.17853 | -120.4971 | -122.7676
802.7188 | 122.6761 | -2.3026 | 120.3873 | 0.10762 | 0.081191 | 0.035943 | 0.26074 | -0.11098 | -0.082229 | 0.18881 | 0.032043 | 0.1236 | -0.13275 | -2.1606 | -2.1652 | -2.1652 | -2.298 | -2.1057 | -2.1149 | -2.3758 | 2.1698 | -120.2637 | 2.3346 | 0.14191 | -122.5525 | -0.073242 | -122.5021 | 0.16479 | 0.004577 | 0.19684 | 0.13733 | 2.4261 | 2.3346 | 0.18768 | 0.13733 | -0.073242 | 2.4261 | 2.3346 | 0.13733 | 0.13733 | 0.18768 | -120.52 | -122.7631
803.6562 | 122.6898 | -2.2568 | 120.4376 | 0.18391 | 0.0876 | 0.040215 | 0.25754 | -0.10671 | -0.086501 | 0.18026 | 0.027466 | 0.10071 | -0.15106 | -2.1286 | -2.1286 | -2.1194 | -2.2568 | -2.0599 | -2.0828 | -2.33 | 2.1057 | -120.3369 | 2.2842 | 0.12817 | -122.5662 | -0.073242 | -122.5204 | 0.17853 | 0 | 0.19684 | 0.12817 | 2.3575 | 2.2842 | 0.17395 | 0.13733 | -0.073242 | 2.3575 | 2.2842 | 0.13733 | 0.12817 | 0.17395 | -120.5887 | -122.7676
804.6562 | 122.6852 | -2.1973 | 120.4926 | -0.014452 | 0.080123 | 0.027398 | 0.26288 | -0.10457 | -0.079024 | 0.18453 | 0.032043 | 0.12817 | -0.13733 | -2.0645 | -2.0691 | -2.0508 | -2.211 | -1.9958 | -2.0187 | -2.2614 | 2.0599 | -120.3644 | 2.2293 | 0.13275 | -122.5616 | -0.064087 | -122.5113 | 0.16937 | -0.013733 | 0.20142 | 0.12817 | 2.3254 | 2.2293 | 0.17853 | 0.14648 | -0.064087 | 2.3254 | 2.2293 | 0.14648 | 0.12817 | 0.17853 | -120.6299 | -122.7539
805.7188 | 122.7859 | -2.1194 | 120.52 | 0.50435 | 0.075851 | 0.024194 | 0.24686 | -0.11098 | -0.072616 | 0.1824 | 0.068665 | 0.082397 | -0.12817 | -2.1423 | -2.1149 | -2.1194 | -2.0416 | -2.0508 | -1.9501 | -2.2568 | 1.9913 | -120.4376 | 2.1881 | -0.022888 | -122.6349 | -0.13733 | -122.4701 | 0.19684 | 0.07782 | 0.068665 | 0.004578 | 2.2018 | 2.1881 | 0.16937 | 0 | -0.13733 | 2.2018 | 2.1881 | 0 | 0.004578 | 0.16937 | -120.6482 | -122.7768
806.6562 | 122.6944 | -2.0874 | 120.7077 | 0.12288 | 0.080123 | 0.040215 | 0.2554 | -0.11952 | -0.079024 | 0.1856 | 0.045776 | 0.10986 | -0.15564 | -2.0142 | -2.0096 | -2.005 | -2.1011 | -1.9409 | -1.918 | -2.179 | 1.9318 | -120.5978 | 2.1332 | 0.073242 | -122.7173 | -0.091553 | -122.6257 | 0.20142 | -0.013733 | 0.14648 | 0.077819 | 2.1973 | 2.1332 | 0.16937 | 0.082397 | -0.091553 | 2.1973 | 2.1332 | 0.082397 | 0.077819 | 0.16937 | -120.8633 | -122.8867
807.7188 | 122.7997 | -2.0645 | 120.5566 | 0.62642 | 0.089736 | 0.022057 | 0.25006 | -0.11739 | -0.097182 | 0.18453 | 0.064087 | 0.054932 | -0.11902 | -2.1103 | -2.0462 | -2.0737 | -1.9867 | -2.0187 | -1.8997 | -2.211 | 1.9455 | -120.5017 | 2.1286 | -0.045777 | -122.6028 | -0.14649 | -122.4564 | 0.18311 | 0.07782 | 0.045776 | 0.01831 | 2.1194 | 2.1286 | 0.1648 | -0.009155 | -0.14649 | 2.1194 | 2.1286 | -0.009155 | 0.01831 | 0.1648 | -120.6757 | -122.7676
808.6562 | 122.644 | -2.1194 | 120.6207 | 0.30598 | 0.092941 | 0.030602 | 0.25434 | -0.10778 | -0.074752 | 0.18453 | -0.036621 | 0.082397 | -0.15106 | -1.9089 | -1.9089 | -1.8906 | -2.1561 | -1.8356 | -1.9363 | -2.1561 | 1.9684 | -120.5383 | 2.0828 | 0.21057 | -122.5296 | -0.036621 | -122.5571 | 0.11444 | -0.036621 | 0.28381 | 0.21057 | 2.2018 | 2.0828 | 0.18311 | 0.22888 | -0.036621 | 2.2018 | 2.0828 | 0.22888 | 0.21057 | 0.18311 | -120.7718 | -122.7768
809.7031 | 122.7264 | -2.1286 | 120.575 | -0.16704 | 0.081191 | 0.0071045 | 0.26395 | -0.1003 | -0.087569 | 0.19094 | -0.022888 | 0.086975 | -0.16479 | -1.9775 | -1.9867 | -1.9775 | -2.1515 | -1.9089 | -1.9455 | -2.1927 | 1.9638 | -120.488 | 2.1057 | 0.15106 | -122.5616 | -0.064087 | -122.5204 | 0.14191 | -0.022888 | 0.21973 | 0.14191 | 2.2156 | 2.1057 | 0.18311 | 0.15106 | -0.064087 | 2.2156 | 2.1057 | 0.15106 | 0.14191 | 0.18311 | -120.7397 | -122.7676
810.6562 | 122.6212 | -2.0782 | 120.6436 | 0.42805 | 0.080123 | 0.039147 | 0.26395 | -0.11632 | -0.087569 | 0.1856 | -0.013733 | 0.10986 | -0.16022 | -1.9272 | -1.9272 | -1.9272 | -2.1332 | -1.8402 | -1.9226 | -2.1561 | 1.918 | -120.5338 | 2.0645 | 0.15106 | -122.5708 | -0.07782 | -122.5662 | 0.14648 | -0.054932 | 0.23804 | 0.15106 | 2.1881 | 2.0645 | 0.15564 | 0.15106 | -0.07782 | 2.1881 | 2.0645 | 0.15106 | 0.15106 | 0.15564 | -120.8038 | -122.7997
811.6562 | 122.6852 | -2.0782 | 120.6573 | 0.48909 | 0.080123 | 0.033807 | 0.23938 | -0.11205 | -0.088637 | 0.17919 | -0.022888 | 0.10529 | -0.16479 | -1.9409 | -1.9043 | -1.9272 | -2.1286 | -1.8219 | -1.9135 | -2.1378 | 1.9135 | -120.5521 | 2.0554 | 0.13733 | -122.5616 | -0.059509 | -122.5708 | 0.14191 | -0.050354 | 0.25635 | 0.17395 | 2.1835 | 2.0554 | 0.1648 | 0.15106 | -0.059509 | 2.1835 | 2.0554 | 0.15106 | 0.17395 | 0.1648 | -120.8221 | -122.7951
812.7188 | 122.6898 | -2.1011 | 120.6436 | -0.27385 | 0.080123 | 0.027398 | 0.2554 | -0.11632 | -0.09291 | 0.18774 | -0.054932 | 0.09613 | -0.16479 | -1.9501 | -1.9547 | -1.9135 | -2.1378 | -1.8402 | -1.9043 | -2.1378 | 1.9363 | -120.5475 | 2.0462 | 0.15106 | -122.5983 | -0.036621 | -122.5479 | 0.10986 | -0.036621 | 0.26093 | 0.14648 | 2.1973 | 2.0462 | 0.19684 | 0.18768 | -0.036621 | 2.1973 | 2.0462 | 0.18768 | 0.14648 | 0.19684 | -120.8084 | -122.7814
813.6562 | 122.7585 | -1.9958 | 120.7581 | 0.38228 | 0.092941 | 0.02633 | 0.26395 | -0.10778 | -0.076888 | 0.1856 | -0.027466 | 0.11444 | -0.16937 | -1.8585 | -1.8539 | -1.8448 | -1.9638 | -1.6022 | -1.8631 | -2.0462 | 1.8265 | -120.6436 | 1.9684 | 0.13733 | -122.612 | -0.050354 | -122.6212 | 0.14191 | 0.032044 | 0.39368 | 0.14191 | 2.1103 | 1.9684 | 0.13275 | 0.15106 | -0.050354 | 2.1103 | 1.9684 | 0.15106 | 0.14191 | 0.13275 | -120.9274 | -122.8043
814.6562 | 122.7402 | -1.9913 | 120.694 | 0.55012 | 0.079055 | 0.034875 | 0.26074 | -0.11952 | -0.089705 | 0.18774 | -0.013733 | 0.086975 | -0.13733 | -1.918 | -1.9089 | -1.8951 | -1.973 | -1.8265 | -1.8448 | -2.0782 | 1.8539 | -120.607 | 1.9775 | 0.073242 | -122.6028 | -0.086975 | -122.5388 | 0.1236 | 0.018311 | 0.1648 | 0.082397 | 2.0782 | 1.9775 | 0.14648 | 0.09613 | -0.086975 | 2.0782 | 1.9775 | 0.09613 | 0.082397 | 0.14648 | -120.8313 | -122.7722
815.6562 | 122.7631 | -1.9867 | 120.6299 | 0.61116 | 0.080123 | 0.024194 | 0.23938 | -0.10991 | -0.076888 | 0.18347 | 0.068665 | 0.059509 | -0.10986 | -1.9913 | -1.9547 | -1.9547 | -1.8631 | -1.9089 | -1.7853 | -2.1149 | 1.8768 | -120.5704 | 2.0554 | -0.004578 | -122.5845 | -0.12817 | -122.4152 | 0.17853 | 0.1236 | 0.077819 | 0.032043 | 2.0462 | 2.0554 | 0.20142 | 0.032043 | -0.12817 | 2.0462 | 2.0554 | 0.032043 | 0.032043 | 0.20142 | -120.7397 | -122.7448
816.6562 | 122.8134 | -1.973 | 120.7031 | 0.48909 | 0.071578 | 0.027398 | 0.24686 | -0.12914 | -0.10039 | 0.18026 | 0.11902 | 0.041199 | -0.11444 | -2.0279 | -1.9821 | -1.9913 | -1.8631 | -1.918 | -1.8127 | -2.1057 | 1.8585 | -120.6619 | 2.092 | -0.054932 | -122.6852 | -0.13275 | -122.5159 | 0.23346 | 0.10986 | 0.054931 | -0.009156 | 2.0142 | 2.092 | 0.16022 | -0.018311 | -0.13275 | 2.0142 | 2.092 | -0.018311 | -0.009156 | 0.16022 | -120.8176 | -122.8088
817.6719 | 122.7768 | -1.9455 | 120.7581 | -0.21282 | 0.066238 | 0.035943 | 0.25006 | -0.12059 | -0.11427 | 0.18881 | 0.041199 | 0.059509 | -0.10529 | -1.9409 | -1.9318 | -1.8997 | -1.9272 | -1.8448 | -1.7578 | -2.0599 | 1.8402 | -120.6985 | 1.9867 | 0.004578 | -122.6898 | -0.11444 | -122.5159 | 0.14649 | 0.018311 | 0.10071 | 0.013733 | 2.005 | 1.9867 | 0.18768 | 0.045777 | -0.11444 | 2.005 | 1.9867 | 0.045777 | 0.013733 | 0.18768 | -120.8633 | -122.818
818.6562 | 122.7768 | -1.9455 | 120.7397 | 0.42805 | 0.068374 | 0.016717 | 0.24579 | -0.12059 | -0.10466 | 0.18133 | 0.045776 | 0.041199 | -0.09613 | -1.9775 | -1.9547 | -1.9592 | -1.8814 | -1.886 | -1.7899 | -2.092 | 1.8494 | -120.6985 | 1.9913 | -0.032043 | -122.6944 | -0.14648 | -122.5296 | 0.14191 | 0.064087 | 0.05951 | -0.009155 | 1.9867 | 1.9913 | 0.15564 | -0.013733 | -0.14648 | 1.9867 | 1.9913 | -0.013733 | -0.009155 | 0.15564 | -120.8359 | -122.8317
819.7031 | 122.7951 | -1.9135 | 120.7626 | 0.47383 | 0.069442 | 0.018853 | 0.25006 | -0.12593 | -0.093978 | 0.17278 | 0.064087 | 0.027466 | -0.11902 | -1.9363 | -1.9272 | -1.9272 | -1.8448 | -1.8494 | -1.7578 | -2.0462 | 1.7944 | -120.7352 | 1.9775 | -0.022888 | -122.6898 | -0.13275 | -122.5204 | 0.18311 | 0.068664 | 0.064087 | -0.013733 | 1.9409 | 1.9775 | 0.15564 | -0.013733 | -0.13275 | 1.9409 | 1.9775 | -0.013733 | -0.013733 | 0.15564 | -120.8817 | -122.8088
820.6562 | 122.8088 | -1.918 | 120.7764 | -0.075488 | 0.066238 | 0.037011 | 0.26074 | -0.13341 | -0.10359 | 0.17919 | 0.045776 | 0.013733 | -0.15106 | -1.9547 | -1.9363 | -1.9501 | -1.8402 | -1.8677 | -1.7715 | -2.0691 | 1.767 | -120.7626 | 1.9638 | -0.036621 | -122.7127 | -0.15106 | -122.5479 | 0.19684 | 0.07782 | 0.050354 | -0.01831 | 1.9318 | 1.9638 | 0.14648 | -0.032043 | -0.15106 | 1.9318 | 1.9638 | -0.032043 | -0.01831 | 0.14648 | -120.9274 | -122.8455
821.6562 | 122.7814 | -1.8951 | 120.7672 | 0.39753 | 0.060897 | 0.022057 | 0.25006 | -0.127 | -0.10573 | 0.18774 | 0.018311 | 0.050354 | -0.11444 | -1.8906 | -1.8723 | -1.8814 | -1.886 | -1.8082 | -1.7487 | -2.0142 | 1.7807 | -120.7169 | 1.9135 | 0.004578 | -122.6395 | -0.11902 | -122.5159 | 0.13275 | 0.009156 | 0.086975 | 0.022889 | 1.9455 | 1.9135 | 0.14649 | 0.013733 | -0.11902 | 1.9455 | 1.9135 | 0.013733 | 0.022889 | 0.14649 | -120.8817 | -122.7814
822.7188 | 122.7997 | -1.8677 | 120.845 | -3.1578 | 0.060897 | 0.033807 | 0.24793 | -0.12487 | -0.097182 | 0.19308 | -0.064087 | 0.045776 | -0.13275 | -1.8997 | -1.9043 | -1.8768 | -1.7899 | -1.799 | -1.6937 | -1.9958 | 1.7349 | -120.7993 | 1.8036 | -0.032043 | -122.7493 | -0.12817 | -122.5388 | 0.068664 | 0.07782 | 0.068665 | -0.036621 | 1.9135 | 1.8036 | 0.17395 | -0.009155 | -0.12817 | 1.9135 | 1.8036 | -0.009155 | -0.036621 | 0.17395 | -120.9778 | -122.8409
823.6562 | 122.7859 | -1.8585 | 120.8633 | 0.092359 | 0.061965 | 0.02633 | 0.24686 | -0.12487 | -0.11214 | 0.18774 | -0.082397 | 0.032043 | -0.16479 | -1.8402 | -1.8311 | -1.8173 | -1.8219 | -1.7212 | -1.7303 | -1.973 | 1.6937 | -120.8313 | 1.7761 | 0.018311 | -122.6944 | -0.11444 | -122.5937 | 0.082398 | 0.036622 | 0.13733 | 0.027466 | 1.8906 | 1.7761 | 0.12817 | 0.041199 | -0.11444 | 1.8906 | 1.7761 | 0.041199 | 0.027466 | 0.12817 | -121.0281 | -122.8363
824.6562 | 122.8134 | -1.8036 | 120.8908 | 0.21443 | 0.052352 | 0.038079 | 0.24686 | -0.12807 | -0.10359 | 0.18133 | -0.032043 | 0.013733 | -0.16937 | -1.8173 | -1.8082 | -1.7944 | -1.7853 | -1.7029 | -1.6479 | -1.9226 | 1.6342 | -120.8771 | 1.7715 | -0.013733 | -122.699 | -0.11902 | -122.5388 | 0.13733 | 0.018311 | 0.10071 | -0.004578 | 1.8173 | 1.7715 | 0.15564 | 0.009155 | -0.11902 | 1.8173 | 1.7715 | 0.009155 | -0.004578 | 0.15564 | -121.0602 | -122.8134
825.7188 | 122.8134 | -1.7532 | 120.9366 | 0.18391 | 0.07051 | 0.014581 | 0.25434 | -0.13234 | -0.11534 | 0.18347 | 0.004578 | 0.045776 | -0.1236 | -1.7624 | -1.7624 | -1.7578 | -1.7441 | -1.6617 | -1.593 | -1.8814 | 1.6296 | -120.8908 | 1.7578 | -0.009155 | -122.699 | -0.12817 | -122.5296 | 0.12817 | 0.009155 | 0.091553 | -0.009155 | 1.799 | 1.7578 | 0.16022 | -0.004577 | -0.12817 | 1.799 | 1.7578 | -0.004577 | -0.009155 | 0.16022 | -121.0602 | -122.818
826.6562 | 122.6532 | -1.7807 | 120.8359 | 0.29072 | 0.058761 | 0.032739 | 0.24899 | -0.12593 | -0.1068 | 0.17706 | 0 | 0.059509 | -0.13733 | -1.7395 | -1.7441 | -1.7303 | -1.7624 | -1.6617 | -1.6113 | -1.886 | 1.6434 | -120.7764 | 1.7807 | 0.041199 | -122.58 | -0.10528 | -122.4472 | 0.13733 | 0.018311 | 0.11902 | 0.036621 | 1.8402 | 1.7807 | 0.16937 | 0.050354 | -0.10528 | 1.8402 | 1.7807 | 0.050354 | 0.036621 | 0.16937 | -120.9732 | -122.7219
827.6719 | 122.7448 | -1.7807 | 120.9869 | 0.00080561 | 0.071578 | 0.0049685 | 0.27783 | -0.1238 | -0.10039 | 0.18667 | 0.041199 | 0.091553 | -0.14648 | -1.6479 | -1.7075 | -1.6846 | -1.7624 | -1.6022 | -1.6113 | -1.8402 | 1.6342 | -120.8954 | 1.8219 | 0.13275 | -122.6944 | -0.059509 | -122.5983 | 0.18768 | 0.018311 | 0.17853 | 0.073243 | 1.8723 | 1.8219 | 0.16937 | 0.096131 | -0.059509 | 1.8723 | 1.8219 | 0.096131 | 0.073243 | 0.16937 | -121.1334 | -122.8271
828.7031 | 122.8043 | -1.6846 | 120.9732 | 0.47383 | 0.074783 | 0.017785 | 0.25754 | -0.11846 | -0.10252 | 0.18133 | 0.054932 | 0.041199 | -0.11444 | -1.7258 | -1.7212 | -1.7212 | -1.6479 | -1.6525 | -1.561 | -1.8173 | 1.5701 | -120.932 | 1.7395 | -0.041199 | -122.6944 | -0.13275 | -122.5342 | 0.16937 | 0.036621 | 0.032043 | -0.036621 | 1.7258 | 1.7395 | 0.1236 | -0.036621 | -0.13275 | 1.7258 | 1.7395 | -0.036621 | -0.036621 | 0.1236 | -121.0876 | -122.7905
829.6562 | 122.8729 | -1.6937 | 120.9915 | 0.016065 | 0.07051 | 0.016717 | 0.25006 | -0.13448 | -0.10893 | 0.17813 | 0.059509 | 0.059509 | -0.11444 | -1.7807 | -1.7532 | -1.7487 | -1.6251 | -1.6708 | -1.5472 | -1.8356 | 1.5793 | -120.932 | 1.7532 | -0.086975 | -122.7448 | -0.14191 | -122.5388 | 0.17395 | 0.068665 | 0.022889 | -0.059509 | 1.7532 | 1.7532 | 0.14648 | -0.054931 | -0.14191 | 1.7532 | 1.7532 | -0.054931 | -0.059509 | 0.14648 | -121.106 | -122.8271
830.6562 | 122.8592 | -1.6937 | 121.0144 | 0.092359 | 0.059829 | 0.015649 | 0.25861 | -0.11846 | -0.11427 | 0.18347 | 0.032043 | 0.073242 | -0.10986 | -1.6983 | -1.7075 | -1.6983 | -1.6342 | -1.6342 | -1.5244 | -1.8219 | 1.5839 | -120.9412 | 1.7258 | -0.004577 | -122.7219 | -0.12817 | -122.5388 | 0.14191 | 0.05951 | 0.05951 | -0.013732 | 1.767 | 1.7258 | 0.16937 | -0.004577 | -0.12817 | 1.767 | 1.7258 | -0.004577 | -0.013732 | 0.16937 | -121.1243 | -122.8363
831.7188 | 122.9462 | -1.6663 | 121.0052 | -0.12126 | 0.058761 | -0.00037251 | 0.24472 | -0.14089 | -0.10466 | 0.18453 | 0.07782 | 0.041199 | -0.11902 | -1.712 | -1.7258 | -1.7029 | -1.6159 | -1.6663 | -1.5244 | -1.8265 | 1.5472 | -120.9641 | 1.7441 | -0.045776 | -122.731 | -0.16022 | -122.5296 | 0.19684 | 0.050354 | 0 | -0.059509 | 1.7075 | 1.7441 | 0.14191 | -0.036621 | -0.16022 | 1.7075 | 1.7441 | -0.036621 | -0.059509 | 0.14191 | -121.1243 | -122.8317
832.6562 | 122.85 | -1.68 | 121.0419 | -0.24333 | 0.05342 | 0.017785 | 0.25434 | -0.13127 | -0.1132 | 0.18347 | 0.054932 | 0.045776 | -0.10986 | -1.6983 | -1.6937 | -1.7899 | -1.8539 | -1.6571 | -1.4877 | -1.8356 | 1.5701 | -120.9961 | 1.7349 | -0.01831 | -122.7356 | -0.15564 | -122.5296 | 0.16479 | -0.17395 | 0.022889 | -0.013733 | 1.7258 | 1.7349 | 0.19226 | -0.10986 | -0.15564 | 1.7258 | 1.7349 | -0.10986 | -0.013733 | 0.19226 | -121.1517 | -122.8775
833.6562 | 122.8592 | -1.6342 | 121.0464 | -0.12126 | 0.06517 | 0.0081725 | 0.2554 | -0.13234 | -0.10252 | 0.16638 | 0.082397 | 0.054932 | -0.11444 | -1.6846 | -1.68 | -1.6754 | -1.5564 | -1.6113 | -1.4786 | -1.7853 | 1.5198 | -120.9915 | 1.7166 | -0.050354 | -122.7264 | -0.15106 | -122.525 | 0.19684 | 0.07782 | 0.022888 | -0.045777 | 1.6891 | 1.7166 | 0.15564 | -0.041199 | -0.15106 | 1.6891 | 1.7166 | -0.041199 | -0.045777 | 0.15564 | -121.1609 | -122.8317
834.6562 | 122.8592 | -1.6342 | 121.0464 | 0.031324 | 0.067306 | 0.013512 | 0.25647 | -0.12807 | -0.12282 | 0.17706 | 0.086975 | 0.050354 | -0.09613 | -1.6983 | -1.7029 | -1.68 | -1.5747 | -1.6296 | -1.474 | -1.7899 | 1.5381 | -120.9961 | 1.7212 | -0.064087 | -122.7493 | -0.15564 | -122.5204 | 0.1831 | 0.059509 | 0.004577 | -0.068665 | 1.6846 | 1.7212 | 0.16022 | -0.045777 | -0.15564 | 1.6846 | 1.7212 | -0.045777 | -0.068665 | 0.16022 | -121.1426 | -122.8363
835.6562 | 122.7814 | -1.6388 | 121.1243 | -0.27385 | 0.071578 | -0.0025085 | 0.25327 | -0.12487 | -0.10573 | 0.18667 | 0.041199 | 0.068665 | -0.15106 | -1.5839 | -1.6159 | -1.5839 | -1.6342 | -1.5106 | -1.4603 | -1.7532 | 1.4877 | -121.0556 | 1.68 | 0.054932 | -122.7402 | -0.11444 | -122.5845 | 0.19226 | 0.004578 | 0.12817 | 0.022888 | 1.7075 | 1.68 | 0.17853 | 0.054932 | -0.11444 | 1.7075 | 1.68 | 0.054932 | 0.022888 | 0.17853 | -121.2753 | -122.8775
836.7188 | 122.8638 | -1.6251 | 121.0876 | -1.3877 | 0.075851 | -0.018531 | 0.26502 | -0.13127 | -0.11534 | 0.18347 | 0.027466 | 0.032043 | -0.1236 | -1.6296 | -1.6251 | -1.6296 | -1.561 | -1.5793 | -1.4465 | -1.7349 | 1.5015 | -121.0556 | 1.6525 | -0.004578 | -122.7127 | -0.10986 | -122.5342 | 0.15106 | 0.064087 | 0.045776 | 0 | 1.6571 | 1.6525 | 0.17853 | -0.004578 | -0.10986 | 1.6571 | 1.6525 | -0.004578 | 0 | 0.17853 | -121.2112 | -122.8226
837.6562 | 122.7631 | -1.6205 | 121.1563 | -0.38066 | 0.058761 | 0.0060365 | 0.27143 | -0.11952 | -0.10252 | 0.18026 | 0.036621 | 0.086975 | -0.13275 | -1.5381 | -1.5564 | -1.5244 | -1.6296 | -1.4694 | -1.4511 | -1.712 | 1.4877 | -121.0693 | 1.6571 | 0.082397 | -122.7127 | -0.091553 | -122.6074 | 0.16937 | -0.009156 | 0.15106 | 0.064087 | 1.7075 | 1.6571 | 0.16937 | 0.09613 | -0.091553 | 1.7075 | 1.6571 | 0.09613 | 0.064087 | 0.16937 | -121.2891 | -122.8683
838.7188 | 122.7676 | -1.6159 | 121.1517 | -0.1823 | 0.067306 | 0.0081725 | 0.26822 | -0.13234 | -0.099318 | 0.18667 | 0.027466 | 0.054932 | -0.11902 | -1.5335 | -1.5381 | -1.5198 | -1.6342 | -1.4465 | -1.4511 | -1.712 | 1.4969 | -121.0968 | 1.6434 | 0.082398 | -122.6898 | -0.09613 | -122.6028 | 0.14649 | -0.01831 | 0.16937 | 0.07782 | 1.6708 | 1.6434 | 0.1648 | 0.096131 | -0.09613 | 1.6708 | 1.6434 | 0.096131 | 0.07782 | 0.1648 | -121.2708 | -122.8638
839.6562 | 122.7585 | -1.6205 | 121.1746 | -0.19756 | 0.057693 | 0.027398 | 0.26288 | -0.12914 | -0.11107 | 0.18667 | 0.013733 | 0.064087 | -0.12817 | -1.4923 | -1.506 | -1.506 | -1.6205 | -1.4282 | -1.4328 | -1.6983 | 1.4923 | -121.1105 | 1.6342 | 0.12817 | -122.6807 | -0.07782 | -122.6074 | 0.14191 | 0 | 0.19226 | 0.11444 | 1.6846 | 1.6342 | 0.18768 | 0.11444 | -0.07782 | 1.6846 | 1.6342 | 0.11444 | 0.11444 | 0.18768 | -121.3028 | -122.8729
840.6562 | 122.8409 | -1.5152 | 121.1975 | -0.28911 | 0.04808 | 0.010308 | 0.2554 | -0.12166 | -0.10359 | 0.17278 | 0.068665 | 0.054932 | -0.11902 | -1.5427 | -1.5472 | -1.5198 | -1.4832 | -1.4877 | -1.3824 | -1.6846 | 1.3962 | -121.1426 | 1.5839 | -0.027466 | -122.7448 | -0.16937 | -122.58 | 0.18768 | 0.032044 | 0.027466 | -0.032043 | 1.5701 | 1.5839 | 0.13275 | -0.004577 | -0.16937 | 1.5701 | 1.5839 | -0.004577 | -0.032043 | 0.13275 | -121.3165 | -122.8821
841.7031 | 122.8455 | -1.5152 | 121.2204 | -0.25859 | 0.066238 | 0.022057 | 0.25861 | -0.12487 | -0.11961 | 0.18987 | -0.022888 | 0.022888 | -0.16937 | -1.506 | -1.4923 | -1.4877 | -1.4969 | -1.4374 | -1.3824 | -1.6205 | 1.3458 | -121.1975 | 1.4923 | 0.009156 | -122.7127 | -0.10528 | -122.6028 | 0.14649 | 0.018311 | 0.07782 | 0.022888 | 1.5381 | 1.4923 | 0.13275 | 0.027466 | -0.10528 | 1.5381 | 1.4923 | 0.027466 | 0.022888 | 0.13275 | -121.3898 | -122.8409
842.6562 | 122.6761 | -1.5106 | 121.3028 | -0.27385 | 0.069442 | 0.02633 | 0.26822 | -0.12059 | -0.10359 | 0.18774 | -0.032043 | 0.082397 | -0.15564 | -1.3641 | -1.4053 | -1.3779 | -1.6022 | -1.2314 | -1.3916 | -1.5793 | 1.355 | -121.2204 | 1.4786 | 0.14648 | -122.7081 | -0.068665 | -122.6944 | 0.1236 | -0.091553 | 0.27924 | 0.10529 | 1.593 | 1.4786 | 0.11902 | 0.13275 | -0.068665 | 1.593 | 1.4786 | 0.13275 | 0.10529 | 0.11902 | -121.4584 | -122.8821
843.6562 | 122.7081 | -1.5244 | 121.3074 | -0.25859 | 0.083328 | 0.019921 | 0.26288 | -0.11952 | -0.09825 | 0.17599 | -0.032043 | 0.10529 | -0.15106 | -1.3733 | -1.387 | -1.3733 | -1.6022 | -1.2634 | -1.387 | -1.593 | 1.3733 | -121.2021 | 1.4923 | 0.15106 | -122.6944 | -0.068665 | -122.6944 | 0.11902 | -0.07782 | 0.26093 | 0.13733 | 1.6296 | 1.4923 | 0.13733 | 0.15106 | -0.068665 | 1.6296 | 1.4923 | 0.15106 | 0.13733 | 0.13733 | -121.4584 | -122.9004
844.7031 | 122.8271 | -1.4877 | 121.257 | 0.50435 | 0.07051 | 0.0028315 | 0.24472 | -0.12914 | -0.11107 | 0.1856 | -0.022888 | 0.018311 | -0.16479 | -1.4832 | -1.4557 | -1.4648 | -1.4648 | -1.3779 | -1.3596 | -1.5884 | 1.3229 | -121.2387 | 1.4648 | 0.004578 | -122.7127 | -0.10071 | -122.6166 | 0.14191 | 0.022888 | 0.10986 | 0.032044 | 1.506 | 1.4648 | 0.12817 | 0.022888 | -0.10071 | 1.506 | 1.4648 | 0.022888 | 0.032044 | 0.12817 | -121.4218 | -122.8455
845.6562 | 122.7859 | -1.506 | 121.2845 | -0.30437 | 0.069442 | -0.0035765 | 0.25754 | -0.12273 | -0.10146 | 0.17919 | 0.032043 | 0.068665 | -0.12817 | -1.4236 | -1.4236 | -1.387 | -1.5152 | -1.3458 | -1.3412 | -1.5747 | 1.3779 | -121.2158 | 1.5381 | 0.082397 | -122.7081 | -0.068665 | -122.6257 | 0.16022 | -0.009156 | 0.16022 | 0.082397 | 1.5747 | 1.5381 | 0.16479 | 0.11902 | -0.068665 | 1.5747 | 1.5381 | 0.11902 | 0.082397 | 0.16479 | -121.4127 | -122.8592
846.6562 | 122.7859 | -1.4877 | 121.2753 | -0.27385 | 0.064101 | 0.0060365 | 0.26929 | -0.11632 | -0.1132 | 0.1856 | 0.036621 | 0.068665 | -0.11444 | -1.4328 | -1.4328 | -1.4053 | -1.4923 | -1.3412 | -1.3321 | -1.5884 | 1.3733 | -121.2067 | 1.5244 | 0.054932 | -122.7081 | -0.10071 | -122.6074 | 0.15106 | -0.004578 | 0.14648 | 0.054932 | 1.5564 | 1.5244 | 0.15564 | 0.082398 | -0.10071 | 1.5564 | 1.5244 | 0.082398 | 0.054932 | 0.15564 | -121.3898 | -122.8638
847.7031 | 122.8683 | -1.4328 | 121.2936 | 0.046583 | 0.060897 | 0.0028315 | 0.25327 | -0.12593 | -0.11854 | 0.18347 | 0.022888 | 0.036621 | -0.10529 | -1.4557 | -1.4465 | -1.4282 | -1.3916 | -1.3733 | -1.3046 | -1.5793 | 1.3275 | -121.257 | 1.4557 | -0.022888 | -122.7402 | -0.14648 | -122.5983 | 0.12817 | 0.041198 | 0.059509 | -0.013733 | 1.4694 | 1.4557 | 0.12817 | 0.004577 | -0.14648 | 1.4694 | 1.4557 | 0.004577 | -0.013733 | 0.12817 | -121.3989 | -122.8729
848.6562 | 122.7631 | -1.4786 | 121.3257 | -0.30437 | 0.066238 | 0.0038995 | 0.27356 | -0.11739 | -0.10146 | 0.18347 | -0.032043 | 0.082397 | -0.15106 | -1.3275 | -1.3504 | -1.3046 | -1.5427 | -1.2634 | -1.3229 | -1.5335 | 1.3275 | -121.2433 | 1.4465 | 0.15106 | -122.6761 | -0.054931 | -122.6486 | 0.11902 | -0.064087 | 0.21515 | 0.12817 | 1.561 | 1.4465 | 0.15564 | 0.17395 | -0.054931 | 1.561 | 1.4465 | 0.17395 | 0.12817 | 0.15564 | -121.4767 | -122.8592
849.6562 | 122.7448 | -1.506 | 121.3394 | 1.2825 | 0.085464 | 0.010308 | 0.26395 | -0.11739 | -0.099318 | 0.1824 | -0.009155 | 0.13275 | -0.11902 | -1.3138 | -1.3412 | -1.2955 | -1.5427 | -1.236 | -1.3092 | -1.5427 | 1.387 | -121.2067 | 1.4969 | 0.19226 | -122.6807 | -0.036622 | -122.6486 | 0.10986 | -0.036622 | 0.27008 | 0.16479 | 1.6388 | 1.4969 | 0.19684 | 0.21057 | -0.036622 | 1.6388 | 1.4969 | 0.21057 | 0.16479 | 0.19684 | -121.4584 | -122.8821
850.6562 | 122.7631 | -1.474 | 121.3348 | -4.3174 | 0.080123 | 0.042352 | 0.27143 | -0.12059 | -0.095046 | 0.1856 | 0 | 0.12817 | -0.11902 | -1.2817 | -1.3275 | -1.3 | -1.5198 | -1.2177 | -1.2909 | -1.5152 | 1.355 | -121.2067 | 1.474 | 0.19226 | -122.6624 | -0.041199 | -122.6257 | 0.11902 | -0.045776 | 0.25635 | 0.14648 | 1.6022 | 1.474 | 0.18311 | 0.17395 | -0.041199 | 1.6022 | 1.474 | 0.17395 | 0.14648 | 0.18311 | -121.4539 | -122.85
851.6562 | 122.7768 | -1.4557 | 121.3623 | -0.28911 | 0.069442 | -0.0067815 | 0.27036 | -0.10884 | -0.10252 | 0.18774 | 0.16479 | 0.13275 | -0.10986 | -1.2726 | -1.2909 | -1.2817 | -1.5152 | -1.2314 | -1.2634 | -1.5015 | 1.3458 | -121.2296 | 1.6205 | 0.18311 | -122.6532 | -0.045777 | -122.6257 | 0.27466 | -0.05951 | 0.2243 | 0.16479 | 1.5884 | 1.6205 | 0.19226 | 0.17395 | -0.045777 | 1.5884 | 1.6205 | 0.17395 | 0.16479 | 0.19226 | -121.4722 | -122.8638
852.7031 | 122.8088 | -1.442 | 121.4493 | -0.27385 | 0.080123 | -0.0025085 | 0.26288 | -0.11205 | -0.11641 | 0.19522 | -0.041199 | 0.082397 | -0.15106 | -1.2863 | -1.2955 | -1.2726 | -1.4969 | -1.1948 | -1.2909 | -1.4786 | 1.2909 | -121.3669 | 1.4008 | 0.15564 | -122.7448 | -0.036621 | -122.7402 | 0.10986 | -0.054931 | 0.24719 | 0.14648 | 1.5244 | 1.4008 | 0.15106 | 0.16937 | -0.036621 | 1.5244 | 1.4008 | 0.16937 | 0.14648 | 0.15106 | -121.6003 | -122.9279
853.6562 | 122.7631 | -1.4282 | 121.3898 | -0.25859 | 0.076919 | 0.019921 | 0.26181 | -0.13021 | -0.10893 | 0.19094 | 0.004578 | 0.086975 | -0.13733 | -1.3046 | -1.2909 | -1.268 | -1.4511 | -1.2085 | -1.2497 | -1.4923 | 1.2909 | -121.3028 | 1.4328 | 0.1236 | -122.6807 | -0.064087 | -122.6395 | 0.14191 | -0.022888 | 0.21973 | 0.13733 | 1.5152 | 1.4328 | 0.17853 | 0.16022 | -0.064087 | 1.5152 | 1.4328 | 0.16022 | 0.13733 | 0.17853 | -121.5271 | -122.8821
854.6562 | 122.7905 | -1.4008 | 121.3989 | -0.22808 | 0.082259 | 0.0060365 | 0.26608 | -0.11205 | -0.10359 | 0.18667 | 0.013733 | 0.082397 | -0.14648 | -1.3 | -1.3092 | -1.2543 | -1.4328 | -1.1993 | -1.2314 | -1.4969 | 1.2543 | -121.3165 | 1.4145 | 0.10071 | -122.7081 | -0.09613 | -122.6303 | 0.16022 | -0.032043 | 0.20142 | 0.091553 | 1.4832 | 1.4145 | 0.16937 | 0.14648 | -0.09613 | 1.4832 | 1.4145 | 0.14648 | 0.091553 | 0.16937 | -121.5454 | -122.8958
855.6562 | 122.7951 | -1.3596 | 121.463 | -0.31963 | 0.082259 | -0.011054 | 0.26074 | -0.11418 | -0.099318 | 0.17813 | -0.036621 | 0.10986 | -0.15106 | -1.2405 | -1.3367 | -1.0117 | -1.3412 | -1.0437 | -1.1948 | -1.4191 | 1.2085 | -121.3531 | 1.3229 | 0.11902 | -122.7997 | -0.059509 | -122.6578 | 0.11444 | 0.01831 | 0.31586 | 0.022888 | 1.4694 | 1.3229 | 0.1648 | 0.3479 | -0.059509 | 1.4694 | 1.3229 | 0.3479 | 0.022888 | 0.1648 | -121.6141 | -122.8821
856.7188 | 122.7997 | -1.3824 | 121.4493 | -0.16704 | 0.076919 | 0.018853 | 0.26502 | -0.11632 | -0.089705 | 0.17599 | -0.013733 | 0.10986 | -0.15106 | -1.2177 | -1.2268 | -1.2177 | -1.4282 | -1.149 | -1.2314 | -1.4557 | 1.2314 | -121.3394 | 1.3687 | 0.1648 | -122.6761 | -0.073242 | -122.6807 | 0.13733 | -0.045777 | 0.23346 | 0.15564 | 1.4923 | 1.3687 | 0.15106 | 0.1648 | -0.073242 | 1.4923 | 1.3687 | 0.1648 | 0.15564 | 0.15106 | -121.6003 | -122.905
857.6562 | 122.7814 | -1.387 | 121.431 | -0.21282 | 0.081191 | 0.019921 | 0.27249 | -0.11098 | -0.093978 | 0.18667 | -0.022888 | 0.10529 | -0.16479 | -1.2222 | -1.2268 | -1.1993 | -1.4282 | -1.149 | -1.2085 | -1.4374 | 1.2222 | -121.3257 | 1.3641 | 0.1648 | -122.6578 | -0.050354 | -122.6395 | 0.14191 | -0.041199 | 0.23804 | 0.16022 | 1.4923 | 1.3641 | 0.17853 | 0.18768 | -0.050354 | 1.4923 | 1.3641 | 0.18768 | 0.16022 | 0.17853 | -121.5958 | -122.8683
858.7188 | 122.8226 | -1.3733 | 121.4584 | -0.16704 | 0.080123 | 0.056237 | 0.26608 | -0.11205 | -0.085433 | 0.18774 | 0.018311 | 0.091553 | -0.14191 | -1.2405 | -1.2634 | -1.236 | -1.3641 | -1.1765 | -1.2039 | -1.4374 | 1.2314 | -121.3669 | 1.3916 | 0.13275 | -122.7219 | -0.064087 | -122.6624 | 0.16022 | 0.009155 | 0.19684 | 0.10986 | 1.4648 | 1.3916 | 0.16937 | 0.13733 | -0.064087 | 1.4648 | 1.3916 | 0.13733 | 0.10986 | 0.16937 | -121.6003 | -122.8958
859.6562 | 122.7905 | -1.3824 | 121.4767 | -0.13652 | 0.084396 | 0.013512 | 0.26929 | -0.11525 | -0.093978 | 0.17492 | -0.022888 | 0.12817 | -0.1236 | -1.1948 | -1.2085 | -1.1765 | -1.4008 | -1.1215 | -1.1948 | -1.4053 | 1.2589 | -121.3486 | 1.3596 | 0.18768 | -122.6852 | -0.022888 | -122.6715 | 0.10071 | -0.018311 | 0.26093 | 0.17395 | 1.5106 | 1.3596 | 0.18768 | 0.20599 | -0.022888 | 1.5106 | 1.3596 | 0.20599 | 0.17395 | 0.18768 | -121.6003 | -122.8821
860.6562 | 122.7814 | -1.3779 | 121.4951 | -0.27385 | 0.079055 | 0.023126 | 0.25006 | -0.11312 | -0.10252 | 0.18347 | -0.041199 | 0.10986 | -0.14648 | -1.2039 | -1.1993 | -1.1627 | -1.387 | -1.0986 | -1.1856 | -1.4008 | 1.2314 | -121.3852 | 1.3367 | 0.17395 | -122.6944 | -0.022888 | -122.6807 | 0.10529 | -0.009155 | 0.27924 | 0.17853 | 1.4877 | 1.3367 | 0.19226 | 0.21515 | -0.022888 | 1.4877 | 1.3367 | 0.21515 | 0.17853 | 0.19226 | -121.6415 | -122.8958
861.7188 | 122.8134 | -1.3458 | 121.4859 | 0.046583 | 0.073715 | 0.014581 | 0.27463 | -0.10778 | -0.096114 | 0.18347 | 0.041199 | 0.07782 | -0.15106 | -1.2177 | -1.2314 | -1.1993 | -1.3138 | -1.1673 | -1.149 | -1.3962 | 1.1948 | -121.4081 | 1.387 | 0.12817 | -122.7173 | -0.050354 | -122.6349 | 0.19226 | 0.032043 | 0.17853 | 0.11444 | 1.4236 | 1.387 | 0.19684 | 0.14648 | -0.050354 | 1.4236 | 1.387 | 0.14648 | 0.11444 | 0.19684 | -121.637 | -122.8821
862.6562 | 122.7814 | -1.3275 | 121.4905 | -2.9289 | 0.07051 | 0.03167 | 0.26608 | -0.12487 | -0.10359 | 0.18987 | 0.018311 | 0.13275 | -0.12817 | -1.1719 | -1.1673 | -1.1536 | -1.3779 | -1.0895 | -1.1398 | -1.3641 | 1.1993 | -121.3577 | 1.3458 | 0.15564 | -122.6578 | -0.036621 | -122.6303 | 0.14649 | -0.050354 | 0.23804 | 0.16022 | 1.4603 | 1.3458 | 0.18768 | 0.17395 | -0.036621 | 1.4603 | 1.3458 | 0.17395 | 0.16022 | 0.18768 | -121.6187 | -122.8546
863.6562 | 122.818 | -1.3412 | 121.5134 | -0.13652 | 0.089736 | 0.0081725 | 0.25968 | -0.11418 | -0.079024 | 0.18347 | -0.009155 | 0.10529 | -0.16022 | -1.1719 | -1.1993 | -1.1627 | -1.3321 | -1.0986 | -1.149 | -1.3916 | 1.181 | -121.4081 | 1.3321 | 0.16937 | -122.7127 | -0.050354 | -122.6624 | 0.15106 | 0.009156 | 0.24262 | 0.14191 | 1.4465 | 1.3321 | 0.19226 | 0.17853 | -0.050354 | 1.4465 | 1.3321 | 0.17853 | 0.14191 | 0.19226 | -121.6736 | -122.905
864.7031 | 122.9004 | -1.2726 | 121.5042 | 0.10762 | 0.066238 | 0.023126 | 0.24259 | -0.12807 | -0.11748 | 0.18026 | -0.004578 | 0.045776 | -0.11902 | -1.2726 | -1.236 | -1.2314 | -1.2222 | -1.1581 | -1.1078 | -1.3596 | 1.1536 | -121.4584 | 1.268 | 0 | -122.7402 | -0.086975 | -122.612 | 0.11444 | 0.050354 | 0.11444 | 0.036621 | 1.3184 | 1.268 | 0.1648 | 0.041199 | -0.086975 | 1.3184 | 1.268 | 0.041199 | 0.036621 | 0.1648 | -121.6232 | -122.8638
865.6562 | 122.8226 | -1.3046 | 121.5408 | -0.12126 | 0.088668 | 0.039147 | 0.25754 | -0.12166 | -0.091842 | 0.19201 | -0.027466 | 0.09613 | -0.15564 | -1.1398 | -1.1719 | -1.1307 | -1.3367 | -1.0666 | -1.1307 | -1.3641 | 1.149 | -121.4447 | 1.2772 | 0.16479 | -122.7127 | -0.05951 | -122.6715 | 0.12817 | -0.032044 | 0.23804 | 0.13275 | 1.4008 | 1.2772 | 0.17395 | 0.17395 | -0.05951 | 1.4008 | 1.2772 | 0.17395 | 0.13275 | 0.17395 | -121.6965 | -122.905
866.7031 | 122.9233 | -1.2268 | 121.5271 | 0.046583 | 0.063033 | 0.016717 | 0.23618 | -0.12487 | -0.11107 | 0.17919 | 0.045776 | 0.064087 | -0.091553 | -1.2863 | -1.2634 | -1.2177 | -1.149 | -1.1581 | -1.0712 | -1.3596 | 1.1353 | -121.463 | 1.2726 | -0.059509 | -122.7905 | -0.13275 | -122.5983 | 0.13733 | 0.07782 | 0.068665 | -0.036621 | 1.2909 | 1.2726 | 0.15564 | 0.009156 | -0.13275 | 1.2909 | 1.2726 | 0.009156 | -0.036621 | 0.15564 | -121.6187 | -122.8867
867.6562 | 122.8043 | -1.2268 | 121.6232 | -0.28911 | 0.075851 | 0.018853 | 0.26715 | -0.12593 | -0.091842 | 0.18774 | -0.032043 | 0.09613 | -0.15564 | -1.1078 | -1.3046 | -0.90637 | -1.2039 | -0.88348 | -1.0849 | -1.2955 | 1.0712 | -121.5271 | 1.1948 | 0.11902 | -122.9279 | -0.068664 | -122.7081 | 0.1236 | 0.022889 | 0.34332 | -0.077819 | 1.3229 | 1.1948 | 0.14191 | 0.32044 | -0.068664 | 1.3229 | 1.1948 | 0.32044 | -0.077819 | 0.14191 | -121.7789 | -122.9187
868.6562 | 122.7356 | -1.2085 | 121.6599 | -0.28911 | 0.073715 | 0.024194 | 0.2757 | -0.11632 | -0.091842 | 0.18133 | -0.027466 | 0.09613 | -0.16022 | -1.1032 | -1.1169 | -1.0757 | -1.2955 | -0.85602 | -1.0666 | -1.2909 | 1.0483 | -121.5637 | 1.181 | 0.10529 | -122.7768 | -0.082398 | -122.7264 | 0.13275 | -0.086975 | 0.35248 | 0.091553 | 1.3046 | 1.181 | 0.14191 | 0.13275 | -0.082398 | 1.3046 | 1.181 | 0.13275 | 0.091553 | 0.14191 | -121.8201 | -122.9507
869.7188 | 122.85 | -1.2314 | 121.5866 | -0.060229 | 0.088668 | 0.041283 | 0.26502 | -0.12166 | -0.090773 | 0.18133 | 0.032043 | 0.10529 | -0.15106 | -1.1261 | -1.1398 | -1.1169 | -1.2405 | -1.0529 | -1.0849 | -1.3229 | 1.0803 | -121.4813 | 1.2634 | 0.10529 | -122.7264 | -0.091553 | -122.6715 | 0.18311 | -0.009156 | 0.17853 | 0.091552 | 1.3367 | 1.2634 | 0.14648 | 0.11444 | -0.091553 | 1.3367 | 1.2634 | 0.11444 | 0.091552 | 0.14648 | -121.7377 | -122.9095
870.6562 | 122.8363 | -1.2268 | 121.6003 | -0.12126 | 0.074783 | 0.028466 | 0.25113 | -0.11312 | -0.097182 | 0.17919 | 0.022888 | 0.09613 | -0.16022 | -1.1078 | -1.1353 | -1.1032 | -1.2222 | -1.0437 | -1.0712 | -1.3 | 1.0666 | -121.5042 | 1.2497 | 0.11902 | -122.7356 | -0.073242 | -122.6715 | 0.1831 | 0.004578 | 0.18311 | 0.091553 | 1.3229 | 1.2497 | 0.15564 | 0.1236 | -0.073242 | 1.3229 | 1.2497 | 0.1236 | 0.091553 | 0.15564 | -121.7606 | -122.9004
871.6562 | 122.8409 | -1.2177 | 121.6232 | -0.15178 | 0.077987 | 0.017785 | 0.26822 | -0.11312 | -0.089705 | 0.1824 | 0.027466 | 0.10071 | -0.14648 | -1.1032 | -1.1169 | -1.0849 | -1.2131 | -1.03 | -1.062 | -1.2955 | 1.0712 | -121.5225 | 1.2451 | 0.11444 | -122.7402 | -0.07782 | -122.6852 | 0.17395 | 0.004577 | 0.18768 | 0.10071 | 1.3184 | 1.2451 | 0.15564 | 0.13275 | -0.07782 | 1.3184 | 1.2451 | 0.13275 | 0.10071 | 0.15564 | -121.7697 | -122.9187
872.7188 | 122.8455 | -1.149 | 121.6599 | 0.00080561 | 0.080123 | 0.017785 | 0.26288 | -0.12593 | -0.084365 | 0.18881 | 0.045776 | 0.11444 | -0.15564 | -1.0345 | -1.0849 | -1.0757 | -1.1581 | -1.0117 | -0.98419 | -1.2039 | 0.99335 | -121.5454 | 1.1948 | 0.11444 | -122.7448 | -0.054931 | -122.644 | 0.20142 | -0.009155 | 0.13733 | 0.064087 | 1.2634 | 1.1948 | 0.1648 | 0.073242 | -0.054931 | 1.2634 | 1.1948 | 0.073242 | 0.064087 | 0.1648 | -121.8155 | -122.8638
873.6562 | 122.85 | -1.2085 | 121.6507 | -0.15178 | 0.089736 | 0.0071045 | 0.26288 | -0.11739 | -0.086501 | 0.18667 | 0.032043 | 0.10071 | -0.15106 | -1.0941 | -1.1032 | -1.0803 | -1.1948 | -1.0208 | -1.03 | -1.2726 | 1.0574 | -121.55 | 1.2405 | 0.11444 | -122.7539 | -0.064087 | -122.6807 | 0.18311 | 0.013733 | 0.18768 | 0.10529 | 1.3092 | 1.2405 | 0.17853 | 0.12817 | -0.064087 | 1.3092 | 1.2405 | 0.12817 | 0.10529 | 0.17853 | -121.8018 | -122.9233
874.6562 | 122.8455 | -1.2131 | 121.6461 | -0.13652 | 0.085464 | 0.027398 | 0.25006 | -0.11632 | -0.093978 | 0.19522 | -0.022888 | 0.11444 | -0.16479 | -1.0483 | -1.0574 | -1.0345 | -1.2497 | -0.97046 | -1.0345 | -1.268 | 1.0483 | -121.5317 | 1.1902 | 0.1648 | -122.7036 | -0.054931 | -122.6807 | 0.14191 | -0.036621 | 0.24262 | 0.15564 | 1.3275 | 1.1902 | 0.17853 | 0.17853 | -0.054931 | 1.3275 | 1.1902 | 0.17853 | 0.15564 | 0.17853 | -121.8109 | -122.9141
875.7031 | 122.937 | -1.1536 | 121.6232 | -0.13652 | 0.066238 | -0.0014405 | 0.23618 | -0.12914 | -0.11 | 0.19415 | 0.073242 | 0.064087 | -0.10071 | -1.2039 | -1.1673 | -1.1444 | -1.0666 | -1.1032 | -0.97504 | -1.2817 | 1.0529 | -121.5591 | 1.2268 | -0.050354 | -122.7905 | -0.12817 | -122.5983 | 0.17395 | 0.086975 | 0.050354 | -0.013733 | 1.2177 | 1.2268 | 0.17853 | 0.009155 | -0.12817 | 1.2177 | 1.2268 | 0.009155 | -0.013733 | 0.17853 | -121.7239 | -122.905
876.6562 | 122.85 | -1.181 | 121.6507 | -0.029711 | 0.077987 | 0.022057 | 0.26181 | -0.12487 | -0.074752 | 0.18881 | 0.054932 | 0.09613 | -0.13275 | -1.062 | -1.0849 | -1.0574 | -1.1536 | -0.99335 | -1.0071 | -1.2405 | 1.0483 | -121.5546 | 1.236 | 0.11902 | -122.7356 | -0.05951 | -122.6578 | 0.18768 | 0.027466 | 0.18768 | 0.09613 | 1.2772 | 1.236 | 0.17395 | 0.1236 | -0.05951 | 1.2772 | 1.236 | 0.1236 | 0.09613 | 0.17395 | -121.7834 | -122.8912
877.7031 | 122.8958 | -1.1765 | 121.669 | -0.28911 | 0.066238 | 0.013512 | 0.24365 | -0.11846 | -0.11107 | 0.19735 | 0.050354 | 0.054932 | -0.1236 | -1.181 | -1.1444 | -1.1169 | -1.1032 | -1.0391 | -0.99335 | -1.2589 | 1.0529 | -121.6141 | 1.2268 | -0.004577 | -122.8134 | -0.082397 | -122.6624 | 0.17395 | 0.073243 | 0.13733 | 0.032044 | 1.2314 | 1.2268 | 0.18311 | 0.05951 | -0.082397 | 1.2314 | 1.2268 | 0.05951 | 0.032044 | 0.18311 | -121.7926 | -122.9279
878.6562 | 122.8546 | -1.1627 | 121.6827 | -0.014452 | 0.082259 | 0.030602 | 0.26715 | -0.1035 | -0.082229 | 0.18026 | 0.068665 | 0.11444 | -0.10529 | -1.0437 | -1.062 | -1.0345 | -1.1719 | -0.97961 | -1.0025 | -1.2405 | 1.0574 | -121.5683 | 1.2314 | 0.11902 | -122.7448 | -0.07782 | -122.6852 | 0.17395 | -0.009155 | 0.18311 | 0.10071 | 1.2772 | 1.2314 | 0.16022 | 0.12817 | -0.07782 | 1.2772 | 1.2314 | 0.12817 | 0.10071 | 0.16022 | -121.788 | -122.9233
879.6562 | 122.8455 | -1.1719 | 121.7239 | 0.10762 | 0.084396 | 0.014581 | 0.26181 | -0.11098 | -0.089705 | 0.18026 | 0.045776 | 0.11444 | -0.12817 | -1.0391 | -1.0529 | -1.0254 | -1.1536 | -0.96588 | -0.99792 | -1.2268 | 1.0437 | -121.6095 | 1.2177 | 0.13275 | -122.7768 | -0.054932 | -122.7219 | 0.17395 | 0.018311 | 0.20599 | 0.11902 | 1.2863 | 1.2177 | 0.17395 | 0.14648 | -0.054932 | 1.2863 | 1.2177 | 0.14648 | 0.11902 | 0.17395 | -121.8521 | -122.9507
880.6562 | 122.8226 | -1.1581 | 121.6919 | 0.10762 | 0.082259 | 0.016717 | 0.26715 | -0.12059 | -0.080092 | 0.18881 | 0.045776 | 0.09613 | -0.13733 | -1.0208 | -1.0345 | -1.0254 | -1.1627 | -0.9613 | -0.99335 | -1.2222 | 1.0208 | -121.5958 | 1.2039 | 0.13733 | -122.7264 | -0.064087 | -122.6852 | 0.18311 | -0.004578 | 0.19684 | 0.1236 | 1.2543 | 1.2039 | 0.1648 | 0.13275 | -0.064087 | 1.2543 | 1.2039 | 0.13275 | 0.1236 | 0.1648 | -121.8292 | -122.9141
881.6562 | 122.85 | -1.0803 | 121.7606 | 0.061841 | 0.077987 | 0.025262 | 0.26822 | -0.10778 | -0.077956 | 0.17492 | 0.036621 | 0.09613 | -0.11902 | -0.76904 | -0.90179 | -0.99335 | -1.1307 | -0.95673 | -0.91095 | -1.1215 | 0.9613 | -121.6644 | 1.1169 | 0.31128 | -122.6624 | -0.041199 | -122.6715 | 0.15564 | -0.050354 | 0.1236 | 0.17853 | 1.1765 | 1.1169 | 0.16937 | 0.086975 | -0.041199 | 1.1765 | 1.1169 | 0.086975 | 0.17853 | 0.16937 | -121.8796 | -122.8821
882.7188 | 122.85 | -1.1169 | 121.7422 | -0.090746 | 0.083328 | 0.024194 | 0.26288 | -0.10884 | -0.091842 | 0.18987 | 0.022888 | 0.09613 | -0.15106 | -1.0162 | -1.0345 | -0.99792 | -1.1169 | -0.93384 | -0.95673 | -1.1948 | 0.96588 | -121.6461 | 1.1398 | 0.10071 | -122.7768 | -0.07782 | -122.699 | 0.17395 | 0 | 0.18311 | 0.082397 | 1.2131 | 1.1398 | 0.16022 | 0.11902 | -0.07782 | 1.2131 | 1.1398 | 0.11902 | 0.082397 | 0.16022 | -121.8933 | -122.937
883.6562 | 122.818 | -1.1215 | 121.7285 | 0.35176 | 0.095077 | 0.027398 | 0.26181 | -0.10671 | -0.091842 | 0.19308 | 0.009155 | 0.11444 | -0.13275 | -0.96588 | -0.97504 | -0.96588 | -1.1536 | -0.90179 | -0.95673 | -1.1856 | 0.98877 | -121.6141 | 1.1307 | 0.15564 | -122.7036 | -0.064087 | -122.6852 | 0.14191 | -0.032043 | 0.21973 | 0.14648 | 1.236 | 1.1307 | 0.1648 | 0.15564 | -0.064087 | 1.236 | 1.1307 | 0.15564 | 0.14648 | 0.1648 | -121.8613 | -122.9141
884.6562 | 122.7997 | -1.1307 | 121.7651 | 0.32124 | 0.076919 | 0.039147 | 0.25968 | -0.12166 | -0.086501 | 0.18667 | -0.036621 | 0.10529 | -0.16479 | -0.94757 | -0.95215 | -0.93842 | -1.1536 | -0.85602 | -0.95215 | -1.1719 | 0.96588 | -121.6599 | 1.0941 | 0.1831 | -122.7173 | -0.041199 | -122.7173 | 0.12817 | -0.022888 | 0.27466 | 0.17853 | 1.236 | 1.0941 | 0.17853 | 0.19226 | -0.041199 | 1.236 | 1.0941 | 0.19226 | 0.17853 | 0.17853 | -121.9299 | -122.937
885.7188 | 122.8455 | -1.1032 | 121.7743 | 0.19917 | 0.085464 | 0.02633 | 0.26822 | -0.11952 | -0.080092 | 0.1824 | 0.068665 | 0.15106 | -0.059509 | -1.0025 | -0.98419 | -0.97961 | -1.1169 | -0.92468 | -0.92468 | -1.1856 | 1.0437 | -121.6232 | 1.1719 | 0.10071 | -122.7585 | -0.082398 | -122.699 | 0.12817 | -0.013733 | 0.17853 | 0.11902 | 1.2543 | 1.1719 | 0.17853 | 0.1236 | -0.082398 | 1.2543 | 1.1719 | 0.1236 | 0.11902 | 0.17853 | -121.8338 | -122.9599
886.6562 | 122.8043 | -1.1215 | 121.7606 | 0.41279 | 0.077987 | 0.024194 | 0.26288 | -0.11525 | -0.080092 | 0.18774 | -0.045776 | 0.11444 | -0.16022 | -0.92926 | -0.93384 | -0.92926 | -1.1398 | -0.8606 | -0.94757 | -1.1581 | 0.9613 | -121.6461 | 1.0757 | 0.19226 | -122.6944 | -0.036621 | -122.7081 | 0.11444 | -0.018311 | 0.26092 | 0.18768 | 1.236 | 1.0757 | 0.17395 | 0.19226 | -0.036621 | 1.236 | 1.0757 | 0.19226 | 0.18768 | 0.17395 | -121.9208 | -122.9187
887.6562 | 122.8134 | -1.0941 | 121.788 | 0.47383 | 0.077987 | 0.046624 | 0.25113 | -0.11952 | -0.086501 | 0.17599 | -0.041199 | 0.10986 | -0.14648 | -0.9201 | -0.9201 | -0.91095 | -1.1215 | -0.82855 | -0.93842 | -1.1581 | 0.94757 | -121.6782 | 1.0529 | 0.17395 | -122.7081 | -0.064087 | -122.7264 | 0.10529 | -0.027466 | 0.2655 | 0.17395 | 1.2039 | 1.0529 | 0.15564 | 0.1831 | -0.064087 | 1.2039 | 1.0529 | 0.1831 | 0.17395 | 0.15564 | -121.9345 | -122.9462
888.6562 | 122.7997 | -1.1169 | 121.788 | 0.32124 | 0.074783 | 0.017785 | 0.26502 | -0.10244 | -0.087569 | 0.18453 | -0.009155 | 0.09613 | -0.16022 | -0.93842 | -0.93384 | -0.9201 | -1.1169 | -0.8606 | -0.93384 | -1.1627 | 0.95673 | -121.6919 | 1.1078 | 0.17853 | -122.7219 | -0.045777 | -122.7219 | 0.15106 | 0 | 0.25635 | 0.18311 | 1.2131 | 1.1078 | 0.18311 | 0.19684 | -0.045777 | 1.2131 | 1.1078 | 0.19684 | 0.18311 | 0.18311 | -121.9482 | -122.9507
889.6562 | 122.8363 | -1.0986 | 121.7743 | 0.24495 | 0.083328 | 0.027398 | 0.25861 | -0.10671 | -0.084365 | 0.17813 | 0 | 0.086975 | -0.15564 | -0.94299 | -0.92926 | -0.90637 | -1.1261 | -0.84686 | -0.92926 | -1.1627 | 0.94299 | -121.6873 | 1.0986 | 0.15564 | -122.7036 | -0.064087 | -122.7036 | 0.15564 | -0.027466 | 0.25177 | 0.16937 | 1.1856 | 1.0986 | 0.16937 | 0.19226 | -0.064087 | 1.1856 | 1.0986 | 0.19226 | 0.16937 | 0.16937 | -121.9299 | -122.937
890.7031 | 122.8546 | -1.0757 | 121.7834 | -0.21282 | 0.071578 | -0.0046445 | 0.24472 | -0.11952 | -0.099318 | 0.1856 | -0.041199 | 0.09613 | -0.14648 | -0.97961 | -0.96588 | -0.90637 | -1.1261 | -0.84686 | -0.91095 | -1.1444 | 0.92926 | -121.6873 | 1.0345 | 0.096131 | -122.7493 | -0.068664 | -122.6944 | 0.10529 | -0.050354 | 0.22888 | 0.10986 | 1.1719 | 1.0345 | 0.16479 | 0.16937 | -0.068664 | 1.1719 | 1.0345 | 0.16937 | 0.10986 | 0.16479 | -121.9299 | -122.9279
891.6562 | 122.8409 | -1.0666 | 121.8292 | 0.3365 | 0.071578 | 0.0081725 | 0.25754 | -0.11632 | -0.083297 | 0.17172 | -0.036621 | 0.10071 | -0.14648 | -0.9201 | -0.91553 | -0.91553 | -1.0757 | -0.84228 | -0.89264 | -1.1398 | 0.9201 | -121.7285 | 1.03 | 0.14648 | -122.7448 | -0.073243 | -122.7219 | 0.10986 | -0.009156 | 0.2243 | 0.15106 | 1.1673 | 1.03 | 0.17395 | 0.15106 | -0.073243 | 1.1673 | 1.03 | 0.15106 | 0.15106 | 0.17395 | -121.9757 | -122.9691
892.7188 | 122.7997 | -1.0529 | 121.8384 | 0.3365 | 0.082259 | 0.027398 | 0.25968 | -0.11739 | -0.084365 | 0.17813 | -0.050354 | 0.10529 | -0.15106 | -0.87891 | -0.90637 | -0.86517 | -1.0941 | -0.81024 | -0.90179 | -1.1307 | 0.90179 | -121.7331 | 1.0025 | 0.17395 | -122.7448 | -0.07782 | -122.7402 | 0.10071 | -0.041199 | 0.24261 | 0.14648 | 1.1581 | 1.0025 | 0.15106 | 0.18768 | -0.07782 | 1.1581 | 1.0025 | 0.18768 | 0.14648 | 0.15106 | -121.9894 | -122.9691
893.6562 | 122.8546 | -1.0712 | 121.8246 | 0.45857 | 0.076919 | 0.051965 | 0.25861 | -0.10991 | -0.082229 | 0.17813 | -0.018311 | 0.10529 | -0.15564 | -0.90637 | -0.90637 | -0.88348 | -1.0574 | -0.81482 | -0.87891 | -1.1169 | 0.91553 | -121.7194 | 1.0529 | 0.1648 | -122.731 | -0.045776 | -122.7036 | 0.13733 | 0.013733 | 0.25635 | 0.1648 | 1.1765 | 1.0529 | 0.19226 | 0.18768 | -0.045776 | 1.1765 | 1.0529 | 0.18768 | 0.1648 | 0.19226 | -121.9803 | -122.9416
894.6562 | 122.8317 | -1.0437 | 121.8109 | 0.41279 | 0.094009 | 0.0017635 | 0.2522 | -0.10884 | -0.086501 | 0.17065 | -0.018311 | 0.10986 | -0.14191 | -0.90179 | -0.91095 | -0.89264 | -1.062 | -0.80566 | -0.88806 | -1.1169 | 0.90179 | -121.701 | 1.0254 | 0.14191 | -122.7219 | -0.073242 | -122.699 | 0.1236 | -0.018311 | 0.23804 | 0.13275 | 1.1536 | 1.0254 | 0.15564 | 0.15106 | -0.073242 | 1.1536 | 1.0254 | 0.15106 | 0.13275 | 0.15564 | -121.9528 | -122.9279
895.7188 | 122.937 | -1.0117 | 121.8063 | 0.50435 | 0.080123 | 0.017785 | 0.25113 | -0.10778 | -0.090773 | 0.18667 | 0.018311 | 0.07782 | -0.13733 | -0.98419 | -0.9613 | -0.96588 | -0.95673 | -0.89722 | -0.85602 | -1.1261 | 0.87433 | -121.7285 | 1.03 | 0.027466 | -122.7676 | -0.11444 | -122.6624 | 0.15564 | 0.054932 | 0.11444 | 0.050354 | 1.0895 | 1.03 | 0.15564 | 0.045777 | -0.11444 | 1.0895 | 1.03 | 0.045777 | 0.050354 | 0.15564 | -121.9437 | -122.9324
896.6562 | 122.85 | -1.0391 | 121.8979 | 0.44331 | 0.073715 | 0.041283 | 0.26395 | -0.10991 | -0.074752 | 0.17706 | -0.036621 | 0.10529 | -0.13733 | -0.86517 | -0.86975 | -0.86517 | -1.0574 | -0.7782 | -0.87891 | -1.0849 | 0.90179 | -121.7926 | 1.0025 | 0.17395 | -122.7676 | -0.045776 | -122.7768 | 0.10071 | -0.01831 | 0.26093 | 0.16937 | 1.1444 | 1.0025 | 0.16022 | 0.17395 | -0.045776 | 1.1444 | 1.0025 | 0.17395 | 0.16937 | 0.16022 | -122.0352 | -122.9828
897.7031 | 122.8867 | -1.03 | 121.8658 | -0.24333 | 0.081191 | 0.027398 | 0.27036 | -0.10778 | -0.093978 | 0.18453 | 0.054932 | 0.15106 | -0.068665 | -0.90179 | -0.93384 | -0.90637 | -1.0345 | -0.83313 | -0.83771 | -1.1124 | 0.9613 | -121.7148 | 1.0849 | 0.12817 | -122.7997 | -0.082398 | -122.7036 | 0.1236 | -0.004578 | 0.19684 | 0.09613 | 1.181 | 1.0849 | 0.19226 | 0.1236 | -0.082398 | 1.181 | 1.0849 | 0.1236 | 0.09613 | 0.19226 | -121.9345 | -122.9782
898.6562 | 122.9599 | -1.0071 | 121.8658 | 0.56538 | 0.071578 | 0.023126 | 0.25754 | -0.11632 | -0.085433 | 0.17813 | 0.018311 | 0.091553 | -0.12817 | -0.97046 | -0.97046 | -0.94299 | -0.90179 | -0.89264 | -0.83771 | -1.1078 | 0.87891 | -121.7743 | 1.0254 | 0.036621 | -122.8363 | -0.10071 | -122.7036 | 0.14649 | 0.10529 | 0.11444 | 0.036621 | 1.0986 | 1.0254 | 0.16937 | 0.064087 | -0.10071 | 1.0986 | 1.0254 | 0.064087 | 0.036621 | 0.16937 | -121.994 | -122.9736
899.7188 | 122.9599 | -0.98877 | 121.8338 | 0.56538 | 0.081191 | 0.02633 | 0.2522 | -0.12273 | -0.096114 | 0.18347 | 0.041199 | 0.073242 | -0.12817 | -0.95673 | -0.9613 | -0.97046 | -0.9201 | -0.88806 | -0.80566 | -1.0986 | 0.8606 | -121.7606 | 1.03 | 0.032044 | -122.7951 | -0.10986 | -122.6395 | 0.16937 | 0.068665 | 0.10071 | 0.027466 | 1.062 | 1.03 | 0.18311 | 0.018311 | -0.10986 | 1.062 | 1.03 | 0.018311 | 0.027466 | 0.18311 | -121.962 | -122.9324
900.6562 | 122.9553 | -0.97046 | 121.8796 | 0.61116 | 0.075851 | 0.027398 | 0.26074 | -0.127 | -0.08116 | 0.17919 | 0.027466 | 0.054932 | -0.11902 | -0.98419 | -0.98877 | -0.96588 | -0.89722 | -0.89722 | -0.83313 | -1.1169 | 0.85144 | -121.8246 | 0.99792 | -0.013733 | -122.8683 | -0.14648 | -122.7127 | 0.14649 | 0.073242 | 0.073242 | -0.018311 | 1.0254 | 0.99792 | 0.13733 | 0.004578 | -0.14648 | 1.0254 | 0.99792 | 0.004578 | -0.018311 | 0.13733 | -121.9986 | -122.9965
901.7031 | 122.8317 | -1.0208 | 121.8933 | 0.27546 | 0.083328 | 0.063714 | 0.27356 | -0.10884 | -0.076888 | 0.17172 | -0.018311 | 0.10071 | -0.16479 | -0.83771 | -0.86517 | -0.85602 | -1.0483 | -0.75531 | -0.8606 | -1.0803 | 0.85602 | -121.7926 | 1.0025 | 0.1831 | -122.7585 | -0.059509 | -122.7539 | 0.14648 | -0.027466 | 0.2655 | 0.15564 | 1.1215 | 1.0025 | 0.16022 | 0.1648 | -0.059509 | 1.1215 | 1.0025 | 0.1648 | 0.15564 | 0.16022 | -122.0581 | -122.9736
902.6562 | 122.8821 | -1.0117 | 121.8842 | 0.5196 | 0.082259 | 0.027398 | 0.26181 | -0.10991 | -0.093978 | 0.17919 | -0.004578 | 0.10071 | -0.13733 | -0.87433 | -0.87433 | -0.87433 | -1.0025 | -0.80566 | -0.84228 | -1.062 | 0.87433 | -121.7834 | 1.0071 | 0.13733 | -122.7585 | -0.050354 | -122.7264 | 0.13275 | 0.009156 | 0.20599 | 0.13733 | 1.1124 | 1.0071 | 0.16937 | 0.13733 | -0.050354 | 1.1124 | 1.0071 | 0.13733 | 0.13733 | 0.16937 | -122.0215 | -122.9462
903.6719 | 122.9279 | -0.95673 | 121.8842 | 0.29072 | 0.067306 | 0.014581 | 0.24472 | -0.1238 | -0.11427 | 0.18667 | -0.022888 | 0.032043 | -0.16022 | -0.97504 | -0.94757 | -0.92468 | -0.91095 | -0.84228 | -0.8194 | -1.0574 | 0.79651 | -121.8521 | 0.93384 | -0.018311 | -122.8317 | -0.10071 | -122.7036 | 0.13733 | 0.045776 | 0.11444 | 0.009155 | 0.98877 | 0.93384 | 0.13733 | 0.032043 | -0.10071 | 0.98877 | 0.93384 | 0.032043 | 0.009155 | 0.13733 | -122.0444 | -122.9416
904.7031 | 122.8363 | -1.0025 | 121.9208 | 0.41279 | 0.097213 | 0.037011 | 0.25861 | -0.127 | -0.084365 | 0.17706 | -0.018311 | 0.10071 | -0.15564 | -0.78735 | -0.83313 | -0.79193 | -1.0391 | -0.72327 | -0.8194 | -1.0574 | 0.84686 | -121.8201 | 0.98419 | 0.21515 | -122.7539 | -0.054932 | -122.7402 | 0.13733 | -0.036622 | 0.27924 | 0.16937 | 1.1032 | 0.98419 | 0.1831 | 0.21057 | -0.054932 | 1.1032 | 0.98419 | 0.21057 | 0.16937 | 0.1831 | -122.0764 | -122.9782
905.6562 | 122.9828 | -0.94757 | 121.8933 | 0.5196 | 0.07051 | 0.019921 | 0.23938 | -0.12914 | -0.097182 | 0.17385 | 0.054932 | 0.027466 | -0.11902 | -0.97961 | -0.93842 | -0.94299 | -0.86517 | -0.86975 | -0.76904 | -1.0803 | 0.82855 | -121.8658 | 1.0025 | -0.032043 | -122.8317 | -0.13275 | -122.6624 | 0.17395 | 0.082398 | 0.07782 | 0.009155 | 0.97504 | 1.0025 | 0.17853 | 0.004578 | -0.13275 | 0.97504 | 1.0025 | 0.004578 | 0.009155 | 0.17853 | -122.0123 | -122.9736
906.6562 | 122.9645 | -0.92926 | 121.8887 | 0.5196 | 0.071578 | 0.024194 | 0.24579 | -0.11846 | -0.10359 | 0.18026 | 0.054932 | 0.032043 | -0.11902 | -0.97046 | -0.94299 | -0.95215 | -0.86517 | -0.86517 | -0.7782 | -1.0712 | 0.81024 | -121.8567 | 0.98419 | -0.041199 | -122.8317 | -0.14191 | -122.6669 | 0.17395 | 0.064087 | 0.064087 | -0.013733 | 0.9613 | 0.98419 | 0.15106 | -0.022888 | -0.14191 | 0.9613 | 0.98419 | -0.022888 | -0.013733 | 0.15106 | -122.0078 | -122.9599
907.6562 | 122.9599 | -0.91553 | 121.9116 | 0.44331 | 0.064101 | 0.0049685 | 0.24579 | -0.12487 | -0.10786 | 0.18881 | 0.068665 | 0.045776 | -0.10529 | -0.9613 | -0.95673 | -0.93384 | -0.8606 | -0.85602 | -0.77362 | -1.0757 | 0.81024 | -121.8658 | 0.98419 | -0.045777 | -122.8683 | -0.16022 | -122.6852 | 0.17395 | 0.054931 | 0.059509 | -0.041199 | 0.9613 | 0.98419 | 0.14191 | -0.018311 | -0.16022 | 0.9613 | 0.98419 | -0.018311 | -0.041199 | 0.14191 | -122.0169 | -122.9874
908.7188 | 122.9691 | -0.92468 | 121.9254 | 3.0526 | 0.079055 | 0.013512 | 0.24365 | -0.13127 | -0.10146 | 0.18667 | 0.064087 | 0.050354 | -0.12817 | -0.98419 | -0.95673 | -0.9201 | -0.86517 | -0.86517 | -0.76446 | -1.0529 | 0.79651 | -121.875 | 0.98877 | -0.059509 | -122.8821 | -0.12817 | -122.6898 | 0.19226 | 0.05951 | 0.05951 | -0.032043 | 0.97504 | 0.98877 | 0.16022 | 0.004578 | -0.12817 | 0.97504 | 0.98877 | 0.004578 | -0.032043 | 0.16022 | -122.0535 | -122.9782
909.6562 | 122.9691 | -0.94757 | 121.9208 | 0.56538 | 0.066238 | 0.0049685 | 0.25434 | -0.13341 | -0.082229 | 0.18026 | 0.073242 | 0.050354 | -0.10529 | -1.1307 | -1.0666 | -0.95673 | -0.84686 | -0.88348 | -0.8194 | -1.1124 | 0.84229 | -121.8704 | 1.0208 | -0.1831 | -122.9874 | -0.16479 | -122.7402 | 0.17853 | 0.10071 | 0.064087 | -0.11902 | 0.99793 | 1.0208 | 0.12817 | -0.009155 | -0.16479 | 0.99793 | 1.0208 | -0.009155 | -0.11902 | 0.12817 | -122.0261 | -123.0331
910.6562 | 122.9782 | -0.92468 | 121.9528 | 0.61116 | 0.068374 | 0.015649 | 0.2554 | -0.12914 | -0.09825 | 0.17599 | 0.086975 | 0.036621 | -0.11902 | -0.9613 | -0.96588 | -0.93842 | -0.82855 | -0.87433 | -0.79193 | -1.0895 | 0.80566 | -121.9162 | 1.0117 | -0.036621 | -122.9187 | -0.16479 | -122.7448 | 0.20599 | 0.096131 | 0.050354 | -0.041198 | 0.9613 | 1.0117 | 0.13275 | -0.013733 | -0.16479 | 0.9613 | 1.0117 | -0.013733 | -0.041198 | 0.13275 | -122.0718 | -123.0423
911.7031 | 122.8729 | -0.95673 | 121.9437 | 0.45857 | 0.082259 | 0.027398 | 0.27036 | -0.12807 | -0.090773 | 0.17492 | -0.009155 | 0.10529 | -0.14191 | -0.71411 | -0.82398 | -0.81482 | -0.96588 | -0.73242 | -0.77362 | -1.0025 | 0.81482 | -121.8384 | 0.94757 | 0.24261 | -122.7676 | -0.045776 | -122.7173 | 0.13275 | -0.009155 | 0.2243 | 0.13275 | 1.062 | 0.94757 | 0.1831 | 0.14191 | -0.045776 | 1.062 | 0.94757 | 0.14191 | 0.13275 | 0.1831 | -122.0856 | -122.9462
912.6562 | 122.9233 | -0.93384 | 121.9437 | 0.30598 | 0.056625 | 0.0092405 | 0.24899 | -0.1238 | -0.11107 | 0.18881 | -0.004578 | 0.054932 | -0.11444 | -0.91095 | -0.86975 | -0.86517 | -0.89722 | -0.80109 | -0.7782 | -1.03 | 0.8194 | -121.8887 | 0.92926 | 0.022888 | -122.8134 | -0.09613 | -122.7219 | 0.10986 | 0.036621 | 0.13275 | 0.064087 | 0.98877 | 0.92926 | 0.15564 | 0.068665 | -0.09613 | 0.98877 | 0.92926 | 0.068665 | 0.064087 | 0.15564 | -122.0581 | -122.9736

## Thermal Data
Fire Time | South 11 C | Cable 1 | Cable 2
-0.8552 | 22.3552 | 20.6639 | 20.7704
0.1448 | 22.3571 | 20.657 | 20.7676
1.1448 | 22.3592 | 20.6584 | 20.7742
2.1448 | 22.359 | 20.6602 | 20.7668
3.1448 | 22.3577 | 20.6568 | 20.7719
4.1448 | 22.5701 | 20.6662 | 20.7694
5.1448 | 23.3165 | 20.6704 | 20.7731
6.1448 | 24.6566 | 20.6751 | 20.7674
7.1448 | 26.5727 | 20.6659 | 20.7779
8.1448 | 28.9632 | 20.6734 | 20.7797
9.1448 | 31.793 | 20.6771 | 20.7877
10.1448 | 34.9609 | 20.6763 | 20.8044
11.1448 | 38.4441 | 20.6957 | 20.8201
12.1448 | 42.1944 | 20.7031 | 20.8471
13.1448 | 46.1877 | 20.7104 | 20.8777
14.1448 | 50.406 | 20.7406 | 20.9154
15.1448 | 54.8039 | 20.7631 | 20.9611
16.1448 | 59.3845 | 20.7949 | 21.0145
17.176 | 64.2657 | 20.8449 | 21.0963
18.1448 | 68.9517 | 20.8828 | 21.1721
19.1448 | 73.9467 | 20.9401 | 21.2652
20.1448 | 79.057 | 20.991 | 21.3635
21.1448 | 84.2596 | 21.0641 | 21.4793
22.1448 | 89.5772 | 21.1349 | 21.6043
23.1448 | 94.9748 | 21.2235 | 21.7391
24.1448 | 100.4894 | 21.3208 | 21.8866
25.1448 | 106.0734 | 21.414 | 22.0466
26.1448 | 111.7153 | 21.5349 | 22.2155
27.1448 | 117.4361 | 21.6546 | 22.3941
28.1448 | 123.2042 | 21.7936 | 22.5816
29.1448 | 129.0585 | 21.9401 | 22.7853
30.1448 | 134.8954 | 22.0847 | 23.024
31.1448 | 140.7236 | 22.2456 | 23.2678
32.1448 | 146.5296 | 22.4289 | 23.5052
33.1448 | 152.3606 | 22.6286 | 23.7863
34.1448 | 158.1562 | 22.8417 | 24.071
35.1448 | 163.9735 | 23.0614 | 24.3724
36.1448 | 169.8732 | 23.303 | 24.6969
37.1448 | 175.7726 | 23.5536 | 25.0372
38.1448 | 181.6815 | 23.8324 | 25.4013
39.1448 | 187.5068 | 24.1281 | 25.7711
40.1448 | 193.3406 | 24.436 | 26.1658
41.1448 | 199.2169 | 24.757 | 26.593
42.1448 | 205.0553 | 25.1141 | 27.0422
43.1448 | 210.8487 | 25.4767 | 27.4989
44.1448 | 216.6546 | 25.8545 | 27.987
45.1448 | 222.4217 | 26.2635 | 28.478
46.1448 | 228.248 | 26.6767 | 28.9962
47.1448 | 234.1122 | 27.1263 | 29.5547
48.1448 | 239.9596 | 27.5771 | 30.1208
49.1448 | 245.7261 | 28.0508 | 30.7109
50.1448 | 251.4925 | 28.5529 | 31.3294
51.1448 | 257.2553 | 29.0703 | 31.9718
52.1448 | 263.0428 | 29.6005 | 32.6453
53.1448 | 268.7665 | 30.158 | 33.3327
54.1448 | 274.4812 | 30.7373 | 34.0465
55.1448 | 280.1635 | 31.3376 | 34.7869
56.1448 | 285.8876 | 31.9503 | 35.5539
57.1448 | 291.531 | 32.59 | 36.3463
58.1448 | 297.1359 | 33.2498 | 37.1664
59.1448 | 302.7294 | 33.9328 | 38.0067
60.1448 | 308.3467 | 34.6284 | 38.877
61.1448 | 314.0041 | 35.3468 | 39.7627
62.1448 | 319.5495 | 36.0894 | 40.6636
63.1448 | 325.0899 | 36.8661 | 41.607
64.1448 | 330.6028 | 37.6462 | 42.5762
65.1448 | 336.0489 | 38.4423 | 43.567
66.1448 | 341.4793 | 39.2669 | 44.5942
67.1448 | 346.9647 | 40.111 | 45.6415
68.1448 | 352.3147 | 40.983 | 46.708
69.1448 | 357.6382 | 41.8722 | 47.8016
70.1448 | 362.9779 | 42.793 | 48.9163
71.1448 | 368.2849 | 43.7373 | 50.0559
72.1448 | 373.5252 | 44.7141 | 51.237
73.1448 | 378.6588 | 45.7237 | 52.4528
74.1448 | 383.8664 | 46.7688 | 53.6888
75.1448 | 389.0447 | 47.8358 | 54.9742
76.1448 | 394.0925 | 48.9361 | 56.3095
77.1448 | 399.111 | 50.0655 | 57.6886
78.1448 | 404.1646 | 51.2328 | 59.1076
79.1448 | 409.1553 | 52.4332 | 60.5592
80.1448 | 414.1154 | 53.6649 | 62.0524
81.1448 | 419.0769 | 54.9358 | 63.5863
82.1448 | 423.9434 | 56.2502 | 65.157
83.1448 | 428.5009 | 57.5967 | 66.7384
84.1448 | 432.7149 | 58.9629 | 68.344
85.1448 | 436.5109 | 60.3555 | 69.9746
86.1448 | 440.0776 | 61.7587 | 71.6189
87.1448 | 443.3854 | 63.1723 | 73.2772
88.1448 | 446.5402 | 64.6016 | 74.9785
89.1448 | 449.5919 | 66.0659 | 76.6787
90.1448 | 452.5828 | 67.5392 | 78.3872
91.1448 | 455.4863 | 69.0247 | 80.1151
92.1448 | 458.3225 | 70.5218 | 81.8515
93.1448 | 460.9517 | 72.0369 | 83.5938
94.1448 | 463.3551 | 73.5608 | 85.3606
95.1448 | 465.4572 | 75.1042 | 87.1133
96.1448 | 467.2548 | 76.6478 | 88.8683
97.1448 | 468.913 | 78.1971 | 90.6252
98.1448 | 470.3217 | 79.7583 | 92.3825
99.1448 | 471.5271 | 81.3121 | 94.1496
100.1448 | 472.4693 | 82.8624 | 95.89
101.1448 | 473.1594 | 84.4263 | 97.6291
102.1448 | 473.6939 | 85.9759 | 99.3602
103.1448 | 474.0362 | 87.5162 | 101.0603
104.1448 | 474.2819 | 89.0538 | 102.7785
105.1448 | 474.4828 | 90.5986 | 104.4558
106.1448 | 474.6115 | 92.1253 | 106.1231
107.1448 | 474.6301 | 93.6622 | 107.7682
108.1448 | 474.6341 | 95.1839 | 109.392
109.1448 | 474.6063 | 96.6944 | 111.0032
110.1448 | 474.5294 | 98.2017 | 112.6155
111.1448 | 474.3923 | 99.688 | 114.1976
112.1448 | 474.2387 | 101.1543 | 115.7612
113.1448 | 474.0323 | 102.6166 | 117.2976
114.1448 | 473.8812 | 104.0752 | 118.8288
115.1448 | 473.8164 | 105.5133 | 120.3383
116.1448 | 473.7291 | 106.9408 | 121.8464
117.1448 | 473.6051 | 108.3529 | 123.3352
118.1448 | 473.4981 | 109.7579 | 124.7941
119.1448 | 473.4025 | 111.1585 | 126.2624
120.1448 | 473.3202 | 112.5469 | 127.7029
121.1448 | 473.1763 | 113.9196 | 129.1276
122.1448 | 473.1716 | 115.2909 | 130.5559
123.1448 | 473.2022 | 116.6419 | 131.9671
124.1448 | 473.2812 | 117.9842 | 133.3626
125.1448 | 473.3296 | 119.3298 | 134.7547
126.1448 | 473.3799 | 120.6667 | 136.1187
127.1448 | 473.4135 | 122.0038 | 137.4797
128.1448 | 473.402 | 123.3145 | 138.8273
129.1448 | 473.4189 | 124.6252 | 140.1788
130.1448 | 473.5283 | 125.9343 | 141.5257
131.1448 | 473.6047 | 127.2342 | 142.8461
132.1448 | 473.5942 | 128.5263 | 144.1641
133.1448 | 473.6438 | 129.8159 | 145.4749
134.1448 | 473.752 | 131.1139 | 146.7686
135.1448 | 473.9163 | 132.4101 | 148.0737
136.1448 | 474.079 | 133.6825 | 149.3438
137.1448 | 474.2621 | 134.9629 | 150.616
138.1448 | 474.4672 | 136.2285 | 151.8865
139.1448 | 474.6311 | 137.5073 | 153.1391
140.1448 | 474.7586 | 138.7831 | 154.3768
141.1448 | 474.9244 | 140.0651 | 155.613
142.1448 | 475.0018 | 141.3462 | 156.8275
143.1448 | 475.0451 | 142.6216 | 158.0333
144.1448 | 475.1644 | 143.9066 | 159.2341
145.1448 | 475.2771 | 145.1834 | 160.41
146.1448 | 475.3788 | 146.4652 | 161.5663
147.1448 | 475.4579 | 147.7338 | 162.7068
148.1448 | 475.5136 | 149.0159 | 163.8401
149.1448 | 475.4407 | 150.2865 | 164.9581
150.1448 | 475.4882 | 151.563 | 166.0612
151.1448 | 475.5435 | 152.8288 | 167.1515
152.1448 | 475.6033 | 154.0887 | 168.2285
153.1448 | 475.6815 | 155.3466 | 169.292
154.1448 | 475.7725 | 156.5869 | 170.3596
155.1448 | 475.856 | 157.8338 | 171.3916
156.1448 | 475.9457 | 159.0796 | 172.4194
157.1448 | 475.985 | 160.3225 | 173.4314
158.1448 | 475.9857 | 161.5695 | 174.4308
159.1448 | 475.9755 | 162.7978 | 175.4177
160.1448 | 475.9876 | 164.0397 | 176.3896
161.1448 | 475.9391 | 165.253 | 177.357
162.1448 | 475.9154 | 166.4763 | 178.3075
163.1448 | 475.9762 | 167.6895 | 179.238
164.1448 | 475.9902 | 168.8892 | 180.177
165.1448 | 476.0083 | 170.0876 | 181.0842
166.1448 | 476.0241 | 171.2687 | 181.9797
167.1448 | 476.0668 | 172.4517 | 182.8502
168.1448 | 476.0949 | 173.6218 | 183.7224
169.1448 | 476.0569 | 174.7785 | 184.5832
170.1448 | 476.051 | 175.9227 | 185.4434
171.1448 | 475.9908 | 177.0553 | 186.2964
172.1448 | 475.8481 | 178.1895 | 187.1369
173.1448 | 475.867 | 179.3018 | 187.9796
174.1448 | 475.8567 | 180.4229 | 188.8222
175.1448 | 475.89 | 181.5198 | 189.6677
176.1448 | 475.8587 | 182.6137 | 190.513
177.1448 | 475.8985 | 183.689 | 191.3429
178.1448 | 475.9425 | 184.7568 | 192.1674
179.1448 | 475.9927 | 185.8055 | 192.9878
180.1448 | 475.9922 | 186.8605 | 193.803
181.1448 | 476.0233 | 187.8986 | 194.6196
182.1448 | 476.0711 | 188.9236 | 195.4305
183.1448 | 476.0742 | 189.9494 | 196.2392
184.1448 | 476.0908 | 190.9442 | 197.0505
185.1448 | 476.0891 | 191.9263 | 197.8574
186.1448 | 476.1259 | 192.9075 | 198.6594
187.1448 | 476.2155 | 193.8753 | 199.4839
188.1448 | 476.3424 | 194.8361 | 200.2873
189.1448 | 476.4466 | 195.7951 | 201.0928
190.1448 | 476.525 | 196.7486 | 201.8979
191.1448 | 476.5584 | 197.712 | 202.6962
192.1448 | 476.6626 | 198.6603 | 203.5047
193.1448 | 476.6991 | 199.6256 | 204.3113
194.1448 | 476.7204 | 200.5784 | 205.1174
195.1448 | 476.7658 | 201.5477 | 205.9312
196.1448 | 476.828 | 202.5006 | 206.7399
197.1448 | 476.748 | 203.4644 | 207.5473
198.1448 | 476.7274 | 204.4258 | 208.3558
199.1448 | 476.7811 | 205.3772 | 209.1591
200.1448 | 476.7813 | 206.3453 | 209.9854
201.1448 | 476.773 | 207.3235 | 210.7909
202.1448 | 476.7341 | 208.3005 | 211.6103
203.1448 | 476.7408 | 209.2764 | 212.4284
204.1448 | 476.8032 | 210.2499 | 213.2526
205.1448 | 476.833 | 211.2301 | 214.075
206.1448 | 476.7611 | 212.1974 | 214.9012
207.1448 | 476.7547 | 213.1661 | 215.7292
208.1448 | 476.678 | 214.1401 | 216.554
209.1448 | 476.5894 | 215.1083 | 217.378
210.1448 | 476.4409 | 216.0865 | 218.2101
211.1448 | 476.3489 | 217.0651 | 219.047
212.1448 | 476.348 | 218.0463 | 219.8748
213.1448 | 476.3069 | 219.0511 | 220.7085
214.1448 | 476.2859 | 220.0194 | 221.532
215.1448 | 476.2865 | 221.0109 | 222.3517
216.1448 | 476.2503 | 221.9999 | 223.1743
217.1448 | 476.2237 | 222.9817 | 224.0132
218.1448 | 476.193 | 223.9709 | 224.8315
219.1448 | 476.2187 | 224.9671 | 225.6624
220.1448 | 476.2411 | 225.9482 | 226.4968
221.1448 | 476.2432 | 226.9507 | 227.3162
222.1448 | 476.1492 | 227.9395 | 228.1283
223.1448 | 476.1014 | 228.9453 | 228.9393
224.1448 | 476.056 | 229.9434 | 229.6969
225.1448 | 476.039 | 230.9039 | 230.4165
226.1448 | 475.9728 | 231.9177 | 231.1126
227.1448 | 475.9338 | 232.9003 | 231.7713
228.1448 | 475.9066 | 233.8406 | 232.4045
229.1448 | 475.9132 | 234.7957 | 233.0222
230.1448 | 475.9648 | 235.6567 | 233.6215
231.1448 | 475.9897 | 235.6765 | 234.1584
232.1448 | 475.9767 | 236.2752 | 234.6608
233.1448 | 475.9834 | 236.9306 | 235.2005
234.1448 | 475.9243 | 237.646 | 235.7518
235.1448 | 475.8118 | 238.3838 | 236.3152
236.1448 | 475.747 | 239.0901 | 236.8537
237.1448 | 475.6458 | 239.7278 | 237.4295
238.1448 | 475.5584 | 240.3006 | 238.0567
239.1448 | 475.5043 | 240.9128 | 238.6877
240.1448 | 475.5194 | 241.4966 | 239.3249
241.1448 | 475.454 | 242.0651 | 239.9594
242.1448 | 475.4397 | 242.6605 | 240.627
243.1448 | 475.4428 | 243.2474 | 241.2858
244.1448 | 475.4045 | 243.8829 | 242.0233
245.1448 | 475.3856 | 244.4661 | 242.7583
246.1448 | 475.4499 | 244.9656 | 243.3947
247.1448 | 475.5249 | 245.3781 | 244.009
248.1448 | 475.5191 | 245.8232 | 244.6146
249.1448 | 475.5478 | 246.313 | 245.186
250.1448 | 475.545 | 246.7707 | 245.7573
251.1448 | 475.5168 | 247.2543 | 246.3362
252.1448 | 475.465 | 247.7377 | 246.8816
253.1448 | 475.479 | 248.2682 | 247.4483
254.1448 | 475.5046 | 248.8357 | 248.0599
255.1448 | 475.5608 | 249.3614 | 248.6777
256.1448 | 475.495 | 249.9024 | 249.3363
257.1448 | 475.4705 | 250.4338 | 249.9699
258.1448 | 475.4965 | 250.945 | 250.6027
259.1448 | 475.4398 | 251.4355 | 251.2082
260.1448 | 475.3995 | 251.9129 | 251.7888
261.1448 | 475.38 | 252.3777 | 252.3575
262.1448 | 475.4143 | 252.8376 | 252.9118
263.1448 | 475.4273 | 253.3175 | 253.4323
264.1448 | 475.4914 | 253.767 | 253.9322
265.1448 | 475.526 | 254.2501 | 254.3676
266.1448 | 475.5135 | 254.6747 | 254.8463
267.1448 | 475.5263 | 255.0241 | 255.4004
268.1448 | 475.5281 | 255.382 | 255.9972
269.1448 | 475.5569 | 255.7867 | 256.6774
270.1448 | 475.5874 | 256.171 | 257.374
271.1448 | 475.647 | 256.5748 | 258.0591
272.1448 | 475.7342 | 256.9881 | 258.7851
273.1448 | 475.7958 | 257.4344 | 259.5206
274.1448 | 475.8516 | 257.8596 | 260.2182
275.1448 | 475.9467 | 258.2874 | 260.8995
276.1448 | 476.0001 | 258.715 | 261.5257
277.1448 | 476.043 | 259.1519 | 262.319
278.1448 | 475.9826 | 259.6074 | 262.7881
279.1448 | 475.8964 | 260.0321 | 262.9816
280.1448 | 475.8503 | 260.4598 | 263.1851
281.1448 | 475.7883 | 260.903 | 263.4627
282.1448 | 475.7876 | 261.3579 | 263.8139
283.1448 | 475.7519 | 261.8306 | 264.1667
284.1448 | 475.741 | 262.2828 | 264.5234
285.1448 | 475.7654 | 262.7571 | 264.8938
286.1448 | 475.7417 | 263.2264 | 265.2625
287.1448 | 475.7477 | 263.7001 | 265.6182
288.1448 | 475.7699 | 264.1569 | 265.9765
289.1448 | 475.7414 | 264.5941 | 266.2541
290.1448 | 475.7489 | 265.0209 | 266.3003
291.1448 | 475.7447 | 265.4602 | 266.3472
292.1448 | 475.7293 | 265.901 | 266.4147
293.1448 | 475.6849 | 266.3476 | 266.4323
294.1448 | 475.6034 | 266.9905 | 265.2859
295.1448 | 475.5854 | 267.5764 | 264.2771
296.1448 | 475.5873 | 267.9694 | 263.5067
297.1448 | 475.614 | 267.9129 | 262.8904
298.1448 | 475.6431 | 267.8657 | 262.476
299.1448 | 475.6047 | 267.9296 | 262.1845
300.1448 | 475.586 | 268.0255 | 262.0071
301.1448 | 475.7402 | 268.217 | 261.9984
302.1448 | 476.0049 | 268.5368 | 262.1374
303.1448 | 476.2579 | 268.9412 | 262.3686
304.1448 | 476.5718 | 269.3215 | 262.7525
305.1448 | 476.8959 | 269.7635 | 263.2892
306.1448 | 477.2489 | 270.2549 | 263.8166
307.1448 | 477.5868 | 270.6844 | 264.4035
308.1448 | 477.9645 | 271.1413 | 265.067
309.1448 | 478.2492 | 271.6539 | 265.7136
310.1448 | 478.4494 | 272.1782 | 266.2408
311.1448 | 478.6153 | 272.7234 | 266.848
312.1448 | 478.7377 | 273.3533 | 267.5158
313.1448 | 478.7679 | 274.0504 | 268.2556
314.1448 | 478.7 | 274.7942 | 269.1029
315.1448 | 478.6232 | 275.5058 | 269.9581
316.1448 | 478.5438 | 276.1617 | 271.0559
317.1448 | 478.4531 | 276.8516 | 272.358
318.1448 | 478.3373 | 277.5965 | 273.9502
319.1448 | 478.2121 | 278.2702 | 275.7741
320.1448 | 478.0374 | 278.9313 | 277.7173
321.1448 | 477.8643 | 279.7098 | 279.5823
322.1448 | 477.6542 | 280.2949 | 281.5325
323.1448 | 477.458 | 280.7614 | 283.521
324.1448 | 477.2234 | 281.0106 | 285.2387
325.1448 | 477.055 | 281.5357 | 287.0394
326.1448 | 476.9042 | 282.3785 | 288.6358
327.1448 | 476.7826 | 283.3965 | 290.0105
328.1448 | 476.6182 | 284.4575 | 291.6578
329.1448 | 476.3969 | 285.6042 | 293.4267
330.1448 | 476.1134 | 286.7321 | 294.9873
331.1448 | 475.8823 | 287.878 | 296.3592
332.1448 | 475.6632 | 288.9942 | 297.7553
333.1448 | 475.4582 | 290.1431 | 299.2701
334.1448 | 475.2656 | 291.3682 | 300.7429
335.1448 | 475.0503 | 292.6322 | 302.2653
336.1448 | 474.8635 | 293.9124 | 303.7762
337.1448 | 474.6315 | 295.1323 | 305.2505
338.1448 | 474.4488 | 296.385 | 306.7599
339.1448 | 474.2967 | 297.6668 | 308.441
340.1448 | 474.1564 | 298.9502 | 309.8159
341.1448 | 474.059 | 300.2962 | 311.2345
342.1448 | 473.9331 | 301.664 | 312.7953
343.1448 | 473.7602 | 303.0423 | 314.2665
344.1448 | 473.5752 | 304.4726 | 315.9832
345.1448 | 473.4269 | 305.8935 | 317.5569
346.1448 | 473.3056 | 307.3892 | 319.0237
347.1448 | 473.1572 | 308.8823 | 320.4893
348.1448 | 473.0036 | 310.4313 | 322.0399
349.1448 | 472.8745 | 311.9958 | 323.7527
350.1448 | 472.7548 | 313.5799 | 325.2358
351.1448 | 472.678 | 315.1466 | 326.3249
352.1448 | 472.6381 | 316.6752 | 327.8369
353.1448 | 472.5916 | 318.1959 | 329.116
354.1448 | 472.5954 | 319.7002 | 330.5031
355.1448 | 472.585 | 321.2402 | 332.0169
356.1448 | 472.5325 | 322.8158 | 333.5236
357.1448 | 472.4746 | 324.4203 | 335.1181
358.1448 | 472.4208 | 326.061 | 336.6575
359.1448 | 472.3432 | 327.6783 | 338.5083
360.1448 | 472.2729 | 329.2549 | 340.0046
361.1448 | 472.1906 | 330.8813 | 341.6486
362.1448 | 472.1447 | 332.3005 | 343.5098
363.1448 | 472.082 | 333.9233 | 345.2989
364.1448 | 471.9857 | 335.4553 | 347.0667
365.1448 | 471.9374 | 337.1177 | 348.9317
366.1448 | 471.8802 | 338.9288 | 350.8405
367.1448 | 471.8311 | 340.5452 | 352.656
368.1448 | 471.727 | 342.3099 | 354.3994
369.1448 | 471.6728 | 344.1867 | 356.2799
370.1448 | 471.7137 | 346.0037 | 358.1419
371.1448 | 471.7274 | 347.786 | 360.0216
372.1448 | 471.7162 | 349.532 | 361.9045
373.1448 | 471.7668 | 351.6394 | 363.6374
374.1448 | 471.7989 | 353.2727 | 365.6638
375.1448 | 471.8614 | 355.279 | 367.2073
376.1448 | 471.888 | 357.4002 | 368.9023
377.1448 | 471.883 | 359.388 | 370.6356
378.1448 | 471.9393 | 361.6401 | 372.3815
379.1448 | 471.947 | 363.5066 | 373.8113
380.1448 | 471.9292 | 364.9574 | 375.6218
381.1448 | 471.9566 | 366.9687 | 377.2202
382.1448 | 472.0105 | 368.4526 | 378.8694
383.1448 | 472.1064 | 370.4582 | 380.1705
384.1448 | 472.2063 | 371.9053 | 381.5401
385.1448 | 472.2289 | 373.7127 | 382.831
386.1448 | 472.2282 | 375.1487 | 384.0815
387.1448 | 472.2597 | 376.8548 | 385.4222
388.1448 | 472.2819 | 378.4102 | 386.6772
389.1448 | 472.2686 | 379.7482 | 387.7562
390.1448 | 472.2169 | 381.2639 | 388.9024
391.1448 | 472.1789 | 382.7706 | 390.1703
392.1448 | 472.1308 | 383.9273 | 391.1166
393.1448 | 472.0782 | 385.3626 | 392.3638
394.1448 | 472.095 | 386.8465 | 393.2673
395.1448 | 472.093 | 388.558 | 394.0187
396.1448 | 472.0876 | 389.9707 | 395.2405
397.1448 | 472.0581 | 391.4788 | 395.8979
398.1448 | 472.0548 | 393.2755 | 396.6628
399.1448 | 472.073 | 394.3334 | 397.1527
400.1448 | 472.0999 | 396.1718 | 395.3442
401.1448 | 472.1416 | 397.455 | 396.0353
402.1448 | 472.1419 | 398.6899 | 397.4085
403.1448 | 472.2254 | 400.1159 | 398.7167
404.1448 | 472.2606 | 401.8566 | 399.5983
405.1448 | 472.2689 | 403.1627 | 400.5349
406.1448 | 472.2964 | 405.0421 | 401.3681
407.1448 | 472.3315 | 406.5544 | 402.1338
408.1448 | 472.3519 | 408.1119 | 403.0262
409.1448 | 472.3877 | 408.9409 | 403.7952
410.1448 | 472.4419 | 410.7553 | 404.6083
411.1448 | 472.5144 | 412.1138 | 405.4207
412.1448 | 472.4974 | 412.8045 | 406.0339
413.1448 | 472.4665 | 414.2928 | 406.6635
414.1448 | 472.5268 | 415.135 | 407.484
415.1448 | 472.5583 | 416.0671 | 408.1675
416.1448 | 472.5343 | 417.3992 | 408.8635
417.1448 | 472.5829 | 417.8825 | 409.6245
418.1448 | 472.6434 | 419.475 | 410.2275
419.1448 | 472.6682 | 420.1759 | 411.2108
420.1448 | 472.6908 | 421.476 | 411.9907
421.1448 | 472.7307 | 422.4238 | 412.7647
422.1448 | 472.8421 | 423.1838 | 413.4729
423.1448 | 472.8856 | 424.0432 | 414.4392
424.1448 | 472.9144 | 424.795 | 415.1705
425.1448 | 472.919 | 424.8564 | 415.9404
426.1448 | 472.9605 | 425.7901 | 416.7733
427.1448 | 473.0253 | 426.5398 | 417.4207
428.1448 | 473.1246 | 426.6553 | 418.1071
429.1448 | 473.1836 | 427.2692 | 418.7606
430.1448 | 473.2949 | 427.9771 | 419.5796
431.1448 | 473.3837 | 428.344 | 420.4061
432.1448 | 473.4792 | 428.8258 | 421.237
433.1448 | 473.5431 | 429.6015 | 421.922
434.1448 | 473.5976 | 430.0652 | 422.4782
435.1448 | 473.6597 | 430.3719 | 423.0562
436.1448 | 473.6935 | 431.0338 | 423.516
437.1448 | 473.7407 | 431.3831 | 424.1068
438.1448 | 473.7548 | 431.8443 | 424.8656
439.1448 | 473.7829 | 432.192 | 425.5815
440.1448 | 473.8013 | 432.8482 | 426.2427
441.1448 | 473.8392 | 433.4009 | 426.9197
442.1448 | 473.8635 | 434.0904 | 427.53
443.1448 | 473.8916 | 434.6638 | 428.0641
444.1448 | 473.895 | 435.0769 | 428.6424
445.1448 | 473.8582 | 435.684 | 429.1682
446.1448 | 473.8589 | 436.5652 | 429.597
447.1448 | 473.8859 | 437.0863 | 430.123
448.1448 | 473.8691 | 437.6049 | 430.6126
449.1448 | 473.7939 | 438.3415 | 431.0356
450.1448 | 473.7434 | 438.9984 | 431.4398
451.1448 | 473.6508 | 439.6146 | 431.8365
452.1448 | 473.5963 | 440.1954 | 432.1864
453.1448 | 473.5199 | 440.7134 | 432.6093
454.1448 | 473.4479 | 441.3227 | 433.0143
455.1448 | 473.4468 | 442.0686 | 433.3659
456.1448 | 473.389 | 442.7507 | 433.9004
457.1448 | 473.3512 | 443.4093 | 434.2975
458.1448 | 473.3192 | 444.0426 | 434.7101
459.1448 | 473.3171 | 444.6198 | 435.1271
460.1448 | 473.2679 | 445.1989 | 435.6469
461.1448 | 473.2167 | 445.8443 | 436.174
462.1448 | 473.1613 | 446.6104 | 436.6912
463.1448 | 473.0839 | 447.5931 | 437.1742
464.1448 | 473.019 | 448.6162 | 437.6843
465.1448 | 472.9179 | 449.6469 | 438.2266
466.1448 | 472.8185 | 450.5854 | 438.6834
467.1448 | 472.7214 | 451.4499 | 439.172
468.1448 | 472.6603 | 452.6309 | 439.7707
469.1448 | 472.6671 | 453.7682 | 440.3411
470.1448 | 472.7179 | 454.6025 | 441.0412
471.1448 | 472.6921 | 455.6346 | 441.6593
472.1448 | 472.6977 | 456.4793 | 442.292
473.1448 | 472.6808 | 457.3344 | 442.8832
474.1448 | 472.6869 | 458.2946 | 443.5821
475.1448 | 472.7623 | 459.233 | 444.2619
476.1448 | 472.768 | 460.1022 | 444.4792
477.1448 | 472.7921 | 460.911 | 445.1432
478.1448 | 472.8408 | 461.6657 | 445.9114
479.1448 | 472.8641 | 462.4108 | 446.6308
480.1448 | 472.9049 | 463.0489 | 447.3939
481.1448 | 472.884 | 463.7774 | 448.2575
482.1448 | 472.8636 | 464.4825 | 449.0757
483.1448 | 472.8362 | 465.1273 | 449.9257
484.1448 | 472.8294 | 465.6543 | 450.8599
485.1448 | 472.8119 | 466.5552 | 451.7025
486.1448 | 472.8058 | 467.1144 | 452.6616
487.1448 | 472.7992 | 467.8618 | 453.5403
488.1448 | 472.8054 | 468.4928 | 454.4644
489.1448 | 472.8471 | 469.1314 | 455.3302
490.1448 | 472.9273 | 469.7725 | 456.2568
491.1448 | 472.9574 | 470.3828 | 457.1237
492.1448 | 473.0097 | 471.0513 | 458.0255
493.1448 | 472.9809 | 471.8494 | 458.9297
494.1448 | 472.9299 | 472.2874 | 459.7557
495.1448 | 472.9062 | 472.6783 | 460.7064
496.1448 | 472.9091 | 473.2712 | 461.5626
497.1448 | 472.9332 | 473.7019 | 462.4313
498.1448 | 472.9896 | 474.2688 | 463.2703
499.1448 | 473.0016 | 474.6203 | 463.955
500.1448 | 473.0532 | 475.1274 | 464.7442
501.1448 | 473.1221 | 475.722 | 465.6638
502.1448 | 473.2225 | 476.3687 | 466.5799
503.1448 | 473.3218 | 476.8754 | 467.4833
504.1448 | 473.36 | 477.1447 | 468.2065
505.1448 | 473.3774 | 477.5499 | 469.0363
506.1448 | 473.3612 | 477.7896 | 469.8194
507.1448 | 473.3237 | 477.9692 | 470.5105
508.1448 | 473.3043 | 478.1344 | 471.1008
509.1448 | 473.3024 | 478.2784 | 471.8553
510.1448 | 473.2851 | 478.1909 | 472.8345
511.1448 | 473.3394 | 478.2804 | 473.5659
512.1448 | 473.4288 | 478.2525 | 474.2684
513.1448 | 473.5131 | 478.3041 | 474.9295
514.1448 | 473.5247 | 478.7706 | 475.5977
515.1448 | 473.5054 | 479.1382 | 476.2407
516.1448 | 473.5484 | 479.557 | 476.8178
517.1448 | 473.5621 | 479.7842 | 477.3693
518.1448 | 473.512 | 479.74 | 477.8658
519.1448 | 473.4949 | 479.8147 | 478.3042
520.1448 | 473.5612 | 480.0216 | 478.816
521.1448 | 473.6103 | 480.145 | 479.1796
522.1448 | 473.6243 | 480.3152 | 479.6581
523.1448 | 473.5678 | 480.4789 | 480.1576
524.1448 | 473.5639 | 480.5663 | 480.5988
525.1448 | 473.5974 | 480.4764 | 481.0189
526.1448 | 473.6133 | 480.178 | 481.5655
527.1448 | 473.6467 | 480.1876 | 481.8979
528.1448 | 473.7056 | 479.9421 | 482.3726
529.1448 | 473.752 | 480.1528 | 483.2018
530.1448 | 473.7869 | 480.0299 | 483.5341
531.1448 | 473.8363 | 479.8586 | 483.8569
532.1448 | 473.9192 | 479.6348 | 484.1413
533.1448 | 473.978 | 479.4179 | 484.5242
534.1448 | 473.9798 | 479.0475 | 484.9159
535.1448 | 473.9608 | 478.7972 | 485.3835
536.1448 | 473.9623 | 478.6465 | 485.862
537.1448 | 474.0282 | 478.3168 | 486.3452
538.1448 | 474.0627 | 478.2302 | 486.7617
539.1448 | 474.1066 | 477.9318 | 487.0885
540.1448 | 474.0735 | 477.8751 | 487.5019
541.1448 | 474.0712 | 477.7724 | 487.9335
542.1448 | 474.1005 | 477.8791 | 488.4961
543.1448 | 474.1213 | 477.8152 | 488.8018
544.1448 | 474.126 | 477.8458 | 489.1891
545.1448 | 474.1225 | 477.6701 | 489.6486
546.1448 | 474.1638 | 477.3901 | 489.8624
547.1448 | 474.2055 | 477.1089 | 490.2171
548.1448 | 474.1427 | 476.7252 | 490.6255
549.1448 | 474.054 | 476.6791 | 491.1585
550.1448 | 474.009 | 476.7541 | 491.7551
551.1448 | 473.9908 | 476.5687 | 492.1484
552.1448 | 473.9377 | 476.4385 | 492.6469
553.1448 | 473.8974 | 476.3694 | 492.9915
554.1448 | 473.8732 | 476.1517 | 493.4904
555.1448 | 473.86 | 476.0145 | 492.0752
556.1448 | 473.8477 | 476.0749 | 490.7904
557.1448 | 473.7396 | 476.0188 | 491.2662
558.1448 | 473.7302 | 475.8769 | 491.4318
559.1448 | 473.7892 | 476.0327 | 491.381
560.1448 | 473.7846 | 475.6747 | 490.8658
561.1448 | 473.8012 | 475.6034 | 491.2034
562.1448 | 473.8037 | 475.5001 | 491.7089
563.1448 | 473.8077 | 476.0362 | 492.1444
564.1448 | 473.8272 | 475.6742 | 492.185
565.1448 | 473.8852 | 475.9036 | 492.5852
566.1448 | 474.0029 | 475.9523 | 493.1118
567.1448 | 474.0862 | 476.5201 | 493.7766
568.1448 | 474.1182 | 476.6492 | 493.8677
569.1448 | 474.2405 | 476.6384 | 494.1117
570.1448 | 474.2876 | 476.9271 | 494.2819
571.1448 | 474.3085 | 477.0737 | 494.3758
572.1448 | 474.2754 | 477.2177 | 494.5935
573.1448 | 474.282 | 477.3631 | 494.7074
574.1448 | 474.3092 | 476.2245 | 493.1596
575.1448 | 474.3774 | 476.1749 | 493.71
576.1448 | 474.4094 | 476.0614 | 493.9919
577.1448 | 474.4449 | 476.2187 | 494.303
578.1448 | 474.43 | 476.6371 | 495.0032
579.1448 | 474.389 | 476.855 | 495.2538
580.1448 | 474.4519 | 477.1403 | 495.2039
581.1448 | 474.4621 | 477.6644 | 494.8653
582.1448 | 474.439 | 478.0834 | 495.3913
583.1448 | 474.3973 | 478.2653 | 495.1606
584.1448 | 474.3811 | 478.6021 | 495.3245
585.1448 | 474.3736 | 479.4169 | 495.0977
586.1448 | 474.3785 | 479.2112 | 493.856
587.1448 | 474.4079 | 479.6609 | 494.156
588.1448 | 474.425 | 480.64 | 496.0931
589.1448 | 474.399 | 480.4844 | 496.1557
590.1448 | 474.4146 | 480.8846 | 496.5274
591.1448 | 474.3785 | 481.3651 | 496.8167
592.1448 | 474.3433 | 481.5893 | 496.9974
593.1448 | 474.3208 | 481.4615 | 497.3484
594.1448 | 474.2862 | 481.6859 | 497.7027
595.1448 | 474.2814 | 481.8748 | 497.9195
596.1448 | 474.2072 | 482.3051 | 498.5774
597.1448 | 474.113 | 482.707 | 498.5525
598.1448 | 474.0873 | 482.8173 | 498.1762
599.1448 | 474.0241 | 482.9345 | 498.3399
600.1448 | 473.943 | 483.366 | 498.4389
601.1448 | 473.8905 | 483.6504 | 498.599
602.1448 | 473.9341 | 484.5437 | 498.659
603.1448 | 473.8997 | 485.5339 | 499.2154
604.1448 | 473.8995 | 485.8332 | 498.8777
605.1448 | 473.9042 | 486.5101 | 498.5967
606.1448 | 473.9105 | 487.0431 | 498.7774
607.1448 | 473.9313 | 487.5192 | 498.9454
608.1448 | 473.9203 | 487.8699 | 499.0044
609.1448 | 473.9478 | 488.1863 | 497.595
610.1448 | 473.9717 | 488.4911 | 497.3336
611.1448 | 473.9503 | 488.4493 | 497.4889
612.1448 | 473.9233 | 488.4891 | 497.8256
613.1448 | 473.8984 | 488.7529 | 498.3198
614.1448 | 473.8766 | 488.6142 | 498.3318
615.1448 | 473.8688 | 488.4825 | 497.7681
616.1448 | 473.8343 | 488.4196 | 497.782
617.1448 | 473.7998 | 488.5518 | 498.4404
618.1448 | 473.7868 | 488.4727 | 498.6957
619.1448 | 473.7946 | 487.9939 | 498.048
620.1448 | 473.8049 | 488.0132 | 498.2047
621.1448 | 473.749 | 487.3683 | 498.5556
622.1448 | 473.6885 | 487.2892 | 499.1932
623.1448 | 473.6745 | 487.5861 | 499.4073
624.1448 | 473.6731 | 487.6391 | 498.9824
625.1448 | 473.6324 | 487.7721 | 498.8153
626.1448 | 473.5623 | 488.3441 | 499.1196
627.1448 | 473.5675 | 488.5941 | 499.5353
628.1448 | 473.615 | 489.2053 | 499.9214
629.1448 | 473.6616 | 489.6697 | 499.8716
630.1448 | 473.6934 | 489.6586 | 500.0491
631.1448 | 473.7453 | 488.7855 | 499.7356
632.1448 | 473.7986 | 489.8093 | 500.1444
633.1448 | 473.859 | 489.5861 | 500.4286
634.1448 | 473.9442 | 489.2488 | 500.4686
635.1448 | 474.03 | 488.48 | 500.4729
636.1448 | 474.0771 | 488.9061 | 500.7389
637.1448 | 474.1137 | 489.0211 | 500.6203
638.1448 | 474.1697 | 488.8623 | 500.784
639.1448 | 474.203 | 487.9176 | 500.611
640.1448 | 474.2512 | 486.9132 | 500.3992
641.1448 | 474.2483 | 486.3303 | 500.788
642.1448 | 474.2577 | 485.974 | 500.9936
643.1448 | 474.3048 | 485.1416 | 500.6385
644.1448 | 474.4047 | 484.7943 | 501.0772
645.1448 | 474.497 | 484.0604 | 501.516
646.1448 | 474.5268 | 484.5218 | 501.9844
647.1448 | 474.5131 | 484.2713 | 501.9614
648.1448 | 474.4718 | 483.9532 | 502.0221
649.1448 | 474.4527 | 482.7714 | 501.6093
650.1448 | 474.4345 | 481.4252 | 501.6195
651.1448 | 474.4393 | 482.2761 | 501.8062
652.1448 | 474.4871 | 483.3972 | 502.2239
653.1448 | 474.4884 | 483.005 | 502.0798
654.1448 | 474.4665 | 482.7189 | 502.048
655.1448 | 474.5078 | 483.7466 | 502.2906
656.1448 | 474.4645 | 484.128 | 502.5197
657.1448 | 474.4296 | 484.1412 | 502.8005
658.1448 | 474.3674 | 483.9613 | 502.8769
659.1448 | 474.2672 | 483.891 | 502.8279
660.1448 | 474.2849 | 483.149 | 501.4365
661.1448 | 474.1896 | 482.9547 | 502.0845
662.1448 | 474.1044 | 483.6861 | 502.2829
663.1448 | 474.1132 | 484.325 | 502.3045
664.1448 | 474.1036 | 478.0314 | 499.9501
665.1448 | 474.0982 | 479.5546 | 500.5884
666.1448 | 474.0189 | 478.7784 | 500.8904
667.1448 | 473.9316 | 477.7385 | 500.5249
668.1448 | 473.8551 | 477.7335 | 500.7892
669.1448 | 473.8058 | 482.4151 | 501.8969
670.1448 | 473.8497 | 482.1714 | 501.8936
671.1448 | 473.8839 | 481.5949 | 501.186
672.1448 | 473.9867 | 480.7131 | 501.9976
673.1448 | 473.9629 | 478.9804 | 502.2386
674.1448 | 473.8925 | 479.8716 | 502.3483
675.1448 | 473.8319 | 479.3254 | 501.8544
676.1448 | 473.8074 | 480.5939 | 502.1563
677.1448 | 473.7195 | 480.2352 | 503.016
678.1448 | 473.6425 | 480.8511 | 503.7898
679.1448 | 473.5677 | 478.9943 | 503.5675
680.1448 | 473.4861 | 479.8579 | 503.5983
681.1448 | 473.3856 | 479.1856 | 504.219
682.1448 | 473.3289 | 484.0661 | 505.6646
683.1448 | 473.2769 | 479.1941 | 504.7621
684.1448 | 473.2507 | 482.2449 | 505.8069
685.1448 | 473.1524 | 482.0709 | 504.7858
686.1448 | 473.1495 | 477.2997 | 504.0046
687.1448 | 473.0432 | 477.5283 | 503.6051
688.1448 | 472.9483 | 477.0523 | 504.1145
689.1448 | 472.8482 | 476.3719 | 503.6785
690.1448 | 472.7104 | 476.8984 | 503.3358
691.1448 | 472.6963 | 477.1609 | 503.3276
692.1448 | 472.7015 | 477.6245 | 503.5124
693.1448 | 472.6799 | 478.3778 | 502.6425
694.1448 | 472.6105 | 478.5266 | 501.9401
695.1448 | 472.4955 | 479.124 | 502.7555
696.1448 | 472.3979 | 480.2588 | 502.803
697.1448 | 472.3377 | 478.4969 | 494.7904
698.1448 | 472.4196 | 490.5406 | 502.552
699.1448 | 472.4265 | 491.7776 | 503.0126
700.1448 | 472.5535 | 492.9899 | 504.0762
701.1448 | 472.5767 | 494.6149 | 505.0488
702.1448 | 472.5191 | 496.7207 | 506.7612
703.1448 | 472.3275 | 498.5357 | 507.6446
704.1448 | 472.0642 | 499.822 | 508.0376
705.1448 | 471.8166 | 500.3444 | 507.938
706.1448 | 471.5978 | 500.8003 | 508.6638
707.1448 | 471.3631 | 501.9257 | 509.2301
708.1448 | 471.1251 | 502.2735 | 509.5532
709.1448 | 470.8435 | 503.0933 | 510.4358
710.1448 | 470.5182 | 503.6761 | 511.1652
711.1448 | 470.2202 | 505.759 | 511.5819
712.1448 | 469.9216 | 506.9225 | 511.9205
713.1448 | 469.7383 | 508.1474 | 512.9545
714.1448 | 469.5703 | 508.9557 | 514.0609
715.1448 | 469.4337 | 514.3166 | 516.8027
716.1448 | 469.2736 | 552.8666 | 533.87
717.1448 | 469.1337 | 560.7323 | 540.8294
718.1448 | 469.0595 | 564.2711 | 542.5698
719.1448 | 469.0261 | 566.7939 | 542.9942
720.1448 | 469.021 | 554.8662 | 542.7519
721.1448 | 469.0467 | 556.6676 | 543.3192
722.1448 | 469.0592 | 557.7171 | 544.3775
723.1448 | 469.1992 | 562.7936 | 547.1108
724.1448 | 469.2129 | 567.8176 | 550.0392
725.1448 | 469.1965 | 566.1077 | 549.8995
726.1448 | 469.1904 | 568.5121 | 551.6007
727.1448 | 469.2185 | 577.5572 | 556.5538
728.1448 | 469.2859 | 550.482 | 539.0866
729.1448 | 469.393 | 543.3708 | 536.9034
730.1448 | 469.5388 | 583.5697 | 561.5391
731.1448 | 469.643 | 590.9323 | 569.0302
732.1448 | 469.7673 | 533.7685 | 536.6456
733.1448 | 469.9079 | 533.1376 | 537.184
734.1448 | 470.072 | 533.2559 | 537.5924
735.1448 | 470.199 | 533.426 | 537.9834
736.1448 | 470.2171 | 533.8292 | 538.3252
737.1448 | 470.2272 | 533.7921 | 538.6438
738.1448 | 470.3081 | 534.4338 | 539.2599
739.1448 | 470.3941 | 535.0896 | 539.7807
740.1448 | 470.5078 | 535.2967 | 540.2259
741.1448 | 470.6501 | 536.048 | 540.7728
742.1448 | 470.7917 | 535.9502 | 541.2029
743.1448 | 470.9193 | 535.883 | 541.7335
744.1448 | 471.0103 | 536.8021 | 542.2553
745.1448 | 471.083 | 536.841 | 542.7051
746.1448 | 471.1191 | 537.264 | 543.4176
747.1448 | 471.1686 | 537.9547 | 543.9926
748.1448 | 471.2099 | 538.2482 | 544.7075
749.1448 | 471.2647 | 538.9294 | 545.4471
750.1448 | 471.3262 | 539.6026 | 545.9682
751.1448 | 471.3431 | 539.8804 | 546.6681
752.1448 | 471.4082 | 540.2294 | 547.3388
753.1448 | 471.456 | 541.0609 | 548.0564
754.1448 | 471.5 | 541.5862 | 548.8799
755.1448 | 471.5304 | 541.4636 | 549.6688
756.1448 | 471.5561 | 541.5229 | 550.3924
757.1448 | 471.544 | 541.7844 | 551.1198
758.1448 | 471.5366 | 542.2612 | 551.8152
759.1448 | 471.528 | 542.8234 | 552.4374
760.1448 | 471.527 | 543.2733 | 553.0357
761.1448 | 471.5271 | 543.9714 | 553.6523
762.1448 | 471.5157 | 544.4412 | 554.36
763.1448 | 471.4646 | 544.5855 | 554.9485
764.1448 | 471.4431 | 544.789 | 555.4626
765.1448 | 471.4151 | 545.2272 | 556.0526
766.1448 | 471.39 | 545.7874 | 556.827
767.1448 | 471.3973 | 546.2593 | 557.413
768.1448 | 471.3906 | 546.4575 | 557.9395
769.1448 | 471.3602 | 546.3723 | 558.454
770.1448 | 471.3503 | 546.8801 | 559.0747
771.1448 | 471.3823 | 547.3125 | 559.8161
772.1448 | 471.3458 | 547.7087 | 560.4545
773.1448 | 471.324 | 548.1386 | 561.1237
774.1448 | 471.3628 | 548.4324 | 561.8381
775.1448 | 471.3906 | 548.7978 | 562.6021
776.1448 | 471.4076 | 548.8818 | 563.2807
777.1448 | 471.4866 | 549.2006 | 564.0147
778.1448 | 471.5774 | 549.7172 | 564.508
779.1448 | 471.6637 | 550.1479 | 565.2627
780.1448 | 471.7392 | 550.7335 | 565.6859
781.1448 | 471.82 | 550.9744 | 566.4721
782.1448 | 471.8751 | 550.9575 | 566.9584
783.1448 | 471.9504 | 551.4133 | 567.8882
784.1448 | 472.0238 | 551.9253 | 568.5263
785.1448 | 472.0618 | 552.42 | 568.9608
786.1448 | 472.1385 | 552.7008 | 569.3821
787.1448 | 472.2371 | 552.6472 | 569.5071
788.1448 | 472.3092 | 553.0206 | 569.837
789.1448 | 472.3836 | 553.4512 | 570.3063
790.1448 | 472.4299 | 553.8699 | 570.7697
791.1448 | 472.4225 | 554.6565 | 571.2189
792.1448 | 472.444 | 555.4365 | 571.5384
793.1448 | 472.4947 | 555.6335 | 572.0077
794.1448 | 472.5432 | 555.8666 | 572.403
795.1448 | 472.5993 | 555.7422 | 572.6005
796.1448 | 472.6468 | 555.5489 | 573.1677
797.1448 | 472.6867 | 555.4148 | 573.5742
798.1448 | 472.6699 | 555.3267 | 573.9974
799.1448 | 472.6873 | 554.8873 | 574.0938
800.1448 | 472.7249 | 555.1856 | 574.3653
801.1448 | 472.7398 | 555.0673 | 574.7055
802.1448 | 472.7591 | 555.2401 | 574.9905
803.1448 | 472.7478 | 555.6942 | 575.1528
804.1448 | 472.7503 | 555.9114 | 575.5106
805.1448 | 472.7461 | 556.3214 | 575.8835
806.1448 | 472.7066 | 556.5333 | 576.1154
807.1448 | 472.6991 | 556.3198 | 576.0558
808.1448 | 472.6812 | 556.9892 | 576.7026
809.1448 | 472.6701 | 557.5556 | 576.9779
810.1448 | 472.6507 | 558.2758 | 577.1023
811.1448 | 472.5933 | 558.5505 | 577.4054
812.1448 | 472.517 | 559.1286 | 577.825
813.1448 | 472.4811 | 559.5199 | 578.1499
814.1448 | 472.4791 | 559.9731 | 578.5729
815.1448 | 472.4689 | 560.0463 | 578.6919
816.1448 | 472.4376 | 560.5186 | 579.2176
817.1448 | 472.3852 | 560.9347 | 579.5203
818.1448 | 472.3443 | 561.1024 | 579.96
819.1448 | 472.3271 | 561.6628 | 580.5719
820.1448 | 472.3161 | 562.0385 | 581.0512
821.1448 | 472.3379 | 562.5308 | 581.4078
822.1448 | 472.3029 | 562.6745 | 581.4134
823.1448 | 472.2511 | 563.2518 | 581.7433
824.1448 | 472.2405 | 563.3978 | 582.028
825.1448 | 472.2777 | 563.765 | 582.2478
826.1448 | 472.2889 | 564.4191 | 582.4844
827.1448 | 472.2658 | 564.6056 | 582.6232
828.1448 | 472.1859 | 564.9928 | 582.5007
829.1448 | 472.1691 | 565.2785 | 582.4602
830.1448 | 472.1979 | 565.1124 | 582.6281
831.1448 | 472.2275 | 565.2792 | 582.7466
832.1448 | 472.2514 | 565.2551 | 582.8054
833.1448 | 472.2745 | 565.1178 | 582.7101
834.1448 | 472.307 | 564.3047 | 582.4079
835.1448 | 472.3101 | 563.969 | 582.2907
836.1448 | 472.3532 | 564.0082 | 582.1796
837.1448 | 472.431 | 564.3431 | 582.1984
838.1448 | 472.4908 | 564.7939 | 582.1245
839.1448 | 472.5805 | 564.9739 | 581.994
840.1448 | 472.6262 | 565.4342 | 582.2092
841.1448 | 472.6476 | 565.4818 | 581.9635
842.1448 | 472.6765 | 565.9975 | 582.1421
843.1448 | 472.7205 | 566.447 | 582.3545
844.1448 | 472.7637 | 565.6119 | 581.8563
845.1448 | 472.7827 | 565.5948 | 581.8306
846.1448 | 472.8541 | 565.7922 | 582.031
847.1448 | 472.8744 | 566.1683 | 582.1443
848.1448 | 472.9121 | 566.5 | 582.3863
849.1448 | 472.9702 | 565.8015 | 582.5495
850.1448 | 472.9906 | 565.783 | 582.7068
851.1448 | 472.9995 | 566.5234 | 583.3531
852.1448 | 473.0377 | 565.9819 | 583.495
853.1448 | 473.0287 | 565.2288 | 583.5557
854.1448 | 473.0364 | 565.6903 | 584.301
855.1448 | 473.0792 | 565.1527 | 584.1298
856.1448 | 473.104 | 564.9464 | 584.719
857.1448 | 473.0957 | 564.913 | 585.3005
858.1448 | 473.0976 | 565.3119 | 585.9068
859.1448 | 473.0742 | 565.5631 | 586.5126
860.1448 | 473.0746 | 566.0545 | 587.1537
861.1448 | 473.0401 | 565.7219 | 587.2613
862.1448 | 473.0011 | 566.533 | 587.7923
863.1448 | 473.0046 | 566.7977 | 588.1354
864.1448 | 473.0128 | 566.9212 | 588.4719
865.1448 | 472.9796 | 567.0556 | 588.524
866.1448 | 472.941 | 567.056 | 588.4242
867.1448 | 472.9446 | 566.9706 | 588.044
868.1448 | 473.0002 | 566.5342 | 587.6665
869.1448 | 473.0558 | 567.2478 | 587.9875
870.1448 | 473.1413 | 567.5336 | 588.013
871.1448 | 473.1697 | 567.9032 | 588.1981
872.1448 | 473.1718 | 568.3267 | 588.4205
873.1448 | 473.2282 | 568.4723 | 588.7676
874.1448 | 473.261 | 568.7789 | 589.022
875.1448 | 473.2444 | 568.3603 | 588.7746
876.1448 | 473.2144 | 568.6703 | 589.1804
877.1448 | 473.2612 | 569.1461 | 589.6922
878.1448 | 473.3282 | 569.449 | 590.0327
879.1448 | 473.4169 | 569.0723 | 590.0435
880.1448 | 473.4695 | 570.1833 | 590.9361
881.1448 | 473.5506 | 570.4162 | 591.1515
882.1448 | 473.5546 | 570.7495 | 591.5014
883.1448 | 473.5712 | 571.4351 | 592.2151
884.1448 | 473.6188 | 570.3906 | 591.8781
885.1448 | 473.588 | 572.0042 | 593.0095
886.1448 | 473.5887 | 571.2317 | 592.6973
887.1448 | 473.5935 | 572.0866 | 593.588
888.1448 | 473.6145 | 572.1976 | 594.0535
889.1448 | 473.5683 | 572.9552 | 594.7333
890.1448 | 473.5788 | 573.552 | 595.307
891.1448 | 473.5924 | 573.4724 | 595.5956
892.1448 | 473.6206 | 573.5681 | 595.7561
893.1448 | 473.5897 | 573.4872 | 595.8417
894.1448 | 473.5272 | 572.8356 | 595.6756
895.1448 | 473.4888 | 572.8468 | 595.7879
896.1448 | 473.4648 | 574.5358 | 597.3334
897.1448 | 473.4461 | 574.626 | 597.5626
898.1448 | 473.3876 | 574.5973 | 597.7325
899.1448 | 473.3227 | 574.8887 | 598.1991
900.1448 | 473.2841 | 574.0887 | 597.9389
901.1448 | 473.2443 | 575.2329 | 599.2867
902.1448 | 473.1888 | 575.7136 | 600.0289
903.1448 | 473.135 | 574.6464 | 599.5483
904.1448 | 473.0867 | 575.3186 | 600.3231
905.1448 | 473.0412 | 576.3717 | 601.3405
906.1448 | 472.98 | 575.9516 | 601.2206
907.1448 | 472.9094 | 574.7011 | 600.4619
908.1448 | 472.9093 | 576.9592 | 602.309
909.1448 | 472.8972 | 577.0967 | 602.6648
910.1448 | 472.8188 | 577.3056 | 603.2245
911.1448 | 472.8067 | 576.7487 | 602.783
912.1448 | 472.7604 | 577.4954 | 603.4794