## Test Conditions
DESIREE-FIRE Test Number 5 - Circuit Data Data Only
Test Date: | 2009-07-22
DCSim DAQ Start Time | 10:15
DCSim Time for Synchronization | 10:28
Heat Source Synchronization | 5:28 | hours:minutes:seconds
Heat Source DAQ Start Time | 10:23
Fire Time | 10:29
Offset | 0:14 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 837 | seconds
Heat Source Offset | 0:06 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 370 | seconds
Heat Source Stop Time | 10:49
Test Duration | 0:20 | hours:minutes:seconds
| 1215 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
Large Coil | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.15625 | 123.1659 | -58.2321 | 64.7873 | 0.5491 | -0.00081686 | 0.061742 | -0.0050682 | 0.071807 | 0.0086597 | -0.0060942 | 0.29095 | 0.003288 | 0.069454 | 0.060993 | 0.0011309 | 0.010796 | 64.8193 | -58.2687 | -0.1236 | -58.4518 | 64.7598 | -58.255 | -58.2642 | -58.1863 | -0.068665 | -58.5388 | 64.801 | 64.7095 | -58.1909 | -58.3374 | -0.022888 | -0.032043 | -0.027465 | -0.036621 | -0.21973 | -0.18768 | 0.032044 | 0.041199 | -0.10528 | 0.013733 | 0.045777 | -0.3067 | -0.20142 | -0.077819 | 122.9919 | 123.0515 | 58.1085 | -123.0515 | 123.0331 | 122.9416 | 58.1635 | -123.1247
0.84375 | 123.2208 | -58.1909 | 64.7736 | 0.41177 | -0.015771 | 0.070287 | -0.0093412 | 0.056853 | -0.029792 | 0.0013818 | 0.44354 | 0.006492 | 0.055569 | 0.06847 | -0.0052781 | 0.0097279 | 64.8468 | -58.1589 | -0.018311 | -58.4015 | 64.7369 | -58.2047 | -58.2321 | -58.1314 | 0.050354 | -58.4427 | 64.7781 | 64.6912 | -58.1818 | -58.3008 | -0.013733 | -0.041199 | -0.036622 | 0.032043 | -0.21057 | -0.16937 | 0.073242 | 0.009155 | -0.10986 | 0.004577 | 0.059509 | -0.25177 | -0.14191 | -0.082398 | 122.9279 | 123.0377 | 58.1726 | -123.0057 | 122.9691 | 122.8821 | 58.2413 | -123.0743
1.8438 | 123.2666 | -58.1909 | 64.7598 | 0.076074 | -0.036065 | 0.078832 | -0.0061362 | 0.076079 | -0.024451 | -0.0092992 | 0.13837 | -0.005257 | 0.065182 | 0.062061 | -0.0084821 | 0.012933 | 64.8743 | -58.1223 | 0.009155 | -58.374 | 64.7324 | -58.2047 | -58.2596 | -58.0902 | 0.10071 | -58.3969 | 64.7736 | 64.7232 | -58.1589 | -58.2962 | -0.013733 | -0.068665 | -0.027466 | 0.068665 | -0.1831 | -0.11444 | 0.11444 | 0.032043 | -0.10529 | 0.013733 | 0.10071 | -0.20599 | -0.10071 | -0.036621 | 122.9233 | 123.0652 | 58.2001 | -123.0194 | 122.9645 | 122.9141 | 58.2916 | -123.056
2.8438 | 123.1613 | -58.2092 | 64.7873 | 0.091333 | 0.010932 | 0.060674 | 0.0077488 | 0.078215 | 0.024682 | -0.0028902 | -0.075256 | 0.007561 | 0.060909 | 0.066333 | 0.0086079 | -0.0030891 | 64.8926 | -58.2001 | -0.018311 | -58.4198 | 64.7644 | -58.2275 | -58.2596 | -58.1497 | -0.004578 | -58.5068 | 64.801 | 64.7141 | -58.2184 | -58.3328 | -0.01831 | -0.050354 | -0.022888 | 0.009156 | -0.21057 | -0.16022 | 0.10529 | -0.009155 | -0.1236 | 0.013733 | 0.05951 | -0.29755 | -0.17395 | -0.073242 | 122.9736 | 123.1018 | 58.1909 | -123.0469 | 123.0103 | 122.9233 | 58.2047 | -123.1201
3.8438 | 123.1934 | -58.2001 | 64.8148 | 0.030298 | -0.0029529 | 0.058538 | 0.0013408 | 0.051512 | 0.014001 | -0.0028902 | 0.0010378 | 8.4049e-05 | 0.056637 | 0.072742 | -0.0031411 | 0.0033199 | 64.9017 | -58.1863 | -0.004578 | -58.4106 | 64.7827 | -58.223 | -58.2367 | -58.1406 | 0.032043 | -58.5159 | 64.8193 | 64.7186 | -58.2001 | -58.3008 | -0.022888 | -0.036621 | -0.032043 | 0.013733 | -0.21057 | -0.17395 | 0.086975 | 0 | -0.10071 | 0.004578 | 0.059509 | -0.31586 | -0.21515 | -0.09613 | 122.9828 | 123.1018 | 58.1955 | -123.0515 | 123.0194 | 122.9187 | 58.2321 | -123.1155
4.8438 | 123.1796 | -58.2092 | 64.7964 | 0.15237 | 0.014137 | 0.069219 | 0.012022 | 0.065398 | 0.0086597 | 0.017404 | 0.016297 | 0.011833 | 0.069454 | 0.074878 | 0.0086079 | 0.00011494 | 64.8376 | -58.2047 | -0.059509 | -58.4244 | 64.7552 | -58.2275 | -58.2733 | -58.1726 | -0.018311 | -58.5388 | 64.8331 | 64.7141 | -58.2184 | -58.3328 | -0.01831 | -0.064086 | -0.041199 | 0.004578 | -0.21515 | -0.15106 | 0.041198 | -0.009155 | -0.1236 | 0.036621 | 0.036622 | -0.32959 | -0.20599 | -0.082398 | 122.9645 | 123.0469 | 58.1497 | -123.0698 | 123.0423 | 122.9233 | 58.1909 | -123.1293
5.8594 | 123.1613 | -58.2092 | 64.8376 | -0.3054 | -0.026452 | 0.0799 | -0.0093412 | 0.062194 | -0.0094983 | 0.00031381 | -0.22784 | 0.005424 | 0.06625 | 0.053516 | -0.0010051 | 0.0075919 | 64.856 | -58.1406 | 0.022888 | -58.3969 | 64.801 | -58.1818 | -58.2413 | -58.1451 | 0.07782 | -58.4702 | 64.8422 | 64.7598 | -58.1818 | -58.2825 | 0.027466 | -0.032043 | -0.036621 | 0.068665 | -0.18768 | -0.15564 | 0.018311 | 0.027466 | -0.073242 | 0.004578 | 0.064087 | -0.26093 | -0.18768 | -0.077819 | 123.0103 | 123.0652 | 58.2321 | -123.0789 | 123.0515 | 122.9691 | 58.287 | -123.1201
6.8438 | 123.2529 | -58.1818 | 64.7598 | 0.36599 | -0.02752 | 0.073492 | -0.014681 | 0.063262 | -0.025519 | -0.0092992 | 0.56561 | -0.010597 | 0.050228 | 0.072742 | 0.0043349 | 0.0011829 | 64.8697 | -58.1131 | -0.013733 | -58.4015 | 64.7049 | -58.2092 | -58.2367 | -58.1039 | 0.050354 | -58.4473 | 64.7736 | 64.6637 | -58.2001 | -58.3237 | -0.027466 | -0.054931 | -0.054932 | 0.068665 | -0.21973 | -0.16479 | 0.10986 | -0.01831 | -0.14191 | 0.013733 | 0.07782 | -0.2655 | -0.1236 | -0.096131 | 122.8867 | 123.0515 | 58.168 | -122.9965 | 122.9553 | 122.8455 | 58.2321 | -123.0835
7.8438 | 123.1613 | -58.2047 | 64.8148 | 0.12185 | 0.022682 | 0.077764 | 0.0066808 | 0.065398 | 0.026818 | -0.0018222 | -0.059997 | 0.001152 | 0.082272 | 0.058857 | -0.0020731 | -0.0030891 | 64.8972 | -58.1497 | 0 | -58.4015 | 64.7873 | -58.2092 | -58.2413 | -58.1268 | 0.032043 | -58.4839 | 64.8331 | 64.7095 | -58.2001 | -58.3099 | -0.004578 | -0.036621 | -0.027466 | 0.054932 | -0.19684 | -0.16022 | 0.082398 | 0.004578 | -0.10529 | 0.018311 | 0.07782 | -0.27924 | -0.17395 | -0.10528 | 122.9919 | 123.1018 | 58.2047 | -123.056 | 123.0377 | 122.9141 | 58.2367 | -123.1247
8.8438 | 123.1842 | -58.2138 | 64.7919 | -0.030737 | 0.021614 | 0.051061 | 0.0013408 | 0.060057 | 0.0075917 | 0.00031381 | -0.13629 | 0.001152 | 0.067318 | 0.054584 | 0.0043349 | 0.0022509 | 64.9017 | -58.1589 | 0.013733 | -58.3923 | 64.7552 | -58.2184 | -58.2504 | -58.1406 | 0.059509 | -58.4885 | 64.8102 | 64.7186 | -58.2001 | -58.3191 | -0.004578 | -0.036621 | -0.036621 | 0.054931 | -0.17853 | -0.14191 | 0.10986 | 0.013733 | -0.10529 | 0.018311 | 0.073242 | -0.27466 | -0.16937 | -0.073242 | 122.9691 | 123.1155 | 58.2275 | -123.0423 | 123.024 | 122.9324 | 58.2733 | -123.111
9.8438 | 123.1705 | -58.2138 | 64.8102 | 0.091333 | 0.0077281 | 0.064947 | 0.0066808 | 0.062194 | 0.0054557 | 0.0056548 | 0.062074 | 0.003288 | 0.06625 | 0.060993 | 0.0032669 | 0.0043879 | 64.8514 | -58.1955 | -0.032043 | -58.4015 | 64.7552 | -58.2138 | -58.2504 | -58.1635 | 0.004578 | -58.5251 | 64.8102 | 64.7324 | -58.2184 | -58.3466 | 0 | -0.036621 | -0.054932 | 0.01831 | -0.18768 | -0.15106 | 0.041198 | -0.004578 | -0.13275 | 0 | 0.050354 | -0.31128 | -0.17853 | -0.07782 | 122.9691 | 123.0652 | 58.1818 | -123.0606 | 123.024 | 122.9462 | 58.2184 | -123.1567
10.8438 | 123.3124 | -58.1772 | 64.7369 | 0.56436 | -0.00081686 | 0.060674 | -0.014681 | 0.076079 | -0.0041573 | -0.0039582 | 0.42828 | -0.003121 | 0.058773 | 0.059925 | -0.0084821 | 0.0011829 | 64.8422 | -58.1635 | -0.054932 | -58.4152 | 64.7324 | -58.2367 | -58.2687 | -58.1131 | 0.027466 | -58.4473 | 64.769 | 64.6866 | -58.1955 | -58.3008 | -0.059509 | -0.091553 | -0.004577 | 0.013733 | -0.23804 | -0.14648 | 0.10529 | -0.018311 | -0.1236 | 0.032044 | 0.064087 | -0.27008 | -0.14648 | -0.050354 | 122.9095 | 123.0194 | 58.1223 | -123.0057 | 122.9462 | 122.8638 | 58.2047 | -123.0377
11.8438 | 123.2391 | -58.2047 | 64.769 | 0.44228 | -0.014702 | 0.072424 | -0.0040002 | 0.067534 | -0.026587 | -0.0060942 | 0.39777 | 0.008629 | 0.039547 | 0.050312 | -0.0052781 | 0.0065239 | 64.8376 | -58.168 | -0.036621 | -58.4106 | 64.7186 | -58.2092 | -58.2367 | -58.1085 | 0.027466 | -58.4702 | 64.7507 | 64.7003 | -58.1909 | -58.3191 | -0.004578 | -0.032043 | -0.050354 | 0.036621 | -0.20599 | -0.17395 | 0.068664 | 0.013733 | -0.11444 | -0.018311 | 0.09613 | -0.2655 | -0.15106 | -0.068665 | 122.9233 | 123.0423 | 58.168 | -123.0057 | 122.9553 | 122.905 | 58.2321 | -123.0881
12.8438 | 123.1567 | -58.2138 | 64.7919 | 0.18289 | 0.0098641 | 0.068151 | 0.0088168 | 0.06967 | 0.015069 | 0.0045868 | 0.092591 | 0.006492 | 0.065182 | 0.052448 | -0.0010051 | 0.00011494 | 64.8651 | -58.2047 | -0.036621 | -58.4198 | 64.7644 | -58.2321 | -58.2458 | -58.1726 | 0.009155 | -58.5205 | 64.8239 | 64.7369 | -58.2184 | -58.342 | -0.018311 | -0.032044 | -0.027466 | 0.009155 | -0.20599 | -0.17395 | 0.073242 | -0.004578 | -0.12817 | 0.032044 | 0.041199 | -0.3067 | -0.17853 | -0.054932 | 122.9782 | 123.0789 | 58.1772 | -123.0377 | 123.0377 | 122.9507 | 58.223 | -123.1338
13.8438 | 123.1522 | -58.2458 | 64.7964 | 0.19814 | 0.015205 | 0.067083 | 0.0066808 | 0.06967 | 0.0043877 | 0.0056548 | 0.062074 | 0.007561 | 0.063046 | 0.057788 | 0.0032669 | 0.0011829 | 64.8285 | -58.2642 | -0.07782 | -58.4427 | 64.7644 | -58.255 | -58.2687 | -58.2047 | -0.045776 | -58.5434 | 64.8239 | 64.7598 | -58.2138 | -58.3557 | -0.009155 | -0.022888 | -0.032044 | -0.01831 | -0.19684 | -0.17395 | 0.032043 | 0.032044 | -0.10986 | 0.027466 | 0.041199 | -0.29755 | -0.18768 | -0.036621 | 123.0103 | 123.0743 | 58.168 | -123.0652 | 123.0698 | 123.0057 | 58.2001 | -123.1522
14.8438 | 123.2071 | -58.2092 | 64.7964 | 0.10659 | -0.0029529 | 0.070287 | -0.0050682 | 0.075011 | 0.012933 | -0.0050262 | -0.16681 | 0.00222 | 0.067318 | 0.064197 | -0.0031411 | -0.0084301 | 64.8972 | -58.1543 | 0.013733 | -58.3878 | 64.769 | -58.2184 | -58.2596 | -58.1177 | 0.082397 | -58.4747 | 64.8102 | 64.7644 | -58.1955 | -58.3191 | -0.009155 | -0.050354 | -0.027466 | 0.054932 | -0.17853 | -0.12817 | 0.10071 | 0.013733 | -0.10986 | 0.013733 | 0.091553 | -0.2655 | -0.15564 | -0.032044 | 122.9782 | 123.1064 | 58.223 | -123.056 | 123.0194 | 122.9736 | 58.2916 | -123.1155
15.8438 | 123.2437 | -58.2047 | 64.7598 | 0.5491 | -0.0093619 | 0.080969 | 0.0088168 | 0.067534 | 0.0022517 | 0.0013818 | 0.47406 | 0.005424 | 0.068386 | 0.062061 | 0.0032669 | 0.00011494 | 64.8239 | -58.2184 | -0.091553 | -58.4335 | 64.7415 | -58.2413 | -58.2504 | -58.1268 | -0.009155 | -58.4702 | 64.7827 | 64.6912 | -58.223 | -58.3191 | -0.036621 | -0.045776 | -0.018311 | -0.013733 | -0.22888 | -0.18311 | 0.064087 | -0.01831 | -0.11444 | 0.022888 | 0.07782 | -0.2655 | -0.15106 | -0.068665 | 122.9462 | 123.0286 | 58.1131 | -123.0103 | 122.9874 | 122.8958 | 58.1955 | -123.0789
16.8438 | 123.2803 | -58.1863 | 64.7507 | 0.4728 | -0.013634 | 0.067083 | -0.0072042 | 0.075011 | -0.016974 | -0.0028902 | 0.59613 | -0.004189 | 0.06625 | 0.077014 | -0.0031411 | 0.0097279 | 64.8834 | -58.1314 | 0 | -58.3923 | 64.682 | -58.1863 | -58.255 | -58.0902 | 0.064087 | -58.4244 | 64.7507 | 64.6866 | -58.1955 | -58.3237 | 0 | -0.068665 | -0.068664 | 0.054931 | -0.20599 | -0.13733 | 0.13275 | -0.009156 | -0.13733 | 0 | 0.09613 | -0.23804 | -0.10071 | -0.064087 | 122.8683 | 123.0698 | 58.1863 | -123.0057 | 122.937 | 122.8729 | 58.2504 | -123.0743
17.8438 | 123.2025 | -58.1955 | 64.801 | -0.15281 | -0.0029529 | 0.073492 | 0.00027184 | 0.06967 | 0.0097277 | 0.0013818 | -0.22784 | 0.00222 | 0.055569 | 0.054584 | 0.0086079 | -0.0062931 | 64.8605 | -58.1818 | -0.013733 | -58.3878 | 64.7736 | -58.2138 | -58.2413 | -58.1268 | 0.086975 | -58.4702 | 64.8422 | 64.7736 | -58.1863 | -58.3145 | -0.01831 | -0.045776 | -0.027465 | 0.013733 | -0.19226 | -0.14648 | 0.05951 | 0.009156 | -0.11902 | 0.041199 | 0.068665 | -0.27466 | -0.15564 | -0.027465 | 122.9691 | 123.056 | 58.1818 | -123.0423 | 123.0377 | 122.9691 | 58.2825 | -123.1155
18.8438 | 123.1888 | -58.1818 | 64.801 | 0.091333 | 0.025886 | 0.059606 | 0.01309 | 0.06433 | 0.014001 | 0.0035188 | -0.25836 | 0.005424 | 0.065182 | 0.067401 | 0.0064719 | -0.00095306 | 64.9063 | -58.168 | 0.004578 | -58.3878 | 64.7827 | -58.2275 | -58.2733 | -58.1268 | 0.091553 | -58.4793 | 64.8102 | 64.7369 | -58.2047 | -58.3054 | -0.045776 | -0.091552 | -0.01831 | 0.013733 | -0.20599 | -0.11444 | 0.10529 | -0.022888 | -0.1236 | 0.009156 | 0.054932 | -0.29755 | -0.17395 | -0.064087 | 122.9645 | 123.0881 | 58.1863 | -123.0743 | 122.9919 | 122.9187 | 58.2733 | -123.1064
19.8438 | 123.2162 | -58.2001 | 64.801 | -0.076513 | -0.014702 | 0.061742 | -0.0082732 | 0.066466 | 0.0075917 | 0.0024508 | 0.046815 | 0.003288 | 0.060909 | 0.066333 | -0.0010051 | -0.0020211 | 64.856 | -58.1726 | -0.009155 | -58.3878 | 64.7827 | -58.2184 | -58.2458 | -58.1589 | 0.07782 | -58.4793 | 64.8056 | 64.7232 | -58.1863 | -58.3237 | -0.018311 | -0.045777 | -0.01831 | 0.027466 | -0.18768 | -0.14191 | 0.054932 | 0.013733 | -0.1236 | 0.004578 | 0.041198 | -0.27924 | -0.15564 | -0.077819 | 122.9828 | 123.056 | 58.1909 | -123.0469 | 123.0057 | 122.9233 | 58.2779 | -123.1247
20.8438 | 123.1613 | -58.223 | 64.7873 | 0.18289 | -0.0040209 | 0.061742 | 0.0066808 | 0.068602 | 0.02575 | -0.00075419 | 0.031556 | 0.008629 | 0.068386 | 0.075946 | 0.0043349 | -0.0030891 | 64.8514 | -58.2001 | -0.036621 | -58.4198 | 64.7919 | -58.2321 | -58.2733 | -58.1635 | -0.009155 | -58.5342 | 64.801 | 64.7415 | -58.223 | -58.3237 | -0.009156 | -0.050354 | 0.004578 | 0.022888 | -0.19684 | -0.14649 | 0.064087 | 0 | -0.10071 | 0.013733 | 0.059509 | -0.31128 | -0.21057 | -0.045776 | 123.0148 | 123.0743 | 58.1863 | -123.0606 | 123.024 | 122.9645 | 58.2138 | -123.111
21.8438 | 123.2529 | -58.1863 | 64.7644 | 0.59487 | -0.011498 | 0.063879 | -0.014681 | 0.073943 | -0.020179 | -0.0028902 | 0.59613 | -0.003121 | 0.04916 | 0.066333 | -0.0031411 | 0.014001 | 64.8697 | -58.1131 | 0.022888 | -58.3878 | 64.7141 | -58.223 | -58.223 | -58.0856 | 0.059509 | -58.4198 | 64.7598 | 64.6912 | -58.1909 | -58.2962 | -0.036621 | -0.036621 | -0.050354 | 0.073242 | -0.20142 | -0.1648 | 0.10529 | -0.004578 | -0.10986 | -0.004577 | 0.10071 | -0.23346 | -0.1236 | -0.073242 | 122.9004 | 123.056 | 58.2092 | -122.9874 | 122.9462 | 122.8775 | 58.2458 | -123.0606
22.8438 | 123.2025 | -58.1863 | 64.7919 | -0.16807 | 0.013069 | 0.061742 | 0.0045448 | 0.06433 | 0.010797 | -0.0028902 | -0.3194 | 0.006492 | 0.06625 | 0.071674 | 0.0064719 | 0.0033199 | 64.8788 | -58.1635 | 0.009155 | -58.3786 | 64.7827 | -58.2321 | -58.223 | -58.1497 | 0.073242 | -58.4747 | 64.8102 | 64.7598 | -58.1909 | -58.3054 | -0.045777 | -0.036621 | -0.009155 | 0.022888 | -0.19226 | -0.15564 | 0.086975 | -0.004578 | -0.11902 | 0.018311 | 0.036621 | -0.28839 | -0.16937 | -0.032043 | 122.9691 | 123.0652 | 58.1955 | -123.0148 | 122.9965 | 122.9462 | 58.2596 | -123.0972
23.8438 | 123.2117 | -58.1909 | 64.8148 | -0.19858 | 0.015205 | 0.075628 | 0.0034768 | 0.06433 | 0.00011475 | 0.0035188 | -0.28888 | 0.007561 | 0.061977 | 0.05138 | 0.0011309 | 0.0086599 | 64.8651 | -58.1818 | 0.009155 | -58.374 | 64.7736 | -58.2138 | -58.2504 | -58.1451 | 0.068665 | -58.4793 | 64.8331 | 64.7552 | -58.2092 | -58.3237 | -0.022888 | -0.059509 | -0.041198 | 0.009155 | -0.1831 | -0.1236 | 0.050354 | -0.018311 | -0.13275 | 0.018311 | 0.045776 | -0.28839 | -0.15564 | -0.059509 | 122.9645 | 123.056 | 58.2001 | -123.0652 | 123.024 | 122.9462 | 58.2596 | -123.1384
24.8438 | 123.1796 | -58.2092 | 64.7919 | 0.060816 | 0.016273 | 0.066015 | -0.0061362 | 0.076079 | 0.012933 | 0.010995 | 0.031556 | 0.001152 | 0.059841 | 0.058857 | 0.0011309 | 0.0011829 | 64.856 | -58.1635 | -0.009155 | -58.429 | 64.7736 | -58.2367 | -58.2596 | -58.1543 | 0.013733 | -58.4885 | 64.8102 | 64.7415 | -58.2047 | -58.3374 | -0.027465 | -0.050354 | -0.01831 | 0.045777 | -0.21973 | -0.16937 | 0.064087 | 0.004578 | -0.12817 | 0.018311 | 0.054932 | -0.27923 | -0.15106 | -0.050354 | 122.9828 | 123.0652 | 58.2001 | -123.0515 | 123.0194 | 122.9507 | 58.223 | -123.1293
25.8438 | 123.1384 | -58.2138 | 64.7964 | 0.25918 | 0.0098641 | 0.066015 | -0.0040002 | 0.080351 | 0.0086597 | 0.0142 | 0.077332 | -0.00098395 | 0.074795 | 0.066333 | 0.0054039 | -0.011634 | 64.8193 | -58.2138 | -0.073242 | -58.4335 | 64.7598 | -58.2275 | -58.2733 | -58.2047 | -0.041199 | -58.5663 | 64.8056 | 64.7507 | -58.2184 | -58.3374 | -0.013733 | -0.059509 | -0.036621 | 0 | -0.21973 | -0.16022 | 0.022888 | -0.004578 | -0.1236 | 0.009155 | 0.009155 | -0.35248 | -0.22888 | -0.045777 | 122.9736 | 123.0331 | 58.1406 | -123.0698 | 123.0194 | 122.9645 | 58.1726 | -123.1338
26.8438 | 123.1888 | -58.2138 | 64.769 | 0.44228 | 0.012 | 0.071355 | 0.0024088 | 0.067534 | 0.0011837 | 0.0067228 | 0.47406 | 0.001152 | 0.063046 | 0.057788 | 0.0032669 | 0.011864 | 64.801 | -58.2367 | -0.12817 | -58.4564 | 64.769 | -58.255 | -58.2825 | -58.168 | -0.050354 | -58.5159 | 64.769 | 64.7232 | -58.2321 | -58.3466 | -0.041199 | -0.068665 | 0 | -0.022888 | -0.24262 | -0.17395 | 0.032043 | -0.018311 | -0.13275 | 0 | 0.045776 | -0.30212 | -0.16937 | -0.045776 | 122.9828 | 123.0148 | 58.0856 | -123.0515 | 122.9828 | 122.937 | 58.1635 | -123.1155
27.8438 | 123.1934 | -58.2047 | 64.7919 | 0.10659 | 0.0087961 | 0.07456 | -0.0072042 | 0.072875 | 0.0011837 | 0.010995 | 0.031556 | -0.002053 | 0.058773 | 0.065265 | 0.0086079 | 0.0011829 | 64.888 | -58.1772 | -0.022888 | -58.4015 | 64.7598 | -58.2275 | -58.2504 | -58.1451 | 0.050354 | -58.4885 | 64.7827 | 64.7461 | -58.1863 | -58.3145 | -0.022888 | -0.045776 | -0.032043 | 0.027466 | -0.19684 | -0.15106 | 0.09613 | 0.018311 | -0.10986 | -0.009155 | 0.059509 | -0.28381 | -0.17395 | -0.045776 | 122.9645 | 123.0927 | 58.1818 | -123.0423 | 122.9874 | 122.9507 | 58.255 | -123.1064
28.8438 | 123.1796 | -58.1818 | 64.8148 | 0.030298 | 0.020545 | 0.060674 | 0.0034768 | 0.078215 | 0.0086597 | 0.0024508 | 0.016297 | -0.00098395 | 0.061977 | 0.060993 | 0.010744 | 0.0033199 | 64.8743 | -58.1635 | -0.009155 | -58.3969 | 64.7461 | -58.2275 | -58.2413 | -58.136 | 0.045776 | -58.4885 | 64.8056 | 64.7507 | -58.1909 | -58.3237 | -0.045776 | -0.059509 | -0.068664 | 0.018311 | -0.21515 | -0.15564 | 0.05951 | -0.009155 | -0.14191 | -0.009155 | 0.045777 | -0.3067 | -0.16479 | -0.064087 | 122.9279 | 123.056 | 58.1726 | -123.056 | 122.9874 | 122.9324 | 58.2275 | -123.1384
29.8438 | 123.1796 | -58.2047 | 64.8056 | 0.30496 | 0.0087961 | 0.063879 | -0.0018642 | 0.063262 | 0.017205 | 0.0099268 | 0.15363 | 0.007561 | 0.060909 | 0.062061 | 0.0032669 | 0.00011494 | 64.801 | -58.2321 | -0.073242 | -58.4244 | 64.7827 | -58.2275 | -58.2642 | -58.1818 | -0.022888 | -58.5434 | 64.8331 | 64.7552 | -58.2184 | -58.3237 | -0.022888 | -0.059509 | -0.022888 | -0.027466 | -0.21973 | -0.16022 | -0.004578 | -0.013733 | -0.11902 | 0.027466 | 0.022888 | -0.33875 | -0.21973 | -0.050354 | 122.9874 | 123.0057 | 58.1314 | -123.0698 | 123.0377 | 122.9599 | 58.1818 | -123.1293
30.8438 | 123.1888 | -58.2001 | 64.8056 | -0.82419 | -0.0040209 | 0.053198 | 0.0088168 | 0.084624 | 0.0054557 | -0.0028902 | -0.16681 | 0.00222 | 0.064114 | 0.059925 | 0.0054039 | 0.0065239 | 64.8514 | -58.168 | 0.009155 | -58.3649 | 64.8056 | -58.2138 | -58.2321 | -58.136 | 0.086975 | -58.4564 | 64.8102 | 64.7507 | -58.2001 | -58.2825 | -0.013733 | -0.032044 | 0 | 0.032043 | -0.16479 | -0.13275 | 0.045776 | 0 | -0.082398 | 0.004578 | 0.064087 | -0.25635 | -0.17395 | -0.054932 | 123.0057 | 123.0515 | 58.2092 | -123.0377 | 123.0103 | 122.9507 | 58.287 | -123.0881
31.8438 | 123.1796 | -58.2275 | 64.7827 | 0.2897 | -0.0093619 | 0.061742 | 0.012022 | 0.068602 | 0.0011837 | -0.0071622 | 0.15363 | 0.004356 | 0.051296 | 0.047107 | 0.018221 | -0.0030891 | 64.8102 | -58.2092 | -0.041199 | -58.4244 | 64.7644 | -58.255 | -58.2733 | -58.1955 | -0.009155 | -58.5297 | 64.8056 | 64.7736 | -58.2092 | -58.3237 | -0.027466 | -0.045776 | -0.018311 | 0.01831 | -0.19684 | -0.15106 | 0.027466 | 0.01831 | -0.09613 | 0.022888 | 0.032043 | -0.30212 | -0.20599 | -0.009155 | 122.9919 | 123.0377 | 58.1863 | -123.056 | 123.0331 | 123.0011 | 58.2184 | -123.1064
32.8438 | 123.1613 | -58.2458 | 64.7827 | 0.22866 | 0.012 | 0.075628 | 0.0098848 | 0.075011 | 0.00011475 | 0.0035188 | 0.0010378 | -0.002053 | 0.075863 | 0.070606 | -0.0010051 | -0.0030891 | 64.8422 | -58.2001 | -0.064087 | -58.4335 | 64.7827 | -58.2458 | -58.2642 | -58.2047 | 0.022888 | -58.5297 | 64.8285 | 64.7552 | -58.2092 | -58.3237 | 0 | -0.01831 | 0 | 0.045777 | -0.18768 | -0.16937 | 0.059509 | 0.036621 | -0.077819 | 0.045776 | 0.041199 | -0.28381 | -0.20599 | -0.027466 | 123.0286 | 123.0881 | 58.1818 | -123.0469 | 123.0743 | 123.0011 | 58.2687 | -123.1064
33.8438 | 123.1705 | -58.2047 | 64.7873 | 0.16763 | 0.0055921 | 0.071355 | -0.016817 | 0.057921 | -0.0052253 | 0.0088588 | 0.2757 | 0.006492 | 0.073727 | 0.062061 | 0.0043349 | 0.0033199 | 64.7552 | -58.2687 | -0.10986 | -58.4564 | 64.7781 | -58.2596 | -58.287 | -58.2275 | -0.086975 | -58.5526 | 64.7919 | 64.7552 | -58.2184 | -58.342 | -0.054932 | -0.082397 | -0.009155 | -0.064087 | -0.25177 | -0.16937 | -0.032043 | -0.013733 | -0.13733 | 0.004578 | -0.022888 | -0.3479 | -0.21057 | -0.032043 | 122.9828 | 122.9599 | 58.0948 | -123.0743 | 122.9965 | 122.9599 | 58.1177 | -123.1293
34.8438 | 123.1522 | -58.2413 | 64.7873 | 0.18289 | 0.0066601 | 0.058538 | -0.00079616 | 0.067534 | 0.0054557 | 0.0024508 | 0.12311 | -0.004189 | 0.069454 | 0.067401 | 0.0011309 | 0.0033199 | 64.8376 | -58.2047 | -0.054932 | -58.4152 | 64.769 | -58.2275 | -58.2596 | -58.1726 | -0.018311 | -58.5251 | 64.8102 | 64.7598 | -58.2047 | -58.3145 | 0.013733 | -0.018311 | -0.01831 | 0.036621 | -0.17395 | -0.15564 | 0.050354 | 0.036621 | -0.073242 | 0.022889 | 0.068665 | -0.28381 | -0.21057 | -0.027465 | 123.0103 | 123.0789 | 58.1863 | -123.0469 | 123.0515 | 123.0011 | 58.223 | -123.1018
35.8438 | 123.1567 | -58.2275 | 64.8056 | 0.13711 | 0.019477 | 0.067083 | -0.0082732 | 0.058989 | 0.0065237 | -0.00075419 | 0.077332 | 0.006492 | 0.053432 | 0.065265 | 0.0054039 | -0.010566 | 64.8422 | -58.2001 | -0.036621 | -58.4244 | 64.7644 | -58.2092 | -58.2642 | -58.1772 | -0.004578 | -58.5068 | 64.7964 | 64.769 | -58.2047 | -58.3466 | 0.01831 | -0.036621 | -0.041199 | 0.027466 | -0.19684 | -0.16022 | 0.036621 | 0.022888 | -0.11902 | -0.009155 | 0.050354 | -0.27924 | -0.16022 | -0.036621 | 122.9919 | 123.0698 | 58.1909 | -123.0698 | 123.024 | 122.9965 | 58.223 | -123.1522
36.8438 | 123.2849 | -58.1818 | 64.7415 | 0.56436 | -0.0040209 | 0.067083 | -0.016817 | 0.072875 | -0.01377 | 0.0056548 | 0.56561 | -0.011666 | 0.063046 | 0.062061 | 6.2882e-05 | 0.0086599 | 64.8651 | -58.1314 | -0.022888 | -58.3694 | 64.7003 | -58.2184 | -58.2413 | -58.0994 | 0.045776 | -58.4335 | 64.7415 | 64.7003 | -58.2092 | -58.2825 | -0.036621 | -0.059509 | -0.041199 | 0.050354 | -0.18768 | -0.12817 | 0.1236 | -0.027466 | -0.10071 | 0 | 0.082398 | -0.25177 | -0.15106 | -0.041199 | 122.8821 | 123.0469 | 58.1589 | -122.9828 | 122.9233 | 122.8821 | 58.2275 | -123.024
37.8438 | 123.1293 | -58.2184 | 64.7827 | 0.2897 | 0.0023871 | 0.05747 | -0.0061362 | 0.057921 | 0.0054557 | 0.0035188 | 0.33673 | -0.004189 | 0.060909 | 0.063129 | 0.0086079 | 0.0065239 | 64.8056 | -58.2916 | -0.11902 | -58.4747 | 64.769 | -58.2504 | -58.2596 | -58.2138 | -0.086975 | -58.5846 | 64.7964 | 64.7369 | -58.2138 | -58.3328 | -0.032043 | -0.041199 | -0.013733 | -0.073242 | -0.25635 | -0.21515 | 0.022888 | 0.004578 | -0.11444 | 0.013733 | 0.004578 | -0.36621 | -0.25177 | -0.045777 | 122.9874 | 123.024 | 58.0994 | -123.0423 | 123.0148 | 122.9553 | 58.1314 | -123.1155
38.8438 | 123.143 | -58.2138 | 64.8056 | 0.16763 | 0.0045241 | 0.05747 | 0.00027184 | 0.068602 | 0.00011475 | 0.0077908 | 0.1994 | 8.4049e-05 | 0.060909 | 0.049243 | 0.0011309 | -0.0030891 | 64.8285 | -58.1863 | -0.050354 | -58.4244 | 64.7415 | -58.2367 | -58.2458 | -58.1818 | 0.009155 | -58.5434 | 64.8376 | 64.7919 | -58.2184 | -58.3282 | -0.022888 | -0.032044 | -0.064087 | 0.027466 | -0.21057 | -0.17853 | 0.022888 | -0.004578 | -0.11444 | 0.032043 | 0.032043 | -0.32959 | -0.21515 | -0.013733 | 122.9553 | 123.0423 | 58.1635 | -123.0515 | 123.0515 | 123.0057 | 58.223 | -123.1338
39.8438 | 123.1796 | -58.2047 | 64.7964 | 0.2134 | 0.0045241 | 0.059606 | 0.0045448 | 0.065398 | 0.0022517 | 0.0045868 | 0.15363 | 0.00222 | 0.081203 | 0.05672 | 0.0086079 | 0.011864 | 64.8422 | -58.2047 | -0.041199 | -58.4198 | 64.7736 | -58.2092 | -58.2504 | -58.168 | 0.009155 | -58.5159 | 64.7873 | 64.7736 | -58.2092 | -58.2962 | -0.004578 | -0.045776 | -0.022888 | 0 | -0.21515 | -0.16937 | 0.045776 | -0.004578 | -0.091553 | -0.009156 | 0.036621 | -0.31128 | -0.21973 | -0.022888 | 122.9782 | 123.0469 | 58.1635 | -123.0469 | 122.9919 | 122.9782 | 58.2138 | -123.0927
40.8438 | 123.1476 | -58.223 | 64.7964 | 0.19814 | 0.0055921 | 0.063879 | 0.00027184 | 0.065398 | 0.0033197 | -0.0082312 | 0.077332 | -0.00098395 | 0.057705 | 0.066333 | -0.0010051 | -0.0030891 | 64.8422 | -58.2001 | -0.050354 | -58.4244 | 64.7644 | -58.2458 | -58.255 | -58.1863 | 0 | -58.5159 | 64.7919 | 64.7598 | -58.2001 | -58.3099 | -0.022889 | -0.032044 | -0.032044 | 0.022888 | -0.20142 | -0.16937 | 0.045776 | 0.022888 | -0.086976 | -0.004578 | 0.036621 | -0.29297 | -0.20599 | -0.036621 | 122.9874 | 123.0652 | 58.1726 | -123.0515 | 123.0148 | 122.9828 | 58.223 | -123.1064
41.8438 | 123.1705 | -58.2413 | 64.7873 | 0.48806 | -0.0018849 | 0.069219 | 0.012022 | 0.070738 | -0.0030893 | 0.0045868 | 0.36725 | 0.001152 | 0.065182 | 0.052448 | -0.0042101 | 0.0033199 | 64.7919 | -58.2642 | -0.12817 | -58.4427 | 64.7598 | -58.255 | -58.2642 | -58.1955 | -0.091553 | -58.548 | 64.7873 | 64.7324 | -58.2413 | -58.3328 | -0.013733 | -0.022888 | -0.027465 | -0.022888 | -0.20142 | -0.17853 | 0.004578 | 0 | -0.091553 | 0 | 0.045776 | -0.3067 | -0.21515 | -0.054931 | 123.0011 | 123.0331 | 58.1131 | -123.0515 | 123.0286 | 122.9736 | 58.1497 | -123.1201
42.8438 | 123.1567 | -58.223 | 64.7919 | 0.15237 | 0.018409 | 0.073492 | -0.0018642 | 0.073943 | 0.0086597 | 0.010995 | 0.046815 | -0.008461 | 0.060909 | 0.042835 | 6.2882e-05 | -0.0062931 | 64.8331 | -58.1772 | -0.027466 | -58.4198 | 64.7736 | -58.2367 | -58.2504 | -58.1863 | 0.013733 | -58.5022 | 64.801 | 64.7827 | -58.2001 | -58.3145 | -0.013733 | -0.027466 | -0.01831 | 0.045776 | -0.19684 | -0.16937 | 0.041199 | 0.022888 | -0.091553 | 0.009155 | 0.036621 | -0.27924 | -0.18768 | -0.009155 | 122.9965 | 123.056 | 58.1955 | -123.0423 | 123.024 | 123.0057 | 58.2367 | -123.1064
43.8438 | 123.2162 | -58.2001 | 64.8148 | -0.015478 | 0.0098641 | 0.066015 | -0.0082732 | 0.073943 | 0.0054557 | 0.0024508 | -0.12103 | -0.00098395 | 0.067318 | 0.066333 | -0.0010051 | 0.0011829 | 64.8651 | -58.1589 | 0.004578 | -58.3832 | 64.7507 | -58.2275 | -58.2504 | -58.1406 | 0.07782 | -58.4793 | 64.8102 | 64.769 | -58.1955 | -58.3374 | -0.027466 | -0.050354 | -0.064087 | 0.041198 | -0.18311 | -0.13275 | 0.050354 | 0.004577 | -0.13733 | -0.004577 | 0.059509 | -0.27924 | -0.14191 | -0.045776 | 122.9507 | 123.0652 | 58.2047 | -123.0652 | 123.0103 | 122.9691 | 58.2779 | -123.1522
44.8438 | 123.1842 | -58.2184 | 64.7736 | 0.16763 | 0.018409 | 0.051061 | 0.0024088 | 0.075011 | 0.00011475 | 0.0142 | 0.24518 | 8.4049e-05 | 0.064114 | 0.065265 | 0.0064719 | 0.0011829 | 64.8376 | -58.1818 | -0.018311 | -58.4198 | 64.7598 | -58.2275 | -58.2825 | -58.1772 | 0.018311 | -58.5068 | 64.8056 | 64.7598 | -58.2001 | -58.3145 | -0.009155 | -0.064087 | -0.013733 | 0.036621 | -0.20142 | -0.13733 | 0.064086 | 0.018311 | -0.09613 | 0.032043 | 0.041199 | -0.28839 | -0.19226 | -0.013733 | 122.9782 | 123.056 | 58.2001 | -123.056 | 123.024 | 122.9782 | 58.2367 | -123.0881
45.8438 | 123.2117 | -58.2138 | 64.801 | 0.53384 | 0.0077281 | 0.071355 | -0.00079616 | 0.071807 | -0.0062933 | 0.00031381 | 0.59613 | 0.005424 | 0.064114 | 0.070606 | 0.0064719 | 0.010796 | 64.7919 | -58.255 | -0.13275 | -58.461 | 64.7552 | -58.255 | -58.287 | -58.1772 | -0.059509 | -58.5297 | 64.8056 | 64.7186 | -58.2321 | -58.3191 | -0.041199 | -0.073242 | -0.045776 | -0.041199 | -0.24719 | -0.17395 | -0.009155 | -0.018311 | -0.10529 | 0.004578 | 0.036621 | -0.31586 | -0.21057 | -0.082397 | 122.9691 | 123.0057 | 58.0811 | -123.0881 | 123.0194 | 122.9324 | 58.1543 | -123.1201
46.8438 | 123.262 | -58.2047 | 64.7507 | 0.53384 | 0.0034561 | 0.069219 | 0.0024088 | 0.058989 | -0.01377 | -0.0071622 | 0.61139 | -0.010597 | 0.06625 | 0.05672 | 0.0032669 | 0.0054559 | 64.8605 | -58.1223 | -0.013733 | -58.3832 | 64.6957 | -58.2184 | -58.2138 | -58.0948 | 0.054932 | -58.4152 | 64.7507 | 64.6637 | -58.223 | -58.3054 | -0.013733 | -0.009155 | -0.054931 | 0.082398 | -0.17853 | -0.16937 | 0.10986 | -0.01831 | -0.10071 | 0 | 0.10986 | -0.21057 | -0.10986 | -0.086975 | 122.9004 | 123.0652 | 58.1909 | -122.9645 | 122.9553 | 122.8683 | 58.2596 | -123.056
47.8438 | 123.1522 | -58.2047 | 64.801 | 0.2134 | 0.0066601 | 0.064947 | 0.0013408 | 0.068602 | 0.0075917 | 0.0056548 | 0.16888 | 0.008629 | 0.070522 | 0.063129 | 0.0021989 | -0.0020211 | 64.8422 | -58.2047 | -0.054932 | -58.4335 | 64.769 | -58.2321 | -58.2504 | -58.168 | 0 | -58.5342 | 64.8056 | 64.7598 | -58.2184 | -58.3328 | -0.027466 | -0.045776 | -0.032043 | 0 | -0.22888 | -0.18311 | 0.041199 | -0.013733 | -0.12817 | 0.004578 | 0.036621 | -0.32959 | -0.20142 | -0.041198 | 122.9736 | 123.0469 | 58.1497 | -123.0515 | 123.0103 | 122.9645 | 58.2047 | -123.1338
48.8438 | 123.1613 | -58.2184 | 64.8056 | 0.15237 | -0.00081686 | 0.067083 | -0.010409 | 0.067534 | 0.0054557 | 0.0024508 | 0.10785 | 0.007561 | 0.07159 | 0.074878 | 0.0011309 | -0.0052251 | 64.8422 | -58.1818 | -0.032043 | -58.4152 | 64.7736 | -58.2001 | -58.2413 | -58.1589 | 0.004578 | -58.5251 | 64.8148 | 64.7552 | -58.1863 | -58.3145 | 0.018311 | -0.022888 | -0.032043 | 0.036621 | -0.19684 | -0.17395 | 0.036621 | 0.032044 | -0.09613 | 0.009155 | 0.059509 | -0.3067 | -0.21057 | -0.050354 | 122.9919 | 123.0606 | 58.1863 | -123.0469 | 123.0331 | 122.9736 | 58.223 | -123.1201
49.8438 | 123.1613 | -58.2321 | 64.7964 | 0.24392 | 0.034431 | 0.069219 | 0.016294 | 0.06967 | 0.011865 | 0.00031381 | 0.046815 | 0.001152 | 0.080135 | 0.055652 | -0.0010051 | 0.0065239 | 64.801 | -58.2367 | -0.07782 | -58.4335 | 64.7324 | -58.2367 | -58.2687 | -58.2321 | -0.07782 | -58.58 | 64.7781 | 64.7507 | -58.2275 | -58.3374 | -0.004577 | -0.036621 | -0.064087 | -0.004577 | -0.20142 | -0.16479 | 0.004577 | 0.004578 | -0.10528 | -0.018311 | 0 | -0.3479 | -0.24262 | -0.045777 | 122.9645 | 123.0331 | 58.1543 | -123.0652 | 123.0103 | 122.9828 | 58.1543 | -123.1338
50.8438 | 123.2162 | -58.1955 | 64.7964 | -0.061255 | 0.0055921 | 0.066015 | -0.0040002 | 0.072875 | 0.0022517 | 0.0013818 | -0.044738 | 8.4049e-05 | 0.072659 | 0.055652 | -0.0042101 | -0.0052251 | 64.8468 | -58.1635 | -0.009155 | -58.4015 | 64.769 | -58.2138 | -58.2138 | -58.1406 | 0.086975 | -58.4702 | 64.8193 | 64.7736 | -58.2047 | -58.3054 | -0.01831 | -0.01831 | -0.027466 | 0.032044 | -0.20599 | -0.18768 | 0.050354 | -0.009155 | -0.10986 | 0.022888 | 0.054932 | -0.27466 | -0.16479 | -0.022888 | 122.9645 | 123.0423 | 58.1863 | -123.0103 | 123.0148 | 122.9691 | 58.2825 | -123.1018
51.8438 | 123.1659 | -58.2138 | 64.8239 | 0.2134 | 0.017341 | 0.063879 | -0.0018642 | 0.076079 | 0.015069 | -0.0050262 | 0.22992 | 0.007561 | 0.059841 | 0.052448 | 0.011812 | 0.0022509 | 64.8148 | -58.2413 | -0.068665 | -58.3969 | 64.7552 | -58.2001 | -58.2413 | -58.2138 | -0.036621 | -58.5434 | 64.8056 | 64.7369 | -58.2184 | -58.3054 | 0.013733 | -0.027466 | -0.068665 | -0.027466 | -0.18311 | -0.15564 | -0.009156 | -0.004578 | -0.091553 | -0.018311 | 0 | -0.32959 | -0.23804 | -0.086976 | 122.9691 | 123.0286 | 58.1451 | -123.0652 | 123.0194 | 122.9507 | 58.1772 | -123.1293
52.8438 | 123.1522 | -58.223 | 64.7827 | 0.076074 | 0.012 | 0.063879 | 0.00027184 | 0.067534 | 0.0086597 | 0.00031381 | 0.15363 | -0.003121 | 0.064114 | 0.063129 | 0.01288 | 0.010796 | 64.8193 | -58.1863 | -0.054932 | -58.4381 | 64.7552 | -58.2321 | -58.2275 | -58.1909 | -0.009155 | -58.5251 | 64.8148 | 64.769 | -58.2047 | -58.3237 | -0.009156 | -0.004578 | -0.027466 | 0.036621 | -0.21515 | -0.21057 | 0.036621 | 0.01831 | -0.10071 | 0.032043 | 0.032043 | -0.30212 | -0.20142 | -0.013733 | 122.9782 | 123.0423 | 58.168 | -123.0103 | 123.0377 | 122.9919 | 58.2138 | -123.1064
53.8438 | 123.1476 | -58.2413 | 64.7919 | 0.22866 | 0.0098641 | 0.067083 | 0.0034768 | 0.061125 | 0.0054557 | 0.0088588 | 0.092591 | 0.00222 | 0.079067 | 0.055652 | 0.0054039 | 0.014001 | 64.7781 | -58.2458 | -0.073242 | -58.4427 | 64.769 | -58.2458 | -58.2458 | -58.2138 | -0.059509 | -58.5526 | 64.801 | 64.7552 | -58.2321 | -58.342 | -0.004578 | -0.004578 | -0.022888 | -0.004578 | -0.20142 | -0.19684 | -0.013733 | 0.009155 | -0.10071 | 0.009155 | 0.027466 | -0.31128 | -0.21057 | -0.036621 | 123.0103 | 123.0194 | 58.168 | -123.0377 | 123.0423 | 122.9965 | 58.1818 | -123.1338
54.8438 | 123.1567 | -58.2047 | 64.7736 | 0.38125 | 0.035499 | 0.063879 | -0.0029322 | 0.057921 | 0.0022517 | -0.0039582 | 0.38251 | 0.004356 | 0.068386 | 0.064197 | 0.0021989 | 0.0054559 | 64.7644 | -58.2825 | -0.11902 | -58.4518 | 64.7461 | -58.2504 | -58.2642 | -58.1909 | -0.091553 | -58.548 | 64.7873 | 64.7461 | -58.2092 | -58.3466 | -0.045776 | -0.059509 | -0.027466 | -0.07782 | -0.24719 | -0.18768 | -0.009156 | -0.004578 | -0.14191 | 0.013732 | 0.013733 | -0.34332 | -0.20142 | -0.027466 | 122.9507 | 122.9691 | 58.0856 | -123.0377 | 122.9919 | 122.9507 | 58.1131 | -123.1201
55.8438 | 123.1018 | -58.2275 | 64.7919 | 0.41177 | 0.0098641 | 0.067083 | 0.0088168 | 0.068602 | -0.0062933 | 0.0056548 | 0.36725 | -0.00098395 | 0.050228 | 0.067401 | -0.0020731 | 0.0054559 | 64.7461 | -58.2779 | -0.14648 | -58.4702 | 64.7919 | -58.2367 | -58.287 | -58.1863 | -0.068665 | -58.5526 | 64.801 | 64.7415 | -58.2184 | -58.3328 | -0.009155 | -0.059509 | 0 | -0.050354 | -0.24262 | -0.18311 | -0.045776 | 0.009155 | -0.10529 | 0.009155 | 0.041199 | -0.32501 | -0.21973 | -0.050354 | 123.0194 | 122.9736 | 58.0811 | -123.0789 | 123.0286 | 122.9691 | 58.1589 | -123.1247
56.8438 | 123.1338 | -58.255 | 64.7964 | 0.25918 | 0.0013191 | 0.0799 | 0.0056128 | 0.067534 | 0.0022517 | -0.0071622 | 0.26044 | 0.009697 | 0.065182 | 0.070606 | 0.0011309 | -0.010566 | 64.8056 | -58.2596 | -0.09613 | -58.4564 | 64.7507 | -58.2413 | -58.287 | -58.223 | -0.086975 | -58.58 | 64.8056 | 64.7736 | -58.2138 | -58.342 | 0.013733 | -0.032043 | -0.045777 | -0.004578 | -0.20142 | -0.16937 | 0.009155 | 0.041199 | -0.086975 | 0.009155 | 0.032044 | -0.32501 | -0.23804 | -0.022888 | 123.0057 | 123.0606 | 58.1589 | -123.0835 | 123.0606 | 123.0286 | 58.168 | -123.1384
57.8438 | 123.1888 | -58.2092 | 64.7781 | 0.13711 | -0.0018849 | 0.068151 | 0.01309 | 0.071807 | 0.012933 | 0.0024508 | 0.13837 | 0.005424 | 0.060909 | 0.063129 | 0.0011309 | 0.0011829 | 64.8468 | -58.2001 | -0.027466 | -58.4015 | 64.7919 | -58.2138 | -58.2321 | -58.1589 | -0.004578 | -58.5114 | 64.8193 | 64.7964 | -58.2092 | -58.342 | -0.004577 | -0.022888 | 0.013733 | 0.009156 | -0.19226 | -0.16937 | 0.068665 | 0 | -0.13275 | 0.041199 | 0.050354 | -0.30212 | -0.16937 | 0.018311 | 123.0011 | 123.056 | 58.1818 | -123.0103 | 123.0286 | 123.0057 | 58.2047 | -123.1201
58.8438 | 123.1567 | -58.1772 | 64.801 | -0.2291 | 0.012 | 0.064947 | -0.011477 | 0.071807 | 0.0075917 | -0.0018222 | -0.15155 | 0.006492 | 0.080135 | 0.06847 | -0.0031411 | -0.0062931 | 64.8697 | -58.1726 | 0 | -58.3969 | 64.7781 | -58.2184 | -58.2321 | -58.1268 | 0.091553 | -58.461 | 64.8148 | 64.7736 | -58.2001 | -58.3145 | -0.041199 | -0.054932 | -0.022888 | 0.004578 | -0.21973 | -0.16479 | 0.068665 | -0.022888 | -0.13733 | 0.013733 | 0.050354 | -0.28381 | -0.14648 | -0.027465 | 122.9553 | 123.0469 | 58.1772 | -123.0331 | 122.9919 | 122.9507 | 58.2687 | -123.1155
59.8438 | 123.1979 | -58.1772 | 64.801 | -0.16807 | 0.010932 | 0.071355 | 0.017362 | 0.061125 | 0.0011837 | 0.010995 | -0.16681 | -0.003121 | 0.074795 | 0.055652 | 0.0043349 | 0.0022509 | 64.8468 | -58.1497 | -0.013733 | -58.3832 | 64.7873 | -58.1818 | -58.2687 | -58.1635 | 0.073242 | -58.4656 | 64.8056 | 64.7736 | -58.1863 | -58.3282 | -0.004578 | -0.091553 | -0.013733 | 0.027466 | -0.20599 | -0.11444 | 0.045777 | -0.009155 | -0.15106 | 0.004578 | 0.013733 | -0.28839 | -0.13733 | -0.027465 | 122.9645 | 123.024 | 58.1635 | -123.0698 | 122.9828 | 122.9507 | 58.2504 | -123.1293
60.8438 | 123.1979 | -58.2092 | 64.8148 | 0.12185 | 0.016273 | 0.061742 | -0.0018642 | 0.071807 | 0.0065237 | -0.0071622 | -0.029479 | -0.003121 | 0.069454 | 0.065265 | 0.0021989 | -0.0084301 | 64.8651 | -58.1451 | -0.009155 | -58.3923 | 64.7736 | -58.2321 | -58.2687 | -58.1223 | 0.059509 | -58.4564 | 64.7873 | 64.7507 | -58.2001 | -58.3145 | -0.022888 | -0.059509 | -0.041198 | 0.064087 | -0.1831 | -0.1236 | 0.050354 | 0.009156 | -0.10529 | -0.027466 | 0.086976 | -0.24719 | -0.14191 | -0.064087 | 122.9828 | 123.0743 | 58.2001 | -123.0835 | 122.9965 | 122.9599 | 58.2687 | -123.1293
61.8438 | 123.2254 | -58.2092 | 64.7964 | 0.48806 | 0.0034561 | 0.070287 | -0.011477 | 0.053649 | -0.011634 | 0.0013818 | 0.4588 | 8.4049e-05 | 0.069454 | 0.058857 | -0.0010051 | 0.0054559 | 64.7873 | -58.2413 | -0.12817 | -58.4564 | 64.7552 | -58.2733 | -58.2504 | -58.1863 | -0.068665 | -58.5114 | 64.7781 | 64.7278 | -58.2413 | -58.3237 | -0.064086 | -0.041198 | -0.041199 | -0.032043 | -0.24719 | -0.20599 | -0.009156 | -0.032043 | -0.11444 | -0.018311 | 0.022889 | -0.30212 | -0.18768 | -0.068665 | 122.9645 | 122.9965 | 58.0811 | -123.0469 | 122.9874 | 122.937 | 58.1406 | -123.1201
62.8438 | 123.1522 | -58.2092 | 64.7873 | 0.24392 | 0.021614 | 0.069219 | 0.015226 | 0.068602 | 0.0011837 | 0.01954 | 0.016297 | -0.004189 | 0.07159 | 0.069538 | -0.0031411 | -0.0030891 | 64.8239 | -58.2138 | -0.054932 | -58.4473 | 64.7827 | -58.223 | -58.2642 | -58.1635 | -0.004578 | -58.5297 | 64.8239 | 64.7644 | -58.1863 | -58.3374 | -0.013732 | -0.054931 | -0.004577 | -0.004577 | -0.23804 | -0.18311 | 0.036622 | 0.022889 | -0.12817 | 0.036622 | 0.045777 | -0.32043 | -0.19226 | -0.022888 | 122.9919 | 123.0331 | 58.1543 | -123.0515 | 123.0331 | 122.9736 | 58.2047 | -123.1247
63.8438 | 123.1796 | -58.2047 | 64.8285 | -0.24436 | 0.0023871 | 0.0799 | 0.0045448 | 0.080351 | -0.011634 | 0.00031381 | -0.13629 | 0.008629 | 0.075863 | 0.072742 | -0.0084821 | 0.0086599 | 64.8148 | -58.2138 | -0.018311 | -58.4106 | 64.8148 | -58.2321 | -58.2504 | -58.1726 | 0.068665 | -58.5022 | 64.8422 | 64.7964 | -58.2001 | -58.2962 | -0.027466 | -0.045776 | -0.013733 | -0.009155 | -0.20599 | -0.16022 | -0.013733 | 0.004578 | -0.091553 | 0.013733 | 0.032044 | -0.29755 | -0.20599 | -0.032043 | 123.0194 | 123.0194 | 58.1863 | -123.0789 | 123.0469 | 123.0011 | 58.2733 | -123.1247
64.8438 | 123.1796 | -58.2001 | 64.801 | -0.19858 | 0.0087961 | 0.071355 | -0.0072042 | 0.061125 | 0.0033197 | -0.0071622 | -0.075256 | 0.005424 | 0.047024 | 0.059925 | -0.0074141 | 0.0033199 | 64.8193 | -58.2001 | -0.091553 | -58.4198 | 64.7736 | -58.2047 | -58.2458 | -58.1589 | 0.059509 | -58.4747 | 64.8239 | 64.7827 | -58.1955 | -58.2962 | -0.004578 | -0.045777 | -0.027465 | 0 | -0.21973 | -0.17395 | 0.018311 | 0.004577 | -0.096131 | 0.022889 | 0.041198 | -0.27466 | -0.17853 | -0.01831 | 122.9736 | 123.0194 | 58.1085 | -123.0469 | 123.024 | 122.9828 | 58.2596 | -123.0972
65.8438 | 123.1979 | -58.2047 | 64.8056 | -0.015478 | 0.0077281 | 0.063879 | 0.00027184 | 0.060057 | -0.0041573 | 0.0035188 | 0.077332 | -0.00098395 | 0.061977 | 0.052448 | -0.0042101 | -0.00095306 | 64.8514 | -58.1497 | -0.004578 | -58.3969 | 64.7598 | -58.2275 | -58.2275 | -58.1451 | 0.054932 | -58.4885 | 64.7919 | 64.7461 | -58.223 | -58.3099 | -0.022888 | -0.022888 | -0.045776 | 0.054932 | -0.19226 | -0.16937 | 0.045776 | -0.01831 | -0.10529 | -0.013733 | 0.059509 | -0.28381 | -0.17853 | -0.059509 | 122.9645 | 123.056 | 58.2001 | -123.0331 | 122.9965 | 122.9507 | 58.2596 | -123.1155
66.8438 | 123.1247 | -58.2321 | 64.7827 | 0.16763 | 0.015205 | 0.058538 | 0.0034768 | 0.050444 | 0.0065237 | 0.0099268 | 0.29095 | -0.00098395 | 0.052364 | 0.067401 | 0.0021989 | 0.0043879 | 64.7873 | -58.2275 | -0.07782 | -58.4244 | 64.7644 | -58.2458 | -58.2687 | -58.223 | -0.09613 | -58.5617 | 64.8056 | 64.7278 | -58.2458 | -58.342 | -0.013733 | -0.036621 | -0.018311 | 0.004578 | -0.19226 | -0.15564 | 0.004577 | -0.013733 | -0.10986 | 0.022888 | 0.009156 | -0.32959 | -0.21973 | -0.054932 | 122.9965 | 123.0194 | 58.1543 | -123.0515 | 123.0377 | 122.9599 | 58.136 | -123.1247
67.8438 | 123.1979 | -58.168 | 64.8102 | -0.21384 | 0.0013191 | 0.069219 | -0.012545 | 0.068602 | -0.0084293 | 0.0013818 | -0.70087 | 0.001152 | 0.06625 | 0.05672 | -0.012754 | -0.0020211 | 64.8331 | -58.1772 | 0.045776 | -58.461 | 64.7781 | -58.2138 | -58.2413 | -58.1406 | 0.068665 | -58.4702 | 64.8239 | 64.7919 | -58.1909 | -58.3099 | -0.045776 | -0.073242 | -0.032044 | -0.009155 | -0.29297 | -0.21973 | 0.022888 | -0.022888 | -0.14191 | 0.013733 | 0.027466 | -0.30212 | -0.16022 | -0.018311 | 122.9462 | 123.0011 | 58.2138 | -123.0515 | 122.9919 | 122.9599 | 58.2367 | -123.1201
68.8438 | 123.1796 | -58.1955 | 64.8376 | -0.24436 | 0.00025114 | 0.073492 | 0.0077488 | 0.060057 | -0.00095325 | 0.00031381 | -0.2431 | 0.006492 | 0.057705 | 0.060993 | -0.011686 | 0.0011829 | 64.8102 | -58.1818 | -0.022888 | -58.4015 | 64.7781 | -58.2275 | -58.2504 | -58.1818 | 0.073242 | -58.5663 | 64.8422 | 64.7461 | -58.2047 | -58.3099 | -0.032043 | -0.054931 | -0.059509 | 0.013733 | -0.20599 | -0.15106 | -0.027465 | -0.009155 | -0.11444 | 0.004578 | 0.013733 | -0.37079 | -0.25635 | -0.091552 | 122.9736 | 123.0057 | 58.1726 | -123.0881 | 123.0377 | 122.9416 | 58.2687 | -123.1476
69.8438 | 123.2025 | -58.2001 | 64.8148 | 0.51858 | 0.0087961 | 0.071355 | -0.0018642 | 0.067534 | -0.0020213 | -0.0071622 | -0.18207 | -0.004189 | 0.061977 | 0.065265 | -0.0020731 | -0.0073621 | 64.8468 | -58.168 | 0.013733 | -58.3603 | 64.7919 | -58.1955 | -58.2413 | -58.1497 | 0.09613 | -58.4702 | 64.8148 | 64.7552 | -58.1955 | -58.3237 | 0.004577 | -0.041199 | -0.022888 | 0.032043 | -0.16022 | -0.11902 | 0.032044 | 0.004577 | -0.1236 | 0 | 0.050354 | -0.27008 | -0.14648 | -0.059509 | 122.9919 | 123.0469 | 58.2138 | -123.056 | 123.0148 | 122.9553 | 58.2962 | -123.1384
70.8438 | 123.2208 | -58.2047 | 64.7919 | 0.045557 | 0.021614 | 0.059606 | 0.0034768 | 0.072875 | 0.011865 | -0.0018222 | 0.0010378 | 0.003288 | 0.064114 | 0.06847 | -0.0052781 | -0.0052251 | 64.8697 | -58.1451 | 0.018311 | -58.3832 | 64.7781 | -58.2184 | -58.2504 | -58.1406 | 0.082397 | -58.461 | 64.8102 | 64.7369 | -58.1955 | -58.3054 | -0.013733 | -0.045776 | -0.013733 | 0.059509 | -0.17853 | -0.13275 | 0.07782 | 0.009155 | -0.10071 | 0.018311 | 0.064087 | -0.25635 | -0.15564 | -0.054932 | 122.9828 | 123.0743 | 58.223 | -123.0423 | 123.0148 | 122.9416 | 58.287 | -123.0972
71.8438 | 123.1293 | -58.2047 | 64.8376 | -0.21384 | -0.014702 | 0.071355 | 0.0066808 | 0.071807 | -0.0094983 | 0.0035188 | -0.22784 | 0.00222 | 0.074795 | 0.074878 | -0.0020731 | -0.0030891 | 64.7919 | -58.168 | -0.013733 | -58.4106 | 64.8148 | -58.2184 | -58.255 | -58.1818 | 0.073242 | -58.4793 | 64.8285 | 64.7827 | -58.2047 | -58.3099 | -0.013733 | -0.050354 | -0.022888 | 0.036621 | -0.20599 | -0.15564 | -0.045776 | 0 | -0.10529 | -0.009155 | 0.022888 | -0.27466 | -0.16937 | -0.054931 | 123.0194 | 122.9965 | 58.1909 | -123.0927 | 123.0331 | 122.9874 | 58.2779 | -123.1476
72.8438 | 123.1567 | -58.1909 | 64.7964 | -0.68687 | -0.011498 | 0.067083 | -0.0050682 | 0.076079 | -0.016974 | -0.0060942 | -0.22784 | -0.009529 | 0.055569 | 0.065265 | -0.0010051 | 0.0033199 | 64.7964 | -58.1589 | 0.004578 | -58.4152 | 64.801 | -58.2092 | -58.2504 | -58.168 | 0.073242 | -58.4793 | 64.8239 | 64.7644 | -58.2001 | -58.3237 | -0.018311 | -0.059509 | 0.004577 | 0.032043 | -0.2243 | -0.16479 | 0 | -0.009155 | -0.13275 | 0.027466 | 0.022888 | -0.28839 | -0.15564 | -0.032044 | 122.9919 | 122.9874 | 58.1955 | -123.0469 | 123.0148 | 122.9553 | 58.2642 | -123.1201
73.8438 | 123.1842 | -58.2047 | 64.8056 | -0.16807 | -0.0072259 | 0.07456 | 0.012022 | 0.078215 | 0.0022517 | -0.0028902 | 0.90131 | -0.011666 | 0.055569 | 0.060993 | -0.0084821 | -0.0041571 | 64.8148 | -58.1772 | -0.013733 | -58.3832 | 64.8056 | -58.2001 | -58.2413 | -58.1451 | 0.054932 | -58.4518 | 64.8376 | 64.7598 | -58.1772 | -58.3191 | 0.004578 | -0.036621 | 0 | 0.027466 | -0.17853 | -0.14191 | 0.009155 | 0.027466 | -0.11444 | 0.032043 | 0.059509 | -0.24719 | -0.13275 | -0.045776 | 123.0103 | 123.0194 | 58.1909 | -123.0469 | 123.0423 | 122.9645 | 58.2596 | -123.1247
74.8438 | 123.2117 | -58.1818 | 64.7919 | -0.41221 | 0.012 | 0.073492 | 0.0077488 | 0.065398 | 0.0011837 | 0.0056548 | -0.029479 | -0.008461 | 0.064114 | 0.066333 | 0.0021989 | -0.010566 | 64.8422 | -58.1451 | 0.013733 | -58.374 | 64.7781 | -58.223 | -58.2367 | -58.1268 | 0.091553 | -58.4427 | 64.8285 | 64.7415 | -58.1863 | -58.3099 | -0.041198 | -0.054931 | -0.013733 | 0.036621 | -0.19226 | -0.13733 | 0.050354 | -0.004577 | -0.12817 | 0.036621 | 0.054932 | -0.26093 | -0.13275 | -0.050354 | 122.9599 | 123.024 | 58.1955 | -123.0286 | 123.0103 | 122.9233 | 58.2733 | -123.1018
75.8438 | 123.1384 | -58.1909 | 64.8331 | -0.2291 | -0.015771 | 0.082037 | -0.010409 | 0.067534 | -0.014838 | -0.0028902 | -0.27362 | 0.007561 | 0.081203 | 0.070606 | -0.0042101 | -0.0062931 | 64.8102 | -58.1726 | -0.018311 | -58.4152 | 64.769 | -58.2138 | -58.2367 | -58.1818 | 0.050354 | -58.4976 | 64.8376 | 64.7598 | -58.1818 | -58.2962 | -0.022888 | -0.045776 | -0.064087 | 0.018311 | -0.2243 | -0.17853 | -0.022888 | 0.009155 | -0.10529 | 0.004577 | 0.009155 | -0.3067 | -0.20142 | -0.073242 | 122.9599 | 123.0011 | 58.1726 | -123.0698 | 123.0286 | 122.9507 | 58.2413 | -123.1293
76.8438 | 123.1476 | -58.1726 | 64.8239 | -0.25962 | 0.0013191 | 0.071355 | 0.0098848 | 0.068602 | -0.0073613 | -0.0071622 | -0.30414 | -0.00098395 | 0.057705 | 0.062061 | -0.0020731 | -0.0084301 | 64.7964 | -58.168 | -0.022888 | -58.4106 | 64.7964 | -58.2275 | -58.2642 | -58.1589 | 0.073242 | -58.4793 | 64.8376 | 64.7873 | -58.1863 | -58.2962 | -0.054932 | -0.091553 | -0.027466 | 0.004577 | -0.23804 | -0.14649 | -0.027466 | -0.013733 | -0.1236 | 0.013732 | 0.013732 | -0.3067 | -0.1831 | -0.036622 | 122.9691 | 122.9691 | 58.1497 | -123.0881 | 123.0103 | 122.9599 | 58.2458 | -123.1201
77.8438 | 123.1659 | -58.2001 | 64.8331 | -0.32065 | -0.0061569 | 0.055334 | -0.0072042 | 0.068602 | -0.0094983 | -0.0050262 | -0.27362 | -0.004189 | 0.068386 | 0.072742 | -0.0074141 | -0.0052251 | 64.7919 | -58.1726 | -0.009155 | -58.4106 | 64.7964 | -58.223 | -58.2321 | -58.168 | 0.059509 | -58.4976 | 64.856 | 64.7736 | -58.1909 | -58.287 | -0.022888 | -0.032044 | -0.036621 | 0.027466 | -0.21057 | -0.17853 | -0.041199 | 0.009155 | -0.086975 | 0.022888 | 0.032043 | -0.29755 | -0.21057 | -0.059509 | 122.9965 | 122.9919 | 58.1909 | -123.0652 | 123.056 | 122.9736 | 58.2596 | -123.1201
78.8438 | 123.1522 | -58.1955 | 64.8422 | -0.24436 | -0.0072259 | 0.062811 | 0.012022 | 0.066466 | 0.0043877 | -0.00075419 | -0.25836 | 8.4049e-05 | 0.055569 | 0.075946 | 0.0021989 | -0.0062931 | 64.8148 | -58.1863 | -0.013733 | -58.4015 | 64.8193 | -58.223 | -58.2458 | -58.1863 | 0.064087 | -58.4885 | 64.8285 | 64.7644 | -58.1726 | -58.2779 | -0.027465 | -0.050354 | -0.022888 | 0.009156 | -0.20599 | -0.15564 | -0.027466 | 0.022889 | -0.082397 | -0.013733 | 0.009156 | -0.29297 | -0.21057 | -0.07782 | 123.0148 | 123.0103 | 58.1818 | -123.0881 | 123.024 | 122.9599 | 58.2596 | -123.1201
79.8438 | 123.1155 | -58.1955 | 64.8376 | -0.16807 | -0.0040209 | 0.073492 | -0.0061362 | 0.073943 | -0.014838 | 0.00031381 | -0.30414 | -0.002053 | 0.076931 | 0.067401 | -0.0052781 | 0.0043879 | 64.8239 | -58.1085 | 0.027466 | -58.4061 | 64.8056 | -58.2138 | -58.2184 | -58.168 | 0.073242 | -58.493 | 64.8331 | 64.7644 | -58.2092 | -58.2916 | -0.01831 | -0.022888 | -0.032043 | 0.086975 | -0.21057 | -0.18768 | -0.013732 | -0.013733 | -0.09613 | -0.004577 | 0.027466 | -0.29755 | -0.20142 | -0.073242 | 123.0011 | 123.0194 | 58.223 | -123.056 | 123.0286 | 122.9599 | 58.2687 | -123.1293
80.8438 | 123.143 | -58.2047 | 64.8376 | -0.36643 | -0.0061569 | 0.076696 | -0.012545 | 0.061125 | -0.011634 | -0.0082312 | -0.029479 | -0.008461 | 0.060909 | 0.05672 | 0.0021989 | -0.00095306 | 64.8376 | -58.1314 | 0.036621 | -58.3923 | 64.7873 | -58.1818 | -58.2321 | -58.1589 | 0.082397 | -58.4656 | 64.856 | 64.7415 | -58.2138 | -58.3099 | 0.022888 | -0.027466 | -0.050354 | 0.073242 | -0.18768 | -0.16022 | 0 | -0.009155 | -0.10529 | 0.018311 | 0.045776 | -0.26093 | -0.15564 | -0.09613 | 122.9919 | 123.0423 | 58.2413 | -123.0698 | 123.0606 | 122.9462 | 58.287 | -123.1476
81.8438 | 123.175 | -58.1863 | 64.8285 | -0.29014 | 0.0045241 | 0.075628 | 0.010954 | 0.05258 | 0.0097277 | -0.0060942 | -0.3194 | 0.007561 | 0.067318 | 0.054584 | -0.0010051 | -0.011634 | 64.8102 | -58.1818 | -0.004578 | -58.4061 | 64.7964 | -58.223 | -58.223 | -58.168 | 0.064087 | -58.5114 | 64.8331 | 64.7507 | -58.1818 | -58.287 | -0.036621 | -0.036621 | -0.032043 | 0.004577 | -0.21973 | -0.18311 | -0.01831 | 0.004577 | -0.10071 | 0.004578 | 0.01831 | -0.32501 | -0.22431 | -0.07782 | 122.9828 | 122.9965 | 58.1818 | -123.0515 | 123.0194 | 122.937 | 58.2504 | -123.1155
82.8438 | 123.1705 | -58.2001 | 64.801 | -0.24436 | -0.0082939 | 0.063879 | -0.0018642 | 0.061125 | 0.00011475 | -0.012503 | -0.3194 | -0.002053 | 0.058773 | 0.064197 | -0.0074141 | -0.0062931 | 64.8102 | -58.1635 | -0.022888 | -58.4198 | 64.8102 | -58.2047 | -58.255 | -58.1726 | 0.059509 | -58.4976 | 64.856 | 64.7552 | -58.2138 | -58.3145 | -0.004578 | -0.054932 | 0.009156 | 0.036621 | -0.21973 | -0.1648 | 0.009156 | -0.013733 | -0.11444 | 0.054932 | 0.027466 | -0.29755 | -0.18311 | -0.045776 | 123.0103 | 123.0103 | 58.1772 | -123.056 | 123.056 | 122.9553 | 58.2596 | -123.1155
83.8438 | 123.23 | -58.1497 | 64.7919 | -0.24436 | -0.016839 | 0.071355 | -0.010409 | 0.06967 | -0.016974 | 0.00031381 | -0.16681 | -0.002053 | 0.056637 | 0.059925 | -0.017027 | 0.00011494 | 64.856 | -58.0582 | 0.10071 | -58.3374 | 64.769 | -58.2001 | -58.2367 | -58.0948 | 0.16022 | -58.4152 | 64.7919 | 64.7278 | -58.1955 | -58.2962 | -0.050354 | -0.086975 | -0.022888 | 0.091552 | -0.18768 | -0.10071 | 0.064087 | -0.045777 | -0.14649 | 0 | 0.054931 | -0.2655 | -0.11902 | -0.064087 | 122.9187 | 123.0057 | 58.2504 | -123.0286 | 122.9416 | 122.8775 | 58.3099 | -123.0881
84.8438 | 123.2574 | -58.1268 | 64.769 | -0.045996 | -0.025384 | 0.059606 | 0.00027184 | 0.061125 | -0.021247 | -0.011435 | -0.029479 | -0.007393 | 0.045956 | 0.048175 | -0.0074141 | 0.00011494 | 64.9155 | -58.0215 | 0.10071 | -58.3374 | 64.769 | -58.1909 | -58.2047 | -58.0673 | 0.17853 | -58.3603 | 64.7781 | 64.7141 | -58.168 | -58.287 | -0.064087 | -0.07782 | 0 | 0.10529 | -0.21057 | -0.13275 | 0.14648 | -0.041199 | -0.16022 | 0.009155 | 0.059509 | -0.23346 | -0.073243 | -0.054932 | 122.8958 | 123.0423 | 58.2275 | -122.9736 | 122.905 | 122.8409 | 58.3054 | -123.056
85.8438 | 123.2574 | -58.1406 | 64.7919 | -0.18333 | -0.022179 | 0.070287 | -0.0093412 | 0.066466 | -0.01377 | -0.012503 | 0.016297 | -0.021279 | 0.055569 | 0.053516 | -0.0042101 | -0.0062931 | 64.9063 | -58.0307 | 0.10071 | -58.3374 | 64.7552 | -58.1955 | -58.223 | -58.0673 | 0.19226 | -58.3878 | 64.7644 | 64.7003 | -58.1497 | -58.2779 | -0.054932 | -0.082397 | -0.036621 | 0.10986 | -0.19684 | -0.11444 | 0.11444 | -0.009155 | -0.13733 | -0.027466 | 0.073242 | -0.24719 | -0.10986 | -0.091553 | 122.8958 | 123.0469 | 58.2413 | -123.0148 | 122.905 | 122.8409 | 58.3328 | -123.0698
86.8438 | 123.1155 | -58.2001 | 64.8193 | -0.27488 | -0.016839 | 0.066015 | 0.012022 | 0.061125 | 0.0043877 | -0.0028902 | -0.39569 | 8.4049e-05 | 0.068386 | 0.064197 | -0.0095501 | -0.0073621 | 64.8239 | -58.1726 | -0.013733 | -58.4106 | 64.8102 | -58.2184 | -58.2367 | -58.1589 | 0.064087 | -58.5022 | 64.8376 | 64.7598 | -58.1818 | -58.3099 | -0.018311 | -0.036621 | -0.009155 | 0.027466 | -0.21057 | -0.17395 | 0.004578 | 0.01831 | -0.10986 | 0.01831 | 0.041198 | -0.30212 | -0.19226 | -0.059509 | 123.0103 | 123.024 | 58.1863 | -123.056 | 123.0377 | 122.9599 | 58.2642 | -123.1293
87.8438 | 123.1567 | -58.1772 | 64.8285 | -0.86997 | -0.020043 | 0.068151 | 0.0034768 | 0.066466 | 0.0022517 | 0.0024508 | -0.3194 | 0.007561 | 0.052364 | 0.071674 | -0.014891 | 0.0075919 | 64.8193 | -58.1406 | -0.018311 | -58.4152 | 64.7827 | -58.2138 | -58.2504 | -58.1589 | 0.064087 | -58.4839 | 64.8422 | 64.7461 | -58.2001 | -58.3008 | -0.036621 | -0.073242 | -0.045776 | 0.036621 | -0.23804 | -0.16479 | -0.009155 | -0.022888 | -0.1236 | 0.013733 | 0.01831 | -0.3067 | -0.18311 | -0.082397 | 122.9599 | 122.9965 | 58.1589 | -123.0789 | 123.0194 | 122.9233 | 58.2413 | -123.1293
88.8438 | 123.2712 | -58.1268 | 64.7964 | -0.19858 | -0.029656 | 0.075628 | -0.013613 | 0.070738 | -0.016974 | -0.010367 | -0.16681 | -0.007393 | 0.053432 | 0.059925 | 0.0011309 | 0.00011494 | 64.8834 | -57.9987 | 0.09613 | -58.3466 | 64.7324 | -58.1818 | -58.2092 | -58.0444 | 0.19226 | -58.374 | 64.7964 | 64.6957 | -58.168 | -58.287 | -0.054932 | -0.082398 | -0.064087 | 0.12817 | -0.21973 | -0.13733 | 0.086975 | -0.041199 | -0.16022 | 0 | 0.082397 | -0.24719 | -0.086975 | -0.10071 | 122.8592 | 123.0103 | 58.223 | -123.0057 | 122.9233 | 122.8226 | 58.3191 | -123.0835
89.8438 | 123.2574 | -58.1589 | 64.7964 | -0.19858 | -0.024315 | 0.062811 | -0.0029322 | 0.072875 | -0.011634 | -0.010367 | -0.18207 | -0.013802 | 0.053432 | 0.054584 | -0.0031411 | -0.01377 | 64.9109 | -58.0444 | 0.10071 | -58.3466 | 64.769 | -58.1863 | -58.2275 | -58.0627 | 0.1831 | -58.3786 | 64.7873 | 64.6774 | -58.1497 | -58.2916 | -0.027465 | -0.068664 | -0.027466 | 0.11444 | -0.18768 | -0.11902 | 0.11444 | 0.009156 | -0.13275 | -0.009156 | 0.096131 | -0.21973 | -0.086975 | -0.11902 | 122.9279 | 123.0698 | 58.2596 | -123.024 | 122.9462 | 122.8363 | 58.342 | -123.0881
90.8438 | 123.2117 | -58.1497 | 64.8239 | -0.25962 | -0.016839 | 0.073492 | -0.0040002 | 0.065398 | -0.0094983 | -0.0028902 | 0.30621 | 0.004356 | 0.04916 | 0.055652 | -0.0010051 | -0.0020211 | 64.8834 | -58.0765 | 0.086975 | -58.3557 | 64.7736 | -58.2047 | -58.2138 | -58.0902 | 0.15564 | -58.4244 | 64.7919 | 64.6912 | -58.1635 | -58.2916 | -0.054932 | -0.064087 | -0.050354 | 0.073242 | -0.20599 | -0.14191 | 0.059509 | -0.013733 | -0.14191 | -0.032044 | 0.059509 | -0.27466 | -0.13275 | -0.13275 | 122.9233 | 123.0331 | 58.2367 | -123.0377 | 122.9416 | 122.8409 | 58.3054 | -123.1155
91.8438 | 123.2391 | -58.2001 | 64.7049 | 0.59487 | -0.0050889 | 0.060674 | 0.012022 | 0.075011 | 0.0097277 | -0.00075419 | 0.74872 | -0.002053 | 0.057705 | 0.071674 | 0.0032669 | 0.0054559 | 64.8651 | -58.0856 | -0.022888 | -58.3603 | 64.769 | -58.2184 | -58.2596 | -58.0765 | 0.041199 | -58.4381 | 64.7644 | 64.6454 | -58.1818 | -58.3054 | -0.018311 | -0.05951 | 0.064087 | 0.11444 | -0.16022 | -0.10071 | 0.16022 | 0.01831 | -0.10529 | 0.059509 | 0.1236 | -0.23804 | -0.13275 | -0.059509 | 122.9691 | 123.0652 | 58.1772 | -122.9645 | 122.9645 | 122.8455 | 58.2413 | -123.0103
92.8438 | 123.2025 | -58.168 | 64.769 | 0.24392 | -0.012566 | 0.064947 | -0.0082732 | 0.044036 | -0.021247 | -0.0082312 | 0.21466 | -0.007393 | 0.04916 | 0.067401 | -0.013823 | 0.0011829 | 64.8331 | -58.1451 | -0.041199 | -58.3923 | 64.7461 | -58.2184 | -58.2367 | -58.1131 | 0.050354 | -58.4427 | 64.7919 | 64.6957 | -58.1497 | -58.2962 | -0.050354 | -0.068664 | -0.022888 | 0.022888 | -0.2243 | -0.15564 | 0.064087 | 0.018311 | -0.12817 | 0.022888 | 0.054932 | -0.27466 | -0.14648 | -0.073242 | 122.9141 | 123.0011 | 58.1268 | -123.0057 | 122.9599 | 122.8638 | 58.2184 | -123.0652
93.8438 | 123.3078 | -58.1543 | 64.769 | -0.18333 | -0.017907 | 0.077764 | 0.0045448 | 0.054717 | -0.0084293 | -0.0082312 | 0.031556 | 0.003288 | 0.057705 | 0.059925 | -0.0010051 | -0.01377 | 64.9063 | -58.0902 | 0.045776 | -58.3557 | 64.769 | -58.1955 | -58.223 | -58.0444 | 0.1236 | -58.4015 | 64.7644 | 64.6866 | -58.1726 | -58.2642 | -0.041199 | -0.068664 | 0 | 0.064087 | -0.20142 | -0.13275 | 0.13733 | -0.01831 | -0.10986 | -0.004578 | 0.10986 | -0.24719 | -0.13733 | -0.082398 | 122.9233 | 123.0606 | 58.2001 | -122.9919 | 122.9187 | 122.8409 | 58.2779 | -123.0331
94.8438 | 123.2574 | -58.1406 | 64.7827 | -0.3054 | -0.0093619 | 0.066015 | -0.0029322 | 0.070738 | 0.0033197 | 0.0035188 | -0.21259 | -0.009529 | 0.050228 | 0.05672 | 0.0075399 | -0.0073621 | 64.8972 | -58.0353 | 0.10529 | -58.342 | 64.7507 | -58.1909 | -58.223 | -58.0399 | 0.1831 | -58.3603 | 64.7873 | 64.7003 | -58.1818 | -58.2733 | -0.050354 | -0.082397 | -0.032044 | 0.10529 | -0.20142 | -0.11902 | 0.11444 | -0.041199 | -0.13275 | 0.004577 | 0.10071 | -0.21973 | -0.086976 | -0.082398 | 122.8912 | 123.0377 | 58.2458 | -123.0057 | 122.9279 | 122.8409 | 58.3237 | -123.056
95.8438 | 123.2849 | -58.1314 | 64.7827 | -0.16807 | -0.018975 | 0.063879 | -0.016817 | 0.079283 | 0.0043877 | -0.0050262 | -0.19733 | -0.005257 | 0.041683 | 0.070606 | -0.0031411 | -0.0052251 | 64.9017 | -58.0124 | 0.10071 | -58.342 | 64.7552 | -58.1772 | -58.2138 | -58.0536 | 0.18768 | -58.3832 | 64.7873 | 64.682 | -58.1909 | -58.287 | -0.045776 | -0.082397 | -0.027466 | 0.11902 | -0.21057 | -0.12817 | 0.11902 | -0.059509 | -0.15564 | 0.004577 | 0.07782 | -0.25177 | -0.096131 | -0.10071 | 122.8867 | 123.0331 | 58.2321 | -122.9965 | 122.9187 | 122.8134 | 58.3191 | -123.0698
96.8438 | 123.1247 | -58.1909 | 64.8148 | -0.18333 | 0.0013191 | 0.072424 | 0.0077488 | 0.06433 | 0.016137 | -0.0050262 | -0.42621 | -0.00098395 | 0.051296 | 0.067401 | 0.0043349 | -0.024451 | 64.8148 | -58.1635 | -0.009155 | -58.4015 | 64.7964 | -58.2001 | -58.2642 | -58.1406 | 0.064087 | -58.493 | 64.8605 | 64.7415 | -58.1863 | -58.287 | -0.009155 | -0.073242 | -0.01831 | 0.027466 | -0.21057 | -0.13733 | 0 | 0.004578 | -0.09613 | 0.045777 | 0.050354 | -0.30212 | -0.20599 | -0.073242 | 122.9874 | 123.0057 | 58.1818 | -123.0789 | 123.0515 | 122.9324 | 58.255 | -123.1018
97.8438 | 123.2254 | -58.1863 | 64.769 | 0.24392 | -0.034997 | 0.066015 | 0.0034768 | 0.065398 | -0.0062933 | -0.0039582 | 0.21466 | -0.004189 | 0.045956 | 0.052448 | -0.0010051 | 0.0054559 | 64.8239 | -58.1177 | -0.018311 | -58.3832 | 64.7598 | -58.2092 | -58.223 | -58.0994 | 0.050354 | -58.4381 | 64.769 | 64.6866 | -58.1772 | -58.2916 | -0.022889 | -0.036621 | -0.009155 | 0.068664 | -0.19684 | -0.16022 | 0.054932 | 0.009155 | -0.10529 | 0 | 0.086975 | -0.25177 | -0.14648 | -0.082398 | 122.9462 | 123.0103 | 58.168 | -122.9919 | 122.9553 | 122.8729 | 58.2367 | -123.0606
98.8438 | 123.2437 | -58.1726 | 64.7736 | 0.2134 | -0.03286 | 0.059606 | 0.0034768 | 0.066466 | -0.010566 | -0.0050262 | 0.077332 | -0.015938 | 0.070522 | 0.05672 | 0.0075399 | -0.00095306 | 64.8239 | -58.1223 | -0.004578 | -58.3969 | 64.7507 | -58.2047 | -58.255 | -58.0811 | 0.091553 | -58.4244 | 64.7736 | 64.6912 | -58.1772 | -58.2962 | -0.032044 | -0.082398 | -0.022889 | 0.050354 | -0.22431 | -0.14191 | 0.050354 | -0.004578 | -0.1236 | 0 | 0.091552 | -0.25177 | -0.12817 | -0.082398 | 122.9233 | 122.9965 | 58.168 | -123.0286 | 122.9462 | 122.8638 | 58.2642 | -123.0698
99.8438 | 123.2254 | -58.1772 | 64.7736 | 0.44228 | -0.017907 | 0.063879 | 0.0034768 | 0.056853 | 0.0097277 | -0.0018222 | 0.36725 | -0.012734 | 0.055569 | 0.058857 | -0.0084821 | -0.0041571 | 64.8331 | -58.1314 | -0.027466 | -58.4061 | 64.7369 | -58.2092 | -58.2458 | -58.1085 | 0.041199 | -58.4473 | 64.7781 | 64.6683 | -58.1955 | -58.2733 | -0.032044 | -0.068665 | -0.036622 | 0.045776 | -0.22888 | -0.16022 | 0.059509 | -0.018311 | -0.09613 | 0.004577 | 0.068664 | -0.27008 | -0.17395 | -0.10529 | 122.9141 | 123.0103 | 58.1497 | -123.0194 | 122.9553 | 122.8455 | 58.2184 | -123.0469
100.8438 | 123.2208 | -58.1726 | 64.7736 | 0.30496 | -0.024315 | 0.071355 | -0.0029322 | 0.06433 | -0.0062933 | 0.0024508 | 0.29095 | -0.002053 | 0.045956 | 0.069538 | 6.2882e-05 | -0.0030891 | 64.8422 | -58.1223 | -0.036621 | -58.4061 | 64.7415 | -58.2275 | -58.2275 | -58.0856 | 0.022888 | -58.4473 | 64.769 | 64.6866 | -58.1818 | -58.3191 | -0.054932 | -0.054932 | -0.032044 | 0.050354 | -0.23346 | -0.17853 | 0.068664 | -0.009156 | -0.14648 | -0.004578 | 0.086975 | -0.27466 | -0.12817 | -0.086976 | 122.9141 | 123.0148 | 58.136 | -123.0011 | 122.9416 | 122.8592 | 58.1955 | -123.0927
101.8438 | 123.2025 | -58.2001 | 64.7736 | -0.030737 | 0.016273 | 0.052129 | 0.0077488 | 0.058989 | 0.032159 | 0.0024508 | -0.25836 | 0.007561 | 0.054501 | 0.059925 | 0.0054039 | -0.01377 | 64.8972 | -58.1223 | 0.009155 | -58.3878 | 64.801 | -58.223 | -58.2642 | -58.1039 | 0.073242 | -58.4656 | 64.8193 | 64.7095 | -58.1818 | -58.3191 | -0.022888 | -0.064087 | 0.027465 | 0.07782 | -0.18768 | -0.1236 | 0.1236 | 0.01831 | -0.11902 | 0.045776 | 0.09613 | -0.2655 | -0.14648 | -0.064087 | 123.0011 | 123.0972 | 58.2092 | -123.0377 | 123.0194 | 122.9095 | 58.2733 | -123.0927
102.8438 | 123.2162 | -58.1772 | 64.7781 | 0.27444 | -0.031792 | 0.060674 | 0.00027184 | 0.06967 | -0.021247 | -0.027457 | 0.21466 | -0.008461 | 0.050228 | 0.064197 | 0.0021989 | 0.0086599 | 64.8422 | -58.136 | -0.027466 | -58.3969 | 64.7644 | -58.223 | -58.2413 | -58.1039 | 0.041199 | -58.4473 | 64.7781 | 64.6774 | -58.2138 | -58.3191 | -0.045776 | -0.064087 | -0.013733 | 0.041199 | -0.21973 | -0.15564 | 0.064087 | -0.036621 | -0.14191 | 0 | 0.073242 | -0.27008 | -0.12817 | -0.10071 | 122.9416 | 123.0194 | 58.1497 | -123.0194 | 122.9553 | 122.8546 | 58.2184 | -123.0972
103.8438 | 123.2254 | -58.1772 | 64.7781 | 0.27444 | -0.013634 | 0.077764 | -0.0029322 | 0.055785 | -0.011634 | -0.0082312 | 0.21466 | -0.007393 | 0.041683 | 0.059925 | 0.0086079 | -0.0041571 | 64.8331 | -58.1314 | -0.022888 | -58.4015 | 64.7461 | -58.2138 | -58.2458 | -58.0948 | 0.050354 | -58.4427 | 64.7873 | 64.682 | -58.1863 | -58.2962 | -0.036621 | -0.068665 | -0.032043 | 0.045776 | -0.2243 | -0.15564 | 0.054932 | -0.009155 | -0.11902 | 0.009155 | 0.082397 | -0.2655 | -0.14648 | -0.09613 | 122.9233 | 123.0103 | 58.1543 | -123.024 | 122.9645 | 122.8592 | 58.2275 | -123.0743
104.8438 | 123.2712 | -58.168 | 64.7781 | 0.10659 | -0.018975 | 0.063879 | -0.018954 | 0.075011 | -0.011634 | -0.0082312 | 0.077332 | 8.4049e-05 | 0.054501 | 0.047107 | -0.0052781 | -0.0073621 | 64.8422 | -58.1177 | 0.004578 | -58.3786 | 64.7278 | -58.1909 | -58.2275 | -58.0719 | 0.068665 | -58.4198 | 64.7827 | 64.6774 | -58.1543 | -58.2962 | -0.022888 | -0.059509 | -0.050354 | 0.050354 | -0.21057 | -0.15106 | 0.064087 | 0.013733 | -0.12817 | 0.004578 | 0.096131 | -0.25177 | -0.1236 | -0.10071 | 122.8958 | 123.0103 | 58.1726 | -123.0057 | 122.9507 | 122.8455 | 58.2367 | -123.0743
105.8438 | 123.2666 | -58.1543 | 64.7415 | 0.48806 | -0.012566 | 0.068151 | -0.0072042 | 0.065398 | 0.0043877 | -0.011435 | 0.39777 | -0.006325 | 0.050228 | 0.046039 | 0.010744 | -0.0020211 | 64.9109 | -58.0948 | -0.009155 | -58.3649 | 64.7049 | -58.1955 | -58.2367 | -58.0627 | 0.045776 | -58.4244 | 64.7415 | 64.6408 | -58.2092 | -58.3099 | -0.041199 | -0.082397 | -0.036621 | 0.059509 | -0.21057 | -0.12817 | 0.16937 | -0.054932 | -0.15564 | 0 | 0.091553 | -0.27008 | -0.11444 | -0.10071 | 122.8592 | 123.0652 | 58.1451 | -122.9782 | 122.8958 | 122.7951 | 58.2001 | -123.0515
106.8438 | 123.2712 | -58.1451 | 64.7507 | -0.076513 | -0.02752 | 0.071355 | 0.0024088 | 0.060057 | -0.0084293 | 0.0013818 | -0.16681 | -0.006325 | 0.038479 | 0.052448 | 0.0011309 | -0.011634 | 64.9612 | -58.0078 | 0.10071 | -58.3328 | 64.7461 | -58.1955 | -58.2047 | -58.0307 | 0.19684 | -58.3511 | 64.7827 | 64.7095 | -58.1451 | -58.2596 | -0.050354 | -0.059509 | -0.004577 | 0.13733 | -0.18768 | -0.12817 | 0.21057 | 0 | -0.11444 | 0.032044 | 0.11444 | -0.20599 | -0.091552 | -0.041198 | 122.8912 | 123.1064 | 58.2458 | -122.9553 | 122.9279 | 122.8546 | 58.342 | -123.0103
107.8438 | 123.2391 | -58.1497 | 64.7369 | 0.45754 | -0.0040209 | 0.061742 | -0.0040002 | 0.070738 | 0.0033197 | -0.0039582 | 0.39777 | -0.033028 | 0.067318 | 0.07381 | 0.015017 | -0.0030891 | 64.8834 | -58.0856 | -0.004578 | -58.374 | 64.7232 | -58.223 | -58.2367 | -58.0719 | 0.036621 | -58.3832 | 64.7369 | 64.6362 | -58.2047 | -58.3099 | -0.073242 | -0.086975 | -0.013732 | 0.064087 | -0.2243 | -0.13733 | 0.14648 | -0.054932 | -0.16022 | 0 | 0.07782 | -0.23346 | -0.073242 | -0.10071 | 122.8729 | 123.0331 | 58.1451 | -122.9736 | 122.8867 | 122.7859 | 58.1863 | -123.0469
108.8438 | 123.2712 | -58.168 | 64.7369 | 0.56436 | 0.0045241 | 0.068151 | -0.0050682 | 0.067534 | 0.011865 | 0.0013818 | 0.38251 | -0.012734 | 0.058773 | 0.041767 | 0.0021989 | 0.0022509 | 64.8972 | -58.0811 | -0.022888 | -58.374 | 64.7003 | -58.2047 | -58.2367 | -58.0536 | 0.050354 | -58.429 | 64.7369 | 64.6591 | -58.2001 | -58.2962 | -0.036621 | -0.068664 | -0.036621 | 0.086975 | -0.20599 | -0.13733 | 0.16022 | -0.032043 | -0.12817 | 0 | 0.11444 | -0.26093 | -0.13275 | -0.077819 | 122.8683 | 123.0652 | 58.1451 | -122.9736 | 122.905 | 122.8271 | 58.2184 | -123.0331
109.8438 | 123.2483 | -58.1863 | 64.7232 | 0.12185 | 0.013069 | 0.062811 | 0.0013408 | 0.06433 | 0.02041 | -0.0082312 | 0.33673 | 0.010765 | 0.065182 | 0.067401 | 0.0011309 | -0.010566 | 64.8651 | -58.1589 | -0.082397 | -58.4335 | 64.7278 | -58.2321 | -58.287 | -58.0948 | 0.009155 | -58.429 | 64.7964 | 64.6866 | -58.1955 | -58.3054 | -0.045777 | -0.10071 | 0.004577 | 0.027465 | -0.24719 | -0.14648 | 0.14191 | -0.009156 | -0.11902 | 0.073242 | 0.091552 | -0.24262 | -0.1236 | -0.036622 | 122.9141 | 123.0515 | 58.1039 | -123.0103 | 122.9828 | 122.8729 | 58.1955 | -123.0286
110.8438 | 123.2803 | -58.1772 | 64.7461 | 0.61013 | -0.0040209 | 0.060674 | -0.0040002 | 0.06433 | 0.0075917 | -0.00075419 | 0.62665 | 0.00222 | 0.052364 | 0.059925 | 0.0054039 | -0.0030891 | 64.888 | -58.0948 | -0.009155 | -58.3969 | 64.7278 | -58.223 | -58.2779 | -58.0719 | 0.054932 | -58.429 | 64.7644 | 64.6683 | -58.2092 | -58.3191 | -0.045776 | -0.10071 | -0.018311 | 0.082397 | -0.21973 | -0.11902 | 0.14191 | -0.032044 | -0.14191 | 0.01831 | 0.10529 | -0.25177 | -0.10986 | -0.07782 | 122.905 | 123.0652 | 58.168 | -123.024 | 122.9416 | 122.8455 | 58.2321 | -123.0652
111.8438 | 123.1613 | -58.1726 | 64.8148 | 0.22866 | -0.0029529 | 0.061742 | -0.0072042 | 0.063262 | 0.011865 | -0.0050262 | -0.13629 | 0.005424 | 0.052364 | 0.057788 | 0.015017 | -0.0073621 | 64.9246 | -58.1223 | 0.009155 | -58.3374 | 64.7964 | -58.2047 | -58.2367 | -58.1589 | 0.009155 | -58.5205 | 64.7873 | 64.7507 | -58.2047 | -58.3511 | -0.032044 | -0.064087 | -0.01831 | 0.050354 | -0.16479 | -0.10071 | 0.10986 | -0.032044 | -0.17853 | -0.027466 | 0.013732 | -0.3479 | -0.16937 | -0.064087 | 122.9691 | 123.0972 | 58.1818 | -123.0515 | 122.9599 | 122.9233 | 58.1818 | -123.1659
112.8438 | 123.1201 | -58.2458 | 64.8056 | 0.44228 | 0.024818 | 0.067083 | -0.0061362 | 0.066466 | 0.02041 | -0.0050262 | 0.35199 | 0.00222 | 0.052364 | 0.066333 | 0.0086079 | 0.012933 | 64.801 | -58.2596 | -0.15106 | -58.4427 | 64.7781 | -58.2413 | -58.2779 | -58.1772 | -0.07782 | -58.5434 | 64.801 | 64.7141 | -58.223 | -58.3603 | 0.004578 | -0.032043 | -0.027466 | -0.013733 | -0.19684 | -0.16479 | -0.004578 | 0.022889 | -0.11444 | -0.004578 | 0.068665 | -0.29755 | -0.18311 | -0.091553 | 123.024 | 123.0469 | 58.0948 | -123.0835 | 123.0469 | 122.9599 | 58.168 | -123.1659
113.8438 | 123.2437 | -58.2184 | 64.7552 | 0.41177 | 0.0013191 | 0.063879 | -0.0040002 | 0.062194 | 0.0022517 | 0.0035188 | 0.32147 | -0.002053 | 0.054501 | 0.05138 | 0.0086079 | 0.0043879 | 64.8056 | -58.2504 | -0.13275 | -58.429 | 64.769 | -58.2367 | -58.2642 | -58.1543 | -0.059509 | -58.5159 | 64.7736 | 64.7049 | -58.223 | -58.3374 | -0.01831 | -0.045776 | 0.013733 | -0.032043 | -0.21057 | -0.1648 | 0.050354 | -0.004577 | -0.11902 | 0.018311 | 0.064087 | -0.29755 | -0.17853 | -0.050354 | 122.9874 | 123.024 | 58.0856 | -123.0194 | 122.9919 | 122.9233 | 58.1589 | -123.0927
114.8438 | 123.2025 | -58.2184 | 64.7919 | 0.51858 | 0.022682 | 0.073492 | 0.0013408 | 0.073943 | 0.0097277 | 0.0024508 | 0.51984 | 8.4049e-05 | 0.055569 | 0.05672 | 6.2882e-05 | -0.0041571 | 64.8193 | -58.2596 | -0.14648 | -58.3694 | 64.7278 | -58.2321 | -58.2687 | -58.1497 | -0.027466 | -58.4793 | 64.7919 | 64.6866 | -58.2275 | -58.3145 | -0.013733 | -0.050354 | -0.064087 | -0.041199 | -0.15106 | -0.10071 | 0.027466 | -0.009155 | -0.09613 | 0 | 0.068665 | -0.26093 | -0.16479 | -0.10529 | 122.9462 | 123.0377 | 58.0719 | -123.0606 | 123.0103 | 122.905 | 58.1909 | -123.1064
115.8438 | 123.2849 | -58.2047 | 64.7461 | 0.91531 | 0.0098641 | 0.064947 | -0.0029322 | 0.06433 | 0.0043877 | -0.015707 | 0.42828 | -0.003121 | 0.059841 | 0.065265 | 6.2882e-05 | -0.0020211 | 64.8331 | -58.1635 | -0.064087 | -58.4015 | 64.7324 | -58.2184 | -58.2642 | -58.0856 | 0.054932 | -58.4335 | 64.7507 | 64.7095 | -58.1955 | -58.3328 | -0.013733 | -0.059509 | -0.013733 | 0.041199 | -0.19684 | -0.13733 | 0.086975 | 0.009155 | -0.12817 | 0.004577 | 0.11902 | -0.22888 | -0.10071 | -0.036621 | 122.937 | 123.0377 | 58.1406 | -123.0103 | 122.9553 | 122.9141 | 58.2596 | -123.0789
116.8438 | 123.2849 | -58.1726 | 64.7324 | 0.51858 | -0.0018849 | 0.059606 | -0.0082732 | 0.067534 | -0.00095325 | -0.0039582 | 0.59613 | -0.004189 | 0.060909 | 0.046039 | -0.0020731 | 0.0022509 | 64.8651 | -58.1177 | -0.004578 | -58.3603 | 64.6774 | -58.2047 | -58.2321 | -58.0719 | 0.045776 | -58.3969 | 64.7644 | 64.6957 | -58.1909 | -58.3191 | -0.032044 | -0.05951 | -0.054932 | 0.054931 | -0.18768 | -0.12817 | 0.13275 | -0.018311 | -0.14648 | 0.032043 | 0.10071 | -0.22431 | -0.07782 | -0.036621 | 122.85 | 123.0377 | 58.168 | -122.9645 | 122.937 | 122.8683 | 58.2184 | -123.0515
117.8438 | 123.111 | -58.2092 | 64.7964 | 0.18289 | 0.020545 | 0.064947 | 0.0013408 | 0.076079 | 0.0033197 | 0.0099268 | 0.046815 | 8.4049e-05 | 0.067318 | 0.058857 | 0.0086079 | -0.011634 | 64.8285 | -58.6395 | -0.30212 | -58.7219 | 64.7003 | -58.287 | -58.3008 | -58.1589 | -0.036621 | -58.548 | 64.8148 | 64.7095 | -58.2275 | -58.3557 | -0.077819 | -0.091552 | -0.096131 | -0.4303 | -0.5127 | -0.42114 | 0.032043 | -0.01831 | -0.14648 | 0.01831 | 0.050354 | -0.33875 | -0.19226 | -0.086975 | 122.9095 | 123.0377 | 57.9071 | -123.0972 | 123.024 | 122.9187 | 58.1726 | -123.1522
118.8438 | 123.1293 | -58.2184 | 64.7873 | -1.3888 | 0.012 | 0.066015 | 0.0066808 | 0.071807 | 0.010797 | 0.0045868 | 0.2757 | -0.010597 | 0.048092 | 0.054584 | 0.020357 | 0.0011829 | 64.8331 | -58.2001 | -0.11444 | -58.4473 | 64.7827 | -58.2413 | -58.2596 | -58.2138 | -0.045776 | -58.5526 | 64.8056 | 64.7232 | -58.2092 | -58.342 | -0.022888 | -0.041199 | -0.004577 | 0.018311 | -0.22888 | -0.18768 | 0.045777 | 0.009155 | -0.1236 | 0.018311 | 0.004578 | -0.33417 | -0.21057 | -0.064086 | 123.0011 | 123.0515 | 58.1039 | -123.0469 | 123.024 | 122.9416 | 58.1726 | -123.1293
119.8438 | 123.1155 | -58.2047 | 64.7964 | 0.27444 | 0.0013191 | 0.068151 | 0.010954 | 0.068602 | 0.017205 | 0.0077908 | 0.092591 | 0.009697 | 0.060909 | 0.05138 | 0.025698 | 0.0022509 | 64.8193 | -58.2092 | -0.07782 | -58.4244 | 64.7598 | -58.2367 | -58.2733 | -58.3145 | 0.24261 | -58.4381 | 64.8468 | 64.7919 | -58.2047 | -58.3282 | -0.032043 | -0.068664 | -0.036621 | -0.004578 | -0.21973 | -0.15106 | 0.022888 | 0 | -0.1236 | 0.050354 | -0.10986 | -0.23346 | -0.10986 | -0.004578 | 122.9645 | 123.024 | 58.1268 | -123.0698 | 123.0515 | 122.9965 | 58.4473 | -123.1247
120.8438 | 123.143 | -58.2047 | 64.7781 | 0.13711 | 0.010932 | 0.058538 | 0.0045448 | 0.066466 | 0.0097277 | 0.0024508 | 0.18414 | 0.003288 | 0.067318 | 0.067401 | 0.0086079 | -0.0073621 | 64.8056 | -58.2047 | -0.064087 | -58.4106 | 64.7736 | -58.2184 | -58.2504 | -58.168 | 0.009155 | -58.5297 | 64.801 | 64.7415 | -58.2138 | -58.342 | -0.013733 | -0.045776 | -0.004577 | 0 | -0.20599 | -0.16022 | 0.027466 | -0.009155 | -0.13733 | 0.022888 | 0.036621 | -0.32501 | -0.18768 | -0.036621 | 122.9782 | 123.0103 | 58.1406 | -123.0286 | 123.0057 | 122.9462 | 58.2138 | -123.1201
121.8438 | 123.2483 | -58.1818 | 64.7369 | 0.59487 | -0.0029529 | 0.0799 | -0.0093412 | 0.063262 | -0.0084293 | 0.0067228 | 0.41303 | 0.001152 | 0.048092 | 0.06847 | 0.0021989 | 0.0011829 | 64.856 | -58.1177 | -0.018311 | -58.3511 | 64.7232 | -58.223 | -58.2458 | -58.0444 | -0.13733 | -58.5617 | 64.7095 | 64.65 | -58.2458 | -58.2916 | -0.041198 | -0.064087 | -0.013732 | 0.064087 | -0.16937 | -0.10529 | 0.11902 | -0.064087 | -0.10986 | -0.027465 | 0.13733 | -0.37994 | -0.27008 | -0.086975 | 122.905 | 123.0377 | 58.1635 | -122.9828 | 122.8912 | 122.8317 | 58.0444 | -123.0286
122.8438 | 123.1476 | -58.1909 | 64.8056 | 0.15237 | 0.0087961 | 0.061742 | -0.0018642 | 0.061125 | 0.0043877 | -0.0028902 | -0.01422 | 8.4049e-05 | 0.070522 | 0.036426 | 0.0086079 | -0.0062931 | 64.856 | -58.136 | -0.018311 | -58.3969 | 64.7461 | -58.223 | -58.2642 | -58.1268 | 0.064087 | -58.4839 | 64.7919 | 64.7369 | -58.2092 | -58.3237 | -0.032043 | -0.073242 | -0.059509 | 0.054932 | -0.20599 | -0.13275 | 0.050354 | -0.018311 | -0.13275 | -0.013733 | 0.064087 | -0.29297 | -0.16022 | -0.068665 | 122.937 | 123.0469 | 58.1726 | -123.0698 | 122.9828 | 122.9279 | 58.255 | -123.1293
123.8438 | 123.1064 | -58.2367 | 64.7827 | 0.27444 | 0.022682 | 0.058538 | 0.0013408 | 0.063262 | 0.015069 | 0.00031381 | 0.062074 | -0.00098395 | 0.060909 | 0.067401 | 0.0043349 | -0.0041571 | 64.7873 | -58.2367 | -0.09613 | -58.4335 | 64.7827 | -58.2367 | -58.2642 | -58.2092 | -0.073242 | -58.5526 | 64.8056 | 64.7186 | -58.2275 | -58.3328 | 0 | -0.027466 | 0 | 0 | -0.19684 | -0.16937 | 0.004577 | 0.009155 | -0.096131 | 0.022888 | 0.027465 | -0.31586 | -0.21973 | -0.064087 | 123.0194 | 123.024 | 58.1406 | -123.0469 | 123.0423 | 122.9553 | 58.1635 | -123.1155
124.8438 | 123.1842 | -58.2047 | 64.7736 | -0.00022031 | 0.00025114 | 0.072424 | 0.0034768 | 0.068602 | 0.0011837 | 0.00031381 | -0.15155 | 0.001152 | 0.059841 | 0.057788 | 0.0096759 | -0.0094981 | 64.8605 | -58.1268 | 0.009155 | -58.374 | 64.7827 | -58.2001 | -58.2458 | -58.136 | 0.082397 | -58.461 | 64.8102 | 64.7461 | -58.2092 | -58.3008 | 0.004578 | -0.041199 | 0.009155 | 0.07782 | -0.16937 | -0.12817 | 0.086975 | -0.004578 | -0.09613 | 0.036621 | 0.068665 | -0.25635 | -0.16022 | -0.027466 | 122.9874 | 123.0652 | 58.2138 | -123.0194 | 123.0148 | 122.9507 | 58.287 | -123.0743
125.8438 | 123.1705 | -58.1726 | 64.8056 | -0.33591 | -0.0072259 | 0.067083 | 0.0066808 | 0.067534 | -0.019111 | -0.016776 | -0.2431 | -0.010597 | 0.067318 | 0.047107 | 0.0064719 | -0.0020211 | 64.801 | -58.1955 | -0.009155 | -58.4015 | 64.801 | -58.2275 | -58.2458 | -58.1451 | 0.068665 | -58.4793 | 64.8468 | 64.7736 | -58.1909 | -58.2916 | -0.054932 | -0.073243 | -0.004578 | -0.022889 | -0.22888 | -0.15564 | -0.004578 | -0.018311 | -0.11902 | 0.041199 | 0.027465 | -0.3067 | -0.18768 | -0.032043 | 122.9736 | 122.9736 | 58.1635 | -123.0515 | 123.0194 | 122.9462 | 58.2413 | -123.0972
126.8438 | 123.143 | -58.2092 | 64.7919 | 0.060816 | 0.0013191 | 0.066015 | 0.01309 | 0.066466 | 0.016137 | -0.00075419 | 0.062074 | 0.008629 | 0.069454 | 0.063129 | 6.2882e-05 | -0.0030891 | 64.8468 | -58.1589 | 0.009155 | -58.3694 | 64.7919 | -58.2138 | -58.223 | -58.1497 | 0.050354 | -58.4793 | 64.8239 | 64.7324 | -58.2184 | -58.3282 | -0.004577 | -0.013732 | 0 | 0.050354 | -0.16022 | -0.14649 | 0.054932 | -0.009155 | -0.11902 | 0.032044 | 0.05951 | -0.27008 | -0.15106 | -0.059509 | 123.0011 | 123.056 | 58.2184 | -123.0148 | 123.0331 | 122.9416 | 58.2596 | -123.1201
127.8438 | 123.1796 | -58.1909 | 64.7736 | 0.015039 | 0.010932 | 0.063879 | -0.0018642 | 0.055785 | 0.0033197 | 0.0045868 | -0.044738 | -0.002053 | 0.070522 | 0.058857 | -0.0052781 | 0.0065239 | 64.856 | -58.136 | -0.004578 | -58.3786 | 64.7781 | -58.2047 | -58.2458 | -58.1863 | 0.004578 | -58.429 | 64.8331 | 64.7461 | -58.2092 | -58.3328 | -0.013733 | -0.054932 | 0.004577 | 0.054932 | -0.18768 | -0.13275 | 0.082397 | -0.018311 | -0.14191 | 0.059509 | 0.004578 | -0.23804 | -0.09613 | -0.027466 | 122.9691 | 123.0469 | 58.1863 | -123.0194 | 123.024 | 122.937 | 58.1955 | -123.1064
128.8438 | 123.1842 | -58.2092 | 64.801 | 0.045557 | 0.0034561 | 0.071355 | -0.0029322 | 0.06433 | -0.00095325 | -0.0060942 | -0.3194 | 0.005424 | 0.061977 | 0.053516 | -0.0020731 | 0.00011494 | 64.8788 | -58.1726 | -0.045776 | -58.3694 | 64.7873 | -58.2458 | -58.2413 | -58.1223 | 0.064087 | -58.4793 | 64.8148 | 64.7324 | -58.1955 | -58.3237 | -0.036621 | -0.032043 | -0.013733 | 0.036622 | -0.16022 | -0.12817 | 0.07782 | 0.013733 | -0.11444 | 0.013733 | 0.086976 | -0.27008 | -0.15564 | -0.068664 | 122.9965 | 123.0881 | 58.1635 | -123.0423 | 123.024 | 122.9416 | 58.2733 | -123.1247
129.8438 | 123.1659 | -58.1955 | 64.7919 | -0.15281 | 0.00025114 | 0.07456 | 0.014158 | 0.06433 | -0.0052253 | -0.0092992 | -0.27362 | -0.011666 | 0.048092 | 0.05138 | -0.0042101 | 0.0054559 | 64.8285 | -58.1497 | 0 | -58.3786 | 64.7919 | -58.2047 | -58.2413 | -58.1497 | 0.082397 | -58.4656 | 64.8285 | 64.7598 | -58.1726 | -58.3145 | -0.009155 | -0.045776 | 0 | 0.045777 | -0.18311 | -0.13733 | 0.036621 | 0.022889 | -0.11902 | 0.036621 | 0.045777 | -0.27008 | -0.15106 | -0.032043 | 122.9874 | 123.024 | 58.1955 | -123.0331 | 123.024 | 122.9553 | 58.2779 | -123.1064
130.8438 | 123.1842 | -58.1635 | 64.8102 | -0.13755 | 0.024818 | 0.070287 | -0.0040002 | 0.072875 | -0.011634 | -0.0028902 | -0.25836 | 0.00222 | 0.053432 | 0.072742 | -0.0063461 | -0.0020211 | 64.8193 | -58.1818 | -0.013733 | -58.3832 | 64.7736 | -58.2047 | -58.2367 | -58.1497 | 0.082397 | -58.4518 | 64.8285 | 64.769 | -58.2047 | -58.3191 | -0.041199 | -0.073242 | -0.036621 | -0.018311 | -0.21973 | -0.14648 | 0.009155 | -0.041199 | -0.15564 | 0.01831 | 0.013733 | -0.28839 | -0.13275 | -0.041199 | 122.937 | 122.9828 | 58.1497 | -123.0469 | 122.9919 | 122.9324 | 58.2458 | -123.1293
131.8438 | 123.1567 | -58.2138 | 64.7781 | 0.48806 | 0.0077281 | 0.066015 | -0.00079616 | 0.062194 | 0.0086597 | -0.0071622 | 0.41303 | 0.006492 | 0.051296 | 0.058857 | -0.011686 | 0.010796 | 64.7644 | -58.255 | -0.13733 | -58.4564 | 64.769 | -58.255 | -58.2642 | -58.0582 | -0.022888 | -58.5022 | 64.8376 | 64.7461 | -58.2504 | -58.342 | -0.041199 | -0.050354 | -0.009155 | -0.041199 | -0.24262 | -0.19226 | -0.013733 | -0.036621 | -0.12817 | 0.059509 | 0.15564 | -0.28839 | -0.16022 | -0.032043 | 122.9828 | 122.9782 | 58.0765 | -123.0423 | 123.0515 | 122.9599 | 58.1909 | -123.1201
132.8438 | 123.1155 | -58.1772 | 64.8193 | -0.24436 | -0.01043 | 0.072424 | -0.0050682 | 0.072875 | -0.025519 | -0.014639 | 0.062074 | -0.012734 | 0.037411 | 0.066333 | -0.013823 | 0.0054559 | 64.8239 | -58.1314 | 0.032043 | -58.3832 | 64.7873 | -58.1772 | -58.2596 | -58.1589 | 0.07782 | -58.4747 | 64.856 | 64.7598 | -58.1909 | -58.3008 | 0 | -0.082398 | -0.032044 | 0.045776 | -0.20599 | -0.1236 | 0.004578 | -0.013733 | -0.1236 | 0.036621 | 0.01831 | -0.29755 | -0.17395 | -0.059509 | 122.9645 | 123.0011 | 58.2092 | -123.0789 | 123.0331 | 122.937 | 58.255 | -123.1201
133.8438 | 123.1247 | -58.2047 | 64.8193 | -0.39695 | -0.014702 | 0.085241 | 0.0066808 | 0.071807 | -0.010566 | -0.0039582 | -0.2431 | 0.004356 | 0.069454 | 0.055652 | -0.0084821 | -0.0030891 | 64.8102 | -58.1589 | -0.018311 | -58.4061 | 64.8102 | -58.1818 | -58.2596 | -58.1589 | 0.064087 | -58.4747 | 64.8376 | 64.7461 | -58.1909 | -58.3191 | 0.022888 | -0.054932 | -0.009155 | 0.045776 | -0.20142 | -0.14648 | -0.009155 | 0.013733 | -0.11444 | 0.01831 | 0.045776 | -0.27008 | -0.15564 | -0.073242 | 123.0148 | 123.0148 | 58.1863 | -123.0789 | 123.0423 | 122.9507 | 58.2687 | -123.1384
134.8438 | 123.1293 | -58.1863 | 64.8331 | -0.25962 | -0.01043 | 0.069219 | -0.0040002 | 0.066466 | -0.0052253 | -0.015707 | -1.006 | 8.4049e-05 | 0.068386 | 0.057788 | 6.2882e-05 | -0.0062931 | 64.801 | -58.168 | 0 | -58.3237 | 64.8193 | -58.1818 | -58.2275 | -58.1863 | 0.036621 | -58.4793 | 64.856 | 64.7598 | -58.2001 | -58.3008 | 0.004577 | -0.041199 | -0.013733 | 0.01831 | -0.13733 | -0.09613 | -0.032044 | -0.013733 | -0.11444 | 0.022888 | 0 | -0.29297 | -0.17853 | -0.073242 | 123.0057 | 122.9874 | 58.1863 | -123.0606 | 123.0423 | 122.9462 | 58.223 | -123.1338
135.8438 | 123.2025 | -58.1818 | 64.7964 | -0.2291 | -0.014702 | 0.064947 | 0.0045448 | 0.065398 | 0.0075917 | 0.0013818 | -0.21259 | 0.007561 | 0.051296 | 0.060993 | -0.0031411 | -0.0052251 | 64.8331 | -58.1543 | 0 | -58.3786 | 64.8102 | -58.2047 | -58.2596 | -58.136 | 0.059509 | -58.461 | 64.8285 | 64.7415 | -58.2092 | -58.3099 | -0.022888 | -0.07782 | 0.013733 | 0.027466 | -0.19684 | -0.11902 | 0.036621 | -0.027466 | -0.12817 | 0.032043 | 0.045777 | -0.27924 | -0.15106 | -0.054932 | 122.9919 | 123.0148 | 58.1818 | -123.056 | 123.0103 | 122.9233 | 58.2413 | -123.1064
136.8438 | 123.1384 | -58.1635 | 64.8148 | 0.35073 | 0.013069 | 0.069219 | -0.0040002 | 0.057921 | 0.0043877 | -0.0082312 | 0.36725 | 0.003288 | 0.057705 | 0.074878 | 0.0011309 | 0.0043879 | 64.7507 | -58.2642 | -0.14191 | -58.4473 | 64.7919 | -58.2458 | -58.2642 | -58.2047 | -0.086975 | -58.5388 | 64.7919 | 64.7003 | -58.2367 | -58.3832 | -0.082398 | -0.10071 | -0.022888 | -0.10071 | -0.28381 | -0.18311 | -0.064087 | -0.073242 | -0.21973 | -0.022888 | -0.041199 | -0.37537 | -0.15564 | -0.11444 | 122.9553 | 122.9141 | 58.0215 | -123.0789 | 122.9553 | 122.8638 | 58.0765 | -123.1979
137.8438 | 123.2483 | -58.1497 | 64.769 | 0.32021 | -0.025384 | 0.068151 | 0.0045448 | 0.065398 | -0.0362 | -0.0050262 | -0.090514 | -0.010597 | 0.059841 | 0.060993 | -0.011686 | 0.0022509 | 64.8697 | -58.0444 | 0.086975 | -58.3237 | 64.7232 | -58.1726 | -58.2367 | -58.0902 | 0.17395 | -58.3694 | 64.7827 | 64.7232 | -58.1726 | -58.2687 | -0.022888 | -0.086975 | -0.045776 | 0.10528 | -0.17395 | -0.086975 | 0.10071 | -0.022888 | -0.11902 | 0.013733 | 0.059509 | -0.21973 | -0.10071 | -0.045776 | 122.8729 | 123.0194 | 58.2367 | -123.0057 | 122.9324 | 122.8729 | 58.3237 | -123.0377
138.8438 | 123.23 | -58.1543 | 64.7736 | -0.2291 | -0.030724 | 0.072424 | 0.0013408 | 0.067534 | -0.012702 | -0.014639 | -0.16681 | -0.008461 | 0.043819 | 0.063129 | -0.0010051 | 0.0043879 | 64.8514 | -58.0399 | 0.07782 | -58.3328 | 64.7644 | -58.1497 | -58.223 | -58.0856 | 0.14648 | -58.4152 | 64.8102 | 64.7369 | -58.1635 | -58.3008 | 0.004578 | -0.068664 | -0.009156 | 0.11444 | -0.17853 | -0.10986 | 0.077819 | -0.009155 | -0.14648 | 0.036621 | 0.068665 | -0.26093 | -0.11444 | -0.036622 | 122.9187 | 123.0057 | 58.2321 | -122.9965 | 122.9645 | 122.8912 | 58.3008 | -123.0743
139.8438 | 123.2849 | -58.1406 | 64.7644 | 0.045557 | -0.011498 | 0.071355 | -0.010409 | 0.058989 | -0.032996 | -0.017844 | 0.18414 | -0.018074 | 0.047024 | 0.059925 | -0.010618 | 0.0054559 | 64.856 | -58.0719 | 0.045776 | -58.342 | 64.7598 | -58.1909 | -58.2275 | -58.049 | 0.1236 | -58.3694 | 64.7781 | 64.6912 | -58.1497 | -58.2825 | -0.050354 | -0.086975 | -0.004577 | 0.068665 | -0.20142 | -0.11444 | 0.091553 | -0.009155 | -0.14191 | 0.013733 | 0.091553 | -0.22888 | -0.086975 | -0.073242 | 122.9004 | 122.9965 | 58.1863 | -122.9919 | 122.9187 | 122.8317 | 58.2642 | -123.0469
140.8438 | 123.2529 | -58.1589 | 64.769 | 0.091333 | -0.034997 | 0.078832 | 0.0088168 | 0.060057 | -0.018043 | -0.0028902 | 0.18414 | -0.007393 | 0.035275 | 0.049243 | -0.0074141 | 0.0011829 | 64.8605 | -58.1039 | 0.018311 | -58.3786 | 64.7369 | -58.2138 | -58.223 | -58.0673 | 0.10986 | -58.3969 | 64.7964 | 64.7003 | -58.1772 | -58.2916 | -0.054931 | -0.064086 | -0.032044 | 0.054932 | -0.21973 | -0.15564 | 0.091553 | -0.01831 | -0.13275 | 0.027466 | 0.091553 | -0.23804 | -0.10529 | -0.068665 | 122.8958 | 123.0194 | 58.1772 | -122.9919 | 122.9553 | 122.8592 | 58.2687 | -123.0606
141.8438 | 123.1613 | -58.1772 | 64.801 | -0.27488 | -0.014702 | 0.0799 | 0.01309 | 0.072875 | -0.0052253 | -0.0018222 | -0.12103 | -0.005257 | 0.053432 | 0.049243 | -0.0020731 | -0.0052251 | 64.856 | -58.1131 | 0.022888 | -58.3832 | 64.7781 | -58.223 | -58.2092 | -58.136 | 0.032043 | -58.4839 | 64.856 | 64.7644 | -58.1772 | -58.3191 | -0.045776 | -0.032044 | -0.022888 | 0.064087 | -0.20599 | -0.17395 | 0.054932 | 0 | -0.14191 | 0.054932 | 0.041199 | -0.3067 | -0.1648 | -0.036621 | 122.9553 | 123.0331 | 58.2001 | -123.0103 | 123.0331 | 122.9416 | 58.2092 | -123.1201
142.8438 | 123.2574 | -58.1406 | 64.7736 | -0.16807 | -0.022179 | 0.070287 | -0.0082732 | 0.065398 | -0.01377 | -0.015707 | -0.2431 | -0.013802 | 0.051296 | 0.047107 | 0.0011309 | -0.0094981 | 64.9063 | -58.0353 | 0.10986 | -58.3328 | 64.7873 | -58.168 | -58.2138 | -58.0582 | 0.1831 | -58.3832 | 64.7873 | 64.7278 | -58.1726 | -58.2642 | -0.027466 | -0.073242 | 0.013732 | 0.10529 | -0.19226 | -0.11902 | 0.13275 | -0.032043 | -0.1236 | 0.013732 | 0.082397 | -0.24262 | -0.11902 | -0.045777 | 122.9279 | 123.0469 | 58.2504 | -122.9874 | 122.9279 | 122.8683 | 58.3237 | -123.0377
143.8438 | 123.1979 | -58.1635 | 64.8056 | -0.24436 | -0.020043 | 0.075628 | 0.00027184 | 0.051512 | -0.00095325 | -0.011435 | -0.28888 | -0.017006 | 0.054501 | 0.052448 | 0.0011309 | -0.0041571 | 64.8743 | -58.0444 | 0.086975 | -58.3466 | 64.7552 | -58.1772 | -58.2184 | -58.0902 | 0.14191 | -58.4198 | 64.801 | 64.7003 | -58.2001 | -58.287 | -0.013733 | -0.054932 | -0.050354 | 0.11902 | -0.18311 | -0.12817 | 0.068665 | -0.036621 | -0.1236 | -0.004578 | 0.073242 | -0.25635 | -0.13275 | -0.10529 | 122.9187 | 123.0377 | 58.2504 | -123.024 | 122.9645 | 122.8638 | 58.3054 | -123.0927
144.8438 | 123.2666 | -58.1497 | 64.7736 | 0.015039 | -0.023247 | 0.0799 | -0.0018642 | 0.056853 | -0.010566 | -0.0018222 | 0.062074 | -0.012734 | 0.063046 | 0.06847 | -0.0042101 | -0.0041571 | 64.8605 | -58.0765 | 0.050354 | -58.342 | 64.7827 | -58.1863 | -58.2138 | -58.0399 | 0.12817 | -58.3878 | 64.7598 | 64.6774 | -58.1635 | -58.3237 | -0.036621 | -0.064087 | 0.009155 | 0.073242 | -0.19226 | -0.12817 | 0.086975 | -0.013733 | -0.17395 | -0.013733 | 0.10986 | -0.23804 | -0.064087 | -0.096131 | 122.9324 | 123.0103 | 58.2001 | -122.9874 | 122.9095 | 122.8271 | 58.2779 | -123.0972
145.8438 | 123.262 | -58.1268 | 64.7781 | -0.12229 | -0.034997 | 0.073492 | -0.0018642 | 0.066466 | -0.011634 | 0.00031381 | -0.090514 | -0.019142 | 0.063046 | 0.030017 | -0.014891 | -0.0020211 | 64.888 | -58.017 | 0.09613 | -58.3511 | 64.7552 | -58.1726 | -58.2367 | -57.8156 | -0.20142 | -58.4427 | 64.7827 | 64.6454 | -58.1955 | -58.3054 | -0.045776 | -0.10986 | -0.022888 | 0.10986 | -0.2243 | -0.11444 | 0.10986 | -0.068665 | -0.17853 | 0.004578 | 0.31128 | -0.31586 | -0.13733 | -0.13275 | 122.8821 | 123.0148 | 58.223 | -123.0148 | 122.9095 | 122.7722 | 57.9254 | -123.0835
146.8438 | 123.2666 | -58.1406 | 64.769 | 3.3262 | -0.018975 | 0.069219 | -0.0061362 | 0.06967 | -0.0094983 | -0.0060942 | -0.21259 | -0.018074 | 0.041683 | 0.057788 | -0.0020731 | -0.010566 | 64.8743 | -58.0444 | 0.073242 | -58.3282 | 64.7415 | -58.1863 | -58.223 | -58.0399 | 0.16937 | -58.3557 | 64.7873 | 64.6912 | -58.136 | -58.2733 | -0.045776 | -0.082397 | -0.027466 | 0.09613 | -0.18768 | -0.10529 | 0.10529 | 0.004578 | -0.13275 | 0.01831 | 0.10071 | -0.21515 | -0.082398 | -0.07782 | 122.8821 | 123.0148 | 58.2138 | -122.9919 | 122.9279 | 122.8317 | 58.3099 | -123.0423
147.8438 | 123.2071 | -58.1818 | 64.7827 | 0.16763 | -0.021111 | 0.0799 | -0.0050682 | 0.062194 | 0.0065237 | -0.0050262 | 0.1994 | -0.009529 | 0.04916 | 0.060993 | 0.0032669 | -0.0073621 | 64.8331 | -58.1131 | -0.027466 | -58.3832 | 64.7552 | -58.1955 | -58.2504 | -58.0856 | 0.064087 | -58.429 | 64.8056 | 64.6774 | -58.1772 | -58.3099 | -0.013733 | -0.068664 | -0.027466 | 0.068665 | -0.20142 | -0.13275 | 0.050354 | 0.004578 | -0.12817 | 0.022888 | 0.096131 | -0.24719 | -0.11902 | -0.10529 | 122.937 | 123.0148 | 58.1543 | -123.0331 | 122.9874 | 122.8592 | 58.2458 | -123.0927
148.8438 | 123.2117 | -58.168 | 64.7736 | 1.4341 | -0.014702 | 0.067083 | 0.0013408 | 0.060057 | -0.0094983 | -0.018912 | 0.1994 | -0.010597 | 0.050228 | 0.069538 | 0.0021989 | 0.00011494 | 64.8331 | -58.1497 | -0.032043 | -58.4106 | 64.7415 | -58.2092 | -58.2367 | -58.1039 | 0.022888 | -58.4656 | 64.7827 | 64.682 | -58.168 | -58.3237 | -0.041199 | -0.068664 | -0.032044 | 0.018311 | -0.24262 | -0.17395 | 0.059509 | 0 | -0.15564 | 0.009155 | 0.064087 | -0.29755 | -0.14191 | -0.091553 | 122.9095 | 123.0011 | 58.136 | -123.0103 | 122.9507 | 122.85 | 58.1909 | -123.0972
149.8438 | 123.2483 | -58.1497 | 64.7736 | 0.19814 | -0.023247 | 0.073492 | -0.0061362 | 0.058989 | -0.0041573 | -0.014639 | 0.092591 | -0.01487 | 0.044888 | 0.05138 | -0.0042101 | -0.0020211 | 64.8468 | -58.0948 | -0.018311 | -58.3786 | 64.7552 | -58.223 | -58.2275 | -58.0765 | 0.068665 | -58.4335 | 64.7781 | 64.6774 | -58.1726 | -58.2779 | -0.073242 | -0.07782 | -0.018311 | 0.054931 | -0.22888 | -0.15106 | 0.073242 | -0.022888 | -0.12817 | 0.004577 | 0.073242 | -0.28381 | -0.15564 | -0.096131 | 122.905 | 122.9965 | 58.1314 | -123.0011 | 122.9279 | 122.8271 | 58.2184 | -123.0515
150.8438 | 123.23 | -58.1635 | 64.7461 | 0.13711 | -0.029656 | 0.070287 | -0.0040002 | 0.06433 | -0.0094983 | 0.0035188 | 0.1994 | 8.4049e-05 | 0.033138 | 0.059925 | 0.0032669 | 0.0011829 | 64.8376 | -58.1131 | -0.027466 | -58.3969 | 64.7461 | -58.2001 | -58.2458 | -58.0856 | 0.064087 | -58.4335 | 64.7781 | 64.682 | -58.1772 | -58.2916 | -0.036621 | -0.082398 | 0 | 0.050354 | -0.23346 | -0.15106 | 0.091552 | -0.013733 | -0.12817 | 0.032043 | 0.07782 | -0.27008 | -0.14191 | -0.064087 | 122.9095 | 123.0011 | 58.136 | -122.9919 | 122.9416 | 122.8455 | 58.2275 | -123.0377
151.8438 | 123.2117 | -58.1909 | 64.769 | 1.19 | -0.023247 | 0.083105 | -0.0061362 | 0.063262 | 0.00011475 | -0.0071622 | 0.29095 | -0.004189 | 0.061977 | 0.069538 | 0.010744 | -0.012702 | 64.8239 | -58.1497 | -0.027466 | -58.4015 | 64.7507 | -58.2275 | -58.255 | -58.1039 | 0.032043 | -58.4473 | 64.7598 | 64.6774 | -58.1726 | -58.2916 | -0.036621 | -0.064087 | -0.018311 | 0.041199 | -0.21057 | -0.14648 | 0.054932 | 0.018311 | -0.10071 | -0.009155 | 0.086975 | -0.25635 | -0.15564 | -0.091553 | 122.9416 | 123.0148 | 58.1635 | -123.024 | 122.9507 | 122.8683 | 58.223 | -123.0606
152.8438 | 123.1888 | -58.1726 | 64.7598 | 0.30496 | -0.021111 | 0.083105 | -0.0029322 | 0.065398 | -0.03086 | 0.0013818 | 0.092591 | -0.006325 | 0.04916 | 0.074878 | 0.0043349 | -0.0020211 | 64.9612 | -58.1497 | -0.013733 | -58.4152 | 64.7552 | -58.1772 | -58.2275 | -58.1085 | 0.036621 | -58.4473 | 64.769 | 64.6683 | -58.2001 | -58.3054 | -0.004578 | -0.054932 | -0.004578 | 0.022888 | -0.24262 | -0.18768 | 0.20142 | -0.027466 | -0.13275 | 0.009155 | 0.064086 | -0.27466 | -0.14191 | -0.091553 | 122.9279 | 123.1338 | 58.1589 | -122.9874 | 122.9416 | 122.8409 | 58.2092 | -123.0652
153.8438 | 123.2346 | -58.1635 | 64.7461 | 0.38125 | -0.0082939 | 0.063879 | 0.0024088 | 0.058989 | 0.0033197 | -0.0071622 | 0.35199 | -0.003121 | 0.064114 | 0.058857 | 0.0054039 | -0.0041571 | 64.888 | -58.0902 | -0.009155 | -58.3878 | 64.7141 | -58.2092 | -58.2596 | -58.0719 | 0.027466 | -58.4198 | 64.7461 | 64.6591 | -58.1909 | -58.3282 | -0.045777 | -0.096131 | -0.032044 | 0.073242 | -0.2243 | -0.12817 | 0.14191 | -0.027466 | -0.16479 | 0 | 0.091553 | -0.25635 | -0.091553 | -0.086975 | 122.8775 | 123.0515 | 58.1543 | -123.0057 | 122.9095 | 122.8226 | 58.1909 | -123.0743
154.8438 | 123.2117 | -58.168 | 64.7324 | 0.41177 | -0.024315 | 0.061742 | 0.0013408 | 0.065398 | -0.00095325 | -0.0039582 | 0.47406 | 0.001152 | 0.051296 | 0.054584 | 0.0011309 | -0.0030891 | 64.8376 | -58.1131 | -0.036621 | -58.4015 | 64.7461 | -58.2138 | -58.2413 | -58.0811 | 0.018311 | -58.4427 | 64.7919 | 64.7003 | -58.1909 | -58.2916 | -0.045776 | -0.073242 | 0.013733 | 0.054932 | -0.23346 | -0.16022 | 0.10529 | -0.022888 | -0.1236 | 0.059509 | 0.086975 | -0.27466 | -0.15106 | -0.032044 | 122.9141 | 123.0057 | 58.1314 | -122.9736 | 122.9599 | 122.8683 | 58.1863 | -123.024
155.8438 | 123.2025 | -58.1589 | 64.7369 | 0.45754 | -0.012566 | 0.069219 | -0.0018642 | 0.058989 | -0.00095325 | -0.0071622 | 0.29095 | -0.006325 | 0.057705 | 0.055652 | 0.0032669 | -0.0020211 | 64.8605 | -58.0994 | -0.022888 | -58.3878 | 64.7324 | -58.2092 | -58.2413 | -58.0856 | 0.036621 | -58.4335 | 64.7827 | 64.6637 | -58.1909 | -58.3099 | -0.050354 | -0.082397 | -0.004577 | 0.05951 | -0.22888 | -0.14648 | 0.1236 | -0.032043 | -0.15106 | 0.045777 | 0.073243 | -0.27466 | -0.1236 | -0.073242 | 122.8912 | 123.0194 | 58.136 | -122.9782 | 122.9416 | 122.8226 | 58.1955 | -123.0469
156.8438 | 123.2254 | -58.2001 | 64.769 | 0.50332 | -0.014702 | 0.076696 | 0.0024088 | 0.066466 | 0.0033197 | -0.0039582 | -0.67035 | -0.008461 | 0.068386 | 0.07381 | 0.0032669 | 0.0011829 | 64.8331 | -58.1909 | 0.13733 | -58.287 | 64.8056 | -58.1726 | -58.223 | -58.1268 | 0.036621 | -58.4381 | 64.769 | 64.6683 | -58.2001 | -58.3099 | 0.027466 | -0.022888 | 0.036621 | 0.009155 | -0.086975 | -0.064087 | 0.064087 | 0 | -0.10986 | 0 | 0.073242 | -0.23804 | -0.12817 | -0.10071 | 123.0057 | 123.0331 | 58.3374 | -122.9919 | 122.9691 | 122.8683 | 58.2367 | -123.0789
157.8438 | 123.1934 | -58.168 | 64.7552 | 0.39651 | -0.0061569 | 0.064947 | 0.0024088 | 0.065398 | 0.00011475 | -0.0071622 | 0.24518 | -0.01487 | 0.056637 | 0.052448 | 0.0011309 | -0.0062931 | 64.8514 | -58.1131 | -0.045776 | -58.4015 | 64.7278 | -58.2184 | -58.2367 | -57.9529 | -0.07782 | -58.4427 | 64.8056 | 64.6774 | -58.168 | -58.2962 | -0.050354 | -0.068664 | -0.027466 | 0.054932 | -0.23346 | -0.16479 | 0.09613 | 0 | -0.12817 | 0.050354 | 0.21515 | -0.27466 | -0.14648 | -0.07782 | 122.8958 | 123.0194 | 58.1223 | -122.9919 | 122.9736 | 122.8455 | 58.0902 | -123.0515
158.8438 | 123.2483 | -58.1772 | 64.7873 | 0.41177 | -0.012566 | 0.070287 | -0.0050682 | 0.060057 | 0.0033197 | -0.00075419 | 0.36725 | -0.010597 | 0.052364 | 0.052448 | 0.0043349 | -0.0030891 | 64.8422 | -58.1177 | -0.027466 | -58.4015 | 64.7232 | -58.2001 | -58.2504 | -58.0765 | 0.022888 | -58.4427 | 64.7415 | 64.682 | -58.168 | -58.3191 | -0.022888 | -0.073242 | -0.064086 | 0.059509 | -0.2243 | -0.15106 | 0.054932 | 0.009155 | -0.14191 | -0.045776 | 0.10071 | -0.2655 | -0.1236 | -0.10528 | 122.9004 | 123.0194 | 58.1497 | -123.0377 | 122.9187 | 122.8592 | 58.2001 | -123.1064
159.8438 | 123.1888 | -58.1726 | 64.7369 | 0.30496 | -0.029656 | 0.094854 | 0.021635 | 0.053649 | 0.0011837 | 0.00031381 | 0.092591 | -0.007393 | 0.053432 | 0.070606 | 0.0086079 | -0.0052251 | 64.8376 | -58.1177 | -0.004578 | -58.3878 | 64.7415 | -58.2047 | -58.2275 | -58.0719 | 0.036621 | -58.4427 | 64.7964 | 64.6774 | -58.2001 | -58.2825 | -0.032044 | -0.054932 | 0.004578 | 0.054931 | -0.21515 | -0.16022 | 0.10071 | -0.027466 | -0.10986 | 0.05951 | 0.10071 | -0.27008 | -0.16022 | -0.059509 | 122.9141 | 123.0103 | 58.168 | -122.9645 | 122.9691 | 122.85 | 58.2092 | -123.0194
160.8438 | 123.2346 | -58.1497 | 64.7644 | 0.25918 | -0.0082939 | 0.089513 | 0.0066808 | 0.067534 | -0.0041573 | -0.0018222 | -0.71613 | -0.013802 | 0.054501 | 0.047107 | 6.2882e-05 | -0.0073621 | 64.8422 | -57.9071 | 0.17395 | -58.3237 | 64.7461 | -58.1772 | -58.2184 | -58.1039 | 0.027466 | -58.4564 | 64.769 | 64.682 | -58.2047 | -58.3008 | -0.027466 | -0.068665 | -0.01831 | 0.24262 | -0.17395 | -0.10529 | 0.07782 | -0.054932 | -0.15106 | 0.004578 | 0.045776 | -0.3067 | -0.15564 | -0.082397 | 122.8958 | 122.9919 | 58.3237 | -122.9828 | 122.9187 | 122.8317 | 58.1772 | -123.0652
161.8438 | 123.2483 | -58.1909 | 64.7736 | 0.16763 | -0.022179 | 0.070287 | 0.0098848 | 0.055785 | -0.0084293 | -0.011435 | 0.12311 | -0.017006 | 0.065182 | 0.060993 | 6.2882e-05 | -0.0073621 | 64.8376 | -58.1085 | -0.018311 | -58.3832 | 64.7507 | -58.2047 | -58.223 | -58.0582 | 0.07782 | -58.4152 | 64.7873 | 64.6545 | -58.1909 | -58.2962 | -0.013733 | -0.032043 | -0.022889 | 0.082397 | -0.19226 | -0.16022 | 0.064086 | 0 | -0.10529 | 0.013732 | 0.13275 | -0.2243 | -0.11902 | -0.11902 | 122.9416 | 123.0286 | 58.1726 | -122.9965 | 122.9782 | 122.8455 | 58.2687 | -123.0698
162.8438 | 123.2117 | -58.1497 | 64.7415 | 0.18289 | -0.0072259 | 0.068151 | -0.013613 | 0.058989 | -0.01377 | 0.0024508 | 0.077332 | -0.006325 | 0.042751 | 0.058857 | -0.0063461 | -0.0073621 | 64.8331 | -58.1131 | -0.027466 | -58.374 | 64.7598 | -58.2092 | -58.2184 | -58.0856 | 0.068665 | -58.429 | 64.7919 | 64.6545 | -58.2138 | -58.2962 | -0.05951 | -0.068665 | 0.018311 | 0.036621 | -0.2243 | -0.15564 | 0.091553 | -0.064087 | -0.14649 | 0.050354 | 0.064087 | -0.27924 | -0.13275 | -0.086975 | 122.9095 | 122.9828 | 58.1223 | -122.9599 | 122.9416 | 122.8043 | 58.2184 | -123.0377
163.8438 | 123.2895 | -58.1543 | 64.7461 | -0.045996 | -0.020043 | 0.0799 | -0.0072042 | 0.071807 | 0.0043877 | -0.0050262 | -0.16681 | -0.015938 | 0.021389 | 0.047107 | 0.016085 | -0.019111 | 64.9338 | -57.9849 | 0.10071 | -58.3282 | 64.7598 | -58.1726 | -58.2047 | -58.168 | 0.10529 | -58.374 | 64.7552 | 64.6317 | -58.168 | -58.2779 | -0.01831 | -0.050354 | 0.013733 | 0.16937 | -0.17395 | -0.1236 | 0.18768 | -0.013733 | -0.1236 | 0.009155 | -0.013733 | -0.21973 | -0.09613 | -0.11444 | 122.9141 | 123.0881 | 58.255 | -122.9507 | 122.9095 | 122.7859 | 58.2596 | -123.024
164.8438 | 123.3078 | -58.1726 | 64.769 | 0.33547 | 0.00025114 | 0.072424 | 0.0034768 | 0.061125 | 0.0033197 | -0.0039582 | 0.22992 | -0.009529 | 0.045956 | 0.062061 | 0.0032669 | 0.0054559 | 64.8422 | -58.1085 | -0.045776 | -58.4106 | 64.7324 | -58.223 | -58.2321 | -58.0811 | 0.032043 | -58.4335 | 64.7781 | 64.6683 | -58.2184 | -58.3054 | -0.050354 | -0.05951 | -0.036621 | 0.064086 | -0.23804 | -0.17853 | 0.073242 | -0.045777 | -0.13275 | 0.009155 | 0.091552 | -0.26093 | -0.12817 | -0.10071 | 122.905 | 123.0148 | 58.1268 | -123.0011 | 122.9507 | 122.8409 | 58.2047 | -123.0743
165.8438 | 123.2666 | -58.1635 | 64.7736 | 0.36599 | -0.022179 | 0.07456 | 0.00027184 | 0.06967 | 0.0075917 | 0.0056548 | 0.32147 | -0.013802 | 0.058773 | 0.05138 | 0.0011309 | -0.0084301 | 64.8468 | -58.1314 | -0.036621 | -58.4106 | 64.7369 | -58.2001 | -58.2275 | -58.0948 | 0.045776 | -58.4427 | 64.7644 | 64.6545 | -58.1863 | -58.3282 | -0.036621 | -0.064087 | -0.036622 | 0.032043 | -0.24719 | -0.18311 | 0.073242 | -0.022888 | -0.16479 | -0.009156 | 0.068664 | -0.27924 | -0.11444 | -0.11902 | 122.9004 | 123.0103 | 58.1268 | -123.0011 | 122.9279 | 122.818 | 58.2092 | -123.1018
166.8438 | 123.1979 | -58.1772 | 64.7827 | 0.42703 | -0.02752 | 0.084173 | 0.0013408 | 0.048308 | -0.010566 | 0.0056548 | 0.24518 | -0.010597 | 0.051296 | 0.065265 | -0.0010051 | 0.0054559 | 64.8239 | -58.1177 | -0.027466 | -58.3969 | 64.7369 | -58.1955 | -58.2413 | -58.0811 | 0.041199 | -58.4518 | 64.7919 | 64.6637 | -58.1909 | -58.3237 | -0.018311 | -0.064087 | -0.045777 | 0.059509 | -0.21973 | -0.15564 | 0.041199 | -0.013733 | -0.14648 | 0.009155 | 0.09613 | -0.27466 | -0.12817 | -0.11902 | 122.9141 | 123.0011 | 58.1497 | -123.024 | 122.9691 | 122.8409 | 58.2184 | -123.1064
167.8438 | 123.2025 | -58.1726 | 64.7552 | 0.39651 | -0.022179 | 0.066015 | -0.014681 | 0.070738 | 0.0097277 | -0.0060942 | 0.22992 | -0.01487 | 0.055569 | 0.05672 | 0.0086079 | 0.0054559 | 64.8468 | -58.1314 | -0.022888 | -58.4015 | 64.7507 | -58.1909 | -58.255 | -58.0948 | 0.045776 | -58.4335 | 64.7873 | 64.682 | -58.1818 | -58.3054 | -0.018311 | -0.082398 | -0.004578 | 0.041198 | -0.22888 | -0.14648 | 0.091553 | -0.009156 | -0.13275 | 0.032043 | 0.077819 | -0.26093 | -0.12817 | -0.073242 | 122.9233 | 123.0194 | 58.1497 | -123.0103 | 122.9599 | 122.8546 | 58.2184 | -123.0606
168.8438 | 123.2208 | -58.168 | 64.7552 | 0.44228 | -0.018975 | 0.061742 | -0.00079616 | 0.063262 | 0.00011475 | 0.0035188 | 0.30621 | -0.009529 | 0.045956 | 0.054584 | 6.2882e-05 | 0.00011494 | 64.8422 | -58.1039 | -0.036621 | -58.3923 | 64.7278 | -58.2047 | -58.2413 | -58.0856 | 0.027466 | -58.4381 | 64.7736 | 64.6683 | -58.1818 | -58.3099 | -0.036621 | -0.073242 | -0.027466 | 0.064087 | -0.2243 | -0.15106 | 0.086975 | -0.013733 | -0.14191 | 0.018311 | 0.082398 | -0.27008 | -0.12817 | -0.086975 | 122.8958 | 123.0103 | 58.1314 | -122.9965 | 122.9416 | 122.8363 | 58.1955 | -123.0652
169.8438 | 123.2437 | -58.1863 | 64.7644 | -2.8231 | 0.00025114 | 0.077764 | -0.010409 | 0.065398 | -0.0084293 | 0.0035188 | 0.077332 | -0.021279 | 0.052364 | 0.055652 | -0.0042101 | -0.0073621 | 64.8285 | -58.1589 | -0.022888 | -58.3786 | 64.7369 | -58.2047 | -58.2275 | -58.0719 | 0.059509 | -58.4381 | 64.7781 | 64.6637 | -58.1955 | -58.2779 | -0.018311 | -0.041199 | -0.027466 | 0.027465 | -0.19226 | -0.15106 | 0.064087 | -0.009156 | -0.091553 | 0.013733 | 0.11444 | -0.25177 | -0.16022 | -0.10071 | 122.9233 | 123.0148 | 58.1635 | -122.9919 | 122.9645 | 122.85 | 58.2458 | -123.0423
170.8438 | 123.1842 | -58.1451 | 64.7552 | 0.18289 | -0.011498 | 0.0799 | -0.0072042 | 0.060057 | -0.0084293 | -0.0060942 | 0.15363 | -0.011666 | 0.04916 | 0.064197 | -0.0020731 | 0.011864 | 64.8285 | -58.1314 | -0.027466 | -58.4061 | 64.7232 | -58.1955 | -58.2275 | -58.0765 | 0.054932 | -58.4244 | 64.769 | 64.6683 | -58.1955 | -58.2779 | -0.050354 | -0.082397 | -0.032043 | 0.013733 | -0.26093 | -0.17853 | 0.073242 | -0.050354 | -0.13275 | 0.013733 | 0.068665 | -0.27923 | -0.14648 | -0.086975 | 122.8683 | 122.9736 | 58.1177 | -122.9828 | 122.9141 | 122.8134 | 58.2001 | -123.0331
171.8438 | 123.2208 | -58.1726 | 64.7598 | 0.16763 | -0.037133 | 0.086309 | -0.0018642 | 0.05258 | -0.0094983 | -0.0050262 | 0.35199 | -0.017006 | 0.052364 | 0.062061 | 6.2882e-05 | -0.0020211 | 64.7461 | -58.1085 | -0.022888 | -58.4152 | 64.7644 | -58.1955 | -58.2413 | -58.1039 | 0.054932 | -58.4335 | 64.7964 | 64.6774 | -58.1726 | -58.2779 | -0.022889 | -0.068665 | 0.004577 | 0.064086 | -0.24262 | -0.17395 | -0.013733 | 0 | -0.10529 | 0.036621 | 0.068664 | -0.26093 | -0.15564 | -0.082398 | 122.937 | 122.9187 | 58.1497 | -123.0011 | 122.9691 | 122.85 | 58.2275 | -123.0377
172.8438 | 123.1979 | -58.1726 | 64.769 | 0.2897 | -0.0061569 | 0.069219 | -0.00079616 | 0.058989 | 0.0022517 | -0.0092992 | 0.77924 | -0.003121 | 0.052364 | 0.038562 | -0.0031411 | -0.012702 | 64.8422 | -58.1268 | -0.013733 | -58.2687 | 64.7781 | -58.1772 | -58.2138 | -58.1039 | 0.018311 | -58.461 | 64.7827 | 64.6637 | -58.2092 | -58.3099 | -0.004578 | -0.041199 | 0.009155 | 0.045776 | -0.096131 | -0.054932 | 0.073242 | -0.036622 | -0.13733 | 0.013733 | 0.068664 | -0.28839 | -0.15106 | -0.10529 | 122.9507 | 123.0148 | 58.1589 | -122.9828 | 122.9553 | 122.8363 | 58.1909 | -123.0789
173.8438 | 123.2162 | -58.1772 | 64.7415 | 0.30496 | -0.00081686 | 0.07456 | 0.0077488 | 0.062194 | -0.0041573 | 0.0099268 | 1.5574 | -0.006325 | 0.041683 | 0.046039 | 0.0043349 | 0.0011829 | 64.8514 | -58.1039 | -0.009155 | -58.3832 | 64.7369 | -58.223 | -58.223 | -58.0856 | -0.004578 | -58.4381 | 64.7781 | 64.6683 | -58.2092 | -58.3008 | -0.045776 | -0.045776 | -0.004578 | 0.073242 | -0.20599 | -0.16022 | 0.10986 | -0.032044 | -0.1236 | 0.036621 | 0.091553 | -0.26093 | -0.13733 | -0.073242 | 122.9141 | 123.0286 | 58.168 | -122.9645 | 122.9553 | 122.8455 | 58.1726 | -123.0423
174.8438 | 123.2254 | -58.1772 | 64.7598 | 0.4728 | -0.026452 | 0.069219 | -0.0029322 | 0.063262 | 0.0086597 | -0.00075419 | 0.38251 | -0.009529 | 0.036343 | 0.059925 | 0.0075399 | -0.0073621 | 64.856 | -58.0719 | -0.018311 | -58.3878 | 64.7232 | -58.2001 | -58.2367 | -58.0765 | 0.032043 | -58.4335 | 64.7736 | 64.6317 | -58.2047 | -58.3054 | -0.022888 | -0.059509 | -0.036621 | 0.10529 | -0.21057 | -0.15106 | 0.09613 | -0.027466 | -0.12817 | 0.013733 | 0.10071 | -0.25635 | -0.12817 | -0.12817 | 122.9004 | 123.0331 | 58.1589 | -122.9965 | 122.9507 | 122.8088 | 58.2092 | -123.0652
175.8438 | 123.1796 | -58.168 | 64.7644 | 0.35073 | -0.031792 | 0.076696 | 0.0056128 | 0.06967 | -0.0052253 | -0.0082312 | 0.16888 | -0.009529 | 0.055569 | 0.043903 | 6.2882e-05 | -0.01377 | 64.8422 | -58.1223 | -0.027466 | -58.3969 | 64.7507 | -58.1909 | -58.2184 | -58.0078 | 0.13275 | -58.4656 | 64.7736 | 64.6957 | -58.168 | -58.2962 | -0.022888 | -0.050354 | -0.013733 | 0.045777 | -0.22888 | -0.17853 | 0.07782 | 0 | -0.12817 | 0.009156 | 0.16022 | -0.29755 | -0.16937 | -0.068664 | 122.9187 | 123.0103 | 58.1406 | -122.9828 | 122.9416 | 122.8638 | 58.3008 | -123.0606
176.8438 | 123.23 | -58.1726 | 64.7781 | 0.35073 | -0.0050889 | 0.064947 | -0.014681 | 0.065398 | 0.0086597 | -0.00075419 | 0.092591 | -0.012734 | 0.054501 | 0.055652 | -0.0042101 | -0.00095306 | 64.8422 | -58.1131 | -0.018311 | -58.3603 | 64.7598 | -58.2047 | -58.2367 | -58.0719 | 0.054932 | -58.4244 | 64.7919 | 64.6729 | -58.2001 | -58.3099 | -0.032044 | -0.064087 | -0.01831 | 0.059509 | -0.18768 | -0.1236 | 0.064087 | -0.027466 | -0.13733 | 0.013733 | 0.10071 | -0.25177 | -0.11444 | -0.10528 | 122.9324 | 123.0148 | 58.1543 | -123.0148 | 122.9645 | 122.8455 | 58.2275 | -123.0881
177.8438 | 123.2346 | -58.1955 | 64.7598 | 0.22866 | -0.02752 | 0.067083 | -0.00079616 | 0.058989 | -0.0052253 | 0.00031381 | 0.15363 | -0.013802 | 0.042751 | 0.052448 | 0.0043349 | 0.00011494 | 64.8056 | -58.1406 | -0.041199 | -58.3969 | 64.7232 | -58.2184 | -58.2413 | -58.0765 | 0.045776 | -58.4198 | 64.7736 | 64.6637 | -58.2047 | -58.3054 | -0.022888 | -0.045776 | -0.036621 | 0.054932 | -0.20142 | -0.15564 | 0.045776 | -0.009155 | -0.10986 | 0.013733 | 0.11902 | -0.2243 | -0.11444 | -0.096131 | 122.9187 | 123.0011 | 58.1543 | -123.0011 | 122.9691 | 122.8592 | 58.2413 | -123.0652
178.8438 | 123.1796 | -58.168 | 64.7369 | 0.15237 | -0.0082939 | 0.064947 | -0.0072042 | 0.055785 | -0.012702 | -0.016776 | 0.18414 | -0.012734 | 0.056637 | 0.041767 | 0.0032669 | -0.012702 | 64.8468 | -58.1085 | -0.004578 | -58.4152 | 64.7507 | -58.2321 | -58.2367 | -58.0811 | 0.068665 | -58.4473 | 64.7873 | 64.65 | -58.1955 | -58.3054 | -0.064087 | -0.068664 | 0.013733 | 0.059509 | -0.24719 | -0.17853 | 0.10986 | -0.027466 | -0.13733 | 0.050354 | 0.086975 | -0.27924 | -0.14191 | -0.086975 | 122.9187 | 123.0148 | 58.1635 | -122.9736 | 122.9553 | 122.818 | 58.2367 | -123.0423
179.8438 | 123.2162 | -58.1589 | 64.7644 | 0.33547 | -0.015771 | 0.072424 | -0.0082732 | 0.068602 | -0.0094983 | -0.013571 | 0.4588 | -0.003121 | 0.045956 | 0.067401 | 0.011812 | -0.0073621 | 64.8056 | -58.1131 | -0.022888 | -58.429 | 64.7415 | -58.2047 | -58.2413 | -58.0994 | 0.027466 | -58.4381 | 64.7919 | 64.682 | -58.1955 | -58.287 | -0.045776 | -0.082397 | -0.022888 | 0.045777 | -0.27008 | -0.18768 | 0.041199 | -0.036621 | -0.12817 | 0.027466 | 0.05951 | -0.27923 | -0.15106 | -0.082397 | 122.9004 | 122.9645 | 58.136 | -123.0057 | 122.9507 | 122.8409 | 58.1863 | -123.0515
180.8438 | 123.1888 | -58.1451 | 64.7324 | 0.45754 | -0.01043 | 0.071355 | -0.0061362 | 0.057921 | 0.0011837 | 0.0024508 | 0.33673 | -0.007393 | 0.051296 | 0.063129 | 0.0054039 | -0.0062931 | 64.856 | -58.0856 | -0.009155 | -58.3923 | 64.7461 | -58.2047 | -58.2413 | -58.0765 | 0.041199 | -58.429 | 64.7736 | 64.6225 | -58.2047 | -58.3099 | -0.059509 | -0.09613 | 0.013733 | 0.05951 | -0.24719 | -0.15106 | 0.1236 | -0.059509 | -0.16479 | 0.041199 | 0.068665 | -0.28381 | -0.11902 | -0.10986 | 122.8912 | 123.0011 | 58.136 | -122.9736 | 122.9187 | 122.7676 | 58.1863 | -123.0423
181.8438 | 123.2162 | -58.1635 | 64.7141 | 0.50332 | -0.016839 | 0.075628 | -0.00079616 | 0.057921 | 0.0054557 | -0.00075419 | 0.41303 | -0.004189 | 0.043819 | 0.057788 | 0.0096759 | -0.0062931 | 64.8651 | -58.0856 | -0.009155 | -58.3923 | 64.7278 | -58.2275 | -58.2687 | -58.049 | 0.036621 | -58.4198 | 64.7736 | 64.65 | -58.2092 | -58.287 | -0.064087 | -0.10529 | 0.013733 | 0.07782 | -0.22888 | -0.1236 | 0.15106 | -0.045777 | -0.1236 | 0.05951 | 0.11444 | -0.25635 | -0.13275 | -0.064087 | 122.8912 | 123.0286 | 58.1543 | -122.9828 | 122.937 | 122.8134 | 58.2001 | -123.0011
182.8438 | 123.1659 | -58.1863 | 64.8148 | -0.21384 | -0.0050889 | 0.071355 | 0.0045448 | 0.063262 | 0.015069 | -0.0050262 | -0.42621 | 0.008629 | 0.052364 | 0.066333 | 0.016085 | -0.018043 | 64.8193 | -58.1497 | -0.018311 | -58.3923 | 64.8285 | -58.223 | -58.2275 | -58.1406 | 0.064087 | -58.4793 | 64.8605 | 64.7232 | -58.2001 | -58.2962 | -0.036621 | -0.041199 | 0.013733 | 0.036621 | -0.20599 | -0.16479 | 0.004578 | -0.013733 | -0.10986 | 0.045777 | 0.045776 | -0.29297 | -0.1831 | -0.091552 | 123.0148 | 123.0057 | 58.168 | -123.0423 | 123.0469 | 122.9095 | 58.2504 | -123.111
183.8438 | 123.1705 | -58.1955 | 64.7644 | 0.42703 | -0.018975 | 0.066015 | -0.00079616 | 0.053649 | -0.020179 | -0.0092992 | 0.12311 | -0.004189 | 0.053432 | 0.065265 | 0.0064719 | -0.0094981 | 64.7964 | -58.1589 | -0.054932 | -58.4015 | 64.7278 | -58.2138 | -58.2504 | -58.0902 | 0.059509 | -58.429 | 64.7873 | 64.682 | -58.1955 | -58.3054 | -0.01831 | -0.054931 | -0.036621 | 0.036621 | -0.20599 | -0.15106 | 0.032044 | 0 | -0.10986 | 0.022888 | 0.10529 | -0.23346 | -0.1236 | -0.082397 | 122.9233 | 122.9919 | 58.1406 | -123.0148 | 122.9828 | 122.8775 | 58.255 | -123.0698
184.8438 | 123.2208 | -58.1451 | 64.7736 | 0.24392 | -0.012566 | 0.063879 | 0.0066808 | 0.056853 | -0.01377 | 0.0077908 | -0.01422 | -0.005257 | 0.04916 | 0.067401 | -0.0052781 | -0.00095306 | 64.9475 | -58.1589 | 0.004578 | -58.3969 | 64.7598 | -58.1909 | -58.2321 | -58.1131 | 0.045776 | -58.4564 | 64.7598 | 64.6545 | -58.2047 | -58.287 | -0.045776 | -0.086975 | -0.013733 | -0.013733 | -0.25177 | -0.16479 | 0.17395 | -0.059509 | -0.14191 | -0.013733 | 0.032044 | -0.31128 | -0.16937 | -0.11902 | 122.905 | 123.0927 | 58.1497 | -123.0057 | 122.905 | 122.7997 | 58.1909 | -123.0606
185.8438 | 123.1934 | -58.1863 | 64.7278 | 0.45754 | -0.0061569 | 0.062811 | -0.0050682 | 0.067534 | -0.0084293 | -0.013571 | -1.9673 | -0.006325 | 0.044888 | 0.055652 | 0.0011309 | 0.0011829 | 64.8468 | -58.1268 | -0.041199 | -58.4061 | 64.7507 | -58.2001 | -58.2458 | -58.1131 | 0.036621 | -58.4473 | 64.769 | 64.6866 | -58.1772 | -58.2962 | -0.013733 | -0.05951 | 0.022888 | 0.059509 | -0.21973 | -0.16022 | 0.11902 | 0.009155 | -0.10986 | 0.041199 | 0.073242 | -0.26093 | -0.15106 | -0.041199 | 122.937 | 123.0331 | 58.1451 | -122.9736 | 122.9553 | 122.8729 | 58.223 | -123.024
186.8438 | 123.2071 | -58.1406 | 64.7644 | 0.38125 | -0.011498 | 0.080969 | -0.0082732 | 0.060057 | 0.0022517 | -0.0092992 | 0.2757 | -0.021279 | 0.042751 | 0.064197 | -0.0010051 | -0.00095306 | 64.8651 | -58.1131 | -0.032043 | -58.4015 | 64.7324 | -58.2092 | -58.223 | -58.0856 | 0.041199 | -58.4518 | 64.7598 | 64.7003 | -58.1726 | -58.2779 | -0.068665 | -0.082397 | -0.032043 | 0.027466 | -0.26093 | -0.17853 | 0.10071 | -0.032043 | -0.13733 | -0.004577 | 0.054932 | -0.31128 | -0.17395 | -0.064087 | 122.8729 | 123.0057 | 58.1085 | -122.9874 | 122.9004 | 122.8409 | 58.1818 | -123.0423
187.8438 | 123.1338 | -58.1955 | 64.8102 | -0.32065 | -0.0050889 | 0.075628 | 0.021635 | 0.04724 | 0.012933 | 0.0013818 | -0.41095 | -0.007393 | 0.050228 | 0.041767 | 0.0043349 | -0.018043 | 64.8285 | -58.1772 | -0.027466 | -58.3969 | 64.8193 | -58.2321 | -58.2413 | -58.1223 | 0.07782 | -58.4885 | 64.8605 | 64.7141 | -58.2001 | -58.3237 | -0.036621 | -0.045776 | 0.009155 | 0.018311 | -0.20142 | -0.15564 | 0.01831 | -0.004577 | -0.12817 | 0.050354 | 0.073243 | -0.29297 | -0.16479 | -0.096131 | 123.0148 | 123.024 | 58.168 | -123.0515 | 123.056 | 122.9095 | 58.2733 | -123.1338
188.8438 | 123.2574 | -58.1726 | 64.7415 | 0.50332 | -0.01043 | 0.059606 | -0.016817 | 0.057921 | 0.0054557 | -0.016776 | 0.36725 | -0.007393 | 0.048092 | 0.065265 | 0.0021989 | 0.00011494 | 64.8743 | -58.0582 | 0.009155 | -58.374 | 64.7186 | -58.168 | -58.2413 | -58.0673 | 0.054932 | -58.4106 | 64.7324 | 64.6271 | -58.2001 | -58.3282 | 0.004577 | -0.068665 | -0.022888 | 0.11444 | -0.20142 | -0.13275 | 0.13275 | -0.027466 | -0.15564 | -0.009155 | 0.10529 | -0.23804 | -0.082398 | -0.11444 | 122.8912 | 123.0469 | 58.1818 | -122.9828 | 122.905 | 122.7997 | 58.2275 | -123.0698
189.8438 | 123.2025 | -58.1543 | 64.7415 | 0.4728 | -0.0061569 | 0.0799 | -0.0082732 | 0.049376 | -0.0041573 | 0.0035188 | 0.41303 | -0.011666 | 0.058773 | 0.055652 | 0.0011309 | 0.0011829 | 64.8514 | -58.0719 | 0 | -58.3878 | 64.7278 | -58.2184 | -58.2458 | -58.0627 | 0.064087 | -58.4198 | 64.7415 | 64.6591 | -58.2047 | -58.3008 | -0.064087 | -0.091553 | -0.013733 | 0.082398 | -0.23346 | -0.14191 | 0.10986 | -0.050354 | -0.14648 | 0 | 0.091553 | -0.2655 | -0.11902 | -0.082397 | 122.8821 | 123.0057 | 58.1543 | -122.9874 | 122.8958 | 122.8134 | 58.2184 | -123.0423
190.8438 | 123.2254 | -58.1726 | 64.7415 | 0.44228 | -0.031792 | 0.083105 | 0.0024088 | 0.057921 | -0.011634 | 0.0013818 | 0.33673 | -0.004189 | 0.065182 | 0.058857 | 0.0021989 | -0.0094981 | 64.8148 | -58.1085 | -0.022888 | -58.3969 | 64.7461 | -58.2275 | -58.2458 | -58.0902 | 0.050354 | -58.429 | 64.7964 | 64.6362 | -58.1863 | -58.3145 | -0.054932 | -0.073243 | 0.004578 | 0.064086 | -0.22431 | -0.15106 | 0.073242 | -0.013733 | -0.14191 | 0.054932 | 0.082397 | -0.25635 | -0.11444 | -0.10529 | 122.9187 | 122.9874 | 58.1497 | -122.9874 | 122.9691 | 122.8088 | 58.223 | -123.056
191.8438 | 123.2391 | -58.1589 | 64.7369 | 0.4728 | -0.015771 | 0.088445 | 0.0088168 | 0.062194 | -0.0052253 | -0.00075419 | 0.42828 | -0.009529 | 0.07159 | 0.060993 | 0.0054039 | -0.0041571 | 64.8468 | -58.0902 | -0.018311 | -58.4015 | 64.7095 | -58.2275 | -58.2367 | -58.0811 | 0.027466 | -58.4198 | 64.769 | 64.6591 | -58.2047 | -58.3191 | -0.068664 | -0.077819 | -0.027465 | 0.068665 | -0.24261 | -0.16479 | 0.10986 | -0.045776 | -0.16022 | 0.032044 | 0.07782 | -0.26093 | -0.10071 | -0.077819 | 122.8683 | 123.0057 | 58.1406 | -122.9736 | 122.9279 | 122.818 | 58.1863 | -123.056
192.8438 | 123.1247 | -58.1909 | 64.8102 | -0.3054 | -0.0040209 | 0.07456 | 0.012022 | 0.065398 | 0.012933 | -0.0018222 | 0.64191 | -0.008461 | 0.056637 | 0.057788 | 6.2882e-05 | -0.0094981 | 64.8285 | -58.1406 | -0.013733 | -58.4015 | 64.8056 | -58.2047 | -58.2413 | -58.1314 | 0.07782 | -58.5022 | 64.8514 | 64.7324 | -58.2047 | -58.3054 | -0.013733 | -0.050354 | -0.004578 | 0.050354 | -0.21057 | -0.16022 | 0.01831 | -0.013733 | -0.11444 | 0.041198 | 0.059509 | -0.31128 | -0.19684 | -0.07782 | 122.9965 | 123.0194 | 58.1772 | -123.0515 | 123.0423 | 122.9233 | 58.2687 | -123.1155
193.8438 | 123.2254 | -58.1772 | 64.7232 | 0.45754 | 0.0066601 | 0.05747 | -0.0082732 | 0.058989 | 0.0043877 | 0.0056548 | 0.39777 | -0.005257 | 0.052364 | 0.066333 | -0.0010051 | -0.012702 | 64.8605 | -58.0811 | -0.004578 | -58.3557 | 64.7003 | -58.2092 | -58.2413 | -58.0627 | 0.045776 | -58.4106 | 64.7598 | 64.6408 | -58.1955 | -58.342 | -0.032044 | -0.064087 | -0.022889 | 0.09613 | -0.17853 | -0.11444 | 0.13733 | -0.018311 | -0.16479 | 0.036621 | 0.11444 | -0.23346 | -0.068665 | -0.082398 | 122.8775 | 123.0377 | 58.1726 | -122.9645 | 122.937 | 122.818 | 58.223 | -123.0652
194.8438 | 123.2803 | -58.1589 | 64.7369 | 0.33547 | -0.0029529 | 0.060674 | 0.00027184 | 0.057921 | 0.022546 | -0.0039582 | 0.35199 | -0.011666 | 0.048092 | 0.060993 | 0.0054039 | -0.0020211 | 64.8514 | -58.0856 | -0.022888 | -58.3557 | 64.7278 | -58.2092 | -58.2367 | -58.0627 | 0.059509 | -58.4061 | 64.7324 | 64.6133 | -58.2504 | -58.3557 | -0.050354 | -0.077819 | -0.009155 | 0.073243 | -0.19684 | -0.11902 | 0.11444 | -0.091552 | -0.19684 | -0.004577 | 0.096131 | -0.24719 | -0.050354 | -0.1236 | 122.8867 | 123.0103 | 58.136 | -122.9736 | 122.8912 | 122.7722 | 58.2184 | -123.0927
195.8438 | 123.262 | -58.1635 | 64.7324 | 0.50332 | 0.013069 | 0.059606 | 0.0056128 | 0.070738 | 0.0097277 | 0.015268 | 0.046815 | -0.009529 | 0.052364 | 0.075946 | 0.0054039 | -0.0020211 | 64.8422 | -58.1314 | -0.054932 | -58.3969 | 64.7507 | -58.2321 | -58.2458 | -58.0582 | 0.036621 | -58.4198 | 64.7552 | 64.6637 | -58.2047 | -58.3008 | -0.068665 | -0.082398 | 0.01831 | 0.032043 | -0.23346 | -0.15106 | 0.10986 | -0.041199 | -0.13733 | 0.022888 | 0.10529 | -0.25635 | -0.11902 | -0.068665 | 122.9141 | 123.0057 | 58.1085 | -122.9782 | 122.9187 | 122.8271 | 58.2001 | -123.0331
196.8438 | 123.2849 | -58.1589 | 64.7049 | 0.64065 | -0.0029529 | 0.062811 | 0.0024088 | 0.06433 | 0.0022517 | 0.0099268 | 0.47406 | 0.00222 | 0.054501 | 0.059925 | 0.0054039 | -0.012702 | 64.8834 | -58.0948 | -0.022888 | -58.3603 | 64.7186 | -58.2001 | -58.2687 | -57.9483 | 0.068665 | -58.3832 | 64.7736 | 64.6683 | -58.1863 | -58.287 | -0.041198 | -0.10986 | 0.013733 | 0.064087 | -0.20142 | -0.091553 | 0.17853 | -0.027465 | -0.12817 | 0.068665 | 0.21057 | -0.2243 | -0.096131 | -0.036621 | 122.8775 | 123.0423 | 58.136 | -122.9736 | 122.9324 | 122.8271 | 58.2275 | -122.9919
197.8438 | 123.2254 | -58.1635 | 64.7781 | -0.21384 | -0.023247 | 0.072424 | 0.00027184 | 0.058989 | -0.016974 | -0.0092992 | -0.19733 | -0.009529 | 0.067318 | 0.062061 | -0.0042101 | -0.014838 | 64.8972 | -58.0353 | 0.091553 | -58.3237 | 64.7644 | -58.168 | -58.2184 | -58.0582 | 0.18768 | -58.3923 | 64.7827 | 64.7369 | -58.1589 | -58.2825 | -0.004578 | -0.054932 | -0.013733 | 0.12817 | -0.16022 | -0.10529 | 0.11902 | 0.004577 | -0.11902 | 0.004578 | 0.10529 | -0.22888 | -0.10986 | -0.041199 | 122.9279 | 123.0606 | 58.255 | -122.9965 | 122.9462 | 122.9004 | 58.3511 | -123.0606
198.8438 | 123.2437 | -58.168 | 64.7278 | 0.57961 | -0.0072259 | 0.048925 | 0.0088168 | 0.071807 | 0.0065237 | 0.0142 | 0.44354 | -0.012734 | 0.033138 | 0.060993 | 0.0054039 | -0.015907 | 64.8193 | -58.2733 | -0.018311 | -58.2733 | 64.6912 | -58.2001 | -58.223 | -58.0856 | 0.050354 | -58.4152 | 64.7461 | 64.6362 | -58.1909 | -58.3054 | -0.032043 | -0.054931 | -0.036621 | -0.10528 | -0.10528 | -0.050354 | 0.091553 | -0.022888 | -0.13733 | 0.018311 | 0.082398 | -0.24719 | -0.10986 | -0.091553 | 122.8592 | 122.9874 | 58.1497 | -122.9507 | 122.9141 | 122.8043 | 58.2184 | -123.0331
199.8438 | 123.262 | -58.1314 | 64.7369 | 1.1594 | 0.016273 | 0.054266 | -0.0040002 | 0.062194 | 0.0086597 | 0.0067228 | 0.33673 | -0.005257 | 0.059841 | 0.062061 | 0.0086079 | -0.0052251 | 64.8697 | -58.0994 | -0.027466 | -58.374 | 64.7461 | -58.2092 | -58.2413 | -58.0078 | -0.25177 | -58.4061 | 64.7141 | 64.6179 | -58.1955 | -58.2916 | -0.07782 | -0.10986 | 0.009156 | 0.032044 | -0.24261 | -0.13275 | 0.13275 | -0.064087 | -0.16022 | -0.022888 | 0.1236 | -0.27466 | -0.11444 | -0.11902 | 122.8775 | 123.0011 | 58.1039 | -122.9782 | 122.8455 | 122.7493 | 57.8796 | -123.0286
200.8438 | 123.2758 | -58.1863 | 64.7324 | 0.51858 | 0.0098641 | 0.068151 | -0.0040002 | 0.083556 | 0.016137 | 0.0035188 | 0.91657 | -0.005257 | 0.054501 | 0.065265 | 0.01288 | -0.0030891 | 64.8468 | -58.1406 | -0.054932 | -58.3923 | 64.7278 | -58.2138 | -58.2458 | -58.0719 | 0.036621 | -58.4152 | 64.7507 | 64.6545 | -58.223 | -58.3054 | -0.027466 | -0.05951 | -0.004578 | 0.045776 | -0.20599 | -0.14648 | 0.11444 | -0.036621 | -0.11902 | 0.01831 | 0.11444 | -0.22888 | -0.10986 | -0.07782 | 122.9141 | 123.0331 | 58.1314 | -122.9782 | 122.937 | 122.8409 | 58.223 | -123.0377
201.8438 | 123.1567 | -58.2321 | 64.7507 | 0.42703 | -0.0061569 | 0.064947 | 0.012022 | 0.06433 | 0.010797 | -0.0071622 | 0.1994 | -0.005257 | 0.057705 | 0.062061 | 0.010744 | -0.0052251 | 64.7873 | -58.2138 | -0.1236 | -58.4381 | 64.801 | -58.255 | -58.2779 | -58.1406 | -0.068665 | -58.5022 | 64.8468 | 64.7095 | -58.223 | -58.3328 | -0.022888 | -0.045776 | 0.050354 | 0.018311 | -0.20599 | -0.16022 | 0.036621 | 0.009156 | -0.10071 | 0.096131 | 0.091553 | -0.27008 | -0.16937 | -0.041198 | 123.0331 | 123.0194 | 58.1085 | -123.0286 | 123.0789 | 122.9416 | 58.1635 | -123.0835
202.8438 | 123.2162 | -58.1635 | 64.7781 | 0.16763 | -0.038201 | 0.071355 | -0.0040002 | 0.056853 | -0.029792 | -0.00075419 | 0.1994 | -0.007393 | 0.052364 | 0.054584 | 0.0043349 | 0.0043879 | 64.8148 | -58.1039 | -0.013733 | -58.3786 | 64.7507 | -58.1909 | -58.2275 | -58.0902 | 0.07782 | -58.4061 | 64.8056 | 64.6912 | -58.2092 | -58.3054 | -0.027466 | -0.064087 | -0.027466 | 0.059509 | -0.21515 | -0.15106 | 0.036621 | -0.045777 | -0.14191 | 0.027466 | 0.073242 | -0.24262 | -0.10071 | -0.086975 | 122.9141 | 122.9782 | 58.1497 | -123.0057 | 122.9691 | 122.8546 | 58.2413 | -123.0835
203.8438 | 123.1522 | -58.2001 | 64.7827 | 0.35073 | 0.032295 | 0.064947 | 0.01309 | 0.062194 | 0.015069 | 0.0045868 | 0.29095 | 8.4049e-05 | 0.052364 | 0.062061 | 6.2882e-05 | -0.010566 | 64.8102 | -58.2138 | -0.12817 | -58.4518 | 64.7827 | -58.2367 | -58.2733 | -58.1406 | -0.054932 | -58.5114 | 64.7873 | 64.6866 | -58.2138 | -58.3374 | -0.036621 | -0.073242 | 0 | -0.013733 | -0.25177 | -0.17853 | 0.027466 | -0.013733 | -0.13733 | 0.004577 | 0.059509 | -0.31128 | -0.17395 | -0.096131 | 122.9828 | 123.0103 | 58.0719 | -123.056 | 122.9874 | 122.8867 | 58.1451 | -123.1201
204.8438 | 123.1979 | -58.1772 | 64.7415 | 0.57961 | 0.0045241 | 0.056402 | 0.017362 | 0.075011 | 0.0097277 | 0.0045868 | 0.38251 | -0.002053 | 0.065182 | 0.059925 | 0.0086079 | 0.0065239 | 64.8056 | -58.1909 | -0.10529 | -58.429 | 64.7736 | -58.2596 | -58.2504 | -58.1268 | -0.036621 | -58.4564 | 64.7827 | 64.682 | -58.2184 | -58.3191 | -0.082398 | -0.073242 | 0.032044 | -0.013733 | -0.25177 | -0.17853 | 0.064087 | -0.041199 | -0.14191 | 0.041199 | 0.050354 | -0.27924 | -0.13733 | -0.059509 | 122.9507 | 122.9828 | 58.0719 | -122.9919 | 122.9599 | 122.8592 | 58.1406 | -123.0606
205.8438 | 123.1613 | -58.1955 | 64.7873 | 0.36599 | 0.019477 | 0.063879 | 0.012022 | 0.055785 | 0.0097277 | 0.0035188 | 0.33673 | -0.009529 | 0.054501 | 0.054584 | 0.0054039 | -0.0041571 | 64.7964 | -58.223 | -0.11902 | -58.4335 | 64.7644 | -58.2275 | -58.2596 | -58.1406 | -0.045776 | -58.4976 | 64.7781 | 64.7186 | -58.2413 | -58.342 | -0.032043 | -0.064087 | -0.022888 | -0.027465 | -0.23804 | -0.17395 | 0.009156 | -0.045776 | -0.14648 | -0.009155 | 0.054932 | -0.30212 | -0.15564 | -0.068664 | 122.9599 | 122.9919 | 58.0765 | -123.0469 | 122.9736 | 122.9141 | 58.1497 | -123.1293
206.8438 | 123.1293 | -58.2184 | 64.7919 | 0.83901 | 0.012 | 0.067083 | -0.00079616 | 0.062194 | 0.015069 | 0.0024508 | 0.2757 | 0.010765 | 0.060909 | 0.057788 | 0.0086079 | -0.0020211 | 64.7781 | -58.2458 | -0.13275 | -58.4473 | 64.7873 | -58.2413 | -58.287 | -58.1635 | -0.054932 | -58.5159 | 64.801 | 64.7415 | -58.2413 | -58.3328 | -0.022888 | -0.068664 | -0.004578 | -0.027466 | -0.22888 | -0.16022 | -0.013733 | -0.022888 | -0.11444 | 0.009155 | 0.054932 | -0.29755 | -0.1831 | -0.050354 | 123.0057 | 122.9965 | 58.0856 | -123.0789 | 123.0194 | 122.9599 | 58.1635 | -123.1247
207.8438 | 123.1247 | -58.1955 | 64.7781 | 0.44228 | 0.017341 | 0.064947 | 0.0098848 | 0.065398 | 0.0086597 | -0.0050262 | 0.44354 | -0.003121 | 0.057705 | 0.063129 | 0.0032669 | -0.0062931 | 64.7598 | -58.4564 | -0.37994 | -58.4702 | 64.7141 | -58.2642 | -58.2413 | -58.1726 | -0.082397 | -58.5388 | 64.7964 | 64.7324 | -58.2184 | -58.3145 | -0.068664 | -0.045776 | -0.064087 | -0.26093 | -0.27466 | -0.22888 | -0.01831 | -0.022888 | -0.11902 | 0.018311 | 0.022889 | -0.34332 | -0.2243 | -0.045776 | 122.9095 | 122.9553 | 57.8156 | -123.0194 | 122.9919 | 122.9279 | 58.1131 | -123.0927
208.8438 | 123.1201 | -58.1955 | 64.7873 | 0.12185 | 0.012 | 0.071355 | 0.0066808 | 0.072875 | 0.0033197 | -0.0039582 | -0.01422 | 0.00222 | 0.063046 | 0.03963 | 0.010744 | 0.0033199 | 64.8148 | -58.1772 | -0.045776 | -58.4015 | 64.7781 | -58.2184 | -58.2275 | -58.1589 | 0.018311 | -58.4976 | 64.8239 | 64.7415 | -58.2047 | -58.3237 | -0.022888 | -0.032043 | -0.009155 | 0.018311 | -0.20599 | -0.17395 | 0.027466 | -0.009155 | -0.12817 | 0.036622 | 0.036621 | -0.30212 | -0.17395 | -0.045776 | 122.9736 | 123.0103 | 58.1497 | -123.0148 | 123.0194 | 122.937 | 58.2138 | -123.111
209.8438 | 123.1522 | -58.2138 | 64.7964 | 0.045557 | 0.021614 | 0.073492 | 0.0034768 | 0.06433 | -0.00095325 | 0.00031381 | 0.046815 | 0.016105 | 0.061977 | 0.063129 | 0.0043349 | -0.0073621 | 64.8331 | -58.1314 | -0.027466 | -58.3878 | 64.7598 | -58.2001 | -58.255 | -58.136 | 0.041199 | -58.461 | 64.801 | 64.7369 | -58.2184 | -58.3145 | 0.013733 | -0.041199 | -0.036621 | 0.082397 | -0.17395 | -0.13275 | 0.036621 | -0.004578 | -0.10071 | 0.004577 | 0.07782 | -0.24719 | -0.14648 | -0.05951 | 122.9736 | 123.0469 | 58.1863 | -123.0515 | 123.0148 | 122.9507 | 58.255 | -123.111
210.8438 | 123.143 | -58.1818 | 64.7736 | 0.19814 | 0.0066601 | 0.061742 | 0.0034768 | 0.06433 | -0.0030893 | 0.0056548 | 0.046815 | 0.010765 | 0.052364 | 0.05138 | 0.0075399 | -0.0041571 | 64.8056 | -58.1726 | -0.050354 | -58.4106 | 64.7736 | -58.2458 | -58.2687 | -58.1772 | -0.004578 | -58.4793 | 64.7873 | 64.7461 | -58.2184 | -58.3511 | -0.064087 | -0.086975 | 0 | 0.009156 | -0.22888 | -0.14191 | 0.032043 | -0.036621 | -0.16937 | 0.013732 | 0.004578 | -0.29755 | -0.12817 | -0.027466 | 122.9553 | 122.9874 | 58.1314 | -123.0423 | 122.9691 | 122.9279 | 58.1772 | -123.1247
211.8438 | 123.1064 | -58.2184 | 64.7827 | 0.19814 | 0.010932 | 0.069219 | 0.0077488 | 0.056853 | -0.0062933 | 0.0067228 | 0.12311 | 0.001152 | 0.067318 | 0.058857 | -0.0010051 | -0.0030891 | 64.7827 | -58.1863 | -0.073242 | -58.4152 | 64.7644 | -58.2413 | -58.2733 | -58.2092 | -0.050354 | -58.5251 | 64.8148 | 64.7369 | -58.2138 | -58.3557 | -0.022888 | -0.054931 | -0.018311 | 0.032044 | -0.19684 | -0.14191 | 0 | 0.004578 | -0.13733 | 0.032043 | 0.009155 | -0.3067 | -0.16937 | -0.045777 | 122.9828 | 123.0011 | 58.1451 | -123.056 | 123.0331 | 122.9553 | 58.168 | -123.1384
212.8438 | 123.1201 | -58.2047 | 64.7919 | 0.30496 | 0.031227 | 0.068151 | -0.00079616 | 0.053649 | -0.0052253 | 0.0045868 | 0.046815 | -0.00098395 | 0.055569 | 0.071674 | 0.0021989 | -0.012702 | 64.801 | -58.1772 | -0.064087 | -58.4152 | 64.7781 | -58.2321 | -58.2596 | -58.168 | 0.004578 | -58.5159 | 64.8239 | 64.7415 | -58.2413 | -58.3237 | -0.027466 | -0.054932 | -0.013733 | 0.027466 | -0.21057 | -0.15564 | 0.009155 | -0.036621 | -0.11902 | 0.032044 | 0.036621 | -0.31128 | -0.19226 | -0.050354 | 122.9828 | 123.0057 | 58.1406 | -123.0515 | 123.0286 | 122.9462 | 58.2092 | -123.1155
213.8438 | 123.1613 | -58.2001 | 64.7736 | 0.15237 | 0.024818 | 0.062811 | 0.0066808 | 0.06433 | -0.0073613 | 0.0035188 | 0.12311 | 0.003288 | 0.077999 | 0.06847 | 0.0054039 | 0.0033199 | 64.8056 | -58.1497 | -0.036621 | -58.3878 | 64.7552 | -58.2184 | -58.2596 | -58.1451 | 0.018311 | -58.4747 | 64.8239 | 64.7232 | -58.2321 | -58.3511 | -0.018311 | -0.05951 | -0.018311 | 0.050354 | -0.18768 | -0.12817 | 0.032043 | -0.032044 | -0.15106 | 0.050354 | 0.054931 | -0.27466 | -0.1236 | -0.050354 | 122.9553 | 123.0057 | 58.1635 | -123.0331 | 123.024 | 122.9233 | 58.2184 | -123.1247
214.8438 | 123.1796 | -58.1863 | 64.7827 | -0.18333 | 0.026954 | 0.067083 | 0.0056128 | 0.070738 | 0.0075917 | 0.0088588 | 0.031556 | 0.005424 | 0.054501 | 0.048175 | 0.0021989 | -0.0094981 | 64.8605 | -58.1497 | -0.018311 | -58.3786 | 64.7644 | -58.2047 | -58.2321 | -58.1177 | 0.059509 | -58.461 | 64.801 | 64.7369 | -58.2092 | -58.3237 | -0.018311 | -0.045777 | -0.018311 | 0.036621 | -0.19226 | -0.14648 | 0.07782 | -0.022889 | -0.13733 | 0.01831 | 0.068664 | -0.27466 | -0.13733 | -0.045777 | 122.9507 | 123.0469 | 58.168 | -123.0148 | 122.9874 | 122.9233 | 58.2458 | -123.1064
215.8438 | 123.1659 | -58.1726 | 64.801 | -0.24436 | 0.0087961 | 0.069219 | -0.0072042 | 0.077147 | -0.0073613 | 0.0099268 | -0.2431 | 0.00222 | 0.04916 | 0.041767 | -0.0052781 | -0.018043 | 64.8331 | -58.1635 | 0.004578 | -58.3786 | 64.801 | -58.2138 | -58.2458 | -58.1223 | 0.07782 | -58.4656 | 64.8422 | 64.7461 | -58.2138 | -58.3054 | -0.041199 | -0.073243 | 0 | 0.009155 | -0.20599 | -0.13275 | 0.032044 | -0.041199 | -0.13275 | 0.041199 | 0.050354 | -0.29297 | -0.16022 | -0.054931 | 122.9736 | 123.0057 | 58.1772 | -123.0469 | 123.0148 | 122.9187 | 58.2504 | -123.1064
216.8438 | 123.1888 | -58.1909 | 64.8148 | -0.091772 | 0.012 | 0.069219 | 0.010954 | 0.060057 | 0.0033197 | 0.0045868 | -0.30414 | -0.006325 | 0.040615 | 0.058857 | 6.2882e-05 | 0.0054559 | 64.7964 | -58.1543 | -0.009155 | -58.3786 | 64.7964 | -58.2184 | -58.2458 | -58.1451 | 0.082397 | -58.4427 | 64.8056 | 64.7781 | -58.223 | -58.2962 | -0.027466 | -0.054932 | -0.01831 | 0.036621 | -0.18768 | -0.13275 | -0.01831 | -0.032043 | -0.10529 | -0.009155 | 0.045776 | -0.25177 | -0.14648 | -0.036621 | 122.9874 | 122.9874 | 58.1818 | -123.0606 | 122.9965 | 122.9691 | 58.2733 | -123.111
217.8438 | 123.1659 | -58.1818 | 64.7919 | 0.060816 | 0.0055921 | 0.041448 | 0.0056128 | 0.063262 | -0.0041573 | 0.0013818 | -0.075256 | -0.00098395 | 0.058773 | 0.065265 | 0.0021989 | -0.0030891 | 64.8285 | -58.1131 | -0.004578 | -58.3832 | 64.7781 | -58.2001 | -58.2458 | -58.1131 | 0.07782 | -58.4473 | 64.7964 | 64.7186 | -58.2138 | -58.3328 | -0.01831 | -0.064087 | -0.013733 | 0.068665 | -0.20142 | -0.13733 | 0.036621 | -0.032043 | -0.15106 | 0.004578 | 0.068665 | -0.2655 | -0.11444 | -0.073242 | 122.9599 | 123.0103 | 58.1772 | -123.0377 | 122.9782 | 122.9004 | 58.2596 | -123.1247
218.8438 | 123.1979 | -58.168 | 64.8056 | 0.060816 | 0.0023871 | 0.059606 | 0.015226 | 0.067534 | 0.0011837 | -0.0039582 | -0.15155 | 0.004356 | 0.055569 | 0.049243 | -0.0020731 | -0.0052251 | 64.8102 | -58.1223 | 0 | -58.3878 | 64.801 | -58.223 | -58.2596 | -58.2092 | 0.13733 | -58.4427 | 64.7964 | 64.7598 | -58.2184 | -58.3054 | -0.054931 | -0.091553 | -0.004578 | 0.045777 | -0.21973 | -0.12817 | 0.004578 | -0.050354 | -0.13733 | -0.009155 | -0.041199 | -0.27466 | -0.13733 | -0.045776 | 122.9691 | 122.9782 | 58.168 | -123.0652 | 122.9645 | 122.9279 | 58.3054 | -123.111
219.8438 | 123.1934 | -58.2001 | 64.7827 | -0.12229 | 0.013069 | 0.064947 | 0.0024088 | 0.068602 | 0.0022517 | 0.0056548 | -0.10577 | 0.010765 | 0.061977 | 0.065265 | 6.2882e-05 | -0.00095306 | 64.8285 | -58.1451 | 0.009155 | -58.3649 | 64.7873 | -58.2047 | -58.2504 | -58.1131 | 0.082397 | -58.4518 | 64.8102 | 64.7827 | -58.2321 | -58.287 | -0.004578 | -0.050354 | 0.004577 | 0.054931 | -0.16479 | -0.11444 | 0.045776 | -0.032044 | -0.086975 | 0.027466 | 0.086975 | -0.25177 | -0.16479 | 0 | 122.9874 | 123.0286 | 58.2092 | -123.0331 | 123.0103 | 122.9828 | 58.2825 | -123.0698
220.8438 | 123.143 | -58.1772 | 64.8056 | -0.2291 | 0.015205 | 0.067083 | -0.00079616 | 0.075011 | -0.01377 | -0.0060942 | -0.16681 | 0.00222 | 0.050228 | 0.05672 | 0.0032669 | 0.0043879 | 64.8056 | -58.1589 | -0.022888 | -58.3694 | 64.8239 | -58.2001 | -58.2367 | -58.1451 | 0.086975 | -58.4473 | 64.8468 | 64.7552 | -58.2184 | -58.3145 | -0.022888 | -0.059509 | 0.018311 | 0.01831 | -0.19226 | -0.13275 | 0 | -0.041199 | -0.13733 | 0.041199 | 0.032043 | -0.27008 | -0.13275 | -0.050354 | 123.0011 | 122.9828 | 58.1543 | -123.0423 | 123.024 | 122.9324 | 58.2642 | -123.1201
221.8438 | 123.1522 | -58.1955 | 64.8148 | -0.27488 | 0.0013191 | 0.075628 | 0.0045448 | 0.061125 | -0.0020213 | -0.0018222 | -0.19733 | -0.013802 | 0.070522 | 0.054584 | 0.0032669 | -0.0041571 | 64.7873 | -58.168 | -0.022888 | -58.3969 | 64.7964 | -58.2184 | -58.2458 | -58.1589 | 0.073242 | -58.461 | 64.8376 | 64.769 | -58.2138 | -58.3237 | -0.022888 | -0.050354 | -0.01831 | 0.027466 | -0.20142 | -0.15106 | -0.027466 | -0.01831 | -0.12817 | 0.022888 | 0.036621 | -0.2655 | -0.13733 | -0.045776 | 122.9919 | 122.9828 | 58.1726 | -123.0606 | 123.0331 | 122.9645 | 58.2687 | -123.1384
222.8438 | 123.1888 | -58.168 | 64.856 | -0.29014 | 0.0066601 | 0.077764 | 0.0077488 | 0.06433 | -0.018043 | -0.013571 | 0.046815 | -0.005257 | 0.053432 | 0.069538 | -0.0074141 | 0.0011829 | 64.801 | -58.1635 | 0.009155 | -58.4015 | 64.801 | -58.1909 | -58.2321 | -58.1497 | 0.068665 | -58.4518 | 64.8422 | 64.8056 | -58.2184 | -58.3328 | -0.022888 | -0.064087 | -0.054932 | 0.004578 | -0.23346 | -0.16937 | -0.054932 | -0.050354 | -0.16479 | -0.013733 | 0.018311 | -0.28381 | -0.11902 | -0.050354 | 122.9691 | 122.9691 | 58.1772 | -123.0881 | 123.0103 | 122.9736 | 58.2367 | -123.1888
223.8438 | 123.1201 | -58.1726 | 64.8193 | -0.015478 | -0.0029529 | 0.066015 | 0.014158 | 0.063262 | -0.012702 | -0.013571 | 0.7182 | -0.011666 | 0.058773 | 0.055652 | 6.2882e-05 | -0.0030891 | 64.7964 | -58.1635 | -0.022888 | -58.3969 | 64.7964 | -58.2092 | -58.2047 | -58.1589 | 0.050354 | -58.4747 | 64.8331 | 64.7919 | -58.1955 | -58.2916 | -0.036622 | -0.032044 | -0.022888 | 0.009155 | -0.22431 | -0.19226 | -0.022888 | -0.022889 | -0.11902 | 0.013733 | 0.013732 | -0.30212 | -0.1831 | -0.027466 | 122.9691 | 122.9691 | 58.1497 | -123.024 | 123.0057 | 122.9645 | 58.223 | -123.111
224.8438 | 123.111 | -58.1726 | 64.8102 | 0.2897 | -0.00081686 | 0.060674 | -0.0018642 | 0.062194 | -0.0052253 | -0.0028902 | -0.28888 | -0.01487 | 0.031002 | 0.041767 | 0.0021989 | -0.0073621 | 64.769 | -58.1772 | -0.018311 | -58.374 | 64.8056 | -58.1863 | -58.2321 | -58.136 | 0.045776 | -58.4702 | 64.8331 | 64.7736 | -58.2138 | -58.3145 | -0.013733 | -0.05951 | -0.004578 | -0.004578 | -0.20142 | -0.14191 | -0.041199 | -0.041199 | -0.14191 | 0.022888 | 0.036621 | -0.29755 | -0.15564 | -0.036621 | 122.9782 | 122.9416 | 58.1543 | -123.0423 | 123.0057 | 122.9462 | 58.2184 | -123.1247
225.8438 | 123.1476 | -58.1818 | 64.8056 | -1.1294 | -0.012566 | 0.070287 | 0.010954 | 0.058989 | -0.0073613 | -0.011435 | -0.2431 | -0.008461 | 0.076931 | 0.063129 | 0.0032669 | -0.0020211 | 64.7736 | -58.1543 | 0 | -58.3832 | 64.8056 | -58.2001 | -58.255 | -58.2138 | 0.059509 | -58.4839 | 64.8148 | 64.7415 | -58.223 | -58.3237 | -0.01831 | -0.073242 | 0 | 0.027466 | -0.20142 | -0.12817 | -0.032043 | -0.041198 | -0.14191 | 0.009155 | -0.032043 | -0.30212 | -0.16022 | -0.064087 | 122.9874 | 122.9553 | 58.1818 | -123.0606 | 122.9965 | 122.9233 | 58.2413 | -123.1293
226.8438 | 123.111 | -58.168 | 64.8193 | -0.21384 | -0.01043 | 0.0799 | 0.0056128 | 0.05258 | -0.016974 | -0.0092992 | -0.2431 | -0.010597 | 0.058773 | 0.06847 | -0.0063461 | -0.0094981 | 64.8239 | -58.0902 | 0.054932 | -58.3511 | 64.801 | -58.1955 | -58.223 | -58.1406 | 0.15106 | -58.461 | 64.8376 | 64.7644 | -58.1955 | -58.287 | -0.027466 | -0.054931 | -0.018311 | 0.07782 | -0.1831 | -0.12817 | 0.004578 | -0.027466 | -0.11902 | 0.01831 | 0.027466 | -0.29297 | -0.17395 | -0.054932 | 122.9691 | 122.9919 | 58.223 | -123.0423 | 123.0057 | 122.9324 | 58.3191 | -123.1064
227.8438 | 123.2025 | -58.1314 | 64.7873 | -0.24436 | -0.021111 | 0.07456 | -0.011477 | 0.063262 | -0.0073613 | -0.024252 | -0.19733 | -0.010597 | 0.052364 | 0.060993 | -0.0084821 | -0.0020211 | 64.8743 | -58.0536 | 0.082397 | -58.3328 | 64.7736 | -58.1772 | -58.2184 | -58.0902 | 0.14191 | -58.4061 | 64.8102 | 64.7369 | -58.1909 | -58.3008 | -0.045776 | -0.086975 | -0.013732 | 0.07782 | -0.20142 | -0.11444 | 0.086976 | -0.059509 | -0.16937 | 0.022889 | 0.041199 | -0.27466 | -0.10529 | -0.050354 | 122.905 | 123.0057 | 58.2138 | -123.0057 | 122.9416 | 122.8683 | 58.2733 | -123.0881
228.8438 | 123.2208 | -58.1223 | 64.8056 | -0.015478 | -0.011498 | 0.075628 | -0.0061362 | 0.066466 | -0.026587 | -0.021048 | -0.16681 | -0.007393 | 0.050228 | 0.054584 | -0.0020731 | -0.0020211 | 64.8605 | -58.0307 | 0.086975 | -58.3374 | 64.7415 | -58.1726 | -58.2092 | -58.0536 | 0.17853 | -58.3511 | 64.7781 | 64.7369 | -58.1589 | -58.2779 | -0.050354 | -0.086976 | -0.064087 | 0.091552 | -0.21515 | -0.12817 | 0.054932 | -0.036622 | -0.15564 | -0.027466 | 0.068664 | -0.22888 | -0.073242 | -0.068665 | 122.8638 | 122.9828 | 58.2092 | -123.0148 | 122.9004 | 122.8592 | 58.3008 | -123.0835
229.8438 | 123.262 | -58.1451 | 64.7827 | -0.015478 | -0.025384 | 0.0799 | 0.0077488 | 0.06967 | -0.018043 | -0.0039582 | 0.046815 | -0.019142 | 0.047024 | 0.067401 | -0.0020731 | -0.011634 | 64.8834 | -58.0719 | 0.064087 | -58.3466 | 64.769 | -58.1863 | -58.2092 | -58.0444 | 0.13733 | -58.3557 | 64.7781 | 64.7095 | -58.168 | -58.2733 | -0.041198 | -0.064087 | -0.013733 | 0.073243 | -0.20142 | -0.13733 | 0.10071 | -0.022888 | -0.12817 | -0.004578 | 0.10071 | -0.21057 | -0.082398 | -0.073242 | 122.9141 | 123.0286 | 58.2092 | -122.9919 | 122.9233 | 122.8546 | 58.2825 | -123.056
230.8438 | 123.2895 | -58.1314 | 64.801 | -0.045996 | -0.018975 | 0.062811 | 0.0024088 | 0.051512 | -0.01377 | -0.024252 | -0.01422 | -0.017006 | 0.041683 | 0.064197 | 6.2882e-05 | -0.015907 | 64.888 | -58.0307 | 0.059509 | -58.3328 | 64.7598 | -58.2001 | -58.223 | -58.0078 | 0.17853 | -58.3191 | 64.7964 | 64.7232 | -58.1589 | -58.2733 | -0.068664 | -0.091552 | -0.041198 | 0.10071 | -0.20142 | -0.10986 | 0.086975 | -0.027466 | -0.14191 | -0.004577 | 0.1236 | -0.18768 | -0.045777 | -0.077819 | 122.8912 | 123.0194 | 58.1909 | -123.024 | 122.9279 | 122.8546 | 58.3099 | -123.0743
231.8438 | 123.2346 | -58.136 | 64.7507 | -0.25962 | -0.022179 | 0.076696 | 0.00027184 | 0.055785 | -0.01377 | -0.013571 | -0.10577 | -0.006325 | 0.025661 | 0.058857 | 0.016085 | -0.0062931 | 64.9017 | -57.9941 | 0.11902 | -58.3099 | 64.7552 | -58.1635 | -58.2092 | -58.1726 | 0.082397 | -58.3649 | 64.7644 | 64.6591 | -58.1772 | -58.287 | -0.027466 | -0.073243 | 0.004578 | 0.14191 | -0.17395 | -0.10071 | 0.15106 | -0.041199 | -0.15106 | 0.013733 | -0.036621 | -0.22888 | -0.07782 | -0.091552 | 122.8912 | 123.0377 | 58.255 | -122.9599 | 122.9004 | 122.7951 | 58.2184 | -123.0377
232.8438 | 123.2758 | -58.1314 | 64.7873 | -0.061255 | -0.030724 | 0.068151 | -0.00079616 | 0.062194 | -0.0052253 | -0.017844 | 0.016297 | -0.006325 | 0.050228 | 0.042835 | -0.0095501 | -0.015907 | 64.8834 | -58.0399 | 0.050354 | -58.3374 | 64.769 | -58.2047 | -58.2275 | -58.0215 | 0.15106 | -58.3328 | 64.8102 | 64.6866 | -58.1589 | -58.2596 | -0.073242 | -0.09613 | -0.01831 | 0.091553 | -0.20599 | -0.10986 | 0.096131 | -0.027466 | -0.12817 | 0.022889 | 0.10986 | -0.20142 | -0.073242 | -0.10071 | 122.9004 | 123.0148 | 58.1818 | -123.0148 | 122.9416 | 122.818 | 58.2825 | -123.0469
233.8438 | 123.2346 | -58.1451 | 64.7507 | 0.015039 | -0.014702 | 0.073492 | -0.0018642 | 0.061125 | -0.020179 | -0.0060942 | 0.016297 | 0.003288 | 0.038479 | 0.05672 | 0.013948 | 0.00011494 | 64.856 | -58.0811 | 0.004578 | -58.3511 | 64.7552 | -58.2001 | -58.2184 | -58.0307 | 0.11902 | -58.3832 | 64.7827 | 64.7003 | -58.1772 | -58.3054 | -0.054931 | -0.073242 | 0.004578 | 0.064087 | -0.20599 | -0.13275 | 0.10529 | -0.032043 | -0.16022 | 0.032044 | 0.11444 | -0.23804 | -0.07782 | -0.050354 | 122.9004 | 123.0011 | 58.1497 | -122.9691 | 122.9279 | 122.8455 | 58.2642 | -123.056
234.8438 | 123.2529 | -58.1406 | 64.7598 | 0.15237 | -0.0093619 | 0.080969 | 0.0024088 | 0.054717 | -0.010566 | -0.017844 | 0.092591 | -0.006325 | 0.04916 | 0.049243 | -0.0031411 | -0.0052251 | 64.8239 | -58.0994 | -0.009155 | -58.374 | 64.7644 | -58.2047 | -58.2596 | -58.0719 | 0.082397 | -58.3969 | 64.7598 | 64.7003 | -58.2092 | -58.2825 | -0.064087 | -0.11902 | 0.004577 | 0.041199 | -0.23346 | -0.11444 | 0.064087 | -0.068665 | -0.14191 | 0 | 0.068665 | -0.25635 | -0.11444 | -0.05951 | 122.905 | 122.9645 | 58.1314 | -123.0194 | 122.9004 | 122.8409 | 58.223 | -123.0423
235.8438 | 123.2071 | -58.1543 | 64.7324 | -3.174 | -0.020043 | 0.070287 | 0.00027184 | 0.060057 | -0.0041573 | -0.016776 | 0.077332 | -0.007393 | 0.054501 | 0.05138 | -0.0010051 | -0.0062931 | 64.8102 | -58.1314 | -0.027466 | -58.3878 | 64.7324 | -58.2001 | -58.2596 | -58.0811 | 0.036621 | -58.429 | 64.7781 | 64.6774 | -58.2047 | -58.3054 | -0.045776 | -0.10529 | 0 | 0.022888 | -0.23346 | -0.12817 | 0.07782 | -0.050354 | -0.15106 | 0.045776 | 0.073242 | -0.27466 | -0.1236 | -0.054932 | 122.8867 | 122.9645 | 58.1268 | -122.9919 | 122.9324 | 122.8317 | 58.1909 | -123.0377
236.8438 | 123.2071 | -58.1772 | 64.7324 | 0.50332 | -0.020043 | 0.062811 | 0.0066808 | 0.055785 | -0.00095325 | -0.0071622 | 0.32147 | -0.018074 | 0.04916 | 0.067401 | -0.0010051 | -0.011634 | 64.8468 | -58.0902 | -0.018311 | -58.3878 | 64.7049 | -58.2138 | -58.2321 | -58.0673 | 0.013733 | -58.4335 | 64.7507 | 64.6683 | -58.2092 | -58.2962 | -0.036621 | -0.054932 | -0.027466 | 0.086975 | -0.21057 | -0.15564 | 0.11444 | -0.032044 | -0.11902 | 0.01831 | 0.10986 | -0.25635 | -0.13733 | -0.064087 | 122.8821 | 123.024 | 58.1589 | -122.9645 | 122.9279 | 122.8455 | 58.1909 | -123.0286
237.8438 | 123.2071 | -58.1863 | 64.7552 | 0.38125 | -0.011498 | 0.072424 | 0.0088168 | 0.057921 | -0.0052253 | -0.0050262 | 0.33673 | -0.003121 | 0.04916 | 0.062061 | 0.0021989 | -0.0084301 | 64.8285 | -58.0994 | -0.036621 | -58.3786 | 64.7232 | -58.2092 | -58.2413 | -58.0948 | -0.018311 | -58.4702 | 64.7736 | 64.6683 | -58.223 | -58.3054 | -0.022889 | -0.054932 | -0.032043 | 0.086975 | -0.19226 | -0.13733 | 0.073242 | -0.036621 | -0.11902 | 0.018311 | 0.091552 | -0.28381 | -0.16479 | -0.086975 | 122.9095 | 123.0148 | 58.1497 | -122.9965 | 122.9599 | 122.8546 | 58.168 | -123.0606
238.8438 | 123.2254 | -58.1543 | 64.7278 | 0.22866 | -0.016839 | 0.067083 | -0.0072042 | 0.070738 | -0.0030893 | -0.022116 | 0.22992 | -0.011666 | 0.056637 | 0.041767 | -0.0052781 | -0.00095306 | 64.8239 | -58.1177 | -0.032043 | -58.3969 | 64.7369 | -58.2092 | -58.2092 | -58.0811 | 0.11902 | -58.3511 | 64.8102 | 64.6957 | -58.1589 | -58.2825 | -0.054932 | -0.054932 | 0.009155 | 0.036621 | -0.24262 | -0.18768 | 0.096131 | -0.004578 | -0.12817 | 0.082398 | 0.073242 | -0.19684 | -0.068664 | -0.032043 | 122.8912 | 122.9782 | 58.1223 | -122.937 | 122.9645 | 122.85 | 58.2733 | -123.0103
239.8438 | 123.1888 | -58.1726 | 64.7644 | 0.4728 | -0.00081686 | 0.086309 | -0.00079616 | 0.053649 | -0.0062933 | 0.0035188 | 0.29095 | -0.005257 | 0.04916 | 0.058857 | 0.0075399 | -0.015907 | 64.8468 | -58.0994 | -0.027466 | -58.3969 | 64.7278 | -58.223 | -58.2642 | -58.0627 | 0.004578 | -58.461 | 64.7507 | 64.6774 | -58.223 | -58.2962 | -0.050354 | -0.091553 | -0.036621 | 0.073242 | -0.22431 | -0.13275 | 0.082398 | -0.050354 | -0.1236 | -0.013733 | 0.10986 | -0.28839 | -0.16479 | -0.086975 | 122.9004 | 123.0194 | 58.1451 | -123.0286 | 122.9233 | 122.85 | 58.1772 | -123.0606
240.8438 | 123.23 | -58.1909 | 64.7415 | 0.4728 | -0.00081686 | 0.075628 | -0.0093412 | 0.063262 | 0.0033197 | -0.0028902 | 0.30621 | -0.006325 | 0.053432 | 0.054584 | -0.0010051 | -0.011634 | 64.856 | -58.0811 | 0.004578 | -58.3923 | 64.7141 | -58.2413 | -58.2687 | -58.0673 | 0.041199 | -58.429 | 64.7507 | 64.6683 | -58.2001 | -58.3191 | -0.050354 | -0.07782 | -0.027466 | 0.10986 | -0.20142 | -0.1236 | 0.11444 | -0.009155 | -0.12817 | 0.009155 | 0.1236 | -0.23804 | -0.10986 | -0.073242 | 122.905 | 123.0469 | 58.1955 | -123.0103 | 122.9416 | 122.8592 | 58.2321 | -123.0606
241.8438 | 123.2071 | -58.1726 | 64.7278 | 0.45754 | -0.00081686 | 0.062811 | 0.0056128 | 0.075011 | -0.0020213 | 0.0024508 | 0.39777 | -0.008461 | 0.043819 | 0.054584 | 0.0075399 | -0.00095306 | 64.8743 | -58.0765 | -0.004578 | -58.3786 | 64.6866 | -58.2092 | -58.2413 | -58.049 | 0.032043 | -58.4061 | 64.7507 | 64.6591 | -58.2092 | -58.287 | -0.036622 | -0.068665 | -0.041199 | 0.09613 | -0.20599 | -0.13733 | 0.14648 | -0.036622 | -0.11444 | 0.022888 | 0.1236 | -0.23346 | -0.11902 | -0.068664 | 122.8592 | 123.0469 | 58.168 | -122.9691 | 122.9233 | 122.8317 | 58.2047 | -123.0148
242.8438 | 123.1934 | -58.1955 | 64.6957 | 0.53384 | -0.0018849 | 0.078832 | 0.0098848 | 0.061125 | 0.015069 | -0.0018222 | -0.30414 | -0.002053 | 0.059841 | 0.058857 | 0.0032669 | -0.01377 | 64.8514 | -58.0856 | -0.013733 | -58.3603 | 64.7369 | -58.2047 | -58.255 | -58.0582 | 0.045776 | -58.4106 | 64.7415 | 64.6317 | -58.2092 | -58.2962 | -0.009155 | -0.059509 | 0.041198 | 0.10986 | -0.16479 | -0.10529 | 0.15564 | -0.013733 | -0.10071 | 0.045776 | 0.13733 | -0.21515 | -0.11444 | -0.064087 | 122.9324 | 123.0469 | 58.1818 | -122.9507 | 122.937 | 122.8271 | 58.2413 | -122.9919
243.8438 | 123.1888 | -58.1772 | 64.7369 | 0.48806 | 0.013069 | 0.07456 | 0.00027184 | 0.068602 | 0.021478 | 0.0035188 | 0.33673 | -0.009529 | 0.051296 | 0.07381 | 0.0075399 | -0.0041571 | 64.8239 | -58.1589 | -0.059509 | -58.3969 | 64.7507 | -58.223 | -58.2779 | -58.0765 | 0.022888 | -58.4015 | 64.7552 | 64.6774 | -58.2001 | -58.2916 | -0.045776 | -0.10071 | 0.013733 | 0.01831 | -0.21973 | -0.11902 | 0.086976 | -0.022888 | -0.11444 | 0.018311 | 0.10071 | -0.2243 | -0.10986 | -0.059509 | 122.9279 | 123.0011 | 58.1177 | -123.0148 | 122.9324 | 122.8546 | 58.2001 | -123.0286
244.8438 | 123.3078 | -58.1909 | 64.7324 | 0.51858 | 0.016273 | 0.069219 | 0.021635 | 0.065398 | 0.0033197 | -0.0039582 | 0.55035 | -0.005257 | 0.060909 | 0.055652 | 0.0054039 | -0.01377 | 64.8697 | -58.1818 | -0.086975 | -58.3557 | 64.7141 | -58.2092 | -58.2504 | -58.0627 | 0.036621 | -58.4106 | 64.7278 | 64.6683 | -58.2275 | -58.3649 | -0.018311 | -0.059509 | -0.018311 | 0.009155 | -0.16479 | -0.10529 | 0.13733 | -0.036621 | -0.17395 | -0.004578 | 0.12817 | -0.21973 | -0.045777 | -0.064087 | 122.905 | 123.0606 | 58.1039 | -122.9828 | 122.9187 | 122.8592 | 58.2275 | -123.0972
245.8438 | 123.2254 | -58.1772 | 64.7278 | 0.5491 | 0.0045241 | 0.064947 | 0.0024088 | 0.045104 | -0.0020213 | 0.0056548 | 0.55035 | -0.009529 | 0.064114 | 0.062061 | 0.0064719 | -0.014838 | 64.6133 | -57.9346 | 0.050354 | -58.2596 | 64.7141 | -58.1772 | -58.2367 | -58.0582 | 0.054932 | -58.4015 | 64.7507 | 64.6683 | -58.2092 | -58.3008 | 0 | -0.059509 | -0.013733 | 0.24262 | -0.082398 | -0.022889 | -0.11444 | -0.032044 | -0.1236 | 0.022888 | 0.11902 | -0.2243 | -0.10071 | -0.059509 | 122.8912 | 122.7905 | 58.2275 | -122.9645 | 122.9279 | 122.8455 | 58.2321 | -123.0286
246.8438 | 123.2758 | -58.1589 | 64.7232 | 0.27444 | 0.0055921 | 0.061742 | -0.025362 | 0.060057 | 0.0075917 | -0.0060942 | 0.44354 | -0.009529 | 0.058773 | 0.054584 | 0.010744 | -0.0020211 | 64.9017 | -58.1039 | -0.018311 | -58.3603 | 64.7232 | -58.2138 | -58.2458 | -58.0307 | -0.25635 | -58.3328 | 64.6912 | 64.6454 | -58.1909 | -58.2687 | -0.054931 | -0.086975 | 0 | 0.054932 | -0.20142 | -0.11444 | 0.17853 | -0.032043 | -0.10986 | -0.032044 | 0.12817 | -0.17395 | -0.064087 | -0.07782 | 122.8821 | 123.0606 | 58.1406 | -122.9691 | 122.85 | 122.8043 | 57.9025 | -122.9919
247.8438 | 123.2346 | -58.168 | 64.7186 | 0.56436 | -0.00081686 | 0.063879 | 0.0098848 | 0.054717 | 0.0022517 | 0.0045868 | 0.13837 | 8.4049e-05 | 0.069454 | 0.05138 | 0.017153 | 0.00011494 | 64.8285 | -58.1406 | -0.054932 | -58.3969 | 64.7369 | -58.2138 | -58.2596 | -58.1268 | 0.059509 | -58.4152 | 64.7415 | 64.6545 | -58.2092 | -58.3008 | -0.045776 | -0.091553 | 0.01831 | 0.027466 | -0.22888 | -0.13733 | 0.10986 | -0.041199 | -0.13275 | 0.022888 | 0.041199 | -0.24719 | -0.11444 | -0.064087 | 122.905 | 122.9965 | 58.1131 | -122.9782 | 122.9095 | 122.8226 | 58.2275 | -123.0194
248.8438 | 123.2162 | -58.1955 | 64.7232 | 0.48806 | 0.010932 | 0.063879 | 0.01309 | 0.056853 | 0.0086597 | -0.0039582 | 0.42828 | -0.002053 | 0.04916 | 0.057788 | 0.0075399 | -0.0052251 | 64.7964 | -58.1589 | -0.086975 | -58.4106 | 64.769 | -58.2138 | -58.255 | -58.0948 | -0.022888 | -58.4702 | 64.7598 | 64.7003 | -58.2138 | -58.3282 | -0.01831 | -0.059509 | 0.045776 | 0.036621 | -0.21515 | -0.15564 | 0.073242 | -0.01831 | -0.13275 | 0.036621 | 0.10071 | -0.27466 | -0.14191 | -0.022889 | 122.9645 | 122.9919 | 58.1085 | -122.9782 | 122.9553 | 122.8958 | 58.1726 | -123.0515
249.8438 | 123.1155 | -58.2184 | 64.7644 | 0.36599 | 0.018409 | 0.069219 | 0.0056128 | 0.066466 | 0.00011475 | 0.0142 | 1.298 | 0.005424 | 0.042751 | 0.052448 | 0.0086079 | 0.00011494 | 64.7598 | -58.2504 | -0.12817 | -58.5159 | 64.7736 | -58.2413 | -58.3145 | -58.136 | -0.045776 | -58.5388 | 64.8331 | 64.7324 | -58.2275 | -58.3328 | -0.022888 | -0.09613 | 0.009156 | -0.032043 | -0.29755 | -0.20142 | -0.004577 | -0.009155 | -0.11444 | 0.068665 | 0.082398 | -0.32043 | -0.20599 | -0.032043 | 122.9919 | 122.9782 | 58.0902 | -123.0789 | 123.0515 | 122.9507 | 58.1726 | -123.0972
250.8438 | 123.1705 | -58.2138 | 64.7324 | 0.30496 | 0.021614 | 0.066015 | 0.0056128 | 0.062194 | 0.012933 | 0.0024508 | 0.13837 | 0.001152 | 0.073727 | 0.069538 | 0.010744 | -0.0020211 | 64.801 | -58.2001 | -0.086975 | -58.4244 | 64.7507 | -58.2458 | -58.2825 | -58.1909 | -0.064087 | -58.5663 | 64.8056 | 64.7278 | -58.223 | -58.342 | -0.032044 | -0.068665 | 0.01831 | 0.013733 | -0.21057 | -0.14191 | 0.068664 | -0.009155 | -0.12817 | 0.073242 | 0.022888 | -0.35248 | -0.2243 | -0.004578 | 122.9645 | 123.0148 | 58.1268 | -123.0148 | 123.0194 | 122.9416 | 58.1497 | -123.0743
251.8438 | 123.1201 | -58.2138 | 64.7827 | 0.4728 | 0.0034561 | 0.077764 | 0.010954 | 0.056853 | -0.0030893 | -0.0018222 | 1.6642 | 0.011833 | 0.053432 | 0.055652 | 0.0064719 | 0.0022509 | 64.7552 | -58.2458 | -0.14191 | -58.4473 | 64.7598 | -58.255 | -58.2733 | -58.1314 | -0.10071 | -58.5114 | 64.8102 | 64.7278 | -58.2138 | -58.3008 | -0.041199 | -0.059509 | -0.022888 | -0.032044 | -0.23346 | -0.17395 | -0.027466 | 0 | -0.086975 | 0.027466 | 0.082397 | -0.29755 | -0.21057 | -0.054932 | 122.9736 | 122.9691 | 58.0719 | -123.056 | 123.024 | 122.9416 | 58.1131 | -123.0835
252.8438 | 123.1155 | -58.2138 | 64.7644 | 1.7393 | 0.015205 | 0.070287 | 0.0088168 | 0.058989 | 0.00011475 | 0.012064 | 0.42828 | -0.005257 | 0.06625 | 0.060993 | 0.0054039 | -0.00095306 | 64.6774 | -58.1909 | -0.09613 | -58.4198 | 64.7919 | -58.2367 | -58.287 | -58.1543 | -0.054932 | -58.5159 | 64.8239 | 64.7415 | -58.2321 | -58.3008 | -0.022888 | -0.073242 | 0.027466 | 0.022888 | -0.20599 | -0.13275 | -0.086975 | -0.018311 | -0.086975 | 0.05951 | 0.059509 | -0.30212 | -0.21515 | -0.022888 | 123.0057 | 122.8912 | 58.1177 | -123.0515 | 123.0377 | 122.9553 | 58.1589 | -123.0652
253.8438 | 123.1384 | -58.2001 | 64.801 | 0.32021 | 0.042976 | 0.069219 | 0.012022 | 0.062194 | 0.0033197 | 0.0035188 | 0.29095 | 0.008629 | 0.065182 | 0.05138 | 0.025698 | -0.0062931 | 64.7369 | -58.2367 | -0.1236 | -58.4244 | 64.7781 | -58.2138 | -58.2642 | -58.3374 | 0.27924 | -58.4564 | 64.8331 | 64.7598 | -58.1955 | -58.3511 | -0.013733 | -0.064087 | -0.022888 | -0.036621 | -0.2243 | -0.16022 | -0.064087 | 0.004577 | -0.15106 | 0.032044 | -0.13733 | -0.25635 | -0.10529 | -0.041198 | 122.9782 | 122.937 | 58.0765 | -123.0652 | 123.0331 | 122.9599 | 58.4793 | -123.1522
254.8438 | 123.1018 | -58.2001 | 64.7964 | 0.24392 | 0.033363 | 0.072424 | 0.0034768 | 0.056853 | 0.012933 | 0.00031381 | 0.092591 | 0.001152 | 0.070522 | 0.07381 | 0.0086079 | -0.0062931 | 64.7736 | -58.2092 | -0.091553 | -58.429 | 64.7919 | -58.2138 | -58.2596 | -58.2138 | -0.07782 | -58.548 | 64.8102 | 64.7415 | -58.2275 | -58.3557 | -0.013733 | -0.05951 | -0.004578 | -0.009156 | -0.22888 | -0.16937 | -0.022888 | -0.027466 | -0.15564 | 0.013733 | -0.013733 | -0.3479 | -0.19226 | -0.054932 | 122.9919 | 122.9736 | 58.1085 | -123.056 | 123.0103 | 122.9416 | 58.1223 | -123.1522
255.8438 | 123.1201 | -58.2138 | 64.7873 | 0.25918 | 0.024818 | 0.068151 | 0.0077488 | 0.06433 | 0.0054557 | 0.0013818 | 0.092591 | 0.003288 | 0.056637 | 0.057788 | 0.015017 | -0.015907 | 64.8056 | -58.168 | -0.054932 | -58.4061 | 64.7598 | -58.2275 | -58.2504 | -58.1635 | -0.004578 | -58.4839 | 64.8331 | 64.7369 | -58.2321 | -58.3054 | -0.013733 | -0.036621 | -0.027465 | 0.045776 | -0.19226 | -0.15564 | 0.018311 | -0.018311 | -0.091553 | 0.045777 | 0.050354 | -0.27008 | -0.17853 | -0.050354 | 122.9736 | 123.0194 | 58.1589 | -123.0377 | 123.0469 | 122.9507 | 58.2092 | -123.0927
256.8438 | 123.1705 | -58.1818 | 64.7827 | -0.18333 | 0.012 | 0.064947 | 0.01309 | 0.058989 | 0.00011475 | -0.011435 | -1.6164 | 0.004356 | 0.057705 | 0.059925 | -0.0031411 | -0.0084301 | 64.8376 | -58.1406 | 0.009155 | -58.374 | 64.769 | -58.2138 | -58.2413 | -58.1268 | 0.11902 | -58.4427 | 64.8285 | 64.7781 | -58.1909 | -58.3099 | -0.032043 | -0.059509 | -0.013733 | 0.041199 | -0.19226 | -0.13275 | 0.054931 | -0.009155 | -0.12817 | 0.045776 | 0.054932 | -0.26093 | -0.13275 | -0.004578 | 122.9507 | 123.0194 | 58.1909 | -123.024 | 123.0103 | 122.9599 | 58.3008 | -123.0927
257.8438 | 123.1705 | -58.1772 | 64.7873 | -0.18333 | 0.0077281 | 0.07456 | 0.015226 | 0.058989 | -0.00095325 | -0.014639 | -0.029479 | -0.004189 | 0.073727 | 0.06847 | 0.0011309 | -0.0084301 | 64.8239 | -58.136 | 0.009155 | -58.3603 | 64.7827 | -58.2184 | -58.2596 | -58.1131 | 0.10071 | -58.429 | 64.8376 | 64.7507 | -58.2001 | -58.3099 | -0.041199 | -0.082398 | -0.004577 | 0.041199 | -0.18311 | -0.10071 | 0.036622 | -0.022888 | -0.13275 | 0.050354 | 0.064087 | -0.25177 | -0.11902 | -0.036621 | 122.9599 | 123.0011 | 58.1863 | -123.0469 | 123.0148 | 122.9279 | 58.2779 | -123.0972
258.8438 | 123.1705 | -58.1772 | 64.7827 | 0.045557 | 0.028022 | 0.066015 | 0.0045448 | 0.065398 | 0.0033197 | 0.0013818 | -0.044738 | -0.00098395 | 0.054501 | 0.057788 | 0.0054039 | -0.010566 | 64.8239 | -58.1223 | 0.004578 | -58.374 | 64.801 | -58.1955 | -58.2687 | -58.2321 | 0.17853 | -58.461 | 64.8193 | 64.7598 | -58.2275 | -58.3374 | -0.018311 | -0.091553 | 0.01831 | 0.054932 | -0.19684 | -0.10529 | 0.041199 | -0.050354 | -0.16022 | 0.036621 | -0.054932 | -0.28381 | -0.1236 | -0.022888 | 122.9782 | 123.0011 | 58.1818 | -123.0515 | 122.9965 | 122.937 | 58.3557 | -123.1201
259.8438 | 123.1934 | -58.1635 | 64.801 | 0.060816 | 0.013069 | 0.084173 | -0.011477 | 0.082488 | -0.0020213 | 0.00031381 | 0.1994 | -0.005257 | 0.058773 | 0.064197 | 0.0043349 | -0.0052251 | 64.7964 | -58.1039 | 0.022888 | -58.3786 | 64.7873 | -58.2092 | -58.2413 | -58.1177 | 0.082397 | -58.4518 | 64.8102 | 64.7369 | -58.2321 | -58.3191 | -0.045777 | -0.07782 | -0.013733 | 0.059509 | -0.21515 | -0.13733 | -0.004577 | -0.068665 | -0.15564 | 0.009156 | 0.045776 | -0.28839 | -0.13275 | -0.064087 | 122.9507 | 122.9599 | 58.1863 | -123.0423 | 122.9736 | 122.9004 | 58.2458 | -123.1201
260.8438 | 123.1842 | -58.1818 | 64.7964 | -0.045996 | 0.012 | 0.064947 | 0.0024088 | 0.057921 | 0.0011837 | -0.00075419 | 0.031556 | -0.00098395 | 0.057705 | 0.048175 | 0.0075399 | 0.00011494 | 64.8651 | -58.136 | 0.027466 | -58.3603 | 64.7827 | -58.2001 | -58.2596 | -58.1223 | 0.086975 | -58.461 | 64.8056 | 64.7415 | -58.2138 | -58.3328 | -0.01831 | -0.07782 | -0.013733 | 0.045777 | -0.17853 | -0.10071 | 0.068664 | -0.032043 | -0.15106 | 0.009155 | 0.05951 | -0.27924 | -0.12817 | -0.054932 | 122.9645 | 123.0469 | 58.2092 | -123.056 | 122.9874 | 122.9233 | 58.2687 | -123.1293
261.8438 | 123.1659 | -58.168 | 64.7964 | -0.24436 | 0.0023871 | 0.070287 | -0.00079616 | 0.071807 | -0.0041573 | 0.00031381 | -0.19733 | -0.003121 | 0.057705 | 0.070606 | 0.0086079 | 0.0022509 | 64.7964 | -58.1314 | -0.018311 | -58.3557 | 64.7781 | -58.2275 | -58.2596 | -58.1314 | 0.09613 | -58.4473 | 64.8193 | 64.7369 | -58.2184 | -58.3237 | -0.059509 | -0.091553 | -0.018311 | 0.036621 | -0.18768 | -0.09613 | 0 | -0.050354 | -0.15564 | 0.022888 | 0.036621 | -0.27924 | -0.1236 | -0.05951 | 122.9462 | 122.9645 | 58.1497 | -123.056 | 122.9874 | 122.905 | 58.2642 | -123.1201
262.8438 | 123.1705 | -58.1818 | 64.8193 | -0.21384 | 0.0087961 | 0.077764 | 0.0066808 | 0.06433 | -0.014838 | 0.0077908 | -0.2431 | -0.009529 | 0.073727 | 0.046039 | 0.0075399 | -0.011634 | 64.7919 | -58.1635 | -0.022888 | -58.3694 | 64.8102 | -58.2001 | -58.2687 | -58.1543 | 0.07782 | -58.4427 | 64.8422 | 64.7736 | -58.2184 | -58.3145 | -0.01831 | -0.086975 | -0.009155 | 0.018311 | -0.18768 | -0.10071 | -0.027466 | -0.036621 | -0.13275 | 0.022888 | 0.027466 | -0.26093 | -0.12817 | -0.045776 | 122.9919 | 122.9736 | 58.1589 | -123.0881 | 123.024 | 122.9553 | 58.2596 | -123.1339
263.8438 | 123.1201 | -58.223 | 64.7964 | -0.030737 | 0.012 | 0.086309 | -0.0082732 | 0.050444 | -0.023383 | -0.016776 | -0.059997 | -0.007393 | 0.051296 | 0.055652 | -0.010618 | 0.0011829 | 64.8697 | -58.1726 | -0.013733 | -58.4015 | 64.7964 | -58.1726 | -58.2367 | -58.1543 | 0.022888 | -58.3374 | 64.8743 | 64.801 | -58.1726 | -58.3008 | 0.050354 | -0.013733 | 0 | 0.050354 | -0.17853 | -0.16479 | 0.073242 | 0.050354 | -0.07782 | 0.07782 | 0.068664 | -0.11444 | -0.036621 | 0.004577 | 123.0194 | 123.0927 | 58.2092 | -123.0331 | 123.0972 | 123.024 | 58.2458 | -123.0972
264.8438 | 123.143 | -58.1726 | 64.8193 | -0.24436 | 0.00025114 | 0.069219 | -0.0040002 | 0.056853 | -0.022315 | -0.010367 | -0.30414 | -0.008461 | 0.058773 | 0.063129 | -0.0031411 | -0.0020211 | 64.8193 | -58.0811 | 0.045776 | -58.3511 | 64.769 | -58.1635 | -58.2321 | -58.1406 | 0.07782 | -58.4518 | 64.8239 | 64.7507 | -58.2092 | -58.3191 | 0.009155 | -0.05951 | -0.050354 | 0.091552 | -0.17853 | -0.11902 | 0 | -0.036622 | -0.14648 | 0.004578 | 0.032043 | -0.27924 | -0.13275 | -0.068665 | 122.9416 | 122.9919 | 58.2184 | -123.0515 | 122.9965 | 122.9233 | 58.2504 | -123.1384
265.8438 | 123.111 | -58.1772 | 64.8239 | -0.19858 | -0.0082939 | 0.073492 | -0.0018642 | 0.055785 | -0.021247 | -0.013571 | -1.1739 | -0.017006 | 0.054501 | 0.060993 | -0.0042101 | -0.014838 | 64.7964 | -58.136 | 0.004578 | -58.3878 | 64.7781 | -58.1955 | -58.2321 | -58.136 | 0.086975 | -58.4518 | 64.8605 | 64.7873 | -58.2184 | -58.3099 | -0.018311 | -0.054932 | -0.045777 | 0.041199 | -0.21057 | -0.15564 | -0.027466 | -0.041199 | -0.13275 | 0.036621 | 0.041199 | -0.27466 | -0.14191 | -0.036622 | 122.9553 | 122.9736 | 58.1818 | -123.056 | 123.0377 | 122.9645 | 58.2642 | -123.1339
266.8438 | 123.1522 | -58.1726 | 64.8193 | -1.1294 | -0.0082939 | 0.072424 | 0.017362 | 0.065398 | -0.01377 | -0.010367 | -0.3194 | -0.009529 | 0.064114 | 0.044971 | -0.010618 | 0.0011829 | 64.7736 | -58.1223 | 0.013733 | -58.3923 | 64.8193 | -58.2184 | -58.2413 | -58.2321 | -0.036621 | -58.4976 | 64.8285 | 64.7369 | -58.2413 | -58.3282 | -0.045777 | -0.068665 | 0 | 0.050354 | -0.21973 | -0.15106 | -0.045776 | -0.068665 | -0.15564 | 0.009155 | -0.05951 | -0.32501 | -0.16937 | -0.082398 | 122.9919 | 122.9462 | 58.1863 | -123.0606 | 123.0011 | 122.9095 | 58.136 | -123.1476
267.8438 | 123.1247 | -58.1955 | 64.8148 | -0.29014 | -0.00081686 | 0.084173 | -0.0061362 | 0.051512 | -0.01377 | -0.014639 | -0.22784 | -0.009529 | 0.037411 | 0.07381 | 0.0064719 | -0.011634 | 64.801 | -58.0765 | 0.032043 | -58.3511 | 64.7736 | -58.2138 | -58.223 | -58.136 | 0.10986 | -58.3923 | 64.8376 | 64.7736 | -58.1818 | -58.3008 | -0.01831 | -0.027465 | -0.041198 | 0.11902 | -0.15564 | -0.12817 | -0.013733 | 0.013733 | -0.10529 | 0.022888 | 0.05951 | -0.19684 | -0.091553 | -0.041198 | 122.9691 | 122.9965 | 58.2275 | -123.0377 | 123.0331 | 122.9691 | 58.3054 | -123.1155
268.8438 | 123.1842 | -58.1451 | 64.7964 | -0.19858 | -0.013634 | 0.078832 | 0.0066808 | 0.067534 | -0.01377 | -0.016776 | -0.22784 | -0.012734 | 0.044888 | 0.050312 | -0.0031411 | -0.0062931 | 64.8468 | -58.0444 | 0.082397 | -58.3282 | 64.7827 | -58.1726 | -58.223 | -58.1039 | 0.13275 | -58.4061 | 64.801 | 64.7186 | -58.1909 | -58.3008 | -0.027465 | -0.077819 | -0.013733 | 0.10071 | -0.1831 | -0.10529 | 0.050354 | -0.045776 | -0.15564 | 0.004577 | 0.041199 | -0.26093 | -0.10529 | -0.07782 | 122.9279 | 122.9919 | 58.2275 | -123.0194 | 122.9462 | 122.8638 | 58.2779 | -123.0972
269.8438 | 123.2162 | -58.136 | 64.769 | -0.13755 | -0.0072259 | 0.087377 | -0.0018642 | 0.077147 | -0.016974 | -0.012503 | -0.18207 | -0.022347 | 0.044888 | 0.059925 | 6.2882e-05 | -0.012702 | 64.8514 | -58.0261 | 0.086975 | -58.3237 | 64.7644 | -58.1726 | -58.1863 | -58.0673 | 0.16937 | -58.3603 | 64.7781 | 64.7049 | -58.168 | -58.2962 | -0.036621 | -0.050354 | -0.004578 | 0.10986 | -0.18768 | -0.13733 | 0.082397 | -0.032044 | -0.16022 | 0.009155 | 0.068664 | -0.2243 | -0.064087 | -0.064087 | 122.9004 | 122.9874 | 58.223 | -122.9553 | 122.9141 | 122.8409 | 58.3054 | -123.0652
270.8438 | 123.2712 | -58.1406 | 64.7781 | 0.030298 | -0.012566 | 0.070287 | 0.00027184 | 0.056853 | -0.023383 | -0.0060942 | 0.062074 | -0.021279 | 0.045956 | 0.049243 | -0.014891 | -0.0062931 | 64.856 | -58.049 | 0.041199 | -58.3374 | 64.7598 | -58.1726 | -58.2458 | -58.0307 | 0.1236 | -58.374 | 64.769 | 64.7049 | -58.1543 | -58.3054 | -0.032043 | -0.10529 | -0.01831 | 0.091553 | -0.19684 | -0.091552 | 0.07782 | -0.013733 | -0.1648 | -0.009155 | 0.10986 | -0.23346 | -0.068664 | -0.073242 | 122.9004 | 122.9965 | 58.1818 | -123.024 | 122.9095 | 122.8455 | 58.2642 | -123.0835
271.8438 | 123.2391 | -58.1772 | 64.7461 | 0.091333 | -0.018975 | 0.084173 | 0.00027184 | 0.062194 | -0.0084293 | -0.012503 | 0.16888 | -0.006325 | 0.058773 | 0.05138 | -0.0063461 | 0.00011494 | 64.8285 | -58.0811 | 0.009155 | -58.3557 | 64.769 | -58.1909 | -58.2367 | -58.0582 | 0.09613 | -58.374 | 64.7919 | 64.7049 | -58.1635 | -58.2825 | -0.013733 | -0.059509 | 0.022888 | 0.09613 | -0.17853 | -0.11902 | 0.082397 | 0.013733 | -0.10529 | 0.045776 | 0.11902 | -0.19684 | -0.091552 | -0.041199 | 122.9462 | 123.0057 | 58.1863 | -122.9828 | 122.9691 | 122.8821 | 58.2733 | -123.0286
272.8594 | 123.2941 | -58.1268 | 64.7461 | 0.076074 | -0.015771 | 0.072424 | -0.0082732 | 0.065398 | -0.0052253 | -0.012503 | 0.046815 | -0.007393 | 0.052364 | 0.049243 | 0.0021989 | -0.01377 | 64.8926 | -58.0307 | 0.068665 | -58.3328 | 64.7552 | -58.2001 | -58.2275 | -57.9941 | 0.1831 | -58.3191 | 64.7736 | 64.7095 | -58.1451 | -58.2733 | -0.073242 | -0.10071 | 0.009155 | 0.09613 | -0.20599 | -0.10529 | 0.14648 | -0.018311 | -0.14648 | 0.027466 | 0.13275 | -0.19226 | -0.045777 | -0.036621 | 122.8821 | 123.0194 | 58.1955 | -122.9736 | 122.9004 | 122.8363 | 58.3099 | -123.0194
274.4062 | 123.175 | -58.1635 | 64.7873 | -0.3054 | -0.014702 | 0.0799 | 0.00027184 | 0.061125 | -0.0020213 | -0.0018222 | -0.30414 | -0.010597 | 0.048092 | 0.065265 | 0.0043349 | -0.011634 | 64.8834 | -58.0582 | 0.068665 | -58.342 | 64.7736 | -58.168 | -58.1955 | -58.0856 | 0.11902 | -58.429 | 64.8102 | 64.7415 | -58.168 | -58.2642 | -0.004578 | -0.032044 | -0.013732 | 0.10529 | -0.17853 | -0.14648 | 0.096131 | -0.004578 | -0.10071 | 0.022889 | 0.07782 | -0.2655 | -0.1648 | -0.045776 | 122.937 | 123.0469 | 58.2321 | -122.9828 | 122.9736 | 122.905 | 58.2825 | -123.0515
275.375 | 123.1522 | -58.1909 | 64.7873 | 0.12185 | 0.0098641 | 0.064947 | 0.0034768 | 0.056853 | 0.032159 | -0.0071622 | 0.18414 | 8.4049e-05 | 0.041683 | 0.052448 | 0.010744 | -0.019111 | 64.769 | -58.255 | -0.1236 | -58.4381 | 64.7827 | -58.2458 | -58.3099 | -58.1543 | -0.013733 | -58.7952 | 64.7415 | 64.6591 | -58.2642 | -58.3511 | -0.054932 | -0.11902 | -0.004577 | -0.064087 | -0.24719 | -0.12817 | -0.01831 | -0.073242 | -0.16022 | -0.045776 | 0.036621 | -0.60425 | -0.44403 | -0.12817 | 122.9736 | 122.9599 | 58.0673 | -123.0972 | 122.9324 | 122.85 | 58.1772 | -123.1384
276.6406 | 123.0835 | -58.2184 | 64.7736 | 0.12185 | 0.025886 | 0.071355 | 0.0013408 | 0.070738 | 0.019342 | -0.00075419 | 0.10785 | -0.002053 | 0.057705 | 0.052448 | 0.019289 | -0.016975 | 64.7781 | -58.1955 | -0.09613 | -58.4061 | 64.8331 | -58.2138 | -58.2779 | -58.2047 | -0.09613 | -58.5526 | 64.7964 | 64.7369 | -58.255 | -58.342 | 0.004578 | -0.059509 | 0.059509 | 0.022888 | -0.18768 | -0.12817 | 0.004577 | -0.036621 | -0.1236 | 0.022888 | 0.013733 | -0.33417 | -0.21057 | -0.036622 | 123.0515 | 122.9965 | 58.1223 | -123.0515 | 123.0148 | 122.9553 | 58.1223 | -123.1155
278.0469 | 123.2162 | -58.1863 | 64.7278 | 0.50332 | 0.010932 | 0.069219 | 0.010954 | 0.063262 | -0.022315 | -0.011435 | 0.48932 | -0.01487 | 0.058773 | 0.066333 | -0.0020731 | 0.0043879 | 64.8422 | -58.0765 | -0.009155 | -58.3694 | 64.7141 | -58.2047 | -58.2596 | -58.0399 | 0.041199 | -58.4061 | 64.7736 | 64.6729 | -58.2275 | -58.2962 | -0.018311 | -0.073243 | -0.013733 | 0.10986 | -0.18311 | -0.10986 | 0.11444 | -0.041199 | -0.10986 | 0.045777 | 0.14648 | -0.21973 | -0.10986 | -0.054931 | 122.9004 | 123.0286 | 58.1772 | -122.9874 | 122.9599 | 122.8592 | 58.2275 | -123.024
279.4219 | 123.1338 | -58.1909 | 64.8148 | -0.12229 | -0.00081686 | 0.073492 | 0.032316 | 0.06433 | -0.0030893 | -0.0092992 | -0.30414 | -0.015938 | 0.060909 | 0.067401 | -0.012754 | -0.0094981 | 64.7873 | -58.1589 | -0.004578 | -58.3923 | 64.8148 | -58.2001 | -58.2504 | -58.136 | 0.15106 | -58.2825 | 64.9063 | 64.8102 | -58.1863 | -58.2962 | -0.009155 | -0.059509 | 0 | 0.032043 | -0.20142 | -0.14191 | -0.027466 | 0.004578 | -0.10529 | 0.091553 | 0.054932 | -0.091553 | 0.013733 | -0.004577 | 123.0057 | 122.9782 | 58.1863 | -123.0652 | 123.0972 | 123.0011 | 58.342 | -123.111
280.2344 | 123.2346 | -58.1772 | 64.7415 | 0.41177 | -0.014702 | 0.062811 | -0.00079616 | 0.051512 | -0.014838 | -0.010367 | 0.30621 | -0.009529 | 0.044888 | 0.050312 | -0.0010051 | 0.00011494 | 64.8239 | -58.1223 | -0.022888 | -58.3969 | 64.7324 | -58.2047 | -58.223 | -58.0856 | 0.036621 | -58.4198 | 64.769 | 64.6912 | -58.1955 | -58.287 | -0.027466 | -0.045776 | -0.009155 | 0.054932 | -0.21973 | -0.17395 | 0.082398 | -0.018311 | -0.10986 | 0.027466 | 0.091553 | -0.24262 | -0.13275 | -0.050354 | 122.9095 | 123.0011 | 58.1543 | -122.9645 | 122.9462 | 122.8683 | 58.2138 | -123.0286
281.2656 | 123.1796 | -58.1589 | 64.7552 | 0.48806 | -0.0018849 | 0.056402 | -0.015749 | 0.06967 | 0.012933 | 0.00031381 | 0.36725 | -0.003121 | 0.044888 | 0.06847 | 0.016085 | -0.010566 | 64.7919 | -58.1955 | -0.11902 | -58.4244 | 64.801 | -58.2184 | -58.2779 | -58.1223 | -0.045776 | -58.493 | 64.801 | 64.6866 | -58.2047 | -58.3374 | -0.059509 | -0.11902 | 0.045776 | -0.036621 | -0.2655 | -0.14648 | 0.036621 | -0.045776 | -0.17853 | 0.045776 | 0.036622 | -0.33417 | -0.15564 | -0.068665 | 122.9599 | 122.9507 | 58.0399 | -123.0331 | 122.9599 | 122.8455 | 58.1131 | -123.0927
285.5938 | 123.262 | -58.1543 | 64.769 | -0.015478 | -0.0093619 | 0.085241 | -0.0050682 | 0.058989 | -0.015906 | -0.011435 | -0.01422 | -0.009529 | 0.040615 | 0.050312 | 6.2882e-05 | 0.0033199 | 64.8743 | -58.0078 | 0.073242 | -58.3282 | 64.7781 | -58.1909 | -58.2138 | -58.0032 | 0.19226 | -58.3191 | 64.769 | 64.7141 | -58.1589 | -58.2733 | -0.036621 | -0.059509 | 0.009155 | 0.14648 | -0.17395 | -0.11444 | 0.10529 | -0.004578 | -0.11902 | 0 | 0.15106 | -0.16479 | -0.045777 | -0.054932 | 122.9324 | 123.0286 | 58.2275 | -122.9828 | 122.9233 | 122.8683 | 58.3466 | -123.0423
286.1562 | 123.1201 | -58.1818 | 64.7964 | -0.015478 | 0.019477 | 0.084173 | 0.016294 | 0.051512 | 0.017205 | -0.0092992 | -0.21259 | 8.4049e-05 | 0.077999 | 0.059925 | 0.018221 | -0.01377 | 64.8697 | -58.1039 | 0 | -58.3603 | 64.8102 | -58.223 | -58.2596 | -58.0948 | 0.07782 | -58.4427 | 64.801 | 64.7095 | -58.2138 | -58.3511 | -0.041198 | -0.07782 | 0.013733 | 0.07782 | -0.17853 | -0.10071 | 0.073242 | -0.032043 | -0.16937 | 0.004577 | 0.086975 | -0.26093 | -0.091553 | -0.086975 | 122.9919 | 123.0515 | 58.1818 | -123.056 | 122.9828 | 122.8912 | 58.2596 | -123.1476
286.8438 | 123.2346 | -58.1635 | 64.7232 | -0.76316 | -0.0050889 | 0.072424 | 0.015226 | 0.066466 | -0.0052253 | -0.00075419 | 0.48932 | -0.011666 | 0.060909 | 0.070606 | 0.0021989 | 0.00011494 | 64.8376 | -58.0353 | 0 | -58.3694 | 64.7186 | -58.2184 | -58.1955 | -58.0536 | 0.041199 | -58.3969 | 64.7369 | 64.65 | -58.2367 | -58.3099 | -0.054932 | -0.032044 | -0.004578 | 0.12817 | -0.20599 | -0.17395 | 0.11444 | -0.073242 | -0.14648 | 0.013732 | 0.10986 | -0.23346 | -0.086975 | -0.073243 | 122.8821 | 123.0011 | 58.1635 | -122.9187 | 122.9004 | 122.8134 | 58.2047 | -123.0331
287.8438 | 123.2071 | -58.1772 | 64.7186 | 0.48806 | -0.0082939 | 0.058538 | 0.01309 | 0.061125 | -0.012702 | -0.015707 | 0.48932 | -0.004189 | 0.061977 | 0.052448 | -0.0020731 | -0.0062931 | 64.8331 | -58.0765 | 0.013733 | -58.3694 | 64.7049 | -58.2001 | -58.2367 | -58.0811 | 0.041199 | -58.3969 | 64.7507 | 64.6683 | -58.2138 | -58.2962 | -0.022888 | -0.059509 | -0.013733 | 0.10071 | -0.19226 | -0.13275 | 0.11444 | -0.036621 | -0.11902 | 0.032043 | 0.09613 | -0.21973 | -0.10071 | -0.050354 | 122.8821 | 123.0103 | 58.1909 | -122.9553 | 122.9279 | 122.8455 | 58.2184 | -123.0148
288.8438 | 123.2071 | -58.168 | 64.7507 | 0.48806 | 0.0023871 | 0.086309 | 0.0034768 | 0.060057 | -0.012702 | -0.0050262 | 0.41303 | -0.021279 | 0.050228 | 0.060993 | -0.0020731 | -0.011634 | 64.8056 | -58.1039 | -0.018311 | -58.3969 | 64.7415 | -58.2001 | -58.2458 | -58.0948 | 0.018311 | -58.4198 | 64.7552 | 64.6912 | -58.2047 | -58.2962 | -0.032043 | -0.07782 | -0.009155 | 0.064087 | -0.22888 | -0.15106 | 0.054932 | -0.036621 | -0.12817 | 0.004578 | 0.073242 | -0.25177 | -0.1236 | -0.059509 | 122.9095 | 122.9736 | 58.1497 | -122.9965 | 122.9233 | 122.8592 | 58.1863 | -123.0469
289.8438 | 123.2071 | -58.1635 | 64.7324 | 0.45754 | 0.0066601 | 0.060674 | 0.0024088 | 0.048308 | 0.0011837 | -0.016776 | 0.33673 | -0.018074 | 0.043819 | 0.053516 | -0.0031411 | -0.0084301 | 64.856 | -58.0765 | -0.032043 | -58.374 | 64.7049 | -58.1772 | -58.2413 | -58.0719 | 0.036621 | -58.4198 | 64.7415 | 64.6637 | -58.2138 | -58.3145 | -0.013733 | -0.07782 | -0.027466 | 0.086975 | -0.21057 | -0.13275 | 0.1236 | -0.050354 | -0.15106 | 0.009155 | 0.091553 | -0.25635 | -0.10529 | -0.068665 | 122.8683 | 123.0194 | 58.1314 | -122.9736 | 122.905 | 122.8271 | 58.2001 | -123.0469
290.8438 | 123.262 | -58.1863 | 64.7186 | 0.42703 | 0.0066601 | 0.071355 | 0.01309 | 0.055785 | 0.0097277 | -0.0071622 | 0.22992 | -0.011666 | 0.044888 | 0.053516 | 0.0064719 | -0.011634 | 64.8651 | -58.0719 | -0.041199 | -58.342 | 64.7278 | -58.1863 | -58.2504 | -58.0399 | 0.041199 | -58.4106 | 64.7598 | 64.6729 | -58.2092 | -58.287 | 0 | -0.064087 | 0.009155 | 0.11444 | -0.15564 | -0.091553 | 0.14648 | -0.022889 | -0.10071 | 0.041199 | 0.14648 | -0.22431 | -0.1236 | -0.045776 | 122.9141 | 123.0515 | 58.1451 | -122.9691 | 122.9462 | 122.8592 | 58.2275 | -123.0057
291.8438 | 123.175 | -58.1726 | 64.7461 | 0.56436 | 0.013069 | 0.076696 | 0.010954 | 0.055785 | 0.015069 | 0.0067228 | 0.35199 | -0.002053 | 0.072659 | 0.052448 | 0.0054039 | -0.01377 | 64.7919 | -58.1909 | -0.091553 | -58.4152 | 64.7644 | -58.2138 | -58.2687 | -58.1131 | -0.036621 | -58.4839 | 64.769 | 64.6866 | -58.2275 | -58.3191 | -0.041199 | -0.096131 | 0.01831 | -0.018311 | -0.24262 | -0.14648 | 0.045776 | -0.054932 | -0.14648 | 0.022888 | 0.059509 | -0.31128 | -0.1648 | -0.05951 | 122.937 | 122.9645 | 58.0811 | -123.0148 | 122.9416 | 122.8592 | 58.136 | -123.0652
292.8438 | 123.2254 | -58.1863 | 64.7232 | 0.5491 | 0.0098641 | 0.063879 | 0.0098848 | 0.056853 | 0.0011837 | 0.0077908 | -0.01422 | 0.001152 | 0.059841 | 0.071674 | 0.015017 | -0.0062931 | 64.8285 | -58.1314 | -0.064087 | -58.3832 | 64.7598 | -58.2138 | -58.2275 | -58.0994 | 0.004578 | -58.4015 | 64.7507 | 64.6729 | -58.2138 | -58.2962 | -0.027466 | -0.041199 | 0.036621 | 0.054931 | -0.19684 | -0.15564 | 0.10528 | -0.027466 | -0.10986 | 0.027465 | 0.086975 | -0.21515 | -0.10528 | -0.050354 | 122.9462 | 123.0148 | 58.1223 | -122.9507 | 122.937 | 122.8592 | 58.1909 | -123.0194
293.8438 | 123.262 | -58.1589 | 64.7324 | 0.76272 | 0.0066601 | 0.062811 | 0.0013408 | 0.071807 | -0.0030893 | 0.0045868 | 0.50458 | -0.002053 | 0.053432 | 0.041767 | -0.0010051 | -0.020179 | 64.856 | -58.0811 | -0.018311 | -58.3649 | 64.7232 | -58.2001 | -58.2321 | -57.962 | 0.068665 | -58.374 | 64.7736 | 64.6912 | -58.1818 | -58.3099 | -0.041198 | -0.073242 | -0.009155 | 0.07782 | -0.20599 | -0.13275 | 0.1236 | -0.022888 | -0.15106 | 0.041199 | 0.19684 | -0.21515 | -0.064086 | -0.041199 | 122.8821 | 123.0148 | 58.1406 | -122.9645 | 122.9324 | 122.85 | 58.2275 | -123.0423
294.8438 | 123.2162 | -58.1818 | 64.682 | 0.38125 | 0.0077281 | 0.05747 | -0.010409 | 0.055785 | 0.0011837 | 0.0035188 | 0.44354 | -0.007393 | 0.057705 | 0.067401 | 0.0021989 | -0.0094981 | 64.7919 | -58.1406 | -0.022888 | -58.3603 | 64.7141 | -58.1909 | -58.2367 | -58.0627 | 0.045776 | -58.4061 | 64.7324 | 64.6866 | -58.2184 | -58.3145 | -0.009155 | -0.054931 | 0.032043 | 0.041199 | -0.17853 | -0.1236 | 0.10986 | -0.036621 | -0.13275 | 0.050354 | 0.11902 | -0.2243 | -0.091553 | 0.004577 | 122.8958 | 122.9736 | 58.1589 | -122.9187 | 122.9141 | 122.8683 | 58.2275 | -122.9965
295.8438 | 123.2346 | -58.168 | 64.7186 | 0.57961 | 0.022682 | 0.069219 | 0.0066808 | 0.060057 | 0.0054557 | -0.0071622 | 0.18414 | -0.013802 | 0.06625 | 0.071674 | 0.018221 | -0.0062931 | 64.8148 | -58.0994 | -0.064087 | -58.3878 | 64.7598 | -58.223 | -58.255 | -58.1177 | 0.059509 | -58.4106 | 64.7598 | 64.6637 | -58.2275 | -58.2962 | -0.054931 | -0.086975 | 0.041199 | 0.068665 | -0.21973 | -0.13275 | 0.09613 | -0.059509 | -0.12817 | 0.041199 | 0.050354 | -0.24262 | -0.11444 | -0.054932 | 122.9279 | 122.9828 | 58.1039 | -122.9736 | 122.9279 | 122.8317 | 58.2275 | -123.0148
296.8438 | 123.23 | -58.1589 | 64.7415 | 0.53384 | 0.00025114 | 0.068151 | 0.0098848 | 0.063262 | 0.0033197 | -0.0050262 | 0.41303 | -0.006325 | 0.044888 | 0.07381 | 0.0096759 | -0.0030891 | 64.801 | -58.1635 | -0.07782 | -58.4106 | 64.7415 | -58.2275 | -58.2642 | -58.0811 | 0 | -58.4473 | 64.7507 | 64.682 | -58.2184 | -58.3145 | -0.068664 | -0.10528 | 0 | -0.004577 | -0.25177 | -0.14649 | 0.059509 | -0.059509 | -0.15564 | 0.009155 | 0.07782 | -0.28839 | -0.13275 | -0.059509 | 122.9004 | 122.9599 | 58.0811 | -123.0057 | 122.9095 | 122.8409 | 58.1589 | -123.056
297.8438 | 123.1201 | -58.2138 | 64.7507 | 0.44228 | 0.013069 | 0.072424 | 0.0045448 | 0.056853 | 0.0086597 | -0.0060942 | -1.3417 | 0.012901 | 0.056637 | 0.060993 | 0.0021989 | -0.0062931 | 64.7827 | -58.2138 | -0.027466 | -58.6533 | 64.7232 | -58.2642 | -58.2962 | -58.1406 | -0.054932 | -58.5388 | 64.8056 | 64.7278 | -58.2321 | -58.3237 | -0.050354 | -0.082398 | -0.027465 | 0 | -0.43945 | -0.35705 | 0.032044 | -0.018311 | -0.10986 | 0.054932 | 0.073242 | -0.32501 | -0.21515 | -0.022888 | 122.937 | 122.9965 | 58.1863 | -123.0469 | 123.0194 | 122.9416 | 58.1589 | -123.0743
298.8438 | 123.1338 | -58.223 | 64.8148 | 0.36599 | 0.026954 | 0.072424 | 0.014158 | 0.06967 | 0.0043877 | -0.0028902 | 0.32147 | 8.4049e-05 | 0.06625 | 0.066333 | 0.0086079 | -0.011634 | 64.7369 | -58.2504 | -0.13275 | -58.4564 | 64.7873 | -58.2413 | -58.2779 | -58.1726 | -0.068665 | -58.5251 | 64.8148 | 64.7049 | -58.2504 | -58.374 | -0.018311 | -0.054932 | -0.027466 | -0.027466 | -0.23346 | -0.17853 | -0.07782 | -0.027466 | -0.15106 | 0 | 0.050354 | -0.30212 | -0.15106 | -0.10986 | 123.0103 | 122.9599 | 58.0902 | -123.0927 | 123.0377 | 122.9279 | 58.1543 | -123.1888
299.8438 | 123.0972 | -58.2138 | 64.7873 | 0.44228 | 0.037635 | 0.067083 | 0.0013408 | 0.073943 | -0.0052253 | -0.013571 | 0.18414 | -0.009529 | 0.059841 | 0.057788 | -0.0020731 | -0.0030891 | 64.9887 | -58.1955 | -0.073242 | -58.3786 | 64.8285 | -58.2138 | -58.2733 | -58.1406 | -0.045776 | -58.5159 | 64.801 | 64.7278 | -58.2184 | -58.3237 | 0 | -0.059509 | 0.041199 | 0.01831 | -0.1648 | -0.10529 | 0.20142 | -0.004578 | -0.10986 | 0.013733 | 0.073242 | -0.30212 | -0.19226 | -0.059509 | 123.0423 | 123.2025 | 58.1406 | -123.0606 | 123.0148 | 122.9416 | 58.168 | -123.111
300.8438 | 123.175 | -58.1772 | 64.7598 | 0.38125 | 0.026954 | 0.078832 | 0.010954 | 0.058989 | 0.00011475 | 0.00031381 | 0.41303 | -0.013802 | 0.067318 | 0.067401 | 0.010744 | -0.011634 | 64.7598 | -58.1955 | -0.11902 | -58.4198 | 64.769 | -58.2321 | -58.2916 | -58.1314 | -0.022888 | -58.4656 | 64.7873 | 64.6866 | -58.2504 | -58.342 | -0.054932 | -0.11444 | 0.009155 | -0.018311 | -0.24262 | -0.12817 | 0 | -0.073242 | -0.16479 | 0.027465 | 0.045776 | -0.28839 | -0.1236 | -0.073243 | 122.9462 | 122.937 | 58.0582 | -123.0515 | 122.9645 | 122.8638 | 58.1543 | -123.1018
301.8438 | 123.1567 | -58.1909 | 64.7552 | -0.51902 | 0.016273 | 0.076696 | -0.00079616 | 0.050444 | 0.0054557 | -0.0092992 | 0.29095 | -0.007393 | 0.056637 | 0.067401 | 0.0021989 | -0.0062931 | 64.7736 | -58.2275 | -0.1236 | -58.4152 | 64.7827 | -58.2321 | -58.2642 | -58.1497 | -0.045776 | -58.493 | 64.7873 | 64.7369 | -58.2275 | -58.3374 | -0.041199 | -0.073242 | 0.027466 | -0.036621 | -0.2243 | -0.15106 | 0.018311 | -0.036621 | -0.14648 | 0.032043 | 0.041199 | -0.30212 | -0.15564 | -0.018311 | 122.9736 | 122.9645 | 58.0673 | -123.0194 | 122.9782 | 122.9279 | 58.1451 | -123.0927
302.8438 | 123.1476 | -58.1955 | 64.7644 | 0.42703 | 0.038703 | 0.073492 | -0.0029322 | 0.051512 | 0.0022517 | -0.0092992 | 0.35199 | -0.006325 | 0.052364 | 0.052448 | -0.0020731 | 0.0011829 | 64.7736 | -58.4198 | -0.3479 | -58.4335 | 64.7186 | -58.2458 | -58.2642 | -58.1543 | -0.086975 | -58.5205 | 64.7827 | 64.7141 | -58.2458 | -58.3603 | -0.050354 | -0.068664 | -0.045776 | -0.2243 | -0.23804 | -0.16937 | 0.009156 | -0.050354 | -0.16479 | 0.018311 | 0.041199 | -0.32501 | -0.16022 | -0.050354 | 122.9141 | 122.9691 | 57.8476 | -123.0286 | 122.9782 | 122.9095 | 58.1085 | -123.1247
303.8438 | 123.1064 | -58.223 | 64.7415 | 0.44228 | 0.0045241 | 0.067083 | -0.0050682 | 0.049376 | 0.0097277 | -0.0092992 | 0.33673 | 8.4049e-05 | 0.064114 | 0.049243 | 0.013948 | -0.0030891 | 64.7552 | -58.2275 | -0.1236 | -58.4198 | 64.769 | -58.2184 | -58.2596 | -58.1543 | -0.42114 | -58.4793 | 64.7598 | 64.7415 | -58.2321 | -58.3191 | 0.004577 | -0.036622 | 0.027466 | -0.004578 | -0.19684 | -0.16022 | 0.013733 | -0.009156 | -0.096131 | 0.018311 | 0.068664 | -0.25635 | -0.16022 | 0 | 122.9919 | 122.9782 | 58.0994 | -123.0011 | 122.9828 | 122.9645 | 57.8018 | -123.0606
304.8438 | 123.1155 | -58.1909 | 64.7964 | 0.27444 | 0.019477 | 0.073492 | 0.021635 | 0.070738 | -0.0020213 | 0.0045868 | 0.077332 | 0.009697 | 0.076931 | 0.047107 | -0.0010051 | -0.0062931 | 64.7964 | -58.1772 | -0.068665 | -58.4015 | 64.7644 | -58.2184 | -58.2596 | -58.1497 | -0.009155 | -58.5114 | 64.8376 | 64.7552 | -58.2321 | -58.3191 | -0.027466 | -0.068665 | -0.032044 | 0.013733 | -0.21057 | -0.14191 | 0 | -0.041199 | -0.12817 | 0.041198 | 0.041199 | -0.32043 | -0.19226 | -0.041199 | 122.9553 | 122.9874 | 58.1223 | -123.056 | 123.0286 | 122.9462 | 58.1818 | -123.1155
305.8594 | 123.2346 | -58.1726 | 64.7278 | 0.50332 | 0.018409 | 0.068151 | 0.020567 | 0.057921 | -0.012702 | -0.0082312 | 0.55035 | -0.005257 | 0.051296 | 0.050312 | 0.0032669 | -0.00095306 | 64.8148 | -58.0811 | -0.032043 | -58.374 | 64.7049 | -58.2001 | -58.2367 | -58.0765 | 0.068665 | -58.3969 | 64.7369 | 64.6683 | -58.2413 | -58.3054 | -0.027466 | -0.064087 | -0.022888 | 0.091552 | -0.20142 | -0.13733 | 0.086975 | -0.068665 | -0.13275 | 0.009155 | 0.09613 | -0.22431 | -0.091553 | -0.059509 | 122.8775 | 122.9874 | 58.1406 | -122.9645 | 122.9095 | 122.8409 | 58.2413 | -123.0331
306.8438 | 123.1247 | -58.2047 | 64.769 | 0.18289 | 0.021614 | 0.064947 | 0.0066808 | 0.066466 | 0.017205 | 0.0056548 | 0.031556 | 0.003288 | 0.081203 | 0.057788 | 0.0086079 | -0.011634 | 64.7827 | -58.1909 | -0.059509 | -58.3923 | 64.7827 | -58.223 | -58.255 | -58.1772 | -0.018311 | -58.5114 | 64.801 | 64.7415 | -58.2504 | -58.342 | -0.01831 | -0.050354 | 0.013733 | 0.013733 | -0.18768 | -0.13733 | 0.013733 | -0.045776 | -0.13733 | 0.032043 | 0.027466 | -0.3067 | -0.16937 | -0.027466 | 122.9874 | 122.9874 | 58.1451 | -123.024 | 123.0057 | 122.9462 | 58.1863 | -123.111
307.8438 | 123.1155 | -58.2367 | 64.7598 | 0.13711 | 0.030158 | 0.068151 | 0.012022 | 0.056853 | 0.0033197 | 0.0024508 | 0.18414 | -0.005257 | 0.063046 | 0.069538 | -0.0063461 | -0.0062931 | 64.7278 | -58.2687 | -0.13733 | -58.4427 | 64.7781 | -58.255 | -58.2687 | -58.1726 | -0.064087 | -58.5251 | 64.8056 | 64.7598 | -58.2321 | -58.3557 | -0.018311 | -0.032044 | 0.01831 | -0.032044 | -0.20599 | -0.17395 | -0.032044 | 0.004577 | -0.11902 | 0.045776 | 0.064087 | -0.28839 | -0.16937 | 0 | 123.0148 | 122.9645 | 58.0994 | -123.0286 | 123.0423 | 122.9965 | 58.1726 | -123.1155
308.8438 | 123.2025 | -58.1726 | 64.7415 | 0.45754 | -0.013634 | 0.0799 | -0.015749 | 0.060057 | -0.023383 | -0.0050262 | 0.58087 | -0.011666 | 0.050228 | 0.059925 | 0.0021989 | 0.0086599 | 64.7964 | -58.0994 | -0.018311 | -58.3786 | 64.7003 | -58.2047 | -58.2596 | -58.0994 | 0.032043 | -58.4015 | 64.7415 | 64.6912 | -58.2092 | -58.3054 | -0.032044 | -0.086976 | -0.041199 | 0.073242 | -0.20599 | -0.11902 | 0.054932 | -0.036622 | -0.13275 | 0 | 0.073242 | -0.22888 | -0.09613 | -0.050354 | 122.8729 | 122.9691 | 58.1543 | -123.0011 | 122.9141 | 122.8638 | 58.2047 | -123.0469
309.8438 | 123.1338 | -58.2092 | 64.8056 | 0.25918 | 0.025886 | 0.070287 | 0.01843 | 0.065398 | 0.0075917 | 0.00031381 | 0.046815 | -0.00098395 | 0.061977 | 0.03963 | 0.015017 | -0.021247 | 64.801 | -58.1818 | -0.07782 | -58.3969 | 64.7552 | -58.2275 | -58.2596 | -58.1772 | -0.018311 | -58.4976 | 64.8239 | 64.7324 | -58.2367 | -58.3466 | -0.01831 | -0.050354 | -0.050354 | 0.027466 | -0.18768 | -0.13733 | -0.004578 | -0.027465 | -0.13733 | 0.018311 | 0.032044 | -0.28839 | -0.15106 | -0.073242 | 122.9645 | 123.0103 | 58.1314 | -123.0652 | 123.0331 | 122.9416 | 58.1909 | -123.1522
310.8438 | 123.111 | -58.2047 | 64.7736 | 0.2134 | 0.018409 | 0.075628 | 0.020567 | 0.071807 | 0.0097277 | 0.0077908 | 0.046815 | -0.017006 | 0.050228 | 0.069538 | -0.0020731 | -0.0030891 | 64.7964 | -58.1497 | -0.027466 | -58.3969 | 64.7873 | -58.2001 | -58.2596 | -58.1589 | 0 | -58.4976 | 64.8193 | 64.7141 | -58.2367 | -58.3328 | 0.004578 | -0.054932 | 0.013732 | 0.054932 | -0.19226 | -0.13733 | 0.022888 | -0.032043 | -0.12817 | 0.045776 | 0.045776 | -0.29297 | -0.16479 | -0.05951 | 122.9919 | 123.0011 | 58.1772 | -123.0331 | 123.024 | 122.9187 | 58.2047 | -123.1064
311.8438 | 123.1567 | -58.1772 | 64.7781 | 0.030298 | 0.038703 | 0.072424 | 0.01843 | 0.058989 | 0.0075917 | -0.0092992 | -0.075256 | -0.006325 | 0.063046 | 0.065265 | -0.0020731 | -0.0073621 | 64.8331 | -58.1085 | 0.004578 | -58.3694 | 64.7781 | -58.2138 | -58.2413 | -58.1131 | 0.09613 | -58.4427 | 64.8148 | 64.7232 | -58.2001 | -58.3054 | -0.036621 | -0.064087 | 0 | 0.068664 | -0.19226 | -0.12817 | 0.054932 | -0.022888 | -0.12817 | 0.036621 | 0.064087 | -0.2655 | -0.13733 | -0.054931 | 122.9553 | 123.0103 | 58.1818 | -123.0194 | 122.9919 | 122.9004 | 58.2733 | -123.0835
312.8438 | 123.175 | -58.1955 | 64.7964 | -0.12229 | 0.013069 | 0.072424 | 0.015226 | 0.065398 | 0.0043877 | -0.0018222 | -0.27362 | -0.002053 | 0.06625 | 0.058857 | 0.0086079 | -0.0041571 | 64.8056 | -58.0994 | 0.022888 | -58.342 | 64.7781 | -58.1863 | -58.223 | -58.1223 | 0.082397 | -58.429 | 64.8102 | 64.7186 | -58.223 | -58.287 | 0.009156 | -0.027465 | -0.018311 | 0.096131 | -0.14648 | -0.11902 | 0.009155 | -0.027465 | -0.091552 | 0.013733 | 0.073243 | -0.23346 | -0.14191 | -0.07782 | 122.9736 | 123.0011 | 58.2184 | -123.0194 | 123.0057 | 122.9141 | 58.2779 | -123.0835
313.8438 | 123.175 | -58.1772 | 64.8056 | 0.076074 | 0.0098641 | 0.073492 | 0.0088168 | 0.058989 | -0.0030893 | -0.00075419 | -0.029479 | 0.004356 | 0.063046 | 0.053516 | 0.010744 | -0.0052251 | 64.8102 | -58.0994 | 0.004578 | -58.3649 | 64.7827 | -58.2092 | -58.2504 | -58.1085 | 0.064087 | -58.4427 | 64.8331 | 64.7324 | -58.223 | -58.3282 | -0.032044 | -0.073242 | -0.022888 | 0.07782 | -0.18768 | -0.11444 | 0.004578 | -0.045776 | -0.15106 | 0.027466 | 0.068664 | -0.2655 | -0.11444 | -0.073242 | 122.9599 | 122.9874 | 58.1818 | -123.056 | 123.0103 | 122.9095 | 58.2413 | -123.1338
314.8438 | 123.1338 | -58.168 | 64.7964 | 0.030298 | 0.031227 | 0.07456 | 0.0098848 | 0.06967 | 0.0065237 | 0.0013818 | -0.22784 | 0.005424 | 0.055569 | 0.07381 | -0.0031411 | -0.0084301 | 64.8468 | -58.1589 | -0.032043 | -58.3694 | 64.769 | -58.223 | -58.2687 | -58.1268 | 0.054932 | -58.4702 | 64.8193 | 64.7278 | -58.2184 | -58.3282 | -0.054931 | -0.10071 | -0.027466 | 0.009155 | -0.20142 | -0.10071 | 0.050354 | -0.050354 | -0.16022 | 0.022888 | 0.041199 | -0.30212 | -0.14191 | -0.068665 | 122.937 | 123.0148 | 58.136 | -123.0652 | 122.9874 | 122.8958 | 58.223 | -123.1247
315.8438 | 123.2208 | -58.1726 | 64.7324 | 0.51858 | 0.0077281 | 0.07456 | -0.017886 | 0.042967 | -0.035132 | -0.012503 | 0.4588 | -0.013802 | 0.053432 | 0.062061 | -0.0042101 | 0.0033199 | 64.9017 | -58.0215 | 0.036621 | -58.3374 | 64.7415 | -58.1863 | -58.2413 | -58.0948 | 0.086975 | -58.3786 | 64.7552 | 64.7232 | -58.2138 | -58.3145 | -0.013733 | -0.068665 | 0.009155 | 0.15106 | -0.16479 | -0.09613 | 0.16937 | -0.041199 | -0.14191 | 0.022888 | 0.077819 | -0.20599 | -0.064087 | -0.009155 | 122.9141 | 123.0743 | 58.2092 | -122.9736 | 122.9279 | 122.8958 | 58.2596 | -123.0469
316.8438 | 123.1476 | -58.1726 | 64.7827 | -0.10703 | 0.021614 | 0.069219 | 0.017362 | 0.055785 | 0.0033197 | -0.011435 | -0.16681 | 0.003288 | 0.048092 | 0.055652 | 0.0054039 | -0.011634 | 64.8422 | -58.1223 | 0 | -58.3603 | 64.7964 | -58.2138 | -58.2367 | -58.1223 | 0.068665 | -58.4244 | 64.8193 | 64.7644 | -58.2092 | -58.3099 | -0.041199 | -0.064087 | 0.013733 | 0.050354 | -0.18768 | -0.1236 | 0.059509 | -0.036622 | -0.13733 | 0.036621 | 0.050354 | -0.25177 | -0.11444 | -0.018311 | 122.9691 | 123.0148 | 58.1726 | -123.0194 | 122.9919 | 122.937 | 58.2413 | -123.0927
317.8438 | 123.2025 | -58.1863 | 64.7919 | -0.10703 | 0.021614 | 0.089513 | 0.0024088 | 0.067534 | 0.0022517 | 0.00031381 | -0.28888 | -0.004189 | 0.060909 | 0.046039 | 0.0075399 | -0.01377 | 64.8193 | -58.1177 | 0.004578 | -58.3832 | 64.7873 | -58.2001 | -58.2596 | -58.1131 | 0.07782 | -58.4427 | 64.8193 | 64.7552 | -58.2138 | -58.3328 | -0.013733 | -0.073243 | -0.004578 | 0.068664 | -0.19684 | -0.1236 | 0.027466 | -0.027466 | -0.14648 | 0.027466 | 0.073242 | -0.25635 | -0.10986 | -0.036621 | 122.9736 | 123.0057 | 58.1909 | -123.0515 | 123.0057 | 122.9416 | 58.2642 | -123.1247
318.8438 | 123.1018 | -58.1635 | 64.801 | -0.27488 | 0.00025114 | 0.066015 | 0.0024088 | 0.062194 | -0.023383 | -0.0071622 | 0.0010378 | -0.008461 | 0.059841 | 0.059925 | 6.2882e-05 | -0.0052251 | 64.9612 | -58.2642 | -0.10071 | -58.4656 | 64.7873 | -58.2321 | -58.2733 | -58.1497 | 0.045776 | -58.4839 | 64.8422 | 64.7598 | -58.223 | -58.3145 | -0.068665 | -0.10986 | -0.013733 | -0.10071 | -0.30212 | -0.19226 | 0.16022 | -0.059509 | -0.15106 | 0.041199 | 0.013733 | -0.32044 | -0.16937 | -0.041198 | 122.9507 | 123.1247 | 58.0627 | -123.0743 | 123.0057 | 122.9233 | 58.2092 | -123.1155
319.8438 | 123.1247 | -58.1955 | 64.8102 | -0.3054 | 0.0034561 | 0.078832 | 0.0056128 | 0.06433 | -0.020179 | -0.0018222 | -0.25836 | -0.004189 | 0.059841 | 0.054584 | -0.0020731 | -0.011634 | 64.7827 | -58.1451 | -0.018311 | -58.3923 | 64.8239 | -58.2092 | -58.255 | -58.1589 | 0.16022 | -58.3237 | 64.8605 | 64.8056 | -58.1772 | -58.3008 | -0.013733 | -0.059509 | 0.013733 | 0.050354 | -0.19684 | -0.13733 | -0.027466 | 0.018311 | -0.10529 | 0.050354 | 0.036621 | -0.12817 | -0.022888 | -0.004578 | 123.0194 | 122.9782 | 58.1772 | -123.0652 | 123.056 | 123.0011 | 58.3557 | -123.111
320.8438 | 123.1338 | -58.1589 | 64.8193 | -0.16807 | 0.025886 | 0.076696 | 0.010954 | 0.063262 | -0.010566 | -0.0018222 | -0.25836 | -0.002053 | 0.064114 | 0.059925 | 0.0096759 | -0.020179 | 64.8056 | -58.1268 | -0.004578 | -58.3694 | 64.8102 | -58.2184 | -58.2504 | -58.1314 | 0.07782 | -58.4381 | 64.8331 | 64.7781 | -58.2138 | -58.3282 | -0.059509 | -0.091552 | -0.009155 | 0.032044 | -0.21057 | -0.11902 | -0.013733 | -0.054931 | -0.16937 | 0.013733 | 0.027466 | -0.27923 | -0.10986 | -0.041199 | 122.9691 | 122.9645 | 58.1543 | -123.0698 | 122.9919 | 122.937 | 58.2367 | -123.1476
321.8438 | 123.1522 | -58.1635 | 64.8102 | -0.18333 | 0.022682 | 0.073492 | 0.016294 | 0.06433 | -0.0030893 | -0.0039582 | -0.25836 | 8.4049e-05 | 0.051296 | 0.064197 | 0.0075399 | -0.01377 | 64.7736 | -58.1497 | -0.009155 | -58.3786 | 64.7827 | -58.223 | -58.2321 | -58.1589 | 0.064087 | -58.4518 | 64.8422 | 64.7873 | -58.2001 | -58.3237 | -0.059509 | -0.068665 | -0.027466 | 0.013733 | -0.21515 | -0.14648 | -0.036621 | -0.036621 | -0.16022 | 0.032043 | 0.004577 | -0.28839 | -0.12817 | -0.022889 | 122.9462 | 122.937 | 58.1543 | -123.0423 | 123.0057 | 122.9507 | 58.2275 | -123.1338
322.8438 | 123.1293 | -58.2092 | 64.8102 | -0.25962 | 0.0098641 | 0.068151 | 0.0098848 | 0.055785 | -0.014838 | -0.010367 | -0.18207 | -0.005257 | 0.061977 | 0.046039 | -0.0084821 | -0.0073621 | 64.7003 | -58.2413 | -0.082397 | -58.429 | 64.7873 | -58.223 | -58.2596 | -58.1635 | 0.050354 | -58.4976 | 64.8331 | 64.7781 | -58.223 | -58.3328 | -0.013732 | -0.050354 | -0.022889 | -0.032043 | -0.21973 | -0.16937 | -0.10986 | -0.013732 | -0.1236 | 0.022888 | 0.045777 | -0.28839 | -0.16479 | -0.032044 | 122.9965 | 122.9095 | 58.1268 | -123.0698 | 123.0423 | 122.9874 | 58.2596 | -123.143
323.8438 | 123.0835 | -58.1818 | 64.7827 | -0.29014 | 0.015205 | 0.082037 | 0.014158 | 0.057921 | -0.014838 | -0.016776 | -0.25836 | 0.003288 | 0.040615 | 0.070606 | -0.0042101 | -0.0041571 | 64.7736 | -58.1497 | -0.022888 | -58.4015 | 64.8376 | -58.2092 | -58.2275 | -58.1589 | 0.045776 | -58.3923 | 64.856 | 64.8193 | -58.168 | -58.2825 | -0.027466 | -0.045776 | 0.054931 | 0.032044 | -0.21973 | -0.17395 | -0.009155 | 0.013733 | -0.10071 | 0.073242 | 0.022888 | -0.21057 | -0.10986 | 0.036621 | 123.0194 | 122.9553 | 58.1589 | -123.0103 | 123.0377 | 123.0011 | 58.2275 | -123.0652
324.8438 | 123.1476 | -58.1818 | 64.8102 | -0.015478 | 0.0045241 | 0.071355 | -0.0040002 | 0.060057 | -0.020179 | -0.0092992 | -0.27362 | -0.010597 | 0.073727 | 0.060993 | -0.0042101 | -0.0052251 | 64.8148 | -58.1451 | -0.018311 | -58.3878 | 64.7736 | -58.1909 | -58.2504 | -58.1451 | 0.059509 | -58.461 | 64.8376 | 64.801 | -58.2184 | -58.3237 | -0.009155 | -0.068664 | -0.036621 | 0.036621 | -0.20599 | -0.13733 | 0.004577 | -0.036621 | -0.14191 | 0.027465 | 0.036621 | -0.27924 | -0.13733 | -0.009156 | 122.9553 | 122.9965 | 58.1635 | -123.0606 | 123.0194 | 122.9828 | 58.2413 | -123.1338
325.8438 | 123.2529 | -58.1543 | 64.7781 | 2.7158 | 0.0045241 | 0.07456 | 0.0034768 | 0.06433 | -0.019111 | -0.014639 | -0.029479 | -0.009529 | 0.061977 | 0.063129 | -0.0095501 | -0.010566 | 64.8056 | -58.0444 | 0.059509 | -58.3099 | 64.7644 | -58.1635 | -58.2321 | -58.0719 | 0.16937 | -58.3466 | 64.8056 | 64.7095 | -58.1726 | -58.2733 | -0.009155 | -0.07782 | -0.013733 | 0.10986 | -0.15564 | -0.07782 | 0.027466 | -0.01831 | -0.11902 | 0.027466 | 0.082398 | -0.19226 | -0.073243 | -0.068664 | 122.9187 | 122.9599 | 58.2138 | -123.0103 | 122.9599 | 122.8638 | 58.3237 | -123.0515
326.8438 | 123.2025 | -58.1497 | 64.769 | -0.18333 | -0.014702 | 0.078832 | 0.0034768 | 0.05258 | -0.018043 | -0.01998 | -0.075256 | -0.003121 | 0.051296 | 0.057788 | 0.0075399 | -0.0094981 | 64.8651 | -58.0124 | 0.10071 | -58.3191 | 64.7507 | -58.1589 | -58.1863 | -58.0765 | 0.091553 | -58.3282 | 64.769 | 64.6912 | -58.1772 | -58.3008 | -0.009156 | -0.036621 | -0.018311 | 0.13733 | -0.16937 | -0.13275 | 0.09613 | -0.027466 | -0.15106 | 0 | 0.073242 | -0.17853 | -0.027466 | -0.07782 | 122.9004 | 123.0148 | 58.2504 | -122.9553 | 122.9187 | 122.8409 | 58.2413 | -123.0698
327.8438 | 123.1476 | -58.1223 | 64.8514 | -0.27488 | -0.014702 | 0.073492 | 0.0098848 | 0.058989 | 0.00011475 | -0.014639 | -0.25836 | -0.01487 | 0.044888 | 0.041767 | -0.0052781 | -0.015907 | 64.8331 | -58.0673 | 0.050354 | -58.3466 | 64.7919 | -58.1955 | -58.2092 | -58.1314 | 0.064087 | -58.4564 | 64.8331 | 64.7186 | -58.223 | -58.3008 | -0.073243 | -0.086976 | -0.059509 | 0.054931 | -0.22431 | -0.13733 | -0.01831 | -0.10071 | -0.17853 | -0.01831 | -0.009156 | -0.33417 | -0.15564 | -0.13275 | 122.9141 | 122.9553 | 58.1726 | -123.0606 | 122.9553 | 122.8409 | 58.1863 | -123.1522
328.8438 | 123.1796 | -58.1314 | 64.7873 | -0.24436 | -0.021111 | 0.090582 | 0.0098848 | 0.051512 | -0.010566 | -0.0050262 | -0.22784 | -0.012734 | 0.052364 | 0.053516 | -0.0042101 | -0.0052251 | 64.8468 | -58.0307 | 0.07782 | -58.3145 | 64.7919 | -58.1863 | -58.2138 | -58.0765 | 0.13275 | -58.3786 | 64.8102 | 64.7369 | -58.1772 | -58.3008 | -0.054931 | -0.082397 | 0.004578 | 0.10071 | -0.18311 | -0.10071 | 0.05951 | -0.045776 | -0.16937 | 0.022889 | 0.054932 | -0.24719 | -0.07782 | -0.050354 | 122.9233 | 122.9782 | 58.2092 | -123.0011 | 122.9416 | 122.8683 | 58.2642 | -123.0881
329.8438 | 123.2025 | -58.136 | 64.7873 | -0.16807 | -0.013634 | 0.071355 | 0.023771 | 0.057921 | 0.0033197 | -0.00075419 | -0.044738 | -0.018074 | 0.029934 | 0.060993 | -0.0063461 | -0.011634 | 64.6362 | -58.0215 | 0.045776 | -58.342 | 64.7369 | -58.1955 | -58.2047 | -58.0627 | 0.17853 | -58.3557 | 64.8102 | 64.7003 | -58.1772 | -58.2825 | -0.05951 | -0.068665 | -0.050354 | 0.11444 | -0.20599 | -0.13733 | -0.15106 | -0.041199 | -0.14648 | 0.022889 | 0.073242 | -0.21973 | -0.073242 | -0.086975 | 122.8729 | 122.7722 | 58.1818 | -122.9919 | 122.9462 | 122.8363 | 58.3145 | -123.0698
330.8438 | 123.1384 | -58.0948 | 64.769 | -0.21384 | -0.023247 | 0.086309 | 0.015226 | 0.058989 | -0.019111 | -0.0071622 | -0.21259 | -0.02021 | 0.050228 | 0.05672 | -0.0031411 | -0.024451 | 64.8697 | -57.9895 | 0.086975 | -58.3191 | 64.7736 | -58.1955 | -58.2001 | -58.0261 | 0.17853 | -58.3466 | 64.8102 | 64.6774 | -58.1589 | -58.2596 | -0.10071 | -0.10529 | 0.004578 | 0.10529 | -0.2243 | -0.11902 | 0.10071 | -0.064087 | -0.16479 | 0.041199 | 0.068665 | -0.25177 | -0.086975 | -0.091553 | 122.8683 | 122.9645 | 58.1818 | -122.9691 | 122.905 | 122.7722 | 58.2733 | -123.0286
331.8438 | 123.2437 | -58.1223 | 64.7598 | -0.015478 | -0.012566 | 0.07456 | 0.0088168 | 0.053649 | -0.014838 | -0.013571 | -0.22784 | -0.026619 | 0.041683 | 0.063129 | -0.0074141 | -0.0030891 | 64.8605 | -58.0215 | 0.068665 | -58.3237 | 64.7736 | -58.2001 | -58.2138 | -58.0032 | 0.19684 | -58.3099 | 64.7598 | 64.7049 | -58.1818 | -58.2733 | -0.07782 | -0.091553 | 0.013733 | 0.10071 | -0.20142 | -0.10986 | 0.10071 | -0.05951 | -0.15106 | 0 | 0.11902 | -0.18768 | -0.036622 | -0.054932 | 122.8958 | 122.9828 | 58.1909 | -122.9736 | 122.8821 | 122.8271 | 58.3191 | -123.0331
332.8438 | 123.2071 | -58.1589 | 64.769 | 0.16763 | -0.029656 | 0.068151 | 0.012022 | 0.062194 | -0.0052253 | -0.0050262 | 0.077332 | -0.008461 | 0.052364 | 0.05138 | -0.0084821 | -0.0062931 | 64.9155 | -58.1268 | -0.004578 | -58.3649 | 64.769 | -58.1863 | -58.2184 | -58.0948 | 0.041199 | -58.429 | 64.769 | 64.6774 | -58.1726 | -58.3099 | -0.027465 | -0.059509 | 0 | 0.032044 | -0.20599 | -0.14648 | 0.14648 | -0.013732 | -0.15106 | 0 | 0.064087 | -0.27008 | -0.11902 | -0.091553 | 122.9279 | 123.0743 | 58.1543 | -122.9874 | 122.9279 | 122.8363 | 58.2001 | -123.0789
333.8438 | 123.2117 | -58.1772 | 64.7461 | 0.24392 | 0.0066601 | 0.066015 | -0.00079616 | 0.056853 | -0.0094983 | -0.017844 | 0.24518 | -0.018074 | 0.047024 | 0.055652 | 0.0011309 | -0.0052251 | 64.7919 | -58.0948 | -0.018311 | -58.3649 | 64.7598 | -58.1863 | -58.2184 | -58.0856 | 0.027466 | -58.4335 | 64.7919 | 64.6774 | -58.2047 | -58.3145 | -0.009155 | -0.041199 | 0.013733 | 0.082397 | -0.18768 | -0.14648 | 0.045776 | -0.027466 | -0.13733 | 0.045776 | 0.091553 | -0.25635 | -0.11902 | -0.068665 | 122.937 | 122.9691 | 58.1589 | -122.9645 | 122.9691 | 122.8546 | 58.2047 | -123.0606
334.8438 | 123.2483 | -58.1543 | 64.7507 | 0.030298 | -0.028588 | 0.075628 | 0.0013408 | 0.054717 | -0.012702 | -0.024252 | 0.031556 | -0.011666 | 0.053432 | 0.058857 | -0.0031411 | -0.019111 | 64.8285 | -58.0582 | 0 | -58.342 | 64.7461 | -58.1818 | -58.2275 | -58.0444 | 0.10529 | -58.3694 | 64.769 | 64.6866 | -58.1818 | -58.287 | -0.027466 | -0.073242 | -0.004577 | 0.09613 | -0.18768 | -0.11444 | 0.07782 | -0.027466 | -0.13275 | 0.018311 | 0.10986 | -0.21515 | -0.082398 | -0.064087 | 122.9004 | 122.9828 | 58.1543 | -122.9782 | 122.9233 | 122.8409 | 58.2596 | -123.0377
335.8438 | 123.2025 | -58.1451 | 64.7461 | 0.22866 | -0.022179 | 0.086309 | 0.0024088 | 0.048308 | 0.0054557 | -0.012503 | 0.26044 | -0.005257 | 0.054501 | 0.050312 | 0.0086079 | -0.0073621 | 64.7781 | -58.0719 | -0.013733 | -58.374 | 64.7644 | -58.1909 | -58.2275 | -58.0765 | 0.073242 | -58.4061 | 64.7781 | 64.6591 | -58.1863 | -58.2916 | -0.045776 | -0.082397 | 0.01831 | 0.073243 | -0.22888 | -0.14648 | 0.032043 | -0.041198 | -0.14648 | 0.032043 | 0.068665 | -0.26093 | -0.11444 | -0.086975 | 122.9095 | 122.9233 | 58.1314 | -122.9736 | 122.9233 | 122.8043 | 58.2184 | -123.0377
336.8438 | 123.2574 | -58.1497 | 64.7552 | 0.24392 | -0.023247 | 0.072424 | -0.0072042 | 0.046172 | -0.0094983 | -0.015707 | 0.1994 | -0.021279 | 0.039547 | 0.058857 | 0.01288 | -0.016975 | 64.8102 | -58.0856 | -0.036621 | -58.3786 | 64.7415 | -58.1772 | -58.2321 | -58.0948 | 0.032043 | -58.4244 | 64.7781 | 64.6729 | -58.2092 | -58.2962 | -0.027466 | -0.082398 | -0.013733 | 0.064087 | -0.22888 | -0.14648 | 0.054932 | -0.05951 | -0.14649 | 0.022888 | 0.054931 | -0.27466 | -0.12817 | -0.082397 | 122.8912 | 122.9599 | 58.1131 | -122.9874 | 122.9279 | 122.8226 | 58.1818 | -123.0515
337.8438 | 123.1796 | -58.1589 | 64.7552 | 0.33547 | 0.0023871 | 0.07456 | 0.016294 | 0.068602 | -0.0020213 | -0.013571 | 0.24518 | -0.007393 | 0.039547 | 0.050312 | -0.0031411 | -0.019111 | 64.8239 | -58.1039 | -0.054932 | -58.3786 | 64.7598 | -58.2047 | -58.255 | -58.0719 | 0.027466 | -58.429 | 64.7781 | 64.682 | -58.2047 | -58.2779 | -0.045776 | -0.09613 | 0.004578 | 0.054932 | -0.21973 | -0.1236 | 0.068665 | -0.045776 | -0.11902 | 0.022888 | 0.086976 | -0.27008 | -0.15106 | -0.073242 | 122.9187 | 122.9828 | 58.1039 | -123.0103 | 122.937 | 122.8409 | 58.1863 | -123.0331
338.8438 | 123.2117 | -58.1497 | 64.7049 | 0.44228 | -0.0082939 | 0.071355 | 0.0013408 | 0.062194 | 0.0011837 | -0.0082312 | 0.36725 | -0.017006 | 0.04916 | 0.053516 | 0.0021989 | -0.016975 | 64.8468 | -58.0673 | -0.013733 | -58.3603 | 64.7049 | -58.1909 | -58.2413 | -58.0582 | 0.018311 | -58.4335 | 64.7507 | 64.6683 | -58.1909 | -58.2962 | -0.041199 | -0.091553 | 0 | 0.082397 | -0.21057 | -0.11902 | 0.14191 | -0.041199 | -0.14649 | 0.045776 | 0.091552 | -0.28381 | -0.13733 | -0.036621 | 122.8546 | 122.9965 | 58.136 | -122.9462 | 122.9004 | 122.818 | 58.168 | -123.0011
339.8438 | 123.2437 | -58.1451 | 64.7141 | 0.68643 | 0.010932 | 0.061742 | 0.0045448 | 0.055785 | 0.015069 | -0.0071622 | 0.33673 | -0.013802 | 0.052364 | 0.05672 | 0.0096759 | -0.015907 | 64.8605 | -58.0627 | -0.022888 | -58.3511 | 64.7232 | -58.2047 | -58.2504 | -58.0353 | 0.045776 | -58.4152 | 64.7369 | 64.6729 | -58.2047 | -58.2962 | -0.059509 | -0.10529 | 0.009156 | 0.082398 | -0.20599 | -0.10071 | 0.14648 | -0.059509 | -0.15106 | 0.022888 | 0.10986 | -0.27008 | -0.11902 | -0.041198 | 122.8683 | 123.0057 | 58.1223 | -122.9645 | 122.8821 | 122.818 | 58.1909 | -123.0103
340.8438 | 123.2162 | -58.1863 | 64.7186 | 0.56436 | 0.022682 | 0.062811 | 0.012022 | 0.06433 | 0.014001 | -0.0071622 | 0.33673 | -0.012734 | 0.058773 | 0.060993 | 0.015017 | -0.020179 | 64.8331 | -58.1131 | -0.07782 | -58.374 | 64.7552 | -58.2047 | -58.2642 | -58.0719 | 0 | -58.4061 | 64.7552 | 64.65 | -58.2184 | -58.3099 | -0.018311 | -0.07782 | 0.036621 | 0.073242 | -0.18768 | -0.10986 | 0.11444 | -0.032044 | -0.1236 | 0.036621 | 0.11444 | -0.21973 | -0.09613 | -0.068665 | 122.9416 | 123.0194 | 58.1085 | -122.9828 | 122.9416 | 122.8363 | 58.1863 | -123.0286
341.8438 | 123.2391 | -58.1497 | 64.7003 | 0.51858 | -0.0072259 | 0.066015 | -0.00079616 | 0.067534 | 0.00011475 | -0.00075419 | -0.45673 | -0.002053 | 0.052364 | 0.05138 | 0.0064719 | -0.020179 | 64.8514 | -58.0627 | -0.004578 | -58.3557 | 64.7186 | -58.2092 | -58.255 | -58.0536 | 0.073242 | -58.3923 | 64.7598 | 64.6774 | -58.2047 | -58.2962 | -0.05951 | -0.10529 | 0.018311 | 0.086975 | -0.20599 | -0.10071 | 0.15106 | -0.054932 | -0.14649 | 0.05951 | 0.09613 | -0.24262 | -0.09613 | -0.022888 | 122.8683 | 123.0011 | 58.1451 | -122.9553 | 122.9095 | 122.8271 | 58.223 | -122.9965
342.8438 | 123.2574 | -58.1635 | 64.7278 | 0.36599 | 0.014137 | 0.071355 | 0.0088168 | 0.066466 | 0.010797 | -0.0028902 | 0.41303 | -0.004189 | 0.061977 | 0.049243 | 0.0086079 | -0.0073621 | 64.8743 | -58.0765 | -0.022888 | -58.3374 | 64.7186 | -58.2047 | -58.2504 | -58.0536 | 0.050354 | -58.3878 | 64.7461 | 64.6591 | -58.2001 | -58.3099 | -0.041199 | -0.086975 | -0.009155 | 0.086975 | -0.17395 | -0.086975 | 0.14648 | -0.036621 | -0.14648 | 0.018311 | 0.10986 | -0.2243 | -0.077819 | -0.068664 | 122.8821 | 123.0377 | 58.1406 | -122.9782 | 122.9095 | 122.8226 | 58.2138 | -123.0377
343.8438 | 123.2346 | -58.1818 | 64.7324 | 0.5491 | 0.020545 | 0.072424 | 0.0066808 | 0.071807 | 0.016137 | 0.0013818 | 0.062074 | 8.4049e-05 | 0.042751 | 0.05138 | 0.015017 | -0.0062931 | 64.8102 | -58.1085 | -0.059509 | -58.3832 | 64.769 | -58.2047 | -58.2596 | -58.1085 | 0.018311 | -58.3923 | 64.7781 | 64.6729 | -58.2047 | -58.2916 | -0.022888 | -0.07782 | 0.036621 | 0.073242 | -0.20142 | -0.1236 | 0.07782 | -0.022888 | -0.10986 | 0.045776 | 0.073242 | -0.21057 | -0.10071 | -0.059509 | 122.9507 | 122.9919 | 58.1223 | -122.9919 | 122.9599 | 122.8546 | 58.2001 | -123.024
344.8438 | 123.175 | -58.1909 | 64.7415 | 0.4728 | 0.020545 | 0.07456 | 0.0098848 | 0.056853 | 0.014001 | 0.0024508 | 0.2757 | 0.001152 | 0.040615 | 0.050312 | 0.0075399 | -0.0052251 | 64.7873 | -58.1772 | -0.10071 | -58.3923 | 64.7964 | -58.2321 | -58.2779 | -58.0902 | -0.013733 | -58.4473 | 64.7964 | 64.6912 | -58.2001 | -58.3145 | -0.041199 | -0.086975 | 0.054932 | 0.013733 | -0.20142 | -0.11444 | 0.045776 | -0.009155 | -0.1236 | 0.054932 | 0.10071 | -0.25635 | -0.13275 | -0.050354 | 122.9874 | 122.9782 | 58.0902 | -123.0194 | 122.9874 | 122.8821 | 58.1772 | -123.056
345.8438 | 123.1201 | -58.1955 | 64.7598 | 0.35073 | 0.034431 | 0.061742 | 0.023771 | 0.06433 | 0.014001 | -0.0039582 | 0.42828 | 0.004356 | 0.065182 | 0.072742 | 0.010744 | -0.0084301 | 64.8102 | -58.2321 | -0.15564 | -58.429 | 64.7736 | -58.2321 | -58.2779 | -58.1223 | -0.054932 | -58.493 | 64.7873 | 64.7141 | -58.2138 | -58.342 | -0.036621 | -0.082397 | 0.013733 | -0.036621 | -0.23346 | -0.15106 | 0.050354 | -0.01831 | -0.14648 | 0.027465 | 0.073243 | -0.29755 | -0.15106 | -0.045777 | 122.9691 | 123.0057 | 58.0399 | -123.0377 | 122.9828 | 122.9095 | 58.1406 | -123.1018
346.8438 | 123.0881 | -58.2184 | 64.7964 | 0.18289 | 0.015205 | 0.069219 | 0.0098848 | 0.055785 | 0.011865 | 0.0067228 | 0.2757 | 0.005424 | 0.051296 | 0.052448 | 0.013948 | -0.0084301 | 64.7736 | -58.2001 | -0.09613 | -58.3923 | 64.7873 | -58.2184 | -58.3008 | -58.1726 | -0.082397 | -58.5342 | 64.7873 | 64.7461 | -58.2367 | -58.3511 | 0 | -0.082397 | -0.009156 | 0.018311 | -0.17395 | -0.091553 | -0.022888 | -0.01831 | -0.13275 | -0.009156 | 0.045777 | -0.31586 | -0.18311 | -0.050354 | 123.0057 | 122.9919 | 58.1223 | -123.0972 | 123.0057 | 122.9645 | 58.136 | -123.1476
347.8438 | 123.0972 | -58.2047 | 64.7827 | 0.41177 | 0.022682 | 0.070287 | 0.00027184 | 0.065398 | 0.0054557 | 0.0013818 | 0.2757 | 8.4049e-05 | 0.063046 | 0.066333 | -0.0010051 | -0.0041571 | 64.7552 | -58.2321 | -0.13275 | -58.4244 | 64.7919 | -58.2138 | -58.2596 | -58.168 | -0.059509 | -58.4976 | 64.8376 | 64.7324 | -58.223 | -58.3282 | -0.009155 | -0.054932 | 0.009155 | -0.027466 | -0.21973 | -0.16479 | -0.027466 | -0.01831 | -0.1236 | 0.054931 | 0.036621 | -0.29297 | -0.16937 | -0.050354 | 122.9965 | 122.9599 | 58.0719 | -123.0423 | 123.0423 | 122.937 | 58.1451 | -123.111
348.8438 | 123.1247 | -58.2047 | 64.7736 | 0.51858 | 0.022682 | 0.073492 | -0.00079616 | 0.055785 | 0.0097277 | -0.0028902 | 0.32147 | 0.001152 | 0.037411 | 0.052448 | 0.0043349 | 0.0086599 | 64.7507 | -58.2275 | -0.13275 | -58.4198 | 64.7919 | -58.223 | -58.2687 | -58.2047 | -0.39825 | -58.374 | 64.7644 | 64.7186 | -58.2001 | -58.3054 | -0.01831 | -0.064087 | 0.01831 | -0.022888 | -0.21515 | -0.15106 | -0.022889 | 0.004578 | -0.10071 | -0.009156 | 0 | -0.16937 | -0.068664 | -0.054932 | 122.9965 | 122.9553 | 58.0719 | -123.0423 | 122.9691 | 122.9233 | 57.8064 | -123.0789
349.8438 | 123.0881 | -58.2184 | 64.7736 | 0.35073 | 0.024818 | 0.067083 | 0.01309 | 0.056853 | 0.0043877 | 0.0035188 | 0.26044 | -0.007393 | 0.052364 | 0.052448 | 0.011812 | 0.0033199 | 64.7369 | -58.2413 | -0.14648 | -58.4244 | 64.7873 | -58.2275 | -58.2687 | -58.1543 | -0.068665 | -58.5022 | 64.8239 | 64.7186 | -58.255 | -58.3557 | -0.009155 | -0.050354 | 0.013732 | -0.022888 | -0.20599 | -0.15564 | -0.036622 | -0.036621 | -0.13733 | 0.050354 | 0.064087 | -0.28381 | -0.14648 | -0.054932 | 123.0057 | 122.9553 | 58.0719 | -123.0423 | 123.0423 | 122.937 | 58.1497 | -123.1293
350.8438 | 123.0789 | -58.2092 | 64.7964 | 0.27444 | 0.016273 | 0.068151 | 0.01309 | 0.051512 | -0.00095325 | 0.0077908 | 0.61139 | -0.00098395 | 0.060909 | 0.066333 | 0.0032669 | -0.0020211 | 64.7736 | -58.2138 | -0.09613 | -58.4152 | 64.7827 | -58.2184 | -58.2687 | -58.2001 | -0.059509 | -58.5297 | 64.8193 | 64.7507 | -58.2367 | -58.3282 | -0.009155 | -0.059509 | -0.013733 | -0.004577 | -0.20599 | -0.14648 | -0.022888 | -0.027465 | -0.11902 | 0.022888 | 0.009156 | -0.32043 | -0.20142 | -0.045777 | 122.9919 | 122.9828 | 58.1131 | -123.0652 | 123.0286 | 122.9599 | 58.1497 | -123.1247
351.8438 | 123.1155 | -58.1772 | 64.7781 | 0.13711 | 0.014137 | 0.061742 | 0.0088168 | 0.054717 | 0.010797 | -0.0018222 | 0.092591 | -0.005257 | 0.047024 | 0.060993 | 0.0011309 | -0.0073621 | 64.7644 | -58.1589 | -0.068665 | -58.3923 | 64.7644 | -58.2184 | -58.2779 | -58.1543 | 0 | -58.5022 | 64.8102 | 64.7552 | -58.2275 | -58.3191 | -0.041199 | -0.10071 | -0.013733 | 0.01831 | -0.21515 | -0.11444 | -0.013733 | -0.050354 | -0.14191 | 0.032044 | 0.022888 | -0.32501 | -0.18311 | -0.022888 | 122.9416 | 122.9416 | 58.1085 | -123.056 | 122.9874 | 122.9324 | 58.1772 | -123.0972
352.8438 | 123.1247 | -58.168 | 64.7827 | 0.24392 | 0.033363 | 0.070287 | 0.0088168 | 0.070738 | 0.0011837 | -0.0060942 | 0.15363 | -0.008461 | 0.047024 | 0.052448 | 0.0075399 | -0.0062931 | 64.8102 | -58.1451 | -0.041199 | -58.3832 | 64.8102 | -58.2001 | -58.2458 | -58.1497 | -0.004578 | -58.4747 | 64.8056 | 64.7598 | -58.2367 | -58.3145 | -0.032043 | -0.07782 | 0.027466 | 0.022888 | -0.21515 | -0.13733 | 0.027466 | -0.068664 | -0.14648 | 0.022888 | 0.018311 | -0.3067 | -0.16022 | -0.022888 | 122.9782 | 122.9782 | 58.1268 | -123.0286 | 122.9736 | 122.9279 | 58.1635 | -123.0972
353.8438 | 123.1247 | -58.1818 | 64.8148 | -0.061255 | 0.0087961 | 0.059606 | 0.019498 | 0.062194 | 0.0022517 | -0.0039582 | -0.075256 | -0.007393 | 0.065182 | 0.040699 | 0.0032669 | -0.0073621 | 64.8285 | -58.1223 | -0.009155 | -58.3649 | 64.7781 | -58.2047 | -58.2458 | -58.0994 | 0.07782 | -58.429 | 64.8056 | 64.7415 | -58.2092 | -58.2916 | -0.022888 | -0.064087 | -0.036621 | 0.05951 | -0.18311 | -0.11902 | 0.013733 | -0.027466 | -0.10986 | -0.009155 | 0.082398 | -0.24719 | -0.13733 | -0.073242 | 122.9599 | 123.0103 | 58.1726 | -123.0606 | 122.9874 | 122.9233 | 58.2596 | -123.1064
354.8438 | 123.1613 | -58.1635 | 64.7644 | 0.10659 | 0.019477 | 0.071355 | 0.014158 | 0.06433 | 0.0065237 | -0.0028902 | 0.0010378 | -0.003121 | 0.051296 | 0.049243 | 0.0064719 | -0.0073621 | 64.8285 | -58.1223 | 0.036621 | -58.5159 | 64.7644 | -58.2367 | -58.2367 | -58.1039 | 0.07782 | -58.4473 | 64.8102 | 64.7507 | -58.2184 | -58.3237 | -0.073242 | -0.073242 | 0 | 0.041199 | -0.35248 | -0.27924 | 0.064087 | -0.054932 | -0.16022 | 0.045777 | 0.059509 | -0.28381 | -0.1236 | -0.013733 | 122.9279 | 122.9919 | 58.2001 | -123.0011 | 122.9736 | 122.9141 | 58.2413 | -123.0881
355.8438 | 123.0972 | -58.1909 | 64.801 | 0.091333 | 0.021614 | 0.066015 | -0.00079616 | 0.06967 | 0.0043877 | -0.0071622 | 0.13837 | -0.004189 | 0.056637 | 0.06847 | 0.0064719 | -0.0062931 | 64.8148 | -58.1543 | -0.027466 | -58.3832 | 64.7919 | -58.2138 | -58.2733 | -58.1406 | 0.004578 | -58.4518 | 64.8056 | 64.7415 | -58.2138 | -58.3237 | -0.022888 | -0.082397 | -0.009155 | 0.036621 | -0.19226 | -0.10986 | 0.013733 | -0.022888 | -0.13275 | 0.004578 | 0.050354 | -0.26092 | -0.12817 | -0.059509 | 122.9828 | 123.0057 | 58.1635 | -123.0743 | 122.9965 | 122.9324 | 58.1955 | -123.1247
356.8438 | 123.143 | -58.1818 | 64.7827 | 0.13711 | 0.020545 | 0.067083 | 0.0088168 | 0.055785 | 0.0011837 | -0.0082312 | 0.046815 | -0.002053 | 0.060909 | 0.05672 | 0.0032669 | -0.0030891 | 64.7827 | -58.1223 | -0.009155 | -58.374 | 64.7827 | -58.1955 | -58.2733 | -58.136 | 0.041199 | -58.4518 | 64.8331 | 64.7644 | -58.2092 | -58.3237 | -0.013733 | -0.091552 | 0 | 0.05951 | -0.19226 | -0.10071 | 0 | -0.027466 | -0.14191 | 0.050354 | 0.045777 | -0.27008 | -0.12817 | -0.018311 | 122.9645 | 122.9645 | 58.1726 | -123.056 | 123.0148 | 122.9462 | 58.223 | -123.1064
357.8438 | 123.1476 | -58.1726 | 64.7919 | 0.030298 | 0.025886 | 0.067083 | 0.0098848 | 0.055785 | -0.0094983 | -0.010367 | -0.01422 | 0.013969 | 0.061977 | 0.064197 | -0.0031411 | -0.01377 | 64.8239 | -58.1131 | 0 | -58.374 | 64.7827 | -58.2047 | -58.2413 | -58.1406 | 0.082397 | -58.4335 | 64.8239 | 64.7324 | -58.2275 | -58.3145 | -0.032044 | -0.068665 | -0.009155 | 0.059509 | -0.20142 | -0.13275 | 0.032044 | -0.054932 | -0.14191 | 0.032044 | 0.032043 | -0.26093 | -0.11902 | -0.059509 | 122.9553 | 122.9965 | 58.1726 | -123.0331 | 122.9965 | 122.905 | 58.255 | -123.1064
358.8438 | 123.143 | -58.1818 | 64.7964 | -0.076513 | 0.010932 | 0.076696 | 0.0034768 | 0.062194 | -0.0030893 | -0.00075419 | -0.044738 | -0.002053 | 0.048092 | 0.05138 | -0.0052781 | -0.0030891 | 64.8285 | -58.1268 | 0 | -58.3511 | 64.769 | -58.2092 | -58.223 | -58.0994 | 0.07782 | -58.4061 | 64.8239 | 64.7461 | -58.2367 | -58.3145 | -0.027466 | -0.041198 | -0.027466 | 0.054932 | -0.16937 | -0.12817 | 0.032043 | -0.054931 | -0.13275 | 0.027466 | 0.082398 | -0.2243 | -0.091553 | -0.050354 | 122.9507 | 123.0103 | 58.1818 | -123.0194 | 123.0057 | 122.9279 | 58.2596 | -123.111
359.8438 | 123.1613 | -58.1589 | 64.8285 | -0.16807 | 0.035499 | 0.069219 | 0.023771 | 0.068602 | -0.0020213 | -0.0082312 | -0.22784 | -0.006325 | 0.063046 | 0.057788 | 0.0021989 | -0.0052251 | 64.7827 | -58.1314 | -0.018311 | -58.3603 | 64.8102 | -58.1863 | -58.2367 | -58.1451 | 0.068665 | -58.4244 | 64.8376 | 64.7827 | -58.2001 | -58.3237 | -0.027465 | -0.077819 | -0.01831 | 0.027466 | -0.20142 | -0.1236 | -0.045776 | -0.041198 | -0.16479 | 0.009155 | 0.013733 | -0.2655 | -0.10071 | -0.045776 | 122.9691 | 122.9416 | 58.1406 | -123.0652 | 122.9965 | 122.9416 | 58.2275 | -123.1522
360.8438 | 123.262 | -58.1635 | 64.7415 | 0.48806 | 0.022682 | 0.071355 | 0.014158 | 0.062194 | -0.025519 | -0.0071622 | 0.32147 | -0.01487 | 0.052364 | 0.062061 | 0.0086079 | -0.0030891 | 64.7095 | -58.1909 | 0 | -58.287 | 64.7003 | -58.1818 | -58.2092 | -58.0902 | 0.027466 | -58.3786 | 64.7644 | 64.6774 | -58.223 | -58.2962 | -0.018311 | -0.045777 | -0.041199 | -0.027466 | -0.1236 | -0.077819 | -0.032043 | -0.059509 | -0.13275 | 0.022888 | 0.073242 | -0.21515 | -0.082397 | -0.064087 | 122.8638 | 122.8729 | 58.1635 | -122.9507 | 122.9279 | 122.8409 | 58.1909 | -123.0377
361.8438 | 123.1659 | -58.168 | 64.7873 | -0.16807 | 0.016273 | 0.072424 | 0.021635 | 0.054717 | 0.0022517 | -0.014639 | -0.33466 | -0.006325 | 0.051296 | 0.062061 | 0.0086079 | -0.010566 | 64.801 | -58.1497 | -0.022888 | -58.374 | 64.8376 | -58.1909 | -58.2596 | -58.1268 | 0.073242 | -58.4335 | 64.8422 | 64.7644 | -58.2047 | -58.3008 | -0.022888 | -0.091553 | 0.050354 | 0.018311 | -0.20599 | -0.11444 | 0.013733 | -0.036621 | -0.13275 | 0.054932 | 0.041199 | -0.2655 | -0.13275 | -0.022888 | 123.0057 | 122.9691 | 58.1451 | -123.0469 | 123.0103 | 122.9324 | 58.2413 | -123.0881
362.8438 | 123.1476 | -58.1863 | 64.8056 | -0.15281 | 0.010932 | 0.062811 | -0.011477 | 0.068602 | 0.0011837 | -0.0018222 | -0.044738 | -0.00098395 | 0.073727 | 0.060993 | 0.0096759 | -0.012702 | 64.8148 | -58.1177 | 0.009155 | -58.3511 | 64.8285 | -58.1955 | -58.2275 | -58.1223 | 0.064087 | -58.4152 | 64.8148 | 64.7507 | -58.1955 | -58.3328 | -0.009156 | -0.041199 | 0.022888 | 0.068664 | -0.16479 | -0.1236 | 0.009155 | -0.009156 | -0.14648 | 0.009155 | 0.064087 | -0.22888 | -0.082397 | -0.054932 | 123.0148 | 123.0011 | 58.1955 | -123.0331 | 123.0011 | 122.937 | 58.2504 | -123.1384
363.8438 | 123.1705 | -58.1726 | 64.8056 | -0.19858 | 0.018409 | 0.067083 | 0.015226 | 0.056853 | -0.0020213 | -0.00075419 | -0.27362 | -0.003121 | 0.050228 | 0.05672 | 0.0032669 | -0.0020211 | 64.8102 | -58.1223 | -0.022888 | -58.3603 | 64.8102 | -58.1909 | -58.2504 | -58.1039 | 0.086975 | -58.429 | 64.8376 | 64.7873 | -58.2001 | -58.2962 | -0.018311 | -0.07782 | 0.004578 | 0.050354 | -0.18768 | -0.10986 | 0.004578 | -0.027466 | -0.1236 | 0.032043 | 0.068664 | -0.25635 | -0.13275 | -0.018311 | 122.9828 | 122.9828 | 58.1497 | -123.056 | 123.0103 | 122.9599 | 58.2596 | -123.1018
364.8438 | 123.1796 | -58.1863 | 64.8422 | -0.16807 | -0.00081686 | 0.072424 | 0.03018 | 0.056853 | -0.0030893 | -0.0082312 | -0.30414 | -0.00098395 | 0.054501 | 0.07381 | -0.0020731 | -0.0052251 | 64.7873 | -58.136 | -0.032043 | -58.3832 | 64.8056 | -58.1955 | -58.2321 | -58.1543 | 0.064087 | -58.4335 | 64.8514 | 64.7964 | -58.2275 | -58.3237 | -0.009156 | -0.045777 | -0.036621 | 0.050354 | -0.19684 | -0.15106 | -0.054932 | -0.041199 | -0.13733 | 0.009155 | 0.032043 | -0.24719 | -0.10986 | -0.045776 | 122.9919 | 122.9736 | 58.1543 | -123.0743 | 123.0377 | 122.9828 | 58.2504 | -123.1659
365.8438 | 123.2437 | -58.1589 | 64.7461 | 0.59487 | -0.0040209 | 0.07456 | 0.0034768 | 0.063262 | -0.0084293 | -0.015707 | 2.3356 | -0.010597 | 0.036343 | 0.050312 | -0.0010051 | 0.0022509 | 64.8148 | -58.0673 | -0.009155 | -58.3374 | 64.7141 | -58.2001 | -58.2367 | -58.0673 | 0.064087 | -58.3832 | 64.7507 | 64.6866 | -58.2092 | -58.2825 | -0.041198 | -0.077819 | -0.032044 | 0.091553 | -0.17853 | -0.10071 | 0.068664 | -0.050354 | -0.1236 | 0.004577 | 0.091553 | -0.2243 | -0.10071 | -0.05951 | 122.8729 | 122.9736 | 58.1497 | -122.9828 | 122.9095 | 122.8455 | 58.223 | -123.0286
366.8438 | 123.0972 | -58.1589 | 64.8239 | -0.32065 | -0.01043 | 0.0799 | 0.0013408 | 0.054717 | -0.022315 | -0.0082312 | -0.5025 | -0.012734 | 0.047024 | 0.052448 | -0.0063461 | -0.011634 | 64.8331 | -58.1039 | 0.018311 | -58.3511 | 64.7827 | -58.2001 | -58.2321 | -58.1223 | 0.073242 | -58.4335 | 64.8514 | 64.7873 | -58.1955 | -58.287 | -0.041198 | -0.073242 | -0.041199 | 0.054932 | -0.19226 | -0.11902 | 0.009155 | -0.036621 | -0.12817 | 0.027465 | 0.036622 | -0.27466 | -0.14648 | -0.036622 | 122.9416 | 122.9919 | 58.1772 | -123.056 | 123.0103 | 122.9462 | 58.2321 | -123.111
367.8438 | 123.1201 | -58.1543 | 64.8239 | -0.27488 | -0.0093619 | 0.082037 | 0.0056128 | 0.056853 | -0.014838 | -0.012503 | -0.18207 | -0.015938 | 0.036343 | 0.059925 | -0.0010051 | -0.016975 | 64.8422 | -58.0582 | 0.050354 | -58.3374 | 64.8056 | -58.168 | -58.2138 | -58.1085 | 0.11902 | -58.3969 | 64.8468 | 64.7644 | -58.1863 | -58.2916 | -0.013733 | -0.059509 | -0.018311 | 0.09613 | -0.1831 | -0.1236 | 0.01831 | -0.032043 | -0.13733 | 0.022888 | 0.045776 | -0.24262 | -0.10529 | -0.05951 | 122.9599 | 122.9965 | 58.2047 | -123.0377 | 123.0011 | 122.9187 | 58.2733 | -123.1155
368.8438 | 123.1155 | -58.1772 | 64.8056 | 0.22866 | 0.035499 | 0.07456 | 0.037656 | 0.062194 | 0.017205 | -0.0018222 | 0.031556 | 0.001152 | 0.056637 | 0.055652 | 0.0075399 | -0.015907 | 64.8056 | -58.1543 | -0.068665 | -58.3969 | 64.7919 | -58.2138 | -58.2504 | -58.1497 | -0.018311 | -58.4976 | 64.8331 | 64.7186 | -58.2184 | -58.3237 | -0.036621 | -0.073242 | -0.013733 | 0.022888 | -0.21973 | -0.14648 | 0 | -0.041199 | -0.14648 | 0.027466 | 0.027466 | -0.32043 | -0.17395 | -0.086975 | 122.9691 | 122.9828 | 58.1085 | -123.056 | 123.0103 | 122.8958 | 58.1589 | -123.1293
369.8438 | 123.1247 | -58.1497 | 64.8193 | -0.24436 | 0.0098641 | 0.07456 | -0.0018642 | 0.056853 | -0.0052253 | -0.0050262 | -0.34991 | -0.006325 | 0.063046 | 0.058857 | -0.0063461 | -0.011634 | 64.7873 | -58.136 | -0.013733 | -58.3832 | 64.8239 | -58.1955 | -58.2504 | -58.1314 | 0.054932 | -58.4335 | 64.8743 | 64.7781 | -58.2001 | -58.2916 | -0.045777 | -0.10071 | 0.004578 | 0.013733 | -0.23346 | -0.13275 | -0.032044 | -0.050354 | -0.14191 | 0.054932 | 0.01831 | -0.28381 | -0.14191 | -0.041199 | 122.9736 | 122.937 | 58.136 | -123.0698 | 123.024 | 122.9279 | 58.2047 | -123.111
370.8438 | 123.2391 | -58.1589 | 64.7415 | 0.56436 | 0.019477 | 0.063879 | 0.0034768 | 0.046172 | -0.0020213 | -0.0082312 | 0.55035 | -0.012734 | 0.054501 | 0.054584 | 0.0075399 | -0.0073621 | 64.8056 | -58.1268 | -0.086975 | -58.3969 | 64.7598 | -58.1955 | -58.2321 | -58.0719 | 0.022888 | -58.4518 | 64.7644 | 64.6774 | -58.2184 | -58.3282 | -0.036621 | -0.073242 | 0.018311 | 0.032044 | -0.23804 | -0.16479 | 0.064087 | -0.059509 | -0.16937 | 0.022888 | 0.086976 | -0.29297 | -0.1236 | -0.064087 | 122.9187 | 122.9645 | 58.0719 | -122.9736 | 122.9233 | 122.8363 | 58.1818 | -123.0698
371.8438 | 123.1293 | -58.1314 | 64.8422 | -0.27488 | -0.018975 | 0.080969 | 0.0077488 | 0.055785 | -0.015906 | -0.011435 | -0.19733 | -0.005257 | 0.038479 | 0.060993 | -0.0010051 | -0.012702 | 64.8422 | -58.0627 | 0.045776 | -58.3328 | 64.7919 | -58.1772 | -58.2275 | -58.1131 | 0.086975 | -58.4152 | 64.8422 | 64.7598 | -58.2001 | -58.2779 | -0.045776 | -0.09613 | -0.050354 | 0.068665 | -0.20142 | -0.10529 | 0 | -0.068664 | -0.14648 | 0 | 0.018311 | -0.28381 | -0.13733 | -0.082397 | 122.9233 | 122.9736 | 58.1772 | -123.0698 | 122.9736 | 122.8912 | 58.2184 | -123.1201
372.8438 | 123.1522 | -58.1451 | 64.8056 | -0.21384 | -0.025384 | 0.072424 | 0.0024088 | 0.05258 | -0.0062933 | -0.021048 | -0.19733 | -0.010597 | 0.054501 | 0.060993 | -0.013823 | -0.018043 | 64.856 | -57.9987 | 0.091553 | -58.3008 | 64.7644 | -58.1818 | -58.2047 | -58.0765 | 0.15106 | -58.3694 | 64.8102 | 64.7461 | -58.1863 | -58.2825 | -0.036621 | -0.059509 | -0.041199 | 0.14648 | -0.15564 | -0.09613 | 0.050354 | -0.041198 | -0.13733 | 0.004578 | 0.068665 | -0.2243 | -0.086975 | -0.059509 | 122.9095 | 123.0011 | 58.2367 | -123.0103 | 122.9553 | 122.8912 | 58.2962 | -123.0881
373.8438 | 123.2254 | -58.136 | 64.7827 | -0.015478 | -0.01043 | 0.075628 | -0.0018642 | 0.057921 | -0.03086 | -0.013571 | -0.090514 | -0.013802 | 0.064114 | 0.03963 | -0.0074141 | -0.0094981 | 64.8834 | -57.9575 | 0.11444 | -58.2962 | 64.7919 | -58.1589 | -58.2001 | -58.0353 | 0.19684 | -58.342 | 64.7827 | 64.7186 | -58.1635 | -58.2825 | -0.022889 | -0.064087 | 0.009155 | 0.17853 | -0.16022 | -0.096131 | 0.10071 | -0.027466 | -0.14648 | 0 | 0.10071 | -0.20599 | -0.059509 | -0.064087 | 122.9279 | 123.0194 | 58.2504 | -122.9828 | 122.9187 | 122.8546 | 58.3328 | -123.0652
374.8438 | 123.2437 | -58.1223 | 64.7781 | -0.030737 | -0.017907 | 0.076696 | 0.0066808 | 0.051512 | -0.016974 | -0.029593 | 0.0010378 | -0.023415 | 0.035275 | 0.059925 | -0.013823 | -0.01377 | 64.856 | -58.0032 | 0.059509 | -58.3054 | 64.7873 | -58.1818 | -58.1909 | -58.0032 | 0.1831 | -58.3145 | 64.7781 | 64.6774 | -58.168 | -58.2779 | -0.05951 | -0.068665 | 0.009155 | 0.11902 | -0.18311 | -0.11444 | 0.07782 | -0.045777 | -0.15564 | 0 | 0.11902 | -0.19226 | -0.036621 | -0.10071 | 122.9095 | 122.9782 | 58.1818 | -122.9691 | 122.9004 | 122.7997 | 58.3054 | -123.056
375.8438 | 123.1247 | -58.136 | 64.8102 | -0.12229 | 0.026954 | 0.066015 | 0.029112 | 0.067534 | 0.023614 | -0.0082312 | -0.56354 | -0.006325 | 0.058773 | 0.077014 | 0.0086079 | -0.019111 | 64.8514 | -58.0856 | 0.004578 | -58.3374 | 64.8239 | -58.2138 | -58.2504 | -58.0856 | 0.09613 | -58.429 | 64.8514 | 64.7369 | -58.1863 | -58.3237 | -0.07782 | -0.11444 | 0.013733 | 0.050354 | -0.20142 | -0.086975 | 0.041198 | -0.050354 | -0.18768 | 0.041198 | 0.050354 | -0.29297 | -0.10529 | -0.073243 | 122.9599 | 122.9874 | 58.1406 | -123.0606 | 122.9874 | 122.8729 | 58.2321 | -123.1338
376.8438 | 123.2254 | -58.0994 | 64.8056 | -0.16807 | -0.031792 | 0.072424 | -0.0072042 | 0.053649 | -0.014838 | -0.0092992 | 2.3967 | -0.005257 | 0.039547 | 0.05672 | -0.0031411 | -0.0052251 | 64.8743 | -57.9895 | 0.091553 | -58.2916 | 64.7827 | -58.1543 | -58.2184 | -57.9987 | 0.13733 | -58.3557 | 64.7964 | 64.6912 | -58.1726 | -58.2642 | -0.054932 | -0.11902 | -0.022888 | 0.10986 | -0.19226 | -0.073242 | 0.068665 | -0.073242 | -0.16479 | -0.009155 | 0.10071 | -0.25635 | -0.091553 | -0.11444 | 122.8821 | 122.9736 | 58.1909 | -123.024 | 122.8958 | 122.7905 | 58.2367 | -123.0698
377.8438 | 123.23 | -58.1085 | 64.7827 | -0.061255 | -0.012566 | 0.09165 | -0.00079616 | 0.051512 | -0.014838 | -0.015707 | -0.075256 | -0.019142 | 0.050228 | 0.059925 | 6.2882e-05 | -0.018043 | 64.8972 | -57.9391 | 0.11902 | -58.2916 | 64.7919 | -58.1543 | -58.2001 | -58.0078 | 0.1831 | -58.3237 | 64.8102 | 64.7095 | -58.168 | -58.2733 | -0.045776 | -0.091552 | 0.009155 | 0.16937 | -0.1831 | -0.091553 | 0.11444 | -0.059509 | -0.16479 | 0.027466 | 0.10071 | -0.21515 | -0.050354 | -0.073242 | 122.9004 | 123.0057 | 58.2275 | -122.9828 | 122.9187 | 122.818 | 58.2916 | -123.056
378.8438 | 123.2437 | -58.1223 | 64.7873 | 0.060816 | -0.034997 | 0.078832 | 0.0045448 | 0.06967 | -0.021247 | -0.01998 | -0.25836 | -0.025551 | 0.033138 | 0.058857 | 0.0032669 | -0.01377 | 64.8514 | -57.9849 | 0.068665 | -58.3145 | 64.769 | -58.1772 | -58.2001 | -57.9849 | 0.20599 | -58.3099 | 64.7827 | 64.7141 | -58.1726 | -58.2687 | -0.054932 | -0.07782 | -0.01831 | 0.13733 | -0.19226 | -0.11444 | 0.064087 | -0.050354 | -0.14648 | -0.004577 | 0.13733 | -0.18768 | -0.041199 | -0.073242 | 122.8912 | 122.9736 | 58.1909 | -122.9874 | 122.905 | 122.8363 | 58.3282 | -123.056
379.8438 | 123.2254 | -58.0902 | 64.7781 | -0.030737 | -0.021111 | 0.075628 | 0.012022 | 0.049376 | -0.015906 | -0.013571 | 0.062074 | -0.01487 | 0.058773 | 0.062061 | 0.0043349 | -0.0052251 | 64.856 | -58.0307 | 0.045776 | -58.3374 | 64.7827 | -58.1451 | -58.1909 | -58.0124 | 0.11902 | -58.3511 | 64.7964 | 64.6957 | -58.1863 | -58.2687 | -0.054932 | -0.10071 | 0.004578 | 0.059509 | -0.24719 | -0.14648 | 0.07782 | -0.09613 | -0.17853 | 0.018311 | 0.07782 | -0.26093 | -0.082397 | -0.082397 | 122.8729 | 122.9462 | 58.136 | -122.9691 | 122.8867 | 122.7859 | 58.2092 | -123.0469
380.8438 | 123.2025 | -58.1451 | 64.7781 | 0.2134 | -0.0093619 | 0.07456 | 0.01309 | 0.056853 | -0.016974 | -0.012503 | 0.13837 | -0.023415 | 0.04916 | 0.057788 | 0.0021989 | -0.0041571 | 64.8056 | -58.0902 | -0.032043 | -58.3603 | 64.769 | -58.1909 | -58.223 | -58.0994 | 0.073242 | -58.3969 | 64.7919 | 64.7003 | -58.168 | -58.2779 | -0.045776 | -0.077819 | -0.009155 | 0.054932 | -0.21515 | -0.13733 | 0.027466 | -0.022888 | -0.13275 | 0.013733 | 0.045777 | -0.25177 | -0.11902 | -0.07782 | 122.9141 | 122.9507 | 58.1131 | -123.0011 | 122.937 | 122.8455 | 58.2184 | -123.056
381.8438 | 123.2071 | -58.1543 | 64.7873 | 0.24392 | -0.021111 | 0.078832 | -0.0050682 | 0.046172 | -0.0094983 | -0.027457 | 0.26044 | -0.011666 | 0.045956 | 0.071674 | -0.0042101 | -0.0084301 | 64.8102 | -58.0811 | -0.045776 | -58.3603 | 64.7919 | -58.2001 | -58.2184 | -58.0811 | 0.041199 | -58.4198 | 64.7873 | 64.7095 | -58.1955 | -58.2825 | -0.045776 | -0.064087 | 0.004578 | 0.073242 | -0.20599 | -0.14191 | 0.022889 | -0.041199 | -0.12817 | 0 | 0.073242 | -0.2655 | -0.13733 | -0.077819 | 122.9462 | 122.9645 | 58.1085 | -123.0057 | 122.9416 | 122.8638 | 58.1955 | -123.0698
382.8438 | 123.2025 | -58.1177 | 64.7552 | 0.16763 | -0.022179 | 0.075628 | 0.0045448 | 0.060057 | -0.0020213 | -0.022116 | 0.077332 | -0.012734 | 0.043819 | 0.057788 | -0.0010051 | -0.015907 | 64.856 | -58.0536 | 0.027466 | -58.3282 | 64.7781 | -58.1772 | -58.2092 | -58.0124 | 0.11444 | -58.3374 | 64.7964 | 64.7095 | -58.168 | -58.2687 | -0.059509 | -0.091553 | 0.022888 | 0.064087 | -0.21057 | -0.11902 | 0.10071 | -0.050354 | -0.15106 | 0.041199 | 0.10529 | -0.21973 | -0.068664 | -0.045776 | 122.8958 | 122.9736 | 58.1451 | -122.9645 | 122.9141 | 122.8271 | 58.2321 | -123.024
383.8438 | 123.2346 | -58.1223 | 64.7552 | -0.030737 | -0.024315 | 0.0799 | 0.00027184 | 0.060057 | -0.0094983 | -0.016776 | 0.22992 | -0.025551 | 0.034206 | 0.062061 | -0.0052781 | -0.0052251 | 64.801 | -58.0811 | -0.032043 | -58.3511 | 64.7781 | -58.1772 | -58.2413 | -58.0399 | 0.073242 | -58.374 | 64.7964 | 64.6957 | -58.1772 | -58.2504 | -0.054932 | -0.11902 | 0.022888 | 0.041198 | -0.22888 | -0.10986 | 0.045776 | -0.054932 | -0.12817 | 0.041199 | 0.082397 | -0.25177 | -0.1236 | -0.059509 | 122.9004 | 122.9233 | 58.0902 | -122.9965 | 122.9187 | 122.818 | 58.1955 | -123.0057
384.8438 | 123.1888 | -58.1406 | 64.7552 | 0.2134 | -0.025384 | 0.066015 | 0.0034768 | 0.060057 | -0.010566 | -0.015707 | 1.3133 | -0.025551 | 0.041683 | 0.054584 | -0.0031411 | -0.0094981 | 64.8285 | -58.0811 | -0.022888 | -58.3328 | 64.7873 | -58.2001 | -58.2092 | -58.0444 | 0.064087 | -58.4152 | 64.7873 | 64.6957 | -58.168 | -58.287 | -0.059509 | -0.068665 | 0.032043 | 0.059509 | -0.19226 | -0.1236 | 0.073242 | -0.027466 | -0.14648 | 0.032043 | 0.09613 | -0.27466 | -0.12817 | -0.059509 | 122.9279 | 122.9691 | 58.1177 | -122.9645 | 122.9279 | 122.8363 | 58.2047 | -123.0423
385.8438 | 123.23 | -58.1314 | 64.7644 | 0.27444 | -0.012566 | 0.077764 | 0.010954 | 0.055785 | -0.0030893 | -0.014639 | 0.22992 | -0.009529 | 0.04916 | 0.046039 | -0.0074141 | -0.015907 | 64.8193 | -58.0582 | -0.009155 | -58.3603 | 64.7781 | -58.168 | -58.2184 | -58.0856 | 0.041199 | -58.4198 | 64.8148 | 64.7003 | -58.1955 | -58.2825 | -0.036621 | -0.086975 | 0.013733 | 0.073242 | -0.22888 | -0.14191 | 0.054932 | -0.064087 | -0.15106 | 0.050354 | 0.045777 | -0.28839 | -0.13733 | -0.064087 | 122.9095 | 122.9507 | 58.1223 | -122.9828 | 122.9462 | 122.8317 | 58.1726 | -123.0469
386.8438 | 123.1888 | -58.1314 | 64.769 | 0.33547 | -0.0082939 | 0.086309 | 0.0024088 | 0.048308 | -0.0073613 | -0.01998 | 0.29095 | -0.015938 | 0.056637 | 0.058857 | 6.2882e-05 | -0.0073621 | 64.8239 | -58.0673 | -0.036621 | -58.3649 | 64.769 | -58.1726 | -58.2367 | -58.0536 | 0.036621 | -58.4061 | 64.8193 | 64.7003 | -58.1863 | -58.287 | -0.041198 | -0.10529 | 0 | 0.064087 | -0.23346 | -0.12817 | 0.054932 | -0.054931 | -0.15564 | 0.050354 | 0.07782 | -0.27466 | -0.11902 | -0.068665 | 122.9004 | 122.9553 | 58.0948 | -123.0057 | 122.9507 | 122.8317 | 58.168 | -123.056
387.8438 | 123.2346 | -58.136 | 64.7507 | 0.83901 | -0.0029529 | 0.085241 | 0.00027184 | 0.049376 | 0.0097277 | -0.0071622 | 0.35199 | -0.011666 | 0.052364 | 0.057788 | 0.011812 | -0.015907 | 64.8788 | -58.0353 | 0 | -58.3237 | 64.7552 | -58.1726 | -58.1955 | -58.0261 | 0.068665 | -58.3786 | 64.7873 | 64.682 | -58.1772 | -58.2779 | -0.036621 | -0.05951 | 0.004578 | 0.10071 | -0.18768 | -0.12817 | 0.12817 | -0.041199 | -0.14191 | 0.036621 | 0.10986 | -0.24262 | -0.10071 | -0.068664 | 122.8912 | 123.0148 | 58.136 | -122.9462 | 122.9233 | 122.818 | 58.2047 | -123.0286
388.8438 | 123.2391 | -58.136 | 64.7736 | 0.57961 | 0.0045241 | 0.060674 | 0.0056128 | 0.051512 | 0.0043877 | -0.0018222 | 0.39777 | -0.011666 | 0.045956 | 0.049243 | 0.0021989 | -0.012702 | 64.888 | -58.0399 | -0.013733 | -58.3191 | 64.7461 | -58.1909 | -58.2047 | -57.9254 | 0.064087 | -58.342 | 64.8056 | 64.6957 | -58.1818 | -58.2687 | -0.054932 | -0.068665 | -0.027466 | 0.09613 | -0.18311 | -0.11444 | 0.11444 | -0.045777 | -0.13275 | 0.032043 | 0.21057 | -0.20599 | -0.073242 | -0.07782 | 122.8821 | 123.024 | 58.1223 | -122.9782 | 122.9416 | 122.8317 | 58.2001 | -123.0423
389.8438 | 123.1979 | -58.136 | 64.7552 | 0.41177 | 0.013069 | 0.068151 | 0.0066808 | 0.045104 | -0.0041573 | -0.0050262 | 0.36725 | -0.013802 | 0.04916 | 0.043903 | -0.0031411 | -0.0073621 | 64.8331 | -58.0582 | -0.027466 | -58.3603 | 64.769 | -58.1863 | -58.223 | -58.0353 | 0.041199 | -58.4015 | 64.7964 | 64.7003 | -58.168 | -58.2733 | -0.050354 | -0.086975 | 0.013733 | 0.077819 | -0.2243 | -0.13733 | 0.07782 | -0.032044 | -0.13733 | 0.041199 | 0.10071 | -0.2655 | -0.12817 | -0.054932 | 122.905 | 122.9691 | 58.1085 | -122.9782 | 122.9324 | 122.8363 | 58.1772 | -123.0286
390.8438 | 123.1934 | -58.1268 | 64.7598 | 0.45754 | -0.0040209 | 0.076696 | 0.0077488 | 0.054717 | 0.0033197 | -0.0060942 | 0.36725 | -0.002053 | 0.04916 | 0.058857 | 6.2882e-05 | -0.0073621 | 64.856 | -58.0444 | -0.013733 | -58.342 | 64.7278 | -58.2001 | -58.2092 | -58.017 | 0.032043 | -58.3923 | 64.7781 | 64.682 | -58.168 | -58.2733 | -0.073242 | -0.082398 | -0.032044 | 0.082397 | -0.21515 | -0.13275 | 0.09613 | -0.041199 | -0.14648 | 0.01831 | 0.10986 | -0.2655 | -0.11902 | -0.07782 | 122.8546 | 122.9828 | 58.1131 | -122.9691 | 122.905 | 122.8088 | 58.1589 | -123.0331
391.8438 | 123.23 | -58.136 | 64.7461 | 0.83901 | 0.0087961 | 0.066015 | 0.0098848 | 0.055785 | 0.0075917 | -0.0050262 | 0.41303 | -0.007393 | 0.072659 | 0.050312 | 0.0096759 | -0.00095306 | 64.8788 | -58.0353 | -0.027466 | -58.3511 | 64.7644 | -58.1818 | -58.2047 | -58.0078 | 0.064087 | -58.3786 | 64.7873 | 64.6591 | -58.2001 | -58.2916 | -0.045777 | -0.068665 | 0.01831 | 0.10071 | -0.21515 | -0.14648 | 0.13275 | -0.064087 | -0.15564 | 0.041198 | 0.12817 | -0.24262 | -0.086975 | -0.086975 | 122.9004 | 123.0148 | 58.1085 | -122.9507 | 122.9233 | 122.7951 | 58.2001 | -123.0377
392.8438 | 123.2529 | -58.1451 | 64.7324 | 0.59487 | 0.020545 | 0.075628 | -0.0029322 | 0.061125 | 0.00011475 | -0.00075419 | -2.1505 | -0.003121 | 0.070522 | 0.054584 | 0.01288 | -0.011634 | 64.8788 | -58.0399 | -0.004578 | -58.3237 | 64.7552 | -58.1909 | -58.2413 | -58.0124 | 0.054932 | -58.3603 | 64.7964 | 64.682 | -58.1909 | -58.2779 | -0.045776 | -0.09613 | 0.022888 | 0.10529 | -0.17853 | -0.082397 | 0.14648 | -0.045776 | -0.13275 | 0.064087 | 0.13275 | -0.21515 | -0.082398 | -0.050354 | 122.9004 | 123.024 | 58.1406 | -122.9736 | 122.9416 | 122.8271 | 58.2001 | -123.0103
393.8438 | 123.2162 | -58.1314 | 64.7278 | 0.82375 | 0.0098641 | 0.076696 | 0.015226 | 0.062194 | 0.016137 | -0.010367 | 0.35199 | -0.007393 | 0.063046 | 0.05672 | 0.0064719 | -0.0073621 | 64.8743 | -58.0673 | -0.027466 | -58.3282 | 64.7598 | -58.1955 | -58.2184 | -58.0215 | 0.068665 | -58.3786 | 64.7781 | 64.6591 | -58.2047 | -58.287 | -0.064087 | -0.086975 | 0.032044 | 0.064087 | -0.19684 | -0.10986 | 0.14648 | -0.073242 | -0.15564 | 0.050354 | 0.10986 | -0.24719 | -0.091553 | -0.068664 | 122.8912 | 123.0057 | 58.1039 | -122.9462 | 122.9095 | 122.7905 | 58.2001 | -123.0148
394.8438 | 123.1338 | -58.1451 | 64.7827 | 0.44228 | 0.02375 | 0.080969 | 0.014158 | 0.040831 | 0.0097277 | -0.0018222 | 0.29095 | -0.006325 | 0.06625 | 0.065265 | 0.0011309 | -0.0020211 | 64.801 | -58.1589 | -0.10986 | -58.3969 | 64.801 | -58.2138 | -58.255 | -58.0902 | -0.045776 | -58.4793 | 64.8239 | 64.6912 | -58.2092 | -58.3237 | -0.068664 | -0.10986 | 0.01831 | -0.013733 | -0.25177 | -0.14191 | 0.01831 | -0.064087 | -0.17853 | 0.041199 | 0.054932 | -0.33417 | -0.15564 | -0.091553 | 122.9462 | 122.9462 | 58.0353 | -123.0377 | 122.9691 | 122.8363 | 58.0994 | -123.1064
395.8438 | 123.1705 | -58.1772 | 64.7644 | 0.61013 | 0.0013191 | 0.068151 | 0.016294 | 0.051512 | 0.015069 | -0.013571 | 0.32147 | -0.010597 | 0.036343 | 0.049243 | 0.0021989 | -0.01377 | 64.8148 | -58.1451 | -0.091553 | -58.374 | 64.7873 | -58.2001 | -58.255 | -58.0811 | -0.009155 | -58.4381 | 64.7919 | 64.7324 | -58.1863 | -58.3374 | -0.022888 | -0.07782 | 0.022888 | 0.032043 | -0.19684 | -0.11902 | 0.050354 | -0.009155 | -0.16022 | 0.027466 | 0.09613 | -0.26093 | -0.10071 | -0.032043 | 122.9645 | 122.9919 | 58.0856 | -123.0194 | 122.9691 | 122.9095 | 58.168 | -123.1018
396.8438 | 123.2346 | -58.1406 | 64.7552 | 0.50332 | 0.017341 | 0.080969 | 0.0024088 | 0.053649 | 0.0043877 | -0.0039582 | 0.38251 | 0.001152 | 0.056637 | 0.054584 | 0.0075399 | -0.010566 | 64.8056 | -58.0811 | -0.073242 | -58.3649 | 64.7598 | -58.1772 | -58.223 | -58.0215 | 0.004578 | -58.4106 | 64.8056 | 64.6637 | -58.1909 | -58.287 | -0.036621 | -0.082397 | 0.004578 | 0.059509 | -0.2243 | -0.14191 | 0.050354 | -0.050354 | -0.14648 | 0.050354 | 0.11902 | -0.27008 | -0.1236 | -0.091553 | 122.9004 | 122.9462 | 58.0673 | -122.9782 | 122.9462 | 122.8043 | 58.1451 | -123.0423
397.8438 | 123.1705 | -58.1406 | 64.7507 | 0.48806 | 0.017341 | 0.069219 | 0.0013408 | 0.054717 | 0.010797 | -0.0092992 | 0.36725 | -0.010597 | 0.067318 | 0.054584 | -0.0010051 | -0.011634 | 64.801 | -58.1406 | -0.09613 | -58.3923 | 64.8102 | -58.1955 | -58.2504 | -58.0811 | -0.018311 | -58.4381 | 64.8193 | 64.7095 | -58.1818 | -58.3008 | -0.054932 | -0.10986 | 0.05951 | 0 | -0.25177 | -0.14191 | 0.050354 | -0.041199 | -0.16022 | 0.068665 | 0.059509 | -0.29755 | -0.13733 | -0.041198 | 122.9507 | 122.9416 | 58.0444 | -123.0011 | 122.9599 | 122.85 | 58.1223 | -123.0515
398.8438 | 123.143 | -58.1909 | 64.8102 | 0.2134 | 0.017341 | 0.071355 | 0.0098848 | 0.057921 | 0.014001 | -0.011435 | 0.36725 | 0.004356 | 0.054501 | 0.064197 | 0.0096759 | -0.0020211 | 64.7873 | -58.1772 | -0.11902 | -58.3969 | 64.8056 | -58.1955 | -58.2275 | -58.1223 | -0.054932 | -58.4793 | 64.8331 | 64.7415 | -58.223 | -58.3008 | -0.004578 | -0.036621 | -0.004578 | 0.013733 | -0.20599 | -0.16937 | -0.022889 | -0.032043 | -0.10986 | 0.022888 | 0.068665 | -0.28839 | -0.17853 | -0.068665 | 122.9965 | 122.9782 | 58.0719 | -123.0377 | 123.024 | 122.9324 | 58.136 | -123.111
399.8438 | 123.1018 | -58.168 | 64.801 | 0.4728 | 0.013069 | 0.073492 | 0.00027184 | 0.053649 | 0.0097277 | 0.0035188 | 0.2757 | -0.00098395 | 0.056637 | 0.058857 | 0.0064719 | -0.0062931 | 64.6912 | -58.4152 | -0.22888 | -58.2321 | 64.7919 | -58.2047 | -58.223 | -58.1406 | -0.064087 | -58.4839 | 64.8193 | 64.7736 | -58.2001 | -58.3008 | -0.036621 | -0.054931 | -0.009155 | -0.24719 | -0.064087 | -0.009156 | -0.10986 | -0.032043 | -0.13275 | 0.018311 | 0.027466 | -0.31586 | -0.18311 | -0.027465 | 122.9599 | 122.8592 | 57.9391 | -123.024 | 122.9874 | 122.9416 | 58.1039 | -123.1018
400.8438 | 123.1934 | -58.2001 | 64.801 | 0.18289 | 0.030158 | 0.058538 | 0.0088168 | 0.05258 | 0.0086597 | -0.0050262 | 0.24518 | 0.005424 | 0.06625 | 0.064197 | 0.0096759 | -0.0020211 | 64.7598 | -58.2138 | -0.13275 | -58.4152 | 64.7964 | -58.2184 | -58.2504 | -58.1406 | -0.059509 | -58.4747 | 64.801 | 64.7644 | -58.2321 | -58.3282 | -0.018311 | -0.050354 | -0.004577 | -0.013733 | -0.21515 | -0.16479 | -0.041198 | -0.032044 | -0.12817 | 0 | 0.059509 | -0.27466 | -0.14648 | -0.036621 | 122.9965 | 122.9599 | 58.0673 | -123.0515 | 123.0011 | 122.9645 | 58.1406 | -123.1293
401.8438 | 123.1293 | -58.1451 | 64.7964 | 0.13711 | 0.022682 | 0.070287 | 0.021635 | 0.055785 | -0.0020213 | 0.0013818 | 0.10785 | -0.002053 | 0.061977 | 0.055652 | 0.0054039 | -0.0084301 | 64.8331 | -58.1039 | -0.009155 | -58.342 | 64.8148 | -58.1955 | -58.223 | -58.1085 | 0.036621 | -58.4381 | 64.8376 | 64.769 | -58.2138 | -58.3099 | -0.050354 | -0.077819 | 0.01831 | 0.041199 | -0.19684 | -0.11902 | 0.036621 | -0.068664 | -0.16479 | 0.041198 | 0.036621 | -0.29297 | -0.12817 | -0.027466 | 122.9599 | 122.9782 | 58.136 | -123.0194 | 122.9828 | 122.9141 | 58.1818 | -123.1064
402.8438 | 123.1293 | -58.168 | 64.8102 | 0.33547 | 0.030158 | 0.067083 | 0.016294 | 0.048308 | 0.0033197 | 0.00031381 | 0.10785 | -0.007393 | 0.06625 | 0.065265 | 0.01288 | -0.0052251 | 64.8102 | -58.1223 | -0.041199 | -58.3649 | 64.8193 | -58.1863 | -58.2275 | -58.136 | 0 | -58.4564 | 64.8743 | 64.7736 | -58.2138 | -58.3099 | -0.01831 | -0.059509 | 0.009155 | 0.045777 | -0.19684 | -0.13733 | 0 | -0.045776 | -0.14191 | 0.064087 | 0.032044 | -0.28839 | -0.14648 | -0.036621 | 122.9874 | 122.9782 | 58.1268 | -123.0377 | 123.0423 | 122.9416 | 58.168 | -123.1201
403.8438 | 123.0881 | -58.1543 | 64.801 | 0.12185 | 0.020545 | 0.066015 | 0.023771 | 0.058989 | -0.0030893 | 0.0045868 | 0.1994 | 0.00222 | 0.057705 | 0.040699 | 0.0096759 | -0.0094981 | 64.7827 | -58.1635 | -0.082397 | -58.3878 | 64.8285 | -58.1772 | -58.223 | -58.1818 | -0.054932 | -58.4885 | 64.8376 | 64.7827 | -58.223 | -58.3145 | -0.022888 | -0.068664 | 0.027466 | -0.009155 | -0.23346 | -0.1648 | -0.01831 | -0.068664 | -0.16022 | 0.036621 | -0.027466 | -0.33417 | -0.17395 | -0.01831 | 122.9828 | 122.937 | 58.0719 | -123.024 | 122.9919 | 122.937 | 58.0994 | -123.1155
404.8438 | 123.1064 | -58.1543 | 64.7919 | 0.18289 | 0.035499 | 0.058538 | 0.024839 | 0.055785 | -0.0084293 | -0.0050262 | 0.092591 | 0.004356 | 0.051296 | 0.049243 | 0.0032669 | -0.0073621 | 64.7873 | -58.1314 | -0.045776 | -58.3649 | 64.8376 | -58.1909 | -58.2321 | -58.1451 | -0.009155 | -58.4656 | 64.8239 | 64.7781 | -58.2092 | -58.3054 | -0.036621 | -0.07782 | 0.045776 | 0.022888 | -0.21057 | -0.13275 | -0.004578 | -0.054932 | -0.15106 | 0.032044 | 0.009155 | -0.31128 | -0.16022 | -0.013733 | 122.9919 | 122.9416 | 58.1085 | -123.024 | 122.9782 | 122.9324 | 58.1451 | -123.0972
405.8438 | 123.1384 | -58.1543 | 64.8056 | 0.091333 | 0.025886 | 0.067083 | 0.0024088 | 0.057921 | -0.0020213 | -0.0028902 | 0.046815 | -0.003121 | 0.061977 | 0.063129 | 0.017153 | -0.0030891 | 64.8193 | -58.1177 | -0.027466 | -58.3374 | 64.8468 | -58.1543 | -58.2138 | -58.1131 | 0.041199 | -58.4335 | 64.8468 | 64.7827 | -58.2001 | -58.3054 | 0 | -0.059509 | 0.041199 | 0.036621 | -0.1831 | -0.1236 | 0.013733 | -0.045776 | -0.15106 | 0.041199 | 0.041199 | -0.27924 | -0.12817 | -0.022888 | 123.0011 | 122.9736 | 58.1268 | -123.0194 | 123.0011 | 122.937 | 58.1955 | -123.111
406.8438 | 123.1155 | -58.1497 | 64.8056 | 0.44228 | 0.032295 | 0.083105 | 0.0045448 | 0.053649 | 0.0075917 | 0.00031381 | -0.01422 | -0.010597 | 0.058773 | 0.063129 | 0.011812 | -0.0020211 | 64.8468 | -58.0673 | 0.009155 | -58.3282 | 64.8331 | -58.168 | -58.2092 | -58.0902 | 0.045776 | -58.4244 | 64.8376 | 64.801 | -58.1772 | -58.2916 | -0.018311 | -0.05951 | 0.027466 | 0.082397 | -0.17853 | -0.11902 | 0.041199 | -0.027466 | -0.14191 | 0.032043 | 0.059509 | -0.27466 | -0.13275 | -0.004578 | 122.9828 | 122.9965 | 58.1589 | -123.0148 | 122.9874 | 122.9507 | 58.1955 | -123.0972
407.8438 | 123.1384 | -58.1268 | 64.8148 | -0.045996 | 0.036567 | 0.058538 | 0.0077488 | 0.068602 | -0.0020213 | -0.012503 | -0.28888 | -0.004189 | 0.053432 | 0.05672 | 0.0086079 | -0.0020211 | 64.8651 | -58.1955 | -0.013733 | -58.3099 | 64.8056 | -58.1818 | -58.2275 | -58.0719 | 0.091553 | -58.3786 | 64.8239 | 64.7827 | -58.168 | -58.2733 | -0.054932 | -0.10071 | -0.009155 | -0.068665 | -0.18311 | -0.082398 | 0.050354 | -0.041199 | -0.14648 | 0.009156 | 0.054932 | -0.25177 | -0.10529 | -0.032043 | 122.9324 | 122.9919 | 58.1131 | -123.0423 | 122.9507 | 122.9095 | 58.2184 | -123.0881
408.8438 | 123.1796 | -58.1314 | 64.8193 | -0.27488 | 0.013069 | 0.069219 | 0.0098848 | 0.060057 | -0.0020213 | -0.0082312 | -0.21259 | -0.005257 | 0.065182 | 0.05672 | 0.0032669 | -0.0073621 | 64.8148 | -58.0856 | 0.004578 | -58.3282 | 64.8422 | -58.1726 | -58.2047 | -58.0811 | 0.10986 | -58.3923 | 64.8468 | 64.7873 | -58.1818 | -58.2962 | -0.041198 | -0.073242 | 0.022888 | 0.045777 | -0.19684 | -0.1236 | -0.004578 | -0.050354 | -0.1648 | 0.027466 | 0.050354 | -0.26093 | -0.09613 | -0.032044 | 122.9736 | 122.9462 | 58.136 | -123.024 | 122.9782 | 122.9187 | 58.2413 | -123.1155
409.8438 | 123.143 | -58.1497 | 64.8056 | -0.091772 | 0.014137 | 0.071355 | -0.0040002 | 0.062194 | 0.0033197 | -0.0082312 | -0.090514 | -0.007393 | 0.06625 | 0.052448 | 6.2882e-05 | -0.015907 | 64.856 | -58.0994 | 0.022888 | -58.3145 | 64.801 | -58.1818 | -58.1955 | -58.0902 | 0.10071 | -58.3923 | 64.8376 | 64.7827 | -58.168 | -58.2779 | -0.032044 | -0.045777 | -0.004578 | 0.050354 | -0.1648 | -0.11902 | 0.050354 | -0.018311 | -0.12817 | 0.032043 | 0.059509 | -0.24262 | -0.11444 | -0.022888 | 122.9507 | 123.0057 | 58.1726 | -123.0011 | 122.9874 | 122.9324 | 58.2504 | -123.0835
410.8438 | 123.1476 | -58.1406 | 64.8376 | 0.060816 | 0.019477 | 0.072424 | -0.0061362 | 0.071807 | -0.0052253 | 0.00031381 | -0.5025 | -0.004189 | 0.064114 | 0.053516 | 0.016085 | -0.0041571 | 64.8422 | -58.0719 | 0.018311 | -58.4152 | 64.801 | -58.1818 | -58.223 | -58.0765 | 0.11444 | -58.3923 | 64.8605 | 64.7736 | -58.1863 | -58.2733 | -0.041199 | -0.082397 | -0.036621 | 0.068665 | -0.27466 | -0.19226 | 0.004578 | -0.045776 | -0.13275 | 0.022889 | 0.064087 | -0.25177 | -0.11902 | -0.064086 | 122.9416 | 122.9828 | 58.1589 | -123.0606 | 123.0011 | 122.9141 | 58.255 | -123.111
411.8438 | 123.1613 | -58.1543 | 64.8148 | -0.030737 | 0.028022 | 0.084173 | 0.014158 | 0.060057 | 0.0011837 | -0.011435 | -0.16681 | -0.022347 | 0.058773 | 0.048175 | 6.2882e-05 | -0.0094981 | 64.8376 | -58.0719 | 0.027466 | -58.3282 | 64.8148 | -58.1863 | -58.2092 | -58.0856 | 0.09613 | -58.4015 | 64.8331 | 64.7598 | -58.1863 | -58.3191 | -0.032043 | -0.054932 | 0 | 0.082398 | -0.17395 | -0.11902 | 0.022888 | -0.032043 | -0.16479 | 0.018311 | 0.068665 | -0.24719 | -0.082397 | -0.054931 | 122.9691 | 122.9919 | 58.1818 | -123.024 | 122.9874 | 122.9141 | 58.2504 | -123.1338
412.8438 | 123.1476 | -58.1497 | 64.8148 | -0.10703 | 0.02909 | 0.09165 | 0.01843 | 0.058989 | 0.0043877 | -0.0039582 | -0.10577 | -0.008461 | 0.054501 | 0.058857 | 6.2882e-05 | -0.0041571 | 64.8468 | -58.0673 | 0.036621 | -58.3282 | 64.8193 | -58.1863 | -58.2184 | -58.0902 | 0.10529 | -58.3786 | 64.8697 | 64.801 | -58.1863 | -58.2825 | -0.036621 | -0.068665 | 0.004578 | 0.082397 | -0.17853 | -0.10986 | 0.032044 | -0.036621 | -0.13275 | 0.054932 | 0.059509 | -0.22888 | -0.09613 | -0.013733 | 122.9691 | 122.9965 | 58.1863 | -123.0331 | 123.0194 | 122.9507 | 58.255 | -123.0972
413.8438 | 123.1796 | -58.1543 | 64.8239 | -0.16807 | 0.031227 | 0.069219 | 0.010954 | 0.058989 | -0.00095325 | -0.010367 | -0.21259 | -0.004189 | 0.075863 | 0.060993 | -0.0074141 | -0.0030891 | 64.8148 | -58.0811 | 0.022888 | -58.3328 | 64.8422 | -58.1635 | -58.1909 | -58.0811 | 0.11444 | -58.3832 | 64.8514 | 64.7736 | -58.1726 | -58.287 | -0.009155 | -0.036621 | 0.01831 | 0.073242 | -0.17853 | -0.14191 | -0.009156 | -0.01831 | -0.13275 | 0.027465 | 0.073242 | -0.22888 | -0.096131 | -0.050354 | 122.9965 | 122.9691 | 58.1772 | -123.0148 | 123.0057 | 122.9279 | 58.2687 | -123.111
414.8438 | 123.1338 | -58.136 | 64.8102 | -0.18333 | 0.0066601 | 0.080969 | 0.0077488 | 0.083556 | 0.0065237 | -0.011435 | -0.28888 | -0.003121 | 0.068386 | 0.047107 | 0.0086079 | -0.015907 | 64.8056 | -58.1039 | 0.004578 | -58.3282 | 64.8376 | -58.1726 | -58.2184 | -58.1085 | 0.11444 | -58.4106 | 64.8697 | 64.8056 | -58.1772 | -58.2733 | -0.036621 | -0.082398 | 0.027465 | 0.032043 | -0.19226 | -0.10986 | -0.004578 | -0.041199 | -0.13733 | 0.059509 | 0.027465 | -0.27466 | -0.13733 | -0.004578 | 122.9736 | 122.9416 | 58.1406 | -123.0286 | 123.0057 | 122.9416 | 58.2504 | -123.0835
415.8438 | 123.0927 | -58.136 | 64.8468 | -0.33591 | -0.0040209 | 0.05747 | 0.025907 | 0.063262 | -0.025519 | -0.0060942 | -0.19733 | -0.004189 | 0.06625 | 0.042835 | -0.021299 | -0.012702 | 64.8056 | -58.0994 | 0.013733 | -58.3557 | 64.8422 | -58.1635 | -58.2413 | -58.1497 | -0.059509 | -58.5022 | 64.8743 | 64.7736 | -58.2367 | -58.2962 | -0.027466 | -0.10529 | -0.004578 | 0.036621 | -0.21973 | -0.11444 | -0.041199 | -0.10071 | -0.16022 | 0.027466 | -0.013733 | -0.36621 | -0.20599 | -0.073242 | 122.9782 | 122.9416 | 58.1497 | -123.0881 | 123.0103 | 122.9095 | 58.0765 | -123.143
416.8438 | 123.1293 | -58.1543 | 64.8422 | -1.6177 | 0.015205 | 0.0799 | 0.021635 | 0.054717 | -0.0052253 | -0.0060942 | -0.21259 | 0.001152 | 0.054501 | 0.064197 | -0.0042101 | -0.010566 | 64.801 | -58.1131 | 0.009155 | -58.3649 | 64.8376 | -58.1726 | -58.2138 | -58.136 | 0.091553 | -58.4335 | 64.8468 | 64.7964 | -58.2001 | -58.3008 | -0.01831 | -0.059509 | -0.004578 | 0.041199 | -0.21057 | -0.15106 | -0.041199 | -0.045776 | -0.14648 | 0.004578 | 0.018311 | -0.27924 | -0.13275 | -0.045776 | 122.9919 | 122.9553 | 58.1635 | -123.056 | 123.0011 | 122.9507 | 58.2458 | -123.143
417.8438 | 123.1293 | -58.1406 | 64.801 | -0.15281 | 0.014137 | 0.080969 | 0.020567 | 0.050444 | -0.010566 | -0.0082312 | -0.25836 | -0.005257 | 0.064114 | 0.058857 | 0.0043349 | -0.0073621 | 64.7873 | -58.1177 | 0.018311 | -58.3466 | 64.8651 | -58.1772 | -58.223 | -58.1039 | 0.09613 | -58.4198 | 64.8697 | 64.8148 | -58.1955 | -58.3054 | -0.036621 | -0.082397 | 0.064087 | 0.022888 | -0.20599 | -0.1236 | -0.013733 | -0.054932 | -0.1648 | 0.068665 | 0.036621 | -0.27924 | -0.11444 | 0.013733 | 123.0057 | 122.9279 | 58.1589 | -123.024 | 123.0103 | 122.9553 | 58.2367 | -123.1064
418.8438 | 123.1338 | -58.1497 | 64.8285 | -0.42747 | 0.017341 | 0.084173 | 0.01843 | 0.051512 | -0.0052253 | -0.0039582 | -0.16681 | -0.009529 | 0.063046 | 0.060993 | -0.0010051 | -0.0041571 | 64.7964 | -58.1268 | 0.004578 | -58.3603 | 64.8422 | -58.168 | -58.2138 | -58.1451 | 0.10071 | -58.4152 | 64.8972 | 64.801 | -58.1818 | -58.2825 | -0.018311 | -0.064087 | 0.013733 | 0.022888 | -0.21057 | -0.14648 | -0.032043 | -0.032044 | -0.13275 | 0.068665 | 0.004577 | -0.2655 | -0.13275 | -0.027466 | 122.9919 | 122.9462 | 58.1543 | -123.0423 | 123.0469 | 122.9507 | 58.2504 | -123.111
419.8438 | 123.1155 | -58.1497 | 64.8422 | -0.29014 | -0.01043 | 0.0799 | 0.023771 | 0.06433 | -0.0073613 | -0.010367 | -0.2431 | -0.002053 | 0.038479 | 0.058857 | -0.0052781 | -0.0041571 | 64.7781 | -58.1131 | 0.009155 | -58.3557 | 64.8331 | -58.168 | -58.2184 | -58.1955 | 0.050354 | -58.461 | 64.8651 | 64.7964 | -58.2184 | -58.3237 | -0.018311 | -0.068665 | -0.009155 | 0.036621 | -0.20599 | -0.13733 | -0.064087 | -0.068665 | -0.17395 | 0.022888 | -0.045777 | -0.31128 | -0.13733 | -0.045776 | 122.9828 | 122.9279 | 58.1589 | -123.0606 | 123.0148 | 122.9462 | 58.2001 | -123.1659
420.8438 | 123.1064 | -58.1451 | 64.8514 | -0.15281 | -0.0093619 | 0.069219 | 0.016294 | 0.063262 | -0.019111 | -0.024252 | -0.22784 | -0.010597 | 0.056637 | 0.059925 | 0.0032669 | -0.0073621 | 64.769 | -58.0902 | 0.032043 | -58.3557 | 64.8468 | -58.1497 | -58.2001 | -58.1223 | 0.10986 | -58.429 | 64.8697 | 64.8148 | -58.1909 | -58.2779 | -0.004577 | -0.054931 | -0.004577 | 0.054932 | -0.21057 | -0.15564 | -0.082397 | -0.045776 | -0.13275 | 0.018311 | 0.022889 | -0.28381 | -0.15106 | -0.036621 | 122.9919 | 122.9141 | 58.1772 | -123.0515 | 123.0148 | 122.9599 | 58.255 | -123.1293
421.8438 | 123.1979 | -58.1268 | 64.8285 | 0.10659 | 0.0034561 | 0.072424 | 0.0013408 | 0.057921 | -0.028724 | -0.018912 | -0.090514 | -0.021279 | 0.054501 | 0.062061 | -0.010618 | -0.0094981 | 64.8651 | -57.9849 | 0.13275 | -58.287 | 64.8193 | -58.136 | -58.168 | -58.0353 | 0.19684 | -58.3145 | 64.8331 | 64.7736 | -58.1543 | -58.2733 | -0.009155 | -0.041199 | -0.009155 | 0.14191 | -0.16022 | -0.11902 | 0.036621 | -0.027466 | -0.14648 | 0.004578 | 0.091553 | -0.18768 | -0.041199 | -0.054931 | 122.9462 | 122.9919 | 58.2596 | -122.9965 | 122.9599 | 122.9004 | 58.3237 | -123.1018
422.8438 | 123.2162 | -58.0994 | 64.8102 | -0.15281 | -0.0093619 | 0.067083 | 0.01309 | 0.060057 | -0.021247 | -0.016776 | 1.5269 | -0.017006 | 0.047024 | 0.072742 | 0.0096759 | -0.0062931 | 64.888 | -57.9437 | 0.10071 | -58.017 | 64.8743 | -58.0948 | -58.1543 | -58.0124 | 0.24261 | -58.2779 | 64.8056 | 64.7141 | -58.1497 | -58.2321 | 0.004577 | -0.054932 | 0.064087 | 0.15564 | 0.082397 | 0.13733 | 0.077819 | -0.050354 | -0.13275 | -0.004578 | 0.086975 | -0.17853 | -0.045776 | -0.096131 | 122.9736 | 122.9874 | 58.2001 | -122.9645 | 122.905 | 122.8134 | 58.342 | -123.0423
423.8438 | 123.2117 | -58.1039 | 64.8148 | 1.5714 | -0.0082939 | 0.083105 | 0.00027184 | 0.045104 | -0.027656 | -0.015707 | -0.15155 | -0.021279 | 0.047024 | 0.050312 | -0.0031411 | -0.015907 | 64.8651 | -57.9254 | 0.16022 | -58.2733 | 64.8239 | -58.1635 | -58.1589 | -58.0078 | 0.2655 | -58.3282 | 64.8376 | 64.7415 | -58.1314 | -58.2642 | -0.059509 | -0.054932 | 0.009156 | 0.17853 | -0.16937 | -0.11444 | 0.050354 | -0.027466 | -0.16022 | 0.022888 | 0.096131 | -0.2243 | -0.064087 | -0.073242 | 122.9279 | 122.9691 | 58.2642 | -122.9736 | 122.9416 | 122.8455 | 58.3694 | -123.0789
424.8438 | 123.1979 | -58.0902 | 64.8148 | -0.13755 | -0.00081686 | 0.075628 | 0.0034768 | 0.060057 | -0.010566 | -0.014639 | -0.25836 | -0.010597 | 0.042751 | 0.044971 | -0.0031411 | -0.0052251 | 64.888 | -57.9758 | 0.15564 | -58.2687 | 64.8056 | -58.1635 | -58.1909 | -58.0399 | 0.24261 | -58.3328 | 64.8651 | 64.769 | -58.1497 | -58.255 | -0.073242 | -0.10071 | -0.009155 | 0.11444 | -0.17853 | -0.07782 | 0.073242 | -0.059509 | -0.16479 | 0.050354 | 0.050354 | -0.24262 | -0.07782 | -0.045776 | 122.8958 | 122.9782 | 58.2458 | -123.0057 | 122.9553 | 122.8592 | 58.3328 | -123.0698
425.8438 | 123.2071 | -58.0719 | 64.8285 | -0.45798 | -0.0072259 | 0.086309 | 0.0056128 | 0.06967 | -0.01377 | -0.011435 | -0.22784 | -0.019142 | 0.061977 | 0.062061 | 6.2882e-05 | -0.018043 | 64.8834 | -57.962 | 0.16022 | -58.2504 | 64.8193 | -58.1131 | -58.1497 | -58.0032 | 0.29297 | -58.3054 | 64.8239 | 64.7552 | -58.1177 | -58.2504 | -0.041199 | -0.07782 | -0.009155 | 0.10986 | -0.17853 | -0.10071 | 0.054932 | -0.045777 | -0.17853 | -0.004577 | 0.068664 | -0.23346 | -0.054932 | -0.073242 | 122.8912 | 122.9553 | 58.2321 | -122.9782 | 122.8958 | 122.8271 | 58.3649 | -123.0789
426.8438 | 123.2208 | -58.0765 | 64.8239 | -0.24436 | -0.014702 | 0.075628 | 0.0098848 | 0.06433 | -0.011634 | -0.024252 | -1.5554 | -0.011666 | 0.048092 | 0.054584 | -0.0042101 | -0.010566 | 64.9155 | -57.9391 | 0.15106 | -58.2458 | 64.8285 | -58.1039 | -58.1451 | -58.0032 | 0.37079 | -58.3099 | 64.8605 | 64.7644 | -58.136 | -58.223 | -0.027466 | -0.068665 | 0.004577 | 0.13733 | -0.16937 | -0.10071 | 0.091552 | -0.059509 | -0.14648 | 0.036621 | 0.073242 | -0.23346 | -0.086976 | -0.05951 | 122.905 | 122.9919 | 58.2275 | -122.9691 | 122.937 | 122.8409 | 58.4473 | -123.0469
427.8438 | 123.2346 | -58.0719 | 64.8468 | -0.045996 | -0.016839 | 0.068151 | 0.010954 | 0.066466 | -0.0084293 | -0.012503 | -0.16681 | -0.012734 | 0.04916 | 0.059925 | -0.0010051 | -0.0073621 | 64.9292 | -57.9117 | 0.16479 | -58.2413 | 64.8193 | -58.1131 | -58.1406 | -57.9529 | 0.37537 | -58.2779 | 64.856 | 64.7507 | -58.1177 | -58.2092 | -0.041199 | -0.068665 | -0.027466 | 0.16022 | -0.16937 | -0.10071 | 0.082397 | -0.045777 | -0.13733 | 0.009155 | 0.11902 | -0.20599 | -0.068664 | -0.096131 | 122.8912 | 123.0011 | 58.2367 | -122.9874 | 122.9279 | 122.8226 | 58.4473 | -123.056
428.8438 | 123.143 | -58.0994 | 64.8788 | -0.18333 | 0.018409 | 0.07456 | 0.022703 | 0.062194 | 0.02041 | -0.0071622 | -0.45673 | -0.008461 | 0.048092 | 0.055652 | 0.0043349 | -0.028724 | 64.8697 | -58.0307 | 0.054932 | -58.2962 | 64.888 | -58.1451 | -58.1909 | -58.0627 | 0.33417 | -58.3832 | 64.8926 | 64.7919 | -58.1406 | -58.2642 | -0.045777 | -0.091553 | 0.009155 | 0.068664 | -0.19684 | -0.10529 | -0.009155 | -0.041199 | -0.16479 | 0.013733 | 0.036621 | -0.28381 | -0.11902 | -0.086975 | 122.9874 | 122.9691 | 58.1543 | -123.0698 | 122.9919 | 122.8912 | 58.4335 | -123.143
429.8438 | 123.1796 | -58.0811 | 64.8239 | -0.42747 | -0.016839 | 0.067083 | -0.00079616 | 0.061125 | -0.032996 | -0.015707 | 0.22992 | -0.011666 | 0.039547 | 0.058857 | 0.0011309 | -0.0041571 | 64.8468 | -57.9758 | 0.050354 | -58.3237 | 64.8102 | -58.1406 | -58.1589 | -57.9941 | 0.38452 | -58.3191 | 64.8468 | 64.7919 | -58.1314 | -58.2413 | -0.059509 | -0.07782 | -0.013733 | 0.10529 | -0.24261 | -0.16479 | 0.022888 | -0.050354 | -0.16022 | 0.022888 | 0.086975 | -0.23804 | -0.07782 | -0.032044 | 122.8912 | 122.9279 | 58.1314 | -122.9828 | 122.9279 | 122.8729 | 58.4656 | -123.0652
430.8438 | 123.2758 | -58.0444 | 64.8376 | -0.00022031 | -0.02752 | 0.085241 | -0.0018642 | 0.051512 | -0.018043 | -0.017844 | -0.090514 | -0.011666 | 0.064114 | 0.055652 | -0.0052781 | -0.0084301 | 64.9612 | -57.8934 | 0.16937 | -58.2458 | 64.8239 | -58.1039 | -58.1451 | -57.93 | 0.54474 | -58.2413 | 64.8605 | 64.7736 | -58.1085 | -58.2047 | -0.059509 | -0.10071 | -0.013732 | 0.15106 | -0.20142 | -0.10071 | 0.1236 | -0.064087 | -0.16022 | 0.022889 | 0.11444 | -0.19684 | -0.036621 | -0.064086 | 122.8683 | 123.0057 | 58.2138 | -122.9828 | 122.905 | 122.818 | 58.5892 | -123.0423
431.8438 | 123.2346 | -58.0536 | 64.8285 | 0.12185 | -0.015771 | 0.07456 | 0.0088168 | 0.054717 | 0.0033197 | -0.016776 | 0.062074 | -0.017006 | 0.031002 | 0.053516 | 0.0043349 | -0.012702 | 64.9246 | -57.9163 | 0.16479 | -58.2458 | 64.8468 | -58.1131 | -58.1406 | -57.9254 | 0.56305 | -58.2642 | 64.8788 | 64.7873 | -58.1131 | -58.2092 | -0.059509 | -0.086975 | 0.018311 | 0.13733 | -0.19226 | -0.10529 | 0.096131 | -0.059509 | -0.15564 | 0.050354 | 0.12817 | -0.21057 | -0.054931 | -0.041199 | 122.9004 | 122.9782 | 58.2184 | -122.9691 | 122.9324 | 122.8409 | 58.6166 | -123.0377
432.8438 | 123.2346 | -58.0307 | 64.8376 | 0.030298 | -0.0072259 | 0.077764 | 0.0066808 | 0.051512 | -0.010566 | -0.015707 | 0.13837 | -0.011666 | 0.056637 | 0.043903 | -0.0031411 | -0.0094981 | 64.92 | -57.9437 | 0.17395 | -58.255 | 64.8468 | -58.1131 | -58.1314 | -57.9346 | 0.54016 | -58.2962 | 64.8651 | 64.7781 | -58.1039 | -58.2092 | -0.082397 | -0.10071 | 0.009156 | 0.086975 | -0.2243 | -0.1236 | 0.082398 | -0.073242 | -0.17853 | 0.027466 | 0.096131 | -0.2655 | -0.086975 | -0.059509 | 122.8775 | 122.9507 | 58.2047 | -122.9691 | 122.8958 | 122.8088 | 58.5709 | -123.0469
433.8438 | 123.2254 | -58.0353 | 64.856 | 0.10659 | -0.0072259 | 0.090582 | -0.0029322 | 0.051512 | -0.012702 | -0.013571 | 0.046815 | -0.011666 | 0.051296 | 0.058857 | 0.0086079 | -0.01377 | 64.8972 | -57.9529 | 0.17395 | -58.2687 | 64.8743 | -58.0994 | -58.136 | -57.9575 | 0.55847 | -58.2916 | 64.8788 | 64.7598 | -58.0902 | -58.2184 | -0.064087 | -0.10071 | 0.018311 | 0.082397 | -0.23346 | -0.13275 | 0.041199 | -0.054932 | -0.18311 | 0.022888 | 0.07782 | -0.25635 | -0.073242 | -0.09613 | 122.9095 | 122.9324 | 58.2092 | -122.9919 | 122.9141 | 122.7951 | 58.5938 | -123.0743
434.8438 | 123.1934 | -58.0261 | 64.8331 | 1.251 | -0.0082939 | 0.076696 | -0.0061362 | 0.048308 | -0.01377 | -0.00075419 | 0.031556 | -0.012734 | 0.045956 | 0.050312 | 0.0011309 | -0.015907 | 64.8788 | -57.962 | 0.20599 | -58.287 | 64.8605 | -58.1223 | -58.1589 | -57.962 | 0.54016 | -58.3099 | 64.8788 | 64.7736 | -58.1131 | -58.1955 | -0.09613 | -0.13275 | 0.027466 | 0.064087 | -0.26093 | -0.12817 | 0.045776 | -0.086975 | -0.16937 | 0.045776 | 0.064087 | -0.28381 | -0.11444 | -0.059509 | 122.8867 | 122.905 | 58.2321 | -122.9919 | 122.905 | 122.7997 | 58.5663 | -123.0286
435.8438 | 123.1934 | -58.0307 | 64.8422 | 0.36599 | -0.018975 | 0.075628 | 0.020567 | 0.060057 | -0.01377 | -0.0092992 | 0.29095 | -0.02021 | 0.050228 | 0.058857 | 6.2882e-05 | -0.018043 | 64.9109 | -57.9529 | 0.30212 | -58.287 | 64.8285 | -58.0948 | -58.1268 | -57.9575 | 0.50354 | -58.3191 | 64.8788 | 64.7644 | -58.1039 | -58.2138 | -0.064087 | -0.09613 | -0.013733 | 0.07782 | -0.25635 | -0.16022 | 0.068665 | -0.073242 | -0.1831 | 0.036621 | 0.073243 | -0.28839 | -0.10529 | -0.07782 | 122.8592 | 122.9416 | 58.3328 | -122.9691 | 122.9095 | 122.7951 | 58.5342 | -123.056
436.8438 | 123.1934 | -58.049 | 64.8468 | 0.53384 | 0.0013191 | 0.086309 | 0.015226 | 0.049376 | 0.00011475 | -0.00075419 | 0.39777 | -0.012734 | 0.047024 | 0.06847 | 6.2882e-05 | -0.012702 | 64.9384 | -57.9391 | 0.35706 | -58.2687 | 64.8193 | -58.1131 | -58.1406 | -57.9254 | 0.50354 | -58.3054 | 64.8651 | 64.7736 | -58.0948 | -58.1772 | -0.064087 | -0.091553 | -0.027466 | 0.10986 | -0.21973 | -0.12817 | 0.091552 | -0.045777 | -0.12817 | 0.01831 | 0.1236 | -0.25635 | -0.12817 | -0.073242 | 122.8683 | 122.9874 | 58.4061 | -122.9874 | 122.9141 | 122.8226 | 58.5526 | -123.024
437.8438 | 123.175 | -58.0307 | 64.8422 | 0.27444 | -0.0040209 | 0.077764 | 0.00027184 | 0.05258 | -0.011634 | -0.022116 | 0.59613 | -0.012734 | 0.048092 | 0.066333 | -0.0042101 | -0.011634 | 64.9155 | -57.9483 | 0.35248 | -58.1314 | 64.888 | -58.0765 | -58.1177 | -57.962 | 0.48523 | -58.3237 | 64.8926 | 64.8148 | -58.0902 | -58.2047 | -0.045776 | -0.086975 | 0.045776 | 0.082398 | -0.10071 | -0.013733 | 0.073242 | -0.059509 | -0.17395 | 0.050354 | 0.068665 | -0.29297 | -0.11902 | -0.027466 | 122.9187 | 122.9462 | 58.3832 | -122.9599 | 122.9233 | 122.8455 | 58.5159 | -123.0469
438.8438 | 123.2025 | -58.0307 | 64.8788 | 0.36599 | -0.0018849 | 0.073492 | 0.0056128 | 0.054717 | -0.0041573 | -0.0060942 | 0.1994 | -0.013802 | 0.050228 | 0.055652 | 0.0032669 | -0.0094981 | 64.9246 | -57.9346 | 0.45319 | -58.2458 | 64.8926 | -58.0811 | -58.1268 | -57.9346 | 0.49439 | -58.2916 | 64.8926 | 64.8285 | -58.0719 | -58.1726 | -0.050354 | -0.09613 | 0.013733 | 0.096131 | -0.21515 | -0.11902 | 0.045777 | -0.041198 | -0.14191 | 0.013733 | 0.096131 | -0.26093 | -0.11902 | -0.050354 | 122.9233 | 122.9553 | 58.4839 | -123.0057 | 122.9233 | 122.8592 | 58.5251 | -123.0515
439.8438 | 123.1659 | -58.0032 | 64.8697 | 0.35073 | -0.0061569 | 0.073492 | -0.0029322 | 0.054717 | -0.0073613 | -0.011435 | 0.22992 | -0.012734 | 0.039547 | 0.063129 | 0.0054039 | -0.0084301 | 64.9292 | -57.9071 | 0.49439 | -58.2321 | 64.8651 | -58.0399 | -58.1039 | -57.9163 | 0.48981 | -58.2733 | 64.9384 | 64.8285 | -58.0811 | -58.1635 | -0.036621 | -0.10071 | -0.004578 | 0.096131 | -0.22888 | -0.12817 | 0.059509 | -0.07782 | -0.16022 | 0.068664 | 0.086975 | -0.27008 | -0.10986 | -0.041199 | 122.8683 | 122.9324 | 58.4976 | -122.9736 | 122.9416 | 122.8317 | 58.493 | -123.0331
440.8438 | 123.1796 | -58.0261 | 64.8651 | 0.4728 | -0.022179 | 0.07456 | -0.0061362 | 0.060057 | -0.0084293 | -0.010367 | 0.33673 | -0.005257 | 0.047024 | 0.063129 | 0.0075399 | -0.012702 | 64.9841 | -57.9025 | 0.55847 | -58.255 | 64.8834 | -58.0719 | -58.0994 | -57.8888 | 0.45776 | -58.287 | 64.92 | 64.8148 | -58.0811 | -58.1818 | -0.045776 | -0.073242 | 0.018311 | 0.1236 | -0.22888 | -0.15564 | 0.11902 | -0.054932 | -0.15564 | 0.054932 | 0.13733 | -0.26093 | -0.10529 | -0.050354 | 122.9095 | 123.0103 | 58.5846 | -122.9645 | 122.9462 | 122.8409 | 58.4839 | -123.0469
441.8438 | 123.1705 | -58.0215 | 64.8743 | 0.44228 | 0.0023871 | 0.071355 | 0.0034768 | 0.05258 | -0.0062933 | -0.0082312 | 0.38251 | -0.010597 | 0.042751 | 0.074878 | -0.0031411 | -0.016975 | 64.9979 | -57.8705 | 0.59509 | -58.2367 | 64.8788 | -58.0627 | -58.0856 | -57.8705 | 0.44861 | -58.2733 | 64.9017 | 64.8239 | -58.0856 | -58.1451 | -0.041199 | -0.064087 | 0.004577 | 0.15106 | -0.21515 | -0.15106 | 0.1236 | -0.064087 | -0.1236 | 0.027465 | 0.15106 | -0.25177 | -0.12817 | -0.050354 | 122.9004 | 123.0194 | 58.6166 | -122.9599 | 122.9233 | 122.8455 | 58.4702 | -123.0194
442.8438 | 123.2346 | -57.9712 | 64.8743 | 0.64065 | 0.00025114 | 0.070287 | 0.010954 | 0.048308 | 0.014001 | 0.0013818 | 0.29095 | -0.005257 | 0.047024 | 0.06847 | 0.010744 | -0.0062931 | 64.9612 | -57.8705 | 0.62256 | -58.1863 | 64.8972 | -58.049 | -58.0673 | -57.8567 | 0.41657 | -58.2367 | 64.9292 | 64.7873 | -58.0856 | -58.1497 | -0.07782 | -0.096131 | 0.022888 | 0.10071 | -0.21515 | -0.11902 | 0.086975 | -0.11444 | -0.17853 | 0.054931 | 0.11444 | -0.2655 | -0.086975 | -0.086976 | 122.8683 | 122.9324 | 58.5938 | -122.9416 | 122.9004 | 122.7585 | 58.3878 | -123.024
443.8438 | 123.2071 | -57.9895 | 64.8972 | 0.56436 | 0.014137 | 0.069219 | 0.0077488 | 0.046172 | 0.014001 | -0.0082312 | 0.38251 | -0.00098395 | 0.056637 | 0.055652 | 0.015017 | -0.021247 | 64.9658 | -57.9025 | 0.54932 | -58.223 | 64.9109 | -58.0673 | -58.1223 | -57.843 | 0.36621 | -58.255 | 64.9658 | 64.8056 | -58.0627 | -58.1543 | -0.07782 | -0.13275 | 0.013733 | 0.086975 | -0.23346 | -0.10071 | 0.068664 | -0.073242 | -0.16479 | 0.068664 | 0.14648 | -0.2655 | -0.10071 | -0.091553 | 122.9004 | 122.9553 | 58.5388 | -123.0194 | 122.9553 | 122.7951 | 58.3557 | -123.0515
444.8438 | 123.2391 | -57.9758 | 64.9109 | 0.56436 | 0.0098641 | 0.055334 | 0.0034768 | 0.062194 | -0.0030893 | -0.0050262 | 0.5351 | -0.01487 | 0.053432 | 0.069538 | 0.0075399 | -0.0041571 | 65.0299 | -57.7881 | 0.65002 | -58.1863 | 64.888 | -58.0032 | -58.0673 | -57.8201 | 0.37994 | -58.2184 | 64.9384 | 64.8376 | -58.0353 | -58.1497 | -0.027466 | -0.091553 | -0.022889 | 0.18768 | -0.21057 | -0.11902 | 0.11902 | -0.059509 | -0.17395 | 0.027465 | 0.15564 | -0.24262 | -0.068665 | -0.073243 | 122.8638 | 123.0057 | 58.6258 | -122.9782 | 122.9141 | 122.8134 | 58.3557 | -123.0606
445.8438 | 123.2117 | -57.9575 | 64.92 | 0.53384 | 0.00025114 | 0.061742 | 0.0098848 | 0.056853 | 0.0086597 | 0.00031381 | 0.39777 | -0.008461 | 0.044888 | 0.060993 | 0.0075399 | -0.01377 | 65.0253 | -57.8339 | 0.68665 | -58.1635 | 64.888 | -58.0261 | -58.0765 | -57.9758 | 0.3479 | -58.1268 | 64.9063 | 64.8468 | -58.017 | -58.1039 | -0.068665 | -0.11902 | -0.032044 | 0.1236 | -0.20599 | -0.086975 | 0.10529 | -0.05951 | -0.14648 | -0.013733 | -0.018311 | -0.16937 | -0.022888 | -0.073242 | 122.8455 | 122.9828 | 58.6441 | -122.9965 | 122.8638 | 122.8043 | 58.3054 | -123.024
446.8438 | 123.23 | -57.9803 | 64.8788 | 0.5491 | 0.014137 | 0.066015 | 0.0024088 | 0.058989 | -0.00095325 | -0.0050262 | 0.42828 | -0.004189 | 0.058773 | 0.062061 | 0.0075399 | -0.0062931 | 65.007 | -57.8613 | 0.6134 | -58.1543 | 64.9246 | -58.0444 | -58.0811 | -57.8156 | 0.29755 | -58.2138 | 64.9384 | 64.8376 | -58.0353 | -58.1268 | -0.064087 | -0.10071 | 0.045777 | 0.11902 | -0.17395 | -0.073242 | 0.12817 | -0.054931 | -0.14648 | 0.059509 | 0.1648 | -0.23346 | -0.086975 | -0.041199 | 122.905 | 122.9874 | 58.5938 | -122.9599 | 122.9187 | 122.818 | 58.2779 | -123.0057
447.8438 | 123.1888 | -57.962 | 64.92 | 0.61013 | 0.0055921 | 0.053198 | 0.0077488 | 0.050444 | 0.011865 | 0.0024508 | 0.36725 | -0.010597 | 0.067318 | 0.060993 | 0.0021989 | -0.016975 | 64.9979 | -57.8842 | 0.51727 | -58.1863 | 64.9704 | -58.0307 | -58.0353 | -57.843 | 0.24261 | -58.2275 | 64.9521 | 64.8788 | -58.017 | -58.0948 | -0.068665 | -0.073242 | 0.050354 | 0.07782 | -0.2243 | -0.15106 | 0.07782 | -0.054932 | -0.13275 | 0.032043 | 0.11902 | -0.2655 | -0.13275 | -0.041199 | 122.9324 | 122.9599 | 58.4793 | -122.9553 | 122.9141 | 122.8409 | 58.2047 | -123.0148
448.8438 | 123.1613 | -57.9712 | 64.9704 | 0.4728 | 0.0087961 | 0.080969 | 0.014158 | 0.056853 | 0.0033197 | -0.0071622 | 0.38251 | -0.004189 | 0.057705 | 0.072742 | 0.0011309 | -0.012702 | 64.9933 | -57.9163 | 0.48981 | -58.2001 | 64.9612 | -58.0032 | -58.0627 | -57.843 | 0.21057 | -58.2504 | 64.9796 | 64.9109 | -58.0215 | -58.1223 | -0.032044 | -0.091553 | -0.009155 | 0.054931 | -0.22888 | -0.13733 | 0.022888 | -0.050354 | -0.15106 | 0.009155 | 0.12817 | -0.27924 | -0.12817 | -0.059509 | 122.9324 | 122.9645 | 58.461 | -123.0331 | 122.9507 | 122.8821 | 58.1818 | -123.0927
449.8438 | 122.9462 | -58.0078 | 64.9109 | 0.41177 | 0.0055921 | 0.072424 | 0.010954 | 0.051512 | -0.00095325 | -0.0071622 | 0.2757 | -0.004189 | 0.072659 | 0.053516 | 0.0086079 | -0.014838 | 64.9384 | -57.9483 | 0.40283 | -58.2092 | 64.9979 | -58.0215 | -58.0582 | -57.9025 | 0.16937 | -58.2962 | 65.0208 | 64.9155 | -58.049 | -58.1177 | -0.013733 | -0.050355 | 0.086975 | 0.059509 | -0.20142 | -0.15106 | 0.027465 | -0.041199 | -0.10986 | 0.10986 | 0.10529 | -0.28839 | -0.17853 | 0.004577 | 123.0057 | 122.9462 | 58.4106 | -122.9691 | 123.0286 | 122.9233 | 58.1772 | -123.0286
450.8438 | 123.1018 | -57.9666 | 64.9841 | 0.2134 | 0.045112 | 0.072424 | 0.010954 | 0.062194 | 0.0054557 | 0.0067228 | 0.0010378 | -0.004189 | 0.042751 | 0.062061 | 0.023561 | -0.015907 | 64.9933 | -57.8751 | 0.30212 | -58.1818 | 65.0024 | -57.9941 | -58.0215 | -57.9163 | 0.16022 | -58.3099 | 65.0482 | 64.9704 | -58.0353 | -58.1177 | -0.027466 | -0.054931 | 0.01831 | 0.091553 | -0.21515 | -0.16022 | 0.009155 | -0.068664 | -0.15106 | 0.064087 | 0.050354 | -0.34332 | -0.19226 | -0.013733 | 122.9691 | 122.9599 | 58.2687 | -123.0057 | 123.0148 | 122.937 | 58.1268 | -123.1018
451.8438 | 123.1796 | -57.9391 | 64.9933 | 0.50332 | -0.0050889 | 0.071355 | -0.0093412 | 0.055785 | -0.037269 | -0.0060942 | 0.50458 | -0.02021 | 0.053432 | 0.064197 | 0.017153 | 0.00011494 | 65.0116 | -57.7881 | 0.31586 | -58.1406 | 64.9612 | -57.9529 | -57.9895 | -57.8156 | 0.31586 | -58.2047 | 64.9979 | 64.8926 | -57.9803 | -58.0948 | -0.013733 | -0.050354 | -0.032043 | 0.15106 | -0.20142 | -0.15106 | 0.018311 | -0.041199 | -0.15564 | 0.004578 | 0.1236 | -0.2655 | -0.10986 | -0.10071 | 122.9004 | 122.9507 | 58.255 | -122.9828 | 122.937 | 122.8317 | 58.255 | -123.0881
452.8438 | 123.0972 | -57.9575 | 64.9979 | 0.48806 | 0.033363 | 0.062811 | 0.023771 | 0.053649 | 0.0075917 | -0.016776 | -0.73138 | -0.005257 | 0.059841 | 0.05672 | 0.016085 | -0.012702 | 64.9841 | -57.8796 | 0.25635 | -58.3466 | 64.9521 | -58.0124 | -58.0582 | -57.8476 | 0.22888 | -58.2733 | 65.0436 | 64.9612 | -58.0124 | -58.0902 | -0.054932 | -0.10071 | -0.045777 | 0.077819 | -0.3891 | -0.28839 | -0.013733 | -0.054932 | -0.13275 | 0.045776 | 0.10986 | -0.31586 | -0.1831 | -0.036621 | 122.9095 | 122.9416 | 58.2138 | -123.056 | 123.0011 | 122.9187 | 58.1863 | -123.0881
453.8438 | 122.9553 | -57.962 | 64.9384 | 0.35073 | 0.036567 | 0.0799 | 0.014158 | 0.054717 | 0.0065237 | -0.0028902 | 0.35199 | -0.00098395 | 0.068386 | 0.075946 | 0.0032669 | -0.0084301 | 64.9979 | -57.8979 | 0.13733 | -58.1772 | 65.0253 | -57.9849 | -58.0261 | -57.8567 | 0.2655 | -58.2825 | 65.0757 | 64.9887 | -58.0032 | -58.1039 | -0.022888 | -0.064087 | 0.086976 | 0.064087 | -0.21515 | -0.15106 | 0.05951 | -0.041199 | -0.14191 | 0.13733 | 0.10529 | -0.32044 | -0.17853 | 0.050354 | 122.9874 | 122.9599 | 58.0994 | -122.9645 | 123.0377 | 122.9507 | 58.2275 | -123.0423
454.8438 | 123.1064 | -57.9346 | 65.0253 | 0.25918 | 0.033363 | 0.0799 | 0.021635 | 0.06967 | 0.014001 | -0.0060942 | 0.24518 | -0.002053 | 0.044888 | 0.055652 | 0.011812 | -0.021247 | 65.0116 | -57.8751 | 0.09613 | -58.1497 | 65.0345 | -57.9849 | -58.0307 | -57.8796 | 0.32501 | -58.2733 | 65.0711 | 64.9933 | -57.9712 | -58.0856 | -0.050354 | -0.096131 | 0.009155 | 0.059509 | -0.21515 | -0.11902 | -0.013733 | -0.036621 | -0.15106 | 0.045776 | 0.054931 | -0.33874 | -0.18768 | -0.032044 | 122.9691 | 122.9462 | 58.0307 | -123.056 | 123.0057 | 122.9279 | 58.2596 | -123.111
455.8438 | 123.0972 | -57.9071 | 65.0528 | 0.13711 | 0.041908 | 0.083105 | 0.0056128 | 0.062194 | 0.014001 | 0.0077908 | 0.092591 | -0.007393 | 0.072659 | 0.058857 | 0.018221 | -0.011634 | 65.0436 | -57.811 | 0.11902 | -58.1223 | 65.0482 | -57.962 | -57.9758 | -57.8384 | 0.39825 | -58.2275 | 65.094 | 65.0253 | -57.9712 | -58.0582 | -0.054932 | -0.068665 | -0.004577 | 0.09613 | -0.21515 | -0.14648 | -0.009155 | -0.064087 | -0.15106 | 0.041199 | 0.068664 | -0.32044 | -0.16937 | -0.027465 | 122.9553 | 122.9507 | 58.0261 | -123.0286 | 123.0011 | 122.9324 | 58.3054 | -123.111
456.8438 | 123.2254 | -57.8613 | 65.0391 | -0.030737 | -0.013634 | -0.090998 | 0.0024088 | 0.063262 | -0.046882 | -0.0071622 | 0.092591 | -0.013802 | 0.039547 | 0.053516 | -0.0052781 | 0.0022509 | 65.094 | -57.6874 | 0.2655 | -58.0399 | 65.0574 | -57.9163 | -57.9575 | -57.7057 | 0.60883 | -58.0399 | 65.0574 | 64.9796 | -57.9163 | -58.0078 | -0.054932 | -0.09613 | 0.018311 | 0.17395 | -0.17853 | -0.082398 | 0.054932 | -0.054932 | -0.14648 | 0.018311 | 0.15564 | -0.17853 | -0.032044 | -0.059509 | 122.9187 | 122.9553 | 58.1268 | -122.9965 | 122.9187 | 122.8409 | 58.4702 | -123.0469
457.8438 | 123.1567 | -57.8522 | 65.0482 | -0.10703 | 0.024818 | 0.063879 | 0.0045448 | 0.056853 | 0.0075917 | -0.0039582 | -0.13629 | -0.006325 | 0.056637 | 0.055652 | -0.0010051 | -0.018043 | 65.1443 | -57.724 | 0.20599 | -58.0536 | 65.0757 | -57.9071 | -57.9483 | -57.7423 | 0.5127 | -58.1314 | 65.1031 | 65.0162 | -57.9437 | -58.0307 | -0.054931 | -0.09613 | 0.027466 | 0.12817 | -0.20142 | -0.10529 | 0.09613 | -0.091553 | -0.17853 | 0.054931 | 0.10986 | -0.27924 | -0.10071 | -0.032044 | 122.9279 | 122.9965 | 58.0582 | -122.9965 | 122.9553 | 122.8683 | 58.3649 | -123.0789
458.8438 | 123.0881 | -57.8979 | 65.0803 | 0.13711 | 0.018409 | 0.059606 | 0.0098848 | 0.061125 | 0.0065237 | -0.0092992 | 0.10785 | -0.003121 | 0.043819 | 0.059925 | 0.0043349 | -0.016975 | 65.1077 | -57.756 | 0.19226 | -58.0948 | 65.1077 | -57.8888 | -57.9529 | -57.7698 | 0.48981 | -58.1818 | 65.1031 | 65.0208 | -57.9483 | -58.0582 | 0.009155 | -0.054932 | 0.027466 | 0.14191 | -0.19684 | -0.14191 | 0.027466 | -0.050354 | -0.16022 | 0.022888 | 0.12817 | -0.28381 | -0.1236 | -0.059509 | 123.0057 | 123.0057 | 58.0902 | -123.0331 | 123.0011 | 122.9187 | 58.3878 | -123.1384
459.8438 | 123.1338 | -57.8705 | 65.0803 | -0.64109 | 0.039771 | 0.072424 | 0.017362 | 0.065398 | -0.0020213 | 0.0024508 | 0.046815 | 0.001152 | 0.055569 | 0.063129 | -0.0052781 | -0.014838 | 65.1581 | -57.6874 | 0.3067 | -58.0307 | 65.0986 | -57.8842 | -57.9391 | -57.724 | 0.56305 | -58.1314 | 65.126 | 65.0482 | -57.9117 | -58.0124 | -0.013733 | -0.068665 | 0.018311 | 0.1831 | -0.16022 | -0.091553 | 0.07782 | -0.041199 | -0.14191 | 0.045777 | 0.14648 | -0.26093 | -0.11902 | -0.032043 | 122.9691 | 123.0286 | 58.1772 | -123.0194 | 122.9965 | 122.9187 | 58.4335 | -123.0927
460.8438 | 123.1567 | -57.8522 | 65.094 | -0.00022031 | 0.04084 | 0.069219 | 0.014158 | 0.061125 | 0.00011475 | -0.0060942 | -0.059997 | -0.009529 | 0.068386 | 0.053516 | 0.0096759 | -0.0041571 | 65.1398 | -57.6874 | 0.29297 | -58.049 | 65.0757 | -57.9208 | -57.9254 | -57.7332 | 0.59052 | -58.0902 | 65.1215 | 65.0482 | -57.9163 | -58.0032 | -0.068664 | -0.073242 | -0.01831 | 0.16479 | -0.19684 | -0.1236 | 0.045777 | -0.064087 | -0.15106 | 0.027466 | 0.11902 | -0.23804 | -0.086975 | -0.045776 | 122.9279 | 122.9919 | 58.1451 | -123.0194 | 122.9736 | 122.9004 | 58.4427 | -123.0972
461.8438 | 123.1567 | -57.8613 | 65.1077 | 0.42703 | 0.0066601 | 0.078832 | 0.0034768 | 0.055785 | -0.0052253 | -0.00075419 | 0.44354 | -0.007393 | 0.058773 | 0.062061 | -0.0031411 | -0.0073621 | 65.0894 | -57.7744 | -0.15564 | -58.0673 | 65.0894 | -57.8934 | -57.9391 | -57.7469 | 0.52185 | -58.1451 | 65.1443 | 65.0528 | -57.9025 | -58.0124 | -0.032044 | -0.07782 | -0.01831 | 0.086975 | -0.20599 | -0.12817 | -0.01831 | -0.041199 | -0.15106 | 0.036621 | 0.11444 | -0.28381 | -0.13275 | -0.054932 | 122.9507 | 122.9507 | 57.7057 | -123.0469 | 123.0057 | 122.9141 | 58.3832 | -123.1201
462.8438 | 123.1476 | -57.811 | 65.126 | -0.091772 | 0.019477 | 0.076696 | 0.020567 | 0.046172 | -0.00095325 | -0.010367 | -0.075256 | -0.010597 | 0.060909 | 0.057788 | -0.0010051 | -0.015907 | 65.1581 | -57.6462 | -0.091553 | -58.0078 | 65.1398 | -57.8659 | -57.9025 | -57.6691 | 0.64545 | -58.0719 | 65.1672 | 65.0986 | -57.8522 | -57.9758 | -0.054932 | -0.091553 | 0.013733 | 0.1648 | -0.19684 | -0.10529 | 0.032043 | -0.041199 | -0.16479 | 0.041198 | 0.14191 | -0.26093 | -0.09613 | -0.027466 | 122.9507 | 122.9691 | 57.7194 | -123.0286 | 122.9782 | 122.9095 | 58.4564 | -123.1018
463.8438 | 123.1522 | -57.8156 | 65.1718 | -0.25962 | 0.016273 | 0.073492 | 0.016294 | 0.054717 | -0.011634 | 0.0024508 | -0.22784 | -0.011666 | 0.055569 | 0.057788 | -0.0052781 | -0.0073621 | 65.0986 | -57.7103 | -0.15564 | -58.0124 | 65.1764 | -57.8476 | -57.9163 | -57.7057 | 0.67291 | -58.0765 | 65.2313 | 65.1398 | -57.8659 | -57.9666 | -0.032043 | -0.10071 | 0.004578 | 0.10529 | -0.19684 | -0.09613 | -0.073242 | -0.050354 | -0.15106 | 0.059509 | 0.10986 | -0.26093 | -0.10986 | -0.032043 | 122.9919 | 122.9141 | 57.6599 | -123.0881 | 123.0469 | 122.9553 | 58.4885 | -123.1384
464.8438 | 123.1293 | -57.7972 | 65.1627 | -0.10703 | 0.0087961 | 0.066015 | 0.024839 | 0.073943 | -0.0084293 | 0.0045868 | -0.19733 | -0.006325 | 0.065182 | 0.064197 | 6.2882e-05 | -0.012702 | 65.1443 | -57.6508 | -0.20142 | -57.9758 | 65.1855 | -57.8156 | -57.8796 | -57.6508 | 0.75531 | -58.0536 | 65.2039 | 65.1215 | -57.8613 | -57.9163 | -0.018311 | -0.082398 | 0.022888 | 0.14648 | -0.17853 | -0.09613 | -0.018311 | -0.064087 | -0.11902 | 0.041198 | 0.14648 | -0.25635 | -0.13733 | -0.041199 | 122.9828 | 122.9416 | 57.5958 | -123.0423 | 123.0011 | 122.9187 | 58.5526 | -123.0789
465.8438 | 123.1705 | -57.7927 | 65.1672 | -0.15281 | 0.049385 | 0.072424 | 0.023771 | 0.057921 | 0.0075917 | -0.0028902 | -0.16681 | -0.009529 | 0.056637 | 0.054584 | 6.2882e-05 | -0.010566 | 65.181 | -57.5867 | -0.1831 | -57.9575 | 65.1855 | -57.843 | -57.8705 | -57.6324 | 0.87891 | -58.049 | 65.2176 | 65.1215 | -57.8613 | -57.9483 | -0.050354 | -0.077819 | 0.018311 | 0.20599 | -0.16479 | -0.086975 | 0.013733 | -0.068664 | -0.15564 | 0.050354 | 0.16022 | -0.25635 | -0.10071 | -0.045776 | 122.9782 | 122.9736 | 57.6096 | -123.0377 | 123.0103 | 122.9141 | 58.6716 | -123.1155
466.8438 | 123.2208 | -57.7835 | 65.1123 | 4.2265 | 0.0077281 | 0.082037 | 0.0066808 | 0.055785 | -0.022315 | -0.0060942 | 0.59613 | -0.015938 | 0.056637 | 0.054584 | -0.011686 | 0.0011829 | 65.2176 | -57.5455 | -0.26093 | -57.9391 | 65.1306 | -57.7789 | -57.8339 | -57.5684 | 1.1398 | -57.9758 | 65.1535 | 65.0803 | -57.8247 | -57.9163 | 0.004577 | -0.050354 | 0.01831 | 0.23804 | -0.15564 | -0.10529 | 0.10528 | -0.041199 | -0.13275 | 0.041198 | 0.21515 | -0.19226 | -0.059509 | -0.032044 | 122.9141 | 123.0011 | 57.5226 | -122.9462 | 122.937 | 122.8638 | 58.9233 | -123.0286
467.8438 | 123.1201 | -57.7652 | 65.213 | -0.21384 | 0.030158 | 0.069219 | 0.0098848 | 0.054717 | 0.0054557 | -0.0082312 | -0.28888 | -0.007393 | 0.056637 | 0.048175 | 0.0011309 | -0.020179 | 65.2222 | -57.5729 | -0.2655 | -57.9437 | 65.2725 | -57.7835 | -57.8201 | -57.5821 | 1.2634 | -57.9941 | 65.2588 | 65.1764 | -57.7927 | -57.8934 | -0.01831 | -0.054931 | 0.059509 | 0.19226 | -0.17853 | -0.1236 | 0.009155 | -0.027466 | -0.12817 | 0.045776 | 0.18311 | -0.22888 | -0.10071 | -0.036621 | 123.0377 | 122.9874 | 57.4997 | -123.0331 | 123.024 | 122.9416 | 59.0286 | -123.1064
468.8438 | 123.1567 | -57.7286 | 65.2313 | -0.15281 | 0.012 | 0.071355 | 0.024839 | 0.060057 | 0.00011475 | -0.018912 | -0.27362 | 0.001152 | 0.054501 | 0.052448 | 0.0064719 | -0.0094981 | 65.1993 | -57.5729 | -0.21515 | -57.9254 | 65.2496 | -57.7606 | -57.8522 | -57.5821 | 1.3092 | -58.017 | 65.2771 | 65.1672 | -57.7927 | -57.8613 | -0.032043 | -0.1236 | 0.018311 | 0.15564 | -0.19684 | -0.073242 | -0.032043 | -0.064087 | -0.13275 | 0.045777 | 0.14648 | -0.28839 | -0.15564 | -0.064087 | 122.9782 | 122.9279 | 57.5134 | -123.0835 | 123.0057 | 122.8958 | 59.0378 | -123.0927
469.8438 | 123.1247 | -57.7194 | 65.2405 | -0.21384 | 0.024818 | 0.085241 | 0.023771 | 0.050444 | -0.0052253 | -0.0060942 | -0.27362 | -0.012734 | 0.045956 | 0.059925 | -0.0020731 | -0.014838 | 65.213 | -57.5455 | -0.20599 | -57.9071 | 65.2634 | -57.756 | -57.811 | -57.5729 | 1.3733 | -57.9987 | 65.2908 | 65.2176 | -57.7972 | -57.8796 | -0.036621 | -0.091553 | 0.022888 | 0.17395 | -0.18768 | -0.09613 | -0.027466 | -0.07782 | -0.16022 | 0.050354 | 0.14648 | -0.27924 | -0.11902 | -0.022889 | 122.9828 | 122.9324 | 57.5134 | -123.0515 | 123.0103 | 122.937 | 59.0927 | -123.1201
470.8438 | 123.1018 | -57.7103 | 65.2817 | -0.10703 | -0.0040209 | 0.083105 | 0.019498 | 0.053649 | -0.01377 | -0.015707 | -0.3194 | -0.013802 | 0.038479 | 0.05672 | -0.0052781 | -0.01377 | 65.2084 | -57.5272 | -0.21057 | -57.9163 | 65.3 | -57.7423 | -57.7606 | -57.5638 | 1.3824 | -57.9941 | 65.3137 | 65.2359 | -57.7423 | -57.8567 | -0.032044 | -0.050354 | 0.018311 | 0.1831 | -0.20599 | -0.15564 | -0.073242 | -0.032044 | -0.14648 | 0.032044 | 0.14648 | -0.28381 | -0.13733 | -0.045776 | 123.0103 | 122.9187 | 57.4997 | -123.0423 | 123.024 | 122.9462 | 59.0927 | -123.1384
471.8438 | 123.1155 | -57.724 | 65.2679 | -0.3054 | -0.0072259 | 0.072424 | 0.017362 | 0.062194 | -0.0030893 | -0.02532 | -0.18207 | -0.013802 | 0.048092 | 0.065265 | 6.2882e-05 | -0.010566 | 65.3732 | -57.5409 | 0.9613 | -57.9987 | 65.2863 | -57.7606 | -57.8247 | -57.5546 | 1.4053 | -58.0078 | 65.3229 | 65.2267 | -57.7881 | -57.8842 | -0.036621 | -0.10071 | 0.018311 | 0.1831 | -0.27466 | -0.17395 | 0.10529 | -0.064087 | -0.16022 | 0.054932 | 0.16937 | -0.28381 | -0.1236 | -0.041198 | 123.0103 | 123.0972 | 58.6853 | -123.0927 | 123.0469 | 122.9507 | 59.1293 | -123.1522
472.8438 | 123.1247 | -57.724 | 65.2634 | -0.15281 | -0.00081686 | 0.085241 | 0.026975 | 0.057921 | -0.0084293 | -0.011435 | -0.28888 | -0.005257 | 0.035275 | 0.05672 | 0.0032669 | -0.018043 | 65.2039 | -57.4997 | 1.1765 | -57.8979 | 65.2954 | -57.7332 | -57.7789 | -57.5455 | 1.2909 | -57.9895 | 65.3137 | 65.2267 | -57.7835 | -57.8476 | -0.009155 | -0.054932 | 0.032043 | 0.2243 | -0.17395 | -0.11902 | -0.05951 | -0.059509 | -0.1236 | 0.050354 | 0.17853 | -0.2655 | -0.14191 | -0.036621 | 123.0194 | 122.9279 | 58.9005 | -123.0423 | 123.0377 | 122.9507 | 59.0149 | -123.111
473.8438 | 123.1018 | -57.6828 | 65.2954 | -1.0073 | 0.018409 | 0.072424 | 0.010954 | 0.050444 | -0.0084293 | -0.010367 | -0.2431 | -0.003121 | 0.050228 | 0.058857 | 0.0054039 | -0.0030891 | 65.2084 | -57.4677 | 1.3596 | -57.8796 | 65.2954 | -57.7148 | -57.7789 | -57.5317 | 1.2589 | -57.9941 | 65.3229 | 65.2451 | -57.7286 | -57.8339 | -0.032044 | -0.096131 | 0 | 0.21515 | -0.19684 | -0.10071 | -0.086975 | -0.045777 | -0.15106 | 0.027466 | 0.15106 | -0.31128 | -0.16022 | -0.050354 | 122.9782 | 122.8912 | 59.0424 | -123.0743 | 123.0057 | 122.9279 | 58.9417 | -123.1293
474.8438 | 123.111 | -57.6782 | 65.3046 | -0.3054 | 0.014137 | 0.084173 | 0.014158 | 0.062194 | -0.011634 | -0.0028902 | -0.34991 | -0.019142 | 0.047024 | 0.059925 | -0.0063461 | -0.011634 | 65.2359 | -57.486 | 1.5335 | -57.7286 | 65.3458 | -57.6645 | -57.7423 | -57.5226 | 1.2589 | -57.9437 | 65.3412 | 65.2588 | -57.724 | -57.8247 | 0.013733 | -0.064087 | 0.041199 | 0.19226 | -0.050354 | 0.013733 | -0.068664 | -0.045776 | -0.14648 | 0.036622 | 0.15564 | -0.2655 | -0.11902 | -0.045776 | 123.024 | 122.9141 | 59.2117 | -123.0469 | 123.0194 | 122.937 | 58.9371 | -123.1293
475.8438 | 123.1018 | -57.6736 | 65.332 | -0.33591 | -0.0082939 | 0.087377 | 0.010954 | 0.049376 | -0.0062933 | -0.011435 | -0.18207 | -0.005257 | 0.061977 | 0.046039 | 0.011812 | -0.011634 | 65.2451 | -57.4356 | 1.6846 | -57.8567 | 65.3229 | -57.6736 | -57.7377 | -57.5226 | 1.5152 | -57.7972 | 65.4144 | 65.3 | -57.6828 | -57.8293 | 0 | -0.064087 | -0.009155 | 0.23804 | -0.1831 | -0.11902 | -0.086975 | -0.009155 | -0.15564 | 0.082398 | 0.15106 | -0.1236 | 0.032044 | -0.032043 | 122.9965 | 122.9187 | 59.3582 | -123.0698 | 123.0881 | 122.9736 | 59.1888 | -123.1613
476.8438 | 123.1659 | -57.6416 | 65.3275 | -0.25962 | -0.011498 | 0.080969 | 0.01309 | 0.051512 | -0.019111 | -0.021048 | -0.19733 | -0.013802 | 0.06625 | 0.055652 | -0.0052781 | -0.015907 | 65.3412 | -57.3074 | 1.9089 | -57.7881 | 65.2908 | -57.637 | -57.7011 | -57.4127 | 1.4191 | -57.8659 | 65.3366 | 65.2542 | -57.6828 | -57.7972 | 0.004578 | -0.059509 | -0.036621 | 0.33417 | -0.14648 | -0.086975 | 0.013733 | -0.041198 | -0.15564 | 0.009155 | 0.22888 | -0.2243 | -0.068665 | -0.073243 | 122.9324 | 122.9828 | 59.5505 | -123.0286 | 122.9782 | 122.8958 | 59.0607 | -123.1247
477.8438 | 123.2025 | -57.5638 | 65.3641 | -0.24436 | -0.013634 | 0.082037 | 0.0024088 | 0.060057 | -0.019111 | -0.013571 | -0.22784 | -0.022347 | 0.059841 | 0.052448 | -0.0074141 | -0.01377 | 65.4053 | -57.2433 | 2.1515 | -57.7423 | 65.3366 | -57.5775 | -57.6553 | -57.3395 | 0.97961 | -57.811 | 65.3458 | 65.3046 | -57.6416 | -57.7469 | -0.013733 | -0.091552 | -0.027466 | 0.32044 | -0.17853 | -0.086976 | 0.041198 | -0.07782 | -0.1831 | -0.018311 | 0.2243 | -0.24719 | -0.064087 | -0.05951 | 122.9004 | 122.9691 | 59.7153 | -123.0194 | 122.9095 | 122.8683 | 58.5434 | -123.111
478.8438 | 123.1338 | -57.5729 | 65.4053 | -0.24436 | -0.0029529 | 0.07456 | 0.0056128 | 0.062194 | -0.020179 | -0.017844 | -0.33466 | -0.012734 | 0.063046 | 0.059925 | 0.0032669 | -0.018043 | 65.4099 | -57.2617 | 2.0508 | -57.7377 | 65.3641 | -57.5958 | -57.6736 | -57.3486 | 0.88348 | -57.8293 | 65.4099 | 65.3 | -57.6462 | -57.7148 | -0.022888 | -0.10071 | -0.041198 | 0.31128 | -0.16479 | -0.064087 | 0.004578 | -0.073242 | -0.14191 | 0.004578 | 0.2243 | -0.25635 | -0.11444 | -0.10528 | 122.937 | 122.9828 | 59.6237 | -123.0789 | 122.9828 | 122.8729 | 58.4564 | -123.1201
479.8438 | 123.0927 | -57.5684 | 65.3778 | -0.32065 | -0.0072259 | 0.083105 | 0.0034768 | 0.051512 | -0.0062933 | -0.01998 | -0.38043 | -0.01487 | 0.033138 | 0.059925 | -0.0052781 | -0.0084301 | 65.3687 | -57.2525 | 2.124 | -57.7972 | 65.4099 | -57.5912 | -57.6416 | -57.3578 | 1.9958 | -57.8705 | 65.4465 | 65.3549 | -57.6508 | -57.724 | -0.022889 | -0.073243 | 0.032043 | 0.31586 | -0.22888 | -0.15564 | -0.009156 | -0.082398 | -0.15564 | 0.068664 | 0.21057 | -0.30212 | -0.14648 | -0.022889 | 122.9782 | 122.937 | 59.6924 | -123.0194 | 123.0148 | 122.9233 | 59.5642 | -123.1018
480.8438 | 123.1201 | -57.5592 | 65.3915 | -0.24436 | -0.023247 | 0.071355 | 0.0066808 | 0.068602 | -0.0073613 | -0.0082312 | -0.27362 | -0.019142 | 0.047024 | 0.053516 | -0.0074141 | -0.014838 | 65.4007 | -57.2296 | 2.243 | -57.7286 | 65.3778 | -57.6096 | -57.6508 | -57.3166 | 2.1835 | -57.8567 | 65.4236 | 65.3549 | -57.6324 | -57.7194 | -0.050354 | -0.091553 | -0.013733 | 0.32959 | -0.16937 | -0.07782 | 0.009155 | -0.073242 | -0.16022 | 0.032043 | 0.24262 | -0.29755 | -0.13733 | -0.036622 | 122.937 | 122.9599 | 59.8022 | -123.0423 | 122.9828 | 122.9141 | 59.7427 | -123.111
481.8438 | 123.143 | -57.5226 | 65.4282 | -0.16807 | -0.0040209 | 0.087377 | 0.0056128 | 0.058989 | -0.0084293 | -0.016776 | -0.21259 | -0.007393 | 0.051296 | 0.040699 | 0.0043349 | -0.012702 | 65.4419 | -57.1609 | 2.3117 | -57.6965 | 65.4007 | -57.55 | -57.5912 | -57.2617 | 2.2705 | -57.7789 | 65.4327 | 65.3366 | -57.5821 | -57.6874 | -0.027466 | -0.068665 | -0.027466 | 0.36163 | -0.17395 | -0.10529 | 0.013733 | -0.059509 | -0.1648 | 0.004577 | 0.26093 | -0.25635 | -0.091553 | -0.091553 | 122.9233 | 122.9645 | 59.8343 | -123.0194 | 122.9553 | 122.8592 | 59.7931 | -123.1155
482.8438 | 123.1476 | -57.5134 | 65.4419 | -0.16807 | 0.0034561 | 0.085241 | 0.0045448 | 0.057921 | -0.0041573 | -0.015707 | -0.36517 | -0.005257 | 0.051296 | 0.055652 | -0.0042101 | -0.016975 | 65.4877 | -57.1243 | 2.3804 | -57.6599 | 65.4099 | -57.5272 | -57.6004 | -57.2113 | 2.2888 | -57.724 | 65.4694 | 65.3915 | -57.5638 | -57.6324 | -0.013733 | -0.086975 | -0.032044 | 0.3891 | -0.14648 | -0.059509 | 0.045776 | -0.050354 | -0.11902 | 0.027465 | 0.30212 | -0.21057 | -0.091553 | -0.050354 | 122.9233 | 123.0011 | 59.8938 | -123.0423 | 122.9828 | 122.905 | 59.8022 | -123.0743
483.8438 | 123.2071 | -57.4631 | 65.4282 | 0.12185 | -0.020043 | 0.086309 | 0.012022 | 0.049376 | -0.020179 | -0.014639 | -0.15155 | -0.028755 | 0.052364 | 0.046039 | -0.0020731 | -0.018043 | 65.5243 | -57.0511 | 2.5497 | -57.6324 | 65.4327 | -57.518 | -57.5638 | -57.1564 | 2.3895 | -57.6691 | 65.451 | 65.3595 | -57.5409 | -57.6141 | -0.054931 | -0.10071 | 0.004577 | 0.41199 | -0.16937 | -0.068664 | 0.09613 | -0.07782 | -0.15106 | 0.022888 | 0.3067 | -0.20599 | -0.054931 | -0.068665 | 122.8958 | 122.9874 | 60.0128 | -122.9919 | 122.9141 | 122.8226 | 59.8526 | -123.0423
484.8438 | 123.2574 | -57.431 | 65.4053 | -0.015478 | -0.0072259 | 0.086309 | 0.0066808 | 0.04724 | -0.015906 | -0.0060942 | 0.092591 | -0.026619 | 0.050228 | 0.059925 | -0.0042101 | -0.0084301 | 65.506 | -57.0465 | 2.5635 | -57.637 | 65.4327 | -57.5363 | -57.5409 | -57.0831 | 2.4902 | -57.6324 | 65.4648 | 65.3641 | -57.5089 | -57.6141 | -0.10529 | -0.10986 | 0.027466 | 0.38452 | -0.20599 | -0.09613 | 0.10071 | -0.07782 | -0.18311 | 0.05951 | 0.3479 | -0.20142 | -0.01831 | -0.041198 | 122.8638 | 122.937 | 59.9945 | -122.9462 | 122.8958 | 122.7951 | 59.9213 | -123.0194
485.8438 | 123.1567 | -57.4356 | 65.4648 | 0.091333 | 0.0013191 | 0.072424 | -0.0093412 | 0.06433 | -0.01377 | -0.011435 | -0.3194 | -0.01487 | 0.060909 | 0.046039 | 0.0075399 | -0.020179 | 65.5426 | -57.0099 | 2.7695 | -57.605 | 65.4785 | -57.4951 | -57.5226 | -57.1014 | 2.5452 | -57.6736 | 65.5106 | 65.4099 | -57.5089 | -57.6004 | -0.059509 | -0.086975 | 0.013733 | 0.42572 | -0.16937 | -0.082397 | 0.07782 | -0.073242 | -0.16479 | 0.045776 | 0.33417 | -0.23804 | -0.073242 | -0.054932 | 122.9141 | 122.9782 | 60.2051 | -122.9874 | 122.9462 | 122.8455 | 59.9808 | -123.0652
486.8438 | 123.2391 | -57.4219 | 65.4922 | -0.091772 | -0.014702 | 0.092718 | -0.0082732 | 0.04724 | -0.0094983 | -0.0071622 | -0.21259 | -0.007393 | 0.04916 | 0.054584 | 6.2882e-05 | -0.012702 | 65.506 | -56.9092 | 2.8015 | -57.5821 | 65.506 | -57.4539 | -57.5317 | -57.0511 | 2.5818 | -57.6279 | 65.5014 | 65.4099 | -57.4722 | -57.5729 | -0.032043 | -0.10986 | 0.013732 | 0.5127 | -0.16022 | -0.050354 | 0.013732 | -0.050354 | -0.15106 | 0.009155 | 0.37079 | -0.20599 | -0.054932 | -0.082398 | 122.9279 | 122.9279 | 60.2234 | -123.024 | 122.9233 | 122.8317 | 60.0037 | -123.0652
487.8438 | 123.2071 | -57.3807 | 65.5106 | -0.18333 | -0.0040209 | 0.064947 | 0.01843 | 0.06433 | -0.019111 | -0.0028902 | -0.73138 | -0.012734 | 0.039547 | 0.053516 | 0.0086079 | -0.020179 | 65.625 | -56.9092 | 2.829 | -57.5592 | 65.5014 | -57.4219 | -57.4677 | -57.0374 | 2.7374 | -57.6187 | 65.5106 | 65.4419 | -57.4265 | -57.5409 | -0.041199 | -0.086975 | -0.009155 | 0.4715 | -0.17853 | -0.091553 | 0.11444 | -0.045777 | -0.16022 | 0 | 0.34332 | -0.23804 | -0.077819 | -0.068664 | 122.8821 | 123.0057 | 60.2097 | -122.9782 | 122.8912 | 122.8226 | 60.1181 | -123.0515
488.8438 | 123.1247 | -57.3853 | 65.5518 | 0.015039 | 0.038703 | 0.061742 | 0.021635 | 0.06433 | 0.02041 | -0.0039582 | -0.67035 | 0.001152 | 0.061977 | 0.054584 | 0.01288 | -0.031928 | 65.6113 | -56.9595 | 2.829 | -57.6965 | 65.5563 | -57.4265 | -57.486 | -56.9962 | 2.655 | -57.6553 | 65.5792 | 65.4831 | -57.431 | -57.5455 | -0.041199 | -0.10071 | 0.004577 | 0.42572 | -0.31128 | -0.21057 | 0.059509 | -0.045776 | -0.16022 | 0.027466 | 0.3891 | -0.27008 | -0.10986 | -0.068665 | 122.9416 | 122.9965 | 60.2142 | -123.0377 | 122.9645 | 122.8683 | 60.0403 | -123.0972
489.8438 | 123.2666 | -57.3257 | 65.5472 | 0.060816 | -0.011498 | 0.077764 | -0.0040002 | 0.054717 | -0.031928 | -0.014639 | -0.075256 | -0.02021 | 0.054501 | 0.063129 | -0.0063461 | -0.01377 | 65.6479 | -56.8497 | 2.8152 | -57.4997 | 65.5472 | -57.3853 | -57.4219 | -56.9 | 2.7145 | -57.5089 | 65.5655 | 65.4968 | -57.3624 | -57.486 | -0.059509 | -0.09613 | 0 | 0.47607 | -0.17395 | -0.07782 | 0.10071 | -0.036621 | -0.16022 | 0.018311 | 0.42572 | -0.18311 | -0.022888 | -0.050354 | 122.8729 | 122.9736 | 60.141 | -122.9691 | 122.8912 | 122.8226 | 60.0403 | -123.0331
490.8438 | 123.23 | -57.3212 | 65.5518 | 0.060816 | -0.020043 | 0.0799 | 0.0066808 | 0.054717 | -0.0030893 | -0.014639 | 0.10785 | -0.027687 | 0.052364 | 0.067401 | -0.0010051 | 0.00011494 | 65.6021 | -56.8817 | 2.7512 | -57.5089 | 65.6067 | -57.3853 | -57.4219 | -56.9183 | 2.6733 | -57.5455 | 65.5884 | 65.4922 | -57.3853 | -57.486 | -0.064087 | -0.10071 | 0.054931 | 0.43945 | -0.18768 | -0.086975 | 0.050354 | -0.064087 | -0.16479 | 0.036621 | 0.40283 | -0.2243 | -0.059509 | -0.059509 | 122.9279 | 122.9233 | 60.0723 | -122.9736 | 122.9095 | 122.8134 | 59.9945 | -123.0377
491.8438 | 123.1613 | -57.28 | 65.6296 | 0.67117 | -0.020043 | 0.073492 | 0.017362 | 0.062194 | -0.014838 | -0.022116 | 0.12311 | -0.010597 | 0.037411 | 0.067401 | 6.2882e-05 | -0.022315 | 65.6204 | -56.8451 | 2.7237 | -57.486 | 65.6433 | -57.3257 | -57.3624 | -56.8771 | 2.6413 | -57.5272 | 65.657 | 65.5334 | -57.3212 | -57.4402 | -0.045777 | -0.082398 | 0.013733 | 0.43487 | -0.20599 | -0.1236 | -0.009156 | -0.041199 | -0.16022 | 0.027465 | 0.40283 | -0.24719 | -0.086975 | -0.096131 | 122.9233 | 122.9004 | 60.0037 | -122.9919 | 122.937 | 122.8134 | 59.9213 | -123.0698
492.8438 | 123.2437 | -57.2205 | 65.6754 | -0.13755 | -0.016839 | 0.076696 | 0.010954 | 0.051512 | -0.018043 | -0.015707 | -0.12103 | -0.011666 | 0.052364 | 0.059925 | -0.0010051 | -0.018043 | 65.7623 | -56.6986 | 2.8152 | -57.3853 | 65.6662 | -57.2617 | -57.3257 | -56.7947 | 2.7786 | -57.431 | 65.6937 | 65.5838 | -57.3212 | -57.399 | -0.041199 | -0.10529 | -0.009155 | 0.52185 | -0.1648 | -0.059509 | 0.086975 | -0.10071 | -0.17853 | 0.018311 | 0.42572 | -0.21057 | -0.032043 | -0.091553 | 122.8867 | 122.9828 | 60.0357 | -123.0011 | 122.9141 | 122.8043 | 59.9991 | -123.0743
493.8438 | 123.2529 | -57.1655 | 65.6982 | -0.091772 | -0.012566 | 0.082037 | 0.023771 | 0.057921 | -0.012702 | -0.0018222 | -0.10577 | -0.024483 | 0.034206 | 0.058857 | 0.0064719 | -0.023383 | 65.8401 | -56.575 | 3.0579 | -57.3349 | 65.744 | -57.2067 | -57.2708 | -56.6666 | 2.9343 | -57.3349 | 65.7257 | 65.625 | -57.2433 | -57.3257 | -0.041199 | -0.10529 | 0.045777 | 0.59051 | -0.16937 | -0.064087 | 0.14191 | -0.07782 | -0.16022 | 0.027466 | 0.49896 | -0.16937 | -0.009155 | -0.073242 | 122.9095 | 123.0057 | 60.2234 | -122.9691 | 122.8912 | 122.7905 | 60.0998 | -123.024
494.8438 | 123.2529 | -57.1335 | 65.7578 | -0.015478 | -0.026452 | 0.076696 | -0.0018642 | 0.058989 | -0.0084293 | -0.0092992 | -0.34991 | -0.01487 | 0.060909 | 0.047107 | -0.0063461 | -0.010566 | 65.8356 | -56.5704 | 3.1219 | -57.3166 | 65.7944 | -57.1976 | -57.2296 | -56.6162 | 2.9251 | -57.3074 | 65.7852 | 65.6616 | -57.2021 | -57.2662 | -0.064087 | -0.09613 | 0.036622 | 0.56305 | -0.1831 | -0.086975 | 0.07782 | -0.068664 | -0.13275 | 0.027466 | 0.51727 | -0.17395 | -0.041199 | -0.09613 | 122.9279 | 122.9691 | 60.2554 | -122.9874 | 122.9187 | 122.7951 | 60.0586 | -123.024
495.8438 | 123.2346 | -57.1014 | 65.7898 | 0.045557 | -0.0082939 | 0.066015 | 0.0077488 | 0.054717 | -0.0062933 | -0.01998 | -0.090514 | -0.007393 | 0.048092 | 0.053516 | -0.0010051 | -0.011634 | 65.8768 | -56.5155 | 3.1265 | -57.2754 | 65.8127 | -57.1381 | -57.2067 | -56.5613 | 2.9297 | -57.2754 | 65.8356 | 65.7166 | -57.1609 | -57.2617 | -0.036622 | -0.10529 | 0.022888 | 0.58594 | -0.17395 | -0.068665 | 0.086975 | -0.05951 | -0.16022 | 0.045776 | 0.54016 | -0.17395 | -0.013733 | -0.073242 | 122.9141 | 122.9782 | 60.228 | -122.9965 | 122.937 | 122.818 | 60.0311 | -123.0515
496.8438 | 123.2391 | -57.0557 | 65.8264 | 0.10659 | -0.018975 | 0.083105 | -0.0029322 | 0.051512 | -0.0073613 | -0.023184 | -0.01422 | -0.023415 | 0.07159 | 0.055652 | -0.0074141 | -0.016975 | 65.9088 | -56.4423 | 3.2593 | -57.2205 | 65.863 | -57.0877 | -57.1381 | -56.5155 | 2.916 | -57.2662 | 65.8676 | 65.7669 | -57.0969 | -57.2067 | -0.032044 | -0.082398 | 0.036621 | 0.6134 | -0.16479 | -0.082397 | 0.082397 | -0.041199 | -0.15106 | 0.041199 | 0.54016 | -0.21057 | -0.059509 | -0.059509 | 122.9187 | 122.9645 | 60.3149 | -122.9645 | 122.9233 | 122.8226 | 59.9716 | -123.0331
497.8438 | 123.1979 | -57.0145 | 65.8905 | 0.19814 | -0.017907 | 0.084173 | 0.0024088 | 0.051512 | -0.0062933 | -0.0092992 | 0.16888 | -0.015938 | 0.033138 | 0.050312 | 0.0011309 | -0.016975 | 65.95 | -56.4377 | 3.1174 | -57.2113 | 65.8859 | -57.0465 | -57.106 | -56.5018 | 2.8656 | -57.28 | 65.9225 | 65.7944 | -57.0602 | -57.1655 | -0.032044 | -0.091553 | -0.004578 | 0.57678 | -0.19684 | -0.10529 | 0.059509 | -0.045777 | -0.15106 | 0.032043 | 0.5127 | -0.2655 | -0.11444 | -0.09613 | 122.9004 | 122.9645 | 60.1318 | -122.9965 | 122.937 | 122.8088 | 59.8801 | -123.056
498.8438 | 123.2117 | -56.9504 | 65.918 | 0.24392 | -0.021111 | 0.07456 | 0.0066808 | 0.060057 | -0.00095325 | -0.0092992 | -0.2431 | -0.010597 | 0.044888 | 0.049243 | -0.0052781 | -0.016975 | 65.9775 | -56.218 | 3.3051 | -57.1655 | 65.9592 | -56.9962 | -57.0511 | -56.4331 | 2.8381 | -57.2205 | 65.9866 | 65.8676 | -57.019 | -57.1243 | -0.045777 | -0.10071 | 0.041198 | 0.73242 | -0.21515 | -0.11444 | 0.059509 | -0.068665 | -0.17395 | 0.068664 | 0.51727 | -0.27008 | -0.09613 | -0.050354 | 122.9095 | 122.9279 | 60.2554 | -122.9691 | 122.937 | 122.818 | 59.7885 | -123.0423
499.8438 | 123.2483 | -56.9 | 65.9958 | -0.076513 | -0.0061569 | 0.07456 | 0.017362 | 0.067534 | -0.0041573 | -0.018912 | -0.30414 | -0.01487 | 0.050228 | 0.055652 | -0.0042101 | -0.0084301 | 66.0828 | -56.1859 | 3.2455 | -57.0511 | 65.9958 | -56.9916 | -57.0145 | -56.2912 | 2.9343 | -57.0831 | 65.9958 | 65.9134 | -56.9595 | -57.0419 | -0.091553 | -0.11444 | 0 | 0.71411 | -0.15106 | -0.036621 | 0.086975 | -0.05951 | -0.14191 | 0 | 0.60883 | -0.18311 | -0.041199 | -0.082398 | 122.8958 | 122.9828 | 60.1456 | -123.0103 | 122.8958 | 122.8134 | 59.8343 | -123.0377
500.8438 | 123.2437 | -56.8726 | 66.0599 | 0.015039 | 0.0087961 | 0.072424 | 0.0045448 | 0.051512 | -0.0030893 | -0.022116 | -0.22784 | -0.013802 | 0.027798 | 0.047107 | 0.0021989 | -0.016975 | 66.1423 | -56.131 | 3.2913 | -57.0236 | 66.0324 | -56.9 | -56.9504 | -56.1951 | 2.9663 | -57.0328 | 66.069 | 65.9409 | -56.9046 | -57.019 | -0.027465 | -0.077819 | -0.027465 | 0.74158 | -0.15106 | -0.073243 | 0.082398 | -0.032043 | -0.14648 | 0.009156 | 0.67749 | -0.16022 | -0.013733 | -0.11902 | 122.905 | 123.0148 | 60.1639 | -123.0103 | 122.9416 | 122.8134 | 59.8389 | -123.0789
501.8438 | 123.2208 | -56.7947 | 66.0828 | 0.060816 | -0.01043 | 0.083105 | 0.0098848 | 0.053649 | -0.0073613 | -0.018912 | -0.01422 | -0.019142 | 0.041683 | 0.05672 | 0.0032669 | -0.012702 | 66.1514 | -56.0669 | 3.3829 | -56.9778 | 66.1102 | -56.8634 | -56.8771 | -56.1218 | 3.0029 | -56.9962 | 66.1102 | 65.9683 | -56.8817 | -56.9595 | -0.068664 | -0.082397 | 0.027465 | 0.72784 | -0.1831 | -0.10071 | 0.068664 | -0.086975 | -0.16479 | 0.027465 | 0.67291 | -0.20142 | -0.036621 | -0.11444 | 122.905 | 122.9462 | 60.1776 | -122.9599 | 122.905 | 122.7631 | 59.7977 | -123.0423
502.8438 | 123.2483 | -56.7078 | 66.1331 | 0.15237 | -0.011498 | 0.087377 | 0.0066808 | 0.051512 | -0.0084293 | -0.0071622 | -0.090514 | -0.02021 | 0.047024 | 0.046039 | -0.0052781 | -0.010566 | 66.2338 | -55.9799 | 3.4653 | -56.9183 | 66.1514 | -56.8085 | -56.8634 | -56.0394 | 2.9251 | -56.9366 | 66.1652 | 66.0461 | -56.8085 | -56.9138 | -0.10071 | -0.15564 | 0.01831 | 0.72784 | -0.21057 | -0.054932 | 0.10071 | -0.10071 | -0.20599 | 0.032043 | 0.66833 | -0.22888 | -0.022889 | -0.086975 | 122.8592 | 122.9416 | 60.173 | -122.9965 | 122.8729 | 122.7539 | 59.6329 | -123.0469
503.8438 | 123.262 | -56.694 | 66.188 | 0.076074 | -0.023247 | 0.084173 | 0.0098848 | 0.062194 | -0.0062933 | -0.0092992 | 0.062074 | -0.01487 | 0.033138 | 0.046039 | -0.0074141 | -0.015907 | 66.2567 | -55.9296 | 3.4103 | -56.9 | 66.1972 | -56.7581 | -56.7947 | -56.0028 | 2.9205 | -56.9229 | 66.1972 | 66.0782 | -56.7719 | -56.8771 | -0.064087 | -0.10071 | 0.009156 | 0.76447 | -0.20599 | -0.10529 | 0.068665 | -0.07782 | -0.1831 | 0.009156 | 0.69122 | -0.22888 | -0.045777 | -0.10986 | 122.8912 | 122.9507 | 60.1044 | -122.9828 | 122.8912 | 122.7722 | 59.6146 | -123.0652
504.8438 | 123.1659 | -56.6666 | 66.2247 | 0.33547 | -0.023247 | 0.077764 | 0.044065 | 0.056853 | 0.0011837 | -0.014639 | 0.062074 | -0.017006 | 0.03207 | 0.052448 | 0.0075399 | -0.01377 | 66.3254 | -55.9021 | 3.3737 | -56.8405 | 66.2521 | -56.7261 | -56.749 | -55.9433 | 2.8152 | -56.9 | 66.2659 | 66.1514 | -56.7123 | -56.8268 | -0.059509 | -0.082397 | 0.027466 | 0.76447 | -0.17395 | -0.091553 | 0.10071 | -0.045776 | -0.16022 | 0.041199 | 0.72327 | -0.23346 | -0.073242 | -0.073242 | 122.9187 | 122.9919 | 60.0403 | -122.9736 | 122.9324 | 122.818 | 59.4818 | -123.0515
505.8438 | 123.1705 | -56.6162 | 66.275 | 0.18289 | -0.0072259 | 0.084173 | 0.01843 | 0.068602 | -0.015906 | -0.014639 | 0.22992 | -0.012734 | 0.039547 | 0.05672 | -0.0020731 | -0.024451 | 66.4124 | -55.8105 | 3.4973 | -56.7993 | 66.3025 | -56.6528 | -56.6849 | -55.8975 | 2.7878 | -56.868 | 66.33 | 66.1835 | -56.6986 | -56.7673 | -0.036621 | -0.068664 | 0.027466 | 0.80566 | -0.1831 | -0.11444 | 0.13733 | -0.082397 | -0.15106 | 0.054932 | 0.71869 | -0.25177 | -0.10071 | -0.091552 | 122.9187 | 123.0286 | 60.1135 | -122.9599 | 122.9462 | 122.7997 | 59.404 | -123.0423
506.8438 | 123.2574 | -56.5201 | 66.362 | -0.00022031 | -0.0050889 | 0.087377 | 0.0045448 | 0.062194 | -0.016974 | -0.015707 | -0.13629 | -0.010597 | 0.041683 | 0.047107 | 0.0064719 | -0.01377 | 66.4993 | -55.5634 | 3.6621 | -56.6711 | 66.3757 | -56.5887 | -56.6071 | -55.6732 | 2.8519 | -56.7032 | 66.4078 | 66.2888 | -56.5704 | -56.6574 | -0.068664 | -0.086975 | 0.013732 | 0.95673 | -0.15106 | -0.064087 | 0.13733 | -0.050354 | -0.13733 | 0.045776 | 0.84686 | -0.18311 | -0.045776 | -0.073243 | 122.8958 | 123.0194 | 60.1822 | -122.9691 | 122.9279 | 122.8088 | 59.3719 | -123.0194
507.8438 | 123.2391 | -56.5247 | 66.362 | -0.076513 | -0.0061569 | 0.083105 | 0.0066808 | 0.055785 | 0.0033197 | -0.0050262 | -0.15155 | -0.011666 | 0.052364 | 0.050312 | 0.0054039 | -0.020179 | 66.4536 | -55.5588 | 3.5889 | -56.6711 | 66.3849 | -56.5704 | -56.5979 | -55.6412 | 2.829 | -56.694 | 66.394 | 66.2796 | -56.6025 | -56.6711 | -0.045777 | -0.073242 | 0.022888 | 0.96588 | -0.14648 | -0.073243 | 0.091552 | -0.07782 | -0.14648 | 0.032043 | 0.88348 | -0.16937 | -0.022888 | -0.082398 | 122.9095 | 122.9782 | 60.1135 | -122.9599 | 122.9187 | 122.8043 | 59.3536 | -123.0331
508.8438 | 123.2666 | -56.4468 | 66.4307 | 0.030298 | 0.0034561 | 0.072424 | 0.0045448 | 0.042967 | -0.014838 | -0.0050262 | -0.51776 | -0.021279 | 0.048092 | 0.05138 | 0.0043349 | -0.026588 | 66.5314 | -55.4535 | 3.566 | -56.6162 | 66.4444 | -56.5155 | -56.5475 | -55.5267 | 2.8885 | -56.6208 | 66.4581 | 66.3437 | -56.5155 | -56.6025 | -0.068665 | -0.10071 | 0.013733 | 0.99335 | -0.16937 | -0.068665 | 0.10071 | -0.068665 | -0.15564 | 0.027466 | 0.9201 | -0.17395 | -0.018311 | -0.086975 | 122.8912 | 122.9782 | 60.0128 | -122.9782 | 122.905 | 122.7905 | 59.3353 | -123.0331
509.8438 | 123.2346 | -56.4148 | 66.4536 | 0.10659 | -0.024315 | 0.076696 | -0.0018642 | 0.051512 | -0.0073613 | -0.010367 | -0.090514 | -0.011666 | 0.040615 | 0.03429 | 6.2882e-05 | -0.024451 | 66.5451 | -55.4031 | 3.5706 | -56.5796 | 66.4948 | -56.4606 | -56.5338 | -55.4535 | 2.8427 | -56.5933 | 66.4993 | 66.3666 | -56.4926 | -56.5567 | -0.045776 | -0.11902 | 0.041199 | 1.0117 | -0.1648 | -0.045777 | 0.091553 | -0.07782 | -0.14191 | 0.045777 | 0.9613 | -0.17853 | -0.036621 | -0.086975 | 122.9095 | 122.9599 | 59.9854 | -122.9874 | 122.9141 | 122.7814 | 59.2575 | -123.0103
510.8438 | 123.262 | -56.3599 | 66.5039 | -0.030737 | -0.017907 | 0.076696 | 0.0024088 | 0.054717 | -0.0052253 | -0.017844 | -0.090514 | -0.007393 | 0.04916 | 0.062061 | -0.0052781 | -0.012702 | 66.6046 | -55.3116 | 3.6255 | -56.5338 | 66.5314 | -56.4194 | -56.4377 | -55.4214 | 2.916 | -56.5475 | 66.5497 | 66.4169 | -56.4102 | -56.5201 | -0.05951 | -0.07782 | 0.027466 | 1.0483 | -0.17395 | -0.09613 | 0.10071 | -0.050354 | -0.16022 | 0.045777 | 0.93841 | -0.18768 | -0.027465 | -0.086975 | 122.8912 | 122.9645 | 59.9854 | -122.9416 | 122.9095 | 122.7768 | 59.2758 | -123.024
511.8438 | 123.2071 | -56.3644 | 66.5268 | -0.36643 | -0.0082939 | 0.093786 | 0.010954 | 0.054717 | -0.0041573 | -0.016776 | 0.031556 | -0.017006 | 0.037411 | 0.047107 | 0.0086079 | -0.016975 | 66.5588 | -55.3299 | 3.4882 | -56.5384 | 66.5588 | -56.4102 | -56.4743 | -55.3986 | 2.8564 | -56.5933 | 66.5955 | 66.4536 | -56.4331 | -56.5109 | -0.045776 | -0.10986 | 0.032044 | 1.0345 | -0.17395 | -0.064087 | 0.032044 | -0.068664 | -0.14648 | 0.068665 | 0.96588 | -0.22888 | -0.082398 | -0.073242 | 122.9233 | 122.9233 | 59.8526 | -123.0011 | 122.9599 | 122.818 | 59.2209 | -123.0377
512.8438 | 123.2025 | -56.3095 | 66.5817 | 0.15237 | -0.023247 | 0.080969 | 0.01309 | 0.045104 | -0.0020213 | -0.017844 | -0.01422 | -0.021279 | 0.055569 | 0.062061 | 0.0064719 | -0.012702 | 66.6733 | -55.188 | 3.6438 | -56.456 | 66.5909 | -56.3461 | -56.4056 | -55.2521 | 2.9617 | -56.5155 | 66.6138 | 66.4902 | -56.369 | -56.4651 | -0.036621 | -0.096131 | 0.009155 | 1.1215 | -0.14648 | -0.050354 | 0.091553 | -0.05951 | -0.15564 | 0.032044 | 1.0574 | -0.20599 | -0.050354 | -0.091553 | 122.9004 | 122.9828 | 59.9533 | -122.9874 | 122.9233 | 122.7997 | 59.2712 | -123.0469
513.8438 | 123.2208 | -56.2775 | 66.6229 | -0.045996 | -0.018975 | 0.0799 | 0.012022 | 0.055785 | -0.0073613 | -0.012503 | -0.30414 | -0.021279 | 0.038479 | 0.05138 | -0.0031411 | -0.015907 | 66.7603 | -55.0186 | 3.717 | -56.3965 | 66.6275 | -56.3141 | -56.3461 | -55.1926 | 2.98 | -56.4423 | 66.6458 | 66.5451 | -56.3416 | -56.4331 | -0.036621 | -0.068664 | 0.004577 | 1.2588 | -0.11902 | -0.050354 | 0.13733 | -0.064087 | -0.15564 | 0.022888 | 1.0849 | -0.1648 | -0.009156 | -0.07782 | 122.905 | 123.0377 | 59.9945 | -122.9691 | 122.9233 | 122.8226 | 59.2575 | -123.056
514.8438 | 123.2483 | -56.2134 | 66.6504 | 0.060816 | -0.011498 | 0.086309 | 0.015226 | 0.04724 | -0.0084293 | -0.018912 | -0.15155 | -0.018074 | 0.040615 | 0.059925 | 0.0075399 | -0.019111 | 66.806 | -54.9042 | 3.772 | -56.3461 | 66.6824 | -56.25 | -56.3004 | -55.0919 | 3.0808 | -56.3919 | 66.687 | 66.5634 | -56.2683 | -56.3736 | -0.036621 | -0.086975 | 0.032043 | 1.3092 | -0.13275 | -0.045776 | 0.15564 | -0.054932 | -0.16022 | 0.036621 | 1.1215 | -0.17853 | -0.018311 | -0.086975 | 122.8958 | 123.0194 | 59.9854 | -122.9507 | 122.9004 | 122.7768 | 59.2941 | -123.024
515.8438 | 123.2254 | -56.1127 | 66.7511 | -0.015478 | -0.013634 | 0.070287 | 0.0088168 | 0.044036 | -0.0084293 | -0.011435 | -0.13629 | -0.010597 | 0.039547 | 0.040699 | 0.0064719 | -0.018043 | 66.8564 | -54.808 | 3.8406 | -56.2683 | 66.7648 | -56.1813 | -56.2271 | -54.9454 | 3.2318 | -56.3004 | 66.7831 | 66.6275 | -56.2134 | -56.2958 | -0.068664 | -0.11444 | 0.013733 | 1.3046 | -0.15564 | -0.041199 | 0.10529 | -0.10071 | -0.1831 | 0.032043 | 1.1673 | -0.18768 | -0.004578 | -0.1236 | 122.8775 | 122.9691 | 59.9533 | -122.9782 | 122.8958 | 122.7402 | 59.3445 | -123.0469
516.8438 | 123.2529 | -56.0669 | 66.8152 | -0.045996 | -0.025384 | 0.087377 | 0.0024088 | 0.062194 | -0.0073613 | -0.016776 | -0.16681 | -0.02021 | 0.048092 | 0.054584 | 6.2882e-05 | -0.015907 | 66.9113 | -54.7165 | 3.8223 | -56.2271 | 66.8198 | -56.131 | -56.1493 | -54.8126 | 3.2501 | -56.2408 | 66.861 | 66.7328 | -56.1447 | -56.2454 | -0.064086 | -0.082397 | 0.004577 | 1.3504 | -0.16022 | -0.07782 | 0.09613 | -0.077819 | -0.17853 | 0.045776 | 1.2543 | -0.17395 | 0.004577 | -0.082398 | 122.8867 | 122.9782 | 59.8892 | -122.9645 | 122.9279 | 122.7997 | 59.317 | -123.0606
517.8438 | 123.2208 | -56.0211 | 66.8335 | 0.045557 | -0.023247 | 0.076696 | 0.014158 | 0.063262 | -0.012702 | -0.012503 | 0.092591 | -0.022347 | 0.041683 | 0.03429 | 0.0011309 | -0.0094981 | 66.9342 | -54.6707 | 3.8727 | -56.1905 | 66.8518 | -56.0898 | -56.1401 | -54.7531 | 3.2364 | -56.2088 | 66.8747 | 66.7511 | -56.0944 | -56.1951 | -0.068665 | -0.11902 | 0.018311 | 1.3504 | -0.16937 | -0.050354 | 0.10071 | -0.073242 | -0.17395 | 0.041199 | 1.268 | -0.18768 | -0.013733 | -0.082397 | 122.8729 | 122.9553 | 59.8938 | -122.9736 | 122.8958 | 122.7722 | 59.2575 | -123.0286
518.8438 | 123.1979 | -55.9753 | 66.9159 | 0.076074 | -0.012566 | 0.080969 | 0.0034768 | 0.051512 | -0.015906 | -0.0050262 | 0.12311 | -0.004189 | 0.031002 | 0.067401 | 0.0043349 | -0.011634 | 66.9617 | -54.5517 | 3.8589 | -56.1081 | 66.9571 | -56.0257 | -56.0806 | -54.689 | 3.2455 | -56.1951 | 66.98 | 66.8289 | -56.044 | -56.1127 | -0.050354 | -0.10529 | 0.041198 | 1.4236 | -0.13275 | -0.027466 | 0.045776 | -0.068664 | -0.13733 | 0.064086 | 1.2863 | -0.21973 | -0.082397 | -0.086976 | 122.9324 | 122.937 | 59.8343 | -122.9965 | 122.9553 | 122.8043 | 59.2209 | -123.0286
519.8438 | 123.2483 | -55.8746 | 66.9983 | 0.060816 | -0.025384 | 0.083105 | 0.014158 | 0.045104 | -0.0094983 | -0.011435 | -0.090514 | -0.017006 | 0.036343 | 0.052448 | -0.0010051 | -0.018043 | 67.067 | -54.3686 | 4.0558 | -56.0074 | 67.0166 | -55.9433 | -55.9937 | -54.5059 | 3.4149 | -56.0715 | 67.0395 | 66.8884 | -55.9662 | -56.0623 | -0.068664 | -0.11902 | 0.018311 | 1.506 | -0.13275 | -0.013733 | 0.068665 | -0.091553 | -0.18768 | 0.041199 | 1.3687 | -0.19684 | -0.009155 | -0.10986 | 122.8912 | 122.9416 | 59.9304 | -122.9919 | 122.9141 | 122.7631 | 59.2896 | -123.0606
520.8438 | 123.1613 | -55.838 | 67.0898 | -0.076513 | -0.016839 | 0.078832 | 0.0066808 | 0.055785 | -0.00095325 | -0.012503 | -0.2431 | -0.006325 | 0.028866 | 0.066333 | 0.0096759 | -0.027656 | 67.1768 | -54.213 | 4.0741 | -55.957 | 67.0532 | -55.8838 | -55.9204 | -54.4098 | 3.4698 | -56.0394 | 67.0944 | 66.9525 | -55.9021 | -56.0211 | -0.045776 | -0.082397 | -0.036621 | 1.6251 | -0.11902 | -0.036621 | 0.086975 | -0.064087 | -0.18311 | 0.004577 | 1.4282 | -0.20142 | -0.018311 | -0.13733 | 122.8912 | 123.0148 | 59.9121 | -123.0103 | 122.9324 | 122.7905 | 59.3079 | -123.111
521.8438 | 123.2574 | -55.751 | 67.1127 | 0.030298 | -0.015771 | 0.082037 | 0.0098848 | 0.057921 | -0.010566 | -0.015707 | -0.15155 | -0.017006 | 0.047024 | 0.058857 | -0.0031411 | -0.018043 | 67.2455 | -54.0573 | 4.1382 | -55.8746 | 67.1219 | -55.8151 | -55.8426 | -54.2542 | 3.6209 | -55.9204 | 67.1997 | 67.0166 | -55.8289 | -55.925 | -0.064087 | -0.091552 | 0.009155 | 1.6937 | -0.1236 | -0.032044 | 0.13275 | -0.077819 | -0.17395 | 0.086975 | 1.4969 | -0.16937 | 0.004578 | -0.09613 | 122.8729 | 122.9965 | 59.8892 | -122.9553 | 122.9507 | 122.7676 | 59.3719 | -123.0377
522.8438 | 123.2712 | -55.6412 | 67.2318 | -0.15281 | -0.0050889 | 0.087377 | 0.017362 | 0.05258 | -0.0020213 | -0.0092992 | -0.33466 | -0.019142 | 0.039547 | 0.05672 | 0.0096759 | -0.016975 | 67.3279 | -53.9383 | 4.2435 | -55.7739 | 67.2592 | -55.7281 | -55.7602 | -54.0619 | 3.6804 | -55.806 | 67.2592 | 67.1539 | -55.719 | -55.8197 | -0.086975 | -0.11902 | 0.027466 | 1.7029 | -0.13275 | -0.013733 | 0.096131 | -0.07782 | -0.17853 | 0.027466 | 1.5793 | -0.16479 | 0.013733 | -0.077819 | 122.9004 | 122.9691 | 59.8846 | -122.9919 | 122.9004 | 122.7951 | 59.3216 | -123.0515
523.8438 | 123.2483 | -55.5771 | 67.2638 | 0.12185 | -0.012566 | 0.085241 | 0.016294 | 0.05258 | -0.0041573 | -0.0050262 | 0.062074 | -0.019142 | 0.050228 | 0.042835 | 0.0043349 | -0.020179 | 67.3462 | -53.8101 | 4.3213 | -55.7465 | 67.305 | -55.687 | -55.7281 | -53.9658 | 3.7765 | -55.7831 | 67.3141 | 67.1677 | -55.6732 | -55.7602 | -0.10986 | -0.15106 | 0.041199 | 1.767 | -0.16937 | -0.018311 | 0.082397 | -0.096131 | -0.18311 | 0.050354 | 1.6113 | -0.20599 | -0.022888 | -0.09613 | 122.8821 | 122.9233 | 59.8984 | -122.9919 | 122.8912 | 122.7448 | 59.3536 | -123.024
524.8438 | 123.262 | -55.5084 | 67.3782 | 0.015039 | -0.020043 | 0.076696 | 0.012022 | 0.058989 | -0.0020213 | -0.013571 | -0.029479 | -0.013802 | 0.045956 | 0.053516 | 0.011812 | -0.012702 | 67.4606 | -53.627 | 4.3396 | -55.6458 | 67.3874 | -55.5771 | -55.6046 | -53.8055 | 3.8635 | -55.6915 | 67.4103 | 67.2958 | -55.5634 | -55.6458 | -0.068664 | -0.09613 | 0.009155 | 1.8814 | -0.13733 | -0.041199 | 0.082397 | -0.054931 | -0.13733 | 0.032043 | 1.7029 | -0.1831 | -0.045776 | -0.082398 | 122.8958 | 122.9691 | 59.848 | -122.9828 | 122.9187 | 122.8043 | 59.3719 | -123.024
525.8438 | 123.1567 | -55.3848 | 67.4606 | 0.15237 | -0.011498 | 0.099126 | 0.0034768 | 0.063262 | -0.012702 | -0.0092992 | 0.13837 | -0.019142 | 0.057705 | 0.053516 | 0.0064719 | -0.016975 | 67.5064 | -53.5217 | 4.4815 | -55.545 | 67.5018 | -55.4581 | -55.4993 | -53.6865 | 3.923 | -55.6366 | 67.5156 | 67.4011 | -55.4764 | -55.5817 | -0.073242 | -0.11444 | 0.041199 | 1.8631 | -0.16022 | -0.045776 | 0.045777 | -0.091552 | -0.19684 | 0.054932 | 1.6983 | -0.25177 | -0.054932 | -0.059509 | 122.8867 | 122.8912 | 59.8663 | -122.9599 | 122.9004 | 122.7859 | 59.3079 | -123.0423
526.8438 | 123.2254 | -55.3299 | 67.5568 | 0.10659 | -0.0040209 | 0.085241 | 0.017362 | 0.049376 | -0.015906 | -0.0092992 | -0.044738 | -0.012734 | 0.045956 | 0.043903 | 6.2882e-05 | -0.024451 | 67.6209 | -53.3112 | 4.5685 | -55.4672 | 67.5934 | -55.3574 | -55.4398 | -53.5217 | 4.1977 | -55.5313 | 67.5842 | 67.4606 | -55.394 | -55.4718 | -0.027466 | -0.10986 | 0.036621 | 2.0187 | -0.13733 | -0.027466 | 0.064087 | -0.064087 | -0.14191 | 0.027466 | 1.8082 | -0.20142 | -0.059509 | -0.096131 | 122.9233 | 122.9507 | 59.8984 | -122.9965 | 122.9141 | 122.7905 | 59.5276 | -123.0286
527.8438 | 123.2346 | -55.2338 | 67.6392 | 0.030298 | -0.020043 | 0.07456 | 0.016294 | 0.056853 | -0.0052253 | -0.011435 | -0.22784 | -0.02021 | 0.043819 | 0.067401 | -0.0052781 | -0.016975 | 67.7628 | -53.0777 | 4.7012 | -55.3665 | 67.6666 | -55.2841 | -55.3482 | -53.302 | 4.422 | -55.3848 | 67.6849 | 67.5705 | -55.2841 | -55.3894 | -0.050354 | -0.11444 | 0.027466 | 2.1561 | -0.13275 | -0.01831 | 0.1236 | -0.050354 | -0.15564 | 0.045777 | 1.9318 | -0.15106 | 0.004577 | -0.068664 | 122.9004 | 122.9965 | 59.935 | -122.9874 | 122.9187 | 122.8043 | 59.6558 | -123.0286
528.8438 | 123.2071 | -55.1102 | 67.7399 | 0.10659 | -0.013634 | 0.083105 | 0.0098848 | 0.060057 | -0.010566 | -0.0060942 | 0.0010378 | -0.02021 | 0.04916 | 0.06847 | -0.0031411 | -0.010566 | 67.8406 | -52.9175 | 4.8431 | -55.2521 | 67.7856 | -55.1834 | -55.2109 | -53.1418 | 4.6188 | -55.2841 | 67.8085 | 67.6575 | -55.2246 | -55.307 | -0.073243 | -0.10071 | 0.045777 | 2.1927 | -0.14191 | -0.041199 | 0.10071 | -0.11444 | -0.19684 | 0.068665 | 1.9684 | -0.17395 | 0.022888 | -0.082397 | 122.8958 | 122.9507 | 59.9533 | -122.9507 | 122.9187 | 122.7676 | 59.729 | -123.0469
529.8438 | 123.2437 | -55.0507 | 67.8452 | -0.015478 | -0.013634 | 0.07456 | 0.010954 | 0.056853 | -0.0073613 | -0.011435 | -0.13629 | -0.010597 | 0.045956 | 0.055652 | -0.0052781 | -0.018043 | 67.9047 | -52.7664 | 4.9942 | -55.1697 | 67.8497 | -55.0964 | -55.1559 | -52.9999 | 4.9026 | -55.2612 | 67.8635 | 67.7444 | -55.1193 | -55.2246 | -0.045777 | -0.10529 | 0.004577 | 2.2842 | -0.11902 | -0.013733 | 0.059509 | -0.068665 | -0.17395 | 0.01831 | 2.0508 | -0.21057 | -0.036621 | -0.10071 | 122.9004 | 122.9553 | 60.0449 | -123.0011 | 122.9141 | 122.7951 | 59.9533 | -123.0698
530.8438 | 123.2071 | -54.9408 | 67.9459 | 0.12185 | -0.022179 | 0.073492 | 0.0088168 | 0.063262 | 0.00011475 | -0.016776 | 0.0010378 | -0.013802 | 0.036343 | 0.053516 | 0.0096759 | -0.021247 | 68.0008 | -52.5604 | 5.1453 | -55.0644 | 67.9916 | -54.9774 | -55.0369 | -52.7985 | 5.1041 | -55.1559 | 67.9962 | 67.8726 | -54.9957 | -55.1193 | -0.036621 | -0.09613 | 0.045776 | 2.3804 | -0.1236 | -0.027466 | 0.054931 | -0.054932 | -0.17853 | 0.050354 | 2.1423 | -0.21515 | -0.036621 | -0.073242 | 122.9324 | 122.9416 | 60.0861 | -122.9828 | 122.937 | 122.8134 | 60.0449 | -123.0652
531.8438 | 123.2254 | -54.8218 | 68.0649 | 0.10659 | -0.0050889 | 0.07456 | 0.016294 | 0.04724 | 0.0011837 | -0.017844 | -0.01422 | -0.017006 | 0.056637 | 0.046039 | 0.010744 | -0.024451 | 68.1335 | -52.3499 | 5.3009 | -54.95 | 68.1015 | -54.8767 | -54.9362 | -52.6337 | 5.246 | -55.0415 | 68.0923 | 67.9779 | -54.9133 | -54.982 | -0.054932 | -0.11444 | 0.036621 | 2.4719 | -0.12817 | -0.013733 | 0.068665 | -0.091553 | -0.16022 | 0.027466 | 2.1881 | -0.21973 | -0.059509 | -0.086975 | 122.9233 | 122.9553 | 60.1227 | -123.0011 | 122.9141 | 122.7997 | 60.0677 | -123.0469
532.8438 | 123.1705 | -54.7806 | 68.1564 | 0.36599 | -0.024315 | 0.077764 | 0.0098848 | 0.049376 | 0.0054557 | -0.0039582 | 0.21466 | -0.009529 | 0.03207 | 0.059925 | -0.0020731 | -0.0084301 | 68.1931 | -52.2308 | 5.4428 | -54.8859 | 68.1702 | -54.776 | -54.8447 | -52.4597 | 5.3604 | -55.0003 | 68.1839 | 68.0649 | -54.8218 | -54.9133 | 0.004578 | -0.064087 | 0.013733 | 2.5497 | -0.10528 | -0.041198 | 0.036621 | -0.041198 | -0.13275 | 0.027466 | 2.3209 | -0.21973 | -0.086975 | -0.091553 | 122.9507 | 122.9736 | 60.2234 | -123.0011 | 122.9645 | 122.8455 | 60.141 | -123.0698
533.8438 | 123.1659 | -54.7119 | 68.2022 | 0.2134 | -0.013634 | 0.085241 | 0.0056128 | 0.058989 | -0.0020213 | -0.018912 | -1.7079 | -0.015938 | 0.050228 | 0.065265 | 0.0054039 | -0.01377 | 68.2205 | -52.0615 | 5.5389 | -54.8264 | 68.2068 | -54.7668 | -54.7943 | -52.4048 | 5.4428 | -54.9408 | 68.2343 | 68.1107 | -54.7897 | -54.8859 | -0.054932 | -0.082398 | 0.004578 | 2.6505 | -0.11444 | -0.032043 | 0.018311 | -0.07782 | -0.17395 | 0.032044 | 2.3071 | -0.22888 | -0.054932 | -0.091552 | 122.9187 | 122.9324 | 60.2509 | -122.9965 | 122.9462 | 122.8226 | 60.1547 | -123.0881
534.8438 | 123.1979 | -54.689 | 68.1976 | 0.82375 | -0.022179 | 0.090582 | 0.01843 | 0.055785 | 0.0022517 | -0.0050262 | 0.12311 | -0.013802 | 0.035275 | 0.048175 | -0.0052781 | -0.012702 | 68.2114 | -51.9653 | 5.658 | -54.8309 | 68.1976 | -54.7348 | -54.808 | -52.24 | 5.5756 | -54.9271 | 68.2663 | 68.0923 | -54.776 | -54.863 | -0.045776 | -0.11902 | 0 | 2.7237 | -0.14191 | -0.022889 | 0.013733 | -0.086975 | -0.17395 | 0.068664 | 2.449 | -0.23804 | -0.064087 | -0.10529 | 122.8867 | 122.9004 | 60.347 | -123.0057 | 122.9553 | 122.7814 | 60.2646 | -123.0606
535.8438 | 123.2025 | -54.8492 | 68.0695 | 0.24392 | -0.01043 | 0.07456 | 0.016294 | 0.062194 | -0.00095325 | -0.0092992 | -0.25836 | -0.008461 | 0.039547 | 0.054584 | 0.0075399 | -0.015907 | 68.1198 | -51.9608 | 5.4565 | -54.9042 | 68.1198 | -54.8538 | -54.9225 | -52.3132 | 5.0629 | -55.0827 | 68.0969 | 67.9779 | -54.9179 | -55.0049 | -0.004578 | -0.073242 | 0.050354 | 2.8885 | -0.054932 | 0.01831 | 0.050354 | -0.068665 | -0.15564 | 0.027466 | 2.536 | -0.23346 | -0.07782 | -0.091553 | 122.9691 | 122.9691 | 60.3058 | -122.9919 | 122.9462 | 122.8271 | 59.9121 | -123.0743
536.8438 | 123.1476 | -54.6021 | 68.2892 | 0.70168 | -0.0040209 | 0.068151 | 0.012022 | 0.05258 | 0.0011837 | -0.013571 | 0.15363 | -0.019142 | 0.043819 | 0.053516 | 0.0096759 | -0.0094981 | 68.3441 | -51.6403 | 5.6305 | -54.7028 | 68.3258 | -54.6341 | -54.6753 | -51.9882 | 5.397 | -54.8355 | 68.3304 | 68.2114 | -54.6661 | -54.7531 | -0.032043 | -0.073242 | 0.036621 | 2.9617 | -0.10071 | -0.027466 | 0.054931 | -0.064087 | -0.15106 | 0.041198 | 2.6138 | -0.23346 | -0.082397 | -0.07782 | 122.9279 | 122.9462 | 60.2325 | -122.9645 | 122.9324 | 122.8134 | 59.9991 | -123.0423
537.8438 | 123.0881 | -54.4739 | 68.4998 | -0.47324 | 0.021614 | 0.082037 | 0.029112 | 0.053649 | 0.015069 | -0.0060942 | -0.41095 | -0.00098395 | 0.054501 | 0.066333 | 0.0075399 | -0.021247 | 68.486 | -51.4526 | 5.5389 | -54.57 | 68.4906 | -54.538 | -54.57 | -51.7868 | 5.4108 | -54.7577 | 68.541 | 68.3899 | -54.5609 | -54.6341 | -0.064087 | -0.09613 | -0.009155 | 3.0212 | -0.09613 | 0 | -0.013733 | -0.086975 | -0.16022 | 0.041199 | 2.6871 | -0.28381 | -0.1236 | -0.10986 | 122.9645 | 122.9599 | 60.0128 | -123.0698 | 123.0148 | 122.8638 | 59.8846 | -123.1338
538.8438 | 123.2025 | -54.3732 | 68.4998 | 0.53384 | 0.010932 | 0.084173 | 0.015226 | 0.066466 | 0.0043877 | -0.0018222 | 0.29095 | -0.008461 | 0.044888 | 0.055652 | 0.013948 | -0.0094981 | 68.3762 | -51.0406 | 5.6946 | -54.3961 | 68.4952 | -54.4189 | -54.451 | -51.5259 | 5.0949 | -54.5792 | 68.5089 | 68.3807 | -54.451 | -54.5425 | -0.045776 | -0.07782 | -0.004578 | 3.3325 | -0.022888 | 0.054932 | -0.1236 | -0.07782 | -0.16937 | 0.009155 | 2.8473 | -0.20599 | -0.036621 | -0.11902 | 122.8683 | 122.7493 | 60.0677 | -122.9507 | 122.8821 | 122.7539 | 59.4681 | -123.0423
539.8438 | 123.1613 | -54.332 | 68.5501 | 0.2134 | 0.0034561 | 0.060674 | 0.012022 | 0.045104 | 0.010797 | 0.0035188 | 0.36725 | -0.005257 | 0.051296 | 0.057788 | 0.0043349 | -0.010566 | 68.6966 | -50.9399 | 5.6259 | -54.332 | 68.5867 | -54.3594 | -54.4052 | -51.3336 | 5.0903 | -54.5151 | 68.6096 | 68.486 | -54.3594 | -54.4464 | -0.027466 | -0.073242 | 0.036621 | 3.392 | 0 | 0.073242 | 0.14648 | -0.027466 | -0.11444 | 0.059509 | 2.9984 | -0.18311 | -0.068665 | -0.064087 | 122.9187 | 123.0286 | 59.9579 | -122.9553 | 122.9416 | 122.818 | 59.4223 | -122.9965
540.8438 | 123.2025 | -54.1992 | 68.6829 | 0.59487 | 0.026954 | 0.070287 | 0.01843 | 0.070738 | 0.012933 | -0.0060942 | -0.44147 | -0.007393 | 0.041683 | 0.072742 | 6.2882e-05 | -0.029792 | 68.7836 | -50.7294 | 5.6213 | -54.2542 | 68.6874 | -54.2679 | -54.3091 | -51.1414 | 4.9988 | -54.3869 | 68.7149 | 68.6096 | -54.2725 | -54.364 | -0.068664 | -0.10986 | 0.004578 | 3.4698 | -0.054931 | 0.054932 | 0.10071 | -0.073242 | -0.16479 | 0.032044 | 3.0579 | -0.18768 | -0.022888 | -0.073242 | 122.8867 | 122.9828 | 59.8206 | -122.9919 | 122.9141 | 122.8088 | 59.198 | -123.0469
541.8438 | 123.2025 | -54.0527 | 68.8248 | 0.76272 | -0.00081686 | 0.090582 | 0.015226 | 0.057921 | -0.0041573 | -0.0082312 | 0.36725 | -0.009529 | 0.055569 | 0.057788 | 0.0096759 | -0.018043 | 68.9255 | -50.4456 | 5.8685 | -54.0802 | 68.8385 | -54.0756 | -54.1351 | -50.8621 | 5.2872 | -54.2404 | 68.8431 | 68.7881 | -54.1168 | -54.1901 | -0.022889 | -0.082398 | 0.013733 | 3.6072 | -0.027466 | 0.054932 | 0.10071 | -0.064087 | -0.13733 | 0.018311 | 3.1906 | -0.18768 | -0.050354 | -0.036621 | 122.8912 | 122.9782 | 59.9213 | -122.9599 | 122.8958 | 122.8409 | 59.3399 | -123.0148
542.8438 | 123.1567 | -53.9246 | 68.9896 | -0.24436 | 0.0055921 | 0.090582 | 0.00027184 | 0.046172 | -0.011634 | -0.012503 | -0.33466 | -0.010597 | 0.057705 | 0.050312 | 0.01288 | -0.02552 | 69.0491 | -50.1938 | 5.9235 | -53.9429 | 68.9941 | -53.952 | -54.007 | -50.6516 | 5.452 | -54.1397 | 69.0399 | 68.9392 | -54.0115 | -54.0894 | -0.027465 | -0.082397 | 0.004578 | 3.7308 | -0.01831 | 0.064087 | 0.059509 | -0.086975 | -0.16479 | 0.050354 | 3.273 | -0.21515 | -0.050354 | -0.050354 | 122.9187 | 122.9736 | 59.848 | -122.9965 | 122.9645 | 122.8638 | 59.3765 | -123.0789
543.8438 | 123.2162 | -53.801 | 69.0765 | 0.53384 | 0.037635 | 0.080969 | 0.016294 | 0.054717 | 0.015069 | -0.0060942 | -0.059997 | -0.009529 | 0.038479 | 0.058857 | 0.022493 | -0.01377 | 69.191 | -49.942 | 5.9967 | -53.8055 | 69.1315 | -53.8376 | -53.8696 | -50.3265 | 5.397 | -53.9886 | 69.1406 | 68.9987 | -53.8696 | -53.9703 | -0.036621 | -0.068665 | 0.054932 | 3.8589 | -0.004578 | 0.064087 | 0.11444 | -0.068665 | -0.16937 | 0.064087 | 3.4744 | -0.18768 | -0.01831 | -0.07782 | 122.9324 | 122.9919 | 59.7977 | -122.9462 | 122.9416 | 122.7997 | 59.198 | -123.0469
544.8438 | 123.175 | -53.746 | 69.136 | 0.56436 | 0.030158 | 0.077764 | 0.010954 | 0.053649 | -0.0020213 | -0.014639 | 0.30621 | -0.002053 | 0.060909 | 0.052448 | 0.0075399 | -0.014838 | 69.1452 | -49.8505 | 5.9784 | -53.8239 | 69.2001 | -53.8055 | -53.8696 | -50.148 | 5.5756 | -53.9978 | 69.1864 | 69.0628 | -53.8193 | -53.9291 | -0.059509 | -0.1236 | 0.064087 | 3.8956 | -0.07782 | 0.045776 | 0.009156 | -0.073242 | -0.18311 | 0.050354 | 3.598 | -0.25177 | -0.068665 | -0.073242 | 122.9462 | 122.8912 | 59.7244 | -123.0057 | 122.9324 | 122.8088 | 59.3216 | -123.0652
545.8438 | 123.0835 | -53.7964 | 69.1727 | 0.39651 | 0.036567 | 0.084173 | 0.031248 | 0.051512 | 0.02041 | -0.0028902 | 0.1994 | 0.011833 | 0.051296 | 0.066333 | 0.022493 | -0.0062931 | 69.136 | -49.6262 | 6.3126 | -53.8284 | 69.2001 | -53.801 | -53.8605 | -50.0381 | 5.722 | -54.071 | 69.223 | 69.1269 | -53.8376 | -53.9474 | -0.004577 | -0.064087 | 0.027466 | 4.1702 | -0.032043 | 0.032044 | -0.036621 | -0.041198 | -0.15106 | 0.050354 | 3.7582 | -0.27466 | -0.1236 | -0.045776 | 122.9965 | 122.9324 | 60.1089 | -123.0331 | 123.0194 | 122.9233 | 59.5184 | -123.1201
546.8438 | 123.0652 | -53.7735 | 69.1956 | 0.18289 | 0.036567 | 0.075628 | 0.014158 | 0.054717 | 0.016137 | -0.012503 | -0.13629 | 0.003288 | 0.065182 | 0.059925 | 0.011812 | -0.012702 | 69.1772 | -49.4202 | 6.2714 | -53.7735 | 69.2184 | -53.801 | -53.8559 | -49.8871 | 5.9509 | -54.0665 | 69.2505 | 69.1406 | -53.8147 | -53.9337 | -0.027465 | -0.082397 | 0.022888 | 4.3533 | 0 | 0.082397 | -0.018311 | -0.041198 | -0.16022 | 0.054931 | 3.8864 | -0.29297 | -0.13275 | -0.054932 | 122.9919 | 122.9507 | 60.0449 | -123.0515 | 123.024 | 122.9141 | 59.7244 | -123.1293
547.8438 | 123.1613 | -53.7735 | 69.1177 | 0.48806 | -0.014702 | 0.09699 | 0.0034768 | 0.049376 | -0.027656 | -0.013571 | 0.4588 | -0.012734 | 0.042751 | 0.058857 | 0.0064719 | -0.0052251 | 69.1406 | -49.0311 | 6.7612 | -53.7781 | 69.1086 | -53.8193 | -53.8696 | -49.6765 | 5.9189 | -54.0115 | 69.1589 | 69.0537 | -53.8422 | -53.9612 | -0.045776 | -0.09613 | -0.009155 | 4.7424 | -0.004577 | 0.091553 | 0.022888 | -0.068664 | -0.18768 | 0.041199 | 4.097 | -0.23804 | -0.050354 | -0.064087 | 122.8821 | 122.9141 | 60.5347 | -122.9874 | 122.9324 | 122.8271 | 59.6924 | -123.0789
548.8438 | 123.2025 | -53.5904 | 69.2871 | 0.27444 | -0.020043 | 0.092718 | 0.01309 | 0.050444 | -0.031928 | -0.0092992 | -0.15155 | -0.018074 | 0.040615 | 0.049243 | 0.0011309 | -0.0073621 | 69.3008 | -48.5184 | 7.0862 | -53.6911 | 69.2963 | -53.6636 | -53.7186 | -49.3652 | 5.9921 | -53.8055 | 69.3192 | 69.2139 | -53.6957 | -53.7872 | -0.073242 | -0.12817 | 0.009156 | 5.072 | -0.10071 | 0.027466 | 0.013733 | -0.10529 | -0.19684 | 0.032044 | 4.2252 | -0.21515 | -0.018311 | -0.073242 | 122.8867 | 122.8912 | 60.6766 | -123.0057 | 122.9095 | 122.8043 | 59.5825 | -123.0743
549.8438 | 123.0469 | -53.4485 | 69.4977 | 0.16763 | 0.037635 | 0.086309 | 0.024839 | 0.061125 | 0.016137 | -0.0018222 | 0.16888 | -0.002053 | 0.053432 | 0.057788 | 0.021425 | -0.023383 | 69.516 | -48.6374 | 6.958 | -53.4256 | 69.5572 | -53.4805 | -53.5263 | -49.0768 | 5.809 | -53.7369 | 69.5709 | 69.4565 | -53.4988 | -53.6316 | -0.032044 | -0.07782 | 0.059509 | 4.8111 | 0.022888 | 0.10071 | 0.01831 | -0.050354 | -0.18311 | 0.073242 | 4.3716 | -0.28839 | -0.10529 | -0.041199 | 123.0057 | 122.9645 | 60.4065 | -123.024 | 123.0194 | 122.905 | 59.2575 | -123.1293
550.8438 | 123.0835 | -53.3386 | 69.6167 | 0.15237 | 0.044044 | 0.075628 | 0.029112 | 0.067534 | 0.0086597 | -0.0050262 | 0.0010378 | -0.004189 | 0.054501 | 0.066333 | 0.0011309 | -0.0030891 | 69.635 | -48.3536 | 7.1091 | -53.3066 | 69.635 | -53.3936 | -53.4073 | -48.761 | 6.015 | -53.5858 | 69.6854 | 69.5755 | -53.389 | -53.476 | -0.054932 | -0.068665 | 0.018311 | 4.985 | 0.032043 | 0.10071 | 0.018311 | -0.050354 | -0.13733 | 0.068665 | 4.5776 | -0.24719 | -0.10986 | -0.041199 | 122.9736 | 122.9736 | 60.4477 | -123.024 | 123.024 | 122.9141 | 59.3536 | -123.0927
551.8438 | 123.111 | -52.8763 | 70.0745 | -0.24436 | 0.02909 | 0.060674 | 0.021635 | 0.053649 | 0.015069 | -0.0060942 | -0.075256 | -0.013802 | 0.07159 | 0.059925 | 0.017153 | -0.0073621 | 70.1202 | -47.8729 | 7.5943 | -52.7252 | 70.1111 | -52.8809 | -52.9633 | -48.262 | 5.896 | -53.096 | 70.1248 | 70.0516 | -52.9633 | -53.0273 | -0.004577 | -0.086975 | 0.036621 | 5.0034 | 0.15106 | 0.23804 | 0.045776 | -0.086975 | -0.15106 | 0.050354 | 4.6143 | -0.21973 | -0.068664 | -0.022888 | 122.9874 | 122.9965 | 60.4706 | -123.0377 | 123.0011 | 122.9279 | 58.7723 | -123.1018
552.8438 | 123.23 | -52.771 | 70.1019 | 0.50332 | 0.010932 | 0.080969 | -0.020022 | 0.06433 | -0.027656 | -0.0092992 | 0.59613 | -0.013802 | 0.061977 | 0.048175 | 0.0054039 | -0.0020211 | 70.2942 | -47.5021 | 8.0017 | -52.6062 | 70.1019 | -52.8214 | -52.8717 | -47.9645 | 6.221 | -52.9129 | 70.1477 | 70.0562 | -52.8442 | -52.9495 | -0.050354 | -0.10071 | 0 | 5.2689 | 0.16479 | 0.2655 | 0.19226 | -0.073242 | -0.17853 | 0.045776 | 4.8065 | -0.14191 | 0.036621 | -0.045777 | 122.8729 | 123.0652 | 60.7727 | -122.9736 | 122.9187 | 122.8271 | 58.992 | -123.0515
553.8438 | 123.1338 | -52.8076 | 70.1569 | -0.18333 | 0.020545 | 0.082037 | 0.01843 | 0.061125 | 0.011865 | -0.0050262 | -0.39569 | -0.011666 | 0.042751 | 0.054584 | 0.011812 | -0.023383 | 70.1523 | -47.2412 | 8.3405 | -52.5604 | 70.1889 | -52.8168 | -52.8534 | -47.937 | 6.1157 | -52.9816 | 70.2438 | 70.1294 | -52.8534 | -52.9358 | -0.009155 | -0.045777 | 0.032044 | 5.5664 | 0.24719 | 0.29297 | -0.004577 | -0.045777 | -0.12817 | 0.086975 | 4.8706 | -0.17395 | -0.045776 | -0.027465 | 122.9965 | 122.9599 | 61.1481 | -123.0103 | 123.0515 | 122.937 | 58.9233 | -123.0927
554.8438 | 123.1247 | -52.8351 | 70.0836 | -0.33591 | 0.020545 | 0.086309 | 0.0056128 | 0.063262 | 0.0011837 | 0.00031381 | -0.16681 | -0.017006 | 0.053432 | 0.064197 | 0.010744 | -0.027656 | 70.1157 | -46.9986 | 8.7433 | -52.066 | 70.1065 | -52.9037 | -52.977 | -47.7951 | 5.9647 | -53.0548 | 70.134 | 70.0241 | -52.9266 | -53.0319 | -0.068665 | -0.14191 | 0.022888 | 5.8365 | 0.76904 | 0.91095 | 0.032044 | -0.091553 | -0.19684 | 0.050354 | 5.04 | -0.21973 | -0.022889 | -0.059509 | 122.9416 | 122.9507 | 61.5784 | -123.0606 | 122.9691 | 122.8592 | 58.7997 | -123.1155
555.8438 | 123.1476 | -52.4185 | 70.5597 | -0.19858 | 0.013069 | 0.071355 | 0.0034768 | 0.062194 | -0.0030893 | 0.0045868 | -0.3194 | -0.004189 | 0.065182 | 0.058857 | 0.011812 | -0.0094981 | 70.5322 | -46.8842 | 8.7662 | -52.1942 | 70.5505 | -52.4414 | -52.4872 | -47.168 | 6.3263 | -52.5833 | 70.5963 | 70.5093 | -52.4734 | -52.5513 | -0.022888 | -0.068665 | -0.009155 | 5.5344 | 0.2243 | 0.29297 | -0.027465 | -0.054932 | -0.13275 | 0.036621 | 5.2505 | -0.16479 | -0.032043 | -0.050354 | 122.9691 | 122.9507 | 61.1847 | -123.0469 | 123.0148 | 122.9279 | 58.7448 | -123.111
556.8438 | 123.1522 | -52.3178 | 70.6329 | -0.15281 | 0.010932 | 0.083105 | 0.023771 | 0.057921 | 0.0097277 | -0.0082312 | -0.30414 | -0.006325 | 0.064114 | 0.070606 | 0.01288 | -0.020179 | 70.5963 | -46.582 | 9.2697 | -52.0752 | 70.6558 | -52.3499 | -52.4094 | -46.8933 | 6.5506 | -52.5192 | 70.6833 | 70.5917 | -52.4002 | -52.4643 | -0.032044 | -0.091553 | 0.022888 | 5.7358 | 0.24262 | 0.33417 | -0.036622 | -0.082398 | -0.14648 | 0.050354 | 5.4245 | -0.20142 | -0.054932 | -0.041199 | 122.9736 | 122.9141 | 61.5875 | -123.0423 | 123.0011 | 122.9095 | 58.8684 | -123.0972
557.8438 | 123.1613 | -52.2125 | 70.6833 | 0.39651 | 0.010932 | 0.088445 | 0.014158 | 0.046172 | -0.019111 | -0.0071622 | 0.2757 | -0.009529 | 0.058773 | 0.057788 | -0.0042101 | -0.0062931 | 70.6696 | -46.2158 | 9.6954 | -51.9745 | 70.7016 | -52.2491 | -52.3041 | -46.5134 | 6.4041 | -52.4094 | 70.7199 | 70.6284 | -52.2675 | -52.3819 | -0.036622 | -0.091553 | 0.01831 | 5.9967 | 0.23804 | 0.32959 | -0.013733 | -0.054932 | -0.16937 | 0.036621 | 5.6992 | -0.19684 | -0.027466 | -0.054932 | 122.9141 | 122.8821 | 61.908 | -122.9874 | 122.9324 | 122.8409 | 58.6166 | -123.0652
558.8438 | 123.0194 | -52.034 | 70.9122 | -0.091772 | 0.019477 | 0.0799 | 0.016294 | 0.053649 | -0.0062933 | -0.014639 | -0.25836 | -0.004189 | 0.050228 | 0.057788 | 6.2882e-05 | -0.027656 | 70.7977 | -45.3003 | 9.7824 | -51.8692 | 70.8939 | -52.1027 | -52.1713 | -45.9457 | 6.5643 | -52.2766 | 70.9534 | 70.8527 | -52.1301 | -52.1988 | -0.068664 | -0.13733 | -0.01831 | 6.7337 | 0.16479 | 0.30212 | -0.11444 | -0.09613 | -0.16479 | 0.041199 | 6.0883 | -0.24261 | -0.077819 | -0.059509 | 122.9279 | 122.8317 | 61.8164 | -123.0835 | 122.9874 | 122.8867 | 58.5983 | -123.111
559.9688 | 123.2162 | -52.0615 | 70.8389 | -0.2291 | -0.0018849 | 0.1066 | 0.012022 | 0.062194 | -0.019111 | -0.00075419 | -0.42621 | -0.012734 | 0.04916 | 0.047107 | 0.0043349 | -0.010566 | 70.816 | -44.4717 | 10.5286 | -51.6174 | 70.8344 | -52.1164 | -52.1759 | -45.5429 | 6.4178 | -52.2217 | 70.8435 | 70.752 | -52.1347 | -52.2354 | -0.054932 | -0.11444 | -0.004577 | 7.5897 | 0.44403 | 0.55847 | -0.022888 | -0.073243 | -0.17395 | 0.004578 | 6.5186 | -0.16022 | 0.013733 | -0.086975 | 122.8958 | 122.8775 | 62.59 | -123.0148 | 122.905 | 122.8134 | 58.4793 | -123.0743
560.8594 | 123.1659 | -52.1713 | 70.7199 | 0.27444 | -0.021111 | 0.089513 | 0.014158 | 0.058989 | -0.012702 | -0.02532 | 0.47406 | -0.022347 | 0.068386 | 0.055652 | -0.0084821 | -0.0084301 | 70.7245 | -44.5724 | 10.6613 | -51.7731 | 70.7062 | -52.2125 | -52.2629 | -45.3873 | 6.3354 | -52.3407 | 70.752 | 70.6467 | -52.2537 | -52.3224 | -0.041198 | -0.091552 | -0.013733 | 7.5989 | 0.39825 | 0.48981 | 0.004577 | -0.082397 | -0.15106 | 0.032043 | 6.7841 | -0.16937 | -0.01831 | -0.073243 | 122.8775 | 122.8958 | 62.8326 | -122.9828 | 122.9233 | 122.818 | 58.5068 | -123.0423
561.8438 | 123.1201 | -51.8646 | 71.1136 | -0.29014 | -0.0072259 | 0.085241 | 0.010954 | 0.062194 | 0.0065237 | -0.013571 | -0.27362 | -0.015938 | 0.051296 | 0.062061 | 0.0032669 | -0.018043 | 71.0999 | -44.1513 | 10.8444 | -51.5488 | 71.0861 | -51.9104 | -51.9608 | -45.0211 | 6.4819 | -52.034 | 71.1411 | 71.0587 | -51.9196 | -51.9836 | -0.045776 | -0.09613 | -0.027465 | 7.7133 | 0.31586 | 0.41199 | -0.013732 | -0.054932 | -0.11902 | 0.027466 | 6.8436 | -0.16937 | -0.050354 | -0.054931 | 122.9507 | 122.9645 | 62.709 | -123.0743 | 123.0057 | 122.9233 | 58.3466 | -123.0972
562.8438 | 123.0743 | -51.5808 | 71.3928 | -0.29014 | 0.0055921 | 0.083105 | 0.010954 | 0.061125 | 0.0065237 | -0.017844 | -0.21259 | -0.003121 | 0.064114 | 0.070606 | 0.0086079 | -0.024451 | 71.347 | -43.396 | 11.1832 | -51.4343 | 71.3654 | -51.6129 | -51.6632 | -44.5084 | 6.9855 | -51.7822 | 71.4157 | 71.315 | -51.6449 | -51.7364 | -0.032043 | -0.082397 | -0.027466 | 8.1848 | 0.14648 | 0.22888 | -0.045776 | -0.064086 | -0.15564 | 0.022888 | 7.0724 | -0.20142 | -0.045777 | -0.07782 | 122.9462 | 122.9279 | 62.764 | -123.056 | 122.9965 | 122.8958 | 58.5663 | -123.1293
563.8438 | 123.2071 | -51.6586 | 71.2234 | -0.15281 | -0.015771 | 0.086309 | 0.01309 | 0.061125 | -0.011634 | -0.0071622 | 0.64191 | -0.01487 | 0.070522 | 0.058857 | 0.010744 | -0.010566 | 71.2326 | -42.5262 | 11.5173 | -51.3565 | 71.2463 | -51.7319 | -51.8097 | -44.4168 | 6.7108 | -51.7593 | 71.2006 | 71.1594 | -51.741 | -51.8509 | -0.073243 | -0.15106 | 0.022888 | 9.1324 | 0.30212 | 0.45319 | 0.009155 | -0.082398 | -0.19226 | -0.022888 | 7.2418 | -0.10071 | 0.091553 | -0.064087 | 122.905 | 122.8912 | 63.176 | -123.0331 | 122.8592 | 122.818 | 58.3694 | -123.0743
564.8438 | 123.2071 | -52.0157 | 70.8389 | 0.091333 | -0.020043 | 0.098058 | 0.01309 | 0.066466 | -0.0062933 | -0.022116 | -0.12103 | -0.010597 | 0.064114 | 0.064197 | -0.0042101 | -0.023383 | 70.8435 | -40.947 | 11.9797 | -52.0844 | 70.8069 | -52.1393 | -52.1576 | -44.4946 | 6.2164 | -52.1118 | 70.8755 | 70.7611 | -52.1118 | -52.1942 | -0.1236 | -0.14191 | -0.032043 | 11.0687 | -0.068665 | 0.073242 | 0.004578 | -0.09613 | -0.17853 | 0.036621 | 7.5211 | -0.09613 | 0.082398 | -0.07782 | 122.8226 | 122.8592 | 63.9954 | -122.9965 | 122.8912 | 122.7768 | 58.2321 | -123.0331
565.8438 | 123.2254 | -52.1576 | 70.7016 | -0.030737 | -0.016839 | 0.10126 | 0.0056128 | 0.066466 | -0.00095325 | -0.015707 | -0.13629 | -0.02021 | 0.057705 | 0.065265 | 0.0096759 | -0.0041571 | 70.7657 | -39.9673 | 11.9385 | -51.9424 | 70.7062 | -52.2079 | -52.2537 | -44.5496 | 6.2393 | -52.2629 | 70.7565 | 70.6512 | -52.2354 | -52.3087 | -0.050354 | -0.09613 | 0.004578 | 12.1902 | 0.21515 | 0.31128 | 0.064087 | -0.07782 | -0.15106 | 0.054932 | 7.608 | -0.10529 | 0.045777 | -0.050354 | 122.8638 | 122.9233 | 64.0961 | -122.9553 | 122.9141 | 122.8088 | 58.3969 | -123.0103
566.8438 | 123.1613 | -52.1439 | 70.7428 | 0.33547 | -0.012566 | 0.089513 | 0.01843 | 0.062194 | -0.012702 | -0.010367 | 0.077332 | -0.02021 | 0.054501 | 0.074878 | 0.0075399 | -0.01377 | 70.752 | -40.1962 | 11.8881 | -51.9424 | 70.7565 | -52.1896 | -52.2446 | -44.6045 | 6.0699 | -52.3178 | 70.784 | 70.6604 | -52.2308 | -52.327 | -0.045776 | -0.10071 | 0.013733 | 11.9476 | 0.20142 | 0.30212 | 0.009155 | -0.086975 | -0.18311 | 0.041199 | 7.5394 | -0.17395 | 0.009155 | -0.082398 | 122.9004 | 122.8958 | 64.032 | -122.9874 | 122.9279 | 122.8043 | 58.2138 | -123.0698
567.8438 | 123.1705 | -52.3224 | 70.5368 | 0.38125 | -0.01043 | 0.085241 | -0.0018642 | 0.051512 | -0.012702 | -0.0092992 | 0.13837 | -0.012734 | 0.057705 | 0.063129 | 0.0096759 | -0.0084301 | 70.5826 | -39.537 | 11.8286 | -52.0248 | 70.578 | -52.3773 | -52.4048 | -44.9982 | 5.8365 | -52.4734 | 70.5963 | 70.5002 | -52.4094 | -52.4918 | -0.054931 | -0.082397 | 0.041199 | 12.7853 | 0.29755 | 0.37994 | 0.045777 | -0.086975 | -0.16937 | 0.059509 | 7.3242 | -0.15106 | 0.01831 | -0.036621 | 122.9004 | 122.905 | 64.151 | -122.9416 | 122.9187 | 122.8226 | 58.1589 | -123.0286
568.8438 | 123.1934 | -51.796 | 71.0815 | 0.045557 | -0.0061569 | 0.094854 | 0.0077488 | 0.065398 | -0.0084293 | -0.013571 | -0.01422 | -0.008461 | 0.045956 | 0.063129 | 0.0064719 | -0.011634 | 71.1365 | -38.3881 | 12.4695 | -51.3977 | 71.0907 | -51.8463 | -51.8967 | -43.5791 | 5.0125 | -51.9012 | 71.1456 | 71.0495 | -51.8417 | -51.9424 | -0.050354 | -0.10071 | 0.009155 | 13.4079 | 0.39825 | 0.49896 | 0.054932 | -0.045777 | -0.14648 | 0.064087 | 8.2169 | -0.10529 | 0.041199 | -0.032043 | 122.8867 | 122.9324 | 64.2654 | -122.9782 | 122.9416 | 122.8455 | 56.8085 | -123.024
569.8438 | 123.1888 | -51.7593 | 71.109 | -0.27488 | 0.0013191 | 0.1002 | 0.017362 | 0.062194 | 0.00011475 | -0.0071622 | 0.13837 | -0.011666 | 0.052364 | 0.057788 | 0.0064719 | -0.01377 | 71.1136 | -39.0518 | 12.4603 | -51.6907 | 71.1136 | -51.8417 | -51.8875 | -42.9977 | 5.5618 | -51.9058 | 71.1273 | 71.0312 | -51.86 | -51.9379 | -0.082398 | -0.12817 | 0.004577 | 12.7075 | 0.068664 | 0.19684 | 0.004577 | -0.10071 | -0.17853 | 0.01831 | 8.7616 | -0.14648 | 0.032043 | -0.07782 | 122.8729 | 122.8729 | 64.2197 | -122.9965 | 122.8867 | 122.7905 | 57.3212 | -123.0469
570.8438 | 123.1522 | -51.6678 | 71.2509 | 0.2134 | -0.012566 | 0.082037 | 0.021635 | 0.05258 | 0.0043877 | 0.0013818 | -0.21259 | -0.019142 | 0.058773 | 0.054584 | 0.0054039 | -0.0084301 | 71.2509 | -38.5437 | 12.6846 | -51.1597 | 71.2372 | -51.6998 | -51.7776 | -42.6041 | 4.8706 | -51.7776 | 71.2967 | 71.1685 | -51.7181 | -51.8372 | -0.032043 | -0.10986 | -0.013733 | 13.1241 | 0.50812 | 0.61798 | 0 | -0.050354 | -0.16937 | 0.045776 | 9.0637 | -0.10986 | 0.059509 | -0.082398 | 122.905 | 122.9187 | 64.3524 | -123.0286 | 122.9645 | 122.8363 | 56.5384 | -123.0881
571.8438 | 123.1567 | -51.9608 | 70.9579 | 0.36599 | -0.022179 | 0.087377 | 0.010954 | 0.049376 | 0.0011837 | -0.013571 | 0.18414 | -0.009529 | 0.06625 | 0.062061 | 0.0021989 | -0.018043 | 71.0175 | -38.6444 | 12.5656 | -51.7502 | 71.0037 | -51.9516 | -52.0248 | -42.0044 | 4.7699 | -51.9516 | 71.0083 | 70.9122 | -52.0477 | -52.1301 | 0.009155 | -0.064087 | 0.045776 | 13.3163 | 0.21057 | 0.27466 | 0.059509 | -0.086975 | -0.16937 | 0.050354 | 9.9564 | 0.009155 | 0.17853 | -0.045777 | 122.9645 | 122.9782 | 64.5264 | -122.9828 | 122.9691 | 122.8729 | 56.7307 | -123.0881
572.8438 | 123.1522 | -52.8809 | 69.9783 | 0.27444 | -0.0061569 | 0.085241 | 0.025907 | 0.063262 | -0.0062933 | -0.00075419 | 0.16888 | -0.006325 | 0.06625 | 0.072742 | 0.0021989 | -0.015907 | 70.34 | -38.4384 | 16.864 | -52.7161 | 70.3354 | -52.5879 | -52.6794 | -42.627 | 2.8473 | -52.9724 | 70.079 | 69.9417 | -52.9221 | -53.0319 | 0.29297 | 0.20142 | 0.35705 | 14.4424 | 0.16479 | -0.036621 | 0.36163 | -0.041199 | -0.15106 | 0.10071 | 10.2539 | -0.091553 | 0.059509 | -0.036622 | 123.2162 | 123.2208 | 69.7449 | -122.6578 | 122.9599 | 122.8226 | 55.7281 | -123.0103
573.8438 | 123.1934 | -53.6499 | 69.1956 | 0.5491 | -0.0040209 | 0.09165 | 0.0098848 | 0.068602 | 0.0065237 | -0.011435 | 0.30621 | -0.008461 | 0.064114 | 0.067401 | 0.021425 | -0.016975 | 69.3237 | -38.9694 | 18.1229 | -53.1281 | 69.2047 | -53.7277 | -53.7506 | -35.0372 | 5.1956 | -53.5995 | 69.2276 | 69.136 | -53.7506 | -53.8284 | -0.07782 | -0.10071 | 0.009155 | 14.6805 | 0.52185 | 0.62256 | 0.12817 | -0.10071 | -0.17853 | 0.032043 | 18.6127 | 0.050354 | 0.22888 | -0.05951 | 122.8546 | 122.9736 | 71.7728 | -122.9462 | 122.8775 | 122.7859 | 58.8455 | -123.024
574.8438 | 123.1613 | -53.1372 | 69.7769 | 0.86953 | 0.0087961 | 0.088445 | 0.016294 | 0.067534 | 0.0043877 | 0.0056548 | 0.38251 | -0.002053 | 0.072659 | 0.07381 | 0.021425 | -0.0073621 | 69.8181 | -39.743 | 18.0222 | -52.6474 | 69.754 | -53.183 | -53.2425 | -32.7667 | 4.8523 | -53.1052 | 69.6625 | 69.5663 | -53.2837 | -53.3478 | -0.045776 | -0.10529 | -0.022889 | 13.3942 | 0.48981 | 0.59509 | 0.041198 | -0.14648 | -0.21057 | -0.11444 | 20.3705 | 0.032043 | 0.24261 | -0.21057 | 122.8912 | 122.9553 | 71.1594 | -123.0194 | 122.7997 | 122.7036 | 57.9895 | -123.1247
575.8438 | 123.1613 | -54.7348 | 68.129 | 0.18289 | 0.0055921 | 0.093786 | 0.0077488 | 0.066466 | -0.0020213 | -0.0028902 | 0.29095 | -0.008461 | 0.068386 | 0.071674 | 0.023561 | -0.0052251 | 68.161 | -35.8521 | 22.3068 | -54.2496 | 68.1473 | -54.7852 | -54.8355 | -33.8928 | 6.6193 | -54.6341 | 68.1656 | 68.074 | -54.7989 | -54.8859 | -0.050354 | -0.10071 | 0.018311 | 18.8828 | 0.48523 | 0.58594 | 0.032044 | -0.064087 | -0.15106 | 0.036621 | 20.842 | 0.10071 | 0.25177 | -0.054931 | 122.8821 | 122.8958 | 77.0416 | -122.9645 | 122.9004 | 122.8088 | 61.3541 | -123.0148
576.8438 | 123.143 | -55.3528 | 67.5293 | 0.42703 | -0.0040209 | 0.09165 | 0.012022 | 0.061125 | -0.010566 | -0.017844 | 0.24518 | -0.010597 | 0.069454 | 0.06847 | 0.011812 | -0.0073621 | 67.5842 | -37.944 | 23.0667 | -54.6661 | 67.5522 | -55.3802 | -55.426 | -35.2478 | 10.6018 | -55.0919 | 67.5705 | 67.4744 | -55.4031 | -55.5176 | -0.027466 | -0.073242 | 0.022888 | 17.4088 | 0.68665 | 0.75989 | 0.054932 | -0.050354 | -0.16479 | 0.041199 | 20.105 | 0.26093 | 0.42572 | -0.054932 | 122.905 | 122.937 | 78.4195 | -122.9553 | 122.9233 | 122.8271 | 65.9546 | -123.0469
577.8438 | 123.1796 | -55.0278 | 67.8223 | 0.45754 | -0.0082939 | 0.093786 | 0.0045448 | 0.067534 | 0.0075917 | -0.010367 | 0.2757 | -0.008461 | 0.065182 | 0.072742 | 0.013948 | -0.021247 | 67.8268 | -35.3348 | 24.6231 | -54.3091 | 67.8268 | -55.1102 | -55.1468 | -35.0052 | 13.179 | -54.9591 | 67.8452 | 67.749 | -55.1331 | -55.1971 | -0.082397 | -0.11902 | 0.004577 | 19.693 | 0.71869 | 0.83771 | 0.004577 | -0.10529 | -0.16937 | 0.022888 | 20.0226 | 0.068665 | 0.23804 | -0.073243 | 122.8546 | 122.8546 | 79.6509 | -122.9691 | 122.8729 | 122.7768 | 68.2068 | -123.0194
578.8438 | 123.1567 | -54.808 | 68.0786 | 0.45754 | 0.0087961 | 0.092718 | 0.019498 | 0.063262 | 0.012933 | -0.015707 | 0.36725 | -0.004189 | 0.073727 | 0.080219 | 0.016085 | -0.022315 | 68.1244 | -30.9631 | 30.9128 | -53.8101 | 68.0878 | -54.8309 | -54.8904 | -35.2386 | 9.5718 | -54.744 | 68.1381 | 67.9916 | -54.863 | -54.9683 | -0.022889 | -0.082398 | 0.009156 | 23.8449 | 0.99792 | 1.0803 | 0.045777 | -0.054932 | -0.16022 | 0.05951 | 19.5694 | 0.064086 | 0.2243 | -0.086975 | 122.8958 | 122.9324 | 85.7208 | -122.9691 | 122.9462 | 122.7997 | 64.3799 | -123.0469
579.8438 | 123.1338 | -55.1056 | 67.7536 | 0.45754 | 0.016273 | 0.09699 | 0.0045448 | 0.072875 | 0.0065237 | -0.0082312 | 0.39777 | -0.003121 | 0.059841 | 0.085559 | 0.016085 | -0.010566 | 67.8406 | -27.5711 | 34.3277 | -54.2679 | 67.7719 | -55.1422 | -55.2155 | -34.4513 | 10.4691 | -55.0461 | 67.7948 | 67.6987 | -55.1743 | -55.2567 | -0.036621 | -0.10986 | 0.018311 | 27.5345 | 0.83771 | 0.94757 | 0.086975 | -0.068664 | -0.15106 | 0.041199 | 20.6543 | 0.059509 | 0.21057 | -0.054932 | 122.8775 | 122.9462 | 89.4333 | -122.9691 | 122.9004 | 122.8043 | 65.5746 | -123.0103
580.8438 | 123.2025 | -54.8813 | 67.9642 | 0.61013 | 0.0087961 | 0.092718 | 0.0098848 | 0.06967 | 0.012933 | -0.010367 | 1.0539 | -0.003121 | 0.07159 | 0.066333 | 0.020357 | -0.028724 | 68.1198 | -24.4766 | 34.4238 | -53.9795 | 68.0328 | -54.8996 | -54.9362 | -33.2932 | 9.9655 | -54.8172 | 68.0328 | 67.9092 | -54.9545 | -55.0369 | -0.01831 | -0.054931 | 0.068665 | 30.4047 | 0.90179 | 0.95673 | 0.15564 | -0.073242 | -0.15564 | 0.068665 | 21.5881 | 0.064087 | 0.21973 | -0.054931 | 122.9141 | 123.0011 | 89.3051 | -122.9004 | 122.9141 | 122.7905 | 64.8468 | -123.0011
581.8438 | 123.2117 | -54.7256 | 68.074 | 0.4728 | 0.020545 | 0.1034 | 0.015226 | 0.083556 | 0.019342 | 0.0035188 | 0.33673 | -0.00098395 | 0.079067 | 0.082355 | 0.021425 | -0.01377 | 68.1793 | -21.9269 | 40.86 | -53.627 | 68.0695 | -54.8538 | -54.8676 | -33.0963 | 10.5148 | -54.7577 | 68.1152 | 68.0283 | -54.8447 | -54.9088 | -0.12817 | -0.14191 | -0.004578 | 32.7988 | 1.0986 | 1.2405 | 0.10528 | -0.11902 | -0.1831 | 0.041198 | 21.6293 | -0.032043 | 0.15106 | -0.045777 | 122.7951 | 122.905 | 95.5856 | -122.9416 | 122.8409 | 122.7539 | 65.2405 | -122.9828
582.8438 | 123.1613 | -55.2933 | 67.5751 | 0.48806 | -0.0040209 | 0.10767 | 0.012022 | 0.08142 | 0.0033197 | -0.0082312 | 0.30621 | -0.007393 | 0.080135 | 0.078083 | 0.016085 | -0.0073621 | 67.6071 | -20.7687 | 42.1829 | -54.1901 | 67.5659 | -55.3436 | -55.3848 | -33.1558 | 10.8948 | -55.2292 | 67.6209 | 67.543 | -55.3482 | -55.481 | -0.050354 | -0.091553 | -0.009155 | 34.5245 | 1.1032 | 1.1948 | 0.032044 | -0.054932 | -0.18768 | 0.045777 | 22.1375 | 0.064087 | 0.25177 | -0.032043 | 122.8592 | 122.9004 | 97.4762 | -122.9599 | 122.9141 | 122.8363 | 66.188 | -123.056
583.8438 | 123.1613 | -55.7236 | 67.099 | 0.4728 | 0.0077281 | 0.11942 | 0.00027184 | 0.080351 | -0.0030893 | -0.0060942 | 0.32147 | -0.01487 | 0.077999 | 0.078083 | 0.01288 | -0.0041571 | 67.1906 | -21.2952 | 59.6924 | -54.5288 | 67.131 | -55.751 | -55.806 | -32.753 | 10.4004 | -55.6778 | 67.1677 | 67.067 | -55.7877 | -55.8929 | -0.027466 | -0.082397 | 0.032043 | 34.4284 | 1.1948 | 1.2772 | 0.091553 | -0.064087 | -0.16937 | 0.068665 | 22.9706 | 0.045777 | 0.21515 | -0.032043 | 122.8546 | 122.9141 | 115.416 | -122.905 | 122.8912 | 122.7905 | 66.124 | -122.9919
584.8438 | 123.1293 | -55.9845 | 66.8655 | 0.44228 | 0.012 | 0.11408 | 0.024839 | 0.080351 | -0.0041573 | -0.0050262 | 0.39777 | -0.004189 | 0.068386 | 0.072742 | 0.0011309 | -0.019111 | 66.9571 | -20.2744 | 61.0565 | -54.7668 | 66.8793 | -56.0257 | -56.0669 | -32.2037 | 11.6776 | -55.9479 | 66.8655 | 66.7969 | -56.0806 | -56.1676 | -0.041199 | -0.082398 | 0.013732 | 35.7101 | 1.2177 | 1.3 | 0.091552 | -0.09613 | -0.18311 | 0 | 23.7808 | 0.036621 | 0.21973 | -0.068665 | 122.8638 | 122.9416 | 117.041 | -122.9324 | 122.85 | 122.7814 | 67.662 | -123.0331
585.8438 | 123.1659 | -56.163 | 66.7145 | 0.42703 | 0.0066601 | 0.10874 | 0.0066808 | 0.062194 | 0.0043877 | -0.0082312 | 0.41303 | -0.002053 | 0.08334 | 0.085559 | 0.023561 | -0.0073621 | 66.7831 | -33.5403 | 60.9604 | -54.744 | 66.7145 | -56.1859 | -56.2408 | -29.4708 | 13.4583 | -56.0257 | 66.7374 | 66.6458 | -56.2225 | -56.3049 | -0.022888 | -0.07782 | 0 | 22.6227 | 1.4191 | 1.4969 | 0.068664 | -0.059509 | -0.14191 | 0.022888 | 26.6922 | 0.13733 | 0.27924 | -0.068665 | 122.8775 | 122.9462 | 117.1234 | -122.9553 | 122.9004 | 122.8088 | 69.6213 | -123.0194
586.8438 | 123.1888 | -55.9708 | 66.8518 | 0.44228 | 0.02375 | 0.099126 | 0.01309 | 0.072875 | 0.0097277 | -0.015707 | 0.36725 | -0.005257 | 0.08334 | 0.071674 | 0.013948 | -0.015907 | 66.9617 | -32.666 | 62.5854 | -55.4214 | 66.8976 | -56.0257 | -56.0761 | -30.4596 | 14.5752 | -55.8701 | 66.9022 | 66.8106 | -56.0577 | -56.1401 | -0.054932 | -0.10529 | 0.045776 | 23.3047 | 0.54932 | 0.6546 | 0.10986 | -0.086975 | -0.16937 | 0.050354 | 25.5112 | 0.10071 | 0.27008 | -0.041199 | 122.8683 | 122.9324 | 118.5562 | -122.9279 | 122.8729 | 122.7814 | 70.546 | -122.9919
587.8438 | 123.1979 | -55.719 | 67.1356 | 0.79324 | 0.014137 | 0.095922 | 0.028043 | 0.072875 | 0.016137 | 0.0067228 | 0.41303 | -0.005257 | 0.082272 | 0.067401 | 0.027834 | -0.022315 | 67.2775 | -32.7164 | 64.4623 | -55.101 | 67.1997 | -55.719 | -55.7648 | -28.6331 | 8.5556 | -55.6091 | 67.1539 | 67.0715 | -55.7831 | -55.8655 | 0 | -0.045777 | 0.064087 | 23.0026 | 0.61798 | 0.66376 | 0.14191 | -0.064087 | -0.14648 | 0.018311 | 27.0859 | 0.10986 | 0.25635 | -0.064087 | 122.9187 | 122.9965 | 120.1813 | -122.9004 | 122.8729 | 122.7905 | 64.2746 | -123.0011
588.8438 | 123.175 | -56.2775 | 66.5955 | 0.53384 | 0.025886 | 0.11194 | 0.016294 | 0.091033 | 0.00011475 | 0.022745 | 0.39777 | -0.009529 | 0.08334 | 0.095172 | 0.0096759 | -0.014838 | 66.4352 | -26.5594 | 63.9496 | -54.6844 | 66.5268 | -56.3416 | -56.369 | -29.0176 | 8.5968 | -56.1172 | 66.6 | 66.5314 | -56.337 | -56.4423 | -0.064087 | -0.091553 | -0.068665 | 29.718 | 1.593 | 1.6846 | -0.16022 | -0.059509 | -0.1648 | 0.004578 | 27.2598 | 0.16022 | 0.32501 | -0.064087 | 122.8043 | 122.7127 | 120.2271 | -122.9645 | 122.8775 | 122.8088 | 64.8743 | -123.0377
589.8438 | 123.1476 | -56.8405 | 66.0095 | 0.48806 | 0.0023871 | 0.13117 | 0.0077488 | 0.089965 | 0.0054557 | 0.0013818 | 0.38251 | -0.006325 | 0.086544 | 0.087696 | 0.018221 | -0.010566 | 66.0553 | -2.3529 | 63.3362 | -54.9866 | 65.9912 | -56.9 | -56.955 | -30.0064 | 9.0546 | -56.6895 | 66.0553 | 65.9546 | -56.8954 | -56.987 | -0.059509 | -0.11444 | -0.01831 | 54.4876 | 1.8539 | 1.9684 | 0.045777 | -0.054932 | -0.14648 | 0.045777 | 26.8341 | 0.15106 | 0.29755 | -0.054931 | 122.8317 | 122.8958 | 120.1767 | -122.9645 | 122.8958 | 122.7951 | 65.8951 | -122.9965
590.8438 | 123.143 | -58.4885 | 64.3387 | 0.48806 | 0.0098641 | 0.16642 | 0.0034768 | 0.12308 | 0.024682 | 0.00031381 | 0.39777 | -0.007393 | 0.090817 | 0.077014 | 0.020357 | -0.0041571 | 64.4714 | 48.4909 | 61.8256 | -55.8929 | 64.4119 | -58.4702 | -58.5068 | -32.5882 | 7.8323 | -57.962 | 64.4211 | 64.3158 | -58.5342 | -58.6624 | 0.01831 | -0.018311 | 0.073242 | 106.9794 | 2.5955 | 2.6138 | 0.13275 | -0.045777 | -0.17395 | 0.082398 | 25.9003 | 0.52643 | 0.70038 | -0.022888 | 122.9004 | 122.9599 | 120.314 | -122.8455 | 122.9095 | 122.8043 | 66.3208 | -123.0011
591.8438 | 123.1842 | -58.8455 | 63.9679 | 0.5491 | 0.015205 | 0.15574 | -0.0040002 | 0.12735 | 0.0075917 | 0.0056548 | 0.33673 | -0.006325 | 0.096157 | 0.089832 | 0.015017 | -0.0094981 | 64.1327 | 49.8642 | 61.4548 | -56.2363 | 63.9679 | -58.9279 | -58.9828 | -30.9082 | 7.402 | -58.4656 | 64.0091 | 63.9313 | -58.9279 | -59.0103 | -0.082397 | -0.13733 | 0 | 108.7097 | 2.6093 | 2.7466 | 0.16479 | -0.082397 | -0.16479 | 0.041198 | 27.9373 | 0.37994 | 0.54474 | -0.036622 | 122.8134 | 122.9782 | 120.3003 | -122.9507 | 122.8546 | 122.7768 | 66.2476 | -122.9782
592.8438 | 123.1659 | -57.5729 | 65.2588 | 0.53384 | 0.010932 | 0.16001 | 0.0077488 | 0.13376 | 0.02041 | 0.00031381 | 3.1291 | -0.004189 | 0.091885 | 0.089832 | 0.013948 | -0.0020211 | 65.3229 | 52.5146 | 62.7457 | -54.4693 | 65.2496 | -57.6279 | -57.692 | -25.7355 | 10.2722 | -57.3898 | 65.2771 | 65.1535 | -57.692 | -57.7515 | -0.054932 | -0.11902 | -0.009155 | 110.0876 | 3.1036 | 3.2227 | 0.064087 | -0.11902 | -0.17853 | 0.018311 | 31.8375 | 0.18311 | 0.36163 | -0.10529 | 122.8226 | 122.8958 | 120.3186 | -122.9507 | 122.85 | 122.7264 | 67.8452 | -123.0103
593.8438 | 123.1384 | -58.2184 | 64.5721 | 0.44228 | 0.012 | 0.16855 | 0.016294 | 0.13055 | 0.033227 | -0.010367 | 0.42828 | -0.009529 | 0.096157 | 0.084491 | 0.025698 | -0.0084301 | 64.7278 | 52.4597 | 62.0453 | -54.9637 | 64.6271 | -58.223 | -58.3008 | -26.7838 | 9.3018 | -58.1223 | 64.65 | 64.563 | -58.2962 | -58.3603 | -0.004577 | -0.082397 | 0.054931 | 110.6781 | 3.2547 | 3.3371 | 0.15564 | -0.07782 | -0.14191 | 0.077819 | 31.4346 | 0.096131 | 0.23804 | -0.009156 | 122.8455 | 122.9462 | 120.2637 | -122.8729 | 122.8683 | 122.7814 | 67.5201 | -122.9324
594.8438 | 123.1247 | -59.2712 | 63.5971 | 0.50332 | 0.020545 | 0.16001 | 0.025907 | 0.1188 | 0.034295 | 0.0024508 | 0.33673 | -0.009529 | 0.11538 | 0.081287 | 0.033175 | -0.0041571 | 63.4964 | 51.6449 | 60.8643 | -55.8334 | 63.6154 | -59.3124 | -59.3719 | -25.4745 | 13.4262 | -59.1705 | 63.6841 | 63.5284 | -59.3308 | -59.4498 | -0.041199 | -0.10071 | 0.01831 | 110.9161 | 3.4378 | 3.5385 | -0.10071 | -0.05951 | -0.17853 | 0.086975 | 33.7967 | 0.10071 | 0.27924 | -0.068665 | 122.8867 | 122.7676 | 120.1355 | -122.9691 | 122.9553 | 122.7997 | 72.6974 | -123.0469
595.8438 | 123.1384 | -59.5276 | 63.2812 | 0.5491 | 0.0077281 | 0.17176 | 0.020567 | 0.12842 | 0.015069 | 0.00031381 | 0.41303 | -0.008461 | 0.096157 | 0.1144 | 0.026766 | 0.00011494 | 63.3728 | 51.8509 | 60.5713 | -56.2408 | 63.2904 | -59.5734 | -59.6191 | -23.0621 | 16.5939 | -59.3536 | 63.2858 | 63.2355 | -59.6054 | -59.6878 | -0.045776 | -0.091553 | 0.009155 | 111.3785 | 3.2867 | 3.3783 | 0.091553 | -0.07782 | -0.16022 | 0.004578 | 36.4655 | 0.17395 | 0.33417 | -0.045776 | 122.818 | 122.9004 | 120.0989 | -122.9004 | 122.8134 | 122.7631 | 76.1215 | -122.9691
596.8438 | 123.1888 | -59.6649 | 63.1577 | -0.045996 | 0.020545 | 0.17924 | 0.020567 | 0.12308 | 0.015069 | 0.0035188 | 0.44354 | -0.00098395 | 0.1015 | 0.099445 | 0.020357 | -0.018043 | 63.2492 | 51.9791 | 60.4477 | -55.2612 | 63.1668 | -59.6924 | -59.7061 | -22.6913 | 16.0904 | -59.4635 | 63.208 | 63.1165 | -59.7244 | -59.816 | -0.027466 | -0.041199 | 0.009155 | 111.644 | 4.4037 | 4.4449 | 0.091553 | -0.059509 | -0.15106 | 0.050354 | 36.9736 | 0.20142 | 0.35248 | -0.041199 | 122.8317 | 122.9141 | 120.1126 | -122.8638 | 122.8729 | 122.7814 | 75.7553 | -122.9736
597.8438 | 123.1842 | -59.729 | 63.0478 | 0.53384 | 0.02909 | 0.18137 | 0.024839 | 0.12414 | 0.023614 | 0.0067228 | 0.42828 | -0.005257 | 0.10043 | 0.093036 | 0.019289 | -0.0073621 | 63.1439 | 51.7639 | 60.4568 | -55.687 | 63.0844 | -59.7885 | -59.8297 | -23.8358 | 16.3467 | -59.6329 | 63.1302 | 63.0341 | -59.8343 | -59.8846 | -0.059509 | -0.10071 | 0.036621 | 111.4929 | 4.0421 | 4.1428 | 0.09613 | -0.10529 | -0.15564 | 0.082397 | 35.8933 | 0.09613 | 0.25177 | -0.013733 | 122.8134 | 122.8729 | 120.1859 | -122.8775 | 122.8592 | 122.7631 | 76.0757 | -122.9324
598.8438 | 123.1567 | -59.5184 | 63.2996 | 0.51858 | 0.028022 | 0.18244 | 0.0077488 | 0.12308 | 0.026818 | 0.015268 | 0.41303 | -0.005257 | 0.10043 | 0.0909 | 0.018221 | -0.011634 | 63.3179 | 52.1713 | 60.585 | -55.9067 | 63.3087 | -59.5917 | -59.6512 | -24.2294 | 19.043 | -59.404 | 63.3453 | 63.2538 | -59.6237 | -59.7061 | -0.073242 | -0.13275 | 0.009155 | 111.6898 | 3.6118 | 3.7445 | 0.01831 | -0.10528 | -0.18768 | 0.045776 | 35.289 | 0.11444 | 0.30212 | -0.045777 | 122.8271 | 122.8363 | 120.1035 | -122.9507 | 122.8638 | 122.7722 | 78.5614 | -123.0057
599.8438 | 123.1155 | -59.1843 | 63.6703 | 0.48806 | 0.032295 | 0.18458 | 0.021635 | 0.13055 | 0.030023 | -0.0018222 | 0.32147 | -0.003121 | 0.10791 | 0.10265 | 0.023561 | -0.0084301 | 63.588 | 52.8854 | 60.5576 | -55.9845 | 63.6337 | -59.3079 | -59.3033 | -25.7172 | 15.4404 | -59.0469 | 63.7115 | 63.6749 | -59.2117 | -59.3216 | -0.1236 | -0.11902 | -0.036621 | 112.0697 | 3.1998 | 3.3188 | -0.082397 | -0.027466 | -0.13733 | 0.041199 | 33.4671 | 0.13733 | 0.27466 | 0.004578 | 122.818 | 122.7722 | 119.7418 | -122.9736 | 122.8958 | 122.8592 | 74.6246 | -122.9919
600.8438 | 123.0515 | -59.3079 | 63.6063 | 0.53384 | 0.031227 | 0.1771 | 0.01843 | 0.12735 | 0.039636 | 0.0142 | 0.26044 | 0.007561 | 0.099361 | 0.10265 | 0.02463 | 0.0022509 | 63.501 | 53.0228 | 60.3287 | -55.9067 | 63.5971 | -59.3628 | -59.3765 | -23.0484 | 12.4466 | -59.2621 | 63.6475 | 63.5742 | -59.3582 | -59.4772 | -0.054932 | -0.068665 | -0.009155 | 112.3306 | 3.4012 | 3.4698 | -0.10529 | -0.050354 | -0.16937 | 0.041199 | 36.2595 | 0.045776 | 0.21515 | -0.032043 | 122.905 | 122.8088 | 119.6365 | -122.9828 | 122.9553 | 122.8821 | 71.7545 | -123.0835
601.8438 | 123.024 | -59.0515 | 63.8306 | 0.30496 | 0.039771 | 0.18137 | 0.0066808 | 0.13589 | 0.022546 | 0.0099268 | 0.21466 | 0.005424 | 0.11325 | 0.094104 | 0.020357 | -0.0030891 | 63.7939 | 53.0869 | 60.4431 | -55.5908 | 63.8947 | -59.0698 | -59.1019 | -23.8541 | 11.5082 | -59.0744 | 63.9175 | 63.8489 | -59.1248 | -59.1934 | -0.01831 | -0.050354 | 0.064087 | 112.1384 | 3.4607 | 3.511 | -0.036621 | -0.073242 | -0.14191 | 0.086976 | 35.1974 | -0.022888 | 0.11902 | 0.018311 | 122.9462 | 122.8455 | 119.4946 | -122.9324 | 122.9691 | 122.9004 | 70.5597 | -123.024
602.8438 | 123.0927 | -58.754 | 64.1556 | 3.784 | 0.021614 | 0.18351 | 0.017362 | 0.13162 | 0.023614 | 0.0088588 | 0.30621 | -0.00098395 | 0.10791 | 0.10372 | 0.011812 | 0.0022509 | 64.0137 | 53.4714 | 60.7498 | -55.1834 | 64.151 | -58.7769 | -58.8135 | -23.8861 | 14.4608 | -58.6578 | 64.1739 | 64.1098 | -58.8135 | -58.8959 | -0.022888 | -0.05951 | -0.004578 | 112.2253 | 3.5706 | 3.6301 | -0.14191 | -0.05951 | -0.14191 | 0.01831 | 34.8679 | 0.09613 | 0.23804 | -0.045777 | 122.905 | 122.7676 | 119.5038 | -122.9691 | 122.9279 | 122.8638 | 73.2147 | -123.0515
603.8438 | 123.056 | -58.3008 | 64.6225 | 0.45754 | 0.013069 | 0.1803 | 0.021635 | 0.1188 | 0.027886 | 0.013132 | 0.30621 | 0.007561 | 0.10684 | 0.13042 | 0.02997 | 0.0011829 | 64.5218 | 53.6819 | 61.0565 | -54.7897 | 64.6225 | -58.3191 | -58.3374 | -24.8749 | 13.3987 | -58.1589 | 64.6591 | 64.595 | -58.3237 | -58.4198 | -0.018311 | -0.036621 | 0 | 111.9827 | 3.511 | 3.5477 | -0.10071 | -0.022888 | -0.11902 | 0.036621 | 33.4259 | 0.14191 | 0.26093 | -0.027466 | 122.9233 | 122.8226 | 119.3573 | -122.9599 | 122.9599 | 122.8958 | 71.6995 | -123.0423
604.8438 | 123.0286 | -58.4335 | 64.5081 | 0.50332 | 0.02375 | 0.18885 | 0.020567 | 0.12521 | 0.033227 | 0.012064 | 0.36725 | 0.004356 | 0.12713 | 0.10265 | 0.015017 | -0.0020211 | 64.3753 | 53.5492 | 60.5804 | -55.8243 | 64.4943 | -58.4152 | -58.4793 | -24.8291 | 10.9543 | -58.3557 | 64.5355 | 64.476 | -58.4656 | -58.5434 | 0.018311 | -0.045776 | -0.013733 | 111.9827 | 2.6093 | 2.655 | -0.13275 | -0.032043 | -0.10986 | 0.027465 | 33.6044 | 0.07782 | 0.18768 | -0.032044 | 122.9279 | 122.8088 | 119.014 | -122.9874 | 122.9691 | 122.9095 | 69.3878 | -123.0515
605.8438 | 123.0148 | -58.5617 | 64.325 | 0.12185 | 0.052589 | 0.17817 | 0.017362 | 0.12948 | 0.026818 | 0.0045868 | 0.10785 | -0.00098395 | 0.11218 | 0.11119 | 0.027834 | -0.0052251 | 64.2792 | 53.6041 | 60.3653 | -54.9271 | 64.3707 | -58.5617 | -58.6258 | -21.785 | 17.2485 | -58.4793 | 64.3341 | 64.3066 | -58.6166 | -58.7265 | 0 | -0.064086 | 0.045777 | 112.1658 | 3.6346 | 3.6987 | -0.045776 | -0.054931 | -0.16479 | 0.009155 | 36.7767 | 0.082398 | 0.24719 | -0.01831 | 122.9324 | 122.8409 | 118.927 | -122.9507 | 122.8958 | 122.8683 | 75.8102 | -123.0515
606.8438 | 123.0011 | -58.8318 | 64.0549 | 0.16763 | 0.04084 | 0.18671 | 0.017362 | 0.12735 | 0.024682 | 0.015268 | 0.13837 | 0.011833 | 0.12606 | 0.10051 | 0.018221 | 0.0022509 | 64.0182 | 53.6636 | 59.9442 | -55.0873 | 64.0594 | -58.8684 | -58.9142 | -20.1324 | 13.7741 | -58.7357 | 64.0869 | 64.0228 | -58.8959 | -58.9828 | -0.036621 | -0.082398 | 0.004577 | 112.4954 | 3.7445 | 3.8269 | -0.036621 | -0.064087 | -0.15106 | 0.032043 | 38.6993 | 0.09613 | 0.24719 | -0.032044 | 122.8912 | 122.85 | 118.7759 | -122.9691 | 122.9187 | 122.8546 | 72.6059 | -123.0377
607.8438 | 123.0606 | -58.7631 | 64.1235 | -0.00022031 | 0.055793 | 0.19312 | 0.024839 | 0.13482 | 0.02575 | 0.015268 | -0.13629 | 0.004356 | 0.1282 | 0.10692 | 0.022493 | -0.0073621 | 64.119 | 53.9246 | 60.3333 | -56.3141 | 64.1373 | -58.7631 | -58.8364 | -17.8482 | 13.092 | -58.5526 | 64.1647 | 64.0869 | -58.7997 | -58.8821 | 0 | -0.073242 | 0.013733 | 112.6877 | 2.449 | 2.5223 | -0.004577 | -0.036621 | -0.11902 | 0.041199 | 40.9149 | 0.21057 | 0.32959 | -0.036621 | 122.9004 | 122.8821 | 119.0964 | -122.9599 | 122.9279 | 122.85 | 71.8552 | -123.0057
608.8438 | 123.111 | -57.3624 | 65.4648 | 0.51858 | 0.02375 | 0.19526 | 0.025907 | 0.11667 | 0.017205 | 0.010995 | 0.5351 | -0.00098395 | 0.12286 | 0.10158 | 0.0064719 | 0.0033199 | 65.5151 | 55.2704 | 61.5509 | -53.4576 | 65.5975 | -57.2754 | -57.3257 | -14.9826 | 13.8199 | -57.1838 | 65.5106 | 65.4373 | -57.4356 | -57.518 | 0.086975 | 0.036621 | 0.13275 | 112.6328 | 3.9047 | 3.8681 | 0.050354 | -0.073242 | -0.15564 | 0.045776 | 42.3798 | 0.17853 | 0.33417 | -0.027466 | 122.9599 | 122.8775 | 118.9133 | -122.7905 | 122.8729 | 122.7997 | 71.1823 | -122.9828
609.8438 | 123.0606 | -61.8713 | 60.997 | 0.13711 | 0.042976 | 0.19846 | 0.0056128 | 0.12948 | 0.026818 | 0.018472 | 0.12311 | 0.10476 | 0.098293 | 0.14431 | 0.037447 | -0.0020211 | 60.8551 | 49.9969 | 56.1218 | -57.6553 | 60.9009 | -61.9537 | -62.0224 | 60.5621 | 26.532 | -61.4502 | 61.0107 | 60.965 | -61.94 | -62.0316 | -0.082397 | -0.15106 | -0.09613 | 111.8683 | 4.216 | 4.3671 | -0.14191 | -0.068664 | -0.16022 | 0.013733 | 122.4335 | 0.42114 | 0.58136 | -0.032043 | 122.7722 | 122.7264 | 117.9932 | -123.0194 | 122.8821 | 122.8363 | 88.4033 | -123.0286
610.8438 | 123.024 | -62.5214 | 60.347 | 0.030298 | 0.047248 | 0.18885 | 0.014158 | 0.12094 | 0.031091 | 0.012064 | -0.090514 | 0.25643 | 0.073727 | 0.19024 | 0.15494 | 0.0075919 | 60.2509 | 49.5255 | 55.545 | -58.0994 | 60.2875 | -62.6129 | -62.6633 | 60.0769 | 26.413 | -45.0851 | 60.2646 | 60.2829 | -62.5397 | -62.6404 | -0.091553 | -0.14191 | -0.059509 | 112.0468 | 4.422 | 4.5639 | -0.096131 | -0.018311 | -0.11902 | -0.082398 | 122.5983 | 17.4362 | 17.5552 | -0.064087 | 122.8088 | 122.7722 | 118.0664 | -123.0103 | 122.7859 | 122.8043 | 88.9343 | -122.9874
611.8438 | 123.0652 | -61.4594 | 61.4227 | 0.10659 | 0.038703 | 0.20807 | 0.014158 | 0.1391 | 0.026818 | 0.018472 | -0.075256 | 0.11651 | 0.10684 | 0.15178 | 0.040651 | 0.0033199 | 61.377 | 50.7156 | 56.6574 | -56.4697 | 61.4044 | -61.4822 | -61.5326 | 61.4548 | 23.703 | -60.5438 | 61.4456 | 61.3815 | -61.5005 | -61.615 | -0.022888 | -0.073242 | -0.01831 | 112.175 | 4.9896 | 5.0629 | -0.045776 | -0.041198 | -0.15564 | 0.022889 | 122.9141 | 0.91553 | 1.0712 | -0.041198 | 122.8638 | 122.8363 | 118.1168 | -122.9553 | 122.905 | 122.8409 | 85.1624 | -123.0377
612.8438 | 123.0423 | -61.0153 | 61.8347 | -0.15281 | 0.036567 | 0.21769 | 0.022703 | 0.13269 | 0.019342 | 0.015268 | -0.21259 | 0.11224 | 0.095089 | 0.13897 | 0.048128 | 0.0043879 | 61.6928 | 50.9491 | 56.7261 | -56.3507 | 61.7889 | -61.1206 | -61.1481 | 61.8576 | 23.2178 | -60.1959 | 61.8805 | 61.8073 | -61.0931 | -61.171 | -0.10528 | -0.13275 | -0.045777 | 111.9644 | 4.6646 | 4.7974 | -0.14191 | -0.07782 | -0.15564 | 0.045776 | 122.8729 | 0.8194 | 0.97504 | -0.027466 | 122.8043 | 122.7081 | 117.7414 | -122.9828 | 122.8958 | 122.8226 | 84.2331 | -123.0057
613.8438 | 123.2849 | -62.4207 | 60.2646 | 1.1594 | 0.0023871 | 0.20914 | 0.014158 | 0.13696 | -0.0052253 | 0.01954 | 0.61139 | 0.11437 | 0.085476 | 0.13256 | 0.10367 | 0.015069 | 61.4868 | 48.9578 | 55.1331 | -56.4102 | 61.0107 | -61.7294 | -61.9858 | 61.4868 | 28.2028 | -65.1031 | 61.116 | 61.0611 | -61.6699 | -61.853 | 0.69122 | 0.43487 | 0.74616 | 111.3785 | 6.0104 | 5.5756 | 1.2222 | 0.75073 | 0.56763 | 0.85144 | 123.9075 | -2.6825 | -3.2501 | 0.79651 | 123.4314 | 123.9075 | 117.5537 | -122.2504 | 123.5367 | 123.4818 | 90.6235 | -122.1176
614.8438 | 122.9919 | -62.5259 | 60.3653 | -0.3054 | 0.014137 | 0.23585 | 0.023771 | 0.12628 | 0.039636 | 0.012064 | -0.28888 | 0.099418 | 0.10791 | 0.1411 | 0.02997 | -0.0030891 | 60.2234 | 48.8297 | 53.5721 | -54.5059 | 60.3058 | -62.6175 | -62.6404 | 60.2509 | 33.8333 | -63.3682 | 60.3058 | 60.2509 | -62.645 | -62.6999 | -0.091553 | -0.11444 | -0.059509 | 111.3556 | 8.02 | 8.1345 | -0.14191 | -0.11902 | -0.17395 | -0.059509 | 122.7768 | -0.84229 | -0.66833 | -0.11444 | 122.8317 | 122.7493 | 116.098 | -123.0057 | 122.8317 | 122.7768 | 96.3593 | -123.0652
615.8438 | 122.9233 | -66.7831 | 56.0303 | -0.32065 | 0.031227 | 0.2241 | 0.0077488 | 0.1391 | 0.0086597 | 0.016336 | -0.33466 | 1.5553 | 0.37814 | 0.19558 | 1.6973 | 0.021478 | 56.0577 | 46.0052 | 42.4347 | -62.2833 | 56.1081 | -66.6916 | -66.7191 | 55.7831 | 53.2654 | 1.6342 | 55.9662 | 55.8563 | -66.7145 | -66.7877 | 0.091553 | 0.064087 | 0.07782 | 112.7884 | 4.4998 | 4.4357 | 0.027466 | 0.068664 | -0.004578 | -0.064086 | 122.5662 | 68.4174 | 68.4219 | -0.17395 | 122.8912 | 122.8409 | 109.2178 | -122.7493 | 122.7493 | 122.6395 | 120.0485 | -122.818
616.8438 | 122.8821 | -66.3986 | 56.3324 | -0.19858 | 0.016273 | 0.33304 | 0.024839 | 0.14123 | 0.11013 | 0.01954 | -0.42621 | 1.4484 | 0.56399 | 0.18276 | 1.7902 | 0.0011829 | 56.1356 | 42.8833 | 38.2095 | -44.7098 | 56.3278 | -66.4307 | -66.4627 | 56.0394 | 53.183 | -1.9775 | 56.2363 | 56.1401 | -66.3391 | -66.4124 | -0.032043 | -0.064087 | -0.004577 | 109.2819 | 21.6888 | 21.7529 | -0.19684 | 0.05951 | -0.013733 | -0.09613 | 122.4381 | 64.4211 | 64.4348 | -0.19226 | 122.7264 | 122.5342 | 104.6082 | -122.7951 | 122.6349 | 122.5388 | 119.5816 | -122.7448
617.8438 | 122.8134 | -67.2775 | 55.3894 | -0.29014 | 0.020545 | 0.21769 | 0.017362 | 0.13269 | 0.014001 | 0.018472 | -0.3194 | 1.5157 | 0.815 | 0.20733 | 2.0968 | 0.012933 | 55.3116 | 48.0194 | 37.2665 | -62.6678 | 55.4489 | -67.2867 | -67.3462 | 55.1559 | 52.0248 | 8.1985 | 55.2063 | 55.1285 | -67.2455 | -67.305 | -0.009155 | -0.068664 | 0.05951 | 115.2969 | 4.6097 | 4.6783 | -0.07782 | 0.032044 | -0.027466 | -0.1831 | 122.4335 | 75.4761 | 75.5035 | -0.26093 | 122.7264 | 122.5891 | 104.5441 | -122.7356 | 122.4838 | 122.406 | 119.3024 | -122.6944
618.8438 | 92.0288 | -38.6307 | 83.6884 | 0.24392 | 0.020545 | 0.20914 | 0.031248 | 0.14123 | 0.048181 | 0.024881 | 0.35199 | 0.21478 | -0.0053139 | 0.17849 | 0.044924 | -0.035133 | 83.7982 | 76.2497 | 60.7864 | -34.0439 | 83.9355 | -38.4979 | -38.5803 | -46.2433 | -46.3028 | -46.3165 | -8.8211 | -8.725 | -38.6215 | -38.7589 | 0.13275 | 0.050354 | 0.24719 | 114.8804 | 4.5868 | 4.5364 | 0.10986 | 0.009155 | -0.12817 | -92.5095 | -7.6126 | -7.6859 | -7.5577 | -92.4133 | 122.5662 | 122.4289 | 99.4171 | -122.2687 | 29.8096 | 29.9057 | -7.6721 | -122.4472
619.8438 | 122.7951 | -40.3656 | 82.338 | -0.32065 | 0.0045241 | 0.23691 | 0.020567 | 0.1423 | 0.0054557 | 0.01954 | -0.10577 | 0.19234 | 0.017117 | 0.17421 | 0.0011309 | -0.0052251 | 82.2189 | 74.4644 | 57.1335 | -36.0031 | 82.3242 | -40.361 | -40.4205 | -40.5945 | -40.6174 | -40.6723 | -8.8211 | -8.7341 | -40.3839 | -40.4526 | 0.004578 | -0.054931 | -0.013733 | 114.83 | 4.3625 | 4.4174 | -0.11902 | -0.01831 | -0.086975 | -91.1591 | -0.22888 | -0.3067 | -0.21973 | -91.0721 | 122.6898 | 122.5845 | 97.4991 | -122.7585 | 31.5445 | 31.6315 | -0.25177 | -122.7905
620.8438 | 122.8592 | -40.0314 | 82.6996 | -0.29014 | 0.012 | 0.23157 | 0.021635 | 0.13376 | 0.014001 | 0.01954 | -0.12103 | 0.18914 | -0.0010409 | 0.17635 | 0.0086079 | -0.014838 | 82.608 | 74.762 | 51.915 | -35.6506 | 82.6538 | -40.0452 | -40.1459 | -40.2878 | -40.3244 | -40.4022 | -8.8303 | -8.7433 | -40.1001 | -40.1871 | -0.013733 | -0.11444 | -0.045776 | 114.7934 | 4.3808 | 4.4952 | -0.091553 | -0.068665 | -0.15564 | -91.5298 | -0.25635 | -0.37079 | -0.21515 | -91.4429 | 122.6852 | 122.6395 | 91.9464 | -122.8455 | 31.2012 | 31.2881 | -0.29297 | -122.8867
621.8438 | 122.9736 | -39.7202 | 82.9605 | -0.16807 | -0.012566 | 0.22944 | 0.0077488 | 0.1391 | 0.0033197 | 0.018472 | -0.2431 | 0.1838 | -0.0053139 | 0.18489 | 0.0054039 | -0.01377 | 82.9285 | 75.0504 | 44.2612 | -35.5957 | 82.988 | -39.7247 | -39.7614 | -39.9307 | -39.8758 | -39.9353 | -8.8303 | -8.7479 | -39.7293 | -39.83 | -0.004577 | -0.041199 | 0.027466 | 114.7705 | 4.1245 | 4.1656 | -0.032043 | -0.009155 | -0.10986 | -91.7908 | -0.21057 | -0.21515 | -0.10529 | -91.7084 | 122.7081 | 122.6486 | 83.9813 | -122.7219 | 30.8899 | 30.9723 | -0.15564 | -122.7905
622.8438 | 123.0377 | -39.505 | 83.1757 | -0.21384 | 0.012 | 0.23051 | 0.014158 | 0.13803 | 0.014001 | 0.017404 | -0.22784 | 0.19021 | 2.7137e-05 | 0.17635 | 6.2882e-05 | -0.02552 | 83.139 | 75.4395 | 42.8925 | -34.8404 | 83.1482 | -39.5782 | -39.6332 | -39.7247 | -39.7293 | -39.7888 | -8.8394 | -8.7479 | -39.5691 | -39.6561 | -0.073242 | -0.12817 | -0.027466 | 114.9445 | 4.6646 | 4.7928 | -0.036621 | -0.064087 | -0.15106 | -92.0151 | -0.21973 | -0.28381 | -0.13275 | -91.9235 | 122.6532 | 122.644 | 82.3975 | -122.8088 | 30.6656 | 30.7571 | -0.2243 | -122.8317
623.8438 | 122.937 | -39.5325 | 83.2397 | -0.061255 | 0.035499 | 0.23157 | 0.034452 | 0.15085 | 0.055657 | 0.027017 | -0.18207 | 0.20516 | -0.0063819 | 0.17849 | 0.01288 | -0.021247 | 83.2718 | 75.3479 | 34.6893 | -34.4147 | 83.3633 | -39.4455 | -39.5142 | -39.7156 | -39.7705 | -39.8621 | -8.8348 | -8.7433 | -39.5691 | -39.6698 | 0.086975 | 0.018311 | 0.1236 | 114.8804 | 5.1178 | 5.0995 | 0.032044 | -0.036621 | -0.13733 | -92.0746 | -0.1831 | -0.32959 | -0.19226 | -91.983 | 122.8958 | 122.8043 | 74.2218 | -122.7539 | 30.6976 | 30.7892 | -0.23804 | -122.9095
624.8438 | 123.0057 | -40.2649 | 82.4753 | -0.18333 | -0.0029529 | 0.22837 | 0.0098848 | 0.15085 | 0.012933 | 0.029153 | -0.33466 | 0.19341 | 0.0096401 | 0.18169 | 0.0043349 | -0.018043 | 82.2235 | 74.2905 | 30.2673 | -34.5886 | 82.4432 | -40.2924 | -40.3519 | -40.4663 | -40.4663 | -40.5487 | -8.8348 | -8.7479 | -40.3198 | -40.4022 | -0.027465 | -0.086975 | -0.032044 | 114.5554 | 5.6763 | 5.7632 | -0.25177 | -0.054931 | -0.13733 | -91.3101 | -0.20142 | -0.28381 | -0.14648 | -91.2231 | 122.7081 | 122.4884 | 70.5322 | -122.8271 | 31.4301 | 31.517 | -0.20142 | -122.8775
625.8438 | 123.024 | -39.7247 | 82.9834 | -0.25962 | -0.0029529 | 0.2476 | 0.016294 | 0.13696 | 0.014001 | 0.020609 | -0.13629 | 0.18914 | -0.015995 | 0.17528 | 0.0096759 | -0.0062931 | 82.9926 | 75.3616 | 27.594 | -34.4879 | 82.9971 | -39.7659 | -39.8209 | -39.9261 | -39.8117 | -40.2283 | -8.8303 | -8.7433 | -39.8117 | -39.9261 | -0.041199 | -0.096131 | 0.013733 | 115.0864 | 5.2368 | 5.3329 | 0.009156 | -0.086976 | -0.20142 | -91.8137 | -0.20142 | -0.50354 | -0.30212 | -91.7267 | 122.7219 | 122.7173 | 67.3187 | -122.8043 | 30.8945 | 30.9814 | -0.086976 | -122.9095
626.8438 | 123.0423 | -39.0884 | 83.6288 | -0.25962 | -0.0050889 | 0.23478 | 0.01309 | 0.1391 | 0.010797 | 0.030222 | -0.25836 | 0.19448 | -0.0031779 | 0.18703 | 0.0075399 | -0.021247 | 83.6014 | 76.2177 | 29.512 | -33.9569 | 83.5648 | -39.1708 | -39.2578 | -39.2578 | -39.2715 | -39.3494 | -8.844 | -8.7479 | -39.1617 | -39.2349 | -0.082397 | -0.16937 | -0.064087 | 115.3061 | 5.1315 | 5.3009 | -0.027466 | -0.073242 | -0.14648 | -92.4728 | -0.16937 | -0.26093 | -0.11444 | -92.3767 | 122.6532 | 122.6898 | 68.6005 | -122.8867 | 30.2444 | 30.3406 | -0.18311 | -122.8638
627.8438 | 123.0606 | -38.6856 | 84.0546 | -0.045996 | 0.0023871 | 0.23905 | 0.015226 | 0.14657 | 0.014001 | 0.021677 | -0.25836 | 0.18594 | -0.014927 | 0.18596 | 0.021425 | -0.0084301 | 84.0775 | 76.9318 | 28.3813 | -33.9249 | 84.0912 | -38.6856 | -38.8 | -38.8641 | -38.9053 | -39.0106 | -8.8348 | -8.7433 | -38.7726 | -38.887 | 0 | -0.11444 | 0.036622 | 115.6174 | 4.7607 | 4.8752 | 0.022889 | -0.086975 | -0.20142 | -92.8894 | -0.17853 | -0.32501 | -0.1236 | -92.7979 | 122.7768 | 122.7631 | 67.067 | -122.8546 | 29.8508 | 29.9423 | -0.21973 | -122.9416
628.8438 | 122.9004 | -39.1205 | 83.6792 | 0.24392 | 0.047248 | 0.23051 | 0.03552 | 0.1423 | 0.064202 | 0.032358 | -0.10577 | 0.20623 | 0.016048 | 0.18489 | 0.017153 | -0.034064 | 83.6334 | 76.2039 | 34.053 | -33.728 | 83.7158 | -39.1251 | -39.1937 | -39.3677 | -39.4501 | -39.5142 | -8.8303 | -8.7479 | -39.1983 | -39.2715 | -0.004578 | -0.073243 | 0.036621 | 115.3244 | 5.3925 | 5.4657 | -0.045776 | -0.07782 | -0.15106 | -92.5095 | -0.24719 | -0.39368 | -0.24261 | -92.4271 | 122.8363 | 122.7539 | 73.1735 | -122.8729 | 30.2902 | 30.3726 | -0.32959 | -122.9507
629.8438 | 123.0103 | -38.8046 | 83.9447 | 0.19814 | 0.013069 | 0.24653 | 0.0077488 | 0.14017 | 0.0033197 | 0.016336 | 0.10785 | 0.19982 | -0.010654 | 0.18917 | 0.0064719 | -0.010566 | 83.8623 | 76.6342 | 30.6244 | -34.1263 | 83.9676 | -38.8458 | -38.9008 | -39.0244 | -39.0976 | -39.1434 | -8.8348 | -8.7433 | -38.8733 | -38.9877 | -0.041199 | -0.096131 | 0.022888 | 115.4388 | 4.6783 | 4.7745 | -0.082397 | -0.068665 | -0.18311 | -92.7795 | -0.21973 | -0.33875 | -0.15564 | -92.688 | 122.7722 | 122.6669 | 69.429 | -122.8455 | 29.9698 | 30.0613 | -0.29297 | -122.9324
630.8438 | 123.0972 | -37.7289 | 85.0342 | -0.12229 | 0.0013191 | 0.23905 | 0.010954 | 0.15191 | 0.0075917 | 0.0099268 | -0.16681 | 0.19555 | -0.0021099 | 0.18383 | 0.010744 | -0.01377 | 85.0159 | 77.9388 | 31.311 | -32.3227 | 85.0571 | -37.7289 | -37.8067 | -37.8616 | -37.912 | -37.9807 | -8.8394 | -8.7433 | -37.7792 | -37.8708 | 0 | -0.07782 | 0.022888 | 115.6677 | 5.4062 | 5.484 | -0.018311 | -0.050354 | -0.14191 | -93.8736 | -0.13275 | -0.25177 | -0.10986 | -93.7775 | 122.7859 | 122.7448 | 69.0399 | -122.8409 | 28.8895 | 28.9856 | -0.18311 | -122.905
631.8438 | 123.0606 | -36.9415 | 85.7849 | 0.060816 | -0.00081686 | 0.41849 | 0.017362 | 0.13162 | 0.21481 | 0.030222 | -0.029479 | 0.19341 | -0.0021099 | 0.17528 | 0.010744 | -0.023383 | 85.7529 | 38.6627 | 26.4267 | 0.99335 | 85.8398 | -36.9415 | -36.9919 | -37.1246 | -37.1567 | -37.2391 | -8.8303 | -8.7479 | -37.0056 | -37.0743 | 0 | -0.050354 | 0.054932 | 75.6042 | 37.9349 | 37.9852 | -0.032043 | -0.064087 | -0.13275 | -94.6152 | -0.18311 | -0.29755 | -0.16479 | -94.5328 | 122.7814 | 122.6944 | 63.3682 | -122.7768 | 28.1113 | 28.1937 | -0.21515 | -122.8592
632.8438 | 123.0881 | -32.1991 | 90.5869 | 0.16763 | 0.016273 | 0.17924 | 0.019498 | 0.080351 | 0.035363 | 0.0045868 | -0.029479 | 0.19769 | 0.0085721 | 0.18489 | 0.011812 | -0.014838 | 90.5548 | -14.2319 | 19.812 | -24.1058 | 90.5914 | -32.2403 | -32.3135 | -32.4051 | -32.5012 | -32.5287 | -8.8394 | -8.7433 | -32.2952 | -32.3959 | -0.041198 | -0.11444 | 0.004578 | 17.9672 | 8.0933 | 8.2077 | -0.032043 | -0.09613 | -0.19684 | -99.4263 | -0.20599 | -0.32959 | -0.13275 | -99.3301 | 122.7905 | 122.7539 | 52.0111 | -122.9004 | 23.3597 | 23.4558 | -0.30212 | -122.9828
633.8438 | 122.9599 | -36.9781 | 85.7849 | -0.18333 | 0.0098641 | 0.37363 | 0.025907 | 0.1423 | 0.19985 | 0.024881 | -0.44147 | 0.19982 | 0.010708 | 0.18169 | 0.025698 | -0.031928 | 85.6842 | 46.0007 | 28.2806 | 9.256 | 85.8078 | -37.0514 | -37.1246 | -37.2528 | -37.2711 | -37.3627 | -8.8394 | -8.7479 | -37.0697 | -37.1887 | -0.073243 | -0.14648 | 0.022888 | 82.9788 | 46.2341 | 46.3806 | -0.10071 | -0.091553 | -0.21057 | -94.6243 | -0.27466 | -0.38452 | -0.17395 | -94.5328 | 122.7859 | 122.6624 | 65.2588 | -122.9095 | 28.1387 | 28.2303 | -0.29297 | -122.9736
634.8438 | 123.0469 | -37.3352 | 85.3958 | 0.27444 | 0.0034561 | 0.47083 | 0.0045448 | 0.14871 | 0.23083 | 0.020609 | 0.74872 | 0.19234 | 0.0075041 | 0.18169 | 0.016085 | -0.010566 | 85.2722 | 70.99 | 24.733 | 3.9551 | 85.4187 | -37.3444 | -37.4039 | -37.5366 | -37.6099 | -37.6465 | -8.8394 | -8.7433 | -37.4039 | -37.5092 | -0.009155 | -0.068665 | 0.022888 | 108.3252 | 41.2903 | 41.3589 | -0.1236 | -0.068665 | -0.17395 | -94.2352 | -0.20142 | -0.31128 | -0.13733 | -94.1391 | 122.7539 | 122.6074 | 62.0682 | -122.7997 | 28.4958 | 28.5919 | -0.27466 | -122.905
635.8438 | 123.0011 | -37.8387 | 84.9014 | 0.38125 | -0.0040209 | 0.43238 | 0.021635 | 0.15191 | 0.20626 | 0.032358 | 0.24518 | 0.19448 | 0.01498 | 0.18703 | 0.0086079 | -0.014838 | 84.668 | 73.1461 | 22.0688 | 13.7924 | 84.8007 | -37.9486 | -38.0035 | -38.0676 | -38.0539 | -38.1729 | -8.8394 | -8.7479 | -37.8845 | -38.0035 | -0.10986 | -0.16479 | -0.10071 | 110.9848 | 51.6312 | 51.796 | -0.23346 | -0.045776 | -0.16479 | -93.7408 | -0.22888 | -0.33417 | -0.16937 | -93.6493 | 122.6395 | 122.5067 | 59.9075 | -122.905 | 28.9993 | 29.0909 | -0.21515 | -122.905
636.8438 | 123.0286 | -34.9319 | 87.8082 | 0.44228 | 0.0066601 | 0.24546 | -0.0018642 | 0.14444 | 0.049249 | 0.024881 | 0.5351 | 0.19555 | -0.021336 | 0.17635 | 0.011812 | -0.0094981 | 87.767 | 83.844 | 23.8129 | -32.6248 | 87.8265 | -34.9548 | -35.0235 | -35.1608 | -35.2386 | -35.3027 | -8.8303 | -8.7479 | -34.996 | -35.1105 | -0.022888 | -0.091553 | 0.01831 | 118.7759 | 2.3071 | 2.3987 | -0.041199 | -0.064087 | -0.17853 | -96.6385 | -0.22888 | -0.37079 | -0.19226 | -96.5561 | 122.7585 | 122.699 | 58.7448 | -122.8317 | 26.1017 | 26.1841 | -0.3067 | -122.9187
637.8438 | 123.0286 | -36.3373 | 86.412 | 0.13711 | -0.0072259 | 0.4452 | 0.0077488 | 0.14978 | 0.17208 | 0.020609 | 0.13837 | 0.19448 | -0.0074499 | 0.18276 | 0.0064719 | -0.019111 | 86.348 | 76.3779 | 25.8911 | -0.99792 | 86.4029 | -36.3922 | -36.4243 | -36.525 | -36.6028 | -36.6531 | -8.8394 | -8.7524 | -36.3831 | -36.4975 | -0.054932 | -0.086975 | -0.009155 | 112.7151 | 35.3394 | 35.4263 | -0.064087 | -0.045777 | -0.16022 | -95.2515 | -0.18768 | -0.31586 | -0.15564 | -95.1645 | 122.7402 | 122.6852 | 62.2284 | -122.8363 | 27.4979 | 27.5848 | -0.2655 | -122.9095
638.8438 | 123.0515 | -34.52 | 88.2156 | 0.18289 | 0.019477 | 0.23585 | 0.017362 | 0.13269 | 0.037499 | 0.023813 | -0.79242 | 0.20089 | 0.0085721 | 0.18489 | 0.0075399 | -0.014838 | 88.2019 | 84.8236 | 22.6181 | -27.2415 | 88.2385 | -34.5428 | -34.6252 | -34.7488 | -34.7992 | -34.8679 | -8.844 | -8.7524 | -34.6344 | -34.7031 | -0.022889 | -0.10529 | 0.022888 | 119.3436 | 7.2784 | 7.3837 | -0.013733 | -0.11444 | -0.18311 | -97.0596 | -0.22888 | -0.3479 | -0.1648 | -96.9681 | 122.7585 | 122.7219 | 57.1381 | -122.8409 | 25.676 | 25.7675 | -0.27924 | -122.9187
639.8438 | 123.024 | -34.7122 | 88.0692 | 0.16763 | 0.082496 | 0.16749 | 0.017362 | 0.13055 | 0.041772 | 0.024881 | 0.046815 | 0.18166 | 0.0075041 | 0.1881 | 0.0054039 | -0.03086 | 87.9913 | 87.3276 | 27.3605 | -27.1317 | 88.1012 | -34.7763 | -34.8267 | -34.9503 | -34.9731 | -35.0235 | -8.8348 | -8.7433 | -34.7488 | -34.8221 | -0.064087 | -0.11444 | 0.032043 | 122.0398 | 7.5806 | 7.695 | -0.07782 | -0.036621 | -0.10986 | -96.904 | -0.23804 | -0.31128 | -0.20142 | -96.8124 | 122.8134 | 122.7036 | 62.0728 | -122.8958 | 25.8774 | 25.9689 | -0.26093 | -122.8912
640.8438 | 123.0377 | -36.7218 | 86.0641 | 0.22866 | 0.12308 | 0.13758 | 0.017362 | 0.15619 | 0.049249 | 0.027017 | 0.10785 | 0.19982 | -0.0074499 | 0.18276 | 0.013948 | -0.027656 | 85.9406 | 86.0275 | 32.7026 | -29.837 | 86.0092 | -36.7905 | -36.8088 | -36.882 | -36.9278 | -37.001 | -8.844 | -8.7524 | -36.7447 | -36.8591 | -0.068664 | -0.086975 | -0.054932 | 122.7493 | 6.8848 | 6.9717 | -0.1236 | -0.022888 | -0.13733 | -94.9081 | -0.16022 | -0.27924 | -0.14191 | -94.8166 | 122.731 | 122.6624 | 69.4244 | -122.8729 | 27.8778 | 27.9694 | -0.20599 | -122.9233
641.8438 | 123.0103 | -35.2295 | 87.6526 | 0.18289 | 0.12095 | 0.15146 | 0.021635 | 0.14017 | 0.052453 | 0.035562 | 0.092591 | 0.19448 | 0.0085721 | 0.18489 | 0.0064719 | -0.014838 | 87.6572 | 87.7762 | 24.8657 | -30.8212 | 87.7625 | -35.0647 | -35.1425 | -35.5362 | -36.3235 | -36.5753 | -8.8394 | -8.7662 | -35.6003 | -35.5774 | 0.16479 | 0.086975 | 0.10986 | 123.0057 | 4.4083 | 4.3213 | 0.004578 | -0.37079 | -0.3479 | -96.492 | -0.3067 | -1.3458 | -0.99792 | -96.4188 | 122.9919 | 122.8867 | 60.0952 | -122.7951 | 26.3901 | 26.4633 | -1.0941 | -123.23
642.8438 | 122.9874 | -39.8804 | 82.8323 | 0.51858 | 0.6486 | 0.0083374 | 0.44034 | 0.26407 | 0.73711 | 0.033426 | 0.26044 | 0.20196 | -0.0031779 | 0.16994 | 0.01288 | -0.023383 | 78.3737 | 82.7362 | 33.0414 | 77.9572 | 82.7499 | -39.8712 | -39.9582 | -40.0681 | -40.1642 | -40.2649 | -8.8394 | -8.7479 | -39.9948 | -40.0818 | 0.009155 | -0.07782 | -0.082397 | 122.6166 | 117.8375 | 117.9153 | -4.4586 | -0.11444 | -0.20142 | -91.6718 | -0.18768 | -0.38452 | -0.18311 | -91.5802 | 122.6303 | 118.2541 | 72.9218 | -122.7905 | 31.041 | 31.1325 | -0.28381 | -122.9141
643.8438 | 123.0835 | -40.361 | 82.3242 | 0.44228 | 0.72657 | 0.014745 | 0.35061 | 0.24057 | 0.73818 | 0.043039 | 0.30621 | 0.19875 | -0.0010409 | 0.18383 | 0.0086079 | -0.018043 | 77.9617 | 82.3151 | 30.5786 | 78.1036 | 82.2784 | -40.329 | -40.3519 | -40.5487 | -40.6357 | -40.6815 | -8.8348 | -8.7479 | -40.448 | -40.5167 | 0.032044 | 0.009155 | -0.045777 | 122.6761 | 118.4647 | 118.4555 | -4.3625 | -0.086975 | -0.15564 | -91.1591 | -0.18768 | -0.32043 | -0.16479 | -91.0721 | 122.6395 | 118.3228 | 70.9396 | -122.6761 | 31.5262 | 31.6132 | -0.27466 | -122.8409
644.8438 | 122.9828 | -40.1779 | 82.4524 | 0.10659 | 0.79707 | 0.014745 | 0.29721 | 0.24805 | 0.72109 | 0.049448 | 0.33673 | 0.19128 | -0.019199 | 0.16994 | 0.013948 | -0.028724 | 77.71 | 82.4066 | 48.0194 | 78.5797 | 82.4387 | -40.1917 | -40.242 | -40.4022 | -40.4251 | -40.4984 | -8.8531 | -8.7524 | -40.2786 | -40.3656 | -0.013733 | -0.064087 | -0.013733 | 122.5845 | 118.7576 | 118.8217 | -4.7424 | -0.10071 | -0.18768 | -91.3055 | -0.22431 | -0.32043 | -0.13275 | -91.2048 | 122.6166 | 117.8879 | 88.1973 | -122.6944 | 31.3248 | 31.4255 | -0.24719 | -122.818
645.8438 | 122.9736 | -40.4709 | 82.1915 | 0.15237 | 0.83445 | 0.0051324 | 0.26944 | 0.24911 | 0.72964 | 0.054788 | 0.046815 | 0.1838 | 0.010708 | 0.16994 | 0.013948 | -0.020179 | 77.2751 | 82.196 | 56.9092 | 78.4561 | 82.1411 | -40.416 | -40.4938 | -40.7089 | -40.741 | -40.7913 | -8.8394 | -8.7479 | -40.5533 | -40.6311 | 0.054931 | -0.022888 | -0.050354 | 122.6669 | 118.927 | 118.9499 | -4.9164 | -0.082398 | -0.16022 | -91.0309 | -0.23804 | -0.32044 | -0.16022 | -90.9393 | 122.612 | 117.746 | 97.3801 | -122.6852 | 31.6315 | 31.723 | -0.27008 | -122.8226
646.8438 | 122.8958 | -40.9973 | 81.6559 | 0.12185 | 0.99039 | 0.0072694 | 0.28866 | 0.43497 | 0.72537 | 0.057993 | 0.10785 | 0.19662 | -0.017063 | 0.16674 | 0.013948 | -0.038337 | 76.7303 | 81.6605 | 65.7715 | 78.0853 | 81.6742 | -40.7089 | -40.9286 | -41.2445 | -41.304 | -41.3177 | -8.8394 | -8.7524 | -41.0706 | -41.1621 | 0.28839 | 0.068664 | 0.01831 | 122.6578 | 119.0826 | 119.014 | -4.9255 | -0.073243 | -0.16479 | -90.4953 | -0.24719 | -0.32043 | -0.15564 | -90.4083 | 122.6715 | 117.7277 | 106.7688 | -122.5845 | 32.1579 | 32.2449 | -0.3067 | -122.818
647.8438 | 122.9691 | -40.8829 | 81.7337 | 0.16763 | 0.85688 | 0.016882 | 0.22992 | 0.24377 | 0.7275 | 0.055856 | 0.046815 | 0.19662 | -0.0031779 | 0.17101 | 0.018221 | -0.016975 | 76.8631 | 81.7657 | 67.3691 | 78.2318 | 81.7474 | -40.8325 | -40.8737 | -41.0477 | -41.1163 | -41.1804 | -8.8394 | -8.757 | -40.9103 | -41.0385 | 0.050354 | 0.009156 | 0.013733 | 122.6486 | 119.1147 | 119.1055 | -4.8706 | -0.027465 | -0.15564 | -90.5731 | -0.16479 | -0.29755 | -0.14191 | -90.4907 | 122.6303 | 117.746 | 108.252 | -122.6074 | 32.0435 | 32.1259 | -0.23346 | -122.7722
648.8438 | 122.9141 | -37.1658 | 85.4919 | 0.2134 | 0.16367 | 0.17176 | 0.025907 | 0.17114 | 0.06527 | 0.045175 | 0.0010378 | 0.19448 | -0.0095859 | 0.17742 | 0.015017 | -0.03086 | 85.3683 | 85.4599 | 78.8635 | -36.4059 | 85.4553 | -37.2437 | -37.2711 | -37.4084 | -37.5092 | -37.5778 | -8.844 | -8.7616 | -37.2894 | -37.3581 | -0.077819 | -0.10529 | -0.036621 | 122.6257 | 0.75989 | 0.86517 | -0.1236 | -0.1236 | -0.19226 | -94.3359 | -0.24261 | -0.41199 | -0.21973 | -94.2535 | 122.6212 | 122.5342 | 116.0294 | -122.7631 | 28.3218 | 28.4042 | -0.34332 | -122.85
649.8438 | 122.9141 | -37.8159 | 84.8099 | 0.45754 | 0.8697 | 0.0094054 | 0.26837 | 0.25979 | 0.74139 | 0.10392 | 0.35199 | 0.19128 | -0.018131 | 0.1881 | 0.0032669 | -0.012702 | 79.1336 | 84.8282 | -33.1879 | 82.5073 | 84.7229 | -37.825 | -37.8571 | -38.0035 | -38.0859 | -38.1363 | -8.8348 | -8.757 | -37.8799 | -38.0035 | -0.009155 | -0.041199 | -0.086975 | 122.644 | 120.3232 | 120.3644 | -5.6763 | -0.064087 | -0.18768 | -93.6447 | -0.18768 | -0.32043 | -0.13275 | -93.5669 | 122.5388 | 116.9495 | 4.628 | -122.6669 | 28.981 | 29.0588 | -0.27008 | -122.8134
650.8438 | 123.0194 | -37.8845 | 84.7504 | 0.30496 | 0.91883 | -0.0055486 | 0.54822 | 0.2865 | 0.74566 | 0.29832 | 0.18414 | 0.19769 | -0.0031779 | 0.17742 | 0.019289 | -0.022315 | 79.2755 | 84.6863 | -34.1904 | 83.4 | 84.6542 | -37.7792 | -37.8479 | -38.0859 | -38.1683 | -38.2278 | -8.8486 | -8.7524 | -37.9486 | -38.0493 | 0.10529 | 0.036621 | -0.09613 | 122.5708 | 121.2845 | 121.2479 | -5.4749 | -0.064087 | -0.16479 | -93.5989 | -0.20142 | -0.34332 | -0.17853 | -93.5028 | 122.5388 | 117.16 | 3.6942 | -122.5983 | 29.0359 | 29.1321 | -0.28381 | -122.7997
651.8438 | 122.8683 | -37.7197 | 84.8236 | 0.076074 | 0.90601 | 0.0083374 | 0.74688 | 0.28543 | 0.751 | 0.59846 | -0.029479 | 0.18914 | -0.0021099 | 0.1881 | 0.02463 | -0.019111 | 79.1199 | 84.8648 | -34.7122 | 84.2651 | 84.8053 | -37.619 | -37.6648 | -37.9074 | -37.9944 | -38.0219 | -8.844 | -8.757 | -37.8159 | -37.9028 | 0.10071 | 0.054932 | -0.01831 | 122.5845 | 121.9849 | 121.9299 | -5.7037 | -0.09613 | -0.1831 | -93.6676 | -0.18768 | -0.30212 | -0.11902 | -93.5806 | 122.525 | 116.8396 | 3.0075 | -122.4884 | 28.8757 | 28.9627 | -0.27466 | -122.7264
652.8438 | 122.8088 | -58.992 | 63.6612 | 0.39651 | 0.95301 | -0.0023436 | 1.25 | 0.32281 | 0.74352 | 1.1069 | -0.16681 | 0.187 | -0.0021099 | 0.17635 | 0.017153 | -0.010566 | 56.3599 | 61.5509 | -56.0349 | 62.4023 | 62.384 | -59.9716 | -60.1364 | -60.0311 | -59.4131 | -59.5871 | -8.8531 | -8.757 | -59.61 | -59.6878 | -0.97961 | -1.1444 | -1.2772 | 120.5429 | 121.3943 | 122.5388 | -7.3013 | -0.61798 | -0.6958 | -72.5143 | -1.0391 | -0.59509 | 0.10071 | -72.4182 | 121.376 | 115.3519 | 2.9572 | -123.7976 | 50.1389 | 50.235 | -0.42114 | -123.349
653.8438 | 122.7631 | -2.3621 | 120.2637 | 0.030298 | 1.6195 | 0.0094054 | 0.46704 | 0.96475 | 0.73925 | 0.31114 | 0.36725 | 0.19128 | -0.0085179 | 0.18276 | 0.0064719 | -0.027656 | 41.6565 | 120.0531 | -1.1948 | 119.8334 | 120.163 | -2.037 | -2.1835 | -2.33 | -2.2156 | -2.3987 | -2.4353 | -2.4811 | -2.504 | -2.5406 | 0.32501 | 0.17853 | -0.10071 | 122.4152 | 122.1954 | 122.0169 | -78.6072 | -0.14191 | -0.17853 | -122.699 | 0.032044 | -0.036621 | 0.14191 | -122.7448 | 122.525 | 44.0186 | 1.1673 | -122.4472 | -0.073242 | -0.11902 | 0.14649 | -122.8043
654.8438 | 122.6898 | -24.3393 | 97.9019 | 0.24392 | 0.20106 | 3.4797 | 0.040861 | 0.17862 | 0.13683 | 3.272 | 0.22992 | 0.18273 | -0.0042459 | 0.16994 | 0.0086079 | -0.023383 | 86.9476 | 80.0812 | -9.8373 | -5.983 | 104.7821 | -17.0792 | -17.1112 | -24.7696 | -24.4492 | -24.3576 | -8.8348 | -8.757 | -23.6664 | -24.1928 | 7.2601 | 7.2281 | 6.8802 | 104.4205 | 18.3563 | 11.1282 | -10.9543 | 0.67291 | 0.14648 | -106.7368 | -0.4303 | -0.018311 | -0.16479 | -106.6589 | 129.1214 | 111.2869 | 14.502 | -115.0131 | 15.5045 | 15.5823 | -0.10986 | -122.0947
655.8438 | 122.8226 | -26.5503 | 96.0663 | 0.42703 | 0.12843 | 0.1269 | 0.047269 | 0.12735 | 0.010797 | 0.047311 | 0.64191 | 0.19128 | -0.0031779 | 0.18169 | 0.031038 | -0.021247 | 0.07782 | 0.09613 | 0.032043 | -0.013733 | 0.13733 | -0.073242 | -0.15106 | -26.7014 | -26.7883 | -26.8433 | -8.8303 | -8.757 | -26.5594 | -26.6602 | 26.4771 | 26.3992 | -95.929 | 26.6464 | 26.5366 | 0.13733 | -95.9885 | -0.009155 | -0.10986 | -104.8965 | -0.15106 | -0.29297 | -0.18311 | -104.8233 | 26.6876 | 26.6281 | 26.5823 | -96.2173 | 17.72 | 17.7933 | -0.23804 | -122.7264
656.8438 | 122.8775 | -26.4908 | 96.167 | 0.18289 | 0.14445 | 0.14506 | 0.056883 | 0.10705 | 0.018273 | 0.043039 | 0.50458 | 0.19234 | -0.0031779 | 0.18169 | 0.021425 | -0.028724 | 0.10071 | 0.09613 | 0.032043 | 0.036621 | 0.12817 | 0.018311 | -0.10529 | -26.651 | -26.7151 | -26.7883 | -8.8394 | -8.757 | -26.5228 | -26.6006 | 26.5091 | 26.3855 | -96.0388 | 26.5869 | 26.5274 | 0.14191 | -96.0663 | -0.032043 | -0.10986 | -105.0064 | -0.16022 | -0.29755 | -0.18768 | -104.924 | 26.619 | 26.5915 | 26.5228 | -96.2723 | 17.6514 | 17.7338 | -0.2243 | -122.7676
657.8438 | 122.9187 | -26.5594 | 96.1121 | 0.15237 | 0.12629 | 0.14399 | 0.055814 | 0.12201 | 0.0033197 | 0.040903 | 0.031556 | 0.18487 | -0.0053139 | 0.19237 | 0.01288 | -0.021247 | 0.032043 | 0.064087 | -0.009155 | 0.041199 | 0.14648 | 0.004578 | -0.11444 | -26.7014 | -26.7242 | -26.8204 | -8.8394 | -8.7616 | -26.564 | -26.6418 | 26.564 | 26.445 | -95.9656 | 26.6235 | 26.6006 | 0.15564 | -96.08 | -0.004578 | -0.082398 | -104.9515 | -0.14191 | -0.26093 | -0.17853 | -104.8737 | 26.7059 | 26.5915 | 26.5503 | -96.2265 | 17.72 | 17.7979 | -0.1648 | -122.7539
658.8438 | 122.9233 | -26.3947 | 96.2631 | 0.2134 | 0.12629 | 0.15681 | 0.049406 | 0.12308 | 0.0086597 | 0.044107 | 0.0010378 | 0.19021 | -0.0021099 | 0.18169 | 0.0064719 | -0.01377 | 0.036621 | 0.059509 | -0.009155 | 0.032043 | 0.15106 | 0 | -0.12817 | -26.5961 | -26.6418 | -26.7014 | -8.844 | -8.7524 | -26.4679 | -26.5366 | 26.3947 | 26.2665 | -96.1121 | 26.4542 | 26.4267 | 0.16022 | -96.2265 | -0.073243 | -0.14191 | -105.1071 | -0.20142 | -0.3067 | -0.16479 | -105.0156 | 26.5457 | 26.4313 | 26.3855 | -96.3913 | 17.5507 | 17.6422 | -0.24719 | -122.7997
659.8438 | 122.905 | -26.3947 | 96.3181 | 0.30496 | 0.12308 | 0.15253 | 0.051542 | 0.12628 | 0.0086597 | 0.043039 | -0.059997 | 0.19662 | -0.0063819 | 0.1881 | 0.015017 | -0.023383 | 0.036621 | 0.054932 | -0.009155 | 0.050354 | 0.12817 | 0.013733 | -0.086975 | -26.564 | -26.6144 | -26.6647 | -8.844 | -8.7524 | -26.3947 | -26.5091 | 26.4084 | 26.3077 | -96.1899 | 26.4496 | 26.445 | 0.13733 | -96.2814 | 0 | -0.11444 | -105.162 | -0.16937 | -0.27008 | -0.15564 | -105.0705 | 26.5228 | 26.4313 | 26.3855 | -96.405 | 17.5507 | 17.6422 | -0.21973 | -122.8271
660.8438 | 122.9462 | -26.2527 | 96.4508 | 0.30496 | 0.14658 | 0.15146 | 0.0697 | 0.1156 | 0.0054557 | 0.037698 | -0.10577 | 0.19341 | -0.0053139 | 0.18169 | 0.0096759 | -0.015907 | 0.036621 | 0.045776 | 0 | 0.036621 | 0.14191 | 0.013733 | -0.12817 | -26.4221 | -26.4816 | -26.5594 | -8.844 | -8.757 | -26.3077 | -26.3947 | 26.2665 | 26.1246 | -96.3089 | 26.2985 | 26.2894 | 0.1648 | -96.4142 | -0.054931 | -0.14191 | -105.2948 | -0.16937 | -0.3067 | -0.16479 | -105.2078 | 26.3947 | 26.2894 | 26.2527 | -96.579 | 17.4088 | 17.4957 | -0.22888 | -122.8455
661.8438 | 122.937 | -26.3031 | 96.4142 | 0.38125 | 0.12415 | 0.13972 | 0.070768 | 0.11987 | 0.0075917 | 0.034494 | -0.059997 | 0.19341 | -0.012791 | 0.19451 | 0.017153 | -0.021247 | 0.036621 | 0.050354 | -0.004578 | 0.022888 | 0.13733 | 0.009155 | -0.12817 | -26.4771 | -26.5182 | -26.5869 | -8.844 | -8.757 | -26.3306 | -26.4175 | 26.3123 | 26.1749 | -96.2769 | 26.3535 | 26.326 | 0.15106 | -96.3776 | -0.027465 | -0.11444 | -105.2582 | -0.17395 | -0.28381 | -0.16937 | -105.1712 | 26.4404 | 26.3397 | 26.2985 | -96.5424 | 17.4591 | 17.5461 | -0.21515 | -122.8317
662.8438 | 122.9736 | -25.9964 | 96.73 | 0.4728 | 0.14231 | 0.14399 | 0.049406 | 0.11133 | 0.021478 | 0.05372 | -0.21259 | 0.19769 | -0.0031779 | 0.17528 | 0.018221 | -0.024451 | -0.13275 | 0.004578 | 0.027466 | 0.059509 | 0.086975 | -0.013733 | -0.13733 | -26.1383 | -26.1887 | -26.2848 | -8.844 | -8.7524 | -26.0422 | -26.1291 | 25.9827 | 25.8591 | -96.6431 | 26.001 | 26.0559 | 0.19684 | -96.8628 | -0.045776 | -0.13275 | -105.574 | -0.14191 | -0.28839 | -0.15564 | -105.4825 | 26.0834 | 25.8636 | 26.0239 | -96.8674 | 17.1524 | 17.244 | -0.19226 | -122.8592
663.8438 | 122.9691 | -25.7584 | 96.9635 | 0.50332 | 0.14765 | 0.14719 | 0.0697 | 0.12521 | 0.017205 | 0.050516 | 0.15363 | 0.19448 | 0.0021631 | 0.19024 | 0.018221 | -0.027656 | 0.091553 | 0.10986 | 0.045776 | 0.068665 | 0.10986 | 0.018311 | -0.10986 | -25.8316 | -25.8545 | -25.9506 | -8.844 | -8.757 | -25.7767 | -25.8682 | 25.7767 | 25.6485 | -96.8536 | 25.8682 | 25.827 | 0.17853 | -96.8719 | -0.01831 | -0.10986 | -105.8075 | -0.073242 | -0.19226 | -0.082398 | -105.7205 | 25.8682 | 25.8499 | 25.8041 | -97.0734 | 16.9144 | 17.0013 | -0.09613 | -122.8317
664.8438 | 122.9874 | -25.502 | 97.229 | 0.41177 | 0.11988 | 0.14826 | 0.060087 | 0.13482 | 0.0065237 | 0.041971 | -0.090514 | 0.19128 | -0.0063819 | 0.17208 | 0.0043349 | -0.01377 | 0.036621 | 0.068665 | -0.009155 | 0.018311 | 0.13275 | 0.022888 | -0.12817 | -25.676 | -25.6805 | -25.7904 | -8.8394 | -8.7524 | -25.5432 | -25.6119 | 25.5249 | 25.3738 | -97.0963 | 25.5707 | 25.5203 | 0.14649 | -97.1924 | -0.041199 | -0.10986 | -106.0684 | -0.17395 | -0.28839 | -0.17853 | -105.9814 | 25.6348 | 25.5386 | 25.4929 | -97.3572 | 16.6626 | 16.7496 | -0.17853 | -122.8409
665.8438 | 122.9691 | -25.5478 | 97.2107 | 0.36599 | 0.12736 | 0.14078 | 0.059019 | 0.11774 | 0.0086597 | 0.04838 | 0.077332 | 0.19021 | -0.011723 | 0.18383 | 0.0075399 | -0.016975 | 0.054932 | 0.091553 | 0.013733 | 0.013733 | 0.15564 | 0.009155 | -0.11444 | -25.6805 | -25.7217 | -25.827 | -8.8348 | -8.757 | -25.5936 | -25.6714 | 25.5569 | 25.4334 | -97.0551 | 25.6393 | 25.5615 | 0.12817 | -97.1558 | -0.045776 | -0.1236 | -106.0455 | -0.13275 | -0.27923 | -0.15564 | -105.9677 | 25.7034 | 25.6027 | 25.5615 | -97.3251 | 16.713 | 16.7908 | -0.17395 | -122.8821
666.8438 | 123.0011 | -25.4471 | 97.3022 | 0.44228 | 0.14124 | 0.1504 | 0.048338 | 0.11774 | 0.011865 | 0.043039 | 0.15363 | 0.18807 | 0.0042991 | 0.18276 | 0.020357 | -0.018043 | 0.073242 | 0.09613 | 0.027466 | 0.036621 | 0.13275 | 0.027466 | -0.10529 | -25.5981 | -25.6485 | -25.7355 | -8.8348 | -8.7616 | -25.4883 | -25.5936 | 25.4745 | 25.3418 | -97.1695 | 25.5432 | 25.4837 | 0.14191 | -97.229 | -0.041198 | -0.14648 | -106.1371 | -0.15106 | -0.28839 | -0.14191 | -106.0638 | 25.5798 | 25.5203 | 25.4745 | -97.4075 | 16.6122 | 16.6855 | -0.20142 | -122.8958
667.8438 | 122.9645 | -25.3922 | 97.3663 | 0.82375 | 0.14017 | 0.1301 | 0.055814 | 0.11453 | 0.0086597 | 0.035562 | 0.26044 | 0.19341 | -0.018131 | 0.18276 | 0.013948 | -0.015907 | 0.082397 | 0.11902 | 0.041199 | 0.059509 | 0.10986 | 0.022888 | -0.091553 | -25.5341 | -25.5936 | -25.6805 | -8.844 | -8.7616 | -25.4471 | -25.5386 | 25.415 | 25.3006 | -97.2565 | 25.5112 | 25.4517 | 0.15106 | -97.2839 | -0.054932 | -0.14648 | -106.2103 | -0.14191 | -0.28839 | -0.14191 | -106.1279 | 25.502 | 25.4745 | 25.4333 | -97.4579 | 16.5482 | 16.6306 | -0.20142 | -122.905
668.8438 | 122.9919 | -25.2274 | 97.5403 | 0.50332 | 0.15192 | 0.14292 | 0.059019 | 0.1156 | 0.0097277 | 0.037698 | 0.24518 | 0.19341 | -0.0085179 | 0.17849 | 0.023561 | -0.019111 | 0.07782 | 0.11444 | 0.036621 | 0.059509 | 0.068665 | -0.036621 | -0.16022 | -25.351 | -25.4013 | -25.4929 | -8.8394 | -8.7616 | -25.2686 | -25.3647 | 25.1907 | 25.0671 | -97.4716 | 25.3418 | 25.2869 | 0.21973 | -97.4625 | -0.041199 | -0.13733 | -106.3797 | -0.1236 | -0.2655 | -0.12817 | -106.3019 | 25.296 | 25.3052 | 25.264 | -97.7005 | 16.3879 | 16.4658 | -0.17395 | -122.905
669.8438 | 123.0286 | -25.0488 | 97.6547 | 0.36599 | 0.15406 | 0.14292 | 0.055814 | 0.12521 | 0.018273 | 0.040903 | 0.18414 | 0.20089 | -0.0074499 | 0.17528 | 0.020357 | -0.03086 | 0.086975 | 0.09613 | 0.032043 | 0.068665 | 0.11444 | 0.022888 | -0.11902 | -25.2045 | -25.2457 | -25.3464 | -8.8394 | -8.7616 | -25.1404 | -25.2319 | 25.0717 | 24.9298 | -97.5403 | 25.145 | 25.1175 | 0.18768 | -97.5677 | -0.091553 | -0.18311 | -106.4941 | -0.15564 | -0.29755 | -0.11444 | -106.4163 | 25.1633 | 25.1358 | 25.0809 | -97.7737 | 16.2094 | 16.2872 | -0.19684 | -122.8867
670.8438 | 123.0606 | -25.0122 | 97.7325 | 0.51858 | 0.16795 | 0.13865 | 0.068632 | 0.11239 | 0.030023 | 0.05372 | 0.16888 | 0.19662 | -0.0053139 | 0.17955 | 0.021425 | -0.034064 | 0.073242 | 0.059509 | 0.027466 | 0.054932 | 0.12817 | 0.009155 | -0.13275 | -25.1358 | -25.1724 | -25.3006 | -8.844 | -8.7524 | -25.0626 | -25.1678 | 25.0214 | 24.8795 | -97.6044 | 25.0717 | 25.0671 | 0.18768 | -97.6593 | -0.050354 | -0.15564 | -106.5765 | -0.1236 | -0.28839 | -0.13275 | -106.485 | 25.1404 | 25.0854 | 25.0397 | -97.8653 | 16.1682 | 16.2598 | -0.16022 | -122.9004
671.8438 | 123.0194 | -24.7696 | 98.0026 | 0.48806 | 0.13911 | 0.14078 | 0.061155 | 0.11026 | 0.0097277 | 0.044107 | 0.15363 | 0.19448 | -0.0010409 | 0.1678 | 0.0064719 | -0.028724 | -0.1236 | -0.064087 | 0.013733 | 0.059509 | 0.082397 | -0.022888 | -0.13733 | -24.9161 | -24.9435 | -25.0488 | -8.844 | -8.757 | -24.8657 | -24.9344 | 24.7467 | 24.6323 | -97.9202 | 24.7055 | 24.8291 | 0.19684 | -98.1262 | -0.096131 | -0.1648 | -106.8466 | -0.14649 | -0.27924 | -0.11444 | -106.7596 | 24.852 | 24.646 | 24.7833 | -98.14 | 15.9256 | 16.0126 | -0.17395 | -122.937
672.8438 | 123.056 | -24.4766 | 98.2773 | 0.5491 | 0.15833 | 0.14292 | 0.070768 | 0.11774 | 0.016137 | 0.045175 | 0.2757 | 0.18914 | -0.011723 | 0.17955 | 0.01288 | -0.027656 | 0.07782 | 0.10529 | 0.054932 | 0.054932 | 0.1236 | 0.009155 | -0.11444 | -24.6597 | -24.7787 | -24.7055 | -8.8531 | -8.7662 | -24.5544 | -24.614 | 24.4858 | 24.3622 | -98.1537 | 24.5819 | 24.5316 | 0.16937 | -98.1995 | -0.077819 | -0.13733 | -107.1304 | -0.1831 | -0.22888 | -0.091552 | -107.0435 | 24.6002 | 24.5544 | 24.5316 | -98.3917 | 15.6235 | 15.7105 | -0.30212 | -122.8912
673.8438 | 123.0377 | -24.6048 | 98.1537 | 0.56436 | 0.15833 | 0.13651 | 0.059019 | 0.13162 | 0.0097277 | 0.04838 | 0.26044 | 0.18487 | -0.0010409 | 0.18917 | 0.020357 | -0.014838 | 0.091553 | 0.09613 | 0.054932 | 0.064087 | 0.091553 | 0.013733 | -0.12817 | -24.733 | -24.7604 | -24.8703 | -8.844 | -8.7616 | -24.6552 | -24.733 | 24.6185 | 24.4766 | -98.0621 | 24.7009 | 24.6689 | 0.19226 | -98.0621 | -0.050354 | -0.12817 | -106.9977 | -0.12817 | -0.2655 | -0.13733 | -106.9153 | 24.6964 | 24.6964 | 24.6597 | -98.2819 | 15.7608 | 15.8432 | -0.15564 | -122.8867
674.8438 | 123.0743 | -24.5316 | 98.2452 | 0.68643 | 0.1359 | 0.14506 | 0.053678 | 0.12094 | 0.023614 | 0.059061 | 0.33673 | 0.20089 | 0.0032311 | 0.18276 | 0.023561 | -0.021247 | 0.10986 | 0.10071 | 0.036621 | 0.086975 | 0.11444 | 0.022888 | -0.11902 | -24.6689 | -24.6918 | -24.8016 | -8.8394 | -8.7616 | -24.5819 | -24.678 | 24.5544 | 24.4125 | -98.1308 | 24.6323 | 24.6185 | 0.20599 | -98.1354 | -0.050354 | -0.14648 | -107.0847 | -0.13733 | -0.27008 | -0.1236 | -107.0068 | 24.646 | 24.6414 | 24.5682 | -98.3643 | 15.6921 | 15.77 | -0.16022 | -122.9233
675.8438 | 123.0515 | -24.3713 | 98.3871 | 0.57961 | 0.15299 | 0.12476 | 0.064359 | 0.11667 | 0.017205 | 0.047311 | 0.1994 | 0.187 | 0.0085721 | 0.17208 | 0.028902 | -0.03086 | 0.064087 | 0.050354 | 0.009155 | 0.050354 | 0.13275 | 0.022888 | -0.13275 | -24.5178 | -24.5453 | -24.646 | -8.8394 | -8.757 | -24.4537 | -24.4995 | 24.3942 | 24.2386 | -98.2544 | 24.4217 | 24.4217 | 0.18311 | -98.3231 | -0.082397 | -0.12817 | -107.2266 | -0.14648 | -0.27466 | -0.14648 | -107.1442 | 24.5041 | 24.4354 | 24.3805 | -98.5199 | 15.5319 | 15.6143 | -0.17395 | -122.8867
676.8438 | 122.9599 | -24.4446 | 98.3826 | 0.44228 | 0.16367 | 0.14506 | 0.065427 | 0.1188 | 0.027886 | 0.052652 | 2.534 | 0.20516 | -0.0085179 | 0.19237 | 0.016085 | -0.022315 | 0.009155 | -0.045776 | -0.09613 | -0.009155 | 0.14648 | -0.032043 | -0.15564 | -24.6597 | -24.7375 | -24.7879 | -8.8394 | -8.7616 | -24.4949 | -24.5819 | 24.4125 | 24.2889 | -98.2361 | 24.3988 | 24.4354 | 0.14649 | -98.3734 | -0.050354 | -0.13733 | -107.222 | -0.21515 | -0.34332 | -0.20599 | -107.1442 | 24.5911 | 24.4537 | 24.3484 | -98.5382 | 15.6052 | 15.683 | -0.29297 | -122.9645
677.8438 | 122.9095 | -24.4125 | 98.4421 | 0.45754 | 0.16795 | 0.14506 | 0.082517 | 0.11774 | 0.02575 | 0.057993 | 0.12311 | 0.20089 | -0.0053139 | 0.18917 | 0.017153 | -0.01377 | -0.013733 | -0.045776 | -0.10529 | -0.009155 | 0.13275 | -0.027466 | -0.14191 | -24.6002 | -24.6643 | -24.7559 | -8.8486 | -8.757 | -24.4308 | -24.5499 | 24.3851 | 24.2706 | -98.3093 | 24.3668 | 24.4034 | 0.13275 | -98.4558 | -0.01831 | -0.13733 | -107.2906 | -0.18768 | -0.34332 | -0.20599 | -107.1991 | 24.5453 | 24.3988 | 24.3073 | -98.584 | 15.564 | 15.6555 | -0.25177 | -122.9919
678.8438 | 123.0698 | -24.1608 | 98.6115 | 0.4728 | 0.16047 | 0.1301 | 0.051542 | 0.1188 | 0.015069 | 0.055856 | 0.22992 | 0.19448 | 0.01498 | 0.17421 | 0.026766 | -0.020179 | 0.022888 | 0.022888 | -0.004578 | 0.027466 | 0.1236 | 0.004578 | -0.13275 | -24.321 | -24.3256 | -24.4583 | -8.844 | -8.757 | -24.2157 | -24.3118 | 24.1653 | 24.028 | -98.4879 | 24.1837 | 24.1882 | 0.16022 | -98.5886 | -0.054931 | -0.15106 | -107.4554 | -0.16022 | -0.29755 | -0.14648 | -107.3685 | 24.2844 | 24.1837 | 24.1562 | -98.7442 | 15.3168 | 15.4037 | -0.1648 | -122.9233
679.8438 | 123.0377 | -23.8632 | 98.9639 | 0.51858 | 0.15406 | 0.12903 | 0.065427 | 0.11453 | 0.016137 | 0.034494 | 0.29095 | 0.19448 | 0.019253 | 0.1913 | 0.020357 | -0.0094981 | 0.013733 | -0.004578 | -0.050354 | 0.004578 | 0.13275 | 0 | -0.15564 | -24.0326 | -24.0646 | -24.1699 | -8.8394 | -8.7616 | -23.8953 | -24.0097 | 23.8632 | 23.7076 | -98.8312 | 23.8586 | 23.8678 | 0.16022 | -98.9502 | -0.032044 | -0.14649 | -107.8033 | -0.16937 | -0.3067 | -0.16022 | -107.7255 | 23.996 | 23.877 | 23.8129 | -99.1196 | 15.0238 | 15.1016 | -0.20142 | -122.9736
680.8438 | 123.0423 | -23.909 | 98.9044 | 1.6477 | 0.16795 | 0.14826 | 0.066496 | 0.11026 | 0.014001 | 0.050516 | 0.33673 | 0.20303 | 0.010708 | 0.1913 | 0.0086079 | -0.014838 | -0.004578 | -0.027466 | -0.068665 | 0 | 0.16022 | -0.022888 | -0.16022 | -24.1104 | -24.147 | -24.2523 | -8.844 | -8.7479 | -23.9502 | -24.0555 | 23.8861 | 23.7488 | -98.7442 | 23.8815 | 23.909 | 0.16022 | -98.909 | -0.041198 | -0.14648 | -107.7484 | -0.20142 | -0.34332 | -0.19684 | -107.6523 | 24.0692 | 23.9044 | 23.8403 | -99.0646 | 15.065 | 15.1611 | -0.23804 | -122.9599
681.8438 | 122.9691 | -23.9182 | 98.9731 | 0.45754 | 0.16367 | 0.15146 | 0.073972 | 0.12735 | 0.018273 | 0.044107 | 0.26044 | 0.20837 | 0.0053671 | 0.18703 | 6.2882e-05 | -0.031928 | 0.13275 | -0.17853 | -0.11444 | 0.073242 | 0.15106 | 0.013733 | -0.10986 | -24.1104 | -24.1653 | -24.2523 | -8.844 | -8.757 | -23.9594 | -24.0555 | 23.9319 | 23.8083 | -98.822 | 23.7396 | 23.9914 | 0.18311 | -98.8403 | -0.041199 | -0.13733 | -107.8171 | -0.19226 | -0.33417 | -0.19684 | -107.7301 | 24.0692 | 24.0509 | 23.8037 | -99.0829 | 15.0742 | 15.1611 | -0.24719 | -123.0286
682.8438 | 122.9782 | -23.4924 | 99.3668 | 0.45754 | 0.15299 | 0.15253 | 0.065427 | 0.11774 | 0.019342 | 0.044107 | 0.1994 | 0.20837 | 0.0085721 | 0.17101 | 0.010744 | -0.015907 | -0.022888 | -0.050354 | -0.086975 | -0.018311 | 0.14648 | -0.009155 | -0.15106 | -23.6893 | -24.0005 | -23.7762 | -8.8394 | -8.7524 | -23.5291 | -23.6343 | 23.4833 | 23.3414 | -99.2203 | 23.4421 | 23.4741 | 0.13275 | -99.3896 | -0.036621 | -0.14191 | -108.2062 | -0.19684 | -0.28381 | -0.14191 | -108.1192 | 23.6389 | 23.4695 | 23.4055 | -99.5178 | 14.653 | 14.74 | -0.50812 | -123.0011
683.8438 | 122.9553 | -23.7396 | 99.1653 | 0.13711 | 0.16901 | 0.13972 | 0.073972 | 0.12094 | 0.02041 | 0.049448 | -0.075256 | 0.19662 | 0.0096401 | 0.17955 | 0.021425 | -0.020179 | -0.022888 | -0.054932 | -0.082397 | -0.013733 | 0.12817 | -0.027466 | -0.16937 | -23.9594 | -23.9868 | -24.0967 | -8.844 | -8.7524 | -23.7717 | -23.8586 | 23.7122 | 23.5703 | -99.0372 | 23.6847 | 23.7259 | 0.15564 | -99.1882 | -0.032043 | -0.11902 | -108.0093 | -0.21973 | -0.35706 | -0.23804 | -107.9178 | 23.8678 | 23.7167 | 23.6572 | -99.3347 | 14.8956 | 14.9872 | -0.24719 | -123.024
684.8438 | 122.9828 | -23.3597 | 99.5224 | 0.13711 | 0.17863 | 0.13544 | 0.059019 | 0.1188 | 0.019342 | 0.059061 | -0.01422 | 0.20623 | 0.0053671 | 0.19558 | 0.017153 | -0.01377 | -0.013733 | -0.013733 | -0.07782 | -0.009155 | 0.13275 | -0.032043 | -0.15106 | -23.5748 | -23.5474 | -23.6893 | -8.8348 | -8.757 | -23.3917 | -23.4787 | 23.3276 | 23.2086 | -99.3896 | 23.3459 | 23.3505 | 0.14191 | -99.5361 | -0.032044 | -0.11902 | -108.3572 | -0.21515 | -0.32959 | -0.21057 | -108.2794 | 23.4924 | 23.3459 | 23.2819 | -99.6735 | 14.5248 | 14.6027 | -0.18768 | -123.0011
685.8438 | 122.9782 | -23.0759 | 99.8062 | 0.45754 | 0.16795 | 0.13865 | 0.068632 | 0.12094 | 0.0086597 | 0.049448 | 0.21466 | 0.19769 | 0.016048 | 0.19558 | 0.018221 | 0.0033199 | -0.027466 | -0.059509 | -0.10986 | 0.004578 | 0.17853 | -0.018311 | -0.14648 | -23.3734 | -23.1079 | -23.3139 | -8.844 | -8.7616 | -23.1216 | -23.2269 | 23.0576 | 22.9294 | -99.6277 | 23.0164 | 23.0804 | 0.15106 | -99.8337 | -0.045776 | -0.15106 | -108.6502 | -0.29755 | -0.23804 | -0.086975 | -108.5678 | 23.2544 | 23.0484 | 22.966 | -99.9527 | 14.2319 | 14.3143 | -0.032043 | -123.0331
686.8438 | 122.9645 | -23.0026 | 99.8932 | 0.44228 | 0.16795 | 0.13758 | 0.063291 | 0.13482 | 0.011865 | 0.055856 | 0.15363 | 0.2073 | 0.0096401 | 0.1913 | 0.020357 | -0.016975 | -0.041199 | -0.050354 | -0.10529 | -0.027466 | 0.14191 | -0.009155 | -0.14191 | -23.2224 | -23.2361 | -23.3414 | -8.8394 | -8.7524 | -23.0301 | -23.1308 | 22.9935 | 22.8607 | -99.7513 | 22.9523 | 22.9752 | 0.11444 | -99.9344 | -0.027465 | -0.12817 | -108.7326 | -0.21973 | -0.33875 | -0.21057 | -108.6456 | 23.1445 | 22.9614 | 22.8973 | -100.0351 | 14.1632 | 14.2502 | -0.23346 | -123.024
687.8438 | 122.9507 | -23.1766 | 99.7604 | 0.38125 | 0.15192 | 0.14826 | 0.073972 | 0.12521 | 0.0054557 | 0.050516 | 0.16888 | 0.20303 | 0.029934 | 0.1678 | 0.01288 | -0.018043 | -0.036621 | -0.09613 | -0.10529 | -0.018311 | 0.15106 | -0.004578 | -0.14191 | -23.4055 | -23.4055 | -23.5245 | -8.8394 | -8.757 | -23.2132 | -23.3002 | 23.172 | 23.0347 | -99.6094 | 23.0804 | 23.1583 | 0.1236 | -99.7971 | -0.036621 | -0.1236 | -108.5999 | -0.22888 | -0.3479 | -0.2243 | -108.5175 | 23.3276 | 23.14 | 23.0713 | -99.9023 | 14.3372 | 14.4196 | -0.22888 | -123.0606
688.8438 | 122.9874 | -23.1766 | 99.7238 | 0.13711 | 0.18504 | 0.13651 | 0.076109 | 0.11667 | 0.016137 | 0.033426 | 0.15363 | 0.20623 | 0.0096401 | 0.1881 | 0.017153 | -0.011634 | -0.041199 | -0.07782 | -0.10071 | -0.027466 | 0.13275 | -0.036621 | -0.16479 | -23.4421 | -23.4146 | -23.5519 | -8.8394 | -8.757 | -23.2224 | -23.3139 | 23.14 | 23.0118 | -99.5911 | 23.0988 | 23.1491 | 0.13733 | -99.765 | -0.045776 | -0.13733 | -108.5632 | -0.2655 | -0.37537 | -0.23804 | -108.4808 | 23.3093 | 23.1354 | 23.0759 | -99.8886 | 14.3372 | 14.4196 | -0.23804 | -123.0377
689.8438 | 122.9416 | -22.9477 | 99.9527 | 0.25918 | 0.16581 | 0.13865 | 0.068632 | 0.12628 | 0.024682 | 0.041971 | -0.044738 | 0.20089 | -0.0031779 | 0.18489 | 0.016085 | -0.018043 | -0.032043 | -0.054932 | -0.09613 | -0.018311 | 0.13733 | -0.027466 | -0.16937 | -23.1857 | -23.1583 | -23.3231 | -8.8348 | -8.7479 | -22.9797 | -23.0713 | 22.9202 | 22.7783 | -99.8154 | 22.8928 | 22.9294 | 0.15106 | -99.9847 | -0.032043 | -0.1236 | -108.7875 | -0.23804 | -0.37537 | -0.25177 | -108.7006 | 23.085 | 22.9156 | 22.8516 | -100.1221 | 14.1129 | 14.1998 | -0.21057 | -123.024
690.8438 | 123.0057 | -22.9156 | 100.0305 | 0.060816 | 0.17329 | 0.14719 | 0.072904 | 0.11453 | 0.018273 | 0.04838 | 1.7253 | 0.20089 | 0.0096401 | 0.1881 | 0.011812 | -0.014838 | 0.036621 | 0.032043 | -0.018311 | 0.022888 | 0.14191 | -0.009155 | -0.13733 | -23.053 | -23.0576 | -23.204 | -8.844 | -8.7524 | -22.9294 | -23.0209 | 22.9065 | 22.7783 | -99.8886 | 22.9477 | 22.9385 | 0.16022 | -99.9939 | -0.013733 | -0.10529 | -108.8745 | -0.13733 | -0.28839 | -0.18311 | -108.783 | 23.0576 | 22.9523 | 22.8973 | -100.1678 | 14.0717 | 14.1632 | -0.14191 | -123.0515
691.8438 | 122.9507 | -22.7783 | 100.1129 | 0.076074 | 0.17649 | 0.13758 | 0.062223 | 0.12842 | 0.010797 | 0.046243 | -0.22784 | 0.20623 | 0.011776 | 0.18703 | 0.016085 | -0.02552 | 0.013733 | 0.041199 | -0.045776 | 0.032043 | 0.14191 | -0.004578 | -0.14648 | -22.9568 | -22.934 | -23.0804 | -8.844 | -8.757 | -22.8195 | -22.9431 | 22.7737 | 22.6318 | -99.971 | 22.8195 | 22.8104 | 0.17853 | -100.0992 | -0.041199 | -0.16479 | -108.9569 | -0.17853 | -0.30212 | -0.13733 | -108.8699 | 22.9202 | 22.7921 | 22.7325 | -100.2594 | 13.9343 | 14.0213 | -0.15564 | -123.056
692.8438 | 122.9645 | -22.6273 | 100.3052 | 0.19814 | 0.16367 | 0.13758 | 0.0697 | 0.12308 | 0.015069 | 0.04838 | 0.031556 | 0.19448 | 2.7137e-05 | 0.19344 | 0.017153 | -0.022315 | -0.036621 | -0.036621 | -0.082397 | -0.013733 | 0.11902 | -0.022888 | -0.15564 | -22.8561 | -22.8378 | -22.9797 | -8.8394 | -8.757 | -22.6776 | -22.7509 | 22.6044 | 22.4716 | -100.1862 | 22.5906 | 22.6135 | 0.14191 | -100.3418 | -0.050354 | -0.1236 | -109.1446 | -0.22888 | -0.35248 | -0.22888 | -109.0622 | 22.7463 | 22.5906 | 22.5449 | -100.4608 | 13.7878 | 13.8702 | -0.21057 | -123.056
693.8438 | 123.0011 | -22.6089 | 100.3189 | 0.091333 | 0.1829 | 0.13651 | 0.063291 | 0.1188 | 0.011865 | 0.047311 | 0.10785 | 0.18914 | 0.011776 | 0.18383 | 0.01288 | -0.02552 | -0.022888 | -0.027466 | -0.073242 | 0.004578 | 0.13275 | -0.027466 | -0.13733 | -22.8333 | -22.7737 | -22.9431 | -8.844 | -8.757 | -22.6639 | -22.7188 | 22.5815 | 22.4716 | -100.1862 | 22.5815 | 22.6135 | 0.14191 | -100.3418 | -0.054931 | -0.10986 | -109.1629 | -0.2243 | -0.33417 | -0.2243 | -109.0759 | 22.7417 | 22.5861 | 22.5357 | -100.4562 | 13.765 | 13.8519 | -0.16479 | -123.0377
694.8438 | 123.0377 | -22.467 | 100.47 | 0.2897 | 0.18076 | 0.13437 | 0.077177 | 0.1156 | 0.017205 | 0.040903 | -0.090514 | 0.20409 | 0.011776 | 0.18703 | 0.021425 | -0.01377 | 0.013733 | 0 | -0.064087 | 0.018311 | 0.13733 | 0 | -0.13733 | -22.6822 | -22.641 | -22.7921 | -8.8348 | -8.757 | -22.5128 | -22.5998 | 22.467 | 22.3297 | -100.3326 | 22.467 | 22.4854 | 0.15564 | -100.4562 | -0.045776 | -0.13275 | -109.3048 | -0.21515 | -0.32501 | -0.19226 | -109.227 | 22.6044 | 22.4808 | 22.403 | -100.6073 | 13.6322 | 13.71 | -0.17395 | -123.0698
695.8438 | 122.9965 | -21.9681 | 100.946 | -0.00022031 | 0.19038 | 0.13437 | 0.082517 | 0.13482 | 0.018273 | 0.044107 | -0.059997 | 0.20516 | 0.0032311 | 0.18917 | 0.017153 | -0.015907 | 0.25635 | 0.17853 | 0.022888 | 0.036621 | 0.17853 | 0.1236 | -0.018311 | -22.1649 | -22.1054 | -22.2794 | -8.8394 | -8.757 | -22.0001 | -22.0871 | 22.0917 | 21.9498 | -100.7675 | 22.1466 | 22.0047 | 0.054932 | -100.6897 | -0.032043 | -0.11902 | -109.7855 | -0.19684 | -0.31128 | -0.19226 | -109.7031 | 22.1466 | 22.2244 | 21.991 | -100.9644 | 13.1287 | 13.2111 | -0.13733 | -123.0331
696.8438 | 123.0377 | -21.8124 | 101.1063 | -0.061255 | 0.16047 | 0.13865 | 0.07504 | 0.11987 | 0.0033197 | 0.041971 | -0.10577 | 0.19128 | 0.0021631 | 0.1913 | 0.02997 | -0.015907 | 0.018311 | 0.018311 | -0.036621 | 0.018311 | 0.13275 | -0.009155 | -0.1236 | -22.023 | -21.9086 | -22.142 | -8.8348 | -8.757 | -21.8399 | -21.936 | 21.8033 | 21.6888 | -100.9735 | 21.8308 | 21.8308 | 0.14191 | -101.088 | -0.027466 | -0.1236 | -109.9411 | -0.21057 | -0.32959 | -0.20599 | -109.8633 | 21.9452 | 21.8308 | 21.7758 | -101.2299 | 12.9776 | 13.0554 | -0.09613 | -123.0423
697.8438 | 123.0469 | -21.5698 | 101.3718 | -0.15281 | 0.17008 | 0.14506 | 0.077177 | 0.13589 | 0.0033197 | 0.04838 | -0.34991 | 0.19769 | 0.0021631 | 0.1881 | 0.015017 | -0.014838 | -0.009155 | -0.013733 | -0.073242 | 0.009155 | 0.1236 | -0.018311 | -0.14648 | -21.7758 | -21.698 | -21.8582 | -8.8486 | -8.7616 | -21.6064 | -21.6797 | 21.5515 | 21.4233 | -101.2482 | 21.5561 | 21.579 | 0.15564 | -101.3809 | -0.036621 | -0.10986 | -110.2203 | -0.20599 | -0.28839 | -0.17853 | -110.1334 | 21.6934 | 21.5607 | 21.4966 | -101.5182 | 12.7213 | 12.8082 | -0.12817 | -123.0515
698.8438 | 123.0423 | -21.4554 | 101.4908 | -0.18333 | 0.16154 | 0.14933 | 0.070768 | 0.12414 | 0.010797 | 0.047311 | -0.38043 | 0.20837 | 0.0032311 | 0.17955 | 0.010744 | -0.019111 | -0.045776 | -0.022888 | -0.07782 | 0.004578 | 0.15564 | -0.032043 | -0.15564 | -21.6705 | -21.5744 | -21.7575 | -8.8394 | -8.7524 | -21.4828 | -21.6019 | 21.4233 | 21.2997 | -101.3351 | 21.4325 | 21.46 | 0.16022 | -101.5366 | -0.027466 | -0.14648 | -110.3302 | -0.21515 | -0.30212 | -0.15564 | -110.2432 | 21.611 | 21.4096 | 21.3776 | -101.6464 | 12.616 | 12.7029 | -0.11902 | -123.0927
699.8438 | 123.0377 | -21.2173 | 101.6785 | -0.16807 | 0.1562 | 0.15253 | 0.062223 | 0.12201 | 0.00011475 | 0.037698 | -0.18207 | 0.19875 | 0.01498 | 0.17101 | 0.0086079 | -0.019111 | -0.004578 | 0.018311 | -0.050354 | 0.041199 | 0.13275 | -0.022888 | -0.16479 | -21.4142 | -21.3455 | -21.5012 | -8.844 | -8.757 | -21.2494 | -21.3593 | 21.1945 | 21.0526 | -101.5457 | 21.2357 | 21.2585 | 0.20599 | -101.683 | -0.032044 | -0.14191 | -110.5225 | -0.19684 | -0.28381 | -0.14191 | -110.4355 | 21.3501 | 21.2128 | 21.167 | -101.8433 | 12.3734 | 12.4603 | -0.12817 | -123.0377
700.8438 | 123.0377 | -20.9747 | 101.9531 | -0.00022031 | 0.16261 | 0.13865 | 0.064359 | 0.12201 | 0.012933 | 0.04838 | -0.075256 | 0.19769 | -0.0021099 | 0.18169 | 0.011812 | -0.021247 | 0 | 0.022888 | -0.032043 | 0.018311 | 0.14191 | 0 | -0.13733 | -21.167 | -21.1166 | -21.2723 | -8.844 | -8.757 | -21.0251 | -21.0892 | 20.9747 | 20.8374 | -101.8112 | 20.9976 | 20.993 | 0.15564 | -101.9531 | -0.050354 | -0.11444 | -110.7971 | -0.19226 | -0.29755 | -0.18311 | -110.7101 | 21.1166 | 20.9747 | 20.9427 | -102.0905 | 12.1307 | 12.2177 | -0.14191 | -123.0423
701.8438 | 123.0423 | -20.9244 | 101.9943 | -0.00022031 | 0.17542 | 0.14719 | 0.064359 | 0.11987 | 0.0011837 | 0.041971 | -0.22784 | 0.19448 | -0.0021099 | 0.19451 | 0.0086079 | -0.019111 | 0.009155 | 0.032043 | -0.036621 | 0.032043 | 0.15106 | -0.018311 | -0.15564 | -21.1258 | -21.0571 | -21.2219 | -8.8394 | -8.7616 | -20.9702 | -21.0388 | 20.9061 | 20.7687 | -101.8433 | 20.9564 | 20.9564 | 0.18768 | -101.9852 | -0.045777 | -0.11444 | -110.8337 | -0.20142 | -0.29755 | -0.18311 | -110.7559 | 21.0754 | 20.9335 | 20.8878 | -102.15 | 12.085 | 12.1628 | -0.13275 | -123.0331
702.8438 | 123.0652 | -20.755 | 102.182 | -0.18333 | 0.16795 | 0.14826 | 0.072904 | 0.12201 | 0.0086597 | 0.037698 | -0.44147 | 0.19982 | 0.013912 | 0.18276 | 0.025698 | -0.020179 | -0.018311 | 0.018311 | -0.045776 | 0.018311 | 0.15106 | -0.041199 | -0.15564 | -20.9564 | -20.8649 | -21.0526 | -8.8486 | -8.7662 | -20.7916 | -20.8923 | 20.7138 | 20.5994 | -102.0309 | 20.7733 | 20.7733 | 0.17395 | -102.2003 | -0.036621 | -0.13733 | -111.0306 | -0.20142 | -0.29755 | -0.16022 | -110.9482 | 20.9061 | 20.7367 | 20.7092 | -102.3376 | 11.9064 | 11.9888 | -0.10986 | -123.0743
703.8438 | 123.0331 | -20.6726 | 102.2507 | -0.2291 | 0.16901 | 0.14185 | 0.056883 | 0.12308 | 0.0043877 | 0.047311 | -0.33466 | 0.19662 | 0.0053671 | 0.18596 | 0.0086079 | -0.023383 | -0.045776 | -0.004578 | -0.086975 | 0.022888 | 0.13275 | -0.036621 | -0.15106 | -20.9015 | -20.8054 | -20.993 | -8.844 | -8.7524 | -20.7321 | -20.8191 | 20.636 | 20.5215 | -102.1179 | 20.668 | 20.6955 | 0.17395 | -102.2964 | -0.05951 | -0.14649 | -111.0947 | -0.22888 | -0.32043 | -0.17395 | -111.0031 | 20.8054 | 20.6268 | 20.5856 | -102.4017 | 11.8286 | 11.9202 | -0.13275 | -123.0698
704.8438 | 123.0148 | -20.6589 | 102.2964 | -0.2291 | 0.15726 | 0.15787 | 0.065427 | 0.12308 | -0.0062933 | 0.037698 | -2.6845 | 0.19021 | 0.0085721 | 0.19451 | 0.017153 | -0.012702 | -0.054932 | -0.018311 | -0.082397 | 0 | 0.14648 | -0.036621 | -0.15564 | -20.9106 | -20.8466 | -21.0022 | -8.8394 | -8.7662 | -20.7184 | -20.7916 | 20.6223 | 20.5032 | -102.15 | 20.6406 | 20.6589 | 0.15564 | -102.3514 | -0.059509 | -0.13275 | -111.1359 | -0.25177 | -0.34332 | -0.21057 | -111.0626 | 20.8054 | 20.6039 | 20.5765 | -102.4521 | 11.8195 | 11.8927 | -0.18768 | -123.0881
705.8438 | 123.0515 | -20.5124 | 102.4658 | 0.13711 | 0.14338 | 0.13865 | 0.062223 | 0.11987 | 0.015069 | 0.038766 | -0.28888 | 0.20196 | 0.0085721 | 0.17955 | 0.011812 | -0.029792 | -0.050354 | -0.022888 | -0.082397 | -0.004578 | 0.16937 | -0.036621 | -0.14191 | -20.7092 | -20.6131 | -20.8282 | -8.8486 | -8.7662 | -20.5399 | -20.6223 | 20.4758 | 20.3705 | -102.2964 | 20.4895 | 20.5078 | 0.13733 | -102.5162 | -0.027466 | -0.10986 | -111.3144 | -0.19684 | -0.31586 | -0.20599 | -111.232 | 20.6818 | 20.462 | 20.43 | -102.6077 | 11.6638 | 11.7462 | -0.10071 | -123.0881
706.8438 | 123.0423 | -20.1141 | 102.8229 | -0.2291 | 0.14979 | 0.14292 | 0.064359 | 0.12201 | -0.00095325 | 0.040903 | -0.30414 | 0.19875 | 0.0010951 | 0.1913 | 0.02463 | -0.016975 | -0.045776 | -0.022888 | -0.086975 | 0 | 0.14191 | -0.027466 | -0.14191 | -20.3156 | -20.192 | -20.4254 | -8.844 | -8.757 | -20.137 | -20.2332 | 20.0867 | 19.9722 | -102.681 | 20.0912 | 20.1141 | 0.14191 | -102.8687 | -0.022888 | -0.11902 | -111.6669 | -0.20142 | -0.31128 | -0.19226 | -111.5799 | 20.256 | 20.0684 | 20.0272 | -102.9648 | 11.2701 | 11.3571 | -0.07782 | -123.056
707.8438 | 123.0606 | -20.2103 | 102.7359 | -0.12229 | 0.14231 | 0.14292 | 0.055814 | 0.11774 | 0.0054557 | 0.050516 | -0.28888 | 0.21157 | -0.0063819 | 0.18276 | 0.011812 | -0.015907 | -0.041199 | -0.032043 | -0.07782 | 0 | 0.14648 | -0.018311 | -0.16022 | -20.4529 | -20.3568 | -20.5307 | -8.844 | -8.7616 | -20.2698 | -20.3384 | 20.192 | 20.05 | -102.5894 | 20.1782 | 20.2103 | 0.16022 | -102.7771 | -0.059509 | -0.12817 | -111.5799 | -0.24262 | -0.32043 | -0.19226 | -111.4975 | 20.3568 | 20.1691 | 20.1324 | -102.8961 | 11.3663 | 11.4487 | -0.14648 | -123.0743
708.8438 | 123.0423 | -20.137 | 102.8183 | -1.0683 | 0.14017 | 0.14826 | 0.056883 | 0.11774 | -0.0041573 | 0.039835 | -0.42621 | 0.19448 | 0.0096401 | 0.19024 | 0.0064719 | -0.023383 | -0.050354 | -0.018311 | -0.082397 | 0.004578 | 0.17853 | -0.018311 | -0.15564 | -20.3659 | -20.3156 | -20.4666 | -8.844 | -8.757 | -20.1645 | -20.2652 | 20.1187 | 19.9814 | -102.6398 | 20.1187 | 20.1416 | 0.16022 | -102.8687 | -0.027466 | -0.12817 | -111.6623 | -0.22888 | -0.32959 | -0.20142 | -111.5753 | 20.3156 | 20.0867 | 20.0546 | -102.9739 | 11.293 | 11.38 | -0.17853 | -123.0835
709.8438 | 123.0652 | -19.9173 | 103.038 | -0.015478 | 0.19144 | 0.15253 | 0.073972 | 0.11667 | 0.016137 | 0.047311 | 0.29095 | 0.2073 | 0.019253 | 0.17849 | 0.013948 | -0.021247 | -0.032043 | -0.018311 | -0.086975 | -0.018311 | 0.14191 | -0.022888 | -0.14191 | -20.1096 | -20.1462 | -20.2515 | -8.844 | -8.7616 | -19.9539 | -20.0363 | 19.8944 | 19.7754 | -102.8961 | 19.899 | 19.899 | 0.1236 | -103.0701 | -0.036621 | -0.11902 | -111.882 | -0.19226 | -0.33417 | -0.21515 | -111.7996 | 20.0592 | 19.8853 | 19.8303 | -103.1799 | 11.0733 | 11.1557 | -0.22888 | -123.0743
710.8438 | 123.0377 | -19.9631 | 102.9877 | -0.27488 | 0.14338 | 0.15253 | 0.062223 | 0.12414 | 0.0011837 | 0.035562 | -0.33466 | 0.20409 | -0.0063819 | 0.19024 | 0.0032669 | -0.024451 | -0.059509 | -0.018311 | -0.09613 | -0.009155 | 0.15564 | -0.036621 | -0.15564 | -20.2332 | -20.1736 | -20.3018 | -8.844 | -8.757 | -20.0043 | -20.0867 | 19.9265 | 19.8074 | -102.832 | 19.9448 | 19.9539 | 0.14649 | -103.0472 | -0.041198 | -0.1236 | -111.8317 | -0.27008 | -0.33874 | -0.21515 | -111.7447 | 20.1187 | 19.9036 | 19.8669 | -103.1433 | 11.1191 | 11.2061 | -0.21057 | -123.0743
711.8438 | 123.0515 | -19.3771 | 103.5736 | -0.3054 | 0.14338 | 0.14719 | 0.060087 | 0.11667 | -0.0094983 | 0.043039 | -0.36517 | 0.187 | -0.0021099 | 0.18062 | 0.0011309 | -0.012702 | -0.009155 | 0.073242 | -0.009155 | 0.036621 | 0.13733 | -0.004578 | -0.13275 | -19.5648 | -19.5374 | -19.6838 | -8.8486 | -8.757 | -19.4138 | -19.4916 | 19.3726 | 19.2444 | -103.4363 | 19.4504 | 19.4138 | 0.16937 | -103.5828 | -0.036621 | -0.11444 | -112.4222 | -0.18768 | -0.3067 | -0.19226 | -112.3306 | 19.5145 | 19.368 | 19.368 | -103.7064 | 10.5286 | 10.6201 | -0.16022 | -123.0652
712.8438 | 123.0423 | -19.5831 | 103.3905 | -2.9909 | 0.13697 | 0.15467 | 0.055814 | 0.13162 | 0.012933 | 0.037698 | -0.36517 | 0.19769 | 0.0032311 | 0.18383 | 0.015017 | -0.027656 | -0.018311 | -0.004578 | -0.086975 | 0.009155 | 0.17853 | 0 | -0.13275 | -19.7937 | -19.78 | -19.9081 | -8.8394 | -8.757 | -19.6243 | -19.7113 | 19.5831 | 19.4504 | -103.212 | 19.5786 | 19.5923 | 0.14191 | -103.4088 | -0.041199 | -0.12817 | -112.2299 | -0.21057 | -0.32501 | -0.19684 | -112.1475 | 19.7617 | 19.5648 | 19.4962 | -103.5233 | 10.7437 | 10.8261 | -0.19684 | -123.1018
713.8438 | 123.0423 | -19.3588 | 103.6331 | -0.3054 | 0.1327 | 0.16108 | 0.077177 | 0.13269 | 0.0033197 | 0.034494 | -0.42621 | 0.19234 | 0.0032311 | 0.18489 | 0.0043349 | -0.023383 | -0.022888 | -0.027466 | -0.050354 | 0.004578 | 0.14648 | -0.013733 | -0.16022 | -19.5648 | -19.5511 | -19.6701 | -8.844 | -8.7662 | -19.4 | -19.4824 | 19.3451 | 19.1986 | -103.4866 | 19.3314 | 19.3634 | 0.16479 | -103.656 | -0.041198 | -0.1236 | -112.4771 | -0.20599 | -0.31128 | -0.18768 | -112.3993 | 19.5053 | 19.3359 | 19.3085 | -103.7933 | 10.5148 | 10.5927 | -0.19226 | -123.1155
714.8438 | 123.1247 | -19.2993 | 103.5965 | 0.57961 | 0.15086 | 0.14078 | 0.080381 | 0.11774 | 0.0097277 | 0.039835 | 0.2757 | 0.18914 | 0.0096401 | 0.18383 | 0.015017 | -0.014838 | -0.009155 | 0.013733 | -0.027466 | 0.018311 | 0.12817 | -0.013733 | -0.13733 | -19.4778 | -19.4733 | -19.5877 | -8.844 | -8.7616 | -19.3359 | -19.4412 | 19.2856 | 19.162 | -103.4683 | 19.313 | 19.3176 | 0.15564 | -103.6057 | -0.036621 | -0.14191 | -112.4405 | -0.17853 | -0.28839 | -0.14648 | -112.3581 | 19.4275 | 19.2902 | 19.2719 | -103.7338 | 10.4553 | 10.5377 | -0.17395 | -123.0377
715.8438 | 123.0194 | -19.1666 | 103.8437 | -0.27488 | 0.13911 | 0.14826 | 0.060087 | 0.12201 | 0.0054557 | 0.045175 | -0.34991 | 0.19555 | 0.0064351 | 0.1913 | -0.0010051 | -0.024451 | -0.045776 | -0.022888 | -0.082397 | -0.013733 | 0.14648 | -0.022888 | -0.16022 | -19.3451 | -19.2719 | -19.3359 | -8.8394 | -8.7524 | -19.1528 | -19.2581 | 19.1437 | 19.0063 | -103.6972 | 19.1437 | 19.1528 | 0.14648 | -103.8895 | 0.013733 | -0.091553 | -112.6831 | -0.17853 | -0.16937 | -0.077819 | -112.5961 | 19.313 | 19.1208 | 19.0842 | -104.0039 | 10.3271 | 10.4141 | -0.10529 | -123.1018
716.8438 | 123.0835 | -19.1254 | 103.8757 | -0.35117 | 0.15513 | 0.16001 | 0.077177 | 0.11026 | 0.0043877 | 0.043039 | -0.44147 | 0.187 | 0.0064351 | 0.17955 | -0.0010051 | -0.020179 | -0.050354 | -0.018311 | -0.07782 | -0.009155 | 0.15106 | -0.027466 | -0.16022 | -19.3588 | -19.3314 | -19.4687 | -8.8394 | -8.7616 | -19.1849 | -19.249 | 19.0979 | 18.9651 | -103.7247 | 19.1071 | 19.1162 | 0.15106 | -103.9261 | -0.059509 | -0.1236 | -112.7151 | -0.23346 | -0.34332 | -0.21973 | -112.6373 | 19.2764 | 19.075 | 19.0475 | -104.0359 | 10.2859 | 10.3638 | -0.20599 | -123.1247
717.8438 | 123.0423 | -18.7683 | 104.2053 | -0.25962 | 0.1327 | 0.14185 | 0.065427 | 0.10919 | -0.014838 | 0.040903 | -0.28888 | 0.18914 | 2.7137e-05 | 0.1881 | 0.0054039 | -0.019111 | 0.013733 | 0.073242 | 0.004578 | 0.059509 | 0.13275 | 0.004578 | -0.1236 | -18.9606 | -18.924 | -19.0659 | -8.8394 | -8.7616 | -18.8049 | -18.8828 | 18.7729 | 18.6447 | -104.0726 | 18.8416 | 18.8278 | 0.1831 | -104.1916 | -0.036621 | -0.11444 | -113.0447 | -0.19226 | -0.29755 | -0.18311 | -112.9669 | 18.9011 | 18.782 | 18.7729 | -104.3289 | 9.9289 | 10.0067 | -0.15564 | -123.0881
718.8438 | 123.0698 | -18.5211 | 104.4113 | -0.24436 | 0.14124 | 0.15146 | 0.057951 | 0.12308 | -0.015906 | 0.027017 | -0.41095 | 0.17739 | 0.0064351 | 0.18703 | 6.2882e-05 | -0.023383 | 0.009155 | 0.091553 | 0.013733 | 0.045776 | 0.14191 | 0.009155 | -0.13275 | -18.7042 | -18.663 | -18.8004 | -8.8486 | -8.757 | -18.5715 | -18.631 | 18.5303 | 18.3884 | -104.2694 | 18.6127 | 18.5669 | 0.17853 | -104.4022 | -0.050354 | -0.10986 | -113.2599 | -0.18311 | -0.27924 | -0.16937 | -113.1683 | 18.663 | 18.5303 | 18.5349 | -104.5441 | 9.6725 | 9.7641 | -0.14191 | -123.0423
719.8438 | 123.1155 | -18.4891 | 104.4342 | 0.45754 | 0.17008 | 0.15787 | 0.063291 | 0.11453 | 0.028955 | 0.043039 | 0.22992 | 0.19662 | 0.025661 | 0.17742 | 0.020357 | -0.020179 | -0.018311 | -0.018311 | -0.07782 | -0.009155 | 0.12817 | -0.004578 | -0.15106 | -18.6539 | -18.6859 | -18.8141 | -8.8394 | -8.7524 | -18.5257 | -18.6127 | 18.4845 | 18.338 | -104.306 | 18.4708 | 18.4799 | 0.14191 | -104.4525 | -0.036621 | -0.1236 | -113.2736 | -0.1648 | -0.32501 | -0.20142 | -113.1866 | 18.6172 | 18.4708 | 18.4113 | -104.5853 | 9.6497 | 9.7366 | -0.19684 | -123.0469
720.8438 | 123.0331 | -18.338 | 104.6814 | -0.2291 | 0.12843 | 0.14078 | 0.053678 | 0.13269 | 0.0086597 | 0.032358 | -0.41095 | 0.19555 | 0.0085721 | 0.17742 | 0.018221 | -0.02552 | -0.022888 | 0 | -0.073242 | 0.004578 | 0.18768 | 0.032043 | -0.14648 | -18.5257 | -18.4891 | -18.6493 | -8.844 | -8.7616 | -18.3472 | -18.4341 | 18.3701 | 18.1915 | -104.4937 | 18.338 | 18.3426 | 0.15106 | -104.7043 | -0.009155 | -0.09613 | -113.5254 | -0.18768 | -0.31128 | -0.21515 | -113.443 | 18.5257 | 18.3151 | 18.2648 | -104.8279 | 9.494 | 9.5764 | -0.15106 | -123.1155
721.8438 | 123.0789 | -18.0862 | 104.8874 | -3.2046 | 0.14338 | 0.1504 | 0.061155 | 0.14017 | 0.011865 | 0.044107 | -0.47198 | 0.20409 | 0.0010951 | 0.18596 | 0.011812 | -0.029792 | -0.041199 | -0.013733 | -0.086975 | 0 | 0.17853 | 0.004578 | -0.10986 | -18.3014 | -18.2556 | -18.4204 | -8.844 | -8.7616 | -18.1366 | -18.2236 | 18.0908 | 17.9764 | -104.7089 | 18.0725 | 18.0862 | 0.10986 | -104.9286 | -0.050354 | -0.13733 | -113.7314 | -0.21515 | -0.33417 | -0.19684 | -113.649 | 18.2648 | 18.045 | 17.9993 | -104.9973 | 9.2422 | 9.3246 | -0.16937 | -123.111
722.8438 | 123.0606 | -18.0267 | 104.9835 | -3.8454 | 0.13697 | 0.13331 | 0.056883 | 0.1156 | 0.0011837 | 0.044107 | -0.56354 | 0.19662 | 0.0021631 | 0.1913 | 0.016085 | -0.023383 | -0.041199 | -0.009155 | -0.082397 | 0.018311 | 0.19226 | 0.022888 | -0.12817 | -18.2327 | -18.1915 | -18.3426 | -8.8394 | -8.7662 | -18.0725 | -18.132 | 18.0496 | 17.8986 | -104.7913 | 18.0176 | 18.045 | 0.14649 | -105.0247 | -0.045777 | -0.10529 | -113.8229 | -0.20599 | -0.31586 | -0.21057 | -113.7497 | 18.219 | 17.9855 | 17.9443 | -105.1117 | 9.1873 | 9.2606 | -0.1648 | -123.1155
723.8438 | 123.0423 | -17.9031 | 105.0751 | -3.174 | 0.13056 | 0.13224 | 0.056883 | 0.1156 | 0.0075917 | 0.033426 | -0.42621 | 0.20943 | 0.012844 | 0.19664 | 0.015017 | -0.022315 | -0.054932 | 0.013733 | -0.07782 | 0.004578 | 0.17395 | 0 | -0.12817 | -18.1229 | -18.0679 | -18.2465 | -8.844 | -8.7616 | -17.9352 | -18.0313 | 17.9031 | 17.775 | -104.9011 | 17.9169 | 17.9077 | 0.13275 | -105.13 | -0.032044 | -0.12817 | -113.9191 | -0.21973 | -0.34332 | -0.21515 | -113.8367 | 18.0771 | 17.8482 | 17.8253 | -105.2032 | 9.0591 | 9.1415 | -0.16479 | -123.1064
724.8438 | 123.024 | -17.6605 | 105.3635 | 0.16763 | 0.16581 | 0.14292 | 0.080381 | 0.12521 | 0.016137 | 0.047311 | -0.01422 | 0.20837 | 0.0032311 | 0.18169 | 0.015017 | -0.016975 | -0.036621 | -0.036621 | -0.09613 | -0.022888 | 0.12817 | -0.050354 | -0.16937 | -17.8665 | -17.8986 | -18.0222 | -8.844 | -8.757 | -17.7063 | -17.7933 | 17.6102 | 17.4911 | -105.2353 | 17.6239 | 17.6376 | 0.14649 | -105.4001 | -0.045777 | -0.13275 | -114.2075 | -0.20599 | -0.36163 | -0.22888 | -114.1205 | 17.7887 | 17.6239 | 17.5644 | -105.5328 | 8.8165 | 8.9035 | -0.23804 | -123.1567
725.8438 | 123.0423 | -17.3813 | 105.6198 | -0.045996 | 0.14338 | 0.14506 | 0.072904 | 0.12521 | -0.0041573 | 0.043039 | -0.39569 | 0.19128 | 0.0042991 | 0.18169 | 0.0064719 | -0.019111 | -0.036621 | -0.018311 | -0.059509 | -0.032043 | 0.13733 | -0.032043 | -0.14648 | -17.5873 | -17.5369 | -17.7017 | -8.844 | -8.7662 | -17.4362 | -17.5003 | 17.3492 | 17.2348 | -105.4825 | 17.363 | 17.3492 | 0.11444 | -105.6564 | -0.054931 | -0.11902 | -114.4638 | -0.20599 | -0.32043 | -0.20142 | -114.386 | 17.5186 | 17.3447 | 17.3218 | -105.7663 | 8.5373 | 8.6151 | -0.15564 | -123.1201
726.8438 | 123.1201 | -16.9052 | 106.0501 | -0.2291 | 0.16367 | 0.14826 | 0.064359 | 0.1156 | 0.010797 | 0.057993 | -0.41095 | 0.19662 | -0.0063819 | 0.19771 | 0.013948 | -0.027656 | -0.041199 | -0.004578 | -0.068665 | 0.004578 | 0.13733 | -0.013733 | -0.16479 | -17.1066 | -17.0517 | -17.2119 | -8.8486 | -8.7662 | -16.9739 | -17.0609 | 16.8915 | 16.7404 | -105.9128 | 16.9006 | 16.9098 | 0.16937 | -106.0913 | -0.068665 | -0.15564 | -114.8987 | -0.20142 | -0.3067 | -0.15106 | -114.8163 | 17.0425 | 16.864 | 16.8365 | -106.2149 | 8.0566 | 8.139 | -0.14649 | -123.111
727.8438 | 123.1064 | -16.8365 | 106.1737 | -0.15281 | 0.14552 | 0.14826 | 0.067564 | 0.12842 | 0.0065237 | 0.047311 | -0.47198 | 0.19769 | 0.0053671 | 0.18489 | 0.018221 | -0.02552 | -0.027466 | -0.004578 | -0.068665 | 0.013733 | 0.13733 | -0.004578 | -0.16022 | -17.0059 | -16.951 | -17.1021 | -8.844 | -8.757 | -16.8961 | -16.951 | 16.832 | 16.6763 | -106.0364 | 16.832 | 16.8503 | 0.17395 | -106.2012 | -0.059509 | -0.11444 | -115.0177 | -0.16937 | -0.2655 | -0.15106 | -114.9307 | 16.9739 | 16.8091 | 16.7679 | -106.3339 | 7.9926 | 8.0795 | -0.11444 | -123.1247
728.8438 | 123.0743 | -16.4795 | 106.4941 | -0.15281 | 0.14979 | 0.15253 | 0.062223 | 0.13055 | 0.0075917 | 0.04838 | -0.42621 | 0.19875 | 0.012844 | 0.19451 | 0.020357 | -0.023383 | -0.045776 | -0.009155 | -0.07782 | -0.004578 | 0.13275 | -0.009155 | -0.17395 | -16.6534 | -16.5894 | -16.7633 | -8.844 | -8.7662 | -16.5161 | -16.5985 | 16.4703 | 16.3055 | -106.3614 | 16.4703 | 16.4749 | 0.16937 | -106.5399 | -0.036621 | -0.11902 | -115.3381 | -0.17395 | -0.28381 | -0.1648 | -115.2603 | 16.6122 | 16.4337 | 16.4017 | -106.6681 | 7.6355 | 7.7133 | -0.10986 | -123.0927
729.8438 | 123.0927 | -16.3422 | 106.6681 | -0.15281 | 0.14338 | 0.14612 | 0.068632 | 0.1188 | 0.0054557 | 0.038766 | -0.41095 | 0.19982 | 0.0053671 | 0.18917 | 0.011812 | -0.026588 | -0.022888 | -0.013733 | -0.086975 | 0.004578 | 0.1236 | -0.018311 | -0.17395 | -16.4978 | -16.4337 | -16.6031 | -8.844 | -8.7616 | -16.333 | -16.4108 | 16.3239 | 16.1682 | -106.5445 | 16.3284 | 16.3467 | 0.17853 | -106.691 | 0.009155 | -0.068665 | -115.5121 | -0.15564 | -0.26093 | -0.19226 | -115.4297 | 16.4658 | 16.3193 | 16.2552 | -106.842 | 7.4982 | 7.5806 | -0.091553 | -123.0789
730.8438 | 123.0789 | -16.3605 | 106.6086 | -0.2291 | 0.17115 | 0.1504 | 0.073972 | 0.12735 | 0.0054557 | 0.039835 | -0.33466 | 0.19555 | 0.0053671 | 0.17955 | 0.0064719 | -0.016975 | -0.036621 | -0.013733 | -0.082397 | -0.009155 | 0.12817 | -0.018311 | -0.16022 | -16.5665 | -16.4841 | -16.6626 | -8.8394 | -8.7524 | -16.3879 | -16.4795 | 16.3422 | 16.2003 | -106.4804 | 16.3467 | 16.3513 | 0.15106 | -106.6452 | -0.027465 | -0.11902 | -115.448 | -0.20599 | -0.30212 | -0.18311 | -115.361 | 16.4886 | 16.3239 | 16.2781 | -106.7688 | 7.5211 | 7.608 | -0.1236 | -123.0881
731.8438 | 123.0377 | -16.2506 | 106.7642 | -0.24436 | 0.14124 | 0.14292 | 0.0697 | 0.13696 | -0.011634 | 0.051584 | -0.34991 | 0.20089 | -0.0021099 | 0.1881 | 0.0032669 | -0.019111 | -0.054932 | -0.004578 | -0.07782 | -0.022888 | 0.15106 | -0.027466 | -0.16022 | -16.4749 | -16.1636 | -16.4795 | -8.8394 | -8.7616 | -16.3055 | -16.3605 | 16.2231 | 16.0904 | -106.6132 | 16.246 | 16.2277 | 0.13733 | -106.8192 | -0.054932 | -0.10986 | -115.6036 | -0.2243 | -0.22888 | -0.11902 | -115.5258 | 16.4017 | 16.1957 | 16.1728 | -106.9244 | 7.4112 | 7.489 | 0.086975 | -123.1247
732.8438 | 123.1064 | -15.7837 | 107.2403 | -0.24436 | 0.1327 | 0.15253 | 0.078245 | 0.13055 | -0.0073613 | 0.024881 | -0.41095 | 0.19341 | 0.0032311 | 0.1678 | 0.0086079 | -0.024451 | -0.064087 | 0.009155 | -0.091553 | -0.022888 | 0.16022 | -0.022888 | -0.14191 | -15.9943 | -15.9348 | -16.1041 | -8.844 | -8.7708 | -15.834 | -15.9164 | 15.7608 | 15.6418 | -107.0801 | 15.7928 | 15.7608 | 0.11902 | -107.3044 | -0.050354 | -0.13275 | -116.0843 | -0.21057 | -0.32044 | -0.18768 | -116.011 | 15.9439 | 15.7196 | 15.6921 | -107.3822 | 6.9397 | 7.0129 | -0.15106 | -123.1567
733.8438 | 123.0972 | -15.7013 | 107.2815 | -0.2291 | 0.17222 | 0.14826 | 0.083585 | 0.11346 | 0.014001 | 0.04838 | -0.41095 | 0.19234 | -0.0031779 | 0.17101 | 0.0064719 | -0.028724 | -0.018311 | -0.004578 | -0.068665 | 0 | 0.1236 | -0.018311 | -0.15564 | -15.8707 | -15.8203 | -15.976 | -8.844 | -8.7616 | -15.7516 | -15.8295 | 15.683 | 15.5457 | -107.1579 | 15.6967 | 15.7013 | 0.15564 | -107.2998 | -0.050354 | -0.12817 | -116.1255 | -0.16937 | -0.27466 | -0.14648 | -116.0431 | 15.8249 | 15.683 | 15.6326 | -107.4371 | 6.8573 | 6.9397 | -0.11902 | -123.111
734.8438 | 123.1018 | -15.6876 | 107.3273 | -0.18333 | 0.14979 | 0.14292 | 0.055814 | 0.10919 | 0.015069 | 0.046243 | -0.38043 | 0.19662 | -0.0053139 | 0.1881 | 0.016085 | -0.027656 | -0.041199 | -0.009155 | -0.07782 | 0.004578 | 0.11902 | -0.018311 | -0.16022 | -15.834 | -15.7745 | -15.9393 | -8.844 | -8.7662 | -15.7013 | -15.8066 | 15.6692 | 15.5273 | -107.2083 | 15.6784 | 15.6921 | 0.16479 | -107.3685 | -0.013733 | -0.11902 | -116.1713 | -0.14648 | -0.25177 | -0.13275 | -116.0934 | 15.8066 | 15.6464 | 15.6097 | -107.4875 | 6.8436 | 6.9214 | -0.086975 | -123.1339
735.8438 | 123.1018 | -15.5548 | 107.4646 | -0.18333 | 0.15726 | 0.12583 | 0.08679 | 0.11133 | 0.012933 | 0.040903 | -0.34991 | 0.19555 | 0.016048 | 0.19664 | 0.0086079 | -0.037269 | -0.041199 | -0.022888 | -0.086975 | 0.009155 | 0.14191 | -0.013733 | -0.16479 | -15.7288 | -15.6555 | -15.8386 | -8.8486 | -8.7524 | -15.5823 | -15.6647 | 15.5411 | 15.39 | -107.3227 | 15.5319 | 15.564 | 0.17395 | -107.5058 | -0.027465 | -0.10986 | -116.3132 | -0.17395 | -0.28381 | -0.17395 | -116.217 | 15.6967 | 15.5136 | 15.4678 | -107.6294 | 6.7062 | 6.8024 | -0.10071 | -123.1293
736.8438 | 123.0743 | -15.4724 | 107.5607 | -0.3054 | 0.16261 | 0.13972 | 0.061155 | 0.1156 | 0.0011837 | 0.037698 | -0.39569 | 0.18914 | -0.0031779 | 0.19024 | 0.025698 | -0.014838 | -0.032043 | -0.032043 | -0.082397 | -0.004578 | 0.12817 | -0.036621 | -0.15564 | -15.6372 | -15.5777 | -15.7471 | -8.8486 | -8.7662 | -15.4907 | -15.5777 | 15.4358 | 15.3168 | -107.4326 | 15.4404 | 15.4678 | 0.15106 | -107.5928 | -0.018311 | -0.10529 | -116.4093 | -0.16479 | -0.27466 | -0.16937 | -116.3269 | 15.6006 | 15.4404 | 15.39 | -107.7164 | 6.6238 | 6.7062 | -0.10529 | -123.1384
737.8438 | 123.0743 | -15.1474 | 107.8949 | 0.7322 | 0.15299 | 0.15146 | 0.078245 | 0.10492 | 0.010797 | 0.035562 | -0.30414 | 0.20196 | -0.0063819 | 0.19558 | 0.0011309 | -0.0052251 | -0.050354 | -0.018311 | -0.086975 | -0.009155 | 0.16479 | -0.018311 | -0.13733 | -15.3122 | -15.2527 | -15.4312 | -8.8486 | -8.7616 | -15.184 | -15.2527 | 15.1291 | 15.0101 | -107.7301 | 15.1291 | 15.1382 | 0.12817 | -107.9453 | -0.036621 | -0.10529 | -116.7435 | -0.16479 | -0.28381 | -0.17853 | -116.6565 | 15.3122 | 15.097 | 15.0604 | -108.0322 | 6.2988 | 6.3858 | -0.10529 | -123.1476
738.8438 | 123.0469 | -14.9918 | 108.0276 | -0.29014 | 0.13804 | 0.15253 | 0.055814 | 0.11667 | -0.0084293 | 0.021677 | -0.38043 | 0.19448 | 0.0096401 | 0.18276 | 0.0075399 | -0.0094981 | -0.032043 | 0.018311 | -0.059509 | 0.032043 | 0.14648 | -0.027466 | -0.13733 | -15.1886 | -15.1245 | -15.2847 | -8.8394 | -8.7616 | -15.0558 | -15.1199 | 14.9643 | 14.8544 | -107.8812 | 15.0101 | 15.0238 | 0.16937 | -108.0597 | -0.064087 | -0.12817 | -116.8671 | -0.19684 | -0.29297 | -0.16479 | -116.7892 | 15.1382 | 14.9597 | 14.9323 | -108.165 | 6.1523 | 6.2302 | -0.13275 | -123.1476
739.8438 | 123.0331 | -14.8315 | 108.2199 | -0.25962 | 0.14872 | 0.1504 | 0.068632 | 0.10919 | -0.0041573 | 0.029153 | -0.38043 | 0.19448 | 0.020321 | 0.17849 | 0.016085 | -0.015907 | -0.064087 | -0.022888 | -0.086975 | -0.009155 | 0.15564 | -0.018311 | -0.15564 | -15.0467 | -14.9414 | -15.0879 | -8.844 | -8.7616 | -14.8361 | -14.9185 | 14.8132 | 14.6759 | -108.0643 | 14.8087 | 14.8224 | 0.14649 | -108.284 | -0.004578 | -0.086975 | -117.0639 | -0.21515 | -0.25635 | -0.16937 | -116.9815 | 14.9872 | 14.7675 | 14.7446 | -108.3756 | 5.9875 | 6.0699 | -0.10986 | -123.1384
740.8438 | 123.1064 | -14.5615 | 108.4579 | 0.030298 | 0.16795 | 0.15574 | 0.066496 | 0.12842 | 0.014001 | 0.030222 | -0.39569 | 0.20089 | 2.7137e-05 | 0.18169 | 0.011812 | -0.022315 | -0.032043 | -0.018311 | -0.082397 | 0 | 0.14191 | -0.018311 | -0.15564 | -14.7125 | -14.6622 | -14.827 | -8.844 | -8.7616 | -14.5752 | -14.6622 | 14.5432 | 14.4058 | -108.316 | 14.5432 | 14.5615 | 0.15564 | -108.49 | -0.013733 | -0.10071 | -117.3019 | -0.15106 | -0.2655 | -0.16479 | -117.2195 | 14.7034 | 14.5294 | 14.4791 | -108.6136 | 5.7175 | 5.7999 | -0.10071 | -123.1201
741.8438 | 123.0652 | -14.1724 | 108.8654 | -3.174 | 0.14658 | 0.14719 | 0.05261 | 0.10385 | 0.0075917 | 0.034494 | -0.38043 | 0.19341 | 0.0075041 | 0.18917 | 0.018221 | -0.019111 | -0.054932 | -0.004578 | -0.07782 | -0.004578 | 0.18768 | -0.013733 | -0.14191 | -14.3234 | -14.2639 | -14.4333 | -8.844 | -8.7662 | -14.209 | -14.2731 | 14.1586 | 14.0305 | -108.6777 | 14.1678 | 14.1678 | 0.13733 | -108.9203 | -0.036621 | -0.10071 | -117.7094 | -0.15106 | -0.26093 | -0.16022 | -117.6315 | 14.36 | 14.1174 | 14.0945 | -109.0073 | 5.3284 | 5.4062 | -0.091553 | -123.1384
742.8438 | 123.0469 | -13.9481 | 109.0622 | -0.33591 | 0.14872 | 0.16215 | 0.0697 | 0.11987 | 0.0011837 | 0.045175 | -0.27362 | 0.19769 | 0.0096401 | 0.1881 | 0.0054039 | -0.022315 | -0.045776 | -0.018311 | 0.11444 | 0.15106 | 0.15564 | 0.009155 | -0.10071 | -14.1266 | -14.0533 | -14.2227 | -8.8394 | -8.7616 | -13.9847 | -14.0442 | 13.9572 | 13.8474 | -108.9066 | 13.9297 | 14.0991 | 0.25177 | -109.108 | -0.036621 | -0.09613 | -117.9016 | -0.17853 | -0.27466 | -0.17853 | -117.8238 | 14.1037 | 13.9023 | 14.0625 | -109.1629 | 5.1086 | 5.1865 | -0.10529 | -123.1064
743.8438 | 123.0789 | -13.797 | 109.2728 | -0.29014 | 0.1327 | 0.14185 | 0.080381 | 0.11453 | 0.0011837 | 0.043039 | -0.42621 | 0.20303 | -0.011723 | 0.18276 | 0.0086079 | -0.029792 | -0.045776 | -0.022888 | -0.082397 | -0.004578 | 0.14648 | -0.018311 | -0.16479 | -13.9114 | -13.6734 | -14.1495 | -8.844 | -8.7524 | -13.8016 | -13.8931 | 13.7787 | 13.6322 | -109.1263 | 13.7741 | 13.7924 | 0.16022 | -109.3185 | -0.004578 | -0.09613 | -118.1168 | -0.11444 | -0.35248 | -0.25635 | -118.0252 | 13.9435 | 13.7512 | 13.7146 | -109.4376 | 4.953 | 5.0446 | 0.1236 | -123.1659
744.8438 | 123.0606 | -13.4445 | 109.584 | 0.25918 | 0.14658 | 0.14506 | 0.066496 | 0.1188 | 0.0054557 | 0.03663 | -0.30414 | 0.20196 | -0.0010409 | 0.19985 | 0.01288 | -0.022315 | -0.050354 | -0.009155 | -0.054932 | -0.018311 | 0.15564 | -0.022888 | -0.15106 | -13.5956 | -13.5361 | -13.71 | -8.8486 | -8.7616 | -13.4537 | -13.5544 | 13.4216 | 13.2935 | -109.4284 | 13.4354 | 13.4262 | 0.13275 | -109.6344 | -0.009155 | -0.10986 | -118.4326 | -0.15106 | -0.2655 | -0.15564 | -118.3456 | 13.6002 | 13.3942 | 13.3896 | -109.7351 | 4.5959 | 4.6829 | -0.091553 | -123.1384
745.8438 | 123.0972 | -13.3209 | 109.6893 | -0.15281 | 0.14124 | 0.1536 | 0.070768 | 0.11239 | -0.0062933 | 0.038766 | -0.41095 | 0.1838 | -0.0042459 | 0.17421 | 0.0086079 | -0.018043 | 0.036621 | 0.10071 | 0.027466 | 0.068665 | 0.11444 | 0.009155 | -0.10986 | -13.4125 | -13.3392 | -13.5086 | -8.8486 | -8.7662 | -13.3209 | -13.4171 | 13.3301 | 13.2111 | -109.5749 | 13.4216 | 13.3896 | 0.17853 | -109.6527 | 0 | -0.09613 | -118.5379 | -0.091553 | -0.18768 | -0.091553 | -118.4555 | 13.4354 | 13.3575 | 13.3484 | -109.7992 | 4.4724 | 4.5547 | -0.01831 | -123.1064
746.8438 | 123.0515 | -13.0737 | 109.9319 | -0.25962 | 0.14338 | 0.15681 | 0.070768 | 0.11667 | -0.0094983 | 0.027017 | -0.36517 | 0.18594 | -0.0010409 | 0.17849 | 0.013948 | -0.03086 | 0 | 0.045776 | -0.022888 | 0.041199 | 0.14648 | -0.027466 | -0.13275 | -13.1927 | -13.1882 | -13.3392 | -8.8394 | -8.7616 | -13.0966 | -13.1973 | 13.0463 | 12.941 | -109.7855 | 13.1195 | 13.1149 | 0.17395 | -109.9319 | -0.022889 | -0.1236 | -118.7714 | -0.11902 | -0.2655 | -0.14191 | -118.6935 | 13.2202 | 13.0737 | 13.0508 | -110.0647 | 4.2343 | 4.3121 | -0.11444 | -123.1293
747.8438 | 122.9874 | -13.0371 | 109.9823 | -0.16807 | 0.14979 | 0.14399 | 0.063291 | 0.1156 | 0.0065237 | 0.032358 | -0.54828 | 0.19448 | -0.0021099 | 0.18383 | 0.011812 | -0.020179 | -0.050354 | 0.004578 | -0.07782 | -0.027466 | 0.16022 | -0.018311 | -0.16479 | -13.2111 | -13.1561 | -13.3484 | -8.8531 | -8.7616 | -13.0966 | -13.1744 | 13.0188 | 12.8723 | -109.8221 | 13.0417 | 13.0096 | 0.13733 | -110.0327 | -0.05951 | -0.13733 | -118.8354 | -0.17395 | -0.31128 | -0.17395 | -118.7439 | 13.1973 | 12.9868 | 12.9593 | -110.1471 | 4.184 | 4.2755 | -0.11902 | -123.1567
748.8438 | 123.0698 | -12.7853 | 110.2936 | -0.2291 | 0.13911 | 0.14933 | 0.060087 | 0.11346 | -0.0052253 | 0.032358 | -0.41095 | 0.20943 | 0.0010951 | 0.17635 | 0.0075399 | -0.018043 | -0.004578 | -0.027466 | -0.064087 | -0.004578 | 0.16479 | -0.009155 | -0.15106 | -12.9089 | -12.8586 | -13.0234 | -8.8394 | -8.7616 | -12.7899 | -12.886 | 12.7762 | 12.6343 | -110.1288 | 12.7579 | 12.7808 | 0.14648 | -110.2982 | -0.004578 | -0.10071 | -119.133 | -0.1236 | -0.23804 | -0.13733 | -119.0552 | 12.9501 | 12.7808 | 12.7213 | -110.4446 | 3.9459 | 4.0237 | -0.073243 | -123.1796
749.8438 | 123.0927 | -12.4237 | 110.6232 | -0.3054 | 0.12308 | 0.16428 | 0.064359 | 0.12414 | 0.0022517 | 0.027017 | -0.12103 | 0.187 | -0.025608 | 0.18062 | 0.016085 | -0.024451 | -0.004578 | 0.050354 | -0.018311 | 0.018311 | 0.15106 | 0.009155 | -0.11444 | -12.5565 | -12.4649 | -12.6617 | -8.8303 | -8.7479 | -12.4558 | -12.5244 | 12.4329 | 12.3093 | -110.4721 | 12.4741 | 12.442 | 0.13275 | -110.6277 | -0.032044 | -0.10071 | -119.4534 | -0.13275 | -0.23804 | -0.13733 | -119.371 | 12.5748 | 12.4191 | 12.4054 | -110.7376 | 3.5934 | 3.6758 | -0.041199 | -123.1476
750.8438 | 123.0927 | -12.1811 | 110.8429 | -0.27488 | 0.12736 | 0.13331 | 0.056883 | 0.12414 | -0.0030893 | 0.032358 | -0.41095 | 0.19448 | 0.0085721 | 0.17849 | 0.0054039 | -0.023383 | 0.032043 | 0.073242 | -0.009155 | 0.064087 | 0.12817 | 0 | -0.12817 | -12.2955 | -12.2177 | -12.3962 | -8.8257 | -8.757 | -12.204 | -12.2635 | 12.1811 | 12.0529 | -110.7147 | 12.2543 | 12.2452 | 0.19226 | -110.8109 | -0.022888 | -0.082398 | -119.6686 | -0.11444 | -0.21515 | -0.13275 | -119.5999 | 12.3093 | 12.2131 | 12.1719 | -110.9711 | 3.3554 | 3.4241 | -0.036621 | -123.1064
751.8438 | 123.0743 | -11.9064 | 111.1404 | -0.15281 | 0.1562 | 0.14826 | 0.068632 | 0.11346 | -0.0052253 | 0.041971 | -0.3194 | 0.19982 | 0.0075041 | 0.1913 | 0.010744 | -0.027656 | -0.036621 | -0.009155 | -0.086975 | 0 | 0.13733 | -0.013733 | -0.14191 | -12.0392 | -11.9797 | -12.1674 | -8.8074 | -8.7387 | -11.9522 | -12.0255 | 11.8927 | 11.7645 | -111.0031 | 11.8973 | 11.9064 | 0.14191 | -111.1771 | -0.045776 | -0.11902 | -119.9478 | -0.13275 | -0.26093 | -0.14191 | -119.8791 | 12.0438 | 11.8698 | 11.8195 | -111.2823 | 3.0991 | 3.1677 | -0.073242 | -123.1659
752.8438 | 123.2117 | -11.499 | 111.4517 | -0.19858 | 0.13377 | 0.14719 | 0.065427 | 0.11987 | -0.0094983 | 0.043039 | 4.3956 | 0.19982 | -0.0053139 | 0.18062 | 0.01288 | -0.03086 | 0.054932 | 0.13733 | 0.059509 | 0.064087 | 0.10986 | 0.009155 | -0.10986 | -11.5219 | -11.5173 | -11.673 | -8.7891 | -8.725 | -11.5677 | -11.6272 | 11.5082 | 11.3892 | -111.3419 | 11.6364 | 11.5631 | 0.17395 | -111.3968 | -0.068665 | -0.12817 | -120.2408 | -0.022889 | -0.17395 | -0.045777 | -120.1767 | 11.6089 | 11.554 | 11.5585 | -111.5616 | 2.71 | 2.774 | -0.018311 | -123.0789
753.8438 | 123.1476 | -11.3113 | 111.6531 | -0.39695 | 0.1327 | 0.14399 | 0.056883 | 0.12414 | 0.0022517 | 0.032358 | -0.3194 | 0.18594 | -0.0063819 | 0.18276 | 0.0096759 | -0.027656 | 0.050354 | 0.11902 | 0.050354 | 0.082397 | 0.11444 | 0.027466 | -0.09613 | -11.3892 | -11.2839 | -11.4853 | -8.7891 | -8.7112 | -11.3434 | -11.4258 | 11.3388 | 11.2152 | -111.5387 | 11.4304 | 11.3937 | 0.17853 | -111.6028 | -0.032044 | -0.11444 | -120.4422 | -0.07782 | -0.17395 | -0.05951 | -120.3644 | 11.4258 | 11.3617 | 11.3617 | -111.7493 | 2.5223 | 2.6001 | 0.027465 | -123.0789
754.8438 | 123.111 | -11.0687 | 111.9644 | -0.21384 | 0.13911 | 0.1536 | 0.060087 | 0.11774 | 0.0065237 | 0.03663 | -0.44147 | 0.1838 | -0.0021099 | 0.19237 | 0.013948 | -0.03086 | 0.027466 | 0.09613 | 0.004578 | 0.054932 | 0.1236 | 0.009155 | -0.11444 | -11.1328 | -11.0779 | -11.261 | -8.7616 | -8.6975 | -11.0962 | -11.174 | 11.0779 | 10.9543 | -111.8408 | 11.1649 | 11.1237 | 0.16937 | -111.937 | -0.027465 | -0.10529 | -120.726 | -0.064086 | -0.19226 | -0.086975 | -120.6619 | 11.1923 | 11.0962 | 11.0733 | -112.0789 | 2.3071 | 2.3712 | -0.009155 | -123.1384
755.8438 | 123.1293 | -10.7758 | 112.2253 | -0.25962 | 0.14017 | 0.14719 | 0.066496 | 0.12628 | -0.0041573 | 0.039835 | -0.45673 | 0.18487 | 0.0021631 | 0.19771 | 0.0086079 | -0.024451 | 0.050354 | 0.11902 | 0.027466 | 0.068665 | 0.11902 | 0 | -0.1236 | -10.8582 | -10.7712 | -10.9589 | -8.7296 | -8.67 | -10.8124 | -10.9085 | 10.7758 | 10.6522 | -112.1063 | 10.8948 | 10.8444 | 0.19226 | -112.175 | -0.036621 | -0.13275 | -120.9549 | -0.082397 | -0.1831 | -0.050354 | -120.8954 | 10.8948 | 10.8261 | 10.8032 | -112.3489 | 2.0462 | 2.1057 | 0.004578 | -123.1338
756.8438 | 123.1522 | -10.5103 | 112.4863 | -0.21384 | 0.12308 | 0.15467 | 0.070768 | 0.11453 | -0.0030893 | 0.032358 | -0.45673 | 0.18166 | -0.0085179 | 0.18169 | 0.015017 | -0.023383 | 0.054932 | 0.12817 | 0.045776 | 0.068665 | 0.11444 | 0.013733 | -0.11902 | -10.5652 | -10.4691 | -10.6888 | -8.7067 | -8.638 | -10.5377 | -10.6247 | 10.524 | 10.3912 | -112.3718 | 10.6384 | 10.5789 | 0.18768 | -112.4313 | -0.027466 | -0.11444 | -121.1929 | -0.054932 | -0.17853 | -0.064087 | -121.1243 | 10.6247 | 10.5652 | 10.556 | -112.6053 | 1.8036 | 1.8723 | 0.041199 | -123.111
757.8438 | 123.1705 | -10.3226 | 112.6923 | -0.15281 | 0.13163 | 0.14612 | 0.061155 | 0.11239 | 0.0043877 | 0.03663 | -0.30414 | 0.18594 | -0.0010409 | 0.18383 | 0.0064719 | -0.024451 | 0.054932 | 0.14191 | 0.059509 | 0.07782 | 0.11902 | 0.018311 | -0.10529 | -10.3363 | -10.2722 | -10.4691 | -8.67 | -8.6197 | -10.3546 | -10.4324 | 10.3409 | 10.2173 | -112.5732 | 10.4645 | 10.4004 | 0.18311 | -112.6373 | -0.032043 | -0.10986 | -121.3623 | -0.013733 | -0.14648 | -0.036621 | -121.312 | 10.4416 | 10.3775 | 10.3821 | -112.7975 | 1.6525 | 1.7029 | 0.050354 | -123.1247
758.8438 | 123.1659 | -10.1212 | 112.8937 | 0.25918 | 0.13056 | 0.15467 | 0.063291 | 0.11453 | 0.0054557 | 0.037698 | -0.33466 | 0.18807 | -0.011723 | 0.17849 | 0.0086079 | -0.018043 | 0.027466 | 0.13733 | 0.059509 | 0.086975 | 0.1236 | 0 | -0.10529 | -10.1349 | -10.0479 | -10.2448 | -8.638 | -8.5922 | -10.1349 | -10.2219 | 10.1212 | 10.0159 | -112.7701 | 10.2585 | 10.2081 | 0.19226 | -112.8662 | -0.013733 | -0.10071 | -121.5317 | -0.013733 | -0.1236 | -0.022888 | -121.4859 | 10.2448 | 10.1486 | 10.1807 | -112.999 | 1.4832 | 1.5289 | 0.073242 | -123.1155
759.8438 | 123.2162 | -9.8831 | 113.1592 | 0.091333 | 0.12949 | 0.14826 | 0.059019 | 0.10705 | -0.0084293 | 0.028085 | -0.59405 | 0.1838 | -0.0063819 | 0.17635 | 0.0011309 | -0.026588 | 0.073242 | 0.17395 | 0.064087 | 0.068665 | 0.14191 | 0.032043 | -0.091553 | -9.8511 | -9.7916 | -9.9609 | -8.5876 | -8.5373 | -9.8785 | -9.9884 | 9.9152 | 9.7916 | -113.0173 | 10.0571 | 9.9518 | 0.16022 | -113.0859 | 0.004578 | -0.10529 | -121.7468 | 0.032044 | -0.077819 | 0.027466 | -121.6965 | 10.025 | 9.9564 | 9.9472 | -113.2507 | 1.2955 | 1.3458 | 0.091553 | -123.1476
760.8438 | 123.2208 | -9.6909 | 113.2645 | -0.15281 | 0.12415 | 0.14185 | 0.07504 | 0.1188 | -0.00095325 | 0.032358 | -3.9662 | 0.17953 | 0.0042991 | 0.18383 | 0.011812 | -0.023383 | 0.07782 | 0.14648 | 0.064087 | 0.07782 | 0.091553 | 0.004578 | -0.10071 | -9.7412 | -9.6085 | -9.8557 | -8.5419 | -8.5052 | -9.7458 | -9.8465 | 9.6954 | 9.5901 | -113.1729 | 9.8373 | 9.7687 | 0.17853 | -113.1866 | -0.054932 | -0.15564 | -121.8063 | -0.050354 | -0.16479 | -0.009155 | -121.7697 | 9.7824 | 9.7687 | 9.7549 | -113.3652 | 1.149 | 1.1856 | 0.082398 | -123.111
761.8438 | 123.143 | -9.668 | 113.3286 | -0.3054 | 0.13483 | 0.16215 | 0.057951 | 0.10278 | 0.0054557 | 0.03129 | -0.39569 | 0.19982 | -0.0074499 | 0.17528 | 0.0086079 | -0.032996 | 0.068665 | 0.14191 | 0.045776 | 0.073242 | 0.10986 | 0.004578 | -0.10071 | -9.6817 | -9.6085 | -9.8053 | -8.5373 | -8.4869 | -9.7 | -9.7778 | 9.6725 | 9.5673 | -113.2187 | 9.8099 | 9.7412 | 0.17395 | -113.2599 | -0.032043 | -0.10986 | -121.8658 | -0.013733 | -0.13733 | -0.027466 | -121.8155 | 9.7778 | 9.7366 | 9.7137 | -113.4293 | 1.1307 | 1.181 | 0.05951 | -123.1064
762.8438 | 123.2117 | -9.6725 | 113.3286 | 1.0984 | 0.12629 | 0.1536 | 0.071836 | 0.12521 | 0.0011837 | 0.038766 | -0.3194 | 0.18914 | -0.0095859 | 0.17101 | 0.0064719 | -0.027656 | 0.068665 | 0.16479 | 0.064087 | 0.07782 | 0.10071 | 0.027466 | -0.11902 | -9.6909 | -9.6039 | -9.8007 | -8.5373 | -8.4961 | -9.7046 | -9.7961 | 9.7 | 9.5535 | -113.2278 | 9.8373 | 9.7504 | 0.19684 | -113.2599 | -0.032044 | -0.1236 | -121.8658 | -0.018311 | -0.12817 | -0.004577 | -121.8246 | 9.7733 | 9.7412 | 9.7366 | -113.4476 | 1.1353 | 1.1765 | 0.068664 | -123.1247
763.8438 | 123.1934 | -9.4528 | 113.5437 | -0.13755 | 0.12095 | 0.16001 | 0.07504 | 0.1156 | 0.012933 | 0.035562 | -0.44147 | 0.19555 | 2.7137e-05 | 0.18276 | 0.013948 | -0.027656 | 0.10986 | 0.086975 | 0.045776 | 0.068665 | 0.10071 | 0.004578 | -0.11444 | -9.4574 | -9.3796 | -9.5627 | -8.4686 | -8.4366 | -9.5078 | -9.5627 | 9.4574 | 9.3384 | -113.443 | 9.5398 | 9.5215 | 0.18311 | -113.4338 | -0.054931 | -0.10986 | -122.0123 | -0.004577 | -0.10986 | 0 | -121.9803 | 9.5535 | 9.5627 | 9.4986 | -113.6581 | 0.98419 | 1.0162 | 0.073242 | -123.1064
764.8438 | 123.0972 | -9.2743 | 113.8138 | -0.25962 | 0.14872 | 0.15574 | 0.070768 | 0.11774 | 0.018273 | 0.038766 | -0.5025 | 0.19662 | 0.0010951 | 0.18383 | 0.018221 | -0.026588 | 0 | -0.009155 | -0.073242 | -0.009155 | 0.19684 | 0.022888 | -0.11902 | -9.3292 | -9.2743 | -9.4528 | -8.3496 | -8.3267 | -9.288 | -9.3475 | 9.2972 | 9.1553 | -113.6169 | 9.2651 | 9.2651 | 0.10986 | -113.8138 | -0.013733 | -0.073242 | -122.1634 | -0.054932 | -0.17853 | -0.10529 | -122.1405 | 9.4711 | 9.2743 | 9.2011 | -113.9328 | 0.92468 | 0.94757 | 0 | -123.1613
765.8438 | 123.2117 | -9.0454 | 113.9786 | -0.12229 | 0.13163 | 0.15574 | 0.068632 | 0.10705 | -0.0094983 | 0.039835 | -0.28888 | 0.20196 | -0.02454 | 0.17742 | 0.026766 | -0.024451 | 0.064087 | 0.15106 | 0.059509 | 0.059509 | 0.11444 | 0.009155 | -0.11444 | -9.0775 | -8.9218 | -9.1324 | -8.2855 | -8.2764 | -9.0637 | -9.1507 | 9.0546 | 8.931 | -113.8641 | 9.1965 | 9.1049 | 0.17395 | -113.9145 | -0.018311 | -0.10529 | -122.2641 | -0.032044 | -0.086975 | 0.018311 | -122.2549 | 9.1599 | 9.1095 | 9.1049 | -114.093 | 0.75989 | 0.76904 | 0.1236 | -123.1293
766.8438 | 123.2071 | -8.8486 | 114.1434 | 0.15237 | 0.11881 | 0.14612 | 0.060087 | 0.10278 | 0.0022517 | 0.034494 | -0.090514 | 0.19875 | 0.0096401 | 0.18062 | 0.0064719 | -0.021247 | 0.054932 | 0.12817 | 0.032043 | 0.064087 | 0.11902 | 0.018311 | -0.10986 | -8.844 | -8.7845 | -8.9401 | -8.1985 | -8.1985 | -8.8806 | -8.9767 | 8.8669 | 8.7387 | -114.0244 | 8.9767 | 8.9127 | 0.17395 | -114.0884 | -0.032043 | -0.12817 | -122.3419 | 0.004578 | -0.091553 | 0.036621 | -122.3419 | 8.9676 | 8.9035 | 8.8806 | -114.2532 | 0.65003 | 0.65003 | 0.064087 | -123.1201
767.8438 | 123.2025 | -8.6655 | 114.299 | 0.045557 | 0.13697 | 0.14185 | 0.062223 | 0.11667 | -0.0073613 | 0.033426 | -0.27362 | 0.19448 | -0.0042459 | 0.16674 | 0.017153 | -0.02552 | 0.082397 | 0.1831 | 0.073242 | 0.086975 | 0.13275 | 0.027466 | -0.086975 | -8.6426 | -8.6014 | -8.7616 | -8.107 | -8.1024 | -8.6838 | -8.7845 | 8.6929 | 8.5785 | -114.1663 | 8.8486 | 8.7524 | 0.17395 | -114.2166 | -0.018311 | -0.11902 | -122.406 | 0.022888 | -0.096131 | 0.022888 | -122.4014 | 8.7982 | 8.7479 | 8.7387 | -114.386 | 0.55847 | 0.56305 | 0.064087 | -123.0835
768.8438 | 123.2254 | -8.4549 | 114.537 | -0.091772 | 0.14124 | 0.1771 | 0.063291 | 0.11667 | 0.031091 | 0.028085 | -0.30414 | 0.18914 | -0.0010409 | 0.17528 | 0.0054039 | -0.029792 | 0.10529 | 0.082397 | 0.036621 | 0.082397 | 0.10071 | 0.013733 | -0.10529 | -8.4549 | -8.3771 | -8.5693 | -7.988 | -7.9926 | -8.4686 | -8.5785 | 8.4686 | 8.3496 | -114.4363 | 8.5373 | 8.5373 | 0.18768 | -114.4318 | -0.013733 | -0.1236 | -122.525 | 0 | -0.11444 | 0.009155 | -122.5296 | 8.5556 | 8.5602 | 8.4915 | -114.6423 | 0.46692 | 0.46234 | 0.07782 | -123.1155
769.8438 | 123.1338 | -8.3267 | 114.7247 | -0.19858 | 0.14445 | 0.14826 | 0.063291 | 0.1156 | 0.010797 | 0.041971 | -0.45673 | 0.18487 | -0.0085179 | 0.19344 | 0.019289 | -0.018043 | 0.050354 | 0.13275 | 0.027466 | 0.054932 | 0.11902 | 0.004578 | -0.11444 | -8.3359 | -8.2626 | -8.4595 | -7.869 | -7.8735 | -8.3496 | -8.4503 | 8.3313 | 8.2123 | -114.6057 | 8.4595 | 8.3817 | 0.16937 | -114.6744 | -0.022888 | -0.1236 | -122.5937 | -0.009155 | -0.13275 | -0.009156 | -122.5983 | 8.4457 | 8.3771 | 8.3542 | -114.8392 | 0.45776 | 0.45319 | 0.064087 | -123.175
770.8438 | 123.2208 | -8.107 | 114.8941 | -0.2291 | 0.1327 | 0.16108 | 0.053678 | 0.11453 | -0.0084293 | 0.033426 | -0.38043 | 0.16564 | -0.010654 | 0.18917 | 0.02463 | -0.026588 | 0.07782 | 0.15106 | 0.064087 | 0.064087 | 0.10986 | 0.032043 | -0.11902 | -8.075 | -8.0841 | -8.1802 | -7.7408 | -7.7683 | -8.1665 | -8.2352 | 8.139 | 7.988 | -114.7842 | 8.2581 | 8.1711 | 0.18311 | -114.8163 | -0.059509 | -0.12817 | -122.6349 | 0.032044 | -0.073242 | 0.054931 | -122.6624 | 8.2169 | 8.1848 | 8.1711 | -115.0131 | 0.36621 | 0.33874 | 0.022889 | -123.1293
771.8438 | 123.2574 | -8.0154 | 115.004 | -0.33591 | 0.12415 | 0.1536 | 0.048338 | 0.12628 | -0.011634 | 0.041971 | -0.27362 | 0.1838 | 0.0010951 | 0.1678 | 0.0064719 | -0.027656 | 0.091553 | 0.17395 | 0.054932 | 0.091553 | 0.10986 | 0.018311 | -0.11902 | -7.9514 | -7.8781 | -8.0841 | -7.6538 | -7.663 | -8.0475 | -8.1299 | 8.0338 | 7.8964 | -114.8941 | 8.1894 | 8.107 | 0.21057 | -114.9124 | -0.032043 | -0.11444 | -122.6578 | 0.064087 | -0.068664 | 0.045777 | -122.6669 | 8.1253 | 8.107 | 8.0704 | -115.123 | 0.36163 | 0.35248 | 0.13733 | -123.1338
772.8438 | 123.2254 | -7.8918 | 115.1093 | 0.015039 | 0.12736 | 0.14506 | 0.055814 | 0.13055 | -0.0052253 | 0.038766 | -0.090514 | 0.19448 | 0.0075041 | 0.17955 | 0.0096759 | -0.020179 | 0.050354 | 0.11902 | 0.045776 | 0.073242 | 0.1236 | 0.027466 | -0.091553 | -7.8644 | -7.8369 | -7.9651 | -7.5577 | -7.5851 | -7.933 | -8.0063 | 7.9193 | 7.8003 | -114.9857 | 8.0109 | 7.9651 | 0.16479 | -115.0589 | -0.041198 | -0.11444 | -122.6669 | 0.027466 | -0.073242 | 0.041199 | -122.6944 | 8.0154 | 7.9422 | 7.9376 | -115.2008 | 0.33417 | 0.3067 | 0.054932 | -123.1155
773.8438 | 123.2025 | -7.7637 | 115.274 | 0.045557 | 0.12843 | 0.14506 | 0.078245 | 0.13055 | 0.0065237 | 0.03663 | -0.059997 | 0.19662 | 0.0085721 | 0.18383 | 0.0096759 | -0.027656 | 0.045776 | 0.10529 | 0.027466 | 0.068665 | 0.11444 | 0.036621 | -0.09613 | -7.7179 | -7.6767 | -7.8278 | -7.4478 | -7.4615 | -7.7774 | -7.8735 | 7.8003 | 7.6675 | -115.1596 | 7.869 | 7.8323 | 0.16479 | -115.2283 | -0.013733 | -0.10986 | -122.7219 | 0.045776 | -0.064087 | 0.045776 | -122.7356 | 7.8781 | 7.8094 | 7.7911 | -115.3702 | 0.31586 | 0.30212 | 0.086975 | -123.1476
774.8438 | 123.2025 | -7.6447 | 115.3702 | -0.21384 | 0.12095 | 0.14506 | 0.063291 | 0.10705 | 0.012933 | 0.027017 | -0.56354 | 0.19555 | 2.7137e-05 | 0.18276 | 0.013948 | -0.015907 | 0.082397 | 0.14648 | 0.050354 | -0.036621 | 0.10529 | 0.018311 | -0.12817 | -7.6035 | -7.5485 | -7.7179 | -7.3608 | -7.3837 | -7.6767 | -7.7454 | 7.663 | 7.5165 | -115.2649 | 7.7911 | 7.608 | 0.091553 | -115.2878 | -0.032044 | -0.10071 | -122.731 | 0.041198 | -0.073243 | 0.027465 | -122.7539 | 7.7499 | 7.7271 | 7.695 | -115.4984 | 0.28381 | 0.26093 | 0.09613 | -123.1155
775.8438 | 123.2025 | -7.6996 | 115.3061 | -0.15281 | 0.12843 | 0.1504 | 0.067564 | 0.10705 | 0.0075917 | 0.032358 | -0.2431 | 0.20623 | -0.025608 | 0.18917 | 0.032106 | -0.024451 | 0.07782 | 0.15564 | 0.064087 | 0.086975 | 0.11444 | 0.009155 | -0.11444 | -7.695 | -7.6401 | -7.7683 | -7.3975 | -7.4295 | -7.7316 | -7.814 | 7.7087 | 7.5851 | -115.1916 | 7.8552 | 7.7866 | 0.20142 | -115.2283 | -0.032043 | -0.11444 | -122.7036 | 0.004578 | -0.068665 | 0.045776 | -122.7356 | 7.814 | 7.7774 | 7.7637 | -115.4205 | 0.30212 | 0.27008 | 0.059509 | -123.1201
776.8438 | 123.2117 | -7.5302 | 115.5075 | -0.13755 | 0.13377 | 0.15574 | 0.066496 | 0.11667 | 0.0075917 | 0.037698 | -0.30414 | 0.20089 | -0.0095859 | 0.18703 | 0.010744 | -0.022315 | 0.073242 | 0.16479 | 0.059509 | 0.068665 | 0.12817 | -0.004578 | -0.11444 | -7.457 | -7.3883 | -7.4707 | -7.2556 | -7.2693 | -7.5577 | -7.6538 | 7.5256 | 7.4158 | -115.3793 | 7.695 | 7.5989 | 0.18311 | -115.4343 | -0.027466 | -0.1236 | -122.7631 | 0.073242 | 0.059509 | 0.18311 | -122.7768 | 7.6584 | 7.6035 | 7.5897 | -115.6219 | 0.27466 | 0.26092 | 0.14191 | -123.1613
777.8438 | 123.2071 | -7.3929 | 115.6128 | -0.061255 | 0.12522 | 0.14506 | 0.050474 | 0.10705 | -0.0030893 | 0.033426 | -0.3194 | 0.18273 | -0.0063819 | 0.17635 | 0.010744 | -0.026588 | 0.091553 | 0.1831 | 0.07782 | 0.10986 | 0.1236 | 0.022888 | -0.11444 | -7.3517 | -7.2922 | -7.457 | -7.1457 | -7.1823 | -7.4295 | -7.5165 | 7.4158 | 7.2784 | -115.4892 | 7.576 | 7.5027 | 0.2243 | -115.5212 | -0.036621 | -0.1236 | -122.7585 | 0.041198 | -0.064087 | 0.059509 | -122.7951 | 7.5165 | 7.4844 | 7.4707 | -115.7272 | 0.24719 | 0.21057 | 0.10071 | -123.1293
778.8438 | 123.2483 | -7.2647 | 115.7318 | 0.060816 | 0.13377 | 0.14719 | 0.0697 | 0.1156 | 0.0011837 | 0.038766 | -0.2431 | 0.19555 | -0.012791 | 0.17635 | 0.0075399 | -0.016975 | 0.086975 | 0.16022 | 0.073242 | 0.082397 | 0.10071 | 0.022888 | -0.10071 | -7.196 | -7.1457 | -7.3196 | -7.0267 | -7.0633 | -7.2922 | -7.37 | 7.2876 | 7.164 | -115.6311 | 7.4249 | 7.3471 | 0.18311 | -115.6448 | -0.027466 | -0.10529 | -122.7585 | 0.068664 | -0.054932 | 0.050354 | -122.7951 | 7.3654 | 7.3517 | 7.338 | -115.8325 | 0.23804 | 0.20142 | 0.11902 | -123.1018
779.8438 | 123.0881 | -7.0999 | 116.0751 | 0.030298 | 0.1594 | 0.13651 | 0.059019 | 0.1188 | 0.036431 | 0.045175 | -0.41095 | 0.20303 | 0.0010951 | 0.18383 | 0.02997 | -0.03086 | 0.059509 | 0.07782 | -0.032043 | 0.018311 | 0.14191 | -0.018311 | -0.16479 | -7.0908 | -7.0633 | -7.2418 | -6.8527 | -6.8756 | -7.1274 | -7.2098 | 7.0816 | 6.9351 | -115.9332 | 7.1777 | 7.1182 | 0.18311 | -116.0156 | -0.027465 | -0.10986 | -122.9279 | 0.009156 | -0.14191 | -0.032043 | -122.9507 | 7.2418 | 7.1594 | 7.0679 | -116.2399 | 0.24719 | 0.22431 | 0.036622 | -123.2849
780.8438 | 123.2208 | -6.9489 | 116.0568 | 0.10659 | 0.13377 | 0.13437 | 0.062223 | 0.11453 | -0.0084293 | 0.046243 | 0.0010378 | 0.18807 | 0.0064351 | 0.17635 | 0.01288 | -0.015907 | 0.013733 | 0.091553 | 0 | 0.045776 | 0.13733 | 0.032043 | -0.10071 | -6.9305 | -6.8756 | -7.0312 | -6.7429 | -6.7749 | -6.9717 | -7.0679 | 6.9809 | 6.8481 | -115.9195 | 7.0404 | 6.9946 | 0.14648 | -116.0431 | -0.022888 | -0.11902 | -122.7997 | 0.018311 | -0.082397 | 0.036621 | -122.8317 | 7.0862 | 6.9626 | 6.9489 | -116.1575 | 0.20599 | 0.17395 | 0.073243 | -123.1247
781.8438 | 123.2483 | -6.8985 | 116.1255 | -0.00022031 | 0.1359 | 0.15253 | 0.065427 | 0.12521 | -0.0062933 | 0.034494 | -0.30414 | 0.19662 | -0.0053139 | 0.16994 | 0.011812 | -0.02552 | 0.07782 | 0.16479 | 0.054932 | 0.073242 | 0.11902 | 0.027466 | -0.10529 | -6.8436 | -6.7566 | -6.8665 | -6.6833 | -6.7154 | -6.9351 | -6.9901 | 6.926 | 6.7932 | -116.0065 | 7.0633 | 6.9717 | 0.17853 | -116.0477 | -0.036621 | -0.091552 | -122.8088 | 0.054932 | 0.032044 | 0.1236 | -122.8409 | 7.0175 | 6.9763 | 6.9534 | -116.2308 | 0.21515 | 0.18311 | 0.14191 | -123.1155
782.8438 | 123.2117 | -7.2235 | 115.8279 | 0.18289 | 0.12522 | 0.14399 | 0.060087 | 0.10705 | -0.0073613 | 0.039835 | -0.3194 | 0.1838 | -0.0095859 | 0.17101 | 0.015017 | -0.028724 | 0.09613 | 0.1831 | 0.082397 | 0.086975 | 0.11444 | 0.041199 | -0.10986 | -7.1686 | -7.1136 | -7.2647 | -6.9946 | -7.0221 | -7.2647 | -7.3196 | 7.2647 | 7.1136 | -115.7135 | 7.4066 | 7.3105 | 0.19684 | -115.7318 | -0.041198 | -0.09613 | -122.8226 | 0.054932 | -0.041198 | 0.054932 | -122.85 | 7.338 | 7.3196 | 7.3059 | -115.9378 | 0.22888 | 0.20142 | 0.10986 | -123.1476
783.8438 | 123.262 | -7.0267 | 115.9836 | 0.015039 | 0.11347 | 0.14933 | 0.063291 | 0.12201 | 0.0022517 | 0.03663 | -0.19733 | 0.20196 | -0.011723 | 0.1678 | 0.0064719 | -0.016975 | 0.07782 | 0.16022 | 0.054932 | 0.073242 | 0.12817 | 0.032043 | -0.091553 | -6.9626 | -6.9031 | -7.0587 | -6.8161 | -6.8527 | -7.0679 | -7.132 | 7.0587 | 6.9351 | -115.8554 | 7.1869 | 7.0999 | 0.16479 | -115.9058 | -0.041199 | -0.10529 | -122.7997 | 0.064087 | -0.032044 | 0.073242 | -122.8363 | 7.1548 | 7.1045 | 7.0816 | -116.0751 | 0.21057 | 0.17395 | 0.1236 | -123.1155
784.8438 | 123.1018 | -7.0358 | 116.0797 | 0.38125 | 0.17435 | 0.13117 | 0.068632 | 0.11346 | 0.034295 | 0.041971 | 0.077332 | 0.19982 | 0.0064351 | 0.17421 | 0.02463 | -0.038337 | -0.032043 | -0.050354 | -0.09613 | -0.032043 | 0.15106 | -0.018311 | -0.13733 | -7.0404 | -7.0633 | -7.2052 | -6.7566 | -6.7841 | -7.0496 | -7.1274 | 7.0175 | 6.8985 | -115.9287 | 6.9855 | 7.0038 | 0.10529 | -116.1118 | -0.013733 | -0.091552 | -122.8363 | -0.004577 | -0.16937 | -0.07782 | -122.8638 | 7.1869 | 7.0038 | 6.9397 | -116.217 | 0.27924 | 0.25177 | -0.027465 | -123.2071
785.8438 | 123.2254 | -6.8024 | 116.2033 | 0.015039 | 0.12308 | 0.14719 | 0.061155 | 0.11774 | -0.011634 | 0.03663 | -0.16681 | 0.19021 | -0.010654 | 0.18489 | 0.0064719 | -0.021247 | 0.064087 | 0.11902 | 0.027466 | 0.059509 | 0.13275 | 0.027466 | -0.091553 | -6.752 | -6.7062 | -6.8436 | -6.6147 | -6.6513 | -6.8436 | -6.9031 | 6.8298 | 6.7108 | -116.0706 | 6.9214 | 6.8619 | 0.15106 | -116.1392 | -0.041199 | -0.10071 | -122.818 | 0.050354 | -0.041199 | 0.059509 | -122.8546 | 6.9351 | 6.8665 | 6.8298 | -116.2949 | 0.18768 | 0.15106 | 0.09613 | -123.1064
786.8438 | 123.1888 | -6.6788 | 116.391 | 0.19814 | 0.13056 | 0.15574 | 0.078245 | 0.11133 | -0.011634 | 0.034494 | -0.63983 | 0.18914 | -0.0031779 | 0.17315 | -0.0010051 | -0.020179 | 0.009155 | 0.073242 | -0.004578 | 0.036621 | 0.1236 | 0.018311 | -0.1236 | -6.665 | -6.601 | -6.7612 | -6.459 | -6.5002 | -6.6971 | -6.7703 | 6.6971 | 6.5552 | -116.2674 | 6.752 | 6.7154 | 0.16022 | -116.3818 | -0.018311 | -0.091553 | -122.85 | 0.013733 | -0.082397 | 0.009156 | -122.8912 | 6.8024 | 6.6879 | 6.6742 | -116.5146 | 0.21973 | 0.17853 | 0.07782 | -123.1613
787.8438 | 123.1796 | -6.5781 | 116.4505 | 0.27444 | 0.13163 | 0.14612 | 0.061155 | 0.11774 | -0.011634 | 0.044107 | 0.092591 | 0.18487 | -0.011723 | 0.1881 | 0.0075399 | -0.015907 | 0.018311 | 0.045776 | 0.004578 | 0.032043 | 0.11902 | 0.036621 | -0.10986 | -6.4819 | -6.4728 | -6.601 | -6.3263 | -6.3583 | -6.546 | -6.6238 | 6.6147 | 6.4682 | -116.3315 | 6.6238 | 6.6101 | 0.14191 | -116.4322 | 0.032043 | -0.045776 | -122.7768 | 0.09613 | -0.022888 | 0.022888 | -122.8088 | 6.6971 | 6.5964 | 6.5826 | -116.5604 | 0.25177 | 0.21973 | 0.10529 | -123.0743
788.8438 | 123.2483 | -6.3126 | 116.6977 | 0.10659 | 0.12629 | 0.14292 | 0.071836 | 0.11667 | 0.010797 | 0.044107 | -0.059997 | 0.19982 | -0.0042459 | 0.18489 | 0.0043349 | -0.027656 | 0.059509 | 0.1236 | 0.045776 | 0.068665 | 0.13275 | 0.036621 | -0.091553 | -6.2668 | -6.2256 | -6.3492 | -6.134 | -6.1844 | -6.3446 | -6.4316 | 6.3492 | 6.221 | -116.5649 | 6.4362 | 6.3812 | 0.16022 | -116.6382 | -0.032043 | -0.11902 | -122.8317 | 0.045776 | -0.036621 | 0.082398 | -122.8821 | 6.4453 | 6.3721 | 6.3583 | -116.7892 | 0.17853 | 0.12817 | 0.086975 | -123.1293
789.8438 | 123.2208 | -6.2164 | 116.8213 | 0.13711 | 0.12736 | 0.14399 | 0.061155 | 0.1156 | -0.0041573 | 0.03129 | -0.01422 | 0.18594 | -0.014927 | 0.19237 | 0.0086079 | -0.019111 | 0.032043 | 0.09613 | 0.022888 | 0.068665 | 0.13275 | 0.018311 | -0.09613 | -6.1844 | -6.1386 | -6.2805 | -6.0471 | -6.1066 | -6.2531 | -6.3492 | 6.2347 | 6.1203 | -116.6885 | 6.3126 | 6.2851 | 0.16479 | -116.7892 | -0.036621 | -0.13275 | -122.8683 | 0.032044 | -0.064087 | 0.068664 | -122.9279 | 6.3492 | 6.2485 | 6.2393 | -116.9174 | 0.16937 | 0.10986 | 0.07782 | -123.1705
790.8438 | 123.2071 | -6.0287 | 116.9952 | -0.15281 | 0.12736 | 0.16001 | 0.065427 | 0.10278 | 0.0011837 | 0.034494 | 0.0010378 | 0.18487 | -0.0074499 | 0.18489 | 0.015017 | -0.031928 | 0.045776 | 0.073242 | 0.013733 | 0.041199 | 0.11444 | 0.009155 | -0.11444 | -6.0059 | -5.9784 | -6.1249 | -5.8914 | -5.9418 | -6.0837 | -6.1478 | 6.0379 | 5.9143 | -116.8808 | 6.102 | 6.0699 | 0.15564 | -116.9495 | -0.054931 | -0.11902 | -122.8867 | 0.022889 | -0.09613 | 0.022888 | -122.937 | 6.1432 | 6.0745 | 6.0425 | -117.1097 | 0.13733 | 0.086976 | 0.050354 | -123.143
791.8438 | 123.2254 | -5.9509 | 117.0959 | 0.18289 | 0.12308 | 0.14292 | 0.067564 | 0.12628 | -0.0030893 | 0.029153 | 0.16888 | 0.18487 | -0.0063819 | 0.18596 | 0.0086079 | -0.02552 | -0.10071 | 0.004578 | -0.13275 | -0.045776 | 0.059509 | -0.041199 | -0.16479 | -5.928 | -5.9006 | -6.0242 | -5.809 | -5.8502 | -5.9875 | -6.0654 | 5.9097 | 5.7861 | -117.0364 | 5.9555 | 5.9052 | 0.11902 | -117.1967 | -0.036621 | -0.11444 | -122.905 | 0.022888 | -0.073242 | 0.041199 | -122.9462 | 6.0104 | 5.8502 | 5.8182 | -117.2607 | 0.14191 | 0.10071 | 0.050354 | -123.1613
792.8438 | 123.1796 | -5.9097 | 117.1692 | 0.2134 | 0.11881 | 0.1504 | 0.050474 | 0.11026 | -0.0073613 | 0.03129 | 0.13837 | 0.18807 | -0.0053139 | 0.18596 | 0.011812 | -0.015907 | 0.022888 | 0.064087 | -0.004578 | 0.041199 | 0.10529 | 0.013733 | -0.10986 | -5.809 | -5.8731 | -6.1157 | -5.6763 | -5.7358 | -5.9326 | -6.0059 | 5.9235 | 5.7999 | -117.0639 | 5.9738 | 5.9509 | 0.15106 | -117.1463 | -0.022888 | -0.09613 | -122.8455 | 0.10071 | -0.20599 | -0.10986 | -122.905 | 6.015 | 5.9326 | 5.9052 | -117.2791 | 0.23346 | 0.17395 | 0.036621 | -123.175
793.8438 | 123.1705 | -5.722 | 117.3248 | 0.41177 | 0.12629 | 0.13544 | 0.059019 | 0.12414 | 0.0075917 | 0.040903 | 0.30621 | 0.19555 | -0.0053139 | 0.18917 | 0.019289 | -0.019111 | 0.09613 | 0.1236 | 0.032043 | 0.07782 | 0.091553 | 0.022888 | -0.091553 | -5.6534 | -5.6534 | -5.7907 | -5.5756 | -5.5984 | -5.7358 | -5.8228 | 5.7449 | 5.6305 | -117.2333 | 5.8456 | 5.7999 | 0.16937 | -117.2287 | -0.013733 | -0.10071 | -122.9004 | 0.068665 | -0.068664 | 0.032044 | -122.9233 | 5.8136 | 5.8182 | 5.7541 | -117.4164 | 0.14648 | 0.1236 | 0.068665 | -123.1476
794.8438 | 123.1293 | -5.69 | 117.4347 | -1.1446 | 0.15726 | 0.14292 | 0.073972 | 0.11239 | 0.022546 | 0.040903 | -0.5025 | 0.20516 | -0.018131 | 0.19664 | 0.016085 | -0.038337 | 0.027466 | 0.018311 | -0.07782 | 0 | 0.19226 | 0.009155 | -0.13275 | -5.6671 | -5.6442 | -5.809 | -5.4428 | -5.4932 | -5.6854 | -5.7678 | 5.6992 | 5.5573 | -117.2424 | 5.7083 | 5.69 | 0.13275 | -117.4072 | 0.004577 | -0.07782 | -122.8775 | 0.022888 | -0.11902 | -0.041199 | -122.9279 | 5.8823 | 5.7175 | 5.6122 | -117.5674 | 0.24719 | 0.19684 | 0.045776 | -123.2025
795.8438 | 123.1155 | -5.5939 | 117.54 | -0.24436 | 0.13697 | 0.14933 | 0.063291 | 0.11453 | 0.0075917 | 0.03663 | -0.15155 | 0.19448 | -0.010654 | 0.17955 | 0.0075399 | -0.022315 | 0.027466 | 0.068665 | -0.036621 | 0.022888 | 0.14648 | 0 | -0.13733 | -5.5847 | -5.5481 | -5.69 | -5.3787 | -5.4291 | -5.6351 | -5.6992 | 5.5939 | 5.4565 | -117.3935 | 5.6625 | 5.6168 | 0.16022 | -117.5125 | -0.041199 | -0.10529 | -122.9187 | 0.009155 | -0.09613 | 0.009156 | -122.9691 | 5.7404 | 5.6213 | 5.5573 | -117.6773 | 0.21515 | 0.16479 | 0.045776 | -123.2391
796.8438 | 123.1979 | -5.4932 | 117.5766 | 0.38125 | 0.12736 | 0.13758 | 0.056883 | 0.10812 | -0.0084293 | 0.033426 | 0.22992 | 0.18487 | -0.028812 | 0.1646 | 0.0064719 | -0.022315 | 0.022888 | 0.086975 | 0.009155 | 0.032043 | 0.13275 | 0.027466 | -0.10986 | -5.452 | -5.4153 | -5.5481 | -5.3329 | -5.3604 | -5.5161 | -5.5893 | 5.5206 | 5.3833 | -117.4438 | 5.5801 | 5.5252 | 0.14191 | -117.5537 | -0.022888 | -0.09613 | -122.9095 | 0.041199 | -0.054932 | 0.041198 | -122.937 | 5.6259 | 5.5161 | 5.5023 | -117.6865 | 0.16022 | 0.13275 | 0.07782 | -123.1659
797.8438 | 123.2025 | -5.4062 | 117.6086 | 0.42703 | 0.15406 | 0.13972 | 0.060087 | 0.12094 | 0.0011837 | 0.030222 | 0.32147 | 0.19128 | -0.0042459 | 0.20305 | 0.011812 | -0.016975 | 0.059509 | 0.10071 | 0.032043 | 0.041199 | 0.10529 | 0.036621 | -0.09613 | -5.3513 | -5.3421 | -5.4794 | -5.278 | -5.3009 | -5.4153 | -5.5389 | 5.4428 | 5.3101 | -117.5034 | 5.5069 | 5.4474 | 0.13733 | -117.5491 | -0.009155 | -0.13275 | -122.8867 | 0.054932 | -0.073242 | 0.059509 | -122.9095 | 5.5115 | 5.4657 | 5.4382 | -117.7048 | 0.12817 | 0.10529 | 0.064087 | -123.1476
798.8438 | 123.1979 | -5.3329 | 117.7368 | 0.50332 | 0.14979 | 0.14719 | 0.065427 | 0.12414 | 0.0097277 | 0.030222 | 0.33673 | 0.19982 | -0.0010409 | 0.18169 | 0.011812 | -0.0094981 | 0.086975 | 0.10071 | 0.032043 | 0.059509 | 0.10986 | 0.027466 | -0.086975 | -5.2551 | -5.2368 | -5.3787 | -5.1865 | -5.2231 | -5.3375 | -5.4245 | 5.3604 | 5.246 | -117.627 | 5.4337 | 5.3925 | 0.14648 | -117.6498 | -0.004577 | -0.091553 | -122.9233 | 0.07782 | -0.045776 | 0.045777 | -122.9599 | 5.4428 | 5.4199 | 5.365 | -117.8238 | 0.14649 | 0.10986 | 0.096131 | -123.1613
799.8438 | 123.2162 | -5.2231 | 117.7872 | 0.5491 | 0.14445 | 0.1301 | 0.065427 | 0.11346 | 0.011865 | 0.041971 | 0.24518 | 0.19341 | -0.023472 | 0.18703 | 0.031038 | -0.03086 | 0.082397 | 0.11902 | 0.036621 | 0.064087 | 0.10529 | 0.032043 | -0.10529 | -5.1407 | -5.159 | -5.2643 | -5.1132 | -5.1544 | -5.2597 | -5.3329 | 5.2551 | 5.1178 | -117.6819 | 5.3421 | 5.2872 | 0.16937 | -117.7048 | -0.036622 | -0.10986 | -122.9004 | 0.082397 | -0.041199 | 0.068665 | -122.9416 | 5.3284 | 5.3055 | 5.2597 | -117.8925 | 0.10986 | 0.068664 | 0.064086 | -123.1201
800.8438 | 123.0927 | -5.1682 | 117.9428 | -0.29014 | 0.13483 | 0.14506 | 0.067564 | 0.12521 | 0.012933 | 0.040903 | 2.122 | 0.2073 | 0.0085721 | 0.16674 | 0.021425 | -0.029792 | -0.004578 | -0.009155 | -0.073242 | -0.009155 | 0.14648 | -0.009155 | -0.16022 | -5.1544 | -5.1086 | -5.2734 | -4.9255 | -4.9622 | -5.1956 | -5.2689 | 5.159 | 5.0079 | -117.7963 | 5.159 | 5.159 | 0.15106 | -117.9474 | -0.027466 | -0.10071 | -122.8683 | 0.013733 | -0.10529 | -0.004577 | -122.905 | 5.3146 | 5.1636 | 5.0949 | -118.103 | 0.24261 | 0.20599 | 0.059509 | -123.2117
801.8438 | 123.2346 | -5.0354 | 117.9749 | 0.50332 | 0.14658 | 0.13437 | 0.05261 | 0.12201 | 0.014001 | 0.040903 | -1.4638 | 0.18914 | -0.0021099 | 0.18169 | 0.023561 | -0.03086 | 0.073242 | 0.11444 | 0.054932 | 0.068665 | 0.086975 | 0.032043 | -0.13275 | -4.9576 | -4.9347 | -5.0674 | -4.9667 | -4.9988 | -5.0858 | -5.1315 | 5.0674 | 4.9026 | -117.8879 | 5.1498 | 5.1041 | 0.20142 | -117.9016 | -0.050354 | -0.096131 | -122.9416 | 0.077819 | -0.032044 | 0.064087 | -122.9736 | 5.1224 | 5.1086 | 5.0903 | -118.1076 | 0.068664 | 0.036621 | 0.10071 | -123.1064
802.8438 | 123.2071 | -5.0171 | 118.0389 | 0.42703 | 0.14338 | 0.13544 | 0.076109 | 0.1156 | 0.012933 | 0.03663 | 0.24518 | 0.18807 | -0.0074499 | 0.1913 | 0.016085 | -0.012702 | 0.07782 | 0.1236 | 0.041199 | 0.059509 | 0.10071 | 0.032043 | -0.09613 | -4.921 | -4.9026 | -5.0171 | -4.8981 | -4.9393 | -5.0354 | -5.1132 | 5.0491 | 4.921 | -117.9382 | 5.1407 | 5.0766 | 0.15564 | -117.9611 | -0.01831 | -0.09613 | -122.937 | 0.096131 | 0 | 0.09613 | -122.9782 | 5.1178 | 5.0949 | 5.0583 | -118.1351 | 0.11902 | 0.07782 | 0.11444 | -123.1522
803.8438 | 123.2391 | -4.9026 | 118.1213 | 0.53384 | 0.14231 | 0.13544 | 0.068632 | 0.11667 | 0.0011837 | 0.032358 | 0.42828 | 0.20089 | -0.0042459 | 0.19024 | 0.018221 | -0.021247 | 0.064087 | 0.11902 | 0.045776 | 0.064087 | 0.068665 | -0.013733 | -0.13275 | -4.834 | -4.8157 | -4.9301 | -4.8386 | -4.8523 | -4.9393 | -4.9988 | 4.8889 | 4.7699 | -118.0527 | 5.0217 | 4.9667 | 0.19684 | -118.0573 | -0.036621 | -0.09613 | -122.9599 | 0.068665 | -0.027466 | 0.068664 | -122.9736 | 4.9713 | 4.9667 | 4.9484 | -118.2541 | 0.064087 | 0.050354 | 0.086975 | -123.1201
804.8438 | 123.23 | -4.8248 | 118.2129 | 0.45754 | 0.13697 | 0.13972 | 0.0697 | 0.11667 | 0.0075917 | 0.039835 | -0.85345 | 0.19555 | 0.0032311 | 0.19024 | 0.020357 | -0.034064 | 0.10071 | 0.10529 | 0.036621 | 0.064087 | 0.09613 | 0.018311 | -0.11902 | -4.7333 | -4.7058 | -4.834 | -4.7241 | -4.7607 | -4.8614 | -4.9164 | 4.8431 | 4.7058 | -118.1168 | 4.9301 | 4.8889 | 0.18311 | -118.1122 | -0.036621 | -0.091553 | -122.937 | 0.091553 | -0.009155 | 0.082398 | -122.9736 | 4.921 | 4.9255 | 4.8615 | -118.3319 | 0.10071 | 0.064087 | 0.11902 | -123.1293
805.8438 | 123.2346 | -4.7195 | 118.3411 | -0.2291 | 0.11988 | 0.14719 | 0.05261 | 0.1156 | -0.010566 | 0.029153 | -0.91449 | 0.18914 | -0.018131 | 0.18596 | 0.013948 | -0.027656 | 0.086975 | 0.13275 | 0.050354 | -0.009155 | 0.10986 | -0.018311 | -0.14191 | -4.66 | -4.5731 | -4.7195 | -4.6234 | -4.66 | -4.7379 | -4.8157 | 4.7012 | 4.5776 | -118.2312 | 4.8523 | 4.7104 | 0.13275 | -118.2541 | -0.018311 | -0.096131 | -122.9645 | 0.059509 | 0 | 0.096131 | -123.0011 | 4.8294 | 4.8065 | 4.7699 | -118.483 | 0.09613 | 0.059509 | 0.14648 | -123.1567
806.8438 | 123.2346 | -4.6463 | 118.3685 | 0.36599 | 0.14658 | 0.14078 | 0.070768 | 0.12094 | 0.016137 | 0.039835 | 0.16888 | 0.1838 | -0.0074499 | 0.18917 | 0.023561 | -0.024451 | 0.068665 | 0.09613 | 0.027466 | 0.07782 | 0.10986 | 0.018311 | -0.09613 | -4.5593 | -4.5456 | -4.6783 | -4.5502 | -4.5868 | -4.6692 | -4.7562 | 4.6646 | 4.5502 | -118.2587 | 4.7424 | 4.7241 | 0.17395 | -118.2999 | -0.022888 | -0.10986 | -122.9187 | 0.086975 | -0.032044 | 0.07782 | -122.9553 | 4.7562 | 4.715 | 4.6738 | -118.4647 | 0.09613 | 0.059509 | 0.10071 | -123.1247
807.8438 | 123.1522 | -4.6188 | 118.4875 | 0.50332 | 0.17435 | 0.14078 | 0.070768 | 0.1188 | 0.028955 | 0.046243 | 0.13837 | 0.20089 | -0.0085179 | 0.18703 | 0.022493 | -0.016975 | 0.009155 | -0.022888 | -0.10529 | -0.009155 | 0.1236 | -0.018311 | -0.13275 | -4.5685 | -4.5868 | -4.7012 | -4.4357 | -4.4678 | -4.6234 | -4.7012 | 4.6005 | 4.4861 | -118.364 | 4.5959 | 4.6097 | 0.1236 | -118.4784 | -0.004578 | -0.082398 | -122.9233 | 0.050354 | -0.082398 | 0 | -122.9553 | 4.7424 | 4.628 | 4.5135 | -118.6203 | 0.1831 | 0.15106 | 0.032043 | -123.1888
808.8438 | 123.2025 | -4.5136 | 118.5654 | 0.4728 | 0.15513 | 0.14185 | 0.070768 | 0.11026 | 0.016137 | 0.03663 | 0.24518 | 0.20409 | 0.0010951 | 0.19985 | 0.022493 | -0.020179 | 0.027466 | -0.004578 | -0.050354 | 0.004578 | 0.11902 | -0.009155 | -0.14191 | -4.4495 | -4.454 | -4.5639 | -4.3671 | -4.4174 | -4.5227 | -4.6005 | 4.5044 | 4.3716 | -118.4464 | 4.509 | 4.5181 | 0.14649 | -118.5379 | -0.009155 | -0.086975 | -122.9324 | 0.064087 | -0.050354 | 0.036621 | -122.9828 | 4.6326 | 4.541 | 4.4632 | -118.7073 | 0.14649 | 0.096131 | 0.059509 | -123.1659
809.8438 | 123.2574 | -4.4083 | 118.634 | 0.56436 | 0.14979 | 0.13758 | 0.0697 | 0.1188 | 0.017205 | 0.045175 | 0.33673 | 0.19555 | 0.0042991 | 0.17528 | 0.013948 | -0.021247 | 0.068665 | 0.091553 | 0.004578 | 0.07782 | 0.10529 | 0.018311 | -0.11902 | -4.3259 | -4.3076 | -4.4357 | -4.3076 | -4.335 | -4.422 | -4.4998 | 4.4266 | 4.2892 | -118.5287 | 4.4998 | 4.4861 | 0.19684 | -118.5654 | -0.013733 | -0.091553 | -122.9416 | 0.082397 | -0.027466 | 0.064087 | -122.9691 | 4.5136 | 4.4769 | 4.4128 | -118.7531 | 0.10071 | 0.073242 | 0.10071 | -123.1338
810.8438 | 123.1338 | -4.3945 | 118.721 | -1.2514 | 0.13804 | 0.14399 | 0.064359 | 0.13055 | -0.00095325 | 0.039835 | -0.47198 | 0.19341 | 0.0021631 | 0.18062 | 0.0086079 | -0.018043 | -0.022888 | -0.009155 | -0.068665 | -0.022888 | 0.14648 | -0.013733 | -0.17395 | -4.3808 | -4.3259 | -4.4678 | -4.1794 | -4.2206 | -4.3991 | -4.4952 | 4.3808 | 4.2206 | -118.5745 | 4.3854 | 4.3716 | 0.15106 | -118.7439 | -0.004578 | -0.10071 | -122.9004 | 0.013733 | -0.073242 | 0.027466 | -122.9416 | 4.541 | 4.3716 | 4.3259 | -118.895 | 0.21515 | 0.17395 | 0.068664 | -123.2162
811.8438 | 123.2071 | -4.2847 | 118.8126 | 0.50332 | 0.17008 | 0.13758 | 0.076109 | 0.12521 | 0.016137 | 0.05372 | 0.30621 | 0.19769 | 0.0053671 | 0.18703 | 0.025698 | -0.02552 | 0.018311 | -0.004578 | -0.059509 | 0 | 0.13733 | -0.013733 | -0.14191 | -4.2252 | -4.2297 | -4.335 | -4.1382 | -4.1702 | -4.2984 | -4.3625 | 4.2709 | 4.1428 | -118.6752 | 4.2801 | 4.2847 | 0.14191 | -118.7943 | -0.013733 | -0.07782 | -122.9507 | 0.059509 | -0.050354 | 0.027466 | -122.9828 | 4.422 | 4.303 | 4.2252 | -118.9545 | 0.14648 | 0.11444 | 0.054932 | -123.175
812.8438 | 123.1659 | -4.2206 | 118.8904 | 0.41177 | 0.18931 | 0.13758 | 0.068632 | 0.11239 | 0.012933 | 0.039835 | 0.2757 | 0.20623 | 0.0032311 | 0.17208 | 0.017153 | -0.021247 | 0 | -0.036621 | -0.064087 | -0.018311 | 0.15564 | -0.004578 | -0.13733 | -4.1656 | -4.1702 | -4.2801 | -4.0375 | -4.0787 | -4.2114 | -4.2938 | 4.216 | 4.0833 | -118.7347 | 4.184 | 4.2023 | 0.11902 | -118.8904 | 0.009155 | -0.073242 | -122.9279 | 0.054932 | -0.059509 | 0.013733 | -122.9691 | 4.3762 | 4.2206 | 4.1565 | -119.0277 | 0.18311 | 0.14191 | 0.050354 | -123.1842
813.8438 | 123.1384 | -4.1473 | 118.9774 | -0.29014 | 0.16795 | 0.14078 | 0.066496 | 0.11774 | 0.017205 | 0.046243 | 0.1994 | 0.2073 | 0.0010951 | 0.19664 | 0.022493 | -0.026588 | 0.009155 | -0.050354 | -0.091553 | 0 | 0.13733 | -0.013733 | -0.17395 | -4.1107 | -4.129 | -4.2252 | -3.9642 | -3.9917 | -4.1611 | -4.2206 | 4.1336 | 3.9734 | -118.84 | 4.097 | 4.1473 | 0.17395 | -118.9682 | -0.013733 | -0.073242 | -122.9416 | 0.036621 | -0.07782 | -0.004578 | -122.9691 | 4.2847 | 4.1565 | 4.0558 | -119.1513 | 0.18311 | 0.15564 | 0.018311 | -123.1979
814.8438 | 123.2666 | -4.0329 | 119.0277 | 0.060816 | 0.11561 | 0.14292 | 0.057951 | 0.10812 | -0.018043 | 0.047311 | 0.016297 | 0.187 | -0.0063819 | 0.16994 | 0.0043349 | -0.012702 | 0.068665 | 0.11444 | 0.050354 | 0.082397 | 0.12817 | 0.041199 | -0.091553 | -3.9368 | -3.9093 | -3.978 | -3.923 | -3.9413 | -4.0375 | -4.1153 | 4.0741 | 3.9413 | -118.8995 | 4.1473 | 4.1153 | 0.17395 | -118.959 | -0.004578 | -0.082397 | -122.9507 | 0.09613 | 0.054932 | 0.13733 | -122.9691 | 4.1611 | 4.1016 | 4.0833 | -119.1193 | 0.10986 | 0.091553 | 0.1236 | -123.143
815.8438 | 123.1659 | -3.9597 | 119.1101 | 0.4728 | 0.14872 | 0.14506 | 0.061155 | 0.11987 | -0.0073613 | 0.035562 | 0.29095 | 0.19875 | 0.0010951 | 0.16887 | 0.016085 | -0.014838 | 0.059509 | 0.11444 | 0.050354 | 0.054932 | 0.10529 | 0.041199 | -0.10071 | -3.8818 | -3.8727 | -3.9597 | -3.8406 | -3.8818 | -3.9734 | -4.0283 | 4.0009 | 3.8589 | -119.0048 | 4.0741 | 4.0146 | 0.15564 | -119.0506 | -0.013733 | -0.068664 | -122.9507 | 0.07782 | 0 | 0.068664 | -122.9919 | 4.0649 | 4.0192 | 4.01 | -119.2108 | 0.11902 | 0.07782 | 0.086975 | -123.1384
816.8438 | 123.1247 | -3.923 | 119.2017 | 0.35073 | 0.15726 | 0.14078 | 0.078245 | 0.11667 | 0.035363 | 0.034494 | 0.18414 | 0.19769 | -0.0042459 | 0.19237 | 0.020357 | -0.021247 | 0.018311 | -0.045776 | -0.10071 | -0.009155 | 0.14648 | -0.018311 | -0.15564 | -3.8773 | -3.9093 | -4.0054 | -3.7537 | -3.7994 | -3.9276 | -4.0237 | 3.9047 | 3.7674 | -119.0552 | 3.8773 | 3.9139 | 0.14649 | -119.1833 | -0.004577 | -0.10071 | -122.9553 | 0.045777 | -0.082397 | 0.018311 | -123.0011 | 4.0695 | 3.9413 | 3.8223 | -119.3573 | 0.16937 | 0.1236 | 0.013733 | -123.2254
817.8438 | 123.1476 | -3.8681 | 119.2566 | 0.41177 | 0.1797 | 0.10447 | 0.067564 | 0.12308 | 0.0054557 | 0.037698 | 0.1994 | 0.20196 | 0.0075041 | 0.19344 | 0.017153 | -0.02552 | 0.036621 | -0.004578 | -0.073242 | -0.013733 | 0.16937 | 0.004578 | -0.12817 | -3.8315 | -3.8498 | -3.9505 | -3.6713 | -3.7125 | -3.8727 | -3.9322 | 3.8727 | 3.7399 | -119.0872 | 3.8635 | 3.8544 | 0.11444 | -119.22 | -0.004578 | -0.064087 | -122.9279 | 0.036621 | -0.082397 | -0.01831 | -122.9691 | 4.0375 | 3.9047 | 3.7949 | -119.3848 | 0.19684 | 0.15564 | 0.018311 | -123.1888
818.8438 | 123.2071 | -3.7262 | 119.339 | 0.41177 | 0.12629 | 0.1536 | 0.067564 | 0.10599 | -0.01377 | 0.028085 | 0.39777 | 0.187 | 0.0032311 | 0.20733 | 0.013948 | -0.0073621 | 0.054932 | 0.10071 | 0.041199 | 0.050354 | 0.10986 | 0.032043 | -0.11444 | -3.6667 | -3.653 | -3.7399 | -3.6163 | -3.6484 | -3.7628 | -3.8269 | 3.7582 | 3.6118 | -119.2291 | 3.8269 | 3.7765 | 0.16479 | -119.2841 | -0.036621 | -0.10071 | -122.9553 | 0.059509 | -0.013733 | 0.086975 | -122.9874 | 3.8361 | 3.7811 | 3.7674 | -119.4534 | 0.10986 | 0.07782 | 0.073242 | -123.1659
819.8438 | 123.1018 | -3.6942 | 119.4443 | 0.36599 | 0.17222 | 0.14719 | 0.065427 | 0.10065 | 0.02575 | 0.040903 | 0.077332 | 0.20623 | 0.013912 | 0.18383 | 0.020357 | -0.034064 | -0.004578 | -0.068665 | -0.10071 | -0.009155 | 0.15106 | -0.013733 | -0.14191 | -3.7033 | -3.7262 | -3.8361 | -3.5339 | -3.5706 | -3.717 | -3.804 | 3.6804 | 3.5522 | -119.2932 | 3.6255 | 3.685 | 0.13275 | -119.4489 | -0.022888 | -0.10986 | -122.9782 | -0.009155 | -0.14191 | -0.032044 | -123.0148 | 3.8452 | 3.6896 | 3.5934 | -119.5862 | 0.16022 | 0.1236 | -0.032043 | -123.2483
820.8438 | 123.1155 | -3.6346 | 119.5129 | 0.19814 | 0.17542 | 0.1301 | 0.0697 | 0.11987 | 0.02575 | 0.044107 | 0.077332 | 0.19875 | 0.0096401 | 0.19771 | 0.022493 | -0.032996 | -0.027466 | -0.068665 | -0.10529 | -0.032043 | 0.15564 | -0.004578 | -0.14191 | -3.6392 | -3.6301 | -3.7308 | -3.4698 | -3.511 | -3.6392 | -3.7399 | 3.6301 | 3.4927 | -119.3573 | 3.566 | 3.6026 | 0.10986 | -119.5404 | -0.004577 | -0.10528 | -122.9828 | -0.004577 | -0.09613 | 0.009155 | -123.024 | 3.7903 | 3.6072 | 3.5294 | -119.6548 | 0.1648 | 0.1236 | 0.004578 | -123.2529
821.8438 | 123.1476 | -3.6072 | 119.5312 | 0.13711 | 0.16261 | 0.14078 | 0.067564 | 0.11987 | 0.010797 | 0.046243 | -0.01422 | 0.19662 | 0.020321 | 0.18383 | 0.019289 | -0.028724 | 0 | 0.009155 | -0.059509 | 0.004578 | 0.11902 | -0.027466 | -0.15106 | -3.5477 | -3.5522 | -3.6713 | -3.4241 | -3.4607 | -3.6301 | -3.685 | 3.5797 | 3.4561 | -119.4122 | 3.6163 | 3.6118 | 0.15564 | -119.5312 | -0.022888 | -0.07782 | -122.9553 | 0.05951 | -0.064087 | 0.013733 | -122.9919 | 3.7262 | 3.6072 | 3.5477 | -119.6823 | 0.18311 | 0.14649 | 0.054932 | -123.2162
822.8438 | 123.1018 | -3.5156 | 119.6457 | 0.22866 | 0.16367 | 0.13758 | 0.07504 | 0.098509 | 0.018273 | 0.049448 | -0.19733 | 0.20089 | 0.010708 | 0.17635 | 0.019289 | -0.016975 | -0.036621 | -0.045776 | -0.082397 | -0.022888 | 0.14191 | -0.022888 | -0.16479 | -3.5248 | -3.511 | -3.6301 | -3.3279 | -3.3737 | -3.5202 | -3.6026 | 3.4927 | 3.3508 | -119.5038 | 3.4698 | 3.4927 | 0.14191 | -119.6823 | -0.004578 | -0.086975 | -122.9736 | -0.009155 | -0.11444 | -0.027466 | -123.0194 | 3.6575 | 3.479 | 3.4332 | -119.8105 | 0.18768 | 0.14191 | 0.004578 | -123.2483
823.8438 | 123.143 | -3.4653 | 119.6823 | 0.36599 | 0.17008 | 0.12583 | 0.070768 | 0.12521 | 0.016137 | 0.030222 | 0.1994 | 0.20303 | 0.017117 | 0.19664 | 0.020357 | -0.0062931 | -0.041199 | -0.054932 | -0.09613 | -0.018311 | 0.14191 | -0.027466 | -0.14648 | -3.2959 | -3.6942 | -3.4561 | -3.2776 | -3.3005 | -3.4561 | -3.5248 | 3.4378 | 3.3188 | -119.5404 | 3.4103 | 3.447 | 0.12817 | -119.7235 | 0.009155 | -0.059509 | -122.9599 | 0.16937 | 0.009155 | 0.068664 | -122.9828 | 3.6072 | 3.4241 | 3.3691 | -119.8288 | 0.18768 | 0.16479 | -0.22888 | -123.2071
824.8438 | 123.2117 | -3.3875 | 119.7235 | 0.24392 | 0.11668 | 0.14399 | 0.072904 | 0.1156 | -0.027656 | 0.032358 | 0.5351 | 0.18807 | 0.0032311 | 0.19344 | -0.0074141 | -0.014838 | -0.022888 | 0.045776 | -0.013733 | 0.041199 | 0.1236 | 0.009155 | -0.14191 | -3.3508 | -3.2822 | -3.3966 | -3.3051 | -3.3279 | -3.392 | -3.4698 | 3.3966 | 3.2455 | -119.5999 | 3.4332 | 3.4287 | 0.18311 | -119.7464 | -0.004578 | -0.082398 | -123.0286 | 0.036621 | -0.009155 | 0.073243 | -123.0515 | 3.511 | 3.3646 | 3.3737 | -119.8654 | 0.082397 | 0.059509 | 0.10528 | -123.1934
825.8438 | 123.1247 | -3.3463 | 119.7784 | 0.22866 | 0.16154 | 0.14506 | 0.087858 | 0.10919 | 0.02575 | 0.029153 | 0.13837 | 0.20409 | 0.016048 | 0.18276 | 0.026766 | -0.024451 | -0.041199 | -0.082397 | -0.12817 | -0.018311 | 0.15564 | -0.013733 | -0.14648 | -3.3234 | -3.3417 | -3.4424 | -3.1631 | -3.2227 | -3.3646 | -3.447 | 3.3325 | 3.1998 | -119.6228 | 3.2639 | 3.3279 | 0.12817 | -119.8196 | -0.018311 | -0.10071 | -122.9416 | 0.022888 | -0.096131 | 0.004577 | -123.0011 | 3.5019 | 3.3051 | 3.2181 | -119.9249 | 0.1831 | 0.1236 | 0.004577 | -123.2254
826.8438 | 123.1018 | -3.2959 | 119.8746 | 0.19814 | 0.17756 | 0.15253 | 0.059019 | 0.11133 | 0.014001 | 0.033426 | 0.077332 | 0.19875 | 0.016048 | 0.18489 | 0.026766 | -0.021247 | -0.036621 | -0.041199 | -0.10986 | 0 | 0.13275 | -0.032043 | -0.17395 | -3.3096 | -3.2867 | -3.392 | -3.0945 | -3.1494 | -3.3051 | -3.3646 | 3.2639 | 3.1219 | -119.7418 | 3.2547 | 3.2959 | 0.17395 | -119.9112 | -0.009156 | -0.068665 | -122.9691 | -0.013733 | -0.096131 | -0.027466 | -123.024 | 3.4286 | 3.2593 | 3.186 | -120.0485 | 0.20142 | 0.14648 | 0.009155 | -123.2391
827.8438 | 123.0972 | -3.2272 | 119.9387 | 0.19814 | 0.17329 | 0.13437 | 0.064359 | 0.11239 | 0.018273 | 0.043039 | -0.10577 | 0.18914 | 0.0032311 | 0.19237 | 0.021425 | -0.018043 | -0.041199 | -0.068665 | -0.09613 | -0.013733 | 0.11902 | -0.032043 | -0.15564 | -3.2501 | -3.2318 | -3.3508 | -3.0533 | -3.0853 | -3.2455 | -3.3234 | 3.1952 | 3.0716 | -119.8196 | 3.1586 | 3.2135 | 0.14191 | -119.9799 | -0.01831 | -0.09613 | -122.9919 | -0.022888 | -0.1236 | -0.027466 | -123.024 | 3.3463 | 3.186 | 3.1311 | -120.0943 | 0.17395 | 0.14191 | -0.004578 | -123.262
828.8438 | 123.143 | -3.1586 | 119.9982 | 0.45754 | 0.16901 | 0.13758 | 0.077177 | 0.11026 | 0.0043877 | 0.041971 | 0.22992 | 0.19341 | 0.013912 | 0.18276 | 0.045992 | -0.022315 | -0.036621 | -0.064087 | -0.11444 | -0.013733 | 0.13275 | -0.022888 | -0.14648 | -3.1403 | -2.9846 | -3.154 | -2.9984 | -3.0212 | -3.1906 | -3.2455 | 3.1357 | 3.0121 | -119.8654 | 3.0945 | 3.1448 | 0.13275 | -120.0348 | -0.032044 | -0.086975 | -122.9965 | 0.01831 | 0.004577 | 0.091552 | -123.0194 | 3.2913 | 3.1219 | 3.0441 | -120.1447 | 0.16022 | 0.13733 | 0.17395 | -123.2437
829.8438 | 123.2803 | -3.0991 | 120.0531 | 0.50332 | 0.15192 | 0.13544 | 0.065427 | 0.11453 | 0.014001 | 0.04838 | 0.16888 | 0.19555 | 0.027798 | 0.1913 | 0.010744 | -0.014838 | -0.050354 | -0.091553 | -0.12817 | -0.027466 | 0.14191 | -0.009155 | -0.13275 | -3.1174 | -3.1128 | -3.2043 | -2.9434 | -2.9709 | -3.1219 | -3.1952 | 3.0899 | 2.9663 | -119.9112 | 3.0075 | 3.0716 | 0.10529 | -120.1035 | -0.022888 | -0.09613 | -122.9965 | -0.018311 | -0.10529 | -0.009156 | -123.024 | 3.241 | 3.0487 | 2.9709 | -120.1859 | 0.15564 | 0.12817 | -0.013733 | -123.2483
830.8438 | 123.2071 | -3.035 | 120.0302 | 0.5491 | 0.16154 | 0.1301 | 0.078245 | 0.1188 | -0.0041573 | 0.037698 | 0.44354 | 0.19448 | -0.0031779 | 0.18062 | 0.017153 | -0.011634 | -0.009155 | -0.004578 | -0.041199 | 0.022888 | 0.1236 | -0.004578 | -0.1236 | -2.9892 | -2.9755 | -3.0624 | -2.9343 | -2.9663 | -3.0487 | -3.1448 | 3.0304 | 2.9114 | -119.9066 | 3.0304 | 3.0579 | 0.14648 | -120.0394 | -0.013733 | -0.10986 | -122.9645 | 0.045776 | -0.027466 | 0.082397 | -122.9965 | 3.1586 | 3.0258 | 2.9938 | -120.1538 | 0.10071 | 0.068664 | 0.059509 | -123.175
831.8438 | 123.1018 | -3.0396 | 120.1263 | 0.32021 | 0.18504 | 0.13651 | 0.080381 | 0.11239 | 0.014001 | 0.03129 | 0.22992 | 0.18594 | 0.0010951 | 0.18917 | 0.022493 | -0.027656 | -0.036621 | -0.059509 | -0.082397 | -0.022888 | 0.11902 | -0.022888 | -0.13275 | -3.0533 | -3.0441 | -3.1128 | -2.8656 | -2.8839 | -3.0533 | -3.1265 | 3.0167 | 2.9068 | -120.0073 | 2.98 | 3.0167 | 0.10986 | -120.163 | -0.013733 | -0.086975 | -122.9919 | -0.013733 | -0.073242 | 0.013733 | -123.0103 | 3.1586 | 3.0029 | 2.9572 | -120.2591 | 0.17395 | 0.15564 | -0.004577 | -123.2529
832.8438 | 123.1247 | -2.98 | 120.1904 | 0.44228 | 0.18076 | 0.13224 | 0.070768 | 0.11346 | 0.0033197 | 0.035562 | -1.006 | 0.21157 | 0.020321 | 0.20198 | 0.016085 | -0.024451 | -0.045776 | -0.064087 | 0 | -0.050354 | 0.15564 | 0 | -0.12817 | -2.9526 | -2.9755 | -3.0624 | -2.7924 | -2.8336 | -3.0029 | -3.0853 | 2.98 | 2.8519 | -120.0348 | 2.916 | 2.9297 | 0.07782 | -120.2362 | -0.022888 | -0.10528 | -122.9828 | 0.027466 | -0.082397 | 0.022888 | -123.024 | 3.1357 | 2.9343 | 2.98 | -120.3186 | 0.18768 | 0.14649 | 0.004578 | -123.2758
833.8438 | 123.1201 | -2.9572 | 120.2179 | 0.22866 | 0.18504 | 0.14719 | 0.07504 | 0.11453 | 0.012933 | 0.033426 | -0.029479 | 0.20089 | 0.0021631 | 0.18169 | 0.021425 | -0.031928 | -0.027466 | -0.045776 | -0.091553 | -0.018311 | 0.1236 | -0.022888 | -0.16479 | -2.9251 | -2.8976 | -3.0029 | -2.7603 | -2.8015 | -2.9526 | -3.0167 | 2.9343 | 2.7924 | -120.0943 | 2.9114 | 2.9388 | 0.14648 | -120.2454 | 0.004577 | -0.05951 | -122.9782 | 0.032043 | -0.045777 | 0.013733 | -123.0194 | 3.0807 | 2.9297 | 2.8656 | -120.3827 | 0.19684 | 0.15564 | 0.059509 | -123.2346
834.8438 | 123.1659 | -2.8748 | 120.2774 | -0.51902 | 0.18824 | 0.13972 | 0.067564 | 0.12308 | 0.015069 | 0.038766 | -0.090514 | 0.19982 | -0.0074499 | 0.17635 | 0.026766 | -0.026588 | 0.045776 | 0.050354 | -0.027466 | 0.013733 | 0.15564 | 0.032043 | -0.11902 | -2.8336 | -2.8152 | -2.9205 | -2.7237 | -2.7603 | -2.9114 | -2.9709 | 2.9068 | 2.7557 | -120.1218 | 2.9251 | 2.8885 | 0.13275 | -120.2316 | -0.036621 | -0.09613 | -123.0011 | 0.041199 | -0.045776 | 0.050354 | -123.0377 | 3.0304 | 2.9205 | 2.8473 | -120.3964 | 0.15106 | 0.11444 | 0.059509 | -123.2483
835.8438 | 123.1796 | -2.8519 | 120.3369 | 0.10659 | 0.17649 | 0.1301 | 0.060087 | 0.11667 | 0.030023 | 0.049448 | -0.044738 | 0.19128 | -0.0031779 | 0.19237 | 0.02463 | -0.026588 | 0.10071 | 0.064087 | -0.041199 | 0.027466 | 0.18768 | 0.086975 | -0.041199 | -2.8015 | -2.7695 | -2.8793 | -2.6459 | -2.6871 | -2.861 | -2.9251 | 2.9388 | 2.8107 | -120.1492 | 2.916 | 2.8793 | 0.068665 | -120.2362 | -0.009155 | -0.073242 | -122.9828 | 0.050354 | -0.027465 | 0.045777 | -123.024 | 3.0396 | 2.9526 | 2.8107 | -120.3781 | 0.20599 | 0.1648 | 0.082398 | -123.262
836.8438 | 123.1064 | -2.7786 | 120.3781 | 0.2897 | 0.19251 | 0.14078 | 0.072904 | 0.10812 | 0.010797 | 0.047311 | 0.38251 | 0.20409 | 0.0032311 | 0.19344 | 0.017153 | -0.023383 | -0.045776 | -0.054932 | -0.09613 | -0.004578 | 0.1236 | -0.027466 | -0.16479 | -2.8061 | -2.7832 | -2.8976 | -2.6184 | -2.6413 | -2.7969 | -2.8793 | 2.7512 | 2.6138 | -120.2545 | 2.7237 | 2.774 | 0.16022 | -120.4239 | -0.018311 | -0.10071 | -122.9965 | -0.027466 | -0.11902 | -0.018311 | -123.0194 | 2.9022 | 2.7328 | 2.6825 | -120.5429 | 0.16022 | 0.13733 | -0.004578 | -123.2574
837.8438 | 123.1201 | -2.7512 | 120.4239 | 0.2897 | 0.17863 | 0.13865 | 0.072904 | 0.1156 | 0.012933 | 0.040903 | -0.044738 | 0.20196 | -0.0010409 | 0.19237 | 0.0075399 | -0.02552 | -0.059509 | -0.059509 | -0.09613 | -0.022888 | 0.11902 | -0.022888 | -0.16937 | -2.7603 | -2.742 | -2.8427 | -2.5681 | -2.5955 | -2.7695 | -2.8336 | 2.7283 | 2.5818 | -120.3049 | 2.6917 | 2.7283 | 0.14649 | -120.4834 | -0.01831 | -0.082397 | -122.9919 | -0.009155 | -0.091552 | -0.009155 | -123.0194 | 2.8702 | 2.6917 | 2.655 | -120.5933 | 0.18311 | 0.15564 | 0.009156 | -123.2574
838.8438 | 123.0972 | -2.7237 | 120.4559 | 0.2134 | 0.17649 | 0.1504 | 0.061155 | 0.1156 | 0.019342 | 0.039835 | 0.016297 | 0.19875 | 0.018185 | 0.20519 | 0.020357 | -0.023383 | -0.027466 | -0.045776 | -0.10529 | 0.004578 | 0.11902 | -0.032043 | -0.16022 | -2.7237 | -2.6962 | -2.774 | -2.5497 | -2.5772 | -2.7374 | -2.8152 | 2.6917 | 2.5635 | -120.3369 | 2.6779 | 2.7283 | 0.16479 | -120.4834 | -0.013733 | -0.091553 | -123.0057 | 0 | -0.050354 | 0.041199 | -123.0331 | 2.8427 | 2.6962 | 2.6184 | -120.6162 | 0.17395 | 0.14649 | 0.027466 | -123.2712
839.8438 | 123.2437 | -2.6779 | 120.4376 | 0.56436 | 0.14979 | 0.13758 | 0.068632 | 0.11987 | -0.0030893 | 0.033426 | 0.47406 | 0.19982 | -0.0063819 | 0.18062 | 0.0011309 | 0.0033199 | 0.054932 | 0.07782 | 0.041199 | 0.07782 | 0.09613 | 0.022888 | -0.10529 | -2.5497 | -2.742 | -2.8244 | -2.5635 | -2.5772 | -2.6871 | -2.7649 | 2.7008 | 2.5726 | -120.3415 | 2.7557 | 2.7557 | 0.18311 | -120.3827 | -0.009156 | -0.086976 | -123.0011 | 0.12817 | -0.14649 | -0.059509 | -123.0148 | 2.774 | 2.7328 | 2.7191 | -120.5429 | 0.11444 | 0.10071 | -0.064087 | -123.2025
840.8438 | 123.1155 | -2.6413 | 120.5154 | 0.27444 | 0.16261 | 0.14078 | 0.065427 | 0.10919 | 0.0033197 | 0.040903 | 0.092591 | 0.19875 | -0.0053139 | 0.18383 | 0.013948 | -0.026588 | -0.022888 | -0.064087 | -0.086975 | 0.009155 | 0.13733 | -0.036621 | -0.15106 | -2.6505 | -2.6459 | -2.7374 | -2.449 | -2.4719 | -2.6459 | -2.7191 | 2.6047 | 2.4902 | -120.3781 | 2.5772 | 2.6505 | 0.16022 | -120.5383 | -0.004578 | -0.07782 | -122.9645 | -0.009156 | -0.096131 | -0.018311 | -122.9874 | 2.7786 | 2.6184 | 2.5543 | -120.6665 | 0.19226 | 0.16937 | -0.004578 | -123.2346
841.8438 | 123.1888 | -2.5177 | 120.5795 | -0.076513 | 0.1594 | 0.14292 | 0.0697 | 0.11346 | 0.0097277 | 0.040903 | -0.15155 | 0.19662 | 0.0075041 | 0.18917 | 0.0096759 | -0.018043 | 0.032043 | 0.022888 | -0.041199 | 0.032043 | 0.11444 | -0.009155 | -0.14191 | -2.3804 | -2.3987 | -2.4628 | -2.3987 | -2.4216 | -2.5452 | -2.6184 | 2.5085 | 2.3758 | -120.4651 | 2.5406 | 2.5497 | 0.17395 | -120.5475 | -0.027466 | -0.10071 | -122.9782 | 0.13733 | 0.054931 | 0.15564 | -123.0011 | 2.6321 | 2.5497 | 2.4765 | -120.7214 | 0.11902 | 0.09613 | 0.11902 | -123.1979
842.8438 | 123.175 | -2.536 | 120.6207 | -0.33591 | 0.16261 | 0.15146 | 0.066496 | 0.12414 | 0.015069 | 0.041971 | -0.12103 | 0.19875 | 0.036343 | 0.17955 | 0.0096759 | -0.023383 | 0.041199 | 0.013733 | -0.045776 | 0.027466 | 0.12817 | -0.018311 | -0.15564 | -2.4948 | -2.4582 | -2.5497 | -2.3849 | -2.4216 | -2.5635 | -2.6413 | 2.5177 | 2.3804 | -120.4926 | 2.5497 | 2.5635 | 0.18311 | -120.5795 | -0.027466 | -0.10529 | -123.0057 | 0.041199 | -0.013733 | 0.091552 | -123.0423 | 2.6642 | 2.5772 | 2.4902 | -120.7764 | 0.15106 | 0.11444 | 0.07782 | -123.262
844.1094 | 123.2666 | -2.4536 | 120.6619 | 0.12185 | 0.12202 | 0.13544 | 0.0697 | 0.099578 | -0.034064 | 0.021677 | 0.10785 | 0.18594 | -0.02454 | 0.18703 | 0.0021989 | -0.0084301 | 0.004578 | 0.086975 | 0.027466 | 0.050354 | 0.1236 | 0.041199 | -0.09613 | -2.3987 | -2.3483 | -2.4078 | -2.3575 | -2.3849 | -2.4811 | -2.5589 | 2.4948 | 2.3575 | -120.5383 | 2.5406 | 2.504 | 0.14648 | -120.6573 | -0.027466 | -0.10529 | -123.0194 | 0.054931 | 0.045776 | 0.15106 | -123.0469 | 2.5772 | 2.4582 | 2.4811 | -120.7581 | 0.09613 | 0.068664 | 0.10528 | -123.2208
846.0156 | 123.2254 | -2.3987 | 120.7031 | 0.70168 | 0.17542 | 0.1504 | 0.046201 | 0.11453 | -0.022315 | 0.03663 | 0.22992 | 0.18487 | -0.017063 | 0.17742 | 0.0064719 | -0.018043 | -0.022888 | 0.045776 | -0.004578 | 0.045776 | 0.086975 | 0 | -0.1236 | -2.3529 | -2.3163 | -2.3895 | -2.2888 | -2.33 | -2.4216 | -2.5131 | 2.3987 | 2.2751 | -120.6162 | 2.4445 | 2.4445 | 0.16937 | -120.726 | -0.022888 | -0.11444 | -122.9919 | 0.045777 | 0.009156 | 0.1236 | -123.0331 | 2.4857 | 2.3758 | 2.3941 | -120.8267 | 0.10986 | 0.068665 | 0.082398 | -123.2162
846.8438 | 123.1705 | -2.4399 | 120.6894 | 0.19814 | 0.19465 | 0.13544 | 0.083585 | 0.11346 | 0.02575 | 0.032358 | -0.15155 | 0.20196 | 0.0085721 | 0.18383 | 0.020357 | -0.035133 | 0.041199 | -0.032043 | -0.10071 | -0.009155 | 0.12817 | 0 | -0.15564 | -2.4078 | -2.4033 | -2.4948 | -2.2568 | -2.298 | -2.4765 | -2.5406 | 2.4399 | 2.2842 | -120.5612 | 2.4078 | 2.4307 | 0.14649 | -120.6482 | -0.036621 | -0.10071 | -122.9462 | 0.032043 | -0.054932 | 0.045776 | -122.9874 | 2.5681 | 2.4811 | 2.3392 | -120.845 | 0.1831 | 0.14191 | 0.036621 | -123.23
848.25 | 123.2117 | -2.3575 | 120.7443 | 0.24392 | 0.13804 | 0.14399 | 0.070768 | 0.1156 | -0.012702 | 0.029153 | 0.2757 | 0.17739 | 0.0032311 | 0.17635 | -0.0031411 | -0.018043 | -0.009155 | 0.036621 | -0.009155 | 0.018311 | 0.10071 | 0.009155 | -0.10071 | -2.2934 | -2.2797 | -2.3392 | -2.211 | -2.2659 | -2.3666 | -2.4216 | 2.3666 | 2.2568 | -120.6436 | 2.3941 | 2.3758 | 0.11902 | -120.7535 | -0.009155 | -0.064087 | -122.9553 | 0.064087 | 0.018311 | 0.082398 | -123.0103 | 2.4582 | 2.3483 | 2.3483 | -120.845 | 0.14648 | 0.091553 | 0.07782 | -123.1659
849.0156 | 123.2437 | -2.3163 | 120.8038 | -0.29014 | 0.14872 | 0.15894 | 0.055814 | 0.12094 | 0.00011475 | 0.029153 | -0.22784 | 0.18807 | -0.0042459 | 0.17955 | 0.0043349 | -0.018043 | 0.07782 | 0.10071 | 0.045776 | 0.068665 | 0.11902 | 0.013733 | -0.091553 | -2.2385 | -2.1927 | -2.298 | -2.2018 | -2.2385 | -2.3346 | -2.4216 | 2.33 | 2.2247 | -120.6848 | 2.417 | 2.3849 | 0.16022 | -120.726 | -0.018311 | -0.10529 | -123.0057 | 0.07782 | 0.01831 | 0.1236 | -123.0423 | 2.4353 | 2.3941 | 2.3621 | -120.8954 | 0.11444 | 0.07782 | 0.1236 | -123.2254
849.8438 | 123.1476 | -2.3254 | 120.845 | 0.24392 | 0.16154 | 0.13651 | 0.076109 | 0.12201 | 0.023614 | 0.034494 | 0.046815 | 0.19341 | -0.0021099 | 0.17955 | 0.022493 | -0.038337 | -0.004578 | -0.07782 | -0.12817 | -0.022888 | 0.15106 | -0.013733 | -0.15106 | -2.3026 | -2.3346 | -2.4216 | -2.1515 | -2.1652 | -2.3483 | -2.4124 | 2.3117 | 2.1744 | -120.694 | 2.2476 | 2.3026 | 0.12817 | -120.8496 | -0.022889 | -0.086976 | -122.9965 | 0.022888 | -0.096131 | -0.009155 | -123.0103 | 2.4765 | 2.3209 | 2.1973 | -120.9961 | 0.17395 | 0.16022 | -0.009156 | -123.2574
850.9062 | 123.23 | -2.2522 | 120.8862 | -0.58005 | 0.13163 | 0.1536 | 0.055814 | 0.1156 | -0.01377 | 0.027017 | -0.2431 | 0.19769 | -0.0010409 | 0.15819 | 0.015017 | -0.020179 | 0.054932 | 0.10986 | 0.050354 | 0.082397 | 0.091553 | 0.018311 | -0.1236 | -2.1698 | -2.1149 | -2.2339 | -2.1332 | -2.1698 | -2.2934 | -2.3483 | 2.2705 | 2.1286 | -120.7947 | 2.3621 | 2.3346 | 0.20599 | -120.8313 | -0.041199 | -0.096131 | -123.0194 | 0.082397 | 0.01831 | 0.11444 | -123.056 | 2.3438 | 2.3071 | 2.3026 | -121.0098 | 0.11902 | 0.082397 | 0.13733 | -123.2346
851.8594 | 123.2391 | -2.2476 | 120.8817 | 0.16763 | 0.12095 | 0.14185 | 0.060087 | 0.11453 | -0.018043 | 0.028085 | -2.4709 | 0.17953 | 2.7137e-05 | 0.1678 | 0.0021989 | -0.028724 | 0.009155 | 0.041199 | -0.018311 | 0.050354 | 0.11444 | 0.013733 | -0.13733 | -2.1973 | -2.1973 | -2.2705 | -2.1515 | -2.2018 | -2.3026 | -2.3621 | 2.2614 | 2.1103 | -120.7672 | 2.2888 | 2.298 | 0.18768 | -120.8725 | -0.054931 | -0.11444 | -123.0331 | 0.050354 | -0.022888 | 0.091553 | -123.0835 | 2.3621 | 2.2568 | 2.2293 | -121.019 | 0.096131 | 0.045777 | 0.050354 | -123.2437
852.9062 | 123.2025 | -2.2202 | 120.7764 | 0.53384 | 0.13056 | 0.15787 | 0.055814 | 0.10919 | 0.0022517 | 0.027017 | 0.15363 | 0.19128 | -0.012791 | 0.18596 | 0.019289 | -0.020179 | 0.004578 | 0.041199 | -0.013733 | 0.032043 | 0.12817 | 0.018311 | -0.10529 | -2.1515 | -2.1423 | -2.2156 | -2.0828 | -2.1378 | -2.2156 | -2.2888 | 2.2385 | 2.1149 | -120.6482 | 2.2614 | 2.2522 | 0.13733 | -120.7718 | 0.004578 | -0.068664 | -122.8592 | 0.068665 | 0.004578 | 0.073242 | -122.9141 | 2.3483 | 2.2247 | 2.2064 | -120.8817 | 0.13733 | 0.082398 | 0.07782 | -123.0652
853.8438 | 123.1796 | -2.211 | 120.9595 | 0.030298 | 0.1829 | 0.13544 | 0.091062 | 0.10492 | 0.022546 | 0.034494 | -0.36517 | 0.19341 | -0.0031779 | 0.16353 | 0.016085 | -0.041541 | 0.045776 | 0.027466 | -0.022888 | 0.041199 | 0.14191 | -0.013733 | -0.14648 | -2.1149 | -2.1194 | -2.2247 | -2.0599 | -2.0737 | -2.2064 | -2.2888 | 2.1973 | 2.0645 | -120.8176 | 2.2385 | 2.2522 | 0.18768 | -120.9137 | 0.004578 | -0.077819 | -123.0194 | 0.096131 | -0.013732 | 0.064087 | -123.0331 | 2.3529 | 2.2568 | 2.1881 | -121.106 | 0.15106 | 0.13733 | 0.091553 | -123.2483
854.9062 | 123.2162 | -2.1515 | 120.9732 | -0.19858 | 0.13163 | 0.1536 | 0.045133 | 0.11667 | -0.015906 | 0.043039 | -0.47198 | 0.1838 | -0.02454 | 0.1678 | 0.010744 | -0.022315 | 0.059509 | 0.09613 | 0.041199 | 0.073242 | 0.10986 | 0.009155 | -0.10986 | -2.0828 | -2.0187 | -2.1149 | -2.0416 | -2.0554 | -2.1561 | -2.2522 | 2.1606 | 2.0416 | -120.8633 | 2.2476 | 2.2247 | 0.18311 | -120.9137 | -0.004578 | -0.10071 | -123.0148 | 0.068664 | 0.036621 | 0.13733 | -123.0286 | 2.2614 | 2.211 | 2.1927 | -121.0831 | 0.10986 | 0.09613 | 0.13275 | -123.2254
855.8438 | 123.1567 | -2.179 | 121.0464 | -0.13755 | 0.14445 | 0.1504 | 0.079313 | 0.1188 | 0.0086597 | 0.039835 | -0.5025 | 0.19234 | 0.0021631 | 0.18276 | 0.0086079 | -0.018043 | -0.032043 | 0.009155 | -0.064087 | -0.004578 | 0.14648 | -0.013733 | -0.15106 | -2.1057 | -2.1057 | -2.1973 | -1.973 | -2.0096 | -2.1835 | -2.243 | 2.1652 | 2.0279 | -120.9 | 2.1881 | 2.1744 | 0.14648 | -121.0785 | -0.004578 | -0.064087 | -123.0194 | 0.073242 | -0.018311 | 0.045776 | -123.056 | 2.3254 | 2.1469 | 2.1149 | -121.1975 | 0.20599 | 0.16937 | 0.073242 | -123.2895
856.8438 | 123.1338 | -2.1378 | 121.051 | 0.48806 | 0.16474 | 0.13651 | 0.07504 | 0.11026 | 0.030023 | 0.043039 | 0.077332 | 0.20409 | 0.0053671 | 0.18169 | 0.02463 | -0.026588 | -0.027466 | -0.059509 | -0.10529 | -0.022888 | 0.15106 | -0.022888 | -0.14648 | -2.092 | -2.1194 | -2.1973 | -1.9455 | -1.9775 | -2.1286 | -2.1973 | 2.1149 | 1.9913 | -120.9 | 2.0782 | 2.1149 | 0.1236 | -121.0785 | 0.009155 | -0.05951 | -122.9965 | 0.045776 | -0.05951 | 0 | -123.0286 | 2.2888 | 2.1103 | 2.0325 | -121.1975 | 0.19226 | 0.16022 | 0.01831 | -123.2483
857.9062 | 123.262 | -2.0691 | 121.0648 | 0.86953 | 0.14124 | 0.14826 | 0.057951 | 0.11453 | -0.026587 | 0.03663 | 0.046815 | 0.1838 | -0.011723 | 0.17742 | 0.011812 | -0.020179 | -0.032043 | 0.041199 | -0.013733 | 0.022888 | 0.082397 | -0.018311 | -0.13733 | -1.9958 | -1.9638 | -2.0462 | -1.9501 | -1.973 | -2.0737 | -2.1515 | 2.0508 | 1.9318 | -120.9824 | 2.1103 | 2.092 | 0.16022 | -121.0968 | -0.004577 | -0.082397 | -123.0148 | 0.073242 | 0.022888 | 0.10529 | -123.0377 | 2.1515 | 2.037 | 2.0554 | -121.2021 | 0.11902 | 0.096131 | 0.10529 | -123.2162
858.8438 | 123.1659 | -2.0828 | 121.1105 | -0.32065 | 0.1562 | 0.14719 | 0.07504 | 0.10492 | 0.0022517 | 0.025949 | -0.56354 | 0.19769 | -0.0074499 | 0.18489 | 0.0064719 | -0.023383 | 0.10986 | 0.21515 | -0.013733 | -0.032043 | 0.19226 | 0.036621 | -0.10071 | -2.0233 | -2.0233 | -2.1286 | -1.8585 | -1.9272 | -2.0874 | -2.1652 | 2.1194 | 1.9821 | -120.9183 | 2.298 | 2.0508 | 0.068665 | -121.0007 | -0.004577 | -0.082397 | -122.9691 | 0.05951 | -0.045776 | 0.036621 | -123.0377 | 2.2751 | 2.1927 | 2.0691 | -121.2112 | 0.2243 | 0.15564 | 0.05951 | -123.2758
859.9062 | 123.262 | -2.0233 | 121.1288 | -0.16807 | 0.13697 | 0.15253 | 0.046201 | 0.10919 | -0.01377 | 0.034494 | -0.19733 | 0.19021 | -0.018131 | 0.18169 | -0.015959 | -0.014838 | 0.068665 | 0.15106 | 0.050354 | 0.073242 | 0.11444 | 0.004578 | -0.10986 | -1.8677 | -2.1423 | -1.9958 | -1.918 | -1.9638 | -2.0416 | -2.1149 | 2.0279 | 1.9135 | -121.0144 | 2.1744 | 2.0966 | 0.18311 | -121.0602 | -0.018311 | -0.091553 | -123.0469 | 0.15564 | 0.027465 | 0.11902 | -123.0927 | 2.1378 | 2.092 | 2.0737 | -121.2387 | 0.10529 | 0.059509 | -0.11902 | -123.2437
860.8438 | 123.1796 | -2.0325 | 121.1609 | -0.19858 | 0.14872 | 0.14185 | 0.070768 | 0.11239 | -0.0020213 | 0.041971 | -0.44147 | 0.19341 | -0.0010409 | 0.18489 | 0.018221 | -0.029792 | -0.013733 | 0.041199 | -0.07782 | -0.022888 | 0.14648 | -0.027466 | -0.15564 | -1.973 | -1.9775 | -2.0645 | -1.8219 | -1.8906 | -2.037 | -2.1103 | 2.005 | 1.8768 | -121.0144 | 2.0737 | 2.0096 | 0.13275 | -121.1746 | -0.004577 | -0.07782 | -122.9828 | 0.05951 | -0.032043 | 0.045777 | -123.0515 | 2.179 | 2.0187 | 1.9547 | -121.3165 | 0.21057 | 0.14191 | 0.054932 | -123.2712
861.9062 | 123.1979 | -2.005 | 121.1655 | -0.27488 | 0.16047 | 0.13865 | 0.096403 | 0.11133 | 0.028955 | 0.046243 | -0.47198 | 0.19234 | 0.021389 | 0.17208 | 0.017153 | -0.028724 | -0.004578 | -0.018311 | -0.073242 | 0.004578 | 0.14648 | -0.027466 | -0.16937 | -1.9409 | -1.9226 | -2.0325 | -1.8448 | -1.8768 | -2.0142 | -2.1011 | 1.9775 | 1.8356 | -121.019 | 1.9867 | 2.0096 | 0.17395 | -121.17 | -0.009155 | -0.09613 | -123.0103 | 0.064087 | -0.027466 | 0.068664 | -123.0423 | 2.1515 | 2.0004 | 1.9318 | -121.3348 | 0.16022 | 0.12817 | 0.082398 | -123.2666
862.8438 | 123.262 | -1.9318 | 121.2067 | -0.19858 | 0.12736 | 0.1739 | 0.078245 | 0.10065 | 0.0075917 | 0.034494 | -0.21259 | 0.19021 | -0.0074499 | 0.17955 | 0.0043349 | -0.029792 | 0.018311 | 0.054932 | 0.022888 | 0.073242 | 0.091553 | 0.004578 | -0.11902 | -1.8356 | -1.7807 | -1.8906 | -1.8448 | -1.8723 | -1.9684 | -2.0187 | 1.9363 | 1.8127 | -121.1151 | 1.9867 | 2.005 | 0.19226 | -121.1884 | -0.036621 | -0.086975 | -123.0515 | 0.096131 | 0.041199 | 0.12817 | -123.0789 | 2.0233 | 1.9501 | 1.9547 | -121.3257 | 0.086975 | 0.05951 | 0.15106 | -123.2254
863.9062 | 123.2803 | -1.9547 | 121.1655 | 0.71694 | 0.16367 | 0.13972 | 0.077177 | 0.1188 | 0.011865 | 0.043039 | 0.33673 | 0.18487 | 0.0085721 | 0.18489 | 0.021425 | -0.02552 | 0.068665 | 0.11902 | 0.050354 | 0.073242 | 0.09613 | 0.013733 | -0.09613 | -1.9272 | -2.1103 | -1.8585 | -1.8311 | -1.8951 | -1.9867 | -2.0416 | 1.9684 | 1.8585 | -121.0693 | 2.0737 | 2.0279 | 0.16937 | -121.0968 | -0.032043 | -0.086975 | -122.9965 | 0.027466 | 0.09613 | 0.1831 | -123.0606 | 2.0508 | 2.0233 | 2.005 | -121.2616 | 0.1236 | 0.059509 | -0.15564 | -123.2071
864.8438 | 123.2117 | -1.8723 | 121.2753 | -0.030737 | 0.16688 | 0.14506 | 0.072904 | 0.10919 | 0.02575 | 0.032358 | -0.22784 | 0.20409 | 0.012844 | 0.18062 | 0.022493 | -0.029792 | 0.059509 | 0.050354 | -0.036621 | 0.027466 | 0.13733 | -0.013733 | -0.15106 | -1.8173 | -1.8127 | -1.8997 | -1.6983 | -1.7532 | -1.8906 | -1.9592 | 1.8585 | 1.7212 | -121.138 | 1.9226 | 1.8997 | 0.17853 | -121.2158 | -0.018311 | -0.086976 | -122.9736 | 0.054931 | -0.027466 | 0.05951 | -123.0286 | 2.0096 | 1.9318 | 1.8356 | -121.4264 | 0.17395 | 0.11902 | 0.059509 | -123.2346
865.9062 | 123.2391 | -1.886 | 121.2524 | 0.2897 | 0.12736 | 0.1536 | 0.056883 | 0.10812 | -0.01377 | 0.033426 | -0.01422 | 0.1806 | -0.0074499 | 0.17635 | 0.0064719 | -0.0084301 | -0.013733 | 0 | -0.16479 | -0.064087 | 0.07782 | -0.022888 | -0.16937 | -1.799 | -1.7807 | -1.8494 | -1.7853 | -1.8173 | -1.8906 | -1.9638 | 1.8631 | 1.7166 | -121.1746 | 1.886 | 1.8219 | 0.10529 | -121.2662 | -0.004578 | -0.07782 | -123.0377 | 0.086975 | 0.036621 | 0.11444 | -123.0698 | 1.9638 | 1.8723 | 1.7212 | -121.4218 | 0.10071 | 0.068664 | 0.10528 | -123.2162
866.8438 | 123.1705 | -1.886 | 121.2982 | 0.48806 | 0.17222 | 0.11408 | 0.054746 | 0.11239 | 0.0054557 | 0.046243 | 0.16888 | 0.19341 | 0.016048 | 0.19985 | 0.026766 | -0.023383 | -0.054932 | 0.009155 | -0.07782 | -0.018311 | 0.15564 | -0.004578 | -0.14191 | -1.8173 | -1.8723 | -1.9318 | -1.6937 | -1.7532 | -1.8997 | -1.9638 | 1.8814 | 1.7441 | -121.1426 | 1.8951 | 1.8677 | 0.1236 | -121.3531 | -0.013733 | -0.07782 | -122.9919 | 0.068664 | -0.045777 | 0.032043 | -123.0515 | 2.0416 | 1.8311 | 1.8082 | -121.4401 | 0.19226 | 0.13275 | 0.013733 | -123.262
867.9062 | 123.2391 | -1.8082 | 121.3348 | 0.41177 | 0.13911 | 0.15253 | 0.054746 | 0.098509 | -0.01377 | 0.030222 | 0.21466 | 0.19128 | 0.0075041 | 0.16994 | 0.0064719 | -0.022315 | 0 | 0.059509 | -0.004578 | 0.018311 | 0.10529 | 0.032043 | -0.10986 | -1.7487 | -1.7349 | -1.8127 | -1.6846 | -1.7487 | -1.8448 | -1.918 | 1.8402 | 1.6983 | -121.2296 | 1.8677 | 1.8265 | 0.12817 | -121.3348 | -0.036621 | -0.10986 | -123.0194 | 0.05951 | -0.004577 | 0.10529 | -123.0835 | 1.9135 | 1.8082 | 1.8036 | -121.4447 | 0.1236 | 0.05951 | 0.073243 | -123.2529
868.8438 | 123.2758 | -1.7944 | 121.3074 | -0.076513 | 0.12736 | 0.14292 | 0.070768 | 0.11453 | -0.00095325 | 0.033426 | -0.22784 | 0.187 | -0.0042459 | 0.18169 | -0.0042101 | -0.021247 | 0.068665 | 0.13275 | 0.059509 | 0.07782 | 0.10529 | 0.022888 | -0.11902 | -1.7487 | -1.712 | -1.7532 | -1.7029 | -1.7532 | -1.8539 | -1.9089 | 1.8173 | 1.6754 | -121.2021 | 1.9272 | 1.8723 | 0.19684 | -121.2387 | -0.059509 | -0.11444 | -123.0103 | 0.045777 | 0.041199 | 0.15564 | -123.0606 | 1.8997 | 1.8631 | 1.8539 | -121.4264 | 0.091553 | 0.041199 | 0.082398 | -123.2162
869.9062 | 123.2758 | -1.7853 | 121.344 | -0.13755 | 0.12095 | 0.15894 | 0.054746 | 0.11667 | -0.011634 | 0.027017 | -0.19733 | 0.18166 | -0.0021099 | 0.17208 | 0.0021989 | -0.044746 | 0.07782 | 0.15106 | 0.050354 | 0.07782 | 0.10986 | 0.009155 | -0.1236 | -1.6846 | -1.7349 | -1.8173 | -1.6617 | -1.7303 | -1.8356 | -1.8814 | 1.7944 | 1.6617 | -121.2341 | 1.9363 | 1.8631 | 0.20142 | -121.2662 | -0.050354 | -0.096131 | -123.0057 | 0.10071 | -0.032044 | 0.064087 | -123.0743 | 1.8951 | 1.8631 | 1.8356 | -121.4676 | 0.1236 | 0.054931 | 0.050354 | -123.2254
870.8438 | 123.3078 | -1.7532 | 121.3669 | -0.00022031 | 0.1327 | 0.15787 | 0.05261 | 0.11239 | 0.0043877 | 0.018472 | -0.28888 | 0.17632 | 2.7137e-05 | 0.16567 | 0.0064719 | -0.016975 | 0.073242 | 0.12817 | 0.059509 | 0.064087 | 0.12817 | 0.036621 | -0.10071 | -1.6022 | -1.5839 | -1.6663 | -1.6525 | -1.7212 | -1.7853 | -1.8402 | 1.7899 | 1.6525 | -121.2387 | 1.8814 | 1.8173 | 0.1648 | -121.2936 | -0.032043 | -0.086975 | -123.0194 | 0.15106 | 0.086975 | 0.17395 | -123.0881 | 1.8814 | 1.8265 | 1.8127 | -121.4676 | 0.10071 | 0.032044 | 0.16937 | -123.2071
871.9062 | 123.1567 | -1.7761 | 121.4264 | -1.0226 | 0.15086 | 0.14612 | 0.055814 | 0.12842 | 0.021478 | 0.03129 | -0.56354 | 0.19555 | -0.010654 | 0.19237 | 0.020357 | -0.031928 | 0.004578 | -0.018311 | -0.07782 | 0.004578 | 0.17853 | 0.009155 | -0.15106 | -1.7395 | -1.7258 | -1.8036 | -1.5884 | -1.6525 | -1.799 | -1.8906 | 1.7853 | 1.6251 | -121.2479 | 1.7578 | 1.7807 | 0.15564 | -121.4218 | -0.022888 | -0.11444 | -123.0148 | 0.036621 | -0.027466 | 0.086975 | -123.0789 | 1.9547 | 1.7807 | 1.6983 | -121.5775 | 0.18768 | 0.1236 | 0.050354 | -123.317
872.8438 | 123.2895 | -1.7441 | 121.3898 | 0.030298 | 0.12736 | 0.13758 | 0.062223 | 0.11453 | -0.00095325 | 0.027017 | -0.19733 | 0.17739 | -0.010654 | 0.18489 | 0.0096759 | -0.014838 | 0.07782 | 0.16937 | 0.068665 | 0.07782 | 0.11444 | 0.013733 | -0.11444 | -1.6022 | -1.561 | -1.6388 | -1.6113 | -1.6708 | -1.7349 | -1.8173 | 1.7578 | 1.6296 | -121.2753 | 1.9135 | 1.8219 | 0.19226 | -121.312 | 0.009156 | -0.073242 | -123.0011 | 0.14191 | 0.10529 | 0.17853 | -123.0606 | 1.8585 | 1.8219 | 1.8127 | -121.5042 | 0.13275 | 0.073243 | 0.18311 | -123.2071
873.8438 | 123.3124 | -1.6983 | 121.4172 | -0.00022031 | 0.12949 | 0.15787 | 0.067564 | 0.11133 | -0.0094983 | 0.022745 | -0.2431 | 0.18594 | -0.010654 | 0.17528 | 0.0021989 | -0.019111 | 0.07782 | 0.14648 | 0.059509 | 0.07782 | 0.11444 | 0.032043 | -0.10071 | -1.561 | -1.5427 | -1.6113 | -1.6113 | -1.6617 | -1.7212 | -1.8082 | 1.7303 | 1.5976 | -121.3028 | 1.8448 | 1.7761 | 0.17853 | -121.3394 | -0.022888 | -0.10986 | -123.0286 | 0.13733 | 0.086975 | 0.19684 | -123.0789 | 1.8127 | 1.7761 | 1.7578 | -121.5179 | 0.086975 | 0.036621 | 0.15564 | -123.2254
874.9219 | 123.2254 | -1.6571 | 121.5225 | -0.015478 | 0.16688 | 0.15146 | 0.09213 | 0.11346 | 0.031091 | 0.045175 | -0.38043 | 0.18594 | 0.0032311 | 0.19451 | 0.028902 | -0.034064 | 0.054932 | 0.045776 | -0.032043 | 0.018311 | 0.14648 | -0.004578 | -0.13733 | -1.6296 | -1.6342 | -1.7303 | -1.561 | -1.6159 | -1.7349 | -1.799 | 1.6525 | 1.5198 | -121.376 | 1.7029 | 1.6754 | 0.15564 | -121.4676 | -0.07782 | -0.14191 | -123.0835 | 0.027465 | -0.073243 | 0.068664 | -123.1384 | 1.8036 | 1.712 | 1.6251 | -121.6599 | 0.09613 | 0.041198 | 0.022888 | -123.3215
875.8438 | 123.2986 | -1.6479 | 121.4401 | 0.091333 | 0.12415 | 0.15467 | 0.066496 | 0.11667 | -0.01377 | 0.03129 | -0.34991 | 0.1838 | 2.7137e-05 | 0.19024 | 0.013948 | -0.0073621 | 0.07782 | 0.16937 | 0.082397 | 0.086975 | 0.11444 | 0.022888 | -0.10071 | -1.5427 | -1.506 | -1.6022 | -1.5839 | -1.6159 | -1.7029 | -1.7624 | 1.6708 | 1.5472 | -121.3257 | 1.8173 | 1.7349 | 0.18768 | -121.3623 | -0.054932 | -0.11444 | -123.024 | 0.10529 | 0.045776 | 0.16022 | -123.056 | 1.7624 | 1.7258 | 1.7303 | -121.5408 | 0.064087 | 0.032043 | 0.14191 | -123.2025
876.9062 | 123.1842 | -1.7212 | 121.4859 | -0.29014 | 0.1594 | 0.13651 | 0.083585 | 0.11239 | 0.014001 | 0.027017 | -0.5025 | 0.19769 | 0.020321 | 0.17742 | 0.02463 | -0.037269 | -0.018311 | 0.004578 | -0.091553 | -0.004578 | 0.14648 | -0.050354 | -0.16479 | -1.6525 | -1.6205 | -1.7212 | -1.5152 | -1.5701 | -1.7212 | -1.7944 | 1.6708 | 1.5564 | -121.3394 | 1.7258 | 1.7166 | 0.16022 | -121.5042 | 0 | -0.073243 | -123.0011 | 0.068664 | 0 | 0.073243 | -123.056 | 1.8677 | 1.7029 | 1.6296 | -121.6507 | 0.20599 | 0.15106 | 0.10071 | -123.2803
877.8438 | 123.2437 | -1.6388 | 121.5271 | -0.19858 | 0.14231 | 0.13865 | 0.073972 | 0.10385 | -0.010566 | 0.039835 | -0.33466 | 0.1838 | -0.017063 | 0.17528 | 0.0096759 | -0.028724 | 0.050354 | 0.14191 | 0.045776 | 0.07782 | 0.10986 | 0.009155 | -0.11902 | -1.5427 | -1.4923 | -1.6022 | -1.5244 | -1.561 | -1.6525 | -1.7395 | 1.6479 | 1.5198 | -121.4172 | 1.7807 | 1.7166 | 0.19684 | -121.4767 | -0.013733 | -0.10071 | -123.0515 | 0.09613 | 0.036621 | 0.13733 | -123.0881 | 1.7487 | 1.6891 | 1.6846 | -121.6461 | 0.11444 | 0.07782 | 0.14648 | -123.2666
878.9062 | 123.2803 | -1.6022 | 121.5134 | 2.9905 | 0.17435 | 0.15253 | 0.078245 | 0.11774 | 0.0043877 | 0.027017 | 0.36725 | 0.1806 | -0.0074499 | 0.18169 | 0.010744 | -0.020179 | 0.050354 | 0.10529 | 0.036621 | 0.059509 | 0.059509 | 0.004578 | -0.13733 | -1.4969 | -1.5015 | -1.561 | -1.5289 | -1.5656 | -1.6388 | -1.7029 | 1.6068 | 1.4648 | -121.4539 | 1.7075 | 1.6617 | 0.19684 | -121.463 | -0.036621 | -0.10071 | -123.0423 | 0.10529 | 0.041199 | 0.14191 | -123.0789 | 1.6617 | 1.6525 | 1.6388 | -121.6507 | 0.073242 | 0.036621 | 0.10071 | -123.2162
879.8594 | 123.2803 | -1.593 | 121.5088 | 0.12185 | 0.11347 | 0.15787 | 0.061155 | 0.10171 | -0.012702 | 0.027017 | -0.27362 | 0.18914 | 0.0053671 | 0.17955 | -0.0052781 | -0.021247 | 0.07782 | 0.1831 | 0.07782 | 0.07782 | 0.10071 | 0.027466 | -0.10071 | -1.4786 | -1.4374 | -1.5289 | -1.5152 | -1.5381 | -1.6342 | -1.6983 | 1.6205 | 1.4923 | -121.4081 | 1.7761 | 1.6708 | 0.17853 | -121.431 | -0.041198 | -0.10528 | -123.024 | 0.11444 | 0.064087 | 0.16937 | -123.0469 | 1.6937 | 1.6708 | 1.6708 | -121.6095 | 0.07782 | 0.054932 | 0.15564 | -123.2071
880.8438 | 123.2849 | -1.6342 | 121.4081 | 0.27444 | 0.1359 | 0.1504 | 0.056883 | 0.11026 | -0.0020213 | 0.033426 | 0.077332 | 0.18594 | 2.7137e-05 | 0.19024 | 0.0054039 | -0.021247 | 0.004578 | 0.068665 | 0.004578 | 0.018311 | 0.10529 | 0.022888 | -0.11902 | -1.5289 | -1.5244 | -1.5701 | -1.4877 | -1.5427 | -1.6067 | -1.6891 | 1.6571 | 1.5152 | -121.3028 | 1.7029 | 1.6525 | 0.13733 | -121.4035 | 0.027466 | -0.054932 | -122.8958 | 0.10528 | 0.064087 | 0.11902 | -122.9507 | 1.7395 | 1.6388 | 1.6388 | -121.5271 | 0.14648 | 0.091552 | 0.10986 | -123.0972
881.9062 | 123.2712 | -1.5793 | 121.5363 | 0.50332 | 0.17542 | 0.13224 | 0.067564 | 0.11667 | 0.027886 | 0.028085 | 0.33673 | 0.19234 | 0.0075041 | 0.19558 | 0.02463 | -0.020179 | 0.064087 | 0.11444 | 0.027466 | 0.064087 | 0.1236 | 0.018311 | -0.10071 | -1.4511 | -1.4648 | -1.5427 | -1.4969 | -1.5381 | -1.5976 | -1.6663 | 1.5976 | 1.4786 | -121.4127 | 1.6937 | 1.6434 | 0.1648 | -121.4722 | -0.01831 | -0.086975 | -123.0331 | 0.12817 | 0.036621 | 0.1236 | -123.0743 | 1.7029 | 1.6434 | 1.6068 | -121.637 | 0.082398 | 0.041199 | 0.11444 | -123.2025
882.8438 | 123.2529 | -1.5564 | 121.5775 | 0.25918 | 0.14124 | 0.14826 | 0.065427 | 0.11026 | 0.0022517 | 0.035562 | -0.10577 | 0.18594 | -0.011723 | 0.18703 | 6.2882e-05 | -0.023383 | 0.004578 | 0.09613 | 0.004578 | 0.041199 | 0.13275 | 0.045776 | -0.11444 | -1.4557 | -1.4465 | -1.5015 | -1.4328 | -1.4786 | -1.5656 | -1.6479 | 1.6022 | 1.442 | -121.4447 | 1.6525 | 1.5976 | 0.15564 | -121.5729 | -0.009156 | -0.091553 | -123.0103 | 0.10071 | 0.054931 | 0.14648 | -123.056 | 1.6891 | 1.561 | 1.561 | -121.6919 | 0.1236 | 0.077819 | 0.10986 | -123.2254
883.9062 | 123.1796 | -1.5701 | 121.582 | -4.3642 | 0.15192 | 0.13437 | 0.089994 | 0.10812 | 0.022546 | 0.034494 | 0.046815 | 0.20089 | 0.010708 | 0.1913 | 0.017153 | -0.03086 | 0.004578 | -0.032043 | -0.10986 | -0.004578 | 0.15564 | -0.027466 | -0.12817 | -1.4969 | -1.5701 | -1.6113 | -1.4053 | -1.4694 | -1.5884 | -1.6708 | 1.5427 | 1.442 | -121.4264 | 1.5381 | 1.5656 | 0.1236 | -121.5775 | -0.018311 | -0.10071 | -122.9874 | 0.073242 | -0.041199 | 0.059509 | -123.0515 | 1.7258 | 1.5747 | 1.4603 | -121.7102 | 0.1648 | 0.10071 | 0 | -123.2529
884.8594 | 123.2758 | -1.5289 | 121.582 | -0.00022031 | 0.12095 | 0.14612 | 0.051542 | 0.10065 | -0.018043 | 0.035562 | 0.0010378 | 0.18594 | -0.012791 | 0.17849 | 6.2882e-05 | -0.029792 | 0.054932 | 0.11902 | 0.045776 | 0.07782 | 0.13275 | 0.036621 | -0.10529 | -1.387 | -1.3641 | -1.4465 | -1.4328 | -1.4557 | -1.5335 | -1.6022 | 1.5656 | 1.4236 | -121.4493 | 1.648 | 1.6068 | 0.18311 | -121.5271 | -0.004577 | -0.073242 | -123.0148 | 0.14191 | 0.082398 | 0.15564 | -123.0377 | 1.6617 | 1.5839 | 1.5747 | -121.6873 | 0.096131 | 0.073243 | 0.1648 | -123.1842
885.9062 | 123.1979 | -1.5564 | 121.6415 | 0.12185 | 0.18397 | 0.13865 | 0.072904 | 0.1188 | 0.022546 | 0.054788 | 0.21466 | 0.19982 | 0.023525 | 0.1913 | 0.02463 | -0.03086 | -0.004578 | -0.018311 | -0.091553 | -0.009155 | 0.14191 | -0.032043 | -0.15106 | -1.4465 | -1.5244 | -1.5747 | -1.4008 | -1.4465 | -1.5656 | -1.6434 | 1.5244 | 1.4053 | -121.4996 | 1.5381 | 1.5472 | 0.14191 | -121.6461 | -0.009156 | -0.086976 | -123.0423 | 0.10986 | -0.018311 | 0.068665 | -123.0881 | 1.6983 | 1.5518 | 1.4648 | -121.7926 | 0.15564 | 0.10986 | 0.032043 | -123.2849
886.8438 | 123.262 | -1.5106 | 121.6415 | 0.4728 | 0.1327 | 0.13224 | 0.076109 | 0.11667 | -0.011634 | 0.027017 | 0.12311 | 0.19555 | -0.0085179 | 0.18917 | 0.0032669 | -0.021247 | 0.009155 | 0.064087 | 0 | 0.018311 | 0.10986 | 0.009155 | -0.1236 | -1.4282 | -1.4374 | -1.4923 | -1.4008 | -1.4511 | -1.5427 | -1.6113 | 1.5198 | 1.387 | -121.5317 | 1.5747 | 1.5289 | 0.14191 | -121.6324 | -0.032044 | -0.10071 | -123.0423 | 0.082397 | 0.01831 | 0.11902 | -123.0927 | 1.6205 | 1.5198 | 1.5106 | -121.7651 | 0.10986 | 0.059509 | 0.073242 | -123.2529
887.9062 | 123.1384 | -1.5472 | 121.6599 | 0.16763 | 0.1797 | 0.1269 | 0.079313 | 0.10599 | 0.022546 | 0.044107 | -0.22784 | 0.19875 | 0.0064351 | 0.17315 | 0.02997 | -0.032996 | -0.009155 | -0.041199 | -0.10071 | -0.027466 | 0.1236 | -0.022888 | -0.16937 | -1.5015 | -1.5244 | -1.6159 | -1.3733 | -1.4145 | -1.5381 | -1.6113 | 1.5244 | 1.3779 | -121.5363 | 1.506 | 1.5198 | 0.14191 | -121.669 | 0.009155 | -0.064087 | -123.0331 | 0.045776 | -0.068665 | -0.004578 | -123.0743 | 1.6708 | 1.5381 | 1.4465 | -121.8292 | 0.17395 | 0.13275 | 0.022888 | -123.2712
888.8438 | 123.2666 | -1.474 | 121.669 | 0.076074 | 0.12308 | 0.14933 | 0.051542 | 0.10812 | -0.019111 | 0.043039 | 0.0010378 | 0.1806 | -0.012791 | 0.19558 | 0.0043349 | -0.014838 | 0 | 0.068665 | 0.004578 | 0.045776 | 0.12817 | 0.018311 | -0.10986 | -1.3687 | -1.3504 | -1.4328 | -1.3687 | -1.4053 | -1.5015 | -1.5839 | 1.4923 | 1.3641 | -121.5408 | 1.5427 | 1.5198 | 0.15564 | -121.669 | -0.027466 | -0.10986 | -123.0377 | 0.10529 | 0.041199 | 0.15106 | -123.0743 | 1.6022 | 1.474 | 1.4786 | -121.7789 | 0.10529 | 0.068665 | 0.1236 | -123.2529
889.9219 | 123.2346 | -1.5152 | 121.6827 | -0.15281 | 0.17435 | 0.13865 | 0.087858 | 0.11987 | 0.031091 | 0.035562 | -0.30414 | 0.18914 | 0.019253 | 0.17849 | 0.0075399 | -0.039405 | 0.036621 | 0.059509 | -0.032043 | 0.022888 | 0.13275 | -0.013733 | -0.16479 | -1.4008 | -1.4145 | -1.506 | -1.3367 | -1.3962 | -1.506 | -1.5884 | 1.5015 | 1.3504 | -121.55 | 1.5747 | 1.5381 | 0.18768 | -121.6461 | 0.009156 | -0.073242 | -123.0194 | 0.11444 | 0.009156 | 0.082398 | -123.0789 | 1.6479 | 1.5518 | 1.4832 | -121.8475 | 0.17853 | 0.11902 | 0.10071 | -123.2712
890.8438 | 123.23 | -1.4786 | 121.701 | 0.50332 | 0.13483 | 0.14719 | 0.060087 | 0.1188 | -0.015906 | 0.035562 | 0.1994 | 0.19021 | -0.018131 | 0.18169 | 0.010744 | -0.024451 | 0.018311 | 0.086975 | 0.018311 | 0.041199 | 0.10986 | 0.018311 | -0.11444 | -1.3824 | -1.4008 | -1.4465 | -1.3596 | -1.387 | -1.4923 | -1.5701 | 1.4969 | 1.3641 | -121.5912 | 1.5656 | 1.5198 | 0.15564 | -121.6827 | -0.013733 | -0.091552 | -123.0606 | 0.096131 | 0.032044 | 0.1236 | -123.0881 | 1.5884 | 1.4969 | 1.4969 | -121.8155 | 0.11902 | 0.091553 | 0.07782 | -123.2712
891.9062 | 123.1705 | -1.4923 | 121.7285 | 0.15237 | 0.1797 | 0.12903 | 0.076109 | 0.11026 | 0.021478 | 0.038766 | 0.16888 | 0.19662 | 0.023525 | 0.19878 | 0.027834 | -0.036201 | -0.032043 | -0.068665 | -0.10986 | -0.027466 | 0.14191 | -0.013733 | -0.15106 | -1.4511 | -1.474 | -1.5198 | -1.3229 | -1.3687 | -1.4969 | -1.561 | 1.4786 | 1.3412 | -121.5866 | 1.4236 | 1.4648 | 0.1236 | -121.7606 | -0.004577 | -0.068664 | -123.0515 | 0.041199 | -0.027465 | 0.041199 | -123.0972 | 1.6342 | 1.4603 | 1.3824 | -121.8796 | 0.16937 | 0.1236 | 0.018311 | -123.2895
892.8438 | 123.2529 | -1.442 | 121.6873 | 0.25918 | 0.12522 | 0.1504 | 0.054746 | 0.10705 | -0.043677 | 0.044107 | 0.26044 | 0.1806 | -0.0095859 | 0.17955 | -0.0020731 | -0.015907 | -0.073242 | 0.07782 | -0.022888 | 0.009155 | 0.054932 | -0.041199 | -0.17853 | -1.3824 | -1.3504 | -1.4191 | -1.3412 | -1.3779 | -1.4603 | -1.5289 | 1.4008 | 1.2634 | -121.6324 | 1.5198 | 1.4511 | 0.18768 | -121.7606 | -0.01831 | -0.086975 | -123.0286 | 0.05951 | 0.022889 | 0.10986 | -123.0652 | 1.4969 | 1.3687 | 1.4191 | -121.8658 | 0.10071 | 0.064087 | 0.091553 | -123.2162
893.9062 | 123.3032 | -1.4557 | 121.6827 | 0.51858 | 0.15513 | 0.13972 | 0.061155 | 0.12414 | 0.0097277 | 0.038766 | 0.35199 | 0.20089 | 0.011776 | 0.18169 | 0.026766 | -0.032996 | 0.064087 | 0.11902 | 0.041199 | 0.068665 | 0.082397 | 0.018311 | -0.11902 | -1.2863 | -1.2955 | -1.387 | -1.3733 | -1.4236 | -1.4877 | -1.5656 | 1.474 | 1.3367 | -121.6003 | 1.5747 | 1.5244 | 0.18768 | -121.6187 | -0.032044 | -0.10986 | -123.056 | 0.16937 | 0.068664 | 0.17853 | -123.1064 | 1.5381 | 1.5198 | 1.4969 | -121.8018 | 0.082397 | 0.032043 | 0.16022 | -123.2483
894.8438 | 123.3261 | -1.4145 | 121.6827 | -0.061255 | 0.12095 | 0.1536 | 0.064359 | 0.11667 | -0.01377 | 0.035562 | -0.39569 | 0.17526 | -0.022404 | 0.16994 | 0.0021989 | -0.028724 | 0.07782 | 0.18768 | 0.068665 | 0.073242 | 0.10071 | 0.036621 | -0.10986 | -1.3 | -1.2589 | -1.3458 | -1.3229 | -1.3458 | -1.4282 | -1.506 | 1.4511 | 1.3046 | -121.582 | 1.6022 | 1.4877 | 0.18311 | -121.6049 | -0.013733 | -0.091552 | -123.0057 | 0.11444 | 0.068665 | 0.16022 | -123.0286 | 1.5152 | 1.4923 | 1.4832 | -121.7926 | 0.091553 | 0.068665 | 0.15564 | -123.1888
895.9062 | 123.2117 | -1.4465 | 121.8338 | 0.076074 | 0.18504 | 0.14506 | 0.089994 | 0.11667 | 0.026818 | 0.046243 | -0.42621 | 0.20623 | 0.022457 | 0.17955 | 0.025698 | -0.03086 | 0.045776 | 0.064087 | -0.036621 | 0.027466 | 0.14648 | -0.004578 | -0.16479 | -1.3458 | -1.3367 | -1.442 | -1.2817 | -1.3412 | -1.4557 | -1.5335 | 1.442 | 1.2817 | -121.6873 | 1.5106 | 1.474 | 0.19226 | -121.788 | -0.009155 | -0.086975 | -123.1155 | 0.10071 | 0.004577 | 0.091552 | -123.175 | 1.593 | 1.4923 | 1.4099 | -121.9986 | 0.1648 | 0.10529 | 0.10986 | -123.3673
896.8438 | 123.2574 | -1.387 | 121.7239 | 0.5491 | 0.16474 | 0.14399 | 0.0697 | 0.11774 | 0.010797 | 0.041971 | 0.41303 | 0.18914 | -0.0074499 | 0.18062 | 0.0075399 | -0.024451 | -0.15564 | 0.19684 | 0.07782 | 0.059509 | 0.050354 | -0.018311 | -0.17395 | -1.268 | -1.2772 | -1.3367 | -1.3092 | -1.3596 | -1.4282 | -1.4969 | 1.3687 | 1.2131 | -121.6736 | 1.5839 | 1.4465 | 0.23346 | -121.8796 | -0.041199 | -0.10986 | -123.0331 | 0.11902 | 0.050354 | 0.16022 | -123.0835 | 1.4374 | 1.2314 | 1.4648 | -121.8979 | 0.07782 | 0.027466 | 0.10986 | -123.2208
897.9062 | 123.1842 | -1.442 | 121.8155 | -1.3277 | 0.14979 | 0.13758 | 0.061155 | 0.10599 | 0.023614 | 0.032358 | -0.38043 | 0.19234 | -0.0074499 | 0.18489 | 0.02463 | -0.020179 | -0.022888 | 0.009155 | -0.073242 | -0.009155 | 0.18768 | -0.004578 | -0.1236 | -1.3916 | -1.355 | -1.4465 | -1.2497 | -1.3184 | -1.4465 | -1.5106 | 1.4374 | 1.3184 | -121.6278 | 1.4511 | 1.4328 | 0.11444 | -121.8384 | -0.004577 | -0.068664 | -123.0652 | 0.050354 | -0.004577 | 0.064087 | -123.1338 | 1.6296 | 1.4191 | 1.3687 | -121.9391 | 0.19226 | 0.1236 | 0.086976 | -123.3261
898.8438 | 123.2162 | -1.387 | 121.7789 | 0.48806 | 0.16901 | 0.13758 | 0.062223 | 0.10492 | 0.019342 | 0.039835 | 0.2757 | 0.19021 | 2.7137e-05 | 0.18276 | 0.02997 | -0.023383 | -0.022888 | 0 | -0.054932 | 0 | 0.15106 | -0.018311 | -0.14648 | -1.3229 | -1.3367 | -1.4053 | -1.2634 | -1.3 | -1.4099 | -1.4877 | 1.3687 | 1.2405 | -121.6278 | 1.387 | 1.387 | 0.14648 | -121.8018 | -0.022888 | -0.10071 | -123.0423 | 0.064087 | -0.01831 | 0.082398 | -123.0789 | 1.5381 | 1.3641 | 1.3321 | -121.9254 | 0.1236 | 0.086975 | 0.050354 | -123.2666
899.9062 | 123.2162 | -1.3138 | 121.8338 | -0.10703 | 0.17115 | 0.13758 | 0.079313 | 0.11667 | 0.012933 | 0.04838 | -0.27362 | 0.20303 | 0.0042991 | 0.20198 | 0.026766 | -0.038337 | 0.036621 | 0.045776 | -0.036621 | 0.032043 | 0.13275 | -0.009155 | -0.14648 | -1.3 | -1.0803 | -1.1673 | -1.2085 | -1.2451 | -1.3367 | -1.4053 | 1.3046 | 1.1673 | -121.701 | 1.3596 | 1.3458 | 0.17853 | -121.7972 | -0.022888 | -0.091552 | -123.0423 | 0.013733 | 0.14648 | 0.23804 | -123.0789 | 1.4465 | 1.3504 | 1.2772 | -121.9803 | 0.10529 | 0.068665 | 0.23346 | -123.2391
900.8438 | 123.2803 | -1.3321 | 121.7926 | -1.9533 | 0.15086 | 0.13972 | 0.055814 | 0.11346 | -0.0062933 | 0.035562 | 0.26044 | 0.19021 | 0.0075041 | 0.17208 | 0.0086079 | -0.02552 | 0.036621 | 0.12817 | 0.059509 | 0.059509 | 0.073242 | 0.004578 | -0.10986 | -1.236 | -1.236 | -1.2772 | -1.2451 | -1.2909 | -1.3641 | -1.4236 | 1.3367 | 1.2222 | -121.7194 | 1.4603 | 1.3916 | 0.16937 | -121.756 | -0.032044 | -0.091553 | -123.0377 | 0.09613 | 0.054931 | 0.14648 | -123.0835 | 1.4053 | 1.3687 | 1.3916 | -121.9025 | 0.086975 | 0.041198 | 0.09613 | -123.2162
901.9062 | 123.175 | -1.3824 | 121.8338 | 0.091333 | 0.17435 | 0.13331 | 0.076109 | 0.11987 | 0.031091 | 0.037698 | -0.029479 | 0.19555 | 0.0075041 | 0.19451 | 0.020357 | -0.026588 | 0.022888 | 0.018311 | -0.068665 | 0.027466 | 0.1236 | -0.022888 | -0.14648 | -1.3275 | -1.3092 | -1.4099 | -1.2131 | -1.2634 | -1.3962 | -1.4786 | 1.3596 | 1.236 | -121.7102 | 1.4008 | 1.4099 | 0.17395 | -121.8109 | -0.013733 | -0.096131 | -123.0469 | 0.054931 | -0.027466 | 0.068665 | -123.0972 | 1.506 | 1.4053 | 1.3138 | -121.9803 | 0.16937 | 0.11902 | 0.073242 | -123.3124
902.8438 | 123.2346 | -1.355 | 121.7972 | 0.51858 | 0.15513 | 0.13544 | 0.0697 | 0.12842 | 0.0065237 | 0.040903 | 0.2757 | 0.20409 | -0.0042459 | 0.18383 | 0.015017 | -0.019111 | -0.004578 | 0 | -0.059509 | -0.009155 | 0.11902 | -0.004578 | -0.1236 | -1.2634 | -1.2909 | -1.3596 | -1.2177 | -1.2543 | -1.3458 | -1.4328 | 1.3504 | 1.2314 | -121.6782 | 1.355 | 1.3458 | 0.11444 | -121.8018 | 0.009155 | -0.07782 | -123.0148 | 0.091552 | -0.004578 | 0.073242 | -123.0515 | 1.474 | 1.3504 | 1.2955 | -121.9208 | 0.13733 | 0.10071 | 0.064086 | -123.23
903.9062 | 123.1842 | -1.3046 | 121.8796 | -0.50376 | 0.14338 | 0.14292 | 0.063291 | 0.13803 | -0.010566 | 0.028085 | -0.42621 | 0.18487 | -0.0085179 | 0.19024 | 0.010744 | -0.02552 | -0.041199 | -0.013733 | -0.091553 | -0.027466 | 0.14648 | -0.009155 | -0.16937 | -1.3092 | -1.1444 | -1.1261 | -1.149 | -1.1673 | -1.3412 | -1.4008 | 1.2955 | 1.1353 | -121.7331 | 1.2909 | 1.2772 | 0.14191 | -121.9208 | -0.036622 | -0.096131 | -123.0286 | -0.004578 | 0.17853 | 0.27466 | -123.0469 | 1.4511 | 1.2634 | 1.2131 | -122.049 | 0.15564 | 0.13733 | 0.16022 | -123.2803
904.8438 | 123.2574 | -1.3275 | 121.8338 | 0.44228 | 0.13804 | 0.14933 | 0.044065 | 0.1156 | -0.0062933 | 0.025949 | 0.30621 | 0.18807 | -0.0042459 | 0.16994 | 0.0054039 | -0.010566 | 0.027466 | 0.073242 | 0.013733 | 0.045776 | 0.10071 | 0.032043 | -0.10071 | -1.2314 | -1.2405 | -1.2955 | -1.2039 | -1.2543 | -1.3275 | -1.4191 | 1.3596 | 1.2268 | -121.7331 | 1.4008 | 1.3733 | 0.14648 | -121.8063 | 0 | -0.091552 | -123.0377 | 0.096131 | 0.032044 | 0.1236 | -123.0881 | 1.4282 | 1.355 | 1.3412 | -121.9345 | 0.1236 | 0.073243 | 0.086975 | -123.2529
905.9062 | 123.1613 | -1.3184 | 121.8842 | -0.32065 | 0.14338 | 0.15787 | 0.067564 | 0.1156 | -0.0030893 | 0.027017 | -0.44147 | 0.19021 | -0.017063 | 0.17955 | 0.017153 | -0.031928 | -0.022888 | -0.018311 | -0.09613 | -0.013733 | 0.16937 | -0.018311 | -0.15106 | -1.1627 | -1.2955 | -1.3962 | -1.1353 | -1.1581 | -1.3 | -1.3779 | 1.3 | 1.1673 | -121.7148 | 1.3 | 1.3046 | 0.13733 | -121.907 | 0.01831 | -0.05951 | -123.0194 | 0.15564 | -0.07782 | -0.01831 | -123.0423 | 1.4877 | 1.2955 | 1.2222 | -122.0352 | 0.18311 | 0.16022 | 0.022888 | -123.262
906.8438 | 123.2758 | -1.2955 | 121.8613 | 0.51858 | 0.16474 | 0.13865 | 0.065427 | 0.11239 | 0.017205 | 0.03663 | 0.26044 | 0.18487 | 0.0010951 | 0.17528 | 0.018221 | -0.016975 | 0.013733 | 0.009155 | -0.050354 | 0 | 0.13733 | 0.004578 | -0.15564 | -1.2177 | -1.236 | -1.2726 | -1.1856 | -1.2405 | -1.3367 | -1.3962 | 1.3 | 1.1398 | -121.7239 | 1.3046 | 1.2955 | 0.15564 | -121.8475 | -0.041199 | -0.10071 | -123.0469 | 0.07782 | 0.022888 | 0.1236 | -123.1018 | 1.4328 | 1.3092 | 1.2451 | -122.0169 | 0.10986 | 0.054931 | 0.059509 | -123.2574
907.9062 | 123.2849 | -1.3138 | 121.8704 | -0.12229 | 0.12736 | 0.16001 | 0.063291 | 0.10492 | -0.022315 | 0.034494 | -0.22784 | 0.18273 | -0.013859 | 0.18169 | 0.013948 | -0.021247 | 0.07782 | 0.16022 | 0.073242 | 0.091553 | 0.10986 | 0.004578 | -0.12817 | -1.1673 | -1.2177 | -1.1536 | -1.1856 | -1.2177 | -1.3046 | -1.4008 | 1.3184 | 1.1856 | -121.7606 | 1.474 | 1.4053 | 0.21973 | -121.7926 | 0.009156 | -0.086975 | -123.056 | 0.14648 | 0.16022 | 0.24719 | -123.0881 | 1.4236 | 1.3916 | 1.387 | -121.9986 | 0.12817 | 0.096131 | 0.096131 | -123.2712
908.8438 | 123.3032 | -1.2863 | 121.8521 | 0.61013 | 0.15513 | 0.14399 | 0.066496 | 0.11987 | 0.0043877 | 0.030222 | 0.33673 | 0.17098 | 0.0042991 | 0.1881 | 0.017153 | -0.02552 | 0.091553 | 0.10071 | 0.027466 | 0.054932 | 0.10071 | 0.032043 | -0.09613 | -1.1307 | -1.1215 | -1.2222 | -1.2085 | -1.2543 | -1.3367 | -1.4053 | 1.3184 | 1.1902 | -121.7514 | 1.387 | 1.3412 | 0.15106 | -121.7606 | -0.050354 | -0.11902 | -123.0606 | 0.15564 | 0.064087 | 0.18311 | -123.1064 | 1.387 | 1.3779 | 1.3138 | -121.9482 | 0.07782 | 0.032044 | 0.1648 | -123.2574
909.8438 | 123.1705 | -1.3092 | 121.9162 | 0.41177 | 0.15192 | 0.14719 | 0.088926 | 0.12308 | 0.021478 | 0.062265 | -0.19733 | 0.19234 | -0.0021099 | 0.17742 | 0.011812 | -0.035133 | -0.13733 | 0.23346 | -0.009155 | -0.022888 | 0.14191 | 0.018311 | -0.1236 | -1.2405 | -1.2863 | -1.3184 | -1.1032 | -1.1627 | -1.3184 | -1.3733 | 1.3275 | 1.1856 | -121.7743 | 1.5427 | 1.2863 | 0.10071 | -122.0535 | -0.009155 | -0.064087 | -123.0194 | 0.068664 | -0.009155 | 0.054932 | -123.0789 | 1.4511 | 1.1719 | 1.3 | -122.0398 | 0.20599 | 0.14648 | 0.022888 | -123.2895
910.9062 | 123.3078 | -1.2405 | 121.8979 | -0.030737 | 0.14765 | 0.14399 | 0.059019 | 0.11453 | -0.019111 | 0.033426 | -0.27362 | 0.18166 | -0.011723 | 0.18489 | 0.0011309 | -0.022315 | 0.10071 | 0.16022 | 0.073242 | 0.086975 | 0.10986 | 0.022888 | -0.10071 | -1.1398 | -1.0849 | -1.1719 | -1.1444 | -1.1719 | -1.2543 | -1.3321 | 1.2634 | 1.1398 | -121.788 | 1.4008 | 1.3275 | 0.18768 | -121.7972 | -0.013732 | -0.091552 | -123.0423 | 0.10071 | 0.068665 | 0.16022 | -123.0698 | 1.3504 | 1.3412 | 1.3138 | -121.9986 | 0.096131 | 0.068665 | 0.15564 | -123.23
911.8438 | 123.175 | -1.2909 | 121.9208 | 0.15237 | 0.17008 | 0.14506 | 0.083585 | 0.1156 | 0.038568 | 0.046243 | -0.12103 | 0.20196 | -0.0010409 | 0.17955 | 0.019289 | -0.027656 | 0.022888 | -0.013733 | -0.068665 | -0.004578 | 0.13275 | 0.004578 | -0.15564 | -1.236 | -1.2451 | -1.3275 | -1.1215 | -1.1673 | -1.3 | -1.3916 | 1.2955 | 1.1353 | -121.788 | 1.2772 | 1.2863 | 0.15106 | -121.8979 | -0.009155 | -0.10071 | -123.0423 | 0.054932 | -0.036621 | 0.064087 | -123.0881 | 1.4236 | 1.3138 | 1.2222 | -122.0764 | 0.16937 | 0.1236 | 0.045777 | -123.3124
912.9062 | 123.1979 | -1.2772 | 121.9574 | -0.29014 | 0.1562 | 0.16001 | 0.065427 | 0.11453 | 0.012933 | 0.033426 | -0.44147 | 0.19555 | -0.0074499 | 0.18703 | 0.021425 | -0.026588 | -0.032043 | -0.018311 | -0.082397 | 0.004578 | 0.13733 | -0.027466 | -0.17395 | -1.2268 | -1.2131 | -1.2909 | -1.1032 | -1.1444 | -1.2909 | -1.3504 | 1.2497 | 1.1032 | -121.8201 | 1.2589 | 1.2817 | 0.17853 | -121.9894 | -0.013733 | -0.073242 | -123.0606 | 0.050354 | -0.013733 | 0.059509 | -123.1018 | 1.4145 | 1.2451 | 1.1948 | -122.1313 | 0.17395 | 0.13275 | 0.064087 | -123.3078
913.8438 | 123.2025 | -1.2497 | 121.9482 | 0.10659 | 0.1562 | 0.13544 | 0.088926 | 0.12308 | 0.014001 | 0.030222 | -0.22784 | 0.18807 | 0.01498 | 0.19344 | 0.015017 | -0.032996 | 0.11902 | 0.059509 | -0.004578 | 0.036621 | 0.1831 | 0.059509 | -0.050354 | -1.1581 | -1.1719 | -1.2634 | -1.0941 | -1.1353 | -1.2726 | -1.355 | 1.3092 | 1.1993 | -121.7651 | 1.3092 | 1.2863 | 0.086975 | -121.8292 | -0.022888 | -0.10529 | -123.0423 | 0.091553 | -0.013733 | 0.091552 | -123.0835 | 1.4328 | 1.3687 | 1.2451 | -121.9986 | 0.15564 | 0.11444 | 0.07782 | -123.3032
914.9062 | 123.2574 | -1.2268 | 121.962 | -0.21384 | 0.13911 | 0.14826 | 0.051542 | 0.11026 | -0.019111 | 0.030222 | -0.25836 | 0.1806 | -0.011723 | 0.17208 | 0.013948 | -0.01377 | 0.041199 | 0.13275 | 0.059509 | 0.068665 | 0.09613 | 0.018311 | -0.11444 | -1.1353 | -1.0712 | -1.1719 | -1.1032 | -1.1215 | -1.2222 | -1.3 | 1.2451 | 1.1124 | -121.8658 | 1.3596 | 1.2955 | 0.18311 | -121.9208 | 0.004578 | -0.073242 | -123.0652 | 0.091553 | 0.054932 | 0.12817 | -123.0835 | 1.3229 | 1.268 | 1.2863 | -122.0764 | 0.1236 | 0.10529 | 0.15564 | -123.262
915.8438 | 123.1979 | -1.2085 | 122.0032 | 0.50332 | 0.17435 | 0.14933 | 0.072904 | 0.11346 | 0.022546 | 0.028085 | 0.1994 | 0.19021 | 0.021389 | 0.18596 | 0.01288 | -0.022315 | -0.041199 | -0.068665 | -0.1236 | -0.022888 | 0.15106 | -0.027466 | -0.15106 | -1.2039 | -1.2268 | -1.3 | -1.0666 | -1.1078 | -1.236 | -1.3046 | 1.181 | 1.0574 | -121.8521 | 1.1398 | 1.1856 | 0.12817 | -122.0444 | -0.027466 | -0.09613 | -123.0698 | 0.004578 | -0.091553 | 0.004577 | -123.111 | 1.3596 | 1.1673 | 1.0849 | -122.1542 | 0.14191 | 0.10071 | -0.018311 | -123.3078
916.9062 | 123.2437 | -1.2451 | 121.9666 | -0.15281 | 0.16795 | 0.14292 | 0.071836 | 0.10599 | 0.02041 | 0.039835 | -0.42621 | 0.19341 | 0.011776 | 0.19451 | 0.0086079 | -0.026588 | -0.022888 | -0.022888 | -0.073242 | 0.009155 | 0.13733 | -0.018311 | -0.15106 | -1.1948 | -1.1536 | -1.2497 | -1.0666 | -1.1124 | -1.2726 | -1.3321 | 1.2268 | 1.0941 | -121.8292 | 1.2222 | 1.2543 | 0.16022 | -121.9894 | -0.027466 | -0.086975 | -123.0331 | 0.050354 | -0.004578 | 0.082397 | -123.0789 | 1.3824 | 1.2222 | 1.1719 | -122.1176 | 0.17853 | 0.13275 | 0.091553 | -123.2986
917.8438 | 123.1796 | -1.2314 | 121.9894 | 2.1055 | 0.14124 | 0.13972 | 0.066496 | 0.12735 | 0.0022517 | 0.035562 | -0.3194 | 0.187 | 0.0096401 | 0.18169 | -0.0010051 | -0.019111 | -0.022888 | -0.013733 | -0.091553 | 0.009155 | 0.17395 | 0 | -0.13733 | -1.2039 | -1.1581 | -1.2405 | -1.0391 | -1.1032 | -1.2497 | -1.3184 | 1.2314 | 1.0941 | -121.8155 | 1.2177 | 1.2405 | 0.14648 | -122.0123 | -0.018311 | -0.086975 | -123.0286 | 0.027466 | -0.009156 | 0.077819 | -123.0927 | 1.4053 | 1.2085 | 1.1398 | -122.1268 | 0.19226 | 0.12817 | 0.073242 | -123.3078
918.9062 | 123.3032 | -1.1673 | 121.9849 | -0.19858 | 0.14124 | 0.16215 | 0.0697 | 0.12094 | -0.018043 | 0.01954 | 0.85553 | 0.18166 | -0.0053139 | 0.18703 | 0.015017 | -0.026588 | 0.041199 | 0.15106 | 0.004578 | 0.032043 | 0.11902 | -0.009155 | -0.13275 | -1.0849 | -1.0391 | -1.0849 | -1.0941 | -1.1261 | -1.2039 | -1.2451 | 1.1581 | 1.0345 | -121.8658 | 1.3184 | 1.1993 | 0.16479 | -121.9437 | -0.036621 | -0.07782 | -123.0789 | 0.082397 | 0.082397 | 0.16022 | -123.111 | 1.2863 | 1.2085 | 1.1719 | -122.1176 | 0.073242 | 0.041198 | 0.12817 | -123.23
919.8438 | 123.3124 | -1.1719 | 121.9711 | 0.61013 | 0.14231 | 0.14933 | 0.070768 | 0.10705 | 0.015069 | 0.034494 | 0.35199 | 0.18594 | -0.019199 | 0.17955 | 0.023561 | -0.016975 | 0.045776 | 0.064087 | 0.009155 | 0.054932 | 0.11444 | 0.013733 | -0.10529 | -1.0483 | -1.0712 | -1.1215 | -1.1032 | -1.1353 | -1.1948 | -1.2497 | 1.1856 | 1.0666 | -121.8567 | 1.236 | 1.2268 | 0.16022 | -121.9254 | -0.022888 | -0.07782 | -123.0743 | 0.1236 | 0.050354 | 0.12817 | -123.1064 | 1.2863 | 1.2177 | 1.181 | -122.0764 | 0.068665 | 0.036621 | 0.10071 | -123.2208
920.9062 | 123.2208 | -1.1948 | 122.0169 | -0.29014 | 0.13483 | 0.13331 | 0.061155 | 0.11026 | -0.01377 | 0.03129 | -0.34991 | 0.1806 | -0.011723 | 0.17528 | 0.01288 | -0.012702 | 0.045776 | 0.10529 | 0.036621 | 0.064087 | 0.13275 | -0.004578 | -0.13733 | -1.1215 | -1.0666 | -1.1398 | -1.0437 | -1.0895 | -1.2039 | -1.2817 | 1.1902 | 1.0574 | -121.8842 | 1.3 | 1.2589 | 0.20142 | -121.9711 | -0.009155 | -0.086975 | -123.0606 | 0.073242 | 0.054931 | 0.14191 | -123.1064 | 1.3275 | 1.2405 | 1.2314 | -122.1542 | 0.15106 | 0.10529 | 0.12817 | -123.2986
921.8438 | 123.1888 | -1.2039 | 122.0123 | -0.27488 | 0.16474 | 0.15787 | 0.079313 | 0.10812 | 0.0054557 | 0.040903 | -0.39569 | 0.19341 | -0.0063819 | 0.1881 | 0.011812 | -0.031928 | -0.009155 | -0.013733 | -0.091553 | 0.009155 | 0.13733 | -0.027466 | -0.16937 | -1.1627 | -1.1353 | -1.236 | -1.0162 | -1.0803 | -1.2085 | -1.2909 | 1.1765 | 1.0345 | -121.875 | 1.1902 | 1.2131 | 0.17853 | -122.0215 | -0.004578 | -0.086976 | -123.0286 | 0.041198 | -0.032044 | 0.054932 | -123.0927 | 1.3412 | 1.1948 | 1.1124 | -122.1817 | 0.18768 | 0.1236 | 0.068664 | -123.3032
922.9062 | 123.2391 | -1.1627 | 122.0123 | 0.27444 | 0.12415 | 0.16855 | 0.063291 | 0.10278 | -0.0094983 | 0.021677 | 0.12311 | 0.1806 | -0.015995 | 0.18383 | 0.0021989 | -0.024451 | -0.068665 | 0.032043 | -0.032043 | 0.027466 | 0.064087 | -0.045776 | -0.16022 | -1.0941 | -1.062 | -1.1169 | -1.0483 | -1.0986 | -1.181 | -1.2405 | 1.1169 | 1.0025 | -121.9482 | 1.1948 | 1.1902 | 0.18768 | -122.081 | -0.01831 | -0.07782 | -123.0606 | 0.068665 | 0.045777 | 0.1236 | -123.111 | 1.2268 | 1.0941 | 1.1307 | -122.1725 | 0.11444 | 0.064087 | 0.10071 | -123.2529
923.8438 | 123.2071 | -1.2131 | 122.0123 | -0.21384 | 0.16047 | 0.14185 | 0.084654 | 0.1188 | 0.015069 | 0.034494 | -0.48724 | 0.19662 | 0.0021631 | 0.18276 | 0.0043349 | -0.02552 | 0 | -0.009155 | -0.082397 | 0.004578 | 0.13733 | -0.050354 | -0.15106 | -1.1581 | -1.1215 | -1.2085 | -1.0162 | -1.0529 | -1.1902 | -1.2589 | 1.1627 | 1.062 | -121.875 | 1.2039 | 1.2177 | 0.15564 | -122.0123 | 0.022888 | -0.045776 | -123.0286 | 0.054932 | 0.004578 | 0.050354 | -123.0652 | 1.3504 | 1.2131 | 1.1307 | -122.1634 | 0.19684 | 0.16022 | 0.091553 | -123.2712
924.8438 | 123.2986 | -1.1215 | 122.0306 | 0.51858 | 0.16261 | 0.11942 | 0.071836 | 0.10919 | 0.011865 | 0.03129 | 0.44354 | 0.18594 | -0.0031779 | 0.18169 | 0.016085 | -0.015907 | 0.050354 | 0.1236 | 0.032043 | 0.059509 | 0.07782 | -0.013733 | -0.13275 | -1.0117 | -1.0345 | -1.0666 | -1.0437 | -1.0666 | -1.1536 | -1.2177 | 1.1078 | 0.98877 | -121.9528 | 1.2451 | 1.181 | 0.19226 | -121.9803 | -0.032043 | -0.09613 | -123.0743 | 0.10986 | 0.054932 | 0.15106 | -123.0972 | 1.1993 | 1.1719 | 1.1536 | -122.1634 | 0.07782 | 0.054932 | 0.086975 | -123.2483
925.9062 | 123.2117 | -1.1444 | 122.0535 | -0.35117 | 0.14124 | 0.14612 | 0.053678 | 0.11026 | 0.0033197 | 0.025949 | -0.36517 | 0.17739 | -0.0021099 | 0.17955 | 0.011812 | -0.026588 | 0.041199 | 0.082397 | 0.004578 | 0.064087 | 0.1236 | -0.004578 | -0.11902 | -1.0803 | -1.0437 | -1.1307 | -0.99335 | -1.0574 | -1.1627 | -1.236 | 1.1398 | 1.0254 | -121.9299 | 1.2268 | 1.2085 | 0.18311 | -122.0123 | -0.018311 | -0.091553 | -123.0469 | 0.064087 | 0.013733 | 0.10529 | -123.111 | 1.268 | 1.1856 | 1.149 | -122.1725 | 0.15106 | 0.086975 | 0.10071 | -123.2895
926.8438 | 123.1934 | -1.1536 | 122.0947 | -0.3054 | 0.1359 | 0.15894 | 0.063291 | 0.12201 | 0.0033197 | 0.027017 | -2.3793 | 0.18807 | 0.0042991 | 0.17421 | 0.0086079 | -0.031928 | -0.027466 | 0 | -0.091553 | -0.004578 | 0.15564 | -0.022888 | -0.13275 | -1.0986 | -1.1215 | -1.1719 | -0.94299 | -1.0025 | -1.149 | -1.2268 | 1.1307 | 1.0208 | -121.9391 | 1.1536 | 1.149 | 0.12817 | -122.1222 | 0.004577 | -0.073243 | -123.0377 | 0.054931 | -0.018311 | 0.054932 | -123.0972 | 1.3092 | 1.1261 | 1.062 | -122.2275 | 0.21057 | 0.15106 | 0.032043 | -123.3215
927.9062 | 123.2071 | -1.1353 | 122.0398 | -0.015478 | 0.12629 | 0.1536 | 0.050474 | 0.10171 | -0.0030893 | 0.037698 | -0.38043 | 0.17632 | -0.013859 | 0.17528 | 0.0054039 | -0.020179 | 0.07782 | 0.16479 | 0.082397 | 0.086975 | 0.12817 | 0.027466 | -0.10986 | -0.99792 | -0.95673 | -1.0391 | -1.0254 | -1.0574 | -1.1353 | -1.2314 | 1.1627 | 1.0254 | -121.9116 | 1.3 | 1.2222 | 0.19684 | -121.962 | 0 | -0.09613 | -123.0652 | 0.13733 | 0.09613 | 0.19226 | -123.0972 | 1.2634 | 1.2131 | 1.2177 | -122.1497 | 0.10986 | 0.07782 | 0.17853 | -123.2712
928.8438 | 123.2254 | -1.1673 | 122.0901 | -0.16807 | 0.14552 | 0.14506 | 0.082517 | 0.12094 | 0.021478 | 0.033426 | -0.5025 | 0.18487 | -0.0010409 | 0.18489 | 0.025698 | -0.034064 | -0.009155 | 0 | -0.064087 | 0.009155 | 0.13275 | -0.027466 | -0.14648 | -1.0895 | -1.0803 | -1.1673 | -0.97504 | -1.0437 | -1.1856 | -1.2314 | 1.1398 | 1.0208 | -121.9574 | 1.1673 | 1.1765 | 0.15564 | -122.0993 | -0.018311 | -0.064087 | -123.0652 | 0.077819 | 0 | 0.064087 | -123.1338 | 1.3 | 1.1581 | 1.1032 | -122.2366 | 0.19226 | 0.1236 | 0.086975 | -123.3215
929.9062 | 123.3124 | -1.0986 | 122.0398 | 0.030298 | 0.1327 | 0.15146 | 0.065427 | 0.11133 | -0.019111 | 0.029153 | -0.059997 | 0.18166 | -0.012791 | 0.18062 | 0.0064719 | -0.015907 | 0.054932 | 0.15564 | 0.054932 | 0.073242 | 0.13733 | 0.032043 | -0.091553 | -0.97046 | -0.94299 | -0.99335 | -0.99335 | -1.03 | -1.1261 | -1.181 | 1.1307 | 1.0071 | -121.9025 | 1.2543 | 1.1719 | 0.16479 | -121.9849 | -0.027466 | -0.082397 | -123.0331 | 0.12817 | 0.10529 | 0.18768 | -123.0698 | 1.236 | 1.1536 | 1.1536 | -122.1313 | 0.10529 | 0.068665 | 0.15564 | -123.2208
930.8438 | 123.2391 | -1.1215 | 122.081 | -0.21384 | 0.15086 | 0.15146 | 0.0697 | 0.11774 | 0.0033197 | 0.029153 | -0.34991 | 0.187 | 0.011776 | 0.18169 | 0.018221 | -0.029792 | 0.050354 | 0.10986 | 0.018311 | 0.059509 | 0.11444 | 0.009155 | -0.1236 | -1.0483 | -0.99792 | -1.0941 | -0.98419 | -1.0254 | -1.1307 | -1.2177 | 1.1307 | 0.99792 | -121.9666 | 1.2314 | 1.181 | 0.1831 | -122.0306 | -0.009155 | -0.09613 | -123.0652 | 0.073242 | 0.027466 | 0.1236 | -123.1064 | 1.236 | 1.1719 | 1.1398 | -122.2046 | 0.13733 | 0.09613 | 0.1236 | -123.2986
931.9062 | 123.2895 | -1.0986 | 122.0718 | 0.48806 | 0.14124 | 0.14933 | 0.065427 | 0.10599 | 0.010797 | 0.022745 | 0.2757 | 0.18807 | -0.0031779 | 0.17101 | 0.0075399 | -0.026588 | 0.059509 | 0.11444 | 0.045776 | 0.064087 | 0.10071 | 0.027466 | -0.10529 | -0.95673 | -0.99335 | -1.0483 | -0.97961 | -1.0529 | -1.1261 | -1.181 | 1.1261 | 0.99335 | -121.9711 | 1.2131 | 1.1627 | 0.16937 | -122.0123 | -0.027466 | -0.082397 | -123.0515 | 0.14191 | 0.050354 | 0.13275 | -123.1247 | 1.1993 | 1.1581 | 1.1444 | -122.1771 | 0.11902 | 0.045777 | 0.10529 | -123.2529
932.8438 | 123.23 | -1.1307 | 122.0993 | -0.29014 | 0.14552 | 0.14185 | 0.0697 | 0.10812 | 0.0022517 | 0.028085 | -0.42621 | 0.19662 | 0.0021631 | 0.17421 | -0.0031411 | -0.031928 | 0.041199 | 0.082397 | 0 | 0.045776 | 0.10529 | 0.009155 | -0.11444 | -1.0666 | -1.0437 | -1.1215 | -0.9613 | -0.99792 | -1.1307 | -1.2085 | 1.1398 | 1.0162 | -121.994 | 1.2131 | 1.1765 | 0.16022 | -122.0581 | 0 | -0.07782 | -123.0606 | 0.064087 | 0.009155 | 0.086975 | -123.0972 | 1.236 | 1.1719 | 1.1307 | -122.2137 | 0.16937 | 0.13275 | 0.086975 | -123.3078
933.9062 | 123.2758 | -1.0849 | 122.081 | 0.19814 | 0.12522 | 0.14933 | 0.067564 | 0.11133 | -0.0030893 | 0.027017 | 0.12311 | 0.19341 | 2.7137e-05 | 0.16887 | 0.0054039 | -0.018043 | -0.004578 | 0.022888 | -0.041199 | 0.027466 | 0.073242 | -0.036621 | -0.17395 | -1.0117 | -1.0025 | -1.062 | -0.9613 | -1.0071 | -1.1078 | -1.1673 | 1.0483 | 0.91095 | -122.0078 | 1.1078 | 1.1124 | 0.20142 | -122.0856 | -0.022888 | -0.082397 | -123.0423 | 0.073242 | 0.022888 | 0.10529 | -123.0881 | 1.1581 | 1.0803 | 1.0437 | -122.2549 | 0.1236 | 0.07782 | 0.082398 | -123.2483
934.8438 | 123.23 | -1.1169 | 122.1039 | -0.13755 | 0.16901 | 0.13224 | 0.099607 | 0.11774 | 0.028955 | 0.030222 | -0.42621 | 0.19555 | 0.0032311 | 0.18276 | 0.026766 | -0.037269 | 0.036621 | 0.036621 | -0.041199 | 0.036621 | 0.14648 | -0.036621 | -0.15564 | -1.0071 | -1.03 | -1.1078 | -0.95673 | -1.0071 | -1.1261 | -1.2039 | 1.0803 | 0.9613 | -121.9574 | 1.1536 | 1.1536 | 0.19226 | -122.0673 | -0.009156 | -0.086975 | -123.0606 | 0.10986 | 0.009155 | 0.09613 | -123.111 | 1.2634 | 1.1536 | 1.0757 | -122.2595 | 0.16022 | 0.10986 | 0.086975 | -123.3078
935.9062 | 123.0194 | -1.1032 | 121.962 | 0.16763 | 0.13163 | 0.13758 | 0.066496 | 0.10278 | -0.0020213 | 0.032358 | 0.1994 | 0.17953 | -0.0063819 | 0.18169 | 0.015017 | -0.011634 | 0.013733 | 0.059509 | -0.009155 | 0.027466 | 0.12817 | 0 | -0.11902 | -0.99792 | -1.0162 | -1.0529 | -0.9613 | -1.0071 | -1.0986 | -1.1581 | 1.1032 | 0.98419 | -121.8338 | 1.1627 | 1.1307 | 0.14649 | -121.9482 | 0.004577 | -0.054932 | -122.9233 | 0.10529 | 0.050354 | 0.10529 | -122.9691 | 1.2314 | 1.1169 | 1.0941 | -122.081 | 0.14191 | 0.09613 | 0.086975 | -123.1201
936.8438 | 123.2254 | -1.1215 | 122.0947 | -0.16807 | 0.16688 | 0.13117 | 0.072904 | 0.11774 | 0.016137 | 0.039835 | -0.53302 | 0.18914 | 2.7137e-05 | 0.19344 | 0.019289 | -0.042609 | -0.009155 | -0.004578 | -0.073242 | -0.004578 | 0.14191 | -0.013733 | -0.17395 | -1.0483 | -1.0162 | -1.1124 | -0.93842 | -0.97046 | -1.1215 | -1.2039 | 1.1078 | 0.94757 | -121.9528 | 1.1169 | 1.1169 | 0.16937 | -122.1039 | 0 | -0.082397 | -123.0331 | 0.073242 | 0.009155 | 0.091552 | -123.0652 | 1.2634 | 1.1124 | 1.0483 | -122.2687 | 0.1831 | 0.15106 | 0.10529 | -123.2986
937.9062 | 123.2666 | -1.0803 | 122.1176 | 0.44228 | 0.17649 | 0.12583 | 0.084654 | 0.11453 | 0.015069 | 0.043039 | 0.32147 | 0.19128 | 0.0085721 | 0.19237 | 0.018221 | -0.029792 | -0.009155 | 0.009155 | -0.041199 | 0.004578 | 0.13733 | -0.004578 | -0.12817 | -0.98419 | -1.0208 | -1.0529 | -0.92468 | -0.98877 | -1.0986 | -1.1673 | 1.0757 | 0.95215 | -121.9803 | 1.0895 | 1.0849 | 0.13275 | -122.1268 | -0.018311 | -0.086975 | -123.0423 | 0.09613 | 0.027466 | 0.11444 | -123.1064 | 1.2177 | 1.0712 | 1.0391 | -122.2458 | 0.15564 | 0.091552 | 0.059509 | -123.2849
938.8438 | 123.349 | -1.0574 | 122.113 | -0.030737 | 0.12522 | 0.15467 | 0.056883 | 0.11987 | -0.021247 | 0.035562 | -0.075256 | 0.187 | -0.0031779 | 0.19878 | 0.010744 | -0.019111 | 0.054932 | 0.15106 | 0.068665 | 0.082397 | 0.1236 | 0.009155 | -0.10529 | -0.90637 | -0.87433 | -0.97046 | -0.95215 | -1.0071 | -1.0895 | -1.1536 | 1.0666 | 0.95215 | -121.9894 | 1.2085 | 1.1398 | 0.18768 | -122.0581 | -0.032044 | -0.09613 | -123.0652 | 0.15106 | 0.086975 | 0.18311 | -123.1201 | 1.181 | 1.1124 | 1.1261 | -122.2183 | 0.10529 | 0.050354 | 0.1831 | -123.2666
939.9062 | 123.3444 | -1.0391 | 122.0947 | 0.076074 | 0.11881 | 0.15146 | 0.065427 | 0.1156 | -0.0062933 | 0.03129 | -0.2431 | 0.17632 | -0.013859 | 0.18489 | 0.0086079 | -0.016975 | 0.064087 | 0.14191 | 0.068665 | 0.07782 | 0.11444 | 0.022888 | -0.10071 | -0.89264 | -0.8606 | -0.93384 | -0.94757 | -1.0025 | -1.0574 | -1.1353 | 1.062 | 0.93842 | -121.9803 | 1.181 | 1.1169 | 0.17853 | -122.0306 | -0.01831 | -0.09613 | -123.0423 | 0.14648 | 0.10529 | 0.20142 | -123.0972 | 1.1536 | 1.1032 | 1.1078 | -122.1954 | 0.091553 | 0.036622 | 0.17853 | -123.23
940.8438 | 123.2254 | -1.0712 | 122.1359 | -0.25962 | 0.14979 | 0.1504 | 0.064359 | 0.11133 | 0.0054557 | 0.028085 | -0.42621 | 0.19448 | -0.0085179 | 0.18276 | 0.013948 | -0.03086 | 0.027466 | 0.082397 | -0.013733 | 0.054932 | 0.13275 | -0.027466 | -0.14648 | -1.0117 | -0.99792 | -1.0712 | -0.91095 | -0.95673 | -1.0849 | -1.1581 | 1.0437 | 0.92468 | -122.0032 | 1.1536 | 1.1261 | 0.20142 | -122.1085 | -0.013733 | -0.086975 | -123.0469 | 0.059509 | 0 | 0.086975 | -123.0927 | 1.2039 | 1.0986 | 1.0574 | -122.2824 | 0.16022 | 0.11444 | 0.073242 | -123.2941
941.9062 | 123.262 | -1.03 | 122.1542 | 0.50332 | 0.14338 | 0.1504 | 0.056883 | 0.1156 | -0.0041573 | 0.024881 | 0.30621 | 0.19662 | 0.0064351 | 0.17315 | 0.015017 | -0.016975 | 0.059509 | 0.1236 | 0.050354 | 0.068665 | 0.10071 | 0.041199 | -0.10529 | -0.91095 | -0.94299 | -0.99335 | -0.9201 | -0.98877 | -1.0574 | -1.1444 | 1.0712 | 0.92468 | -122.0535 | 1.1536 | 1.0986 | 0.17395 | -122.0947 | -0.027466 | -0.11444 | -123.0743 | 0.11902 | 0.036621 | 0.15106 | -123.143 | 1.1307 | 1.0895 | 1.0803 | -122.2595 | 0.10986 | 0.041198 | 0.086975 | -123.2986
942.8438 | 123.2758 | -1.0574 | 122.1359 | -0.18333 | 0.13163 | 0.13865 | 0.07504 | 0.10599 | 0.0011837 | 0.035562 | -0.36517 | 0.1838 | -0.0085179 | 0.17208 | 0.013948 | -0.03086 | 0.059509 | 0.12817 | 0.050354 | 0.068665 | 0.10071 | 0.013733 | -0.1236 | -0.95215 | -0.91095 | -0.99792 | -0.9201 | -0.97504 | -1.0666 | -1.1307 | 1.0712 | 0.93384 | -122.0352 | 1.1856 | 1.1261 | 0.19226 | -122.0764 | -0.009155 | -0.073242 | -123.056 | 0.10529 | 0.059509 | 0.13275 | -123.111 | 1.1581 | 1.1169 | 1.1078 | -122.2595 | 0.13733 | 0.082397 | 0.14648 | -123.2666
943.9062 | 123.2483 | -1.0254 | 122.1176 | 0.41177 | 0.14017 | 0.14185 | 0.068632 | 0.11453 | 0.011865 | 0.041971 | 0.29095 | 0.18273 | 0.0042991 | 0.18489 | 0.010744 | -0.024451 | 0.059509 | 0.11902 | 0.036621 | 0.054932 | 0.1236 | 0.018311 | -0.10071 | -0.92468 | -0.93842 | -0.99792 | -0.9201 | -0.97046 | -1.0437 | -1.1307 | 1.0437 | 0.92468 | -121.994 | 1.1444 | 1.0803 | 0.15564 | -122.0581 | -0.01831 | -0.10529 | -123.0377 | 0.10071 | 0.027466 | 0.13275 | -123.0881 | 1.149 | 1.0849 | 1.062 | -122.2183 | 0.10529 | 0.054932 | 0.086975 | -123.2483
944.8438 | 123.1979 | -1.0849 | 122.1725 | 0.22866 | 0.17649 | 0.087377 | 0.088926 | 0.11453 | 0.036431 | 0.046243 | -0.13629 | 0.18914 | 0.0064351 | 0.18596 | 0.015017 | -0.040473 | -0.004578 | -0.018311 | -0.07782 | -0.009155 | 0.13733 | -0.027466 | -0.15564 | -1.0254 | -1.0345 | -1.1215 | -0.90637 | -0.95215 | -1.0986 | -1.1627 | 1.0574 | 0.92926 | -122.0352 | 1.0666 | 1.0757 | 0.14649 | -122.1771 | -0.013733 | -0.07782 | -123.0789 | 0.059509 | -0.036621 | 0.041199 | -123.1247 | 1.2222 | 1.0803 | 1.0071 | -122.3282 | 0.17853 | 0.13275 | 0.050354 | -123.3353
945.9062 | 123.1796 | -1.0666 | 122.168 | 0.22866 | 0.17222 | 0.13331 | 0.08679 | 0.12094 | 0.027886 | 0.041971 | 0.031556 | 0.19662 | 0.01498 | 0.19878 | 0.021425 | -0.03086 | -0.032043 | -0.050354 | -0.09613 | -0.013733 | 0.13275 | -0.032043 | -0.16479 | -1.0254 | -1.0529 | -1.1032 | -0.89722 | -0.92926 | -1.0803 | -1.1673 | 1.0345 | 0.90179 | -122.0352 | 1.0162 | 1.0529 | 0.15106 | -122.2 | -0.013733 | -0.10071 | -123.0652 | 0.041198 | -0.036621 | 0.064087 | -123.0972 | 1.1993 | 1.0345 | 0.97046 | -122.3328 | 0.16937 | 0.13733 | 0.013733 | -123.3353
946.8438 | 123.2758 | -1.03 | 122.1542 | 0.2897 | 0.13056 | 0.13972 | 0.070768 | 0.11133 | -0.024451 | 0.037698 | 0.61139 | 0.19128 | 0.012844 | 0.17849 | 0.0011309 | -0.015907 | -0.004578 | 0.059509 | -0.10071 | -0.20599 | 0.086975 | -0.027466 | -0.16937 | -0.96588 | -0.94757 | -0.99335 | -0.94299 | -0.98419 | -1.0529 | -1.1215 | 1.0025 | 0.86059 | -122.0673 | 1.0895 | 0.82397 | -0.036621 | -122.1588 | -0.022888 | -0.091553 | -123.0972 | 0.064087 | 0.036621 | 0.12817 | -123.1384 | 1.1169 | 1.0254 | 0.92926 | -122.3236 | 0.086975 | 0.045776 | 0.082397 | -123.2758
947.9062 | 123.23 | -1.0437 | 122.1725 | 0.82375 | 0.16047 | 0.13224 | 0.070768 | 0.11346 | 0.021478 | 0.03129 | 0.077332 | 0.19662 | 0.0085721 | 0.19344 | 0.010744 | -0.02552 | -0.027466 | -0.032043 | -0.091553 | -0.009155 | 0.15564 | -0.027466 | -0.15106 | -0.9613 | -1.0208 | -1.0666 | -0.88348 | -0.93842 | -1.062 | -1.1215 | 1.0162 | 0.89264 | -122.0169 | 1.0117 | 1.0345 | 0.14191 | -122.2 | -0.018311 | -0.07782 | -123.056 | 0.082397 | -0.022888 | 0.054932 | -123.111 | 1.1993 | 1.0162 | 0.95215 | -122.3236 | 0.16022 | 0.10528 | 0.022888 | -123.2941
948.8438 | 123.3078 | -0.98419 | 122.1725 | 0.015039 | 0.13377 | 0.13865 | 0.05261 | 0.10705 | -0.025519 | 0.035562 | 0.077332 | 0.18807 | -0.0095859 | 0.17528 | 0.01288 | -0.022315 | 0.041199 | 0.10071 | 0.041199 | 0.068665 | 0.1236 | 0.022888 | -0.10529 | -0.88348 | -0.86517 | -0.92468 | -0.88806 | -0.93842 | -1.0071 | -1.0986 | 1.0071 | 0.87891 | -122.0489 | 1.0849 | 1.0529 | 0.17395 | -122.1313 | -0.022888 | -0.11444 | -123.0606 | 0.10071 | 0.059509 | 0.17395 | -123.111 | 1.1078 | 1.0254 | 1.0254 | -122.2778 | 0.09613 | 0.045776 | 0.11902 | -123.2712
949.9062 | 123.3215 | -0.98877 | 122.168 | 5.0199 | 0.17435 | 0.15787 | 0.061155 | 0.11346 | -0.011634 | 0.029153 | -0.28888 | 0.17632 | -0.0053139 | 0.17849 | 0.01288 | -0.031928 | 0.041199 | 0.13733 | 0.045776 | 0.082397 | 0.10529 | 0.004578 | -0.12817 | -0.89264 | -0.83771 | -0.93384 | -0.88806 | -0.93842 | -1.0025 | -1.0849 | 0.99335 | 0.8606 | -122.0627 | 1.1261 | 1.0712 | 0.21057 | -122.1268 | -0.013732 | -0.09613 | -123.056 | 0.096131 | 0.054932 | 0.15106 | -123.1064 | 1.0941 | 1.03 | 1.0345 | -122.2961 | 0.10071 | 0.050354 | 0.15106 | -123.2529
950.8438 | 123.2758 | -0.99335 | 122.1909 | -0.10703 | 0.13697 | 0.15574 | 0.053678 | 0.10492 | -0.0062933 | 0.025949 | 0.10785 | 0.18594 | -0.020267 | 0.16246 | 0.0096759 | -0.027656 | 0.004578 | 0.07782 | -0.009155 | 0.054932 | 0.11902 | 0.018311 | -0.11444 | -0.89722 | -0.90637 | -0.94299 | -0.85602 | -0.9201 | -0.99335 | -1.1032 | 1.0117 | 0.87891 | -122.0718 | 1.0712 | 1.0483 | 0.16937 | -122.1863 | 0 | -0.10986 | -123.0469 | 0.09613 | 0.050354 | 0.16022 | -123.111 | 1.1124 | 0.99792 | 0.98419 | -122.3053 | 0.13733 | 0.073242 | 0.086975 | -123.2941
951.9062 | 123.1613 | -1.1032 | 122.1497 | 0.25918 | 0.1861 | 0.13224 | 0.085722 | 0.11987 | 0.027886 | 0.041971 | -0.15155 | 0.19662 | 0.025661 | 0.18703 | 0.02463 | -0.029792 | -0.013733 | -0.022888 | -0.091553 | -0.022888 | 0.12817 | -0.036621 | -0.17395 | -1.0529 | -1.0986 | -1.1765 | -0.91553 | -0.97961 | -1.1261 | -1.1993 | 1.0666 | 0.92926 | -122.0215 | 1.0803 | 1.0803 | 0.15106 | -122.1634 | -0.022889 | -0.096131 | -123.0652 | 0.050354 | -0.073243 | 0.022888 | -123.1293 | 1.2314 | 1.0895 | 1.0117 | -122.3236 | 0.18768 | 0.1236 | 0.004577 | -123.349
952.8438 | 123.1934 | -1.1032 | 122.1359 | -0.3054 | 0.14872 | 0.14292 | 0.067564 | 0.10492 | 0.010797 | 0.024881 | -0.47198 | 0.18914 | 0.0032311 | 0.18917 | 0.0075399 | -0.03086 | 0.23346 | -0.013733 | -0.10071 | -0.036621 | 0.20599 | 0.018311 | -0.1236 | -1.0529 | -1.0025 | -1.1078 | -0.89722 | -0.93842 | -1.1169 | -1.1673 | 1.1215 | 0.97961 | -121.9299 | 1.0895 | 1.0666 | 0.086975 | -121.9025 | -0.013733 | -0.064087 | -123.0331 | 0.050354 | -0.004578 | 0.059509 | -123.0743 | 1.3092 | 1.3367 | 1.0025 | -122.2595 | 0.20599 | 0.16479 | 0.10071 | -123.3032
953.9219 | 123.3261 | -1.0757 | 122.0901 | 0.5491 | 0.16901 | 0.14078 | 0.0697 | 0.11453 | 0.016137 | 0.041971 | 0.36725 | 0.1806 | 0.0064351 | 0.19664 | 0.019289 | -0.01377 | 0.059509 | 0.10529 | 0.032043 | 0.07782 | 0.10986 | 0.018311 | -0.10071 | -1.0757 | -1.1719 | -0.95215 | -0.99335 | -1.0391 | -1.1124 | -1.1719 | 1.0941 | 0.97504 | -121.9803 | 1.181 | 1.1536 | 0.17853 | -122.0306 | -0.036621 | -0.09613 | -123.0835 | 0 | 0.1236 | 0.21973 | -123.1293 | 1.1856 | 1.1353 | 1.1078 | -122.1909 | 0.082398 | 0.036621 | -0.09613 | -123.262
954.8438 | 123.2254 | -1.0574 | 122.1451 | -0.29014 | 0.14445 | 0.14292 | 0.063291 | 0.11133 | -0.0094983 | 0.03129 | -0.38043 | 0.19128 | -0.0053139 | 0.18383 | 0.0086079 | -0.026588 | 0.036621 | 0.10071 | 0.022888 | 0.054932 | 0.1236 | 0.032043 | -0.1236 | -0.98419 | -0.93384 | -1.0162 | -0.91095 | -0.96588 | -1.0666 | -1.1444 | 1.0895 | 0.93384 | -122.0215 | 1.1581 | 1.1124 | 0.17853 | -122.1085 | -0.009155 | -0.086975 | -123.056 | 0.073242 | 0.041199 | 0.12817 | -123.111 | 1.181 | 1.0941 | 1.0803 | -122.2687 | 0.14648 | 0.091553 | 0.1236 | -123.2895
955.8438 | 123.2666 | -1.0254 | 122.1451 | 0.45754 | 0.13804 | 0.14826 | 0.072904 | 0.11346 | 0.0043877 | 0.03129 | 0.29095 | 0.187 | -0.0031779 | 0.17635 | 0.018221 | -0.012702 | 0.045776 | 0.11444 | 0.041199 | 0.050354 | 0.11444 | 0.036621 | -0.1236 | -0.9201 | -0.94757 | -0.98877 | -0.93384 | -0.97046 | -1.0345 | -1.1169 | 1.062 | 0.90179 | -122.0306 | 1.1398 | 1.0757 | 0.17395 | -122.0993 | -0.009155 | -0.091552 | -123.0789 | 0.10529 | 0.036621 | 0.12817 | -123.1155 | 1.1398 | 1.0712 | 1.0666 | -122.2687 | 0.091553 | 0.054932 | 0.07782 | -123.262
956.8438 | 123.3032 | -1.0162 | 122.1542 | 0.10659 | 0.11561 | 0.14933 | 0.057951 | 0.10919 | -0.016974 | 0.033426 | -0.10577 | 0.17953 | -0.0031779 | 0.16567 | 0.0086079 | -0.021247 | 0.050354 | 0.091553 | 0.036621 | 0.082397 | 0.13733 | 0.032043 | -0.11902 | -0.91553 | -0.88806 | -0.94757 | -0.90637 | -0.95215 | -1.0345 | -1.1124 | 1.0483 | 0.89722 | -122.0169 | 1.1078 | 1.0986 | 0.20142 | -122.1039 | -0.018311 | -0.096131 | -123.0606 | 0.10071 | 0.068664 | 0.16479 | -123.1064 | 1.1536 | 1.0666 | 1.0529 | -122.2733 | 0.10986 | 0.064087 | 0.12817 | -123.2666
957.9062 | 123.2849 | -1.03 | 122.1634 | 0.41177 | 0.14017 | 0.14399 | 0.063291 | 0.1188 | 0.016137 | 0.020609 | 0.2757 | 0.18487 | 0.0010951 | 0.18489 | 0.017153 | -0.026588 | 0.064087 | 0.11902 | 0.041199 | 0.073242 | 0.10071 | 0.045776 | -0.10071 | -0.89264 | -0.92468 | -0.97046 | -0.92468 | -0.96588 | -1.03 | -1.1078 | 1.0757 | 0.92926 | -122.0627 | 1.149 | 1.1032 | 0.17395 | -122.0993 | 0 | -0.07782 | -123.0881 | 0.13733 | 0.059509 | 0.13733 | -123.1293 | 1.1307 | 1.0941 | 1.0712 | -122.2641 | 0.10528 | 0.064087 | 0.10528 | -123.2712
958.8438 | 123.2803 | -1.0117 | 122.1588 | 0.41177 | 0.14658 | 0.13651 | 0.045133 | 0.11667 | -0.0073613 | 0.033426 | 0.2757 | 0.19128 | 0.01498 | 0.1881 | 0.015017 | -0.0084301 | 0.086975 | 0.10529 | 0.041199 | 0.068665 | 0.10986 | 0.018311 | -0.10071 | -0.89722 | -0.9201 | -0.9613 | -0.89264 | -0.95215 | -1.0208 | -1.1078 | 1.03 | 0.91095 | -122.0489 | 1.1169 | 1.0803 | 0.16937 | -122.0718 | -0.009155 | -0.09613 | -123.0515 | 0.11444 | 0.050354 | 0.14648 | -123.111 | 1.1215 | 1.0986 | 1.0529 | -122.2595 | 0.11902 | 0.05951 | 0.091553 | -123.2666
959.8438 | 123.2574 | -1.03 | 122.1817 | 0.2134 | 0.12202 | 0.14719 | 0.060087 | 0.12094 | 0.0054557 | 0.033426 | 1.4048 | 0.18914 | -0.022404 | 0.17849 | 0.011812 | -0.028724 | 0.004578 | 0.064087 | -0.009155 | 0.036621 | 0.11902 | 0.018311 | -0.11444 | -0.95215 | -0.96588 | -1.0025 | -0.96588 | -0.99792 | -1.0757 | -1.149 | 1.0483 | 0.91553 | -122.0627 | 1.0941 | 1.0666 | 0.15106 | -122.1771 | -0.045777 | -0.11902 | -123.1476 | 0.07782 | 0.027466 | 0.14648 | -123.1796 | 1.149 | 1.0345 | 1.0208 | -122.2961 | 0.064087 | 0.032043 | 0.064087 | -123.3307
960.9062 | 123.2071 | -1.0666 | 122.1863 | 0.2134 | 0.1861 | 0.13972 | 0.08679 | 0.10919 | 0.034295 | 0.043039 | 0.046815 | 0.19769 | 0.0096401 | 0.16887 | 0.037447 | -0.038337 | -0.013733 | -0.068665 | -0.11444 | -0.036621 | 0.15564 | 0.013733 | -0.15106 | -0.99335 | -1.0529 | -1.0803 | -0.86975 | -0.91095 | -1.0574 | -1.1261 | 1.0803 | 0.91553 | -122.0306 | 0.99792 | 1.03 | 0.11444 | -122.2 | 0.009155 | -0.05951 | -123.056 | 0.073242 | -0.013733 | 0.045777 | -123.0972 | 1.2222 | 1.0529 | 0.95215 | -122.3373 | 0.19684 | 0.15564 | 0.013733 | -123.3124
961.8438 | 123.2986 | -1.0117 | 122.168 | 0.24392 | 0.11347 | 0.16321 | 0.066496 | 0.11453 | -0.0094983 | 0.029153 | -0.029479 | 0.17739 | 0.0010951 | 0.18169 | 0.015017 | -0.018043 | -0.086975 | -0.11444 | -0.059509 | 0.018311 | 0.054932 | -0.050354 | -0.18768 | -0.91553 | -0.91095 | -0.96588 | -0.91095 | -0.93384 | -1.0162 | -1.0757 | 0.9613 | 0.82397 | -122.113 | 0.89722 | 1.03 | 0.20599 | -122.2549 | -0.004577 | -0.064087 | -123.0789 | 0.096131 | 0.045777 | 0.10986 | -123.1018 | 1.0666 | 0.92468 | 0.95215 | -122.3557 | 0.10071 | 0.07782 | 0.10071 | -123.2437
962.9062 | 123.3215 | -1.0208 | 122.168 | 0.45754 | 0.1594 | 0.14292 | 0.063291 | 0.12308 | 0.018273 | 0.03129 | 0.36725 | 0.17632 | 2.7137e-05 | 0.18169 | 0.010744 | -0.03086 | 0.09613 | 0.10986 | 0.041199 | 0.07782 | 0.10071 | 0.018311 | -0.10071 | -0.83771 | -0.89264 | -0.93842 | -0.93384 | -0.99335 | -1.0666 | -1.1169 | 1.0391 | 0.9201 | -122.0673 | 1.1307 | 1.0986 | 0.17853 | -122.0718 | -0.045776 | -0.09613 | -123.1018 | 0.1831 | 0.082397 | 0.17853 | -123.1613 | 1.1215 | 1.1169 | 1.062 | -122.2687 | 0.086975 | 0.027466 | 0.12817 | -123.2849
963.8438 | 123.3215 | -0.97504 | 122.1725 | 0.51858 | 0.15406 | 0.14826 | 0.072904 | 0.10171 | 0.017205 | 0.029153 | 0.29095 | 0.19128 | -0.0010409 | 0.17528 | 0.02463 | -0.026588 | 0.068665 | 0.073242 | -0.004578 | 0.054932 | 0.11444 | 0.004578 | -0.11902 | -0.87433 | -0.89722 | -0.93842 | -0.88806 | -0.92926 | -1.0117 | -1.0666 | 0.97962 | 0.85602 | -122.0581 | 1.0483 | 1.03 | 0.17395 | -122.1039 | -0.036621 | -0.091552 | -123.0606 | 0.10071 | 0.036621 | 0.12817 | -123.1018 | 1.0895 | 1.0437 | 0.97046 | -122.2916 | 0.086975 | 0.045777 | 0.07782 | -123.2391
964.9062 | 123.317 | -0.97504 | 122.1909 | 0.56436 | 0.16047 | 0.15146 | 0.073972 | 0.1188 | 0.0086597 | 0.032358 | -0.13629 | 0.187 | 2.7137e-05 | 0.18703 | 0.018221 | -0.02552 | 0.09613 | -0.18768 | -0.19684 | -0.027466 | 0.059509 | -0.018311 | -0.16022 | -0.83771 | -0.87433 | -0.93384 | -0.89722 | -0.93384 | -0.97504 | -1.0574 | 0.95673 | 0.81482 | -122.1313 | 0.78735 | 0.94757 | 0.13275 | -122.0947 | 0 | -0.082397 | -123.0881 | 0.13733 | 0.041199 | 0.1236 | -123.1247 | 1.0345 | 1.0712 | 0.7782 | -122.3511 | 0.07782 | 0.041199 | 0.10071 | -123.2483
965.8438 | 123.2803 | -0.97961 | 122.2046 | 0.4728 | 0.14231 | 0.14078 | 0.050474 | 0.11133 | -0.00095325 | 0.035562 | 0.38251 | 0.17953 | -0.0031779 | 0.17955 | 0.01288 | -0.028724 | 0.045776 | 0.09613 | 0.036621 | 0.064087 | 0.11444 | 0.022888 | -0.10071 | -0.86975 | -0.88806 | -0.93842 | -0.86517 | -0.91095 | -0.99335 | -1.0574 | 1.0025 | 0.87891 | -122.0901 | 1.0757 | 1.0437 | 0.1648 | -122.1588 | -0.013733 | -0.07782 | -123.0698 | 0.10986 | 0.041198 | 0.11902 | -123.1155 | 1.0941 | 1.0254 | 1.0162 | -122.3053 | 0.11444 | 0.068664 | 0.091552 | -123.262
966.9062 | 123.2162 | -0.99792 | 122.2321 | 0.41177 | 0.17649 | 0.11622 | 0.057951 | 0.10599 | 0.014001 | 0.041971 | 0.15363 | 0.19128 | 0.010708 | 0.18276 | 0.02463 | -0.032996 | -0.004578 | 0.032043 | -0.07782 | -0.018311 | 0.15106 | 0.009155 | -0.13275 | -0.93842 | -0.99335 | -1.0345 | -0.84686 | -0.87433 | -1.0345 | -1.0941 | 1.0071 | 0.86517 | -122.081 | 1.03 | 0.97961 | 0.11444 | -122.2366 | -0.036621 | -0.09613 | -123.0789 | 0.059509 | -0.036621 | 0.059509 | -123.1064 | 1.149 | 0.99335 | 0.9201 | -122.3648 | 0.15106 | 0.1236 | 0.004578 | -123.3261
967.8438 | 123.3032 | -0.96588 | 122.2366 | -4.6389 | 0.11881 | 0.14719 | 0.05261 | 0.10705 | -0.0062933 | 0.03129 | -0.10577 | 0.18914 | -0.0085179 | 0.18062 | 0.011812 | -0.027656 | 0.032043 | 0.15106 | 0.041199 | 0.068665 | 0.10071 | 0.013733 | -0.11902 | -0.83771 | -0.79651 | -0.87891 | -0.84228 | -0.89264 | -0.98877 | -1.0483 | 0.97961 | 0.84686 | -122.1359 | 1.1169 | 1.0345 | 0.18768 | -122.2046 | -0.022889 | -0.082398 | -123.0789 | 0.12817 | 0.086975 | 0.16937 | -123.1293 | 1.0666 | 0.99792 | 1.0071 | -122.3557 | 0.1236 | 0.073242 | 0.16937 | -123.2849
968.9062 | 123.23 | -0.99792 | 122.2183 | 0.56436 | 0.17435 | 0.13224 | 0.0697 | 0.11026 | 0.028955 | 0.035562 | 0.15363 | 0.20409 | 0.0075041 | 0.18489 | 0.018221 | -0.023383 | -0.009155 | -0.027466 | -0.082397 | -0.022888 | 0.13733 | -0.018311 | -0.16479 | -0.91095 | -0.96588 | -1.0071 | -0.81482 | -0.87891 | -1.0071 | -1.0803 | 0.97961 | 0.83313 | -122.081 | 0.97046 | 0.97504 | 0.14191 | -122.2275 | -0.009155 | -0.082397 | -123.0331 | 0.086975 | -0.009155 | 0.073242 | -123.0972 | 1.1353 | 0.98877 | 0.91553 | -122.3831 | 0.18311 | 0.11902 | 0.032044 | -123.2986
969.8438 | 123.2849 | -0.93842 | 122.2504 | -0.045996 | 0.14552 | 0.13972 | 0.059019 | 0.1156 | -0.0062933 | 0.028085 | -0.30414 | 0.187 | 2.7137e-05 | 0.17849 | 0.011812 | -0.029792 | 0.054932 | 0.11902 | 0.054932 | 0.073242 | 0.13733 | 0.032043 | -0.11444 | -0.85144 | -0.80109 | -0.89722 | -0.83313 | -0.88806 | -0.97504 | -1.0391 | 0.97046 | 0.82398 | -122.113 | 1.0574 | 1.0117 | 0.18768 | -122.1954 | -0.036621 | -0.10071 | -123.0835 | 0.086976 | 0.041199 | 0.14191 | -123.1384 | 1.0757 | 0.99335 | 0.99335 | -122.3648 | 0.10529 | 0.050354 | 0.13733 | -123.2895
970.9062 | 123.2483 | -0.99792 | 122.2641 | -0.19858 | 0.17329 | 0.1536 | 0.079313 | 0.12201 | 0.02575 | 0.035562 | -0.5025 | 0.19982 | 0.017117 | 0.17315 | 0.02463 | -0.034064 | 0.018311 | 0.022888 | -0.054932 | 0.018311 | 0.1236 | -0.013733 | -0.15564 | -0.90179 | -0.89722 | -0.9613 | -0.8194 | -0.87433 | -1.0071 | -1.0666 | 0.98419 | 0.84228 | -122.1405 | 1.0208 | 1.0162 | 0.17395 | -122.2458 | -0.009155 | -0.068664 | -123.0835 | 0.096131 | 0.036621 | 0.10528 | -123.1384 | 1.1215 | 1.0162 | 0.94299 | -122.4197 | 0.17853 | 0.1236 | 0.10071 | -123.3307
971.8438 | 123.23 | -0.98877 | 122.2778 | 0.97634 | 0.17435 | 0.14292 | 0.082517 | 0.11774 | 0.015069 | 0.035562 | 0.26044 | 0.18594 | 0.0042991 | 0.17955 | 0.017153 | -0.020179 | -0.032043 | -0.013733 | -0.086975 | -0.004578 | 0.13733 | -0.013733 | -0.15106 | -0.91095 | -0.93842 | -0.98419 | -0.81482 | -0.8606 | -0.99792 | -1.0712 | 0.97504 | 0.83771 | -122.1405 | 0.97504 | 0.98419 | 0.14648 | -122.3099 | -0.009155 | -0.082397 | -123.0927 | 0.07782 | 0.004578 | 0.086975 | -123.1384 | 1.1261 | 0.95673 | 0.9018 | -122.4289 | 0.17395 | 0.12817 | 0.050354 | -123.349
972.8438 | 123.2758 | -0.95215 | 122.2412 | 0.42703 | 0.17222 | 0.13758 | 0.084654 | 0.11987 | 0.010797 | 0.038766 | 0.29095 | 0.20623 | 0.0096401 | 0.19344 | 0.023561 | -0.019111 | -0.004578 | -0.004578 | -0.054932 | 0 | 0.15106 | -0.009155 | -0.14648 | -0.86975 | -0.88348 | -0.93842 | -0.82855 | -0.8606 | -0.96588 | -1.03 | 0.94299 | 0.80566 | -122.0901 | 0.94757 | 0.95215 | 0.14648 | -122.2458 | -0.013733 | -0.07782 | -123.0698 | 0.082397 | 0.013732 | 0.091552 | -123.1018 | 1.1032 | 0.94757 | 0.89722 | -122.3877 | 0.1236 | 0.091552 | 0.068664 | -123.2712
973.9062 | 123.2346 | -0.95215 | 122.2961 | 0.060816 | 0.18076 | 0.14826 | 0.077177 | 0.10065 | 0.011865 | 0.039835 | 0.41303 | 0.19128 | 0.0096401 | 0.18169 | 0.016085 | -0.027656 | 0.032043 | 0.050354 | -0.032043 | 0.036621 | 0.15564 | 0 | -0.11444 | -0.83771 | -0.85602 | -0.94299 | -0.75989 | -0.81024 | -0.94757 | -1.0117 | 0.95215 | 0.83771 | -122.1405 | 1.0025 | 0.98877 | 0.15106 | -122.2641 | 0.004577 | -0.05951 | -123.056 | 0.11444 | 0.009155 | 0.068665 | -123.1064 | 1.1078 | 0.98419 | 0.9201 | -122.4106 | 0.19226 | 0.14191 | 0.09613 | -123.3078
974.8438 | 123.2986 | -0.90637 | 122.2504 | 0.045557 | 0.12629 | -0.090998 | 0.054746 | 0.10705 | -0.027656 | 0.038766 | 0.077332 | 0.17953 | -0.018131 | 0.16674 | 0.0043349 | -0.01377 | 0.004578 | 0.10071 | 0.018311 | 0.068665 | 0.12817 | 0.013733 | -0.12817 | -0.81482 | -0.78735 | -0.83313 | -0.79651 | -0.85144 | -0.92926 | -1.0025 | 0.9201 | 0.7782 | -122.1222 | 1.0071 | 0.97504 | 0.19684 | -122.2458 | -0.022888 | -0.09613 | -123.0469 | 0.091553 | 0.073242 | 0.16937 | -123.1018 | 1.0345 | 0.91095 | 0.92468 | -122.3785 | 0.10986 | 0.054932 | 0.11902 | -123.2529
975.9062 | 123.2025 | -0.98419 | 122.2961 | -0.27488 | 0.14338 | 0.14719 | 0.073972 | 0.11133 | 0.0011837 | 0.040903 | -0.39569 | 0.18914 | 0.0096401 | 0.18703 | 0.0064719 | -0.021247 | -0.009155 | -0.009155 | -0.064087 | 0.022888 | 0.16022 | -0.018311 | -0.15106 | -0.92926 | -0.89264 | -0.95673 | -0.75073 | -0.83313 | -0.98419 | -1.0483 | 0.96588 | 0.83313 | -122.1359 | 0.97504 | 1.0071 | 0.17395 | -122.3053 | 0 | -0.064087 | -123.0469 | 0.054932 | 0.027466 | 0.091553 | -123.1293 | 1.1444 | 0.97504 | 0.9201 | -122.4472 | 0.23346 | 0.15106 | 0.091553 | -123.3444
976.8438 | 123.2574 | -0.94299 | 122.2687 | 0.50332 | 0.17115 | 0.13651 | 0.078245 | 0.11667 | 0.014001 | 0.040903 | 0.36725 | 0.19021 | 0.010708 | 0.18596 | 0.021425 | -0.02552 | -0.004578 | 0 | -0.082397 | 0 | 0.12817 | -0.009155 | -0.14191 | -0.86975 | -0.90179 | -0.93842 | -0.80109 | -0.85144 | -0.97504 | -1.0254 | 0.93384 | 0.80109 | -122.1405 | 0.94299 | 0.94299 | 0.14191 | -122.2733 | -0.032044 | -0.082398 | -123.0698 | 0.073242 | 0.004577 | 0.086975 | -123.1201 | 1.0712 | 0.93841 | 0.8606 | -122.4106 | 0.14191 | 0.091553 | 0.041199 | -123.2941
977.9062 | 123.2117 | -0.95215 | 122.2916 | -0.33591 | 0.1562 | 0.13331 | 0.065427 | 0.1188 | 0.019342 | 0.045175 | -0.44147 | 0.19341 | 0.0064351 | 0.19024 | 0.013948 | -0.024451 | -0.022888 | -0.018311 | -0.07782 | 0.009155 | 0.15106 | -0.027466 | -0.17853 | -0.91095 | -0.88806 | -0.97046 | -0.75989 | -0.8194 | -0.97504 | -1.0574 | 0.92468 | 0.77362 | -122.1405 | 0.93384 | 0.9613 | 0.18768 | -122.3145 | -0.022889 | -0.10529 | -123.0515 | 0.041198 | -0.018311 | 0.086975 | -123.111 | 1.1032 | 0.92926 | 0.87433 | -122.4701 | 0.19226 | 0.13275 | 0.064086 | -123.349
978.8438 | 123.2391 | -0.94757 | 122.3099 | -4.4863 | 0.15513 | 0.14826 | 0.081449 | 0.1156 | 0.016137 | 0.033426 | 0.15363 | 0.19128 | -0.0021099 | 0.17955 | 0.021425 | -0.028724 | 0.004578 | -0.059509 | -0.10071 | -0.009155 | 0.16479 | -0.004578 | -0.14648 | -0.88348 | -0.92468 | -0.97961 | -0.76904 | -0.83771 | -0.95673 | -1.03 | 0.94299 | 0.80109 | -122.1451 | 0.88806 | 0.93842 | 0.13733 | -122.3053 | -0.009155 | -0.082397 | -123.0789 | 0.064087 | -0.032043 | 0.050354 | -123.1476 | 1.1124 | 0.95215 | 0.84686 | -122.4564 | 0.17853 | 0.10986 | 0.022888 | -123.3398
979.9062 | 123.2391 | -0.95215 | 122.319 | -0.19858 | 0.17542 | 0.13331 | 0.078245 | 0.12521 | 0.015069 | 0.03129 | -0.42621 | 0.19128 | -0.011723 | 0.1881 | 0.013948 | -0.021247 | -0.009155 | -0.013733 | -0.09613 | 0.013733 | 0.14648 | -0.009155 | -0.15564 | -0.9201 | -0.86975 | -0.9613 | -0.75531 | -0.8194 | -0.97046 | -1.03 | 0.94299 | 0.79651 | -122.1725 | 0.93841 | 0.96588 | 0.16937 | -122.3282 | -0.018311 | -0.07782 | -123.0743 | 0.032043 | -0.009156 | 0.068664 | -123.1384 | 1.0986 | 0.94299 | 0.85602 | -122.4747 | 0.19684 | 0.13275 | 0.082397 | -123.349
980.8438 | 123.2071 | -0.92468 | 122.3373 | 0.38125 | 0.16047 | 0.13865 | 0.073972 | 0.11346 | 0.02041 | 0.041971 | 0.21466 | 0.19448 | 0.0032311 | 0.17101 | 0.02997 | -0.024451 | -0.041199 | -0.068665 | -0.091553 | 0 | 0.14191 | -0.018311 | -0.15106 | -0.77362 | -1.1673 | -0.91553 | -0.75531 | -0.78278 | -0.9201 | -0.99335 | 0.90637 | 0.77362 | -122.1954 | 0.85602 | 0.92468 | 0.15106 | -122.3785 | 0.004578 | -0.068664 | -123.0927 | 0.15106 | 0.009156 | 0.07782 | -123.1201 | 1.0666 | 0.88348 | 0.83313 | -122.4884 | 0.16937 | 0.14191 | -0.24261 | -123.3307
981.9062 | 123.2346 | -0.93842 | 122.3007 | 0.57961 | 0.16581 | 0.14506 | 0.067564 | 0.10812 | 0.016137 | 0.040903 | -0.21259 | 0.19341 | -0.0010409 | 0.17955 | 0.016085 | -0.036201 | 0.064087 | 0.050354 | -0.041199 | 0.018311 | 0.16937 | 0 | -0.13733 | -0.8606 | -0.8606 | -0.92926 | -0.7782 | -0.81482 | -0.93842 | -1.0117 | 0.93842 | 0.80109 | -122.1313 | 0.98877 | 0.95673 | 0.15564 | -122.2366 | 0 | -0.073242 | -123.0789 | 0.07782 | 0.009156 | 0.082398 | -123.1155 | 1.1078 | 1.0025 | 0.89722 | -122.438 | 0.16022 | 0.1236 | 0.07782 | -123.3124
982.8438 | 123.2574 | -0.91553 | 122.319 | 0.41177 | 0.17222 | 0.14612 | 0.068632 | 0.11987 | 0.0065237 | 0.03663 | 0.41303 | 0.19769 | 0.010708 | 0.18489 | 0.016085 | -0.010566 | -0.018311 | -0.027466 | -0.082397 | -0.004578 | 0.14191 | -0.022888 | -0.16022 | -0.85144 | -0.88348 | -0.89722 | -0.75989 | -0.79651 | -0.92468 | -1.0071 | 0.89264 | 0.75531 | -122.1771 | 0.88806 | 0.91095 | 0.15564 | -122.3373 | -0.009156 | -0.091553 | -123.0789 | 0.064087 | 0.01831 | 0.10986 | -123.1155 | 1.0574 | 0.89722 | 0.83313 | -122.4792 | 0.15564 | 0.11902 | 0.032043 | -123.3261
983.9062 | 123.1934 | -0.92468 | 122.3465 | -0.21384 | 0.15726 | 0.1504 | 0.072904 | 0.11133 | -0.0062933 | 0.029153 | -0.5025 | 0.17953 | -0.014927 | 0.17421 | 0.010744 | -0.021247 | -0.068665 | 0.082397 | -0.045776 | -0.013733 | 0.14648 | -0.013733 | -0.16479 | -0.89264 | -0.85602 | -0.92926 | -0.74158 | -0.79193 | -0.97046 | -1.0208 | 0.91095 | 0.75989 | -122.2 | 1.0071 | 0.91095 | 0.15106 | -122.4152 | -0.045776 | -0.09613 | -123.0881 | 0.032044 | -0.004577 | 0.091553 | -123.1384 | 1.0712 | 0.85602 | 0.87891 | -122.5113 | 0.18311 | 0.13275 | 0.068665 | -123.3673
984.8438 | 123.317 | -0.87433 | 122.3373 | 0.50332 | 0.14979 | 0.13865 | 0.080381 | 0.1188 | -0.0062933 | 0.022745 | 0.51984 | 0.1838 | -0.0085179 | 0.17101 | 0.0096759 | -0.018043 | 0 | 0.11444 | 0.027466 | 0.068665 | 0.064087 | -0.004578 | -0.14191 | -0.77362 | -0.75073 | -0.81024 | -0.78735 | -0.83771 | -0.89722 | -0.97961 | 0.86975 | 0.73242 | -122.2733 | 0.98877 | 0.94299 | 0.21057 | -122.3373 | -0.022888 | -0.10528 | -123.1247 | 0.10071 | 0.064087 | 0.16937 | -123.175 | 0.93842 | 0.87433 | 0.9018 | -122.4792 | 0.086975 | 0.036621 | 0.1236 | -123.317
985.9062 | 123.2437 | -0.89722 | 122.3282 | -0.29014 | 0.13483 | 0.15681 | 0.056883 | 0.11453 | -0.0041573 | 0.030222 | -0.33466 | 0.19662 | -0.023472 | 0.18917 | 0.0032669 | -0.014838 | 0.041199 | 0.086975 | 0.013733 | 0.064087 | 0.12817 | 0.009155 | -0.13733 | -0.82855 | -0.80566 | -0.86975 | -0.76446 | -0.79193 | -0.90637 | -1.0071 | 0.90637 | 0.75989 | -122.2 | 0.98419 | 0.9613 | 0.20142 | -122.287 | -0.009155 | -0.10986 | -123.0927 | 0.068665 | 0.027466 | 0.13733 | -123.1201 | 1.0254 | 0.93842 | 0.91095 | -122.4655 | 0.13275 | 0.10529 | 0.091553 | -123.3353
986.8438 | 123.2162 | -0.93842 | 122.3328 | 0.39651 | 0.17115 | 0.09699 | 0.045133 | 0.11774 | 0.0086597 | 0.030222 | 0.30621 | 0.19769 | -0.0031779 | 0.17528 | 0.020357 | -0.031928 | -0.073242 | 0.036621 | -0.07782 | -0.022888 | 0.18768 | 0 | -0.12817 | -0.86517 | -0.90179 | -0.93384 | -0.75073 | -0.79193 | -0.93842 | -1.0071 | 0.93842 | 0.81024 | -122.1451 | 0.97504 | 0.91553 | 0.10529 | -122.406 | 0 | -0.068664 | -123.0835 | 0.073243 | 0.004578 | 0.073242 | -123.1247 | 1.1261 | 0.86517 | 0.8606 | -122.4609 | 0.18768 | 0.14648 | 0.036622 | -123.3398
987.9062 | 123.2071 | -0.89264 | 122.3557 | -0.33591 | 0.14765 | 0.14399 | 0.064359 | 0.11774 | 0.00011475 | 0.021677 | -0.44147 | 0.19448 | -0.010654 | 0.17955 | 0.0075399 | -0.029792 | -0.032043 | -0.022888 | -0.091553 | -0.009155 | 0.13733 | -0.036621 | -0.15564 | -0.70496 | -0.71411 | -0.97504 | -0.69122 | -0.737 | -0.89264 | -0.95215 | 0.85602 | 0.737 | -122.2183 | 0.86975 | 0.88348 | 0.14649 | -122.3877 | 0 | -0.059509 | -123.0469 | 0.18768 | -0.082398 | -0.022889 | -123.0927 | 1.03 | 0.8606 | 0.80109 | -122.5113 | 0.20142 | 0.15564 | 0.17853 | -123.3078
988.8438 | 123.2346 | -0.91095 | 122.3145 | 3.372 | 0.17222 | 0.13437 | 0.078245 | 0.10919 | 0.027886 | 0.033426 | -0.15155 | 0.19234 | 0.02673 | 0.17849 | 0.010744 | -0.02552 | 0.064087 | 0.059509 | 0 | 0.041199 | 0.19226 | 0.027466 | -0.09613 | -0.82855 | -0.82855 | -0.91095 | -0.77362 | -0.79651 | -0.93842 | -0.98877 | 0.93842 | 0.81482 | -122.1222 | 0.97046 | 0.95215 | 0.13733 | -122.2504 | -0.027466 | -0.07782 | -123.0881 | 0.082398 | 0 | 0.07782 | -123.111 | 1.1032 | 0.97504 | 0.91095 | -122.4106 | 0.13733 | 0.11444 | 0.082398 | -123.3032
989.9062 | 123.2666 | -0.91553 | 122.3785 | 0.35073 | 0.16901 | 0.14292 | 0.053678 | 0.11453 | 0.017205 | 0.038766 | 0.15363 | 0.18914 | -0.0042459 | 0.18276 | 0.020357 | -0.024451 | -0.018311 | -0.07782 | -0.1236 | -0.013733 | 0.15564 | -0.009155 | -0.16022 | -0.86975 | -0.88348 | -0.95215 | -0.71869 | -0.7782 | -0.91553 | -0.99792 | 0.90637 | 0.75531 | -122.2229 | 0.83771 | 0.90179 | 0.14648 | -122.3969 | 0 | -0.082398 | -123.0972 | 0.045776 | -0.036621 | 0.045777 | -123.1567 | 1.0712 | 0.89722 | 0.79193 | -122.5388 | 0.19684 | 0.13733 | 0.032043 | -123.3765
990.8438 | 123.2666 | -0.90179 | 122.3648 | 0.44228 | 0.16154 | 0.13437 | 0.076109 | 0.12201 | 0.016137 | 0.035562 | 0.22992 | 0.19234 | 0.0075041 | 0.18917 | 6.2882e-05 | -0.018043 | -0.009155 | -0.032043 | -0.07782 | -0.018311 | 0.14648 | -0.032043 | -0.13275 | -0.83313 | -0.87433 | -0.91095 | -0.75989 | -0.78735 | -0.91095 | -0.97961 | 0.86975 | 0.76904 | -122.2183 | 0.86975 | 0.88348 | 0.11444 | -122.374 | -0.009156 | -0.07782 | -123.1247 | 0.068664 | -0.009156 | 0.068664 | -123.1522 | 1.0483 | 0.89264 | 0.82397 | -122.4976 | 0.14191 | 0.11444 | 0.027465 | -123.3444
991.9062 | 123.2437 | -0.87433 | 122.319 | -0.21384 | 0.1327 | 0.14826 | 0.062223 | 0.12948 | -0.031928 | 0.03129 | -0.33466 | 0.18594 | -0.0010409 | 0.17101 | 0.0064719 | -0.018043 | 0.045776 | 0.091553 | 0.004578 | 0.059509 | 0.11902 | -0.009155 | -0.14191 | -0.82398 | -0.76446 | -0.84686 | -0.75989 | -0.7782 | -0.90637 | -0.96588 | 0.86517 | 0.73242 | -122.2 | 0.96588 | 0.93384 | 0.20142 | -122.2733 | -0.032043 | -0.091552 | -123.0789 | 0.050354 | 0.027466 | 0.11902 | -123.0972 | 0.99335 | 0.92011 | 0.87891 | -122.4609 | 0.11444 | 0.096131 | 0.10986 | -123.2849
992.8438 | 123.2254 | -0.9201 | 122.3465 | -0.015478 | 0.18504 | 0.13865 | 0.077177 | 0.10705 | 0.011865 | 0.047311 | -0.029479 | 0.19662 | 0.0032311 | 0.17742 | 0.023561 | -0.040473 | 0.018311 | 0.013733 | -0.059509 | 0.013733 | 0.12817 | -0.018311 | -0.16937 | -0.8606 | -0.84686 | -0.94757 | -0.737 | -0.77362 | -0.91095 | -1.0025 | 0.90179 | 0.75073 | -122.2183 | 0.93384 | 0.93384 | 0.18311 | -122.3282 | 0.009155 | -0.082397 | -123.0835 | 0.059509 | -0.027466 | 0.054931 | -123.1201 | 1.0483 | 0.93842 | 0.8606 | -122.5159 | 0.1831 | 0.14648 | 0.073242 | -123.349
993.9062 | 123.3215 | -0.85602 | 122.3648 | 0.50332 | 0.15192 | 0.14719 | 0.067564 | 0.12094 | -0.011634 | 0.023813 | -0.22784 | 0.19021 | -0.012791 | 0.1678 | 0.011812 | -0.020179 | 0.054932 | 0.12817 | 0.045776 | 0.07782 | 0.10529 | 0.022888 | -0.10529 | -0.77362 | -0.69122 | -0.78735 | -0.737 | -0.76446 | -0.88348 | -0.94299 | 0.87891 | 0.75073 | -122.2595 | 0.98419 | 0.93384 | 0.18311 | -122.3099 | -0.027466 | -0.086975 | -123.1018 | 0.082397 | 0.068664 | 0.15564 | -123.1293 | 0.9613 | 0.91095 | 0.90179 | -122.4701 | 0.11902 | 0.091553 | 0.16479 | -123.3078
994.8438 | 123.23 | -0.89722 | 122.3557 | 0.62539 | 0.16261 | 0.13544 | 0.065427 | 0.11239 | 0.02041 | 0.035562 | 0.2757 | 0.19341 | 0.0053671 | 0.17849 | 0.02463 | -0.027656 | -0.027466 | -0.036621 | -0.086975 | 0.004578 | 0.13733 | -0.018311 | -0.15564 | -0.83313 | -0.85602 | -0.89264 | -0.72784 | -0.75989 | -0.90179 | -0.97961 | 0.87891 | 0.74158 | -122.2183 | 0.8606 | 0.9018 | 0.16022 | -122.3831 | -0.004577 | -0.082397 | -123.0835 | 0.064087 | 0.004578 | 0.086975 | -123.1155 | 1.0345 | 0.86975 | 0.81024 | -122.5113 | 0.16937 | 0.13733 | 0.041199 | -123.3353
995.9062 | 123.3261 | -0.83313 | 122.3465 | -0.19858 | 0.13377 | 0.16108 | 0.050474 | 0.1156 | -0.024451 | 0.022745 | 1.0997 | 0.1806 | -0.0095859 | 0.17528 | 0.015017 | -0.020179 | 0.059509 | 0.1236 | 0.050354 | 0.09613 | 0.1236 | 0 | -0.13275 | -0.74616 | -0.70953 | -0.76904 | -0.76446 | -0.78735 | -0.87433 | -0.93384 | 0.83313 | 0.70038 | -122.2229 | 0.95673 | 0.92926 | 0.22888 | -122.287 | -0.041199 | -0.10071 | -123.111 | 0.086975 | 0.064087 | 0.16479 | -123.1339 | 0.95673 | 0.89264 | 0.88348 | -122.4792 | 0.068665 | 0.045776 | 0.1236 | -123.2803
996.8438 | 123.2254 | -0.89264 | 122.3694 | 0.091333 | 0.17222 | 0.13865 | 0.087858 | 0.12201 | 0.032159 | 0.03129 | -0.090514 | 0.19341 | -0.0063819 | 0.18917 | 0.021425 | -0.038337 | 0.032043 | 0.004578 | -0.059509 | 0.013733 | 0.13733 | -0.004578 | -0.15106 | -0.8194 | -0.85144 | -0.91095 | -0.71869 | -0.77362 | -0.90637 | -0.97961 | 0.88806 | 0.74158 | -122.2321 | 0.89722 | 0.90637 | 0.16479 | -122.3373 | -0.013733 | -0.086975 | -123.0881 | 0.073242 | -0.018311 | 0.068664 | -123.143 | 1.03 | 0.92468 | 0.83313 | -122.5204 | 0.17395 | 0.11902 | 0.041199 | -123.349
997.8438 | 123.2666 | -0.85602 | 122.5021 | -0.061255 | 0.17329 | 0.13651 | 0.077177 | 0.11133 | 0.012933 | 0.029153 | -0.22784 | 0.19875 | -0.0031779 | 0.19878 | 0.011812 | -0.026588 | 0.045776 | 0.032043 | -0.045776 | 0.027466 | 0.12817 | -0.004578 | -0.14648 | -0.79651 | -0.7782 | -0.85602 | -0.72327 | -0.75073 | -0.89264 | -0.97046 | 0.85144 | 0.70953 | -122.374 | 0.88806 | 0.88348 | 0.17395 | -122.4564 | -0.036621 | -0.11444 | -123.2254 | 0.059509 | 0 | 0.11444 | -123.2529 | 0.98419 | 0.90179 | 0.81024 | -122.6486 | 0.13275 | 0.10529 | 0.07782 | -123.4726
998.9062 | 123.2208 | -0.90179 | 122.3969 | -0.3054 | 0.15513 | 0.13544 | 0.072904 | 0.11346 | -0.0073613 | 0.030222 | -0.41095 | 0.19128 | 0.0010951 | 0.1913 | 6.2882e-05 | -0.03086 | -0.009155 | -0.018311 | -0.086975 | 0 | 0.20599 | 0.004578 | -0.1236 | -0.8606 | -0.80109 | -0.89722 | -0.69122 | -0.73242 | -0.89722 | -0.97046 | 0.90637 | 0.7782 | -122.1909 | 0.88348 | 0.90179 | 0.1236 | -122.406 | 0.004577 | -0.068665 | -123.0881 | 0.041198 | 0.004577 | 0.073242 | -123.1293 | 1.1078 | 0.89264 | 0.81482 | -122.5204 | 0.21057 | 0.16937 | 0.10071 | -123.3673
999.8438 | 123.2666 | -0.81482 | 122.4014 | 0.13711 | 0.16154 | 0.13544 | 0.067564 | 0.10919 | 0.023614 | 0.03663 | -0.19733 | 0.187 | 2.7137e-05 | 0.18276 | 0.019289 | -0.029792 | 0.036621 | 0.041199 | -0.032043 | 0.041199 | 0.14191 | -0.009155 | -0.14648 | -0.79193 | -0.74158 | -0.85602 | -0.64087 | -0.69122 | -0.82855 | -0.90637 | 0.80566 | 0.66833 | -122.2595 | 0.85602 | 0.85602 | 0.18768 | -122.3648 | -0.013733 | -0.091553 | -123.0423 | 0.022888 | -0.041199 | 0.050354 | -123.0927 | 0.95673 | 0.85144 | 0.78278 | -122.5479 | 0.17395 | 0.1236 | 0.073242 | -123.3078
1000.9062 | 123.3215 | -0.82398 | 122.4106 | -0.27488 | 0.1562 | 0.14933 | 0.064359 | 0.10812 | -0.018043 | 0.034494 | -0.28888 | 0.17739 | -0.013859 | 0.18489 | 0.011812 | -0.010566 | 0.036621 | 0.11902 | 0.054932 | 0.086975 | 0.091553 | 0.018311 | -0.1236 | -0.737 | -0.68207 | -0.75989 | -0.73242 | -0.7782 | -0.84686 | -0.92468 | 0.84229 | 0.70038 | -122.319 | 0.94299 | 0.91095 | 0.21057 | -122.374 | -0.022888 | -0.10071 | -123.143 | 0.086975 | 0.064087 | 0.1648 | -123.1888 | 0.91553 | 0.8606 | 0.87891 | -122.5342 | 0.091553 | 0.045777 | 0.14191 | -123.3353
1001.8438 | 123.2483 | -0.88348 | 122.3923 | -0.2291 | 0.17329 | 0.15253 | 0.081449 | 0.11346 | 0.014001 | 0.035562 | -0.53302 | 0.20303 | -0.0063819 | 0.1881 | 0.015017 | -0.03086 | -0.027466 | -0.009155 | -0.073242 | 0.009155 | 0.14191 | -0.032043 | -0.16022 | -0.84686 | -0.8194 | -0.88806 | -0.70496 | -0.74616 | -0.90179 | -0.97961 | 0.85144 | 0.72327 | -122.2504 | 0.87433 | 0.89264 | 0.16937 | -122.4197 | -0.01831 | -0.09613 | -123.0972 | 0.036621 | -0.004578 | 0.091552 | -123.1384 | 1.0254 | 0.85602 | 0.81024 | -122.5525 | 0.17853 | 0.13733 | 0.064087 | -123.3719
1002.9062 | 123.23 | -0.84228 | 122.406 | -0.33591 | 0.15192 | 0.13651 | 0.079313 | 0.10812 | -0.0020213 | 0.020609 | -0.42621 | 0.187 | -0.0085179 | 0.18596 | -0.011686 | -0.03086 | -0.050354 | 0 | -0.068665 | 0 | 0.15106 | -0.036621 | -0.17395 | -0.73242 | -0.95673 | -0.90179 | -0.65002 | -0.69122 | -0.85602 | -0.92468 | 0.80566 | 0.66833 | -122.2549 | 0.84228 | 0.84228 | 0.17395 | -122.4564 | -0.013733 | -0.082398 | -123.056 | 0.10986 | -0.059509 | 0.022889 | -123.0972 | 0.99335 | 0.79193 | 0.77362 | -122.58 | 0.19226 | 0.15106 | -0.11444 | -123.3307
1003.8438 | 123.2483 | -0.89264 | 122.3831 | -0.19858 | 0.16581 | 0.1504 | 0.088926 | 0.11453 | 0.015069 | 0.025949 | -0.39569 | 0.1838 | 0.010708 | 0.18596 | 0.0021989 | -0.03086 | -0.045776 | -0.004578 | -0.073242 | -0.009155 | 0.14191 | -0.013733 | -0.16937 | -0.85602 | -0.79651 | -0.89722 | -0.72327 | -0.74616 | -0.88806 | -0.9613 | 0.87891 | 0.72327 | -122.2412 | 0.88806 | 0.88348 | 0.16022 | -122.4289 | 0.004577 | -0.068665 | -123.1064 | 0.036621 | -0.004578 | 0.064087 | -123.1293 | 1.0345 | 0.84686 | 0.8194 | -122.5525 | 0.16937 | 0.14648 | 0.09613 | -123.3444
1004.9062 | 123.3032 | -0.85602 | 122.3511 | -0.21384 | 0.13163 | 0.16108 | 0.065427 | 0.12201 | -0.016974 | 0.038766 | -0.15155 | 0.18594 | -0.015995 | 0.17849 | 0.0054039 | -0.027656 | 0.059509 | 0.17395 | 0.064087 | 0.10071 | 0.12817 | 0.004578 | -0.10986 | -0.72784 | -0.70496 | -0.72327 | -0.737 | -0.78278 | -0.88348 | -0.95673 | 0.8606 | 0.74615 | -122.2229 | 1.03 | 0.95673 | 0.21057 | -122.2916 | -0.027466 | -0.10071 | -123.0881 | 0.12817 | 0.13275 | 0.23346 | -123.1338 | 0.98419 | 0.91553 | 0.9201 | -122.4609 | 0.11902 | 0.073242 | 0.15106 | -123.3078
1005.8438 | 123.2254 | -0.86975 | 122.4014 | -0.29014 | 0.15833 | 0.14826 | 0.079313 | 0.10599 | -0.0052253 | 0.033426 | -0.15155 | 0.18914 | 0.0085721 | 0.18596 | 0.010744 | -0.035133 | 0.11444 | -0.086975 | -0.11444 | 0.009155 | 0.19684 | 0.045776 | -0.10529 | -0.82398 | -0.83771 | -0.90179 | -0.68207 | -0.737 | -0.90179 | -0.97046 | 0.91553 | 0.76447 | -122.2046 | 0.78278 | 0.87891 | 0.11444 | -122.287 | -0.032043 | -0.10071 | -123.0835 | 0.045776 | -0.032043 | 0.068665 | -123.1384 | 1.0666 | 0.98419 | 0.75531 | -122.5067 | 0.18768 | 0.13275 | 0.032043 | -123.3719
1006.9062 | 123.3719 | -0.83313 | 122.3557 | 0.045557 | 0.14445 | 0.15146 | 0.057951 | 0.10171 | -0.022315 | 0.021677 | 0.0010378 | 0.17632 | -0.018131 | 0.18276 | 0.010744 | -0.022315 | 0.045776 | 0.13733 | 0.045776 | 0.082397 | 0.13275 | 0.022888 | -0.091553 | -0.70496 | -0.6958 | -0.75531 | -0.73242 | -0.75531 | -0.84228 | -0.92926 | 0.85602 | 0.74158 | -122.2229 | 0.97046 | 0.91553 | 0.17395 | -122.3099 | -0.009155 | -0.09613 | -123.0881 | 0.12817 | 0.07782 | 0.17395 | -123.111 | 0.96588 | 0.87891 | 0.87891 | -122.4472 | 0.10071 | 0.07782 | 0.13733 | -123.2849
1007.8438 | 123.2666 | -0.88806 | 122.3831 | -0.25962 | 0.17435 | 0.14399 | 0.089994 | 0.11239 | 0.022546 | 0.023813 | -0.54828 | 0.18807 | 0.016048 | 0.18917 | 0.018221 | -0.040473 | -0.022888 | -0.009155 | -0.086975 | 0 | 0.16479 | -0.027466 | -0.17395 | -0.8194 | -0.79651 | -0.87891 | -0.6958 | -0.75531 | -0.91095 | -0.97046 | 0.8606 | 0.71411 | -122.2183 | 0.87891 | 0.88806 | 0.17395 | -122.406 | -0.022888 | -0.082397 | -123.0789 | 0.068665 | 0.009156 | 0.091553 | -123.1384 | 1.0529 | 0.86517 | 0.80109 | -122.5571 | 0.19226 | 0.13275 | 0.091553 | -123.3536
1008.9062 | 123.2712 | -0.89264 | 122.3557 | 0.24392 | 0.14552 | 0.14078 | 0.060087 | 0.10385 | -0.020179 | 0.025949 | 0.21466 | 0.18487 | -0.0021099 | 0.18489 | 0.0086079 | -0.0062931 | -0.013733 | 0.073242 | -0.004578 | 0.032043 | 0.11444 | 0.009155 | -0.12817 | -1.0757 | -0.86517 | -0.89722 | -0.75531 | -0.8194 | -0.9201 | -0.98419 | 0.90179 | 0.76446 | -122.2412 | 0.96588 | 0.92468 | 0.16022 | -122.3694 | -0.027466 | -0.091553 | -123.111 | -0.18311 | -0.004578 | 0.086975 | -123.175 | 1.0071 | 0.87891 | 0.88806 | -122.4838 | 0.13733 | 0.073242 | 0.027466 | -123.3398
1009.8438 | 123.2483 | -0.86975 | 122.3923 | 0.076074 | 0.17435 | 0.14399 | 0.097471 | 0.12094 | 0.031091 | 0.037698 | -0.28888 | 0.19341 | 0.0032311 | 0.17955 | 0.010744 | -0.041541 | 0.045776 | 0.036621 | -0.054932 | 0.022888 | 0.13733 | -0.004578 | -0.16022 | -0.78735 | -0.81482 | -0.89722 | -0.70953 | -0.75073 | -0.87433 | -0.9613 | 0.86517 | 0.70953 | -122.2549 | 0.90637 | 0.89264 | 0.1831 | -122.3465 | -0.004578 | -0.091553 | -123.1018 | 0.082397 | -0.027466 | 0.064087 | -123.143 | 1.0071 | 0.91553 | 0.81482 | -122.5525 | 0.16022 | 0.11902 | 0.054932 | -123.3536
1010.9062 | 123.3032 | -0.84228 | 122.3831 | 0.45754 | 0.15299 | 0.15146 | 0.0697 | 0.12414 | -0.019111 | 0.034494 | 0.35199 | 0.17953 | -0.010654 | 0.1881 | 0.011812 | -0.021247 | 0.018311 | 0.091553 | 0.009155 | 0.045776 | 0.1236 | 0.004578 | -0.10986 | -0.74616 | -0.7782 | -0.82398 | -0.72327 | -0.76446 | -0.85144 | -0.91553 | 0.84686 | 0.73242 | -122.2595 | 0.93384 | 0.88806 | 0.15564 | -122.3648 | -0.009155 | -0.073242 | -123.1064 | 0.09613 | 0.01831 | 0.091552 | -123.1476 | 0.96588 | 0.8606 | 0.85144 | -122.493 | 0.11902 | 0.07782 | 0.064087 | -123.2986
1011.8438 | 123.3353 | -0.80566 | 122.3831 | -0.13755 | 0.12522 | 0.13758 | 0.053678 | 0.11987 | -0.00095325 | 0.034494 | -0.3194 | 0.1838 | -0.0042459 | 0.18169 | 0.0043349 | -0.024451 | 0.068665 | 0.1236 | 0.050354 | 0.082397 | 0.091553 | 0.013733 | -0.11444 | -0.72327 | -0.67291 | -0.75531 | -0.71869 | -0.76446 | -0.8606 | -0.9201 | 0.8194 | 0.69122 | -122.2916 | 0.92926 | 0.88806 | 0.19684 | -122.3145 | -0.054932 | -0.11444 | -123.1018 | 0.082397 | 0.050354 | 0.16479 | -123.1476 | 0.89722 | 0.87433 | 0.85602 | -122.4976 | 0.086975 | 0.041199 | 0.13275 | -123.3032
1012.9062 | 123.2849 | -0.83771 | 122.374 | 0.25918 | 0.13163 | 0.14292 | 0.085722 | 0.096373 | 0.00011475 | 0.029153 | 0.58087 | 0.1838 | -0.025608 | 0.18703 | 0.010744 | -0.034064 | -0.018311 | 0.059509 | -0.004578 | -0.20142 | 0.11444 | -0.027466 | -0.17853 | -0.76446 | -0.77362 | -0.81482 | -0.75989 | -0.7782 | -0.86517 | -0.9201 | 0.81024 | 0.65918 | -122.2595 | 0.89722 | 0.63629 | -0.022888 | -122.3923 | -0.027465 | -0.082397 | -123.1339 | 0.073243 | 0.022889 | 0.10529 | -123.1522 | 0.95215 | 0.8194 | 0.83313 | -122.5525 | 0.07782 | 0.05951 | 0.064087 | -123.2941
1013.8438 | 123.3307 | -0.82855 | 122.3923 | -0.13755 | 0.13377 | 0.15146 | 0.073972 | 0.11133 | -0.0084293 | 0.022745 | -0.3194 | 0.17739 | -0.0042459 | 0.18276 | 0.010744 | -0.040473 | 0.09613 | 0.1236 | 0.050354 | 0.082397 | 0.10986 | 0.032043 | -0.10529 | -0.71411 | -0.68207 | -0.76446 | -0.70038 | -0.76904 | -0.84228 | -0.9201 | 0.86059 | 0.72327 | -122.2824 | 0.95215 | 0.91095 | 0.18768 | -122.2961 | -0.013733 | -0.091553 | -123.0927 | 0.11444 | 0.064087 | 0.15564 | -123.1613 | 0.93841 | 0.92468 | 0.87891 | -122.4976 | 0.12817 | 0.059509 | 0.14648 | -123.3124
1014.9062 | 123.3215 | -0.8194 | 122.406 | -0.4885 | 0.15406 | 0.14826 | 0.071836 | 0.11987 | -0.0052253 | 0.021677 | -0.3194 | 0.17846 | -0.0053139 | 0.17315 | 0.0064719 | -0.034064 | 0.10529 | 0.086975 | 0.059509 | 0.073242 | 0.10986 | 0.009155 | -0.1236 | -0.70953 | -0.67291 | -0.74616 | -0.71869 | -0.76446 | -0.83313 | -0.91095 | 0.82855 | 0.6958 | -122.2961 | 0.90637 | 0.89264 | 0.19684 | -122.3007 | -0.013733 | -0.091553 | -123.1247 | 0.10986 | 0.073242 | 0.1648 | -123.1705 | 0.92926 | 0.92468 | 0.87891 | -122.5296 | 0.10071 | 0.054932 | 0.14648 | -123.317
1015.8438 | 123.23 | -0.86517 | 122.4152 | -0.27488 | 0.14445 | 0.15146 | 0.0697 | 0.11346 | 0.0033197 | 0.032358 | -0.47198 | 0.1806 | 0.0032311 | 0.19024 | 0.015017 | -0.024451 | 0.050354 | 0.09613 | 0 | 0.041199 | 0.14191 | -0.009155 | -0.14191 | -0.77362 | -0.76446 | -0.83313 | -0.67749 | -0.71869 | -0.86975 | -0.93842 | 0.85602 | 0.72327 | -122.2733 | 0.9613 | 0.90637 | 0.18311 | -122.3648 | -0.004578 | -0.073243 | -123.0927 | 0.091552 | 0.032043 | 0.10529 | -123.1338 | 1.0071 | 0.91553 | 0.86517 | -122.5571 | 0.18768 | 0.14648 | 0.10071 | -123.3536
1016.9062 | 123.3307 | -0.82855 | 122.3831 | -0.80894 | 0.13697 | 0.14612 | 0.065427 | 0.099578 | 0.0054557 | 0.025949 | -0.2431 | 0.17526 | -0.0042459 | 0.18062 | 0.016085 | -0.02552 | 0.086975 | 0.12817 | 0.041199 | 0.073242 | 0.10529 | 0.018311 | -0.12817 | -0.68665 | -0.64545 | -0.75073 | -0.71869 | -0.76446 | -0.8194 | -0.9201 | 0.84686 | 0.70038 | -122.2778 | 0.95673 | 0.90179 | 0.20142 | -122.2961 | 0.009155 | -0.091553 | -123.1018 | 0.14191 | 0.07782 | 0.16937 | -123.1476 | 0.93384 | 0.91553 | 0.86975 | -122.5113 | 0.10986 | 0.064087 | 0.1831 | -123.3032
1017.8438 | 123.2529 | -0.79651 | 122.3831 | -0.24436 | 0.1359 | 0.14506 | 0.072904 | 0.12414 | -0.0073613 | 0.029153 | -0.3194 | 0.17739 | -0.018131 | 0.1678 | 0.020357 | -0.028724 | 0.073242 | 0.16479 | 0.064087 | 0.07782 | 0.12817 | 0.013733 | -0.11444 | -0.67291 | -0.65918 | -0.72784 | -0.70496 | -0.74616 | -0.84686 | -0.90179 | 0.81024 | 0.68207 | -122.2549 | 0.9613 | 0.87433 | 0.19226 | -122.3099 | -0.050354 | -0.10528 | -123.0881 | 0.1236 | 0.068665 | 0.17395 | -123.1293 | 0.92468 | 0.86975 | 0.8606 | -122.4976 | 0.091553 | 0.050354 | 0.13733 | -123.2849
1018.9062 | 123.3124 | -0.8194 | 122.4106 | 0.5491 | 0.16795 | 0.14185 | 0.079313 | 0.11346 | 0.031091 | 0.030222 | 0.1994 | 0.18914 | 0.0032311 | 0.18917 | 0.032106 | -0.035133 | 0.027466 | 0.059509 | -0.027466 | 0.022888 | 0.12817 | 0.018311 | -0.14648 | -0.70953 | -0.71869 | -0.78735 | -0.71411 | -0.77362 | -0.83771 | -0.91095 | 0.83771 | 0.67291 | -122.2824 | 0.87891 | 0.84229 | 0.16937 | -122.3831 | -0.018311 | -0.091553 | -123.1247 | 0.10986 | 0.032043 | 0.1236 | -123.1842 | 0.94757 | 0.84686 | 0.79193 | -122.5571 | 0.10529 | 0.045776 | 0.10071 | -123.3215
1019.8438 | 123.3307 | -0.81024 | 122.406 | -0.77842 | 0.14658 | 0.14292 | 0.068632 | 0.11667 | 0.0086597 | 0.03129 | -0.3194 | 0.18594 | -0.010654 | 0.18383 | 0.0011309 | -0.038337 | 0.073242 | 0.12817 | 0.054932 | 0.091553 | 0.082397 | 0.004578 | -0.10529 | -0.70038 | -0.64087 | -0.74158 | -0.71411 | -0.75073 | -0.83313 | -0.88806 | 0.81482 | 0.70496 | -122.3236 | 0.93842 | 0.9018 | 0.19684 | -122.3328 | -0.022888 | -0.07782 | -123.1201 | 0.10986 | 0.068665 | 0.14648 | -123.1567 | 0.89264 | 0.88348 | 0.86517 | -122.5113 | 0.096131 | 0.05951 | 0.16937 | -123.2941
1020.9062 | 123.2437 | -0.83313 | 122.3877 | 0.45754 | 0.15299 | 0.13651 | 0.087858 | 0.11133 | 0.030023 | 0.032358 | 0.077332 | 0.20089 | 2.7137e-05 | 0.19024 | 0.025698 | -0.023383 | -0.022888 | -0.022888 | -0.09613 | 0 | 0.16022 | -0.018311 | -0.16479 | -0.77362 | -0.81024 | -0.86975 | -0.66834 | -0.71411 | -0.85144 | -0.92926 | 0.81482 | 0.66834 | -122.2275 | 0.81024 | 0.83313 | 0.16479 | -122.4106 | -0.01831 | -0.09613 | -123.056 | 0.059509 | -0.036621 | 0.059509 | -123.1018 | 0.99335 | 0.81024 | 0.737 | -122.5525 | 0.1648 | 0.11902 | 0.022888 | -123.317
1021.8438 | 123.2986 | -0.80566 | 122.4014 | 0.38125 | 0.14765 | 0.13651 | 0.063291 | 0.10812 | -0.0073613 | 0.03663 | 0.077332 | 0.1838 | -0.0031779 | 0.20412 | 6.2882e-05 | -0.021247 | 0.027466 | 0.07782 | 0 | 0.036621 | 0.14648 | 0.036621 | -0.10071 | -0.70953 | -0.72784 | -0.7782 | -0.70038 | -0.76446 | -0.84228 | -0.90637 | 0.84229 | 0.70496 | -122.2549 | 0.88348 | 0.84229 | 0.13733 | -122.374 | -0.036621 | -0.10071 | -123.1018 | 0.09613 | 0.027466 | 0.12817 | -123.1659 | 0.95215 | 0.83313 | 0.80566 | -122.5021 | 0.10529 | 0.041199 | 0.07782 | -123.3078
1022.9062 | 123.2254 | -0.84686 | 122.4106 | -2.0449 | 0.16901 | 0.15467 | 0.073972 | 0.10278 | 0.030023 | 0.041971 | -0.029479 | 0.20089 | 0.017117 | 0.20626 | 0.011812 | -0.035133 | 0.013733 | -0.032043 | -0.09613 | -0.009155 | 0.17395 | -0.027466 | -0.13733 | -0.76904 | -0.82398 | -0.88348 | -0.67749 | -0.70496 | -0.85602 | -0.93384 | 0.8194 | 0.70953 | -122.2366 | 0.81482 | 0.83771 | 0.12817 | -122.3969 | -0.009155 | -0.086975 | -123.0881 | 0.07782 | -0.036621 | 0.050354 | -123.1155 | 1.0208 | 0.8606 | 0.75073 | -122.5479 | 0.16937 | 0.14191 | 0.022888 | -123.3444
1023.8438 | 123.3627 | -0.80566 | 122.3785 | -0.015478 | 0.12308 | 0.15574 | 0.056883 | 0.10919 | -0.011634 | 0.027017 | -0.075256 | 0.17846 | -0.026676 | 0.1881 | 0.01288 | -0.019111 | 0.07782 | 0.16479 | 0.054932 | 0.07782 | 0.13275 | 0.032043 | -0.10986 | -0.64087 | -0.60883 | -0.67749 | -0.69122 | -0.72784 | -0.81024 | -0.89264 | 0.83771 | 0.6958 | -122.2458 | 0.97046 | 0.88348 | 0.18768 | -122.3007 | -0.004578 | -0.086975 | -123.0698 | 0.1648 | 0.12817 | 0.21515 | -123.1064 | 0.93841 | 0.88348 | 0.8606 | -122.4884 | 0.11444 | 0.07782 | 0.19684 | -123.2712
1024.9062 | 123.2941 | -0.81482 | 122.406 | 0.45754 | 0.17329 | 0.13331 | 0.079313 | 0.11239 | 0.02041 | 0.038766 | 0.26044 | 0.19234 | -0.0063819 | 0.19344 | 0.017153 | -0.024451 | 0 | 0.004578 | -0.064087 | 0.009155 | 0.14191 | -0.009155 | -0.12817 | -0.71411 | -0.77362 | -0.80566 | -0.69122 | -0.71411 | -0.84228 | -0.91553 | 0.80566 | 0.68664 | -122.2641 | 0.8194 | 0.82397 | 0.13733 | -122.406 | -0.027466 | -0.10071 | -123.0972 | 0.10071 | 0.009155 | 0.10986 | -123.1201 | 0.95673 | 0.81482 | 0.75073 | -122.5342 | 0.1236 | 0.10071 | 0.041198 | -123.3215
1025.8438 | 123.2941 | -0.83771 | 122.3923 | 0.2134 | 0.14017 | 0.14933 | 0.067564 | 0.095305 | -0.015906 | 0.029153 | 0.092591 | 0.18594 | -0.021336 | 0.15071 | 6.2882e-05 | -0.015907 | 0.004578 | 0.068665 | -0.018311 | 0.036621 | 0.13275 | 0.004578 | -0.11902 | -0.75531 | -0.75073 | -0.77362 | -0.737 | -0.79651 | -0.88806 | -0.94757 | 0.84229 | 0.71869 | -122.2595 | 0.90637 | 0.87433 | 0.15564 | -122.3877 | -0.050354 | -0.10986 | -123.1293 | 0.082398 | 0.064087 | 0.17395 | -123.1888 | 0.97046 | 0.84229 | 0.8194 | -122.5113 | 0.10071 | 0.041199 | 0.086976 | -123.3398
1026.9062 | 123.1888 | -0.8194 | 122.4335 | 0.2897 | 0.18717 | 0.14185 | 0.085722 | 0.11239 | 0.026818 | 0.043039 | 0.21466 | 0.19341 | 0.017117 | 0.18703 | 0.026766 | -0.041541 | -0.009155 | -0.054932 | -0.086975 | -0.004578 | 0.12817 | -0.032043 | -0.16022 | -0.79651 | -0.82398 | -0.88348 | -0.65918 | -0.68665 | -0.85602 | -0.90637 | 0.78735 | 0.65918 | -122.3053 | 0.76447 | 0.81482 | 0.15564 | -122.4426 | -0.036621 | -0.086975 | -123.0927 | 0.022888 | -0.064087 | 0.022888 | -123.1201 | 0.94757 | 0.81024 | 0.73242 | -122.5937 | 0.16022 | 0.13275 | -0.004578 | -123.3398
1027.8438 | 123.2986 | -0.78735 | 122.4243 | 0.50332 | 0.1594 | 0.13651 | 0.079313 | 0.10492 | 0.026818 | 0.039835 | 0.26044 | 0.19234 | 0.0064351 | 0.18596 | 0.01288 | -0.027656 | -0.004578 | 0.013733 | -0.059509 | 0 | 0.13733 | -0.032043 | -0.15106 | -0.71411 | -0.74158 | -0.80566 | -0.66834 | -0.70953 | -0.83771 | -0.89264 | 0.75531 | 0.63629 | -122.287 | 0.80109 | 0.78735 | 0.15106 | -122.4289 | -0.050354 | -0.10528 | -123.0927 | 0.073243 | -0.01831 | 0.086975 | -123.1339 | 0.92468 | 0.78278 | 0.72784 | -122.5754 | 0.11902 | 0.07782 | 0.045777 | -123.317
1028.9062 | 123.2346 | -0.82398 | 122.4426 | 0.10659 | 0.15833 | 0.13972 | 0.081449 | 0.12308 | 0.024682 | 0.034494 | -0.075256 | 0.20623 | 2.7137e-05 | 0.1881 | 0.022493 | -0.027656 | 0.027466 | 0.027466 | -0.050354 | 0.013733 | 0.13275 | -0.009155 | -0.16479 | -0.74158 | -0.75073 | -0.83771 | -0.67291 | -0.70953 | -0.8194 | -0.91095 | 0.81482 | 0.65918 | -122.3099 | 0.85144 | 0.83771 | 0.17853 | -122.4152 | 0.004578 | -0.086975 | -123.1155 | 0.082398 | -0.013733 | 0.073242 | -123.1522 | 0.95673 | 0.85144 | 0.77362 | -122.6074 | 0.15106 | 0.11444 | 0.073243 | -123.3536
1029.8438 | 123.2941 | -0.76446 | 122.4518 | 0.44228 | 0.16047 | 0.15146 | 0.056883 | 0.11239 | -0.011634 | 0.029153 | 0.41303 | 0.1806 | 0.0021631 | 0.18489 | 0.017153 | -0.016975 | 0.050354 | 0.09613 | 0.022888 | 0.054932 | 0.11902 | 0.018311 | -0.11444 | -0.68665 | -0.67749 | -0.73242 | -0.66376 | -0.70953 | -0.79651 | -0.86517 | 0.78278 | 0.65002 | -122.3328 | 0.86059 | 0.8194 | 0.16937 | -122.4014 | -0.032044 | -0.10071 | -123.1155 | 0.077819 | 0.032043 | 0.13275 | -123.1613 | 0.88348 | 0.81482 | 0.78735 | -122.5662 | 0.10071 | 0.054931 | 0.086975 | -123.317
1030.9062 | 123.2758 | -0.79193 | 122.4243 | 0.4728 | 0.1797 | 0.12797 | 0.0697 | 0.11026 | 0.019342 | 0.041971 | 0.29095 | 0.19021 | 0.0032311 | 0.19237 | 0.0075399 | -0.034064 | -0.004578 | -0.009155 | -0.068665 | -0.009155 | 0.14648 | -0.032043 | -0.14191 | -0.71869 | -0.75989 | -0.80109 | -0.64087 | -0.68665 | -0.82398 | -0.88348 | 0.75989 | 0.65002 | -122.2778 | 0.78278 | 0.78278 | 0.13275 | -122.4289 | -0.032044 | -0.091553 | -123.0652 | 0.073242 | -0.009155 | 0.082398 | -123.111 | 0.93841 | 0.78735 | 0.72327 | -122.5662 | 0.15106 | 0.10529 | 0.032043 | -123.3078
1031.8438 | 123.3032 | -0.84686 | 122.406 | 0.19814 | 0.1359 | 0.1536 | 0.041929 | 0.11346 | -0.020179 | 0.01954 | 0.18414 | 0.18807 | 0.0021631 | 0.17742 | 6.2882e-05 | -0.018043 | 0.013733 | 0.050354 | 0.004578 | 0.036621 | 0.10529 | 0.013733 | -0.13733 | -0.70496 | -0.70496 | -0.94299 | -0.67291 | -0.72327 | -0.83771 | -0.92468 | 0.8606 | 0.70953 | -122.3007 | 0.89722 | 0.88348 | 0.17395 | -122.3923 | 0.009155 | -0.07782 | -123.0789 | 0.14191 | -0.09613 | -0.01831 | -123.1293 | 0.95215 | 0.8606 | 0.85144 | -122.5433 | 0.17395 | 0.1236 | 0.14191 | -123.3307
1032.9062 | 123.2666 | -0.79193 | 122.4472 | -0.16807 | 0.16901 | 0.13331 | 0.0697 | 0.11239 | 0.028955 | 0.03663 | -0.41095 | 0.20089 | 0.0053671 | 0.17315 | 0.025698 | -0.035133 | 0.032043 | 0.009155 | -0.059509 | 0.045776 | 0.14191 | -0.009155 | -0.17395 | -0.72327 | -0.6958 | -0.78735 | -0.62714 | -0.68207 | -0.81024 | -0.90179 | 0.78278 | 0.61798 | -122.3053 | 0.80109 | 0.83771 | 0.21973 | -122.4152 | -0.018311 | -0.10986 | -123.0743 | 0.068664 | 0.004577 | 0.11444 | -123.1293 | 0.93384 | 0.82397 | 0.73242 | -122.6212 | 0.1648 | 0.10986 | 0.09613 | -123.349
1033.8438 | 123.3032 | -0.75989 | 122.4426 | 0.44228 | 0.15726 | 0.14506 | 0.066496 | 0.092101 | 0.010797 | 0.037698 | 0.32147 | 0.18273 | -0.0031779 | 0.18276 | 0.022493 | -0.01377 | 0.009155 | 0.004578 | -0.050354 | 0.004578 | 0.1236 | -0.004578 | -0.16479 | -0.68207 | -0.70038 | -0.75073 | -0.6546 | -0.70496 | -0.78735 | -0.86517 | 0.75531 | 0.59509 | -122.319 | 0.76447 | 0.76447 | 0.16937 | -122.4335 | -0.027466 | -0.10528 | -123.0972 | 0.07782 | 0.009156 | 0.11444 | -123.1476 | 0.88348 | 0.76904 | 0.70953 | -122.6074 | 0.10529 | 0.054932 | 0.05951 | -123.3078
1034.9062 | 123.317 | -0.77362 | 122.4564 | 0.5491 | 0.14872 | 0.13544 | 0.063291 | 0.11987 | 0.012933 | 0.030222 | 0.2757 | 0.19555 | -0.0042459 | 0.16674 | 0.01288 | -0.018043 | 0.013733 | 0.009155 | -0.041199 | -0.004578 | 0.12817 | -0.018311 | -0.13275 | -0.68207 | -0.70953 | -0.74158 | -0.6546 | -0.70496 | -0.81024 | -0.85144 | 0.75531 | 0.64087 | -122.3282 | 0.78278 | 0.76904 | 0.12817 | -122.4426 | -0.036621 | -0.077819 | -123.111 | 0.091553 | 0.032044 | 0.10986 | -123.1613 | 0.9018 | 0.78735 | 0.73242 | -122.5891 | 0.11902 | 0.068665 | 0.064087 | -123.3078
1035.8438 | 123.262 | -0.78278 | 122.493 | 0.33547 | 0.16795 | 0.14185 | 0.080381 | 0.11667 | 0.0065237 | 0.032358 | 0.21466 | 0.19662 | -0.0031779 | 0.1881 | 0.020357 | -0.018043 | 0.009155 | -0.041199 | -0.086975 | -0.013733 | 0.15106 | -0.027466 | -0.16479 | -0.70496 | -0.75989 | -0.81024 | -0.63171 | -0.67291 | -0.82398 | -0.87891 | 0.75531 | 0.61798 | -122.3419 | 0.74158 | 0.76904 | 0.15106 | -122.4838 | -0.041199 | -0.09613 | -123.1247 | 0.07782 | -0.027466 | 0.068664 | -123.1659 | 0.93384 | 0.79193 | 0.6958 | -122.6578 | 0.15106 | 0.10986 | 0.022888 | -123.3719
1036.8438 | 123.3353 | -0.79651 | 122.4472 | 0.53384 | 0.15833 | 0.14292 | 0.062223 | 0.11667 | -0.0062933 | 0.023813 | 0.42828 | 0.19234 | -0.012791 | 0.18276 | 0.018221 | -0.023383 | 0.091553 | 0.091553 | 0.045776 | 0.082397 | 0.09613 | 0.027466 | -0.11902 | -0.64087 | -0.737 | -0.95673 | -0.70038 | -0.73242 | -0.83313 | -0.89722 | 0.82398 | 0.67749 | -122.3511 | 0.88806 | 0.87891 | 0.20142 | -122.3557 | -0.036621 | -0.10071 | -123.1476 | 0.15564 | -0.16022 | -0.059509 | -123.1796 | 0.89264 | 0.88806 | 0.84229 | -122.5662 | 0.096131 | 0.064087 | 0.059509 | -123.3444
1037.9062 | 123.2666 | -0.78735 | 122.4701 | -0.18333 | 0.16047 | 0.14399 | 0.078245 | 0.11133 | 0.017205 | 0.027017 | -0.21259 | 0.18594 | 0.0053671 | 0.18917 | 0.017153 | -0.036201 | 0.041199 | 0.050354 | -0.022888 | 0.041199 | 0.12817 | -0.018311 | -0.16479 | -0.70038 | -0.69122 | -0.75989 | -0.63171 | -0.66376 | -0.79651 | -0.87433 | 0.76904 | 0.62256 | -122.3419 | 0.83771 | 0.82855 | 0.20599 | -122.4289 | -0.009155 | -0.086975 | -123.1018 | 0.086976 | 0.027466 | 0.11444 | -123.1339 | 0.91553 | 0.82855 | 0.76447 | -122.6349 | 0.15564 | 0.1236 | 0.096131 | -123.3444
1038.8594 | 123.2712 | -0.79651 | 122.4701 | -0.21384 | 0.15513 | 0.14185 | 0.073972 | 0.12201 | 0.015069 | 0.038766 | -0.41095 | 0.18807 | 0.0010951 | 0.19237 | 0.017153 | -0.031928 | -0.009155 | -0.022888 | -0.082397 | 0.009155 | 0.15106 | -0.045776 | -0.16937 | -0.76904 | -0.71869 | -0.79193 | -0.61798 | -0.66834 | -0.80566 | -0.89264 | 0.75073 | 0.62714 | -122.319 | 0.77362 | 0.80566 | 0.17853 | -122.4792 | -0.009155 | -0.09613 | -123.0881 | 0.027466 | 0.004578 | 0.10071 | -123.1384 | 0.94757 | 0.78735 | 0.71411 | -122.6395 | 0.17853 | 0.12817 | 0.07782 | -123.3627
1039.9062 | 123.2254 | -0.81024 | 122.4609 | 0.045557 | 0.18931 | 0.14506 | 0.079313 | 0.11346 | 0.014001 | 0.027017 | -0.10577 | 0.19341 | 0.017117 | 0.18489 | 0.021425 | -0.026588 | 0.004578 | 0.013733 | -0.064087 | 0.004578 | 0.13275 | -0.036621 | -0.16479 | -0.737 | -0.72784 | -0.79651 | -0.62714 | -0.66834 | -0.81024 | -0.89264 | 0.77362 | 0.64545 | -122.3282 | 0.82398 | 0.81482 | 0.16937 | -122.4564 | 0 | -0.082397 | -123.0881 | 0.073242 | 0.013733 | 0.09613 | -123.1293 | 0.94299 | 0.81482 | 0.74616 | -122.6257 | 0.18311 | 0.14191 | 0.082398 | -123.3536
1040.8438 | 123.2712 | -0.78735 | 122.4792 | 0.45754 | 0.1562 | 0.14399 | 0.078245 | 0.1156 | 0.0086597 | 0.029153 | 0.24518 | 0.187 | 0.019253 | 0.17742 | 0.0096759 | -0.021247 | -0.022888 | -0.036621 | -0.10071 | -0.013733 | 0.15564 | -0.013733 | -0.15106 | -0.71869 | -0.737 | -0.80566 | -0.62714 | -0.67291 | -0.81024 | -0.8606 | 0.77362 | 0.63629 | -122.3236 | 0.75073 | 0.77362 | 0.13733 | -122.5021 | -0.022888 | -0.073242 | -123.1064 | 0.068665 | -0.01831 | 0.054932 | -123.1522 | 0.94299 | 0.76447 | 0.68665 | -122.6303 | 0.16022 | 0.11444 | 0.050354 | -123.3398
1041.9062 | 123.2162 | -0.78735 | 122.5021 | -0.33591 | 0.14765 | 0.16001 | 0.060087 | 0.10385 | -0.016974 | 0.024881 | -0.42621 | 0.19021 | -0.0010409 | 0.1913 | 0.0032669 | -0.016975 | -0.027466 | 0.009155 | -0.064087 | 0.004578 | 0.13733 | -0.013733 | -0.16479 | -0.74616 | -0.70038 | -0.7782 | -0.60425 | -0.64545 | -0.8194 | -0.87433 | 0.77362 | 0.62256 | -122.3648 | 0.79651 | 0.79193 | 0.16937 | -122.5296 | -0.032043 | -0.086975 | -123.1064 | 0.041199 | 0.009156 | 0.096131 | -123.1476 | 0.92468 | 0.75989 | 0.72327 | -122.6669 | 0.18311 | 0.14191 | 0.086976 | -123.3765
1042.8438 | 123.2758 | -0.7782 | 122.3694 | 0.44228 | 0.16581 | 0.15467 | 0.071836 | 0.11133 | 0.0075917 | 0.037698 | 0.35199 | 0.1838 | -0.0021099 | 0.18703 | 0.015017 | -0.021247 | 0.050354 | 0.09613 | 0.032043 | 0.07782 | 0.12817 | 0.022888 | -0.10529 | -0.62714 | -0.62256 | -0.66834 | -0.65918 | -0.69122 | -0.76904 | -0.84228 | 0.80109 | 0.67291 | -122.2412 | 0.87433 | 0.85602 | 0.18311 | -122.319 | 0.009155 | -0.064087 | -123.0286 | 0.15106 | 0.10986 | 0.17395 | -123.0606 | 0.90637 | 0.82855 | 0.81024 | -122.4747 | 0.11902 | 0.086975 | 0.15564 | -123.2117
1043.9062 | 123.3536 | -0.76446 | 122.4518 | 0.57961 | 0.14552 | 0.15146 | 0.067564 | 0.095305 | 0.0086597 | 0.038766 | 0.39777 | 0.17953 | 0.0064351 | 0.18276 | 0.020357 | -0.012702 | 0.082397 | 0.10071 | 0.027466 | 0.073242 | 0.10529 | 0.032043 | -0.10529 | -0.79651 | -0.80109 | -0.62256 | -0.69122 | -0.737 | -0.80566 | -0.87433 | 0.79651 | 0.65918 | -122.3465 | 0.86517 | 0.83771 | 0.17853 | -122.3694 | -0.041199 | -0.10986 | -123.143 | -0.032044 | 0.14191 | 0.25177 | -123.1888 | 0.86975 | 0.84686 | 0.79193 | -122.5571 | 0.073242 | 0.027465 | -0.036621 | -123.3261
1044.8438 | 123.3078 | -0.74158 | 122.493 | 0.44228 | 0.13911 | 0.14612 | 0.068632 | 0.11026 | -0.014838 | 0.023813 | 0.38251 | 0.1806 | -0.012791 | 0.18383 | 0.0011309 | -0.0084301 | 0.07782 | 0.091553 | 0.022888 | 0.059509 | 0.1236 | 0.036621 | -0.10071 | -0.64087 | -0.65918 | -0.69122 | -0.62714 | -0.67291 | -0.75073 | -0.82855 | 0.7782 | 0.64087 | -122.3694 | 0.83313 | 0.80109 | 0.16022 | -122.4152 | -0.009155 | -0.086975 | -123.1201 | 0.10071 | 0.050354 | 0.13733 | -123.1659 | 0.86517 | 0.8194 | 0.76447 | -122.5937 | 0.11444 | 0.068664 | 0.082397 | -123.3215
1045.9062 | 123.2666 | -0.79193 | 122.493 | -0.18333 | 0.16901 | 0.14826 | 0.079313 | 0.11239 | 0.018273 | 0.023813 | -0.44147 | 0.19128 | -0.0074499 | 0.18703 | 0.01288 | -0.039405 | -0.004578 | -0.032043 | -0.086975 | 0.004578 | 0.14191 | -0.013733 | -0.15564 | -0.74158 | -0.70496 | -0.79651 | -0.60425 | -0.64087 | -0.81024 | -0.87891 | 0.7782 | 0.63629 | -122.3511 | 0.75989 | 0.79651 | 0.16022 | -122.4976 | -0.018311 | -0.086975 | -123.0972 | 0.050354 | -0.004578 | 0.082397 | -123.1338 | 0.93384 | 0.78735 | 0.70496 | -122.6486 | 0.18768 | 0.15106 | 0.086975 | -123.3719
1046.8438 | 123.3444 | -0.71411 | 122.5021 | 0.51858 | 0.16795 | 0.13331 | 0.076109 | 0.10812 | 0.011865 | 0.039835 | 0.35199 | 0.18487 | -0.0031779 | 0.1881 | 0.016085 | -0.027656 | 0.036621 | 0.064087 | 0 | 0.054932 | 0.10986 | 0.004578 | -0.13733 | -0.63171 | -0.65002 | -0.6958 | -0.64545 | -0.66376 | -0.75073 | -0.8194 | 0.71869 | 0.57678 | -122.3923 | 0.7782 | 0.76904 | 0.19226 | -122.4655 | -0.036621 | -0.10529 | -123.1476 | 0.082397 | 0.01831 | 0.1236 | -123.1659 | 0.82397 | 0.75073 | 0.71411 | -122.6395 | 0.068664 | 0.050354 | 0.064087 | -123.3215
1047.9062 | 123.2895 | -0.74158 | 122.5067 | -0.030737 | 0.1594 | 0.13758 | 0.064359 | 0.10385 | 0.02575 | 0.035562 | -0.54828 | 0.1838 | 0.019253 | 0.19451 | 0.013948 | -0.031928 | 0.068665 | 0.041199 | -0.032043 | 0.032043 | 0.14648 | -0.018311 | -0.17395 | -0.67291 | -0.63629 | -0.74158 | -0.53558 | -0.59967 | -0.74616 | -0.81024 | 0.72327 | 0.56763 | -122.3602 | 0.78278 | 0.77362 | 0.20599 | -122.438 | -0.004578 | -0.068665 | -123.0423 | 0.068664 | 0 | 0.068665 | -123.1064 | 0.88806 | 0.81024 | 0.70953 | -122.6807 | 0.20599 | 0.14191 | 0.10529 | -123.317
1048.8594 | 123.2025 | -0.73242 | 122.5754 | -0.15281 | 0.15833 | 0.16001 | 0.067564 | 0.10919 | -0.0030893 | 0.030222 | -0.41095 | 0.18594 | -0.0010409 | 0.17955 | 6.2882e-05 | -0.021247 | -0.022888 | 0 | -0.07782 | -0.013733 | 0.15564 | -0.032043 | -0.16937 | -0.73242 | -0.70496 | -0.78278 | -0.58136 | -0.61798 | -0.78735 | -0.84686 | 0.70038 | 0.56305 | -122.4197 | 0.73242 | 0.71869 | 0.15564 | -122.5983 | -0.054932 | -0.11444 | -123.1567 | 0 | -0.050354 | 0.064087 | -123.1934 | 0.88806 | 0.70953 | 0.6546 | -122.7448 | 0.15106 | 0.11444 | 0.027466 | -123.4222
1049.9062 | 123.3307 | -0.70953 | 122.4976 | 0.57961 | 0.16474 | 0.13758 | 0.071836 | 0.11133 | -0.0020213 | 0.040903 | 0.35199 | 0.1838 | 2.7137e-05 | 0.17635 | 0.010744 | -0.024451 | -0.15106 | -0.082397 | 0.032043 | 0.10071 | 0.073242 | -0.022888 | -0.14191 | -0.59052 | -0.62714 | -0.66834 | -0.65002 | -0.68665 | -0.75989 | -0.80566 | 0.68665 | 0.56763 | -122.4243 | 0.62714 | 0.81024 | 0.24262 | -122.6486 | -0.050354 | -0.09613 | -123.1476 | 0.11902 | 0.041199 | 0.13733 | -123.1842 | 0.78278 | 0.55847 | 0.74158 | -122.6395 | 0.05951 | 0.022888 | 0.082398 | -123.3032
1050.8438 | 123.3261 | -0.72784 | 122.4701 | 0.5491 | 0.17008 | 0.14612 | 0.076109 | 0.11133 | 0.010797 | 0.022745 | 0.36725 | 0.19448 | 0.0085721 | 0.17421 | 0.0096759 | -0.02552 | 0.022888 | 0.004578 | -0.032043 | 0.027466 | 0.13275 | 0.009155 | -0.13275 | -0.64087 | -0.66834 | -0.70953 | -0.60883 | -0.6546 | -0.76446 | -0.82398 | 0.737 | 0.59509 | -122.3373 | 0.73242 | 0.75531 | 0.16022 | -122.4472 | -0.036621 | -0.096131 | -123.0789 | 0.086975 | 0.01831 | 0.11444 | -123.1247 | 0.86059 | 0.75073 | 0.6958 | -122.6028 | 0.11902 | 0.073242 | 0.059509 | -123.2941
1051.9062 | 123.2849 | -0.78278 | 122.5067 | -0.18333 | 0.17542 | 0.13224 | 0.089994 | 0.10385 | 0.0086597 | 0.03129 | -0.44147 | 0.19341 | -0.0053139 | 0.17421 | 0.015017 | -0.029792 | 0.004578 | -0.009155 | -0.10071 | 0.013733 | 0.14648 | -0.032043 | -0.16937 | -0.70496 | -0.69122 | -0.76446 | -0.58136 | -0.62714 | -0.80109 | -0.8606 | 0.75073 | 0.6134 | -122.3602 | 0.77362 | 0.79651 | 0.18311 | -122.5021 | -0.01831 | -0.07782 | -123.0881 | 0.07782 | 0.018311 | 0.096131 | -123.1338 | 0.92926 | 0.78735 | 0.68207 | -122.6761 | 0.20142 | 0.15564 | 0.091553 | -123.3673
1052.8438 | 123.3078 | -0.74158 | 122.4838 | 0.45754 | 0.16581 | 0.13972 | 0.07504 | 0.10278 | 0.011865 | 0.038766 | 0.24518 | 0.19234 | -0.010654 | 0.19344 | 0.020357 | -0.035133 | -0.018311 | -0.018311 | -0.073242 | 0 | 0.14648 | -0.009155 | -0.14648 | -0.6546 | -0.69122 | -0.737 | -0.59509 | -0.65918 | -0.77362 | -0.83313 | 0.73242 | 0.59509 | -122.3373 | 0.72327 | 0.74158 | 0.14648 | -122.5021 | -0.032044 | -0.091553 | -123.0789 | 0.086975 | 0.004577 | 0.09613 | -123.143 | 0.88806 | 0.72327 | 0.66834 | -122.6303 | 0.14648 | 0.082397 | 0.050354 | -123.317
1053.9219 | 123.3398 | -0.70496 | 122.5021 | 0.091333 | 0.13377 | -0.092066 | 0.056883 | 0.11667 | -0.016974 | 0.030222 | 0.15363 | 0.187 | 2.7137e-05 | 0.17315 | 0.0086079 | -0.028724 | 0.009155 | 0.054932 | 0.004578 | 0.054932 | 0.13275 | 0.018311 | -0.10529 | -0.62714 | -0.61798 | -0.65918 | -0.58594 | -0.64545 | -0.74158 | -0.81024 | 0.72327 | 0.59967 | -122.3694 | 0.75989 | 0.75989 | 0.16022 | -122.493 | -0.036621 | -0.10529 | -123.0881 | 0.07782 | 0.045776 | 0.15106 | -123.1476 | 0.83771 | 0.71411 | 0.70953 | -122.6074 | 0.11902 | 0.059509 | 0.086975 | -123.3124
1054.8438 | 123.3353 | -0.70038 | 122.5067 | 0.45754 | 0.14231 | 0.14933 | 0.072904 | 0.11239 | -0.014838 | 0.027017 | 0.42828 | 0.18487 | 0.0053671 | 0.17315 | 0.011812 | -0.018043 | 0.073242 | 0.11902 | 0.041199 | 0.064087 | 0.13275 | 0.027466 | -0.10071 | -0.59967 | -0.62256 | -0.64545 | -0.60883 | -0.6546 | -0.72784 | -0.81482 | 0.72784 | 0.59967 | -122.374 | 0.8194 | 0.76446 | 0.1648 | -122.4335 | -0.027466 | -0.11444 | -123.1155 | 0.10071 | 0.054931 | 0.16937 | -123.1613 | 0.83313 | 0.77362 | 0.74158 | -122.6074 | 0.091552 | 0.045776 | 0.077819 | -123.3215
1055.8438 | 123.3353 | -0.72784 | 122.4976 | 0.42703 | 0.14445 | 0.14185 | 0.054746 | 0.11667 | -0.0094983 | 0.021677 | 0.24518 | 0.18166 | -0.0063819 | 0.18917 | 0.016085 | -0.023383 | 0.050354 | 0.073242 | 0.018311 | 0.041199 | 0.12817 | 0.018311 | -0.10529 | -0.63629 | -0.65002 | -0.68207 | -0.59967 | -0.62256 | -0.737 | -0.80566 | 0.74616 | 0.62256 | -122.3694 | 0.80109 | 0.76904 | 0.14649 | -122.4472 | -0.009156 | -0.07782 | -123.0972 | 0.091552 | 0.045776 | 0.1236 | -123.1201 | 0.85602 | 0.7782 | 0.74616 | -122.6028 | 0.12817 | 0.10529 | 0.07782 | -123.3032
1056.9062 | 123.2437 | -0.76904 | 122.5296 | 0.22866 | 0.18076 | 0.13224 | 0.09213 | 0.099578 | 0.031091 | 0.039835 | -0.18207 | 0.19448 | 0.0042991 | 0.15499 | 0.023561 | -0.037269 | 0.022888 | -0.018311 | -0.073242 | -0.018311 | 0.14648 | -0.022888 | -0.17395 | -0.70496 | -0.72784 | -0.80566 | -0.58594 | -0.62256 | -0.77362 | -0.85602 | 0.74616 | 0.59509 | -122.3831 | 0.75073 | 0.75073 | 0.15564 | -122.5067 | -0.004578 | -0.086975 | -123.1155 | 0.064087 | -0.036621 | 0.050354 | -123.1522 | 0.91553 | 0.79193 | 0.6958 | -122.7036 | 0.18311 | 0.14648 | 0.041199 | -123.3856
1057.8438 | 123.349 | -0.70038 | 122.5204 | 0.51858 | 0.16901 | 0.14185 | 0.065427 | 0.10919 | 0.0075917 | 0.033426 | 0.22992 | 0.1838 | -0.0021099 | 0.17955 | 0.025698 | -0.027656 | 0.07782 | 0.07782 | 0.027466 | 0.07782 | 0.11902 | 0.013733 | -0.10986 | -0.58594 | -0.59967 | -0.66376 | -0.61798 | -0.66834 | -0.71869 | -0.79193 | 0.71411 | 0.59051 | -122.4014 | 0.7782 | 0.7782 | 0.18768 | -122.4426 | -0.018311 | -0.091553 | -123.1384 | 0.11444 | 0.036621 | 0.12817 | -123.1888 | 0.8194 | 0.7782 | 0.72784 | -122.6303 | 0.082397 | 0.032043 | 0.10071 | -123.3124
1058.9062 | 123.3765 | -0.70038 | 122.5204 | 0.56436 | 0.16688 | 0.14826 | 0.077177 | 0.10919 | 0.00011475 | 0.030222 | 0.35199 | 0.1838 | -0.0053139 | 0.17208 | 0.021425 | -0.038337 | 0.086975 | 0.068665 | 0.032043 | 0.073242 | 0.11902 | 0.018311 | -0.12817 | -0.55847 | -0.59052 | -0.64087 | -0.62714 | -0.65002 | -0.72327 | -0.79651 | 0.71869 | 0.5722 | -122.4014 | 0.76904 | 0.77362 | 0.20142 | -122.4335 | -0.022889 | -0.096131 | -123.1476 | 0.14191 | 0.059509 | 0.15564 | -123.1705 | 0.8194 | 0.78735 | 0.73242 | -122.6486 | 0.073242 | 0.050354 | 0.10986 | -123.317
1059.8438 | 123.3215 | -0.71869 | 122.5433 | 0.30496 | 0.13056 | 0.16428 | 0.051542 | 0.10812 | -0.018043 | 0.025949 | 1.176 | 0.1838 | -0.0095859 | 0.17528 | 0.0054039 | -0.020179 | 0.018311 | 0.041199 | -0.018311 | 0.036621 | 0.11444 | 0 | -0.14191 | -0.66834 | -0.63629 | -0.67749 | -0.62714 | -0.68665 | -0.75073 | -0.83313 | 0.71869 | 0.57678 | -122.4289 | 0.75989 | 0.75531 | 0.17853 | -122.525 | -0.032043 | -0.11444 | -123.1705 | 0.050354 | 0.041199 | 0.15564 | -123.23 | 0.83313 | 0.737 | 0.70038 | -122.6852 | 0.091553 | 0.032043 | 0.082397 | -123.3765
1060.9062 | 123.2986 | -0.737 | 122.5342 | 0.015039 | 0.17542 | 0.14719 | 0.082517 | 0.12308 | 0.02041 | 0.030222 | -0.27362 | 0.19555 | -0.0074499 | 0.18169 | 0.026766 | -0.041541 | 0.045776 | 0.036621 | -0.027466 | 0.032043 | 0.13733 | -0.027466 | -0.15106 | -0.62714 | -0.64545 | -0.71411 | -0.56763 | -0.60425 | -0.75531 | -0.81024 | 0.70953 | 0.58594 | -122.3969 | 0.77362 | 0.76904 | 0.18311 | -122.4884 | -0.01831 | -0.073242 | -123.1018 | 0.10986 | 0.022889 | 0.096131 | -123.1384 | 0.87433 | 0.78278 | 0.70953 | -122.6852 | 0.16937 | 0.13275 | 0.091553 | -123.3444
1061.8438 | 123.2483 | -0.72327 | 122.5433 | 0.44228 | 0.17115 | 0.14078 | 0.060087 | 0.10171 | 0.018273 | 0.028085 | 0.15363 | 0.19341 | 0.017117 | 0.17849 | 0.011812 | -0.026588 | -0.018311 | -0.054932 | -0.10071 | 0 | 0.13275 | -0.018311 | -0.15106 | -0.64087 | -0.85602 | -0.77362 | -0.55389 | -0.60425 | -0.73242 | -0.79193 | 0.70496 | 0.5722 | -122.4106 | 0.66834 | 0.72327 | 0.15106 | -122.5616 | -0.009155 | -0.068664 | -123.0972 | 0.082398 | -0.050354 | 0.01831 | -123.1476 | 0.85602 | 0.70496 | 0.62256 | -122.6944 | 0.16937 | 0.11902 | -0.13275 | -123.3353
1062.9062 | 123.2437 | -0.75073 | 122.5571 | 0.19814 | 0.19038 | 0.14719 | 0.08679 | 0.11346 | 0.015069 | 0.030222 | -0.059997 | 0.19021 | 0.0085721 | 0.19451 | 0.015017 | -0.032996 | 0.036621 | 0.041199 | -0.036621 | 0.018311 | 0.13733 | -0.004578 | -0.14648 | -0.66834 | -0.65918 | -0.737 | -0.56305 | -0.6134 | -0.76446 | -0.81482 | 0.74615 | 0.60425 | -122.4197 | 0.79193 | 0.76904 | 0.16479 | -122.5204 | -0.013733 | -0.064087 | -123.1201 | 0.082397 | 0.013732 | 0.077819 | -123.1705 | 0.88806 | 0.78735 | 0.71411 | -122.7036 | 0.18768 | 0.13733 | 0.091552 | -123.3719
1063.8438 | 123.3353 | -0.70496 | 122.5159 | 0.48806 | 0.15406 | 0.13865 | 0.063291 | 0.10919 | 0.0043877 | 0.033426 | 0.35199 | 0.18807 | 0.0075041 | 0.19344 | 0.015017 | -0.021247 | 0.022888 | 0.022888 | -0.036621 | 0.018311 | 0.14191 | -0.018311 | -0.15106 | -0.60883 | -0.61798 | -0.66834 | -0.59967 | -0.62256 | -0.71411 | -0.78735 | 0.68665 | 0.55389 | -122.374 | 0.72784 | 0.72327 | 0.16937 | -122.493 | -0.009155 | -0.082398 | -123.1155 | 0.09613 | 0.036621 | 0.11902 | -123.1384 | 0.84686 | 0.72784 | 0.66834 | -122.6669 | 0.10529 | 0.082397 | 0.086975 | -123.3032
1064.8438 | 123.3536 | -0.70496 | 122.5204 | 0.4728 | 0.17329 | 0.14506 | 0.056883 | 0.099578 | -0.0084293 | 0.029153 | 0.44354 | 0.17632 | -0.0042459 | 0.1881 | 0.016085 | -0.023383 | 0.059509 | 0.11444 | 0.050354 | 0.054932 | 0.10529 | 0.027466 | -0.1236 | -0.5722 | -0.5722 | -0.63171 | -0.59509 | -0.65002 | -0.737 | -0.7782 | 0.73242 | 0.58136 | -122.4152 | 0.8194 | 0.75989 | 0.17853 | -122.4609 | -0.032044 | -0.073242 | -123.1155 | 0.13275 | 0.073242 | 0.14648 | -123.1705 | 0.81024 | 0.76447 | 0.75531 | -122.644 | 0.10986 | 0.054932 | 0.13275 | -123.2986
1065.9062 | 123.2391 | -0.737 | 122.525 | 0.16763 | 0.18504 | 0.13651 | 0.080381 | 0.097441 | 0.033227 | 0.040903 | -0.059997 | 0.19234 | 0.019253 | 0.1913 | 0.023561 | -0.037269 | 0.041199 | 0.009155 | -0.050354 | 0.009155 | 0.14191 | -0.009155 | -0.15106 | -0.67291 | -0.68207 | -0.76904 | -0.56305 | -0.61798 | -0.74158 | -0.82398 | 0.72784 | 0.58594 | -122.3831 | 0.74616 | 0.74616 | 0.16022 | -122.4838 | -0.004577 | -0.086975 | -123.0881 | 0.064087 | -0.032043 | 0.054932 | -123.143 | 0.87891 | 0.7782 | 0.68665 | -122.6761 | 0.17395 | 0.11902 | 0.054932 | -123.349
1066.8438 | 123.2346 | -0.73242 | 122.5388 | 0.44228 | 0.19038 | 0.13437 | 0.072904 | 0.1188 | 0.023614 | 0.037698 | 0.16888 | 0.19555 | 0.018185 | 0.19558 | 0.0075399 | -0.024451 | -0.045776 | -0.068665 | -0.11444 | -0.027466 | 0.12817 | 0 | -0.15106 | -0.70038 | -0.70953 | -0.76904 | -0.55847 | -0.59509 | -0.737 | -0.81482 | 0.73242 | 0.58136 | -122.4106 | 0.66376 | 0.70496 | 0.1236 | -122.5845 | -0.004578 | -0.082397 | -123.0972 | 0.032044 | -0.036621 | 0.045776 | -123.1339 | 0.8606 | 0.68665 | 0.61798 | -122.6898 | 0.17395 | 0.13733 | 0.022888 | -123.3536
1067.9062 | 123.2666 | -0.71411 | 122.5479 | 0.076074 | 0.1829 | 0.13331 | 0.081449 | 0.11133 | 0.021478 | 0.040903 | -0.12103 | 0.19234 | -0.013859 | 0.18703 | 0.015017 | -0.028724 | 0.036621 | 0.036621 | -0.036621 | 0.041199 | 0.13733 | 0.004578 | -0.14191 | -0.64087 | -0.63171 | -0.71869 | -0.57678 | -0.59509 | -0.73242 | -0.79651 | 0.71869 | 0.5722 | -122.4106 | 0.75073 | 0.75531 | 0.18311 | -122.5113 | -0.018311 | -0.082398 | -123.1247 | 0.073242 | -0.004578 | 0.07782 | -123.143 | 0.85144 | 0.75073 | 0.67749 | -122.6898 | 0.13733 | 0.11902 | 0.082397 | -123.3444
1068.8438 | 123.2162 | -0.71869 | 122.58 | 0.24392 | 0.17222 | 0.14506 | 0.063291 | 0.099578 | 0.0054557 | 0.025949 | -0.10577 | 0.19448 | -0.0042459 | 0.19344 | 0.02997 | -0.029792 | -0.004578 | -0.027466 | -0.086975 | 0.009155 | 0.14191 | -0.027466 | -0.15564 | -0.70038 | -0.71869 | -0.77362 | -0.54932 | -0.58594 | -0.75073 | -0.82855 | 0.69122 | 0.56305 | -122.438 | 0.69122 | 0.72784 | 0.16479 | -122.5845 | -0.032043 | -0.10986 | -123.1293 | 0.018311 | -0.054932 | 0.054931 | -123.1659 | 0.8606 | 0.71411 | 0.63171 | -122.7356 | 0.16937 | 0.13275 | 0 | -123.4085
1069.9062 | 123.3765 | -0.6958 | 122.5113 | 0.091333 | 0.15192 | 0.1504 | 0.072904 | 0.10278 | -0.026587 | 0.028085 | 0.24518 | 0.17419 | -0.0042459 | 0.1614 | 0.0011309 | -0.0084301 | 0.004578 | 0.073242 | 0.036621 | 0.059509 | 0.12817 | 0.022888 | -0.12817 | -0.60425 | -0.55847 | -0.60883 | -0.59052 | -0.60883 | -0.72327 | -0.79193 | 0.71869 | 0.56763 | -122.3831 | 0.76904 | 0.75531 | 0.18768 | -122.5067 | -0.027466 | -0.09613 | -123.1018 | 0.091553 | 0.086975 | 0.18311 | -123.1201 | 0.82398 | 0.70038 | 0.73242 | -122.6395 | 0.10529 | 0.086975 | 0.13733 | -123.3032
1070.8438 | 123.3765 | -0.67749 | 122.5204 | 0.48806 | 0.15086 | 0.12903 | 0.0697 | 0.1156 | 0.010797 | 0.035562 | 0.39777 | 0.17312 | 0.0064351 | 0.17315 | 0.019289 | -0.026588 | 0.07782 | 0.09613 | 0.041199 | 0.07782 | 0.10986 | 0.013733 | -0.1236 | -0.56763 | -0.5722 | -0.63171 | -0.59509 | -0.64087 | -0.70953 | -0.78735 | 0.69122 | 0.55389 | -122.4106 | 0.77362 | 0.75531 | 0.20142 | -122.4426 | -0.032044 | -0.10986 | -123.1155 | 0.10986 | 0.045776 | 0.15564 | -123.1613 | 0.78735 | 0.75531 | 0.71869 | -122.644 | 0.082397 | 0.036621 | 0.10529 | -123.3078
1071.9062 | 123.2483 | -0.70953 | 122.5662 | 0.15237 | 0.19038 | 0.13544 | 0.07504 | 0.11026 | 0.014001 | 0.034494 | -0.044738 | 0.19234 | -0.0021099 | 0.20305 | 0.020357 | -0.037269 | 0.022888 | -0.004578 | -0.068665 | 0.009155 | 0.16022 | -0.018311 | -0.13733 | -0.66834 | -0.6546 | -0.72784 | -0.55389 | -0.58594 | -0.737 | -0.79651 | 0.69122 | 0.5722 | -122.406 | 0.70496 | 0.71869 | 0.14648 | -122.5433 | -0.027466 | -0.086975 | -123.1201 | 0.041199 | -0.01831 | 0.068665 | -123.1522 | 0.86975 | 0.73242 | 0.64087 | -122.7036 | 0.15564 | 0.1236 | 0.054932 | -123.3627
1072.8438 | 123.349 | -0.70953 | 122.5342 | 0.57961 | 0.16901 | 0.15467 | 0.082517 | 0.10812 | 0.00011475 | 0.034494 | 0.35199 | 0.18594 | 0.0064351 | 0.17421 | 0.0086079 | -0.029792 | 0.013733 | 0.036621 | -0.032043 | 0.041199 | 0.13275 | 0.009155 | -0.11444 | -0.57678 | -0.60883 | -0.64087 | -0.5722 | -0.61798 | -0.71411 | -0.78278 | 0.71869 | 0.59509 | -122.4014 | 0.74616 | 0.75073 | 0.15564 | -122.5204 | -0.004577 | -0.073242 | -123.1064 | 0.13275 | 0.068665 | 0.14191 | -123.1522 | 0.84228 | 0.72327 | 0.67749 | -122.6486 | 0.13733 | 0.091553 | 0.10071 | -123.317
1073.9062 | 123.2437 | -0.72784 | 122.5891 | -0.24436 | 0.14231 | 0.14719 | 0.072904 | 0.095305 | -0.011634 | 0.017404 | -0.41095 | 0.18807 | -0.013859 | 0.17742 | 0.011812 | -0.022315 | -0.004578 | 0.022888 | -0.050354 | 0 | 0.15106 | -0.018311 | -0.15106 | -0.67749 | -0.65002 | -0.72327 | -0.53101 | -0.5722 | -0.73242 | -0.80566 | 0.70953 | 0.57678 | -122.438 | 0.75073 | 0.72784 | 0.15106 | -122.5937 | -0.004578 | -0.07782 | -123.1201 | 0.050354 | 0.004577 | 0.082397 | -123.1613 | 0.87891 | 0.72327 | 0.67749 | -122.7402 | 0.19684 | 0.15564 | 0.07782 | -123.3948
1074.8438 | 123.2529 | -0.72327 | 122.5983 | 0.44228 | 0.16795 | 0.13117 | 0.072904 | 0.099578 | 0.02041 | 0.03129 | 0.18414 | 0.19234 | 0.0085721 | 0.18596 | 0.01288 | -0.027656 | -0.004578 | -0.064087 | -0.10071 | -0.013733 | 0.14648 | -0.013733 | -0.15106 | -0.67749 | -0.71869 | -0.75531 | -0.52185 | -0.56763 | -0.74616 | -0.81024 | 0.70953 | 0.5722 | -122.4518 | 0.65918 | 0.70953 | 0.13733 | -122.6028 | -0.022888 | -0.086975 | -123.1201 | 0.045777 | -0.032043 | 0.054932 | -123.1659 | 0.86975 | 0.71869 | 0.62256 | -122.7493 | 0.20142 | 0.15564 | 0.004578 | -123.4085
1075.9062 | 123.2162 | -0.72784 | 122.58 | 0.12185 | 0.19572 | 0.12797 | 0.087858 | 0.10812 | 0.02041 | 0.038766 | 0.016297 | 0.18914 | 0.0032311 | 0.17742 | 0.023561 | -0.040473 | 0 | -0.036621 | -0.073242 | 0 | 0.13275 | -0.027466 | -0.15564 | -0.66834 | -0.69122 | -0.76446 | -0.56763 | -0.56763 | -0.73242 | -0.81482 | 0.70038 | 0.5722 | -122.4472 | 0.69122 | 0.72784 | 0.15564 | -122.58 | -0.004578 | -0.086975 | -123.1476 | 0.059509 | -0.036621 | 0.050354 | -123.1476 | 0.86059 | 0.72784 | 0.6546 | -122.7356 | 0.16022 | 0.16022 | 0.036621 | -123.3948
1076.8438 | 123.2162 | -0.70953 | 122.5708 | 0.2134 | 0.16901 | 0.14078 | 0.077177 | 0.11667 | 0.0086597 | 0.038766 | 0.13837 | 0.19555 | 0.012844 | 0.19024 | 0.021425 | -0.031928 | -0.022888 | -0.059509 | -0.09613 | -0.018311 | 0.15106 | -0.036621 | -0.14648 | -0.6958 | -0.70038 | -0.77362 | -0.53101 | -0.5722 | -0.71869 | -0.80566 | 0.67291 | 0.56305 | -122.4197 | 0.65002 | 0.69122 | 0.12817 | -122.5937 | -0.009155 | -0.09613 | -123.1018 | 0.013733 | -0.064087 | 0.032043 | -123.143 | 0.8606 | 0.68665 | 0.6134 | -122.7173 | 0.17853 | 0.13733 | 0.009156 | -123.3765
1077.9062 | 123.2895 | -0.70496 | 122.5845 | 0.060816 | 0.18504 | 0.13651 | 0.076109 | 0.095305 | 0.011865 | 0.03663 | -0.15155 | 0.19341 | -0.0042459 | 0.18596 | 0.021425 | -0.027656 | 0.045776 | 0.032043 | -0.032043 | 0.036621 | 0.13733 | -0.018311 | -0.14648 | -0.60425 | -0.59967 | -0.67291 | -0.54474 | -0.58594 | -0.71869 | -0.78278 | 0.68665 | 0.55847 | -122.4472 | 0.737 | 0.74158 | 0.18311 | -122.5388 | -0.013733 | -0.07782 | -123.1293 | 0.10071 | 0.032043 | 0.10986 | -123.1705 | 0.84229 | 0.75073 | 0.67291 | -122.731 | 0.16022 | 0.11902 | 0.10529 | -123.3673
1078.8438 | 123.2712 | -0.70496 | 122.6074 | -0.15281 | 0.18504 | 0.14399 | 0.07504 | 0.12094 | 0.012933 | 0.033426 | -0.63983 | 0.19555 | 0.0075041 | 0.19344 | 0.018221 | -0.02552 | 0.022888 | 0.027466 | -0.045776 | 0.036621 | 0.16479 | -0.022888 | -0.13733 | -0.63629 | -0.59052 | -0.68207 | -0.54474 | -0.5722 | -0.73242 | -0.78278 | 0.68207 | 0.56763 | -122.4426 | 0.73242 | 0.74158 | 0.17395 | -122.5845 | -0.027466 | -0.07782 | -123.1522 | 0.068664 | 0.022888 | 0.10071 | -123.1796 | 0.86975 | 0.72784 | 0.65918 | -122.7448 | 0.16022 | 0.13275 | 0.11444 | -123.3902
1079.9219 | 123.3765 | -0.68207 | 122.5479 | 0.030298 | 0.14445 | 0.14612 | 0.064359 | 0.094237 | -0.022315 | 0.021677 | 0.092591 | 0.17526 | 0.0010951 | 0.16887 | 0.0054039 | -0.015907 | -0.018311 | 0.054932 | 0.013733 | 0.054932 | 0.10529 | 0.022888 | -0.13275 | -0.58136 | -0.56763 | -0.58594 | -0.54932 | -0.58136 | -0.70038 | -0.75073 | 0.70496 | 0.54932 | -122.4426 | 0.737 | 0.737 | 0.18768 | -122.5662 | -0.01831 | -0.068664 | -123.0972 | 0.10071 | 0.096131 | 0.16479 | -123.1293 | 0.78735 | 0.66376 | 0.6958 | -122.6807 | 0.13275 | 0.10071 | 0.11444 | -123.2986
1080.8438 | 123.2346 | -0.71411 | 122.6074 | 0.045557 | 0.19251 | 0.14506 | 0.072904 | 0.1156 | 0.027886 | 0.021677 | -0.13629 | 0.19128 | 0.012844 | 0.18489 | 0.020357 | -0.036201 | 0.009155 | 0 | -0.07782 | 0.009155 | 0.14191 | -0.009155 | -0.15106 | -0.66834 | -0.66376 | -0.73242 | -0.52185 | -0.56305 | -0.71869 | -0.79651 | 0.70496 | 0.56305 | -122.4655 | 0.71411 | 0.72327 | 0.16022 | -122.5983 | -0.004578 | -0.082398 | -123.1293 | 0.045776 | -0.018311 | 0.064087 | -123.1705 | 0.85602 | 0.72327 | 0.63629 | -122.7585 | 0.19226 | 0.15106 | 0.050354 | -123.4039
1081.9062 | 123.262 | -0.6958 | 122.5937 | -0.15281 | 0.17329 | 0.1536 | 0.072904 | 0.11239 | 0.0075917 | 0.028085 | -0.45673 | 0.18914 | -0.0042459 | 0.18276 | 0.0096759 | -0.02552 | -0.036621 | -0.009155 | -0.091553 | 0.018311 | 0.16022 | -0.022888 | -0.15564 | -0.66834 | -0.62714 | -0.68665 | -0.51727 | -0.55847 | -0.72784 | -0.78278 | 0.67291 | 0.54016 | -122.4335 | 0.68665 | 0.71411 | 0.17395 | -122.6303 | -0.032043 | -0.086975 | -123.111 | 0.027466 | 0.009155 | 0.09613 | -123.1522 | 0.85602 | 0.65918 | 0.60425 | -122.7493 | 0.17853 | 0.13733 | 0.068665 | -123.3765
1082.8438 | 123.23 | -0.70038 | 122.5983 | 0.45754 | 0.18717 | 0.16108 | 0.072904 | 0.10278 | 0.010797 | 0.032358 | 0.18414 | 0.19662 | 0.011776 | 0.18703 | 0.022493 | -0.024451 | -0.050354 | -0.064087 | -0.10529 | -0.022888 | 0.16479 | -0.022888 | -0.15564 | -0.6546 | -0.68665 | -0.73242 | -0.50354 | -0.56305 | -0.71869 | -0.80566 | 0.67749 | 0.54474 | -122.4335 | 0.63629 | 0.67749 | 0.13275 | -122.6486 | -0.018311 | -0.10529 | -123.1018 | 0.045776 | -0.032044 | 0.073242 | -123.1613 | 0.86517 | 0.65002 | 0.59509 | -122.7539 | 0.19684 | 0.13733 | 0.013732 | -123.4039
1083.8438 | 123.2437 | -0.71869 | 122.5937 | -0.41221 | 0.15406 | 0.14826 | 0.076109 | 0.10278 | -0.0073613 | 0.029153 | -0.39569 | 0.18807 | 0.0042991 | 0.16887 | 0.010744 | -0.034064 | -0.041199 | -0.018311 | -0.064087 | -0.013733 | 0.16479 | -0.032043 | -0.1831 | -0.65918 | -0.63629 | -0.70496 | -0.50354 | -0.54474 | -0.72784 | -0.78735 | 0.68665 | 0.53558 | -122.4289 | 0.70038 | 0.70496 | 0.16937 | -122.6349 | -0.009155 | -0.068665 | -123.0972 | 0.059509 | 0.013733 | 0.082398 | -123.1384 | 0.88348 | 0.67749 | 0.6546 | -122.7768 | 0.21515 | 0.17395 | 0.082397 | -123.381
1084.9219 | 123.3536 | -0.66376 | 122.5754 | 0.50332 | 0.16688 | 0.15146 | 0.066496 | 0.10492 | -0.014838 | 0.030222 | 0.4588 | 0.17098 | -0.0095859 | 0.18489 | 0.011812 | -0.023383 | 0.064087 | 0.11902 | 0.041199 | 0.068665 | 0.10529 | 0.032043 | -0.10986 | -0.54016 | -0.54932 | -0.58594 | -0.55847 | -0.59052 | -0.68207 | -0.75073 | 0.6958 | 0.55389 | -122.4701 | 0.78278 | 0.73242 | 0.17853 | -122.5113 | -0.018311 | -0.086975 | -123.1338 | 0.1236 | 0.07782 | 0.16479 | -123.1659 | 0.76904 | 0.72784 | 0.70496 | -122.6852 | 0.10529 | 0.073242 | 0.11444 | -123.3261
1085.8438 | 123.2574 | -0.70496 | 122.5937 | -0.2291 | 0.16581 | 0.14399 | 0.088926 | 0.11774 | 0.0033197 | 0.03129 | -0.47198 | 0.18914 | 0.0085721 | 0.19344 | 0.0064719 | -0.028724 | -0.022888 | -0.022888 | -0.09613 | 0.022888 | 0.16022 | -0.027466 | -0.15106 | -0.65918 | -0.62256 | -0.69122 | -0.50354 | -0.57678 | -0.69122 | -0.78278 | 0.67749 | 0.55389 | -122.4335 | 0.68207 | 0.72784 | 0.17395 | -122.6166 | 0.013733 | -0.07782 | -123.0972 | 0.045776 | 0.013733 | 0.091553 | -123.1705 | 0.86517 | 0.68207 | 0.60883 | -122.7448 | 0.20142 | 0.12817 | 0.082397 | -123.3765
1086.9062 | 123.2849 | -0.6958 | 122.5891 | 0.045557 | 0.18183 | 0.13651 | 0.087858 | 0.099578 | 0.017205 | 0.037698 | -0.22784 | 0.187 | 0.012844 | 0.17849 | 0.015017 | -0.041541 | 0.036621 | 0.064087 | -0.027466 | 0.032043 | 0.13275 | -0.009155 | -0.14648 | -0.59052 | -0.59967 | -0.66376 | -0.51727 | -0.56763 | -0.71869 | -0.78735 | 0.68665 | 0.54932 | -122.4564 | 0.75989 | 0.72784 | 0.17853 | -122.5525 | -0.022888 | -0.091553 | -123.1064 | 0.10529 | 0.032044 | 0.1236 | -123.1567 | 0.82855 | 0.73242 | 0.66834 | -122.7356 | 0.17853 | 0.12817 | 0.096131 | -123.3765
1087.8438 | 123.2437 | -0.6958 | 122.5937 | -0.3054 | 0.12843 | 0.14826 | 0.061155 | 0.10919 | -0.0052253 | 0.027017 | -0.28888 | 0.18166 | -0.0010409 | 0.1881 | 0.0096759 | -0.027656 | -0.004578 | 0.054932 | -0.032043 | 0.018311 | 0.13733 | -0.009155 | -0.13733 | -0.63171 | -0.61798 | -0.67749 | -0.5127 | -0.54932 | -0.71869 | -0.77362 | 0.68665 | 0.55847 | -122.4564 | 0.75073 | 0.71411 | 0.15564 | -122.5983 | -0.022888 | -0.07782 | -123.1064 | 0.064087 | 0.018311 | 0.096131 | -123.143 | 0.83313 | 0.69122 | 0.66376 | -122.731 | 0.18311 | 0.14648 | 0.07782 | -123.3673
1088.9062 | 123.3261 | -0.6546 | 122.58 | 0.33547 | 0.13056 | 0.1504 | 0.080381 | 0.10065 | -0.024451 | 0.029153 | 0.18414 | 0.17846 | 0.0064351 | 0.18276 | 0.0032669 | -0.020179 | -0.022888 | 0.036621 | -0.013733 | 0.045776 | 0.15106 | 0 | -0.12817 | -0.56763 | -0.57678 | -0.60883 | -0.53558 | -0.58594 | -0.68665 | -0.74616 | 0.6546 | 0.52643 | -122.4289 | 0.69122 | 0.70038 | 0.17395 | -122.6028 | -0.032044 | -0.091553 | -123.1155 | 0.086975 | 0.045776 | 0.13733 | -123.1659 | 0.80566 | 0.63171 | 0.64087 | -122.7081 | 0.11902 | 0.068665 | 0.07782 | -123.3261
1089.8438 | 123.2941 | -0.66834 | 122.5983 | -0.12229 | 0.17863 | 0.14078 | 0.0697 | 0.098509 | 0.015069 | 0.029153 | -0.36517 | 0.19021 | -0.0010409 | 0.18276 | 0.018221 | -0.041541 | 0.036621 | 0.041199 | -0.054932 | 0.045776 | 0.15564 | -0.022888 | -0.13275 | -0.60883 | -0.59509 | -0.67291 | -0.49439 | -0.56305 | -0.71411 | -0.75531 | 0.64545 | 0.53558 | -122.4426 | 0.70953 | 0.71411 | 0.17853 | -122.5616 | -0.045776 | -0.086975 | -123.0927 | 0.059509 | -0.004578 | 0.082397 | -123.1613 | 0.82398 | 0.70496 | 0.6134 | -122.731 | 0.17395 | 0.10529 | 0.073242 | -123.3536
1090.9062 | 123.3536 | -0.66376 | 122.5891 | -0.21384 | 0.13911 | 0.15681 | 0.073972 | 0.095305 | -0.022315 | 0.01954 | -0.2431 | 0.18166 | -0.012791 | 0.19558 | 0.0011309 | -0.020179 | 0.059509 | 0.16937 | 0.082397 | 0.09613 | 0.10986 | 0.013733 | -0.10986 | -0.52643 | -0.48981 | -0.54932 | -0.54016 | -0.59052 | -0.68207 | -0.73242 | 0.67749 | 0.55389 | -122.4792 | 0.83313 | 0.75989 | 0.20599 | -122.5296 | -0.018311 | -0.068665 | -123.1293 | 0.13733 | 0.11444 | 0.18311 | -123.1796 | 0.77362 | 0.72327 | 0.74615 | -122.699 | 0.1236 | 0.073242 | 0.17395 | -123.3215
1091.8438 | 123.3307 | -0.65918 | 122.5845 | -0.21384 | 0.13697 | 0.14399 | 0.067564 | 0.11239 | -0.010566 | 0.032358 | -0.39569 | 0.1806 | 0.01498 | 0.17208 | 0.0075399 | -0.034064 | 0.041199 | 0.12817 | 0.045776 | 0.086975 | 0.1236 | 0.004578 | -0.11444 | -0.57678 | -0.52185 | -0.60425 | -0.54932 | -0.5722 | -0.6958 | -0.75531 | 0.66376 | 0.54474 | -122.4609 | 0.78735 | 0.74616 | 0.20142 | -122.5433 | -0.036621 | -0.09613 | -123.1339 | 0.082398 | 0.054932 | 0.15106 | -123.1567 | 0.78278 | 0.70038 | 0.70496 | -122.699 | 0.10986 | 0.086975 | 0.13733 | -123.3398
1092.9062 | 123.2529 | -0.6958 | 122.6212 | -0.24436 | 0.15192 | 0.14506 | 0.080381 | 0.10705 | 0.012933 | 0.016336 | -0.45673 | 0.17846 | 0.010708 | 0.18169 | 0.013948 | -0.035133 | -0.036621 | 0.004578 | -0.091553 | -0.004578 | 0.17853 | -0.013733 | -0.18768 | -0.63629 | -0.63171 | -0.70496 | -0.49896 | -0.54932 | -0.72327 | -0.78735 | 0.68207 | 0.50812 | -122.4426 | 0.70038 | 0.69122 | 0.1831 | -122.6578 | -0.027466 | -0.091553 | -123.1201 | 0.059509 | -0.009155 | 0.082398 | -123.1705 | 0.87433 | 0.65918 | 0.60425 | -122.8088 | 0.19684 | 0.14648 | 0.064087 | -123.4085
1093.8438 | 123.2529 | -0.68665 | 122.6166 | -0.13755 | 0.15513 | 0.14612 | 0.067564 | 0.11026 | 0.0022517 | 0.030222 | -0.45673 | 0.18273 | 2.7137e-05 | 0.18703 | 0.015017 | -0.02552 | -0.004578 | 0.009155 | -0.073242 | 0 | 0.16479 | -0.018311 | -0.16479 | -0.63629 | -0.63171 | -0.6958 | -0.49439 | -0.54932 | -0.71869 | -0.78278 | 0.66834 | 0.52185 | -122.4518 | 0.6958 | 0.68665 | 0.16479 | -122.6212 | -0.032043 | -0.09613 | -123.111 | 0.050354 | -0.009155 | 0.086975 | -123.1659 | 0.85144 | 0.68207 | 0.6134 | -122.7814 | 0.19226 | 0.13733 | 0.054932 | -123.3994
1094.9062 | 123.2803 | -0.66834 | 122.6028 | -0.19858 | 0.1562 | 0.16001 | 0.055814 | 0.10919 | 0.023614 | 0.029153 | -0.47198 | 0.18914 | -0.0021099 | 0.17742 | 0.032106 | -0.039405 | -0.032043 | 0.027466 | -0.073242 | 0.013733 | 0.14191 | -0.032043 | -0.16022 | -0.60425 | -0.59509 | -0.65918 | -0.48981 | -0.54474 | -0.70038 | -0.78735 | 0.63629 | 0.50812 | -122.4609 | 0.6958 | 0.68207 | 0.17395 | -122.6349 | -0.032043 | -0.11902 | -123.0927 | 0.064087 | 0.009155 | 0.12817 | -123.1476 | 0.81024 | 0.63629 | 0.59509 | -122.7631 | 0.17853 | 0.1236 | 0.073242 | -123.3902
1095.8438 | 123.4085 | -0.64087 | 122.5891 | 0.015039 | 0.13804 | 0.1536 | 0.079313 | 0.092101 | -0.018043 | 0.024881 | -0.12103 | 0.17953 | -0.0063819 | 0.18169 | 0.0011309 | -0.019111 | 0.054932 | 0.16479 | 0.064087 | 0.068665 | 0.10071 | 0.022888 | -0.12817 | -0.54016 | -0.47607 | -0.55389 | -0.54016 | -0.60883 | -0.67749 | -0.72784 | 0.66376 | 0.5127 | -122.4884 | 0.80566 | 0.70953 | 0.19684 | -122.5342 | -0.036621 | -0.086975 | -123.1293 | 0.10071 | 0.086975 | 0.17395 | -123.1979 | 0.74158 | 0.6958 | 0.70496 | -122.7173 | 0.10071 | 0.032043 | 0.1648 | -123.317
1096.9062 | 123.3536 | -0.64545 | 122.5708 | 0.060816 | 0.14231 | 0.14612 | 0.072904 | 0.10171 | -0.0084293 | 0.027017 | -0.10577 | 0.16885 | -0.015995 | 0.17528 | 0.0021989 | -0.023383 | 0.027466 | 0.10071 | 0.013733 | 0.059509 | 0.13275 | -0.004578 | -0.10986 | -0.52643 | -0.53558 | -0.5722 | -0.53558 | -0.57678 | -0.68207 | -0.74158 | 0.64087 | 0.53558 | -122.4381 | 0.74616 | 0.70496 | 0.16937 | -122.5433 | -0.036621 | -0.09613 | -123.1064 | 0.11902 | 0.073242 | 0.16937 | -123.1476 | 0.7782 | 0.67291 | 0.65918 | -122.6807 | 0.10986 | 0.068665 | 0.10986 | -123.3124
1097.8438 | 123.3536 | -0.65002 | 122.58 | -0.19858 | 0.14765 | 0.15467 | 0.054746 | 0.11133 | -0.014838 | 0.03129 | -0.30414 | 0.17953 | -0.012791 | 0.18917 | 0.0043349 | -0.036201 | 0.059509 | 0.15564 | 0.054932 | 0.07782 | 0.11902 | 0.018311 | -0.13275 | -0.51727 | -0.46692 | -0.56305 | -0.53558 | -0.58136 | -0.66376 | -0.72784 | 0.66834 | 0.51727 | -122.4609 | 0.80566 | 0.72784 | 0.21057 | -122.5204 | -0.013733 | -0.07782 | -123.1155 | 0.13275 | 0.086975 | 0.1648 | -123.1613 | 0.76904 | 0.70953 | 0.70496 | -122.7127 | 0.11444 | 0.068664 | 0.18311 | -123.3078
1098.9062 | 123.3124 | -0.64087 | 122.6074 | -0.2291 | 0.14979 | 0.1536 | 0.064359 | 0.10385 | 0.010797 | 0.028085 | -0.45673 | 0.187 | -0.0085179 | 0.18703 | 0.0021989 | -0.044746 | 0.036621 | 0.10071 | 0.032043 | 0.068665 | 0.1236 | 0 | -0.13733 | -0.5722 | -0.54474 | -0.61798 | -0.52185 | -0.54932 | -0.6958 | -0.74158 | 0.64087 | 0.50354 | -122.4838 | 0.74158 | 0.70953 | 0.20599 | -122.5708 | -0.054932 | -0.10071 | -123.1293 | 0.068664 | 0.022888 | 0.1236 | -123.1567 | 0.76447 | 0.67749 | 0.67291 | -122.7448 | 0.11902 | 0.091553 | 0.09613 | -123.349
1099.8438 | 123.2574 | -0.68207 | 122.6349 | -0.29014 | 0.14765 | 0.14292 | 0.060087 | 0.11239 | 0.015069 | 0.030222 | -0.56354 | 0.19662 | -0.0031779 | 0.1881 | 0.01288 | -0.042609 | 0 | 0.009155 | -0.07782 | 0 | 0.16022 | -0.027466 | -0.16479 | -0.60425 | -0.61798 | -0.70496 | -0.50354 | -0.55389 | -0.70496 | -0.79193 | 0.6546 | 0.51727 | -122.4747 | 0.69122 | 0.68207 | 0.16479 | -122.6349 | -0.022888 | -0.10986 | -123.1384 | 0.07782 | -0.022888 | 0.086975 | -123.1888 | 0.84228 | 0.68207 | 0.60425 | -122.7997 | 0.17853 | 0.12817 | 0.064087 | -123.4268
1100.9062 | 123.3948 | -0.63171 | 122.6028 | 0.16763 | 0.13697 | 0.1504 | 0.072904 | 0.094237 | -0.0073613 | 0.029153 | -0.15155 | 0.18807 | -0.0010409 | 0.18917 | 0.0075399 | -0.019111 | 0.032043 | 0.13275 | 0.022888 | 0.073242 | 0.13275 | 0.022888 | -0.1236 | -0.50812 | -0.53558 | -0.55847 | -0.53558 | -0.59052 | -0.65918 | -0.74158 | 0.6546 | 0.50812 | -122.4701 | 0.76446 | 0.70496 | 0.19684 | -122.5708 | -0.027466 | -0.10986 | -123.1384 | 0.1236 | 0.073242 | 0.18311 | -123.1934 | 0.76446 | 0.66376 | 0.6546 | -122.7264 | 0.096131 | 0.041199 | 0.096131 | -123.3444
1101.8438 | 123.3627 | -0.63629 | 122.6212 | -0.21384 | 0.15299 | 0.15467 | 0.08679 | 0.10278 | -0.00095325 | 0.029153 | -0.3194 | 0.1838 | -0.022404 | 0.16246 | 0.0011309 | -0.039405 | 0.064087 | 0.13733 | 0.050354 | 0.091553 | 0.10986 | 0.013733 | -0.11444 | -0.53101 | -0.48523 | -0.57678 | -0.52643 | -0.57678 | -0.67291 | -0.74616 | 0.65002 | 0.52185 | -122.5113 | 0.77362 | 0.72784 | 0.20599 | -122.5571 | -0.036621 | -0.10986 | -123.1476 | 0.10529 | 0.05951 | 0.16937 | -123.1979 | 0.74616 | 0.70038 | 0.68665 | -122.7356 | 0.10986 | 0.05951 | 0.15106 | -123.3673
1102.9062 | 123.3856 | -0.62714 | 122.5708 | -0.64109 | 0.12736 | 0.13651 | 0.079313 | 0.11346 | -0.011634 | 0.027017 | -0.27362 | 0.17632 | -0.0085179 | 0.17315 | 0.0096759 | -0.03086 | 0.091553 | 0.18768 | 0.068665 | 0.082397 | 0.11902 | 0 | -0.11902 | -0.5127 | -0.46692 | -0.55847 | -0.55389 | -0.59509 | -0.66376 | -0.72784 | 0.62714 | 0.50812 | -122.4518 | 0.81482 | 0.70953 | 0.20142 | -122.4792 | -0.036621 | -0.10071 | -123.1247 | 0.11444 | 0.068664 | 0.16937 | -123.1659 | 0.74616 | 0.71869 | 0.6958 | -122.6898 | 0.073242 | 0.032043 | 0.16022 | -123.2986
1103.8438 | 123.2574 | -0.69122 | 122.6486 | -0.25962 | 0.15513 | 0.15146 | 0.085722 | 0.10171 | 0.024682 | 0.032358 | -0.51776 | 0.187 | -0.0021099 | 0.18276 | 0.022493 | -0.043678 | -0.018311 | -0.009155 | -0.07782 | -0.018311 | 0.16479 | -0.018311 | -0.16479 | -0.61798 | -0.6134 | -0.70038 | -0.49439 | -0.55389 | -0.6958 | -0.77362 | 0.67291 | 0.52643 | -122.4838 | 0.68207 | 0.67291 | 0.14648 | -122.6669 | -0.004578 | -0.082398 | -123.143 | 0.073242 | -0.009155 | 0.073243 | -123.2025 | 0.85602 | 0.67291 | 0.6134 | -122.8134 | 0.19684 | 0.13733 | 0.07782 | -123.4222
1104.9062 | 123.2712 | -0.67749 | 122.5983 | -0.00022031 | 0.16901 | 0.14506 | 0.072904 | 0.10171 | 0.02575 | 0.030222 | -0.25836 | 0.19234 | 0.0053671 | 0.19344 | 0.02463 | -0.038337 | 0.054932 | 0.059509 | -0.036621 | 0.018311 | 0.15564 | -0.018311 | -0.14648 | -0.58594 | -0.58594 | -0.67291 | -0.50354 | -0.54932 | -0.69122 | -0.75531 | 0.65918 | 0.53101 | -122.4426 | 0.737 | 0.6958 | 0.16479 | -122.5433 | -0.013733 | -0.07782 | -123.1018 | 0.091553 | 0.004577 | 0.082397 | -123.1476 | 0.83313 | 0.73242 | 0.64087 | -122.7448 | 0.17395 | 0.12817 | 0.091553 | -123.3536
1105.8438 | 123.317 | -0.6546 | 122.5937 | -0.24436 | 0.14658 | 0.13865 | 0.062223 | 0.11346 | -0.014838 | 0.030222 | -0.3194 | 0.17739 | -0.013859 | 0.1678 | 0.0043349 | -0.026588 | 0.027466 | 0.15106 | 0.027466 | 0.07782 | 0.1236 | 0.004578 | -0.1236 | -0.54932 | -0.52643 | -0.57678 | -0.51727 | -0.56763 | -0.67291 | -0.74616 | 0.65918 | 0.53101 | -122.4701 | 0.80566 | 0.73242 | 0.20142 | -122.5662 | -0.018311 | -0.091553 | -123.111 | 0.10529 | 0.07782 | 0.16937 | -123.1613 | 0.7782 | 0.68207 | 0.68207 | -122.7173 | 0.13733 | 0.086975 | 0.12817 | -123.3398
1106.9062 | 123.2574 | -0.70038 | 122.6669 | -0.32065 | 0.14445 | 0.14719 | 0.067564 | 0.11346 | 0.00011475 | 0.037698 | -0.21259 | 0.19234 | 2.7137e-05 | 0.15926 | 0.0021989 | -0.03086 | -0.032043 | 0.082397 | -0.032043 | 0.009155 | 0.15106 | -0.018311 | -0.15564 | -0.62714 | -0.59967 | -0.67291 | -0.49896 | -0.53558 | -0.72327 | -0.79193 | 0.68207 | 0.54474 | -122.5159 | 0.78277 | 0.70953 | 0.16479 | -122.699 | -0.022889 | -0.091553 | -123.1659 | 0.073242 | 0.027465 | 0.11902 | -123.2025 | 0.85144 | 0.66833 | 0.66833 | -122.8226 | 0.20142 | 0.16479 | 0.10071 | -123.4589
1107.8438 | 123.3627 | -0.6546 | 122.5983 | -0.19858 | 0.14765 | 0.14185 | 0.064359 | 0.12094 | -0.01377 | 0.030222 | -0.25836 | 0.18273 | 0.0032311 | 0.18489 | 0.0043349 | -0.029792 | 0.036621 | 0.15106 | 0.041199 | 0.073242 | 0.1236 | 0.004578 | -0.10529 | -0.54932 | -0.49439 | -0.57678 | -0.54474 | -0.58136 | -0.68207 | -0.76904 | 0.65918 | 0.54932 | -122.4747 | 0.80566 | 0.72784 | 0.17853 | -122.5616 | -0.027466 | -0.11444 | -123.143 | 0.10529 | 0.07782 | 0.19226 | -123.1796 | 0.7782 | 0.69122 | 0.6958 | -122.7036 | 0.10986 | 0.073242 | 0.16022 | -123.3673
1108.9062 | 123.3902 | -0.64087 | 122.5845 | -0.13755 | 0.13804 | 0.15681 | 0.064359 | 0.11026 | -0.022315 | 0.023813 | -0.075256 | 0.1806 | -0.017063 | 0.17208 | 0.0064719 | -0.027656 | 0.022888 | 0.1236 | 0.036621 | 0.064087 | 0.12817 | 0.013733 | -0.11444 | -0.51727 | -0.49896 | -0.55847 | -0.52643 | -0.5722 | -0.64545 | -0.74158 | 0.6546 | 0.52643 | -122.4564 | 0.76447 | 0.70496 | 0.17853 | -122.5616 | -0.004578 | -0.10071 | -123.111 | 0.1236 | 0.082397 | 0.18311 | -123.1567 | 0.76904 | 0.66376 | 0.67749 | -122.699 | 0.11444 | 0.068664 | 0.14191 | -123.3261
1109.8438 | 123.2483 | -0.70496 | 122.6257 | -0.77842 | 0.13911 | 0.14612 | 0.067564 | 0.12308 | 0.014001 | 0.021677 | -0.42621 | 0.19128 | -0.013859 | 0.1881 | 0.021425 | -0.029792 | -0.022888 | 0.027466 | -0.064087 | -0.018311 | 0.16022 | -0.018311 | -0.17853 | -0.62256 | -0.62256 | -0.70496 | -0.50812 | -0.55847 | -0.70496 | -0.79193 | 0.68665 | 0.52643 | -122.4655 | 0.73242 | 0.68665 | 0.16022 | -122.6486 | 0 | -0.086975 | -123.1338 | 0.082397 | 0 | 0.086975 | -123.1842 | 0.86517 | 0.68207 | 0.64087 | -122.8043 | 0.19684 | 0.14648 | 0.082397 | -123.4177
1110.9062 | 123.3398 | -0.65002 | 122.5845 | -0.24436 | 0.14124 | 0.15681 | 0.063291 | 0.11453 | -0.0030893 | 0.024881 | -0.25836 | 0.18273 | -0.0021099 | 0.19771 | 0.015017 | -0.028724 | 0.050354 | 0.14191 | 0.050354 | 0.07782 | 0.11444 | 0.027466 | -0.11902 | -0.53558 | -0.49439 | -0.58594 | -0.53101 | -0.59967 | -0.68207 | -0.737 | 0.67749 | 0.53101 | -122.4701 | 0.79193 | 0.72784 | 0.19684 | -122.5342 | -0.032044 | -0.086976 | -123.1155 | 0.11444 | 0.064087 | 0.15106 | -123.1842 | 0.76447 | 0.70038 | 0.70038 | -122.7036 | 0.11902 | 0.050354 | 0.15564 | -123.3215
1111.8438 | 123.3948 | -0.64545 | 122.5937 | -0.030737 | 0.14231 | 0.15574 | 0.064359 | 0.10919 | -0.011634 | 0.027017 | 0.046815 | 0.17312 | 0.0010951 | 0.1678 | 0.0054039 | -0.026588 | 0.054932 | 0.14191 | 0.054932 | 0.068665 | 0.10986 | 0 | -0.12817 | -0.49896 | -0.47607 | -0.53558 | -0.54016 | -0.58594 | -0.68207 | -0.74616 | 0.64545 | 0.51727 | -122.4838 | 0.78735 | 0.71411 | 0.19684 | -122.5388 | -0.036621 | -0.10071 | -123.1338 | 0.14648 | 0.10986 | 0.21057 | -123.1796 | 0.75531 | 0.70038 | 0.70038 | -122.7219 | 0.10529 | 0.05951 | 0.16937 | -123.3398
1112.8438 | 123.3536 | -0.65002 | 122.5983 | -0.10703 | 0.14017 | 0.1536 | 0.08679 | 0.11239 | -0.010566 | 0.03129 | -0.28888 | 0.17632 | -0.0021099 | 0.17421 | 0.015017 | -0.027656 | 0.07782 | 0.16937 | 0.050354 | 0.07782 | 0.12817 | 0.013733 | -0.13275 | -0.49896 | -0.48981 | -0.55847 | -0.54016 | -0.58594 | -0.67749 | -0.72327 | 0.66376 | 0.51727 | -122.4701 | 0.8194 | 0.72784 | 0.21057 | -122.5204 | -0.027466 | -0.073243 | -123.1384 | 0.15106 | 0.091552 | 0.1648 | -123.1842 | 0.7782 | 0.72784 | 0.70038 | -122.731 | 0.10986 | 0.064087 | 0.16022 | -123.3215
1113.9062 | 123.3536 | -0.64087 | 122.5983 | 0.060816 | 0.12949 | 0.14292 | 0.066496 | 0.11346 | -0.010566 | 0.032358 | -0.029479 | 0.16457 | -0.0053139 | 0.17955 | 0.0054039 | -0.021247 | 0.004578 | 0.09613 | 0.009155 | 0.054932 | 0.10986 | 0.004578 | -0.11902 | -0.53558 | -0.53101 | -0.5722 | -0.54016 | -0.56763 | -0.67749 | -0.72327 | 0.64545 | 0.52185 | -122.4884 | 0.737 | 0.6958 | 0.17395 | -122.5937 | -0.036621 | -0.082398 | -123.1384 | 0.10529 | 0.068664 | 0.15106 | -123.1659 | 0.75073 | 0.64545 | 0.65002 | -122.7173 | 0.10071 | 0.073242 | 0.10986 | -123.3215
1114.8438 | 123.2437 | -0.67749 | 122.644 | -0.27488 | 0.17008 | 0.14933 | 0.071836 | 0.10065 | 0.016137 | 0.034494 | -0.5788 | 0.18594 | -0.011723 | 0.18596 | 0.01288 | -0.038337 | -0.013733 | 0.018311 | -0.082397 | -0.013733 | 0.15106 | -0.041199 | -0.17395 | -0.6134 | -0.6134 | -0.69122 | -0.47607 | -0.52643 | -0.71411 | -0.78735 | 0.63629 | 0.50354 | -122.493 | 0.6958 | 0.66376 | 0.16022 | -122.6578 | -0.036621 | -0.10986 | -123.1201 | 0.064087 | -0.013733 | 0.096131 | -123.1705 | 0.82855 | 0.66376 | 0.59509 | -122.818 | 0.20142 | 0.15106 | 0.064087 | -123.4314
1115.9062 | 123.3627 | -0.6546 | 122.6166 | 0.16763 | 0.15833 | 0.13865 | 0.064359 | 0.11239 | -0.0052253 | 0.024881 | -0.044738 | 0.1806 | 0.01498 | 0.17742 | -0.0020731 | -0.02552 | 0.004578 | 0.07782 | 0.013733 | 0.036621 | 0.12817 | 0 | -0.1236 | -0.55389 | -0.54016 | -0.59052 | -0.52643 | -0.5722 | -0.66376 | -0.737 | 0.6546 | 0.53101 | -122.4884 | 0.73242 | 0.69122 | 0.16022 | -122.612 | -0.009155 | -0.082398 | -123.143 | 0.10071 | 0.064087 | 0.14648 | -123.1888 | 0.78278 | 0.65918 | 0.66834 | -122.7402 | 0.12817 | 0.082397 | 0.11444 | -123.3536
1116.8438 | 123.3353 | -0.61798 | 122.6074 | -0.21384 | 0.15513 | 0.13437 | 0.070768 | 0.10278 | -0.0094983 | 0.018472 | -0.30414 | 0.17098 | -0.014927 | 0.1678 | 0.0043349 | -0.035133 | 0.07782 | 0.14648 | 0.045776 | 0.07782 | 0.11444 | 0.009155 | -0.12817 | -0.49896 | -0.48065 | -0.55847 | -0.56305 | -0.56763 | -0.66834 | -0.72327 | 0.62714 | 0.48981 | -122.493 | 0.76446 | 0.6958 | 0.20599 | -122.5296 | -0.050354 | -0.10529 | -123.1705 | 0.11902 | 0.059509 | 0.1648 | -123.175 | 0.73242 | 0.6958 | 0.66376 | -122.7356 | 0.054932 | 0.050354 | 0.13733 | -123.3307
1117.9062 | 123.3948 | -0.62714 | 122.5983 | 0.015039 | 0.14765 | 0.14399 | 0.063291 | 0.096373 | -0.0084293 | 0.017404 | -0.2431 | 0.17526 | -0.010654 | 0.1913 | 0.019289 | -0.029792 | 0.07782 | 0.17853 | 0.059509 | 0.091553 | 0.1236 | 0.022888 | -0.11902 | -0.50354 | -0.46234 | -0.52643 | -0.54016 | -0.56763 | -0.66834 | -0.737 | 0.65002 | 0.50812 | -122.4747 | 0.80566 | 0.71869 | 0.21057 | -122.5204 | -0.041199 | -0.10986 | -123.1384 | 0.1236 | 0.10071 | 0.21057 | -123.1659 | 0.75073 | 0.70496 | 0.68665 | -122.7173 | 0.086975 | 0.059509 | 0.1648 | -123.3353
1118.8438 | 123.3765 | -0.62714 | 122.6028 | -0.10703 | 0.12095 | 0.14933 | 0.076109 | 0.10065 | -0.0073613 | 0.025949 | -0.30414 | 0.18273 | -0.014927 | 0.18276 | 0.018221 | -0.036201 | 0.064087 | 0.16022 | 0.068665 | 0.086975 | 0.11444 | 0.013733 | -0.11902 | -0.50354 | -0.48065 | -0.54932 | -0.52643 | -0.58136 | -0.69122 | -0.75531 | 0.64087 | 0.50812 | -122.4884 | 0.78735 | 0.71411 | 0.20599 | -122.5388 | -0.064087 | -0.12817 | -123.1293 | 0.1236 | 0.07782 | 0.20599 | -123.1842 | 0.74158 | 0.69122 | 0.6958 | -122.7219 | 0.10071 | 0.045776 | 0.14648 | -123.3582
1119.9219 | 123.3353 | -0.64545 | 122.5983 | 0.4728 | 0.16154 | 0.1536 | 0.087858 | 0.10812 | 0.0086597 | 0.038766 | 0.33673 | 0.17846 | 0.0032311 | 0.17955 | 0.011812 | -0.03086 | 0.07782 | 0.11902 | 0.045776 | 0.059509 | 0.11444 | 0.018311 | -0.11444 | -0.48981 | -0.53101 | -0.5722 | -0.52643 | -0.56305 | -0.65918 | -0.73242 | 0.66376 | 0.53101 | -122.4838 | 0.76447 | 0.70496 | 0.17395 | -122.5204 | -0.013733 | -0.086975 | -123.1247 | 0.15564 | 0.073242 | 0.16022 | -123.1613 | 0.75989 | 0.72327 | 0.69122 | -122.7127 | 0.11902 | 0.082398 | 0.11444 | -123.3307
1120.8438 | 123.2758 | -0.68207 | 122.6257 | -0.24436 | 0.14338 | 0.14612 | 0.083585 | 0.098509 | 0.017205 | 0.030222 | -0.54828 | 0.19128 | -0.011723 | 0.1881 | 0.018221 | -0.038337 | -0.004578 | -0.009155 | -0.09613 | 0.013733 | 0.1831 | -0.050354 | -0.17853 | -0.60425 | -0.6134 | -0.69122 | -0.46692 | -0.52643 | -0.70496 | -0.76446 | 0.63171 | 0.50354 | -122.4426 | 0.67291 | 0.6958 | 0.19226 | -122.6303 | -0.022888 | -0.082397 | -123.0927 | 0.07782 | -0.009155 | 0.073242 | -123.1522 | 0.86517 | 0.67749 | 0.58594 | -122.8043 | 0.21515 | 0.15564 | 0.068665 | -123.3902
1121.9062 | 123.3627 | -0.64087 | 122.6074 | -0.045996 | 0.12415 | 0.15467 | 0.080381 | 0.10492 | -0.0041573 | 0.022745 | -0.075256 | 0.1838 | -0.022404 | 0.18062 | 0.0064719 | -0.026588 | 0.032043 | 0.10529 | 0.027466 | 0.064087 | 0.11444 | 0.013733 | -0.11444 | -0.51727 | -0.49896 | -0.55389 | -0.51727 | -0.56305 | -0.66376 | -0.737 | 0.6546 | 0.52643 | -122.493 | 0.74616 | 0.70496 | 0.17853 | -122.5754 | -0.022888 | -0.096131 | -123.1247 | 0.1236 | 0.086975 | 0.18311 | -123.1705 | 0.75531 | 0.67291 | 0.66834 | -122.7219 | 0.1236 | 0.07782 | 0.14191 | -123.3444
1122.8438 | 123.3215 | -0.64545 | 122.5937 | -0.24436 | 0.13056 | 0.15146 | 0.07504 | 0.11453 | 0.0033197 | 0.022745 | -0.47198 | 0.18487 | 0.0085721 | 0.19024 | 0.0043349 | -0.038337 | 0.045776 | 0.13733 | 0.036621 | 0.082397 | 0.11444 | -0.004578 | -0.11902 | -0.52643 | -0.49896 | -0.57678 | -0.48523 | -0.56305 | -0.66376 | -0.74616 | 0.64087 | 0.52643 | -122.4792 | 0.78278 | 0.72784 | 0.20142 | -122.5479 | -0.01831 | -0.10071 | -123.0789 | 0.11902 | 0.068665 | 0.16937 | -123.1567 | 0.75989 | 0.69122 | 0.68207 | -122.7127 | 0.16022 | 0.082398 | 0.14648 | -123.3398
1123.9062 | 123.3398 | -0.64087 | 122.6212 | 0.19814 | 0.12308 | 0.15253 | 0.070768 | 0.10599 | -0.0084293 | 0.021677 | -0.01422 | 0.1806 | -0.0053139 | 0.18917 | 0.0054039 | -0.032996 | 0 | 0.082397 | 0.009155 | 0.054932 | 0.13275 | -0.004578 | -0.10986 | -0.5127 | -0.54016 | -0.55847 | -0.52185 | -0.56305 | -0.65002 | -0.73242 | 0.63629 | 0.53101 | -122.4884 | 0.72327 | 0.6958 | 0.16479 | -122.6212 | -0.009155 | -0.091553 | -123.143 | 0.12817 | 0.082397 | 0.17395 | -123.1842 | 0.77362 | 0.64087 | 0.65002 | -122.731 | 0.11902 | 0.07782 | 0.10071 | -123.3536
1124.8438 | 123.2529 | -0.67291 | 122.644 | 0.2134 | 0.18397 | 0.12263 | 0.099607 | 0.10492 | 0.041772 | 0.034494 | -0.16681 | 0.20089 | 0.01498 | 0.18596 | 0.026766 | -0.032996 | 0.022888 | 0.009155 | -0.068665 | 0.009155 | 0.13733 | -0.027466 | -0.15106 | -0.60425 | -0.60883 | -0.6958 | -0.48523 | -0.52643 | -0.68207 | -0.76446 | 0.64545 | 0.52185 | -122.5067 | 0.68207 | 0.68207 | 0.16022 | -122.6212 | -0.009155 | -0.091552 | -123.1293 | 0.068665 | -0.022888 | 0.068664 | -123.1705 | 0.81024 | 0.6958 | 0.60425 | -122.7951 | 0.18768 | 0.14648 | 0.064087 | -123.4085
1125.9062 | 123.3536 | -0.61798 | 122.5754 | 0.51858 | 0.17115 | 0.14399 | 0.088926 | 0.11026 | 0.0022517 | 0.028085 | 0.2757 | 0.19448 | -0.0010409 | 0.18276 | 0.018221 | -0.031928 | 0.082397 | 0.11902 | 0.059509 | 0.073242 | 0.11902 | 0.018311 | -0.1236 | -0.48523 | -0.52185 | -0.56305 | -0.53101 | -0.5722 | -0.64087 | -0.71411 | 0.63629 | 0.49439 | -122.4564 | 0.737 | 0.69122 | 0.19684 | -122.493 | -0.022888 | -0.09613 | -123.1064 | 0.13275 | 0.054932 | 0.15106 | -123.1476 | 0.737 | 0.70038 | 0.67749 | -122.699 | 0.086975 | 0.045776 | 0.09613 | -123.2895
1126.8438 | 123.3948 | -0.61798 | 122.5937 | 0.015039 | 0.13804 | 0.14185 | 0.071836 | 0.11667 | -0.014838 | 0.020609 | -0.22784 | 0.17739 | -0.015995 | 0.16994 | 0.0054039 | -0.032996 | 0.068665 | 0.13275 | 0.032043 | 0.091553 | 0.1236 | 0.013733 | -0.10529 | -0.4715 | -0.4303 | -0.51727 | -0.5127 | -0.55847 | -0.68207 | -0.71869 | 0.63171 | 0.5127 | -122.4701 | 0.75073 | 0.70953 | 0.19684 | -122.525 | -0.064087 | -0.10071 | -123.1064 | 0.14648 | 0.10071 | 0.20142 | -123.1522 | 0.74158 | 0.68665 | 0.65002 | -122.699 | 0.10529 | 0.059509 | 0.18768 | -123.3124
1127.9062 | 123.3444 | -0.65002 | 122.58 | 0.27444 | 0.12522 | 0.15681 | 0.049406 | 0.11239 | -0.0073613 | 0.017404 | 0.12311 | 0.1806 | -0.0074499 | 0.18276 | 0.015017 | -0.026588 | 0.013733 | 0.068665 | -0.013733 | 0.036621 | 0.13733 | 0.018311 | -0.15564 | -0.54932 | -0.54016 | -0.59509 | -0.5127 | -0.56763 | -0.68665 | -0.74158 | 0.66834 | 0.49438 | -122.4426 | 0.71869 | 0.68665 | 0.19226 | -122.5662 | -0.036622 | -0.091553 | -123.0927 | 0.10071 | 0.054931 | 0.14648 | -123.1476 | 0.78735 | 0.66376 | 0.63629 | -122.7356 | 0.13733 | 0.082397 | 0.10986 | -123.3215
1128.8438 | 123.349 | -0.65918 | 122.6074 | 0.22866 | 0.14338 | 0.14292 | 0.066496 | 0.095305 | -0.0041573 | 0.021677 | 0.062074 | 0.18914 | -0.0053139 | 0.18703 | 0.010744 | -0.024451 | 0.018311 | 0.082397 | -0.018311 | 0.032043 | 0.12817 | 0 | -0.10986 | -0.54474 | -0.54016 | -0.57678 | -0.51727 | -0.56763 | -0.6546 | -0.72784 | 0.65918 | 0.54932 | -122.4792 | 0.74158 | 0.69122 | 0.14191 | -122.5891 | 0.004578 | -0.068664 | -123.1247 | 0.11444 | 0.082398 | 0.15106 | -123.175 | 0.78735 | 0.67749 | 0.64087 | -122.7173 | 0.14191 | 0.091553 | 0.11902 | -123.3353
1129.9219 | 123.317 | -0.6546 | 122.6257 | 0.44228 | 0.17115 | 0.13651 | 0.080381 | 0.11133 | 0.040704 | 0.032358 | 0.16888 | 0.18487 | -0.0053139 | 0.18489 | 0.021425 | -0.046882 | 0.009155 | -0.009155 | -0.10071 | -0.018311 | 0.15106 | -0.027466 | -0.14191 | -0.56763 | -0.62256 | -0.67291 | -0.49439 | -0.54016 | -0.67291 | -0.74158 | 0.62714 | 0.5127 | -122.4747 | 0.64545 | 0.63629 | 0.1236 | -122.6166 | -0.018311 | -0.086975 | -123.1201 | 0.086975 | -0.018311 | 0.068664 | -123.1659 | 0.80566 | 0.66376 | 0.55389 | -122.7676 | 0.16022 | 0.11444 | 0.032043 | -123.3673
1130.8438 | 123.3673 | -0.64087 | 122.6074 | 0.4728 | 0.14658 | 0.13651 | 0.078245 | 0.11026 | -0.00095325 | 0.032358 | 0.30621 | 0.18914 | -0.0053139 | 0.19024 | 0.021425 | -0.027656 | 0.086975 | 0.11902 | 0.045776 | 0.054932 | 0.10986 | 0.022888 | -0.10986 | -0.47607 | -0.52643 | -0.55389 | -0.5127 | -0.56305 | -0.64087 | -0.72327 | 0.66376 | 0.53101 | -122.4976 | 0.75989 | 0.6958 | 0.16479 | -122.5204 | 0 | -0.082398 | -123.1201 | 0.1648 | 0.086975 | 0.16937 | -123.1705 | 0.75073 | 0.72784 | 0.68665 | -122.7173 | 0.12817 | 0.07782 | 0.11444 | -123.3307
1131.9062 | 123.3765 | -0.62256 | 122.6166 | 0.030298 | 0.13483 | 0.14612 | 0.073972 | 0.099578 | -0.010566 | 0.021677 | -0.34991 | 0.1838 | -0.0095859 | 0.18489 | 0.0064719 | -0.026588 | 0.07782 | 0.16022 | 0.054932 | 0.07782 | 0.11444 | 0.013733 | -0.13275 | -0.48523 | -0.45319 | -0.53558 | -0.50812 | -0.56305 | -0.6546 | -0.71869 | 0.63629 | 0.48981 | -122.5021 | 0.78278 | 0.70038 | 0.21057 | -122.5388 | -0.032043 | -0.09613 | -123.1247 | 0.13733 | 0.086976 | 0.18311 | -123.1796 | 0.737 | 0.70038 | 0.67749 | -122.7493 | 0.11444 | 0.05951 | 0.16937 | -123.3353
1132.8438 | 123.3353 | -0.62714 | 122.6074 | 0.4728 | 0.14017 | 0.15253 | 0.068632 | 0.098509 | -0.0094983 | 0.018472 | 0.26044 | 0.17632 | 0.0021631 | 0.18703 | 0.017153 | -0.024451 | 0.041199 | 0.10529 | 0.013733 | 0.032043 | 0.11902 | 0 | -0.12817 | -0.52643 | -0.54474 | -0.59052 | -0.50354 | -0.54474 | -0.64545 | -0.737 | 0.62714 | 0.49896 | -122.4884 | 0.73242 | 0.65918 | 0.16022 | -122.5662 | -0.018311 | -0.10986 | -123.111 | 0.10071 | 0.036621 | 0.14648 | -123.1522 | 0.74616 | 0.66834 | 0.64087 | -122.7356 | 0.1236 | 0.082397 | 0.082397 | -123.3444
1133.9062 | 123.2483 | -0.6546 | 122.6349 | 0.51858 | 0.19465 | 0.13865 | 0.062223 | 0.11026 | 0.032159 | 0.037698 | 0.077332 | 0.19662 | 2.7137e-05 | 0.17101 | 0.026766 | -0.042609 | 0.018311 | -0.032043 | -0.09613 | -0.004578 | 0.17395 | -0.022888 | -0.13275 | -0.58594 | -0.65002 | -0.69122 | -0.48065 | -0.52185 | -0.69122 | -0.74616 | 0.63171 | 0.52185 | -122.4609 | 0.62256 | 0.65002 | 0.12817 | -122.6166 | -0.036621 | -0.091553 | -123.1155 | 0.068665 | -0.036621 | 0.054932 | -123.1567 | 0.82855 | 0.67291 | 0.55847 | -122.7676 | 0.17395 | 0.13275 | 0.004578 | -123.381
1134.8438 | 123.2941 | -0.6546 | 122.644 | -0.12229 | 0.16474 | 0.14292 | 0.08679 | 0.094237 | 0.02575 | 0.038766 | -0.25836 | 0.187 | 0.0032311 | 0.18703 | 0.028902 | -0.04795 | 0.050354 | 0.041199 | -0.032043 | 0.032043 | 0.16022 | -0.032043 | -0.16479 | -0.54474 | -0.54932 | -0.62714 | -0.48523 | -0.51727 | -0.67291 | -0.72784 | 0.62256 | 0.48981 | -122.4838 | 0.6958 | 0.68665 | 0.19684 | -122.5937 | -0.018311 | -0.073242 | -123.1293 | 0.10986 | 0.027466 | 0.10071 | -123.1613 | 0.81482 | 0.70496 | 0.62256 | -122.8088 | 0.16937 | 0.13733 | 0.10529 | -123.3719
1135.9062 | 123.2391 | -0.67291 | 122.6349 | 0.42703 | 0.17649 | 0.12476 | 0.083585 | 0.1156 | 0.019342 | 0.03129 | 0.16888 | 0.19555 | -0.0095859 | 0.19558 | 0.013948 | -0.037269 | -0.013733 | -0.018311 | -0.09613 | -0.013733 | 0.16022 | -0.041199 | -0.15564 | -0.59509 | -0.64545 | -0.68207 | -0.47607 | -0.51727 | -0.67749 | -0.75531 | 0.63171 | 0.51727 | -122.4747 | 0.6546 | 0.65918 | 0.14191 | -122.6486 | -0.004577 | -0.082397 | -123.111 | 0.07782 | -0.009155 | 0.073242 | -123.1522 | 0.83313 | 0.65918 | 0.57678 | -122.7905 | 0.19684 | 0.15564 | 0.027466 | -123.3902
1136.8438 | 123.381 | -0.62256 | 122.5983 | 0.48806 | 0.17542 | 0.14612 | 0.067564 | 0.10171 | 0.0097277 | 0.033426 | 0.33673 | 0.18273 | -0.0085179 | 0.17955 | 0.019289 | -0.028724 | 0.054932 | 0.11444 | 0.050354 | 0.073242 | 0.10529 | 0.013733 | -0.12817 | -0.48523 | -0.49439 | -0.54474 | -0.54016 | -0.55847 | -0.66376 | -0.71411 | 0.63629 | 0.49438 | -122.493 | 0.737 | 0.6958 | 0.20142 | -122.5433 | -0.041198 | -0.091552 | -123.1384 | 0.13733 | 0.07782 | 0.16937 | -123.1567 | 0.72784 | 0.67749 | 0.67291 | -122.7264 | 0.082398 | 0.064087 | 0.12817 | -123.3124
1137.9062 | 123.2712 | -0.66376 | 122.6166 | 0.48806 | 0.17115 | 0.1301 | 0.073972 | 0.11346 | 0.015069 | 0.034494 | 0.26044 | 0.19341 | 0.0053671 | 0.1678 | 0.027834 | -0.029792 | -0.009155 | -0.018311 | -0.09613 | -0.018311 | 0.15106 | -0.013733 | -0.15564 | -0.5722 | -0.62256 | -0.64545 | -0.49439 | -0.52643 | -0.67291 | -0.74616 | 0.65002 | 0.50812 | -122.4655 | 0.64545 | 0.64545 | 0.13733 | -122.6257 | -0.009156 | -0.082398 | -123.111 | 0.091552 | 0.01831 | 0.10071 | -123.143 | 0.81482 | 0.6546 | 0.56763 | -122.7722 | 0.16937 | 0.13733 | 0.041198 | -123.3627
1138.8438 | 123.3398 | -0.62256 | 122.5937 | 0.45754 | 0.15833 | 0.13865 | 0.066496 | 0.12628 | -0.00095325 | 0.022745 | 0.35199 | 0.17953 | -0.011723 | 0.18276 | 0.011812 | -0.03086 | 0.059509 | 0.10986 | 0.032043 | 0.064087 | 0.10071 | 0.022888 | -0.10986 | -0.50812 | -0.5127 | -0.56305 | -0.52643 | -0.56305 | -0.67291 | -0.71869 | 0.64545 | 0.5127 | -122.493 | 0.73242 | 0.68665 | 0.17395 | -122.5342 | -0.050354 | -0.09613 | -123.1201 | 0.11444 | 0.05951 | 0.15564 | -123.1567 | 0.72327 | 0.68207 | 0.6546 | -122.7036 | 0.096131 | 0.05951 | 0.10986 | -123.3124
1139.9219 | 123.3719 | -0.60883 | 122.58 | 0.53384 | 0.15726 | 0.14185 | 0.072904 | 0.10705 | 0.017205 | 0.018472 | 0.42828 | 0.19234 | -0.0031779 | 0.17635 | 0.022493 | -0.019111 | 0.086975 | 0.10986 | 0.045776 | 0.07782 | 0.10986 | 0.013733 | -0.12817 | -0.48981 | -0.49896 | -0.54932 | -0.49439 | -0.55847 | -0.65918 | -0.72784 | 0.62256 | 0.48065 | -122.4701 | 0.71869 | 0.68665 | 0.20599 | -122.493 | -0.050354 | -0.11902 | -123.0743 | 0.11902 | 0.05951 | 0.17853 | -123.1384 | 0.71869 | 0.6958 | 0.6546 | -122.7081 | 0.11444 | 0.050354 | 0.10986 | -123.3078
1140.8438 | 123.2895 | -0.66834 | 122.6212 | 0.51858 | 0.16795 | 0.13865 | 0.077177 | 0.1156 | 0.030023 | 0.035562 | 0.1994 | 0.19982 | 0.0053671 | 0.19024 | 0.018221 | -0.019111 | 0.018311 | -0.036621 | -0.10071 | -0.004578 | 0.15106 | -0.018311 | -0.14648 | -0.58594 | -0.62714 | -0.65002 | -0.49896 | -0.53101 | -0.65918 | -0.72784 | 0.65002 | 0.52185 | -122.4701 | 0.63171 | 0.66376 | 0.14191 | -122.6028 | 0.009155 | -0.059509 | -123.1201 | 0.082398 | 0.018311 | 0.07782 | -123.1522 | 0.8194 | 0.68665 | 0.56763 | -122.7676 | 0.16937 | 0.13733 | 0.041199 | -123.349
1141.9062 | 123.2346 | -0.66834 | 122.6486 | 0.35073 | 0.17649 | 0.14078 | 0.068632 | 0.10812 | 0.02575 | 0.044107 | 0.10785 | 0.20409 | 2.7137e-05 | 0.17849 | 0.034243 | -0.027656 | 0 | -0.041199 | -0.10071 | -0.013733 | 0.1831 | -0.022888 | -0.16022 | -0.6134 | -0.63629 | -0.70038 | -0.4715 | -0.5127 | -0.68207 | -0.74616 | 0.64545 | 0.50812 | -122.4655 | 0.62714 | 0.6546 | 0.14648 | -122.6486 | -0.013733 | -0.07782 | -123.1201 | 0.054932 | -0.032043 | 0.045777 | -123.1613 | 0.85144 | 0.66834 | 0.56763 | -122.8088 | 0.19684 | 0.15564 | 0.032043 | -123.3948
1142.8438 | 123.3032 | -0.6546 | 122.6257 | 0.44228 | 0.16901 | 0.14506 | 0.068632 | 0.10705 | 0.015069 | 0.028085 | 0.1994 | 0.19021 | -0.0010409 | 0.17955 | 0.026766 | -0.029792 | -0.009155 | -0.018311 | -0.091553 | -0.004578 | 0.14648 | -0.013733 | -0.17395 | -0.59967 | -0.63629 | -0.66376 | -0.48523 | -0.54016 | -0.66376 | -0.73242 | 0.64087 | 0.48065 | -122.4792 | 0.63629 | 0.65002 | 0.16937 | -122.6349 | -0.009155 | -0.07782 | -123.111 | 0.054932 | -0.009155 | 0.068665 | -123.1659 | 0.80109 | 0.64545 | 0.56305 | -122.7997 | 0.16937 | 0.11444 | 0.01831 | -123.3582
1143.9062 | 123.2666 | -0.65918 | 122.6349 | 0.091333 | 0.17863 | 0.13544 | 0.088926 | 0.10065 | 0.024682 | 0.033426 | -0.01422 | 0.19769 | 0.0053671 | 0.17742 | 0.025698 | -0.037269 | 0.036621 | 0.004578 | -0.050354 | 0.022888 | 0.14191 | -0.013733 | -0.14648 | -0.59052 | -0.59052 | -0.66376 | -0.46692 | -0.51727 | -0.66834 | -0.75073 | 0.64545 | 0.5127 | -122.493 | 0.66376 | 0.68207 | 0.16937 | -122.5983 | -0.009155 | -0.091552 | -123.1018 | 0.068665 | -0.004577 | 0.086975 | -123.1522 | 0.80109 | 0.6958 | 0.60883 | -122.7814 | 0.19226 | 0.14191 | 0.068665 | -123.3856
1144.8438 | 123.2803 | -0.6546 | 122.6532 | -0.015478 | 0.18076 | 0.14292 | 0.071836 | 0.10278 | 0.012933 | 0.035562 | -0.16681 | 0.19128 | -0.0031779 | 0.19451 | 0.028902 | -0.037269 | 0.041199 | 0.054932 | -0.036621 | 0.022888 | 0.10986 | -0.018311 | -0.16022 | -0.55389 | -0.54474 | -0.65002 | -0.48065 | -0.53101 | -0.65002 | -0.72784 | 0.63629 | 0.49439 | -122.5433 | 0.70953 | 0.67749 | 0.1831 | -122.612 | 0.004578 | -0.073242 | -123.1339 | 0.10071 | 0.004578 | 0.07782 | -123.1842 | 0.76447 | 0.6958 | 0.61798 | -122.8134 | 0.17395 | 0.1236 | 0.10986 | -123.381
1145.9062 | 123.2712 | -0.65918 | 122.6349 | 0.10659 | 0.19572 | 0.14292 | 0.071836 | 0.10812 | 0.021478 | 0.043039 | 0.0010378 | 0.19555 | 0.0032311 | 0.18383 | 0.020357 | -0.028724 | 0.022888 | 0.032043 | -0.041199 | 0.027466 | 0.13733 | -0.018311 | -0.17395 | -0.58594 | -0.59052 | -0.64545 | -0.48523 | -0.51727 | -0.65002 | -0.76904 | 0.64087 | 0.48523 | -122.4976 | 0.69122 | 0.68665 | 0.20142 | -122.612 | 0.009156 | -0.10986 | -123.1201 | 0.073243 | 0.013733 | 0.1236 | -123.1522 | 0.79651 | 0.68207 | 0.61798 | -122.8088 | 0.17395 | 0.14191 | 0.068665 | -123.4039
1146.8438 | 123.262 | -0.65002 | 122.6624 | 0.076074 | 0.19785 | 0.13972 | 0.071836 | 0.10705 | 0.019342 | 0.035562 | -0.090514 | 0.18166 | 0.017117 | 0.18169 | 0.021425 | -0.031928 | 0.004578 | 0.009155 | -0.059509 | 0.032043 | 0.14191 | -0.013733 | -0.16479 | -0.59967 | -0.58136 | -0.67291 | -0.48065 | -0.52643 | -0.68207 | -0.74616 | 0.63629 | 0.48523 | -122.5204 | 0.65918 | 0.68207 | 0.19684 | -122.6578 | -0.032044 | -0.096131 | -123.143 | 0.050354 | -0.022889 | 0.073242 | -123.1888 | 0.79193 | 0.6546 | 0.59052 | -122.8271 | 0.16937 | 0.1236 | 0.068664 | -123.4085
1147.8438 | 123.262 | -0.67291 | 122.6532 | 0.2897 | 0.17649 | 0.13972 | 0.083585 | 0.11346 | 0.014001 | 0.038766 | 0.22992 | 0.187 | 0.017117 | 0.16994 | 0.0064719 | -0.024451 | -0.068665 | -0.059509 | -0.12817 | -0.013733 | 0.13733 | -0.018311 | -0.16937 | -0.63171 | -0.64087 | -0.6958 | -0.48523 | -0.52643 | -0.67749 | -0.74616 | 0.6546 | 0.50354 | -122.5159 | 0.6134 | 0.65918 | 0.15564 | -122.7219 | -0.004577 | -0.073242 | -123.1384 | 0.041199 | -0.022888 | 0.050354 | -123.1796 | 0.81024 | 0.60425 | 0.54474 | -122.8226 | 0.18768 | 0.14648 | 0.032044 | -123.3994
1148.9062 | 123.3536 | -0.63629 | 122.6395 | 0.16763 | 0.12949 | 0.17069 | 0.059019 | 0.10065 | -0.028724 | 0.021677 | 0.16888 | 0.18273 | 0.0032311 | 0.18917 | 0.0075399 | -0.016975 | -0.027466 | 0.036621 | -0.013733 | 0.050354 | 0.12817 | -0.022888 | -0.12817 | -0.56763 | -0.53101 | -0.56305 | -0.52185 | -0.54016 | -0.63629 | -0.72327 | 0.6134 | 0.50812 | -122.5113 | 0.67291 | 0.68665 | 0.17853 | -122.6669 | 0 | -0.086975 | -123.1613 | 0.068665 | 0.073243 | 0.16022 | -123.1796 | 0.76447 | 0.60883 | 0.62256 | -122.7676 | 0.11444 | 0.096131 | 0.10529 | -123.3627
1149.8438 | 123.2803 | -0.6546 | 122.6578 | -0.19858 | 0.1797 | 0.15146 | 0.10067 | 0.10492 | 0.018273 | 0.032358 | -0.42621 | 0.1806 | 0.0085721 | 0.17955 | 0.013948 | -0.032996 | -0.004578 | -0.009155 | -0.082397 | 0.018311 | 0.16022 | -0.022888 | -0.16479 | -0.63629 | -0.59052 | -0.65002 | -0.4715 | -0.51727 | -0.67749 | -0.74158 | 0.63171 | 0.48981 | -122.4976 | 0.64545 | 0.67291 | 0.18311 | -122.6624 | -0.022888 | -0.086975 | -123.1293 | 0.01831 | 0.004578 | 0.091553 | -123.175 | 0.81482 | 0.65002 | 0.57221 | -122.8226 | 0.18311 | 0.13733 | 0.064087 | -123.3994
1150.9062 | 123.2666 | -0.67291 | 122.6715 | -0.39695 | 0.14124 | 0.15681 | 0.064359 | 0.10278 | -0.0020213 | 0.021677 | -0.41095 | 0.1806 | -0.0021099 | 0.18917 | 0.016085 | -0.026588 | -0.032043 | 0 | -0.082397 | -0.022888 | 0.16022 | -0.032043 | -0.1831 | -0.63629 | -0.60883 | -0.67291 | -0.44403 | -0.52185 | -0.67749 | -0.76446 | 0.64087 | 0.48981 | -122.5113 | 0.67291 | 0.65002 | 0.16022 | -122.7036 | -0.004577 | -0.091552 | -123.1155 | 0.036621 | 0 | 0.091552 | -123.1934 | 0.83313 | 0.64087 | 0.59052 | -122.8546 | 0.22888 | 0.15106 | 0.064087 | -123.436
1151.8438 | 123.2849 | -0.66376 | 122.6624 | -0.24436 | 0.17329 | 0.15681 | 0.070768 | 0.10385 | -0.0020213 | 0.020609 | -0.38043 | 0.19234 | 0.0096401 | 0.17742 | 0.0075399 | -0.035133 | -0.022888 | -0.013733 | -0.091553 | -0.004578 | 0.17395 | -0.036621 | -0.16937 | -0.63171 | -0.59052 | -0.67291 | -0.46692 | -0.50354 | -0.68665 | -0.737 | 0.62714 | 0.49438 | -122.4884 | 0.65002 | 0.65918 | 0.16479 | -122.6852 | -0.022889 | -0.073243 | -123.1293 | 0.032043 | -0.009156 | 0.064087 | -123.1659 | 0.83771 | 0.64087 | 0.5722 | -122.8317 | 0.19684 | 0.16022 | 0.073242 | -123.3994
1152.9062 | 123.2574 | -0.65918 | 122.6761 | -0.25962 | 0.15406 | 0.14826 | 0.07504 | 0.10919 | -0.00095325 | 0.022745 | -0.41095 | 0.18273 | -0.0031779 | 0.17528 | 0.0064719 | -0.022315 | -0.045776 | -0.013733 | -0.082397 | -0.004578 | 0.15564 | -0.041199 | -0.17395 | -0.62714 | -0.61798 | -0.68207 | -0.45776 | -0.49439 | -0.67291 | -0.74616 | 0.61798 | 0.48523 | -122.5204 | 0.64545 | 0.6546 | 0.16937 | -122.7219 | -0.013733 | -0.086975 | -123.1338 | 0.032044 | -0.022888 | 0.064087 | -123.1705 | 0.81482 | 0.6134 | 0.57678 | -122.85 | 0.20142 | 0.16479 | 0.041199 | -123.4222
1153.8438 | 123.2529 | -0.65918 | 122.6715 | -0.19858 | 0.16688 | 0.14933 | 0.076109 | 0.11133 | -0.0062933 | 0.024881 | -0.44147 | 0.1806 | 0.0042991 | 0.18596 | 0.023561 | -0.042609 | -0.036621 | 0 | -0.10071 | -0.004578 | 0.16479 | -0.022888 | -0.16937 | -0.63171 | -0.60883 | -0.65918 | -0.45776 | -0.51727 | -0.66834 | -0.75073 | 0.63629 | 0.48981 | -122.5067 | 0.65918 | 0.6546 | 0.16479 | -122.7081 | -0.009155 | -0.091552 | -123.1293 | 0.027466 | 0 | 0.091552 | -123.1888 | 0.82398 | 0.62256 | 0.55847 | -122.8409 | 0.20142 | 0.14191 | 0.050354 | -123.4222
1154.9062 | 123.2666 | -0.67749 | 122.6669 | -0.32065 | 0.15513 | 0.1269 | 0.080381 | 0.10065 | 0.0054557 | 0.018472 | -0.71613 | 0.18487 | 0.020321 | 0.17421 | 0.0032669 | -0.029792 | -0.027466 | 0.027466 | -0.064087 | 0.013733 | 0.15564 | -0.018311 | -0.16022 | -0.6134 | -0.58136 | -0.65002 | -0.48065 | -0.53558 | -0.67291 | -0.76446 | 0.65918 | 0.51727 | -122.5113 | 0.70496 | 0.69122 | 0.17395 | -122.6944 | 0.004577 | -0.086975 | -123.1476 | 0.064087 | 0.027466 | 0.11444 | -123.2025 | 0.83313 | 0.65002 | 0.6134 | -122.8271 | 0.19684 | 0.14191 | 0.09613 | -123.4314
1155.8438 | 123.262 | -0.67749 | 122.6578 | -0.32065 | 0.15192 | 0.13972 | 0.081449 | 0.11133 | -0.0041573 | 0.030222 | 0.046815 | 0.187 | -0.0095859 | 0.17742 | 0.0054039 | -0.023383 | -0.018311 | 0.009155 | -0.054932 | 0.004578 | 0.14648 | -0.032043 | -0.17395 | -0.63171 | -0.60425 | -0.66834 | -0.46692 | -0.52185 | -0.70496 | -0.76446 | 0.64545 | 0.50354 | -122.5113 | 0.68665 | 0.68207 | 0.17853 | -122.6761 | -0.027466 | -0.086975 | -123.1247 | 0.045776 | 0.009155 | 0.09613 | -123.1796 | 0.82397 | 0.65918 | 0.62256 | -122.8317 | 0.21057 | 0.15564 | 0.073242 | -123.4222
1156.9062 | 123.3719 | -0.61798 | 122.6028 | 0.56436 | 0.16367 | 0.1504 | 0.065427 | 0.11239 | 0.0086597 | 0.041971 | 0.33673 | 0.18273 | -0.0063819 | 0.17742 | 0.013948 | -0.022315 | 0.059509 | 0.11902 | 0.036621 | 0.064087 | 0.10986 | 0 | -0.1236 | -0.49439 | -0.50354 | -0.54932 | -0.52185 | -0.55389 | -0.63629 | -0.70496 | 0.61798 | 0.49439 | -122.493 | 0.737 | 0.68207 | 0.18768 | -122.5433 | -0.018311 | -0.086975 | -123.1247 | 0.1236 | 0.068665 | 0.15564 | -123.1567 | 0.72784 | 0.67749 | 0.6546 | -122.7264 | 0.09613 | 0.064087 | 0.11444 | -123.3078
1157.8438 | 123.3994 | -0.62256 | 122.6074 | -0.12229 | 0.13697 | 0.14185 | 0.073972 | 0.10278 | -0.0094983 | 0.018472 | -0.22784 | 0.16778 | -0.010654 | 0.17101 | 0.0075399 | -0.034064 | 0.086975 | 0.16479 | 0.064087 | 0.10529 | 0.10986 | 0.027466 | -0.1236 | -0.5127 | -0.46692 | -0.53558 | -0.51727 | -0.54932 | -0.62714 | -0.71869 | 0.65002 | 0.49896 | -122.4976 | 0.78735 | 0.72784 | 0.22888 | -122.5204 | -0.004577 | -0.09613 | -123.1247 | 0.10986 | 0.086976 | 0.18311 | -123.1567 | 0.73242 | 0.70953 | 0.68665 | -122.731 | 0.10529 | 0.073243 | 0.15564 | -123.3261
1158.9062 | 123.3353 | -0.62256 | 122.6257 | 0.2897 | 0.12736 | 0.15146 | 0.081449 | 0.10278 | -0.0094983 | 0.013132 | 0.046815 | 0.17098 | -0.0085179 | 0.19024 | 0.011812 | -0.02552 | 0.009155 | 0.054932 | -0.009155 | 0.036621 | 0.12817 | 0.004578 | -0.13275 | -0.56305 | -0.55389 | -0.58594 | -0.49896 | -0.55389 | -0.65002 | -0.72327 | 0.62714 | 0.48981 | -122.4976 | 0.67749 | 0.65918 | 0.16937 | -122.6166 | -0.027465 | -0.10071 | -123.1247 | 0.05951 | 0.036622 | 0.13733 | -123.1796 | 0.75073 | 0.63171 | 0.6134 | -122.7585 | 0.1236 | 0.068665 | 0.068665 | -123.349
1159.8438 | 123.3948 | -0.62714 | 122.5983 | -0.33591 | 0.14552 | 0.15574 | 0.076109 | 0.10492 | -0.0062933 | 0.0142 | -0.3194 | 0.16885 | -0.018131 | 0.16887 | 0.0011309 | -0.018043 | 0.09613 | 0.15564 | 0.064087 | 0.07782 | 0.11902 | 0.022888 | -0.11444 | -0.5127 | -0.46234 | -0.53558 | -0.50812 | -0.53558 | -0.64087 | -0.71411 | 0.65002 | 0.5127 | -122.4792 | 0.78278 | 0.70496 | 0.19226 | -122.5021 | -0.013733 | -0.086975 | -123.1064 | 0.11444 | 0.091553 | 0.17853 | -123.1339 | 0.74616 | 0.72327 | 0.69122 | -122.7127 | 0.11902 | 0.091553 | 0.1648 | -123.3124
1160.9062 | 123.3444 | -0.63629 | 122.6349 | 0.10659 | 0.13377 | 0.14292 | 0.076109 | 0.10171 | -0.0030893 | 0.016336 | 0.046815 | 0.16564 | -0.014927 | 0.17528 | 0.0086079 | -0.024451 | 0.027466 | 0.032043 | -0.009155 | 0.032043 | 0.13733 | 0.013733 | -0.11902 | -0.55389 | -0.5722 | -0.59052 | -0.50354 | -0.54932 | -0.65918 | -0.72327 | 0.65002 | 0.51727 | -122.4976 | 0.66834 | 0.66834 | 0.15106 | -122.6074 | -0.022888 | -0.086975 | -123.1384 | 0.082398 | 0.045777 | 0.13275 | -123.1842 | 0.77362 | 0.66376 | 0.62714 | -122.7539 | 0.13275 | 0.086976 | 0.064087 | -123.3582
1161.8438 | 123.4131 | -0.60425 | 122.6212 | -0.061255 | 0.14765 | 0.1504 | 0.072904 | 0.10492 | 0.0075917 | 0.022745 | -0.28888 | 0.18166 | 0.0064351 | 0.16674 | 0.0075399 | -0.031928 | 0.10071 | 0.14191 | 0.064087 | 0.07782 | 0.12817 | 0.009155 | -0.13733 | -0.4715 | -0.45776 | -0.50812 | -0.51727 | -0.56305 | -0.65002 | -0.70038 | 0.6134 | 0.46692 | -122.493 | 0.74616 | 0.68207 | 0.21515 | -122.5204 | -0.045776 | -0.09613 | -123.1384 | 0.13275 | 0.09613 | 0.19226 | -123.1842 | 0.73242 | 0.70496 | 0.66834 | -122.7585 | 0.086975 | 0.041199 | 0.14648 | -123.3215
1162.9062 | 123.3444 | -0.61798 | 122.6486 | 0.45754 | 0.14445 | 0.15467 | 0.085722 | 0.10278 | 0.0011837 | 0.017404 | 0.16888 | 0.17632 | 0.0021631 | 0.17208 | 0.0075399 | -0.036201 | 0.054932 | 0.07782 | 0.013733 | 0.027466 | 0.11444 | 0.013733 | -0.11902 | -0.52643 | -0.55389 | -0.60425 | -0.52643 | -0.55847 | -0.64087 | -0.72327 | 0.63171 | 0.49896 | -122.5342 | 0.6958 | 0.64545 | 0.14649 | -122.5937 | -0.022888 | -0.10529 | -123.175 | 0.091553 | 0.013733 | 0.11902 | -123.2071 | 0.73242 | 0.67291 | 0.63171 | -122.7676 | 0.091553 | 0.059509 | 0.064087 | -123.3719
1163.8438 | 123.381 | -0.63171 | 122.6166 | 0.10659 | 0.13056 | 0.15146 | 0.067564 | 0.098509 | -0.0052253 | 0.029153 | -0.01422 | 0.17312 | -0.012791 | 0.1913 | 0.0021989 | -0.024451 | 0.041199 | 0.086975 | 0.027466 | 0.036621 | 0.11902 | -0.009155 | -0.14191 | -0.50812 | -0.52185 | -0.55847 | -0.5127 | -0.54474 | -0.6546 | -0.72327 | 0.62256 | 0.48981 | -122.4976 | 0.71869 | 0.66834 | 0.17853 | -122.5754 | -0.022888 | -0.091553 | -123.1293 | 0.1236 | 0.073242 | 0.1648 | -123.1613 | 0.75073 | 0.67291 | 0.65918 | -122.7585 | 0.11902 | 0.086975 | 0.10986 | -123.3398
1164.9062 | 123.4177 | -0.60883 | 122.6303 | 0.045557 | 0.15299 | 0.1504 | 0.070768 | 0.10705 | -0.0020213 | 0.020609 | -0.65509 | 0.17632 | 0.0053671 | 0.16353 | 0.011812 | -0.034064 | 0.091553 | 0.13733 | 0.054932 | 0.07782 | 0.10986 | 0.004578 | -0.13275 | -0.46692 | -0.45319 | -0.51727 | -0.52643 | -0.56763 | -0.64545 | -0.74158 | 0.6134 | 0.47607 | -122.5204 | 0.74616 | 0.68665 | 0.21057 | -122.5388 | -0.036621 | -0.13275 | -123.1567 | 0.14191 | 0.091553 | 0.2243 | -123.1979 | 0.71869 | 0.70038 | 0.66376 | -122.7631 | 0.082398 | 0.041199 | 0.15564 | -123.3719
1165.8438 | 123.381 | -0.62714 | 122.6395 | 0.045557 | 0.1327 | 0.13972 | 0.063291 | 0.099578 | -0.0073613 | 0.015268 | -0.10577 | 0.17526 | -0.0042459 | 0.18276 | 0.015017 | -0.034064 | 0.059509 | 0.11444 | 0.027466 | 0.054932 | 0.13733 | 0.013733 | -0.14191 | -0.48981 | -0.50354 | -0.56763 | -0.50812 | -0.55847 | -0.64087 | -0.71411 | 0.64087 | 0.48523 | -122.5021 | 0.74158 | 0.68207 | 0.19684 | -122.58 | -0.013733 | -0.086975 | -123.1476 | 0.13733 | 0.059509 | 0.14648 | -123.1979 | 0.76447 | 0.68665 | 0.6546 | -122.7814 | 0.11902 | 0.068664 | 0.1236 | -123.3536
1166.9062 | 123.3856 | -0.6134 | 122.6486 | 0.56436 | 0.17435 | 0.1301 | 0.094267 | 0.10705 | 0.02575 | 0.025949 | 0.30621 | 0.1838 | -0.0095859 | 0.1646 | 0.021425 | -0.038337 | 0.11902 | 0.10529 | 0.041199 | 0.064087 | 0.11444 | 0.018311 | -0.1236 | -0.4715 | -0.50354 | -0.55389 | -0.5127 | -0.55847 | -0.6546 | -0.70496 | 0.63171 | 0.48981 | -122.5342 | 0.71869 | 0.67749 | 0.18768 | -122.5296 | -0.041199 | -0.091553 | -123.1613 | 0.14191 | 0.059509 | 0.15106 | -123.2071 | 0.72784 | 0.73242 | 0.6546 | -122.7722 | 0.10071 | 0.054931 | 0.10986 | -123.3536
1167.8438 | 123.3627 | -0.63171 | 122.6486 | 0.18289 | 0.14017 | 0.13224 | 0.068632 | 0.095305 | -0.010566 | 0.025949 | 0.077332 | 0.1838 | -0.019199 | 0.18276 | 0.020357 | -0.029792 | 0.018311 | 0.064087 | 0 | 0.041199 | 0.12817 | 0 | -0.12817 | -0.52185 | -0.53558 | -0.58136 | -0.5127 | -0.54016 | -0.6546 | -0.70496 | 0.63171 | 0.50354 | -122.5204 | 0.6958 | 0.67291 | 0.16937 | -122.6303 | -0.022888 | -0.073242 | -123.1613 | 0.10986 | 0.050354 | 0.1236 | -123.1888 | 0.75989 | 0.65002 | 0.63171 | -122.7768 | 0.11902 | 0.091553 | 0.096131 | -123.3536
1168.9062 | 123.2941 | -0.64545 | 122.6532 | 0.030298 | 0.18504 | 0.13331 | 0.07504 | 0.10919 | 0.031091 | 0.032358 | -0.25836 | 0.19555 | 0.0032311 | 0.19024 | 0.027834 | -0.04795 | 0.086975 | 0.050354 | -0.036621 | 0.018311 | 0.14191 | -0.018311 | -0.14648 | -0.54474 | -0.58594 | -0.67749 | -0.48981 | -0.52643 | -0.67291 | -0.74616 | 0.62714 | 0.49896 | -122.5113 | 0.6958 | 0.66376 | 0.16479 | -122.5662 | -0.027466 | -0.10071 | -123.143 | 0.10071 | -0.032043 | 0.068665 | -123.1796 | 0.78735 | 0.73242 | 0.60883 | -122.7997 | 0.15564 | 0.11902 | 0.05951 | -123.3994
1169.8438 | 123.3536 | -0.63171 | 122.6624 | 0.2134 | 0.1327 | 0.16001 | 0.059019 | 0.10812 | -0.019111 | 0.023813 | 0.0010378 | 0.17632 | -0.022404 | 0.17635 | 0.0032669 | -0.027656 | -0.013733 | 0.073242 | -0.004578 | 0.027466 | 0.1236 | -0.018311 | -0.15564 | -0.52185 | -0.52185 | -0.56763 | -0.50354 | -0.54016 | -0.64545 | -0.71869 | 0.6134 | 0.47607 | -122.5388 | 0.70496 | 0.65918 | 0.18311 | -122.6761 | -0.013733 | -0.086975 | -123.1659 | 0.10986 | 0.064087 | 0.15106 | -123.2025 | 0.75531 | 0.61798 | 0.62714 | -122.818 | 0.12817 | 0.091553 | 0.10986 | -123.381
1170.9062 | 123.2529 | -0.66376 | 122.6715 | 0.42703 | 0.17649 | 0.13331 | 0.084654 | 0.10278 | 0.031091 | 0.038766 | 0.062074 | 0.18914 | -0.0053139 | 0.18062 | 0.031038 | -0.035133 | 0 | -0.027466 | -0.086975 | 0 | 0.16479 | -0.032043 | -0.15564 | -0.58136 | -0.65002 | -0.6958 | -0.48065 | -0.52185 | -0.66834 | -0.73242 | 0.63171 | 0.50812 | -122.5067 | 0.63629 | 0.66376 | 0.15564 | -122.6715 | -0.004578 | -0.068665 | -123.1522 | 0.082397 | -0.032044 | 0.036621 | -123.1934 | 0.82855 | 0.66376 | 0.57678 | -122.8271 | 0.18311 | 0.14191 | 0.013733 | -123.4039
1171.8438 | 123.3536 | -0.64545 | 122.6486 | 0.45754 | 0.12843 | 0.14292 | 0.055814 | 0.10919 | -0.011634 | 0.021677 | 0.12311 | 0.18273 | -0.0063819 | 0.18383 | 0.0096759 | -0.023383 | 0.004578 | 0.073242 | 0.013733 | 0.036621 | 0.12817 | 0.009155 | -0.1236 | -0.53558 | -0.53558 | -0.59052 | -0.5127 | -0.56305 | -0.64087 | -0.74158 | 0.6546 | 0.52185 | -122.5204 | 0.71869 | 0.68207 | 0.16022 | -122.644 | 0.004578 | -0.09613 | -123.1613 | 0.10986 | 0.054932 | 0.15106 | -123.2117 | 0.77362 | 0.65002 | 0.65918 | -122.7722 | 0.13275 | 0.082398 | 0.10986 | -123.3902
1172.9062 | 123.2986 | -0.64087 | 122.6761 | 0.4728 | 0.17542 | 0.13544 | 0.081449 | 0.10278 | 0.023614 | 0.029153 | 0.22992 | 0.17846 | 0.0085721 | 0.17635 | 0.01288 | -0.031928 | 0.018311 | 0.009155 | -0.073242 | -0.013733 | 0.17395 | -0.013733 | -0.13733 | -0.55389 | -0.59967 | -0.64545 | -0.49439 | -0.52643 | -0.67749 | -0.737 | 0.62714 | 0.50354 | -122.5021 | 0.65002 | 0.62714 | 0.1236 | -122.6578 | -0.036621 | -0.096131 | -123.1705 | 0.086975 | -0.004578 | 0.091553 | -123.2025 | 0.81482 | 0.65918 | 0.56763 | -122.8134 | 0.14648 | 0.11444 | 0.041199 | -123.4131
1173.8438 | 123.3444 | -0.61798 | 122.6212 | 0.57961 | 0.1594 | 0.15467 | 0.068632 | 0.10492 | -0.0030893 | 0.016336 | 0.41303 | 0.18594 | -0.0031779 | 0.18703 | 0.0096759 | -0.032996 | 0.054932 | 0.10529 | 0.027466 | 0.050354 | 0.10986 | 0.009155 | -0.1236 | -0.50354 | -0.52643 | -0.58136 | -0.52643 | -0.55847 | -0.6546 | -0.70953 | 0.62714 | 0.49439 | -122.5113 | 0.72327 | 0.66834 | 0.17395 | -122.5662 | -0.036621 | -0.091553 | -123.1476 | 0.11444 | 0.036621 | 0.12817 | -123.1796 | 0.72784 | 0.67291 | 0.64545 | -122.7448 | 0.091553 | 0.059509 | 0.091553 | -123.3307
1174.9062 | 123.3673 | -0.60883 | 122.6166 | 0.5491 | 0.17756 | 0.12903 | 0.078245 | 0.10065 | 0.017205 | 0.030222 | 0.2757 | 0.19448 | -0.0053139 | 0.16887 | 0.019289 | -0.038337 | 0.064087 | 0.082397 | 0.009155 | 0.054932 | 0.13275 | 0.009155 | -0.13275 | -0.48981 | -0.50354 | -0.5722 | -0.51727 | -0.5722 | -0.65002 | -0.72327 | 0.61798 | 0.47607 | -122.4838 | 0.69122 | 0.66376 | 0.18768 | -122.5525 | -0.041198 | -0.11444 | -123.1339 | 0.11902 | 0.036621 | 0.15106 | -123.1888 | 0.74158 | 0.67291 | 0.61798 | -122.7493 | 0.091553 | 0.036621 | 0.10529 | -123.3398
1175.8438 | 123.3948 | -0.59509 | 122.6166 | 0.5491 | 0.16047 | 0.14506 | 0.068632 | 0.12094 | -0.0062933 | 0.025949 | 0.38251 | 0.18594 | -0.0031779 | 0.17955 | 0.020357 | -0.024451 | 0.082397 | 0.11902 | 0.041199 | 0.068665 | 0.10986 | 0.009155 | -0.13733 | -0.48981 | -0.48981 | -0.55389 | -0.52643 | -0.55389 | -0.63629 | -0.70496 | 0.60425 | 0.45776 | -122.5067 | 0.71411 | 0.66376 | 0.20599 | -122.5342 | -0.041199 | -0.10986 | -123.143 | 0.10529 | 0.041199 | 0.15106 | -123.1705 | 0.70496 | 0.67749 | 0.63629 | -122.7539 | 0.068665 | 0.041199 | 0.10529 | -123.3215
1176.8438 | 123.3856 | -0.59509 | 122.6257 | 0.64065 | 0.17008 | 0.12369 | 0.081449 | 0.12094 | 0.0043877 | 0.023813 | 0.33673 | 0.19021 | -0.018131 | 0.18383 | 0.021425 | -0.035133 | 0.09613 | 0.10529 | 0.032043 | 0.07782 | 0.11902 | 0.009155 | -0.10986 | -0.48065 | -0.49896 | -0.55847 | -0.53101 | -0.56305 | -0.65002 | -0.70496 | 0.60425 | 0.48523 | -122.5067 | 0.70038 | 0.67291 | 0.18768 | -122.5296 | -0.054931 | -0.10986 | -123.1567 | 0.11444 | 0.036621 | 0.14648 | -123.1888 | 0.71411 | 0.69122 | 0.62714 | -122.7356 | 0.064087 | 0.032044 | 0.096131 | -123.3307
1177.9062 | 123.317 | -0.63171 | 122.6807 | -0.18333 | 0.16688 | 0.13224 | 0.057951 | 0.11453 | 0.019342 | 0.029153 | -0.3194 | 0.19234 | 0.0021631 | 0.18596 | 0.025698 | -0.037269 | 0.036621 | 0.032043 | -0.036621 | 0.041199 | 0.15564 | -0.032043 | -0.16022 | -0.5722 | -0.53101 | -0.64087 | -0.48523 | -0.53558 | -0.67291 | -0.75531 | 0.59967 | 0.4715 | -122.525 | 0.66376 | 0.67291 | 0.20142 | -122.644 | -0.041199 | -0.1236 | -123.1659 | 0.059509 | -0.009155 | 0.11444 | -123.2162 | 0.78735 | 0.66834 | 0.59509 | -122.8409 | 0.14648 | 0.096131 | 0.10071 | -123.436
1178.8438 | 123.3902 | -0.59509 | 122.6349 | 0.67117 | 0.15513 | 0.13651 | 0.059019 | 0.10385 | 0.0022517 | 0.034494 | 0.38251 | 0.18807 | -0.012791 | 0.17421 | 0.020357 | -0.021247 | 0.059509 | 0.10986 | 0.009155 | 0.07782 | 0.10529 | 0.013733 | -0.13733 | -0.48523 | -0.48981 | -0.55389 | -0.52643 | -0.57678 | -0.64545 | -0.71411 | 0.60883 | 0.45776 | -122.5296 | 0.70496 | 0.67291 | 0.21515 | -122.5754 | -0.050354 | -0.11902 | -123.1613 | 0.10986 | 0.041199 | 0.16022 | -123.2117 | 0.70038 | 0.6546 | 0.60425 | -122.7722 | 0.068665 | 0.018311 | 0.10529 | -123.349
1179.9062 | 123.2483 | -0.66376 | 122.6761 | 0.27444 | 0.1829 | 0.13972 | 0.088926 | 0.10919 | 0.028955 | 0.033426 | -0.090514 | 0.19448 | 0.010708 | 0.17421 | 0.028902 | -0.039405 | 0 | -0.013733 | -0.086975 | -0.004578 | 0.16479 | -0.027466 | -0.16937 | -0.61798 | -0.63629 | -0.71869 | -0.4715 | -0.52643 | -0.70038 | -0.75989 | 0.63629 | 0.49438 | -122.5113 | 0.65002 | 0.65918 | 0.16479 | -122.6761 | -0.036621 | -0.096131 | -123.1476 | 0.045776 | -0.054932 | 0.041199 | -123.2025 | 0.82855 | 0.66376 | 0.57678 | -122.8455 | 0.19226 | 0.13733 | 0.027465 | -123.436
1180.8438 | 123.3124 | -0.63629 | 122.6669 | 0.39651 | 0.17542 | 0.14399 | 0.065427 | 0.10599 | 0.0075917 | 0.025949 | 0.30621 | 0.19128 | 2.7137e-05 | 0.17849 | 0.017153 | -0.029792 | 0.004578 | -0.009155 | -0.073242 | 0.018311 | 0.16479 | -0.032043 | -0.15106 | -0.55389 | -0.58594 | -0.62714 | -0.50812 | -0.54474 | -0.65002 | -0.737 | 0.60425 | 0.48523 | -122.5021 | 0.62714 | 0.6546 | 0.16937 | -122.6624 | -0.013732 | -0.10071 | -123.175 | 0.082398 | 0.009156 | 0.10986 | -123.2117 | 0.80109 | 0.64087 | 0.56305 | -122.818 | 0.12817 | 0.091553 | 0.050355 | -123.4039
1181.9062 | 123.2666 | -0.65002 | 122.6761 | -0.18333 | 0.16474 | 0.1536 | 0.076109 | 0.10919 | -0.010566 | 0.025949 | -0.56354 | 0.17739 | -0.0042459 | 0.18596 | 0.011812 | -0.023383 | -0.054932 | 0.059509 | -0.054932 | -0.009155 | 0.16479 | -0.027466 | -0.16479 | -0.62714 | -0.58136 | -0.66834 | -0.46692 | -0.53101 | -0.69122 | -0.75531 | 0.62256 | 0.48523 | -122.5113 | 0.70953 | 0.64087 | 0.15564 | -122.731 | -0.041199 | -0.10529 | -123.143 | 0.022888 | -0.018311 | 0.086975 | -123.2071 | 0.81482 | 0.59509 | 0.59509 | -122.8409 | 0.18311 | 0.11902 | 0.068664 | -123.4314
1182.8438 | 123.2437 | -0.65918 | 122.6669 | 0.18289 | 0.19251 | 0.14399 | 0.085722 | 0.10492 | 0.030023 | 0.035562 | 0.13837 | 0.18487 | 0.0053671 | 0.17315 | 0.037447 | -0.029792 | 0 | -0.018311 | -0.091553 | -0.009155 | 0.15564 | -0.018311 | -0.17853 | -0.6134 | -0.63629 | -0.69122 | -0.48065 | -0.52643 | -0.67749 | -0.75531 | 0.64087 | 0.48065 | -122.5113 | 0.64087 | 0.65002 | 0.16937 | -122.6669 | -0.01831 | -0.09613 | -123.1476 | 0.045777 | -0.032043 | 0.064087 | -123.1934 | 0.81482 | 0.65918 | 0.56763 | -122.8455 | 0.17853 | 0.13275 | 0.022888 | -123.4222
1183.9062 | 123.2803 | -0.67749 | 122.6532 | -0.39695 | 0.16047 | 0.15253 | 0.073972 | 0.099578 | 0.00011475 | 0.020609 | -0.38043 | 0.18594 | -0.0053139 | 0.19664 | 0.013948 | -0.032996 | -0.022888 | -0.022888 | -0.086975 | -0.009155 | 0.16479 | -0.027466 | -0.16937 | -0.63171 | -0.59967 | -0.67291 | -0.48065 | -0.5127 | -0.6958 | -0.75073 | 0.65002 | 0.50812 | -122.4884 | 0.6546 | 0.66834 | 0.16022 | -122.6761 | -0.018311 | -0.073242 | -123.1339 | 0.045776 | 0.004577 | 0.077819 | -123.1659 | 0.84229 | 0.6546 | 0.59052 | -122.8226 | 0.19684 | 0.1648 | 0.07782 | -123.4039
1184.8438 | 123.2986 | -0.66376 | 122.6578 | 0.45754 | 0.19251 | 0.1269 | 0.068632 | 0.10705 | 0.0033197 | 0.021677 | 0.33673 | 0.18807 | 0.0032311 | 0.17849 | 0.020357 | -0.021247 | -0.013733 | -0.018311 | -0.086975 | -0.018311 | 0.14648 | -0.013733 | -0.17395 | -0.59052 | -0.59509 | -0.6546 | -0.47607 | -0.52185 | -0.66376 | -0.74616 | 0.65002 | 0.48981 | -122.5113 | 0.64545 | 0.64545 | 0.15564 | -122.6715 | 0 | -0.082398 | -123.1338 | 0.073242 | 0.009155 | 0.091553 | -123.1796 | 0.81024 | 0.65002 | 0.57678 | -122.8317 | 0.18768 | 0.14191 | 0.068664 | -123.4039
1185.9062 | 123.381 | -0.61798 | 122.644 | -0.18333 | 0.15192 | 0.14933 | 0.059019 | 0.093169 | -0.027656 | 0.017404 | -0.19733 | 0.18594 | -0.0074499 | 0.18276 | 0.0032669 | -0.023383 | 0.059509 | 0.13733 | 0.041199 | 0.07782 | 0.1236 | 0.004578 | -0.13733 | -0.52185 | -0.43945 | -0.52643 | -0.50812 | -0.55847 | -0.65918 | -0.72784 | 0.62256 | 0.48065 | -122.5204 | 0.75531 | 0.6958 | 0.21515 | -122.5845 | -0.041199 | -0.10986 | -123.1522 | 0.09613 | 0.091553 | 0.20142 | -123.2025 | 0.74158 | 0.67749 | 0.65918 | -122.7814 | 0.10986 | 0.059509 | 0.17853 | -123.3719
1186.8438 | 123.3124 | -0.63629 | 122.6532 | -0.21384 | 0.19465 | 0.14719 | 0.082517 | 0.12308 | 0.027886 | 0.032358 | -0.39569 | 0.17953 | -0.0031779 | 0.16887 | 0.031038 | -0.036201 | 0.036621 | 0.045776 | -0.027466 | 0.032043 | 0.15564 | -0.022888 | -0.16479 | -0.56763 | -0.56305 | -0.62256 | -0.48981 | -0.53101 | -0.68665 | -0.74616 | 0.6134 | 0.4715 | -122.4976 | 0.68207 | 0.66834 | 0.19684 | -122.6166 | -0.050354 | -0.10986 | -123.143 | 0.068665 | 0.013733 | 0.1236 | -123.1842 | 0.79193 | 0.67291 | 0.60883 | -122.818 | 0.14648 | 0.10529 | 0.073243 | -123.3994
1187.9062 | 123.2941 | -0.66834 | 122.6486 | -0.27488 | 0.14231 | 0.16001 | 0.049406 | 0.096373 | -0.0041573 | 0.028085 | -0.42621 | 0.17632 | -0.015995 | 0.17421 | 0.0043349 | -0.021247 | 0.013733 | 0.054932 | -0.027466 | 0.032043 | 0.14648 | -0.018311 | -0.14648 | -0.60883 | -0.58136 | -0.63171 | -0.48981 | -0.51727 | -0.68665 | -0.75989 | 0.65002 | 0.52185 | -122.5021 | 0.72327 | 0.70038 | 0.17853 | -122.6349 | -0.018311 | -0.091553 | -123.1384 | 0.059509 | 0.036621 | 0.12817 | -123.1659 | 0.81482 | 0.68207 | 0.64087 | -122.7951 | 0.17853 | 0.15106 | 0.086975 | -123.4085
1188.8438 | 123.2986 | -0.66834 | 122.6578 | -0.00022031 | 0.17329 | 0.12583 | 0.078245 | 0.11239 | 0.027886 | 0.033426 | -0.18207 | 0.18273 | 0.01498 | 0.17528 | 0.017153 | -0.02552 | 0.041199 | 0.036621 | -0.032043 | 0.036621 | 0.14648 | -0.027466 | -0.15106 | -0.58136 | -0.58136 | -0.6546 | -0.49896 | -0.54016 | -0.68207 | -0.74616 | 0.64087 | 0.51727 | -122.5113 | 0.70496 | 0.70496 | 0.18768 | -122.6166 | -0.013733 | -0.07782 | -123.1567 | 0.086975 | 0.013733 | 0.091553 | -123.1979 | 0.81482 | 0.70953 | 0.63629 | -122.8088 | 0.16937 | 0.12817 | 0.086975 | -123.4039
1189.9062 | 123.4085 | -0.62714 | 122.6395 | -0.13755 | 0.13483 | 0.16001 | 0.077177 | 0.10278 | -0.012702 | 0.022745 | -0.19733 | 0.18273 | -0.019199 | 0.15926 | 0.0075399 | -0.018043 | 0.068665 | 0.16479 | 0.068665 | 0.086975 | 0.1236 | -0.004578 | -0.1236 | -0.52643 | -0.46692 | -0.53101 | -0.50812 | -0.55847 | -0.66376 | -0.72327 | 0.62256 | 0.50354 | -122.5159 | 0.79193 | 0.71411 | 0.21057 | -122.5708 | -0.036621 | -0.096131 | -123.1476 | 0.10071 | 0.09613 | 0.19226 | -123.1979 | 0.75073 | 0.6958 | 0.6958 | -122.7631 | 0.11902 | 0.068664 | 0.16022 | -123.3627
1190.8438 | 123.2529 | -0.65918 | 122.6761 | 0.19814 | 0.1797 | 0.13865 | 0.077177 | 0.096373 | 0.037499 | 0.034494 | -0.12103 | 0.19021 | 0.0064351 | 0.18062 | 0.022493 | -0.029792 | 0.022888 | -0.013733 | -0.059509 | 0 | 0.15564 | -0.022888 | -0.16022 | -0.61798 | -0.62256 | -0.68207 | -0.46692 | -0.53101 | -0.6958 | -0.77362 | 0.63629 | 0.49896 | -122.5204 | 0.64545 | 0.65918 | 0.16022 | -122.6532 | -0.036621 | -0.11444 | -123.143 | 0.041199 | -0.022888 | 0.091553 | -123.2071 | 0.81482 | 0.68207 | 0.59967 | -122.8363 | 0.19226 | 0.12817 | 0.036621 | -123.4497
1191.9062 | 123.3673 | -0.61798 | 122.6395 | 0.16763 | 0.14231 | -0.092066 | 0.066496 | 0.10919 | -0.018043 | 0.027017 | 0.12311 | 0.18166 | -0.028812 | 0.17955 | 0.0021989 | -0.026588 | -0.004578 | 0.045776 | -0.009155 | 0.045776 | 0.13733 | -0.004578 | -0.13275 | -0.54932 | -0.52185 | -0.56763 | -0.5127 | -0.53558 | -0.66376 | -0.71869 | 0.6134 | 0.48523 | -122.5021 | 0.66376 | 0.66376 | 0.17853 | -122.644 | -0.045776 | -0.10071 | -123.1522 | 0.068665 | 0.050354 | 0.15106 | -123.175 | 0.75531 | 0.6134 | 0.60883 | -122.7722 | 0.10529 | 0.082398 | 0.09613 | -123.3582
1192.8438 | 123.2758 | -0.67749 | 122.6486 | -0.3054 | 0.15513 | 0.13972 | 0.08679 | 0.10705 | 0.0065237 | 0.022745 | -0.47198 | 0.18166 | 2.7137e-05 | 0.18276 | 0.011812 | -0.031928 | -0.013733 | -0.036621 | -0.10529 | 0.009155 | 0.15564 | -0.022888 | -0.17853 | -0.62256 | -0.6134 | -0.68207 | -0.48065 | -0.52185 | -0.70038 | -0.76446 | 0.6546 | 0.49896 | -122.493 | 0.64087 | 0.68665 | 0.18768 | -122.6624 | -0.022888 | -0.086975 | -123.1293 | 0.054931 | -0.004578 | 0.082397 | -123.1705 | 0.83313 | 0.66376 | 0.5722 | -122.8271 | 0.19684 | 0.15564 | 0.064087 | -123.4131
1193.9062 | 123.3994 | -0.63171 | 122.6349 | -0.16807 | 0.13804 | 0.1536 | 0.066496 | 0.098509 | -0.0073613 | 0.016336 | -0.2431 | 0.17312 | -0.015995 | 0.15499 | 0.013948 | -0.019111 | 0.054932 | 0.14648 | 0.045776 | 0.082397 | 0.12817 | 0 | -0.12817 | -0.53558 | -0.46692 | -0.54016 | -0.52643 | -0.55847 | -0.6546 | -0.71869 | 0.63171 | 0.50354 | -122.5067 | 0.7782 | 0.71411 | 0.21057 | -122.58 | -0.022888 | -0.086975 | -123.1613 | 0.096131 | 0.091553 | 0.17853 | -123.1934 | 0.75989 | 0.68665 | 0.67749 | -122.7631 | 0.10529 | 0.073242 | 0.1648 | -123.3536
1194.8438 | 123.3032 | -0.68207 | 122.6486 | -0.25962 | 0.18183 | 0.14292 | 0.061155 | 0.10812 | 0.032159 | 0.03663 | -0.39569 | 0.1806 | -0.0074499 | 0.17742 | 0.019289 | -0.039405 | 0.032043 | 0.036621 | -0.045776 | 0.032043 | 0.16937 | -0.022888 | -0.16479 | -0.5722 | -0.58594 | -0.64545 | -0.50354 | -0.54016 | -0.6958 | -0.75073 | 0.65918 | 0.51727 | -122.4792 | 0.71869 | 0.71411 | 0.19684 | -122.6166 | -0.013733 | -0.068664 | -123.1522 | 0.10986 | 0.036621 | 0.10528 | -123.1888 | 0.85144 | 0.71411 | 0.63629 | -122.8134 | 0.17853 | 0.14191 | 0.096131 | -123.3994
1195.9062 | 123.4085 | -0.64545 | 122.6303 | -0.58005 | 0.12095 | 0.15467 | 0.061155 | 0.099578 | -0.014838 | 0.034494 | -0.27362 | 0.17419 | -0.018131 | 0.17421 | 0.0043349 | -0.028724 | 0.07782 | 0.14191 | 0.07782 | 0.073242 | 0.10071 | 0.009155 | -0.12817 | -0.51727 | -0.47607 | -0.54474 | -0.53101 | -0.5722 | -0.66834 | -0.70953 | 0.6546 | 0.51727 | -122.5296 | 0.78735 | 0.71869 | 0.20142 | -122.5525 | -0.022888 | -0.064087 | -123.1613 | 0.12817 | 0.10071 | 0.1648 | -123.2025 | 0.74616 | 0.72327 | 0.72327 | -122.7585 | 0.11444 | 0.073242 | 0.16937 | -123.3398
1196.8438 | 123.3078 | -0.66834 | 122.6578 | -0.29014 | 0.16474 | 0.14399 | 0.079313 | 0.10919 | 0.016137 | 0.023813 | -0.53302 | 0.18487 | -0.0042459 | 0.18276 | 0.026766 | -0.050086 | -0.004578 | 0.004578 | -0.068665 | 0.022888 | 0.16479 | -0.032043 | -0.16022 | -0.59509 | -0.59509 | -0.65002 | -0.48981 | -0.50812 | -0.6958 | -0.74158 | 0.63629 | 0.50812 | -122.493 | 0.67291 | 0.69122 | 0.1831 | -122.6624 | -0.027466 | -0.073242 | -123.1476 | 0.073242 | 0.018311 | 0.091553 | -123.1659 | 0.83313 | 0.66376 | 0.59967 | -122.818 | 0.17853 | 0.16022 | 0.073242 | -123.3994
1197.9062 | 123.3948 | -0.6134 | 122.6212 | -0.21384 | 0.13163 | 0.15146 | 0.068632 | 0.10065 | -0.0094983 | 0.016336 | -0.25836 | 0.16671 | -0.0021099 | 0.16033 | 0.0021989 | -0.02552 | 0.068665 | 0.14191 | 0.045776 | 0.086975 | 0.1236 | 0.004578 | -0.14191 | -0.51727 | -0.48065 | -0.54474 | -0.51727 | -0.55389 | -0.6546 | -0.72784 | 0.61798 | 0.4715 | -122.4976 | 0.75531 | 0.70038 | 0.22888 | -122.5525 | -0.041199 | -0.11444 | -123.1384 | 0.09613 | 0.068664 | 0.18311 | -123.175 | 0.737 | 0.68207 | 0.65918 | -122.7631 | 0.09613 | 0.059509 | 0.13275 | -123.349
1198.8438 | 123.2849 | -0.66834 | 122.6761 | -0.24436 | 0.16581 | 0.15787 | 0.082517 | 0.10385 | 0.019342 | 0.024881 | -0.47198 | 0.18273 | -0.0042459 | 0.17528 | 0.018221 | -0.040473 | -0.013733 | -0.013733 | -0.082397 | -0.009155 | 0.15564 | -0.041199 | -0.16479 | -0.64545 | -0.6134 | -0.67749 | -0.4715 | -0.54474 | -0.68665 | -0.76446 | 0.62714 | 0.50354 | -122.5204 | 0.6546 | 0.65918 | 0.15564 | -122.6898 | -0.018311 | -0.09613 | -123.1476 | 0.022888 | -0.009155 | 0.086975 | -123.2208 | 0.82398 | 0.6546 | 0.58594 | -122.8409 | 0.19684 | 0.1236 | 0.054932 | -123.4406
1199.8438 | 123.262 | -0.66834 | 122.6669 | -0.16807 | 0.17329 | 0.14933 | 0.07504 | 0.096373 | 0.00011475 | 0.018472 | -0.41095 | 0.1838 | -0.0010409 | 0.17528 | 0.015017 | -0.029792 | -0.022888 | -0.004578 | -0.091553 | 0 | 0.16937 | -0.032043 | -0.17395 | -0.61798 | -0.60425 | -0.67291 | -0.4715 | -0.53101 | -0.68665 | -0.75989 | 0.63629 | 0.49439 | -122.4976 | 0.66376 | 0.66834 | 0.17395 | -122.6898 | -0.018311 | -0.091553 | -123.1384 | 0.050354 | -0.004578 | 0.086975 | -123.1979 | 0.83771 | 0.64545 | 0.57678 | -122.8409 | 0.19684 | 0.13733 | 0.064087 | -123.4268
1200.9062 | 123.3032 | -0.66834 | 122.6624 | -0.29014 | 0.12843 | 0.14826 | 0.062223 | 0.096373 | -0.016974 | 0.028085 | -0.3194 | 0.1806 | -0.0063819 | 0.1646 | 0.0021989 | -0.041541 | 0.013733 | 0.086975 | -0.004578 | 0.054932 | 0.12817 | 0 | -0.15106 | -0.59509 | -0.54474 | -0.64087 | -0.48523 | -0.52643 | -0.67749 | -0.75531 | 0.66834 | 0.51727 | -122.5342 | 0.75531 | 0.72327 | 0.20599 | -122.6486 | -0.009155 | -0.086975 | -123.1476 | 0.073242 | 0.027466 | 0.11444 | -123.1888 | 0.79651 | 0.68207 | 0.66376 | -122.8134 | 0.18311 | 0.14191 | 0.1236 | -123.4177
1201.8438 | 123.3261 | -0.65918 | 122.6532 | -0.10703 | 0.1861 | 0.14185 | 0.081449 | 0.12308 | 0.016137 | 0.03129 | -0.2431 | 0.18166 | 2.7137e-05 | 0.18062 | 0.017153 | -0.03086 | 0.050354 | 0.054932 | -0.041199 | 0.032043 | 0.15564 | -0.041199 | -0.17853 | -0.56305 | -0.56305 | -0.63629 | -0.49896 | -0.53101 | -0.66834 | -0.76446 | 0.61798 | 0.48065 | -122.4976 | 0.71411 | 0.69122 | 0.21057 | -122.6028 | -0.009155 | -0.10528 | -123.1522 | 0.096131 | 0.022888 | 0.12817 | -123.1842 | 0.81482 | 0.70953 | 0.61798 | -122.8317 | 0.16022 | 0.12817 | 0.096131 | -123.4177
1202.9062 | 123.2803 | -0.66376 | 122.699 | -0.27488 | 0.13377 | 0.15681 | 0.067564 | 0.11774 | 0.0022517 | 0.023813 | -0.45673 | 0.18914 | -0.0042459 | 0.18169 | 0.0064719 | -0.031928 | -0.022888 | 0 | -0.10071 | -0.013733 | 0.16937 | -0.045776 | -0.16937 | -0.62714 | -0.59509 | -0.68207 | -0.48523 | -0.53101 | -0.67749 | -0.75531 | 0.61798 | 0.49438 | -122.5296 | 0.66376 | 0.65002 | 0.15564 | -122.7219 | -0.013733 | -0.091553 | -123.1842 | 0.036621 | -0.018311 | 0.073242 | -123.23 | 0.83313 | 0.64087 | 0.56305 | -122.8683 | 0.17853 | 0.13275 | 0.068664 | -123.4543
1203.8438 | 123.3078 | -0.68207 | 122.6532 | -0.2291 | 0.15406 | 0.14826 | 0.072904 | 0.11026 | 0.0033197 | 0.029153 | -0.41095 | 0.18273 | 0.0096401 | 0.18169 | 0.017153 | -0.038337 | -0.018311 | -0.004578 | -0.082397 | 0.009155 | 0.16022 | -0.013733 | -0.1831 | -0.62714 | -0.60425 | -0.68207 | -0.48065 | -0.54016 | -0.70038 | -0.75531 | 0.66834 | 0.49896 | -122.493 | 0.67749 | 0.69122 | 0.19226 | -122.6715 | -0.01831 | -0.073242 | -123.1339 | 0.054932 | 0 | 0.073242 | -123.1934 | 0.84228 | 0.66376 | 0.59967 | -122.8363 | 0.20142 | 0.14191 | 0.07782 | -123.4085
1204.9062 | 123.3948 | -0.62256 | 122.6395 | 0.045557 | 0.13911 | -0.090998 | 0.065427 | 0.093169 | -0.024451 | 0.0099268 | 0.092591 | 0.16671 | -0.023472 | 0.16567 | 0.0032669 | -0.018043 | 0.022888 | 0.09613 | 0.013733 | 0.064087 | 0.11444 | 0 | -0.13275 | -0.52643 | -0.50354 | -0.54474 | -0.53101 | -0.55847 | -0.64087 | -0.70953 | 0.62256 | 0.48981 | -122.525 | 0.71869 | 0.68665 | 0.19684 | -122.6166 | -0.01831 | -0.086975 | -123.1705 | 0.096131 | 0.07782 | 0.1648 | -123.1979 | 0.737 | 0.64545 | 0.63629 | -122.7722 | 0.091553 | 0.064087 | 0.11902 | -123.349
1205.8438 | 123.3902 | -0.61798 | 122.644 | 0.71694 | 0.16901 | 0.14078 | 0.078245 | 0.10705 | 0.024682 | 0.030222 | 0.29095 | 0.17526 | 2.7137e-05 | 0.17208 | 0.018221 | -0.021247 | 0.086975 | 0.10986 | 0.032043 | 0.082397 | 0.10529 | 0.009155 | -0.13733 | -0.48981 | -0.51727 | -0.56305 | -0.53558 | -0.56305 | -0.6546 | -0.74158 | 0.62714 | 0.48065 | -122.5388 | 0.72784 | 0.70038 | 0.21973 | -122.5571 | -0.036621 | -0.1236 | -123.1796 | 0.12817 | 0.054932 | 0.17853 | -123.2071 | 0.72327 | 0.70496 | 0.65002 | -122.7814 | 0.082398 | 0.054932 | 0.10071 | -123.3856
1206.9062 | 123.3719 | -0.64545 | 122.6395 | 0.060816 | 0.13911 | -0.090998 | 0.063291 | 0.10278 | -0.014838 | 0.022745 | 0.12311 | 0.16457 | -0.0042459 | 0.16887 | 0.011812 | -0.024451 | 0.018311 | 0.082397 | 0 | 0.050354 | 0.12817 | -0.004578 | -0.13275 | -0.54016 | -0.53558 | -0.56763 | -0.51727 | -0.56305 | -0.6546 | -0.73242 | 0.64087 | 0.5127 | -122.5113 | 0.72784 | 0.6958 | 0.18311 | -122.6212 | -0.009155 | -0.086975 | -123.1567 | 0.10529 | 0.07782 | 0.1648 | -123.2025 | 0.77362 | 0.66376 | 0.64545 | -122.7722 | 0.12817 | 0.082398 | 0.10986 | -123.3719
1207.8438 | 123.2849 | -0.69122 | 122.6669 | -0.25962 | 0.15726 | 0.14826 | 0.078245 | 0.1156 | 0.0054557 | 0.023813 | -0.47198 | 0.187 | -0.0042459 | 0.17315 | 0.01288 | -0.044746 | -0.009155 | 0.004578 | -0.082397 | -0.018311 | 0.15564 | -0.050354 | -0.17853 | -0.62714 | -0.62714 | -0.69122 | -0.48065 | -0.52643 | -0.70953 | -0.7782 | 0.64087 | 0.5127 | -122.5113 | 0.6958 | 0.67291 | 0.16022 | -122.6761 | -0.018311 | -0.086975 | -123.1476 | 0.064087 | 0 | 0.086975 | -123.1934 | 0.84686 | 0.68207 | 0.60883 | -122.8455 | 0.21057 | 0.1648 | 0.064087 | -123.4451
1208.9062 | 123.3902 | -0.61798 | 122.6349 | -0.12229 | 0.12202 | 0.15253 | 0.059019 | 0.096373 | -0.022315 | 0.01954 | -0.27362 | 0.18273 | -0.0021099 | 0.17528 | 0.0064719 | -0.021247 | 0.082397 | 0.14648 | 0.036621 | 0.082397 | 0.10986 | -0.013733 | -0.16479 | -0.5127 | -0.4715 | -0.55847 | -0.52643 | -0.57678 | -0.66834 | -0.74158 | 0.60425 | 0.45319 | -122.525 | 0.76446 | 0.70038 | 0.24719 | -122.5525 | -0.050354 | -0.1236 | -123.1613 | 0.10529 | 0.059509 | 0.18311 | -123.2117 | 0.72784 | 0.70038 | 0.6546 | -122.7997 | 0.091553 | 0.041199 | 0.14648 | -123.3765
1209.8438 | 123.2986 | -0.68665 | 122.6761 | -0.27488 | 0.14765 | 0.14933 | 0.071836 | 0.10599 | 0.0075917 | 0.028085 | -0.39569 | 0.18273 | -0.0031779 | 0.19024 | 0.018221 | -0.042609 | -0.009155 | -0.027466 | -0.086975 | -0.009155 | 0.14191 | -0.041199 | -0.18768 | -0.61798 | -0.62256 | -0.6958 | -0.48065 | -0.54016 | -0.70038 | -0.75531 | 0.64545 | 0.49896 | -122.5342 | 0.65918 | 0.67749 | 0.17853 | -122.6852 | -0.013732 | -0.068664 | -123.1567 | 0.068665 | -0.009155 | 0.059509 | -123.2162 | 0.82855 | 0.67749 | 0.59967 | -122.8638 | 0.20599 | 0.14648 | 0.064087 | -123.4314
1210.9062 | 123.2849 | -0.67291 | 122.6669 | -0.32065 | 0.1562 | 0.15574 | 0.068632 | 0.10812 | -0.0052253 | 0.020609 | -0.36517 | 0.18487 | -0.0031779 | 0.1646 | 0.015017 | -0.036201 | 0.027466 | 0.091553 | 0.004578 | 0.050354 | 0.12817 | -0.018311 | -0.16479 | -0.59052 | -0.54474 | -0.64087 | -0.50354 | -0.54474 | -0.67749 | -0.75989 | 0.6546 | 0.50812 | -122.5388 | 0.76447 | 0.72327 | 0.21515 | -122.6395 | -0.004577 | -0.086975 | -123.1705 | 0.082398 | 0.032044 | 0.11902 | -123.2117 | 0.80109 | 0.70038 | 0.67749 | -122.8317 | 0.16937 | 0.12817 | 0.12817 | -123.4268
1211.8438 | 123.2941 | -0.67291 | 122.6715 | -0.3054 | 0.16474 | 0.15146 | 0.089994 | 0.10278 | 0.018273 | 0.029153 | -0.39569 | 0.18166 | 0.0021631 | 0.16674 | 0.015017 | -0.03086 | -0.027466 | 0.004578 | -0.10071 | 0 | 0.16479 | -0.036621 | -0.19226 | -0.63629 | -0.62714 | -0.70038 | -0.48065 | -0.52643 | -0.72784 | -0.76904 | 0.63629 | 0.48065 | -122.5067 | 0.67749 | 0.67291 | 0.19226 | -122.699 | -0.054931 | -0.09613 | -123.1522 | 0.036621 | -0.027465 | 0.068665 | -123.1979 | 0.83771 | 0.64545 | 0.5722 | -122.8638 | 0.19226 | 0.14648 | 0.045777 | -123.4406
1212.8438 | 123.2666 | -0.68207 | 122.6669 | -0.42747 | 0.15833 | 0.15253 | 0.071836 | 0.10919 | 0.0033197 | 0.021677 | -0.5025 | 0.17632 | -0.0053139 | 0.16567 | 0.016085 | -0.036201 | -0.022888 | 0 | -0.086975 | 0 | 0.15564 | -0.050354 | -0.17395 | -0.6546 | -0.62714 | -0.68665 | -0.48981 | -0.54474 | -0.70953 | -0.7782 | 0.63171 | 0.50812 | -122.5113 | 0.68207 | 0.68207 | 0.17395 | -122.6898 | -0.027466 | -0.09613 | -123.1567 | 0.027466 | -0.004578 | 0.091552 | -123.2117 | 0.83771 | 0.65918 | 0.59509 | -122.8409 | 0.19226 | 0.13733 | 0.054932 | -123.4451
1213.8438 | 123.2529 | -0.68665 | 122.6669 | -0.33591 | 0.16047 | 0.15253 | 0.076109 | 0.094237 | 0.00011475 | 0.027017 | -0.38043 | 0.17526 | -0.011723 | 0.1881 | 0.0075399 | -0.037269 | -0.050354 | 0.009155 | -0.086975 | -0.013733 | 0.16479 | -0.032043 | -0.18768 | -0.64087 | -0.62256 | -0.70953 | -0.49896 | -0.54932 | -0.70496 | -0.77362 | 0.6546 | 0.49896 | -122.5021 | 0.6958 | 0.67291 | 0.17395 | -122.7173 | -0.01831 | -0.086975 | -123.1659 | 0.045777 | -0.022888 | 0.064087 | -123.2162 | 0.85144 | 0.63629 | 0.59967 | -122.8546 | 0.18768 | 0.13733 | 0.064087 | -123.4406
1214.9062 | 123.3994 | -0.64087 | 122.6166 | 0.13711 | 0.13911 | 0.1536 | 0.060087 | 0.10385 | -0.018043 | 0.020609 | -0.13629 | 0.17526 | 0.0032311 | 0.16246 | 0.011812 | -0.032996 | 0.068665 | 0.15564 | 0.050354 | 0.073242 | 0.11444 | 0.004578 | -0.12817 | -0.51727 | -0.48065 | -0.54016 | -0.54474 | -0.58594 | -0.65002 | -0.74616 | 0.64545 | 0.5127 | -122.5021 | 0.79651 | 0.71411 | 0.20142 | -122.5479 | -0.009155 | -0.10529 | -123.1613 | 0.1236 | 0.10071 | 0.20599 | -123.2025 | 0.75531 | 0.70953 | 0.69122 | -122.7448 | 0.09613 | 0.054932 | 0.16022 | -123.3627
1215.8438 | 123.3902 | -0.63171 | 122.6349 | 0.59487 | 0.15726 | 0.14612 | 0.066496 | 0.10919 | 0.017205 | 0.039835 | 0.2757 | 0.1806 | -0.0095859 | 0.17315 | 0.026766 | -0.029792 | 0.041199 | 0.059509 | -0.018311 | 0.027466 | 0.1236 | 0.013733 | -0.15106 | -0.53101 | -0.54474 | -0.60883 | -0.52643 | -0.57678 | -0.6546 | -0.73242 | 0.64545 | 0.48065 | -122.5113 | 0.69122 | 0.65918 | 0.17853 | -122.5937 | -0.022888 | -0.10071 | -123.1613 | 0.10071 | 0.022888 | 0.1236 | -123.2117 | 0.75531 | 0.67291 | 0.6134 | -122.7859 | 0.10529 | 0.054932 | 0.086975 | -123.3673

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.6052 | 21.4622 | 21.0737 | 21.3133
0.3948 | 21.4628 | 21.0563 | 21.304
1.3948 | 21.447 | 21.0707 | 21.3024
2.3948 | 21.5699 | 21.0672 | 21.3058
3.3948 | 22.2389 | 21.0601 | 21.3037
4.3948 | 23.5973 | 21.0713 | 21.2992
5.3948 | 25.6258 | 21.0693 | 21.302
6.3948 | 28.2568 | 21.0692 | 21.3068
7.3948 | 31.3617 | 21.0661 | 21.3066
8.3948 | 34.8623 | 21.0743 | 21.3084
9.3948 | 38.6864 | 21.0733 | 21.315
10.3948 | 42.7666 | 21.0874 | 21.3263
11.3948 | 47.18 | 21.0923 | 21.3271
12.3948 | 51.819 | 21.1127 | 21.3423
13.3948 | 56.6613 | 21.1359 | 21.3624
14.3948 | 61.6059 | 21.1553 | 21.3816
15.3948 | 66.7353 | 21.1949 | 21.4129
16.3948 | 71.9723 | 21.2194 | 21.4378
17.3948 | 77.4095 | 21.2654 | 21.4696
18.3948 | 82.9206 | 21.31 | 21.5104
19.3948 | 88.5145 | 21.3562 | 21.5621
20.3948 | 94.2254 | 21.4164 | 21.6152
21.3948 | 99.9537 | 21.487 | 21.6734
22.3948 | 105.806 | 21.556 | 21.7393
23.3948 | 111.7179 | 21.6369 | 21.8146
24.3948 | 117.6807 | 21.7352 | 21.8972
25.3948 | 123.6884 | 21.833 | 21.9888
26.3948 | 129.7038 | 21.9427 | 22.086
27.3948 | 135.7749 | 22.0742 | 22.195
28.3948 | 141.9265 | 22.2028 | 22.303
29.3948 | 148.0059 | 22.3585 | 22.4385
30.3948 | 153.975 | 22.5172 | 22.5714
31.3948 | 159.9341 | 22.682 | 22.7225
32.3948 | 165.9402 | 22.8687 | 22.8757
33.3948 | 172.0224 | 23.0604 | 23.0517
34.3948 | 178.1036 | 23.2663 | 23.2188
35.3948 | 184.1774 | 23.4907 | 23.4163
36.426 | 190.251 | 23.733 | 23.6241
37.3948 | 195.7611 | 23.9827 | 23.8199
38.3948 | 201.7439 | 24.2532 | 24.0621
39.3948 | 207.7732 | 24.535 | 24.2984
40.3948 | 213.8024 | 24.8451 | 24.5443
41.3948 | 219.7429 | 25.1857 | 24.8084
42.3948 | 225.5923 | 25.5307 | 25.0832
43.3948 | 231.4618 | 25.912 | 25.3749
44.3948 | 237.3919 | 26.2934 | 25.6791
45.3948 | 243.2856 | 26.6975 | 26.0013
46.3948 | 249.0975 | 27.1052 | 26.3313
47.3948 | 254.8442 | 27.5478 | 26.6791
48.3948 | 260.6024 | 27.988 | 27.0542
49.3948 | 266.3511 | 28.455 | 27.4288
50.3948 | 272.1324 | 28.9383 | 27.8236
51.3948 | 277.8854 | 29.4578 | 28.2383
52.3948 | 283.5871 | 29.98 | 28.6722
53.3948 | 289.2707 | 30.5291 | 29.1289
54.3948 | 294.7127 | 31.0947 | 29.5976
55.3948 | 299.8895 | 31.6823 | 30.0807
56.3948 | 305.2552 | 32.2825 | 30.5834
57.3948 | 310.8818 | 32.9088 | 31.1053
58.3948 | 316.4006 | 33.5474 | 31.6488
59.3948 | 321.6864 | 34.214 | 32.2176
60.3948 | 327.2088 | 34.8981 | 32.791
61.3948 | 332.7284 | 35.5956 | 33.3903
62.3948 | 338.2524 | 36.321 | 34.0057
63.3948 | 343.7304 | 37.0657 | 34.629
64.3948 | 349.1044 | 37.8311 | 35.2782
65.3948 | 354.3743 | 38.619 | 35.9434
66.3948 | 359.5017 | 39.4399 | 36.6292
67.3948 | 364.6776 | 40.2781 | 37.3367
68.3948 | 369.8159 | 41.1215 | 38.054
69.3948 | 374.9508 | 41.9963 | 38.8065
70.3948 | 380.2009 | 42.8773 | 39.5604
71.3948 | 385.1335 | 43.7807 | 40.3495
72.3948 | 390.1495 | 44.6911 | 41.1483
73.3948 | 395.0924 | 45.6403 | 41.9575
74.3948 | 400.1512 | 46.6089 | 42.7945
75.3948 | 405.1701 | 47.6063 | 43.6475
76.3948 | 410.2575 | 48.637 | 44.5217
77.3948 | 415.1106 | 49.6958 | 45.4245
78.3948 | 420.0112 | 50.7889 | 46.3451
79.3948 | 424.9585 | 51.924 | 47.2969
80.3948 | 429.8596 | 53.1001 | 48.2817
81.3948 | 434.5623 | 54.3057 | 49.2983
82.3948 | 438.7326 | 55.544 | 50.3166
83.3948 | 442.5198 | 56.8283 | 51.3494
84.3948 | 446.0829 | 58.1309 | 52.4196
85.3948 | 449.3209 | 59.45 | 53.499
86.3948 | 452.5314 | 60.7889 | 54.6085
87.3948 | 455.6313 | 62.1392 | 55.7228
88.3948 | 458.5852 | 63.5007 | 56.8731
89.3948 | 461.4498 | 64.8748 | 58.0394
90.3948 | 464.1863 | 66.2541 | 59.2144
91.3948 | 466.665 | 67.655 | 60.3907
92.3948 | 469.1654 | 69.0461 | 61.5675
93.3948 | 473.6206 | 70.4574 | 62.7613
94.3948 | 477.22 | 71.8607 | 63.9629
95.3948 | 479.3232 | 73.2801 | 65.1601
96.3948 | 479.1248 | 74.7112 | 66.3668
97.3948 | 478.71 | 76.1445 | 67.5771
98.3948 | 478.6359 | 77.5979 | 68.7809
99.3948 | 478.6067 | 79.0493 | 69.9777
100.3948 | 478.5633 | 80.5031 | 71.1619
101.3948 | 478.4469 | 81.9464 | 72.3414
102.3948 | 478.3919 | 83.3948 | 73.5307
103.3948 | 478.2334 | 84.8355 | 74.7094
104.3948 | 477.9527 | 86.2838 | 75.8775
105.3948 | 477.6935 | 87.7224 | 77.0591
106.3948 | 477.3901 | 89.1444 | 78.2222
107.3948 | 477.0129 | 90.5601 | 79.3684
108.3948 | 476.5981 | 91.9657 | 80.5076
109.3948 | 476.0933 | 93.3634 | 81.6424
110.3948 | 475.7151 | 94.7476 | 82.7615
111.3948 | 475.2386 | 96.1435 | 83.8732
112.3948 | 474.838 | 97.5101 | 84.9726
113.3948 | 474.4631 | 98.8698 | 86.077
114.3948 | 474.1738 | 100.2232 | 87.1619
115.3948 | 473.9269 | 101.5583 | 88.2296
116.3948 | 473.7942 | 102.8738 | 89.2852
117.3948 | 473.628 | 104.1932 | 90.3308
118.3948 | 473.4816 | 105.5032 | 91.3683
119.3948 | 473.5086 | 106.8014 | 92.3858
120.3948 | 473.5515 | 108.0833 | 93.4013
121.3948 | 473.631 | 109.3575 | 94.3979
122.3948 | 473.6892 | 110.6299 | 95.414
123.3948 | 473.8911 | 111.8913 | 96.3867
124.3948 | 474.1178 | 113.1439 | 97.3537
125.3948 | 474.3275 | 114.4034 | 98.336
126.3948 | 474.6909 | 115.6469 | 99.2946
127.3948 | 474.9846 | 116.8829 | 100.273
128.3948 | 475.1634 | 118.0907 | 101.2355
129.3948 | 475.3037 | 119.3174 | 102.201
130.3948 | 475.4992 | 120.5369 | 103.1667
131.3948 | 475.7638 | 121.7512 | 104.1289
132.3948 | 475.9658 | 122.9613 | 105.1023
133.3948 | 476.1655 | 124.1761 | 106.067
134.3948 | 476.3861 | 125.377 | 107.0225
135.3948 | 476.7633 | 126.5789 | 107.9891
136.3948 | 476.9139 | 127.769 | 108.9544
137.3948 | 477.2149 | 128.9435 | 109.9344
138.3948 | 477.559 | 130.1265 | 110.9121
139.3948 | 477.695 | 131.3016 | 111.8888
140.3948 | 477.7195 | 132.472 | 112.8568
141.3948 | 477.8831 | 133.6457 | 113.826
142.3948 | 477.9447 | 134.8071 | 114.8016
143.3948 | 477.9124 | 135.9582 | 115.7526
144.3948 | 477.9967 | 137.0969 | 116.7106
145.3948 | 478.0673 | 138.2383 | 117.6506
146.3948 | 478.136 | 139.361 | 118.5939
147.3948 | 478.0997 | 140.481 | 119.5193
148.3948 | 478.091 | 141.5887 | 120.4187
149.3948 | 478.198 | 142.6894 | 121.3175
150.3948 | 478.2963 | 143.7967 | 122.1964
151.3948 | 478.2713 | 144.8703 | 123.0764
152.3948 | 478.2138 | 145.9538 | 123.9429
153.3948 | 478.1982 | 147.0103 | 124.793
154.3948 | 478.2454 | 148.0666 | 125.6217
155.3948 | 478.3258 | 149.1167 | 126.4424
156.3948 | 478.5074 | 150.1553 | 127.2382
157.3948 | 478.5084 | 151.1866 | 128.0354
158.3948 | 478.3918 | 152.211 | 128.8065
159.3948 | 478.4523 | 153.2506 | 129.5636
160.3948 | 478.6252 | 154.2638 | 130.3087
161.3948 | 478.6661 | 155.2725 | 131.0395
162.3948 | 478.7331 | 156.2773 | 131.7502
163.3948 | 478.621 | 157.2701 | 132.4668
164.3948 | 478.605 | 158.2709 | 133.1867
165.3948 | 478.6063 | 159.2602 | 133.9106
166.3948 | 478.5526 | 160.2419 | 134.6259
167.3948 | 478.5222 | 161.2175 | 135.351
168.3948 | 478.4941 | 162.1932 | 136.0779
169.3948 | 478.418 | 163.1721 | 136.8144
170.3948 | 478.3464 | 164.1282 | 137.5509
171.3948 | 478.2629 | 165.0867 | 138.2876
172.3948 | 478.0151 | 166.04 | 139.0332
173.3948 | 477.8921 | 166.9776 | 139.7886
174.3948 | 477.85 | 167.928 | 140.5541
175.3948 | 477.7029 | 168.8523 | 141.3222
176.3948 | 477.6041 | 169.786 | 142.1124
177.3948 | 477.5676 | 170.7227 | 142.8989
178.3948 | 477.5388 | 171.6446 | 143.705
179.3948 | 477.5351 | 172.5673 | 144.5086
180.3948 | 477.4736 | 173.4873 | 145.3114
181.3948 | 477.3771 | 174.3926 | 146.1286
182.3948 | 477.2356 | 175.3095 | 146.9508
183.3948 | 477.2425 | 176.2035 | 147.7629
184.3948 | 477.0771 | 177.0886 | 148.5815
185.3948 | 477.0354 | 177.9642 | 149.4027
186.3948 | 476.9986 | 178.8413 | 150.2361
187.3948 | 477.0515 | 179.7061 | 151.0732
188.3948 | 477.1067 | 180.5645 | 151.9052
189.3948 | 477.1581 | 181.4232 | 152.7499
190.3948 | 477.226 | 182.2809 | 153.6069
191.3948 | 477.2707 | 183.1285 | 154.453
192.3948 | 477.2265 | 183.9721 | 155.3098
193.3948 | 477.2019 | 184.8155 | 156.1706
194.3948 | 477.2053 | 185.6734 | 157.0346
195.3948 | 477.1592 | 186.5158 | 157.9006
196.3948 | 477.1228 | 187.3858 | 158.7743
197.3948 | 477.0221 | 188.239 | 159.6495
198.3948 | 477.1221 | 189.1046 | 160.5301
199.3948 | 477.2667 | 189.9694 | 161.4197
200.3948 | 477.4907 | 190.8395 | 162.298
201.3948 | 477.5968 | 191.7012 | 163.191
202.3948 | 477.6923 | 192.5763 | 164.0725
203.3948 | 477.7605 | 193.4284 | 164.9479
204.3948 | 477.7651 | 194.2902 | 165.8284
205.3948 | 477.747 | 195.1431 | 166.7044
206.3948 | 477.6516 | 196.0118 | 167.573
207.3948 | 477.6665 | 196.8784 | 168.4442
208.3948 | 477.6192 | 197.7456 | 169.3161
209.3948 | 477.5605 | 198.6234 | 170.1917
210.3948 | 477.6495 | 199.4907 | 171.0668
211.3948 | 477.7178 | 200.3655 | 171.9416
212.3948 | 477.7196 | 201.2405 | 172.8208
213.3948 | 477.7562 | 202.1232 | 173.6898
214.3948 | 477.8065 | 202.9881 | 174.5712
215.3948 | 477.7153 | 203.8492 | 175.4305
216.3948 | 477.6541 | 204.7176 | 176.3084
217.3948 | 477.675 | 205.5763 | 177.1701
218.3948 | 477.7222 | 206.4344 | 178.0358
219.3948 | 477.9011 | 207.2948 | 178.8968
220.3948 | 477.9562 | 208.1544 | 179.7636
221.3948 | 478.0331 | 209.0004 | 180.6219
222.3948 | 478.1368 | 209.861 | 181.4816
223.3948 | 478.1126 | 210.7059 | 182.3458
224.3948 | 478.0216 | 211.5625 | 183.2058
225.3948 | 477.9714 | 212.4115 | 184.0536
226.3948 | 477.9903 | 213.2753 | 184.9047
227.3948 | 477.9744 | 214.1243 | 185.7575
228.3948 | 477.8559 | 214.9812 | 186.6034
229.3948 | 477.7164 | 215.826 | 187.4521
230.3948 | 477.5458 | 216.6619 | 188.2932
231.3948 | 477.4166 | 217.4944 | 189.1395
232.3948 | 477.4625 | 218.3309 | 189.9749
233.3948 | 477.5506 | 219.1675 | 190.8123
234.3948 | 477.5625 | 219.9853 | 191.6492
235.3948 | 477.4869 | 220.7986 | 192.4943
236.3948 | 477.4896 | 221.6306 | 193.3249
237.3948 | 477.4397 | 222.44 | 194.152
238.3948 | 477.4204 | 223.2297 | 194.9814
239.3948 | 477.4294 | 224.0194 | 195.8081
240.3948 | 477.382 | 224.7832 | 196.6287
241.3948 | 477.2639 | 225.5254 | 197.4465
242.3948 | 477.2124 | 226.2348 | 198.2696
243.3948 | 477.2065 | 226.9301 | 199.0796
244.3948 | 477.3052 | 227.5138 | 199.899
245.3948 | 477.3358 | 227.6882 | 200.7197
246.3948 | 477.367 | 227.9416 | 201.5319
247.3948 | 477.3454 | 228.1984 | 202.3544
248.3948 | 477.3401 | 228.439 | 203.1717
249.3948 | 477.438 | 228.6321 | 203.9765
250.3948 | 477.3665 | 228.664 | 204.7943
251.3948 | 477.2069 | 228.6438 | 205.5944
252.3948 | 477.1604 | 228.6379 | 206.4032
253.3948 | 477.2019 | 228.6432 | 207.2188
254.3948 | 477.2926 | 228.6735 | 208.0391
255.3948 | 477.2934 | 228.7547 | 208.8534
256.3948 | 477.1789 | 228.8872 | 209.6744
257.3948 | 477.0445 | 229.1044 | 210.4983
258.3948 | 476.9692 | 229.3765 | 211.3183
259.3948 | 476.9196 | 229.6734 | 212.128
260.3948 | 476.8232 | 229.9517 | 212.9321
261.3948 | 476.7412 | 230.2172 | 213.719
262.3948 | 476.5621 | 230.6182 | 214.4991
263.3948 | 476.4117 | 231.2914 | 215.2765
264.3948 | 476.3437 | 232.7294 | 216.0506
265.3948 | 476.4112 | 233.3503 | 216.8172
266.3948 | 476.5594 | 234.3098 | 217.4097
267.3948 | 476.6856 | 235.8867 | 217.3036
268.3948 | 476.8622 | 237.2191 | 217.3802
269.3948 | 477.0906 | 238.42 | 217.5704
270.3948 | 477.2443 | 239.3584 | 217.9841
271.3948 | 477.3871 | 240.2224 | 218.4371
272.3948 | 477.4722 | 241.0271 | 218.9706
273.3948 | 477.5071 | 241.8416 | 219.6091
274.3948 | 477.5307 | 242.6823 | 220.3257
275.3948 | 477.5201 | 243.497 | 221.1386
276.3948 | 477.4834 | 244.3404 | 221.959
277.3948 | 477.4253 | 245.2682 | 222.7667
278.3948 | 477.3546 | 246.2523 | 223.596
279.3948 | 477.2332 | 247.2354 | 224.4749
280.3948 | 477.0545 | 248.2521 | 225.3311
281.3948 | 476.8265 | 249.3249 | 226.1943
282.3948 | 476.6415 | 250.4012 | 227.036
283.3948 | 476.4626 | 251.5333 | 227.8761
284.3948 | 476.2114 | 252.6375 | 228.7035
285.3948 | 475.946 | 253.8209 | 229.5158
286.3948 | 475.6816 | 255.1859 | 230.3579
287.3948 | 475.4184 | 256.5906 | 231.2509
288.3948 | 475.1826 | 257.1445 | 232.1321
289.3948 | 474.9963 | 257.9054 | 233.0676
290.3948 | 474.8491 | 259.4452 | 233.8627
291.3948 | 474.604 | 261.1256 | 234.7361
292.3948 | 474.3281 | 263.6829 | 235.695
293.3948 | 474.0473 | 264.5822 | 236.6137
294.3948 | 473.8458 | 265.8786 | 237.6147
295.3948 | 473.564 | 266.9806 | 238.5804
296.3948 | 473.3154 | 268.9303 | 239.5385
297.3948 | 473.1825 | 270.6618 | 240.479
298.3948 | 472.9417 | 270.4007 | 241.3591
299.3948 | 472.8543 | 272.1847 | 242.1133
300.3948 | 472.6492 | 272.9643 | 242.8139
301.3948 | 472.5705 | 274.4889 | 243.5253
302.3948 | 472.3781 | 275.5691 | 244.2147
303.3948 | 472.1824 | 275.971 | 244.9356
304.3948 | 472.0244 | 277.2988 | 245.6781
305.3948 | 471.9047 | 278.8855 | 246.462
306.3948 | 471.6877 | 280.5887 | 247.5902
307.3948 | 471.5353 | 281.3167 | 248.8594
308.3948 | 471.2773 | 283.2119 | 250.0657
309.3948 | 471.0552 | 282.5844 | 251.7665
310.3948 | 470.9275 | 283.8092 | 252.967
311.3948 | 470.7649 | 285.1596 | 254.0686
312.3948 | 470.6649 | 286.1127 | 255.1547
313.3948 | 470.5716 | 287.0911 | 256.2078
314.3948 | 470.5474 | 287.8981 | 257.2887
315.3948 | 470.4976 | 289.9881 | 258.2933
316.3948 | 470.3849 | 292.583 | 259.1374
317.3948 | 470.2849 | 293.9354 | 259.968
318.3948 | 470.2011 | 295.0728 | 260.7741
319.3948 | 470.0563 | 296.5617 | 261.5959
320.3948 | 469.99 | 298.1481 | 262.4527
321.3948 | 469.9009 | 300.2417 | 263.3131
322.3948 | 469.6742 | 302.1741 | 264.1516
323.3948 | 469.4543 | 303.4668 | 265.078
324.3948 | 469.3205 | 304.6018 | 266.127
325.3948 | 469.2047 | 306.1271 | 266.9262
326.3948 | 469.092 | 307.9246 | 268.0636
327.3948 | 469.0533 | 307.2455 | 268.8826
328.3948 | 468.9675 | 309.1041 | 269.8084
329.3948 | 468.8023 | 311.0639 | 270.6681
330.3948 | 468.6067 | 315.4414 | 271.8528
331.3948 | 468.3851 | 315.7749 | 272.5748
332.3948 | 468.2351 | 314.7417 | 273.3105
333.3948 | 468.1589 | 316.7804 | 274.3433
334.3948 | 468.0963 | 319.1687 | 275.4762
335.3948 | 467.9665 | 320.6759 | 276.5498
336.3948 | 467.8568 | 319.2864 | 277.0158
337.3948 | 467.7904 | 321.615 | 277.7943
338.3948 | 467.6654 | 324.6603 | 278.5936
339.3948 | 467.6366 | 323.8549 | 279.601
340.3948 | 467.6599 | 325.1634 | 280.4321
341.3948 | 467.6492 | 326.4863 | 281.6646
342.3948 | 467.5497 | 327.8984 | 282.4764
343.3948 | 467.4286 | 329.8123 | 283.6824
344.3948 | 467.2743 | 331.0718 | 284.5951
345.3948 | 467.1215 | 332.8538 | 285.4401
346.3948 | 466.9467 | 333.51 | 286.4445
347.3948 | 466.8616 | 335.9978 | 287.4005
348.3948 | 466.7453 | 336.2171 | 288.518
349.3948 | 466.6583 | 338.441 | 289.5051
350.3948 | 466.4681 | 339.3605 | 290.5547
351.3948 | 466.3549 | 341.9997 | 291.4075
352.3948 | 466.2457 | 343.7346 | 292.9512
353.3948 | 466.1554 | 344.2189 | 293.3345
354.3948 | 466.0816 | 344.1264 | 294.4916
355.3948 | 466.037 | 345.6886 | 295.4537
356.3948 | 465.9204 | 347.547 | 296.5562
357.3948 | 465.8485 | 350.7914 | 297.6346
358.3948 | 465.7329 | 351.1011 | 298.8193
359.3948 | 465.6045 | 352.5509 | 299.8146
360.3948 | 465.5309 | 353.2483 | 300.9298
361.3948 | 465.4376 | 355.7822 | 302.2208
362.3948 | 465.3499 | 356.6413 | 303.3948
363.3948 | 465.2522 | 357.186 | 304.6106
364.3948 | 465.1972 | 358.9538 | 305.8264
365.3948 | 465.2006 | 359.8144 | 307.226
366.3948 | 465.1959 | 361.3439 | 308.5622
367.3948 | 465.2832 | 361.9074 | 309.9409
368.3948 | 465.3172 | 362.4567 | 311.2886
369.3948 | 465.3235 | 363.3138 | 312.6028
370.3948 | 465.396 | 364.3207 | 313.8801
371.3948 | 465.4777 | 365.5523 | 315.0079
372.3948 | 465.4808 | 365.9913 | 316.2375
373.3948 | 465.5183 | 366.7253 | 317.4569
374.3948 | 465.5579 | 368.069 | 318.9101
375.3948 | 465.6193 | 369.474 | 320.2309
376.3948 | 465.7364 | 371.4994 | 321.5461
377.3948 | 465.8614 | 371.582 | 322.4122
378.3948 | 465.9617 | 373.4495 | 323.5024
379.3948 | 466.0278 | 374.6451 | 324.9624
380.3948 | 466.1426 | 377.7535 | 326.3989
381.3948 | 466.1907 | 378.8039 | 327.8084
382.3948 | 466.244 | 379.0645 | 329.028
383.3948 | 466.2675 | 380.0869 | 330.3827
384.3948 | 466.3111 | 380.7675 | 331.5136
385.3948 | 466.427 | 383.0195 | 332.5331
386.3948 | 466.5397 | 383.7167 | 334.0215
387.3948 | 466.5867 | 383.7664 | 335.4423
388.3948 | 466.6232 | 384.6634 | 336.4629
389.3948 | 466.699 | 386.6187 | 338.0091
390.3948 | 466.8208 | 385.7508 | 339.8196
391.3948 | 466.8797 | 386.2598 | 340.8991
392.3948 | 466.8855 | 389.2113 | 342.1072
393.3948 | 466.8747 | 389.2699 | 343.4215
394.3948 | 466.9417 | 390.4583 | 344.726
395.3948 | 466.9874 | 389.8425 | 345.7164
396.3948 | 467.0446 | 391.9913 | 346.9786
397.3948 | 467.131 | 390.8167 | 348.52
398.3948 | 467.1808 | 391.641 | 349.7829
399.3948 | 467.1435 | 391.775 | 350.8906
400.3948 | 467.1231 | 391.6738 | 352.5778
401.3948 | 467.1631 | 392.5285 | 353.6354
402.3948 | 467.1704 | 392.272 | 354.6896
403.3948 | 467.2432 | 392.1174 | 355.8454
404.3948 | 467.233 | 393.3245 | 357.5997
405.3948 | 467.2008 | 393.2607 | 358.4258
406.3948 | 467.2765 | 393.2831 | 359.3455
407.3948 | 467.3777 | 393.5979 | 360.6617
408.3948 | 467.4227 | 392.4349 | 361.6905
409.3948 | 467.5205 | 392.5472 | 363.3
410.3948 | 467.5655 | 392.4231 | 364.5733
411.3948 | 467.5656 | 392.6474 | 365.5243
412.3948 | 467.595 | 393.0578 | 367.0019
413.3948 | 467.6826 | 393.5562 | 367.8245
414.3948 | 467.7589 | 392.7736 | 369.0311
415.3948 | 467.8276 | 393.0187 | 370.3964
416.3948 | 467.8652 | 393.1656 | 371.7859
417.3948 | 467.9575 | 394.1619 | 373.1193
418.3948 | 467.9715 | 393.4595 | 373.9977
419.3948 | 468.0083 | 393.7559 | 375.157
420.3948 | 468.113 | 394.7898 | 375.968
421.3948 | 468.1274 | 394.432 | 376.8548
422.3948 | 468.1036 | 394.7186 | 378.7012
423.3948 | 468.0747 | 394.4157 | 379.4049
424.3948 | 468.1024 | 393.9335 | 380.1587
425.3948 | 468.1398 | 394.3637 | 380.9972
426.3948 | 468.201 | 393.7469 | 381.6105
427.3948 | 468.2619 | 393.7871 | 382.6255
428.3948 | 468.297 | 394.235 | 383.3742
429.3948 | 468.4345 | 394.3993 | 384.2936
430.3948 | 468.6438 | 394.6716 | 385.1666
431.3948 | 468.719 | 395.0058 | 386.0275
432.3948 | 468.7428 | 395.4662 | 386.4755
433.3948 | 468.7258 | 396.1091 | 386.8712
434.3948 | 468.7359 | 396.6732 | 387.3459
435.3948 | 468.741 | 397.2461 | 387.9728
436.3948 | 468.8375 | 397.959 | 387.9974
437.3948 | 468.8607 | 398.5022 | 388.2703
438.3948 | 468.9281 | 399.3172 | 388.1368
439.3948 | 468.9211 | 399.8884 | 388.1065
440.3948 | 468.946 | 400.5658 | 388.5346
441.3948 | 469.0267 | 401.2465 | 388.672
442.3948 | 469.0704 | 401.9336 | 388.7633
443.3948 | 469.1091 | 402.5314 | 389.1091
444.3948 | 469.2031 | 403.3347 | 389.5167
445.3948 | 469.2765 | 404.0171 | 389.8206
446.3948 | 469.2537 | 404.8015 | 389.9915
447.3948 | 469.1314 | 405.5451 | 390.4973
448.3948 | 469.204 | 406.4433 | 391.0427
449.3948 | 469.278 | 407.179 | 391.5797
450.3948 | 469.3375 | 407.8409 | 391.9816
451.3948 | 469.3437 | 408.7791 | 392.551
452.3948 | 469.3912 | 409.6137 | 393.0356
453.3948 | 469.4803 | 410.4989 | 393.6875
454.3948 | 469.5937 | 411.1615 | 394.4518
455.3948 | 469.6593 | 412.1325 | 395.2986
456.3948 | 469.6636 | 412.693 | 395.9054
457.3948 | 469.5784 | 413.2467 | 396.8933
458.3948 | 469.5186 | 413.7858 | 397.5317
459.3948 | 469.5232 | 414.6101 | 398.3155
460.3948 | 469.5662 | 415.3418 | 398.9469
461.3948 | 469.5973 | 416.0235 | 399.7213
462.3948 | 469.5135 | 416.7186 | 400.3752
463.3948 | 469.4556 | 417.2302 | 401.1188
464.3948 | 469.4101 | 418.0275 | 401.7994
465.3948 | 469.4273 | 418.7264 | 402.4895
466.3948 | 469.5183 | 419.2416 | 403.2214
467.3948 | 469.6363 | 419.9508 | 403.7836
468.3948 | 469.7003 | 420.7081 | 404.4799
469.3948 | 469.7701 | 421.2427 | 405.0072
470.3948 | 469.806 | 421.9558 | 405.7625
471.3948 | 469.843 | 422.5758 | 406.4214
472.3948 | 469.8806 | 423.0924 | 406.9601
473.3948 | 469.7168 | 423.7775 | 407.5834
474.3948 | 469.7128 | 424.3087 | 408.1958
475.3948 | 469.7437 | 424.9305 | 408.8819
476.3948 | 469.8233 | 425.5725 | 409.5436
477.3948 | 469.8081 | 425.9649 | 410.0448
478.3948 | 469.6876 | 426.6592 | 410.6513
479.3948 | 469.5867 | 427.2875 | 411.3711
480.3948 | 469.5129 | 428.0528 | 411.9121
481.3948 | 469.4513 | 428.7734 | 412.6018
482.3948 | 469.4035 | 429.2085 | 413.2034
483.3948 | 469.3024 | 429.8504 | 413.4985
484.3948 | 469.2377 | 430.4034 | 413.5707
485.3948 | 469.2347 | 430.9324 | 413.89
486.3948 | 469.1801 | 431.4369 | 414.2866
487.3948 | 469.2005 | 431.8302 | 414.7199
488.3948 | 469.1676 | 432.702 | 415.1414
489.3948 | 469.1388 | 433.0228 | 415.6145
490.3948 | 469.1033 | 433.5132 | 416.0301
491.3948 | 469.0426 | 433.9959 | 416.5812
492.3948 | 469.0136 | 434.7842 | 417.0119
493.3948 | 469.0121 | 435.2488 | 417.4396
494.3948 | 469.0411 | 435.8358 | 417.8453
495.3948 | 469.0914 | 436.357 | 418.4062
496.3948 | 469.1431 | 436.9501 | 418.8371
497.3948 | 469.1177 | 437.5999 | 419.2718
498.3948 | 469.1262 | 438.0929 | 419.9181
499.3948 | 469.1093 | 438.7208 | 420.4733
500.3948 | 469.0597 | 439.3663 | 421.0171
501.3948 | 468.9365 | 439.8158 | 421.3546
502.3948 | 468.9326 | 440.3527 | 421.9799
503.3948 | 468.954 | 440.9633 | 422.4461
504.3948 | 468.9236 | 441.3886 | 422.9974
505.3948 | 468.8943 | 441.8337 | 423.4257
506.3948 | 468.7624 | 442.4868 | 424.023
507.3948 | 468.7425 | 442.9361 | 424.136
508.3948 | 468.7569 | 443.356 | 424.7526
509.3948 | 468.7883 | 444.0444 | 425.5095
510.3948 | 468.8417 | 444.4072 | 426.1396
511.3948 | 468.8687 | 444.7979 | 426.6818
512.3948 | 468.8778 | 445.2796 | 427.2427
513.3948 | 468.9719 | 445.7681 | 427.7385
514.3948 | 468.9373 | 446.2245 | 428.2252
515.3948 | 468.9059 | 446.5707 | 428.8773
516.3948 | 468.9024 | 447.2077 | 429.6232
517.3948 | 468.8468 | 447.8147 | 430.4636
518.3948 | 468.8524 | 448.2377 | 431.3282
519.3948 | 468.8489 | 448.5611 | 432.027
520.3948 | 468.9238 | 448.9357 | 432.4841
521.3948 | 468.9311 | 449.4493 | 433.5673
522.3948 | 468.9408 | 449.8355 | 434.5216
523.3948 | 468.9531 | 450.3057 | 435.1857
524.3948 | 468.9175 | 450.4086 | 435.496
525.3948 | 468.8722 | 450.8435 | 436.3177
526.3948 | 468.8381 | 451.4305 | 437.7215
527.3948 | 468.843 | 451.7779 | 438.5675
528.3948 | 468.7814 | 452.0064 | 439.4058
529.3948 | 468.6755 | 452.5096 | 440.275
530.3948 | 468.6187 | 453.1179 | 441.5606
531.3948 | 468.5754 | 453.3779 | 442.0887
532.3948 | 468.5477 | 453.7586 | 443.8182
533.3948 | 468.4938 | 453.9609 | 443.71
534.3948 | 468.4671 | 454.439 | 445.0751
535.3948 | 468.4856 | 454.6735 | 445.5418
536.3948 | 468.518 | 455.0002 | 446.3472
537.3948 | 468.4976 | 455.3732 | 447.9311
538.3948 | 468.4992 | 455.9714 | 449.2315
539.3948 | 468.4747 | 456.3983 | 449.9839
540.3948 | 468.4818 | 456.8359 | 450.6181
541.3948 | 468.491 | 456.7962 | 450.8481
542.3948 | 468.5395 | 457.1454 | 451.5709
543.3948 | 468.5891 | 457.6922 | 453.2672
544.3948 | 468.6486 | 458.0042 | 453.7728
545.3948 | 468.6762 | 459.0122 | 459.2293
546.3948 | 468.7619 | 459.1687 | 459.3654
547.3948 | 468.8036 | 459.7285 | 462.2103
548.3948 | 468.8445 | 460.3235 | 465.5995
549.3948 | 468.8601 | 460.5184 | 466.0976
550.3948 | 468.8784 | 460.8306 | 467.3856
551.3948 | 468.8755 | 460.9456 | 469.1942
552.3948 | 468.8961 | 461.6467 | 471.8364
553.3948 | 468.9132 | 461.7518 | 472.3889
554.3948 | 468.8884 | 462.5851 | 473.9116
555.3948 | 468.8762 | 462.5577 | 473.947
556.3948 | 468.8238 | 463.5003 | 478.3369
557.3948 | 468.8464 | 463.8751 | 474.991
558.3948 | 468.8656 | 463.1124 | 472.1749
559.3948 | 468.8964 | 464.1013 | 475.6357
560.3948 | 468.9116 | 464.1615 | 477.6622
561.3948 | 468.9054 | 464.7119 | 477.7835
562.3948 | 468.9562 | 465.844 | 481.508
563.3948 | 469.0061 | 465.8431 | 480.9715
564.3948 | 468.9916 | 466.0304 | 483.731
565.3948 | 468.9475 | 466.3695 | 485.6473
566.3948 | 468.8591 | 466.8305 | 488.0417
567.3948 | 468.7863 | 467.2996 | 488.6398
568.3948 | 468.738 | 467.4138 | 492.9715
569.3948 | 468.7263 | 467.8534 | 492.6956
570.3948 | 468.7062 | 468.8889 | 495.5504
571.3948 | 468.5904 | 469.2319 | 495.9192
572.3948 | 468.5725 | 470.4694 | 496.0988
573.3948 | 468.5443 | 470.1458 | 497.1862
574.3948 | 468.4559 | 469.9868 | 498.1428
575.3948 | 468.32 | 470.3961 | 499.2883
576.3948 | 468.2839 | 470.6313 | 499.6644
577.3948 | 468.2433 | 471.1469 | 499.6861
578.3948 | 468.2049 | 470.8704 | 498.9589
579.3948 | 468.1889 | 470.2016 | 499.7952
580.3948 | 468.1882 | 470.7523 | 498.2221
581.3948 | 468.1712 | 471.2246 | 501.9911
582.3948 | 468.1509 | 472.1483 | 503.126
583.3948 | 468.1365 | 472.8393 | 502.4494
584.3948 | 468.183 | 473.3229 | 505.6795
585.3948 | 468.1954 | 473.7175 | 506.2438
586.3948 | 468.1314 | 473.9218 | 505.1542
587.3948 | 467.9792 | 474.3681 | 501.8567
588.3948 | 467.9597 | 476.0159 | 502.7399
589.3948 | 467.9296 | 475.7049 | 499.7509
590.3948 | 467.8577 | 476.03 | 498.3352
591.3948 | 467.8188 | 464.3463 | 463.9208
592.3948 | 467.783 | 465.3933 | 464.9367
593.3948 | 467.7261 | 465.2323 | 471.1738
594.3948 | 467.6042 | 464.8823 | 468.308
595.3948 | 467.5218 | 463.4924 | 463.3945
596.3948 | 467.5235 | 462.3841 | 463.8118
597.3948 | 467.4175 | 462.0493 | 463.0774
598.3948 | 467.3602 | 462.0724 | 457.8325
599.3948 | 467.254 | 462.1019 | 457.5033
600.3948 | 467.1835 | 462.4835 | 457.6688
601.3948 | 467.0336 | 462.7843 | 460.836
602.3948 | 466.8919 | 460.9132 | 458.1162
603.3948 | 466.787 | 460.164 | 455.9206
604.3948 | 466.6091 | 457.6079 | 455.2313
605.3948 | 466.4324 | 449.3167 | 471.3366
606.3948 | 466.3919 | 453.1078 | 486.4556
607.3948 | 466.3478 | 446.8498 | 480.636
608.3948 | 466.2831 | 441.7735 | 479.7002
609.3948 | 466.1836 | 435.98 | 471.7114
610.3948 | 465.9975 | 436.7881 | 466.7195
611.3948 | 465.8013 | 435.3173 | 466.9939
612.3948 | 465.6131 | 432.8202 | 466.2491
613.3948 | 465.4469 | 437.6363 | 480.7878
614.3948 | 465.2226 | 436.0099 | 489.706
615.3948 | 465.056 | 432.9542 | 459.8063
616.3948 | 464.8404 | 438.7431 | 481.1028
617.3948 | 464.6802 | 429.3142 | 469.3249
618.3948 | 464.5511 | 418.5264 | 453.0655
619.3948 | 464.4267 | 417.2634 | 452.0546
620.3948 | 464.283 | 416.2415 | 452.1082
621.3948 | 464.2125 | 418.7741 | 452.0559
622.3948 | 464.238 | 416.401 | 450.2762
623.3948 | 464.2965 | 408.5311 | 445.5945
624.3948 | 464.2559 | 315.579 | 386.4317
625.3948 | 464.2143 | 364.2247 | 392.0535
626.3948 | 464.1546 | 495.2428 | 520.6423
627.3948 | 464.0539 | 128.3359 | 115.4083
628.3948 | 463.9267 | 397.0558 | 413.062
629.3948 | 463.8221 | 412.9233 | 392.6912
630.3948 | 463.6696 | 413.1915 | 391.1509
631.3948 | 463.4814 | 407.0888 | 394.4836
632.3948 | 463.281 | 404.4391 | 392.2361
633.3948 | 463.019 | 364.7609 | 432.6048
634.3948 | 462.7591 | 355.6093 | 437.3061
635.3948 | 462.5344 | 357.112 | 435.4485
636.3948 | 462.5109 | 353.8595 | 436.8338
637.3948 | 462.5816 | 351.3455 | 437.9705
638.3948 | 462.3088 | 351.6694 | 438.5927
639.3948 | 461.9993 | 350.3173 | 440.2705
640.3948 | 461.7457 | 340.355 | 448.7151
641.3948 | 461.6246 | 343.3214 | 446.3634
642.3948 | 461.4872 | 338.9164 | 447.6748
643.3948 | 461.3519 | 341.6145 | 441.9959
644.3948 | 461.0684 | 338.781 | 440.212
645.3948 | 460.9605 | 337.6819 | 440.8693
646.3948 | 460.9997 | 340.3558 | 440.805
647.3948 | 460.9176 | 335.448 | 442.1911
648.3948 | 460.7661 | 337.0658 | 443.3072
649.3948 | 460.5895 | 337.3244 | 441.4317
650.3948 | 460.3384 | 333.1443 | 440.4714
651.3948 | 460.0522 | 335.2421 | 440.4931
652.3948 | 459.9616 | 337.641 | 440.8302
653.3948 | 460.0313 | 337.3854 | 439.8264
654.3948 | 459.9948 | 340.7968 | 441.7873
655.3948 | 459.8293 | 343.7843 | 442.1973
656.3948 | 459.6546 | 337.3666 | 438.3868
657.3948 | 459.6066 | 338.7082 | 437.0331
658.3948 | 459.5397 | 342.6644 | 436.9967
659.3948 | 459.4471 | 336.5822 | 437.2046
660.3948 | 459.3878 | 340.4658 | 437.9763
661.3948 | 459.3415 | 315.0026 | 459.7853
662.3948 | 459.2323 | 305.1005 | 465.4329
663.3948 | 459.2792 | 302.4326 | 464.8538
664.3948 | 459.4282 | 301.3857 | 465.2189
665.3948 | 459.562 | 302.7707 | 465.6726
666.3948 | 459.6663 | 301.6893 | 465.4284
667.3948 | 459.6806 | 296.4686 | 463.6113
668.3948 | 459.728 | 294.0073 | 463.2052
669.3948 | 459.8208 | 296.9284 | 462.6313
670.3948 | 459.7906 | 297.5512 | 465.8165
671.3948 | 459.9265 | 289.9012 | 463.8213
672.3948 | 460.0019 | 276.737 | 461.2587
673.3948 | 459.9748 | 289.3612 | 458.5524
674.3948 | 459.866 | 290.5535 | 458.2621
675.3948 | 459.8416 | 285.8513 | 457.7882
676.3948 | 459.8251 | 285.5371 | 457.3415
677.3948 | 459.8508 | 276.5793 | 457.3219
678.3948 | 459.8157 | 288.2488 | 460.636
679.3948 | 459.8947 | 277.1087 | 460.9219
680.3948 | 459.9421 | 287.4729 | 461.9097
681.3948 | 459.9909 | 280.6858 | 460.135
682.3948 | 460.1176 | 285.4967 | 463.7074
683.3948 | 460.1227 | 284.7129 | 463.9175
684.3948 | 460.1225 | 290.9077 | 465.9781
685.3948 | 460.1302 | 286.4626 | 465.6619
686.3948 | 460.1815 | 290.9762 | 466.6833
687.3948 | 460.3071 | 291.5757 | 467.0153
688.3948 | 460.4659 | 293.5235 | 467.9146
689.3948 | 460.6347 | 298.8854 | 468.4342
690.3948 | 460.5606 | 286.4528 | 467.5032
691.3948 | 460.6386 | 291.4844 | 469.2399
692.3948 | 460.8386 | 289.345 | 470.4096
693.3948 | 460.8688 | 289.0022 | 469.9444
694.3948 | 460.8526 | 295.1478 | 469.915
695.3948 | 460.8231 | 294.5167 | 471.6608
696.3948 | 460.7642 | 297.39 | 472.2255
697.3948 | 460.7845 | 296.5279 | 472.7383
698.3948 | 460.8556 | 294.198 | 473.0073
699.3948 | 460.9397 | 293.2555 | 474.698
700.3948 | 460.9414 | 292.0944 | 474.9488
701.3948 | 460.939 | 293.421 | 475.6258
702.3948 | 460.9368 | 292.7099 | 475.1958
703.3948 | 460.9131 | 305.847 | 477.4116
704.3948 | 460.9238 | 299.554 | 475.0921
705.3948 | 460.9605 | 292.2886 | 473.9772
706.3948 | 461.0076 | 300.992 | 476.8509
707.3948 | 461.0582 | 305.1445 | 477.9545
708.3948 | 461.1185 | 313.9834 | 479.3003
709.3948 | 461.1269 | 322.5166 | 481.0265
710.3948 | 461.1221 | 327.8665 | 481.9294
711.3948 | 461.1566 | 328.5015 | 482.31
712.3948 | 461.2101 | 342.049 | 484.4443
713.3948 | 461.257 | 338.2175 | 484.5485
714.3948 | 461.2831 | 341.9201 | 485.3688
715.3948 | 461.3247 | 351.1811 | 486.9732
716.3948 | 461.3339 | 354.1222 | 487.9956
717.3948 | 461.3389 | 359.7769 | 489.7306
718.3948 | 461.4115 | 367.8028 | 491.0061
719.3948 | 461.4613 | 371.4961 | 492.4745
720.3948 | 461.5376 | 374.0824 | 493.1165
721.3948 | 461.6222 | 376.1278 | 493.7074
722.3948 | 461.6555 | 374.0664 | 493.628
723.3948 | 461.7475 | 380.3341 | 495.1553
724.3948 | 461.8712 | 378.2041 | 494.8555
725.3948 | 461.9941 | 384.0236 | 496.1909
726.3948 | 462.0989 | 386.3706 | 496.9228
727.3948 | 462.196 | 383.8496 | 496.6449
728.3948 | 462.2776 | 385.4555 | 496.7616
729.3948 | 462.3776 | 386.5558 | 497.4726
730.3948 | 462.567 | 390.812 | 498.9208
731.3948 | 462.7562 | 392.6389 | 499.9821
732.3948 | 462.9452 | 396.2596 | 501.0799
733.3948 | 463.1218 | 398.9116 | 501.6977
734.3948 | 463.2864 | 401.8255 | 503.2699
735.3948 | 463.4543 | 404.4103 | 503.7995
736.3948 | 463.5875 | 405.7684 | 504.2624
737.3948 | 463.7524 | 406.7356 | 504.1557
738.3948 | 463.8354 | 408.2856 | 505.0459
739.3948 | 463.975 | 413.2823 | 506.4735
740.3948 | 464.1038 | 417.5534 | 507.5433
741.3948 | 464.2441 | 420.1056 | 508.4965
742.3948 | 464.3948 | 424.3708 | 509.9822
743.3948 | 464.5394 | 425.812 | 510.7018
744.3948 | 464.6504 | 428.6662 | 511.6227
745.3948 | 464.7332 | 433.797 | 513.2053
746.3948 | 464.862 | 438.1726 | 514.8321
747.3948 | 465.0178 | 445.9225 | 517.565
748.3948 | 465.1128 | 461.3814 | 522.3316
749.3948 | 465.1576 | 466.5977 | 524.2152
750.3948 | 465.2116 | 469.8123 | 525.5932
751.3948 | 465.2554 | 471.7872 | 526.5353
752.3948 | 465.3034 | 472.7696 | 527.4003
753.3948 | 465.333 | 483.5024 | 530.926
754.3948 | 465.3846 | 528.0099 | 544.4127
755.3948 | 465.4325 | 529.4505 | 545.3145
756.3948 | 465.4568 | 530.3816 | 546.166
757.3948 | 465.4915 | 532.4501 | 547.3371
758.3948 | 465.5911 | 533.5775 | 548.4979
759.3948 | 465.6381 | 534.5106 | 549.3877
760.3948 | 465.6453 | 535.7935 | 550.4825
761.3948 | 465.7116 | 537.0363 | 551.5477
762.3948 | 465.7959 | 537.6753 | 552.3277
763.3948 | 465.828 | 538.6654 | 553.2134
764.3948 | 465.8546 | 539.1658 | 553.9429
765.3948 | 465.8897 | 539.9651 | 554.7817
766.3948 | 465.9472 | 540.4531 | 555.4467
767.3948 | 465.9579 | 541.1245 | 556.1136
768.3948 | 465.9934 | 542.1404 | 556.9196
769.3948 | 465.9906 | 543.0516 | 557.7788
770.3948 | 466.0537 | 543.7253 | 558.5376
771.3948 | 466.0481 | 544.6961 | 559.3464
772.3948 | 466.0774 | 545.9494 | 560.3061
773.3948 | 466.1348 | 546.3779 | 560.7752
774.3948 | 466.2108 | 547.0175 | 561.4253
775.3948 | 466.2212 | 547.8131 | 562.1694
776.3948 | 466.1694 | 548.7258 | 562.9681
777.3948 | 466.2358 | 550.1449 | 563.926
778.3948 | 466.2999 | 551.1848 | 564.7639
779.3948 | 466.3515 | 551.7453 | 565.3939
780.3948 | 466.4056 | 552.5491 | 566.0894
781.3948 | 466.417 | 553.0532 | 566.6685
782.3948 | 466.3797 | 553.6183 | 567.1455
783.3948 | 466.3933 | 554.2647 | 567.6921
784.3948 | 466.3999 | 554.8446 | 568.2539
785.3948 | 466.4305 | 555.4639 | 568.8555
786.3948 | 466.5015 | 556.1279 | 569.4627
787.3948 | 466.5724 | 556.676 | 569.9748
788.3948 | 466.6046 | 557.6364 | 570.7363
789.3948 | 466.6519 | 558.4538 | 571.45
790.3948 | 466.672 | 559.2199 | 572.0289
791.3948 | 466.6975 | 559.9007 | 572.7369
792.3948 | 466.67 | 560.7362 | 573.4317
793.3948 | 466.7033 | 561.7243 | 574.2059
794.3948 | 466.7688 | 563.1243 | 575.2698
795.3948 | 466.813 | 564.1773 | 576.0781
796.3948 | 466.8854 | 564.7426 | 576.5387
797.3948 | 466.9598 | 565.265 | 577.0495
798.3948 | 466.9827 | 565.2112 | 577.1466
799.3948 | 466.9896 | 565.6798 | 577.5577
800.3948 | 467.0682 | 566.3181 | 578.0894
801.3948 | 467.1394 | 566.5142 | 578.4161
802.3948 | 467.1766 | 566.4569 | 578.6378
803.3948 | 467.1671 | 567.0587 | 579.2487
804.3948 | 467.1968 | 567.6675 | 579.7873
805.3948 | 467.2124 | 568.1673 | 580.2792
806.3948 | 467.1769 | 568.0837 | 580.4862
807.3948 | 467.1393 | 568.5133 | 580.9564
808.3948 | 467.1364 | 568.6127 | 581.1986
809.3948 | 467.1429 | 569.3222 | 581.7995
810.3948 | 467.1689 | 569.1593 | 581.8653
811.3948 | 467.2081 | 569.635 | 582.3483
812.3948 | 467.2405 | 570.4644 | 583.0352
813.3948 | 467.2665 | 571.2907 | 583.6104
814.3948 | 467.2916 | 571.4921 | 583.9844
815.3948 | 467.3531 | 572.4276 | 584.7448
816.3948 | 467.3846 | 572.6107 | 585.131
817.3948 | 467.4643 | 572.9001 | 585.5432
818.3948 | 467.495 | 573.0841 | 585.9672
819.3948 | 467.4694 | 573.3345 | 586.3366
820.3948 | 467.5388 | 573.5233 | 586.6766
821.3948 | 467.5906 | 573.689 | 587.0567
822.3948 | 467.636 | 573.7777 | 587.3706
823.3948 | 467.6731 | 573.7987 | 587.6716
824.3948 | 467.7258 | 573.9423 | 587.9299
825.3948 | 467.7481 | 574.1774 | 588.2188
826.3948 | 467.7986 | 574.4542 | 588.5745
827.3948 | 467.7837 | 574.6135 | 588.8355
828.3948 | 467.7643 | 574.9901 | 589.2149
829.3948 | 467.7925 | 575.0864 | 589.3406
830.3948 | 467.8405 | 575.2305 | 589.5678
831.3948 | 467.8519 | 575.4571 | 589.8961
832.3948 | 467.8764 | 575.7082 | 590.2082
833.3948 | 467.8952 | 576.4233 | 590.8565
834.3948 | 467.8742 | 576.2138 | 590.875
835.3948 | 467.818 | 576.2303 | 591.0706
836.3948 | 467.804 | 576.503 | 591.3507
837.3948 | 467.7997 | 576.5798 | 591.5374
838.3948 | 467.795 | 577.0225 | 592.0226
839.3948 | 467.8058 | 576.9094 | 592.0488
840.3948 | 467.81 | 577.1781 | 592.4213
841.3948 | 467.8725 | 577.5735 | 592.8779
842.3948 | 467.8869 | 577.8654 | 593.2056
843.3948 | 467.9234 | 578.0477 | 593.412
844.3948 | 467.8597 | 578.1991 | 593.6188
845.3948 | 467.8133 | 578.3031 | 593.9275
846.3948 | 467.8423 | 578.4603 | 594.2445
847.3948 | 467.8767 | 578.6248 | 594.6812
848.3948 | 467.9339 | 578.7378 | 594.9916
849.3948 | 467.9212 | 578.7507 | 595.1858
850.3948 | 467.925 | 578.7966 | 595.4471
851.3948 | 467.9696 | 579.0456 | 595.75
852.3948 | 467.9611 | 579.2728 | 596.071
853.3948 | 468.0125 | 579.7004 | 596.4637
854.3948 | 467.9995 | 580.1447 | 596.7933
855.3948 | 468.0365 | 580.4038 | 597.129
856.3948 | 468.0401 | 580.4791 | 597.3172
857.3948 | 468.0219 | 580.6223 | 597.5422
858.3948 | 468.0649 | 581.0073 | 597.7412
859.3948 | 468.1211 | 582.0397 | 598.6034
860.3948 | 468.142 | 582.0849 | 598.6251
861.3948 | 468.1845 | 582.2758 | 598.8472
862.3948 | 468.1927 | 582.4398 | 598.9773
863.3948 | 468.1522 | 582.4203 | 599.0989
864.3948 | 468.1762 | 582.5956 | 599.2774
865.3948 | 468.1805 | 582.6364 | 599.5635
866.3948 | 468.1805 | 582.9912 | 599.9916
867.3948 | 468.1727 | 583.2088 | 600.1363
868.3948 | 468.2203 | 583.3026 | 600.2908
869.3948 | 468.2516 | 583.5084 | 600.4871
870.3948 | 468.2505 | 583.5658 | 600.5678
871.3948 | 468.3497 | 583.712 | 600.822
872.3948 | 468.4704 | 583.9596 | 600.9719
873.3948 | 468.5374 | 584.0755 | 601.2363
874.3948 | 468.5552 | 584.2629 | 601.4742
875.3948 | 468.5759 | 584.3724 | 601.5883
876.3948 | 468.6081 | 584.516 | 601.7261
877.3948 | 468.6225 | 584.6745 | 602.0069
878.3948 | 468.6135 | 585.0509 | 602.2885
879.3948 | 468.5662 | 585.0943 | 602.3745
880.3948 | 468.5673 | 585.1394 | 602.5334
881.3948 | 468.6168 | 585.2775 | 602.7245
882.3948 | 468.6543 | 585.4012 | 602.9379
883.3948 | 468.6269 | 585.5121 | 603.06
884.3948 | 468.7084 | 585.5978 | 603.2443
885.3948 | 468.7762 | 585.5996 | 603.2982
886.3948 | 468.8199 | 585.8868 | 603.53
887.3948 | 468.817 | 586.0408 | 603.6012
888.3948 | 468.8071 | 586.0277 | 603.5865
889.3948 | 468.8578 | 586.0117 | 603.5373
890.3948 | 468.9032 | 585.9751 | 603.4469
891.3948 | 468.8764 | 586.361 | 603.731
892.3948 | 468.89 | 586.2797 | 603.8257
893.3948 | 468.942 | 586.1395 | 603.8261
894.3948 | 468.9771 | 586.2932 | 603.9486
895.3948 | 468.9986 | 586.6406 | 604.2567
896.3948 | 468.9658 | 586.7523 | 604.3752
897.3948 | 469.0013 | 586.8228 | 604.5978
898.3948 | 469.0749 | 586.813 | 604.5885
899.3948 | 469.0856 | 586.749 | 604.5704
900.3948 | 469.0472 | 586.8331 | 604.5864
901.3948 | 469.079 | 587.0485 | 604.8306
902.3948 | 469.047 | 587.239 | 605.0283
903.3948 | 469.0612 | 587.1181 | 605.1232
904.3948 | 469.1301 | 587.1184 | 605.1382
905.3948 | 469.1497 | 587.0023 | 605.1948
906.3948 | 469.1811 | 587.2107 | 605.3714
907.3948 | 469.1832 | 587.1667 | 605.3815
908.3948 | 469.1295 | 587.107 | 605.5393
909.3948 | 469.1418 | 587.1566 | 605.6631
910.3948 | 469.2326 | 587.1713 | 606.0168
911.3948 | 469.3279 | 587.3787 | 606.5584
912.3948 | 469.3564 | 587.4752 | 606.8179
913.3948 | 469.3595 | 587.4563 | 606.9956
914.3948 | 469.3618 | 587.6297 | 607.1952
915.3948 | 469.3946 | 587.6576 | 607.1908
916.3948 | 469.4966 | 587.8075 | 607.3118
917.3948 | 469.5249 | 587.7194 | 607.3238
918.3948 | 469.5266 | 587.8898 | 607.5413
919.3948 | 469.5428 | 588.0458 | 607.6349
920.3948 | 469.5537 | 587.9405 | 607.6927
921.3948 | 469.5801 | 588.3909 | 608.022
922.3948 | 469.5695 | 588.5486 | 608.0992
923.3948 | 469.6121 | 588.5886 | 607.9971
924.3948 | 469.6585 | 589.2059 | 608.7397
925.3948 | 469.6358 | 589.288 | 608.8098
926.3948 | 469.6428 | 589.6406 | 609.1674
927.3948 | 469.6631 | 590.0834 | 609.56
928.3948 | 469.717 | 590.1508 | 609.7834
929.3948 | 469.8133 | 591.0278 | 610.3221
930.3948 | 469.8861 | 591.1416 | 610.3594
931.3948 | 469.8239 | 591.3233 | 610.5863
932.3948 | 469.8084 | 591.6237 | 610.559
933.3948 | 469.7762 | 591.8391 | 610.6713
934.3948 | 469.7728 | 591.8803 | 610.7307
935.3948 | 469.8108 | 591.7938 | 610.5679
936.3948 | 469.8359 | 591.9161 | 610.6435
937.3948 | 469.8881 | 592.0372 | 610.7694
938.3948 | 469.93 | 591.9712 | 610.7569
939.3948 | 469.9863 | 591.9348 | 610.6517
940.3948 | 469.9087 | 591.9378 | 610.6824
941.3948 | 469.9484 | 592.3265 | 610.9923
942.3948 | 469.9387 | 592.2839 | 611.1708
943.3948 | 469.9309 | 592.6776 | 611.4445
944.3948 | 469.8904 | 587.3402 | 607.9933
945.3948 | 469.9097 | 592.2544 | 611.5019
946.3948 | 469.8447 | 592.4665 | 611.9262
947.3948 | 469.8323 | 587.8527 | 608.8076
948.3948 | 469.7874 | 592.8879 | 612.2693
949.3948 | 469.7565 | 593.1471 | 612.4679
950.3948 | 469.7216 | 593.2792 | 612.7
951.3948 | 469.6992 | 593.4347 | 612.8905
952.3948 | 469.7567 | 593.5534 | 613.0985
953.3948 | 469.7673 | 593.2793 | 612.9086
954.3948 | 469.7187 | 593.9095 | 613.443
955.3948 | 469.7943 | 589.9064 | 610.7961
956.3948 | 469.8332 | 594.3346 | 613.8969
957.3948 | 469.8483 | 593.6587 | 613.5322
958.3948 | 469.8482 | 590.5785 | 611.3517
959.3948 | 469.8484 | 594.7243 | 614.3322
960.3948 | 469.825 | 591.422 | 612.0175
961.3948 | 469.8251 | 593.1245 | 613.3044
962.3948 | 469.8493 | 593.5798 | 613.7911
963.3948 | 469.8412 | 592.7186 | 613.3453
964.3948 | 469.8954 | 593.4718 | 613.8817
965.3948 | 469.9011 | 595.5868 | 615.5436
966.3948 | 469.9469 | 594.7296 | 615.1775
967.3948 | 469.9658 | 592.1979 | 613.6801
968.3948 | 469.954 | 591.9908 | 613.8916
969.3948 | 469.9173 | 595.8517 | 616.8228
970.3948 | 469.9008 | 590.6559 | 613.2759
971.3948 | 469.9569 | 595.9825 | 617.3474
972.3948 | 469.9271 | 592.0266 | 614.7621
973.3948 | 469.9159 | 591.8784 | 614.9008
974.3948 | 469.9772 | 595.3023 | 617.5594
975.3948 | 470.0732 | 587.9767 | 612.5597
976.3948 | 470.1237 | 596.4164 | 618.8337
977.3948 | 470.1068 | 594.6708 | 617.823
978.3948 | 470.0977 | 592.9571 | 616.6905
979.3948 | 470.1121 | 595.3122 | 618.6085
980.3948 | 470.1393 | 595.7197 | 618.8938
981.3948 | 470.1315 | 593.8534 | 617.5557
982.3948 | 470.1603 | 595.4222 | 618.724
983.3948 | 470.2255 | 593.2531 | 617.4708
984.3948 | 470.2485 | 593.7072 | 617.9228
985.3948 | 470.2423 | 597.0238 | 620.5088
986.3948 | 470.1977 | 597.6743 | 621.0459
987.3948 | 470.1702 | 593.7769 | 618.2768
988.3948 | 470.2263 | 587.9495 | 613.9451
989.3948 | 470.2875 | 589.2019 | 614.9391
990.3948 | 470.3818 | 597.8402 | 621.5663
991.3948 | 470.4368 | 597.5464 | 621.4797
992.3948 | 470.4225 | 597.6625 | 621.6835
993.3948 | 470.4303 | 596.4417 | 621.0405
994.3948 | 470.4242 | 595.5234 | 620.6225
995.3948 | 470.4371 | 593.0752 | 618.8651
996.3948 | 470.4758 | 597.4479 | 622.2661
997.4104 | 470.5074 | 593.367 | 619.4558
998.3948 | 470.5596 | 591.3667 | 618.0364
999.3948 | 470.6276 | 591.039 | 618.1309
1000.3948 | 470.6842 | 591.3105 | 618.6259
1001.3948 | 470.693 | 594.6698 | 621.2652
1002.3948 | 470.7518 | 594.4023 | 621.1694
1003.3948 | 470.7052 | 594.6465 | 621.3304
1004.3948 | 470.6687 | 593.8479 | 620.7828
1005.3948 | 470.6333 | 598.2034 | 624.1822
1006.3948 | 470.6136 | 594.7491 | 621.6267
1007.3948 | 470.6087 | 598.9591 | 624.9288
1008.3948 | 470.6405 | 599.2266 | 625.0993
1009.3948 | 470.7054 | 598.702 | 624.6672
1010.3948 | 470.7012 | 595.3756 | 622.2944
1011.3948 | 470.6966 | 590.4145 | 618.5174
1012.3948 | 470.6566 | 598.1156 | 624.4618
1013.3948 | 470.599 | 599.3878 | 625.5936
1014.3948 | 470.5391 | 600.0592 | 626.1427
1015.3948 | 470.5531 | 599.5041 | 625.7567
1016.3948 | 470.5198 | 597.1565 | 624.1424
1017.3948 | 470.4512 | 590.2804 | 618.8308
1018.3948 | 470.474 | 598.3146 | 625.0885
1019.3948 | 470.5031 | 600.3094 | 626.6838
1020.3948 | 470.5906 | 600.2027 | 626.5356
1021.3948 | 470.6936 | 598.0304 | 624.7785
1022.3948 | 470.729 | 598.5799 | 625.1718
1023.3948 | 470.8027 | 598.3311 | 625.1046
1024.3948 | 470.897 | 599.4738 | 626.0504
1025.3948 | 470.928 | 600.6967 | 626.9642
1026.3948 | 470.9854 | 600.4615 | 626.6623
1027.3948 | 470.9803 | 599.5851 | 625.9475
1028.3948 | 471.0917 | 597.7012 | 624.7191
1029.3948 | 471.1528 | 592.5371 | 620.6426
1030.3948 | 471.1681 | 592.673 | 620.6442
1031.3948 | 471.1789 | 590.9632 | 619.1645
1032.3948 | 471.1711 | 591.979 | 619.7539
1033.3948 | 471.1715 | 600.6451 | 626.4899
1034.3948 | 471.0576 | 597.6061 | 624.0806
1035.3948 | 471.1318 | 594.419 | 621.6063
1036.3948 | 471.0469 | 589.4435 | 617.6229
1037.3948 | 470.8577 | 596.3771 | 623.0289
1038.3948 | 470.5704 | 600.8725 | 626.624
1039.3948 | 470.1848 | 599.3157 | 625.5772
1040.3948 | 469.804 | 600.4315 | 626.4448
1041.3948 | 469.479 | 601.5208 | 627.4025
1042.3948 | 469.0678 | 600.6589 | 626.6547
1043.3948 | 468.5797 | 596.2045 | 622.8947
1044.3948 | 468.0979 | 598.9736 | 625.0882
1045.3948 | 467.4998 | 600.5044 | 626.2809
1046.3948 | 466.9727 | 601.5595 | 627.3744
1047.3948 | 466.4715 | 600.5748 | 626.9773
1048.3948 | 465.8843 | 597.2769 | 624.6437
1049.3948 | 465.2787 | 590.1409 | 619.0176
1050.3948 | 464.7048 | 595.8706 | 623.6939
1051.3948 | 464.1095 | 597.1805 | 624.8751
1052.3948 | 463.504 | 599.8779 | 627.049
1053.3948 | 462.937 | 599.0881 | 626.5231
1054.3948 | 462.3389 | 600.6107 | 627.6563
1055.3948 | 461.692 | 601.531 | 628.2159
1056.3948 | 461.0928 | 601.5084 | 628.256
1057.3948 | 460.554 | 600.0209 | 627.2379
1058.3948 | 460.0005 | 599.6353 | 626.9332
1059.3948 | 459.3639 | 601.7353 | 628.6931
1060.3948 | 458.7649 | 601.6033 | 628.5042
1061.3948 | 458.1648 | 599.1394 | 626.6125
1062.3948 | 457.6164 | 600.0658 | 627.4042
1063.3948 | 457.0422 | 599.2026 | 626.8381
1064.3948 | 456.4172 | 599.7829 | 627.5162
1065.3948 | 455.8156 | 598.5254 | 627.1252
1066.3948 | 455.2115 | 599.0349 | 627.7352
1067.3948 | 454.5437 | 598.9837 | 627.7954
1068.3948 | 453.8811 | 601.012 | 629.4442
1069.3948 | 453.24 | 600.7442 | 629.4541
1070.3948 | 452.6378 | 598.5741 | 627.7748
1071.3948 | 452.0039 | 595.2481 | 625.1803
1072.3948 | 451.4085 | 589.7733 | 620.7417
1073.3948 | 450.8591 | 593.1415 | 623.5617
1074.3948 | 450.313 | 596.0625 | 625.6906
1075.3948 | 449.6709 | 596.0227 | 625.7748
1076.3948 | 449.0305 | 600.4353 | 629.4002
1077.3948 | 448.3906 | 600.1025 | 629.0841
1078.3948 | 447.7082 | 595.4194 | 625.3052
1079.3948 | 447.1038 | 596.6254 | 626.2916
1080.3948 | 446.5302 | 597.5908 | 627.22
1081.3948 | 445.909 | 591.9207 | 622.7241
1082.3948 | 445.287 | 594.4187 | 624.6034
1083.3948 | 444.7339 | 597.8052 | 627.2189
1084.3948 | 444.0785 | 588.236 | 619.4888
1085.3948 | 443.494 | 589.847 | 621.0102
1086.3948 | 442.8958 | 593.7952 | 624.1924
1087.3948 | 442.2861 | 594.2751 | 624.6647
1088.3948 | 441.6822 | 595.052 | 625.2526
1089.3948 | 441.1026 | 596.6745 | 626.5852
1090.3948 | 440.5099 | 597.1887 | 626.9686
1091.3948 | 439.8764 | 596.5777 | 626.4052
1092.3948 | 439.3084 | 597.8651 | 627.5469
1093.3948 | 438.6919 | 594.626 | 625.0104
1094.3948 | 438.1481 | 594.9982 | 625.2179
1095.3948 | 437.5353 | 597.605 | 627.3627
1096.3948 | 436.9125 | 596.7985 | 626.8608
1097.3948 | 436.2989 | 593.1415 | 624.083
1098.3948 | 435.7029 | 595.8067 | 626.6118
1099.3948 | 435.0834 | 597.3883 | 627.9784
1100.3948 | 434.4959 | 595.3824 | 626.2863
1101.3948 | 433.9005 | 593.2669 | 624.5457
1102.3948 | 433.3172 | 596.3411 | 627.0764
1103.3948 | 432.6885 | 594.1751 | 625.4433
1104.3948 | 432.1444 | 593.6646 | 625.2269
1105.3948 | 431.6071 | 589.504 | 622.0909
1106.3948 | 431.0559 | 591.3843 | 623.7809
1107.3948 | 430.4737 | 591.6826 | 624.1111
1108.3948 | 429.8802 | 595.4623 | 627.0842
1109.3948 | 429.3141 | 593.4392 | 625.4989
1110.3948 | 428.7148 | 595.4913 | 627.1241
1111.3948 | 428.0683 | 593.9958 | 625.8829
1112.3948 | 427.4741 | 591.6866 | 624.0454
1113.3948 | 426.9175 | 592.3555 | 624.6665
1114.3948 | 426.3566 | 590.1738 | 623.1226
1115.3948 | 425.8109 | 592.0328 | 624.5812
1116.3948 | 425.2122 | 593.5044 | 625.6615
1117.3948 | 424.5582 | 589.6449 | 622.4261
1118.3948 | 423.9578 | 590.4939 | 623.1681
1119.3948 | 423.3394 | 589.9237 | 622.8104
1120.3948 | 422.7542 | 593.3565 | 625.5616
1121.3948 | 422.2346 | 591.6707 | 624.1893
1122.3948 | 421.6814 | 592.9826 | 625.4318
1123.3948 | 421.1647 | 593.6638 | 625.9938
1124.3948 | 420.5866 | 591.7274 | 624.6964
1125.3948 | 419.9844 | 589.7199 | 623.0266
1126.3948 | 419.4475 | 591.368 | 624.3801
1127.3948 | 418.8369 | 590.4121 | 623.8847
1128.3948 | 418.2529 | 592.9439 | 626.0779
1129.3948 | 417.6678 | 592.8307 | 625.8082
1130.3948 | 417.1094 | 591.8745 | 625.0926
1131.3948 | 416.5935 | 590.3115 | 623.5499
1132.3948 | 416.0785 | 581.217 | 615.9393
1133.3948 | 415.5768 | 591.1228 | 623.8992
1134.3948 | 415.0492 | 588.0804 | 621.4193
1135.3948 | 414.5234 | 587.5006 | 620.6455
1136.3948 | 413.991 | 583.4644 | 617.3338
1137.3948 | 413.4114 | 586.8553 | 619.7265
1138.3948 | 412.8132 | 587.2787 | 619.7564
1139.3948 | 412.2308 | 589.0436 | 621.0462
1140.3948 | 411.644 | 588.9548 | 621.0237
1141.3948 | 411.0904 | 590.3071 | 621.6676
1142.3948 | 410.5906 | 589.6431 | 620.9119
1143.3948 | 410.0023 | 587.9885 | 619.4444
1144.3948 | 409.4363 | 589.5662 | 620.5044
1145.3948 | 408.9109 | 589.0228 | 619.7144
1146.3948 | 408.3825 | 588.3592 | 618.9937
1147.3948 | 407.7957 | 586.3361 | 617.3172
1148.3948 | 407.1835 | 588.6043 | 619.0461
1149.3948 | 406.5771 | 587.0783 | 617.6533
1150.3948 | 406.0541 | 578.4645 | 610.6648
1151.3948 | 405.5135 | 588.1746 | 618.175
1152.3948 | 404.9821 | 587.4449 | 617.331
1153.3948 | 404.4256 | 587.1423 | 616.65
1154.3948 | 403.9234 | 582.68 | 612.8595
1155.3948 | 403.3953 | 583.7488 | 613.4277
1156.3948 | 402.8705 | 585.7226 | 614.9603
1157.3948 | 402.3051 | 586.9174 | 615.7397
1158.3948 | 401.7848 | 586.1711 | 614.9007
1159.3948 | 401.2114 | 582.3571 | 611.5274
1160.3948 | 400.7126 | 584.9903 | 613.3567
1161.3948 | 400.2309 | 583.4058 | 611.695
1162.3948 | 399.6954 | 584.4031 | 611.916
1163.3948 | 399.1394 | 585.1161 | 611.9929
1164.3948 | 398.5856 | 582.1993 | 609.3623
1165.3948 | 398.0695 | 583.6456 | 610.1449
1166.3948 | 397.5625 | 581.9869 | 608.5083
1167.3948 | 397.0494 | 583.4594 | 609.3642
1168.3948 | 396.5476 | 583.9842 | 609.5326
1169.3948 | 395.9766 | 581.05 | 606.5922
1170.3948 | 395.4578 | 582.9677 | 607.3052
1171.3948 | 394.9215 | 582.5642 | 606.3139
1172.3948 | 394.4155 | 583.1956 | 606.2383
1173.3948 | 393.8858 | 582.6873 | 605.289
1174.3948 | 393.3387 | 573.2775 | 597.4282
1175.3948 | 392.8447 | 579.6983 | 601.7715
1176.3948 | 392.3462 | 573.3831 | 596.4236
1177.3948 | 391.8495 | 579.331 | 600.2408
1178.3948 | 391.3798 | 577.4373 | 598.1929
1179.3948 | 390.8613 | 580.3907 | 599.8871
1180.3948 | 390.3567 | 579.7914 | 598.8311
1181.3948 | 389.8283 | 574.796 | 594.3939
1182.3948 | 389.3015 | 578.8545 | 596.7967
1183.3948 | 388.8275 | 579.5519 | 596.6997
1184.3948 | 388.3476 | 579.208 | 595.8528
1185.3948 | 387.8323 | 577.3837 | 593.9055
1186.3948 | 387.3438 | 575.0291 | 591.6319
1187.3948 | 386.8749 | 576.5466 | 592.2607
1188.3948 | 386.4166 | 571.1965 | 587.7811
1189.3948 | 385.9362 | 577.2446 | 591.6776
1190.3948 | 385.4151 | 577.3859 | 591.1697
1191.3948 | 384.9456 | 579.0526 | 591.7488
1192.3948 | 384.5012 | 577.5135 | 590.018
1193.3948 | 383.9274 | 576.9928 | 589.0349
1194.3948 | 383.4238 | 575.8613 | 587.6169
1195.3948 | 382.9213 | 574.6653 | 586.1871
1196.3948 | 382.4228 | 577.4414 | 587.5983
1197.3948 | 381.9088 | 576.9989 | 586.653
1198.3948 | 381.4581 | 573.2095 | 583.2157
1199.3948 | 381.0026 | 566.8085 | 577.9015
1200.3948 | 380.4901 | 574.9513 | 583.2324
1201.3948 | 379.9833 | 564.5463 | 575.0875
1202.3948 | 379.5053 | 569.6219 | 578.218
1203.3948 | 378.997 | 571.0356 | 578.6699
1204.3948 | 378.4848 | 575.1295 | 581.165
1205.3948 | 377.9947 | 570.4523 | 577.1974
1206.3948 | 377.552 | 569.7847 | 576.1891
1207.3948 | 377.0781 | 573.1067 | 578.0916
1208.3948 | 376.6322 | 571.6269 | 576.4893
1209.3948 | 376.254 | 573.171 | 576.9834
1210.3948 | 375.7948 | 574.0791 | 577.0456
1211.3948 | 375.3281 | 573.247 | 575.8875
1212.3948 | 374.8402 | 571.3013 | 573.9899
1213.3948 | 374.3241 | 568.908 | 571.7291
1214.3948 | 373.8479 | 570.638 | 572.4649
1215.3948 | 373.3834 | 571.49 | 572.5646
1216.3948 | 372.9481 | 570.3233 | 571.2365
1217.3948 | 372.477 | 570.2149 | 570.733
1218.3948 | 372.015 | 569.0898 | 569.5167
1219.3948 | 371.5994 | 569.9661 | 569.7336
1220.3948 | 371.1245 | 570.5156 | 569.6605
1221.3948 | 370.6541 | 570.9168 | 569.4113
1222.3948 | 370.1492 | 568.7769 | 567.4874
1223.3948 | 369.7023 | 570.7042 | 568.2515
1224.3948 | 369.2454 | 568.2883 | 566.0755
1225.3948 | 368.7623 | 568.9346 | 566.017
1226.3948 | 368.2747 | 567.3755 | 564.5078
1227.3948 | 367.859 | 569.3182 | 565.3416
1228.3948 | 367.4291 | 566.8087 | 563.2296
1229.3948 | 366.9094 | 566.4797 | 562.5378
1230.3948 | 366.4043 | 559.5639 | 557.4349
1231.3948 | 365.9447 | 568.1879 | 562.8571
1232.3948 | 365.5344 | 567.4636 | 561.9304
1233.3948 | 365.0973 | 567.1597 | 561.2101
1234.3948 | 364.6731 | 556.3643 | 553.5221
1235.3948 | 364.2912 | 565.4147 | 559.0009
1236.4104 | 363.8585 | 565.2767 | 558.4366
1237.3948 | 363.4033 | 566.8633 | 559.1266
1238.3948 | 362.9478 | 566.0191 | 558.1164
1239.3948 | 362.4793 | 564.5748 | 556.7653
1240.3948 | 362.0147 | 562.764 | 555.1486
1241.3948 | 361.5764 | 565.5864 | 556.3939
1242.3948 | 361.1339 | 564.0507 | 554.9675
1243.3948 | 360.6866 | 560.445 | 552.1903
1244.3948 | 360.2498 | 563.6036 | 553.7762
1245.3948 | 359.8169 | 564.2011 | 553.9485
1246.3948 | 359.372 | 553.6952 | 546.8726
1247.3948 | 358.9283 | 564.6194 | 553.2811
1248.3948 | 358.5042 | 563.8731 | 552.3732
1249.3948 | 358.0806 | 562.7278 | 551.2153
1250.3948 | 357.648 | 558.9175 | 548.468
1251.3948 | 357.2355 | 563.0766 | 550.65
1252.3948 | 356.7643 | 558.3347 | 547.3276
1253.3948 | 356.3482 | 562.7193 | 549.6227
1254.3948 | 355.909 | 557.8323 | 546.2864
1255.3948 | 355.4598 | 562.2544 | 548.4569
1256.3948 | 355.0745 | 560.192 | 546.9219
1257.3948 | 354.632 | 560.322 | 546.5994
1258.3948 | 354.2201 | 561.9619 | 547.1368
1259.3948 | 353.8061 | 559.8831 | 545.4382
1260.3948 | 353.3842 | 557.5728 | 543.6432