## Test Conditions
DESIREE-FIRE Test Number 2 - Circuit Simulator Data Only
Test Date: | 2009-07-17
DCSim DAQ Start Time | 14:00
DCSim Time for Synchronization | 14:00
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 13:59
Fire Time | 14:01
Offset | 0:01 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 61 | seconds
Heat Source Offset | 0:02 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 108 | seconds
Heat Source Stop Time | 14:12
Test Duration | 0:11 | hour:minutes:seconds
| 687 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SOV 2 | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.76562 | 123.6191 | -66.8793 | 56.4102 | 0.079707 | 0.0023358 | 0.00029306 | 0.058738 | 0.00027203 | 0.058979 | 0.081635 | 5.2637e-05 | 0.00055508 | 0.067042 | -0.0085783 | 0.066989 | -66.9396 | 0.0243 | -66.8925 | 56.4304 | 56.1151 | 56.4496 | -66.7505 | -66.958 | 0.018674 | -67.02 | 56.3771 | 56.4816 | 55.9629 | -67.1935 | 0.12876 | 0.020179 | -0.060289 | -0.013238 | -0.142 | -0.29514 | 0.039403 | -0.31418 | -0.033111 | -0.078733 | -0.14071 | 0.17347 | 0.071394 | -0.44737 | 123.3097 | 122.9944 | 123.3289 | 66.9036 | -123.1607 | 123.2564 | 123.3609 | 122.8421 | 66.8979 | -123.6037
0.23438 | 123.6603 | -66.8884 | 56.4285 | 0.064445 | 0.0023358 | 0.00029306 | 0.058738 | -0.00079597 | 0.055774 | 0.081635 | 0.0021886 | -0.00051292 | 0.064905 | -0.0043053 | 0.066989 | -66.9304 | 0.019721 | -66.8971 | 56.435 | 56.1471 | 56.4542 | -66.8329 | -66.9488 | 0.018674 | -67.0154 | 56.3771 | 56.4862 | 55.9629 | -67.1889 | 0.055493 | 0.006446 | -0.041977 | -0.00866 | -0.064153 | -0.2814 | 0.02567 | -0.30045 | -0.051422 | -0.06042 | -0.12698 | 0.17347 | 0.057662 | -0.46568 | 123.3234 | 123.0356 | 123.3426 | 66.9081 | -123.2615 | 123.2655 | 123.3746 | 122.8513 | 66.9071 | -123.6174
1.2344 | 123.6328 | -66.8838 | 56.4423 | 0.064445 | 0.0012678 | 0.0013621 | 0.059806 | 0.001341 | 0.057911 | 0.081635 | 0.0011206 | 0.0016231 | 0.067042 | -0.0032363 | 0.064853 | -66.9304 | 0.0243 | -66.8925 | 56.4396 | 56.1883 | 56.445 | -66.7001 | -66.9534 | 0.027831 | -67.0108 | 56.3725 | 56.477 | 55.9674 | -67.1935 | 0.1837 | -0.002708 | -0.046555 | -0.00866 | -0.19236 | -0.25392 | 0.00278 | -0.3096 | -0.069733 | -0.069577 | -0.12698 | 0.18263 | 0.034772 | -0.47483 | 123.3234 | 123.0722 | 123.3289 | 66.9081 | -123.1424 | 123.2564 | 123.3609 | 122.8513 | 66.9117 | -123.6357
2.2344 | 123.555 | -66.9296 | 56.4468 | 0.049183 | 0.0012678 | 0.0024301 | 0.058738 | 0.00027203 | 0.055774 | 0.051113 | 0.0021886 | 0.00055508 | 0.065973 | -0.0064413 | 0.066989 | -66.935 | 0.0243 | -66.9108 | 56.4396 | 56.1609 | 56.4405 | -66.7688 | -66.9534 | 0.023253 | -67.02 | 56.3725 | 56.4862 | 55.9674 | -67.1935 | 0.1608 | -0.007285 | -0.005357 | 0.018803 | -0.14199 | -0.28597 | -0.006375 | -0.26383 | -0.07431 | -0.023801 | -0.090357 | 0.17347 | 0.039352 | -0.47941 | 123.3692 | 123.0905 | 123.3701 | 66.9539 | -123.2157 | 123.3022 | 123.4158 | 122.8971 | 66.9529 | -123.6403
3.2344 | 123.642 | -66.8884 | 56.4468 | 0.079707 | 0.0023358 | 0.0013621 | 0.05767 | 0.00027203 | 0.056843 | 0.066374 | 0.0011206 | 0.0016231 | 0.067042 | -0.0064413 | 0.065921 | -66.935 | 0.028878 | -66.8971 | 56.4304 | 56.1929 | 56.4496 | -66.7276 | -66.9534 | 0.023253 | -67.02 | 56.3771 | 56.4816 | 55.9857 | -67.1935 | 0.16081 | -0.016442 | -0.046555 | -0.00866 | -0.16947 | -0.25392 | 0.002782 | -0.30503 | -0.069732 | -0.064999 | -0.13155 | 0.17347 | 0.034773 | -0.46109 | 123.3188 | 123.0813 | 123.338 | 66.9173 | -123.1745 | 123.2655 | 123.37 | 122.8742 | 66.9117 | -123.6403
4.2344 | 123.6603 | -66.8976 | 56.4148 | 0.049183 | -0.00086922 | 0.0024301 | 0.05767 | -0.001864 | 0.056843 | 0.081635 | -0.0010164 | -0.00051292 | 0.064905 | -0.0064413 | 0.065921 | -66.9396 | 0.019721 | -66.9154 | 56.4441 | 56.3303 | 56.4588 | -67.0756 | -66.958 | 0.023253 | -67.0108 | 56.3725 | 56.4816 | 56.4024 | -67.1889 | -0.17804 | 0.029336 | -0.041978 | -0.017818 | 0.16022 | -0.084506 | 0.043982 | -0.29129 | -0.042267 | -0.060422 | -0.11324 | 0.17805 | 0.066816 | -0.012397 | 123.3417 | 123.2279 | 123.3564 | 66.9173 | -123.4904 | 123.2701 | 123.3792 | 123.3 | 66.9208 | -123.6037
5.2344 | 123.5825 | -66.9022 | 56.456 | 0.064445 | 0.0012678 | 0.0013621 | 0.056601 | 0.00027203 | 0.056843 | 0.066374 | 0.0011206 | 0.0016231 | 0.067042 | -0.0043053 | 0.066989 | -66.9304 | 0.028878 | -66.8971 | 56.4396 | 56.1929 | 56.445 | -66.8604 | -66.9488 | 0.023253 | -67.0062 | 56.3725 | 56.4862 | 56.0682 | -67.198 | 0.041753 | -0.016441 | -0.028244 | 0.005073 | -0.03668 | -0.26307 | -0.010953 | -0.29587 | -0.083466 | -0.046687 | -0.10409 | 0.19179 | 0.030196 | -0.38783 | 123.3417 | 123.0951 | 123.3472 | 66.931 | -123.3164 | 123.2747 | 123.3884 | 122.9703 | 66.9254 | -123.654
6.2344 | 123.5733 | -66.9113 | 56.456 | 0.049183 | 0.0034038 | 0.0034981 | 0.05767 | 0.001341 | 0.057911 | 0.066374 | 0.0021886 | 0.0016231 | 0.067042 | -0.0064413 | 0.065921 | -66.935 | 0.019721 | -66.8879 | 56.435 | 56.17 | 56.4496 | -66.8833 | -66.9534 | 0.023253 | -67.0154 | 56.3817 | 56.4862 | 56.1094 | -67.1843 | 0.028013 | -0.02102 | -0.023667 | 0.023384 | -0.004629 | -0.28597 | -0.006374 | -0.27298 | -0.074309 | -0.042111 | -0.10409 | 0.16889 | 0.030196 | -0.34663 | 123.3463 | 123.0813 | 123.3609 | 66.931 | -123.3393 | 123.293 | 123.3975 | 123.0207 | 66.9346 | -123.6403
7.2344 | 123.5367 | -66.9388 | 56.456 | 0.064445 | 0.0012678 | 0.0013621 | 0.05767 | 0.00027203 | 0.057911 | 0.081635 | 5.2637e-05 | 0.0016231 | 0.065973 | -0.0053733 | 0.064853 | -66.9304 | 0.0243 | -66.8971 | 56.4487 | 56.17 | 56.4634 | -66.8925 | -66.9534 | 0.023253 | -67.0108 | 56.3725 | 56.4862 | 56.1185 | -67.2026 | 0.046321 | -0.007285 | 0.008377 | 0.041694 | -0.004627 | -0.28597 | 0.007362 | -0.26383 | -0.083466 | -0.014645 | -0.072043 | 0.19179 | 0.030196 | -0.33747 | 123.3875 | 123.1088 | 123.4021 | 66.9631 | -123.3485 | 123.3113 | 123.425 | 123.0573 | 66.962 | -123.6586
8.2344 | 123.5046 | -66.925 | 56.456 | 0.079707 | 0.0023358 | -0.00077494 | 0.05767 | 0.001341 | 0.058979 | 0.051113 | 5.2637e-05 | 0.00055508 | 0.065973 | -0.0064413 | 0.065921 | -66.9396 | 0.0243 | -66.9017 | 56.4441 | 56.1838 | 56.4313 | -66.8696 | -66.9443 | 0.018674 | -67.0154 | 56.3771 | 56.4908 | 56.1231 | -67.1935 | 0.055483 | -0.011863 | -0.014512 | 0.023383 | -0.0321 | -0.27223 | -0.024689 | -0.26841 | -0.078888 | -0.01922 | -0.090355 | 0.17805 | 0.034775 | -0.33289 | 123.3692 | 123.1088 | 123.3564 | 66.9493 | -123.3256 | 123.3022 | 123.4158 | 123.0482 | 66.9437 | -123.6494
9.2344 | 123.4955 | -66.9159 | 56.4789 | 0.033921 | 0.0023358 | 0.00029306 | 0.05767 | 0.002409 | 0.056843 | 0.081635 | -0.0010164 | 0.0016231 | 0.067042 | -0.0053733 | 0.065921 | -66.9304 | 0.0243 | -66.8971 | 56.4441 | 56.1792 | 56.4634 | -66.8558 | -66.9534 | 0.027831 | -67.0154 | 56.3725 | 56.4862 | 56.1277 | -67.198 | 0.060064 | -0.034751 | -0.014511 | 0.018806 | -0.041258 | -0.2997 | -0.015526 | -0.28214 | -0.10635 | -0.037533 | -0.09951 | 0.18263 | 0.007308 | -0.3512 | 123.36 | 123.0951 | 123.3792 | 66.9402 | -123.3347 | 123.2884 | 123.4021 | 123.0436 | 66.9437 | -123.6769
10.2344 | 123.5229 | -66.9388 | 56.456 | 0.049183 | 0.0012678 | 0.00029306 | 0.059806 | 0.00027203 | 0.056843 | 0.066374 | 0.0011206 | 0.00055508 | 0.067042 | -0.0043053 | 0.064853 | -66.9304 | 0.0243 | -66.8971 | 56.4487 | 56.1792 | 56.4221 | -66.9062 | -66.9488 | 0.018674 | -67.0154 | 56.3817 | 56.4862 | 56.1368 | -67.1843 | 0.032584 | -0.007285 | 0.008377 | 0.041694 | 0.00911 | -0.27681 | -0.033846 | -0.24551 | -0.074309 | -0.010066 | -0.076622 | 0.16889 | 0.030196 | -0.31915 | 123.3875 | 123.118 | 123.3609 | 66.9631 | -123.3622 | 123.3205 | 123.425 | 123.0756 | 66.9575 | -123.6403
11.2344 | 123.5092 | -66.9159 | 56.4697 | 0.064445 | 0.0012678 | 0.00029306 | 0.05767 | -0.00079597 | 0.056843 | 0.051113 | 5.2637e-05 | 0.00055508 | 0.065973 | -0.0053733 | 0.066989 | -66.9441 | 0.019721 | -66.8971 | 56.4396 | 56.1746 | 56.4405 | -66.8833 | -66.9534 | 0.023253 | -67.02 | 56.3817 | 56.4908 | 56.1414 | -67.198 | 0.032591 | -0.030174 | -0.028246 | 0.018806 | -0.013785 | -0.29512 | -0.029264 | -0.28214 | -0.088042 | -0.037533 | -0.10409 | 0.17805 | 0.021042 | -0.32831 | 123.3554 | 123.0905 | 123.3564 | 66.9356 | -123.353 | 123.2976 | 123.4067 | 123.0573 | 66.9391 | -123.6678
12.2344 | 123.555 | -66.9205 | 56.4697 | 0.049183 | 0.0012678 | 0.00029306 | 0.05767 | 0.001341 | 0.056843 | 0.066374 | -0.0010164 | 0.0026921 | 0.065973 | -0.0053733 | 0.065921 | -66.9396 | 0.019721 | -66.8925 | 56.4441 | 56.138 | 56.3901 | -66.8192 | -66.9443 | 0.027831 | -67.0108 | 56.3725 | 56.4816 | 56.1414 | -67.1889 | 0.10127 | -0.025596 | -0.01909 | 0.027961 | -0.073312 | -0.33175 | -0.079629 | -0.2684 | -0.097199 | -0.023798 | -0.090354 | 0.17805 | 0.011884 | -0.32831 | 123.3646 | 123.0584 | 123.3106 | 66.9402 | -123.2889 | 123.293 | 123.4021 | 123.0619 | 66.9483 | -123.6586
13.2344 | 123.5001 | -66.9296 | 56.4835 | 0.049183 | 0.0034038 | 0.00029306 | 0.056601 | 0.002409 | 0.058979 | 0.081635 | 0.0011206 | 0.0016231 | 0.067042 | -0.0043053 | 0.063784 | -66.9396 | 0.0243 | -66.9017 | 56.4441 | 56.2067 | 56.4313 | -66.8375 | -66.9488 | 0.023253 | -67.0154 | 56.3817 | 56.4908 | 56.1414 | -67.1935 | 0.092112 | -0.039328 | -0.009935 | 0.02796 | -0.064152 | -0.2768 | -0.052154 | -0.26383 | -0.10177 | -0.019222 | -0.085778 | 0.17805 | 0.00731 | -0.34204 | 123.3738 | 123.1363 | 123.3609 | 66.9539 | -123.321 | 123.3113 | 123.4204 | 123.071 | 66.9529 | -123.6769
14.2344 | 123.5275 | -66.9525 | 56.4789 | 0.033921 | 0.0012678 | 0.00029306 | 0.058738 | -0.001864 | 0.057911 | 0.051113 | 0.0021886 | 0.0016231 | 0.064905 | -0.0043053 | 0.065921 | -66.9258 | 0.028878 | -66.8971 | 56.4533 | 56.1838 | 56.4176 | -66.8696 | -66.9488 | 0.023253 | -67.0108 | 56.3817 | 56.4816 | 56.1414 | -67.1935 | 0.082949 | -0.025594 | 0.026689 | 0.055427 | -0.027522 | -0.29512 | -0.061312 | -0.24094 | -0.097197 | 0.003667 | -0.05831 | 0.18263 | 0.002729 | -0.33746 | 123.4058 | 123.1363 | 123.3701 | 66.9814 | -123.3484 | 123.3342 | 123.4341 | 123.0939 | 66.9758 | -123.6723
15.2344 | 123.5367 | -66.9479 | 56.4743 | 0.049183 | 0.0012678 | 0.00029306 | 0.056601 | 0.00027203 | 0.058979 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.065973 | -0.0043053 | 0.064853 | -66.935 | 0.019721 | -66.8925 | 56.4304 | 56.1563 | 56.4359 | -66.8558 | -66.958 | 0.023253 | -67.0108 | 56.3771 | 56.4816 | 56.1414 | -67.1935 | 0.092107 | -0.043908 | 0.012954 | 0.055427 | -0.03668 | -0.31801 | -0.03842 | -0.24552 | -0.097198 | -0.010068 | -0.062888 | 0.18263 | 0.007307 | -0.33289 | 123.3783 | 123.1042 | 123.3838 | 66.9677 | -123.3301 | 123.325 | 123.4295 | 123.0894 | 66.9712 | -123.6678
16.2344 | 123.5596 | -66.9388 | 56.4514 | 0.049183 | 0.0012678 | 0.0013621 | 0.05767 | -0.00079597 | 0.055774 | 0.066374 | -0.0010164 | -0.00051292 | 0.064905 | -0.0032363 | 0.064853 | -66.935 | 0.0243 | -66.9017 | 56.4441 | 56.1654 | 56.4221 | -66.8833 | -66.9488 | 0.018674 | -67.0108 | 56.3771 | 56.4862 | 56.1323 | -67.1843 | 0.055479 | -0.007285 | 0.003799 | 0.037116 | -0.018363 | -0.28597 | -0.029268 | -0.24551 | -0.07431 | -0.010066 | -0.072043 | 0.17347 | 0.034774 | -0.31916 | 123.3829 | 123.1042 | 123.3609 | 66.9631 | -123.3347 | 123.3159 | 123.425 | 123.071 | 66.9575 | -123.6357
17.2344 | 123.5367 | -66.9388 | 56.4377 | 0.049183 | 0.0012678 | 0.00029306 | 0.05767 | 0.00027203 | 0.056843 | 0.066374 | 0.0011206 | 0.00055508 | 0.065973 | -0.0043053 | 0.063784 | -66.935 | 0.033457 | -66.9062 | 56.4441 | 56.1288 | 56.4496 | -66.8467 | -66.9534 | 0.03241 | -67.0062 | 56.3817 | 56.4953 | 56.1368 | -67.1935 | 0.09211 | 0.006448 | 0.003799 | 0.032537 | -0.059573 | -0.30887 | 0.011937 | -0.25467 | -0.055998 | -0.014645 | -0.067465 | 0.18721 | 0.057664 | -0.30084 | 123.3829 | 123.0676 | 123.3884 | 66.9722 | -123.2844 | 123.3205 | 123.4341 | 123.0756 | 66.9712 | -123.6311
18.2344 | 123.5504 | -66.925 | 56.4514 | 0.049183 | 0.0034038 | 0.0013621 | 0.05767 | 0.001341 | 0.057911 | 0.081635 | 0.0011206 | 0.00055508 | 0.065973 | -0.0043053 | 0.066989 | -66.935 | 0.0243 | -66.9062 | 56.4487 | 56.1792 | 56.4084 | -66.8787 | -66.9534 | 0.027831 | -67.02 | 56.3771 | 56.4908 | 56.1414 | -67.198 | 0.046325 | -0.002707 | -0.009934 | 0.018804 | -0.027521 | -0.27223 | -0.043004 | -0.27298 | -0.07431 | -0.028378 | -0.094934 | 0.17805 | 0.039353 | -0.31 | 123.3738 | 123.1042 | 123.3335 | 66.9493 | -123.3301 | 123.3022 | 123.4158 | 123.0665 | 66.9529 | -123.6494
19.25 | 123.6282 | -66.9113 | 56.3965 | 0.049183 | 0.0023358 | -0.00077494 | 0.059806 | 0.001341 | 0.057911 | 0.081635 | 5.2637e-05 | 0.0016231 | 0.064905 | -0.0032363 | 0.064853 | -66.9304 | 0.0243 | -66.8971 | 56.4441 | 56.1517 | 56.4313 | -66.8421 | -66.9488 | 0.027831 | -67.0062 | 56.3817 | 56.4908 | 56.1368 | -67.198 | 0.069223 | 0.047647 | -0.019089 | 0.014228 | -0.054995 | -0.24477 | 0.034821 | -0.28672 | -0.014799 | -0.037532 | -0.094931 | 0.19179 | 0.094285 | -0.25964 | 123.3554 | 123.063 | 123.3426 | 66.9356 | -123.2386 | 123.293 | 123.4021 | 123.0482 | 66.9391 | -123.5945
20.2344 | 123.5229 | -66.9571 | 56.4423 | 0.064445 | 0.0012678 | 0.0024301 | 0.056601 | -0.00079597 | 0.057911 | 0.066374 | 5.2637e-05 | -0.0015819 | 0.067042 | -0.0053733 | 0.065921 | -66.9304 | 0.0243 | -66.9017 | 56.4441 | 56.1242 | 56.4542 | -66.8787 | -66.9397 | 0.018674 | -67.0108 | 56.3725 | 56.4908 | 56.1414 | -67.1935 | 0.078368 | 0.00187 | 0.026687 | 0.055426 | -0.022942 | -0.31802 | 0.011937 | -0.23636 | -0.069733 | 0.017402 | -0.053733 | 0.18263 | 0.048508 | -0.30084 | 123.4012 | 123.0813 | 123.4113 | 66.9814 | -123.321 | 123.3296 | 123.4479 | 123.0985 | 66.9758 | -123.6357
21.2344 | 123.4909 | -66.9342 | 56.4423 | 0.049183 | 0.0012678 | 0.00029306 | 0.058738 | 0.00027203 | 0.057911 | 0.081635 | 0.0011206 | -0.0015819 | 0.065973 | -0.0032363 | 0.066989 | -66.9304 | 0.019721 | -66.9017 | 56.4487 | 56.1929 | 56.4176 | -66.865 | -66.9488 | 0.023253 | -67.0154 | 56.3771 | 56.4908 | 56.1368 | -67.1935 | 0.069217 | 0.006448 | 0.003799 | 0.032538 | -0.036679 | -0.24934 | -0.024691 | -0.25925 | -0.065155 | -0.014644 | -0.0812 | 0.17805 | 0.048508 | -0.30542 | 123.3829 | 123.1271 | 123.3518 | 66.9539 | -123.3072 | 123.3113 | 123.425 | 123.071 | 66.9575 | -123.6357
22.25 | 123.642 | -66.9205 | 56.4285 | 0.064445 | 0.0023358 | -0.00077494 | 0.056601 | 0.00027203 | 0.057911 | 0.035852 | 0.0011206 | -0.00051292 | 0.064905 | -0.0032363 | 0.065921 | -66.935 | 0.019721 | -66.8925 | 56.4396 | 56.1883 | 56.4313 | -66.8787 | -66.9488 | 0.018674 | -67.0154 | 56.3725 | 56.4908 | 56.1506 | -67.1935 | 0.041747 | 0.011025 | -0.014512 | 0.027961 | -0.013786 | -0.24019 | 0.002777 | -0.27298 | -0.056 | -0.028377 | -0.094933 | 0.17805 | 0.062241 | -0.27795 | 123.36 | 123.1088 | 123.3518 | 66.9402 | -123.3073 | 123.293 | 123.4112 | 123.071 | 66.9391 | -123.622
23.2344 | 123.5184 | -66.9662 | 56.4377 | 0.064445 | 0.00019878 | 0.00029306 | 0.05767 | 0.001341 | 0.055774 | 0.051113 | -0.0010164 | -0.00051292 | 0.065973 | -0.0032363 | 0.065921 | -66.9258 | 0.028878 | -66.8925 | 56.4396 | 56.1975 | 56.4176 | -66.8467 | -66.9534 | 0.023253 | -67.02 | 56.3863 | 56.4862 | 56.1368 | -67.1889 | 0.11958 | 0.00187 | 0.040422 | 0.073738 | -0.045838 | -0.24018 | -0.020113 | -0.22263 | -0.05142 | 0.012821 | -0.053735 | 0.16889 | 0.048507 | -0.30084 | 123.4058 | 123.1637 | 123.3838 | 66.9951 | -123.2844 | 123.3525 | 123.4524 | 123.1031 | 66.9895 | -123.6266
24.25 | 123.6282 | -66.9067 | 56.4377 | 0.064445 | 0.0012678 | 0.0013621 | 0.056601 | 0.001341 | 0.056843 | 0.051113 | -0.0010164 | 0.0016231 | 0.065973 | -0.0021683 | 0.064853 | -66.9304 | 0.0243 | -66.8971 | 56.4441 | 56.1426 | 56.4405 | -66.8558 | -66.9488 | 0.023253 | -67.0108 | 56.3771 | 56.4908 | 56.1323 | -67.1935 | 0.050908 | 0.006448 | -0.023667 | 0.00965 | -0.041258 | -0.29513 | 0.00278 | -0.28672 | -0.060577 | -0.04211 | -0.10409 | 0.18263 | 0.053086 | -0.30542 | 123.3509 | 123.0493 | 123.3472 | 66.931 | -123.2935 | 123.2838 | 123.3975 | 123.039 | 66.93 | -123.6311
25.2344 | 123.5092 | -66.9296 | 56.4697 | 0.049183 | 0.00019878 | -0.0018439 | 0.056601 | 0.00027203 | 0.056843 | 0.066374 | 5.2637e-05 | 0.0016231 | 0.067042 | -0.0043053 | 0.064853 | -66.9304 | 0.038035 | -66.8971 | 56.4441 | 56.1838 | 56.4359 | -66.8879 | -66.9443 | 0.023253 | -67.0108 | 56.3725 | 56.4908 | 56.1368 | -67.1935 | 0.041744 | -0.025596 | -0.000779 | 0.032538 | -0.009206 | -0.28596 | -0.033843 | -0.26383 | -0.097199 | -0.014643 | -0.081199 | 0.18263 | 0.021042 | -0.33289 | 123.3738 | 123.1134 | 123.3655 | 66.9677 | -123.3576 | 123.3022 | 123.4204 | 123.0665 | 66.9529 | -123.6632
26.2344 | 123.5138 | -66.9754 | 56.4423 | 0.064445 | 0.00019878 | -0.0018439 | 0.058738 | 0.00027203 | 0.055774 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.063837 | -0.0021683 | 0.064853 | -66.935 | 0.0243 | -66.8971 | 56.435 | 56.17 | 56.4084 | -66.8787 | -66.9488 | 0.023253 | -67.0108 | 56.3725 | 56.4953 | 56.1323 | -67.1935 | 0.096679 | -0.007287 | 0.04042 | 0.078315 | -0.018364 | -0.27224 | -0.033849 | -0.21805 | -0.069733 | 0.026555 | -0.035422 | 0.18263 | 0.053086 | -0.31 | 123.4104 | 123.1454 | 123.3838 | 66.9997 | -123.321 | 123.3479 | 123.4708 | 123.1077 | 66.9987 | -123.6357
27.25 | 123.6191 | -66.9022 | 56.4102 | 0.064445 | 0.0012678 | 0.0013621 | 0.056601 | 0.001341 | 0.056843 | 0.066374 | 0.0011206 | 0.0016231 | 0.064905 | -0.0021683 | 0.068058 | -66.9258 | 0.019721 | -66.8925 | 56.4441 | 56.1654 | 56.4084 | -66.8009 | -66.9443 | 0.014095 | -67.0108 | 56.3771 | 56.4862 | 56.1277 | -67.1889 | 0.10128 | 0.033914 | -0.023665 | 0.009651 | -0.091628 | -0.24477 | -0.001805 | -0.28671 | -0.033111 | -0.042108 | -0.10866 | 0.17805 | 0.075973 | -0.28254 | 123.3463 | 123.0676 | 123.3106 | 66.9219 | -123.2111 | 123.2793 | 123.3884 | 123.0298 | 66.9163 | -123.5991
28.2344 | 123.4955 | -66.9662 | 56.4285 | 0.033921 | 0.0012678 | 0.0013621 | 0.05767 | 0.00027203 | 0.055774 | 0.051113 | 0.0011206 | -0.00051292 | 0.064905 | -0.0032363 | 0.068058 | -66.935 | 0.028878 | -66.8971 | 56.4487 | 56.2021 | 56.4634 | -66.8329 | -66.9488 | 0.027831 | -67.0062 | 56.3771 | 56.4862 | 56.1368 | -67.1935 | 0.13331 | 0.020181 | 0.031265 | 0.06916 | -0.064153 | -0.22645 | 0.034828 | -0.22721 | -0.051422 | 0.0174 | -0.039999 | 0.18721 | 0.057662 | -0.29169 | 123.415 | 123.1683 | 123.4296 | 66.9951 | -123.2615 | 123.3434 | 123.4524 | 123.1031 | 66.9941 | -123.622
29.25 | 123.6786 | -66.893 | 56.4331 | 0.049183 | 0.00019878 | 0.0013621 | 0.055533 | 0.00027203 | 0.056843 | 0.081635 | 5.2637e-05 | 0.0016231 | 0.064905 | -0.0032363 | 0.065921 | -66.9396 | 0.0243 | -66.8925 | 56.435 | 56.17 | 56.413 | -66.8329 | -66.9488 | 0.023253 | -67.0062 | 56.3817 | 56.4908 | 56.1277 | -67.1935 | 0.06007 | 0.001869 | -0.046556 | 0.000495 | -0.059575 | -0.26308 | -0.020114 | -0.30045 | -0.05142 | -0.055843 | -0.11324 | 0.18721 | 0.057664 | -0.30542 | 123.328 | 123.063 | 123.306 | 66.9173 | -123.266 | 123.2747 | 123.3838 | 123.0207 | 66.9163 | -123.6266
30.2344 | 123.6099 | -66.9067 | 56.3965 | 0.064445 | 0.0012678 | 0.00029306 | 0.05767 | 0.00027203 | 0.057911 | 0.066374 | 5.2637e-05 | 0.00055508 | 0.065973 | -0.0010993 | 0.065921 | -66.9304 | 0.028878 | -66.9017 | 56.4487 | 56.1563 | 56.4542 | -66.8055 | -66.9488 | 0.018674 | -67.0062 | 56.3771 | 56.4862 | 56.1368 | -67.1935 | 0.10128 | 0.052225 | -0.023667 | 0.005072 | -0.096205 | -0.24019 | 0.057714 | -0.28672 | -0.019378 | -0.04211 | -0.099509 | 0.18721 | 0.089706 | -0.25964 | 123.3554 | 123.063 | 123.3609 | 66.9356 | -123.2019 | 123.2838 | 123.3929 | 123.0436 | 66.9254 | -123.5899
31.2344 | 123.5504 | -66.9479 | 56.4148 | 0.049183 | 0.0012678 | -0.00077494 | 0.056601 | -0.00079597 | 0.056843 | 0.051113 | -0.0010164 | -0.00051292 | 0.067042 | -0.0021683 | 0.065921 | -66.9258 | 0.0243 | -66.9062 | 56.4487 | 56.1746 | 56.4313 | -66.8513 | -66.9534 | 0.018674 | -67.0062 | 56.3771 | 56.4862 | 56.1323 | -67.198 | 0.096686 | 0.033914 | 0.022111 | 0.041692 | -0.054994 | -0.24019 | 0.01651 | -0.2501 | -0.037689 | -0.00549 | -0.05831 | 0.19179 | 0.071395 | -0.28253 | 123.3966 | 123.1225 | 123.3792 | 66.9722 | -123.266 | 123.325 | 123.4341 | 123.0802 | 66.9666 | -123.6128
32.25 | 123.5962 | -66.9113 | 56.4285 | 0.064445 | 0.00019878 | -0.00077494 | 0.056601 | -0.00079597 | 0.056843 | 0.051113 | 0.0011206 | 0.0016231 | 0.064905 | -3.1333e-05 | 0.065921 | -66.9304 | 0.019721 | -66.8971 | 56.4396 | 56.138 | 56.4405 | -66.8055 | -66.9534 | 0.018674 | -67.0154 | 56.3725 | 56.4862 | 56.1368 | -67.2026 | 0.10586 | 0.011025 | -0.019089 | 0.014228 | -0.091627 | -0.29055 | 0.011935 | -0.2913 | -0.056 | -0.042111 | -0.10409 | 0.18721 | 0.057662 | -0.29169 | 123.3509 | 123.0493 | 123.3518 | 66.931 | -123.234 | 123.2838 | 123.3975 | 123.0482 | 66.93 | -123.6311
33.2344 | 123.6099 | -66.9022 | 56.4102 | 0.033921 | 0.00019878 | 0.00029306 | 0.055533 | 0.001341 | 0.056843 | 0.066374 | -0.0010164 | 0.00055508 | 0.063837 | -0.0021683 | 0.066989 | -66.9258 | 0.010564 | -66.9017 | 56.4441 | 56.1609 | 56.445 | -66.8741 | -66.9443 | 0.023253 | -67.0108 | 56.3771 | 56.4816 | 56.1323 | -67.198 | 0.028016 | 0.033914 | -0.023665 | 0.000495 | -0.027521 | -0.24935 | 0.034824 | -0.29587 | -0.033111 | -0.042108 | -0.10866 | 0.18721 | 0.071394 | -0.27796 | 123.3463 | 123.063 | 123.3472 | 66.9127 | -123.2844 | 123.2793 | 123.3838 | 123.0344 | 66.9254 | -123.6082
34.25 | 123.5184 | -66.9388 | 56.4972 | 0.033921 | 0.0012678 | -0.00077494 | 0.055533 | -0.00079597 | 0.055774 | 0.066374 | -0.0010164 | 0.00055508 | 0.065973 | -0.0021683 | 0.066989 | -66.935 | 0.019721 | -66.9017 | 56.4441 | 56.1883 | 56.3993 | -66.81 | -66.9534 | 0.023253 | -67.0108 | 56.3679 | 56.4862 | 56.1368 | -67.1935 | 0.12874 | -0.053061 | 0.003799 | 0.037116 | -0.091626 | -0.30885 | -0.097937 | -0.25467 | -0.12924 | -0.014645 | -0.072043 | 0.18263 | -0.011002 | -0.36035 | 123.3829 | 123.1271 | 123.338 | 66.9585 | -123.3072 | 123.3067 | 123.425 | 123.0756 | 66.962 | -123.6906
35.2344 | 123.6511 | -66.9205 | 56.3919 | 0.033921 | -0.0019382 | 0.00029306 | 0.058738 | 0.00027203 | 0.057911 | 0.081635 | 5.2637e-05 | 0.00055508 | 0.064905 | -0.0021683 | 0.065921 | -66.9304 | 0.0243 | -66.9017 | 56.4396 | 56.1426 | 56.413 | -66.81 | -66.958 | 0.018674 | -67.0108 | 56.3771 | 56.4862 | 56.1323 | -67.198 | 0.11043 | 0.047646 | -0.009934 | 0.018805 | -0.091626 | -0.24935 | 0.021084 | -0.27756 | -0.014801 | -0.037534 | -0.090354 | 0.18721 | 0.094283 | -0.25965 | 123.36 | 123.063 | 123.3335 | 66.9448 | -123.2019 | 123.2976 | 123.4067 | 123.0527 | 66.9391 | -123.5899
36.2344 | 123.5779 | -66.925 | 56.4011 | 0.033921 | 0.0012678 | -0.0018439 | 0.056601 | 0.002409 | 0.057911 | 0.066374 | -0.0010164 | 0.00055508 | 0.065973 | -0.0032363 | 0.066989 | -66.9396 | 0.0243 | -66.8971 | 56.435 | 56.1563 | 56.413 | -66.8604 | -66.9443 | 0.023253 | -67.0108 | 56.3679 | 56.4816 | 56.1277 | -67.1935 | 0.064641 | 0.033912 | -0.014512 | 0.027961 | -0.03668 | -0.24477 | 0.011929 | -0.26841 | -0.033113 | -0.01922 | -0.085776 | 0.18263 | 0.080549 | -0.27338 | 123.36 | 123.0813 | 123.338 | 66.9493 | -123.2615 | 123.293 | 123.4067 | 123.0527 | 66.9483 | -123.5945
37.25 | 123.6649 | -66.8838 | 56.4377 | 0.064445 | 0.0023358 | -0.00077494 | 0.05767 | 0.002409 | 0.056843 | 0.066374 | -0.0010164 | 0.0016231 | 0.065973 | -0.0021683 | 0.065921 | -66.9258 | 0.0243 | -66.8971 | 56.4441 | 56.1517 | 56.4176 | -66.8284 | -66.9443 | 0.023253 | -67.0154 | 56.3679 | 56.4908 | 56.1323 | -67.198 | 0.055494 | 0.006448 | -0.041976 | -0.013238 | -0.068732 | -0.28597 | -0.020113 | -0.31418 | -0.069734 | -0.060419 | -0.13155 | 0.18263 | 0.053086 | -0.30542 | 123.328 | 123.0356 | 123.3014 | 66.9081 | -123.266 | 123.2518 | 123.3746 | 123.0161 | 66.9071 | -123.6357
38.2344 | 123.6374 | -66.9022 | 56.4056 | 0.033921 | 0.00019878 | -0.00077494 | 0.056601 | 0.00027203 | 0.056843 | 0.035852 | 0.0011206 | -0.00051292 | 0.065973 | -3.1333e-05 | 0.065921 | -66.9258 | 0.033457 | -66.8925 | 56.4441 | 56.1563 | 56.4496 | -66.8604 | -66.9488 | 0.014095 | -67.0062 | 56.3679 | 56.4953 | 56.1323 | -67.198 | 0.041753 | 0.038491 | -0.023665 | 0.009651 | -0.032102 | -0.24935 | 0.04398 | -0.29587 | -0.037691 | -0.046687 | -0.10409 | 0.19179 | 0.089707 | -0.27338 | 123.3463 | 123.0585 | 123.3518 | 66.9356 | -123.266 | 123.2701 | 123.3975 | 123.0344 | 66.9163 | -123.6037
39.25 | 123.6465 | -66.893 | 56.4194 | 0.049183 | 0.00019878 | -0.00077494 | 0.05767 | 0.00027203 | 0.056843 | 0.081635 | 0.0011206 | 0.00055508 | 0.064905 | -0.0010993 | 0.063784 | -66.9212 | 0.0243 | -66.9017 | 56.4441 | 56.1746 | 56.4267 | -66.897 | -66.9534 | 0.023253 | -67.0108 | 56.3817 | 56.4908 | 56.1323 | -67.198 | -0.004035 | 0.024758 | -0.028243 | -0.008661 | -0.004626 | -0.24477 | 0.007354 | -0.30503 | -0.037688 | -0.060422 | -0.11782 | 0.18721 | 0.071396 | -0.28711 | 123.3371 | 123.0676 | 123.3197 | 66.9173 | -123.3164 | 123.2747 | 123.3838 | 123.0253 | 66.9163 | -123.6174
40.2344 | 123.5779 | -66.9022 | 56.4239 | 0.079707 | -0.00086922 | -0.0029119 | 0.056601 | 0.00027203 | 0.056843 | 0.066374 | 5.2637e-05 | 0.0016231 | 0.064905 | -0.0021683 | 0.063784 | -66.935 | 0.028878 | -66.8971 | 56.435 | 56.138 | 56.3901 | -66.8284 | -66.9443 | 0.018674 | -67.0108 | 56.3771 | 56.4908 | 56.1368 | -67.1935 | 0.073805 | 0.011024 | -0.032822 | 0.005073 | -0.068732 | -0.28598 | -0.033852 | -0.29129 | -0.046844 | -0.042108 | -0.10866 | 0.18263 | 0.066819 | -0.28711 | 123.3371 | 123.0401 | 123.2923 | 66.931 | -123.2523 | 123.2793 | 123.3929 | 123.039 | 66.9208 | -123.6174
41.2344 | 123.587 | -66.8976 | 56.4194 | 0.049183 | 0.0012678 | -0.00077494 | 0.056601 | 0.00027203 | 0.056843 | 0.066374 | 5.2637e-05 | 0.0016231 | 0.067042 | -0.0010993 | 0.065921 | -66.9304 | 0.033457 | -66.8971 | 56.4304 | 56.1609 | 56.3855 | -66.8238 | -66.9488 | 0.014095 | -67.0062 | 56.3771 | 56.4862 | 56.1368 | -67.1935 | 0.073806 | 0.011023 | -0.032822 | 0.000495 | -0.073311 | -0.2585 | -0.033854 | -0.29587 | -0.042267 | -0.051265 | -0.10866 | 0.18721 | 0.066817 | -0.28253 | 123.328 | 123.0585 | 123.2831 | 66.931 | -123.2432 | 123.2747 | 123.3838 | 123.0344 | 66.9117 | -123.6128
42.2344 | 123.5962 | -66.8838 | 56.4377 | 0.049183 | 0.00019878 | -0.00077494 | 0.056601 | 0.001341 | 0.056843 | 0.066374 | 5.2637e-05 | 0.00055508 | 0.064905 | -0.0010993 | 0.063784 | -66.9304 | 0.019721 | -66.9017 | 56.4441 | 56.1334 | 56.4176 | -66.8192 | -66.9488 | 0.023253 | -67.0154 | 56.3771 | 56.4908 | 56.146 | -67.198 | 0.064652 | 0.006448 | -0.046555 | -0.017816 | -0.082468 | -0.30429 | -0.020113 | -0.31418 | -0.060577 | -0.064998 | -0.13155 | 0.18263 | 0.053086 | -0.29169 | 123.328 | 123.0172 | 123.3014 | 66.9036 | -123.2569 | 123.261 | 123.3746 | 123.0298 | 66.9071 | -123.6357
43.2344 | 123.6282 | -66.893 | 56.4377 | 0.064445 | -0.00086922 | -0.00077494 | 0.056601 | 0.001341 | 0.056843 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.064905 | -3.1333e-05 | 0.064853 | -66.9304 | 0.0243 | -66.8971 | 56.4396 | 56.1975 | 56.4405 | -66.8604 | -66.9443 | 0.023253 | -67.0108 | 56.3817 | 56.4908 | 56.1368 | -67.2026 | 0.032597 | 0.00187 | -0.0374 | -0.004083 | -0.03668 | -0.24018 | 0.00278 | -0.30961 | -0.055998 | -0.051264 | -0.11782 | 0.19179 | 0.053086 | -0.30084 | 123.3326 | 123.0905 | 123.3335 | 66.9173 | -123.2981 | 123.2747 | 123.3838 | 123.0298 | 66.9163 | -123.6403
44.2344 | 123.6374 | -66.8884 | 56.4194 | 0.064445 | 0.0012678 | -0.00077494 | 0.055533 | 0.001341 | 0.056843 | 0.051113 | -0.0010164 | 0.0016231 | 0.065973 | -3.1333e-05 | 0.063784 | -66.9304 | 0.019721 | -66.8971 | 56.4396 | 56.2433 | 56.4542 | -66.8467 | -66.9488 | 0.018674 | -67.0246 | 56.3725 | 56.4999 | 56.146 | -67.1935 | 0.041756 | 0.02018 | -0.041977 | -0.00866 | -0.050416 | -0.17608 | 0.034825 | -0.30503 | -0.046845 | -0.06042 | -0.13613 | 0.16889 | 0.080553 | -0.27338 | 123.328 | 123.1317 | 123.3426 | 66.9081 | -123.266 | 123.261 | 123.3884 | 123.0344 | 66.9071 | -123.6128
45.2344 | 123.5916 | -66.9113 | 56.4148 | 0.049183 | 0.0012678 | 0.00029306 | 0.05767 | 0.00027203 | 0.055774 | 0.035852 | 0.0011206 | -0.0015819 | 0.063837 | -0.0010993 | 0.063784 | -66.9258 | 0.028878 | -66.8971 | 56.435 | 56.1563 | 56.4313 | -66.8192 | -66.9443 | 0.018674 | -67.0154 | 56.3679 | 56.4908 | 56.1368 | -67.198 | 0.092118 | 0.020179 | -0.01451 | 0.014228 | -0.07789 | -0.2585 | 0.01651 | -0.28672 | -0.046846 | -0.032953 | -0.10409 | 0.18263 | 0.075974 | -0.27796 | 123.3463 | 123.0676 | 123.3426 | 66.9402 | -123.234 | 123.2793 | 123.4021 | 123.0482 | 66.93 | -123.6128
46.2344 | 123.6511 | -66.9022 | 56.4514 | 0.064445 | 0.00019878 | 0.00029306 | 0.055533 | 0.00027203 | 0.056843 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.063837 | -0.0010993 | 0.065921 | -66.9304 | 0.019721 | -66.9017 | 56.435 | 56.1654 | 56.3901 | -66.8192 | -66.9443 | 0.014095 | -67.0017 | 56.3771 | 56.4953 | 56.1368 | -67.198 | 0.082963 | -0.016442 | -0.028244 | 0.000495 | -0.082468 | -0.28597 | -0.061318 | -0.29587 | -0.07431 | -0.042108 | -0.099507 | 0.19637 | 0.043931 | -0.31458 | 123.3371 | 123.0676 | 123.2923 | 66.9219 | -123.2706 | 123.2793 | 123.3975 | 123.039 | 66.9163 | -123.6494
47.25 | 123.4955 | -66.9205 | 56.4743 | 0.079707 | 0.0012678 | 0.00029306 | 0.055533 | 0.001341 | 0.056843 | 0.066374 | 0.0011206 | -0.00051292 | 0.065973 | -0.0021683 | 0.065921 | -66.9304 | 0.028878 | -66.9062 | 56.4441 | 56.138 | 56.4359 | -66.865 | -66.9488 | 0.027831 | -67.0154 | 56.3771 | 56.4908 | 56.146 | -67.1935 | 0.055484 | -0.030173 | -0.009934 | 0.014226 | -0.041258 | -0.33633 | -0.03842 | -0.27298 | -0.097198 | -0.028377 | -0.094933 | 0.17805 | 0.016465 | -0.32831 | 123.3646 | 123.0584 | 123.3564 | 66.9493 | -123.3393 | 123.2976 | 123.4112 | 123.0665 | 66.9483 | -123.6678
48.2344 | 123.6282 | -66.8976 | 56.4148 | 0.064445 | 0.00019878 | -0.00077494 | 0.05767 | 0.00027203 | 0.056843 | 0.051113 | 5.2637e-05 | 0.0016231 | 0.062769 | 0.0021057 | 0.064853 | -66.9396 | 0.0243 | -66.9017 | 56.4487 | 56.1838 | 56.4038 | -66.8879 | -66.9488 | 0.014095 | -67.0154 | 56.3771 | 56.4908 | 56.1368 | -67.1935 | 0.009701 | 0.033914 | -0.041978 | -0.004083 | -0.013784 | -0.23103 | -0.010961 | -0.29587 | -0.037689 | -0.051265 | -0.11782 | 0.17805 | 0.075974 | -0.27796 | 123.3463 | 123.0813 | 123.3014 | 66.9219 | -123.3027 | 123.2747 | 123.3884 | 123.0344 | 66.9117 | -123.6082
49.2344 | 123.6328 | -66.8884 | 56.4102 | 0.064445 | 0.00019878 | -0.00077494 | 0.056601 | 0.001341 | 0.056843 | 0.066374 | 5.2637e-05 | 0.00055508 | 0.064905 | -3.1333e-05 | 0.065921 | -66.935 | 0.015142 | -66.8971 | 56.435 | 56.2112 | 56.4313 | -66.8513 | -66.9443 | 0.009516 | -67.0108 | 56.3725 | 56.4862 | 56.1414 | -67.1935 | 0.037177 | 0.024757 | -0.046555 | -0.00866 | -0.045837 | -0.19898 | 0.021088 | -0.30503 | -0.037689 | -0.055841 | -0.1224 | 0.18263 | 0.075973 | -0.2688 | 123.3234 | 123.0997 | 123.3197 | 66.9036 | -123.2615 | 123.261 | 123.3746 | 123.0298 | 66.8979 | -123.6037
50.2344 | 123.6282 | -66.861 | 56.4514 | 0.064445 | -0.0019382 | -0.00077494 | 0.055533 | 0.00027203 | 0.056843 | 0.051113 | -0.0020844 | 0.00055508 | 0.063837 | -3.1333e-05 | 0.064853 | -66.935 | 0.019721 | -66.8971 | 56.4441 | 56.1471 | 56.413 | -66.8284 | -66.9488 | 0.018674 | -67.0154 | 56.3771 | 56.4862 | 56.1323 | -67.1935 | 0.032606 | -0.007285 | -0.074021 | -0.036126 | -0.068732 | -0.30428 | -0.038425 | -0.33249 | -0.07431 | -0.087886 | -0.15444 | 0.17805 | 0.034774 | -0.31916 | 123.3051 | 123.0081 | 123.274 | 66.8807 | -123.2798 | 123.2381 | 123.3472 | 122.9932 | 66.8796 | -123.6449
51.2344 | 123.6099 | -66.8747 | 56.4331 | 0.064445 | 0.0012678 | -0.0018439 | 0.054464 | 0.00027203 | 0.055774 | 0.051113 | 0.0011206 | -0.00051292 | 0.065973 | -3.1333e-05 | 0.064853 | -66.9304 | 0.019721 | -66.9017 | 56.4441 | 56.1517 | 56.4221 | -66.8421 | -66.9534 | 0.018674 | -67.0108 | 56.3771 | 56.4816 | 56.1414 | -67.198 | 0.032602 | 0.011026 | -0.05571 | -0.026971 | -0.059573 | -0.28139 | -0.010957 | -0.32334 | -0.055999 | -0.078732 | -0.13613 | 0.18721 | 0.048506 | -0.29169 | 123.3188 | 123.0264 | 123.2968 | 66.8944 | -123.2752 | 123.2518 | 123.3563 | 123.0161 | 66.8934 | -123.6311
52.25 | 123.6145 | -66.9159 | 56.4331 | 0.064445 | 0.00019878 | -0.00077494 | 0.055533 | -0.001864 | 0.058979 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.065973 | -0.0010993 | 0.065921 | -66.935 | 0.019721 | -66.9108 | 56.4396 | 56.1654 | 56.413 | -66.8284 | -66.9488 | 0.023253 | -67.0154 | 56.3771 | 56.477 | 56.1368 | -67.1935 | 0.087538 | 0.006448 | -0.019089 | 0.005071 | -0.082467 | -0.26766 | -0.020114 | -0.27756 | -0.055999 | -0.032954 | -0.09951 | 0.17805 | 0.043928 | -0.29627 | 123.3554 | 123.0813 | 123.3289 | 66.9356 | -123.2615 | 123.293 | 123.3929 | 123.0527 | 66.9391 | -123.6266
53.2344 | 123.6328 | -66.8793 | 56.4468 | 0.079707 | 0.00019878 | -0.00077494 | 0.054464 | 0.001341 | 0.058979 | 0.066374 | 5.2637e-05 | -0.0015819 | 0.067042 | -3.1333e-05 | 0.064853 | -66.935 | 0.019721 | -66.9017 | 56.4396 | 56.2021 | 56.4588 | -66.8604 | -66.9534 | 0.018674 | -67.0062 | 56.3771 | 56.4862 | 56.146 | -67.2026 | 0.018864 | -0.007285 | -0.055711 | -0.022394 | -0.041258 | -0.24476 | 0.011939 | -0.32334 | -0.069732 | -0.074155 | -0.12698 | 0.19636 | 0.039352 | -0.30084 | 123.3188 | 123.0814 | 123.338 | 66.899 | -123.3072 | 123.2564 | 123.3655 | 123.0253 | 66.8979 | -123.6494
54.2344 | 123.6465 | -66.8976 | 56.456 | 0.079707 | -0.00086922 | 0.00029306 | 0.05767 | -0.00079597 | 0.057911 | 0.081635 | -0.0010164 | -0.00051292 | 0.065973 | -3.1333e-05 | 0.064853 | -66.9304 | 0.0243 | -66.8925 | 56.4441 | 56.1975 | 56.4313 | -66.8513 | -66.9443 | 0.023253 | -67.0154 | 56.3817 | 56.4908 | 56.1414 | -67.198 | 0.046332 | -0.011863 | -0.032822 | 0.005073 | -0.041259 | -0.25849 | -0.024689 | -0.30045 | -0.074309 | -0.046686 | -0.11782 | 0.18263 | 0.034775 | -0.31458 | 123.3417 | 123.0951 | 123.3289 | 66.9219 | -123.3072 | 123.2793 | 123.3884 | 123.039 | 66.9208 | -123.654
55.2344 | 123.6191 | -66.8884 | 56.4468 | 0.064445 | 0.0012678 | 0.00029306 | 0.054464 | -0.00079597 | 0.056843 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.063837 | 0.0010367 | 0.063784 | -66.9304 | 0.028878 | -66.8925 | 56.4441 | 56.1563 | 56.445 | -66.8696 | -66.9443 | 0.009516 | -67.0062 | 56.3817 | 56.4908 | 56.1368 | -67.1889 | 0.018862 | -0.002707 | -0.041977 | -0.004082 | -0.022944 | -0.29055 | -0.001797 | -0.30045 | -0.065153 | -0.055841 | -0.11782 | 0.18263 | 0.043931 | -0.31 | 123.3326 | 123.0447 | 123.3335 | 66.9173 | -123.3164 | 123.2701 | 123.3792 | 123.0253 | 66.8979 | -123.6357
56.2344 | 123.6145 | -66.8838 | 56.4423 | 0.049183 | -0.00086922 | 0.00029306 | 0.05767 | -0.00079597 | 0.056843 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.064905 | -0.0010993 | 0.065921 | -66.9304 | 0.0243 | -66.9017 | 56.4441 | 56.1792 | 56.3809 | -66.8284 | -66.9488 | 0.014095 | -67.0108 | 56.3771 | 56.4816 | 56.1368 | -67.1935 | 0.055494 | 0.00187 | -0.046555 | -0.017816 | -0.07331 | -0.26308 | -0.06132 | -0.3096 | -0.065155 | -0.064998 | -0.12698 | 0.18263 | 0.03935 | -0.30542 | 123.328 | 123.063 | 123.2648 | 66.9081 | -123.2706 | 123.261 | 123.3655 | 123.0207 | 66.8979 | -123.6357
57.25 | 123.5596 | -66.9022 | 56.4606 | 0.049183 | -0.0019382 | -0.0018439 | 0.058738 | 0.00027203 | 0.056843 | 0.081635 | -0.0010164 | -0.00051292 | 0.067042 | -3.1333e-05 | 0.065921 | -66.9304 | 0.019721 | -66.8971 | 56.4396 | 56.1563 | 56.4359 | -66.81 | -66.958 | 0.018674 | -67.0062 | 56.3725 | 56.4908 | 56.1506 | -67.1935 | 0.092121 | -0.021018 | -0.028244 | 0.005073 | -0.087048 | -0.30428 | -0.024687 | -0.29129 | -0.088043 | -0.055844 | -0.10409 | 0.18721 | 0.030198 | -0.31 | 123.3417 | 123.0585 | 123.338 | 66.9219 | -123.2706 | 123.2747 | 123.3929 | 123.0527 | 66.9208 | -123.654
58.2344 | 123.6053 | -66.8884 | 56.4331 | 0.079707 | 0.0012678 | 0.00029306 | 0.056601 | -0.00079597 | 0.055774 | 0.051113 | 0.0011206 | -0.00051292 | 0.064905 | 0.0010367 | 0.063784 | -66.9304 | 0.028878 | -66.8925 | 56.4396 | 56.1975 | 56.4267 | -66.8146 | -66.9488 | 0.018674 | -67.0108 | 56.3771 | 56.4862 | 56.1414 | -67.1889 | 0.073809 | 0.006448 | -0.041977 | -0.004082 | -0.077891 | -0.2356 | -0.006378 | -0.30045 | -0.055999 | -0.06042 | -0.1224 | 0.17805 | 0.053085 | -0.29169 | 123.328 | 123.0859 | 123.3152 | 66.9173 | -123.2477 | 123.2655 | 123.3746 | 123.0298 | 66.9071 | -123.622
59.2344 | 123.6053 | -66.8976 | 56.4148 | 0.049183 | -0.00086922 | 0.00029306 | 0.056601 | -0.00079597 | 0.056843 | 0.081635 | 5.2637e-05 | -0.00051292 | 0.062769 | 0.0021057 | 0.065921 | -66.9258 | 0.0243 | -66.9017 | 56.4441 | 56.1563 | 56.445 | -66.8055 | -66.9488 | 0.018674 | -67.0154 | 56.3863 | 56.4908 | 56.1414 | -67.198 | 0.092122 | 0.029336 | -0.028243 | -0.004083 | -0.096205 | -0.2585 | 0.030246 | -0.30045 | -0.028532 | -0.051265 | -0.11782 | 0.18263 | 0.075974 | -0.27338 | 123.3417 | 123.0539 | 123.3426 | 66.9219 | -123.2203 | 123.2838 | 123.3884 | 123.039 | 66.9163 | -123.6128
60.2344 | 123.5092 | -66.925 | 56.4606 | 0.049183 | 0.00019878 | -0.00077494 | 0.055533 | 0.00027203 | 0.056843 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0031737 | 0.065921 | -66.9258 | 0.028878 | -66.8971 | 56.435 | 56.1471 | 56.4405 | -66.8467 | -66.9534 | 0.023253 | -67.0108 | 56.3817 | 56.5045 | 56.146 | -67.198 | 0.078377 | -0.025597 | -0.000777 | 0.027961 | -0.050416 | -0.31344 | -0.020108 | -0.27298 | -0.078886 | -0.028378 | -0.085776 | 0.18721 | 0.043933 | -0.31458 | 123.36 | 123.0722 | 123.3655 | 66.9539 | -123.3072 | 123.3067 | 123.4296 | 123.071 | 66.9483 | -123.6586
61.2344 | 123.5321 | -66.9022 | 56.4514 | 0.033921 | -0.00086922 | -0.0029119 | 0.055533 | 0.00027203 | 0.055774 | 0.051113 | 5.2637e-05 | 0.00055508 | 0.062769 | 0.0021057 | 0.063784 | -66.9304 | 0.028878 | -66.9017 | 56.4396 | 56.17 | 56.4588 | -66.8329 | -66.958 | 0.018674 | -67.0062 | 56.3771 | 56.4908 | 56.1323 | -67.198 | 0.069226 | -0.011863 | -0.028244 | 0.000495 | -0.068731 | -0.28139 | 0.007361 | -0.29587 | -0.07431 | -0.055844 | -0.10409 | 0.19179 | 0.039353 | -0.31916 | 123.3417 | 123.0722 | 123.3609 | 66.931 | -123.2844 | 123.2793 | 123.3929 | 123.0344 | 66.9208 | -123.6494
62.25 | 123.5458 | -66.9113 | 56.4606 | 0.049183 | 0.00019878 | -0.00077494 | 0.055533 | 0.001341 | 0.055774 | 0.081635 | 0.0011206 | -0.00051292 | 0.064905 | 0.0031737 | 0.064853 | -66.9304 | 0.028878 | -66.9062 | 56.4487 | 56.1792 | 56.4221 | -66.8604 | -66.9443 | 0.023253 | -67.0017 | 56.3725 | 56.4862 | 56.146 | -67.198 | 0.050908 | -0.011862 | -0.019089 | 0.005071 | -0.045837 | -0.28139 | -0.038423 | -0.28672 | -0.088043 | -0.032953 | -0.090352 | 0.19637 | 0.025619 | -0.31458 | 123.36 | 123.0905 | 123.3335 | 66.9402 | -123.321 | 123.2838 | 123.3975 | 123.0573 | 66.9346 | -123.6586
63.2344 | 123.5046 | -66.925 | 56.4743 | 0.079707 | 0.00019878 | 0.0013621 | 0.056601 | 0.00027203 | 0.057911 | 0.051113 | 5.2637e-05 | -0.0015819 | 0.067042 | 0.0010367 | 0.061648 | -66.9304 | 0.0243 | -66.8971 | 56.4441 | 56.1929 | 56.4359 | -66.8604 | -66.9534 | 0.018674 | -67.0108 | 56.3679 | 56.4953 | 56.146 | -67.2072 | 0.064641 | -0.030173 | -0.005356 | 0.027961 | -0.03668 | -0.28138 | -0.03842 | -0.28214 | -0.10635 | -0.028378 | -0.085776 | 0.19637 | 0.021043 | -0.32831 | 123.3692 | 123.118 | 123.3609 | 66.9493 | -123.3347 | 123.293 | 123.4204 | 123.071 | 66.9437 | -123.6815
64.2344 | 123.4863 | -66.9388 | 56.4651 | 0.064445 | 0.00019878 | 0.00029306 | 0.056601 | -0.00079597 | 0.056843 | 0.081635 | -0.0020844 | -0.00051292 | 0.065973 | 0.0021057 | 0.064853 | -66.935 | 0.028878 | -66.9017 | 56.4533 | 56.2067 | 56.4634 | -66.8421 | -66.9488 | 0.018674 | -67.0108 | 56.3817 | 56.4908 | 56.1368 | -67.198 | 0.096689 | -0.011861 | 0.003799 | 0.037116 | -0.059573 | -0.25849 | -0.001793 | -0.25925 | -0.083464 | -0.010066 | -0.072043 | 0.18721 | 0.02562 | -0.32831 | 123.3921 | 123.1454 | 123.4021 | 66.9677 | -123.3072 | 123.3205 | 123.4296 | 123.0756 | 66.9575 | -123.6632
65.2344 | 123.5046 | -66.9296 | 56.4697 | 0.079707 | 0.0012678 | -0.00077494 | 0.056601 | -0.001864 | 0.057911 | 0.066374 | 5.2637e-05 | 0.00055508 | 0.065973 | 0.0010367 | 0.065921 | -66.9304 | 0.033457 | -66.9017 | 56.4441 | 56.1517 | 56.4176 | -66.8055 | -66.9488 | 0.014095 | -67.0108 | 56.3725 | 56.4953 | 56.1414 | -67.2026 | 0.12417 | -0.025596 | -0.000779 | 0.02796 | -0.096205 | -0.31802 | -0.052157 | -0.27299 | -0.097199 | -0.019222 | -0.081199 | 0.19179 | 0.02562 | -0.32831 | 123.3738 | 123.0813 | 123.3472 | 66.9631 | -123.2752 | 123.3022 | 123.425 | 123.071 | 66.9437 | -123.6723
66.2344 | 123.5275 | -66.8976 | 56.4468 | 0.064445 | -0.0019382 | -0.00077494 | 0.056601 | -0.001864 | 0.054706 | 0.066374 | 5.2637e-05 | 0.00055508 | 0.064905 | 0.0010367 | 0.063784 | -66.9258 | 0.0243 | -66.8925 | 56.4487 | 56.1426 | 56.4084 | -66.8238 | -66.9488 | 0.023253 | -67.0108 | 56.3817 | 56.4862 | 56.1368 | -67.198 | 0.073806 | 0.001871 | -0.028243 | 0.005073 | -0.068733 | -0.30429 | -0.038426 | -0.30045 | -0.065153 | -0.051265 | -0.11324 | 0.18721 | 0.039352 | -0.31 | 123.3463 | 123.0401 | 123.306 | 66.9219 | -123.2706 | 123.2793 | 123.3838 | 123.0344 | 66.9208 | -123.6449
67.2344 | 123.5367 | -66.925 | 56.4789 | 0.049183 | -0.0030062 | 0.00029306 | 0.055533 | -0.00079597 | 0.056843 | 0.081635 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0010367 | 0.065921 | -66.9304 | 0.0243 | -66.8971 | 56.4487 | 56.2112 | 56.4359 | -66.865 | -66.9488 | 0.027831 | -67.0062 | 56.3771 | 56.4908 | 56.1414 | -67.198 | 0.060062 | -0.030173 | -0.005356 | 0.027961 | -0.032101 | -0.26765 | -0.042998 | -0.27298 | -0.10178 | -0.023799 | -0.081198 | 0.19179 | 0.011887 | -0.33746 | 123.3738 | 123.1363 | 123.3609 | 66.9493 | -123.3439 | 123.3022 | 123.4158 | 123.0665 | 66.9529 | -123.6769
68.2344 | 123.5275 | -66.9525 | 56.4835 | 0.079707 | 0.0012678 | 0.00029306 | 0.056601 | 0.00027203 | 0.055774 | 0.066374 | 5.2637e-05 | 0.00055508 | 0.063837 | 0.0021057 | 0.064853 | -66.9304 | 0.0243 | -66.8971 | 56.4487 | 56.1883 | 56.4359 | -66.8696 | -66.9488 | 0.03241 | -67.0062 | 56.3725 | 56.4953 | 56.1414 | -67.1935 | 0.082949 | -0.03475 | 0.02211 | 0.055427 | -0.027522 | -0.29512 | -0.047575 | -0.24094 | -0.11093 | 0.003667 | -0.053732 | 0.18721 | 0.011888 | -0.34204 | 123.4012 | 123.1409 | 123.3884 | 66.9768 | -123.353 | 123.325 | 123.4479 | 123.0939 | 66.9849 | -123.6769
69.2344 | 123.5138 | -66.925 | 56.4697 | 0.064445 | 0.00019878 | 0.00029306 | 0.056601 | 0.00027203 | 0.057911 | 0.066374 | 0.0011206 | -0.00051292 | 0.065973 | 0.0010367 | 0.064853 | -66.935 | 0.0243 | -66.9062 | 56.4396 | 56.2204 | 56.4588 | -66.81 | -66.9488 | 0.023253 | -67.0017 | 56.3771 | 56.4953 | 56.1506 | -67.198 | 0.11501 | -0.030174 | -0.009934 | 0.018804 | -0.096205 | -0.24933 | -0.01095 | -0.27298 | -0.092621 | -0.023799 | -0.076619 | 0.19637 | 0.02562 | -0.31915 | 123.3646 | 123.1454 | 123.3838 | 66.9493 | -123.2798 | 123.3022 | 123.4204 | 123.0756 | 66.9483 | -123.6678
70.2344 | 123.4955 | -66.9113 | 56.4651 | 0.049183 | 0.00019878 | 0.00029306 | 0.056601 | -0.00079597 | 0.057911 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0031737 | 0.063784 | -66.9258 | 0.019721 | -66.8925 | 56.4441 | 56.1792 | 56.4542 | -66.8513 | -66.958 | 0.03241 | -67.0154 | 56.3771 | 56.4908 | 56.1368 | -67.198 | 0.060065 | -0.021018 | -0.01451 | 0.018806 | -0.041259 | -0.28596 | -0.010951 | -0.28672 | -0.088043 | -0.046689 | -0.10409 | 0.18263 | 0.02562 | -0.32831 | 123.3554 | 123.0905 | 123.3655 | 66.931 | -123.3164 | 123.2884 | 123.4021 | 123.0482 | 66.9437 | -123.6632
71.2344 | 123.5321 | -66.9479 | 56.4697 | 0.064445 | -0.0019382 | 0.00029306 | 0.055533 | -0.00079597 | 0.055774 | 0.051113 | -0.0010164 | -0.0015819 | 0.065973 | 0.0042417 | 0.065921 | -66.9304 | 0.0243 | -66.9017 | 56.4487 | 56.1334 | 56.4221 | -66.8421 | -66.9488 | 0.018674 | -67.0062 | 56.3725 | 56.4908 | 56.1506 | -67.1935 | 0.10584 | -0.021018 | 0.017532 | 0.046271 | -0.059573 | -0.33633 | -0.047579 | -0.24552 | -0.097199 | -0.000911 | -0.05831 | 0.18721 | 0.021042 | -0.31915 | 123.3966 | 123.0813 | 123.3701 | 66.9722 | -123.3118 | 123.3205 | 123.4387 | 123.0985 | 66.9666 | -123.6632
72.25 | 123.5367 | -66.925 | 56.4423 | 0.049183 | -0.0030062 | 0.0013621 | 0.05767 | 0.00027203 | 0.057911 | 0.066374 | -0.0020844 | -0.0015819 | 0.064905 | 0.0021057 | 0.064853 | -66.935 | 0.028878 | -66.9108 | 56.4396 | 56.1426 | 56.4176 | -66.8146 | -66.9488 | 0.018674 | -67.0108 | 56.3817 | 56.4862 | 56.146 | -67.198 | 0.11043 | -0.002708 | -0.009934 | 0.014226 | -0.096204 | -0.29971 | -0.024691 | -0.27298 | -0.060576 | -0.023799 | -0.085776 | 0.18721 | 0.043929 | -0.29627 | 123.3646 | 123.0676 | 123.3426 | 66.9539 | -123.2569 | 123.3067 | 123.4112 | 123.071 | 66.9437 | -123.6403
73.2344 | 123.4772 | -66.9434 | 56.4423 | 0.049183 | -0.00086922 | -0.00077494 | 0.055533 | -0.00079597 | 0.054706 | 0.081635 | -0.0020844 | -0.0026499 | 0.064905 | 0.0031737 | 0.065921 | -66.935 | 0.033457 | -66.9017 | 56.435 | 56.1975 | 56.4267 | -66.8238 | -66.9488 | 0.018674 | -67.0062 | 56.3725 | 56.4999 | 56.1414 | -67.1889 | 0.11958 | -0.007287 | 0.008376 | 0.041693 | -0.077889 | -0.24476 | -0.015534 | -0.24552 | -0.069733 | -0.005489 | -0.062888 | 0.18263 | 0.057665 | -0.30084 | 123.3783 | 123.1409 | 123.3701 | 66.9768 | -123.266 | 123.3159 | 123.4433 | 123.0848 | 66.962 | -123.6311
74.2344 | 123.5046 | -66.9205 | 56.4789 | 0.094969 | -0.0019382 | -0.00077494 | 0.056601 | -0.00079597 | 0.056843 | 0.051113 | 5.2637e-05 | 0.00055508 | 0.064905 | 0.0031737 | 0.065921 | -66.9304 | 0.0243 | -66.8971 | 56.4396 | 56.2112 | 56.4359 | -66.897 | -66.9488 | 0.023253 | -67.0062 | 56.3771 | 56.4999 | 56.1414 | -67.198 | 0.023431 | -0.039329 | -0.009934 | 0.023383 | -4.8e-05 | -0.26765 | -0.042998 | -0.27756 | -0.10178 | -0.028377 | -0.085776 | 0.19179 | 0.021044 | -0.33746 | 123.36 | 123.1317 | 123.3564 | 66.9448 | -123.3759 | 123.2976 | 123.4204 | 123.0619 | 66.9437 | -123.6769
75.2344 | 123.5229 | -66.925 | 56.4697 | 0.049183 | -0.0030062 | -0.0018439 | 0.054464 | -0.001864 | 0.055774 | 0.066374 | -0.0010164 | -0.00051292 | 0.063837 | 0.0042417 | 0.065921 | -66.9258 | 0.0243 | -66.9017 | 56.4487 | 56.1471 | 56.4588 | -66.8741 | -66.9488 | 0.018674 | -67.0062 | 56.3817 | 56.4908 | 56.1414 | -67.198 | 0.050904 | -0.021018 | -0.000777 | 0.023383 | -0.027521 | -0.32259 | -0.01095 | -0.27298 | -0.088042 | -0.023799 | -0.081198 | 0.19179 | 0.021042 | -0.32831 | 123.3738 | 123.0722 | 123.3838 | 66.9493 | -123.3439 | 123.3067 | 123.4158 | 123.0665 | 66.9437 | -123.6678
76.2344 | 123.5184 | -66.9205 | 56.4606 | 0.064445 | -0.0019382 | -0.00077494 | 0.056601 | -0.00079597 | 0.056843 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0042417 | 0.064853 | -66.9258 | 0.019721 | -66.8971 | 56.435 | 56.138 | 56.4542 | -66.81 | -66.9488 | 0.018674 | -67.0017 | 56.3725 | 56.4999 | 56.146 | -67.198 | 0.11043 | -0.025597 | -0.005355 | 0.023383 | -0.087048 | -0.3226 | -0.006373 | -0.27756 | -0.088043 | -0.028377 | -0.081197 | 0.19637 | 0.039355 | -0.31458 | 123.3554 | 123.0584 | 123.3747 | 66.9402 | -123.2706 | 123.293 | 123.4204 | 123.0665 | 66.9391 | -123.6586
77.25 | 123.4772 | -66.9479 | 56.4285 | 0.064445 | -0.00086922 | 0.0013621 | 0.054464 | 0.00027203 | 0.056843 | 0.081635 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0053107 | 0.062716 | -66.9258 | 0.0243 | -66.9017 | 56.4487 | 56.1609 | 56.4496 | -66.8375 | -66.9488 | 0.018674 | -67.0017 | 56.3771 | 56.4908 | 56.1414 | -67.1935 | 0.11042 | 0.020181 | 0.022111 | 0.046271 | -0.064152 | -0.26766 | 0.021092 | -0.24552 | -0.051422 | -0.000911 | -0.053731 | 0.19179 | 0.062241 | -0.28711 | 123.3966 | 123.1088 | 123.3976 | 66.9722 | -123.266 | 123.325 | 123.4387 | 123.0894 | 66.9666 | -123.622
78.2344 | 123.5321 | -66.9113 | 56.4651 | 0.049183 | -0.0030062 | 0.00029306 | 0.056601 | 0.00027203 | 0.056843 | 0.096896 | 5.2637e-05 | -0.00051292 | 0.062769 | 0.0021057 | 0.064853 | -66.9304 | 0.0243 | -66.9017 | 56.4487 | 56.1517 | 56.445 | -66.8513 | -66.9488 | 0.023253 | -67.0154 | 56.3725 | 56.4953 | 56.1414 | -67.2026 | 0.060065 | -0.01644 | -0.019089 | 0.00965 | -0.050415 | -0.31344 | -0.020108 | -0.2913 | -0.092621 | -0.037532 | -0.10409 | 0.18721 | 0.030198 | -0.32373 | 123.36 | 123.063 | 123.3564 | 66.9356 | -123.3164 | 123.2838 | 123.4067 | 123.0527 | 66.9346 | -123.6678
79.2344 | 123.5184 | -66.9113 | 56.4514 | 0.079707 | 0.00019878 | 0.00029306 | 0.056601 | -0.00079597 | 0.055774 | 0.081635 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0031737 | 0.063784 | -66.9304 | 0.0243 | -66.9017 | 56.4396 | 56.1929 | 56.4542 | -66.9154 | -66.9443 | 0.023253 | -67.0062 | 56.3771 | 56.4953 | 56.1414 | -67.198 | -0.00404 | -0.011863 | -0.019089 | 0.00965 | 0.01369 | -0.2585 | 0.002782 | -0.28672 | -0.07431 | -0.032953 | -0.094931 | 0.19179 | 0.043931 | -0.31 | 123.3509 | 123.1042 | 123.3655 | 66.9356 | -123.3668 | 123.2884 | 123.4067 | 123.0527 | 66.9346 | -123.6494
80.2344 | 123.4863 | -66.9388 | 56.4651 | 0.064445 | -0.0019382 | -0.0018439 | 0.056601 | 0.00027203 | 0.055774 | 0.066374 | 0.0011206 | -0.0015819 | 0.063837 | 0.0042417 | 0.063784 | -66.9258 | 0.028878 | -66.9017 | 56.4396 | 56.1929 | 56.4542 | -66.8513 | -66.9397 | 0.027831 | -67.0108 | 56.3817 | 56.4862 | 56.1368 | -67.198 | 0.087531 | -0.025596 | 0.012956 | 0.037116 | -0.050415 | -0.27223 | -0.010951 | -0.25925 | -0.083464 | -0.000908 | -0.072043 | 0.18721 | 0.021041 | -0.32831 | 123.3783 | 123.1317 | 123.393 | 66.9677 | -123.3164 | 123.3205 | 123.425 | 123.0756 | 66.9666 | -123.6632
81.2344 | 123.5367 | -66.9388 | 56.4331 | 0.049183 | -0.00086922 | 0.00029306 | 0.05767 | -0.001864 | 0.056843 | 0.035852 | 5.2637e-05 | 0.00055508 | 0.063837 | 0.0042417 | 0.065921 | -66.935 | 0.028878 | -66.9017 | 56.4487 | 56.225 | 56.4588 | -66.8925 | -66.9443 | 0.027831 | -67.0017 | 56.3817 | 56.4816 | 56.1368 | -67.1935 | 0.046321 | 0.015604 | 0.003799 | 0.037116 | -0.009205 | -0.20813 | 0.025672 | -0.25467 | -0.05142 | -0.005487 | -0.062886 | 0.19179 | 0.048506 | -0.29627 | 123.3875 | 123.1638 | 123.3976 | 66.9677 | -123.3256 | 123.3205 | 123.4204 | 123.0756 | 66.9666 | -123.6266
82.25 | 123.5275 | -66.9571 | 56.4423 | 0.049183 | -0.00086922 | -0.00077494 | 0.055533 | -0.00079597 | 0.055774 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0053107 | 0.064853 | -66.9258 | 0.028878 | -66.8971 | 56.435 | 56.225 | 56.445 | -66.9154 | -66.9443 | 0.023253 | -67.0062 | 56.3771 | 56.4908 | 56.0636 | -67.198 | 0.041736 | -0.007287 | 0.031266 | 0.060004 | 0.018268 | -0.21729 | 0.00278 | -0.24094 | -0.065155 | 0.012823 | -0.049155 | 0.19179 | 0.048508 | -0.37868 | 123.3921 | 123.1821 | 123.4021 | 66.986 | -123.3576 | 123.3342 | 123.4479 | 123.0207 | 66.9803 | -123.6403
83.2344 | 123.5733 | -66.925 | 56.4194 | 0.049183 | -0.00086922 | 0.0013621 | 0.055533 | 0.00027203 | 0.053638 | 0.051113 | -0.0010164 | -0.0015819 | 0.063837 | 0.0042417 | 0.064853 | -66.9258 | 0.033457 | -66.9291 | 56.4716 | 56.3166 | 56.5046 | -67.1168 | -66.9672 | 0.036989 | -67.0017 | 56.3725 | 56.4908 | 56.2605 | -67.2026 | -0.19178 | 0.052228 | -0.000777 | -0.004087 | 0.18769 | -0.10282 | 0.08519 | -0.27756 | -0.046845 | -0.042114 | -0.076619 | 0.20094 | 0.071396 | -0.15891 | 123.3966 | 123.2416 | 123.4296 | 66.9585 | -123.5362 | 123.2976 | 123.4158 | 123.1855 | 66.962 | -123.622
84.2344 | 123.5504 | -66.9113 | 56.4331 | 0.049183 | 0.00019878 | -0.0018439 | 0.054464 | -0.00079597 | 0.054706 | 0.066374 | -0.0010164 | 0.00055508 | 0.064905 | 0.0042417 | 0.064853 | -66.9258 | 0.038035 | -66.9246 | 56.4762 | 56.3166 | 56.5 | -67.1122 | -66.9626 | 0.041567 | -67.0062 | 56.3679 | 56.4862 | 56.2513 | -67.1935 | -0.20093 | 0.043075 | -0.01451 | -0.013242 | 0.18769 | -0.11655 | 0.066879 | -0.28214 | -0.065156 | -0.051268 | -0.094931 | 0.18721 | 0.053085 | -0.1818 | 123.3875 | 123.2279 | 123.4113 | 66.9494 | -123.5454 | 123.2793 | 123.3975 | 123.1626 | 66.9529 | -123.6266
85.2344 | 123.5733 | -66.9205 | 56.4514 | 0.064445 | -0.00086922 | 0.0024301 | 0.055533 | 0.00027203 | 0.054706 | 0.066374 | -0.0010164 | -0.00051292 | 0.062769 | 0.0053107 | 0.063784 | -66.9304 | 0.038035 | -66.9246 | 56.4808 | 56.3166 | 56.5091 | -67.1122 | -66.958 | 0.027831 | -67.0017 | 56.3817 | 56.4908 | 56.2101 | -67.198 | -0.19178 | 0.029342 | -0.009934 | -0.004087 | 0.18769 | -0.13486 | 0.057726 | -0.27756 | -0.069731 | -0.037534 | -0.081197 | 0.19637 | 0.039353 | -0.24132 | 123.4012 | 123.237 | 123.4296 | 66.9585 | -123.5637 | 123.3022 | 123.4112 | 123.1306 | 66.9483 | -123.6494
86.2344 | 123.5687 | -66.9388 | 56.4377 | 0.049183 | -0.0019382 | 0.0013621 | 0.05767 | 0.00027203 | 0.054706 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0042417 | 0.064853 | -66.935 | 0.033457 | -66.9246 | 56.4808 | 56.3166 | 56.5046 | -67.1168 | -66.9717 | 0.046146 | -67.0062 | 56.3771 | 56.4862 | 56.2193 | -67.2026 | -0.17805 | 0.043075 | 0.003799 | 0.014224 | 0.19227 | -0.12113 | 0.06688 | -0.26383 | -0.060577 | -0.032959 | -0.067465 | 0.19636 | 0.048507 | -0.21843 | 123.4195 | 123.2553 | 123.4433 | 66.9722 | -123.5545 | 123.3159 | 123.425 | 123.158 | 66.9849 | -123.6403
87.25 | 123.5367 | -66.9388 | 56.4056 | 0.033921 | -0.0019382 | 0.0013621 | 0.056601 | -0.00079597 | 0.054706 | 0.066374 | -0.0010164 | -0.00051292 | 0.062769 | 0.0053107 | 0.065921 | -66.9304 | 0.042614 | -66.92 | 56.4808 | 56.312 | 56.5137 | -67.1077 | -66.9717 | 0.041567 | -67.0108 | 56.3863 | 56.4908 | 56.2147 | -67.2072 | -0.16889 | 0.075118 | 0.008377 | 0.018803 | 0.18769 | -0.093667 | 0.10808 | -0.26841 | -0.019377 | -0.032959 | -0.072043 | 0.19637 | 0.085129 | -0.19096 | 123.4195 | 123.2508 | 123.4525 | 66.9814 | -123.5133 | 123.325 | 123.4296 | 123.1535 | 66.9803 | -123.6128
88.2344 | 123.5275 | -66.9525 | 56.4468 | 0.064445 | -0.0019382 | -0.00077494 | 0.055533 | -0.001864 | 0.055774 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0042417 | 0.063784 | -66.9258 | 0.042614 | -66.9246 | 56.4808 | 56.3166 | 56.5137 | -67.0756 | -66.9672 | 0.036989 | -66.9971 | 56.3817 | 56.4953 | 56.2376 | -67.2026 | -0.1231 | 0.03392 | 0.026689 | 0.027957 | 0.15106 | -0.13029 | 0.066882 | -0.2501 | -0.065153 | -0.014648 | -0.044574 | 0.20552 | 0.048509 | -0.20927 | 123.4333 | 123.2691 | 123.4662 | 66.9951 | -123.5225 | 123.3342 | 123.4479 | 123.1901 | 66.9895 | -123.6494
89.2344 | 123.5641 | -66.9296 | 56.4331 | 0.033921 | -0.0030062 | 0.0013621 | 0.056601 | -0.001864 | 0.054706 | 0.081635 | 5.2637e-05 | -0.0015819 | 0.063837 | 0.0031737 | 0.063784 | -66.9258 | 0.042614 | -66.9337 | 56.4899 | 56.3211 | 56.5137 | -67.1214 | -66.9763 | 0.041567 | -67.0062 | 56.3863 | 56.4953 | 56.2467 | -67.198 | -0.19178 | 0.05681 | 0.0038 | -0.004088 | 0.18769 | -0.11197 | 0.080615 | -0.26841 | -0.046842 | -0.046694 | -0.076621 | 0.19179 | 0.062242 | -0.18638 | 123.4195 | 123.2508 | 123.4433 | 66.9722 | -123.5545 | 123.3159 | 123.425 | 123.1764 | 66.9712 | -123.6311
90.2344 | 123.5596 | -66.9388 | 56.4331 | 0.064445 | -0.0019382 | 0.0013621 | 0.055533 | -0.00079597 | 0.054706 | 0.066374 | -0.0010164 | -0.0015819 | 0.062769 | 0.0063787 | 0.064853 | -66.9258 | 0.038035 | -66.9337 | 56.4853 | 56.3211 | 56.5137 | -67.1214 | -66.9763 | 0.036989 | -67.0108 | 56.3771 | 56.4908 | 56.2421 | -67.2026 | -0.18263 | 0.052231 | 0.012956 | 0.005068 | 0.18769 | -0.11197 | 0.080615 | -0.26383 | -0.055999 | -0.037538 | -0.072043 | 0.19179 | 0.057664 | -0.19096 | 123.4241 | 123.2599 | 123.4525 | 66.9768 | -123.5545 | 123.3159 | 123.4296 | 123.1809 | 66.9758 | -123.6357
91.2344 | 123.5229 | -66.9479 | 56.4102 | 0.064445 | -0.0019382 | -0.00077494 | 0.055533 | -0.00079597 | 0.054706 | 0.051113 | -0.0010164 | -0.00051292 | 0.063837 | 0.0053107 | 0.061648 | -66.935 | 0.033457 | -66.9108 | 56.467 | 56.312 | 56.4954 | -67.1168 | -66.9626 | 0.036989 | -67.0108 | 56.3771 | 56.4862 | 56.3429 | -67.2072 | -0.16889 | 0.056806 | 0.012954 | 0.037114 | 0.20601 | -0.098244 | 0.085189 | -0.25925 | -0.033111 | -0.014647 | -0.062888 | 0.19637 | 0.075973 | -0.067341 | 123.415 | 123.2599 | 123.4433 | 66.9814 | -123.527 | 123.325 | 123.4341 | 123.2908 | 66.9849 | -123.6174
92.25 | 123.5962 | -66.9296 | 56.3736 | 0.033921 | -0.0019382 | -0.0029119 | 0.055533 | 0.00027203 | 0.056843 | 0.081635 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0053107 | 0.064853 | -66.9258 | 0.028878 | -66.9017 | 56.4579 | 56.3028 | 56.4908 | -67.0985 | -66.9443 | 0.018674 | -67.0062 | 56.3863 | 56.4908 | 56.407 | -67.198 | -0.16889 | 0.08427 | 0.0038 | 0.02796 | 0.19685 | -0.070781 | 0.11723 | -0.26841 | 0.012667 | -0.014643 | -0.076621 | 0.19179 | 0.11717 | 0.03338 | 123.3875 | 123.2324 | 123.4205 | 66.9585 | -123.4721 | 123.3159 | 123.4204 | 123.3366 | 66.9483 | -123.5716
93.2344 | 123.5596 | -66.9205 | 56.4606 | 0.049183 | -0.0030062 | 0.00029306 | 0.055533 | -0.00079597 | 0.055774 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.0063787 | 0.063784 | -66.9258 | 0.0243 | -66.9017 | 56.4487 | 56.3394 | 56.4817 | -67.0894 | -66.9534 | 0.027831 | -67.0108 | 56.3817 | 56.4953 | 56.4528 | -67.198 | -0.16888 | -0.011862 | -0.005355 | 0.018805 | 0.18769 | -0.12112 | 0.021099 | -0.27756 | -0.078886 | -0.032956 | -0.090354 | 0.18721 | 0.034776 | -0.007809 | 123.3692 | 123.2599 | 123.4021 | 66.9448 | -123.5499 | 123.3022 | 123.4158 | 123.3732 | 66.9483 | -123.6586
94.2344 | 123.5321 | -66.9479 | 56.4514 | 0.049183 | -0.0019382 | -0.00077494 | 0.055533 | 0.00027203 | 0.055774 | 0.081635 | -0.0031524 | -0.00051292 | 0.063837 | 0.0053107 | 0.064853 | -66.9212 | 0.0243 | -66.9062 | 56.4487 | 56.2982 | 56.4817 | -67.071 | -66.9397 | 0.018674 | -67.0062 | 56.3771 | 56.4862 | 56.3612 | -67.1935 | -0.1231 | -0.002707 | 0.026689 | 0.041692 | 0.16479 | -0.15318 | 0.030254 | -0.24552 | -0.07431 | 0.008247 | -0.05831 | 0.18721 | 0.034774 | -0.090226 | 123.3966 | 123.2462 | 123.4296 | 66.9722 | -123.5225 | 123.325 | 123.4341 | 123.3091 | 66.9666 | -123.6449
95.2344 | 123.5001 | -66.9571 | 56.4606 | 0.064445 | -0.00086922 | 0.00029306 | 0.055533 | -0.00079597 | 0.056843 | 0.066374 | -0.0010164 | -0.0015819 | 0.064905 | 0.0042417 | 0.064853 | -66.9258 | 0.0243 | -66.9062 | 56.435 | 56.3486 | 56.4725 | -67.0481 | -66.9488 | 0.018674 | -66.9925 | 56.3771 | 56.4908 | 56.4207 | -67.198 | -0.091052 | -0.025597 | 0.031266 | 0.050847 | 0.1419 | -0.11197 | 0.011942 | -0.24094 | -0.083465 | 0.008244 | -0.035418 | 0.20552 | 0.030198 | -0.039859 | 123.3921 | 123.3057 | 123.4296 | 66.9814 | -123.5087 | 123.3342 | 123.4479 | 123.3778 | 66.9758 | -123.6586
96.2344 | 123.5229 | -66.9708 | 56.4651 | 0.018659 | -0.00086922 | 0.00029306 | 0.056601 | 0.00027203 | 0.054706 | 0.066374 | 5.2637e-05 | -0.0015819 | 0.064905 | 0.0053107 | 0.063784 | -66.9304 | 0.028878 | -66.8971 | 56.4533 | 56.3303 | 56.4771 | -67.0161 | -66.9534 | 0.023253 | -67.0108 | 56.3771 | 56.4908 | 56.2193 | -67.2118 | -0.045267 | -0.011861 | 0.04042 | 0.073737 | 0.119 | -0.13486 | 0.011942 | -0.24094 | -0.088043 | 0.017398 | -0.04 | 0.20094 | 0.02562 | -0.24589 | 123.4241 | 123.3011 | 123.4479 | 66.9997 | -123.4812 | 123.3479 | 123.4616 | 123.1901 | 66.9941 | -123.6769
97.25 | 123.5916 | -66.9388 | 56.4102 | 0.049183 | -0.0019382 | -0.0018439 | 0.054464 | -0.001864 | 0.055774 | 0.066374 | -0.0010164 | 0.00055508 | 0.065973 | 0.0053107 | 0.063784 | -66.9258 | 0.0243 | -66.8971 | 56.4441 | 56.344 | 56.4679 | -67.0573 | -66.9488 | 0.027831 | -67.0154 | 56.3725 | 56.5045 | 56.2421 | -67.2026 | -0.11852 | 0.033914 | 0.012956 | 0.041694 | 0.16021 | -0.066192 | 0.057717 | -0.26383 | -0.037689 | -0.010066 | -0.076622 | 0.18721 | 0.094287 | -0.16807 | 123.3829 | 123.2828 | 123.4067 | 66.9631 | -123.4675 | 123.3113 | 123.4433 | 123.1809 | 66.9666 | -123.6128
98.2344 | 123.642 | -66.9479 | 56.4148 | 0.049183 | -0.00086922 | -0.00077494 | 0.054464 | -0.00079597 | 0.056843 | 0.066374 | 0.0011206 | -0.00051292 | 0.063837 | 0.0063787 | 0.064853 | -66.9304 | 0.033457 | -66.9062 | 56.435 | 56.3349 | 56.4771 | -67.0573 | -66.9443 | 0.018674 | -67.0017 | 56.3863 | 56.4953 | 56.3017 | -67.198 | -0.10937 | 0.020179 | 0.017532 | 0.041692 | 0.15106 | -0.079927 | 0.062296 | -0.2501 | -0.028532 | 0.003668 | -0.053731 | 0.19637 | 0.080552 | -0.11313 | 123.3829 | 123.2828 | 123.425 | 66.9814 | -123.4721 | 123.3342 | 123.4433 | 123.2496 | 66.9666 | -123.6128
99.2344 | 123.642 | -66.9525 | 56.4789 | 0.049183 | -0.0040742 | 0.0013621 | 0.055533 | -0.00079597 | 0.054706 | 0.051113 | 5.2637e-05 | 0.00055508 | 0.063837 | 0.0063787 | 0.064853 | -66.9212 | 0.028878 | -66.9108 | 56.4441 | 56.3211 | 56.4771 | -67.0527 | -66.9397 | 0.023253 | -67.0062 | 56.3817 | 56.4999 | 56.2376 | -67.198 | -0.10021 | -0.034751 | 0.031267 | 0.041692 | 0.1419 | -0.15775 | -0.001791 | -0.24552 | -0.097197 | 0.012825 | -0.053732 | 0.19179 | 0.021044 | -0.24131 | 123.3966 | 123.2736 | 123.4296 | 66.9814 | -123.5316 | 123.3342 | 123.4524 | 123.1901 | 66.9758 | -123.6769
100.2344 | 123.4909 | -66.9434 | 56.4651 | 0.079707 | -0.0030062 | -0.00077494 | 0.055533 | -0.001864 | 0.056843 | 0.066374 | 5.2637e-05 | -0.0026499 | 0.064905 | 0.0063787 | 0.063784 | -66.9258 | 0.033457 | -66.9017 | 56.4487 | 56.3211 | 56.4771 | -67.0573 | -66.9488 | 0.023253 | -67.0062 | 56.3771 | 56.4953 | 56.2421 | -67.198 | -0.11394 | -0.01644 | 0.017533 | 0.041693 | 0.15564 | -0.14402 | 0.011942 | -0.25467 | -0.088043 | -0.005489 | -0.062888 | 0.19179 | 0.030198 | -0.223 | 123.3921 | 123.2645 | 123.4205 | 66.9768 | -123.5225 | 123.3205 | 123.4387 | 123.1855 | 66.9666 | -123.6632
101.2344 | 123.5001 | -66.9342 | 56.4468 | 0.064445 | -0.0030062 | 0.00029306 | 0.055533 | -0.00079597 | 0.056843 | 0.081635 | -0.0010164 | -0.0015819 | 0.062769 | 0.0042417 | 0.063784 | -66.9304 | 0.028878 | -66.9062 | 56.4441 | 56.3257 | 56.4679 | -67.0573 | -66.9443 | 0.023253 | -67.0062 | 56.3817 | 56.4862 | 56.3246 | -67.2072 | -0.1231 | -0.002707 | 0.003799 | 0.027959 | 0.15106 | -0.12113 | 0.021096 | -0.27299 | -0.065153 | -0.010065 | -0.072043 | 0.20094 | 0.039352 | -0.12228 | 123.3783 | 123.2599 | 123.4021 | 66.9631 | -123.5041 | 123.3159 | 123.4204 | 123.2588 | 66.9575 | -123.654
102.25 | 123.5916 | -66.9067 | 56.3919 | 0.064445 | -0.0030062 | -0.0018439 | 0.054464 | 0.00027203 | 0.054706 | 0.051113 | 5.2637e-05 | -0.0015819 | 0.065973 | 0.0053107 | 0.064853 | -66.9258 | 0.019721 | -66.9062 | 56.435 | 56.3257 | 56.4634 | -67.0481 | -66.9397 | 0.023253 | -67.0062 | 56.3817 | 56.4953 | 56.2788 | -67.198 | -0.14141 | 0.043067 | -0.019088 | 0.000493 | 0.1419 | -0.066197 | 0.071449 | -0.29129 | -0.010222 | -0.032952 | -0.099509 | 0.19179 | 0.10344 | -0.11313 | 123.3417 | 123.2324 | 123.3701 | 66.9265 | -123.4401 | 123.2884 | 123.4021 | 123.1855 | 66.93 | -123.5899
103.2344 | 123.4772 | -66.9479 | 56.4377 | 0.033921 | -0.0030062 | 0.00029306 | 0.056601 | -0.001864 | 0.056843 | 0.081635 | 5.2637e-05 | -0.0015819 | 0.063837 | 0.0085157 | 0.062716 | -66.9304 | 0.0243 | -66.9017 | 56.4396 | 56.312 | 56.4588 | -67.0481 | -66.9534 | 0.023253 | -67.0017 | 56.3771 | 56.4816 | 56.3337 | -67.2026 | -0.10021 | 0.00187 | 0.017532 | 0.046271 | 0.14648 | -0.12571 | 0.021094 | -0.25467 | -0.060577 | -0.00549 | -0.053731 | 0.20094 | 0.043928 | -0.10396 | 123.3875 | 123.2599 | 123.4067 | 66.9722 | -123.4858 | 123.325 | 123.4295 | 123.2817 | 66.9712 | -123.6403
104.2344 | 123.4909 | -66.9525 | 56.4468 | 0.049183 | -0.0040742 | 0.00029306 | 0.054464 | -0.00079597 | 0.055774 | 0.066374 | 0.0011206 | -0.0015819 | 0.062769 | 0.0074467 | 0.063784 | -66.9212 | 0.033457 | -66.9017 | 56.4396 | 56.3211 | 56.4725 | -67.039 | -66.9488 | 0.027831 | -67.0017 | 56.3725 | 56.4862 | 56.3566 | -67.198 | -0.086472 | -0.007285 | 0.031267 | 0.050849 | 0.13732 | -0.12571 | 0.025675 | -0.24552 | -0.07431 | 0.003667 | -0.049153 | 0.19637 | 0.039352 | -0.090226 | 123.3921 | 123.2736 | 123.425 | 66.986 | -123.4858 | 123.325 | 123.4387 | 123.3091 | 66.9803 | -123.6449
105.2344 | 123.5275 | -66.9617 | 56.4377 | 0.079707 | -0.00086922 | -0.00077494 | 0.056601 | -0.001864 | 0.055774 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.0617 | 0.0085157 | 0.063784 | -66.9258 | 0.028878 | -66.9017 | 56.4441 | 56.3211 | 56.4725 | -67.039 | -66.9534 | 0.03241 | -67.0062 | 56.3817 | 56.4953 | 56.3566 | -67.1935 | -0.077317 | 0.006448 | 0.035844 | 0.060004 | 0.13732 | -0.11655 | 0.03483 | -0.23178 | -0.055998 | 0.008243 | -0.044577 | 0.18721 | 0.057664 | -0.081071 | 123.4058 | 123.2828 | 123.4342 | 66.9905 | -123.4767 | 123.3434 | 123.457 | 123.3183 | 66.9941 | -123.6311
106.2344 | 123.5367 | -66.9342 | 56.4377 | 0.049183 | -0.0030062 | -0.00077494 | 0.054464 | -0.001864 | 0.054706 | 0.051113 | -0.0010164 | -0.00051292 | 0.063837 | 0.0074467 | 0.062716 | -66.9258 | 0.0243 | -66.8971 | 56.4441 | 56.312 | 56.4679 | -67.0436 | -66.958 | 0.027831 | -67.0062 | 56.3817 | 56.4999 | 56.3337 | -67.2026 | -0.10936 | 0.006448 | 0.008378 | 0.037116 | 0.14648 | -0.12571 | 0.030251 | -0.26841 | -0.055998 | -0.023801 | -0.072043 | 0.19636 | 0.062243 | -0.10396 | 123.3783 | 123.2462 | 123.4021 | 66.9585 | -123.4812 | 123.3159 | 123.4341 | 123.2679 | 66.962 | -123.6403
107.25 | 123.6099 | -66.9296 | 56.3599 | 0.049183 | -0.0040742 | -0.00077494 | 0.054464 | -0.002933 | 0.055774 | 0.051113 | -0.0020844 | -0.0015819 | 0.063837 | 0.0063787 | 0.064853 | -66.9258 | 0.028878 | -66.9108 | 56.435 | 56.3211 | 56.4679 | -67.0665 | -66.9534 | 0.023253 | -67.0062 | 56.3771 | 56.4908 | 56.3246 | -67.2026 | -0.13683 | 0.075111 | 0.0038 | 0.018803 | 0.15564 | -0.038732 | 0.10807 | -0.27299 | 0.017243 | -0.023801 | -0.076621 | 0.19636 | 0.13091 | -0.035301 | 123.3646 | 123.2508 | 123.3976 | 66.9585 | -123.4263 | 123.3067 | 123.4204 | 123.2542 | 66.9529 | -123.5625
108.2344 | 123.4818 | -66.9617 | 56.4377 | 0.049183 | -0.0040742 | -0.00077494 | 0.055533 | -0.001864 | 0.054706 | 0.051113 | 5.2637e-05 | -0.0015819 | 0.063837 | 0.0074467 | 0.061648 | -66.9258 | 0.028878 | -66.9108 | 56.4441 | 56.3166 | 56.4725 | -67.039 | -66.9443 | 0.023253 | -67.0017 | 56.3725 | 56.4953 | 56.3017 | -67.2026 | -0.077317 | 0.006448 | 0.035844 | 0.050847 | 0.12816 | -0.12113 | 0.03483 | -0.24094 | -0.065155 | 0.017401 | -0.039998 | 0.20094 | 0.057664 | -0.13601 | 123.4058 | 123.2782 | 123.4342 | 66.9905 | -123.4767 | 123.3342 | 123.457 | 123.2633 | 66.9849 | -123.6403
109.2344 | 123.5184 | -66.9617 | 56.4331 | 0.049183 | -0.0019382 | 0.00029306 | 0.054464 | -0.001864 | 0.056843 | 0.066374 | -0.0010164 | 0.0016231 | 0.062769 | 0.0063787 | 0.063784 | -66.9258 | 0.019721 | -66.9062 | 56.4487 | 56.3166 | 56.4771 | -67.0344 | -66.9443 | 0.023253 | -67.0154 | 56.3863 | 56.4862 | 56.3383 | -67.2026 | -0.072738 | 0.015604 | 0.035844 | 0.055425 | 0.12816 | -0.11655 | 0.043986 | -0.24094 | -0.046842 | 0.017401 | -0.053734 | 0.18721 | 0.053085 | -0.094808 | 123.4104 | 123.2782 | 123.4388 | 66.9814 | -123.4675 | 123.3479 | 123.4479 | 123.3 | 66.9849 | -123.6357
110.2344 | 123.5046 | -66.9388 | 56.4514 | 0.064445 | -0.0019382 | 0.00029306 | 0.056601 | -0.00079597 | 0.055774 | 0.066374 | -0.0010164 | -0.0015819 | 0.063837 | 0.0063787 | 0.062716 | -66.9258 | 0.033457 | -66.9017 | 56.4487 | 56.312 | 56.4634 | -67.0344 | -66.9488 | 0.018674 | -67.0062 | 56.3725 | 56.4953 | 56.3062 | -67.2026 | -0.095626 | -0.002707 | 0.012956 | 0.037116 | 0.13274 | -0.13944 | 0.01194 | -0.26383 | -0.078888 | -0.010066 | -0.067465 | 0.19636 | 0.043931 | -0.14517 | 123.3875 | 123.2508 | 123.4021 | 66.9722 | -123.4858 | 123.3113 | 123.4341 | 123.245 | 66.9575 | -123.654
111.2344 | 123.5321 | -66.9525 | 56.4468 | 0.064445 | -0.0030062 | -0.00077494 | 0.055533 | -0.00079597 | 0.056843 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.063837 | 0.0074467 | 0.063784 | -66.9258 | 0.028878 | -66.9062 | 56.4441 | 56.3028 | 56.4725 | -67.0527 | -66.9534 | 0.018674 | -67.0062 | 56.3771 | 56.4953 | 56.3062 | -67.2026 | -0.10021 | -0.002707 | 0.026689 | 0.04627 | 0.14648 | -0.14402 | 0.025675 | -0.2501 | -0.069732 | -0.000912 | -0.053732 | 0.19636 | 0.048509 | -0.14059 | 123.3966 | 123.2553 | 123.425 | 66.9814 | -123.4996 | 123.3296 | 123.4479 | 123.2588 | 66.9712 | -123.6494
112.25 | 123.5825 | -66.893 | 56.4102 | 0.018659 | -0.0019382 | 0.00029306 | 0.054464 | -0.001864 | 0.054706 | 0.066374 | -0.0020844 | -0.0026499 | 0.062769 | 0.0063787 | 0.064853 | -66.9212 | 0.028878 | -66.9017 | 56.4396 | 56.3166 | 56.4725 | -67.0436 | -66.9443 | 0.018674 | -66.9971 | 56.3817 | 56.4953 | 56.2742 | -67.2026 | -0.15056 | 0.029336 | -0.028243 | -0.008661 | 0.1419 | -0.093665 | 0.062296 | -0.30961 | -0.028532 | -0.051264 | -0.10408 | 0.20552 | 0.08513 | -0.13602 | 123.3326 | 123.2096 | 123.3655 | 66.9219 | -123.4538 | 123.2747 | 123.3884 | 123.1672 | 66.9117 | -123.6128
113.2344 | 123.5321 | -66.9067 | 56.4102 | 0.064445 | -0.00086922 | -0.00077494 | 0.056601 | -0.00079597 | 0.054706 | 0.066374 | -0.0010164 | -0.0015819 | 0.063837 | 0.0085157 | 0.061648 | -66.9212 | 0.0243 | -66.9062 | 56.4396 | 56.3211 | 56.4771 | -67.0527 | -66.9534 | 0.018674 | -67.0062 | 56.3817 | 56.4862 | 56.2605 | -67.198 | -0.14598 | 0.029336 | -0.01451 | 0.000493 | 0.14648 | -0.089086 | 0.066874 | -0.29129 | -0.028532 | -0.046689 | -0.099509 | 0.19179 | 0.075973 | -0.14976 | 123.3463 | 123.2279 | 123.3838 | 66.931 | -123.4629 | 123.2884 | 123.3929 | 123.1672 | 66.9254 | -123.6082
114.2344 | 123.4177 | -66.9296 | 56.456 | 0.033921 | -0.0019382 | -0.0018439 | 0.054464 | -0.002933 | 0.054706 | 0.066374 | 5.2637e-05 | -0.0015819 | 0.060632 | 0.0085157 | 0.062716 | -66.9258 | 0.0243 | -66.9062 | 56.4487 | 56.3257 | 56.4725 | -67.0436 | -66.9488 | 0.018674 | -67.0017 | 56.3771 | 56.4953 | 56.2559 | -67.1935 | -0.11394 | -0.007285 | 0.0038 | 0.023381 | 0.13732 | -0.13028 | 0.016519 | -0.26383 | -0.078888 | -0.019222 | -0.072042 | 0.19179 | 0.039353 | -0.20011 | 123.3783 | 123.2553 | 123.4021 | 66.9539 | -123.4996 | 123.3067 | 123.425 | 123.1855 | 66.9483 | -123.6494
115.25 | 123.5733 | -66.8976 | 56.4148 | 0.079707 | 0.00019878 | 0.00029306 | 0.054464 | -0.001864 | 0.055774 | 0.035852 | 5.2637e-05 | 0.0016231 | 0.064905 | 0.0063787 | 0.065921 | -66.9212 | 0.028878 | -66.8971 | 56.4396 | 56.344 | 56.4771 | -67.0527 | -66.9534 | 0.018674 | -67.0108 | 56.3771 | 56.4908 | 56.2421 | -67.198 | -0.15514 | 0.024758 | -0.023665 | 0.000495 | 0.15564 | -0.07077 | 0.062296 | -0.30045 | -0.037689 | -0.055844 | -0.11324 | 0.18721 | 0.075974 | -0.17265 | 123.3371 | 123.2416 | 123.3747 | 66.9265 | -123.4675 | 123.2747 | 123.3884 | 123.1397 | 66.9163 | -123.6128
116.2344 | 123.5046 | -66.9525 | 56.4331 | 0.049183 | -0.00086922 | -0.00077494 | 0.054464 | -0.00079597 | 0.054706 | 0.035852 | 5.2637e-05 | 0.00055508 | 0.064905 | 0.0074467 | 0.062716 | -66.9212 | 0.0243 | -66.8971 | 56.4441 | 56.3303 | 56.4679 | -67.0481 | -66.958 | 0.03241 | -67.0017 | 56.3725 | 56.4908 | 56.2421 | -67.2072 | -0.095629 | 0.011026 | 0.031267 | 0.055427 | 0.15106 | -0.10282 | 0.034829 | -0.25467 | -0.060577 | -0.00549 | -0.049153 | 0.20552 | 0.057664 | -0.19096 | 123.3966 | 123.2828 | 123.4204 | 66.9768 | -123.4812 | 123.325 | 123.4433 | 123.1947 | 66.9849 | -123.6403
117.25 | 123.5916 | -66.9022 | 56.4285 | 0.079707 | -0.0030062 | -0.0029119 | 0.055533 | -0.001864 | 0.055774 | 0.066374 | -0.0010164 | -0.0015819 | 0.063837 | 0.0063787 | 0.065921 | -66.9212 | 0.0243 | -66.8971 | 56.4396 | 56.344 | 56.4725 | -67.0436 | -66.9488 | 0.023253 | -67.0062 | 56.3725 | 56.4953 | 56.2009 | -67.198 | -0.1414 | 0.011025 | -0.019087 | 0.005073 | 0.14648 | -0.084503 | 0.043985 | -0.29587 | -0.056 | -0.046687 | -0.10409 | 0.19179 | 0.066819 | -0.22759 | 123.3417 | 123.2462 | 123.3747 | 66.9265 | -123.4721 | 123.2747 | 123.3975 | 123.1031 | 66.9254 | -123.6266
118.2344 | 123.4955 | -66.9708 | 56.4423 | 0.064445 | -0.0019382 | -0.0018439 | 0.055533 | -0.00079597 | 0.055774 | 0.051113 | -0.0020844 | -0.0015819 | 0.064905 | 0.0085157 | 0.061648 | -66.9304 | 0.019721 | -66.9017 | 56.4441 | 56.3349 | 56.4725 | -67.0573 | -66.9626 | 0.023253 | -67.0017 | 56.3771 | 56.4908 | 56.2605 | -67.2026 | -0.086477 | 0.00187 | 0.04042 | 0.069159 | 0.15564 | -0.10739 | 0.030252 | -0.23179 | -0.065155 | 0.008241 | -0.030843 | 0.20094 | 0.048508 | -0.1818 | 123.415 | 123.3057 | 123.4433 | 66.9905 | -123.4996 | 123.3479 | 123.4616 | 123.2313 | 66.9941 | -123.6449
119.2344 | 123.5825 | -66.9479 | 56.4148 | 0.049183 | -0.00086922 | 0.00029306 | 0.054464 | -0.00079597 | 0.055774 | 0.066374 | -0.0020844 | -0.0015819 | 0.062769 | 0.0085157 | 0.062716 | -66.9258 | 0.033457 | -66.9017 | 56.4441 | 56.3394 | 56.4771 | -67.0665 | -66.9488 | 0.03241 | -67.0062 | 56.3863 | 56.4908 | 56.265 | -67.198 | -0.11852 | 0.029336 | 0.022111 | 0.046271 | 0.16479 | -0.075348 | 0.062296 | -0.2501 | -0.028532 | -0.000911 | -0.05831 | 0.19179 | 0.075974 | -0.14975 | 123.3921 | 123.2874 | 123.425 | 66.9814 | -123.4813 | 123.3342 | 123.4387 | 123.213 | 66.9803 | -123.6128
120.25 | 123.6374 | -66.8518 | 56.3965 | 0.049183 | -0.0030062 | -0.00077494 | 0.054464 | 0.00027203 | 0.057911 | 0.096896 | -0.0020844 | -0.00051292 | 0.063837 | 0.0085157 | 0.064853 | -66.9304 | 0.0243 | -66.8971 | 56.4441 | 56.3394 | 56.4725 | -67.0619 | -66.9443 | 0.023253 | -67.0108 | 56.3817 | 56.4908 | 56.2147 | -67.2072 | -0.21007 | 0.047647 | -0.078598 | -0.045281 | 0.16479 | -0.057037 | 0.076029 | -0.35538 | -0.014799 | -0.092462 | -0.15902 | 0.19637 | 0.094285 | -0.18181 | 123.2959 | 123.1913 | 123.3243 | 66.8761 | -123.4584 | 123.2335 | 123.3426 | 123.0665 | 66.8751 | -123.6037
121.2344 | 123.4909 | -66.9434 | 56.4377 | 0.033921 | -0.0030062 | -0.00077494 | 0.05767 | -0.002933 | 0.054706 | 0.066374 | -0.0010164 | -0.00051292 | 0.064905 | 0.0074467 | 0.062716 | -66.9212 | 0.033457 | -66.9062 | 56.4487 | 56.344 | 56.4817 | -67.0665 | -66.9534 | 0.027831 | -67.0062 | 56.3771 | 56.4908 | 56.2971 | -67.2118 | -0.1231 | 0.011026 | 0.022111 | 0.037114 | 0.16022 | -0.093658 | 0.043987 | -0.26841 | -0.060577 | -0.010068 | -0.062888 | 0.20552 | 0.053086 | -0.14059 | 123.3921 | 123.2874 | 123.425 | 66.9768 | -123.5041 | 123.3205 | 123.4341 | 123.2404 | 66.9712 | -123.6495
122.25 | 123.6008 | -66.8838 | 56.4011 | 0.079707 | -0.0019382 | -0.00077494 | 0.055533 | -0.00079597 | 0.054706 | 0.081635 | -0.0031524 | -0.0015819 | 0.062769 | 0.0095837 | 0.061648 | -66.9212 | 0.019721 | -66.9062 | 56.435 | 56.3349 | 56.4679 | -67.0161 | -66.9488 | 0.023253 | -67.0062 | 56.3725 | 56.4953 | 56.265 | -67.2118 | -0.13224 | 0.033912 | -0.037398 | -0.022395 | 0.10985 | -0.066194 | 0.066872 | -0.32792 | -0.028534 | -0.064998 | -0.1224 | 0.20552 | 0.094285 | -0.13602 | 123.3188 | 123.2187 | 123.3518 | 66.9036 | -123.4172 | 123.2564 | 123.3792 | 123.1489 | 66.9071 | -123.6128
123.2344 | 123.5138 | -66.9617 | 56.4285 | 0.049183 | -0.0030062 | 0.00029306 | 0.054464 | -0.001864 | 0.055774 | 0.051113 | -0.0010164 | -0.00051292 | 0.063837 | 0.0074467 | 0.061648 | -66.9258 | 0.028878 | -66.9108 | 56.4396 | 56.344 | 56.4817 | -66.9795 | -66.9443 | 0.018674 | -67.0017 | 56.3817 | 56.4953 | 56.2513 | -67.198 | -0.017791 | 0.011025 | 0.035844 | 0.050847 | 0.068638 | -0.084503 | 0.053142 | -0.23636 | -0.046843 | 0.017401 | -0.039998 | 0.19637 | 0.066819 | -0.17722 | 123.4012 | 123.3057 | 123.4433 | 66.9905 | -123.408 | 123.3434 | 123.457 | 123.213 | 66.9803 | -123.6266
124.2344 | 123.5138 | -66.9388 | 56.4423 | 0.049183 | -0.0019382 | -0.00077494 | 0.055533 | -0.00079597 | 0.055774 | 0.066374 | 5.2637e-05 | -0.0026499 | 0.062769 | 0.0095837 | 0.064853 | -66.9212 | 0.033457 | -66.9062 | 56.4441 | 56.3211 | 56.4679 | -67.0527 | -66.9443 | 0.027831 | -67.0017 | 56.3679 | 56.4862 | 56.2788 | -67.2072 | -0.11394 | 0.00187 | 0.017534 | 0.032537 | 0.14648 | -0.12113 | 0.025673 | -0.26841 | -0.074312 | -0.005487 | -0.062886 | 0.20552 | 0.043929 | -0.16349 | 123.3829 | 123.2599 | 123.4067 | 66.9722 | -123.495 | 123.3067 | 123.425 | 123.2176 | 66.9666 | -123.6495
125.25 | 123.6145 | -66.9205 | 56.4331 | 0.064445 | -0.0030062 | -0.00077494 | 0.054464 | 0.00027203 | 0.055774 | 0.081635 | -0.0020844 | -0.0026499 | 0.063837 | 0.0074467 | 0.062716 | -66.9212 | 0.033457 | -66.9062 | 56.4441 | 56.3486 | 56.4725 | -67.0665 | -66.9443 | 0.023253 | -67.0017 | 56.3725 | 56.4862 | 56.2696 | -67.2026 | -0.14599 | 0.011026 | -0.000777 | 0.014226 | 0.16022 | -0.084501 | 0.039408 | -0.28214 | -0.060577 | -0.023798 | -0.081197 | 0.20094 | 0.053085 | -0.16349 | 123.3646 | 123.2691 | 123.393 | 66.9539 | -123.4996 | 123.293 | 123.4067 | 123.1901 | 66.9437 | -123.6357
126.2344 | 123.5687 | -66.9525 | 56.4148 | 0.049183 | -0.0030062 | 0.00029306 | 0.055533 | -0.001864 | 0.054706 | 0.051113 | -0.0010164 | 0.00055508 | 0.063837 | 0.0095837 | 0.062716 | -66.9212 | 0.0243 | -66.8971 | 56.4487 | 56.344 | 56.4862 | -67.0252 | -66.9534 | 0.027831 | -67.0108 | 56.3725 | 56.4953 | 56.3017 | -67.198 | -0.072735 | 0.033914 | 0.031267 | 0.055427 | 0.12816 | -0.07077 | 0.071454 | -0.24552 | -0.042267 | -0.000912 | -0.05831 | 0.18721 | 0.080552 | -0.11313 | 123.4012 | 123.2965 | 123.4388 | 66.9768 | -123.44 | 123.325 | 123.4479 | 123.2542 | 66.9803 | -123.6128
127.25 | 123.5641 | -66.9205 | 56.4102 | 0.049183 | -0.0030062 | -0.00077494 | 0.055533 | -0.002933 | 0.054706 | 0.035852 | -0.0010164 | -0.0015819 | 0.063837 | 0.0085157 | 0.062716 | -66.9258 | 0.028878 | -66.9017 | 56.4487 | 56.344 | 56.4725 | -67.0069 | -66.9443 | 0.023253 | -67.0062 | 56.3817 | 56.4953 | 56.2742 | -67.2026 | -0.086463 | 0.038492 | -0.005355 | 0.018805 | 0.10527 | -0.066192 | 0.062296 | -0.28214 | -0.028532 | -0.023798 | -0.085776 | 0.19636 | 0.08513 | -0.13602 | 123.3692 | 123.2645 | 123.393 | 66.9493 | -123.4172 | 123.3022 | 123.4158 | 123.1947 | 66.9437 | -123.6128
128.2344 | 123.5001 | -66.9525 | 56.4331 | 0.049183 | -0.0030062 | -0.0018439 | 0.054464 | -0.00079597 | 0.055774 | 0.066374 | 5.2637e-05 | 0.00055508 | 0.0617 | 0.0085157 | 0.063784 | -66.9258 | 0.033457 | -66.9062 | 56.4487 | 56.3394 | 56.4771 | -67.0481 | -66.9488 | 0.018674 | -67.0062 | 56.3817 | 56.5045 | 56.2559 | -67.198 | -0.095629 | 0.015604 | 0.026689 | 0.04627 | 0.1419 | -0.093658 | 0.043986 | -0.24552 | -0.05142 | 0.003667 | -0.053732 | 0.19179 | 0.071399 | -0.17722 | 123.4012 | 123.292 | 123.4296 | 66.986 | -123.4812 | 123.3342 | 123.457 | 123.2084 | 66.9712 | -123.6311
129.2344 | 123.5229 | -66.9342 | 56.4285 | 0.049183 | -0.0019382 | 0.0013621 | 0.052327 | 0.00027203 | 0.057911 | 0.051113 | -0.0010164 | 0.00055508 | 0.062769 | 0.012789 | 0.061648 | -66.9212 | 0.0243 | -66.9108 | 56.4441 | 56.3349 | 56.4725 | -66.9703 | -66.9443 | 0.023253 | -67.0062 | 56.3725 | 56.4999 | 56.2834 | -67.198 | -0.036099 | 0.015603 | 0.012956 | 0.023381 | 0.05948 | -0.09366 | 0.043985 | -0.26383 | -0.056 | -0.010065 | -0.072043 | 0.19179 | 0.071398 | -0.14517 | 123.3783 | 123.2691 | 123.4067 | 66.9585 | -123.3988 | 123.3067 | 123.4341 | 123.2176 | 66.9575 | -123.6266
130.25 | 123.6008 | -66.8884 | 56.4331 | 0.064445 | -0.0030062 | 0.0013621 | 0.055533 | -0.001864 | 0.056843 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.062769 | 0.0085157 | 0.062716 | -66.9304 | 0.028878 | -66.9017 | 56.4533 | 56.2982 | 56.4817 | -66.9428 | -66.9488 | 0.023253 | -67.0017 | 56.3725 | 56.4908 | 56.2284 | -67.2072 | -0.054401 | 0.020183 | -0.041977 | -0.013238 | 0.041163 | -0.13487 | 0.048565 | -0.31876 | -0.060577 | -0.06042 | -0.11324 | 0.20552 | 0.057664 | -0.20469 | 123.3417 | 123.1867 | 123.3701 | 66.9173 | -123.3759 | 123.261 | 123.3792 | 123.1168 | 66.9117 | -123.6403
131.2344 | 123.5458 | -66.9296 | 56.4514 | 0.064445 | -0.00086922 | -0.00077494 | 0.054464 | -0.001864 | 0.054706 | 0.051113 | -0.0020844 | -0.00051292 | 0.063837 | 0.0085157 | 0.062716 | -66.9121 | 0.0243 | -66.9017 | 56.4441 | 56.344 | 56.4725 | -66.952 | -66.9397 | 0.018674 | -67.0108 | 56.3863 | 56.4999 | 56.2879 | -67.2026 | -0.022361 | -0.007285 | 0.017535 | 0.02796 | 0.050321 | -0.10739 | 0.021097 | -0.27299 | -0.065153 | -0.010064 | -0.081199 | 0.19179 | 0.04851 | -0.16348 | 123.3738 | 123.2737 | 123.4021 | 66.9539 | -123.4034 | 123.3159 | 123.4296 | 123.2176 | 66.9483 | -123.654
132.2344 | 123.5641 | -66.9067 | 56.3965 | 0.064445 | -0.00086922 | 0.00029306 | 0.056601 | -0.001864 | 0.057911 | 0.066374 | 5.2637e-05 | -0.0015819 | 0.064905 | 0.0085157 | 0.062716 | -66.9212 | 0.033457 | -66.9062 | 56.4533 | 56.344 | 56.4725 | -66.9657 | -66.9443 | 0.023253 | -67.0062 | 56.3771 | 56.4953 | 56.2467 | -67.198 | -0.058986 | 0.056804 | -0.01451 | 0.000493 | 0.059479 | -0.052459 | 0.076029 | -0.29129 | -0.019378 | -0.037531 | -0.099509 | 0.19179 | 0.098863 | -0.14976 | 123.36 | 123.2508 | 123.3793 | 66.9402 | -123.3622 | 123.2838 | 123.4021 | 123.1535 | 66.93 | -123.5945
133.2344 | 123.5779 | -66.9296 | 56.4239 | 0.033921 | -0.0019382 | -0.00077494 | 0.054464 | -0.00079597 | 0.056843 | 0.066374 | -0.0010164 | 0.00055508 | 0.0617 | 0.010653 | 0.06058 | -66.935 | 0.0243 | -66.9017 | 56.4396 | 56.3486 | 56.4771 | -67.0573 | -66.9397 | 0.023253 | -67.0017 | 56.3817 | 56.4953 | 56.2513 | -67.2072 | -0.12768 | 0.015603 | -0.005357 | 0.02796 | 0.15564 | -0.075346 | 0.053141 | -0.27756 | -0.042265 | -0.010064 | -0.072042 | 0.20552 | 0.071397 | -0.17265 | 123.3692 | 123.2782 | 123.4067 | 66.9539 | -123.4813 | 123.3113 | 123.425 | 123.1809 | 66.9529 | -123.6311
134.2344 | 123.4955 | -66.9342 | 56.4606 | 0.049183 | -0.0019382 | -0.0018439 | 0.054464 | 0.00027203 | 0.054706 | 0.066374 | 0.0011206 | -0.0026499 | 0.063837 | 0.0085157 | 0.061648 | -66.9212 | 0.033457 | -66.9017 | 56.4441 | 56.344 | 56.4588 | -67.0665 | -66.9488 | 0.023253 | -67.0017 | 56.3863 | 56.4908 | 56.2971 | -67.198 | -0.13226 | -0.01644 | 0.012956 | 0.032538 | 0.16479 | -0.11655 | -0.001794 | -0.26383 | -0.074308 | -0.014644 | -0.067464 | 0.19637 | 0.030198 | -0.16348 | 123.3783 | 123.2782 | 123.393 | 66.9677 | -123.527 | 123.3205 | 123.425 | 123.2313 | 66.9575 | -123.6586
135.2344 | 123.5046 | -66.9479 | 56.4423 | 0.049183 | -0.00086922 | 0.00029306 | 0.055533 | 0.00027203 | 0.054706 | 0.051113 | -0.0031524 | 0.00055508 | 0.062769 | 0.0085157 | 0.06058 | -66.9258 | 0.028878 | -66.9108 | 56.4441 | 56.3349 | 56.4725 | -67.0619 | -66.9534 | 0.027831 | -67.0017 | 56.3771 | 56.4953 | 56.2605 | -67.1935 | -0.11394 | 0.00187 | 0.022111 | 0.037114 | 0.15106 | -0.10739 | 0.030252 | -0.24552 | -0.065155 | -0.00549 | -0.053731 | 0.19179 | 0.053086 | -0.1818 | 123.3921 | 123.2828 | 123.4204 | 66.9768 | -123.5041 | 123.325 | 123.4433 | 123.2084 | 66.9758 | -123.6357
136.2344 | 123.5367 | -66.9205 | 56.4194 | 0.033921 | -0.00086922 | 0.00029306 | 0.056601 | 0.00027203 | 0.055774 | 0.066374 | -0.0010164 | -0.00051292 | 0.062769 | 0.0095837 | 0.062716 | -66.9212 | 0.019721 | -66.9017 | 56.4396 | 56.3303 | 56.4771 | -67.0665 | -66.9443 | 0.014095 | -67.0062 | 56.3725 | 56.4908 | 56.2238 | -67.2026 | -0.14599 | 0.02018 | -0.000777 | 0.018805 | 0.16479 | -0.089084 | 0.057718 | -0.28214 | -0.046845 | -0.023798 | -0.085776 | 0.19636 | 0.071396 | -0.19554 | 123.36 | 123.2508 | 123.3976 | 66.9402 | -123.4858 | 123.293 | 123.4112 | 123.1443 | 66.9346 | -123.622
137.25 | 123.5825 | -66.9205 | 56.4194 | 0.049183 | -0.0030062 | 0.00029306 | 0.055533 | -0.002933 | 0.054706 | 0.066374 | -0.0010164 | -0.0015819 | 0.063837 | 0.011721 | 0.061648 | -66.9258 | 0.028878 | -66.9017 | 56.4487 | 56.344 | 56.4679 | -67.0527 | -66.9488 | 0.023253 | -66.9971 | 56.3863 | 56.4908 | 56.2193 | -67.2026 | -0.13225 | 0.029336 | -0.005355 | 0.018805 | 0.15106 | -0.075348 | 0.048561 | -0.28214 | -0.03311 | -0.028377 | -0.076618 | 0.20552 | 0.071396 | -0.20012 | 123.3692 | 123.2645 | 123.3884 | 66.9493 | -123.4721 | 123.3067 | 123.4112 | 123.1397 | 66.9437 | -123.622
138.2344 | 123.5275 | -66.9296 | 56.4514 | 0.049183 | -0.0030062 | 0.00029306 | 0.054464 | -0.00079597 | 0.054706 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.062769 | 0.010653 | 0.062716 | -66.9212 | 0.028878 | -66.9062 | 56.4441 | 56.3349 | 56.4679 | -67.0527 | -66.9488 | 0.027831 | -67.0062 | 56.3817 | 56.4953 | 56.2559 | -67.2026 | -0.1231 | -0.007285 | 0.008378 | 0.023381 | 0.14648 | -0.11655 | 0.016518 | -0.27299 | -0.069731 | -0.019222 | -0.076621 | 0.19636 | 0.043931 | -0.19553 | 123.3738 | 123.2645 | 123.3976 | 66.9585 | -123.5041 | 123.3113 | 123.425 | 123.1855 | 66.9575 | -123.654
139.2344 | 123.6099 | -66.9022 | 56.4148 | 0.064445 | -0.0019382 | -0.0018439 | 0.053396 | -0.001864 | 0.056843 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.064905 | 0.010653 | 0.063784 | -66.9258 | 0.028878 | -66.9017 | 56.4396 | 56.344 | 56.4771 | -67.0619 | -66.9443 | 0.023253 | -67.0062 | 56.3725 | 56.4908 | 56.2559 | -67.2118 | -0.15972 | 0.024758 | -0.023665 | 0.000495 | 0.16021 | -0.07077 | 0.062296 | -0.30961 | -0.042267 | -0.042108 | -0.10409 | 0.20552 | 0.075974 | -0.15891 | 123.3417 | 123.2462 | 123.3793 | 66.931 | -123.4767 | 123.2747 | 123.3929 | 123.158 | 66.9254 | -123.6266
140.2344 | 123.6053 | -66.9296 | 56.4102 | 0.079707 | -0.0030062 | 0.00029306 | 0.054464 | -0.001864 | 0.053638 | 0.066374 | 0.0011206 | 0.00055508 | 0.062769 | 0.0095837 | 0.062716 | -66.9212 | 0.033457 | -66.9017 | 56.4441 | 56.3349 | 56.4679 | -67.0573 | -66.9488 | 0.018674 | -67.0017 | 56.3817 | 56.4862 | 56.2513 | -67.2072 | -0.12768 | 0.033914 | 0.008378 | 0.02796 | 0.15564 | -0.075349 | 0.057717 | -0.27756 | -0.028532 | -0.019222 | -0.072042 | 0.20552 | 0.075973 | -0.15891 | 123.3738 | 123.2645 | 123.3976 | 66.9631 | -123.4675 | 123.3113 | 123.4158 | 123.1809 | 66.9483 | -123.6174
141.2344 | 123.5138 | -66.9479 | 56.4331 | 0.049183 | -0.00086922 | 0.00029306 | 0.054464 | -0.00079597 | 0.054706 | 0.096896 | -0.0010164 | -0.0015819 | 0.063837 | 0.0095837 | 0.061648 | -66.9258 | 0.028878 | -66.9062 | 56.4487 | 56.3257 | 56.4679 | -67.0527 | -66.9443 | 0.027831 | -67.0062 | 56.3817 | 56.4999 | 56.2559 | -67.2072 | -0.10479 | 0.015604 | 0.022111 | 0.041692 | 0.14648 | -0.10739 | 0.034829 | -0.25925 | -0.05142 | 0.003668 | -0.05831 | 0.20094 | 0.066821 | -0.17722 | 123.3966 | 123.2736 | 123.4159 | 66.9768 | -123.4858 | 123.3296 | 123.4479 | 123.2038 | 66.9758 | -123.6403
142.25 | 123.6191 | -66.893 | 56.3919 | 0.049183 | -0.0019382 | -0.00077494 | 0.056601 | 0.00027203 | 0.055774 | 0.051113 | -0.0020844 | -0.0015819 | 0.064905 | 0.0095837 | 0.062716 | -66.9212 | 0.028878 | -66.9017 | 56.4441 | 56.3303 | 56.4725 | -67.0527 | -66.9488 | 0.023253 | -67.0017 | 56.3863 | 56.4862 | 56.2559 | -67.2118 | -0.15972 | 0.052224 | -0.028243 | -0.008661 | 0.15106 | -0.061618 | 0.080606 | -0.31876 | -0.005644 | -0.055843 | -0.10866 | 0.2101 | 0.094283 | -0.13602 | 123.3371 | 123.2233 | 123.3655 | 66.9219 | -123.4446 | 123.2793 | 123.3792 | 123.1489 | 66.9163 | -123.6037
143.2344 | 123.587 | -66.925 | 56.4239 | 0.049183 | -0.0019382 | 0.0013621 | 0.055533 | -0.00079597 | 0.056843 | 0.066374 | -0.0010164 | -0.00051292 | 0.0617 | 0.0085157 | 0.061648 | -66.9258 | 0.0243 | -66.9108 | 56.4396 | 56.3349 | 56.4771 | -67.0527 | -66.9443 | 0.027831 | -67.0062 | 56.3771 | 56.4908 | 56.2971 | -67.198 | -0.12767 | 0.015603 | -0.000777 | 0.014226 | 0.1419 | -0.089082 | 0.053141 | -0.27298 | -0.046844 | -0.01922 | -0.081198 | 0.19179 | 0.066819 | -0.12686 | 123.3646 | 123.2599 | 123.4021 | 66.9493 | -123.4767 | 123.3022 | 123.4158 | 123.2221 | 66.9529 | -123.622
144.2344 | 123.5504 | -66.9113 | 56.4148 | 0.049183 | -0.0030062 | 0.00029306 | 0.055533 | -0.001864 | 0.054706 | 0.051113 | -0.0010164 | 0.00055508 | 0.0617 | 0.010653 | 0.063784 | -66.9258 | 0.0243 | -66.9017 | 56.4441 | 56.344 | 56.4725 | -67.071 | -66.9534 | 0.023253 | -67.0017 | 56.3863 | 56.4953 | 56.2879 | -67.2072 | -0.15972 | 0.029336 | -0.01451 | 0.00965 | 0.16937 | -0.07077 | 0.057718 | -0.29587 | -0.028532 | -0.042111 | -0.090352 | 0.20552 | 0.080552 | -0.12686 | 123.3554 | 123.2553 | 123.3838 | 66.9356 | -123.4858 | 123.2976 | 123.4067 | 123.1992 | 66.9346 | -123.622
145.2344 | 123.5229 | -66.925 | 56.4285 | 0.049183 | -0.0030062 | -0.0018439 | 0.054464 | -0.00079597 | 0.055774 | 0.035852 | -0.0020844 | -0.0015819 | 0.062769 | 0.010653 | 0.062716 | -66.9167 | 0.028878 | -66.9154 | 56.4441 | 56.344 | 56.4771 | -67.0527 | -66.9534 | 0.018674 | -67.0017 | 56.3771 | 56.4908 | 56.265 | -67.2118 | -0.12767 | 0.015603 | 0.00838 | 0.009648 | 0.13732 | -0.084503 | 0.048563 | -0.28672 | -0.051422 | -0.028378 | -0.076619 | 0.2101 | 0.062241 | -0.16349 | 123.3692 | 123.2691 | 123.4021 | 66.9539 | -123.4813 | 123.3022 | 123.4158 | 123.1901 | 66.9437 | -123.6403
146.2344 | 123.6008 | -66.8838 | 56.4102 | 0.049183 | -0.0019382 | -0.00077494 | 0.054464 | -0.001864 | 0.056843 | 0.066374 | 5.2637e-05 | -0.0015819 | 0.063837 | 0.010653 | 0.06058 | -66.9258 | 0.0243 | -66.9108 | 56.435 | 56.3394 | 56.4771 | -67.0527 | -66.958 | 0.027831 | -66.9971 | 56.3817 | 56.4908 | 56.2467 | -67.2026 | -0.16887 | 0.024757 | -0.041976 | -0.026973 | 0.1419 | -0.07077 | 0.066874 | -0.31876 | -0.028532 | -0.074155 | -0.11324 | 0.20552 | 0.080552 | -0.16349 | 123.3188 | 123.2233 | 123.3609 | 66.9081 | -123.4629 | 123.2655 | 123.3746 | 123.1306 | 66.9117 | -123.6128
147.25 | 123.5916 | -66.925 | 56.4102 | 0.049183 | -0.0019382 | 0.00029306 | 0.054464 | -0.002933 | 0.055774 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.063837 | 0.010653 | 0.062716 | -66.9258 | 0.0243 | -66.9017 | 56.4441 | 56.3303 | 56.4679 | -67.0436 | -66.9443 | 0.023253 | -67.0108 | 56.3725 | 56.4953 | 56.2284 | -67.2026 | -0.11852 | 0.033914 | -0.000777 | 0.023383 | 0.1419 | -0.079928 | 0.057717 | -0.27756 | -0.037689 | -0.01922 | -0.085776 | 0.19179 | 0.08513 | -0.18181 | 123.3692 | 123.2553 | 123.393 | 66.9493 | -123.4538 | 123.2976 | 123.4204 | 123.1535 | 66.9483 | -123.6128
148.2344 | 123.5275 | -66.9388 | 56.4239 | 0.049183 | -0.0040742 | -0.0018439 | 0.053396 | -0.00079597 | 0.054706 | 0.066374 | -0.0010164 | 0.0016231 | 0.062769 | 0.011721 | 0.061648 | -66.9212 | 0.0243 | -66.9017 | 56.4441 | 56.3349 | 56.4771 | -67.0481 | -66.9534 | 0.023253 | -67.0017 | 56.3817 | 56.4953 | 56.2284 | -67.2026 | -0.10936 | 0.020181 | 0.017534 | 0.037116 | 0.14648 | -0.089082 | 0.053141 | -0.26383 | -0.042265 | -0.014645 | -0.062886 | 0.20094 | 0.071397 | -0.19554 | 123.3829 | 123.2737 | 123.4159 | 66.9631 | -123.4721 | 123.3205 | 123.4341 | 123.1672 | 66.962 | -123.6266
149.2344 | 123.5413 | -66.9479 | 56.4377 | 0.033921 | -0.0051432 | -0.0018439 | 0.053396 | -0.001864 | 0.054706 | 0.066374 | -0.0020844 | -0.00051292 | 0.0617 | 0.010653 | 0.062716 | -66.9212 | 0.019721 | -66.9108 | 56.4533 | 56.3349 | 56.4771 | -67.0527 | -66.9443 | 0.027831 | -66.9971 | 56.3817 | 56.4953 | 56.265 | -67.2026 | -0.10479 | 0.015605 | 0.026689 | 0.037114 | 0.1419 | -0.10281 | 0.039408 | -0.25467 | -0.055998 | 0.003668 | -0.049152 | 0.20552 | 0.057664 | -0.17264 | 123.4012 | 123.2828 | 123.425 | 66.9677 | -123.4904 | 123.3296 | 123.4433 | 123.213 | 66.9758 | -123.6403
150.2344 | 123.587 | -66.925 | 56.4148 | 0.049183 | -0.0051432 | 0.00029306 | 0.055533 | -0.001864 | 0.053638 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.063837 | 0.011721 | 0.061648 | -66.9212 | 0.028878 | -66.9017 | 56.4487 | 56.3303 | 56.4679 | -67.0573 | -66.9488 | 0.023253 | -67.0017 | 56.3771 | 56.4862 | 56.2284 | -67.2026 | -0.13225 | 0.033914 | 0.003801 | 0.023383 | 0.15564 | -0.084506 | 0.053139 | -0.27756 | -0.037689 | -0.023799 | -0.076619 | 0.20094 | 0.071395 | -0.18638 | 123.3738 | 123.2553 | 123.393 | 66.9539 | -123.4721 | 123.3022 | 123.4112 | 123.1535 | 66.9483 | -123.6174
151.2344 | 123.555 | -66.9296 | 56.4423 | 0.049183 | -0.0030062 | 0.0024301 | 0.054464 | -0.00079597 | 0.056843 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.062769 | 0.011721 | 0.061648 | -66.9212 | 0.0243 | -66.9017 | 56.4487 | 56.3486 | 56.4771 | -67.0573 | -66.9488 | 0.03241 | -67.0062 | 56.3817 | 56.4908 | 56.2925 | -67.2026 | -0.12768 | 0.006448 | 0.008378 | 0.02796 | 0.15564 | -0.093657 | 0.03483 | -0.27299 | -0.060576 | -0.019222 | -0.076621 | 0.19636 | 0.048508 | -0.14975 | 123.3783 | 123.2782 | 123.4067 | 66.9539 | -123.4996 | 123.3113 | 123.4204 | 123.2221 | 66.962 | -123.6449
152.2344 | 123.6053 | -66.9113 | 56.3873 | 0.064445 | -0.0030062 | -0.00077494 | 0.053396 | -0.00079597 | 0.055774 | 0.035852 | 5.2637e-05 | -0.00051292 | 0.063837 | 0.010653 | 0.061648 | -66.9212 | 0.0243 | -66.9062 | 56.4487 | 56.3349 | 56.4817 | -67.0573 | -66.9443 | 0.03241 | -67.0017 | 56.3771 | 56.4908 | 56.2834 | -67.2072 | -0.14599 | 0.06138 | -0.009932 | 0.005071 | 0.15106 | -0.052461 | 0.094341 | -0.29587 | -0.010223 | -0.032953 | -0.090352 | 0.20552 | 0.10344 | -0.10397 | 123.36 | 123.2462 | 123.393 | 66.9356 | -123.4446 | 123.2884 | 123.4021 | 123.1947 | 66.9437 | -123.5945
153.2344 | 123.587 | -66.9296 | 56.4102 | 0.049183 | -0.0040742 | 0.00029306 | 0.053396 | 0.00027203 | 0.053638 | 0.066374 | 5.2637e-05 | -0.0026499 | 0.063837 | 0.011721 | 0.063784 | -66.9212 | 0.0243 | -66.9062 | 56.4487 | 56.3394 | 56.4817 | -67.0436 | -66.9488 | 0.023253 | -67.0108 | 56.3817 | 56.4953 | 56.2925 | -67.2072 | -0.11394 | 0.038492 | 0.008378 | 0.023381 | 0.13732 | -0.07077 | 0.071453 | -0.27756 | -0.028532 | -0.019222 | -0.081199 | 0.19637 | 0.08513 | -0.11771 | 123.3783 | 123.2691 | 123.4113 | 66.9539 | -123.4538 | 123.3113 | 123.425 | 123.2221 | 66.9529 | -123.6174
154.2344 | 123.6191 | -66.9159 | 56.4194 | 0.049183 | -0.0019382 | -0.00077494 | 0.052327 | -0.001864 | 0.055774 | 0.051113 | 5.2637e-05 | -0.0015819 | 0.065973 | 0.012789 | 0.06058 | -66.9258 | 0.028878 | -66.9108 | 56.4396 | 56.3303 | 56.4771 | -67.0573 | -66.9443 | 0.027831 | -67.0017 | 56.3817 | 56.4908 | 56.2193 | -67.2072 | -0.14141 | 0.02018 | -0.009932 | 0.005071 | 0.14648 | -0.089084 | 0.057718 | -0.2913 | -0.037688 | -0.028375 | -0.085774 | 0.20552 | 0.071396 | -0.20012 | 123.3554 | 123.2462 | 123.393 | 66.9448 | -123.4767 | 123.2976 | 123.4067 | 123.1351 | 66.9437 | -123.6266
155.2344 | 123.5138 | -66.9434 | 56.4285 | 0.049183 | -0.0040742 | -0.00077494 | 0.053396 | -0.001864 | 0.055774 | 0.066374 | -0.0010164 | -0.00051292 | 0.062769 | 0.012789 | 0.061648 | -66.9258 | 0.028878 | -66.9017 | 56.4579 | 56.3303 | 56.4725 | -67.0481 | -66.9488 | 0.027831 | -67.0108 | 56.3771 | 56.4908 | 56.2696 | -67.2072 | -0.10478 | 0.029338 | 0.017533 | 0.041693 | 0.14648 | -0.098239 | 0.043985 | -0.26383 | -0.051422 | -0.005489 | -0.067466 | 0.19637 | 0.062241 | -0.15891 | 123.4012 | 123.2736 | 123.4159 | 66.9722 | -123.4767 | 123.3205 | 123.4341 | 123.213 | 66.9712 | -123.6357
156.2344 | 123.5138 | -66.9388 | 56.4514 | 0.049183 | -0.0040742 | -0.00077494 | 0.055533 | -0.00079597 | 0.055774 | 0.066374 | -0.0010164 | -0.0026499 | 0.063837 | 0.010653 | 0.062716 | -66.9167 | 0.019721 | -66.9108 | 56.4396 | 56.3394 | 56.4771 | -67.0527 | -66.9443 | 0.03241 | -67.0017 | 56.3817 | 56.4953 | 56.2376 | -67.2072 | -0.11394 | -0.011863 | 0.022113 | 0.027959 | 0.1419 | -0.11197 | 0.025675 | -0.26841 | -0.069731 | -0.005487 | -0.062886 | 0.20552 | 0.043931 | -0.21385 | 123.3783 | 123.2782 | 123.4159 | 66.9585 | -123.5041 | 123.3205 | 123.4341 | 123.1764 | 66.9712 | -123.6586
157.25 | 123.6099 | -66.9022 | 56.4102 | 0.049183 | -0.0030062 | -0.0018439 | 0.053396 | 0.00027203 | 0.054706 | 0.066374 | -0.0020844 | 0.00055508 | 0.063837 | 0.011721 | 0.061648 | -66.9212 | 0.0243 | -66.8971 | 56.4441 | 56.3303 | 56.4679 | -67.0436 | -66.9488 | 0.018674 | -67.0017 | 56.3771 | 56.4908 | 56.2467 | -67.198 | -0.1414 | 0.033914 | -0.019087 | 0.005073 | 0.14648 | -0.079928 | 0.057717 | -0.29587 | -0.033111 | -0.046687 | -0.099507 | 0.19637 | 0.080552 | -0.16349 | 123.3463 | 123.2325 | 123.3701 | 66.9265 | -123.4538 | 123.2793 | 123.3929 | 123.1489 | 66.9208 | -123.6082
158.2344 | 123.6145 | -66.9159 | 56.3828 | 0.049183 | -0.0040742 | -0.00077494 | 0.056601 | -0.002933 | 0.053638 | 0.081635 | -0.0010164 | -0.00051292 | 0.062769 | 0.010653 | 0.061648 | -66.9258 | 0.019721 | -66.9017 | 56.4396 | 56.3303 | 56.4679 | -67.0527 | -66.9488 | 0.023253 | -67.0017 | 56.3771 | 56.4999 | 56.2559 | -67.2072 | -0.13683 | 0.056802 | -0.009932 | 0.014228 | 0.15106 | -0.052462 | 0.085183 | -0.2913 | -0.005645 | -0.032954 | -0.085774 | 0.20552 | 0.11718 | -0.12687 | 123.3554 | 123.2462 | 123.3838 | 66.9356 | -123.4355 | 123.293 | 123.4158 | 123.1718 | 66.9391 | -123.5899
159.2344 | 123.5229 | -66.9388 | 56.4148 | 0.064445 | -0.0040742 | -0.0018439 | 0.055533 | -0.00079597 | 0.053638 | 0.066374 | -0.0010164 | -0.00051292 | 0.062769 | 0.012789 | 0.061648 | -66.9258 | 0.028878 | -66.9062 | 56.4396 | 56.3394 | 56.4817 | -67.0481 | -66.9488 | 0.027831 | -66.9971 | 56.3725 | 56.4953 | 56.2925 | -67.2072 | -0.10936 | 0.024758 | 0.012956 | 0.032537 | 0.1419 | -0.075348 | 0.066875 | -0.26841 | -0.042267 | -0.010066 | -0.058307 | 0.2101 | 0.080552 | -0.12228 | 123.3783 | 123.2782 | 123.4205 | 66.9677 | -123.4629 | 123.3113 | 123.4341 | 123.2313 | 66.9666 | -123.622
160.2344 | 123.5229 | -66.9479 | 56.4102 | 0.079707 | -0.0019382 | -0.00077494 | 0.054464 | -0.001864 | 0.055774 | 0.066374 | -0.0010164 | -0.0015819 | 0.062769 | 0.012789 | 0.062716 | -66.9304 | 0.028878 | -66.9062 | 56.4396 | 56.3303 | 56.4817 | -67.0527 | -66.9488 | 0.03241 | -67.0017 | 56.3817 | 56.5045 | 56.2376 | -67.2072 | -0.10479 | 0.029336 | 0.017532 | 0.041692 | 0.14648 | -0.079928 | 0.071453 | -0.25925 | -0.028532 | -0.000911 | -0.053731 | 0.20552 | 0.094287 | -0.17265 | 123.3875 | 123.2782 | 123.4296 | 66.9768 | -123.4629 | 123.3296 | 123.4524 | 123.1855 | 66.9803 | -123.6174
161.2344 | 123.6237 | -66.9067 | 56.4011 | 0.033921 | -0.0051432 | -0.0018439 | 0.054464 | -0.00079597 | 0.055774 | 0.051113 | -0.0010164 | 0.00055508 | 0.062769 | 0.011721 | 0.061648 | -66.9212 | 0.0243 | -66.8925 | 56.4441 | 56.3349 | 56.4817 | -67.0436 | -66.9488 | 0.027831 | -67.0108 | 56.3725 | 56.4953 | 56.233 | -67.2026 | -0.13683 | 0.043069 | -0.01451 | 0.014228 | 0.15105 | -0.066194 | 0.080608 | -0.29587 | -0.028534 | -0.04211 | -0.10409 | 0.19179 | 0.094285 | -0.16807 | 123.3509 | 123.2416 | 123.3884 | 66.931 | -123.4446 | 123.2793 | 123.4021 | 123.1397 | 66.9346 | -123.6037
162.25 | 123.5779 | -66.9113 | 56.4239 | 0.049183 | -0.0030062 | -0.00077494 | 0.054464 | -0.00079597 | 0.054706 | 0.051113 | -0.0010164 | -0.00051292 | 0.062769 | 0.012789 | 0.061648 | -66.9212 | 0.028878 | -66.9017 | 56.4441 | 56.3257 | 56.4817 | -67.039 | -66.9443 | 0.018674 | -67.0062 | 56.3771 | 56.5045 | 56.2055 | -67.1935 | -0.12767 | 0.020181 | -0.009932 | 0.00965 | 0.13732 | -0.09824 | 0.05772 | -0.28214 | -0.046844 | -0.032953 | -0.094931 | 0.18721 | 0.080554 | -0.21843 | 123.3554 | 123.237 | 123.393 | 66.9402 | -123.4629 | 123.2884 | 123.4158 | 123.1168 | 66.93 | -123.6174
163.2344 | 123.5184 | -66.9205 | 56.4285 | 0.049183 | -0.0040742 | 0.00029306 | 0.055533 | -0.001864 | 0.055774 | 0.051113 | -0.0031524 | -0.0015819 | 0.0617 | 0.012789 | 0.062716 | -66.9212 | 0.028878 | -66.9062 | 56.4487 | 56.3303 | 56.4725 | -67.0481 | -66.9534 | 0.023253 | -67.0017 | 56.3771 | 56.4862 | 56.2376 | -67.2072 | -0.12767 | 0.020181 | -0.000777 | 0.014226 | 0.1419 | -0.098239 | 0.043985 | -0.28672 | -0.051422 | -0.032956 | -0.081197 | 0.20552 | 0.057662 | -0.19096 | 123.3692 | 123.2508 | 123.393 | 66.9493 | -123.4767 | 123.2976 | 123.4067 | 123.158 | 66.9437 | -123.6357
164.2344 | 123.5962 | -66.9159 | 56.4148 | 0.049183 | -0.0030062 | 0.00029306 | 0.053396 | -0.001864 | 0.054706 | 0.066374 | 5.2637e-05 | -0.00051292 | 0.062769 | 0.010653 | 0.063784 | -66.9212 | 0.028878 | -66.8971 | 56.435 | 56.3349 | 56.4771 | -67.0436 | -66.9397 | 0.014095 | -67.0062 | 56.3817 | 56.4908 | 56.2513 | -67.2072 | -0.12767 | 0.020179 | -0.005354 | 0.018806 | 0.14648 | -0.079927 | 0.062296 | -0.2913 | -0.03311 | -0.023796 | -0.090353 | 0.20094 | 0.075974 | -0.16349 | 123.3509 | 123.2508 | 123.393 | 66.9448 | -123.4584 | 123.2976 | 123.4067 | 123.1672 | 66.93 | -123.622
165.2344 | 123.5596 | -66.9296 | 56.4148 | 0.049183 | -0.0040742 | -0.0018439 | 0.053396 | -0.001864 | 0.054706 | 0.066374 | -0.0010164 | 0.0016231 | 0.062769 | 0.011721 | 0.062716 | -66.9167 | 0.028878 | -66.9017 | 56.4441 | 56.3349 | 56.4771 | -67.039 | -66.9488 | 0.018674 | -67.0062 | 56.3771 | 56.4908 | 56.2513 | -67.2026 | -0.10936 | 0.029336 | 0.012957 | 0.02796 | 0.13732 | -0.079927 | 0.062296 | -0.27299 | -0.037689 | -0.019222 | -0.076621 | 0.19636 | 0.075974 | -0.16349 | 123.3738 | 123.2645 | 123.4067 | 66.9585 | -123.4538 | 123.3067 | 123.4204 | 123.1809 | 66.9483 | -123.6174
166.2344 | 123.5687 | -66.925 | 56.4011 | 0.064445 | -0.0030062 | 0.00029306 | 0.053396 | -0.001864 | 0.054706 | 0.066374 | -0.0010164 | -0.0015819 | 0.062769 | 0.010653 | 0.06058 | -66.9212 | 0.033457 | -66.9062 | 56.4396 | 56.3349 | 56.4771 | -67.0436 | -66.9534 | 0.03241 | -67.0108 | 56.3863 | 56.4908 | 56.2559 | -67.198 | -0.11852 | 0.038491 | 0.003801 | 0.018804 | 0.13732 | -0.066194 | 0.076029 | -0.27298 | -0.014799 | -0.028378 | -0.085776 | 0.18721 | 0.089707 | -0.14518 | 123.3646 | 123.2599 | 123.4021 | 66.9585 | -123.4446 | 123.3113 | 123.4158 | 123.1809 | 66.9575 | -123.5991
167.2344 | 123.6328 | -66.8747 | 56.4423 | 0.064445 | -0.0062112 | -0.00077494 | 0.053396 | -0.00079597 | 0.056843 | 0.051113 | 5.2637e-05 | -0.0026499 | 0.063837 | 0.012789 | 0.06058 | -66.9212 | 0.028878 | -66.9062 | 56.435 | 56.344 | 56.4817 | -67.0527 | -66.9488 | 0.018674 | -67.0017 | 56.3771 | 56.4953 | 56.2376 | -67.2026 | -0.17803 | -0.007287 | -0.046553 | -0.03155 | 0.14648 | -0.098236 | 0.039409 | -0.32792 | -0.065155 | -0.074153 | -0.12697 | 0.20094 | 0.053086 | -0.20469 | 123.3097 | 123.2187 | 123.3564 | 66.9036 | -123.495 | 123.2518 | 123.37 | 123.1123 | 66.8934 | -123.6449
168.2344 | 123.7061 | -66.9067 | 56.4102 | 0.064445 | -0.0040742 | -0.0018439 | 0.055533 | -0.00079597 | 0.054706 | 0.051113 | -0.0010164 | 0.00055508 | 0.064905 | 0.013858 | 0.061648 | -66.9167 | 0.019721 | -66.9108 | 56.4441 | 56.3303 | 56.4771 | -67.039 | -66.9488 | 0.018674 | -67.0062 | 56.3817 | 56.4953 | 56.2376 | -67.2026 | -0.13225 | 0.033914 | -0.009931 | -0.004085 | 0.12816 | -0.079928 | 0.066874 | -0.29587 | -0.028532 | -0.04211 | -0.099509 | 0.19636 | 0.08513 | -0.17265 | 123.3509 | 123.237 | 123.3838 | 66.9265 | -123.4492 | 123.2884 | 123.4021 | 123.1443 | 66.9254 | -123.6128
169.2344 | 123.555 | -66.9113 | 56.4194 | 0.033921 | -0.0051432 | -0.00077494 | 0.053396 | -0.001864 | 0.055774 | 0.051113 | -0.0020844 | -0.00051292 | 0.062769 | 0.013858 | 0.06058 | -66.9212 | 0.028878 | -66.8971 | 56.4487 | 56.3257 | 56.4771 | -67.0573 | -66.9488 | 0.03241 | -67.0017 | 56.3771 | 56.4953 | 56.2925 | -67.2163 | -0.14599 | 0.029336 | -0.009932 | 0.014228 | 0.16021 | -0.093663 | 0.057718 | -0.30503 | -0.042267 | -0.037532 | -0.090352 | 0.21468 | 0.075974 | -0.12686 | 123.36 | 123.237 | 123.3884 | 66.9402 | -123.4767 | 123.2884 | 123.4067 | 123.2038 | 66.9437 | -123.6357
170.2344 | 123.555 | -66.9434 | 56.4285 | 0.049183 | -0.0040742 | 0.00029306 | 0.054464 | -0.004001 | 0.054706 | 0.051113 | -0.0010164 | -0.0015819 | 0.062769 | 0.012789 | 0.062716 | -66.9212 | 0.028878 | -66.9062 | 56.4487 | 56.3394 | 56.4725 | -67.0436 | -66.9488 | 0.023253 | -67.0017 | 56.3817 | 56.4999 | 56.2742 | -67.2026 | -0.10021 | 0.020181 | 0.022111 | 0.037114 | 0.13732 | -0.089081 | 0.043985 | -0.25925 | -0.046843 | -0.005489 | -0.058309 | 0.20094 | 0.071398 | -0.15433 | 123.3921 | 123.2828 | 123.4159 | 66.9722 | -123.4721 | 123.325 | 123.4433 | 123.2176 | 66.9666 | -123.6311
171.2344 | 123.6237 | -66.9067 | 56.4011 | 0.049183 | -0.0040742 | 0.00029306 | 0.053396 | -0.00079597 | 0.055774 | 0.066374 | -0.0010164 | -0.0026499 | 0.062769 | 0.012789 | 0.06058 | -66.9212 | 0.0243 | -66.8925 | 56.4441 | 56.3394 | 56.4771 | -67.0481 | -66.9534 | 0.027831 | -67.0017 | 56.3771 | 56.4953 | 56.2193 | -67.2026 | -0.14141 | 0.043069 | -0.01451 | 0.014228 | 0.15563 | -0.061615 | 0.076029 | -0.29587 | -0.023956 | -0.046689 | -0.09493 | 0.20094 | 0.094285 | -0.18181 | 123.3509 | 123.2462 | 123.3838 | 66.931 | -123.4492 | 123.2838 | 123.4021 | 123.126 | 66.9346 | -123.6037
172.2344 | 123.6282 | -66.893 | 56.4194 | 0.033921 | -0.0040742 | 0.00029306 | 0.054464 | -0.00079597 | 0.053638 | 0.066374 | -0.0020844 | -0.00051292 | 0.063837 | 0.010653 | 0.059511 | -66.9258 | 0.0243 | -66.9062 | 56.4396 | 56.3349 | 56.4725 | -67.0436 | -66.9488 | 0.023253 | -66.9971 | 56.3817 | 56.4999 | 56.2788 | -67.2072 | -0.15056 | 0.02018 | -0.032821 | -0.01324 | 0.13732 | -0.084505 | 0.05314 | -0.31418 | -0.037688 | -0.055843 | -0.10408 | 0.2101 | 0.080553 | -0.1406 | 123.3326 | 123.2279 | 123.3655 | 66.9173 | -123.4629 | 123.2747 | 123.3929 | 123.1718 | 66.9163 | -123.6266
173.2344 | 123.6374 | -66.9159 | 56.4102 | 0.018659 | -0.0051432 | 0.00029306 | 0.053396 | -0.00079597 | 0.055774 | 0.051113 | -0.0010164 | 0.00055508 | 0.062769 | 0.014926 | 0.061648 | -66.9167 | 0.028878 | -66.9062 | 56.4441 | 56.3349 | 56.4725 | -67.0436 | -66.958 | 0.018674 | -67.0017 | 56.3817 | 56.4999 | 56.2284 | -67.2072 | -0.12767 | 0.033914 | -0.000775 | 0.009649 | 0.13732 | -0.075349 | 0.062296 | -0.2913 | -0.028532 | -0.042111 | -0.085774 | 0.20552 | 0.089709 | -0.18181 | 123.36 | 123.2508 | 123.3884 | 66.9448 | -123.4538 | 123.2976 | 123.4158 | 123.1443 | 66.9346 | -123.6174
174.2344 | 123.6145 | -66.8838 | 56.4011 | 0.079707 | -0.0040742 | -0.00077494 | 0.053396 | 0.00027203 | 0.054706 | 0.081635 | 0.0011206 | -0.0015819 | 0.063837 | 0.012789 | 0.061648 | -66.9258 | 0.0243 | -66.9017 | 56.4533 | 56.3394 | 56.4725 | -67.0619 | -66.9443 | 0.018674 | -67.0108 | 56.3771 | 56.4953 | 56.2284 | -67.2072 | -0.17803 | 0.052226 | -0.041976 | -0.017816 | 0.16021 | -0.061615 | 0.071451 | -0.32334 | -0.023956 | -0.060419 | -0.12698 | 0.19637 | 0.094285 | -0.17265 | 123.3371 | 123.2233 | 123.3564 | 66.9081 | -123.4629 | 123.261 | 123.3792 | 123.1123 | 66.9025 | -123.6083
175.2344 | 123.6465 | -66.8838 | 56.4011 | 0.064445 | -0.0051432 | 0.00029306 | 0.053396 | -0.00079597 | 0.054706 | 0.066374 | 5.2637e-05 | -0.0015819 | 0.064905 | 0.012789 | 0.061648 | -66.9304 | 0.0243 | -66.9017 | 56.4396 | 56.3394 | 56.4771 | -67.0573 | -66.9488 | 0.023253 | -67.0062 | 56.3817 | 56.5045 | 56.2605 | -67.2072 | -0.17345 | 0.038491 | -0.046555 | -0.017816 | 0.15564 | -0.061615 | 0.076029 | -0.32334 | -0.019377 | -0.064998 | -0.1224 | 0.20094 | 0.10344 | -0.1406 | 123.3234 | 123.2233 | 123.3609 | 66.9081 | -123.4584 | 123.2655 | 123.3884 | 123.1443 | 66.9071 | -123.6083
176.2344 | 123.6099 | -66.8747 | 56.4468 | 0.064445 | -0.0040742 | 0.00029306 | 0.053396 | -0.00079597 | 0.053638 | 0.066374 | -0.0020844 | -0.0026499 | 0.062769 | 0.013858 | 0.06058 | -66.9212 | 0.028878 | -66.9017 | 56.4441 | 56.3349 | 56.4725 | -67.0573 | -66.9488 | 0.027831 | -66.9971 | 56.3725 | 56.4953 | 56.2559 | -67.2118 | -0.18261 | -0.002707 | -0.046553 | -0.026971 | 0.15564 | -0.11197 | 0.025675 | -0.33707 | -0.07431 | -0.074153 | -0.12239 | 0.21468 | 0.048509 | -0.19096 | 123.3188 | 123.2096 | 123.3472 | 66.9036 | -123.5041 | 123.2472 | 123.37 | 123.1306 | 66.9025 | -123.6586
177.2344 | 123.6099 | -66.9022 | 56.3919 | 0.049183 | -0.0062112 | -0.00077494 | 0.054464 | -0.001864 | 0.054706 | 0.035852 | -0.0020844 | -0.0015819 | 0.063837 | 0.013858 | 0.061648 | -66.9212 | 0.028878 | -66.9017 | 56.4487 | 56.3394 | 56.4862 | -67.0573 | -66.9488 | 0.023253 | -67.0017 | 56.3817 | 56.4908 | 56.2421 | -67.2072 | -0.15514 | 0.056802 | -0.019087 | 0.000495 | 0.15564 | -0.05246 | 0.094342 | -0.30503 | -0.010222 | -0.046687 | -0.099507 | 0.20552 | 0.098862 | -0.14976 | 123.3509 | 123.2416 | 123.3884 | 66.931 | -123.4492 | 123.2838 | 123.3929 | 123.1443 | 66.9254 | -123.5991
178.2344 | 123.6145 | -66.8793 | 56.3965 | 0.064445 | -0.0040742 | 0.00029306 | 0.054464 | -0.001864 | 0.054706 | 0.051113 | -0.0020844 | -0.0015819 | 0.0617 | 0.014926 | 0.063784 | -66.9258 | 0.0243 | -66.9108 | 56.4441 | 56.3486 | 56.4817 | -67.0527 | -66.9443 | 0.018674 | -67.0017 | 56.3817 | 56.5091 | 56.2421 | -67.2118 | -0.17345 | 0.047647 | -0.046554 | -0.031551 | 0.1419 | -0.04788 | 0.085186 | -0.3325 | -0.014799 | -0.064997 | -0.1224 | 0.2101 | 0.1126 | -0.15434 | 123.3234 | 123.2279 | 123.3609 | 66.9036 | -123.4492 | 123.261 | 123.3884 | 123.1214 | 66.8979 | -123.6083
179.2344 | 123.6237 | -66.8976 | 56.4011 | 0.064445 | -0.0062112 | -0.0018439 | 0.053396 | -0.001864 | 0.053638 | 0.035852 | -0.0020844 | -0.0015819 | 0.0617 | 0.014926 | 0.061648 | -66.9212 | 0.0243 | -66.9017 | 56.4487 | 56.3303 | 56.4725 | -67.0573 | -66.958 | 0.014095 | -66.9971 | 56.3817 | 56.4953 | 56.265 | -67.2026 | -0.15972 | 0.047647 | -0.023665 | -0.004083 | 0.15564 | -0.070773 | 0.071451 | -0.30503 | -0.019377 | -0.060422 | -0.099506 | 0.20552 | 0.094285 | -0.13602 | 123.3463 | 123.2279 | 123.3701 | 66.9219 | -123.4584 | 123.2793 | 123.3929 | 123.1626 | 66.9117 | -123.6037
180.2344 | 123.6237 | -66.8976 | 56.4331 | 0.064445 | -0.0040742 | -0.00077494 | 0.055533 | -0.001864 | 0.053638 | 0.081635 | -0.0020844 | -0.0015819 | 0.062769 | 0.015994 | 0.06058 | -66.9258 | 0.019721 | -66.9062 | 56.4441 | 56.3349 | 56.4725 | -67.0481 | -66.9443 | 0.023253 | -66.9925 | 56.3771 | 56.4953 | 56.2559 | -67.2026 | -0.15056 | 0.011026 | -0.028243 | -0.008662 | 0.1419 | -0.098237 | 0.039408 | -0.30503 | -0.055999 | -0.046686 | -0.094927 | 0.2101 | 0.062242 | -0.17722 | 123.3417 | 123.2325 | 123.3701 | 66.9173 | -123.4812 | 123.2747 | 123.3929 | 123.1535 | 66.9208 | -123.6357
181.2344 | 123.5962 | -66.9205 | 56.3919 | 0.064445 | -0.0040742 | -0.00077494 | 0.054464 | -0.00079597 | 0.055774 | 0.051113 | 5.2637e-05 | -0.0015819 | 0.0617 | 0.014926 | 0.06058 | -66.9212 | 0.028878 | -66.9017 | 56.4533 | 56.3303 | 56.4771 | -67.039 | -66.9443 | 0.023253 | -67.0062 | 56.3817 | 56.4953 | 56.2605 | -67.2026 | -0.11852 | 0.061381 | -0.000777 | 0.018805 | 0.13732 | -0.061618 | 0.085184 | -0.28214 | -0.010222 | -0.023798 | -0.085776 | 0.19636 | 0.10344 | -0.13145 | 123.3738 | 123.2508 | 123.3976 | 66.9493 | -123.4309 | 123.3022 | 123.4158 | 123.1809 | 66.9437 | -123.5945
182.2344 | 123.5641 | -66.9205 | 56.4194 | 0.049183 | -0.0040742 | -0.00077494 | 0.053396 | -0.001864 | 0.054706 | 0.066374 | -0.0010164 | -0.00051292 | 0.0617 | 0.014926 | 0.062716 | -66.9167 | 0.028878 | -66.8925 | 56.4396 | 56.3257 | 56.4725 | -67.0481 | -66.9488 | 0.023253 | -66.9971 | 56.3817 | 56.4908 | 56.2559 | -67.2118 | -0.12767 | 0.02018 | 0.003802 | 0.027961 | 0.15563 | -0.093663 | 0.05314 | -0.2913 | -0.037688 | -0.028377 | -0.076618 | 0.21468 | 0.071396 | -0.16349 | 123.36 | 123.2462 | 123.393 | 66.9493 | -123.4675 | 123.3022 | 123.4112 | 123.1764 | 66.9437 | -123.6311
183.2344 | 123.6328 | -66.8884 | 56.3873 | 0.049183 | -0.0051432 | 0.00029306 | 0.054464 | -0.00079597 | 0.053638 | 0.051113 | -0.0031524 | -0.0026499 | 0.062769 | 0.015994 | 0.06058 | -66.9167 | 0.033457 | -66.8971 | 56.4441 | 56.3303 | 56.4817 | -67.0573 | -66.9534 | 0.027831 | -67.0017 | 56.3725 | 56.4953 | 56.2467 | -67.2026 | -0.16887 | 0.056802 | -0.028241 | -0.00866 | 0.16021 | -0.05704 | 0.094341 | -0.31418 | -0.014801 | -0.064999 | -0.11324 | 0.20094 | 0.10802 | -0.1406 | 123.3326 | 123.2187 | 123.3701 | 66.9219 | -123.4446 | 123.261 | 123.3838 | 123.1352 | 66.9163 | -123.5899
184.2344 | 123.6053 | -66.893 | 56.3782 | 0.033921 | -0.0040742 | 0.00029306 | 0.052327 | -0.001864 | 0.053638 | 0.066374 | -0.0020844 | 0.00055508 | 0.0617 | 0.013858 | 0.06058 | -66.9212 | 0.0243 | -66.9108 | 56.4441 | 56.3394 | 56.4817 | -67.0436 | -66.9488 | 0.023253 | -67.0062 | 56.3771 | 56.5045 | 56.2101 | -67.198 | -0.15056 | 0.065957 | -0.028243 | -0.017818 | 0.13274 | -0.038727 | 0.1035 | -0.30503 | -0.001068 | -0.055843 | -0.11324 | 0.19179 | 0.12633 | -0.16808 | 123.3371 | 123.2325 | 123.3747 | 66.9173 | -123.4217 | 123.2701 | 123.3975 | 123.1031 | 66.9163 | -123.5762
185.2344 | 123.6053 | -66.893 | 56.4468 | 0.049183 | -0.0040742 | 0.00029306 | 0.052327 | -0.001864 | 0.055774 | 0.051113 | -0.0010164 | -0.0015819 | 0.062769 | 0.014926 | 0.06058 | -66.9167 | 0.028878 | -66.9062 | 56.4487 | 56.3349 | 56.4771 | -67.0481 | -66.9443 | 0.027831 | -67.0062 | 56.3817 | 56.4908 | 56.265 | -67.2072 | -0.15514 | 0.001871 | -0.023664 | -0.01324 | 0.1419 | -0.11197 | 0.030253 | -0.31418 | -0.065153 | -0.051264 | -0.11324 | 0.20094 | 0.043931 | -0.1818 | 123.3417 | 123.2279 | 123.3701 | 66.9219 | -123.495 | 123.2747 | 123.3838 | 123.158 | 66.9208 | -123.654
186.2344 | 123.6053 | -66.9067 | 56.3965 | 0.064445 | -0.0040742 | 0.00029306 | 0.055533 | -0.001864 | 0.055774 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.0617 | 0.014926 | 0.06058 | -66.9258 | 0.028878 | -66.9062 | 56.4441 | 56.3349 | 56.4817 | -67.0573 | -66.9443 | 0.023253 | -66.9925 | 56.3771 | 56.4953 | 56.2467 | -67.2072 | -0.15056 | 0.047647 | -0.019088 | 0.000493 | 0.15106 | -0.061616 | 0.085186 | -0.30045 | -0.019378 | -0.037531 | -0.085772 | 0.21468 | 0.098863 | -0.14976 | 123.3509 | 123.2416 | 123.3884 | 66.9356 | -123.4538 | 123.2838 | 123.4021 | 123.1535 | 66.93 | -123.6037
187.2344 | 123.6053 | -66.8838 | 56.4148 | 0.049183 | -0.0051432 | 0.00029306 | 0.054464 | -0.00079597 | 0.055774 | 0.081635 | 5.2637e-05 | -0.00051292 | 0.0617 | 0.017063 | 0.061648 | -66.9212 | 0.028878 | -66.9017 | 56.4487 | 56.3303 | 56.4817 | -67.0481 | -66.9488 | 0.023253 | -67.0017 | 56.3725 | 56.4999 | 56.2193 | -67.2118 | -0.16429 | 0.033914 | -0.037398 | -0.017816 | 0.14648 | -0.084506 | 0.066875 | -0.32792 | -0.042267 | -0.064998 | -0.11782 | 0.2101 | 0.085131 | -0.19554 | 123.3326 | 123.2141 | 123.3655 | 66.9127 | -123.4629 | 123.2564 | 123.3838 | 123.1031 | 66.9071 | -123.6266
188.2344 | 123.5779 | -66.9067 | 56.3873 | 0.079707 | -0.0040742 | -0.0018439 | 0.054464 | 0.00027203 | 0.052569 | 0.035852 | -0.0010164 | -0.0026499 | 0.062769 | 0.015994 | 0.062716 | -66.9121 | 0.033457 | -66.9017 | 56.4441 | 56.3303 | 56.4771 | -67.0436 | -66.9488 | 0.014095 | -67.0062 | 56.3771 | 56.4999 | 56.2467 | -67.2026 | -0.13683 | 0.056802 | -0.005353 | 0.005072 | 0.1419 | -0.05704 | 0.089762 | -0.29587 | -0.010223 | -0.04211 | -0.099509 | 0.19636 | 0.1126 | -0.1406 | 123.3509 | 123.237 | 123.3838 | 66.9402 | -123.4309 | 123.2838 | 123.4067 | 123.1535 | 66.9208 | -123.5899
189.2344 | 123.5596 | -66.9113 | 56.4239 | 0.033921 | -0.0062112 | -0.0018439 | 0.054464 | -0.001864 | 0.053638 | 0.081635 | -0.0020844 | -0.00051292 | 0.062769 | 0.014926 | 0.061648 | -66.9167 | 0.028878 | -66.9017 | 56.4396 | 56.3349 | 56.4771 | -67.0481 | -66.9488 | 0.023253 | -67.0108 | 56.3863 | 56.4953 | 56.2788 | -67.2026 | -0.13683 | 0.015603 | -0.005353 | 0.00965 | 0.14648 | -0.089082 | 0.053141 | -0.2913 | -0.037687 | -0.037532 | -0.099509 | 0.19179 | 0.071397 | -0.14517 | 123.3509 | 123.2462 | 123.3884 | 66.9402 | -123.4721 | 123.2976 | 123.4067 | 123.1901 | 66.9346 | -123.6266
190.2344 | 123.6191 | -66.8976 | 56.3965 | 0.064445 | -0.0051432 | -0.00077494 | 0.054464 | -0.00079597 | 0.055774 | 0.051113 | 5.2637e-05 | 0.00055508 | 0.0617 | 0.014926 | 0.061648 | -66.9212 | 0.0243 | -66.9017 | 56.4441 | 56.3394 | 56.4862 | -67.039 | -66.9488 | 0.023253 | -67.0017 | 56.3863 | 56.4908 | 56.2788 | -67.2072 | -0.1414 | 0.047647 | -0.023665 | -0.004083 | 0.13732 | -0.057037 | 0.089765 | -0.30961 | -0.010221 | -0.051265 | -0.10408 | 0.20552 | 0.094285 | -0.11771 | 123.3417 | 123.237 | 123.3838 | 66.9219 | -123.4355 | 123.2838 | 123.3884 | 123.1764 | 66.9208 | -123.6037
191.2344 | 123.6008 | -66.8793 | 56.3873 | 0.049183 | -0.0062112 | -0.0018439 | 0.053396 | -0.001864 | 0.054706 | 0.051113 | -0.0010164 | -0.00051292 | 0.0617 | 0.017063 | 0.059511 | -66.9212 | 0.0243 | -66.9062 | 56.4441 | 56.3349 | 56.4725 | -67.0481 | -66.9488 | 0.027831 | -66.9971 | 56.3679 | 56.4953 | 56.1918 | -67.2072 | -0.16887 | 0.056802 | -0.041976 | -0.026973 | 0.1419 | -0.052461 | 0.085184 | -0.32792 | -0.01938 | -0.069576 | -0.11782 | 0.2101 | 0.10802 | -0.19555 | 123.3234 | 123.2141 | 123.3518 | 66.9036 | -123.4355 | 123.2472 | 123.3746 | 123.0711 | 66.9071 | -123.5945
192.25 | 123.6511 | -66.8838 | 56.4468 | 0.033921 | -0.0040742 | -0.00077494 | 0.055533 | -0.00079597 | 0.054706 | 0.066374 | -0.0010164 | -0.00051292 | 0.062769 | 0.014926 | 0.059511 | -66.9212 | 0.028878 | -66.9017 | 56.4396 | 56.3303 | 56.4725 | -67.0573 | -66.9443 | 0.014095 | -67.0062 | 56.3863 | 56.4953 | 56.2376 | -67.2072 | -0.17345 | -0.007285 | -0.037398 | -0.017816 | 0.15564 | -0.11655 | 0.025675 | -0.32334 | -0.060575 | -0.060419 | -0.1224 | 0.20094 | 0.048509 | -0.20927 | 123.3234 | 123.2141 | 123.3564 | 66.9127 | -123.5041 | 123.2701 | 123.3792 | 123.1214 | 66.8979 | -123.654
193.2344 | 123.5962 | -66.9067 | 56.4377 | 0.064445 | -0.0072792 | -0.0018439 | 0.052327 | -0.002933 | 0.054706 | 0.051113 | -0.0020844 | -0.00051292 | 0.062769 | 0.014926 | 0.06058 | -66.9212 | 0.033457 | -66.8971 | 56.4396 | 56.3303 | 56.4771 | -67.039 | -66.9443 | 0.023253 | -67.0062 | 56.3817 | 56.4953 | 56.1964 | -67.2026 | -0.13225 | 0.00187 | -0.01451 | 0.00965 | 0.1419 | -0.10739 | 0.039408 | -0.29587 | -0.055998 | -0.037531 | -0.099509 | 0.19636 | 0.057664 | -0.24132 | 123.3463 | 123.237 | 123.3838 | 66.9402 | -123.4767 | 123.2884 | 123.4021 | 123.1031 | 66.93 | -123.6403
194.2344 | 123.5825 | -66.9022 | 56.4239 | 0.049183 | -0.0072792 | -0.00077494 | 0.053396 | -0.00079597 | 0.054706 | 0.051113 | -0.0031524 | 0.00055508 | 0.062769 | 0.018131 | 0.059511 | -66.9167 | 0.0243 | -66.8971 | 56.4396 | 56.3257 | 56.4679 | -67.0527 | -66.9397 | 0.027831 | -66.9925 | 56.3863 | 56.4908 | 56.2742 | -67.2118 | -0.15056 | 0.015603 | -0.014508 | 0.005073 | 0.15564 | -0.09824 | 0.043984 | -0.30961 | -0.037687 | -0.037529 | -0.090349 | 0.21926 | 0.066819 | -0.14975 | 123.3417 | 123.2279 | 123.3701 | 66.9265 | -123.4767 | 123.2884 | 123.3929 | 123.1764 | 66.93 | -123.6357
195.2344 | 123.5641 | -66.9159 | 56.4102 | 0.033921 | -0.0062112 | -0.0018439 | 0.053396 | -0.001864 | 0.054706 | 0.081635 | -0.0020844 | -0.0015819 | 0.060632 | 0.015994 | 0.059511 | -66.9258 | 0.028878 | -66.9017 | 56.4487 | 56.3257 | 56.4817 | -67.0481 | -66.9488 | 0.023253 | -66.9971 | 56.3725 | 56.4862 | 56.233 | -67.2118 | -0.13225 | 0.038492 | -0.009932 | 0.014228 | 0.14648 | -0.084507 | 0.071453 | -0.29588 | -0.037689 | -0.032954 | -0.081195 | 0.21468 | 0.075973 | -0.17723 | 123.3646 | 123.2416 | 123.3976 | 66.9448 | -123.4584 | 123.2884 | 123.4021 | 123.1489 | 66.9391 | -123.622
196.2344 | 123.587 | -66.9022 | 56.4377 | 0.049183 | -0.0040742 | 0.00029306 | 0.053396 | -0.004001 | 0.052569 | 0.096896 | -0.0020844 | -0.00051292 | 0.060632 | 0.015994 | 0.06058 | -66.9258 | 0.0243 | -66.9017 | 56.4396 | 56.3303 | 56.4771 | -67.0527 | -66.9443 | 0.018674 | -66.9971 | 56.3863 | 56.4953 | 56.2559 | -67.2118 | -0.15056 | 0.00187 | -0.023665 | 0.000495 | 0.15106 | -0.10739 | 0.039408 | -0.30961 | -0.05142 | -0.042108 | -0.094928 | 0.21468 | 0.057664 | -0.1818 | 123.3417 | 123.2325 | 123.3793 | 66.9265 | -123.4904 | 123.2884 | 123.3975 | 123.158 | 66.9208 | -123.6495
197.25 | 123.6237 | -66.8793 | 56.4239 | 0.033921 | -0.0051432 | -0.0018439 | 0.053396 | -0.002933 | 0.053638 | 0.081635 | -0.0020844 | -0.0015819 | 0.060632 | 0.017063 | 0.061648 | -66.9121 | 0.028878 | -66.9062 | 56.4304 | 56.3394 | 56.4771 | -67.0481 | -66.9488 | 0.023253 | -67.0062 | 56.3771 | 56.4999 | 56.2742 | -67.2026 | -0.16887 | 0.006446 | -0.032819 | -0.026973 | 0.1419 | -0.084503 | 0.053141 | -0.32334 | -0.046844 | -0.069576 | -0.12698 | 0.19636 | 0.075976 | -0.14975 | 123.3097 | 123.2187 | 123.3564 | 66.9082 | -123.4721 | 123.2564 | 123.3792 | 123.1535 | 66.9025 | -123.6266
198.2344 | 123.5687 | -66.9113 | 56.4285 | 0.049183 | -0.0051432 | 0.00029306 | 0.053396 | -0.001864 | 0.054706 | 0.051113 | 5.2637e-05 | 0.00055508 | 0.062769 | 0.014926 | 0.061648 | -66.9212 | 0.033457 | -66.9017 | 56.4441 | 56.3349 | 56.4771 | -67.0573 | -66.9397 | 0.018674 | -66.9971 | 56.3771 | 56.5045 | 56.2742 | -67.2026 | -0.14599 | 0.015603 | -0.009932 | 0.00965 | 0.15564 | -0.09366 | 0.048563 | -0.2913 | -0.051422 | -0.028374 | -0.085773 | 0.20552 | 0.075976 | -0.15433 | 123.3554 | 123.2462 | 123.3884 | 66.9448 | -123.4858 | 123.2884 | 123.4158 | 123.1855 | 66.93 | -123.6311
199.2344 | 123.5962 | -66.8884 | 56.4377 | 0.079707 | -0.0072792 | -0.00077494 | 0.052327 | -0.001864 | 0.055774 | 0.066374 | -0.0020844 | -0.00051292 | 0.062769 | 0.018131 | 0.06058 | -66.9212 | 0.028878 | -66.9017 | 56.4396 | 56.3303 | 56.4817 | -67.0527 | -66.9443 | 0.023253 | -66.9971 | 56.3908 | 56.5045 | 56.2879 | -67.2072 | -0.16429 | 0.00187 | -0.03282 | -0.013238 | 0.15106 | -0.10739 | 0.043987 | -0.31876 | -0.046841 | -0.055841 | -0.10866 | 0.2101 | 0.066821 | -0.14975 | 123.328 | 123.2187 | 123.3701 | 66.9173 | -123.4904 | 123.2793 | 123.3929 | 123.1764 | 66.9117 | -123.6449
200.2344 | 123.6053 | -66.8976 | 56.3828 | 0.049183 | -0.0072792 | 0.00029306 | 0.053396 | -0.004001 | 0.054706 | 0.066374 | -0.0020844 | 0.00055508 | 0.062769 | 0.014926 | 0.061648 | -66.9167 | 0.028878 | -66.9062 | 56.4441 | 56.3257 | 56.4771 | -67.039 | -66.9534 | 0.018674 | -66.9925 | 56.3863 | 56.4953 | 56.2925 | -67.2118 | -0.1414 | 0.06138 | -0.019086 | -0.008662 | 0.13274 | -0.057041 | 0.09434 | -0.31419 | 0.003512 | -0.055844 | -0.094927 | 0.21926 | 0.1126 | -0.09024 | 123.3417 | 123.2233 | 123.3747 | 66.9265 | -123.4217 | 123.2838 | 123.3929 | 123.1901 | 66.9163 | -123.5945
201.2344 | 123.7015 | -66.8976 | 56.4239 | 0.079707 | -0.0062112 | -0.00077494 | 0.054464 | -0.001864 | 0.053638 | 0.066374 | -0.0020844 | -0.0015819 | 0.0617 | 0.015994 | 0.06058 | -66.9167 | 0.033457 | -66.8971 | 56.4533 | 56.344 | 56.4771 | -67.0619 | -66.9488 | 0.023253 | -66.9925 | 56.3771 | 56.4953 | 56.2742 | -67.2163 | -0.1643 | 0.029338 | -0.019086 | 0.000495 | 0.16479 | -0.079925 | 0.053141 | -0.31876 | -0.046844 | -0.051265 | -0.094927 | 0.22384 | 0.071397 | -0.14975 | 123.3509 | 123.2416 | 123.3747 | 66.931 | -123.4858 | 123.2747 | 123.3929 | 123.1718 | 66.9208 | -123.6403
202.25 | 123.6923 | -66.8198 | 56.456 | 0.064445 | -0.0051432 | 0.00029306 | 0.054464 | -0.001864 | 0.054706 | 0.066374 | -0.0042204 | -0.0015819 | 0.0617 | 0.017063 | 0.058443 | -66.9258 | 0.019721 | -66.9062 | 56.4441 | 56.3303 | 56.4725 | -67.0527 | -66.9443 | 0.023253 | -67.0017 | 56.3771 | 56.4953 | 56.2696 | -67.2072 | -0.23296 | -0.011863 | -0.10606 | -0.086482 | 0.14648 | -0.1257 | 0.016519 | -0.38743 | -0.078888 | -0.12451 | -0.18191 | 0.20552 | 0.039353 | -0.18638 | 123.2639 | 123.1501 | 123.2923 | 66.8395 | -123.5087 | 123.1969 | 123.3151 | 123.0894 | 66.843 | -123.6632
203.2344 | 123.5779 | -66.9067 | 56.4239 | 0.079707 | -0.0072792 | -0.00077494 | 0.054464 | -0.002933 | 0.055774 | 0.066374 | -0.0010164 | -0.00051292 | 0.060632 | 0.015994 | 0.059511 | -66.9212 | 0.0243 | -66.9017 | 56.4441 | 56.3257 | 56.4817 | -67.0481 | -66.9488 | 0.018674 | -67.0017 | 56.3725 | 56.4999 | 56.2193 | -67.2209 | -0.14141 | 0.020181 | -0.01451 | 0.005072 | 0.14648 | -0.09824 | 0.05772 | -0.31419 | -0.051422 | -0.04211 | -0.09493 | 0.21926 | 0.075976 | -0.2047 | 123.3509 | 123.2324 | 123.3884 | 66.931 | -123.4721 | 123.2793 | 123.4067 | 123.126 | 66.9254 | -123.6449
204.2344 | 123.6099 | -66.8884 | 56.4011 | 0.079707 | -0.0051432 | 0.00029306 | 0.054464 | -0.001864 | 0.053638 | 0.035852 | -0.0031524 | -0.0015819 | 0.0617 | 0.017063 | 0.06058 | -66.9212 | 0.0243 | -66.9017 | 56.4441 | 56.3349 | 56.4817 | -67.0481 | -66.9488 | 0.018674 | -66.9971 | 56.3725 | 56.5045 | 56.2421 | -67.2118 | -0.15972 | 0.043069 | -0.03282 | -0.013238 | 0.14648 | -0.066194 | 0.080608 | -0.32334 | -0.028534 | -0.06042 | -0.10866 | 0.21468 | 0.10344 | -0.15892 | 123.3326 | 123.2233 | 123.3701 | 66.9127 | -123.4492 | 123.261 | 123.3929 | 123.1306 | 66.9071 | -123.6128
205.2344 | 123.5962 | -66.8976 | 56.4331 | 0.064445 | -0.0062112 | -0.0029119 | 0.054464 | -0.001864 | 0.054706 | 0.066374 | -0.0020844 | -0.0026499 | 0.0617 | 0.018131 | 0.06058 | -66.9167 | 0.028878 | -66.8925 | 56.4533 | 56.3303 | 56.4817 | -67.0527 | -66.9397 | 0.027831 | -66.9971 | 56.3771 | 56.5045 | 56.2788 | -67.2118 | -0.15514 | 0.020183 | -0.019086 | 0.005073 | 0.16021 | -0.10282 | 0.048565 | -0.31419 | -0.055999 | -0.042107 | -0.099506 | 0.21468 | 0.071399 | -0.15433 | 123.3509 | 123.2279 | 123.3793 | 66.9265 | -123.4858 | 123.2747 | 123.4021 | 123.1764 | 66.9254 | -123.6449
206.25 | 123.5367 | -66.9022 | 56.4514 | 0.064445 | -0.0083482 | 0.00029306 | 0.052327 | -0.001864 | 0.053638 | 0.066374 | 5.2637e-05 | -0.0026499 | 0.0617 | 0.018131 | 0.06058 | -66.9167 | 0.028878 | -66.9062 | 56.4441 | 56.344 | 56.4817 | -67.0527 | -66.9443 | 0.03241 | -66.9925 | 56.3771 | 56.5045 | 56.2696 | -67.2072 | -0.15056 | -0.007285 | -0.014508 | -0.004084 | 0.14648 | -0.10739 | 0.030254 | -0.30503 | -0.07431 | -0.042108 | -0.090349 | 0.21468 | 0.053088 | -0.1818 | 123.3463 | 123.2462 | 123.3838 | 66.931 | -123.5041 | 123.2793 | 123.4067 | 123.1718 | 66.9346 | -123.6586
207.25 | 123.5779 | -66.9022 | 56.4377 | 0.064445 | -0.0072792 | -0.0018439 | 0.053396 | -0.004001 | 0.055774 | 0.051113 | -0.0020844 | -0.0015819 | 0.0617 | 0.018131 | 0.059511 | -66.9167 | 0.028878 | -66.9017 | 56.4487 | 56.344 | 56.4771 | -67.039 | -66.9397 | 0.03241 | -67.0017 | 56.3771 | 56.5045 | 56.2696 | -67.2072 | -0.13683 | 0.011026 | -0.014508 | 0.000495 | 0.13732 | -0.093658 | 0.039408 | -0.30503 | -0.060577 | -0.037529 | -0.099507 | 0.20552 | 0.066821 | -0.16806 | 123.3509 | 123.2462 | 123.3793 | 66.931 | -123.4767 | 123.2793 | 123.4067 | 123.1718 | 66.9346 | -123.6449
208.2344 | 123.6465 | -66.8655 | 56.4194 | 0.049183 | -0.0062112 | -0.00077494 | 0.053396 | -0.004001 | 0.054706 | 0.081635 | -0.0042204 | -0.0015819 | 0.0617 | 0.017063 | 0.059511 | -66.9212 | 0.0243 | -66.9062 | 56.4396 | 56.3303 | 56.4817 | -67.0619 | -66.9534 | 0.018674 | -66.9971 | 56.3817 | 56.4908 | 56.178 | -67.2118 | -0.19634 | 0.02018 | -0.055708 | -0.040705 | 0.15564 | -0.089084 | 0.062297 | -0.34623 | -0.037688 | -0.087887 | -0.13155 | 0.21468 | 0.071396 | -0.24133 | 123.3051 | 123.1958 | 123.3472 | 66.8898 | -123.4813 | 123.2472 | 123.3563 | 123.0436 | 66.8842 | -123.6311
209.2344 | 123.5596 | -66.8838 | 56.4194 | 0.079707 | -0.0062112 | -0.00077494 | 0.053396 | -0.002933 | 0.055774 | 0.051113 | -0.0020844 | -0.00051292 | 0.062769 | 0.018131 | 0.06058 | -66.9212 | 0.0243 | -66.8971 | 56.4396 | 56.3349 | 56.4817 | -67.039 | -66.9397 | 0.023253 | -67.0017 | 56.3725 | 56.5045 | 56.2101 | -67.2072 | -0.15514 | 0.02018 | -0.037398 | -0.013238 | 0.1419 | -0.084505 | 0.062297 | -0.32334 | -0.046845 | -0.05584 | -0.11782 | 0.20552 | 0.085131 | -0.20928 | 123.3234 | 123.2187 | 123.3655 | 66.9081 | -123.4584 | 123.2564 | 123.3884 | 123.0939 | 66.9071 | -123.6266
210.2344 | 123.6328 | -66.893 | 56.4102 | 0.049183 | -0.0072792 | -0.0018439 | 0.055533 | -0.002933 | 0.053638 | 0.051113 | -0.0031524 | -0.0037179 | 0.060632 | 0.018131 | 0.059511 | -66.9167 | 0.0243 | -66.9062 | 56.4487 | 56.3303 | 56.4817 | -67.039 | -66.9397 | 0.023253 | -67.0017 | 56.3817 | 56.5091 | 56.2559 | -67.2072 | -0.14598 | 0.038492 | -0.023664 | -0.01324 | 0.13274 | -0.079928 | 0.071453 | -0.31418 | -0.028532 | -0.046685 | -0.10866 | 0.20552 | 0.098866 | -0.15433 | 123.3417 | 123.2233 | 123.3747 | 66.9173 | -123.4492 | 123.2747 | 123.4021 | 123.1489 | 66.9163 | -123.6174
211.25 | 123.5916 | -66.8884 | 56.456 | 0.079707 | -0.0062112 | -0.00077494 | 0.054464 | -0.001864 | 0.051501 | 0.051113 | -0.0010164 | -0.0037179 | 0.0617 | 0.015994 | 0.059511 | -66.9121 | 0.028878 | -66.9062 | 56.4487 | 56.3394 | 56.4817 | -67.0436 | -66.9443 | 0.023253 | -66.9971 | 56.3771 | 56.4999 | 56.2742 | -67.2118 | -0.15514 | -0.007285 | -0.023663 | -0.017817 | 0.13732 | -0.11655 | 0.025676 | -0.32334 | -0.078888 | -0.055841 | -0.10866 | 0.21468 | 0.043932 | -0.1818 | 123.3371 | 123.2279 | 123.3701 | 66.9173 | -123.4996 | 123.2655 | 123.3884 | 123.1626 | 66.9117 | -123.6678
212.2344 | 123.5779 | -66.9205 | 56.4194 | 0.049183 | -0.0062112 | -0.00077494 | 0.052327 | -0.002933 | 0.054706 | 0.081635 | -0.0020844 | -0.0026499 | 0.062769 | 0.018131 | 0.06058 | -66.9212 | 0.028878 | -66.9017 | 56.4441 | 56.3257 | 56.4817 | -67.0436 | -66.9443 | 0.027831 | -66.9971 | 56.3817 | 56.4999 | 56.2605 | -67.2163 | -0.12309 | 0.024758 | -0.000777 | 0.018805 | 0.1419 | -0.093663 | 0.062297 | -0.29588 | -0.037688 | -0.023798 | -0.076618 | 0.21926 | 0.080553 | -0.15891 | 123.3646 | 123.2462 | 123.4021 | 66.9493 | -123.4629 | 123.3022 | 123.4204 | 123.1809 | 66.9483 | -123.6357
213.2344 | 123.6145 | -66.9022 | 56.4148 | 0.064445 | -0.0083482 | -0.0018439 | 0.052327 | -0.004001 | 0.054706 | 0.081635 | -0.0020844 | -0.0015819 | 0.0617 | 0.019199 | 0.058443 | -66.9212 | 0.0243 | -66.9017 | 56.4396 | 56.3349 | 56.4817 | -67.0527 | -66.9534 | 0.023253 | -67.0017 | 56.3863 | 56.5045 | 56.2284 | -67.2118 | -0.15056 | 0.024758 | -0.019087 | 0.000495 | 0.15106 | -0.079927 | 0.066875 | -0.30961 | -0.028532 | -0.051266 | -0.099507 | 0.2101 | 0.089709 | -0.18638 | 123.3417 | 123.237 | 123.3838 | 66.9265 | -123.4675 | 123.2884 | 123.4067 | 123.1306 | 66.9254 | -123.6266
214.2344 | 123.6374 | -66.893 | 56.3919 | 0.064445 | -0.0083482 | -0.00077494 | 0.052327 | -0.001864 | 0.053638 | 0.051113 | -0.0010164 | -0.00051292 | 0.0617 | 0.020268 | 0.06058 | -66.9167 | 0.028878 | -66.9108 | 56.4487 | 56.3394 | 56.4771 | -67.0436 | -66.9397 | 0.023253 | -66.9971 | 56.3817 | 56.5045 | 56.233 | -67.2072 | -0.15056 | 0.056802 | -0.023664 | -0.017818 | 0.13274 | -0.05246 | 0.085184 | -0.31418 | -0.010222 | -0.046685 | -0.10408 | 0.2101 | 0.1126 | -0.15892 | 123.3417 | 123.2325 | 123.3701 | 66.9219 | -123.4355 | 123.2747 | 123.3975 | 123.126 | 66.9163 | -123.5991
215.2344 | 123.6008 | -66.9022 | 56.4194 | 0.049183 | -0.0072792 | 0.00029306 | 0.054464 | -0.002933 | 0.053638 | 0.066374 | -0.0020844 | -0.0026499 | 0.060632 | 0.015994 | 0.06058 | -66.9212 | 0.0243 | -66.9017 | 56.4441 | 56.3394 | 56.4908 | -67.0344 | -66.9488 | 0.027831 | -67.0017 | 56.3771 | 56.4999 | 56.2605 | -67.2163 | -0.13225 | 0.024758 | -0.019087 | 0.000495 | 0.13274 | -0.079926 | 0.071454 | -0.31419 | -0.042267 | -0.046687 | -0.099507 | 0.21468 | 0.080553 | -0.15891 | 123.3463 | 123.2416 | 123.393 | 66.9265 | -123.4538 | 123.2793 | 123.4021 | 123.1626 | 66.93 | -123.6357
216.25 | 123.587 | -66.8793 | 56.4468 | 0.064445 | -0.0083482 | -0.00077494 | 0.054464 | -0.001864 | 0.054706 | 0.081635 | 5.2637e-05 | -0.00051292 | 0.062769 | 0.020268 | 0.06058 | -66.9167 | 0.033457 | -66.9108 | 56.4487 | 56.3303 | 56.4817 | -67.0573 | -66.9443 | 0.023253 | -67.0062 | 56.3771 | 56.5045 | 56.2605 | -67.2072 | -0.17803 | 0.001871 | -0.037397 | -0.031551 | 0.14648 | -0.11655 | 0.034832 | -0.32792 | -0.069732 | -0.064997 | -0.12698 | 0.20094 | 0.057666 | -0.18638 | 123.328 | 123.2096 | 123.3609 | 66.9127 | -123.5041 | 123.2564 | 123.3838 | 123.1397 | 66.9025 | -123.654
217.25 | 123.6008 | -66.8884 | 56.4377 | 0.033921 | -0.0072792 | -0.00077494 | 0.053396 | -0.002933 | 0.053638 | 0.035852 | 0.0011206 | -0.0026499 | 0.0617 | 0.019199 | 0.059511 | -66.9167 | 0.0243 | -66.9017 | 56.4396 | 56.3394 | 56.4817 | -67.0527 | -66.9397 | 0.018674 | -67.0017 | 56.3817 | 56.4999 | 56.2193 | -67.2118 | -0.16429 | 0.00187 | -0.028241 | -0.013238 | 0.15106 | -0.098236 | 0.043987 | -0.32334 | -0.055998 | -0.051262 | -0.11324 | 0.2101 | 0.062243 | -0.21843 | 123.328 | 123.2279 | 123.3701 | 66.9127 | -123.4904 | 123.2701 | 123.3884 | 123.1077 | 66.9071 | -123.6495
218.2344 | 123.6099 | -66.893 | 56.4011 | 0.079707 | -0.0072792 | -0.00077494 | 0.053396 | -0.001864 | 0.053638 | 0.051113 | -0.0020844 | -0.0015819 | 0.0617 | 0.018131 | 0.06058 | -66.9212 | 0.028878 | -66.9017 | 56.4396 | 56.3394 | 56.4817 | -67.0527 | -66.9397 | 0.023253 | -66.9925 | 56.3771 | 56.5045 | 56.265 | -67.2118 | -0.15972 | 0.038491 | -0.028243 | -0.008661 | 0.15106 | -0.061615 | 0.080608 | -0.31876 | -0.023956 | -0.046685 | -0.099505 | 0.21926 | 0.10344 | -0.13602 | 123.3326 | 123.2325 | 123.3747 | 66.9219 | -123.4538 | 123.2701 | 123.3975 | 123.158 | 66.9163 | -123.6128
219.2344 | 123.6145 | -66.893 | 56.3919 | 0.064445 | -0.0094162 | -0.00077494 | 0.052327 | -0.004001 | 0.053638 | 0.081635 | -0.0020844 | -0.00051292 | 0.0617 | 0.020268 | 0.058443 | -66.9212 | 0.028878 | -66.9062 | 56.4487 | 56.3394 | 56.4817 | -67.0436 | -66.9443 | 0.018674 | -67.0017 | 56.3817 | 56.4999 | 56.2238 | -67.2118 | -0.15056 | 0.056802 | -0.028243 | -0.01324 | 0.13732 | -0.05246 | 0.089763 | -0.31876 | -0.010222 | -0.051264 | -0.10866 | 0.2101 | 0.10802 | -0.16808 | 123.3417 | 123.2325 | 123.3747 | 66.9219 | -123.4355 | 123.2747 | 123.3929 | 123.1168 | 66.9117 | -123.6037
220.2344 | 123.6145 | -66.8838 | 56.4056 | 0.049183 | -0.0062112 | 0.00029306 | 0.054464 | -0.001864 | 0.054706 | 0.066374 | -0.0020844 | -0.0015819 | 0.063837 | 0.019199 | 0.059511 | -66.9212 | 0.028878 | -66.9017 | 56.4487 | 56.3303 | 56.4771 | -67.0481 | -66.9488 | 0.023253 | -66.9971 | 56.3771 | 56.5091 | 56.2513 | -67.2072 | -0.16429 | 0.043069 | -0.037398 | -0.017816 | 0.14648 | -0.075351 | 0.071451 | -0.32334 | -0.028534 | -0.064998 | -0.11324 | 0.2101 | 0.10344 | -0.15434 | 123.3326 | 123.2141 | 123.3609 | 66.9127 | -123.4538 | 123.261 | 123.3929 | 123.1352 | 66.9071 | -123.6128
221.25 | 123.5458 | -66.8518 | 56.4651 | 0.049183 | -0.0094162 | -0.00077494 | 0.052327 | -0.002933 | 0.053638 | 0.051113 | -0.0010164 | -0.0026499 | 0.062769 | 0.020268 | 0.059511 | -66.9212 | 0.0243 | -66.9062 | 56.4396 | 56.3257 | 56.4817 | -67.0527 | -66.9443 | 0.027831 | -67.0017 | 56.3771 | 56.5045 | 56.2467 | -67.2118 | -0.20092 | -0.025596 | -0.069441 | -0.054438 | 0.14648 | -0.13944 | 0.016521 | -0.35996 | -0.088043 | -0.092462 | -0.14986 | 0.2101 | 0.039355 | -0.21842 | 123.2914 | 123.1775 | 123.3335 | 66.8761 | -123.5179 | 123.2289 | 123.3563 | 123.0985 | 66.8796 | -123.6769
222.25 | 123.6053 | -66.8564 | 56.4194 | 0.079707 | -0.0083482 | -0.0018439 | 0.054464 | -0.002933 | 0.053638 | 0.066374 | -0.0020844 | -0.0037179 | 0.0617 | 0.020268 | 0.058443 | -66.9167 | 0.019721 | -66.9062 | 56.4441 | 56.3303 | 56.4771 | -67.0573 | -66.9443 | 0.023253 | -67.0017 | 56.3817 | 56.4953 | 56.2193 | -67.2163 | -0.20092 | 0.024758 | -0.060285 | -0.049861 | 0.15106 | -0.089084 | 0.057718 | -0.35996 | -0.037688 | -0.087885 | -0.14528 | 0.21468 | 0.075974 | -0.20012 | 123.3005 | 123.1867 | 123.3335 | 66.8761 | -123.4767 | 123.2381 | 123.3517 | 123.0756 | 66.8796 | -123.6357
223.2344 | 123.6053 | -66.8976 | 56.4194 | 0.064445 | -0.0083482 | -0.00077494 | 0.053396 | -0.001864 | 0.052569 | 0.051113 | -0.0020844 | -0.0015819 | 0.060632 | 0.018131 | 0.061648 | -66.9167 | 0.033457 | -66.9017 | 56.4441 | 56.3303 | 56.4817 | -67.0481 | -66.9351 | 0.03241 | -66.9971 | 56.3817 | 56.4953 | 56.2696 | -67.2163 | -0.15056 | 0.024758 | -0.019086 | -0.004083 | 0.14648 | -0.089084 | 0.062297 | -0.31876 | -0.037688 | -0.037529 | -0.099506 | 0.21926 | 0.075974 | -0.14975 | 123.3417 | 123.2279 | 123.3793 | 66.931 | -123.4675 | 123.2793 | 123.3929 | 123.1672 | 66.93 | -123.6357
224.2344 | 123.6511 | -66.8884 | 56.4377 | 0.049183 | -0.0094162 | 0.00029306 | 0.052327 | -0.002933 | 0.052569 | 0.081635 | -0.0020844 | -0.0015819 | 0.060632 | 0.019199 | 0.059511 | -66.9212 | 0.028878 | -66.9017 | 56.4441 | 56.3349 | 56.4908 | -67.0298 | -66.9443 | 0.023253 | -66.9971 | 56.3771 | 56.5045 | 56.2147 | -67.2163 | -0.1414 | 0.006448 | -0.03282 | -0.013238 | 0.12816 | -0.10281 | 0.053144 | -0.32792 | -0.060577 | -0.055841 | -0.10866 | 0.21926 | 0.066821 | -0.22301 | 123.3326 | 123.2233 | 123.3793 | 66.9173 | -123.4675 | 123.2655 | 123.3929 | 123.1031 | 66.9117 | -123.654
225.2344 | 123.6145 | -66.9205 | 56.4011 | 0.064445 | -0.0094162 | -0.00077494 | 0.052327 | -0.004001 | 0.052569 | 0.051113 | -0.0010164 | -0.0015819 | 0.062769 | 0.020268 | 0.059511 | -66.9167 | 0.033457 | -66.9017 | 56.4441 | 56.3394 | 56.4817 | -67.0527 | -66.9488 | 0.03241 | -67.0017 | 56.3725 | 56.4999 | 56.2559 | -67.2118 | -0.13225 | 0.043069 | 0.003802 | 0.018805 | 0.15106 | -0.061615 | 0.080608 | -0.2913 | -0.028534 | -0.028377 | -0.081197 | 0.2101 | 0.098864 | -0.14518 | 123.3646 | 123.2599 | 123.4021 | 66.9539 | -123.4538 | 123.293 | 123.4204 | 123.1764 | 66.9529 | -123.6128
226.25 | 123.4955 | -66.9342 | 56.4606 | 0.064445 | -0.0083482 | -0.0018439 | 0.053396 | -0.001864 | 0.055774 | 0.081635 | -0.0020844 | -0.0026499 | 0.060632 | 0.019199 | 0.058443 | -66.9167 | 0.0243 | -66.9062 | 56.4441 | 56.3394 | 56.4908 | -67.0573 | -66.9488 | 0.023253 | -66.9971 | 56.3817 | 56.5045 | 56.233 | -67.2072 | -0.1231 | -0.01644 | 0.017535 | 0.027959 | 0.15106 | -0.12112 | 0.030256 | -0.27299 | -0.078886 | -0.014644 | -0.062885 | 0.2101 | 0.043933 | -0.22758 | 123.3783 | 123.2737 | 123.425 | 66.9585 | -123.5179 | 123.3159 | 123.4387 | 123.1672 | 66.9575 | -123.6678
227.25 | 123.5596 | -66.8976 | 56.4102 | 0.079707 | -0.0083482 | 0.00029306 | 0.055533 | -0.004001 | 0.054706 | 0.096896 | -0.0010164 | -0.0026499 | 0.062769 | 0.022405 | 0.06058 | -66.9212 | 0.0243 | -66.9017 | 56.4441 | 56.3349 | 56.4862 | -67.0573 | -66.9397 | 0.018674 | -67.0017 | 56.3771 | 56.5045 | 56.265 | -67.2118 | -0.15972 | 0.033914 | -0.023665 | -0.004083 | 0.15564 | -0.075349 | 0.076032 | -0.31419 | -0.033111 | -0.042107 | -0.10408 | 0.2101 | 0.094287 | -0.14518 | 123.3417 | 123.2325 | 123.3838 | 66.9219 | -123.4675 | 123.2747 | 123.4021 | 123.1626 | 66.9163 | -123.622
228.2344 | 123.5687 | -66.9022 | 56.4148 | 0.049183 | -0.0072792 | 0.00029306 | 0.052327 | -0.002933 | 0.053638 | 0.066374 | -0.0020844 | -0.0015819 | 0.060632 | 0.020268 | 0.059511 | -66.9167 | 0.028878 | -66.9062 | 56.4487 | 56.3349 | 56.4817 | -67.0481 | -66.9443 | 0.023253 | -67.0062 | 56.3817 | 56.5091 | 56.2559 | -67.2118 | -0.14598 | 0.033914 | -0.014508 | -0.004084 | 0.1419 | -0.079927 | 0.066875 | -0.30961 | -0.03311 | -0.042108 | -0.10409 | 0.20552 | 0.094288 | -0.15891 | 123.3509 | 123.237 | 123.3838 | 66.931 | -123.4629 | 123.2838 | 123.4112 | 123.158 | 66.9254 | -123.6266
229.2344 | 123.587 | -66.8793 | 56.4148 | 0.049183 | -0.0094162 | -0.0018439 | 0.051259 | -0.002933 | 0.052569 | 0.066374 | -0.0042204 | -0.00051292 | 0.060632 | 0.020268 | 0.06058 | -66.9212 | 0.028878 | -66.9108 | 56.4441 | 56.3303 | 56.4817 | -67.0161 | -66.9443 | 0.018674 | -67.0017 | 56.3771 | 56.4999 | 56.2284 | -67.2118 | -0.13682 | 0.029336 | -0.041976 | -0.031551 | 0.10527 | -0.084506 | 0.066875 | -0.3325 | -0.037689 | -0.064997 | -0.1224 | 0.2101 | 0.085131 | -0.18638 | 123.3234 | 123.2096 | 123.3609 | 66.9082 | -123.4309 | 123.2564 | 123.3792 | 123.1077 | 66.8979 | -123.6266
230.2344 | 123.5779 | -66.893 | 56.4239 | 0.049183 | -0.0072792 | 0.00029306 | 0.053396 | -0.001864 | 0.052569 | 0.051113 | -0.0020844 | -0.0026499 | 0.059564 | 0.021336 | 0.059511 | -66.9167 | 0.028878 | -66.8971 | 56.4441 | 56.3303 | 56.4817 | -67.0527 | -66.9397 | 0.023253 | -67.0017 | 56.3771 | 56.5091 | 56.2467 | -67.2163 | -0.15972 | 0.020181 | -0.023664 | -0.004083 | 0.15564 | -0.093661 | 0.05772 | -0.32334 | -0.046844 | -0.046685 | -0.10866 | 0.21468 | 0.085133 | -0.17722 | 123.3371 | 123.2233 | 123.3747 | 66.9219 | -123.4767 | 123.2701 | 123.4021 | 123.1397 | 66.9163 | -123.6403
231.2344 | 123.6145 | -66.9022 | 56.4239 | 0.049183 | -0.0072792 | -0.00077494 | 0.052327 | -0.005069 | 0.053638 | 0.066374 | -0.0010164 | -0.0026499 | 0.0617 | 0.022405 | 0.06058 | -66.9212 | 0.028878 | -66.9062 | 56.4441 | 56.3257 | 56.4817 | -67.0527 | -66.9397 | 0.023253 | -67.0017 | 56.3771 | 56.5045 | 56.2101 | -67.2118 | -0.15056 | 0.020181 | -0.019087 | -0.004084 | 0.14648 | -0.09824 | 0.05772 | -0.30961 | -0.046844 | -0.037529 | -0.099507 | 0.2101 | 0.080554 | -0.21385 | 123.3463 | 123.2279 | 123.3838 | 66.931 | -123.4767 | 123.2793 | 123.4067 | 123.1123 | 66.9254 | -123.6357
232.25 | 123.6511 | -66.8838 | 56.4239 | 0.049183 | -0.0072792 | -0.0018439 | 0.053396 | -0.004001 | 0.053638 | 0.066374 | -0.0020844 | -0.0015819 | 0.0617 | 0.020268 | 0.059511 | -66.9212 | 0.028878 | -66.8971 | 56.4441 | 56.344 | 56.4862 | -67.0527 | -66.9397 | 0.027831 | -66.9971 | 56.3771 | 56.5045 | 56.2971 | -67.2072 | -0.16887 | 0.020181 | -0.037398 | -0.013238 | 0.15564 | -0.079925 | 0.062299 | -0.32334 | -0.046844 | -0.05584 | -0.11324 | 0.2101 | 0.080554 | -0.12686 | 123.328 | 123.2279 | 123.3701 | 66.9127 | -123.4767 | 123.261 | 123.3884 | 123.1809 | 66.9117 | -123.6311
233.2344 | 123.5733 | -66.893 | 56.4148 | 0.064445 | -0.0083482 | -0.0018439 | 0.052327 | -0.001864 | 0.054706 | 0.051113 | -0.0010164 | -0.00051292 | 0.060632 | 0.020268 | 0.06058 | -66.9167 | 0.0243 | -66.9017 | 56.4487 | 56.3394 | 56.4908 | -67.0436 | -66.9397 | 0.027831 | -67.0017 | 56.3771 | 56.4999 | 56.2605 | -67.2209 | -0.15056 | 0.033914 | -0.023664 | -0.008661 | 0.1419 | -0.075348 | 0.076032 | -0.32792 | -0.037689 | -0.046685 | -0.10866 | 0.21926 | 0.085131 | -0.15433 | 123.3417 | 123.2325 | 123.3838 | 66.9173 | -123.4584 | 123.2701 | 123.3929 | 123.1535 | 66.9208 | -123.6357
234.2344 | 123.587 | -66.9022 | 56.4056 | 0.064445 | -0.0083482 | -0.0018439 | 0.053396 | -0.002933 | 0.053638 | 0.051113 | -0.0031524 | 0.00055508 | 0.0617 | 0.019199 | 0.058443 | -66.9167 | 0.0243 | -66.9017 | 56.4533 | 56.344 | 56.4954 | -67.0481 | -66.9397 | 0.023253 | -66.9925 | 56.3863 | 56.4999 | 56.3108 | -67.2118 | -0.14598 | 0.047648 | -0.014508 | 0.000495 | 0.14648 | -0.061615 | 0.089766 | -0.30961 | -0.019377 | -0.037529 | -0.090349 | 0.21926 | 0.094286 | -0.094814 | 123.3554 | 123.2462 | 123.3976 | 66.9265 | -123.4538 | 123.2884 | 123.4021 | 123.213 | 66.9254 | -123.6174
235.2344 | 123.5779 | -66.9067 | 56.4239 | 0.049183 | -0.0083482 | -0.00077494 | 0.052327 | -0.001864 | 0.055774 | 0.035852 | -0.0010164 | -0.0026499 | 0.0617 | 0.021336 | 0.059511 | -66.9121 | 0.019721 | -66.9062 | 56.4441 | 56.3349 | 56.4862 | -67.0527 | -66.9488 | 0.018674 | -67.0017 | 56.3725 | 56.5091 | 56.265 | -67.2118 | -0.14598 | 0.020181 | -0.005353 | 0.000493 | 0.14648 | -0.089082 | 0.062299 | -0.30503 | -0.051422 | -0.04211 | -0.09493 | 0.2101 | 0.085133 | -0.15891 | 123.3509 | 123.2416 | 123.393 | 66.9265 | -123.4767 | 123.2793 | 123.4158 | 123.1718 | 66.9254 | -123.6357
236.2344 | 123.5321 | -66.9022 | 56.456 | 0.033921 | -0.0072792 | -0.00077494 | 0.051259 | -0.001864 | 0.054706 | 0.066374 | -0.0020844 | 0.00055508 | 0.060632 | 0.021336 | 0.058443 | -66.9167 | 0.0243 | -66.9017 | 56.435 | 56.3394 | 56.4908 | -67.0481 | -66.9443 | 0.027831 | -66.9971 | 56.3771 | 56.5045 | 56.265 | -67.2118 | -0.14598 | -0.02102 | -0.014508 | 0.000495 | 0.14648 | -0.11655 | 0.034833 | -0.30961 | -0.078888 | -0.042108 | -0.094928 | 0.21468 | 0.04851 | -0.19095 | 123.3371 | 123.2416 | 123.393 | 66.9265 | -123.5041 | 123.2793 | 123.4067 | 123.1672 | 66.93 | -123.6678
237.2344 | 123.7381 | -66.8701 | 56.4331 | 0.064445 | -0.0062112 | -0.00077494 | 0.053396 | -0.002933 | 0.053638 | 0.051113 | -0.0020844 | -0.0015819 | 0.0617 | 0.021336 | 0.059511 | -66.9258 | 0.0243 | -66.9017 | 56.4533 | 56.3303 | 56.4862 | -67.0573 | -66.9488 | 0.023253 | -67.0017 | 56.3817 | 56.4999 | 56.233 | -67.2163 | -0.18719 | 0.020183 | -0.055709 | -0.031549 | 0.15564 | -0.10282 | 0.053144 | -0.34623 | -0.05142 | -0.078731 | -0.13155 | 0.21468 | 0.066821 | -0.20011 | 123.3234 | 123.2004 | 123.3564 | 66.8944 | -123.4904 | 123.2518 | 123.37 | 123.1031 | 66.8934 | -123.6495
238.2344 | 123.6053 | -66.893 | 56.4102 | 0.049183 | -0.0083482 | -0.0018439 | 0.054464 | -0.002933 | 0.053638 | 0.051113 | -0.0031524 | -0.00051292 | 0.060632 | 0.021336 | 0.059511 | -66.9212 | 0.028878 | -66.9062 | 56.4441 | 56.3394 | 56.4862 | -67.0527 | -66.9443 | 0.014095 | -67.0017 | 56.3817 | 56.4999 | 56.3154 | -67.2163 | -0.15972 | 0.033914 | -0.028243 | -0.01324 | 0.14648 | -0.07077 | 0.076032 | -0.32334 | -0.028532 | -0.051264 | -0.10866 | 0.21468 | 0.089709 | -0.094813 | 123.3371 | 123.2325 | 123.3793 | 66.9219 | -123.4629 | 123.2747 | 123.3929 | 123.2084 | 66.9071 | -123.6266
239.2344 | 123.5733 | -66.8701 | 56.4331 | 0.033921 | -0.0072792 | -0.00077494 | 0.051259 | -0.002933 | 0.053638 | 0.066374 | -0.0020844 | -0.0015819 | 0.060632 | 0.020268 | 0.059511 | -66.9075 | 0.028878 | -66.9062 | 56.4487 | 56.344 | 56.4908 | -67.0527 | -66.9443 | 0.023253 | -66.9971 | 56.3817 | 56.4953 | 56.32 | -67.2163 | -0.18261 | 0.015604 | -0.037396 | -0.036128 | 0.14648 | -0.08908 | 0.057722 | -0.34623 | -0.05142 | -0.074152 | -0.12697 | 0.21926 | 0.062242 | -0.11312 | 123.3188 | 123.2141 | 123.3609 | 66.899 | -123.4858 | 123.2518 | 123.3655 | 123.1901 | 66.8934 | -123.6495
240.2344 | 123.5825 | -66.9067 | 56.4514 | 0.064445 | -0.0072792 | -0.0018439 | 0.052327 | -0.002933 | 0.054706 | 0.081635 | -0.0031524 | -0.00051292 | 0.062769 | 0.019199 | 0.06058 | -66.9212 | 0.028878 | -66.9108 | 56.4441 | 56.3349 | 56.4817 | -67.0573 | -66.9443 | 0.023253 | -66.9971 | 56.3771 | 56.4953 | 56.3108 | -67.2118 | -0.15056 | -0.007285 | -0.01451 | -0.004085 | 0.14648 | -0.11655 | 0.030254 | -0.30503 | -0.07431 | -0.037531 | -0.090351 | 0.21468 | 0.043931 | -0.14059 | 123.3509 | 123.2416 | 123.3884 | 66.9356 | -123.5087 | 123.2838 | 123.4021 | 123.2176 | 66.93 | -123.6632
241.2344 | 123.5641 | -66.9022 | 56.4331 | 0.079707 | -0.0094162 | 0.00029306 | 0.052327 | -0.001864 | 0.053638 | 0.066374 | -0.0020844 | -0.0015819 | 0.059564 | 0.022405 | 0.057375 | -66.9167 | 0.0243 | -66.9017 | 56.4441 | 56.3211 | 56.4862 | -67.0573 | -66.9397 | 0.023253 | -66.9971 | 56.3771 | 56.5045 | 56.265 | -67.2163 | -0.15514 | 0.011026 | -0.014508 | 0.000495 | 0.15564 | -0.11197 | 0.053144 | -0.31419 | -0.055999 | -0.037529 | -0.094928 | 0.21926 | 0.071399 | -0.16806 | 123.3463 | 123.2233 | 123.3884 | 66.9265 | -123.4904 | 123.2793 | 123.4067 | 123.1672 | 66.9254 | -123.6495
242.25 | 123.6008 | -66.8884 | 56.4194 | 0.064445 | -0.0083482 | -0.0018439 | 0.053396 | -0.00079597 | 0.054706 | 0.066374 | -0.0010164 | 0.00055508 | 0.0617 | 0.021336 | 0.06058 | -66.9167 | 0.019721 | -66.9017 | 56.4441 | 56.3349 | 56.4862 | -67.0481 | -66.9443 | 0.027831 | -66.9971 | 56.3817 | 56.4999 | 56.2742 | -67.2118 | -0.15972 | 0.024758 | -0.028241 | -0.013238 | 0.14648 | -0.084505 | 0.066876 | -0.32334 | -0.037688 | -0.055841 | -0.10866 | 0.21468 | 0.080553 | -0.14518 | 123.3326 | 123.2233 | 123.3747 | 66.9081 | -123.4675 | 123.2701 | 123.3884 | 123.1626 | 66.9163 | -123.6311
243.2344 | 123.5367 | -66.9113 | 56.4148 | 0.064445 | -0.0062112 | -0.00077494 | 0.053396 | -0.004001 | 0.053638 | 0.035852 | -0.0020844 | -0.0015819 | 0.0617 | 0.021336 | 0.058443 | -66.9167 | 0.028878 | -66.9062 | 56.4487 | 56.3394 | 56.4817 | -67.0527 | -66.9488 | 0.023253 | -66.9971 | 56.3817 | 56.4999 | 56.2238 | -67.2163 | -0.14141 | 0.033914 | -0.005353 | 0.005071 | 0.14648 | -0.075348 | 0.066875 | -0.30503 | -0.03311 | -0.037532 | -0.085773 | 0.21926 | 0.085131 | -0.19096 | 123.36 | 123.2508 | 123.393 | 66.9402 | -123.4675 | 123.293 | 123.4112 | 123.1351 | 66.9346 | -123.6311
244.2344 | 123.5413 | -66.8838 | 56.4102 | 0.079707 | -0.010484 | -0.00077494 | 0.054464 | -0.001864 | 0.053638 | 0.066374 | -0.0031524 | -0.00051292 | 0.0617 | 0.021336 | 0.059511 | -66.9167 | 0.019721 | -66.8971 | 56.4487 | 56.3303 | 56.4908 | -67.0573 | -66.9351 | 0.027831 | -67.0017 | 56.3817 | 56.4953 | 56.2605 | -67.2118 | -0.17345 | 0.038492 | -0.032819 | -0.013238 | 0.16021 | -0.079928 | 0.08061 | -0.32792 | -0.028532 | -0.051262 | -0.11782 | 0.2101 | 0.08513 | -0.14976 | 123.3326 | 123.2141 | 123.3747 | 66.9036 | -123.4675 | 123.2655 | 123.3792 | 123.1443 | 66.9117 | -123.622
245.2344 | 123.5779 | -66.8884 | 56.4011 | 0.064445 | -0.010484 | 0.00029306 | 0.054464 | -0.002933 | 0.052569 | 0.096896 | -0.0020844 | -0.0026499 | 0.060632 | 0.021336 | 0.059511 | -66.9212 | 0.028878 | -66.9017 | 56.4441 | 56.3394 | 56.5 | -67.0481 | -66.9397 | 0.018674 | -66.9925 | 56.3771 | 56.4953 | 56.2742 | -67.2118 | -0.15972 | 0.043069 | -0.03282 | -0.013238 | 0.14648 | -0.061615 | 0.098922 | -0.32334 | -0.023956 | -0.051262 | -0.10408 | 0.21926 | 0.094285 | -0.12687 | 123.3326 | 123.2279 | 123.3884 | 66.9173 | -123.4492 | 123.2655 | 123.3838 | 123.1626 | 66.9071 | -123.6128
246.2344 | 123.5641 | -66.8747 | 56.4148 | 0.064445 | -0.0083482 | -0.0018439 | 0.052327 | -0.002933 | 0.053638 | 0.066374 | -0.0031524 | -0.0026499 | 0.0617 | 0.023473 | 0.059511 | -66.9167 | 0.033457 | -66.9062 | 56.4396 | 56.3257 | 56.4862 | -67.0481 | -66.9397 | 0.023253 | -66.9971 | 56.3771 | 56.4953 | 56.2742 | -67.2163 | -0.17345 | 0.024758 | -0.041974 | -0.03155 | 0.1419 | -0.089085 | 0.071454 | -0.34165 | -0.037689 | -0.064995 | -0.12239 | 0.21926 | 0.080552 | -0.1406 | 123.3142 | 123.2004 | 123.3609 | 66.9082 | -123.4629 | 123.2518 | 123.37 | 123.1489 | 66.8979 | -123.6311
247.25 | 123.6099 | -66.9067 | 56.4331 | 0.079707 | -0.0094162 | -0.0018439 | 0.053396 | -0.004001 | 0.054706 | 0.066374 | 0.0011206 | -0.0026499 | 0.060632 | 0.022405 | 0.059511 | -66.9121 | 0.028878 | -66.8971 | 56.4396 | 56.3303 | 56.4817 | -67.0527 | -66.9488 | 0.018674 | -67.0017 | 56.3817 | 56.4953 | 56.2834 | -67.2072 | -0.14598 | 0.006448 | -0.005353 | 0.00965 | 0.15564 | -0.10282 | 0.048565 | -0.30045 | -0.05142 | -0.04211 | -0.09493 | 0.20552 | 0.062242 | -0.14975 | 123.3463 | 123.237 | 123.3884 | 66.9356 | -123.4858 | 123.2884 | 123.4021 | 123.1901 | 66.9254 | -123.6403
248.2344 | 123.5641 | -66.8884 | 56.4102 | 0.064445 | -0.0094162 | -0.00077494 | 0.052327 | -0.002933 | 0.052569 | 0.066374 | -0.0042204 | -0.00051292 | 0.0617 | 0.023473 | 0.06058 | -66.9167 | 0.0243 | -66.9017 | 56.4487 | 56.3303 | 56.4817 | -67.039 | -66.9351 | 0.023253 | -67.0017 | 56.3863 | 56.4999 | 56.2055 | -67.2118 | -0.15056 | 0.038492 | -0.028241 | -0.013238 | 0.13732 | -0.079928 | 0.071453 | -0.32334 | -0.023954 | -0.046684 | -0.11324 | 0.2101 | 0.089709 | -0.2047 | 123.3371 | 123.2187 | 123.3701 | 66.9127 | -123.4492 | 123.2747 | 123.3884 | 123.0939 | 66.9117 | -123.622
249.2344 | 123.5733 | -66.8976 | 56.4102 | 0.079707 | -0.010484 | -0.00077494 | 0.054464 | -0.002933 | 0.052569 | 0.051113 | -0.0020844 | -0.0015819 | 0.062769 | 0.024541 | 0.059511 | -66.9167 | 0.033457 | -66.9017 | 56.4487 | 56.3349 | 56.4862 | -67.039 | -66.9397 | 0.023253 | -67.0017 | 56.3725 | 56.4999 | 56.2193 | -67.2118 | -0.1414 | 0.038492 | -0.019086 | -0.004083 | 0.13732 | -0.075349 | 0.076032 | -0.31419 | -0.037689 | -0.042107 | -0.10408 | 0.2101 | 0.089709 | -0.19096 | 123.3463 | 123.2325 | 123.3838 | 66.931 | -123.4492 | 123.2701 | 123.3975 | 123.1168 | 66.9208 | -123.622
250.2344 | 123.5504 | -66.8884 | 56.4102 | 0.064445 | -0.010484 | -0.00077494 | 0.052327 | -0.004001 | 0.054706 | 0.066374 | -0.0020844 | -0.0026499 | 0.0617 | 0.023473 | 0.059511 | -66.9167 | 0.0243 | -66.9108 | 56.4441 | 56.3257 | 56.4817 | -67.0527 | -66.9397 | 0.018674 | -67.0017 | 56.3771 | 56.5091 | 56.2376 | -67.2118 | -0.16429 | 0.033914 | -0.028241 | -0.022395 | 0.1419 | -0.084507 | 0.071453 | -0.32334 | -0.033111 | -0.051262 | -0.11324 | 0.2101 | 0.098866 | -0.17265 | 123.3326 | 123.2141 | 123.3701 | 66.9127 | -123.4629 | 123.2655 | 123.3975 | 123.126 | 66.9071 | -123.622
251.2344 | 123.587 | -66.8976 | 56.4194 | 0.064445 | -0.010484 | -0.00077494 | 0.053396 | -0.004001 | 0.052569 | 0.051113 | 5.2637e-05 | -0.0015819 | 0.0617 | 0.022405 | 0.058443 | -66.9121 | 0.0243 | -66.9062 | 56.4441 | 56.344 | 56.4908 | -67.0436 | -66.9397 | 0.018674 | -67.0017 | 56.3863 | 56.5045 | 56.2238 | -67.2163 | -0.14598 | 0.024758 | -0.014508 | -0.008662 | 0.13732 | -0.075348 | 0.071454 | -0.31876 | -0.03311 | -0.042107 | -0.10408 | 0.21468 | 0.085131 | -0.19554 | 123.3417 | 123.2416 | 123.3884 | 66.9219 | -123.4629 | 123.2838 | 123.4021 | 123.1214 | 66.9163 | -123.6357
252.2344 | 123.6465 | -66.9022 | 56.4056 | 0.079707 | -0.0083482 | 0.00029306 | 0.053396 | -0.004001 | 0.054706 | 0.066374 | -0.0031524 | -0.0015819 | 0.060632 | 0.022405 | 0.059511 | -66.9167 | 0.028878 | -66.8925 | 56.4396 | 56.3349 | 56.4862 | -67.0573 | -66.9397 | 0.023253 | -67.0017 | 56.3771 | 56.5091 | 56.3108 | -67.2118 | -0.15514 | 0.033913 | -0.014508 | 0.009651 | 0.16479 | -0.070772 | 0.080609 | -0.30961 | -0.028534 | -0.037529 | -0.099507 | 0.2101 | 0.10344 | -0.094814 | 123.3417 | 123.237 | 123.3884 | 66.931 | -123.4629 | 123.2793 | 123.4112 | 123.213 | 66.9254 | -123.6174
253.2344 | 123.587 | -66.893 | 56.4148 | 0.064445 | -0.0072792 | 0.00029306 | 0.053396 | -0.004001 | 0.053638 | 0.066374 | -0.0031524 | -0.0015819 | 0.062769 | 0.022405 | 0.061648 | -66.9121 | 0.0243 | -66.8971 | 56.4441 | 56.3303 | 56.4908 | -67.0573 | -66.9397 | 0.018674 | -67.0017 | 56.3817 | 56.4953 | 56.2696 | -67.2118 | -0.1643 | 0.029336 | -0.019086 | -0.004083 | 0.16021 | -0.084506 | 0.076032 | -0.31876 | -0.03311 | -0.046685 | -0.10866 | 0.2101 | 0.080552 | -0.14518 | 123.3371 | 123.2233 | 123.3838 | 66.9173 | -123.4721 | 123.2747 | 123.3884 | 123.1626 | 66.9117 | -123.6266
254.2344 | 123.5825 | -66.9022 | 56.4377 | 0.033921 | -0.0083482 | 0.00029306 | 0.053396 | -0.004001 | 0.053638 | 0.051113 | 5.2637e-05 | -0.00051292 | 0.0617 | 0.022405 | 0.06058 | -66.9167 | 0.0243 | -66.8971 | 56.4441 | 56.3303 | 56.4771 | -67.039 | -66.9397 | 0.023253 | -66.9971 | 56.3771 | 56.5045 | 56.2193 | -67.2118 | -0.13683 | 0.006448 | -0.014508 | 0.005073 | 0.1419 | -0.10739 | 0.039408 | -0.30961 | -0.060577 | -0.037529 | -0.094928 | 0.21468 | 0.066821 | -0.21843 | 123.3463 | 123.2325 | 123.3793 | 66.9265 | -123.4767 | 123.2793 | 123.4067 | 123.1214 | 66.9254 | -123.6495
255.2344 | 123.5687 | -66.8976 | 56.4331 | 0.049183 | -0.0083482 | 0.00029306 | 0.051259 | -0.002933 | 0.053638 | 0.081635 | -0.0020844 | -0.00051292 | 0.0617 | 0.023473 | 0.06058 | -66.9167 | 0.028878 | -66.8971 | 56.4396 | 56.3303 | 56.4817 | -67.0344 | -66.9443 | 0.023253 | -66.9971 | 56.3771 | 56.4999 | 56.2467 | -67.2118 | -0.13683 | 0.006448 | -0.019086 | 0.000495 | 0.13732 | -0.10282 | 0.048565 | -0.31419 | -0.055999 | -0.046686 | -0.099506 | 0.21468 | 0.066821 | -0.18638 | 123.3371 | 123.2279 | 123.3793 | 66.9265 | -123.4675 | 123.2747 | 123.3975 | 123.1443 | 66.9208 | -123.6449
256.2344 | 123.555 | -66.8701 | 56.4331 | 0.049183 | -0.0072792 | -0.0018439 | 0.051259 | -0.004001 | 0.052569 | 0.051113 | -0.0020844 | -0.0015819 | 0.060632 | 0.024541 | 0.058443 | -66.9167 | 0.019721 | -66.9017 | 56.4441 | 56.3349 | 56.4908 | -67.0481 | -66.9443 | 0.023253 | -67.0017 | 56.3817 | 56.4999 | 56.265 | -67.2163 | -0.17803 | 0.011026 | -0.046552 | -0.031549 | 0.14648 | -0.098237 | 0.057722 | -0.34623 | -0.05142 | -0.074152 | -0.13155 | 0.21468 | 0.066821 | -0.16806 | 123.3142 | 123.205 | 123.3609 | 66.8898 | -123.4812 | 123.2518 | 123.37 | 123.1352 | 66.8934 | -123.6495
257.25 | 123.6465 | -66.8655 | 56.4423 | 0.064445 | -0.0083482 | -0.00077494 | 0.053396 | -0.002933 | 0.054706 | 0.066374 | -0.0020844 | -0.0037179 | 0.0617 | 0.022405 | 0.059511 | -66.9167 | 0.019721 | -66.9062 | 56.4441 | 56.3303 | 56.4862 | -67.0527 | -66.9443 | 0.014095 | -67.0108 | 56.3817 | 56.5045 | 56.2696 | -67.2209 | -0.18718 | 0.00187 | -0.051129 | -0.040705 | 0.14648 | -0.11197 | 0.043988 | -0.35539 | -0.060576 | -0.078729 | -0.14529 | 0.2101 | 0.062243 | -0.17264 | 123.3097 | 123.1958 | 123.3518 | 66.8853 | -123.495 | 123.2472 | 123.37 | 123.1352 | 66.8796 | -123.6632
258.2344 | 123.5687 | -66.9205 | 56.4331 | 0.064445 | -0.0094162 | -0.00077494 | 0.053396 | -0.001864 | 0.053638 | 0.051113 | -0.0020844 | -0.0015819 | 0.0617 | 0.024541 | 0.059511 | -66.9121 | 0.028878 | -66.9017 | 56.4533 | 56.3349 | 56.4862 | -67.0481 | -66.9443 | 0.023253 | -67.0017 | 56.3908 | 56.5091 | 56.2467 | -67.2209 | -0.12767 | 0.020183 | 0.00838 | 0.018805 | 0.14648 | -0.098237 | 0.053144 | -0.30046 | -0.042263 | -0.023798 | -0.081197 | 0.21926 | 0.075978 | -0.18638 | 123.3738 | 123.2553 | 123.4067 | 66.9493 | -123.4812 | 123.3113 | 123.4296 | 123.1672 | 66.9437 | -123.654
259.2344 | 123.5962 | -66.9022 | 56.4102 | 0.049183 | -0.0094162 | -0.00077494 | 0.052327 | -0.004001 | 0.052569 | 0.051113 | -0.0020844 | -0.0037179 | 0.060632 | 0.024541 | 0.058443 | -66.9167 | 0.033457 | -66.9017 | 56.4441 | 56.3303 | 56.4908 | -67.0252 | -66.9351 | 0.036989 | -67.0017 | 56.3725 | 56.4999 | 56.2009 | -67.2209 | -0.12309 | 0.033914 | -0.014508 | 0.000495 | 0.12358 | -0.079928 | 0.08061 | -0.31877 | -0.037689 | -0.032951 | -0.099507 | 0.21926 | 0.089709 | -0.20928 | 123.3463 | 123.2325 | 123.393 | 66.9356 | -123.4355 | 123.2747 | 123.4021 | 123.1031 | 66.9392 | -123.6311
260.2344 | 123.5687 | -66.9067 | 56.4331 | 0.049183 | -0.011553 | 0.00029306 | 0.052327 | -0.004001 | 0.053638 | 0.066374 | -0.0031524 | -0.0026499 | 0.0617 | 0.024541 | 0.059511 | -66.9075 | 0.028878 | -66.9017 | 56.4396 | 56.3303 | 56.4908 | -67.0573 | -66.9397 | 0.023253 | -66.9925 | 56.3634 | 56.4953 | 56.233 | -67.2118 | -0.15056 | 0.006448 | -0.000775 | 0.005072 | 0.15564 | -0.10282 | 0.057722 | -0.30503 | -0.069734 | -0.032952 | -0.085772 | 0.21926 | 0.062242 | -0.20011 | 123.3463 | 123.237 | 123.3976 | 66.9356 | -123.4904 | 123.2701 | 123.4021 | 123.1397 | 66.93 | -123.6449
261.2344 | 123.5687 | -66.8884 | 56.4468 | 0.094969 | -0.010484 | -0.00077494 | 0.052327 | -0.004001 | 0.054706 | 0.066374 | -0.0031524 | -0.0026499 | 0.0617 | 0.023473 | 0.057375 | -66.9212 | 0.028878 | -66.9017 | 56.4533 | 56.3394 | 56.4908 | -67.0436 | -66.9397 | 0.023253 | -66.9925 | 56.3725 | 56.4953 | 56.233 | -67.2163 | -0.15514 | 0.00645 | -0.03282 | -0.013238 | 0.1419 | -0.10739 | 0.043989 | -0.32792 | -0.07431 | -0.051262 | -0.10408 | 0.22384 | 0.048509 | -0.21385 | 123.3417 | 123.2279 | 123.3793 | 66.9173 | -123.4904 | 123.261 | 123.3838 | 123.1214 | 66.9117 | -123.6632
262.25 | 123.6374 | -66.861 | 56.4423 | 0.094969 | -0.0083482 | -0.00077494 | 0.051259 | -0.005069 | 0.053638 | 0.081635 | -0.0020844 | -0.0026499 | 0.060632 | 0.022405 | 0.06058 | -66.9075 | 0.0243 | -66.9062 | 56.4487 | 56.3303 | 56.4908 | -67.0527 | -66.9488 | 0.027831 | -66.9971 | 56.3771 | 56.4908 | 56.2559 | -67.2072 | -0.19176 | 0.006448 | -0.046551 | -0.045283 | 0.14648 | -0.11197 | 0.048566 | -0.34623 | -0.065155 | -0.087886 | -0.13613 | 0.2101 | 0.048508 | -0.18638 | 123.3097 | 123.1913 | 123.3518 | 66.8853 | -123.495 | 123.2381 | 123.3517 | 123.1168 | 66.8888 | -123.6495
263.2344 | 123.5825 | -66.8793 | 56.4423 | 0.049183 | -0.0083482 | 0.00029306 | 0.054464 | -0.004001 | 0.052569 | 0.051113 | -0.0020844 | -0.0015819 | 0.060632 | 0.021336 | 0.061648 | -66.9121 | 0.019721 | -66.9017 | 56.435 | 56.3303 | 56.4908 | -67.0527 | -66.9443 | 0.018674 | -66.9971 | 56.3863 | 56.5045 | 56.2055 | -67.2118 | -0.17345 | -0.007287 | -0.032819 | -0.022394 | 0.15106 | -0.11197 | 0.048566 | -0.3325 | -0.055998 | -0.064997 | -0.11782 | 0.21468 | 0.062243 | -0.23674 | 123.3142 | 123.2096 | 123.3701 | 66.899 | -123.495 | 123.2655 | 123.3838 | 123.0848 | 66.8979 | -123.654
264.2344 | 123.5916 | -66.893 | 56.4148 | 0.064445 | -0.010484 | -0.0018439 | 0.051259 | -0.001864 | 0.052569 | 0.051113 | -0.0020844 | -0.0026499 | 0.0617 | 0.024541 | 0.059511 | -66.9167 | 0.0243 | -66.9017 | 56.435 | 56.3349 | 56.4817 | -67.039 | -66.9443 | 0.018674 | -67.0062 | 56.3908 | 56.4999 | 56.2284 | -67.2118 | -0.14598 | 0.020179 | -0.023664 | -0.008661 | 0.13732 | -0.079927 | 0.066875 | -0.31876 | -0.023953 | -0.051264 | -0.11324 | 0.20552 | 0.085131 | -0.18638 | 123.328 | 123.2279 | 123.3747 | 66.9173 | -123.4538 | 123.2838 | 123.3929 | 123.1214 | 66.9117 | -123.6266
265.2344 | 123.5825 | -66.9067 | 56.4194 | 0.064445 | -0.010484 | -0.0039799 | 0.052327 | -0.005069 | 0.052569 | 0.051113 | -0.0010164 | -0.00051292 | 0.0617 | 0.023473 | 0.058443 | -66.9167 | 0.0243 | -66.9017 | 56.4487 | 56.3394 | 56.4908 | -67.0436 | -66.9443 | 0.027831 | -67.0017 | 56.3771 | 56.4953 | 56.265 | -67.2118 | -0.13683 | 0.029336 | -0.009931 | 0.005072 | 0.1419 | -0.079926 | 0.071454 | -0.30503 | -0.042267 | -0.037531 | -0.09493 | 0.2101 | 0.075974 | -0.15433 | 123.3554 | 123.2462 | 123.3976 | 66.931 | -123.4629 | 123.2838 | 123.4021 | 123.1718 | 66.9346 | -123.6311
266.2344 | 123.5733 | -66.8793 | 56.4102 | 0.064445 | -0.010484 | -0.00077494 | 0.052327 | -0.005069 | 0.052569 | 0.081635 | -0.0010164 | -0.00051292 | 0.059564 | 0.023473 | 0.058443 | -66.9075 | 0.028878 | -66.8971 | 56.4533 | 56.3394 | 56.4954 | -67.0481 | -66.9488 | 0.014095 | -66.9971 | 56.3771 | 56.4999 | 56.2834 | -67.2118 | -0.16887 | 0.043071 | -0.028241 | -0.017816 | 0.15106 | -0.07077 | 0.085189 | -0.3325 | -0.033111 | -0.069576 | -0.11782 | 0.21468 | 0.089709 | -0.12686 | 123.3326 | 123.2187 | 123.3747 | 66.9082 | -123.4584 | 123.2564 | 123.3792 | 123.1626 | 66.8934 | -123.622
267.25 | 123.5825 | -66.8793 | 56.4148 | 0.049183 | -0.0094162 | -0.00077494 | 0.053396 | -0.004001 | 0.051501 | 0.066374 | -0.0020844 | -0.0015819 | 0.0617 | 0.023473 | 0.058443 | -66.9121 | 0.0243 | -66.9017 | 56.4441 | 56.3211 | 56.4817 | -67.0481 | -66.9534 | 0.018674 | -66.9971 | 56.3817 | 56.4953 | 56.2421 | -67.2072 | -0.16887 | 0.029336 | -0.032819 | -0.022394 | 0.14648 | -0.093664 | 0.066875 | -0.32792 | -0.03311 | -0.074155 | -0.11782 | 0.2101 | 0.080552 | -0.17265 | 123.3234 | 123.2004 | 123.3609 | 66.9036 | -123.4629 | 123.261 | 123.3746 | 123.1214 | 66.8979 | -123.622
268.2344 | 123.555 | -66.9022 | 56.4148 | 0.049183 | -0.010484 | 0.00029306 | 0.052327 | -0.002933 | 0.052569 | 0.066374 | -0.0042204 | -0.0015819 | 0.058496 | 0.024541 | 0.059511 | -66.9121 | 0.0243 | -66.9062 | 56.4396 | 56.3486 | 56.4862 | -67.0481 | -66.9443 | 0.018674 | -67.0017 | 56.3771 | 56.4908 | 56.2513 | -67.2118 | -0.14598 | 0.024758 | -0.00993 | -0.004084 | 0.1419 | -0.066191 | 0.071454 | -0.30961 | -0.037689 | -0.042108 | -0.099507 | 0.2101 | 0.075974 | -0.16349 | 123.3417 | 123.2508 | 123.3884 | 66.9265 | -123.4629 | 123.2793 | 123.3929 | 123.1535 | 66.9208 | -123.6266
269.2344 | 123.5687 | -66.8976 | 56.4056 | 0.049183 | -0.0094162 | -0.00077494 | 0.053396 | -0.005069 | 0.053638 | 0.081635 | -0.0020844 | -0.0026499 | 0.0617 | 0.023473 | 0.057375 | -66.9121 | 0.019721 | -66.9062 | 56.4441 | 56.3303 | 56.4954 | -67.039 | -66.9443 | 0.018674 | -66.9971 | 56.3863 | 56.4999 | 56.2513 | -67.2118 | -0.1414 | 0.038491 | -0.014508 | -0.008662 | 0.13274 | -0.075351 | 0.089766 | -0.31419 | -0.019377 | -0.046686 | -0.099506 | 0.21468 | 0.094286 | -0.15434 | 123.3417 | 123.2279 | 123.393 | 66.9173 | -123.4446 | 123.2838 | 123.3975 | 123.1489 | 66.9163 | -123.6174
270.2344 | 123.5687 | -66.8976 | 56.4331 | 0.064445 | -0.0094162 | -0.00077494 | 0.052327 | -0.002933 | 0.052569 | 0.066374 | -0.0010164 | -0.0037179 | 0.060632 | 0.023473 | 0.06058 | -66.9075 | 0.028878 | -66.8971 | 56.4441 | 56.3349 | 56.4954 | -67.039 | -66.9351 | 0.023253 | -66.9925 | 56.3863 | 56.4999 | 56.233 | -67.2118 | -0.1414 | 0.011026 | -0.00993 | 0.000495 | 0.1419 | -0.098237 | 0.062301 | -0.31419 | -0.046842 | -0.037529 | -0.094927 | 0.21926 | 0.066821 | -0.20011 | 123.3417 | 123.2325 | 123.393 | 66.9265 | -123.4721 | 123.2838 | 123.3975 | 123.1306 | 66.9208 | -123.6449
271.2344 | 123.5733 | -66.9113 | 56.4148 | 0.079707 | -0.010484 | 0.00029306 | 0.052327 | -0.004001 | 0.053638 | 0.035852 | -0.0020844 | -0.0026499 | 0.060632 | 0.023473 | 0.06058 | -66.9304 | 0.019721 | -66.8971 | 56.4441 | 56.3257 | 56.4862 | -67.0344 | -66.9443 | 0.018674 | -66.9925 | 56.3771 | 56.4999 | 56.2925 | -67.2163 | -0.12309 | 0.029336 | -0.019089 | 0.014228 | 0.13732 | -0.089085 | 0.071454 | -0.30503 | -0.037689 | -0.032953 | -0.081194 | 0.22384 | 0.085131 | -0.12228 | 123.3554 | 123.237 | 123.3976 | 66.931 | -123.4492 | 123.2884 | 123.4112 | 123.2038 | 66.93 | -123.6311
272.25 | 123.6282 | -66.8747 | 56.4468 | 0.064445 | -0.010484 | -0.00077494 | 0.052327 | -0.004001 | 0.052569 | 0.081635 | -0.0020844 | -0.00051292 | 0.0617 | 0.023473 | 0.058443 | -66.9029 | 0.019721 | -66.9017 | 56.4441 | 56.3394 | 56.4908 | -67.0481 | -66.9443 | 0.014095 | -66.9971 | 56.3817 | 56.5045 | 56.2376 | -67.2163 | -0.17345 | -0.002707 | -0.028239 | -0.026971 | 0.14648 | -0.10739 | 0.043989 | -0.34165 | -0.065153 | -0.069574 | -0.12239 | 0.21926 | 0.057666 | -0.20927 | 123.3188 | 123.2141 | 123.3655 | 66.8944 | -123.495 | 123.2564 | 123.3792 | 123.1123 | 66.8888 | -123.6632
273.2344 | 123.6237 | -66.8976 | 56.4331 | 0.079707 | -0.0094162 | -0.0018439 | 0.052327 | -0.002933 | 0.053638 | 0.051113 | -0.0031524 | -0.0026499 | 0.0617 | 0.026678 | 0.058443 | -66.9167 | 0.0243 | -66.9108 | 56.4396 | 56.3394 | 56.4908 | -67.0207 | -66.9397 | 0.027831 | -66.9925 | 56.3863 | 56.4999 | 56.2101 | -67.2163 | -0.12309 | 0.006448 | -0.019086 | -0.01324 | 0.10985 | -0.093658 | 0.057722 | -0.31876 | -0.046842 | -0.042107 | -0.094927 | 0.22384 | 0.066821 | -0.22301 | 123.3371 | 123.237 | 123.3884 | 66.9219 | -123.4538 | 123.2838 | 123.3975 | 123.1077 | 66.9254 | -123.6495
274.2344 | 123.5733 | -66.8701 | 56.4377 | 0.049183 | -0.0094162 | -0.0018439 | 0.051259 | -0.00079597 | 0.053638 | 0.066374 | -0.0020844 | -0.0015819 | 0.060632 | 0.02561 | 0.056307 | -66.9167 | 0.019721 | -66.9017 | 56.4396 | 56.3394 | 56.4862 | -67.039 | -66.9397 | 0.018674 | -67.0062 | 56.3817 | 56.4999 | 56.2605 | -67.2163 | -0.16887 | 0.00187 | -0.046552 | -0.031549 | 0.13732 | -0.098236 | 0.048566 | -0.34623 | -0.055998 | -0.069573 | -0.13613 | 0.2101 | 0.062243 | -0.17722 | 123.3097 | 123.2096 | 123.3564 | 66.8898 | -123.4767 | 123.2518 | 123.37 | 123.1306 | 66.8888 | -123.654
275.2344 | 123.5733 | -66.8884 | 56.4285 | 0.064445 | -0.010484 | -0.0018439 | 0.052327 | -0.002933 | 0.051501 | 0.096896 | -0.0031524 | -0.0015819 | 0.059564 | 0.024541 | 0.06058 | -66.9075 | 0.0243 | -66.9062 | 56.4441 | 56.3394 | 56.4862 | -67.0527 | -66.9443 | 0.018674 | -67.0062 | 56.3863 | 56.4999 | 56.3017 | -67.2163 | -0.16429 | 0.015603 | -0.019085 | -0.017817 | 0.14648 | -0.089081 | 0.057721 | -0.32792 | -0.042265 | -0.055841 | -0.11782 | 0.2101 | 0.071398 | -0.12686 | 123.3326 | 123.2279 | 123.3747 | 66.9127 | -123.4813 | 123.2747 | 123.3884 | 123.1901 | 66.9071 | -123.6449
276.2344 | 123.555 | -66.8976 | 56.4377 | 0.064445 | -0.010484 | 0.00029306 | 0.050191 | -0.004001 | 0.052569 | 0.066374 | -0.0031524 | -0.0015819 | 0.060632 | 0.024541 | 0.058443 | -66.9212 | 0.028878 | -66.9108 | 56.4441 | 56.3394 | 56.4908 | -67.0436 | -66.9397 | 0.014095 | -66.9971 | 56.3771 | 56.5045 | 56.2742 | -67.2118 | -0.14598 | 0.006448 | -0.023665 | -0.01324 | 0.13274 | -0.098236 | 0.053144 | -0.31419 | -0.060577 | -0.042107 | -0.099506 | 0.21468 | 0.066821 | -0.16349 | 123.3417 | 123.237 | 123.3884 | 66.9265 | -123.4812 | 123.2747 | 123.4021 | 123.1718 | 66.9117 | -123.6495
277.2344 | 123.587 | -66.8655 | 56.4468 | 0.064445 | -0.010484 | 0.00029306 | 0.052327 | -0.004001 | 0.052569 | 0.051113 | -0.0031524 | -0.0015819 | 0.060632 | 0.026678 | 0.06058 | -66.9212 | 0.0243 | -66.9108 | 56.4487 | 56.344 | 56.4862 | -67.0527 | -66.9397 | 0.018674 | -67.0062 | 56.3863 | 56.5045 | 56.2513 | -67.2209 | -0.18718 | 0.001871 | -0.055708 | -0.045283 | 0.1419 | -0.10281 | 0.039411 | -0.35539 | -0.060575 | -0.07415 | -0.14071 | 0.21468 | 0.057666 | -0.19553 | 123.3142 | 123.2096 | 123.3518 | 66.8898 | -123.4996 | 123.2518 | 123.37 | 123.1168 | 66.8842 | -123.6678
278.25 | 123.6282 | -66.8564 | 56.4377 | 0.079707 | -0.010484 | 0.00029306 | 0.053396 | -0.004001 | 0.052569 | 0.081635 | -0.0010164 | -0.0015819 | 0.059564 | 0.027746 | 0.058443 | -66.9212 | 0.010564 | -66.9017 | 56.4487 | 56.3349 | 56.4954 | -67.0665 | -66.9443 | 0.018674 | -67.0017 | 56.3817 | 56.5091 | 56.2467 | -67.2163 | -0.21008 | 0.011026 | -0.064864 | -0.045282 | 0.16479 | -0.10281 | 0.057723 | -0.35996 | -0.055998 | -0.087885 | -0.14528 | 0.21468 | 0.0714 | -0.19096 | 123.3051 | 123.1913 | 123.3518 | 66.8669 | -123.5041 | 123.2381 | 123.3655 | 123.1031 | 66.8751 | -123.654
279.2344 | 123.5825 | -66.9022 | 56.4194 | 0.064445 | -0.012621 | -0.0018439 | 0.052327 | -0.004001 | 0.054706 | 0.066374 | -0.0020844 | -0.0015819 | 0.058496 | 0.02561 | 0.059511 | -66.9167 | 0.019721 | -66.9017 | 56.4487 | 56.3211 | 56.4862 | -67.0481 | -66.9351 | 0.014095 | -67.0017 | 56.3817 | 56.5045 | 56.2421 | -67.2118 | -0.14598 | 0.029336 | -0.014508 | 0.000495 | 0.14648 | -0.098242 | 0.066876 | -0.30961 | -0.037688 | -0.032951 | -0.099507 | 0.2101 | 0.085131 | -0.17723 | 123.3509 | 123.2233 | 123.3884 | 66.9219 | -123.4675 | 123.2838 | 123.4067 | 123.1443 | 66.9163 | -123.6311
280.2344 | 123.5138 | -66.8838 | 56.4331 | 0.064445 | -0.010484 | -0.00077494 | 0.052327 | -0.002933 | 0.052569 | 0.066374 | -0.0042204 | -0.0015819 | 0.060632 | 0.024541 | 0.058443 | -66.9075 | 0.019721 | -66.9062 | 56.4441 | 56.3257 | 56.4954 | -67.0619 | -66.9397 | 0.027831 | -67.0017 | 56.3817 | 56.4999 | 56.2605 | -67.2163 | -0.17803 | 0.011026 | -0.023663 | -0.022395 | 0.15564 | -0.10739 | 0.062301 | -0.3325 | -0.05142 | -0.05584 | -0.11782 | 0.21468 | 0.066821 | -0.17264 | 123.328 | 123.2096 | 123.3793 | 66.9036 | -123.495 | 123.2655 | 123.3838 | 123.1443 | 66.9117 | -123.6495
281.2344 | 123.5916 | -66.8838 | 56.4377 | 0.018659 | -0.012621 | -0.0029119 | 0.051259 | -0.002933 | 0.051501 | 0.081635 | 5.2637e-05 | -0.0037179 | 0.059564 | 0.02561 | 0.058443 | -66.9167 | 0.019721 | -66.9017 | 56.4441 | 56.3303 | 56.4908 | -67.0481 | -66.9351 | 0.018674 | -67.0108 | 56.3817 | 56.5045 | 56.2376 | -67.2163 | -0.16429 | 0.006448 | -0.032819 | -0.017816 | 0.14648 | -0.10739 | 0.053144 | -0.3325 | -0.055998 | -0.051262 | -0.12698 | 0.20552 | 0.066821 | -0.20011 | 123.328 | 123.2141 | 123.3747 | 66.9036 | -123.4858 | 123.2655 | 123.3884 | 123.1214 | 66.9025 | -123.654
282.25 | 123.5001 | -66.8747 | 56.488 | 0.079707 | -0.010484 | -0.00077494 | 0.052327 | -0.004001 | 0.053638 | 0.081635 | -0.0020844 | -0.0026499 | 0.062769 | 0.024541 | 0.058443 | -66.9212 | 0.0243 | -66.9062 | 56.4487 | 56.3394 | 56.4817 | -67.0527 | -66.9397 | 0.023253 | -66.9971 | 56.3771 | 56.5045 | 56.2513 | -67.2163 | -0.17803 | -0.039328 | -0.046553 | -0.03155 | 0.14648 | -0.14859 | -0.006367 | -0.34165 | -0.11093 | -0.064995 | -0.12239 | 0.21926 | 0.016467 | -0.23673 | 123.3234 | 123.2141 | 123.3564 | 66.899 | -123.5408 | 123.2518 | 123.3792 | 123.126 | 66.8979 | -123.7044
283.2344 | 123.5733 | -66.8976 | 56.4239 | 0.079707 | -0.011553 | 0.00029306 | 0.051259 | -0.004001 | 0.052569 | 0.096896 | -0.0020844 | -0.0026499 | 0.059564 | 0.024541 | 0.057375 | -66.9212 | 0.015142 | -66.9108 | 56.4441 | 56.3257 | 56.4862 | -67.039 | -66.9397 | 0.014095 | -66.9971 | 56.3725 | 56.5045 | 56.1735 | -67.2209 | -0.1414 | 0.020181 | -0.023665 | -0.01324 | 0.12816 | -0.09824 | 0.062299 | -0.32334 | -0.051422 | -0.042107 | -0.099506 | 0.22384 | 0.080554 | -0.25048 | 123.3417 | 123.2233 | 123.3838 | 66.9127 | -123.4629 | 123.2701 | 123.4021 | 123.0711 | 66.9117 | -123.6449
284.2344 | 123.5825 | -66.8838 | 56.456 | 0.064445 | -0.010484 | -0.00077494 | 0.051259 | -0.004001 | 0.052569 | 0.081635 | -0.0020844 | -0.0026499 | 0.060632 | 0.024541 | 0.058443 | -66.9167 | 0.028878 | -66.9017 | 56.4487 | 56.3211 | 56.4954 | -67.0573 | -66.9488 | 0.023253 | -66.9971 | 56.3771 | 56.4953 | 56.233 | -67.2209 | -0.17345 | -0.007285 | -0.032819 | -0.017816 | 0.15564 | -0.13486 | 0.039412 | -0.33708 | -0.078888 | -0.064998 | -0.11324 | 0.22384 | 0.039353 | -0.223 | 123.3326 | 123.205 | 123.3793 | 66.9127 | -123.5133 | 123.261 | 123.3792 | 123.1168 | 66.9071 | -123.6769
285.2344 | 123.5916 | -66.861 | 56.4056 | 0.064445 | -0.010484 | -0.0018439 | 0.051259 | -0.004001 | 0.052569 | 0.066374 | -0.0042204 | -0.0015819 | 0.059564 | 0.02561 | 0.057375 | -66.9258 | 0.019721 | -66.9062 | 56.4396 | 56.3303 | 56.4862 | -67.0481 | -66.9397 | 0.014095 | -67.0017 | 56.3771 | 56.5045 | 56.265 | -67.2163 | -0.18718 | 0.033913 | -0.064864 | -0.045283 | 0.1419 | -0.075351 | 0.080609 | -0.35539 | -0.028534 | -0.078728 | -0.14071 | 0.21468 | 0.098864 | -0.1406 | 123.3005 | 123.1913 | 123.3472 | 66.8807 | -123.4538 | 123.2381 | 123.3655 | 123.126 | 66.8751 | -123.622
286.2344 | 123.6237 | -66.8884 | 56.4194 | 0.064445 | -0.011553 | -0.00077494 | 0.052327 | -0.002933 | 0.052569 | 0.066374 | -0.0031524 | -0.0015819 | 0.059564 | 0.026678 | 0.058443 | -66.9121 | 0.019721 | -66.9062 | 56.4441 | 56.3211 | 56.4954 | -67.0573 | -66.9488 | 0.014095 | -67.0062 | 56.3817 | 56.4999 | 56.3566 | -67.2163 | -0.16887 | 0.024758 | -0.023663 | -0.017817 | 0.15106 | -0.098242 | 0.076033 | -0.32792 | -0.037688 | -0.06042 | -0.11782 | 0.2101 | 0.080553 | -0.062761 | 123.3326 | 123.2096 | 123.3838 | 66.9081 | -123.4767 | 123.2701 | 123.3884 | 123.245 | 66.9025 | -123.6357
287.25 | 123.6282 | -66.8701 | 56.4239 | 0.049183 | -0.01369 | -0.00077494 | 0.051259 | -0.006137 | 0.051501 | 0.081635 | -0.0031524 | -0.0037179 | 0.059564 | 0.027746 | 0.059511 | -66.9167 | 0.0243 | -66.9017 | 56.4441 | 56.3257 | 56.4908 | -67.0252 | -66.9443 | 0.018674 | -67.0017 | 56.3817 | 56.5045 | 56.3475 | -67.2163 | -0.15513 | 0.020181 | -0.046552 | -0.031549 | 0.12358 | -0.09824 | 0.066877 | -0.34623 | -0.042265 | -0.074152 | -0.13155 | 0.21468 | 0.080554 | -0.076495 | 123.3142 | 123.1958 | 123.3609 | 66.8944 | -123.4492 | 123.2518 | 123.3746 | 123.2176 | 66.8888 | -123.6403
288.2344 | 123.5779 | -66.8793 | 56.4377 | 0.064445 | -0.012621 | -0.0018439 | 0.052327 | -0.004001 | 0.052569 | 0.066374 | -0.0031524 | -0.0026499 | 0.060632 | 0.028815 | 0.059511 | -66.9167 | 0.0243 | -66.8971 | 56.4441 | 56.3303 | 56.5 | -67.0481 | -66.9443 | 0.023253 | -66.9971 | 56.3817 | 56.5045 | 56.3658 | -67.2118 | -0.16887 | 0.006448 | -0.037397 | -0.017816 | 0.15106 | -0.10739 | 0.062301 | -0.3325 | -0.055998 | -0.064997 | -0.11782 | 0.21468 | 0.066821 | -0.071914 | 123.3234 | 123.2096 | 123.3793 | 66.9036 | -123.4858 | 123.261 | 123.3838 | 123.245 | 66.9025 | -123.6495
289.2344 | 123.5962 | -66.8884 | 56.4331 | 0.064445 | -0.01369 | -0.00077494 | 0.050191 | -0.002933 | 0.052569 | 0.051113 | -0.0031524 | -0.0015819 | 0.058496 | 0.027746 | 0.058443 | -66.9075 | 0.019721 | -66.9062 | 56.4396 | 56.3074 | 56.4908 | -67.0436 | -66.9351 | 0.018674 | -66.9971 | 56.3817 | 56.4999 | 56.3429 | -67.2163 | -0.15514 | 0.006448 | -0.019085 | -0.017817 | 0.13732 | -0.12571 | 0.057722 | -0.32792 | -0.05142 | -0.046684 | -0.10866 | 0.21926 | 0.066821 | -0.090229 | 123.328 | 123.1958 | 123.3793 | 66.9081 | -123.4767 | 123.2701 | 123.3884 | 123.2313 | 66.9071 | -123.6495
290.2344 | 123.6008 | -66.9022 | 56.4148 | 0.079707 | -0.012621 | -0.0018439 | 0.051259 | -0.006137 | 0.053638 | 0.051113 | -0.0020844 | -0.0037179 | 0.059564 | 0.026678 | 0.058443 | -66.9075 | 0.0243 | -66.9062 | 56.4533 | 56.3028 | 56.4954 | -67.0527 | -66.9488 | 0.018674 | -66.9971 | 56.3817 | 56.5045 | 56.352 | -67.2118 | -0.15056 | 0.038493 | -0.005352 | -0.004084 | 0.14648 | -0.11198 | 0.080611 | -0.30961 | -0.03311 | -0.046687 | -0.094928 | 0.21468 | 0.089709 | -0.062762 | 123.3554 | 123.205 | 123.3976 | 66.9265 | -123.4675 | 123.2838 | 123.4067 | 123.2542 | 66.9208 | -123.6266
291.2344 | 123.6191 | -66.8655 | 56.4331 | 0.049183 | -0.01369 | 0.0013621 | 0.052327 | -0.005069 | 0.053638 | 0.081635 | -0.0031524 | -0.00051292 | 0.058496 | 0.028815 | 0.056307 | -66.9167 | 0.019721 | -66.9017 | 56.4441 | 56.3074 | 56.4954 | -67.0573 | -66.9397 | 0.018674 | -66.9971 | 56.3771 | 56.5045 | 56.3291 | -67.2163 | -0.19176 | 0.011026 | -0.051129 | -0.036126 | 0.15564 | -0.12571 | 0.062301 | -0.35081 | -0.055999 | -0.07415 | -0.13155 | 0.21926 | 0.071399 | -0.10396 | 123.3097 | 123.1729 | 123.3609 | 66.8853 | -123.4904 | 123.2426 | 123.37 | 123.1947 | 66.8842 | -123.6495
292.25 | 123.5733 | -66.8655 | 56.4606 | 0.049183 | -0.011553 | -0.0018439 | 0.053396 | -0.004001 | 0.051501 | 0.051113 | -0.0031524 | -0.0015819 | 0.060632 | 0.027746 | 0.058443 | -66.9167 | 0.0243 | -66.8971 | 56.4441 | 56.3166 | 56.4908 | -67.0252 | -66.9488 | 0.018674 | -66.9971 | 56.3817 | 56.5045 | 56.3475 | -67.2209 | -0.15971 | -0.01644 | -0.051129 | -0.031548 | 0.12816 | -0.14402 | 0.030256 | -0.35539 | -0.078886 | -0.083308 | -0.13155 | 0.22384 | 0.043933 | -0.11312 | 123.3097 | 123.1821 | 123.3564 | 66.8898 | -123.4858 | 123.2472 | 123.37 | 123.213 | 66.8842 | -123.6815
293.2344 | 123.587 | -66.893 | 56.4468 | 0.064445 | -0.010484 | -0.00077494 | 0.052327 | -0.007206 | 0.051501 | 0.066374 | -0.0042204 | -0.0015819 | 0.059564 | 0.02561 | 0.057375 | -66.9075 | 0.019721 | -66.9017 | 56.4441 | 56.2982 | 56.4862 | -67.0527 | -66.9488 | 0.018674 | -67.0017 | 56.3771 | 56.5045 | 56.3566 | -67.2118 | -0.15972 | -0.002707 | -0.014508 | -0.008661 | 0.15106 | -0.1486 | 0.039411 | -0.31876 | -0.069732 | -0.055843 | -0.10866 | 0.2101 | 0.057666 | -0.090226 | 123.3371 | 123.1912 | 123.3793 | 66.9127 | -123.4996 | 123.2701 | 123.3975 | 123.2496 | 66.9117 | -123.6586
294.2344 | 123.6053 | -66.9067 | 56.4194 | 0.049183 | -0.011553 | 0.00029306 | 0.052327 | -0.006137 | 0.051501 | 0.066374 | -0.0031524 | 0.00055508 | 0.059564 | 0.02561 | 0.059511 | -66.9121 | 0.0243 | -66.9062 | 56.4396 | 56.3028 | 56.4954 | -67.0436 | -66.9397 | 0.018674 | -66.9925 | 56.3817 | 56.5045 | 56.3475 | -67.2163 | -0.13683 | 0.02018 | -0.005353 | 0.000493 | 0.13732 | -0.11656 | 0.076033 | -0.30961 | -0.037688 | -0.032952 | -0.085772 | 0.22384 | 0.085131 | -0.071918 | 123.3463 | 123.2096 | 123.4021 | 66.931 | -123.4629 | 123.2884 | 123.4112 | 123.2542 | 66.9254 | -123.6357
295.2344 | 123.6374 | -66.8655 | 56.4331 | 0.064445 | -0.011553 | -0.0018439 | 0.051259 | -0.002933 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.058496 | 0.027746 | 0.058443 | -66.9121 | 0.019721 | -66.9108 | 56.4441 | 56.312 | 56.4908 | -67.0207 | -66.9397 | 0.023253 | -67.0017 | 56.3771 | 56.5045 | 56.352 | -67.2163 | -0.15513 | 0.011026 | -0.046551 | -0.045283 | 0.10985 | -0.12113 | 0.057722 | -0.35081 | -0.055999 | -0.07415 | -0.13613 | 0.21468 | 0.071399 | -0.081072 | 123.3097 | 123.1775 | 123.3564 | 66.8853 | -123.4538 | 123.2426 | 123.37 | 123.2176 | 66.8888 | -123.6495
296.2344 | 123.6145 | -66.8564 | 56.4285 | 0.064445 | -0.011553 | -0.0018439 | 0.053396 | -0.006137 | 0.052569 | 0.066374 | -0.0010164 | -0.00051292 | 0.058496 | 0.028815 | 0.059511 | -66.9121 | 0.019721 | -66.9108 | 56.4441 | 56.3028 | 56.4954 | -67.0161 | -66.9397 | 0.018674 | -66.9971 | 56.3817 | 56.4999 | 56.3383 | -67.2163 | -0.15971 | 0.015603 | -0.055707 | -0.054439 | 0.10527 | -0.12571 | 0.066878 | -0.35996 | -0.046843 | -0.083306 | -0.1407 | 0.21926 | 0.071398 | -0.090231 | 123.3005 | 123.1592 | 123.3518 | 66.8761 | -123.4446 | 123.2381 | 123.3563 | 123.1947 | 66.8751 | -123.6449
297.25 | 123.5001 | -66.925 | 56.4514 | 0.049183 | -0.0094162 | 0.00029306 | 0.051259 | -0.004001 | 0.052569 | 0.051113 | -0.0031524 | -0.0037179 | 0.058496 | 0.029883 | 0.058443 | -66.9075 | 0.019721 | -66.9017 | 56.4487 | 56.312 | 56.4908 | -67.0298 | -66.9443 | 0.014095 | -66.9925 | 56.3817 | 56.5137 | 56.3383 | -67.2163 | -0.10478 | -0.002707 | 0.017536 | 0.023383 | 0.12816 | -0.13944 | 0.039411 | -0.2913 | -0.069731 | -0.01922 | -0.067461 | 0.22384 | 0.062246 | -0.11312 | 123.3738 | 123.237 | 123.4159 | 66.9448 | -123.4812 | 123.3067 | 123.4387 | 123.2633 | 66.9391 | -123.6678
298.2344 | 123.6053 | -66.8701 | 56.456 | 0.064445 | -0.011553 | -0.00077494 | 0.051259 | -0.004001 | 0.052569 | 0.051113 | -0.0020844 | -0.0037179 | 0.057427 | 0.028815 | 0.058443 | -66.9121 | 0.0243 | -66.9062 | 56.4441 | 56.3211 | 56.4954 | -67.0527 | -66.9351 | 0.018674 | -66.9971 | 56.3771 | 56.5091 | 56.3429 | -67.2163 | -0.18261 | -0.011863 | -0.041974 | -0.036128 | 0.14648 | -0.13486 | 0.039412 | -0.34623 | -0.078888 | -0.064995 | -0.12697 | 0.21926 | 0.053089 | -0.11312 | 123.3142 | 123.1912 | 123.3655 | 66.8944 | -123.5087 | 123.2472 | 123.3792 | 123.213 | 66.8888 | -123.6723
299.2344 | 123.6008 | -66.8793 | 56.4514 | 0.079707 | -0.012621 | -0.00077494 | 0.052327 | -0.004001 | 0.053638 | 0.066374 | -0.0010164 | -0.0026499 | 0.059564 | 0.028815 | 0.057375 | -66.9167 | 0.019721 | -66.9062 | 56.4441 | 56.2982 | 56.4954 | -67.0344 | -66.9397 | 0.018674 | -66.9925 | 56.3817 | 56.4999 | 56.3337 | -67.2255 | -0.15514 | -0.007285 | -0.037397 | -0.026973 | 0.12816 | -0.15318 | 0.04399 | -0.34623 | -0.069731 | -0.060418 | -0.11324 | 0.233 | 0.04851 | -0.1177 | 123.3234 | 123.1775 | 123.3747 | 66.899 | -123.4858 | 123.261 | 123.3792 | 123.213 | 66.8979 | -123.6769
300.2344 | 123.6328 | -66.861 | 56.4423 | 0.079707 | -0.01369 | -0.00077494 | 0.051259 | -0.001864 | 0.052569 | 0.066374 | -0.0020844 | -0.0037179 | 0.059564 | 0.029883 | 0.057375 | -66.9167 | 0.0243 | -66.9108 | 56.4533 | 56.2937 | 56.5 | -67.0436 | -66.9443 | 0.018674 | -66.9925 | 56.3863 | 56.5045 | 56.3246 | -67.2118 | -0.1826 | 0.011027 | -0.055707 | -0.049861 | 0.13274 | -0.1486 | 0.057723 | -0.35081 | -0.055998 | -0.083307 | -0.13155 | 0.21926 | 0.062243 | -0.1177 | 123.3143 | 123.1546 | 123.3609 | 66.8853 | -123.4858 | 123.2472 | 123.3655 | 123.1855 | 66.8796 | -123.654
301.2344 | 123.6282 | -66.861 | 56.4377 | 0.064445 | -0.014758 | 0.00029306 | 0.052327 | -0.004001 | 0.051501 | 0.066374 | -0.0031524 | -0.0015819 | 0.0617 | 0.029883 | 0.057375 | -66.9121 | 0.0243 | -66.8971 | 56.4441 | 56.3166 | 56.4954 | -67.039 | -66.9443 | 0.018674 | -67.0017 | 56.3863 | 56.4999 | 56.2559 | -67.2163 | -0.17803 | 0.006448 | -0.051129 | -0.036126 | 0.1419 | -0.12113 | 0.057723 | -0.35539 | -0.05142 | -0.083307 | -0.14071 | 0.21468 | 0.062243 | -0.1818 | 123.3051 | 123.1775 | 123.3564 | 66.8853 | -123.4767 | 123.2472 | 123.3609 | 123.1168 | 66.8796 | -123.654
302.25 | 123.4726 | -66.9342 | 56.4423 | 0.033921 | -0.01369 | -0.0018439 | 0.051259 | -0.004001 | 0.051501 | 0.066374 | -0.0031524 | -0.0026499 | 0.059564 | 0.030951 | 0.057375 | -66.9075 | 0.028878 | -66.9017 | 56.4396 | 56.3074 | 56.4954 | -67.0207 | -66.9443 | 0.018674 | -66.9925 | 56.3863 | 56.4999 | 56.2559 | -67.2209 | -0.086467 | -0.002708 | 0.026691 | 0.032538 | 0.119 | -0.13487 | 0.053145 | -0.28672 | -0.055998 | -0.010065 | -0.058306 | 0.22842 | 0.057665 | -0.18638 | 123.3738 | 123.2416 | 123.4296 | 66.9631 | -123.4629 | 123.3205 | 123.4341 | 123.1901 | 66.9529 | -123.6632
303.2344 | 123.6145 | -66.8701 | 56.4148 | 0.064445 | -0.01369 | -0.0018439 | 0.052327 | -0.004001 | 0.052569 | 0.081635 | -0.0031524 | -0.0058549 | 0.060632 | 0.029883 | 0.057375 | -66.9167 | 0.019721 | -66.9017 | 56.4441 | 56.2982 | 56.5 | -67.0344 | -66.9397 | 0.014095 | -66.9971 | 56.3817 | 56.4999 | 56.2467 | -67.2209 | -0.16429 | 0.029336 | -0.046552 | -0.031549 | 0.13274 | -0.11656 | 0.085189 | -0.35081 | -0.03311 | -0.069573 | -0.12697 | 0.22384 | 0.085131 | -0.16807 | 123.3142 | 123.1684 | 123.3701 | 66.8898 | -123.4492 | 123.2518 | 123.37 | 123.1168 | 66.8842 | -123.6357
304.2344 | 123.6099 | -66.8518 | 56.4285 | 0.064445 | -0.015826 | -0.00077494 | 0.052327 | -0.006137 | 0.052569 | 0.066374 | -0.0031524 | -0.0037179 | 0.059564 | 0.027746 | 0.057375 | -66.9075 | 0.028878 | -66.9017 | 56.4441 | 56.2937 | 56.4908 | -67.0252 | -66.9443 | 0.018674 | -67.0062 | 56.3817 | 56.5091 | 56.2513 | -67.2163 | -0.17344 | 0.015603 | -0.055706 | -0.049859 | 0.12358 | -0.13487 | 0.062299 | -0.36454 | -0.046843 | -0.092462 | -0.15444 | 0.2101 | 0.080555 | -0.17722 | 123.2959 | 123.1455 | 123.3426 | 66.8807 | -123.4538 | 123.2335 | 123.3609 | 123.1031 | 66.8705 | -123.6449
305.2344 | 123.587 | -66.8518 | 56.4377 | 0.064445 | -0.012621 | -0.0029119 | 0.051259 | -0.004001 | 0.053638 | 0.066374 | -0.0031524 | -0.0026499 | 0.058496 | 0.030951 | 0.057375 | -66.9121 | 0.010564 | -66.9017 | 56.4487 | 56.3074 | 56.4908 | -67.0344 | -66.9351 | 0.014095 | -66.9971 | 56.3817 | 56.4999 | 56.2879 | -67.2209 | -0.1826 | 0.011026 | -0.060284 | -0.049859 | 0.13274 | -0.13029 | 0.053144 | -0.36912 | -0.055998 | -0.083305 | -0.14528 | 0.22384 | 0.062243 | -0.14975 | 123.3005 | 123.1592 | 123.3426 | 66.8624 | -123.4721 | 123.2335 | 123.3517 | 123.1397 | 66.8659 | -123.6586
306.2344 | 123.587 | -66.861 | 56.4331 | 0.033921 | -0.015826 | -0.0018439 | 0.051259 | -0.004001 | 0.050433 | 0.081635 | -0.0020844 | -0.0026499 | 0.058496 | 0.030951 | 0.058443 | -66.9121 | 0.0243 | -66.9062 | 56.4487 | 56.312 | 56.4954 | -67.0481 | -66.9443 | 0.014095 | -66.9879 | 56.3817 | 56.4999 | 56.265 | -67.2118 | -0.18718 | 0.015604 | -0.051129 | -0.045283 | 0.1419 | -0.12113 | 0.062301 | -0.35081 | -0.05142 | -0.083307 | -0.12697 | 0.22384 | 0.066821 | -0.16806 | 123.3097 | 123.1729 | 123.3564 | 66.8853 | -123.4812 | 123.2426 | 123.3609 | 123.126 | 66.8751 | -123.6449
307.25 | 123.6053 | -66.8884 | 56.4011 | 0.064445 | -0.014758 | 0.00029306 | 0.049122 | -0.004001 | 0.052569 | 0.066374 | -0.0042204 | -0.0058549 | 0.058496 | 0.029883 | 0.058443 | -66.9121 | 0.028878 | -66.9017 | 56.4579 | 56.2662 | 56.5 | -67.0573 | -66.9351 | 0.018674 | -66.9879 | 56.3771 | 56.4953 | 56.2421 | -67.2118 | -0.16887 | 0.056804 | -0.023663 | -0.013238 | 0.15564 | -0.13488 | 0.098922 | -0.32334 | -0.023956 | -0.046684 | -0.099504 | 0.22384 | 0.094285 | -0.15892 | 123.3463 | 123.1546 | 123.3884 | 66.9173 | -123.4584 | 123.2655 | 123.3838 | 123.1306 | 66.9071 | -123.6128
308.2344 | 123.6694 | -66.8838 | 56.4514 | 0.094969 | -0.014758 | 0.00029306 | 0.050191 | -0.005069 | 0.053638 | 0.081635 | -0.0031524 | -0.0015819 | 0.060632 | 0.027746 | 0.058443 | -66.9075 | 0.028878 | -66.9017 | 56.4533 | 56.3028 | 56.4862 | -67.0481 | -66.9397 | 0.018674 | -66.9971 | 56.3863 | 56.5091 | 56.2284 | -67.2209 | -0.16429 | 0.001872 | -0.023663 | -0.017816 | 0.14648 | -0.1486 | 0.034833 | -0.33708 | -0.065153 | -0.05584 | -0.11324 | 0.22384 | 0.057667 | -0.22301 | 123.3371 | 123.1867 | 123.3701 | 66.9127 | -123.4996 | 123.2701 | 123.3929 | 123.1123 | 66.9025 | -123.6723
309.2344 | 123.6237 | -66.8655 | 56.4697 | 0.049183 | -0.01369 | -0.00077494 | 0.051259 | -0.004001 | 0.051501 | 0.066374 | 5.2637e-05 | -0.0037179 | 0.060632 | 0.027746 | 0.056307 | -66.9121 | 0.019721 | -66.8971 | 56.4487 | 56.3028 | 56.5 | -67.0573 | -66.9351 | 0.023253 | -66.9971 | 56.3863 | 56.4999 | 56.233 | -67.2163 | -0.19176 | -0.021018 | -0.046551 | -0.031548 | 0.16021 | -0.16691 | 0.030257 | -0.35081 | -0.083464 | -0.069572 | -0.13155 | 0.21926 | 0.030199 | -0.23674 | 123.3142 | 123.1684 | 123.3655 | 66.8853 | -123.527 | 123.2518 | 123.3655 | 123.0985 | 66.8888 | -123.6861
310.2344 | 123.6099 | -66.8884 | 56.4239 | 0.064445 | -0.015826 | -0.00077494 | 0.051259 | -0.006137 | 0.052569 | 0.066374 | -0.0020844 | -0.0026499 | 0.059564 | 0.030951 | 0.056307 | -66.9121 | 0.019721 | -66.9017 | 56.4441 | 56.3028 | 56.4954 | -67.0252 | -66.9397 | 0.014095 | -67.0017 | 56.3863 | 56.5045 | 56.2742 | -67.2255 | -0.13682 | 0.020181 | -0.023663 | -0.013238 | 0.12358 | -0.12113 | 0.071456 | -0.33708 | -0.037687 | -0.051262 | -0.11324 | 0.22384 | 0.080554 | -0.14975 | 123.3326 | 123.1912 | 123.3838 | 66.9081 | -123.4492 | 123.2747 | 123.3929 | 123.1626 | 66.9025 | -123.6495
311.2344 | 123.6328 | -66.8747 | 56.4423 | 0.064445 | -0.014758 | 0.00029306 | 0.050191 | -0.004001 | 0.052569 | 0.066374 | -0.0020844 | -0.0026499 | 0.058496 | 0.029883 | 0.057375 | -66.9212 | 0.0243 | -66.9062 | 56.4396 | 56.2982 | 56.5 | -67.0298 | -66.9443 | 0.014095 | -67.0062 | 56.3817 | 56.4999 | 56.2376 | -67.2072 | -0.15513 | -0.002708 | -0.046553 | -0.03155 | 0.12358 | -0.14402 | 0.057723 | -0.33249 | -0.060576 | -0.069574 | -0.13155 | 0.20094 | 0.057665 | -0.20469 | 123.3142 | 123.1729 | 123.3747 | 66.899 | -123.4721 | 123.2564 | 123.3746 | 123.1123 | 66.8888 | -123.6495
312.25 | 123.4955 | -66.9296 | 56.4651 | 0.049183 | -0.015826 | -0.0018439 | 0.050191 | -0.005069 | 0.052569 | 0.051113 | -0.0020844 | -0.0037179 | 0.059564 | 0.027746 | 0.056307 | -66.9075 | 0.028878 | -66.9017 | 56.4533 | 56.2982 | 56.5046 | -67.0436 | -66.9351 | 0.018674 | -66.9879 | 56.3863 | 56.5045 | 56.2696 | -67.2209 | -0.11394 | -0.011861 | 0.022113 | 0.02796 | 0.1419 | -0.16691 | 0.039414 | -0.2913 | -0.078886 | -0.005486 | -0.058306 | 0.233 | 0.039355 | -0.19553 | 123.3829 | 123.2279 | 123.4342 | 66.9585 | -123.5087 | 123.3159 | 123.4341 | 123.1992 | 66.9483 | -123.6861
313.2344 | 123.6008 | -66.8701 | 56.4148 | 0.049183 | -0.015826 | -0.00077494 | 0.051259 | -0.004001 | 0.053638 | 0.081635 | 5.2637e-05 | -0.0015819 | 0.057427 | 0.029883 | 0.058443 | -66.9212 | 0.019721 | -66.9017 | 56.4533 | 56.3166 | 56.5 | -67.0573 | -66.9351 | 0.014095 | -66.9879 | 56.3863 | 56.4999 | 56.2376 | -67.2209 | -0.18719 | 0.038493 | -0.051131 | -0.031549 | 0.15564 | -0.098243 | 0.085189 | -0.35081 | -0.028532 | -0.064995 | -0.11782 | 0.233 | 0.085131 | -0.17723 | 123.3234 | 123.1867 | 123.3701 | 66.8898 | -123.4721 | 123.2564 | 123.37 | 123.1077 | 66.8842 | -123.6357
314.2344 | 123.6282 | -66.8564 | 56.4102 | 0.049183 | -0.014758 | 0.00029306 | 0.052327 | -0.004001 | 0.052569 | 0.051113 | -0.0020844 | -0.0026499 | 0.059564 | 0.029883 | 0.057375 | -66.9167 | 0.0243 | -66.8925 | 56.4441 | 56.3074 | 56.4908 | -67.0573 | -66.9397 | 0.009516 | -66.9971 | 56.3817 | 56.4999 | 56.2513 | -67.2163 | -0.20092 | 0.033914 | -0.060285 | -0.036126 | 0.16479 | -0.10282 | 0.08061 | -0.35996 | -0.028532 | -0.083306 | -0.1407 | 0.21926 | 0.089709 | -0.15891 | 123.3005 | 123.1638 | 123.3472 | 66.8807 | -123.4675 | 123.2381 | 123.3563 | 123.1077 | 66.8659 | -123.6266
315.2344 | 123.6328 | -66.8518 | 56.4285 | 0.079707 | -0.012621 | 0.0013621 | 0.051259 | -0.002933 | 0.052569 | 0.051113 | -0.0010164 | -0.0026499 | 0.058496 | 0.030951 | 0.057375 | -66.9121 | 0.015142 | -66.9062 | 56.4579 | 56.3166 | 56.5 | -67.0252 | -66.9488 | 0.014095 | -66.9925 | 56.3863 | 56.4999 | 56.2559 | -67.2118 | -0.17344 | 0.029338 | -0.060284 | -0.054438 | 0.11901 | -0.11198 | 0.071456 | -0.35996 | -0.042265 | -0.097041 | -0.1407 | 0.21926 | 0.071398 | -0.17265 | 123.3097 | 123.1684 | 123.3518 | 66.8669 | -123.4538 | 123.2381 | 123.3517 | 123.1077 | 66.8659 | -123.6403
316.2344 | 123.5733 | -66.8701 | 56.4239 | 0.064445 | -0.014758 | -0.00077494 | 0.052327 | -0.005069 | 0.053638 | 0.066374 | -0.0020844 | -0.0026499 | 0.057427 | 0.030951 | 0.057375 | -66.9075 | 0.028878 | -66.8925 | 56.4533 | 56.3211 | 56.5 | -67.0481 | -66.9443 | 0.014095 | -66.9971 | 56.3863 | 56.5091 | 56.3154 | -67.2118 | -0.17803 | 0.029338 | -0.037396 | -0.022393 | 0.15563 | -0.10282 | 0.076034 | -0.34165 | -0.037687 | -0.074152 | -0.12697 | 0.21468 | 0.085133 | -0.10855 | 123.3234 | 123.1912 | 123.3701 | 66.899 | -123.4721 | 123.2564 | 123.3792 | 123.1855 | 66.8842 | -123.6357
317.2344 | 123.5229 | -66.8793 | 56.4651 | 0.064445 | -0.014758 | -0.00077494 | 0.050191 | -0.007206 | 0.052569 | 0.066374 | -0.0010164 | -0.0047869 | 0.058496 | 0.030951 | 0.056307 | -66.9029 | 0.0243 | -66.9017 | 56.4487 | 56.3211 | 56.5 | -67.0573 | -66.9397 | 0.014095 | -66.9971 | 56.3863 | 56.5182 | 56.3383 | -67.2163 | -0.17803 | -0.01644 | -0.023662 | -0.022394 | 0.15564 | -0.14402 | 0.034835 | -0.33708 | -0.078886 | -0.060418 | -0.11782 | 0.21926 | 0.053091 | -0.12685 | 123.328 | 123.2004 | 123.3793 | 66.9036 | -123.5225 | 123.2655 | 123.3975 | 123.2176 | 66.8934 | -123.6815
318.2344 | 123.6328 | -66.9022 | 56.4239 | 0.064445 | -0.015826 | -0.0018439 | 0.051259 | -0.004001 | 0.052569 | 0.066374 | -0.0020844 | -0.0037179 | 0.057427 | 0.029883 | 0.057375 | -66.9075 | 0.019721 | -66.9062 | 56.4533 | 56.2982 | 56.5 | -67.0344 | -66.9397 | 0.018674 | -66.9834 | 56.3817 | 56.5091 | 56.3337 | -67.2163 | -0.13225 | 0.029338 | -0.005352 | -0.004084 | 0.12816 | -0.12571 | 0.076034 | -0.31419 | -0.042265 | -0.037529 | -0.081192 | 0.233 | 0.085133 | -0.090231 | 123.3554 | 123.2004 | 123.4021 | 66.9219 | -123.4584 | 123.2838 | 123.4112 | 123.2359 | 66.9208 | -123.6403
319.2344 | 123.555 | -66.893 | 56.4651 | 0.064445 | -0.01369 | -0.0018439 | 0.050191 | -0.005069 | 0.051501 | 0.051113 | -0.0020844 | -0.0047869 | 0.059564 | 0.03202 | 0.056307 | -66.9029 | 0.019721 | -66.9108 | 56.4533 | 56.3028 | 56.4908 | -67.0207 | -66.9351 | 0.018674 | -66.9925 | 56.3863 | 56.5091 | 56.2513 | -67.2118 | -0.12767 | -0.011861 | -0.009929 | -0.017818 | 0.10985 | -0.16233 | 0.025678 | -0.31876 | -0.078886 | -0.042107 | -0.099505 | 0.21926 | 0.043934 | -0.21384 | 123.3463 | 123.1958 | 123.3838 | 66.9127 | -123.4858 | 123.2793 | 123.4021 | 123.1443 | 66.9117 | -123.6769
320.2344 | 123.5458 | -66.8655 | 56.456 | 0.064445 | -0.015826 | -0.0018439 | 0.053396 | -0.005069 | 0.050433 | 0.081635 | -0.0031524 | -0.0037179 | 0.058496 | 0.030951 | 0.057375 | -66.9075 | 0.019721 | -66.9062 | 56.4533 | 56.3211 | 56.5046 | -67.0436 | -66.9443 | 0.009516 | -66.9834 | 56.3863 | 56.5091 | 56.2513 | -67.2163 | -0.17803 | -0.002706 | -0.041973 | -0.040705 | 0.13732 | -0.13486 | 0.048569 | -0.35081 | -0.069731 | -0.078729 | -0.11781 | 0.233 | 0.053089 | -0.20469 | 123.3188 | 123.1867 | 123.3701 | 66.8853 | -123.4996 | 123.2518 | 123.3746 | 123.1168 | 66.8751 | -123.6723
321.2344 | 123.6053 | -66.8564 | 56.4331 | 0.079707 | -0.01369 | -0.0018439 | 0.050191 | -0.004001 | 0.050433 | 0.096896 | -0.0042204 | -0.0047869 | 0.058496 | 0.028815 | 0.056307 | -66.9167 | 0.019721 | -66.9017 | 56.4533 | 56.2937 | 56.5 | -67.0207 | -66.9351 | 0.004938 | -66.9834 | 56.3908 | 56.5091 | 56.2238 | -67.2163 | -0.16429 | 0.020183 | -0.060285 | -0.045282 | 0.119 | -0.13945 | 0.066879 | -0.35996 | -0.042263 | -0.078728 | -0.12697 | 0.233 | 0.075978 | -0.20927 | 123.3097 | 123.15 | 123.3564 | 66.8761 | -123.4538 | 123.2472 | 123.3655 | 123.0802 | 66.8613 | -123.6495
322.25 | 123.5092 | -66.9067 | 56.4743 | 0.049183 | -0.015826 | -0.00077494 | 0.052327 | -0.004001 | 0.052569 | 0.096896 | -0.0031524 | -0.0026499 | 0.060632 | 0.030951 | 0.058443 | -66.9121 | 0.0243 | -66.9017 | 56.4533 | 56.3028 | 56.5 | -67.0481 | -66.9443 | 0.018674 | -66.9925 | 56.3817 | 56.5091 | 56.2376 | -67.2163 | -0.14141 | -0.021016 | -0.005353 | 0.005072 | 0.14648 | -0.17149 | 0.02568 | -0.30961 | -0.092619 | -0.037531 | -0.085772 | 0.22384 | 0.034779 | -0.23674 | 123.36 | 123.2096 | 123.4067 | 66.931 | -123.5224 | 123.2884 | 123.4158 | 123.1443 | 66.9254 | -123.6907
323.2344 | 123.555 | -66.9022 | 56.4743 | 0.079707 | -0.014758 | -0.0018439 | 0.050191 | -0.005069 | 0.052569 | 0.081635 | -0.0020844 | -0.0037179 | 0.059564 | 0.03202 | 0.058443 | -66.9121 | 0.0243 | -66.9017 | 56.4487 | 56.2891 | 56.5137 | -67.0527 | -66.9397 | 0.014095 | -66.9834 | 56.3817 | 56.5137 | 56.2925 | -67.2163 | -0.15056 | -0.025595 | -0.00993 | 0.000495 | 0.15106 | -0.18523 | 0.039416 | -0.31419 | -0.092619 | -0.037529 | -0.081192 | 0.233 | 0.039358 | -0.18179 | 123.3509 | 123.1912 | 123.4159 | 66.9265 | -123.527 | 123.2838 | 123.4158 | 123.1947 | 66.9163 | -123.6907
324.2344 | 123.5641 | -66.8701 | 56.4606 | 0.049183 | -0.015826 | -0.0018439 | 0.050191 | -0.005069 | 0.052569 | 0.051113 | -0.0031524 | -0.0026499 | 0.058496 | 0.030951 | 0.056307 | -66.9075 | 0.015142 | -66.9017 | 56.4579 | 56.3028 | 56.5 | -67.0298 | -66.9443 | 0.009516 | -66.9971 | 56.3863 | 56.5091 | 56.265 | -67.2163 | -0.15971 | -0.002705 | -0.037396 | -0.031549 | 0.12816 | -0.15776 | 0.039413 | -0.34623 | -0.074308 | -0.074152 | -0.12697 | 0.21926 | 0.048512 | -0.19553 | 123.328 | 123.1729 | 123.3701 | 66.8853 | -123.4904 | 123.2564 | 123.3792 | 123.1352 | 66.8796 | -123.6769
325.2344 | 123.5825 | -66.8793 | 56.4468 | 0.094969 | -0.015826 | -0.0029119 | 0.050191 | -0.004001 | 0.051501 | 0.051113 | -0.0042204 | -0.0015819 | 0.057427 | 0.029883 | 0.058443 | -66.9075 | 0.0243 | -66.8971 | 56.4533 | 56.2891 | 56.5 | -67.0344 | -66.9443 | 0.014095 | -66.9879 | 56.3817 | 56.5091 | 56.2605 | -67.2163 | -0.15514 | 0.00645 | -0.028241 | -0.017816 | 0.13732 | -0.15776 | 0.053146 | -0.33708 | -0.065153 | -0.064997 | -0.10866 | 0.22842 | 0.062245 | -0.18638 | 123.3326 | 123.1684 | 123.3793 | 66.9036 | -123.4812 | 123.261 | 123.3884 | 123.1397 | 66.8934 | -123.6632
326.2344 | 123.5001 | -66.8884 | 56.4697 | 0.033921 | -0.016895 | -0.0029119 | 0.051259 | -0.005069 | 0.051501 | 0.051113 | -0.0020844 | -0.0026499 | 0.058496 | 0.03202 | 0.057375 | -66.9075 | 0.015142 | -66.8925 | 56.4487 | 56.2799 | 56.4908 | -67.0436 | -66.9351 | 0.009516 | -66.9925 | 56.3908 | 56.5091 | 56.2879 | -67.2163 | -0.15514 | -0.021018 | -0.019085 | -0.004082 | 0.15105 | -0.18981 | 0.0211 | -0.32792 | -0.078885 | -0.046684 | -0.10408 | 0.22384 | 0.039356 | -0.18179 | 123.3371 | 123.1683 | 123.3793 | 66.9036 | -123.5133 | 123.2793 | 123.3975 | 123.1764 | 66.8979 | -123.6861
327.2344 | 123.5458 | -66.893 | 56.4651 | 0.064445 | -0.016895 | -0.00077494 | 0.051259 | -0.004001 | 0.052569 | 0.051113 | -0.0031524 | -0.0026499 | 0.057427 | 0.030951 | 0.055238 | -66.9121 | 0.0243 | -66.9017 | 56.4441 | 56.3257 | 56.5 | -67.0527 | -66.9397 | 0.014095 | -66.9879 | 56.3817 | 56.5091 | 56.2513 | -67.2209 | -0.15972 | -0.021018 | -0.019086 | -0.008661 | 0.15106 | -0.13944 | 0.034835 | -0.32792 | -0.083464 | -0.046685 | -0.094927 | 0.233 | 0.043934 | -0.21384 | 123.3371 | 123.2187 | 123.393 | 66.9173 | -123.5179 | 123.2747 | 123.4021 | 123.1443 | 66.9071 | -123.6861
328.2344 | 123.5779 | -66.8747 | 56.4423 | 0.079707 | -0.015826 | -0.0018439 | 0.050191 | -0.004001 | 0.052569 | 0.081635 | -0.0010164 | -0.0026499 | 0.057427 | 0.033088 | 0.057375 | -66.9029 | 0.015142 | -66.8971 | 56.4487 | 56.3257 | 56.5 | -67.0481 | -66.9351 | 0.004938 | -66.9834 | 56.3863 | 56.5045 | 56.3017 | -67.2163 | -0.17345 | 0.006448 | -0.028239 | -0.022393 | 0.15106 | -0.11655 | 0.057723 | -0.34165 | -0.055998 | -0.060417 | -0.10866 | 0.233 | 0.062243 | -0.14059 | 123.3234 | 123.2004 | 123.3747 | 66.8898 | -123.4904 | 123.261 | 123.3792 | 123.1764 | 66.8796 | -123.6586
329.2344 | 123.6053 | -66.8747 | 56.4468 | 0.079707 | -0.014758 | -0.0018439 | 0.050191 | -0.005069 | 0.050433 | 0.081635 | -0.0042204 | -0.0026499 | 0.058496 | 0.030951 | 0.058443 | -66.9121 | 0.019721 | -66.9017 | 56.4579 | 56.3166 | 56.5046 | -67.0207 | -66.9397 | -0.00422 | -66.9925 | 56.3817 | 56.5091 | 56.3383 | -67.2118 | -0.14598 | 0.011028 | -0.037396 | -0.026971 | 0.119 | -0.13029 | 0.057725 | -0.33707 | -0.065153 | -0.064995 | -0.11781 | 0.21926 | 0.062245 | -0.10854 | 123.3326 | 123.1912 | 123.3793 | 66.8944 | -123.4675 | 123.2564 | 123.3838 | 123.213 | 66.8705 | -123.6586
330.2344 | 123.5413 | -66.9113 | 56.4835 | 0.064445 | -0.014758 | -0.00077494 | 0.050191 | -0.005069 | 0.052569 | 0.066374 | -0.0020844 | -0.0026499 | 0.058496 | 0.033088 | 0.058443 | -66.9212 | 0.019721 | -66.9017 | 56.4487 | 56.3257 | 56.5046 | -67.039 | -66.9305 | 0.004938 | -66.9879 | 56.3863 | 56.5091 | 56.3658 | -67.2118 | -0.12767 | -0.03475 | -0.009932 | 0.00965 | 0.13732 | -0.15775 | 0.021104 | -0.30045 | -0.097196 | -0.019217 | -0.076616 | 0.22384 | 0.025624 | -0.11769 | 123.36 | 123.237 | 123.4159 | 66.931 | -123.5224 | 123.2976 | 123.4204 | 123.2771 | 66.9163 | -123.6952
331.2344 | 123.4909 | -66.9159 | 56.4926 | 0.064445 | -0.015826 | -0.00077494 | 0.050191 | -0.004001 | 0.051501 | 0.051113 | -0.0031524 | -0.0037179 | 0.058496 | 0.034157 | 0.056307 | -66.9075 | 0.019721 | -66.9017 | 56.4533 | 56.312 | 56.5046 | -67.039 | -66.9397 | 0.000359 | -66.9834 | 56.3817 | 56.5137 | 56.3658 | -67.2163 | -0.12309 | -0.039327 | 0.008381 | 0.014228 | 0.13732 | -0.18064 | 0.011948 | -0.30045 | -0.11093 | -0.023796 | -0.067459 | 0.233 | 0.021047 | -0.12685 | 123.3692 | 123.2279 | 123.4205 | 66.9356 | -123.5316 | 123.2976 | 123.4296 | 123.2817 | 66.9163 | -123.709
332.25 | 123.5001 | -66.9067 | 56.4514 | 0.064445 | -0.015826 | -0.0018439 | 0.051259 | -0.006137 | 0.052569 | 0.081635 | -0.0020844 | -0.0037179 | 0.058496 | 0.03202 | 0.057375 | -66.9029 | 0.0243 | -66.8925 | 56.4579 | 56.3166 | 56.5 | -67.0481 | -66.9443 | 0.009516 | -66.9834 | 56.3863 | 56.5091 | 56.3612 | -67.2118 | -0.14141 | 0.00645 | 0.003804 | 0.014228 | 0.15563 | -0.13486 | 0.048568 | -0.30503 | -0.065153 | -0.037531 | -0.076615 | 0.22842 | 0.057667 | -0.090226 | 123.3646 | 123.2233 | 123.4067 | 66.931 | -123.4996 | 123.293 | 123.4158 | 123.2679 | 66.9163 | -123.6632
333.2344 | 123.4772 | -66.9205 | 56.4789 | 0.064445 | -0.015826 | 0.00029306 | 0.051259 | -0.002933 | 0.051501 | 0.066374 | -0.0031524 | -0.0047869 | 0.058496 | 0.034157 | 0.055238 | -66.9075 | 0.019721 | -66.8925 | 56.4487 | 56.3166 | 56.4954 | -67.0481 | -66.9488 | 0.004938 | -66.9879 | 56.3817 | 56.5137 | 56.3612 | -67.2118 | -0.12767 | -0.030173 | 0.012958 | 0.027961 | 0.15563 | -0.16233 | 0.016524 | -0.2913 | -0.097197 | -0.028377 | -0.067461 | 0.22384 | 0.03478 | -0.11769 | 123.3692 | 123.237 | 123.4159 | 66.9402 | -123.527 | 123.3022 | 123.4341 | 123.2817 | 66.9254 | -123.6907
334.2344 | 123.4726 | -66.9113 | 56.4789 | 0.064445 | -0.016895 | -0.00077494 | 0.051259 | -0.006137 | 0.051501 | 0.066374 | -0.0020844 | -0.0037179 | 0.059564 | 0.03202 | 0.056307 | -66.9121 | 0.019721 | -66.8971 | 56.4533 | 56.3211 | 56.5 | -67.0527 | -66.9443 | 0.009516 | -66.9834 | 56.3771 | 56.5182 | 56.3658 | -67.2118 | -0.14141 | -0.025594 | -0.000775 | 0.014228 | 0.15564 | -0.15775 | 0.021102 | -0.30045 | -0.10178 | -0.032953 | -0.072037 | 0.22842 | 0.039358 | -0.11311 | 123.3646 | 123.2324 | 123.4113 | 66.931 | -123.5316 | 123.2884 | 123.4296 | 123.2771 | 66.9208 | -123.6907
335.2344 | 123.5367 | -66.8884 | 56.4697 | 0.094969 | -0.017963 | -0.00077494 | 0.053396 | -0.006137 | 0.050433 | 0.066374 | -0.0010164 | -0.0047869 | 0.058496 | 0.03202 | 0.05417 | -66.9029 | 0.019721 | -66.8925 | 56.4533 | 56.3349 | 56.5046 | -67.0481 | -66.9397 | 0.009516 | -66.9879 | 56.3863 | 56.5091 | 56.3658 | -67.2209 | -0.15972 | -0.016439 | -0.014506 | -0.004082 | 0.15563 | -0.13486 | 0.034836 | -0.3325 | -0.083464 | -0.051262 | -0.099504 | 0.233 | 0.039356 | -0.10396 | 123.3417 | 123.2233 | 123.393 | 66.9081 | -123.5179 | 123.2747 | 123.3975 | 123.2542 | 66.8979 | -123.6907
336.2344 | 123.5138 | -66.9159 | 56.4789 | 0.079707 | -0.015826 | -0.00077494 | 0.051259 | -0.005069 | 0.051501 | 0.051113 | -0.0010164 | -0.0026499 | 0.059564 | 0.030951 | 0.056307 | -66.9075 | 0.015142 | -66.8971 | 56.4441 | 56.3303 | 56.5091 | -67.0436 | -66.9443 | 0.004938 | -66.9834 | 56.3771 | 56.5137 | 56.3658 | -67.2209 | -0.12767 | -0.034751 | 0.008381 | 0.018806 | 0.14648 | -0.14859 | 0.03026 | -0.30503 | -0.10178 | -0.028375 | -0.067459 | 0.23757 | 0.03478 | -0.11311 | 123.36 | 123.2462 | 123.425 | 66.931 | -123.5224 | 123.293 | 123.4296 | 123.2817 | 66.9208 | -123.6998
337.25 | 123.5596 | -66.9205 | 56.4606 | 0.064445 | -0.016895 | -0.0018439 | 0.051259 | -0.005069 | 0.052569 | 0.051113 | -0.0031524 | -0.0047869 | 0.057427 | 0.033088 | 0.058443 | -66.8984 | 0.0243 | -66.9108 | 56.4487 | 56.3257 | 56.5046 | -67.0344 | -66.9443 | 0.004938 | -66.9834 | 56.3863 | 56.5137 | 56.3749 | -67.2163 | -0.11394 | -0.011862 | 0.022115 | 0.009648 | 0.12359 | -0.13486 | 0.043992 | -0.29588 | -0.074308 | -0.023798 | -0.062882 | 0.233 | 0.053091 | -0.085645 | 123.3692 | 123.2462 | 123.425 | 66.9448 | -123.495 | 123.3067 | 123.4341 | 123.2954 | 66.9254 | -123.6769
338.2344 | 123.4955 | -66.8793 | 56.488 | 0.079707 | -0.017963 | -0.00077494 | 0.050191 | -0.005069 | 0.052569 | 0.081635 | -0.0020844 | -0.0058549 | 0.058496 | 0.03202 | 0.058443 | -66.9075 | 0.015142 | -66.8971 | 56.4533 | 56.3211 | 56.4954 | -67.0481 | -66.9443 | 0.000359 | -66.9925 | 56.3817 | 56.5182 | 56.3795 | -67.2209 | -0.16887 | -0.034749 | -0.028241 | -0.017816 | 0.15106 | -0.16691 | 0.007369 | -0.34166 | -0.10635 | -0.064997 | -0.11324 | 0.22842 | 0.030203 | -0.10853 | 123.3326 | 123.2004 | 123.3747 | 66.8944 | -123.5362 | 123.261 | 123.3975 | 123.2588 | 66.8796 | -123.709
339.2344 | 123.4314 | -66.9205 | 56.5338 | 0.079707 | -0.017963 | -0.00077494 | 0.051259 | -0.004001 | 0.051501 | 0.066374 | -0.0031524 | -0.0047869 | 0.058496 | 0.03202 | 0.057375 | -66.9029 | 0.015142 | -66.9017 | 56.4487 | 56.3257 | 56.5046 | -67.039 | -66.9443 | 0.004938 | -66.9971 | 56.3863 | 56.5182 | 56.3749 | -67.2118 | -0.11852 | -0.085104 | 0.017537 | 0.018805 | 0.13732 | -0.2081 | -0.02925 | -0.2913 | -0.14755 | -0.023798 | -0.076618 | 0.21468 | -0.015573 | -0.15889 | 123.3692 | 123.2462 | 123.425 | 66.9356 | -123.5728 | 123.3067 | 123.4387 | 123.2954 | 66.9254 | -123.7456
340.2344 | 123.5275 | -66.9067 | 56.488 | 0.064445 | -0.016895 | -0.00077494 | 0.050191 | -0.006137 | 0.052569 | 0.066374 | -0.0031524 | -0.0047869 | 0.057427 | 0.034157 | 0.058443 | -66.9075 | 0.015142 | -66.9017 | 56.4533 | 56.3303 | 56.5 | -67.0436 | -66.9351 | 0.009516 | -66.9879 | 56.3863 | 56.5137 | 56.3612 | -67.2163 | -0.13683 | -0.034749 | -0.000775 | 0.005072 | 0.1419 | -0.15775 | 0.011947 | -0.30961 | -0.10177 | -0.028374 | -0.081194 | 0.22842 | 0.025625 | -0.12685 | 123.36 | 123.237 | 123.4067 | 66.9219 | -123.5316 | 123.293 | 123.4204 | 123.2679 | 66.9163 | -123.7044
341.2344 | 123.5046 | -66.9205 | 56.4697 | 0.049183 | -0.016895 | -0.00077494 | 0.050191 | -0.005069 | 0.051501 | 0.081635 | -0.0031524 | -0.0026499 | 0.057427 | 0.033088 | 0.057375 | -66.9029 | 0.015142 | -66.9017 | 56.4533 | 56.3349 | 56.5046 | -67.0436 | -66.9488 | 0.004938 | -66.9834 | 56.3817 | 56.5091 | 56.3658 | -67.2118 | -0.12309 | -0.016439 | 0.017537 | 0.018805 | 0.1419 | -0.13486 | 0.034836 | -0.2913 | -0.088042 | -0.028377 | -0.062882 | 0.22842 | 0.039356 | -0.10396 | 123.3738 | 123.2553 | 123.425 | 66.9356 | -123.5133 | 123.3022 | 123.4296 | 123.2862 | 66.9254 | -123.6815
342.25 | 123.5138 | -66.9342 | 56.4743 | 0.033921 | -0.016895 | -0.00077494 | 0.050191 | -0.006137 | 0.051501 | 0.081635 | -0.0052884 | -0.0047869 | 0.057427 | 0.033088 | 0.056307 | -66.9075 | 0.010564 | -66.8925 | 56.4624 | 56.3349 | 56.5046 | -67.0436 | -66.9397 | 0.004938 | -66.9834 | 56.3908 | 56.5137 | 56.3612 | -67.2163 | -0.10936 | -0.011859 | 0.026691 | 0.041694 | 0.15105 | -0.13944 | 0.030259 | -0.28214 | -0.083462 | -0.005486 | -0.049149 | 0.233 | 0.039358 | -0.11311 | 123.3966 | 123.2691 | 123.4388 | 66.9448 | -123.5179 | 123.325 | 123.4479 | 123.2954 | 66.9391 | -123.6907
343.2344 | 123.5458 | -66.8976 | 56.4835 | 0.079707 | -0.016895 | -0.0018439 | 0.050191 | -0.005069 | 0.051501 | 0.066374 | -0.0031524 | -0.0058549 | 0.058496 | 0.033088 | 0.057375 | -66.8984 | 0.010564 | -66.9017 | 56.4579 | 56.3349 | 56.5046 | -67.0298 | -66.9397 | 0.000359 | -66.9834 | 56.3908 | 56.5045 | 56.3841 | -67.2163 | -0.13225 | -0.025593 | -0.000773 | -0.004083 | 0.12816 | -0.14859 | 0.021104 | -0.31876 | -0.092617 | -0.042107 | -0.08577 | 0.233 | 0.021045 | -0.099376 | 123.3554 | 123.2325 | 123.4021 | 66.9081 | -123.5133 | 123.2884 | 123.4021 | 123.2817 | 66.8979 | -123.6998
344.2344 | 123.5138 | -66.9022 | 56.456 | 0.049183 | -0.019031 | -0.0029119 | 0.051259 | -0.004001 | 0.052569 | 0.066374 | -0.0042204 | -0.0037179 | 0.058496 | 0.033088 | 0.056307 | -66.8984 | 0.015142 | -66.8971 | 56.4579 | 56.3349 | 56.5091 | -67.0436 | -66.9351 | -0.00422 | -66.9834 | 56.3817 | 56.5182 | 56.352 | -67.2118 | -0.1414 | 0.001872 | 0.003805 | 0.005073 | 0.14648 | -0.12113 | 0.053148 | -0.30961 | -0.074309 | -0.032951 | -0.081192 | 0.22842 | 0.062246 | -0.10396 | 123.36 | 123.237 | 123.4113 | 66.9173 | -123.4996 | 123.2838 | 123.4204 | 123.2542 | 66.8979 | -123.6678
345.2344 | 123.5092 | -66.9022 | 56.4835 | 0.064445 | -0.019031 | -0.0018439 | 0.051259 | -0.005069 | 0.050433 | 0.096896 | -0.0031524 | -0.0037179 | 0.059564 | 0.034157 | 0.055238 | -66.8984 | 0.010564 | -66.8971 | 56.4579 | 56.3211 | 56.5091 | -67.0527 | -66.9397 | -0.00422 | -66.9879 | 56.4 | 56.5091 | 56.3703 | -67.2118 | -0.15056 | -0.025593 | 0.003805 | 0.005073 | 0.15564 | -0.16233 | 0.025683 | -0.30961 | -0.08346 | -0.037529 | -0.085771 | 0.22384 | 0.025624 | -0.11311 | 123.36 | 123.2233 | 123.4113 | 66.9127 | -123.5362 | 123.3022 | 123.4112 | 123.2725 | 66.8979 | -123.6952
346.2344 | 123.5504 | -66.9296 | 56.4239 | 0.049183 | -0.017963 | -0.0018439 | 0.049122 | -0.005069 | 0.052569 | 0.081635 | -0.0020844 | -0.0037179 | 0.057427 | 0.035225 | 0.058443 | -66.8984 | 0.010564 | -66.8971 | 56.4579 | 56.3486 | 56.5091 | -67.0573 | -66.9351 | 0.009516 | -66.9788 | 56.3863 | 56.5137 | 56.3612 | -67.2118 | -0.12768 | 0.033916 | 0.03127 | 0.032538 | 0.16021 | -0.075346 | 0.085192 | -0.28214 | -0.037687 | -0.005486 | -0.049148 | 0.233 | 0.089712 | -0.06276 | 123.3875 | 123.2782 | 123.4388 | 66.9402 | -123.4813 | 123.3159 | 123.4433 | 123.2908 | 66.9391 | -123.6357
347.25 | 123.4909 | -66.9342 | 56.456 | 0.049183 | -0.017963 | -0.0018439 | 0.052327 | -0.005069 | 0.052569 | 0.066374 | -0.0031524 | -0.0037179 | 0.060632 | 0.034157 | 0.056307 | -66.9075 | 0.010564 | -66.9017 | 56.4579 | 56.3303 | 56.5091 | -67.0527 | -66.9397 | -0.00422 | -66.9788 | 56.3908 | 56.5137 | 56.3703 | -67.2118 | -0.11852 | 0.001872 | 0.026691 | 0.032538 | 0.15106 | -0.1257 | 0.053148 | -0.27757 | -0.065152 | -0.005486 | -0.04457 | 0.233 | 0.057668 | -0.085646 | 123.3921 | 123.2645 | 123.4433 | 66.9448 | -123.5087 | 123.325 | 123.4479 | 123.3046 | 66.93 | -123.6678
348.2344 | 123.5458 | -66.893 | 56.4606 | 0.064445 | -0.016895 | -0.0018439 | 0.052327 | -0.005069 | 0.052569 | 0.066374 | -0.0042204 | -0.0037179 | 0.058496 | 0.034157 | 0.056307 | -66.9121 | 0.010564 | -66.8925 | 56.4487 | 56.3394 | 56.5091 | -67.0481 | -66.9397 | -0.00422 | -66.9834 | 56.3954 | 56.5137 | 56.3703 | -67.2118 | -0.15514 | -0.011862 | -0.019086 | 0.000495 | 0.15563 | -0.12112 | 0.048571 | -0.31876 | -0.065151 | -0.046685 | -0.090348 | 0.22842 | 0.053091 | -0.090223 | 123.3417 | 123.2325 | 123.4021 | 66.9036 | -123.5087 | 123.2884 | 123.4067 | 123.2634 | 66.8888 | -123.6723
349.2344 | 123.5229 | -66.9205 | 56.4835 | 0.064445 | -0.016895 | -0.00077494 | 0.051259 | -0.006137 | 0.051501 | 0.051113 | -0.0020844 | -0.0047869 | 0.058496 | 0.033088 | 0.056307 | -66.8938 | 0.005985 | -66.9017 | 56.4624 | 56.3394 | 56.5137 | -67.039 | -66.9397 | -0.008798 | -66.9834 | 56.3908 | 56.5137 | 56.3703 | -67.2118 | -0.11852 | -0.021014 | 0.026694 | 0.018805 | 0.13732 | -0.14401 | 0.030261 | -0.2913 | -0.092617 | -0.019219 | -0.062882 | 0.22842 | 0.030203 | -0.11311 | 123.3829 | 123.2599 | 123.4342 | 66.9265 | -123.5224 | 123.3113 | 123.4341 | 123.2908 | 66.9117 | -123.6952
350.2344 | 123.5275 | -66.8976 | 56.4651 | 0.049183 | -0.016895 | -0.00077494 | 0.052327 | -0.006137 | 0.052569 | 0.081635 | -0.0031524 | -0.0026499 | 0.058496 | 0.034157 | 0.057375 | -66.8984 | 0.010564 | -66.8971 | 56.4579 | 56.344 | 56.5137 | -67.0481 | -66.9305 | -0.00422 | -66.9788 | 56.3908 | 56.5137 | 56.3658 | -67.2118 | -0.15056 | -0.007283 | -0.000773 | 0.000495 | 0.15106 | -0.12112 | 0.048571 | -0.31419 | -0.074307 | -0.03295 | -0.081191 | 0.233 | 0.048513 | -0.09938 | 123.3554 | 123.2416 | 123.4113 | 66.9081 | -123.5133 | 123.2884 | 123.4112 | 123.2634 | 66.8934 | -123.6769
351.2344 | 123.5458 | -66.9205 | 56.456 | 0.064445 | -0.016895 | -0.00077494 | 0.052327 | -0.006137 | 0.052569 | 0.081635 | -0.0010164 | -0.0037179 | 0.058496 | 0.035225 | 0.056307 | -66.8938 | -0.007751 | -66.8971 | 56.4624 | 56.3257 | 56.5091 | -67.0298 | -66.9397 | -0.008798 | -66.9788 | 56.3908 | 56.5091 | 56.3749 | -67.2072 | -0.10936 | 0.006451 | 0.026694 | 0.023383 | 0.13274 | -0.13028 | 0.053148 | -0.28672 | -0.065152 | -0.019219 | -0.058303 | 0.22842 | 0.053089 | -0.081068 | 123.3829 | 123.2462 | 123.4296 | 66.9127 | -123.4858 | 123.3113 | 123.4296 | 123.2954 | 66.9117 | -123.6632
352.25 | 123.4909 | -66.9159 | 56.4514 | 0.064445 | -0.019031 | 0.00029306 | 0.051259 | -0.007206 | 0.052569 | 0.081635 | -0.0031524 | -0.0037179 | 0.057427 | 0.035225 | 0.056307 | -66.8984 | 0.001407 | -66.8879 | 56.4624 | 56.3349 | 56.5137 | -67.039 | -66.9305 | -0.008798 | -66.9834 | 56.3908 | 56.5091 | 56.3658 | -67.2072 | -0.12309 | 0.011029 | 0.017538 | 0.027962 | 0.15105 | -0.11655 | 0.062304 | -0.2913 | -0.060574 | -0.014639 | -0.067459 | 0.22384 | 0.057667 | -0.085647 | 123.3783 | 123.2508 | 123.4296 | 66.9173 | -123.4904 | 123.3067 | 123.425 | 123.2817 | 66.9071 | -123.6586
353.2344 | 123.5458 | -66.8838 | 56.456 | 0.064445 | -0.019031 | 0.00029306 | 0.050191 | -0.006137 | 0.051501 | 0.066374 | -0.0031524 | -0.0058549 | 0.059564 | 0.034157 | 0.057375 | -66.8938 | 0.005985 | -66.8925 | 56.4533 | 56.3486 | 56.5137 | -67.0344 | -66.9351 | -0.008798 | -66.9788 | 56.4 | 56.5182 | 56.3887 | -67.2163 | -0.15056 | -0.002706 | -0.009927 | -0.00866 | 0.1419 | -0.10739 | 0.057726 | -0.3325 | -0.055995 | -0.051262 | -0.094924 | 0.23757 | 0.062246 | -0.067332 | 123.3371 | 123.2325 | 123.3976 | 66.8898 | -123.4904 | 123.2838 | 123.4021 | 123.2725 | 66.8751 | -123.6723
354.2344 | 123.5413 | -66.9067 | 56.4377 | 0.064445 | -0.0201 | -0.00077494 | 0.046985 | -0.006137 | 0.053638 | 0.081635 | -0.0020844 | -0.0037179 | 0.057427 | 0.035225 | 0.056307 | -66.9029 | 0.001407 | -66.8971 | 56.4624 | 56.344 | 56.5183 | -67.0436 | -66.9305 | -0.013377 | -66.9788 | 56.3863 | 56.5137 | 56.3795 | -67.2163 | -0.13683 | 0.024762 | 0.003804 | 0.00965 | 0.14648 | -0.093658 | 0.080616 | -0.30961 | -0.05142 | -0.023795 | -0.072036 | 0.23757 | 0.075979 | -0.058178 | 123.3692 | 123.2508 | 123.425 | 66.9081 | -123.4812 | 123.293 | 123.4204 | 123.2862 | 66.8934 | -123.654
355.2344 | 123.5184 | -66.9205 | 56.4285 | 0.033921 | -0.017963 | -0.00077494 | 0.051259 | -0.006137 | 0.051501 | 0.081635 | -0.0042204 | -0.0047869 | 0.057427 | 0.034157 | 0.057375 | -66.8938 | -0.007751 | -66.8925 | 56.4533 | 56.3303 | 56.5183 | -67.0344 | -66.9351 | -0.017956 | -66.9834 | 56.3954 | 56.5228 | 56.3841 | -67.2026 | -0.11394 | 0.02476 | 0.026694 | 0.027961 | 0.1419 | -0.098239 | 0.089771 | -0.28214 | -0.033108 | -0.014641 | -0.062882 | 0.21926 | 0.094291 | -0.044445 | 123.3738 | 123.2508 | 123.4388 | 66.9127 | -123.4629 | 123.3159 | 123.4433 | 123.3046 | 66.9025 | -123.6311
356.2344 | 123.5413 | -66.9022 | 56.4651 | 0.049183 | -0.019031 | -0.0029119 | 0.051259 | -0.005069 | 0.052569 | 0.051113 | -0.0020844 | -0.0047869 | 0.058496 | 0.035225 | 0.056307 | -66.8938 | 0.001407 | -66.8879 | 56.4624 | 56.3349 | 56.5183 | -67.0436 | -66.9305 | -0.013377 | -66.9834 | 56.4 | 56.5137 | 56.3703 | -67.198 | -0.1414 | -0.002704 | 0.008384 | 0.014229 | 0.15563 | -0.13028 | 0.05315 | -0.29587 | -0.06515 | -0.028372 | -0.081192 | 0.21468 | 0.048513 | -0.094801 | 123.3646 | 123.237 | 123.4205 | 66.9036 | -123.5087 | 123.3022 | 123.4158 | 123.2725 | 66.8888 | -123.6632
357.25 | 123.5001 | -66.9296 | 56.456 | 0.033921 | -0.017963 | -0.00077494 | 0.051259 | -0.006137 | 0.051501 | 0.051113 | -0.0042204 | -0.0026499 | 0.056359 | 0.035225 | 0.057375 | -66.8984 | -0.003172 | -66.8925 | 56.4533 | 56.3394 | 56.5137 | -67.0344 | -66.9305 | -0.008798 | -66.9788 | 56.3863 | 56.5182 | 56.3887 | -67.2026 | -0.10478 | -0.002706 | 0.03127 | 0.037116 | 0.1419 | -0.11655 | 0.057726 | -0.27299 | -0.069731 | -0.000907 | -0.049148 | 0.22384 | 0.062246 | -0.067332 | 123.3829 | 123.2691 | 123.4433 | 66.9265 | -123.4904 | 123.3159 | 123.4479 | 123.3183 | 66.9208 | -123.6586
358.2344 | 123.5092 | -66.9113 | 56.4697 | 0.079707 | -0.016895 | -0.0029119 | 0.051259 | -0.004001 | 0.051501 | 0.066374 | -0.0010164 | -0.0037179 | 0.057427 | 0.036293 | 0.056307 | -66.8938 | -0.003172 | -66.8925 | 56.467 | 56.3486 | 56.5183 | -67.039 | -66.9351 | -0.013377 | -66.9742 | 56.3863 | 56.5137 | 56.3887 | -67.2026 | -0.12767 | -0.002704 | 0.017539 | 0.018806 | 0.14648 | -0.12112 | 0.048572 | -0.2913 | -0.083464 | -0.023796 | -0.06288 | 0.22841 | 0.043935 | -0.081065 | 123.3783 | 123.2599 | 123.4296 | 66.9081 | -123.5087 | 123.2976 | 123.425 | 123.3 | 66.8979 | -123.6723
359.2344 | 123.5001 | -66.9113 | 56.4606 | 0.049183 | -0.019031 | -0.0029119 | 0.051259 | -0.006137 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.058496 | 0.036293 | 0.057375 | -66.8984 | -0.007751 | -66.8925 | 56.4624 | 56.344 | 56.5137 | -67.0436 | -66.926 | -0.022535 | -66.9696 | 56.3863 | 56.5137 | 56.3887 | -67.2118 | -0.13225 | 0.001874 | 0.01296 | 0.018806 | 0.15105 | -0.11655 | 0.053149 | -0.30045 | -0.074308 | -0.014638 | -0.058301 | 0.24215 | 0.053091 | -0.071909 | 123.3738 | 123.2553 | 123.425 | 66.9036 | -123.5041 | 123.2976 | 123.425 | 123.3 | 66.8888 | -123.6723
360.2344 | 123.5275 | -66.8976 | 56.456 | 0.049183 | -0.019031 | -0.0018439 | 0.050191 | -0.006137 | 0.052569 | 0.066374 | -0.0031524 | -0.0026499 | 0.056359 | 0.036293 | 0.057375 | -66.8846 | -0.003172 | -66.8925 | 56.4579 | 56.3349 | 56.5183 | -67.0298 | -66.926 | -0.017956 | -66.9742 | 56.3954 | 56.5182 | 56.3841 | -67.2118 | -0.13225 | 0.001872 | 0.012962 | 0.005073 | 0.13732 | -0.12113 | 0.062305 | -0.31419 | -0.060574 | -0.028371 | -0.076613 | 0.23757 | 0.062246 | -0.071911 | 123.3554 | 123.2325 | 123.4159 | 66.8944 | -123.4858 | 123.293 | 123.4158 | 123.2817 | 66.8796 | -123.6678
361.2344 | 123.5229 | -66.8976 | 56.4697 | 0.064445 | -0.017963 | -0.0018439 | 0.049122 | -0.006137 | 0.051501 | 0.051113 | -0.0031524 | -0.0026499 | 0.059564 | 0.036293 | 0.057375 | -66.8938 | 0.001407 | -66.8879 | 56.4716 | 56.344 | 56.5137 | -67.0573 | -66.926 | -0.022535 | -66.9742 | 56.3954 | 56.5091 | 56.3795 | -67.2026 | -0.15972 | 0.001874 | 0.003806 | 0.009651 | 0.16937 | -0.1257 | 0.043993 | -0.30503 | -0.074307 | -0.028371 | -0.076613 | 0.22841 | 0.039356 | -0.090222 | 123.3692 | 123.2416 | 123.4113 | 66.899 | -123.527 | 123.293 | 123.4067 | 123.2771 | 66.875 | -123.6723
362.2344 | 123.5413 | -66.9159 | 56.4377 | 0.064445 | -0.019031 | -0.00077494 | 0.052327 | -0.005069 | 0.051501 | 0.051113 | -0.0010164 | -0.0037179 | 0.057427 | 0.034157 | 0.057375 | -66.8892 | -0.007751 | -66.8925 | 56.4624 | 56.3394 | 56.5229 | -67.0252 | -66.926 | -0.027113 | -66.9742 | 56.3954 | 56.5182 | 56.3932 | -67.2072 | -0.10936 | 0.024762 | 0.026695 | 0.023384 | 0.13274 | -0.098236 | 0.085194 | -0.2913 | -0.042263 | -0.01006 | -0.058302 | 0.23299 | 0.080557 | -0.044442 | 123.3783 | 123.2553 | 123.4388 | 66.9081 | -123.4629 | 123.3113 | 123.4341 | 123.3091 | 66.8888 | -123.6449
363.2344 | 123.5641 | -66.9159 | 56.4651 | 0.079707 | -0.017963 | 0.00029306 | 0.051259 | -0.006137 | 0.050433 | 0.066374 | -0.0020844 | -0.0058549 | 0.055291 | 0.036293 | 0.057375 | -66.8892 | -0.016908 | -66.8925 | 56.4716 | 56.3349 | 56.5183 | -67.0298 | -66.926 | -0.031692 | -66.9696 | 56.4 | 56.5182 | 56.3795 | -67.2118 | -0.11394 | 0.006452 | 0.026695 | 0.023384 | 0.13732 | -0.13028 | 0.05315 | -0.29588 | -0.06515 | -0.01006 | -0.053723 | 0.24215 | 0.053091 | -0.085644 | 123.3875 | 123.2508 | 123.4342 | 66.899 | -123.495 | 123.3159 | 123.4341 | 123.2954 | 66.8842 | -123.6769
364.2344 | 123.5229 | -66.9067 | 56.456 | 0.064445 | -0.019031 | -0.00077494 | 0.052327 | -0.007206 | 0.050433 | 0.066374 | -0.0010164 | -0.0047869 | 0.057427 | 0.036293 | 0.055238 | -66.8892 | -0.012329 | -66.8834 | 56.467 | 56.3486 | 56.5183 | -67.039 | -66.9305 | -0.031692 | -66.9742 | 56.4046 | 56.5182 | 56.3841 | -67.2026 | -0.13225 | 0.011029 | 0.017539 | 0.023385 | 0.15563 | -0.10739 | 0.062305 | -0.29587 | -0.051417 | -0.023795 | -0.067458 | 0.22841 | 0.062246 | -0.071911 | 123.3738 | 123.2553 | 123.425 | 66.8944 | -123.495 | 123.3113 | 123.425 | 123.2908 | 66.875 | -123.6586
365.2344 | 123.5046 | -66.8976 | 56.4514 | 0.064445 | -0.017963 | -0.00077494 | 0.052327 | -0.006137 | 0.050433 | 0.051113 | -0.0020844 | -0.0058549 | 0.057427 | 0.035225 | 0.058443 | -66.8892 | -0.016908 | -66.8879 | 56.4624 | 56.3532 | 56.5229 | -67.0344 | -66.926 | -0.022535 | -66.9742 | 56.3954 | 56.5274 | 56.3887 | -67.2118 | -0.13683 | 0.011029 | 0.008384 | 0.009651 | 0.14648 | -0.098233 | 0.071461 | -0.31419 | -0.055996 | -0.028371 | -0.076613 | 0.23757 | 0.075981 | -0.062754 | 123.36 | 123.2508 | 123.4205 | 66.8807 | -123.4858 | 123.293 | 123.425 | 123.2862 | 66.875 | -123.6632
366.2344 | 123.5001 | -66.9067 | 56.4606 | 0.049183 | -0.016895 | -0.00077494 | 0.051259 | -0.005069 | 0.051501 | 0.051113 | -0.0020844 | -0.0037179 | 0.057427 | 0.037362 | 0.058443 | -66.8938 | -0.016908 | -66.8879 | 56.4624 | 56.3623 | 56.5229 | -67.0207 | -66.9168 | -0.031692 | -66.9834 | 56.4092 | 56.5228 | 56.3841 | -67.2072 | -0.11393 | 0.001874 | 0.012961 | 0.018806 | 0.13274 | -0.09823 | 0.062306 | -0.30045 | -0.051415 | -0.010059 | -0.076615 | 0.22384 | 0.062248 | -0.076488 | 123.3692 | 123.2691 | 123.4296 | 66.8898 | -123.4812 | 123.3159 | 123.4296 | 123.2908 | 66.875 | -123.6678
367.25 | 123.6191 | -66.8838 | 56.4148 | 0.049183 | -0.021168 | -0.0029119 | 0.050191 | -0.007206 | 0.052569 | 0.051113 | -0.0031524 | -0.0037179 | 0.057427 | 0.037362 | 0.055238 | -66.8846 | -0.026065 | -66.8742 | 56.467 | 56.3486 | 56.5183 | -67.0115 | -66.9214 | -0.027113 | -66.9742 | 56.4046 | 56.5366 | 56.3841 | -67.2118 | -0.12766 | 0.052228 | -0.000771 | 0.009653 | 0.13732 | -0.066191 | 0.1035 | -0.32792 | -0.010218 | -0.037526 | -0.090346 | 0.23757 | 0.12176 | -0.030712 | 123.3509 | 123.2325 | 123.4021 | 66.8578 | -123.4263 | 123.2884 | 123.4204 | 123.2679 | 66.8567 | -123.6266
368.2344 | 123.4589 | -66.9296 | 56.4606 | 0.064445 | -0.016895 | -0.0029119 | 0.051259 | -0.004001 | 0.052569 | 0.066374 | -0.0010164 | -0.0026499 | 0.059564 | 0.036293 | 0.057375 | -66.8892 | -0.021486 | -66.8834 | 56.4716 | 56.3532 | 56.5183 | -67.0481 | -66.926 | -0.027113 | -66.9788 | 56.4 | 56.5274 | 56.3795 | -67.2026 | -0.11852 | 0.01103 | 0.040427 | 0.046273 | 0.16479 | -0.10739 | 0.057728 | -0.27299 | -0.060572 | 0.003672 | -0.049148 | 0.22384 | 0.066826 | -0.081066 | 123.4012 | 123.2828 | 123.4479 | 66.9081 | -123.5087 | 123.3296 | 123.457 | 123.3091 | 66.9025 | -123.6632
369.2344 | 123.5092 | -66.9113 | 56.4697 | 0.049183 | -0.017963 | -0.0018439 | 0.051259 | -0.007206 | 0.052569 | 0.096896 | -0.0031524 | -0.0037179 | 0.059564 | 0.036293 | 0.057375 | -66.8892 | -0.030644 | -66.8834 | 56.4624 | 56.3532 | 56.5275 | -67.039 | -66.9122 | -0.040849 | -66.9742 | 56.4 | 56.5228 | 56.3795 | -67.2026 | -0.12767 | -0.007282 | 0.022117 | 0.027963 | 0.15563 | -0.11654 | 0.057729 | -0.2913 | -0.069728 | -0.000902 | -0.06288 | 0.22841 | 0.053092 | -0.090222 | 123.3738 | 123.2645 | 123.4388 | 66.8807 | -123.5087 | 123.3113 | 123.4341 | 123.2908 | 66.8705 | -123.6723
370.2344 | 123.4955 | -66.9113 | 56.456 | 0.079707 | -0.017963 | -0.0018439 | 0.050191 | -0.006137 | 0.051501 | 0.081635 | -0.0031524 | -0.0047869 | 0.057427 | 0.036293 | 0.056307 | -66.8846 | -0.021486 | -66.8879 | 56.4716 | 56.3394 | 56.5229 | -67.0344 | -66.926 | -0.036271 | -66.9696 | 56.4 | 56.5228 | 56.3795 | -67.2026 | -0.12309 | 0.015607 | 0.026695 | 0.023384 | 0.14648 | -0.11655 | 0.066883 | -0.2913 | -0.055995 | -0.014638 | -0.058301 | 0.23299 | 0.066825 | -0.076489 | 123.3829 | 123.2508 | 123.4342 | 66.8898 | -123.4904 | 123.3113 | 123.4341 | 123.2908 | 66.875 | -123.6586
371.2344 | 123.4726 | -66.925 | 56.456 | 0.064445 | -0.015826 | -0.0029119 | 0.050191 | -0.005069 | 0.050433 | 0.096896 | -0.0042204 | -0.0037179 | 0.056359 | 0.036293 | 0.056307 | -66.8846 | -0.035222 | -66.8788 | 56.4716 | 56.3578 | 56.5275 | -67.039 | -66.9214 | -0.036271 | -66.9788 | 56.3954 | 56.5274 | 56.3887 | -67.2072 | -0.11394 | 0.015607 | 0.040428 | 0.046274 | 0.16021 | -0.098232 | 0.071462 | -0.28214 | -0.060574 | 0.003673 | -0.053725 | 0.22842 | 0.071403 | -0.067332 | 123.3966 | 123.2828 | 123.4525 | 66.8898 | -123.495 | 123.3205 | 123.4524 | 123.3137 | 66.8888 | -123.6632
372.25 | 123.5825 | -66.8701 | 56.4331 | 0.079707 | -0.016895 | -0.0018439 | 0.051259 | -0.006137 | 0.051501 | 0.051113 | -0.0042204 | -0.0026499 | 0.057427 | 0.037362 | 0.056307 | -66.8846 | -0.026065 | -66.8788 | 56.467 | 56.3623 | 56.5183 | -67.0161 | -66.9122 | -0.045428 | -66.9788 | 56.4046 | 56.5274 | 56.3932 | -67.2026 | -0.14598 | 0.033918 | -0.014504 | -0.008658 | 0.13732 | -0.070764 | 0.085194 | -0.33249 | -0.028528 | -0.042101 | -0.10866 | 0.22384 | 0.094292 | -0.039864 | 123.3371 | 123.2325 | 123.3884 | 66.8441 | -123.4492 | 123.2747 | 123.3975 | 123.2634 | 66.8247 | -123.6357
373.2344 | 123.4589 | -66.9388 | 56.456 | 0.049183 | -0.017963 | -0.00077494 | 0.051259 | -0.007206 | 0.052569 | 0.066374 | -0.0031524 | -0.0058549 | 0.057427 | 0.035225 | 0.055238 | -66.8846 | -0.026065 | -66.8879 | 56.467 | 56.3532 | 56.5229 | -67.0436 | -66.9122 | -0.040849 | -66.9696 | 56.4092 | 56.5274 | 56.3978 | -67.2026 | -0.10478 | 0.011029 | 0.054161 | 0.05085 | 0.15563 | -0.10281 | 0.066883 | -0.26383 | -0.046838 | 0.026564 | -0.030835 | 0.23299 | 0.071403 | -0.058175 | 123.4058 | 123.292 | 123.4617 | 66.9127 | -123.4996 | 123.3479 | 123.4662 | 123.3366 | 66.8979 | -123.6586
374.2344 | 123.4955 | -66.9067 | 56.4514 | 0.079707 | -0.019031 | -0.0029119 | 0.049122 | -0.006137 | 0.051501 | 0.051113 | -0.0042204 | -0.0037179 | 0.058496 | 0.037362 | 0.057375 | -66.8846 | -0.035222 | -66.8742 | 56.467 | 56.3623 | 56.5275 | -67.0298 | -66.9122 | -0.050007 | -66.9696 | 56.4046 | 56.5274 | 56.4024 | -67.2026 | -0.12309 | 0.015607 | 0.022117 | 0.032541 | 0.15563 | -0.089075 | 0.07604 | -0.29587 | -0.046839 | -0.00548 | -0.062879 | 0.23299 | 0.075981 | -0.049018 | 123.3738 | 123.2691 | 123.4342 | 66.8715 | -123.4812 | 123.3113 | 123.4341 | 123.3091 | 66.8567 | -123.654
375.2344 | 123.4955 | -66.9159 | 56.4606 | 0.049183 | -0.017963 | -0.0029119 | 0.049122 | -0.004001 | 0.051501 | 0.051113 | -0.0031524 | -0.0047869 | 0.055291 | 0.036293 | 0.057375 | -66.8938 | -0.026065 | -66.8788 | 56.467 | 56.3349 | 56.5275 | -67.0252 | -66.9122 | -0.040849 | -66.9742 | 56.3954 | 56.5228 | 56.4024 | -67.2026 | -0.10936 | 0.006452 | 0.022117 | 0.037119 | 0.14647 | -0.1257 | 0.066885 | -0.28672 | -0.065151 | 0.003676 | -0.058302 | 0.22841 | 0.062248 | -0.058173 | 123.3829 | 123.2508 | 123.4433 | 66.8898 | -123.4858 | 123.3113 | 123.4387 | 123.3183 | 66.875 | -123.6632
376.2344 | 123.468 | -66.9205 | 56.456 | 0.049183 | -0.017963 | -0.0029119 | 0.051259 | -0.005069 | 0.052569 | 0.051113 | -0.0020844 | -0.0037179 | 0.058496 | 0.037362 | 0.057375 | -66.8846 | -0.035222 | -66.8788 | 56.467 | 56.3532 | 56.5275 | -67.039 | -66.9214 | -0.050007 | -66.9696 | 56.4046 | 56.5228 | 56.3749 | -67.2026 | -0.11852 | 0.011029 | 0.03585 | 0.041696 | 0.16021 | -0.10281 | 0.071462 | -0.28214 | -0.051417 | -0.000905 | -0.049146 | 0.23299 | 0.066825 | -0.081068 | 123.3875 | 123.2737 | 123.4479 | 66.8852 | -123.495 | 123.325 | 123.4433 | 123.2954 | 66.8705 | -123.6586
377.25 | 123.5596 | -66.8655 | 56.4331 | 0.079707 | -0.016895 | -0.00077494 | 0.050191 | -0.005069 | 0.051501 | 0.035852 | -0.0020844 | -0.0037179 | 0.057427 | 0.03843 | 0.056307 | -66.8892 | -0.035222 | -66.8788 | 56.4716 | 56.3486 | 56.5183 | -67.0252 | -66.9122 | -0.054586 | -66.9742 | 56.4046 | 56.5274 | 56.3887 | -67.2072 | -0.15971 | 0.038496 | -0.023659 | -0.013235 | 0.14647 | -0.084501 | 0.085194 | -0.34165 | -0.028528 | -0.046678 | -0.10866 | 0.23299 | 0.094292 | -0.044443 | 123.3371 | 123.2141 | 123.3838 | 66.8303 | -123.4584 | 123.2701 | 123.3929 | 123.2542 | 66.811 | -123.6403
378.2344 | 123.4863 | -66.8976 | 56.4835 | 0.049183 | -0.016895 | -0.0018439 | 0.051259 | -0.006137 | 0.050433 | 0.066374 | -0.0020844 | -0.0026499 | 0.058496 | 0.036293 | 0.057375 | -66.8846 | -0.035222 | -66.8788 | 56.4716 | 56.3532 | 56.5229 | -67.0207 | -66.9168 | -0.050007 | -66.9696 | 56.4046 | 56.5228 | 56.3887 | -67.1935 | -0.12309 | -0.011858 | 0.012962 | 0.018808 | 0.1419 | -0.13028 | 0.039418 | -0.29587 | -0.078882 | -0.019214 | -0.072034 | 0.22384 | 0.03936 | -0.094797 | 123.3692 | 123.2508 | 123.4205 | 66.8624 | -123.5041 | 123.3022 | 123.4204 | 123.2862 | 66.8476 | -123.6769
379.2344 | 123.4909 | -66.8976 | 56.4423 | 0.049183 | -0.017963 | -0.0029119 | 0.049122 | -0.007206 | 0.051501 | 0.051113 | -0.0031524 | -0.0026499 | 0.058496 | 0.037362 | 0.057375 | -66.8846 | -0.030644 | -66.8788 | 56.4716 | 56.3532 | 56.5183 | -67.0344 | -66.9031 | -0.050007 | -66.965 | 56.4092 | 56.532 | 56.3612 | -67.198 | -0.13683 | 0.02934 | 0.012962 | 0.018808 | 0.15563 | -0.089078 | 0.076038 | -0.30045 | -0.033105 | -0.005478 | -0.067455 | 0.23299 | 0.089715 | -0.081071 | 123.3692 | 123.2508 | 123.4159 | 66.8669 | -123.4767 | 123.3067 | 123.4296 | 123.2588 | 66.8476 | -123.6403
380.2344 | 123.5092 | -66.9067 | 56.4423 | 0.049183 | -0.019031 | -0.0029119 | 0.049122 | -0.005069 | 0.051501 | 0.096896 | -0.0020844 | -0.0026499 | 0.058496 | 0.037362 | 0.056307 | -66.8846 | -0.030644 | -66.8834 | 56.467 | 56.3623 | 56.532 | -67.0298 | -66.9214 | -0.045428 | -66.965 | 56.4137 | 56.5228 | 56.3337 | -67.1935 | -0.12309 | 0.024762 | 0.022117 | 0.023385 | 0.14648 | -0.07992 | 0.089774 | -0.28672 | -0.028527 | -0.014638 | -0.0583 | 0.22842 | 0.080558 | -0.10854 | 123.3738 | 123.2691 | 123.4388 | 66.8761 | -123.4721 | 123.3205 | 123.4296 | 123.2405 | 66.8613 | -123.6357
381.2344 | 123.587 | -66.8655 | 56.4423 | 0.033921 | -0.016895 | -0.0029119 | 0.049122 | -0.004001 | 0.052569 | 0.051113 | -0.0031524 | -0.0047869 | 0.058496 | 0.036293 | 0.056307 | -66.8846 | -0.030644 | -66.8788 | 56.4716 | 56.3578 | 56.5275 | -67.0344 | -66.9076 | -0.040849 | -66.9696 | 56.4 | 56.532 | 56.3978 | -67.2026 | -0.16887 | 0.02934 | -0.019081 | -0.013235 | 0.15563 | -0.084499 | 0.085195 | -0.33707 | -0.042262 | -0.042099 | -0.10408 | 0.23299 | 0.089715 | -0.044442 | 123.3371 | 123.2233 | 123.393 | 66.8349 | -123.4767 | 123.2655 | 123.3975 | 123.2634 | 66.8247 | -123.6449
382.25 | 123.5458 | -66.8518 | 56.4743 | 0.049183 | -0.019031 | -0.0018439 | 0.051259 | -0.004001 | 0.051501 | 0.081635 | -0.0031524 | -0.0037179 | 0.057427 | 0.037362 | 0.056307 | -66.8846 | -0.039801 | -66.8788 | 56.467 | 56.3623 | 56.532 | -67.0298 | -66.9122 | -0.045428 | -66.9696 | 56.4 | 56.5366 | 56.3429 | -67.2026 | -0.17802 | -0.007281 | -0.032814 | -0.026968 | 0.15105 | -0.11196 | 0.057731 | -0.3508 | -0.074305 | -0.060411 | -0.11781 | 0.23299 | 0.062251 | -0.13143 | 123.3188 | 123.2141 | 123.3838 | 66.812 | -123.5041 | 123.2518 | 123.3884 | 123.1947 | 66.8064 | -123.6769
383.25 | 123.5458 | -66.8655 | 56.488 | 0.079707 | -0.017963 | -0.00077494 | 0.051259 | -0.002933 | 0.050433 | 0.066374 | -0.0010164 | -0.0026499 | 0.056359 | 0.036293 | 0.056307 | -66.8846 | -0.044379 | -66.8742 | 56.4579 | 56.3623 | 56.5275 | -67.0252 | -66.9122 | -0.045428 | -66.9605 | 56.4 | 56.5274 | 56.3841 | -67.198 | -0.15971 | -0.030171 | -0.019081 | -0.008657 | 0.15105 | -0.1257 | 0.039419 | -0.33249 | -0.088038 | -0.046678 | -0.094919 | 0.23757 | 0.03936 | -0.10395 | 123.3234 | 123.2279 | 123.393 | 66.8212 | -123.5133 | 123.2655 | 123.3929 | 123.2496 | 66.8201 | -123.6861
384.2344 | 123.5001 | -66.9113 | 56.4697 | 0.018659 | -0.017963 | -0.0029119 | 0.049122 | -0.004001 | 0.051501 | 0.035852 | -0.0042204 | -0.0047869 | 0.059564 | 0.037362 | 0.056307 | -66.88 | -0.030644 | -66.8834 | 56.467 | 56.3578 | 56.5275 | -67.0436 | -66.9122 | -0.040849 | -66.9696 | 56.4092 | 56.5366 | 56.3337 | -67.2026 | -0.13225 | -0.002704 | 0.031274 | 0.027963 | 0.16021 | -0.11196 | 0.057729 | -0.2913 | -0.060571 | -0.000902 | -0.058301 | 0.23299 | 0.066828 | -0.13601 | 123.3783 | 123.2691 | 123.4388 | 66.8807 | -123.5133 | 123.3205 | 123.4479 | 123.245 | 66.8705 | -123.6723
385.2344 | 123.555 | -66.9022 | 56.4377 | 0.064445 | -0.0201 | -0.0029119 | 0.050191 | -0.006137 | 0.052569 | 0.081635 | -0.0010164 | -0.0047869 | 0.057427 | 0.037362 | 0.055238 | -66.88 | -0.030644 | -66.8788 | 56.4716 | 56.3669 | 56.532 | -67.0344 | -66.9076 | -0.045428 | -66.9742 | 56.4092 | 56.5274 | 56.3749 | -67.198 | -0.13225 | 0.033918 | 0.022119 | 0.023386 | 0.15563 | -0.070763 | 0.094352 | -0.29587 | -0.028527 | -0.005478 | -0.072035 | 0.22384 | 0.089714 | -0.062757 | 123.3738 | 123.2691 | 123.4342 | 66.8715 | -123.4721 | 123.3113 | 123.4296 | 123.2771 | 66.8567 | -123.6357
386.2344 | 123.5641 | -66.8701 | 56.4285 | 0.049183 | -0.019031 | -0.0029119 | 0.048054 | -0.005069 | 0.051501 | 0.081635 | -0.0020844 | -0.0037179 | 0.057427 | 0.037362 | 0.056307 | -66.88 | -0.035222 | -66.8788 | 56.4716 | 56.344 | 56.5229 | -67.0115 | -66.9168 | -0.040849 | -66.9742 | 56.4092 | 56.5274 | 56.3658 | -67.2026 | -0.1414 | 0.043073 | -0.009925 | -0.008658 | 0.13274 | -0.084503 | 0.094349 | -0.33249 | -0.019372 | -0.04668 | -0.10408 | 0.22841 | 0.098869 | -0.062759 | 123.3417 | 123.2141 | 123.393 | 66.8349 | -123.44 | 123.2793 | 123.3975 | 123.2359 | 66.8293 | -123.6311
387.25 | 123.6008 | -66.8747 | 56.4285 | 0.064445 | -0.0201 | -0.0018439 | 0.050191 | -0.004001 | 0.052569 | 0.066374 | -0.0042204 | -0.0015819 | 0.057427 | 0.037362 | 0.056307 | -66.8846 | -0.035222 | -66.8879 | 56.467 | 56.3532 | 56.5229 | -67.0298 | -66.9122 | -0.050007 | -66.965 | 56.4046 | 56.5228 | 56.3978 | -67.1935 | -0.15513 | 0.038495 | -0.009926 | -0.013237 | 0.1419 | -0.075345 | 0.094349 | -0.31876 | -0.023951 | -0.037523 | -0.090343 | 0.22842 | 0.094291 | -0.030709 | 123.3417 | 123.2279 | 123.3976 | 66.8395 | -123.4584 | 123.2793 | 123.3975 | 123.2725 | 66.8247 | -123.622
388.25 | 123.6374 | -66.8243 | 56.4651 | 0.049183 | -0.017963 | -0.0018439 | 0.050191 | -0.004001 | 0.051501 | 0.066374 | -0.0020844 | -0.0026499 | 0.058496 | 0.03843 | 0.057375 | -66.88 | -0.035222 | -66.8788 | 56.4716 | 56.3532 | 56.532 | -67.0207 | -66.9122 | -0.045428 | -66.965 | 56.4046 | 56.5274 | 56.32 | -67.2026 | -0.19633 | 0.006452 | -0.055701 | -0.054434 | 0.1419 | -0.11197 | 0.066886 | -0.37827 | -0.060572 | -0.087877 | -0.1407 | 0.23757 | 0.062248 | -0.14517 | 123.2959 | 123.1775 | 123.3564 | 66.7891 | -123.4858 | 123.2289 | 123.3517 | 123.1443 | 66.7789 | -123.6678
389.2344 | 123.6053 | -66.8747 | 56.4468 | 0.049183 | -0.017963 | -0.0029119 | 0.049122 | -0.005069 | 0.051501 | 0.051113 | -0.0031524 | -0.0037179 | 0.058496 | 0.03843 | 0.055238 | -66.88 | -0.030644 | -66.8788 | 56.4624 | 56.3623 | 56.5275 | -67.039 | -66.9122 | -0.031692 | -66.9696 | 56.4092 | 56.532 | 56.3887 | -67.2072 | -0.16429 | 0.015607 | -0.005347 | -0.00408 | 0.16021 | -0.084497 | 0.080618 | -0.33249 | -0.037682 | -0.037523 | -0.094922 | 0.23757 | 0.085138 | -0.058176 | 123.3371 | 123.237 | 123.4022 | 66.8441 | -123.4858 | 123.2839 | 123.4067 | 123.2634 | 66.843 | -123.654
390.2344 | 123.5092 | -66.8838 | 56.4331 | 0.049183 | -0.019031 | -0.0029119 | 0.049122 | -0.005069 | 0.052569 | 0.051113 | -0.0020844 | -0.0026499 | 0.057427 | 0.037362 | 0.056307 | -66.8846 | -0.035222 | -66.8788 | 56.4716 | 56.3532 | 56.5275 | -67.0298 | -66.9076 | -0.040849 | -66.9696 | 56.4 | 56.532 | 56.3795 | -67.198 | -0.14598 | 0.038496 | -0.000771 | 0.005075 | 0.15105 | -0.079922 | 0.094351 | -0.31418 | -0.033106 | -0.023789 | -0.085767 | 0.22842 | 0.098871 | -0.0536 | 123.3555 | 123.237 | 123.4113 | 66.8486 | -123.4629 | 123.2838 | 123.4158 | 123.2634 | 66.843 | -123.6311
391.2344 | 123.5321 | -66.9067 | 56.4468 | 0.049183 | -0.017963 | -0.0050489 | 0.048054 | -0.004001 | 0.051501 | 0.051113 | -0.0020844 | -0.0026499 | 0.058496 | 0.03843 | 0.056307 | -66.8846 | -0.030644 | -66.8834 | 56.467 | 56.3532 | 56.5275 | -67.0252 | -66.9168 | -0.036271 | -66.965 | 56.4092 | 56.5274 | 56.3612 | -67.2072 | -0.11851 | 0.020185 | 0.022117 | 0.023385 | 0.1419 | -0.093655 | 0.080618 | -0.30045 | -0.037682 | -0.010059 | -0.0583 | 0.24215 | 0.080559 | -0.085648 | 123.3738 | 123.2599 | 123.4342 | 66.8761 | -123.4721 | 123.3159 | 123.4341 | 123.2679 | 66.8705 | -123.654
392.25 | 123.5504 | -66.893 | 56.4468 | 0.064445 | -0.016895 | -0.0018439 | 0.049122 | -0.006137 | 0.051501 | 0.081635 | -0.0052884 | -0.0015819 | 0.058496 | 0.039498 | 0.056307 | -66.8892 | -0.030644 | -66.8834 | 56.4762 | 56.3532 | 56.5275 | -67.0344 | -66.9031 | -0.036271 | -66.965 | 56.4 | 56.532 | 56.2788 | -67.2072 | -0.1414 | 0.029342 | 0.003806 | 0.009652 | 0.15105 | -0.093655 | 0.080618 | -0.31418 | -0.046839 | -0.010056 | -0.072033 | 0.24215 | 0.085138 | -0.16806 | 123.3692 | 123.2462 | 123.4205 | 66.8624 | -123.4812 | 123.293 | 123.425 | 123.1718 | 66.8567 | -123.654
393.25 | 123.5138 | -66.8838 | 56.4926 | 0.079707 | -0.019031 | -0.0018439 | 0.048054 | -0.005069 | 0.051501 | 0.051113 | -0.0031524 | -0.0037179 | 0.057427 | 0.039498 | 0.057375 | -66.8846 | -0.026065 | -66.8788 | 56.4624 | 56.3761 | 56.5275 | -67.0344 | -66.9076 | -0.040849 | -66.965 | 56.4046 | 56.532 | 56.3658 | -67.2026 | -0.15056 | -0.03017 | -0.000771 | 0.005075 | 0.15563 | -0.11654 | 0.034841 | -0.31876 | -0.088038 | -0.023789 | -0.081188 | 0.23757 | 0.039361 | -0.12685 | 123.3463 | 123.2599 | 123.4113 | 66.8578 | -123.527 | 123.2884 | 123.4158 | 123.2496 | 66.843 | -123.6952
394.2344 | 123.5916 | -66.8701 | 56.4148 | 0.049183 | -0.021168 | -0.00077494 | 0.051259 | -0.005069 | 0.050433 | 0.066374 | -0.0020844 | -0.0015819 | 0.057427 | 0.039498 | 0.05417 | -66.8846 | -0.026065 | -66.8834 | 56.467 | 56.3578 | 56.5137 | -67.0298 | -66.9076 | -0.031692 | -66.9696 | 56.4046 | 56.532 | 56.3612 | -67.2026 | -0.15971 | 0.052228 | -0.014504 | -0.013236 | 0.14648 | -0.057033 | 0.098925 | -0.33249 | -0.010218 | -0.037522 | -0.0995 | 0.23299 | 0.11718 | -0.053605 | 123.3371 | 123.2279 | 123.3838 | 66.8441 | -123.4446 | 123.2747 | 123.4021 | 123.2313 | 66.8384 | -123.6174
395.2344 | 123.6008 | -66.861 | 56.4468 | 0.064445 | -0.019031 | -0.0018439 | 0.050191 | -0.005069 | 0.051501 | 0.066374 | -0.0042204 | -0.0037179 | 0.056359 | 0.037362 | 0.05417 | -66.88 | -0.016908 | -66.8788 | 56.4624 | 56.3578 | 56.5229 | -67.0298 | -66.9076 | -0.036271 | -66.9696 | 56.3954 | 56.532 | 56.352 | -67.2026 | -0.16887 | 0.015607 | -0.01908 | -0.017813 | 0.15105 | -0.089076 | 0.076039 | -0.34165 | -0.051418 | -0.046677 | -0.10865 | 0.23299 | 0.085138 | -0.094805 | 123.3234 | 123.2187 | 123.3838 | 66.8441 | -123.4767 | 123.2564 | 123.3929 | 123.213 | 66.8247 | -123.6494
396.2344 | 123.6053 | -66.8701 | 56.4331 | 0.049183 | -0.019031 | -0.0018439 | 0.050191 | -0.006137 | 0.052569 | 0.051113 | -0.0031524 | -0.0037179 | 0.058496 | 0.040567 | 0.056307 | -66.8892 | -0.030644 | -66.8834 | 56.4624 | 56.3532 | 56.532 | -67.0161 | -66.9076 | -0.036271 | -66.9696 | 56.4 | 56.532 | 56.3154 | -67.2072 | -0.14598 | 0.02934 | -0.019082 | -0.013236 | 0.13274 | -0.079922 | 0.09893 | -0.33707 | -0.033106 | -0.037522 | -0.0995 | 0.23757 | 0.098871 | -0.1177 | 123.3326 | 123.2233 | 123.4022 | 66.8395 | -123.4492 | 123.2701 | 123.4021 | 123.1855 | 66.8338 | -123.6403
397.25 | 123.6008 | -66.8838 | 56.4423 | 0.079707 | -0.017963 | -0.0029119 | 0.051259 | -0.005069 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.057427 | 0.03843 | 0.056307 | -66.88 | -0.021486 | -66.8834 | 56.467 | 56.3623 | 56.5275 | -67.0436 | -66.9076 | -0.036271 | -66.965 | 56.3954 | 56.5274 | 56.2834 | -67.2072 | -0.15972 | 0.024762 | 0.003808 | 0.000497 | 0.16021 | -0.07992 | 0.085195 | -0.32334 | -0.046841 | -0.023789 | -0.081188 | 0.24215 | 0.085136 | -0.15891 | 123.3509 | 123.2462 | 123.4113 | 66.8624 | -123.4858 | 123.2793 | 123.4112 | 123.1672 | 66.8476 | -123.6495
398.25 | 123.4863 | -66.8381 | 56.4514 | 0.079707 | -0.019031 | -0.0029119 | 0.051259 | -0.006137 | 0.050433 | 0.096896 | -0.0052884 | -0.0037179 | 0.057427 | 0.037362 | 0.056307 | -66.8846 | -0.026065 | -66.8788 | 56.467 | 56.3578 | 56.532 | -67.0436 | -66.9076 | -0.045428 | -66.9696 | 56.3954 | 56.5274 | 56.2376 | -67.2072 | -0.20549 | 0.015607 | -0.046547 | -0.040701 | 0.16479 | -0.093654 | 0.080619 | -0.36912 | -0.055996 | -0.069565 | -0.13154 | 0.23757 | 0.075981 | -0.21385 | 123.3051 | 123.1958 | 123.3701 | 66.812 | -123.495 | 123.2335 | 123.3655 | 123.0756 | 66.7926 | -123.6586
399.2344 | 123.6099 | -66.8655 | 56.4423 | 0.064445 | -0.019031 | 0.00029306 | 0.049122 | -0.004001 | 0.052569 | 0.066374 | -0.0052884 | -0.0026499 | 0.059564 | 0.03843 | 0.057375 | -66.8846 | -0.016908 | -66.8742 | 56.467 | 56.3623 | 56.5275 | -67.0298 | -66.9031 | -0.054586 | -66.965 | 56.4 | 56.5228 | 56.3291 | -67.2072 | -0.16429 | 0.024762 | -0.019081 | -0.008657 | 0.15563 | -0.07992 | 0.085195 | -0.34165 | -0.042262 | -0.037521 | -0.099498 | 0.24215 | 0.080558 | -0.11312 | 123.3326 | 123.2279 | 123.393 | 66.8486 | -123.4721 | 123.2655 | 123.3884 | 123.1947 | 66.811 | -123.6495
400.2344 | 123.5916 | -66.8564 | 56.4377 | 0.064445 | -0.021168 | -0.0029119 | 0.051259 | -0.005069 | 0.051501 | 0.081635 | -0.0042204 | -0.0037179 | 0.056359 | 0.039498 | 0.057375 | -66.8846 | -0.021486 | -66.8788 | 56.4579 | 56.3578 | 56.5229 | -67.0161 | -66.8985 | -0.063743 | -66.965 | 56.4046 | 56.5274 | 56.2971 | -67.2072 | -0.15971 | 0.020183 | -0.028237 | -0.022391 | 0.13732 | -0.079921 | 0.085194 | -0.35081 | -0.033106 | -0.042098 | -0.10865 | 0.24215 | 0.089714 | -0.14059 | 123.3143 | 123.2141 | 123.3793 | 66.8349 | -123.4538 | 123.261 | 123.3838 | 123.1535 | 66.7926 | -123.6449
401.2344 | 123.6374 | -66.8564 | 56.4468 | 0.064445 | -0.019031 | -0.0018439 | 0.049122 | -0.007206 | 0.049364 | 0.051113 | -0.0031524 | -0.0026499 | 0.056359 | 0.041635 | 0.055238 | -66.88 | -0.016908 | -66.8834 | 56.467 | 56.3578 | 56.532 | -67.0252 | -66.8985 | -0.0729 | -66.9696 | 56.4046 | 56.5411 | 56.3429 | -67.1935 | -0.16887 | 0.020185 | -0.023658 | -0.026969 | 0.1419 | -0.089076 | 0.085197 | -0.33707 | -0.042261 | -0.042098 | -0.11323 | 0.22384 | 0.094295 | -0.10396 | 123.3234 | 123.2141 | 123.3884 | 66.8395 | -123.4721 | 123.261 | 123.3975 | 123.1993 | 66.7835 | -123.6403
402.25 | 123.6237 | -66.8381 | 56.4651 | 0.079707 | -0.021168 | -0.0018439 | 0.051259 | -0.005069 | 0.052569 | 0.096896 | -0.0031524 | -0.00051292 | 0.057427 | 0.037362 | 0.055238 | -66.8755 | -0.021486 | -66.8742 | 56.4762 | 56.3532 | 56.5366 | -67.0207 | -66.8939 | -0.10037 | -66.965 | 56.4092 | 56.5411 | 56.3658 | -67.198 | -0.1826 | 0.011031 | -0.03739 | -0.036123 | 0.14647 | -0.11197 | 0.071464 | -0.35996 | -0.055993 | -0.055829 | -0.12696 | 0.23299 | 0.075984 | -0.09938 | 123.3143 | 123.1913 | 123.3747 | 66.8166 | -123.4858 | 123.2472 | 123.3792 | 123.2038 | 66.7377 | -123.6632
403.25 | 123.587 | -66.8655 | 56.4651 | 0.064445 | -0.0201 | -0.0029119 | 0.049122 | -0.005069 | 0.051501 | 0.081635 | -0.0020844 | -0.0026499 | 0.058496 | 0.03843 | 0.055238 | -66.88 | -0.016908 | -66.8696 | 56.4762 | 56.3578 | 56.5366 | -67.0344 | -66.8847 | -0.11869 | -66.9605 | 56.4092 | 56.532 | 56.3749 | -67.1935 | -0.16887 | 0.011031 | -0.014502 | -0.004078 | 0.16479 | -0.10739 | 0.071464 | -0.32791 | -0.055993 | -0.019206 | -0.094919 | 0.233 | 0.066827 | -0.090223 | 123.3417 | 123.2233 | 123.4022 | 66.8486 | -123.4996 | 123.2747 | 123.3975 | 123.2405 | 66.7469 | -123.6586
404.2344 | 123.6237 | -66.8564 | 56.4468 | 0.033921 | -0.021168 | -0.0029119 | 0.048054 | -0.006137 | 0.052569 | 0.081635 | -0.0031524 | -0.0037179 | 0.059564 | 0.039498 | 0.055238 | -66.8709 | -0.035222 | -66.8696 | 56.4762 | 56.3623 | 56.5366 | -67.0115 | -66.8802 | -0.14158 | -66.9605 | 56.4137 | 56.5366 | 56.3429 | -67.1935 | -0.15513 | 0.029342 | -0.014502 | -0.013234 | 0.14189 | -0.084497 | 0.089775 | -0.33707 | -0.033104 | -0.023783 | -0.10407 | 0.233 | 0.089717 | -0.10396 | 123.3326 | 123.2187 | 123.393 | 66.8212 | -123.4584 | 123.2701 | 123.3929 | 123.1993 | 66.7148 | -123.6403
405.2344 | 123.6008 | -66.8655 | 56.4606 | 0.064445 | -0.0201 | -0.00077494 | 0.048054 | -0.006137 | 0.052569 | 0.066374 | -0.0020844 | -0.0047869 | 0.056359 | 0.040567 | 0.05417 | -66.8663 | -0.030644 | -66.8696 | 56.4808 | 56.3623 | 56.5458 | -67.0252 | -66.8802 | -0.18279 | -66.9513 | 56.4137 | 56.5457 | 56.4024 | -67.1843 | -0.15971 | 0.020187 | -0.000767 | -0.004078 | 0.15563 | -0.09823 | 0.085199 | -0.31876 | -0.046837 | -0.014627 | -0.085762 | 0.23299 | 0.085141 | -0.058173 | 123.3463 | 123.2279 | 123.4113 | 66.8349 | -123.4858 | 123.2793 | 123.4113 | 123.2679 | 66.6828 | -123.6449
406.2344 | 123.5687 | -66.8655 | 56.4743 | 0.049183 | -0.019031 | -0.0029119 | 0.050191 | -0.004001 | 0.051501 | 0.051113 | -0.0031524 | -0.0037179 | 0.056359 | 0.03843 | 0.056307 | -66.8663 | -0.039801 | -66.8559 | 56.4853 | 56.3761 | 56.5412 | -66.9932 | -66.8756 | -0.22858 | -66.9559 | 56.4229 | 56.5457 | 56.4161 | -67.1843 | -0.12766 | 0.011032 | -0.000767 | 0.009656 | 0.13731 | -0.098226 | 0.066888 | -0.31876 | -0.051413 | -0.010049 | -0.090341 | 0.22841 | 0.071408 | -0.05817 | 123.3509 | 123.2416 | 123.4067 | 66.8257 | -123.4675 | 123.2884 | 123.4113 | 123.2817 | 66.637 | -123.6586
407.25 | 123.6145 | -66.8106 | 56.4651 | 0.079707 | -0.019031 | -0.0018439 | 0.049122 | -0.005069 | 0.052569 | 0.035852 | -0.0031524 | -0.0026499 | 0.057427 | 0.039498 | 0.056307 | -66.8572 | -0.058115 | -66.8559 | 56.4899 | 56.3761 | 56.5458 | -67.0069 | -66.8664 | -0.29726 | -66.9376 | 56.4275 | 56.5457 | 56.4116 | -67.1843 | -0.19633 | 0.024766 | -0.046542 | -0.045276 | 0.15105 | -0.089071 | 0.080621 | -0.37369 | -0.037679 | -0.055823 | -0.12696 | 0.24673 | 0.080563 | -0.053594 | 123.3005 | 123.1867 | 123.3564 | 66.7525 | -123.4721 | 123.2381 | 123.3563 | 123.2222 | 66.5134 | -123.6494
408.2344 | 123.5733 | -66.8564 | 56.488 | 0.064445 | -0.019031 | -0.00077494 | 0.049122 | -0.006137 | 0.051501 | 0.081635 | -0.0020844 | -0.0026499 | 0.057427 | 0.040567 | 0.057375 | -66.8526 | -0.071851 | -66.8421 | 56.4945 | 56.3807 | 56.5503 | -67.0161 | -66.8527 | -0.35678 | -66.9284 | 56.432 | 56.5503 | 56.4116 | -67.1797 | -0.15971 | 0.006456 | 0.003812 | 0.014235 | 0.17394 | -0.10738 | 0.062312 | -0.32333 | -0.055989 | 0.003689 | -0.072025 | 0.25131 | 0.062253 | -0.076482 | 123.3509 | 123.237 | 123.4067 | 66.7845 | -123.5041 | 123.2884 | 123.4067 | 123.2679 | 66.4996 | -123.6678
409.2344 | 123.5733 | -66.8427 | 56.488 | 0.064445 | -0.021168 | -0.0029119 | 0.050191 | -0.006137 | 0.051501 | 0.051113 | -0.0031524 | -0.0015819 | 0.056359 | 0.039498 | 0.05417 | -66.8388 | -0.094744 | -66.8376 | 56.4945 | 56.3852 | 56.5595 | -66.9932 | -66.8435 | -0.43004 | -66.9238 | 56.4366 | 56.5594 | 56.3795 | -67.1751 | -0.15055 | 0.006456 | 0.003814 | 0.005081 | 0.15563 | -0.1028 | 0.071469 | -0.33249 | -0.05141 | -0.000887 | -0.081179 | 0.25131 | 0.071411 | -0.10853 | 123.3371 | 123.2279 | 123.4022 | 66.7479 | -123.4812 | 123.2793 | 123.4021 | 123.2222 | 66.4126 | -123.6632
410.2344 | 123.5458 | -66.8472 | 56.4789 | 0.079707 | -0.019031 | -0.00077494 | 0.046985 | -0.006137 | 0.051501 | 0.096896 | -0.0031524 | -0.0037179 | 0.058496 | 0.040567 | 0.055238 | -66.8343 | -0.13595 | -66.8421 | 56.5082 | 56.4036 | 56.5641 | -66.9978 | -66.8435 | -0.51704 | -66.9193 | 56.4458 | 56.5686 | 56.4207 | -67.1614 | -0.15055 | 0.029346 | 0.012971 | 0.00508 | 0.15563 | -0.075331 | 0.085203 | -0.31417 | -0.033098 | 0.003691 | -0.072022 | 0.24215 | 0.089723 | -0.05817 | 123.3555 | 123.2508 | 123.4113 | 66.7113 | -123.4767 | 123.293 | 123.4158 | 123.2679 | 66.3302 | -123.6403
411.2344 | 123.5825 | -66.8152 | 56.4926 | 0.033921 | -0.0201 | -0.00077494 | 0.049122 | -0.007206 | 0.053638 | 0.066374 | -0.0042204 | -0.0058549 | 0.055291 | 0.041635 | 0.057375 | -66.8251 | -0.17716 | -66.833 | 56.5082 | 56.399 | 56.5687 | -66.984 | -66.8298 | -0.64982 | -66.9009 | 56.4504 | 56.5732 | 56.4299 | -67.166 | -0.16885 | 0.015613 | -0.009916 | -0.017806 | 0.15105 | -0.093642 | 0.076048 | -0.3508 | -0.042253 | -0.014615 | -0.08575 | 0.26505 | 0.080568 | -0.062746 | 123.3234 | 123.2142 | 123.3838 | 66.638 | -123.4767 | 123.2655 | 123.3884 | 123.2451 | 66.1654 | -123.6586
412.25 | 123.5733 | -66.8198 | 56.5063 | 0.079707 | -0.021168 | -0.0029119 | 0.048054 | -0.006137 | 0.052569 | 0.096896 | -0.0031524 | -0.0058549 | 0.056359 | 0.041635 | 0.056307 | -66.8114 | -0.22752 | -66.8238 | 56.5174 | 56.4127 | 56.5778 | -66.9795 | -66.8115 | -0.80549 | -66.9101 | 56.4595 | 56.5823 | 56.4482 | -67.1568 | -0.1597 | 0.011037 | 0.008396 | -0.004073 | 0.15563 | -0.093639 | 0.071473 | -0.33706 | -0.046829 | 0.008276 | -0.090331 | 0.24673 | 0.075993 | -0.058164 | 123.3371 | 123.2325 | 123.3976 | 66.5922 | -123.4858 | 123.2793 | 123.4021 | 123.2679 | 66.0143 | -123.6632
413.2344 | 123.5413 | -66.8152 | 56.5109 | 0.079707 | -0.019031 | -0.00077494 | 0.049122 | -0.006137 | 0.050433 | 0.066374 | -0.0031524 | -0.0037179 | 0.056359 | 0.040567 | 0.056307 | -66.7976 | -0.2962 | -66.8101 | 56.5311 | 56.4219 | 56.587 | -66.984 | -66.8069 | -0.98864 | -66.8872 | 56.4687 | 56.5915 | 56.4528 | -67.1477 | -0.16885 | 0.020195 | 0.017555 | 0.005085 | 0.17394 | -0.089058 | 0.076053 | -0.33248 | -0.042249 | 0.008278 | -0.072014 | 0.26047 | 0.080573 | -0.058163 | 123.3463 | 123.2371 | 123.4022 | 66.519 | -123.495 | 123.2839 | 123.4067 | 123.2679 | 65.8265 | -123.6586
414.2344 | 123.5733 | -66.7923 | 56.5247 | 0.064445 | -0.022236 | -0.00077494 | 0.050191 | -0.006137 | 0.051501 | 0.066374 | -0.0031524 | -0.0026499 | 0.056359 | 0.040567 | 0.055238 | -66.7931 | -0.37862 | -66.8009 | 56.5357 | 56.431 | 56.6053 | -66.9611 | -66.7886 | -1.2222 | -66.8735 | 56.4824 | 56.6007 | 56.4619 | -67.1385 | -0.16885 | 0.011041 | -0.000756 | -0.008647 | 0.1602 | -0.093633 | 0.080634 | -0.34621 | -0.042246 | 0.003704 | -0.081167 | 0.26504 | 0.075997 | -0.062738 | 123.328 | 123.2233 | 123.3976 | 66.4137 | -123.4858 | 123.2747 | 123.393 | 123.2542 | 65.5701 | -123.6632
415.2344 | 123.5825 | -66.7877 | 56.5292 | 0.079707 | -0.0201 | -0.0018439 | 0.049122 | -0.005069 | 0.051501 | 0.096896 | -0.0042204 | -0.0047869 | 0.056359 | 0.041635 | 0.058443 | -66.7793 | -0.4885 | -66.7918 | 56.5449 | 56.4356 | 56.6144 | -66.9566 | -66.784 | -1.4557 | -66.8643 | 56.4824 | 56.6052 | 56.4711 | -67.1294 | -0.16885 | 0.01562 | 0.008402 | -0.004068 | 0.16478 | -0.093632 | 0.085213 | -0.34163 | -0.046824 | 0.003706 | -0.076587 | 0.26504 | 0.075998 | -0.058159 | 123.3326 | 123.2233 | 123.4022 | 66.2992 | -123.4858 | 123.2701 | 123.393 | 123.2588 | 65.332 | -123.6586
416.2344 | 123.5825 | -66.806 | 56.543 | 0.064445 | -0.0201 | -0.0018439 | 0.050191 | -0.007206 | 0.051501 | 0.066374 | -0.0042204 | -0.0037179 | 0.056359 | 0.041635 | 0.056307 | -66.7702 | -0.59381 | -66.7826 | 56.554 | 56.4402 | 56.6144 | -66.9291 | -66.7657 | -1.7304 | -66.8643 | 56.487 | 56.619 | 56.4757 | -67.1202 | -0.12306 | 0.011043 | 0.035869 | 0.023399 | 0.14646 | -0.10279 | 0.07148 | -0.31416 | -0.055979 | 0.040331 | -0.058277 | 0.25589 | 0.076 | -0.067313 | 123.36 | 123.2462 | 123.4205 | 66.2122 | -123.4721 | 123.293 | 123.425 | 123.2817 | 65.0756 | -123.6632
417.2344 | 123.6145 | -66.7419 | 56.5567 | 0.049183 | -0.021168 | -0.0018439 | 0.049122 | -0.007206 | 0.051501 | 0.066374 | -0.0042204 | -0.0047869 | 0.055291 | 0.040567 | 0.055238 | -66.761 | -0.73575 | -66.7735 | 56.5632 | 56.4585 | 56.6282 | -66.9108 | -66.7565 | -2.028 | -66.846 | 56.5053 | 56.6327 | 56.4848 | -67.1065 | -0.16883 | 0.006467 | -0.019061 | -0.031531 | 0.1373 | -0.098203 | 0.071483 | -0.36451 | -0.051398 | -0.014599 | -0.10405 | 0.26046 | 0.076003 | -0.071889 | 123.3051 | 123.2004 | 123.3701 | 66.0062 | -123.4675 | 123.2472 | 123.3746 | 123.2268 | 64.7139 | -123.6632
418.2344 | 123.5596 | -66.7648 | 56.5887 | 0.064445 | -0.023305 | -0.0029119 | 0.050191 | -0.008274 | 0.052569 | 0.066374 | -0.0031524 | -0.0037179 | 0.055291 | 0.042703 | 0.056307 | -66.7381 | -0.90973 | -66.7552 | 56.5769 | 56.4677 | 56.6373 | -66.9245 | -66.7382 | -2.3394 | -66.8277 | 56.5145 | 56.6464 | 56.4985 | -67.0881 | -0.15968 | -0.011841 | 0.02672 | 0.009671 | 0.16935 | -0.12109 | 0.048597 | -0.32331 | -0.074284 | 0.026605 | -0.062845 | 0.26046 | 0.057696 | -0.090196 | 123.3417 | 123.2325 | 123.4022 | 65.8551 | -123.5133 | 123.2793 | 123.4113 | 123.2634 | 64.4255 | -123.6769
419.2344 | 123.5825 | -66.7099 | 56.5613 | 0.064445 | -0.022236 | -0.0029119 | 0.050191 | -0.007206 | 0.052569 | 0.066374 | -0.0020844 | -0.0037179 | 0.056359 | 0.042703 | 0.056307 | -66.729 | -1.1204 | -66.7368 | 56.5952 | 56.4768 | 56.6511 | -66.9108 | -66.7291 | -2.669 | -66.8185 | 56.5282 | 56.651 | 56.5169 | -67.079 | -0.20088 | 0.033939 | -0.019056 | -0.026948 | 0.17393 | -0.084465 | 0.089799 | -0.36908 | -0.033082 | -0.01917 | -0.10862 | 0.26046 | 0.089741 | -0.044416 | 123.3051 | 123.1867 | 123.361 | 65.5895 | -123.4721 | 123.2381 | 123.3609 | 123.2268 | 64.0409 | -123.6403
420.2344 | 123.587 | -66.7282 | 56.5979 | 0.064445 | -0.022236 | -0.0018439 | 0.048054 | -0.005069 | 0.050433 | 0.066374 | -0.0020844 | -0.0047869 | 0.056359 | 0.041635 | 0.055238 | -66.7198 | -1.3127 | -66.7185 | 56.6044 | 56.4997 | 56.6694 | -66.897 | -66.7016 | -3.0262 | -66.7865 | 56.5465 | 56.6693 | 56.5306 | -67.0698 | -0.16883 | 0.006475 | 0.008411 | 0.009675 | 0.17851 | -0.098191 | 0.071493 | -0.34162 | -0.051389 | 0.026612 | -0.058259 | 0.28336 | 0.071434 | -0.067301 | 123.3326 | 123.2279 | 123.3976 | 65.4156 | -123.4949 | 123.2747 | 123.3975 | 123.2588 | 63.702 | -123.6677
421.2344 | 123.555 | -66.7099 | 56.6208 | 0.064445 | -0.021168 | -0.0018439 | 0.049122 | -0.004001 | 0.050433 | 0.066374 | -0.0052884 | -0.0047869 | 0.057427 | 0.042703 | 0.056307 | -66.6969 | -1.5691 | -66.714 | 56.6227 | 56.5089 | 56.6786 | -66.8787 | -66.6833 | -3.4245 | -66.7773 | 56.5511 | 56.6831 | 56.5398 | -67.0561 | -0.16882 | 0.001899 | 0.012993 | -0.004057 | 0.16477 | -0.11192 | 0.057761 | -0.34619 | -0.0697 | 0.026617 | -0.067411 | 0.27878 | 0.062281 | -0.081033 | 123.3326 | 123.2188 | 123.3885 | 65.1408 | -123.4995 | 123.261 | 123.393 | 123.2497 | 63.2854 | -123.6769
422.25 | 123.5092 | -66.7053 | 56.662 | 0.049183 | -0.021168 | -0.00077494 | 0.050191 | -0.008274 | 0.051501 | 0.081635 | -0.0042204 | -0.0037179 | 0.055291 | 0.04484 | 0.05417 | -66.674 | -1.8575 | -66.7002 | 56.6318 | 56.5318 | 56.6923 | -66.8787 | -66.6604 | -3.8641 | -66.759 | 56.5648 | 56.6831 | 56.5535 | -67.0378 | -0.1734 | -0.030142 | 0.031307 | 0.0051 | 0.1785 | -0.13023 | 0.030299 | -0.33245 | -0.097162 | 0.044933 | -0.053674 | 0.27878 | 0.021083 | -0.1085 | 123.3372 | 123.2371 | 123.3976 | 64.8478 | -123.5407 | 123.2701 | 123.3884 | 123.2588 | 62.8412 | -123.6998
423.2344 | 123.555 | -66.7007 | 56.6254 | 0.064445 | -0.021168 | -0.0029119 | 0.049122 | -0.008274 | 0.050433 | 0.066374 | -0.0031524 | -0.0047869 | 0.054223 | 0.042703 | 0.055238 | -66.6557 | -2.1689 | -66.6773 | 56.641 | 56.5226 | 56.7106 | -66.8513 | -66.6604 | -4.2853 | -66.7453 | 56.5831 | 56.7014 | 56.5626 | -67.0286 | -0.15051 | 0.015636 | 0.045044 | 0.023414 | 0.17392 | -0.10276 | 0.085234 | -0.32787 | -0.042227 | 0.040356 | -0.044515 | 0.28336 | 0.076018 | -0.062717 | 123.3417 | 123.2233 | 123.4113 | 64.5319 | -123.4766 | 123.2839 | 123.4021 | 123.2634 | 62.4154 | -123.654
424.2344 | 123.5779 | -66.6962 | 56.6483 | 0.064445 | -0.022236 | -0.0029119 | 0.051259 | -0.005069 | 0.052569 | 0.081635 | -0.0042204 | -0.0026499 | 0.054223 | 0.042703 | 0.056307 | -66.6465 | -2.4848 | -66.6636 | 56.6639 | 56.5363 | 56.7198 | -66.8192 | -66.6375 | -4.7203 | -66.7178 | 56.5969 | 56.7151 | 56.5764 | -67.0195 | -0.12303 | 0.01564 | 0.049622 | 0.032571 | 0.1556 | -0.11191 | 0.071503 | -0.32329 | -0.05138 | 0.058671 | -0.021621 | 0.30167 | 0.066866 | -0.071869 | 123.3601 | 123.2325 | 123.4159 | 64.2114 | -123.4675 | 123.293 | 123.4113 | 123.2726 | 61.9759 | -123.6677
425.2344 | 123.555 | -66.6687 | 56.6483 | 0.049183 | -0.023305 | -0.0039799 | 0.051259 | -0.006137 | 0.051501 | 0.066374 | -0.0031524 | -0.0026499 | 0.056359 | 0.040567 | 0.057375 | -66.6328 | -2.8099 | -66.6499 | 56.6639 | 56.5547 | 56.7335 | -66.8284 | -66.6192 | -5.1644 | -66.7041 | 56.606 | 56.7289 | 56.5947 | -67.0057 | -0.15966 | 0.01564 | 0.035892 | 0.01884 | 0.17849 | -0.093598 | 0.085239 | -0.33702 | -0.042223 | 0.04952 | -0.035351 | 0.30167 | 0.080602 | -0.053555 | 123.3326 | 123.2234 | 123.4022 | 63.8588 | -123.4766 | 123.2747 | 123.3976 | 123.2634 | 61.5043 | -123.654
426.2344 | 123.5687 | -66.6183 | 56.6666 | 0.049183 | -0.021168 | -0.00077494 | 0.050191 | -0.007206 | 0.050433 | 0.066374 | -0.0031524 | -0.0037179 | 0.055291 | 0.041635 | 0.05417 | -66.6099 | -3.1487 | -66.6315 | 56.6822 | 56.573 | 56.7381 | -66.81 | -66.6009 | -5.6269 | -66.6903 | 56.6198 | 56.7426 | 56.613 | -66.9874 | -0.19169 | 0.015642 | 0.00843 | -0.013201 | 0.17849 | -0.093593 | 0.071507 | -0.36906 | -0.046798 | 0.017481 | -0.071969 | 0.29709 | 0.076027 | -0.053551 | 123.3006 | 123.1913 | 123.3564 | 63.4697 | -123.4766 | 123.2381 | 123.3609 | 123.2314 | 60.9915 | -123.654
427.25 | 123.5916 | -66.6046 | 56.6986 | 0.094969 | -0.021168 | -0.0029119 | 0.049122 | -0.006137 | 0.050433 | 0.081635 | -0.0052884 | -0.0047869 | 0.055291 | 0.043772 | 0.057375 | -66.6008 | -3.5195 | -66.6178 | 56.6959 | 56.5867 | 56.761 | -66.7871 | -66.5826 | -6.1672 | -66.6812 | 56.6335 | 56.7563 | 56.613 | -66.9828 | -0.18253 | -0.002666 | 0.003853 | -0.013199 | 0.16933 | -0.1119 | 0.062357 | -0.37821 | -0.065106 | 0.022063 | -0.076544 | 0.30167 | 0.05772 | -0.085594 | 123.3006 | 123.1913 | 123.3656 | 63.0851 | -123.4858 | 123.2381 | 123.3609 | 123.2176 | 60.4375 | -123.6814
428.2344 | 123.5596 | -66.6138 | 56.7123 | 0.064445 | -0.024373 | -0.0018439 | 0.048054 | -0.007206 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.056359 | 0.042703 | 0.055238 | -66.5779 | -3.9041 | -66.5949 | 56.7143 | 56.5959 | 56.7701 | -66.7871 | -66.5688 | -6.5976 | -66.6628 | 56.6518 | 56.7746 | 56.6267 | -66.9599 | -0.17338 | 0.001915 | 0.035901 | 0.018848 | 0.19222 | -0.11648 | 0.057781 | -0.34616 | -0.060525 | 0.044955 | -0.049073 | 0.29709 | 0.062301 | -0.085592 | 123.328 | 123.2096 | 123.3839 | 62.7096 | -123.4995 | 123.2656 | 123.3884 | 123.2405 | 60.0162 | -123.6723
429.2344 | 123.6008 | -66.5817 | 56.7078 | 0.079707 | -0.023305 | -0.0039799 | 0.048054 | -0.008274 | 0.050433 | 0.051113 | -0.0042204 | -0.0037179 | 0.057427 | 0.042703 | 0.055238 | -66.5641 | -4.2796 | -66.5812 | 56.7234 | 56.6142 | 56.7884 | -66.7734 | -66.5551 | -7.0234 | -66.6399 | 56.661 | 56.7838 | 56.6405 | -66.9508 | -0.19168 | 0.015649 | 0.017592 | 0.000539 | 0.19222 | -0.093582 | 0.080672 | -0.36905 | -0.046791 | 0.026647 | -0.058224 | 0.31083 | 0.076035 | -0.067279 | 123.3051 | 123.1959 | 123.3702 | 62.3021 | -123.4812 | 123.2427 | 123.3655 | 123.2222 | 59.5583 | -123.6585
430.2344 | 123.5962 | -66.6138 | 56.7169 | 0.064445 | -0.022236 | -0.0018439 | 0.048054 | -0.007206 | 0.051501 | 0.051113 | -0.0031524 | -0.0037179 | 0.056359 | 0.041635 | 0.055238 | -66.555 | -4.7146 | -66.5629 | 56.7326 | 56.6233 | 56.8068 | -66.7551 | -66.5368 | -7.44 | -66.6171 | 56.6747 | 56.793 | 56.6588 | -66.937 | -0.14132 | 0.01565 | 0.058793 | 0.050896 | 0.19222 | -0.093579 | 0.089832 | -0.32327 | -0.04221 | 0.077006 | -0.003286 | 0.31998 | 0.076037 | -0.058119 | 123.3463 | 123.2371 | 123.4205 | 61.8992 | -123.472 | 123.2885 | 123.4067 | 123.2726 | 59.1737 | -123.654
431.2344 | 123.5825 | -66.5726 | 56.7535 | 0.064445 | -0.022236 | -0.0039799 | 0.050191 | -0.007206 | 0.051501 | 0.066374 | -0.0042204 | -0.0047869 | 0.057427 | 0.041635 | 0.05417 | -66.5275 | -5.1129 | -66.5491 | 56.7509 | 56.6325 | 56.8068 | -66.7322 | -66.5184 | -7.8888 | -66.6033 | 56.693 | 56.8067 | 56.6725 | -66.9279 | -0.15963 | -0.002657 | 0.045065 | 0.023432 | 0.18306 | -0.12104 | 0.053211 | -0.35531 | -0.060517 | 0.054122 | -0.030749 | 0.32456 | 0.053152 | -0.081005 | 123.3235 | 123.2051 | 123.3793 | 61.4597 | -123.4857 | 123.2656 | 123.3793 | 123.2451 | 58.6838 | -123.6814
432.2344 | 123.5596 | -66.5588 | 56.781 | 0.033921 | -0.024373 | -0.00077494 | 0.049122 | -0.005069 | 0.051501 | 0.081635 | -0.0042204 | -0.0047869 | 0.056359 | 0.043772 | 0.055238 | -66.5138 | -5.5158 | -66.5308 | 56.76 | 56.6554 | 56.8205 | -66.7322 | -66.4956 | -8.2596 | -66.5942 | 56.7068 | 56.8204 | 56.6771 | -66.9096 | -0.17336 | -0.020966 | 0.045067 | 0.028012 | 0.20137 | -0.12561 | 0.039481 | -0.35073 | -0.074248 | 0.063282 | -0.035325 | 0.3154 | 0.039422 | -0.10389 | 123.3189 | 123.2142 | 123.3793 | 61.043 | -123.5132 | 123.2656 | 123.3793 | 123.236 | 58.2992 | -123.6906
433.2344 | 123.5916 | -66.5543 | 56.7261 | 0.064445 | -0.023305 | -0.0018439 | 0.050191 | -0.005069 | 0.050433 | 0.051113 | -0.0020844 | -0.0047869 | 0.056359 | 0.042703 | 0.055238 | -66.4955 | -5.9004 | -66.5171 | 56.7784 | 56.6737 | 56.8342 | -66.7276 | -66.4772 | -8.6626 | -66.5804 | 56.7113 | 56.8387 | 56.6863 | -66.8958 | -0.17336 | 0.052279 | 0.058802 | 0.037169 | 0.21053 | -0.052366 | 0.10815 | -0.34157 | -0.014737 | 0.077019 | -0.026167 | 0.3154 | 0.11267 | -0.039803 | 123.3326 | 123.228 | 123.3885 | 60.6538 | -123.4537 | 123.2656 | 123.393 | 123.2405 | 57.8917 | -123.6219
434.2344 | 123.6237 | -66.5268 | 56.7764 | 0.064445 | -0.022236 | -0.0039799 | 0.050191 | -0.006137 | 0.051501 | 0.066374 | -0.0042204 | -0.0026499 | 0.057427 | 0.043772 | 0.056307 | -66.4726 | -6.2713 | -66.4988 | 56.7921 | 56.6737 | 56.8571 | -66.7093 | -66.4589 | -9.0472 | -66.5621 | 56.7205 | 56.8479 | 56.7229 | -66.8867 | -0.18251 | 0.01566 | 0.054228 | 0.028016 | 0.21053 | -0.10272 | 0.080687 | -0.35988 | -0.055935 | 0.067868 | -0.035318 | 0.32456 | 0.071472 | -0.053528 | 123.3189 | 123.2005 | 123.3839 | 60.2555 | -123.4857 | 123.2473 | 123.3747 | 123.2497 | 57.4796 | -123.6631
435.2344 | 123.5916 | -66.5314 | 56.813 | 0.064445 | -0.023305 | -0.00077494 | 0.049122 | -0.005069 | 0.051501 | 0.051113 | -0.0042204 | -0.0026499 | 0.055291 | 0.043772 | 0.056307 | -66.4634 | -6.6513 | -66.485 | 56.8058 | 56.6829 | 56.8617 | -66.6864 | -66.4452 | -9.4226 | -66.5438 | 56.7388 | 56.8616 | 56.7229 | -66.8775 | -0.15504 | -0.007225 | 0.067963 | 0.046329 | 0.20137 | -0.13018 | 0.048645 | -0.34614 | -0.074242 | 0.086182 | -0.012425 | 0.33372 | 0.048586 | -0.090149 | 123.3372 | 123.2142 | 123.3931 | 59.8801 | -123.4995 | 123.2702 | 123.393 | 123.2543 | 57.1087 | -123.6906
436.2344 | 123.6282 | -66.481 | 56.7993 | 0.049183 | -0.022236 | -0.0018439 | 0.050191 | -0.008274 | 0.050433 | 0.081635 | -0.0020844 | -0.0037179 | 0.056359 | 0.042703 | 0.056307 | -66.4405 | -7.068 | -66.4713 | 56.815 | 56.7058 | 56.88 | -66.691 | -66.4177 | -9.7523 | -66.5301 | 56.748 | 56.8754 | 56.7412 | -66.8546 | -0.20997 | 0.015664 | 0.040501 | 0.00971 | 0.21968 | -0.093555 | 0.080692 | -0.3736 | -0.051352 | 0.0633 | -0.049043 | 0.32456 | 0.076055 | -0.058102 | 123.296 | 123.1868 | 123.361 | 59.4131 | -123.4903 | 123.229 | 123.3564 | 123.2222 | 56.7287 | -123.6539
437.2344 | 123.6145 | -66.4856 | 56.7993 | 0.079707 | -0.023305 | -0.00077494 | 0.049122 | -0.008274 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.057427 | 0.043772 | 0.055238 | -66.4314 | -7.4892 | -66.4622 | 56.8287 | 56.7241 | 56.8892 | -66.6544 | -66.4131 | -10.0865 | -66.5072 | 56.7617 | 56.8891 | 56.7458 | -66.85 | -0.16876 | 0.0294 | 0.054236 | 0.023445 | 0.19221 | -0.07524 | 0.08985 | -0.36445 | -0.037616 | 0.072457 | -0.021571 | 0.34288 | 0.089791 | -0.053523 | 123.3143 | 123.2097 | 123.3748 | 58.9964 | -123.4537 | 123.2473 | 123.3747 | 123.2314 | 56.3991 | -123.6494
438.2344 | 123.6237 | -66.481 | 56.8222 | 0.064445 | -0.024373 | -0.0029119 | 0.051259 | -0.005069 | 0.051501 | 0.081635 | -0.0052884 | -0.0026499 | 0.057427 | 0.04484 | 0.057375 | -66.413 | -7.8921 | -66.4347 | 56.8287 | 56.7241 | 56.8983 | -66.6635 | -66.3948 | -10.4208 | -66.498 | 56.7663 | 56.8983 | 56.7504 | -66.8363 | -0.1825 | 0.006511 | 0.067971 | 0.046336 | 0.22883 | -0.098129 | 0.076118 | -0.35529 | -0.055927 | 0.086194 | -0.016992 | 0.3383 | 0.076059 | -0.071833 | 123.3097 | 123.2051 | 123.3793 | 58.5889 | -123.4857 | 123.2473 | 123.3793 | 123.2314 | 56.0602 | -123.6585
439.2344 | 123.587 | -66.4948 | 56.8085 | 0.049183 | -0.022236 | -0.0018439 | 0.050191 | -0.005069 | 0.051501 | 0.051113 | -0.0020844 | -0.0037179 | 0.057427 | 0.04484 | 0.05417 | -66.3947 | -8.263 | -66.4255 | 56.8516 | 56.7332 | 56.9121 | -66.6269 | -66.3765 | -10.9794 | -66.4751 | 56.7846 | 56.9074 | 56.7778 | -66.8271 | -0.13213 | 0.043135 | 0.10002 | 0.069226 | 0.20136 | -0.075238 | 0.10359 | -0.3324 | -0.02388 | 0.11824 | 0.019635 | 0.35203 | 0.098949 | -0.030629 | 123.3464 | 123.228 | 123.4068 | 58.2318 | -123.4354 | 123.2793 | 123.4022 | 123.2726 | 55.5154 | -123.6356
440.2344 | 123.6237 | -66.4352 | 56.8497 | 0.049183 | -0.024373 | -0.0029119 | 0.050191 | -0.006137 | 0.050433 | 0.066374 | -0.0042204 | -0.0026499 | 0.055291 | 0.04484 | 0.056307 | -66.3764 | -8.643 | -66.4118 | 56.8745 | 56.7561 | 56.9304 | -66.6223 | -66.349 | -11.1717 | -66.466 | 56.8029 | 56.9257 | 56.7824 | -66.8134 | -0.18706 | 0.024829 | 0.058822 | 0.023452 | 0.21051 | -0.093541 | 0.080703 | -0.37817 | -0.046764 | 0.086205 | -0.030717 | 0.34745 | 0.076066 | -0.067248 | 123.3097 | 123.1914 | 123.3656 | 57.7922 | -123.472 | 123.2381 | 123.361 | 123.2177 | 55.2635 | -123.6631
441.2344 | 123.642 | -66.4215 | 56.9092 | 0.064445 | -0.025442 | -0.0018439 | 0.046985 | -0.007206 | 0.050433 | 0.051113 | -0.0031524 | -0.0037179 | 0.056359 | 0.04484 | 0.057375 | -66.3444 | -9.0001 | -66.3706 | 56.8928 | 56.779 | 56.9624 | -66.5948 | -66.2987 | -11.5105 | -66.4248 | 56.835 | 56.9578 | 56.8191 | -66.7859 | -0.17332 | -0.016367 | 0.077138 | 0.050923 | 0.22424 | -0.13016 | 0.053243 | -0.36443 | -0.074224 | 0.12284 | -0.003241 | 0.36119 | 0.048606 | -0.090129 | 123.3143 | 123.2005 | 123.3839 | 57.4214 | -123.504 | 123.2565 | 123.3793 | 123.2406 | 54.911 | -123.6951
442.2344 | 123.5321 | -66.4078 | 56.9458 | 0.064445 | -0.023305 | -0.0039799 | 0.049122 | -0.006137 | 0.052569 | 0.066374 | -0.0042204 | -0.0037179 | 0.058496 | 0.042703 | 0.055238 | -66.3032 | -9.3573 | -66.3523 | 56.9157 | 56.8157 | 56.9807 | -66.5903 | -66.2666 | -11.6662 | -66.3973 | 56.8533 | 56.9761 | 56.8419 | -66.7539 | -0.18248 | -0.030096 | 0.10461 | 0.055503 | 0.23798 | -0.13015 | 0.034937 | -0.34611 | -0.092531 | 0.14116 | 0.010498 | 0.35661 | 0.030299 | -0.10386 | 123.3235 | 123.2234 | 123.3885 | 57.0505 | -123.5361 | 123.261 | 123.3839 | 123.2497 | 54.7416 | -123.6997
443.2344 | 123.5962 | -66.3757 | 56.9366 | 0.064445 | -0.022236 | -0.0039799 | 0.048054 | -0.008274 | 0.051501 | 0.051113 | -0.0031524 | -0.0058549 | 0.058496 | 0.04484 | 0.056307 | -66.2849 | -9.6823 | -66.3248 | 56.934 | 56.8294 | 57.0036 | -66.5536 | -66.2346 | -11.8081 | -66.3835 | 56.8716 | 56.999 | 56.8603 | -66.7447 | -0.17789 | -0.002628 | 0.09088 | 0.050929 | 0.22882 | -0.10726 | 0.066985 | -0.369 | -0.065062 | 0.14116 | -0.00781 | 0.36119 | 0.062347 | -0.076388 | 123.3098 | 123.2051 | 123.3794 | 56.6934 | -123.4903 | 123.2473 | 123.3747 | 123.236 | 54.5676 | -123.6814
444.2344 | 123.6191 | -66.3712 | 56.9275 | 0.079707 | -0.024373 | -0.00077494 | 0.048054 | -0.006137 | 0.050433 | 0.081635 | -0.0031524 | -0.0037179 | 0.056359 | 0.043772 | 0.056307 | -66.2849 | -10.1539 | -66.3111 | 56.9386 | 56.8385 | 56.9991 | -66.5582 | -66.2208 | -11.831 | -66.3606 | 56.8762 | 57.0036 | 56.8648 | -66.7264 | -0.18704 | 0.011107 | 0.086303 | 0.060087 | 0.24713 | -0.088941 | 0.071562 | -0.35526 | -0.051328 | 0.15032 | 0.010507 | 0.36577 | 0.076082 | -0.062653 | 123.3098 | 123.2097 | 123.3702 | 56.2172 | -123.4857 | 123.2473 | 123.3747 | 123.236 | 54.5401 | -123.6539
445.2344 | 123.6465 | -66.3483 | 56.9229 | 0.064445 | -0.023305 | -0.0018439 | 0.050191 | -0.007206 | 0.049364 | 0.066374 | -0.0031524 | -0.0047869 | 0.055291 | 0.043772 | 0.056307 | -66.262 | -10.5477 | -66.3019 | 56.9432 | 56.8385 | 57.0036 | -66.5399 | -66.2025 | -11.8997 | -66.3561 | 56.8807 | 57.0082 | 56.8694 | -66.731 | -0.19162 | 0.020262 | 0.086307 | 0.046355 | 0.23797 | -0.084364 | 0.080718 | -0.38273 | -0.042172 | 0.14575 | -0.007803 | 0.37492 | 0.085238 | -0.053498 | 123.2914 | 123.1868 | 123.3519 | 55.8006 | -123.4628 | 123.229 | 123.3564 | 123.2177 | 54.4486 | -123.6539
446.2344 | 123.6099 | -66.3712 | 56.9641 | 0.064445 | -0.022236 | -0.0029119 | 0.049122 | -0.006137 | 0.051501 | 0.066374 | -0.0031524 | -0.0047869 | 0.058496 | 0.045909 | 0.056307 | -66.2482 | -10.8499 | -66.279 | 56.9615 | 56.8614 | 57.0311 | -66.5353 | -66.1705 | -12.0325 | -66.3332 | 56.8991 | 57.0265 | 56.8923 | -66.7127 | -0.16415 | -0.002622 | 0.12293 | 0.092135 | 0.25628 | -0.10267 | 0.066991 | -0.34152 | -0.065056 | 0.20069 | 0.037979 | 0.3795 | 0.062354 | -0.071803 | 123.3326 | 123.2326 | 123.4023 | 55.5213 | -123.4994 | 123.2702 | 123.3976 | 123.2635 | 54.3387 | -123.6768
447.25 | 123.4772 | -66.3895 | 56.9733 | 0.064445 | -0.024373 | -0.0018439 | 0.051259 | -0.005069 | 0.050433 | 0.096896 | -0.0042204 | -0.0047869 | 0.057427 | 0.045909 | 0.055238 | -66.2391 | -11.1704 | -66.279 | 56.9661 | 56.8569 | 57.0357 | -66.5399 | -66.1659 | -12.0325 | -66.3194 | 56.8991 | 57.0219 | 56.8832 | -66.7218 | -0.15042 | -0.0072 | 0.1504 | 0.11044 | 0.26086 | -0.1164 | 0.062414 | -0.33237 | -0.074212 | 0.22358 | 0.070025 | 0.4024 | 0.048619 | -0.090116 | 123.3555 | 123.2463 | 123.4251 | 55.2191 | -123.5132 | 123.2885 | 123.4114 | 123.2726 | 54.357 | -123.6951
448.2344 | 123.5138 | -66.362 | 56.987 | 0.064445 | -0.023305 | -0.0018439 | 0.046985 | -0.006137 | 0.051501 | 0.081635 | -0.0052884 | -0.0037179 | 0.057427 | 0.045909 | 0.055238 | -66.2208 | -11.4222 | -66.2653 | 56.9798 | 56.866 | 57.0403 | -66.5261 | -66.1338 | -12.1653 | -66.3011 | 56.9128 | 57.031 | 56.906 | -66.7035 | -0.16415 | -0.007198 | 0.14125 | 0.096715 | 0.26086 | -0.12098 | 0.053259 | -0.34152 | -0.07421 | 0.22816 | 0.060875 | 0.40239 | 0.044044 | -0.080956 | 123.3418 | 123.228 | 123.4023 | 54.9398 | -123.5131 | 123.2748 | 123.393 | 123.268 | 54.1967 | -123.6905
449.2344 | 123.4955 | -66.3574 | 57.0282 | 0.079707 | -0.023305 | -0.0029119 | 0.048054 | -0.007206 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.054223 | 0.04484 | 0.056307 | -66.2024 | -11.6603 | -66.247 | 56.9935 | 56.8798 | 57.0448 | -66.5216 | -66.1064 | -12.2431 | -66.2874 | 56.9174 | 57.0494 | 56.906 | -66.6852 | -0.16415 | -0.03466 | 0.15498 | 0.11045 | 0.2746 | -0.14844 | 0.01664 | -0.32778 | -0.11083 | 0.25106 | 0.070033 | 0.39782 | 0.02116 | -0.12215 | 123.351 | 123.2372 | 123.4023 | 54.6971 | -123.5498 | 123.2748 | 123.4068 | 123.2635 | 54.1143 | -123.7134
450.2344 | 123.4772 | -66.3712 | 57.0236 | 0.064445 | -0.025442 | -0.0018439 | 0.049122 | -0.006137 | 0.051501 | 0.066374 | -0.0063574 | -0.0037179 | 0.056359 | 0.043772 | 0.053102 | -66.1887 | -11.8618 | -66.2332 | 56.9981 | 56.8752 | 57.054 | -66.5033 | -66.088 | -12.3255 | -66.2737 | 56.9357 | 57.0585 | 56.9244 | -66.6852 | -0.1321 | -0.025505 | 0.18245 | 0.13792 | 0.27002 | -0.14844 | 0.030374 | -0.31405 | -0.087938 | 0.28311 | 0.097502 | 0.41155 | 0.034894 | -0.099262 | 123.3693 | 123.2463 | 123.4252 | 54.5094 | -123.5269 | 123.3068 | 123.4297 | 123.2955 | 54.0456 | -123.7088
451.2344 | 123.4772 | -66.3483 | 57.0236 | 0.064445 | -0.024373 | -0.0029119 | 0.049122 | -0.009342 | 0.050433 | 0.081635 | -0.0042204 | -0.0058549 | 0.055291 | 0.04484 | 0.055238 | -66.1795 | -12.0769 | -66.2241 | 57.0027 | 56.8935 | 57.0677 | -66.5078 | -66.0606 | -12.4354 | -66.2508 | 56.9357 | 57.0677 | 56.9289 | -66.6715 | -0.15956 | -0.020927 | 0.16872 | 0.12419 | 0.28375 | -0.13012 | 0.04411 | -0.3232 | -0.087938 | 0.28769 | 0.097508 | 0.42071 | 0.044051 | -0.094684 | 123.351 | 123.2418 | 123.416 | 54.2713 | -123.5315 | 123.284 | 123.4159 | 123.2772 | 53.9129 | -123.6951
452.25 | 123.5138 | -66.3712 | 57.0007 | 0.064445 | -0.023305 | -0.0029119 | 0.049122 | -0.007206 | 0.051501 | 0.051113 | -0.0042204 | -0.0058549 | 0.056359 | 0.04484 | 0.056307 | -66.175 | -12.2464 | -66.2149 | 57.0119 | 56.8981 | 57.0723 | -66.4941 | -66.0423 | -12.7971 | -66.2508 | 56.9357 | 57.0631 | 56.9198 | -66.676 | -0.12294 | 0.011119 | 0.19618 | 0.15623 | 0.27917 | -0.10266 | 0.071578 | -0.30489 | -0.065049 | 0.32889 | 0.1204 | 0.42529 | 0.062362 | -0.080952 | 123.383 | 123.2692 | 123.4435 | 54.1248 | -123.4948 | 123.3068 | 123.4342 | 123.2909 | 53.574 | -123.6768
453.2344 | 123.5504 | -66.3345 | 56.987 | 0.079707 | -0.025442 | -0.0029119 | 0.051259 | -0.007206 | 0.050433 | 0.081635 | -0.0031524 | -0.0047869 | 0.055291 | 0.04484 | 0.055238 | -66.1612 | -12.489 | -66.2058 | 56.9981 | 56.8935 | 57.0632 | -66.4987 | -66.0377 | -13.3008 | -66.2508 | 56.9357 | 57.0677 | 56.9244 | -66.676 | -0.16414 | 0.011116 | 0.1733 | 0.12877 | 0.2929 | -0.093504 | 0.076152 | -0.34151 | -0.051317 | 0.29685 | 0.083775 | 0.42529 | 0.080672 | -0.062641 | 123.3327 | 123.228 | 123.3977 | 53.8455 | -123.4857 | 123.2702 | 123.4022 | 123.2589 | 53.0337 | -123.663
454.2344 | 123.4863 | -66.3391 | 57.0511 | 0.079707 | -0.024373 | -0.0018439 | 0.049122 | -0.008274 | 0.050433 | 0.081635 | -0.0031524 | -0.0047869 | 0.055291 | 0.045909 | 0.05417 | -66.1429 | -12.6218 | -66.2012 | 57.0164 | 56.9118 | 57.0769 | -66.4758 | -66.0011 | -13.5023 | -66.2324 | 56.9494 | 57.086 | 56.9473 | -66.6577 | -0.13667 | -0.034657 | 0.19619 | 0.13792 | 0.27459 | -0.13927 | 0.025802 | -0.31862 | -0.10167 | 0.33806 | 0.10667 | 0.42529 | 0.034901 | -0.10383 | 123.3555 | 123.2509 | 123.416 | 53.7173 | -123.5269 | 123.2885 | 123.4251 | 123.2864 | 52.8369 | -123.7088
455.2344 | 123.5001 | -66.3025 | 57.0831 | 0.049183 | -0.024373 | -0.0039799 | 0.051259 | -0.006137 | 0.050433 | 0.096896 | -0.0031524 | -0.0047869 | 0.056359 | 0.045909 | 0.055238 | -66.1063 | -12.7454 | -66.1646 | 57.0439 | 56.9393 | 57.1089 | -66.4529 | -65.9553 | -14.1204 | -66.1867 | 56.986 | 57.1089 | 56.9656 | -66.6348 | -0.15039 | -0.03923 | 0.1962 | 0.13793 | 0.28832 | -0.14384 | 0.025809 | -0.33235 | -0.097084 | 0.34722 | 0.11583 | 0.44818 | 0.02575 | -0.11756 | 123.3464 | 123.2418 | 123.4114 | 53.5571 | -123.536 | 123.2885 | 123.4114 | 123.2681 | 52.1821 | -123.718
456.2344 | 123.4772 | -66.2842 | 57.0969 | 0.079707 | -0.024373 | -0.00077494 | 0.049122 | -0.007206 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.056359 | 0.046977 | 0.056307 | -66.0788 | -12.8324 | -66.1417 | 57.0668 | 56.953 | 57.1318 | -66.4437 | -65.9141 | -14.2898 | -66.1454 | 57.0044 | 57.1226 | 56.993 | -66.6028 | -0.15955 | -0.030071 | 0.20536 | 0.14251 | 0.30205 | -0.14384 | 0.034969 | -0.31861 | -0.092503 | 0.37012 | 0.13873 | 0.45734 | 0.025753 | -0.10383 | 123.351 | 123.2372 | 123.416 | 53.4518 | -123.5406 | 123.2885 | 123.4068 | 123.2772 | 51.9944 | -123.6996
457.2344 | 123.5184 | -66.2613 | 57.074 | 0.049183 | -0.025442 | -0.0029119 | 0.050191 | -0.008274 | 0.050433 | 0.081635 | -0.0042204 | -0.0047869 | 0.054223 | 0.049114 | 0.055238 | -66.0422 | -12.9789 | -66.1096 | 57.0897 | 56.9668 | 57.1501 | -66.4117 | -65.8774 | -14.5325 | -66.1042 | 57.0181 | 57.1455 | 57.0022 | -66.5982 | -0.15038 | 0.015709 | 0.21909 | 0.15167 | 0.30205 | -0.10722 | 0.076171 | -0.33692 | -0.055879 | 0.38386 | 0.15705 | 0.49397 | 0.071534 | -0.07178 | 123.351 | 123.2281 | 123.4114 | 53.2824 | -123.4856 | 123.2794 | 123.4068 | 123.2635 | 51.7288 | -123.6722
458.2344 | 123.4863 | -66.2704 | 57.1106 | 0.049183 | -0.024373 | -0.0039799 | 0.049122 | -0.007206 | 0.050433 | 0.081635 | -0.0020844 | -0.0047869 | 0.055291 | 0.04484 | 0.055238 | -66.0285 | -13.2949 | -66.0959 | 57.0988 | 56.9897 | 57.1639 | -66.4025 | -65.8454 | -14.798 | -66.0859 | 57.0364 | 57.1638 | 57.0159 | -66.5753 | -0.13207 | -0.011756 | 0.24198 | 0.17456 | 0.30663 | -0.12094 | 0.053286 | -0.30487 | -0.074186 | 0.42507 | 0.18452 | 0.48939 | 0.053227 | -0.094665 | 123.3693 | 123.2601 | 123.4343 | 52.9756 | -123.5131 | 123.3069 | 123.4343 | 123.2864 | 51.4724 | -123.6859
459.2344 | 123.5046 | -66.2476 | 57.1747 | 0.064445 | -0.025442 | -0.0029119 | 0.050191 | -0.007206 | 0.050433 | 0.081635 | -0.0052884 | -0.0026499 | 0.056359 | 0.045909 | 0.055238 | -66.0056 | -13.3773 | -66.0501 | 57.1217 | 57.0125 | 57.1868 | -66.3659 | -65.7996 | -15.059 | -66.0493 | 57.0593 | 57.1913 | 57.0434 | -66.557 | -0.11833 | -0.052951 | 0.24199 | 0.19745 | 0.31578 | -0.16213 | 0.012092 | -0.30944 | -0.11538 | 0.44797 | 0.19826 | 0.5077 | 0.016612 | -0.13128 | 123.3693 | 123.2601 | 123.4343 | 52.8703 | -123.5406 | 123.3069 | 123.4389 | 123.291 | 51.1885 | -123.7317
460.2344 | 123.4726 | -66.2064 | 57.1564 | 0.079707 | -0.023305 | -0.0039799 | 0.048054 | -0.006137 | 0.051501 | 0.081635 | -0.0042204 | -0.0037179 | 0.055291 | 0.046977 | 0.057375 | -65.9781 | -13.5238 | -66.0364 | 57.1492 | 57.0263 | 57.2142 | -66.3476 | -65.7584 | -15.3108 | -66.0218 | 57.0776 | 57.2142 | 57.0709 | -66.5387 | -0.14121 | -0.007169 | 0.22826 | 0.16999 | 0.3112 | -0.13009 | 0.057874 | -0.33232 | -0.078756 | 0.44798 | 0.18454 | 0.51686 | 0.057816 | -0.085498 | 123.3556 | 123.2326 | 123.4206 | 52.6826 | -123.5039 | 123.284 | 123.4205 | 123.2772 | 50.8955 | -123.6951
461.2344 | 123.4818 | -66.1972 | 57.1838 | 0.064445 | -0.02651 | -0.0039799 | 0.049122 | -0.007206 | 0.051501 | 0.051113 | -0.0031524 | -0.0037179 | 0.056359 | 0.04484 | 0.05417 | -65.9415 | -13.6291 | -66.0043 | 57.1629 | 57.0538 | 57.2326 | -66.3109 | -65.708 | -15.6314 | -65.9852 | 57.1051 | 57.2417 | 57.0983 | -66.5112 | -0.11373 | -0.0209 | 0.25573 | 0.19288 | 0.30661 | -0.13008 | 0.048723 | -0.31401 | -0.078751 | 0.48919 | 0.21201 | 0.52602 | 0.057821 | -0.085493 | 123.3601 | 123.251 | 123.4298 | 52.5681 | -123.4948 | 123.3023 | 123.4389 | 123.2955 | 50.5658 | -123.695
462.25 | 123.4909 | -66.1835 | 57.1793 | 0.049183 | -0.023305 | -0.0029119 | 0.048054 | -0.006137 | 0.050433 | 0.081635 | -0.0042204 | -0.0037179 | 0.056359 | 0.045909 | 0.056307 | -65.914 | -13.7985 | -65.986 | 57.1904 | 57.0767 | 57.2555 | -66.3201 | -65.6668 | -15.929 | -65.9531 | 57.1188 | 57.26 | 57.1212 | -66.4883 | -0.13662 | 0.011148 | 0.26947 | 0.19746 | 0.33409 | -0.10261 | 0.076194 | -0.30484 | -0.060437 | 0.51666 | 0.23033 | 0.53517 | 0.080714 | -0.058022 | 123.3739 | 123.2601 | 123.4389 | 52.385 | -123.4994 | 123.3023 | 123.4434 | 123.3047 | 50.2545 | -123.6676
463.2344 | 123.4863 | -66.1285 | 57.2571 | 0.064445 | -0.024373 | -0.0029119 | 0.050191 | -0.006137 | 0.051501 | 0.066374 | -0.0052884 | -0.0037179 | 0.056359 | 0.045909 | 0.055238 | -65.8407 | -14.8104 | -65.9311 | 57.2453 | 57.1316 | 57.2967 | -66.2606 | -65.5798 | -16.2724 | -65.8799 | 57.1738 | 57.3103 | 57.1716 | -66.4288 | -0.13203 | -0.011731 | 0.28779 | 0.19747 | 0.3295 | -0.12548 | 0.039581 | -0.30025 | -0.083315 | 0.54873 | 0.24866 | 0.54891 | 0.053258 | -0.085477 | 123.3739 | 123.2601 | 123.4252 | 51.3182 | -123.5176 | 123.3023 | 123.4389 | 123.3001 | 49.8562 | -123.6859
464.2344 | 123.5229 | -66.0919 | 57.28 | 0.064445 | -0.025442 | -0.0018439 | 0.050191 | -0.006137 | 0.050433 | 0.081635 | -0.0020844 | -0.0037179 | 0.055291 | 0.046977 | 0.057375 | -65.795 | -15.0439 | -65.8899 | 57.2637 | 57.1545 | 57.3424 | -66.2285 | -65.5249 | -16.6387 | -65.8478 | 57.2058 | 57.3287 | 57.1945 | -66.4059 | -0.1366 | -0.016306 | 0.29696 | 0.20205 | 0.33865 | -0.12547 | 0.062479 | -0.31398 | -0.074154 | 0.56705 | 0.24409 | 0.55806 | 0.048685 | -0.085472 | 123.3556 | 123.2464 | 123.4344 | 51.048 | -123.5085 | 123.2977 | 123.4206 | 123.2864 | 49.4532 | -123.6859
465.2344 | 123.4863 | -66.037 | 57.3395 | 0.064445 | -0.025442 | -0.0029119 | 0.049122 | -0.008274 | 0.051501 | 0.066374 | -0.0042204 | -0.0037179 | 0.056359 | 0.048045 | 0.057375 | -65.7629 | -15.2545 | -65.8578 | 57.2957 | 57.182 | 57.3608 | -66.2056 | -65.4699 | -17.0141 | -65.802 | 57.2287 | 57.3561 | 57.2128 | -66.3876 | -0.16864 | -0.043767 | 0.27407 | 0.17917 | 0.3478 | -0.15751 | 0.021284 | -0.35059 | -0.11077 | 0.56706 | 0.23494 | 0.58554 | 0.016646 | -0.12667 | 123.3327 | 123.219 | 123.3977 | 50.7825 | -123.5451 | 123.2657 | 123.3931 | 123.2498 | 49.0229 | -123.7271
466.2344 | 123.5046 | -66.0324 | 57.3303 | 0.049183 | -0.025442 | -0.0029119 | 0.050191 | -0.006137 | 0.049364 | 0.081635 | -0.0042204 | -0.0047869 | 0.054223 | 0.046977 | 0.05417 | -65.7217 | -15.5246 | -65.8166 | 57.3232 | 57.2094 | 57.3928 | -66.1873 | -65.4104 | -17.3484 | -65.7563 | 57.2608 | 57.3836 | 57.2586 | -66.3555 | -0.1549 | -0.007141 | 0.3107 | 0.2158 | 0.37069 | -0.12088 | 0.06249 | -0.32312 | -0.069566 | 0.62201 | 0.27615 | 0.59927 | 0.053274 | -0.071725 | 123.3556 | 123.2419 | 123.4252 | 50.5078 | -123.5176 | 123.2932 | 123.416 | 123.291 | 48.684 | -123.6859
467.2344 | 123.5458 | -66.0049 | 57.3669 | 0.064445 | -0.025442 | -0.0029119 | 0.048054 | -0.008274 | 0.051501 | 0.096896 | -0.0063574 | -0.0047869 | 0.055291 | 0.046977 | 0.055238 | -65.7034 | -15.7581 | -65.8029 | 57.3369 | 57.2278 | 57.3882 | -66.1598 | -65.3646 | -17.8383 | -65.7334 | 57.2699 | 57.3928 | 57.2632 | -66.3464 | -0.15489 | -0.030026 | 0.30155 | 0.20206 | 0.35695 | -0.13918 | 0.02129 | -0.34143 | -0.09703 | 0.64033 | 0.27158 | 0.61301 | 0.02581 | -0.10377 | 123.3419 | 123.2327 | 123.3932 | 50.2468 | -123.5268 | 123.2749 | 123.3977 | 123.2681 | 48.1666 | -123.7133
468.2344 | 123.4772 | -66.0233 | 57.3807 | 0.064445 | -0.025442 | -0.0029119 | 0.050191 | -0.008274 | 0.051501 | 0.096896 | -0.0031524 | -0.0037179 | 0.055291 | 0.048045 | 0.056307 | -65.6668 | -16.0329 | -65.7754 | 57.3644 | 57.2552 | 57.4249 | -66.1507 | -65.2959 | -18.2183 | -65.6876 | 57.2974 | 57.4202 | 57.2952 | -66.3189 | -0.12742 | -0.016289 | 0.35648 | 0.24784 | 0.37527 | -0.12544 | 0.044186 | -0.29565 | -0.083292 | 0.72732 | 0.33568 | 0.63132 | 0.039549 | -0.085451 | 123.3876 | 123.2785 | 123.4481 | 49.9904 | -123.5314 | 123.3206 | 123.4435 | 123.3185 | 47.8049 | -123.6996
469.2344 | 123.4772 | -65.95 | 57.4356 | 0.079707 | -0.025442 | -0.0039799 | 0.050191 | -0.007206 | 0.050433 | 0.081635 | -0.0042204 | -0.0037179 | 0.055291 | 0.046977 | 0.05417 | -65.6118 | -16.2526 | -65.725 | 57.4056 | 57.2873 | 57.4661 | -66.0728 | -65.2135 | -18.6991 | -65.6235 | 57.3432 | 57.4569 | 57.3181 | -66.2685 | -0.12282 | -0.030016 | 0.33818 | 0.22496 | 0.34779 | -0.14832 | 0.030462 | -0.31852 | -0.092439 | 0.7365 | 0.32654 | 0.64506 | 0.021246 | -0.11749 | 123.3556 | 123.2373 | 123.4161 | 49.6974 | -123.5084 | 123.2932 | 123.4069 | 123.2681 | 47.2509 | -123.7041
470.2344 | 123.5184 | -65.9134 | 57.4448 | 0.049183 | -0.025442 | -0.0018439 | 0.049122 | -0.007206 | 0.050433 | 0.081635 | -0.0031524 | -0.0037179 | 0.055291 | 0.046977 | 0.05417 | -65.5706 | -16.9989 | -65.6793 | 57.4422 | 57.3422 | 57.5073 | -66.0683 | -65.1219 | -19.1753 | -65.5731 | 57.3752 | 57.4981 | 57.3547 | -66.2365 | -0.15486 | -0.002543 | 0.34277 | 0.23413 | 0.38899 | -0.10253 | 0.062514 | -0.32309 | -0.069545 | 0.79145 | 0.34028 | 0.66337 | 0.053298 | -0.090016 | 123.3556 | 123.2556 | 123.4207 | 48.9144 | -123.513 | 123.2886 | 123.4115 | 123.2681 | 46.7381 | -123.6812
471.2344 | 123.5184 | -65.8722 | 57.5089 | 0.049183 | -0.025442 | -0.0029119 | 0.050191 | -0.006137 | 0.051501 | 0.051113 | -0.0042204 | -0.0037179 | 0.057427 | 0.046977 | 0.055238 | -65.4974 | -17.2462 | -65.6243 | 57.488 | 57.3789 | 57.5531 | -66.0225 | -65.0304 | -19.5278 | -65.4953 | 57.4164 | 57.5622 | 57.4005 | -66.1907 | -0.15027 | -0.020847 | 0.37482 | 0.24787 | 0.39814 | -0.12999 | 0.044213 | -0.3185 | -0.092425 | 0.84182 | 0.37692 | 0.69542 | 0.053312 | -0.10832 | 123.3602 | 123.2511 | 123.4253 | 48.626 | -123.5313 | 123.2886 | 123.4344 | 123.2727 | 46.3444 | -123.6995
472.2344 | 123.4634 | -65.8722 | 57.518 | 0.049183 | -0.02651 | -0.0029119 | 0.048054 | -0.006137 | 0.051501 | 0.035852 | -0.0020844 | -0.0026499 | 0.055291 | 0.046977 | 0.056307 | -65.4607 | -17.585 | -65.5785 | 57.5246 | 57.4109 | 57.5897 | -65.9858 | -64.948 | -20.0178 | -65.4357 | 57.4576 | 57.5896 | 57.4601 | -66.1586 | -0.11364 | 0.006626 | 0.41145 | 0.29365 | 0.40729 | -0.10709 | 0.071687 | -0.28645 | -0.060374 | 0.92424 | 0.43644 | 0.72289 | 0.071628 | -0.05795 | 123.3968 | 123.2831 | 123.4619 | 48.2872 | -123.5038 | 123.3298 | 123.4618 | 123.3322 | 45.8544 | -123.6766
473.2344 | 123.4955 | -65.8127 | 57.5684 | 0.049183 | -0.024373 | -0.0029119 | 0.048054 | -0.007206 | 0.051501 | 0.051113 | -0.0042204 | -0.0047869 | 0.055291 | 0.045909 | 0.056307 | -65.3921 | -17.8689 | -65.5236 | 57.5704 | 57.4475 | 57.6355 | -65.9309 | -64.8381 | -20.4207 | -65.3625 | 57.4943 | 57.6263 | 57.4875 | -66.1129 | -0.1182 | 0.002055 | 0.42062 | 0.28908 | 0.40728 | -0.12081 | 0.067119 | -0.30017 | -0.0741 | 0.97462 | 0.45019 | 0.75036 | 0.057903 | -0.080832 | 123.3831 | 123.2602 | 123.4482 | 47.9438 | -123.4992 | 123.3069 | 123.4389 | 123.3002 | 45.392 | -123.6812
474.2344 | 123.4955 | -65.7486 | 57.6141 | 0.079707 | -0.025442 | -0.0029119 | 0.049122 | -0.006137 | 0.051501 | 0.066374 | -0.0042204 | -0.0037179 | 0.055291 | 0.049114 | 0.056307 | -65.3509 | -18.139 | -65.4778 | 57.6025 | 57.4979 | 57.6675 | -65.8897 | -64.7419 | -20.9152 | -65.2984 | 57.5446 | 57.6583 | 57.5333 | -66.0716 | -0.14108 | -0.011673 | 0.39774 | 0.27078 | 0.41185 | -0.11622 | 0.053392 | -0.32305 | -0.069513 | 1.0067 | 0.45021 | 0.77325 | 0.044176 | -0.080823 | 123.3511 | 123.2465 | 123.4161 | 47.6096 | -123.5038 | 123.2932 | 123.4069 | 123.2819 | 44.8334 | -123.6858
475.2344 | 123.5184 | -65.712 | 57.637 | 0.049183 | -0.02651 | -0.0050489 | 0.049122 | -0.007206 | 0.051501 | 0.066374 | -0.0052884 | -0.0037179 | 0.057427 | 0.048045 | 0.055238 | -65.3051 | -18.2993 | -65.4366 | 57.6345 | 57.5162 | 57.695 | -65.8668 | -64.6503 | -21.3914 | -65.2389 | 57.5675 | 57.6949 | 57.5608 | -66.0487 | -0.15481 | -0.002512 | 0.4069 | 0.27536 | 0.43017 | -0.12079 | 0.057976 | -0.33677 | -0.069509 | 1.0616 | 0.47311 | 0.80988 | 0.057917 | -0.07624 | 123.3465 | 123.2282 | 123.407 | 47.4127 | -123.5038 | 123.2795 | 123.4069 | 123.2728 | 44.3206 | -123.6858
476.2344 | 123.5138 | -65.6479 | 57.6874 | 0.049183 | -0.02651 | -0.0029119 | 0.046985 | -0.007206 | 0.050433 | 0.081635 | -0.0052884 | -0.0047869 | 0.055291 | 0.046977 | 0.056307 | -65.241 | -18.4275 | -65.3908 | 57.6803 | 57.5666 | 57.7454 | -65.8347 | -64.5404 | -21.7577 | -65.1702 | 57.6087 | 57.7361 | 57.6111 | -66.0075 | -0.18684 | -0.007082 | 0.40691 | 0.25705 | 0.44389 | -0.12078 | 0.057986 | -0.35965 | -0.078656 | 1.1074 | 0.4777 | 0.83736 | 0.04877 | -0.076229 | 123.3282 | 123.2145 | 123.3933 | 47.2204 | -123.5221 | 123.2566 | 123.384 | 123.259 | 43.8902 | -123.6949
477.25 | 123.5092 | -65.6845 | 57.6553 | 0.049183 | -0.02651 | -0.0018439 | 0.048054 | -0.006137 | 0.051501 | 0.066374 | -0.0042204 | -0.0037179 | 0.058496 | 0.049114 | 0.055238 | -65.1952 | -18.7159 | -65.3496 | 57.694 | 57.5895 | 57.7637 | -65.7935 | -64.4489 | -22.1377 | -65.1198 | 57.6362 | 57.759 | 57.6295 | -65.9755 | -0.10901 | 0.038697 | 0.48931 | 0.33488 | 0.44389 | -0.065841 | 0.10834 | -0.29098 | -0.019141 | 1.2356 | 0.56469 | 0.85567 | 0.10371 | -0.025871 | 123.3785 | 123.274 | 123.4482 | 46.9686 | -123.4489 | 123.3207 | 123.4436 | 123.314 | 43.5468 | -123.6308
478.2344 | 123.5413 | -65.5975 | 57.7423 | 0.049183 | -0.025442 | -0.0039799 | 0.050191 | -0.007206 | 0.049364 | 0.081635 | -0.0042204 | -0.0037179 | 0.055291 | 0.048045 | 0.056307 | -65.1494 | -18.9403 | -65.3084 | 57.7398 | 57.6215 | 57.8003 | -65.7615 | -64.3527 | -22.6688 | -65.0328 | 57.6637 | 57.7911 | 57.6615 | -65.9434 | -0.16393 | -0.002495 | 0.44812 | 0.28911 | 0.45304 | -0.12077 | 0.057997 | -0.3459 | -0.078647 | 1.2448 | 0.56471 | 0.91061 | 0.048782 | -0.080796 | 123.3373 | 123.2191 | 123.3978 | 46.6573 | -123.5038 | 123.2612 | 123.3886 | 123.259 | 42.9287 | -123.6857
479.25 | 123.5687 | -65.5563 | 57.7148 | 0.064445 | -0.028647 | -0.0029119 | 0.046985 | -0.008274 | 0.050433 | 0.081635 | -0.0042204 | -0.0047869 | 0.057427 | 0.048045 | 0.055238 | -65.0762 | -19.2699 | -65.2443 | 57.7764 | 57.6582 | 57.8461 | -65.7065 | -64.2291 | -23.0763 | -64.9596 | 57.7232 | 57.8323 | 57.6936 | -65.9022 | -0.15018 | 0.061598 | 0.48018 | 0.31201 | 0.46219 | -0.056667 | 0.13125 | -0.34589 | 0.00834 | 1.3272 | 0.59677 | 0.94266 | 0.11745 | -0.02128 | 123.3328 | 123.2145 | 123.4024 | 46.2864 | -123.4214 | 123.2795 | 123.3886 | 123.2499 | 42.48 | -123.6171
480.2344 | 123.5046 | -65.5334 | 57.8293 | 0.079707 | -0.02651 | -0.00077494 | 0.049122 | -0.007206 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.055291 | 0.046977 | 0.055238 | -65.0166 | -19.7232 | -65.194 | 57.8222 | 57.7131 | 57.8873 | -65.6836 | -64.1238 | -23.4518 | -64.8771 | 57.7507 | 57.8781 | 57.7394 | -65.861 | -0.15018 | -0.007059 | 0.51681 | 0.33948 | 0.48966 | -0.11616 | 0.058016 | -0.32757 | -0.07863 | 1.4097 | 0.6563 | 0.98387 | 0.0488 | -0.089935 | 123.3557 | 123.2466 | 123.4207 | 45.8102 | -123.5129 | 123.2841 | 123.4115 | 123.2728 | 42.0817 | -123.6903
481.2344 | 123.5138 | -65.5472 | 57.8384 | 0.079707 | -0.02651 | -0.0039799 | 0.049122 | -0.008274 | 0.050433 | 0.051113 | -0.0031524 | -0.0047869 | 0.055291 | 0.050182 | 0.05417 | -64.9754 | -20.0208 | -65.1619 | 57.8497 | 57.7177 | 57.9056 | -65.6653 | -64.0185 | -23.8135 | -64.813 | 57.7781 | 57.901 | 57.7668 | -65.8381 | -0.11813 | 0.011256 | 0.57175 | 0.38526 | 0.50339 | -0.12074 | 0.067175 | -0.29094 | -0.060314 | 1.5287 | 0.73413 | 1.0251 | 0.062538 | -0.071619 | 123.3969 | 123.2649 | 123.4528 | 45.5264 | -123.5037 | 123.3253 | 123.4482 | 123.314 | 41.7337 | -123.6766
482.25 | 123.6008 | -65.4785 | 57.8293 | 0.049183 | -0.027578 | -0.0018439 | 0.049122 | -0.007206 | 0.049364 | 0.081635 | -0.0031524 | -0.0037179 | 0.056359 | 0.048045 | 0.056307 | -64.9388 | -20.3871 | -65.1207 | 57.8589 | 57.7406 | 57.9239 | -65.6516 | -63.9223 | -24.2714 | -64.7581 | 57.7873 | 57.9239 | 57.7806 | -65.8198 | -0.17306 | 0.029568 | 0.53971 | 0.3578 | 0.53086 | -0.088688 | 0.094645 | -0.34129 | -0.042002 | 1.5562 | 0.72042 | 1.0617 | 0.094586 | -0.048728 | 123.3374 | 123.2191 | 123.4024 | 45.0914 | -123.4809 | 123.2658 | 123.4024 | 123.2591 | 41.2071 | -123.6491
483.2344 | 123.4909 | -65.4282 | 57.8842 | 0.064445 | -0.02651 | -0.0018439 | 0.050191 | -0.008274 | 0.050433 | 0.066374 | -0.0042204 | -0.0058549 | 0.056359 | 0.05125 | 0.056307 | -64.8793 | -20.5519 | -65.0704 | 57.9001 | 57.791 | 57.9651 | -65.6104 | -63.7895 | -24.5598 | -64.6803 | 57.8376 | 57.9605 | 57.8309 | -65.7832 | -0.1822 | 0.015842 | 0.54887 | 0.35781 | 0.54001 | -0.09325 | 0.080921 | -0.35502 | -0.04657 | 1.6386 | 0.7479 | 1.1029 | 0.076284 | -0.053294 | 123.3282 | 123.2191 | 123.3933 | 44.8762 | -123.4946 | 123.2658 | 123.3887 | 123.2591 | 40.8683 | -123.6674
484.25 | 123.5596 | -65.387 | 57.9025 | 0.064445 | -0.025442 | -0.0018439 | 0.048054 | -0.006137 | 0.051501 | 0.066374 | -0.0042204 | -0.0037179 | 0.055291 | 0.050182 | 0.056307 | -64.8015 | -20.9915 | -65.0017 | 57.9458 | 57.8368 | 58.0155 | -65.5279 | -63.6293 | -24.7109 | -64.5795 | 57.888 | 58.0109 | 57.8767 | -65.7237 | -0.14098 | 0.043315 | 0.58551 | 0.38528 | 0.52626 | -0.065772 | 0.11297 | -0.33669 | -0.014517 | 1.7577 | 0.80743 | 1.1441 | 0.10834 | -0.025819 | 123.3328 | 123.2237 | 123.4025 | 44.3955 | -123.4305 | 123.275 | 123.3978 | 123.2637 | 40.676 | -123.6262
485.2344 | 123.4818 | -65.3778 | 58.0078 | 0.064445 | -0.024373 | -0.0039799 | 0.050191 | -0.006137 | 0.051501 | 0.020591 | -0.0020844 | -0.0015819 | 0.055291 | 0.050182 | 0.056307 | -64.7236 | -21.3166 | -64.9422 | 58.0008 | 57.8825 | 58.0613 | -65.5096 | -63.4919 | -24.9216 | -64.4788 | 57.9338 | 58.0567 | 57.9225 | -65.6824 | -0.13182 | -0.007029 | 0.65419 | 0.43565 | 0.56746 | -0.12527 | 0.053476 | -0.30464 | -0.074017 | 1.8859 | 0.89901 | 1.2036 | 0.048839 | -0.085318 | 123.3786 | 123.2604 | 123.4391 | 44.0612 | -123.5174 | 123.3116 | 123.4345 | 123.3003 | 40.4562 | -123.6903
486.2344 | 123.7244 | -65.3687 | 58.0399 | 0.049183 | -0.02651 | -0.0018439 | 0.048054 | -0.008274 | 0.051501 | 0.066374 | -0.0031524 | -0.0037179 | 0.055291 | 0.048045 | 0.057375 | -64.6733 | -21.5272 | -64.7911 | 58.0237 | 57.91 | 58.0979 | -65.4684 | -63.2905 | -24.9032 | -64.3872 | 57.9613 | 58.0841 | 57.9454 | -65.6504 | -0.099763 | -0.016181 | 0.69539 | 0.57757 | 0.67734 | -0.12984 | 0.058061 | -0.28174 | -0.07859 | 2.0782 | 0.98143 | 1.2632 | 0.044266 | -0.094469 | 123.3923 | 123.2787 | 123.4666 | 43.8415 | -123.5083 | 123.3299 | 123.4528 | 123.314 | 40.4654 | -123.6902
487.25 | 123.5184 | -65.2908 | 58.0536 | 0.064445 | -0.02651 | -0.0039799 | 0.050191 | -0.006137 | 0.050433 | 0.066374 | -0.0042204 | -0.0026499 | 0.057427 | 0.049114 | 0.056307 | -64.6 | -22.1224 | -64.8369 | 58.0649 | 57.9421 | 58.1254 | -65.4409 | -63.2035 | -25.3794 | -64.314 | 57.9979 | 58.1253 | 57.982 | -65.6183 | -0.15011 | 0.011291 | 0.69083 | 0.45397 | 0.60408 | -0.11152 | 0.071799 | -0.32751 | -0.055695 | 2.0874 | 0.97687 | 1.3044 | 0.071741 | -0.071573 | 123.3557 | 123.2329 | 123.4162 | 43.1684 | -123.4945 | 123.2887 | 123.4162 | 123.2728 | 39.9114 | -123.6719
488.2344 | 123.4314 | -65.2771 | 58.0582 | 0.064445 | -0.02651 | -0.0018439 | 0.049122 | -0.006137 | 0.050433 | 0.066374 | -0.0052884 | -0.0015819 | 0.056359 | 0.049114 | 0.055238 | -64.5039 | -23.061 | -64.7316 | 58.1336 | 58.0153 | 58.1941 | -65.3768 | -63.0249 | -25.5214 | -64.1903 | 58.0666 | 58.1986 | 58.069 | -65.5497 | -0.099737 | 0.075389 | 0.77324 | 0.54554 | 0.64528 | -0.042834 | 0.1359 | -0.27256 | 0.008404 | 2.2522 | 1.0868 | 1.3593 | 0.14042 | 0.010842 | 123.4107 | 123.2924 | 123.4712 | 42.2161 | -123.435 | 123.3437 | 123.4757 | 123.3461 | 39.7557 | -123.6078
489.25 | 123.587 | -65.1535 | 58.1451 | 0.049183 | -0.025442 | -0.0029119 | 0.048054 | -0.007206 | 0.051501 | 0.051113 | -0.0042204 | -0.0026499 | 0.056359 | 0.049114 | 0.056307 | -64.4443 | -23.5051 | -64.6583 | 58.1748 | 58.0657 | 58.2444 | -65.3219 | -62.8555 | -25.6908 | -64.0896 | 58.1078 | 58.2352 | 58.1011 | -65.5084 | -0.16839 | 0.02962 | 0.70916 | 0.49519 | 0.66358 | -0.079441 | 0.09929 | -0.35495 | -0.037364 | 2.298 | 1.0639 | 1.4188 | 0.090074 | -0.044083 | 123.3283 | 123.2192 | 123.3979 | 41.6484 | -123.467 | 123.2613 | 123.3887 | 123.2546 | 39.4627 | -123.6536
490.2344 | 123.4497 | -65.1489 | 58.2184 | 0.049183 | -0.02651 | -0.0029119 | 0.049122 | -0.007206 | 0.052569 | 0.035852 | -0.0031524 | -0.0037179 | 0.056359 | 0.049114 | 0.057375 | -64.339 | -24.0088 | -64.5622 | 58.2343 | 58.1298 | 58.3085 | -65.2715 | -62.654 | -25.8327 | -63.966 | 58.1673 | 58.2993 | 58.1514 | -65.4489 | -0.1226 | 0.015897 | 0.80989 | 0.58676 | 0.70936 | -0.088578 | 0.090148 | -0.3 | -0.051086 | 2.4949 | 1.1829 | 1.4829 | 0.080933 | -0.06696 | 123.3832 | 123.2787 | 123.4575 | 41.1401 | -123.4899 | 123.3162 | 123.4482 | 123.3004 | 39.3162 | -123.6673
491.2344 | 123.5046 | -65.0528 | 58.3008 | 0.064445 | -0.02651 | -0.0029119 | 0.048054 | -0.007206 | 0.050433 | 0.066374 | -0.0031524 | -0.0047869 | 0.054223 | 0.05125 | 0.057375 | -64.2292 | -24.5307 | -64.4706 | 58.3167 | 58.2031 | 58.3864 | -65.1845 | -62.4251 | -25.819 | -63.8286 | 58.2543 | 58.3817 | 58.243 | -65.3665 | -0.13173 | 0.015911 | 0.82364 | 0.5822 | 0.71392 | -0.097712 | 0.085588 | -0.31371 | -0.046492 | 2.6277 | 1.2242 | 1.5379 | 0.08095 | -0.057785 | 123.3695 | 123.2559 | 123.4392 | 40.522 | -123.4853 | 123.3071 | 123.4345 | 123.2958 | 39.2338 | -123.6673
492.25 | 123.5641 | -64.975 | 58.3008 | 0.049183 | -0.025442 | -0.0039799 | 0.049122 | -0.008274 | 0.051501 | 0.035852 | -0.0042204 | -0.0015819 | 0.056359 | 0.05125 | 0.055238 | -64.1513 | -24.9474 | -64.4111 | 58.3487 | 58.2351 | 58.4184 | -65.157 | -62.2374 | -25.9472 | -63.7279 | 58.2863 | 58.4184 | 58.2659 | -65.3253 | -0.18207 | 0.047959 | 0.82365 | 0.56389 | 0.74597 | -0.06566 | 0.11764 | -0.35032 | -0.014442 | 2.7376 | 1.2471 | 1.5974 | 0.11758 | -0.034892 | 123.3237 | 123.2101 | 123.3934 | 40.0276 | -123.4578 | 123.2613 | 123.3933 | 123.2409 | 39.0278 | -123.6261
493.2344 | 123.4955 | -64.9979 | 58.3923 | 0.033921 | -0.027578 | -0.0029119 | 0.049122 | -0.007206 | 0.050433 | 0.066374 | -0.0031524 | -0.0047869 | 0.057427 | 0.050182 | 0.056307 | -64.0689 | -25.4648 | -64.3333 | 58.4037 | 58.2946 | 58.4642 | -65.0929 | -62.0405 | -26.0159 | -63.6088 | 58.3275 | 58.4687 | 58.3208 | -65.2749 | -0.09508 | 0.011347 | 0.92895 | 0.66461 | 0.75969 | -0.097687 | 0.071871 | -0.27706 | -0.064789 | 2.9574 | 1.389 | 1.6661 | 0.076391 | -0.071502 | 123.4015 | 123.2925 | 123.4621 | 39.5331 | -123.4853 | 123.3254 | 123.4666 | 123.3187 | 38.982 | -123.6673
494.25 | 123.5962 | -64.888 | 58.429 | 0.049183 | -0.027578 | -0.0018439 | 0.046985 | -0.008274 | 0.050433 | 0.066374 | -0.0052884 | -0.0047869 | 0.054223 | 0.05125 | 0.057375 | -63.9957 | -25.9593 | -64.2646 | 58.4312 | 58.3359 | 58.5054 | -65.0655 | -61.8299 | -26.0983 | -63.5035 | 58.3733 | 58.5008 | 58.3483 | -65.2475 | -0.17747 | 0.002196 | 0.89234 | 0.62342 | 0.80089 | -0.093097 | 0.076457 | -0.35946 | -0.055625 | 3.0582 | 1.3845 | 1.7439 | 0.07182 | -0.080651 | 123.3192 | 123.2239 | 123.3934 | 38.9287 | -123.4944 | 123.2613 | 123.3888 | 123.2363 | 38.7897 | -123.6764
495.2344 | 123.4268 | -64.8743 | 58.5342 | 0.049183 | -0.028647 | -0.0029119 | 0.048054 | -0.007206 | 0.051501 | 0.066374 | -0.0031524 | -0.0026499 | 0.055291 | 0.049114 | 0.057375 | -63.9087 | -26.3759 | -64.1455 | 58.5181 | 58.3862 | 58.5787 | -64.9693 | -61.5551 | -26.08 | -63.3479 | 58.4466 | 58.574 | 58.4261 | -65.1742 | -0.095045 | -0.0161 | 0.9656 | 0.72873 | 0.82377 | -0.14802 | 0.044429 | -0.29993 | -0.087655 | 3.3191 | 1.5264 | 1.8263 | 0.039792 | -0.1081 | 123.3924 | 123.2605 | 123.4529 | 38.4983 | -123.5036 | 123.3209 | 123.4483 | 123.3004 | 38.7943 | -123.7084
496.2344 | 123.5184 | -64.7919 | 58.5938 | 0.064445 | -0.028647 | -0.0029119 | 0.049122 | -0.006137 | 0.050433 | 0.081635 | -0.0031524 | -0.0015819 | 0.057427 | 0.05125 | 0.058443 | -63.7896 | -26.8796 | -64.0769 | 58.5685 | 58.4503 | 58.6336 | -64.951 | -61.3445 | -26.199 | -63.2197 | 58.5015 | 58.6336 | 58.4765 | -65.1147 | -0.15913 | -0.025247 | 1.0022 | 0.715 | 0.87413 | -0.14342 | 0.039863 | -0.3228 | -0.092222 | 3.4474 | 1.5722 | 1.895 | 0.039805 | -0.11724 | 123.3604 | 123.2422 | 123.4255 | 37.9123 | -123.5447 | 123.2934 | 123.4254 | 123.2684 | 38.5929 | -123.7084
497.25 | 123.6008 | -64.6912 | 58.5846 | 0.049183 | -0.028647 | -0.0029119 | 0.048054 | -0.006137 | 0.051501 | 0.051113 | -0.0052884 | -0.00051292 | 0.057427 | 0.052319 | 0.057375 | -63.6797 | -27.342 | -63.9807 | 58.6189 | 58.5053 | 58.7023 | -64.864 | -61.0698 | -26.199 | -63.0823 | 58.5565 | 58.6931 | 58.5406 | -65.0551 | -0.17283 | 0.03427 | 1.0114 | 0.71044 | 0.88327 | -0.079317 | 0.1177 | -0.36398 | -0.028125 | 3.6214 | 1.6089 | 1.9729 | 0.10848 | -0.04399 | 123.31 | 123.1964 | 123.3935 | 37.3492 | -123.4486 | 123.2476 | 123.3842 | 123.2318 | 38.4921 | -123.6397
498.2344 | 123.4955 | -64.6637 | 58.6761 | 0.033921 | -0.027578 | -0.0039799 | 0.048054 | -0.007206 | 0.051501 | 0.051113 | -0.0031524 | -0.00051292 | 0.055291 | 0.052319 | 0.057375 | -63.5836 | -27.6305 | -63.8892 | 58.683 | 58.5648 | 58.7481 | -64.8228 | -60.8225 | -26.167 | -62.9266 | 58.616 | 58.748 | 58.5864 | -64.991 | -0.15909 | 0.006816 | 1.0801 | 0.77454 | 0.93363 | -0.11134 | 0.071931 | -0.32735 | -0.060157 | 3.8412 | 1.7371 | 2.0644 | 0.071873 | -0.089756 | 123.3467 | 123.2285 | 123.4118 | 37.0332 | -123.4989 | 123.2797 | 123.4117 | 123.2501 | 38.4967 | -123.6672
499.25 | 123.6053 | -64.5813 | 58.7631 | 0.064445 | -0.027578 | -0.0018439 | 0.048054 | -0.006137 | 0.051501 | 0.051113 | -0.0042204 | -0.0026499 | 0.058496 | 0.052319 | 0.056307 | -63.4554 | -28.0196 | -63.7839 | 58.7608 | 58.6426 | 58.8213 | -64.7358 | -60.4929 | -26.112 | -62.7755 | 58.6892 | 58.8259 | 58.678 | -64.9269 | -0.15449 | -0.002328 | 1.1259 | 0.79744 | 0.95193 | -0.12048 | 0.058213 | -0.34564 | -0.073877 | 4.0884 | 1.8058 | 2.1514 | 0.062733 | -0.08516 | 123.3421 | 123.2239 | 123.4026 | 36.5617 | -123.4989 | 123.2705 | 123.4072 | 123.2593 | 38.4693 | -123.6901
500.2344 | 123.4772 | -64.5355 | 58.7997 | 0.094969 | -0.029715 | -0.0050489 | 0.048054 | -0.007206 | 0.051501 | 0.051113 | -0.0020844 | -0.0015819 | 0.057427 | 0.050182 | 0.057375 | -63.3364 | -28.3127 | -63.674 | 58.834 | 58.7159 | 58.9038 | -64.6671 | -60.209 | -25.938 | -62.6015 | 58.7625 | 58.8945 | 58.7512 | -64.8491 | -0.13158 | 0.034305 | 1.1992 | 0.86154 | 0.99312 | -0.083836 | 0.10401 | -0.31358 | -0.037242 | 4.3265 | 1.934 | 2.2476 | 0.094791 | -0.048523 | 123.3696 | 123.2514 | 123.4393 | 36.2229 | -123.4668 | 123.298 | 123.4301 | 123.2867 | 38.5975 | -123.6488
501.2344 | 123.4863 | -64.5081 | 58.8684 | 0.033921 | -0.027578 | -0.0029119 | 0.046985 | -0.007206 | 0.051501 | 0.051113 | -0.0031524 | -0.0026499 | 0.057427 | 0.05125 | 0.058443 | -63.2311 | -28.6423 | -63.587 | 58.8798 | 58.7754 | 58.945 | -64.6259 | -59.861 | -25.7137 | -62.4504 | 58.8129 | 58.9449 | 58.8016 | -64.8033 | -0.11784 | 0.011425 | 1.277 | 0.92107 | 1.0389 | -0.092974 | 0.07655 | -0.29525 | -0.055542 | 4.6471 | 2.0576 | 2.3529 | 0.076492 | -0.066822 | 123.3879 | 123.2835 | 123.453 | 35.8657 | -123.4943 | 123.3209 | 123.453 | 123.3096 | 38.7944 | -123.6717
502.2344 | 123.5825 | -64.4669 | 58.9233 | 0.064445 | -0.027578 | -0.00077494 | 0.048054 | -0.008274 | 0.051501 | 0.066374 | -0.0063574 | -0.0037179 | 0.056359 | 0.05125 | 0.058443 | -63.1258 | -28.798 | -63.3443 | 58.8936 | 58.7846 | 58.9587 | -64.5984 | -59.3848 | -25.0543 | -62.2902 | 58.8312 | 58.9541 | 58.8016 | -64.785 | -0.13156 | -0.029772 | 1.3411 | 1.1225 | 1.2541 | -0.13875 | 0.035354 | -0.31814 | -0.09216 | 5.082 | 2.1767 | 2.4948 | 0.030717 | -0.12175 | 123.3604 | 123.2515 | 123.4256 | 35.6689 | -123.5218 | 123.298 | 123.4209 | 123.2684 | 39.4125 | -123.7083
503.2344 | 123.4497 | -64.4302 | 58.9554 | 0.049183 | -0.027578 | -0.0029119 | 0.049122 | -0.008274 | 0.050433 | 0.096896 | -0.0052884 | -0.0015819 | 0.055291 | 0.052319 | 0.059511 | -63.0937 | -29.1597 | -63.4725 | 58.9165 | 58.8121 | 58.977 | -64.5847 | -59.3116 | -25.4802 | -62.1757 | 58.8449 | 58.977 | 58.8291 | -64.7667 | -0.15445 | -0.038923 | 1.3365 | 0.9577 | 1.1121 | -0.14332 | 0.021625 | -0.33644 | -0.11047 | 5.1187 | 2.2545 | 2.591 | 0.021567 | -0.12633 | 123.3467 | 123.2423 | 123.4072 | 35.2705 | -123.5401 | 123.2752 | 123.4072 | 123.2593 | 38.9501 | -123.7221
504.2344 | 123.6145 | -64.389 | 58.9325 | 0.064445 | -0.02651 | -0.0018439 | 0.048054 | -0.007206 | 0.050433 | 0.066374 | -0.0020844 | -0.00051292 | 0.057427 | 0.052319 | 0.059511 | -62.993 | -29.3657 | -63.3993 | 58.9485 | 58.835 | 59.0091 | -64.5572 | -58.9819 | -24.9994 | -62.0063 | 58.877 | 59.0136 | 58.8748 | -64.7346 | -0.16817 | 0.016014 | 1.396 | 0.98976 | 1.1579 | -0.097535 | 0.076564 | -0.34559 | -0.05553 | 5.4071 | 2.3827 | 2.7283 | 0.081084 | -0.057652 | 123.3375 | 123.224 | 123.3981 | 35.0233 | -123.4897 | 123.266 | 123.4026 | 123.2639 | 39.3896 | -123.6671
505.2344 | 123.5229 | -64.682 | 58.6716 | 0.049183 | -0.027578 | -0.0029119 | 0.048054 | -0.006137 | 0.052569 | 0.081635 | -0.0031524 | 0.00055508 | 0.057427 | 0.053387 | 0.057375 | -63.167 | -29.6542 | -63.5961 | 58.7104 | 58.6014 | 58.7847 | -64.7816 | -58.6522 | -23.8776 | -62.0383 | 58.6435 | 58.7755 | 58.6322 | -64.9727 | -0.09957 | 0.038863 | 1.515 | 1.0859 | 1.1854 | -0.070135 | 0.11314 | -0.29072 | -0.028109 | 6.0298 | 2.6437 | 2.9344 | 0.10392 | -0.039393 | 123.3924 | 123.2834 | 123.4667 | 35.0278 | -123.4531 | 123.3255 | 123.4575 | 123.3142 | 40.8044 | -123.6443
506.2344 | 123.5184 | -64.7644 | 58.5938 | 0.049183 | -0.027578 | -0.0029119 | 0.049122 | -0.006137 | 0.051501 | 0.066374 | -0.0042204 | -0.00051292 | 0.058496 | 0.052319 | 0.06058 | -63.199 | -29.9427 | -63.6465 | 58.6097 | 58.4915 | 58.6702 | -64.9006 | -58.3226 | -23.5113 | -61.9697 | 58.5382 | 58.6702 | 58.536 | -65.0689 | -0.13622 | 0.015958 | 1.5654 | 1.1179 | 1.2541 | -0.10221 | 0.076492 | -0.30448 | -0.055594 | 6.4418 | 2.7947 | 3.0992 | 0.076433 | -0.057723 | 123.3741 | 123.2559 | 123.4346 | 34.8217 | -123.4944 | 123.3026 | 123.4346 | 123.3004 | 41.2531 | -123.6626
507.25 | 123.5916 | -64.7095 | 58.6075 | 0.033921 | -0.028647 | -0.0039799 | 0.049122 | -0.007206 | 0.050433 | 0.051113 | -0.0042204 | 0.0016231 | 0.055291 | 0.052319 | 0.06058 | -63.0846 | -30.1991 | -63.5504 | 58.6601 | 58.5511 | 58.7206 | -64.8503 | -57.6907 | -23.5617 | -61.7499 | 58.5931 | 58.716 | 58.5772 | -65.0185 | -0.14079 | 0.052588 | 1.6249 | 1.1591 | 1.2999 | -0.056416 | 0.11312 | -0.30904 | -0.014385 | 7.0188 | 2.9596 | 3.2686 | 0.10849 | -0.030249 | 123.3695 | 123.2605 | 123.4301 | 34.5104 | -123.4577 | 123.3026 | 123.4254 | 123.2867 | 41.1478 | -123.626
508.2344 | 123.4589 | -64.6408 | 58.7128 | 0.033921 | -0.028647 | -0.0029119 | 0.048054 | -0.006137 | 0.049364 | 0.081635 | -0.0020844 | 0.0016231 | 0.056359 | 0.054456 | 0.06058 | -62.8419 | -30.4234 | -63.3352 | 58.8295 | 58.7205 | 58.8992 | -64.6717 | -56.6376 | -23.493 | -61.3836 | 58.7671 | 58.89 | 58.7604 | -64.8445 | -0.030875 | 0.1167 | 1.7989 | 1.3056 | 1.3365 | 0.007718 | 0.1864 | -0.20371 | 0.054312 | 8.0032 | 3.2572 | 3.4609 | 0.17719 | 0.047609 | 123.4703 | 123.3613 | 123.54 | 34.2174 | -123.3845 | 123.4079 | 123.5308 | 123.4012 | 41.1478 | -123.5573
509.2344 | 123.5229 | -64.8422 | 58.5571 | 0.079707 | -0.028647 | -0.00077494 | 0.048054 | -0.007206 | 0.051501 | 0.066374 | -0.0042204 | 0.0026921 | 0.058496 | 0.054456 | 0.06058 | -62.906 | -30.6523 | -63.4313 | 58.6875 | 58.5877 | 58.7572 | -64.809 | -55.8867 | -22.5635 | -61.3149 | 58.6206 | 58.7526 | 58.6139 | -64.991 | 0.033174 | 0.13041 | 1.9362 | 1.4109 | 1.3777 | 0.030569 | 0.20011 | -0.14882 | 0.06344 | 8.9555 | 3.5273 | 3.6761 | 0.19547 | 0.056734 | 123.5298 | 123.4299 | 123.5995 | 34.1899 | -123.3662 | 123.4628 | 123.5948 | 123.4561 | 42.2787 | -123.5482
510.2344 | 123.5275 | -64.8239 | 58.4976 | 0.049183 | -0.027578 | -0.0029119 | 0.049122 | -0.007206 | 0.050433 | 0.066374 | -0.0020844 | 0.00055508 | 0.054223 | 0.054456 | 0.062716 | -62.9518 | -30.982 | -63.4954 | 58.5777 | 58.4686 | 58.6473 | -64.9327 | -55.6669 | -22.5269 | -61.2325 | 58.5061 | 58.6381 | 58.4902 | -65.1101 | -0.10877 | 0.08004 | 1.8721 | 1.3285 | 1.4373 | -0.028974 | 0.14973 | -0.28618 | 0.008487 | 9.157 | 3.5914 | 3.8776 | 0.14051 | -0.007379 | 123.4016 | 123.2926 | 123.4713 | 33.8419 | -123.4303 | 123.33 | 123.462 | 123.3142 | 42.297 | -123.6077
511.2344 | 123.4772 | -65.1215 | 58.2642 | 0.064445 | -0.028647 | -0.0039799 | 0.050191 | -0.007206 | 0.051501 | 0.051113 | -0.0042204 | 0.0016231 | 0.055291 | 0.053387 | 0.061648 | -63.1349 | -31.71 | -63.7198 | 58.303 | 58.1756 | 58.3681 | -65.1891 | -55.2274 | -21.428 | -61.2554 | 58.2268 | 58.3588 | 58.2293 | -65.3802 | -0.067641 | 0.038796 | 1.9865 | 1.4017 | 1.4693 | -0.088565 | 0.10389 | -0.25878 | -0.037342 | 9.8941 | 3.8661 | 4.1249 | 0.094678 | -0.0349 | 123.4244 | 123.2971 | 123.4895 | 33.4115 | -123.4533 | 123.3483 | 123.4803 | 123.3507 | 43.6935 | -123.6444
512.25 | 123.6053 | -65.1855 | 58.1085 | 0.079707 | -0.028647 | -0.0039799 | 0.049122 | -0.007206 | 0.052569 | 0.096896 | -0.0042204 | 0.0026921 | 0.057427 | 0.054456 | 0.061648 | -63.0525 | -31.8153 | -63.6602 | 58.3075 | 58.1939 | 58.3772 | -65.1937 | -54.6138 | -20.4207 | -60.9257 | 58.2314 | 58.368 | 58.2247 | -65.3711 | -0.008133 | 0.19901 | 2.133 | 1.5253 | 1.5334 | 0.08539 | 0.26869 | -0.18554 | 0.12288 | 10.5717 | 4.2598 | 4.4454 | 0.25947 | 0.11616 | 123.4931 | 123.3795 | 123.5628 | 33.3702 | -123.3022 | 123.4169 | 123.5535 | 123.4102 | 44.7649 | -123.4796
513.2344 | 123.4863 | -64.7095 | 58.6395 | 0.049183 | -0.02651 | -0.0029119 | 0.048054 | -0.006137 | 0.051501 | 0.051113 | -0.0042204 | 0.0037601 | 0.058496 | 0.055524 | 0.062716 | -62.6633 | -31.7375 | -63.294 | 58.6143 | 58.4961 | 58.6794 | -64.8732 | -53.8675 | -19.7476 | -60.4404 | 58.5473 | 58.6748 | 58.5269 | -65.0643 | -0.16368 | -0.025239 | 2.0461 | 1.4155 | 1.5792 | -0.14341 | 0.039873 | -0.35483 | -0.092213 | 10.842 | 4.2691 | 4.6239 | 0.035236 | -0.11266 | 123.3238 | 123.2056 | 123.3889 | 32.972 | -123.5127 | 123.2568 | 123.3842 | 123.2363 | 44.9619 | -123.7038
514.2344 | 123.4589 | -64.2517 | 59.1568 | 0.064445 | -0.027578 | -0.0018439 | 0.049122 | -0.007206 | 0.052569 | 0.051113 | -0.0020844 | 0.0037601 | 0.057427 | 0.054456 | 0.063784 | -62.0727 | -31.4307 | -62.7354 | 59.1179 | 59.009 | 59.183 | -64.3832 | -52.1047 | -18.4931 | -59.6483 | 59.0509 | 59.1738 | 59.0397 | -64.5515 | -0.1315 | -0.03889 | 2.179 | 1.5163 | 1.6478 | -0.14784 | 0.026246 | -0.29977 | -0.10585 | 12.147 | 4.6034 | 4.9032 | 0.017031 | -0.11713 | 123.3696 | 123.2607 | 123.4348 | 32.821 | -123.54 | 123.3027 | 123.4255 | 123.2914 | 45.7587 | -123.7083
515.2344 | 123.4634 | -64.7598 | 58.6578 | 0.064445 | -0.02651 | -0.0018439 | 0.050191 | -0.007206 | 0.052569 | 0.066374 | -0.0042204 | 0.0026921 | 0.057427 | 0.055524 | 0.063784 | -62.178 | -31.7466 | -62.8774 | 58.9256 | 58.8075 | 58.9862 | -64.5847 | -52.4023 | -17.8383 | -59.5933 | 58.8541 | 58.9724 | 58.8336 | -64.7621 | 0.17514 | 0.26778 | 2.5818 | 1.8825 | 1.7073 | 0.14965 | 0.32833 | -0.002275 | 0.19624 | 12.3575 | 5.1665 | 5.1688 | 0.31453 | 0.1758 | 123.6854 | 123.5673 | 123.746 | 33.0132 | -123.2425 | 123.6139 | 123.7322 | 123.5935 | 46.9215 | -123.4199
516.2344 | 123.4726 | -64.6317 | 58.699 | 0.064445 | -0.028647 | -0.0018439 | 0.049122 | -0.008274 | 0.051501 | 0.051113 | -0.0031524 | 0.0058961 | 0.058496 | 0.056592 | 0.063784 | -62.0956 | -31.8748 | -62.8224 | 58.9119 | 58.7846 | 58.9679 | -64.603 | -52.0039 | -17.0324 | -59.282 | 58.8358 | 58.9586 | 58.8016 | -64.7758 | 0.028654 | 0.21285 | 2.536 | 1.8092 | 1.7806 | 0.085556 | 0.26882 | -0.14418 | 0.13672 | 12.6277 | 5.3497 | 5.4939 | 0.2596 | 0.10255 | 123.5435 | 123.4162 | 123.5995 | 32.7568 | -123.302 | 123.4674 | 123.5903 | 123.4332 | 47.5992 | -123.4749
517.25 | 123.5458 | -64.3433 | 58.9828 | 0.049183 | -0.027578 | -0.0018439 | 0.050191 | -0.007206 | 0.052569 | 0.066374 | -0.0031524 | 0.0048281 | 0.058496 | 0.056592 | 0.064853 | -62.3108 | -32.2091 | -63.0651 | 58.5868 | 58.4824 | 58.6473 | -64.8961 | -51.7842 | -16.6982 | -59.227 | 58.5336 | 58.6519 | 58.5269 | -65.0826 | -0.55279 | -0.39603 | 2.0325 | 1.2782 | 1.831 | -0.50047 | -0.3355 | -0.73936 | -0.44927 | 12.5591 | 5.1162 | 5.8556 | -0.33098 | -0.45598 | 122.9301 | 122.8256 | 122.9906 | 32.1342 | -123.8789 | 122.8768 | 122.9951 | 122.8701 | 47.6451 | -124.0655
518.2344 | 123.4497 | -64.6317 | 58.7585 | 0.049183 | -0.028647 | -0.0039799 | 0.049122 | -0.007206 | 0.052569 | 0.035852 | -0.0031524 | 0.0026921 | 0.059564 | 0.055524 | 0.064853 | -62.0178 | -32.0351 | -62.8087 | 58.7883 | 58.6701 | 58.8488 | -64.7175 | -51.1477 | -16.277 | -58.6776 | 58.7076 | 58.8396 | 58.7146 | -64.8903 | -0.085819 | 0.029721 | 2.6139 | 1.823 | 1.9088 | -0.088426 | 0.090262 | -0.25866 | -0.050985 | 13.4839 | 5.9541 | 6.2127 | 0.081047 | -0.043953 | 123.4199 | 123.3018 | 123.4805 | 32.5966 | -123.476 | 123.3392 | 123.4712 | 123.3462 | 48.3547 | -123.6489
519.2344 | 123.4726 | -64.4577 | 58.9005 | 0.064445 | -0.029715 | -0.0018439 | 0.050191 | -0.007206 | 0.051501 | 0.066374 | -0.0052884 | 0.0069651 | 0.057427 | 0.054456 | 0.062716 | -61.8667 | -31.9252 | -62.6988 | 58.8478 | 58.7205 | 58.9083 | -64.6579 | -50.992 | -15.9336 | -57.9404 | 58.7717 | 58.8991 | 58.7512 | -64.8354 | -0.20024 | -0.052667 | 2.591 | 1.7589 | 1.9591 | -0.17997 | 0.007877 | -0.37766 | -0.12879 | 13.4657 | 6.5173 | 6.895 | -0.001339 | -0.14923 | 123.3055 | 123.1782 | 123.366 | 32.5325 | -123.5584 | 123.2294 | 123.3568 | 123.2089 | 48.5242 | -123.7358
520.2344 | 123.4406 | -64.8148 | 58.5663 | 0.064445 | -0.029715 | -0.0018439 | 0.049122 | -0.007206 | 0.052569 | 0.051113 | -0.0031524 | 0.0069651 | 0.059564 | 0.058729 | 0.064853 | -62.0956 | -32.1266 | -62.9643 | 58.4998 | 58.3816 | 58.5741 | -64.9922 | -50.0488 | -16.0343 | -57.8259 | 58.4374 | 58.5649 | 58.4078 | -65.1834 | -0.17745 | -0.066457 | 2.7191 | 1.8504 | 2.0279 | -0.18464 | 0.007807 | -0.36859 | -0.12886 | 14.7659 | 6.9888 | 7.3574 | -0.001408 | -0.15846 | 123.3146 | 123.1964 | 123.3888 | 32.6881 | -123.5585 | 123.2522 | 123.3796 | 123.2226 | 48.7805 | -123.7496
521.2344 | 123.4863 | -64.8148 | 58.5342 | 0.049183 | -0.028647 | -0.0029119 | 0.049122 | -0.005069 | 0.050433 | 0.066374 | -0.0031524 | 0.0069651 | 0.058496 | 0.058729 | 0.065921 | -62.1277 | -32.3418 | -63.033 | 58.3625 | 58.2534 | 58.4276 | -65.1479 | -49.4673 | -15.7962 | -57.3085 | 58.3001 | 58.4275 | 58.2842 | -65.3161 | -0.33313 | -0.17177 | 2.6871 | 1.7817 | 2.1149 | -0.2808 | -0.10666 | -0.50138 | -0.23417 | 15.3474 | 7.5062 | 8.0076 | -0.10672 | -0.25004 | 123.1772 | 123.0682 | 123.2423 | 32.4729 | -123.6821 | 123.1148 | 123.2423 | 123.099 | 49.0186 | -123.8504
522.25 | 123.5138 | -64.8148 | 58.5297 | 0.033921 | -0.027578 | -0.0018439 | 0.049122 | -0.006137 | 0.052569 | 0.051113 | -0.0031524 | 0.0058961 | 0.059564 | 0.057661 | 0.064853 | -61.8301 | -32.1038 | -62.7629 | 58.5548 | 58.4366 | 58.6245 | -64.9556 | -48.9087 | -15.5306 | -56.8736 | 58.4741 | 58.6152 | 58.4628 | -65.1238 | -0.14082 | 0.025105 | 2.9847 | 2.0519 | 2.1927 | -0.093069 | 0.094793 | -0.30907 | -0.055606 | 15.906 | 7.9412 | 8.2503 | 0.085577 | -0.066894 | 123.3695 | 123.2514 | 123.4392 | 32.711 | -123.4852 | 123.2888 | 123.43 | 123.2775 | 49.2841 | -123.6535
523.2344 | 123.5001 | -64.389 | 58.9966 | 0.064445 | -0.029715 | -0.0029119 | 0.049122 | -0.008274 | 0.050433 | 0.066374 | -0.0042204 | 0.0069651 | 0.058496 | 0.057661 | 0.068058 | -61.2074 | -31.5543 | -62.186 | 59.0584 | 58.954 | 59.1235 | -64.4519 | -48.0983 | -15.2376 | -55.9716 | 58.9823 | 59.1097 | 58.9847 | -64.6156 | -0.062856 | 0.061808 | 3.1816 | 2.203 | 2.2659 | -0.04257 | 0.12694 | -0.22654 | -0.014312 | 16.2907 | 8.4175 | 8.644 | 0.11315 | -0.011852 | 123.4474 | 123.3431 | 123.5126 | 32.8347 | -123.4485 | 123.3713 | 123.4988 | 123.3738 | 49.1515 | -123.6122
524.2344 | 123.5001 | -64.5401 | 58.8272 | 0.049183 | -0.028647 | -0.0018439 | 0.050191 | -0.007206 | 0.051501 | 0.066374 | -0.0020844 | 0.0069651 | 0.057427 | 0.057661 | 0.066989 | -61.3814 | -31.7741 | -62.3966 | 58.7608 | 58.6472 | 58.8305 | -64.7312 | -48.0021 | -15.5901 | -55.9899 | 58.6984 | 58.8259 | 58.6825 | -64.9132 | -0.19111 | -0.066414 | 3.1587 | 2.1435 | 2.3346 | -0.17998 | 0.003284 | -0.3731 | -0.12881 | 16.538 | 8.5502 | 8.9233 | -0.001353 | -0.14467 | 123.3009 | 123.1873 | 123.3706 | 32.766 | -123.5584 | 123.2385 | 123.366 | 123.2226 | 48.95 | -123.7404
525.2344 | 123.5275 | -64.6179 | 58.754 | 0.079707 | -0.028647 | -0.00077494 | 0.050191 | -0.006137 | 0.051501 | 0.081635 | -0.0042204 | 0.0069651 | 0.060632 | 0.059797 | 0.066989 | -61.1708 | -31.5772 | -62.2227 | 58.8615 | 58.7388 | 58.9266 | -64.6534 | -47.4023 | -15.2513 | -55.413 | 58.79 | 58.922 | 58.7695 | -64.8216 | -0.035447 | 0.10755 | 3.4471 | 2.3953 | 2.4307 | -0.015164 | 0.17268 | -0.20371 | 0.036006 | 17.2156 | 9.205 | 9.4087 | 0.16804 | 0.015568 | 123.4794 | 123.3567 | 123.5446 | 33.0407 | -123.4073 | 123.4079 | 123.5399 | 123.3875 | 49.3666 | -123.5756
526.2344 | 123.4818 | -64.2563 | 59.1202 | 0.064445 | -0.028647 | 0.00029306 | 0.049122 | -0.005069 | 0.051501 | 0.096896 | -0.0031524 | 0.0058961 | 0.060632 | 0.060866 | 0.068058 | -60.7633 | -31.2018 | -61.8427 | 59.1408 | 59.0364 | 59.2105 | -64.3649 | -47.1322 | -14.8072 | -54.5659 | 59.0693 | 59.2013 | 59.0671 | -64.5286 | -0.10861 | 0.020623 | 3.493 | 2.4136 | 2.5222 | -0.083745 | 0.090339 | -0.27229 | -0.050916 | 17.1241 | 9.6904 | 9.9627 | 0.081123 | -0.053033 | 123.3971 | 123.2927 | 123.4668 | 33.0545 | -123.4851 | 123.3255 | 123.4576 | 123.3234 | 49.4491 | -123.6488
527.25 | 123.6008 | -64.6088 | 58.6578 | 0.033921 | -0.029715 | -0.0018439 | 0.048054 | -0.007206 | 0.052569 | 0.051113 | -0.0052884 | 0.0080331 | 0.0617 | 0.059797 | 0.068058 | -60.9968 | -31.3529 | -62.1403 | 58.7516 | 58.6518 | 58.8122 | -64.7404 | -45.9188 | -13.6396 | -54.5064 | 58.6892 | 58.8121 | 58.6505 | -64.9224 | -0.1316 | 0.093801 | 3.612 | 2.4685 | 2.6001 | -0.006034 | 0.15434 | -0.31359 | 0.031409 | 18.6899 | 10.1024 | 10.416 | 0.15428 | -0.007345 | 123.3604 | 123.2606 | 123.4209 | 33.2559 | -123.3982 | 123.298 | 123.4209 | 123.2593 | 50.9691 | -123.5802
528.2344 | 123.4955 | -64.7232 | 58.6624 | 0.064445 | -0.029715 | 0.00029306 | 0.049122 | -0.006137 | 0.052569 | 0.081635 | -0.0031524 | 0.0091011 | 0.0617 | 0.060866 | 0.068058 | -60.9602 | -31.3025 | -62.1448 | 58.6601 | 58.5419 | 58.7343 | -64.8411 | -45.7265 | -13.0306 | -53.8287 | 58.5931 | 58.716 | 58.5772 | -65.0139 | -0.1179 | -0.002344 | 3.763 | 2.5784 | 2.6963 | -0.12051 | 0.071927 | -0.29073 | -0.069317 | 18.9967 | 10.8945 | 11.1852 | 0.053554 | -0.085181 | 123.3833 | 123.2651 | 123.4575 | 33.4207 | -123.5035 | 123.3163 | 123.4392 | 123.3004 | 51.6926 | -123.6764
529.2344 | 123.5138 | -65.6433 | 57.6553 | 0.033921 | -0.027578 | -0.00077494 | 0.051259 | -0.005069 | 0.053638 | 0.066374 | -0.0020844 | 0.0080331 | 0.062769 | 0.059797 | 0.069126 | -61.5004 | -31.5955 | -62.7446 | 57.9642 | 57.8459 | 58.0247 | -65.5325 | -45.7174 | -12.1882 | -54.3782 | 57.8926 | 58.02 | 57.8721 | -65.7191 | 0.11079 | 0.30882 | 4.1429 | 2.8987 | 2.7879 | 0.19058 | 0.36932 | -0.075764 | 0.23725 | 19.9259 | 11.2651 | 11.3409 | 0.36469 | 0.21679 | 123.6075 | 123.4892 | 123.668 | 34.0478 | -123.1879 | 123.5359 | 123.6633 | 123.5154 | 53.4551 | -123.3744
530.2344 | 123.5413 | -64.563 | 58.8135 | 0.064445 | -0.027578 | -0.00077494 | 0.051259 | -0.007206 | 0.051501 | 0.066374 | -0.0010164 | 0.0091011 | 0.0617 | 0.063002 | 0.070194 | -60.6672 | -30.7073 | -61.9754 | 58.6326 | 58.5144 | 58.6977 | -64.8503 | -45.0626 | -14.0975 | -52.1895 | 58.561 | 58.6931 | 58.5406 | -65.0414 | -0.28727 | -0.18088 | 3.8958 | 2.5876 | 2.8748 | -0.29904 | -0.11576 | -0.47842 | -0.25243 | 19.5004 | 12.3734 | 12.8519 | -0.1204 | -0.27287 | 123.1956 | 123.0774 | 123.2607 | 33.8557 | -123.6637 | 123.124 | 123.2561 | 123.1036 | 50.4655 | -123.8549
531.2344 | 123.5138 | -65.1031 | 58.2321 | 0.064445 | -0.027578 | -0.00077494 | 0.049122 | -0.005069 | 0.053638 | 0.096896 | -0.0020844 | 0.0091011 | 0.0617 | 0.061934 | 0.071262 | -60.8824 | -30.6981 | -62.2364 | 58.248 | 58.1481 | 58.3268 | -65.2532 | -43.3044 | -12.8567 | -53.2289 | 58.181 | 58.3085 | 58.1743 | -65.426 | -0.15006 | 0.015899 | 4.2208 | 2.8668 | 3.0168 | -0.083995 | 0.09473 | -0.32288 | -0.051084 | 21.7988 | 11.8742 | 12.1971 | 0.076357 | -0.0578 | 123.3512 | 123.2513 | 123.43 | 34.405 | -123.4853 | 123.2842 | 123.4116 | 123.2775 | 52.2465 | -123.6581
532.25 | 123.4955 | -64.7919 | 58.5434 | 0.049183 | -0.028647 | -0.00077494 | 0.048054 | -0.006137 | 0.053638 | 0.066374 | -0.0020844 | 0.012306 | 0.0617 | 0.065139 | 0.070194 | -60.397 | -30.3639 | -61.8472 | 58.5502 | 58.4412 | 58.6245 | -64.9602 | -43.6661 | -13.0627 | -52.098 | 58.4786 | 58.6152 | 58.4673 | -65.1238 | -0.16828 | 0.006793 | 4.3948 | 2.9446 | 3.1129 | -0.10222 | 0.08106 | -0.33196 | -0.06476 | 21.1258 | 12.6939 | 13.0259 | 0.071844 | -0.076048 | 123.3421 | 123.233 | 123.4163 | 34.428 | -123.5036 | 123.2705 | 123.4071 | 123.2592 | 51.7292 | -123.6672
533.2344 | 123.5229 | -64.6637 | 58.6578 | 0.064445 | -0.027578 | 0.00029306 | 0.050191 | -0.007206 | 0.053638 | 0.066374 | -0.0010164 | 0.011238 | 0.0617 | 0.063002 | 0.072331 | -60.159 | -29.9793 | -61.655 | 58.6372 | 58.5328 | 58.6977 | -64.8411 | -43.1167 | -12.7193 | -51.1914 | 58.561 | 58.6977 | 58.5452 | -65.0368 | -0.17741 | -0.020658 | 4.5047 | 3.0087 | 3.1861 | -0.12509 | 0.039877 | -0.37314 | -0.096788 | 21.547 | 13.4723 | 13.8454 | 0.039818 | -0.11265 | 123.3009 | 123.1964 | 123.3614 | 34.6844 | -123.4989 | 123.2247 | 123.3614 | 123.2089 | 51.9444 | -123.6947
534.2344 | 123.5321 | -64.9017 | 58.4656 | 0.064445 | -0.027578 | -0.00077494 | 0.049122 | -0.008274 | 0.055774 | 0.066374 | -0.0020844 | 0.013374 | 0.063837 | 0.066208 | 0.072331 | -60.2414 | -29.9884 | -61.8015 | 58.3808 | 58.2718 | 58.4505 | -65.125 | -42.3291 | -13.0352 | -49.7674 | 58.3092 | 58.4413 | 58.3117 | -65.2978 | -0.22326 | -0.084787 | 4.6604 | 3.1003 | 3.3235 | -0.19382 | -0.015107 | -0.39609 | -0.15635 | 22.5726 | 15.1343 | 15.5304 | -0.024323 | -0.1539 | 123.2825 | 123.1735 | 123.3522 | 34.9133 | -123.5906 | 123.211 | 123.343 | 123.2134 | 51.8665 | -123.7634
535.2344 | 123.4909 | -64.5767 | 58.7631 | 0.079707 | -0.029715 | 0.00029306 | 0.048054 | -0.007206 | 0.054706 | 0.066374 | -0.0010164 | 0.013374 | 0.063837 | 0.066208 | 0.072331 | -60.0033 | -29.5535 | -61.6138 | 58.4403 | 58.3359 | 58.5054 | -65.0517 | -42.2421 | -13.7175 | -47.8718 | 58.3779 | 58.5054 | 58.362 | -65.2291 | -0.47501 | -0.32281 | 4.5734 | 2.963 | 3.438 | -0.42726 | -0.25771 | -0.65242 | -0.38521 | 22.3346 | 16.7049 | 17.3573 | -0.25777 | -0.40108 | 123.017 | 122.9126 | 123.0821 | 35.0232 | -123.8149 | 122.9546 | 123.0821 | 122.9388 | 50.8593 | -123.9923
536.2344 | 123.4726 | -64.4348 | 58.9279 | 0.049183 | -0.027578 | -0.00077494 | 0.049122 | -0.005069 | 0.053638 | 0.096896 | -0.0010164 | 0.015511 | 0.065973 | 0.067276 | 0.073399 | -59.3852 | -28.8575 | -61.0918 | 58.8615 | 58.7571 | 58.9221 | -64.6259 | -40.3237 | -12.8109 | -45.7656 | 58.7946 | 58.9083 | 58.7833 | -64.8125 | -0.19108 | -0.066397 | 5.0496 | 3.343 | 3.5341 | -0.1708 | -0.005852 | -0.37765 | -0.13336 | 24.1112 | 18.6692 | 19.0469 | -0.019646 | -0.14465 | 123.2963 | 123.1919 | 123.3569 | 35.5773 | -123.5538 | 123.2294 | 123.3431 | 123.2181 | 51.6239 | -123.7404
537.2344 | 123.5092 | -64.3066 | 59.0424 | 0.049183 | -0.028647 | 0.00029306 | 0.049122 | -0.004001 | 0.054706 | 0.051113 | -0.0010164 | 0.017648 | 0.067042 | 0.072618 | 0.075535 | -59.1334 | -28.5004 | -60.9087 | 58.9165 | 58.8121 | 58.9907 | -64.5847 | -38.7119 | -12.8796 | -42.6292 | 58.8449 | 58.9678 | 58.8291 | -64.7529 | -0.27804 | -0.1259 | 5.1732 | 3.3979 | 3.676 | -0.23029 | -0.051614 | -0.4463 | -0.19744 | 25.5947 | 21.6774 | 22.1237 | -0.074565 | -0.2133 | 123.2231 | 123.1187 | 123.2974 | 35.8062 | -123.627 | 123.1516 | 123.2744 | 123.1357 | 51.4271 | -123.7953
538.2344 | 123.5184 | -64.064 | 59.317 | 0.064445 | -0.027578 | -0.0018439 | 0.048054 | -0.005069 | 0.053638 | 0.066374 | -0.0010164 | 0.018716 | 0.067042 | 0.071549 | 0.074467 | -58.6435 | -27.9235 | -60.5287 | 59.1866 | 59.0685 | 59.2563 | -64.3191 | -38.918 | -13.5572 | -40.6512 | 59.1105 | 59.2425 | 59.0992 | -64.4874 | -0.25508 | -0.13043 | 5.4205 | 3.5353 | 3.7904 | -0.24853 | -0.060714 | -0.42335 | -0.20655 | 25.146 | 23.4128 | 23.8362 | -0.074508 | -0.21782 | 123.2506 | 123.1325 | 123.3203 | 36.1405 | -123.6361 | 123.1745 | 123.3065 | 123.1632 | 50.5068 | -123.8044
539.2344 | 123.5138 | -63.858 | 59.4589 | 0.064445 | -0.029715 | 0.00029306 | 0.049122 | -0.008274 | 0.053638 | 0.081635 | -0.0010164 | 0.019784 | 0.065973 | 0.074754 | 0.075535 | -58.1674 | -27.516 | -60.1716 | 59.4201 | 59.2974 | 59.4807 | -64.0856 | -37.8511 | -14.5828 | -38.2932 | 59.3394 | 59.4714 | 59.3419 | -64.2539 | -0.22755 | -0.03884 | 5.6907 | 3.6864 | 3.914 | -0.16149 | 0.021732 | -0.39582 | -0.11953 | 26.0069 | 25.5649 | 25.9607 | 0.012516 | -0.11706 | 123.2781 | 123.1555 | 123.3387 | 36.342 | -123.5445 | 123.1974 | 123.3295 | 123.1999 | 49.2752 | -123.7128
540.2344 | 123.5138 | -63.9542 | 59.3948 | 0.064445 | -0.029715 | 0.00029306 | 0.049122 | -0.005069 | 0.055774 | 0.066374 | -0.0010164 | 0.020852 | 0.069178 | 0.073686 | 0.074467 | -57.5401 | -27.3329 | -60.0159 | 59.4613 | 59.3524 | 59.531 | -64.0169 | -37.5032 | -14.0654 | -36.5212 | 59.3943 | 59.5172 | 59.3785 | -64.2126 | -0.062733 | 0.066453 | 6.414 | 3.9382 | 4.001 | -0.042457 | 0.13618 | -0.25848 | -0.000501 | 26.451 | 27.433 | 27.6914 | 0.12239 | -0.016346 | 123.4155 | 123.3065 | 123.4852 | 36.6213 | -123.4117 | 123.3485 | 123.4714 | 123.3327 | 49.8887 | -123.6075
541.2344 | 123.5229 | -63.5834 | 59.7748 | 0.033921 | -0.028647 | -0.00077494 | 0.051259 | -0.005069 | 0.053638 | 0.081635 | 5.2637e-05 | 0.018716 | 0.073451 | 0.07796 | 0.074467 | -57.1189 | -27.0123 | -59.7229 | 59.6353 | 59.5172 | 59.6958 | -63.8429 | -38.6158 | -13.9098 | -33.5221 | 59.5592 | 59.6821 | 59.5479 | -64.0341 | -0.25952 | -0.13951 | 6.4645 | 3.8605 | 4.12 | -0.25756 | -0.078931 | -0.4507 | -0.21562 | 24.9676 | 30.0612 | 30.5119 | -0.092725 | -0.22688 | 123.2186 | 123.1006 | 123.2792 | 36.571 | -123.6177 | 123.1425 | 123.2654 | 123.1313 | 49.6736 | -123.8089
542.25 | 123.4543 | -63.533 | 59.7977 | 0.064445 | -0.027578 | -0.00077494 | 0.049122 | -0.006137 | 0.054706 | 0.051113 | 5.2637e-05 | 0.018716 | 0.074519 | 0.079028 | 0.075535 | -56.4734 | -26.3988 | -59.2239 | 60.0153 | 59.9064 | 60.0759 | -63.4674 | -38.0755 | -13.8777 | -31.6174 | 59.9392 | 60.0667 | 59.9233 | -63.654 | 0.065595 | 0.21761 | 7.0597 | 4.3091 | 4.2435 | 0.10876 | 0.2782 | -0.12101 | 0.14151 | 25.4575 | 31.9156 | 32.0366 | 0.26899 | 0.12568 | 123.5483 | 123.4394 | 123.6089 | 37.1342 | -123.2651 | 123.4722 | 123.5997 | 123.4564 | 49.6553 | -123.4517
543.2344 | 123.436 | -62.2055 | 61.1526 | 0.064445 | -0.027578 | -0.00077494 | 0.050191 | -0.006137 | 0.056843 | 0.066374 | -0.0020844 | 0.016579 | 0.075588 | 0.080096 | 0.075535 | -55.8736 | -25.1901 | -58.3632 | 60.7341 | 60.6299 | 60.8039 | -62.7485 | -37.6405 | -13.9189 | -29.1769 | 60.6672 | 60.7947 | 60.6468 | -62.926 | -0.54303 | -0.41857 | 6.3319 | 3.8423 | 4.3854 | -0.52275 | -0.34878 | -0.72049 | -0.48549 | 24.565 | 33.0286 | 33.749 | -0.35799 | -0.50589 | 122.9396 | 122.8354 | 123.0094 | 37.0154 | -123.9012 | 122.8727 | 123.0002 | 122.8523 | 48.2866 | -124.0786
544.2344 | 123.5001 | -62.8189 | 60.5713 | 0.079707 | -0.027578 | -0.00077494 | 0.050191 | -0.007206 | 0.055774 | 0.081635 | -0.0010164 | 0.018716 | 0.075588 | 0.080096 | 0.07874 | -55.2784 | -24.7139 | -58.0793 | 60.8897 | 60.7764 | 60.9595 | -62.6066 | -36.8209 | -10.2972 | -28.2887 | 60.8091 | 60.9457 | 60.7841 | -62.7795 | 0.21232 | 0.31846 | 7.5405 | 4.7396 | 4.5273 | 0.20513 | 0.38825 | 0.039435 | 0.2378 | 25.998 | 34.5302 | 34.4908 | 0.37446 | 0.21283 | 123.7087 | 123.5953 | 123.7785 | 38.105 | -123.1779 | 123.628 | 123.7647 | 123.603 | 52.5217 | -123.3508
545.2344 | 123.4772 | -62.8326 | 60.5255 | 0.033921 | -0.028647 | 0.00029306 | 0.050191 | -0.005069 | 0.056843 | 0.051113 | -0.0020844 | 0.018716 | 0.077724 | 0.083301 | 0.077672 | -55.6355 | -24.8329 | -58.267 | 60.5693 | 60.4559 | 60.639 | -62.918 | -37.233 | -10.3384 | -26.2008 | 60.484 | 60.6161 | 60.4865 | -63.0908 | -0.085312 | 0.043745 | 7.1971 | 4.5656 | 4.6509 | -0.069613 | 0.11353 | -0.25819 | -0.041496 | 25.5996 | 36.6319 | 36.89 | 0.090576 | -0.039002 | 123.4019 | 123.2885 | 123.4717 | 37.9997 | -123.4435 | 123.3167 | 123.4487 | 123.3192 | 52.4943 | -123.6163
546.2344 | 123.4955 | -63.9313 | 59.4177 | 0.064445 | -0.028647 | 0.00029306 | 0.050191 | -0.005069 | 0.056843 | 0.081635 | -0.0020844 | 0.016579 | 0.084133 | 0.083301 | 0.079808 | -56.5237 | -25.4968 | -59.1506 | 59.5254 | 59.4211 | 59.5997 | -63.9528 | -36.5416 | -6.8311 | -25.2393 | 59.4493 | 59.5859 | 59.4334 | -64.1394 | -0.021517 | 0.10766 | 7.4075 | 4.7806 | 4.8022 | 0.003338 | 0.18197 | -0.20811 | 0.031552 | 27.3896 | 38.692 | 38.9001 | 0.16818 | 0.015708 | 123.4567 | 123.3523 | 123.531 | 38.4344 | -123.3705 | 123.3806 | 123.5172 | 123.3647 | 57.1002 | -123.5571
547.25 | 123.468 | -63.9038 | 59.4635 | 0.049183 | -0.029715 | -0.00077494 | 0.050191 | -0.005069 | 0.057911 | 0.066374 | -0.0010164 | 0.019784 | 0.085202 | 0.085438 | 0.081945 | -56.391 | -25.2496 | -59.1735 | 59.3651 | 59.2562 | 59.4257 | -64.1085 | -35.5389 | -5.375 | -24.3418 | 59.2845 | 59.4211 | 59.2732 | -64.2996 | -0.20467 | -0.098359 | 7.5129 | 4.7303 | 4.9349 | -0.20728 | -0.03779 | -0.39583 | -0.17905 | 28.3649 | 39.562 | 39.9578 | -0.042427 | -0.19032 | 123.269 | 123.16 | 123.3295 | 38.6542 | -123.572 | 123.1883 | 123.3249 | 123.177 | 58.5288 | -123.7631
548.2344 | 123.5001 | -64.6133 | 58.7494 | 0.064445 | -0.028647 | 0.00029306 | 0.051259 | -0.006137 | 0.056843 | 0.066374 | -0.0010164 | 0.017648 | 0.087338 | 0.085438 | 0.083013 | -56.6794 | -25.3274 | -59.6359 | 58.7287 | 58.606 | 58.803 | -64.7724 | -34.3622 | -10.9657 | -23.8977 | 58.6526 | 58.7801 | 58.6184 | -64.9361 | -0.15908 | -0.020643 | 7.9339 | 4.9774 | 5.1365 | -0.14338 | 0.053631 | -0.32276 | -0.096772 | 30.2512 | 40.7156 | 41.0384 | 0.03068 | -0.13095 | 123.3421 | 123.2194 | 123.4164 | 39.2859 | -123.5218 | 123.266 | 123.3934 | 123.2318 | 53.6477 | -123.6855
549.2344 | 123.4772 | -64.8148 | 58.5251 | 0.049183 | -0.027578 | 0.00029306 | 0.050191 | -0.006137 | 0.056843 | 0.051113 | -0.0010164 | 0.019784 | 0.090543 | 0.086506 | 0.081945 | -56.4642 | -25.3732 | -59.8877 | 58.3258 | 58.2214 | 58.4001 | -65.1525 | -33.6479 | -5.6956 | -23.6367 | 58.2543 | 58.3817 | 58.243 | -65.3299 | -0.33771 | -0.19924 | 8.3505 | 4.927 | 5.2647 | -0.3037 | -0.12498 | -0.51512 | -0.2708 | 31.1669 | 41.1781 | 41.6932 | -0.14335 | -0.28209 | 123.1406 | 123.0361 | 123.2149 | 39.4415 | -123.6776 | 123.069 | 123.1965 | 123.0578 | 59.1192 | -123.855
550.2344 | 123.5458 | -64.5447 | 58.8409 | 0.049183 | -0.028647 | 0.00029306 | 0.049122 | -0.004001 | 0.058979 | 0.096896 | -0.0010164 | 0.020852 | 0.087338 | 0.085438 | 0.08515 | -55.0083 | -24.9611 | -59.1323 | 58.9851 | 58.8624 | 59.0548 | -64.4977 | -33.0343 | -0.77344 | -23.5451 | 58.909 | 59.041 | 58.8932 | -64.6843 | 0.046995 | 0.14419 | 9.5364 | 5.4124 | 5.3654 | 0.021492 | 0.2139 | -0.13958 | 0.068072 | 31.5103 | 40.9995 | 41.1391 | 0.20011 | 0.052216 | 123.5298 | 123.4071 | 123.5995 | 39.5835 | -123.3386 | 123.4537 | 123.5857 | 123.4378 | 63.7712 | -123.5252
551.2344 | 123.4955 | -65.0299 | 58.3374 | 0.033921 | -0.029715 | 0.0024301 | 0.050191 | -0.005069 | 0.058979 | 0.066374 | 5.2637e-05 | 0.022989 | 0.091611 | 0.089712 | 0.088355 | -55.5073 | -25.2267 | -59.5947 | 58.3625 | 58.258 | 58.4367 | -65.1387 | -31.9217 | -3.8778 | -22.2219 | 58.2818 | 58.4138 | 58.2705 | -65.3024 | -0.10883 | 0.025073 | 9.5226 | 5.4352 | 5.544 | -0.079386 | 0.099331 | -0.2725 | -0.055642 | 33.1082 | 42.808 | 43.0805 | 0.07638 | -0.066934 | 123.3924 | 123.2879 | 123.4666 | 39.8032 | -123.4761 | 123.3117 | 123.4437 | 123.3004 | 61.1521 | -123.6398
552.25 | 123.4451 | -64.8605 | 58.4564 | 0.064445 | -0.027578 | 0.00029306 | 0.051259 | -0.005069 | 0.060048 | 0.066374 | -0.0010164 | 0.019784 | 0.091611 | 0.089712 | 0.086218 | -55.7683 | -24.7597 | -59.4208 | 58.3579 | 58.2489 | 58.4367 | -65.0929 | -31.9583 | -0.2881 | -20.5507 | 58.2863 | 58.4184 | 58.2796 | -65.2932 | -0.23241 | -0.098524 | 9.0922 | 5.4398 | 5.6722 | -0.20756 | -0.019688 | -0.43271 | -0.17008 | 32.9022 | 44.3099 | 44.7426 | -0.038061 | -0.1768 | 123.2184 | 123.1094 | 123.2973 | 40.1009 | -123.5494 | 123.1469 | 123.2789 | 123.1402 | 64.5724 | -123.7497
553.2344 | 123.4955 | -65.5701 | 57.7515 | 0.064445 | -0.028647 | -0.00077494 | 0.052327 | -0.004001 | 0.057911 | 0.081635 | -0.0010164 | 0.025126 | 0.091611 | 0.09078 | 0.088355 | -55.7637 | -25.1031 | -59.6588 | 57.955 | 57.8413 | 58.0247 | -65.5188 | -30.8182 | -0.88791 | -19.1038 | 57.8697 | 58.0109 | 57.8492 | -65.7053 | 0.051284 | 0.20353 | 9.8064 | 5.9112 | 5.86 | 0.089869 | 0.27319 | -0.13527 | 0.11823 | 34.7518 | 46.4663 | 46.6016 | 0.2594 | 0.097771 | 123.5251 | 123.4114 | 123.5947 | 40.467 | -123.2702 | 123.4398 | 123.5809 | 123.4193 | 64.6822 | -123.4568
554.2344 | 123.4909 | -66.0828 | 57.2525 | 0.064445 | -0.028647 | 0.0013621 | 0.050191 | -0.002933 | 0.057911 | 0.081635 | -0.0010164 | 0.02833 | 0.091611 | 0.092917 | 0.092628 | -56.0705 | -25.5564 | -60.1808 | 57.2591 | 57.1362 | 57.3241 | -66.2239 | -25.539 | -3.5939 | -17.3822 | 57.1738 | 57.3103 | 57.1716 | -66.4105 | -0.14117 | 0.006582 | 10.0123 | 5.902 | 6.0432 | -0.11632 | 0.071631 | -0.32771 | -0.078737 | 40.5438 | 48.7006 | 49.0283 | 0.057836 | -0.080899 | 123.3418 | 123.2189 | 123.4069 | 40.5264 | -123.4764 | 123.2565 | 123.3931 | 123.2544 | 62.4888 | -123.663
555.2344 | 123.4955 | -67.0303 | 56.3095 | 0.033921 | -0.027578 | 0.0024301 | 0.051259 | -0.005069 | 0.060048 | 0.066374 | -0.0020844 | 0.031535 | 0.092679 | 0.093985 | 0.094764 | -56.542 | -25.9959 | -60.9133 | 56.3114 | 56.2158 | 56.3901 | -67.1764 | -25.9557 | -5.1598 | -16.5077 | 56.2398 | 56.3717 | 56.2284 | -67.3354 | -0.14602 | 0.001849 | 10.4883 | 6.1171 | 6.2631 | -0.093693 | 0.080589 | -0.30506 | -0.069758 | 41.0747 | 50.5227 | 50.8277 | 0.062216 | -0.081098 | 123.3417 | 123.2462 | 123.4204 | 41.0344 | -123.4859 | 123.2701 | 123.4021 | 123.2587 | 61.8705 | -123.6449
556.2344 | 123.4634 | -67.6071 | 55.7281 | 0.079707 | -0.027578 | 0.0013621 | 0.051259 | -0.004001 | 0.060048 | 0.066374 | -0.0020844 | 0.033672 | 0.091611 | 0.093985 | 0.092628 | -56.6061 | -26.266 | -61.2292 | 55.7803 | 55.6755 | 55.8636 | -67.6938 | -25.246 | 2.4317 | -15.2256 | 55.7178 | 55.8406 | 55.6927 | -67.862 | -0.086656 | 0.052116 | 11.001 | 6.3779 | 6.4646 | -0.052647 | 0.13541 | -0.25484 | -0.010346 | 42.3612 | 52.3815 | 52.6363 | 0.11246 | -0.035435 | 123.3874 | 123.2826 | 123.4707 | 41.3411 | -123.4219 | 123.3249 | 123.4477 | 123.2998 | 70.0388 | -123.5901
557.25 | 123.4955 | -67.8726 | 55.4169 | 0.049183 | -0.029715 | 0.0013621 | 0.051259 | -0.004001 | 0.058979 | 0.066374 | -0.0020844 | 0.03474 | 0.093748 | 0.09719 | 0.094764 | -56.0201 | -26.5591 | -61.1788 | 55.7024 | 55.5839 | 55.772 | -67.7762 | -25.333 | 2.6148 | -15.1295 | 55.6217 | 55.7536 | 55.6103 | -67.9581 | 0.096427 | 0.28556 | 11.8525 | 6.6938 | 6.5974 | 0.16705 | 0.35512 | -0.085496 | 0.20478 | 42.5397 | 52.7432 | 52.8287 | 0.33674 | 0.19343 | 123.5751 | 123.4565 | 123.6446 | 41.3136 | -123.1931 | 123.4943 | 123.6262 | 123.4829 | 70.4874 | -123.375
558.2344 | 123.4955 | -68.399 | 54.9454 | 0.094969 | -0.029715 | 0.0024301 | 0.051259 | -0.004001 | 0.061116 | 0.066374 | -0.0020844 | 0.036877 | 0.095884 | 0.095053 | 0.095832 | -56.6245 | -26.7468 | -61.6824 | 54.9012 | 54.7963 | 54.9753 | -68.5729 | -25.7267 | -0.22858 | -14.8044 | 54.825 | 54.9569 | 54.809 | -68.7503 | -0.17388 | -0.04416 | 11.7746 | 6.7166 | 6.8905 | -0.14903 | 0.029936 | -0.3512 | -0.12038 | 42.6723 | 53.5947 | 53.9459 | 0.011563 | -0.13633 | 123.3003 | 123.1954 | 123.3744 | 41.6523 | -123.5183 | 123.224 | 123.356 | 123.2081 | 68.1705 | -123.6956
559.2344 | 123.5092 | -69.6167 | 53.7552 | 0.064445 | -0.028647 | 0.0024301 | 0.051259 | -0.004001 | 0.060048 | 0.096896 | 5.2637e-05 | 0.035809 | 0.099089 | 0.099327 | 0.097969 | -57.1327 | -27.5389 | -62.5019 | 53.8344 | 53.7249 | 53.9085 | -69.649 | -25.1361 | 0.22014 | -12.5837 | 53.7628 | 53.8947 | 53.7377 | -69.8171 | -0.032275 | 0.079262 | 12.484 | 7.1148 | 7.147 | -0.030307 | 0.15331 | -0.20042 | 0.007598 | 44.4806 | 57.033 | 57.2334 | 0.13951 | -0.017537 | 123.4511 | 123.3416 | 123.5252 | 42.0778 | -123.4042 | 123.3795 | 123.5114 | 123.3543 | 69.8368 | -123.5723
560.2344 | 123.4863 | -69.7495 | 53.5355 | 0.064445 | -0.028647 | 0.0034981 | 0.051259 | -0.004001 | 0.060048 | 0.081635 | 5.2637e-05 | 0.036877 | 0.099089 | 0.10039 | 0.096901 | -56.1208 | -28.3722 | -62.447 | 53.7566 | 53.6516 | 53.849 | -69.736 | -25.0445 | 0.33918 | -12.5837 | 53.685 | 53.8123 | 53.6552 | -69.8995 | 0.013478 | 0.22116 | 13.6286 | 7.3025 | 7.289 | 0.11616 | 0.31351 | -0.15008 | 0.14949 | 44.705 | 57.1657 | 57.3158 | 0.27683 | 0.11978 | 123.5061 | 123.4011 | 123.5984 | 41.3773 | -123.2714 | 123.4344 | 123.5617 | 123.4047 | 70.0886 | -123.435
561.2344 | 123.4726 | -70.8389 | 52.4689 | 0.049183 | -0.028647 | 0.0045671 | 0.052327 | -0.001864 | 0.062184 | 0.066374 | -0.0020844 | 0.037945 | 0.10229 | 0.10253 | 0.096901 | -56.4917 | -28.3218 | -62.8178 | 53.0836 | 52.9556 | 53.1713 | -70.4091 | -26.7844 | 1.4472 | -10.5645 | 52.989 | 53.1255 | 52.9593 | -70.5864 | 0.42985 | 0.61472 | 14.3472 | 8.0211 | 7.5912 | 0.48675 | 0.70247 | 0.25257 | 0.52015 | 44.0545 | 60.2744 | 60.0219 | 0.65662 | 0.49042 | 123.9225 | 123.7945 | 124.0103 | 42.5171 | -122.8779 | 123.8279 | 123.9644 | 123.7982 | 72.2862 | -123.0552
562.2344 | 123.4177 | -71.228 | 52.1072 | 0.064445 | -0.027578 | 0.0045671 | 0.050191 | -0.001864 | 0.062184 | 0.081635 | -0.0020844 | 0.036877 | 0.10763 | 0.10253 | 0.10117 | -56.8442 | -29.5901 | -63.6374 | 52.1313 | 52.0169 | 52.2144 | -71.3569 | -27.1919 | 3.2741 | -10.0517 | 52.0504 | 52.1823 | 52.0344 | -71.525 | -0.12888 | 0.024051 | 14.3838 | 7.5907 | 7.7196 | -0.090297 | 0.10717 | -0.29699 | -0.056811 | 44.0361 | 61.1764 | 61.4733 | 0.075065 | -0.072828 | 123.3593 | 123.245 | 123.4424 | 41.6379 | -123.4642 | 123.2785 | 123.4103 | 123.2624 | 74.5022 | -123.6323
563.2344 | 123.468 | -71.2234 | 52.0935 | 0.079707 | -0.030783 | 0.0034981 | 0.052327 | -0.002933 | 0.062184 | 0.081635 | -0.0010164 | 0.035809 | 0.1087 | 0.10253 | 0.097969 | -56.542 | -29.7275 | -63.5229 | 52.0351 | 51.9345 | 52.1183 | -71.4027 | -26.061 | 3.2512 | -9.1909 | 51.968 | 52.0907 | 51.952 | -71.6029 | -0.17925 | -0.058363 | 14.6814 | 7.7006 | 7.8798 | -0.15899 | 0.024756 | -0.37941 | -0.12549 | 45.1625 | 62.0326 | 62.412 | -0.002774 | -0.14151 | 123.2586 | 123.158 | 123.3417 | 41.496 | -123.4962 | 123.1915 | 123.3142 | 123.1754 | 74.4747 | -123.6964
564.2344 | 123.468 | -71.5027 | 51.8372 | 0.064445 | -0.028647 | 0.0045671 | 0.052327 | -0.002933 | 0.062184 | 0.081635 | -0.0020844 | 0.037945 | 0.1055 | 0.10253 | 0.10224 | -56.1758 | -30.895 | -62.8407 | 52.0443 | 51.9162 | 52.1183 | -71.4119 | -24.9392 | 4.7393 | -9.5709 | 51.968 | 52.0907 | 51.9337 | -71.6074 | 0.090827 | 0.20714 | 15.3269 | 8.662 | 8.5711 | 0.079047 | 0.2811 | -0.10475 | 0.13086 | 46.5635 | 61.9318 | 62.0365 | 0.25357 | 0.096524 | 123.547 | 123.4189 | 123.6209 | 40.6077 | -123.249 | 123.4707 | 123.5934 | 123.4364 | 76.242 | -123.4446
565.2344 | 123.5001 | -71.9376 | 51.3886 | 0.064445 | -0.028647 | 0.0056351 | 0.052327 | -0.00079597 | 0.064321 | 0.081635 | -0.0010164 | 0.040082 | 0.1087 | 0.1036 | 0.10438 | -56.6473 | -31.2521 | -62.9872 | 51.504 | 51.3805 | 51.5963 | -71.9934 | -23.6526 | 2.8987 | -8.2385 | 51.4232 | 51.5505 | 51.4026 | -72.1477 | -0.055822 | 0.1155 | 15.2902 | 8.9503 | 9.0061 | -0.008079 | 0.20775 | -0.21017 | 0.034625 | 48.285 | 63.6991 | 63.9092 | 0.16191 | 0.014014 | 123.4416 | 123.318 | 123.5339 | 40.6854 | -123.3819 | 123.3607 | 123.488 | 123.3401 | 74.8362 | -123.5363
566.2344 | 123.4451 | -72.5281 | 50.7751 | 0.064445 | -0.030783 | 0.0045671 | 0.052327 | -0.001864 | 0.062184 | 0.051113 | -0.0020844 | 0.043287 | 0.11298 | 0.10787 | 0.10758 | -56.1987 | -32.2869 | -62.9735 | 51.0279 | 50.9088 | 51.1155 | -72.4192 | -22.3934 | -2.5317 | -5.4226 | 50.9516 | 51.0789 | 50.9355 | -72.6194 | 0.10885 | 0.25275 | 16.3294 | 9.5546 | 9.4457 | 0.1337 | 0.3404 | -0.091276 | 0.17644 | 50.1347 | 67.1055 | 67.1968 | 0.30371 | 0.1604 | 123.556 | 123.4369 | 123.6436 | 40.2412 | -123.1944 | 123.4797 | 123.6069 | 123.4636 | 69.9964 | -123.3945
567.25 | 123.4451 | -73.0499 | 50.2899 | 0.049183 | -0.027578 | 0.0067031 | 0.052327 | -0.001864 | 0.064321 | 0.051113 | -0.0010164 | 0.04756 | 0.11084 | 0.10574 | 0.11186 | -55.576 | -31.0003 | -64.4752 | 49.9382 | 49.8328 | 50.0304 | -73.5411 | -20.8916 | -2.93 | -5.6561 | 49.8665 | 49.9983 | 49.8321 | -73.7045 | -0.49113 | -0.35168 | 17.4739 | 8.5747 | 9.0659 | -0.45712 | -0.2595 | -0.65461 | -0.42343 | 52.1583 | 67.3938 | 68.0484 | -0.29161 | -0.45781 | 122.9882 | 122.8827 | 123.0803 | 42.0496 | -123.831 | 122.9164 | 123.0482 | 122.882 | 70.1199 | -123.9944
568.2344 | 123.4955 | -73.2925 | 50.0244 | 0.049183 | -0.028647 | 0.0056351 | 0.052327 | -0.002933 | 0.066458 | 0.081635 | -0.0010164 | 0.048628 | 0.11725 | 0.11108 | 0.11399 | -54.6237 | -32.003 | -63.9349 | 50.0985 | 49.9885 | 50.1769 | -73.3671 | -17.7277 | -0.23316 | -2.3823 | 50.0267 | 50.154 | 50.0107 | -73.5443 | -0.074518 | 0.074071 | 18.6688 | 9.3576 | 9.4321 | -0.035936 | 0.15252 | -0.25173 | 0.00232 | 55.5648 | 70.9102 | 71.1619 | 0.12957 | -0.013745 | 123.391 | 123.281 | 123.4695 | 41.2895 | -123.3915 | 123.3193 | 123.4465 | 123.3032 | 73.0594 | -123.5687
569.2344 | 123.4818 | -73.1415 | 50.1709 | 0.064445 | -0.028647 | 0.0056351 | 0.051259 | -0.00079597 | 0.067526 | 0.066374 | 0.0011206 | 0.049696 | 0.12152 | 0.11108 | 0.1172 | -53.6943 | -33.3949 | -63.6511 | 49.778 | 49.6771 | 49.861 | -73.6876 | -16.9356 | 0.71464 | -1.1278 | 49.7154 | 49.8335 | 49.7039 | -73.8511 | -0.54611 | -0.3929 | 19.4472 | 9.4904 | 10.0365 | -0.49379 | -0.30989 | -0.70958 | -0.4555 | 56.2059 | 72.0137 | 72.7233 | -0.33742 | -0.467 | 122.9195 | 122.8186 | 123.0025 | 39.7466 | -123.8585 | 122.8569 | 122.975 | 122.8454 | 73.8561 | -124.022
570.2344 | 123.4909 | -72.1252 | 51.21 | 0.064445 | -0.027578 | 0.0088401 | 0.053396 | 0.002409 | 0.066458 | 0.096896 | -0.0010164 | 0.052901 | 0.11938 | 0.11001 | 0.11933 | -51.9637 | -33.0973 | -62.5203 | 50.6662 | 50.57 | 50.763 | -72.7764 | -16.6655 | 0.064461 | -2.2496 | 50.6174 | 50.7355 | 50.583 | -72.9673 | -0.65114 | -0.54382 | 20.1616 | 9.605 | 10.2561 | -0.64002 | -0.44703 | -0.8421 | -0.59266 | 55.4598 | 69.8757 | 70.7178 | -0.47456 | -0.62703 | 122.7914 | 122.6952 | 122.8882 | 39.0279 | -123.9864 | 122.7426 | 122.8607 | 122.7082 | 72.1897 | -124.1774
571.2344 | 123.4818 | -72.5555 | 50.7339 | 0.049183 | -0.028647 | 0.0088401 | 0.054464 | -0.00079597 | 0.067526 | 0.066374 | 5.2637e-05 | 0.051833 | 0.11938 | 0.11001 | 0.1204 | -51.1441 | -32.8913 | -62.2227 | 50.6754 | 50.5654 | 50.7676 | -72.7855 | -15.8138 | 0.35292 | -2.0252 | 50.599 | 50.7355 | 50.583 | -72.9536 | -0.23 | -0.058586 | 21.4114 | 10.3329 | 10.5629 | -0.16852 | 0.033626 | -0.39806 | -0.1349 | 56.7417 | 70.5303 | 70.9284 | 0.001517 | -0.15095 | 123.2309 | 123.121 | 123.3231 | 39.6643 | -123.5195 | 123.1546 | 123.291 | 123.1385 | 72.9085 | -123.6876
572.25 | 123.4268 | -72.3358 | 50.9949 | 0.049183 | -0.027578 | 0.0088401 | 0.054464 | 0.00027203 | 0.069662 | 0.081635 | -0.0010164 | 0.056106 | 0.11938 | 0.11215 | 0.12254 | -50.1415 | -33.633 | -62.3005 | 50.4007 | 50.2998 | 50.4929 | -73.0786 | -14.1655 | 1.3969 | -1.256 | 50.3335 | 50.4607 | 50.2945 | -73.2329 | -0.74277 | -0.59421 | 22.1944 | 10.0353 | 10.7781 | -0.69503 | -0.50202 | -0.8971 | -0.66138 | 58.1703 | 71.0798 | 71.9769 | -0.53412 | -0.70033 | 122.7365 | 122.6357 | 122.8287 | 38.7028 | -124.0735 | 122.6693 | 122.7966 | 122.6304 | 73.7327 | -124.2278
573.2344 | 123.468 | -72.258 | 51.0498 | 0.079707 | -0.029715 | 0.0099091 | 0.054464 | -0.00079597 | 0.070731 | 0.066374 | -0.0020844 | 0.043287 | 0.12152 | 0.11215 | 0.11186 | -49.3448 | -33.6834 | -61.6962 | 50.8402 | 50.7394 | 50.9232 | -72.6115 | -23.9273 | 2.8987 | 0.46562 | 50.7639 | 50.9049 | 50.757 | -72.7933 | -0.35354 | -0.20962 | 22.9132 | 10.5618 | 10.9154 | -0.31038 | -0.12656 | -0.53535 | -0.28593 | 48.3307 | 72.7236 | 73.259 | -0.14493 | -0.29282 | 123.0982 | 122.9974 | 123.1812 | 38.5746 | -123.6613 | 123.0219 | 123.1629 | 123.015 | 75.1567 | -123.8432
574.2344 | 123.4589 | -72.1481 | 51.1871 | 0.049183 | -0.027578 | 0.013114 | 0.054464 | 0.00027203 | 0.072867 | 0.020591 | -0.0010164 | 0.044355 | 0.11832 | 0.11108 | 0.10972 | -42.8618 | -34.8967 | -61.2063 | 51.2293 | 51.1241 | 51.3124 | -72.2269 | -28.126 | 1.841 | -0.35855 | 51.1576 | 51.2849 | 51.137 | -72.3996 | -0.078776 | 0.042213 | 29.2863 | 10.9418 | 11.0206 | -0.063083 | 0.12529 | -0.25144 | -0.029512 | 44.0222 | 71.7896 | 72.041 | 0.097763 | -0.050129 | 123.3775 | 123.2722 | 123.4606 | 37.2514 | -123.414 | 123.3058 | 123.433 | 123.2851 | 73.9891 | -123.5867
575.2344 | 123.4818 | -72.2488 | 51.0178 | 0.064445 | -0.027578 | 0.014182 | 0.054464 | 0.00027203 | 0.073936 | 0.051113 | 5.2637e-05 | 0.040082 | 0.11832 | 0.11322 | 0.10758 | -41.557 | -34.915 | -60.9499 | 51.1744 | 51.0508 | 51.2712 | -72.2773 | -31.3082 | 3.1597 | 1.1066 | 51.1027 | 51.2391 | 51.0683 | -72.4591 | -0.028436 | 0.15665 | 30.6919 | 11.2989 | 11.3274 | 0.033028 | 0.25346 | -0.21025 | 0.084919 | 40.9407 | 73.3555 | 73.5657 | 0.22135 | 0.050565 | 123.4232 | 123.2996 | 123.5201 | 37.3338 | -123.295 | 123.3515 | 123.488 | 123.3172 | 75.4085 | -123.4769
576.2344 | 123.4726 | -71.5118 | 51.7685 | 0.049183 | -0.030783 | 0.019524 | 0.054464 | -0.001864 | 0.082482 | 0.096896 | 0.0011206 | 0.043287 | 0.12152 | 0.11322 | 0.11186 | -31.8737 | -32.3052 | -60.1716 | 51.3759 | 51.2797 | 51.4544 | -72.0712 | -29.3576 | 3.5168 | 1.4134 | 51.3133 | 51.4451 | 51.3018 | -72.2485 | -0.55938 | -0.39264 | 39.6382 | 11.3402 | 11.8996 | -0.48876 | -0.31413 | -0.73663 | -0.4552 | 42.1542 | 72.9253 | 73.6619 | -0.32334 | -0.46666 | 122.8877 | 122.7916 | 122.9662 | 39.2066 | -123.8397 | 122.8251 | 122.957 | 122.8137 | 75.0286 | -124.017
577.2344 | 123.468 | -73.7137 | 49.5804 | 0.064445 | -0.028647 | 0.024866 | 0.056601 | 0.00027203 | 0.084619 | 0.066374 | 0.0021886 | 0.042218 | 0.12259 | 0.11108 | 0.11399 | -28.4078 | -33.1935 | -61.5588 | 49.5491 | 49.4344 | 49.6367 | -73.8936 | -27.5948 | 1.4747 | -1.6452 | 49.4865 | 49.5908 | 49.4429 | -74.0846 | -0.17995 | -0.031304 | 45.3058 | 12.1549 | 12.3348 | -0.14596 | 0.056276 | -0.37089 | -0.093912 | 46.1188 | 72.0685 | 72.4394 | 0.010432 | -0.13746 | 123.2628 | 123.1481 | 123.3503 | 40.5202 | -123.474 | 123.2002 | 123.3045 | 123.1566 | 75.1884 | -123.665
578.2344 | 123.468 | -73.3932 | 49.91 | 0.049183 | -0.027578 | 0.025934 | 0.056601 | 0.001341 | 0.083551 | 0.051113 | 5.2637e-05 | 0.043287 | 0.12152 | 0.11108 | 0.11506 | -26.8237 | -33.5552 | -61.3299 | 49.572 | 49.4527 | 49.6596 | -73.8616 | -28.4373 | 6.3098 | -2.8036 | 49.5139 | 49.6412 | 49.4979 | -74.0434 | -0.46833 | -0.338 | 46.5695 | 12.0634 | 12.5317 | -0.45723 | -0.25042 | -0.65011 | -0.39603 | 44.9559 | 70.5897 | 71.2398 | -0.26879 | -0.41211 | 122.9652 | 122.846 | 123.0528 | 39.8381 | -123.7716 | 122.9072 | 123.0344 | 122.8911 | 79.7031 | -123.9533
579.2344 | 123.4726 | -74.8444 | 48.4589 | 0.064445 | -0.027578 | 0.027003 | 0.054464 | 0.002409 | 0.088892 | 0.066374 | -0.0010164 | 0.046491 | 0.12259 | 0.11215 | 0.11506 | -23.8524 | -33.9444 | -61.8106 | 48.7982 | 48.6835 | 48.8903 | -74.6492 | -28.5243 | 6.438 | -3.4354 | 48.7219 | 48.8491 | 48.7012 | -74.8309 | 0.1952 | 0.33936 | 50.992 | 13.0337 | 12.8385 | 0.22462 | 0.43148 | 0.013439 | 0.263 | 46.32 | 71.4089 | 71.3955 | 0.39022 | 0.24233 | 123.6426 | 123.5278 | 123.7347 | 40.9 | -123.108 | 123.5662 | 123.6934 | 123.5455 | 81.2824 | -123.2898
580.25 | 123.5229 | -74.9268 | 48.3536 | 0.079707 | -0.028647 | 0.032345 | 0.054464 | 0.001341 | 0.091029 | 0.066374 | 0.0011206 | 0.044355 | 0.12473 | 0.11322 | 0.11613 | -18.0424 | -33.2988 | -61.6366 | 48.4594 | 48.3538 | 48.5424 | -74.9972 | -27.7505 | 7.3583 | -2.5701 | 48.3876 | 48.5103 | 48.3624 | -75.1698 | -0.070399 | 0.10585 | 56.8844 | 13.2901 | 13.3605 | 0.000225 | 0.1888 | -0.24299 | 0.034055 | 47.1762 | 72.3567 | 72.5997 | 0.15669 | 0.008795 | 123.3862 | 123.2806 | 123.4691 | 41.628 | -123.3507 | 123.3144 | 123.437 | 123.2891 | 82.2851 | -123.5233
581.2344 | 123.4314 | -76.2222 | 47.0764 | 0.049183 | -0.029715 | 0.033413 | 0.055533 | 0.001341 | 0.093165 | 0.051113 | -0.0010164 | 0.049696 | 0.12686 | 0.11108 | 0.1204 | -17.2686 | -35.4049 | -62.534 | 47.15 | 47.0351 | 47.2512 | -76.2793 | -27.4071 | 7.6148 | -5.1708 | 47.0873 | 47.2099 | 47.0575 | -76.4793 | -0.057027 | 0.073588 | 58.9536 | 13.6882 | 13.7453 | -0.041344 | 0.17479 | -0.25707 | 0.010924 | 48.8151 | 71.0515 | 71.3085 | 0.13352 | -0.018946 | 123.3722 | 123.2573 | 123.4734 | 40.8173 | -123.3557 | 123.3096 | 123.4322 | 123.2797 | 83.837 | -123.5557
582.25 | 123.4177 | -77.1515 | 46.1426 | 0.033921 | -0.029715 | 0.036618 | 0.056601 | 0.002409 | 0.093165 | 0.066374 | 5.2637e-05 | 0.048628 | 0.12579 | 0.11108 | 0.12254 | -16.7009 | -34.0313 | -62.6301 | 46.184 | 46.0827 | 46.2897 | -77.25 | -24.9667 | 6.5296 | -6.3383 | 46.1167 | 46.2484 | 46.0456 | -77.4363 | -0.098499 | 0.041386 | 60.4506 | 14.5214 | 14.6199 | -0.059922 | 0.14712 | -0.28478 | -0.025879 | 52.1848 | 70.8131 | 71.0979 | 0.10586 | -0.096979 | 123.3355 | 123.2341 | 123.4412 | 43.1201 | -123.3926 | 123.2682 | 123.3999 | 123.1971 | 83.6811 | -123.5788
583.2344 | 123.4772 | -74.2264 | 48.9624 | 0.064445 | -0.029715 | 0.03555 | 0.055533 | 0.002409 | 0.095302 | 0.066374 | 5.2637e-05 | 0.065721 | 0.10443 | 0.10467 | 0.12681 | -13.2946 | -31.8061 | -60.515 | 47.8551 | 47.786 | 47.9472 | -75.5878 | -24.5225 | -0.62235 | -13.417 | 47.8199 | 47.9288 | 47.8038 | -75.7467 | -1.3615 | -1.1073 | 60.9318 | 13.7114 | 15.0729 | -1.1764 | -1.0152 | -1.5203 | -1.1425 | 49.7039 | 60.8094 | 62.3297 | -1.0336 | -1.1586 | 122.0815 | 122.0124 | 122.1735 | 42.4202 | -124.5502 | 122.0463 | 122.1552 | 122.0302 | 73.604 | -124.7091
584.2344 | 123.4634 | -70.7016 | 52.5879 | 0.049183 | -0.029715 | 0.039824 | 0.056601 | 0.001341 | 0.097439 | 0.081635 | 5.2637e-05 | 0.075335 | 0.11084 | 0.09719 | 0.15565 | -6.4041 | -28.537 | -55.7444 | 52.7997 | 52.6992 | 52.8783 | -70.6792 | -24.6095 | -17.8566 | -19.4701 | 52.7235 | 52.8462 | 52.6892 | -70.8153 | 0.022367 | 0.21184 | 64.2975 | 14.9572 | 14.9348 | 0.11131 | 0.29042 | -0.1137 | 0.13558 | 46.0921 | 51.2315 | 51.3452 | 0.25831 | 0.10126 | 123.5013 | 123.4008 | 123.5799 | 42.1646 | -123.2671 | 123.4251 | 123.5478 | 123.3907 | 52.845 | -123.4032
585.25 | 123.468 | -70.3949 | 52.8671 | 0.049183 | -0.027578 | 0.039824 | 0.058738 | 0.001341 | 0.098507 | 0.066374 | -0.0010164 | 0.074267 | 0.11298 | 0.098259 | 0.15459 | -10.5476 | -28.7385 | -55.7352 | 52.58 | 52.4565 | 52.6585 | -70.8624 | -23.3412 | -15.1231 | -17.4738 | 52.5083 | 52.6402 | 52.4785 | -71.0351 | -0.46749 | -0.28715 | 59.8473 | 14.6597 | 15.1271 | -0.41061 | -0.20859 | -0.64018 | -0.35885 | 47.0537 | 52.9211 | 53.5613 | -0.22696 | -0.38859 | 122.9749 | 122.8514 | 123.0534 | 41.6564 | -123.7295 | 122.9032 | 123.0351 | 122.8734 | 55.2718 | -123.9022
586.2344 | 123.4818 | -68.7012 | 54.5883 | 0.064445 | -0.028647 | 0.040892 | 0.059806 | 0.003477 | 0.098507 | 0.066374 | -0.0010164 | 0.080677 | 0.11191 | 0.096122 | 0.16313 | -10.3003 | -27.4794 | -53.1485 | 54.654 | 54.5399 | 54.7326 | -68.7881 | -22.8879 | -17.4079 | -17.3593 | 54.5778 | 54.7051 | 54.5572 | -68.9609 | -0.086964 | 0.065663 | 58.4008 | 15.5527 | 15.6396 | -0.048389 | 0.14433 | -0.2597 | -0.01056 | 45.8132 | 51.3419 | 51.6016 | 0.1168 | -0.031097 | 123.3552 | 123.2411 | 123.4338 | 41.2218 | -123.3765 | 123.2789 | 123.4063 | 123.2584 | 51.2933 | -123.5492
587.25 | 123.4451 | -71.8872 | 51.3702 | 0.079707 | -0.029715 | 0.046234 | 0.055533 | 0.004546 | 0.10064 | 0.066374 | 5.2637e-05 | 0.20246 | 0.11511 | 0.095053 | 0.29026 | -9.1786 | -28.5187 | -55.8451 | 51.3438 | 51.2294 | 51.4223 | -72.0895 | 44.1856 | -22.6414 | -21.7091 | 51.2583 | 51.3856 | 51.2332 | -72.2485 | -0.20233 | -0.026432 | 62.7086 | 16.0421 | 16.2444 | -0.14087 | 0.052075 | -0.36126 | -0.11189 | 116.0728 | 50.1781 | 50.5394 | 0.015388 | -0.13708 | 123.231 | 123.1166 | 123.3095 | 43.3685 | -123.4598 | 123.1456 | 123.2728 | 123.1204 | 49.2458 | -123.6187
588.2344 | 123.4634 | -68.8889 | 54.3777 | 0.049183 | -0.028647 | 0.048371 | 0.058738 | 0.005614 | 0.10171 | 0.066374 | -0.0010164 | 0.20033 | 0.12366 | 0.093985 | 0.29987 | -4.385 | -27.3054 | -51.7979 | 54.0863 | 53.9767 | 54.1649 | -69.333 | 48.311 | -23.1221 | -22.2677 | 54.0009 | 54.1328 | 53.9803 | -69.4874 | -0.44417 | -0.29149 | 64.5038 | 17.0909 | 17.5351 | -0.40103 | -0.21285 | -0.59859 | -0.37688 | 117.1999 | 46.6212 | 47.2198 | -0.24496 | -0.39743 | 122.9751 | 122.8656 | 123.0538 | 41.5835 | -123.7108 | 122.8897 | 123.0216 | 122.8692 | 45.7667 | -123.8652
589.2344 | 123.4634 | -71.9147 | 51.3519 | 0.094969 | -0.028647 | 0.051576 | 0.05767 | 0.004546 | 0.10812 | 0.066374 | -0.0010164 | 0.19392 | 0.10657 | 0.096122 | 0.2721 | -4.0371 | -28.9491 | -53.6201 | 51.3484 | 51.2339 | 51.4406 | -72.1857 | 46.0537 | -21.2265 | -19.5479 | 51.2583 | 51.3856 | 51.1645 | -72.2302 | -0.27103 | -0.003544 | 67.8776 | 18.2946 | 18.5656 | -0.11798 | 0.0887 | -0.31548 | -0.09358 | 117.9684 | 52.3668 | 52.6822 | 0.033698 | -0.18745 | 123.2631 | 123.1486 | 123.3553 | 42.9656 | -123.5376 | 123.173 | 123.3003 | 123.0791 | 50.6881 | -123.5821
590.25 | 123.4726 | -64.1464 | 59.1248 | 0.033921 | -0.028647 | 0.052644 | 0.056601 | 0.004546 | 0.10598 | 0.066374 | 0.0032566 | 0.1811 | 0.12579 | 0.09078 | 0.29346 | 2.8168 | -21.5089 | -44.8756 | 59.8047 | 59.6729 | 59.8744 | -63.6094 | -51.4179 | -21.6203 | -20.3446 | 59.7057 | 59.8423 | 59.6898 | -63.7822 | 0.53705 | 0.67991 | 66.9632 | 19.2709 | 18.7338 | 0.54815 | 0.74966 | 0.36419 | 0.58092 | 12.7286 | 43.8018 | 43.4376 | 0.71755 | 0.56508 | 123.9511 | 123.8193 | 124.0208 | 42.6376 | -122.7341 | 123.8521 | 123.9887 | 123.8363 | 42.5261 | -122.907
591.2344 | 123.4314 | -70.3217 | 52.9587 | 0.064445 | -0.029715 | 0.056918 | 0.056601 | 0.006682 | 0.10919 | 0.081635 | 5.2637e-05 | 0.18751 | 0.10336 | 0.099327 | 0.26248 | -2.5262 | -29.0086 | -50.3832 | 52.6715 | 52.5664 | 52.7593 | -70.8761 | 14.3782 | -17.82 | -16.5855 | 52.5403 | 52.6859 | 52.5838 | -70.916 | -0.55447 | -0.28714 | 67.7954 | 19.9384 | 20.4929 | -0.39227 | -0.19941 | -0.59438 | -0.41835 | 84.6999 | 53.7362 | 54.3305 | -0.27273 | -0.37484 | 122.9932 | 122.8881 | 123.0809 | 41.313 | -123.8348 | 122.862 | 123.0076 | 122.9055 | 52.5017 | -123.8747
592.25 | 123.2208 | -73.3704 | 49.9191 | 0.033921 | -0.028647 | 0.057986 | 0.056601 | 0.007751 | 0.11026 | 0.066374 | 0.0021886 | 0.18537 | 0.11084 | 0.10467 | 0.26675 | -1.9402 | -28.4638 | -50.9143 | 50.9821 | 50.8356 | 51.056 | -72.5429 | 14.4606 | -14.9033 | -12.396 | 50.86 | 50.9964 | 50.8348 | -72.5919 | 0.82751 | 1.063 | 71.4302 | 22.4561 | 21.6285 | 0.91645 | 1.1369 | 0.77848 | 0.94089 | 87.831 | 60.9744 | 60.1959 | 1.0773 | 0.91569 | 124.3525 | 124.2059 | 124.4264 | 44.9066 | -122.462 | 124.2304 | 124.3668 | 124.2052 | 58.467 | -122.511
593.2344 | 123.3765 | -75.6546 | 47.7036 | 0.064445 | -0.028647 | 0.063328 | 0.056601 | 0.008819 | 0.11346 | 0.066374 | 5.2637e-05 | 0.14905 | 0.28283 | 0.1474 | 0.35969 | -5.0718 | -31.4902 | -57.1362 | 44.2977 | 44.2053 | 44.4033 | -79.2006 | 7.5284 | 0.97105 | 35.8224 | 44.2395 | 44.3529 | 44.2096 | -79.1854 | -3.546 | -3.4059 | 70.5828 | 18.5184 | 22.0644 | -3.4983 | -3.3002 | -3.5308 | -3.464 | 83.183 | 111.477 | 115.0078 | -3.3507 | -3.494 | 119.9523 | 119.8599 | 120.0579 | 44.1644 | -126.9042 | 119.8941 | 120.0075 | 119.8642 | 76.6256 | -126.8889
594.2344 | 123.436 | -79.1565 | 44.0964 | 0.079707 | -0.030783 | 0.061191 | 0.059806 | 0.009887 | 0.1156 | 0.066374 | 5.2637e-05 | 0.18751 | 0.25185 | 0.14847 | 0.36397 | -2.453 | -29.9655 | -56.7974 | 43.9909 | 43.8894 | 44.092 | -79.5166 | 4.0166 | 7.3538 | 39.4533 | 43.9099 | 44.0324 | 43.8662 | -79.3731 | -0.36006 | -0.10546 | 76.7035 | 22.3591 | 22.7192 | -0.20702 | -0.004403 | -0.21661 | -0.18651 | 83.1731 | 118.6098 | 118.8264 | -0.063984 | -0.23019 | 123.1474 | 123.0458 | 123.2485 | 49.1909 | -123.6129 | 123.0664 | 123.1889 | 123.0227 | 86.5103 | -123.4695
595.25 | 123.436 | -72.6654 | 50.5508 | 0.079707 | -0.027578 | 0.06226 | 0.059806 | 0.008819 | 0.11346 | 0.066374 | 5.2637e-05 | 0.24306 | 0.3309 | 0.14954 | 0.50177 | 1.1502 | -26.7926 | -52.1688 | 48.3907 | 48.3263 | 48.4691 | -75.0796 | -0.32862 | -24.2119 | 43.1484 | 48.3098 | 48.4141 | 48.3166 | -74.5287 | -2.4142 | -2.1601 | 73.8156 | 20.4966 | 22.9108 | -2.2245 | -2.0817 | -1.8633 | -2.241 | 72.3368 | 115.8138 | 117.6771 | -2.1367 | -2.2343 | 121.0562 | 120.9917 | 121.1345 | 45.8728 | -125.6304 | 120.9752 | 121.0795 | 120.982 | 48.4535 | -125.0796
596.2344 | 123.2712 | -64.5172 | 58.6212 | 0.049183 | -0.029715 | 0.065465 | 0.059806 | 0.007751 | 0.11453 | 0.081635 | 0.52667 | 1.9053 | 0.40995 | 0.1474 | 2.7921 | 13.2921 | -16.6555 | -41.3365 | 58.8753 | 58.7571 | 58.9495 | -64.429 | -58.666 | -57.7326 | 54.096 | 58.4924 | 58.6152 | 58.4445 | -64.2722 | 0.088212 | 0.25404 | 77.8093 | 23.1807 | 23.0925 | 0.1359 | 0.32832 | 0.24504 | -0.12884 | 5.8513 | 118.6133 | 118.3682 | -0.005976 | -0.17676 | 123.3925 | 123.2743 | 123.4667 | 47.8617 | -123.0502 | 123.0096 | 123.1325 | 122.9617 | 6.7846 | -122.8934
597.25 | 123.3215 | -65.094 | 58.1635 | 0.064445 | -0.028647 | 0.065465 | 0.060875 | 0.009887 | 0.11453 | 0.066374 | 5.2637e-05 | 0.073199 | -0.018418 | 0.059797 | 0.013576 | 9.112 | -17.2966 | -41.071 | 58.1839 | 58.0565 | 58.249 | -65.1479 | -0.14089 | -0.054586 | 0.16343 | 0.32259 | 0.46241 | 0.4473 | -0.48009 | -0.053897 | 0.020466 | 74.206 | 24.023 | 24.0769 | -0.10691 | 0.085559 | 64.6139 | -57.8409 | 64.9531 | 65.2574 | 0.64351 | -57.701 | -57.7162 | 123.2779 | 123.1505 | 123.343 | 47.7974 | -123.3113 | 65.4166 | 65.5564 | 65.5413 | 65.0394 | -58.6435
598.2344 | 123.3856 | -65.3549 | 57.8842 | 0.064445 | -0.029715 | 0.066533 | 0.060875 | 0.009887 | 0.11667 | 0.051113 | 0.0032566 | 0.064652 | -0.018418 | 0.059797 | 0.0082349 | 10.4352 | -17.5758 | -40.8558 | 58.1336 | 58.0108 | 58.2078 | -65.2395 | 0.023941 | 0.087354 | -0.005985 | 0.13029 | 0.26095 | 0.27331 | -0.27404 | 0.11545 | 0.24934 | 75.7901 | 24.4991 | 24.3836 | 0.12654 | 0.32359 | 65.0809 | -57.7539 | 65.3789 | 65.3489 | 0.26805 | -57.6233 | -57.6109 | 123.4885 | 123.3657 | 123.5627 | 47.7791 | -123.1237 | 65.4852 | 65.6159 | 65.6282 | 65.4423 | -58.1583
599.2344 | 123.3994 | -65.5884 | 57.6645 | 0.064445 | -0.029715 | 0.067602 | 0.06408 | 0.009887 | 0.11987 | 0.051113 | 5.2637e-05 | 0.065721 | -0.018418 | 0.058729 | 0.0050299 | 9.5424 | -18.7846 | -40.9062 | 57.5658 | 57.4384 | 57.6446 | -65.8347 | 0.014784 | 0.082776 | -0.010564 | 0.13029 | 0.26095 | 0.27789 | -0.27404 | -0.24635 | -0.098654 | 75.1308 | 24.6822 | 24.9285 | -0.2261 | -0.019855 | 65.3143 | -57.5342 | 65.6032 | 65.5778 | 0.26348 | -57.4035 | -57.3866 | 123.1542 | 123.0268 | 123.233 | 46.8038 | -123.4992 | 65.7187 | 65.8493 | 65.8663 | 65.6712 | -57.9385
600.25 | 123.4726 | -64.9704 | 58.223 | 0.064445 | -0.028647 | 0.070807 | 0.061943 | 0.010956 | 0.1188 | 0.051113 | 0.0011206 | 0.066789 | -0.018418 | 0.060866 | 0.0093029 | 11.8224 | -16.0466 | -39.1756 | 58.042 | 57.9283 | 58.1117 | -65.331 | 0.019362 | 0.050725 | -0.015143 | 0.13487 | 0.25179 | 0.27331 | -0.27862 | -0.36065 | -0.18097 | 76.7928 | 25.7948 | 26.1554 | -0.29463 | -0.11131 | 64.6918 | -58.0881 | 64.9898 | 64.9553 | 0.26348 | -57.9712 | -57.9497 | 123.0124 | 122.8987 | 123.0821 | 48.9238 | -123.554 | 65.1053 | 65.2222 | 65.2437 | 65.0211 | -58.5016
601.2344 | 123.349 | -63.6475 | 59.6146 | 0.049183 | -0.027578 | 0.074012 | 0.061943 | 0.009887 | 0.12735 | 0.051113 | 5.2637e-05 | 0.065721 | -0.019486 | 0.060866 | 0.0071659 | 10.9297 | -19.5355 | -39.725 | 59.5757 | 59.4623 | 59.6272 | -63.82 | 0.023941 | 0.055303 | -0.005985 | 0.13487 | 0.25637 | 0.26873 | -0.26946 | -0.17254 | -0.038815 | 74.5771 | 23.9225 | 24.095 | -0.15229 | 0.012607 | 63.378 | -59.4797 | 63.6714 | 63.6415 | 0.26348 | -59.3582 | -59.3458 | 123.2232 | 123.1097 | 123.2746 | 44.112 | -123.4346 | 63.7823 | 63.9038 | 63.9162 | 63.7028 | -59.884
602.25 | 123.5046 | -59.4727 | 63.707 | 0.033921 | -0.027578 | 0.052644 | 0.066217 | 0.007751 | 0.11133 | 0.051113 | 5.2637e-05 | 0.063584 | -0.018418 | 0.061934 | 0.0071659 | -3.8402 | -15.749 | -36.2363 | 63.6322 | 63.5055 | 63.6975 | -59.7631 | 0.023941 | 0.050725 | -0.015143 | 0.12114 | 0.25637 | 0.26415 | -0.27404 | -0.29042 | -0.07477 | 55.6324 | 23.2363 | 23.5267 | -0.20151 | -0.009422 | 59.1986 | -63.5858 | 59.4966 | 59.4575 | 0.2589 | -63.4506 | -63.4428 | 123.1049 | 122.9781 | 123.1702 | 43.7237 | -123.47 | 59.5938 | 59.729 | 59.7368 | 59.5234 | -63.981
603.2344 | 123.381 | -59.5963 | 63.7024 | 0.049183 | -0.028647 | 0.057986 | 0.066217 | 0.010956 | 0.11133 | 0.051113 | 0.0011206 | 0.064652 | -0.019486 | 0.061934 | 0.0071659 | -2.3156 | -18.9265 | -33.5306 | 63.5177 | 63.391 | 63.5785 | -59.8547 | 0.019362 | 0.050725 | -0.019721 | 0.11656 | 0.24264 | 0.255 | -0.2603 | -0.2584 | -0.18465 | 57.2806 | 26.0657 | 26.3241 | -0.3114 | -0.12389 | 59.3359 | -63.5858 | 59.6156 | 59.5765 | 0.24058 | -63.4598 | -63.4474 | 123.114 | 122.9872 | 123.1748 | 40.6697 | -123.557 | 59.7128 | 59.8389 | 59.8512 | 59.647 | -63.9627
604.2344 | 123.4451 | -63.2309 | 60.0815 | 0.064445 | -0.029715 | 0.053713 | 0.068354 | 0.013092 | 0.11026 | 0.066374 | 0.0011206 | 0.064652 | -0.018418 | 0.063002 | 0.0071659 | -3.4831 | -17.5575 | -34.6294 | 60.7341 | 60.607 | 60.8039 | -62.6844 | 0.019362 | 0.059882 | -0.019721 | 0.11198 | 0.23806 | 0.25042 | -0.25572 | 0.54647 | 0.6526 | 59.7478 | 28.6015 | 28.0551 | 0.52552 | 0.72239 | 62.9752 | -59.9695 | 63.2503 | 63.2112 | 0.236 | -59.8434 | -59.8311 | 123.965 | 123.8379 | 124.0348 | 45.6734 | -122.7659 | 63.3429 | 63.469 | 63.4813 | 63.2908 | -60.3372
605.2344 | 123.4406 | -64.5584 | 58.7128 | 0.049183 | -0.027578 | 0.052644 | 0.072627 | 0.015229 | 0.11346 | 0.081635 | -0.0020844 | 0.063584 | -0.019486 | 0.060866 | 0.0071659 | -1.7067 | -16.5777 | -34.2952 | 58.7791 | 58.6426 | 58.8534 | -64.6305 | 0.02852 | 0.046146 | -0.0243 | 0.11656 | 0.25179 | -0.028878 | -0.25572 | -0.072061 | 0.06634 | 62.8517 | 30.2633 | 30.3353 | -0.070123 | 0.14062 | 64.3027 | -58.5962 | 64.5869 | 64.5341 | 0.23142 | -58.461 | -58.7416 | 123.3375 | 123.2011 | 123.4118 | 47.9807 | -123.3432 | 64.675 | 64.8102 | 64.5295 | 64.6046 | -58.9685
606.2344 | 123.4222 | -64.4394 | 58.8547 | 0.079707 | -0.027578 | 0.051576 | 0.076901 | 0.016297 | 0.11346 | 0.081635 | 5.2637e-05 | 0.064652 | -0.018418 | 0.060866 | 0.0071659 | -2.0913 | -17.759 | -32.5966 | 58.8615 | 58.7525 | 58.9404 | -64.5206 | 0.023941 | 0.055303 | -0.019721 | 0.11198 | 0.23806 | -0.028878 | -0.2603 | -0.081186 | 0.006845 | 62.3481 | 31.8428 | 31.924 | -0.10213 | 0.085705 | 64.1791 | -58.7427 | 64.4633 | 64.4197 | 0.24058 | -58.6166 | -58.8836 | 123.3009 | 123.1919 | 123.3798 | 46.6804 | -123.3753 | 64.5514 | 64.6774 | 64.4105 | 64.4947 | -59.115
607.25 | 123.3902 | -66.2384 | 57.0465 | 0.033921 | -0.028647 | 0.050507 | 0.082243 | 0.015229 | 0.1188 | 0.051113 | 5.2637e-05 | 0.063584 | -0.018418 | 0.061934 | 0.0071659 | -2.279 | -16.1199 | -35.307 | 57.108 | 56.9805 | 57.1868 | -66.3247 | 0.019362 | 0.055303 | -0.0243 | 0.11198 | 0.24721 | -0.042614 | -0.25572 | -0.086271 | 0.061488 | 63.9594 | 30.9315 | 31.0177 | -0.066013 | 0.14027 | 65.9827 | -56.9345 | 66.2578 | 66.2141 | 0.23142 | -56.7993 | -57.0891 | 123.3464 | 123.2189 | 123.4252 | 50.1186 | -123.3712 | 66.3504 | 66.4856 | 66.1958 | 66.2937 | -57.3022
608.2344 | 123.4039 | -68.6966 | 54.6249 | 0.049183 | -0.029715 | 0.048371 | 0.091859 | 0.016297 | 0.12308 | 0.051113 | -0.0010164 | 0.063584 | -0.019486 | 0.060866 | 0.0082349 | -2.9612 | -15.7398 | -35.5267 | 54.7776 | 54.6361 | 54.8608 | -68.6096 | 0.02852 | 0.050725 | -0.0243 | 0.11656 | 0.23806 | -0.0243 | -0.25572 | 0.087036 | 0.15266 | 65.7354 | 33.1699 | 33.0828 | 0.011148 | 0.23591 | 68.4409 | -54.5084 | 68.7251 | 68.6723 | 0.23142 | -54.3869 | -54.6492 | 123.4742 | 123.3327 | 123.5574 | 52.9568 | -123.2345 | 68.8132 | 68.9347 | 68.6723 | 68.7473 | -54.8807
609.2344 | 123.3765 | -69.1544 | 54.1672 | 0.049183 | -0.027578 | 0.057986 | 0.087585 | 0.015229 | 0.13162 | 0.066374 | 0.0021886 | 0.063584 | -0.019486 | 0.064071 | 0.0060979 | -3.4327 | -15.2408 | -37.5686 | 54.2557 | 54.1416 | 54.348 | -69.159 | 0.023941 | 0.055303 | -0.0243 | 0.11198 | 0.23806 | -0.033457 | -0.25115 | -0.004671 | 0.088487 | 65.7216 | 31.5857 | 31.5904 | -0.025612 | 0.18087 | 68.9032 | -54.0552 | 69.1783 | 69.1301 | 0.22685 | -53.9291 | -54.2006 | 123.41 | 123.2959 | 123.5024 | 53.9136 | -123.3262 | 69.2663 | 69.3924 | 69.1209 | 69.2097 | -54.4183
610.2344 | 123.4085 | -69.841 | 53.421 | 0.049183 | -0.028647 | 0.06867 | 0.086517 | 0.016297 | 0.13803 | 0.066374 | 0.0011206 | 0.063584 | -0.020554 | 0.064071 | 0.0082349 | -2.4942 | -14.5769 | -36.8727 | 53.7383 | 53.6241 | 53.8169 | -69.6673 | 0.033099 | 0.055303 | -0.0243 | 0.10282 | 0.24264 | -0.033457 | -0.24657 | 0.17371 | 0.31728 | 67.3468 | 32.9683 | 32.7946 | 0.20312 | 0.3959 | 69.5944 | -53.3182 | 69.8741 | 69.8167 | 0.22227 | -53.1784 | -53.4545 | 123.5793 | 123.4651 | 123.6579 | 55.2641 | -123.0883 | 69.9438 | 70.0836 | 69.8075 | 69.8963 | -53.6676
611.2344 | 123.4314 | -70.0241 | 53.2837 | 0.064445 | -0.027578 | 0.078286 | 0.080106 | 0.017365 | 0.14124 | 0.035852 | 0.0021886 | 0.063584 | -0.020554 | 0.061934 | 0.0071659 | 2.478 | -16.1794 | -35.4718 | 53.5506 | 53.4135 | 53.6338 | -69.8779 | 0.033099 | 0.050725 | -0.019721 | 0.11198 | 0.24264 | -0.033457 | -0.25115 | 0.14619 | 0.2669 | 72.5021 | 34.5523 | 34.4062 | 0.12982 | 0.35009 | 69.773 | -53.1717 | 70.0572 | 70.0044 | 0.23142 | -53.0411 | -53.3171 | 123.5747 | 123.4376 | 123.6579 | 53.8447 | -123.1616 | 70.1361 | 70.2667 | 69.9907 | 70.0748 | -53.5348
612.2344 | 123.4039 | -70.2713 | 53.0136 | 0.049183 | -0.02651 | 0.084696 | 0.082243 | 0.02057 | 0.14658 | 0.081635 | 0.0011206 | 0.060379 | -0.016281 | 0.061934 | 0.0071659 | 5.2708 | -15.5017 | -32.1891 | 53.0699 | 52.9419 | 53.1484 | -70.3404 | 0.014784 | 0.050725 | -0.028879 | 0.1074 | 0.23806 | -0.042614 | -0.24199 | -0.06909 | 0.056248 | 75.5421 | 38.0822 | 38.1512 | -0.071726 | 0.13484 | 70.0293 | -52.9062 | 70.2861 | 70.2424 | 0.21311 | -52.7756 | -53.0562 | 123.3412 | 123.2132 | 123.4197 | 54.7696 | -123.354 | 70.3787 | 70.5094 | 70.2287 | 70.322 | -53.2556
613.2344 | 123.3994 | -68.6462 | 54.6799 | 0.033921 | -0.02651 | 0.077217 | 0.086517 | 0.019502 | 0.14124 | 0.035852 | 0.0021886 | 0.063584 | -0.018418 | 0.063002 | 0.0060979 | 2.2124 | -19.3752 | -32.3036 | 54.3014 | 54.1828 | 54.3847 | -69.0766 | 0.023941 | 0.046146 | -0.0243 | 0.11656 | 0.23806 | -0.042614 | -0.2603 | -0.43037 | -0.37843 | 70.8586 | 36.3426 | 36.773 | -0.4971 | -0.2952 | 68.3859 | -54.5633 | 68.6702 | 68.6219 | 0.236 | -54.4418 | -54.7225 | 122.9477 | 122.829 | 123.0309 | 49.271 | -123.7565 | 68.7628 | 68.8843 | 68.6036 | 68.6924 | -54.9402
614.2344 | 123.4222 | -65.9454 | 57.3624 | 0.049183 | -0.02651 | 0.082559 | 0.083312 | 0.018434 | 0.14551 | 0.066374 | 0.0021886 | 0.064652 | -0.020554 | 0.064071 | 0.0071659 | 1.7912 | -21.5318 | -32.0655 | 57.2362 | 57.1179 | 57.3058 | -66.1781 | 0.023941 | 0.055303 | -0.015143 | 0.11198 | 0.23806 | -0.042614 | -0.24657 | -0.23271 | -0.12617 | 67.7366 | 33.8799 | 34.1126 | -0.2445 | -0.056548 | 65.6989 | -57.2504 | 65.9694 | 65.9303 | 0.23142 | -57.1243 | -57.405 | 123.1816 | 123.0633 | 123.2513 | 44.4137 | -123.5405 | 66.0574 | 66.1835 | 65.9028 | 66.0007 | -57.6089
615.2344 | 123.3627 | -65.5426 | 57.7744 | 0.064445 | -0.02651 | 0.083628 | 0.080106 | 0.017365 | 0.14872 | 0.066374 | 0.0021886 | 0.062516 | -0.018418 | 0.063002 | 0.0082349 | 0.87094 | -20.8999 | -32.6149 | 57.8039 | 57.6811 | 57.8827 | -65.6058 | 0.001048 | 0.041567 | -0.0243 | 0.11198 | 0.23806 | -0.042614 | -0.24657 | -0.06318 | 0.029559 | 66.4135 | 32.9277 | 32.9909 | -0.093282 | 0.10837 | 65.296 | -57.6624 | 65.5437 | 65.5183 | 0.22227 | -57.5363 | -57.817 | 123.3465 | 123.2237 | 123.4253 | 44.6427 | -123.3801 | 65.6546 | 65.7807 | 65.5 | 65.5842 | -58.0209
616.2344 | 123.4085 | -65.7394 | 57.5592 | 0.033921 | -0.027578 | 0.083628 | 0.083312 | 0.019502 | 0.14765 | 0.066374 | 0.0011206 | 0.063584 | -0.020554 | 0.064071 | 0.0071659 | 1.1777 | -17.6949 | -30.541 | 57.5155 | 57.4018 | 57.5988 | -65.8943 | 0.001048 | 0.046146 | -0.0243 | 0.11198 | 0.24264 | -0.0243 | -0.24199 | -0.15481 | -0.04373 | 66.9171 | 35.1985 | 35.3533 | -0.15745 | 0.039645 | 65.4975 | -57.4472 | 65.7405 | 65.7151 | 0.21769 | -57.3166 | -57.5835 | 123.2549 | 123.1412 | 123.3383 | 48.0445 | -123.4535 | 65.8514 | 65.9821 | 65.7151 | 65.7856 | -57.8012
617.25 | 123.5229 | -65.6067 | 57.6187 | 0.079707 | -0.027578 | 0.085764 | 0.086517 | 0.019502 | 0.15085 | 0.051113 | 0.0011206 | 0.062516 | -0.019486 | 0.063002 | 0.0071659 | 2.6657 | -19.9567 | -28.5082 | 57.4651 | 57.3514 | 57.5485 | -65.9126 | 0.001048 | 0.050725 | -0.028879 | 0.1074 | 0.23806 | -0.033457 | -0.25115 | -0.30588 | -0.1536 | 68.2724 | 37.0985 | 37.4044 | -0.26732 | -0.070229 | 65.3555 | -57.5113 | 65.6077 | 65.5778 | 0.22227 | -57.3807 | -57.6522 | 123.0718 | 122.9581 | 123.1552 | 45.65 | -123.5313 | 65.7141 | 65.8447 | 65.5732 | 65.6574 | -57.8699
618.2344 | 123.4314 | -66.7191 | 56.543 | 0.049183 | -0.027578 | 0.084696 | 0.085448 | 0.02057 | 0.15192 | 0.081635 | 0.0021886 | 0.063584 | -0.018418 | 0.063002 | 0.0082349 | 1.576 | -19.801 | -27.1439 | 56.4991 | 56.3852 | 56.5687 | -66.9199 | 0.010205 | 0.050725 | -0.0243 | 0.098244 | 0.2289 | -0.033457 | -0.24657 | -0.20088 | -0.043897 | 68.2951 | 39.5752 | 39.7761 | -0.15773 | 0.025694 | 66.4725 | -56.4447 | 66.7293 | 66.6948 | 0.22227 | -56.3141 | -56.5764 | 123.2181 | 123.1043 | 123.2877 | 46.918 | -123.4629 | 66.8173 | 66.948 | 66.6856 | 66.7698 | -56.7895
619.2344 | 123.4314 | -66.9388 | 56.3461 | 0.064445 | -0.02651 | 0.08897 | 0.087585 | 0.021639 | 0.15299 | 0.066374 | 0.0021886 | 0.063584 | -0.017349 | 0.064071 | 0.0093029 | 1.196 | -14.2655 | -26.4342 | 56.6135 | 56.486 | 56.6969 | -66.7597 | 0.005626 | 0.050725 | -0.019721 | 0.10282 | 0.2289 | -0.047193 | -0.24657 | 0.17911 | 0.2674 | 68.1348 | 40.5045 | 40.3254 | 0.13984 | 0.35073 | 66.6922 | -56.2433 | 66.9444 | 66.9191 | 0.22685 | -56.1172 | -56.3933 | 123.5523 | 123.4248 | 123.6356 | 52.6733 | -123.1058 | 67.0416 | 67.1677 | 66.8916 | 66.9895 | -56.5927
620.2344 | 123.3902 | -65.4694 | 57.8705 | 0.049183 | -0.027578 | 0.085764 | 0.086517 | 0.021639 | 0.15299 | 0.081635 | 0.0021886 | 0.063584 | -0.019486 | 0.061934 | 0.0071659 | 0.51383 | -17.4476 | -26.2603 | 57.662 | 57.53 | 57.7316 | -65.7111 | 0.005626 | 0.050725 | -0.0243 | 0.1074 | 0.2289 | -0.05635 | -0.24657 | -0.24174 | -0.2085 | 65.9832 | 39.2091 | 39.4508 | -0.34052 | -0.13885 | 65.2228 | -57.7631 | 65.475 | 65.4451 | 0.22227 | -57.6416 | -57.9268 | 123.1313 | 122.9993 | 123.201 | 48.0217 | -123.5816 | 65.5768 | 65.6983 | 65.413 | 65.5201 | -58.117
621.2344 | 123.3902 | -64.4852 | 58.7814 | 0.079707 | -0.02651 | 0.090038 | 0.08438 | 0.02057 | 0.15833 | 0.051113 | 0.0043246 | 0.063584 | -0.020554 | 0.064071 | 0.0060979 | 2.1575 | -18.954 | -24.7906 | 58.3716 | 58.258 | 58.455 | -65.0197 | -0.003531 | 0.050725 | -0.015143 | 0.10282 | 0.24264 | -0.042614 | -0.25115 | -0.53451 | -0.4098 | 66.6426 | 39.6945 | 40.229 | -0.52342 | -0.32639 | 64.234 | -58.6786 | 64.4816 | 64.47 | 0.236 | -58.5388 | -58.824 | 122.8568 | 122.7432 | 122.9402 | 45.5312 | -123.8011 | 64.588 | 64.7278 | 64.4426 | 64.5359 | -59.0326
622.25 | 123.5321 | -65.0894 | 58.1039 | 0.049183 | -0.02651 | 0.093243 | 0.08438 | 0.022707 | 0.15406 | 0.066374 | 0.0021886 | 0.064652 | -0.019486 | 0.064071 | 0.0093029 | 3.8194 | -21.8339 | -23.3347 | 58.0695 | 57.9375 | 58.1483 | -65.3265 | 0.001048 | 0.046146 | -0.019721 | 0.10282 | 0.23348 | -0.051771 | -0.24657 | -0.23705 | -0.034484 | 68.9088 | 41.7547 | 41.9917 | -0.16645 | 0.044338 | 64.8428 | -58.0011 | 65.0905 | 65.0697 | 0.22685 | -57.8705 | -58.1557 | 123.1589 | 123.0269 | 123.2377 | 43.2555 | -123.4304 | 65.1922 | 65.3229 | 65.0376 | 65.1356 | -58.3505
623.2344 | 123.3948 | -65.2405 | 58.0719 | 0.049183 | -0.028647 | 0.094311 | 0.085448 | 0.025912 | 0.1594 | 0.066374 | 0.0021886 | 0.062516 | -0.018418 | 0.064071 | 0.0082349 | 2.8351 | -22.1819 | -22.5839 | 58.1061 | 57.9787 | 58.1803 | -65.2715 | 0.001048 | 0.050725 | -0.019721 | 0.10282 | 0.2289 | -0.042614 | -0.24657 | -0.031043 | 0.034187 | 68.0755 | 42.6566 | 42.6876 | -0.093197 | 0.10843 | 64.9939 | -57.9691 | 65.2415 | 65.2208 | 0.22685 | -57.843 | -58.1145 | 123.3466 | 123.2192 | 123.4208 | 43.0586 | -123.3434 | 65.3433 | 65.4694 | 65.1979 | 65.2912 | -58.3185
624.2344 | 123.3856 | -64.5218 | 58.7952 | 0.033921 | -0.027578 | 0.092175 | 0.087585 | 0.022707 | 0.16047 | 0.081635 | 0.0021886 | 0.066789 | -0.020554 | 0.063002 | 0.0082349 | 0.21623 | -23.9676 | -23.2615 | 58.715 | 58.574 | 58.7893 | -64.6808 | -0.003531 | 0.046146 | -0.028879 | 0.1074 | 0.23348 | -0.065507 | -0.24199 | -0.15905 | -0.080155 | 64.738 | 41.2603 | 41.4193 | -0.2212 | -0.00588 | 64.2798 | -58.6878 | 64.5183 | 64.4929 | 0.21311 | -58.5617 | -58.8607 | 123.2368 | 123.0958 | 123.3111 | 40.5542 | -123.476 | 64.6292 | 64.7553 | 64.4563 | 64.5679 | -59.0372
625.2344 | 123.4177 | -63.8077 | 59.4864 | 0.049183 | -0.027578 | 0.092175 | 0.085448 | 0.023775 | 0.15726 | 0.035852 | 0.0011206 | 0.065721 | -0.020554 | 0.065139 | 0.0071659 | -2.7414 | -22.8916 | -22.5107 | 59.3697 | 59.2196 | 59.444 | -64.0352 | 0.010205 | 0.050725 | -0.019721 | 0.11198 | 0.2289 | -0.042614 | -0.24199 | -0.22753 | -0.11667 | 61.0663 | 41.297 | 41.5246 | -0.2668 | -0.042363 | 63.5657 | -59.3744 | 63.8179 | 63.788 | 0.22227 | -59.2575 | -59.529 | 123.1774 | 123.0273 | 123.2517 | 40.9161 | -123.5216 | 63.9197 | 64.0366 | 63.7651 | 63.8584 | -59.7284
626.2344 | 123.4222 | -61.8942 | 61.3998 | 0.049183 | -0.028647 | 0.093243 | 0.088654 | 0.022707 | 0.16154 | 0.035852 | 0.0011206 | 0.066789 | -0.019486 | 0.065139 | 0.0071659 | -2.4347 | -20.6893 | -20.3039 | 61.2652 | 61.1427 | 61.3304 | -62.1304 | 0.005626 | 0.046146 | -0.019721 | 0.10282 | 0.23348 | -0.05635 | -0.24199 | -0.23615 | -0.13467 | 59.4596 | 41.5903 | 41.8265 | -0.2571 | -0.069431 | 61.6522 | -61.297 | 61.8999 | 61.8745 | 0.22227 | -61.1664 | -61.4562 | 123.1594 | 123.037 | 123.2246 | 41.2049 | -123.5302 | 61.997 | 62.1277 | 61.8379 | 61.9404 | -61.6418
627.2344 | 123.3902 | -62.6862 | 60.5896 | 0.049183 | -0.027578 | 0.098585 | 0.09079 | 0.022707 | 0.16688 | 0.051113 | 0.0011206 | 0.064652 | -0.017349 | 0.065139 | 0.0060979 | -2.8055 | -20.323 | -19.5439 | 61.3522 | 61.2023 | 61.4174 | -62.0388 | 0.005626 | 0.050725 | -0.0243 | 0.1074 | 0.23348 | -0.051771 | -0.24199 | 0.64736 | 0.76256 | 59.8807 | 43.1422 | 42.4949 | 0.61266 | 0.8278 | 62.4442 | -60.4822 | 62.6918 | 62.6619 | 0.21769 | -60.3561 | -60.6414 | 124.0383 | 123.8884 | 124.1036 | 42.3631 | -122.6284 | 62.7936 | 62.9196 | 62.6344 | 62.7369 | -60.8316
628.2344 | 123.3856 | -61.9308 | 61.3724 | 0.049183 | -0.027578 | 0.099653 | 0.083312 | 0.022707 | 0.16581 | 0.081635 | 0.0011206 | 0.064652 | -0.018418 | 0.063002 | 0.0060979 | -2.1508 | -22.8412 | -22.6709 | 61.1232 | 60.9825 | 61.1976 | -62.2357 | 0.005626 | 0.055303 | -0.0243 | 0.10282 | 0.23348 | -0.05635 | -0.23741 | -0.30485 | -0.24913 | 59.7801 | 39.2599 | 39.5648 | -0.3899 | -0.17474 | 61.6934 | -61.2696 | 61.9365 | 61.9065 | 0.21311 | -61.1389 | -61.4287 | 123.0541 | 122.9133 | 123.1285 | 39.0896 | -123.6081 | 62.0337 | 62.1643 | 61.8745 | 61.9862 | -61.6098
629.2344 | 123.2986 | -61.0703 | 62.2284 | 0.033921 | -0.027578 | 0.10286 | 0.083312 | 0.019502 | 0.17008 | 0.066374 | 0.0021886 | 0.064652 | -0.020554 | 0.065139 | 0.0082349 | -0.63993 | -23.5463 | -23.0784 | 62.1625 | 62.0265 | 62.2232 | -61.2146 | 0.005626 | 0.050725 | -0.019721 | 0.098244 | 0.2289 | -0.060928 | -0.24657 | -0.14434 | -0.065857 | 60.4303 | 37.9919 | 38.1362 | -0.20192 | -0.005156 | 60.8237 | -62.1302 | 61.0759 | 61.0505 | 0.22685 | -61.9995 | -62.2893 | 123.2328 | 123.0967 | 123.2935 | 37.5239 | -123.443 | 61.1685 | 61.2992 | 61.0093 | 61.121 | -62.475
630.2344 | 123.4131 | -61.4365 | 61.8805 | 0.033921 | -0.02651 | 0.10606 | 0.08438 | 0.021639 | 0.17436 | 0.081635 | 0.0021886 | 0.063584 | -0.019486 | 0.064071 | 0.0071659 | -1.0199 | -24.0637 | -23.4172 | 61.9611 | 61.8113 | 62.0264 | -61.4481 | 0.001048 | 0.046146 | -0.019721 | 0.1074 | 0.24264 | -0.05635 | -0.24657 | -0.011658 | 0.080595 | 60.4165 | 38.0193 | 38.031 | -0.069232 | 0.14587 | 61.1899 | -61.7731 | 61.4375 | 61.4167 | 0.22685 | -61.6379 | -61.9368 | 123.3975 | 123.2477 | 123.4628 | 37.3727 | -123.3286 | 61.5439 | 61.6791 | 61.3801 | 61.4826 | -62.1271
631.2344 | 123.3994 | -59.6832 | 63.5971 | 0.064445 | -0.02651 | 0.10179 | 0.082243 | 0.018434 | 0.17543 | 0.066374 | 0.0032566 | 0.064652 | -0.019486 | 0.064071 | 0.0060979 | -0.2645 | -25.7578 | -24.4518 | 63.6414 | 63.5192 | 63.7067 | -59.7402 | 0.010205 | 0.050725 | -0.0243 | 0.10282 | 0.2289 | -0.070086 | -0.24199 | -0.056953 | 0.04425 | 59.4187 | 35.2314 | 35.2883 | -0.077907 | 0.1096 | 59.4412 | -63.4943 | 59.6934 | 59.6589 | 0.21769 | -63.3682 | -63.6672 | 123.3246 | 123.2024 | 123.3899 | 33.9254 | -123.3373 | 59.7861 | 59.9121 | 59.6131 | 59.734 | -63.8391
632.25 | 123.4497 | -58.5571 | 64.6957 | 0.049183 | -0.024373 | 0.096448 | 0.086517 | 0.018434 | 0.17543 | 0.096896 | 0.0032566 | 0.064652 | -0.019486 | 0.064071 | 0.0060979 | -1.6105 | -28.3264 | -26.4068 | 64.5158 | 64.348 | 64.5721 | -58.8656 | 0.001048 | 0.046146 | -0.015143 | 0.1074 | 0.23348 | -0.060928 | -0.24657 | -0.30848 | -0.17991 | 56.9466 | 32.1504 | 32.4588 | -0.34775 | -0.12368 | 58.3106 | -64.5883 | 58.5582 | 58.542 | 0.23142 | -64.4623 | -64.7567 | 123.073 | 122.9051 | 123.1292 | 30.2307 | -123.5613 | 58.6645 | 58.7906 | 58.4962 | 58.6033 | -64.9423
633.2344 | 123.4222 | -57.518 | 65.831 | 0.049183 | -0.028647 | 0.097517 | 0.09079 | 0.015229 | 0.17543 | 0.066374 | 0.0032566 | 0.064652 | -0.021622 | 0.065139 | 0.0071659 | -2.7689 | -26.9666 | -24.6716 | 65.8665 | 65.7308 | 65.9273 | -57.5011 | -0.003531 | 0.046146 | -0.0243 | 0.093665 | 0.2289 | -0.060928 | -0.24657 | 0.016918 | 0.035459 | 54.7491 | 32.8464 | 32.8295 | -0.10017 | 0.096333 | 57.2714 | -65.7373 | 57.5145 | 57.4937 | 0.22227 | -65.6021 | -65.8919 | 123.3845 | 123.2488 | 123.4453 | 30.5514 | -123.3321 | 57.6117 | 57.7469 | 57.4571 | 57.5642 | -66.0776
634.2344 | 123.3948 | -56.813 | 66.5131 | 0.064445 | -0.027578 | 0.098585 | 0.092927 | 0.012024 | 0.18504 | 0.066374 | 0.0021886 | 0.066789 | -0.020554 | 0.065139 | 0.0071659 | -3.0711 | -29.2925 | -26.5121 | 66.4662 | 66.3078 | 66.518 | -56.9196 | -0.003531 | 0.050725 | -0.028879 | 0.098244 | 0.2289 | -0.065507 | -0.24657 | -0.10651 | -0.04684 | 53.742 | 30.301 | 30.4075 | -0.2053 | 0.004905 | 56.5665 | -66.4148 | 56.8095 | 56.7842 | 0.21769 | -66.2842 | -66.5786 | 123.2793 | 123.1208 | 123.331 | 27.5206 | -123.4326 | 56.9113 | 57.0419 | 56.7475 | 56.8638 | -66.7596
635.2344 | 123.4177 | -55.8838 | 67.3828 | 0.049183 | -0.027578 | 0.10393 | 0.096132 | 0.010956 | 0.19252 | 0.051113 | -0.0010164 | 0.063584 | -0.022691 | 0.067276 | 0.0071659 | -2.8009 | -31.0965 | -27.0889 | 67.2903 | 67.1182 | 67.3192 | -56.1411 | 0.014784 | 0.050725 | -0.0243 | 0.098244 | 0.23806 | -0.074664 | -0.24199 | -0.25736 | -0.09248 | 53.0829 | 28.7949 | 29.0522 | -0.26458 | -0.06359 | 55.6418 | -67.2846 | 55.8986 | 55.8595 | 0.21769 | -67.1448 | -67.4575 | 123.1741 | 123.002 | 123.203 | 24.7873 | -123.524 | 55.982 | 56.1218 | 55.8091 | 55.9345 | -67.6248
636.2344 | 123.4406 | -56.8497 | 66.4261 | 0.064445 | -0.02651 | 0.097517 | 0.096132 | 0.007751 | 0.19252 | 0.066374 | 0.0011206 | 0.063584 | -0.021622 | 0.066208 | 0.0071659 | -2.1233 | -35.9681 | -32.3448 | 66.4433 | 66.2482 | 66.4676 | -56.9837 | 0.019362 | 0.055303 | -0.033458 | 0.1074 | 0.2289 | -0.079243 | -0.24657 | -0.134 | 0.017244 | 54.7263 | 24.5049 | 24.6389 | -0.17785 | 0.041516 | 56.6031 | -66.3187 | 56.869 | 56.8162 | 0.21311 | -66.1972 | -66.5053 | 123.293 | 123.0979 | 123.3173 | 20.8816 | -123.4098 | 56.9571 | 57.0786 | 56.7704 | 56.905 | -66.6727
637.25 | 123.4726 | -56.2271 | 66.9891 | 0.033921 | -0.027578 | 0.098585 | 0.096132 | 0.008819 | 0.19465 | 0.066374 | -0.0010164 | 0.065721 | -0.020554 | 0.066208 | 0.0071659 | -1.3633 | -37.7995 | -33.0407 | 66.8783 | 66.7199 | 66.898 | -56.5487 | 0.010205 | 0.055303 | -0.019721 | 0.10282 | 0.23806 | -0.079243 | -0.23741 | -0.32156 | -0.11086 | 54.8638 | 23.1864 | 23.508 | -0.26927 | -0.091145 | 55.9897 | -66.8863 | 56.2373 | 56.2074 | 0.21769 | -66.7511 | -67.0684 | 123.1054 | 122.947 | 123.1251 | 18.4276 | -123.5378 | 56.3299 | 56.4652 | 56.1479 | 56.2824 | -67.2265
638.2344 | 123.468 | -54.7806 | 68.4723 | 0.079707 | -0.025442 | 0.098585 | 0.096132 | 0.007751 | 0.19572 | 0.051113 | 0.0011206 | 0.063584 | -0.020554 | 0.065139 | 0.0082349 | 2.0384 | -37.566 | -32.2578 | 68.3113 | 68.1805 | 68.3494 | -55.1155 | 0.010205 | 0.055303 | -0.028879 | 0.093665 | 0.23348 | -0.0884 | -0.24657 | -0.33489 | -0.16098 | 56.819 | 22.5228 | 22.8576 | -0.29175 | -0.12288 | 54.534 | -68.3786 | 54.7908 | 54.7517 | 0.21769 | -68.2388 | -68.5607 | 123.0919 | 122.9611 | 123.13 | 17.2146 | -123.5878 | 54.8742 | 55.0141 | 54.6922 | 54.8359 | -68.7189
639.2344 | 123.4177 | -64.1327 | 59.1614 | 0.049183 | -0.028647 | 0.30051 | 0.087585 | 0.009887 | 0.38695 | 0.051113 | 0.0011206 | 0.064652 | -0.020554 | 0.066208 | 0.0060979 | 52.3824 | -46.0776 | -37.4084 | 59.9741 | 59.8698 | 60.0347 | -63.5544 | 0.014784 | 0.064461 | -0.0243 | 0.10282 | 0.2289 | -0.083821 | -0.23283 | 0.57826 | 0.81269 | 116.5151 | 26.7243 | 26.146 | 0.70842 | 0.87329 | 63.8999 | -59.0586 | 64.1475 | 64.1084 | 0.20853 | -58.9325 | -59.2452 | 124.1068 | 124.0025 | 124.1674 | 18.055 | -122.7158 | 64.2355 | 64.3616 | 64.0489 | 64.1972 | -59.3942
640.2344 | 123.468 | -45.9824 | 77.2751 | 0.064445 | -0.024373 | 0.10713 | 0.11536 | 0.007751 | 0.23205 | 0.066374 | 0.0011206 | 0.063584 | -0.021622 | 0.065139 | 0.0071659 | -28.8382 | -37.3875 | -23.0234 | 77.2575 | 77.1003 | 77.2777 | -46.2507 | 0.014784 | 0.064461 | -0.015143 | 0.10282 | 0.2289 | -0.0884 | -0.23283 | -0.26831 | -0.017603 | 17.1441 | 22.9589 | 23.2272 | -0.1748 | 0.002598 | 45.7495 | -77.1723 | 45.9971 | 45.9672 | 0.21769 | -77.0462 | -77.3635 | 123.2398 | 123.0827 | 123.26 | 8.5949 | -123.5258 | 46.0852 | 46.2113 | 45.894 | 46.0468 | -77.5079
641.2344 | 123.3673 | -44.0048 | 79.2435 | 0.049183 | -0.023305 | 0.098585 | 0.11857 | 0.007751 | 0.2235 | 0.081635 | 5.2637e-05 | 0.063584 | -0.020554 | 0.065139 | 0.0071659 | -33.3983 | -38.9808 | -21.7827 | 79.1667 | 79.0692 | 79.1961 | -44.2543 | 0.02852 | 0.059882 | -0.0243 | 0.10282 | 0.2289 | -0.092979 | -0.24199 | -0.24944 | -0.076799 | 10.6065 | 22.2221 | 22.4715 | -0.17424 | -0.047352 | 43.7628 | -79.1406 | 44.0333 | 43.9805 | 0.21769 | -79.0146 | -79.3364 | 123.1715 | 123.074 | 123.2009 | 5.024 | -123.4977 | 44.1076 | 44.2337 | 43.9118 | 44.0647 | -79.4855
642.25 | 123.5184 | -42.9062 | 80.3192 | 0.049183 | -0.022236 | 0.090038 | 0.11002 | 0.006682 | 0.20641 | 0.081635 | 0.0021886 | 0.063584 | -0.019486 | 0.066208 | 0.0071659 | -35.9713 | -39.5119 | -21.1646 | 80.3433 | 80.1682 | 80.3591 | -43.1049 | 0.019362 | 0.064461 | -0.028879 | 0.11198 | 0.23348 | -0.0884 | -0.24199 | -0.19876 | 0.024102 | 6.9348 | 21.7415 | 21.9403 | -0.15104 | 0.039868 | 42.6642 | -80.2072 | 42.9256 | 42.8773 | 0.21311 | -80.0857 | -80.4076 | 123.2495 | 123.0744 | 123.2653 | 3.3943 | -123.4242 | 43.0182 | 43.1397 | 42.8178 | 42.9706 | -80.5612
643.2344 | 123.5184 | -43.5059 | 79.7195 | 0.049183 | -0.023305 | 0.086833 | 0.11643 | 0.008819 | 0.20961 | 0.051113 | 0.0011206 | 0.064652 | -0.020554 | 0.066208 | 0.0060979 | -36.7726 | -40.2537 | -18.5321 | 79.5833 | 79.4493 | 79.6128 | -43.8742 | 0.019362 | 0.06904 | -0.019721 | 0.098244 | 0.23348 | -0.079243 | -0.24199 | -0.36835 | -0.13624 | 6.7333 | 24.9737 | 25.3421 | -0.27026 | -0.10677 | 43.2639 | -79.6213 | 43.5252 | 43.4861 | 0.22227 | -79.4861 | -79.7988 | 123.0892 | 122.9551 | 123.1186 | 3.2522 | -123.5938 | 43.6041 | 43.7393 | 43.4266 | 43.5749 | -79.9615
644.2344 | 123.4818 | -43.8675 | 79.3716 | 0.049183 | -0.023305 | 0.093243 | 0.11323 | 0.005614 | 0.20961 | 0.051113 | 0.0021886 | 0.062516 | -0.020554 | 0.068344 | 0.0082349 | -37.1114 | -40.7344 | -18.4726 | 79.652 | 79.4996 | 79.6586 | -43.8513 | 0.014784 | 0.059882 | -0.0243 | 0.098244 | 0.23348 | -0.065507 | -0.24199 | 0.01618 | 0.28034 | 6.7561 | 25.3949 | 25.3787 | 0.128 | 0.28691 | 43.6255 | -79.2734 | 43.8823 | 43.8432 | 0.21769 | -79.1382 | -79.4372 | 123.5195 | 123.3671 | 123.526 | 3.1331 | -123.223 | 43.9657 | 44.101 | 43.802 | 43.9274 | -79.6136
645.2344 | 123.4268 | -44.4946 | 78.7125 | 0.064445 | -0.023305 | 0.91163 | 0.10895 | 0.010956 | 1.0301 | 0.066374 | 0.0021886 | 0.062516 | -0.020554 | 0.065139 | 0.0082349 | -34.5658 | -41.4762 | -18.3902 | 78.4662 | 78.3091 | 78.4773 | -44.8633 | 0.014784 | 0.055303 | -0.019721 | 0.10282 | 0.23348 | -0.074664 | -0.24199 | -0.36863 | -0.24629 | 9.9288 | 26.1044 | 26.473 | -0.40334 | -0.23519 | 44.2526 | -78.6096 | 44.5094 | 44.4749 | 0.22227 | -78.479 | -78.7871 | 122.9608 | 122.8038 | 122.9719 | 3.0185 | -123.5757 | 44.5975 | 44.7281 | 44.42 | 44.5499 | -78.9545
646.2344 | 123.3673 | -38.0905 | 84.993 | 0.018659 | -0.024373 | 2.3454 | 0.11323 | 0.013092 | 2.4723 | 0.066374 | 5.2637e-05 | 0.063584 | -0.020554 | 0.067276 | 0.0093029 | 15.3524 | -29.4894 | -5.0811 | 90.0907 | 89.729 | 90.1298 | -33.0451 | 0.019362 | 0.059882 | -0.019721 | 0.1074 | 0.23348 | -0.070086 | -0.23741 | 5.0455 | 5.0977 | 53.4429 | 33.0094 | 27.9639 | 4.736 | 5.1368 | 37.8531 | -84.8856 | 38.1099 | 38.0708 | 0.21769 | -84.7595 | -85.0631 | 128.1812 | 127.8195 | 128.2203 | 8.6011 | -118.038 | 38.1979 | 38.324 | 38.0204 | 38.1504 | -85.2304
647.2344 | 123.2483 | -50.592 | 72.7158 | 0.049183 | -0.024373 | 2.9031 | 0.11216 | 0.016297 | 3.0246 | 0.081635 | 0.0021886 | 0.064652 | -0.020554 | 0.066208 | 0.0050299 | 33.1074 | -39.3013 | -13.1984 | 79.5604 | 79.4218 | 79.6128 | -43.3339 | 0.014784 | 0.06904 | -0.0243 | 0.098244 | 0.22432 | -0.083821 | -0.24199 | 7.2581 | 6.8447 | 83.6994 | 37.3936 | 30.1355 | 6.706 | 6.897 | 50.3501 | -72.6175 | 50.6068 | 50.5677 | 0.21769 | -72.4914 | -72.7996 | 130.1525 | 130.0138 | 130.2048 | 11.2907 | -116.0497 | 50.6903 | 50.8164 | 50.5082 | 50.6611 | -72.9577
648.2344 | 123.4451 | -61.5372 | 61.6379 | 0.064445 | -0.041467 | 0.051576 | -0.021393 | -0.014684 | -0.0029834 | 0.066374 | 0.0011206 | 0.062516 | -0.018418 | 0.067276 | 0.0082349 | -0.012688 | 0.051771 | 0.000747 | 0.249 | 0.23846 | 0.44873 | -0.2279 | 0.010205 | 0.064461 | -0.019721 | 0.089087 | 0.22432 | -0.074664 | -0.24657 | 61.3093 | -61.3889 | 61.5245 | 61.5379 | 0.22865 | -61.3994 | -61.1891 | 61.2906 | -61.5488 | 61.5474 | 61.5174 | 0.22685 | -61.4136 | -61.7125 | 61.7862 | 61.7756 | 61.9859 | 61.5889 | -61.8658 | 61.6263 | 61.7615 | 61.4625 | 61.6016 | -61.8844
649.2344 | 123.4818 | -61.5326 | 61.6608 | 0.033921 | -0.041467 | 0.051576 | -0.021393 | -0.016821 | -0.0029834 | 0.066374 | 0.0011206 | 0.065721 | -0.021622 | 0.067276 | 0.0071659 | -0.012688 | 0.065507 | 0.005325 | 0.23526 | 0.22473 | 0.43042 | -0.21416 | 0.014784 | 0.059882 | -0.028879 | 0.098244 | 0.2289 | -0.070086 | -0.23283 | 61.3184 | -61.4255 | 61.5199 | 61.5379 | 0.21949 | -61.436 | -61.2303 | 61.2998 | -61.5625 | 61.5474 | 61.5037 | 0.20395 | -61.4319 | -61.7309 | 61.7679 | 61.7573 | 61.963 | 61.5981 | -61.8749 | 61.6308 | 61.7615 | 61.4625 | 61.5925 | -61.8936
650.2344 | 123.4589 | -61.5143 | 61.6699 | 0.079707 | -0.041467 | 0.050507 | -0.020325 | -0.015752 | -0.0029834 | 0.066374 | 5.2637e-05 | 0.064652 | -0.021622 | 0.066208 | 0.0071659 | -0.012688 | 0.065507 | -0.003831 | 0.22153 | 0.21557 | 0.4121 | -0.19585 | 0.014784 | 0.064461 | -0.028879 | 0.093665 | 0.22432 | -0.070086 | -0.24199 | 61.3184 | -61.4484 | 61.5016 | 61.5105 | 0.19201 | -61.4544 | -61.2578 | 61.2723 | -61.5763 | 61.5291 | 61.4854 | 0.21311 | -61.4456 | -61.74 | 61.7358 | 61.7298 | 61.9264 | 61.5798 | -61.8658 | 61.6079 | 61.7386 | 61.4442 | 61.5787 | -61.9119
651.2344 | 123.4497 | -61.5234 | 61.6974 | 0.064445 | -0.040399 | 0.048371 | -0.022462 | -0.012547 | -0.0019154 | 0.066374 | 0.0011206 | 0.063584 | -0.020554 | 0.066208 | 0.0082349 | -0.012688 | 0.060928 | -0.003831 | 0.22611 | 0.21099 | 0.41668 | -0.205 | 0.010205 | 0.050725 | -0.0243 | 0.093665 | 0.23806 | -0.065507 | -0.23283 | 61.3184 | -61.4713 | 61.5107 | 61.5196 | 0.20117 | -61.4864 | -61.2807 | 61.2906 | -61.6037 | 61.5336 | 61.4991 | 0.20853 | -61.4593 | -61.7629 | 61.7495 | 61.7344 | 61.9401 | 61.5844 | -61.9024 | 61.6171 | 61.7615 | 61.4579 | 61.5742 | -61.9302
652.25 | 123.5184 | -61.528 | 61.702 | 0.064445 | -0.041467 | 0.049439 | -0.022462 | -0.015752 | 0.0012896 | 0.066374 | 0.0021886 | 0.063584 | -0.021622 | 0.067276 | 0.0050299 | -0.017266 | 0.065507 | -0.003831 | 0.13454 | 0.20641 | 0.41668 | -0.20042 | 0.014784 | 0.041567 | -0.033458 | 0.098244 | 0.23348 | -0.070086 | -0.23741 | 61.3276 | -61.5674 | 61.5107 | 61.5242 | 0.19659 | -61.4956 | -61.2853 | 61.2906 | -61.6037 | 61.5428 | 61.4946 | 0.20395 | -61.4685 | -61.7721 | 61.6626 | 61.7344 | 61.9447 | 61.5935 | -61.9024 | 61.6263 | 61.7615 | 61.4579 | 61.5696 | -61.9394
653.2344 | 123.5001 | -61.5005 | 61.6974 | 0.033921 | -0.041467 | 0.050507 | -0.021393 | -0.015752 | -0.0019154 | 0.081635 | 0.0011206 | 0.064652 | -0.021622 | 0.069413 | 0.0071659 | -0.017266 | 0.05635 | -0.003831 | 0.093333 | 0.20183 | 0.4121 | -0.19585 | 0.010205 | 0.041567 | -0.019721 | 0.093665 | 0.24264 | -0.070086 | -0.24657 | 61.3047 | -61.6041 | 61.4833 | 61.4967 | 0.19201 | -61.4956 | -61.2853 | 61.254 | -61.6037 | 61.5108 | 61.4808 | 0.22685 | -61.4548 | -61.7675 | 61.5939 | 61.7024 | 61.9127 | 61.5569 | -61.8932 | 61.5942 | 61.7432 | 61.4305 | 61.5421 | -61.944
654.2344 | 123.5001 | -61.5143 | 61.6791 | 0.049183 | -0.041467 | 0.049439 | -0.021393 | -0.015752 | -0.0019154 | 0.081635 | 0.0011206 | 0.062516 | -0.021622 | 0.068344 | 0.0050299 | -0.012688 | 0.070086 | -0.008409 | 0.13912 | 0.20183 | 0.40753 | -0.20042 | -0.003531 | 0.059882 | -0.028879 | 0.10282 | 0.23348 | -0.065507 | -0.23741 | 61.3139 | -61.54 | 61.5016 | 61.5059 | 0.19202 | -61.4772 | -61.2716 | 61.2769 | -61.5763 | 61.5108 | 61.4854 | 0.20853 | -61.4456 | -61.7446 | 61.6534 | 61.7161 | 61.9218 | 61.5844 | -61.8795 | 61.6171 | 61.7478 | 61.4488 | 61.5742 | -61.9165
655.2344 | 123.4909 | -61.5417 | 61.6699 | 0.049183 | -0.041467 | 0.047302 | -0.02353 | -0.016821 | 0.0023586 | 0.066374 | 0.0021886 | 0.065721 | -0.022691 | 0.068344 | 0.0071659 | -0.026423 | 0.065507 | -0.003831 | 0.12996 | 0.20183 | 0.39837 | -0.19585 | 0.005626 | 0.050725 | -0.028879 | 0.093665 | 0.22432 | -0.05635 | -0.23741 | 61.3459 | -61.54 | 61.5153 | 61.5379 | 0.19201 | -61.4681 | -61.2716 | 61.3043 | -61.5763 | 61.5474 | 61.5129 | 0.20853 | -61.4456 | -61.7263 | 61.6717 | 61.7436 | 61.9401 | 61.6073 | -61.8658 | 61.6354 | 61.7661 | 61.4854 | 61.5925 | -61.9073
656.2344 | 123.4818 | -61.528 | 61.6974 | 0.049183 | -0.040399 | 0.045166 | -0.021393 | -0.013616 | 0.0023586 | 0.081635 | 0.0011206 | 0.064652 | -0.021622 | 0.061934 | 0.0060979 | -0.017266 | 0.038035 | 0.000747 | 0.12996 | 0.19725 | 0.40753 | -0.118 | 0.001048 | 0.046146 | -0.033458 | 0.093665 | 0.2289 | -0.05635 | -0.24199 | 61.41 | -61.5674 | 61.5107 | 61.5288 | 0.11875 | -61.5001 | -61.2899 | 61.286 | -61.6037 | 61.5291 | 61.4946 | 0.20853 | -61.4685 | -61.7537 | 61.658 | 61.7253 | 61.9355 | 61.5661 | -61.8154 | 61.6217 | 61.7569 | 61.4717 | 61.5742 | -61.9394
657.25 | 123.5001 | -61.5417 | 61.7157 | 0.049183 | -0.03933 | 0.047302 | -0.022462 | -0.012547 | 0.0012896 | 0.096896 | 0.0011206 | 0.065721 | -0.019486 | 0.066208 | 0.0071659 | -0.017266 | 0.047193 | -0.012988 | 0.10249 | -0.008799 | 0.39837 | -0.044742 | 0.005626 | 0.050725 | -0.0243 | 0.1074 | 0.2289 | -0.05635 | -0.23741 | 61.497 | -61.6132 | 61.5245 | 61.5288 | 0.031754 | -61.7245 | -61.3173 | 61.3043 | -61.6083 | 61.5474 | 61.5174 | 0.21311 | -61.4868 | -61.772 | 61.6442 | 61.5329 | 61.9401 | 61.5889 | -61.7604 | 61.6491 | 61.7706 | 61.4854 | 61.5925 | -61.9531
658.2344 | 123.5001 | -61.5555 | 61.6791 | 0.033921 | -0.03933 | 0.046234 | -0.021393 | -0.012547 | 0.0012896 | 0.051113 | 0.0021886 | 0.064652 | -0.020554 | 0.065139 | 0.0060979 | -0.017266 | 0.042614 | -0.008409 | 0.12996 | -0.008799 | 0.40295 | -0.049321 | -0.00811 | 0.041567 | -0.028879 | 0.098244 | 0.22432 | -0.051771 | -0.24199 | 61.5062 | -61.5491 | 61.5382 | 61.5471 | 0.040912 | -61.6879 | -61.2761 | 61.3135 | -61.5808 | 61.5474 | 61.5266 | 0.21311 | -61.4548 | -61.7308 | 61.6854 | 61.5467 | 61.9584 | 61.5981 | -61.7284 | 61.6537 | 61.7798 | 61.5037 | 61.597 | -61.9211
659.2344 | 123.5321 | -61.5234 | 61.6791 | 0.049183 | -0.03933 | 0.046234 | -0.021393 | -0.013616 | 0.0012896 | 0.066374 | 0.0021886 | 0.064652 | -0.017349 | 0.065139 | 0.0050299 | -0.021844 | 0.038035 | -0.008409 | 0.12538 | -0.013378 | 0.40295 | -0.058478 | 0.001048 | 0.046146 | -0.0243 | 0.098244 | 0.2289 | -0.05635 | -0.23741 | 61.465 | -61.5537 | 61.5016 | 61.515 | 0.050069 | -61.6925 | -61.2761 | 61.286 | -61.5808 | 61.5245 | 61.4991 | 0.21311 | -61.4502 | -61.7354 | 61.6488 | 61.5101 | 61.9264 | 61.5615 | -61.7376 | 61.6217 | 61.7523 | 61.4671 | 61.5696 | -61.9165
660.2344 | 123.5367 | -61.528 | 61.6699 | 0.064445 | -0.03933 | 0.047302 | -0.021393 | -0.012547 | -0.00084642 | 0.066374 | 0.0032566 | 0.065721 | -0.018418 | 0.067276 | 0.0082349 | -0.017266 | 0.038035 | 0.000747 | 0.13454 | -0.013378 | 0.40295 | -0.058478 | 0.001048 | 0.046146 | -0.015143 | 0.10282 | 0.2289 | -0.060928 | -0.23741 | 61.4695 | -61.5354 | 61.5107 | 61.5288 | 0.059225 | -61.6833 | -61.267 | 61.2906 | -61.5671 | 61.5291 | 61.5129 | 0.22227 | -61.441 | -61.7308 | 61.6626 | 61.5146 | 61.931 | 61.5661 | -61.7284 | 61.6308 | 61.7569 | 61.4671 | 61.5742 | -61.9073
661.2344 | 123.5321 | -61.5326 | 61.6791 | 0.064445 | -0.041467 | 0.047302 | -0.021393 | -0.012547 | 0.0012896 | 0.081635 | 0.0043246 | 0.064652 | -0.018418 | 0.067276 | 0.0071659 | -0.017266 | 0.038035 | -0.008409 | 0.11165 | -0.022536 | 0.39837 | -0.049321 | 0.001048 | 0.050725 | -0.019721 | 0.1074 | 0.22432 | -0.060928 | -0.23741 | 61.4833 | -61.5674 | 61.5153 | 61.5242 | 0.040912 | -61.7016 | -61.2807 | 61.2952 | -61.5717 | 61.5336 | 61.5129 | 0.21769 | -61.4548 | -61.74 | 61.6442 | 61.5101 | 61.931 | 61.5706 | -61.7284 | 61.64 | 61.7569 | 61.4717 | 61.5833 | -61.9165
662.25 | 123.5092 | -61.528 | 61.7111 | 0.079707 | -0.037194 | 0.047302 | -0.02353 | -0.014684 | 0.0012896 | 0.081635 | 0.0021886 | 0.064652 | -0.019486 | 0.067276 | 0.0060979 | -0.017266 | 0.033457 | -0.008409 | 0.11165 | -0.013378 | 0.40753 | -0.044742 | -0.003531 | 0.050725 | -0.015143 | 0.10282 | 0.23348 | -0.060928 | -0.23283 | 61.4833 | -61.5995 | 61.5107 | 61.5196 | 0.036333 | -61.7245 | -61.3036 | 61.2952 | -61.6083 | 61.5245 | 61.5129 | 0.21769 | -61.4776 | -61.772 | 61.6397 | 61.5146 | 61.9355 | 61.5615 | -61.7559 | 61.6308 | 61.7615 | 61.4671 | 61.5787 | -61.944
663.2344 | 123.5046 | -61.528 | 61.6928 | 0.033921 | -0.03933 | 0.046234 | -0.021393 | -0.013616 | 0.00022158 | 0.051113 | 0.0011206 | 0.062516 | -0.019486 | 0.066208 | 0.0071659 | -0.021844 | 0.033457 | -0.003831 | 0.10707 | -0.013378 | 0.39379 | -0.053899 | 0.001048 | 0.041567 | -0.028879 | 0.098244 | 0.22432 | -0.05635 | -0.23741 | 61.4741 | -61.5857 | 61.5062 | 61.5242 | 0.050068 | -61.7062 | -61.299 | 61.2906 | -61.5946 | 61.5291 | 61.4991 | 0.20853 | -61.4685 | -61.7492 | 61.6351 | 61.5146 | 61.9218 | 61.5615 | -61.7467 | 61.6263 | 61.7523 | 61.4717 | 61.5696 | -61.9302
664.2344 | 123.5229 | -61.5601 | 61.6928 | 0.049183 | -0.037194 | 0.046234 | -0.022462 | -0.013616 | 0.0023586 | 0.035852 | 0.0032566 | 0.064652 | -0.019486 | 0.067276 | 0.0060979 | -0.012688 | 0.038035 | -0.012988 | 0.11165 | -0.013378 | 0.39379 | -0.072215 | 0.005626 | 0.046146 | -0.0243 | 0.098244 | 0.2289 | -0.065507 | -0.23741 | 61.4878 | -61.5812 | 61.5474 | 61.5471 | 0.059227 | -61.7062 | -61.299 | 61.3226 | -61.5946 | 61.5657 | 61.5358 | 0.21311 | -61.4639 | -61.7583 | 61.6717 | 61.5467 | 61.9538 | 61.5981 | -61.765 | 61.6583 | 61.789 | 61.4946 | 61.6062 | -61.9302
665.2344 | 123.5275 | -61.5417 | 61.6974 | 0.064445 | -0.03933 | 0.047302 | -0.022462 | -0.014684 | 0.0023586 | 0.081635 | 5.2637e-05 | 0.065721 | -0.018418 | 0.067276 | 0.0060979 | -0.017266 | 0.038035 | -0.003831 | 0.11165 | -0.017957 | 0.39837 | -0.076794 | 0.005626 | 0.046146 | -0.019721 | 0.098244 | 0.23348 | -0.05635 | -0.23283 | 61.465 | -61.5857 | 61.5245 | 61.5379 | 0.072963 | -61.7153 | -61.299 | 61.3089 | -61.5991 | 61.5474 | 61.522 | 0.21311 | -61.4639 | -61.7537 | 61.6534 | 61.5238 | 61.9401 | 61.5798 | -61.7742 | 61.64 | 61.7752 | 61.4854 | 61.5879 | -61.9302
666.2344 | 123.5413 | -61.5463 | 61.702 | 0.049183 | -0.03933 | 0.047302 | -0.021393 | -0.014684 | 0.0034266 | 0.051113 | 0.0011206 | 0.064652 | -0.020554 | 0.067276 | 0.0050299 | -0.012688 | 0.042614 | -0.003831 | 0.093333 | -0.022536 | 0.39379 | -0.044742 | 0.001048 | 0.046146 | -0.0243 | 0.098244 | 0.21516 | -0.051771 | -0.24199 | 61.5016 | -61.6086 | 61.5336 | 61.5425 | 0.040911 | -61.7245 | -61.3082 | 61.3043 | -61.6037 | 61.5474 | 61.522 | 0.21769 | -61.4868 | -61.7537 | 61.6397 | 61.5238 | 61.9401 | 61.5889 | -61.7467 | 61.6446 | 61.7615 | 61.4946 | 61.5925 | -61.944
667.25 | 123.5092 | -61.5646 | 61.7294 | 0.079707 | -0.03933 | 0.045166 | -0.022462 | -0.014684 | 0.00022158 | 0.081635 | 0.0021886 | 0.064652 | -0.019486 | 0.067276 | 0.0060979 | -0.012688 | 0.028878 | 0.000747 | 0.12538 | -0.008799 | 0.39379 | -0.049321 | 0.001048 | 0.041567 | -0.0243 | 0.098244 | 0.21974 | -0.060928 | -0.23741 | 61.5153 | -61.604 | 61.5519 | 61.5654 | 0.050068 | -61.7382 | -61.3356 | 61.3272 | -61.6312 | 61.5657 | 61.5403 | 0.21311 | -61.5097 | -61.7904 | 61.69 | 61.5558 | 61.9584 | 61.5935 | -61.7788 | 61.6629 | 61.7844 | 61.5037 | 61.6062 | -61.9668
668.2344 | 123.5413 | -61.5463 | 61.7111 | 0.049183 | -0.041467 | 0.046234 | -0.020325 | -0.013616 | 0.0012896 | 0.066374 | 0.0011206 | 0.064652 | -0.020554 | 0.067276 | 0.0082349 | -0.012688 | 0.042614 | -0.003831 | 0.10249 | -0.017957 | 0.39837 | -0.040163 | 0.001048 | 0.041567 | -0.028879 | 0.098244 | 0.21974 | -0.060928 | -0.24199 | 61.5062 | -61.6086 | 61.5336 | 61.5425 | 0.036332 | -61.7291 | -61.3128 | 61.3043 | -61.6129 | 61.5474 | 61.5174 | 0.21311 | -61.4914 | -61.772 | 61.6488 | 61.5284 | 61.9447 | 61.5889 | -61.7513 | 61.6446 | 61.7661 | 61.4854 | 61.5879 | -61.9531
669.2344 | 123.5504 | -61.5555 | 61.6928 | 0.049183 | -0.03933 | 0.047302 | -0.022462 | -0.013616 | 0.0034266 | 0.051113 | 0.0021886 | 0.064652 | -0.020554 | 0.068344 | 0.0060979 | -0.012688 | 0.033457 | 0.000747 | 0.11622 | 0.000359 | 0.39379 | -0.053899 | 0.010205 | 0.050725 | -0.028879 | 0.098244 | 0.22432 | -0.051771 | -0.24657 | 61.5016 | -61.5766 | 61.5428 | 61.5562 | 0.054646 | -61.6925 | -61.299 | 61.3089 | -61.5946 | 61.5657 | 61.5266 | 0.21769 | -61.4685 | -61.7446 | 61.6717 | 61.5558 | 61.9493 | 61.5889 | -61.7467 | 61.6537 | 61.7798 | 61.5037 | 61.6062 | -61.9394
670.2344 | 123.5641 | -61.5417 | 61.7065 | 0.079707 | -0.03933 | 0.046234 | -0.022462 | -0.013616 | 0.0012896 | 0.051113 | 0.0032566 | 0.065721 | -0.020554 | 0.067276 | 0.0050299 | -0.017266 | 0.038035 | -0.003831 | 0.11622 | 0.014096 | 0.39379 | -0.053899 | 0.001048 | 0.041567 | -0.015143 | 0.093665 | 0.22432 | -0.05635 | -0.22825 | 61.4878 | -61.5903 | 61.5245 | 61.5379 | 0.050068 | -61.6924 | -61.3128 | 61.3135 | -61.6129 | 61.5428 | 61.5266 | 0.21311 | -61.4822 | -61.7629 | 61.658 | 61.5558 | 61.9355 | 61.5798 | -61.7604 | 61.6354 | 61.7661 | 61.4854 | 61.5833 | -61.9348
671.25 | 123.5229 | -61.5692 | 61.702 | 0.079707 | -0.038262 | 0.045166 | -0.02353 | -0.015752 | -0.00084642 | 0.066374 | 0.0021886 | 0.063584 | -0.019486 | 0.068344 | 0.0071659 | -0.012688 | 0.038035 | -0.003831 | 0.10249 | 0.03699 | 0.39379 | -0.049321 | 0.005626 | 0.041567 | -0.028879 | 0.10282 | 0.22432 | -0.051771 | -0.23741 | 61.5199 | -61.5995 | 61.5565 | 61.5654 | 0.04549 | -61.665 | -61.3082 | 61.3318 | -61.5991 | 61.5748 | 61.5403 | 0.20853 | -61.4776 | -61.7537 | 61.6717 | 61.6062 | 61.963 | 61.6072 | -61.7513 | 61.672 | 61.7935 | 61.5174 | 61.6108 | -61.9394
672.25 | 123.5504 | -61.5646 | 61.7294 | 0.049183 | -0.037194 | 0.047302 | -0.021393 | -0.013616 | 0.0034266 | 0.066374 | 0.0011206 | 0.064652 | -0.020554 | 0.067276 | 0.0082349 | -0.017266 | 0.038035 | -0.003831 | 0.10249 | 0.041569 | 0.39379 | -0.049321 | 0.010205 | 0.046146 | -0.0243 | 0.093665 | 0.2289 | -0.051771 | -0.23283 | 61.5153 | -61.6269 | 61.5474 | 61.5608 | 0.04549 | -61.6879 | -61.3356 | 61.3318 | -61.6358 | 61.5748 | 61.5403 | 0.20853 | -61.5005 | -61.7812 | 61.6671 | 61.6062 | 61.9584 | 61.6027 | -61.7788 | 61.6583 | 61.7935 | 61.5129 | 61.6108 | -61.9623
673.2344 | 123.4543 | -61.6013 | 61.7432 | 0.033921 | -0.03933 | 0.046234 | -0.022462 | -0.014684 | 0.0023586 | 0.035852 | 5.2637e-05 | 0.065721 | -0.020554 | 0.067276 | 0.0071659 | -0.012688 | 0.038035 | 0.000747 | 0.1208 | 0.041569 | 0.39379 | -0.044742 | -0.003531 | 0.046146 | -0.0243 | 0.098244 | 0.2289 | -0.05635 | -0.24199 | 61.5565 | -61.6224 | 61.5886 | 61.602 | 0.045489 | -61.7016 | -61.3494 | 61.3593 | -61.6449 | 61.5977 | 61.577 | 0.21769 | -61.5143 | -61.7995 | 61.7221 | 61.6428 | 61.995 | 61.6393 | -61.7879 | 61.6995 | 61.8302 | 61.5449 | 61.6474 | -61.9852
674.2344 | 123.4726 | -61.5967 | 61.7249 | 0.049183 | -0.038262 | 0.047302 | -0.021393 | -0.012547 | 0.0023586 | 0.066374 | 0.0021886 | 0.065721 | -0.018418 | 0.067276 | 0.0060979 | -0.012688 | 0.038035 | 0.005325 | 0.11622 | 0.03699 | 0.39379 | -0.067636 | 0.005626 | 0.046146 | -0.0243 | 0.098244 | 0.2289 | -0.047193 | -0.24657 | 61.529 | -61.6086 | 61.584 | 61.602 | 0.072961 | -61.6879 | -61.3311 | 61.3501 | -61.6266 | 61.6023 | 61.5724 | 0.22227 | -61.496 | -61.772 | 61.7129 | 61.6337 | 61.9905 | 61.6347 | -61.7925 | 61.6949 | 61.8256 | 61.5495 | 61.6428 | -61.9714
675.25 | 123.5046 | -61.5738 | 61.702 | 0.079707 | -0.03933 | 0.046234 | -0.022462 | -0.014684 | 0.0012896 | 0.081635 | 0.0011206 | 0.065721 | -0.020554 | 0.068344 | 0.0071659 | -0.017266 | 0.033457 | -0.003831 | 0.093333 | 0.041569 | 0.39379 | -0.049321 | -0.00811 | 0.050725 | -0.028879 | 0.089087 | 0.22432 | -0.042614 | -0.23741 | 61.5245 | -61.6086 | 61.5565 | 61.57 | 0.04549 | -61.6604 | -61.3082 | 61.3364 | -61.6129 | 61.5657 | 61.5449 | 0.20853 | -61.4776 | -61.7446 | 61.6671 | 61.6154 | 61.9676 | 61.6072 | -61.7513 | 61.6629 | 61.7981 | 61.5312 | 61.6245 | -61.9394
676.25 | 123.5046 | -61.5509 | 61.7386 | 0.033921 | -0.038262 | 0.046234 | -0.022462 | -0.013616 | 0.0023586 | 0.051113 | 0.0021886 | 0.065721 | -0.021622 | 0.069413 | 0.0071659 | -0.021844 | 0.033457 | -0.003831 | 0.1208 | 0.050727 | 0.2839 | -0.076794 | 0.005626 | 0.050725 | -0.0243 | 0.093665 | 0.22432 | -0.051771 | -0.23283 | 61.4741 | -61.6178 | 61.5291 | 61.5471 | 0.072963 | -61.6879 | -61.4547 | 61.3181 | -61.6449 | 61.5565 | 61.5266 | 0.20853 | -61.5143 | -61.7904 | 61.6717 | 61.6016 | 61.8348 | 61.5844 | -61.8154 | 61.6446 | 61.7752 | 61.4991 | 61.6016 | -61.9714
677.25 | 123.5321 | -61.5601 | 61.7111 | 0.049183 | -0.040399 | 0.046234 | -0.021393 | -0.014684 | 0.00022158 | 0.035852 | 0.0011206 | 0.064652 | -0.019486 | 0.068344 | 0.0060979 | -0.021844 | 0.038035 | 0.000747 | 0.12538 | 0.046148 | 0.29306 | -0.058478 | 0.001048 | 0.041567 | -0.028879 | 0.093665 | 0.21974 | -0.060928 | -0.23283 | 61.5016 | -61.5857 | 61.5382 | 61.5608 | 0.059225 | -61.665 | -61.4181 | 61.3272 | -61.6175 | 61.5611 | 61.5312 | 0.20395 | -61.4914 | -61.772 | 61.6854 | 61.6062 | 61.8531 | 61.5981 | -61.7696 | 61.6537 | 61.7798 | 61.4991 | 61.6016 | -61.944
678.2344 | 123.3856 | -61.6333 | 61.7203 | 0.049183 | -0.040399 | 0.048371 | -0.021393 | -0.015752 | 0.0012896 | 0.035852 | 0.0011206 | 0.063584 | -0.018418 | 0.070481 | 0.0071659 | -0.012688 | 0.038035 | -0.008409 | 0.10249 | 0.046148 | 0.29764 | -0.049321 | 0.001048 | 0.046146 | -0.0243 | 0.098244 | 0.2289 | -0.074664 | -0.23283 | 61.584 | -61.6178 | 61.6206 | 61.6249 | 0.040912 | -61.6741 | -61.4226 | 61.4005 | -61.622 | 61.6343 | 61.609 | 0.20853 | -61.4914 | -61.7949 | 61.7358 | 61.6794 | 61.9309 | 61.6713 | -61.7696 | 61.7315 | 61.8622 | 61.5586 | 61.6794 | -61.9531
679.2344 | 123.468 | -61.6104 | 61.7249 | 0.033921 | -0.043604 | 0.046234 | -0.021393 | -0.013616 | 0.00022158 | 0.096896 | 0.0021886 | 0.065721 | -0.019486 | 0.068344 | 0.0071659 | -0.017266 | 0.042614 | -0.003831 | 0.10707 | 0.050727 | 0.29306 | -0.053899 | 0.001048 | 0.046146 | -0.028879 | 0.089087 | 0.2289 | -0.070086 | -0.24199 | 61.5565 | -61.6178 | 61.5931 | 61.6066 | 0.050068 | -61.6741 | -61.4318 | 61.3684 | -61.6358 | 61.6115 | 61.5815 | 0.21311 | -61.496 | -61.7949 | 61.7175 | 61.6611 | 61.9035 | 61.653 | -61.7788 | 61.6995 | 61.8393 | 61.5403 | 61.6566 | -61.9668
680.25 | 123.5504 | -61.5875 | 61.7157 | 0.049183 | -0.040399 | 0.046234 | -0.020325 | -0.013616 | 0.0012896 | 0.066374 | 0.0021886 | 0.064652 | -0.020554 | 0.067276 | 0.0060979 | -0.021844 | 0.033457 | -0.003831 | 0.11622 | 0.046148 | 0.30222 | -0.067636 | 0.001048 | 0.046146 | -0.019721 | 0.093665 | 0.22432 | -0.079243 | -0.24657 | 61.5199 | -61.5995 | 61.5657 | 61.5837 | 0.063805 | -61.6696 | -61.4135 | 61.341 | -61.622 | 61.5886 | 61.5678 | 0.22685 | -61.4914 | -61.7949 | 61.7037 | 61.6337 | 61.8897 | 61.621 | -61.7833 | 61.6812 | 61.8118 | 61.5083 | 61.6337 | -61.9623
681.25 | 123.5321 | -61.5646 | 61.702 | 0.079707 | -0.041467 | 0.046234 | -0.022462 | -0.013616 | 0.00022158 | 0.051113 | 0.0021886 | 0.065721 | -0.020554 | 0.068344 | 0.0071659 | -0.012688 | 0.038035 | -0.008409 | 0.10707 | 0.055306 | 0.28848 | -0.063057 | 0.005626 | 0.041567 | -0.028879 | 0.093665 | 0.2289 | -0.097557 | -0.23741 | 61.5016 | -61.5949 | 61.5519 | 61.5562 | 0.054648 | -61.6467 | -61.4135 | 61.3272 | -61.6083 | 61.5703 | 61.5358 | 0.20853 | -61.4731 | -61.7995 | 61.6717 | 61.6199 | 61.8531 | 61.6027 | -61.765 | 61.6583 | 61.7935 | 61.4671 | 61.6062 | -61.9394
682.2344 | 123.436 | -61.5967 | 61.7752 | 0.033921 | -0.040399 | 0.047302 | -0.022462 | -0.013616 | 0.0023586 | 0.051113 | 0.0021886 | 0.064652 | -0.019486 | 0.070481 | 0.0071659 | -0.017266 | 0.033457 | -0.003831 | 0.088755 | 0.03699 | 0.29764 | -0.063057 | 0.005626 | 0.041567 | -0.033458 | 0.093665 | 0.22432 | -0.11587 | -0.23283 | 61.5336 | -61.6865 | 61.5794 | 61.5928 | 0.059226 | -61.7382 | -61.4776 | 61.3638 | -61.6815 | 61.6023 | 61.5632 | 0.19937 | -61.5509 | -61.8911 | 61.6854 | 61.6337 | 61.8943 | 61.6301 | -61.8383 | 61.6903 | 61.821 | 61.4808 | 61.6382 | -62.008
683.2344 | 123.4451 | -61.6333 | 61.7523 | 0.049183 | -0.043604 | 0.046234 | -0.02353 | -0.014684 | 0.00022158 | 0.081635 | 0.0011206 | 0.064652 | -0.020554 | 0.069413 | 0.0050299 | -0.017266 | 0.033457 | -0.003831 | 0.11622 | 0.041569 | 0.30222 | -0.049321 | 0.005626 | 0.050725 | -0.028879 | 0.089087 | 0.2289 | -0.11129 | -0.24199 | 61.584 | -61.6361 | 61.616 | 61.6295 | 0.04549 | -61.7107 | -61.4501 | 61.3913 | -61.6632 | 61.6389 | 61.6044 | 0.21311 | -61.5234 | -61.8636 | 61.7495 | 61.6749 | 61.9355 | 61.6668 | -61.8016 | 61.7224 | 61.8622 | 61.522 | 61.684 | -61.9943
684.2344 | 123.4772 | -61.6013 | 61.734 | 0.064445 | -0.041467 | 0.046234 | -0.022462 | -0.014684 | 0.00022158 | 0.066374 | 0.0021886 | 0.063584 | -0.019486 | 0.068344 | 0.0060979 | -0.012688 | 0.042614 | -0.008409 | 0.12538 | 0.046148 | 0.30222 | -0.058478 | 0.001048 | 0.050725 | -0.0243 | 0.098244 | 0.21516 | -0.12045 | -0.23741 | 61.5428 | -61.6086 | 61.5886 | 61.5928 | 0.050069 | -61.6879 | -61.4318 | 61.3638 | -61.6358 | 61.6023 | 61.577 | 0.21311 | -61.5188 | -61.8545 | 61.7266 | 61.6474 | 61.9035 | 61.6439 | -61.7925 | 61.6995 | 61.8164 | 61.4808 | 61.652 | -61.9714
685.25 | 123.5413 | -61.5555 | 61.7523 | 0.064445 | -0.040399 | 0.047302 | -0.019256 | -0.012547 | 0.00022158 | 0.035852 | 0.0021886 | 0.063584 | -0.019486 | 0.068344 | 0.0039619 | -0.017266 | 0.038035 | -0.003831 | 0.088755 | 0.046148 | 0.3068 | -0.063057 | 0.001048 | 0.050725 | -0.028879 | 0.10282 | 0.2289 | -0.079243 | -0.24199 | 61.4924 | -61.6636 | 61.5382 | 61.5517 | 0.059226 | -61.7062 | -61.4455 | 61.3135 | -61.6495 | 61.5565 | 61.5266 | 0.21311 | -61.5234 | -61.8316 | 61.6442 | 61.6016 | 61.8623 | 61.5935 | -61.8154 | 61.6583 | 61.7844 | 61.4762 | 61.6062 | -61.9943
686.25 | 123.5779 | -61.5601 | 61.6882 | 0.033921 | -0.041467 | 0.045166 | -0.024598 | -0.013616 | -0.00084642 | 0.066374 | 0.0021886 | 0.064652 | -0.019486 | 0.069413 | 0.0050299 | -0.012688 | 0.038035 | 0.000747 | 0.10707 | 0.03699 | 0.30222 | -0.072215 | -0.003531 | 0.041567 | -0.0243 | 0.098244 | 0.21974 | -0.10671 | -0.24657 | 61.4878 | -61.5812 | 61.5474 | 61.5608 | 0.072962 | -61.6512 | -61.386 | 61.3135 | -61.59 | 61.5565 | 61.5358 | 0.22227 | -61.4685 | -61.7949 | 61.6671 | 61.597 | 61.8623 | 61.5981 | -61.7604 | 61.6583 | 61.7798 | 61.4533 | 61.6016 | -61.9348
687.25 | 123.5916 | -61.5784 | 61.734 | 0.064445 | -0.042535 | 0.048371 | -0.02353 | -0.013616 | -0.00084642 | 0.051113 | 0.0021886 | 0.064652 | -0.020554 | 0.069413 | 0.0060979 | -0.012688 | 0.038035 | -0.008409 | 0.1208 | 0.032411 | 0.29764 | -0.053899 | 0.001048 | 0.050725 | -0.028879 | 0.093665 | 0.2289 | -0.11587 | -0.24199 | 61.5245 | -61.6132 | 61.5657 | 61.57 | 0.04549 | -61.7016 | -61.4364 | 61.3364 | -61.6403 | 61.5794 | 61.5495 | 0.21311 | -61.5051 | -61.8499 | 61.6992 | 61.6108 | 61.876 | 61.6164 | -61.7879 | 61.672 | 61.8073 | 61.4625 | 61.6291 | -61.976

## Thermal Data
Fire Time | South 11 C | Cable 1 | Cable 2
-0.0427 | 28.5861 | 27.9716 | 28.2515
0.9573 | 28.5876 | 27.9645 | 28.2461
1.9573 | 28.5885 | 27.9878 | 28.2441
2.9573 | 28.5732 | 27.9818 | 28.244
3.9573 | 28.6319 | 27.9816 | 28.237
4.9573 | 29.0443 | 27.9751 | 28.2414
5.9573 | 30.0415 | 27.9672 | 28.2363
6.9573 | 31.6397 | 27.9686 | 28.2334
7.9573 | 33.7527 | 27.9652 | 28.2366
8.9573 | 36.3133 | 27.9566 | 28.2381
9.9573 | 39.2776 | 27.9649 | 28.2422
10.9573 | 42.6006 | 27.9651 | 28.2471
11.9573 | 46.189 | 27.9671 | 28.2585
12.9573 | 50.0452 | 27.9764 | 28.2772
13.9573 | 54.0995 | 27.9808 | 28.3033
14.9573 | 58.3576 | 27.998 | 28.3347
15.9573 | 62.8089 | 28.0257 | 28.3602
16.9573 | 67.4722 | 28.0425 | 28.3978
17.9573 | 72.2876 | 28.064 | 28.4421
18.9573 | 77.1942 | 28.0942 | 28.5039
19.9573 | 82.191 | 28.1335 | 28.5709
20.9573 | 87.3494 | 28.1801 | 28.6441
21.9573 | 92.5832 | 28.2147 | 28.7399
22.9573 | 97.9223 | 28.2872 | 28.8305
23.9573 | 103.3497 | 28.3352 | 28.947
24.9573 | 108.8733 | 28.3993 | 29.0706
25.9573 | 114.445 | 28.4857 | 29.2092
26.9573 | 120.0597 | 28.5664 | 29.3569
27.9573 | 125.7272 | 28.6584 | 29.534
28.9573 | 131.4747 | 28.762 | 29.7088
29.9573 | 137.2652 | 28.8704 | 29.9036
30.9573 | 143.0647 | 28.9996 | 30.103
31.9573 | 148.8918 | 29.1316 | 30.3219
32.9573 | 154.7512 | 29.2822 | 30.5556
33.9573 | 160.5944 | 29.4355 | 30.7969
34.9573 | 166.4528 | 29.6116 | 31.0657
35.9573 | 172.2964 | 29.7932 | 31.3335
36.9573 | 178.1244 | 29.9813 | 31.624
37.9573 | 183.9768 | 30.1899 | 31.9203
38.9573 | 189.8203 | 30.4115 | 32.2477
39.9573 | 195.7149 | 30.6384 | 32.5981
40.9573 | 201.565 | 30.8883 | 32.9565
41.9573 | 207.3946 | 31.1462 | 33.3387
42.9573 | 213.2808 | 31.4168 | 33.7468
43.9573 | 219.1379 | 31.7125 | 34.1611
44.9573 | 224.9902 | 32.0028 | 34.5981
45.9573 | 230.8764 | 32.3198 | 35.0472
46.9573 | 236.7533 | 32.6383 | 35.5343
47.9573 | 242.566 | 32.979 | 36.0257
48.9573 | 248.371 | 33.345 | 36.5666
49.9573 | 254.2333 | 33.7212 | 37.1324
50.9573 | 260.1511 | 34.1139 | 37.6893
51.9573 | 265.9712 | 34.5062 | 38.3034
52.9573 | 271.7402 | 34.9331 | 38.9306
53.9573 | 277.4415 | 35.3727 | 39.5843
54.9573 | 283.1055 | 35.8264 | 40.2455
55.9573 | 288.8124 | 36.3036 | 40.9316
56.9573 | 294.5422 | 36.7731 | 41.6247
57.9573 | 300.2765 | 37.294 | 42.3508
58.9573 | 305.9702 | 37.8019 | 43.0862
59.9573 | 311.6205 | 38.3453 | 43.8624
60.9573 | 317.1417 | 38.9109 | 44.6522
61.9573 | 322.6226 | 39.5115 | 45.472
62.9573 | 328.1764 | 40.1052 | 46.3132
63.9573 | 333.6904 | 40.727 | 47.1698
64.9573 | 339.1922 | 41.3776 | 48.0519
65.9573 | 344.6081 | 42.04 | 48.9523
66.9573 | 349.9371 | 42.7043 | 49.8915
67.9573 | 355.2809 | 43.4198 | 50.8456
68.9573 | 360.6305 | 44.125 | 51.8378
69.9573 | 366.0293 | 44.8647 | 52.8388
70.9573 | 371.3999 | 45.6214 | 53.8929
71.9573 | 376.7046 | 46.4005 | 54.9619
72.9573 | 382.0413 | 47.2021 | 56.062
73.9573 | 387.304 | 48.0321 | 57.2011
74.9573 | 392.5311 | 48.8967 | 58.3843
75.9573 | 397.6589 | 49.7802 | 59.5736
76.9573 | 402.7974 | 50.6982 | 60.7991
77.9573 | 407.9136 | 51.6415 | 62.0654
78.9573 | 412.9916 | 52.6337 | 63.3477
79.9573 | 417.9175 | 53.6338 | 64.673
80.9573 | 422.7388 | 54.6616 | 66.0242
81.9573 | 427.2674 | 55.7256 | 67.4079
82.9573 | 431.5739 | 56.8248 | 68.8294
83.9573 | 435.6063 | 57.9261 | 70.2658
84.9573 | 439.2886 | 59.083 | 71.7204
85.9573 | 442.6101 | 60.2497 | 73.1936
86.9573 | 445.806 | 61.4325 | 74.6776
87.9573 | 448.7708 | 62.6366 | 76.1903
88.9573 | 451.7082 | 63.8548 | 77.7368
89.9573 | 454.5866 | 65.0916 | 79.2966
90.9573 | 457.3315 | 66.3277 | 80.8624
91.9573 | 459.801 | 67.5996 | 82.4524
92.9573 | 462.086 | 68.8684 | 84.0407
93.9573 | 464.2319 | 70.1498 | 85.65
94.9573 | 466.1251 | 71.4418 | 87.2693
95.9573 | 467.6174 | 72.7364 | 88.8881
96.9573 | 469.0282 | 74.0313 | 90.5187
97.9573 | 470.0898 | 75.3313 | 92.153
98.9573 | 470.994 | 76.6432 | 93.8007
99.9573 | 471.6666 | 77.9629 | 95.4385
100.9573 | 472.2411 | 79.2651 | 97.0927
101.9573 | 472.6336 | 80.5745 | 98.7364
102.9573 | 472.8614 | 81.8792 | 100.3717
103.9573 | 473.0604 | 83.1792 | 101.9882
104.9573 | 473.2256 | 84.4809 | 103.5907
105.9573 | 473.3305 | 85.7742 | 105.1851
106.9573 | 473.362 | 87.0713 | 106.7616
107.9573 | 473.2055 | 88.3498 | 108.3042
108.9573 | 473.1648 | 89.6227 | 109.8444
109.9573 | 472.9922 | 90.8986 | 111.3769
110.9573 | 472.7939 | 92.1464 | 112.8687
111.9573 | 472.5949 | 93.4089 | 114.3572
112.9573 | 472.3645 | 94.6568 | 115.8252
113.9573 | 472.2559 | 95.9112 | 117.2777
114.9573 | 472.0579 | 97.1401 | 118.7035
115.9573 | 472.0132 | 98.3742 | 120.107
116.9573 | 471.9106 | 99.575 | 121.5087
117.9573 | 471.7894 | 100.7915 | 122.8845
118.9573 | 471.5835 | 101.9929 | 124.2653
119.9573 | 471.4792 | 103.1826 | 125.6092
120.9573 | 471.3744 | 104.3735 | 126.9363
121.9573 | 471.361 | 105.5494 | 128.2464
122.9573 | 471.5027 | 106.7252 | 129.5431
123.9573 | 471.5487 | 107.8916 | 130.8374
124.9573 | 471.6762 | 109.0437 | 132.1244
125.9573 | 471.7654 | 110.1876 | 133.4103
126.9573 | 471.913 | 111.3176 | 134.6986
127.9573 | 472.0516 | 112.4518 | 135.9635
128.9573 | 472.1982 | 113.5845 | 137.2217
129.9573 | 472.2948 | 114.7189 | 138.4652
130.9573 | 472.5117 | 115.8386 | 139.7084
131.9573 | 472.7976 | 116.962 | 140.9454
132.9573 | 472.9333 | 118.0677 | 142.1758
133.9573 | 473.104 | 119.1883 | 143.3958
134.9573 | 473.2825 | 120.2841 | 144.6188
135.9573 | 473.4163 | 121.3849 | 145.8194
136.9573 | 473.6435 | 122.4767 | 147.0195
137.9573 | 473.8148 | 123.5643 | 148.2176
138.9573 | 473.8695 | 124.6664 | 149.4101
139.9573 | 473.8305 | 125.7465 | 150.5988
140.9573 | 473.9609 | 126.8125 | 151.7741
141.9573 | 474.0097 | 127.8812 | 152.9608
142.9573 | 474.1138 | 128.9294 | 154.1394
143.9573 | 474.1457 | 129.9738 | 155.3042
144.9573 | 474.1589 | 130.9986 | 156.47
145.9573 | 474.1737 | 132.0253 | 157.6185
146.9573 | 474.2364 | 133.0318 | 158.7651
147.9573 | 474.2034 | 134.0544 | 159.9062
148.9573 | 474.1655 | 135.0331 | 161.0501
149.9573 | 474.1563 | 135.999 | 162.1745
150.9573 | 474.2137 | 136.9696 | 163.3056
151.9573 | 474.2029 | 137.9158 | 164.4167
152.9573 | 474.2761 | 138.8261 | 165.5282
153.9573 | 474.2655 | 139.7417 | 166.6302
154.9573 | 474.2348 | 140.6309 | 167.7155
155.9573 | 474.2716 | 141.5074 | 168.7939
156.9573 | 474.3012 | 142.3736 | 169.8689
157.9573 | 474.3113 | 143.2103 | 170.9241
158.9573 | 474.1711 | 144.0514 | 171.9773
159.9573 | 474.1839 | 144.8762 | 173.0233
160.9573 | 474.2579 | 145.6775 | 174.0492
161.9573 | 474.1884 | 146.4643 | 175.0679
162.9573 | 474.2002 | 147.2414 | 176.0661
163.9573 | 474.167 | 148.0139 | 177.0596
164.9573 | 474.1436 | 148.7712 | 178.0317
165.9573 | 474.1349 | 149.527 | 179.0155
166.9573 | 474.1019 | 150.2816 | 179.9746
167.9573 | 474.1715 | 151.0398 | 180.9337
168.9573 | 474.2786 | 151.784 | 181.8779
169.9573 | 474.2808 | 152.5293 | 182.8223
170.9573 | 474.2983 | 153.2898 | 183.7507
171.9573 | 474.256 | 154.0269 | 184.6701
172.9573 | 474.2626 | 154.7753 | 185.5842
173.9573 | 474.2597 | 155.5118 | 186.5023
174.9573 | 474.2798 | 156.2707 | 187.3954
175.9573 | 474.394 | 157.0146 | 188.29
176.9573 | 474.4919 | 157.7489 | 189.1646
177.9573 | 474.4711 | 158.489 | 190.0384
178.9573 | 474.5008 | 159.2292 | 190.895
179.9573 | 474.5593 | 159.9753 | 191.7532
180.9573 | 474.5733 | 160.7313 | 192.612
181.9573 | 474.6434 | 161.4657 | 193.4611
182.9573 | 474.746 | 162.229 | 194.3073
183.9573 | 474.7916 | 163.009 | 195.1504
184.9573 | 474.977 | 163.7727 | 195.9829
185.9573 | 475.1143 | 164.5702 | 196.8265
186.9573 | 475.138 | 165.3642 | 197.6543
187.9573 | 475.2388 | 166.1628 | 198.4912
188.9573 | 475.4173 | 166.9767 | 199.3277
189.9573 | 475.5025 | 167.801 | 200.1813
190.9573 | 475.4699 | 168.6319 | 201.0162
191.9573 | 475.5474 | 169.4708 | 201.8571
192.9573 | 475.6449 | 170.3043 | 202.6975
193.9573 | 475.5504 | 171.1558 | 203.5345
194.9573 | 475.5835 | 172.0145 | 204.3693
195.9573 | 475.5533 | 172.9013 | 205.2068
196.9573 | 475.4923 | 173.774 | 206.0419
197.9573 | 475.3791 | 174.6495 | 206.8698
198.9573 | 475.3618 | 175.5226 | 207.7024
199.9573 | 475.4295 | 176.4048 | 208.5427
200.9573 | 475.5233 | 177.2927 | 209.3886
201.9573 | 475.4503 | 178.1645 | 210.2306
202.9573 | 475.4771 | 179.0602 | 211.0594
203.9573 | 475.5719 | 179.9429 | 211.906
204.9573 | 475.4934 | 180.816 | 212.7338
205.9573 | 475.267 | 181.7141 | 213.5603
206.9573 | 475.0748 | 182.5951 | 214.3781
207.9573 | 474.9926 | 183.4749 | 215.1882
208.9573 | 474.8589 | 184.3659 | 215.9779
209.9573 | 474.8246 | 185.2764 | 216.7459
210.9573 | 474.8466 | 186.1879 | 217.4962
211.9573 | 474.9141 | 187.0767 | 218.233
212.9573 | 474.9001 | 187.9663 | 218.9353
213.9573 | 474.8096 | 188.8621 | 219.6106
214.9573 | 474.7796 | 189.7415 | 220.2724
215.9573 | 474.7752 | 190.6354 | 220.901
216.9573 | 474.7828 | 191.5109 | 221.5504
217.9573 | 474.7982 | 192.4046 | 222.1768
218.9573 | 474.8727 | 193.2768 | 222.7821
219.9573 | 474.9272 | 194.1419 | 223.3671
220.9573 | 474.8675 | 195.0014 | 223.9373
221.9573 | 474.7521 | 195.8836 | 224.5072
222.9573 | 474.8132 | 196.748 | 225.0417
223.9573 | 474.817 | 197.6209 | 225.5026
224.9573 | 474.8475 | 198.4724 | 225.9226
225.9573 | 474.92 | 199.3491 | 226.343
226.9573 | 474.8933 | 200.2068 | 226.6101
227.9573 | 474.8451 | 201.0668 | 226.4638
228.9573 | 474.8113 | 201.9495 | 226.3089
229.9573 | 474.7519 | 202.8106 | 226.3014
230.9573 | 474.7428 | 203.6528 | 226.3853
231.9573 | 474.68 | 204.5124 | 226.615
232.9573 | 474.6858 | 205.3649 | 226.839
233.9573 | 474.6448 | 206.2044 | 227.0656
234.9573 | 474.6711 | 207.0456 | 227.2905
235.9573 | 474.8412 | 207.8749 | 227.5015
236.9573 | 474.9268 | 208.7055 | 227.7548
237.9573 | 475.083 | 209.5235 | 228.008
238.9573 | 475.1454 | 210.3374 | 228.2397
239.9573 | 475.2801 | 211.1523 | 228.4359
240.9573 | 475.3364 | 211.9629 | 228.6552
241.9573 | 475.4628 | 212.776 | 228.8451
242.9573 | 475.5612 | 213.5737 | 229.0404
243.9573 | 475.6397 | 214.376 | 229.1872
244.9573 | 475.7384 | 215.149 | 229.3282
245.9573 | 475.906 | 215.9254 | 229.5334
246.9573 | 475.9355 | 216.6649 | 229.7543
247.9573 | 475.9508 | 217.3921 | 229.9656
248.9573 | 475.8988 | 218.1086 | 230.1477
249.9573 | 475.8916 | 218.7694 | 230.39
250.9573 | 475.8572 | 219.4193 | 230.6365
251.9573 | 475.8858 | 219.9944 | 230.8886
252.9573 | 475.8804 | 220.5563 | 231.1748
253.9573 | 475.9627 | 221.1673 | 231.4398
254.9573 | 476.079 | 221.7908 | 231.722
255.9573 | 476.1232 | 222.41 | 232.0231
256.9573 | 476.1655 | 222.9972 | 232.3298
257.9573 | 476.1164 | 223.5996 | 232.6551
258.9573 | 476.0185 | 224.1942 | 233.014
259.9573 | 475.9787 | 224.8005 | 233.3949
260.9573 | 475.88 | 225.4088 | 233.815
261.9573 | 475.8162 | 226.0011 | 234.2422
262.9573 | 475.8074 | 226.48 | 234.6932
263.9573 | 475.7467 | 226.5915 | 235.1615
264.9573 | 475.7859 | 226.7603 | 235.6295
265.9573 | 475.7427 | 226.9901 | 236.111
266.9573 | 475.6885 | 227.2533 | 236.5974
267.9573 | 475.6474 | 227.5818 | 237.0958
268.9573 | 475.667 | 227.8482 | 237.6249
269.9573 | 475.5902 | 228.1149 | 238.15
270.9573 | 475.6001 | 228.3769 | 238.7261
271.9573 | 475.5845 | 228.7198 | 239.3622
272.9573 | 475.5902 | 228.9719 | 240.0004
273.9573 | 475.6287 | 229.2882 | 240.6116
274.9573 | 475.6372 | 229.6551 | 241.239
275.9573 | 475.5678 | 229.9694 | 241.8638
276.9573 | 475.4735 | 230.308 | 242.5025
277.9573 | 475.5242 | 230.7087 | 243.1363
278.9573 | 475.6283 | 231.1137 | 243.7814
279.9573 | 475.6863 | 231.4512 | 244.391
280.9573 | 475.7921 | 231.8142 | 244.9498
281.9573 | 475.9166 | 231.9872 | 245.6463
282.9573 | 476.2472 | 232.1403 | 247.0421
283.9573 | 476.7797 | 232.2866 | 248.3076
284.9573 | 477.2644 | 232.4494 | 249.2074
285.9573 | 477.6122 | 232.7073 | 250.0553
286.9573 | 477.8805 | 233.0434 | 250.8428
287.9573 | 478.0306 | 233.4856 | 251.5291
288.9573 | 478.0712 | 234.0266 | 252.2433
289.9573 | 478.0131 | 234.6759 | 253.0623
290.9573 | 477.952 | 235.4975 | 254.0086
291.9573 | 477.8498 | 236.8698 | 254.9408
292.9573 | 477.7511 | 238.57 | 256.0062
293.9573 | 477.706 | 240.2904 | 257.2562
294.9573 | 477.6358 | 242.0507 | 258.398
295.9573 | 477.5356 | 243.6602 | 259.5184
296.9573 | 477.4661 | 245.1991 | 260.4637
297.9573 | 477.4282 | 246.6611 | 261.1456
298.9573 | 477.3192 | 248.5515 | 261.6135
299.9573 | 477.188 | 250.5267 | 261.8849
300.9573 | 477.1335 | 252.2507 | 261.9373
301.9573 | 477.0696 | 254.9206 | 262.0438
302.9573 | 476.9079 | 257.187 | 262.2152
303.9573 | 476.7728 | 259.5683 | 262.2773
304.9573 | 476.6311 | 263.7363 | 262.4082
305.9573 | 476.6768 | 265.8316 | 262.7712
306.9573 | 476.5039 | 269.4525 | 263.246
307.9573 | 476.2397 | 271.0936 | 263.6908
308.9573 | 475.9729 | 272.7462 | 264.1732
309.9573 | 475.7029 | 272.0181 | 264.5609
310.9573 | 475.5291 | 272.4561 | 265.2867
311.9573 | 475.3633 | 272.2681 | 266.207
312.9573 | 475.1431 | 272.2735 | 267.2465
313.9573 | 474.9213 | 272.9334 | 268.3008
314.9573 | 474.7124 | 273.4186 | 269.3589
315.9573 | 474.5502 | 273.6043 | 270.6285
316.9573 | 474.5329 | 273.5393 | 271.5966
317.9573 | 474.5399 | 273.2459 | 272.5727
318.9573 | 474.5593 | 272.888 | 273.6696
319.9573 | 474.527 | 271.853 | 274.7371
320.9573 | 474.3239 | 271.6812 | 276.0853
321.9573 | 474.0361 | 271.8549 | 277.3679
322.9573 | 473.9829 | 271.3515 | 278.7031
323.9573 | 473.8403 | 271.8586 | 280.7214
324.9573 | 473.4228 | 273.3067 | 282.486
325.9573 | 473.0565 | 273.5108 | 283.5754
326.9573 | 472.7037 | 274.5642 | 285.1388
327.9573 | 472.4672 | 275.3742 | 286.73
328.9573 | 472.1431 | 276.1923 | 288.1468
329.9573 | 471.8204 | 276.3968 | 290.1443
330.9573 | 471.5589 | 276.3626 | 291.1775
331.9573 | 471.3899 | 276.32 | 292.2262
332.9573 | 471.1826 | 276.0053 | 293.359
333.9573 | 471.0599 | 276.2504 | 295.2314
334.9573 | 470.9279 | 276.28 | 296.6862
335.9573 | 470.8299 | 276.4214 | 299.3939
336.9573 | 470.7084 | 277.3326 | 300.7752
337.9573 | 470.6957 | 278.2499 | 301.6989
338.9573 | 470.6961 | 279.2395 | 303.045
339.9573 | 470.6325 | 279.7201 | 304.6035
340.9573 | 470.5918 | 279.7884 | 305.866
341.9573 | 470.4868 | 281.212 | 307.4406
342.9573 | 470.5094 | 281.8261 | 309.538
343.9573 | 470.6265 | 282.2962 | 310.9392
344.9573 | 470.6429 | 282.5568 | 312.9194
345.9573 | 470.5699 | 283.3027 | 314.4827
346.9573 | 470.5988 | 283.4832 | 316.3992
347.9573 | 470.6761 | 284.746 | 318.2843
348.9573 | 470.5521 | 285.5361 | 320.5131
349.9573 | 470.4811 | 286.6602 | 323.3937
350.9573 | 470.5189 | 287.2167 | 324.2121
351.9573 | 470.612 | 287.9847 | 326.9275
352.9573 | 470.6448 | 289.168 | 328.9645
353.9573 | 470.6698 | 291.1527 | 331.4304
354.9573 | 470.6324 | 291.3794 | 333.5734
355.9573 | 470.6762 | 292.5491 | 335.6422
356.9573 | 470.7353 | 294.5895 | 338.1747
357.9573 | 470.802 | 296.9896 | 340.5835
358.9573 | 470.8782 | 297.2049 | 343.5988
359.9573 | 470.9436 | 298.8286 | 344.891
360.9573 | 470.9325 | 300.0779 | 346.3435
361.9573 | 470.9096 | 300.8762 | 348.327
362.9573 | 470.8401 | 302.4092 | 350.4338
363.9573 | 470.836 | 304.1525 | 352.1668
364.9573 | 470.9226 | 305.3604 | 354.1127
365.9573 | 471.0033 | 307.1381 | 356.4227
366.9573 | 471.036 | 308.9725 | 358.7489
367.9573 | 471.0864 | 310.4456 | 359.7029
368.9573 | 471.0938 | 312.019 | 361.6664
369.9573 | 471.0624 | 313.4108 | 363.181
370.9573 | 471.0295 | 314.9806 | 365.2851
371.9573 | 470.979 | 316.5449 | 367.0455
372.9573 | 470.9361 | 318.0931 | 369.0154
373.9573 | 470.8895 | 319.4501 | 370.9574
374.9573 | 470.7816 | 321.2459 | 372.8081
375.9573 | 470.6971 | 322.8425 | 374.7819
376.9573 | 470.7253 | 324.2057 | 376.2342
377.9573 | 470.7339 | 326.0786 | 378.3323
378.9573 | 470.7033 | 327.8247 | 380.2795
379.9573 | 470.7227 | 329.3883 | 382.3007
380.9573 | 470.7292 | 331.4209 | 384.1295
381.9573 | 470.7638 | 333.6948 | 385.4045
382.9573 | 470.8381 | 334.5018 | 386.9358
383.9573 | 470.9823 | 336.9971 | 388.1475
384.9573 | 471.1118 | 337.735 | 389.6094
385.9573 | 471.2239 | 339.7165 | 390.9528
386.9573 | 471.3286 | 341.1158 | 391.9249
387.9573 | 471.4047 | 342.0845 | 392.7613
388.9573 | 471.4323 | 343.607 | 394.4852
389.9573 | 471.4578 | 345.4779 | 395.2723
390.9573 | 471.5569 | 346.5645 | 396.9839
391.9573 | 471.6498 | 347.8394 | 398.2813
392.9573 | 471.7131 | 349.4648 | 399.1642
393.9573 | 471.78 | 350.695 | 400.31
394.9573 | 471.8537 | 350.9667 | 401.545
395.9573 | 471.9496 | 353.3142 | 403.1104
396.9573 | 472.1063 | 353.3408 | 403.6977
397.9573 | 472.2294 | 355.4758 | 404.6338
398.9573 | 472.3351 | 356.0442 | 405.5692
399.9573 | 472.4781 | 356.9518 | 406.6242
400.9573 | 472.6427 | 358.6228 | 407.5405
401.9573 | 472.7903 | 359.9241 | 408.4359
402.9573 | 472.8913 | 362.5681 | 409.1904
403.9573 | 472.9861 | 364.6991 | 409.9657
404.9573 | 473.0503 | 365.8634 | 410.7428
405.9573 | 473.1035 | 367.9389 | 410.9005
406.9573 | 473.1774 | 369.6139 | 411.9419
407.9573 | 473.2201 | 371.1749 | 412.6816
408.9573 | 473.2852 | 372.9185 | 413.1452
409.9573 | 473.2953 | 373.3206 | 412.9857
410.9573 | 473.2821 | 373.9272 | 414.2461
411.9573 | 473.3757 | 375.3028 | 414.6429
412.9573 | 473.4746 | 375.4388 | 415.587
413.9573 | 473.498 | 376.4051 | 416.4233
414.9573 | 473.5379 | 377.9976 | 416.8343
415.9573 | 473.5917 | 378.2034 | 418.042
416.9573 | 473.6251 | 379.1292 | 418.9587
417.9573 | 473.6561 | 380.0578 | 419.7035
418.9573 | 473.7252 | 380.9425 | 421.2451
419.9573 | 473.7362 | 381.5009 | 421.6885
420.9573 | 473.7069 | 382.4409 | 421.9408
421.9573 | 473.6549 | 383.5409 | 422.586
422.9573 | 473.6205 | 384.4957 | 423.2062
423.9573 | 473.6188 | 384.3938 | 424.0264
424.9573 | 473.5733 | 385.2195 | 424.4377
425.9573 | 473.5407 | 385.5367 | 425.3774
426.9573 | 473.4184 | 386.1472 | 426.8705
427.9573 | 473.2704 | 386.5581 | 427.7618
428.9573 | 473.1944 | 387.3523 | 428.8791
429.9573 | 473.16 | 387.8193 | 430.0788
430.9573 | 473.0818 | 388.3849 | 431.3487
431.9573 | 472.9449 | 388.832 | 432.6478
432.9573 | 472.9049 | 389.0916 | 434.1984
433.9573 | 472.9437 | 389.0874 | 436.0697
434.9573 | 472.9534 | 389.4017 | 437.402
435.9573 | 472.9049 | 389.5908 | 439.2615
436.9573 | 472.8753 | 390.0581 | 441.2376
437.9573 | 472.8354 | 390.4637 | 443.6726
438.9573 | 472.8619 | 390.6751 | 446.4191
439.9573 | 472.8875 | 390.8713 | 447.8526
440.9573 | 472.794 | 391.4221 | 449.924
441.9573 | 472.7644 | 391.7519 | 451.7872
442.9573 | 472.8373 | 392.0024 | 453.5749
443.9573 | 472.9691 | 392.2904 | 455.215
444.9573 | 473.061 | 392.7481 | 457.2797
445.9573 | 473.1542 | 393.2158 | 459.4757
446.9573 | 473.2247 | 393.4139 | 461.3565
447.9573 | 473.2813 | 393.8219 | 463.1404
448.9573 | 473.3574 | 394.2329 | 465.8542
449.9573 | 473.4041 | 394.6776 | 468.5501
450.9573 | 473.3917 | 394.9533 | 470.8309
451.9573 | 473.4378 | 395.7274 | 472.0053
452.9573 | 473.5119 | 396.2171 | 474.8426
453.9573 | 473.543 | 396.7406 | 477.1991
454.9573 | 473.5616 | 397.3066 | 479.7148
455.9573 | 473.5302 | 397.9472 | 481.7669
456.9573 | 473.4995 | 398.5375 | 484.3432
457.9573 | 473.472 | 399.342 | 486.9983
458.9573 | 473.499 | 399.897 | 489.0007
459.9573 | 473.4555 | 400.5335 | 490.9004
460.9573 | 473.4562 | 401.2902 | 492.9211
461.9573 | 473.5042 | 401.9918 | 494.8935
462.9573 | 473.5868 | 402.7359 | 496.3788
463.9573 | 473.6345 | 403.3583 | 497.6693
464.9573 | 473.5347 | 404.1886 | 498.6161
465.9573 | 473.4761 | 404.8229 | 499.9974
466.9573 | 473.3158 | 405.6418 | 501.4704
467.9573 | 473.2344 | 406.4665 | 502.7324
468.9573 | 473.2368 | 406.9986 | 504.8528
469.9573 | 473.2838 | 407.8646 | 505.9288
470.9573 | 473.3095 | 408.4636 | 507.1259
471.9573 | 473.3377 | 409.2391 | 507.6494
472.9573 | 473.2804 | 410.1638 | 508.2077
473.9573 | 473.2926 | 410.9435 | 508.6068
474.9573 | 473.3211 | 411.4876 | 509.6725
475.9573 | 473.3763 | 412.2197 | 509.4601
476.9573 | 473.4301 | 413.2247 | 509.5789
477.9573 | 473.4523 | 414.0937 | 509.4311
478.9573 | 473.4926 | 414.8394 | 509.6426
479.9573 | 473.45 | 415.7287 | 509.7941
480.9573 | 473.4319 | 416.1221 | 508.6661
481.9573 | 473.4586 | 417.3746 | 507.7037
482.9573 | 473.4133 | 418.0069 | 507.1696
483.9573 | 473.4443 | 419.0446 | 506.8664
484.9573 | 473.4511 | 419.3261 | 506.9843
485.9573 | 473.4808 | 420.503 | 507.0386
486.9573 | 473.4675 | 421.0898 | 506.9025
487.9573 | 473.4831 | 422.1116 | 506.5196
488.9573 | 473.4404 | 422.8713 | 506.8745
489.9573 | 473.3659 | 423.6536 | 506.8218
490.9573 | 473.3792 | 424.3985 | 506.8693
491.9573 | 473.4527 | 425.239 | 506.2998
492.9573 | 473.4748 | 426.1681 | 505.5755
493.9573 | 473.5144 | 426.8844 | 505.9004
494.9573 | 473.5055 | 427.7433 | 504.7238
495.9573 | 473.4163 | 428.2229 | 504.5835
496.9573 | 473.3803 | 428.6694 | 504.0337
497.9573 | 473.3428 | 429.9069 | 503.6127
498.9573 | 473.3668 | 430.3102 | 503.288
499.9573 | 473.36 | 431.4221 | 502.7517
500.9573 | 473.3258 | 432.0493 | 502.1884
501.9573 | 473.3217 | 432.597 | 501.8287
502.9573 | 473.2615 | 433.7666 | 500.818
503.9573 | 473.2833 | 434.5824 | 500.2021
504.9573 | 473.2085 | 435.4491 | 499.7548
505.9573 | 473.1787 | 436.4713 | 498.7707
506.9573 | 473.2118 | 436.8918 | 498.0314
507.9573 | 473.2721 | 438.1926 | 496.7355
508.9573 | 473.345 | 439.0953 | 497.0881
509.9573 | 473.3627 | 439.9459 | 496.7623
510.9573 | 473.4059 | 440.7521 | 495.8909
511.9573 | 473.4544 | 441.656 | 494.949
512.9573 | 473.4796 | 442.5808 | 494.4782
513.9573 | 473.5195 | 443.6407 | 493.7054
514.9573 | 473.5551 | 444.2569 | 492.998
515.9573 | 473.5199 | 445.5262 | 491.9931
516.9573 | 473.475 | 446.1391 | 492.0372
517.9573 | 473.4725 | 447.1876 | 491.3501
518.9573 | 473.5122 | 448.0437 | 491.0054
519.9573 | 473.4817 | 448.826 | 490.91
520.9573 | 473.4477 | 450.0773 | 491.3416
521.9573 | 473.476 | 450.8777 | 490.3483
522.9573 | 473.479 | 451.7342 | 489.9937
523.9573 | 473.4482 | 452.805 | 489.5758
524.9573 | 473.4061 | 454.1296 | 488.9668
525.9573 | 473.3725 | 455.0438 | 488.0645
526.9573 | 473.3439 | 456.3466 | 486.8003
527.9573 | 473.3046 | 456.9584 | 486.0869
528.9573 | 473.2983 | 457.6421 | 485.6024
529.9573 | 473.2417 | 458.319 | 485.3961
530.9573 | 473.2427 | 459.1787 | 484.7719
531.9573 | 473.2628 | 459.332 | 484.0133
532.9573 | 473.2259 | 460.1544 | 483.4572
533.9573 | 473.163 | 461.0167 | 482.9031
534.9573 | 473.1765 | 461.6399 | 483.2935
535.9573 | 473.2242 | 462.3642 | 482.4217
536.9573 | 473.3066 | 463.166 | 482.2772
537.9573 | 473.3947 | 463.6515 | 480.0511
538.9573 | 473.475 | 464.0185 | 481.4306
539.9573 | 473.4872 | 464.816 | 482.074
540.9573 | 473.461 | 465.5127 | 482.7462
541.9573 | 473.4776 | 466.1107 | 484.6467
542.9573 | 473.5104 | 466.9857 | 483.7772
543.9573 | 473.53 | 467.878 | 484.0597
544.9573 | 473.4982 | 468.427 | 484.1477
545.9573 | 473.4655 | 468.5709 | 484.1524
546.9573 | 473.4455 | 469.4198 | 483.314
547.9573 | 473.4238 | 469.4157 | 480.1055
548.9573 | 473.4809 | 469.6889 | 480.5388
549.9573 | 473.5794 | 470.8575 | 482.0561
550.9573 | 473.6342 | 471.4457 | 481.7282
551.9573 | 473.6113 | 472.0081 | 480.2922
552.9573 | 473.6238 | 472.8764 | 479.7439
553.9573 | 473.6485 | 473.2148 | 480.3617
554.9573 | 473.6865 | 473.9664 | 479.4751
555.9573 | 473.7384 | 474.3651 | 479.2981
556.9573 | 473.7582 | 474.0966 | 480.8432
557.9573 | 473.7517 | 474.8353 | 476.5592
558.9573 | 473.6867 | 475.1118 | 477.1336
559.9573 | 473.6911 | 475.2889 | 474.2461
560.9573 | 473.7862 | 475.6218 | 472.0813
561.9573 | 473.8648 | 475.3755 | 466.5746
562.9573 | 473.8849 | 475.8696 | 465.5664
563.9573 | 473.8677 | 476.3531 | 462.5901
564.9573 | 473.7726 | 476.3753 | 467.0227
565.9573 | 473.7425 | 475.5605 | 463.4276
566.9573 | 473.7248 | 475.1222 | 459.6366
567.9573 | 473.7727 | 475.8075 | 459.7111
568.9573 | 473.8182 | 475.972 | 461.3135
569.9573 | 473.8459 | 475.65 | 460.7259
570.9573 | 473.9018 | 475.1747 | 460.0104
571.9573 | 473.9628 | 475.7665 | 451.9843
572.9573 | 473.9651 | 476.528 | 453.1004
573.9573 | 473.9435 | 476.7322 | 464.8498
574.9573 | 473.8779 | 475.9481 | 463.2623
575.9573 | 473.8098 | 476.12 | 460.3321
576.9573 | 473.7901 | 476.3215 | 461.6757
577.9573 | 473.7656 | 476.3604 | 461.4849
578.9573 | 473.7407 | 476.0244 | 456.7107
579.9573 | 473.6245 | 476.0979 | 455.5016
580.9573 | 473.5826 | 476.1761 | 458.2985
581.9573 | 473.5856 | 477.2948 | 471.4527
582.9573 | 473.5926 | 477.3328 | 463.6881
583.9573 | 473.6541 | 477.4338 | 463.3189
584.9573 | 473.6315 | 477.1557 | 460.4201
585.9573 | 473.644 | 478.0567 | 466.9571
586.9573 | 473.697 | 478.1032 | 465.4912
587.9573 | 473.7002 | 479.9204 | 486.5689
588.9573 | 473.6556 | 478.8422 | 470.9441
589.9573 | 473.6256 | 479.6471 | 473.9614
590.9573 | 473.6537 | 479.1355 | 460.6457
591.9573 | 473.7114 | 479.79 | 463.523
592.9573 | 473.7352 | 480.2528 | 467.9199
593.9573 | 473.7935 | 483.795 | 501.9739
594.9573 | 473.8553 | 483.5963 | 495.041
595.9573 | 473.9595 | 483.4334 | 498.513
596.9573 | 473.9418 | 484.8488 | 497.459
597.9573 | 473.9497 | 485.8576 | 502.9172
598.9573 | 473.9188 | 485.2113 | 497.9107
599.9573 | 473.9065 | 486.4831 | 496.7618
600.9573 | 473.9354 | 486.6359 | 496.7532
601.9573 | 473.9178 | 486.6791 | 501.716
602.9573 | 473.8887 | 486.5635 | 495.3993
603.9573 | 473.8592 | 485.8788 | 493.7744
604.9573 | 473.8119 | 485.4744 | 492.2348
605.9573 | 473.8803 | 485.732 | 490.7227
606.9573 | 473.8498 | 485.0767 | 487.9088
607.9573 | 473.8494 | 484.7986 | 493.1255
608.9573 | 473.8287 | 485.7783 | 495.5496
609.9573 | 473.7946 | 486.9945 | 506.8777
610.9573 | 473.7335 | 487.049 | 506.3782
611.9573 | 473.6702 | 488.1791 | 508.2823
612.9573 | 473.6125 | 487.3627 | 506.4327
613.9573 | 473.5612 | 487.0101 | 508.972
614.9573 | 473.5247 | 485.5856 | 508.1881
615.9573 | 473.5185 | 486.9145 | 507.3543
616.9573 | 473.7138 | 487.8992 | 505.0539
617.9573 | 473.896 | 487.4528 | 504.3541
618.9573 | 473.8487 | 488.7346 | 513.7072
619.9573 | 473.7831 | 489.1832 | 515.0493
620.9573 | 473.7732 | 491.015 | 518.1201
621.9573 | 473.8618 | 491.0855 | 517.6087
622.9573 | 473.8605 | 493.3741 | 522.2969
623.9573 | 473.8207 | 494.8347 | 526.8661
624.9573 | 473.7847 | 496.4192 | 528.1725
625.9573 | 473.84 | 494.4725 | 522.5879
626.9573 | 473.8929 | 495.575 | 526.107
627.9573 | 473.9509 | 497.4531 | 525.1745
628.9573 | 473.9433 | 497.4611 | 523.6963
629.9573 | 473.9903 | 496.6811 | 519.7441
630.9573 | 474.04 | 497.7123 | 521.5931
631.9573 | 474.0201 | 496.5179 | 524.5425
632.9573 | 474.1401 | 497.6094 | 529.4298
633.9573 | 474.2536 | 495.8497 | 524.5905
634.9573 | 474.3972 | 496.0473 | 526.6374
635.9573 | 474.4039 | 497.683 | 531.8477
636.9573 | 474.261 | 498.6852 | 564.0865
637.9573 | 474.2144 | 502.6424 | 558.3308
638.9573 | 474.188 | 503.678 | 566.9349
639.9573 | 474.0776 | 507.0358 | 600.8732
640.9573 | 473.9462 | 508.6971 | 615.8692
641.9573 | 473.8412 | 509.8465 | 626.5714
642.9573 | 473.7287 | 510.7302 | 629.6035
643.9573 | 473.6637 | 540.5813 | 831.4334
644.9573 | 473.5304 | 524.554 | 728.8162
645.9573 | 473.4692 | 507.1474 | 521.5
646.9573 | 473.2617 | 507.6401 | 521.9977
647.9573 | 473.1137 | 508.4693 | 522.6172
648.9573 | 472.9533 | 509.6505 | 523.368
649.9573 | 472.6668 | 510.4582 | 524.3896
650.9573 | 472.5698 | 510.7603 | 524.8125
651.9573 | 472.4284 | 511.7682 | 525.609
652.9573 | 472.1392 | 512.095 | 526.2416
653.9573 | 471.9584 | 513.0285 | 527.2526
654.9573 | 471.8014 | 514.0404 | 528.4459
655.9573 | 471.7061 | 515.1085 | 529.2304
656.9573 | 471.5464 | 516.0563 | 529.5259
657.9573 | 471.3552 | 516.672 | 530.2998
658.9573 | 471.2283 | 517.6636 | 530.8678
659.9573 | 471.135 | 519.1699 | 531.6271
660.9573 | 471.0572 | 520.0433 | 531.7938
661.9573 | 471.0292 | 520.7183 | 532.2695
662.9573 | 470.8787 | 521.7889 | 532.6475
663.9573 | 470.7828 | 522.9169 | 532.9252
664.9573 | 470.7143 | 524.0074 | 533.7658
665.9573 | 470.6087 | 525.2766 | 534.0398
666.9573 | 470.4186 | 526.31 | 534.3863
667.9573 | 470.3431 | 527.2181 | 534.7815
668.9573 | 470.2441 | 528.4206 | 535.2076
669.9573 | 470.18 | 529.9705 | 536.191
670.9573 | 470.0937 | 530.4268 | 536.4211
671.9573 | 469.989 | 531.927 | 536.6325
672.9573 | 469.8989 | 533.3529 | 537.2068
673.9573 | 469.7421 | 533.5926 | 537.5441
674.9573 | 469.548 | 535.1776 | 538.5294
675.9573 | 469.5058 | 535.7169 | 538.6134
676.9573 | 469.5167 | 536.7758 | 538.7355
677.9573 | 469.4236 | 537.9113 | 538.9554
678.9573 | 469.3333 | 538.8823 | 539.2704
679.9573 | 469.2675 | 539.8698 | 540.2592
680.9573 | 469.2893 | 540.475 | 540.5133
681.9573 | 469.3014 | 541.4732 | 541.2341
682.9573 | 469.3644 | 541.9165 | 541.5503
683.9573 | 469.3346 | 542.8752 | 542.2638
684.9573 | 469.2952 | 543.4014 | 543.0544
685.9573 | 469.3276 | 544.5919 | 542.9011
686.9573 | 469.358 | 545.1216 | 542.9609
687.9573 | 469.4052 | 546.0402 | 543.1982