## Test Conditions
DESIREE-FIRE Test Number 1 - Circuit Simulator Data Only
Test Date: | 2009-07-15
DCSim DAQ Start Time | 15:04
DCSim Time for Synchronization | 15:07
Heat Source Synchronization | 0:16 | hour:minutes:seconds
Heat Source DAQ Start Time | 14:51
Fire Time | 15:09
Offset | 0:05 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 285 | seconds
Heat Source Offset | 0:18 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1060 | seconds
Heat Source Stop Time | 15:26
Test Duration | 0:17 | hour:minutes:seconds
| 1018 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SOV 2 | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.71875 | 123.3902 | -66.7923 | 56.2912 | 0.041851 | 0.0053207 | 0.0010261 | 0.05766 | 0.0012778 | 0.058602 | 0.043632 | 0.0013613 | -0.00021967 | 0.066664 | -0.0033627 | 0.066266 | -64.5771 | 0.019721 | -66.7597 | 56.261 | 56.0235 | 56.1429 | -66.8696 | -66.7932 | 0.023253 | -66.9009 | 56.2077 | 56.2847 | 55.9583 | -66.9874 | -0.077269 | -0.030204 | 2.2152 | 0.032557 | 0.10983 | -0.2677 | -0.14835 | -0.19511 | -0.083497 | -0.000875 | -0.10864 | 0.086471 | -0.006468 | -0.33293 | 123.0533 | 122.8158 | 122.9352 | 66.812 | -123.1608 | 123 | 123.077 | 122.7506 | 66.8156 | -123.2786
0.28125 | 123.3994 | -66.7923 | 56.2958 | 0.041851 | 0.0053207 | 0.0010261 | 0.05766 | 0.0012778 | 0.058602 | 0.043632 | 0.0013613 | 0.0029843 | 0.066664 | -0.0022937 | 0.068403 | -64.5771 | 0.0243 | -66.7689 | 56.261 | 56.0235 | 56.1474 | -66.8787 | -66.8023 | 0.023253 | -66.8918 | 56.1985 | 56.2893 | 55.9491 | -66.9782 | -0.086427 | -0.034781 | 2.2152 | 0.023401 | 0.10983 | -0.27227 | -0.14834 | -0.18595 | -0.097231 | -0.010032 | -0.099482 | 0.08647 | -0.006466 | -0.34666 | 123.0533 | 122.8158 | 122.9397 | 66.8166 | -123.1745 | 122.9908 | 123.0816 | 122.7414 | 66.8156 | -123.274
1.2812 | 123.3765 | -66.8152 | 56.3004 | 0.057113 | 0.0063897 | -4.1882e-05 | 0.05766 | 0.0012778 | 0.057534 | 0.043632 | 0.0013613 | 0.0019163 | 0.066664 | -0.0044307 | 0.067334 | -64.6 | 0.0243 | -66.7689 | 56.2702 | 56.0281 | 56.1474 | -66.8421 | -66.7886 | 0.018674 | -66.9009 | 56.194 | 56.2893 | 55.9629 | -66.9874 | -0.026907 | -0.030202 | 2.2152 | 0.04629 | 0.073197 | -0.27227 | -0.15292 | -0.17222 | -0.10639 | 0.026593 | -0.08575 | 0.086471 | -0.011044 | -0.3375 | 123.0853 | 122.8433 | 122.9626 | 66.8395 | -123.1424 | 123.0092 | 123.1045 | 122.778 | 66.8339 | -123.2878
2.2812 | 123.3902 | -66.8106 | 56.2958 | 0.057113 | 0.0053207 | -4.1882e-05 | 0.058728 | 0.0023458 | 0.05967 | 0.074154 | 0.0013613 | 0.0019163 | 0.067733 | -0.0054987 | 0.067334 | -64.5908 | 0.028878 | -66.7689 | 56.261 | 56.0235 | 56.152 | -66.897 | -66.7932 | 0.023253 | -66.9009 | 56.1985 | 56.2847 | 55.9491 | -66.9874 | -0.086432 | -0.034781 | 2.2198 | 0.041712 | 0.12814 | -0.27227 | -0.14376 | -0.1768 | -0.097231 | 0.017436 | -0.090328 | 0.086471 | -0.011045 | -0.34666 | 123.0716 | 122.8341 | 122.9626 | 66.8395 | -123.1928 | 123.0092 | 123.0953 | 122.7597 | 66.8339 | -123.2832
3.2812 | 123.3673 | -66.7877 | 56.3736 | 0.057113 | 0.0053207 | 0.0010261 | 0.056591 | 0.0023458 | 0.056465 | 0.074154 | 0.0013613 | 0.00084833 | 0.065596 | -0.0044307 | 0.065198 | -64.5634 | 0.028878 | -66.7597 | 56.2702 | 56.0281 | 56.1474 | -66.8833 | -66.784 | 0.023253 | -66.8918 | 56.194 | 56.2939 | 55.9674 | -66.9782 | -0.095583 | -0.10344 | 2.2243 | 0.02798 | 0.12356 | -0.34552 | -0.22616 | -0.19053 | -0.17963 | 0.003706 | -0.10406 | 0.08647 | -0.079707 | -0.40617 | 123.0579 | 122.8158 | 122.9352 | 66.8166 | -123.2569 | 122.9817 | 123.0816 | 122.7552 | 66.811 | -123.3518
4.2812 | 123.3902 | -66.7877 | 56.2775 | 0.057113 | 0.0063897 | -4.1882e-05 | 0.05766 | 0.0023458 | 0.058602 | 0.043632 | 0.0024293 | 0.00084833 | 0.066664 | -0.0065677 | 0.065198 | -64.5954 | 0.028878 | -66.7643 | 56.2656 | 56.0189 | 56.1474 | -66.8833 | -66.7932 | 0.023253 | -66.8964 | 56.2031 | 56.2847 | 55.9629 | -66.9828 | -0.095583 | -0.011892 | 2.1923 | 0.023402 | 0.11898 | -0.25854 | -0.13003 | -0.19511 | -0.074342 | -0.005452 | -0.10864 | 0.08647 | 0.007265 | -0.31461 | 123.0533 | 122.8066 | 122.9352 | 66.8166 | -123.1608 | 122.9908 | 123.0725 | 122.7506 | 66.811 | -123.2603
5.2812 | 123.3902 | -66.7969 | 56.2683 | 0.057113 | 0.0053207 | 0.0020951 | 0.056591 | 0.0012778 | 0.058602 | 0.043632 | 0.0024293 | 0.0019163 | 0.065596 | -0.0044307 | 0.065198 | -64.5908 | 0.033457 | -66.7643 | 56.2656 | 56.0281 | 56.152 | -66.8925 | -66.7932 | 0.023253 | -66.8964 | 56.194 | 56.2939 | 55.9583 | -66.992 | -0.095586 | -0.002737 | 2.206 | 0.032557 | 0.12814 | -0.24023 | -0.1163 | -0.19511 | -0.074344 | 0.003703 | -0.099483 | 0.095628 | 0.025578 | -0.31004 | 123.0624 | 122.825 | 122.9489 | 66.8303 | -123.1608 | 122.9908 | 123.0908 | 122.7551 | 66.8201 | -123.2603
6.2812 | 123.3627 | -66.806 | 56.2958 | 0.041851 | 0.0063897 | 0.0020951 | 0.058728 | 0.0012778 | 0.057534 | 0.058893 | 0.0024293 | 0.00084833 | 0.067733 | -0.0044307 | 0.068403 | -64.5725 | 0.0243 | -66.7643 | 56.261 | 56.0235 | 56.152 | -66.8879 | -66.784 | 0.023253 | -66.9009 | 56.2077 | 56.2939 | 55.9629 | -66.992 | -0.081852 | -0.034781 | 2.2335 | 0.041712 | 0.12356 | -0.27227 | -0.14376 | -0.18596 | -0.088074 | 0.022016 | -0.094906 | 0.09105 | -0.001887 | -0.33292 | 123.067 | 122.8295 | 122.958 | 66.8303 | -123.1837 | 123.0137 | 123.0999 | 122.7689 | 66.8293 | -123.2878
7.2812 | 123.381 | -66.8106 | 56.3187 | 0.041851 | 0.0053207 | 0.0010261 | 0.058728 | 0.00020984 | 0.058602 | 0.058893 | 0.00029332 | -0.00021967 | 0.068801 | -0.0044307 | 0.067334 | -64.5725 | 0.028878 | -66.7597 | 56.261 | 56.0327 | 56.152 | -66.8604 | -66.784 | 0.023253 | -66.8964 | 56.1985 | 56.2893 | 55.9812 | -66.9828 | -0.0498 | -0.05767 | 2.2381 | 0.050868 | 0.10067 | -0.28601 | -0.16665 | -0.17222 | -0.12012 | 0.026594 | -0.08575 | 0.08647 | -0.029355 | -0.3375 | 123.0716 | 122.8433 | 122.9626 | 66.8395 | -123.1791 | 123.0092 | 123.0999 | 122.7918 | 66.8339 | -123.3015
8.2812 | 123.3994 | -66.8015 | 56.2775 | 0.057113 | 0.0031837 | 0.0010261 | 0.055523 | 0.0012778 | 0.057534 | 0.074154 | 0.0013613 | 0.00084833 | 0.066664 | -0.0044307 | 0.068403 | -64.5954 | 0.028878 | -66.7643 | 56.2702 | 56.0235 | 56.152 | -66.8604 | -66.7977 | 0.014095 | -66.8918 | 56.1894 | 56.2893 | 55.9583 | -66.9874 | -0.058955 | -0.007314 | 2.206 | 0.037135 | 0.09609 | -0.25396 | -0.12545 | -0.18595 | -0.088078 | 0.003703 | -0.090326 | 0.095628 | 0.011844 | -0.31919 | 123.0716 | 122.825 | 122.9535 | 66.8303 | -123.1379 | 122.9908 | 123.0908 | 122.7597 | 66.8155 | -123.2649
9.2812 | 123.3627 | -66.7877 | 56.2775 | 0.057113 | 0.0042527 | 0.0010261 | 0.05766 | 0.00020984 | 0.057534 | 0.074154 | 0.0024293 | 0.00084833 | 0.065596 | -0.0044307 | 0.065198 | -64.5771 | 0.038035 | -66.7597 | 56.2656 | 56.0281 | 56.1566 | -66.8329 | -66.784 | 0.023253 | -66.8964 | 56.194 | 56.2939 | 55.9537 | -66.9828 | -0.045215 | -0.011892 | 2.2106 | 0.02798 | 0.073195 | -0.24939 | -0.12088 | -0.19511 | -0.083499 | 0.003706 | -0.10864 | 0.08647 | 0.016423 | -0.32377 | 123.0533 | 122.8158 | 122.9443 | 66.8258 | -123.1104 | 122.9817 | 123.0816 | 122.7414 | 66.811 | -123.2603
10.2812 | 123.3673 | -66.8335 | 56.3095 | 0.041851 | 0.0053207 | 0.0020951 | 0.05766 | 0.0012778 | 0.056465 | 0.028371 | 0.00029332 | 0.0019163 | 0.065596 | -0.0033627 | 0.067334 | -64.5817 | 0.028878 | -66.7643 | 56.2656 | 56.0281 | 56.152 | -66.8467 | -66.7977 | 0.03241 | -66.8964 | 56.2031 | 56.2893 | 55.972 | -66.9828 | -0.013176 | -0.043935 | 2.2518 | 0.069178 | 0.082354 | -0.28143 | -0.1575 | -0.14933 | -0.10638 | 0.035746 | -0.062862 | 0.08647 | -0.020199 | -0.3375 | 123.0991 | 122.8616 | 122.9855 | 66.8624 | -123.1562 | 123.0366 | 123.1228 | 122.8055 | 66.8659 | -123.2923
11.2812 | 123.4177 | -66.8152 | 56.3049 | 0.026589 | 0.0053207 | 0.0020951 | 0.056591 | 0.00020984 | 0.057534 | 0.043632 | 0.0013613 | 0.00084833 | 0.066664 | -0.0033627 | 0.067334 | -64.5863 | 0.028878 | -66.7689 | 56.261 | 56.0327 | 56.152 | -66.865 | -66.7932 | 0.027831 | -66.8918 | 56.194 | 56.2893 | 55.9583 | -66.9828 | -0.049801 | -0.043937 | 2.2289 | 0.04629 | 0.096091 | -0.27227 | -0.15292 | -0.16764 | -0.11097 | 0.022014 | -0.076593 | 0.091049 | -0.015622 | -0.34666 | 123.0762 | 122.8478 | 122.9672 | 66.8441 | -123.1699 | 123.0092 | 123.1045 | 122.7735 | 66.843 | -123.2878
12.3125 | 123.2758 | -66.861 | 56.3324 | 0.041851 | 0.0042527 | 0.0020951 | 0.056591 | 0.0012778 | 0.058602 | 0.074154 | 0.00029332 | -0.00021967 | 0.065596 | -0.0022937 | 0.067334 | -64.5313 | 0.028878 | -66.7735 | 56.2656 | 56.0281 | 56.152 | -66.8238 | -66.7932 | 0.027831 | -66.8918 | 56.1985 | 56.2939 | 55.9674 | -66.9828 | 0.037185 | -0.066823 | 2.3296 | 0.087488 | 0.050303 | -0.30432 | -0.18039 | -0.12187 | -0.13385 | 0.06779 | -0.030817 | 0.091049 | -0.038508 | -0.36497 | 123.1265 | 122.889 | 123.013 | 66.8898 | -123.1562 | 123.0595 | 123.1549 | 122.8284 | 66.8888 | -123.3152
13.2812 | 123.3673 | -66.8106 | 56.3461 | 0.041851 | 0.0042527 | -0.0011099 | 0.05766 | 0.0023458 | 0.056465 | 0.058893 | 0.0013613 | 0.0019163 | 0.066664 | -0.0044307 | 0.065198 | -64.5634 | 0.028878 | -66.7597 | 56.2702 | 56.0235 | 56.152 | -66.8787 | -66.7886 | 0.027831 | -66.8964 | 56.1985 | 56.2893 | 55.9583 | -66.992 | -0.068116 | -0.075978 | 2.2472 | 0.050868 | 0.11898 | -0.32263 | -0.19412 | -0.18138 | -0.14758 | 0.022015 | -0.08575 | 0.095628 | -0.05682 | -0.38786 | 123.0808 | 122.8341 | 122.9626 | 66.8395 | -123.2249 | 123.0092 | 123.0999 | 122.7689 | 66.8384 | -123.3381
14.2812 | 123.3719 | -66.806 | 56.3004 | 0.057113 | 0.0031837 | 0.0020951 | 0.059797 | -0.00085916 | 0.057534 | 0.058893 | 0.0024293 | 0.0019163 | 0.066664 | -0.0012257 | 0.066266 | -64.5817 | 0.028878 | -66.7643 | 56.2702 | 56.0281 | 56.1566 | -66.8741 | -66.7886 | 0.023253 | -66.8964 | 56.1985 | 56.2939 | 55.9537 | -66.992 | -0.068115 | -0.030202 | 2.2243 | 0.041712 | 0.10983 | -0.27227 | -0.14377 | -0.18596 | -0.10181 | 0.017437 | -0.090328 | 0.095628 | -0.006465 | -0.34666 | 123.0762 | 122.8341 | 122.9626 | 66.8349 | -123.1745 | 123.0046 | 123.0999 | 122.7597 | 66.8293 | -123.2923
15.2812 | 123.3673 | -66.8152 | 56.2912 | 0.041851 | 0.0031837 | -4.1882e-05 | 0.056591 | 0.0023458 | 0.057534 | 0.058893 | 0.00029332 | 0.00084833 | 0.067733 | -0.0022937 | 0.065198 | -64.5725 | 0.033457 | -66.7689 | 56.2656 | 56.0235 | 56.152 | -66.8787 | -66.7977 | 0.027831 | -66.8964 | 56.194 | 56.2893 | 55.9857 | -66.9828 | -0.063538 | -0.025625 | 2.2427 | 0.04629 | 0.10983 | -0.2677 | -0.13919 | -0.16764 | -0.097232 | 0.017436 | -0.081172 | 0.08647 | -0.001889 | -0.30545 | 123.0808 | 122.8387 | 122.9672 | 66.8486 | -123.1699 | 123.0092 | 123.1045 | 122.8009 | 66.843 | -123.274
16.2812 | 123.4131 | -66.7923 | 56.3095 | 0.057113 | 0.0031837 | 0.0010261 | 0.05766 | 0.0023458 | 0.058602 | 0.074154 | 0.0013613 | 0.0019163 | 0.065596 | -0.0022937 | 0.065198 | -64.5771 | 0.028878 | -66.7689 | 56.2702 | 56.0235 | 56.152 | -66.8467 | -66.7932 | 0.018674 | -66.9009 | 56.1985 | 56.2939 | 55.9583 | -66.9874 | -0.054375 | -0.039357 | 2.2152 | 0.023401 | 0.077776 | -0.28601 | -0.1575 | -0.19511 | -0.11096 | -0.000875 | -0.10864 | 0.086471 | -0.01562 | -0.35124 | 123.0624 | 122.8158 | 122.9443 | 66.8212 | -123.1562 | 122.9908 | 123.0862 | 122.7506 | 66.811 | -123.2969
17.2812 | 123.4085 | -66.806 | 56.2729 | 0.072375 | 0.0053207 | -4.1882e-05 | 0.056591 | 0.0012778 | 0.056465 | 0.058893 | 0.00029332 | 0.00084833 | 0.065596 | -0.0033627 | 0.066266 | -64.5725 | 0.033457 | -66.7643 | 56.2702 | 56.0327 | 56.1566 | -66.8696 | -66.8023 | 0.018674 | -66.8872 | 56.194 | 56.2939 | 55.9629 | -66.9828 | -0.063536 | -0.002736 | 2.2335 | 0.041712 | 0.10525 | -0.24023 | -0.1163 | -0.1768 | -0.078921 | 0.003701 | -0.08117 | 0.095628 | 0.021001 | -0.31004 | 123.0762 | 122.8387 | 122.9626 | 66.8395 | -123.1425 | 123 | 123.0999 | 122.7689 | 66.8247 | -123.2557
18.2812 | 123.4085 | -66.7694 | 56.3004 | 0.072375 | 0.0031837 | -4.1882e-05 | 0.056591 | 0.0012778 | 0.058602 | 0.074154 | 0.00029332 | -0.00021967 | 0.067733 | -0.0022937 | 0.066266 | -64.5908 | 0.033457 | -66.7643 | 56.261 | 56.0281 | 56.152 | -66.865 | -66.7886 | 0.018674 | -66.8964 | 56.2077 | 56.2939 | 55.9583 | -66.9828 | -0.095578 | -0.039359 | 2.1786 | 0.005091 | 0.10067 | -0.27227 | -0.14834 | -0.21342 | -0.092652 | -0.019184 | -0.12695 | 0.08647 | -0.006465 | -0.34208 | 123.0304 | 122.7975 | 122.9214 | 66.8029 | -123.1653 | 122.9771 | 123.0633 | 122.7277 | 66.7881 | -123.2832
19.2812 | 123.3627 | -66.8243 | 56.3095 | 0.057113 | 0.0042527 | 0.0010261 | 0.05766 | 0.0023458 | 0.057534 | 0.058893 | -0.00077468 | -0.00021967 | 0.066664 | -0.0022937 | 0.066266 | -64.5771 | 0.0243 | -66.7643 | 56.2656 | 56.0327 | 56.152 | -66.8787 | -66.7932 | 0.027831 | -66.8964 | 56.194 | 56.2893 | 55.9537 | -66.9874 | -0.054383 | -0.043935 | 2.2472 | 0.060023 | 0.11441 | -0.27685 | -0.1575 | -0.16307 | -0.11554 | 0.031169 | -0.072017 | 0.091049 | -0.020199 | -0.35581 | 123.0899 | 122.857 | 122.9764 | 66.8486 | -123.1882 | 123.0183 | 123.1137 | 122.778 | 66.8522 | -123.2969
20.2812 | 123.2849 | -66.8335 | 56.3324 | 0.057113 | 0.0042527 | 0.0010261 | 0.056591 | 0.0023458 | 0.056465 | 0.089415 | 0.0013613 | -0.00021967 | 0.067733 | -0.0012257 | 0.067334 | -64.5496 | 0.033457 | -66.7735 | 56.2656 | 56.0281 | 56.1566 | -66.8467 | -66.7886 | 0.023253 | -66.9009 | 56.194 | 56.2893 | 55.9629 | -66.992 | -0.013176 | -0.066823 | 2.2839 | 0.060022 | 0.073198 | -0.30432 | -0.17581 | -0.15849 | -0.13843 | 0.044903 | -0.06744 | 0.09105 | -0.043087 | -0.36955 | 123.0991 | 122.8616 | 122.9901 | 66.867 | -123.1791 | 123.0275 | 123.1228 | 122.7963 | 66.8567 | -123.3244
21.2812 | 123.3856 | -66.8152 | 56.3141 | 0.041851 | 0.0031837 | -4.1882e-05 | 0.05766 | 0.0012778 | 0.05967 | 0.058893 | 0.0013613 | -0.00021967 | 0.067733 | -0.0022937 | 0.067334 | -64.5634 | 0.028878 | -66.7735 | 56.2702 | 56.0235 | 56.1566 | -66.8009 | -66.7977 | 0.023253 | -66.8872 | 56.194 | 56.2847 | 55.9583 | -66.9874 | 0.014304 | -0.043935 | 2.2518 | 0.041712 | 0.027408 | -0.29059 | -0.1575 | -0.17222 | -0.12012 | 0.017436 | -0.072014 | 0.10021 | -0.029356 | -0.35581 | 123.0853 | 122.8387 | 122.9718 | 66.8441 | -123.115 | 123.0092 | 123.0999 | 122.7735 | 66.8384 | -123.3015
22.2812 | 123.3719 | -66.8198 | 56.3141 | 0.057113 | 0.0031837 | -4.1882e-05 | 0.056591 | 0.0023458 | 0.057534 | 0.074154 | 0.0013613 | 0.00084833 | 0.066664 | -0.0012257 | 0.066266 | -64.5771 | 0.033457 | -66.7781 | 56.2656 | 56.0327 | 56.152 | -66.81 | -66.7977 | 0.023253 | -66.8964 | 56.1985 | 56.2893 | 55.9537 | -66.9782 | 0.009723 | -0.048513 | 2.2426 | 0.04171 | 0.031987 | -0.28143 | -0.16208 | -0.15849 | -0.11554 | 0.022013 | -0.076595 | 0.081891 | -0.024777 | -0.36039 | 123.0853 | 122.8524 | 122.9718 | 66.8532 | -123.1241 | 123.0183 | 123.1091 | 122.7735 | 66.843 | -123.2923
23.2812 | 123.2895 | -66.8243 | 56.3141 | 0.041851 | 0.0031837 | -4.1882e-05 | 0.056591 | -0.00085916 | 0.056465 | 0.043632 | 0.00029332 | -0.00021967 | 0.065596 | -0.0022937 | 0.065198 | -64.5588 | 0.028878 | -66.7735 | 56.261 | 56.0327 | 56.1612 | -66.8833 | -66.7932 | 0.027831 | -66.9009 | 56.1985 | 56.2893 | 55.9949 | -66.9874 | -0.058962 | -0.053092 | 2.2655 | 0.050867 | 0.10983 | -0.28143 | -0.15292 | -0.16307 | -0.11554 | 0.031169 | -0.076595 | 0.086471 | -0.024777 | -0.31918 | 123.0853 | 122.857 | 122.9855 | 66.8532 | -123.1974 | 123.0229 | 123.1137 | 122.8192 | 66.8522 | -123.3015
24.2812 | 123.4039 | -66.7969 | 56.2958 | 0.057113 | 0.0042527 | 0.0020951 | 0.056591 | 0.0012778 | 0.056465 | 0.058893 | 0.00029332 | -0.00021967 | 0.066664 | -0.0022937 | 0.067334 | -64.5863 | 0.028878 | -66.7689 | 56.261 | 56.0281 | 56.152 | -66.8055 | -66.7886 | 0.018674 | -66.8918 | 56.1985 | 56.2985 | 55.9537 | -66.9874 | -0.008586 | -0.034781 | 2.2106 | 0.027979 | 0.036565 | -0.2677 | -0.14376 | -0.19053 | -0.097231 | 0.008282 | -0.094904 | 0.095628 | 0.002691 | -0.34208 | 123.0579 | 122.825 | 122.9489 | 66.8258 | -123.1012 | 122.9954 | 123.0953 | 122.7506 | 66.8155 | -123.2832
25.2812 | 123.3719 | -66.8106 | 56.3232 | 0.057113 | 0.0031837 | -4.1882e-05 | 0.056591 | 0.0012778 | 0.058602 | 0.043632 | -0.00077468 | 0.00084833 | 0.065596 | -0.0012257 | 0.066266 | -64.5634 | 0.042614 | -66.7781 | 56.2747 | 56.0372 | 56.1566 | -66.8329 | -66.7977 | 0.023253 | -66.8918 | 56.1985 | 56.2847 | 55.9629 | -66.9874 | -0.022327 | -0.048511 | 2.2472 | 0.032555 | 0.054882 | -0.286 | -0.16665 | -0.1768 | -0.1247 | 0.012858 | -0.081171 | 0.095628 | -0.038511 | -0.36039 | 123.0853 | 122.8478 | 122.9672 | 66.8532 | -123.1562 | 123.0092 | 123.0953 | 122.7735 | 66.8339 | -123.3106
26.2812 | 123.381 | -66.8015 | 56.3095 | 0.057113 | 0.0021157 | 0.0020951 | 0.05766 | 0.0023458 | 0.056465 | 0.058893 | -0.00077468 | 0.00084833 | 0.065596 | -0.0022937 | 0.066266 | -64.5908 | 0.028878 | -66.7735 | 56.2656 | 56.0235 | 56.1474 | -66.8879 | -66.7886 | 0.018674 | -66.8964 | 56.2031 | 56.2939 | 55.9537 | -66.9828 | -0.086429 | -0.043935 | 2.2106 | 0.027979 | 0.11441 | -0.28601 | -0.16208 | -0.18138 | -0.10638 | 0.01286 | -0.094905 | 0.08647 | -0.01562 | -0.35581 | 123.067 | 122.825 | 122.9489 | 66.8303 | -123.1974 | 123.0046 | 123.0953 | 122.7551 | 66.8201 | -123.2923
27.2812 | 123.2574 | -66.8655 | 56.3599 | 0.057113 | 0.0010477 | 0.0010261 | 0.056591 | -0.00085916 | 0.056465 | 0.074154 | 0.00029332 | -0.00021967 | 0.064528 | -0.0012257 | 0.066266 | -64.5496 | 0.028878 | -66.7781 | 56.2656 | 56.0327 | 56.152 | -66.8696 | -66.7886 | 0.027831 | -66.8964 | 56.2077 | 56.2802 | 55.9949 | -66.9874 | -0.004026 | -0.094289 | 2.3159 | 0.087487 | 0.091513 | -0.3272 | -0.20785 | -0.12187 | -0.15216 | 0.076947 | -0.030818 | 0.091049 | -0.07971 | -0.36496 | 123.1311 | 122.8982 | 123.0176 | 66.8944 | -123.2294 | 123.0732 | 123.1457 | 122.8604 | 66.8934 | -123.3473
28.2812 | 123.2895 | -66.8472 | 56.3416 | 0.057113 | 0.0021157 | 0.0020951 | 0.056591 | 0.0012778 | 0.056465 | 0.058893 | 0.00029332 | -0.00021967 | 0.067733 | -0.0022937 | 0.067334 | -64.5542 | 0.033457 | -66.7735 | 56.2656 | 56.0281 | 56.152 | -66.897 | -66.7932 | 0.027831 | -66.8918 | 56.2031 | 56.2893 | 55.9583 | -66.9782 | -0.049811 | -0.075979 | 2.293 | 0.073755 | 0.12357 | -0.31347 | -0.18954 | -0.13102 | -0.13843 | 0.054057 | -0.04455 | 0.08647 | -0.052243 | -0.38328 | 123.1128 | 122.8753 | 122.9992 | 66.8807 | -123.2386 | 123.0504 | 123.1365 | 122.8055 | 66.8751 | -123.3198
29.2812 | 123.2849 | -66.8518 | 56.3278 | 0.072375 | 0.0031837 | 0.0010261 | 0.059797 | 0.00020984 | 0.058602 | 0.058893 | 0.0013613 | 0.0019163 | 0.065596 | -0.0033627 | 0.067334 | -64.5542 | 0.028878 | -66.7735 | 56.2702 | 56.0327 | 56.1612 | -66.8833 | -66.7932 | 0.027831 | -66.9009 | 56.1985 | 56.2847 | 55.9629 | -66.9828 | -0.031496 | -0.057668 | 2.2976 | 0.078333 | 0.10983 | -0.29516 | -0.16665 | -0.13102 | -0.12927 | 0.058635 | -0.049129 | 0.081892 | -0.043089 | -0.36497 | 123.122 | 122.8845 | 123.013 | 66.8807 | -123.2111 | 123.0504 | 123.1365 | 122.8147 | 66.8796 | -123.3106
30.2812 | 123.3673 | -66.8152 | 56.3004 | 0.072375 | 0.0021157 | -4.1882e-05 | 0.056591 | 0.0012778 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.065596 | -0.0022937 | 0.066266 | -64.568 | 0.033457 | -66.7689 | 56.2656 | 56.0281 | 56.1612 | -66.8421 | -66.7977 | 0.023253 | -66.8918 | 56.2077 | 56.2847 | 55.9583 | -66.9874 | -0.026907 | -0.03478 | 2.2472 | 0.04629 | 0.073197 | -0.27227 | -0.13919 | -0.17222 | -0.092652 | 0.017436 | -0.076593 | 0.095628 | -0.015623 | -0.34208 | 123.0808 | 122.8433 | 122.9764 | 66.8486 | -123.1424 | 123.0229 | 123.0999 | 122.7735 | 66.8384 | -123.2878
31.2812 | 123.2712 | -66.8289 | 56.3278 | 0.057113 | 0.0021157 | 0.0010261 | 0.05766 | 0.0012778 | 0.055397 | 0.074154 | 0.00029332 | 0.00084833 | 0.066664 | -0.0012257 | 0.067334 | -64.5496 | 0.028878 | -66.7735 | 56.2702 | 56.0281 | 56.1612 | -66.8833 | -66.7977 | 0.023253 | -66.8872 | 56.1985 | 56.2893 | 55.9583 | -66.9828 | -0.054385 | -0.057668 | 2.2793 | 0.055444 | 0.10983 | -0.29974 | -0.16665 | -0.15391 | -0.12927 | 0.031168 | -0.058282 | 0.095628 | -0.03851 | -0.36955 | 123.0991 | 122.857 | 122.9901 | 66.8578 | -123.2111 | 123.0275 | 123.1182 | 122.7872 | 66.8522 | -123.3106
32.2812 | 123.349 | -66.8289 | 56.2912 | 0.072375 | 0.0021157 | -4.1882e-05 | 0.05766 | 0.0023458 | 0.057534 | 0.074154 | -0.0018437 | -0.00021967 | 0.064528 | -0.00015667 | 0.066266 | -64.5634 | 0.038035 | -66.7781 | 56.2656 | 56.0327 | 56.152 | -66.8741 | -66.7886 | 0.018674 | -66.8918 | 56.2031 | 56.2847 | 55.9995 | -66.9966 | -0.045227 | -0.025625 | 2.2655 | 0.050865 | 0.096092 | -0.25854 | -0.13919 | -0.16765 | -0.088075 | 0.040325 | -0.062861 | 0.10479 | -0.006468 | -0.29172 | 123.0945 | 122.8616 | 122.9809 | 66.867 | -123.1653 | 123.032 | 123.1136 | 122.8284 | 66.8476 | -123.2878
33.2812 | 123.2803 | -66.8427 | 56.3232 | 0.072375 | 0.0021157 | -4.1882e-05 | 0.058728 | 0.0012778 | 0.056465 | 0.043632 | 0.0013613 | 0.00084833 | 0.064528 | -0.0022937 | 0.066266 | -64.5359 | 0.028878 | -66.7735 | 56.2656 | 56.0281 | 56.1566 | -66.8513 | -66.7977 | 0.03241 | -66.8964 | 56.1985 | 56.2847 | 55.9674 | -66.9874 | -0.0086 | -0.057668 | 2.3067 | 0.069177 | 0.077777 | -0.29516 | -0.16665 | -0.14476 | -0.1247 | 0.044901 | -0.053707 | 0.091049 | -0.038511 | -0.35581 | 123.1082 | 122.8707 | 122.9992 | 66.8715 | -123.1745 | 123.0412 | 123.1274 | 122.8101 | 66.8751 | -123.3106
34.2812 | 123.2712 | -66.8427 | 56.3461 | 0.072375 | 0.0021157 | -4.1882e-05 | 0.056591 | 0.0012778 | 0.056465 | 0.058893 | 0.00029332 | -0.0012887 | 0.066664 | 0.00091133 | 0.065198 | -64.5359 | 0.0243 | -66.7826 | 56.2747 | 56.0372 | 56.1657 | -66.8329 | -66.7886 | 0.018674 | -66.9009 | 56.2031 | 56.2802 | 55.9674 | -66.9874 | 0.009716 | -0.071399 | 2.3067 | 0.06002 | 0.050304 | -0.30889 | -0.18038 | -0.14476 | -0.14301 | 0.054058 | -0.058285 | 0.086471 | -0.065977 | -0.3787 | 123.1174 | 122.8799 | 123.0084 | 66.867 | -123.1791 | 123.0458 | 123.1228 | 122.8101 | 66.8613 | -123.3335
35.2812 | 123.2437 | -66.8518 | 56.3553 | 0.072375 | 0.0021157 | 0.0010261 | 0.055523 | 0.0012778 | 0.056465 | 0.058893 | 0.0013613 | 0.00084833 | 0.065596 | -0.0012257 | 0.06413 | -64.5451 | 0.033457 | -66.7781 | 56.2656 | 56.0327 | 56.1612 | -66.8604 | -66.7886 | 0.03241 | -66.8872 | 56.1985 | 56.2847 | 55.9674 | -66.9828 | -0.008601 | -0.089712 | 2.3067 | 0.073754 | 0.082355 | -0.32263 | -0.19412 | -0.13102 | -0.15674 | 0.063214 | -0.035393 | 0.095628 | -0.070555 | -0.38786 | 123.1174 | 122.8845 | 123.013 | 66.8853 | -123.2157 | 123.0504 | 123.1365 | 122.8192 | 66.8842 | -123.3381
36.2812 | 123.262 | -66.8472 | 56.3416 | 0.026589 | 0.0021157 | 0.0010261 | 0.056591 | 0.0012778 | 0.056465 | 0.043632 | 0.00029332 | -0.0012887 | 0.064528 | -0.0012257 | 0.066266 | -64.5451 | 0.028878 | -66.7735 | 56.2702 | 56.0281 | 56.152 | -66.8833 | -66.7932 | 0.027831 | -66.8964 | 56.1985 | 56.2847 | 55.9583 | -66.9828 | -0.036074 | -0.071401 | 2.3022 | 0.073755 | 0.10983 | -0.31347 | -0.18954 | -0.1356 | -0.14301 | 0.054057 | -0.049129 | 0.08647 | -0.056822 | -0.38328 | 123.1174 | 122.8753 | 122.9992 | 66.8761 | -123.2249 | 123.0458 | 123.132 | 122.8055 | 66.8751 | -123.3244
37.2812 | 123.2758 | -66.8472 | 56.3278 | 0.057113 | 0.0010477 | -0.0011099 | 0.055523 | 0.0023458 | 0.056465 | 0.074154 | 0.00029332 | -0.00021967 | 0.065596 | -0.0012257 | 0.066266 | -64.5313 | 0.028878 | -66.7781 | 56.2702 | 56.0372 | 56.1657 | -66.8879 | -66.8023 | 0.023253 | -66.8964 | 56.194 | 56.2802 | 55.9903 | -66.9874 | -0.040653 | -0.057668 | 2.3159 | 0.069176 | 0.10983 | -0.29058 | -0.16207 | -0.14018 | -0.13385 | 0.0449 | -0.049129 | 0.091049 | -0.047667 | -0.3375 | 123.1174 | 122.8845 | 123.013 | 66.8761 | -123.2157 | 123.0412 | 123.1274 | 122.8376 | 66.8705 | -123.3152
38.2812 | 123.262 | -66.8335 | 56.337 | 0.041851 | 0.0021157 | -4.1882e-05 | 0.055523 | 0.00020984 | 0.055397 | 0.058893 | 0.00029332 | -0.0012887 | 0.065596 | -0.0012257 | 0.066266 | -64.5451 | 0.028878 | -66.7781 | 56.2656 | 56.0281 | 56.1566 | -66.8513 | -66.7977 | 0.023253 | -66.8964 | 56.194 | 56.2893 | 55.9629 | -66.9874 | -0.017755 | -0.071401 | 2.2884 | 0.055443 | 0.073198 | -0.30889 | -0.18039 | -0.15391 | -0.14301 | 0.035746 | -0.062862 | 0.091049 | -0.047665 | -0.37412 | 123.0991 | 122.8616 | 122.9901 | 66.8624 | -123.1882 | 123.0275 | 123.1228 | 122.7963 | 66.8567 | -123.3244
39.2969 | 123.3444 | -66.8015 | 56.2912 | 0.057113 | 0.0021157 | 0.0010261 | 0.054455 | 0.0023458 | 0.055397 | 0.074154 | 0.0013613 | 0.00084833 | 0.066664 | -0.0012257 | 0.066266 | -64.6412 | 0.038035 | -66.7781 | 56.2747 | 56.0235 | 56.1612 | -66.8604 | -66.7886 | 0.023253 | -66.8964 | 56.1985 | 56.2893 | 55.9537 | -66.992 | -0.058955 | -0.016468 | 2.1602 | 0.0234 | 0.082355 | -0.2677 | -0.13003 | -0.19053 | -0.092654 | 0.01286 | -0.094905 | 0.095628 | -0.001889 | -0.3375 | 123.0762 | 122.825 | 122.9626 | 66.8395 | -123.1516 | 123 | 123.0908 | 122.7551 | 66.8247 | -123.2832
40.2812 | 123.23 | -66.8381 | 56.3416 | 0.041851 | 0.0031837 | -4.1882e-05 | 0.056591 | 0.00020984 | 0.058602 | 0.058893 | -0.0018437 | 0.00084833 | 0.066664 | -0.0012257 | 0.065198 | -64.5451 | 0.033457 | -66.7781 | 56.2656 | 56.0327 | 56.1612 | -66.8238 | -66.7932 | 0.023253 | -66.8964 | 56.2031 | 56.2847 | 55.9629 | -66.992 | 0.014297 | -0.075979 | 2.293 | 0.060021 | 0.045724 | -0.30889 | -0.18038 | -0.15391 | -0.13843 | 0.044902 | -0.058284 | 0.095628 | -0.056822 | -0.3787 | 123.1036 | 122.8707 | 122.9992 | 66.8715 | -123.1653 | 123.0412 | 123.1228 | 122.8009 | 66.8613 | -123.3335
41.2812 | 123.3261 | -66.8381 | 56.3324 | 0.057113 | 0.0021157 | -4.1882e-05 | 0.05766 | -0.0019272 | 0.056465 | 0.058893 | 0.00029332 | 0.0019163 | 0.062391 | -0.0012257 | 0.065198 | -64.5313 | 0.033457 | -66.7872 | 56.2702 | 56.0464 | 56.1566 | -66.8833 | -66.7977 | 0.023253 | -66.8964 | 56.1985 | 56.2802 | 55.9629 | -66.9874 | -0.045229 | -0.062245 | 2.3067 | 0.050865 | 0.096094 | -0.286 | -0.17581 | -0.14933 | -0.13385 | 0.040324 | -0.058284 | 0.091049 | -0.052244 | -0.36955 | 123.1082 | 122.8845 | 122.9947 | 66.8715 | -123.2157 | 123.0366 | 123.1182 | 122.8009 | 66.8613 | -123.3198
42.2812 | 123.3032 | -66.8198 | 56.3507 | 0.057113 | -2.1265e-05 | 0.0010261 | 0.05766 | 0.0012778 | 0.057534 | 0.028371 | -0.00077468 | 0.00084833 | 0.064528 | -0.00015667 | 0.065198 | -64.5359 | 0.033457 | -66.7689 | 56.2747 | 56.0372 | 56.1612 | -66.8192 | -66.7886 | 0.018674 | -66.8918 | 56.1985 | 56.2802 | 55.9583 | -66.9828 | 0.000565 | -0.075977 | 2.2839 | 0.050867 | 0.050302 | -0.31347 | -0.18954 | -0.16307 | -0.15216 | 0.03117 | -0.072016 | 0.091049 | -0.070555 | -0.39243 | 123.0945 | 122.857 | 122.9809 | 66.8532 | -123.1699 | 123.0183 | 123.0999 | 122.778 | 66.8384 | -123.3335
43.2812 | 123.3078 | -66.8152 | 56.3553 | 0.072375 | 0.0010477 | -4.1882e-05 | 0.055523 | 0.0012778 | 0.056465 | 0.074154 | -0.00077468 | -0.00021967 | 0.066664 | -0.00015667 | 0.066266 | -64.5313 | 0.038035 | -66.7918 | 56.2702 | 56.0327 | 56.1612 | -66.8421 | -66.7932 | 0.023253 | -66.8964 | 56.1985 | 56.2847 | 55.9674 | -66.992 | -0.026907 | -0.085134 | 2.2839 | 0.023398 | 0.050305 | -0.32263 | -0.19412 | -0.1768 | -0.15674 | 0.022014 | -0.081172 | 0.095628 | -0.070555 | -0.38786 | 123.0853 | 122.8478 | 122.9764 | 66.8532 | -123.1974 | 123.0137 | 123.0999 | 122.7826 | 66.8384 | -123.3473
44.2812 | 123.3307 | -66.8335 | 56.3324 | 0.041851 | -2.1265e-05 | -4.1882e-05 | 0.056591 | 0.00020984 | 0.057534 | 0.058893 | -0.00077468 | 0.00084833 | 0.065596 | -0.0012257 | 0.066266 | -64.5313 | 0.028878 | -66.7735 | 56.2656 | 56.0327 | 56.1612 | -66.8558 | -66.7886 | 0.023253 | -66.9009 | 56.1985 | 56.2847 | 55.9537 | -66.9874 | -0.022334 | -0.066823 | 2.3022 | 0.060022 | 0.082356 | -0.29974 | -0.17123 | -0.15391 | -0.13385 | 0.044903 | -0.06744 | 0.086471 | -0.047666 | -0.3787 | 123.0991 | 122.8662 | 122.9947 | 66.8624 | -123.1882 | 123.032 | 123.1182 | 122.7872 | 66.8567 | -123.3198
45.2812 | 123.3124 | -66.8198 | 56.3461 | 0.072375 | -2.1265e-05 | 0.0010261 | 0.058728 | 0.00020984 | 0.057534 | 0.058893 | 0.0013613 | 0.00084833 | 0.064528 | -0.00015667 | 0.065198 | -64.5313 | 0.038035 | -66.7735 | 56.261 | 56.0372 | 56.1703 | -66.865 | -66.7977 | 0.023253 | -66.8964 | 56.1985 | 56.2847 | 55.9629 | -66.9874 | -0.045224 | -0.085135 | 2.2884 | 0.046289 | 0.091513 | -0.30889 | -0.17581 | -0.16764 | -0.14758 | 0.022013 | -0.076595 | 0.091049 | -0.061399 | -0.38328 | 123.0808 | 122.857 | 122.9901 | 66.8578 | -123.2111 | 123.0183 | 123.1045 | 122.7826 | 66.843 | -123.3335
46.2812 | 123.2895 | -66.8289 | 56.3324 | 0.057113 | -0.0010893 | -0.0011099 | 0.05766 | -0.0019272 | 0.057534 | 0.074154 | -0.00077468 | -0.00021967 | 0.066664 | -0.0012257 | 0.065198 | -64.5359 | 0.028878 | -66.7781 | 56.2702 | 56.0327 | 56.1566 | -66.8558 | -66.8023 | 0.018674 | -66.9009 | 56.2077 | 56.2802 | 55.9949 | -66.9874 | -0.026912 | -0.062245 | 2.293 | 0.050865 | 0.077777 | -0.29974 | -0.17581 | -0.15849 | -0.1247 | 0.026589 | -0.072018 | 0.086471 | -0.052244 | -0.33749 | 123.0991 | 122.8616 | 122.9855 | 66.8578 | -123.1882 | 123.0366 | 123.1091 | 122.8238 | 66.8476 | -123.3198
47.2812 | 123.2758 | -66.8381 | 56.3278 | 0.057113 | 0.0021157 | 0.0010261 | 0.056591 | 0.00020984 | 0.055397 | 0.074154 | 0.00029332 | 0.0029843 | 0.06346 | -0.0012257 | 0.065198 | -64.5359 | 0.028878 | -66.7781 | 56.261 | 56.0372 | 56.1566 | -66.897 | -66.7932 | 0.027831 | -66.8918 | 56.1985 | 56.2893 | 55.9857 | -66.9874 | -0.058966 | -0.066825 | 2.3022 | 0.060021 | 0.11899 | -0.29058 | -0.17123 | -0.14933 | -0.12927 | 0.044902 | -0.053705 | 0.095628 | -0.03851 | -0.34208 | 123.0991 | 122.8753 | 122.9947 | 66.867 | -123.2249 | 123.0366 | 123.1274 | 122.8238 | 66.8659 | -123.3152
48.2812 | 123.2666 | -66.8427 | 56.3324 | 0.041851 | -2.1265e-05 | -4.1882e-05 | 0.054455 | 0.00020984 | 0.056465 | 0.058893 | -0.0018437 | 0.00084833 | 0.064528 | -0.0022937 | 0.066266 | -64.5496 | 0.033457 | -66.7735 | 56.2702 | 56.0327 | 56.1612 | -66.8696 | -66.7977 | 0.014095 | -66.8964 | 56.194 | 56.2893 | 55.9629 | -66.9828 | -0.026915 | -0.062245 | 2.293 | 0.069177 | 0.096092 | -0.29974 | -0.17123 | -0.14018 | -0.13843 | 0.044901 | -0.053707 | 0.08647 | -0.043087 | -0.36955 | 123.1128 | 122.8753 | 123.0038 | 66.8761 | -123.202 | 123.0366 | 123.132 | 122.8055 | 66.8567 | -123.3152
49.2812 | 123.2849 | -66.8152 | 56.3782 | 0.057113 | 0.0010477 | -4.1882e-05 | 0.056591 | 0.00020984 | 0.056465 | 0.058893 | 0.00029332 | -0.00021967 | 0.06346 | -0.00015667 | 0.065198 | -64.5313 | 0.028878 | -66.7781 | 56.2702 | 56.051 | 56.1612 | -66.8879 | -66.7977 | 0.023253 | -66.8964 | 56.2031 | 56.2939 | 55.9857 | -66.9874 | -0.072696 | -0.10802 | 2.2839 | 0.037133 | 0.10983 | -0.3272 | -0.21701 | -0.17222 | -0.17505 | 0.017436 | -0.081172 | 0.091049 | -0.084285 | -0.39243 | 123.0853 | 122.8662 | 122.9764 | 66.8441 | -123.2661 | 123.0183 | 123.1091 | 122.8009 | 66.8384 | -123.3656
50.2812 | 123.262 | -66.8243 | 56.369 | 0.041851 | 0.0010477 | -4.1882e-05 | 0.056591 | 0.0012778 | 0.057534 | 0.074154 | 0.0024293 | -0.00021967 | 0.064528 | -0.00015667 | 0.065198 | -64.5359 | 0.033457 | -66.7689 | 56.261 | 56.0372 | 56.1566 | -66.9016 | -66.7886 | 0.023253 | -66.8918 | 56.194 | 56.2893 | 55.9537 | -66.992 | -0.077278 | -0.10802 | 2.2884 | 0.055445 | 0.13272 | -0.33178 | -0.21243 | -0.16764 | -0.17505 | 0.035748 | -0.067438 | 0.10021 | -0.079709 | -0.41532 | 123.0853 | 122.8616 | 122.9809 | 66.8578 | -123.2706 | 123.0183 | 123.1137 | 122.778 | 66.8476 | -123.361
51.2812 | 123.2758 | -66.8335 | 56.337 | 0.057113 | 0.0010477 | -4.1882e-05 | 0.055523 | -0.00085916 | 0.057534 | 0.043632 | 0.00029332 | -0.00021967 | 0.065596 | -0.00015667 | 0.065198 | -64.5359 | 0.0243 | -66.7689 | 56.2747 | 56.0418 | 56.1566 | -66.897 | -66.784 | 0.023253 | -66.9009 | 56.1985 | 56.2847 | 55.972 | -66.9966 | -0.063544 | -0.062244 | 2.2976 | 0.0646 | 0.12814 | -0.29516 | -0.18039 | -0.16307 | -0.13843 | 0.049482 | -0.06744 | 0.095629 | -0.052244 | -0.36497 | 123.1082 | 122.8753 | 122.9901 | 66.8578 | -123.234 | 123.032 | 123.1182 | 122.8055 | 66.8567 | -123.3335
52.2812 | 123.2941 | -66.8152 | 56.3507 | 0.041851 | -2.1265e-05 | -0.0021789 | 0.055523 | -0.00085916 | 0.056465 | 0.043632 | 0.00029332 | -0.0012887 | 0.065596 | 0.0019793 | 0.065198 | -64.5359 | 0.033457 | -66.7735 | 56.2747 | 56.0372 | 56.152 | -66.9016 | -66.7932 | 0.018674 | -66.8964 | 56.194 | 56.2847 | 55.9583 | -66.992 | -0.086433 | -0.075977 | 2.2793 | 0.041712 | 0.12815 | -0.31347 | -0.1987 | -0.1768 | -0.15674 | 0.022014 | -0.081172 | 0.095628 | -0.065977 | -0.39243 | 123.0899 | 122.8524 | 122.9672 | 66.8486 | -123.2523 | 123.0092 | 123.0999 | 122.7735 | 66.8339 | -123.3427
53.2812 | 123.2758 | -66.8381 | 56.3599 | 0.057113 | 0.0010477 | -0.0011099 | 0.05766 | -0.00085916 | 0.055397 | 0.074154 | 0.00029332 | -0.00021967 | 0.065596 | 0.00091133 | 0.066266 | -64.5496 | 0.033457 | -66.7689 | 56.2702 | 56.0418 | 56.1612 | -66.8696 | -66.7977 | 0.018674 | -66.8964 | 56.2031 | 56.2847 | 55.9583 | -66.9828 | -0.031492 | -0.089711 | 2.2884 | 0.069178 | 0.10067 | -0.31805 | -0.19869 | -0.14475 | -0.15674 | 0.040324 | -0.058284 | 0.08647 | -0.075132 | -0.40159 | 123.1082 | 122.8799 | 122.9992 | 66.8715 | -123.2294 | 123.0412 | 123.1228 | 122.7963 | 66.8567 | -123.3427
54.2812 | 123.2574 | -66.806 | 56.3416 | 0.057113 | -0.0010893 | 0.0010261 | 0.055523 | -0.0019272 | 0.057534 | 0.074154 | 0.0013613 | -0.0012887 | 0.066664 | 0.00091133 | 0.06413 | -64.5542 | 0.028878 | -66.7781 | 56.261 | 56.0372 | 56.1612 | -66.8879 | -66.7886 | 0.023253 | -66.8964 | 56.1985 | 56.2939 | 55.9629 | -66.9874 | -0.081852 | -0.080558 | 2.2518 | 0.027977 | 0.10983 | -0.30431 | -0.18038 | -0.18138 | -0.14301 | 0.017437 | -0.090328 | 0.091049 | -0.047664 | -0.3787 | 123.067 | 122.8433 | 122.9672 | 66.8349 | -123.2294 | 123.0046 | 123.0999 | 122.7689 | 66.8293 | -123.329
55.2812 | 123.2666 | -66.8243 | 56.3736 | 0.072375 | -0.0010893 | -0.0011099 | 0.056591 | -0.0019272 | 0.055397 | 0.058893 | -0.00077468 | -0.00021967 | 0.066664 | -0.00015667 | 0.063061 | -64.5588 | 0.0243 | -66.7735 | 56.2747 | 56.0327 | 56.1703 | -66.9016 | -66.7932 | 0.023253 | -66.8918 | 56.1985 | 56.2893 | 55.9491 | -66.9828 | -0.077278 | -0.098865 | 2.2655 | 0.050867 | 0.12815 | -0.34094 | -0.20327 | -0.15849 | -0.17505 | 0.031169 | -0.067438 | 0.091049 | -0.084286 | -0.42448 | 123.0991 | 122.857 | 122.9947 | 66.8486 | -123.2752 | 123.0229 | 123.1137 | 122.7735 | 66.8476 | -123.3564
56.2812 | 123.2758 | -66.8106 | 56.3553 | 0.057113 | -0.0010893 | -4.1882e-05 | 0.059797 | -0.00085916 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.065596 | 0.0019793 | 0.06413 | -64.5451 | 0.028878 | -66.7689 | 56.2656 | 56.0418 | 56.1657 | -66.9016 | -66.7977 | 0.023253 | -66.8964 | 56.1985 | 56.2756 | 55.9537 | -66.9874 | -0.091011 | -0.089712 | 2.2655 | 0.041712 | 0.13272 | -0.31347 | -0.18954 | -0.1768 | -0.15674 | 0.012858 | -0.08575 | 0.091049 | -0.079712 | -0.40159 | 123.0762 | 122.8524 | 122.9764 | 66.8395 | -123.2569 | 123.0092 | 123.0862 | 122.7643 | 66.8339 | -123.3427
57.2812 | 123.2758 | -66.8381 | 56.369 | 0.1029 | -2.1265e-05 | 0.0010261 | 0.055523 | 0.00020984 | 0.055397 | 0.074154 | 0.00029332 | 0.00084833 | 0.06346 | -0.00015667 | 0.063061 | -64.5588 | 0.033457 | -66.7689 | 56.261 | 56.0372 | 56.1566 | -66.9062 | -66.7932 | 0.014095 | -66.8918 | 56.2031 | 56.2847 | 55.9903 | -66.992 | -0.068124 | -0.10802 | 2.2793 | 0.069178 | 0.1373 | -0.33178 | -0.21243 | -0.15391 | -0.16589 | 0.044902 | -0.053705 | 0.10021 | -0.084288 | -0.3787 | 123.0991 | 122.8753 | 122.9947 | 66.8715 | -123.2752 | 123.0412 | 123.1228 | 122.8284 | 66.8522 | -123.361
58.2812 | 123.2986 | -66.8243 | 56.369 | 0.072375 | -2.1265e-05 | -4.1882e-05 | 0.05766 | 0.0012778 | 0.057534 | 0.089415 | -0.00077468 | 0.00084833 | 0.066664 | 0.0019793 | 0.06413 | -64.5588 | 0.028878 | -66.7781 | 56.261 | 56.0418 | 56.1612 | -66.897 | -66.784 | 0.018674 | -66.8964 | 56.2031 | 56.2847 | 55.9491 | -66.992 | -0.072699 | -0.10802 | 2.2655 | 0.046288 | 0.11899 | -0.3272 | -0.20785 | -0.16764 | -0.16589 | 0.040327 | -0.072017 | 0.095628 | -0.084288 | -0.4199 | 123.0853 | 122.8662 | 122.9855 | 66.8532 | -123.2661 | 123.0275 | 123.1091 | 122.7735 | 66.843 | -123.361
59.2812 | 123.2712 | -66.8243 | 56.3736 | 0.057113 | -0.0021573 | -0.0011099 | 0.056591 | -0.00085916 | 0.055397 | 0.089415 | -0.00077468 | -0.00021967 | 0.06346 | 0.0019793 | 0.065198 | -64.5542 | 0.028878 | -66.7735 | 56.2702 | 56.0372 | 56.1657 | -66.8925 | -66.7886 | 0.023253 | -66.9009 | 56.1894 | 56.2893 | 55.9491 | -66.9874 | -0.06812 | -0.10344 | 2.2701 | 0.050867 | 0.11899 | -0.33636 | -0.20785 | -0.16307 | -0.18421 | 0.035748 | -0.076595 | 0.086471 | -0.084286 | -0.42448 | 123.0945 | 122.8616 | 122.9901 | 66.8532 | -123.2661 | 123.0137 | 123.1137 | 122.7735 | 66.8476 | -123.361
60.2812 | 123.262 | -66.8198 | 56.3553 | 0.057113 | -2.1265e-05 | -0.0021789 | 0.05766 | -0.00085916 | 0.057534 | 0.089415 | 0.0024293 | 0.00084833 | 0.065596 | -0.00015667 | 0.06413 | -64.5542 | 0.033457 | -66.7643 | 56.2656 | 56.0327 | 56.1612 | -66.8696 | -66.7932 | 0.023253 | -66.8964 | 56.2077 | 56.2847 | 55.9674 | -66.992 | -0.049803 | -0.089712 | 2.2655 | 0.055445 | 0.10525 | -0.32263 | -0.19412 | -0.17222 | -0.14758 | 0.026591 | -0.076595 | 0.095628 | -0.070555 | -0.38786 | 123.0853 | 122.8524 | 122.9809 | 66.8532 | -123.2249 | 123.0275 | 123.1045 | 122.7872 | 66.843 | -123.3473
61.2812 | 123.3582 | -66.7923 | 56.369 | 0.072375 | -0.0021573 | -4.1882e-05 | 0.056591 | 0.00020984 | 0.058602 | 0.10468 | 0.0024293 | -0.00021967 | 0.066664 | -0.0012257 | 0.063061 | -64.5771 | 0.0243 | -66.7689 | 56.2656 | 56.0372 | 56.1612 | -66.9062 | -66.784 | 0.023253 | -66.8964 | 56.2031 | 56.2893 | 55.9491 | -66.9828 | -0.1139 | -0.10345 | 2.2152 | 0.023401 | 0.1373 | -0.33178 | -0.20785 | -0.19053 | -0.16589 | 0.008283 | -0.10406 | 0.08647 | -0.079709 | -0.4199 | 123.0579 | 122.8295 | 122.9535 | 66.8166 | -123.2752 | 122.9954 | 123.0816 | 122.7414 | 66.8156 | -123.3518
62.2812 | 123.2758 | -66.8106 | 56.3461 | 0.072375 | -0.0021573 | 0.0010261 | 0.056591 | 0.0012778 | 0.057534 | 0.074154 | -0.00077468 | -0.00021967 | 0.065596 | 0.00091133 | 0.065198 | -64.5588 | 0.019721 | -66.7735 | 56.2564 | 56.0372 | 56.1612 | -66.8879 | -66.7977 | 0.023253 | -66.8918 | 56.1985 | 56.2802 | 55.9445 | -66.9874 | -0.077274 | -0.089713 | 2.2518 | 0.037134 | 0.11441 | -0.30889 | -0.18496 | -0.1768 | -0.14758 | 0.012858 | -0.081171 | 0.095628 | -0.065977 | -0.40159 | 123.067 | 122.8478 | 122.9718 | 66.8303 | -123.234 | 123.0092 | 123.0908 | 122.7551 | 66.8339 | -123.3335
63.2812 | 123.2803 | -66.8015 | 56.3828 | 0.057113 | -0.0010893 | 0.0020951 | 0.056591 | -0.00085916 | 0.057534 | 0.058893 | 0.00029332 | -0.00021967 | 0.064528 | 0.0030483 | 0.065198 | -64.568 | 0.028878 | -66.7689 | 56.2656 | 56.0372 | 56.1566 | -66.8925 | -66.7932 | 0.023253 | -66.8964 | 56.2031 | 56.2847 | 55.9583 | -66.992 | -0.091008 | -0.11718 | 2.2335 | 0.032557 | 0.12356 | -0.34551 | -0.22616 | -0.19053 | -0.17963 | 0.008281 | -0.094905 | 0.095628 | -0.09802 | -0.42448 | 123.067 | 122.8387 | 122.958 | 66.8303 | -123.2752 | 123.0046 | 123.0862 | 122.7597 | 66.8247 | -123.3747
64.2812 | 123.3032 | -66.8106 | 56.3644 | 0.072375 | -0.0032263 | -4.1882e-05 | 0.056591 | -0.0019272 | 0.05967 | 0.058893 | 0.00029332 | -0.0012887 | 0.065596 | 0.0019793 | 0.065198 | -64.5634 | 0.0243 | -66.7689 | 56.2564 | 56.0327 | 56.1612 | -66.9062 | -66.784 | 0.023253 | -66.8918 | 56.194 | 56.2847 | 55.9537 | -66.9966 | -0.09559 | -0.10802 | 2.2472 | 0.041712 | 0.1373 | -0.33178 | -0.20327 | -0.18596 | -0.17047 | 0.026594 | -0.081171 | 0.10479 | -0.07971 | -0.41075 | 123.067 | 122.8433 | 122.9718 | 66.8349 | -123.2706 | 123.0046 | 123.0953 | 122.7643 | 66.8339 | -123.361
65.2812 | 123.2849 | -66.8198 | 56.3141 | 0.072375 | -2.1265e-05 | -0.0011099 | 0.056591 | 0.00020984 | 0.057534 | 0.058893 | -0.00077468 | -0.00021967 | 0.064528 | 0.00091133 | 0.065198 | -64.5725 | 0.019721 | -66.7689 | 56.2702 | 56.0372 | 56.1612 | -66.897 | -66.7932 | 0.014095 | -66.8964 | 56.194 | 56.2893 | 55.9491 | -66.9828 | -0.077277 | -0.043935 | 2.2472 | 0.050867 | 0.12814 | -0.27685 | -0.15292 | -0.16307 | -0.12012 | 0.026591 | -0.076595 | 0.08647 | -0.024777 | -0.36497 | 123.0899 | 122.857 | 122.9809 | 66.8395 | -123.2111 | 123.0137 | 123.1091 | 122.7689 | 66.8339 | -123.2969
66.3125 | 123.4085 | -66.7831 | 56.3141 | 0.041851 | -0.0042943 | -0.0011099 | 0.055523 | -0.00085916 | 0.057534 | 0.074154 | -0.0018437 | -0.0012887 | 0.065596 | 0.0019793 | 0.06413 | -64.6137 | 0.033457 | -66.7643 | 56.261 | 56.0281 | 56.1612 | -66.8787 | -66.784 | 0.014095 | -66.9009 | 56.1985 | 56.2847 | 55.9491 | -66.992 | -0.095582 | -0.053092 | 2.1694 | 0.018824 | 0.11441 | -0.28601 | -0.15292 | -0.20884 | -0.11554 | -0.000872 | -0.11779 | 0.09105 | -0.029356 | -0.36497 | 123.0441 | 122.8112 | 122.9443 | 66.8166 | -123.1928 | 122.9817 | 123.0679 | 122.7323 | 66.7972 | -123.3061
67.2812 | 123.2712 | -66.806 | 56.3599 | 0.041851 | -0.0010893 | -4.1882e-05 | 0.056591 | 0.0012778 | 0.056465 | 0.074154 | 0.00029332 | -0.00021967 | 0.065596 | 0.0030483 | 0.06413 | -64.5725 | 0.0243 | -66.7643 | 56.2702 | 56.0372 | 56.1566 | -66.8375 | -66.7932 | 0.023253 | -66.9009 | 56.1985 | 56.2847 | 55.9445 | -66.992 | -0.031484 | -0.089711 | 2.2335 | 0.041712 | 0.073196 | -0.32262 | -0.20327 | -0.18596 | -0.16132 | 0.012858 | -0.094906 | 0.09105 | -0.075132 | -0.41532 | 123.0762 | 122.8433 | 122.9626 | 66.8303 | -123.1974 | 123.0046 | 123.0908 | 122.7506 | 66.8293 | -123.3518
68.2812 | 123.3582 | -66.7786 | 56.3232 | 0.072375 | -0.0010893 | -4.1882e-05 | 0.056591 | -0.00085916 | 0.056465 | 0.089415 | -0.00077468 | -0.00021967 | 0.064528 | 0.0019793 | 0.065198 | -64.5908 | 0.0243 | -66.7689 | 56.2656 | 56.0372 | 56.1566 | -66.8467 | -66.7932 | 0.023253 | -66.9009 | 56.1985 | 56.2893 | 55.9583 | -66.9874 | -0.068108 | -0.057668 | 2.1877 | 0.009668 | 0.077776 | -0.286 | -0.16665 | -0.20884 | -0.1247 | -0.014608 | -0.12237 | 0.086471 | -0.033932 | -0.36497 | 123.0441 | 122.8158 | 122.9352 | 66.8029 | -123.1699 | 122.9771 | 123.0679 | 122.7368 | 66.8018 | -123.3106
69.2812 | 123.3765 | -66.774 | 56.3507 | 0.072375 | -0.0021573 | -4.1882e-05 | 0.056591 | 0.00020984 | 0.056465 | 0.074154 | -0.00077468 | 0.00084833 | 0.064528 | 0.00091133 | 0.06413 | -64.5908 | 0.028878 | -66.7735 | 56.261 | 56.0418 | 56.1657 | -66.897 | -66.7932 | 0.018674 | -66.8872 | 56.1985 | 56.2847 | 55.9583 | -67.0011 | -0.12305 | -0.089713 | 2.1831 | 0.000513 | 0.12357 | -0.30889 | -0.18496 | -0.22716 | -0.15216 | -0.019185 | -0.11321 | 0.11394 | -0.065977 | -0.39243 | 123.035 | 122.8158 | 122.9397 | 66.8029 | -123.2477 | 122.9725 | 123.0587 | 122.7323 | 66.7927 | -123.3519
70.2812 | 123.2529 | -66.8152 | 56.3507 | 0.087637 | -0.0010893 | -0.0032469 | 0.056591 | -0.0019272 | 0.056465 | 0.074154 | -0.0018437 | -0.0012887 | 0.065596 | 0.0019793 | 0.065198 | -64.5634 | 0.028878 | -66.7643 | 56.2656 | 56.0372 | 56.1612 | -66.8879 | -66.7886 | 0.018674 | -66.8918 | 56.1985 | 56.2893 | 55.9903 | -66.9828 | -0.072696 | -0.085134 | 2.2518 | 0.050868 | 0.12356 | -0.31347 | -0.18954 | -0.16764 | -0.15216 | 0.026593 | -0.076593 | 0.091049 | -0.061398 | -0.36038 | 123.0808 | 122.8524 | 122.9764 | 66.8441 | -123.2386 | 123.0137 | 123.1045 | 122.8055 | 66.8339 | -123.3335
71.2812 | 123.3856 | -66.7786 | 56.3416 | 0.087637 | -0.0010893 | 0.0010261 | 0.056591 | -0.00085916 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.064528 | 0.00091133 | 0.06413 | -64.5771 | 0.0243 | -66.7735 | 56.2702 | 56.0464 | 56.1612 | -66.8741 | -66.7886 | 0.023253 | -66.8964 | 56.1985 | 56.2802 | 55.9537 | -66.9874 | -0.095581 | -0.071401 | 2.2015 | 0.00509 | 0.10067 | -0.29516 | -0.18038 | -0.20884 | -0.14301 | -0.010029 | -0.11779 | 0.091049 | -0.0614 | -0.38786 | 123.0487 | 122.825 | 122.9397 | 66.8029 | -123.2157 | 122.9771 | 123.0587 | 122.7323 | 66.8018 | -123.329
72.2812 | 123.4039 | -66.774 | 56.337 | 0.057113 | -0.0021573 | -0.0011099 | 0.056591 | -0.00085916 | 0.056465 | 0.074154 | -0.00077468 | -0.0023567 | 0.064528 | 0.0019793 | 0.065198 | -64.5588 | 0.019721 | -66.7689 | 56.2564 | 56.0235 | 56.1429 | -66.7917 | -66.7886 | 0.014095 | -66.9009 | 56.1985 | 56.2847 | 56.0224 | -66.9828 | -0.017738 | -0.080558 | 2.2152 | 0.005091 | 0.022829 | -0.31347 | -0.19412 | -0.20884 | -0.13843 | -0.014606 | -0.12695 | 0.081892 | -0.052244 | -0.3146 | 123.0304 | 122.7975 | 122.9168 | 66.7937 | -123.1287 | 122.9725 | 123.0587 | 122.7964 | 66.7881 | -123.3198
73.2812 | 123.3398 | -66.774 | 56.3599 | 0.057113 | -0.0032263 | -0.0011099 | 0.056591 | 0.0012778 | 0.057534 | 0.074154 | 0.00029332 | 0.00084833 | 0.06346 | 0.0019793 | 0.063061 | -64.6046 | 0.033457 | -66.7781 | 56.293 | 56.051 | 56.1795 | -66.9428 | -66.7886 | 0.027831 | -66.8872 | 56.194 | 56.2939 | 56.1964 | -66.992 | -0.16884 | -0.066819 | 2.1694 | -0.004066 | 0.16478 | -0.30889 | -0.18038 | -0.218 | -0.1659 | -0.014606 | -0.11321 | 0.10479 | -0.065974 | -0.1635 | 123.067 | 122.825 | 122.9535 | 66.8074 | -123.3027 | 122.968 | 123.0679 | 122.9703 | 66.8018 | -123.3518
74.2812 | 123.3078 | -66.8655 | 56.3736 | 0.041851 | -0.0032263 | -4.1882e-05 | 0.055523 | 0.00020984 | 0.056465 | 0.043632 | 0.00029332 | -0.00021967 | 0.06346 | 0.00091133 | 0.06413 | -64.568 | 0.028878 | -66.7781 | 56.2839 | 56.0464 | 56.1841 | -66.9291 | -66.7932 | 0.023253 | -66.8964 | 56.1985 | 56.2847 | 56.1964 | -66.9874 | -0.063552 | -0.089709 | 2.2976 | 0.087487 | 0.15104 | -0.3272 | -0.18953 | -0.12187 | -0.17505 | 0.072368 | -0.030818 | 0.091049 | -0.088865 | -0.17723 | 123.1494 | 122.9119 | 123.0496 | 66.8944 | -123.3027 | 123.0641 | 123.1503 | 123.0619 | 66.8888 | -123.361
75.2812 | 123.381 | -66.7465 | 56.337 | 0.072375 | -0.0042943 | 0.0010261 | 0.05766 | -0.0019272 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.064528 | 0.0019793 | 0.06413 | -64.6458 | 0.033457 | -66.7826 | 56.2885 | 56.0464 | 56.1841 | -66.9291 | -66.7977 | 0.027831 | -66.8918 | 56.1985 | 56.2893 | 56.2009 | -66.9966 | -0.18257 | -0.048509 | 2.1007 | -0.03611 | 0.14646 | -0.29058 | -0.15291 | -0.25004 | -0.13843 | -0.051229 | -0.14526 | 0.10479 | -0.047665 | -0.13604 | 123.035 | 122.7929 | 122.9306 | 66.78 | -123.2661 | 122.9451 | 123.0358 | 122.9475 | 66.7744 | -123.3335
76.2812 | 123.3902 | -66.806 | 56.3049 | 0.057113 | -0.0021573 | -0.0011099 | 0.056591 | -0.00085916 | 0.056465 | 0.074154 | -0.00077468 | -0.00021967 | 0.064528 | 0.0019793 | 0.063061 | -64.6504 | 0.033457 | -66.7826 | 56.293 | 56.0464 | 56.1795 | -66.9337 | -66.7977 | 0.03241 | -66.8918 | 56.1985 | 56.2847 | 56.2101 | -66.9874 | -0.12764 | -0.011888 | 2.1557 | 0.023399 | 0.15104 | -0.25854 | -0.12545 | -0.18138 | -0.10639 | 0.00828 | -0.085749 | 0.095628 | -0.020201 | -0.094835 | 123.0991 | 122.8524 | 122.9855 | 66.8395 | -123.2386 | 123.0046 | 123.0908 | 123.0161 | 66.8384 | -123.2923
77.2812 | 123.4085 | -66.774 | 56.3232 | 0.072375 | -0.0032263 | -0.0011099 | 0.053386 | 0.00020984 | 0.055397 | 0.074154 | -0.00077468 | -0.00021967 | 0.065596 | 0.0041163 | 0.06413 | -64.6137 | 0.033457 | -66.7918 | 56.2885 | 56.0556 | 56.1886 | -66.9337 | -66.7977 | 0.023253 | -66.9009 | 56.194 | 56.2893 | 56.2101 | -66.9874 | -0.15968 | -0.034776 | 2.1602 | -0.017801 | 0.14188 | -0.26769 | -0.1346 | -0.21342 | -0.12927 | -0.023763 | -0.12695 | 0.086471 | -0.033932 | -0.11315 | 123.0625 | 122.8295 | 122.9626 | 66.8074 | -123.2569 | 122.968 | 123.0633 | 122.9841 | 66.7972 | -123.3106
78.2812 | 123.3948 | -66.7557 | 56.3461 | 0.057113 | -0.0021573 | -0.0011099 | 0.056591 | -0.0029952 | 0.056465 | 0.074154 | -0.0018437 | -0.0023567 | 0.065596 | 0.0041163 | 0.063061 | -64.6229 | 0.038035 | -66.7964 | 56.2976 | 56.0693 | 56.1978 | -66.9337 | -66.8069 | 0.03241 | -66.8826 | 56.1985 | 56.2893 | 56.2696 | -66.9828 | -0.178 | -0.048507 | 2.1328 | -0.04069 | 0.1373 | -0.27684 | -0.14833 | -0.22715 | -0.14758 | -0.051232 | -0.12695 | 0.10021 | -0.05682 | -0.076512 | 123.0533 | 122.825 | 122.9535 | 66.7937 | -123.2798 | 122.9542 | 123.045 | 123.0253 | 66.7881 | -123.329
79.2812 | 123.2483 | -66.8198 | 56.369 | 0.026589 | -0.0032263 | -0.0021789 | 0.055523 | 0.0012778 | 0.055397 | 0.058893 | -0.00077468 | -0.00021967 | 0.06346 | 0.0041163 | 0.06413 | -64.5725 | 0.033457 | -66.7964 | 56.3022 | 56.0647 | 56.1932 | -66.9474 | -66.8069 | 0.023253 | -66.8918 | 56.1985 | 56.2847 | 56.3337 | -66.992 | -0.12765 | -0.066818 | 2.2472 | 0.023397 | 0.15104 | -0.30431 | -0.1758 | -0.17222 | -0.17047 | 0.012855 | -0.072016 | 0.10021 | -0.084288 | -0.0353 | 123.122 | 122.8845 | 123.013 | 66.8532 | -123.3164 | 123.0183 | 123.1045 | 123.1535 | 66.843 | -123.361
80.2812 | 123.4085 | -66.774 | 56.3278 | 0.057113 | -0.0042943 | -4.1882e-05 | 0.055523 | 0.00020984 | 0.055397 | 0.074154 | -0.00077468 | -0.0012887 | 0.066664 | 0.0019793 | 0.06413 | -64.6229 | 0.033457 | -66.7918 | 56.2976 | 56.0647 | 56.1978 | -66.9428 | -66.8069 | 0.027831 | -66.8964 | 56.2031 | 56.2939 | 56.2742 | -66.9874 | -0.16884 | -0.030197 | 2.1511 | -0.017801 | 0.15104 | -0.26311 | -0.13002 | -0.21342 | -0.1247 | -0.032921 | -0.12237 | 0.091049 | -0.033931 | -0.053623 | 123.0716 | 122.8387 | 122.9718 | 66.8074 | -123.2706 | 122.9771 | 123.0679 | 123.0482 | 66.8018 | -123.3152
81.2812 | 123.4955 | -66.7236 | 56.3232 | 0.041851 | -0.0042943 | -0.0011099 | 0.054455 | -0.00085916 | 0.056465 | 0.043632 | -0.00077468 | -0.00021967 | 0.065596 | 0.0041163 | 0.063061 | -64.6687 | 0.028878 | -66.7735 | 56.2793 | 56.051 | 56.1749 | -66.9245 | -66.7932 | 0.027831 | -66.8872 | 56.1985 | 56.2893 | 56.1918 | -66.9874 | -0.20088 | -0.043933 | 2.055 | -0.049841 | 0.15104 | -0.27227 | -0.14834 | -0.26377 | -0.1247 | -0.069539 | -0.16357 | 0.10021 | -0.033932 | -0.13146 | 123.0029 | 122.7746 | 122.8985 | 66.7525 | -123.2478 | 122.9222 | 123.0129 | 122.9154 | 66.7515 | -123.3106
82.2812 | 123.3536 | -66.806 | 56.3461 | 0.041851 | -0.0021573 | 0.0010261 | 0.054455 | -0.00085916 | 0.055397 | 0.074154 | 0.0013613 | -0.00021967 | 0.065596 | 0.0041163 | 0.063061 | -64.6962 | 0.019721 | -66.7735 | 56.261 | 56.0464 | 56.152 | -66.9062 | -66.7886 | 0.014095 | -66.8918 | 56.2031 | 56.2847 | 56.2925 | -66.9874 | -0.10017 | -0.085135 | 2.1099 | 0.032556 | 0.13272 | -0.29974 | -0.19412 | -0.18138 | -0.14301 | 0.017437 | -0.085749 | 0.095628 | -0.061399 | -0.053619 | 123.067 | 122.8524 | 122.958 | 66.8258 | -123.2523 | 123.0092 | 123.0908 | 123.0985 | 66.8201 | -123.3335
83.2812 | 123.3353 | -66.806 | 56.3232 | 0.041851 | -0.0042943 | -0.0011099 | 0.054455 | -0.00085916 | 0.054329 | 0.058893 | 0.00029332 | 0.00084833 | 0.06346 | 0.0019793 | 0.06413 | -64.687 | 0.005985 | -66.7689 | 56.2564 | 56.1242 | 56.1474 | -66.897 | -66.784 | 0.023253 | -66.8964 | 56.1985 | 56.2802 | 56.2788 | -66.992 | -0.09101 | -0.066825 | 2.119 | 0.037134 | 0.12814 | -0.199 | -0.17581 | -0.18596 | -0.1247 | 0.022016 | -0.090328 | 0.095628 | -0.043089 | -0.044466 | 123.0624 | 122.9303 | 122.9535 | 66.812 | -123.2203 | 123.0046 | 123.0862 | 123.0848 | 66.8293 | -123.3152
84.2812 | 123.2941 | -66.806 | 56.3736 | 0.057113 | -0.0032263 | -4.1882e-05 | 0.056591 | -0.0029952 | 0.055397 | 0.058893 | 0.00029332 | -0.0023567 | 0.064528 | 0.0041163 | 0.06413 | -64.5954 | 0.019721 | -66.7735 | 56.261 | 56.1151 | 56.1474 | -66.8925 | -66.7932 | 0.027831 | -66.8872 | 56.194 | 56.2893 | 56.2605 | -66.9828 | -0.086431 | -0.1126 | 2.2106 | 0.032556 | 0.11899 | -0.25852 | -0.22616 | -0.1768 | -0.17963 | 0.012858 | -0.08117 | 0.095628 | -0.084286 | -0.11313 | 123.067 | 122.9211 | 122.9535 | 66.8258 | -123.2661 | 123 | 123.0953 | 123.0665 | 66.8339 | -123.3564
85.2812 | 123.4222 | -66.8152 | 56.3416 | 0.057113 | -0.0032263 | -4.1882e-05 | 0.055523 | -0.0019272 | 0.056465 | 0.074154 | -0.00077468 | 0.00084833 | 0.062391 | 0.0019793 | 0.061993 | -64.6733 | 0.010564 | -66.7735 | 56.2564 | 56.2021 | 56.1474 | -66.8604 | -66.7886 | 0.023253 | -66.8918 | 56.1985 | 56.2893 | 56.2376 | -66.9874 | -0.045222 | -0.085136 | 2.1419 | 0.041712 | 0.086934 | -0.13947 | -0.19412 | -0.17222 | -0.14301 | 0.026593 | -0.076593 | 0.095628 | -0.052243 | -0.10398 | 123.0716 | 123.0173 | 122.9626 | 66.8257 | -123.202 | 123.0137 | 123.1045 | 123.0528 | 66.8384 | -123.329
86.2812 | 123.349 | -66.8243 | 56.3141 | 0.041851 | -0.0042943 | -4.1882e-05 | 0.055523 | -0.0019272 | 0.055397 | 0.074154 | -0.00077468 | -0.0012887 | 0.06346 | 0.0030483 | 0.063061 | -64.6824 | 0.019721 | -66.7781 | 56.261 | 56.0968 | 56.1429 | -66.8192 | -66.7886 | 0.014095 | -66.8918 | 56.2077 | 56.2847 | 56.1231 | -66.9874 | 0.005143 | -0.053092 | 2.1419 | 0.046288 | 0.041145 | -0.21732 | -0.17123 | -0.16307 | -0.10639 | 0.035748 | -0.067438 | 0.095628 | -0.029356 | -0.19098 | 123.0853 | 122.9211 | 122.9672 | 66.8441 | -123.1333 | 123.032 | 123.1091 | 122.9474 | 66.8384 | -123.3015
87.2812 | 123.381 | -66.7877 | 56.3232 | 0.087637 | -0.0042943 | -0.0021789 | 0.05766 | 0.00020984 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.06346 | 0.0030483 | 0.065198 | -64.6366 | 0.0243 | -66.7735 | 56.2564 | 56.1013 | 56.1474 | -66.8604 | -66.7886 | 0.014095 | -66.8918 | 56.1985 | 56.2847 | 56.1002 | -66.992 | -0.072688 | -0.066825 | 2.1511 | 0.014246 | 0.086934 | -0.2219 | -0.17581 | -0.20427 | -0.1247 | -0.000873 | -0.10406 | 0.10021 | -0.038511 | -0.22303 | 123.0441 | 122.8891 | 122.9352 | 66.812 | -123.1837 | 122.9863 | 123.0725 | 122.8879 | 66.8018 | -123.3152
88.2812 | 123.3627 | -66.7923 | 56.3141 | 0.041851 | -0.0053623 | -0.0011099 | 0.056591 | -0.00085916 | 0.057534 | 0.074154 | 0.00029332 | 0.00084833 | 0.064528 | 0.0030483 | 0.063061 | -64.6458 | 0.019721 | -66.7781 | 56.261 | 56.0876 | 56.1429 | -66.8833 | -66.7886 | 0.014095 | -66.8872 | 56.1985 | 56.2847 | 56.1643 | -66.9874 | -0.091006 | -0.053092 | 2.1465 | 0.014244 | 0.10525 | -0.22648 | -0.17123 | -0.19511 | -0.11554 | 0.003704 | -0.094903 | 0.10021 | -0.029356 | -0.14978 | 123.0533 | 122.8799 | 122.9352 | 66.812 | -123.1974 | 122.9908 | 123.077 | 122.9566 | 66.8064 | -123.3015
89.2812 | 123.3994 | -66.774 | 56.3324 | 0.057113 | -0.0042943 | -0.0021789 | 0.055523 | 0.00020984 | 0.055397 | 0.074154 | 0.00029332 | -0.00021967 | 0.062391 | 0.0030483 | 0.065198 | -64.5863 | 0.015142 | -66.7826 | 56.261 | 56.0739 | 56.1429 | -66.8833 | -66.7932 | 0.014095 | -66.8918 | 56.1985 | 56.2939 | 56.2009 | -66.992 | -0.10932 | -0.071402 | 2.1877 | -0.008644 | 0.10067 | -0.25853 | -0.18954 | -0.218 | -0.13385 | -0.019185 | -0.11779 | 0.10021 | -0.038508 | -0.13146 | 123.035 | 122.8479 | 122.9168 | 66.7891 | -123.2157 | 122.9725 | 123.0679 | 122.9749 | 66.7881 | -123.3244
90.2812 | 123.4085 | -66.7969 | 56.2912 | 0.041851 | -0.0064313 | 0.0010261 | 0.055523 | -0.0019272 | 0.056465 | 0.058893 | -0.0018437 | -0.00021967 | 0.06346 | 0.00091133 | 0.065198 | -64.5863 | 0.019721 | -66.7689 | 56.2518 | 56.0739 | 56.1383 | -66.8604 | -66.7977 | 0.018674 | -66.8872 | 56.2031 | 56.2847 | 56.1872 | -66.9874 | -0.063533 | -0.03936 | 2.2106 | 0.027979 | 0.091512 | -0.21733 | -0.15292 | -0.19053 | -0.088075 | -0.000875 | -0.090325 | 0.10021 | -0.006468 | -0.10399 | 123.0487 | 122.8707 | 122.9351 | 66.8166 | -123.1516 | 123 | 123.0816 | 122.9841 | 66.8155 | -123.2786
91.2812 | 123.4406 | -66.806 | 56.2866 | 0.026589 | -0.0042943 | 0.0010261 | 0.05766 | -0.0019272 | 0.054329 | 0.058893 | -0.0018437 | -0.0023567 | 0.06346 | 0.0030483 | 0.063061 | -64.5771 | 0.019721 | -66.7735 | 56.261 | 56.0647 | 56.1429 | -66.8833 | -66.7932 | 0.014095 | -66.8918 | 56.2031 | 56.2802 | 56.1964 | -66.9874 | -0.077273 | -0.025626 | 2.2289 | 0.032556 | 0.10983 | -0.22191 | -0.14377 | -0.18138 | -0.083497 | 0.012858 | -0.085749 | 0.095628 | -0.006468 | -0.09026 | 123.067 | 122.8707 | 122.9489 | 66.8258 | -123.1699 | 123.0092 | 123.0862 | 123.0024 | 66.8201 | -123.274
92.2812 | 123.4039 | -66.7923 | 56.3004 | 0.087637 | -0.0064313 | -0.0011099 | 0.055523 | -0.00085916 | 0.054329 | 0.058893 | -0.0029117 | 0.00084833 | 0.062391 | 0.0041163 | 0.06413 | -64.6092 | 0.015142 | -66.7689 | 56.261 | 56.0693 | 56.1383 | -66.8604 | -66.7932 | 0.014095 | -66.8964 | 56.2031 | 56.2802 | 56.2009 | -66.992 | -0.068111 | -0.039359 | 2.1831 | 0.023401 | 0.091512 | -0.23106 | -0.16208 | -0.19969 | -0.09723 | -0.000875 | -0.10406 | 0.095628 | -0.020201 | -0.099415 | 123.0533 | 122.8616 | 122.9306 | 66.8074 | -123.1608 | 122.9954 | 123.0725 | 122.9932 | 66.8064 | -123.2923
93.2812 | 123.4222 | -66.7831 | 56.3095 | 0.057113 | -0.0064313 | -4.1882e-05 | 0.055523 | -0.0029952 | 0.054329 | 0.089415 | -0.0018437 | -0.0023567 | 0.062391 | 0.0030483 | 0.06413 | -64.5817 | 0.028878 | -66.7689 | 56.2564 | 56.0647 | 56.1474 | -66.8696 | -66.8023 | 0.014095 | -66.9009 | 56.2031 | 56.2847 | 56.178 | -66.9828 | -0.086424 | -0.053092 | 2.2014 | 0.014246 | 0.10067 | -0.2448 | -0.16208 | -0.19969 | -0.10638 | -0.019187 | -0.11779 | 0.081892 | -0.024778 | -0.13146 | 123.0396 | 122.8479 | 122.9306 | 66.812 | -123.1791 | 122.9863 | 123.0679 | 122.9612 | 66.7972 | -123.2923
94.2812 | 123.2758 | -66.8198 | 56.3782 | 0.057113 | -0.0074993 | -0.0021789 | 0.05766 | -0.0040642 | 0.05326 | 0.074154 | -0.0018437 | -0.0034247 | 0.06346 | 0.0041163 | 0.063061 | -64.5405 | 0.019721 | -66.7735 | 56.2518 | 56.0693 | 56.1429 | -66.8696 | -66.8023 | 0.009516 | -66.8918 | 56.1985 | 56.2802 | 56.178 | -66.992 | -0.049803 | -0.12634 | 2.2793 | 0.046289 | 0.096092 | -0.30888 | -0.23532 | -0.17222 | -0.17963 | 0.017434 | -0.072016 | 0.10021 | -0.098021 | -0.20013 | 123.0716 | 122.8891 | 122.9626 | 66.8395 | -123.2477 | 123.0183 | 123.0999 | 122.9978 | 66.8293 | -123.3702
95.2812 | 123.3719 | -66.806 | 56.3049 | 0.057113 | -0.0064313 | -0.0011099 | 0.055523 | -0.0019272 | 0.05326 | 0.074154 | -0.00077468 | -0.0012887 | 0.062391 | 0.0041163 | 0.06413 | -64.5634 | 0.019721 | -66.7826 | 56.2564 | 56.0647 | 56.1474 | -66.8879 | -66.7977 | 0.018674 | -66.8964 | 56.2031 | 56.2893 | 56.1735 | -66.992 | -0.081852 | -0.048515 | 2.2427 | 0.023399 | 0.10525 | -0.24022 | -0.1575 | -0.18596 | -0.10181 | 0.00828 | -0.090328 | 0.095628 | -0.015622 | -0.13146 | 123.0624 | 122.8707 | 122.9535 | 66.8258 | -123.1928 | 123.0092 | 123.0953 | 122.9795 | 66.8247 | -123.2969
96.2812 | 123.3673 | -66.8152 | 56.3004 | 0.041851 | -0.0064313 | -0.0011099 | 0.056591 | -0.0029952 | 0.055397 | 0.074154 | -0.0018437 | -0.0023567 | 0.062391 | 0.0030483 | 0.06413 | -64.5634 | 0.0243 | -66.7735 | 56.2518 | 56.0647 | 56.1429 | -66.8833 | -66.7977 | 0.004938 | -66.8918 | 56.194 | 56.2847 | 56.1826 | -66.9828 | -0.068117 | -0.048515 | 2.2518 | 0.041712 | 0.10983 | -0.23564 | -0.1575 | -0.16764 | -0.10639 | 0.017436 | -0.076593 | 0.091049 | -0.015623 | -0.11773 | 123.067 | 122.8799 | 122.958 | 66.8395 | -123.1837 | 123.0092 | 123.0999 | 122.9978 | 66.8201 | -123.2832
97.2812 | 123.4085 | -66.7923 | 56.3187 | 0.041851 | -0.0064313 | -0.0021789 | 0.055523 | -0.0019272 | 0.05326 | 0.074154 | -0.0039797 | -0.0023567 | 0.06346 | 0.0041163 | 0.063061 | -64.6 | 0.019721 | -66.7781 | 56.2564 | 56.0556 | 56.1474 | -66.8696 | -66.8069 | 0.009516 | -66.8964 | 56.2031 | 56.2847 | 56.1826 | -66.992 | -0.077269 | -0.062248 | 2.1923 | 0.014244 | 0.091513 | -0.26311 | -0.17123 | -0.19969 | -0.11554 | -0.014611 | -0.10406 | 0.095628 | -0.033934 | -0.13604 | 123.0487 | 122.8479 | 122.9397 | 66.812 | -123.1882 | 122.9954 | 123.077 | 122.9749 | 66.8018 | -123.3107
98.2812 | 123.3673 | -66.7877 | 56.3232 | 0.087637 | -0.0074993 | -0.0021789 | 0.055523 | -0.0051322 | 0.05326 | 0.089415 | -0.00077468 | -0.0012887 | 0.061323 | 0.0041163 | 0.061993 | -64.5588 | 0.015142 | -66.7826 | 56.261 | 56.0647 | 56.1429 | -66.8833 | -66.8023 | 0.014095 | -66.8918 | 56.2031 | 56.2847 | 56.178 | -66.992 | -0.095583 | -0.062247 | 2.2289 | 0.005089 | 0.10067 | -0.25853 | -0.18039 | -0.20427 | -0.12012 | -0.014609 | -0.10406 | 0.10021 | -0.038511 | -0.1452 | 123.0487 | 122.8524 | 122.9306 | 66.8029 | -123.2065 | 122.9908 | 123.0725 | 122.9658 | 66.8018 | -123.3152
99.2812 | 123.2895 | -66.8518 | 56.3324 | 0.041851 | -0.0074993 | -0.0011099 | 0.055523 | -0.0029952 | 0.054329 | 0.074154 | -0.0029117 | -0.0012887 | 0.061323 | 0.0041163 | 0.06413 | -64.5405 | 0.019721 | -66.7781 | 56.2564 | 56.0647 | 56.1429 | -66.8696 | -66.7977 | 0.023253 | -66.9009 | 56.1985 | 56.2802 | 56.1735 | -66.9874 | -0.017759 | -0.07598 | 2.3113 | 0.073754 | 0.091513 | -0.26769 | -0.18954 | -0.1356 | -0.13385 | 0.054057 | -0.049129 | 0.086471 | -0.052244 | -0.15893 | 123.1082 | 122.9165 | 122.9947 | 66.8715 | -123.202 | 123.0504 | 123.132 | 123.0253 | 66.8751 | -123.3198
100.2812 | 123.317 | -66.8289 | 56.3095 | 0.057113 | -0.0074993 | -0.0032469 | 0.05766 | -0.0040642 | 0.055397 | 0.089415 | -0.0018437 | -0.0023567 | 0.061323 | 0.0041163 | 0.063061 | -64.5496 | 0.019721 | -66.7781 | 56.2656 | 56.0601 | 56.1474 | -66.8879 | -66.7977 | 0.018674 | -66.8918 | 56.2031 | 56.2847 | 56.1964 | -66.9828 | -0.058964 | -0.043935 | 2.2793 | 0.050865 | 0.10983 | -0.24938 | -0.16208 | -0.15391 | -0.10638 | 0.031168 | -0.062861 | 0.091049 | -0.024778 | -0.11315 | 123.0945 | 122.889 | 122.9763 | 66.8486 | -123.1974 | 123.032 | 123.1136 | 123.0253 | 66.8476 | -123.2923
101.2812 | 123.3078 | -66.8381 | 56.3324 | 0.057113 | -0.0064313 | -0.0011099 | 0.054455 | -0.0019272 | 0.054329 | 0.043632 | -0.0029117 | -0.00021967 | 0.061323 | 0.0051843 | 0.063061 | -64.5496 | 0.0243 | -66.7872 | 56.2656 | 56.0693 | 56.1429 | -66.8741 | -66.7977 | 0.014095 | -66.8918 | 56.2031 | 56.2847 | 56.1918 | -66.992 | -0.036071 | -0.066823 | 2.2884 | 0.050865 | 0.086936 | -0.26311 | -0.18954 | -0.15391 | -0.12927 | 0.040324 | -0.053705 | 0.10021 | -0.047666 | -0.14061 | 123.1036 | 122.9074 | 122.9809 | 66.8624 | -123.2065 | 123.0412 | 123.1228 | 123.0299 | 66.8522 | -123.3244
102.2812 | 123.2712 | -66.8381 | 56.3507 | 0.072375 | -0.0074993 | -0.0011099 | 0.055523 | -0.0019272 | 0.054329 | 0.074154 | -0.00077468 | -0.0012887 | 0.06346 | 0.0041163 | 0.063061 | -64.5405 | 0.010564 | -66.7918 | 56.2564 | 56.0739 | 56.152 | -66.8741 | -66.8069 | 0.023253 | -66.8918 | 56.2031 | 56.2847 | 56.1918 | -66.992 | -0.036071 | -0.094291 | 2.2976 | 0.046286 | 0.082357 | -0.27684 | -0.1987 | -0.15391 | -0.14758 | 0.031166 | -0.053705 | 0.10021 | -0.065977 | -0.15893 | 123.0945 | 122.9119 | 122.9901 | 66.8486 | -123.2249 | 123.0412 | 123.1228 | 123.0299 | 66.8613 | -123.3427
103.2812 | 123.2437 | -66.8655 | 56.3324 | 0.057113 | -0.0074993 | -0.0011099 | 0.055523 | -0.0040642 | 0.054329 | 0.074154 | -0.00077468 | -0.0012887 | 0.062391 | 0.0041163 | 0.061993 | -64.5268 | 0.015142 | -66.7781 | 56.261 | 56.0739 | 56.1474 | -66.8925 | -66.7977 | 0.014095 | -66.8964 | 56.1894 | 56.2847 | 56.2009 | -66.9874 | -0.026921 | -0.071402 | 2.3388 | 0.087487 | 0.11441 | -0.25853 | -0.18496 | -0.12187 | -0.14301 | 0.06779 | -0.030818 | 0.091049 | -0.047666 | -0.13146 | 123.1265 | 122.9394 | 123.013 | 66.8807 | -123.2249 | 123.0549 | 123.1503 | 123.0665 | 66.8796 | -123.3198
104.2812 | 123.2391 | -66.8518 | 56.3278 | 0.072375 | -0.0074993 | -0.0011099 | 0.056591 | -0.0019272 | 0.056465 | 0.058893 | -0.0018437 | -0.0023567 | 0.062391 | 0.0051843 | 0.061993 | -64.5405 | 0.0243 | -66.7735 | 56.2656 | 56.0739 | 56.152 | -66.8833 | -66.7977 | 0.018674 | -66.8918 | 56.1985 | 56.2847 | 56.1872 | -66.992 | -0.031496 | -0.062246 | 2.3113 | 0.078333 | 0.10983 | -0.25395 | -0.17581 | -0.14018 | -0.12927 | 0.054057 | -0.039972 | 0.10021 | -0.043089 | -0.14062 | 123.1174 | 122.9257 | 123.0038 | 66.8761 | -123.2111 | 123.0504 | 123.1365 | 123.039 | 66.8705 | -123.3198
105.2812 | 123.2666 | -66.8289 | 56.3187 | 0.041851 | -0.0064313 | 0.0010261 | 0.055523 | -0.0019272 | 0.054329 | 0.043632 | -0.0018437 | -0.0023567 | 0.062391 | 0.0051843 | 0.063061 | -64.5451 | 0.0243 | -66.7735 | 56.2564 | 56.0739 | 56.1474 | -66.8741 | -66.7977 | 0.014095 | -66.8964 | 56.1985 | 56.2847 | 56.1964 | -66.9874 | -0.045227 | -0.062248 | 2.2839 | 0.055444 | 0.10067 | -0.2448 | -0.17123 | -0.15849 | -0.12012 | 0.031168 | -0.06744 | 0.091049 | -0.033934 | -0.1223 | 123.0853 | 122.9028 | 122.9763 | 66.8532 | -123.1928 | 123.0275 | 123.1136 | 123.0253 | 66.843 | -123.3061
106.2812 | 123.2986 | -66.8289 | 56.3141 | 0.041851 | -0.0064313 | -0.0011099 | 0.055523 | -0.00085916 | 0.055397 | 0.058893 | -0.00077468 | -0.00021967 | 0.062391 | 0.0041163 | 0.06413 | -64.5496 | 0.015142 | -66.7826 | 56.261 | 56.083 | 56.1474 | -66.8787 | -66.784 | 0.009516 | -66.8918 | 56.2031 | 56.2847 | 56.1964 | -66.9874 | -0.049806 | -0.053092 | 2.2793 | 0.046287 | 0.096093 | -0.23106 | -0.16665 | -0.15849 | -0.11096 | 0.044904 | -0.062861 | 0.095628 | -0.029356 | -0.11773 | 123.0899 | 122.9119 | 122.9763 | 66.8441 | -123.1928 | 123.032 | 123.1136 | 123.0253 | 66.8384 | -123.3015
107.2969 | 123.2895 | -66.8381 | 56.3278 | 0.057113 | -0.0085683 | -0.0011099 | 0.056591 | -0.0019272 | 0.055397 | 0.074154 | -0.0018437 | -0.0023567 | 0.062391 | 0.0051843 | 0.06413 | -64.5359 | 0.019721 | -66.7689 | 56.261 | 56.083 | 56.152 | -66.8833 | -66.7977 | 0.018674 | -66.8872 | 56.194 | 56.2802 | 56.2055 | -66.9874 | -0.045229 | -0.066825 | 2.3022 | 0.069178 | 0.11441 | -0.24479 | -0.17581 | -0.14933 | -0.13385 | 0.040324 | -0.049126 | 0.10021 | -0.047667 | -0.1223 | 123.0991 | 122.9211 | 122.9901 | 66.8578 | -123.2111 | 123.032 | 123.1182 | 123.0436 | 66.8567 | -123.3152
108.2812 | 123.3307 | -66.8015 | 56.3004 | 0.057113 | -0.0053623 | -0.0011099 | 0.055523 | -0.00085916 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.064528 | 0.0062533 | 0.06413 | -64.6137 | 0.0243 | -66.7735 | 56.2656 | 56.083 | 56.1429 | -66.8741 | -66.7932 | 0.014095 | -66.8964 | 56.1985 | 56.2939 | 56.2055 | -66.992 | -0.072692 | -0.03478 | 2.1877 | 0.027979 | 0.10067 | -0.21733 | -0.1575 | -0.19053 | -0.10181 | 0.008281 | -0.094905 | 0.095628 | -0.006465 | -0.094836 | 123.067 | 122.8845 | 122.9443 | 66.8258 | -123.1745 | 123 | 123.0953 | 123.007 | 66.8155 | -123.2923
109.2812 | 123.2941 | -66.8243 | 56.3507 | 0.057113 | -0.0064313 | -0.0021789 | 0.055523 | -0.00085916 | 0.055397 | 0.074154 | -0.0018437 | 0.00084833 | 0.06346 | 0.0073213 | 0.063061 | -64.5359 | 0.019721 | -66.7781 | 56.261 | 56.0876 | 56.1474 | -66.8787 | -66.7932 | 0.023253 | -66.8964 | 56.2077 | 56.2939 | 56.2055 | -66.992 | -0.054383 | -0.089713 | 2.2884 | 0.046288 | 0.10067 | -0.2631 | -0.20328 | -0.16764 | -0.14301 | 0.031169 | -0.072017 | 0.095628 | -0.056819 | -0.14519 | 123.0853 | 122.9119 | 122.9718 | 66.8441 | -123.2294 | 123.032 | 123.1182 | 123.0299 | 66.8476 | -123.3427
110.2812 | 123.2529 | -66.8243 | 56.3461 | 0.057113 | -0.0053623 | -0.0011099 | 0.056591 | -0.00085916 | 0.056465 | 0.074154 | -0.00077468 | 0.00084833 | 0.064528 | 0.0030483 | 0.060925 | -64.5451 | 0.019721 | -66.7781 | 56.2702 | 56.0968 | 56.152 | -66.865 | -66.7977 | 0.023253 | -66.8918 | 56.194 | 56.2802 | 56.1689 | -66.992 | -0.040646 | -0.075978 | 2.2793 | 0.046288 | 0.086934 | -0.24937 | -0.19412 | -0.16764 | -0.15216 | 0.026591 | -0.067438 | 0.10021 | -0.065977 | -0.17724 | 123.0945 | 122.9211 | 122.9764 | 66.8441 | -123.2111 | 123.0183 | 123.1045 | 122.9932 | 66.8476 | -123.3381
111.2812 | 123.2895 | -66.8793 | 56.3644 | 0.057113 | -0.0064313 | -4.1882e-05 | 0.055523 | -0.00085916 | 0.055397 | 0.058893 | -0.0018437 | -0.00021967 | 0.064528 | 0.0051843 | 0.061993 | -64.5588 | 0.0243 | -66.7735 | 56.2702 | 56.083 | 56.1474 | -66.8925 | -66.7932 | 0.023253 | -66.8964 | 56.2077 | 56.2847 | 56.146 | -66.9966 | -0.013189 | -0.094289 | 2.3205 | 0.1058 | 0.11899 | -0.28141 | -0.21701 | -0.11729 | -0.15674 | 0.0861 | -0.017086 | 0.10021 | -0.07971 | -0.21845 | 123.1494 | 122.9623 | 123.0267 | 66.9036 | -123.2569 | 123.087 | 123.164 | 123.0253 | 66.9025 | -123.361
112.2969 | 123.2574 | -66.806 | 56.3736 | 0.072375 | -0.0085683 | 0.0010261 | 0.055523 | -0.0019272 | 0.057534 | 0.058893 | -0.00077468 | -0.00021967 | 0.064528 | 0.0051843 | 0.063061 | -64.5542 | 0.019721 | -66.7781 | 56.2656 | 56.0968 | 56.152 | -66.8787 | -66.7932 | 0.014095 | -66.8964 | 56.2077 | 56.2802 | 56.1277 | -67.0011 | -0.072694 | -0.10802 | 2.2518 | 0.027977 | 0.10067 | -0.27683 | -0.22158 | -0.19511 | -0.16589 | 0.012858 | -0.090328 | 0.10478 | -0.093443 | -0.24591 | 123.0716 | 122.9028 | 122.958 | 66.8258 | -123.2523 | 123.0137 | 123.0862 | 122.9337 | 66.8201 | -123.3747
113.2812 | 123.2803 | -66.8243 | 56.3507 | 0.026589 | -0.0085683 | -4.1882e-05 | 0.054455 | -0.0019272 | 0.055397 | 0.043632 | -0.0018437 | -0.0023567 | 0.06346 | 0.0062533 | 0.063061 | -64.5496 | 0.019721 | -66.7735 | 56.2656 | 56.0968 | 56.1566 | -66.8558 | -66.7932 | 0.014095 | -66.8964 | 56.194 | 56.2847 | 56.0865 | -66.992 | -0.031489 | -0.085134 | 2.2747 | 0.050867 | 0.082356 | -0.25394 | -0.19412 | -0.16764 | -0.15674 | 0.031169 | -0.072017 | 0.095628 | -0.065977 | -0.26423 | 123.0899 | 122.9211 | 122.9809 | 66.8441 | -123.2065 | 123.0183 | 123.1091 | 122.9108 | 66.8384 | -123.3427
114.2812 | 123.262 | -66.8243 | 56.3507 | 0.087637 | -0.0085683 | -4.1882e-05 | 0.055523 | -0.0019272 | 0.056465 | 0.043632 | -0.00077468 | -0.00021967 | 0.06346 | 0.0062533 | 0.061993 | -64.5634 | 0.0243 | -66.7781 | 56.261 | 56.0968 | 56.152 | -66.8741 | -66.784 | 0.018674 | -66.8918 | 56.1985 | 56.2847 | 56.0727 | -66.9966 | -0.049804 | -0.089713 | 2.261 | 0.046288 | 0.096092 | -0.25394 | -0.1987 | -0.17222 | -0.15216 | 0.040327 | -0.067438 | 0.10479 | -0.065977 | -0.27797 | 123.0853 | 122.9211 | 122.9764 | 66.8486 | -123.2249 | 123.0229 | 123.1091 | 122.8971 | 66.843 | -123.3473
115.2812 | 123.2483 | -66.8518 | 56.3461 | 0.057113 | -0.0064313 | -0.0011099 | 0.055523 | -0.0019272 | 0.055397 | 0.058893 | -0.0029117 | -0.0012887 | 0.06346 | 0.0073213 | 0.063061 | -64.5817 | 0.0243 | -66.7781 | 56.2702 | 56.1013 | 56.152 | -66.8741 | -66.784 | 0.023253 | -66.8918 | 56.2077 | 56.2847 | 56.0956 | -66.9874 | -0.022338 | -0.075978 | 2.2701 | 0.073754 | 0.096092 | -0.24479 | -0.19412 | -0.1356 | -0.13843 | 0.067793 | -0.039972 | 0.095628 | -0.061399 | -0.2505 | 123.122 | 122.9531 | 123.0038 | 66.8761 | -123.2203 | 123.0595 | 123.1365 | 122.9474 | 66.8751 | -123.3335
116.2812 | 123.2986 | -66.8015 | 56.3599 | 0.072375 | -0.0074993 | -0.0011099 | 0.055523 | -0.0019272 | 0.054329 | 0.058893 | -0.00077468 | -0.0012887 | 0.06346 | 0.0041163 | 0.061993 | -64.5725 | 0.015142 | -66.7781 | 56.2656 | 56.1013 | 56.1612 | -66.8696 | -66.7932 | 0.023253 | -66.8872 | 56.1985 | 56.2939 | 56.0682 | -66.992 | -0.068113 | -0.094289 | 2.2289 | 0.0234 | 0.091513 | -0.25852 | -0.19869 | -0.19053 | -0.16132 | 0.008281 | -0.085747 | 0.10479 | -0.065974 | -0.2917 | 123.067 | 122.9028 | 122.9626 | 66.8166 | -123.2294 | 123 | 123.0953 | 122.8696 | 66.8247 | -123.3518
117.2969 | 123.3948 | -66.7694 | 56.3095 | 0.072375 | -0.0074993 | -0.0011099 | 0.054455 | -0.0029952 | 0.057534 | 0.058893 | -0.00077468 | -0.00021967 | 0.064528 | 0.0062533 | 0.063061 | -64.6321 | 0.0243 | -66.7689 | 56.2564 | 56.0968 | 56.152 | -66.8696 | -66.7932 | 0.014095 | -66.8918 | 56.1985 | 56.2939 | 56.0819 | -66.992 | -0.10016 | -0.053092 | 2.1374 | 0.000513 | 0.10067 | -0.21274 | -0.1575 | -0.22258 | -0.11096 | -0.023763 | -0.12237 | 0.10021 | -0.01562 | -0.22761 | 123.0258 | 122.8662 | 122.9214 | 66.7937 | -123.1791 | 122.968 | 123.0633 | 122.8513 | 66.7835 | -123.3015
118.2812 | 123.317 | -66.8152 | 56.3278 | 0.041851 | -0.0096363 | 0.0010261 | 0.05766 | -0.0019272 | 0.054329 | 0.058893 | 0.00029332 | -0.0012887 | 0.06346 | 0.0051843 | 0.063061 | -64.568 | 0.019721 | -66.7689 | 56.261 | 56.1059 | 56.152 | -66.8741 | -66.8023 | 0.014095 | -66.8964 | 56.1985 | 56.2939 | 56.059 | -66.9966 | -0.058959 | -0.066825 | 2.2472 | 0.04629 | 0.10525 | -0.2219 | -0.17581 | -0.18138 | -0.12927 | 0.012857 | -0.081172 | 0.10021 | -0.033931 | -0.26882 | 123.0762 | 122.9211 | 122.9672 | 66.8349 | -123.202 | 123.0137 | 123.1091 | 122.8742 | 66.8293 | -123.3244
119.2812 | 123.3032 | -66.8152 | 56.3416 | 0.057113 | -0.0085683 | -4.1882e-05 | 0.054455 | -0.0019272 | 0.055397 | 0.058893 | 0.00029332 | -0.00021967 | 0.062391 | 0.0062533 | 0.06413 | -64.568 | 0.0243 | -66.7735 | 56.261 | 56.1013 | 56.1566 | -66.8833 | -66.7932 | 0.023253 | -66.8964 | 56.1985 | 56.2893 | 56.0819 | -66.9874 | -0.068117 | -0.080558 | 2.2472 | 0.041712 | 0.10983 | -0.24021 | -0.18496 | -0.17222 | -0.14301 | 0.022014 | -0.081172 | 0.091049 | -0.052243 | -0.25966 | 123.0762 | 122.9165 | 122.9718 | 66.8395 | -123.2249 | 123.0137 | 123.1045 | 122.8971 | 66.8384 | -123.329
120.2812 | 123.2666 | -66.806 | 56.3599 | 0.057113 | -0.0085683 | -4.1882e-05 | 0.054455 | -0.0029952 | 0.054329 | 0.043632 | -0.00077468 | -0.00021967 | 0.06346 | 0.0051843 | 0.063061 | -64.5725 | 0.019721 | -66.7781 | 56.2656 | 56.0922 | 56.152 | -66.8741 | -66.7932 | 0.014095 | -66.8964 | 56.2077 | 56.2847 | 56.1048 | -66.992 | -0.068115 | -0.094289 | 2.2335 | 0.027977 | 0.096092 | -0.26768 | -0.20785 | -0.18596 | -0.15216 | 0.012858 | -0.090328 | 0.095628 | -0.075132 | -0.25507 | 123.0716 | 122.8982 | 122.958 | 66.8258 | -123.234 | 123.0137 | 123.0908 | 122.9108 | 66.8201 | -123.3518
121.2812 | 123.2941 | -66.7969 | 56.3416 | 0.057113 | -0.0096363 | -0.0021789 | 0.053386 | -0.0019272 | 0.054329 | 0.058893 | -0.0018437 | -0.00021967 | 0.064528 | 0.0073213 | 0.061993 | -64.5268 | 0.019721 | -66.7781 | 56.2656 | 56.1059 | 56.1566 | -66.8879 | -66.7932 | 0.018674 | -66.8918 | 56.1985 | 56.2847 | 56.0773 | -66.9874 | -0.091007 | -0.075979 | 2.2701 | 0.018822 | 0.10983 | -0.23563 | -0.18496 | -0.19053 | -0.14301 | 0.003703 | -0.094904 | 0.095628 | -0.056822 | -0.26424 | 123.0624 | 122.9028 | 122.9535 | 66.8166 | -123.2294 | 122.9954 | 123.0816 | 122.8742 | 66.8155 | -123.329
122.2969 | 123.3719 | -66.7603 | 56.3507 | 0.026589 | -0.0064313 | -0.0011099 | 0.054455 | -0.00085916 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.06346 | 0.0062533 | 0.061993 | -64.5771 | 0.015142 | -66.7735 | 56.261 | 56.1013 | 56.1429 | -66.8741 | -66.7932 | 0.018674 | -66.8964 | 56.1985 | 56.2802 | 56.1185 | -66.992 | -0.11389 | -0.089713 | 2.1831 | -0.01322 | 0.10067 | -0.24937 | -0.20785 | -0.23173 | -0.15216 | -0.032918 | -0.1361 | 0.095628 | -0.070555 | -0.23218 | 123.0212 | 122.8616 | 122.9031 | 66.7754 | -123.2249 | 122.9588 | 123.0404 | 122.8788 | 66.7789 | -123.3427
123.2812 | 123.2986 | -66.8335 | 56.3416 | 0.057113 | -0.0074993 | -0.0011099 | 0.056591 | -0.0019272 | 0.056465 | 0.043632 | -0.0018437 | -0.0012887 | 0.064528 | 0.0062533 | 0.061993 | -64.5313 | 0.019721 | -66.7689 | 56.261 | 56.1013 | 56.1474 | -66.8879 | -66.7932 | 0.014095 | -66.8964 | 56.2123 | 56.2847 | 56.0727 | -66.9874 | -0.054386 | -0.080558 | 2.3022 | 0.0646 | 0.11899 | -0.24021 | -0.19412 | -0.15391 | -0.12927 | 0.040324 | -0.062862 | 0.091049 | -0.056822 | -0.26881 | 123.0945 | 122.9348 | 122.9809 | 66.8532 | -123.2294 | 123.0458 | 123.1182 | 122.9062 | 66.8476 | -123.329
124.2812 | 123.2895 | -66.8427 | 56.3873 | 0.072375 | -0.0074993 | -0.0032469 | 0.055523 | -0.0019272 | 0.054329 | 0.089415 | -0.0029117 | -0.0012887 | 0.062391 | 0.0073213 | 0.063061 | -64.5496 | 0.019721 | -66.7689 | 56.2656 | 56.1059 | 56.1474 | -66.8558 | -66.7886 | 0.014095 | -66.8964 | 56.2031 | 56.2847 | 56.0911 | -66.992 | -0.013179 | -0.12176 | 2.293 | 0.073755 | 0.086934 | -0.28141 | -0.2399 | -0.14933 | -0.1842 | 0.054058 | -0.053707 | 0.095628 | -0.1026 | -0.29628 | 123.1082 | 122.9486 | 122.9901 | 66.8624 | -123.2432 | 123.0458 | 123.1274 | 122.9337 | 66.8567 | -123.3793
125.2812 | 123.2758 | -66.8152 | 56.3644 | 0.072375 | -0.0096363 | -0.0011099 | 0.053386 | -0.00085916 | 0.056465 | 0.058893 | -0.00077468 | -0.0012887 | 0.06346 | 0.0073213 | 0.063061 | -64.5451 | 0.0243 | -66.7781 | 56.2656 | 56.1059 | 56.1566 | -66.8558 | -66.784 | 0.018674 | -66.8918 | 56.2031 | 56.2847 | 56.1139 | -66.992 | -0.040644 | -0.098867 | 2.2701 | 0.037133 | 0.077777 | -0.25852 | -0.20785 | -0.1768 | -0.16132 | 0.031172 | -0.076593 | 0.10021 | -0.07971 | -0.2505 | 123.0808 | 122.9211 | 122.9718 | 66.8395 | -123.2203 | 123.0183 | 123.0999 | 122.9291 | 66.8339 | -123.3564
126.2812 | 123.2803 | -66.8335 | 56.3553 | 0.041851 | -0.0096363 | -4.1882e-05 | 0.054455 | -0.0019272 | 0.055397 | 0.058893 | -0.00077468 | -0.0012887 | 0.061323 | 0.0073213 | 0.06413 | -64.5313 | 0.019721 | -66.7735 | 56.2564 | 56.1059 | 56.1566 | -66.8604 | -66.7932 | 0.014095 | -66.8964 | 56.2031 | 56.2939 | 56.1323 | -66.9966 | -0.026912 | -0.098869 | 2.3022 | 0.060022 | 0.086934 | -0.24936 | -0.1987 | -0.16307 | -0.15216 | 0.040324 | -0.062862 | 0.10021 | -0.061397 | -0.22303 | 123.0899 | 122.9394 | 122.9901 | 66.8532 | -123.2157 | 123.0366 | 123.1274 | 122.9658 | 66.8476 | -123.3519
127.2812 | 123.2666 | -66.8564 | 56.3187 | 0.041851 | -0.0085683 | -0.0011099 | 0.054455 | -0.0019272 | 0.057534 | 0.074154 | -0.0018437 | 0.00084833 | 0.06346 | 0.0062533 | 0.061993 | -64.6 | 0.0243 | -66.7735 | 56.2656 | 56.1013 | 56.1474 | -66.865 | -66.7977 | 0.018674 | -66.8826 | 56.1985 | 56.2893 | 56.0727 | -66.9966 | -0.008603 | -0.053091 | 2.2564 | 0.08291 | 0.091513 | -0.21732 | -0.17123 | -0.14018 | -0.12012 | 0.058634 | -0.026237 | 0.11394 | -0.029355 | -0.24593 | 123.122 | 122.9577 | 123.0038 | 66.8807 | -123.1837 | 123.0549 | 123.1457 | 122.9291 | 66.8751 | -123.3152
128.2812 | 123.3124 | -66.8106 | 56.3507 | 0.072375 | -0.0085683 | -4.1882e-05 | 0.053386 | -0.0019272 | 0.055397 | 0.089415 | -0.00077468 | -0.00021967 | 0.06346 | 0.0073213 | 0.061993 | -64.568 | 0.019721 | -66.7826 | 56.2656 | 56.1013 | 56.1566 | -66.8741 | -66.7977 | 0.023253 | -66.8918 | 56.1985 | 56.2939 | 56.1506 | -66.992 | -0.063537 | -0.085134 | 2.2427 | 0.027977 | 0.091514 | -0.24937 | -0.19412 | -0.18138 | -0.15216 | 0.012858 | -0.081171 | 0.10021 | -0.056819 | -0.20013 | 123.0762 | 122.912 | 122.9672 | 66.8303 | -123.2249 | 123.0092 | 123.1045 | 122.9612 | 66.8339 | -123.3427
129.2812 | 123.2941 | -66.8335 | 56.3736 | 0.057113 | -0.0074993 | -4.1882e-05 | 0.054455 | -0.00085916 | 0.056465 | 0.074154 | -0.00077468 | -0.00021967 | 0.065596 | 0.0073213 | 0.061993 | -64.5954 | 0.015142 | -66.7689 | 56.2702 | 56.1013 | 56.152 | -66.8833 | -66.7932 | 0.004938 | -66.8918 | 56.2031 | 56.2893 | 56.1048 | -66.9966 | -0.049807 | -0.10344 | 2.2381 | 0.0646 | 0.11441 | -0.27225 | -0.22158 | -0.16307 | -0.17047 | 0.040324 | -0.058283 | 0.10479 | -0.084286 | -0.26881 | 123.1036 | 122.9348 | 122.9855 | 66.8486 | -123.2569 | 123.0366 | 123.1228 | 122.9383 | 66.8384 | -123.3702
130.2812 | 123.349 | -66.7786 | 56.3324 | 0.041851 | -0.0085683 | -0.0021789 | 0.055523 | -0.0019272 | 0.055397 | 0.089415 | -0.00077468 | -0.0012887 | 0.06346 | 0.0083893 | 0.061993 | -64.6092 | 0.028878 | -66.7689 | 56.261 | 56.1105 | 56.152 | -66.8833 | -66.7886 | 0.014095 | -66.8918 | 56.2031 | 56.2893 | 56.0865 | -66.9966 | -0.10474 | -0.071402 | 2.1694 | 0.009668 | 0.11441 | -0.2219 | -0.18039 | -0.218 | -0.12927 | -0.010029 | -0.11321 | 0.10479 | -0.043087 | -0.24592 | 123.0396 | 122.8891 | 122.9306 | 66.8074 | -123.2157 | 122.9817 | 123.0679 | 122.865 | 66.7927 | -123.329
131.2812 | 123.3124 | -66.7877 | 56.3461 | 0.087637 | -0.0085683 | -0.0011099 | 0.056591 | -0.0029952 | 0.056465 | 0.028371 | -0.00077468 | -0.00021967 | 0.064528 | 0.0073213 | 0.061993 | -64.5954 | 0.019721 | -66.7689 | 56.261 | 56.0968 | 56.1474 | -66.865 | -66.7932 | 0.009516 | -66.8872 | 56.1985 | 56.2802 | 56.1323 | -66.9874 | -0.077267 | -0.085135 | 2.1923 | 0.018824 | 0.096091 | -0.24937 | -0.1987 | -0.19969 | -0.14758 | -0.005452 | -0.09948 | 0.10021 | -0.065977 | -0.21387 | 123.0487 | 122.8845 | 122.9352 | 66.8074 | -123.2111 | 122.9863 | 123.0679 | 122.92 | 66.7972 | -123.3335
132.2812 | 123.3582 | -66.8015 | 56.369 | 0.026589 | -0.0085683 | -0.0011099 | 0.054455 | -0.0029952 | 0.052192 | 0.058893 | -0.00077468 | -0.0012887 | 0.064528 | 0.0083893 | 0.061993 | -64.568 | 0.0243 | -66.7689 | 56.2656 | 56.1059 | 56.152 | -66.8787 | -66.7977 | 0.014095 | -66.8964 | 56.2031 | 56.2939 | 56.1002 | -66.992 | -0.077271 | -0.10345 | 2.2335 | 0.032557 | 0.10983 | -0.2631 | -0.21701 | -0.19053 | -0.16589 | 0.003703 | -0.094905 | 0.095628 | -0.07513 | -0.26881 | 123.067 | 122.9074 | 122.9535 | 66.8258 | -123.2477 | 123.0046 | 123.0953 | 122.9017 | 66.8155 | -123.361
133.2812 | 123.3719 | -66.7648 | 56.337 | 0.087637 | -0.010704 | -0.0021789 | 0.055523 | -0.0019272 | 0.055397 | 0.089415 | -0.0018437 | -0.0023567 | 0.06346 | 0.0083893 | 0.063061 | -64.6137 | 0.019721 | -66.7689 | 56.2656 | 56.1059 | 56.1474 | -66.8696 | -66.7932 | 0.014095 | -66.8918 | 56.1985 | 56.2893 | 56.1185 | -66.992 | -0.10473 | -0.071401 | 2.1511 | -0.004064 | 0.10067 | -0.23105 | -0.18954 | -0.22715 | -0.13843 | -0.02834 | -0.12695 | 0.10021 | -0.047665 | -0.21845 | 123.0304 | 122.8708 | 122.9123 | 66.7846 | -123.2065 | 122.9634 | 123.0541 | 122.8834 | 66.7789 | -123.329
134.2812 | 123.3261 | -66.7831 | 56.3553 | 0.072375 | -0.0096363 | -0.0021789 | 0.053386 | -0.0029952 | 0.056465 | 0.058893 | -0.00077468 | -0.0023567 | 0.062391 | 0.0073213 | 0.063061 | -64.6046 | 0.019721 | -66.7735 | 56.261 | 56.1013 | 56.1566 | -66.8787 | -66.7932 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.1002 | -66.992 | -0.095582 | -0.094291 | 2.1786 | 0.009668 | 0.10525 | -0.25394 | -0.1987 | -0.20884 | -0.15216 | -0.01003 | -0.10406 | 0.10479 | -0.061397 | -0.25508 | 123.0441 | 122.8845 | 122.9397 | 66.8029 | -123.234 | 122.9863 | 123.077 | 122.8834 | 66.7972 | -123.3473
135.2812 | 123.2941 | -66.806 | 56.3782 | 0.072375 | -0.010704 | -0.0011099 | 0.054455 | -0.0019272 | 0.055397 | 0.074154 | -0.00077468 | -0.00021967 | 0.06346 | 0.0073213 | 0.061993 | -64.6 | 0.019721 | -66.7689 | 56.261 | 56.0876 | 56.1566 | -66.8833 | -66.7932 | 0.014095 | -66.8918 | 56.2031 | 56.2939 | 56.1231 | -67.0011 | -0.077273 | -0.11718 | 2.206 | 0.037134 | 0.11441 | -0.29057 | -0.22159 | -0.19511 | -0.17505 | 0.012858 | -0.085749 | 0.10936 | -0.084285 | -0.25507 | 123.067 | 122.8936 | 122.9626 | 66.8258 | -123.2615 | 123.0092 | 123.0999 | 122.9291 | 66.8201 | -123.3793
136.2812 | 123.2391 | -66.8152 | 56.369 | 0.041851 | -0.010704 | -0.0011099 | 0.052318 | -0.0019272 | 0.055397 | 0.058893 | -0.00077468 | -0.00021967 | 0.06346 | 0.0083893 | 0.060925 | -64.5771 | 0.028878 | -66.7735 | 56.261 | 56.0968 | 56.152 | -66.8879 | -66.7886 | 0.018674 | -66.8918 | 56.2077 | 56.2847 | 56.0865 | -66.992 | -0.072696 | -0.10802 | 2.2381 | 0.041712 | 0.11441 | -0.27226 | -0.21701 | -0.1768 | -0.16132 | 0.026593 | -0.076593 | 0.10021 | -0.084288 | -0.28254 | 123.0762 | 122.9119 | 122.9672 | 66.8441 | -123.2569 | 123.0229 | 123.0999 | 122.9017 | 66.8339 | -123.361
137.2812 | 123.2941 | -66.7877 | 56.4011 | 0.072375 | -0.0074993 | -0.0021789 | 0.055523 | -0.0019272 | 0.05326 | 0.058893 | 0.00029332 | -0.00021967 | 0.062391 | 0.0073213 | 0.061993 | -64.5405 | 0.019721 | -66.7689 | 56.261 | 56.1013 | 56.152 | -66.8787 | -66.8023 | 0.018674 | -66.8872 | 56.1985 | 56.2893 | 56.0819 | -66.992 | -0.091004 | -0.14007 | 2.2472 | 0.018824 | 0.10983 | -0.29972 | -0.24905 | -0.20427 | -0.20252 | -0.014609 | -0.09948 | 0.10479 | -0.11175 | -0.31917 | 123.0487 | 122.8891 | 122.9397 | 66.8074 | -123.2798 | 122.9863 | 123.077 | 122.8696 | 66.8064 | -123.393
138.2812 | 123.3948 | -66.7969 | 56.337 | 0.072375 | -0.010704 | -0.0021789 | 0.054455 | -0.0029952 | 0.05326 | 0.074154 | 0.00029332 | -0.00021967 | 0.06346 | 0.0094583 | 0.061993 | -64.6046 | 0.0243 | -66.7735 | 56.261 | 56.0968 | 56.1474 | -66.8741 | -66.7886 | 0.018674 | -66.8918 | 56.1985 | 56.2939 | 56.1506 | -66.992 | -0.07727 | -0.07598 | 2.1923 | 0.023401 | 0.10067 | -0.24021 | -0.18954 | -0.19511 | -0.13843 | 0.008282 | -0.094904 | 0.10021 | -0.043086 | -0.1864 | 123.0579 | 122.8936 | 122.9443 | 66.8212 | -123.2111 | 122.9954 | 123.0908 | 122.9475 | 66.8155 | -123.329
139.2812 | 123.4131 | -66.7923 | 56.3278 | 0.041851 | -0.0096363 | -4.1882e-05 | 0.055523 | -0.0019272 | 0.055397 | 0.074154 | -0.0029117 | -0.00021967 | 0.062391 | 0.0083893 | 0.060925 | -64.568 | 0.015142 | -66.7689 | 56.2564 | 56.0968 | 56.152 | -66.8696 | -66.7886 | 0.014095 | -66.8918 | 56.2077 | 56.2847 | 56.1826 | -66.9966 | -0.077269 | -0.071403 | 2.2243 | 0.023401 | 0.10067 | -0.23106 | -0.17581 | -0.20427 | -0.12012 | 0.003704 | -0.099482 | 0.10479 | -0.043089 | -0.1452 | 123.0487 | 122.8891 | 122.9443 | 66.8074 | -123.1974 | 123 | 123.077 | 122.9749 | 66.8064 | -123.3244
140.2812 | 123.3948 | -66.7603 | 56.3095 | 0.057113 | -0.0096363 | -4.1882e-05 | 0.053386 | -0.0040642 | 0.056465 | 0.043632 | -0.00077468 | -0.0034247 | 0.062391 | 0.0083893 | 0.060925 | -64.5954 | 0.015142 | -66.7689 | 56.2564 | 56.0922 | 56.152 | -66.8787 | -66.784 | 0.014095 | -66.9009 | 56.2031 | 56.303 | 56.178 | -66.9966 | -0.11847 | -0.053092 | 2.1648 | -0.008642 | 0.10983 | -0.21732 | -0.1575 | -0.23631 | -0.10638 | -0.02376 | -0.14068 | 0.095629 | -0.006463 | -0.13146 | 123.0167 | 122.8524 | 122.9123 | 66.7754 | -123.1882 | 122.9634 | 123.0633 | 122.9383 | 66.7743 | -123.3061
141.2812 | 123.4085 | -66.7694 | 56.3187 | 0.072375 | -0.010704 | -4.1882e-05 | 0.055523 | -0.0019272 | 0.054329 | 0.058893 | -0.0018437 | -0.0023567 | 0.062391 | 0.0062533 | 0.061993 | -64.6 | 0.015142 | -66.7689 | 56.2564 | 56.0968 | 56.1474 | -66.8696 | -66.7932 | 0.018674 | -66.8918 | 56.2077 | 56.2893 | 56.1964 | -66.9966 | -0.10016 | -0.062248 | 2.1694 | 0.000513 | 0.10067 | -0.2219 | -0.17123 | -0.22716 | -0.11096 | -0.023763 | -0.12237 | 0.10479 | -0.029355 | -0.1223 | 123.0258 | 122.8662 | 122.9168 | 66.7846 | -123.1882 | 122.9771 | 123.0587 | 122.9658 | 66.7881 | -123.3152
142.2812 | 123.262 | -66.8152 | 56.369 | 0.057113 | -0.011773 | -4.1882e-05 | 0.053386 | -0.0019272 | 0.055397 | 0.074154 | -0.00077468 | -0.00021967 | 0.061323 | 0.0094583 | 0.060925 | -64.5222 | 0.0243 | -66.7781 | 56.2564 | 56.0968 | 56.152 | -66.8741 | -66.7886 | 0.018674 | -66.8872 | 56.2077 | 56.2893 | 56.1689 | -67.0011 | -0.058959 | -0.1126 | 2.293 | 0.037133 | 0.096092 | -0.27226 | -0.21701 | -0.18596 | -0.16132 | 0.026593 | -0.072014 | 0.11394 | -0.079709 | -0.20013 | 123.0716 | 122.9119 | 122.9672 | 66.8395 | -123.2432 | 123.0229 | 123.1045 | 122.9841 | 66.8339 | -123.3702
143.2812 | 123.4039 | -66.7603 | 56.3187 | 0.057113 | -0.0096363 | 0.0010261 | 0.053386 | -0.0019272 | 0.055397 | 0.058893 | -0.00077468 | -0.0012887 | 0.06346 | 0.0094583 | 0.060925 | -64.568 | 0.019721 | -66.7689 | 56.2656 | 56.0922 | 56.152 | -66.8787 | -66.7932 | 0.018674 | -66.8918 | 56.2077 | 56.2847 | 56.1094 | -66.992 | -0.11847 | -0.053091 | 2.1923 | -0.008642 | 0.10983 | -0.22648 | -0.16665 | -0.23173 | -0.11096 | -0.032918 | -0.13152 | 0.10021 | -0.033934 | -0.2093 | 123.0258 | 122.8524 | 122.9123 | 66.78 | -123.1974 | 122.968 | 123.045 | 122.8696 | 66.7789 | -123.3107
144.2812 | 123.3948 | -66.7923 | 56.3416 | 0.087637 | -0.010704 | -0.0011099 | 0.055523 | -0.00085916 | 0.054329 | 0.074154 | 0.00029332 | -0.00021967 | 0.062391 | 0.011595 | 0.061993 | -64.5588 | 0.019721 | -66.7643 | 56.2564 | 56.1013 | 56.1474 | -66.8696 | -66.784 | 0.009516 | -66.8964 | 56.2031 | 56.2939 | 56.0956 | -66.992 | -0.077269 | -0.085136 | 2.2335 | 0.027979 | 0.10525 | -0.24021 | -0.19412 | -0.19969 | -0.13843 | 0.008283 | -0.10406 | 0.095628 | -0.047664 | -0.24592 | 123.0487 | 122.8936 | 122.9397 | 66.812 | -123.2111 | 122.9954 | 123.0862 | 122.8879 | 66.8018 | -123.3335
145.2812 | 123.3261 | -66.7877 | 56.3141 | 0.057113 | -0.0096363 | -4.1882e-05 | 0.053386 | -0.0029952 | 0.055397 | 0.043632 | 0.00029332 | -0.00021967 | 0.06346 | 0.0094583 | 0.061993 | -64.6092 | 0.010564 | -66.7643 | 56.261 | 56.0922 | 56.1474 | -66.8696 | -66.7886 | 0.023253 | -66.9009 | 56.194 | 56.2939 | 56.1872 | -66.992 | -0.081846 | -0.053092 | 2.1786 | 0.023402 | 0.10525 | -0.2219 | -0.16665 | -0.20427 | -0.12012 | -0.000873 | -0.11322 | 0.09105 | -0.020198 | -0.12688 | 123.0487 | 122.8799 | 122.9352 | 66.7983 | -123.1837 | 122.9817 | 123.0816 | 122.9749 | 66.811 | -123.3061
146.2812 | 123.3582 | -66.8198 | 56.3232 | 0.072375 | -0.010704 | -0.0011099 | 0.054455 | -0.0019272 | 0.055397 | 0.074154 | 0.00029332 | -0.0023567 | 0.06346 | 0.0094583 | 0.061993 | -64.6137 | 0.019721 | -66.7643 | 56.261 | 56.1059 | 56.152 | -66.8925 | -66.7932 | 0.018674 | -66.8918 | 56.2031 | 56.2893 | 56.1368 | -66.9966 | -0.072698 | -0.062247 | 2.206 | 0.055445 | 0.12814 | -0.21732 | -0.17123 | -0.1768 | -0.12012 | 0.026591 | -0.072016 | 0.10479 | -0.033932 | -0.1864 | 123.0808 | 122.9257 | 122.9718 | 66.8395 | -123.2157 | 123.0229 | 123.1091 | 122.9566 | 66.8384 | -123.3198
147.2812 | 123.2849 | -66.806 | 56.3828 | 0.057113 | -0.011773 | -0.0011099 | 0.053386 | -0.0019272 | 0.056465 | 0.058893 | -0.0018437 | -0.00021967 | 0.062391 | 0.0073213 | 0.061993 | -64.513 | 0.005985 | -66.7689 | 56.261 | 56.0968 | 56.152 | -66.8833 | -66.7886 | 0.023253 | -66.8918 | 56.1985 | 56.2939 | 56.1689 | -66.9966 | -0.077273 | -0.12176 | 2.293 | 0.037134 | 0.11441 | -0.28599 | -0.23074 | -0.19053 | -0.18421 | 0.017437 | -0.085749 | 0.10479 | -0.088862 | -0.21386 | 123.067 | 122.9028 | 122.958 | 66.812 | -123.2661 | 123.0046 | 123.0999 | 122.9749 | 66.8293 | -123.3793
148.2812 | 123.4268 | -66.774 | 56.3232 | 0.057113 | -0.010704 | -4.1882e-05 | 0.054455 | -0.00085916 | 0.055397 | 0.074154 | -0.0018437 | -0.0012887 | 0.061323 | 0.0083893 | 0.060925 | -64.5908 | 0.015142 | -66.7643 | 56.261 | 56.0968 | 56.1566 | -66.8696 | -66.784 | 0.018674 | -66.8918 | 56.2031 | 56.2939 | 56.2055 | -66.9874 | -0.095579 | -0.062247 | 2.1831 | 0.009669 | 0.10525 | -0.22648 | -0.16665 | -0.21342 | -0.12012 | -0.010027 | -0.11779 | 0.095628 | -0.029353 | -0.11772 | 123.035 | 122.8708 | 122.9306 | 66.7891 | -123.1928 | 122.9771 | 123.0679 | 122.9795 | 66.7927 | -123.3106
149.2812 | 123.3627 | -66.8015 | 56.3232 | 0.057113 | -0.011773 | -0.0021789 | 0.053386 | -0.0019272 | 0.054329 | 0.074154 | -0.0018437 | -0.0012887 | 0.062391 | 0.0083893 | 0.060925 | -64.6092 | 0.019721 | -66.7735 | 56.261 | 56.1013 | 56.152 | -66.8741 | -66.7886 | 0.018674 | -66.8918 | 56.1985 | 56.2893 | 56.1643 | -66.9966 | -0.072692 | -0.062247 | 2.1923 | 0.027979 | 0.10067 | -0.2219 | -0.17123 | -0.19511 | -0.1247 | 0.01286 | -0.090326 | 0.10479 | -0.033932 | -0.15893 | 123.0624 | 122.9028 | 122.9535 | 66.8212 | -123.1974 | 123 | 123.0908 | 122.9658 | 66.8201 | -123.3198
150.2812 | 123.3398 | -66.7969 | 56.337 | 0.072375 | -0.010704 | -0.0011099 | 0.053386 | -0.0019272 | 0.055397 | 0.058893 | -0.0018437 | -0.0012887 | 0.062391 | 0.0094583 | 0.060925 | -64.6092 | 0.015142 | -66.7643 | 56.2564 | 56.0922 | 56.1566 | -66.8787 | -66.7932 | 0.018674 | -66.8918 | 56.1985 | 56.2893 | 56.1735 | -66.9966 | -0.081849 | -0.080558 | 2.1877 | 0.032557 | 0.11441 | -0.24479 | -0.18039 | -0.19969 | -0.13843 | 0.003703 | -0.094904 | 0.10479 | -0.047665 | -0.16351 | 123.0533 | 122.8891 | 122.9535 | 66.812 | -123.2157 | 122.9954 | 123.0862 | 122.9703 | 66.8155 | -123.3335
151.2812 | 123.3536 | -66.7648 | 56.3232 | 0.057113 | -0.010704 | -0.0011099 | 0.055523 | -0.0019272 | 0.055397 | 0.058893 | -0.00077468 | -0.0012887 | 0.06346 | 0.0083893 | 0.060925 | -64.6092 | 0.0243 | -66.7643 | 56.2656 | 56.0922 | 56.152 | -66.8696 | -66.784 | 0.009516 | -66.8964 | 56.1985 | 56.2985 | 56.1323 | -66.9966 | -0.10473 | -0.057668 | 2.1557 | 0.000514 | 0.10525 | -0.23106 | -0.17123 | -0.23173 | -0.1247 | -0.019182 | -0.13153 | 0.10021 | -0.024775 | -0.19098 | 123.0304 | 122.857 | 122.9168 | 66.7891 | -123.1928 | 122.9634 | 123.0633 | 122.8971 | 66.7743 | -123.3198
152.2812 | 123.3215 | -66.806 | 56.3828 | 0.041851 | -0.010704 | -4.1882e-05 | 0.053386 | -0.0029952 | 0.054329 | 0.089415 | -0.0018437 | -0.0012887 | 0.062391 | 0.0083893 | 0.060925 | -64.5084 | 0.028878 | -66.7597 | 56.2656 | 56.1013 | 56.152 | -66.8925 | -66.7886 | 0.018674 | -66.8918 | 56.2031 | 56.2893 | 56.1964 | -66.992 | -0.086431 | -0.11718 | 2.2976 | 0.04629 | 0.13272 | -0.28141 | -0.23074 | -0.18596 | -0.17963 | 0.017437 | -0.085749 | 0.10021 | -0.093441 | -0.18639 | 123.0716 | 122.9074 | 122.958 | 66.8349 | -123.2752 | 123.0092 | 123.0953 | 123.0024 | 66.8247 | -123.3747
153.2812 | 123.3536 | -66.8015 | 56.3187 | 0.072375 | -0.010704 | -0.0011099 | 0.053386 | -0.0029952 | 0.054329 | 0.089415 | -0.00077468 | -0.0012887 | 0.06346 | 0.010526 | 0.060925 | -64.6092 | 0.019721 | -66.7689 | 56.2564 | 56.0968 | 56.1566 | -66.865 | -66.7886 | 0.014095 | -66.8826 | 56.2077 | 56.2893 | 56.178 | -66.992 | -0.063534 | -0.062248 | 2.1923 | 0.032557 | 0.096091 | -0.2219 | -0.16208 | -0.19053 | -0.11096 | 0.01286 | -0.081168 | 0.10936 | -0.029355 | -0.14062 | 123.0579 | 122.8982 | 122.958 | 66.8212 | -123.1837 | 123.0092 | 123.0908 | 122.9795 | 66.8155 | -123.3107
154.2812 | 123.3261 | -66.8015 | 56.3324 | 0.057113 | -0.013909 | -0.0011099 | 0.054455 | -0.0029952 | 0.05326 | 0.074154 | -0.00077468 | -0.00021967 | 0.06346 | 0.0094583 | 0.061993 | -64.5954 | 0.019721 | -66.7643 | 56.261 | 56.0968 | 56.1612 | -66.8833 | -66.7886 | 0.014095 | -66.8872 | 56.1985 | 56.2985 | 56.178 | -66.9966 | -0.08185 | -0.071402 | 2.206 | 0.037135 | 0.11898 | -0.23563 | -0.17123 | -0.19511 | -0.13385 | 0.01286 | -0.085747 | 0.10936 | -0.03393 | -0.15435 | 123.0624 | 122.8982 | 122.9626 | 66.8212 | -123.2157 | 123 | 123.0999 | 122.9795 | 66.8155 | -123.329
155.2812 | 123.3444 | -66.7786 | 56.3278 | 0.057113 | -0.011773 | -0.0011099 | 0.054455 | -0.00085916 | 0.055397 | 0.074154 | -0.0018437 | -0.0012887 | 0.062391 | 0.010526 | 0.061993 | -64.6137 | 0.015142 | -66.7643 | 56.2518 | 56.0968 | 56.1566 | -66.8741 | -66.7886 | 0.018674 | -66.8872 | 56.2077 | 56.2847 | 56.2009 | -66.992 | -0.095581 | -0.075981 | 2.1648 | 0.014246 | 0.10983 | -0.23106 | -0.17123 | -0.21342 | -0.12012 | -0.010029 | -0.10864 | 0.10479 | -0.043089 | -0.12688 | 123.0304 | 122.8753 | 122.9352 | 66.7937 | -123.202 | 122.9863 | 123.0633 | 122.9795 | 66.7972 | -123.3198
156.2812 | 123.349 | -66.7877 | 56.337 | 0.057113 | -0.011773 | -0.0011099 | 0.054455 | -0.0040642 | 0.055397 | 0.043632 | -0.0018437 | -0.0012887 | 0.06346 | 0.0094583 | 0.060925 | -64.6183 | 0.0243 | -66.7735 | 56.2518 | 56.0922 | 56.152 | -66.8879 | -66.7886 | 0.018674 | -66.8872 | 56.2031 | 56.2893 | 56.1552 | -66.9966 | -0.10016 | -0.085136 | 2.1694 | 0.014246 | 0.11441 | -0.24479 | -0.18496 | -0.20885 | -0.13385 | -0.000873 | -0.09948 | 0.10936 | -0.047665 | -0.18182 | 123.0396 | 122.8799 | 122.9397 | 66.812 | -123.2249 | 122.9908 | 123.077 | 122.9429 | 66.8064 | -123.3335
157.2812 | 123.2895 | -66.7923 | 56.3599 | 0.072375 | -0.012841 | -4.1882e-05 | 0.054455 | -0.0019272 | 0.056465 | 0.058893 | -0.0018437 | -0.0012887 | 0.06346 | 0.0083893 | 0.061993 | -64.5313 | 0.019721 | -66.7689 | 56.261 | 56.0968 | 56.1566 | -66.8833 | -66.7886 | 0.014095 | -66.8918 | 56.2077 | 56.2939 | 56.1414 | -66.9966 | -0.091006 | -0.098868 | 2.261 | 0.023401 | 0.11441 | -0.2631 | -0.20327 | -0.20427 | -0.15216 | 0.003704 | -0.099482 | 0.10479 | -0.065974 | -0.21844 | 123.0533 | 122.8891 | 122.9489 | 66.812 | -123.2432 | 123 | 123.0862 | 122.9337 | 66.8064 | -123.3564
158.2812 | 123.317 | -66.7877 | 56.3049 | 0.057113 | -0.011773 | -0.0032469 | 0.055523 | -0.0029952 | 0.055397 | 0.10468 | -0.00077468 | -0.0023567 | 0.062391 | 0.011595 | 0.059856 | -64.5908 | 0.019721 | -66.7643 | 56.2564 | 56.1013 | 56.1566 | -66.8787 | -66.7977 | 0.018674 | -66.8918 | 56.194 | 56.2893 | 56.1597 | -66.9966 | -0.091004 | -0.048515 | 2.1969 | 0.023402 | 0.11441 | -0.20359 | -0.14834 | -0.20885 | -0.11097 | -0.01003 | -0.10406 | 0.10479 | -0.015622 | -0.1452 | 123.0441 | 122.8891 | 122.9443 | 66.8074 | -123.1837 | 122.9817 | 123.077 | 122.9475 | 66.8064 | -123.3015
159.2812 | 123.349 | -66.7923 | 56.3141 | 0.026589 | -0.010704 | -0.0021789 | 0.054455 | -0.0040642 | 0.055397 | 0.058893 | -0.00077468 | -0.00021967 | 0.062391 | 0.011595 | 0.059856 | -64.6 | 0.0243 | -66.7689 | 56.2564 | 56.1013 | 56.152 | -66.8696 | -66.784 | 0.014095 | -66.8918 | 56.1985 | 56.2939 | 56.1368 | -66.992 | -0.077269 | -0.05767 | 2.1923 | 0.023401 | 0.10067 | -0.21274 | -0.16208 | -0.19969 | -0.11554 | 0.008283 | -0.099482 | 0.10021 | -0.020198 | -0.17725 | 123.0487 | 122.8936 | 122.9443 | 66.8166 | -123.1837 | 122.9908 | 123.0862 | 122.9291 | 66.8064 | -123.3061
160.2812 | 123.349 | -66.7694 | 56.3232 | 0.087637 | -0.013909 | -0.0011099 | 0.055523 | -0.0029952 | 0.055397 | 0.074154 | -0.0018437 | -0.0023567 | 0.064528 | 0.010526 | 0.060925 | -64.6137 | 0.015142 | -66.7735 | 56.261 | 56.083 | 56.152 | -66.8741 | -66.784 | 0.009516 | -66.8918 | 56.2031 | 56.2893 | 56.1139 | -66.9874 | -0.10474 | -0.062247 | 2.1557 | -0.004065 | 0.10067 | -0.24021 | -0.17123 | -0.218 | -0.12012 | -0.014605 | -0.12237 | 0.095628 | -0.033932 | -0.2093 | 123.0304 | 122.8524 | 122.9214 | 66.7846 | -123.1974 | 122.9725 | 123.0587 | 122.8834 | 66.7789 | -123.3106
161.2812 | 123.3536 | -66.806 | 56.3004 | 0.057113 | -0.012841 | -0.0011099 | 0.053386 | -0.0029952 | 0.05326 | 0.058893 | -0.00077468 | -0.0012887 | 0.062391 | 0.010526 | 0.059856 | -64.5954 | 0.0243 | -66.7689 | 56.2564 | 56.0876 | 56.1474 | -66.8741 | -66.7886 | 0.018674 | -66.8826 | 56.2031 | 56.2893 | 56.2101 | -66.992 | -0.068115 | -0.043937 | 2.2106 | 0.037134 | 0.10525 | -0.21275 | -0.15292 | -0.18596 | -0.09723 | 0.017437 | -0.076591 | 0.10936 | -0.011044 | -0.090257 | 123.0624 | 122.8936 | 122.9535 | 66.8303 | -123.1745 | 123.0092 | 123.0953 | 123.0161 | 66.8247 | -123.2923
162.2812 | 123.3444 | -66.774 | 56.3416 | 0.087637 | -0.010704 | -0.0011099 | 0.054455 | -0.0040642 | 0.055397 | 0.058893 | -0.0018437 | -0.0012887 | 0.064528 | 0.010526 | 0.063061 | -64.5496 | 0.019721 | -66.7643 | 56.2656 | 56.1013 | 56.152 | -66.8741 | -66.7794 | 0.014095 | -66.8964 | 56.2031 | 56.2893 | 56.1918 | -67.0011 | -0.10016 | -0.075979 | 2.2243 | 0.009669 | 0.10983 | -0.24021 | -0.18954 | -0.22716 | -0.13843 | -0.005449 | -0.12237 | 0.10478 | -0.052243 | -0.14977 | 123.0396 | 122.8753 | 122.926 | 66.7937 | -123.2157 | 122.9771 | 123.0633 | 122.9658 | 66.7881 | -123.3427
163.2812 | 123.3215 | -66.8335 | 56.3232 | 0.057113 | -0.013909 | -0.0011099 | 0.054455 | -0.0019272 | 0.055397 | 0.058893 | -0.0018437 | -0.0012887 | 0.062391 | 0.011595 | 0.061993 | -64.5954 | 0.0243 | -66.7689 | 56.2518 | 56.0876 | 56.152 | -66.8741 | -66.7886 | 0.009516 | -66.8918 | 56.1985 | 56.2939 | 56.2101 | -66.992 | -0.040649 | -0.071403 | 2.2381 | 0.0646 | 0.10525 | -0.23564 | -0.17123 | -0.15849 | -0.1247 | 0.044903 | -0.058283 | 0.10021 | -0.029353 | -0.11315 | 123.0853 | 122.9211 | 122.9855 | 66.8578 | -123.1974 | 123.032 | 123.1274 | 123.0436 | 66.843 | -123.3152
164.2812 | 123.3582 | -66.7557 | 56.3416 | 0.057113 | -0.011773 | -0.0011099 | 0.053386 | -0.0040642 | 0.054329 | 0.058893 | -0.00077468 | -0.0012887 | 0.061323 | 0.011595 | 0.060925 | -64.6092 | 0.015142 | -66.7643 | 56.261 | 56.0922 | 56.152 | -66.8787 | -66.7886 | 0.014095 | -66.8826 | 56.2077 | 56.2893 | 56.1872 | -66.9874 | -0.12305 | -0.080558 | 2.1465 | -0.008642 | 0.11441 | -0.24937 | -0.18954 | -0.23173 | -0.13385 | -0.032917 | -0.12695 | 0.10479 | -0.052243 | -0.15435 | 123.0167 | 122.8479 | 122.9077 | 66.7708 | -123.2203 | 122.9634 | 123.045 | 122.9429 | 66.7698 | -123.329
165.2812 | 123.3902 | -66.8015 | 56.2912 | 0.087637 | -0.012841 | -0.0032469 | 0.053386 | -0.0051322 | 0.055397 | 0.058893 | -0.00077468 | -0.0012887 | 0.06346 | 0.010526 | 0.060925 | -64.5771 | 0.0243 | -66.7552 | 56.261 | 56.0968 | 56.152 | -66.8833 | -66.7932 | 0.014095 | -66.8918 | 56.2077 | 56.2939 | 56.2101 | -66.9966 | -0.08185 | -0.030204 | 2.2243 | 0.046292 | 0.12814 | -0.19443 | -0.13919 | -0.19511 | -0.083497 | 0.008281 | -0.090326 | 0.10479 | 0.00269 | -0.081102 | 123.0624 | 122.8982 | 122.9535 | 66.8258 | -123.1745 | 123.0092 | 123.0953 | 123.0115 | 66.8155 | -123.2878
166.2812 | 123.3902 | -66.7694 | 56.3095 | 0.041851 | -0.013909 | -0.0032469 | 0.055523 | -0.0040642 | 0.054329 | 0.058893 | -0.00077468 | -0.00021967 | 0.062391 | 0.010526 | 0.059856 | -64.5725 | 0.019721 | -66.746 | 56.261 | 56.0968 | 56.1429 | -66.8787 | -66.7932 | 0.014095 | -66.8918 | 56.2031 | 56.2893 | 56.2009 | -66.992 | -0.10932 | -0.048514 | 2.1969 | 0.023404 | 0.13272 | -0.21274 | -0.16666 | -0.22258 | -0.10638 | -0.023763 | -0.12237 | 0.10021 | -0.020199 | -0.10857 | 123.0304 | 122.8662 | 122.9123 | 66.7891 | -123.1882 | 122.9725 | 123.0587 | 122.9703 | 66.7835 | -123.3015
167.2812 | 123.3948 | -66.7923 | 56.3095 | 0.072375 | -0.011773 | -4.1882e-05 | 0.053386 | -0.0019272 | 0.05326 | 0.074154 | 0.00029332 | -0.0023567 | 0.062391 | 0.010526 | 0.061993 | -64.5908 | 0.019721 | -66.7552 | 56.2564 | 56.0922 | 56.152 | -66.8833 | -66.7886 | 0.009516 | -66.8872 | 56.1985 | 56.2893 | 56.1826 | -66.992 | -0.091006 | -0.053092 | 2.2014 | 0.037136 | 0.12814 | -0.21732 | -0.1575 | -0.19969 | -0.11096 | 0.003704 | -0.094903 | 0.10479 | -0.020199 | -0.12688 | 123.0487 | 122.8845 | 122.9443 | 66.812 | -123.1928 | 122.9908 | 123.0816 | 122.9749 | 66.8018 | -123.3015
168.2812 | 123.2895 | -66.8198 | 56.3644 | 0.057113 | -0.012841 | -0.0032469 | 0.054455 | -0.0040642 | 0.056465 | 0.058893 | -0.0018437 | -0.00021967 | 0.062391 | 0.011595 | 0.061993 | -64.513 | 0.010564 | -66.7552 | 56.2564 | 56.0922 | 56.152 | -66.8787 | -66.784 | 0.014095 | -66.8918 | 56.2031 | 56.2802 | 56.2055 | -66.9874 | -0.058961 | -0.10802 | 2.3067 | 0.064602 | 0.12356 | -0.27226 | -0.21243 | -0.16764 | -0.16132 | 0.035749 | -0.072016 | 0.095628 | -0.084288 | -0.15892 | 123.0762 | 122.9119 | 122.9718 | 66.8303 | -123.2432 | 123.0229 | 123.0999 | 123.0253 | 66.8339 | -123.3518
169.2812 | 123.3673 | -66.7831 | 56.3599 | 0.057113 | -0.012841 | -0.0032469 | 0.053386 | -0.0040642 | 0.055397 | 0.058893 | 0.00029332 | -0.0023567 | 0.061323 | 0.011595 | 0.061993 | -64.6046 | 0.0243 | -66.7552 | 56.261 | 56.1059 | 56.1566 | -66.8879 | -66.7932 | 0.023253 | -66.8918 | 56.1985 | 56.2893 | 56.1826 | -67.0011 | -0.10474 | -0.098868 | 2.1786 | 0.027981 | 0.13272 | -0.25394 | -0.20327 | -0.218 | -0.16132 | -0.01003 | -0.10864 | 0.10936 | -0.070553 | -0.17724 | 123.0441 | 122.8891 | 122.9397 | 66.8074 | -123.2477 | 122.9817 | 123.0725 | 122.9658 | 66.8064 | -123.361
170.2812 | 123.2666 | -66.8152 | 56.3599 | 0.057113 | -0.013909 | -0.0021789 | 0.054455 | -0.0029952 | 0.056465 | 0.043632 | -0.00077468 | -0.0012887 | 0.061323 | 0.010526 | 0.061993 | -64.5313 | 0.015142 | -66.7506 | 56.2518 | 56.0922 | 56.1612 | -66.8879 | -66.7932 | 0.014095 | -66.8964 | 56.2031 | 56.2893 | 56.1689 | -66.992 | -0.072696 | -0.10802 | 2.2839 | 0.064603 | 0.1373 | -0.26768 | -0.19869 | -0.1768 | -0.15674 | 0.022014 | -0.081172 | 0.095628 | -0.070553 | -0.19097 | 123.067 | 122.9074 | 122.9764 | 66.8303 | -123.2477 | 123.0183 | 123.1045 | 122.9841 | 66.8293 | -123.3518
171.2812 | 123.3536 | -66.8106 | 56.2958 | 0.072375 | -0.012841 | -0.0021789 | 0.054455 | -0.00085916 | 0.056465 | 0.058893 | -0.00077468 | -0.00021967 | 0.062391 | 0.011595 | 0.060925 | -64.5908 | 0.010564 | -66.7597 | 56.261 | 56.0922 | 56.1474 | -66.8741 | -66.7886 | 0.018674 | -66.8964 | 56.1985 | 56.2893 | 56.1964 | -67.0011 | -0.063537 | -0.034781 | 2.2198 | 0.050868 | 0.11441 | -0.20359 | -0.14834 | -0.19053 | -0.097231 | 0.022015 | -0.08575 | 0.10478 | -0.006466 | -0.099415 | 123.0716 | 122.9028 | 122.958 | 66.8212 | -123.1699 | 123.0092 | 123.0999 | 123.007 | 66.8293 | -123.2969
172.2812 | 123.2712 | -66.8106 | 56.3644 | 0.057113 | -0.014978 | -0.0032469 | 0.054455 | -0.0040642 | 0.055397 | 0.074154 | -0.0018437 | -0.0012887 | 0.062391 | 0.011595 | 0.060925 | -64.5084 | 0.0243 | -66.7506 | 56.261 | 56.0922 | 56.1566 | -66.8696 | -66.784 | 0.014095 | -66.8918 | 56.2031 | 56.2939 | 56.2101 | -66.9966 | -0.058958 | -0.10345 | 2.3022 | 0.060025 | 0.11898 | -0.27226 | -0.20785 | -0.18596 | -0.16132 | 0.026594 | -0.081171 | 0.10479 | -0.070552 | -0.15434 | 123.0716 | 122.9028 | 122.9672 | 66.8349 | -123.234 | 123.0137 | 123.1045 | 123.0207 | 66.8247 | -123.361
173.2812 | 123.3948 | -66.7969 | 56.2866 | 0.072375 | -0.014978 | -0.0021789 | 0.052318 | -0.0029952 | 0.056465 | 0.089415 | -0.0018437 | -0.0023567 | 0.062391 | 0.0094583 | 0.061993 | -64.5634 | 0.019721 | -66.7552 | 56.2564 | 56.0922 | 56.1566 | -66.8741 | -66.7932 | 0.018674 | -66.8872 | 56.1985 | 56.2939 | 56.2009 | -66.992 | -0.07727 | -0.030204 | 2.2335 | 0.041714 | 0.11898 | -0.19444 | -0.13003 | -0.19511 | -0.088076 | 0.003703 | -0.090325 | 0.10479 | 0.007268 | -0.085682 | 123.0533 | 122.8891 | 122.9535 | 66.8166 | -123.1608 | 122.9954 | 123.0908 | 122.9978 | 66.8155 | -123.2786
174.2812 | 123.3398 | -66.8015 | 56.3187 | 0.072375 | -0.013909 | -0.0021789 | 0.052318 | -0.0029952 | 0.055397 | 0.043632 | -0.0018437 | -0.00021967 | 0.060255 | 0.011595 | 0.059856 | -64.5863 | 0.015142 | -66.7597 | 56.261 | 56.0876 | 56.1566 | -66.8879 | -66.784 | 0.018674 | -66.8918 | 56.1985 | 56.2939 | 56.2009 | -67.0011 | -0.086429 | -0.05767 | 2.2152 | 0.041713 | 0.12814 | -0.23106 | -0.16208 | -0.19969 | -0.12012 | 0.017439 | -0.090326 | 0.10936 | -0.024776 | -0.11773 | 123.0624 | 122.8891 | 122.958 | 66.8166 | -123.2065 | 123 | 123.0953 | 123.0024 | 66.8201 | -123.3198
175.2812 | 123.4177 | -66.7694 | 56.3232 | 0.072375 | -0.016046 | -0.0021789 | 0.054455 | -0.0029952 | 0.055397 | 0.089415 | -0.0018437 | -0.0012887 | 0.061323 | 0.012663 | 0.059856 | -64.5725 | 0.015142 | -66.7552 | 56.261 | 56.0922 | 56.1612 | -66.8787 | -66.784 | 0.014095 | -66.8826 | 56.2031 | 56.2939 | 56.2009 | -66.9966 | -0.10932 | -0.062247 | 2.1969 | 0.014248 | 0.12356 | -0.23106 | -0.16207 | -0.22716 | -0.12012 | -0.014605 | -0.11321 | 0.11394 | -0.029353 | -0.1223 | 123.0304 | 122.8616 | 122.9306 | 66.7846 | -123.202 | 122.9725 | 123.0633 | 122.9703 | 66.7835 | -123.3198
176.2812 | 123.3582 | -66.806 | 56.3324 | 0.041851 | -0.014978 | -0.0021789 | 0.055523 | -0.0029952 | 0.05326 | 0.089415 | 0.00029332 | -0.00021967 | 0.062391 | 0.012663 | 0.061993 | -64.6046 | 0.0243 | -66.7643 | 56.2564 | 56.083 | 56.152 | -66.865 | -66.7886 | 0.009516 | -66.8918 | 56.2077 | 56.2847 | 56.1826 | -67.0011 | -0.058957 | -0.07598 | 2.2014 | 0.041712 | 0.10067 | -0.24937 | -0.18039 | -0.19511 | -0.1247 | 0.017437 | -0.085749 | 0.10936 | -0.047666 | -0.14977 | 123.0624 | 122.8891 | 122.958 | 66.8303 | -123.1974 | 123.0137 | 123.0908 | 122.9887 | 66.8155 | -123.3335
177.2812 | 123.262 | -66.806 | 56.3736 | 0.057113 | -0.017114 | -0.0011099 | 0.054455 | -0.0040642 | 0.054329 | 0.058893 | -0.0018437 | -0.0012887 | 0.060255 | 0.012663 | 0.059856 | -64.513 | 0.019721 | -66.7597 | 56.2702 | 56.0876 | 56.1612 | -66.8604 | -66.784 | 0.023253 | -66.8964 | 56.2031 | 56.2893 | 56.2055 | -66.9828 | -0.054378 | -0.10344 | 2.293 | 0.04629 | 0.10067 | -0.28599 | -0.21243 | -0.1768 | -0.17047 | 0.022016 | -0.090328 | 0.08647 | -0.084286 | -0.16808 | 123.0762 | 122.8936 | 122.9672 | 66.8258 | -123.234 | 123.0092 | 123.0953 | 123.0115 | 66.8293 | -123.3564
178.2812 | 123.3902 | -66.7694 | 56.3004 | 0.057113 | -0.016046 | -0.0032469 | 0.053386 | -0.0040642 | 0.055397 | 0.058893 | -0.0018437 | -0.0012887 | 0.062391 | 0.011595 | 0.059856 | -64.5771 | 0.019721 | -66.7552 | 56.261 | 56.0922 | 56.1474 | -66.8696 | -66.7932 | 0.014095 | -66.8872 | 56.2031 | 56.2893 | 56.2055 | -66.992 | -0.10016 | -0.039359 | 2.1923 | 0.014248 | 0.11441 | -0.20817 | -0.15292 | -0.22258 | -0.09723 | -0.023763 | -0.11779 | 0.10479 | -0.011044 | -0.094836 | 123.0304 | 122.8616 | 122.9168 | 66.7891 | -123.1699 | 122.9725 | 123.0587 | 122.9749 | 66.7835 | -123.2923
179.2812 | 123.3215 | -66.8015 | 56.2683 | 0.057113 | -0.014978 | -0.0011099 | 0.053386 | -0.0029952 | 0.055397 | 0.058893 | -0.0029117 | 0.00084833 | 0.062391 | 0.013731 | 0.060925 | -64.5542 | 0.019721 | -66.7597 | 56.2656 | 56.0968 | 56.1612 | -66.8833 | -66.784 | 0.018674 | -66.8872 | 56.1985 | 56.2939 | 56.2055 | -66.9966 | -0.08185 | -0.002737 | 2.2472 | 0.041713 | 0.12356 | -0.17155 | -0.10714 | -0.19511 | -0.069766 | 0.017439 | -0.085747 | 0.10936 | 0.025578 | -0.062793 | 123.067 | 122.8982 | 122.9626 | 66.8212 | -123.1516 | 123 | 123.0953 | 123.007 | 66.8201 | -123.2649
180.2812 | 123.3673 | -66.774 | 56.337 | 0.057113 | -0.013909 | -0.0032469 | 0.053386 | -0.0029952 | 0.054329 | 0.058893 | -0.0018437 | -0.00021967 | 0.060255 | 0.010526 | 0.061993 | -64.5634 | 0.0243 | -66.7689 | 56.2564 | 56.1013 | 56.1566 | -66.8741 | -66.784 | 0.018674 | -66.8918 | 56.2031 | 56.2847 | 56.178 | -66.992 | -0.10016 | -0.080558 | 2.2106 | 0.005091 | 0.10525 | -0.23563 | -0.18039 | -0.218 | -0.13385 | -0.010027 | -0.11779 | 0.10021 | -0.052244 | -0.15893 | 123.0304 | 122.8753 | 122.9306 | 66.7983 | -123.2111 | 122.9771 | 123.0587 | 122.952 | 66.7927 | -123.329
181.2812 | 123.3765 | -66.806 | 56.2958 | 0.041851 | -0.016046 | -0.0021789 | 0.054455 | -0.0040642 | 0.055397 | 0.074154 | 0.00029332 | -0.0023567 | 0.061323 | 0.012663 | 0.060925 | -64.5725 | 0.019721 | -66.7643 | 56.261 | 56.0968 | 56.1657 | -66.8513 | -66.7886 | 0.023253 | -66.8826 | 56.2031 | 56.2893 | 56.1689 | -66.992 | -0.045221 | -0.034781 | 2.2335 | 0.041712 | 0.086933 | -0.19901 | -0.13003 | -0.18596 | -0.092652 | 0.017437 | -0.076591 | 0.10936 | -0.006466 | -0.12689 | 123.067 | 122.9028 | 122.9718 | 66.8258 | -123.147 | 123.0092 | 123.0953 | 122.9749 | 66.8293 | -123.2878
182.2812 | 123.4039 | -66.774 | 56.3278 | 0.072375 | -0.014978 | -0.0011099 | 0.050181 | -0.0051322 | 0.054329 | 0.089415 | -0.0018437 | -0.0023567 | 0.06346 | 0.011595 | 0.059856 | -64.5908 | 0.0243 | -66.7597 | 56.261 | 56.0968 | 56.1566 | -66.865 | -66.7886 | 0.023253 | -66.8964 | 56.194 | 56.2802 | 56.1964 | -67.0011 | -0.091 | -0.066825 | 2.1831 | 0.014247 | 0.10525 | -0.23106 | -0.17123 | -0.22716 | -0.13385 | -0.014606 | -0.12237 | 0.10478 | -0.047667 | -0.13146 | 123.035 | 122.8708 | 122.9306 | 66.7983 | -123.1928 | 122.968 | 123.0541 | 122.9703 | 66.7972 | -123.329
183.2812 | 123.3353 | -66.8015 | 56.3004 | 0.041851 | -0.014978 | -0.0011099 | 0.055523 | -0.0029952 | 0.055397 | 0.058893 | -0.00077468 | -0.0023567 | 0.061323 | 0.013731 | 0.059856 | -64.6 | 0.019721 | -66.7552 | 56.2564 | 56.0968 | 56.1612 | -66.865 | -66.784 | 0.018674 | -66.8964 | 56.2031 | 56.2847 | 56.1735 | -66.9966 | -0.063534 | -0.043937 | 2.2014 | 0.046292 | 0.10983 | -0.20359 | -0.13919 | -0.19511 | -0.09723 | 0.017439 | -0.094905 | 0.10021 | -0.015623 | -0.12689 | 123.0579 | 122.8982 | 122.9626 | 66.8212 | -123.1653 | 123.0046 | 123.0862 | 122.9749 | 66.8201 | -123.2969
184.3125 | 123.3902 | -66.7923 | 56.282 | 0.041851 | -0.014978 | -0.0032469 | 0.052318 | -0.0040642 | 0.056465 | 0.058893 | -0.00077468 | -0.0012887 | 0.060255 | 0.013731 | 0.059856 | -64.5496 | 0.0243 | -66.7643 | 56.2656 | 56.0922 | 56.152 | -66.8879 | -66.7886 | 0.023253 | -66.8918 | 56.2031 | 56.2985 | 56.1826 | -66.9966 | -0.095585 | -0.016469 | 2.2427 | 0.027979 | 0.12356 | -0.18986 | -0.13003 | -0.20427 | -0.078919 | 0.003704 | -0.099482 | 0.10479 | 0.016424 | -0.099418 | 123.0579 | 122.8845 | 122.9443 | 66.8166 | -123.1699 | 122.9954 | 123.0908 | 122.9749 | 66.8156 | -123.2786
185.2812 | 123.317 | -66.7877 | 56.3416 | 0.057113 | -0.017114 | -4.1882e-05 | 0.055523 | -0.0051322 | 0.05326 | 0.043632 | -0.0018437 | 0.00084833 | 0.061323 | 0.013731 | 0.060925 | -64.5084 | 0.0243 | -66.7597 | 56.261 | 56.1013 | 56.1657 | -66.8833 | -66.7977 | 0.023253 | -66.8872 | 56.1985 | 56.2847 | 56.1689 | -66.9874 | -0.095583 | -0.080558 | 2.2793 | 0.02798 | 0.12356 | -0.24021 | -0.17581 | -0.19969 | -0.14301 | -0.01003 | -0.09948 | 0.10021 | -0.056822 | -0.17266 | 123.0487 | 122.8891 | 122.9535 | 66.812 | -123.2249 | 122.9863 | 123.0725 | 122.9566 | 66.811 | -123.329
186.2812 | 123.349 | -66.7877 | 56.2866 | 0.041851 | -0.014978 | -0.0032469 | 0.052318 | -0.0019272 | 0.054329 | 0.058893 | -0.00077468 | -0.0023567 | 0.060255 | 0.013731 | 0.059856 | -64.5817 | 0.0243 | -66.7597 | 56.2473 | 56.1013 | 56.152 | -66.8696 | -66.784 | 0.014095 | -66.8826 | 56.2077 | 56.2802 | 56.2055 | -67.0011 | -0.081846 | -0.039361 | 2.206 | 0.02798 | 0.10983 | -0.18528 | -0.13461 | -0.21342 | -0.078919 | 0.003706 | -0.094901 | 0.11852 | -0.006468 | -0.081103 | 123.035 | 122.8891 | 122.9397 | 66.812 | -123.1562 | 122.9954 | 123.0679 | 122.9932 | 66.8018 | -123.2878
187.3125 | 123.2391 | -66.8472 | 56.3187 | 0.057113 | -0.014978 | -0.0021789 | 0.052318 | -0.0029952 | 0.055397 | 0.074154 | 0.00029332 | -0.00021967 | 0.060255 | 0.013731 | 0.061993 | -64.5268 | 0.019721 | -66.7689 | 56.2656 | 56.0968 | 56.1612 | -66.8925 | -66.7886 | 0.014095 | -66.8918 | 56.2077 | 56.2847 | 56.2009 | -66.992 | -0.045232 | -0.053091 | 2.3205 | 0.078333 | 0.12356 | -0.2219 | -0.1575 | -0.14476 | -0.11096 | 0.058636 | -0.04455 | 0.10021 | -0.033934 | -0.11773 | 123.1128 | 122.944 | 123.0084 | 66.867 | -123.2111 | 123.0549 | 123.132 | 123.0482 | 66.8613 | -123.3107
188.2812 | 123.4085 | -66.7969 | 56.2729 | 0.041851 | -0.014978 | -0.0011099 | 0.052318 | -0.0029952 | 0.055397 | 0.058893 | -0.00077468 | -0.0012887 | 0.060255 | 0.012663 | 0.059856 | -64.5725 | 0.0243 | -66.7597 | 56.2564 | 56.0922 | 56.1566 | -66.8696 | -66.7794 | 0.018674 | -66.8872 | 56.1985 | 56.2893 | 56.2101 | -66.992 | -0.072691 | -0.016471 | 2.2243 | 0.037135 | 0.10983 | -0.1807 | -0.1163 | -0.19511 | -0.074343 | 0.017439 | -0.090325 | 0.10479 | 0.016422 | -0.062791 | 123.0533 | 122.8891 | 122.9535 | 66.8212 | -123.1425 | 122.9954 | 123.0862 | 123.007 | 66.8155 | -123.2649
189.2812 | 123.3536 | -66.8015 | 56.3141 | 0.057113 | -0.014978 | -0.0021789 | 0.052318 | -0.0029952 | 0.056465 | 0.089415 | -0.0018437 | -0.00021967 | 0.060255 | 0.012663 | 0.059856 | -64.6046 | 0.028878 | -66.7597 | 56.2564 | 56.0922 | 56.1566 | -66.8879 | -66.7932 | 0.018674 | -66.8872 | 56.1985 | 56.2939 | 56.2009 | -67.0011 | -0.086429 | -0.05767 | 2.1969 | 0.041713 | 0.12814 | -0.2219 | -0.1575 | -0.19969 | -0.11554 | 0.008281 | -0.085747 | 0.11394 | -0.020198 | -0.11315 | 123.0579 | 122.8936 | 122.958 | 66.8303 | -123.202 | 123 | 123.0953 | 123.0024 | 66.8201 | -123.3152
190.2969 | 123.2712 | -66.8289 | 56.3644 | 0.057113 | -0.017114 | -0.0032469 | 0.054455 | -0.0019272 | 0.05326 | 0.074154 | -0.0018437 | -0.0012887 | 0.06346 | 0.012663 | 0.059856 | -64.5176 | 0.028878 | -66.7643 | 56.2702 | 56.0968 | 56.1612 | -66.8925 | -66.784 | 0.018674 | -66.8872 | 56.1985 | 56.2939 | 56.2009 | -66.992 | -0.063543 | -0.094289 | 2.3113 | 0.0646 | 0.12814 | -0.26768 | -0.20327 | -0.16307 | -0.1659 | 0.044904 | -0.058282 | 0.10479 | -0.070552 | -0.1635 | 123.0991 | 122.9257 | 122.9901 | 66.8578 | -123.2569 | 123.0275 | 123.1228 | 123.0299 | 66.8476 | -123.3564
191.2812 | 123.3398 | -66.7923 | 56.3095 | 0.072375 | -0.014978 | -0.0021789 | 0.052318 | -0.0029952 | 0.05326 | 0.058893 | -0.0029117 | -0.0012887 | 0.060255 | 0.012663 | 0.058788 | -64.5954 | 0.0243 | -66.7643 | 56.2564 | 56.0968 | 56.1657 | -66.8741 | -66.7886 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.2055 | -66.9966 | -0.081848 | -0.053092 | 2.1969 | 0.027979 | 0.10983 | -0.21274 | -0.14376 | -0.20427 | -0.10638 | 0.003704 | -0.094903 | 0.10936 | -0.01562 | -0.10399 | 123.0487 | 122.8891 | 122.958 | 66.8166 | -123.1837 | 122.9954 | 123.0862 | 122.9978 | 66.8064 | -123.3061
192.2812 | 123.3444 | -66.8015 | 56.2958 | 0.057113 | -0.014978 | -0.0021789 | 0.052318 | -0.0029952 | 0.055397 | 0.058893 | -0.00077468 | -0.0034247 | 0.062391 | 0.012663 | 0.060925 | -64.5863 | 0.015142 | -66.7689 | 56.2564 | 56.1013 | 56.1566 | -66.8696 | -66.7886 | 0.018674 | -66.8918 | 56.1985 | 56.2939 | 56.1643 | -67.0011 | -0.068113 | -0.039359 | 2.2152 | 0.032557 | 0.10067 | -0.19443 | -0.13919 | -0.19969 | -0.097231 | 0.01286 | -0.090326 | 0.10936 | -0.001887 | -0.13146 | 123.0579 | 122.9028 | 122.958 | 66.8166 | -123.1653 | 123 | 123.0953 | 122.9658 | 66.8201 | -123.2969
193.2812 | 123.3673 | -66.7694 | 56.2912 | 0.057113 | -0.016046 | -0.0011099 | 0.052318 | -0.0051322 | 0.055397 | 0.089415 | -0.0018437 | -0.0012887 | 0.060255 | 0.010526 | 0.059856 | -64.5863 | 0.019721 | -66.7643 | 56.2564 | 56.0922 | 56.1566 | -66.8833 | -66.784 | 0.014095 | -66.8918 | 56.2031 | 56.2893 | 56.2009 | -66.992 | -0.11389 | -0.034782 | 2.1831 | 0.005091 | 0.11898 | -0.19901 | -0.13461 | -0.22258 | -0.088075 | -0.014605 | -0.12237 | 0.10021 | -0.001889 | -0.09026 | 123.0258 | 122.8616 | 122.926 | 66.7891 | -123.1745 | 122.9725 | 123.0587 | 122.9703 | 66.7835 | -123.2832
194.2812 | 123.3948 | -66.7831 | 56.3095 | 0.041851 | -0.016046 | -0.0021789 | 0.053386 | -0.0040642 | 0.05326 | 0.074154 | -0.00077468 | -0.0012887 | 0.064528 | 0.011595 | 0.059856 | -64.5771 | 0.028878 | -66.7597 | 56.261 | 56.1013 | 56.152 | -66.8833 | -66.7932 | 0.018674 | -66.8918 | 56.1985 | 56.2847 | 56.1689 | -67.0011 | -0.10016 | -0.048514 | 2.206 | 0.023402 | 0.12356 | -0.20817 | -0.1575 | -0.218 | -0.11096 | -0.01003 | -0.10864 | 0.10936 | -0.024778 | -0.14062 | 123.0441 | 122.8845 | 122.9352 | 66.812 | -123.1928 | 122.9817 | 123.0679 | 122.952 | 66.8018 | -123.3107
195.2812 | 123.3948 | -66.774 | 56.3004 | 0.057113 | -0.016046 | -0.0032469 | 0.054455 | -0.0062002 | 0.055397 | 0.058893 | -0.0018437 | -0.0012887 | 0.059187 | 0.0148 | 0.060925 | -64.5725 | 0.0243 | -66.7643 | 56.2656 | 56.1059 | 56.1566 | -66.8879 | -66.7794 | 0.018674 | -66.8918 | 56.2031 | 56.2985 | 56.2009 | -66.992 | -0.11389 | -0.03478 | 2.2015 | 0.009669 | 0.12356 | -0.19443 | -0.14377 | -0.218 | -0.09723 | -0.005449 | -0.11779 | 0.10021 | -0.001887 | -0.099415 | 123.0396 | 122.8799 | 122.9306 | 66.7983 | -123.1882 | 122.9771 | 123.0725 | 122.9749 | 66.7927 | -123.2923
196.2812 | 123.3856 | -66.7923 | 56.282 | 0.057113 | -0.016046 | -0.0021789 | 0.052318 | -0.0051322 | 0.056465 | 0.089415 | -0.00077468 | -0.0023567 | 0.061323 | 0.011595 | 0.05772 | -64.5725 | 0.015142 | -66.7735 | 56.261 | 56.0968 | 56.1657 | -66.8833 | -66.7886 | 0.023253 | -66.8872 | 56.2031 | 56.2893 | 56.1552 | -66.9966 | -0.091006 | -0.021048 | 2.2198 | 0.018823 | 0.10983 | -0.18528 | -0.1163 | -0.20427 | -0.078919 | 0.003704 | -0.094903 | 0.10936 | 0.007267 | -0.12689 | 123.0533 | 122.8891 | 122.958 | 66.8074 | -123.1653 | 122.9954 | 123.0816 | 122.9475 | 66.8156 | -123.2786
197.2812 | 123.2895 | -66.8152 | 56.3736 | 0.057113 | -0.018183 | -0.0043149 | 0.054455 | -0.0051322 | 0.055397 | 0.028371 | -0.00077468 | -0.0012887 | 0.061323 | 0.012663 | 0.059856 | -64.5359 | 0.028878 | -66.7643 | 56.2564 | 56.1013 | 56.1612 | -66.8741 | -66.7932 | 0.018674 | -66.8964 | 56.1985 | 56.2847 | 56.1826 | -67.0011 | -0.058959 | -0.11718 | 2.2793 | 0.050868 | 0.10983 | -0.27225 | -0.21243 | -0.18596 | -0.17505 | 0.022014 | -0.081172 | 0.10478 | -0.088865 | -0.19097 | 123.0716 | 122.9165 | 122.9764 | 66.8441 | -123.2477 | 123.0137 | 123.0999 | 122.9978 | 66.8339 | -123.3747
198.2812 | 123.3307 | -66.7694 | 56.282 | 0.026589 | -0.018183 | -0.0011099 | 0.053386 | -0.0040642 | 0.056465 | 0.058893 | -0.0018437 | -0.0012887 | 0.060255 | 0.012663 | 0.059856 | -64.6 | 0.019721 | -66.7643 | 56.261 | 56.1013 | 56.1612 | -66.8741 | -66.7932 | 0.018674 | -66.8918 | 56.2031 | 56.2939 | 56.1872 | -66.9966 | -0.10474 | -0.021048 | 2.1694 | 0.005091 | 0.10983 | -0.1807 | -0.12087 | -0.22716 | -0.078919 | -0.023763 | -0.12237 | 0.10479 | 0.011846 | -0.094839 | 123.0304 | 122.8708 | 122.9306 | 66.7891 | -123.1562 | 122.9725 | 123.0633 | 122.9566 | 66.7881 | -123.2786
199.2812 | 123.3673 | -66.7786 | 56.2866 | 0.057113 | -0.016046 | -0.0032469 | 0.053386 | -0.0029952 | 0.05326 | 0.074154 | -0.00077468 | -0.00021967 | 0.061323 | 0.012663 | 0.059856 | -64.5542 | 0.0243 | -66.7597 | 56.2656 | 56.0922 | 56.1566 | -66.8787 | -66.7932 | 0.023253 | -66.8826 | 56.2031 | 56.2939 | 56.1964 | -66.9966 | -0.10016 | -0.021047 | 2.2243 | 0.018824 | 0.11898 | -0.19444 | -0.13003 | -0.218 | -0.083497 | -0.014608 | -0.10406 | 0.11394 | 0.007268 | -0.09026 | 123.0441 | 122.8707 | 122.9352 | 66.8029 | -123.1653 | 122.9817 | 123.0725 | 122.9749 | 66.8018 | -123.2832
200.2969 | 123.381 | -66.7694 | 56.3324 | 0.057113 | -0.019251 | -0.0032469 | 0.053386 | -0.0040642 | 0.056465 | 0.089415 | -0.0029117 | -0.0034247 | 0.061323 | 0.0148 | 0.059856 | -64.5496 | 0.015142 | -66.7735 | 56.261 | 56.0968 | 56.1657 | -66.865 | -66.7932 | 0.014095 | -66.8872 | 56.1985 | 56.2939 | 56.1826 | -66.992 | -0.095578 | -0.071402 | 2.2198 | -0.004065 | 0.091513 | -0.23563 | -0.16665 | -0.22258 | -0.13385 | -0.023763 | -0.11779 | 0.10479 | -0.038508 | -0.14977 | 123.0304 | 122.8662 | 122.9352 | 66.7846 | -123.1974 | 122.968 | 123.0633 | 122.952 | 66.7835 | -123.3244
201.2812 | 123.2941 | -66.8243 | 56.3187 | 0.041851 | -0.019251 | -0.0021789 | 0.052318 | -0.0051322 | 0.05326 | 0.058893 | -0.00077468 | -0.0023567 | 0.061323 | 0.015868 | 0.060925 | -64.5405 | 0.019721 | -66.7643 | 56.2656 | 56.0968 | 56.1612 | -66.8833 | -66.7886 | 0.018674 | -66.8826 | 56.2077 | 56.2939 | 56.2055 | -67.0011 | -0.058962 | -0.053091 | 2.2839 | 0.060023 | 0.11898 | -0.2219 | -0.1575 | -0.1768 | -0.11096 | 0.035748 | -0.05828 | 0.11852 | -0.024776 | -0.11315 | 123.0899 | 122.9211 | 122.9855 | 66.8441 | -123.202 | 123.032 | 123.1182 | 123.0299 | 66.843 | -123.3198
202.2812 | 123.4085 | -66.7831 | 56.3141 | 0.072375 | -0.018183 | -0.0021789 | 0.053386 | -0.0051322 | 0.052192 | 0.074154 | -0.00077468 | -0.0023567 | 0.061323 | 0.0148 | 0.05772 | -64.5908 | 0.019721 | -66.7689 | 56.261 | 56.0876 | 56.1612 | -66.8741 | -66.7886 | 0.018674 | -66.8872 | 56.2077 | 56.2939 | 56.2009 | -66.9966 | -0.091003 | -0.053092 | 2.1923 | 0.014246 | 0.10525 | -0.22648 | -0.15292 | -0.21342 | -0.10639 | -0.005451 | -0.10406 | 0.10936 | -0.020198 | -0.11315 | 123.0441 | 122.8707 | 122.9443 | 66.8029 | -123.1882 | 122.9908 | 123.077 | 122.9841 | 66.8018 | -123.3107
203.2812 | 123.2712 | -66.806 | 56.337 | 0.041851 | -0.017114 | -0.0032469 | 0.054455 | -0.0051322 | 0.054329 | 0.058893 | -0.0029117 | -0.0012887 | 0.059187 | 0.013731 | 0.060925 | -64.5268 | 0.0243 | -66.7689 | 56.261 | 56.0922 | 56.1612 | -66.8787 | -66.7886 | 0.018674 | -66.8826 | 56.2077 | 56.2939 | 56.2009 | -66.9966 | -0.072694 | -0.07598 | 2.2793 | 0.037134 | 0.10983 | -0.24479 | -0.17581 | -0.19053 | -0.12927 | 0.017437 | -0.076591 | 0.11394 | -0.043086 | -0.13604 | 123.067 | 122.8982 | 122.9672 | 66.8303 | -123.2157 | 123.0137 | 123.0999 | 123.007 | 66.8247 | -123.3335
204.2812 | 123.3078 | -66.8198 | 56.3141 | 0.026589 | -0.019251 | -0.0011099 | 0.052318 | -0.0040642 | 0.05326 | 0.043632 | -0.00077468 | -0.0012887 | 0.060255 | 0.0148 | 0.059856 | -64.5313 | 0.015142 | -66.7597 | 56.261 | 56.1013 | 56.1657 | -66.8787 | -66.7932 | 0.018674 | -66.8826 | 56.2077 | 56.303 | 56.2009 | -67.0011 | -0.058961 | -0.053092 | 2.2884 | 0.060023 | 0.11898 | -0.21274 | -0.14834 | -0.18138 | -0.10639 | 0.026591 | -0.062858 | 0.11852 | -0.011041 | -0.11315 | 123.0808 | 122.9211 | 122.9855 | 66.8349 | -123.1928 | 123.0275 | 123.1228 | 123.0207 | 66.8384 | -123.3152
205.2812 | 123.3627 | -66.7831 | 56.3141 | 0.072375 | -0.017114 | -0.0021789 | 0.053386 | -0.0040642 | 0.054329 | 0.058893 | -0.0018437 | -0.0012887 | 0.061323 | 0.015868 | 0.059856 | -64.5359 | 0.010564 | -66.7643 | 56.2564 | 56.0876 | 56.1566 | -66.8741 | -66.7886 | 0.004938 | -66.8826 | 56.1985 | 56.303 | 56.1918 | -67.0011 | -0.091003 | -0.05767 | 2.2472 | 0.018824 | 0.10983 | -0.22648 | -0.1575 | -0.218 | -0.11554 | -0.005451 | -0.099479 | 0.11852 | -0.011041 | -0.1223 | 123.0396 | 122.8707 | 122.9397 | 66.7937 | -123.1882 | 122.9817 | 123.0862 | 122.9749 | 66.7881 | -123.3152
206.2812 | 123.3673 | -66.7786 | 56.3049 | 0.057113 | -0.019251 | -0.0021789 | 0.053386 | -0.0040642 | 0.052192 | 0.074154 | -0.00077468 | -0.0034247 | 0.060255 | 0.015868 | 0.058788 | -64.5451 | 0.0243 | -66.7689 | 56.261 | 56.0876 | 56.1566 | -66.8696 | -66.784 | 0.014095 | -66.8872 | 56.2077 | 56.2939 | 56.2009 | -67.0011 | -0.091002 | -0.043937 | 2.2335 | 0.009668 | 0.10067 | -0.21733 | -0.14834 | -0.22258 | -0.09723 | -0.00545 | -0.10864 | 0.11394 | -0.011043 | -0.10399 | 123.0396 | 122.8662 | 122.9352 | 66.8029 | -123.1745 | 122.9863 | 123.0725 | 122.9795 | 66.7927 | -123.3061
207.2812 | 123.3673 | -66.806 | 56.3187 | 0.057113 | -0.017114 | -0.0021789 | 0.052318 | -0.0019272 | 0.055397 | 0.058893 | -0.0029117 | -0.00021967 | 0.060255 | 0.013731 | 0.060925 | -64.6046 | 0.019721 | -66.7643 | 56.261 | 56.0876 | 56.1566 | -66.8833 | -66.7886 | 0.014095 | -66.8872 | 56.2077 | 56.2847 | 56.2009 | -66.9966 | -0.077273 | -0.05767 | 2.2014 | 0.041712 | 0.11898 | -0.23106 | -0.16208 | -0.19053 | -0.11096 | 0.017437 | -0.08117 | 0.10936 | -0.033934 | -0.11773 | 123.067 | 122.8936 | 122.9626 | 66.8258 | -123.202 | 123.0137 | 123.0908 | 123.007 | 66.8201 | -123.3152
208.2812 | 123.2849 | -66.8427 | 56.3232 | 0.041851 | -0.017114 | -0.0032469 | 0.052318 | -0.0029952 | 0.054329 | 0.074154 | -0.0039797 | -0.0012887 | 0.059187 | 0.0148 | 0.058788 | -64.5222 | 0.0243 | -66.7689 | 56.261 | 56.0922 | 56.1703 | -66.8833 | -66.7886 | 0.009516 | -66.878 | 56.2077 | 56.2847 | 56.2009 | -67.0011 | -0.040652 | -0.062247 | 2.3205 | 0.073755 | 0.11441 | -0.23106 | -0.15292 | -0.15849 | -0.11554 | 0.054058 | -0.035392 | 0.1231 | -0.038511 | -0.1223 | 123.1036 | 122.9348 | 123.013 | 66.867 | -123.2065 | 123.0504 | 123.1274 | 123.0436 | 66.8522 | -123.3244
209.2812 | 123.262 | -66.8198 | 56.3599 | 0.072375 | -0.018183 | -0.0021789 | 0.054455 | -0.0029952 | 0.054329 | 0.043632 | -0.0018437 | -0.00021967 | 0.060255 | 0.013731 | 0.059856 | -64.5176 | 0.0243 | -66.7689 | 56.261 | 56.0922 | 56.1612 | -66.8879 | -66.7886 | 0.018674 | -66.8918 | 56.2077 | 56.2847 | 56.2101 | -66.992 | -0.068119 | -0.098868 | 2.3022 | 0.050867 | 0.11899 | -0.26768 | -0.19869 | -0.17222 | -0.15216 | 0.03117 | -0.072016 | 0.10021 | -0.075132 | -0.14977 | 123.0808 | 122.9119 | 122.9809 | 66.8441 | -123.2477 | 123.0275 | 123.1045 | 123.0299 | 66.8384 | -123.3518
210.2812 | 123.2803 | -66.8335 | 56.337 | 0.072375 | -0.019251 | -0.0021789 | 0.054455 | -0.0051322 | 0.054329 | 0.074154 | -0.00077468 | -0.0012887 | 0.059187 | 0.0148 | 0.058788 | -64.5359 | 0.0243 | -66.7643 | 56.261 | 56.0876 | 56.1612 | -66.8741 | -66.7886 | 0.018674 | -66.8918 | 56.2031 | 56.2939 | 56.2009 | -66.992 | -0.040649 | -0.07598 | 2.2976 | 0.069178 | 0.10983 | -0.24937 | -0.17581 | -0.15849 | -0.13385 | 0.044903 | -0.058283 | 0.10021 | -0.043086 | -0.13604 | 123.0945 | 122.9211 | 122.9947 | 66.8578 | -123.2111 | 123.0366 | 123.1274 | 123.0344 | 66.8522 | -123.329
211.2812 | 123.2529 | -66.8427 | 56.337 | 0.041851 | -0.018183 | -0.0021789 | 0.052318 | -0.0051322 | 0.054329 | 0.058893 | -0.0018437 | -0.0012887 | 0.060255 | 0.0148 | 0.058788 | -64.5176 | 0.019721 | -66.7689 | 56.261 | 56.0922 | 56.1612 | -66.8833 | -66.7977 | 0.018674 | -66.8918 | 56.2031 | 56.2939 | 56.2101 | -66.9966 | -0.040652 | -0.07598 | 2.3251 | 0.073755 | 0.11441 | -0.24479 | -0.17581 | -0.15391 | -0.13385 | 0.044901 | -0.049128 | 0.10479 | -0.043086 | -0.12688 | 123.1036 | 122.9348 | 123.0038 | 66.8624 | -123.2203 | 123.0458 | 123.1365 | 123.0527 | 66.8613 | -123.3335
212.2812 | 123.3765 | -66.7694 | 56.3095 | 0.057113 | -0.018183 | -0.0021789 | 0.050181 | -0.0040642 | 0.054329 | 0.058893 | -0.0018437 | -0.0023567 | 0.062391 | 0.0148 | 0.058788 | -64.6183 | 0.019721 | -66.7643 | 56.261 | 56.0876 | 56.1612 | -66.8833 | -66.7886 | 0.027831 | -66.8918 | 56.2031 | 56.2847 | 56.1964 | -67.0011 | -0.11389 | -0.048514 | 2.1511 | 0.005091 | 0.11898 | -0.2219 | -0.14834 | -0.23173 | -0.10638 | -0.019184 | -0.12237 | 0.10936 | -0.024778 | -0.11315 | 123.0304 | 122.857 | 122.9306 | 66.7891 | -123.1928 | 122.9725 | 123.0541 | 122.9658 | 66.7972 | -123.3107
213.2812 | 123.23 | -66.8243 | 56.3782 | 0.072375 | -0.017114 | -0.0043149 | 0.052318 | -0.0029952 | 0.054329 | 0.058893 | -0.0018437 | -0.0023567 | 0.061323 | 0.0148 | 0.059856 | -64.5313 | 0.015142 | -66.7643 | 56.2747 | 56.0922 | 56.1566 | -66.8787 | -66.7932 | 0.018674 | -66.8918 | 56.2077 | 56.2802 | 56.2101 | -67.0011 | -0.054383 | -0.10344 | 2.293 | 0.060023 | 0.11441 | -0.28599 | -0.22159 | -0.1768 | -0.17047 | 0.031169 | -0.067438 | 0.10936 | -0.098021 | -0.16808 | 123.0991 | 122.9165 | 122.9809 | 66.8395 | -123.2569 | 123.032 | 123.1045 | 123.0344 | 66.843 | -123.3793
214.3125 | 123.4177 | -66.7465 | 56.2912 | 0.057113 | -0.018183 | -0.0011099 | 0.052318 | -0.0051322 | 0.054329 | 0.043632 | -0.0018437 | -0.0034247 | 0.061323 | 0.013731 | 0.059856 | -64.5908 | 0.0243 | -66.7689 | 56.261 | 56.0968 | 56.1657 | -66.8741 | -66.784 | 0.009516 | -66.8826 | 56.1985 | 56.2847 | 56.2055 | -67.0011 | -0.12762 | -0.030204 | 2.1557 | -0.022375 | 0.10525 | -0.19443 | -0.12545 | -0.25462 | -0.092654 | -0.037493 | -0.1361 | 0.11852 | -0.006468 | -0.085681 | 123.0075 | 122.8433 | 122.9123 | 66.7708 | -123.1653 | 122.9451 | 123.0313 | 122.952 | 66.756 | -123.2923
215.2812 | 123.262 | -66.806 | 56.337 | 0.087637 | -0.018183 | -0.0011099 | 0.052318 | -0.0040642 | 0.054329 | 0.089415 | -0.0029117 | -0.0012887 | 0.060255 | 0.0148 | 0.05772 | -64.513 | 0.019721 | -66.7689 | 56.261 | 56.0968 | 56.1703 | -66.8879 | -66.784 | 0.018674 | -66.8826 | 56.2077 | 56.2985 | 56.2055 | -66.992 | -0.081852 | -0.07598 | 2.293 | 0.037134 | 0.11899 | -0.24021 | -0.16665 | -0.18596 | -0.12927 | 0.022016 | -0.076591 | 0.10936 | -0.038508 | -0.13146 | 123.067 | 122.9028 | 122.9764 | 66.8258 | -123.2249 | 123.0137 | 123.1045 | 123.0115 | 66.8247 | -123.329
216.2812 | 123.2986 | -66.7923 | 56.3507 | 0.057113 | -0.018183 | -0.0021789 | 0.052318 | -0.0051322 | 0.054329 | 0.074154 | -0.0018437 | -0.0012887 | 0.059187 | 0.0148 | 0.058788 | -64.513 | 0.028878 | -66.7689 | 56.2702 | 56.1013 | 56.1749 | -66.8879 | -66.784 | 0.023253 | -66.8872 | 56.2077 | 56.2893 | 56.2101 | -67.0011 | -0.095585 | -0.080556 | 2.2793 | 0.023401 | 0.11899 | -0.24937 | -0.1758 | -0.20885 | -0.14301 | 0.008283 | -0.094903 | 0.11394 | -0.061398 | -0.14061 | 123.0624 | 122.8936 | 122.9672 | 66.8212 | -123.2386 | 123 | 123.0816 | 123.0024 | 66.8156 | -123.3519
217.2812 | 123.3902 | -66.806 | 56.2912 | 0.026589 | -0.018183 | -0.0032469 | 0.054455 | -0.0029952 | 0.054329 | 0.074154 | -0.00077468 | -0.00021967 | 0.060255 | 0.016936 | 0.05772 | -64.5496 | 0.015142 | -66.7689 | 56.2702 | 56.0968 | 56.1566 | -66.8833 | -66.784 | 0.014095 | -66.8918 | 56.1985 | 56.2985 | 56.2009 | -67.0011 | -0.077273 | -0.021047 | 2.2564 | 0.037134 | 0.11441 | -0.19443 | -0.13461 | -0.19511 | -0.092654 | 0.022016 | -0.085749 | 0.10936 | 0.007268 | -0.09026 | 123.0762 | 122.9028 | 122.9626 | 66.8212 | -123.1745 | 123.0046 | 123.1045 | 123.007 | 66.8201 | -123.2923
218.2812 | 123.2849 | -66.8472 | 56.3278 | 0.057113 | -0.019251 | -0.0021789 | 0.052318 | -0.0072692 | 0.052192 | 0.058893 | -0.0029117 | -0.0023567 | 0.058119 | 0.015868 | 0.060925 | -64.5268 | 0.019721 | -66.7643 | 56.2564 | 56.1013 | 56.1612 | -66.8833 | -66.7886 | 0.014095 | -66.8826 | 56.1985 | 56.2939 | 56.1872 | -67.0103 | -0.036074 | -0.071403 | 2.3205 | 0.082911 | 0.11898 | -0.22648 | -0.16665 | -0.16307 | -0.12927 | 0.058636 | -0.035392 | 0.12768 | -0.033931 | -0.14062 | 123.1036 | 122.9486 | 123.0084 | 66.867 | -123.2111 | 123.0458 | 123.1411 | 123.0344 | 66.8613 | -123.3381
219.2812 | 123.2849 | -66.7877 | 56.3599 | 0.087637 | -0.019251 | -0.0011099 | 0.053386 | -0.0051322 | 0.054329 | 0.074154 | -0.0018437 | -0.0034247 | 0.060255 | 0.015868 | 0.059856 | -64.5451 | 0.019721 | -66.7643 | 56.2656 | 56.0922 | 56.1703 | -66.865 | -66.784 | 0.018674 | -66.8918 | 56.1985 | 56.2939 | 56.2055 | -67.0057 | -0.077267 | -0.094289 | 2.2427 | 0.023402 | 0.10067 | -0.26768 | -0.18954 | -0.218 | -0.16132 | 0.003706 | -0.10406 | 0.11394 | -0.065974 | -0.15434 | 123.0533 | 122.8799 | 122.958 | 66.8074 | -123.2249 | 122.9863 | 123.0816 | 122.9932 | 66.8064 | -123.3656
220.2812 | 123.2666 | -66.8655 | 56.337 | 0.041851 | -0.02032 | -0.0021789 | 0.053386 | -0.0051322 | 0.05326 | 0.058893 | -0.0029117 | -0.0023567 | 0.060255 | 0.015868 | 0.058788 | -64.5496 | 0.019721 | -66.7643 | 56.2702 | 56.0922 | 56.1657 | -66.8879 | -66.7932 | 0.014095 | -66.8918 | 56.2031 | 56.2939 | 56.2101 | -66.9966 | -0.022342 | -0.066823 | 2.3159 | 0.10122 | 0.12356 | -0.24479 | -0.17123 | -0.13103 | -0.13385 | 0.072368 | -0.026239 | 0.10479 | -0.043086 | -0.12688 | 123.1357 | 122.9577 | 123.0313 | 66.8853 | -123.2249 | 123.0687 | 123.1594 | 123.0756 | 66.8796 | -123.3335
221.2812 | 123.317 | -66.8289 | 56.3461 | 0.072375 | -0.02032 | -0.0032469 | 0.054455 | -0.0062002 | 0.05326 | 0.074154 | -0.0029117 | -0.0034247 | 0.060255 | 0.015868 | 0.058788 | -64.5451 | 0.0243 | -66.7689 | 56.2564 | 56.0968 | 56.1612 | -66.8833 | -66.7932 | 0.014095 | -66.8918 | 56.2031 | 56.2939 | 56.2101 | -66.992 | -0.054385 | -0.089713 | 2.2839 | 0.060022 | 0.11441 | -0.24937 | -0.18496 | -0.16307 | -0.14301 | 0.035746 | -0.062861 | 0.10021 | -0.052241 | -0.13603 | 123.0853 | 122.9257 | 122.9901 | 66.8532 | -123.2294 | 123.032 | 123.1228 | 123.039 | 66.843 | -123.3381
222.2812 | 123.2849 | -66.806 | 56.3416 | 0.057113 | -0.019251 | -0.0021789 | 0.052318 | -0.0029952 | 0.056465 | 0.074154 | -0.0018437 | -0.0034247 | 0.060255 | 0.016936 | 0.059856 | -64.5771 | 0.0243 | -66.7643 | 56.261 | 56.0876 | 56.1612 | -66.8787 | -66.7886 | 0.018674 | -66.8918 | 56.2031 | 56.2893 | 56.1964 | -67.0057 | -0.072694 | -0.080558 | 2.2289 | 0.041712 | 0.11441 | -0.25395 | -0.18038 | -0.19969 | -0.13843 | 0.017437 | -0.085749 | 0.11394 | -0.052243 | -0.14519 | 123.067 | 122.8936 | 122.9672 | 66.8303 | -123.2203 | 123.0092 | 123.0953 | 123.0024 | 66.8247 | -123.3473
223.2812 | 123.2803 | -66.8152 | 56.3507 | 0.057113 | -0.02032 | -0.0021789 | 0.052318 | -0.0051322 | 0.05326 | 0.058893 | -0.00077468 | -0.0012887 | 0.062391 | 0.016936 | 0.058788 | -64.5451 | 0.028878 | -66.7689 | 56.2702 | 56.0968 | 56.1612 | -66.8879 | -66.7886 | 0.018674 | -66.8872 | 56.1985 | 56.2893 | 56.2055 | -66.9966 | -0.072696 | -0.080556 | 2.2701 | 0.04629 | 0.11899 | -0.25394 | -0.18954 | -0.18138 | -0.15216 | 0.026593 | -0.072014 | 0.10936 | -0.061398 | -0.14519 | 123.0853 | 122.9119 | 122.9764 | 66.8441 | -123.2386 | 123.0137 | 123.1045 | 123.0207 | 66.8339 | -123.3473
224.2812 | 123.2895 | -66.8015 | 56.3553 | 0.041851 | -0.02032 | -0.0021789 | 0.054455 | -0.0019272 | 0.054329 | 0.043632 | -0.0029117 | -0.0012887 | 0.060255 | 0.018005 | 0.059856 | -64.5634 | 0.0243 | -66.7643 | 56.2564 | 56.1013 | 56.1612 | -66.8787 | -66.7932 | 0.014095 | -66.8826 | 56.2077 | 56.2939 | 56.2147 | -67.0011 | -0.077271 | -0.098869 | 2.2381 | 0.037135 | 0.11441 | -0.25394 | -0.19412 | -0.19969 | -0.14758 | 0.008281 | -0.081168 | 0.11852 | -0.061397 | -0.14061 | 123.0579 | 122.9028 | 122.9626 | 66.8258 | -123.234 | 123.0092 | 123.0953 | 123.0161 | 66.8155 | -123.3564
225.2812 | 123.2941 | -66.7877 | 56.3599 | 0.072375 | -0.019251 | -0.0043149 | 0.052318 | -0.0040642 | 0.055397 | 0.089415 | -0.0029117 | -0.0012887 | 0.061323 | 0.016936 | 0.059856 | -64.5496 | 0.019721 | -66.7643 | 56.261 | 56.0968 | 56.1703 | -66.8787 | -66.7886 | 0.018674 | -66.8872 | 56.2123 | 56.2893 | 56.2101 | -67.0011 | -0.091004 | -0.098868 | 2.2381 | 0.023402 | 0.11441 | -0.2631 | -0.18954 | -0.21342 | -0.14758 | -0.000873 | -0.09948 | 0.11394 | -0.070553 | -0.14977 | 123.0487 | 122.8845 | 122.958 | 66.8074 | -123.2386 | 123 | 123.077 | 122.9978 | 66.8064 | -123.361
226.2812 | 123.3215 | -66.8152 | 56.3232 | 0.041851 | -0.021388 | -0.0011099 | 0.053386 | -0.0051322 | 0.054329 | 0.058893 | -0.0029117 | -0.00021967 | 0.061323 | 0.015868 | 0.058788 | -64.5496 | 0.0243 | -66.7643 | 56.261 | 56.0968 | 56.1657 | -66.8833 | -66.7932 | 0.014095 | -66.8826 | 56.2077 | 56.2985 | 56.1918 | -67.0057 | -0.068117 | -0.062247 | 2.2655 | 0.050868 | 0.11898 | -0.22648 | -0.1575 | -0.19054 | -0.11554 | 0.022014 | -0.067435 | 0.1231 | -0.024775 | -0.13146 | 123.0762 | 122.9119 | 122.9809 | 66.8395 | -123.2065 | 123.0229 | 123.1137 | 123.007 | 66.8293 | -123.329
227.2812 | 123.3536 | -66.7877 | 56.3187 | 0.041851 | -0.022456 | -0.0032469 | 0.053386 | -0.0040642 | 0.05326 | 0.074154 | -0.0018437 | -0.0012887 | 0.060255 | 0.018005 | 0.058788 | -64.5954 | 0.028878 | -66.7597 | 56.261 | 56.0922 | 56.1612 | -66.8696 | -66.7794 | 0.018674 | -66.8918 | 56.2031 | 56.2893 | 56.2009 | -66.9966 | -0.081846 | -0.05767 | 2.1923 | 0.02798 | 0.10983 | -0.22648 | -0.1575 | -0.20885 | -0.11554 | 0.008284 | -0.10406 | 0.10479 | -0.029355 | -0.11773 | 123.0487 | 122.8799 | 122.9489 | 66.8166 | -123.1882 | 122.9908 | 123.077 | 122.9887 | 66.8064 | -123.3152
228.2812 | 123.3536 | -66.806 | 56.3049 | 0.072375 | -0.021388 | -0.0011099 | 0.051249 | -0.0040642 | 0.052192 | 0.058893 | -0.00077468 | -0.0023567 | 0.062391 | 0.016936 | 0.05772 | -64.6229 | 0.0243 | -66.7597 | 56.261 | 56.0922 | 56.1612 | -66.8696 | -66.7886 | 0.018674 | -66.8918 | 56.2031 | 56.2893 | 56.1964 | -66.9966 | -0.063536 | -0.043937 | 2.1831 | 0.04629 | 0.10983 | -0.21275 | -0.14376 | -0.19053 | -0.10181 | 0.017437 | -0.085749 | 0.10479 | -0.015622 | -0.10857 | 123.067 | 122.8982 | 122.9672 | 66.8303 | -123.1745 | 123.0092 | 123.0953 | 123.0024 | 66.8247 | -123.3015
229.2812 | 123.2529 | -66.8243 | 56.369 | 0.072375 | -0.021388 | -0.0032469 | 0.052318 | -0.0062002 | 0.055397 | 0.043632 | -0.0029117 | -0.00021967 | 0.062391 | 0.019073 | 0.05772 | -64.568 | 0.0243 | -66.7643 | 56.261 | 56.1013 | 56.1612 | -66.8833 | -66.7932 | 0.014095 | -66.8826 | 56.2031 | 56.2939 | 56.2055 | -66.9966 | -0.058962 | -0.10802 | 2.2564 | 0.060023 | 0.11898 | -0.26768 | -0.20785 | -0.17222 | -0.16589 | 0.031169 | -0.05828 | 0.11394 | -0.07513 | -0.1635 | 123.0853 | 122.9257 | 122.9855 | 66.8486 | -123.2523 | 123.0275 | 123.1182 | 123.0299 | 66.8384 | -123.3656
230.2812 | 123.3215 | -66.7831 | 56.3553 | 0.057113 | -0.021388 | -0.0032469 | 0.051249 | -0.0062002 | 0.054329 | 0.074154 | -0.0018437 | -0.0012887 | 0.059187 | 0.016936 | 0.058788 | -64.5496 | 0.019721 | -66.7643 | 56.261 | 56.0968 | 56.1657 | -66.8696 | -66.7886 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.2009 | -67.0011 | -0.086424 | -0.094291 | 2.2335 | 0.018824 | 0.10525 | -0.25852 | -0.18954 | -0.218 | -0.15216 | -0.005451 | -0.10406 | 0.11394 | -0.061397 | -0.15435 | 123.0441 | 122.8799 | 122.9489 | 66.8029 | -123.2249 | 122.9863 | 123.077 | 122.9841 | 66.7972 | -123.3564
231.2812 | 123.2895 | -66.7969 | 56.3599 | 0.072375 | -0.02032 | -0.0011099 | 0.053386 | -0.0029952 | 0.05326 | 0.074154 | -0.0029117 | -0.0023567 | 0.060255 | 0.016936 | 0.058788 | -64.5771 | 0.0243 | -66.7597 | 56.2656 | 56.0968 | 56.1566 | -66.8833 | -66.784 | 0.014095 | -66.8872 | 56.1985 | 56.2847 | 56.1826 | -66.992 | -0.086428 | -0.094289 | 2.2198 | 0.037135 | 0.12356 | -0.2631 | -0.20327 | -0.19511 | -0.16132 | 0.012861 | -0.090325 | 0.10479 | -0.075132 | -0.17724 | 123.0624 | 122.8936 | 122.9535 | 66.8212 | -123.2432 | 122.9954 | 123.0816 | 122.9795 | 66.811 | -123.3518
232.2812 | 123.3032 | -66.8152 | 56.3599 | 0.072375 | -0.021388 | -0.0021789 | 0.053386 | -0.0051322 | 0.054329 | 0.074154 | -0.0039797 | -0.0023567 | 0.060255 | 0.016936 | 0.05772 | -64.5451 | 0.019721 | -66.7689 | 56.2656 | 56.0968 | 56.1612 | -66.8741 | -66.784 | 0.014095 | -66.8918 | 56.2077 | 56.2939 | 56.2193 | -67.0011 | -0.058959 | -0.094289 | 2.2701 | 0.04629 | 0.10525 | -0.2631 | -0.19869 | -0.18596 | -0.15216 | 0.031172 | -0.076593 | 0.10936 | -0.065974 | -0.14061 | 123.0808 | 122.9119 | 122.9764 | 66.8349 | -123.234 | 123.0229 | 123.1091 | 123.0344 | 66.8293 | -123.361
233.2812 | 123.2574 | -66.8152 | 56.3599 | 0.041851 | -0.022456 | -0.0021789 | 0.049112 | -0.0051322 | 0.055397 | 0.058893 | -0.0029117 | -0.0012887 | 0.059187 | 0.016936 | 0.059856 | -64.5634 | 0.028878 | -66.7597 | 56.261 | 56.0968 | 56.1657 | -66.8741 | -66.7886 | 0.014095 | -66.8826 | 56.2031 | 56.2893 | 56.2009 | -66.9966 | -0.058959 | -0.098868 | 2.2518 | 0.055446 | 0.11441 | -0.2631 | -0.19412 | -0.18138 | -0.15674 | 0.026593 | -0.067435 | 0.11394 | -0.070553 | -0.15892 | 123.0762 | 122.9119 | 122.9809 | 66.8441 | -123.234 | 123.0183 | 123.1045 | 123.0161 | 66.8293 | -123.3564
234.2812 | 123.2849 | -66.8106 | 56.3736 | 0.057113 | -0.021388 | -0.0032469 | 0.053386 | -0.0040642 | 0.054329 | 0.043632 | -0.00077468 | -0.0023567 | 0.060255 | 0.016936 | 0.05772 | -64.5725 | 0.0243 | -66.7643 | 56.261 | 56.0968 | 56.1612 | -66.8787 | -66.7886 | 0.009516 | -66.8872 | 56.2077 | 56.2847 | 56.2101 | -66.9966 | -0.068116 | -0.1126 | 2.2381 | 0.04629 | 0.11441 | -0.27683 | -0.21243 | -0.18596 | -0.16589 | 0.022015 | -0.076592 | 0.10936 | -0.088865 | -0.1635 | 123.0716 | 122.9074 | 122.9718 | 66.8349 | -123.2523 | 123.0183 | 123.0953 | 123.0207 | 66.8201 | -123.3702
235.2812 | 123.2849 | -66.7923 | 56.3736 | 0.072375 | -0.02032 | -0.0011099 | 0.052318 | -0.0040642 | 0.052192 | 0.058893 | -0.0029117 | -0.0012887 | 0.059187 | 0.018005 | 0.058788 | -64.5542 | 0.0243 | -66.7597 | 56.261 | 56.1013 | 56.1657 | -66.8879 | -66.7932 | 0.014095 | -66.8872 | 56.2123 | 56.2939 | 56.2147 | -67.0057 | -0.095585 | -0.1126 | 2.2381 | 0.032557 | 0.12814 | -0.27225 | -0.20785 | -0.21343 | -0.16132 | -0.000875 | -0.094903 | 0.11852 | -0.079707 | -0.15892 | 123.0533 | 122.8936 | 122.958 | 66.8166 | -123.2615 | 123.0046 | 123.0862 | 123.007 | 66.8064 | -123.3793
236.2812 | 123.3719 | -66.7694 | 56.3553 | 0.057113 | -0.02032 | -0.0011099 | 0.052318 | -0.0062002 | 0.054329 | 0.074154 | -0.00077468 | -0.0012887 | 0.05705 | 0.016936 | 0.05772 | -64.5908 | 0.019721 | -66.7643 | 56.2656 | 56.0968 | 56.1612 | -66.8833 | -66.784 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.2055 | -67.0057 | -0.11389 | -0.089712 | 2.1786 | 0.005091 | 0.11898 | -0.25852 | -0.19412 | -0.23631 | -0.15216 | -0.014605 | -0.11779 | 0.11852 | -0.061397 | -0.14977 | 123.035 | 122.8662 | 122.9306 | 66.7891 | -123.2386 | 122.9725 | 123.0633 | 122.9749 | 66.7835 | -123.361
237.2812 | 123.2529 | -66.8106 | 56.3553 | 0.057113 | -0.022456 | -0.0021789 | 0.054455 | -0.0062002 | 0.054329 | 0.089415 | -0.00077468 | -0.0034247 | 0.058119 | 0.015868 | 0.056652 | -64.5634 | 0.0243 | -66.7643 | 56.2564 | 56.1013 | 56.1657 | -66.8787 | -66.7932 | 0.018674 | -66.8918 | 56.2031 | 56.2985 | 56.2009 | -67.0011 | -0.068116 | -0.098869 | 2.2472 | 0.04629 | 0.11441 | -0.25394 | -0.18954 | -0.19053 | -0.15216 | 0.017436 | -0.081171 | 0.10936 | -0.056819 | -0.15435 | 123.067 | 122.912 | 122.9764 | 66.8349 | -123.234 | 123.0137 | 123.1091 | 123.0115 | 66.8293 | -123.3564
238.2812 | 123.262 | -66.7969 | 56.3736 | 0.072375 | -0.023525 | -0.0011099 | 0.052318 | -0.0062002 | 0.05326 | 0.043632 | -0.00077468 | -0.0034247 | 0.058119 | 0.015868 | 0.059856 | -64.5634 | 0.019721 | -66.7597 | 56.261 | 56.0968 | 56.1657 | -66.8879 | -66.7886 | 0.014095 | -66.8918 | 56.1985 | 56.2939 | 56.2147 | -66.9966 | -0.091007 | -0.1126 | 2.2335 | 0.037135 | 0.12814 | -0.27683 | -0.20785 | -0.19969 | -0.17505 | 0.008282 | -0.094904 | 0.10479 | -0.079707 | -0.15892 | 123.0579 | 122.8936 | 122.9626 | 66.8166 | -123.2615 | 122.9954 | 123.0908 | 123.0115 | 66.811 | -123.3702
239.2812 | 123.2712 | -66.8015 | 56.3507 | 0.072375 | -0.022456 | -0.0011099 | 0.053386 | -0.0062002 | 0.05326 | 0.074154 | -0.0029117 | -0.0023567 | 0.061323 | 0.016936 | 0.058788 | -64.5405 | 0.019721 | -66.7597 | 56.2656 | 56.0968 | 56.1657 | -66.897 | -66.784 | 0.014095 | -66.878 | 56.2031 | 56.2939 | 56.2147 | -67.0011 | -0.095587 | -0.085134 | 2.261 | 0.041713 | 0.1373 | -0.25394 | -0.18496 | -0.19969 | -0.14758 | 0.017439 | -0.07659 | 0.1231 | -0.056819 | -0.13603 | 123.067 | 122.8982 | 122.9672 | 66.8212 | -123.2477 | 123.0046 | 123.0953 | 123.0161 | 66.8155 | -123.3519
240.2812 | 123.3765 | -66.7603 | 56.3507 | 0.057113 | -0.022456 | -0.0032469 | 0.053386 | -0.0051322 | 0.054329 | 0.074154 | -0.0029117 | -0.0023567 | 0.060255 | 0.018005 | 0.058788 | -64.6 | 0.019721 | -66.7643 | 56.2656 | 56.1013 | 56.1566 | -66.8741 | -66.7932 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.2009 | -67.0011 | -0.11389 | -0.085134 | 2.1602 | -0.004064 | 0.10983 | -0.24937 | -0.19412 | -0.24089 | -0.14758 | -0.032918 | -0.12695 | 0.11394 | -0.056819 | -0.14977 | 123.0258 | 122.8616 | 122.9168 | 66.78 | -123.2249 | 122.9634 | 123.0541 | 122.9612 | 66.7743 | -123.3519
241.2969 | 123.2391 | -66.8381 | 56.3324 | 0.041851 | -0.023525 | -0.0032469 | 0.052318 | -0.0040642 | 0.052192 | 0.043632 | -0.0029117 | -0.0044937 | 0.059187 | 0.016936 | 0.059856 | -64.5725 | 0.019721 | -66.7643 | 56.2564 | 56.0968 | 56.1657 | -66.8833 | -66.7886 | 0.018674 | -66.878 | 56.2031 | 56.2893 | 56.2055 | -67.0103 | -0.045229 | -0.07598 | 2.2655 | 0.073756 | 0.11898 | -0.23563 | -0.16665 | -0.17223 | -0.12927 | 0.049481 | -0.039969 | 0.13226 | -0.043087 | -0.12688 | 123.0945 | 122.9348 | 123.0038 | 66.8578 | -123.2157 | 123.0412 | 123.1274 | 123.0436 | 66.8567 | -123.3427
242.2812 | 123.2849 | -66.8106 | 56.3507 | 0.057113 | -0.02032 | -0.0032469 | 0.053386 | -0.0051322 | 0.055397 | 0.058893 | -0.0029117 | -0.0012887 | 0.060255 | 0.018005 | 0.056652 | -64.5542 | 0.019721 | -66.7643 | 56.261 | 56.0922 | 56.1657 | -66.8741 | -66.784 | 0.009516 | -66.8918 | 56.2077 | 56.2893 | 56.2101 | -67.0057 | -0.063537 | -0.089713 | 2.2564 | 0.04629 | 0.10983 | -0.25852 | -0.18496 | -0.19511 | -0.14301 | 0.026594 | -0.081171 | 0.11394 | -0.061398 | -0.14061 | 123.0716 | 122.9028 | 122.9764 | 66.8303 | -123.2249 | 123.0183 | 123.0999 | 123.0207 | 66.8201 | -123.3564
243.2812 | 123.2941 | -66.7877 | 56.3324 | 0.057113 | -0.022456 | -0.0043149 | 0.051249 | -0.0051322 | 0.054329 | 0.074154 | -0.0018437 | -0.0023567 | 0.059187 | 0.020141 | 0.05772 | -64.5771 | 0.015142 | -66.7643 | 56.261 | 56.0968 | 56.1795 | -66.865 | -66.784 | 0.014095 | -66.8826 | 56.1985 | 56.2985 | 56.2009 | -66.9966 | -0.077267 | -0.071402 | 2.2106 | 0.023402 | 0.10067 | -0.23563 | -0.15292 | -0.20885 | -0.13385 | 0.003706 | -0.094901 | 0.11394 | -0.03393 | -0.13146 | 123.0487 | 122.8845 | 122.9672 | 66.8029 | -123.1974 | 122.9863 | 123.0862 | 122.9887 | 66.8018 | -123.329
244.2812 | 123.3994 | -66.7603 | 56.3324 | 0.057113 | -0.021388 | -0.0021789 | 0.052318 | -0.0040642 | 0.055397 | 0.058893 | -0.0029117 | -0.0012887 | 0.060255 | 0.018005 | 0.05772 | -64.6366 | 0.019721 | -66.7597 | 56.261 | 56.1013 | 56.1703 | -66.8696 | -66.7886 | 0.004938 | -66.8826 | 56.2031 | 56.2893 | 56.2009 | -67.0011 | -0.10931 | -0.071402 | 2.1236 | 0.000514 | 0.10983 | -0.23105 | -0.16207 | -0.24089 | -0.12927 | -0.028339 | -0.12237 | 0.11852 | -0.043087 | -0.13146 | 123.0212 | 122.8616 | 122.9306 | 66.78 | -123.202 | 122.9634 | 123.0496 | 122.9612 | 66.7652 | -123.3335
245.2812 | 123.4039 | -66.7694 | 56.3141 | 0.041851 | -0.022456 | -0.0032469 | 0.051249 | -0.0040642 | 0.05326 | 0.089415 | -0.0029117 | -0.0012887 | 0.059187 | 0.018005 | 0.056652 | -64.6275 | 0.019721 | -66.7643 | 56.261 | 56.0968 | 56.1612 | -66.8696 | -66.7794 | 0.014095 | -66.8872 | 56.2077 | 56.2939 | 56.2055 | -67.0011 | -0.10016 | -0.053092 | 2.1419 | 0.005091 | 0.10525 | -0.21732 | -0.15292 | -0.23173 | -0.10639 | -0.010027 | -0.11779 | 0.11394 | -0.020198 | -0.10857 | 123.0304 | 122.8662 | 122.9306 | 66.7891 | -123.1837 | 122.9771 | 123.0633 | 122.9749 | 66.7835 | -123.3152
246.2812 | 123.2437 | -66.8015 | 56.3644 | 0.087637 | -0.022456 | -0.0032469 | 0.053386 | -0.0040642 | 0.054329 | 0.058893 | -0.0029117 | -0.0023567 | 0.059187 | 0.018005 | 0.058788 | -64.5634 | 0.015142 | -66.7597 | 56.2702 | 56.0968 | 56.1703 | -66.865 | -66.7886 | 0.014095 | -66.8826 | 56.2123 | 56.2939 | 56.2101 | -66.9966 | -0.063534 | -0.094289 | 2.2381 | 0.041713 | 0.10525 | -0.26768 | -0.19412 | -0.19511 | -0.15216 | 0.01286 | -0.081168 | 0.11394 | -0.070552 | -0.15434 | 123.0716 | 122.8982 | 122.9718 | 66.8166 | -123.2294 | 123.0137 | 123.0953 | 123.0115 | 66.8155 | -123.361
247.2812 | 123.262 | -66.8106 | 56.3644 | 0.057113 | -0.022456 | -0.0032469 | 0.052318 | -0.0051322 | 0.054329 | 0.074154 | -0.0039797 | -0.0034247 | 0.059187 | 0.018005 | 0.059856 | -64.5588 | 0.019721 | -66.7597 | 56.261 | 56.0922 | 56.1657 | -66.8787 | -66.7886 | 0.018674 | -66.8918 | 56.2077 | 56.2939 | 56.2101 | -67.0057 | -0.068116 | -0.10345 | 2.2518 | 0.050868 | 0.11898 | -0.27226 | -0.1987 | -0.19511 | -0.15674 | 0.022015 | -0.081171 | 0.11394 | -0.070552 | -0.15434 | 123.0716 | 122.9028 | 122.9764 | 66.8303 | -123.2432 | 123.0183 | 123.1045 | 123.0207 | 66.8293 | -123.3702
248.2812 | 123.3719 | -66.7877 | 56.3187 | 0.072375 | -0.024593 | -0.0021789 | 0.049112 | -0.0051322 | 0.051124 | 0.10468 | -0.0018437 | -0.0012887 | 0.060255 | 0.019073 | 0.058788 | -64.6458 | 0.015142 | -66.7643 | 56.261 | 56.0922 | 56.1657 | -66.8787 | -66.7886 | 0.018674 | -66.8918 | 56.2077 | 56.2939 | 56.2055 | -66.9966 | -0.091004 | -0.05767 | 2.1419 | 0.023402 | 0.11441 | -0.22648 | -0.15292 | -0.20885 | -0.11096 | -0.000873 | -0.10406 | 0.10479 | -0.024776 | -0.11315 | 123.0487 | 122.8799 | 122.9535 | 66.8029 | -123.1974 | 122.9954 | 123.0816 | 122.9932 | 66.8064 | -123.3152
249.2812 | 123.3627 | -66.7877 | 56.3461 | 0.072375 | -0.022456 | -0.0032469 | 0.051249 | -0.0051322 | 0.054329 | 0.074154 | -0.0039797 | -0.0012887 | 0.059187 | 0.018005 | 0.056652 | -64.6412 | 0.019721 | -66.7643 | 56.2702 | 56.0968 | 56.1657 | -66.8696 | -66.7886 | 0.018674 | -66.8918 | 56.2077 | 56.2893 | 56.2009 | -66.9966 | -0.081846 | -0.075978 | 2.1465 | 0.023402 | 0.10525 | -0.24937 | -0.18038 | -0.20885 | -0.13843 | -0.000873 | -0.10406 | 0.10479 | -0.05682 | -0.14519 | 123.0579 | 122.8845 | 122.9535 | 66.8074 | -123.2157 | 122.9954 | 123.077 | 122.9887 | 66.8064 | -123.3427
250.2812 | 123.436 | -66.7511 | 56.3828 | 0.057113 | -0.023525 | -0.0021789 | 0.052318 | -0.0040642 | 0.05326 | 0.043632 | 0.00029332 | -0.0012887 | 0.060255 | 0.018005 | 0.058788 | -64.6229 | 0.015142 | -66.7597 | 56.261 | 56.0968 | 56.1657 | -66.8833 | -66.7932 | 0.014095 | -66.8918 | 56.1985 | 56.2939 | 56.2055 | -67.0103 | -0.1322 | -0.12176 | 2.1282 | -0.008641 | 0.12356 | -0.28599 | -0.21701 | -0.2592 | -0.18421 | -0.042073 | -0.14068 | 0.11852 | -0.088862 | -0.17723 | 123.0121 | 122.8479 | 122.9168 | 66.7662 | -123.2661 | 122.9496 | 123.045 | 122.9566 | 66.7652 | -123.3931
251.2812 | 123.3856 | -66.7511 | 56.3324 | 0.087637 | -0.022456 | -0.0032469 | 0.052318 | -0.0051322 | 0.05326 | 0.089415 | -0.0029117 | -0.0034247 | 0.058119 | 0.020141 | 0.05772 | -64.6 | 0.015142 | -66.7643 | 56.2564 | 56.0968 | 56.1657 | -66.8741 | -66.7794 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.1964 | -67.0057 | -0.12305 | -0.07598 | 2.1511 | -0.013219 | 0.10983 | -0.23563 | -0.16665 | -0.25462 | -0.12927 | -0.028337 | -0.1361 | 0.11852 | -0.038508 | -0.13604 | 123.0075 | 122.8479 | 122.9168 | 66.7662 | -123.2065 | 122.9542 | 123.045 | 122.9475 | 66.7652 | -123.3381
252.2812 | 123.3902 | -66.7694 | 56.3324 | 0.057113 | -0.023525 | -0.0021789 | 0.053386 | -0.0040642 | 0.05326 | 0.10468 | -0.0029117 | -0.0023567 | 0.059187 | 0.020141 | 0.058788 | -64.6321 | 0.019721 | -66.7689 | 56.261 | 56.1013 | 56.1703 | -66.8833 | -66.7932 | 0.018674 | -66.8872 | 56.2031 | 56.2939 | 56.2101 | -67.0011 | -0.11389 | -0.071402 | 2.1374 | 0.000513 | 0.11441 | -0.23105 | -0.16207 | -0.23173 | -0.12927 | -0.023763 | -0.11779 | 0.11394 | -0.038508 | -0.1223 | 123.0304 | 122.8708 | 122.9397 | 66.7891 | -123.2157 | 122.9725 | 123.0633 | 122.9795 | 66.7881 | -123.3335
253.2812 | 123.3719 | -66.7603 | 56.3278 | 0.057113 | -0.023525 | -0.0053839 | 0.052318 | -0.0040642 | 0.05326 | 0.089415 | -0.0018437 | -0.0044937 | 0.059187 | 0.020141 | 0.058788 | -64.6366 | 0.015142 | -66.7643 | 56.261 | 56.0968 | 56.1657 | -66.8879 | -66.7886 | 0.009516 | -66.8872 | 56.194 | 56.2985 | 56.2101 | -67.0011 | -0.12763 | -0.066825 | 2.1236 | -0.004064 | 0.12356 | -0.23106 | -0.16207 | -0.24089 | -0.13385 | -0.028339 | -0.12695 | 0.11394 | -0.029353 | -0.11772 | 123.0212 | 122.857 | 122.926 | 66.7754 | -123.2157 | 122.9542 | 123.0587 | 122.9704 | 66.7698 | -123.329
254.3125 | 123.2758 | -66.8335 | 56.337 | 0.057113 | -0.023525 | -0.0011099 | 0.052318 | -0.0040642 | 0.052192 | 0.028371 | -0.0039797 | -0.0034247 | 0.060255 | 0.019073 | 0.056652 | -64.5588 | 0.019721 | -66.7597 | 56.2702 | 56.0922 | 56.1612 | -66.8741 | -66.7886 | 0.018674 | -66.8872 | 56.2031 | 56.2893 | 56.1964 | -67.0011 | -0.040649 | -0.066823 | 2.2747 | 0.073756 | 0.11441 | -0.24479 | -0.17581 | -0.16765 | -0.13385 | 0.044903 | -0.053704 | 0.11394 | -0.047665 | -0.14061 | 123.1036 | 122.9257 | 122.9947 | 66.8532 | -123.2111 | 123.0366 | 123.1228 | 123.0299 | 66.8522 | -123.3381
255.2812 | 123.4085 | -66.7694 | 56.3232 | 0.072375 | -0.024593 | -0.0032469 | 0.053386 | -0.0051322 | 0.051124 | 0.074154 | -0.0029117 | -0.0023567 | 0.05705 | 0.018005 | 0.05772 | -64.6458 | 0.015142 | -66.7689 | 56.261 | 56.0922 | 56.1657 | -66.8787 | -66.7886 | 0.009516 | -66.8918 | 56.2031 | 56.2985 | 56.2055 | -66.9966 | -0.10932 | -0.062247 | 2.1236 | 0.000513 | 0.10983 | -0.23106 | -0.1575 | -0.22716 | -0.12012 | -0.019184 | -0.12237 | 0.10479 | -0.024775 | -0.11772 | 123.0304 | 122.8616 | 122.9352 | 66.7846 | -123.202 | 122.9725 | 123.0679 | 122.9749 | 66.7789 | -123.3198
256.2812 | 123.3353 | -66.774 | 56.3278 | 0.057113 | -0.024593 | -0.0043149 | 0.050181 | -0.0062002 | 0.05326 | 0.074154 | -0.0029117 | -0.0044937 | 0.059187 | 0.019073 | 0.058788 | -64.6504 | 0.019721 | -66.7643 | 56.2564 | 56.1013 | 56.1657 | -66.8604 | -66.784 | 0.014095 | -66.8872 | 56.1985 | 56.303 | 56.2055 | -67.0057 | -0.086421 | -0.071403 | 2.1236 | 0.009669 | 0.09609 | -0.22648 | -0.16207 | -0.23174 | -0.12927 | -0.010027 | -0.11321 | 0.11852 | -0.024774 | -0.1223 | 123.0304 | 122.8753 | 122.9397 | 66.7937 | -123.1882 | 122.9725 | 123.077 | 122.9795 | 66.7881 | -123.3335
257.2812 | 123.3307 | -66.7877 | 56.3599 | 0.057113 | -0.024593 | -0.0021789 | 0.052318 | -0.0051322 | 0.052192 | 0.074154 | -0.00077468 | -0.0034247 | 0.058119 | 0.019073 | 0.056652 | -64.5725 | 0.019721 | -66.7643 | 56.261 | 56.0968 | 56.1657 | -66.8741 | -66.7932 | 0.014095 | -66.8918 | 56.2031 | 56.2985 | 56.2055 | -67.0011 | -0.086425 | -0.098868 | 2.2152 | 0.023402 | 0.10983 | -0.2631 | -0.19412 | -0.21342 | -0.15674 | -0.005452 | -0.10406 | 0.10936 | -0.061396 | -0.15434 | 123.0487 | 122.8845 | 122.9535 | 66.8074 | -123.234 | 122.9908 | 123.0862 | 122.9932 | 66.8018 | -123.361
258.2812 | 123.4177 | -66.7465 | 56.3278 | 0.057113 | -0.023525 | -0.0021789 | 0.051249 | -0.0062002 | 0.052192 | 0.058893 | -0.0018437 | -0.0034247 | 0.058119 | 0.019073 | 0.058788 | -64.6275 | 0.015142 | -66.7597 | 56.261 | 56.1013 | 56.1612 | -66.8833 | -66.7932 | 0.018674 | -66.878 | 56.2031 | 56.303 | 56.2055 | -67.0011 | -0.13678 | -0.066825 | 2.119 | -0.013219 | 0.12356 | -0.22648 | -0.16665 | -0.25462 | -0.1247 | -0.046651 | -0.13152 | 0.1231 | -0.024774 | -0.1223 | 123.0075 | 122.8479 | 122.9077 | 66.7617 | -123.2111 | 122.9496 | 123.0496 | 122.952 | 66.7652 | -123.329
259.2812 | 123.3078 | -66.7923 | 56.3507 | 0.072375 | -0.023525 | -0.0032469 | 0.053386 | -0.0051322 | 0.05326 | 0.043632 | -0.0029117 | -0.0034247 | 0.058119 | 0.019073 | 0.056652 | -64.5725 | 0.019721 | -66.7597 | 56.2656 | 56.1013 | 56.1749 | -66.8925 | -66.7886 | 0.014095 | -66.8872 | 56.2123 | 56.2985 | 56.2101 | -67.0057 | -0.10016 | -0.085134 | 2.2198 | 0.032557 | 0.13272 | -0.24937 | -0.1758 | -0.21343 | -0.13843 | 0.003704 | -0.094903 | 0.11852 | -0.052241 | -0.14061 | 123.0579 | 122.8936 | 122.9672 | 66.812 | -123.2432 | 123.0046 | 123.0908 | 123.0024 | 66.8064 | -123.3564
260.2812 | 123.2666 | -66.8106 | 56.3599 | 0.041851 | -0.022456 | -0.0021789 | 0.053386 | -0.0062002 | 0.051124 | 0.074154 | -0.0018437 | -0.0023567 | 0.060255 | 0.020141 | 0.05772 | -64.5634 | 0.015142 | -66.7643 | 56.2702 | 56.0968 | 56.1703 | -66.8879 | -66.7886 | 0.014095 | -66.8964 | 56.1985 | 56.2847 | 56.2147 | -67.0011 | -0.077274 | -0.089711 | 2.2472 | 0.04629 | 0.12356 | -0.2631 | -0.18954 | -0.19053 | -0.16132 | 0.022015 | -0.08575 | 0.10478 | -0.075132 | -0.14519 | 123.0808 | 122.9074 | 122.9809 | 66.8257 | -123.2477 | 123.0092 | 123.0953 | 123.0253 | 66.8247 | -123.361
261.2812 | 123.4039 | -66.7603 | 56.3278 | 0.072375 | -0.025661 | -0.0021789 | 0.051249 | -0.0040642 | 0.052192 | 0.058893 | -0.0029117 | -0.0023567 | 0.058119 | 0.020141 | 0.05772 | -64.6366 | 0.010564 | -66.7643 | 56.2564 | 56.0922 | 56.1657 | -66.8879 | -66.7932 | 0.009516 | -66.8872 | 56.2031 | 56.2847 | 56.2055 | -66.9966 | -0.12763 | -0.071403 | 2.1236 | -0.004064 | 0.12356 | -0.23564 | -0.16207 | -0.23631 | -0.1247 | -0.032918 | -0.12695 | 0.10936 | -0.043089 | -0.1223 | 123.0167 | 122.8524 | 122.926 | 66.7708 | -123.2157 | 122.9634 | 123.045 | 122.9658 | 66.7698 | -123.3244
262.2812 | 123.3582 | -66.7877 | 56.3324 | 0.057113 | -0.024593 | -0.0032469 | 0.052318 | -0.0062002 | 0.052192 | 0.074154 | -0.0029117 | -0.0023567 | 0.058119 | 0.019073 | 0.05772 | -64.5863 | 0.0243 | -66.7689 | 56.2656 | 56.1013 | 56.1612 | -66.8833 | -66.7932 | 0.009516 | -66.8826 | 56.2031 | 56.2893 | 56.2101 | -67.0057 | -0.095583 | -0.066823 | 2.2014 | 0.018824 | 0.11441 | -0.23105 | -0.17123 | -0.218 | -0.12927 | -0.005452 | -0.094901 | 0.1231 | -0.043087 | -0.1223 | 123.0533 | 122.8891 | 122.9489 | 66.812 | -123.2157 | 122.9908 | 123.077 | 122.9978 | 66.7972 | -123.3381
263.2812 | 123.3536 | -66.774 | 56.337 | 0.057113 | -0.02673 | -0.0032469 | 0.051249 | -0.0051322 | 0.054329 | 0.058893 | -0.0029117 | -0.0023567 | 0.059187 | 0.018005 | 0.05772 | -64.5908 | 0.010564 | -66.7597 | 56.2702 | 56.1013 | 56.1612 | -66.8833 | -66.7886 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.2009 | -67.0103 | -0.10932 | -0.066823 | 2.1831 | 0.014247 | 0.12356 | -0.23563 | -0.17581 | -0.23631 | -0.13385 | -0.014606 | -0.11321 | 0.1231 | -0.043086 | -0.13604 | 123.0441 | 122.8753 | 122.9352 | 66.7846 | -123.2203 | 122.9771 | 123.0679 | 122.9749 | 66.7881 | -123.3473
264.2812 | 123.3765 | -66.7648 | 56.3141 | 0.072375 | -0.023525 | -0.0021789 | 0.054455 | -0.0062002 | 0.05326 | 0.043632 | -0.0039797 | -0.0012887 | 0.059187 | 0.02121 | 0.05772 | -64.6366 | 0.0243 | -66.7643 | 56.261 | 56.0922 | 56.1657 | -66.8741 | -66.784 | 0.004938 | -66.8918 | 56.1985 | 56.2985 | 56.2055 | -67.0103 | -0.10931 | -0.053092 | 2.1282 | 0.000514 | 0.10983 | -0.2219 | -0.14834 | -0.24547 | -0.11554 | -0.019182 | -0.12695 | 0.11852 | -0.01562 | -0.10857 | 123.0258 | 122.857 | 122.9306 | 66.7891 | -123.1882 | 122.9634 | 123.0633 | 122.9703 | 66.7698 | -123.3244
265.2812 | 123.3902 | -66.7694 | 56.3278 | 0.087637 | -0.023525 | -0.0021789 | 0.051249 | -0.0062002 | 0.05326 | 0.074154 | -0.0029117 | -0.0012887 | 0.05705 | 0.02121 | 0.058788 | -64.6321 | 0.019721 | -66.7552 | 56.2564 | 56.0922 | 56.1703 | -66.8833 | -66.7886 | 0.014095 | -66.8826 | 56.2031 | 56.2893 | 56.2147 | -67.0103 | -0.11389 | -0.071403 | 2.1374 | 0.014248 | 0.12814 | -0.23564 | -0.1575 | -0.24089 | -0.1247 | -0.019184 | -0.11321 | 0.12768 | -0.03851 | -0.11315 | 123.0258 | 122.8616 | 122.9397 | 66.7891 | -123.2111 | 122.9725 | 123.0587 | 122.9841 | 66.7835 | -123.3381
266.2812 | 123.3536 | -66.774 | 56.3278 | 0.041851 | -0.024593 | -0.0011099 | 0.052318 | -0.0051322 | 0.05326 | 0.074154 | -0.0039797 | -0.0023567 | 0.05705 | 0.019073 | 0.05772 | -64.6092 | 0.019721 | -66.7597 | 56.2656 | 56.0922 | 56.1657 | -66.897 | -66.7886 | 0.018674 | -66.8826 | 56.1985 | 56.2939 | 56.2101 | -67.0103 | -0.12305 | -0.062246 | 2.1648 | 0.014247 | 0.1373 | -0.23564 | -0.16207 | -0.23631 | -0.12927 | -0.014606 | -0.10863 | 0.12768 | -0.033931 | -0.11772 | 123.0396 | 122.8662 | 122.9397 | 66.7937 | -123.2249 | 122.9725 | 123.0679 | 122.9841 | 66.7927 | -123.3381
267.2812 | 123.2666 | -66.8015 | 56.3873 | 0.057113 | -0.02673 | -0.0043149 | 0.051249 | -0.0072692 | 0.052192 | 0.058893 | -0.0018437 | -0.0034247 | 0.059187 | 0.022278 | 0.05772 | -64.5588 | 0.015142 | -66.7552 | 56.2702 | 56.1013 | 56.1703 | -66.8879 | -66.7886 | 0.009516 | -66.8872 | 56.1985 | 56.2939 | 56.2101 | -67.0057 | -0.086429 | -0.11718 | 2.2427 | 0.046292 | 0.13272 | -0.28599 | -0.217 | -0.20427 | -0.18878 | 0.01286 | -0.085747 | 0.11852 | -0.09344 | -0.17723 | 123.0716 | 122.9028 | 122.9718 | 66.8166 | -123.2752 | 123 | 123.0953 | 123.0115 | 66.811 | -123.3931
268.3125 | 123.3765 | -66.7877 | 56.2729 | 0.057113 | -0.02673 | -0.0032469 | 0.052318 | -0.0051322 | 0.052192 | 0.074154 | -0.0039797 | -0.0044937 | 0.058119 | 0.022278 | 0.055583 | -64.5908 | 0.0243 | -66.7552 | 56.2564 | 56.0876 | 56.1657 | -66.8787 | -66.7886 | 0.004938 | -66.878 | 56.2077 | 56.2939 | 56.2009 | -67.0011 | -0.091004 | -0.016471 | 2.1969 | 0.032559 | 0.12356 | -0.18528 | -0.10714 | -0.21342 | -0.065186 | -0.000873 | -0.090323 | 0.1231 | 0.021001 | -0.071949 | 123.0441 | 122.8753 | 122.9535 | 66.812 | -123.1516 | 122.9954 | 123.0816 | 122.9887 | 66.7927 | -123.274
269.2812 | 123.3673 | -66.7786 | 56.3004 | 0.072375 | -0.025661 | -0.0021789 | 0.052318 | -0.0051322 | 0.05326 | 0.058893 | -0.0039797 | -0.0023567 | 0.058119 | 0.02121 | 0.056652 | -64.6321 | 0.019721 | -66.7552 | 56.2656 | 56.0968 | 56.1703 | -66.8925 | -66.7886 | 0.023253 | -66.878 | 56.2123 | 56.2939 | 56.2055 | -67.0057 | -0.1139 | -0.03478 | 2.1465 | 0.023403 | 0.1373 | -0.20359 | -0.13003 | -0.22716 | -0.088073 | -0.010029 | -0.099479 | 0.12768 | -0.006465 | -0.094836 | 123.0441 | 122.8753 | 122.9489 | 66.7983 | -123.1928 | 122.9908 | 123.0725 | 122.9841 | 66.8018 | -123.3061
270.2812 | 123.4085 | -66.7648 | 56.3232 | 0.057113 | -0.027798 | -0.0021789 | 0.051249 | -0.0072692 | 0.052192 | 0.058893 | -0.0039797 | -0.0034247 | 0.058119 | 0.020141 | 0.056652 | -64.6092 | 0.015142 | -66.7552 | 56.2702 | 56.0876 | 56.1657 | -66.8833 | -66.7932 | 0.009516 | -66.8826 | 56.2031 | 56.2939 | 56.1918 | -67.0011 | -0.11847 | -0.05309 | 2.1557 | 0.009671 | 0.12814 | -0.23564 | -0.1575 | -0.23631 | -0.12012 | -0.02834 | -0.11779 | 0.11852 | -0.029353 | -0.13146 | 123.035 | 122.8524 | 122.9306 | 66.78 | -123.2065 | 122.968 | 123.0587 | 122.9566 | 66.7743 | -123.3244
271.2812 | 123.3215 | -66.8152 | 56.3507 | 0.057113 | -0.029935 | -0.0032469 | 0.052318 | -0.0062002 | 0.052192 | 0.058893 | -0.0039797 | -0.0034247 | 0.055982 | 0.02121 | 0.056652 | -64.5313 | 0.019721 | -66.7597 | 56.261 | 56.0739 | 56.1703 | -66.8879 | -66.7886 | 0.014095 | -66.878 | 56.1985 | 56.2939 | 56.1964 | -67.0057 | -0.072696 | -0.089713 | 2.2839 | 0.055446 | 0.12814 | -0.27684 | -0.18038 | -0.19054 | -0.15216 | 0.026593 | -0.062857 | 0.12768 | -0.056819 | -0.15435 | 123.0762 | 122.8891 | 122.9855 | 66.8349 | -123.2386 | 123.0137 | 123.1091 | 123.0115 | 66.8293 | -123.3564
272.2812 | 123.3582 | -66.7603 | 56.3278 | 0.072375 | -0.027798 | -0.0032469 | 0.052318 | -0.0072692 | 0.050055 | 0.058893 | -0.0039797 | -0.0055617 | 0.05705 | 0.02121 | 0.05772 | -64.5817 | 0.015142 | -66.7689 | 56.2656 | 56.0693 | 56.1703 | -66.8879 | -66.7932 | 0.009516 | -66.8826 | 56.2031 | 56.2893 | 56.1323 | -67.0011 | -0.12763 | -0.062246 | 2.1786 | -0.008642 | 0.11899 | -0.25853 | -0.1575 | -0.24089 | -0.1247 | -0.032918 | -0.12237 | 0.11852 | -0.03851 | -0.19556 | 123.0258 | 122.8295 | 122.9306 | 66.7754 | -123.2157 | 122.9634 | 123.0496 | 122.8925 | 66.7698 | -123.329
273.2812 | 123.3673 | -66.7603 | 56.3049 | 0.041851 | -0.028867 | -0.0043149 | 0.053386 | -0.0062002 | 0.051124 | 0.043632 | -0.0029117 | -0.0023567 | 0.055982 | 0.02121 | 0.056652 | -64.5908 | 0.0243 | -66.7597 | 56.261 | 56.0647 | 56.1749 | -66.8696 | -66.7886 | 0.009516 | -66.8872 | 56.2031 | 56.2893 | 56.1185 | -67.0011 | -0.10931 | -0.043937 | 2.1694 | 0.000514 | 0.10983 | -0.24022 | -0.13003 | -0.24089 | -0.10181 | -0.028339 | -0.12695 | 0.11394 | -0.015622 | -0.18641 | 123.0212 | 122.825 | 122.9352 | 66.7846 | -123.1745 | 122.9634 | 123.0496 | 122.8788 | 66.7698 | -123.3061
274.2812 | 123.2803 | -66.7969 | 56.3873 | 0.057113 | -0.028867 | -0.0032469 | 0.052318 | -0.0051322 | 0.050055 | 0.074154 | -0.0039797 | -0.0034247 | 0.05705 | 0.022278 | 0.058788 | -64.5405 | 0.015142 | -66.7597 | 56.2656 | 56.0556 | 56.1703 | -66.8833 | -66.7932 | 0.009516 | -66.8826 | 56.2077 | 56.2847 | 56.0865 | -67.0057 | -0.086428 | -0.12176 | 2.2564 | 0.037135 | 0.12356 | -0.33178 | -0.217 | -0.20885 | -0.17963 | 0.003703 | -0.085746 | 0.1231 | -0.1026 | -0.30085 | 123.0624 | 122.8524 | 122.9672 | 66.812 | -123.2706 | 123.0046 | 123.0816 | 122.8833 | 66.8064 | -123.3931
275.2812 | 123.317 | -66.7877 | 56.3461 | 0.057113 | -0.028867 | -0.0021789 | 0.052318 | -0.0094052 | 0.051124 | 0.074154 | -0.0039797 | -0.0034247 | 0.058119 | 0.02121 | 0.056652 | -64.568 | 0.010564 | -66.7597 | 56.2702 | 56.0556 | 56.1749 | -66.8741 | -66.7886 | 0.004938 | -66.8872 | 56.2031 | 56.2893 | 56.0636 | -67.0057 | -0.086425 | -0.075978 | 2.2198 | 0.02798 | 0.11441 | -0.29058 | -0.17123 | -0.218 | -0.14301 | -0.000873 | -0.09948 | 0.11852 | -0.05682 | -0.28255 | 123.0579 | 122.8433 | 122.9626 | 66.7983 | -123.2203 | 122.9908 | 123.077 | 122.8513 | 66.7927 | -123.3519
276.2812 | 123.2574 | -66.8198 | 56.3187 | 0.057113 | -0.028867 | -0.0021789 | 0.052318 | -0.0072692 | 0.050055 | 0.074154 | -0.0061157 | -0.0044937 | 0.054914 | 0.02121 | 0.056652 | -64.5451 | 0.015142 | -66.7643 | 56.2702 | 56.0464 | 56.1795 | -66.8741 | -66.8023 | 0.009516 | -66.8826 | 56.1985 | 56.303 | 56.0911 | -67.0057 | -0.054382 | -0.048513 | 2.2747 | 0.055445 | 0.10983 | -0.27227 | -0.13918 | -0.18596 | -0.12012 | 0.017434 | -0.062858 | 0.1231 | -0.015619 | -0.22761 | 123.0899 | 122.8662 | 122.9992 | 66.8349 | -123.1928 | 123.0183 | 123.1228 | 122.9108 | 66.8293 | -123.3244
277.2812 | 123.3765 | -66.7694 | 56.3278 | 0.057113 | -0.029935 | -0.0032469 | 0.052318 | -0.0062002 | 0.048987 | 0.043632 | -0.0071847 | -0.0055617 | 0.05705 | 0.022278 | 0.05772 | -64.6092 | 0.019721 | -66.7872 | 56.2793 | 56.0601 | 56.1703 | -66.8879 | -66.8069 | 0.009516 | -66.8826 | 56.2077 | 56.2985 | 56.0865 | -67.0011 | -0.11847 | -0.048511 | 2.1602 | -0.0178 | 0.10067 | -0.26769 | -0.1575 | -0.23173 | -0.12012 | -0.037499 | -0.11321 | 0.11852 | -0.029353 | -0.24135 | 123.0487 | 122.8295 | 122.9397 | 66.7891 | -123.2157 | 122.9771 | 123.0679 | 122.8559 | 66.7789 | -123.329
278.2812 | 123.349 | -66.7648 | 56.3416 | 0.041851 | -0.031003 | -0.0043149 | 0.053386 | -0.0072692 | 0.048987 | 0.074154 | -0.0050477 | -0.0055617 | 0.054914 | 0.02121 | 0.055583 | -64.5863 | 0.028878 | -66.7918 | 56.3205 | 56.083 | 56.2161 | -66.9199 | -66.8115 | 0.014095 | -66.8872 | 56.2031 | 56.2939 | 56.0865 | -67.0057 | -0.1551 | -0.021039 | 2.1786 | -0.026956 | 0.12815 | -0.25853 | -0.12544 | -0.24089 | -0.13843 | -0.046655 | -0.12237 | 0.11852 | -0.047664 | -0.25508 | 123.0853 | 122.8479 | 122.9809 | 66.7937 | -123.2615 | 122.968 | 123.0587 | 122.8513 | 66.7789 | -123.3473
279.2812 | 123.3673 | -66.774 | 56.369 | 0.057113 | -0.029935 | -0.0043149 | 0.051249 | -0.0083372 | 0.050055 | 0.089415 | -0.0039797 | -0.0066297 | 0.05705 | 0.02121 | 0.056652 | -64.5908 | 0.033457 | -66.7781 | 56.3159 | 56.0922 | 56.2253 | -66.9382 | -66.8023 | 0.014095 | -66.8872 | 56.1985 | 56.2893 | 56.0819 | -67.0057 | -0.16426 | -0.053083 | 2.1831 | -0.004066 | 0.1602 | -0.27683 | -0.14375 | -0.23174 | -0.17047 | -0.028342 | -0.11321 | 0.11852 | -0.079709 | -0.28712 | 123.0899 | 122.8662 | 122.9993 | 66.8074 | -123.3073 | 122.9725 | 123.0633 | 122.8559 | 66.7881 | -123.3747
280.2812 | 123.2758 | -66.7969 | 56.3919 | 0.072375 | -0.029935 | -0.0021789 | 0.053386 | -0.0072692 | 0.051124 | 0.074154 | -0.0050477 | -0.0055617 | 0.059187 | 0.02121 | 0.056652 | -64.5542 | 0.028878 | -66.7826 | 56.3205 | 56.0922 | 56.2344 | -66.9382 | -66.7977 | 0.014095 | -66.8872 | 56.2077 | 56.2893 | 56.0819 | -67.0057 | -0.14137 | -0.071393 | 2.2427 | 0.014244 | 0.15562 | -0.29972 | -0.15748 | -0.20885 | -0.18421 | -0.000875 | -0.090325 | 0.11852 | -0.1026 | -0.31001 | 123.1174 | 122.8891 | 123.0313 | 66.8258 | -123.3302 | 123.0046 | 123.0862 | 122.8788 | 66.811 | -123.3976
281.3125 | 123.2529 | -66.8152 | 56.3736 | 0.057113 | -0.028867 | -0.0043149 | 0.052318 | -0.0062002 | 0.051124 | 0.074154 | -0.0039797 | -0.0034247 | 0.059187 | 0.022278 | 0.05772 | -64.5634 | 0.033457 | -66.7735 | 56.3022 | 56.0876 | 56.2207 | -66.952 | -66.8023 | 0.018674 | -66.8826 | 56.1985 | 56.2893 | 56.1231 | -67.0057 | -0.1368 | -0.071395 | 2.2518 | 0.041712 | 0.17851 | -0.28599 | -0.15291 | -0.19054 | -0.17505 | 0.012857 | -0.067435 | 0.1231 | -0.084286 | -0.25049 | 123.1174 | 122.9028 | 123.0359 | 66.8486 | -123.3256 | 123.0137 | 123.1045 | 122.9383 | 66.8339 | -123.3793
282.2812 | 123.3902 | -66.7603 | 56.3278 | 0.041851 | -0.028867 | -0.0032469 | 0.051249 | -0.0062002 | 0.052192 | 0.10468 | -0.0039797 | -0.0034247 | 0.058119 | 0.020141 | 0.056652 | -64.6092 | 0.028878 | -66.7826 | 56.3022 | 56.083 | 56.2253 | -66.952 | -66.7977 | 0.023253 | -66.8872 | 56.2031 | 56.2985 | 56.0727 | -67.0011 | -0.19173 | -0.025619 | 2.1511 | -0.022377 | 0.16936 | -0.24479 | -0.10255 | -0.24089 | -0.1247 | -0.037496 | -0.12695 | 0.11394 | -0.029353 | -0.25508 | 123.0625 | 122.8433 | 122.9855 | 66.7891 | -123.2798 | 122.9634 | 123.0587 | 122.833 | 66.7835 | -123.329
283.2812 | 123.3261 | -66.7694 | 56.3095 | 0.072375 | -0.027798 | -0.0021789 | 0.051249 | -0.0062002 | 0.052192 | 0.058893 | -0.0029117 | -0.0044937 | 0.059187 | 0.022278 | 0.056652 | -64.5863 | 0.0243 | -66.7826 | 56.2976 | 56.0876 | 56.2253 | -66.9382 | -66.7977 | 0.018674 | -66.8872 | 56.2077 | 56.2893 | 56.1277 | -67.0057 | -0.16884 | -0.011886 | 2.1831 | -0.013222 | 0.15562 | -0.2219 | -0.084241 | -0.23631 | -0.10181 | -0.028341 | -0.11779 | 0.11852 | -0.020199 | -0.18183 | 123.067 | 122.857 | 122.9947 | 66.7937 | -123.2478 | 122.9771 | 123.0587 | 122.8971 | 66.7881 | -123.3152
284.2812 | 123.3765 | -66.774 | 56.3828 | 0.072375 | -0.028867 | -0.0021789 | 0.052318 | -0.0072692 | 0.05326 | 0.089415 | -0.0039797 | -0.0044937 | 0.05705 | 0.02121 | 0.058788 | -64.5771 | 0.038035 | -66.7735 | 56.2976 | 56.083 | 56.2161 | -66.9428 | -66.7977 | 0.03241 | -66.8918 | 56.2031 | 56.2847 | 56.1002 | -67.0057 | -0.16884 | -0.085128 | 2.1969 | 0.000513 | 0.16936 | -0.29972 | -0.16664 | -0.23174 | -0.17963 | -0.023763 | -0.11779 | 0.11394 | -0.09802 | -0.28254 | 123.0716 | 122.857 | 122.9901 | 66.812 | -123.3256 | 122.9771 | 123.0587 | 122.8742 | 66.8064 | -123.3885
285.2812 | 123.4268 | -66.7831 | 56.3278 | 0.057113 | -0.027798 | -0.0032469 | 0.051249 | -0.0083372 | 0.050055 | 0.074154 | -0.0061157 | -0.0034247 | 0.058119 | 0.02121 | 0.055583 | -64.6183 | 0.028878 | -66.7735 | 56.3068 | 56.083 | 56.2161 | -66.9428 | -66.7977 | 0.023253 | -66.8918 | 56.2077 | 56.2985 | 56.1139 | -67.0011 | -0.15969 | -0.021041 | 2.1648 | 0.009668 | 0.16936 | -0.24479 | -0.11171 | -0.218 | -0.12012 | -0.014608 | -0.10864 | 0.10936 | -0.029353 | -0.21387 | 123.0899 | 122.8662 | 122.9993 | 66.812 | -123.2706 | 122.9908 | 123.0816 | 122.8971 | 66.8064 | -123.329
286.2812 | 123.3124 | -66.8015 | 56.3599 | 0.041851 | -0.029935 | -0.0021789 | 0.052318 | -0.0072692 | 0.050055 | 0.058893 | -0.0050477 | -0.0034247 | 0.059187 | 0.02121 | 0.056652 | -64.5496 | 0.033457 | -66.7781 | 56.3159 | 56.1013 | 56.2344 | -66.952 | -66.7977 | 0.023253 | -66.878 | 56.2031 | 56.2939 | 56.0682 | -67.0011 | -0.15053 | -0.043927 | 2.2518 | 0.0234 | 0.17393 | -0.25852 | -0.12544 | -0.19969 | -0.15674 | 0.003703 | -0.07659 | 0.1231 | -0.065974 | -0.2917 | 123.1174 | 122.9028 | 123.0359 | 66.8349 | -123.3118 | 123.0046 | 123.0953 | 122.8696 | 66.8247 | -123.361
287.2812 | 123.2666 | -66.8106 | 56.369 | 0.057113 | -0.029935 | -0.0043149 | 0.051249 | -0.0072692 | 0.050055 | 0.089415 | -0.0050477 | -0.0044937 | 0.055982 | 0.022278 | 0.055583 | -64.568 | 0.033457 | -66.7826 | 56.3114 | 56.0968 | 56.2344 | -66.952 | -66.8115 | 0.027831 | -66.8826 | 56.2077 | 56.2939 | 56.0911 | -67.0057 | -0.14138 | -0.057661 | 2.2427 | 0.027977 | 0.16936 | -0.27226 | -0.13459 | -0.19511 | -0.16132 | -0.000879 | -0.072013 | 0.1231 | -0.07513 | -0.27797 | 123.122 | 122.9074 | 123.045 | 66.8441 | -123.321 | 123.0183 | 123.1045 | 122.9017 | 66.8384 | -123.3747
288.2812 | 123.3215 | -66.8106 | 56.3141 | 0.057113 | -0.031003 | -0.0021789 | 0.053386 | -0.0083372 | 0.047919 | 0.074154 | -0.0061157 | -0.0044937 | 0.055982 | 0.022278 | 0.058788 | -64.5817 | 0.033457 | -66.7918 | 56.3251 | 56.0922 | 56.2298 | -66.952 | -66.8115 | 0.03241 | -66.8872 | 56.2031 | 56.2939 | 56.1002 | -67.0011 | -0.14138 | 0.011006 | 2.2289 | 0.01882 | 0.1602 | -0.2219 | -0.08424 | -0.19053 | -0.11096 | -0.000879 | -0.076592 | 0.11394 | -0.020198 | -0.21388 | 123.1357 | 122.9028 | 123.0405 | 66.8441 | -123.2661 | 123.0137 | 123.1045 | 122.9108 | 66.843 | -123.3152
289.2812 | 123.436 | -66.7603 | 56.337 | 0.087637 | -0.032072 | -0.0032469 | 0.051249 | -0.0083372 | 0.04685 | 0.058893 | -0.0050477 | -0.0055617 | 0.055982 | 0.022278 | 0.055583 | -64.6183 | 0.033457 | -66.7918 | 56.3251 | 56.083 | 56.2344 | -66.9108 | -66.8069 | 0.009516 | -66.8918 | 56.2077 | 56.2939 | 56.1002 | -67.0103 | -0.15052 | -0.011882 | 2.1419 | -0.031534 | 0.11899 | -0.25395 | -0.10255 | -0.25005 | -0.12927 | -0.046654 | -0.13152 | 0.11852 | -0.043086 | -0.23677 | 123.0853 | 122.8433 | 122.9947 | 66.7937 | -123.2478 | 122.968 | 123.0541 | 122.8605 | 66.7698 | -123.3473
290.2812 | 123.3536 | -66.7603 | 56.3141 | 0.041851 | -0.03314 | -0.0043149 | 0.052318 | -0.0083372 | 0.04685 | 0.074154 | -0.0071847 | -0.0066297 | 0.055982 | 0.022278 | 0.056652 | -64.6733 | 0.033457 | -66.7918 | 56.3114 | 56.0693 | 56.1978 | -66.9108 | -66.8161 | 0.014095 | -66.8872 | 56.2077 | 56.2939 | 56.1643 | -67.0149 | -0.15052 | -0.002729 | 2.087 | -0.031534 | 0.11899 | -0.2448 | -0.11629 | -0.25463 | -0.10639 | -0.055811 | -0.12695 | 0.12768 | -0.020198 | -0.14978 | 123.0716 | 122.8295 | 122.9581 | 66.7937 | -123.2249 | 122.968 | 123.0541 | 122.9246 | 66.7743 | -123.329
291.2812 | 123.2574 | -66.8152 | 56.3736 | 0.041851 | -0.029935 | -0.0043149 | 0.052318 | -0.0083372 | 0.04685 | 0.074154 | -0.0050477 | -0.0055617 | 0.054914 | 0.023347 | 0.05772 | -64.5496 | 0.0243 | -66.7918 | 56.3114 | 56.0556 | 56.1795 | -66.8833 | -66.8115 | 0.014095 | -66.8872 | 56.2077 | 56.2939 | 56.1094 | -67.0057 | -0.068117 | -0.062238 | 2.2655 | 0.023398 | 0.091515 | -0.31804 | -0.19411 | -0.19054 | -0.16589 | 0.003699 | -0.072014 | 0.11852 | -0.079707 | -0.26423 | 123.1265 | 122.8707 | 122.9947 | 66.8395 | -123.2569 | 123.0229 | 123.1091 | 122.9246 | 66.8293 | -123.3793
292.2812 | 123.3902 | -66.7465 | 56.3232 | 0.072375 | -0.032072 | -0.0053839 | 0.052318 | -0.0094052 | 0.048987 | 0.089415 | -0.0061157 | -0.0055617 | 0.054914 | 0.022278 | 0.055583 | -64.5908 | 0.019721 | -66.7781 | 56.2839 | 56.0647 | 56.1795 | -66.8787 | -66.8161 | 0.004938 | -66.8826 | 56.2031 | 56.2939 | 56.0956 | -67.0011 | -0.1322 | -0.039355 | 2.1557 | -0.031532 | 0.10067 | -0.25853 | -0.14376 | -0.25462 | -0.12012 | -0.069544 | -0.1361 | 0.11852 | -0.029353 | -0.22761 | 123.0304 | 122.8112 | 122.926 | 66.7662 | -123.202 | 122.9496 | 123.0404 | 122.8422 | 66.7515 | -123.3244
293.2812 | 123.3765 | -66.7786 | 56.3324 | 0.072375 | -0.028867 | -0.0021789 | 0.053386 | -0.0083372 | 0.050055 | 0.089415 | -0.0061157 | -0.0044937 | 0.058119 | 0.022278 | 0.056652 | -64.6366 | 0.010564 | -66.7552 | 56.2747 | 56.0601 | 56.1657 | -66.8741 | -66.7886 | 0.018674 | -66.8826 | 56.1985 | 56.2939 | 56.1094 | -67.0057 | -0.095581 | -0.057666 | 2.1419 | 0.023403 | 0.11898 | -0.27226 | -0.16665 | -0.22716 | -0.13385 | -0.010029 | -0.10406 | 0.1231 | -0.038508 | -0.22303 | 123.0533 | 122.8387 | 122.9443 | 66.7891 | -123.2065 | 122.9771 | 123.0725 | 122.8879 | 66.7972 | -123.3381
294.2812 | 123.3765 | -66.7694 | 56.3232 | 0.041851 | -0.029935 | -0.0043149 | 0.050181 | -0.0062002 | 0.051124 | 0.058893 | -0.0050477 | -0.0055617 | 0.060255 | 0.023347 | 0.055583 | -64.6229 | 0.015142 | -66.7643 | 56.2702 | 56.0601 | 56.1795 | -66.8925 | -66.7886 | 0.014095 | -66.8826 | 56.2077 | 56.2939 | 56.1139 | -67.0011 | -0.12305 | -0.05309 | 2.1465 | 0.005091 | 0.12814 | -0.26311 | -0.14376 | -0.23173 | -0.11554 | -0.019184 | -0.11321 | 0.11852 | -0.029353 | -0.2093 | 123.0396 | 122.8295 | 122.9489 | 66.7846 | -123.2157 | 122.9771 | 123.0633 | 122.8834 | 66.7835 | -123.3244
295.2812 | 123.3765 | -66.774 | 56.3232 | 0.057113 | -0.028867 | -0.0021789 | 0.053386 | -0.0062002 | 0.051124 | 0.043632 | -0.0050477 | -0.0034247 | 0.05705 | 0.025483 | 0.055583 | -64.6321 | 0.015142 | -66.7597 | 56.2656 | 56.0601 | 56.1749 | -66.8879 | -66.784 | 0.009516 | -66.8918 | 56.2077 | 56.2939 | 56.1002 | -67.0103 | -0.11389 | -0.057668 | 2.1419 | 0.014247 | 0.12814 | -0.26311 | -0.14834 | -0.23631 | -0.11554 | -0.010027 | -0.11779 | 0.11852 | -0.029353 | -0.22303 | 123.0396 | 122.8341 | 122.9489 | 66.7891 | -123.2111 | 122.9817 | 123.0679 | 122.8742 | 66.7835 | -123.3335
296.2812 | 123.3994 | -66.7786 | 56.337 | 0.087637 | -0.029935 | -0.0043149 | 0.052318 | -0.0062002 | 0.048987 | 0.058893 | -0.0029117 | -0.0034247 | 0.053846 | 0.022278 | 0.056652 | -64.6 | 0.019721 | -66.7597 | 56.2656 | 56.0647 | 56.1703 | -66.8696 | -66.7886 | 0.009516 | -66.8826 | 56.2031 | 56.2985 | 56.1048 | -67.0057 | -0.091002 | -0.071401 | 2.1786 | 0.018824 | 0.10983 | -0.27226 | -0.16665 | -0.22716 | -0.13385 | -0.010029 | -0.10406 | 0.1231 | -0.038508 | -0.23219 | 123.0441 | 122.8433 | 122.9489 | 66.7983 | -123.2065 | 122.9817 | 123.077 | 122.8834 | 66.7881 | -123.3427
297.2812 | 123.3582 | -66.7648 | 56.3324 | 0.057113 | -0.029935 | -0.0032469 | 0.050181 | -0.0083372 | 0.051124 | 0.074154 | -0.0039797 | -0.0044937 | 0.055982 | 0.023347 | 0.055583 | -64.6366 | 0.015142 | -66.7643 | 56.2564 | 56.051 | 56.1749 | -66.8558 | -66.7794 | 0.014095 | -66.8918 | 56.1985 | 56.2939 | 56.0773 | -67.0103 | -0.090998 | -0.07598 | 2.1282 | 0.000514 | 0.091512 | -0.28142 | -0.15749 | -0.24547 | -0.13385 | -0.014604 | -0.12695 | 0.11852 | -0.038508 | -0.25508 | 123.0212 | 122.8158 | 122.9397 | 66.78 | -123.1882 | 122.9634 | 123.0587 | 122.8421 | 66.7789 | -123.3427
298.2812 | 123.3307 | -66.774 | 56.3187 | 0.072375 | -0.028867 | -0.0032469 | 0.052318 | -0.0083372 | 0.051124 | 0.074154 | -0.0050477 | -0.0044937 | 0.055982 | 0.024415 | 0.055583 | -64.6321 | 0.019721 | -66.7506 | 56.2702 | 56.0739 | 56.1795 | -66.8741 | -66.7886 | 0.004938 | -66.8918 | 56.2077 | 56.2939 | 56.1277 | -67.0057 | -0.10016 | -0.048513 | 2.1419 | 0.023404 | 0.12356 | -0.2448 | -0.13918 | -0.23174 | -0.11096 | -0.014606 | -0.11779 | 0.11394 | -0.024776 | -0.19098 | 123.0441 | 122.8479 | 122.9535 | 66.7937 | -123.1928 | 122.9817 | 123.0679 | 122.9017 | 66.7789 | -123.3244
299.2812 | 123.3719 | -66.774 | 56.3232 | 0.087637 | -0.029935 | -0.0032469 | 0.052318 | -0.0083372 | 0.051124 | 0.058893 | -0.0071847 | -0.0044937 | 0.055982 | 0.023347 | 0.054515 | -64.6321 | 0.015142 | -66.7643 | 56.261 | 56.0693 | 56.1657 | -66.8879 | -66.7932 | 0.004938 | -66.878 | 56.2031 | 56.2893 | 56.1231 | -67.0149 | -0.11389 | -0.062247 | 2.1419 | 0.009669 | 0.12356 | -0.25395 | -0.1575 | -0.24089 | -0.12012 | -0.019185 | -0.10406 | 0.13684 | -0.033932 | -0.20014 | 123.035 | 122.8433 | 122.9397 | 66.7891 | -123.2111 | 122.9771 | 123.0633 | 122.8971 | 66.7789 | -123.3381
300.2812 | 123.3719 | -66.7648 | 56.3187 | 0.072375 | -0.028867 | -0.0021789 | 0.054455 | -0.0072692 | 0.051124 | 0.074154 | -0.0039797 | -0.0044937 | 0.058119 | 0.023347 | 0.056652 | -64.6275 | 0.015142 | -66.7597 | 56.2702 | 56.0601 | 56.1795 | -66.8696 | -66.7886 | 0.009516 | -66.8826 | 56.2077 | 56.2985 | 56.1231 | -67.0011 | -0.10473 | -0.048513 | 2.1374 | 0.005092 | 0.10983 | -0.25853 | -0.13918 | -0.23631 | -0.11096 | -0.023761 | -0.11779 | 0.11852 | -0.020198 | -0.19556 | 123.035 | 122.825 | 122.9443 | 66.78 | -123.1882 | 122.9725 | 123.0633 | 122.8879 | 66.7743 | -123.3198
301.2812 | 123.4085 | -66.7374 | 56.3232 | 0.072375 | -0.031003 | -0.0032469 | 0.051249 | -0.0083372 | 0.051124 | 0.058893 | -0.0039797 | -0.0055617 | 0.05705 | 0.023347 | 0.054515 | -64.6137 | 0.019721 | -66.7735 | 56.261 | 56.0739 | 56.1749 | -66.8741 | -66.7932 | 0.004938 | -66.8826 | 56.2031 | 56.2939 | 56.1826 | -67.0149 | -0.13678 | -0.062247 | 2.1236 | -0.036108 | 0.10067 | -0.24937 | -0.14834 | -0.27751 | -0.12012 | -0.055806 | -0.14526 | 0.13226 | -0.029353 | -0.14062 | 122.9984 | 122.8112 | 122.9123 | 66.7571 | -123.1974 | 122.9405 | 123.0313 | 122.92 | 66.7423 | -123.3381
302.2812 | 123.3765 | -66.8015 | 56.337 | 0.072375 | -0.032072 | -0.0021789 | 0.051249 | -0.0083372 | 0.048987 | 0.058893 | -0.0050477 | -0.0055617 | 0.05705 | 0.025483 | 0.055583 | -64.6229 | 0.010564 | -66.7689 | 56.261 | 56.0739 | 56.1749 | -66.8879 | -66.7932 | 0.014095 | -66.8872 | 56.2031 | 56.303 | 56.2009 | -67.0103 | -0.086429 | -0.07598 | 2.1786 | 0.032557 | 0.11899 | -0.26311 | -0.16207 | -0.20885 | -0.13385 | 0.008281 | -0.085747 | 0.1231 | -0.033929 | -0.13604 | 123.0624 | 122.8753 | 122.9764 | 66.812 | -123.2249 | 123.0046 | 123.1045 | 123.0024 | 66.8155 | -123.3473
303.2812 | 123.3673 | -66.7923 | 56.3187 | 0.057113 | -0.031003 | -0.0032469 | 0.051249 | -0.0072692 | 0.050055 | 0.043632 | -0.0039797 | -0.0044937 | 0.05705 | 0.024415 | 0.058788 | -64.6321 | 0.015142 | -66.7643 | 56.2656 | 56.0739 | 56.1795 | -66.8925 | -66.784 | 0.000359 | -66.878 | 56.2077 | 56.2985 | 56.1872 | -67.0011 | -0.10016 | -0.053091 | 2.1602 | 0.027979 | 0.12814 | -0.2448 | -0.13918 | -0.20885 | -0.11096 | 0.008283 | -0.085746 | 0.1231 | -0.020198 | -0.13146 | 123.0579 | 122.8662 | 122.9718 | 66.8074 | -123.2111 | 123 | 123.0908 | 122.9795 | 66.7927 | -123.3198
304.2812 | 123.3398 | -66.806 | 56.3004 | 0.057113 | -0.031003 | -0.0032469 | 0.052318 | -0.0072692 | 0.047919 | 0.058893 | -0.0050477 | -0.0044937 | 0.055982 | 0.023347 | 0.056652 | -64.6275 | 0.019721 | -66.7689 | 56.2656 | 56.0784 | 56.1795 | -66.8833 | -66.7749 | 0.014095 | -66.8735 | 56.2077 | 56.3076 | 56.1826 | -67.0011 | -0.077273 | -0.03478 | 2.1786 | 0.037134 | 0.11441 | -0.22191 | -0.12087 | -0.19511 | -0.092652 | 0.031173 | -0.067434 | 0.12768 | 0.00727 | -0.11773 | 123.0716 | 122.8845 | 122.9855 | 66.8258 | -123.1837 | 123.0137 | 123.1137 | 122.9887 | 66.8201 | -123.3015
305.2812 | 123.349 | -66.8015 | 56.3095 | 0.041851 | -0.031003 | -0.0043149 | 0.052318 | -0.0083372 | 0.051124 | 0.058893 | -0.0039797 | -0.0044937 | 0.055982 | 0.023347 | 0.05772 | -64.6183 | 0.015142 | -66.7552 | 56.261 | 56.0784 | 56.1703 | -66.8833 | -66.7886 | 0.009516 | -66.8826 | 56.2077 | 56.2985 | 56.178 | -67.0149 | -0.08185 | -0.048514 | 2.1831 | 0.046292 | 0.12814 | -0.23106 | -0.13918 | -0.21343 | -0.10181 | 0.01286 | -0.081168 | 0.13226 | -0.011042 | -0.13146 | 123.0624 | 122.8799 | 122.9718 | 66.8166 | -123.1928 | 123.0092 | 123.0999 | 122.9795 | 66.811 | -123.3244
306.2812 | 123.3444 | -66.7923 | 56.3095 | 0.057113 | -0.032072 | -0.0043149 | 0.051249 | -0.0072692 | 0.048987 | 0.089415 | -0.0050477 | -0.0034247 | 0.05705 | 0.023347 | 0.056652 | -64.6092 | 0.019721 | -66.7689 | 56.2702 | 56.083 | 56.1749 | -66.8741 | -66.7977 | 0.014095 | -66.8735 | 56.2123 | 56.303 | 56.1918 | -67.0103 | -0.081848 | -0.039357 | 2.1831 | 0.023401 | 0.10525 | -0.22648 | -0.13461 | -0.218 | -0.097228 | -0.005453 | -0.081167 | 0.13684 | -0.006463 | -0.11773 | 123.0624 | 122.8753 | 122.9672 | 66.812 | -123.1837 | 123.0046 | 123.0953 | 122.9841 | 66.8064 | -123.3198
307.2812 | 123.3536 | -66.7877 | 56.3232 | 0.057113 | -0.031003 | -0.0032469 | 0.052318 | -0.0072692 | 0.051124 | 0.058893 | -0.0050477 | -0.0055617 | 0.05705 | 0.024415 | 0.056652 | -64.6275 | 0.010564 | -66.7689 | 56.2702 | 56.0922 | 56.1749 | -66.865 | -66.7886 | 0.009516 | -66.8735 | 56.2077 | 56.303 | 56.1918 | -67.0103 | -0.077267 | -0.05309 | 2.1602 | 0.018824 | 0.096091 | -0.23106 | -0.14834 | -0.22258 | -0.11554 | -0.000873 | -0.085744 | 0.13684 | -0.020196 | -0.13146 | 123.0579 | 122.8799 | 122.9626 | 66.7983 | -123.1882 | 122.9954 | 123.0908 | 122.9795 | 66.7972 | -123.3335
308.2812 | 123.3673 | -66.7603 | 56.3141 | 0.057113 | -0.032072 | -0.0032469 | 0.052318 | -0.0083372 | 0.050055 | 0.058893 | -0.0050477 | -0.0044937 | 0.054914 | 0.024415 | 0.055583 | -64.6229 | 0.010564 | -66.7597 | 56.261 | 56.0968 | 56.1749 | -66.8741 | -66.784 | 0.014095 | -66.878 | 56.2031 | 56.3076 | 56.1964 | -67.0103 | -0.11389 | -0.053092 | 2.1374 | 0.000514 | 0.11441 | -0.21732 | -0.13918 | -0.25005 | -0.11096 | -0.02376 | -0.11779 | 0.13226 | -0.006463 | -0.11773 | 123.0212 | 122.857 | 122.9352 | 66.7708 | -123.1882 | 122.9634 | 123.0679 | 122.9566 | 66.7743 | -123.3244
309.2812 | 123.3627 | -66.7603 | 56.3324 | 0.057113 | -0.031003 | -0.0053839 | 0.051249 | -0.0072692 | 0.050055 | 0.074154 | -0.0061157 | -0.0034247 | 0.058119 | 0.024415 | 0.055583 | -64.6321 | 0.010564 | -66.7552 | 56.261 | 56.0876 | 56.1795 | -66.8696 | -66.7932 | 0.009516 | -66.8826 | 56.2077 | 56.303 | 56.1964 | -67.0057 | -0.10931 | -0.071402 | 2.1282 | 0.005093 | 0.11441 | -0.24479 | -0.15292 | -0.24547 | -0.1247 | -0.032918 | -0.12237 | 0.1231 | -0.029351 | -0.13604 | 123.0212 | 122.8479 | 122.9397 | 66.7708 | -123.202 | 122.968 | 123.0633 | 122.9566 | 66.7698 | -123.3381
310.2812 | 123.3948 | -66.7786 | 56.3095 | 0.041851 | -0.029935 | -0.0032469 | 0.051249 | -0.0083372 | 0.051124 | 0.058893 | -0.0039797 | -0.0034247 | 0.05705 | 0.023347 | 0.056652 | -64.5908 | 0.005985 | -66.7643 | 56.2656 | 56.0922 | 56.1795 | -66.8787 | -66.7932 | 0.004938 | -66.8826 | 56.2077 | 56.2939 | 56.1964 | -67.0057 | -0.10016 | -0.043935 | 2.1877 | 0.014246 | 0.11441 | -0.21732 | -0.13003 | -0.22716 | -0.10181 | -0.014608 | -0.10406 | 0.1231 | -0.01562 | -0.11315 | 123.0441 | 122.8707 | 122.958 | 66.7845 | -123.1882 | 122.9863 | 123.0725 | 122.9749 | 66.7835 | -123.3152
311.2812 | 123.381 | -66.7923 | 56.3095 | 0.087637 | -0.031003 | -0.0032469 | 0.051249 | -0.0094052 | 0.050055 | 0.089415 | -0.0039797 | -0.0034247 | 0.05705 | 0.025483 | 0.054515 | -64.5863 | 0.015142 | -66.7689 | 56.2702 | 56.0876 | 56.1749 | -66.865 | -66.7886 | 0.009516 | -66.8826 | 56.2031 | 56.303 | 56.2009 | -67.0011 | -0.07269 | -0.039357 | 2.206 | 0.023401 | 0.096091 | -0.2219 | -0.13461 | -0.20885 | -0.10638 | 0.003704 | -0.090324 | 0.11852 | -0.006463 | -0.10857 | 123.0624 | 122.8799 | 122.9672 | 66.8074 | -123.1745 | 122.9954 | 123.0953 | 122.9932 | 66.8018 | -123.3107
312.2812 | 123.3856 | -66.7557 | 56.3324 | 0.057113 | -0.03314 | -0.0032469 | 0.052318 | -0.0062002 | 0.050055 | 0.089415 | -0.0039797 | -0.0044937 | 0.055982 | 0.025483 | 0.055583 | -64.6183 | 0.019721 | -66.7643 | 56.2702 | 56.0876 | 56.1795 | -66.8787 | -66.7932 | 0.018674 | -66.8826 | 56.2031 | 56.303 | 56.2009 | -67.0057 | -0.12305 | -0.062245 | 2.1374 | -0.008642 | 0.11441 | -0.24479 | -0.15292 | -0.25005 | -0.12927 | -0.037496 | -0.12695 | 0.1231 | -0.029351 | -0.13146 | 123.0258 | 122.8433 | 122.9352 | 66.7754 | -123.2111 | 122.9588 | 123.0587 | 122.9566 | 66.7743 | -123.3381
313.2812 | 123.3444 | -66.7923 | 56.3049 | 0.057113 | -0.032072 | -0.0011099 | 0.051249 | -0.0072692 | 0.050055 | 0.074154 | -0.0050477 | -0.0044937 | 0.055982 | 0.025483 | 0.056652 | -64.6 | 0.005985 | -66.7552 | 56.261 | 56.0922 | 56.1749 | -66.8833 | -66.7932 | 0.009516 | -66.8872 | 56.2031 | 56.303 | 56.2009 | -67.0103 | -0.091006 | -0.043937 | 2.1923 | 0.037136 | 0.12814 | -0.21275 | -0.13003 | -0.218 | -0.10181 | -0.000875 | -0.094903 | 0.1231 | -0.001886 | -0.10399 | 123.0533 | 122.8845 | 122.9672 | 66.7983 | -123.1882 | 122.9954 | 123.0953 | 122.9932 | 66.8018 | -123.3152
314.2812 | 123.3673 | -66.7786 | 56.3141 | 0.057113 | -0.032072 | -0.0021789 | 0.050181 | -0.0062002 | 0.050055 | 0.074154 | -0.0050477 | -0.0044937 | 0.055982 | 0.025483 | 0.054515 | -64.6 | 0.010564 | -66.7597 | 56.2702 | 56.0922 | 56.1795 | -66.8879 | -66.7886 | 0.014095 | -66.8872 | 56.2077 | 56.303 | 56.1918 | -67.0011 | -0.10932 | -0.043935 | 2.1786 | 0.018824 | 0.12814 | -0.2219 | -0.13461 | -0.22258 | -0.10639 | -0.010029 | -0.10864 | 0.11394 | -0.011041 | -0.1223 | 123.0487 | 122.8707 | 122.958 | 66.7891 | -123.202 | 122.9863 | 123.0816 | 122.9703 | 66.7927 | -123.3152
315.2812 | 123.3627 | -66.7877 | 56.3049 | 0.087637 | -0.032072 | -0.0021789 | 0.049112 | -0.0083372 | 0.050055 | 0.074154 | -0.0050477 | -0.0044937 | 0.058119 | 0.025483 | 0.055583 | -64.6092 | 0.015142 | -66.7597 | 56.2656 | 56.0922 | 56.1749 | -66.8696 | -66.7886 | 0.014095 | -66.8826 | 56.2077 | 56.2985 | 56.2009 | -67.0057 | -0.081846 | -0.039358 | 2.1786 | 0.02798 | 0.10983 | -0.21275 | -0.13003 | -0.218 | -0.09723 | -0.000873 | -0.094901 | 0.1231 | -0.006465 | -0.10399 | 123.0533 | 122.8799 | 122.9626 | 66.8029 | -123.1745 | 122.9954 | 123.0862 | 122.9887 | 66.8018 | -123.3107
316.2812 | 123.349 | -66.8015 | 56.3324 | 0.041851 | -0.032072 | -0.0032469 | 0.052318 | -0.0072692 | 0.051124 | 0.074154 | -0.0039797 | -0.0055617 | 0.054914 | 0.025483 | 0.055583 | -64.6275 | 0.010564 | -66.7552 | 56.2656 | 56.0968 | 56.1703 | -66.8787 | -66.7886 | 0.009516 | -66.8826 | 56.2077 | 56.303 | 56.1964 | -67.0103 | -0.077271 | -0.066823 | 2.174 | 0.046292 | 0.12356 | -0.23563 | -0.16207 | -0.20885 | -0.1247 | 0.01286 | -0.081168 | 0.12768 | -0.029351 | -0.13604 | 123.067 | 122.8982 | 122.9718 | 66.812 | -123.2111 | 123.0092 | 123.1045 | 122.9978 | 66.811 | -123.3427
317.2812 | 123.381 | -66.7557 | 56.3416 | 0.072375 | -0.03314 | -0.0043149 | 0.050181 | -0.0083372 | 0.051124 | 0.074154 | -0.0039797 | -0.0044937 | 0.05705 | 0.025483 | 0.055583 | -64.5863 | 0.010564 | -66.7552 | 56.261 | 56.0968 | 56.1749 | -66.8787 | -66.7749 | 0.009516 | -66.8826 | 56.2123 | 56.303 | 56.2101 | -67.0103 | -0.12305 | -0.080558 | 2.1694 | 0.000515 | 0.12356 | -0.24479 | -0.16665 | -0.25463 | -0.12927 | -0.019181 | -0.12695 | 0.12768 | -0.038507 | -0.13146 | 123.0167 | 122.8524 | 122.9306 | 66.7662 | -123.2203 | 122.968 | 123.0587 | 122.9658 | 66.7652 | -123.3519
318.2812 | 123.3948 | -66.7511 | 56.3049 | 0.072375 | -0.032072 | -0.0032469 | 0.051249 | -0.0072692 | 0.050055 | 0.074154 | -0.0050477 | -0.0034247 | 0.05705 | 0.024415 | 0.054515 | -64.5771 | 0.010564 | -66.7552 | 56.2702 | 56.0922 | 56.1795 | -66.8787 | -66.7794 | 0.004938 | -66.878 | 56.2077 | 56.3076 | 56.2101 | -67.0103 | -0.12763 | -0.03478 | 2.174 | -0.004062 | 0.12356 | -0.21275 | -0.12545 | -0.2592 | -0.09723 | -0.028337 | -0.12694 | 0.13226 | 0.002692 | -0.094835 | 123.0213 | 122.8433 | 122.9306 | 66.7617 | -123.1837 | 122.9588 | 123.0587 | 122.9612 | 66.756 | -123.3152
319.2812 | 123.3765 | -66.8015 | 56.2958 | 0.041851 | -0.03314 | -0.0021789 | 0.050181 | -0.0072692 | 0.051124 | 0.058893 | -0.0050477 | -0.0023567 | 0.055982 | 0.024415 | 0.054515 | -64.6046 | 0.010564 | -66.7552 | 56.2747 | 56.0968 | 56.1749 | -66.8879 | -66.7886 | 0.004938 | -66.8872 | 56.2169 | 56.303 | 56.2009 | -67.0149 | -0.086429 | -0.021045 | 2.1969 | 0.046292 | 0.13272 | -0.19901 | -0.12087 | -0.21343 | -0.078917 | 0.01286 | -0.085747 | 0.12768 | 0.00727 | -0.094837 | 123.0762 | 122.8982 | 122.9764 | 66.812 | -123.1837 | 123.0183 | 123.1045 | 123.0024 | 66.8064 | -123.3107
320.2812 | 123.3673 | -66.774 | 56.3324 | 0.057113 | -0.031003 | -0.0032469 | 0.049112 | -0.0062002 | 0.051124 | 0.074154 | -0.0039797 | -0.0044937 | 0.05705 | 0.026552 | 0.054515 | -64.6229 | 0.010564 | -66.7597 | 56.2702 | 56.0922 | 56.1841 | -66.8833 | -66.7886 | 0.014095 | -66.8826 | 56.2077 | 56.3076 | 56.2009 | -67.0103 | -0.10932 | -0.062245 | 2.1511 | 0.014247 | 0.12356 | -0.24021 | -0.14834 | -0.23631 | -0.1247 | -0.014606 | -0.10863 | 0.12768 | -0.024773 | -0.13146 | 123.0441 | 122.8662 | 122.958 | 66.7846 | -123.2157 | 122.9817 | 123.0816 | 122.9749 | 66.7881 | -123.3427
321.2812 | 123.4222 | -66.8015 | 56.2866 | 0.057113 | -0.03314 | -0.0021789 | 0.052318 | -0.0072692 | 0.051124 | 0.043632 | -0.0050477 | -0.0044937 | 0.055982 | 0.025483 | 0.055583 | -64.5908 | 0.010564 | -66.7597 | 56.2702 | 56.0968 | 56.1795 | -66.8741 | -66.7886 | 0.009516 | -66.8735 | 56.2123 | 56.3076 | 56.1964 | -67.0057 | -0.072692 | -0.016469 | 2.2106 | 0.041713 | 0.11441 | -0.18986 | -0.10714 | -0.20427 | -0.07434 | 0.01286 | -0.072011 | 0.13226 | 0.021003 | -0.09026 | 123.0716 | 122.8982 | 122.9809 | 66.812 | -123.1608 | 123.0137 | 123.1091 | 122.9978 | 66.811 | -123.2923
322.2812 | 123.3536 | -66.774 | 56.3095 | 0.057113 | -0.03314 | -0.0021789 | 0.050181 | -0.0083372 | 0.051124 | 0.058893 | -0.0039797 | -0.0034247 | 0.054914 | 0.026552 | 0.055583 | -64.6321 | 0.019721 | -66.7597 | 56.2793 | 56.0922 | 56.1795 | -66.8696 | -66.7932 | 0.000359 | -66.878 | 56.2077 | 56.303 | 56.2055 | -67.0011 | -0.095579 | -0.0302 | 2.1419 | 0.014247 | 0.10983 | -0.21732 | -0.13003 | -0.22716 | -0.10181 | -0.019185 | -0.10406 | 0.1231 | -0.006463 | -0.10399 | 123.0533 | 122.8662 | 122.9535 | 66.7937 | -123.1791 | 122.9817 | 123.077 | 122.9795 | 66.7743 | -123.3107
323.2812 | 123.3719 | -66.7877 | 56.3004 | 0.057113 | -0.032072 | -0.0032469 | 0.051249 | -0.0094052 | 0.051124 | 0.043632 | -0.0029117 | -0.0044937 | 0.055982 | 0.024415 | 0.055583 | -64.5908 | 0.010564 | -66.7552 | 56.2656 | 56.0876 | 56.1841 | -66.8787 | -66.7794 | 0.004938 | -66.8872 | 56.2123 | 56.303 | 56.1964 | -67.0011 | -0.091004 | -0.03478 | 2.1969 | 0.032559 | 0.12356 | -0.21275 | -0.11629 | -0.21342 | -0.088073 | 0.008284 | -0.09948 | 0.11394 | 0.002692 | -0.10399 | 123.0533 | 122.8753 | 122.9718 | 66.7983 | -123.1791 | 123 | 123.0908 | 122.9841 | 66.7927 | -123.3015
324.2812 | 123.3902 | -66.7603 | 56.3187 | 0.072375 | -0.03314 | -0.0032469 | 0.051249 | -0.0062002 | 0.051124 | 0.058893 | -0.0050477 | -0.0023567 | 0.055982 | 0.025483 | 0.055583 | -64.5817 | 0.019721 | -66.7597 | 56.2702 | 56.0922 | 56.1795 | -66.8741 | -66.7794 | 0.004938 | -66.8689 | 56.2123 | 56.303 | 56.2009 | -67.0011 | -0.11389 | -0.048513 | 2.1786 | 0.000514 | 0.11441 | -0.22648 | -0.13918 | -0.24089 | -0.10638 | -0.019182 | -0.10863 | 0.13226 | -0.015619 | -0.11773 | 123.0304 | 122.8524 | 122.9397 | 66.78 | -123.1928 | 122.9725 | 123.0633 | 122.9612 | 66.7652 | -123.3198
325.2812 | 123.3444 | -66.806 | 56.3141 | 0.041851 | -0.032072 | -0.0032469 | 0.051249 | -0.0083372 | 0.051124 | 0.043632 | -0.0029117 | -0.0044937 | 0.05705 | 0.025483 | 0.054515 | -64.5954 | 0.015142 | -66.746 | 56.2747 | 56.0968 | 56.1841 | -66.8741 | -66.7794 | 0.004938 | -66.8826 | 56.2077 | 56.303 | 56.2147 | -67.0103 | -0.068115 | -0.039356 | 2.2106 | 0.060025 | 0.12814 | -0.21732 | -0.13003 | -0.20427 | -0.10639 | 0.026594 | -0.076591 | 0.12768 | -0.011041 | -0.099412 | 123.0808 | 122.9028 | 122.9901 | 66.8212 | -123.1882 | 123.0137 | 123.1091 | 123.0207 | 66.811 | -123.3244
326.2812 | 123.3765 | -66.774 | 56.2958 | 0.057113 | -0.034208 | -0.0032469 | 0.052318 | -0.0072692 | 0.051124 | 0.058893 | -0.0039797 | -0.0055617 | 0.055982 | 0.024415 | 0.056652 | -64.5725 | 0.010564 | -66.7597 | 56.2702 | 56.0922 | 56.1841 | -66.8513 | -66.7794 | 0.004938 | -66.878 | 56.2123 | 56.303 | 56.1964 | -67.0057 | -0.077264 | -0.025624 | 2.2015 | 0.014247 | 0.091511 | -0.20359 | -0.11171 | -0.23174 | -0.083495 | -0.005449 | -0.10406 | 0.12768 | 0.00727 | -0.099415 | 123.0441 | 122.8662 | 122.958 | 66.7846 | -123.147 | 122.9863 | 123.077 | 122.9703 | 66.7789 | -123.3015
327.2812 | 123.3398 | -66.7694 | 56.3187 | 0.057113 | -0.035277 | -0.0043149 | 0.051249 | -0.0062002 | 0.052192 | 0.074154 | -0.0050477 | -0.0012887 | 0.05705 | 0.024415 | 0.055583 | -64.6275 | 0.010564 | -66.7506 | 56.2702 | 56.0922 | 56.1841 | -66.8925 | -66.7749 | 0.000359 | -66.8735 | 56.2077 | 56.3122 | 56.2055 | -67.0057 | -0.12305 | -0.048513 | 2.1419 | 0.018826 | 0.14188 | -0.22648 | -0.1346 | -0.23631 | -0.11096 | -0.005448 | -0.10406 | 0.13226 | -0.006462 | -0.11315 | 123.0396 | 122.8616 | 122.9535 | 66.78 | -123.2111 | 122.9771 | 123.0816 | 122.9749 | 66.7698 | -123.3244
328.2812 | 123.3673 | -66.7786 | 56.2958 | 0.041851 | -0.036345 | -0.0032469 | 0.050181 | -0.010474 | 0.048987 | 0.074154 | -0.0050477 | -0.0044937 | 0.054914 | 0.025483 | 0.055583 | -64.6046 | 0.010564 | -66.7597 | 56.2793 | 56.1013 | 56.1749 | -66.8879 | -66.784 | 0.004938 | -66.8826 | 56.2077 | 56.2985 | 56.2055 | -67.0103 | -0.10932 | -0.016467 | 2.174 | 0.018824 | 0.12814 | -0.19443 | -0.12087 | -0.23174 | -0.088074 | -0.00545 | -0.10406 | 0.12768 | 0.002691 | -0.090258 | 123.0579 | 122.8799 | 122.9535 | 66.7891 | -123.1837 | 122.9863 | 123.077 | 122.9841 | 66.7835 | -123.3061
329.2812 | 123.3353 | -66.7877 | 56.3187 | 0.072375 | -0.034208 | -0.0043149 | 0.050181 | -0.0072692 | 0.048987 | 0.058893 | -0.0039797 | -0.0023567 | 0.05705 | 0.023347 | 0.055583 | -64.6046 | 0.010564 | -66.7506 | 56.2747 | 56.0968 | 56.1841 | -66.8879 | -66.7886 | -0.00422 | -66.878 | 56.2077 | 56.303 | 56.2055 | -67.0057 | -0.10016 | -0.043934 | 2.1831 | 0.037137 | 0.1373 | -0.2219 | -0.1346 | -0.218 | -0.11096 | -0.000873 | -0.090323 | 0.12768 | -0.015619 | -0.11315 | 123.0625 | 122.8845 | 122.9718 | 66.7983 | -123.2065 | 122.9954 | 123.0908 | 122.9932 | 66.7835 | -123.3244
330.2812 | 123.381 | -66.7877 | 56.2958 | 0.041851 | -0.032072 | -0.0021789 | 0.053386 | -0.0083372 | 0.050055 | 0.089415 | -0.0061157 | -0.0044937 | 0.055982 | 0.026552 | 0.055583 | -64.5634 | 0.015142 | -66.7552 | 56.2656 | 56.0968 | 56.1886 | -66.8787 | -66.7749 | 0.000359 | -66.878 | 56.2123 | 56.3076 | 56.2101 | -67.0057 | -0.091004 | -0.030202 | 2.2243 | 0.032559 | 0.12356 | -0.19901 | -0.10714 | -0.218 | -0.083495 | 0.012863 | -0.090323 | 0.12768 | 0.011848 | -0.085679 | 123.0533 | 122.8845 | 122.9764 | 66.8029 | -123.1745 | 123 | 123.0953 | 122.9978 | 66.7881 | -123.3015
331.2812 | 123.2529 | -66.8015 | 56.3507 | 0.087637 | -0.035277 | -0.0032469 | 0.052318 | -0.0094052 | 0.050055 | 0.089415 | -0.0050477 | -0.0023567 | 0.05705 | 0.02762 | 0.053447 | -64.5496 | 0.005985 | -66.7506 | 56.2793 | 56.0968 | 56.1841 | -66.8696 | -66.784 | 0.000359 | -66.8735 | 56.2123 | 56.3076 | 56.2101 | -67.0011 | -0.068113 | -0.071399 | 2.2518 | 0.05087 | 0.11898 | -0.25394 | -0.16665 | -0.19969 | -0.13843 | 0.017439 | -0.072011 | 0.12768 | -0.043084 | -0.14061 | 123.0808 | 122.8982 | 122.9855 | 66.8074 | -123.2203 | 123.0137 | 123.1091 | 123.0115 | 66.8018 | -123.3519
332.2812 | 123.3215 | -66.8015 | 56.3095 | 0.041851 | -0.034208 | -0.0032469 | 0.049112 | -0.0083372 | 0.050055 | 0.058893 | -0.0050477 | -0.0044937 | 0.054914 | 0.02762 | 0.055583 | -64.5634 | 0.005985 | -66.7506 | 56.2747 | 56.0968 | 56.1841 | -66.865 | -66.7794 | 0.000359 | -66.8735 | 56.2123 | 56.2939 | 56.1964 | -67.0011 | -0.063534 | -0.034778 | 2.2381 | 0.05087 | 0.1144 | -0.21274 | -0.12545 | -0.19969 | -0.097228 | 0.022017 | -0.072011 | 0.12768 | -0.01562 | -0.11315 | 123.0762 | 122.8982 | 122.9855 | 66.8074 | -123.1745 | 123.0137 | 123.0953 | 122.9978 | 66.8018 | -123.3107
333.2812 | 123.3719 | -66.7603 | 56.3004 | 0.072375 | -0.034208 | -0.0021789 | 0.051249 | -0.0094052 | 0.050055 | 0.074154 | -0.0050477 | -0.0034247 | 0.05705 | 0.026552 | 0.054515 | -64.5863 | 0.005985 | -66.7597 | 56.2747 | 56.0968 | 56.1932 | -66.865 | -66.7794 | -0.00422 | -66.8735 | 56.2214 | 56.2939 | 56.2055 | -67.0057 | -0.10473 | -0.025623 | 2.174 | 0.000514 | 0.10525 | -0.20359 | -0.10714 | -0.24547 | -0.078916 | -0.019182 | -0.11321 | 0.13226 | -0.006465 | -0.094836 | 123.035 | 122.857 | 122.9535 | 66.7662 | -123.1653 | 122.9817 | 123.0541 | 122.9658 | 66.756 | -123.3061
334.2812 | 123.2849 | -66.8106 | 56.3324 | 0.057113 | -0.034208 | -0.0032469 | 0.050181 | -0.0072692 | 0.050055 | 0.058893 | -0.0039797 | -0.0055617 | 0.05705 | 0.026552 | 0.055583 | -64.5542 | 0.005985 | -66.7552 | 56.2702 | 56.0968 | 56.1886 | -66.865 | -66.7794 | 0.000359 | -66.8735 | 56.2169 | 56.2985 | 56.2147 | -66.9966 | -0.054379 | -0.062245 | 2.2564 | 0.055447 | 0.10983 | -0.23563 | -0.14376 | -0.18596 | -0.11554 | 0.031172 | -0.062856 | 0.1231 | -0.03393 | -0.11772 | 123.0808 | 122.9074 | 122.9992 | 66.8166 | -123.1974 | 123.0275 | 123.1091 | 123.0253 | 66.811 | -123.329
335.2812 | 123.3444 | -66.7969 | 56.3187 | 0.041851 | -0.03314 | -0.0064519 | 0.050181 | -0.0094052 | 0.051124 | 0.089415 | -0.0050477 | -0.0034247 | 0.055982 | 0.025483 | 0.054515 | -64.5634 | 0.015142 | -66.7414 | 56.2747 | 56.0968 | 56.1841 | -66.8741 | -66.7794 | -0.00422 | -66.8735 | 56.2169 | 56.303 | 56.2009 | -67.0057 | -0.07727 | -0.043934 | 2.2335 | 0.055448 | 0.13272 | -0.2219 | -0.1346 | -0.20885 | -0.10181 | 0.017439 | -0.076589 | 0.13226 | -0.015619 | -0.11773 | 123.0716 | 122.8936 | 122.9809 | 66.812 | -123.1928 | 123.0137 | 123.0999 | 122.9978 | 66.7927 | -123.3244
336.2812 | 123.3078 | -66.8243 | 56.3232 | 0.041851 | -0.035277 | -0.0032469 | 0.051249 | -0.0072692 | 0.050055 | 0.058893 | -0.0039797 | -0.0023567 | 0.055982 | 0.026552 | 0.054515 | -64.5634 | -0.003172 | -66.7552 | 56.2747 | 56.1013 | 56.1841 | -66.8833 | -66.784 | -0.00422 | -66.8735 | 56.2169 | 56.2985 | 56.2101 | -67.0011 | -0.058962 | -0.048511 | 2.261 | 0.06918 | 0.12814 | -0.2219 | -0.13918 | -0.1768 | -0.10638 | 0.040327 | -0.049123 | 0.12768 | -0.024775 | -0.11315 | 123.0991 | 122.9257 | 123.0084 | 66.8212 | -123.2065 | 123.0412 | 123.1228 | 123.0344 | 66.8201 | -123.3244
337.2812 | 123.349 | -66.7786 | 56.3141 | 0.057113 | -0.034208 | -0.0075209 | 0.051249 | -0.0083372 | 0.051124 | 0.058893 | -0.0050477 | -0.0055617 | 0.055982 | 0.02762 | 0.055583 | -64.6229 | 0.001407 | -66.7552 | 56.2702 | 56.0968 | 56.1886 | -66.8696 | -66.784 | -0.008798 | -66.878 | 56.2123 | 56.3168 | 56.2101 | -66.9966 | -0.091002 | -0.043935 | 2.1557 | 0.023403 | 0.11441 | -0.21732 | -0.12545 | -0.218 | -0.10181 | -0.00545 | -0.099479 | 0.11852 | 0.002695 | -0.10399 | 123.0487 | 122.8753 | 122.9672 | 66.78 | -123.1837 | 122.9908 | 123.0953 | 122.9887 | 66.7698 | -123.3107
338.2812 | 123.262 | -66.8243 | 56.3416 | 0.072375 | -0.034208 | -0.0043149 | 0.052318 | -0.0094052 | 0.047919 | 0.089415 | -0.0050477 | -0.0055617 | 0.054914 | 0.02762 | 0.053447 | -64.5359 | 0.010564 | -66.7597 | 56.2747 | 56.1013 | 56.1886 | -66.8787 | -66.784 | -0.008798 | -66.8735 | 56.226 | 56.3076 | 56.2147 | -67.0011 | -0.054383 | -0.066822 | 2.2884 | 0.064601 | 0.11898 | -0.24021 | -0.15291 | -0.1768 | -0.11554 | 0.040327 | -0.049123 | 0.12768 | -0.033929 | -0.12688 | 123.0991 | 122.9257 | 123.013 | 66.8349 | -123.2203 | 123.0504 | 123.132 | 123.039 | 66.8155 | -123.3427
339.2812 | 123.2208 | -66.8015 | 56.3416 | 0.026589 | -0.03314 | -0.0043149 | 0.050181 | -0.0094052 | 0.04685 | 0.058893 | -0.0050477 | -0.0044937 | 0.055982 | 0.026552 | 0.054515 | -64.5359 | 0.001407 | -66.7506 | 56.2702 | 56.1013 | 56.1932 | -66.8833 | -66.7794 | -0.00422 | -66.8735 | 56.2169 | 56.3122 | 56.2055 | -67.0057 | -0.08185 | -0.071401 | 2.2655 | 0.05087 | 0.13272 | -0.24021 | -0.14833 | -0.20427 | -0.12469 | 0.022017 | -0.072011 | 0.13226 | -0.02935 | -0.13603 | 123.0716 | 122.9028 | 122.9947 | 66.8029 | -123.2249 | 123.0183 | 123.1137 | 123.007 | 66.7972 | -123.3473
340.2812 | 123.2895 | -66.8289 | 56.3553 | 0.041851 | -0.034208 | -0.0043149 | 0.049112 | -0.0072692 | 0.051124 | 0.058893 | -0.0039797 | -0.0055617 | 0.054914 | 0.026552 | 0.053447 | -64.5588 | 0.010564 | -66.7506 | 56.2747 | 56.1013 | 56.1932 | -66.8787 | -66.784 | -0.00422 | -66.8735 | 56.2077 | 56.3168 | 56.2238 | -66.992 | -0.049806 | -0.080555 | 2.2701 | 0.078335 | 0.12814 | -0.25394 | -0.16207 | -0.16307 | -0.14758 | 0.044904 | -0.044546 | 0.11852 | -0.038504 | -0.13145 | 123.1036 | 122.9303 | 123.0221 | 66.8395 | -123.234 | 123.0366 | 123.1457 | 123.0528 | 66.8247 | -123.3473
341.2812 | 123.349 | -66.774 | 56.2866 | 0.072375 | -0.035277 | -0.0043149 | 0.050181 | -0.0062002 | 0.048987 | 0.074154 | -0.0061157 | -0.0044937 | 0.055982 | 0.028688 | 0.053447 | -64.568 | 0.005985 | -66.7506 | 56.2702 | 56.0968 | 56.1932 | -66.8787 | -66.7794 | -0.013377 | -66.878 | 56.2123 | 56.3168 | 56.2009 | -66.9966 | -0.10474 | -0.016469 | 2.206 | 0.023404 | 0.12814 | -0.18986 | -0.093403 | -0.22258 | -0.07434 | -0.005449 | -0.10406 | 0.11852 | 0.030161 | -0.085682 | 123.0441 | 122.8708 | 122.9672 | 66.78 | -123.1653 | 122.9863 | 123.0908 | 122.9749 | 66.7606 | -123.2832
342.2812 | 123.3765 | -66.7603 | 56.3461 | 0.057113 | -0.03314 | -0.0043149 | 0.050181 | -0.0094052 | 0.048987 | 0.089415 | -0.0039797 | -0.0044937 | 0.055982 | 0.028688 | 0.054515 | -64.6229 | -0.003172 | -66.7552 | 56.2656 | 56.1059 | 56.1886 | -66.8741 | -66.7794 | -0.00422 | -66.8735 | 56.2214 | 56.3122 | 56.2101 | -67.0011 | -0.11389 | -0.080556 | 2.1374 | 0.005093 | 0.11898 | -0.24021 | -0.15749 | -0.24089 | -0.12469 | -0.019182 | -0.11321 | 0.12768 | -0.033927 | -0.13603 | 123.0258 | 122.8662 | 122.9489 | 66.7571 | -123.2203 | 122.9817 | 123.0725 | 122.9704 | 66.756 | -123.3473
343.2812 | 123.2712 | -66.8335 | 56.3599 | 0.041851 | -0.035277 | -0.0032469 | 0.051249 | -0.0072692 | 0.050055 | 0.028371 | -0.0039797 | -0.0044937 | 0.055982 | 0.026552 | 0.053447 | -64.5405 | 0.001407 | -66.7552 | 56.2747 | 56.1059 | 56.1886 | -66.865 | -66.784 | -0.00422 | -66.878 | 56.2123 | 56.3076 | 56.2009 | -67.0011 | -0.031491 | -0.085132 | 2.293 | 0.078335 | 0.10983 | -0.25394 | -0.17122 | -0.16765 | -0.14758 | 0.049482 | -0.044547 | 0.1231 | -0.052239 | -0.15892 | 123.1082 | 122.9394 | 123.0221 | 66.8349 | -123.2249 | 123.0458 | 123.1411 | 123.0344 | 66.8293 | -123.361
344.2812 | 123.2391 | -66.8335 | 56.3644 | 0.057113 | -0.035277 | -0.0043149 | 0.050181 | -0.010474 | 0.050055 | 0.089415 | -0.0050477 | -0.0044937 | 0.055982 | 0.02762 | 0.055583 | -64.5405 | -0.003172 | -66.7552 | 56.2702 | 56.1059 | 56.1978 | -66.8696 | -66.7749 | -0.008798 | -66.8689 | 56.2123 | 56.3076 | 56.2055 | -67.0057 | -0.03607 | -0.094289 | 2.293 | 0.078335 | 0.11441 | -0.25852 | -0.16664 | -0.17223 | -0.15216 | 0.058639 | -0.035389 | 0.13684 | -0.056817 | -0.15892 | 123.1036 | 122.9394 | 123.0313 | 66.8303 | -123.234 | 123.0458 | 123.1411 | 123.039 | 66.8247 | -123.3702
345.2812 | 123.2391 | -66.8152 | 56.3507 | 0.026589 | -0.036345 | -0.0032469 | 0.052318 | -0.0083372 | 0.051124 | 0.058893 | -0.0061157 | -0.0044937 | 0.055982 | 0.025483 | 0.054515 | -64.5405 | -0.003172 | -66.7552 | 56.2747 | 56.1013 | 56.1978 | -66.8604 | -66.7703 | -0.008798 | -66.8643 | 56.2169 | 56.3122 | 56.2055 | -67.0011 | -0.045222 | -0.075977 | 2.2747 | 0.060025 | 0.10525 | -0.24937 | -0.15291 | -0.18596 | -0.13385 | 0.044908 | -0.049121 | 0.13684 | -0.038505 | -0.14519 | 123.0899 | 122.9165 | 123.013 | 66.812 | -123.2111 | 123.032 | 123.1274 | 123.0207 | 66.8064 | -123.3519
346.2812 | 123.2391 | -66.8106 | 56.3416 | 0.041851 | -0.035277 | -0.0043149 | 0.050181 | -0.010474 | 0.048987 | 0.074154 | -0.0039797 | -0.0023567 | 0.055982 | 0.028688 | 0.055583 | -64.5222 | -0.007751 | -66.7552 | 56.2839 | 56.1059 | 56.1932 | -66.8741 | -66.7794 | -0.013377 | -66.8689 | 56.2169 | 56.3076 | 56.2055 | -67.0011 | -0.063537 | -0.057666 | 2.2884 | 0.055447 | 0.11898 | -0.23563 | -0.14833 | -0.19053 | -0.12469 | 0.031172 | -0.058277 | 0.13226 | -0.033929 | -0.13603 | 123.0945 | 122.9165 | 123.0038 | 66.8029 | -123.2157 | 123.0275 | 123.1182 | 123.0161 | 66.7972 | -123.3427
347.2812 | 123.3032 | -66.806 | 56.3278 | 0.041851 | -0.037413 | -0.0043149 | 0.051249 | -0.0094052 | 0.050055 | 0.058893 | -0.0061157 | -0.0044937 | 0.055982 | 0.025483 | 0.052379 | -64.5405 | -0.007751 | -66.746 | 56.2793 | 56.1105 | 56.1932 | -66.865 | -66.7749 | -0.008798 | -66.8689 | 56.2169 | 56.3076 | 56.2238 | -66.9966 | -0.058957 | -0.048511 | 2.2655 | 0.060025 | 0.11898 | -0.21732 | -0.1346 | -0.19053 | -0.11096 | 0.031173 | -0.062855 | 0.12768 | -0.020196 | -0.10399 | 123.0853 | 122.9165 | 122.9992 | 66.7983 | -123.1928 | 123.0229 | 123.1137 | 123.0299 | 66.7972 | -123.3244
348.3125 | 123.2803 | -66.774 | 56.3782 | 0.072375 | -0.036345 | -0.0032469 | 0.051249 | -0.0083372 | 0.048987 | 0.058893 | -0.0061157 | -0.0055617 | 0.055982 | 0.028688 | 0.054515 | -64.5313 | 0.005985 | -66.7506 | 56.2839 | 56.1105 | 56.1932 | -66.8741 | -66.7703 | -0.013377 | -66.8689 | 56.2214 | 56.3122 | 56.2147 | -66.9966 | -0.10016 | -0.094287 | 2.2427 | 0.023404 | 0.12356 | -0.26767 | -0.18496 | -0.22258 | -0.15674 | 0.003709 | -0.094898 | 0.12768 | -0.065971 | -0.1635 | 123.0579 | 122.8845 | 122.9672 | 66.78 | -123.2523 | 122.9954 | 123.0862 | 122.9887 | 66.7606 | -123.3747
349.2812 | 123.3032 | -66.8015 | 56.3324 | 0.026589 | -0.035277 | -0.0032469 | 0.050181 | -0.010474 | 0.050055 | 0.074154 | -0.0050477 | -0.0034247 | 0.053846 | 0.028688 | 0.055583 | -64.5542 | -0.012329 | -66.7552 | 56.2747 | 56.1059 | 56.1932 | -66.8604 | -66.7749 | -0.008798 | -66.8643 | 56.226 | 56.3168 | 56.2147 | -66.992 | -0.058955 | -0.057666 | 2.2472 | 0.046292 | 0.10525 | -0.22648 | -0.13918 | -0.19053 | -0.10638 | 0.026596 | -0.062854 | 0.12768 | -0.015615 | -0.11772 | 123.0762 | 122.9074 | 122.9947 | 66.7891 | -123.1928 | 123.0275 | 123.1182 | 123.0161 | 66.7927 | -123.3244
350.2812 | 123.381 | -66.774 | 56.3049 | 0.041851 | -0.036345 | -0.0043149 | 0.050181 | -0.0083372 | 0.051124 | 0.074154 | -0.0061157 | -0.0034247 | 0.054914 | 0.02762 | 0.055583 | -64.5725 | -0.007751 | -66.7506 | 56.2747 | 56.1013 | 56.1932 | -66.865 | -66.7657 | -0.017956 | -66.8689 | 56.2169 | 56.3076 | 56.2055 | -66.992 | -0.091 | -0.030201 | 2.2015 | 0.023404 | 0.1144 | -0.20359 | -0.11171 | -0.218 | -0.088073 | 0.008288 | -0.094898 | 0.1231 | 0.002692 | -0.099414 | 123.0487 | 122.8753 | 122.9672 | 66.7662 | -123.1699 | 122.9908 | 123.0816 | 122.9795 | 66.756 | -123.2969
351.2812 | 123.3353 | -66.8289 | 56.3599 | 0.057113 | -0.036345 | -0.0043149 | 0.052318 | -0.0083372 | 0.048987 | 0.028371 | -0.0039797 | -0.0044937 | 0.055982 | 0.028688 | 0.053447 | -64.5313 | -0.003172 | -66.7597 | 56.2839 | 56.1059 | 56.1978 | -66.8833 | -66.7749 | -0.017956 | -66.8597 | 56.2306 | 56.3168 | 56.2147 | -66.992 | -0.054385 | -0.075976 | 2.2976 | 0.069178 | 0.12356 | -0.25394 | -0.16207 | -0.16307 | -0.12927 | 0.054061 | -0.03081 | 0.13226 | -0.043081 | -0.14519 | 123.1128 | 122.9348 | 123.0267 | 66.8257 | -123.2432 | 123.0595 | 123.1457 | 123.0436 | 66.811 | -123.3518
352.2812 | 123.3719 | -66.7786 | 56.2958 | 0.026589 | -0.034208 | -0.0053839 | 0.051249 | -0.0083372 | 0.048987 | 0.074154 | -0.0050477 | -0.0055617 | 0.055982 | 0.029757 | 0.052379 | -64.5588 | -0.007751 | -66.7506 | 56.2839 | 56.1059 | 56.207 | -66.865 | -66.7703 | -0.017956 | -66.8643 | 56.2123 | 56.3214 | 56.2193 | -67.0011 | -0.086423 | -0.011889 | 2.2198 | 0.027981 | 0.1144 | -0.18985 | -0.088822 | -0.22258 | -0.083495 | 0.008286 | -0.085743 | 0.13684 | 0.025584 | -0.076522 | 123.0625 | 122.8845 | 122.9855 | 66.7708 | -123.1608 | 122.9908 | 123.0999 | 122.9978 | 66.7606 | -123.2969
353.2812 | 123.2666 | -66.8015 | 56.337 | 0.041851 | -0.037413 | -0.0064519 | 0.050181 | -0.0083372 | 0.047919 | 0.074154 | -0.0050477 | -0.0055617 | 0.053846 | 0.02762 | 0.055583 | -64.5405 | -0.012329 | -66.7597 | 56.2747 | 56.1105 | 56.1978 | -66.8696 | -66.7794 | -0.017956 | -66.8643 | 56.2214 | 56.3122 | 56.2147 | -66.992 | -0.068113 | -0.062244 | 2.261 | 0.041713 | 0.10983 | -0.22648 | -0.13918 | -0.19053 | -0.11554 | 0.022017 | -0.062854 | 0.12768 | -0.024772 | -0.1223 | 123.0762 | 122.912 | 122.9992 | 66.7891 | -123.2065 | 123.0229 | 123.1137 | 123.0161 | 66.7835 | -123.329
354.2812 | 123.2391 | -66.8198 | 56.3416 | 0.057113 | -0.038482 | -0.0053839 | 0.051249 | -0.010474 | 0.048987 | 0.058893 | -0.0071847 | -0.0044937 | 0.053846 | 0.028688 | 0.053447 | -64.5268 | 0.001407 | -66.7506 | 56.2839 | 56.1059 | 56.2024 | -66.8558 | -66.7749 | -0.013377 | -66.8597 | 56.2169 | 56.3076 | 56.2101 | -67.0011 | -0.036067 | -0.057666 | 2.293 | 0.06918 | 0.10525 | -0.23563 | -0.13918 | -0.18138 | -0.12469 | 0.044906 | -0.039965 | 0.14141 | -0.033929 | -0.13146 | 123.1036 | 122.9257 | 123.0221 | 66.8212 | -123.1974 | 123.0366 | 123.1274 | 123.0299 | 66.8064 | -123.3427
355.2812 | 123.2162 | -66.8243 | 56.3461 | 0.026589 | -0.036345 | -0.0043149 | 0.051249 | -0.0094052 | 0.048987 | 0.058893 | -0.0061157 | -0.0034247 | 0.054914 | 0.028688 | 0.053447 | -64.5222 | -0.007751 | -66.7552 | 56.2839 | 56.1059 | 56.2024 | -66.8604 | -66.7749 | -0.017956 | -66.8643 | 56.2214 | 56.3168 | 56.2101 | -67.0011 | -0.036067 | -0.062243 | 2.3022 | 0.06918 | 0.10525 | -0.24021 | -0.14375 | -0.1768 | -0.12469 | 0.049484 | -0.039966 | 0.13684 | -0.029348 | -0.13603 | 123.1082 | 122.9303 | 123.0267 | 66.8166 | -123.2065 | 123.0458 | 123.1411 | 123.0344 | 66.8064 | -123.3473
356.2812 | 123.2529 | -66.806 | 56.3507 | 0.057113 | -0.038482 | -0.0043149 | 0.050181 | -0.0094052 | 0.050055 | 0.074154 | -0.0050477 | -0.0044937 | 0.054914 | 0.02762 | 0.055583 | -64.5313 | -0.007751 | -66.7552 | 56.2885 | 56.1013 | 56.1978 | -66.865 | -66.7749 | -0.008798 | -66.8643 | 56.226 | 56.3076 | 56.2284 | -66.9966 | -0.058957 | -0.062242 | 2.2747 | 0.050869 | 0.10983 | -0.24937 | -0.15291 | -0.19053 | -0.12469 | 0.031173 | -0.058277 | 0.13226 | -0.043084 | -0.1223 | 123.0945 | 122.9074 | 123.0038 | 66.7983 | -123.2157 | 123.032 | 123.1137 | 123.0344 | 66.7972 | -123.3473
357.2812 | 123.2758 | -66.7831 | 56.3416 | 0.087637 | -0.036345 | -0.0032469 | 0.050181 | -0.0094052 | 0.047919 | 0.074154 | -0.0061157 | -0.0044937 | 0.054914 | 0.02762 | 0.055583 | -64.5405 | -0.012329 | -66.7552 | 56.2839 | 56.1105 | 56.1978 | -66.8741 | -66.7657 | -0.022535 | -66.8643 | 56.2214 | 56.3122 | 56.2101 | -66.9966 | -0.091003 | -0.057666 | 2.2427 | 0.027981 | 0.11898 | -0.23105 | -0.14376 | -0.21342 | -0.12011 | 0.017443 | -0.081165 | 0.13226 | -0.02935 | -0.13146 | 123.067 | 122.8936 | 122.9809 | 66.7708 | -123.2157 | 123.0046 | 123.0953 | 122.9932 | 66.7606 | -123.3381
358.2812 | 123.3215 | -66.7923 | 56.3782 | 0.026589 | -0.037413 | -0.0043149 | 0.050181 | -0.0083372 | 0.048987 | 0.074154 | -0.0061157 | -0.0034247 | 0.055982 | 0.028688 | 0.053447 | -64.5359 | -0.016908 | -66.7552 | 56.2839 | 56.1059 | 56.2024 | -66.8696 | -66.7703 | -0.027113 | -66.8689 | 56.226 | 56.3168 | 56.233 | -66.9874 | -0.077269 | -0.094287 | 2.2564 | 0.037136 | 0.11441 | -0.27225 | -0.1758 | -0.19511 | -0.15216 | 0.022019 | -0.076588 | 0.11852 | -0.061392 | -0.14518 | 123.0762 | 122.8982 | 122.9947 | 66.7754 | -123.2477 | 123.0183 | 123.1091 | 123.0253 | 66.7652 | -123.3656
359.2812 | 123.2437 | -66.8015 | 56.3644 | 0.057113 | -0.036345 | -0.0043149 | 0.052318 | -0.0094052 | 0.048987 | 0.058893 | -0.0050477 | -0.0076977 | 0.054914 | 0.031893 | 0.053447 | -64.5268 | -0.012329 | -66.7506 | 56.2839 | 56.1059 | 56.2115 | -66.865 | -66.7703 | -0.022535 | -66.8643 | 56.2214 | 56.3259 | 56.2055 | -66.992 | -0.063534 | -0.080554 | 2.2747 | 0.05087 | 0.1144 | -0.25852 | -0.15291 | -0.19053 | -0.143 | 0.031175 | -0.062854 | 0.12768 | -0.038502 | -0.15892 | 123.0853 | 122.9074 | 123.013 | 66.7891 | -123.2294 | 123.0229 | 123.1274 | 123.007 | 66.7789 | -123.3564
360.2812 | 123.2483 | -66.8198 | 56.3644 | 0.041851 | -0.037413 | -0.0043149 | 0.050181 | -0.010474 | 0.048987 | 0.074154 | -0.0061157 | -0.0055617 | 0.054914 | 0.028688 | 0.055583 | -64.5268 | -0.012329 | -66.7506 | 56.2885 | 56.1059 | 56.207 | -66.8604 | -66.7703 | -0.027113 | -66.8643 | 56.2214 | 56.3168 | 56.2284 | -66.992 | -0.040645 | -0.075975 | 2.293 | 0.06918 | 0.10983 | -0.25852 | -0.15749 | -0.17222 | -0.143 | 0.049485 | -0.044544 | 0.12768 | -0.047659 | -0.13603 | 123.1082 | 122.9257 | 123.0267 | 66.8074 | -123.2248 | 123.0412 | 123.1365 | 123.0482 | 66.7926 | -123.3564
361.2812 | 123.23 | -66.8106 | 56.3507 | 0.057113 | -0.037413 | -0.0043149 | 0.051249 | -0.0062002 | 0.048987 | 0.058893 | -0.0061157 | -0.0066297 | 0.055982 | 0.030825 | 0.053447 | -64.5359 | -0.012329 | -66.7506 | 56.2885 | 56.1151 | 56.2115 | -66.8558 | -66.7703 | -0.022535 | -66.8689 | 56.2306 | 56.3168 | 56.2147 | -66.992 | -0.045222 | -0.062242 | 2.2747 | 0.060025 | 0.10525 | -0.23563 | -0.13918 | -0.18138 | -0.12011 | 0.04033 | -0.058277 | 0.1231 | -0.033926 | -0.13603 | 123.0991 | 122.9257 | 123.0221 | 66.7983 | -123.2065 | 123.0412 | 123.1274 | 123.0253 | 66.7881 | -123.3427
362.2812 | 123.2712 | -66.8243 | 56.337 | 0.072375 | -0.038482 | -0.0064519 | 0.050181 | -0.010474 | 0.047919 | 0.058893 | -0.0071847 | -0.0055617 | 0.053846 | 0.029757 | 0.054515 | -64.5405 | -0.012329 | -66.7506 | 56.2885 | 56.1059 | 56.2024 | -66.8513 | -66.7703 | -0.022535 | -66.8689 | 56.2214 | 56.3305 | 56.2284 | -66.9966 | -0.02691 | -0.048509 | 2.2839 | 0.073758 | 0.10067 | -0.23105 | -0.1346 | -0.17222 | -0.11554 | 0.054063 | -0.044544 | 0.12768 | -0.006458 | -0.10856 | 123.1128 | 122.9303 | 123.0267 | 66.812 | -123.1882 | 123.0458 | 123.1549 | 123.0528 | 66.8018 | -123.3335
363.2812 | 123.3078 | -66.8243 | 56.3599 | 0.057113 | -0.037413 | -0.0053839 | 0.052318 | -0.0094052 | 0.047919 | 0.089415 | -0.0061157 | -0.0044937 | 0.055982 | 0.028688 | 0.055583 | -64.5405 | -0.012329 | -66.7506 | 56.2885 | 56.1105 | 56.207 | -66.8696 | -66.7657 | -0.013377 | -66.8643 | 56.2306 | 56.3122 | 56.2284 | -67.0011 | -0.045225 | -0.071397 | 2.2839 | 0.073758 | 0.11898 | -0.24936 | -0.15291 | -0.1768 | -0.12927 | 0.058642 | -0.039966 | 0.13684 | -0.04766 | -0.13145 | 123.1128 | 122.9348 | 123.0313 | 66.812 | -123.2294 | 123.0549 | 123.1365 | 123.0528 | 66.811 | -123.361
364.2812 | 123.2712 | -66.8152 | 56.3782 | 0.072375 | -0.03955 | -0.0032469 | 0.049112 | -0.0083372 | 0.047919 | 0.043632 | -0.0050477 | -0.0066297 | 0.05705 | 0.028688 | 0.055583 | -64.5359 | -0.012329 | -66.7506 | 56.2885 | 56.1105 | 56.2024 | -66.8787 | -66.7611 | -0.022535 | -66.8597 | 56.226 | 56.3168 | 56.2193 | -66.992 | -0.063538 | -0.089708 | 2.2793 | 0.064603 | 0.12814 | -0.26767 | -0.1758 | -0.1768 | -0.15216 | 0.054065 | -0.044542 | 0.13226 | -0.061392 | -0.15892 | 123.1037 | 122.9257 | 123.0176 | 66.8029 | -123.2569 | 123.0412 | 123.132 | 123.0344 | 66.7927 | -123.3702
365.2812 | 123.2208 | -66.7969 | 56.3599 | 0.072375 | -0.038482 | -0.0043149 | 0.050181 | -0.0094052 | 0.048987 | 0.058893 | -0.0061157 | -0.0055617 | 0.054914 | 0.029757 | 0.053447 | -64.5313 | -0.012329 | -66.7506 | 56.293 | 56.1059 | 56.207 | -66.865 | -66.7565 | -0.027113 | -66.8551 | 56.2306 | 56.3214 | 56.2147 | -66.9966 | -0.068112 | -0.066819 | 2.2655 | 0.046292 | 0.1144 | -0.25394 | -0.15291 | -0.19969 | -0.12927 | 0.040333 | -0.058274 | 0.14142 | -0.038503 | -0.14519 | 123.0899 | 122.9028 | 123.0038 | 66.7845 | -123.2249 | 123.0275 | 123.1182 | 123.0115 | 66.7698 | -123.3564
366.2812 | 123.2574 | -66.8198 | 56.3461 | 0.041851 | -0.038482 | -0.0053839 | 0.049112 | -0.0094052 | 0.050055 | 0.058893 | -0.0061157 | -0.0055617 | 0.051709 | 0.029757 | 0.053447 | -64.5359 | -0.016908 | -66.746 | 56.2839 | 56.1105 | 56.2115 | -66.8696 | -66.7657 | -0.027113 | -66.8551 | 56.2306 | 56.3259 | 56.2193 | -66.992 | -0.049803 | -0.062243 | 2.2839 | 0.073758 | 0.12356 | -0.23563 | -0.1346 | -0.17222 | -0.11554 | 0.054064 | -0.035386 | 0.13684 | -0.020191 | -0.12688 | 123.1036 | 122.9303 | 123.0313 | 66.8029 | -123.2157 | 123.0504 | 123.1457 | 123.039 | 66.7926 | -123.3381
367.2812 | 123.4177 | -66.7236 | 56.3324 | 0.057113 | -0.03955 | -0.0032469 | 0.050181 | -0.0083372 | 0.051124 | 0.058893 | -0.0050477 | -0.0044937 | 0.054914 | 0.030825 | 0.054515 | -64.5954 | -0.021486 | -66.746 | 56.2839 | 56.1105 | 56.207 | -66.865 | -66.7657 | -0.031692 | -66.8689 | 56.2306 | 56.3122 | 56.2238 | -66.9828 | -0.14135 | -0.04851 | 2.1282 | -0.022372 | 0.11898 | -0.2219 | -0.12544 | -0.25919 | -0.1018 | -0.042066 | -0.14525 | 0.11394 | -0.020194 | -0.10856 | 123.0075 | 122.8341 | 122.9306 | 66.7021 | -123.1974 | 122.9542 | 123.0358 | 122.9475 | 66.6919 | -123.3152
368.2812 | 123.3215 | -66.7877 | 56.3232 | 0.041851 | -0.038482 | -0.0043149 | 0.050181 | -0.0094052 | 0.050055 | 0.058893 | -0.0061157 | -0.0066297 | 0.054914 | 0.030825 | 0.055583 | -64.5451 | -0.016908 | -66.7506 | 56.2885 | 56.1105 | 56.2115 | -66.8696 | -66.7611 | -0.022535 | -66.8643 | 56.2306 | 56.3214 | 56.2147 | -66.9874 | -0.081846 | -0.034776 | 2.2427 | 0.037137 | 0.11898 | -0.21274 | -0.11171 | -0.19969 | -0.092647 | 0.026599 | -0.076587 | 0.1231 | -0.001882 | -0.10857 | 123.0762 | 122.8982 | 122.9993 | 66.7708 | -123.1928 | 123.0183 | 123.1091 | 123.0024 | 66.7652 | -123.3106
369.2812 | 123.3673 | -66.7694 | 56.2912 | 0.041851 | -0.03955 | -0.0064519 | 0.049112 | -0.0094052 | 0.050055 | 0.074154 | -0.0071847 | -0.0044937 | 0.052777 | 0.030825 | 0.053447 | -64.5725 | -0.021486 | -66.746 | 56.2976 | 56.1105 | 56.2024 | -66.8513 | -66.7657 | -0.022535 | -66.8597 | 56.2352 | 56.3168 | 56.2147 | -66.992 | -0.081842 | 0.006424 | 2.1969 | 0.023404 | 0.10525 | -0.1807 | -0.088824 | -0.22258 | -0.056026 | 0.00371 | -0.090319 | 0.13226 | 0.025583 | -0.076524 | 123.067 | 122.8799 | 122.9718 | 66.7479 | -123.1424 | 123.0046 | 123.0862 | 122.9841 | 66.7469 | -123.2832
370.2812 | 123.3582 | -66.7831 | 56.3232 | 0.057113 | -0.03955 | -0.0032469 | 0.050181 | -0.010474 | 0.047919 | 0.074154 | -0.0050477 | -0.0055617 | 0.054914 | 0.028688 | 0.053447 | -64.5817 | -0.021486 | -66.746 | 56.2839 | 56.1105 | 56.2024 | -66.8558 | -66.7703 | -0.031692 | -66.8597 | 56.226 | 56.3168 | 56.2193 | -66.992 | -0.072688 | -0.039355 | 2.2014 | 0.037137 | 0.10983 | -0.21274 | -0.12087 | -0.20884 | -0.097226 | 0.012864 | -0.076586 | 0.13226 | -0.00646 | -0.10399 | 123.067 | 122.8936 | 122.9855 | 66.7617 | -123.1791 | 123.0092 | 123.0999 | 123.0024 | 66.7514 | -123.3152
371.2812 | 123.2803 | -66.8198 | 56.369 | 0.057113 | -0.040619 | -0.0043149 | 0.051249 | -0.0083372 | 0.048987 | 0.058893 | -0.0050477 | -0.0023567 | 0.054914 | 0.029757 | 0.053447 | -64.5359 | -0.021486 | -66.7506 | 56.2839 | 56.1105 | 56.2024 | -66.8604 | -66.7703 | -0.027113 | -66.8643 | 56.2306 | 56.3122 | 56.2238 | -66.992 | -0.040645 | -0.085132 | 2.2839 | 0.06918 | 0.10983 | -0.25852 | -0.16664 | -0.17222 | -0.13842 | 0.049485 | -0.044544 | 0.12768 | -0.056816 | -0.14519 | 123.1036 | 122.9303 | 123.0221 | 66.7983 | -123.2294 | 123.0504 | 123.132 | 123.0436 | 66.7926 | -123.361
372.2812 | 123.3902 | -66.7557 | 56.3507 | 0.041851 | -0.03955 | -0.0021789 | 0.050181 | -0.010474 | 0.047919 | 0.074154 | -0.0050477 | -0.0055617 | 0.052777 | 0.029757 | 0.053447 | -64.6092 | -0.026065 | -66.7552 | 56.2839 | 56.1059 | 56.207 | -66.8604 | -66.7749 | -0.027113 | -66.8597 | 56.2306 | 56.3168 | 56.2193 | -66.9966 | -0.10473 | -0.066821 | 2.1465 | 0.000515 | 0.10525 | -0.24479 | -0.14375 | -0.24089 | -0.12011 | -0.019181 | -0.10405 | 0.13684 | -0.033926 | -0.13145 | 123.0396 | 122.8616 | 122.9626 | 66.7296 | -123.2111 | 122.9863 | 123.0725 | 122.9749 | 66.7286 | -123.3473
373.2812 | 123.2758 | -66.8015 | 56.3782 | 0.072375 | -0.041687 | -0.0032469 | 0.049112 | -0.0094052 | 0.050055 | 0.089415 | -0.0050477 | -0.0055617 | 0.054914 | 0.031893 | 0.053447 | -64.5268 | -0.021486 | -66.746 | 56.2793 | 56.1151 | 56.2024 | -66.8833 | -66.7657 | -0.027113 | -66.8597 | 56.226 | 56.3214 | 56.2193 | -66.992 | -0.08185 | -0.098865 | 2.2747 | 0.055448 | 0.1373 | -0.26309 | -0.1758 | -0.19053 | -0.15216 | 0.035754 | -0.058275 | 0.13226 | -0.056814 | -0.15892 | 123.0808 | 122.9165 | 123.0038 | 66.78 | -123.2615 | 123.0275 | 123.1228 | 123.0207 | 66.7743 | -123.3702
374.2812 | 123.2346 | -66.8198 | 56.3828 | 0.057113 | -0.040619 | -0.0021789 | 0.049112 | -0.0094052 | 0.048987 | 0.058893 | -0.0071847 | -0.0044937 | 0.052777 | 0.029757 | 0.053447 | -64.5405 | -0.021486 | -66.7506 | 56.2885 | 56.1059 | 56.2024 | -66.8696 | -66.7703 | -0.022535 | -66.8506 | 56.2214 | 56.3259 | 56.2238 | -66.992 | -0.049803 | -0.094285 | 2.2793 | 0.06918 | 0.11898 | -0.27683 | -0.18038 | -0.17222 | -0.16131 | 0.049485 | -0.030807 | 0.14142 | -0.056812 | -0.15892 | 123.1082 | 122.9257 | 123.0221 | 66.7983 | -123.2523 | 123.0412 | 123.1457 | 123.0436 | 66.7972 | -123.3747
375.2812 | 123.1842 | -66.7877 | 56.369 | 0.041851 | -0.03955 | -0.0032469 | 0.051249 | -0.010474 | 0.048987 | 0.058893 | -0.0061157 | -0.0055617 | 0.055982 | 0.031893 | 0.053447 | -64.5268 | -0.021486 | -66.7552 | 56.2885 | 56.1059 | 56.2024 | -66.8696 | -66.7749 | -0.017956 | -66.8597 | 56.226 | 56.3214 | 56.2147 | -66.9966 | -0.081846 | -0.080553 | 2.261 | 0.032559 | 0.11441 | -0.2631 | -0.16664 | -0.20885 | -0.143 | 0.012863 | -0.072008 | 0.13684 | -0.047659 | -0.15434 | 123.0762 | 122.8936 | 122.9901 | 66.7662 | -123.2386 | 123.0137 | 123.1091 | 123.0024 | 66.7698 | -123.3656
376.2812 | 123.2025 | -66.8289 | 56.3416 | 0.072375 | -0.040619 | -0.0043149 | 0.049112 | -0.0083372 | 0.047919 | 0.058893 | -0.0071847 | -0.0055617 | 0.053846 | 0.031893 | 0.053447 | -64.5359 | -0.021486 | -66.7506 | 56.2793 | 56.1059 | 56.2024 | -66.8696 | -66.7703 | -0.022535 | -66.8597 | 56.2214 | 56.3168 | 56.2193 | -66.9966 | -0.040648 | -0.062244 | 2.293 | 0.078335 | 0.11898 | -0.23563 | -0.13918 | -0.16765 | -0.12011 | 0.05864 | -0.03081 | 0.13684 | -0.024771 | -0.1223 | 123.1082 | 122.9348 | 123.0313 | 66.8074 | -123.2111 | 123.0504 | 123.1457 | 123.0482 | 66.8064 | -123.3381
377.2812 | 123.2849 | -66.8015 | 56.3599 | 0.072375 | -0.03955 | -0.0032469 | 0.050181 | -0.010474 | 0.050055 | 0.089415 | -0.0061157 | -0.0044937 | 0.053846 | 0.030825 | 0.05131 | -64.5268 | -0.021486 | -66.7552 | 56.2747 | 56.1105 | 56.2024 | -66.865 | -66.7703 | -0.022535 | -66.8643 | 56.2306 | 56.3122 | 56.2055 | -66.9966 | -0.063534 | -0.085132 | 2.2747 | 0.046292 | 0.10983 | -0.24936 | -0.15749 | -0.19511 | -0.12927 | 0.031175 | -0.062854 | 0.13226 | -0.04766 | -0.15434 | 123.0762 | 122.912 | 123.0038 | 66.78 | -123.2249 | 123.032 | 123.1137 | 123.007 | 66.7789 | -123.3564
378.2812 | 123.2849 | -66.8106 | 56.3461 | 0.041851 | -0.040619 | -0.0032469 | 0.050181 | -0.0094052 | 0.048987 | 0.058893 | -0.0039797 | -0.0044937 | 0.055982 | 0.029757 | 0.053447 | -64.5496 | -0.016908 | -66.7506 | 56.2839 | 56.1105 | 56.1932 | -66.8696 | -66.7794 | -0.027113 | -66.8597 | 56.2214 | 56.3122 | 56.2147 | -66.992 | -0.058958 | -0.062243 | 2.261 | 0.060025 | 0.11898 | -0.23563 | -0.15291 | -0.18138 | -0.12469 | 0.031172 | -0.04912 | 0.13226 | -0.033927 | -0.13146 | 123.0945 | 122.9211 | 123.0038 | 66.7937 | -123.2157 | 123.032 | 123.1228 | 123.0253 | 66.7835 | -123.3381
379.2812 | 123.2849 | -66.8289 | 56.3507 | 0.057113 | -0.038482 | -0.0053839 | 0.049112 | -0.0094052 | 0.048987 | 0.089415 | -0.0050477 | -0.0044937 | 0.052777 | 0.029757 | 0.053447 | -64.5496 | -0.021486 | -66.746 | 56.2839 | 56.1059 | 56.2024 | -66.8696 | -66.7703 | -0.017956 | -66.8643 | 56.2306 | 56.3076 | 56.2101 | -66.9966 | -0.040648 | -0.066821 | 2.2793 | 0.082913 | 0.12356 | -0.24479 | -0.14833 | -0.16765 | -0.12011 | 0.05864 | -0.035389 | 0.13226 | -0.043084 | -0.14061 | 123.1128 | 122.9348 | 123.0313 | 66.8074 | -123.2203 | 123.0595 | 123.1365 | 123.039 | 66.811 | -123.3473
380.2812 | 123.2346 | -66.8198 | 56.3324 | 0.057113 | -0.040619 | -0.0064519 | 0.049112 | -0.010474 | 0.047919 | 0.058893 | -0.0061157 | -0.0044937 | 0.052777 | 0.030825 | 0.054515 | -64.5359 | -0.016908 | -66.7506 | 56.2793 | 56.1105 | 56.207 | -66.8696 | -66.7703 | -0.017956 | -66.8597 | 56.2214 | 56.3122 | 56.2147 | -66.992 | -0.049803 | -0.053088 | 2.2839 | 0.06918 | 0.11898 | -0.2219 | -0.12544 | -0.17222 | -0.11096 | 0.049485 | -0.039965 | 0.13226 | -0.020194 | -0.11772 | 123.0991 | 122.9303 | 123.0267 | 66.8029 | -123.202 | 123.0412 | 123.132 | 123.0344 | 66.8018 | -123.3244
381.2812 | 123.2803 | -66.8381 | 56.3416 | 0.057113 | -0.040619 | -0.0064519 | 0.049112 | -0.0094052 | 0.050055 | 0.089415 | -0.0050477 | -0.0055617 | 0.054914 | 0.031893 | 0.052379 | -64.5451 | -0.026065 | -66.7506 | 56.2793 | 56.1059 | 56.207 | -66.8741 | -66.7749 | -0.013377 | -66.8643 | 56.226 | 56.3214 | 56.2193 | -67.0011 | -0.036071 | -0.062244 | 2.293 | 0.087491 | 0.12356 | -0.23563 | -0.1346 | -0.16307 | -0.11554 | 0.063217 | -0.026233 | 0.13684 | -0.020193 | -0.1223 | 123.1174 | 122.944 | 123.045 | 66.812 | -123.2157 | 123.0641 | 123.1594 | 123.0573 | 66.8247 | -123.3427
382.2812 | 123.3215 | -66.774 | 56.3049 | 0.057113 | -0.040619 | -0.0032469 | 0.049112 | -0.0083372 | 0.050055 | 0.043632 | -0.0050477 | -0.0066297 | 0.054914 | 0.030825 | 0.055583 | -64.6183 | -0.016908 | -66.7552 | 56.2793 | 56.1013 | 56.1978 | -66.8787 | -66.7657 | -0.017956 | -66.8689 | 56.2169 | 56.3122 | 56.2238 | -66.9966 | -0.10474 | -0.025623 | 2.1557 | 0.018826 | 0.12356 | -0.20359 | -0.10713 | -0.22258 | -0.088073 | 0.008288 | -0.094898 | 0.12768 | 0.007271 | -0.0811 | 123.0533 | 122.8753 | 122.9718 | 66.7571 | -123.1837 | 122.9908 | 123.0862 | 122.9978 | 66.756 | -123.3015
383.2812 | 123.2986 | -66.806 | 56.3141 | 0.057113 | -0.041687 | -0.0043149 | 0.050181 | -0.010474 | 0.048987 | 0.043632 | -0.0039797 | -0.0066297 | 0.053846 | 0.031893 | 0.053447 | -64.5313 | -0.012329 | -66.7506 | 56.2747 | 56.1105 | 56.207 | -66.865 | -66.7657 | -0.022535 | -66.8597 | 56.2214 | 56.3122 | 56.2193 | -67.0011 | -0.058957 | -0.039356 | 2.2747 | 0.055447 | 0.1144 | -0.20359 | -0.10713 | -0.19511 | -0.092649 | 0.040331 | -0.053698 | 0.14141 | -0.001884 | -0.094833 | 123.0808 | 122.9165 | 123.013 | 66.7937 | -123.1791 | 123.0275 | 123.1182 | 123.0253 | 66.7835 | -123.3152
384.2812 | 123.2941 | -66.7969 | 56.3278 | 0.072375 | -0.041687 | -0.0053839 | 0.050181 | -0.0094052 | 0.047919 | 0.043632 | -0.0050477 | -0.0076977 | 0.052777 | 0.029757 | 0.052379 | -64.5496 | -0.012329 | -66.7552 | 56.2793 | 56.1059 | 56.2024 | -66.8741 | -66.7611 | -0.022535 | -66.8643 | 56.2214 | 56.3122 | 56.2147 | -66.992 | -0.07727 | -0.048511 | 2.2472 | 0.041714 | 0.11898 | -0.2219 | -0.12544 | -0.19511 | -0.10638 | 0.035754 | -0.067432 | 0.12768 | -0.015617 | -0.11315 | 123.0762 | 122.9028 | 122.9993 | 66.7845 | -123.202 | 123.0183 | 123.1091 | 123.0115 | 66.7743 | -123.3198
385.2812 | 123.2803 | -66.8152 | 56.3324 | 0.041851 | -0.040619 | -0.0043149 | 0.051249 | -0.0094052 | 0.050055 | 0.058893 | -0.0061157 | -0.0044937 | 0.053846 | 0.030825 | 0.053447 | -64.5451 | -0.012329 | -66.7506 | 56.2747 | 56.1059 | 56.1932 | -66.865 | -66.7749 | -0.022535 | -66.8597 | 56.2169 | 56.3122 | 56.2101 | -66.9966 | -0.049801 | -0.057666 | 2.2701 | 0.064603 | 0.1144 | -0.22648 | -0.13918 | -0.18138 | -0.11554 | 0.040329 | -0.044542 | 0.13684 | -0.020194 | -0.1223 | 123.0899 | 122.9211 | 123.0084 | 66.8029 | -123.1974 | 123.032 | 123.1274 | 123.0253 | 66.7927 | -123.329
386.2812 | 123.2254 | -66.8198 | 56.3644 | 0.072375 | -0.041687 | -0.0043149 | 0.051249 | -0.0083372 | 0.048987 | 0.058893 | -0.0061157 | -0.0055617 | 0.053846 | 0.030825 | 0.053447 | -64.5268 | -0.016908 | -66.7552 | 56.2793 | 56.1059 | 56.2024 | -66.8741 | -66.7749 | -0.036271 | -66.8597 | 56.2169 | 56.3076 | 56.2147 | -66.9966 | -0.054382 | -0.085132 | 2.293 | 0.064602 | 0.11898 | -0.25852 | -0.16207 | -0.1768 | -0.14758 | 0.044906 | -0.039965 | 0.13684 | -0.056817 | -0.14977 | 123.0991 | 122.9257 | 123.0221 | 66.8029 | -123.2386 | 123.0366 | 123.1274 | 123.0344 | 66.7835 | -123.361
387.2812 | 123.4131 | -66.7923 | 56.3232 | 0.087637 | -0.043824 | -0.0032469 | 0.050181 | -0.010474 | 0.051124 | 0.058893 | -0.0071847 | -0.0044937 | 0.051709 | 0.029757 | 0.054515 | -64.6092 | -0.016908 | -66.746 | 56.2747 | 56.0968 | 56.2024 | -66.865 | -66.7749 | -0.050007 | -66.8735 | 56.226 | 56.3076 | 56.2055 | -67.0011 | -0.07269 | -0.048511 | 2.1831 | 0.046292 | 0.11898 | -0.22648 | -0.12087 | -0.20885 | -0.097226 | 0.01744 | -0.081167 | 0.12768 | -0.015618 | -0.11772 | 123.067 | 122.8891 | 122.9947 | 66.7754 | -123.1882 | 123.0183 | 123.0999 | 122.9978 | 66.7423 | -123.3244
388.2812 | 123.3444 | -66.7969 | 56.3049 | 0.041851 | -0.041687 | -0.0032469 | 0.051249 | -0.011542 | 0.048987 | 0.043632 | -0.0061157 | -0.0044937 | 0.052777 | 0.031893 | 0.05131 | -64.5588 | -0.021486 | -66.7506 | 56.2793 | 56.1013 | 56.1932 | -66.8558 | -66.7749 | -0.050007 | -66.8689 | 56.2214 | 56.3076 | 56.2009 | -67.0057 | -0.058955 | -0.025623 | 2.2381 | 0.046292 | 0.10525 | -0.20359 | -0.11171 | -0.20885 | -0.083494 | 0.022018 | -0.07201 | 0.13684 | 0.002692 | -0.10399 | 123.0762 | 122.8982 | 122.9901 | 66.7754 | -123.1608 | 123.0183 | 123.1045 | 122.9978 | 66.7469 | -123.3107
389.2812 | 123.23 | -66.7969 | 56.3416 | 0.041851 | -0.043824 | -0.0053839 | 0.050181 | -0.010474 | 0.048987 | 0.058893 | -0.0061157 | -0.0055617 | 0.053846 | 0.032962 | 0.052379 | -64.5313 | -0.007751 | -66.7552 | 56.2839 | 56.1059 | 56.1932 | -66.8787 | -66.7703 | -0.059164 | -66.8643 | 56.2169 | 56.3122 | 56.2055 | -67.0011 | -0.081849 | -0.057666 | 2.2655 | 0.041714 | 0.12356 | -0.23563 | -0.14833 | -0.20427 | -0.12469 | 0.026597 | -0.067432 | 0.13684 | -0.02935 | -0.13603 | 123.0808 | 122.9028 | 122.9901 | 66.7891 | -123.2203 | 123.0137 | 123.1091 | 123.0024 | 66.7377 | -123.3427
390.2812 | 123.2208 | -66.8015 | 56.3416 | 0.041851 | -0.041687 | -0.0043149 | 0.050181 | -0.011542 | 0.048987 | 0.028371 | -0.0071847 | -0.0055617 | 0.052777 | 0.031893 | 0.052379 | -64.5176 | -0.021486 | -66.746 | 56.2793 | 56.1013 | 56.1978 | -66.8833 | -66.7657 | -0.086637 | -66.8643 | 56.2169 | 56.3076 | 56.2009 | -67.0057 | -0.08185 | -0.062244 | 2.2839 | 0.055448 | 0.1373 | -0.24021 | -0.14376 | -0.20427 | -0.12469 | 0.035754 | -0.062854 | 0.14142 | -0.033929 | -0.14061 | 123.0808 | 122.9028 | 122.9992 | 66.78 | -123.2249 | 123.0183 | 123.1091 | 123.0024 | 66.7148 | -123.3473
391.2812 | 123.2895 | -66.8289 | 56.3507 | 0.072375 | -0.041687 | -0.0043149 | 0.050181 | -0.010474 | 0.04685 | 0.058893 | -0.0061157 | -0.0066297 | 0.052777 | 0.031893 | 0.053447 | -64.5313 | -0.026065 | -66.7506 | 56.2702 | 56.1105 | 56.207 | -66.8787 | -66.7611 | -0.10495 | -66.8643 | 56.2214 | 56.3168 | 56.2193 | -66.9966 | -0.049806 | -0.080556 | 2.2976 | 0.078335 | 0.12814 | -0.24021 | -0.14375 | -0.16765 | -0.12927 | 0.067797 | -0.035389 | 0.13226 | -0.033926 | -0.13145 | 123.0991 | 122.9394 | 123.0359 | 66.8029 | -123.2294 | 123.0504 | 123.1457 | 123.0482 | 66.724 | -123.3473
392.2812 | 123.3353 | -66.7969 | 56.282 | 0.041851 | -0.042755 | -0.0053839 | 0.049112 | -0.0094052 | 0.047919 | 0.089415 | -0.0050477 | -0.0055617 | 0.052777 | 0.032962 | 0.052379 | -64.5496 | -0.039801 | -66.746 | 56.2839 | 56.1059 | 56.2024 | -66.8604 | -66.7611 | -0.137 | -66.8551 | 56.2214 | 56.3168 | 56.2193 | -66.992 | -0.063533 | 0.001844 | 2.2472 | 0.05087 | 0.1144 | -0.17612 | -0.079668 | -0.19511 | -0.060605 | 0.035754 | -0.058274 | 0.13684 | 0.034739 | -0.062789 | 123.0808 | 122.9028 | 122.9993 | 66.7571 | -123.1425 | 123.0183 | 123.1137 | 123.0161 | 66.6599 | -123.274
393.2812 | 123.262 | -66.8015 | 56.369 | 0.057113 | -0.041687 | -0.0043149 | 0.050181 | -0.010474 | 0.047919 | 0.058893 | -0.0071847 | -0.0066297 | 0.051709 | 0.031893 | 0.054515 | -64.5084 | -0.048958 | -66.7414 | 56.293 | 56.1105 | 56.2115 | -66.8741 | -66.7565 | -0.18279 | -66.8551 | 56.2214 | 56.3259 | 56.2238 | -66.9966 | -0.072692 | -0.075975 | 2.293 | 0.060026 | 0.13272 | -0.25852 | -0.15749 | -0.19511 | -0.14758 | 0.044911 | -0.053696 | 0.14142 | -0.04308 | -0.14519 | 123.0945 | 122.912 | 123.013 | 66.7525 | -123.2432 | 123.0229 | 123.1274 | 123.0253 | 66.6187 | -123.3656
394.2812 | 123.262 | -66.8152 | 56.3599 | 0.041851 | -0.043824 | -0.0064519 | 0.048044 | -0.0094052 | 0.050055 | 0.074154 | -0.0071847 | -0.0066297 | 0.054914 | 0.031893 | 0.054515 | -64.4993 | -0.053537 | -66.7368 | 56.293 | 56.1151 | 56.2115 | -66.8696 | -66.7428 | -0.22858 | -66.846 | 56.226 | 56.3259 | 56.2193 | -66.992 | -0.05438 | -0.066819 | 2.3159 | 0.078338 | 0.13272 | -0.24478 | -0.14833 | -0.1768 | -0.13385 | 0.07238 | -0.030806 | 0.14599 | -0.033924 | -0.14061 | 123.1082 | 122.9303 | 123.0267 | 66.7616 | -123.2294 | 123.0412 | 123.1411 | 123.0344 | 66.5866 | -123.3518
395.2812 | 123.23 | -66.7969 | 56.3873 | 0.041851 | -0.041687 | -0.0053839 | 0.051249 | -0.0094052 | 0.048987 | 0.058893 | -0.0061157 | -0.0055617 | 0.054914 | 0.035099 | 0.052379 | -64.4947 | -0.07643 | -66.7277 | 56.293 | 56.1242 | 56.2207 | -66.8513 | -66.7474 | -0.31099 | -66.846 | 56.2352 | 56.3259 | 56.2238 | -66.992 | -0.054376 | -0.094285 | 2.3022 | 0.069183 | 0.12356 | -0.26309 | -0.16664 | -0.19511 | -0.15216 | 0.04949 | -0.049117 | 0.14599 | -0.06139 | -0.1635 | 123.0899 | 122.9211 | 123.0176 | 66.7204 | -123.2386 | 123.032 | 123.1228 | 123.0207 | 66.4859 | -123.3793
396.2812 | 123.2483 | -66.7923 | 56.3736 | 0.057113 | -0.043824 | -0.0064519 | 0.050181 | -0.010474 | 0.050055 | 0.058893 | -0.0061157 | -0.0076977 | 0.051709 | 0.030825 | 0.053447 | -64.4993 | -0.11764 | -66.7185 | 56.3022 | 56.1242 | 56.2253 | -66.8329 | -66.7336 | -0.37967 | -66.8323 | 56.2398 | 56.3259 | 56.233 | -66.992 | -0.040638 | -0.071395 | 2.293 | 0.073762 | 0.1144 | -0.24936 | -0.14833 | -0.19969 | -0.13385 | 0.058648 | -0.039959 | 0.15973 | -0.047657 | -0.14061 | 123.0945 | 122.9165 | 123.0176 | 66.6747 | -123.2065 | 123.032 | 123.1182 | 123.0253 | 66.4126 | -123.3656
397.2812 | 123.2483 | -66.7969 | 56.3599 | 0.041851 | -0.043824 | -0.0053839 | 0.050181 | -0.011542 | 0.047919 | 0.089415 | -0.0071847 | -0.0055617 | 0.052777 | 0.032962 | 0.053447 | -64.4947 | -0.15884 | -66.7185 | 56.3114 | 56.1334 | 56.2253 | -66.8558 | -66.7291 | -0.46667 | -66.8231 | 56.2535 | 56.3397 | 56.233 | -66.9691 | -0.058955 | -0.048505 | 2.3022 | 0.07834 | 0.13729 | -0.22647 | -0.13459 | -0.17222 | -0.10638 | 0.067805 | -0.026223 | 0.14599 | -0.020188 | -0.12687 | 123.1082 | 122.9303 | 123.0221 | 66.638 | -123.2157 | 123.0504 | 123.1365 | 123.0299 | 66.3302 | -123.329
398.2812 | 123.2529 | -66.7969 | 56.3919 | 0.057113 | -0.043824 | -0.0053839 | 0.050181 | -0.010474 | 0.050055 | 0.058893 | -0.0071847 | -0.0076977 | 0.053846 | 0.032962 | 0.053447 | -64.4718 | -0.21837 | -66.714 | 56.3114 | 56.1334 | 56.2344 | -66.8375 | -66.7153 | -0.57198 | -66.8185 | 56.2581 | 56.3397 | 56.2467 | -66.9691 | -0.040639 | -0.080549 | 2.3251 | 0.082918 | 0.12356 | -0.25851 | -0.15748 | -0.17222 | -0.13384 | 0.081541 | -0.021644 | 0.15057 | -0.052232 | -0.14518 | 123.1082 | 122.9303 | 123.0313 | 66.5785 | -123.2294 | 123.0549 | 123.1365 | 123.0436 | 66.2249 | -123.361
399.2812 | 123.2346 | -66.7511 | 56.3965 | 0.041851 | -0.044892 | -0.0064519 | 0.050181 | -0.010474 | 0.047919 | 0.089415 | -0.0061157 | -0.0066297 | 0.054914 | 0.03403 | 0.053447 | -64.4718 | -0.28704 | -66.7002 | 56.3205 | 56.1426 | 56.239 | -66.8146 | -66.7016 | -0.70018 | -66.8094 | 56.2581 | 56.3488 | 56.2513 | -66.9645 | -0.06352 | -0.07597 | 2.2793 | 0.050877 | 0.1144 | -0.25393 | -0.15748 | -0.21341 | -0.13842 | 0.049501 | -0.058263 | 0.15515 | -0.047652 | -0.14518 | 123.0716 | 122.8937 | 122.9901 | 66.4641 | -123.2111 | 123.0092 | 123.0999 | 123.0024 | 66.0509 | -123.361
400.2812 | 123.3353 | -66.7374 | 56.4102 | 0.057113 | -0.043824 | -0.0053839 | 0.049112 | -0.010474 | 0.047919 | 0.058893 | -0.0061157 | -0.0066297 | 0.050641 | 0.032962 | 0.054515 | -64.4581 | -0.37404 | -66.7002 | 56.3297 | 56.1563 | 56.2482 | -66.8238 | -66.7016 | -0.86502 | -66.8048 | 56.2672 | 56.3534 | 56.2605 | -66.9554 | -0.086411 | -0.080546 | 2.2793 | 0.037144 | 0.12356 | -0.25393 | -0.16206 | -0.21799 | -0.143 | 0.035768 | -0.067417 | 0.15057 | -0.056807 | -0.14976 | 123.067 | 122.8937 | 122.9855 | 66.3633 | -123.234 | 123.0046 | 123.0908 | 122.9978 | 65.8723 | -123.3656
401.2812 | 123.3032 | -66.7145 | 56.4239 | 0.057113 | -0.043824 | -0.0053839 | 0.051249 | -0.011542 | 0.04685 | 0.058893 | -0.0061157 | -0.0066297 | 0.053846 | 0.032962 | 0.053447 | -64.4443 | -0.47477 | -66.6819 | 56.3388 | 56.1609 | 56.2573 | -66.8284 | -66.6833 | -1.039 | -66.791 | 56.2718 | 56.3671 | 56.2696 | -66.9462 | -0.11388 | -0.085122 | 2.2701 | 0.032569 | 0.14645 | -0.26308 | -0.16663 | -0.23172 | -0.15215 | 0.031195 | -0.076569 | 0.15515 | -0.056804 | -0.15433 | 123.0533 | 122.8753 | 122.9718 | 66.2397 | -123.2523 | 122.9863 | 123.0816 | 122.9841 | 65.6755 | -123.3701
402.2812 | 123.2849 | -66.7236 | 56.3873 | 0.072375 | -0.043824 | -0.0043149 | 0.050181 | -0.011542 | 0.04685 | 0.074154 | -0.0071847 | -0.0055617 | 0.053846 | 0.032962 | 0.053447 | -64.4398 | -0.59381 | -66.6819 | 56.3388 | 56.1609 | 56.2573 | -66.8146 | -66.6833 | -1.2222 | -66.7819 | 56.281 | 56.3763 | 56.2742 | -66.9554 | -0.090986 | -0.048501 | 2.2839 | 0.041724 | 0.13271 | -0.22646 | -0.13001 | -0.23172 | -0.10637 | 0.04035 | -0.058257 | 0.17346 | -0.011026 | -0.11313 | 123.0625 | 122.8845 | 122.981 | 66.1298 | -123.2019 | 123.0046 | 123.0999 | 122.9978 | 65.5015 | -123.3427
403.2812 | 123.3078 | -66.7419 | 56.4148 | 0.041851 | -0.043824 | -0.0064519 | 0.048044 | -0.011542 | 0.047919 | 0.058893 | -0.0061157 | -0.0076977 | 0.053846 | 0.032962 | 0.053447 | -64.3802 | -0.74033 | -66.6636 | 56.348 | 56.1746 | 56.2665 | -66.8009 | -66.6695 | -1.419 | -66.7773 | 56.2855 | 56.3809 | 56.2742 | -66.937 | -0.058939 | -0.06681 | 2.3617 | 0.078347 | 0.13729 | -0.24019 | -0.14832 | -0.1951 | -0.12926 | 0.072396 | -0.035368 | 0.15973 | -0.033913 | -0.1406 | 123.0899 | 122.9165 | 123.0084 | 66.0016 | -123.2157 | 123.0275 | 123.1228 | 123.0161 | 65.3229 | -123.3518
404.2812 | 123.2483 | -66.7145 | 56.4423 | 0.057113 | -0.04596 | -0.0064519 | 0.049112 | -0.011542 | 0.047919 | 0.074154 | -0.0082527 | -0.0055617 | 0.052777 | 0.035099 | 0.053447 | -64.3711 | -0.91889 | -66.659 | 56.3571 | 56.1838 | 56.2756 | -66.8055 | -66.6467 | -1.6388 | -66.7636 | 56.2993 | 56.39 | 56.2879 | -66.9233 | -0.090983 | -0.085119 | 2.3434 | 0.055461 | 0.14644 | -0.2585 | -0.16663 | -0.20883 | -0.14299 | 0.067825 | -0.049097 | 0.15973 | -0.052222 | -0.15433 | 123.0716 | 122.8982 | 122.9901 | 65.7956 | -123.2477 | 123.0138 | 123.1045 | 123.0024 | 65.0757 | -123.3656
405.2812 | 123.2529 | -66.7282 | 56.4331 | 0.087637 | -0.04596 | -0.0064519 | 0.048044 | -0.011542 | 0.047919 | 0.058893 | -0.0071847 | -0.0034247 | 0.052777 | 0.032962 | 0.052379 | -64.3619 | -1.0883 | -66.6499 | 56.3617 | 56.1929 | 56.2802 | -66.7871 | -66.6467 | -1.8449 | -66.7453 | 56.313 | 56.4038 | 56.2971 | -66.9187 | -0.058936 | -0.071385 | 2.3663 | 0.078349 | 0.13729 | -0.24018 | -0.15289 | -0.19051 | -0.1201 | 0.081557 | -0.01705 | 0.17346 | -0.02933 | -0.13602 | 123.0899 | 122.9211 | 123.0084 | 65.6399 | -123.2203 | 123.0412 | 123.132 | 123.0253 | 64.8833 | -123.3518
406.2812 | 123.2895 | -66.7282 | 56.4423 | 0.072375 | -0.043824 | -0.0043149 | 0.048044 | -0.0094052 | 0.047919 | 0.074154 | -0.0061157 | -0.0044937 | 0.050641 | 0.032962 | 0.05131 | -64.3345 | -1.2989 | -66.6407 | 56.3663 | 56.2021 | 56.2939 | -66.7963 | -66.6283 | -2.0646 | -66.7453 | 56.3222 | 56.4038 | 56.3108 | -66.9141 | -0.068094 | -0.075963 | 2.3938 | 0.087506 | 0.1556 | -0.24018 | -0.14831 | -0.18594 | -0.1201 | 0.099872 | -0.01705 | 0.16889 | -0.038486 | -0.13144 | 123.0945 | 122.9303 | 123.0222 | 65.4293 | -123.2386 | 123.0504 | 123.132 | 123.039 | 64.6636 | -123.3564
407.2812 | 123.317 | -66.6916 | 56.456 | 0.057113 | -0.043824 | -0.0043149 | 0.050181 | -0.0094052 | 0.04685 | 0.058893 | -0.0071847 | -0.0055617 | 0.054914 | 0.03403 | 0.050242 | -64.3253 | -1.505 | -66.6224 | 56.3846 | 56.2021 | 56.3077 | -66.7597 | -66.6238 | -2.2982 | -66.7315 | 56.3313 | 56.4175 | 56.3062 | -66.9004 | -0.068083 | -0.071382 | 2.3663 | 0.069198 | 0.13728 | -0.25391 | -0.14831 | -0.20882 | -0.12467 | 0.06783 | -0.039935 | 0.16889 | -0.038483 | -0.14975 | 123.0762 | 122.8937 | 122.9993 | 65.1866 | -123.2157 | 123.0229 | 123.1091 | 122.9978 | 64.3934 | -123.3564
408.2812 | 123.3078 | -66.6687 | 56.4743 | 0.057113 | -0.042755 | -0.0043149 | 0.049112 | -0.010474 | 0.047919 | 0.089415 | -0.0061157 | -0.0055617 | 0.053846 | 0.032962 | 0.052379 | -64.3116 | -1.7751 | -66.6087 | 56.3846 | 56.225 | 56.3168 | -66.7505 | -66.61 | -2.5454 | -66.7178 | 56.3359 | 56.4312 | 56.3154 | -66.8913 | -0.081813 | -0.089692 | 2.3571 | 0.060045 | 0.14186 | -0.24933 | -0.15746 | -0.22255 | -0.1384 | 0.058678 | -0.049087 | 0.17346 | -0.043057 | -0.1589 | 123.0533 | 122.8937 | 122.9855 | 64.8936 | -123.2248 | 123.0046 | 123.0999 | 122.9841 | 64.1233 | -123.3656
409.2812 | 123.2941 | -66.6733 | 56.4377 | 0.072375 | -0.044892 | -0.0043149 | 0.049112 | -0.011542 | 0.047919 | 0.074154 | -0.0061157 | -0.0066297 | 0.053846 | 0.031893 | 0.053447 | -64.3024 | -2.0406 | -66.5949 | 56.3983 | 56.2341 | 56.3306 | -66.7597 | -66.5917 | -2.8155 | -66.7041 | 56.3542 | 56.445 | 56.3383 | -66.8867 | -0.086393 | -0.039336 | 2.3709 | 0.078357 | 0.16475 | -0.20355 | -0.10711 | -0.21339 | -0.083469 | 0.08157 | -0.030773 | 0.18262 | 0.0073 | -0.099386 | 123.0716 | 122.9074 | 123.0039 | 64.6326 | -123.1974 | 123.0275 | 123.1183 | 123.0116 | 63.8577 | -123.3244
410.2812 | 123.2941 | -66.6504 | 56.488 | 0.057113 | -0.044892 | -0.0053839 | 0.049112 | -0.011542 | 0.045782 | 0.074154 | -0.0071847 | -0.0055617 | 0.051709 | 0.031893 | 0.052379 | -64.2795 | -2.3108 | -66.5858 | 56.4167 | 56.2433 | 56.3352 | -66.7459 | -66.578 | -3.0765 | -66.6995 | 56.3634 | 56.4496 | 56.352 | -66.8684 | -0.095544 | -0.071376 | 2.3709 | 0.064626 | 0.16017 | -0.24475 | -0.15288 | -0.21797 | -0.12467 | 0.072419 | -0.049082 | 0.16889 | -0.038476 | -0.136 | 123.0671 | 122.8937 | 122.9855 | 64.3396 | -123.234 | 123.0138 | 123.1 | 123.0024 | 63.5739 | -123.3564
411.2812 | 123.3078 | -66.6367 | 56.5063 | 0.057113 | -0.04596 | -0.0053839 | 0.050181 | -0.010474 | 0.04685 | 0.089415 | -0.0071847 | -0.0066297 | 0.054914 | 0.032962 | 0.053447 | -64.2658 | -2.5901 | -66.572 | 56.4258 | 56.2479 | 56.3535 | -66.7322 | -66.5551 | -3.3696 | -66.6766 | 56.3771 | 56.4679 | 56.352 | -66.8546 | -0.095541 | -0.080531 | 2.3709 | 0.064628 | 0.16017 | -0.25848 | -0.15288 | -0.21796 | -0.12924 | 0.081579 | -0.039921 | 0.17804 | -0.038472 | -0.15432 | 123.0625 | 122.8845 | 122.9901 | 64.0466 | -123.2385 | 123.0138 | 123.1045 | 122.9887 | 63.2671 | -123.361
412.2812 | 123.3078 | -66.6092 | 56.5063 | 0.041851 | -0.04596 | -0.0075209 | 0.049112 | -0.010474 | 0.04685 | 0.058893 | -0.0071847 | -0.0055617 | 0.052777 | 0.03403 | 0.052379 | -64.252 | -2.8831 | -66.5537 | 56.4487 | 56.257 | 56.3672 | -66.7139 | -66.5459 | -3.6351 | -66.6628 | 56.3771 | 56.477 | 56.3749 | -66.85 | -0.10469 | -0.057639 | 2.3571 | 0.055475 | 0.16017 | -0.24932 | -0.13914 | -0.24085 | -0.12924 | 0.063271 | -0.053651 | 0.1872 | -0.029315 | -0.13142 | 123.0579 | 122.8662 | 122.9764 | 63.7261 | -123.2202 | 122.9863 | 123.0862 | 122.9841 | 62.9741 | -123.3564
413.2812 | 123.317 | -66.6046 | 56.5338 | 0.057113 | -0.044892 | -0.0064519 | 0.048044 | -0.0094052 | 0.04685 | 0.058893 | -0.0071847 | -0.0055617 | 0.051709 | 0.03403 | 0.053447 | -64.2429 | -3.1853 | -66.54 | 56.4441 | 56.2708 | 56.3672 | -66.7001 | -66.5368 | -3.919 | -66.6445 | 56.3954 | 56.4862 | 56.3703 | -66.8363 | -0.095532 | -0.089682 | 2.3617 | 0.064632 | 0.16016 | -0.26305 | -0.16661 | -0.23169 | -0.13839 | 0.06785 | -0.039915 | 0.19178 | -0.047623 | -0.16347 | 123.0487 | 122.8754 | 122.9718 | 63.4193 | -123.234 | 123 | 123.0908 | 122.975 | 62.6856 | -123.3701
414.2812 | 123.2895 | -66.6321 | 56.5247 | 0.041851 | -0.04596 | -0.0075209 | 0.050181 | -0.010474 | 0.047919 | 0.089415 | -0.0061157 | -0.0066297 | 0.050641 | 0.03403 | 0.052379 | -64.2292 | -3.4921 | -66.5308 | 56.467 | 56.2845 | 56.3855 | -66.6956 | -66.523 | -4.2212 | -66.6354 | 56.4137 | 56.4953 | 56.3841 | -66.8271 | -0.063487 | -0.057635 | 2.4029 | 0.10125 | 0.16474 | -0.24016 | -0.13914 | -0.19507 | -0.11092 | 0.10905 | -0.003291 | 0.19178 | -0.029311 | -0.14058 | 123.0991 | 122.9166 | 123.0176 | 63.14 | -123.2202 | 123.0458 | 123.1274 | 123.0162 | 62.4109 | -123.3518
415.2812 | 123.2437 | -66.5863 | 56.5704 | 0.057113 | -0.047029 | -0.0064519 | 0.049112 | -0.011542 | 0.047919 | 0.058893 | -0.0071847 | -0.0066297 | 0.052777 | 0.032962 | 0.052379 | -64.2154 | -3.7897 | -66.5034 | 56.4716 | 56.2982 | 56.4038 | -66.6773 | -66.5093 | -4.5463 | -66.6171 | 56.4229 | 56.5091 | 56.3932 | -66.8088 | -0.090948 | -0.098834 | 2.3709 | 0.082948 | 0.1739 | -0.2722 | -0.1666 | -0.22253 | -0.14754 | 0.077012 | -0.030752 | 0.19178 | -0.061352 | -0.17719 | 123.0579 | 122.8845 | 122.9901 | 62.7966 | -123.2477 | 123.0092 | 123.0954 | 122.9795 | 62.04 | -123.3793
416.2812 | 123.2712 | -66.5909 | 56.5796 | 0.072375 | -0.04596 | -0.0053839 | 0.050181 | -0.011542 | 0.045782 | 0.10468 | -0.0071847 | -0.0044937 | 0.053846 | 0.035099 | 0.05131 | -64.1925 | -4.1193 | -66.485 | 56.4945 | 56.3166 | 56.413 | -66.6498 | -66.4864 | -4.8302 | -66.6079 | 56.4412 | 56.5366 | 56.4161 | -66.7905 | -0.058897 | -0.085097 | 2.3984 | 0.10584 | 0.16473 | -0.26304 | -0.1666 | -0.19964 | -0.13839 | 0.10448 | -0.017018 | 0.18262 | -0.043035 | -0.16346 | 123.0854 | 122.9074 | 123.0039 | 62.4715 | -123.2294 | 123.0321 | 123.1274 | 123.007 | 61.7607 | -123.3701
417.2812 | 123.3032 | -66.5955 | 56.5842 | 0.072375 | -0.047029 | -0.0043149 | 0.049112 | -0.010474 | 0.047919 | 0.074154 | -0.0082527 | -0.0066297 | 0.052777 | 0.035099 | 0.052379 | -64.1742 | -4.4261 | -66.4805 | 56.4945 | 56.3211 | 56.4405 | -66.6498 | -66.4727 | -5.169 | -66.5804 | 56.4549 | 56.5411 | 56.4344 | -66.7768 | -0.054319 | -0.089674 | 2.4212 | 0.11499 | 0.16931 | -0.26304 | -0.1437 | -0.18132 | -0.12923 | 0.1228 | 0.015032 | 0.19635 | -0.043034 | -0.14972 | 123.09 | 122.9166 | 123.0359 | 62.1694 | -123.2339 | 123.0504 | 123.1366 | 123.0299 | 61.4265 | -123.3609
418.2812 | 123.2666 | -66.5543 | 56.5887 | 0.1029 | -0.044892 | -0.0053839 | 0.049112 | -0.01261 | 0.04685 | 0.058893 | -0.0061157 | -0.0066297 | 0.051709 | 0.035099 | 0.05131 | -64.1605 | -4.7741 | -66.453 | 56.522 | 56.3486 | 56.445 | -66.6315 | -66.4452 | -5.517 | -66.5713 | 56.4687 | 56.5594 | 56.4482 | -66.7722 | -0.077202 | -0.066781 | 2.3938 | 0.10126 | 0.17847 | -0.24014 | -0.1437 | -0.21794 | -0.12007 | 0.10907 | -0.017009 | 0.20093 | -0.029297 | -0.14056 | 123.0762 | 122.9029 | 122.9993 | 61.7802 | -123.2202 | 123.0229 | 123.1137 | 123.0024 | 61.0373 | -123.3609
419.2812 | 123.2437 | -66.5497 | 56.6071 | 0.072375 | -0.047029 | -0.0053839 | 0.050181 | -0.0094052 | 0.04685 | 0.074154 | -0.0071847 | -0.0055617 | 0.051709 | 0.03403 | 0.05131 | -64.133 | -5.0992 | -66.4393 | 56.5403 | 56.3623 | 56.4542 | -66.6177 | -66.436 | -5.8558 | -66.553 | 56.4778 | 56.5778 | 56.4528 | -66.7493 | -0.068042 | -0.066779 | 2.4167 | 0.11042 | 0.17846 | -0.24471 | -0.15286 | -0.19962 | -0.12922 | 0.11365 | -0.003271 | 0.19635 | -0.029294 | -0.15429 | 123.09 | 122.912 | 123.0039 | 61.4505 | -123.2248 | 123.0275 | 123.1274 | 123.0024 | 60.6939 | -123.3564
420.2812 | 123.2437 | -66.5359 | 56.6574 | 0.057113 | -0.044892 | -0.0043149 | 0.049112 | -0.0083372 | 0.047919 | 0.074154 | -0.0061157 | -0.0055617 | 0.052777 | 0.035099 | 0.052379 | -64.1193 | -5.4288 | -66.4164 | 56.5449 | 56.3761 | 56.4725 | -66.6086 | -66.4131 | -6.1717 | -66.5301 | 56.4961 | 56.5915 | 56.4802 | -66.7264 | -0.072618 | -0.11255 | 2.4167 | 0.11958 | 0.1922 | -0.28133 | -0.1849 | -0.19046 | -0.16126 | 0.12281 | 0.005889 | 0.19635 | -0.065912 | -0.17718 | 123.0808 | 122.912 | 123.0085 | 61.1071 | -123.266 | 123.0321 | 123.1274 | 123.0162 | 60.3642 | -123.3838
421.2812 | 123.2986 | -66.5131 | 56.662 | 0.057113 | -0.04596 | -0.0075209 | 0.049112 | -0.010474 | 0.04685 | 0.058893 | -0.0071847 | -0.0055617 | 0.052777 | 0.03403 | 0.050242 | -64.1193 | -5.7356 | -66.4118 | 56.5632 | 56.3898 | 56.4771 | -66.5903 | -66.3948 | -6.5106 | -66.5163 | 56.5053 | 56.5915 | 56.494 | -66.7264 | -0.07719 | -0.098818 | 2.3938 | 0.10127 | 0.17846 | -0.27217 | -0.1849 | -0.21335 | -0.15668 | 0.11824 | -0.003263 | 0.21009 | -0.070489 | -0.16802 | 123.0762 | 122.9029 | 122.9902 | 60.7775 | -123.2522 | 123.0184 | 123.1046 | 123.007 | 60.0025 | -123.3884
422.2812 | 123.2941 | -66.4764 | 56.6528 | 0.087637 | -0.04596 | -0.0053839 | 0.050181 | -0.010474 | 0.04685 | 0.074154 | -0.0061157 | -0.0066297 | 0.053846 | 0.036167 | 0.052379 | -64.1055 | -6.0515 | -66.3889 | 56.5723 | 56.399 | 56.5 | -66.5811 | -66.3811 | -6.8631 | -66.5072 | 56.5236 | 56.6052 | 56.4985 | -66.7173 | -0.10465 | -0.080506 | 2.3709 | 0.087541 | 0.19219 | -0.25386 | -0.15285 | -0.24082 | -0.12921 | 0.095352 | -0.030727 | 0.21009 | -0.047598 | -0.15428 | 123.0488 | 122.8754 | 122.9764 | 60.4249 | -123.2339 | 123.0001 | 123.0817 | 122.975 | 59.6133 | -123.3701
423.2812 | 123.2712 | -66.5039 | 56.6803 | 0.072375 | -0.047029 | -0.0053839 | 0.050181 | -0.011542 | 0.047919 | 0.074154 | -0.0071847 | -0.0055617 | 0.052777 | 0.035099 | 0.053447 | -64.0918 | -6.3674 | -66.3843 | 56.5861 | 56.4127 | 56.5137 | -66.5674 | -66.3719 | -7.1745 | -66.4843 | 56.5282 | 56.6235 | 56.5214 | -66.6989 | -0.063451 | -0.094237 | 2.4121 | 0.11959 | 0.18304 | -0.26759 | -0.16658 | -0.19504 | -0.1521 | 0.13198 | 0.019632 | 0.21467 | -0.05675 | -0.15886 | 123.09 | 122.9166 | 123.0176 | 60.1365 | -123.2477 | 123.0321 | 123.1275 | 123.0253 | 59.3294 | -123.3792
424.2812 | 123.2803 | -66.481 | 56.6986 | 0.041851 | -0.044892 | -0.0043149 | 0.049112 | -0.010474 | 0.047919 | 0.089415 | -0.0050477 | -0.0044937 | 0.051709 | 0.035099 | 0.052379 | -64.0781 | -6.665 | -66.3614 | 56.5861 | 56.4264 | 56.5183 | -66.5628 | -66.349 | -7.4629 | -66.466 | 56.5511 | 56.6373 | 56.5352 | -66.6944 | -0.08176 | -0.11255 | 2.4029 | 0.11959 | 0.20135 | -0.27216 | -0.18031 | -0.21334 | -0.14752 | 0.13198 | 0.015059 | 0.2284 | -0.061324 | -0.16343 | 123.0671 | 122.9075 | 122.9993 | 59.816 | -123.2614 | 123.0321 | 123.1183 | 123.0162 | 59.0181 | -123.393
425.2812 | 123.2712 | -66.481 | 56.694 | 0.041851 | -0.04596 | -0.0064519 | 0.048044 | -0.011542 | 0.04685 | 0.074154 | -0.0071847 | -0.0066297 | 0.052777 | 0.036167 | 0.05131 | -64.0414 | -6.9901 | -66.3477 | 56.6044 | 56.4264 | 56.532 | -66.5582 | -66.3307 | -7.7743 | -66.4614 | 56.5602 | 56.6419 | 56.5398 | -66.676 | -0.077181 | -0.089656 | 2.4396 | 0.13332 | 0.2105 | -0.26759 | -0.162 | -0.19503 | -0.13379 | 0.1503 | 0.019638 | 0.21467 | -0.052169 | -0.15428 | 123.0854 | 122.9075 | 123.0131 | 59.4909 | -123.2522 | 123.0413 | 123.1229 | 123.0208 | 58.7067 | -123.3701
426.2812 | 123.2437 | -66.4536 | 56.7078 | 0.041851 | -0.047029 | -0.0064519 | 0.046976 | -0.010474 | 0.048987 | 0.058893 | -0.0082527 | -0.0066297 | 0.052777 | 0.036167 | 0.05131 | -64.046 | -7.2923 | -66.334 | 56.6227 | 56.4448 | 56.5412 | -66.5353 | -66.3216 | -8.0444 | -66.4385 | 56.574 | 56.651 | 56.5443 | -66.6623 | -0.081753 | -0.085076 | 2.4075 | 0.11959 | 0.20134 | -0.263 | -0.16657 | -0.20876 | -0.13378 | 0.13199 | 0.015065 | 0.22382 | -0.056744 | -0.16343 | 123.0762 | 122.8983 | 122.9947 | 59.1612 | -123.2431 | 123.0275 | 123.1046 | 122.9979 | 58.4091 | -123.3701
427.2812 | 123.2803 | -66.4398 | 56.7307 | 0.041851 | -0.04596 | -0.0053839 | 0.046976 | -0.010474 | 0.04685 | 0.058893 | -0.0050477 | -0.0066297 | 0.053846 | 0.035099 | 0.05131 | -64.0231 | -7.6311 | -66.3111 | 56.6273 | 56.4585 | 56.5503 | -66.5216 | -66.2987 | -8.2963 | -66.4202 | 56.5831 | 56.6602 | 56.5672 | -66.6577 | -0.081749 | -0.10339 | 2.4167 | 0.12875 | 0.2105 | -0.27215 | -0.1803 | -0.21791 | -0.14751 | 0.14115 | 0.019647 | 0.23756 | -0.070475 | -0.16342 | 123.0671 | 122.8983 | 122.9902 | 58.8087 | -123.2522 | 123.023 | 123.1 | 123.007 | 58.1436 | -123.3884
428.2812 | 123.3673 | -66.3849 | 56.6986 | 0.072375 | -0.047029 | -0.0053839 | 0.050181 | -0.010474 | 0.047919 | 0.058893 | -0.0082527 | -0.0066297 | 0.052777 | 0.036167 | 0.050242 | -64.0369 | -7.947 | -66.3065 | 56.6364 | 56.4677 | 56.5641 | -66.5216 | -66.2895 | -8.5069 | -66.4156 | 56.5923 | 56.6831 | 56.581 | -66.6532 | -0.13668 | -0.062185 | 2.348 | 0.078398 | 0.21508 | -0.23095 | -0.13452 | -0.26826 | -0.10631 | 0.095374 | -0.030705 | 0.23756 | -0.015538 | -0.11765 | 123.0213 | 122.8525 | 122.949 | 58.4378 | -123.2202 | 122.9772 | 123.068 | 122.9659 | 57.878 | -123.3518
429.3125 | 123.3673 | -66.4124 | 56.6574 | 0.057113 | -0.047029 | -0.0064519 | 0.048044 | -0.011542 | 0.047919 | 0.074154 | -0.0082527 | -0.0044937 | 0.053846 | 0.035099 | 0.05131 | -64.0323 | -8.3133 | -66.2882 | 56.6502 | 56.4722 | 56.5732 | -66.5033 | -66.2666 | -8.6992 | -66.3973 | 56.6015 | 56.6876 | 56.581 | -66.6348 | -0.090898 | -0.007252 | 2.3801 | 0.12418 | 0.21507 | -0.18518 | -0.084168 | -0.22248 | -0.055957 | 0.14573 | 0.015076 | 0.23756 | 0.030238 | -0.076447 | 123.0625 | 122.8846 | 122.9856 | 58.099 | -123.1607 | 123.0138 | 123.1 | 122.9933 | 57.7132 | -123.2922
430.2812 | 123.3353 | -66.3757 | 56.7261 | 0.087637 | -0.047029 | -0.0064519 | 0.049112 | -0.011542 | 0.047919 | 0.058893 | -0.0082527 | -0.0055617 | 0.052777 | 0.036167 | 0.052379 | -64.0002 | -8.6796 | -66.279 | 56.6685 | 56.486 | 56.587 | -66.5078 | -66.2575 | -8.832 | -66.3881 | 56.6106 | 56.7014 | 56.5855 | -66.6165 | -0.1321 | -0.057602 | 2.3755 | 0.096712 | 0.22881 | -0.2401 | -0.1391 | -0.24079 | -0.11546 | 0.11827 | -0.012389 | 0.2284 | -0.02469 | -0.14053 | 123.0442 | 122.8617 | 122.9627 | 57.6961 | -123.2339 | 122.9863 | 123.0771 | 122.9613 | 57.5438 | -123.3426
431.2812 | 123.3627 | -66.3437 | 56.7352 | 0.041851 | -0.049165 | -0.0043149 | 0.049112 | -0.011542 | 0.047919 | 0.074154 | -0.0082527 | -0.0055617 | 0.052777 | 0.035099 | 0.052379 | -63.9911 | -8.9406 | -66.2699 | 56.6685 | 56.4951 | 56.5961 | -66.4849 | -66.2391 | -8.9556 | -66.3698 | 56.6152 | 56.7151 | 56.6039 | -66.6211 | -0.14125 | -0.066757 | 2.3526 | 0.073825 | 0.21507 | -0.2401 | -0.13909 | -0.27741 | -0.12004 | 0.10454 | -0.026117 | 0.2513 | -0.020109 | -0.13137 | 123.0122 | 122.8388 | 122.9398 | 57.4031 | -123.2202 | 122.9589 | 123.0588 | 122.9475 | 57.3881 | -123.3563
432.2812 | 123.3444 | -66.3712 | 56.7535 | 0.072375 | -0.047029 | -0.0053839 | 0.050181 | -0.011542 | 0.047919 | 0.074154 | -0.0061157 | -0.0066297 | 0.052777 | 0.035099 | 0.05131 | -63.9682 | -9.1741 | -66.2561 | 56.6685 | 56.4997 | 56.6007 | -66.4758 | -66.23 | -9.2074 | -66.3652 | 56.6335 | 56.7105 | 56.5993 | -66.6074 | -0.10462 | -0.085068 | 2.403 | 0.11503 | 0.21965 | -0.25383 | -0.15283 | -0.23621 | -0.12004 | 0.14117 | 0.005928 | 0.24214 | -0.042999 | -0.15426 | 123.0396 | 122.8709 | 122.9719 | 57.197 | -123.2293 | 123.0047 | 123.0817 | 122.9704 | 57.1637 | -123.3609
433.2812 | 123.3627 | -66.3254 | 56.7398 | 0.072375 | -0.049165 | -0.0085889 | 0.049112 | -0.010474 | 0.047919 | 0.058893 | -0.0061157 | -0.0044937 | 0.051709 | 0.037235 | 0.052379 | -63.9545 | -9.4443 | -66.2378 | 56.6914 | 56.5134 | 56.6099 | -66.462 | -66.2117 | -9.4135 | -66.3469 | 56.6381 | 56.7197 | 56.6222 | -66.5982 | -0.13666 | -0.048443 | 2.3709 | 0.087562 | 0.22423 | -0.22636 | -0.12994 | -0.27283 | -0.10173 | 0.1137 | -0.021534 | 0.25129 | -0.020108 | -0.11764 | 123.0167 | 122.8388 | 122.9352 | 56.8811 | -123.2018 | 122.9635 | 123.0451 | 122.9475 | 56.9119 | -123.338
434.2812 | 123.3627 | -66.3437 | 56.7261 | 0.072375 | -0.049165 | -0.0064519 | 0.048044 | -0.01261 | 0.048987 | 0.074154 | -0.0071847 | -0.0055617 | 0.052777 | 0.037235 | 0.052379 | -63.959 | -9.6274 | -66.2332 | 56.6914 | 56.518 | 56.6236 | -66.4391 | -66.1979 | -9.56 | -66.3332 | 56.6472 | 56.7334 | 56.6176 | -66.5845 | -0.095458 | -0.03471 | 2.3847 | 0.11045 | 0.20591 | -0.20805 | -0.10247 | -0.24078 | -0.078836 | 0.14575 | 0.010513 | 0.25129 | 0.00736 | -0.10848 | 123.0351 | 122.8617 | 122.9673 | 56.7163 | -123.1652 | 122.9909 | 123.0771 | 122.9613 | 56.7837 | -123.3105
435.2812 | 123.381 | -66.3345 | 56.749 | 0.057113 | -0.047029 | -0.0043149 | 0.046976 | -0.01261 | 0.04685 | 0.089415 | -0.0071847 | -0.0066297 | 0.051709 | 0.036167 | 0.050242 | -63.9682 | -9.806 | -66.2241 | 56.7051 | 56.5272 | 56.6328 | -66.4346 | -66.175 | -9.6882 | -66.3286 | 56.6564 | 56.7426 | 56.6267 | -66.5845 | -0.10003 | -0.043863 | 2.3663 | 0.11045 | 0.21049 | -0.22178 | -0.1162 | -0.24994 | -0.092567 | 0.15949 | 0.005936 | 0.25587 | -0.00637 | -0.12221 | 123.0396 | 122.8617 | 122.9673 | 56.5286 | -123.1835 | 122.9909 | 123.0771 | 122.9613 | 56.6463 | -123.3334
436.2812 | 123.3673 | -66.3208 | 56.7627 | 0.026589 | -0.047029 | -0.0075209 | 0.048044 | -0.011542 | 0.048987 | 0.058893 | -0.0071847 | -0.0076977 | 0.051709 | 0.035099 | 0.052379 | -63.9545 | -9.9433 | -66.2012 | 56.7143 | 56.5409 | 56.6328 | -66.4391 | -66.1613 | -9.821 | -66.3103 | 56.6701 | 56.7472 | 56.6496 | -66.5662 | -0.11835 | -0.048439 | 2.3663 | 0.11961 | 0.23796 | -0.22178 | -0.12993 | -0.24536 | -0.092565 | 0.15949 | 0.010518 | 0.25587 | -0.015525 | -0.11305 | 123.0351 | 122.8617 | 122.9536 | 56.3775 | -123.2018 | 122.9909 | 123.068 | 122.9704 | 56.4998 | -123.3289
437.2812 | 123.4177 | -66.3071 | 56.7627 | 0.057113 | -0.047029 | -0.0053839 | 0.050181 | -0.0094052 | 0.048987 | 0.074154 | -0.0061157 | -0.0066297 | 0.051709 | 0.036167 | 0.05131 | -63.9819 | -10.0761 | -66.1966 | 56.7097 | 56.5363 | 56.6419 | -66.43 | -66.1567 | -9.7706 | -66.3057 | 56.6564 | 56.7472 | 56.6359 | -66.5799 | -0.12292 | -0.053018 | 2.3251 | 0.11046 | 0.23338 | -0.22635 | -0.12077 | -0.27282 | -0.1063 | 0.15034 | 0.001364 | 0.27419 | -0.015525 | -0.12679 | 123.0167 | 122.8434 | 122.949 | 56.231 | -123.1927 | 122.9635 | 123.0542 | 122.943 | 56.5365 | -123.3426
438.2812 | 123.381 | -66.2933 | 56.7719 | 0.057113 | -0.049165 | -0.0053839 | 0.048044 | -0.0094052 | 0.044714 | 0.074154 | -0.0071847 | -0.0066297 | 0.051709 | 0.036167 | 0.05131 | -63.9728 | -10.218 | -66.1966 | 56.7234 | 56.5409 | 56.6465 | -66.4163 | -66.1384 | -9.8301 | -66.292 | 56.6701 | 56.7609 | 56.6359 | -66.5616 | -0.12292 | -0.048438 | 2.3206 | 0.096724 | 0.21964 | -0.23093 | -0.12535 | -0.26824 | -0.10172 | 0.15492 | 0.001367 | 0.26961 | -0.010945 | -0.13594 | 123.0167 | 122.8343 | 122.9398 | 56.0753 | -123.1881 | 122.9635 | 123.0542 | 122.9292 | 56.4632 | -123.3334
439.2812 | 123.4039 | -66.3116 | 56.7627 | 0.057113 | -0.048097 | -0.0053839 | 0.049112 | -0.010474 | 0.047919 | 0.089415 | -0.0071847 | -0.0076977 | 0.051709 | 0.037235 | 0.05131 | -63.9682 | -10.3783 | -66.1966 | 56.7051 | 56.5318 | 56.6373 | -66.43 | -66.1384 | -9.8622 | -66.2874 | 56.661 | 56.7472 | 56.6405 | -66.5799 | -0.11834 | -0.057596 | 2.3435 | 0.11503 | 0.23338 | -0.23093 | -0.12535 | -0.26825 | -0.10172 | 0.17323 | 0.024257 | 0.2925 | -0.015525 | -0.12221 | 123.0167 | 122.8434 | 122.949 | 55.9334 | -123.1927 | 122.9726 | 123.0588 | 122.9521 | 56.4495 | -123.3426
440.3125 | 123.2391 | -66.3895 | 56.7856 | 0.057113 | -0.04596 | -0.0043149 | 0.049112 | -0.010474 | 0.04685 | 0.043632 | -0.0061157 | -0.0055617 | 0.051709 | 0.037235 | 0.050242 | -63.8904 | -10.7858 | -66.1783 | 56.7234 | 56.5501 | 56.6465 | -66.4483 | -66.1155 | -9.8988 | -66.2737 | 56.6701 | 56.7563 | 56.6588 | -66.5662 | -0.05884 | -0.06217 | 2.4991 | 0.21117 | 0.27001 | -0.23551 | -0.13908 | -0.17669 | -0.11545 | 0.27394 | 0.11581 | 0.2925 | -0.029255 | -0.12678 | 123.1129 | 122.9395 | 123.036 | 55.6037 | -123.2339 | 123.0596 | 123.1458 | 123.0483 | 56.4907 | -123.3517
441.2812 | 123.3673 | -66.2796 | 56.7764 | 0.057113 | -0.048097 | -0.0064519 | 0.048044 | -0.010474 | 0.047919 | 0.058893 | -0.0071847 | -0.0066297 | 0.051709 | 0.038304 | 0.050242 | -63.9545 | -11.0742 | -66.1646 | 56.7234 | 56.5455 | 56.6511 | -66.43 | -66.1109 | -9.9263 | -66.2645 | 56.6747 | 56.7609 | 56.6588 | -66.5616 | -0.15039 | -0.053015 | 2.3251 | 0.11504 | 0.26543 | -0.23093 | -0.12535 | -0.28198 | -0.10172 | 0.16866 | 0.015106 | 0.29708 | -0.015522 | -0.11763 | 123.003 | 122.8251 | 122.9307 | 55.2054 | -123.2064 | 122.9543 | 123.0405 | 122.9384 | 56.3533 | -123.338
442.3125 | 123.2529 | -66.3528 | 56.8039 | 0.057113 | -0.047029 | -0.0064519 | 0.049112 | -0.01261 | 0.04685 | 0.058893 | -0.0061157 | -0.0055617 | 0.050641 | 0.038304 | 0.05131 | -63.872 | -11.3032 | -66.1508 | 56.7326 | 56.5592 | 56.6602 | -66.4254 | -66.0972 | -10.0087 | -66.2553 | 56.6793 | 56.7701 | 56.6496 | -66.557 | -0.072567 | -0.071325 | 2.4808 | 0.20202 | 0.27458 | -0.24466 | -0.14366 | -0.20415 | -0.12461 | 0.25564 | 0.097506 | 0.30166 | -0.033831 | -0.15425 | 123.0854 | 122.9121 | 123.0131 | 55.0497 | -123.2293 | 123.0321 | 123.1229 | 123.0025 | 56.3441 | -123.3609
443.2812 | 123.3398 | -66.3345 | 56.7947 | 0.072375 | -0.047029 | -0.0053839 | 0.046976 | -0.010474 | 0.04685 | 0.058893 | -0.0071847 | -0.0055617 | 0.052777 | 0.036167 | 0.050242 | -63.9453 | -11.5504 | -66.1462 | 56.7326 | 56.5638 | 56.6511 | -66.4254 | -66.0835 | -10.0041 | -66.2462 | 56.6839 | 56.7746 | 56.6634 | -66.557 | -0.090877 | -0.06217 | 2.3892 | 0.18828 | 0.27916 | -0.23092 | -0.14366 | -0.22246 | -0.11087 | 0.25106 | 0.088353 | 0.31082 | -0.020097 | -0.13136 | 123.0671 | 122.8983 | 122.9856 | 54.7841 | -123.2201 | 123.0184 | 123.1092 | 122.9979 | 56.3304 | -123.3517
444.2812 | 123.3398 | -66.2796 | 56.813 | 0.057113 | -0.049165 | -0.0053839 | 0.048044 | -0.01261 | 0.04685 | 0.10468 | -0.0071847 | -0.0055617 | 0.051709 | 0.037235 | 0.05131 | -63.9316 | -11.7244 | -66.1371 | 56.7463 | 56.573 | 56.674 | -66.4163 | -66.056 | -10.1873 | -66.2279 | 56.7022 | 56.7838 | 56.6725 | -66.5433 | -0.13665 | -0.066744 | 2.348 | 0.14251 | 0.27916 | -0.24008 | -0.13908 | -0.26366 | -0.11087 | 0.2236 | 0.051736 | 0.3154 | -0.02925 | -0.14051 | 123.0259 | 122.8526 | 122.9536 | 54.5552 | -123.2293 | 122.9818 | 123.0634 | 122.9521 | 56.0923 | -123.3563
445.2812 | 123.3673 | -66.2704 | 56.7947 | 0.041851 | -0.048097 | -0.0043149 | 0.049112 | -0.0094052 | 0.047919 | 0.10468 | -0.0071847 | -0.0066297 | 0.051709 | 0.038304 | 0.05131 | -63.8995 | -11.99 | -66.1142 | 56.76 | 56.5776 | 56.6877 | -66.3979 | -66.0377 | -10.581 | -66.2141 | 56.7159 | 56.793 | 56.6817 | -66.5249 | -0.12749 | -0.034699 | 2.3709 | 0.15624 | 0.28373 | -0.21719 | -0.10703 | -0.2545 | -0.078824 | 0.23276 | 0.056317 | 0.31082 | -0.001783 | -0.11305 | 123.0305 | 122.848 | 122.9582 | 54.2805 | -123.1927 | 122.9864 | 123.0634 | 122.9521 | 55.6894 | -123.3197
446.2812 | 123.3444 | -66.2704 | 56.8039 | 0.072375 | -0.050234 | -0.0043149 | 0.048044 | -0.010474 | 0.047919 | 0.074154 | -0.0071847 | -0.0066297 | 0.051709 | 0.035099 | 0.049174 | -63.8766 | -12.1777 | -66.0867 | 56.7829 | 56.6096 | 56.6969 | -66.3888 | -66.0148 | -10.7688 | -66.1867 | 56.7342 | 56.8113 | 56.7 | -66.5112 | -0.11833 | -0.020962 | 2.3938 | 0.18372 | 0.30205 | -0.19429 | -0.10703 | -0.24076 | -0.069665 | 0.25566 | 0.083789 | 0.32455 | 0.007377 | -0.10389 | 123.0534 | 122.8801 | 122.9673 | 54.0928 | -123.1927 | 123.0047 | 123.0817 | 122.9705 | 55.5017 | -123.3151
447.2812 | 123.3307 | -66.2613 | 56.8542 | 0.057113 | -0.049165 | -0.0064519 | 0.048044 | -0.010474 | 0.045782 | 0.043632 | -0.0061157 | -0.0066297 | 0.051709 | 0.036167 | 0.052379 | -63.8492 | -12.37 | -66.0776 | 56.7875 | 56.6096 | 56.7152 | -66.375 | -66.0011 | -10.9336 | -66.1638 | 56.748 | 56.8296 | 56.7092 | -66.4975 | -0.11375 | -0.066738 | 2.4121 | 0.18372 | 0.29747 | -0.24464 | -0.13907 | -0.23618 | -0.10628 | 0.26024 | 0.097528 | 0.33371 | -0.024663 | -0.14508 | 123.0488 | 122.8709 | 122.9765 | 53.8913 | -123.2293 | 123.0093 | 123.0909 | 122.9705 | 55.3277 | -123.3517
448.2812 | 123.349 | -66.2247 | 56.8588 | 0.057113 | -0.050234 | -0.0064519 | 0.045907 | -0.010474 | 0.047919 | 0.089415 | -0.0061157 | -0.0076977 | 0.051709 | 0.038304 | 0.052379 | -63.8125 | -12.5943 | -66.0501 | 56.815 | 56.6417 | 56.7472 | -66.3338 | -65.9507 | -11.5426 | -66.118 | 56.7663 | 56.8525 | 56.7412 | -66.47 | -0.10916 | -0.043846 | 2.4121 | 0.17456 | 0.28373 | -0.21717 | -0.1116 | -0.24533 | -0.092548 | 0.27398 | 0.10669 | 0.35202 | -0.006348 | -0.11761 | 123.0396 | 122.8663 | 122.9719 | 53.6303 | -123.1927 | 122.9909 | 123.0771 | 122.9659 | 54.6821 | -123.3288
449.2812 | 123.2986 | -66.2476 | 56.868 | 0.057113 | -0.049165 | -0.0053839 | 0.048044 | -0.011542 | 0.048987 | 0.074154 | -0.0071847 | -0.0076977 | 0.050641 | 0.036167 | 0.05131 | -63.7851 | -12.75 | -66.0364 | 56.815 | 56.6417 | 56.7472 | -66.343 | -65.9461 | -12.005 | -66.1134 | 56.7709 | 56.8479 | 56.7366 | -66.47 | -0.095431 | -0.053001 | 2.4625 | 0.21119 | 0.30662 | -0.22633 | -0.12075 | -0.22244 | -0.097124 | 0.30145 | 0.13416 | 0.3566 | -0.020081 | -0.13135 | 123.0625 | 122.8892 | 122.9948 | 53.4976 | -123.211 | 123.0184 | 123.0955 | 122.9842 | 54.2425 | -123.338
450.2812 | 123.3307 | -66.2338 | 56.8634 | 0.072375 | -0.050234 | -0.0043149 | 0.048044 | -0.011542 | 0.045782 | 0.043632 | -0.0050477 | -0.0055617 | 0.051709 | 0.037235 | 0.050242 | -63.7393 | -12.9515 | -66.0181 | 56.8287 | 56.6554 | 56.7564 | -66.3247 | -65.9278 | -12.2248 | -66.0997 | 56.78 | 56.8525 | 56.7595 | -66.4608 | -0.090848 | -0.034687 | 2.4946 | 0.21577 | 0.30662 | -0.20801 | -0.10702 | -0.22702 | -0.083389 | 0.30603 | 0.13416 | 0.36118 | -0.010925 | -0.10387 | 123.0625 | 122.8892 | 122.9902 | 53.2824 | -123.1881 | 123.0138 | 123.0863 | 122.9934 | 54.009 | -123.3242
451.2969 | 123.2941 | -66.2109 | 56.9366 | 0.057113 | -0.049165 | -0.0064519 | 0.046976 | -0.011542 | 0.044714 | 0.058893 | -0.0061157 | -0.0066297 | 0.050641 | 0.037235 | 0.05131 | -63.6385 | -13.2262 | -65.9997 | 56.847 | 56.6554 | 56.7655 | -66.3109 | -65.9049 | -12.4675 | -66.0722 | 56.7937 | 56.8754 | 56.7733 | -66.4563 | -0.1 | -0.089617 | 2.5724 | 0.21119 | 0.31119 | -0.28125 | -0.1711 | -0.24533 | -0.1429 | 0.30603 | 0.13875 | 0.38407 | -0.061275 | -0.16338 | 123.058 | 122.8663 | 122.9765 | 52.9848 | -123.2476 | 123.0047 | 123.0863 | 122.9842 | 53.7435 | -123.3929
452.2812 | 123.3444 | -66.1972 | 56.9046 | 0.026589 | -0.050234 | -0.0064519 | 0.048044 | -0.011542 | 0.047919 | 0.058893 | -0.0071847 | -0.0055617 | 0.051709 | 0.036167 | 0.05131 | -63.6843 | -13.4047 | -65.9631 | 56.8562 | 56.692 | 56.7884 | -66.2926 | -65.8545 | -12.8704 | -66.0356 | 56.8121 | 56.8983 | 56.787 | -66.4242 | -0.095417 | -0.048416 | 2.5129 | 0.23409 | 0.3295 | -0.21258 | -0.11617 | -0.22701 | -0.092539 | 0.34267 | 0.16164 | 0.38865 | -0.006338 | -0.1176 | 123.0534 | 122.8892 | 122.9856 | 52.7925 | -123.1972 | 123.0093 | 123.0955 | 122.9842 | 53.3268 | -123.3288
453.2812 | 123.3215 | -66.1926 | 56.9092 | 0.041851 | -0.049165 | -0.0043149 | 0.049112 | -0.010474 | 0.048987 | 0.043632 | -0.0061157 | -0.0066297 | 0.051709 | 0.037235 | 0.050242 | -63.6706 | -13.5513 | -65.9494 | 56.8791 | 56.692 | 56.8068 | -66.2606 | -65.8225 | -13.1039 | -66.0127 | 56.8212 | 56.912 | 56.8007 | -66.4105 | -0.067942 | -0.030102 | 2.522 | 0.24324 | 0.31119 | -0.21716 | -0.10243 | -0.21785 | -0.08796 | 0.37014 | 0.17996 | 0.39781 | 0.00282 | -0.10844 | 123.0717 | 122.8847 | 122.9994 | 52.6414 | -123.1697 | 123.0138 | 123.1046 | 122.9934 | 53.0887 | -123.3197
454.2812 | 123.3353 | -66.1469 | 56.9412 | 0.072375 | -0.050234 | -0.0053839 | 0.048044 | -0.011542 | 0.047919 | 0.074154 | -0.0071847 | -0.0044937 | 0.051709 | 0.038304 | 0.050242 | -63.6202 | -13.7344 | -65.9219 | 56.9065 | 56.7195 | 56.8296 | -66.2514 | -65.7859 | -13.548 | -65.9806 | 56.8533 | 56.9395 | 56.8236 | -66.3876 | -0.10456 | -0.034675 | 2.5266 | 0.22494 | 0.3295 | -0.22173 | -0.11158 | -0.24073 | -0.087953 | 0.361 | 0.16624 | 0.40697 | -0.001751 | -0.11759 | 123.0534 | 122.8663 | 122.9765 | 52.4124 | -123.1926 | 123.0001 | 123.0863 | 122.9705 | 52.5988 | -123.3288
455.3125 | 123.2529 | -66.1606 | 56.9733 | 0.057113 | -0.050234 | -0.0085889 | 0.049112 | -0.010474 | 0.04685 | 0.074154 | -0.0071847 | -0.0066297 | 0.051709 | 0.037235 | 0.05131 | -63.5103 | -14.4532 | -65.8853 | 56.9203 | 56.7424 | 56.848 | -66.2331 | -65.7492 | -13.8045 | -65.9486 | 56.867 | 56.9669 | 56.8511 | -66.3601 | -0.072513 | -0.052984 | 2.6502 | 0.27529 | 0.34781 | -0.23087 | -0.12531 | -0.19953 | -0.10626 | 0.41136 | 0.21202 | 0.41154 | -0.006324 | -0.12217 | 123.0809 | 122.903 | 123.0085 | 51.7073 | -123.2064 | 123.0276 | 123.1275 | 123.0117 | 52.3561 | -123.3334
456.2812 | 123.3902 | -66.1102 | 56.9458 | 0.057113 | -0.050234 | -0.0053839 | 0.049112 | -0.011542 | 0.048987 | 0.058893 | -0.0082527 | -0.0055617 | 0.052777 | 0.039372 | 0.052379 | -63.5287 | -14.7142 | -65.8624 | 56.9203 | 56.7516 | 56.8571 | -66.2285 | -65.7172 | -14.1204 | -65.9257 | 56.8762 | 56.9715 | 56.8511 | -66.351 | -0.11829 | -0.025518 | 2.5816 | 0.24783 | 0.36612 | -0.19425 | -0.088686 | -0.24072 | -0.069639 | 0.39305 | 0.18456 | 0.42528 | 0.025721 | -0.0947 | 123.0305 | 122.8618 | 122.9673 | 51.396 | -123.1743 | 122.9864 | 123.0818 | 122.9613 | 51.9898 | -123.2968
457.2969 | 123.2758 | -66.124 | 57.0602 | 0.057113 | -0.050234 | -0.0075209 | 0.049112 | -0.011542 | 0.045782 | 0.074154 | -0.0061157 | -0.0076977 | 0.051709 | 0.038304 | 0.050242 | -63.4417 | -14.9248 | -65.8349 | 56.9569 | 56.7836 | 56.8892 | -66.2285 | -65.6805 | -14.3997 | -65.889 | 56.9036 | 56.9944 | 56.874 | -66.3372 | -0.10455 | -0.10333 | 2.6823 | 0.28904 | 0.39359 | -0.27664 | -0.17108 | -0.21325 | -0.15661 | 0.44342 | 0.23492 | 0.44817 | -0.065827 | -0.18625 | 123.0809 | 122.9076 | 123.0131 | 51.1991 | -123.2888 | 123.0276 | 123.1184 | 122.998 | 51.7243 | -123.3975
458.2812 | 123.4314 | -66.0828 | 57.019 | 0.057113 | -0.050234 | -0.0064519 | 0.046976 | -0.010474 | 0.047919 | 0.058893 | -0.0071847 | -0.0055617 | 0.050641 | 0.038304 | 0.05131 | -63.4691 | -15.1217 | -65.8075 | 56.9752 | 56.7928 | 56.8983 | -66.1873 | -65.6439 | -14.6881 | -65.8478 | 56.9219 | 57.0082 | 56.8969 | -66.3143 | -0.10454 | -0.043819 | 2.6136 | 0.27531 | 0.37985 | -0.22628 | -0.12072 | -0.23156 | -0.097096 | 0.43885 | 0.23493 | 0.46649 | -0.010892 | -0.12216 | 123.058 | 122.8755 | 122.9811 | 50.961 | -123.2064 | 123.0047 | 123.0909 | 122.9797 | 51.3946 | -123.3334
459.3125 | 123.2849 | -66.069 | 57.0694 | 0.072375 | -0.053439 | -0.0064519 | 0.049112 | -0.01261 | 0.04685 | 0.074154 | -0.0082527 | -0.0055617 | 0.051709 | 0.039372 | 0.05131 | -63.3684 | -15.4376 | -65.7754 | 56.9935 | 56.8157 | 56.9258 | -66.1507 | -65.6073 | -14.9308 | -65.8204 | 56.9403 | 57.031 | 56.9198 | -66.296 | -0.081644 | -0.075859 | 2.7006 | 0.29362 | 0.37527 | -0.25374 | -0.1436 | -0.22698 | -0.12914 | 0.46174 | 0.24867 | 0.47565 | -0.038353 | -0.14962 | 123.0626 | 122.8847 | 122.9948 | 50.6314 | -123.2201 | 123.0093 | 123.1001 | 122.9888 | 51.1382 | -123.3654
460.2812 | 123.3994 | -66.0095 | 57.0648 | 0.057113 | -0.051302 | -0.0053839 | 0.048044 | -0.010474 | 0.047919 | 0.058893 | -0.0050477 | -0.0055617 | 0.051709 | 0.04044 | 0.05131 | -63.373 | -15.6162 | -65.7296 | 57.0256 | 56.8477 | 56.9533 | -66.1278 | -65.5523 | -15.2513 | -65.7837 | 56.9769 | 57.0677 | 56.9473 | -66.264 | -0.11826 | -0.039233 | 2.6365 | 0.27989 | 0.39815 | -0.21711 | -0.11155 | -0.25443 | -0.08793 | 0.45718 | 0.22579 | 0.48022 | 0.002853 | -0.11757 | 123.0351 | 122.8572 | 122.9628 | 50.3933 | -123.1926 | 122.9864 | 123.0772 | 122.9568 | 50.7582 | -123.3288
461.3125 | 123.2803 | -66.0233 | 57.1289 | 0.072375 | -0.052371 | -0.0064519 | 0.050181 | -0.011542 | 0.04685 | 0.058893 | -0.0061157 | -0.0055617 | 0.051709 | 0.037235 | 0.052379 | -63.2769 | -15.8314 | -65.7067 | 57.0485 | 56.866 | 56.9762 | -66.1232 | -65.5249 | -15.6405 | -65.7379 | 56.986 | 57.0768 | 56.9656 | -66.2502 | -0.099948 | -0.080428 | 2.7464 | 0.31652 | 0.41647 | -0.26288 | -0.15275 | -0.22696 | -0.14286 | 0.49838 | 0.28531 | 0.51227 | -0.052076 | -0.16334 | 123.0717 | 122.8893 | 122.9994 | 50.1919 | -123.2521 | 123.0093 | 123.1001 | 122.9888 | 50.3827 | -123.3791
462.2812 | 123.2895 | -66.0049 | 57.1289 | 0.057113 | -0.052371 | -0.0053839 | 0.049112 | -0.011542 | 0.047919 | 0.058893 | -0.0061157 | -0.0044937 | 0.051709 | 0.04044 | 0.050242 | -63.254 | -16.0695 | -65.6747 | 57.0714 | 56.8798 | 56.9991 | -66.1049 | -65.4653 | -15.9473 | -65.6922 | 57.0181 | 57.118 | 56.9885 | -66.2227 | -0.099942 | -0.057536 | 2.751 | 0.33026 | 0.4302 | -0.24915 | -0.12985 | -0.2178 | -0.11081 | 0.5396 | 0.31279 | 0.53059 | -0.010869 | -0.14045 | 123.0763 | 122.8847 | 123.004 | 49.9355 | -123.2338 | 123.023 | 123.123 | 122.9934 | 50.0577 | -123.3517
463.3125 | 123.3719 | -65.9271 | 57.1518 | 0.072375 | -0.052371 | -0.0064519 | 0.049112 | -0.010474 | 0.047919 | 0.058893 | -0.0061157 | -0.0076977 | 0.050641 | 0.039372 | 0.050242 | -63.2128 | -16.7929 | -65.6014 | 57.1217 | 56.9439 | 57.0403 | -66.0408 | -65.3921 | -16.3044 | -65.6189 | 57.0685 | 57.1592 | 57.0388 | -66.1724 | -0.11366 | -0.030062 | 2.7144 | 0.32569 | 0.43935 | -0.20793 | -0.11154 | -0.24525 | -0.083335 | 0.53504 | 0.30823 | 0.55348 | 0.007451 | -0.11297 | 123.0489 | 122.871 | 122.9674 | 49.1342 | -123.1926 | 122.9956 | 123.0864 | 122.9659 | 49.6227 | -123.3242
464.2812 | 123.317 | -65.9409 | 57.1838 | 0.057113 | -0.051302 | -0.0053839 | 0.048044 | -0.011542 | 0.045782 | 0.074154 | -0.0050477 | -0.0076977 | 0.050641 | 0.04044 | 0.05131 | -63.1258 | -17.0722 | -65.5557 | 57.1629 | 56.9713 | 57.0769 | -66.0087 | -65.3371 | -16.6204 | -65.5685 | 57.0959 | 57.1867 | 57.08 | -66.1403 | -0.067872 | -0.0209 | 2.8151 | 0.3852 | 0.45308 | -0.2125 | -0.10695 | -0.19947 | -0.087908 | 0.60371 | 0.37232 | 0.57179 | 0.002878 | -0.10381 | 123.1038 | 122.9122 | 123.0177 | 48.8687 | -123.1926 | 123.0368 | 123.1276 | 123.0209 | 49.3205 | -123.3242
465.2812 | 123.2849 | -65.9409 | 57.2067 | 0.041851 | -0.051302 | -0.0064519 | 0.049112 | -0.011542 | 0.047919 | 0.074154 | -0.0061157 | -0.0066297 | 0.052777 | 0.039372 | 0.050242 | -63.08 | -17.4202 | -65.5144 | 57.1675 | 56.9897 | 57.1044 | -65.9813 | -65.2914 | -17.0095 | -65.5227 | 57.1234 | 57.2096 | 57.0846 | -66.122 | -0.040398 | -0.03921 | 2.8609 | 0.42641 | 0.46681 | -0.21707 | -0.10237 | -0.18115 | -0.083325 | 0.6495 | 0.41811 | 0.59927 | 0.002883 | -0.12212 | 123.1084 | 122.9305 | 123.0452 | 48.5207 | -123.188 | 123.0643 | 123.1505 | 123.0255 | 48.9313 | -123.3287
466.2812 | 123.2941 | -65.8539 | 57.2159 | 0.057113 | -0.051302 | -0.0064519 | 0.046976 | -0.011542 | 0.04685 | 0.058893 | -0.0093207 | -0.0066297 | 0.051709 | 0.037235 | 0.050242 | -63.0388 | -17.6995 | -65.4732 | 57.2087 | 57.0171 | 57.1227 | -65.9584 | -65.241 | -17.4125 | -65.477 | 57.1463 | 57.2371 | 57.1121 | -66.09 | -0.10448 | -0.007159 | 2.8151 | 0.38064 | 0.48512 | -0.19875 | -0.093207 | -0.23608 | -0.069587 | 0.61289 | 0.37692 | 0.613 | 0.0212 | -0.1038 | 123.0626 | 122.871 | 122.9766 | 48.1544 | -123.1742 | 123.0002 | 123.091 | 122.966 | 48.4414 | -123.3058
467.2812 | 123.2803 | -65.8539 | 57.3029 | 0.041851 | -0.052371 | -0.0064519 | 0.050181 | -0.01261 | 0.04685 | 0.058893 | -0.0071847 | -0.0066297 | 0.051709 | 0.037235 | 0.05131 | -62.9701 | -18.0337 | -65.4229 | 57.2316 | 57.0538 | 57.1593 | -65.9309 | -65.1815 | -17.8749 | -65.422 | 57.1738 | 57.2691 | 57.1487 | -66.0671 | -0.077005 | -0.071242 | 2.8838 | 0.431 | 0.508 | -0.2491 | -0.14355 | -0.21318 | -0.12909 | 0.67242 | 0.43187 | 0.64505 | -0.033725 | -0.15415 | 123.0855 | 122.9076 | 123.0132 | 47.8202 | -123.2337 | 123.0276 | 123.123 | 123.0026 | 47.979 | -123.3699
468.2812 | 123.3353 | -65.7898 | 57.3486 | 0.057113 | -0.052371 | -0.0064519 | 0.045907 | -0.011542 | 0.048987 | 0.089415 | -0.0082527 | -0.0076977 | 0.051709 | 0.039372 | 0.050242 | -62.906 | -18.3817 | -65.3725 | 57.2637 | 57.0858 | 57.1914 | -65.8988 | -65.1174 | -18.2962 | -65.3625 | 57.2195 | 57.3012 | 57.1808 | -66.0259 | -0.10904 | -0.084971 | 2.8838 | 0.41727 | 0.52631 | -0.26282 | -0.15728 | -0.23606 | -0.12908 | 0.67243 | 0.42731 | 0.66337 | -0.047452 | -0.16787 | 123.0535 | 122.8756 | 122.9811 | 47.4081 | -123.2475 | 123.0093 | 123.091 | 122.9706 | 47.4936 | -123.3745
469.2969 | 123.381 | -65.712 | 57.3486 | 0.072375 | -0.050234 | -0.0064519 | 0.046976 | -0.011542 | 0.047919 | 0.074154 | -0.0061157 | -0.0087667 | 0.052777 | 0.039372 | 0.050242 | -62.8831 | -18.748 | -65.3038 | 57.3094 | 57.1362 | 57.2371 | -65.8302 | -65.0441 | -18.6579 | -65.2892 | 57.2562 | 57.3561 | 57.2311 | -65.9709 | -0.11818 | -0.039187 | 2.8289 | 0.40813 | 0.5263 | -0.21245 | -0.11149 | -0.25893 | -0.092456 | 0.66787 | 0.42274 | 0.68168 | 0.007491 | -0.11751 | 123.0214 | 122.8482 | 122.9491 | 46.964 | -123.1788 | 122.9682 | 123.0681 | 122.9431 | 47.0541 | -123.3195
470.2812 | 123.2574 | -65.744 | 57.431 | 0.057113 | -0.053439 | -0.0064519 | 0.049112 | -0.013679 | 0.047919 | 0.074154 | -0.0050477 | -0.0055617 | 0.052777 | 0.039372 | 0.049174 | -62.7183 | -19.2013 | -65.226 | 57.3598 | 57.1774 | 57.2829 | -65.8027 | -64.9663 | -19.1066 | -65.2114 | 57.3111 | 57.3928 | 57.2769 | -65.9343 | -0.058658 | -0.071221 | 3.0257 | 0.518 | 0.57666 | -0.25364 | -0.14811 | -0.19026 | -0.11991 | 0.77775 | 0.53263 | 0.72289 | -0.038277 | -0.15412 | 123.1038 | 122.9214 | 123.0269 | 46.5428 | -123.2337 | 123.0551 | 123.1368 | 123.0209 | 46.6374 | -123.3653
471.3125 | 123.2758 | -65.6662 | 57.4997 | 0.087637 | -0.052371 | -0.0075209 | 0.048044 | -0.010474 | 0.047919 | 0.074154 | -0.0071847 | -0.0055617 | 0.051709 | 0.04044 | 0.049174 | -62.613 | -19.6362 | -65.1619 | 57.4193 | 57.2323 | 57.3424 | -65.7569 | -64.8747 | -19.5965 | -65.1244 | 57.3661 | 57.4477 | 57.3227 | -65.8748 | -0.090689 | -0.080367 | 3.0532 | 0.50428 | 0.59497 | -0.26736 | -0.15725 | -0.20855 | -0.13363 | 0.79151 | 0.5418 | 0.75036 | -0.051999 | -0.177 | 123.0855 | 122.8985 | 123.0086 | 46.03 | -123.2566 | 123.0323 | 123.1139 | 122.9889 | 46.0697 | -123.3744
472.2812 | 123.2483 | -65.6342 | 57.4997 | 0.087637 | -0.054507 | -0.0075209 | 0.049112 | -0.0094052 | 0.04685 | 0.074154 | -0.0082527 | -0.0044937 | 0.051709 | 0.04044 | 0.05131 | -62.5489 | -20.0391 | -65.0978 | 57.4605 | 57.2735 | 57.3791 | -65.6882 | -64.8014 | -20.1368 | -65.0557 | 57.4073 | 57.4889 | 57.3868 | -65.8381 | -0.054049 | -0.039162 | 3.0853 | 0.53633 | 0.59038 | -0.22615 | -0.12062 | -0.20397 | -0.092427 | 0.83272 | 0.57844 | 0.78241 | -0.010791 | -0.1129 | 123.0947 | 122.9077 | 123.0132 | 45.595 | -123.1879 | 123.0414 | 123.1231 | 123.021 | 45.4973 | -123.3378
473.3125 | 123.3902 | -65.5609 | 57.518 | 0.057113 | -0.053439 | -0.0053839 | 0.046976 | -0.010474 | 0.047919 | 0.074154 | -0.0071847 | -0.0076977 | 0.052777 | 0.04044 | 0.050242 | -62.4894 | -20.5062 | -65.0108 | 57.5155 | 57.3331 | 57.434 | -65.6516 | -64.7053 | -20.3657 | -64.9687 | 57.4576 | 57.5438 | 57.4326 | -65.7832 | -0.090659 | -0.002531 | 3.0715 | 0.55008 | 0.64074 | -0.18493 | -0.083986 | -0.22227 | -0.060374 | 0.85563 | 0.59219 | 0.81446 | 0.025842 | -0.085422 | 123.0764 | 122.894 | 122.9949 | 45.0548 | -123.1696 | 123.0185 | 123.1048 | 122.9935 | 45.1952 | -123.3012
474.2812 | 123.2483 | -65.5151 | 57.6462 | 0.041851 | -0.052371 | -0.0053839 | 0.048044 | -0.01261 | 0.047919 | 0.074154 | -0.0071847 | -0.0066297 | 0.052777 | 0.039372 | 0.05131 | -62.3612 | -20.9228 | -64.9284 | 57.5704 | 57.3926 | 57.4844 | -65.5966 | -64.6137 | -20.6176 | -64.8817 | 57.5126 | 57.5988 | 57.5013 | -65.7191 | -0.081488 | -0.075765 | 3.154 | 0.58671 | 0.6682 | -0.25358 | -0.16179 | -0.20394 | -0.13361 | 0.90143 | 0.63341 | 0.83735 | -0.047389 | -0.14492 | 123.0856 | 122.9077 | 122.9995 | 44.5923 | -123.2428 | 123.0277 | 123.1139 | 123.0164 | 44.8976 | -123.3653
475.2812 | 123.2712 | -65.4419 | 57.7011 | 0.041851 | -0.052371 | -0.0053839 | 0.050181 | -0.013679 | 0.04685 | 0.058893 | -0.0071847 | -0.0055617 | 0.052777 | 0.039372 | 0.050242 | -62.2513 | -21.4081 | -64.8414 | 57.6299 | 57.443 | 57.5576 | -65.5234 | -64.5221 | -20.9839 | -64.7856 | 57.5767 | 57.6675 | 57.5608 | -65.6687 | -0.081468 | -0.071178 | 3.1906 | 0.60045 | 0.68192 | -0.25814 | -0.14347 | -0.22681 | -0.12444 | 0.91976 | 0.65632 | 0.88314 | -0.033642 | -0.14033 | 123.0718 | 122.8849 | 122.9995 | 44.0338 | -123.2245 | 123.0186 | 123.1094 | 123.0027 | 44.458 | -123.3698
476.2812 | 123.3215 | -65.387 | 57.7698 | 0.057113 | -0.052371 | -0.0075209 | 0.048044 | -0.011542 | 0.045782 | 0.074154 | -0.0061157 | -0.0055617 | 0.050641 | 0.041509 | 0.05131 | -62.1368 | -21.8111 | -64.7499 | 57.6986 | 57.5162 | 57.6217 | -65.473 | -64.4122 | -21.2403 | -64.6711 | 57.6454 | 57.7361 | 57.634 | -65.5954 | -0.086031 | -0.071166 | 3.2501 | 0.63709 | 0.72312 | -0.25355 | -0.14803 | -0.20848 | -0.12443 | 0.97472 | 0.71586 | 0.92434 | -0.033627 | -0.13573 | 123.0856 | 122.9032 | 123.0087 | 43.5759 | -123.2428 | 123.0323 | 123.1231 | 123.021 | 44.1467 | -123.3652
477.2812 | 123.2712 | -65.2908 | 57.8522 | 0.041851 | -0.054507 | -0.0075209 | 0.050181 | -0.011542 | 0.047919 | 0.058893 | -0.0071847 | -0.0066297 | 0.051709 | 0.042577 | 0.05131 | -62.0041 | -22.2598 | -64.6308 | 57.7856 | 57.6032 | 57.7042 | -65.3906 | -64.284 | -21.4875 | -64.5429 | 57.7323 | 57.8186 | 57.7119 | -65.5176 | -0.099741 | -0.066574 | 3.2868 | 0.65999 | 0.75974 | -0.24894 | -0.14802 | -0.22677 | -0.11983 | 1.0068 | 0.74793 | 0.97471 | -0.03361 | -0.1403 | 123.0764 | 122.8941 | 122.995 | 43.0311 | -123.2427 | 123.0232 | 123.1094 | 123.0027 | 43.8033 | -123.3698
478.2812 | 123.381 | -65.2039 | 57.843 | 0.057113 | -0.053439 | -0.0043149 | 0.048044 | -0.01261 | 0.047919 | 0.058893 | -0.0071847 | -0.0055617 | 0.051709 | 0.04044 | 0.05131 | -61.9491 | -22.6947 | -64.5439 | 57.836 | 57.649 | 57.7499 | -65.3265 | -64.1833 | -21.6753 | -64.4513 | 57.7827 | 57.8827 | 57.7714 | -65.4627 | -0.12261 | -0.007057 | 3.2547 | 0.66 | 0.78262 | -0.194 | -0.093075 | -0.2588 | -0.060314 | 1.0206 | 0.75253 | 1.0113 | 0.039646 | -0.071618 | 123.0398 | 122.8529 | 122.9538 | 42.5091 | -123.1695 | 122.9866 | 123.0865 | 122.9753 | 43.5286 | -123.3057
479.2812 | 123.2986 | -65.1443 | 57.9803 | 0.072375 | -0.053439 | -0.0064519 | 0.048044 | -0.011542 | 0.048987 | 0.074154 | -0.0082527 | -0.0066297 | 0.053846 | 0.041509 | 0.050242 | -61.766 | -23.0793 | -64.4294 | 57.9184 | 57.736 | 57.8507 | -65.244 | -64.0551 | -21.8721 | -64.3094 | 57.8697 | 57.9559 | 57.8401 | -65.3711 | -0.0997 | -0.061975 | 3.3784 | 0.71495 | 0.81465 | -0.24433 | -0.12967 | -0.22674 | -0.11065 | 1.0892 | 0.83496 | 1.0617 | -0.024426 | -0.14027 | 123.0627 | 122.8804 | 122.995 | 42.065 | -123.2244 | 123.014 | 123.1003 | 122.9844 | 43.2722 | -123.3514
480.2812 | 123.2712 | -65.0986 | 58.0353 | 0.072375 | -0.054507 | -0.0043149 | 0.050181 | -0.01261 | 0.047919 | 0.074154 | -0.0082527 | -0.0055617 | 0.049573 | 0.041509 | 0.052379 | -61.6332 | -23.4822 | -64.3195 | 57.9916 | 57.8139 | 57.9194 | -65.1662 | -63.9406 | -22.0782 | -64.2041 | 57.9338 | 58.0338 | 57.9133 | -65.3024 | -0.067634 | -0.043652 | 3.4654 | 0.77906 | 0.84669 | -0.22142 | -0.11593 | -0.20383 | -0.10148 | 1.1579 | 0.8945 | 1.0983 | -0.00152 | -0.12194 | 123.0902 | 122.9124 | 123.0179 | 41.6163 | -123.2015 | 123.0324 | 123.1323 | 123.0119 | 43.0204 | -123.3377
481.2812 | 123.3078 | -65.0116 | 58.1406 | 0.057113 | -0.054507 | -0.0085889 | 0.049112 | -0.013679 | 0.045782 | 0.074154 | -0.0071847 | -0.0076977 | 0.049573 | 0.041509 | 0.05131 | -61.4913 | -23.789 | -64.2096 | 58.074 | 57.8871 | 58.0018 | -65.0884 | -63.8079 | -22.5864 | -64.0576 | 58.0208 | 58.0979 | 57.9774 | -65.2154 | -0.076768 | -0.066527 | 3.5203 | 0.80196 | 0.87873 | -0.25344 | -0.1388 | -0.20381 | -0.11978 | 1.2037 | 0.95404 | 1.1578 | -0.042706 | -0.16313 | 123.0856 | 122.8987 | 123.0134 | 41.2226 | -123.2289 | 123.0324 | 123.1095 | 122.989 | 42.4252 | -123.356
482.2812 | 123.2895 | -64.9429 | 58.2596 | 0.072375 | -0.053439 | -0.0064519 | 0.049112 | -0.011542 | 0.04685 | 0.074154 | -0.0061157 | -0.0066297 | 0.051709 | 0.041509 | 0.050242 | -61.3677 | -24.1599 | -64.0998 | 58.1427 | 57.965 | 58.075 | -65.0288 | -63.6796 | -22.9573 | -63.9202 | 58.0895 | 58.1803 | 58.069 | -65.1559 | -0.085907 | -0.11687 | 3.5753 | 0.84317 | 0.92908 | -0.29462 | -0.18456 | -0.21295 | -0.17012 | 1.2633 | 1.0227 | 1.2357 | -0.07931 | -0.19057 | 123.0856 | 122.9079 | 123.018 | 40.7831 | -123.2884 | 123.0324 | 123.1232 | 123.0119 | 41.9856 | -123.4155
483.3125 | 123.262 | -64.8193 | 58.3511 | 0.041851 | -0.053439 | -0.0053839 | 0.048044 | -0.010474 | 0.04685 | 0.043632 | -0.0071847 | -0.0066297 | 0.048504 | 0.042577 | 0.05131 | -61.2074 | -24.4575 | -63.9624 | 58.2389 | 58.0657 | 58.1712 | -64.9052 | -63.524 | -23.2961 | -63.7737 | 58.1902 | 58.281 | 58.1514 | -65.0506 | -0.085872 | -0.11228 | 3.6119 | 0.85693 | 0.9428 | -0.28543 | -0.17996 | -0.23123 | -0.16094 | 1.2954 | 1.0457 | 1.2769 | -0.070133 | -0.19971 | 123.0582 | 122.885 | 122.9905 | 40.3618 | -123.2563 | 123.0095 | 123.1003 | 122.9708 | 41.5232 | -123.4017
484.2812 | 123.2712 | -64.7461 | 58.4244 | 0.072375 | -0.054507 | -0.0053839 | 0.050181 | -0.01261 | 0.047919 | 0.089415 | -0.0071847 | -0.0076977 | 0.050641 | 0.041509 | 0.05131 | -61.0563 | -24.7459 | -63.8342 | 58.3304 | 58.1481 | 58.2536 | -64.8274 | -63.3683 | -23.5983 | -63.618 | 58.2909 | 58.3726 | 58.2567 | -64.9636 | -0.081272 | -0.09395 | 3.6898 | 0.91188 | 0.99315 | -0.27625 | -0.17079 | -0.21748 | -0.13346 | 1.3778 | 1.1281 | 1.3456 | -0.051803 | -0.16765 | 123.0765 | 122.8942 | 122.9997 | 40.0002 | -123.2517 | 123.037 | 123.1187 | 123.0028 | 41.1478 | -123.3879
485.2812 | 123.2574 | -64.6362 | 58.4976 | 0.041851 | -0.053439 | -0.0075209 | 0.049112 | -0.011542 | 0.047919 | 0.089415 | -0.0082527 | -0.0066297 | 0.051709 | 0.039372 | 0.050242 | -60.8778 | -25.158 | -63.7106 | 58.4174 | 58.2351 | 58.3406 | -64.7358 | -63.2355 | -24.0287 | -63.4715 | 58.3688 | 58.4596 | 58.3346 | -64.8766 | -0.099558 | -0.080204 | 3.7585 | 0.92562 | 1.0252 | -0.2625 | -0.15704 | -0.24034 | -0.12887 | 1.4007 | 1.1647 | 1.4051 | -0.038052 | -0.16305 | 123.0536 | 122.8714 | 122.9768 | 39.4782 | -123.2334 | 123.005 | 123.0958 | 122.9708 | 40.6075 | -123.3742
486.2812 | 123.2574 | -64.5538 | 58.6349 | 0.087637 | -0.054507 | -0.0053839 | 0.046976 | -0.010474 | 0.050055 | 0.058893 | -0.0082527 | -0.0076977 | 0.052777 | 0.041509 | 0.05131 | -60.6717 | -25.4923 | -63.5641 | 58.5136 | 58.3359 | 58.4367 | -64.6534 | -63.0753 | -24.3446 | -63.325 | 58.4603 | 58.5466 | 58.4399 | -64.7804 | -0.099534 | -0.12139 | 3.8821 | 0.98973 | 1.0893 | -0.29909 | -0.19822 | -0.22658 | -0.17463 | 1.4786 | 1.2289 | 1.4555 | -0.088388 | -0.19507 | 123.0674 | 122.8897 | 122.9906 | 39.0616 | -123.2883 | 123.0142 | 123.1004 | 122.9937 | 40.2092 | -123.4154
487.2812 | 123.2529 | -64.4485 | 58.7265 | 0.057113 | -0.053439 | -0.0064519 | 0.048044 | -0.011542 | 0.047919 | 0.058893 | -0.0082527 | -0.0076977 | 0.052777 | 0.041509 | 0.050242 | -60.4428 | -25.6846 | -63.3947 | 58.6372 | 58.4503 | 58.5558 | -64.5297 | -62.9058 | -24.7064 | -63.1418 | 58.5794 | 58.6748 | 58.5406 | -64.6614 | -0.081189 | -0.089322 | 4.0057 | 1.0538 | 1.135 | -0.27617 | -0.17072 | -0.21282 | -0.14714 | 1.5427 | 1.3067 | 1.5196 | -0.051739 | -0.1859 | 123.0857 | 122.8989 | 123.0043 | 38.764 | -123.2562 | 123.0279 | 123.1233 | 122.9892 | 39.7422 | -123.3879
488.2812 | 123.2758 | -64.3112 | 58.8455 | 0.057113 | -0.054507 | -0.0064519 | 0.048044 | -0.010474 | 0.047919 | 0.074154 | -0.0050477 | -0.0076977 | 0.052777 | 0.041509 | 0.050242 | -60.2505 | -25.9593 | -63.2345 | 58.7516 | 58.5648 | 58.6794 | -64.3878 | -62.6998 | -25.0086 | -62.9358 | 58.6984 | 58.7984 | 58.678 | -64.5332 | -0.076571 | -0.093882 | 4.0607 | 1.0768 | 1.1533 | -0.28072 | -0.16612 | -0.22194 | -0.14712 | 1.6114 | 1.3754 | 1.5974 | -0.047136 | -0.16756 | 123.0629 | 122.876 | 122.9906 | 38.3519 | -123.2333 | 123.0096 | 123.1096 | 122.9892 | 39.3027 | -123.3787
489.2812 | 123.2529 | -64.2654 | 58.9142 | 0.041851 | -0.054507 | -0.0053839 | 0.048044 | -0.011542 | 0.047919 | 0.074154 | -0.0071847 | -0.0055617 | 0.051709 | 0.042577 | 0.05131 | -60.1178 | -26.2111 | -63.1337 | 58.802 | 58.6152 | 58.7252 | -64.3603 | -62.5945 | -25.3016 | -62.8167 | 58.7442 | 58.8442 | 58.7329 | -64.4874 | -0.094874 | -0.11218 | 4.1477 | 1.1317 | 1.2266 | -0.29901 | -0.189 | -0.22193 | -0.17 | 1.6709 | 1.4487 | 1.6706 | -0.070015 | -0.18128 | 123.0674 | 122.8806 | 122.9906 | 38.0543 | -123.2745 | 123.0096 | 123.1096 | 122.9983 | 38.9638 | -123.4016
490.2812 | 123.3353 | -64.1281 | 58.9737 | 0.072375 | -0.053439 | -0.0075209 | 0.048044 | -0.010474 | 0.048987 | 0.058893 | -0.0061157 | -0.0055617 | 0.050641 | 0.041509 | 0.049174 | -59.9346 | -26.408 | -62.9735 | 58.921 | 58.7342 | 58.8488 | -64.2458 | -62.4068 | -25.3611 | -62.6198 | 58.8678 | 58.9632 | 58.8336 | -64.3683 | -0.11773 | -0.052655 | 4.1935 | 1.1546 | 1.2723 | -0.23947 | -0.12489 | -0.24021 | -0.10589 | 1.7213 | 1.5083 | 1.7485 | -0.01048 | -0.14006 | 123.0492 | 122.8623 | 122.9769 | 37.7201 | -123.2195 | 122.9959 | 123.0913 | 122.9617 | 38.767 | -123.342
491.2812 | 123.3627 | -63.9908 | 59.1019 | 0.057113 | -0.055576 | -0.0064519 | 0.049112 | -0.011542 | 0.048987 | 0.058893 | -0.0061157 | -0.0066297 | 0.051709 | 0.042577 | 0.049174 | -59.7194 | -26.5865 | -62.8133 | 59.0218 | 58.8533 | 58.9495 | -64.1222 | -62.2236 | -25.4344 | -62.4367 | 58.9868 | 59.0639 | 58.9573 | -64.263 | -0.13143 | -0.080105 | 4.2713 | 1.1775 | 1.309 | -0.24859 | -0.15233 | -0.27223 | -0.11502 | 1.7672 | 1.5541 | 1.8263 | -0.037925 | -0.14461 | 123.0125 | 122.8441 | 122.9403 | 37.4042 | -123.2241 | 122.9776 | 123.0547 | 122.948 | 38.5564 | -123.3649
492.2812 | 123.3353 | -63.8947 | 59.2346 | 0.072375 | -0.056644 | -0.0075209 | 0.049112 | -0.01261 | 0.04685 | 0.074154 | -0.0061157 | -0.0066297 | 0.051709 | 0.042577 | 0.05131 | -59.5134 | -26.7331 | -62.6851 | 59.1179 | 58.9265 | 59.0365 | -64.0581 | -62.0771 | -25.8465 | -62.2673 | 59.0647 | 59.1418 | 59.0351 | -64.1806 | -0.16345 | -0.11671 | 4.3812 | 1.2096 | 1.373 | -0.30808 | -0.19809 | -0.28594 | -0.16994 | 1.8176 | 1.6274 | 1.9133 | -0.09284 | -0.19953 | 123.0126 | 122.8212 | 122.9312 | 37.1616 | -123.2927 | 122.9593 | 123.0364 | 122.9297 | 38.0482 | -123.4152
493.2812 | 123.3673 | -63.858 | 59.2346 | 0.057113 | -0.054507 | -0.0075209 | 0.046976 | -0.011542 | 0.050055 | 0.10468 | -0.0071847 | -0.0066297 | 0.052777 | 0.042577 | 0.050242 | -59.344 | -26.9849 | -62.5615 | 59.1683 | 58.9998 | 59.1052 | -63.9803 | -61.926 | -25.8877 | -62.1208 | 59.1196 | 59.215 | 59.09 | -64.1165 | -0.12223 | -0.066347 | 4.514 | 1.2966 | 1.4188 | -0.23482 | -0.12941 | -0.25846 | -0.11499 | 1.932 | 1.7373 | 1.9957 | -0.019582 | -0.14458 | 123.0263 | 122.8578 | 122.9632 | 36.8732 | -123.2149 | 122.9777 | 123.0731 | 122.9481 | 37.9704 | -123.3511
494.2812 | 123.2941 | -63.8077 | 59.3079 | 0.057113 | -0.055576 | -0.0043149 | 0.048044 | -0.011542 | 0.047919 | 0.089415 | -0.0071847 | -0.0055617 | 0.052777 | 0.042577 | 0.050242 | -59.1197 | -26.9803 | -62.415 | 59.2598 | 59.0822 | 59.1922 | -63.8887 | -61.7474 | -26.1212 | -61.9468 | 59.2066 | 59.2975 | 59.177 | -64.0341 | -0.081008 | -0.048021 | 4.688 | 1.3927 | 1.4737 | -0.22564 | -0.11566 | -0.22639 | -0.10125 | 2.0602 | 1.8609 | 2.0873 | -0.010409 | -0.13083 | 123.0675 | 122.8899 | 122.9999 | 36.8274 | -123.1965 | 123.0143 | 123.1051 | 122.9847 | 37.6865 | -123.3419
495.2812 | 123.3032 | -63.6795 | 59.4452 | 0.072375 | -0.054507 | -0.0053839 | 0.049112 | -0.011542 | 0.047919 | 0.058893 | -0.0071847 | -0.0055617 | 0.051709 | 0.042577 | 0.050242 | -58.8908 | -26.9803 | -62.2639 | 59.3697 | 59.1875 | 59.2975 | -63.7925 | -61.5551 | -26.1761 | -61.7499 | 59.3165 | 59.4073 | 59.3007 | -63.9288 | -0.11303 | -0.075469 | 4.7887 | 1.4156 | 1.5287 | -0.25765 | -0.14768 | -0.24925 | -0.12869 | 2.1244 | 1.9296 | 2.1789 | -0.037852 | -0.14454 | 123.0492 | 122.867 | 122.977 | 36.6992 | -123.2377 | 122.996 | 123.0868 | 122.9802 | 37.5034 | -123.3739
496.2812 | 123.349 | -63.5605 | 59.5367 | 0.026589 | -0.056644 | -0.0053839 | 0.048044 | -0.01261 | 0.047919 | 0.043632 | -0.0082527 | -0.0055617 | 0.052777 | 0.042577 | 0.052379 | -58.6618 | -26.9895 | -62.0807 | 59.475 | 59.2929 | 59.3937 | -63.6689 | -61.3537 | -26.3364 | -61.5484 | 59.4218 | 59.5126 | 59.3922 | -63.8143 | -0.10841 | -0.061719 | 4.8986 | 1.4797 | 1.5882 | -0.24389 | -0.14308 | -0.2538 | -0.11494 | 2.2068 | 2.0121 | 2.2659 | -0.024097 | -0.14452 | 123.0355 | 122.8533 | 122.9541 | 36.571 | -123.2056 | 122.9823 | 123.0731 | 122.9527 | 37.2241 | -123.351
497.2812 | 123.381 | -63.4598 | 59.61 | 0.041851 | -0.054507 | -0.0053839 | 0.049112 | -0.011542 | 0.050055 | 0.058893 | -0.0093207 | -0.0076977 | 0.051709 | 0.043646 | 0.053447 | -58.4879 | -27.0078 | -61.9571 | 59.5437 | 59.3615 | 59.4761 | -63.6002 | -61.1705 | -26.5241 | -61.3699 | 59.4996 | 59.5859 | 59.4746 | -63.7364 | -0.14044 | -0.066285 | 4.9719 | 1.5027 | 1.6431 | -0.24845 | -0.13391 | -0.27667 | -0.11035 | 2.2893 | 2.0899 | 2.3666 | -0.024081 | -0.13535 | 123.0035 | 122.8213 | 122.9359 | 36.452 | -123.2102 | 122.9594 | 123.0457 | 122.9344 | 36.9357 | -123.3464
498.2812 | 123.4314 | -63.3179 | 59.7656 | 0.072375 | -0.056644 | -0.0053839 | 0.049112 | -0.01261 | 0.048987 | 0.089415 | -0.0082527 | -0.0055617 | 0.052777 | 0.043646 | 0.05131 | -58.2727 | -27.0536 | -61.8015 | 59.6353 | 59.4531 | 59.5585 | -63.5132 | -60.9416 | -26.8034 | -61.1775 | 59.5821 | 59.6729 | 59.5525 | -63.6586 | -0.19534 | -0.13036 | 5.0452 | 1.5164 | 1.7118 | -0.31251 | -0.20713 | -0.34074 | -0.18357 | 2.3763 | 2.1403 | 2.4811 | -0.092728 | -0.21315 | 122.9531 | 122.771 | 122.8764 | 36.2643 | -123.2788 | 122.8999 | 122.9908 | 122.8703 | 36.5145 | -123.4242
499.2812 | 123.5001 | -63.1805 | 59.903 | 0.072375 | -0.054507 | -0.0075209 | 0.048044 | -0.01261 | 0.050055 | 0.058893 | -0.0061157 | -0.0044937 | 0.052777 | 0.044714 | 0.05131 | -57.9201 | -26.7926 | -61.5451 | 59.8276 | 59.6363 | 59.7416 | -63.3346 | -60.4974 | -27.2384 | -60.8891 | 59.7743 | 59.8515 | 59.7448 | -63.4663 | -0.15409 | -0.075394 | 5.2604 | 1.6355 | 1.7896 | -0.26668 | -0.16132 | -0.28575 | -0.1286 | 2.6831 | 2.2915 | 2.5772 | -0.051491 | -0.15818 | 123.0081 | 122.8168 | 122.9222 | 36.388 | -123.2376 | 122.9549 | 123.032 | 122.9253 | 35.9422 | -123.3692
500.2812 | 123.3719 | -63.1668 | 59.9121 | 0.072375 | -0.056644 | -0.0075209 | 0.049112 | -0.010474 | 0.050055 | 0.089415 | -0.0082527 | -0.0055617 | 0.053846 | 0.043646 | 0.05131 | -57.6821 | -26.5865 | -61.3848 | 59.91 | 59.7187 | 59.8378 | -63.2476 | -60.3738 | -27.1056 | -60.6739 | 59.8522 | 59.9385 | 59.8364 | -63.3747 | -0.080828 | -0.002138 | 5.4847 | 1.782 | 1.8628 | -0.19342 | -0.074323 | -0.20791 | -0.059925 | 2.793 | 2.4929 | 2.7008 | 0.026347 | -0.075759 | 123.0768 | 122.8855 | 123.0046 | 36.5803 | -123.1597 | 123.019 | 123.1053 | 123.0032 | 36.0612 | -123.2868
501.2812 | 123.3856 | -62.9517 | 60.1318 | 0.072375 | -0.056644 | -0.0064519 | 0.048044 | -0.01261 | 0.048987 | 0.074154 | -0.0093207 | -0.0055617 | 0.052777 | 0.044714 | 0.052379 | -57.3845 | -26.4492 | -61.1788 | 60.0519 | 59.8606 | 59.9706 | -63.1148 | -60.035 | -27.9069 | -60.4175 | 59.9987 | 60.0804 | 59.9691 | -63.2419 | -0.16319 | -0.079935 | 5.5672 | 1.7728 | 1.936 | -0.2712 | -0.16127 | -0.29027 | -0.13314 | 2.9167 | 2.5342 | 2.8245 | -0.051443 | -0.16271 | 123.0036 | 122.8123 | 122.9222 | 36.5025 | -123.2467 | 122.9504 | 123.0321 | 122.9208 | 35.0448 | -123.3738
502.2812 | 123.349 | -62.7594 | 60.347 | 0.057113 | -0.054507 | -0.0053839 | 0.049112 | -0.011542 | 0.047919 | 0.10468 | -0.0061157 | -0.0044937 | 0.053846 | 0.045782 | 0.052379 | -57.009 | -26.2019 | -60.8812 | 60.2717 | 60.0896 | 60.1858 | -62.8951 | -59.6046 | -28.2686 | -60.0603 | 60.2139 | 60.3139 | 60.1981 | -63.0176 | -0.13566 | -0.075322 | 5.7504 | 1.8782 | 2.0138 | -0.2574 | -0.16123 | -0.25817 | -0.1331 | 3.1548 | 2.6991 | 2.9572 | -0.033083 | -0.14893 | 123.0311 | 122.849 | 122.9452 | 36.5575 | -123.242 | 122.9733 | 123.0733 | 122.9575 | 34.4908 | -123.3646
503.2812 | 123.3948 | -62.6678 | 60.3928 | 0.057113 | -0.055576 | -0.0043149 | 0.048044 | -0.011542 | 0.047919 | 0.074154 | -0.0061157 | -0.0055617 | 0.051709 | 0.044714 | 0.05131 | -56.7801 | -26.2889 | -60.7347 | 60.3312 | 60.1491 | 60.259 | -62.831 | -59.3436 | -28.4792 | -59.8635 | 60.278 | 60.378 | 60.2667 | -62.9535 | -0.16311 | -0.061579 | 5.8877 | 1.9331 | 2.0962 | -0.24365 | -0.13374 | -0.28562 | -0.11478 | 3.3242 | 2.8044 | 3.09 | -0.014759 | -0.12602 | 122.999 | 122.817 | 122.9269 | 36.3789 | -123.2237 | 122.9458 | 123.0458 | 122.9346 | 34.1886 | -123.3462
504.2812 | 123.3856 | -62.6129 | 60.5026 | 0.072375 | -0.056644 | -0.0053839 | 0.049112 | -0.011542 | 0.047919 | 0.058893 | -0.0071847 | -0.0034247 | 0.053846 | 0.044714 | 0.05131 | -56.4825 | -26.1287 | -60.5287 | 60.464 | 60.2819 | 60.3826 | -62.6753 | -59.0735 | -28.7494 | -59.5933 | 60.4153 | 60.5062 | 60.3812 | -62.8298 | -0.062356 | -0.038669 | 6.1304 | 2.0842 | 2.1466 | -0.22072 | -0.11999 | -0.21693 | -0.087286 | 3.5394 | 3.0196 | 3.2365 | 0.003578 | -0.12142 | 123.0769 | 122.8948 | 122.9956 | 36.4842 | -123.1779 | 123.0283 | 123.1191 | 122.9941 | 33.8636 | -123.3325
505.2812 | 123.3856 | -62.4756 | 60.5896 | 0.057113 | -0.056644 | -0.0075209 | 0.050181 | -0.011542 | 0.050055 | 0.074154 | -0.0082527 | -0.0034247 | 0.052777 | 0.044714 | 0.053447 | -56.1758 | -26.0051 | -60.3456 | 60.5647 | 60.3826 | 60.4834 | -62.5791 | -58.8125 | -30.9242 | -59.3369 | 60.5069 | 60.6069 | 60.4865 | -62.7199 | -0.10353 | -0.02492 | 6.2998 | 2.13 | 2.2335 | -0.20696 | -0.10623 | -0.24436 | -0.082691 | 3.6631 | 3.1387 | 3.383 | 0.017332 | -0.10309 | 123.0403 | 122.8582 | 122.959 | 36.4705 | -123.1687 | 122.9825 | 123.0825 | 122.9621 | 31.5513 | -123.3095
506.2812 | 123.3856 | -62.3566 | 60.7498 | 0.057113 | -0.056644 | -0.0053839 | 0.048044 | -0.011542 | 0.050055 | 0.058893 | -0.0061157 | -0.0055617 | 0.052777 | 0.045782 | 0.054515 | -55.8736 | -25.8219 | -60.1624 | 60.6562 | 60.4788 | 60.5749 | -62.5013 | -58.579 | -32.3757 | -59.0942 | 60.5985 | 60.6985 | 60.5781 | -62.6375 | -0.14471 | -0.093569 | 6.483 | 2.1941 | 2.3388 | -0.27102 | -0.17488 | -0.28096 | -0.15134 | 3.7776 | 3.2623 | 3.5433 | -0.051313 | -0.17173 | 123.0128 | 122.8354 | 122.9315 | 36.5347 | -123.2511 | 122.955 | 123.0551 | 122.9347 | 29.9809 | -123.3873
507.2812 | 123.3444 | -61.3403 | 61.7523 | 0.057113 | -0.056644 | -0.0053839 | 0.049112 | -0.010474 | 0.047919 | 0.043632 | -0.0071847 | -0.0034247 | 0.053846 | 0.046851 | 0.054515 | -55.3791 | -25.5655 | -59.787 | 60.9447 | 60.7673 | 60.8588 | -62.1991 | -58.4691 | -33.3968 | -58.2151 | 60.8915 | 60.9778 | 60.8757 | -62.3353 | -0.85873 | -0.80763 | 5.9612 | 1.5533 | 2.412 | -0.98505 | -0.8935 | -0.995 | -0.86082 | 2.8713 | 3.1252 | 4.1202 | -0.77452 | -0.87663 | 122.285 | 122.1076 | 122.1991 | 35.7748 | -123.9514 | 122.2318 | 122.3181 | 122.216 | 27.9436 | -124.0876
508.2812 | 123.4085 | -60.6766 | 62.3703 | 0.072375 | -0.056644 | -0.0053839 | 0.049112 | -0.011542 | 0.050055 | 0.074154 | -0.0093207 | -0.0055617 | 0.053846 | 0.047919 | 0.053447 | -53.8637 | -24.6132 | -58.3952 | 62.2495 | 62.0677 | 62.1637 | -60.8895 | -57.1367 | -39.3765 | -55.4999 | 62.1964 | 62.2873 | 62.1898 | -61.0304 | -0.21292 | -0.12077 | 6.8129 | 2.2814 | 2.4943 | -0.30262 | -0.20658 | -0.35379 | -0.17393 | 3.5399 | 5.1766 | 5.5304 | -0.083021 | -0.18055 | 122.9261 | 122.7443 | 122.8403 | 36.0634 | -123.2598 | 122.8729 | 122.9639 | 122.8663 | 21.3 | -123.4007
509.3125 | 123.3582 | -60.4568 | 62.59 | 0.057113 | -0.056644 | -0.0032469 | 0.050181 | -0.010474 | 0.050055 | 0.028371 | -0.0071847 | -0.0044937 | 0.052777 | 0.046851 | 0.054515 | -53.209 | -24.3568 | -58.0152 | 62.538 | 62.347 | 62.4567 | -60.6239 | -56.7566 | -40.2373 | -54.8589 | 62.4757 | 62.5712 | 62.4507 | -60.7556 | -0.16707 | -0.052062 | 7.2479 | 2.4416 | 2.6087 | -0.24303 | -0.13328 | -0.29879 | -0.11436 | 3.7002 | 5.5979 | 5.8967 | -0.018874 | -0.13929 | 122.9948 | 122.8038 | 122.9136 | 36.1001 | -123.2139 | 122.9325 | 123.028 | 122.9076 | 20.2195 | -123.3457
510.2812 | 123.3948 | -60.1776 | 62.9242 | 0.072375 | -0.056644 | -0.0043149 | 0.049112 | -0.013679 | 0.048987 | 0.074154 | -0.0061157 | -0.0044937 | 0.052777 | 0.047919 | 0.053447 | -51.9041 | -24.6956 | -57.4292 | 63.0141 | 62.8232 | 62.9238 | -60.1477 | -56.1294 | -39.8344 | -54.1538 | 62.9472 | 63.0382 | 62.9315 | -60.2794 | 0.029907 | 0.089924 | 8.2735 | 2.7484 | 2.7185 | -0.10099 | -0.00043 | -0.10183 | 0.023053 | 4.0483 | 6.0238 | 6.1256 | 0.11398 | 0.007291 | 123.1917 | 123.0008 | 123.1014 | 35.482 | -123.0719 | 123.1249 | 123.2158 | 123.1091 | 20.3432 | -123.2036
511.2812 | 123.3719 | -58.342 | 64.7461 | 0.057113 | -0.057712 | -0.0043149 | 0.050181 | -0.0094052 | 0.051124 | 0.074154 | -0.0061157 | -0.0034247 | 0.054914 | 0.048987 | 0.053447 | -50.7824 | -23.6974 | -55.9596 | 64.2137 | 64.0275 | 64.1188 | -58.9434 | -54.9023 | -46.5148 | -51.782 | 64.1605 | 64.2515 | 64.1402 | -59.0706 | -0.60147 | -0.53244 | 7.5595 | 2.3824 | 2.9839 | -0.71863 | -0.62731 | -0.72865 | -0.58555 | 3.4397 | 6.5599 | 7.2886 | -0.49459 | -0.60586 | 122.5556 | 122.3694 | 122.4608 | 34.6445 | -123.6895 | 122.5025 | 122.5935 | 122.4822 | 11.8272 | -123.8167
512.2812 | 123.3398 | -58.3008 | 64.8148 | 0.041851 | -0.055576 | -0.0043149 | 0.048044 | -0.0094052 | 0.051124 | 0.074154 | -0.0082527 | -0.0034247 | 0.052777 | 0.047919 | 0.053447 | -50.4711 | -23.5967 | -55.1218 | 64.612 | 64.4212 | 64.508 | -58.5497 | -54.3666 | -47.4854 | -51.402 | 64.5451 | 64.6407 | 64.5432 | -58.6814 | -0.24888 | -0.20278 | 7.8297 | 3.179 | 3.4279 | -0.39351 | -0.3068 | -0.38065 | -0.26962 | 3.9342 | 6.8988 | 7.2794 | -0.17408 | -0.2716 | 122.9128 | 122.722 | 122.8087 | 34.7041 | -123.3644 | 122.8459 | 122.9415 | 122.8439 | 10.8153 | -123.4962
513.2812 | 123.3719 | -58.2458 | 64.8285 | 0.057113 | -0.058781 | -0.0053839 | 0.050181 | -0.010474 | 0.050055 | 0.074154 | -0.0082527 | -0.0044937 | 0.054914 | 0.050056 | 0.054515 | -49.9217 | -23.1343 | -54.9752 | 64.7173 | 64.5266 | 64.627 | -58.4398 | -54.1239 | -48.8316 | -51.1868 | 64.6504 | 64.746 | 64.6347 | -58.5761 | -0.19392 | -0.11121 | 8.3242 | 3.2706 | 3.4645 | -0.30193 | -0.20149 | -0.33027 | -0.17804 | 4.122 | 7.059 | 7.3893 | -0.082502 | -0.19377 | 122.9631 | 122.7724 | 122.8729 | 35.1116 | -123.2683 | 122.8963 | 122.9918 | 122.8806 | 9.4143 | -123.4046
514.2812 | 123.3902 | -58.6624 | 64.4257 | 0.072375 | -0.057712 | -0.0032469 | 0.049112 | -0.011542 | 0.054329 | 0.074154 | -0.0061157 | -0.0012887 | 0.053846 | 0.048987 | 0.054515 | -50.1048 | -22.8641 | -55.314 | 64.3739 | 64.1877 | 64.2928 | -58.7878 | -54.2933 | -49.2345 | -51.3058 | 64.3162 | 64.4118 | 64.3096 | -58.915 | -0.12535 | -0.05176 | 8.5576 | 3.3484 | 3.4737 | -0.23794 | -0.13289 | -0.25254 | -0.10944 | 4.3691 | 7.3566 | 7.6091 | -0.013908 | -0.11601 | 123.0363 | 122.8501 | 122.9552 | 35.7983 | -123.2134 | 122.9786 | 123.0742 | 122.9721 | 9.4279 | -123.3406
515.2812 | 123.4039 | -58.5938 | 64.4394 | 0.072375 | -0.056644 | -0.0032469 | 0.050181 | -0.01261 | 0.05326 | 0.074154 | -0.0071847 | -0.0044937 | 0.052777 | 0.047919 | 0.053447 | -49.18 | -22.4566 | -55.1492 | 64.4197 | 64.2381 | 64.3431 | -58.7237 | -54.0598 | -48.6805 | -51.2234 | 64.3666 | 64.4621 | 64.3509 | -58.8646 | -0.12991 | -0.019709 | 9.4138 | 3.4445 | 3.5744 | -0.2013 | -0.096262 | -0.27083 | -0.072812 | 4.534 | 7.3703 | 7.6412 | 0.022724 | -0.08854 | 123.0134 | 122.8318 | 122.9369 | 36.1371 | -123.1631 | 122.9603 | 123.0559 | 122.9446 | 9.9133 | -123.304
516.2812 | 123.3948 | -58.4885 | 64.5859 | 0.057113 | -0.056644 | -0.0032469 | 0.049112 | -0.0094052 | 0.052192 | 0.058893 | -0.0071847 | -0.0044937 | 0.054914 | 0.048987 | 0.053447 | -49.0106 | -22.626 | -54.8425 | 64.5708 | 64.3846 | 64.4759 | -58.5771 | -53.4462 | -48.4561 | -50.6465 | 64.5039 | 64.6041 | 64.4974 | -58.7181 | -0.08867 | -0.015107 | 9.4779 | 3.646 | 3.7347 | -0.20126 | -0.10997 | -0.2296 | -0.081941 | 5.0422 | 7.8419 | 8.0715 | 0.018176 | -0.088509 | 123.0592 | 122.8731 | 122.9644 | 35.8624 | -123.163 | 122.9924 | 123.0925 | 122.9858 | 10.0323 | -123.3039
517.2812 | 123.3673 | -57.8934 | 65.1993 | 0.057113 | -0.058781 | -0.0032469 | 0.049112 | -0.0094052 | 0.050055 | 0.089415 | -0.0061157 | -0.0034247 | 0.053846 | 0.048987 | 0.054515 | -48.1453 | -22.04 | -54.3709 | 64.992 | 64.815 | 64.9063 | -58.1467 | -52.9014 | -48.9094 | -50.3947 | 64.9389 | 65.0253 | 64.9278 | -58.2877 | -0.25334 | -0.2073 | 9.7481 | 3.5225 | 3.7758 | -0.38424 | -0.29298 | -0.39428 | -0.26039 | 4.992 | 7.4987 | 7.893 | -0.174 | -0.27152 | 122.8854 | 122.7084 | 122.7997 | 35.8534 | -123.346 | 122.8323 | 122.9187 | 122.8211 | 8.984 | -123.4869
518.2812 | 123.349 | -58.0353 | 65.0848 | 0.041851 | -0.057712 | -0.0021789 | 0.050181 | -0.010474 | 0.054329 | 0.089415 | -0.0071847 | -0.0034247 | 0.054914 | 0.050056 | 0.055583 | -47.6371 | -21.953 | -54.3206 | 64.9737 | 64.7784 | 64.8742 | -58.1925 | -52.6221 | -47.8609 | -49.7491 | 64.9114 | 64.9978 | 64.8957 | -58.3197 | -0.15723 | -0.11117 | 10.3982 | 3.7147 | 3.872 | -0.30644 | -0.21059 | -0.28443 | -0.17342 | 5.4132 | 8.2862 | 8.5706 | -0.087027 | -0.18913 | 123.0089 | 122.8137 | 122.9095 | 36.0823 | -123.2773 | 122.9467 | 123.0331 | 122.931 | 10.1744 | -123.4045
519.2812 | 123.349 | -58.136 | 64.9292 | 0.041851 | -0.056644 | -0.0043149 | 0.050181 | -0.010474 | 0.051124 | 0.043632 | -0.0050477 | -0.0023567 | 0.054914 | 0.048987 | 0.055583 | -47.1243 | -21.3715 | -54.3526 | 65.0103 | 64.8242 | 64.9155 | -58.1513 | -51.3995 | -48.3462 | -49.5888 | 64.9389 | 65.0344 | 64.9323 | -58.2877 | -0.015308 | 0.081096 | 11.0117 | 3.7834 | 3.7987 | -0.105 | -0.013743 | -0.15167 | 0.009693 | 6.7364 | 8.5472 | 8.6988 | 0.10524 | 0.003135 | 123.1463 | 122.9602 | 123.0514 | 36.7645 | -123.0805 | 123.0749 | 123.1704 | 123.0683 | 9.7897 | -123.2169
520.2812 | 123.349 | -58.5526 | 64.5584 | 0.057113 | -0.056644 | -0.0043149 | 0.049112 | -0.0094052 | 0.05326 | 0.074154 | -0.0039797 | -0.0012887 | 0.055982 | 0.052192 | 0.055583 | -47.0007 | -21.6279 | -54.6456 | 64.5479 | 64.3709 | 64.4576 | -58.6092 | -51.8849 | -47.2336 | -48.087 | 64.4902 | 64.5812 | 64.4745 | -58.7364 | -0.056635 | -0.010534 | 11.5519 | 3.9069 | 3.9636 | -0.18753 | -0.10082 | -0.18383 | -0.068211 | 6.6677 | 10.4655 | 10.6494 | 0.022748 | -0.083937 | 123.1004 | 122.9234 | 123.0101 | 36.9246 | -123.1676 | 123.0428 | 123.1337 | 123.027 | 11.3189 | -123.2948
521.3125 | 123.3627 | -59.404 | 63.707 | 0.041851 | -0.057712 | -0.0011099 | 0.052318 | -0.0083372 | 0.05326 | 0.074154 | -0.0050477 | -0.0012887 | 0.055982 | 0.053261 | 0.058788 | -45.7783 | -21.1014 | -55.1813 | 63.7375 | 63.5467 | 63.6472 | -59.4426 | -52.2329 | -46.7712 | -48.5495 | 63.6706 | 63.757 | 63.6595 | -59.5606 | -0.038559 | 0.030533 | 13.6257 | 4.2227 | 4.2613 | -0.1603 | -0.059787 | -0.15657 | -0.036321 | 7.1711 | 10.8545 | 11.0111 | 0.050041 | -0.047487 | 123.1415 | 122.9507 | 123.0512 | 38.3026 | -123.1495 | 123.0746 | 123.161 | 123.0635 | 12.6328 | -123.2675
522.2812 | 123.3582 | -59.3399 | 63.739 | 0.072375 | -0.057712 | -0.0021789 | 0.049112 | -0.010474 | 0.056465 | 0.074154 | -0.0050477 | -0.00021967 | 0.05705 | 0.052192 | 0.05772 | -45.911 | -20.2818 | -55.0393 | 63.7375 | 63.565 | 63.6518 | -59.4105 | -51.7613 | -46.3133 | -48.4671 | 63.6798 | 63.7753 | 63.6778 | -59.5514 | -0.070593 | -0.001511 | 13.4289 | 4.3006 | 4.3712 | -0.17403 | -0.087252 | -0.2115 | -0.059208 | 7.5786 | 10.8729 | 11.0844 | 0.036311 | -0.061217 | 123.0774 | 122.9049 | 122.9917 | 39.0581 | -123.1495 | 123.0197 | 123.1152 | 123.0177 | 13.0266 | -123.2904
523.2812 | 123.3627 | -59.3903 | 63.7115 | 0.041851 | -0.057712 | -0.0011099 | 0.049112 | -0.0094052 | 0.054329 | 0.058893 | -0.0039797 | -0.0012887 | 0.055982 | 0.054329 | 0.056652 | -44.8351 | -20.0025 | -54.7555 | 63.7283 | 63.5421 | 63.638 | -59.4426 | -51.2301 | -46.4186 | -47.913 | 63.6523 | 63.7479 | 63.6457 | -59.5697 | -0.052292 | 0.016798 | 14.5552 | 4.6348 | 4.6871 | -0.16945 | -0.073522 | -0.17946 | -0.059213 | 8.1601 | 11.4772 | 11.6567 | 0.036306 | -0.065801 | 123.1186 | 122.9324 | 123.0283 | 39.3878 | -123.1541 | 123.0426 | 123.1381 | 123.036 | 12.9717 | -123.2813
524.2812 | 123.3398 | -59.6283 | 63.4644 | 0.072375 | -0.055576 | 0.0010261 | 0.048044 | -0.010474 | 0.056465 | 0.074154 | -0.0061157 | -0.0012887 | 0.060255 | 0.054329 | 0.05772 | -44.2033 | -19.6774 | -55.1309 | 63.3346 | 63.1575 | 63.2488 | -59.8089 | -52.0497 | -45.4433 | -47.3544 | 63.2815 | 63.3678 | 63.2749 | -59.9498 | -0.18057 | -0.12975 | 15.425 | 4.4974 | 4.678 | -0.30689 | -0.21551 | -0.32147 | -0.18288 | 7.5786 | 12.2739 | 12.5953 | -0.096525 | -0.18947 | 122.9629 | 122.7858 | 122.8771 | 39.9509 | -123.2732 | 122.9098 | 122.9961 | 122.9032 | 14.185 | -123.4141
525.2812 | 123.349 | -60.0906 | 62.9974 | 0.072375 | -0.057712 | -4.1882e-05 | 0.050181 | -0.010474 | 0.058602 | 0.074154 | -0.0050477 | -0.00021967 | 0.061323 | 0.053261 | 0.05772 | -42.5139 | -18.9632 | -55.2087 | 63.0004 | 62.8095 | 62.9054 | -60.1614 | -52.4618 | -45.0313 | -46.4936 | 62.9335 | 63.0107 | 62.9177 | -60.2978 | -0.070805 | 0.002945 | 17.5768 | 4.8819 | 4.9527 | -0.18797 | -0.091988 | -0.20712 | -0.063926 | 7.6288 | 13.597 | 13.8041 | 0.013262 | -0.079688 | 123.091 | 122.9001 | 122.9961 | 41.1275 | -123.1589 | 123.0241 | 123.1013 | 123.0084 | 15.0594 | -123.2952
526.2812 | 123.349 | -60.878 | 62.1964 | 0.057113 | -0.057712 | -4.1882e-05 | 0.049112 | -0.0094052 | 0.058602 | 0.074154 | -0.0061157 | -0.00021967 | 0.062391 | 0.059671 | 0.05772 | -42.9122 | -19.1005 | -55.9504 | 62.1259 | 61.9349 | 62.0401 | -61.0452 | -52.5442 | -41.7483 | -42.9451 | 62.0636 | 62.1453 | 62.0524 | -61.1677 | -0.16718 | -0.07044 | 17.9658 | 4.9276 | 5.0948 | -0.26146 | -0.15626 | -0.28974 | -0.13275 | 8.3338 | 17.9329 | 18.2226 | -0.051007 | -0.14396 | 123.0039 | 122.8129 | 122.9181 | 41.7775 | -123.2415 | 122.9416 | 123.0233 | 122.9304 | 19.1297 | -123.3641
527.2812 | 123.3261 | -60.8688 | 62.2284 | 0.072375 | -0.057712 | 0.0020951 | 0.048044 | -0.0094052 | 0.058602 | 0.074154 | -0.0061157 | 0.0019163 | 0.062391 | 0.058603 | 0.059856 | -41.383 | -18.5969 | -55.5613 | 62.3457 | 62.1684 | 62.2644 | -60.7933 | -51.9444 | -42.0368 | -43.3023 | 62.2879 | 62.3743 | 62.2722 | -60.9388 | 0.075502 | 0.11728 | 19.4858 | 5.3076 | 5.2321 | -0.059977 | 0.036051 | -0.069954 | 0.05955 | 8.9244 | 17.5666 | 17.6365 | 0.14588 | 0.043772 | 123.2145 | 123.0373 | 123.1333 | 42.272 | -123.0217 | 123.1568 | 123.2431 | 123.141 | 18.8321 | -123.1672
528.2812 | 123.3261 | -61.0886 | 61.9949 | 0.072375 | -0.056644 | 0.0031631 | 0.049112 | -0.0083372 | 0.058602 | 0.058893 | -0.0050477 | 0.0019163 | 0.06346 | 0.058603 | 0.058788 | -41.09 | -18.867 | -55.8405 | 61.929 | 61.7517 | 61.8478 | -61.2146 | -51.7384 | -40.8555 | -41.9424 | 61.8667 | 61.9576 | 61.8509 | -61.3463 | -0.12603 | -0.065894 | 19.9986 | 5.248 | 5.3741 | -0.2432 | -0.14714 | -0.25774 | -0.12821 | 9.3502 | 19.1462 | 19.4039 | -0.037314 | -0.144 | 123.0176 | 122.8403 | 122.9364 | 42.2215 | -123.2095 | 122.9553 | 123.0462 | 122.9395 | 20.2331 | -123.3412
529.2812 | 123.3719 | -61.3495 | 61.7111 | 0.087637 | -0.057712 | 0.0020951 | 0.048044 | -0.0083372 | 0.05967 | 0.074154 | -0.0061157 | 0.00084833 | 0.064528 | 0.061808 | 0.060925 | -41.0259 | -19.0547 | -55.9046 | 61.6955 | 61.5091 | 61.6051 | -61.4619 | -51.482 | -39.5872 | -40.6283 | 61.6332 | 61.7241 | 61.6083 | -61.589 | -0.11237 | -0.015579 | 20.3236 | 5.4449 | 5.5572 | -0.20207 | -0.106 | -0.23949 | -0.077902 | 9.8675 | 20.7212 | 20.9607 | 0.01299 | -0.10285 | 123.045 | 122.8585 | 122.9546 | 42.2948 | -123.173 | 122.9827 | 123.0736 | 122.9578 | 21.7623 | -123.3001
530.2812 | 123.3307 | -61.7386 | 61.3678 | 0.072375 | -0.055576 | 0.0042321 | 0.049112 | -0.0094052 | 0.061807 | 0.074154 | -0.0039797 | 0.0040533 | 0.066664 | 0.060739 | 0.058788 | -38.4162 | -19.2333 | -56.0054 | 61.4117 | 61.2343 | 61.335 | -61.7412 | -51.3538 | -39.1064 | -39.9781 | 61.3494 | 61.4448 | 61.3473 | -61.8729 | -0.002585 | 0.043884 | 23.3224 | 5.7332 | 5.7358 | -0.13348 | -0.032809 | -0.13428 | -0.018446 | 10.3848 | 21.7605 | 21.8947 | 0.077018 | -0.020509 | 123.1503 | 122.9729 | 123.0736 | 42.5053 | -123.109 | 123.0879 | 123.1834 | 123.0859 | 22.6322 | -123.2407
531.2812 | 123.3261 | -61.6791 | 61.3998 | 0.057113 | -0.056644 | 0.0042321 | 0.052318 | -0.0094052 | 0.060738 | 0.043632 | -0.0029117 | 0.0019163 | 0.065596 | 0.062876 | 0.060925 | -37.6745 | -18.6656 | -55.7581 | 61.4392 | 61.2572 | 61.3533 | -61.7229 | -51.0699 | -39.2071 | -39.9919 | 61.3768 | 61.4723 | 61.361 | -61.8546 | -0.043778 | 0.039311 | 24.0046 | 5.9209 | 5.9647 | -0.14263 | -0.046538 | -0.17548 | -0.023018 | 10.6092 | 21.6872 | 21.8627 | 0.072447 | -0.038817 | 123.1182 | 122.9363 | 123.0324 | 43.0135 | -123.1227 | 123.0559 | 123.1514 | 123.0401 | 22.4719 | -123.2544
532.2812 | 123.3582 | -61.5738 | 61.4822 | 0.072375 | -0.056644 | 0.0053001 | 0.050181 | -0.0072692 | 0.062875 | 0.058893 | -0.0029117 | 0.0019163 | 0.067733 | 0.060739 | 0.060925 | -37.4364 | -18.4916 | -55.4468 | 61.3659 | 61.2023 | 61.2892 | -61.7686 | -50.6944 | -38.8225 | -39.4745 | 61.3173 | 61.4219 | 61.2969 | -61.9003 | -0.19485 | -0.11634 | 24.1374 | 6.127 | 6.3218 | -0.27998 | -0.19304 | -0.32655 | -0.16494 | 10.8794 | 22.0993 | 22.4259 | -0.060316 | -0.18532 | 122.9397 | 122.7761 | 122.863 | 43.0822 | -123.2509 | 122.8911 | 122.9957 | 122.8707 | 22.7513 | -123.3826
533.2812 | 123.381 | -61.7981 | 61.2488 | 0.072375 | -0.056644 | 0.0053001 | 0.051249 | -0.0083372 | 0.063943 | 0.074154 | -0.0050477 | 0.0029843 | 0.066664 | 0.061808 | 0.060925 | -36.7817 | -18.4824 | -55.2042 | 61.3842 | 61.2114 | 61.3075 | -61.7641 | -50.4838 | -38.8363 | -39.7217 | 61.331 | 61.4219 | 61.3152 | -61.8958 | 0.034031 | 0.13543 | 25.0164 | 6.5939 | 6.5599 | -0.037357 | 0.058738 | -0.097666 | 0.082259 | 11.3143 | 22.0764 | 22.174 | 0.17314 | 0.066459 | 123.1823 | 123.0095 | 123.1056 | 43.3157 | -123.0128 | 123.1291 | 123.22 | 123.1133 | 22.9618 | -123.1445
534.2812 | 123.2803 | -61.8805 | 61.2213 | 0.057113 | -0.057712 | 0.0074371 | 0.051249 | -0.0094052 | 0.063943 | 0.074154 | -0.0061157 | 0.0019163 | 0.065596 | 0.062876 | 0.063061 | -35.4815 | -18.1802 | -55.0256 | 61.2698 | 61.0969 | 61.1976 | -61.8511 | -50.3373 | -38.3143 | -39.1997 | 61.2212 | 61.3075 | 61.2099 | -62.0057 | 0.029428 | 0.048439 | 26.399 | 6.8549 | 6.8255 | -0.12436 | -0.023682 | -0.12516 | -0.000159 | 11.5432 | 22.6808 | 22.8059 | 0.086145 | -0.011382 | 123.1502 | 122.9774 | 123.0781 | 43.7003 | -123.0724 | 123.1016 | 123.188 | 123.0904 | 23.5662 | -123.227
535.3125 | 123.3627 | -62.1506 | 60.9192 | 0.041851 | -0.055576 | 0.0053001 | 0.051249 | -0.0083372 | 0.063943 | 0.043632 | -0.0050477 | 0.0061893 | 0.065596 | 0.062876 | 0.063061 | -34.0759 | -17.8597 | -55.3278 | 60.7707 | 60.5933 | 60.7031 | -62.3685 | -49.9069 | -37.9068 | -38.7236 | 60.7175 | 60.813 | 60.6925 | -62.5047 | -0.21791 | -0.14848 | 28.0747 | 6.8228 | 7.0407 | -0.32592 | -0.21605 | -0.35417 | -0.20167 | 12.2437 | 23.427 | 23.7812 | -0.10622 | -0.22664 | 122.9213 | 122.7438 | 122.8537 | 44.2909 | -123.2877 | 122.8681 | 122.9635 | 122.8431 | 24.2438 | -123.4239
536.2812 | 123.3627 | -62.6266 | 60.4797 | 0.072375 | -0.055576 | 0.0074371 | 0.051249 | -0.0083372 | 0.065012 | 0.074154 | -0.0050477 | 0.0040533 | 0.068801 | 0.063944 | 0.065198 | -32.9221 | -17.5713 | -55.1355 | 60.496 | 60.3231 | 60.433 | -62.6432 | -49.7558 | -37.3711 | -38.0139 | 60.4428 | 60.5383 | 60.4224 | -62.7795 | -0.016571 | 0.016268 | 29.7045 | 7.4912 | 7.5077 | -0.15663 | -0.046732 | -0.15283 | -0.036926 | 12.8709 | 24.6128 | 24.7656 | 0.058517 | -0.057325 | 123.1227 | 122.9498 | 123.0597 | 45.0554 | -123.123 | 123.0695 | 123.1649 | 123.0491 | 25.2556 | -123.2592
537.2812 | 123.3307 | -62.7228 | 60.3745 | 0.057113 | -0.057712 | 0.0074371 | 0.051249 | -0.0072692 | 0.067148 | 0.058893 | -0.0039797 | 0.0051213 | 0.069869 | 0.065013 | 0.06413 | -31.512 | -17.5301 | -54.6685 | 60.3953 | 60.2224 | 60.3277 | -62.7485 | -49.2476 | -36.9498 | -37.3912 | 60.3467 | 60.4284 | 60.3263 | -62.8848 | -0.025756 | 0.020829 | 31.2108 | 8.0543 | 8.08 | -0.15208 | -0.046755 | -0.16201 | -0.027789 | 13.4752 | 25.3316 | 25.4936 | 0.053916 | -0.048191 | 123.1181 | 122.9452 | 123.0505 | 45.1927 | -123.123 | 123.0694 | 123.1511 | 123.049 | 25.7729 | -123.2592
538.2812 | 123.3307 | -63.7848 | 59.2941 | 0.041851 | -0.059849 | 0.0085051 | 0.053386 | -0.0083372 | 0.06608 | 0.058893 | -0.0061157 | 0.0061893 | 0.073074 | 0.066081 | 0.067334 | -29.937 | -17.1638 | -54.9386 | 59.9695 | 59.7828 | 59.8927 | -63.1652 | -47.3016 | -35.8235 | -35.3903 | 59.9071 | 59.998 | 59.8867 | -63.3244 | 0.61957 | 0.67536 | 33.8478 | 8.8462 | 8.2266 | 0.48867 | 0.5986 | 0.46044 | 0.613 | 16.4832 | 28.3945 | 27.9341 | 0.70385 | 0.59259 | 123.7543 | 123.5676 | 123.6775 | 46.621 | -122.4593 | 123.6919 | 123.7828 | 123.6715 | 27.9613 | -122.6185
539.2812 | 123.3078 | -63.295 | 59.8251 | 0.057113 | -0.058781 | 0.0095741 | 0.052318 | -0.0083372 | 0.067148 | 0.058893 | -0.0029117 | 0.0061893 | 0.074142 | 0.066081 | 0.068403 | -28.6871 | -17.1455 | -54.8425 | 59.5437 | 59.357 | 59.4669 | -63.6002 | -46.7476 | -35.8235 | -34.8729 | 59.4859 | 59.5722 | 59.4563 | -63.741 | -0.30523 | -0.28143 | 34.6079 | 8.4525 | 8.7577 | -0.46818 | -0.35822 | -0.44604 | -0.33923 | 16.5474 | 28.4221 | 28.8682 | -0.25297 | -0.36881 | 122.8387 | 122.6519 | 122.7619 | 46.1495 | -123.4253 | 122.7809 | 122.8672 | 122.7513 | 27.4715 | -123.5662
540.2812 | 123.349 | -64.9338 | 58.1451 | 0.072375 | -0.057712 | 0.015984 | 0.051249 | -0.0072692 | 0.074627 | 0.074154 | -0.0050477 | 0.0093943 | 0.07521 | 0.068218 | 0.071607 | -20.7436 | -16.2618 | -55.8543 | 58.2251 | 58.0474 | 58.162 | -64.9144 | -44.7742 | -36.5011 | -34.795 | 58.1719 | 58.2627 | 58.1514 | -65.0597 | 0.019411 | 0.079982 | 44.1901 | 9.0795 | 9.0601 | -0.097757 | 0.016875 | -0.12595 | 0.026734 | 20.1596 | 30.1388 | 30.2647 | 0.11755 | 0.006282 | 123.1589 | 122.9812 | 123.0958 | 48.672 | -123.0595 | 123.1057 | 123.1965 | 123.0852 | 28.4327 | -123.2049
541.2812 | 123.3032 | -64.9658 | 58.1085 | 0.072375 | -0.057712 | 0.019189 | 0.051249 | -0.0083372 | 0.075695 | 0.074154 | -0.0029117 | 0.0093943 | 0.078415 | 0.068218 | 0.071607 | -15.0893 | -15.0897 | -54.5312 | 58.1381 | 57.9695 | 58.075 | -65.0059 | -44.9207 | -36.6202 | -33.2703 | 58.0895 | 58.1803 | 58.069 | -65.133 | -0.040124 | 0.029613 | 49.8765 | 10.4347 | 10.4748 | -0.13898 | -0.033497 | -0.16717 | -0.019057 | 20.0451 | 31.6955 | 31.8627 | 0.071752 | -0.039512 | 123.104 | 122.9354 | 123.0408 | 49.8762 | -123.1145 | 123.0553 | 123.1461 | 123.0348 | 28.3457 | -123.2415
542.2812 | 123.3032 | -72.1252 | 50.9628 | 0.041851 | -0.058781 | 0.021326 | 0.052318 | -0.0072692 | 0.077832 | 0.058893 | -0.0050477 | 0.0072583 | 0.16281 | 0.13339 | 0.087631 | -21.3617 | -20.2223 | -61.5359 | 51.092 | 50.9317 | 51.0423 | -72.0392 | -50.4838 | -9.4409 | 41.6649 | 51.0432 | 51.1338 | 51.0134 | -72.1523 | 0.086072 | 0.12917 | 50.7635 | 10.5893 | 10.5032 | -0.031093 | 0.07946 | -0.027069 | 0.080329 | 21.6414 | 113.7901 | 113.8172 | 0.17097 | 0.050553 | 123.2172 | 123.057 | 123.1675 | 51.903 | -123.002 | 123.1684 | 123.259 | 123.1386 | 62.6843 | -123.1151
543.2812 | 123.3261 | -71.814 | 51.2009 | 0.057113 | -0.059849 | 0.022394 | 0.051249 | -0.0062002 | 0.077832 | 0.043632 | -0.0039797 | 0.0072583 | 0.16067 | 0.13232 | 0.084427 | -19.5807 | -20.0987 | -60.6294 | 51.3392 | 51.1561 | 51.2758 | -71.8285 | -49.1972 | -17.5178 | 42.9194 | 51.2767 | 51.3582 | 51.2423 | -71.9188 | -0.014577 | 0.13836 | 52.2332 | 11.1845 | 11.1991 | -0.044763 | 0.074932 | -0.10483 | 0.075796 | 22.6168 | 114.7334 | 114.8382 | 0.15729 | 0.041446 | 123.1532 | 122.9701 | 123.0898 | 51.7153 | -123.0294 | 123.0906 | 123.1721 | 123.0563 | 54.2962 | -123.1197
544.2812 | 123.3032 | -72.7478 | 50.322 | 0.072375 | -0.057712 | 0.023463 | 0.052318 | -0.0051322 | 0.077832 | 0.074154 | -0.0039797 | 0.0072583 | 0.16174 | 0.13339 | 0.086563 | -19.599 | -20.7213 | -59.9289 | 50.4098 | 50.2403 | 50.3601 | -72.7031 | -48.3868 | -21.2403 | 42.3974 | 50.3564 | 50.4379 | 50.322 | -72.8529 | 0.044687 | 0.087856 | 53.1488 | 12.8189 | 12.7742 | -0.081641 | 0.038118 | -0.10507 | 0.034425 | 24.361 | 115.1453 | 115.2503 | 0.1159 | 5.4e-05 | 123.1576 | 122.9881 | 123.1079 | 52.0265 | -123.0251 | 123.1042 | 123.1857 | 123.0698 | 51.5075 | -123.1748
545.2812 | 123.3124 | -72.3084 | 50.7065 | 0.087637 | -0.058781 | 0.025599 | 0.052318 | -0.0029952 | 0.082105 | 0.058893 | -0.0050477 | 0.011531 | 0.15853 | 0.13446 | 0.091904 | -19.4571 | -21.1472 | -58.5829 | 50.5289 | 50.3777 | 50.4929 | -72.5841 | -44.5177 | -22.4124 | 42.7729 | 50.48 | 50.5661 | 50.4594 | -72.7155 | -0.27571 | -0.17763 | 52.8512 | 13.7254 | 14.0011 | -0.32879 | -0.21362 | -0.40716 | -0.22648 | 27.7906 | 115.0813 | 115.4884 | -0.14043 | -0.24711 | 122.8372 | 122.686 | 122.8012 | 51.1612 | -123.2905 | 122.7884 | 122.8744 | 122.7677 | 49.8959 | -123.422
546.2812 | 123.3124 | -70.8069 | 52.2263 | 0.057113 | -0.058781 | 0.025599 | 0.054455 | -0.0019272 | 0.079968 | 0.074154 | -0.0039797 | 0.012599 | 0.16067 | 0.13339 | 0.091904 | -19.1595 | -22.1178 | -54.696 | 51.971 | 51.8109 | 51.9168 | -71.1371 | -41.6744 | -21.9591 | 44.2472 | 51.9222 | 52.0037 | 51.8971 | -71.2686 | -0.33024 | -0.25521 | 51.6474 | 16.1109 | 16.4412 | -0.41537 | -0.30945 | -0.46172 | -0.30403 | 29.1325 | 115.0541 | 115.5158 | -0.22252 | -0.3292 | 122.7779 | 122.6178 | 122.7237 | 48.6891 | -123.3634 | 122.7291 | 122.8106 | 122.7039 | 48.8478 | -123.4949
547.2812 | 123.3078 | -70.491 | 52.5696 | 0.057113 | -0.059849 | 0.027736 | 0.054455 | -0.00085916 | 0.079968 | 0.089415 | -0.0050477 | 0.013667 | 0.16174 | 0.13446 | 0.095109 | -18.8482 | -22.7039 | -53.1989 | 52.4976 | 52.3283 | 52.4479 | -70.6105 | -37.0132 | -21.3914 | 44.9249 | 52.4442 | 52.5349 | 52.4327 | -70.7375 | -0.11952 | -0.072019 | 51.6429 | 17.2922 | 17.4117 | -0.24127 | -0.12166 | -0.24643 | -0.1254 | 33.4778 | 115.4159 | 115.6624 | -0.034724 | -0.13683 | 122.9886 | 122.8193 | 122.9389 | 47.7871 | -123.1801 | 122.9352 | 123.0259 | 122.9238 | 49.0997 | -123.307
548.2812 | 123.2986 | -71.2051 | 51.8555 | 0.072375 | -0.060917 | 0.026668 | 0.053386 | 0.00020984 | 0.079968 | 0.089415 | -0.0029117 | 0.016872 | 0.16494 | 0.13232 | 0.10259 | -19.306 | -23.1389 | -53.1897 | 51.8795 | 51.7102 | 51.8207 | -71.2287 | -35.6305 | -8.2596 | 44.2015 | 51.8123 | 51.8893 | 51.7872 | -71.3693 | -0.023564 | 0.024009 | 51.8991 | 18.0154 | 18.039 | -0.14531 | -0.034816 | -0.1642 | -0.043122 | 35.5747 | 115.4066 | 115.5708 | 0.033804 | -0.068302 | 123.0846 | 122.9153 | 123.0258 | 48.0663 | -123.0842 | 123.0175 | 123.0944 | 122.9923 | 62.9455 | -123.2248
549.2812 | 123.2986 | -71.8414 | 51.2283 | 0.072375 | -0.058781 | 0.028805 | 0.051249 | -0.00085916 | 0.079968 | 0.043632 | -0.0039797 | 0.021145 | 0.16922 | 0.13446 | 0.10793 | -20.4277 | -23.8623 | -53.7345 | 50.4739 | 50.2907 | 50.4379 | -72.6619 | -33.2541 | 0.096512 | 42.9011 | 50.4113 | 50.4974 | 50.3586 | -72.775 | -0.82048 | -0.75442 | 51.4137 | 18.1069 | 18.9274 | -0.93765 | -0.79042 | -0.9336 | -0.81701 | 38.5873 | 114.7425 | 115.6761 | -0.73096 | -0.86969 | 122.3153 | 122.1321 | 122.2793 | 47.9792 | -123.8902 | 122.2528 | 122.3388 | 122.2001 | 71.9379 | -124.0034
550.2812 | 123.2895 | -72.5555 | 50.4776 | 0.041851 | -0.058781 | 0.029873 | 0.053386 | -0.00085916 | 0.081036 | 0.058893 | -0.0029117 | 0.020077 | 0.17669 | 0.13446 | 0.11541 | -18.8161 | -24.0454 | -54.4442 | 50.158 | 49.9793 | 50.1083 | -73.0007 | -32.2697 | -5.7184 | 42.663 | 50.0954 | 50.1815 | 50.0565 | -73.0818 | -0.4452 | -0.3196 | 53.7394 | 18.1114 | 18.5566 | -0.49828 | -0.36935 | -0.52627 | -0.38219 | 40.2858 | 115.2186 | 115.7448 | -0.29615 | -0.42115 | 122.7135 | 122.5349 | 122.6638 | 48.5101 | -123.4783 | 122.651 | 122.737 | 122.612 | 66.8371 | -123.5594
551.2812 | 123.3124 | -72.4686 | 50.679 | 0.057113 | -0.058781 | 0.029873 | 0.054455 | 0.00020984 | 0.082105 | 0.058893 | -0.0039797 | 0.022214 | 0.17456 | 0.13339 | 0.11541 | -17.3282 | -24.256 | -53.3133 | 50.4831 | 50.3136 | 50.4333 | -72.6299 | -32.1323 | -3.539 | 43.2628 | 50.4205 | 50.5203 | 50.377 | -72.7476 | -0.16129 | -0.19595 | 55.1404 | 19.1552 | 19.3165 | -0.36543 | -0.24568 | -0.27899 | -0.25853 | 40.3362 | 115.7314 | 116.0104 | -0.15874 | -0.30206 | 122.9516 | 122.7821 | 122.9019 | 48.2125 | -123.3089 | 122.8891 | 122.9888 | 122.8455 | 68.9296 | -123.4266
552.2812 | 123.3353 | -73.0682 | 49.9329 | 0.057113 | -0.059849 | 0.029873 | 0.053386 | -0.00085916 | 0.083173 | 0.074154 | -0.0039797 | 0.022214 | 0.17242 | 0.13339 | 0.11113 | -16.7375 | -24.1507 | -52.9013 | 50.2313 | 50.0572 | 50.1952 | -72.8817 | -32.5215 | 1.8547 | 43.391 | 50.1732 | 50.2593 | 50.148 | -73.004 | 0.18654 | 0.2984 | 56.3307 | 20.167 | 19.9804 | 0.1243 | 0.26239 | 0.064264 | 0.24038 | 40.5467 | 116.4593 | 116.395 | 0.32643 | 0.21517 | 123.2995 | 123.1254 | 123.2635 | 48.9175 | -122.8146 | 123.2415 | 123.3275 | 123.2163 | 74.923 | -122.9368
553.2812 | 123.349 | -73.5535 | 49.4751 | 0.072375 | -0.059849 | 0.030941 | 0.055523 | -0.00085916 | 0.084241 | 0.043632 | -0.0039797 | 0.019009 | 0.17135 | 0.13446 | 0.109 | -16.9115 | -23.0564 | -53.6933 | 49.7231 | 49.5535 | 49.6687 | -73.39 | -32.7459 | 5.0644 | 43.0202 | 49.6696 | 49.7602 | 49.6261 | -73.5168 | 0.16351 | 0.24796 | 56.6419 | 19.8601 | 19.6966 | 0.078382 | 0.19361 | 0.036667 | 0.19451 | 40.8076 | 116.5736 | 116.537 | 0.28513 | 0.15097 | 123.2765 | 123.1069 | 123.2222 | 50.497 | -122.8651 | 123.2231 | 123.3137 | 123.1795 | 78.6179 | -122.9919
554.2812 | 123.3719 | -73.6404 | 49.3973 | 0.072375 | -0.059849 | 0.03201 | 0.052318 | 0.0012778 | 0.084241 | 0.058893 | -0.0039797 | 0.020077 | 0.16815 | 0.13339 | 0.10793 | -17.2595 | -22.04 | -53.3912 | 49.398 | 49.2284 | 49.3482 | -73.7196 | -29.614 | 6.5067 | 42.8691 | 49.3445 | 49.4306 | 49.3101 | -73.8419 | -0.079195 | 0.000714 | 56.381 | 20.2493 | 20.3285 | -0.1689 | -0.049071 | -0.20145 | -0.05274 | 44.0264 | 116.5095 | 116.7109 | 0.033285 | -0.087135 | 123.0384 | 122.8688 | 122.9886 | 51.6005 | -123.1169 | 122.985 | 123.071 | 122.9506 | 80.1471 | -123.2392
555.2812 | 123.3307 | -73.6633 | 49.3515 | 0.057113 | -0.057712 | 0.030941 | 0.053386 | 0.0023458 | 0.084241 | 0.074154 | -0.0029117 | 0.022214 | 0.17028 | 0.13339 | 0.11007 | -17.7448 | -21.3761 | -52.915 | 49.5949 | 49.4115 | 49.5405 | -73.509 | -27.0729 | 8.3748 | 43.0156 | 49.5323 | 49.6091 | 49.4887 | -73.6404 | 0.15432 | 0.24336 | 55.9185 | 20.7483 | 20.594 | 0.060033 | 0.18901 | 0.022902 | 0.18075 | 46.5905 | 116.6789 | 116.656 | 0.25763 | 0.13721 | 123.2582 | 123.0749 | 123.2038 | 52.2872 | -122.8605 | 123.1956 | 123.2725 | 123.152 | 82.0381 | -122.9919
556.2812 | 123.3215 | -74.4919 | 48.5458 | 0.057113 | -0.060917 | 0.033078 | 0.053386 | 0.00020984 | 0.084241 | 0.043632 | -0.0029117 | 0.023282 | 0.17028 | 0.13766 | 0.11007 | -19.8188 | -20.7763 | -54.2381 | 48.1298 | 47.9554 | 48.0845 | -74.9834 | -29.5179 | 12.0515 | 41.6511 | 48.0671 | 48.1623 | 48.0373 | -75.1011 | -0.49154 | -0.41606 | 54.6731 | 20.2537 | 20.7453 | -0.5904 | -0.46132 | -0.60919 | -0.4787 | 44.974 | 116.143 | 116.7522 | -0.38355 | -0.50855 | 122.6217 | 122.4473 | 122.5764 | 53.7156 | -123.5293 | 122.559 | 122.6542 | 122.5292 | 86.5434 | -123.6469
557.2812 | 123.262 | -75.5356 | 47.493 | 0.057113 | -0.060917 | 0.035215 | 0.054455 | 0.0023458 | 0.084241 | 0.074154 | -0.0039797 | 0.028623 | 0.17135 | 0.13553 | 0.11648 | -19.8737 | -21.3944 | -53.8215 | 47.5987 | 47.4014 | 47.558 | -75.5375 | -25.8824 | 12.9398 | 41.0467 | 47.5131 | 47.6083 | 47.4741 | -75.6551 | -0.001887 | 0.10571 | 55.6618 | 21.7141 | 21.716 | -0.091595 | 0.064993 | -0.11952 | 0.020159 | 49.6532 | 116.5823 | 116.7018 | 0.1153 | -0.018858 | 123.1343 | 122.937 | 123.0936 | 54.1412 | -123.0305 | 123.0487 | 123.1439 | 123.0097 | 88.4754 | -123.1481
558.2812 | 123.3261 | -77.9343 | 45.0851 | 0.057113 | -0.059849 | 0.035215 | 0.054455 | 0.0023458 | 0.087446 | 0.043632 | -0.0050477 | 0.094857 | 0.17028 | 0.13339 | 0.18057 | -20.9359 | -23.3312 | -55.3095 | 45.3141 | 45.1302 | 45.2733 | -77.7903 | 32.5328 | 12.6101 | 38.7574 | 45.2514 | 45.3281 | 45.1986 | -77.9125 | 0.14396 | 0.22893 | 56.9983 | 22.6248 | 22.4808 | 0.045095 | 0.18811 | 0.0218 | 0.16622 | 110.467 | 116.6916 | 116.6698 | 0.24299 | 0.11341 | 123.2483 | 123.0645 | 123.2075 | 54.6031 | -122.8754 | 123.1856 | 123.2624 | 123.1328 | 90.5444 | -122.9976
559.2812 | 123.317 | -80.0629 | 42.9153 | 0.041851 | -0.059849 | 0.054446 | 0.053386 | 0.0023458 | 0.10454 | 0.074154 | -0.0061157 | 0.086311 | 0.17349 | 0.13446 | 0.1795 | -0.16835 | -21.0235 | -56.5456 | 42.9058 | 42.74 | 42.8786 | -80.1942 | 31.7361 | 10.5451 | 36.3398 | 42.8431 | 42.9335 | 42.8131 | -80.298 | -0.13137 | -0.009506 | 79.8945 | 23.5173 | 23.6486 | -0.1753 | -0.036702 | -0.23516 | -0.072269 | 111.799 | 116.4027 | 116.6378 | 0.018183 | -0.10224 | 122.9687 | 122.8029 | 122.9415 | 59.0393 | -123.1096 | 122.9059 | 122.9964 | 122.876 | 90.608 | -123.2134
560.2812 | 123.1796 | -80.8365 | 42.2791 | 0.057113 | -0.059849 | 0.061925 | 0.053386 | 0.0044828 | 0.11309 | 0.043632 | -0.0050477 | 0.092721 | 0.17242 | 0.13339 | 0.18591 | 10.7328 | -24.8375 | -56.7333 | 42.2237 | 42.0624 | 42.1964 | -80.8444 | 31.7956 | 8.1688 | 35.6713 | 42.17 | 42.2605 | 42.1217 | -80.9711 | -0.007957 | -0.055395 | 91.5693 | 24.1032 | 24.1111 | -0.21669 | -0.082623 | -0.13463 | -0.10902 | 112.6321 | 116.5078 | 116.6424 | -0.018581 | -0.15732 | 123.0601 | 122.8988 | 123.0329 | 55.999 | -123.1235 | 123.0065 | 123.097 | 122.9582 | 89.0053 | -123.2502
561.2812 | 123.2483 | -83.1299 | 39.9078 | 0.011327 | -0.059849 | 0.072609 | 0.052318 | 0.0034148 | 0.11843 | 0.043632 | -0.0061157 | 0.093789 | 0.17776 | 0.13446 | 0.18912 | 16.6526 | -23.148 | -57.2003 | 41.4408 | 41.2656 | 41.4181 | -81.6686 | 31.7636 | 7.569 | 34.7739 | 41.3688 | 41.4592 | 41.3205 | -81.7816 | 1.4612 | 1.5329 | 99.7825 | 25.9296 | 24.4684 | 1.3578 | 1.5102 | 1.3483 | 1.461 | 114.8934 | 117.9038 | 116.5555 | 1.5514 | 1.4126 | 124.5706 | 124.3955 | 124.548 | 59.9819 | -121.5765 | 124.4987 | 124.5891 | 124.4504 | 90.6988 | -121.6894
562.3125 | 123.2025 | -82.2876 | 40.7684 | 0.057113 | -0.060917 | 0.075814 | 0.054455 | 0.0055508 | 0.1227 | 0.043632 | -0.0039797 | 0.10554 | 0.18417 | 0.13553 | 0.20835 | 19.6835 | -19.5492 | -56.9668 | 40.6807 | 40.5238 | 40.658 | -82.4013 | 31.2736 | 5.275 | 33.9451 | 40.6317 | 40.7083 | 40.5742 | -82.5188 | -0.11368 | -0.087691 | 101.9711 | 25.3208 | 25.4345 | -0.24459 | -0.11041 | -0.23116 | -0.13677 | 113.5612 | 116.2327 | 116.4639 | -0.060107 | -0.19426 | 122.9683 | 122.8114 | 122.9456 | 62.7384 | -123.1697 | 122.9193 | 122.9959 | 122.8618 | 87.5626 | -123.2872
563.2812 | 123.2758 | -83.3954 | 39.6057 | 0.041851 | -0.061986 | 0.076882 | 0.053386 | 0.0066188 | 0.1227 | 0.043632 | -0.0061157 | 0.19421 | 0.17456 | 0.11523 | 0.3141 | 23.1265 | -14.2976 | -54.8562 | 42.2099 | 41.9891 | 42.201 | -81.0413 | 31.9375 | -20.2879 | 12.8373 | 42.0739 | 42.1781 | 42.0027 | -81.0581 | 2.354 | 2.6042 | 106.5219 | 28.5392 | 26.1851 | 2.3834 | 2.5953 | 2.3373 | 2.4682 | 115.3329 | 96.2327 | 93.8954 | 2.5723 | 2.397 | 125.6053 | 125.3845 | 125.5964 | 69.0978 | -120.6471 | 125.4693 | 125.5734 | 125.3981 | 63.1075 | -120.6638
564.2812 | 123.143 | -71.3425 | 51.6632 | 0.057113 | -0.060917 | 0.04483 | 0.053386 | 0.0044828 | 0.090651 | 0.058893 | -0.0050477 | 0.15682 | 0.13503 | 0.072491 | 0.28206 | -7.5579 | -10.5294 | -46.597 | 52.2961 | 52.1268 | 52.2465 | -70.8212 | 46.9237 | -66.2902 | -37.3545 | 52.2153 | 52.3059 | 52.1809 | -70.8428 | 0.52129 | 0.6329 | 63.7846 | 24.7455 | 24.2242 | 0.46363 | 0.58326 | 0.4997 | 0.55205 | 118.2661 | 33.9879 | 33.4882 | 0.64272 | 0.51772 | 123.6386 | 123.4693 | 123.5889 | 60.8131 | -122.4844 | 123.5577 | 123.6484 | 123.5234 | 5.0523 | -122.506
565.2812 | 123.111 | -72.3084 | 50.8026 | 0.072375 | -0.061986 | 0.070472 | 0.055523 | 0.0034148 | 0.11629 | 0.058893 | -0.0050477 | 0.1237 | 0.31556 | 0.078902 | 0.4252 | 24.1932 | -5.8592 | -48.0117 | 50.1946 | 49.9839 | 50.154 | -73.042 | -59.22 | -33.3739 | -30.6101 | 50.0222 | 50.1265 | 49.9969 | -73.0498 | -0.73361 | -0.60798 | 96.5016 | 24.2967 | 25.0303 | -0.81871 | -0.64857 | -0.74141 | -0.78046 | 13.0884 | 41.6983 | 42.4397 | -0.6761 | -0.80568 | 122.503 | 122.2922 | 122.4624 | 66.4491 | -123.8446 | 122.3305 | 122.4349 | 122.3053 | 38.9345 | -123.8524
566.2812 | 123.1842 | -74.6063 | 48.2849 | 0.026589 | -0.063054 | 0.081156 | 0.054455 | 0.0044828 | 0.1227 | 0.043632 | -0.0029117 | 0.14507 | 0.94049 | 0.077833 | 1.0544 | 30.6808 | -4.2933 | -46.7801 | 50.8081 | 50.6295 | 50.763 | -72.3185 | -66.6467 | -54.0147 | -31.4159 | 50.6128 | 50.708 | 50.5509 | -72.2668 | 2.2878 | 2.5232 | 105.2871 | 27.8262 | 25.5384 | 2.3446 | 2.4781 | 2.3395 | 2.3279 | 7.9597 | 43.1904 | 40.8508 | 2.4231 | 2.266 | 125.4145 | 125.2359 | 125.3693 | 70.313 | -120.6034 | 125.2191 | 125.3143 | 125.1573 | 20.5916 | -120.5517
567.2812 | 123.1705 | -70.6146 | 52.4506 | 0.057113 | -0.061986 | 0.079019 | 0.054455 | 0.0044828 | 0.1227 | 0.058893 | -0.0029117 | 0.055331 | 0.12969 | 0.062876 | 0.18057 | 33.8628 | -3.0525 | -44.9992 | 53.0149 | 52.8503 | 52.9516 | -70.0428 | -69.1741 | -50.2281 | -49.5339 | 52.9432 | 53.0339 | 52.9089 | -70.188 | 0.57186 | 0.56436 | 104.4774 | 25.6155 | 25.0436 | 0.39974 | 0.501 | 0.42662 | 0.49267 | 1.4405 | 21.0807 | 20.6541 | 0.58336 | 0.45836 | 123.6295 | 123.4649 | 123.5662 | 67.5621 | -122.4933 | 123.5579 | 123.6485 | 123.5235 | 20.3865 | -122.6386
568.2812 | 123.1796 | -67.868 | 55.22 | 0.041851 | -0.063054 | 0.045899 | 0.054455 | 0.0034148 | 0.094925 | 0.058893 | -0.0018437 | 0.056399 | 0.11687 | 0.053261 | 0.18057 | -4.9436 | -5.6898 | -44.2026 | 55.3774 | 55.1947 | 55.3187 | -67.7029 | -66.3811 | -61.9587 | -61.1318 | 55.3103 | 55.4011 | 55.3035 | -67.8208 | 0.16511 | 0.15733 | 62.9244 | 23.6655 | 23.5004 | -0.025317 | 0.098673 | 0.04729 | 0.090285 | 1.487 | 6.7363 | 6.689 | 0.18103 | 0.083501 | 123.2454 | 123.0628 | 123.1867 | 62.1782 | -122.923 | 123.1784 | 123.2691 | 123.1716 | 5.9093 | -123.0408
569.2812 | 123.3124 | -77.8015 | 45.2042 | 0.057113 | -0.061986 | 0.081156 | 0.052318 | 0.0055508 | 0.12591 | 0.074154 | -0.0039797 | 0.045716 | 0.15319 | 0.076765 | 0.18271 | 26.5099 | -7.7593 | -51.0791 | 46.3991 | 46.1971 | 46.3813 | -76.7234 | -75.6576 | -36.318 | -36.2602 | 46.2998 | 46.4041 | 46.2425 | -76.841 | 1.0781 | 1.195 | 104.3114 | 26.7224 | 25.6443 | 0.99297 | 1.1771 | 0.96049 | 1.0957 | 2.144 | 41.5413 | 40.5808 | 1.1999 | 1.0383 | 124.2007 | 123.9986 | 124.1828 | 70.0422 | -121.9276 | 124.1014 | 124.2056 | 124.044 | 41.4835 | -122.0452
570.2812 | 122.9965 | -78.5797 | 44.4534 | 0.057113 | -0.064123 | 0.084361 | 0.052318 | 0.0044828 | 0.12911 | 0.074154 | -0.0039797 | 0.098062 | 0.12542 | 0.070355 | 0.21155 | 26.368 | -8.176 | -52.1367 | 45.424 | 45.2584 | 45.3786 | -77.6804 | -76.3444 | -48.5569 | -48.7784 | 45.375 | 45.4472 | 45.3268 | -77.7247 | 0.8993 | 0.97052 | 104.9477 | 26.443 | 25.5437 | 0.80502 | 0.92513 | 0.85498 | 0.92155 | 2.2354 | 29.8013 | 28.9463 | 0.99375 | 0.87333 | 124.0037 | 123.8382 | 123.9583 | 70.4037 | -122.1338 | 123.9547 | 124.0269 | 123.9065 | 30.0229 | -122.1782
571.2812 | 123.1064 | -82.0816 | 40.7867 | 0.041851 | -0.061986 | 0.086498 | 0.053386 | 0.0055508 | 0.13125 | 0.043632 | -0.0039797 | 0.11836 | 0.71509 | 0.10027 | 0.75743 | 24.9624 | -10.4699 | -53.0432 | 43.0111 | 42.8179 | 42.9977 | -80.066 | -78.3407 | -11.6845 | -10.7156 | 42.8477 | 42.9473 | 42.7948 | -80.0508 | 2.0156 | 2.2244 | 107.044 | 29.0384 | 27.0228 | 2.0311 | 2.2109 | 2.0308 | 2.0609 | 3.7409 | 71.366 | 69.3352 | 2.1605 | 2.008 | 125.0927 | 124.8995 | 125.0793 | 71.6117 | -120.8528 | 124.9293 | 125.0289 | 124.8764 | 70.3971 | -120.8375
572.2812 | 123.1064 | -76.1078 | 46.907 | 0.041851 | -0.061986 | 0.085429 | 0.053386 | 0.0076878 | 0.12697 | 0.058893 | -0.0018437 | 0.091653 | 0.1564 | 0.054329 | 0.24787 | 28.4237 | -7.0039 | -48.1811 | 46.6006 | 46.4352 | 46.5598 | -76.4487 | -75.4469 | -69.1931 | -69.3826 | 46.5562 | 46.6285 | 46.5126 | -76.5388 | -0.34089 | -0.30645 | 104.5315 | 27.9267 | 28.2676 | -0.47181 | -0.34721 | -0.43103 | -0.35081 | 0.66085 | 6.7252 | 7.1562 | -0.27858 | -0.39443 | 122.7084 | 122.543 | 122.6676 | 69.1039 | -123.3557 | 122.664 | 122.7362 | 122.6204 | 6.9147 | -123.4459
573.2812 | 123.1522 | -76.2543 | 46.7926 | 0.057113 | -0.063054 | 0.086498 | 0.052318 | 0.0044828 | 0.13018 | 0.058893 | -0.0029117 | 0.077765 | 0.18631 | 0.051124 | 0.26817 | 29.6415 | -6.7337 | -49.1105 | 47.4384 | 47.2686 | 47.4069 | -75.6382 | -74.5358 | -72.7874 | -73.0868 | 47.3804 | 47.4618 | 47.3368 | -75.7146 | 0.61607 | 0.64584 | 105.8958 | 27.1438 | 26.5277 | 0.47599 | 0.61428 | 0.53964 | 0.58776 | 1.7185 | 3.1675 | 2.6279 | 0.66916 | 0.54416 | 123.6927 | 123.5229 | 123.6612 | 69.5206 | -122.4308 | 123.6346 | 123.716 | 123.591 | 3.4669 | -122.5072
574.2812 | 123.23 | -75.7462 | 47.2366 | 0.072375 | -0.064123 | 0.099318 | 0.054455 | 0.0055508 | 0.14193 | 0.043632 | 0.0013613 | 0.10875 | 0.14785 | 0.050056 | 0.2671 | 28.996 | -11.4405 | -50.4885 | 46.8845 | 46.7237 | 46.8437 | -76.1465 | -75.0944 | -74.2801 | -74.2086 | 46.8447 | 46.9306 | 46.7965 | -76.2549 | -0.40031 | -0.35218 | 104.7421 | 25.2576 | 25.6579 | -0.51293 | -0.39292 | -0.50878 | -0.39195 | 0.65178 | 1.5376 | 2.0464 | -0.30599 | -0.44014 | 122.6306 | 122.4699 | 122.5899 | 64.3056 | -123.3831 | 122.5908 | 122.6768 | 122.5426 | 1.4661 | -123.4916
575.2812 | 123.1522 | -73.7778 | 49.1913 | 0.057113 | -0.063054 | 0.09825 | 0.054455 | 0.0055508 | 0.143 | 0.043632 | 0.022725 | 0.144 | 0.16815 | 0.08638 | 0.30769 | 29.3806 | -11.2665 | -50.1909 | 46.7792 | 46.6275 | 46.7659 | -76.3159 | -74.7281 | -74.1976 | -19.8272 | 46.7394 | 46.8162 | 46.7232 | -76.3236 | -2.5381 | -2.4121 | 103.1583 | 23.5868 | 26.1249 | -2.5637 | -2.4254 | -2.5458 | -2.4519 | -0.95031 | 53.9506 | 56.4964 | -2.3751 | -2.4681 | 120.5569 | 120.4053 | 120.5436 | 62.5112 | -125.5072 | 120.5171 | 120.594 | 120.501 | -0.41986 | -125.5149
576.3125 | 123.1888 | -76.7258 | 46.3394 | 0.072375 | -0.060917 | 0.10787 | 0.056591 | 0.0055508 | 0.15582 | 0.074154 | 0.023793 | 0.15789 | 0.17242 | 0.095995 | 0.31304 | 28.7213 | -19.0227 | -51.2256 | 46.2481 | 46.0735 | 46.2027 | -76.8699 | -75.1859 | -74.3991 | -13.9024 | 46.1716 | 46.2576 | 46.128 | -76.8914 | -0.14417 | -0.091356 | 105.447 | 25.5001 | 25.6443 | -0.26592 | -0.13671 | -0.16562 | -0.16778 | 1.5398 | 62.8234 | 62.989 | -0.081825 | -0.2114 | 122.9738 | 122.7993 | 122.9285 | 57.7031 | -123.2094 | 122.8974 | 122.9834 | 122.8538 | 2.3267 | -123.2308
577.2812 | 123.111 | -73.9471 | 48.8068 | 0.072375 | -0.064123 | 0.12817 | 0.059797 | 0.0012778 | 0.18573 | 0.089415 | 0.36348 | 0.18566 | 0.50571 | 0.10241 | 1.0117 | 4.1079 | -24.7688 | -45.4845 | 55.6887 | 55.5564 | 55.6072 | -67.4007 | -65.7813 | -50.6173 | 4.0782 | 55.5072 | 55.5613 | 55.5782 | -67.372 | 6.5464 | 6.8819 | 78.055 | 28.4627 | 21.9163 | 6.7497 | 6.8004 | 6.5751 | 6.7004 | 8.1659 | 78.0254 | 71.4503 | 6.7545 | 6.7715 | 129.6358 | 129.5036 | 129.5543 | 49.1783 | -116.2075 | 129.4543 | 129.5085 | 129.5254 | 23.3299 | -116.1788
578.2812 | 123.0927 | -70.079 | 52.9633 | 0.041851 | -0.064123 | 0.11321 | 0.055523 | 0.0034148 | 0.16009 | 0.074154 | 0.55682 | 0.25296 | 1.0452 | 0.085312 | 1.8278 | 34.3573 | -18.1115 | -45.0907 | 51.2477 | 51.092 | 51.2025 | -71.7232 | -69.1649 | -48.36 | -22.84 | 51.0111 | 51.1018 | 50.9676 | -71.6303 | -1.6442 | -1.7156 | 104.4363 | 24.9883 | 26.6325 | -1.8713 | -1.7607 | -1.5513 | -1.9521 | 0.9141 | 47.239 | 48.7903 | -1.8615 | -1.9957 | 121.3267 | 121.171 | 121.2816 | 51.9675 | -124.6865 | 121.0902 | 121.1808 | 121.0466 | 21.7191 | -124.5936
579.2812 | 123.2437 | -81.958 | 40.9424 | 0.057113 | -0.061986 | 0.12069 | 0.056591 | 0.0055508 | 0.17184 | 0.058893 | 0.30793 | 0.61084 | 0.090166 | 0.14087 | 0.87708 | 24.5137 | -32.7081 | -55.1584 | 41.2988 | 41.1512 | 41.3723 | -81.7923 | -78.6154 | 34.272 | 41.0009 | 41.1673 | 41.2532 | 41.1053 | -81.6946 | 0.16573 | 0.35644 | 106.4717 | 26.7996 | 26.6339 | 0.20877 | 0.4299 | 0.26344 | 0.22496 | 3.3426 | 122.9589 | 122.6955 | 0.3108 | 0.1629 | 123.2568 | 123.1092 | 123.3303 | 49.2499 | -122.7347 | 123.1254 | 123.2112 | 123.0633 | 116.23 | -122.637
580.2812 | 123.1476 | -83.7433 | 39.267 | 0.057113 | -0.060917 | 0.11855 | 0.05766 | 0.0076878 | 0.16971 | 0.089415 | 0.26414 | 0.14934 | 0.080552 | 0.14194 | 0.34508 | 22.133 | -35.2309 | -56.9714 | 39.4354 | 39.2784 | 39.4218 | -83.5643 | 33.0044 | 30.8013 | 39.577 | 39.368 | 39.4492 | 39.3288 | -83.6635 | 0.17896 | 0.16845 | 105.8763 | 26.7719 | 26.5929 | 0.011406 | 0.15483 | 0.079827 | 0.10103 | 116.7477 | 123.3202 | 123.2404 | 0.18224 | 0.061821 | 123.1787 | 123.0217 | 123.1651 | 48.5123 | -122.8313 | 123.1113 | 123.1925 | 123.0721 | 114.5446 | -122.9304
581.2812 | 123.1293 | -81.1981 | 41.8304 | 0.072375 | -0.060917 | 0.12282 | 0.056591 | 0.0055508 | 0.17825 | 0.074154 | 0.215 | 0.16857 | 0.092302 | 0.143 | 0.32906 | 25.1639 | -30.46 | -52.8372 | 42.242 | 42.0853 | 42.2285 | -80.7712 | 38.7186 | -71.1757 | 42.4066 | 42.1746 | 42.2651 | 42.1492 | -80.8704 | 0.42694 | 0.41153 | 106.362 | 28.3609 | 27.934 | 0.25481 | 0.39804 | 0.32774 | 0.34417 | 119.9167 | 123.6047 | 123.277 | 0.43461 | 0.31876 | 123.4401 | 123.2834 | 123.4266 | 50.7381 | -122.6016 | 123.3727 | 123.4632 | 123.3473 | 10.0224 | -122.7008
582.2812 | 123.0377 | -74.3179 | 48.6328 | 0.041851 | -0.063054 | 0.1271 | 0.061933 | 0.0076878 | 0.18359 | 0.089415 | 0.49807 | 0.79352 | 0.095507 | 0.14194 | 1.2638 | -28.3346 | -36.3069 | -46.2674 | 47.5163 | 47.3648 | 47.4572 | -75.455 | 17.5055 | -66.8534 | 47.5622 | 47.3575 | 47.4434 | 47.3184 | -75.4079 | -1.1371 | -1.1165 | 45.9833 | 28.0506 | 29.1877 | -1.2681 | -1.1756 | -1.0899 | -1.2753 | 91.8234 | 121.8802 | 122.9701 | -1.1894 | -1.3144 | 121.8342 | 121.6827 | 121.7752 | 38.011 | -124.0879 | 121.6754 | 121.7614 | 121.6364 | 7.4645 | -124.0407
583.2812 | 123.1705 | -78.7216 | 44.2703 | 0.072375 | -0.063054 | 0.59719 | 0.05766 | 0.0098238 | 0.64831 | 0.058893 | 0.26841 | 0.18459 | 0.09337 | 0.143 | 0.3985 | 30.1543 | -36.6549 | -47.1555 | 45.2958 | 45.1302 | 45.2641 | -77.598 | 40.1289 | -63.4606 | 45.511 | 45.2697 | 45.3556 | 45.2215 | -77.7064 | 1.1236 | 1.0254 | 108.8759 | 31.5661 | 30.4424 | 0.85991 | 0.99377 | 1.0152 | 0.99935 | 118.8505 | 124.2326 | 123.2174 | 1.0853 | 0.95113 | 124.0174 | 123.8519 | 123.9857 | 42.0667 | -121.8683 | 123.9913 | 124.0772 | 123.9431 | 15.2611 | -121.9767
584.2812 | 123.1934 | -75.9109 | 47.0444 | 0.041851 | -0.061986 | 0.11855 | 0.061933 | 0.0087558 | 0.17825 | 0.074154 | 0.28977 | 0.24869 | 0.090166 | 0.14407 | 0.47648 | -66.001 | -20.4375 | -41.0847 | 48.4365 | 48.2439 | 48.3959 | -74.6537 | 45.4447 | -35.068 | 48.5558 | 48.319 | 48.4187 | 48.2845 | -74.6478 | 1.2572 | 1.3922 | 9.91 | 34.8262 | 33.569 | 1.1995 | 1.3515 | 1.2632 | 1.2746 | 121.3557 | 124.4668 | 123.2036 | 1.3743 | 1.2402 | 124.3475 | 124.1549 | 124.3068 | 55.4735 | -121.6981 | 124.2299 | 124.3296 | 124.1955 | 40.843 | -121.6921
585.2812 | 122.9782 | -69.4748 | 53.476 | 0.072375 | -0.059849 | 0.16556 | 0.065139 | 0.0055508 | 0.23274 | 0.058893 | 0.68821 | 0.87791 | 0.091234 | 0.143 | 1.5074 | -62.8007 | -38.1338 | -41.5334 | 53.8482 | 53.6882 | 53.7803 | -69.0995 | 46.7543 | -35.4526 | 53.803 | 53.6621 | 53.7345 | 53.6415 | -69.0204 | 0.37529 | 0.37223 | 6.6741 | 27.9414 | 27.5661 | 0.2123 | 0.30434 | 0.45439 | 0.18611 | 116.229 | 123.2778 | 122.8234 | 0.2585 | 0.16555 | 123.323 | 123.163 | 123.2551 | 31.341 | -122.5755 | 123.1369 | 123.2092 | 123.1163 | 34.0222 | -122.4964
586.2812 | 123.0698 | -68.7744 | 54.1077 | 0.057113 | -0.059849 | 0.21684 | 0.068344 | 0.0098238 | 0.28295 | 0.074154 | 0.9168 | 0.35445 | 0.090166 | 0.14194 | 1.2136 | -65.9964 | -35.4461 | -38.4293 | 53.9855 | 53.7981 | 53.9268 | -68.9484 | 45.5729 | -19.2669 | 54.0228 | 53.7994 | 53.8993 | 53.7743 | -68.9197 | -0.17398 | -0.12213 | 2.778 | 30.3451 | 30.5191 | -0.30952 | -0.18086 | -0.14525 | -0.30825 | 114.3474 | 122.7972 | 122.9425 | -0.20839 | -0.33339 | 122.76 | 122.5726 | 122.7012 | 33.3283 | -123.0561 | 122.5738 | 122.6737 | 122.5487 | 49.5076 | -123.0273
587.2812 | 123.0469 | -69.8502 | 53.0594 | 0.041851 | -0.059849 | 1.0897 | 0.06407 | 0.0087558 | 1.1611 | 0.089415 | 0.55362 | 0.29997 | 0.091234 | 0.143 | 0.78628 | -66.7518 | -35.8857 | -40.8741 | 52.6761 | 52.4977 | 52.6173 | -70.0153 | 49.4603 | -50.0358 | 52.8918 | 52.6639 | 52.7592 | 52.6342 | -70.1514 | -0.16513 | -0.38327 | 3.0983 | 28.976 | 29.1411 | -0.56166 | -0.44206 | -0.30121 | -0.39544 | 119.3104 | 122.742 | 123.0432 | -0.30018 | -0.42518 | 122.5263 | 122.3479 | 122.4675 | 33.9645 | -123.0747 | 122.5141 | 122.6094 | 122.4844 | 19.8144 | -123.2108
588.2812 | 123.0606 | -81.8298 | 41.1713 | 0.041851 | -0.061986 | 0.16449 | 0.058728 | 0.011961 | 0.21992 | 0.074154 | 0.72132 | 0.30104 | 0.078415 | 0.14087 | 0.954 | -34.14 | -11.8205 | -46.4551 | 38.094 | 37.9505 | 38.1673 | -84.9105 | 34.4604 | 27.4268 | 38.185 | 37.9899 | 38.0711 | 37.9186 | -84.8219 | -3.0807 | -3.0773 | 47.6898 | 35.3748 | 38.4555 | -3.2208 | -3.004 | -2.9921 | -3.1814 | 116.2903 | 120.0149 | 123.0069 | -3.1002 | -3.2527 | 119.9238 | 119.7803 | 119.9971 | 70.0093 | -126.0818 | 119.8197 | 119.9009 | 119.7484 | 109.2567 | -125.9932
589.2812 | 122.9004 | -85.405 | 38.4064 | 0.057113 | -0.065191 | 0.13564 | 0.059797 | 0.015166 | 0.18146 | 0.043632 | 0.86339 | 0.19741 | 0.080552 | 0.14194 | 0.99459 | 11.2456 | -11.294 | -46.4596 | 35.0722 | 34.9604 | 35.0904 | -87.9601 | 32.8991 | 23.1824 | 35.0257 | 34.8353 | 34.9439 | 34.9562 | -87.9172 | -2.5551 | -3.3342 | 96.6505 | 38.9453 | 41.5004 | -3.4459 | -3.3159 | -2.5122 | -3.5711 | 118.304 | 120.4307 | 122.9429 | -3.4625 | -3.4501 | 120.4772 | 120.3654 | 120.4954 | 74.111 | -126.3665 | 120.2403 | 120.3488 | 120.3612 | 108.5873 | -126.3236
590.2812 | 123.0743 | -88.3392 | 34.584 | 0.072375 | -0.063054 | 1.531 | 0.061933 | 0.011961 | 1.5916 | 0.089415 | 0.14877 | 0.0040533 | -0.019863 | 0.060739 | 0.085495 | -24.4613 | -23.4044 | -49.083 | 34.6876 | 34.5575 | 34.6921 | -87.9235 | 35.0328 | 34.7848 | 35.0852 | 34.8536 | 34.9301 | 34.8189 | 8.5081 | 0.41577 | 0.10359 | 63.878 | 39.2562 | 38.8405 | -0.026542 | 0.10806 | 96.8474 | 0.26955 | 123.372 | 123.4245 | 26.5771 | 0.34608 | 0.23482 | 123.0269 | 122.8967 | 123.0313 | 64.9348 | -122.5075 | 123.1928 | 123.2694 | 123.1581 | 123.1241 | -26.0759
591.2812 | 123.0927 | -95.2057 | 27.7405 | 0.057113 | -0.065191 | 0.15701 | 0.059797 | 0.017303 | 0.19855 | 0.058893 | 0.1477 | 0.0072583 | -0.019863 | 0.058603 | 0.085495 | 20.6496 | -11.7336 | -50.2642 | 27.6323 | 27.4831 | 27.6594 | -95.4008 | 27.7984 | 27.697 | 27.8463 | 27.6333 | 27.7234 | 27.5572 | 8.5219 | -0.19516 | -0.10814 | 115.8553 | 44.9415 | 45.1367 | -0.25742 | -0.081112 | 103.7276 | -0.10717 | 123.0041 | 123.052 | 19.3244 | -0.01707 | -0.18328 | 122.838 | 122.6888 | 122.8651 | 83.4721 | -123.1413 | 122.839 | 122.9291 | 122.7629 | 122.9027 | -19.2186
592.2812 | 123.1476 | -95.0088 | 27.9785 | 0.072375 | -0.065191 | 0.16235 | 0.060865 | 0.016234 | 0.20603 | 0.058893 | 0.1477 | 0.0083263 | -0.019863 | 0.058603 | 0.084427 | 20.0132 | -8.849 | -50.2734 | 27.0875 | 26.9382 | 27.0916 | -95.9732 | 27.249 | 27.1201 | 27.3014 | 27.0931 | 27.174 | 27.0078 | 8.5402 | -0.96436 | -0.89101 | 115.022 | 44.7355 | 45.6999 | -1.0403 | -0.8869 | 103.549 | -0.88546 | 122.2578 | 122.3103 | 18.7613 | -0.80454 | -0.97075 | 122.0964 | 121.947 | 122.1005 | 86.1598 | -123.9517 | 122.1019 | 122.1828 | 122.0166 | 122.1289 | -19.4383
593.2812 | 123.1384 | -95.0088 | 27.9785 | 0.087637 | -0.064123 | 0.17624 | 0.061933 | 0.016234 | 0.22099 | 0.058893 | 0.14664 | 0.0061893 | -0.020931 | 0.058603 | 0.085495 | 18.7953 | -9.5312 | -50.0307 | 27.3073 | 27.1763 | 27.3389 | -95.7168 | 27.4962 | 27.3444 | 27.5487 | 27.3357 | 27.4121 | 27.2184 | 8.5356 | -0.70794 | -0.67124 | 113.8042 | 44.9781 | 45.6861 | -0.80224 | -0.63965 | 103.5445 | -0.6428 | 122.505 | 122.5575 | 19.0131 | -0.56645 | -0.76013 | 122.3161 | 122.1851 | 122.3477 | 85.4776 | -123.6953 | 122.3446 | 122.4209 | 122.2272 | 122.3533 | -19.4429
594.2812 | 123.0972 | -96.8399 | 26.1703 | 0.057113 | -0.064123 | 0.30338 | 0.063002 | 0.017303 | 0.34811 | 0.058893 | 0.1477 | 0.0072583 | -0.019863 | 0.059671 | 0.086563 | 20.2329 | -12.4432 | -49.582 | 28.1039 | 27.9867 | 28.1218 | -94.8285 | 28.3249 | 28.1777 | 28.3683 | 28.1598 | 28.2316 | 28.0654 | 8.5585 | 2.0114 | 1.9336 | 117.0728 | 47.2579 | 45.2464 | 1.8164 | 1.9515 | 105.3984 | 1.9895 | 125.1649 | 125.2082 | 19.8098 | 2.0613 | 1.8951 | 124.9438 | 124.8267 | 124.9617 | 84.3967 | -120.9988 | 124.9997 | 125.0715 | 124.9053 | 125.0176 | -17.6119
595.2812 | 123.0927 | -95.1645 | 27.887 | 0.072375 | -0.049165 | 0.16022 | 0.060865 | 0.020508 | 0.21778 | 0.043632 | 0.14557 | 0.0072583 | -0.017727 | 0.059671 | 0.085495 | 19.4546 | -9.664 | -47.7553 | 27.3027 | 27.1763 | 27.3114 | -95.7259 | 27.4825 | 27.3673 | 27.5395 | 27.322 | 27.3983 | 27.1634 | 8.5493 | -0.56146 | -0.58427 | 114.6191 | 47.4092 | 47.9707 | -0.71069 | -0.57557 | 103.7138 | -0.56499 | 122.647 | 122.704 | 18.9902 | -0.48864 | -0.72352 | 122.4672 | 122.3408 | 122.4759 | 85.5005 | -123.6129 | 122.4865 | 122.5628 | 122.3279 | 122.5318 | -19.3376
596.2812 | 123.0515 | -93.4662 | 29.4937 | 0.057113 | 0.24677 | 0.67304 | 0.067275 | 0.019439 | 1.0532 | 0.058893 | 0.14557 | 0.0072583 | -0.016658 | 0.060739 | 0.085495 | 24.3352 | -17.3378 | -46.8122 | 29.0654 | 28.8888 | 29.0787 | -93.725 | 29.3323 | 29.2308 | 29.3802 | 29.1534 | 29.2481 | 29.0361 | 8.5539 | -0.25877 | -0.42834 | 117.8014 | 46.654 | 46.9128 | -0.60492 | -0.41498 | 102.0201 | -0.34034 | 122.7985 | 122.8464 | 20.8263 | -0.24563 | -0.45762 | 122.5316 | 122.355 | 122.5449 | 76.1284 | -123.2187 | 122.6196 | 122.7143 | 122.5023 | 122.697 | -20.9398
597.2812 | 123.1155 | -109.1446 | 13.9023 | 0.057113 | 0.087585 | 0.013847 | -0.012856 | -0.046796 | 0.1227 | 0.058893 | 0.14343 | 0.0072583 | -0.019863 | 0.061808 | 0.084427 | 13.8644 | 13.4533 | 12.9161 | 13.8285 | 13.7005 | 13.8778 | 8.4766 | 13.9157 | 13.8784 | 13.9362 | 13.82 | 13.9006 | 13.6062 | 8.5631 | 117.6212 | -0.073786 | 123.009 | 122.0607 | 4.4394 | -0.20178 | -0.024509 | 117.7077 | -0.082289 | 123.0603 | 123.0808 | 5.3731 | -0.001675 | -0.29608 | 122.9731 | 122.8451 | 123.0224 | 122.5979 | -5.4256 | 122.9646 | 123.0452 | 122.7508 | 123.023 | -5.3392
598.2812 | 123.1338 | -109.2545 | 13.7604 | 0.057113 | 0.087585 | 0.013847 | -0.011787 | -0.04466 | 0.12163 | 0.058893 | 0.14236 | 0.0051213 | -0.019863 | 0.058603 | 0.087631 | 13.6309 | 13.1832 | 12.6597 | 13.5904 | 13.467 | 13.6397 | 8.5133 | 13.6868 | 13.6449 | 13.6981 | 13.5819 | 13.6625 | 13.3818 | 8.5585 | 117.7677 | -0.16996 | 122.8854 | 121.9141 | 4.1464 | -0.2934 | -0.12069 | 117.813 | -0.17846 | 122.9413 | 122.9525 | 5.1396 | -0.097855 | -0.37853 | 122.8449 | 122.7214 | 122.8941 | 122.4377 | -5.2471 | 122.8364 | 122.917 | 122.6363 | 122.8994 | -5.2019
599.2812 | 123.143 | -109.4009 | 13.6688 | 0.057113 | 0.086517 | 0.014916 | -0.012856 | -0.045728 | 0.12056 | 0.058893 | 0.14343 | 0.0072583 | -0.019863 | 0.060739 | 0.084427 | 13.6492 | 13.2153 | 12.6276 | 13.6087 | 13.4807 | 13.658 | 8.5453 | 13.7005 | 13.6632 | 13.7073 | 13.5911 | 13.6854 | 13.4276 | 8.5677 | 117.9463 | -0.060089 | 123.0502 | 122.0286 | 4.0823 | -0.18811 | -0.010822 | 117.9686 | -0.077754 | 123.1015 | 123.1082 | 5.1396 | 0.016591 | -0.24119 | 123.0097 | 122.8817 | 123.0589 | 122.6162 | -5.1235 | 122.992 | 123.0864 | 122.8286 | 123.0642 | -5.1012
600.2812 | 123.1705 | -109.1766 | 13.9023 | 0.057113 | 0.087585 | 0.012779 | -0.012856 | -0.04466 | 0.12163 | 0.043632 | 0.14236 | 0.0083263 | -0.018795 | 0.060739 | 0.086563 | 13.8003 | 12.6246 | 12.7696 | 13.7552 | 13.6318 | 13.7999 | 8.5224 | 13.8471 | 13.7502 | 13.8629 | 13.7467 | 13.8319 | 13.5467 | 8.5677 | 117.6991 | -0.14704 | 122.9769 | 121.9462 | 4.2471 | -0.27047 | -0.10235 | 117.7443 | -0.15555 | 123.0237 | 123.0396 | 5.2953 | -0.070354 | -0.35561 | 122.9319 | 122.8085 | 122.9766 | 121.8012 | -5.3799 | 122.9234 | 123.0086 | 122.7233 | 122.9269 | -5.3346
601.2812 | 123.1293 | -109.259 | 13.8336 | 0.072375 | 0.086517 | 0.013847 | -0.012856 | -0.045728 | 0.12056 | 0.058893 | 0.14343 | 0.0061893 | -0.019863 | 0.060739 | 0.085495 | 14.0018 | 12.9909 | 12.9848 | 13.9475 | 13.8287 | 14.0014 | 8.5362 | 14.044 | 13.9471 | 14.0598 | 13.939 | 14.0334 | 13.7573 | 8.5677 | 117.7952 | 0.11392 | 123.2608 | 122.2438 | 4.4486 | -0.004907 | 0.16778 | 117.8267 | 0.10542 | 123.303 | 123.3188 | 5.4922 | 0.19977 | -0.076324 | 123.2066 | 123.0877 | 123.2604 | 122.2499 | -5.2975 | 123.1981 | 123.2924 | 123.0163 | 123.2061 | -5.266
602.2812 | 123.143 | -109.0164 | 14.0945 | 0.057113 | 0.088654 | 0.012779 | -0.0096504 | -0.04466 | 0.12056 | 0.074154 | 0.14236 | 0.0061893 | -0.019863 | 0.060739 | 0.085495 | 14.0887 | 12.9772 | 12.9985 | 14.0299 | 13.9066 | 14.0838 | 8.5224 | 14.1355 | 14.0341 | 14.1468 | 14.0398 | 14.1112 | 13.8718 | 8.5585 | 117.5388 | -0.064597 | 123.1052 | 122.0149 | 4.4761 | -0.18799 | -0.010732 | 117.5749 | -0.054782 | 123.1519 | 123.1632 | 5.5883 | 0.016681 | -0.22278 | 123.0464 | 122.923 | 123.1002 | 121.9936 | -5.5721 | 123.0562 | 123.1276 | 122.8882 | 123.0505 | -5.536
603.2812 | 123.0743 | -108.8562 | 14.2456 | 0.087637 | 0.086517 | 0.017052 | -0.0096504 | -0.04466 | 0.1195 | 0.074154 | 0.14236 | 0.0083263 | -0.019863 | 0.060739 | 0.085495 | 14.1483 | 12.7528 | 12.9435 | 14.0986 | 13.9752 | 14.1433 | 8.5362 | 14.1905 | 14.0982 | 14.2109 | 14.0901 | 14.1753 | 13.8947 | 8.5722 | 117.3924 | -0.14698 | 123.0045 | 121.7997 | 4.4074 | -0.27037 | -0.10227 | 117.4284 | -0.15548 | 123.0467 | 123.0671 | 5.6387 | -0.070281 | -0.35095 | 122.9548 | 122.8314 | 122.9995 | 121.609 | -5.7094 | 122.9463 | 123.0315 | 122.7509 | 122.9544 | -5.6734
604.2812 | 123.1705 | -108.9569 | 14.1449 | 0.072375 | 0.086517 | 0.014916 | -0.011787 | -0.04466 | 0.1227 | 0.074154 | 0.14343 | 0.0072583 | -0.019863 | 0.059671 | 0.084427 | 14.1071 | 12.8444 | 12.8611 | 14.0437 | 13.9249 | 14.1021 | 8.5499 | 14.1447 | 14.0524 | 14.1605 | 14.0398 | 14.1158 | 13.858 | 8.5677 | 117.5068 | -0.10122 | 123.064 | 121.818 | 4.3112 | -0.22003 | -0.042772 | 117.5246 | -0.10514 | 123.1016 | 123.1175 | 5.5929 | -0.029095 | -0.28687 | 123.0006 | 122.8818 | 123.059 | 121.8013 | -5.595 | 122.9967 | 123.0727 | 122.8149 | 123.0093 | -5.5772
605.2812 | 123.1384 | -108.9066 | 14.2044 | 0.057113 | 0.086517 | 0.013847 | -0.010719 | -0.04466 | 0.12163 | 0.074154 | 0.14343 | 0.0061893 | -0.019863 | 0.060739 | 0.085495 | 14.1483 | 12.6521 | 12.7879 | 14.094 | 13.9661 | 14.1433 | 8.5224 | 14.1813 | 14.0936 | 14.2155 | 14.081 | 14.1662 | 13.9084 | 8.5631 | 117.429 | -0.11036 | 123.0548 | 121.6944 | 4.2655 | -0.23833 | -0.061075 | 117.4696 | -0.12344 | 123.0879 | 123.122 | 5.6524 | -0.03824 | -0.29602 | 123.0006 | 122.8726 | 123.0499 | 121.5586 | -5.682 | 122.9875 | 123.0727 | 122.8149 | 123.0002 | -5.6413
606.2812 | 123.1522 | -109.0851 | 14.0259 | 0.057113 | 0.086517 | 0.014916 | -0.010719 | -0.04466 | 0.12163 | 0.058893 | 0.14343 | 0.0051213 | -0.018795 | 0.062876 | 0.085495 | 13.9834 | 12.5056 | 12.5452 | 13.9384 | 13.8104 | 13.9785 | 8.5499 | 14.0211 | 13.9425 | 14.0461 | 13.9299 | 14.0059 | 13.7161 | 8.5677 | 117.635 | -0.087501 | 123.0685 | 121.6303 | 3.9953 | -0.21548 | -0.047376 | 117.6527 | -0.096002 | 123.1061 | 123.1312 | 5.4784 | -0.019963 | -0.30979 | 123.0235 | 122.8955 | 123.0636 | 121.5907 | -5.476 | 123.015 | 123.091 | 122.8012 | 123.0276 | -5.4582
607.2812 | 123.1567 | -109.2728 | 13.829 | 0.072375 | 0.086517 | 0.015984 | -0.011787 | -0.04466 | 0.1227 | 0.058893 | 0.14236 | 0.0072583 | -0.019863 | 0.062876 | 0.086563 | 13.7912 | 12.3591 | 12.4674 | 13.7278 | 13.6089 | 13.7908 | 8.5362 | 13.8288 | 13.7365 | 13.8492 | 13.7238 | 13.809 | 13.5513 | 8.5677 | 117.8089 | -0.10127 | 123.0639 | 121.7402 | 3.9312 | -0.22012 | -0.038261 | 117.8404 | -0.1052 | 123.1015 | 123.122 | 5.2815 | -0.020005 | -0.27778 | 123.0005 | 122.8817 | 123.0635 | 121.6318 | -5.2929 | 122.9966 | 123.0818 | 122.824 | 123.0093 | -5.2614
608.2812 | 123.2483 | -109.2957 | 13.7741 | 0.057113 | 0.086517 | 0.014916 | -0.0085824 | -0.043591 | 0.12591 | 0.074154 | 0.14236 | 0.0061893 | -0.017727 | 0.060739 | 0.084427 | 13.695 | 12.4277 | 12.4216 | 13.6454 | 13.5082 | 13.6901 | 8.5407 | 13.728 | 13.6403 | 13.7439 | 13.6369 | 13.7175 | 13.4597 | 8.5585 | 117.8364 | -0.12875 | 122.9907 | 121.7173 | 3.8809 | -0.26592 | -0.084058 | 117.8542 | -0.13725 | 123.0237 | 123.0395 | 5.1854 | -0.056645 | -0.31442 | 122.941 | 122.8038 | 122.9857 | 121.7234 | -5.2334 | 122.9325 | 123.0131 | 122.7553 | 122.936 | -5.2156
609.2812 | 123.2391 | -109.3277 | 13.71 | 0.057113 | 0.086517 | 0.013847 | -0.010719 | -0.043591 | 0.12484 | 0.058893 | 0.14236 | 0.0072583 | -0.019863 | 0.061808 | 0.083358 | 13.7225 | 12.5101 | 12.4033 | 13.6637 | 13.5402 | 13.7267 | 8.5362 | 13.7646 | 13.677 | 13.7805 | 13.6643 | 13.7495 | 13.4643 | 8.5631 | 117.8639 | -0.046347 | 123.0502 | 121.731 | 3.8671 | -0.16978 | 0.016658 | 117.8908 | -0.045697 | 123.0923 | 123.1082 | 5.2174 | 0.039492 | -0.24576 | 122.9914 | 122.8679 | 123.0544 | 121.8378 | -5.1739 | 122.992 | 123.0772 | 122.792 | 123.0047 | -5.1469
610.2812 | 123.2758 | -109.3826 | 13.6185 | 0.041851 | 0.088654 | 0.01171 | -0.011787 | -0.045728 | 0.12484 | 0.074154 | 0.14343 | 0.0083263 | -0.020931 | 0.060739 | 0.084427 | 13.6309 | 12.5147 | 12.4399 | 13.5767 | 13.4441 | 13.6214 | 8.5362 | 13.6685 | 13.5717 | 13.6798 | 13.5682 | 13.6396 | 13.3956 | 8.5677 | 117.9188 | -0.041784 | 123.0135 | 121.8226 | 3.9038 | -0.17439 | 0.002903 | 117.9503 | -0.050293 | 123.0511 | 123.0624 | 5.1121 | 0.021159 | -0.22288 | 122.9593 | 122.8267 | 123.004 | 121.8974 | -5.0823 | 122.9508 | 123.0223 | 122.7782 | 122.9543 | -5.0508
611.2812 | 123.2208 | -109.5749 | 13.4949 | 0.057113 | 0.087585 | 0.013847 | -0.010719 | -0.04466 | 0.12591 | 0.058893 | 0.1445 | 0.0061893 | -0.020931 | 0.062876 | 0.084427 | 13.4661 | 12.4827 | 12.3758 | 13.421 | 13.2884 | 13.4657 | 8.5453 | 13.5128 | 13.4251 | 13.5241 | 13.4171 | 13.4931 | 13.2491 | 8.5677 | 118.1202 | -0.073853 | 123.041 | 121.9507 | 3.8305 | -0.20647 | -0.029174 | 118.1425 | -0.077787 | 123.0877 | 123.099 | 4.9564 | -0.001761 | -0.2458 | 122.9959 | 122.8633 | 123.0406 | 122.0576 | -4.9496 | 122.992 | 123.068 | 122.824 | 123 | -4.9272
612.2812 | 123.2712 | -109.7305 | 13.3026 | 0.057113 | 0.086517 | 0.013847 | -0.011787 | -0.043591 | 0.12484 | 0.058893 | 0.14236 | 0.0072583 | -0.023068 | 0.062876 | 0.084427 | 13.3287 | 12.5788 | 12.4903 | 13.2791 | 13.1465 | 13.3329 | 8.5545 | 13.3709 | 13.274 | 13.3822 | 13.2706 | 13.3466 | 13.098 | 8.5677 | 118.285 | -0.023522 | 123.0593 | 122.2208 | 3.9358 | -0.15616 | 0.030308 | 118.2982 | -0.032038 | 123.1014 | 123.1127 | 4.8145 | 0.043985 | -0.20464 | 123.0096 | 122.877 | 123.0635 | 122.3094 | -4.7481 | 123.0011 | 123.0771 | 122.8285 | 123.0046 | -4.735
613.2812 | 123.2986 | -109.8267 | 13.1836 | 0.087637 | 0.087585 | 0.013847 | -0.012856 | -0.043591 | 0.12591 | 0.074154 | 0.14236 | 0.0061893 | -0.018795 | 0.061808 | 0.085495 | 13.2463 | 13.1466 | 12.971 | 13.2013 | 13.0778 | 13.2505 | 8.5407 | 13.293 | 13.1962 | 13.2997 | 13.1973 | 13.2825 | 13.0156 | 8.5677 | 118.3674 | 0.017664 | 123.073 | 122.7977 | 4.4303 | -0.10583 | 0.066911 | 118.3943 | 0.013724 | 123.1197 | 123.1264 | 4.7321 | 0.098903 | -0.16803 | 123.0279 | 122.9044 | 123.0772 | 122.9732 | -4.6429 | 123.024 | 123.1092 | 122.8422 | 123.0229 | -4.6159
614.2812 | 123.2895 | -110.0372 | 13.0005 | 0.072375 | 0.086517 | 0.012779 | -0.010719 | -0.04466 | 0.12377 | 0.074154 | 0.1445 | 0.0093943 | -0.020931 | 0.065013 | 0.086563 | 12.9899 | 12.9039 | 12.765 | 12.9449 | 12.8213 | 12.9941 | 8.5362 | 13.0366 | 12.9444 | 13.0525 | 12.9409 | 13.0215 | 12.7408 | 8.5768 | 118.5734 | -0.05562 | 123.0272 | 122.8022 | 4.2288 | -0.17914 | -0.006385 | 118.614 | -0.059565 | 123.0739 | 123.0897 | 4.4757 | 0.021028 | -0.25964 | 122.9821 | 122.8586 | 123.0313 | 122.9411 | -4.4643 | 122.9782 | 123.0587 | 122.7781 | 122.9816 | -4.4237
615.2812 | 123.2941 | -110.0006 | 13.028 | 0.072375 | 0.086517 | 0.01171 | -0.014993 | -0.04466 | 0.12484 | 0.058893 | 0.14343 | 0.0083263 | -0.019863 | 0.060739 | 0.084427 | 13.0586 | 12.968 | 12.8154 | 12.9998 | 12.8809 | 13.0582 | 8.5362 | 13.0962 | 13.0131 | 13.1166 | 13.005 | 13.0856 | 12.8049 | 8.5768 | 118.5368 | -0.028145 | 123.0592 | 122.816 | 4.2792 | -0.14708 | 0.03025 | 118.5774 | -0.022933 | 123.0968 | 123.1172 | 4.5398 | 0.057663 | -0.22301 | 123.0004 | 122.8815 | 123.0588 | 122.9686 | -4.4918 | 123.0056 | 123.0862 | 122.8056 | 123.0137 | -4.4511
616.2812 | 123.3078 | -110.0555 | 12.9593 | 0.041851 | 0.087585 | 0.014916 | -0.012856 | -0.042523 | 0.12591 | 0.058893 | 0.1445 | 0.0093943 | -0.022 | 0.062876 | 0.084427 | 12.9945 | 12.9131 | 12.765 | 12.9403 | 12.8122 | 12.9941 | 8.5453 | 13.0321 | 12.9489 | 13.0433 | 12.9455 | 13.0169 | 12.7363 | 8.5631 | 118.6009 | -0.019 | 123.0501 | 122.8205 | 4.2197 | -0.1471 | 0.034813 | 118.6186 | -0.013789 | 123.0876 | 123.0989 | 4.4803 | 0.057648 | -0.22302 | 122.9958 | 122.8677 | 123.0496 | 122.9686 | -4.414 | 123.001 | 123.0725 | 122.7918 | 123.0045 | -4.3962
617.2812 | 123.3078 | -110.2432 | 12.7716 | 0.072375 | 0.087585 | 0.01171 | -0.011787 | -0.043591 | 0.12377 | 0.058893 | 0.1445 | 0.0083263 | -0.020931 | 0.063944 | 0.084427 | 12.8343 | 12.7849 | 12.6872 | 12.7984 | 12.6702 | 12.8476 | 8.5407 | 12.881 | 12.7933 | 12.8922 | 12.7898 | 12.8704 | 12.5943 | 8.5722 | 118.784 | 0.026753 | 123.0775 | 122.9304 | 4.1464 | -0.10136 | 0.075982 | 118.8155 | 0.018226 | 123.1242 | 123.1355 | 4.32 | 0.098816 | -0.17728 | 123.0416 | 122.9135 | 123.0908 | 123.0281 | -4.2309 | 123.0331 | 123.1136 | 122.8376 | 123.0365 | -4.1994
618.2812 | 123.3261 | -110.376 | 12.6617 | 0.087637 | 0.087585 | 0.014916 | -0.013924 | -0.04466 | 0.12591 | 0.043632 | 0.14236 | 0.0072583 | -0.022 | 0.062876 | 0.085495 | 12.5458 | 12.6704 | 12.5452 | 12.5832 | 12.4505 | 12.6324 | 8.527 | 12.6749 | 12.5781 | 12.6679 | 12.5838 | 12.6552 | 12.3746 | 8.5722 | 118.903 | -0.078568 | 122.9218 | 122.9212 | 4.0182 | -0.21129 | -0.029349 | 118.9482 | -0.077943 | 123.0509 | 123.0439 | 4.0957 | -0.006515 | -0.28719 | 122.9592 | 122.8264 | 123.0084 | 123.0464 | -4.1347 | 122.9598 | 123.0312 | 122.7505 | 122.9541 | -4.0895
619.2812 | 123.3215 | -110.5362 | 12.4741 | 0.072375 | 0.087585 | 0.010642 | -0.013924 | -0.04466 | 0.12484 | 0.058893 | 0.14236 | 0.0083263 | -0.020931 | 0.061808 | 0.084427 | 12.3719 | 12.5285 | 12.4125 | 12.4367 | 12.3177 | 12.4905 | 8.5362 | 12.5192 | 12.427 | 12.5214 | 12.4327 | 12.5133 | 12.2235 | 8.5768 | 119.0724 | -0.037393 | 122.908 | 122.9487 | 3.8763 | -0.15639 | 0.016397 | 119.113 | -0.04135 | 123.0554 | 123.0576 | 3.9446 | 0.039231 | -0.2506 | 122.9729 | 122.8539 | 123.0267 | 123.0647 | -3.9379 | 122.9689 | 123.0495 | 122.7597 | 122.9632 | -3.8972
620.2812 | 123.2941 | -110.6873 | 12.355 | 0.072375 | 0.086517 | 0.012779 | -0.011787 | -0.04466 | 0.12591 | 0.074154 | 0.14236 | 0.0083263 | -0.018795 | 0.062876 | 0.084427 | 12.2849 | 12.4552 | 12.3301 | 12.3634 | 12.2215 | 12.408 | 8.5362 | 12.4368 | 12.2942 | 12.384 | 12.3549 | 12.4355 | 12.1685 | 8.5677 | 119.2234 | 0.008371 | 122.9721 | 123.0173 | 3.7939 | -0.13353 | 0.053 | 119.2549 | -0.000167 | 123.1241 | 123.0713 | 3.8163 | 0.080413 | -0.18652 | 123.0507 | 122.9088 | 123.0953 | 123.1425 | -3.8189 | 123.0421 | 123.1227 | 122.8558 | 122.9815 | -3.7874
621.2812 | 123.2483 | -110.6735 | 12.4054 | 0.057113 | 0.088654 | 0.012779 | -0.012856 | -0.043591 | 0.12484 | 0.058893 | 0.14023 | 0.0083263 | -0.020931 | 0.062876 | 0.084427 | 12.294 | 12.4415 | 12.3255 | 12.3451 | 12.2124 | 12.3989 | 8.5545 | 12.3865 | 12.2713 | 12.3748 | 12.3411 | 12.4171 | 12.1273 | 8.5677 | 119.228 | -0.060297 | 122.9675 | 122.999 | 3.771 | -0.19304 | -0.006511 | 119.2412 | -0.064256 | 123.06 | 123.0484 | 3.8072 | 0.011745 | -0.27808 | 123.0186 | 122.8859 | 123.0724 | 123.115 | -3.8509 | 123.0147 | 123.0907 | 122.8008 | 122.9448 | -3.8377
622.2812 | 123.2849 | -110.9161 | 12.1536 | 0.087637 | 0.086517 | 0.012779 | -0.011787 | -0.042523 | 0.12484 | 0.058893 | 0.14236 | 0.0083263 | -0.019863 | 0.062876 | 0.084427 | 12.0697 | 12.208 | 12.0874 | 12.1208 | 11.9788 | 12.1791 | 8.5316 | 12.1575 | 12.0515 | 12.1459 | 12.1168 | 12.1882 | 11.8892 | 8.5722 | 119.4477 | -0.032867 | 122.9858 | 123.0035 | 3.5558 | -0.1748 | 0.025487 | 119.4884 | -0.036832 | 123.0737 | 123.062 | 3.5737 | 0.034586 | -0.2644 | 123.0369 | 122.895 | 123.0953 | 123.1241 | -3.622 | 123.0329 | 123.1043 | 122.8054 | 122.9677 | -3.5814
623.2812 | 123.3215 | -111.0214 | 12.0758 | 0.057113 | 0.087585 | 0.012779 | -0.012856 | -0.04466 | 0.12591 | 0.043632 | 0.14129 | 0.0072583 | -0.020931 | 0.063944 | 0.084427 | 12.1109 | 12.1576 | 12.037 | 12.075 | 11.9376 | 12.1242 | 8.5407 | 12.1163 | 12.0241 | 12.1184 | 12.0802 | 12.1516 | 11.8663 | 8.5677 | 119.5622 | -0.000832 | 123.1323 | 123.0585 | 3.4963 | -0.13819 | 0.048363 | 119.5891 | 0.004359 | 123.1377 | 123.1399 | 3.5508 | 0.075776 | -0.20947 | 123.0964 | 122.959 | 123.1456 | 123.179 | -3.5351 | 123.1016 | 123.173 | 122.8878 | 123.0455 | -3.5082
624.2812 | 123.2574 | -111.1359 | 11.9385 | 0.072375 | 0.086517 | 0.01171 | -0.014993 | -0.04466 | 0.12591 | 0.058893 | 0.14129 | 0.0083263 | -0.018795 | 0.062876 | 0.085495 | 11.9323 | 11.9653 | 11.8539 | 11.8918 | 11.7636 | 11.9364 | 8.5407 | 11.924 | 11.8409 | 11.9307 | 11.8924 | 11.973 | 11.7015 | 8.5631 | 119.6766 | -0.046638 | 123.0682 | 122.9898 | 3.3132 | -0.17486 | -0.002031 | 119.6989 | -0.04603 | 123.0599 | 123.0666 | 3.3676 | 0.034539 | -0.23698 | 123.0277 | 122.8995 | 123.0723 | 123.1012 | -3.3977 | 123.0283 | 123.1089 | 122.8374 | 122.9768 | -3.3754
625.2812 | 123.2986 | -111.145 | 11.9247 | 0.087637 | 0.087585 | 0.01171 | -0.012856 | -0.043591 | 0.12484 | 0.074154 | 0.14236 | 0.0083263 | -0.022 | 0.061808 | 0.084427 | 11.9323 | 11.892 | 11.7715 | 11.8781 | 11.7453 | 11.9319 | 8.5316 | 11.9149 | 11.8363 | 11.9353 | 11.8741 | 11.9547 | 11.6557 | 8.5677 | 119.6766 | -0.04664 | 123.0773 | 122.9165 | 3.2399 | -0.17944 | 0.007123 | 119.7127 | -0.050611 | 123.0599 | 123.0803 | 3.3676 | 0.029958 | -0.26903 | 123.0231 | 122.8903 | 123.0769 | 123.0371 | -3.3932 | 123.0192 | 123.0997 | 122.8007 | 122.9813 | -3.3571
626.2812 | 123.3032 | -111.0718 | 12.0163 | 0.072375 | 0.086517 | 0.01171 | -0.012856 | -0.04466 | 0.12484 | 0.074154 | 0.1445 | 0.0083263 | -0.019863 | 0.063944 | 0.085495 | 11.9873 | 11.9241 | 11.8127 | 11.9559 | 11.8231 | 12.0097 | 8.5362 | 11.9973 | 11.9187 | 12.0131 | 11.9565 | 12.0371 | 11.7793 | 8.5631 | 119.6079 | -0.06036 | 123.059 | 122.8845 | 3.2765 | -0.19315 | -0.006592 | 119.6349 | -0.05975 | 123.069 | 123.0849 | 3.4501 | 0.020821 | -0.23696 | 123.0277 | 122.8949 | 123.0815 | 122.9959 | -3.4801 | 123.0283 | 123.1089 | 122.8511 | 122.9905 | -3.4532
627.2812 | 123.2758 | -111.1633 | 11.9293 | 0.057113 | 0.085449 | 0.012779 | -0.011787 | -0.04466 | 0.12591 | 0.074154 | 0.14343 | 0.0061893 | -0.020931 | 0.063944 | 0.083358 | 11.8682 | 11.48 | 11.3869 | 11.8277 | 11.6995 | 11.8907 | 8.5133 | 11.8645 | 11.8043 | 11.8941 | 11.8283 | 11.9089 | 11.6328 | 8.5631 | 119.6766 | -0.10158 | 123.0316 | 122.5503 | 2.8737 | -0.22981 | -0.038661 | 119.7264 | -0.10097 | 123.0278 | 123.0574 | 3.331 | -0.020405 | -0.2965 | 122.9911 | 122.8628 | 123.054 | 122.6433 | -3.4161 | 122.9917 | 123.0722 | 122.7962 | 122.9676 | -3.3662
628.2812 | 123.2803 | -111.3144 | 11.7691 | 0.072375 | 0.086517 | 0.013847 | -0.010719 | -0.04466 | 0.12484 | 0.058893 | 0.14236 | 0.0093943 | -0.020931 | 0.063944 | 0.083358 | 11.7629 | 11.3563 | 11.2771 | 11.7224 | 11.5896 | 11.767 | 8.527 | 11.7592 | 11.6852 | 11.7796 | 11.723 | 11.799 | 11.5184 | 8.5631 | 119.8414 | -0.046666 | 123.0773 | 122.5914 | 2.75 | -0.17949 | -0.002066 | 119.8775 | -0.046061 | 123.0736 | 123.094 | 3.2165 | 0.029925 | -0.25075 | 123.0368 | 122.904 | 123.0814 | 122.6707 | -3.2421 | 123.0374 | 123.1134 | 122.8327 | 122.9996 | -3.206
629.2812 | 123.3078 | -111.4975 | 11.5906 | 0.041851 | 0.08438 | 0.01171 | -0.0096504 | -0.04466 | 0.12484 | 0.043632 | 0.14236 | 0.0093943 | -0.019863 | 0.063944 | 0.085495 | 11.5844 | 11.0358 | 10.9566 | 11.5576 | 11.4248 | 11.6114 | 8.5087 | 11.5898 | 11.5433 | 11.6331 | 11.5582 | 11.6205 | 11.3444 | 8.5677 | 120.0062 | -0.03296 | 123.0819 | 122.4541 | 2.4479 | -0.1658 | 0.020789 | 120.0652 | -0.032359 | 123.0873 | 123.1306 | 3.0654 | 0.029888 | -0.24621 | 123.0551 | 122.9223 | 123.1089 | 122.5333 | -3.0819 | 123.0557 | 123.118 | 122.8419 | 123.0408 | -3.0229
630.3125 | 123.3765 | -111.3235 | 11.7325 | 0.041851 | 0.086517 | 0.012779 | -0.012856 | -0.046796 | 0.12591 | 0.058893 | 0.1445 | 0.0093943 | -0.022 | 0.062876 | 0.085495 | 11.74 | 11.2098 | 11.1489 | 11.6995 | 11.5576 | 11.7533 | 8.5316 | 11.7454 | 11.6944 | 11.7842 | 11.7002 | 11.7807 | 11.4909 | 8.5722 | 119.8551 | -0.032937 | 123.0636 | 122.4724 | 2.6173 | -0.17492 | 0.020819 | 119.8958 | -0.032333 | 123.069 | 123.1077 | 3.212 | 0.048232 | -0.2416 | 123.0231 | 122.8811 | 123.0768 | 122.5334 | -3.2009 | 123.0237 | 123.1043 | 122.8144 | 123.0179 | -3.1602
631.2812 | 123.2941 | -111.525 | 11.5906 | 0.041851 | 0.086517 | 0.01171 | -0.013924 | -0.045728 | 0.12591 | 0.058893 | 0.14236 | 0.0072583 | -0.019863 | 0.061808 | 0.084427 | 11.5615 | 11.5624 | 11.5151 | 11.5347 | 11.3973 | 11.5885 | 8.5453 | 11.5669 | 11.5296 | 11.6148 | 11.5262 | 11.6067 | 11.3032 | 8.5585 | 120.0703 | -0.055852 | 123.0864 | 123.0401 | 2.9698 | -0.19327 | -0.002104 | 120.0835 | -0.064408 | 123.0918 | 123.1397 | 3.0563 | 0.016152 | -0.28741 | 123.0597 | 122.9223 | 123.1134 | 123.0873 | -3.0453 | 123.0511 | 123.1317 | 122.8281 | 123.0545 | -3.0321
632.2812 | 123.2895 | -111.644 | 11.4624 | 0.041851 | 0.086517 | 0.012779 | -0.012856 | -0.046796 | 0.12484 | 0.074154 | 0.14129 | 0.0083263 | -0.022 | 0.065013 | 0.084427 | 11.4653 | 11.4708 | 11.4373 | 11.4294 | 11.3011 | 11.4832 | 8.527 | 11.4616 | 11.4151 | 11.5049 | 11.43 | 11.506 | 11.2207 | 8.5539 | 120.171 | -0.03298 | 123.1093 | 123.0813 | 2.9103 | -0.16126 | 0.020762 | 120.1979 | -0.032383 | 123.1055 | 123.1489 | 2.951 | 0.043597 | -0.24165 | 123.0734 | 122.9451 | 123.1271 | 123.1148 | -2.9354 | 123.074 | 123.15 | 122.8647 | 123.0591 | -2.9085
633.2812 | 123.2712 | -111.6074 | 11.4716 | 0.057113 | 0.08438 | 0.010642 | -0.011787 | -0.04466 | 0.12591 | 0.058893 | 0.1445 | 0.0072583 | -0.022 | 0.063944 | 0.085495 | 11.4516 | 11.4616 | 11.419 | 11.4111 | 11.2828 | 11.4694 | 8.5224 | 11.4478 | 11.3968 | 11.4912 | 11.4117 | 11.4877 | 11.2345 | 8.5585 | 120.1298 | -0.06045 | 123.059 | 123.0263 | 2.8966 | -0.18873 | -0.002129 | 120.1659 | -0.059853 | 123.0552 | 123.0985 | 2.9327 | 0.016126 | -0.23707 | 123.0185 | 122.8902 | 123.0768 | 123.069 | -2.9491 | 123.0191 | 123.095 | 122.8418 | 123.0041 | -2.9131
634.2812 | 123.2941 | -111.676 | 11.38 | 0.057113 | 0.085449 | 0.01171 | -0.011787 | -0.046796 | 0.12591 | 0.074154 | 0.14236 | 0.0072583 | -0.022 | 0.062876 | 0.086563 | 11.3875 | 11.4204 | 11.3595 | 11.3562 | 11.2325 | 11.4099 | 8.5178 | 11.3975 | 11.3464 | 11.4408 | 11.3613 | 11.4419 | 11.1338 | 8.5539 | 120.1939 | -0.023838 | 123.0635 | 123.0355 | 2.8416 | -0.14754 | 0.029902 | 120.2299 | -0.018663 | 123.0735 | 123.1168 | 2.8869 | 0.061893 | -0.24625 | 123.0322 | 122.9085 | 123.0859 | 123.0965 | -2.8622 | 123.0374 | 123.1179 | 122.8098 | 123.0224 | -2.8261
635.2812 | 123.3307 | -111.7172 | 11.3388 | 0.041851 | 0.086517 | 0.012779 | -0.012856 | -0.04466 | 0.12591 | 0.043632 | 0.14343 | 0.0061893 | -0.020931 | 0.063944 | 0.084427 | 11.3371 | 11.3563 | 11.3137 | 11.3058 | 11.1775 | 11.355 | 8.5133 | 11.3379 | 11.3006 | 11.3858 | 11.3018 | 11.3778 | 11.088 | 8.5539 | 120.2305 | -0.033001 | 123.0544 | 123.0309 | 2.8004 | -0.16129 | 0.016158 | 120.2711 | -0.036985 | 123.0552 | 123.1031 | 2.8319 | 0.038992 | -0.25084 | 123.023 | 122.8947 | 123.0722 | 123.0736 | -2.8255 | 123.019 | 123.095 | 122.8052 | 123.0178 | -2.7849
636.2812 | 123.3353 | -111.9141 | 11.1694 | 0.057113 | 0.083312 | 0.012779 | -0.012856 | -0.043591 | 0.12484 | 0.043632 | 0.14236 | 0.0093943 | -0.019863 | 0.062876 | 0.085495 | 11.1815 | 11.2098 | 11.1443 | 11.1501 | 11.0127 | 11.1993 | 8.5224 | 11.1777 | 11.1358 | 11.2164 | 11.1462 | 11.2221 | 10.9323 | 8.5493 | 120.4365 | -0.019294 | 123.0955 | 123.0583 | 2.6219 | -0.15676 | 0.029857 | 120.4634 | -0.023282 | 123.0917 | 123.1305 | 2.6671 | 0.052691 | -0.23714 | 123.0642 | 122.9267 | 123.1134 | 123.1239 | -2.647 | 123.0602 | 123.1362 | 122.8464 | 123.0498 | -2.6201
637.2812 | 123.3444 | -111.8958 | 11.1786 | 0.041851 | 0.08438 | 0.012779 | -0.012856 | -0.04466 | 0.12377 | 0.043632 | 0.14343 | 0.0093943 | -0.019863 | 0.062876 | 0.08229 | 11.1815 | 11.2098 | 11.1626 | 11.1456 | 11.0218 | 11.1993 | 8.5133 | 11.1914 | 11.1495 | 11.2256 | 11.1462 | 11.2313 | 10.9689 | 8.5402 | 120.409 | -0.033028 | 123.0772 | 123.0583 | 2.6493 | -0.15676 | 0.020702 | 120.4359 | -0.032437 | 123.0872 | 123.1213 | 2.6854 | 0.052694 | -0.20966 | 123.0413 | 122.9176 | 123.095 | 123.1056 | -2.6653 | 123.0419 | 123.127 | 122.8647 | 123.0453 | -2.6384
638.2812 | 123.3444 | -111.9232 | 11.1145 | 0.057113 | 0.081175 | 0.014916 | -0.010719 | -0.045728 | 0.12377 | 0.074154 | 0.14343 | 0.0093943 | -0.023068 | 0.063944 | 0.084427 | 11.122 | 11.1595 | 11.0893 | 11.0952 | 10.9623 | 11.1443 | 8.5133 | 11.1182 | 11.0854 | 11.1615 | 11.0866 | 11.1672 | 10.8957 | 8.5448 | 120.4365 | -0.019303 | 123.0452 | 123.0126 | 2.5761 | -0.1522 | 0.029846 | 120.468 | -0.02787 | 123.0414 | 123.0847 | 2.6167 | 0.05268 | -0.21884 | 123.0184 | 122.8855 | 123.0676 | 123.0827 | -2.6012 | 123.0099 | 123.0904 | 122.8189 | 123.0086 | -2.5697
639.2812 | 123.3444 | -111.9141 | 11.1328 | 0.026589 | 0.08438 | 0.014916 | -0.013924 | -0.04466 | 0.12377 | 0.074154 | 0.14236 | 0.0083263 | -0.022 | 0.065013 | 0.086563 | 11.1265 | 11.164 | 11.1031 | 11.0952 | 10.9806 | 11.1581 | 8.5133 | 11.1273 | 11.09 | 11.1798 | 11.1004 | 11.1809 | 10.9277 | 8.5402 | 120.4273 | -0.037613 | 123.0406 | 123.0171 | 2.5898 | -0.15219 | 0.025272 | 120.4542 | -0.032445 | 123.0414 | 123.0939 | 2.6396 | 0.048106 | -0.20509 | 123.0093 | 122.8947 | 123.0721 | 123.0781 | -2.6195 | 123.0144 | 123.095 | 122.8418 | 123.0041 | -2.5926
640.2812 | 123.381 | -112.0651 | 11.0184 | 0.057113 | 0.083312 | 0.01171 | -0.011787 | -0.043591 | 0.12484 | 0.028371 | 0.14236 | 0.0083263 | -0.020931 | 0.063944 | 0.084427 | 10.9754 | 11.0404 | 10.9749 | 10.9762 | 10.8524 | 11.039 | 8.527 | 11.0128 | 10.9664 | 11.0562 | 10.9722 | 11.0573 | 10.7949 | 8.5448 | 120.5921 | -0.042211 | 123.0406 | 123.04 | 2.4479 | -0.16596 | 0.020668 | 120.6099 | -0.046202 | 123.078 | 123.1213 | 2.5114 | 0.038924 | -0.22343 | 123.0413 | 122.9175 | 123.1042 | 123.1055 | -2.4914 | 123.0373 | 123.1224 | 122.8601 | 123.0315 | -2.4736
641.2812 | 123.3398 | -111.9232 | 11.1374 | 0.041851 | 0.083312 | 0.013847 | -0.011787 | -0.043591 | 0.12484 | 0.058893 | 0.14343 | 0.0083263 | -0.023068 | 0.065013 | 0.085495 | 10.9983 | 11.1274 | 11.0893 | 11.0815 | 10.9531 | 11.1352 | 8.5041 | 11.109 | 11.0717 | 11.1569 | 11.0775 | 11.1534 | 10.8682 | 8.5493 | 120.4273 | -0.055926 | 122.9216 | 123.0126 | 2.5852 | -0.18424 | -0.002199 | 120.4726 | -0.059915 | 123.0322 | 123.0801 | 2.6076 | 0.016056 | -0.26919 | 123.0047 | 122.8764 | 123.0584 | 123.0506 | -2.6333 | 123.0007 | 123.0767 | 122.7914 | 122.9949 | -2.588
642.2812 | 123.262 | -112.1933 | 10.9406 | 0.057113 | 0.082244 | 0.012779 | -0.013924 | -0.04466 | 0.12377 | 0.043632 | 0.14129 | 0.0072583 | -0.019863 | 0.063944 | 0.083358 | 10.8106 | 10.9443 | 10.9062 | 10.9029 | 10.77 | 10.952 | 8.5178 | 10.935 | 10.8748 | 10.96 | 10.8943 | 10.9703 | 10.6942 | 8.5356 | 120.7111 | -0.037645 | 123.0039 | 123.0995 | 2.3884 | -0.17056 | 0.011495 | 120.7289 | -0.046217 | 123.1283 | 123.1533 | 2.4244 | 0.02975 | -0.24634 | 123.0962 | 122.9633 | 123.1453 | 123.1376 | -2.4227 | 123.0876 | 123.1636 | 122.8875 | 123.0681 | -2.4049
643.2812 | 123.2483 | -111.9919 | 11.1694 | 0.041851 | 0.082244 | 0.013847 | -0.011787 | -0.042523 | 0.1227 | 0.074154 | 0.14236 | 0.0072583 | -0.019863 | 0.066081 | 0.083358 | 11.0212 | 11.1411 | 11.0939 | 11.086 | 10.9531 | 11.1398 | 8.527 | 11.1227 | 11.0671 | 11.1569 | 11.0866 | 11.158 | 10.8774 | 8.5493 | 120.5189 | -0.083392 | 123.0131 | 123.0858 | 2.5669 | -0.21629 | -0.029665 | 120.5412 | -0.082802 | 123.1146 | 123.1488 | 2.6076 | -0.011409 | -0.29208 | 123.0779 | 122.945 | 123.1317 | 123.133 | -2.6424 | 123.0785 | 123.1499 | 122.8692 | 123.059 | -2.6201
644.2812 | 123.2986 | -112.0468 | 11.0641 | 0.057113 | 0.080107 | 0.013847 | -0.010719 | -0.04466 | 0.1227 | 0.043632 | 0.14023 | 0.0061893 | -0.020931 | 0.065013 | 0.084427 | 10.9571 | 11.0816 | 11.039 | 11.0219 | 10.889 | 11.0757 | 8.5178 | 11.0586 | 10.9938 | 11.0882 | 11.0225 | 11.0985 | 10.7995 | 8.5402 | 120.5647 | -0.042203 | 123.0039 | 123.0858 | 2.5211 | -0.17511 | 0.011521 | 120.587 | -0.041615 | 123.1054 | 123.135 | 2.548 | 0.034355 | -0.26463 | 123.0688 | 122.9359 | 123.1225 | 123.1284 | -2.5463 | 123.0693 | 123.1453 | 122.8463 | 123.0407 | -2.524
645.2812 | 123.2666 | -112.2345 | 10.8994 | 0.057113 | 0.080107 | 0.012779 | -0.010719 | -0.045728 | 0.12377 | 0.058893 | 0.14343 | 0.0083263 | -0.019863 | 0.065013 | 0.084427 | 10.8015 | 10.9168 | 10.8604 | 10.8525 | 10.7379 | 10.9154 | 8.4995 | 10.8892 | 10.829 | 10.9142 | 10.8623 | 10.9383 | 10.653 | 8.531 | 120.734 | -0.046808 | 123.036 | 123.0949 | 2.3609 | -0.16142 | 0.016065 | 120.7655 | -0.037067 | 123.1237 | 123.1487 | 2.3832 | 0.038899 | -0.24635 | 123.087 | 122.9724 | 123.1499 | 123.1513 | -2.3998 | 123.0968 | 123.1727 | 122.8875 | 123.0635 | -2.3683
646.2812 | 123.3261 | -112.1109 | 10.9451 | 0.041851 | 0.079038 | 0.014916 | -0.011787 | -0.043591 | 0.1227 | 0.058893 | 0.14236 | 0.0061893 | -0.019863 | 0.066081 | 0.085495 | 10.8518 | 10.9672 | 10.9108 | 10.9121 | 10.7746 | 10.952 | 8.4995 | 10.9304 | 10.8702 | 10.96 | 10.9081 | 10.9795 | 10.7125 | 8.531 | 120.6104 | -0.033065 | 122.9627 | 123.0217 | 2.4113 | -0.17056 | 0.006918 | 120.6419 | -0.037058 | 123.0413 | 123.0709 | 2.429 | 0.034331 | -0.23261 | 123.023 | 122.8855 | 123.0629 | 123.0781 | -2.4456 | 123.019 | 123.0904 | 122.8234 | 122.9811 | -2.4141
647.2812 | 123.3124 | -112.2208 | 10.8719 | 0.041851 | 0.081175 | 0.014916 | -0.012856 | -0.04466 | 0.12484 | 0.043632 | 0.14236 | 0.0083263 | -0.018795 | 0.063944 | 0.084427 | 10.774 | 10.8939 | 10.833 | 10.8251 | 10.7013 | 10.8834 | 8.5041 | 10.8572 | 10.7878 | 10.8776 | 10.8302 | 10.9062 | 10.6438 | 8.531 | 120.7249 | -0.046813 | 122.9948 | 123.0537 | 2.3288 | -0.17058 | 0.01148 | 120.7518 | -0.041651 | 123.0779 | 123.0984 | 2.3466 | 0.034315 | -0.22804 | 123.0458 | 122.9221 | 123.1041 | 123.1147 | -2.3678 | 123.051 | 123.127 | 122.8646 | 123.0086 | -2.3409
648.2812 | 123.2803 | -112.294 | 10.8353 | 0.057113 | 0.082244 | 0.012779 | -0.012856 | -0.04466 | 0.12484 | 0.043632 | 0.14023 | 0.0093943 | -0.019863 | 0.062876 | 0.083358 | 10.7465 | 10.8527 | 10.7826 | 10.7839 | 10.6647 | 10.8422 | 8.5041 | 10.8205 | 10.7512 | 10.8456 | 10.7936 | 10.8604 | 10.6026 | 8.5356 | 120.7981 | -0.051397 | 123.0405 | 123.0766 | 2.2785 | -0.17059 | 0.006894 | 120.8296 | -0.041658 | 123.1145 | 123.1396 | 2.31 | 0.02515 | -0.23263 | 123.0779 | 122.9587 | 123.1362 | 123.1467 | -2.3312 | 123.0876 | 123.1544 | 122.8966 | 123.0452 | -2.2997
649.2812 | 123.2162 | -112.3947 | 10.7941 | 0.057113 | 0.079038 | 0.012779 | -0.012856 | -0.045728 | 0.12484 | 0.074154 | 0.14129 | 0.0061893 | -0.020931 | 0.063944 | 0.08229 | 10.6824 | 10.7794 | 10.7277 | 10.7198 | 10.596 | 10.7735 | 8.495 | 10.7473 | 10.6779 | 10.7631 | 10.7295 | 10.8009 | 10.5065 | 8.531 | 120.8897 | -0.074296 | 123.0771 | 123.1224 | 2.2327 | -0.19808 | -0.020586 | 120.9257 | -0.064558 | 123.142 | 123.1579 | 2.2321 | 0.006827 | -0.28758 | 123.1145 | 122.9907 | 123.1682 | 123.1742 | -2.2991 | 123.1242 | 123.1956 | 122.9012 | 123.0726 | -2.263
650.2812 | 123.3673 | -112.3535 | 10.7208 | 0.057113 | 0.080107 | 0.012779 | -0.011787 | -0.04466 | 0.12484 | 0.043632 | 0.14129 | 0.0072583 | -0.020931 | 0.063944 | 0.085495 | 10.5909 | 10.7291 | 10.6865 | 10.674 | 10.5456 | 10.7369 | 8.495 | 10.7106 | 10.6596 | 10.7357 | 10.6837 | 10.7505 | 10.4653 | 8.5219 | 120.8485 | -0.046837 | 122.9444 | 123.04 | 2.1915 | -0.1752 | 0.016027 | 120.8754 | -0.037101 | 123.0642 | 123.0892 | 2.2138 | 0.029704 | -0.25555 | 123.0275 | 122.8991 | 123.0904 | 123.0826 | -2.2259 | 123.0372 | 123.104 | 122.8188 | 123.0131 | -2.199
651.2812 | 123.1247 | -112.3856 | 10.762 | 0.057113 | 0.080107 | 0.01171 | -0.011787 | -0.045728 | 0.12484 | 0.043632 | 0.14129 | 0.0072583 | -0.020931 | 0.065013 | 0.084427 | 10.6 | 10.7337 | 10.6819 | 10.6877 | 10.5548 | 10.7369 | 8.4995 | 10.7152 | 10.6688 | 10.7494 | 10.6837 | 10.7643 | 10.4836 | 8.5264 | 120.8851 | -0.074301 | 122.9856 | 123.0674 | 2.1823 | -0.20724 | -0.025172 | 120.912 | -0.0783 | 123.1008 | 123.135 | 2.223 | 0.002241 | -0.27843 | 123.0733 | 122.9403 | 123.1224 | 123.1192 | -2.2625 | 123.0693 | 123.1498 | 122.8692 | 123.0543 | -2.2356
652.2812 | 123.2208 | -112.4496 | 10.7346 | 0.072375 | 0.081175 | 0.013847 | -0.012856 | -0.045728 | 0.1227 | 0.058893 | 0.14129 | 0.0072583 | -0.022 | 0.06715 | 0.085495 | 10.5313 | 10.6833 | 10.6269 | 10.6236 | 10.5044 | 10.6819 | 8.4766 | 10.6511 | 10.6092 | 10.6853 | 10.6196 | 10.7047 | 10.4058 | 8.5173 | 120.9263 | -0.11093 | 122.981 | 123.0766 | 2.1503 | -0.23015 | -0.052649 | 120.9669 | -0.11493 | 123.1008 | 123.1349 | 2.168 | -0.029815 | -0.3288 | 123.0733 | 122.9541 | 123.1316 | 123.1329 | -2.2579 | 123.0693 | 123.1544 | 122.8554 | 123.0589 | -2.2173
653.2812 | 123.23 | -112.4039 | 10.7666 | 0.041851 | 0.079038 | 0.013847 | -0.013924 | -0.045728 | 0.12377 | 0.058893 | 0.14129 | 0.0072583 | -0.020931 | 0.063944 | 0.084427 | 10.5954 | 10.752 | 10.691 | 10.6923 | 10.5639 | 10.7506 | 8.4995 | 10.7152 | 10.6688 | 10.7494 | 10.6791 | 10.7688 | 10.4744 | 8.5219 | 120.9034 | -0.074301 | 122.9993 | 123.0949 | 2.1915 | -0.20266 | -0.016014 | 120.9257 | -0.087456 | 123.1191 | 123.1533 | 2.2275 | 0.002242 | -0.29217 | 123.0962 | 122.9678 | 123.1545 | 123.1558 | -2.2671 | 123.083 | 123.1727 | 122.8783 | 123.0726 | -2.2447
654.2812 | 123.2391 | -112.6877 | 10.5148 | 0.041851 | 0.081175 | 0.012779 | -0.012856 | -0.043591 | 0.12377 | 0.074154 | 0.14343 | 0.0072583 | -0.020931 | 0.066081 | 0.084427 | 10.3986 | 10.5459 | 10.4896 | 10.4817 | 10.3533 | 10.54 | 8.4721 | 10.5046 | 10.4673 | 10.5434 | 10.4823 | 10.5582 | 10.2684 | 8.5127 | 121.1597 | -0.033137 | 123.0862 | 123.1773 | 2.0175 | -0.16153 | 0.02514 | 121.2004 | -0.032561 | 123.1923 | 123.231 | 2.0307 | 0.043396 | -0.24643 | 123.1694 | 123.041 | 123.2277 | 123.2336 | -2.0428 | 123.17 | 123.2459 | 122.9561 | 123.155 | -2.0021
655.2812 | 123.3124 | -112.6648 | 10.4691 | 0.057113 | 0.080107 | 0.012779 | -0.014993 | -0.04466 | 0.12377 | 0.058893 | 0.14343 | 0.010463 | -0.020931 | 0.066081 | 0.084427 | 10.3803 | 10.5047 | 10.4438 | 10.4451 | 10.3213 | 10.4988 | 8.4721 | 10.468 | 10.4215 | 10.5113 | 10.4456 | 10.5308 | 10.2547 | 8.4944 | 121.1369 | -0.023987 | 123.045 | 123.1086 | 1.9717 | -0.1478 | 0.02971 | 121.1592 | -0.023412 | 123.1328 | 123.1761 | 2.0169 | 0.061701 | -0.21439 | 123.1099 | 122.9861 | 123.1636 | 123.1695 | -1.997 | 123.1104 | 123.1956 | 122.9195 | 123.0863 | -1.9747
656.3125 | 123.2391 | -112.5778 | 10.5972 | 0.057113 | 0.080107 | 0.013847 | -0.014993 | -0.045728 | 0.12377 | 0.074154 | 0.14343 | 0.0083263 | -0.020931 | 0.066081 | 0.083358 | 10.4444 | 10.6009 | 10.5354 | 10.5275 | 10.4037 | 10.5949 | 8.4858 | 10.5596 | 10.5131 | 10.5937 | 10.5372 | 10.604 | 10.3004 | 8.5127 | 121.0636 | -0.06975 | 123.0222 | 123.1132 | 2.0496 | -0.19355 | -0.002313 | 121.0905 | -0.060016 | 123.1374 | 123.1715 | 2.081 | 0.006785 | -0.29678 | 123.1053 | 122.9815 | 123.1727 | 123.1787 | -2.1114 | 123.115 | 123.1818 | 122.8783 | 123.0909 | -2.0845
657.2812 | 123.2529 | -112.532 | 10.6247 | 0.072375 | 0.081175 | 0.014916 | -0.011787 | -0.045728 | 0.12484 | 0.058893 | 0.14236 | 0.0083263 | -0.020931 | 0.066081 | 0.08229 | 10.5039 | 10.6375 | 10.5674 | 10.5595 | 10.4449 | 10.6132 | 8.4995 | 10.5916 | 10.5497 | 10.6304 | 10.5647 | 10.6498 | 10.3417 | 8.5081 | 121.0316 | -0.065167 | 123.0359 | 123.0995 | 2.0679 | -0.17981 | -0.011465 | 121.0402 | -0.060011 | 123.1236 | 123.1624 | 2.1222 | 0.025105 | -0.28304 | 123.0916 | 122.9769 | 123.1453 | 123.1695 | -2.1252 | 123.0967 | 123.1818 | 122.8737 | 123.0817 | -2.1166
658.3125 | 123.2437 | -112.5778 | 10.6476 | 0.041851 | 0.079038 | 0.01171 | -0.013924 | -0.043591 | 0.12591 | 0.058893 | 0.14236 | 0.0061893 | -0.020931 | 0.068218 | 0.084427 | 10.4947 | 10.6238 | 10.5537 | 10.5549 | 10.4311 | 10.6041 | 8.5041 | 10.587 | 10.536 | 10.6166 | 10.5464 | 10.6361 | 10.3371 | 8.5127 | 121.0819 | -0.092634 | 123.0725 | 123.1315 | 2.0496 | -0.21643 | -0.04351 | 121.0905 | -0.10121 | 123.1648 | 123.1944 | 2.1039 | -0.011519 | -0.3105 | 123.1328 | 123.009 | 123.1819 | 123.2016 | -2.1435 | 123.1242 | 123.2139 | 122.9149 | 123.1138 | -2.1349
659.2812 | 123.262 | -112.8113 | 10.3683 | 0.057113 | 0.081175 | 0.012779 | -0.011787 | -0.04466 | 0.12591 | 0.058893 | 0.14343 | 0.0083263 | -0.023068 | 0.065013 | 0.084427 | 10.2704 | 10.4086 | 10.3385 | 10.3398 | 10.2205 | 10.3889 | 8.4537 | 10.3627 | 10.3162 | 10.3968 | 10.3449 | 10.4071 | 10.1539 | 8.4944 | 121.265 | -0.028582 | 123.0817 | 123.1498 | 1.8848 | -0.14783 | 0.020531 | 121.3057 | -0.023431 | 123.1739 | 123.2081 | 1.9024 | 0.038787 | -0.21441 | 123.151 | 123.0318 | 123.2002 | 123.2198 | -1.9146 | 123.1562 | 123.2184 | 122.9652 | 123.1275 | -1.874
660.3125 | 123.2712 | -112.7655 | 10.4507 | 0.072375 | 0.080107 | 0.014916 | -0.013924 | -0.04466 | 0.12377 | 0.074154 | 0.14236 | 0.0072583 | -0.022 | 0.063944 | 0.084427 | 10.3024 | 10.4498 | 10.3797 | 10.3672 | 10.2617 | 10.4347 | 8.4858 | 10.3993 | 10.362 | 10.4426 | 10.377 | 10.4575 | 10.1631 | 8.499 | 121.2513 | -0.083509 | 123.0679 | 123.1452 | 1.8939 | -0.18902 | -0.016081 | 121.2645 | -0.07378 | 123.1648 | 123.2081 | 1.9437 | 0.006754 | -0.28765 | 123.1327 | 123.0272 | 123.2002 | 123.2153 | -1.9649 | 123.1425 | 123.223 | 122.9286 | 123.1275 | -1.9518
661.2812 | 123.2666 | -112.912 | 10.2448 | 0.041851 | 0.080107 | 0.015984 | -0.011787 | -0.042523 | 0.12377 | 0.043632 | 0.14343 | 0.0072583 | -0.022 | 0.06715 | 0.084427 | 10.133 | 10.2575 | 10.1874 | 10.1933 | 10.0648 | 10.2424 | 8.4492 | 10.2116 | 10.1697 | 10.2457 | 10.1892 | 10.2652 | 9.9799 | 8.4715 | 121.3611 | -0.051494 | 123.045 | 123.0994 | 1.7383 | -0.17992 | -0.002388 | 121.3835 | -0.055504 | 123.1236 | 123.1577 | 1.7742 | 0.020447 | -0.2648 | 123.1052 | 122.9768 | 123.1543 | 123.1695 | -1.7956 | 123.1012 | 123.1772 | 122.8919 | 123.0817 | -1.7733
662.3125 | 123.381 | -112.9486 | 10.1578 | 0.072375 | 0.080107 | 0.01171 | -0.012856 | -0.04466 | 0.12377 | 0.058893 | 0.14236 | 0.0072583 | -0.023068 | 0.063944 | 0.083358 | 10.0964 | 10.23 | 10.1508 | 10.1429 | 10.0236 | 10.2057 | 8.44 | 10.1704 | 10.1376 | 10.2045 | 10.1526 | 10.2286 | 9.9616 | 8.4623 | 121.3886 | -0.014881 | 123.045 | 123.0994 | 1.7108 | -0.13415 | 0.047958 | 121.411 | -0.005157 | 123.119 | 123.1531 | 1.7422 | 0.070793 | -0.19614 | 123.0915 | 122.9722 | 123.1543 | 123.1786 | -1.7178 | 123.1012 | 123.1772 | 122.9102 | 123.0862 | -1.6954
663.2812 | 123.2758 | -113.2599 | 9.9426 | 0.057113 | 0.080107 | 0.013847 | -0.011787 | -0.04466 | 0.12484 | 0.043632 | 0.14129 | 0.0072583 | -0.022 | 0.06715 | 0.084427 | 9.8217 | 9.9324 | 9.8532 | 9.8636 | 9.7352 | 9.9173 | 8.3896 | 9.8773 | 9.8354 | 9.9069 | 9.855 | 9.9401 | 9.6823 | 8.4257 | 121.6495 | -0.079014 | 123.0816 | 123.1131 | 1.4636 | -0.20747 | -0.025345 | 121.6856 | -0.08761 | 123.1372 | 123.1668 | 1.4812 | -0.00251 | -0.26029 | 123.1235 | 122.995 | 123.1772 | 123.1923 | -1.553 | 123.1149 | 123.2 | 122.9422 | 123.0953 | -1.5169
664.3125 | 123.23 | -113.2507 | 9.9655 | 0.057113 | 0.080107 | 0.012779 | -0.011787 | -0.04466 | 0.1227 | 0.043632 | 0.14236 | 0.0083263 | -0.023068 | 0.065013 | 0.084427 | 9.8354 | 9.969 | 9.8898 | 9.8865 | 9.7672 | 9.9448 | 8.4034 | 9.9094 | 9.8766 | 9.939 | 9.8962 | 9.963 | 9.7373 | 8.4303 | 121.6541 | -0.07901 | 123.0862 | 123.1406 | 1.4865 | -0.19831 | -0.020761 | 121.681 | -0.069292 | 123.1601 | 123.1897 | 1.5087 | -0.002505 | -0.22823 | 123.1372 | 123.0179 | 123.1955 | 123.2198 | -1.5621 | 123.147 | 123.2137 | 122.988 | 123.1274 | -1.5352
665.2812 | 123.3627 | -113.3102 | 9.7412 | 0.057113 | 0.080107 | 0.012779 | -0.013924 | -0.043591 | 0.1227 | 0.043632 | 0.14129 | 0.0061893 | -0.020931 | 0.066081 | 0.083358 | 9.7118 | 9.8271 | 9.7433 | 9.7492 | 9.6298 | 9.8074 | 8.3622 | 9.772 | 9.7255 | 9.8016 | 9.7543 | 9.8302 | 9.5908 | 8.3982 | 121.6724 | 0.007942 | 123.0221 | 123.0536 | 1.3812 | -0.11137 | 0.066185 | 121.7085 | 0.013079 | 123.0823 | 123.1119 | 1.4034 | 0.089019 | -0.15044 | 123.0594 | 122.9401 | 123.1176 | 123.1373 | -1.379 | 123.0645 | 123.1405 | 122.901 | 123.0358 | -1.343
666.3125 | 123.3307 | -113.3652 | 9.7824 | 0.087637 | 0.080107 | 0.012779 | -0.013924 | -0.04466 | 0.12377 | 0.058893 | 0.14129 | 0.0061893 | -0.022 | 0.06715 | 0.084427 | 9.666 | 9.7813 | 9.7021 | 9.7079 | 9.584 | 9.7662 | 8.3347 | 9.7308 | 9.6706 | 9.7421 | 9.7085 | 9.789 | 9.5358 | 8.3891 | 121.6999 | -0.074462 | 123.0312 | 123.0673 | 1.3674 | -0.19836 | -0.016222 | 121.7543 | -0.073905 | 123.096 | 123.1073 | 1.353 | 0.006613 | -0.24659 | 123.0731 | 122.9492 | 123.1314 | 123.1465 | -1.4477 | 123.0737 | 123.1542 | 122.901 | 123.0358 | -1.3933
667.2812 | 123.2895 | -113.5117 | 9.6497 | 0.057113 | 0.079038 | 0.012779 | -0.011787 | -0.046796 | 0.12163 | 0.074154 | 0.14343 | 0.0061893 | -0.022 | 0.06715 | 0.083358 | 9.579 | 9.6852 | 9.6106 | 9.6118 | 9.4833 | 9.67 | 8.3255 | 9.6347 | 9.5744 | 9.6505 | 9.6078 | 9.6883 | 9.4259 | 8.3616 | 121.8372 | -0.037856 | 123.0907 | 123.1222 | 1.285 | -0.16635 | 0.02038 | 121.8733 | -0.04188 | 123.1463 | 123.1622 | 1.2889 | 0.038636 | -0.22372 | 123.1235 | 122.995 | 123.1817 | 123.1968 | -1.3241 | 123.1194 | 123.2 | 122.9376 | 123.0861 | -1.288
668.2969 | 123.317 | -113.562 | 9.5901 | 0.057113 | 0.080107 | 0.013847 | -0.011787 | -0.04466 | 0.12484 | 0.043632 | 0.1445 | 0.0072583 | -0.022 | 0.066081 | 0.084427 | 9.5104 | 9.6165 | 9.5465 | 9.5477 | 9.4192 | 9.5968 | 8.2889 | 9.5614 | 9.5012 | 9.5818 | 9.5437 | 9.6242 | 9.3618 | 8.3479 | 121.8509 | -0.042445 | 123.0724 | 123.1085 | 1.2576 | -0.17094 | 0.006631 | 121.9099 | -0.04647 | 123.1234 | 123.1438 | 1.234 | 0.034044 | -0.22831 | 123.1097 | 122.9812 | 123.1588 | 123.1785 | -1.3012 | 123.1057 | 123.1862 | 122.9238 | 123.0632 | -1.2423
669.2812 | 123.2895 | -113.7177 | 9.462 | 0.026589 | 0.079038 | 0.014916 | -0.011787 | -0.045728 | 0.1227 | 0.074154 | 0.14129 | 0.0061893 | -0.020931 | 0.066081 | 0.083358 | 9.3501 | 9.4654 | 9.3816 | 9.3966 | 9.2727 | 9.4503 | 8.2477 | 9.4057 | 9.3592 | 9.4216 | 9.3926 | 9.4685 | 9.1878 | 8.3021 | 121.9653 | -0.065358 | 123.0678 | 123.0993 | 1.134 | -0.18929 | -0.01171 | 122.0197 | -0.069386 | 123.1234 | 123.1392 | 1.1195 | 0.006546 | -0.27413 | 123.1143 | 122.9903 | 123.1679 | 123.183 | -1.2143 | 123.1102 | 123.1862 | 122.9055 | 123.0769 | -1.1599
670.3125 | 123.2666 | -113.4476 | 9.7549 | 0.057113 | 0.079038 | 0.012779 | -0.010719 | -0.043591 | 0.12377 | 0.089415 | 0.1445 | 0.0072583 | -0.020931 | 0.06715 | 0.083358 | 9.6431 | 9.7584 | 9.6838 | 9.6759 | 9.5657 | 9.7479 | 8.3484 | 9.7033 | 9.6523 | 9.7146 | 9.681 | 9.757 | 9.4855 | 8.3799 | 121.796 | -0.079045 | 123.0907 | 123.1314 | 1.3354 | -0.18921 | -0.00707 | 121.8275 | -0.07391 | 123.1509 | 123.1622 | 1.3347 | 0.002029 | -0.26949 | 123.1235 | 123.0133 | 123.1954 | 123.206 | -1.4065 | 123.1286 | 123.2045 | 122.933 | 123.0999 | -1.375
671.2812 | 123.2712 | -113.5391 | 9.6634 | 0.057113 | 0.076902 | 0.012779 | -0.013924 | -0.04466 | 0.1227 | 0.074154 | 0.14343 | 0.0061893 | -0.020931 | 0.06715 | 0.083358 | 9.5699 | 9.676 | 9.6014 | 9.6026 | 9.4833 | 9.6609 | 8.3164 | 9.6255 | 9.5653 | 9.6459 | 9.5986 | 9.6837 | 9.4214 | 8.3662 | 121.8555 | -0.060746 | 123.109 | 123.1405 | 1.285 | -0.18008 | -0.00251 | 121.9053 | -0.06477 | 123.1646 | 123.1851 | 1.2797 | 0.020324 | -0.24203 | 123.1418 | 123.0224 | 123.2 | 123.2151 | -1.347 | 123.1377 | 123.2228 | 122.9605 | 123.1044 | -1.2972
672.3125 | 123.3261 | -113.6169 | 9.5306 | 0.057113 | 0.080107 | 0.01171 | -0.010719 | -0.04466 | 0.12163 | 0.058893 | 0.14343 | 0.0061893 | -0.023068 | 0.06715 | 0.083358 | 9.4417 | 9.5432 | 9.4686 | 9.4699 | 9.3505 | 9.5281 | 8.2797 | 9.4881 | 9.4371 | 9.5177 | 9.4658 | 9.5509 | 9.2703 | 8.3341 | 121.8967 | -0.060768 | 123.0586 | 123.0856 | 1.1889 | -0.18012 | -0.002539 | 121.9511 | -0.064795 | 123.1051 | 123.1347 | 1.1836 | 0.020296 | -0.26038 | 123.0868 | 122.9675 | 123.145 | 123.1602 | -1.2509 | 123.0828 | 123.1679 | 122.8872 | 123.054 | -1.1965
673.2812 | 123.2574 | -113.7222 | 9.4574 | 0.057113 | 0.079038 | 0.01171 | -0.011787 | -0.04466 | 0.12163 | 0.058893 | 0.14557 | 0.0051213 | -0.019863 | 0.066081 | 0.08229 | 9.3593 | 9.4654 | 9.3816 | 9.3966 | 9.2727 | 9.4548 | 8.2568 | 9.4103 | 9.3638 | 9.4307 | 9.388 | 9.4685 | 9.1924 | 8.3158 | 121.9791 | -0.06078 | 123.0815 | 123.1039 | 1.1248 | -0.18472 | -0.002553 | 122.038 | -0.069387 | 123.1325 | 123.153 | 1.1149 | 0.011124 | -0.26497 | 123.1188 | 122.9949 | 123.1771 | 123.1876 | -1.2005 | 123.1102 | 123.1907 | 122.9147 | 123.0861 | -1.1416
674.2969 | 123.2941 | -113.8046 | 9.3475 | 0.041851 | 0.07797 | 0.01171 | -0.013924 | -0.04466 | 0.12163 | 0.043632 | 0.14236 | 0.0061893 | -0.023068 | 0.068218 | 0.084427 | 9.2723 | 9.3784 | 9.2992 | 9.3142 | 9.1765 | 9.3633 | 8.2202 | 9.3233 | 9.2768 | 9.3483 | 9.2964 | 9.3815 | 9.0963 | 8.2746 | 122.0248 | -0.033328 | 123.0769 | 123.1039 | 1.079 | -0.17101 | 0.015737 | 122.0792 | -0.051094 | 123.1279 | 123.1529 | 1.0737 | 0.033993 | -0.25126 | 123.1188 | 122.9811 | 123.1679 | 123.183 | -1.1273 | 123.1011 | 123.1862 | 122.9009 | 123.0815 | -1.0729
675.2812 | 123.2391 | -113.9191 | 9.3338 | 0.057113 | 0.079038 | 0.012779 | -0.011787 | -0.04466 | 0.1227 | 0.074154 | 0.14343 | 0.0072583 | -0.020931 | 0.068218 | 0.083358 | 9.199 | 9.296 | 9.2168 | 9.2318 | 9.1078 | 9.2854 | 8.2065 | 9.2455 | 9.1944 | 9.2613 | 9.2323 | 9.3083 | 9.023 | 8.2563 | 122.1255 | -0.10201 | 123.1181 | 123.1359 | 1.0103 | -0.22596 | -0.048366 | 122.1754 | -0.10146 | 123.1645 | 123.1804 | 1.005 | -0.025531 | -0.31078 | 123.1509 | 123.0269 | 123.2045 | 123.215 | -1.1273 | 123.1514 | 123.2273 | 122.9421 | 123.1135 | -1.0775
676.2812 | 123.2712 | -114.0839 | 9.1003 | 0.072375 | 0.079038 | 0.012779 | -0.011787 | -0.043591 | 0.12163 | 0.058893 | 0.14236 | 0.0061893 | -0.022 | 0.069286 | 0.084427 | 9.0296 | 9.1266 | 9.052 | 9.0578 | 8.943 | 9.116 | 8.1241 | 9.0806 | 9.0296 | 9.0965 | 9.0629 | 9.1389 | 8.8582 | 8.1876 | 122.2079 | -0.042525 | 123.1135 | 123.1359 | 0.92795 | -0.15734 | 0.015685 | 122.2715 | -0.037405 | 123.1645 | 123.1804 | 0.90888 | 0.038519 | -0.24215 | 123.1417 | 123.0269 | 123.1999 | 123.2104 | -0.97628 | 123.1468 | 123.2227 | 122.9421 | 123.1134 | -0.91273
677.2812 | 123.3765 | -114.0747 | 9.0729 | 0.057113 | 0.076902 | 0.01171 | -0.012856 | -0.04466 | 0.12377 | 0.058893 | 0.1445 | 0.0061893 | -0.019863 | 0.068218 | 0.083358 | 8.9747 | 9.0808 | 8.9879 | 9.0075 | 8.8881 | 9.0657 | 8.1012 | 9.0211 | 8.9701 | 9.0415 | 9.008 | 9.0885 | 8.8261 | 8.1601 | 122.1759 | -0.065422 | 123.0494 | 123.0626 | 0.88675 | -0.18482 | -0.007214 | 122.2348 | -0.064881 | 123.0958 | 123.1163 | 0.8814 | 0.015621 | -0.24674 | 123.0822 | 122.9628 | 123.1404 | 123.1555 | -0.97171 | 123.0827 | 123.1632 | 122.9008 | 123.0448 | -0.91274
678.2812 | 123.3856 | -114.0793 | 9.0408 | 0.057113 | 0.079038 | 0.012779 | -0.012856 | -0.04466 | 0.12484 | 0.074154 | 0.1445 | 0.0051213 | -0.020931 | 0.068218 | 0.085495 | 8.9747 | 9.0716 | 9.0016 | 9.012 | 8.8881 | 9.0702 | 8.1103 | 9.0257 | 8.9701 | 9.0461 | 9.0034 | 9.0931 | 8.904 | 8.1693 | 122.1896 | -0.0288 | 123.054 | 123.0809 | 0.89132 | -0.15278 | 0.029408 | 122.2486 | -0.037416 | 123.105 | 123.1254 | 0.87683 | 0.052242 | -0.13686 | 123.0913 | 122.9673 | 123.1495 | 123.1509 | -0.93051 | 123.0827 | 123.1724 | 122.9833 | 123.0493 | -0.87153
679.2812 | 123.3719 | -114.1251 | 9.0317 | 0.041851 | 0.079038 | 0.01171 | -0.013924 | -0.043591 | 0.12377 | 0.043632 | 0.1445 | 0.0061893 | -0.022 | 0.068218 | 0.085495 | 8.9106 | 9.0121 | 8.933 | 8.925 | 8.8194 | 8.997 | 8.0737 | 8.9524 | 8.906 | 8.9729 | 8.9347 | 9.0198 | 8.8445 | 8.1372 | 122.1988 | -0.10663 | 123.0357 | 123.058 | 0.85928 | -0.21231 | -0.034694 | 122.2623 | -0.096938 | 123.0775 | 123.0979 | 0.83562 | -0.011859 | -0.18722 | 123.0501 | 122.9444 | 123.122 | 123.1372 | -0.95799 | 123.0598 | 123.1449 | 122.9695 | 123.031 | -0.89443
680.2812 | 123.3215 | -114.2899 | 8.8669 | 0.057113 | 0.07797 | 0.010642 | -0.012856 | -0.04466 | 0.12377 | 0.058893 | 0.14343 | 0.0061893 | -0.023068 | 0.069286 | 0.08229 | 8.8144 | 8.9068 | 8.8323 | 8.8381 | 8.7141 | 8.91 | 8.0142 | 8.8563 | 8.8052 | 8.8767 | 8.8477 | 8.9237 | 8.6934 | 8.096 | 122.304 | -0.028828 | 123.1043 | 123.1221 | 0.81808 | -0.15283 | 0.043108 | 122.3859 | -0.019134 | 123.1461 | 123.1666 | 0.78067 | 0.056785 | -0.17352 | 123.1279 | 123.0039 | 123.1998 | 123.1966 | -0.85272 | 123.1376 | 123.2135 | 122.9832 | 123.0951 | -0.77084
681.2812 | 123.349 | -114.299 | 8.8486 | 0.072375 | 0.076902 | 0.01171 | -0.012856 | -0.04466 | 0.1227 | 0.074154 | 0.14343 | 0.0072583 | -0.022 | 0.068218 | 0.084427 | 8.7549 | 8.8427 | 8.7636 | 8.7831 | 8.6637 | 8.8459 | 7.9867 | 8.7922 | 8.7549 | 8.808 | 8.7791 | 8.8687 | 8.6064 | 8.064 | 122.2857 | -0.065459 | 123.0539 | 123.0626 | 0.77688 | -0.18489 | -0.002683 | 122.363 | -0.069502 | 123.0912 | 123.107 | 0.74404 | 0.020152 | -0.24221 | 123.0821 | 122.9627 | 123.1449 | 123.1417 | -0.86188 | 123.0781 | 123.1677 | 122.9054 | 123.0539 | -0.78459
682.2812 | 123.3124 | -114.4501 | 8.7387 | 0.057113 | 0.076902 | 0.01171 | -0.012856 | -0.045728 | 0.12377 | 0.058893 | 0.14343 | 0.0051213 | -0.023068 | 0.068218 | 0.084427 | 8.6542 | 8.7374 | 8.6629 | 8.6778 | 8.5492 | 8.7406 | 7.9272 | 8.6869 | 8.645 | 8.7073 | 8.6738 | 8.768 | 8.5194 | 8.009 | 122.3772 | -0.060898 | 123.1043 | 123.1129 | 0.73569 | -0.1895 | 0.001874 | 122.4591 | -0.064943 | 123.1369 | 123.1574 | 0.69826 | 0.029287 | -0.21934 | 123.1279 | 122.9993 | 123.1907 | 123.1875 | -0.81154 | 123.1238 | 123.2181 | 122.9694 | 123.095 | -0.72967
683.2812 | 123.3994 | -114.5325 | 8.5922 | 0.072375 | 0.076902 | 0.01171 | -0.011787 | -0.04466 | 0.12377 | 0.043632 | 0.14343 | 0.0051213 | -0.023068 | 0.06715 | 0.083358 | 8.5214 | 8.6138 | 8.5392 | 8.5542 | 8.4347 | 8.617 | 7.8447 | 8.5632 | 8.5213 | 8.5883 | 8.5547 | 8.6444 | 8.3912 | 7.9404 | 122.3772 | -0.03803 | 123.0539 | 123.0717 | 0.69449 | -0.15749 | 0.024735 | 122.4728 | -0.0375 | 123.0957 | 123.1207 | 0.6479 | 0.052148 | -0.20105 | 123.0867 | 122.9672 | 123.1494 | 123.1462 | -0.74748 | 123.0872 | 123.1768 | 122.9236 | 123.0538 | -0.65187
684.2812 | 123.4039 | -114.6149 | 8.519 | 0.072375 | 0.079038 | 0.01171 | -0.011787 | -0.04466 | 0.12377 | 0.058893 | 0.14236 | 0.0072583 | -0.022 | 0.068218 | 0.083358 | 8.4253 | 8.5222 | 8.4385 | 8.4489 | 8.3386 | 8.5208 | 7.7898 | 8.4762 | 8.4206 | 8.4875 | 8.4586 | 8.5436 | 8.3133 | 7.8671 | 122.4047 | -0.070091 | 123.0401 | 123.0534 | 0.64872 | -0.1804 | 0.001827 | 122.482 | -0.060406 | 123.0911 | 123.1024 | 0.62042 | 0.024661 | -0.20565 | 123.0638 | 122.9534 | 123.1357 | 123.1371 | -0.72918 | 123.0734 | 123.1585 | 122.9282 | 123.0355 | -0.65188
685.2812 | 123.3902 | -114.6606 | 8.4686 | 0.041851 | 0.076902 | 0.01171 | -0.012856 | -0.046796 | 0.1227 | 0.074154 | 0.1445 | 0.0051213 | -0.022 | 0.06715 | 0.08229 | 8.3612 | 8.4627 | 8.3882 | 8.4031 | 8.2791 | 8.4613 | 7.7303 | 8.4167 | 8.3657 | 8.4372 | 8.4036 | 8.4979 | 8.2355 | 7.8396 | 122.3909 | -0.065521 | 123.0218 | 123.0488 | 0.65788 | -0.18957 | -0.007341 | 122.5003 | -0.064994 | 123.0774 | 123.0978 | 0.59753 | 0.029229 | -0.23313 | 123.0638 | 122.9397 | 123.1219 | 123.1233 | -0.73836 | 123.0643 | 123.1585 | 122.8961 | 123.0263 | -0.629
686.2812 | 123.4085 | -114.798 | 8.3221 | 0.057113 | 0.07797 | 0.01171 | -0.013924 | -0.043591 | 0.1227 | 0.058893 | 0.14343 | 0.0051213 | -0.020931 | 0.069286 | 0.081222 | 8.2559 | 8.3482 | 8.2645 | 8.2932 | 8.1692 | 8.3514 | 7.6433 | 8.3022 | 8.2649 | 8.3227 | 8.2983 | 8.3788 | 8.1027 | 7.7709 | 122.4412 | -0.028918 | 123.0539 | 123.0625 | 0.62127 | -0.15298 | 0.029256 | 122.5689 | -0.023816 | 123.1002 | 123.1207 | 0.55175 | 0.056669 | -0.21942 | 123.0912 | 122.9671 | 123.1494 | 123.1462 | -0.67887 | 123.0963 | 123.1768 | 122.9007 | 123.0629 | -0.5512
687.2812 | 123.4314 | -115.0543 | 8.0841 | 0.087637 | 0.07797 | 0.01171 | -0.011787 | -0.04466 | 0.1227 | 0.074154 | 0.1445 | 0.0072583 | -0.022 | 0.069286 | 0.083358 | 8.0407 | 8.1284 | 8.0539 | 8.078 | 7.9494 | 8.1316 | 7.4876 | 8.0779 | 8.036 | 8.0938 | 8.0694 | 8.1636 | 7.9699 | 7.6015 | 122.5419 | -0.006064 | 123.095 | 123.1083 | 0.56635 | -0.13473 | 0.047521 | 122.6558 | -0.014702 | 123.1322 | 123.1481 | 0.49223 | 0.079513 | -0.11417 | 123.1324 | 123.0037 | 123.1859 | 123.1827 | -0.59652 | 123.1237 | 123.2179 | 123.0243 | 123.0903 | -0.48258
688.2812 | 123.3948 | -115.0543 | 8.0704 | 0.057113 | 0.075833 | 0.01171 | -0.011787 | -0.04466 | 0.1227 | 0.058893 | 0.14343 | 0.0061893 | -0.020931 | 0.068218 | 0.083358 | 7.9903 | 8.0781 | 8.0036 | 8.0277 | 7.9082 | 8.0858 | 7.4601 | 8.0321 | 7.9856 | 8.048 | 8.0328 | 8.1178 | 7.9333 | 7.5695 | 122.5144 | -0.042695 | 123.0447 | 123.0579 | 0.54347 | -0.16221 | 0.015467 | 122.6238 | -0.037598 | 123.0864 | 123.1023 | 0.47849 | 0.047459 | -0.13706 | 123.082 | 122.9625 | 123.1402 | 123.1324 | -0.61026 | 123.0871 | 123.1722 | 122.9876 | 123.04 | -0.5009
689.2812 | 123.3765 | -115.2283 | 7.9102 | 0.041851 | 0.075833 | 0.010642 | -0.012856 | -0.04466 | 0.12163 | 0.074154 | 0.1445 | 0.0051213 | -0.022 | 0.070355 | 0.083358 | 7.8347 | 7.9178 | 7.8525 | 7.8629 | 7.7525 | 7.9302 | 7.3273 | 7.8764 | 7.8345 | 7.8923 | 7.8725 | 7.9576 | 7.7822 | 7.4458 | 122.5556 | -0.047299 | 123.0629 | 123.0808 | 0.52517 | -0.15768 | 0.020013 | 122.6741 | -0.037628 | 123.1047 | 123.1206 | 0.44644 | 0.047426 | -0.12794 | 123.0911 | 122.9807 | 123.1584 | 123.1461 | -0.58283 | 123.1008 | 123.1859 | 123.0105 | 123.0628 | -0.46431
690.2812 | 123.4085 | -115.3564 | 7.7957 | 0.057113 | 0.076902 | 0.01171 | -0.012856 | -0.04466 | 0.12163 | 0.043632 | 0.14557 | 0.0040533 | -0.020931 | 0.06715 | 0.081222 | 7.7065 | 7.7988 | 7.7243 | 7.7392 | 7.638 | 7.8065 | 7.2266 | 7.7436 | 7.7063 | 7.7549 | 7.7489 | 7.8248 | 7.6494 | 7.3451 | 122.583 | -0.056474 | 123.0629 | 123.0808 | 0.49772 | -0.15771 | 0.010832 | 122.7016 | -0.046806 | 123.1001 | 123.1114 | 0.40982 | 0.029087 | -0.14628 | 123.0957 | 122.9945 | 123.163 | 123.1552 | -0.56912 | 123.1054 | 123.1812 | 123.0059 | 123.0628 | -0.4506
691.2812 | 123.381 | -115.4343 | 7.7637 | 0.072375 | 0.076902 | 0.01171 | -0.013924 | -0.04466 | 0.1227 | 0.074154 | 0.14557 | 0.0051213 | -0.022 | 0.069286 | 0.08229 | 7.6744 | 7.7576 | 7.6785 | 7.698 | 7.5876 | 7.7745 | 7.1762 | 7.707 | 7.6651 | 7.7137 | 7.7031 | 7.7973 | 7.5991 | 7.3085 | 122.6105 | -0.065637 | 123.1087 | 123.1128 | 0.5023 | -0.17603 | 0.010824 | 122.7427 | -0.060548 | 123.1413 | 123.148 | 0.40524 | 0.033659 | -0.1646 | 123.1323 | 123.0219 | 123.2088 | 123.1918 | -0.58745 | 123.1374 | 123.2316 | 123.0333 | 123.0994 | -0.45519
692.2969 | 123.3582 | -115.5945 | 7.5577 | 0.057113 | 0.075833 | 0.01171 | -0.014993 | -0.043591 | 0.1227 | 0.074154 | 0.14557 | 0.0061893 | -0.024136 | 0.069286 | 0.083358 | 7.5096 | 7.6065 | 7.5274 | 7.5561 | 7.4411 | 7.6234 | 7.048 | 7.5651 | 7.5003 | 7.5672 | 7.5566 | 7.6417 | 7.4617 | 7.1894 | 122.6425 | -0.001573 | 123.1041 | 123.1219 | 0.47943 | -0.11657 | 0.065724 | 122.7839 | -0.001066 | 123.1596 | 123.1617 | 0.37777 | 0.08398 | -0.095962 | 123.1506 | 123.0356 | 123.2179 | 123.2009 | -0.50967 | 123.1511 | 123.2361 | 123.0562 | 123.0948 | -0.36825
693.8594 | 123.4818 | -115.7822 | 7.4112 | 0.057113 | 0.076902 | 0.010642 | -0.013924 | -0.042523 | 0.12163 | 0.074154 | 0.14343 | 0.0051213 | -0.020931 | 0.069286 | 0.08229 | 7.3356 | 7.4096 | 7.3443 | 7.3684 | 7.2534 | 7.4357 | 6.9015 | 7.3682 | 7.3263 | 7.3795 | 7.3735 | 7.4539 | 7.2694 | 7.0292 | 122.6837 | -0.042803 | 123.1178 | 123.1265 | 0.44282 | -0.15782 | 0.024486 | 122.8113 | -0.037722 | 123.1504 | 123.1616 | 0.3503 | 0.042742 | -0.14178 | 123.1506 | 123.0355 | 123.2178 | 123.1918 | -0.50971 | 123.1556 | 123.2361 | 123.0516 | 123.1085 | -0.38202
694.8281 | 123.262 | -115.86 | 7.3517 | 0.057113 | 0.076902 | 0.01171 | -0.013924 | -0.042523 | 0.1227 | 0.074154 | 0.14236 | 0.0072583 | -0.020931 | 0.069286 | 0.083358 | 7.2486 | 7.3317 | 7.2711 | 7.286 | 7.1755 | 7.3624 | 6.8282 | 7.2904 | 7.253 | 7.2925 | 7.2911 | 7.3761 | 7.2007 | 6.9513 | 122.6882 | -0.065704 | 123.1086 | 123.131 | 0.44283 | -0.17615 | 0.010737 | 122.8113 | -0.060626 | 123.1503 | 123.1525 | 0.34115 | 0.024414 | -0.15095 | 123.146 | 123.0355 | 123.2224 | 123.1917 | -0.52346 | 123.151 | 123.2361 | 123.0607 | 123.113 | -0.40035
695.9844 | 123.3673 | -115.9836 | 7.2144 | 0.041851 | 0.076902 | 0.01171 | -0.012856 | -0.04466 | 0.1227 | 0.089415 | 0.14557 | 0.0051213 | -0.022 | 0.070355 | 0.081222 | 7.1021 | 7.1898 | 7.1154 | 7.1441 | 7.0244 | 7.2068 | 6.6909 | 7.1438 | 7.0974 | 7.1551 | 7.1445 | 7.2342 | 7.0542 | 6.8277 | 122.6744 | -0.070305 | 123.0857 | 123.099 | 0.42454 | -0.18993 | -0.007605 | 122.8113 | -0.069807 | 123.1274 | 123.1387 | 0.32741 | 0.019808 | -0.16014 | 123.1276 | 123.008 | 123.1903 | 123.1734 | -0.5235 | 123.1281 | 123.2177 | 123.0378 | 123.0809 | -0.38665
697.5781 | 123.3948 | -116.0934 | 7.0404 | 0.057113 | 0.073697 | 0.010642 | -0.013924 | -0.043591 | 0.1227 | 0.058893 | 0.1445 | 0.0061893 | -0.022 | 0.070355 | 0.083358 | 6.9739 | 7.0662 | 6.9872 | 7.025 | 6.91 | 7.0877 | 6.5718 | 7.0248 | 6.9737 | 7.0269 | 7.0347 | 7.1014 | 6.9352 | 6.7178 | 122.6652 | -0.015393 | 123.0674 | 123.0806 | 0.4154 | -0.13045 | 0.047301 | 122.8113 | -0.005741 | 123.1182 | 123.1204 | 0.3091 | 0.060978 | -0.10523 | 123.1185 | 123.0034 | 123.1812 | 123.1596 | -0.4686 | 123.1281 | 123.1948 | 123.0286 | 123.0672 | -0.32259
698.7188 | 123.2803 | -116.2857 | 6.9717 | 0.026589 | 0.075833 | 0.01171 | -0.013924 | -0.045728 | 0.12163 | 0.074154 | 0.14343 | 0.0051213 | -0.023068 | 0.070355 | 0.083358 | 6.8549 | 6.938 | 6.8636 | 6.8968 | 6.7772 | 6.9687 | 6.4756 | 6.9057 | 6.8455 | 6.8941 | 6.8973 | 6.9823 | 6.8116 | 6.5988 | 122.7614 | -0.074923 | 123.1406 | 123.1493 | 0.38794 | -0.19457 | -0.003079 | 122.8845 | -0.074432 | 123.1914 | 123.1798 | 0.29537 | 0.010599 | -0.16019 | 123.1825 | 123.0629 | 123.2544 | 123.2237 | -0.49609 | 123.183 | 123.268 | 123.0973 | 123.1312 | -0.37298
699.4531 | 123.381 | -116.2903 | 6.8619 | 0.072375 | 0.074765 | 0.010642 | -0.013924 | -0.043591 | 0.12377 | 0.074154 | 0.1445 | 0.0061893 | -0.023068 | 0.069286 | 0.083358 | 6.7633 | 6.8602 | 6.7812 | 6.8144 | 6.7039 | 6.8817 | 6.3658 | 6.8096 | 6.7631 | 6.8163 | 6.8241 | 6.9045 | 6.7337 | 6.5255 | 122.656 | -0.04747 | 123.0536 | 123.0715 | 0.41543 | -0.15797 | 0.019792 | 122.8158 | -0.037824 | 123.0999 | 123.1066 | 0.29079 | 0.042626 | -0.12816 | 123.1047 | 122.9942 | 123.172 | 123.1504 | -0.49612 | 123.1143 | 123.1948 | 123.024 | 123.0534 | -0.33637
700.6562 | 123.3673 | -116.4368 | 6.752 | 0.057113 | 0.074765 | 0.01171 | -0.014993 | -0.042523 | 0.12163 | 0.089415 | 0.1445 | 0.0061893 | -0.024136 | 0.069286 | 0.08229 | 6.6489 | 6.7365 | 6.6576 | 6.6908 | 6.5803 | 6.758 | 6.2742 | 6.6768 | 6.6441 | 6.6881 | 6.7004 | 6.7717 | 6.6101 | 6.4065 | 122.7109 | -0.061224 | 123.0856 | 123.0943 | 0.38339 | -0.17174 | 0.006033 | 122.8432 | -0.05158 | 123.1136 | 123.1249 | 0.28163 | 0.01971 | -0.14192 | 123.1276 | 123.017 | 123.1948 | 123.1733 | -0.47784 | 123.1372 | 123.2085 | 123.0469 | 123.0808 | -0.34556
704.8281 | 123.2986 | -116.8396 | 6.3766 | 0.057113 | 0.074765 | 0.01171 | -0.013924 | -0.043591 | 0.1227 | 0.043632 | 0.14343 | 0.0051213 | -0.020931 | 0.070355 | 0.08229 | 6.2918 | 6.3702 | 6.305 | 6.3474 | 6.2277 | 6.4147 | 5.9491 | 6.3334 | 6.2915 | 6.3401 | 6.3387 | 6.4238 | 6.2575 | 6.0814 | 122.7887 | -0.029237 | 123.1314 | 123.1446 | 0.35597 | -0.14895 | 0.038003 | 122.921 | -0.037916 | 123.173 | 123.1797 | 0.25875 | 0.047102 | -0.11911 | 123.187 | 123.0673 | 123.2543 | 123.2098 | -0.42758 | 123.1783 | 123.2634 | 123.0971 | 123.1311 | -0.29529
705.3594 | 123.381 | -116.8304 | 6.3492 | 0.041851 | 0.075833 | 0.01171 | -0.013924 | -0.04466 | 0.1227 | 0.043632 | 0.14343 | 0.0072583 | -0.022 | 0.071423 | 0.08229 | 6.246 | 6.329 | 6.2547 | 6.2833 | 6.1819 | 6.3643 | 5.885 | 6.2876 | 6.2457 | 6.2943 | 6.2975 | 6.3871 | 6.2072 | 6.031 | 122.7154 | -0.065868 | 123.0764 | 123.0851 | 0.36971 | -0.16728 | 0.015105 | 122.8614 | -0.051656 | 123.1181 | 123.1248 | 0.26333 | 0.037939 | -0.142 | 123.1138 | 123.0124 | 123.1947 | 123.1595 | -0.46422 | 123.128 | 123.2176 | 123.0376 | 123.0762 | -0.31819
706.2812 | 123.381 | -116.8991 | 6.2393 | 0.072375 | 0.073697 | 0.01171 | -0.013924 | -0.04466 | 0.12484 | 0.074154 | 0.1445 | 0.0061893 | -0.023068 | 0.070355 | 0.08229 | 6.159 | 6.2375 | 6.1723 | 6.2009 | 6.1041 | 6.2819 | 5.8071 | 6.2052 | 6.1587 | 6.2027 | 6.2197 | 6.2955 | 6.1293 | 5.9532 | 122.7062 | -0.038416 | 123.0581 | 123.0714 | 0.36515 | -0.13525 | 0.042553 | 122.8523 | -0.019627 | 123.1043 | 123.1019 | 0.24959 | 0.05623 | -0.10998 | 123.1 | 123.0032 | 123.181 | 123.1366 | -0.4322 | 123.1188 | 123.1947 | 123.0285 | 123.0578 | -0.28617
707.2812 | 123.3902 | -117.009 | 6.1432 | 0.041851 | 0.073697 | 0.01171 | -0.014993 | -0.045728 | 0.12377 | 0.058893 | 0.14557 | 0.0051213 | -0.023068 | 0.070355 | 0.083358 | 6.0537 | 6.1322 | 6.0578 | 6.1002 | 5.9896 | 6.172 | 5.7018 | 6.0816 | 6.0443 | 6.0883 | 6.1098 | 6.1765 | 6.024 | 5.857 | 122.7108 | -0.04301 | 123.0626 | 123.0668 | 0.356 | -0.1536 | 0.028797 | 122.866 | -0.03338 | 123.0905 | 123.0973 | 0.23128 | 0.033317 | -0.11915 | 123.1091 | 122.9986 | 123.181 | 123.1411 | -0.44138 | 123.1188 | 123.1855 | 123.033 | 123.0532 | -0.28619
708.3125 | 123.3261 | -117.1783 | 6.0516 | 0.057113 | 0.074765 | 0.01171 | -0.014993 | -0.04466 | 0.12377 | 0.074154 | 0.14343 | 0.0061893 | -0.024136 | 0.072491 | 0.08229 | 5.9438 | 6.0223 | 5.9479 | 5.9857 | 5.8843 | 6.0713 | 5.5919 | 5.9808 | 5.9389 | 5.983 | 5.9908 | 6.0712 | 5.9096 | 5.7471 | 122.7703 | -0.065918 | 123.1221 | 123.1263 | 0.35602 | -0.16736 | 0.01962 | 122.9254 | -0.060869 | 123.1592 | 123.1613 | 0.23586 | 0.019562 | -0.14207 | 123.1641 | 123.0626 | 123.2496 | 123.2006 | -0.45972 | 123.1691 | 123.2495 | 123.0879 | 123.1173 | -0.30453
709.2812 | 123.3902 | -117.2562 | 5.9143 | 0.041851 | 0.074765 | 0.01171 | -0.014993 | -0.046796 | 0.12484 | 0.058893 | 0.14343 | 0.0051213 | -0.022 | 0.070355 | 0.08229 | 5.8202 | 5.8986 | 5.8381 | 5.8713 | 5.7698 | 5.9476 | 5.4912 | 5.8618 | 5.8153 | 5.8593 | 5.8763 | 5.9567 | 5.7905 | 5.6326 | 122.7473 | -0.043048 | 123.0763 | 123.0942 | 0.34688 | -0.1445 | 0.033327 | 122.8888 | -0.038003 | 123.118 | 123.1155 | 0.22671 | 0.042426 | -0.12378 | 123.1274 | 123.026 | 123.2038 | 123.1548 | -0.42313 | 123.1325 | 123.2129 | 123.0467 | 123.0715 | -0.28167
710.2812 | 123.4039 | -117.3019 | 5.8273 | 0.057113 | 0.073697 | 0.012779 | -0.013924 | -0.045728 | 0.1227 | 0.043632 | 0.1445 | 0.0072583 | -0.023068 | 0.070355 | 0.083358 | 5.7286 | 5.8117 | 5.7419 | 5.7843 | 5.6782 | 5.8561 | 5.4088 | 5.7748 | 5.7283 | 5.7769 | 5.7939 | 5.8697 | 5.7081 | 5.5502 | 122.7107 | -0.043063 | 123.0306 | 123.0439 | 0.33315 | -0.14911 | 0.02873 | 122.8522 | -0.03344 | 123.0767 | 123.0789 | 0.22671 | 0.042407 | -0.11922 | 123.0862 | 122.9802 | 123.158 | 123.1136 | -0.41857 | 123.0958 | 123.1717 | 123.0101 | 123.0303 | -0.27712
711.2812 | 123.3856 | -117.4164 | 5.7449 | 0.057113 | 0.075833 | 0.01171 | -0.013924 | -0.04466 | 0.12377 | 0.058893 | 0.1445 | 0.0051213 | -0.022 | 0.069286 | 0.083358 | 5.6645 | 5.7476 | 5.6778 | 5.7202 | 5.6141 | 5.7874 | 5.3492 | 5.7061 | 5.6642 | 5.6991 | 5.7161 | 5.8011 | 5.6394 | 5.4815 | 122.7656 | -0.024762 | 123.0809 | 123.0942 | 0.32858 | -0.13081 | 0.042449 | 122.8979 | -0.028877 | 123.1225 | 123.1155 | 0.21755 | 0.056126 | -0.1055 | 123.1366 | 123.0305 | 123.2038 | 123.1639 | -0.3957 | 123.1324 | 123.2174 | 123.0558 | 123.0806 | -0.2634
712.2812 | 123.3856 | -117.5491 | 5.6488 | 0.026589 | 0.074765 | 0.010642 | -0.013924 | -0.04466 | 0.1227 | 0.089415 | 0.14343 | 0.0051213 | -0.023068 | 0.070355 | 0.080154 | 5.5317 | 5.6056 | 5.5359 | 5.5782 | 5.4813 | 5.6546 | 5.1935 | 5.5688 | 5.5223 | 5.5709 | 5.5833 | 5.6683 | 5.4883 | 5.3396 | 122.7427 | -0.070562 | 123.0809 | 123.085 | 0.34234 | -0.16747 | 0.005799 | 122.8887 | -0.065523 | 123.1179 | 123.12 | 0.23129 | 0.019477 | -0.16047 | 123.1274 | 123.0305 | 123.2037 | 123.1547 | -0.45526 | 123.1324 | 123.2174 | 123.0375 | 123.0714 | -0.30921
713.2812 | 123.4177 | -117.6407 | 5.5298 | 0.041851 | 0.072628 | 0.01171 | -0.016061 | -0.04466 | 0.12484 | 0.043632 | 0.14343 | 0.0061893 | -0.022 | 0.069286 | 0.080154 | 5.431 | 5.5049 | 5.4352 | 5.4913 | 5.3852 | 5.5539 | 5.1111 | 5.468 | 5.417 | 5.461 | 5.4917 | 5.5676 | 5.3968 | 5.2297 | 122.7518 | -0.038533 | 123.0717 | 123.0759 | 0.32404 | -0.14461 | 0.024089 | 122.8704 | -0.038074 | 123.1087 | 123.1017 | 0.2313 | 0.037766 | -0.13302 | 123.1319 | 123.0259 | 123.1946 | 123.1456 | -0.41866 | 123.1324 | 123.2082 | 123.0375 | 123.0577 | -0.30009
714.2812 | 123.3902 | -117.7368 | 5.4337 | 0.026589 | 0.073697 | 0.0095741 | -0.014993 | -0.04466 | 0.12056 | 0.058893 | 0.1445 | 0.0051213 | -0.022 | 0.070355 | 0.083358 | 5.3211 | 5.4133 | 5.339 | 5.3905 | 5.2844 | 5.4623 | 5.0241 | 5.381 | 5.3208 | 5.3557 | 5.4001 | 5.4714 | 5.3052 | 5.1427 | 122.7609 | -0.043127 | 123.058 | 123.0758 | 0.31489 | -0.14922 | 0.028647 | 122.8795 | -0.033514 | 123.1178 | 123.0925 | 0.21298 | 0.037746 | -0.12846 | 123.1273 | 123.0213 | 123.1991 | 123.1501 | -0.40953 | 123.137 | 123.2082 | 123.042 | 123.0576 | -0.29096
715.3125 | 123.3398 | -117.9016 | 5.3284 | 0.041851 | 0.07156 | 0.010642 | -0.013924 | -0.045728 | 0.1227 | 0.074154 | 0.14343 | 0.0051213 | -0.020931 | 0.070355 | 0.08229 | 5.225 | 5.3034 | 5.2337 | 5.2761 | 5.1608 | 5.3433 | 4.9051 | 5.262 | 5.2109 | 5.2595 | 5.2857 | 5.3661 | 5.1953 | 5.0328 | 122.8067 | -0.052301 | 123.1266 | 123.1353 | 0.32865 | -0.16756 | 0.014889 | 122.9344 | -0.04269 | 123.1636 | 123.1611 | 0.22672 | 0.037724 | -0.13306 | 123.1777 | 123.0624 | 123.2449 | 123.205 | -0.42329 | 123.1873 | 123.2677 | 123.0969 | 123.1125 | -0.29556
716.2812 | 123.4085 | -117.952 | 5.1956 | 0.041851 | 0.074765 | 0.010642 | -0.013924 | -0.04466 | 0.12163 | 0.043632 | 0.14343 | 0.0061893 | -0.023068 | 0.070355 | 0.081222 | 5.1059 | 5.1935 | 5.1284 | 5.1753 | 5.0601 | 5.2471 | 4.7998 | 5.1521 | 5.0965 | 5.1451 | 5.1712 | 5.2562 | 5.09 | 4.9321 | 122.7517 | -0.020274 | 123.0579 | 123.0804 | 0.32866 | -0.13555 | 0.05149 | 122.884 | -0.024402 | 123.1041 | 123.097 | 0.21299 | 0.060588 | -0.10562 | 123.1273 | 123.012 | 123.1991 | 123.1455 | -0.39586 | 123.1232 | 123.2082 | 123.042 | 123.0484 | -0.26354
717.2812 | 123.3765 | -118.0481 | 5.1361 | 0.057113 | 0.072628 | 0.012779 | -0.014993 | -0.04466 | 0.12377 | 0.058893 | 0.1445 | 0.0072583 | -0.023068 | 0.071423 | 0.081222 | 5.0281 | 5.1065 | 5.046 | 5.0838 | 4.9822 | 5.1647 | 4.7311 | 5.0743 | 5.014 | 5.0581 | 5.0934 | 5.1738 | 5.0122 | 4.8542 | 122.7792 | -0.052332 | 123.0762 | 123.0941 | 0.31494 | -0.15388 | 0.028585 | 122.9023 | -0.042726 | 123.1224 | 123.1062 | 0.20383 | 0.037684 | -0.12394 | 123.1319 | 123.0303 | 123.2128 | 123.1546 | -0.40503 | 123.1415 | 123.2219 | 123.0603 | 123.0621 | -0.28187
718.2812 | 123.3032 | -118.1946 | 5.0674 | 0.041851 | 0.072628 | 0.010642 | -0.014993 | -0.045728 | 0.1227 | 0.089415 | 0.1445 | 0.0040533 | -0.023068 | 0.069286 | 0.08229 | 4.9457 | 5.0333 | 4.959 | 5.0105 | 4.8952 | 5.0823 | 4.6441 | 4.9827 | 4.9271 | 4.9619 | 5.011 | 5.0914 | 4.9343 | 4.7489 | 122.8387 | -0.056922 | 123.1403 | 123.1536 | 0.31495 | -0.17222 | 0.014834 | 122.9435 | -0.056475 | 123.1773 | 123.1565 | 0.21299 | 0.023933 | -0.13312 | 123.2051 | 123.0898 | 123.2769 | 123.2279 | -0.42337 | 123.2055 | 123.286 | 123.1289 | 123.1216 | -0.31852
719.3125 | 123.317 | -118.309 | 4.9347 | 0.087637 | 0.073697 | 0.010642 | -0.014993 | -0.045728 | 0.1227 | 0.089415 | 0.14343 | 0.0040533 | -0.022 | 0.071423 | 0.081222 | 4.8267 | 4.9005 | 4.8308 | 4.8823 | 4.7808 | 4.9495 | 4.5159 | 4.8636 | 4.7805 | 4.8291 | 4.8919 | 4.9769 | 4.8107 | 4.6161 | 122.8249 | -0.052365 | 123.1357 | 123.1399 | 0.31497 | -0.15394 | 0.014807 | 122.9252 | -0.042764 | 123.1727 | 123.1382 | 0.213 | 0.04222 | -0.12399 | 123.1913 | 123.0898 | 123.2585 | 123.2095 | -0.41883 | 123.2009 | 123.2859 | 123.1197 | 123.0896 | -0.31856
720.2812 | 123.3215 | -118.3823 | 4.8569 | 0.041851 | 0.073697 | 0.010642 | -0.014993 | -0.04466 | 0.12163 | 0.043632 | 0.14343 | 0.0061893 | -0.022 | 0.070355 | 0.08229 | 4.7397 | 4.8181 | 4.7576 | 4.7953 | 4.6983 | 4.8762 | 4.4426 | 4.7766 | 4.6752 | 4.7238 | 4.8049 | 4.8899 | 4.71 | 4.5017 | 122.8249 | -0.061535 | 123.1219 | 123.1398 | 0.31498 | -0.15854 | 0.019368 | 122.8839 | -0.051936 | 123.1589 | 123.1061 | 0.22216 | 0.033045 | -0.1469 | 123.1776 | 123.0806 | 123.2585 | 123.2004 | -0.41427 | 123.1872 | 123.2722 | 123.0922 | 123.0575 | -0.35521
721.2812 | 123.3719 | -118.4875 | 4.715 | 0.057113 | 0.072628 | 0.0095741 | -0.016061 | -0.045728 | 0.1227 | 0.089415 | 0.14343 | 0.0061893 | -0.022 | 0.072491 | 0.08229 | 4.6206 | 4.7036 | 4.634 | 4.6809 | 4.5747 | 4.7526 | 4.3144 | 4.6576 | 4.5699 | 4.6002 | 4.6859 | 4.7571 | 4.5955 | 4.3918 | 122.8019 | -0.034088 | 123.1082 | 123.1215 | 0.31957 | -0.14026 | 0.037653 | 122.8793 | -0.02907 | 123.1451 | 123.0877 | 0.20842 | 0.042173 | -0.11946 | 123.1684 | 123.0623 | 123.2402 | 123.1912 | -0.40057 | 123.1734 | 123.2447 | 123.0831 | 123.0575 | -0.32319
722.2812 | 123.3215 | -118.5883 | 4.6326 | 0.041851 | 0.072628 | 0.0095741 | -0.014993 | -0.043591 | 0.1227 | 0.043632 | 0.14343 | 0.0061893 | -0.022 | 0.071423 | 0.08229 | 4.5199 | 4.6075 | 4.5378 | 4.5893 | 4.474 | 4.6565 | 4.2228 | 4.566 | 4.4738 | 4.5132 | 4.5852 | 4.6747 | 4.4994 | 4.3002 | 122.8111 | -0.043258 | 123.1082 | 123.1261 | 0.31501 | -0.1586 | 0.0239 | 122.8885 | -0.047399 | 123.1543 | 123.1015 | 0.213 | 0.042156 | -0.13321 | 123.1776 | 123.0622 | 123.2447 | 123.1957 | -0.40975 | 123.1734 | 123.263 | 123.0876 | 123.062 | -0.33237
723.2812 | 123.317 | -118.6981 | 4.541 | 0.041851 | 0.072628 | 0.0095741 | -0.014993 | -0.04466 | 0.1227 | 0.074154 | 0.14343 | 0.0061893 | -0.020931 | 0.070355 | 0.08229 | 4.4329 | 4.5068 | 4.4371 | 4.5023 | 4.3915 | 4.5741 | 4.1267 | 4.4699 | 4.3684 | 4.4079 | 4.4982 | 4.5786 | 4.4169 | 4.1903 | 122.8248 | -0.038695 | 123.131 | 123.1352 | 0.31044 | -0.14947 | 0.033037 | 122.8884 | -0.042839 | 123.168 | 123.106 | 0.21759 | 0.037557 | -0.12407 | 123.2004 | 123.0897 | 123.2722 | 123.2049 | -0.41436 | 123.1963 | 123.2767 | 123.1151 | 123.0666 | -0.35071
724.2812 | 123.3261 | -118.8126 | 4.4357 | 0.057113 | 0.07156 | 0.010642 | -0.013924 | -0.045728 | 0.1227 | 0.043632 | 0.14343 | 0.0051213 | -0.022 | 0.072491 | 0.08229 | 4.3139 | 4.3923 | 4.3226 | 4.3787 | 4.2633 | 4.4504 | 4.0259 | 4.3508 | 4.2494 | 4.2934 | 4.3791 | 4.4641 | 4.2887 | 4.0758 | 122.8385 | -0.057026 | 123.1265 | 123.1352 | 0.29672 | -0.17239 | 0.014701 | 122.8884 | -0.056593 | 123.1634 | 123.106 | 0.21759 | 0.028378 | -0.14699 | 123.1913 | 123.0759 | 123.263 | 123.2048 | -0.40981 | 123.1917 | 123.2767 | 123.1013 | 123.062 | -0.35989
725.2812 | 123.2666 | -118.9041 | 4.3579 | 0.041851 | 0.072628 | 0.010642 | -0.014993 | -0.046796 | 0.1227 | 0.043632 | 0.14343 | 0.0040533 | -0.022 | 0.071423 | 0.080154 | 4.2361 | 4.3099 | 4.2494 | 4.2963 | 4.1855 | 4.3772 | 3.9298 | 4.273 | 4.167 | 4.1927 | 4.3013 | 4.3817 | 4.2201 | 3.9934 | 122.8339 | -0.061617 | 123.1402 | 123.1535 | 0.31963 | -0.17241 | 0.019263 | 122.8975 | -0.056608 | 123.1771 | 123.0968 | 0.19928 | 0.023783 | -0.13785 | 123.2004 | 123.0896 | 123.2813 | 123.214 | -0.42815 | 123.2054 | 123.2858 | 123.1242 | 123.0711 | -0.36449
726.2812 | 123.2941 | -119.0002 | 4.3167 | 0.072375 | 0.072628 | 0.01171 | -0.013924 | -0.047865 | 0.12163 | 0.043632 | 0.14343 | 0.0040533 | -0.023068 | 0.071423 | 0.08229 | 4.1536 | 4.232 | 4.167 | 4.223 | 4.1168 | 4.2948 | 3.8473 | 4.1951 | 4.0891 | 4.1194 | 4.228 | 4.2947 | 4.1285 | 3.9202 | 122.8476 | -0.093672 | 123.1539 | 123.1672 | 0.31964 | -0.1999 | -0.021953 | 122.9204 | -0.088665 | 123.1954 | 123.1197 | 0.19928 | -0.022011 | -0.18822 | 123.2233 | 123.1171 | 123.295 | 123.2323 | -0.46937 | 123.2283 | 123.2949 | 123.1287 | 123.0894 | -0.39655
727.2812 | 123.2666 | -119.0689 | 4.216 | 0.041851 | 0.07156 | 0.010642 | -0.014993 | -0.045728 | 0.12377 | 0.058893 | 0.14343 | 0.0051213 | -0.022 | 0.07356 | 0.080154 | 4.0804 | 4.1588 | 4.0892 | 4.1361 | 4.0161 | 4.2261 | 3.7787 | 4.1219 | 4.0159 | 4.0462 | 4.1502 | 4.2352 | 4.0552 | 3.8469 | 122.8476 | -0.079953 | 123.1493 | 123.1581 | 0.31049 | -0.19993 | 0.010076 | 122.9158 | -0.065791 | 123.1908 | 123.1151 | 0.19928 | 0.019175 | -0.16077 | 123.205 | 123.085 | 123.295 | 123.2277 | -0.43734 | 123.2191 | 123.3041 | 123.1241 | 123.0848 | -0.36911
728.2812 | 123.2712 | -119.1422 | 4.1199 | 0.072375 | 0.072628 | 0.0085051 | -0.014993 | -0.04466 | 0.12163 | 0.058893 | 0.1445 | 0.0051213 | -0.024136 | 0.070355 | 0.081222 | 3.9934 | 4.0718 | 4.0067 | 4.0582 | 3.9474 | 4.1345 | 3.7146 | 4.0395 | 3.9197 | 3.9638 | 4.0541 | 4.1482 | 3.9637 | 3.7691 | 122.8567 | -0.061656 | 123.1356 | 123.1489 | 0.29219 | -0.17248 | 0.014634 | 122.9112 | -0.06581 | 123.1816 | 123.1059 | 0.1947 | 0.028312 | -0.15621 | 123.2004 | 123.0895 | 123.2767 | 123.2139 | -0.40532 | 123.1962 | 123.2903 | 123.1058 | 123.0619 | -0.35082
729.2812 | 123.2895 | -119.2474 | 4.0604 | 0.041851 | 0.07156 | 0.0085051 | -0.013924 | -0.04466 | 0.12163 | 0.028371 | 0.1445 | 0.0051213 | -0.024136 | 0.071423 | 0.08229 | 3.9064 | 3.9802 | 3.906 | 3.9712 | 3.8512 | 4.0384 | 3.6184 | 3.9342 | 3.819 | 3.8539 | 3.9762 | 4.052 | 3.8812 | 3.6729 | 122.8658 | -0.089136 | 123.1538 | 123.1535 | 0.28762 | -0.20913 | -0.022007 | 122.9203 | -0.084135 | 123.1816 | 123.1013 | 0.18097 | -0.00833 | -0.17912 | 123.2187 | 123.0987 | 123.2858 | 123.2276 | -0.44197 | 123.2237 | 123.2995 | 123.1287 | 123.0664 | -0.38746
730.2812 | 123.2803 | -119.3207 | 3.9505 | 0.041851 | 0.072628 | 0.01171 | -0.014993 | -0.04466 | 0.12163 | 0.043632 | 0.1445 | 0.0040533 | -0.020931 | 0.072491 | 0.081222 | 3.8194 | 3.9024 | 3.8419 | 3.8934 | 3.7734 | 3.9697 | 3.536 | 3.8609 | 3.7595 | 3.7806 | 3.8938 | 3.9742 | 3.8034 | 3.5951 | 122.8567 | -0.057105 | 123.1401 | 123.1626 | 0.30595 | -0.17711 | 0.019178 | 122.9157 | -0.056684 | 123.1816 | 123.1013 | 0.18555 | 0.023698 | -0.14709 | 123.2141 | 123.0941 | 123.2904 | 123.2231 | -0.41452 | 123.2145 | 123.2949 | 123.1241 | 123.0802 | -0.35544
731.2969 | 123.4131 | -119.371 | 3.8452 | 0.072375 | 0.072628 | 0.0095741 | -0.013924 | -0.045728 | 0.1227 | 0.058893 | 0.14557 | 0.0051213 | -0.022 | 0.072491 | 0.084427 | 3.7416 | 3.8108 | 3.7549 | 3.811 | 3.6864 | 3.8873 | 3.4627 | 3.7831 | 3.6725 | 3.6982 | 3.8206 | 3.8964 | 3.721 | 3.5172 | 122.8337 | -0.034231 | 123.1126 | 123.126 | 0.29222 | -0.15882 | 0.042048 | 122.8883 | -0.024655 | 123.1541 | 123.0692 | 0.18097 | 0.051146 | -0.12422 | 123.182 | 123.0574 | 123.2583 | 123.1818 | -0.3825 | 123.1916 | 123.2674 | 123.092 | 123.0435 | -0.328
732.2812 | 123.3032 | -119.4489 | 3.7994 | 0.057113 | 0.07156 | 0.0095741 | -0.014993 | -0.04466 | 0.12056 | 0.074154 | 0.14557 | 0.0051213 | -0.024136 | 0.07356 | 0.080154 | 3.6775 | 3.765 | 3.6908 | 3.756 | 3.6314 | 3.8232 | 3.4032 | 3.719 | 3.613 | 3.6432 | 3.7473 | 3.8368 | 3.6569 | 3.4531 | 122.852 | -0.043395 | 123.1263 | 123.1397 | 0.28765 | -0.16799 | 0.023724 | 122.902 | -0.052134 | 123.1678 | 123.0921 | 0.19013 | 0.037402 | -0.14254 | 123.2049 | 123.0803 | 123.272 | 123.2139 | -0.39625 | 123.1962 | 123.2857 | 123.1058 | 123.0618 | -0.34632
733.2812 | 123.3307 | -119.5312 | 3.7125 | 0.057113 | 0.070491 | 0.0095741 | -0.014993 | -0.045728 | 0.12056 | 0.074154 | 0.14664 | 0.0051213 | -0.024136 | 0.07356 | 0.08229 | 3.5951 | 3.6734 | 3.6084 | 3.6599 | 3.549 | 3.7453 | 3.2979 | 3.632 | 3.5351 | 3.5654 | 3.6695 | 3.7498 | 3.5699 | 3.3753 | 122.8291 | -0.052566 | 123.1263 | 123.1397 | 0.31056 | -0.16344 | 0.032863 | 122.9065 | -0.042993 | 123.1632 | 123.0967 | 0.19013 | 0.037383 | -0.14256 | 123.1911 | 123.0803 | 123.2766 | 123.2047 | -0.41459 | 123.2007 | 123.2811 | 123.1012 | 123.0664 | -0.33719
734.2812 | 123.2941 | -119.6091 | 3.6484 | 0.041851 | 0.070491 | 0.0085051 | -0.012856 | -0.04466 | 0.12056 | 0.058893 | 0.14664 | 0.0040533 | -0.024136 | 0.07356 | 0.081222 | 3.5218 | 3.6093 | 3.5398 | 3.5958 | 3.4895 | 3.6766 | 3.2521 | 3.5633 | 3.4756 | 3.4876 | 3.5962 | 3.6857 | 3.4921 | 3.302 | 122.8612 | -0.052576 | 123.1309 | 123.1488 | 0.28767 | -0.15888 | 0.028271 | 122.9111 | -0.052162 | 123.1724 | 123.0966 | 0.18555 | 0.03737 | -0.15631 | 123.2049 | 123.0986 | 123.2857 | 123.2184 | -0.39629 | 123.2053 | 123.2948 | 123.1011 | 123.0847 | -0.34636
735.2969 | 123.4039 | -119.6594 | 3.566 | 0.072375 | 0.070491 | 0.0085051 | -0.016061 | -0.04466 | 0.12056 | 0.058893 | 0.1445 | 0.0051213 | -0.023068 | 0.072491 | 0.08229 | 3.4486 | 3.5178 | 3.4619 | 3.518 | 3.3979 | 3.5897 | 3.1697 | 3.49 | 3.384 | 3.4052 | 3.5184 | 3.5942 | 3.4371 | 3.2196 | 122.8291 | -0.048012 | 123.108 | 123.1214 | 0.29226 | -0.16806 | 0.023675 | 122.879 | -0.0476 | 123.1494 | 123.0646 | 0.18556 | 0.028195 | -0.12886 | 123.1774 | 123.0573 | 123.2491 | 123.1772 | -0.39632 | 123.1778 | 123.2536 | 123.0965 | 123.0435 | -0.34638
736.2812 | 123.3078 | -119.7693 | 3.4973 | 0.057113 | 0.070491 | 0.0095741 | -0.013924 | -0.04466 | 0.1195 | 0.074154 | 0.14343 | 0.0029843 | -0.024136 | 0.07356 | 0.081222 | 3.3891 | 3.4583 | 3.3933 | 3.4539 | 3.3155 | 3.5347 | 3.0964 | 3.4168 | 3.3153 | 3.3502 | 3.4589 | 3.5392 | 3.3593 | 3.1692 | 122.8657 | -0.043444 | 123.1583 | 123.1625 | 0.29685 | -0.18181 | 0.037396 | 122.9385 | -0.038455 | 123.1861 | 123.1195 | 0.18098 | 0.041916 | -0.13803 | 123.2232 | 123.0848 | 123.304 | 123.2275 | -0.40091 | 123.2281 | 123.3085 | 123.1286 | 123.0846 | -0.32808
737.2812 | 123.317 | -119.8425 | 3.447 | 0.041851 | 0.070491 | 0.0074371 | -0.016061 | -0.045728 | 0.1195 | 0.043632 | 0.14343 | 0.0051213 | -0.024136 | 0.072491 | 0.08229 | 3.3204 | 3.3942 | 3.3292 | 3.3852 | 3.2606 | 3.4615 | 3.0277 | 3.3435 | 3.2512 | 3.2769 | 3.3902 | 3.4706 | 3.2952 | 3.1005 | 122.8702 | -0.061766 | 123.1629 | 123.1717 | 0.30144 | -0.18641 | 0.014493 | 122.9431 | -0.056778 | 123.186 | 123.1195 | 0.1764 | 0.023591 | -0.15177 | 123.2277 | 123.1031 | 123.304 | 123.2367 | -0.41924 | 123.2327 | 123.3131 | 123.1377 | 123.0938 | -0.34641
738.2812 | 123.3307 | -119.8929 | 3.3737 | 0.041851 | 0.07156 | 0.0085051 | -0.016061 | -0.046796 | 0.1227 | 0.058893 | 0.14343 | 0.0051213 | -0.024136 | 0.07356 | 0.08229 | 3.2609 | 3.3301 | 3.2651 | 3.3211 | 3.201 | 3.4065 | 2.9773 | 3.2931 | 3.1963 | 3.2083 | 3.3261 | 3.4065 | 3.2311 | 3.0364 | 122.8702 | -0.052621 | 123.1537 | 123.1579 | 0.28771 | -0.17269 | 0.032792 | 122.9293 | -0.047635 | 123.186 | 123.1012 | 0.17183 | 0.032733 | -0.14263 | 123.214 | 123.0939 | 123.2994 | 123.2229 | -0.39637 | 123.219 | 123.2993 | 123.124 | 123.0892 | -0.33727
739.2812 | 123.3536 | -119.9432 | 3.3371 | 0.087637 | 0.069423 | 0.010642 | -0.014993 | -0.045728 | 0.12056 | 0.043632 | 0.1445 | 0.0051213 | -0.020931 | 0.07356 | 0.081222 | 3.1968 | 3.2705 | 3.2101 | 3.2616 | 3.1507 | 3.3424 | 2.9087 | 3.2382 | 3.1276 | 3.1396 | 3.2666 | 3.3515 | 3.1761 | 2.9769 | 122.8519 | -0.075519 | 123.14 | 123.1534 | 0.30146 | -0.18644 | 0.005312 | 122.9202 | -0.070535 | 123.1814 | 123.0828 | 0.16267 | 0.014411 | -0.16095 | 123.2048 | 123.0939 | 123.2856 | 123.2138 | -0.42843 | 123.2098 | 123.2947 | 123.1194 | 123.0709 | -0.36018
740.2812 | 123.349 | -120.0073 | 3.2593 | 0.057113 | 0.070491 | 0.010642 | -0.014993 | -0.045728 | 0.12163 | 0.058893 | 0.14557 | 0.0051213 | -0.024136 | 0.072491 | 0.081222 | 3.1418 | 3.2156 | 3.1506 | 3.2066 | 3.082 | 3.292 | 2.8583 | 3.1741 | 3.0773 | 3.0846 | 3.2116 | 3.2874 | 3.1029 | 2.9174 | 122.8656 | -0.05264 | 123.1491 | 123.1579 | 0.29231 | -0.1773 | 0.032768 | 122.9247 | -0.047657 | 123.1814 | 123.092 | 0.16725 | 0.02813 | -0.15639 | 123.214 | 123.0893 | 123.2994 | 123.2229 | -0.40098 | 123.2189 | 123.2947 | 123.1102 | 123.0846 | -0.34188
741.2812 | 123.3444 | -120.0623 | 3.2089 | 0.041851 | 0.07156 | 0.0095741 | -0.014993 | -0.045728 | 0.1195 | 0.058893 | 0.14557 | 0.0061893 | -0.024136 | 0.072491 | 0.083358 | 3.0731 | 3.1469 | 3.0774 | 3.1471 | 3.0316 | 3.2188 | 2.7759 | 3.1054 | 3.0131 | 3.0297 | 3.1429 | 3.2187 | 3.0434 | 2.867 | 122.8381 | -0.061805 | 123.1354 | 123.1396 | 0.30148 | -0.17732 | 0.009864 | 122.9293 | -0.06598 | 123.1677 | 123.092 | 0.16267 | 0.009805 | -0.16556 | 123.2094 | 123.0939 | 123.281 | 123.2092 | -0.43305 | 123.2052 | 123.281 | 123.1056 | 123.0754 | -0.3419
742.2812 | 123.3582 | -120.0851 | 3.1265 | 0.057113 | 0.070491 | 0.0095741 | -0.017129 | -0.043591 | 0.12163 | 0.028371 | 0.14343 | 0.0040533 | -0.025204 | 0.07356 | 0.081222 | 3.0136 | 3.0965 | 3.0178 | 3.083 | 2.9675 | 3.1638 | 2.7118 | 3.0413 | 2.949 | 2.9748 | 3.0834 | 3.1638 | 2.9747 | 2.7938 | 122.7969 | -0.043506 | 123.0988 | 123.103 | 0.30606 | -0.15902 | 0.037318 | 122.8789 | -0.043104 | 123.1265 | 123.0599 | 0.18099 | 0.037259 | -0.15184 | 123.1682 | 123.0526 | 123.249 | 123.1817 | -0.41475 | 123.1686 | 123.2489 | 123.0598 | 123.0342 | -0.33276
743.2812 | 123.349 | -120.1767 | 3.0945 | 0.072375 | 0.07156 | 0.0085051 | -0.014993 | -0.046796 | 0.12056 | 0.028371 | 0.14343 | 0.0029843 | -0.023068 | 0.07356 | 0.083358 | 2.9587 | 3.0416 | 2.9675 | 3.0235 | 2.8942 | 3.1089 | 2.6751 | 2.9955 | 2.8941 | 2.9015 | 3.0239 | 3.1043 | 2.9289 | 2.7388 | 122.8518 | -0.070981 | 123.1354 | 123.1442 | 0.29233 | -0.20024 | 0.014418 | 122.9155 | -0.07058 | 123.1722 | 123.0782 | 0.16267 | 0.009781 | -0.16558 | 123.2002 | 123.0709 | 123.2856 | 123.2183 | -0.41934 | 123.2006 | 123.281 | 123.1056 | 123.0708 | -0.35566
744.2812 | 123.3673 | -120.2454 | 3.0487 | 0.057113 | 0.069423 | 0.010642 | -0.012856 | -0.045728 | 0.12163 | 0.058893 | 0.1445 | 0.0040533 | -0.023068 | 0.07356 | 0.080154 | 2.9175 | 2.9867 | 2.9217 | 2.9731 | 2.8576 | 3.0631 | 2.6294 | 2.9497 | 2.8437 | 2.8603 | 2.9873 | 3.0631 | 2.8831 | 2.6885 | 122.8747 | -0.075567 | 123.1628 | 123.1671 | 0.29234 | -0.1911 | 0.014408 | 122.9338 | -0.061432 | 123.1951 | 123.1056 | 0.17183 | 0.01435 | -0.16559 | 123.2185 | 123.103 | 123.3085 | 123.232 | -0.41936 | 123.2326 | 123.3084 | 123.1285 | 123.0891 | -0.36025
745.2969 | 123.3719 | -120.2591 | 2.9663 | 0.072375 | 0.069423 | 0.0095741 | -0.016061 | -0.045728 | 0.1227 | 0.058893 | 0.14557 | 0.0051213 | -0.022 | 0.07356 | 0.081222 | 2.8534 | 2.9226 | 2.8622 | 2.9274 | 2.7981 | 3.0036 | 2.5607 | 2.8856 | 2.7888 | 2.8008 | 2.9323 | 3.0081 | 2.8236 | 2.6381 | 122.8198 | -0.038954 | 123.1125 | 123.1213 | 0.30151 | -0.16823 | 0.037284 | 122.8972 | -0.033977 | 123.1447 | 123.0599 | 0.16268 | 0.041804 | -0.14272 | 123.1864 | 123.0572 | 123.2627 | 123.1816 | -0.40564 | 123.1914 | 123.2672 | 123.0827 | 123.0479 | -0.32822
746.2812 | 123.2254 | -120.3049 | 2.9984 | 0.072375 | 0.070491 | 0.0095741 | -0.013924 | -0.043591 | 0.1227 | 0.058893 | 0.14236 | 0.0051213 | -0.024136 | 0.074628 | 0.080154 | 2.8168 | 2.8722 | 2.8255 | 2.877 | 2.7477 | 2.9578 | 2.5149 | 2.8307 | 2.7522 | 2.7641 | 2.882 | 2.9669 | 2.7778 | 2.5923 | 122.8197 | -0.12136 | 123.1216 | 123.1304 | 0.31067 | -0.25064 | -0.040545 | 122.8972 | -0.11638 | 123.1356 | 123.069 | 0.17183 | -0.031447 | -0.22055 | 123.1819 | 123.0526 | 123.2627 | 123.1771 | -0.48348 | 123.1868 | 123.2718 | 123.0827 | 123.057 | -0.40605
747.2812 | 123.2895 | -120.4193 | 2.8931 | 0.057113 | 0.070491 | 0.0085051 | -0.012856 | -0.045728 | 0.12163 | 0.089415 | 0.14557 | 0.0051213 | -0.020931 | 0.07356 | 0.08229 | 2.7572 | 2.8264 | 2.7614 | 2.8221 | 2.6836 | 2.8983 | 2.4599 | 2.7849 | 2.6835 | 2.7092 | 2.8133 | 2.9028 | 2.7137 | 2.5328 | 122.8792 | -0.071014 | 123.1765 | 123.1808 | 0.30152 | -0.20946 | 0.005219 | 122.9521 | -0.079775 | 123.2042 | 123.1285 | 0.17641 | 0.009739 | -0.17936 | 123.2414 | 123.1029 | 123.3176 | 123.2457 | -0.43314 | 123.2326 | 123.3221 | 123.133 | 123.1028 | -0.36029
748.2812 | 123.3032 | -120.4285 | 2.8885 | 0.057113 | 0.068355 | 0.0095741 | -0.016061 | -0.045728 | 0.12056 | 0.058893 | 0.14343 | 0.0051213 | -0.024136 | 0.074628 | 0.079085 | 2.7069 | 2.7669 | 2.7065 | 2.7717 | 2.6516 | 2.8433 | 2.405 | 2.7254 | 2.6469 | 2.6542 | 2.7767 | 2.8524 | 2.6588 | 2.4916 | 122.8334 | -0.1168 | 123.1353 | 123.135 | 0.30153 | -0.23693 | -0.045148 | 122.92 | -0.11183 | 123.1538 | 123.0827 | 0.16268 | -0.036049 | -0.22973 | 123.2002 | 123.08 | 123.2718 | 123.1953 | -0.48351 | 123.2051 | 123.2809 | 123.0872 | 123.0753 | -0.39692
749.2812 | 123.3307 | -120.4926 | 2.7832 | 0.057113 | 0.069423 | 0.0085051 | -0.014993 | -0.045728 | 0.12163 | 0.043632 | 0.1445 | 0.0061893 | -0.025204 | 0.075696 | 0.08229 | 2.6519 | 2.7211 | 2.6561 | 2.7213 | 2.5783 | 2.7884 | 2.3684 | 2.675 | 2.5965 | 2.6085 | 2.7171 | 2.8021 | 2.6038 | 2.4366 | 122.8609 | -0.061875 | 123.1445 | 123.1487 | 0.2878 | -0.20491 | 0.005195 | 122.9292 | -0.06606 | 123.1676 | 123.101 | 0.17184 | 0.018872 | -0.17938 | 123.2139 | 123.0708 | 123.281 | 123.2137 | -0.41485 | 123.2097 | 123.2946 | 123.0964 | 123.089 | -0.34658
750.2812 | 123.3215 | -120.5475 | 2.7512 | 0.057113 | 0.067286 | 0.0095741 | -0.016061 | -0.045728 | 0.12163 | 0.074154 | 0.1445 | 0.0040533 | -0.023068 | 0.074628 | 0.08229 | 2.6061 | 2.6707 | 2.6058 | 2.6755 | 2.5188 | 2.7518 | 2.3226 | 2.6338 | 2.5644 | 2.5856 | 2.6851 | 2.7517 | 2.558 | 2.4275 | 122.87 | -0.075616 | 123.1536 | 123.1533 | 0.28323 | -0.23239 | 0.000609 | 122.9749 | -0.066067 | 123.1813 | 123.133 | 0.1581 | 0.000551 | -0.19313 | 123.223 | 123.0663 | 123.2993 | 123.2182 | -0.4286 | 123.2326 | 123.2992 | 123.1055 | 123.1119 | -0.3237
751.2812 | 123.3078 | -120.5933 | 2.7237 | 0.041851 | 0.069423 | 0.0085051 | -0.016061 | -0.042523 | 0.12163 | 0.058893 | 0.1445 | 0.0051213 | -0.024136 | 0.072491 | 0.08229 | 2.5787 | 2.6387 | 2.5737 | 2.6435 | 2.5096 | 2.7151 | 2.3088 | 2.6018 | 2.5324 | 2.5352 | 2.6439 | 2.7288 | 2.5214 | 2.3771 | 122.9021 | -0.080199 | 123.1719 | 123.167 | 0.26492 | -0.21408 | -0.008553 | 122.9704 | -0.079807 | 123.195 | 123.1285 | 0.1581 | 0.005124 | -0.20229 | 123.2368 | 123.1029 | 123.3084 | 123.2319 | -0.41487 | 123.2371 | 123.3221 | 123.1147 | 123.1256 | -0.3466
752.2812 | 123.3398 | -120.6207 | 2.6413 | 0.026589 | 0.069423 | 0.0085051 | -0.014993 | -0.046796 | 0.12056 | 0.074154 | 0.14343 | 0.0051213 | -0.025204 | 0.07356 | 0.081222 | 2.5375 | 2.5975 | 2.5417 | 2.5931 | 2.473 | 2.6831 | 2.2264 | 2.5605 | 2.4866 | 2.5031 | 2.5981 | 2.683 | 2.4756 | 2.3588 | 122.8471 | -0.048163 | 123.1582 | 123.1624 | 0.31529 | -0.16832 | 0.041794 | 122.9795 | -0.043194 | 123.1813 | 123.1239 | 0.14437 | 0.041736 | -0.16568 | 123.2139 | 123.0937 | 123.3038 | 123.2182 | -0.41489 | 123.2188 | 123.3038 | 123.0963 | 123.1073 | -0.28252
753.2812 | 123.4131 | -120.6482 | 2.6047 | 0.072375 | 0.068355 | 0.0085051 | -0.014993 | -0.046796 | 0.12163 | 0.058893 | 0.1445 | 0.0040533 | -0.024136 | 0.07356 | 0.081222 | 2.478 | 2.5425 | 2.4776 | 2.5428 | 2.4363 | 2.6281 | 2.1989 | 2.5056 | 2.4454 | 2.4528 | 2.5477 | 2.6235 | 2.3978 | 2.3313 | 122.8471 | -0.061904 | 123.1261 | 123.1258 | 0.27867 | -0.16833 | 0.023472 | 122.9795 | -0.056937 | 123.1538 | 123.101 | 0.12148 | 0.018835 | -0.20689 | 123.191 | 123.0845 | 123.2763 | 123.1907 | -0.40574 | 123.1959 | 123.2717 | 123.046 | 123.0936 | -0.27337
754.2812 | 123.3856 | -120.694 | 2.5681 | 0.057113 | 0.069423 | 0.0095741 | -0.014993 | -0.045728 | 0.12163 | 0.058893 | 0.1445 | 0.0051213 | -0.023068 | 0.074628 | 0.08229 | 2.4322 | 2.4922 | 2.4455 | 2.5016 | 2.3768 | 2.5778 | 2.144 | 2.4552 | 2.395 | 2.4162 | 2.5111 | 2.596 | 2.3291 | 2.2855 | 122.838 | -0.066489 | 123.1261 | 123.1395 | 0.30157 | -0.19123 | 0.009729 | 122.9795 | -0.056944 | 123.1492 | 123.1101 | 0.13063 | 0.027984 | -0.23895 | 123.1955 | 123.0708 | 123.2718 | 123.1861 | -0.42407 | 123.2051 | 123.29 | 123.0231 | 123.089 | -0.28254
755.2969 | 123.3994 | -120.6985 | 2.5131 | 0.026589 | 0.068355 | 0.010642 | -0.013924 | -0.046796 | 0.12163 | 0.058893 | 0.14557 | 0.0061893 | -0.022 | 0.075696 | 0.081222 | 2.4047 | 2.4693 | 2.4089 | 2.4741 | 2.3448 | 2.5503 | 2.1028 | 2.4278 | 2.3492 | 2.3612 | 2.4745 | 2.5686 | 2.2879 | 2.2489 | 122.8013 | -0.039028 | 123.1032 | 123.1075 | 0.30615 | -0.16836 | 0.037188 | 122.9474 | -0.03864 | 123.1263 | 123.0598 | 0.11232 | 0.055444 | -0.22523 | 123.1726 | 123.0433 | 123.2489 | 123.1678 | -0.41035 | 123.173 | 123.2671 | 122.9864 | 123.0478 | -0.26424
756.2812 | 123.3627 | -120.7672 | 2.4994 | 0.041851 | 0.068355 | 0.0085051 | -0.013924 | -0.045728 | 0.12163 | 0.074154 | 0.1445 | 0.0051213 | -0.022 | 0.07356 | 0.081222 | 2.3635 | 2.4281 | 2.3677 | 2.4237 | 2.3173 | 2.4999 | 2.0661 | 2.3911 | 2.3126 | 2.3154 | 2.4287 | 2.5136 | 2.2375 | 2.1848 | 122.8334 | -0.075657 | 123.1307 | 123.1349 | 0.30158 | -0.18209 | 0.000556 | 122.952 | -0.070692 | 123.1583 | 123.0826 | 0.13064 | 0.014233 | -0.26186 | 123.1909 | 123.0845 | 123.2672 | 123.1953 | -0.43325 | 123.1959 | 123.2808 | 123.0047 | 123.0798 | -0.31461
757.2812 | 123.349 | -120.813 | 2.504 | 0.057113 | 0.068355 | 0.0085051 | -0.013924 | -0.046796 | 0.12163 | 0.058893 | 0.14129 | 0.0040533 | -0.022 | 0.076765 | 0.081222 | 2.3314 | 2.4006 | 2.3402 | 2.4008 | 2.2807 | 2.4816 | 2.0204 | 2.3591 | 2.2806 | 2.2834 | 2.4058 | 2.4907 | 2.2009 | 2.139 | 122.8333 | -0.10313 | 123.1444 | 123.1532 | 0.3199 | -0.2233 | -0.022335 | 122.952 | -0.098162 | 123.1721 | 123.0964 | 0.14437 | -0.013237 | -0.30307 | 123.2138 | 123.0937 | 123.2946 | 123.2136 | -0.48361 | 123.2188 | 123.3037 | 123.0139 | 123.0935 | -0.36497
758.2812 | 123.4222 | -120.8176 | 2.3895 | 0.057113 | 0.068355 | 0.0085051 | -0.017129 | -0.04466 | 0.12056 | 0.043632 | 0.14343 | 0.0051213 | -0.022 | 0.074628 | 0.080154 | 2.2857 | 2.3457 | 2.2853 | 2.3459 | 2.2211 | 2.4313 | 1.9791 | 2.3133 | 2.2348 | 2.2467 | 2.3554 | 2.4404 | 2.2101 | 2.0978 | 122.7967 | -0.043626 | 123.1032 | 123.1029 | 0.30617 | -0.16839 | 0.041741 | 122.9154 | -0.034084 | 123.1309 | 123.0643 | 0.14895 | 0.05084 | -0.17947 | 123.1635 | 123.0387 | 123.2488 | 123.1632 | -0.41038 | 123.173 | 123.2579 | 123.0276 | 123.0523 | -0.29174
759.2812 | 123.4268 | -120.9 | 2.3529 | 0.072375 | 0.068355 | 0.0074371 | -0.016061 | -0.04466 | 0.12377 | 0.074154 | 0.14236 | 0.0029843 | -0.023068 | 0.074628 | 0.081222 | 2.2445 | 2.3136 | 2.2487 | 2.3139 | 2.1799 | 2.3992 | 1.9562 | 2.2721 | 2.2027 | 2.2101 | 2.3142 | 2.4037 | 2.1917 | 2.0612 | 122.8562 | -0.039054 | 123.1444 | 123.1486 | 0.29244 | -0.17298 | 0.046312 | 122.9611 | -0.03867 | 123.1721 | 123.1101 | 0.14895 | 0.050832 | -0.16116 | 123.2138 | 123.0799 | 123.2992 | 123.2136 | -0.39666 | 123.2142 | 123.3037 | 123.0917 | 123.1027 | -0.29175
760.2812 | 123.4451 | -120.8862 | 2.3529 | 0.057113 | 0.067286 | 0.0085051 | -0.016061 | -0.045728 | 0.1227 | 0.074154 | 0.1445 | 0.0051213 | -0.022 | 0.075696 | 0.081222 | 2.2216 | 2.2816 | 2.2166 | 2.2726 | 2.1616 | 2.358 | 1.9288 | 2.2309 | 2.1661 | 2.1781 | 2.2868 | 2.3671 | 2.1689 | 2.0245 | 122.815 | -0.080259 | 123.1078 | 123.1029 | 0.28786 | -0.19129 | 0.005105 | 122.9108 | -0.066141 | 123.1171 | 123.0643 | 0.15353 | 0.014203 | -0.18405 | 123.1589 | 123.0478 | 123.2442 | 123.1678 | -0.42413 | 123.173 | 123.2533 | 123.0551 | 123.0523 | -0.32838
761.2812 | 123.4589 | -120.9045 | 2.298 | 0.041851 | 0.067286 | 0.0085051 | -0.017129 | -0.04466 | 0.1227 | 0.074154 | 0.14343 | 0.0061893 | -0.023068 | 0.075696 | 0.081222 | 2.1849 | 2.2587 | 2.1937 | 2.2543 | 2.125 | 2.326 | 1.883 | 2.2126 | 2.1432 | 2.1506 | 2.2593 | 2.3351 | 2.146 | 2.0016 | 122.7875 | -0.043642 | 123.0895 | 123.0983 | 0.31076 | -0.17299 | 0.027985 | 122.9062 | -0.038681 | 123.1171 | 123.0551 | 0.14895 | 0.037084 | -0.15202 | 123.1589 | 123.0295 | 123.2305 | 123.1632 | -0.41499 | 123.1638 | 123.2396 | 123.0505 | 123.0477 | -0.29634
762.2812 | 123.3536 | -120.9732 | 2.2842 | 0.057113 | 0.068355 | 0.0095741 | -0.017129 | -0.04466 | 0.12056 | 0.043632 | 0.14557 | 0.0051213 | -0.023068 | 0.075696 | 0.081222 | 2.1529 | 2.222 | 2.148 | 2.2131 | 2.0883 | 2.2939 | 1.8601 | 2.1759 | 2.102 | 2.1094 | 2.2135 | 2.2984 | 2.1139 | 1.9879 | 122.8333 | -0.071114 | 123.1261 | 123.1212 | 0.28787 | -0.19589 | 0.009668 | 122.9611 | -0.070733 | 123.1491 | 123.0826 | 0.12148 | 0.014188 | -0.17033 | 123.1863 | 123.0616 | 123.2671 | 123.1952 | -0.42415 | 123.1867 | 123.2716 | 123.0871 | 123.0752 | -0.29635
763.2812 | 123.4634 | -121.0007 | 2.2247 | 0.057113 | 0.067286 | 0.010642 | -0.013924 | -0.04466 | 0.12163 | 0.058893 | 0.14236 | 0.0061893 | -0.023068 | 0.075696 | 0.080154 | 2.1025 | 2.1717 | 2.1113 | 2.1628 | 2.0517 | 2.2573 | 1.8326 | 2.1347 | 2.0699 | 2.0682 | 2.1769 | 2.2618 | 2.0727 | 1.9421 | 122.8333 | -0.061967 | 123.1032 | 123.112 | 0.27872 | -0.17301 | 0.032549 | 122.9428 | -0.047851 | 123.1354 | 123.0688 | 0.12606 | 0.037069 | -0.15203 | 123.1634 | 123.0524 | 123.258 | 123.1723 | -0.39211 | 123.1776 | 123.2625 | 123.0734 | 123.0706 | -0.28262
764.2812 | 123.4726 | -121.0602 | 2.1973 | 0.072375 | 0.067286 | 0.0095741 | -0.018198 | -0.046796 | 0.12163 | 0.058893 | 0.14343 | 0.0051213 | -0.022 | 0.076765 | 0.081222 | 2.0705 | 2.135 | 2.0793 | 2.1353 | 2.0334 | 2.2161 | 1.7731 | 2.1073 | 2.0196 | 2.0407 | 2.1448 | 2.2252 | 2.0361 | 1.9055 | 122.8333 | -0.061972 | 123.1307 | 123.1395 | 0.3062 | -0.16386 | 0.018807 | 122.9657 | -0.052435 | 123.1674 | 123.1009 | 0.13522 | 0.027906 | -0.16119 | 123.1955 | 123.0936 | 123.2763 | 123.1952 | -0.42417 | 123.205 | 123.2854 | 123.0963 | 123.0798 | -0.29179
765.2812 | 123.436 | -121.0602 | 2.1606 | 0.026589 | 0.068355 | 0.0085051 | -0.017129 | -0.046796 | 0.12056 | 0.043632 | 0.14343 | 0.0061893 | -0.023068 | 0.076765 | 0.081222 | 2.0476 | 2.1076 | 2.0518 | 2.1124 | 1.9876 | 2.1886 | 1.7548 | 2.0706 | 1.9967 | 2.0041 | 2.1128 | 2.2023 | 2.0132 | 1.8872 | 122.815 | -0.048243 | 123.1078 | 123.112 | 0.29704 | -0.17303 | 0.027956 | 122.9473 | -0.047864 | 123.1308 | 123.0642 | 0.11691 | 0.041634 | -0.14747 | 123.1726 | 123.0478 | 123.2488 | 123.1677 | -0.40587 | 123.173 | 123.2625 | 123.0734 | 123.0569 | -0.27348
766.2812 | 123.436 | -121.1014 | 2.1194 | 0.072375 | 0.067286 | 0.010642 | -0.017129 | -0.046796 | 0.12163 | 0.043632 | 0.14129 | 0.0040533 | -0.022 | 0.075696 | 0.080154 | 2.0018 | 2.0664 | 2.0106 | 2.062 | 1.951 | 2.1566 | 1.7044 | 2.034 | 1.9692 | 1.972 | 2.0807 | 2.1565 | 1.9766 | 1.8688 | 122.8058 | -0.057406 | 123.1032 | 123.112 | 0.3062 | -0.16846 | 0.037105 | 122.9702 | -0.038714 | 123.1354 | 123.0734 | 0.10317 | 0.037046 | -0.1429 | 123.1634 | 123.0524 | 123.2579 | 123.1677 | -0.41504 | 123.1821 | 123.2579 | 123.0779 | 123.0706 | -0.2506
767.2812 | 123.4085 | -121.1563 | 2.092 | 0.057113 | 0.067286 | 0.010642 | -0.017129 | -0.045728 | 0.1227 | 0.058893 | 0.14343 | 0.0051213 | -0.024136 | 0.074628 | 0.080154 | 1.9789 | 2.048 | 1.9831 | 2.0437 | 1.9052 | 2.1199 | 1.6998 | 2.0111 | 1.9372 | 1.9491 | 2.0487 | 2.1382 | 1.9445 | 1.8231 | 122.8561 | -0.048254 | 123.1352 | 123.1395 | 0.28331 | -0.18679 | 0.027942 | 122.9794 | -0.043298 | 123.1674 | 123.1054 | 0.12607 | 0.046198 | -0.14748 | 123.2 | 123.0615 | 123.2762 | 123.2044 | -0.39215 | 123.205 | 123.2945 | 123.1008 | 123.0935 | -0.26892
768.2812 | 123.4085 | -121.1563 | 2.0645 | 0.041851 | 0.067286 | 0.0085051 | -0.016061 | -0.045728 | 0.1227 | 0.058893 | 0.1445 | 0.0061893 | -0.020931 | 0.076765 | 0.083358 | 1.9514 | 2.0114 | 1.9603 | 2.0208 | 1.9098 | 2.1016 | 1.6586 | 1.979 | 1.9143 | 1.9217 | 2.0212 | 2.097 | 1.9216 | 1.7956 | 122.8149 | -0.04368 | 123.1078 | 123.1166 | 0.30163 | -0.15474 | 0.037094 | 122.9519 | -0.043303 | 123.1354 | 123.078 | 0.12607 | 0.032457 | -0.14291 | 123.1771 | 123.0661 | 123.2579 | 123.1677 | -0.4059 | 123.1775 | 123.2533 | 123.0779 | 123.0706 | -0.26893
769.2812 | 123.4085 | -121.2433 | 1.9775 | 0.041851 | 0.067286 | 0.0074371 | -0.016061 | -0.04466 | 0.1227 | 0.043632 | 0.14236 | 0.0040533 | -0.020931 | 0.07356 | 0.080154 | 1.9194 | 1.9885 | 1.9236 | 1.9796 | 1.864 | 2.0696 | 1.6311 | 1.9516 | 1.8776 | 1.885 | 1.9892 | 2.0787 | 1.885 | 1.7727 | 122.8744 | 0.00209 | 123.1627 | 123.1669 | 0.29248 | -0.11356 | 0.092019 | 123.016 | 0.011623 | 123.1949 | 123.1283 | 0.11233 | 0.10112 | -0.092561 | 123.2229 | 123.1073 | 123.3128 | 123.2318 | -0.34639 | 123.2324 | 123.3219 | 123.1283 | 123.1209 | -0.20485
770.2812 | 123.4177 | -121.2112 | 2.0187 | 0.041851 | 0.068355 | 0.0085051 | -0.016061 | -0.045728 | 0.12163 | 0.058893 | 0.14343 | 0.0061893 | -0.024136 | 0.076765 | 0.08229 | 1.8965 | 1.9565 | 1.9007 | 1.9613 | 1.8411 | 2.0467 | 1.6037 | 1.9241 | 1.8593 | 1.8667 | 1.9617 | 2.0512 | 1.8667 | 1.7452 | 122.8149 | -0.057423 | 123.1077 | 123.112 | 0.29706 | -0.17765 | 0.027927 | 122.9565 | -0.057047 | 123.1353 | 123.078 | 0.12149 | 0.032447 | -0.15207 | 123.1726 | 123.0523 | 123.2579 | 123.1677 | -0.41507 | 123.1729 | 123.2624 | 123.0779 | 123.0706 | -0.27352
771.2812 | 123.4222 | -121.2616 | 2.0004 | 0.057113 | 0.067286 | 0.0095741 | -0.014993 | -0.046796 | 0.12163 | 0.058893 | 0.14343 | 0.0051213 | -0.023068 | 0.075696 | 0.081222 | 1.869 | 1.9336 | 1.8824 | 1.943 | 1.8136 | 2.0192 | 1.5762 | 1.9012 | 1.8273 | 1.8347 | 1.9388 | 2.0283 | 1.8438 | 1.7177 | 122.8378 | -0.057425 | 123.1306 | 123.144 | 0.30622 | -0.18681 | 0.018766 | 122.9793 | -0.061628 | 123.1628 | 123.0963 | 0.11691 | 0.027865 | -0.15666 | 123.2046 | 123.0752 | 123.2808 | 123.1952 | -0.42423 | 123.2004 | 123.2899 | 123.1054 | 123.0889 | -0.28268
772.2812 | 123.3948 | -121.3028 | 1.9592 | 0.041851 | 0.067286 | 0.0085051 | -0.017129 | -0.046796 | 0.12163 | 0.058893 | 0.1445 | 0.0051213 | -0.024136 | 0.076765 | 0.081222 | 1.8553 | 1.9107 | 1.8504 | 1.9064 | 1.7907 | 1.9917 | 1.5716 | 1.8692 | 1.7998 | 1.8163 | 1.9159 | 2.0008 | 1.8117 | 1.6857 | 122.8744 | -0.052854 | 123.1581 | 123.1532 | 0.27875 | -0.16851 | 0.032492 | 122.9885 | -0.043323 | 123.172 | 123.1191 | 0.13065 | 0.041591 | -0.14751 | 123.2092 | 123.0935 | 123.2945 | 123.2135 | -0.38761 | 123.2187 | 123.3036 | 123.1145 | 123.1026 | -0.27354
773.2812 | 123.4085 | -121.312 | 1.9226 | 0.057113 | 0.068355 | 0.0074371 | -0.018198 | -0.047865 | 0.12056 | 0.074154 | 0.14236 | 0.0072583 | -0.023068 | 0.075696 | 0.080154 | 1.8232 | 1.8786 | 1.8229 | 1.8789 | 1.7724 | 1.9643 | 1.5304 | 1.8508 | 1.7723 | 1.7797 | 1.8884 | 1.9779 | 1.7934 | 1.6628 | 122.8424 | -0.043703 | 123.1352 | 123.1349 | 0.29249 | -0.1502 | 0.041643 | 122.9748 | -0.034172 | 123.1628 | 123.0917 | 0.11691 | 0.05532 | -0.1292 | 123.1909 | 123.0844 | 123.2762 | 123.1906 | -0.3922 | 123.2004 | 123.2899 | 123.1054 | 123.0843 | -0.25981
774.2812 | 123.4085 | -121.3348 | 1.9089 | 0.057113 | 0.067286 | 0.0085051 | -0.017129 | -0.04466 | 0.12056 | 0.074154 | 0.1445 | 0.0051213 | -0.023068 | 0.077833 | 0.079085 | 1.7912 | 1.8512 | 1.7954 | 1.8514 | 1.7495 | 1.9368 | 1.5213 | 1.8142 | 1.7448 | 1.7568 | 1.8655 | 1.9505 | 1.7659 | 1.6307 | 122.8561 | -0.057441 | 123.126 | 123.1303 | 0.27418 | -0.15937 | 0.027903 | 122.9656 | -0.043332 | 123.1491 | 123.0917 | 0.12607 | 0.04158 | -0.14294 | 123.1863 | 123.0843 | 123.2716 | 123.186 | -0.38762 | 123.2004 | 123.2853 | 123.1008 | 123.0797 | -0.27813
775.2812 | 123.4085 | -121.376 | 1.886 | 0.041851 | 0.066218 | 0.0085051 | -0.016061 | -0.04466 | 0.12163 | 0.074154 | 0.14236 | 0.0061893 | -0.022 | 0.076765 | 0.080154 | 1.7591 | 1.8237 | 1.7634 | 1.8194 | 1.7037 | 1.9093 | 1.4892 | 1.7867 | 1.7174 | 1.7293 | 1.8335 | 1.9138 | 1.7247 | 1.5987 | 122.8652 | -0.066601 | 123.1352 | 123.1394 | 0.27419 | -0.18227 | 0.023321 | 122.9747 | -0.052493 | 123.1628 | 123.1054 | 0.13065 | 0.027841 | -0.16126 | 123.1954 | 123.0798 | 123.2853 | 123.1997 | -0.39679 | 123.2095 | 123.2899 | 123.1008 | 123.0934 | -0.28729
776.2812 | 123.4039 | -121.4264 | 1.8356 | 0.072375 | 0.066218 | 0.0095741 | -0.017129 | -0.045728 | 0.12163 | 0.058893 | 0.14236 | 0.0051213 | -0.023068 | 0.075696 | 0.081222 | 1.7363 | 1.8008 | 1.7359 | 1.8011 | 1.69 | 1.8864 | 1.4434 | 1.7547 | 1.6945 | 1.7019 | 1.806 | 1.8909 | 1.7018 | 1.5666 | 122.8698 | -0.03456 | 123.1626 | 123.1623 | 0.29251 | -0.14565 | 0.050782 | 122.993 | -0.02961 | 123.1811 | 123.1283 | 0.13523 | 0.055302 | -0.1338 | 123.2275 | 123.1164 | 123.3128 | 123.2272 | -0.39222 | 123.2324 | 123.3173 | 123.1282 | 123.1209 | -0.26899
777.2812 | 123.349 | -121.4859 | 1.7807 | 0.041851 | 0.067286 | 0.0095741 | -0.018198 | -0.045728 | 0.12056 | 0.058893 | 0.14343 | 0.0051213 | -0.023068 | 0.076765 | 0.081222 | 1.7225 | 1.7733 | 1.7176 | 1.7736 | 1.6717 | 1.8635 | 1.4343 | 1.7455 | 1.6716 | 1.6744 | 1.7877 | 1.8818 | 1.6973 | 1.5483 | 122.9202 | -0.007099 | 123.2084 | 123.2035 | 0.28335 | -0.10903 | 0.08282 | 123.0342 | 0.007007 | 123.2314 | 123.1603 | 0.12607 | 0.10107 | -0.083446 | 123.2595 | 123.1576 | 123.3494 | 123.2592 | -0.34645 | 123.2736 | 123.3677 | 123.1832 | 123.1575 | -0.23237
778.2812 | 123.3994 | -121.4493 | 1.8173 | 0.057113 | 0.067286 | 0.0085051 | -0.016061 | -0.04466 | 0.12163 | 0.074154 | 0.14343 | 0.0051213 | -0.024136 | 0.075696 | 0.080154 | 1.6951 | 1.7596 | 1.6947 | 1.7644 | 1.6396 | 1.8544 | 1.4114 | 1.7181 | 1.6441 | 1.6561 | 1.7694 | 1.8543 | 1.6606 | 1.5209 | 122.8606 | -0.052877 | 123.1443 | 123.144 | 0.28336 | -0.17771 | 0.037041 | 122.9701 | -0.047928 | 123.1673 | 123.1054 | 0.13523 | 0.036983 | -0.1567 | 123.2137 | 123.0889 | 123.3036 | 123.2089 | -0.40597 | 123.2187 | 123.3036 | 123.1099 | 123.0934 | -0.29647
779.2812 | 123.4085 | -121.4584 | 1.767 | 0.087637 | 0.067286 | 0.0085051 | -0.018198 | -0.045728 | 0.12163 | 0.028371 | 0.14343 | 0.0051213 | -0.023068 | 0.076765 | 0.080154 | 1.6676 | 1.7275 | 1.6672 | 1.7232 | 1.6167 | 1.8086 | 1.3885 | 1.6814 | 1.6304 | 1.6332 | 1.7419 | 1.8223 | 1.6377 | 1.5071 | 122.8469 | -0.043729 | 123.126 | 123.1257 | 0.27878 | -0.15025 | 0.041609 | 122.9656 | -0.025045 | 123.1399 | 123.0916 | 0.12607 | 0.055286 | -0.12923 | 123.1817 | 123.0752 | 123.267 | 123.186 | -0.37851 | 123.2004 | 123.2807 | 123.0962 | 123.0888 | -0.25985
780.2812 | 123.4314 | -121.4722 | 1.7715 | 0.041851 | 0.066218 | 0.0085051 | -0.017129 | -0.046796 | 0.12163 | 0.058893 | 0.14236 | 0.0061893 | -0.023068 | 0.077833 | 0.081222 | 1.6447 | 1.7001 | 1.6398 | 1.7049 | 1.5892 | 1.7903 | 1.3473 | 1.6631 | 1.6029 | 1.6057 | 1.719 | 1.8039 | 1.6103 | 1.4659 | 122.8194 | -0.066619 | 123.1169 | 123.1119 | 0.29252 | -0.1823 | 0.018718 | 122.9381 | -0.052514 | 123.1353 | 123.0779 | 0.13981 | 0.032395 | -0.16128 | 123.1771 | 123.0614 | 123.2624 | 123.1722 | -0.42429 | 123.1912 | 123.2761 | 123.0824 | 123.0751 | -0.30563
781.2812 | 123.4314 | -121.5088 | 1.7532 | 0.026589 | 0.066218 | 0.0063681 | -0.017129 | -0.04466 | 0.12163 | 0.043632 | 0.14236 | 0.0040533 | -0.023068 | 0.076765 | 0.08229 | 1.6172 | 1.6863 | 1.6169 | 1.682 | 1.5755 | 1.7765 | 1.3289 | 1.6448 | 1.5754 | 1.5874 | 1.687 | 1.7765 | 1.5919 | 1.4522 | 122.8377 | -0.071201 | 123.126 | 123.1257 | 0.28794 | -0.17773 | 0.023292 | 122.961 | -0.066254 | 123.1536 | 123.0962 | 0.13523 | 0.023233 | -0.16129 | 123.1908 | 123.0843 | 123.2853 | 123.1951 | -0.4243 | 123.1958 | 123.2853 | 123.1007 | 123.0842 | -0.30106
782.2812 | 123.4039 | -121.5408 | 1.7212 | 0.057113 | 0.066218 | 0.0063681 | -0.017129 | -0.045728 | 0.1227 | 0.058893 | 0.14557 | 0.0051213 | -0.024136 | 0.076765 | 0.081222 | 1.5989 | 1.6634 | 1.5986 | 1.6591 | 1.5389 | 1.7445 | 1.3106 | 1.6311 | 1.5709 | 1.5782 | 1.6687 | 1.7536 | 1.5645 | 1.443 | 122.8515 | -0.062049 | 123.1397 | 123.1394 | 0.28795 | -0.18231 | 0.023286 | 122.9838 | -0.052524 | 123.1719 | 123.1191 | 0.13523 | 0.032384 | -0.15671 | 123.2 | 123.0797 | 123.2853 | 123.2043 | -0.41057 | 123.2095 | 123.2944 | 123.1053 | 123.1117 | -0.27817
783.2812 | 123.3994 | -121.5546 | 1.68 | 0.041851 | 0.066218 | 0.0074371 | -0.017129 | -0.045728 | 0.1195 | 0.058893 | 0.1445 | 0.0040533 | -0.027341 | 0.076765 | 0.081222 | 1.5806 | 1.636 | 1.5757 | 1.6408 | 1.5206 | 1.7307 | 1.3015 | 1.6036 | 1.5388 | 1.5462 | 1.6504 | 1.7353 | 1.5462 | 1.4339 | 122.856 | -0.039165 | 123.1352 | 123.1302 | 0.27421 | -0.15943 | 0.050748 | 122.9884 | -0.02964 | 123.1582 | 123.1008 | 0.11234 | 0.055268 | -0.13383 | 123.1954 | 123.0751 | 123.2853 | 123.1905 | -0.37853 | 123.2049 | 123.2898 | 123.1007 | 123.0934 | -0.24613
784.2812 | 123.4406 | -121.5775 | 1.6663 | 0.057113 | 0.067286 | 0.0074371 | -0.018198 | -0.046796 | 0.12163 | 0.058893 | 0.1445 | 0.0051213 | -0.024136 | 0.077833 | 0.080154 | 1.5623 | 1.6177 | 1.5574 | 1.6317 | 1.4977 | 1.7078 | 1.2603 | 1.5807 | 1.5159 | 1.5233 | 1.6229 | 1.7124 | 1.537 | 1.411 | 122.8377 | -0.034588 | 123.1397 | 123.1348 | 0.29711 | -0.16859 | 0.041588 | 122.9884 | -0.043378 | 123.1582 | 123.1008 | 0.11234 | 0.046108 | -0.12926 | 123.2091 | 123.0751 | 123.2853 | 123.1951 | -0.40601 | 123.2003 | 123.2898 | 123.1145 | 123.0934 | -0.2553
785.3125 | 123.4543 | -121.5775 | 1.6251 | 0.041851 | 0.06515 | 0.0074371 | -0.017129 | -0.046796 | 0.1227 | 0.043632 | 0.14343 | 0.0051213 | -0.024136 | 0.077833 | 0.079085 | 1.5302 | 1.6039 | 1.539 | 1.595 | 1.4885 | 1.685 | 1.2511 | 1.5532 | 1.5022 | 1.4913 | 1.6046 | 1.6941 | 1.505 | 1.3972 | 122.8285 | -0.030017 | 123.1077 | 123.1165 | 0.28795 | -0.13655 | 0.059894 | 122.9747 | -0.020493 | 123.1307 | 123.0687 | 0.094025 | 0.068993 | -0.12011 | 123.1725 | 123.066 | 123.2624 | 123.1814 | -0.37397 | 123.182 | 123.2715 | 123.0824 | 123.0796 | -0.22783
786.2812 | 123.4039 | -121.6415 | 1.6388 | 0.057113 | 0.06515 | 0.0085051 | -0.017129 | -0.046796 | 0.12163 | 0.074154 | 0.14236 | 0.0061893 | -0.025204 | 0.077833 | 0.080154 | 1.5165 | 1.581 | 1.5162 | 1.5722 | 1.4656 | 1.6666 | 1.2145 | 1.5395 | 1.4793 | 1.4775 | 1.5908 | 1.6666 | 1.4729 | 1.3743 | 122.856 | -0.066642 | 123.158 | 123.1577 | 0.30169 | -0.17318 | 0.027847 | 123.0159 | -0.047961 | 123.181 | 123.1191 | 0.10318 | 0.027788 | -0.16589 | 123.2137 | 123.1072 | 123.3082 | 123.2226 | -0.42433 | 123.2324 | 123.3081 | 123.1144 | 123.1208 | -0.26446
787.2812 | 123.4451 | -121.6232 | 1.593 | 0.041851 | 0.064081 | 0.0074371 | -0.017129 | -0.046796 | 0.1195 | 0.043632 | 0.1445 | 0.0061893 | -0.025204 | 0.076765 | 0.079085 | 1.4936 | 1.549 | 1.4841 | 1.5538 | 1.4427 | 1.63 | 1.1916 | 1.512 | 1.461 | 1.4546 | 1.5634 | 1.6528 | 1.4592 | 1.3423 | 122.8148 | -0.039179 | 123.1168 | 123.1073 | 0.29254 | -0.1503 | 0.036994 | 122.9655 | -0.029656 | 123.1353 | 123.0779 | 0.11234 | 0.059828 | -0.13385 | 123.1771 | 123.066 | 123.2532 | 123.1722 | -0.40145 | 123.1866 | 123.2761 | 123.0824 | 123.0842 | -0.25074
788.2812 | 123.4543 | -121.6278 | 1.5793 | 0.072375 | 0.06515 | 0.0063681 | -0.016061 | -0.045728 | 0.12056 | 0.028371 | 0.14343 | 0.0051213 | -0.024136 | 0.076765 | 0.080154 | 1.4753 | 1.5307 | 1.4658 | 1.5447 | 1.4198 | 1.6163 | 1.1961 | 1.4983 | 1.4427 | 1.4363 | 1.545 | 1.6254 | 1.4409 | 1.3331 | 122.824 | -0.034603 | 123.1031 | 123.0936 | 0.26965 | -0.15946 | 0.036991 | 122.9609 | -0.034237 | 123.1261 | 123.0641 | 0.10318 | 0.04609 | -0.13843 | 123.1725 | 123.0476 | 123.2441 | 123.1585 | -0.38314 | 123.1729 | 123.2532 | 123.0687 | 123.0705 | -0.24616
789.2812 | 123.4222 | -121.669 | 1.5884 | 0.072375 | 0.066218 | 0.0074371 | -0.018198 | -0.045728 | 0.12056 | 0.043632 | 0.14343 | 0.0051213 | -0.027341 | 0.078902 | 0.080154 | 1.457 | 1.5169 | 1.4566 | 1.5264 | 1.3878 | 1.6071 | 1.187 | 1.4754 | 1.4243 | 1.4272 | 1.5267 | 1.6162 | 1.4317 | 1.324 | 122.856 | -0.062071 | 123.126 | 123.1256 | 0.26965 | -0.20067 | 0.018679 | 122.993 | -0.061706 | 123.1444 | 123.0962 | 0.10318 | 0.027777 | -0.15674 | 123.1954 | 123.0568 | 123.2761 | 123.1859 | -0.40145 | 123.1957 | 123.2852 | 123.1007 | 123.0933 | -0.26447
790.2969 | 123.3444 | -121.7148 | 1.5839 | 0.072375 | 0.063013 | 0.0063681 | -0.018198 | -0.047865 | 0.1195 | 0.074154 | 0.14343 | 0.0051213 | -0.023068 | 0.076765 | 0.081222 | 1.4387 | 1.5032 | 1.4337 | 1.5035 | 1.3924 | 1.5888 | 1.1595 | 1.4571 | 1.406 | 1.3997 | 1.513 | 1.5933 | 1.4088 | 1.2873 | 122.8743 | -0.080385 | 123.1534 | 123.1485 | 0.27423 | -0.19151 | 0.004942 | 123.0021 | -0.070863 | 123.1719 | 123.1145 | 0.11234 | 0.009462 | -0.17506 | 123.2183 | 123.1071 | 123.3036 | 123.218 | -0.42435 | 123.2278 | 123.3081 | 123.1236 | 123.1208 | -0.29653
791.2812 | 123.4177 | -121.7148 | 1.5427 | 0.057113 | 0.066218 | 0.0074371 | -0.016061 | -0.046796 | 0.1227 | 0.043632 | 0.14236 | 0.0051213 | -0.026272 | 0.078902 | 0.080154 | 1.4249 | 1.494 | 1.42 | 1.4897 | 1.3695 | 1.5705 | 1.1366 | 1.4525 | 1.3923 | 1.3814 | 1.5038 | 1.5704 | 1.3996 | 1.2736 | 122.8514 | -0.052923 | 123.1397 | 123.1348 | 0.28339 | -0.17321 | 0.027826 | 122.9884 | -0.038822 | 123.1673 | 123.0961 | 0.10776 | 0.027767 | -0.14302 | 123.2045 | 123.0842 | 123.2853 | 123.2088 | -0.40604 | 123.2186 | 123.2852 | 123.1144 | 123.1071 | -0.26906
792.3125 | 123.3902 | -121.788 | 1.5472 | 0.026589 | 0.06515 | 0.0074371 | -0.017129 | -0.046796 | 0.1195 | 0.058893 | 0.14343 | 0.0029843 | -0.023068 | 0.078902 | 0.081222 | 1.4158 | 1.4757 | 1.4017 | 1.476 | 1.3511 | 1.5659 | 1.132 | 1.4388 | 1.3694 | 1.363 | 1.4901 | 1.5704 | 1.3859 | 1.2599 | 122.9201 | -0.071235 | 123.2038 | 123.1897 | 0.26966 | -0.1961 | 0.01867 | 123.0479 | -0.057135 | 123.2268 | 123.1511 | 0.10319 | 0.02319 | -0.16133 | 123.264 | 123.1392 | 123.3539 | 123.2637 | -0.4152 | 123.2781 | 123.3585 | 123.1739 | 123.1574 | -0.28738
793.2812 | 123.4131 | -121.7377 | 1.506 | 0.072375 | 0.06515 | 0.0085051 | -0.017129 | -0.046796 | 0.12163 | 0.058893 | 0.14236 | 0.0040533 | -0.025204 | 0.081038 | 0.080154 | 1.3975 | 1.4574 | 1.3925 | 1.4577 | 1.3374 | 1.543 | 1.0908 | 1.4159 | 1.3465 | 1.3493 | 1.4581 | 1.5521 | 1.3676 | 1.2324 | 122.8285 | -0.048349 | 123.1351 | 123.1302 | 0.30171 | -0.16864 | 0.036976 | 122.9701 | -0.047985 | 123.1535 | 123.087 | 0.11692 | 0.046075 | -0.13845 | 123.1954 | 123.0751 | 123.2807 | 123.1951 | -0.41521 | 123.1957 | 123.2898 | 123.1053 | 123.0842 | -0.27365
794.3125 | 123.4177 | -121.8018 | 1.4786 | 0.057113 | 0.064081 | 0.0074371 | -0.017129 | -0.045728 | 0.12056 | 0.058893 | 0.14236 | 0.0029843 | -0.025204 | 0.078902 | 0.080154 | 1.37 | 1.4391 | 1.3697 | 1.444 | 1.3191 | 1.5293 | 1.0954 | 1.4021 | 1.319 | 1.3173 | 1.4489 | 1.5338 | 1.3493 | 1.2187 | 122.8972 | -0.034619 | 123.1717 | 123.1714 | 0.27424 | -0.15949 | 0.050706 | 123.0204 | -0.029677 | 123.2039 | 123.119 | 0.098608 | 0.055226 | -0.1293 | 123.2457 | 123.1208 | 123.331 | 123.2408 | -0.38317 | 123.2507 | 123.3356 | 123.151 | 123.1208 | -0.25992
795.2812 | 123.4634 | -121.7697 | 1.4648 | 0.057113 | 0.064081 | 0.0074371 | -0.016061 | -0.04466 | 0.12056 | 0.043632 | 0.14129 | 0.0040533 | -0.024136 | 0.07997 | 0.081222 | 1.3471 | 1.4208 | 1.3513 | 1.4165 | 1.3099 | 1.5064 | 1.0679 | 1.3747 | 1.2961 | 1.2989 | 1.426 | 1.5109 | 1.3218 | 1.1958 | 122.8377 | -0.048357 | 123.1168 | 123.1211 | 0.2834 | -0.15491 | 0.041546 | 122.9655 | -0.038837 | 123.1444 | 123.0687 | 0.10319 | 0.046066 | -0.14303 | 123.1862 | 123.0796 | 123.2761 | 123.1905 | -0.39691 | 123.1957 | 123.2806 | 123.0915 | 123.0658 | -0.26908
796.2969 | 123.3536 | -121.8338 | 1.442 | 0.057113 | 0.066218 | 0.0063681 | -0.016061 | -0.046796 | 0.1195 | 0.074154 | 0.14236 | 0.0051213 | -0.025204 | 0.078902 | 0.079085 | 1.3334 | 1.4025 | 1.333 | 1.3982 | 1.2733 | 1.4881 | 1.0679 | 1.3609 | 1.2778 | 1.2806 | 1.4031 | 1.488 | 1.3127 | 1.1774 | 122.9017 | -0.043782 | 123.1672 | 123.1668 | 0.26509 | -0.16866 | 0.046119 | 123.0112 | -0.038841 | 123.1947 | 123.1144 | 0.10319 | 0.046061 | -0.1293 | 123.232 | 123.1071 | 123.3219 | 123.2363 | -0.37402 | 123.2369 | 123.3218 | 123.1465 | 123.1116 | -0.26451
797.2812 | 123.436 | -121.8063 | 1.4236 | 0.041851 | 0.06515 | 0.0074371 | -0.017129 | -0.045728 | 0.12056 | 0.074154 | 0.1445 | 0.0051213 | -0.025204 | 0.077833 | 0.080154 | 1.3105 | 1.3704 | 1.301 | 1.3799 | 1.2641 | 1.4698 | 1.0405 | 1.3472 | 1.2824 | 1.2715 | 1.394 | 1.4789 | 1.2852 | 1.1683 | 122.8468 | -0.043785 | 123.1168 | 123.1073 | 0.26052 | -0.1595 | 0.046116 | 122.9746 | -0.029687 | 123.1535 | 123.0778 | 0.10319 | 0.055214 | -0.13846 | 123.1862 | 123.0705 | 123.2761 | 123.1767 | -0.38318 | 123.2003 | 123.2852 | 123.0915 | 123.0887 | -0.25536
798.3125 | 123.3673 | -121.8796 | 1.442 | 0.026589 | 0.064081 | 0.0063681 | -0.014993 | -0.046796 | 0.12163 | 0.074154 | 0.1445 | 0.0051213 | -0.026272 | 0.07997 | 0.081222 | 1.3059 | 1.3704 | 1.3056 | 1.3707 | 1.2504 | 1.4606 | 1.0267 | 1.3335 | 1.2687 | 1.2532 | 1.3756 | 1.4651 | 1.2852 | 1.1546 | 122.9063 | -0.071253 | 123.1855 | 123.1851 | 0.27883 | -0.19155 | 0.018648 | 123.0341 | -0.066312 | 123.213 | 123.1327 | 0.098609 | 0.023168 | -0.15678 | 123.2503 | 123.13 | 123.3402 | 123.25 | -0.41523 | 123.2552 | 123.3447 | 123.1648 | 123.1482 | -0.2874
799.2812 | 123.468 | -121.8384 | 1.387 | 0.041851 | 0.063013 | 0.0063681 | -0.016061 | -0.04466 | 0.12163 | 0.043632 | 0.14343 | 0.0061893 | -0.025204 | 0.078902 | 0.079085 | 1.2967 | 1.3521 | 1.2827 | 1.3524 | 1.2275 | 1.4331 | 1.0176 | 1.306 | 1.232 | 1.2303 | 1.3619 | 1.4468 | 1.2577 | 1.1271 | 122.8559 | -0.034634 | 123.1351 | 123.121 | 0.2651 | -0.15951 | 0.046108 | 122.9655 | -0.025116 | 123.1444 | 123.0686 | 0.10319 | 0.059785 | -0.12932 | 123.1908 | 123.0659 | 123.2715 | 123.1905 | -0.36946 | 123.2003 | 123.2852 | 123.0961 | 123.0704 | -0.25995
800.2969 | 123.381 | -121.9254 | 1.4008 | 0.057113 | 0.06515 | 0.0085051 | -0.017129 | -0.046796 | 0.1195 | 0.058893 | 0.14343 | 0.0051213 | -0.025204 | 0.078902 | 0.080154 | 1.2738 | 1.3429 | 1.2781 | 1.3432 | 1.2367 | 1.4331 | 1.0038 | 1.3106 | 1.2137 | 1.2074 | 1.3482 | 1.4422 | 1.2486 | 1.0813 | 122.9292 | -0.057524 | 123.1992 | 123.2034 | 0.27425 | -0.16409 | 0.032375 | 123.0066 | -0.052584 | 123.2359 | 123.1327 | 0.12608 | 0.041473 | -0.1522 | 123.2686 | 123.162 | 123.3585 | 123.2683 | -0.39692 | 123.2735 | 123.3676 | 123.1739 | 123.1391 | -0.31947
801.2812 | 123.4314 | -121.8658 | 1.3733 | 0.057113 | 0.064081 | 0.0074371 | -0.017129 | -0.045728 | 0.12056 | 0.058893 | 0.14343 | 0.0051213 | -0.024136 | 0.077833 | 0.079085 | 1.2738 | 1.3292 | 1.2689 | 1.3341 | 1.2092 | 1.424 | 0.98552 | 1.2922 | 1.2091 | 1.1936 | 1.3436 | 1.4285 | 1.244 | 1.0813 | 122.8514 | -0.039215 | 123.1397 | 123.1348 | 0.28342 | -0.1641 | 0.050684 | 122.9471 | -0.029697 | 123.1581 | 123.0595 | 0.11235 | 0.055204 | -0.12932 | 123.1999 | 123.075 | 123.2898 | 123.195 | -0.38778 | 123.2094 | 123.2943 | 123.1098 | 123.075 | -0.292
802.3125 | 123.3856 | -121.9711 | 1.355 | 0.072375 | 0.063013 | 0.0095741 | -0.016061 | -0.046796 | 0.1227 | 0.074154 | 0.14343 | 0.0040533 | -0.025204 | 0.07997 | 0.081222 | 1.2372 | 1.3017 | 1.2323 | 1.3066 | 1.1863 | 1.3919 | 0.96262 | 1.2693 | 1.1862 | 1.1845 | 1.307 | 1.3873 | 1.2165 | 1.063 | 122.9338 | -0.048374 | 123.2083 | 123.2034 | 0.26968 | -0.16868 | 0.036944 | 123.0341 | -0.048014 | 123.2405 | 123.1556 | 0.1215 | 0.032307 | -0.13848 | 123.2777 | 123.1574 | 123.3631 | 123.2729 | -0.39236 | 123.2781 | 123.3584 | 123.1876 | 123.1574 | -0.29201
803.2812 | 123.4726 | -121.9254 | 1.3321 | 0.057113 | 0.064081 | 0.0063681 | -0.016061 | -0.046796 | 0.12163 | 0.043632 | 0.14343 | 0.0051213 | -0.025204 | 0.078902 | 0.079085 | 1.2189 | 1.288 | 1.2094 | 1.2929 | 1.1726 | 1.3828 | 0.92599 | 1.2465 | 1.1771 | 1.1707 | 1.2932 | 1.3827 | 1.2028 | 1.0584 | 122.8513 | -0.039221 | 123.1443 | 123.1348 | 0.28342 | -0.15953 | 0.050675 | 122.9837 | -0.038861 | 123.1718 | 123.0961 | 0.11235 | 0.050617 | -0.12933 | 123.2182 | 123.0979 | 123.3081 | 123.2133 | -0.4061 | 123.2186 | 123.3081 | 123.1281 | 123.1024 | -0.2737
804.2969 | 123.3719 | -121.9437 | 1.3641 | 0.072375 | 0.061945 | 0.0095741 | -0.016061 | -0.050001 | 0.12163 | 0.058893 | 0.14236 | 0.0061893 | -0.026272 | 0.078902 | 0.079085 | 1.2052 | 1.2788 | 1.2003 | 1.27 | 1.1588 | 1.3599 | 0.94431 | 1.2373 | 1.1542 | 1.157 | 1.2749 | 1.3644 | 1.1845 | 1.0447 | 122.888 | -0.094157 | 123.1488 | 123.1439 | 0.25595 | -0.20531 | -0.004262 | 122.9883 | -0.089219 | 123.181 | 123.1007 | 0.11235 | 0.000258 | -0.17968 | 123.2136 | 123.1025 | 123.3035 | 123.2225 | -0.41983 | 123.2186 | 123.3081 | 123.1281 | 123.0979 | -0.31948
805.2812 | 123.4634 | -121.9345 | 1.3 | 0.087637 | 0.063013 | 0.0074371 | -0.018198 | -0.04466 | 0.1227 | 0.058893 | 0.14236 | 0.0061893 | -0.024136 | 0.07997 | 0.080154 | 1.1868 | 1.2559 | 1.1911 | 1.2608 | 1.1542 | 1.3461 | 0.91225 | 1.2281 | 1.1542 | 1.1341 | 1.2703 | 1.3598 | 1.1799 | 1.0309 | 122.8468 | -0.039227 | 123.1214 | 123.1256 | 0.27885 | -0.1458 | 0.046089 | 122.9654 | -0.029711 | 123.1627 | 123.0686 | 0.10319 | 0.059767 | -0.12018 | 123.1953 | 123.0888 | 123.2806 | 123.1905 | -0.3878 | 123.2048 | 123.2943 | 123.1144 | 123.0887 | -0.26913
806.3125 | 123.3765 | -121.9894 | 1.3321 | 0.041851 | 0.06515 | 0.0085051 | -0.016061 | -0.046796 | 0.12163 | 0.028371 | 0.14343 | 0.0040533 | -0.025204 | 0.07997 | 0.080154 | 1.1731 | 1.2559 | 1.1865 | 1.2562 | 1.1359 | 1.337 | 0.89852 | 1.2144 | 1.145 | 1.125 | 1.2566 | 1.3461 | 1.1616 | 1.0355 | 122.888 | -0.075848 | 123.1626 | 123.176 | 0.28801 | -0.19616 | 0.004889 | 123.0249 | -0.075489 | 123.2038 | 123.1144 | 0.089455 | 0.013988 | -0.17053 | 123.2457 | 123.1254 | 123.3264 | 123.2454 | -0.43358 | 123.246 | 123.3355 | 123.151 | 123.1345 | -0.29659
807.2812 | 123.4268 | -121.9986 | 1.2772 | 0.026589 | 0.063013 | 0.0074371 | -0.018198 | -0.04466 | 0.1195 | 0.074154 | 0.1445 | 0.0040533 | -0.024136 | 0.07997 | 0.079085 | 1.1594 | 1.2331 | 1.1591 | 1.2334 | 1.1176 | 1.3187 | 0.89852 | 1.1824 | 1.1221 | 1.1112 | 1.2429 | 1.3232 | 1.1341 | 1.0218 | 122.8971 | -0.043809 | 123.158 | 123.1576 | 0.26053 | -0.15954 | 0.041506 | 123.0204 | -0.034294 | 123.181 | 123.1098 | 0.089455 | 0.046026 | -0.14307 | 123.2319 | 123.1162 | 123.3173 | 123.2316 | -0.37864 | 123.2415 | 123.3218 | 123.1327 | 123.1207 | -0.2554
808.2969 | 123.3353 | -122.0581 | 1.2955 | 0.057113 | 0.063013 | 0.0085051 | -0.019266 | -0.046796 | 0.1195 | 0.074154 | 0.14343 | 0.0051213 | -0.025204 | 0.082107 | 0.080154 | 1.1456 | 1.2147 | 1.1407 | 1.215 | 1.1085 | 1.3004 | 0.87104 | 1.1778 | 1.1176 | 1.0975 | 1.2246 | 1.3186 | 1.1387 | 1.0126 | 122.9291 | -0.080433 | 123.2037 | 123.1988 | 0.2697 | -0.18701 | 0.004881 | 123.0707 | -0.070918 | 123.2359 | 123.1556 | 0.084877 | 0.023137 | -0.15681 | 123.2731 | 123.1666 | 123.3585 | 123.2728 | -0.42443 | 123.2827 | 123.3767 | 123.1968 | 123.1757 | -0.28286
809.2812 | 123.3444 | -122.0535 | 1.268 | 0.041851 | 0.06515 | 0.0063681 | -0.017129 | -0.047865 | 0.1227 | 0.043632 | 0.14129 | 0.0061893 | -0.027341 | 0.07997 | 0.080154 | 1.1365 | 1.2056 | 1.1362 | 1.2059 | 1.0901 | 1.2912 | 0.85731 | 1.164 | 1.113 | 1.0929 | 1.2154 | 1.2957 | 1.1204 | 1.0034 | 122.9108 | -0.062124 | 123.19 | 123.1897 | 0.27885 | -0.17786 | 0.02319 | 123.057 | -0.052609 | 123.2176 | 123.1464 | 0.089455 | 0.02771 | -0.14765 | 123.2594 | 123.1437 | 123.3447 | 123.2591 | -0.4107 | 123.2689 | 123.3492 | 123.1739 | 123.1665 | -0.26456
810.2969 | 123.381 | -122.0764 | 1.2497 | 0.057113 | 0.063013 | 0.0085051 | -0.016061 | -0.045728 | 0.12056 | 0.10468 | 0.1445 | 0.0040533 | -0.027341 | 0.082107 | 0.080154 | 1.1273 | 1.1918 | 1.1224 | 1.2013 | 1.0856 | 1.282 | 0.85273 | 1.1457 | 1.0992 | 1.0929 | 1.1971 | 1.282 | 1.1112 | 0.99429 | 122.9291 | -0.048392 | 123.2037 | 123.1988 | 0.2697 | -0.16413 | 0.032343 | 123.0707 | -0.052613 | 123.2221 | 123.1693 | 0.098613 | 0.032284 | -0.1385 | 123.2777 | 123.162 | 123.3585 | 123.2683 | -0.39697 | 123.2735 | 123.3584 | 123.1876 | 123.1757 | -0.2554
811.2812 | 123.381 | -122.0901 | 1.2314 | 0.057113 | 0.064081 | 0.0074371 | -0.018198 | -0.045728 | 0.12056 | 0.043632 | 0.14236 | 0.0072583 | -0.026272 | 0.07997 | 0.079085 | 1.109 | 1.1827 | 1.1087 | 1.183 | 1.0535 | 1.2591 | 0.84357 | 1.132 | 1.1038 | 1.0746 | 1.1879 | 1.2637 | 1.0929 | 0.98513 | 122.9337 | -0.048395 | 123.1992 | 123.1988 | 0.26512 | -0.17787 | 0.027761 | 123.0753 | -0.043459 | 123.2221 | 123.1647 | 0.089456 | 0.032281 | -0.13851 | 123.2731 | 123.1437 | 123.3493 | 123.2728 | -0.38781 | 123.2781 | 123.3538 | 123.183 | 123.194 | -0.24625
812.3125 | 123.3856 | -122.0856 | 1.2543 | 0.072375 | 0.061945 | 0.0085051 | -0.016061 | -0.045728 | 0.1227 | 0.058893 | 0.1445 | 0.0051213 | -0.025204 | 0.07997 | 0.079085 | 1.0953 | 1.1735 | 1.095 | 1.1601 | 1.0627 | 1.2637 | 0.8161 | 1.1274 | 1.0764 | 1.0654 | 1.1742 | 1.2591 | 1.0791 | 0.96682 | 122.9017 | -0.094174 | 123.1809 | 123.1805 | 0.27886 | -0.1916 | 0.009452 | 123.0524 | -0.080082 | 123.213 | 123.151 | 0.098614 | 0.004814 | -0.17513 | 123.2457 | 123.1482 | 123.3493 | 123.2591 | -0.43818 | 123.2598 | 123.3447 | 123.1647 | 123.1619 | -0.28745
813.2812 | 123.3353 | -122.1176 | 1.2177 | 0.057113 | 0.060876 | 0.0074371 | -0.017129 | -0.045728 | 0.11843 | 0.043632 | 0.1445 | 0.0061893 | -0.025204 | 0.082107 | 0.079085 | 1.0815 | 1.1598 | 1.0858 | 1.1601 | 1.0444 | 1.2363 | 0.80236 | 1.1045 | 1.0672 | 1.0471 | 1.1605 | 1.2454 | 1.0746 | 0.9485 | 122.92 | -0.057553 | 123.1992 | 123.2034 | 0.28344 | -0.1733 | 0.018601 | 123.0661 | -0.057197 | 123.2221 | 123.1647 | 0.098614 | 0.0277 | -0.14309 | 123.2777 | 123.162 | 123.3539 | 123.2774 | -0.41529 | 123.2781 | 123.363 | 123.1922 | 123.1848 | -0.26915
814.2812 | 123.3582 | -122.113 | 1.2314 | 0.041851 | 0.063013 | 0.0063681 | -0.017129 | -0.045728 | 0.12163 | 0.043632 | 0.14557 | 0.0051213 | -0.027341 | 0.078902 | 0.080154 | 1.0724 | 1.1461 | 1.0766 | 1.1372 | 1.0215 | 1.2271 | 0.8161 | 1.0999 | 1.0626 | 1.0425 | 1.1513 | 1.2408 | 1.0563 | 0.93477 | 122.9291 | -0.094178 | 123.1854 | 123.1897 | 0.26055 | -0.20993 | -0.004289 | 123.0478 | -0.080087 | 123.213 | 123.1556 | 0.10777 | 0.009388 | -0.17513 | 123.2502 | 123.1345 | 123.3401 | 123.2591 | -0.41529 | 123.2643 | 123.3538 | 123.1693 | 123.1757 | -0.29662
815.2812 | 123.3261 | -122.1268 | 1.1993 | 0.072375 | 0.063013 | 0.0074371 | -0.014993 | -0.045728 | 0.1227 | 0.043632 | 0.14343 | 0.0040533 | -0.025204 | 0.07997 | 0.079085 | 1.0587 | 1.1277 | 1.0629 | 1.1326 | 1.0123 | 1.2179 | 0.77946 | 1.0908 | 1.0535 | 1.0334 | 1.1421 | 1.2133 | 1.0471 | 0.92561 | 122.9062 | -0.066714 | 123.1854 | 123.1897 | 0.28344 | -0.18704 | 0.018597 | 123.0524 | -0.057201 | 123.2176 | 123.1602 | 0.10777 | 0.013959 | -0.15225 | 123.2594 | 123.1391 | 123.3447 | 123.2545 | -0.41988 | 123.2689 | 123.3401 | 123.1739 | 123.1802 | -0.27373
816.3125 | 123.3902 | -122.1359 | 1.1856 | 0.072375 | 0.059808 | 0.0074371 | -0.017129 | -0.04466 | 0.12163 | 0.074154 | 0.14343 | 0.0051213 | -0.025204 | 0.078902 | 0.080154 | 1.0449 | 1.1186 | 1.0492 | 1.1143 | 1.0031 | 1.2088 | 0.77031 | 1.0816 | 1.0443 | 1.0196 | 1.1284 | 1.2041 | 1.0288 | 0.91187 | 122.9062 | -0.071294 | 123.1808 | 123.1851 | 0.27887 | -0.18247 | 0.023172 | 123.0478 | -0.057203 | 123.2175 | 123.1556 | 0.10777 | 0.018535 | -0.15683 | 123.2502 | 123.1391 | 123.3447 | 123.2545 | -0.4153 | 123.2643 | 123.3401 | 123.1647 | 123.1802 | -0.27373
817.2812 | 123.3124 | -122.1771 | 1.181 | 0.057113 | 0.061945 | 0.0063681 | -0.016061 | -0.045728 | 0.1227 | 0.028371 | 0.1445 | 0.0051213 | -0.025204 | 0.07997 | 0.079085 | 1.0358 | 1.1049 | 1.04 | 1.1052 | 0.99857 | 1.1905 | 0.76115 | 1.0633 | 1.026 | 1.0105 | 1.1192 | 1.1904 | 1.0196 | 0.90729 | 122.9383 | -0.075873 | 123.2129 | 123.2171 | 0.27887 | -0.18246 | 0.009436 | 123.0844 | -0.061782 | 123.2404 | 123.1876 | 0.10319 | 0.009377 | -0.16141 | 123.2823 | 123.1757 | 123.3676 | 123.282 | -0.41988 | 123.2964 | 123.3675 | 123.1967 | 123.2031 | -0.27374
818.2812 | 123.3536 | -122.1863 | 1.1719 | 0.057113 | 0.064081 | 0.0063681 | -0.017129 | -0.045728 | 0.1195 | 0.058893 | 0.14343 | 0.0061893 | -0.027341 | 0.081038 | 0.079085 | 1.022 | 1.1003 | 1.0263 | 1.0914 | 0.98483 | 1.1813 | 0.74741 | 1.045 | 1.0123 | 1.0013 | 1.0918 | 1.1767 | 1.0059 | 0.89814 | 122.9337 | -0.080453 | 123.2083 | 123.2126 | 0.27887 | -0.18705 | 0.009434 | 123.0844 | -0.080098 | 123.2313 | 123.1876 | 0.10319 | 0.004797 | -0.16599 | 123.2777 | 123.1711 | 123.3676 | 123.2866 | -0.42446 | 123.2781 | 123.363 | 123.1922 | 123.1985 | -0.27374
819.2812 | 123.3765 | -122.1817 | 1.181 | 0.041851 | 0.061945 | 0.0074371 | -0.017129 | -0.046796 | 0.12056 | 0.058893 | 0.14343 | 0.0040533 | -0.026272 | 0.083175 | 0.078017 | 1.0129 | 1.082 | 1.008 | 1.0777 | 0.98025 | 1.1676 | 0.73368 | 1.0404 | 1.0031 | 0.9876 | 1.0918 | 1.1721 | 0.99215 | 0.8844 | 122.9154 | -0.10334 | 123.1946 | 123.1897 | 0.27429 | -0.20078 | -0.013457 | 123.0661 | -0.089253 | 123.2221 | 123.1693 | 0.1032 | -0.008937 | -0.18888 | 123.2594 | 123.162 | 123.3493 | 123.2637 | -0.44735 | 123.2735 | 123.3538 | 123.1739 | 123.1848 | -0.29663
820.2812 | 123.3444 | -122.1863 | 1.1536 | 0.041851 | 0.061945 | 0.0085051 | -0.017129 | -0.046796 | 0.12056 | 0.043632 | 0.14343 | 0.0061893 | -0.027341 | 0.081038 | 0.080154 | 1.0083 | 1.0728 | 1.0034 | 1.0685 | 0.96193 | 1.1584 | 0.74283 | 1.0358 | 0.99852 | 0.97844 | 1.0826 | 1.1629 | 0.98299 | 0.86608 | 122.9291 | -0.085034 | 123.1946 | 123.1897 | 0.26056 | -0.19163 | 0.004852 | 123.0524 | -0.070944 | 123.2221 | 123.1647 | 0.11235 | 0.009372 | -0.17057 | 123.2548 | 123.1482 | 123.3447 | 123.2591 | -0.41073 | 123.2689 | 123.3492 | 123.1693 | 123.1848 | -0.28748
821.2812 | 123.3398 | -122.2183 | 1.1398 | 0.057113 | 0.061945 | 0.0074371 | -0.017129 | -0.045728 | 0.1195 | 0.058893 | 0.14343 | 0.0051213 | -0.026272 | 0.081038 | 0.079085 | 0.99456 | 1.0636 | 0.98966 | 1.064 | 0.95278 | 1.1538 | 0.71994 | 1.0221 | 0.98478 | 0.96928 | 1.0643 | 1.1446 | 0.97384 | 0.86151 | 122.9383 | -0.075881 | 123.2129 | 123.208 | 0.26972 | -0.18706 | 0.014005 | 123.0798 | -0.075526 | 123.2404 | 123.1876 | 0.10777 | 0.004789 | -0.166 | 123.2823 | 123.1711 | 123.3722 | 123.282 | -0.41989 | 123.2826 | 123.3629 | 123.1922 | 123.2031 | -0.27833
822.2812 | 123.3444 | -122.2504 | 1.1124 | 0.026589 | 0.060876 | 0.0063681 | -0.016061 | -0.046796 | 0.12056 | 0.074154 | 0.14236 | 0.0061893 | -0.026272 | 0.07997 | 0.079085 | 0.98082 | 1.0545 | 0.98508 | 1.064 | 0.95278 | 1.1447 | 0.70162 | 1.0175 | 0.97562 | 0.96012 | 1.0643 | 1.1492 | 0.97384 | 0.85235 | 122.952 | -0.048415 | 123.2312 | 123.2354 | 0.28345 | -0.15959 | 0.032314 | 123.1027 | -0.04806 | 123.2679 | 123.2105 | 0.10777 | 0.036834 | -0.13853 | 123.3143 | 123.2031 | 123.395 | 123.3049 | -0.41074 | 123.3147 | 123.3996 | 123.2242 | 123.226 | -0.26002
823.2812 | 123.3719 | -122.2183 | 1.1032 | 0.057113 | 0.059808 | 0.0085051 | -0.016061 | -0.047865 | 0.12056 | 0.058893 | 0.14343 | 0.0051213 | -0.028409 | 0.082107 | 0.079085 | 0.97624 | 1.0407 | 0.96676 | 1.0456 | 0.9253 | 1.1309 | 0.71994 | 0.99463 | 0.97105 | 0.95096 | 1.046 | 1.1355 | 0.9601 | 0.84319 | 122.9383 | -0.057572 | 123.1946 | 123.1851 | 0.24682 | -0.17791 | 0.027734 | 123.0615 | -0.057218 | 123.213 | 123.1693 | 0.10777 | 0.032254 | -0.14311 | 123.264 | 123.1436 | 123.3493 | 123.2591 | -0.38327 | 123.2643 | 123.3538 | 123.1784 | 123.1894 | -0.26002
824.2812 | 123.3353 | -122.2366 | 1.1169 | 0.026589 | 0.060876 | 0.0063681 | -0.016061 | -0.046796 | 0.12056 | 0.043632 | 0.1445 | 0.0061893 | -0.026272 | 0.081038 | 0.079085 | 0.96251 | 1.0316 | 0.96676 | 1.0365 | 0.93446 | 1.1264 | 0.68789 | 0.99463 | 0.95731 | 0.93265 | 1.046 | 1.1172 | 0.95552 | 0.82488 | 122.9245 | -0.080462 | 123.1991 | 123.2034 | 0.27888 | -0.18248 | 0.009423 | 123.0615 | -0.070951 | 123.2313 | 123.1693 | 0.10777 | 0.000207 | -0.16142 | 123.2731 | 123.1711 | 123.363 | 123.2682 | -0.42906 | 123.2826 | 123.3538 | 123.1922 | 123.1939 | -0.29207
825.2812 | 123.3124 | -122.2412 | 1.1169 | 0.072375 | 0.060876 | 0.0074371 | -0.018198 | -0.04466 | 0.12056 | 0.058893 | 0.1445 | 0.0061893 | -0.026272 | 0.081038 | 0.076949 | 0.95335 | 1.0224 | 0.95303 | 1.0273 | 0.91156 | 1.1126 | 0.66499 | 0.98547 | 0.94815 | 0.92349 | 1.0277 | 1.1172 | 0.93721 | 0.81572 | 122.9062 | -0.089619 | 123.1946 | 123.1942 | 0.28804 | -0.20538 | -0.004313 | 123.0569 | -0.089265 | 123.2267 | 123.1647 | 0.10777 | 0.000207 | -0.17974 | 123.2685 | 123.1528 | 123.3538 | 123.2636 | -0.45195 | 123.2689 | 123.3584 | 123.1784 | 123.1894 | -0.30122
826.2812 | 123.3307 | -122.2687 | 1.0895 | 0.057113 | 0.059808 | 0.0063681 | -0.018198 | -0.047865 | 0.1195 | 0.058893 | 0.14343 | 0.0061893 | -0.026272 | 0.081038 | 0.080154 | 0.9442 | 1.0133 | 0.93929 | 1.0182 | 0.89783 | 1.1081 | 0.66957 | 0.97173 | 0.93442 | 0.91434 | 1.0231 | 1.1034 | 0.92347 | 0.80656 | 122.9382 | -0.07131 | 123.2129 | 123.208 | 0.26972 | -0.19165 | 0.018573 | 123.0752 | -0.066378 | 123.2404 | 123.183 | 0.10777 | 0.013936 | -0.16601 | 123.2868 | 123.1665 | 123.3767 | 123.282 | -0.41991 | 123.2918 | 123.3721 | 123.1921 | 123.2031 | -0.28292
827.2812 | 123.3536 | -122.2824 | 1.0895 | 0.041851 | 0.061945 | 0.0053001 | -0.018198 | -0.045728 | 0.12056 | 0.043632 | 0.1445 | 0.0061893 | -0.026272 | 0.081038 | 0.079085 | 0.93504 | 1.0041 | 0.93472 | 1.009 | 0.89325 | 1.0989 | 0.66499 | 0.958 | 0.92068 | 0.9006 | 1.0185 | 1.108 | 0.92347 | 0.80656 | 122.9474 | -0.080467 | 123.2174 | 123.2171 | 0.26972 | -0.19623 | 0.009416 | 123.089 | -0.070957 | 123.2404 | 123.183 | 0.094039 | 0.018515 | -0.16601 | 123.2914 | 123.1757 | 123.3813 | 123.2865 | -0.42449 | 123.3009 | 123.3904 | 123.2059 | 123.2031 | -0.28292
828.2812 | 123.3444 | -122.287 | 1.0574 | 0.057113 | 0.058739 | 0.0063681 | -0.017129 | -0.047865 | 0.1195 | 0.043632 | 0.14343 | 0.0061893 | -0.027341 | 0.081038 | 0.079085 | 0.92588 | 0.99954 | 0.92556 | 0.99528 | 0.87035 | 1.0897 | 0.66041 | 0.958 | 0.9161 | 0.89144 | 1.0048 | 1.0897 | 0.91431 | 0.79282 | 122.9474 | -0.062158 | 123.2129 | 123.2125 | 0.26515 | -0.18708 | 0.032303 | 123.0798 | -0.052648 | 123.245 | 123.1784 | 0.098618 | 0.032244 | -0.14312 | 123.2823 | 123.1573 | 123.3767 | 123.2865 | -0.39702 | 123.2918 | 123.3767 | 123.2013 | 123.2031 | -0.26461
829.2812 | 123.3948 | -122.2641 | 1.0483 | 0.072375 | 0.058739 | 0.0063681 | -0.018198 | -0.045728 | 0.12056 | 0.058893 | 0.14343 | 0.0051213 | -0.027341 | 0.082107 | 0.079085 | 0.90757 | 0.99038 | 0.92098 | 0.9907 | 0.87035 | 1.0806 | 0.63294 | 0.94426 | 0.91152 | 0.89602 | 0.99105 | 1.0851 | 0.90058 | 0.77909 | 122.897 | -0.057582 | 123.1717 | 123.1851 | 0.28804 | -0.17792 | 0.0323 | 123.0432 | -0.057229 | 123.2084 | 123.1601 | 0.11693 | 0.03682 | -0.1477 | 123.2548 | 123.1345 | 123.3447 | 123.2545 | -0.41534 | 123.2551 | 123.3492 | 123.1647 | 123.1756 | -0.26919
830.2812 | 123.349 | -122.3007 | 1.0437 | 0.041851 | 0.061945 | 0.0063681 | -0.017129 | -0.04466 | 0.12056 | 0.089415 | 0.1445 | 0.0061893 | -0.028409 | 0.081038 | 0.079085 | 0.90757 | 0.97207 | 0.90267 | 0.97238 | 0.87035 | 1.0668 | 0.6192 | 0.93968 | 0.89321 | 0.86855 | 0.97732 | 1.0622 | 0.896 | 0.76993 | 122.9199 | -0.071317 | 123.2083 | 123.2034 | 0.28347 | -0.17335 | 0.023143 | 123.0707 | -0.066386 | 123.2404 | 123.1693 | 0.098618 | 0.018505 | -0.1477 | 123.2731 | 123.1711 | 123.3676 | 123.2728 | -0.4245 | 123.278 | 123.3629 | 123.1967 | 123.1939 | -0.27377
831.2812 | 123.381 | -122.3099 | 1.0162 | 0.057113 | 0.061945 | 0.0063681 | -0.017129 | -0.046796 | 0.1195 | 0.058893 | 0.14343 | 0.0061893 | -0.026272 | 0.081038 | 0.078017 | 0.90299 | 0.96291 | 0.89809 | 0.96781 | 0.85662 | 1.0531 | 0.61004 | 0.92595 | 0.88863 | 0.87771 | 0.97274 | 1.0622 | 0.88226 | 0.76077 | 122.9199 | -0.04843 | 123.2129 | 123.208 | 0.28805 | -0.15962 | 0.036873 | 123.0706 | -0.043499 | 123.2358 | 123.1876 | 0.11693 | 0.045971 | -0.13397 | 123.2777 | 123.1665 | 123.363 | 123.2728 | -0.40619 | 123.2826 | 123.3721 | 123.1921 | 123.1985 | -0.25546
832.2812 | 123.3261 | -122.3145 | 1.03 | 0.041851 | 0.058739 | 0.0074371 | -0.017129 | -0.047865 | 0.1195 | 0.058893 | 0.14236 | 0.0040533 | -0.027341 | 0.083175 | 0.079085 | 0.89841 | 0.96291 | 0.89351 | 0.94949 | 0.85204 | 1.0485 | 0.60547 | 0.92137 | 0.87489 | 0.86397 | 0.96358 | 1.0485 | 0.87311 | 0.74704 | 122.9199 | -0.080476 | 123.2129 | 123.208 | 0.28805 | -0.17793 | 0.018561 | 123.0615 | -0.066389 | 123.2358 | 123.1784 | 0.11693 | 0.018503 | -0.15686 | 123.2639 | 123.1665 | 123.363 | 123.2774 | -0.4245 | 123.278 | 123.3629 | 123.1876 | 123.1893 | -0.28293
833.2812 | 123.436 | -122.3053 | 0.95215 | 0.072375 | 0.059808 | 0.0063681 | -0.018198 | -0.047865 | 0.1195 | 0.043632 | 0.14343 | 0.0040533 | -0.028409 | 0.082107 | 0.081222 | 0.8801 | 0.94002 | 0.87978 | 0.94949 | 0.82914 | 1.0394 | 0.6192 | 0.90763 | 0.86574 | 0.84566 | 0.959 | 1.0439 | 0.86853 | 0.74246 | 122.9245 | -0.002656 | 123.1854 | 123.1851 | 0.26058 | -0.123 | 0.087224 | 123.0478 | 0.006853 | 123.2129 | 123.151 | 0.1032 | 0.091744 | -0.08362 | 123.2548 | 123.1344 | 123.3447 | 123.2453 | -0.33295 | 123.2643 | 123.3492 | 123.1738 | 123.171 | -0.20969
834.2812 | 123.3673 | -122.3373 | 1.0025 | 0.057113 | 0.058739 | 0.0063681 | -0.018198 | -0.046796 | 0.12056 | 0.058893 | 0.14343 | 0.0051213 | -0.025204 | 0.082107 | 0.079085 | 0.88468 | 0.94918 | 0.87062 | 0.94491 | 0.83372 | 1.0394 | 0.60089 | 0.90305 | 0.86116 | 0.84108 | 0.95442 | 1.0393 | 0.86395 | 0.72872 | 122.9382 | -0.057589 | 123.222 | 123.208 | 0.26973 | -0.16878 | 0.03687 | 123.0661 | -0.04808 | 123.2404 | 123.1784 | 0.11236 | 0.036811 | -0.13855 | 123.2823 | 123.1711 | 123.3767 | 123.2865 | -0.40162 | 123.2918 | 123.3767 | 123.2013 | 123.1985 | -0.27378
835.2812 | 123.381 | -122.3236 | 1.0162 | 0.057113 | 0.058739 | 0.0063681 | -0.018198 | -0.045728 | 0.12056 | 0.058893 | 0.14236 | 0.0061893 | -0.025204 | 0.082107 | 0.079085 | 0.87094 | 0.93544 | 0.86604 | 0.94491 | 0.81999 | 1.0302 | 0.59173 | 0.88932 | 0.85658 | 0.84108 | 0.94527 | 1.0256 | 0.85479 | 0.72414 | 122.9153 | -0.071322 | 123.1945 | 123.1896 | 0.27431 | -0.19625 | 0.01398 | 123.0477 | -0.07097 | 123.2129 | 123.1647 | 0.11693 | 0.009343 | -0.16144 | 123.2685 | 123.1436 | 123.3538 | 123.259 | -0.42451 | 123.2689 | 123.3492 | 123.1784 | 123.1802 | -0.29209
836.2812 | 123.4222 | -122.3557 | 0.99335 | 0.072375 | 0.058739 | 0.0074371 | -0.018198 | -0.045728 | 0.12056 | 0.028371 | 0.14129 | 0.0040533 | -0.028409 | 0.083175 | 0.078017 | 0.87094 | 0.93086 | 0.86146 | 0.93576 | 0.81999 | 1.0211 | 0.56883 | 0.88474 | 0.852 | 0.81818 | 0.94069 | 1.021 | 0.85021 | 0.71498 | 122.9245 | -0.05759 | 123.2266 | 123.2171 | 0.29263 | -0.17336 | 0.027711 | 123.0706 | -0.05266 | 123.2404 | 123.1738 | 0.1032 | 0.027652 | -0.14313 | 123.2914 | 123.1756 | 123.3767 | 123.2865 | -0.42451 | 123.2963 | 123.3767 | 123.2059 | 123.2077 | -0.27836
837.2812 | 123.3994 | -122.3373 | 1.0117 | 0.072375 | 0.058739 | 0.0074371 | -0.018198 | -0.047865 | 0.12056 | 0.074154 | 0.1445 | 0.0051213 | -0.027341 | 0.084243 | 0.079085 | 0.85721 | 0.92628 | 0.85689 | 0.91744 | 0.81083 | 1.0256 | 0.57799 | 0.88016 | 0.83826 | 0.81818 | 0.92237 | 1.0118 | 0.8319 | 0.71498 | 122.9153 | -0.094215 | 123.1945 | 123.1942 | 0.27889 | -0.20083 | 0.013978 | 123.0523 | -0.089285 | 123.2175 | 123.1555 | 0.1032 | 0.000184 | -0.17976 | 123.2548 | 123.1482 | 123.363 | 123.2636 | -0.43367 | 123.2597 | 123.3492 | 123.1692 | 123.1756 | -0.29667
838.2812 | 123.4863 | -122.3236 | 0.9613 | 0.041851 | 0.058739 | 0.0074371 | -0.019266 | -0.045728 | 0.11843 | 0.043632 | 0.14343 | 0.0051213 | -0.026272 | 0.082107 | 0.078017 | 0.84347 | 0.91255 | 0.84315 | 0.91287 | 0.79709 | 0.99816 | 0.57799 | 0.88016 | 0.8291 | 0.80902 | 0.92237 | 1.0118 | 0.82274 | 0.70125 | 122.9016 | -0.048439 | 123.1671 | 123.1668 | 0.26516 | -0.16421 | 0.036861 | 123.0249 | -0.038931 | 123.2038 | 123.1326 | 0.10778 | 0.050538 | -0.13856 | 123.2365 | 123.1207 | 123.3218 | 123.2362 | -0.38331 | 123.246 | 123.3354 | 123.1463 | 123.1527 | -0.26006
839.2812 | 123.3994 | -122.3557 | 0.97046 | 0.041851 | 0.060876 | 0.0063681 | -0.017129 | -0.046796 | 0.1195 | 0.074154 | 0.14236 | 0.0061893 | -0.027341 | 0.083175 | 0.079085 | 0.84805 | 0.91255 | 0.83399 | 0.91287 | 0.80167 | 0.99816 | 0.5551 | 0.871 | 0.82453 | 0.80445 | 0.92695 | 1.0027 | 0.81816 | 0.70125 | 122.9108 | -0.057594 | 123.2037 | 123.1896 | 0.2789 | -0.16879 | 0.027706 | 123.0569 | -0.043508 | 123.2267 | 123.1601 | 0.1032 | 0.032226 | -0.1523 | 123.2685 | 123.1573 | 123.3538 | 123.2682 | -0.41536 | 123.2826 | 123.3583 | 123.1738 | 123.1802 | -0.26921
840.2812 | 123.4039 | -122.3648 | 0.99335 | 0.057113 | 0.059808 | 0.0053001 | -0.018198 | -0.045728 | 0.1195 | 0.043632 | 0.14343 | 0.0040533 | -0.027341 | 0.083175 | 0.078017 | 0.83889 | 0.90797 | 0.82942 | 0.90829 | 0.78793 | 0.99816 | 0.5551 | 0.86184 | 0.81995 | 0.79987 | 0.91779 | 0.99811 | 0.82274 | 0.68751 | 122.9199 | -0.085061 | 123.2037 | 123.1942 | 0.27432 | -0.20541 | 0.004818 | 123.0523 | -0.075553 | 123.2267 | 123.1647 | 0.11236 | 0.004759 | -0.17061 | 123.2731 | 123.1527 | 123.363 | 123.2728 | -0.43825 | 123.2826 | 123.3629 | 123.1875 | 123.1848 | -0.30584
841.2812 | 123.3261 | -122.2641 | 1.0208 | 0.057113 | 0.057671 | 0.0063681 | -0.018198 | -0.046796 | 0.11843 | 0.058893 | 0.14236 | 0.0051213 | -0.027341 | 0.082107 | 0.079085 | 0.83431 | 0.89881 | 0.82484 | 0.89913 | 0.78336 | 0.98901 | 0.56883 | 0.85269 | 0.81537 | 0.80445 | 0.90406 | 0.99353 | 0.80901 | 0.68293 | 122.8329 | -0.12168 | 123.0984 | 123.0889 | 0.256 | -0.23746 | -0.031806 | 122.947 | -0.11675 | 123.1168 | 123.0685 | 0.12151 | -0.027286 | -0.21181 | 123.1632 | 123.0475 | 123.2531 | 123.1629 | -0.45198 | 123.1682 | 123.2576 | 123.0731 | 123.0795 | -0.33788
842.2812 | 123.3994 | -122.3923 | 0.93384 | 0.072375 | 0.057671 | 0.0053001 | -0.017129 | -0.046796 | 0.1195 | 0.089415 | 0.1445 | 0.0040533 | -0.028409 | 0.083175 | 0.078017 | 0.82516 | 0.88965 | 0.82026 | 0.89913 | 0.78793 | 0.98443 | 0.55052 | 0.85269 | 0.79705 | 0.78613 | 0.8949 | 0.99353 | 0.80901 | 0.66004 | 122.9428 | -0.034709 | 123.2174 | 123.2125 | 0.26974 | -0.1459 | 0.050591 | 123.0523 | -0.038936 | 123.245 | 123.1784 | 0.12609 | 0.059689 | -0.12483 | 123.2914 | 123.1802 | 123.3767 | 123.2819 | -0.38332 | 123.2872 | 123.3858 | 123.2013 | 123.1893 | -0.2738
843.2812 | 123.4406 | -122.3465 | 0.93384 | 0.041851 | 0.057671 | 0.0053001 | -0.019266 | -0.047865 | 0.12056 | 0.058893 | 0.14236 | 0.0051213 | -0.027341 | 0.082107 | 0.079085 | 0.82974 | 0.88965 | 0.81568 | 0.88539 | 0.77878 | 0.97985 | 0.5551 | 0.84353 | 0.7879 | 0.7724 | 0.89948 | 0.99811 | 0.80901 | 0.65088 | 122.9016 | -0.048444 | 123.1762 | 123.1622 | 0.26058 | -0.15506 | 0.046012 | 122.9974 | -0.034358 | 123.19 | 123.1189 | 0.12151 | 0.064268 | -0.12483 | 123.2319 | 123.1253 | 123.3263 | 123.2362 | -0.37874 | 123.246 | 123.3446 | 123.1555 | 123.1344 | -0.28296
844.2969 | 123.4955 | -122.3511 | 0.95215 | 0.057113 | 0.057671 | 0.0063681 | -0.020335 | -0.047865 | 0.12056 | 0.058893 | 0.14129 | 0.0040533 | -0.026272 | 0.082107 | 0.079085 | 0.82058 | 0.8805 | 0.8111 | 0.88539 | 0.77878 | 0.97069 | 0.54136 | 0.84353 | 0.78332 | 0.76324 | 0.8949 | 0.97979 | 0.80901 | 0.64172 | 122.8924 | -0.066754 | 123.1717 | 123.1622 | 0.26974 | -0.17337 | 0.018545 | 122.9928 | -0.057246 | 123.1946 | 123.1143 | 0.12151 | 0.027644 | -0.14314 | 123.2365 | 123.1298 | 123.3218 | 123.2316 | -0.41079 | 123.246 | 123.3309 | 123.1601 | 123.1344 | -0.31042
845.2812 | 123.3856 | -122.3923 | 0.94757 | 0.057113 | 0.057671 | 0.0063681 | -0.017129 | -0.047865 | 0.11843 | 0.058893 | 0.1445 | 0.0061893 | -0.026272 | 0.083175 | 0.078017 | 0.82058 | 0.8805 | 0.80653 | 0.88082 | 0.76962 | 0.97069 | 0.52762 | 0.83895 | 0.77416 | 0.75866 | 0.89032 | 0.96606 | 0.79985 | 0.6463 | 122.9199 | -0.066755 | 123.2129 | 123.1988 | 0.2789 | -0.17795 | 0.023122 | 123.0386 | -0.057248 | 123.2312 | 123.1509 | 0.11236 | 0.018485 | -0.14772 | 123.2731 | 123.1619 | 123.363 | 123.2728 | -0.41995 | 123.2826 | 123.3583 | 123.1921 | 123.1664 | -0.30127
846.2812 | 123.4085 | -122.3831 | 0.94299 | 0.072375 | 0.057671 | 0.0053001 | -0.016061 | -0.046796 | 0.12056 | 0.058893 | 0.1445 | 0.0051213 | -0.026272 | 0.082107 | 0.078017 | 0.80684 | 0.87592 | 0.80653 | 0.87624 | 0.76046 | 0.97069 | 0.52762 | 0.83895 | 0.76958 | 0.75408 | 0.88575 | 0.97979 | 0.79527 | 0.64172 | 122.9107 | -0.066755 | 123.19 | 123.1896 | 0.2789 | -0.18253 | 0.0277 | 123.0248 | -0.057248 | 123.2221 | 123.1372 | 0.11236 | 0.036799 | -0.14772 | 123.2594 | 123.1436 | 123.3538 | 123.259 | -0.41537 | 123.2689 | 123.3629 | 123.1784 | 123.1527 | -0.30127
847.2812 | 123.3994 | -122.406 | 0.93842 | 0.057113 | 0.057671 | 0.0063681 | -0.018198 | -0.047865 | 0.12056 | 0.043632 | 0.14236 | 0.0051213 | -0.026272 | 0.082107 | 0.079085 | 0.81142 | 0.87592 | 0.80195 | 0.86708 | 0.75588 | 0.97069 | 0.51389 | 0.82979 | 0.76958 | 0.74492 | 0.88575 | 0.97063 | 0.79527 | 0.63714 | 122.9199 | -0.071335 | 123.2174 | 123.208 | 0.28806 | -0.18253 | 0.032277 | 123.0432 | -0.052671 | 123.2358 | 123.1509 | 0.10778 | 0.032218 | -0.14315 | 123.2731 | 123.1619 | 123.3767 | 123.2819 | -0.42453 | 123.2918 | 123.3766 | 123.2013 | 123.1756 | -0.30127
848.2812 | 123.4726 | -122.3831 | 0.91553 | 0.041851 | 0.057671 | 0.0042321 | -0.017129 | -0.045728 | 0.11843 | 0.074154 | 0.14343 | 0.0061893 | -0.027341 | 0.083175 | 0.079085 | 0.80227 | 0.86218 | 0.78821 | 0.86708 | 0.74672 | 0.9478 | 0.50015 | 0.81606 | 0.75585 | 0.74034 | 0.87201 | 0.96148 | 0.77238 | 0.62341 | 122.8833 | -0.048446 | 123.1854 | 123.1713 | 0.28806 | -0.1688 | 0.032273 | 123.0065 | -0.043518 | 123.1992 | 123.1235 | 0.11694 | 0.04595 | -0.14315 | 123.2502 | 123.1298 | 123.3309 | 123.2453 | -0.41538 | 123.2551 | 123.3446 | 123.1555 | 123.139 | -0.29212
849.2812 | 123.3673 | -122.4518 | 0.93384 | 0.087637 | 0.057671 | 0.0074371 | -0.014993 | -0.045728 | 0.12163 | 0.058893 | 0.14129 | 0.0061893 | -0.027341 | 0.083175 | 0.080154 | 0.79311 | 0.8576 | 0.77906 | 0.84877 | 0.74672 | 0.9478 | 0.51389 | 0.81148 | 0.74211 | 0.72661 | 0.85827 | 0.94774 | 0.77238 | 0.61883 | 122.9657 | -0.085071 | 123.2449 | 123.2308 | 0.26517 | -0.18711 | 0.013962 | 123.0706 | -0.075564 | 123.2633 | 123.1784 | 0.10778 | 0.013903 | -0.16146 | 123.3005 | 123.1985 | 123.3996 | 123.3094 | -0.41995 | 123.3101 | 123.3995 | 123.2242 | 123.1939 | -0.31501
850.2969 | 123.4497 | -122.3694 | 0.90637 | 0.041851 | 0.056603 | 0.0053001 | -0.019266 | -0.045728 | 0.11843 | 0.058893 | 0.14343 | 0.0061893 | -0.027341 | 0.084243 | 0.076949 | 0.78853 | 0.84845 | 0.7699 | 0.84877 | 0.73757 | 0.93864 | 0.50931 | 0.8069 | 0.74211 | 0.73577 | 0.85827 | 0.94316 | 0.75864 | 0.61425 | 122.8787 | -0.057605 | 123.1579 | 123.1393 | 0.26059 | -0.16881 | 0.032271 | 122.9836 | -0.048098 | 123.1763 | 123.1052 | 0.12152 | 0.036791 | -0.14773 | 123.2182 | 123.107 | 123.308 | 123.2178 | -0.39706 | 123.2277 | 123.3125 | 123.128 | 123.1115 | -0.29212
851.2812 | 123.3719 | -122.438 | 0.89722 | 0.057113 | 0.057671 | 0.0053001 | -0.018198 | -0.046796 | 0.1195 | 0.043632 | 0.14236 | 0.0051213 | -0.027341 | 0.084243 | 0.078017 | 0.78395 | 0.83471 | 0.77448 | 0.84877 | 0.74215 | 0.93406 | 0.50015 | 0.79774 | 0.73753 | 0.71287 | 0.85369 | 0.93858 | 0.76322 | 0.60967 | 122.9382 | -0.04845 | 123.222 | 123.2125 | 0.27433 | -0.15507 | 0.036847 | 123.0477 | -0.043522 | 123.2358 | 123.1509 | 0.1032 | 0.041367 | -0.134 | 123.2868 | 123.1802 | 123.3721 | 123.2728 | -0.39707 | 123.2917 | 123.3766 | 123.2013 | 123.1756 | -0.28755
852.2812 | 123.3582 | -122.438 | 0.91095 | 0.072375 | 0.055534 | 0.0074371 | -0.018198 | -0.045728 | 0.11843 | 0.058893 | 0.14236 | 0.0051213 | -0.027341 | 0.083175 | 0.079085 | 0.78395 | 0.84387 | 0.77906 | 0.83961 | 0.72383 | 0.92491 | 0.50015 | 0.79774 | 0.71464 | 0.70371 | 0.84912 | 0.93858 | 0.75406 | 0.58678 | 122.9382 | -0.07134 | 123.222 | 123.2171 | 0.27891 | -0.18712 | 0.013957 | 123.0248 | -0.061833 | 123.2358 | 123.1418 | 0.11694 | 0.027634 | -0.15689 | 123.2777 | 123.1619 | 123.363 | 123.2819 | -0.4108 | 123.2872 | 123.3766 | 123.1921 | 123.1527 | -0.32417
853.3125 | 123.3948 | -122.438 | 0.90637 | 0.072375 | 0.058739 | 0.0063681 | -0.017129 | -0.046796 | 0.12056 | 0.058893 | 0.14343 | 0.0051213 | -0.026272 | 0.082107 | 0.079085 | 0.77022 | 0.83471 | 0.76532 | 0.83045 | 0.71925 | 0.92949 | 0.49099 | 0.79316 | 0.71464 | 0.69456 | 0.84454 | 0.93858 | 0.75406 | 0.57762 | 122.929 | -0.075918 | 123.2083 | 123.2034 | 0.27433 | -0.18712 | 0.023114 | 123.0157 | -0.061834 | 123.2312 | 123.1326 | 0.11694 | 0.032212 | -0.15231 | 123.2685 | 123.1573 | 123.3675 | 123.2728 | -0.41538 | 123.2826 | 123.3766 | 123.1921 | 123.1527 | -0.32875
854.2812 | 123.3719 | -122.4564 | 0.92468 | 0.057113 | 0.056603 | 0.0042321 | -0.018198 | -0.046796 | 0.1195 | 0.058893 | 0.14236 | 0.0040533 | -0.027341 | 0.085312 | 0.079085 | 0.76564 | 0.83471 | 0.76532 | 0.82588 | 0.71925 | 0.92033 | 0.49099 | 0.78859 | 0.70548 | 0.70371 | 0.83538 | 0.92943 | 0.74491 | 0.57304 | 122.9474 | -0.098808 | 123.222 | 123.2217 | 0.27433 | -0.20543 | -0.004355 | 123.0294 | -0.089302 | 123.2449 | 123.1601 | 0.13067 | 0.004744 | -0.17978 | 123.2822 | 123.1756 | 123.3767 | 123.2911 | -0.43369 | 123.2917 | 123.3858 | 123.2013 | 123.1618 | -0.35164
855.2969 | 123.3902 | -122.4747 | 0.88806 | 0.057113 | 0.055534 | 0.0074371 | -0.020335 | -0.048933 | 0.1195 | 0.074154 | 0.14343 | 0.0051213 | -0.027341 | 0.083175 | 0.07588 | 0.76106 | 0.82556 | 0.75158 | 0.8213 | 0.71009 | 0.91575 | 0.48184 | 0.77943 | 0.69632 | 0.68998 | 0.83538 | 0.92943 | 0.73117 | 0.56388 | 122.9565 | -0.066765 | 123.2357 | 123.2263 | 0.26975 | -0.17797 | 0.027688 | 123.0386 | -0.052681 | 123.2541 | 123.1646 | 0.1261 | 0.041365 | -0.15689 | 123.296 | 123.1848 | 123.3904 | 123.3002 | -0.40623 | 123.3101 | 123.4041 | 123.2058 | 123.171 | -0.32418
856.2812 | 123.4772 | -122.4152 | 0.88348 | 0.057113 | 0.054466 | 0.0074371 | -0.019266 | -0.046796 | 0.1195 | 0.043632 | 0.1445 | 0.0051213 | -0.026272 | 0.084243 | 0.079085 | 0.74733 | 0.80724 | 0.74701 | 0.81672 | 0.70093 | 0.90659 | 0.47268 | 0.77027 | 0.69632 | 0.6854 | 0.82165 | 0.90653 | 0.74491 | 0.56846 | 122.8878 | -0.066766 | 123.1625 | 123.1622 | 0.27433 | -0.18255 | 0.023109 | 122.9836 | -0.061838 | 123.1854 | 123.1006 | 0.11694 | 0.02305 | -0.13858 | 123.2319 | 123.1161 | 123.3218 | 123.2224 | -0.41081 | 123.2368 | 123.3217 | 123.1601 | 123.1115 | -0.31502
857.2969 | 123.4039 | -122.4609 | 0.87433 | 0.041851 | 0.055534 | 0.0063681 | -0.019266 | -0.046796 | 0.1195 | 0.058893 | 0.14129 | 0.0083263 | -0.025204 | 0.084243 | 0.078017 | 0.74733 | 0.80266 | 0.73327 | 0.81214 | 0.69636 | 0.89286 | 0.44978 | 0.77027 | 0.68259 | 0.67624 | 0.82165 | 0.90195 | 0.72201 | 0.55015 | 122.9107 | -0.062189 | 123.2083 | 123.1942 | 0.28349 | -0.17797 | 0.018528 | 123.0111 | -0.052683 | 123.2312 | 123.1372 | 0.12609 | 0.027626 | -0.15232 | 123.2731 | 123.1573 | 123.3538 | 123.2636 | -0.42455 | 123.2826 | 123.3629 | 123.183 | 123.1435 | -0.32418
858.2812 | 123.4726 | -122.4289 | 0.8606 | 0.041851 | 0.054466 | 0.0053001 | -0.018198 | -0.045728 | 0.12056 | 0.058893 | 0.14236 | 0.0051213 | -0.028409 | 0.083175 | 0.078017 | 0.73817 | 0.79351 | 0.71954 | 0.80298 | 0.6872 | 0.89743 | 0.46352 | 0.76111 | 0.68717 | 0.67166 | 0.80791 | 0.8928 | 0.72659 | 0.55015 | 122.8924 | -0.057613 | 123.1671 | 123.1484 | 0.25602 | -0.1734 | 0.036839 | 122.979 | -0.052686 | 123.19 | 123.1006 | 0.12152 | 0.032202 | -0.13401 | 123.2319 | 123.1161 | 123.3263 | 123.2224 | -0.39708 | 123.2368 | 123.3217 | 123.1555 | 123.1161 | -0.31045
859.2969 | 123.4039 | -122.4655 | 0.84686 | 0.057113 | 0.056603 | 0.0063681 | -0.017129 | -0.046796 | 0.1195 | 0.058893 | 0.14236 | 0.0051213 | -0.027341 | 0.083175 | 0.078017 | 0.72901 | 0.79351 | 0.72412 | 0.79383 | 0.67804 | 0.87454 | 0.44062 | 0.74738 | 0.67801 | 0.66709 | 0.79875 | 0.88364 | 0.70828 | 0.54557 | 122.9061 | -0.053036 | 123.1945 | 123.1896 | 0.28349 | -0.16882 | 0.027679 | 123.0111 | -0.04811 | 123.2129 | 123.1326 | 0.12152 | 0.036778 | -0.13859 | 123.2593 | 123.1436 | 123.3401 | 123.259 | -0.40624 | 123.2643 | 123.3492 | 123.1738 | 123.1435 | -0.30129
860.2812 | 123.4589 | -122.438 | 0.84686 | 0.041851 | 0.056603 | 0.0053001 | -0.017129 | -0.046796 | 0.11843 | 0.058893 | 0.14129 | 0.0061893 | -0.026272 | 0.084243 | 0.078017 | 0.72901 | 0.78435 | 0.71038 | 0.78467 | 0.68262 | 0.87454 | 0.44062 | 0.7428 | 0.67343 | 0.65335 | 0.79417 | 0.87906 | 0.7037 | 0.54099 | 122.8787 | -0.062193 | 123.1671 | 123.1484 | 0.26976 | -0.16424 | 0.027679 | 122.979 | -0.052688 | 123.1808 | 123.0914 | 0.11236 | 0.032199 | -0.14316 | 123.2227 | 123.1207 | 123.3126 | 123.2224 | -0.40624 | 123.2322 | 123.3171 | 123.1417 | 123.1115 | -0.30587
861.3125 | 123.4772 | -122.438 | 0.80109 | 0.026589 | 0.053398 | 0.0074371 | -0.019266 | -0.046796 | 0.1195 | 0.089415 | 0.14129 | 0.0051213 | -0.026272 | 0.083175 | 0.076949 | 0.72443 | 0.78435 | 0.7058 | 0.78467 | 0.66888 | 0.86538 | 0.43147 | 0.73364 | 0.65969 | 0.64877 | 0.79417 | 0.86533 | 0.68538 | 0.53641 | 122.8695 | -0.016416 | 123.1625 | 123.1439 | 0.27434 | -0.1322 | 0.064299 | 122.9745 | -0.006911 | 123.1717 | 123.0868 | 0.11236 | 0.064241 | -0.1157 | 123.2227 | 123.1069 | 123.3034 | 123.2224 | -0.36962 | 123.2322 | 123.3034 | 123.1234 | 123.0977 | -0.26468
862.2812 | 123.6008 | -122.4838 | 0.8194 | 0.041851 | 0.056603 | 0.0053001 | -0.019266 | -0.045728 | 0.11843 | 0.074154 | 0.14129 | 0.0051213 | -0.027341 | 0.084243 | 0.078017 | 0.71528 | 0.77061 | 0.70122 | 0.77551 | 0.65514 | 0.86538 | 0.43147 | 0.72906 | 0.66427 | 0.64419 | 0.78044 | 0.86991 | 0.68996 | 0.52725 | 122.9153 | -0.043884 | 123.1991 | 123.185 | 0.26976 | -0.16425 | 0.045988 | 123.0111 | -0.038958 | 123.2129 | 123.128 | 0.11694 | 0.050508 | -0.12944 | 123.2593 | 123.139 | 123.3492 | 123.2544 | -0.38793 | 123.2643 | 123.3537 | 123.1738 | 123.1481 | -0.29214
863.2969 | 123.3719 | -122.5021 | 0.8194 | 0.072375 | 0.055534 | 0.0042321 | -0.018198 | -0.048933 | 0.1195 | 0.043632 | 0.14023 | 0.0061893 | -0.028409 | 0.08638 | 0.078017 | 0.70154 | 0.76603 | 0.69207 | 0.77551 | 0.65057 | 0.86538 | 0.41773 | 0.72448 | 0.65969 | 0.63961 | 0.7667 | 0.84701 | 0.68538 | 0.52267 | 122.9199 | -0.043884 | 123.2037 | 123.1942 | 0.27434 | -0.16883 | 0.045988 | 123.0248 | -0.052693 | 123.2266 | 123.1417 | 0.11694 | 0.027615 | -0.13401 | 123.2776 | 123.1527 | 123.3675 | 123.2682 | -0.40167 | 123.2688 | 123.3491 | 123.1875 | 123.1618 | -0.29672
864.2812 | 123.4634 | -122.4655 | 0.81482 | 0.072375 | 0.055534 | 0.0074371 | -0.018198 | -0.047865 | 0.1195 | 0.058893 | 0.14129 | 0.0051213 | -0.027341 | 0.084243 | 0.07588 | 0.70612 | 0.74772 | 0.68749 | 0.7572 | 0.64141 | 0.85165 | 0.40399 | 0.71075 | 0.65969 | 0.63503 | 0.7667 | 0.85617 | 0.67623 | 0.52267 | 122.8695 | -0.05762 | 123.1716 | 123.153 | 0.2835 | -0.17341 | 0.03683 | 122.9882 | -0.048115 | 123.1763 | 123.1005 | 0.11236 | 0.04135 | -0.13859 | 123.2227 | 123.1069 | 123.3172 | 123.2132 | -0.41083 | 123.2322 | 123.3217 | 123.1417 | 123.1252 | -0.29214
865.2969 | 123.5001 | -122.4609 | 0.80566 | 0.057113 | 0.054466 | 0.0074371 | -0.017129 | -0.046796 | 0.11843 | 0.074154 | 0.14236 | 0.0061893 | -0.027341 | 0.084243 | 0.076949 | 0.69238 | 0.7523 | 0.68749 | 0.7572 | 0.63683 | 0.84707 | 0.40399 | 0.70617 | 0.64138 | 0.63045 | 0.76213 | 0.84243 | 0.66249 | 0.50894 | 122.8649 | -0.048465 | 123.1533 | 123.1484 | 0.2835 | -0.16884 | 0.041407 | 122.9699 | -0.043539 | 123.1671 | 123.0914 | 0.12152 | 0.03677 | -0.14317 | 123.2181 | 123.0978 | 123.308 | 123.2132 | -0.40167 | 123.2231 | 123.3034 | 123.1234 | 123.1023 | -0.29673
866.2812 | 123.4772 | -122.4884 | 0.83313 | 0.057113 | 0.055534 | 0.0074371 | -0.017129 | -0.045728 | 0.1195 | 0.074154 | 0.14129 | 0.0051213 | -0.026272 | 0.08638 | 0.078017 | 0.69238 | 0.75688 | 0.68291 | 0.76178 | 0.65057 | 0.85623 | 0.39483 | 0.71533 | 0.65054 | 0.63045 | 0.7667 | 0.85617 | 0.67623 | 0.51352 | 122.8832 | -0.071352 | 123.1808 | 123.1713 | 0.28808 | -0.18256 | 0.023098 | 123.0019 | -0.066426 | 123.2037 | 123.1189 | 0.11694 | 0.023039 | -0.1569 | 123.2502 | 123.139 | 123.3446 | 123.2453 | -0.4383 | 123.2551 | 123.3446 | 123.1646 | 123.1389 | -0.31961
867.2969 | 123.436 | -122.5113 | 0.80566 | 0.041851 | 0.054466 | 0.0063681 | -0.018198 | -0.046796 | 0.11843 | 0.074154 | 0.14129 | 0.0072583 | -0.026272 | 0.085312 | 0.07588 | 0.69696 | 0.74772 | 0.69207 | 0.75262 | 0.64599 | 0.84707 | 0.40399 | 0.70159 | 0.64138 | 0.63961 | 0.76213 | 0.84701 | 0.67165 | 0.50894 | 122.9153 | -0.053043 | 123.2083 | 123.2034 | 0.28808 | -0.15968 | 0.041407 | 123.0202 | -0.043539 | 123.2129 | 123.1509 | 0.13068 | 0.041348 | -0.13402 | 123.2639 | 123.1573 | 123.3584 | 123.259 | -0.40167 | 123.2734 | 123.3583 | 123.1829 | 123.1527 | -0.29673
868.2812 | 123.4863 | -122.4747 | 0.82855 | 0.041851 | 0.054466 | 0.0063681 | -0.018198 | -0.045728 | 0.12056 | 0.058893 | 0.14129 | 0.0072583 | -0.026272 | 0.085312 | 0.076949 | 0.68323 | 0.74314 | 0.68291 | 0.74804 | 0.62767 | 0.84249 | 0.39483 | 0.70617 | 0.64138 | 0.6213 | 0.75755 | 0.84243 | 0.66707 | 0.49978 | 122.8695 | -0.080509 | 123.1579 | 123.1576 | 0.28808 | -0.20088 | 0.01394 | 122.9745 | -0.071005 | 123.1808 | 123.096 | 0.12152 | 0.013882 | -0.16148 | 123.2227 | 123.1023 | 123.3172 | 123.2178 | -0.43372 | 123.2322 | 123.3171 | 123.1417 | 123.116 | -0.32877
869.3125 | 123.4543 | -122.4701 | 0.81024 | 0.041851 | 0.053398 | 0.0074371 | -0.018198 | -0.047865 | 0.1195 | 0.074154 | 0.14129 | 0.0051213 | -0.026272 | 0.085312 | 0.078017 | 0.69238 | 0.74772 | 0.68291 | 0.74804 | 0.61851 | 0.83791 | 0.3811 | 0.71075 | 0.64138 | 0.61214 | 0.75755 | 0.83786 | 0.66249 | 0.4952 | 122.8512 | -0.062199 | 123.1625 | 123.153 | 0.30181 | -0.19173 | 0.027672 | 122.9653 | -0.052695 | 123.1808 | 123.0822 | 0.11694 | 0.027613 | -0.14775 | 123.2181 | 123.0886 | 123.308 | 123.2178 | -0.42914 | 123.2276 | 123.3079 | 123.1326 | 123.1115 | -0.31504
870.2812 | 123.4497 | -122.4838 | 0.81024 | 0.072375 | 0.053398 | 0.0053001 | -0.018198 | -0.046796 | 0.1195 | 0.074154 | 0.14129 | 0.0061893 | -0.027341 | 0.085312 | 0.080154 | 0.68323 | 0.74314 | 0.67833 | 0.73889 | 0.62309 | 0.84249 | 0.39026 | 0.69701 | 0.6368 | 0.61672 | 0.74839 | 0.84243 | 0.65791 | 0.49978 | 122.8741 | -0.071356 | 123.1671 | 123.1622 | 0.28808 | -0.18715 | 0.03225 | 122.9836 | -0.061852 | 123.1808 | 123.1005 | 0.11694 | 0.032192 | -0.15233 | 123.2227 | 123.1069 | 123.3263 | 123.227 | -0.41999 | 123.2322 | 123.3263 | 123.1417 | 123.1206 | -0.31046
871.2969 | 123.3765 | -122.5433 | 0.80109 | 0.041851 | 0.054466 | 0.0042321 | -0.018198 | -0.045728 | 0.1195 | 0.028371 | 0.14129 | 0.0051213 | -0.028409 | 0.085312 | 0.078017 | 0.68323 | 0.73856 | 0.67833 | 0.74346 | 0.62309 | 0.83334 | 0.40857 | 0.70159 | 0.63222 | 0.60756 | 0.73923 | 0.83786 | 0.65333 | 0.49062 | 122.9519 | -0.057622 | 123.2266 | 123.2217 | 0.26976 | -0.17799 | 0.032249 | 123.034 | -0.061853 | 123.2449 | 123.1509 | 0.11694 | 0.036769 | -0.14775 | 123.2868 | 123.1664 | 123.3767 | 123.2819 | -0.39251 | 123.2826 | 123.3812 | 123.1967 | 123.1756 | -0.31046
872.2812 | 123.4772 | -122.5342 | 0.78278 | 0.057113 | 0.053398 | 0.0042321 | -0.020335 | -0.046796 | 0.12056 | 0.089415 | 0.14023 | 0.0040533 | -0.025204 | 0.089585 | 0.07588 | 0.67407 | 0.7294 | 0.6646 | 0.73889 | 0.61851 | 0.82876 | 0.37652 | 0.68785 | 0.61391 | 0.61214 | 0.73923 | 0.83328 | 0.64418 | 0.49062 | 122.9107 | -0.04389 | 123.2083 | 123.1988 | 0.28808 | -0.16426 | 0.04598 | 123.0248 | -0.043543 | 123.222 | 123.1463 | 0.12152 | 0.0505 | -0.1386 | 123.2731 | 123.1527 | 123.3629 | 123.2636 | -0.40626 | 123.2734 | 123.3675 | 123.1784 | 123.1481 | -0.29215
873.2812 | 123.4222 | -122.5571 | 0.737 | 0.041851 | 0.055534 | 0.0042321 | -0.019266 | -0.047865 | 0.11736 | 0.074154 | 0.14129 | 0.0051213 | -0.028409 | 0.087449 | 0.079085 | 0.66034 | 0.72483 | 0.65544 | 0.72973 | 0.61851 | 0.82418 | 0.37652 | 0.6787 | 0.60933 | 0.60298 | 0.74381 | 0.8287 | 0.64418 | 0.48146 | 122.9336 | -0.007271 | 123.2174 | 123.2125 | 0.27892 | -0.11849 | 0.087178 | 123.0385 | 0.006811 | 123.2358 | 123.1601 | 0.12152 | 0.091698 | -0.092824 | 123.2868 | 123.1756 | 123.3812 | 123.2819 | -0.36048 | 123.3009 | 123.3858 | 123.2012 | 123.1664 | -0.25554
874.2812 | 123.4909 | -122.5204 | 0.78278 | 0.057113 | 0.054466 | 0.0053001 | -0.018198 | -0.046796 | 0.11843 | 0.058893 | 0.14129 | 0.0061893 | -0.028409 | 0.087449 | 0.07588 | 0.66491 | 0.72025 | 0.65544 | 0.72057 | 0.6002 | 0.8196 | 0.37652 | 0.6787 | 0.61391 | 0.59383 | 0.73923 | 0.8287 | 0.6396 | 0.47231 | 122.897 | -0.062204 | 123.1854 | 123.1759 | 0.27892 | -0.18258 | 0.036823 | 122.9928 | -0.043543 | 123.1991 | 123.1143 | 0.12152 | 0.045922 | -0.14318 | 123.241 | 123.1206 | 123.34 | 123.2407 | -0.40626 | 123.2597 | 123.3491 | 123.16 | 123.1344 | -0.31047
875.2812 | 123.468 | -122.5525 | 0.75989 | 0.057113 | 0.053398 | 0.0042321 | -0.020335 | -0.04466 | 0.1195 | 0.074154 | 0.14023 | 0.0029843 | -0.026272 | 0.084243 | 0.07588 | 0.65118 | 0.71567 | 0.65086 | 0.72515 | 0.60936 | 0.80129 | 0.37194 | 0.67412 | 0.60475 | 0.58467 | 0.73465 | 0.81954 | 0.63502 | 0.46773 | 122.9244 | -0.034737 | 123.2037 | 123.2034 | 0.27892 | -0.15053 | 0.041397 | 123.0202 | -0.025234 | 123.2266 | 123.1372 | 0.11694 | 0.059653 | -0.12487 | 123.2776 | 123.1618 | 123.3538 | 123.2682 | -0.38795 | 123.2871 | 123.372 | 123.1875 | 123.1572 | -0.29216
876.2969 | 123.3673 | -122.5525 | 0.80566 | 0.041851 | 0.055534 | 0.0031631 | -0.017129 | -0.04466 | 0.12056 | 0.058893 | 0.14236 | 0.0051213 | -0.027341 | 0.085312 | 0.07588 | 0.65118 | 0.71109 | 0.65086 | 0.71599 | 0.59562 | 0.80586 | 0.3811 | 0.66954 | 0.59559 | 0.58467 | 0.72092 | 0.81038 | 0.63044 | 0.45399 | 122.9336 | -0.08967 | 123.2037 | 123.2034 | 0.26976 | -0.21005 | 0.000199 | 123.0065 | -0.084745 | 123.222 | 123.1372 | 0.13068 | 0.004719 | -0.17522 | 123.2685 | 123.1481 | 123.3584 | 123.2636 | -0.42457 | 123.2734 | 123.3629 | 123.1829 | 123.1481 | -0.35167
877.2812 | 123.4589 | -122.525 | 0.7782 | 0.041851 | 0.054466 | 0.0042321 | -0.018198 | -0.046796 | 0.1195 | 0.043632 | 0.14129 | 0.0061893 | -0.027341 | 0.087449 | 0.078017 | 0.64202 | 0.69735 | 0.64171 | 0.71142 | 0.6002 | 0.79671 | 0.36278 | 0.66954 | 0.59101 | 0.57551 | 0.72092 | 0.8058 | 0.63044 | 0.46315 | 122.8878 | -0.066782 | 123.167 | 123.1667 | 0.27892 | -0.178 | 0.018508 | 122.9882 | -0.057279 | 123.1946 | 123.1005 | 0.11236 | 0.027607 | -0.14776 | 123.2364 | 123.1252 | 123.3217 | 123.2224 | -0.41541 | 123.2459 | 123.3308 | 123.1555 | 123.116 | -0.31505
878.3125 | 123.4222 | -122.5662 | 0.75531 | 0.087637 | 0.054466 | 0.0074371 | -0.019266 | -0.046796 | 0.11843 | 0.043632 | 0.14129 | 0.0051213 | -0.027341 | 0.087449 | 0.076949 | 0.64202 | 0.69735 | 0.63255 | 0.70226 | 0.58646 | 0.79213 | 0.36278 | 0.66038 | 0.58643 | 0.57093 | 0.71176 | 0.79665 | 0.61213 | 0.45399 | 122.929 | -0.053051 | 123.2082 | 123.1988 | 0.26977 | -0.16885 | 0.036818 | 123.0202 | -0.043548 | 123.2266 | 123.1372 | 0.11694 | 0.041338 | -0.14318 | 123.2685 | 123.1527 | 123.3584 | 123.2636 | -0.39253 | 123.278 | 123.3629 | 123.1783 | 123.1527 | -0.30132
879.2812 | 123.4589 | -122.5571 | 0.74158 | 0.057113 | 0.055534 | 0.0042321 | -0.018198 | -0.046796 | 0.11736 | 0.074154 | 0.14129 | 0.0040533 | -0.027341 | 0.08638 | 0.078017 | 0.63287 | 0.69735 | 0.62339 | 0.6931 | 0.58646 | 0.79671 | 0.3582 | 0.65122 | 0.58186 | 0.56635 | 0.70718 | 0.79207 | 0.6167 | 0.44941 | 122.9153 | -0.048475 | 123.1899 | 123.1805 | 0.26519 | -0.15512 | 0.055129 | 123.0065 | -0.034394 | 123.2083 | 123.1234 | 0.11694 | 0.050492 | -0.12487 | 123.2502 | 123.1435 | 123.3538 | 123.2544 | -0.38337 | 123.2643 | 123.3491 | 123.1738 | 123.1389 | -0.29216
880.2969 | 123.4039 | -122.5983 | 0.74158 | 0.072375 | 0.051261 | 0.0063681 | -0.018198 | -0.047865 | 0.11629 | 0.058893 | 0.14129 | 0.0061893 | -0.027341 | 0.08638 | 0.078017 | 0.63744 | 0.6882 | 0.62797 | 0.69768 | 0.58646 | 0.79213 | 0.37652 | 0.65122 | 0.59101 | 0.57093 | 0.70261 | 0.78749 | 0.60755 | 0.45399 | 122.9748 | -0.043897 | 123.2357 | 123.2262 | 0.25145 | -0.15512 | 0.050551 | 123.0523 | -0.038972 | 123.2495 | 123.1692 | 0.11694 | 0.045913 | -0.13403 | 123.2959 | 123.1847 | 123.3904 | 123.2865 | -0.36506 | 123.3009 | 123.3858 | 123.2058 | 123.1893 | -0.28759
881.2812 | 123.4589 | -122.5662 | 0.74616 | 0.041851 | 0.053398 | 0.0042321 | -0.018198 | -0.045728 | 0.11843 | 0.074154 | 0.14129 | 0.0061893 | -0.028409 | 0.085312 | 0.078017 | 0.63744 | 0.67904 | 0.61424 | 0.68852 | 0.57273 | 0.78297 | 0.3582 | 0.64207 | 0.57728 | 0.56178 | 0.70261 | 0.78291 | 0.60297 | 0.44026 | 122.9244 | -0.057631 | 123.2037 | 123.1805 | 0.25603 | -0.17343 | 0.036815 | 123.0065 | -0.04355 | 123.2083 | 123.128 | 0.12152 | 0.036757 | -0.14319 | 123.2547 | 123.1389 | 123.3492 | 123.2453 | -0.38795 | 123.2688 | 123.3491 | 123.1692 | 123.1435 | -0.3059
882.3125 | 123.3902 | -122.6028 | 0.74158 | 0.041851 | 0.051261 | 0.0053001 | -0.018198 | -0.04466 | 0.11843 | 0.074154 | 0.14023 | 0.0061893 | -0.026272 | 0.08638 | 0.076949 | 0.62829 | 0.68362 | 0.61424 | 0.67937 | 0.58646 | 0.79213 | 0.3582 | 0.64665 | 0.57728 | 0.56635 | 0.69803 | 0.78291 | 0.60297 | 0.44483 | 122.961 | -0.06221 | 123.2311 | 123.2171 | 0.25603 | -0.15512 | 0.050551 | 123.0477 | -0.043551 | 123.2495 | 123.1692 | 0.12152 | 0.041335 | -0.13861 | 123.2822 | 123.1893 | 123.395 | 123.2865 | -0.38337 | 123.3009 | 123.3858 | 123.2058 | 123.1801 | -0.29674
883.2812 | 123.4818 | -122.5388 | 0.74158 | 0.057113 | 0.052329 | 0.0042321 | -0.018198 | -0.046796 | 0.11736 | 0.028371 | 0.14023 | 0.0051213 | -0.028409 | 0.08638 | 0.076949 | 0.61913 | 0.67446 | 0.60508 | 0.67937 | 0.5773 | 0.77839 | 0.34905 | 0.63291 | 0.5727 | 0.55262 | 0.68887 | 0.77833 | 0.59381 | 0.44026 | 122.8878 | -0.06221 | 123.1579 | 123.1438 | 0.25603 | -0.16427 | 0.036815 | 122.979 | -0.052708 | 123.1717 | 123.0914 | 0.11236 | 0.036756 | -0.14777 | 123.2181 | 123.1161 | 123.3171 | 123.2132 | -0.39253 | 123.2276 | 123.3171 | 123.1326 | 123.1115 | -0.30132
884.3125 | 123.4131 | -122.6028 | 0.74616 | 0.041851 | 0.054466 | 0.0042321 | -0.018198 | -0.047865 | 0.11843 | 0.058893 | 0.14129 | 0.0051213 | -0.027341 | 0.088517 | 0.074812 | 0.61913 | 0.67904 | 0.6005 | 0.67021 | 0.56815 | 0.76924 | 0.35363 | 0.63291 | 0.5727 | 0.56178 | 0.68887 | 0.78291 | 0.59839 | 0.42652 | 122.9565 | -0.075945 | 123.222 | 123.2033 | 0.24688 | -0.17801 | 0.02308 | 123.0294 | -0.057286 | 123.2358 | 123.1646 | 0.13526 | 0.036757 | -0.14777 | 123.2731 | 123.171 | 123.3721 | 123.2819 | -0.39253 | 123.2917 | 123.3858 | 123.2012 | 123.1755 | -0.31964
885.2812 | 123.4543 | -122.6074 | 0.71869 | 0.057113 | 0.052329 | 0.0053001 | -0.018198 | -0.046796 | 0.1195 | 0.058893 | 0.14023 | 0.0051213 | -0.028409 | 0.087449 | 0.076949 | 0.60997 | 0.6653 | 0.6005 | 0.66563 | 0.54525 | 0.76924 | 0.35363 | 0.61917 | 0.57728 | 0.54804 | 0.67513 | 0.77375 | 0.58008 | 0.43568 | 122.961 | -0.053057 | 123.2174 | 123.2079 | 0.24688 | -0.17344 | 0.050546 | 123.0431 | -0.043555 | 123.2266 | 123.1555 | 0.11236 | 0.055066 | -0.13861 | 123.2731 | 123.1527 | 123.3767 | 123.2727 | -0.36506 | 123.2826 | 123.3812 | 123.1875 | 123.1847 | -0.28301
886.2969 | 123.381 | -122.644 | 0.74616 | 0.057113 | 0.052329 | 0.0042321 | -0.017129 | -0.046796 | 0.11736 | 0.074154 | 0.13916 | 0.0061893 | -0.027341 | 0.08638 | 0.076949 | 0.60997 | 0.65615 | 0.59135 | 0.66105 | 0.54983 | 0.7555 | 0.33531 | 0.61917 | 0.56812 | 0.55262 | 0.67056 | 0.76918 | 0.58923 | 0.42652 | 122.9794 | -0.085102 | 123.254 | 123.2354 | 0.25604 | -0.19632 | 0.009344 | 123.0706 | -0.0756 | 123.2632 | 123.1967 | 0.1261 | 0.023021 | -0.15692 | 123.3051 | 123.1939 | 123.3995 | 123.3002 | -0.41085 | 123.3146 | 123.4132 | 123.2333 | 123.2122 | -0.31964
887.2812 | 123.4406 | -122.6624 | 0.68665 | 0.057113 | 0.052329 | 0.0042321 | -0.014993 | -0.047865 | 0.11843 | 0.058893 | 0.14129 | 0.0051213 | -0.027341 | 0.088517 | 0.078017 | 0.59624 | 0.64699 | 0.59135 | 0.65648 | 0.54525 | 0.75092 | 0.33531 | 0.61002 | 0.5727 | 0.53888 | 0.66598 | 0.75544 | 0.57092 | 0.4311 | 122.9977 | -0.030171 | 123.2586 | 123.2537 | 0.25604 | -0.14139 | 0.064274 | 123.0935 | -0.020669 | 123.2724 | 123.2012 | 0.10778 | 0.068794 | -0.11573 | 123.3188 | 123.2076 | 123.4133 | 123.3093 | -0.35134 | 123.3283 | 123.4178 | 123.2333 | 123.2351 | -0.25555
888.3125 | 123.4314 | -122.6166 | 0.737 | 0.057113 | 0.051261 | 0.0053001 | -0.019266 | -0.046796 | 0.11843 | 0.058893 | 0.14129 | 0.0061893 | -0.027341 | 0.08638 | 0.078017 | 0.59624 | 0.65615 | 0.57761 | 0.65648 | 0.55441 | 0.74634 | 0.33531 | 0.6146 | 0.56812 | 0.53888 | 0.65682 | 0.75086 | 0.58008 | 0.42652 | 122.9519 | -0.080525 | 123.2128 | 123.1942 | 0.2423 | -0.18259 | 0.009342 | 123.0431 | -0.08018 | 123.2312 | 123.1555 | 0.11236 | 0.013862 | -0.15692 | 123.2731 | 123.171 | 123.3629 | 123.2727 | -0.40169 | 123.2734 | 123.3674 | 123.1967 | 123.1847 | -0.31048
889.2812 | 123.4863 | -122.5983 | 0.6958 | 0.057113 | 0.050193 | 0.0042321 | -0.017129 | -0.046796 | 0.11736 | 0.058893 | 0.14023 | 0.0061893 | -0.026272 | 0.087449 | 0.076949 | 0.5825 | 0.64241 | 0.57761 | 0.64732 | 0.54067 | 0.74176 | 0.33073 | 0.61002 | 0.55896 | 0.5343 | 0.6614 | 0.75086 | 0.56634 | 0.42194 | 122.929 | -0.048483 | 123.1808 | 123.1759 | 0.24688 | -0.15513 | 0.045962 | 123.0202 | -0.034403 | 123.2083 | 123.1326 | 0.11236 | 0.055061 | -0.12946 | 123.2456 | 123.1389 | 123.34 | 123.2407 | -0.36507 | 123.2597 | 123.3491 | 123.1646 | 123.1572 | -0.27386
890.2969 | 123.4955 | -122.5845 | 0.70496 | 0.072375 | 0.053398 | 0.0042321 | -0.018198 | -0.045728 | 0.11843 | 0.058893 | 0.14129 | 0.0051213 | -0.025204 | 0.089585 | 0.078017 | 0.58708 | 0.64241 | 0.57303 | 0.6519 | 0.52694 | 0.73718 | 0.32157 | 0.59628 | 0.55896 | 0.53888 | 0.6614 | 0.7417 | 0.56634 | 0.41736 | 122.9061 | -0.053059 | 123.1716 | 123.1576 | 0.25146 | -0.17802 | 0.032228 | 123.0019 | -0.043558 | 123.1808 | 123.1234 | 0.12152 | 0.036748 | -0.13862 | 123.2364 | 123.1115 | 123.3217 | 123.2269 | -0.38338 | 123.2459 | 123.3262 | 123.1509 | 123.1435 | -0.2876
891.2812 | 123.4726 | -122.6257 | 0.737 | 0.072375 | 0.050193 | 0.0031631 | -0.020335 | -0.048933 | 0.11843 | 0.043632 | 0.14236 | 0.0040533 | -0.028409 | 0.087449 | 0.078017 | 0.5825 | 0.63783 | 0.56845 | 0.64274 | 0.52236 | 0.73718 | 0.33073 | 0.60086 | 0.5498 | 0.52972 | 0.65682 | 0.73255 | 0.55718 | 0.41278 | 122.9565 | -0.09426 | 123.2082 | 123.1942 | 0.23772 | -0.21464 | 0.000184 | 123.0385 | -0.08018 | 123.2266 | 123.1555 | 0.11694 | -0.004453 | -0.17982 | 123.2685 | 123.1481 | 123.3629 | 123.2636 | -0.40627 | 123.2826 | 123.3583 | 123.1829 | 123.1755 | -0.32422
892.3125 | 123.3673 | -122.6532 | 0.71869 | 0.057113 | 0.051261 | 0.0042321 | -0.019266 | -0.048933 | 0.11843 | 0.074154 | 0.14129 | 0.0051213 | -0.027341 | 0.08638 | 0.076949 | 0.57792 | 0.63325 | 0.56845 | 0.63358 | 0.52694 | 0.73261 | 0.32157 | 0.59628 | 0.5498 | 0.52514 | 0.64766 | 0.7417 | 0.55718 | 0.42194 | 122.9748 | -0.085106 | 123.2311 | 123.2217 | 0.24688 | -0.19175 | 0.013917 | 123.0751 | -0.071026 | 123.2495 | 123.1783 | 0.1032 | 0.023015 | -0.16151 | 123.2868 | 123.1801 | 123.3858 | 123.2865 | -0.39712 | 123.3009 | 123.3949 | 123.2104 | 123.203 | -0.29675
893.2812 | 123.3994 | -122.6624 | 0.72327 | 0.057113 | 0.050193 | 0.0042321 | -0.017129 | -0.047865 | 0.11736 | 0.043632 | 0.14236 | 0.0051213 | -0.028409 | 0.087449 | 0.07588 | 0.57335 | 0.63325 | 0.5593 | 0.62901 | 0.52694 | 0.72803 | 0.31241 | 0.5917 | 0.5498 | 0.51599 | 0.64766 | 0.73255 | 0.54345 | 0.41278 | 122.9748 | -0.094262 | 123.2357 | 123.2217 | 0.24688 | -0.19633 | 0.00476 | 123.0751 | -0.075604 | 123.2541 | 123.1783 | 0.10321 | 0.00928 | -0.17982 | 123.2914 | 123.1893 | 123.3904 | 123.2956 | -0.41085 | 123.31 | 123.3949 | 123.2058 | 123.2122 | -0.31049
894.2812 | 123.3719 | -122.6395 | 0.70038 | 0.072375 | 0.051261 | 0.0053001 | -0.018198 | -0.048933 | 0.11843 | 0.058893 | 0.14236 | 0.0051213 | -0.027341 | 0.087449 | 0.07588 | 0.57335 | 0.6241 | 0.56388 | 0.63358 | 0.51778 | 0.72345 | 0.30784 | 0.58712 | 0.54522 | 0.51599 | 0.64766 | 0.72797 | 0.54803 | 0.41278 | 122.9473 | -0.066795 | 123.2128 | 123.2033 | 0.25604 | -0.1826 | 0.023071 | 123.0522 | -0.052715 | 123.2266 | 123.1555 | 0.10321 | 0.02759 | -0.15235 | 123.273 | 123.1572 | 123.3629 | 123.2636 | -0.39254 | 123.2871 | 123.3674 | 123.1875 | 123.1847 | -0.2876
895.2812 | 123.3765 | -122.644 | 0.6958 | 0.057113 | 0.051261 | 0.0053001 | -0.017129 | -0.047865 | 0.11843 | 0.043632 | 0.14129 | 0.0051213 | -0.027341 | 0.089585 | 0.074812 | 0.57335 | 0.61952 | 0.55472 | 0.62901 | 0.5132 | 0.71887 | 0.31699 | 0.58712 | 0.54522 | 0.52514 | 0.64308 | 0.72339 | 0.54345 | 0.39905 | 122.961 | -0.066796 | 123.2174 | 123.1988 | 0.23773 | -0.1826 | 0.023069 | 123.0431 | -0.052717 | 123.2312 | 123.1692 | 0.1261 | 0.027589 | -0.15235 | 123.273 | 123.1572 | 123.3629 | 123.2636 | -0.37881 | 123.2871 | 123.3674 | 123.1875 | 123.1893 | -0.29675
896.2812 | 123.3719 | -122.6578 | 0.68665 | 0.041851 | 0.051261 | 0.0042321 | -0.017129 | -0.047865 | 0.11843 | 0.058893 | 0.14129 | 0.0072583 | -0.026272 | 0.088517 | 0.078017 | 0.56877 | 0.62867 | 0.55472 | 0.62443 | 0.50404 | 0.71887 | 0.29868 | 0.57339 | 0.54065 | 0.51141 | 0.63393 | 0.71881 | 0.53887 | 0.40363 | 122.9565 | -0.06222 | 123.2265 | 123.2125 | 0.25604 | -0.18261 | 0.032224 | 123.0614 | -0.052719 | 123.2312 | 123.1692 | 0.10778 | 0.032165 | -0.14778 | 123.2822 | 123.1618 | 123.3766 | 123.2865 | -0.38797 | 123.2917 | 123.3766 | 123.1966 | 123.1984 | -0.28302
897.3125 | 123.3948 | -122.6898 | 0.69122 | 0.041851 | 0.052329 | 0.0042321 | -0.020335 | -0.047865 | 0.1195 | 0.074154 | 0.14129 | 0.0051213 | -0.029477 | 0.088517 | 0.07588 | 0.56419 | 0.61952 | 0.54556 | 0.61527 | 0.50404 | 0.71429 | 0.2941 | 0.57339 | 0.53149 | 0.50683 | 0.63393 | 0.72339 | 0.53887 | 0.39447 | 122.9839 | -0.075954 | 123.254 | 123.2354 | 0.25146 | -0.18718 | 0.023068 | 123.0843 | -0.057296 | 123.2632 | 123.1966 | 0.11236 | 0.032167 | -0.15235 | 123.3051 | 123.1939 | 123.4041 | 123.3093 | -0.39712 | 123.3237 | 123.4132 | 123.2287 | 123.2213 | -0.29676
898.2812 | 123.4085 | -122.6944 | 0.68207 | 0.072375 | 0.050193 | 0.0031631 | -0.018198 | -0.046796 | 0.11843 | 0.058893 | 0.14129 | 0.0061893 | -0.028409 | 0.090654 | 0.080154 | 0.55503 | 0.60578 | 0.54556 | 0.61985 | 0.49488 | 0.71887 | 0.30784 | 0.57339 | 0.52691 | 0.49767 | 0.62477 | 0.70508 | 0.53429 | 0.38531 | 123.0022 | -0.06222 | 123.2494 | 123.24 | 0.23773 | -0.18718 | 0.036802 | 123.0797 | -0.057298 | 123.2678 | 123.1921 | 0.11236 | 0.023007 | -0.14778 | 123.3142 | 123.1893 | 123.4133 | 123.3002 | -0.37423 | 123.3192 | 123.3995 | 123.2287 | 123.2213 | -0.29676
899.3125 | 123.5413 | -122.6349 | 0.66834 | 0.041851 | 0.052329 | 0.0042321 | -0.019266 | -0.046796 | 0.11843 | 0.074154 | 0.14236 | 0.0040533 | -0.028409 | 0.089585 | 0.07588 | 0.55045 | 0.61036 | 0.54098 | 0.61527 | 0.50404 | 0.69598 | 0.30326 | 0.55965 | 0.52691 | 0.49767 | 0.61561 | 0.71423 | 0.52971 | 0.38531 | 122.9381 | -0.053066 | 123.1853 | 123.1759 | 0.23773 | -0.16429 | 0.027642 | 123.0202 | -0.052722 | 123.1945 | 123.1326 | 0.11236 | 0.045898 | -0.13862 | 123.2502 | 123.1389 | 123.3309 | 123.2452 | -0.36508 | 123.2505 | 123.3491 | 123.1646 | 123.1618 | -0.28303
900.2812 | 123.3902 | -122.7081 | 0.66376 | 0.041851 | 0.051261 | 0.0031631 | -0.018198 | -0.045728 | 0.11843 | 0.074154 | 0.14129 | 0.0061893 | -0.027341 | 0.089585 | 0.07588 | 0.54588 | 0.60578 | 0.53641 | 0.61069 | 0.49946 | 0.70056 | 0.29868 | 0.56423 | 0.52233 | 0.49767 | 0.62935 | 0.7005 | 0.52513 | 0.38989 | 123.0068 | -0.053066 | 123.254 | 123.2445 | 0.23773 | -0.1643 | 0.036798 | 123.098 | -0.034408 | 123.2724 | 123.2058 | 0.10778 | 0.03674 | -0.13862 | 123.3188 | 123.2076 | 123.4087 | 123.3139 | -0.36508 | 123.3375 | 123.4086 | 123.2333 | 123.2305 | -0.27387
901.3125 | 123.4131 | -122.6761 | 0.66834 | 0.072375 | 0.051261 | 0.0031631 | -0.018198 | -0.046796 | 0.12056 | 0.058893 | 0.14129 | 0.0051213 | -0.029477 | 0.089585 | 0.078017 | 0.55045 | 0.59662 | 0.53183 | 0.60611 | 0.49946 | 0.69598 | 0.2941 | 0.55965 | 0.51775 | 0.48851 | 0.61103 | 0.7005 | 0.52971 | 0.37157 | 122.9702 | -0.062222 | 123.2265 | 123.2079 | 0.23773 | -0.16887 | 0.027642 | 123.0477 | -0.0573 | 123.2357 | 123.1646 | 0.11694 | 0.032162 | -0.13862 | 123.2822 | 123.1755 | 123.3721 | 123.2727 | -0.37424 | 123.2871 | 123.3766 | 123.2058 | 123.1938 | -0.29676
902.2812 | 123.3994 | -122.7081 | 0.65002 | 0.041851 | 0.050193 | 0.0042321 | -0.018198 | -0.046796 | 0.11843 | 0.074154 | 0.14129 | 0.0051213 | -0.029477 | 0.089585 | 0.076949 | 0.54588 | 0.59205 | 0.52725 | 0.60611 | 0.49488 | 0.70513 | 0.29868 | 0.55507 | 0.51317 | 0.49309 | 0.61103 | 0.69592 | 0.52055 | 0.37615 | 123.0068 | -0.043911 | 123.254 | 123.2354 | 0.22857 | -0.15514 | 0.05511 | 123.0843 | -0.038989 | 123.2632 | 123.2012 | 0.11694 | 0.045894 | -0.12947 | 123.3142 | 123.203 | 123.4133 | 123.3002 | -0.35135 | 123.3192 | 123.404 | 123.2287 | 123.2213 | -0.27387
903.3125 | 123.4085 | -122.6944 | 0.69122 | 0.057113 | 0.052329 | 0.0042321 | -0.018198 | -0.045728 | 0.11843 | 0.074154 | 0.14129 | 0.0051213 | -0.029477 | 0.090654 | 0.076949 | 0.55045 | 0.58747 | 0.52267 | 0.60153 | 0.48573 | 0.6914 | 0.2941 | 0.55507 | 0.51775 | 0.48394 | 0.60646 | 0.7005 | 0.52055 | 0.37157 | 122.9885 | -0.089689 | 123.2449 | 123.2171 | 0.22857 | -0.2055 | 0.000175 | 123.066 | -0.084767 | 123.2495 | 123.1783 | 0.11236 | 0.009274 | -0.17067 | 123.2959 | 123.1801 | 123.3858 | 123.2819 | -0.39712 | 123.3009 | 123.3949 | 123.215 | 123.2121 | -0.31965
904.2812 | 123.4406 | -122.7219 | 0.69122 | 0.057113 | 0.049124 | 0.0042321 | -0.019266 | -0.046796 | 0.11629 | 0.043632 | 0.14023 | 0.0051213 | -0.029477 | 0.087449 | 0.078017 | 0.53214 | 0.59662 | 0.51809 | 0.59238 | 0.47199 | 0.68682 | 0.27578 | 0.55049 | 0.5086 | 0.48851 | 0.60646 | 0.68676 | 0.51598 | 0.37615 | 122.9976 | -0.098846 | 123.254 | 123.24 | 0.24231 | -0.21924 | -0.004403 | 123.098 | -0.084767 | 123.2724 | 123.2104 | 0.11236 | -0.004462 | -0.17525 | 123.3142 | 123.1939 | 123.4087 | 123.3185 | -0.41544 | 123.3283 | 123.4086 | 123.2378 | 123.2305 | -0.31507
905.2969 | 123.4634 | -122.6624 | 0.6546 | 0.041851 | 0.051261 | 0.0031631 | -0.020335 | -0.046796 | 0.11736 | 0.058893 | 0.14023 | 0.0051213 | -0.029477 | 0.089585 | 0.076949 | 0.53214 | 0.57831 | 0.51352 | 0.5878 | 0.46283 | 0.68682 | 0.28036 | 0.54591 | 0.5086 | 0.47936 | 0.60646 | 0.68676 | 0.49766 | 0.37157 | 122.9427 | -0.066803 | 123.1945 | 123.1759 | 0.23315 | -0.19177 | 0.032218 | 123.0339 | -0.048146 | 123.2083 | 123.1417 | 0.10779 | 0.032159 | -0.15694 | 123.2502 | 123.1252 | 123.3492 | 123.2407 | -0.37424 | 123.2688 | 123.3491 | 123.16 | 123.1709 | -0.28303
906.2812 | 123.4177 | -122.7402 | 0.6546 | 0.087637 | 0.048056 | 0.0031631 | -0.019266 | -0.047865 | 0.11736 | 0.074154 | 0.14236 | 0.0040533 | -0.030545 | 0.090654 | 0.07588 | 0.53214 | 0.57373 | 0.50894 | 0.5878 | 0.46283 | 0.68224 | 0.2712 | 0.54134 | 0.51317 | 0.48394 | 0.59272 | 0.68676 | 0.49766 | 0.36241 | 123.0114 | -0.066803 | 123.2723 | 123.2491 | 0.23773 | -0.19177 | 0.027639 | 123.1026 | -0.061881 | 123.2815 | 123.2241 | 0.12152 | 0.032159 | -0.15694 | 123.328 | 123.203 | 123.4224 | 123.3139 | -0.3834 | 123.3329 | 123.4269 | 123.2378 | 123.2533 | -0.29219
907.3125 | 123.5321 | -122.6532 | 0.63629 | 0.057113 | 0.051261 | 0.0042321 | -0.018198 | -0.048933 | 0.11736 | 0.058893 | 0.13916 | 0.0051213 | -0.028409 | 0.091722 | 0.074812 | 0.52298 | 0.57373 | 0.50436 | 0.5878 | 0.46741 | 0.67766 | 0.28036 | 0.53218 | 0.49486 | 0.4702 | 0.59272 | 0.6776 | 0.49766 | 0.36241 | 122.9336 | -0.048493 | 123.1762 | 123.1576 | 0.224 | -0.16888 | 0.04137 | 123.0156 | -0.043571 | 123.1854 | 123.1234 | 0.10779 | 0.041312 | -0.13863 | 123.241 | 123.1206 | 123.3309 | 123.2269 | -0.35593 | 123.2459 | 123.3308 | 123.1509 | 123.1481 | -0.27388
908.2812 | 123.436 | -122.6807 | 0.71869 | 0.041851 | 0.050193 | 0.0042321 | -0.019266 | -0.047865 | 0.1195 | 0.058893 | 0.14023 | 0.0051213 | -0.029477 | 0.089585 | 0.07588 | 0.51841 | 0.57373 | 0.50436 | 0.57864 | 0.47199 | 0.67308 | 0.27578 | 0.53218 | 0.50402 | 0.4702 | 0.58814 | 0.67302 | 0.49308 | 0.35784 | 122.9564 | -0.14005 | 123.1991 | 123.185 | 0.22857 | -0.2467 | -0.045605 | 123.0385 | -0.13055 | 123.2128 | 123.1509 | 0.11236 | -0.045664 | -0.22561 | 123.2593 | 123.1527 | 123.3537 | 123.2544 | -0.44291 | 123.2688 | 123.3537 | 123.1737 | 123.1847 | -0.36085
909.3125 | 123.4726 | -122.6807 | 0.62714 | 0.041851 | 0.050193 | 0.0053001 | -0.020335 | -0.045728 | 0.11843 | 0.074154 | 0.14129 | 0.0040533 | -0.029477 | 0.089585 | 0.076949 | 0.51841 | 0.56458 | 0.50436 | 0.57864 | 0.45825 | 0.66851 | 0.27578 | 0.52302 | 0.49486 | 0.4702 | 0.58356 | 0.66845 | 0.49308 | 0.35326 | 122.9564 | -0.048494 | 123.1991 | 123.185 | 0.22857 | -0.16889 | 0.041369 | 123.0339 | -0.043572 | 123.2037 | 123.1509 | 0.11694 | 0.041311 | -0.13405 | 123.2593 | 123.1389 | 123.3492 | 123.2452 | -0.35135 | 123.2642 | 123.3491 | 123.1737 | 123.1755 | -0.27388
910.2812 | 123.4177 | -122.7127 | 0.61798 | 0.057113 | 0.049124 | 0.0042321 | -0.018198 | -0.045728 | 0.11736 | 0.043632 | 0.14236 | 0.0051213 | -0.029477 | 0.087449 | 0.07588 | 0.50925 | 0.56 | 0.49978 | 0.56949 | 0.45825 | 0.66393 | 0.26663 | 0.52302 | 0.49028 | 0.45646 | 0.57899 | 0.65929 | 0.48392 | 0.34868 | 122.9793 | -0.048495 | 123.222 | 123.2125 | 0.23316 | -0.15973 | 0.045946 | 123.0614 | -0.038995 | 123.2357 | 123.1692 | 0.10778 | 0.041308 | -0.13406 | 123.2822 | 123.171 | 123.3766 | 123.2727 | -0.35136 | 123.2917 | 123.372 | 123.1966 | 123.203 | -0.2693
911.3125 | 123.5184 | -122.6807 | 0.6134 | 0.057113 | 0.046987 | 0.0042321 | -0.019266 | -0.045728 | 0.1195 | 0.043632 | 0.14236 | 0.0061893 | -0.029477 | 0.089585 | 0.07588 | 0.50467 | 0.56 | 0.48147 | 0.55575 | 0.45367 | 0.66393 | 0.26205 | 0.51386 | 0.48112 | 0.46562 | 0.57899 | 0.65929 | 0.47935 | 0.34868 | 122.9427 | -0.057653 | 123.1853 | 123.1621 | 0.21942 | -0.15973 | 0.050524 | 123.0293 | -0.034417 | 123.1945 | 123.1463 | 0.11694 | 0.045886 | -0.13406 | 123.2364 | 123.1343 | 123.3446 | 123.2407 | -0.35136 | 123.2596 | 123.34 | 123.16 | 123.1618 | -0.26472
912.2812 | 123.3994 | -122.7264 | 0.64545 | 0.041851 | 0.050193 | 0.0053001 | -0.018198 | -0.046796 | 0.11843 | 0.058893 | 0.14236 | 0.0040533 | -0.029477 | 0.088517 | 0.074812 | 0.50925 | 0.56 | 0.49062 | 0.56491 | 0.44909 | 0.66393 | 0.2712 | 0.51386 | 0.48112 | 0.45189 | 0.57899 | 0.65929 | 0.47935 | 0.34868 | 122.9976 | -0.08054 | 123.2357 | 123.2171 | 0.21942 | -0.19635 | 0.01848 | 123.0751 | -0.066461 | 123.2403 | 123.1783 | 0.10321 | 0.013842 | -0.1661 | 123.2913 | 123.1755 | 123.3904 | 123.2864 | -0.37424 | 123.3054 | 123.3857 | 123.2058 | 123.2076 | -0.29677
913.3125 | 123.5367 | -122.6761 | 0.61798 | 0.041851 | 0.048056 | 0.0053001 | -0.019266 | -0.047865 | 0.11843 | 0.074154 | 0.13916 | 0.0051213 | -0.027341 | 0.089585 | 0.078017 | 0.50925 | 0.55084 | 0.48605 | 0.55117 | 0.44909 | 0.65477 | 0.26663 | 0.50471 | 0.47654 | 0.44731 | 0.57899 | 0.65013 | 0.48392 | 0.33494 | 122.9427 | -0.066809 | 123.1853 | 123.1621 | 0.21942 | -0.16889 | 0.036788 | 123.011 | -0.038995 | 123.1808 | 123.1234 | 0.11236 | 0.032151 | -0.13406 | 123.2273 | 123.1252 | 123.3309 | 123.2269 | -0.35136 | 123.2551 | 123.3262 | 123.16 | 123.1526 | -0.28304
914.2812 | 123.4085 | -122.7676 | 0.6134 | 0.072375 | 0.049124 | 0.0042321 | -0.017129 | -0.048933 | 0.11736 | 0.089415 | 0.14236 | 0.0040533 | -0.028409 | 0.088517 | 0.074812 | 0.50467 | 0.55542 | 0.49062 | 0.56491 | 0.45367 | 0.65477 | 0.2712 | 0.50471 | 0.47197 | 0.45646 | 0.56067 | 0.65471 | 0.46561 | 0.33494 | 123.0388 | -0.048496 | 123.2723 | 123.2583 | 0.21942 | -0.15973 | 0.041366 | 123.1026 | -0.052731 | 123.2723 | 123.2241 | 0.12152 | 0.041308 | -0.14779 | 123.3325 | 123.2213 | 123.4224 | 123.3231 | -0.3422 | 123.3283 | 123.4224 | 123.2332 | 123.2396 | -0.27846
915.3125 | 123.4772 | -122.6898 | 0.59967 | 0.057113 | 0.049124 | 0.0031631 | -0.019266 | -0.047865 | 0.11843 | 0.074154 | 0.14023 | 0.0051213 | -0.030545 | 0.089585 | 0.073744 | 0.49551 | 0.55084 | 0.48605 | 0.54659 | 0.43536 | 0.64561 | 0.25747 | 0.50471 | 0.47197 | 0.44273 | 0.56525 | 0.65013 | 0.46561 | 0.33036 | 122.9473 | -0.053076 | 123.1853 | 123.1759 | 0.22858 | -0.16431 | 0.045942 | 123.0202 | -0.03442 | 123.1945 | 123.1325 | 0.11236 | 0.050462 | -0.13406 | 123.2364 | 123.1252 | 123.3354 | 123.2407 | -0.3422 | 123.2551 | 123.34 | 123.1554 | 123.1618 | -0.26931
916.2812 | 123.4177 | -122.7402 | 0.62714 | 0.057113 | 0.049124 | 0.0053001 | -0.019266 | -0.046796 | 0.11843 | 0.058893 | 0.14129 | 0.0029843 | -0.028409 | 0.088517 | 0.078017 | 0.49094 | 0.55084 | 0.48147 | 0.54659 | 0.43078 | 0.64561 | 0.25289 | 0.50471 | 0.48112 | 0.45646 | 0.55151 | 0.64555 | 0.47019 | 0.32578 | 122.9931 | -0.080542 | 123.2311 | 123.2216 | 0.22858 | -0.19636 | 0.018476 | 123.066 | -0.075621 | 123.2449 | 123.1966 | 0.13068 | 0.018418 | -0.15695 | 123.2868 | 123.171 | 123.3858 | 123.291 | -0.37425 | 123.2917 | 123.3857 | 123.2104 | 123.2213 | -0.30135
917.3125 | 123.4863 | -122.7036 | 0.60883 | 0.057113 | 0.049124 | 0.0042321 | -0.019266 | -0.045728 | 0.1195 | 0.043632 | 0.14129 | 0.0051213 | -0.026272 | 0.090654 | 0.076949 | 0.48636 | 0.5371 | 0.47231 | 0.54659 | 0.43536 | 0.63645 | 0.25747 | 0.48639 | 0.46739 | 0.43357 | 0.55609 | 0.65471 | 0.46103 | 0.32578 | 122.961 | -0.062232 | 123.1899 | 123.1759 | 0.21484 | -0.17347 | 0.027629 | 123.0293 | -0.052733 | 123.1899 | 123.1371 | 0.10779 | 0.045885 | -0.14779 | 123.2501 | 123.1389 | 123.34 | 123.2407 | -0.35136 | 123.2596 | 123.3583 | 123.1646 | 123.1709 | -0.28304
918.2812 | 123.3902 | -122.7676 | 0.62714 | 0.072375 | 0.048056 | 0.0042321 | -0.019266 | -0.047865 | 0.1195 | 0.074154 | 0.14343 | 0.0040533 | -0.028409 | 0.088517 | 0.07588 | 0.49094 | 0.5371 | 0.46773 | 0.55117 | 0.43078 | 0.63645 | 0.2712 | 0.50471 | 0.46739 | 0.43357 | 0.55609 | 0.64097 | 0.46561 | 0.32121 | 123.0388 | -0.075964 | 123.2586 | 123.2354 | 0.19653 | -0.19636 | 0.009319 | 123.0888 | -0.071043 | 123.2723 | 123.2012 | 0.11236 | 0.013839 | -0.16153 | 123.3188 | 123.1984 | 123.4041 | 123.3047 | -0.35593 | 123.3237 | 123.4086 | 123.2332 | 123.235 | -0.30593
919.2969 | 123.4085 | -122.7676 | 0.59967 | 0.041851 | 0.050193 | 0.0042321 | -0.019266 | -0.045728 | 0.11736 | 0.043632 | 0.14023 | 0.0040533 | -0.028409 | 0.089585 | 0.076949 | 0.48178 | 0.54168 | 0.46315 | 0.54202 | 0.4262 | 0.63188 | 0.24831 | 0.49555 | 0.46281 | 0.43815 | 0.55151 | 0.63182 | 0.46103 | 0.33036 | 123.0159 | -0.057655 | 123.2494 | 123.2308 | 0.21484 | -0.17347 | 0.032206 | 123.098 | -0.048155 | 123.2632 | 123.2058 | 0.10779 | 0.032148 | -0.13864 | 123.3097 | 123.1938 | 123.3995 | 123.3093 | -0.35136 | 123.3192 | 123.3995 | 123.2287 | 123.2304 | -0.26931
920.2812 | 123.3948 | -122.7676 | 0.62714 | 0.057113 | 0.048056 | 0.0031631 | -0.018198 | -0.045728 | 0.11736 | 0.074154 | 0.14129 | 0.0040533 | -0.030545 | 0.090654 | 0.076949 | 0.48636 | 0.52795 | 0.47231 | 0.53744 | 0.43078 | 0.63645 | 0.25289 | 0.48639 | 0.45823 | 0.43357 | 0.53778 | 0.64097 | 0.45645 | 0.32578 | 123.0205 | -0.089699 | 123.254 | 123.2399 | 0.21942 | -0.19636 | 0.009319 | 123.0934 | -0.089357 | 123.254 | 123.2012 | 0.10779 | 0.013839 | -0.17068 | 123.3051 | 123.1984 | 123.4041 | 123.2956 | -0.37425 | 123.3054 | 123.4086 | 123.2241 | 123.2259 | -0.30135
921.3125 | 123.4726 | -122.7493 | 0.59967 | 0.057113 | 0.049124 | 0.0042321 | -0.018198 | -0.045728 | 0.11629 | 0.089415 | 0.14023 | 0.0061893 | -0.029477 | 0.090654 | 0.07588 | 0.4772 | 0.53252 | 0.46315 | 0.52828 | 0.40788 | 0.6273 | 0.24373 | 0.49097 | 0.45823 | 0.42899 | 0.54694 | 0.6364 | 0.45188 | 0.31663 | 122.9931 | -0.07139 | 123.2265 | 123.2125 | 0.21942 | -0.19179 | 0.027628 | 123.066 | -0.052734 | 123.2403 | 123.1783 | 0.11236 | 0.036726 | -0.1478 | 123.2776 | 123.1572 | 123.3766 | 123.2819 | -0.35594 | 123.2963 | 123.3857 | 123.2012 | 123.2076 | -0.28304
922.2812 | 123.3902 | -122.7631 | 0.62714 | 0.072375 | 0.048056 | 0.0042321 | -0.019266 | -0.047865 | 0.11736 | 0.058893 | 0.14023 | 0.0051213 | -0.029477 | 0.090654 | 0.07588 | 0.47262 | 0.52795 | 0.45858 | 0.52828 | 0.41246 | 0.63188 | 0.24831 | 0.48639 | 0.45365 | 0.42441 | 0.54694 | 0.62724 | 0.45188 | 0.31663 | 123.0114 | -0.098856 | 123.2357 | 123.2216 | 0.21027 | -0.21467 | 0.00474 | 123.0797 | -0.0802 | 123.2495 | 123.1875 | 0.10779 | 0.000103 | -0.17526 | 123.2913 | 123.1755 | 123.3949 | 123.291 | -0.37883 | 123.31 | 123.3903 | 123.2149 | 123.2167 | -0.31051
923.2969 | 123.4268 | -122.7768 | 0.5722 | 0.057113 | 0.046987 | 0.0031631 | -0.019266 | -0.045728 | 0.11736 | 0.058893 | 0.14023 | 0.0040533 | -0.029477 | 0.089585 | 0.07588 | 0.4772 | 0.52337 | 0.45858 | 0.53286 | 0.42162 | 0.62272 | 0.24373 | 0.47723 | 0.44907 | 0.42441 | 0.53778 | 0.63182 | 0.45188 | 0.30747 | 123.0205 | -0.039347 | 123.254 | 123.2354 | 0.21484 | -0.15058 | 0.050514 | 123.0843 | -0.034426 | 123.254 | 123.2012 | 0.11694 | 0.059613 | -0.12033 | 123.3097 | 123.1984 | 123.3995 | 123.3002 | -0.32847 | 123.3146 | 123.4086 | 123.2287 | 123.2259 | -0.26474
924.2812 | 123.3994 | -122.7997 | 0.61798 | 0.057113 | 0.048056 | 0.0053001 | -0.020335 | -0.045728 | 0.11736 | 0.074154 | 0.13916 | 0.0051213 | -0.028409 | 0.089585 | 0.07588 | 0.47262 | 0.51879 | 0.44942 | 0.53286 | 0.41704 | 0.61356 | 0.25289 | 0.47265 | 0.44907 | 0.41526 | 0.54236 | 0.62266 | 0.44272 | 0.31205 | 123.0526 | -0.085123 | 123.2723 | 123.2491 | 0.19653 | -0.20094 | -0.004419 | 123.1117 | -0.075623 | 123.2723 | 123.2149 | 0.10321 | 0.00468 | -0.17526 | 123.3325 | 123.2167 | 123.4132 | 123.3185 | -0.36509 | 123.342 | 123.4223 | 123.2424 | 123.2488 | -0.30593
925.3125 | 123.5138 | -122.7356 | 0.54016 | 0.072375 | 0.048056 | 0.0031631 | -0.020335 | -0.045728 | 0.11843 | 0.074154 | 0.14023 | 0.0040533 | -0.030545 | 0.088517 | 0.07588 | 0.47262 | 0.51421 | 0.44484 | 0.5237 | 0.38957 | 0.61814 | 0.22542 | 0.4635 | 0.44449 | 0.41526 | 0.5332 | 0.61808 | 0.43356 | 0.30747 | 122.961 | -0.016459 | 123.2082 | 123.1804 | 0.21943 | -0.15059 | 0.07798 | 123.0431 | -0.00696 | 123.1991 | 123.1509 | 0.10779 | 0.077921 | -0.1066 | 123.2593 | 123.1252 | 123.3537 | 123.2498 | -0.31475 | 123.2688 | 123.3537 | 123.1692 | 123.1801 | -0.23269
926.2812 | 123.5046 | -122.7539 | 0.57678 | 0.041851 | 0.048056 | 0.0053001 | -0.018198 | -0.047865 | 0.11629 | 0.074154 | 0.13916 | 0.0061893 | -0.029477 | 0.090654 | 0.076949 | 0.46804 | 0.51421 | 0.44942 | 0.5237 | 0.41704 | 0.6273 | 0.23915 | 0.46808 | 0.44449 | 0.41984 | 0.52862 | 0.6135 | 0.44272 | 0.29373 | 122.9931 | -0.05308 | 123.2219 | 123.2033 | 0.21027 | -0.15974 | 0.050516 | 123.0476 | -0.04816 | 123.222 | 123.1737 | 0.1261 | 0.036721 | -0.13406 | 123.2776 | 123.1709 | 123.3812 | 123.2681 | -0.33763 | 123.2825 | 123.3674 | 123.1966 | 123.1984 | -0.28305
927.2969 | 123.4863 | -122.731 | 0.57678 | 0.057113 | 0.048056 | 0.0042321 | -0.020335 | -0.046796 | 0.11843 | 0.058893 | 0.14023 | 0.0051213 | -0.028409 | 0.090654 | 0.074812 | 0.45889 | 0.50505 | 0.44484 | 0.51455 | 0.40788 | 0.61814 | 0.23457 | 0.46808 | 0.44449 | 0.41068 | 0.52862 | 0.61808 | 0.43814 | 0.30747 | 122.9656 | -0.062237 | 123.1899 | 123.1759 | 0.21027 | -0.1689 | 0.041359 | 123.0385 | -0.04816 | 123.1991 | 123.1417 | 0.10321 | 0.0413 | -0.13864 | 123.2456 | 123.1389 | 123.3492 | 123.2361 | -0.34221 | 123.2596 | 123.3491 | 123.1692 | 123.1755 | -0.26931
928.2812 | 123.4909 | -122.7493 | 0.56305 | 0.087637 | 0.046987 | 0.0031631 | -0.020335 | -0.046796 | 0.11629 | 0.058893 | 0.14129 | 0.0040533 | -0.029477 | 0.090654 | 0.076949 | 0.45889 | 0.50505 | 0.44026 | 0.51455 | 0.4033 | 0.60898 | 0.22999 | 0.46808 | 0.43534 | 0.4061 | 0.52404 | 0.6135 | 0.42898 | 0.29831 | 122.9793 | -0.048504 | 123.2082 | 123.1896 | 0.21027 | -0.15975 | 0.045934 | 123.0476 | -0.039005 | 123.2174 | 123.1554 | 0.10779 | 0.050454 | -0.13407 | 123.2639 | 123.1526 | 123.3583 | 123.2544 | -0.33305 | 123.2734 | 123.3628 | 123.1783 | 123.1847 | -0.26474
929.3125 | 123.436 | -122.7951 | 0.55847 | 0.057113 | 0.049124 | 0.0042321 | -0.019266 | -0.046796 | 0.11629 | 0.074154 | 0.14236 | 0.0061893 | -0.030545 | 0.090654 | 0.074812 | 0.45889 | 0.50047 | 0.44026 | 0.50081 | 0.4033 | 0.61356 | 0.23915 | 0.4635 | 0.44907 | 0.41526 | 0.52862 | 0.6135 | 0.44272 | 0.30289 | 123.0343 | -0.057662 | 123.254 | 123.2354 | 0.20111 | -0.15517 | 0.05509 | 123.098 | -0.02985 | 123.2586 | 123.2104 | 0.11236 | 0.055031 | -0.11575 | 123.2959 | 123.1984 | 123.4087 | 123.2956 | -0.31932 | 123.3237 | 123.4086 | 123.2378 | 123.2442 | -0.25558
930.2812 | 123.468 | -122.7768 | 0.59509 | 0.072375 | 0.049124 | 0.0031631 | -0.019266 | -0.046796 | 0.11736 | 0.089415 | 0.14129 | 0.0051213 | -0.030545 | 0.093859 | 0.07588 | 0.44973 | 0.4959 | 0.43568 | 0.50997 | 0.39872 | 0.59983 | 0.22542 | 0.47265 | 0.43076 | 0.41068 | 0.50573 | 0.60435 | 0.43356 | 0.28915 | 123.0022 | -0.085127 | 123.2265 | 123.2125 | 0.21027 | -0.19637 | 0.004733 | 123.0659 | -0.089363 | 123.2494 | 123.1875 | 0.12152 | 0.009253 | -0.16153 | 123.2868 | 123.1755 | 123.3766 | 123.2727 | -0.36968 | 123.2825 | 123.3811 | 123.2104 | 123.2076 | -0.30594
931.3125 | 123.5367 | -122.7722 | 0.51727 | 0.041851 | 0.049124 | 0.0031631 | -0.020335 | -0.045728 | 0.1195 | 0.074154 | 0.14023 | 0.0051213 | -0.029477 | 0.091722 | 0.076949 | 0.44973 | 0.49132 | 0.42653 | 0.50081 | 0.38499 | 0.59983 | 0.22542 | 0.45434 | 0.42618 | 0.40152 | 0.51031 | 0.60435 | 0.41525 | 0.29373 | 122.9976 | -0.016463 | 123.2219 | 123.1987 | 0.20111 | -0.13228 | 0.082553 | 123.066 | -0.006965 | 123.2266 | 123.1737 | 0.10779 | 0.087073 | -0.10203 | 123.273 | 123.1572 | 123.372 | 123.2635 | -0.29186 | 123.2825 | 123.3766 | 123.1875 | 123.1984 | -0.22354
932.2812 | 123.5275 | -122.7997 | 0.56305 | 0.057113 | 0.046987 | 0.0020951 | -0.019266 | -0.047865 | 0.11843 | 0.074154 | 0.14023 | 0.0051213 | -0.029477 | 0.090654 | 0.074812 | 0.44973 | 0.4959 | 0.42195 | 0.49623 | 0.38499 | 0.59525 | 0.22542 | 0.45434 | 0.4216 | 0.39694 | 0.50573 | 0.59519 | 0.4244 | 0.28 | 123.0251 | -0.066818 | 123.2494 | 123.2216 | 0.19653 | -0.17806 | 0.032199 | 123.0797 | -0.057319 | 123.254 | 123.1966 | 0.11694 | 0.03214 | -0.13865 | 123.2959 | 123.1847 | 123.3949 | 123.2956 | -0.33763 | 123.3054 | 123.3949 | 123.2241 | 123.2213 | -0.28305
933.3125 | 123.4406 | -122.7859 | 0.55847 | 0.041851 | 0.045919 | 0.0031631 | -0.019266 | -0.046796 | 0.11736 | 0.058893 | 0.14023 | 0.0051213 | -0.028409 | 0.091722 | 0.07588 | 0.44515 | 0.49132 | 0.42653 | 0.50539 | 0.38499 | 0.59983 | 0.21626 | 0.45892 | 0.42618 | 0.39694 | 0.51031 | 0.59977 | 0.41983 | 0.28458 | 123.0022 | -0.053084 | 123.2311 | 123.2125 | 0.21027 | -0.17348 | 0.041354 | 123.0705 | -0.048164 | 123.2449 | 123.1829 | 0.11237 | 0.041296 | -0.13865 | 123.2913 | 123.1709 | 123.3858 | 123.2773 | -0.34221 | 123.2963 | 123.3857 | 123.2058 | 123.2121 | -0.2739
934.2812 | 123.4177 | -122.8134 | 0.56763 | 0.057113 | 0.045919 | 0.0042321 | -0.019266 | -0.046796 | 0.11629 | 0.074154 | 0.14023 | 0.0051213 | -0.028409 | 0.091722 | 0.07588 | 0.44057 | 0.48674 | 0.42195 | 0.49623 | 0.38957 | 0.58609 | 0.22542 | 0.45434 | 0.42618 | 0.39694 | 0.50115 | 0.59977 | 0.41983 | 0.28 | 123.0388 | -0.071396 | 123.254 | 123.2354 | 0.19653 | -0.17806 | 0.018463 | 123.0934 | -0.066476 | 123.2678 | 123.2104 | 0.11694 | 0.032141 | -0.1478 | 123.3096 | 123.203 | 123.3995 | 123.3002 | -0.34221 | 123.3146 | 123.4132 | 123.2332 | 123.2396 | -0.28763
935.3125 | 123.436 | -122.8043 | 0.56305 | 0.057113 | 0.045919 | 0.0020951 | -0.019266 | -0.046796 | 0.11843 | 0.058893 | 0.14129 | 0.0029843 | -0.027341 | 0.090654 | 0.07588 | 0.43599 | 0.48216 | 0.42195 | 0.49623 | 0.38957 | 0.59067 | 0.22084 | 0.4406 | 0.42618 | 0.39694 | 0.50573 | 0.58603 | 0.40609 | 0.27542 | 123.0251 | -0.066818 | 123.2403 | 123.2262 | 0.20111 | -0.17348 | 0.02762 | 123.0797 | -0.057319 | 123.2449 | 123.2012 | 0.12152 | 0.022983 | -0.15696 | 123.3005 | 123.1938 | 123.3949 | 123.2864 | -0.34221 | 123.31 | 123.3903 | 123.2103 | 123.2304 | -0.28763
936.2812 | 123.5504 | -122.7814 | 0.53101 | 0.041851 | 0.048056 | 0.0020951 | -0.018198 | -0.045728 | 0.11736 | 0.074154 | 0.14129 | 0.0029843 | -0.029477 | 0.091722 | 0.07588 | 0.43599 | 0.47758 | 0.42195 | 0.48707 | 0.38041 | 0.58609 | 0.21626 | 0.44518 | 0.41702 | 0.38778 | 0.50115 | 0.59519 | 0.41525 | 0.28 | 122.9976 | -0.043931 | 123.2174 | 123.2033 | 0.20569 | -0.1506 | 0.055084 | 123.0614 | -0.029855 | 123.2266 | 123.1692 | 0.10779 | 0.064183 | -0.11576 | 123.2684 | 123.1618 | 123.3675 | 123.259 | -0.31475 | 123.2825 | 123.3766 | 123.1966 | 123.1984 | -0.25101
937.3125 | 123.5138 | -122.7448 | 0.54016 | 0.057113 | 0.046987 | 0.0020951 | -0.020335 | -0.046796 | 0.1195 | 0.058893 | 0.14129 | 0.0040533 | -0.030545 | 0.091722 | 0.07588 | 0.43142 | 0.473 | 0.41737 | 0.4825 | 0.38041 | 0.58151 | 0.22084 | 0.43602 | 0.41702 | 0.38778 | 0.50115 | 0.57688 | 0.40151 | 0.27542 | 122.9656 | -0.057665 | 123.1762 | 123.1621 | 0.19653 | -0.15975 | 0.041351 | 123.0202 | -0.03901 | 123.1808 | 123.1325 | 0.11237 | 0.036714 | -0.13865 | 123.2272 | 123.1252 | 123.3263 | 123.2178 | -0.31932 | 123.2459 | 123.3216 | 123.1463 | 123.1618 | -0.26474
938.2812 | 123.5138 | -122.7905 | 0.55389 | 0.041851 | 0.045919 | 0.0031631 | -0.018198 | -0.045728 | 0.11522 | 0.074154 | 0.13916 | 0.0040533 | -0.031614 | 0.091722 | 0.074812 | 0.42684 | 0.48216 | 0.41737 | 0.49165 | 0.37583 | 0.57235 | 0.21168 | 0.43602 | 0.41702 | 0.38778 | 0.49657 | 0.58145 | 0.40151 | 0.27542 | 123.0022 | -0.062241 | 123.2174 | 123.2079 | 0.20569 | -0.17806 | 0.018461 | 123.0659 | -0.057321 | 123.2266 | 123.1783 | 0.11237 | 0.027559 | -0.15238 | 123.2822 | 123.1664 | 123.3629 | 123.2727 | -0.34222 | 123.2871 | 123.372 | 123.192 | 123.2075 | -0.27848
939.3125 | 123.468 | -122.7951 | 0.55389 | 0.041851 | 0.045919 | 0.0042321 | -0.019266 | -0.045728 | 0.1195 | 0.074154 | 0.13809 | 0.00084833 | -0.029477 | 0.093859 | 0.078017 | 0.43599 | 0.47758 | 0.40821 | 0.4825 | 0.36667 | 0.58151 | 0.21168 | 0.42687 | 0.41244 | 0.38778 | 0.49657 | 0.57688 | 0.39693 | 0.27084 | 123.0068 | -0.071398 | 123.2311 | 123.2033 | 0.19654 | -0.18722 | 0.027618 | 123.0659 | -0.057321 | 123.222 | 123.1829 | 0.11695 | 0.022981 | -0.15696 | 123.2776 | 123.1618 | 123.3766 | 123.2727 | -0.34222 | 123.2917 | 123.372 | 123.192 | 123.2075 | -0.28306
940.2812 | 123.4909 | -122.7814 | 0.54016 | 0.057113 | 0.046987 | 0.0042321 | -0.019266 | -0.047865 | 0.11629 | 0.058893 | 0.14129 | 0.0040533 | -0.029477 | 0.089585 | 0.07588 | 0.42226 | 0.46842 | 0.40364 | 0.4825 | 0.36667 | 0.57693 | 0.2071 | 0.43602 | 0.41702 | 0.38321 | 0.49657 | 0.58603 | 0.40609 | 0.26168 | 122.9885 | -0.057665 | 123.2036 | 123.185 | 0.19654 | -0.17349 | 0.036772 | 123.0431 | -0.043588 | 123.2174 | 123.1646 | 0.12152 | 0.045871 | -0.13407 | 123.2639 | 123.148 | 123.3583 | 123.2498 | -0.33306 | 123.2779 | 123.3674 | 123.1875 | 123.1984 | -0.27848
941.3125 | 123.3994 | -122.8226 | 0.55389 | 0.057113 | 0.046987 | 0.0031631 | -0.020335 | -0.047865 | 0.11522 | 0.074154 | 0.14023 | 0.0051213 | -0.029477 | 0.09279 | 0.076949 | 0.43142 | 0.46842 | 0.41279 | 0.4825 | 0.36667 | 0.58151 | 0.19794 | 0.42687 | 0.41702 | 0.37863 | 0.48742 | 0.57688 | 0.40609 | 0.27084 | 123.0205 | -0.071398 | 123.254 | 123.2354 | 0.21485 | -0.18722 | 0.027618 | 123.0934 | -0.066478 | 123.2494 | 123.2012 | 0.10779 | 0.022981 | -0.14781 | 123.3051 | 123.1892 | 123.4041 | 123.291 | -0.35595 | 123.31 | 123.3994 | 123.2287 | 123.2396 | -0.28306
942.2812 | 123.5458 | -122.937 | 0.51727 | 0.057113 | 0.049124 | 0.0042321 | -0.019266 | -0.046796 | 0.11843 | 0.058893 | 0.13916 | 0.0040533 | -0.031614 | 0.090654 | 0.074812 | 0.43142 | 0.473 | 0.41279 | 0.49165 | 0.35752 | 0.57693 | 0.21168 | 0.4406 | 0.41244 | 0.38321 | 0.49199 | 0.57688 | 0.40151 | 0.27542 | 123.1487 | -0.02562 | 123.3684 | 123.3498 | 0.20111 | -0.15976 | 0.05966 | 123.2124 | -0.025279 | 123.3776 | 123.3202 | 0.10779 | 0.059602 | -0.11576 | 123.4287 | 123.2945 | 123.5139 | 123.41 | -0.30559 | 123.429 | 123.5139 | 123.3385 | 123.3495 | -0.24185
943.2969 | 123.4085 | -122.8134 | 0.56763 | 0.057113 | 0.045919 | 0.0042321 | -0.019266 | -0.046796 | 0.1195 | 0.089415 | 0.13809 | 0.0051213 | -0.029477 | 0.091722 | 0.07588 | 0.42684 | 0.47758 | 0.41737 | 0.4825 | 0.38041 | 0.57693 | 0.21168 | 0.43602 | 0.41702 | 0.38321 | 0.49199 | 0.57688 | 0.40609 | 0.27542 | 123.0251 | -0.085131 | 123.2403 | 123.2308 | 0.20569 | -0.18722 | 0.009306 | 123.0888 | -0.075633 | 123.2494 | 123.1966 | 0.10779 | 0.009248 | -0.16154 | 123.2959 | 123.1938 | 123.3903 | 123.291 | -0.35595 | 123.3054 | 123.3903 | 123.2195 | 123.2304 | -0.29221
944.2812 | 123.4131 | -122.8271 | 0.54016 | 0.057113 | 0.045919 | 0.0031631 | -0.020335 | -0.046796 | 0.11736 | 0.074154 | 0.13809 | 0.0051213 | -0.029477 | 0.09279 | 0.076949 | 0.42684 | 0.47758 | 0.41279 | 0.47792 | 0.37125 | 0.57235 | 0.2071 | 0.43145 | 0.41244 | 0.38321 | 0.49657 | 0.57688 | 0.40609 | 0.27084 | 123.0342 | -0.062243 | 123.254 | 123.2399 | 0.20569 | -0.16891 | 0.032194 | 123.098 | -0.043588 | 123.2586 | 123.2104 | 0.11237 | 0.036714 | -0.13407 | 123.3051 | 123.1984 | 123.3995 | 123.3047 | -0.33306 | 123.3237 | 123.404 | 123.2332 | 123.2396 | -0.26932
945.3125 | 123.5001 | -122.7905 | 0.52185 | 0.057113 | 0.044851 | 0.0020951 | -0.021403 | -0.048933 | 0.11843 | 0.074154 | 0.13916 | 0.0051213 | -0.028409 | 0.091722 | 0.073744 | 0.42226 | 0.46842 | 0.40364 | 0.4825 | 0.38499 | 0.57235 | 0.2071 | 0.43602 | 0.41244 | 0.37863 | 0.48742 | 0.57688 | 0.39693 | 0.28 | 122.9976 | -0.039355 | 123.2128 | 123.1942 | 0.19654 | -0.13686 | 0.050504 | 123.0705 | -0.034435 | 123.2266 | 123.1692 | 0.098629 | 0.055024 | -0.12492 | 123.273 | 123.1755 | 123.3629 | 123.259 | -0.31475 | 123.2779 | 123.3674 | 123.1875 | 123.203 | -0.24185
946.2812 | 123.4818 | -122.7814 | 0.51727 | 0.057113 | 0.045919 | 0.0020951 | -0.019266 | -0.046796 | 0.11736 | 0.058893 | 0.14023 | 0.0051213 | -0.028409 | 0.093859 | 0.078017 | 0.41768 | 0.46842 | 0.40364 | 0.47792 | 0.36667 | 0.56778 | 0.2071 | 0.42687 | 0.41702 | 0.37405 | 0.48284 | 0.5723 | 0.38777 | 0.27084 | 122.9885 | -0.039355 | 123.1991 | 123.185 | 0.19654 | -0.1506 | 0.050503 | 123.0522 | -0.034436 | 123.2082 | 123.1554 | 0.10321 | 0.055023 | -0.1295 | 123.2593 | 123.148 | 123.3491 | 123.2498 | -0.31017 | 123.2642 | 123.3537 | 123.1691 | 123.1984 | -0.24643
947.3125 | 123.4589 | -122.8363 | 0.54474 | 0.041851 | 0.044851 | 0.0031631 | -0.018198 | -0.046796 | 0.11736 | 0.043632 | 0.14023 | 0.0029843 | -0.029477 | 0.09279 | 0.076949 | 0.41768 | 0.46385 | 0.40821 | 0.47334 | 0.36209 | 0.57235 | 0.20252 | 0.42687 | 0.41702 | 0.37863 | 0.48742 | 0.5723 | 0.40609 | 0.27084 | 123.0388 | -0.0714 | 123.254 | 123.2445 | 0.20569 | -0.18264 | 0.027616 | 123.1071 | -0.057323 | 123.2632 | 123.2149 | 0.10779 | 0.027557 | -0.13865 | 123.3096 | 123.1984 | 123.4087 | 123.3001 | -0.34222 | 123.3237 | 123.4086 | 123.2424 | 123.2533 | -0.2739
948.2812 | 123.4726 | -122.7722 | 0.49896 | 0.057113 | 0.045919 | 0.0042321 | -0.020335 | -0.046796 | 0.11843 | 0.074154 | 0.14023 | 0.0051213 | -0.028409 | 0.09279 | 0.074812 | 0.41768 | 0.46385 | 0.39448 | 0.46876 | 0.35752 | 0.5632 | 0.19794 | 0.42687 | 0.41244 | 0.37863 | 0.48284 | 0.56772 | 0.38777 | 0.26168 | 122.9702 | -0.030201 | 123.1899 | 123.1667 | 0.19654 | -0.14145 | 0.064235 | 123.0339 | -0.016125 | 123.1991 | 123.1508 | 0.11695 | 0.068755 | -0.11119 | 123.241 | 123.1297 | 123.3354 | 123.2361 | -0.30102 | 123.2551 | 123.3399 | 123.16 | 123.1847 | -0.23728
949.2812 | 123.4131 | -122.8363 | 0.54932 | 0.072375 | 0.044851 | 0.0042321 | -0.019266 | -0.047865 | 0.11736 | 0.058893 | 0.13916 | 0.0051213 | -0.029477 | 0.091722 | 0.07588 | 0.42226 | 0.45927 | 0.39906 | 0.46876 | 0.35294 | 0.5632 | 0.20252 | 0.42229 | 0.41244 | 0.36489 | 0.48284 | 0.56772 | 0.39235 | 0.26626 | 123.0388 | -0.080555 | 123.2586 | 123.2354 | 0.19654 | -0.19638 | 0.013881 | 123.1026 | -0.066479 | 123.2586 | 123.2012 | 0.09863 | 0.018401 | -0.15696 | 123.3051 | 123.1892 | 123.3995 | 123.2956 | -0.3468 | 123.3191 | 123.404 | 123.2287 | 123.2487 | -0.28306
950.2812 | 123.4909 | -122.7997 | 0.52643 | 0.087637 | 0.043782 | 0.0031631 | -0.020335 | -0.045728 | 0.12056 | 0.058893 | 0.13916 | 0.0029843 | -0.028409 | 0.091722 | 0.07588 | 0.4131 | 0.45927 | 0.39448 | 0.46876 | 0.34836 | 0.56778 | 0.19336 | 0.42229 | 0.41244 | 0.37405 | 0.48284 | 0.56314 | 0.38777 | 0.26168 | 122.993 | -0.057667 | 123.2128 | 123.1942 | 0.20112 | -0.17807 | 0.041348 | 123.0614 | -0.043591 | 123.222 | 123.1737 | 0.11237 | 0.036711 | -0.13865 | 123.2684 | 123.148 | 123.3675 | 123.2589 | -0.33307 | 123.2825 | 123.3628 | 123.1875 | 123.2121 | -0.26475
951.2812 | 123.5046 | -122.7905 | 0.5127 | 0.057113 | 0.044851 | 0.0042321 | -0.020335 | -0.045728 | 0.11843 | 0.043632 | 0.14023 | 0.0051213 | -0.029477 | 0.093859 | 0.072676 | 0.40852 | 0.45469 | 0.3899 | 0.46418 | 0.34836 | 0.5632 | 0.19336 | 0.41771 | 0.41702 | 0.37863 | 0.4691 | 0.56772 | 0.37862 | 0.2571 | 122.9839 | -0.048512 | 123.1991 | 123.1804 | 0.19654 | -0.16434 | 0.050502 | 123.0476 | -0.043593 | 123.2082 | 123.1692 | 0.12152 | 0.055022 | -0.13408 | 123.2547 | 123.1389 | 123.3537 | 123.2452 | -0.31933 | 123.2596 | 123.3582 | 123.1691 | 123.2075 | -0.25559
952.2812 | 123.5046 | -122.7859 | 0.50354 | 0.026589 | 0.044851 | 0.0031631 | -0.019266 | -0.045728 | 0.11736 | 0.058893 | 0.14023 | 0.0061893 | -0.029477 | 0.09279 | 0.07588 | 0.4131 | 0.45469 | 0.39448 | 0.46418 | 0.35752 | 0.54488 | 0.19336 | 0.41313 | 0.40329 | 0.38321 | 0.47368 | 0.56772 | 0.3832 | 0.25252 | 122.9793 | -0.039357 | 123.1991 | 123.1804 | 0.20112 | -0.14602 | 0.041343 | 123.0385 | -0.02986 | 123.1991 | 123.1692 | 0.13068 | 0.064177 | -0.12034 | 123.2501 | 123.1435 | 123.3308 | 123.2406 | -0.31018 | 123.2596 | 123.3537 | 123.1691 | 123.1892 | -0.25102
953.2969 | 123.5138 | -122.8134 | 0.51727 | 0.057113 | 0.043782 | 0.0020951 | -0.018198 | -0.046796 | 0.11629 | 0.058893 | 0.13916 | 0.0040533 | -0.030545 | 0.091722 | 0.07588 | 0.39937 | 0.44553 | 0.38532 | 0.4596 | 0.36209 | 0.55404 | 0.18878 | 0.41771 | 0.40329 | 0.36947 | 0.47368 | 0.55398 | 0.3832 | 0.25252 | 123.0022 | -0.057669 | 123.2128 | 123.1987 | 0.19654 | -0.15518 | 0.036767 | 123.0659 | -0.043593 | 123.2311 | 123.1829 | 0.11694 | 0.036709 | -0.13408 | 123.273 | 123.1755 | 123.3675 | 123.2589 | -0.32849 | 123.2871 | 123.3674 | 123.1966 | 123.2167 | -0.26475
954.2812 | 123.4222 | -122.85 | 0.54932 | 0.057113 | 0.043782 | 0.0031631 | -0.018198 | -0.046796 | 0.11736 | 0.043632 | 0.14023 | 0.0061893 | -0.029477 | 0.093859 | 0.07588 | 0.40395 | 0.45011 | 0.3899 | 0.4596 | 0.34378 | 0.54946 | 0.18878 | 0.41313 | 0.39871 | 0.36489 | 0.47826 | 0.5494 | 0.37862 | 0.25252 | 123.0388 | -0.089712 | 123.254 | 123.2399 | 0.20112 | -0.20554 | 0.000146 | 123.1026 | -0.071057 | 123.2632 | 123.2149 | 0.11237 | 8.7e-05 | -0.1707 | 123.3096 | 123.1938 | 123.3995 | 123.3001 | -0.36053 | 123.3283 | 123.3994 | 123.2287 | 123.2487 | -0.29679
955.2812 | 123.381 | -122.8546 | 0.51727 | 0.072375 | 0.044851 | 0.0020951 | -0.019266 | -0.045728 | 0.11843 | 0.043632 | 0.13916 | 0.0040533 | -0.029477 | 0.091722 | 0.07588 | 0.40852 | 0.44553 | 0.37617 | 0.45045 | 0.35294 | 0.54946 | 0.19336 | 0.40855 | 0.40329 | 0.36947 | 0.46452 | 0.54482 | 0.37404 | 0.24794 | 123.048 | -0.066826 | 123.2631 | 123.2308 | 0.1828 | -0.16434 | 0.032189 | 123.1026 | -0.05275 | 123.2632 | 123.2241 | 0.12152 | 0.027551 | -0.14323 | 123.3051 | 123.2075 | 123.4041 | 123.3001 | -0.32391 | 123.3191 | 123.3994 | 123.2287 | 123.2579 | -0.26933
956.2812 | 123.436 | -122.85 | 0.50354 | 0.072375 | 0.043782 | 0.0020951 | -0.018198 | -0.046796 | 0.11843 | 0.074154 | 0.13809 | 0.0051213 | -0.027341 | 0.093859 | 0.074812 | 0.40395 | 0.45011 | 0.3899 | 0.4596 | 0.34378 | 0.54946 | 0.18878 | 0.40855 | 0.39413 | 0.36489 | 0.45994 | 0.54482 | 0.36488 | 0.25252 | 123.0388 | -0.043936 | 123.254 | 123.2399 | 0.20112 | -0.15976 | 0.045922 | 123.1026 | -0.043595 | 123.2586 | 123.2149 | 0.11237 | 0.041284 | -0.13866 | 123.3096 | 123.1938 | 123.3995 | 123.3001 | -0.31476 | 123.31 | 123.3949 | 123.2149 | 123.2442 | -0.25102
957.3125 | 123.3994 | -122.8775 | 0.54932 | 0.041851 | 0.044851 | -4.1882e-05 | -0.020335 | -0.046796 | 0.11843 | 0.058893 | 0.13916 | 0.0051213 | -0.029477 | 0.094927 | 0.07588 | 0.39479 | 0.44553 | 0.37617 | 0.44587 | 0.33462 | 0.54946 | 0.18421 | 0.3994 | 0.39871 | 0.36031 | 0.45994 | 0.55398 | 0.37862 | 0.24794 | 123.0617 | -0.10345 | 123.2723 | 123.2537 | 0.19196 | -0.2147 | 0.000146 | 123.1254 | -0.089371 | 123.2769 | 123.2378 | 0.11237 | 0.004666 | -0.1707 | 123.3234 | 123.2121 | 123.427 | 123.323 | -0.36511 | 123.3374 | 123.4315 | 123.2561 | 123.2762 | -0.30137
958.2812 | 123.3719 | -122.8683 | 0.54016 | 0.041851 | 0.043782 | 0.0031631 | -0.021403 | -0.045728 | 0.11843 | 0.058893 | 0.14023 | 0.0051213 | -0.029477 | 0.093859 | 0.07588 | 0.39479 | 0.44095 | 0.38074 | 0.45503 | 0.3392 | 0.54946 | 0.18878 | 0.40397 | 0.39871 | 0.36947 | 0.45994 | 0.54482 | 0.37404 | 0.24794 | 123.0571 | -0.085135 | 123.2631 | 123.2491 | 0.19196 | -0.20096 | 0.009301 | 123.1163 | -0.080216 | 123.2723 | 123.2378 | 0.12152 | 0.004663 | -0.16612 | 123.3234 | 123.2075 | 123.4178 | 123.3093 | -0.35138 | 123.3283 | 123.4132 | 123.2424 | 123.2671 | -0.29222
959.2812 | 123.3719 | -122.9004 | 0.52643 | 0.057113 | 0.043782 | 0.0042321 | -0.019266 | -0.046796 | 0.11736 | 0.074154 | 0.14023 | 0.0029843 | -0.029477 | 0.093859 | 0.076949 | 0.39479 | 0.43179 | 0.37159 | 0.44129 | 0.33462 | 0.5403 | 0.17963 | 0.39482 | 0.39413 | 0.35573 | 0.45537 | 0.54482 | 0.3603 | 0.24794 | 123.08 | -0.085137 | 123.2952 | 123.272 | 0.19196 | -0.19181 | 0.013876 | 123.1483 | -0.071062 | 123.2952 | 123.2561 | 0.10779 | 0.018396 | -0.16613 | 123.3417 | 123.235 | 123.4407 | 123.3322 | -0.3468 | 123.3558 | 123.4452 | 123.2607 | 123.2945 | -0.27848
960.2812 | 123.4222 | -122.8775 | 0.49439 | 0.057113 | 0.041646 | 0.0020951 | -0.019266 | -0.047865 | 0.11736 | 0.074154 | 0.14023 | 0.0040533 | -0.028409 | 0.093859 | 0.073744 | 0.38563 | 0.43637 | 0.37617 | 0.43671 | 0.32546 | 0.54946 | 0.17505 | 0.39024 | 0.39413 | 0.36031 | 0.44621 | 0.54025 | 0.36488 | 0.24337 | 123.0525 | -0.057673 | 123.2631 | 123.2537 | 0.20112 | -0.16892 | 0.055077 | 123.1209 | -0.048176 | 123.2677 | 123.2378 | 0.11694 | 0.045861 | -0.1295 | 123.3142 | 123.203 | 123.427 | 123.3139 | -0.31934 | 123.3237 | 123.4177 | 123.2424 | 123.2716 | -0.25102
961.2812 | 123.4406 | -122.8775 | 0.49439 | 0.057113 | 0.043782 | 0.0020951 | -0.019266 | -0.046796 | 0.11736 | 0.074154 | 0.14023 | 0.0051213 | -0.029477 | 0.094927 | 0.074812 | 0.38105 | 0.43179 | 0.37159 | 0.45045 | 0.32546 | 0.53573 | 0.17963 | 0.39482 | 0.39413 | 0.36947 | 0.44621 | 0.54025 | 0.35572 | 0.24794 | 123.0571 | -0.043938 | 123.2586 | 123.2491 | 0.19196 | -0.16892 | 0.041341 | 123.1254 | -0.048176 | 123.2723 | 123.247 | 0.12152 | 0.045861 | -0.13866 | 123.3279 | 123.203 | 123.4132 | 123.3093 | -0.31476 | 123.3237 | 123.4177 | 123.2332 | 123.2716 | -0.24644
962.2812 | 123.4085 | -122.8821 | 0.49896 | 0.072375 | 0.041646 | 0.0031631 | -0.019266 | -0.047865 | 0.11522 | 0.043632 | 0.13809 | 0.0040533 | -0.029477 | 0.093859 | 0.07588 | 0.39021 | 0.43179 | 0.36701 | 0.44587 | 0.32546 | 0.53573 | 0.17047 | 0.39024 | 0.39413 | 0.36031 | 0.44163 | 0.53109 | 0.35572 | 0.23879 | 123.0525 | -0.053093 | 123.2723 | 123.2491 | 0.19654 | -0.1735 | 0.036764 | 123.1209 | -0.057331 | 123.2723 | 123.2424 | 0.12152 | 0.032127 | -0.14324 | 123.3279 | 123.2075 | 123.4178 | 123.3139 | -0.32849 | 123.3237 | 123.4132 | 123.2378 | 123.2762 | -0.26018
963.2812 | 123.3948 | -122.9004 | 0.48981 | 0.057113 | 0.042714 | 0.0020951 | -0.021403 | -0.048933 | 0.11736 | 0.058893 | 0.13809 | 0.0040533 | -0.029477 | 0.094927 | 0.074812 | 0.38105 | 0.43179 | 0.35785 | 0.43671 | 0.32546 | 0.53115 | 0.16131 | 0.38566 | 0.39413 | 0.36947 | 0.44621 | 0.52651 | 0.35572 | 0.23879 | 123.0617 | -0.053095 | 123.2814 | 123.2582 | 0.19654 | -0.16434 | 0.04134 | 123.1392 | -0.043598 | 123.2861 | 123.2699 | 0.13068 | 0.036703 | -0.13408 | 123.3371 | 123.2259 | 123.4315 | 123.3322 | -0.3285 | 123.3466 | 123.4269 | 123.2561 | 123.2945 | -0.25102
964.2812 | 123.3994 | -122.9004 | 0.48523 | 0.011327 | 0.041646 | 0.0031631 | -0.018198 | -0.046796 | 0.11736 | 0.074154 | 0.13809 | 0.0019163 | -0.029477 | 0.095995 | 0.074812 | 0.3719 | 0.42264 | 0.35328 | 0.44129 | 0.33004 | 0.53115 | 0.16589 | 0.38566 | 0.38955 | 0.36031 | 0.44621 | 0.53567 | 0.35572 | 0.23421 | 123.0663 | -0.043938 | 123.2723 | 123.2537 | 0.18739 | -0.15519 | 0.045918 | 123.1346 | -0.03902 | 123.2861 | 123.2607 | 0.1261 | 0.050438 | -0.12951 | 123.3417 | 123.2304 | 123.4315 | 123.323 | -0.31934 | 123.3466 | 123.4361 | 123.2561 | 123.2899 | -0.25102
965.2812 | 123.4406 | -122.8912 | 0.48523 | 0.072375 | 0.043782 | 0.0020951 | -0.018198 | -0.047865 | 0.11736 | 0.074154 | 0.13916 | 0.0040533 | -0.028409 | 0.093859 | 0.07588 | 0.3719 | 0.42722 | 0.36243 | 0.43213 | 0.31173 | 0.53115 | 0.16131 | 0.38566 | 0.38955 | 0.36031 | 0.44163 | 0.52651 | 0.35115 | 0.23421 | 123.0525 | -0.053095 | 123.2631 | 123.2537 | 0.20112 | -0.1735 | 0.045918 | 123.1254 | -0.043598 | 123.2769 | 123.2515 | 0.1261 | 0.041281 | -0.13408 | 123.3234 | 123.203 | 123.4224 | 123.3185 | -0.32392 | 123.3329 | 123.4177 | 123.2424 | 123.2808 | -0.25102
966.2812 | 123.468 | -122.8683 | 0.53558 | 0.072375 | 0.043782 | 0.0020951 | -0.019266 | -0.045728 | 0.11843 | 0.043632 | 0.13916 | 0.0051213 | -0.029477 | 0.09279 | 0.074812 | 0.37648 | 0.42264 | 0.35785 | 0.43671 | 0.32088 | 0.52657 | 0.17505 | 0.37192 | 0.38497 | 0.35573 | 0.44163 | 0.52193 | 0.35115 | 0.23421 | 123.0434 | -0.098871 | 123.2448 | 123.2262 | 0.18281 | -0.2147 | -0.009014 | 123.1026 | -0.093952 | 123.2403 | 123.2241 | 0.12153 | -0.013652 | -0.18444 | 123.3051 | 123.1892 | 123.3949 | 123.291 | -0.36054 | 123.31 | 123.3903 | 123.2195 | 123.2533 | -0.30138
967.2812 | 123.4314 | -122.9187 | 0.47607 | 0.041851 | 0.040577 | 0.0042321 | -0.019266 | -0.046796 | 0.11629 | 0.089415 | 0.14023 | 0.0051213 | -0.030545 | 0.091722 | 0.074812 | 0.38105 | 0.41348 | 0.35328 | 0.42756 | 0.32546 | 0.52199 | 0.17047 | 0.38108 | 0.39413 | 0.35115 | 0.43247 | 0.51735 | 0.34657 | 0.22963 | 123.0892 | -0.048519 | 123.2998 | 123.272 | 0.18281 | -0.15061 | 0.045916 | 123.1483 | -0.0436 | 123.2998 | 123.2699 | 0.12152 | 0.041279 | -0.12951 | 123.3463 | 123.2442 | 123.4407 | 123.3322 | -0.30561 | 123.3512 | 123.4361 | 123.2653 | 123.3128 | -0.24644
968.2812 | 123.4268 | -122.9233 | 0.50812 | 0.057113 | 0.042714 | 0.0031631 | -0.019266 | -0.048933 | 0.11629 | 0.058893 | 0.13916 | 0.0029843 | -0.029477 | 0.093859 | 0.07588 | 0.3719 | 0.41348 | 0.3487 | 0.42756 | 0.31173 | 0.51741 | 0.16589 | 0.3765 | 0.38039 | 0.36031 | 0.4279 | 0.51735 | 0.34199 | 0.22963 | 123.0892 | -0.080563 | 123.2952 | 123.272 | 0.18281 | -0.19639 | 0.009293 | 123.1529 | -0.080223 | 123.2998 | 123.2836 | 0.13068 | 0.009235 | -0.16613 | 123.3508 | 123.235 | 123.4407 | 123.3368 | -0.34223 | 123.3512 | 123.4406 | 123.2653 | 123.3037 | -0.27849
969.2812 | 123.4314 | -122.8317 | 0.56305 | 0.057113 | 0.043782 | 0.0020951 | -0.020335 | -0.046796 | 0.11843 | 0.058893 | 0.13809 | 0.0040533 | -0.028409 | 0.094927 | 0.073744 | 0.36274 | 0.4089 | 0.35328 | 0.4184 | 0.31631 | 0.52657 | 0.16131 | 0.36734 | 0.38497 | 0.35573 | 0.4279 | 0.51735 | 0.34657 | 0.22047 | 122.993 | -0.14465 | 123.1945 | 123.185 | 0.19196 | -0.24674 | -0.03648 | 123.0522 | -0.13515 | 123.1991 | 123.1875 | 0.13526 | -0.045696 | -0.21648 | 123.2501 | 123.148 | 123.3583 | 123.2406 | -0.40174 | 123.2596 | 123.3491 | 123.1783 | 123.2167 | -0.34258
970.2812 | 123.4406 | -122.9095 | 0.48523 | 0.057113 | 0.040577 | 0.0020951 | -0.019266 | -0.047865 | 0.11629 | 0.058893 | 0.13702 | 0.0040533 | -0.029477 | 0.093859 | 0.076949 | 0.36732 | 0.4089 | 0.35328 | 0.4184 | 0.30715 | 0.51741 | 0.16589 | 0.3765 | 0.37123 | 0.35115 | 0.4279 | 0.51277 | 0.34657 | 0.22505 | 123.0754 | -0.06683 | 123.2769 | 123.2628 | 0.18739 | -0.17808 | 0.032182 | 123.1346 | -0.057334 | 123.286 | 123.2607 | 0.1261 | 0.027545 | -0.13866 | 123.3279 | 123.2167 | 123.427 | 123.3184 | -0.31934 | 123.3374 | 123.4223 | 123.2561 | 123.2808 | -0.26018
971.2812 | 123.4589 | -122.8867 | 0.48981 | 0.057113 | 0.044851 | 0.0042321 | -0.018198 | -0.047865 | 0.11629 | 0.058893 | 0.13809 | 0.0029843 | -0.030545 | 0.094927 | 0.07588 | 0.36732 | 0.40432 | 0.3487 | 0.42298 | 0.31631 | 0.51283 | 0.16589 | 0.3765 | 0.38039 | 0.35115 | 0.43705 | 0.51277 | 0.34199 | 0.22505 | 123.0525 | -0.06683 | 123.254 | 123.2354 | 0.18281 | -0.1735 | 0.023026 | 123.1117 | -0.052755 | 123.2632 | 123.2378 | 0.1261 | 0.022967 | -0.14782 | 123.3096 | 123.203 | 123.3995 | 123.291 | -0.32392 | 123.3237 | 123.3994 | 123.2286 | 123.267 | -0.26476
972.2812 | 123.4543 | -122.905 | 0.48065 | 0.072375 | 0.040577 | 0.0031631 | -0.018198 | -0.047865 | 0.11629 | 0.058893 | 0.14023 | 0.0029843 | -0.028409 | 0.095995 | 0.073744 | 0.3719 | 0.40432 | 0.35328 | 0.41382 | 0.30715 | 0.51741 | 0.16131 | 0.36734 | 0.37581 | 0.34658 | 0.42332 | 0.51735 | 0.34657 | 0.22047 | 123.0663 | -0.066832 | 123.2769 | 123.2582 | 0.19196 | -0.17351 | 0.036759 | 123.1254 | -0.057335 | 123.2723 | 123.2515 | 0.1261 | 0.036701 | -0.13409 | 123.3188 | 123.2121 | 123.4224 | 123.3093 | -0.31934 | 123.3283 | 123.4223 | 123.2515 | 123.2808 | -0.26018
973.2812 | 123.4451 | -122.905 | 0.48065 | 0.057113 | 0.042714 | 0.0042321 | -0.017129 | -0.045728 | 0.11736 | 0.058893 | 0.13702 | 0.0061893 | -0.029477 | 0.095995 | 0.074812 | 0.36274 | 0.40432 | 0.3487 | 0.4184 | 0.31631 | 0.51283 | 0.15673 | 0.36734 | 0.36666 | 0.35115 | 0.42332 | 0.51735 | 0.33741 | 0.22505 | 123.0617 | -0.062253 | 123.2677 | 123.2537 | 0.19196 | -0.16435 | 0.032181 | 123.13 | -0.057335 | 123.2723 | 123.2561 | 0.1261 | 0.036701 | -0.14324 | 123.3234 | 123.2213 | 123.4178 | 123.3093 | -0.32392 | 123.3283 | 123.4223 | 123.2424 | 123.2716 | -0.2556
974.2812 | 123.4085 | -122.8867 | 0.54016 | 0.072375 | 0.042714 | 0.0020951 | -0.020335 | -0.047865 | 0.11629 | 0.043632 | 0.13809 | 0.0029843 | -0.029477 | 0.094927 | 0.07588 | 0.36732 | 0.40432 | 0.33954 | 0.41382 | 0.30715 | 0.50825 | 0.16131 | 0.36277 | 0.36666 | 0.342 | 0.42332 | 0.5082 | 0.32825 | 0.21131 | 123.048 | -0.12634 | 123.254 | 123.2262 | 0.17823 | -0.23301 | -0.031907 | 123.098 | -0.11684 | 123.2494 | 123.2287 | 0.13068 | -0.031965 | -0.21191 | 123.3005 | 123.1938 | 123.3949 | 123.291 | -0.37885 | 123.31 | 123.3949 | 123.2149 | 123.2533 | -0.32885
975.2812 | 123.4085 | -122.937 | 0.48065 | 0.057113 | 0.040577 | 0.0010261 | -0.019266 | -0.046796 | 0.11736 | 0.074154 | 0.13702 | 0.0029843 | -0.029477 | 0.095995 | 0.074812 | 0.35816 | 0.40432 | 0.3487 | 0.40924 | 0.29341 | 0.51741 | 0.15215 | 0.36277 | 0.36666 | 0.342 | 0.41874 | 0.50362 | 0.33283 | 0.20674 | 123.0892 | -0.07141 | 123.2952 | 123.2857 | 0.19654 | -0.18724 | 0.036759 | 123.1437 | -0.061914 | 123.2998 | 123.279 | 0.13526 | 0.022965 | -0.14782 | 123.3463 | 123.2304 | 123.4544 | 123.3413 | -0.3285 | 123.3558 | 123.4406 | 123.2698 | 123.3037 | -0.27392
976.2812 | 123.3994 | -122.9324 | 0.48065 | 0.057113 | 0.042714 | 0.0042321 | -0.019266 | -0.047865 | 0.11736 | 0.074154 | 0.13809 | 0.0051213 | -0.027341 | 0.095995 | 0.074812 | 0.35358 | 0.40432 | 0.33954 | 0.40466 | 0.30257 | 0.50368 | 0.15215 | 0.35819 | 0.36208 | 0.342 | 0.41416 | 0.49446 | 0.32367 | 0.20216 | 123.0846 | -0.075988 | 123.286 | 123.272 | 0.18739 | -0.17808 | 0.023024 | 123.1346 | -0.066492 | 123.2906 | 123.2744 | 0.13984 | 0.013808 | -0.15698 | 123.3371 | 123.235 | 123.4361 | 123.3368 | -0.3285 | 123.3466 | 123.4269 | 123.2561 | 123.2945 | -0.2785
977.2969 | 123.5321 | -122.9095 | 0.42572 | 0.041851 | 0.039509 | 0.0020951 | -0.018198 | -0.046796 | 0.11736 | 0.10468 | 0.13809 | 0.0061893 | -0.027341 | 0.094927 | 0.074812 | 0.35358 | 0.39975 | 0.33954 | 0.40466 | 0.30715 | 0.4991 | 0.14299 | 0.35361 | 0.36208 | 0.35115 | 0.41874 | 0.5082 | 0.32367 | 0.20674 | 123.0525 | -0.021056 | 123.2631 | 123.2491 | 0.19655 | -0.11857 | 0.073377 | 123.1163 | -0.006982 | 123.2632 | 123.2607 | 0.14442 | 0.082476 | -0.10205 | 123.3142 | 123.2167 | 123.4086 | 123.3093 | -0.28273 | 123.3283 | 123.4177 | 123.2332 | 123.2716 | -0.21898
978.2812 | 123.4314 | -122.9324 | 0.47607 | 0.057113 | 0.041646 | 0.0031631 | -0.018198 | -0.045728 | 0.11522 | 0.074154 | 0.13809 | 0.0040533 | -0.028409 | 0.094927 | 0.074812 | 0.35358 | 0.39975 | 0.33038 | 0.40009 | 0.29799 | 0.49452 | 0.15215 | 0.36277 | 0.36666 | 0.33742 | 0.41416 | 0.49904 | 0.32367 | 0.20674 | 123.0846 | -0.075989 | 123.286 | 123.2628 | 0.17823 | -0.17808 | 0.018444 | 123.1392 | -0.061914 | 123.2952 | 123.2699 | 0.13068 | 0.022964 | -0.1524 | 123.3325 | 123.2304 | 123.427 | 123.3322 | -0.32392 | 123.3466 | 123.4315 | 123.2561 | 123.2991 | -0.26934
979.2812 | 123.4314 | -122.9507 | 0.4715 | 0.041851 | 0.040577 | 0.0010261 | -0.020335 | -0.048933 | 0.11736 | 0.074154 | 0.13702 | 0.0040533 | -0.030545 | 0.095995 | 0.072676 | 0.35358 | 0.39517 | 0.33496 | 0.40924 | 0.30257 | 0.4991 | 0.14299 | 0.35361 | 0.3575 | 0.342 | 0.41416 | 0.49904 | 0.32825 | 0.19758 | 123.0937 | -0.062255 | 123.3043 | 123.2857 | 0.19197 | -0.16893 | 0.0276 | 123.1483 | -0.057337 | 123.3044 | 123.2927 | 0.14442 | 0.027541 | -0.14324 | 123.36 | 123.2533 | 123.4498 | 123.3459 | -0.3285 | 123.3649 | 123.4498 | 123.279 | 123.3082 | -0.27392
980.2812 | 123.4177 | -122.937 | 0.47607 | 0.057113 | 0.039509 | 0.0020951 | -0.019266 | -0.047865 | 0.11629 | 0.058893 | 0.13916 | 0.0040533 | -0.027341 | 0.097064 | 0.073744 | 0.35358 | 0.39059 | 0.33038 | 0.40466 | 0.28883 | 0.49452 | 0.14299 | 0.35819 | 0.35292 | 0.342 | 0.405 | 0.49446 | 0.31452 | 0.19758 | 123.08 | -0.07141 | 123.2906 | 123.2674 | 0.18739 | -0.18724 | 0.018444 | 123.1346 | -0.071071 | 123.2952 | 123.279 | 0.14442 | 0.018386 | -0.16156 | 123.3417 | 123.2258 | 123.4315 | 123.3276 | -0.33308 | 123.342 | 123.4315 | 123.2515 | 123.2899 | -0.2785
981.2812 | 123.3994 | -122.9279 | 0.4715 | 0.057113 | 0.040577 | 0.0020951 | -0.019266 | -0.047865 | 0.11629 | 0.058893 | 0.13916 | 0.0029843 | -0.028409 | 0.095995 | 0.073744 | 0.35358 | 0.39517 | 0.33496 | 0.40009 | 0.29341 | 0.48994 | 0.14757 | 0.35361 | 0.35292 | 0.33284 | 0.40958 | 0.50362 | 0.32367 | 0.20216 | 123.0754 | -0.071412 | 123.2814 | 123.2628 | 0.18739 | -0.17809 | 0.018443 | 123.13 | -0.061916 | 123.2815 | 123.2607 | 0.13068 | 0.03212 | -0.14782 | 123.3279 | 123.2213 | 123.4178 | 123.323 | -0.32392 | 123.3374 | 123.4315 | 123.2515 | 123.2808 | -0.26934
982.2812 | 123.3994 | -122.9141 | 0.49896 | 0.072375 | 0.039509 | 0.0031631 | -0.019266 | -0.046796 | 0.11736 | 0.089415 | 0.13809 | 0.0051213 | -0.028409 | 0.095995 | 0.073744 | 0.34901 | 0.39059 | 0.32123 | 0.38635 | 0.29341 | 0.48994 | 0.13842 | 0.34903 | 0.3575 | 0.33742 | 0.405 | 0.50362 | 0.31452 | 0.18842 | 123.0525 | -0.11261 | 123.2631 | 123.2354 | 0.18281 | -0.20555 | -0.009022 | 123.1025 | -0.093959 | 123.2632 | 123.2515 | 0.149 | 0.004655 | -0.18445 | 123.3005 | 123.2075 | 123.4041 | 123.3047 | -0.36055 | 123.3191 | 123.4177 | 123.2286 | 123.2716 | -0.31054
983.3125 | 123.5092 | -122.8775 | 0.46692 | 0.057113 | 0.039509 | 0.0042321 | -0.020335 | -0.046796 | 0.11736 | 0.10468 | 0.13916 | 0.0029843 | -0.029477 | 0.093859 | 0.07588 | 0.34443 | 0.38601 | 0.31665 | 0.39093 | 0.27967 | 0.48994 | 0.13842 | 0.34903 | 0.35292 | 0.32826 | 0.405 | 0.49904 | 0.3191 | 0.19758 | 123.0159 | -0.075991 | 123.2219 | 123.1942 | 0.17823 | -0.18725 | 0.023021 | 123.0751 | -0.061916 | 123.2265 | 123.2058 | 0.13068 | 0.032119 | -0.14782 | 123.2684 | 123.1572 | 123.3674 | 123.2635 | -0.3285 | 123.2825 | 123.3765 | 123.1966 | 123.2304 | -0.26934
984.2812 | 123.4314 | -122.9416 | 0.46692 | 0.072375 | 0.038441 | 0.0042321 | -0.019266 | -0.046796 | 0.11522 | 0.058893 | 0.13916 | 0.0029843 | -0.028409 | 0.094927 | 0.074812 | 0.34443 | 0.38601 | 0.32123 | 0.39551 | 0.27967 | 0.48994 | 0.13842 | 0.34445 | 0.34834 | 0.33742 | 0.40042 | 0.49446 | 0.31452 | 0.20674 | 123.08 | -0.071412 | 123.286 | 123.2628 | 0.18281 | -0.18725 | 0.023021 | 123.1483 | -0.066495 | 123.286 | 123.279 | 0.13068 | 0.027541 | -0.1524 | 123.3371 | 123.2213 | 123.4315 | 123.3276 | -0.3285 | 123.342 | 123.436 | 123.2561 | 123.2899 | -0.26018
985.2812 | 123.3994 | -122.9507 | 0.4715 | 0.072375 | 0.039509 | 0.0010261 | -0.018198 | -0.047865 | 0.11629 | 0.058893 | 0.13702 | 0.0040533 | -0.028409 | 0.094927 | 0.073744 | 0.34443 | 0.38143 | 0.32123 | 0.39551 | 0.28883 | 0.49452 | 0.12926 | 0.34903 | 0.34834 | 0.33284 | 0.405 | 0.48988 | 0.31452 | 0.20216 | 123.08 | -0.07599 | 123.2952 | 123.272 | 0.19197 | -0.18267 | 0.023021 | 123.1529 | -0.066494 | 123.2998 | 123.2836 | 0.13068 | 0.018384 | -0.15698 | 123.3463 | 123.2396 | 123.4453 | 123.3322 | -0.34224 | 123.3557 | 123.4406 | 123.2653 | 123.2991 | -0.26934
986.2812 | 123.4039 | -122.9462 | 0.48065 | 0.041851 | 0.040577 | 0.0031631 | -0.019266 | -0.046796 | 0.11736 | 0.074154 | 0.13702 | 0.0040533 | -0.028409 | 0.099201 | 0.074812 | 0.33985 | 0.37685 | 0.32581 | 0.39093 | 0.29799 | 0.48536 | 0.13384 | 0.34445 | 0.34834 | 0.33284 | 0.40042 | 0.48988 | 0.30994 | 0.18842 | 123.08 | -0.089724 | 123.286 | 123.272 | 0.19197 | -0.18266 | 0.004709 | 123.1346 | -0.080228 | 123.2906 | 123.279 | 0.14442 | 0.009229 | -0.17071 | 123.3371 | 123.2442 | 123.4315 | 123.323 | -0.34682 | 123.3466 | 123.436 | 123.2561 | 123.2945 | -0.29223
987.2812 | 123.3902 | -122.9279 | 0.49439 | 0.072375 | 0.037372 | 0.0020951 | -0.019266 | -0.047865 | 0.11522 | 0.089415 | 0.13702 | 0.0029843 | -0.029477 | 0.095995 | 0.074812 | 0.33527 | 0.37685 | 0.32123 | 0.38177 | 0.29341 | 0.48994 | 0.14299 | 0.34903 | 0.34834 | 0.33284 | 0.39585 | 0.48988 | 0.30994 | 0.193 | 123.0709 | -0.11261 | 123.2631 | 123.2491 | 0.17823 | -0.20098 | -0.004445 | 123.1209 | -0.098539 | 123.2769 | 123.2607 | 0.13984 | -0.004504 | -0.18445 | 123.3096 | 123.2213 | 123.4178 | 123.3047 | -0.35139 | 123.3237 | 123.4177 | 123.2378 | 123.2762 | -0.30139
988.2812 | 123.4314 | -122.9462 | 0.46692 | 0.057113 | 0.040577 | 0.0020951 | -0.020335 | -0.045728 | 0.11736 | 0.089415 | 0.13809 | 0.0051213 | -0.028409 | 0.097064 | 0.073744 | 0.33527 | 0.38143 | 0.31207 | 0.39093 | 0.28425 | 0.48994 | 0.12926 | 0.34445 | 0.34834 | 0.32368 | 0.39585 | 0.4853 | 0.30994 | 0.18842 | 123.0754 | -0.075991 | 123.2814 | 123.2582 | 0.18281 | -0.18267 | 0.023021 | 123.1346 | -0.071073 | 123.2906 | 123.2698 | 0.13526 | 0.018384 | -0.15698 | 123.3371 | 123.2304 | 123.4361 | 123.3276 | -0.33766 | 123.342 | 123.4315 | 123.2561 | 123.2945 | -0.2785
989.2812 | 123.4451 | -122.9507 | 0.46692 | 0.057113 | 0.038441 | 0.0042321 | -0.018198 | -0.046796 | 0.11522 | 0.058893 | 0.13702 | 0.0040533 | -0.029477 | 0.097064 | 0.072676 | 0.33527 | 0.37227 | 0.31207 | 0.38635 | 0.29341 | 0.48078 | 0.12926 | 0.33529 | 0.33918 | 0.32368 | 0.39585 | 0.4853 | 0.31452 | 0.18384 | 123.08 | -0.080569 | 123.286 | 123.2628 | 0.18281 | -0.17351 | 0.013864 | 123.1346 | -0.071073 | 123.286 | 123.2744 | 0.13984 | 0.018384 | -0.1524 | 123.3371 | 123.2442 | 123.4315 | 123.323 | -0.33766 | 123.3466 | 123.436 | 123.2653 | 123.2899 | -0.28308
990.2812 | 123.468 | -122.9462 | 0.44861 | 0.057113 | 0.039509 | 0.0020951 | -0.019266 | -0.047865 | 0.11522 | 0.074154 | 0.13809 | 0.0051213 | -0.029477 | 0.099201 | 0.072676 | 0.33527 | 0.37227 | 0.31665 | 0.39093 | 0.27967 | 0.48536 | 0.13384 | 0.33987 | 0.3346 | 0.32826 | 0.39127 | 0.48988 | 0.30536 | 0.18842 | 123.08 | -0.05768 | 123.2814 | 123.2628 | 0.18281 | -0.16894 | 0.036753 | 123.1346 | -0.057341 | 123.286 | 123.2744 | 0.13984 | 0.041273 | -0.14325 | 123.3371 | 123.2258 | 123.4315 | 123.3184 | -0.31477 | 123.3374 | 123.436 | 123.2515 | 123.2808 | -0.26019
991.2812 | 123.436 | -122.9599 | 0.46234 | 0.057113 | 0.038441 | 0.0020951 | -0.020335 | -0.045728 | 0.11629 | 0.043632 | 0.13809 | 0.0040533 | -0.029477 | 0.097064 | 0.072676 | 0.33527 | 0.37227 | 0.30749 | 0.39093 | 0.27967 | 0.48994 | 0.14299 | 0.32614 | 0.33918 | 0.3191 | 0.39127 | 0.48072 | 0.30536 | 0.17926 | 123.1029 | -0.071413 | 123.2952 | 123.2674 | 0.1645 | -0.18267 | 0.027599 | 123.1392 | -0.071074 | 123.286 | 123.279 | 0.13984 | 0.018383 | -0.15698 | 123.3508 | 123.2396 | 123.4498 | 123.3322 | -0.31935 | 123.3512 | 123.4406 | 123.2653 | 123.2991 | -0.28308
992.2812 | 123.4268 | -122.9691 | 0.44403 | 0.041851 | 0.037372 | 0.0010261 | -0.020335 | -0.047865 | 0.11522 | 0.058893 | 0.13702 | 0.0029843 | -0.028409 | 0.095995 | 0.074812 | 0.33527 | 0.36769 | 0.31665 | 0.38635 | 0.27509 | 0.4762 | 0.12926 | 0.33529 | 0.3346 | 0.3191 | 0.39585 | 0.47614 | 0.30078 | 0.17926 | 123.0983 | -0.057681 | 123.3043 | 123.2857 | 0.18739 | -0.16894 | 0.032173 | 123.1483 | -0.048185 | 123.3043 | 123.2882 | 0.13984 | 0.032114 | -0.14325 | 123.3554 | 123.2441 | 123.4453 | 123.3367 | -0.31477 | 123.3649 | 123.4452 | 123.2698 | 123.3037 | -0.26477
993.2812 | 123.4314 | -122.9691 | 0.45776 | 0.072375 | 0.038441 | 0.0031631 | -0.019266 | -0.047865 | 0.11415 | 0.074154 | 0.13809 | 0.0029843 | -0.029477 | 0.097064 | 0.073744 | 0.33527 | 0.37685 | 0.31207 | 0.37261 | 0.27967 | 0.4762 | 0.13384 | 0.33529 | 0.3346 | 0.3191 | 0.38669 | 0.47614 | 0.30078 | 0.17468 | 123.1029 | -0.085149 | 123.3043 | 123.2811 | 0.17823 | -0.17809 | 0.01844 | 123.1437 | -0.071075 | 123.3043 | 123.2882 | 0.14442 | 0.018381 | -0.15698 | 123.3417 | 123.2487 | 123.4453 | 123.3459 | -0.32393 | 123.3557 | 123.4452 | 123.2698 | 123.3037 | -0.28308
994.2812 | 123.4222 | -122.9599 | 0.45776 | 0.057113 | 0.038441 | 0.0042321 | -0.018198 | -0.047865 | 0.11522 | 0.058893 | 0.13809 | 0.0040533 | -0.030545 | 0.097064 | 0.074812 | 0.32611 | 0.36312 | 0.30749 | 0.38177 | 0.28883 | 0.4762 | 0.13384 | 0.33071 | 0.34376 | 0.3191 | 0.37753 | 0.4853 | 0.2962 | 0.17468 | 123.0937 | -0.075992 | 123.286 | 123.2674 | 0.17366 | -0.16893 | 0.01844 | 123.1346 | -0.080232 | 123.2906 | 123.279 | 0.14442 | 0.027539 | -0.16156 | 123.3417 | 123.2487 | 123.4361 | 123.323 | -0.32393 | 123.3374 | 123.4452 | 123.2561 | 123.3037 | -0.28308
995.2812 | 123.5184 | -122.9187 | 0.44861 | 0.072375 | 0.038441 | 0.0010261 | -0.019266 | -0.045728 | 0.11309 | 0.058893 | 0.13809 | 0.0040533 | -0.027341 | 0.097064 | 0.073744 | 0.32154 | 0.35854 | 0.31207 | 0.37261 | 0.27052 | 0.47163 | 0.12926 | 0.32614 | 0.33918 | 0.32826 | 0.38211 | 0.48072 | 0.2962 | 0.17468 | 123.048 | -0.075993 | 123.2402 | 123.2308 | 0.18281 | -0.17809 | 0.023017 | 123.0934 | -0.066498 | 123.2448 | 123.247 | 0.15358 | 0.032116 | -0.15241 | 123.2913 | 123.1892 | 123.3903 | 123.2772 | -0.31935 | 123.3008 | 123.3994 | 123.2149 | 123.2579 | -0.27392
996.2812 | 123.4222 | -122.9507 | 0.45776 | 0.057113 | 0.037372 | 0.0042321 | -0.016061 | -0.046796 | 0.11629 | 0.089415 | 0.13809 | 0.0029843 | -0.030545 | 0.098132 | 0.074812 | 0.33069 | 0.35854 | 0.30749 | 0.37261 | 0.26136 | 0.47163 | 0.13842 | 0.32156 | 0.33003 | 0.30995 | 0.38669 | 0.47157 | 0.30078 | 0.17468 | 123.0892 | -0.085149 | 123.2814 | 123.2582 | 0.16908 | -0.19641 | 0.013861 | 123.1254 | -0.071075 | 123.2723 | 123.2607 | 0.13526 | 0.013803 | -0.15698 | 123.3234 | 123.2121 | 123.4224 | 123.3093 | -0.31935 | 123.3374 | 123.4223 | 123.2515 | 123.2808 | -0.28308
997.2812 | 123.4543 | -122.9324 | 0.43945 | 0.041851 | 0.039509 | 0.0020951 | -0.020335 | -0.046796 | 0.11629 | 0.058893 | 0.13702 | 0.0051213 | -0.027341 | 0.098132 | 0.073744 | 0.32611 | 0.35854 | 0.29834 | 0.37261 | 0.26136 | 0.47163 | 0.13384 | 0.32614 | 0.32545 | 0.3191 | 0.37753 | 0.46699 | 0.2962 | 0.17011 | 123.0663 | -0.066838 | 123.2585 | 123.2308 | 0.1645 | -0.1781 | 0.032172 | 123.1025 | -0.061921 | 123.2586 | 123.2515 | 0.149 | 0.027535 | -0.14325 | 123.305 | 123.1938 | 123.4041 | 123.291 | -0.30562 | 123.31 | 123.3994 | 123.2286 | 123.2579 | -0.26935
998.2812 | 123.3902 | -122.9462 | 0.45776 | 0.072375 | 0.036304 | 0.0010261 | -0.021403 | -0.046796 | 0.11629 | 0.058893 | 0.13702 | 0.0029843 | -0.029477 | 0.097064 | 0.074812 | 0.33069 | 0.36769 | 0.30749 | 0.36804 | 0.27509 | 0.47163 | 0.12926 | 0.32614 | 0.3346 | 0.30995 | 0.38669 | 0.47157 | 0.29162 | 0.17011 | 123.0754 | -0.089728 | 123.2769 | 123.2537 | 0.17823 | -0.18267 | 0.013861 | 123.1163 | -0.071075 | 123.2723 | 123.2561 | 0.13984 | 0.013803 | -0.16614 | 123.3142 | 123.2213 | 123.4178 | 123.3139 | -0.32851 | 123.3329 | 123.4177 | 123.2378 | 123.2808 | -0.28766
999.2812 | 123.4222 | -122.937 | 0.46234 | 0.072375 | 0.037372 | -4.1882e-05 | -0.019266 | -0.045728 | 0.11629 | 0.058893 | 0.13809 | 0.0040533 | -0.029477 | 0.099201 | 0.073744 | 0.33069 | 0.36769 | 0.30291 | 0.36804 | 0.26136 | 0.47163 | 0.12926 | 0.32614 | 0.32545 | 0.31452 | 0.38211 | 0.47614 | 0.29162 | 0.17011 | 123.0663 | -0.094305 | 123.2677 | 123.2399 | 0.17366 | -0.20098 | 0.009284 | 123.1071 | -0.080231 | 123.2631 | 123.2515 | 0.14442 | 0.013804 | -0.17072 | 123.305 | 123.1984 | 123.4086 | 123.3047 | -0.33308 | 123.3191 | 123.4132 | 123.2286 | 123.2625 | -0.29224
1000.2812 | 123.4314 | -122.9782 | 0.43488 | 0.072375 | 0.039509 | 0.0020951 | -0.020335 | -0.046796 | 0.11522 | 0.074154 | 0.13702 | 0.0029843 | -0.030545 | 0.098132 | 0.072676 | 0.31696 | 0.35854 | 0.30291 | 0.36804 | 0.27509 | 0.46705 | 0.12926 | 0.32156 | 0.33003 | 0.31452 | 0.37753 | 0.47157 | 0.2962 | 0.17011 | 123.1075 | -0.066839 | 123.2952 | 123.2811 | 0.17366 | -0.15978 | 0.032172 | 123.1483 | -0.057343 | 123.2998 | 123.2927 | 0.14442 | 0.036692 | -0.13867 | 123.3462 | 123.2533 | 123.4453 | 123.3367 | -0.30562 | 123.3557 | 123.4498 | 123.2744 | 123.3082 | -0.26477
1001.3125 | 123.4863 | -122.9736 | 0.37079 | 0.072375 | 0.038441 | 0.0031631 | -0.019266 | -0.046796 | 0.11629 | 0.043632 | 0.13702 | 0.0051213 | -0.029477 | 0.098132 | 0.074812 | 0.31696 | 0.35854 | 0.29834 | 0.36804 | 0.25678 | 0.46247 | 0.12926 | 0.32614 | 0.31629 | 0.30537 | 0.37753 | 0.47614 | 0.28247 | 0.16095 | 123.1029 | -0.002753 | 123.2906 | 123.272 | 0.16908 | -0.11401 | 0.091679 | 123.1346 | 0.006743 | 123.2998 | 123.279 | 0.14442 | 0.10536 | -0.088322 | 123.3417 | 123.2304 | 123.4361 | 123.3322 | -0.24153 | 123.3512 | 123.4498 | 123.2561 | 123.2899 | -0.20984
1002.2812 | 123.5092 | -122.9141 | 0.4303 | 0.057113 | 0.038441 | 0.0010261 | -0.020335 | -0.047865 | 0.11736 | 0.058893 | 0.13809 | 0.0029843 | -0.028409 | 0.098132 | 0.074812 | 0.32611 | 0.35854 | 0.29834 | 0.36346 | 0.27052 | 0.46705 | 0.12926 | 0.32614 | 0.33003 | 0.31452 | 0.38211 | 0.46241 | 0.29162 | 0.16553 | 123.0434 | -0.06684 | 123.2402 | 123.2125 | 0.16908 | -0.15978 | 0.036749 | 123.0797 | -0.048188 | 123.2403 | 123.2286 | 0.149 | 0.032112 | -0.13867 | 123.2776 | 123.1846 | 123.3812 | 123.2727 | -0.30104 | 123.2962 | 123.3765 | 123.2057 | 123.2442 | -0.26477
1003.2969 | 123.4085 | -122.9736 | 0.43488 | 0.057113 | 0.039509 | -4.1882e-05 | -0.019266 | -0.047865 | 0.11522 | 0.043632 | 0.13809 | 0.0029843 | -0.028409 | 0.097064 | 0.073744 | 0.32154 | 0.35854 | 0.29834 | 0.35888 | 0.25678 | 0.45789 | 0.12468 | 0.32156 | 0.33003 | 0.31452 | 0.36838 | 0.47157 | 0.28247 | 0.16553 | 123.0983 | -0.075995 | 123.2952 | 123.272 | 0.17366 | -0.1781 | 0.023015 | 123.1392 | -0.0665 | 123.2952 | 123.2882 | 0.149 | 0.036692 | -0.15241 | 123.3325 | 123.2304 | 123.4315 | 123.3322 | -0.3102 | 123.342 | 123.4452 | 123.2561 | 123.3037 | -0.26935
1004.2812 | 123.4314 | -122.937 | 0.45776 | 0.057113 | 0.036304 | 0.0031631 | -0.017129 | -0.048933 | 0.11415 | 0.10468 | 0.13916 | 0.0029843 | -0.030545 | 0.099201 | 0.074812 | 0.32154 | 0.35854 | 0.29376 | 0.35888 | 0.26136 | 0.46247 | 0.12926 | 0.32156 | 0.32087 | 0.30537 | 0.37753 | 0.46699 | 0.28247 | 0.17468 | 123.0663 | -0.098884 | 123.2585 | 123.2308 | 0.1645 | -0.19641 | 0.004704 | 123.1117 | -0.080232 | 123.2586 | 123.2424 | 0.13068 | 0.009224 | -0.1753 | 123.2959 | 123.1984 | 123.3995 | 123.2955 | -0.32851 | 123.3145 | 123.404 | 123.2195 | 123.2579 | -0.28308
1005.2812 | 123.4314 | -122.9874 | 0.45776 | 0.057113 | 0.036304 | 0.0031631 | -0.019266 | -0.047865 | 0.11629 | 0.074154 | 0.13809 | 0.0051213 | -0.027341 | 0.099201 | 0.073744 | 0.31238 | 0.36312 | 0.2846 | 0.35888 | 0.26594 | 0.46247 | 0.12926 | 0.32156 | 0.31629 | 0.30537 | 0.37295 | 0.46241 | 0.28247 | 0.16553 | 123.1166 | -0.098884 | 123.2997 | 123.272 | 0.15534 | -0.19183 | 0.004704 | 123.1529 | -0.084811 | 123.3089 | 123.2927 | 0.13984 | 0.004646 | -0.1753 | 123.3462 | 123.2533 | 123.4498 | 123.3505 | -0.32851 | 123.3603 | 123.4498 | 123.2698 | 123.3037 | -0.29224
1006.2812 | 123.4406 | -122.9324 | 0.44861 | 0.072375 | 0.038441 | 0.0031631 | -0.019266 | -0.047865 | 0.11522 | 0.074154 | 0.13809 | 0.0019163 | -0.029477 | 0.098132 | 0.07588 | 0.31238 | 0.3448 | 0.28918 | 0.35888 | 0.26136 | 0.45789 | 0.12926 | 0.32156 | 0.31629 | 0.30079 | 0.37295 | 0.46699 | 0.27789 | 0.15637 | 123.0617 | -0.089728 | 123.2448 | 123.2216 | 0.15992 | -0.18725 | 0.009282 | 123.0888 | -0.075655 | 123.254 | 123.2332 | 0.14442 | 0.01838 | -0.17072 | 123.2913 | 123.1938 | 123.3903 | 123.2772 | -0.31935 | 123.3054 | 123.3994 | 123.2103 | 123.2487 | -0.29224
1007.2812 | 123.4863 | -122.9416 | 0.42114 | 0.072375 | 0.036304 | 0.0020951 | -0.020335 | -0.046796 | 0.11522 | 0.089415 | 0.13702 | 0.0029843 | -0.029477 | 0.099201 | 0.073744 | 0.31696 | 0.3448 | 0.29376 | 0.35888 | 0.24762 | 0.45331 | 0.12468 | 0.3124 | 0.31629 | 0.29621 | 0.37295 | 0.45783 | 0.28247 | 0.16095 | 123.0663 | -0.062263 | 123.2585 | 123.2353 | 0.16908 | -0.17352 | 0.032168 | 123.1025 | -0.04819 | 123.254 | 123.2378 | 0.13526 | 0.036688 | -0.13868 | 123.3005 | 123.1892 | 123.3949 | 123.2864 | -0.29646 | 123.3145 | 123.3994 | 123.2241 | 123.2579 | -0.2602
1008.2812 | 123.5092 | -122.9416 | 0.41199 | 0.041851 | 0.037372 | 0.0020951 | -0.021403 | -0.046796 | 0.11522 | 0.058893 | 0.13702 | 0.0040533 | -0.028409 | 0.099201 | 0.072676 | 0.31238 | 0.34938 | 0.28002 | 0.3543 | 0.25678 | 0.45789 | 0.12468 | 0.3124 | 0.32087 | 0.29163 | 0.3638 | 0.46699 | 0.28247 | 0.16095 | 123.0663 | -0.057686 | 123.254 | 123.2216 | 0.15534 | -0.15521 | 0.045903 | 123.1025 | -0.048191 | 123.254 | 123.2332 | 0.13068 | 0.055001 | -0.12952 | 123.2959 | 123.1984 | 123.3995 | 123.291 | -0.28731 | 123.3054 | 123.4086 | 123.2241 | 123.2625 | -0.25104
1009.2812 | 123.349 | -122.937 | 0.40283 | 0.057113 | 0.037372 | 0.0010261 | -0.020335 | -0.046796 | 0.11522 | 0.089415 | 0.13916 | 0.0029843 | -0.029477 | 0.097064 | 0.073744 | 0.3078 | 0.34022 | 0.28918 | 0.3543 | 0.2522 | 0.45789 | 0.1201 | 0.30782 | 0.31171 | 0.29621 | 0.3638 | 0.46241 | 0.27789 | 0.16095 | 123.0571 | -0.048531 | 123.2448 | 123.2262 | 0.16908 | -0.15063 | 0.055058 | 123.098 | -0.039036 | 123.2448 | 123.2332 | 0.13526 | 0.059578 | -0.12494 | 123.2913 | 123.1892 | 123.3949 | 123.2772 | -0.28273 | 123.3008 | 123.3994 | 123.2149 | 123.2487 | -0.24189
1010.2812 | 123.5275 | -122.9599 | 0.40741 | 0.072375 | 0.037372 | 0.0020951 | -0.021403 | -0.047865 | 0.11736 | 0.043632 | 0.13702 | 0.0061893 | -0.030545 | 0.097064 | 0.073744 | 0.31238 | 0.3448 | 0.28918 | 0.34514 | 0.24762 | 0.46247 | 0.1201 | 0.3124 | 0.32087 | 0.29621 | 0.3638 | 0.45783 | 0.27331 | 0.15637 | 123.08 | -0.062265 | 123.2723 | 123.2491 | 0.16908 | -0.15979 | 0.055058 | 123.1163 | -0.043614 | 123.2723 | 123.2561 | 0.13984 | 0.050421 | -0.1341 | 123.305 | 123.2075 | 123.4224 | 123.3047 | -0.28731 | 123.3237 | 123.4177 | 123.2332 | 123.2808 | -0.25104
1011.2969 | 123.4451 | -122.9782 | 0.41657 | 0.057113 | 0.036304 | 0.0010261 | -0.020335 | -0.048933 | 0.11629 | 0.074154 | 0.13809 | 0.0040533 | -0.029477 | 0.098132 | 0.072676 | 0.3078 | 0.34938 | 0.29376 | 0.34972 | 0.22015 | 0.46247 | 0.11552 | 0.3124 | 0.31629 | 0.29163 | 0.35922 | 0.45325 | 0.11764 | 0.15637 | 123.0937 | -0.066842 | 123.286 | 123.272 | 0.17824 | -0.19642 | 0.045903 | 123.1346 | -0.057347 | 123.2906 | 123.2698 | 0.13526 | 0.036687 | -0.29893 | 123.3279 | 123.1984 | 123.4407 | 123.3276 | -0.30104 | 123.3374 | 123.4315 | 123.0958 | 123.2945 | -0.2602
1012.2812 | 123.4818 | -122.9462 | 0.40283 | 0.072375 | 0.037372 | -4.1882e-05 | -0.019266 | -0.047865 | 0.11629 | 0.074154 | 0.13595 | 0.0029843 | -0.028409 | 0.099201 | 0.07588 | 0.30322 | 0.34022 | 0.2846 | 0.34514 | 0.069043 | 0.44415 | 0.0331 | 0.30782 | 0.31171 | 0.29163 | 0.35922 | 0.44867 | -0.0884 | 0.14721 | 122.9793 | -0.057687 | 123.2494 | 123.2308 | 0.2515 | -0.33379 | 0.041322 | 123.0934 | -0.043614 | 123.254 | 123.2378 | 0.14442 | 0.045842 | -0.49123 | 123.2913 | 123.0152 | 123.3903 | 123.2864 | -0.36973 | 123.3054 | 123.3948 | 122.8578 | 123.2579 | -0.25562
1013.2812 | 123.5229 | -122.9187 | 0.41199 | 0.087637 | 0.036304 | -4.1882e-05 | -0.019266 | -0.046796 | 0.11629 | 0.043632 | 0.13595 | 0.0040533 | -0.030545 | 0.099201 | 0.073744 | 0.30322 | 0.34022 | 0.2846 | 0.34057 | 0.03699 | 0.43957 | 0.037679 | 0.30782 | 0.31171 | 0.29621 | 0.35922 | 0.45783 | -0.10214 | 0.14721 | 122.9564 | -0.071421 | 123.2219 | 123.2033 | 0.24692 | -0.375 | 0.027588 | 123.0659 | -0.052769 | 123.2265 | 123.2149 | 0.149 | 0.045844 | -0.51412 | 123.2593 | 122.9557 | 123.3583 | 123.2589 | -0.37431 | 123.2779 | 123.3765 | 122.8166 | 123.2304 | -0.26478
1014.3125 | 123.4177 | -122.9874 | 0.42114 | 0.041851 | 0.037372 | 0.0020951 | -0.019266 | -0.047865 | 0.11629 | 0.043632 | 0.13809 | 0.0061893 | -0.029477 | 0.099201 | 0.072676 | 0.3078 | 0.34022 | 0.2846 | 0.34514 | 0.069043 | 0.44415 | 0.0331 | 0.29866 | 0.30713 | 0.29163 | 0.35922 | 0.45325 | -0.10671 | 0.15179 | 123.0205 | -0.075998 | 123.2952 | 123.272 | 0.2515 | -0.3521 | 0.023011 | 123.1392 | -0.061925 | 123.286 | 123.279 | 0.13984 | 0.032109 | -0.52786 | 123.3325 | 123.0564 | 123.4315 | 123.3276 | -0.38804 | 123.3466 | 123.4406 | 122.8807 | 123.2945 | -0.26935
1015.2812 | 123.5596 | -122.9507 | 0.38452 | 0.057113 | 0.038441 | 0.0020951 | -0.022471 | -0.047865 | 0.11736 | 0.058893 | 0.13702 | 0.0029843 | -0.029477 | 0.10027 | 0.073744 | 0.29406 | 0.33565 | 0.27544 | 0.34514 | 0.059885 | 0.43957 | 0.023942 | 0.29408 | 0.29797 | 0.29621 | 0.35464 | 0.45783 | -0.10671 | 0.14263 | 122.9747 | -0.039376 | 123.2448 | 123.2262 | 0.2515 | -0.32464 | 0.055054 | 123.0934 | -0.029882 | 123.2448 | 123.247 | 0.15358 | 0.07331 | -0.49123 | 123.2959 | 123.0106 | 123.3903 | 123.2864 | -0.36058 | 123.3054 | 123.4086 | 122.844 | 123.2487 | -0.24189
1016.2812 | 123.5596 | -122.937 | 0.40283 | 0.072375 | 0.034167 | 0.0031631 | -0.019266 | -0.046796 | 0.11629 | 0.058893 | 0.13702 | 0.0040533 | -0.028409 | 0.098132 | 0.074812 | 0.3078 | 0.33565 | 0.27087 | 0.33599 | 0.069043 | 0.435 | 0.0331 | 0.29866 | 0.30713 | 0.29621 | 0.35464 | 0.45783 | -0.10671 | 0.15179 | 122.9701 | -0.066844 | 123.2448 | 123.2079 | 0.23777 | -0.33379 | 0.032165 | 123.0888 | -0.048193 | 123.2357 | 123.2332 | 0.14442 | 0.054999 | -0.50955 | 123.273 | 123.0061 | 123.372 | 123.2727 | -0.36973 | 123.2917 | 123.3948 | 122.8303 | 123.2441 | -0.25104
1017.2812 | 123.4268 | -122.9691 | 0.42114 | 0.041851 | 0.035235 | 0.0020951 | -0.019266 | -0.046796 | 0.11736 | 0.058893 | 0.13489 | 0.0051213 | -0.029477 | 0.097064 | 0.072676 | 0.30322 | 0.34022 | 0.2846 | 0.34514 | 0.046148 | 0.44873 | 0.028521 | 0.30324 | 0.30713 | 0.29163 | 0.35464 | 0.44867 | -0.12045 | 0.14721 | 122.9976 | -0.075998 | 123.2723 | 123.2537 | 0.25608 | -0.37499 | 0.027589 | 123.1163 | -0.066504 | 123.2723 | 123.2607 | 0.14442 | 0.027531 | -0.54159 | 123.3142 | 123.0152 | 123.4178 | 123.3093 | -0.39262 | 123.3237 | 123.4177 | 122.8486 | 123.2762 | -0.27393
1018.2812 | 123.5321 | -122.9599 | 0.39368 | 0.057113 | 0.036304 | 0.0010261 | -0.020335 | -0.047865 | 0.11843 | 0.089415 | 0.13702 | 0.0029843 | -0.029477 | 0.099201 | 0.072676 | 0.30322 | 0.33107 | 0.27544 | 0.33141 | 0.050727 | 0.435 | 0.0331 | 0.29408 | 0.30255 | 0.28247 | 0.35006 | 0.44867 | -0.11129 | 0.13805 | 122.993 | -0.062268 | 123.2631 | 123.2353 | 0.24234 | -0.34295 | 0.04132 | 123.098 | -0.043616 | 123.254 | 123.2424 | 0.14442 | 0.054997 | -0.50497 | 123.2913 | 123.0106 | 123.3949 | 123.291 | -0.36058 | 123.31 | 123.4086 | 122.8486 | 123.2625 | -0.25562

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.1677 | 21.4941 | 20.56 | 20.6681
0.8323 | 21.4906 | 20.5617 | 20.6727
1.8323 | 21.4904 | 20.5598 | 20.6722
2.8323 | 21.5587 | 20.5585 | 20.6683
3.8323 | 22.0433 | 20.5652 | 20.6766
4.8323 | 23.2334 | 20.5676 | 20.6736
5.8323 | 25.1288 | 20.5588 | 20.6587
6.8323 | 27.671 | 20.5542 | 20.6737
7.8323 | 30.7085 | 20.561 | 20.6793
8.8323 | 34.2041 | 20.5612 | 20.6869
9.8323 | 38.071 | 20.5696 | 20.6836
10.8323 | 42.2453 | 20.5766 | 20.699
11.8323 | 46.6506 | 20.587 | 20.7148
12.8323 | 51.2455 | 20.5889 | 20.7264
13.8323 | 56.03 | 20.6092 | 20.7605
14.8323 | 61.0424 | 20.6246 | 20.788
15.8323 | 66.2384 | 20.6499 | 20.8273
16.8323 | 71.4784 | 20.6646 | 20.8661
17.8323 | 76.8916 | 20.6981 | 20.9298
18.8323 | 82.4414 | 20.739 | 20.9842
19.8323 | 88.0241 | 20.7811 | 21.0533
20.8323 | 93.7578 | 20.8176 | 21.1249
21.8323 | 99.5245 | 20.872 | 21.2059
22.8323 | 105.4188 | 20.9314 | 21.2987
23.8323 | 111.3775 | 20.9967 | 21.4033
24.8323 | 117.3557 | 21.0691 | 21.5202
25.8323 | 123.4049 | 21.1451 | 21.6478
26.8323 | 129.5201 | 21.2365 | 21.7854
27.8323 | 135.626 | 21.3357 | 21.9389
28.8323 | 141.7615 | 21.4377 | 22.1145
29.8323 | 147.8473 | 21.5558 | 22.2948
30.8323 | 153.9402 | 21.6865 | 22.4939
31.8323 | 160.019 | 21.8185 | 22.7084
32.8323 | 166.0489 | 21.9753 | 22.9305
33.8323 | 172.1233 | 22.132 | 23.1724
34.8323 | 178.0287 | 22.3047 | 23.4262
35.8323 | 184.0834 | 22.4901 | 23.7152
36.8323 | 190.1324 | 22.6826 | 24.0143
37.8323 | 195.9814 | 22.9026 | 24.3368
38.8323 | 201.9077 | 23.1274 | 24.6641
39.8323 | 207.9381 | 23.3673 | 25.0169
40.8323 | 213.9372 | 23.6155 | 25.3949
41.8323 | 219.8551 | 23.8852 | 25.796
42.8323 | 225.7659 | 24.1724 | 26.2108
43.8323 | 231.5843 | 24.4718 | 26.6482
44.8323 | 237.4195 | 24.7809 | 27.1105
45.8323 | 243.385 | 25.117 | 27.5757
46.8323 | 249.2164 | 25.4678 | 28.0787
47.8323 | 254.9522 | 25.8317 | 28.5851
48.8323 | 260.8164 | 26.2078 | 29.1271
49.8323 | 266.5952 | 26.6 | 29.6943
50.8323 | 272.5081 | 27.0158 | 30.2624
51.8323 | 278.3355 | 27.4446 | 30.8617
52.8323 | 284.0473 | 27.9127 | 31.4737
53.8323 | 289.7538 | 28.3708 | 32.1103
54.8323 | 295.4282 | 28.8475 | 32.7639
55.8323 | 301.0705 | 29.3496 | 33.4355
56.8323 | 306.6714 | 29.8601 | 34.1425
57.8323 | 312.1973 | 30.3922 | 34.8648
58.8323 | 317.719 | 30.9383 | 35.6187
59.8323 | 323.1326 | 31.5058 | 36.389
60.8323 | 328.4671 | 32.0915 | 37.1753
61.8323 | 333.9412 | 32.6904 | 37.9955
62.8323 | 339.3572 | 33.3138 | 38.8317
63.8323 | 344.7333 | 33.9568 | 39.7033
64.8323 | 350.2138 | 34.6096 | 40.6092
65.8323 | 355.6217 | 35.2835 | 41.5371
66.8323 | 360.8268 | 35.9825 | 42.4869
67.8323 | 366.1 | 36.6966 | 43.4542
68.8323 | 371.2277 | 37.4447 | 44.4435
69.8323 | 376.5023 | 38.1836 | 45.4427
70.8323 | 381.7558 | 38.9508 | 46.4564
71.8323 | 387.0578 | 39.7382 | 47.5037
72.8323 | 392.0866 | 40.5451 | 48.5633
73.8323 | 397.1216 | 41.3761 | 49.656
74.8323 | 402.3152 | 42.2355 | 50.7789
75.8323 | 407.4171 | 43.1252 | 51.9255
76.8323 | 412.3879 | 44.0411 | 53.1179
77.8323 | 417.2695 | 44.9941 | 54.3537
78.8323 | 422.0488 | 45.9783 | 55.6155
79.8323 | 426.9452 | 47.0021 | 56.9501
80.8323 | 431.9043 | 48.0533 | 58.3011
81.8323 | 436.4524 | 49.1219 | 59.6931
82.8323 | 440.5782 | 50.2251 | 61.1171
83.8323 | 444.3442 | 51.3567 | 62.5775
84.8323 | 447.7751 | 52.5038 | 64.0633
85.8323 | 450.9358 | 53.6642 | 65.5658
86.8323 | 453.9631 | 54.8512 | 67.1119
87.8323 | 456.937 | 56.0593 | 68.6451
88.8323 | 459.735 | 57.2718 | 70.1899
89.8479 | 462.1661 | 58.5119 | 71.7293
90.8323 | 464.5521 | 59.7529 | 73.2876
91.8323 | 466.9416 | 61.0037 | 74.8463
92.8479 | 469.1132 | 62.2764 | 76.4248
93.8323 | 470.9562 | 63.5494 | 77.9888
94.8323 | 472.5507 | 64.8367 | 79.5541
95.8323 | 473.8245 | 66.1234 | 81.136
96.8323 | 474.9877 | 67.4286 | 82.7072
97.8323 | 475.9588 | 68.7293 | 84.2919
98.8323 | 476.6811 | 70.0271 | 85.8851
99.8323 | 477.1649 | 71.3208 | 87.4437
100.8323 | 477.4818 | 72.6264 | 89.0032
101.8323 | 477.5607 | 73.9237 | 90.5413
102.8323 | 477.5876 | 75.2304 | 92.0685
103.8479 | 477.5595 | 76.5294 | 93.5875
104.8323 | 477.374 | 77.8101 | 95.1068
105.8323 | 477.203 | 79.0973 | 96.5808
106.8323 | 476.9343 | 80.3725 | 98.0494
107.8323 | 476.7067 | 81.6466 | 99.5073
108.8323 | 476.4047 | 82.9156 | 100.9484
109.8323 | 476.0694 | 84.1819 | 102.363
110.8323 | 475.7403 | 85.4512 | 103.7875
111.8323 | 475.3237 | 86.697 | 105.1712
112.8323 | 474.9402 | 87.9432 | 106.5514
113.8323 | 474.5446 | 89.184 | 107.8979
114.8323 | 474.1921 | 90.4068 | 109.233
115.8323 | 473.7885 | 91.626 | 110.5589
116.8323 | 473.4471 | 92.8414 | 111.8607
117.8323 | 473.159 | 94.0421 | 113.1574
118.8323 | 473.0368 | 95.2305 | 114.4219
119.8323 | 472.9195 | 96.4217 | 115.6652
120.8323 | 472.7726 | 97.5882 | 116.9024
121.8323 | 472.6732 | 98.7667 | 118.1193
122.8323 | 472.6041 | 99.9225 | 119.3154
123.8323 | 472.5531 | 101.088 | 120.504
124.8323 | 472.5564 | 102.2335 | 121.6792
125.8323 | 472.5551 | 103.3777 | 122.8414
126.8323 | 472.6168 | 104.523 | 123.9879
127.8323 | 472.7555 | 105.659 | 125.1277
128.8323 | 472.8805 | 106.7715 | 126.2523
129.8323 | 472.9625 | 107.8891 | 127.3718
130.8323 | 473.09 | 109.0039 | 128.4816
131.8323 | 473.325 | 110.1031 | 129.5707
132.8323 | 473.5175 | 111.2149 | 130.6519
133.8479 | 473.6595 | 112.3151 | 131.7214
134.8323 | 473.9102 | 113.4194 | 132.7793
135.8323 | 474.1162 | 114.4981 | 133.8193
136.8323 | 474.2763 | 115.5697 | 134.8644
137.8323 | 474.4699 | 116.6493 | 135.884
138.8323 | 474.8043 | 117.721 | 136.904
139.8323 | 475.1047 | 118.774 | 137.9087
140.8323 | 475.2973 | 119.8228 | 138.9105
141.8323 | 475.5236 | 120.8836 | 139.9136
142.8323 | 475.8711 | 121.929 | 140.8944
143.8323 | 476.0907 | 122.9759 | 141.891
144.8323 | 476.2095 | 124.0107 | 142.8688
145.8323 | 476.2948 | 125.0395 | 143.8328
146.8323 | 476.4816 | 126.0502 | 144.7937
147.8323 | 476.6285 | 127.0717 | 145.7499
148.8323 | 476.8536 | 128.0738 | 146.7007
149.8323 | 477.1192 | 129.0671 | 147.6427
150.8323 | 477.3255 | 130.0529 | 148.591
151.8323 | 477.3589 | 131.0205 | 149.5248
152.8323 | 477.4688 | 131.9892 | 150.4577
153.8323 | 477.46 | 132.9425 | 151.396
154.8323 | 477.3856 | 133.8952 | 152.326
155.8323 | 477.389 | 134.8221 | 153.254
156.8323 | 477.4095 | 135.7521 | 154.1792
157.8323 | 477.4578 | 136.6654 | 155.1
158.8323 | 477.3778 | 137.564 | 156.0208
159.8323 | 477.4963 | 138.4569 | 156.9301
160.8323 | 477.5376 | 139.3477 | 157.8373
161.8323 | 477.4563 | 140.2178 | 158.7466
162.8323 | 477.4781 | 141.1066 | 159.6524
163.8323 | 477.6064 | 141.9827 | 160.557
164.8323 | 477.6511 | 142.8236 | 161.476
165.8323 | 477.6178 | 143.6667 | 162.3709
166.8323 | 477.5825 | 144.5072 | 163.254
167.8323 | 477.5038 | 145.3483 | 164.1369
168.8323 | 477.5244 | 146.1769 | 165.0112
169.8323 | 477.6427 | 147.0104 | 165.8788
170.8323 | 477.7542 | 147.8565 | 166.7364
171.8323 | 477.8384 | 148.6979 | 167.5943
172.8323 | 477.944 | 149.5571 | 168.4507
173.8323 | 478.0687 | 150.4034 | 169.3061
174.8323 | 478.1558 | 151.2536 | 170.1529
175.8323 | 478.1161 | 152.1389 | 171.02
176.8323 | 478.2106 | 152.9725 | 171.8722
177.8323 | 478.2468 | 153.8549 | 172.7134
178.8323 | 478.1319 | 154.7113 | 173.5665
179.8323 | 478.078 | 155.5664 | 174.406
180.8323 | 478.0177 | 156.4278 | 175.2427
181.8323 | 478.0374 | 157.2886 | 176.0785
182.8323 | 478.1051 | 158.1483 | 176.9185
183.8323 | 478.0813 | 158.9991 | 177.7683
184.8323 | 478.0159 | 159.8753 | 178.6149
185.8323 | 477.8259 | 160.74 | 179.4568
186.8323 | 477.8014 | 161.6187 | 180.3071
187.8323 | 477.7674 | 162.4959 | 181.1805
188.8323 | 477.9013 | 163.369 | 182.045
189.8323 | 477.8905 | 164.2656 | 182.9083
190.8323 | 478.0056 | 165.1461 | 183.7668
191.8323 | 478.0214 | 166.023 | 184.6228
192.8323 | 477.9634 | 166.9114 | 185.4929
193.8479 | 478.0413 | 167.7908 | 186.3668
194.8323 | 478.0171 | 168.6767 | 187.2404
195.8323 | 477.87 | 169.5582 | 188.1043
196.8323 | 477.8085 | 170.444 | 188.9674
197.8323 | 477.7154 | 171.3488 | 189.8464
198.8323 | 477.7108 | 172.2333 | 190.7119
199.8323 | 477.6914 | 173.1285 | 191.5676
200.8323 | 477.6795 | 174.0102 | 192.4188
201.8323 | 477.5898 | 174.8998 | 193.2624
202.8323 | 477.5752 | 175.796 | 194.1066
203.8323 | 477.5356 | 176.676 | 194.9611
204.8323 | 477.4778 | 177.5717 | 195.8015
205.8323 | 477.4466 | 178.4632 | 196.6559
206.8323 | 477.4648 | 179.3497 | 197.4971
207.8323 | 477.5584 | 180.2492 | 198.3444
208.8323 | 477.5024 | 181.1632 | 199.1839
209.8323 | 477.5805 | 182.0508 | 200.0242
210.8323 | 477.6513 | 182.95 | 200.881
211.8323 | 477.7634 | 183.8383 | 201.7116
212.8323 | 477.7675 | 184.749 | 202.5546
213.8323 | 477.7806 | 185.6425 | 203.3877
214.8323 | 477.6565 | 186.5379 | 204.2195
215.8323 | 477.6123 | 187.4344 | 205.0562
216.8323 | 477.5324 | 188.324 | 205.8774
217.8323 | 477.573 | 189.2255 | 206.7065
218.8323 | 477.5702 | 190.1162 | 207.5145
219.8323 | 477.3743 | 191.0221 | 208.3299
220.8323 | 477.2897 | 191.9115 | 209.1462
221.8323 | 477.3203 | 192.8084 | 209.9565
222.8323 | 477.1551 | 193.6931 | 210.7707
223.8323 | 477.199 | 194.593 | 211.5724
224.8323 | 477.3255 | 195.4689 | 212.3684
225.8323 | 477.4009 | 196.3493 | 213.1716
226.8323 | 477.4021 | 197.2318 | 213.9638
227.8323 | 477.3415 | 198.1118 | 214.7565
228.8323 | 477.4486 | 198.9719 | 215.5396
229.8323 | 477.4816 | 199.8354 | 216.3272
230.8323 | 477.3494 | 200.6992 | 217.098
231.8323 | 477.2622 | 201.5591 | 217.8827
232.8323 | 477.2796 | 202.3977 | 218.6529
233.8323 | 477.3083 | 203.2408 | 219.4268
234.8323 | 477.3057 | 204.0361 | 220.2133
235.8323 | 477.2102 | 204.8391 | 220.98
236.8323 | 477.11 | 205.6641 | 221.7598
237.8323 | 477.0124 | 206.5022 | 222.5445
238.8323 | 476.9925 | 207.3297 | 223.3198
239.8323 | 476.9953 | 208.1155 | 224.1071
240.8323 | 477.0054 | 208.8507 | 225.0024
241.8323 | 477.0832 | 209.4379 | 225.8517
242.8323 | 477.1081 | 209.8895 | 226.6478
243.8323 | 477.1171 | 210.3333 | 227.4769
244.8323 | 477.1716 | 210.7262 | 228.3575
245.8323 | 477.2642 | 211.0765 | 229.2396
246.8323 | 477.2531 | 211.1354 | 230.1087
247.8323 | 477.2209 | 210.8438 | 230.9442
248.8323 | 477.1087 | 210.4211 | 231.7982
249.8323 | 477.1394 | 210.0064 | 232.6485
250.8323 | 477.2312 | 209.693 | 233.4675
251.8323 | 477.2884 | 209.5228 | 234.2688
252.8323 | 477.2738 | 209.4843 | 235.0448
253.8323 | 477.2194 | 209.5581 | 235.8512
254.8323 | 477.2149 | 209.7043 | 236.6986
255.8323 | 477.1776 | 209.9294 | 237.645
256.8323 | 477.1762 | 210.1971 | 238.6775
257.8323 | 477.1472 | 210.486 | 239.6654
258.8323 | 477.0948 | 210.8123 | 240.713
259.8323 | 477.0295 | 211.1462 | 241.7559
260.8323 | 476.9822 | 211.5049 | 242.7644
261.8323 | 476.9146 | 211.8731 | 243.7012
262.8323 | 476.8362 | 212.2697 | 244.5763
263.8323 | 476.8018 | 212.7204 | 245.5827
264.8323 | 476.8901 | 213.1946 | 246.7487
265.8323 | 476.8886 | 213.6609 | 248.0577
266.8323 | 476.9018 | 214.1278 | 249.1494
267.8323 | 476.871 | 214.5616 | 250.2689
268.8323 | 476.7723 | 214.9837 | 251.1038
269.8323 | 476.6491 | 215.4089 | 251.8798
270.8323 | 476.496 | 215.8032 | 252.5855
271.8323 | 476.4531 | 216.2035 | 253.3547
272.8323 | 476.39 | 216.5786 | 253.9962
273.8323 | 476.3152 | 216.9376 | 254.5928
274.8323 | 476.3491 | 217.2964 | 255.1396
275.8323 | 476.6359 | 217.649 | 255.7456
276.8323 | 476.9462 | 218.0275 | 256.1965
277.8323 | 477.4897 | 218.4174 | 256.5951
278.8323 | 478.0519 | 218.822 | 257.118
279.8323 | 478.4959 | 219.2492 | 257.6699
280.8323 | 478.9033 | 219.6931 | 258.2603
281.8323 | 479.072 | 220.181 | 258.9663
282.8323 | 479.0241 | 220.695 | 259.5178
283.8323 | 478.998 | 221.3024 | 259.1723
284.8323 | 478.9811 | 222.0145 | 260.3343
285.8323 | 478.7888 | 222.7555 | 261.1072
286.8323 | 478.6129 | 223.5616 | 261.5535
287.8323 | 478.39 | 225.4043 | 262.1282
288.8323 | 478.098 | 226.296 | 262.5561
289.8323 | 477.7385 | 227.3118 | 262.2925
290.8323 | 477.258 | 228.4199 | 261.7745
291.8323 | 476.7785 | 229.4759 | 261.6052
292.8323 | 476.2244 | 230.5869 | 261.6019
293.8323 | 475.6151 | 231.7682 | 261.6411
294.8323 | 475.1522 | 233.1012 | 261.7769
295.8323 | 474.7752 | 234.4779 | 262.0792
296.8323 | 474.3801 | 236.2717 | 262.351
297.8323 | 473.9211 | 238.2135 | 262.5152
298.8323 | 473.4054 | 240.0756 | 262.7162
299.8323 | 472.9028 | 242.0628 | 262.9975
300.8323 | 472.3404 | 244.167 | 263.299
301.8323 | 471.8969 | 246.5216 | 263.5992
302.8323 | 471.4416 | 249.164 | 264.0896
303.8323 | 471.0172 | 252.5162 | 264.7643
304.8323 | 470.6237 | 256.5301 | 265.5837
305.8323 | 470.1911 | 260.3629 | 266.4832
306.8323 | 469.7109 | 263.3405 | 267.5091
307.8323 | 469.3108 | 266.0404 | 268.5789
308.8323 | 469.0006 | 268.9356 | 269.6229
309.8323 | 468.6371 | 271.5644 | 270.6938
310.8323 | 468.3699 | 273.9673 | 271.8361
311.8323 | 468.1515 | 276.2382 | 273.6954
312.8323 | 467.9286 | 278.4094 | 275.3802
313.8323 | 467.5914 | 280.7043 | 277.1091
314.8323 | 467.4331 | 282.9486 | 278.8146
315.8323 | 467.2808 | 284.6957 | 280.4674
316.8323 | 467.049 | 286.7561 | 281.9391
317.8323 | 466.7774 | 288.8996 | 283.6499
318.8323 | 466.6564 | 290.9518 | 285.5
319.8323 | 466.6651 | 292.8978 | 287.0409
320.8323 | 466.5174 | 294.9212 | 288.6574
321.8323 | 466.3075 | 297.3746 | 290.3558
322.8323 | 466.2169 | 299.1907 | 291.821
323.8323 | 466.2617 | 301.0724 | 293.3599
324.8323 | 466.2892 | 303.1175 | 295.3014
325.8323 | 466.2634 | 305.0974 | 297.2814
326.8323 | 466.1493 | 307.4486 | 299.3623
327.8323 | 466.0895 | 309.318 | 301.5793
328.8323 | 466.1816 | 311.3855 | 303.5569
329.8323 | 466.2388 | 313.6154 | 305.9327
330.8323 | 466.1643 | 315.519 | 308.0452
331.8323 | 466.171 | 317.9561 | 310.5921
332.8323 | 466.2648 | 320.3692 | 312.5984
333.8323 | 466.2834 | 321.8812 | 314.2286
334.8323 | 466.2342 | 323.9773 | 315.4107
335.8323 | 466.1979 | 326.0378 | 317.4212
336.8323 | 466.2084 | 327.9026 | 318.8922
337.8479 | 466.2543 | 329.9404 | 320.3673
338.8323 | 466.2761 | 331.2822 | 322.0426
339.8323 | 466.2279 | 333.2561 | 324.1291
340.8323 | 466.247 | 334.8293 | 326.2441
341.8323 | 466.3071 | 336.2867 | 328.1568
342.8323 | 466.4232 | 338.163 | 330.2425
343.8479 | 466.4567 | 340.3957 | 332.3007
344.8323 | 466.4807 | 342.9544 | 334.7561
345.8323 | 466.4761 | 344.0186 | 336.3474
346.8323 | 466.5351 | 345.683 | 338.9335
347.8323 | 466.6536 | 346.5359 | 341.0245
348.8323 | 466.7387 | 347.8308 | 343.3667
349.8323 | 466.777 | 349.3716 | 346.0188
350.8323 | 466.7558 | 352.3954 | 348.8768
351.8323 | 466.7425 | 354.3796 | 350.9188
352.8323 | 466.814 | 355.7942 | 353.2264
353.8323 | 466.8111 | 356.4861 | 354.846
354.8323 | 466.7914 | 357.4442 | 356.4922
355.8479 | 466.7692 | 358.8366 | 358.6005
356.8323 | 466.7691 | 361.6942 | 360.0753
357.8323 | 466.7981 | 362.7803 | 362.1874
358.8323 | 466.8457 | 363.0754 | 364.2484
359.8323 | 466.9249 | 366.8729 | 366.1638
360.8323 | 466.8863 | 368.2469 | 368.1001
361.8323 | 466.8556 | 367.7481 | 370.518
362.8323 | 466.8703 | 368.8456 | 372.5707
363.8323 | 466.9739 | 370.7294 | 374.6638
364.8323 | 466.9742 | 373.1992 | 375.9788
365.8323 | 466.9713 | 374.3119 | 378.2906
366.8323 | 467.0123 | 374.0535 | 379.6156
367.8323 | 467.0573 | 376.4312 | 382.0775
368.8323 | 467.0749 | 380.5196 | 383.7487
369.8323 | 467.0462 | 380.5596 | 385.1803
370.8323 | 466.9519 | 382.2657 | 386.7991
371.8323 | 466.932 | 383.4933 | 388.7827
372.8323 | 467.0436 | 383.8576 | 390.3355
373.8323 | 467.0329 | 392.0737 | 391.4316
374.8323 | 467.0123 | 388.8765 | 392.8231
375.8323 | 467.0595 | 392.2544 | 394.1484
376.8323 | 467.0052 | 390.2297 | 395.323
377.8323 | 466.9628 | 391.6998 | 397.377
378.8323 | 466.9176 | 395.1764 | 398.8658
379.8323 | 466.8828 | 395.4426 | 400.3433
380.8323 | 466.8842 | 399.4206 | 401.8323
381.8323 | 466.8941 | 400.0695 | 403.4881
382.8323 | 466.8592 | 400.944 | 404.7411
383.8323 | 466.8882 | 401.7541 | 405.9997
384.8323 | 466.928 | 404.6292 | 407.3239
385.8323 | 466.91 | 409.9214 | 408.3003
386.8323 | 466.8395 | 406.9198 | 410.6046
387.8323 | 466.7766 | 410.7056 | 411.6033
388.8323 | 466.696 | 411.0298 | 413.2416
389.8323 | 466.7061 | 415.0941 | 414.5489
390.8323 | 466.7274 | 416.3876 | 414.7559
391.8323 | 466.7997 | 416.6 | 415.7215
392.8323 | 466.8176 | 417.1445 | 416.9904
393.8323 | 466.7847 | 418.6066 | 418.6
394.8323 | 466.8397 | 420.4209 | 419.5864
395.8323 | 466.8384 | 420.1289 | 420.5558
396.8323 | 466.8219 | 422.3188 | 421.7211
397.8323 | 466.8304 | 423.2877 | 422.7686
398.8323 | 466.8339 | 422.8116 | 423.8148
399.8323 | 466.843 | 425.5973 | 424.8868
400.8323 | 466.8989 | 426.0933 | 425.7743
401.8323 | 466.8282 | 428.6157 | 427.3056
402.8323 | 466.7904 | 426.8555 | 428.604
403.8323 | 466.8091 | 431.3338 | 429.9278
404.8323 | 466.7811 | 429.7288 | 430.8225
405.8323 | 466.789 | 432.3377 | 431.2352
406.8323 | 466.752 | 432.8106 | 432.6486
407.8323 | 466.7186 | 432.3299 | 433.9567
408.8323 | 466.7348 | 435.7717 | 434.8822
409.8323 | 466.7009 | 434.0254 | 435.4842
410.8323 | 466.6642 | 437.1689 | 436.9327
411.8323 | 466.6325 | 436.1123 | 437.744
412.8323 | 466.6272 | 438.8231 | 438.8862
413.8323 | 466.6412 | 439.5471 | 438.9309
414.8323 | 466.5824 | 438.912 | 439.7076
415.8323 | 466.5347 | 439.844 | 440.4933
416.8323 | 466.5015 | 439.0947 | 441.2721
417.8323 | 466.4866 | 439.3954 | 441.768
418.8323 | 466.4304 | 439.9369 | 442.332
419.8323 | 466.5117 | 438.6412 | 443.2015
420.8323 | 466.5029 | 438.8462 | 443.3395
421.8323 | 466.4902 | 437.8658 | 443.5936
422.8323 | 466.4394 | 436.004 | 444.6133
423.8323 | 466.4227 | 436.2032 | 444.4843
424.8323 | 466.3433 | 432.4447 | 445.1102
425.8323 | 466.2609 | 433.6007 | 445.3225
426.8323 | 466.2094 | 432.7097 | 446.2735
427.8323 | 466.1596 | 431.8612 | 446.8041
428.8323 | 466.1074 | 430.1053 | 446.4002
429.8323 | 466.0287 | 429.2385 | 446.7326
430.8323 | 466.0214 | 428.1381 | 447.676
431.8323 | 466.1064 | 428.1802 | 448.125
432.8323 | 466.0889 | 427.2306 | 447.7939
433.8323 | 465.9805 | 426.3678 | 448.9122
434.8323 | 465.9839 | 425.6869 | 449.0713
435.8323 | 465.9843 | 424.7912 | 449.6293
436.8323 | 465.9171 | 424.9644 | 450.0579
437.8323 | 465.8928 | 425.1431 | 450.9684
438.8323 | 465.8548 | 425.084 | 450.9199
439.8323 | 465.8595 | 425.3063 | 451.7423
440.8323 | 465.8163 | 425.6079 | 452.6839
441.8323 | 465.8085 | 426.1129 | 452.7379
442.8323 | 465.8264 | 426.8156 | 453.398
443.8323 | 465.8194 | 427.3896 | 454.1184
444.8323 | 465.8384 | 428.3488 | 454.8682
445.8323 | 465.8854 | 429.2927 | 455.3741
446.8323 | 465.9437 | 430.7337 | 456.2412
447.8323 | 466.0249 | 432.8588 | 457.3034
448.8323 | 466.0861 | 434.9123 | 457.7633
449.8323 | 466.039 | 436.5252 | 458.4064
450.8323 | 466.0481 | 438.5039 | 459.4241
451.8323 | 466.0656 | 440.836 | 459.7521
452.8323 | 466.0375 | 441.978 | 460.2929
453.8323 | 465.9882 | 444.1142 | 461.5148
454.8323 | 465.9906 | 445.6252 | 462.3578
455.8323 | 466.0149 | 447.2578 | 463.1467
456.8323 | 466.06 | 448.8176 | 464.1122
457.8323 | 466.0143 | 450.5593 | 464.7238
458.8323 | 465.9793 | 451.9736 | 465.505
459.8323 | 465.9816 | 454.1928 | 466.3908
460.8323 | 465.92 | 456.1615 | 467.2052
461.8323 | 465.9711 | 457.9512 | 468.0868
462.8323 | 465.9925 | 459.7345 | 469.0989
463.8323 | 465.995 | 461.6599 | 469.9044
464.8323 | 465.9585 | 463.3098 | 470.8214
465.8323 | 465.9961 | 465.0217 | 471.9099
466.8323 | 465.9421 | 466.858 | 472.6312
467.8323 | 465.905 | 468.8302 | 473.5556
468.8323 | 465.8476 | 470.8655 | 474.3225
469.8323 | 465.8422 | 472.5768 | 475.2282
470.8323 | 465.7986 | 474.101 | 475.9615
471.8323 | 465.7149 | 475.8204 | 476.6949
472.8323 | 465.7142 | 478.6292 | 477.3149
473.8323 | 465.7078 | 481.0983 | 478.1656
474.8323 | 465.6477 | 483.6633 | 478.9824
475.8323 | 465.6137 | 486.1175 | 479.6007
476.8323 | 465.6336 | 489.4168 | 480.2333
477.8323 | 465.4707 | 491.529 | 481.0344
478.8323 | 465.4181 | 493.7534 | 481.7711
479.8323 | 465.4478 | 496.0334 | 482.5693
480.8323 | 465.3676 | 498.7394 | 483.2295
481.8323 | 465.3534 | 500.614 | 483.901
482.8323 | 465.2986 | 502.2377 | 484.5092
483.8323 | 465.2305 | 503.4934 | 485.1563
484.8323 | 465.1927 | 505.0257 | 485.7993
485.8323 | 465.216 | 506.3139 | 486.6331
486.8479 | 465.1516 | 508.8025 | 487.3555
487.8323 | 465.0786 | 510.9809 | 488.0795
488.8323 | 465.0845 | 512.7722 | 488.748
489.8323 | 465.0322 | 515.2187 | 489.5454
490.8323 | 464.9603 | 517.352 | 490.2179
491.8479 | 464.9003 | 520.5119 | 491.0486
492.8323 | 464.9998 | 522.9485 | 491.7617
493.8479 | 465.0465 | 525.2169 | 492.4313
494.8323 | 465.0485 | 525.4761 | 493.1821
495.8479 | 464.9008 | 526.9505 | 493.8937
496.8479 | 464.7712 | 528.328 | 494.4903
497.8479 | 464.7187 | 529.5441 | 495.0629
498.8479 | 464.7401 | 531.7461 | 495.7323
499.8479 | 464.7197 | 530.9841 | 496.4523
500.8323 | 464.7004 | 529.1393 | 497.1585
501.8479 | 464.632 | 528.8818 | 497.7911
502.8323 | 464.5726 | 529.6196 | 498.4236
503.8323 | 464.562 | 530.6666 | 499.1197
504.8323 | 464.5211 | 530.4008 | 499.8272
505.8323 | 464.5435 | 529.022 | 500.437
506.8323 | 464.4793 | 527.9068 | 501.1686
507.8323 | 464.4185 | 526.9966 | 501.9919
508.8323 | 464.289 | 526.1218 | 502.6664
509.8323 | 464.1781 | 525.2585 | 503.4652
510.8323 | 464.1086 | 524.3937 | 503.9789
511.8323 | 464.0785 | 524.1976 | 504.6527
512.8323 | 464.0898 | 522.7993 | 505.1386
513.8323 | 463.9982 | 522.1415 | 505.7418
514.8479 | 463.9208 | 521.7332 | 506.057
515.8323 | 463.8333 | 522.1217 | 506.5212
516.8323 | 463.7043 | 522.8265 | 506.9893
517.8323 | 463.668 | 521.7591 | 507.4175
518.8323 | 463.6316 | 521.2875 | 507.7942
519.8323 | 463.5773 | 520.6922 | 508.1117
520.8323 | 463.541 | 520.3987 | 507.9059
521.8323 | 463.5398 | 519.6344 | 506.3226
522.8323 | 463.4785 | 519.3596 | 505.6374
523.8323 | 463.4669 | 519.5286 | 505.3909
524.8323 | 463.5026 | 518.8946 | 504.9846
525.8323 | 463.4253 | 518.2592 | 504.7626
526.8323 | 463.3184 | 517.3295 | 504.7187
527.8323 | 463.1096 | 516.9245 | 504.6691
528.8323 | 463.0173 | 516.6523 | 504.7861
529.8323 | 462.9542 | 516.136 | 504.8599
530.8323 | 463.0192 | 516.1483 | 504.9252
531.8323 | 463.0934 | 515.9626 | 504.8654
532.8323 | 463.068 | 516.1641 | 504.943
533.8323 | 463.0854 | 516.4643 | 504.8608
534.8323 | 463.1519 | 516.5265 | 505.0808
535.8323 | 463.2049 | 516.0949 | 505.1769
536.8323 | 463.2145 | 516.2206 | 505.2861
537.8323 | 463.2179 | 516.066 | 505.4208
538.8323 | 463.3017 | 516.362 | 505.6715
539.8323 | 463.4027 | 516.6942 | 506.048
540.8323 | 463.512 | 516.8 | 506.0626
541.8323 | 463.6461 | 516.8969 | 506.2158
542.8323 | 463.7198 | 517.0469 | 506.4489
543.8323 | 463.8561 | 517.3484 | 506.7796
544.8323 | 464.0014 | 517.5916 | 507.1808
545.8323 | 464.1664 | 518.0419 | 507.6246
546.8323 | 464.278 | 518.0054 | 508.2862
547.8323 | 464.2751 | 517.652 | 508.7788
548.8323 | 464.2901 | 517.7703 | 509.0912
549.8323 | 464.3298 | 518.4164 | 509.288
550.8323 | 464.3867 | 519.164 | 509.1785
551.8323 | 464.4661 | 519.2471 | 509.4362
552.8323 | 464.556 | 520.201 | 509.6476
553.8323 | 464.6547 | 520.1996 | 509.884
554.8323 | 464.7734 | 520.9255 | 510.0636
555.8479 | 464.8581 | 521.4755 | 510.1924
556.8479 | 464.9838 | 521.7634 | 510.3898
557.8323 | 464.9384 | 521.8315 | 510.5607
558.8479 | 464.8681 | 522.2623 | 510.6361
559.8479 | 464.8784 | 522.857 | 510.7417
560.8323 | 464.8653 | 523.4105 | 510.9076
561.8323 | 464.946 | 524.296 | 510.9287
562.8323 | 464.9331 | 524.675 | 511.0871
563.8323 | 464.9429 | 525.31 | 511.3281
564.8323 | 464.913 | 525.6513 | 511.5446
565.8479 | 465.0013 | 525.7992 | 511.8673
566.8323 | 465.0335 | 526.129 | 512.1569
567.8323 | 465.059 | 527.3825 | 512.5535
568.8479 | 465.0762 | 527.6719 | 512.673
569.8323 | 465.1114 | 527.6269 | 512.6935
570.8323 | 465.0853 | 528.0316 | 512.7698
571.8323 | 465.072 | 528.9906 | 512.7425
572.8323 | 465.0111 | 529.2142 | 512.924
573.8323 | 465.0091 | 529.2841 | 513.0254
574.8479 | 464.9708 | 529.5479 | 513.3165
575.8479 | 464.9402 | 529.9834 | 513.4544
576.8479 | 464.9936 | 530.083 | 513.5474
577.8323 | 465.0193 | 531.0322 | 513.6474
578.8479 | 465.0643 | 531.1451 | 513.7109
579.8479 | 465.0244 | 531.0365 | 513.8281
580.8323 | 464.9991 | 531.2749 | 514.0686
581.8479 | 465.0031 | 531.4383 | 514.2422
582.8479 | 465.095 | 531.8528 | 514.5267
583.8479 | 465.1906 | 532.3571 | 514.6609
584.8479 | 465.226 | 533.1356 | 514.8123
585.8479 | 465.2469 | 533.5644 | 515.0059
586.8479 | 465.287 | 534.1941 | 515.1805
587.8479 | 465.3428 | 535.1491 | 515.4133
588.8479 | 465.3676 | 535.9118 | 515.6907
589.8479 | 465.4077 | 535.8332 | 515.746
590.8479 | 465.4266 | 535.9052 | 515.8119
591.8323 | 465.492 | 535.948 | 515.939
592.8479 | 465.4893 | 535.6738 | 515.8363
593.8479 | 465.6015 | 535.3472 | 515.8506
594.8479 | 465.7632 | 535.0889 | 515.824
595.8479 | 465.8047 | 534.9447 | 515.6735
596.8479 | 465.8785 | 535.0912 | 515.7222
597.8479 | 465.9849 | 534.8775 | 515.5947
598.8479 | 466.0583 | 535.1238 | 515.4514
599.8479 | 466.0954 | 535.144 | 515.475
600.8479 | 466.128 | 534.8663 | 515.48
601.8479 | 466.2112 | 535.159 | 515.3826
602.8323 | 466.1885 | 534.6553 | 515.2806
603.8323 | 466.1767 | 534.0637 | 515.0467
604.8323 | 466.0605 | 533.743 | 514.9128
605.8323 | 466.03 | 534.0475 | 514.6763
606.8323 | 466.0776 | 534.5145 | 514.4919
607.8323 | 466.0812 | 534.831 | 514.3063
608.8323 | 466.0842 | 535.295 | 514.0913
609.8323 | 465.9665 | 535.4023 | 514.0258
610.8323 | 465.8672 | 535.901 | 513.8579
611.8323 | 465.8414 | 536.3381 | 513.7307
612.8323 | 465.8144 | 536.1715 | 513.6089
613.8323 | 465.7484 | 537.1003 | 513.4186
614.8323 | 465.7197 | 537.3786 | 513.238
615.8323 | 465.7887 | 537.9168 | 513.0205
616.8323 | 465.8805 | 538.448 | 512.888
617.8323 | 465.8434 | 539.3428 | 512.6669
618.8323 | 465.766 | 540.3042 | 512.509
619.8323 | 465.7632 | 540.824 | 512.2942
620.8323 | 465.7538 | 541.1203 | 512.2697
621.8323 | 465.6686 | 541.428 | 512.202
622.8323 | 465.62 | 541.7382 | 512.1933
623.8323 | 465.5602 | 542.6087 | 512.2017
624.8323 | 465.543 | 543.0869 | 512.1893
625.8323 | 465.5404 | 543.8314 | 512.2385
626.8323 | 465.5234 | 544.3151 | 512.3042
627.8323 | 465.5502 | 544.8578 | 512.5433
628.8323 | 465.5188 | 545.2326 | 512.7259
629.8323 | 465.5125 | 545.239 | 512.9762
630.8323 | 465.4503 | 545.3326 | 513.1897
631.8323 | 465.3315 | 545.3877 | 513.4505
632.8323 | 465.2894 | 545.3991 | 513.7401
633.8323 | 465.1844 | 545.7869 | 514.1381
634.8323 | 465.1134 | 546.7427 | 513.9405
635.8323 | 465.1052 | 547.2678 | 514.4985
636.8323 | 465.1826 | 547.8595 | 515.2475
637.8479 | 465.2298 | 548.5721 | 515.7531
638.8479 | 465.206 | 548.9975 | 516.2965
639.8479 | 465.2005 | 549.5408 | 516.7199
640.8479 | 465.1589 | 550.0593 | 517.1211
641.8323 | 465.0771 | 550.3177 | 517.8542
642.8323 | 464.9403 | 550.8078 | 518.4297
643.8323 | 464.9011 | 551.2543 | 518.9058
644.8479 | 464.9745 | 551.6678 | 519.5148
645.8323 | 464.9827 | 552.7433 | 520.3702
646.8323 | 464.9454 | 553.4018 | 520.9806
647.8323 | 464.9045 | 553.7073 | 521.6027
648.8323 | 465.0044 | 553.9589 | 522.3405
649.8323 | 464.9693 | 554.9574 | 522.8964
650.8323 | 464.9472 | 555.4724 | 523.934
651.8323 | 464.9672 | 556.0904 | 524.6926
652.8323 | 464.899 | 557.277 | 525.5461
653.8323 | 464.8373 | 557.3178 | 526.2818
654.8323 | 464.8052 | 557.5064 | 526.5827
655.8323 | 464.8006 | 557.7948 | 527.3952
656.8323 | 464.7725 | 558.3594 | 527.9578
657.8323 | 464.77 | 558.3758 | 527.0453
658.8323 | 464.7644 | 559.2415 | 530.2088
659.8323 | 464.7561 | 559.8076 | 530.7522
660.8323 | 464.6572 | 560.6327 | 531.6315
661.8323 | 464.4428 | 561.6113 | 532.3314
662.8323 | 464.4014 | 561.8449 | 533.1219
663.8323 | 464.3749 | 562.8664 | 534.0701
664.8323 | 464.4324 | 563.9217 | 535.0046
665.8323 | 464.4639 | 565.2065 | 535.8488
666.8323 | 464.5812 | 566.2823 | 536.6437
667.8323 | 464.7303 | 567.5785 | 537.6507
668.8323 | 464.7879 | 568.5174 | 538.5591
669.8323 | 464.708 | 569.7347 | 539.4537
670.8323 | 464.6863 | 570.3936 | 540.4565
671.8323 | 464.8268 | 571.7137 | 541.3127
672.8323 | 464.935 | 572.227 | 542.3225
673.8323 | 464.9366 | 572.8037 | 543.2612
674.8323 | 464.9911 | 574.1403 | 544.4741
675.8323 | 465.047 | 574.9491 | 545.4173
676.8323 | 464.9536 | 575.4916 | 546.3187
677.8323 | 464.8569 | 576.1639 | 547.3376
678.8323 | 464.8465 | 576.3315 | 548.186
679.8323 | 464.9224 | 576.9674 | 549.1203
680.8323 | 464.9537 | 577.3362 | 549.8718
681.8323 | 464.8917 | 577.0358 | 550.5315
682.8323 | 464.8734 | 577.6563 | 551.4264
683.8323 | 464.9592 | 578.3777 | 552.3338
684.8323 | 465.0597 | 578.7234 | 552.9894
685.8323 | 465.1445 | 578.8755 | 553.7379
686.8323 | 465.1024 | 579.5218 | 554.4082
687.8323 | 465.0551 | 579.7136 | 555.0803
688.8323 | 464.9624 | 580.7031 | 555.7791
689.8323 | 464.8612 | 581.9065 | 556.6374
690.8323 | 464.8297 | 582.6759 | 557.3946
691.8323 | 464.8591 | 583.2404 | 558.0278
692.8323 | 464.9302 | 583.5012 | 558.8528
693.8323 | 464.8916 | 584.1298 | 559.6052
694.8323 | 464.8433 | 584.6445 | 560.3551
695.8323 | 464.8318 | 585.2005 | 560.8844
696.8323 | 464.8368 | 585.7921 | 561.511
697.8323 | 464.773 | 585.9304 | 562.2395
698.8323 | 464.7196 | 586.9006 | 562.8718
699.8323 | 464.706 | 587.4371 | 563.464
700.8323 | 464.744 | 588.0696 | 564.2784
701.8323 | 464.7809 | 588.9479 | 564.7699
702.8323 | 464.8172 | 590.0619 | 565.447
703.8323 | 464.8245 | 590.7817 | 566.0191
704.8323 | 464.7495 | 591.2431 | 566.6959
705.8323 | 464.669 | 591.7448 | 567.365
706.8323 | 464.6269 | 592.3459 | 567.7543
707.8323 | 464.6461 | 592.936 | 568.6066
708.8323 | 464.6612 | 593.2983 | 569.1504
709.8323 | 464.6683 | 593.7042 | 569.6632
710.8323 | 464.6854 | 594.3875 | 570.2699
711.8323 | 464.7285 | 594.5299 | 570.7575
712.8323 | 464.8363 | 595.0645 | 571.0095
713.8323 | 464.9701 | 595.3965 | 571.5143
714.8323 | 465.0343 | 596.2017 | 572.1368
715.8323 | 465.098 | 596.0893 | 572.6395
716.8323 | 465.1772 | 596.4828 | 572.8511
717.8323 | 465.2834 | 596.9215 | 573.426
718.8323 | 465.4355 | 597.0326 | 573.9988
719.8323 | 465.6239 | 596.9741 | 574.5627
720.8323 | 465.7772 | 597.0604 | 575.4066
721.8323 | 465.8865 | 597.2218 | 575.8065
722.8323 | 465.9939 | 597.5289 | 576.4096
723.8323 | 466.155 | 597.8058 | 576.9592
724.8323 | 466.2971 | 598.0199 | 577.56
725.8323 | 466.391 | 598.2827 | 578.1845
726.8323 | 466.4899 | 598.3982 | 578.5594
727.8323 | 466.6165 | 598.343 | 579.0811
728.8323 | 466.7357 | 598.8881 | 579.4043
729.8323 | 466.8693 | 599.1064 | 579.9824
730.8323 | 467.1268 | 599.4687 | 580.5641
731.8323 | 467.28 | 599.4844 | 580.961
732.8323 | 467.3463 | 599.5839 | 581.3519
733.8323 | 467.4384 | 599.4976 | 581.7267
734.8323 | 467.5318 | 599.6643 | 582.2957
735.8323 | 467.5804 | 600.2132 | 582.6945
736.8323 | 467.6473 | 600.4924 | 583.1397
737.8323 | 467.7672 | 600.4509 | 583.5826
738.8323 | 467.876 | 600.1255 | 583.8447
739.8323 | 467.9468 | 599.831 | 584.1151
740.8323 | 467.9821 | 600.1678 | 584.6352
741.8323 | 468.0355 | 600.628 | 585.0097
742.8323 | 468.102 | 601.0763 | 585.4076
743.8323 | 468.15 | 601.4655 | 585.7307
744.8323 | 468.1882 | 601.9037 | 586.016
745.8323 | 468.2582 | 602.2195 | 586.3058
746.8323 | 468.2725 | 602.1509 | 586.6881
747.8323 | 468.3166 | 602.3534 | 587.0902
748.8323 | 468.3914 | 602.2931 | 587.4313
749.8323 | 468.4544 | 601.9662 | 587.7292
750.8323 | 468.4703 | 601.9733 | 588.0755
751.8323 | 468.4121 | 602.1174 | 587.7877
752.8323 | 468.3505 | 602.5824 | 588.4093
753.8323 | 468.2686 | 602.7995 | 588.8847
754.8323 | 468.1946 | 603.2466 | 589.12
755.8323 | 468.1126 | 603.2909 | 589.1969
756.8323 | 468.0873 | 603.6559 | 589.5079
757.8323 | 468.1187 | 603.7733 | 589.5813
758.8323 | 468.0862 | 604.1442 | 589.7752
759.8323 | 468.0167 | 603.8848 | 589.9038
760.8323 | 467.9948 | 603.8321 | 589.9553
761.8323 | 467.8394 | 603.6628 | 589.9906
762.8323 | 467.7356 | 603.7854 | 590.06
763.8323 | 467.7077 | 604.1354 | 589.8059
764.8323 | 467.6484 | 604.3928 | 589.7524
765.8323 | 467.6294 | 604.1003 | 589.6583
766.8323 | 467.5987 | 604.1212 | 589.68
767.8323 | 467.5703 | 603.8284 | 589.5583
768.8323 | 467.5567 | 603.7681 | 589.6167
769.8323 | 467.5333 | 603.5961 | 589.6307
770.8323 | 467.4646 | 603.6226 | 589.5742
771.8323 | 467.3756 | 603.4746 | 589.5819
772.8323 | 467.2816 | 604.3733 | 589.5294
773.8323 | 467.1459 | 604.7827 | 589.5679
774.8323 | 467.0361 | 604.6375 | 589.4425
775.8323 | 466.9491 | 604.2031 | 589.3253
776.8323 | 466.8742 | 603.6358 | 589.2065
777.8323 | 466.8423 | 603.2815 | 589.1105
778.8323 | 466.8043 | 602.6537 | 588.9078
779.8323 | 466.8286 | 602.4651 | 588.7785
780.8323 | 466.89 | 602.0286 | 588.4745
781.8323 | 466.9169 | 601.5409 | 588.4841
782.8323 | 466.9297 | 600.9128 | 588.4706
783.8323 | 466.9059 | 600.6677 | 588.4086
784.8323 | 466.871 | 600.0388 | 588.4227
785.8323 | 466.8465 | 600.0458 | 588.5724
786.8323 | 466.8487 | 600.1139 | 588.6339
787.8323 | 466.8492 | 600.3958 | 588.6371
788.8323 | 466.7739 | 600.6497 | 588.6705
789.8323 | 466.7286 | 600.2649 | 588.6723
790.8323 | 466.7287 | 599.6943 | 588.6498
791.8323 | 466.7161 | 599.2302 | 588.2854
792.8323 | 466.6715 | 598.8749 | 588.2857
793.8323 | 466.6314 | 598.5484 | 588.3447
794.8323 | 466.5563 | 598.8059 | 588.2856
795.8323 | 466.5563 | 599.0073 | 588.0535
796.8323 | 466.5573 | 599.0561 | 587.878
797.8323 | 466.4925 | 598.9989 | 587.8087
798.8479 | 466.4769 | 599.2183 | 587.6309
799.8323 | 466.5225 | 599.5665 | 587.3442
800.8479 | 466.5159 | 599.5554 | 586.9078
801.8323 | 466.4697 | 599.3276 | 586.694
802.8323 | 466.4825 | 598.3727 | 586.0964
803.8323 | 466.5101 | 597.7248 | 585.8106
804.8323 | 466.5315 | 597.1228 | 585.5629
805.8323 | 466.5282 | 596.0242 | 585.5219
806.8323 | 466.4786 | 594.8246 | 585.0812
807.8323 | 466.4306 | 593.8491 | 584.9966
808.8323 | 466.4326 | 592.8654 | 585.1115
809.8323 | 466.4474 | 592.3319 | 584.9464
810.8323 | 466.4293 | 591.5549 | 584.9325
811.8323 | 466.387 | 591.3465 | 584.6027
812.8323 | 466.343 | 590.5918 | 584.6633
813.8323 | 466.3442 | 589.9671 | 584.6699
814.8323 | 466.3497 | 589.6587 | 584.5716
815.8323 | 466.3312 | 589.4442 | 584.6274
816.8323 | 466.3222 | 589.4613 | 584.451
817.8323 | 466.3028 | 589.0479 | 584.1346
818.8323 | 466.3174 | 588.6287 | 584.2151
819.8323 | 466.3214 | 588.3689 | 584.3312
820.8323 | 466.3474 | 588.7212 | 584.7401
821.8323 | 466.3543 | 588.6693 | 584.7319
822.8323 | 466.4139 | 589.0687 | 584.8371
823.8323 | 466.4711 | 589.2034 | 584.9745
824.8323 | 466.4848 | 589.6759 | 585.0831
825.8323 | 466.5166 | 589.608 | 585.4115
826.8323 | 466.5711 | 590.1286 | 585.4328
827.8323 | 466.5774 | 590.8482 | 585.6275
828.8323 | 466.6256 | 590.8718 | 585.8604
829.8323 | 466.69 | 590.8179 | 586.0379
830.8323 | 466.6927 | 591.2126 | 586.517
831.8323 | 466.7287 | 591.6505 | 586.7616
832.8323 | 466.7854 | 592.518 | 586.8777
833.8323 | 466.8188 | 592.7481 | 586.9385
834.8323 | 466.8684 | 593.1154 | 586.9557
835.8323 | 466.9227 | 594.0043 | 587.6684
836.8323 | 466.9927 | 594.2599 | 587.4434
837.8323 | 467.0103 | 593.7447 | 587.407
838.8323 | 467.0227 | 593.5928 | 587.7264
839.8323 | 467.0571 | 593.8459 | 588.2934
840.8323 | 467.0536 | 594.2685 | 588.7876
841.8323 | 467.0167 | 594.4903 | 588.8502
842.8323 | 467.009 | 594.5154 | 589.2338
843.8323 | 467.0312 | 594.3978 | 589.6128
844.8323 | 467.0739 | 594.2948 | 589.7855
845.8323 | 467.0588 | 594.4599 | 590.2376
846.8323 | 467.1034 | 594.3465 | 590.3795
847.8323 | 467.1549 | 594.3563 | 590.565
848.8323 | 467.2283 | 594.1667 | 590.9983
849.8323 | 467.2975 | 594.2651 | 591.341
850.8323 | 467.3667 | 594.556 | 591.5948
851.8323 | 467.3899 | 594.2155 | 591.5426
852.8323 | 467.3888 | 593.9376 | 591.5938
853.8323 | 467.3877 | 593.6604 | 591.8549
854.8323 | 467.3772 | 593.5905 | 591.9083
855.8323 | 467.3763 | 593.1214 | 592.0047
856.8323 | 467.4171 | 592.9223 | 591.6385
857.8323 | 467.4676 | 593.1851 | 591.5583
858.8323 | 467.4977 | 593.5596 | 591.515
859.8323 | 467.5055 | 594.3355 | 591.6169
860.8323 | 467.4642 | 594.7302 | 591.8241
861.8323 | 467.4273 | 594.3578 | 591.7654
862.8323 | 467.4558 | 593.8369 | 592.0328
863.8323 | 467.473 | 593.9807 | 592.1062
864.8323 | 467.498 | 593.4206 | 592.6559
865.8323 | 467.5187 | 593.6617 | 593.2206
866.8323 | 467.5243 | 593.1539 | 592.8143
867.8323 | 467.5491 | 593.7994 | 593.0807
868.8323 | 467.5827 | 594.7674 | 593.2215
869.8323 | 467.5981 | 595.7996 | 593.3628
870.8323 | 467.6567 | 596.0179 | 593.8669
871.8323 | 467.6957 | 595.6501 | 593.6907
872.8323 | 467.716 | 595.8726 | 593.827
873.8323 | 467.7057 | 595.286 | 594.1444
874.8323 | 467.714 | 594.5227 | 594.2245
875.8323 | 467.7396 | 594.7502 | 594.6771
876.8323 | 467.7852 | 594.7886 | 595.1722
877.8323 | 467.8152 | 594.3804 | 594.7334
878.8323 | 467.8284 | 593.8482 | 594.7426
879.8323 | 467.7952 | 593.1134 | 594.0998
880.8323 | 467.8015 | 592.7279 | 594.0122
881.8323 | 467.815 | 592.36 | 593.0401
882.8323 | 467.7854 | 592.0892 | 592.7793
883.8323 | 467.769 | 591.7701 | 592.6308
884.8323 | 467.7758 | 591.8484 | 592.1388
885.8323 | 467.7613 | 591.9859 | 592.1388
886.8323 | 467.7565 | 591.9525 | 591.24
887.8323 | 467.7621 | 591.7242 | 591.0468
888.8323 | 467.7512 | 591.2769 | 590.7922
889.8323 | 467.7381 | 592.4555 | 590.567
890.8323 | 467.7087 | 593.2606 | 590.8317
891.8323 | 467.708 | 593.3669 | 590.4888
892.8323 | 467.6925 | 593.7384 | 590.6162
893.8323 | 467.6473 | 593.6935 | 590.8849
894.8323 | 467.6226 | 593.9622 | 591.1567
895.8323 | 467.6014 | 594.3872 | 591.4138
896.8323 | 467.5867 | 594.9811 | 591.7215
897.8323 | 467.5792 | 595.7331 | 592.2123
898.8323 | 467.5683 | 596.3078 | 592.6755
899.8323 | 467.5733 | 597.0699 | 593.2114
900.8323 | 467.5687 | 598.0086 | 594.3676
901.8323 | 467.5989 | 598.161 | 594.5021
902.8323 | 467.5825 | 598.2519 | 594.792
903.8323 | 467.5765 | 598.0586 | 595.1655
904.8323 | 467.5874 | 597.739 | 595.2674
905.8323 | 467.5813 | 597.6907 | 595.6581
906.8323 | 467.6371 | 597.9817 | 595.5209
907.8323 | 467.6682 | 598.4996 | 595.9725
908.8323 | 467.7025 | 598.307 | 595.8094
909.8323 | 467.7013 | 598.4937 | 596.4485
910.8323 | 467.7115 | 598.4202 | 596.7111
911.8323 | 467.7 | 598.383 | 596.5665
912.8323 | 467.6949 | 598.7688 | 596.8568
913.8323 | 467.6891 | 598.8883 | 597.2381
914.8323 | 467.6811 | 599.0021 | 597.6217
915.8479 | 467.6924 | 598.9635 | 598.5072
916.8323 | 467.6848 | 599.033 | 598.3236
917.8323 | 467.6908 | 599.3456 | 598.4859
918.8323 | 467.7567 | 599.6503 | 598.8059
919.8323 | 467.7624 | 599.8213 | 599.412
920.8323 | 467.7498 | 600.0154 | 600.0931
921.8323 | 467.7643 | 599.9904 | 599.8415
922.8323 | 467.7743 | 600.3225 | 600.2654
923.8323 | 467.7536 | 600.3937 | 600.7232
924.8323 | 467.7548 | 600.4452 | 601.1913
925.8323 | 467.7529 | 600.6787 | 602.0893
926.8323 | 467.7857 | 600.7256 | 602.1185
927.8323 | 467.7807 | 600.9011 | 602.6292
928.8323 | 467.7815 | 600.8814 | 603.069
929.8323 | 467.8032 | 600.3423 | 603.5266
930.8323 | 467.8006 | 599.9951 | 604.39
931.8323 | 467.7966 | 599.431 | 604.5499
932.8323 | 467.795 | 599.3426 | 604.6874
933.8323 | 467.7942 | 599.113 | 604.5526
934.8323 | 467.7968 | 599.0625 | 604.6899
935.8323 | 467.7914 | 599.2769 | 605.4012
936.8323 | 467.8221 | 599.0693 | 605.4661
937.8323 | 467.8537 | 598.9026 | 605.6032
938.8323 | 467.8748 | 598.9169 | 605.3471
939.8323 | 467.9046 | 599.3689 | 605.103
940.8323 | 467.8923 | 599.8503 | 605.527
941.8323 | 467.8932 | 600.1934 | 605.0991
942.8323 | 467.8774 | 600.5816 | 605.202
943.8323 | 467.8598 | 600.6029 | 605.5317
944.8323 | 467.85 | 600.3832 | 605.8774
945.8323 | 467.8233 | 601.0721 | 606.7946
946.8323 | 467.8719 | 601.2046 | 606.7018
947.8323 | 467.9394 | 601.5635 | 607.0131
948.8323 | 467.947 | 601.8284 | 607.3585
949.8323 | 467.972 | 601.8237 | 607.7652
950.8323 | 467.9927 | 602.1458 | 608.8308
951.8323 | 468.0319 | 601.9903 | 609.1238
952.8323 | 468.0806 | 602.0017 | 609.5666
953.8323 | 468.1329 | 602.5093 | 610.3933
954.8479 | 468.1366 | 603.0535 | 611.0318
955.8323 | 468.1282 | 603.4315 | 611.3986
956.8323 | 468.1414 | 603.5364 | 611.464
957.8479 | 468.1665 | 603.8958 | 611.7975
958.8479 | 468.2126 | 603.9998 | 612.1286
959.8323 | 468.2653 | 603.9672 | 612.4009
960.8323 | 468.2805 | 604.1782 | 612.5971
961.8323 | 468.2861 | 604.0884 | 612.5587
962.8323 | 468.3473 | 603.7108 | 612.487
963.8323 | 468.4001 | 603.5797 | 612.5446
964.8323 | 468.4352 | 603.2832 | 613.1361
965.8323 | 468.4773 | 603.5187 | 613.7384
966.8323 | 468.5328 | 603.3439 | 613.5488
967.8323 | 468.5831 | 603.6594 | 613.7324
968.8323 | 468.635 | 604.6049 | 613.7859
969.8323 | 468.6487 | 605.3673 | 613.7301
970.8323 | 468.6712 | 605.8721 | 614.0773
971.8323 | 468.6926 | 605.3607 | 613.8412
972.8323 | 468.7521 | 604.9568 | 614.0809
973.8323 | 468.7536 | 605.4338 | 614.3456
974.8323 | 468.8075 | 605.575 | 614.768
975.8323 | 468.8326 | 605.9863 | 615.0061
976.8323 | 468.8595 | 606.0386 | 615.0957
977.8323 | 468.9187 | 606.4662 | 615.181
978.8323 | 468.9561 | 605.9909 | 615.2396
979.8323 | 468.9742 | 605.8327 | 615.3104
980.8323 | 469.0051 | 605.5467 | 615.8713
981.8323 | 469.0735 | 605.1168 | 615.9124
982.8323 | 469.1328 | 605.4144 | 616.1511
983.8323 | 469.1941 | 605.8511 | 616.4546
984.8323 | 469.2323 | 606.0805 | 616.9496
985.8323 | 469.2605 | 606.3791 | 617.781
986.8323 | 469.2829 | 606.4344 | 617.8049
987.8323 | 469.3363 | 606.0983 | 617.9005
988.8323 | 469.3221 | 606.0732 | 618.3892
989.8323 | 469.3617 | 606.3394 | 619.0002
990.8323 | 469.3995 | 606.6038 | 619.6968
991.8323 | 469.4442 | 606.5439 | 619.2289
992.8323 | 469.4855 | 606.6255 | 619.5146
993.8323 | 469.49 | 606.6235 | 619.7299
994.8323 | 469.5193 | 606.5131 | 620.2647
995.8323 | 469.519 | 606.7644 | 621.0875
996.8323 | 469.5193 | 606.6056 | 621.3105
997.8323 | 469.4979 | 606.4631 | 621.6633
998.8323 | 469.5226 | 606.7262 | 622.1121
999.8323 | 469.5437 | 606.8548 | 622.8129
1000.8323 | 469.5543 | 606.749 | 623.3532
1001.8323 | 469.5266 | 606.73 | 623.7178
1002.8323 | 469.4904 | 606.738 | 624.3577
1003.8323 | 469.4818 | 606.6722 | 624.8361
1004.8323 | 469.4735 | 606.832 | 625.3312
1005.8323 | 469.4865 | 606.9932 | 625.8566
1006.8323 | 469.5221 | 606.9049 | 625.7684
1007.8323 | 469.5395 | 607.2288 | 625.6706
1008.8323 | 469.524 | 607.3549 | 626.1072
1009.8323 | 469.558 | 607.3018 | 626.5499
1010.8323 | 469.5666 | 607.2875 | 626.8047
1011.8323 | 469.529 | 607.4568 | 626.4338
1012.8323 | 469.5178 | 607.9597 | 626.2655
1013.8323 | 469.5446 | 607.9227 | 626.4923
1014.8323 | 469.5875 | 607.4286 | 626.7034
1015.8323 | 469.5788 | 606.6936 | 627.0663
1016.8323 | 469.5796 | 606.7295 | 627.4199
1017.8323 | 469.4992 | 606.8792 | 627.2058
1018.8323 | 469.4849 | 607.3591 | 627.137
1019.8323 | 469.5162 | 607.4214 | 627.5932
1020.8323 | 469.5158 | 607.3199 | 628.3064
1021.8323 | 469.4005 | 607.7228 | 628.4911
1022.8323 | 469.2082 | 608.0985 | 628.845
1023.8323 | 468.9499 | 608.4563 | 629.179
1024.8323 | 468.6633 | 608.6653 | 629.4744
1025.8323 | 468.3493 | 608.7756 | 629.7136
1026.8323 | 467.9753 | 608.6367 | 630.0369
1027.8323 | 467.6149 | 608.1181 | 629.8106
1028.8323 | 467.1676 | 608.0065 | 630.1756
1029.8323 | 466.6635 | 607.943 | 630.8405
1030.8323 | 466.1683 | 607.4709 | 631.3698
1031.8323 | 465.6793 | 607.5739 | 631.3989
1032.8323 | 465.171 | 607.5783 | 632.2664
1033.8323 | 464.6614 | 607.4533 | 633.2442
1034.8323 | 464.1542 | 607.0876 | 633.4384
1035.8323 | 463.6493 | 606.2672 | 633.0897
1036.8323 | 463.12 | 605.9563 | 633.5661
1037.8323 | 462.5984 | 606.0213 | 633.8379
1038.8323 | 462.0755 | 606.3135 | 634.686
1039.8323 | 461.5353 | 606.2733 | 634.9735
1040.8323 | 461.0149 | 605.7749 | 635.092
1041.8479 | 460.4747 | 605.2754 | 635.0658
1042.8323 | 459.9481 | 605.3481 | 635.8185
1043.8323 | 459.3876 | 605.0975 | 636.1196
1044.8479 | 458.8146 | 604.7788 | 636.0918
1045.8323 | 458.2864 | 604.639 | 636.144
1047.0042 | 457.652 | 593.96 | 619.9384
1047.8323 | 457.2116 | 604.3703 | 636.2653
1048.8323 | 456.6797 | 604.5171 | 636.6301
1049.8323 | 456.1142 | 604.4018 | 636.3983
1050.8323 | 455.532 | 604.1128 | 636.4406
1051.8323 | 454.9019 | 603.0412 | 635.5868
1052.8323 | 454.2989 | 603.4069 | 636.436
1053.8323 | 453.6821 | 603.8034 | 636.198
1055.0667 | 452.9719 | 598.5859 | 629.1175
1055.8323 | 452.544 | 604.0914 | 637.4277
1056.8479 | 451.9481 | 603.6271 | 637.2605
1057.8323 | 451.3934 | 603.425 | 637.7277
1058.8323 | 450.8226 | 603.1573 | 638.1206
1059.8323 | 450.2651 | 603.339 | 638.5197
1060.8323 | 449.6558 | 602.7537 | 636.904
1062.4573 | 448.6754 | 590.6805 | 620.0152
1062.9885 | 448.3103 | 600.8086 | 635.1794
1063.8323 | 447.7712 | 602.5045 | 638.3237
1064.8479 | 447.2123 | 602.3412 | 638.0059
1065.8323 | 446.6872 | 602.2225 | 637.7784
1066.8323 | 446.1337 | 602.2662 | 637.7136
1067.8635 | 445.56 | 597.4854 | 630.6425
1068.8323 | 445.0419 | 602.5802 | 637.8197