## Test Conditions
DESIREE-FIRE Test Number 46 - Circuit Simulator Data Only
Test Date: | 2009-10-08
DCSim DAQ Start Time | 15:39
DCSim Time for Synchronization | 16:11
Heat Source Synchronization | 4:49 | minutes:seconds
Heat Source DAQ Start Time | 16:06
Fire Time | 16:10
Offset | 0:31 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 1860 | seconds
Heat Source Offset | 0:04 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 214 | seconds
Heat Source Stop Time | 16:34
Test Duration | 0:24 | minutes:seconds
| 1440 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.40625 | 123.2437 | -61.4685 | 61.6104 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5508 | 0.088375 | 61.4546 | -0.033101 | 0.029923 | 61.5433 | 0.016878 | 61.5137 | 61.4988 | 61.428 | 61.4519 | 61.471 | 61.5002 | 61.4808 | 61.5019 | 123.0193 | 61.5569 | 122.9231 | 61.4354 | 61.4984 | 123.0118 | 61.4854 | 122.9822 | 61.5209 | 61.534 | 61.4247 | 61.4377
0.59375 | 123.2849 | -61.4777 | 61.6104 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.5508 | 0.07006 | 61.4684 | -0.10637 | 0.020767 | 61.5478 | 0.016878 | 61.5412 | 61.5034 | 61.4326 | 61.4611 | 61.4801 | 61.5185 | 61.4854 | 61.5202 | 123.0285 | 61.5477 | 122.946 | 61.3713 | 61.4984 | 123.0255 | 61.4945 | 123.0189 | 61.5301 | 61.534 | 61.4476 | 61.4515
1.5938 | 123.2895 | -61.496 | 61.6241 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5463 | 0.07006 | 61.4638 | -0.092628 | 0.025345 | 61.5524 | -0.015171 | 61.5412 | 61.5125 | 61.4509 | 61.484 | 61.4984 | 61.5368 | 61.4991 | 61.5386 | 123.0422 | 61.566 | 122.9597 | 61.4033 | 61.5213 | 123.0484 | 61.4808 | 123.0372 | 61.5209 | 61.5614 | 61.4384 | 61.4789
2.5938 | 123.2529 | -61.4868 | 61.6241 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.5508 | 0.07006 | 61.4592 | -0.092628 | 0.016188 | 61.5524 | -0.010593 | 61.3443 | 61.5125 | 61.4463 | 61.4702 | 61.4938 | 61.5322 | 61.4946 | 61.534 | 123.0377 | 61.5569 | 122.946 | 61.3942 | 61.503 | 123.0392 | 61.4762 | 122.8312 | 61.5346 | 61.5614 | 61.443 | 61.4698
3.5938 | 123.2758 | -61.4731 | 61.6196 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.003172 | 0.047159 | 61.5508 | 0.074638 | 61.4729 | -0.097207 | 0.020767 | 61.5478 | -0.028906 | 61.326 | 61.4942 | 61.4326 | 61.4657 | 61.4755 | 61.5048 | 61.4763 | 61.5202 | 123.0239 | 61.5477 | 122.946 | 61.3759 | 61.4939 | 123.0209 | 61.4442 | 122.7991 | 61.5301 | 61.5797 | 61.4522 | 61.5018
4.5938 | 123.2803 | -61.4639 | 61.6058 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.038003 | 61.5463 | 0.065481 | 61.4684 | -0.088049 | 0.025345 | 61.557 | -0.010593 | 61.326 | 61.4851 | 61.4188 | 61.4519 | 61.4664 | 61.4956 | 61.4717 | 61.5019 | 123.0102 | 61.5294 | 122.9323 | 61.3759 | 61.4893 | 123.0209 | 61.4533 | 122.79 | 61.5209 | 61.5568 | 61.443 | 61.4789
5.5938 | 123.2941 | -61.4777 | 61.6104 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.5554 | 0.07006 | 61.4958 | -0.092628 | 0.020767 | 61.5387 | -0.015171 | 61.3306 | 61.4988 | 61.4417 | 61.4657 | 61.4847 | 61.5185 | 61.4854 | 61.5248 | 123.0331 | 61.5477 | 122.9735 | 61.385 | 61.4984 | 123.0164 | 61.4625 | 122.8083 | 61.5346 | 61.5706 | 61.4751 | 61.511
6.5938 | 123.2529 | -61.4914 | 61.6104 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.040843 | 0.00775 | 0.038003 | 61.5554 | 0.07006 | 61.4912 | -0.092628 | 0.020767 | 61.557 | -0.010593 | 61.3169 | 61.5125 | 61.4509 | 61.4794 | 61.4938 | 61.5322 | 61.4991 | 61.5294 | 123.0468 | 61.5615 | 122.9826 | 61.3988 | 61.5122 | 123.0484 | 61.4808 | 122.8083 | 61.5346 | 61.566 | 61.4705 | 61.5018
7.5938 | 123.2391 | -61.4777 | 61.615 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5554 | 0.079217 | 61.4912 | -0.092628 | 0.029923 | 61.5478 | -0.010593 | 61.3306 | 61.5034 | 61.4371 | 61.4611 | 61.4801 | 61.5185 | 61.4808 | 61.5202 | 123.0331 | 61.5569 | 122.9689 | 61.385 | 61.5076 | 123.0255 | 61.4671 | 122.8083 | 61.5255 | 61.566 | 61.4613 | 61.5018
8.5938 | 123.2666 | -61.4594 | 61.6196 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5554 | 0.065481 | 61.4912 | -0.092628 | 0.020767 | 61.5478 | -0.019749 | 61.3215 | 61.4851 | 61.4143 | 61.4474 | 61.4618 | 61.5002 | 61.4625 | 61.5019 | 123.0148 | 61.5248 | 122.9506 | 61.3667 | 61.4801 | 123.0072 | 61.4396 | 122.7808 | 61.5346 | 61.5752 | 61.4705 | 61.511
9.5938 | 123.3032 | -61.4822 | 61.6013 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.5554 | 0.07006 | 61.5004 | -0.097207 | 0.029923 | 61.557 | -0.006014 | 61.3215 | 61.4988 | 61.4417 | 61.4702 | 61.4893 | 61.5231 | 61.4808 | 61.5294 | 123.0377 | 61.5523 | 122.9826 | 61.385 | 61.5122 | 123.0392 | 61.4762 | 122.8037 | 61.5255 | 61.5614 | 61.4705 | 61.5064
10.5938 | 123.3078 | -61.4731 | 61.6196 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.047159 | 61.5508 | 0.079217 | 61.5004 | -0.092628 | 0.025345 | 61.557 | -0.006014 | 61.3306 | 61.4896 | 61.4326 | 61.4565 | 61.4801 | 61.5093 | 61.4717 | 61.5202 | 123.0239 | 61.5523 | 122.9735 | 61.3805 | 61.4984 | 123.0301 | 61.4671 | 122.8037 | 61.5255 | 61.5568 | 61.4751 | 61.5064
11.5938 | 123.2574 | -61.4594 | 61.6241 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.5508 | 0.074638 | 61.5004 | -0.097207 | 0.020767 | 61.5524 | -0.010593 | 61.3352 | 61.4805 | 61.4188 | 61.4474 | 61.4618 | 61.5048 | 61.4671 | 61.5019 | 123.0102 | 61.534 | 122.9598 | 61.3621 | 61.4801 | 123.0118 | 61.4488 | 122.7945 | 61.5301 | 61.5614 | 61.4796 | 61.511
12.5938 | 123.262 | -61.5005 | 61.615 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.038003 | 61.5508 | 0.065481 | 61.4958 | -0.097207 | 0.025345 | 61.5524 | -0.010593 | 61.3215 | 61.5263 | 61.4554 | 61.484 | 61.4984 | 61.5322 | 61.5037 | 61.5386 | 123.0514 | 61.566 | 122.9964 | 61.4033 | 61.5259 | 123.053 | 61.49 | 122.822 | 61.5255 | 61.5614 | 61.4705 | 61.5064
13.5938 | 123.2208 | -61.4731 | 61.6241 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.047159 | 61.5508 | 0.074638 | 61.5004 | -0.088049 | 0.025345 | 61.5524 | -0.015171 | 61.3169 | 61.4942 | 61.4326 | 61.4565 | 61.4755 | 61.5093 | 61.4763 | 61.5202 | 123.0239 | 61.5477 | 122.9735 | 61.385 | 61.4984 | 123.0255 | 61.4579 | 122.79 | 61.5255 | 61.566 | 61.4751 | 61.5156
14.5938 | 123.2437 | -61.496 | 61.6104 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.042581 | 61.5554 | 0.074638 | 61.4912 | -0.092628 | 0.020767 | 61.5524 | -0.006014 | 61.326 | 61.5125 | 61.4509 | 61.4794 | 61.4938 | 61.5322 | 61.4991 | 61.5386 | 123.0514 | 61.5706 | 122.9872 | 61.4033 | 61.5167 | 123.0484 | 61.49 | 122.822 | 61.5346 | 61.5614 | 61.4705 | 61.4973
15.5938 | 123.2346 | -61.5051 | 61.615 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.040843 | 0.00775 | 0.038003 | 61.5508 | 0.083796 | 61.505 | -0.092628 | 0.029923 | 61.5616 | -0.006014 | 61.3215 | 61.5263 | 61.4646 | 61.4931 | 61.503 | 61.546 | 61.5129 | 61.5431 | 123.056 | 61.5889 | 123.0101 | 61.4125 | 61.535 | 123.0667 | 61.4991 | 122.8266 | 61.5209 | 61.5568 | 61.4751 | 61.511
16.5938 | 123.2712 | -61.4914 | 61.6287 | 0.016548 | -0.049678 | -0.007421 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.5508 | 0.065481 | 61.4958 | -0.092628 | 0.020767 | 61.5524 | -0.010593 | 61.3352 | 61.5079 | 61.4417 | 61.484 | 61.4938 | 61.5277 | 61.4991 | 61.534 | 123.0422 | 61.5569 | 122.9872 | 61.3988 | 61.5122 | 123.0438 | 61.4808 | 122.8266 | 61.5301 | 61.5614 | 61.4751 | 61.5064
17.5938 | 123.349 | -61.4548 | 61.5646 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.5463 | 0.074638 | 61.4958 | -0.097207 | 0.025345 | 61.557 | -0.015171 | 61.3215 | 61.4805 | 61.4188 | 61.4382 | 61.4572 | 61.491 | 61.4534 | 61.4928 | 123.001 | 61.5294 | 122.9506 | 61.3576 | 61.4801 | 123.0118 | 61.4396 | 122.7762 | 61.5209 | 61.5614 | 61.4705 | 61.511
18.5938 | 123.2712 | -61.4868 | 61.6058 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.5463 | 0.079217 | 61.4912 | -0.092628 | 0.020767 | 61.5524 | -0.006014 | 61.3169 | 61.5125 | 61.4417 | 61.4702 | 61.4938 | 61.5277 | 61.4946 | 61.534 | 123.0331 | 61.566 | 122.9781 | 61.3942 | 61.5076 | 123.0392 | 61.4808 | 122.8037 | 61.5255 | 61.5523 | 61.4705 | 61.4973
19.5938 | 123.2574 | -61.4822 | 61.5921 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.047159 | 61.5508 | 0.074638 | 61.4958 | -0.088049 | 0.020767 | 61.5478 | -0.010593 | 61.3215 | 61.4988 | 61.4371 | 61.4657 | 61.4847 | 61.5185 | 61.49 | 61.5294 | 123.0331 | 61.5569 | 122.9781 | 61.3942 | 61.503 | 123.0301 | 61.4716 | 122.8037 | 61.5301 | 61.5614 | 61.4751 | 61.5064
20.5938 | 123.2437 | -61.5097 | 61.5875 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.5417 | 0.07006 | 61.4958 | -0.092628 | 0.020767 | 61.5524 | -0.010593 | 61.326 | 61.5263 | 61.4692 | 61.4977 | 61.5122 | 61.546 | 61.5083 | 61.5477 | 123.0514 | 61.5798 | 123.0055 | 61.4171 | 61.5305 | 123.0621 | 61.4991 | 122.8357 | 61.5209 | 61.5523 | 61.4751 | 61.5064
21.5938 | 123.262 | -61.496 | 61.6287 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.040843 | 0.012329 | 0.038003 | 61.5554 | 0.07006 | 61.4958 | -0.097207 | 0.025345 | 61.5524 | -0.010593 | 61.326 | 61.5171 | 61.4555 | 61.484 | 61.4984 | 61.5368 | 61.5083 | 61.534 | 123.0514 | 61.566 | 122.9918 | 61.3988 | 61.5213 | 123.0484 | 61.4854 | 122.822 | 61.5301 | 61.566 | 61.4705 | 61.5064
22.5938 | 123.3627 | -61.4548 | 61.6196 | 0.01197 | -0.035942 | -0.021157 | 0.007033 | 0.031687 | -0.001406 | 0.038003 | 61.5463 | 0.074638 | 61.4867 | -0.097207 | 0.025345 | 61.5524 | -0.006014 | 61.3306 | 61.4667 | 61.4188 | 61.4336 | 61.4618 | 61.4865 | 61.4534 | 61.4928 | 123.001 | 61.5294 | 122.9414 | 61.3576 | 61.4801 | 123.0072 | 61.4488 | 122.7854 | 61.5209 | 61.5523 | 61.4613 | 61.4927
23.5938 | 123.2986 | -61.4502 | 61.6241 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.033424 | 61.5508 | 0.079217 | 61.4958 | -0.092628 | 0.020767 | 61.5478 | -0.006014 | 61.3306 | 61.4759 | 61.4097 | 61.4382 | 61.4526 | 61.4956 | 61.4579 | 61.4836 | 123.001 | 61.5294 | 122.946 | 61.3576 | 61.471 | 122.998 | 61.4442 | 122.7808 | 61.5301 | 61.5568 | 61.4751 | 61.5018
24.5938 | 123.317 | -61.4777 | 61.6241 | 0.030283 | -0.049678 | -0.007421 | 0.011611 | 0.036265 | 0.003172 | 0.038003 | 61.5646 | 0.07006 | 61.4958 | -0.088049 | 0.029923 | 61.5478 | -0.006014 | 61.326 | 61.5079 | 61.428 | 61.4702 | 61.4893 | 61.5139 | 61.4808 | 61.5157 | 123.0422 | 61.5477 | 122.9735 | 61.3896 | 61.5076 | 123.0255 | 61.4716 | 122.8037 | 61.5346 | 61.5706 | 61.4659 | 61.5018
25.5938 | 123.3124 | -61.4731 | 61.6013 | 0.016548 | -0.049678 | -0.016578 | 0.011611 | 0.036265 | 0.016907 | 0.038003 | 61.5508 | 0.079217 | 61.505 | -0.092628 | 0.025345 | 61.5478 | -0.006014 | 61.326 | 61.4896 | 61.4234 | 61.4565 | 61.4847 | 61.5093 | 61.49 | 61.5111 | 123.0239 | 61.5523 | 122.9781 | 61.3805 | 61.4984 | 123.0209 | 61.4671 | 122.7991 | 61.5255 | 61.5568 | 61.4796 | 61.511
26.5938 | 123.2712 | -61.4822 | 61.6196 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.5508 | 0.079217 | 61.5004 | -0.08347 | 0.025345 | 61.5524 | -0.015171 | 61.326 | 61.5079 | 61.4371 | 61.4702 | 61.4893 | 61.5277 | 61.49 | 61.5294 | 123.0331 | 61.5615 | 122.9826 | 61.3988 | 61.5076 | 123.0347 | 61.4671 | 122.8083 | 61.5255 | 61.566 | 61.4751 | 61.5156
27.5938 | 123.3582 | -61.4777 | 61.5875 | 0.021127 | -0.049678 | -0.021157 | 0.011611 | 0.040843 | -0.001406 | 0.038003 | 61.5463 | 0.07006 | 61.505 | -0.088049 | 0.020767 | 61.5524 | -0.006014 | 61.326 | 61.4988 | 61.428 | 61.4565 | 61.4893 | 61.5185 | 61.4763 | 61.5157 | 123.0239 | 61.5477 | 122.9826 | 61.3896 | 61.4984 | 123.0301 | 61.4716 | 122.8037 | 61.5255 | 61.5523 | 61.4842 | 61.511
28.5938 | 123.2941 | -61.4731 | 61.6333 | 0.021127 | -0.040521 | -0.021157 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.5554 | 0.074638 | 61.4912 | -0.092628 | 0.025345 | 61.5524 | -0.010593 | 61.3352 | 61.4942 | 61.4326 | 61.4519 | 61.4847 | 61.5139 | 61.4763 | 61.5157 | 123.0285 | 61.5477 | 122.9643 | 61.3805 | 61.4984 | 123.0255 | 61.4625 | 122.8083 | 61.5301 | 61.566 | 61.4659 | 61.5018
29.5938 | 123.2803 | -61.4685 | 61.6241 | 0.030283 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.5508 | 0.079217 | 61.5004 | -0.092628 | 0.016188 | 61.5524 | -0.015171 | 61.3352 | 61.4988 | 61.4371 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.5065 | 123.0193 | 61.5477 | 122.9689 | 61.3759 | 61.4847 | 123.0209 | 61.4533 | 122.8037 | 61.5346 | 61.566 | 61.4842 | 61.5156
30.5938 | 123.2941 | -61.4822 | 61.6104 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.051737 | 61.5554 | 0.079217 | 61.5004 | -0.092628 | 0.029923 | 61.557 | -0.015171 | 61.3306 | 61.4988 | 61.4371 | 61.4702 | 61.4847 | 61.5185 | 61.4854 | 61.534 | 123.0377 | 61.5615 | 122.9826 | 61.3896 | 61.5122 | 123.0392 | 61.4671 | 122.8129 | 61.5255 | 61.5706 | 61.4705 | 61.5156
31.5938 | 123.2895 | -61.4731 | 61.6425 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.045421 | 0.003172 | 0.038003 | 61.5508 | 0.074638 | 61.5004 | -0.092628 | 0.020767 | 61.5524 | -0.019749 | 61.326 | 61.4988 | 61.428 | 61.4519 | 61.4755 | 61.5185 | 61.4763 | 61.5111 | 123.0239 | 61.5477 | 122.9735 | 61.3805 | 61.4939 | 123.0255 | 61.4533 | 122.7991 | 61.5301 | 61.5706 | 61.4796 | 61.5201
32.5938 | 123.3582 | -61.4685 | 61.5921 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.00775 | 0.042581 | 61.56 | 0.07006 | 61.4958 | -0.097207 | 0.025345 | 61.557 | -0.015171 | 61.3169 | 61.4851 | 61.4234 | 61.4519 | 61.4664 | 61.5002 | 61.4763 | 61.5111 | 123.0285 | 61.5386 | 122.9643 | 61.3713 | 61.4939 | 123.0255 | 61.4533 | 122.7854 | 61.5346 | 61.5752 | 61.4705 | 61.511
33.5938 | 123.2712 | -61.4548 | 61.6013 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5508 | 0.079217 | 61.5004 | -0.08347 | 0.034501 | 61.5524 | -0.001436 | 61.3306 | 61.4759 | 61.4143 | 61.4428 | 61.4618 | 61.491 | 61.4671 | 61.4928 | 123.0056 | 61.534 | 122.9552 | 61.3713 | 61.4893 | 123.0072 | 61.4533 | 122.7854 | 61.5163 | 61.5523 | 61.4659 | 61.5018
34.5938 | 123.2712 | -61.4685 | 61.6013 | 0.025705 | -0.049678 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.5508 | 0.079217 | 61.5004 | -0.092628 | 0.025345 | 61.557 | -0.010593 | 61.326 | 61.4942 | 61.4188 | 61.4565 | 61.471 | 61.5048 | 61.4763 | 61.5111 | 123.0193 | 61.5477 | 122.9689 | 61.3759 | 61.4939 | 123.0255 | 61.4579 | 122.7945 | 61.5255 | 61.5614 | 61.4751 | 61.511
35.5938 | 123.3078 | -61.4777 | 61.647 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.56 | 0.07006 | 61.5004 | -0.092628 | 0.029923 | 61.5524 | -0.001436 | 61.326 | 61.4988 | 61.4371 | 61.4611 | 61.4847 | 61.5185 | 61.4854 | 61.5248 | 123.0377 | 61.5477 | 122.9781 | 61.385 | 61.5076 | 123.0301 | 61.4762 | 122.8037 | 61.5301 | 61.5614 | 61.4705 | 61.5018
36.5938 | 123.2574 | -61.4914 | 61.6196 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5463 | 0.07006 | 61.4958 | -0.097207 | 0.020767 | 61.557 | -0.006014 | 61.3215 | 61.5125 | 61.4555 | 61.4748 | 61.4938 | 61.5322 | 61.4946 | 61.534 | 123.0377 | 61.5615 | 122.9872 | 61.3942 | 61.5122 | 123.0484 | 61.4854 | 122.8129 | 61.5255 | 61.5523 | 61.4751 | 61.5018
37.5938 | 123.2574 | -61.4731 | 61.6653 | 0.021127 | -0.0451 | -0.021157 | -0.002124 | 0.040843 | 0.012329 | 0.042581 | 61.5508 | 0.074638 | 61.5004 | -0.092628 | 0.020767 | 61.5478 | -0.010593 | 61.3398 | 61.4942 | 61.428 | 61.4519 | 61.471 | 61.5139 | 61.4854 | 61.5157 | 123.0239 | 61.5477 | 122.9735 | 61.3805 | 61.4939 | 123.0209 | 61.4625 | 122.8129 | 61.5301 | 61.5614 | 61.4796 | 61.511
38.5938 | 123.2758 | -61.4639 | 61.615 | 0.016548 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.5554 | 0.074638 | 61.505 | -0.092628 | 0.025345 | 61.5524 | -0.010593 | 61.3352 | 61.4805 | 61.4234 | 61.4474 | 61.4755 | 61.5048 | 61.4717 | 61.5111 | 123.0193 | 61.5386 | 122.9689 | 61.3713 | 61.4893 | 123.0164 | 61.4533 | 122.7991 | 61.5301 | 61.566 | 61.4796 | 61.5156
39.5938 | 123.2483 | -61.4731 | 61.6333 | 0.025705 | -0.0451 | -0.021157 | 0.007033 | 0.045421 | -0.001406 | 0.038003 | 61.5646 | 0.079217 | 61.5004 | -0.097207 | 0.020767 | 61.5478 | -0.015171 | 61.3352 | 61.4988 | 61.428 | 61.4519 | 61.4801 | 61.5185 | 61.4717 | 61.5111 | 123.0377 | 61.5523 | 122.9735 | 61.3759 | 61.4939 | 123.0209 | 61.4579 | 122.8083 | 61.5438 | 61.5797 | 61.4796 | 61.5156
40.5938 | 123.23 | -61.4502 | 61.6562 | 0.01197 | -0.0451 | -0.012 | -0.002124 | 0.036265 | 0.00775 | 0.038003 | 61.5554 | 0.074638 | 61.4867 | -0.092628 | 0.025345 | 61.5524 | -0.010593 | 61.3306 | 61.4622 | 61.4051 | 61.4382 | 61.4481 | 61.4865 | 61.4579 | 61.4882 | 123.0056 | 61.5248 | 122.9369 | 61.3576 | 61.4755 | 123.0026 | 61.4396 | 122.7808 | 61.5301 | 61.566 | 61.4613 | 61.4973
41.5938 | 123.3353 | -61.4777 | 61.6562 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.049999 | 0.003172 | 0.042581 | 61.56 | 0.074638 | 61.5004 | -0.097207 | 0.025345 | 61.5524 | -0.010593 | 61.326 | 61.4988 | 61.4326 | 61.4611 | 61.4847 | 61.5277 | 61.4808 | 61.5202 | 123.0377 | 61.5523 | 122.9781 | 61.3805 | 61.503 | 123.0301 | 61.4671 | 122.8037 | 61.5346 | 61.5706 | 61.4751 | 61.511
42.5938 | 123.3124 | -61.4731 | 61.6562 | 0.021127 | -0.049678 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.042581 | 61.5554 | 0.074638 | 61.5004 | -0.10179 | 0.025345 | 61.5616 | -0.010593 | 61.3306 | 61.4942 | 61.4234 | 61.4611 | 61.4801 | 61.5048 | 61.4808 | 61.5157 | 123.0285 | 61.5477 | 122.9735 | 61.3713 | 61.4984 | 123.0347 | 61.4625 | 122.8037 | 61.5301 | 61.566 | 61.4751 | 61.511
43.5938 | 123.3078 | -61.4685 | 61.6791 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.040843 | 0.00775 | 0.038003 | 61.56 | 0.079217 | 61.4958 | -0.092628 | 0.025345 | 61.5524 | -0.010593 | 61.3306 | 61.4896 | 61.428 | 61.4519 | 61.4664 | 61.5093 | 61.4763 | 61.5065 | 123.0285 | 61.5477 | 122.9643 | 61.3759 | 61.4939 | 123.0209 | 61.4579 | 122.7991 | 61.5346 | 61.5706 | 61.4705 | 61.5064
44.5938 | 123.2574 | -61.4731 | 61.615 | 0.025705 | -0.049678 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.5554 | 0.074638 | 61.4912 | -0.088049 | 0.025345 | 61.5524 | 0.003143 | 61.3215 | 61.4988 | 61.4234 | 61.4565 | 61.4755 | 61.5139 | 61.4808 | 61.5157 | 123.0285 | 61.5477 | 122.9643 | 61.385 | 61.4984 | 123.0255 | 61.4762 | 122.7945 | 61.5301 | 61.5523 | 61.4659 | 61.4881
45.5938 | 123.2803 | -61.4639 | 61.6333 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.047159 | 61.5554 | 0.07006 | 61.5004 | -0.088049 | 0.020767 | 61.5524 | -0.010593 | 61.3352 | 61.4896 | 61.4234 | 61.4519 | 61.471 | 61.5048 | 61.4671 | 61.5111 | 123.0193 | 61.534 | 122.9643 | 61.3759 | 61.4847 | 123.0164 | 61.4533 | 122.7991 | 61.5346 | 61.566 | 61.4796 | 61.511
46.5938 | 123.2574 | -61.4777 | 61.6379 | 0.016548 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.00775 | 0.038003 | 61.56 | 0.079217 | 61.4958 | -0.092628 | 0.025345 | 61.5524 | -0.006014 | 61.3352 | 61.4942 | 61.4326 | 61.4702 | 61.4847 | 61.5231 | 61.4854 | 61.5157 | 123.0377 | 61.5569 | 122.9735 | 61.385 | 61.503 | 123.0301 | 61.4716 | 122.8129 | 61.5346 | 61.566 | 61.4705 | 61.5018
47.5938 | 123.2208 | -61.4822 | 61.6562 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.042581 | 61.5508 | 0.083796 | 61.5004 | -0.092628 | 0.020767 | 61.5478 | -0.006014 | 61.3352 | 61.5034 | 61.4371 | 61.4657 | 61.4893 | 61.5185 | 61.4763 | 61.5248 | 123.0331 | 61.566 | 122.9826 | 61.3896 | 61.503 | 123.0301 | 61.4762 | 122.8174 | 61.5301 | 61.5568 | 61.4796 | 61.5064
48.5938 | 123.2437 | -61.441 | 61.615 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.5646 | 0.074638 | 61.5004 | -0.092628 | 0.020767 | 61.557 | -0.010593 | 61.326 | 61.4622 | 61.3959 | 61.4245 | 61.4481 | 61.4819 | 61.4396 | 61.479 | 123.0056 | 61.5157 | 122.9414 | 61.3484 | 61.4618 | 122.998 | 61.4304 | 122.7671 | 61.5438 | 61.5752 | 61.4796 | 61.511
49.5938 | 123.2666 | -61.4914 | 61.6287 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.047159 | 61.5554 | 0.07006 | 61.4912 | -0.092628 | 0.029923 | 61.5524 | -0.015171 | 61.3306 | 61.5125 | 61.4463 | 61.4748 | 61.4984 | 61.5322 | 61.4946 | 61.5386 | 123.0468 | 61.5615 | 122.9826 | 61.3988 | 61.5213 | 123.0438 | 61.4762 | 122.822 | 61.5255 | 61.5706 | 61.4613 | 61.5064
50.5938 | 123.2849 | -61.4548 | 61.6425 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.038003 | 61.5508 | 0.079217 | 61.4958 | -0.088049 | 0.029923 | 61.557 | -0.010593 | 61.3352 | 61.4805 | 61.4097 | 61.4428 | 61.4572 | 61.5002 | 61.4625 | 61.4928 | 123.0056 | 61.534 | 122.9506 | 61.3667 | 61.4847 | 123.0118 | 61.4442 | 122.79 | 61.5209 | 61.5614 | 61.4659 | 61.5064
51.5938 | 123.2666 | -61.4685 | 61.647 | 0.021127 | -0.0451 | -0.021157 | 0.011611 | 0.031687 | 0.003172 | 0.042581 | 61.5554 | 0.074638 | 61.5004 | -0.088049 | 0.016188 | 61.557 | -0.001436 | 61.3306 | 61.4896 | 61.4234 | 61.4473 | 61.4801 | 61.5002 | 61.4717 | 61.5111 | 123.0239 | 61.5431 | 122.9689 | 61.3805 | 61.4847 | 123.0255 | 61.4671 | 122.7991 | 61.5392 | 61.5568 | 61.4842 | 61.5018
52.5938 | 123.2986 | -61.4685 | 61.647 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.038003 | 61.5554 | 0.07006 | 61.4958 | -0.097207 | 0.025345 | 61.557 | -0.010593 | 61.326 | 61.4896 | 61.428 | 61.4519 | 61.4755 | 61.5002 | 61.4717 | 61.5065 | 123.0239 | 61.5386 | 122.9643 | 61.3713 | 61.4939 | 123.0255 | 61.4579 | 122.7945 | 61.5301 | 61.566 | 61.4705 | 61.5064
53.5938 | 123.2849 | -61.5051 | 61.6379 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.56 | 0.07006 | 61.4958 | -0.097207 | 0.025345 | 61.5524 | -0.006014 | 61.3306 | 61.5263 | 61.4692 | 61.4931 | 61.5122 | 61.5414 | 61.5037 | 61.5431 | 123.0651 | 61.5752 | 123.001 | 61.4079 | 61.5305 | 123.0576 | 61.4991 | 122.8357 | 61.5346 | 61.566 | 61.4705 | 61.5018
54.5938 | 123.3856 | -61.4868 | 61.5463 | 0.025705 | -0.0451 | -0.007421 | -0.002124 | 0.036265 | 0.00775 | 0.033424 | 61.5508 | 0.074638 | 61.4912 | -0.088049 | 0.020767 | 61.557 | -0.010593 | 61.326 | 61.5125 | 61.4417 | 61.4794 | 61.4847 | 61.5231 | 61.4946 | 61.5202 | 123.0377 | 61.5615 | 122.9781 | 61.3988 | 61.5076 | 123.0438 | 61.4762 | 122.8129 | 61.5301 | 61.5614 | 61.4705 | 61.5018
55.5938 | 123.2803 | -61.4777 | 61.6379 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.040843 | 0.003172 | 0.047159 | 61.5554 | 0.079217 | 61.4912 | -0.097207 | 0.025345 | 61.5616 | -0.006014 | 61.3306 | 61.5034 | 61.4326 | 61.4657 | 61.4755 | 61.5185 | 61.4808 | 61.5248 | 123.0331 | 61.5569 | 122.9689 | 61.3805 | 61.503 | 123.0392 | 61.4716 | 122.8083 | 61.5301 | 61.5614 | 61.4659 | 61.4973
56.5938 | 123.2208 | -61.4685 | 61.6379 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.56 | 0.079217 | 61.4958 | -0.088049 | 0.025345 | 61.5524 | -0.010593 | 61.326 | 61.4988 | 61.428 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.5019 | 123.0285 | 61.5477 | 122.9643 | 61.3805 | 61.4939 | 123.0209 | 61.4579 | 122.7945 | 61.5346 | 61.5706 | 61.4705 | 61.5064
57.5938 | 123.2574 | -61.4822 | 61.6562 | 0.025705 | -0.0451 | -0.025735 | 0.002454 | 0.031687 | 0.003172 | 0.038003 | 61.5646 | 0.083796 | 61.4958 | -0.092628 | 0.025345 | 61.557 | -0.015171 | 61.3352 | 61.5079 | 61.4371 | 61.4565 | 61.4847 | 61.5139 | 61.4854 | 61.5202 | 123.0468 | 61.566 | 122.9781 | 61.3896 | 61.5076 | 123.0392 | 61.4671 | 122.8174 | 61.5392 | 61.5797 | 61.4705 | 61.511
58.5938 | 123.2529 | -61.4731 | 61.6425 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.56 | 0.065481 | 61.4912 | -0.097207 | 0.020767 | 61.5524 | -0.010593 | 61.3352 | 61.4988 | 61.4371 | 61.4611 | 61.4755 | 61.5093 | 61.4808 | 61.5157 | 123.0331 | 61.5386 | 122.9643 | 61.3759 | 61.4939 | 123.0255 | 61.4625 | 122.8083 | 61.5392 | 61.5706 | 61.4705 | 61.5018
59.5938 | 123.2574 | -61.4822 | 61.6241 | 0.025705 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.00775 | 0.038003 | 61.56 | 0.079217 | 61.505 | -0.092628 | 0.025345 | 61.5524 | -0.015171 | 61.326 | 61.5079 | 61.4463 | 61.4748 | 61.4939 | 61.5231 | 61.49 | 61.5202 | 123.0422 | 61.5615 | 122.9872 | 61.3896 | 61.5076 | 123.0347 | 61.4671 | 122.8083 | 61.5346 | 61.5752 | 61.4796 | 61.5202
60.5938 | 123.2803 | -61.4822 | 61.6562 | 0.021127 | -0.049678 | -0.021157 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.56 | 0.079217 | 61.4958 | -0.097207 | 0.025345 | 61.557 | -0.010593 | 61.3306 | 61.5034 | 61.4326 | 61.4611 | 61.4893 | 61.5231 | 61.4854 | 61.5248 | 123.0422 | 61.5615 | 122.9781 | 61.385 | 61.5076 | 123.0392 | 61.4716 | 122.8129 | 61.5346 | 61.5706 | 61.4705 | 61.5064
61.5938 | 123.2666 | -61.4777 | 61.6516 | 0.016548 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.5554 | 0.079217 | 61.4958 | -0.092628 | 0.020767 | 61.557 | -0.006014 | 61.3306 | 61.4942 | 61.4326 | 61.4611 | 61.4847 | 61.5185 | 61.4808 | 61.5111 | 123.0331 | 61.5569 | 122.9735 | 61.385 | 61.4984 | 123.0347 | 61.4716 | 122.8083 | 61.5346 | 61.5614 | 61.4751 | 61.5018
62.5938 | 123.2712 | -61.4685 | 61.6379 | 0.021127 | -0.0451 | -0.021157 | 0.007033 | 0.036265 | 0.00775 | 0.042581 | 61.5554 | 0.079217 | 61.5004 | -0.088049 | 0.020767 | 61.557 | -0.006014 | 61.3306 | 61.4896 | 61.4234 | 61.4473 | 61.4755 | 61.5048 | 61.4763 | 61.5111 | 123.0239 | 61.5477 | 122.9689 | 61.3805 | 61.4893 | 123.0255 | 61.4625 | 122.7991 | 61.5346 | 61.5614 | 61.4796 | 61.5064
63.5938 | 123.2071 | -61.496 | 61.6425 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.045421 | -0.001406 | 0.042581 | 61.56 | 0.083796 | 61.4958 | -0.088049 | 0.025345 | 61.5524 | -0.010593 | 61.3306 | 61.5217 | 61.4555 | 61.484 | 61.4984 | 61.5414 | 61.4946 | 61.5386 | 123.056 | 61.5798 | 122.9918 | 61.4079 | 61.5213 | 123.0484 | 61.4854 | 122.8266 | 61.5346 | 61.5706 | 61.4705 | 61.5064
64.5938 | 123.3078 | -61.4868 | 61.6104 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.036265 | 0.00775 | 0.038003 | 61.5554 | 0.07006 | 61.4958 | -0.097207 | 0.025345 | 61.557 | -0.010593 | 61.3215 | 61.5079 | 61.4463 | 61.4702 | 61.4847 | 61.5231 | 61.4946 | 61.5248 | 123.0422 | 61.5569 | 122.9826 | 61.3896 | 61.5122 | 123.0438 | 61.4762 | 122.8083 | 61.5301 | 61.566 | 61.4705 | 61.5064
65.5938 | 123.4222 | -61.4456 | 61.5875 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.56 | 0.074638 | 61.5004 | -0.088049 | 0.034501 | 61.557 | -0.010593 | 61.3306 | 61.4667 | 61.4005 | 61.429 | 61.4481 | 61.491 | 61.4488 | 61.4882 | 123.0056 | 61.5203 | 122.946 | 61.3576 | 61.4801 | 123.0026 | 61.435 | 122.7762 | 61.5255 | 61.5706 | 61.4659 | 61.511
66.5938 | 123.3948 | -61.4548 | 61.615 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.036265 | 0.00775 | 0.033424 | 61.5508 | 0.074638 | 61.4958 | -0.088049 | 0.020767 | 61.5524 | -0.015171 | 61.3306 | 61.4713 | 61.4097 | 61.4428 | 61.4526 | 61.491 | 61.4625 | 61.4882 | 123.0056 | 61.5294 | 122.9506 | 61.3667 | 61.4755 | 123.0072 | 61.4396 | 122.7854 | 61.5301 | 61.566 | 61.4751 | 61.511
67.5938 | 123.3032 | -61.4456 | 61.6379 | 0.016548 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.038003 | 61.56 | 0.079217 | 61.5004 | -0.10179 | 0.029923 | 61.557 | -0.001436 | 61.3306 | 61.4622 | 61.4005 | 61.4336 | 61.4527 | 61.4865 | 61.4534 | 61.4836 | 123.0056 | 61.5248 | 122.946 | 61.3438 | 61.4755 | 123.0026 | 61.4442 | 122.7762 | 61.5301 | 61.5614 | 61.4705 | 61.5018
68.5938 | 123.2803 | -61.5097 | 61.6516 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.033424 | 61.56 | 0.079217 | 61.4958 | -0.10179 | 0.025345 | 61.5524 | -0.015171 | 61.3306 | 61.5354 | 61.4692 | 61.4931 | 61.5122 | 61.546 | 61.5175 | 61.5431 | 123.0697 | 61.5889 | 123.0055 | 61.4079 | 61.535 | 123.0621 | 61.4945 | 122.8403 | 61.5346 | 61.5752 | 61.4705 | 61.511
69.5938 | 123.3765 | -61.4365 | 61.615 | 0.016548 | -0.040521 | -0.021157 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5554 | 0.079217 | 61.4867 | -0.10179 | 0.025345 | 61.5478 | -0.006014 | 61.3306 | 61.453 | 61.3959 | 61.4153 | 61.4389 | 61.4773 | 61.4396 | 61.479 | 122.9919 | 61.5157 | 122.9231 | 61.3347 | 61.4618 | 122.9843 | 61.4304 | 122.7671 | 61.5301 | 61.5614 | 61.4613 | 61.4927
70.5938 | 123.262 | -61.4548 | 61.6196 | 0.021127 | -0.049678 | -0.021157 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.5554 | 0.083796 | 61.4912 | -0.097207 | 0.025345 | 61.5524 | -0.010593 | 61.3306 | 61.4759 | 61.4051 | 61.4336 | 61.4618 | 61.5002 | 61.4625 | 61.4974 | 123.0102 | 61.5386 | 122.946 | 61.3576 | 61.4801 | 123.0072 | 61.4442 | 122.7854 | 61.5301 | 61.566 | 61.4659 | 61.5018
71.5938 | 123.2803 | -61.4594 | 61.6379 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.038003 | 61.5554 | 0.079217 | 61.4912 | -0.088049 | 0.025345 | 61.5524 | -0.010593 | 61.3352 | 61.4805 | 61.4188 | 61.4474 | 61.471 | 61.5002 | 61.4671 | 61.4974 | 123.0148 | 61.5386 | 122.9506 | 61.3713 | 61.4847 | 123.0118 | 61.4488 | 122.7945 | 61.5301 | 61.566 | 61.4659 | 61.5018
72.5938 | 123.2208 | -61.4822 | 61.6425 | 0.025705 | -0.049678 | -0.012 | -0.002124 | 0.045421 | 0.012329 | 0.051737 | 61.5554 | 0.079217 | 61.4912 | -0.088049 | 0.020767 | 61.557 | -0.010593 | 61.3306 | 61.5079 | 61.4326 | 61.4702 | 61.4801 | 61.5277 | 61.4946 | 61.534 | 123.0377 | 61.5615 | 122.9735 | 61.3942 | 61.503 | 123.0392 | 61.4716 | 122.8129 | 61.5346 | 61.566 | 61.4705 | 61.5018
73.5938 | 123.3078 | -61.4502 | 61.6287 | 0.030283 | -0.040521 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.038003 | 61.5554 | 0.074638 | 61.4912 | -0.088049 | 0.029923 | 61.5524 | -0.010593 | 61.3352 | 61.4805 | 61.4097 | 61.4336 | 61.4481 | 61.491 | 61.4534 | 61.4882 | 123.0056 | 61.5248 | 122.9414 | 61.3621 | 61.4801 | 123.0026 | 61.4396 | 122.7854 | 61.5255 | 61.566 | 61.4613 | 61.5018
74.6094 | 123.2712 | -61.4868 | 61.6516 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.036265 | -0.001406 | 0.038003 | 61.5554 | 0.079217 | 61.4912 | -0.08347 | 0.020767 | 61.5616 | -0.010593 | 61.3352 | 61.5034 | 61.4417 | 61.4702 | 61.4847 | 61.5231 | 61.4854 | 61.5248 | 123.0422 | 61.566 | 122.9781 | 61.4033 | 61.5076 | 123.0484 | 61.4762 | 122.822 | 61.5346 | 61.566 | 61.4705 | 61.5018
75.5938 | 123.3536 | -61.4502 | 61.5967 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.56 | 0.07006 | 61.4729 | -0.10637 | 0.029923 | 61.557 | -0.001436 | 61.3352 | 61.4759 | 61.4051 | 61.4336 | 61.4572 | 61.491 | 61.4488 | 61.4928 | 123.0102 | 61.5203 | 122.9231 | 61.3438 | 61.4801 | 123.0072 | 61.4488 | 122.7854 | 61.5301 | 61.5614 | 61.443 | 61.4744
76.5938 | 123.3627 | -61.4502 | 61.6104 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.592 | 0.16164 | 61.5416 | -0.019364 | 0.029923 | 61.5662 | -0.019749 | 61.3718 | 61.4759 | 61.4097 | 61.4382 | 61.4572 | 61.4956 | 61.4534 | 61.4974 | 123.0422 | 61.6118 | 122.9918 | 61.4308 | 61.4801 | 123.0164 | 61.4304 | 122.822 | 61.5621 | 61.6118 | 61.5117 | 61.5614
77.5938 | 123.3536 | -61.4365 | 61.6425 | 0.025705 | -0.0451 | -0.012 | 0.01619 | 0.054577 | 0.003172 | 0.047159 | 61.6012 | 0.17079 | 61.5279 | -0.014785 | 0.025345 | 61.5662 | -0.019749 | 61.3718 | 61.4622 | 61.3914 | 61.4245 | 61.4527 | 61.491 | 61.4396 | 61.4836 | 123.0377 | 61.6073 | 122.9643 | 61.4217 | 61.4618 | 123.0026 | 61.4167 | 122.8083 | 61.5759 | 61.6209 | 61.5025 | 61.5476
78.5938 | 123.262 | -61.4868 | 61.6287 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.049999 | 0.00775 | 0.051737 | 61.592 | 0.16622 | 61.537 | -0.019364 | 0.034501 | 61.5524 | -0.024328 | 61.3718 | 61.5125 | 61.4417 | 61.4702 | 61.4893 | 61.5368 | 61.4946 | 61.5386 | 123.0789 | 61.653 | 123.0238 | 61.4675 | 61.5213 | 123.0392 | 61.4625 | 122.8586 | 61.5575 | 61.6164 | 61.5025 | 61.5614
79.6094 | 123.2346 | -61.496 | 61.6608 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.012329 | 0.056315 | 61.6012 | 0.16622 | 61.5462 | -0.019364 | 0.025345 | 61.5478 | -0.010593 | 61.381 | 61.5217 | 61.4509 | 61.4794 | 61.4984 | 61.5414 | 61.5083 | 61.5523 | 123.0972 | 61.6622 | 123.0422 | 61.4766 | 61.5213 | 123.0438 | 61.4854 | 122.8769 | 61.5759 | 61.6118 | 61.5208 | 61.5568
80.5938 | 123.3719 | -61.4319 | 61.6104 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.049999 | 0.003172 | 0.056315 | 61.6012 | 0.17995 | 61.537 | -0.033101 | 0.029923 | 61.5524 | -0.010593 | 61.3764 | 61.4576 | 61.3914 | 61.4153 | 61.4389 | 61.4819 | 61.4351 | 61.4882 | 123.0331 | 61.6118 | 122.9689 | 61.3988 | 61.4618 | 122.9843 | 61.4213 | 122.8083 | 61.5713 | 61.6118 | 61.5071 | 61.5476
81.5938 | 123.3444 | -61.4548 | 61.5967 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.056315 | 61.6058 | 0.17079 | 61.5416 | -0.03768 | 0.034501 | 61.5616 | -0.015171 | 61.3856 | 61.4851 | 61.4097 | 61.4382 | 61.4572 | 61.5002 | 61.4625 | 61.5111 | 123.0606 | 61.6256 | 122.9964 | 61.4171 | 61.4893 | 123.0164 | 61.4396 | 122.8403 | 61.5713 | 61.6209 | 61.5071 | 61.5568
82.5938 | 123.3765 | -61.4548 | 61.6196 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.049999 | 0.012329 | 0.051737 | 61.5966 | 0.17995 | 61.5462 | -0.060575 | 0.029923 | 61.5478 | 0.003143 | 61.381 | 61.4851 | 61.4143 | 61.4382 | 61.4618 | 61.5048 | 61.4671 | 61.5065 | 123.0514 | 61.6347 | 123.001 | 61.3942 | 61.4847 | 123.0026 | 61.4579 | 122.8357 | 61.5667 | 61.5935 | 61.5163 | 61.543
83.5938 | 123.2849 | -61.4639 | 61.6516 | 0.030283 | -0.031363 | -0.012 | 0.011611 | 0.054577 | 0.012329 | 0.047159 | 61.6149 | 0.18453 | 61.5508 | -0.08347 | 0.025345 | 61.557 | -0.001436 | 61.3947 | 61.4942 | 61.4326 | 61.4519 | 61.4755 | 61.5185 | 61.4763 | 61.5111 | 123.0789 | 61.6485 | 123.0147 | 61.3805 | 61.4893 | 123.0209 | 61.4625 | 122.8586 | 61.5896 | 61.6164 | 61.5254 | 61.5522
84.5938 | 123.3627 | -61.496 | 61.5692 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.054577 | 0.016907 | 0.051737 | 61.6104 | 0.17537 | 61.5553 | -0.08347 | 0.025345 | 61.557 | -0.001436 | 61.3901 | 61.5263 | 61.46 | 61.484 | 61.503 | 61.5505 | 61.5129 | 61.5477 | 123.1063 | 61.6713 | 123.0513 | 61.4125 | 61.5213 | 123.053 | 61.4945 | 122.8861 | 61.585 | 61.6118 | 61.53 | 61.5568
85.5938 | 123.381 | -61.4822 | 61.5921 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.049999 | 0.00775 | 0.042581 | 61.5966 | 0.17995 | 61.5416 | -0.019364 | 0.029923 | 61.5662 | -0.010593 | 61.3764 | 61.5034 | 61.4417 | 61.4702 | 61.4847 | 61.5322 | 61.49 | 61.5248 | 123.0789 | 61.6622 | 123.0238 | 61.4629 | 61.5122 | 123.0484 | 61.4716 | 122.8586 | 61.5667 | 61.6072 | 61.5117 | 61.5522
86.5938 | 123.3536 | -61.4685 | 61.5692 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.5737 | 0.16622 | 61.5233 | -0.023943 | 0.034501 | 61.557 | -0.083847 | 61.3581 | 61.4896 | 61.4234 | 61.4565 | 61.4755 | 61.5093 | 61.4717 | 61.5111 | 123.0422 | 61.6347 | 122.9918 | 61.4446 | 61.503 | 123.0255 | 61.3847 | 122.8266 | 61.5392 | 61.6576 | 61.4888 | 61.6071
87.5938 | 123.3444 | -61.4639 | 61.5875 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.5691 | 0.10211 | 61.5096 | -0.028522 | 0.016188 | 61.557 | -0.07469 | 61.3489 | 61.4896 | 61.4188 | 61.4428 | 61.4664 | 61.5048 | 61.4625 | 61.5019 | 123.0331 | 61.566 | 122.9735 | 61.4354 | 61.4801 | 123.0209 | 61.3892 | 122.8129 | 61.553 | 61.6438 | 61.4934 | 61.5842
88.5938 | 123.3994 | -61.4639 | 61.6196 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.5646 | 0.083796 | 61.5004 | -0.028522 | 0.01161 | 61.5616 | 0.021456 | 61.3398 | 61.4805 | 61.4234 | 61.4474 | 61.4618 | 61.4956 | 61.4717 | 61.4928 | 123.0285 | 61.5477 | 122.9643 | 61.4354 | 61.4755 | 123.0255 | 61.4854 | 122.8037 | 61.553 | 61.5431 | 61.4888 | 61.4789
89.6094 | 123.3765 | -61.4502 | 61.6104 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.045421 | 0.003172 | 0.038003 | 61.56 | 0.083796 | 61.4546 | -0.028522 | 0.048236 | 61.5524 | 0.012299 | 61.3489 | 61.4667 | 61.4097 | 61.4336 | 61.4481 | 61.4956 | 61.4534 | 61.4882 | 123.0102 | 61.534 | 122.9048 | 61.4217 | 61.4984 | 123.0026 | 61.4625 | 122.7991 | 61.5118 | 61.5477 | 61.4064 | 61.4423
90.5938 | 123.3719 | -61.4456 | 61.5829 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.038003 | 61.5691 | 0.088375 | 61.45 | -0.08347 | -0.006702 | 61.557 | 0.016878 | 61.5549 | 61.4667 | 61.4005 | 61.429 | 61.4527 | 61.491 | 61.4488 | 61.4836 | 123.0148 | 61.534 | 122.8957 | 61.3621 | 61.4389 | 123.0026 | 61.4625 | 123.0006 | 61.5759 | 61.5523 | 61.4567 | 61.4332
91.5938 | 123.3856 | -61.4777 | 61.5784 | 0.021127 | -0.0451 | -0.021157 | 0.011611 | 0.036265 | -0.001406 | 0.033424 | 61.5737 | 0.079217 | 61.4821 | -0.10637 | 0.029923 | 61.5616 | 0.021456 | 61.5504 | 61.4988 | 61.4326 | 61.4565 | 61.4893 | 61.5139 | 61.4763 | 61.5111 | 123.0514 | 61.5569 | 122.9597 | 61.3713 | 61.5076 | 123.0392 | 61.4991 | 123.028 | 61.5438 | 61.5523 | 61.4522 | 61.4606
92.5938 | 123.3353 | -61.496 | 61.5829 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.00775 | 0.047159 | 61.5691 | 0.083796 | 61.4775 | -0.055996 | 0.020767 | 61.5616 | 0.021456 | 61.3352 | 61.5125 | 61.4555 | 61.4794 | 61.503 | 61.5322 | 61.5037 | 61.5431 | 123.0651 | 61.5798 | 122.9735 | 61.44 | 61.5167 | 123.0576 | 61.5174 | 122.8312 | 61.5484 | 61.5477 | 61.4567 | 61.4561
93.5938 | 123.3948 | -61.4868 | 61.5555 | 0.021127 | -0.040521 | -0.021157 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.5646 | 0.083796 | 61.4867 | -0.03768 | 0.025345 | 61.557 | 0.021456 | 61.3443 | 61.5079 | 61.4463 | 61.4657 | 61.4984 | 61.5277 | 61.49 | 61.5248 | 123.0514 | 61.5706 | 122.9735 | 61.4491 | 61.5122 | 123.0438 | 61.5083 | 122.8312 | 61.5392 | 61.5431 | 61.4613 | 61.4652
94.5938 | 123.3032 | -61.4777 | 61.6241 | 0.025705 | -0.0451 | -0.021157 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.5737 | 0.088375 | 61.4821 | -0.03768 | 0.025345 | 61.5616 | 0.021456 | 61.3535 | 61.5034 | 61.4326 | 61.4565 | 61.4893 | 61.5139 | 61.4763 | 61.5157 | 123.0514 | 61.566 | 122.9597 | 61.44 | 61.503 | 123.0392 | 61.4991 | 122.8312 | 61.5484 | 61.5523 | 61.4567 | 61.4606
95.5938 | 123.349 | -61.4594 | 61.5692 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.012329 | 0.033424 | 61.5691 | 0.083796 | 61.4867 | -0.042259 | 0.025345 | 61.557 | 0.007721 | 61.3443 | 61.4851 | 61.4143 | 61.4428 | 61.4618 | 61.4956 | 61.4717 | 61.4928 | 123.0285 | 61.5431 | 122.946 | 61.4171 | 61.4847 | 123.0164 | 61.4671 | 122.8037 | 61.5438 | 61.5614 | 61.4613 | 61.4789
96.5938 | 123.3719 | -61.4548 | 61.5829 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.56 | 0.083796 | 61.4912 | -0.042259 | 0.029923 | 61.557 | 0.003143 | 61.3443 | 61.4759 | 61.4097 | 61.4382 | 61.4618 | 61.4956 | 61.4579 | 61.4882 | 123.0148 | 61.5386 | 122.946 | 61.4125 | 61.4847 | 123.0118 | 61.4579 | 122.7991 | 61.5301 | 61.5568 | 61.4613 | 61.4881
97.5938 | 123.3765 | -61.4731 | 61.5509 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.5737 | 0.079217 | 61.4867 | -0.046838 | 0.025345 | 61.5662 | 0.003143 | 61.3398 | 61.4988 | 61.4326 | 61.4611 | 61.4755 | 61.5093 | 61.4763 | 61.5111 | 123.0468 | 61.5523 | 122.9597 | 61.4262 | 61.4984 | 123.0392 | 61.4762 | 122.8129 | 61.5484 | 61.5706 | 61.4613 | 61.4835
98.5938 | 123.3627 | -61.4639 | 61.5509 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.038003 | 61.5691 | 0.092954 | 61.4821 | -0.046838 | 0.016188 | 61.5616 | 0.012299 | 61.3443 | 61.4851 | 61.4188 | 61.4519 | 61.471 | 61.5093 | 61.4717 | 61.5019 | 123.0331 | 61.5569 | 122.946 | 61.4171 | 61.4801 | 123.0255 | 61.4762 | 122.8083 | 61.553 | 61.5569 | 61.4659 | 61.4698
99.5938 | 123.2529 | -61.4685 | 61.6196 | 0.021127 | -0.0451 | -0.021157 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.56 | 0.083796 | 61.5004 | -0.03768 | 0.020767 | 61.557 | 0.021456 | 61.3443 | 61.4896 | 61.4234 | 61.4473 | 61.471 | 61.5048 | 61.4671 | 61.5065 | 123.0285 | 61.5523 | 122.9689 | 61.4308 | 61.4893 | 123.0255 | 61.49 | 122.8129 | 61.5392 | 61.5385 | 61.4796 | 61.4789
100.5938 | 123.2391 | -61.5005 | 61.6058 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.033424 | 61.5691 | 0.083796 | 61.4867 | -0.033101 | 0.029923 | 61.557 | 0.021456 | 61.3398 | 61.5263 | 61.4554 | 61.4885 | 61.503 | 61.5414 | 61.5037 | 61.534 | 123.0697 | 61.5843 | 122.9872 | 61.4674 | 61.5305 | 123.0576 | 61.522 | 122.8403 | 61.5392 | 61.5477 | 61.4567 | 61.4652
101.5938 | 123.2483 | -61.5005 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.038003 | 61.5691 | 0.083796 | 61.4958 | -0.03768 | 0.020767 | 61.557 | 0.016878 | 61.3398 | 61.5263 | 61.46 | 61.484 | 61.5122 | 61.5414 | 61.5083 | 61.5386 | 123.0697 | 61.5843 | 122.9964 | 61.4629 | 61.5213 | 123.0576 | 61.5174 | 122.8403 | 61.5484 | 61.5523 | 61.4751 | 61.4789
102.5938 | 123.3948 | -61.4594 | 61.5646 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.038003 | 61.5737 | 0.088375 | 61.4912 | -0.046838 | 0.020767 | 61.557 | 0.016878 | 61.3398 | 61.4805 | 61.4188 | 61.4428 | 61.4664 | 61.491 | 61.4671 | 61.4974 | 123.0331 | 61.5477 | 122.9506 | 61.4125 | 61.4801 | 123.0164 | 61.4762 | 122.7991 | 61.553 | 61.5569 | 61.4705 | 61.4744
103.5938 | 123.3032 | -61.5005 | 61.5692 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.038003 | 61.5691 | 0.088375 | 61.4867 | -0.03768 | 0.025345 | 61.5662 | 0.021456 | 61.3443 | 61.5263 | 61.4646 | 61.484 | 61.503 | 61.5414 | 61.5083 | 61.5386 | 123.0697 | 61.5889 | 122.9872 | 61.4629 | 61.5259 | 123.0667 | 61.522 | 122.8449 | 61.5438 | 61.5477 | 61.4613 | 61.4652
104.5938 | 123.2574 | -61.496 | 61.6425 | 0.025705 | -0.049678 | -0.021157 | 0.002454 | 0.031687 | 0.016907 | 0.042581 | 61.5691 | 0.079217 | 61.4912 | -0.042259 | 0.025345 | 61.557 | 0.021456 | 61.3535 | 61.5217 | 61.4463 | 61.4748 | 61.4984 | 61.5277 | 61.5129 | 61.5386 | 123.0651 | 61.5752 | 122.9872 | 61.4537 | 61.5213 | 123.053 | 61.5174 | 122.8495 | 61.5438 | 61.5477 | 61.4659 | 61.4698
105.5938 | 123.111 | -61.5417 | 61.5463 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.049999 | 0.00775 | 0.042581 | 61.5691 | 0.088375 | 61.5004 | -0.03768 | 0.025345 | 61.557 | 0.016878 | 61.3443 | 61.5675 | 61.5012 | 61.5297 | 61.5488 | 61.5917 | 61.5495 | 61.5843 | 123.1109 | 61.6301 | 123.0421 | 61.5041 | 61.5671 | 123.0988 | 61.5586 | 122.8861 | 61.5438 | 61.5523 | 61.4751 | 61.4835
106.5938 | 123.2574 | -61.4914 | 61.6241 | 0.030283 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.5737 | 0.083796 | 61.4912 | -0.03768 | 0.029923 | 61.5616 | 0.026035 | 61.3443 | 61.5217 | 61.4463 | 61.4748 | 61.4984 | 61.5368 | 61.4946 | 61.5386 | 123.0651 | 61.5752 | 122.9826 | 61.4537 | 61.5213 | 123.053 | 61.5174 | 122.8357 | 61.5438 | 61.5477 | 61.4613 | 61.4652
107.5938 | 123.2529 | -61.4731 | 61.6379 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.5691 | 0.088375 | 61.505 | -0.042259 | 0.020767 | 61.557 | 0.021456 | 61.3489 | 61.4988 | 61.4326 | 61.4657 | 61.4755 | 61.5093 | 61.4808 | 61.5157 | 123.0422 | 61.5615 | 122.9781 | 61.4308 | 61.4939 | 123.0301 | 61.4945 | 122.822 | 61.5484 | 61.5477 | 61.4842 | 61.4835
108.5938 | 123.1934 | -61.4822 | 61.6425 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.049999 | 0.003172 | 0.038003 | 61.5783 | 0.083796 | 61.4958 | -0.033101 | 0.020767 | 61.5662 | 0.021456 | 61.3398 | 61.5034 | 61.4463 | 61.4702 | 61.4847 | 61.5322 | 61.4854 | 61.5202 | 123.0605 | 61.566 | 122.9781 | 61.4491 | 61.503 | 123.0484 | 61.5037 | 122.822 | 61.5575 | 61.5568 | 61.4751 | 61.4744
109.5938 | 123.3994 | -61.4594 | 61.5784 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.047159 | 61.5691 | 0.083796 | 61.4958 | -0.046838 | 0.020767 | 61.5616 | 0.021456 | 61.3443 | 61.4759 | 61.4188 | 61.4428 | 61.4664 | 61.5002 | 61.4625 | 61.5065 | 123.0285 | 61.5431 | 122.9552 | 61.4125 | 61.4801 | 123.0209 | 61.4808 | 122.8037 | 61.5484 | 61.5477 | 61.4751 | 61.4744
110.5938 | 123.2895 | -61.5097 | 61.5875 | 0.030283 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.5646 | 0.083796 | 61.4912 | -0.028522 | 0.029923 | 61.5616 | 0.026035 | 61.3443 | 61.54 | 61.4646 | 61.4931 | 61.5167 | 61.5551 | 61.5175 | 61.5523 | 123.0743 | 61.5935 | 123.0009 | 61.4812 | 61.5396 | 123.0713 | 61.5357 | 122.8541 | 61.5346 | 61.5385 | 61.4613 | 61.4652
111.5938 | 123.2666 | -61.4777 | 61.6287 | 0.025705 | -0.040521 | -0.012 | 0.01619 | 0.040843 | -0.001406 | 0.047159 | 61.5737 | 0.088375 | 61.5004 | -0.033101 | 0.020767 | 61.5616 | 0.016878 | 61.3443 | 61.5034 | 61.4371 | 61.4657 | 61.4939 | 61.5185 | 61.4763 | 61.5248 | 123.0514 | 61.566 | 122.9781 | 61.4446 | 61.4984 | 123.0392 | 61.4945 | 122.822 | 61.553 | 61.5569 | 61.4796 | 61.4835
112.5938 | 123.262 | -61.4777 | 61.5829 | 0.016548 | -0.049678 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.038003 | 61.5691 | 0.083796 | 61.4821 | -0.042259 | 0.016188 | 61.5616 | 0.016878 | 61.3443 | 61.4942 | 61.428 | 61.4657 | 61.4801 | 61.5139 | 61.4854 | 61.5157 | 123.0468 | 61.5615 | 122.9597 | 61.4354 | 61.4938 | 123.0392 | 61.4945 | 122.822 | 61.553 | 61.5523 | 61.4659 | 61.4652
113.5938 | 123.3765 | -61.4685 | 61.5738 | 0.021127 | -0.0451 | -0.007421 | 0.002454 | 0.040843 | 0.003172 | 0.038003 | 61.5737 | 0.079217 | 61.4912 | -0.042259 | 0.016188 | 61.557 | 0.021456 | 61.3352 | 61.4896 | 61.4234 | 61.4611 | 61.471 | 61.5093 | 61.4717 | 61.5065 | 123.0422 | 61.5477 | 122.9598 | 61.4262 | 61.4847 | 123.0255 | 61.49 | 122.8037 | 61.5575 | 61.5523 | 61.4751 | 61.4698
114.5938 | 123.436 | -61.4502 | 61.5921 | 0.025705 | -0.0451 | -0.016578 | -0.006703 | 0.045421 | -0.001406 | 0.038003 | 61.5691 | 0.079217 | 61.4821 | -0.042259 | 0.029923 | 61.557 | 0.021456 | 61.3489 | 61.4759 | 61.4051 | 61.4336 | 61.4435 | 61.4956 | 61.4488 | 61.4882 | 123.0193 | 61.5294 | 122.9323 | 61.4079 | 61.4801 | 123.0072 | 61.4717 | 122.7991 | 61.5392 | 61.5477 | 61.4522 | 61.4606
115.5938 | 123.2758 | -61.4639 | 61.6058 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.5737 | 0.092954 | 61.4958 | -0.033101 | 0.025345 | 61.5662 | 0.021456 | 61.3489 | 61.4896 | 61.4234 | 61.4474 | 61.4664 | 61.5048 | 61.4717 | 61.5065 | 123.0377 | 61.5569 | 122.9598 | 61.4308 | 61.4893 | 123.0301 | 61.4854 | 122.8129 | 61.5484 | 61.5523 | 61.4705 | 61.4744
116.5938 | 123.3307 | -61.5097 | 61.6196 | 0.030283 | -0.031363 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.5737 | 0.083796 | 61.4867 | -0.033101 | 0.016188 | 61.5662 | 0.021456 | 61.3443 | 61.54 | 61.4783 | 61.4931 | 61.5167 | 61.5505 | 61.5175 | 61.5569 | 123.0834 | 61.5935 | 122.9964 | 61.4766 | 61.5259 | 123.0759 | 61.5312 | 122.8541 | 61.5575 | 61.5523 | 61.4705 | 61.4652
117.5938 | 123.2803 | -61.4685 | 61.6196 | 0.021127 | -0.040521 | -0.021157 | 0.011611 | 0.036265 | 0.003172 | 0.042581 | 61.5691 | 0.088375 | 61.505 | -0.03768 | 0.020767 | 61.557 | 0.021456 | 61.3535 | 61.4896 | 61.428 | 61.4473 | 61.4801 | 61.5048 | 61.4717 | 61.5111 | 123.0377 | 61.5569 | 122.9735 | 61.4308 | 61.4893 | 123.0255 | 61.49 | 122.822 | 61.5484 | 61.5477 | 61.4842 | 61.4835
118.5938 | 123.262 | -61.4777 | 61.6333 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5646 | 0.083796 | 61.4912 | -0.046838 | 0.029923 | 61.5524 | 0.016878 | 61.3489 | 61.4988 | 61.4326 | 61.4657 | 61.4801 | 61.5185 | 61.4808 | 61.5202 | 123.0422 | 61.5615 | 122.9689 | 61.4308 | 61.5076 | 123.0301 | 61.4945 | 122.8266 | 61.5346 | 61.5477 | 61.4613 | 61.4744
119.5938 | 123.2712 | -61.5051 | 61.6196 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.049999 | 0.012329 | 0.051737 | 61.5783 | 0.088375 | 61.5004 | -0.03768 | 0.029923 | 61.5616 | 0.016878 | 61.3398 | 61.5263 | 61.4646 | 61.4931 | 61.5122 | 61.5551 | 61.5175 | 61.5569 | 123.0834 | 61.5935 | 123.0055 | 61.4674 | 61.535 | 123.0667 | 61.522 | 122.8449 | 61.5484 | 61.5614 | 61.4705 | 61.4835
120.5938 | 123.3032 | -61.4731 | 61.6516 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.049999 | 0.003172 | 0.033424 | 61.5737 | 0.083796 | 61.4912 | -0.042259 | 0.025345 | 61.5616 | 0.026035 | 61.3489 | 61.4988 | 61.428 | 61.4565 | 61.4801 | 61.5231 | 61.4763 | 61.5065 | 123.0468 | 61.5569 | 122.9643 | 61.4308 | 61.4984 | 123.0347 | 61.4991 | 122.822 | 61.5484 | 61.5477 | 61.4659 | 61.4652
121.5938 | 123.3124 | -61.4639 | 61.6516 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.5737 | 0.088375 | 61.5004 | -0.046838 | 0.029923 | 61.5707 | 0.021456 | 61.3535 | 61.4805 | 61.4188 | 61.4474 | 61.4664 | 61.5002 | 61.4717 | 61.5065 | 123.0377 | 61.5523 | 122.9643 | 61.4171 | 61.4939 | 123.0347 | 61.4854 | 122.8174 | 61.5438 | 61.5523 | 61.4705 | 61.4789
122.5938 | 123.2986 | -61.4639 | 61.6013 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.049999 | 0.00775 | 0.047159 | 61.5691 | 0.079217 | 61.4912 | -0.03768 | 0.020767 | 61.5616 | 0.021456 | 61.3443 | 61.4851 | 61.4234 | 61.4519 | 61.4755 | 61.5139 | 61.4717 | 61.5111 | 123.0331 | 61.5431 | 122.9552 | 61.4262 | 61.4847 | 123.0255 | 61.4854 | 122.8083 | 61.5484 | 61.5477 | 61.4705 | 61.4698
123.5938 | 123.3398 | -61.4731 | 61.5875 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.5646 | 0.083796 | 61.4958 | -0.046838 | 0.020767 | 61.5616 | 0.026035 | 61.3443 | 61.4942 | 61.428 | 61.4565 | 61.4801 | 61.5139 | 61.4763 | 61.5111 | 123.0377 | 61.5569 | 122.9689 | 61.4262 | 61.4939 | 123.0347 | 61.4991 | 122.8174 | 61.5438 | 61.5385 | 61.4751 | 61.4698
124.5938 | 123.2666 | -61.5143 | 61.6058 | 0.021127 | -0.0451 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.042581 | 61.5783 | 0.097532 | 61.5004 | -0.03768 | 0.020767 | 61.5662 | 0.016878 | 61.3489 | 61.5354 | 61.4692 | 61.4977 | 61.5259 | 61.5551 | 61.522 | 61.5569 | 123.0926 | 61.6118 | 123.0147 | 61.4766 | 61.535 | 123.0804 | 61.5312 | 122.8632 | 61.5575 | 61.5614 | 61.4796 | 61.4835
125.5938 | 123.2986 | -61.4639 | 61.5967 | 0.030283 | -0.0451 | -0.021157 | 0.007033 | 0.040843 | 0.00775 | 0.033424 | 61.5691 | 0.083796 | 61.4867 | -0.03768 | 0.025345 | 61.5662 | 0.016878 | 61.3535 | 61.4942 | 61.4188 | 61.4428 | 61.471 | 61.5048 | 61.4717 | 61.4974 | 123.0331 | 61.5477 | 122.9506 | 61.4262 | 61.4893 | 123.0301 | 61.4808 | 122.8174 | 61.5438 | 61.5523 | 61.4613 | 61.4698
126.5938 | 123.3261 | -61.4731 | 61.6013 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.5783 | 0.083796 | 61.505 | -0.03768 | 0.025345 | 61.5524 | 0.016878 | 61.3489 | 61.4988 | 61.4326 | 61.4565 | 61.4847 | 61.5185 | 61.4763 | 61.5157 | 123.0514 | 61.5569 | 122.9781 | 61.4354 | 61.4984 | 123.0255 | 61.49 | 122.822 | 61.553 | 61.5614 | 61.4796 | 61.4881
127.5938 | 123.2529 | -61.4777 | 61.615 | 0.025705 | -0.040521 | -0.021157 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.5783 | 0.083796 | 61.4867 | -0.046838 | 0.025345 | 61.5616 | 0.016878 | 61.3443 | 61.5034 | 61.4371 | 61.4565 | 61.4847 | 61.5231 | 61.4854 | 61.5202 | 123.056 | 61.5615 | 122.9643 | 61.4308 | 61.503 | 123.0392 | 61.4945 | 122.822 | 61.553 | 61.5614 | 61.4613 | 61.4698
128.5938 | 123.317 | -61.4914 | 61.5784 | 0.021127 | -0.035942 | -0.021157 | -0.002124 | 0.040843 | 0.00775 | 0.042581 | 61.5737 | 0.083796 | 61.4912 | -0.03768 | 0.020767 | 61.557 | 0.021456 | 61.3443 | 61.5125 | 61.4555 | 61.4702 | 61.4893 | 61.5322 | 61.4991 | 61.534 | 123.0651 | 61.5752 | 122.9826 | 61.4537 | 61.5122 | 123.0484 | 61.5129 | 122.8357 | 61.553 | 61.5523 | 61.4705 | 61.4698
129.5938 | 123.381 | -61.441 | 61.6241 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5737 | 0.092954 | 61.505 | -0.042259 | 0.025345 | 61.5616 | 0.021456 | 61.3489 | 61.4622 | 61.4005 | 61.4245 | 61.4435 | 61.4819 | 61.4442 | 61.4836 | 123.0148 | 61.534 | 122.946 | 61.3988 | 61.4664 | 123.0026 | 61.4625 | 122.79 | 61.5484 | 61.5523 | 61.4796 | 61.4835
130.5938 | 123.2941 | -61.5005 | 61.6379 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.049999 | 0.003172 | 0.051737 | 61.5737 | 0.083796 | 61.4867 | -0.03768 | 0.034501 | 61.5616 | 0.021456 | 61.3489 | 61.5217 | 61.46 | 61.484 | 61.5076 | 61.5505 | 61.5037 | 61.5523 | 123.0743 | 61.5843 | 122.9872 | 61.4629 | 61.535 | 123.0621 | 61.522 | 122.8495 | 61.5392 | 61.5523 | 61.4522 | 61.4652
131.5938 | 123.2391 | -61.496 | 61.6241 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.5737 | 0.088375 | 61.4958 | -0.042259 | 0.025345 | 61.5707 | 0.021456 | 61.3489 | 61.5217 | 61.4555 | 61.484 | 61.503 | 61.5368 | 61.4991 | 61.5386 | 123.0697 | 61.5843 | 122.9918 | 61.4537 | 61.5213 | 123.0667 | 61.5174 | 122.8449 | 61.5484 | 61.5523 | 61.4705 | 61.4744
132.5938 | 123.2574 | -61.5189 | 61.6013 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.047159 | 61.5737 | 0.079217 | 61.4958 | -0.046838 | 0.016188 | 61.5662 | 0.016878 | 61.3443 | 61.5446 | 61.4829 | 61.5069 | 61.5213 | 61.5551 | 61.5175 | 61.566 | 123.0926 | 61.5981 | 123.0147 | 61.472 | 61.535 | 123.085 | 61.5357 | 122.8632 | 61.5575 | 61.5569 | 61.4796 | 61.4789
133.5938 | 123.3124 | -61.4594 | 61.5829 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5691 | 0.088375 | 61.5004 | -0.046838 | 0.025345 | 61.5616 | 0.026035 | 61.3489 | 61.4759 | 61.4143 | 61.4428 | 61.4618 | 61.5002 | 61.4625 | 61.5019 | 123.0285 | 61.5477 | 122.9598 | 61.4125 | 61.4847 | 123.0209 | 61.4854 | 122.8083 | 61.5438 | 61.5431 | 61.4751 | 61.4744
134.5938 | 123.3765 | -61.4639 | 61.5829 | 0.016548 | -0.049678 | -0.012 | 0.002454 | 0.045421 | -0.001406 | 0.038003 | 61.5691 | 0.083796 | 61.4958 | -0.046838 | 0.025345 | 61.5616 | 0.012299 | 61.3443 | 61.4805 | 61.4143 | 61.4519 | 61.4664 | 61.5093 | 61.4625 | 61.5019 | 123.0331 | 61.5477 | 122.9598 | 61.4171 | 61.4893 | 123.0255 | 61.4762 | 122.8083 | 61.5438 | 61.5569 | 61.4705 | 61.4835
135.5938 | 123.3398 | -61.4685 | 61.615 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.042581 | 61.5691 | 0.083796 | 61.5004 | -0.046838 | 0.029923 | 61.557 | 0.012299 | 61.3443 | 61.4988 | 61.428 | 61.4519 | 61.471 | 61.5048 | 61.4671 | 61.5111 | 123.0377 | 61.5523 | 122.9689 | 61.4217 | 61.4984 | 123.0255 | 61.4808 | 122.8129 | 61.5392 | 61.5569 | 61.4705 | 61.4881
136.5938 | 123.317 | -61.496 | 61.6104 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.5783 | 0.088375 | 61.4912 | -0.042259 | 0.034501 | 61.557 | 0.021456 | 61.3535 | 61.5263 | 61.4509 | 61.484 | 61.503 | 61.5414 | 61.4991 | 61.5386 | 123.0743 | 61.5843 | 122.9872 | 61.4537 | 61.5305 | 123.053 | 61.5174 | 122.8495 | 61.5438 | 61.5568 | 61.4567 | 61.4698
137.5938 | 123.317 | -61.4639 | 61.6104 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.047159 | 61.5737 | 0.088375 | 61.505 | -0.046838 | 0.034501 | 61.5662 | 0.012299 | 61.3489 | 61.4851 | 61.4234 | 61.4474 | 61.4664 | 61.5093 | 61.4717 | 61.5111 | 123.0377 | 61.5523 | 122.9689 | 61.4171 | 61.4984 | 123.0301 | 61.4762 | 122.8129 | 61.5392 | 61.5614 | 61.4705 | 61.4927
138.5938 | 123.2941 | -61.4914 | 61.6425 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.038003 | 61.5737 | 0.092954 | 61.4958 | -0.046838 | 0.025345 | 61.5616 | 0.016878 | 61.3443 | 61.5171 | 61.4509 | 61.4794 | 61.4984 | 61.5277 | 61.4991 | 61.5294 | 123.0651 | 61.5843 | 122.9872 | 61.4446 | 61.5167 | 123.053 | 61.5083 | 122.8357 | 61.5484 | 61.5569 | 61.4705 | 61.4789
139.5938 | 123.3032 | -61.4639 | 61.5784 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.5783 | 0.083796 | 61.4958 | -0.046838 | 0.025345 | 61.557 | 0.021456 | 61.3398 | 61.4896 | 61.4188 | 61.4519 | 61.4664 | 61.5002 | 61.4671 | 61.5019 | 123.0422 | 61.5477 | 122.9598 | 61.4171 | 61.4893 | 123.0209 | 61.4854 | 122.8037 | 61.553 | 61.5568 | 61.4705 | 61.4744
140.5938 | 123.3124 | -61.4548 | 61.615 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.054577 | -0.001406 | 0.047159 | 61.5829 | 0.092954 | 61.4912 | -0.055996 | 0.025345 | 61.5616 | 0.026035 | 61.3215 | 61.4851 | 61.4143 | 61.4336 | 61.4618 | 61.5094 | 61.4534 | 61.5019 | 123.0377 | 61.5477 | 122.946 | 61.3988 | 61.4801 | 123.0164 | 61.4808 | 122.7762 | 61.5575 | 61.5568 | 61.4659 | 61.4652
141.5938 | 123.3078 | -61.4685 | 61.615 | 0.025705 | -0.040521 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.5783 | 0.092954 | 61.4958 | -0.092628 | 0.034501 | 61.5662 | 0.026035 | 61.3581 | 61.4942 | 61.428 | 61.4565 | 61.4801 | 61.5139 | 61.4671 | 61.5111 | 123.0468 | 61.5615 | 122.9643 | 61.3759 | 61.503 | 123.0347 | 61.4945 | 122.8266 | 61.5438 | 61.5523 | 61.4613 | 61.4698
142.5938 | 123.2941 | -61.4914 | 61.6058 | 0.030283 | -0.040521 | -0.007421 | 0.01619 | 0.045421 | 0.003172 | 0.047159 | 61.5829 | 0.092954 | 61.4867 | -0.092628 | 0.025345 | 61.5616 | 0.016878 | 61.3856 | 61.5217 | 61.4509 | 61.484 | 61.5076 | 61.5368 | 61.4946 | 61.5386 | 123.0743 | 61.5843 | 122.9781 | 61.3988 | 61.5167 | 123.053 | 61.5083 | 122.8769 | 61.5575 | 61.566 | 61.4613 | 61.4698
143.5938 | 123.317 | -61.4594 | 61.6196 | 0.025705 | -0.0451 | -0.021157 | 0.007033 | 0.031687 | 0.00775 | 0.042581 | 61.5783 | 0.092954 | 61.4958 | -0.078891 | 0.029923 | 61.5616 | 0.012299 | 61.3489 | 61.4851 | 61.4143 | 61.4382 | 61.4664 | 61.491 | 61.4671 | 61.5019 | 123.0377 | 61.5523 | 122.9552 | 61.3805 | 61.4893 | 123.0209 | 61.4716 | 122.8083 | 61.5484 | 61.566 | 61.4659 | 61.4835
144.5938 | 123.3078 | -61.4685 | 61.6241 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.042581 | 61.5737 | 0.088375 | 61.4912 | -0.033101 | 0.029923 | 61.5616 | 0.030613 | 61.3398 | 61.4896 | 61.4234 | 61.4519 | 61.4664 | 61.5093 | 61.4717 | 61.5111 | 123.0422 | 61.5569 | 122.9598 | 61.4354 | 61.4984 | 123.0301 | 61.4991 | 122.8083 | 61.5438 | 61.5431 | 61.4613 | 61.4606
145.5938 | 123.2574 | -61.4685 | 61.6425 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.012329 | 0.047159 | 61.5783 | 0.088375 | 61.5096 | -0.042259 | 0.025345 | 61.5662 | 0.021456 | 61.3581 | 61.4942 | 61.4234 | 61.4519 | 61.4755 | 61.5048 | 61.4808 | 61.5157 | 123.0468 | 61.5569 | 122.9781 | 61.4262 | 61.4939 | 123.0347 | 61.49 | 122.8266 | 61.553 | 61.5568 | 61.4842 | 61.4881
146.5938 | 123.2712 | -61.4685 | 61.6333 | 0.021127 | -0.0451 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.047159 | 61.5783 | 0.088375 | 61.4912 | -0.03768 | 0.025345 | 61.5616 | 0.026035 | 61.3443 | 61.4896 | 61.4234 | 61.4611 | 61.4755 | 61.5048 | 61.4808 | 61.5157 | 123.0468 | 61.5569 | 122.9598 | 61.4308 | 61.4939 | 123.0301 | 61.4945 | 122.8129 | 61.553 | 61.5523 | 61.4659 | 61.4652
147.5938 | 123.3353 | -61.4685 | 61.6425 | 0.016548 | -0.040521 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.5783 | 0.088375 | 61.4958 | -0.046838 | 0.034501 | 61.557 | 0.016878 | 61.3581 | 61.4851 | 61.428 | 61.4611 | 61.4801 | 61.5093 | 61.4717 | 61.5111 | 123.0468 | 61.5569 | 122.9643 | 61.4217 | 61.503 | 123.0255 | 61.4854 | 122.8266 | 61.5438 | 61.5614 | 61.4613 | 61.4789
148.5938 | 123.262 | -61.496 | 61.6013 | 0.025705 | -0.040521 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.5783 | 0.083796 | 61.4912 | -0.042259 | 0.029923 | 61.5616 | 0.021456 | 61.3398 | 61.5217 | 61.4555 | 61.484 | 61.5076 | 61.5414 | 61.4991 | 61.5386 | 123.0743 | 61.5798 | 122.9872 | 61.4537 | 61.5259 | 123.0576 | 61.5174 | 122.8357 | 61.5484 | 61.5568 | 61.4613 | 61.4698
149.5938 | 123.23 | -61.4914 | 61.6287 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.5783 | 0.088375 | 61.5004 | -0.042259 | 0.029923 | 61.5616 | 0.021456 | 61.3489 | 61.5171 | 61.4509 | 61.484 | 61.4938 | 61.5277 | 61.4946 | 61.534 | 123.0697 | 61.5798 | 122.9918 | 61.4491 | 61.5213 | 123.053 | 61.5129 | 122.8403 | 61.5484 | 61.5568 | 61.4705 | 61.4789
150.5938 | 123.1796 | -61.4777 | 61.615 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.5737 | 0.083796 | 61.4867 | -0.03768 | 0.029923 | 61.5662 | 0.016878 | 61.3489 | 61.4988 | 61.4371 | 61.4657 | 61.4801 | 61.5185 | 61.4808 | 61.5248 | 123.0514 | 61.5615 | 122.9643 | 61.44 | 61.5076 | 123.0438 | 61.4945 | 122.8266 | 61.5438 | 61.5569 | 61.4567 | 61.4698
151.5938 | 123.2666 | -61.4914 | 61.6379 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.5783 | 0.083796 | 61.5004 | -0.03768 | 0.025345 | 61.5616 | 0.021456 | 61.3535 | 61.5217 | 61.4509 | 61.4748 | 61.4938 | 61.5322 | 61.4991 | 61.534 | 123.0697 | 61.5752 | 122.9918 | 61.4537 | 61.5167 | 123.053 | 61.5129 | 122.8449 | 61.553 | 61.5568 | 61.4751 | 61.4789
152.5938 | 123.2574 | -61.5005 | 61.6287 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.5691 | 0.088375 | 61.4912 | -0.03768 | 0.020767 | 61.557 | 0.016878 | 61.3535 | 61.5263 | 61.46 | 61.484 | 61.503 | 61.5414 | 61.5083 | 61.5431 | 123.0697 | 61.5889 | 122.9918 | 61.4629 | 61.5213 | 123.0576 | 61.5174 | 122.8541 | 61.5484 | 61.5523 | 61.4705 | 61.4744
153.5938 | 123.2437 | -61.4777 | 61.6516 | 0.021127 | -0.049678 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.5829 | 0.083796 | 61.5004 | -0.042259 | 0.025345 | 61.5662 | 0.016878 | 61.3489 | 61.4988 | 61.428 | 61.4657 | 61.4847 | 61.5185 | 61.4854 | 61.5202 | 123.0605 | 61.5615 | 122.9781 | 61.4354 | 61.503 | 123.0438 | 61.4945 | 122.8266 | 61.5575 | 61.566 | 61.4751 | 61.4835
154.5938 | 123.2208 | -61.5005 | 61.6241 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.047159 | 61.5691 | 0.092954 | 61.505 | -0.042259 | 0.034501 | 61.5616 | 0.026035 | 61.3443 | 61.5263 | 61.46 | 61.484 | 61.5122 | 61.5414 | 61.5037 | 61.5477 | 123.0697 | 61.5935 | 123.0055 | 61.4583 | 61.535 | 123.0621 | 61.5266 | 122.8449 | 61.5346 | 61.5431 | 61.4705 | 61.4789
155.5938 | 123.2162 | -61.4822 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.047159 | 61.5783 | 0.088375 | 61.4867 | -0.042259 | 0.029923 | 61.5662 | 0.012299 | 61.3581 | 61.5079 | 61.4417 | 61.4657 | 61.4939 | 61.5185 | 61.4854 | 61.5294 | 123.0605 | 61.5706 | 122.9689 | 61.44 | 61.5122 | 123.0484 | 61.4945 | 122.8403 | 61.5484 | 61.566 | 61.4567 | 61.4744
156.5938 | 123.2025 | -61.4594 | 61.6013 | 0.030283 | -0.040521 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.5783 | 0.088375 | 61.4912 | -0.033101 | 0.020767 | 61.557 | 0.016878 | 61.3489 | 61.4896 | 61.4188 | 61.4474 | 61.471 | 61.5048 | 61.4625 | 61.5019 | 123.0377 | 61.5477 | 122.9506 | 61.4262 | 61.4801 | 123.0164 | 61.4762 | 122.8083 | 61.5575 | 61.5614 | 61.4705 | 61.4744
157.5938 | 123.2941 | -61.496 | 61.6196 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.045421 | -0.001406 | 0.047159 | 61.5737 | 0.092954 | 61.5004 | -0.042259 | 0.034501 | 61.5616 | 0.021456 | 61.3489 | 61.5171 | 61.4509 | 61.484 | 61.4984 | 61.5414 | 61.4946 | 61.5431 | 123.0697 | 61.5889 | 122.9964 | 61.4537 | 61.5305 | 123.0576 | 61.5174 | 122.8449 | 61.5392 | 61.5523 | 61.4659 | 61.4789
158.5938 | 123.2529 | -61.496 | 61.647 | 0.021127 | -0.049678 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.042581 | 61.5875 | 0.092954 | 61.4958 | -0.042259 | 0.029923 | 61.5662 | 0.012299 | 61.3535 | 61.5171 | 61.4463 | 61.484 | 61.503 | 61.5322 | 61.4946 | 61.5386 | 123.0834 | 61.5889 | 122.9918 | 61.4537 | 61.5259 | 123.0621 | 61.5083 | 122.8495 | 61.5575 | 61.5752 | 61.4659 | 61.4835
159.5938 | 123.349 | -61.4685 | 61.5829 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.036265 | -0.005985 | 0.038003 | 61.5829 | 0.083796 | 61.4958 | -0.046838 | 0.025345 | 61.557 | 0.012299 | 61.3489 | 61.4896 | 61.4234 | 61.4565 | 61.471 | 61.5048 | 61.4625 | 61.5065 | 123.0514 | 61.5523 | 122.9643 | 61.4217 | 61.4939 | 123.0255 | 61.4808 | 122.8174 | 61.5575 | 61.5706 | 61.4705 | 61.4835
160.5938 | 123.2529 | -61.4731 | 61.647 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.054577 | 0.003172 | 0.042581 | 61.5783 | 0.083796 | 61.5004 | -0.042259 | 0.029923 | 61.5707 | 0.012299 | 61.3627 | 61.4942 | 61.4326 | 61.4611 | 61.4847 | 61.5277 | 61.4763 | 61.5157 | 123.0514 | 61.5569 | 122.9735 | 61.4308 | 61.503 | 123.0438 | 61.4854 | 122.8357 | 61.5484 | 61.566 | 61.4705 | 61.4881
161.5938 | 123.2666 | -61.4639 | 61.6562 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | -0.001406 | 0.047159 | 61.5829 | 0.088375 | 61.4867 | -0.03768 | 0.029923 | 61.5616 | 0.021456 | 61.3581 | 61.4851 | 61.4188 | 61.4474 | 61.4664 | 61.5002 | 61.4625 | 61.5111 | 123.0468 | 61.5523 | 122.9506 | 61.4262 | 61.4939 | 123.0255 | 61.4854 | 122.822 | 61.553 | 61.5614 | 61.4567 | 61.4652
162.5938 | 123.2483 | -61.4685 | 61.6104 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5829 | 0.088375 | 61.4821 | -0.046838 | 0.034501 | 61.5616 | 0.021456 | 61.3535 | 61.4896 | 61.4234 | 61.4519 | 61.471 | 61.5093 | 61.4717 | 61.5111 | 123.0514 | 61.5569 | 122.9506 | 61.4217 | 61.503 | 123.0301 | 61.49 | 122.822 | 61.5484 | 61.5614 | 61.4476 | 61.4606
163.5938 | 123.3627 | -61.4456 | 61.6333 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.5737 | 0.088375 | 61.4912 | -0.03768 | 0.029923 | 61.5662 | 0.021456 | 61.3535 | 61.4667 | 61.4005 | 61.429 | 61.4481 | 61.491 | 61.4534 | 61.4882 | 123.0193 | 61.534 | 122.9369 | 61.4079 | 61.4755 | 123.0118 | 61.4671 | 122.7991 | 61.5438 | 61.5523 | 61.4613 | 61.4698
164.5938 | 123.3215 | -61.4822 | 61.6058 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.049999 | 0.00775 | 0.042581 | 61.5783 | 0.088375 | 61.5004 | -0.03768 | 0.029923 | 61.5662 | 0.016878 | 61.3535 | 61.5034 | 61.4417 | 61.4702 | 61.4893 | 61.5322 | 61.49 | 61.5248 | 123.0605 | 61.5706 | 122.9826 | 61.4446 | 61.5122 | 123.0484 | 61.4991 | 122.8357 | 61.5484 | 61.5614 | 61.4705 | 61.4835
165.5938 | 123.3765 | -61.4502 | 61.615 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.5737 | 0.092954 | 61.4958 | -0.03768 | 0.029923 | 61.5616 | 0.021456 | 61.3581 | 61.4713 | 61.4051 | 61.4336 | 61.4526 | 61.4865 | 61.4534 | 61.4928 | 123.0239 | 61.5431 | 122.946 | 61.4125 | 61.4801 | 123.0118 | 61.4717 | 122.8083 | 61.5438 | 61.5523 | 61.4659 | 61.4744
166.5938 | 123.262 | -61.5189 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.5783 | 0.088375 | 61.4867 | -0.03768 | 0.034501 | 61.5616 | 0.007721 | 61.3535 | 61.5446 | 61.4783 | 61.5023 | 61.5213 | 61.5597 | 61.5175 | 61.5569 | 123.0972 | 61.6072 | 123.0055 | 61.4812 | 61.5534 | 123.0804 | 61.5266 | 122.8724 | 61.5438 | 61.5706 | 61.4522 | 61.4789
167.5938 | 123.2986 | -61.4456 | 61.6287 | 0.025705 | -0.049678 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5783 | 0.092954 | 61.4958 | -0.03768 | 0.029923 | 61.5616 | 0.012299 | 61.3535 | 61.4713 | 61.3959 | 61.429 | 61.4481 | 61.4865 | 61.4488 | 61.4882 | 123.0239 | 61.5386 | 122.9414 | 61.4079 | 61.4755 | 123.0072 | 61.4579 | 122.7991 | 61.5484 | 61.566 | 61.4659 | 61.4835
168.5938 | 123.2895 | -61.4685 | 61.615 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.5829 | 0.088375 | 61.5004 | -0.042259 | 0.029923 | 61.557 | 0.012299 | 61.3535 | 61.4942 | 61.4234 | 61.4519 | 61.471 | 61.5139 | 61.4717 | 61.5111 | 123.0514 | 61.5569 | 122.9689 | 61.4262 | 61.4984 | 123.0255 | 61.4808 | 122.822 | 61.553 | 61.5706 | 61.4705 | 61.4881
169.5938 | 123.2986 | -61.4822 | 61.6425 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.00775 | 0.038003 | 61.5737 | 0.092954 | 61.4958 | -0.033101 | 0.029923 | 61.5662 | 0.016878 | 61.3581 | 61.5079 | 61.4417 | 61.4657 | 61.4801 | 61.5139 | 61.49 | 61.5202 | 123.056 | 61.5752 | 122.9781 | 61.4491 | 61.5122 | 123.0484 | 61.4991 | 122.8403 | 61.5438 | 61.5569 | 61.4659 | 61.4789
170.5938 | 123.3398 | -61.4639 | 61.6562 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.5691 | 0.088375 | 61.4912 | -0.042259 | 0.029923 | 61.5662 | 0.003143 | 61.3535 | 61.4805 | 61.4234 | 61.4474 | 61.471 | 61.5002 | 61.4671 | 61.5019 | 123.0331 | 61.5523 | 122.9552 | 61.4217 | 61.4939 | 123.0301 | 61.4671 | 122.8174 | 61.5392 | 61.566 | 61.4613 | 61.4881
171.5938 | 123.3444 | -61.4868 | 61.6425 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5829 | 0.083796 | 61.4867 | -0.042259 | 0.029923 | 61.5662 | 0.007721 | 61.3489 | 61.5125 | 61.4463 | 61.4702 | 61.4938 | 61.5231 | 61.49 | 61.5202 | 123.0697 | 61.5706 | 122.9735 | 61.4446 | 61.5167 | 123.053 | 61.4945 | 122.8357 | 61.553 | 61.5752 | 61.4567 | 61.4789
172.5938 | 123.3215 | -61.4914 | 61.6241 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5783 | 0.083796 | 61.5004 | -0.042259 | 0.029923 | 61.5707 | 0.003143 | 61.3535 | 61.5171 | 61.4463 | 61.4702 | 61.4938 | 61.5322 | 61.4946 | 61.534 | 123.0697 | 61.5752 | 122.9918 | 61.4491 | 61.5213 | 123.0621 | 61.4945 | 122.8449 | 61.5484 | 61.5752 | 61.4705 | 61.4973
173.5938 | 123.2712 | -61.4868 | 61.647 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.051737 | 61.5829 | 0.083796 | 61.4958 | -0.042259 | 0.029923 | 61.5662 | -0.001436 | 61.3489 | 61.5125 | 61.4417 | 61.4702 | 61.4938 | 61.5231 | 61.49 | 61.5386 | 123.0697 | 61.5706 | 122.9826 | 61.4446 | 61.5167 | 123.053 | 61.4854 | 122.8357 | 61.553 | 61.5843 | 61.4659 | 61.4973
174.5938 | 123.2986 | -61.4685 | 61.6562 | 0.025705 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.5783 | 0.088375 | 61.4912 | -0.042259 | 0.029923 | 61.5662 | -0.001436 | 61.3535 | 61.4942 | 61.428 | 61.4611 | 61.4755 | 61.5048 | 61.4717 | 61.5111 | 123.0468 | 61.5569 | 122.9598 | 61.4262 | 61.4984 | 123.0347 | 61.4671 | 122.822 | 61.5484 | 61.5797 | 61.4613 | 61.4927
175.5938 | 123.3765 | -61.4548 | 61.5967 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.036265 | 0.003172 | 0.042581 | 61.5783 | 0.079217 | 61.4867 | -0.046838 | 0.020767 | 61.5707 | 0.003143 | 61.3535 | 61.4713 | 61.4097 | 61.4428 | 61.4526 | 61.491 | 61.4579 | 61.4974 | 123.0331 | 61.534 | 122.9414 | 61.4079 | 61.4755 | 123.0255 | 61.4579 | 122.8083 | 61.5575 | 61.5752 | 61.4659 | 61.4835
176.5938 | 123.2346 | -61.4777 | 61.6699 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.038003 | 61.5829 | 0.088375 | 61.4912 | -0.042259 | 0.025345 | 61.5616 | 0.007721 | 61.3535 | 61.4942 | 61.4326 | 61.4611 | 61.4755 | 61.5185 | 61.4808 | 61.5157 | 123.0605 | 61.566 | 122.9689 | 61.4354 | 61.503 | 123.0392 | 61.4854 | 122.8312 | 61.5575 | 61.5752 | 61.4659 | 61.4835
177.5938 | 123.3902 | -61.4594 | 61.5967 | 0.021127 | -0.049678 | -0.021157 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.5737 | 0.079217 | 61.4958 | -0.03768 | 0.025345 | 61.5662 | 0.012299 | 61.3443 | 61.4805 | 61.4097 | 61.4382 | 61.4618 | 61.5002 | 61.4671 | 61.5019 | 123.0331 | 61.5386 | 122.9552 | 61.4217 | 61.4847 | 123.0255 | 61.4716 | 122.8037 | 61.5484 | 61.5614 | 61.4705 | 61.4835
178.5938 | 123.317 | -61.496 | 61.6058 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.00775 | 0.047159 | 61.5783 | 0.097532 | 61.4958 | -0.042259 | 0.029923 | 61.5616 | 0.012299 | 61.3535 | 61.5171 | 61.4509 | 61.4794 | 61.503 | 61.5322 | 61.5037 | 61.5431 | 123.0743 | 61.5935 | 122.9918 | 61.4537 | 61.5259 | 123.0576 | 61.5083 | 122.8495 | 61.5484 | 61.566 | 61.4659 | 61.4835
179.5938 | 123.3673 | -61.4502 | 61.6104 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.5783 | 0.088375 | 61.4958 | -0.046838 | 0.025345 | 61.5662 | 0.016878 | 61.3535 | 61.4667 | 61.4097 | 61.4382 | 61.4572 | 61.491 | 61.4488 | 61.4882 | 123.0285 | 61.5386 | 122.946 | 61.4034 | 61.4755 | 123.0164 | 61.4671 | 122.8037 | 61.553 | 61.5614 | 61.4705 | 61.4789
180.5938 | 123.2803 | -61.496 | 61.6516 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.038003 | 61.5829 | 0.083796 | 61.4867 | -0.042259 | 0.029923 | 61.5662 | 0.012299 | 61.3489 | 61.5263 | 61.4555 | 61.484 | 61.503 | 61.5414 | 61.5037 | 61.534 | 123.0789 | 61.5798 | 122.9826 | 61.4537 | 61.5259 | 123.0621 | 61.5083 | 122.8449 | 61.553 | 61.5706 | 61.4567 | 61.4744
181.5938 | 123.3307 | -61.4731 | 61.6196 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.038003 | 61.5783 | 0.092954 | 61.4912 | -0.03768 | 0.029923 | 61.5662 | 0.016878 | 61.3535 | 61.4988 | 61.4326 | 61.4611 | 61.4755 | 61.5185 | 61.4808 | 61.5111 | 123.0514 | 61.566 | 122.9643 | 61.4354 | 61.503 | 123.0392 | 61.49 | 122.8266 | 61.5484 | 61.5614 | 61.4613 | 61.4744
182.5938 | 123.3856 | -61.4548 | 61.6196 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.5737 | 0.088375 | 61.5004 | -0.033101 | 0.034501 | 61.5707 | 0.021456 | 61.3489 | 61.4805 | 61.4097 | 61.4428 | 61.4572 | 61.491 | 61.4534 | 61.4928 | 123.0285 | 61.5431 | 122.9552 | 61.4217 | 61.4893 | 123.0255 | 61.4762 | 122.8037 | 61.5392 | 61.5523 | 61.4659 | 61.4789
183.5938 | 123.4177 | -61.4365 | 61.6058 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.047159 | 61.5737 | 0.088375 | 61.4912 | -0.042259 | 0.025345 | 61.5524 | 0.021456 | 61.3535 | 61.4576 | 61.3959 | 61.4199 | 61.4389 | 61.4727 | 61.4396 | 61.4836 | 123.0102 | 61.5248 | 122.9277 | 61.3942 | 61.4618 | 122.9889 | 61.4579 | 122.79 | 61.5484 | 61.5523 | 61.4659 | 61.4698
184.5938 | 123.2574 | -61.4914 | 61.6425 | 0.030283 | -0.040521 | -0.002842 | 0.007033 | 0.045421 | -0.001406 | 0.042581 | 61.5783 | 0.083796 | 61.4958 | -0.042259 | 0.029923 | 61.5707 | 0.021456 | 61.3535 | 61.5217 | 61.4509 | 61.4886 | 61.4984 | 61.5368 | 61.49 | 61.534 | 123.0697 | 61.5752 | 122.9872 | 61.4491 | 61.5213 | 123.0621 | 61.5129 | 122.8449 | 61.5484 | 61.5568 | 61.4659 | 61.4744
185.5938 | 123.3994 | -61.4594 | 61.5967 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5875 | 0.092954 | 61.4958 | -0.03768 | 0.029923 | 61.5616 | 0.021456 | 61.3535 | 61.4805 | 61.4188 | 61.4474 | 61.4618 | 61.5002 | 61.4625 | 61.5019 | 123.0468 | 61.5523 | 122.9552 | 61.4217 | 61.4893 | 123.0209 | 61.4808 | 122.8129 | 61.5575 | 61.566 | 61.4659 | 61.4744
186.5938 | 123.3582 | -61.4548 | 61.6196 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.038003 | 61.5783 | 0.088375 | 61.4867 | -0.046838 | 0.029923 | 61.5662 | 0.026035 | 61.3535 | 61.4759 | 61.4097 | 61.4428 | 61.4618 | 61.5002 | 61.4625 | 61.4928 | 123.0331 | 61.5431 | 122.9414 | 61.4079 | 61.4847 | 123.0209 | 61.4808 | 122.8083 | 61.5484 | 61.5523 | 61.4567 | 61.4606
187.5938 | 123.3719 | -61.4731 | 61.5646 | 0.030283 | -0.049678 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.038003 | 61.5783 | 0.088375 | 61.4958 | -0.03768 | 0.029923 | 61.5662 | 0.026035 | 61.3489 | 61.5034 | 61.4234 | 61.4565 | 61.4801 | 61.5185 | 61.4763 | 61.5111 | 123.0514 | 61.5615 | 122.9689 | 61.4354 | 61.503 | 123.0392 | 61.4991 | 122.822 | 61.5484 | 61.5523 | 61.4659 | 61.4698
188.5938 | 123.2666 | -61.5097 | 61.615 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.038003 | 61.5783 | 0.092954 | 61.4958 | -0.033101 | 0.025345 | 61.5616 | 0.026035 | 61.3489 | 61.5354 | 61.4646 | 61.4977 | 61.5122 | 61.5505 | 61.5129 | 61.5477 | 123.088 | 61.6027 | 123.0055 | 61.4766 | 61.535 | 123.0713 | 61.5357 | 122.8586 | 61.553 | 61.5523 | 61.4705 | 61.4698
189.5938 | 123.3078 | -61.4868 | 61.6562 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.049999 | 0.00775 | 0.038003 | 61.5875 | 0.088375 | 61.505 | -0.03768 | 0.029923 | 61.5662 | 0.021456 | 61.3535 | 61.5125 | 61.4463 | 61.4748 | 61.4893 | 61.5368 | 61.4946 | 61.5248 | 123.0743 | 61.5752 | 122.9918 | 61.4491 | 61.5167 | 123.053 | 61.5083 | 122.8403 | 61.5575 | 61.566 | 61.4751 | 61.4835
190.5938 | 123.4039 | -61.4685 | 61.5967 | 0.021127 | -0.035942 | -0.021157 | 0.002454 | 0.040843 | -0.001406 | 0.042581 | 61.5783 | 0.088375 | 61.4912 | -0.03768 | 0.025345 | 61.5616 | 0.016878 | 61.3489 | 61.4896 | 61.4326 | 61.4473 | 61.471 | 61.5093 | 61.4671 | 61.5111 | 123.0468 | 61.5569 | 122.9598 | 61.4308 | 61.4939 | 123.0301 | 61.4854 | 122.8174 | 61.553 | 61.5614 | 61.4659 | 61.4744
191.5938 | 123.3719 | -61.4685 | 61.6058 | 0.025705 | -0.040521 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.5783 | 0.079217 | 61.4958 | -0.042259 | 0.025345 | 61.5662 | 0.021456 | 61.3581 | 61.4942 | 61.428 | 61.4473 | 61.471 | 61.5048 | 61.4717 | 61.5065 | 123.0468 | 61.5477 | 122.9643 | 61.4262 | 61.4939 | 123.0347 | 61.49 | 122.8266 | 61.553 | 61.5568 | 61.4705 | 61.4744
192.5938 | 123.2758 | -61.4822 | 61.6653 | 0.016548 | -0.0451 | -0.007421 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.5783 | 0.083796 | 61.4867 | -0.042259 | 0.029923 | 61.5662 | 0.021456 | 61.3489 | 61.4988 | 61.4371 | 61.4748 | 61.4847 | 61.5277 | 61.49 | 61.5248 | 123.0605 | 61.566 | 122.9689 | 61.44 | 61.5122 | 123.0484 | 61.5037 | 122.8312 | 61.5484 | 61.5568 | 61.4567 | 61.4652
193.5938 | 123.3673 | -61.4502 | 61.6104 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.047159 | 61.5783 | 0.079217 | 61.4958 | -0.042259 | 0.025345 | 61.5662 | 0.021456 | 61.3489 | 61.4713 | 61.4051 | 61.4336 | 61.4572 | 61.491 | 61.4534 | 61.4974 | 123.0285 | 61.5294 | 122.946 | 61.4079 | 61.4755 | 123.0164 | 61.4717 | 122.7991 | 61.553 | 61.5568 | 61.4705 | 61.4744
194.5938 | 123.2849 | -61.4868 | 61.6562 | 0.016548 | -0.049678 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.042581 | 61.5783 | 0.088375 | 61.4958 | -0.03768 | 0.029923 | 61.5616 | 0.021456 | 61.3535 | 61.5034 | 61.4371 | 61.4702 | 61.4938 | 61.5185 | 61.4854 | 61.5294 | 123.0651 | 61.5752 | 122.9826 | 61.4491 | 61.5167 | 123.0484 | 61.5083 | 122.8403 | 61.5484 | 61.5568 | 61.4659 | 61.4744
195.5938 | 123.2941 | -61.4868 | 61.6287 | 0.016548 | -0.049678 | -0.012 | 0.007033 | 0.049999 | 0.00775 | 0.042581 | 61.5829 | 0.088375 | 61.4867 | -0.03768 | 0.034501 | 61.5616 | 0.026035 | 61.3535 | 61.5034 | 61.4371 | 61.4748 | 61.4938 | 61.5368 | 61.4946 | 61.5294 | 123.0697 | 61.5752 | 122.9735 | 61.4491 | 61.5213 | 123.0484 | 61.5129 | 122.8403 | 61.5484 | 61.5568 | 61.4522 | 61.4606
196.5938 | 123.2803 | -61.4639 | 61.6379 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.5829 | 0.092954 | 61.505 | -0.042259 | 0.020767 | 61.5707 | 0.012299 | 61.3535 | 61.4896 | 61.4234 | 61.4474 | 61.4664 | 61.5002 | 61.4717 | 61.5065 | 123.0468 | 61.5569 | 122.9689 | 61.4217 | 61.4847 | 123.0347 | 61.4762 | 122.8174 | 61.5621 | 61.5706 | 61.4842 | 61.4927
197.5938 | 123.436 | -61.4044 | 61.6196 | 0.021127 | -0.0451 | -0.007421 | -0.002124 | 0.036265 | 0.00775 | 0.042581 | 61.5783 | 0.088375 | 61.4958 | -0.03768 | 0.029923 | 61.5616 | 0.021456 | 61.3581 | 61.4255 | 61.3593 | 61.397 | 61.4023 | 61.4407 | 61.4122 | 61.447 | 122.9827 | 61.4928 | 122.9002 | 61.3667 | 61.4343 | 122.966 | 61.4259 | 122.7625 | 61.5484 | 61.5568 | 61.4659 | 61.4744
198.5938 | 123.4085 | -61.4731 | 61.5967 | 0.016548 | -0.0451 | -0.021157 | 0.011611 | 0.045421 | -0.001406 | 0.047159 | 61.5783 | 0.088375 | 61.4912 | -0.042259 | 0.020767 | 61.5616 | 0.026035 | 61.3535 | 61.4896 | 61.428 | 61.4519 | 61.4847 | 61.5185 | 61.4717 | 61.5202 | 123.0514 | 61.5615 | 122.9643 | 61.4308 | 61.4939 | 123.0347 | 61.4991 | 122.8266 | 61.5575 | 61.5523 | 61.4705 | 61.4652
199.5938 | 123.381 | -61.4502 | 61.6058 | 0.025705 | -0.040521 | -0.021157 | 0.002454 | 0.040843 | 0.00775 | 0.033424 | 61.5783 | 0.083796 | 61.4912 | -0.046838 | 0.029923 | 61.5662 | 0.003143 | 61.3581 | 61.4759 | 61.4097 | 61.429 | 61.4526 | 61.491 | 61.4579 | 61.4836 | 123.0285 | 61.534 | 122.9414 | 61.4034 | 61.4801 | 123.0164 | 61.4533 | 122.8083 | 61.5484 | 61.5752 | 61.4613 | 61.4881
200.5938 | 123.3902 | -61.441 | 61.5967 | 0.021127 | -0.0451 | -0.021157 | 0.011611 | 0.040843 | 0.003172 | 0.047159 | 61.5783 | 0.097532 | 61.4958 | -0.042259 | 0.034501 | 61.5616 | 0.003143 | 61.3627 | 61.4622 | 61.3959 | 61.4199 | 61.4527 | 61.4819 | 61.4442 | 61.4882 | 123.0193 | 61.5386 | 122.9369 | 61.3988 | 61.4755 | 123.0026 | 61.4442 | 122.8037 | 61.5438 | 61.5752 | 61.4613 | 61.4927
201.5938 | 123.4039 | -61.4502 | 61.5921 | 0.016548 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.042581 | 61.5829 | 0.079217 | 61.4958 | -0.03768 | 0.029923 | 61.5662 | 0.007721 | 61.3581 | 61.4667 | 61.4143 | 61.4336 | 61.4526 | 61.4819 | 61.4625 | 61.4928 | 123.0331 | 61.5294 | 122.946 | 61.4125 | 61.4801 | 123.0164 | 61.4579 | 122.8083 | 61.553 | 61.5752 | 61.4659 | 61.4881
202.5938 | 123.4039 | -61.4548 | 61.6241 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.5829 | 0.088375 | 61.4821 | -0.046838 | 0.025345 | 61.5616 | -0.001436 | 61.3489 | 61.4759 | 61.4097 | 61.4382 | 61.4618 | 61.4956 | 61.4579 | 61.4928 | 123.0377 | 61.5431 | 122.9369 | 61.4079 | 61.4801 | 123.0164 | 61.4533 | 122.8037 | 61.5575 | 61.5843 | 61.4567 | 61.4835
203.5938 | 123.3444 | -61.441 | 61.6058 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.051737 | 61.5783 | 0.088375 | 61.4775 | -0.042259 | 0.025345 | 61.5662 | -0.001436 | 61.3489 | 61.4622 | 61.4051 | 61.429 | 61.4435 | 61.4819 | 61.4442 | 61.4928 | 123.0193 | 61.5294 | 122.9186 | 61.3988 | 61.4664 | 123.0072 | 61.4396 | 122.79 | 61.553 | 61.5797 | 61.4522 | 61.4789
204.5938 | 123.3536 | -61.4548 | 61.6104 | 0.01197 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.047159 | 61.5783 | 0.083796 | 61.4958 | -0.046838 | 0.029923 | 61.5662 | 0.007721 | 61.3581 | 61.4667 | 61.4143 | 61.4382 | 61.4664 | 61.491 | 61.4579 | 61.5019 | 123.0331 | 61.5386 | 122.9506 | 61.4079 | 61.4847 | 123.0209 | 61.4625 | 122.8129 | 61.5484 | 61.5706 | 61.4659 | 61.4881
205.5938 | 123.3398 | -61.4777 | 61.5967 | 0.021127 | -0.049678 | -0.016578 | 0.011611 | 0.031687 | 0.00775 | 0.042581 | 61.5829 | 0.083796 | 61.4867 | -0.03768 | 0.025345 | 61.5616 | 0.012299 | 61.3489 | 61.4988 | 61.428 | 61.4611 | 61.4893 | 61.5093 | 61.4854 | 61.5202 | 123.0605 | 61.5615 | 122.9643 | 61.44 | 61.503 | 123.0392 | 61.49 | 122.8266 | 61.5575 | 61.5706 | 61.4613 | 61.4744
206.5938 | 123.3124 | -61.4868 | 61.5967 | 0.021127 | -0.049678 | -0.007421 | 0.002454 | 0.036265 | 0.012329 | 0.038003 | 61.5829 | 0.083796 | 61.4867 | -0.042259 | 0.029923 | 61.5616 | 0.003143 | 61.3489 | 61.5079 | 61.4371 | 61.4794 | 61.4893 | 61.5231 | 61.4991 | 61.5248 | 123.0697 | 61.5706 | 122.9735 | 61.4446 | 61.5167 | 123.0484 | 61.49 | 122.8357 | 61.553 | 61.5797 | 61.4567 | 61.4835
207.5938 | 123.349 | -61.4914 | 61.5738 | 0.021127 | -0.040521 | -0.021157 | 0.01619 | 0.040843 | -0.001406 | 0.042581 | 61.5783 | 0.088375 | 61.4912 | -0.046838 | 0.020767 | 61.557 | 0.003143 | 61.3535 | 61.5125 | 61.4509 | 61.4702 | 61.5076 | 61.5322 | 61.49 | 61.534 | 123.0697 | 61.5798 | 122.9826 | 61.4446 | 61.5122 | 123.0484 | 61.4945 | 122.8449 | 61.5575 | 61.5752 | 61.4705 | 61.4881
208.5938 | 123.3765 | -61.4548 | 61.5967 | 0.01197 | -0.0451 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.051737 | 61.5829 | 0.088375 | 61.5004 | -0.042259 | 0.025345 | 61.5662 | 0.007721 | 61.3535 | 61.4667 | 61.4097 | 61.4382 | 61.4572 | 61.4956 | 61.4534 | 61.5065 | 123.0377 | 61.5431 | 122.9552 | 61.4125 | 61.4801 | 123.0209 | 61.4625 | 122.8083 | 61.5575 | 61.5752 | 61.4751 | 61.4927
209.5938 | 123.3353 | -61.4639 | 61.5601 | 0.021127 | -0.049678 | -0.021157 | -0.002124 | 0.040843 | 0.003172 | 0.038003 | 61.5783 | 0.083796 | 61.4958 | -0.03768 | 0.029923 | 61.5707 | 0.012299 | 61.3489 | 61.4851 | 61.4143 | 61.4428 | 61.4618 | 61.5048 | 61.4671 | 61.5019 | 123.0422 | 61.5477 | 122.9598 | 61.4262 | 61.4939 | 123.0347 | 61.4762 | 122.8129 | 61.5484 | 61.566 | 61.4659 | 61.4835
210.5938 | 123.3444 | -61.4685 | 61.5967 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.040843 | -0.005985 | 0.047159 | 61.5783 | 0.083796 | 61.5004 | -0.046838 | 0.025345 | 61.5662 | 0.016878 | 61.3535 | 61.4896 | 61.428 | 61.4565 | 61.4755 | 61.5093 | 61.4625 | 61.5157 | 123.0468 | 61.5523 | 122.9689 | 61.4217 | 61.4939 | 123.0347 | 61.4854 | 122.822 | 61.553 | 61.5614 | 61.4751 | 61.4835
211.5938 | 123.468 | -61.4822 | 61.5738 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.038003 | 61.5829 | 0.088375 | 61.5004 | -0.03768 | 0.025345 | 61.5707 | 0.016878 | 61.3581 | 61.5079 | 61.4371 | 61.4702 | 61.4847 | 61.5231 | 61.4854 | 61.5202 | 123.0651 | 61.5706 | 122.9826 | 61.4446 | 61.5076 | 123.053 | 61.4991 | 122.8403 | 61.5575 | 61.566 | 61.4751 | 61.4835
212.5938 | 123.3582 | -61.4639 | 61.5738 | 0.016548 | -0.040521 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.038003 | 61.5829 | 0.074638 | 61.4912 | -0.042259 | 0.029923 | 61.5707 | 0.003143 | 61.3535 | 61.4805 | 61.4234 | 61.4519 | 61.4755 | 61.5002 | 61.4625 | 61.5019 | 123.0468 | 61.5386 | 122.9552 | 61.4217 | 61.4939 | 123.0347 | 61.4671 | 122.8174 | 61.553 | 61.5797 | 61.4613 | 61.4881
213.5938 | 123.3353 | -61.4868 | 61.5784 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.5829 | 0.083796 | 61.4821 | -0.03768 | 0.025345 | 61.5707 | 0.021456 | 61.3489 | 61.5125 | 61.4463 | 61.4702 | 61.4893 | 61.5231 | 61.4946 | 61.5294 | 123.0697 | 61.5706 | 122.9689 | 61.4491 | 61.5122 | 123.0576 | 61.5083 | 122.8357 | 61.5575 | 61.5614 | 61.4567 | 61.4606
214.5938 | 123.262 | -61.5005 | 61.6287 | 0.025705 | -0.040521 | -0.021157 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.5875 | 0.092954 | 61.4958 | -0.033101 | 0.025345 | 61.5662 | 0.016878 | 61.3535 | 61.5263 | 61.46 | 61.4794 | 61.5076 | 61.5414 | 61.5083 | 61.5431 | 123.088 | 61.5935 | 122.9964 | 61.4674 | 61.5259 | 123.0667 | 61.5174 | 122.8541 | 61.5621 | 61.5706 | 61.4705 | 61.4789
215.5938 | 123.3215 | -61.4639 | 61.5921 | 0.021127 | -0.040521 | -0.021157 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.5875 | 0.083796 | 61.5004 | -0.042259 | 0.020767 | 61.5616 | 0.021456 | 61.3489 | 61.4851 | 61.4234 | 61.4428 | 61.471 | 61.5093 | 61.4671 | 61.5065 | 123.0514 | 61.5477 | 122.9643 | 61.4217 | 61.4847 | 123.0255 | 61.4854 | 122.8129 | 61.5667 | 61.566 | 61.4796 | 61.4789
216.5938 | 123.3398 | -61.4731 | 61.5921 | 0.01197 | -0.040521 | -0.012 | -0.002124 | 0.045421 | -0.001406 | 0.042581 | 61.5875 | 0.088375 | 61.505 | -0.03768 | 0.025345 | 61.5707 | 0.016878 | 61.3489 | 61.4851 | 61.4326 | 61.4611 | 61.471 | 61.5185 | 61.4717 | 61.5157 | 123.0605 | 61.5615 | 122.9781 | 61.4354 | 61.4984 | 123.0438 | 61.49 | 122.822 | 61.5621 | 61.5706 | 61.4796 | 61.4881
217.5938 | 123.381 | -61.4777 | 61.5646 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5829 | 0.088375 | 61.4958 | -0.03768 | 0.025345 | 61.5662 | 0.012299 | 61.3489 | 61.4988 | 61.4417 | 61.4611 | 61.4801 | 61.5185 | 61.4808 | 61.5202 | 123.0605 | 61.566 | 122.9735 | 61.44 | 61.503 | 123.0438 | 61.49 | 122.8266 | 61.5575 | 61.5706 | 61.4705 | 61.4835
218.5938 | 123.436 | -61.4639 | 61.5372 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.042581 | 61.5783 | 0.088375 | 61.4958 | -0.046838 | 0.029923 | 61.5707 | 0.007721 | 61.3489 | 61.4896 | 61.4188 | 61.4474 | 61.4664 | 61.5002 | 61.4579 | 61.5065 | 123.0422 | 61.5523 | 122.9598 | 61.4171 | 61.4939 | 123.0347 | 61.4716 | 122.8129 | 61.5484 | 61.5706 | 61.4659 | 61.4881
219.5938 | 123.3215 | -61.4731 | 61.6058 | 0.016548 | -0.049678 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.042581 | 61.5875 | 0.088375 | 61.4958 | -0.042259 | 0.034501 | 61.5707 | 0.021456 | 61.3535 | 61.4896 | 61.4234 | 61.4565 | 61.4755 | 61.5093 | 61.4671 | 61.5157 | 123.0605 | 61.5615 | 122.9689 | 61.4308 | 61.5076 | 123.0438 | 61.4945 | 122.8266 | 61.553 | 61.566 | 61.4613 | 61.4744
220.5938 | 123.4039 | -61.4548 | 61.5921 | 0.016548 | -0.0451 | -0.012 | 0.011611 | 0.036265 | 0.003172 | 0.047159 | 61.5829 | 0.083796 | 61.4958 | -0.03768 | 0.025345 | 61.5616 | 0.021456 | 61.3581 | 61.4713 | 61.4097 | 61.4428 | 61.4664 | 61.491 | 61.4579 | 61.5019 | 123.0377 | 61.5386 | 122.9506 | 61.4171 | 61.4801 | 123.0164 | 61.4762 | 122.8129 | 61.5575 | 61.5614 | 61.4705 | 61.4744
221.5938 | 123.3902 | -61.4685 | 61.5738 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.045421 | -0.001406 | 0.042581 | 61.5783 | 0.079217 | 61.5004 | -0.03768 | 0.025345 | 61.5662 | 0.026035 | 61.3443 | 61.4942 | 61.428 | 61.4519 | 61.4755 | 61.5139 | 61.4671 | 61.5111 | 123.0468 | 61.5477 | 122.9689 | 61.4308 | 61.4939 | 123.0347 | 61.4945 | 122.8129 | 61.553 | 61.5523 | 61.4751 | 61.4744
222.5938 | 123.3353 | -61.4685 | 61.5692 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.047159 | 61.5737 | 0.092954 | 61.4821 | -0.03768 | 0.025345 | 61.5707 | 0.026035 | 61.3535 | 61.4942 | 61.4234 | 61.4519 | 61.4755 | 61.5048 | 61.4717 | 61.5157 | 123.0422 | 61.5615 | 122.9506 | 61.4308 | 61.4939 | 123.0392 | 61.4945 | 122.822 | 61.5484 | 61.5477 | 61.4567 | 61.4561
223.5938 | 123.2849 | -61.4777 | 61.6013 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.047159 | 61.592 | 0.088375 | 61.5004 | -0.03768 | 0.025345 | 61.5616 | 0.016878 | 61.3443 | 61.5034 | 61.4371 | 61.4611 | 61.4801 | 61.5231 | 61.4854 | 61.5248 | 123.0697 | 61.566 | 122.9781 | 61.44 | 61.503 | 123.0392 | 61.4945 | 122.822 | 61.5667 | 61.5752 | 61.4751 | 61.4835
224.5938 | 123.2986 | -61.4822 | 61.6379 | 0.021127 | -0.035942 | -0.012 | 0.020768 | 0.045421 | 0.003172 | 0.047159 | 61.5875 | 0.10211 | 61.505 | -0.03768 | 0.029923 | 61.5662 | 0.016878 | 61.3581 | 61.5034 | 61.4463 | 61.4702 | 61.503 | 61.5277 | 61.4854 | 61.5294 | 123.0697 | 61.5844 | 122.9872 | 61.4446 | 61.5122 | 123.0484 | 61.4991 | 122.8403 | 61.5575 | 61.5706 | 61.4751 | 61.4881
225.5938 | 123.3261 | -61.4777 | 61.6287 | 0.021127 | -0.0451 | -0.007421 | 0.011611 | 0.040843 | 0.012329 | 0.047159 | 61.5875 | 0.097532 | 61.5004 | -0.042259 | 0.029923 | 61.5662 | 0.021456 | 61.3581 | 61.4988 | 61.4326 | 61.4702 | 61.4893 | 61.5185 | 61.49 | 61.5248 | 123.0651 | 61.5752 | 122.9781 | 61.4354 | 61.5076 | 123.0438 | 61.4991 | 122.8357 | 61.5575 | 61.566 | 61.4705 | 61.4789
226.5938 | 123.23 | -61.496 | 61.6379 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.5829 | 0.088375 | 61.5004 | -0.028522 | 0.025345 | 61.5662 | 0.021456 | 61.3489 | 61.5171 | 61.46 | 61.484 | 61.503 | 61.5368 | 61.5037 | 61.5386 | 123.0789 | 61.5843 | 122.9964 | 61.4674 | 61.5213 | 123.0621 | 61.5174 | 122.8449 | 61.5575 | 61.5614 | 61.4751 | 61.4789
227.5938 | 123.2254 | -61.4822 | 61.6516 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.5783 | 0.088375 | 61.5096 | -0.033101 | 0.020767 | 61.5616 | 0.021456 | 61.3535 | 61.5125 | 61.4417 | 61.4702 | 61.4893 | 61.5277 | 61.49 | 61.5294 | 123.0605 | 61.5706 | 122.9918 | 61.4491 | 61.503 | 123.0438 | 61.5037 | 122.8357 | 61.5575 | 61.5568 | 61.4888 | 61.4881
228.5938 | 123.3398 | -61.4914 | 61.5967 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.038003 | 61.5783 | 0.083796 | 61.4912 | -0.03768 | 0.029923 | 61.5707 | 0.016878 | 61.3443 | 61.5217 | 61.4463 | 61.4748 | 61.4938 | 61.5368 | 61.4991 | 61.5294 | 123.0697 | 61.5752 | 122.9826 | 61.4537 | 61.5213 | 123.0621 | 61.5083 | 122.8357 | 61.5484 | 61.5614 | 61.4613 | 61.4744
229.5938 | 123.2666 | -61.4777 | 61.6562 | 0.021127 | -0.049678 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.047159 | 61.592 | 0.092954 | 61.5096 | -0.03768 | 0.034501 | 61.5616 | 0.016878 | 61.3535 | 61.4988 | 61.428 | 61.4657 | 61.4847 | 61.5139 | 61.4808 | 61.5248 | 123.0697 | 61.5706 | 122.9872 | 61.44 | 61.5122 | 123.0392 | 61.4945 | 122.8312 | 61.5575 | 61.5752 | 61.4751 | 61.4927
230.5938 | 123.2529 | -61.5143 | 61.6058 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.047159 | 61.5783 | 0.088375 | 61.4912 | -0.033101 | 0.029923 | 61.5662 | 0.016878 | 61.3627 | 61.5354 | 61.4692 | 61.4977 | 61.5167 | 61.5597 | 61.522 | 61.5614 | 123.0926 | 61.6027 | 123.0055 | 61.4812 | 61.5442 | 123.0804 | 61.5312 | 122.8769 | 61.5484 | 61.5614 | 61.4613 | 61.4744
231.5938 | 123.2391 | -61.5097 | 61.6333 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.047159 | 61.592 | 0.088375 | 61.505 | -0.03768 | 0.034501 | 61.5662 | 0.007721 | 61.3581 | 61.5354 | 61.4692 | 61.4977 | 61.5122 | 61.5551 | 61.5175 | 61.5569 | 123.1017 | 61.5981 | 123.0147 | 61.472 | 61.5442 | 123.0759 | 61.5174 | 122.8678 | 61.5575 | 61.5843 | 61.4705 | 61.4973
232.5938 | 123.2529 | -61.5143 | 61.6013 | 0.030283 | -0.040521 | -0.007421 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.5829 | 0.092954 | 61.505 | -0.03768 | 0.025345 | 61.5662 | 0.007721 | 61.3535 | 61.5446 | 61.4738 | 61.5069 | 61.5213 | 61.5597 | 61.5175 | 61.5569 | 123.0972 | 61.6072 | 123.0193 | 61.4766 | 61.5396 | 123.0804 | 61.522 | 122.8678 | 61.5575 | 61.5752 | 61.4796 | 61.4973
233.5938 | 123.2346 | -61.4731 | 61.6287 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.5783 | 0.092954 | 61.5004 | -0.028522 | 0.025345 | 61.5707 | 0.012299 | 61.3581 | 61.4988 | 61.4326 | 61.4611 | 61.4801 | 61.5185 | 61.4763 | 61.5202 | 123.0514 | 61.566 | 122.9735 | 61.4446 | 61.4984 | 123.0438 | 61.4854 | 122.8312 | 61.553 | 61.566 | 61.4751 | 61.4881
234.5938 | 123.3307 | -61.4777 | 61.5829 | 0.021127 | -0.035942 | -0.021157 | 0.007033 | 0.045421 | 0.003172 | 0.038003 | 61.5875 | 0.088375 | 61.5096 | -0.042259 | 0.029923 | 61.5616 | 0.012299 | 61.3489 | 61.4988 | 61.4417 | 61.4565 | 61.4847 | 61.5231 | 61.4808 | 61.5157 | 123.0651 | 61.566 | 122.9872 | 61.4354 | 61.5076 | 123.0392 | 61.49 | 122.8266 | 61.5575 | 61.5752 | 61.4796 | 61.4973
235.5938 | 123.1384 | -61.528 | 61.5875 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.012329 | 0.047159 | 61.5783 | 0.088375 | 61.4958 | -0.033101 | 0.029923 | 61.5616 | 0.016878 | 61.3535 | 61.5491 | 61.4875 | 61.5114 | 61.5305 | 61.5689 | 61.5403 | 61.5752 | 123.1063 | 61.6164 | 123.0238 | 61.4949 | 61.5579 | 123.0896 | 61.5449 | 122.8815 | 61.5484 | 61.5614 | 61.4659 | 61.4789
236.5938 | 123.3032 | -61.496 | 61.5784 | 0.025705 | -0.049678 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.042581 | 61.5875 | 0.083796 | 61.505 | -0.042259 | 0.025345 | 61.5616 | 0.016878 | 61.3535 | 61.5217 | 61.4463 | 61.4794 | 61.4938 | 61.5368 | 61.4991 | 61.5386 | 123.0834 | 61.5798 | 123.001 | 61.4537 | 61.5213 | 123.0576 | 61.5129 | 122.8495 | 61.5621 | 61.5706 | 61.4796 | 61.4881
237.5938 | 123.2574 | -61.496 | 61.6196 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.049999 | 0.012329 | 0.042581 | 61.5829 | 0.088375 | 61.4958 | -0.042259 | 0.020767 | 61.5662 | 0.016878 | 61.3535 | 61.5217 | 61.4555 | 61.484 | 61.4984 | 61.546 | 61.5083 | 61.5386 | 123.0789 | 61.5843 | 122.9918 | 61.4537 | 61.5167 | 123.0621 | 61.5129 | 122.8495 | 61.5621 | 61.566 | 61.4751 | 61.4789
238.5938 | 123.3856 | -61.4731 | 61.5738 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.5875 | 0.088375 | 61.505 | -0.03768 | 0.025345 | 61.5662 | 0.016878 | 61.3581 | 61.4988 | 61.428 | 61.4611 | 61.4755 | 61.5185 | 61.4763 | 61.5157 | 123.0605 | 61.5615 | 122.9781 | 61.4354 | 61.4984 | 123.0392 | 61.49 | 122.8312 | 61.5621 | 61.5706 | 61.4796 | 61.4881
239.5938 | 123.3994 | -61.4594 | 61.5692 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.5783 | 0.092954 | 61.5004 | -0.046838 | 0.029923 | 61.5616 | 0.007721 | 61.3581 | 61.4805 | 61.4188 | 61.4382 | 61.4618 | 61.5048 | 61.4625 | 61.5019 | 123.0377 | 61.5523 | 122.9598 | 61.4125 | 61.4893 | 123.0209 | 61.4671 | 122.8174 | 61.5484 | 61.5706 | 61.4705 | 61.4927
240.5938 | 123.2117 | -61.5005 | 61.6379 | 0.021127 | -0.0451 | -0.012 | 0.011611 | 0.031687 | 0.003172 | 0.047159 | 61.5829 | 0.088375 | 61.4912 | -0.03768 | 0.025345 | 61.5662 | 0.007721 | 61.3581 | 61.5217 | 61.4554 | 61.4885 | 61.5122 | 61.5322 | 61.5037 | 61.5477 | 123.0834 | 61.5889 | 122.9918 | 61.4629 | 61.5259 | 123.0667 | 61.5083 | 122.8586 | 61.5575 | 61.5752 | 61.4659 | 61.4835
241.5938 | 123.2483 | -61.4731 | 61.6287 | 0.021127 | -0.049678 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.5875 | 0.088375 | 61.5004 | -0.046838 | 0.025345 | 61.5662 | 0.003143 | 61.3535 | 61.4942 | 61.4234 | 61.4565 | 61.4755 | 61.5139 | 61.4763 | 61.5157 | 123.0605 | 61.5615 | 122.9735 | 61.4262 | 61.4984 | 123.0392 | 61.4762 | 122.8266 | 61.5621 | 61.5843 | 61.4751 | 61.4973
242.5938 | 123.3994 | -61.4731 | 61.5829 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.042581 | 61.5875 | 0.088375 | 61.505 | -0.03768 | 0.029923 | 61.5662 | 0.012299 | 61.3489 | 61.4942 | 61.4326 | 61.4611 | 61.4755 | 61.5139 | 61.4717 | 61.5157 | 123.0605 | 61.5615 | 122.9781 | 61.4354 | 61.503 | 123.0392 | 61.4854 | 122.822 | 61.5575 | 61.5752 | 61.4751 | 61.4927
243.5938 | 123.2437 | -61.4868 | 61.6241 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.051737 | 61.5875 | 0.092954 | 61.5004 | -0.042259 | 0.020767 | 61.5662 | 0.003143 | 61.3535 | 61.5079 | 61.4417 | 61.4702 | 61.4893 | 61.5322 | 61.49 | 61.5386 | 123.0743 | 61.5798 | 122.9872 | 61.4446 | 61.5076 | 123.053 | 61.49 | 122.8403 | 61.5667 | 61.5843 | 61.4796 | 61.4973
244.5938 | 123.3627 | -61.4594 | 61.5738 | 0.021127 | -0.0451 | -0.021157 | 0.002454 | 0.045421 | -0.001406 | 0.038003 | 61.5875 | 0.092954 | 61.4821 | -0.03768 | 0.034501 | 61.5662 | 0.016878 | 61.3535 | 61.4805 | 61.4143 | 61.4382 | 61.4618 | 61.5048 | 61.4579 | 61.4974 | 123.0468 | 61.5523 | 122.9414 | 61.4217 | 61.4939 | 123.0255 | 61.4762 | 122.8129 | 61.553 | 61.5706 | 61.4476 | 61.4652
245.5938 | 123.2391 | -61.5051 | 61.6333 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.047159 | 61.5875 | 0.088375 | 61.4912 | -0.042259 | 0.025345 | 61.5662 | 0.007721 | 61.3535 | 61.5308 | 61.4646 | 61.4931 | 61.5076 | 61.5414 | 61.5129 | 61.5523 | 123.0926 | 61.5935 | 122.9964 | 61.4629 | 61.5305 | 123.0713 | 61.5128 | 122.8586 | 61.5621 | 61.5797 | 61.4659 | 61.4835
246.5938 | 123.3215 | -61.4868 | 61.6058 | 0.016548 | -0.049678 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.047159 | 61.592 | 0.088375 | 61.5004 | -0.042259 | 0.034501 | 61.5616 | 0.007721 | 61.3581 | 61.5034 | 61.4371 | 61.4702 | 61.4938 | 61.5231 | 61.49 | 61.534 | 123.0789 | 61.5752 | 122.9872 | 61.4446 | 61.5213 | 123.0484 | 61.4945 | 122.8449 | 61.5575 | 61.5843 | 61.4659 | 61.4927
247.5938 | 123.2254 | -61.5005 | 61.6241 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.036265 | -0.001406 | 0.042581 | 61.5875 | 0.088375 | 61.4821 | -0.042259 | 0.029923 | 61.5662 | 0.012299 | 61.3581 | 61.5263 | 61.4554 | 61.4885 | 61.4984 | 61.5368 | 61.4991 | 61.5431 | 123.088 | 61.5889 | 122.9826 | 61.4583 | 61.5305 | 123.0667 | 61.5128 | 122.8586 | 61.5575 | 61.5752 | 61.4522 | 61.4698
248.5938 | 123.3215 | -61.5097 | 61.6058 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.051737 | 61.5875 | 0.088375 | 61.4958 | -0.042259 | 0.029923 | 61.5662 | 0.007721 | 61.3535 | 61.5354 | 61.4738 | 61.4931 | 61.5122 | 61.5551 | 61.5129 | 61.5614 | 123.0972 | 61.5981 | 123.0055 | 61.4674 | 61.5396 | 123.0759 | 61.5174 | 122.8632 | 61.5575 | 61.5797 | 61.4659 | 61.4881
249.5938 | 123.3627 | -61.4594 | 61.5738 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.042581 | 61.5875 | 0.088375 | 61.5004 | -0.046838 | 0.025345 | 61.5753 | 0.026035 | 61.3535 | 61.4851 | 61.4143 | 61.4428 | 61.4572 | 61.5002 | 61.4625 | 61.5019 | 123.0468 | 61.5477 | 122.9598 | 61.4125 | 61.4847 | 123.0347 | 61.4854 | 122.8129 | 61.5621 | 61.5614 | 61.4751 | 61.4744
250.5938 | 123.3582 | -61.4822 | 61.5967 | 0.021127 | -0.049678 | -0.021157 | 0.011611 | 0.045421 | 0.003172 | 0.033424 | 61.5966 | 0.083796 | 61.505 | -0.046838 | 0.025345 | 61.5753 | 0.026035 | 61.3535 | 61.5034 | 61.4326 | 61.4611 | 61.4939 | 61.5277 | 61.4854 | 61.5157 | 123.0789 | 61.566 | 122.9872 | 61.4354 | 61.5076 | 123.0576 | 61.5083 | 122.8357 | 61.5713 | 61.5706 | 61.4796 | 61.4789
251.5938 | 123.1247 | -61.5601 | 61.5967 | 0.016548 | -0.040521 | -0.007421 | 0.01619 | 0.036265 | 0.003172 | 0.042581 | 61.592 | 0.083796 | 61.4912 | -0.033101 | 0.025345 | 61.5616 | 0.012299 | 61.3581 | 61.5766 | 61.5195 | 61.5526 | 61.5762 | 61.5963 | 61.5632 | 61.6026 | 123.1521 | 61.6439 | 123.0513 | 61.527 | 61.5854 | 123.1216 | 61.5724 | 122.9181 | 61.5667 | 61.5797 | 61.4659 | 61.4789
252.5938 | 123.2986 | -61.5005 | 61.6058 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.5875 | 0.088375 | 61.4912 | -0.033101 | 0.020767 | 61.5662 | 0.016878 | 61.3535 | 61.5263 | 61.4554 | 61.484 | 61.503 | 61.5414 | 61.5083 | 61.5431 | 123.088 | 61.5889 | 122.9918 | 61.4674 | 61.5213 | 123.0667 | 61.5174 | 122.8541 | 61.5667 | 61.5706 | 61.4705 | 61.4744
253.5938 | 123.2162 | -61.5005 | 61.6241 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.5966 | 0.083796 | 61.4867 | -0.03768 | 0.020767 | 61.5662 | 0.007721 | 61.3535 | 61.5217 | 61.46 | 61.484 | 61.5076 | 61.5414 | 61.5083 | 61.5477 | 123.0972 | 61.5843 | 122.9872 | 61.4629 | 61.5213 | 123.0667 | 61.5083 | 122.8541 | 61.5759 | 61.5889 | 61.4659 | 61.4789
254.5938 | 123.4085 | -61.4731 | 61.5738 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.045421 | 0.016907 | 0.047159 | 61.5875 | 0.088375 | 61.4958 | -0.033101 | 0.020767 | 61.5662 | 0.021456 | 61.3581 | 61.5034 | 61.4326 | 61.4519 | 61.4801 | 61.5185 | 61.49 | 61.5202 | 123.0605 | 61.5615 | 122.9689 | 61.44 | 61.4939 | 123.0392 | 61.4945 | 122.8312 | 61.5667 | 61.566 | 61.4751 | 61.4744
255.5938 | 123.349 | -61.4822 | 61.6104 | 0.025705 | -0.049678 | -0.021157 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.5829 | 0.092954 | 61.505 | -0.042259 | 0.029923 | 61.5662 | -0.001436 | 61.3581 | 61.5079 | 61.4326 | 61.4611 | 61.4893 | 61.5231 | 61.4854 | 61.5248 | 123.0651 | 61.5752 | 122.9872 | 61.44 | 61.5122 | 123.0484 | 61.4808 | 122.8403 | 61.553 | 61.5843 | 61.4751 | 61.5064
256.5938 | 123.3536 | -61.4822 | 61.6058 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.038003 | 61.5875 | 0.088375 | 61.4958 | -0.033101 | 0.025345 | 61.5707 | 0.007721 | 61.3535 | 61.4988 | 61.4463 | 61.4702 | 61.4893 | 61.5185 | 61.49 | 61.5202 | 123.0697 | 61.5706 | 122.9781 | 61.4491 | 61.5076 | 123.053 | 61.49 | 122.8357 | 61.5621 | 61.5797 | 61.4705 | 61.4881
257.5938 | 123.2666 | -61.5005 | 61.6104 | 0.021127 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | 0.00775 | 0.033424 | 61.5875 | 0.083796 | 61.4958 | -0.03768 | 0.029923 | 61.5707 | 0.016878 | 61.3489 | 61.5217 | 61.46 | 61.484 | 61.5122 | 61.5368 | 61.5083 | 61.534 | 123.088 | 61.5843 | 122.9964 | 61.4629 | 61.5305 | 123.0713 | 61.5174 | 122.8495 | 61.5575 | 61.5706 | 61.4659 | 61.4789
258.5938 | 123.23 | -61.5005 | 61.6425 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.5875 | 0.088375 | 61.4958 | -0.042259 | 0.025345 | 61.5707 | 0.003143 | 61.3535 | 61.5217 | 61.46 | 61.4885 | 61.5122 | 61.546 | 61.4991 | 61.5431 | 123.088 | 61.5889 | 122.9964 | 61.4583 | 61.5259 | 123.0713 | 61.5037 | 122.8541 | 61.5621 | 61.5843 | 61.4705 | 61.4927
259.5938 | 123.4085 | -61.4456 | 61.5829 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.047159 | 61.5829 | 0.097532 | 61.5004 | -0.046838 | 0.020767 | 61.5707 | -0.006014 | 61.3535 | 61.4667 | 61.4051 | 61.4336 | 61.4527 | 61.4865 | 61.4488 | 61.4928 | 123.0285 | 61.5432 | 122.946 | 61.3988 | 61.4664 | 123.0164 | 61.4396 | 122.7991 | 61.5621 | 61.5889 | 61.4796 | 61.5064
260.5938 | 123.2986 | -61.4914 | 61.6013 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.5875 | 0.088375 | 61.505 | -0.03768 | 0.016188 | 61.5662 | 0.007721 | 61.3581 | 61.5079 | 61.4509 | 61.4794 | 61.4984 | 61.5368 | 61.4991 | 61.534 | 123.0789 | 61.5798 | 122.9964 | 61.4537 | 61.5076 | 123.0576 | 61.4991 | 122.8495 | 61.5713 | 61.5797 | 61.4888 | 61.4973
261.5938 | 123.3719 | -61.4777 | 61.6104 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.042581 | 61.5966 | 0.092954 | 61.4912 | -0.03768 | 0.029923 | 61.5662 | 0.003143 | 61.3535 | 61.4988 | 61.4326 | 61.4657 | 61.4801 | 61.5185 | 61.4763 | 61.5202 | 123.0743 | 61.5706 | 122.9689 | 61.44 | 61.5076 | 123.0438 | 61.4808 | 122.8312 | 61.5667 | 61.5935 | 61.4613 | 61.4881
262.5938 | 123.262 | -61.5005 | 61.6333 | 0.021127 | -0.035942 | -0.012 | 0.01619 | 0.036265 | 0.003172 | 0.042581 | 61.5875 | 0.088375 | 61.4867 | -0.051417 | 0.025345 | 61.5662 | 0.007721 | 61.3535 | 61.5217 | 61.4646 | 61.4885 | 61.5167 | 61.5368 | 61.5037 | 61.5431 | 123.088 | 61.5889 | 122.9872 | 61.4491 | 61.5259 | 123.0667 | 61.5083 | 122.8541 | 61.5621 | 61.5797 | 61.4613 | 61.4789
263.5938 | 123.2849 | -61.5005 | 61.6425 | 0.030283 | -0.054257 | -0.012 | 0.002454 | 0.040843 | 0.012329 | 0.051737 | 61.5966 | 0.097532 | 61.505 | -0.042259 | 0.029923 | 61.5616 | 0.003143 | 61.3489 | 61.5308 | 61.4463 | 61.4885 | 61.503 | 61.5414 | 61.5129 | 61.5523 | 123.0972 | 61.5981 | 123.0055 | 61.4583 | 61.5305 | 123.0621 | 61.5037 | 122.8495 | 61.5667 | 61.5935 | 61.4751 | 61.5018
264.5938 | 123.3719 | -61.4777 | 61.5692 | 0.016548 | -0.049678 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.033424 | 61.5829 | 0.088375 | 61.4958 | -0.033101 | 0.020767 | 61.5662 | 0.003143 | 61.3581 | 61.4942 | 61.428 | 61.4702 | 61.4893 | 61.5185 | 61.4808 | 61.5111 | 123.0605 | 61.566 | 122.9735 | 61.4446 | 61.4984 | 123.0438 | 61.4808 | 122.8357 | 61.5621 | 61.5797 | 61.4751 | 61.4927
265.5938 | 123.2254 | -61.4731 | 61.6608 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.049999 | 0.003172 | 0.042581 | 61.5875 | 0.088375 | 61.5004 | -0.03768 | 0.020767 | 61.5707 | 0.003143 | 61.3581 | 61.4988 | 61.428 | 61.4565 | 61.4801 | 61.5231 | 61.4763 | 61.5157 | 123.0605 | 61.5615 | 122.9735 | 61.4354 | 61.4939 | 123.0438 | 61.4762 | 122.8312 | 61.5667 | 61.5843 | 61.4796 | 61.4973
266.5938 | 123.2162 | -61.5005 | 61.5967 | 0.021127 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.592 | 0.088375 | 61.4867 | -0.03768 | 0.029923 | 61.5616 | 0.007721 | 61.3627 | 61.5217 | 61.4554 | 61.4931 | 61.5076 | 61.546 | 61.5037 | 61.5431 | 123.0926 | 61.5889 | 122.9872 | 61.4629 | 61.5305 | 123.0621 | 61.5083 | 122.8632 | 61.5621 | 61.5843 | 61.4567 | 61.4789
267.5938 | 123.3444 | -61.4639 | 61.6058 | 0.021127 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.6012 | 0.10669 | 61.4958 | -0.03768 | 0.025345 | 61.5616 | 0.003143 | 61.3627 | 61.4851 | 61.4234 | 61.4474 | 61.4755 | 61.5048 | 61.4717 | 61.5111 | 123.0651 | 61.5706 | 122.9598 | 61.4262 | 61.4893 | 123.0255 | 61.4671 | 122.8266 | 61.5759 | 61.5981 | 61.4705 | 61.4927
268.5938 | 123.2666 | -61.5051 | 61.6013 | 0.025705 | -0.040521 | -0.012 | 0.011611 | 0.045421 | -0.001406 | 0.047159 | 61.5875 | 0.092954 | 61.5096 | -0.033101 | 0.025345 | 61.5662 | 0.003143 | 61.3581 | 61.5308 | 61.4646 | 61.4931 | 61.5167 | 61.5505 | 61.5037 | 61.5523 | 123.0926 | 61.5981 | 123.0147 | 61.472 | 61.5305 | 123.0713 | 61.5083 | 122.8632 | 61.5621 | 61.5843 | 61.4842 | 61.5064
269.5938 | 123.317 | -61.5005 | 61.615 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.054577 | 0.003172 | 0.047159 | 61.5875 | 0.092954 | 61.5004 | -0.042259 | 0.025345 | 61.5707 | 0.012299 | 61.3535 | 61.5171 | 61.46 | 61.484 | 61.5076 | 61.5551 | 61.5037 | 61.5477 | 123.088 | 61.5935 | 123.0009 | 61.4583 | 61.5259 | 123.0713 | 61.5128 | 122.8541 | 61.5621 | 61.5752 | 61.4751 | 61.4881
270.5938 | 123.0789 | -61.5097 | 61.5601 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.592 | 0.097532 | 61.4912 | -0.03768 | 0.025345 | 61.5616 | 0.016878 | 61.3535 | 61.5354 | 61.4692 | 61.4931 | 61.5213 | 61.5551 | 61.5129 | 61.5523 | 123.1017 | 61.6072 | 123.0009 | 61.472 | 61.535 | 123.0713 | 61.5266 | 122.8632 | 61.5667 | 61.5752 | 61.4659 | 61.4744
271.5938 | 123.2849 | -61.496 | 61.6241 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.045421 | 0.012329 | 0.051737 | 61.592 | 0.097532 | 61.4958 | -0.03768 | 0.025345 | 61.5753 | 0.016878 | 61.3581 | 61.5217 | 61.4509 | 61.4748 | 61.4984 | 61.5414 | 61.5083 | 61.5477 | 123.088 | 61.5935 | 122.9918 | 61.4583 | 61.5213 | 123.0713 | 61.5129 | 122.8541 | 61.5667 | 61.5752 | 61.4705 | 61.4789
272.5938 | 123.2162 | -61.496 | 61.6196 | 0.025705 | -0.049678 | -0.012 | 0.007033 | 0.045421 | 0.012329 | 0.047159 | 61.5875 | 0.088375 | 61.5004 | -0.03768 | 0.025345 | 61.5707 | 0.012299 | 61.3443 | 61.5217 | 61.4463 | 61.484 | 61.503 | 61.5414 | 61.5083 | 61.5431 | 123.0834 | 61.5843 | 122.9964 | 61.4583 | 61.5213 | 123.0667 | 61.5083 | 122.8403 | 61.5621 | 61.5752 | 61.4751 | 61.4881
273.5938 | 123.2391 | -61.5005 | 61.6196 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.5966 | 0.088375 | 61.505 | -0.03768 | 0.025345 | 61.5753 | 0.012299 | 61.3489 | 61.5171 | 61.46 | 61.484 | 61.503 | 61.546 | 61.5083 | 61.5431 | 123.0972 | 61.5889 | 123.0055 | 61.4629 | 61.5259 | 123.0759 | 61.5128 | 122.8495 | 61.5713 | 61.5843 | 61.4796 | 61.4927
274.5938 | 123.2849 | -61.4822 | 61.6745 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.5966 | 0.097532 | 61.5187 | -0.033101 | 0.029923 | 61.5707 | 0.003143 | 61.3581 | 61.5079 | 61.4417 | 61.4702 | 61.4893 | 61.5231 | 61.49 | 61.5248 | 123.0789 | 61.5798 | 123.001 | 61.4491 | 61.5122 | 123.053 | 61.4854 | 122.8403 | 61.5667 | 61.5935 | 61.4888 | 61.5156
275.5938 | 123.2712 | -61.4777 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.592 | 0.092954 | 61.4958 | -0.042259 | 0.034501 | 61.5662 | -0.001436 | 61.3627 | 61.5034 | 61.4371 | 61.4611 | 61.4801 | 61.5185 | 61.4808 | 61.5248 | 123.0697 | 61.5706 | 122.9735 | 61.4354 | 61.5122 | 123.0438 | 61.4762 | 122.8403 | 61.5575 | 61.5935 | 61.4613 | 61.4973
276.5938 | 123.2574 | -61.4822 | 61.6425 | 0.021127 | -0.040521 | -0.002842 | 0.011611 | 0.045421 | 0.00775 | 0.047159 | 61.592 | 0.097532 | 61.4958 | -0.03768 | 0.029923 | 61.5662 | 0.003143 | 61.3627 | 61.5034 | 61.4417 | 61.4794 | 61.4939 | 61.5277 | 61.49 | 61.5294 | 123.0743 | 61.5798 | 122.9781 | 61.4446 | 61.5122 | 123.0484 | 61.4854 | 122.8449 | 61.5621 | 61.5889 | 61.4659 | 61.4927
277.5938 | 123.2895 | -61.4822 | 61.6425 | 0.016548 | -0.035942 | -0.016578 | 0.011611 | 0.040843 | 0.012329 | 0.042581 | 61.5966 | 0.092954 | 61.4958 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3535 | 61.4988 | 61.4463 | 61.4657 | 61.4939 | 61.5231 | 61.4946 | 61.5248 | 123.0789 | 61.5752 | 122.9781 | 61.4446 | 61.5122 | 123.053 | 61.4854 | 122.8357 | 61.5667 | 61.5935 | 61.4659 | 61.4927
278.5938 | 123.3032 | -61.4822 | 61.6379 | 0.025705 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.012329 | 0.047159 | 61.5875 | 0.10211 | 61.5096 | -0.03768 | 0.034501 | 61.5662 | 0.007721 | 61.3535 | 61.5079 | 61.4371 | 61.4748 | 61.4893 | 61.5277 | 61.4946 | 61.5294 | 123.0697 | 61.5844 | 122.9918 | 61.4446 | 61.5167 | 123.0484 | 61.49 | 122.8357 | 61.553 | 61.5797 | 61.4751 | 61.5018
279.5938 | 123.3307 | -61.4868 | 61.647 | 0.025705 | -0.0451 | -0.012 | 0.011611 | 0.049999 | 0.00775 | 0.042581 | 61.592 | 0.092954 | 61.505 | -0.042259 | 0.025345 | 61.5662 | 0.003143 | 61.3581 | 61.5125 | 61.4417 | 61.4748 | 61.4984 | 61.5368 | 61.4946 | 61.5294 | 123.0789 | 61.5798 | 122.9918 | 61.4446 | 61.5122 | 123.053 | 61.49 | 122.8449 | 61.5667 | 61.5889 | 61.4796 | 61.5018
280.5938 | 123.3124 | -61.4685 | 61.6058 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.045421 | 0.012329 | 0.042581 | 61.5966 | 0.088375 | 61.4958 | -0.042259 | 0.034501 | 61.5707 | -0.001436 | 61.3581 | 61.4988 | 61.428 | 61.4519 | 61.471 | 61.5139 | 61.4808 | 61.5111 | 123.0651 | 61.5569 | 122.9643 | 61.4262 | 61.503 | 123.0392 | 61.4671 | 122.8266 | 61.5621 | 61.5981 | 61.4613 | 61.4973
281.5938 | 123.2986 | -61.4594 | 61.6287 | 0.025705 | -0.040521 | -0.007421 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.5875 | 0.092954 | 61.5004 | -0.03768 | 0.029923 | 61.5799 | -0.001436 | 61.3581 | 61.4851 | 61.4188 | 61.4519 | 61.4664 | 61.5048 | 61.4671 | 61.5065 | 123.0468 | 61.5523 | 122.9598 | 61.4217 | 61.4893 | 123.0392 | 61.4579 | 122.8174 | 61.5575 | 61.5889 | 61.4705 | 61.5018
282.5938 | 123.3215 | -61.4731 | 61.6608 | 0.025705 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.592 | 0.092954 | 61.5096 | -0.03768 | 0.029923 | 61.5753 | 0.007721 | 61.3627 | 61.4988 | 61.428 | 61.4657 | 61.4801 | 61.5185 | 61.4808 | 61.5157 | 123.0651 | 61.566 | 122.9826 | 61.4354 | 61.503 | 123.0484 | 61.4808 | 122.8357 | 61.5621 | 61.5843 | 61.4796 | 61.5018
283.5938 | 123.2666 | -61.5097 | 61.6608 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.5966 | 0.092954 | 61.5004 | -0.033101 | 0.029923 | 61.5753 | 0.003143 | 61.3535 | 61.54 | 61.4692 | 61.4977 | 61.5167 | 61.5505 | 61.5175 | 61.5523 | 123.1063 | 61.6027 | 123.0101 | 61.4766 | 61.5396 | 123.085 | 61.5128 | 122.8632 | 61.5667 | 61.5935 | 61.4705 | 61.4973
284.5938 | 123.2986 | -61.4914 | 61.6104 | 0.021127 | -0.040521 | -0.007421 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.5966 | 0.083796 | 61.5004 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3489 | 61.5125 | 61.4509 | 61.484 | 61.4984 | 61.5322 | 61.4946 | 61.534 | 123.088 | 61.5752 | 122.9918 | 61.4491 | 61.5167 | 123.0667 | 61.4945 | 122.8403 | 61.5713 | 61.5935 | 61.4751 | 61.4973
285.5938 | 123.2895 | -61.4731 | 61.6241 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.045421 | 0.003172 | 0.047159 | 61.5966 | 0.10211 | 61.5096 | -0.03768 | 0.029923 | 61.5753 | 0.012299 | 61.3535 | 61.4942 | 61.4326 | 61.4519 | 61.4755 | 61.5185 | 61.4763 | 61.5202 | 123.0697 | 61.5752 | 122.9826 | 61.4354 | 61.503 | 123.0484 | 61.4854 | 122.8266 | 61.5667 | 61.5843 | 61.4796 | 61.4973
286.5938 | 123.2666 | -61.496 | 61.6241 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.5875 | 0.092954 | 61.5004 | -0.03768 | 0.029923 | 61.5662 | 0.003143 | 61.3581 | 61.5171 | 61.4555 | 61.484 | 61.503 | 61.5414 | 61.5037 | 61.5386 | 123.0834 | 61.5889 | 122.9964 | 61.4583 | 61.5259 | 123.0621 | 61.4991 | 122.8541 | 61.5575 | 61.5843 | 61.4705 | 61.4973
287.5938 | 123.3261 | -61.4777 | 61.6333 | 0.016548 | -0.049678 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.5966 | 0.088375 | 61.5096 | -0.03768 | 0.025345 | 61.5662 | 0.007721 | 61.3627 | 61.4942 | 61.428 | 61.4657 | 61.4801 | 61.5185 | 61.4808 | 61.5248 | 123.0743 | 61.566 | 122.9872 | 61.44 | 61.503 | 123.0438 | 61.4854 | 122.8403 | 61.5713 | 61.5889 | 61.4842 | 61.5018
288.5938 | 123.2346 | -61.4914 | 61.6379 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.040843 | 0.012329 | 0.051737 | 61.5966 | 0.092954 | 61.505 | -0.03768 | 0.025345 | 61.5707 | 0.003143 | 61.3627 | 61.5125 | 61.4555 | 61.4794 | 61.4938 | 61.5322 | 61.5037 | 61.5431 | 123.088 | 61.5843 | 122.9964 | 61.4537 | 61.5167 | 123.0621 | 61.4945 | 122.8541 | 61.5713 | 61.5935 | 61.4796 | 61.5018
289.5938 | 123.2391 | -61.5051 | 61.6241 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.045421 | 0.00775 | 0.047159 | 61.5875 | 0.088375 | 61.5096 | -0.03768 | 0.020767 | 61.5707 | 0.003143 | 61.3489 | 61.5354 | 61.4692 | 61.4931 | 61.503 | 61.5505 | 61.5129 | 61.5523 | 123.0926 | 61.5935 | 123.0147 | 61.4674 | 61.5259 | 123.0759 | 61.5083 | 122.8541 | 61.5667 | 61.5843 | 61.4888 | 61.5064
290.5938 | 123.2941 | -61.4594 | 61.6516 | 0.016548 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.592 | 0.092954 | 61.4958 | -0.03768 | 0.029923 | 61.5707 | 0.016878 | 61.3581 | 61.4759 | 61.4143 | 61.4428 | 61.4664 | 61.5048 | 61.4671 | 61.5065 | 123.0514 | 61.5523 | 122.9552 | 61.4217 | 61.4893 | 123.0301 | 61.4762 | 122.8174 | 61.5621 | 61.5752 | 61.4659 | 61.4789
291.5938 | 123.2986 | -61.4731 | 61.615 | 0.030283 | -0.049678 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.592 | 0.10669 | 61.5096 | -0.042259 | 0.029923 | 61.5707 | 0.003143 | 61.3581 | 61.5034 | 61.4234 | 61.4565 | 61.4755 | 61.5139 | 61.4763 | 61.5202 | 123.0651 | 61.5798 | 122.9826 | 61.4308 | 61.503 | 123.0438 | 61.4762 | 122.8312 | 61.5621 | 61.5889 | 61.4796 | 61.5064
292.5938 | 123.2712 | -61.4639 | 61.647 | 0.030283 | -0.040521 | -0.016578 | 0.011611 | 0.049999 | 0.00775 | 0.042581 | 61.5966 | 0.097532 | 61.505 | -0.03768 | 0.029923 | 61.5662 | -0.001436 | 61.3581 | 61.4942 | 61.4234 | 61.4474 | 61.4755 | 61.5139 | 61.4717 | 61.5065 | 123.0605 | 61.5615 | 122.9689 | 61.4262 | 61.4939 | 123.0301 | 61.4625 | 122.822 | 61.5667 | 61.5981 | 61.4751 | 61.5064
293.5938 | 123.3078 | -61.4731 | 61.6425 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.047159 | 61.5875 | 0.10211 | 61.5004 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3535 | 61.4942 | 61.4326 | 61.4519 | 61.4755 | 61.5093 | 61.4763 | 61.5202 | 123.0605 | 61.5752 | 122.9735 | 61.4354 | 61.503 | 123.0438 | 61.4762 | 122.8266 | 61.5575 | 61.5843 | 61.4705 | 61.4973
294.5938 | 123.2986 | -61.496 | 61.6791 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.047159 | 61.592 | 0.083796 | 61.505 | -0.042259 | 0.039079 | 61.5707 | 0.012299 | 61.3581 | 61.5171 | 61.4555 | 61.484 | 61.4984 | 61.5414 | 61.5037 | 61.5431 | 123.088 | 61.5798 | 123.001 | 61.4537 | 61.5351 | 123.0667 | 61.5083 | 122.8541 | 61.553 | 61.5797 | 61.4659 | 61.4927
295.5938 | 123.2849 | -61.4868 | 61.647 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.5966 | 0.088375 | 61.5096 | -0.033101 | 0.034501 | 61.5707 | 0.003143 | 61.3581 | 61.5034 | 61.4417 | 61.4748 | 61.4893 | 61.5277 | 61.49 | 61.534 | 123.0834 | 61.5752 | 122.9964 | 61.4537 | 61.5213 | 123.0576 | 61.49 | 122.8449 | 61.5621 | 61.5935 | 61.4751 | 61.5064
296.5938 | 123.2803 | -61.4731 | 61.6791 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.047159 | 61.592 | 0.088375 | 61.5096 | -0.042259 | 0.025345 | 61.5662 | 0.003143 | 61.3627 | 61.4942 | 61.4326 | 61.4611 | 61.4847 | 61.5185 | 61.4763 | 61.5202 | 123.0651 | 61.5615 | 122.9826 | 61.4308 | 61.4984 | 123.0392 | 61.4762 | 122.8357 | 61.5667 | 61.5889 | 61.4842 | 61.5064
297.5938 | 123.2666 | -61.5051 | 61.647 | 0.016548 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.592 | 0.092954 | 61.5096 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3627 | 61.5217 | 61.46 | 61.4885 | 61.5122 | 61.546 | 61.5037 | 61.5523 | 123.0972 | 61.5981 | 123.0147 | 61.4674 | 61.535 | 123.0759 | 61.5083 | 122.8678 | 61.5621 | 61.5889 | 61.4796 | 61.5064
298.5938 | 123.3124 | -61.4731 | 61.647 | 0.025705 | -0.0451 | -0.016578 | 0.01619 | 0.036265 | 0.003172 | 0.047159 | 61.5966 | 0.10211 | 61.5004 | -0.03768 | 0.039079 | 61.5753 | 0.003143 | 61.3672 | 61.4988 | 61.428 | 61.4565 | 61.4893 | 61.5093 | 61.4763 | 61.5202 | 123.0697 | 61.5752 | 122.9735 | 61.4354 | 61.5122 | 123.0484 | 61.4762 | 122.8403 | 61.5575 | 61.5935 | 61.4613 | 61.4973
299.5938 | 123.3078 | -61.4731 | 61.6516 | 0.021127 | -0.040521 | -0.007421 | 0.011611 | 0.045421 | 0.003172 | 0.038003 | 61.5966 | 0.088375 | 61.4958 | -0.046838 | 0.029923 | 61.5753 | -0.001436 | 61.3627 | 61.4942 | 61.4326 | 61.4657 | 61.4847 | 61.5185 | 61.4763 | 61.5111 | 123.0697 | 61.5615 | 122.9689 | 61.4262 | 61.503 | 123.0484 | 61.4716 | 122.8357 | 61.5667 | 61.5981 | 61.4659 | 61.4973
300.5938 | 123.2849 | -61.4822 | 61.6837 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.040843 | 0.012329 | 0.047159 | 61.5875 | 0.097532 | 61.5004 | -0.03768 | 0.039079 | 61.5753 | 0.007721 | 61.3672 | 61.5079 | 61.4417 | 61.4748 | 61.4847 | 61.5231 | 61.4946 | 61.5294 | 123.0697 | 61.5798 | 122.9826 | 61.4446 | 61.5213 | 123.0576 | 61.49 | 122.8495 | 61.5484 | 61.5797 | 61.4613 | 61.4927
301.5938 | 123.2529 | -61.496 | 61.6745 | 0.016548 | -0.040521 | -0.007421 | 0.007033 | 0.040843 | 0.00775 | 0.038003 | 61.592 | 0.092954 | 61.5004 | -0.03768 | 0.029923 | 61.5707 | 0.007721 | 61.3581 | 61.5125 | 61.4555 | 61.4886 | 61.503 | 61.5368 | 61.5037 | 61.534 | 123.088 | 61.5889 | 122.9964 | 61.4583 | 61.5259 | 123.0667 | 61.5037 | 122.8541 | 61.5621 | 61.5843 | 61.4705 | 61.4927
302.5938 | 123.2574 | -61.4639 | 61.6562 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.5966 | 0.092954 | 61.505 | -0.033101 | 0.029923 | 61.5707 | 0.012299 | 61.3672 | 61.4851 | 61.4234 | 61.4519 | 61.471 | 61.5048 | 61.4625 | 61.5111 | 123.0605 | 61.5569 | 122.9689 | 61.4308 | 61.4939 | 123.0347 | 61.4762 | 122.8312 | 61.5667 | 61.5843 | 61.4751 | 61.4927
303.5938 | 123.2483 | -61.496 | 61.6745 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.045421 | 0.00775 | 0.042581 | 61.592 | 0.092954 | 61.4958 | -0.03768 | 0.039079 | 61.5753 | 0.003143 | 61.3672 | 61.5217 | 61.4509 | 61.484 | 61.4938 | 61.5414 | 61.5037 | 61.5386 | 123.088 | 61.5889 | 122.9918 | 61.4583 | 61.5351 | 123.0713 | 61.4991 | 122.8632 | 61.553 | 61.5889 | 61.4567 | 61.4927
304.5938 | 123.2483 | -61.496 | 61.6837 | 0.025705 | -0.0451 | -0.021157 | 0.01619 | 0.040843 | -0.005985 | 0.042581 | 61.592 | 0.092954 | 61.505 | -0.03768 | 0.025345 | 61.5753 | 0.016878 | 61.3627 | 61.5217 | 61.4509 | 61.4748 | 61.5122 | 61.5368 | 61.49 | 61.5386 | 123.088 | 61.5889 | 123.001 | 61.4583 | 61.5213 | 123.0713 | 61.5129 | 122.8586 | 61.5667 | 61.5752 | 61.4796 | 61.4881
305.5938 | 123.2254 | -61.5143 | 61.6379 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.054577 | 0.003172 | 0.047159 | 61.592 | 0.088375 | 61.505 | -0.033101 | 0.034501 | 61.5662 | 0.007721 | 61.3535 | 61.5354 | 61.4783 | 61.4977 | 61.5213 | 61.5689 | 61.5175 | 61.5614 | 123.1063 | 61.6027 | 123.0193 | 61.4812 | 61.5488 | 123.0804 | 61.522 | 122.8678 | 61.5575 | 61.5843 | 61.4705 | 61.4973
306.5938 | 123.2803 | -61.496 | 61.6608 | 0.021127 | -0.0451 | -0.007421 | 0.007033 | 0.040843 | 0.016907 | 0.038003 | 61.5966 | 0.097532 | 61.5096 | -0.03768 | 0.025345 | 61.5662 | 0.012299 | 61.3535 | 61.5171 | 61.4509 | 61.4886 | 61.503 | 61.5368 | 61.5129 | 61.534 | 123.0926 | 61.5935 | 123.0055 | 61.4583 | 61.5213 | 123.0621 | 61.5083 | 122.8495 | 61.5713 | 61.5843 | 61.4842 | 61.4973
307.5938 | 123.2803 | -61.5005 | 61.6699 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.6058 | 0.097532 | 61.5004 | -0.03768 | 0.039079 | 61.5753 | 0.007721 | 61.3581 | 61.5263 | 61.4554 | 61.484 | 61.503 | 61.546 | 61.5083 | 61.5431 | 123.1063 | 61.5981 | 123.0009 | 61.4629 | 61.5396 | 123.0759 | 61.5083 | 122.8586 | 61.5667 | 61.5981 | 61.4613 | 61.4927
308.5938 | 123.2849 | -61.4456 | 61.6562 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.049999 | -0.005985 | 0.038003 | 61.6012 | 0.088375 | 61.4958 | -0.028522 | 0.029923 | 61.5707 | 0.007721 | 61.3581 | 61.4667 | 61.4051 | 61.4382 | 61.4481 | 61.4956 | 61.4396 | 61.4836 | 123.0468 | 61.534 | 122.9414 | 61.4171 | 61.4755 | 123.0164 | 61.4533 | 122.8037 | 61.5713 | 61.5935 | 61.4659 | 61.4881
309.5938 | 123.3261 | -61.4822 | 61.6562 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.045421 | 0.00775 | 0.038003 | 61.6012 | 0.097532 | 61.5096 | -0.028522 | 0.034501 | 61.5707 | 0.007721 | 61.3535 | 61.5079 | 61.4371 | 61.4702 | 61.4801 | 61.5277 | 61.49 | 61.5202 | 123.0834 | 61.5798 | 122.9918 | 61.4537 | 61.5167 | 123.053 | 61.49 | 122.8357 | 61.5667 | 61.5935 | 61.4751 | 61.5018
310.5938 | 123.3765 | -61.4822 | 61.5646 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.592 | 0.10211 | 61.5004 | -0.03768 | 0.029923 | 61.557 | 0.007721 | 61.3489 | 61.5079 | 61.4417 | 61.4657 | 61.4939 | 61.5231 | 61.4808 | 61.5248 | 123.0743 | 61.5844 | 122.9826 | 61.4446 | 61.5122 | 123.0392 | 61.49 | 122.8312 | 61.5621 | 61.5843 | 61.4705 | 61.4927
311.5938 | 123.2574 | -61.496 | 61.6653 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.5966 | 0.088375 | 61.505 | -0.046838 | 0.034501 | 61.5662 | 0.003143 | 61.3535 | 61.5263 | 61.46 | 61.484 | 61.503 | 61.5368 | 61.4991 | 61.5477 | 123.0926 | 61.5843 | 123.001 | 61.4491 | 61.5305 | 123.0621 | 61.4991 | 122.8495 | 61.5621 | 61.5935 | 61.4705 | 61.5018
312.5938 | 123.2346 | -61.4777 | 61.6562 | 0.030283 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.5966 | 0.10211 | 61.505 | -0.046838 | 0.034501 | 61.5753 | 0.003143 | 61.3627 | 61.5079 | 61.4326 | 61.4702 | 61.4847 | 61.5231 | 61.4854 | 61.5202 | 123.0743 | 61.5798 | 122.9826 | 61.4308 | 61.5122 | 123.053 | 61.4808 | 122.8403 | 61.5621 | 61.5935 | 61.4705 | 61.5018
313.5938 | 123.2712 | -61.496 | 61.647 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.592 | 0.083796 | 61.4958 | -0.033101 | 0.029923 | 61.5662 | -0.001436 | 61.3627 | 61.5217 | 61.4555 | 61.4794 | 61.4984 | 61.5414 | 61.5037 | 61.5386 | 123.088 | 61.5798 | 122.9918 | 61.4629 | 61.5259 | 123.0621 | 61.4945 | 122.8586 | 61.5621 | 61.5935 | 61.4659 | 61.4973
314.5938 | 123.3398 | -61.496 | 61.7111 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.038003 | 61.6012 | 0.10211 | 61.5004 | -0.042259 | 0.029923 | 61.5707 | 0.003143 | 61.3672 | 61.5217 | 61.46 | 61.4794 | 61.4984 | 61.5414 | 61.5037 | 61.534 | 123.0972 | 61.5981 | 122.9964 | 61.4537 | 61.5259 | 123.0667 | 61.4991 | 122.8632 | 61.5713 | 61.5981 | 61.4705 | 61.4973
315.5938 | 123.3032 | -61.4868 | 61.6196 | 0.025705 | -0.0451 | -0.007421 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.5875 | 0.083796 | 61.5004 | -0.03768 | 0.034501 | 61.5753 | 0.007721 | 61.3581 | 61.5125 | 61.4417 | 61.4794 | 61.4984 | 61.5277 | 61.4946 | 61.534 | 123.0743 | 61.5706 | 122.9872 | 61.4491 | 61.5213 | 123.0621 | 61.4945 | 122.8449 | 61.553 | 61.5797 | 61.4659 | 61.4927
316.5938 | 123.3719 | -61.4731 | 61.6013 | 0.025705 | -0.0451 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.5875 | 0.088375 | 61.5141 | -0.03768 | 0.029923 | 61.5707 | 0.007721 | 61.3581 | 61.4988 | 61.428 | 61.4657 | 61.4755 | 61.5093 | 61.4763 | 61.5157 | 123.0605 | 61.5615 | 122.9872 | 61.4354 | 61.503 | 123.0438 | 61.4808 | 122.8312 | 61.5575 | 61.5797 | 61.4842 | 61.5064
317.5938 | 123.2986 | -61.4822 | 61.6516 | 0.016548 | -0.049678 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.5875 | 0.097532 | 61.505 | -0.042259 | 0.034501 | 61.5662 | 0.007721 | 61.3581 | 61.4988 | 61.4326 | 61.4702 | 61.4893 | 61.5231 | 61.4854 | 61.5248 | 123.0697 | 61.5798 | 122.9872 | 61.44 | 61.5167 | 123.0484 | 61.49 | 122.8403 | 61.553 | 61.5797 | 61.4705 | 61.4973
318.5938 | 123.23 | -61.5005 | 61.6653 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.00775 | 0.047159 | 61.5829 | 0.092954 | 61.5004 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3672 | 61.5217 | 61.4554 | 61.4885 | 61.503 | 61.5414 | 61.5083 | 61.5477 | 123.0834 | 61.5935 | 123.0009 | 61.4629 | 61.5305 | 123.0713 | 61.5037 | 122.8678 | 61.553 | 61.5797 | 61.4705 | 61.4973
319.5938 | 123.2483 | -61.4731 | 61.6653 | 0.016548 | -0.040521 | -0.021157 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.5966 | 0.10211 | 61.4958 | -0.042259 | 0.034501 | 61.5753 | 0.007721 | 61.3627 | 61.4896 | 61.4326 | 61.4519 | 61.4755 | 61.5185 | 61.4763 | 61.5157 | 123.0697 | 61.5752 | 122.9689 | 61.4308 | 61.5076 | 123.0484 | 61.4808 | 122.8357 | 61.5621 | 61.5889 | 61.4613 | 61.4881
320.5938 | 123.2803 | -61.496 | 61.647 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.049999 | 0.00775 | 0.047159 | 61.592 | 0.092954 | 61.5096 | -0.042259 | 0.034501 | 61.5707 | 0.003143 | 61.3581 | 61.5217 | 61.4509 | 61.484 | 61.503 | 61.546 | 61.5037 | 61.5431 | 123.088 | 61.5889 | 123.0055 | 61.4537 | 61.5305 | 123.0667 | 61.4991 | 122.8541 | 61.5575 | 61.5889 | 61.4751 | 61.5064
321.5938 | 123.2986 | -61.4731 | 61.6333 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.045421 | 0.003172 | 0.038003 | 61.5966 | 0.088375 | 61.505 | -0.033101 | 0.029923 | 61.5707 | 0.007721 | 61.3672 | 61.4942 | 61.428 | 61.4611 | 61.471 | 61.5185 | 61.4763 | 61.5111 | 123.0697 | 61.5615 | 122.9781 | 61.44 | 61.503 | 123.0438 | 61.4808 | 122.8403 | 61.5667 | 61.5889 | 61.4751 | 61.4973
322.5938 | 123.3856 | -61.4639 | 61.6241 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.592 | 0.092954 | 61.5004 | -0.042259 | 0.025345 | 61.5753 | -0.001436 | 61.3581 | 61.4851 | 61.4234 | 61.4474 | 61.4664 | 61.5048 | 61.4671 | 61.5065 | 123.056 | 61.5569 | 122.9643 | 61.4217 | 61.4893 | 123.0392 | 61.4625 | 122.822 | 61.5667 | 61.5935 | 61.4751 | 61.5018
323.5938 | 123.4085 | -61.4548 | 61.6333 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.042581 | 61.592 | 0.088375 | 61.4958 | -0.042259 | 0.029923 | 61.5707 | 0.003143 | 61.3627 | 61.4805 | 61.4097 | 61.4382 | 61.4572 | 61.4956 | 61.4534 | 61.4974 | 123.0468 | 61.5431 | 122.9506 | 61.4125 | 61.4847 | 123.0255 | 61.4579 | 122.8174 | 61.5621 | 61.5889 | 61.4659 | 61.4927
324.5938 | 123.4222 | -61.441 | 61.6196 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.5966 | 0.097532 | 61.5004 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3627 | 61.4622 | 61.4051 | 61.4245 | 61.4435 | 61.4773 | 61.4442 | 61.479 | 123.0377 | 61.5386 | 122.9414 | 61.3988 | 61.471 | 123.0164 | 61.4488 | 122.8037 | 61.5667 | 61.5889 | 61.4705 | 61.4927
325.5938 | 123.3444 | -61.4685 | 61.6562 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6058 | 0.097532 | 61.5096 | -0.033101 | 0.039079 | 61.5707 | 0.003143 | 61.3535 | 61.4942 | 61.428 | 61.4565 | 61.4755 | 61.5093 | 61.4763 | 61.5111 | 123.0743 | 61.566 | 122.9781 | 61.4354 | 61.5076 | 123.0392 | 61.4716 | 122.822 | 61.5667 | 61.6026 | 61.4705 | 61.5064
326.5938 | 123.3215 | -61.4731 | 61.6333 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.012329 | 0.042581 | 61.5966 | 0.092954 | 61.5096 | -0.03768 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.4942 | 61.428 | 61.4565 | 61.4801 | 61.5139 | 61.4854 | 61.5157 | 123.0697 | 61.566 | 122.9826 | 61.4354 | 61.503 | 123.0484 | 61.4808 | 122.8403 | 61.5667 | 61.5889 | 61.4796 | 61.5018
327.5938 | 123.3582 | -61.4456 | 61.5875 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.5875 | 0.092954 | 61.5141 | -0.03768 | 0.034501 | 61.5662 | 0.007721 | 61.3627 | 61.4667 | 61.4005 | 61.429 | 61.4481 | 61.4819 | 61.4488 | 61.4882 | 123.0331 | 61.5386 | 122.9598 | 61.4079 | 61.4801 | 123.0118 | 61.4533 | 122.8083 | 61.553 | 61.5797 | 61.4796 | 61.5064
328.5938 | 123.349 | -61.4594 | 61.615 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.049999 | 0.003172 | 0.042581 | 61.5966 | 0.097532 | 61.505 | -0.03768 | 0.029923 | 61.5753 | 0.007721 | 61.3627 | 61.4851 | 61.4188 | 61.4474 | 61.4664 | 61.5093 | 61.4625 | 61.5019 | 123.056 | 61.5569 | 122.9643 | 61.4217 | 61.4893 | 123.0347 | 61.4671 | 122.822 | 61.5667 | 61.5889 | 61.4751 | 61.4973
329.5938 | 123.3902 | -61.4639 | 61.6287 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.045421 | -0.001406 | 0.047159 | 61.592 | 0.092954 | 61.505 | -0.051417 | 0.029923 | 61.5662 | 0.003143 | 61.3627 | 61.4851 | 61.4234 | 61.4474 | 61.471 | 61.5093 | 61.4625 | 61.5111 | 123.056 | 61.5569 | 122.9689 | 61.4125 | 61.4939 | 123.0301 | 61.4671 | 122.8266 | 61.5621 | 61.5889 | 61.4751 | 61.5018
330.5938 | 123.3902 | -61.4685 | 61.615 | 0.021127 | -0.049678 | -0.025735 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.592 | 0.088375 | 61.5004 | -0.033101 | 0.034501 | 61.5707 | -0.006014 | 61.3535 | 61.4896 | 61.4188 | 61.4428 | 61.471 | 61.5093 | 61.4717 | 61.5111 | 123.0605 | 61.5569 | 122.9689 | 61.4354 | 61.503 | 123.0392 | 61.4625 | 122.822 | 61.5575 | 61.5981 | 61.4659 | 61.5064
331.5938 | 123.4314 | -61.4502 | 61.6241 | 0.021127 | -0.0451 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.038003 | 61.5966 | 0.088375 | 61.4912 | -0.03768 | 0.029923 | 61.5707 | 0.007721 | 61.3672 | 61.4713 | 61.4051 | 61.4382 | 61.4618 | 61.491 | 61.4488 | 61.4882 | 123.0468 | 61.5386 | 122.9414 | 61.4125 | 61.4801 | 123.0209 | 61.4579 | 122.8174 | 61.5667 | 61.5889 | 61.4613 | 61.4835
332.5938 | 123.3765 | -61.4548 | 61.6058 | 0.016548 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.033424 | 61.6012 | 0.10211 | 61.5004 | -0.042259 | 0.029923 | 61.5799 | 0.003143 | 61.3581 | 61.4713 | 61.4097 | 61.4382 | 61.4618 | 61.491 | 61.4534 | 61.4882 | 123.056 | 61.5569 | 122.9552 | 61.4125 | 61.4847 | 123.0347 | 61.4579 | 122.8129 | 61.5713 | 61.5981 | 61.4705 | 61.4973
333.5938 | 123.3719 | -61.4502 | 61.6241 | 0.016548 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | -0.001406 | 0.042581 | 61.592 | 0.097532 | 61.505 | -0.033101 | 0.039079 | 61.5753 | 0.007721 | 61.3581 | 61.4667 | 61.4051 | 61.4336 | 61.4572 | 61.4956 | 61.4488 | 61.4928 | 123.0422 | 61.5477 | 122.9552 | 61.4171 | 61.4893 | 123.0255 | 61.4579 | 122.8083 | 61.553 | 61.5843 | 61.4659 | 61.4973
334.5938 | 123.5413 | -61.4136 | 61.6882 | 0.025705 | -0.0451 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.047159 | 61.6012 | 0.097532 | 61.5096 | -0.046838 | 0.034501 | 61.5707 | 0.003143 | 61.3627 | 61.4393 | 61.3685 | 61.4016 | 61.4252 | 61.4498 | 61.4122 | 61.4607 | 123.0148 | 61.5111 | 122.9231 | 61.3667 | 61.4481 | 122.9843 | 61.4167 | 122.7762 | 61.5667 | 61.5981 | 61.4751 | 61.5064
335.5938 | 123.3719 | -61.4319 | 61.5921 | 0.016548 | -0.049678 | -0.012 | 0.007033 | 0.045421 | -0.001406 | 0.042581 | 61.5966 | 0.092954 | 61.5004 | -0.03768 | 0.029923 | 61.5707 | 0.012299 | 61.3581 | 61.4484 | 61.3822 | 61.4199 | 61.4389 | 61.4773 | 61.4305 | 61.4745 | 123.0285 | 61.5248 | 122.9323 | 61.3942 | 61.4618 | 123.0026 | 61.4442 | 122.79 | 61.5667 | 61.5843 | 61.4705 | 61.4881
336.5938 | 123.3215 | -61.4822 | 61.615 | 0.025705 | -0.049678 | -0.012 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.5966 | 0.088375 | 61.5004 | -0.042259 | 0.029923 | 61.5707 | 0.003143 | 61.3672 | 61.5079 | 61.4326 | 61.4702 | 61.4847 | 61.5277 | 61.4854 | 61.5248 | 123.0789 | 61.5706 | 122.9826 | 61.44 | 61.5122 | 123.053 | 61.4854 | 122.8495 | 61.5667 | 61.5935 | 61.4705 | 61.4973
337.5938 | 123.3261 | -61.496 | 61.5967 | 0.021127 | -0.049678 | -0.021157 | 0.007033 | 0.040843 | -0.001406 | 0.038003 | 61.5966 | 0.088375 | 61.4912 | -0.03768 | 0.034501 | 61.5662 | 0.007721 | 61.3718 | 61.5171 | 61.4463 | 61.4748 | 61.503 | 61.5368 | 61.4946 | 61.534 | 123.0926 | 61.5843 | 122.9872 | 61.4583 | 61.5305 | 123.0621 | 61.5037 | 122.8678 | 61.5621 | 61.5889 | 61.4567 | 61.4835
338.5938 | 123.3856 | -61.496 | 61.615 | 0.021127 | -0.054257 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.047159 | 61.592 | 0.092954 | 61.505 | -0.046838 | 0.034501 | 61.5662 | 0.012299 | 61.3581 | 61.5171 | 61.4417 | 61.484 | 61.503 | 61.5322 | 61.4991 | 61.5431 | 123.088 | 61.5889 | 123.001 | 61.4491 | 61.5305 | 123.0621 | 61.5083 | 122.8541 | 61.5575 | 61.5797 | 61.4705 | 61.4927
339.5938 | 123.3856 | -61.4777 | 61.5875 | 0.025705 | -0.0451 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.042581 | 61.6012 | 0.088375 | 61.5096 | -0.042259 | 0.029923 | 61.5662 | 0.003143 | 61.3627 | 61.5034 | 61.4326 | 61.4611 | 61.4893 | 61.5139 | 61.4763 | 61.5202 | 123.0789 | 61.566 | 122.9872 | 61.4354 | 61.5076 | 123.0438 | 61.4808 | 122.8403 | 61.5713 | 61.5981 | 61.4796 | 61.5064
340.5938 | 123.3582 | -61.4594 | 61.6058 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.038003 | 61.6012 | 0.088375 | 61.5096 | -0.033101 | 0.025345 | 61.5753 | 0.007721 | 61.3581 | 61.4851 | 61.4143 | 61.4474 | 61.4664 | 61.4956 | 61.4579 | 61.4974 | 123.0606 | 61.5477 | 122.9689 | 61.4262 | 61.4847 | 123.0347 | 61.4671 | 122.8174 | 61.5759 | 61.5935 | 61.4842 | 61.5018
341.5938 | 123.3444 | -61.441 | 61.615 | 0.025705 | -0.035942 | -0.012 | 0.007033 | 0.049999 | 0.00775 | 0.042581 | 61.6012 | 0.092954 | 61.505 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3627 | 61.4667 | 61.4051 | 61.429 | 61.4481 | 61.491 | 61.4488 | 61.4836 | 123.0422 | 61.534 | 122.946 | 61.4034 | 61.471 | 123.0118 | 61.4442 | 122.8037 | 61.5713 | 61.5981 | 61.4751 | 61.5018
342.5938 | 123.349 | -61.4777 | 61.6013 | 0.016548 | -0.049678 | -0.016578 | -0.002124 | 0.040843 | -0.001406 | 0.042581 | 61.6012 | 0.10211 | 61.5096 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3627 | 61.4942 | 61.428 | 61.4611 | 61.4755 | 61.5185 | 61.4763 | 61.5202 | 123.0789 | 61.5798 | 122.9872 | 61.44 | 61.5076 | 123.0484 | 61.4808 | 122.8403 | 61.5713 | 61.5981 | 61.4796 | 61.5064
343.5938 | 123.3261 | -61.4731 | 61.6287 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.045421 | -0.005985 | 0.047159 | 61.5875 | 0.092954 | 61.505 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3535 | 61.4988 | 61.4326 | 61.4611 | 61.4755 | 61.5185 | 61.4671 | 61.5202 | 123.0605 | 61.566 | 122.9781 | 61.4354 | 61.503 | 123.0484 | 61.4762 | 122.8266 | 61.5575 | 61.5843 | 61.4751 | 61.5018
344.5938 | 123.3582 | -61.4731 | 61.6058 | 0.025705 | -0.049678 | -0.012 | 0.002454 | 0.031687 | -0.001406 | 0.042581 | 61.5966 | 0.088375 | 61.5004 | -0.03768 | 0.029923 | 61.5753 | 0.007721 | 61.3489 | 61.4988 | 61.4234 | 61.4611 | 61.4755 | 61.5048 | 61.4717 | 61.5157 | 123.0697 | 61.5615 | 122.9735 | 61.4354 | 61.503 | 123.0484 | 61.4808 | 122.822 | 61.5667 | 61.5889 | 61.4705 | 61.4927
345.5938 | 123.3536 | -61.4594 | 61.6013 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.6058 | 0.097532 | 61.5096 | -0.046838 | 0.029923 | 61.5707 | 0.003143 | 61.3581 | 61.4851 | 61.4234 | 61.4428 | 61.4618 | 61.4956 | 61.4671 | 61.5019 | 123.0651 | 61.5569 | 122.9689 | 61.4125 | 61.4893 | 123.0301 | 61.4625 | 122.8174 | 61.5759 | 61.6026 | 61.4796 | 61.5064
346.5938 | 123.3765 | -61.4914 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5966 | 0.092954 | 61.5004 | -0.042259 | 0.034501 | 61.5753 | 0.007721 | 61.3581 | 61.5171 | 61.4509 | 61.4748 | 61.4984 | 61.5277 | 61.4946 | 61.5248 | 123.088 | 61.5843 | 122.9918 | 61.4491 | 61.5259 | 123.0667 | 61.4991 | 122.8495 | 61.5621 | 61.5889 | 61.4659 | 61.4927
347.5938 | 123.3444 | -61.5005 | 61.5784 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.040843 | 0.003172 | 0.038003 | 61.592 | 0.097532 | 61.505 | -0.03768 | 0.029923 | 61.5662 | 0.003143 | 61.3535 | 61.5263 | 61.4646 | 61.4885 | 61.4984 | 61.5414 | 61.5037 | 61.5386 | 123.0926 | 61.5981 | 123.0055 | 61.4629 | 61.5305 | 123.0667 | 61.5037 | 122.8541 | 61.5621 | 61.5889 | 61.4751 | 61.5018
348.5938 | 123.3307 | -61.4777 | 61.6104 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.5966 | 0.088375 | 61.5141 | -0.03768 | 0.029923 | 61.5707 | 0.007721 | 61.3535 | 61.5079 | 61.4371 | 61.4657 | 61.4847 | 61.5231 | 61.4808 | 61.5248 | 123.0743 | 61.566 | 122.9918 | 61.44 | 61.5076 | 123.0484 | 61.4854 | 122.8312 | 61.5667 | 61.5889 | 61.4842 | 61.5064
349.5938 | 123.3307 | -61.4685 | 61.5921 | 0.016548 | -0.049678 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.592 | 0.092954 | 61.5096 | -0.042259 | 0.025345 | 61.5707 | 0.007721 | 61.3535 | 61.4851 | 61.4188 | 61.4519 | 61.4755 | 61.5093 | 61.4717 | 61.5065 | 123.0605 | 61.5615 | 122.9781 | 61.4262 | 61.4939 | 123.0392 | 61.4762 | 122.822 | 61.5667 | 61.5843 | 61.4842 | 61.5018
350.5938 | 123.3536 | -61.4777 | 61.5829 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.045421 | 0.00775 | 0.047159 | 61.6012 | 0.097532 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3581 | 61.4988 | 61.4371 | 61.4657 | 61.4893 | 61.5231 | 61.4854 | 61.5248 | 123.0789 | 61.5752 | 122.9872 | 61.4354 | 61.5076 | 123.053 | 61.4854 | 122.8357 | 61.5713 | 61.5935 | 61.4796 | 61.5018
351.5938 | 123.3582 | -61.4731 | 61.5875 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.040843 | -0.001406 | 0.033424 | 61.6012 | 0.088375 | 61.505 | -0.042259 | 0.025345 | 61.5799 | -0.001436 | 61.3581 | 61.4942 | 61.4326 | 61.4519 | 61.4755 | 61.5139 | 61.4717 | 61.5065 | 123.0743 | 61.5615 | 122.9781 | 61.4308 | 61.4984 | 123.053 | 61.4716 | 122.8312 | 61.5759 | 61.6026 | 61.4796 | 61.5064
352.5938 | 123.3856 | -61.4868 | 61.5875 | 0.021127 | -0.040521 | -0.021157 | 0.007033 | 0.040843 | 0.003172 | 0.047159 | 61.592 | 0.088375 | 61.5096 | -0.042259 | 0.025345 | 61.5707 | 0.007721 | 61.3581 | 61.5079 | 61.4463 | 61.4657 | 61.4938 | 61.5277 | 61.49 | 61.534 | 123.0789 | 61.5752 | 122.9964 | 61.4446 | 61.5122 | 123.0576 | 61.4945 | 122.8449 | 61.5667 | 61.5843 | 61.4842 | 61.5018
353.5938 | 123.349 | -61.4822 | 61.6013 | 0.016548 | -0.040521 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.047159 | 61.6104 | 0.097532 | 61.5187 | -0.03768 | 0.025345 | 61.5753 | 0.007721 | 61.3535 | 61.4988 | 61.4417 | 61.4611 | 61.4847 | 61.5185 | 61.4854 | 61.5294 | 123.0926 | 61.5798 | 123.001 | 61.4446 | 61.5076 | 123.0576 | 61.49 | 122.8357 | 61.585 | 61.6026 | 61.4934 | 61.511
354.5938 | 123.3536 | -61.4731 | 61.5692 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.040843 | 0.00775 | 0.038003 | 61.5966 | 0.092954 | 61.5004 | -0.03768 | 0.025345 | 61.5707 | 0.007721 | 61.3627 | 61.4988 | 61.4326 | 61.4611 | 61.4755 | 61.5139 | 61.4808 | 61.5111 | 123.0697 | 61.566 | 122.9735 | 61.4354 | 61.4984 | 123.0438 | 61.4808 | 122.8357 | 61.5713 | 61.5889 | 61.4751 | 61.4927
355.5938 | 123.3719 | -61.4685 | 61.5784 | 0.025705 | -0.0451 | -0.007421 | -0.002124 | 0.045421 | 0.003172 | 0.042581 | 61.5966 | 0.092954 | 61.505 | -0.046838 | 0.029923 | 61.5707 | 0.003143 | 61.3535 | 61.4942 | 61.4234 | 61.4611 | 61.4664 | 61.5139 | 61.4717 | 61.5111 | 123.0651 | 61.5615 | 122.9735 | 61.4217 | 61.4984 | 123.0392 | 61.4716 | 122.822 | 61.5667 | 61.5935 | 61.4751 | 61.5018
356.5938 | 123.3856 | -61.4685 | 61.5738 | 0.021127 | -0.040521 | -0.007421 | 0.011611 | 0.036265 | 0.003172 | 0.042581 | 61.5966 | 0.088375 | 61.5141 | -0.042259 | 0.020767 | 61.5707 | -0.001436 | 61.3627 | 61.4896 | 61.428 | 61.4611 | 61.4801 | 61.5048 | 61.4717 | 61.5111 | 123.0651 | 61.5569 | 122.9826 | 61.4262 | 61.4893 | 123.0392 | 61.4671 | 122.8312 | 61.5759 | 61.5981 | 61.4934 | 61.5156
357.5938 | 123.3261 | -61.4731 | 61.5829 | 0.016548 | -0.040521 | -0.012 | 0.01619 | 0.045421 | 0.012329 | 0.051737 | 61.6012 | 0.097532 | 61.5141 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3535 | 61.4896 | 61.4326 | 61.4611 | 61.4893 | 61.5185 | 61.4854 | 61.5248 | 123.0743 | 61.5706 | 122.9872 | 61.4354 | 61.503 | 123.0438 | 61.4762 | 122.8266 | 61.5713 | 61.5981 | 61.4842 | 61.511
358.5938 | 123.3765 | -61.4777 | 61.5692 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.047159 | 61.6012 | 0.088375 | 61.5096 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3581 | 61.4988 | 61.4326 | 61.4611 | 61.4801 | 61.5185 | 61.4763 | 61.5248 | 123.0789 | 61.566 | 122.9872 | 61.4354 | 61.503 | 123.053 | 61.4808 | 122.8357 | 61.5759 | 61.5981 | 61.4842 | 61.5064
359.5938 | 123.3902 | -61.4685 | 61.5875 | 0.030283 | -0.054257 | -0.016578 | 0.002454 | 0.045421 | 0.00775 | 0.047159 | 61.6058 | 0.088375 | 61.5141 | -0.046838 | 0.025345 | 61.5616 | 0.007721 | 61.3581 | 61.4988 | 61.4142 | 61.4519 | 61.471 | 61.5139 | 61.4763 | 61.5157 | 123.0743 | 61.5569 | 122.9826 | 61.4217 | 61.4939 | 123.0301 | 61.4762 | 122.8266 | 61.5804 | 61.5981 | 61.4888 | 61.5064
360.5938 | 123.4177 | -61.4502 | 61.5967 | 0.030283 | -0.0451 | -0.007421 | 0.011611 | 0.040843 | -0.001406 | 0.042581 | 61.592 | 0.088375 | 61.5096 | -0.046838 | 0.029923 | 61.5707 | 0.003143 | 61.3581 | 61.4805 | 61.4051 | 61.4428 | 61.4618 | 61.491 | 61.4488 | 61.4928 | 123.0422 | 61.5386 | 122.9598 | 61.4034 | 61.4801 | 123.0209 | 61.4533 | 122.8083 | 61.5621 | 61.5889 | 61.4796 | 61.5064
361.5938 | 123.3994 | -61.4639 | 61.5692 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.049999 | 0.003172 | 0.042581 | 61.6012 | 0.097532 | 61.505 | -0.03768 | 0.034501 | 61.5753 | -0.006014 | 61.3627 | 61.4805 | 61.4234 | 61.4519 | 61.4664 | 61.5139 | 61.4671 | 61.5065 | 123.0651 | 61.5615 | 122.9689 | 61.4262 | 61.4984 | 123.0392 | 61.4579 | 122.8266 | 61.5667 | 61.6072 | 61.4705 | 61.511
362.5938 | 123.381 | -61.4639 | 61.5738 | 0.016548 | -0.040521 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.047159 | 61.6012 | 0.092954 | 61.5096 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3535 | 61.4805 | 61.4234 | 61.4519 | 61.4755 | 61.5093 | 61.4671 | 61.5111 | 123.0651 | 61.5569 | 122.9735 | 61.4217 | 61.4893 | 123.0392 | 61.4671 | 122.8174 | 61.5759 | 61.5981 | 61.4842 | 61.5064
363.5938 | 123.2758 | -61.5051 | 61.5875 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.045421 | -0.001406 | 0.042581 | 61.592 | 0.092954 | 61.505 | -0.042259 | 0.034501 | 61.5707 | 0.003143 | 61.3627 | 61.5308 | 61.4646 | 61.4931 | 61.5076 | 61.5505 | 61.5037 | 61.5477 | 123.0972 | 61.5981 | 123.0101 | 61.4629 | 61.5396 | 123.0759 | 61.5083 | 122.8678 | 61.5575 | 61.5889 | 61.4705 | 61.5018
364.5938 | 123.2529 | -61.5143 | 61.6333 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.040843 | 0.003172 | 0.047159 | 61.5966 | 0.092954 | 61.5004 | -0.03768 | 0.020767 | 61.5753 | -0.001436 | 61.3627 | 61.5354 | 61.4738 | 61.5023 | 61.5122 | 61.5551 | 61.5175 | 61.5614 | 123.1109 | 61.6072 | 123.0147 | 61.4766 | 61.535 | 123.0896 | 61.5128 | 122.8769 | 61.5759 | 61.5981 | 61.4796 | 61.5018
365.5938 | 123.3215 | -61.4914 | 61.5921 | 0.016548 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | 0.012329 | 0.042581 | 61.6058 | 0.097532 | 61.5096 | -0.042259 | 0.029923 | 61.5707 | -0.001436 | 61.3581 | 61.5079 | 61.4555 | 61.4748 | 61.4984 | 61.5277 | 61.5037 | 61.534 | 123.0972 | 61.5889 | 123.001 | 61.4491 | 61.5213 | 123.0621 | 61.49 | 122.8495 | 61.5759 | 61.6072 | 61.4796 | 61.511
366.5938 | 123.3124 | -61.5051 | 61.6196 | 0.025705 | -0.049678 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.5966 | 0.088375 | 61.505 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3627 | 61.5308 | 61.4554 | 61.4885 | 61.5122 | 61.5505 | 61.5083 | 61.5477 | 123.1017 | 61.5935 | 123.0101 | 61.4674 | 61.535 | 123.085 | 61.5128 | 122.8678 | 61.5667 | 61.5889 | 61.4751 | 61.4973
367.5938 | 123.381 | -61.4548 | 61.5692 | 0.030283 | -0.0451 | -0.007421 | 0.007033 | 0.036265 | 0.00775 | 0.042581 | 61.5966 | 0.092954 | 61.505 | -0.03768 | 0.034501 | 61.5707 | -0.006014 | 61.3581 | 61.4851 | 61.4097 | 61.4474 | 61.4618 | 61.491 | 61.4625 | 61.4974 | 123.0514 | 61.5477 | 122.9598 | 61.4171 | 61.4893 | 123.0255 | 61.4488 | 122.8129 | 61.5621 | 61.6026 | 61.4705 | 61.511
368.5938 | 123.3536 | -61.4777 | 61.5646 | 0.025705 | -0.0451 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.038003 | 61.6012 | 0.097532 | 61.5096 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3581 | 61.5034 | 61.4326 | 61.4611 | 61.4893 | 61.5231 | 61.4808 | 61.5157 | 123.0789 | 61.5752 | 122.9872 | 61.44 | 61.5076 | 123.053 | 61.4808 | 122.8357 | 61.5713 | 61.5981 | 61.4796 | 61.5064
369.5938 | 123.381 | -61.4777 | 61.5829 | 0.021127 | -0.035942 | -0.007421 | 0.011611 | 0.045421 | 0.00775 | 0.038003 | 61.5966 | 0.097532 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | 0.003143 | 61.3627 | 61.4988 | 61.4417 | 61.4702 | 61.4893 | 61.5231 | 61.4854 | 61.5157 | 123.0743 | 61.5752 | 122.9872 | 61.4354 | 61.5076 | 123.053 | 61.4808 | 122.8403 | 61.5667 | 61.5935 | 61.4796 | 61.5064
370.5938 | 123.2895 | -61.496 | 61.6379 | 0.025705 | -0.040521 | -0.007421 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.6012 | 0.092954 | 61.5141 | -0.03768 | 0.029923 | 61.5753 | -0.001436 | 61.3581 | 61.5217 | 61.4555 | 61.4886 | 61.503 | 61.5414 | 61.5037 | 61.5431 | 123.0972 | 61.5889 | 123.0101 | 61.4583 | 61.5259 | 123.0713 | 61.4945 | 122.8541 | 61.5713 | 61.6026 | 61.4842 | 61.5156
371.5938 | 123.2941 | -61.5005 | 61.6287 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.040843 | 0.003172 | 0.038003 | 61.6012 | 0.097532 | 61.5141 | -0.03768 | 0.025345 | 61.5753 | 0.003143 | 61.3535 | 61.5263 | 61.46 | 61.4931 | 61.503 | 61.5414 | 61.5037 | 61.5386 | 123.1017 | 61.5981 | 123.0147 | 61.4629 | 61.5259 | 123.0759 | 61.5037 | 122.8541 | 61.5759 | 61.5981 | 61.4888 | 61.511
372.5938 | 123.2712 | -61.4914 | 61.5921 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.038003 | 61.592 | 0.088375 | 61.5004 | -0.042259 | 0.025345 | 61.5707 | 0.007721 | 61.3581 | 61.5125 | 61.4509 | 61.4794 | 61.503 | 61.5322 | 61.4946 | 61.5294 | 123.0834 | 61.5798 | 122.9918 | 61.4491 | 61.5167 | 123.0621 | 61.4991 | 122.8495 | 61.5667 | 61.5843 | 61.4751 | 61.4927
373.5938 | 123.2849 | -61.4868 | 61.6104 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.047159 | 61.5966 | 0.088375 | 61.5096 | -0.03768 | 0.025345 | 61.5707 | -0.001436 | 61.3581 | 61.5079 | 61.4417 | 61.4702 | 61.4893 | 61.5322 | 61.49 | 61.534 | 123.0834 | 61.5752 | 122.9964 | 61.4491 | 61.5122 | 123.0576 | 61.4854 | 122.8449 | 61.5713 | 61.5981 | 61.4842 | 61.511
374.5938 | 123.3582 | -61.4914 | 61.5738 | 0.021127 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | 0.003172 | 0.047159 | 61.6012 | 0.092954 | 61.505 | -0.03768 | 0.020767 | 61.5753 | 0.003143 | 61.3627 | 61.5125 | 61.46 | 61.4748 | 61.503 | 61.5322 | 61.4946 | 61.5386 | 123.0926 | 61.5843 | 122.9964 | 61.4537 | 61.5122 | 123.0667 | 61.4945 | 122.8541 | 61.5804 | 61.5981 | 61.4842 | 61.5018
375.5938 | 123.3856 | -61.4731 | 61.5692 | 0.025705 | -0.035942 | -0.016578 | 0.01619 | 0.040843 | 0.003172 | 0.047159 | 61.6012 | 0.092954 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3581 | 61.4988 | 61.4371 | 61.4565 | 61.4893 | 61.5139 | 61.4763 | 61.5202 | 123.0743 | 61.566 | 122.9826 | 61.4308 | 61.503 | 123.0484 | 61.4808 | 122.8312 | 61.5713 | 61.5935 | 61.4796 | 61.5018
376.5938 | 123.349 | -61.496 | 61.5967 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.00775 | 0.042581 | 61.6012 | 0.092954 | 61.505 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3535 | 61.5263 | 61.4509 | 61.484 | 61.4984 | 61.5368 | 61.5037 | 61.5386 | 123.0972 | 61.5889 | 123.001 | 61.4537 | 61.5259 | 123.0713 | 61.4945 | 122.8495 | 61.5713 | 61.6026 | 61.4751 | 61.5064
377.5938 | 123.2895 | -61.528 | 61.6333 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.036265 | 0.00775 | 0.047159 | 61.6012 | 0.10211 | 61.5141 | -0.03768 | 0.029923 | 61.5707 | 0.007721 | 61.3581 | 61.5491 | 61.4875 | 61.5206 | 61.5305 | 61.5643 | 61.5358 | 61.5752 | 123.1292 | 61.6301 | 123.0422 | 61.4903 | 61.5579 | 123.0988 | 61.5357 | 122.8861 | 61.5713 | 61.5935 | 61.4842 | 61.5064
378.5938 | 123.2712 | -61.5097 | 61.6058 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.6058 | 0.092954 | 61.5141 | -0.03768 | 0.034501 | 61.5753 | 0.003143 | 61.3627 | 61.5308 | 61.4692 | 61.4931 | 61.5167 | 61.5551 | 61.5129 | 61.5523 | 123.1155 | 61.6027 | 123.0238 | 61.472 | 61.5442 | 123.085 | 61.5128 | 122.8724 | 61.5713 | 61.6026 | 61.4796 | 61.511
379.5938 | 123.2803 | -61.5097 | 61.6013 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.6058 | 0.097532 | 61.505 | -0.042259 | 0.025345 | 61.5707 | 0.003143 | 61.3581 | 61.5308 | 61.4646 | 61.4977 | 61.5122 | 61.5551 | 61.5175 | 61.5523 | 123.1155 | 61.6072 | 123.0147 | 61.4674 | 61.535 | 123.0804 | 61.5128 | 122.8678 | 61.5804 | 61.6026 | 61.4796 | 61.5018
380.5938 | 123.2712 | -61.5051 | 61.6104 | 0.025705 | -0.0451 | -0.007421 | 0.002454 | 0.045421 | 0.012329 | 0.038003 | 61.6149 | 0.10669 | 61.5096 | -0.03768 | 0.034501 | 61.5707 | 0.003143 | 61.3581 | 61.5308 | 61.46 | 61.4977 | 61.5076 | 61.5505 | 61.5175 | 61.5431 | 123.1201 | 61.6118 | 123.0147 | 61.4674 | 61.5396 | 123.0759 | 61.5083 | 122.8632 | 61.5804 | 61.6118 | 61.4751 | 61.5064
381.5938 | 123.3353 | -61.4777 | 61.5967 | 0.016548 | -0.035942 | -0.021157 | 0.011611 | 0.045421 | 0.00775 | 0.047159 | 61.5966 | 0.097532 | 61.505 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.3581 | 61.4942 | 61.4417 | 61.4565 | 61.4893 | 61.5231 | 61.4854 | 61.5248 | 123.0743 | 61.5752 | 122.9826 | 61.44 | 61.5122 | 123.0576 | 61.4762 | 122.8357 | 61.5621 | 61.5981 | 61.4705 | 61.5064
382.5938 | 123.3215 | -61.496 | 61.5875 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.040843 | 0.012329 | 0.051737 | 61.5966 | 0.097532 | 61.505 | -0.046838 | 0.034501 | 61.5753 | -0.001436 | 61.3581 | 61.5171 | 61.46 | 61.484 | 61.4984 | 61.5368 | 61.5083 | 61.5477 | 123.0926 | 61.5935 | 123.001 | 61.4491 | 61.5305 | 123.0713 | 61.4945 | 122.8541 | 61.5621 | 61.5981 | 61.4705 | 61.5064
383.5938 | 123.3124 | -61.5189 | 61.5875 | 0.025705 | -0.0451 | -0.007421 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.5966 | 0.092954 | 61.5004 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3627 | 61.5446 | 61.4738 | 61.5114 | 61.5305 | 61.5643 | 61.5175 | 61.5614 | 123.1155 | 61.6118 | 123.0193 | 61.4812 | 61.5488 | 123.0942 | 61.522 | 122.8815 | 61.5667 | 61.5935 | 61.4705 | 61.4973
384.5938 | 123.262 | -61.5234 | 61.6379 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.045421 | 0.00775 | 0.042581 | 61.5966 | 0.10211 | 61.505 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3535 | 61.5491 | 61.4829 | 61.5114 | 61.5259 | 61.5689 | 61.5312 | 61.566 | 123.1201 | 61.6255 | 123.0284 | 61.4858 | 61.5534 | 123.0942 | 61.5266 | 122.8769 | 61.5667 | 61.5935 | 61.4751 | 61.5018
385.5938 | 123.2803 | -61.5189 | 61.6196 | 0.034862 | -0.035942 | -0.012 | 0.011611 | 0.049999 | 0.012329 | 0.047159 | 61.6012 | 0.10211 | 61.5096 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3672 | 61.5537 | 61.4829 | 61.5069 | 61.5305 | 61.5689 | 61.5312 | 61.566 | 123.1201 | 61.621 | 123.0284 | 61.4812 | 61.5488 | 123.0896 | 61.522 | 122.8861 | 61.5713 | 61.5981 | 61.4796 | 61.5064
386.5938 | 123.2712 | -61.5051 | 61.6196 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.054577 | -0.001406 | 0.047159 | 61.6012 | 0.088375 | 61.5141 | -0.03768 | 0.025345 | 61.5753 | 0.007721 | 61.3581 | 61.5354 | 61.4646 | 61.4885 | 61.5122 | 61.5597 | 61.5037 | 61.5523 | 123.1063 | 61.5935 | 123.0193 | 61.4674 | 61.5305 | 123.0804 | 61.5128 | 122.8632 | 61.5759 | 61.5935 | 61.4888 | 61.5064
387.5938 | 123.2758 | -61.5189 | 61.615 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.6104 | 0.097532 | 61.5233 | -0.03768 | 0.034501 | 61.5753 | 0.003143 | 61.3581 | 61.5491 | 61.4783 | 61.4977 | 61.5259 | 61.5643 | 61.5266 | 61.5614 | 123.1292 | 61.6164 | 123.0422 | 61.4812 | 61.5534 | 123.0942 | 61.522 | 122.8769 | 61.5759 | 61.6072 | 61.4888 | 61.5202
388.5938 | 123.2574 | -61.4914 | 61.6196 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.036265 | 0.003172 | 0.047159 | 61.6058 | 0.10211 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | 0.003143 | 61.3581 | 61.5217 | 61.4463 | 61.4794 | 61.4984 | 61.5277 | 61.4946 | 61.5386 | 123.0972 | 61.5935 | 123.001 | 61.4491 | 61.5213 | 123.0667 | 61.4945 | 122.8495 | 61.5759 | 61.6026 | 61.4796 | 61.5064
389.5938 | 123.2712 | -61.4914 | 61.6196 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.049999 | 0.00775 | 0.047159 | 61.6012 | 0.10211 | 61.5096 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3535 | 61.5171 | 61.4509 | 61.4794 | 61.4984 | 61.5414 | 61.4991 | 61.5386 | 123.0926 | 61.5935 | 123.001 | 61.4537 | 61.5213 | 123.0667 | 61.4945 | 122.8449 | 61.5713 | 61.5981 | 61.4796 | 61.5064
390.5938 | 123.2574 | -61.5143 | 61.6241 | 0.021127 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5966 | 0.088375 | 61.505 | -0.033101 | 0.029923 | 61.5707 | -0.001436 | 61.3672 | 61.5354 | 61.4738 | 61.5069 | 61.5213 | 61.5505 | 61.5266 | 61.5523 | 123.1109 | 61.6027 | 123.0193 | 61.4812 | 61.5442 | 123.085 | 61.5128 | 122.8815 | 61.5667 | 61.5981 | 61.4751 | 61.5064
391.5938 | 123.2208 | -61.5051 | 61.6196 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.6058 | 0.092954 | 61.5141 | -0.042259 | 0.025345 | 61.5799 | 0.003143 | 61.3672 | 61.5308 | 61.4646 | 61.4931 | 61.5122 | 61.5505 | 61.5129 | 61.5523 | 123.1109 | 61.5981 | 123.0193 | 61.4629 | 61.5305 | 123.085 | 61.5083 | 122.8724 | 61.5804 | 61.6026 | 61.4888 | 61.511
392.5938 | 123.2574 | -61.4914 | 61.6196 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.6058 | 0.10211 | 61.505 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3672 | 61.5125 | 61.4555 | 61.4748 | 61.4938 | 61.5322 | 61.4946 | 61.5386 | 123.0972 | 61.5935 | 122.9964 | 61.4491 | 61.5167 | 123.0667 | 61.4945 | 122.8586 | 61.5804 | 61.6026 | 61.4796 | 61.5018
393.5938 | 123.2895 | -61.4777 | 61.6425 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.036265 | 0.00775 | 0.051737 | 61.6149 | 0.097532 | 61.5096 | -0.046838 | 0.029923 | 61.5799 | 0.007721 | 61.3581 | 61.4942 | 61.4371 | 61.4702 | 61.4801 | 61.5139 | 61.4854 | 61.5294 | 123.0926 | 61.5752 | 122.9872 | 61.4308 | 61.5076 | 123.0576 | 61.4854 | 122.8357 | 61.585 | 61.6072 | 61.4796 | 61.5018
394.5938 | 123.3444 | -61.5234 | 61.5829 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.038003 | 61.6058 | 0.088375 | 61.5096 | -0.042259 | 0.034501 | 61.5753 | 0.003143 | 61.3672 | 61.5537 | 61.4875 | 61.5069 | 61.5305 | 61.5689 | 61.5266 | 61.5614 | 123.1292 | 61.6118 | 123.033 | 61.4812 | 61.5579 | 123.0988 | 61.5266 | 122.8907 | 61.5713 | 61.6026 | 61.4751 | 61.5064
395.5938 | 123.2712 | -61.5097 | 61.6379 | 0.016548 | -0.0451 | -0.007421 | 0.002454 | 0.045421 | -0.001406 | 0.042581 | 61.6012 | 0.092954 | 61.5004 | -0.03768 | 0.020767 | 61.5753 | 0.012299 | 61.3627 | 61.5263 | 61.4646 | 61.5023 | 61.5122 | 61.5551 | 61.5083 | 61.5523 | 123.1109 | 61.6027 | 123.0101 | 61.472 | 61.5305 | 123.085 | 61.522 | 122.8724 | 61.5804 | 61.5889 | 61.4796 | 61.4881
396.5938 | 123.2346 | -61.5097 | 61.6287 | 0.021127 | -0.035942 | -0.007421 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6058 | 0.092954 | 61.505 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3627 | 61.5308 | 61.4738 | 61.5023 | 61.5167 | 61.5505 | 61.5129 | 61.5614 | 123.1155 | 61.6027 | 123.0147 | 61.472 | 61.5442 | 123.0896 | 61.5128 | 122.8724 | 61.5713 | 61.6026 | 61.4705 | 61.5018
397.5938 | 123.2437 | -61.5051 | 61.6287 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.049999 | 0.003172 | 0.047159 | 61.6104 | 0.092954 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3581 | 61.5308 | 61.46 | 61.4931 | 61.5122 | 61.5551 | 61.5083 | 61.5523 | 123.1155 | 61.5981 | 123.0147 | 61.4629 | 61.535 | 123.0804 | 61.5128 | 122.8632 | 61.5804 | 61.6026 | 61.4796 | 61.5018
398.5938 | 123.2574 | -61.5189 | 61.6241 | 0.025705 | -0.035942 | -0.012 | 0.01619 | 0.045421 | 0.00775 | 0.051737 | 61.6058 | 0.11127 | 61.5187 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3581 | 61.5446 | 61.4829 | 61.5069 | 61.535 | 61.5643 | 61.5266 | 61.5706 | 123.1246 | 61.6301 | 123.0376 | 61.4812 | 61.5488 | 123.0942 | 61.522 | 122.8769 | 61.5759 | 61.6026 | 61.4888 | 61.5156
399.5938 | 123.23 | -61.4914 | 61.6425 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.5966 | 0.11127 | 61.5096 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3672 | 61.5217 | 61.4555 | 61.4748 | 61.4984 | 61.5322 | 61.4991 | 61.5386 | 123.088 | 61.6027 | 123.001 | 61.4537 | 61.5213 | 123.0759 | 61.4945 | 122.8586 | 61.5667 | 61.5935 | 61.4796 | 61.5064
400.5938 | 123.3307 | -61.4868 | 61.6058 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.045421 | -0.001406 | 0.047159 | 61.6104 | 0.10211 | 61.5141 | -0.03768 | 0.029923 | 61.5753 | -0.001436 | 61.3672 | 61.5079 | 61.4509 | 61.4748 | 61.4938 | 61.5322 | 61.4854 | 61.534 | 123.0972 | 61.5889 | 123.001 | 61.4491 | 61.5167 | 123.0621 | 61.4854 | 122.8541 | 61.5804 | 61.6118 | 61.4842 | 61.5156
401.5938 | 123.262 | -61.5005 | 61.6425 | 0.021127 | -0.049678 | -0.016578 | 0.011611 | 0.049999 | 0.003172 | 0.042581 | 61.6012 | 0.097532 | 61.505 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3627 | 61.5217 | 61.4509 | 61.484 | 61.5122 | 61.5505 | 61.5037 | 61.5431 | 123.1017 | 61.5981 | 123.0055 | 61.4583 | 61.5305 | 123.0804 | 61.4991 | 122.8632 | 61.5713 | 61.6026 | 61.4751 | 61.5064
402.5938 | 123.2712 | -61.5005 | 61.6196 | 0.030283 | -0.040521 | -0.012 | 0.002454 | 0.040843 | 0.012329 | 0.051737 | 61.6012 | 0.097532 | 61.5096 | -0.042259 | 0.025345 | 61.5799 | 0.007721 | 61.3581 | 61.5308 | 61.46 | 61.4885 | 61.503 | 61.5414 | 61.5129 | 61.5523 | 123.1017 | 61.5981 | 123.0101 | 61.4583 | 61.5259 | 123.0804 | 61.5083 | 122.8586 | 61.5759 | 61.5935 | 61.4842 | 61.5018
403.5938 | 123.2895 | -61.4914 | 61.615 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.6012 | 0.097532 | 61.5187 | -0.033101 | 0.029923 | 61.5753 | 0.003143 | 61.3581 | 61.5125 | 61.4509 | 61.4794 | 61.4984 | 61.5322 | 61.49 | 61.5386 | 123.0926 | 61.5889 | 123.0101 | 61.4583 | 61.5213 | 123.0667 | 61.4945 | 122.8495 | 61.5713 | 61.5981 | 61.4888 | 61.5156
404.5938 | 123.349 | -61.5234 | 61.6653 | 0.034862 | -0.035942 | -0.021157 | 0.011611 | 0.040843 | 0.012329 | 0.047159 | 61.6058 | 0.092954 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3627 | 61.5583 | 61.4875 | 61.5023 | 61.535 | 61.5643 | 61.5358 | 61.5706 | 123.1292 | 61.6164 | 123.033 | 61.4812 | 61.5534 | 123.0988 | 61.5312 | 122.8861 | 61.5759 | 61.5981 | 61.4796 | 61.5018
405.5938 | 123.262 | -61.4868 | 61.6425 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.049999 | 0.00775 | 0.047159 | 61.6058 | 0.10669 | 61.5187 | -0.028522 | 0.039079 | 61.5707 | 0.007721 | 61.3627 | 61.5125 | 61.4463 | 61.4702 | 61.4938 | 61.5368 | 61.4946 | 61.534 | 123.0926 | 61.5935 | 123.0055 | 61.4583 | 61.5259 | 123.0576 | 61.4945 | 122.8495 | 61.5667 | 61.5981 | 61.4796 | 61.511
406.5938 | 123.3948 | -61.496 | 61.5921 | 0.01197 | -0.040521 | -0.007421 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6012 | 0.097532 | 61.5233 | -0.046838 | 0.020767 | 61.5799 | 0.003143 | 61.3535 | 61.5079 | 61.4555 | 61.4886 | 61.503 | 61.5368 | 61.4946 | 61.5386 | 123.0972 | 61.5935 | 123.0193 | 61.4491 | 61.5167 | 123.0759 | 61.4991 | 122.8495 | 61.5804 | 61.5981 | 61.5025 | 61.5202
407.5938 | 123.2437 | -61.4914 | 61.615 | 0.030283 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.6149 | 0.10211 | 61.5141 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3627 | 61.5217 | 61.4463 | 61.4748 | 61.4984 | 61.5368 | 61.4991 | 61.5386 | 123.1063 | 61.5935 | 123.0055 | 61.4583 | 61.5259 | 123.0713 | 61.4945 | 122.8541 | 61.5804 | 61.6118 | 61.4796 | 61.511
408.5938 | 123.2712 | -61.4731 | 61.6287 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.054577 | 0.00775 | 0.042581 | 61.6104 | 0.097532 | 61.5141 | -0.028522 | 0.029923 | 61.5799 | 0.007721 | 61.3627 | 61.4942 | 61.4371 | 61.4611 | 61.4801 | 61.5277 | 61.4808 | 61.5157 | 123.0834 | 61.5706 | 122.9872 | 61.4446 | 61.503 | 123.053 | 61.4808 | 122.8357 | 61.5804 | 61.6026 | 61.4842 | 61.5064
409.5938 | 123.2117 | -61.4639 | 61.6608 | 0.025705 | -0.0451 | -0.012 | 0.011611 | 0.045421 | 0.00775 | 0.051737 | 61.6012 | 0.10669 | 61.5279 | -0.033101 | 0.029923 | 61.5799 | -0.001436 | 61.3627 | 61.4896 | 61.4188 | 61.4519 | 61.4755 | 61.5093 | 61.4717 | 61.5157 | 123.0651 | 61.5706 | 122.9918 | 61.4308 | 61.4939 | 123.0438 | 61.4625 | 122.8266 | 61.5713 | 61.6026 | 61.4979 | 61.5293
410.5938 | 123.2483 | -61.5189 | 61.6196 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.051737 | 61.6058 | 0.10211 | 61.5096 | -0.033101 | 0.029923 | 61.5753 | 0.003143 | 61.3627 | 61.54 | 61.4738 | 61.5069 | 61.5259 | 61.5643 | 61.5266 | 61.5706 | 123.1246 | 61.621 | 123.0284 | 61.4858 | 61.5488 | 123.0942 | 61.522 | 122.8815 | 61.5759 | 61.6026 | 61.4796 | 61.5064
411.5938 | 123.381 | -61.4777 | 61.6104 | 0.025705 | -0.049678 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.042581 | 61.6058 | 0.092954 | 61.5004 | -0.033101 | 0.034501 | 61.5707 | 0.007721 | 61.3672 | 61.5034 | 61.428 | 61.4657 | 61.4801 | 61.5185 | 61.4763 | 61.5202 | 123.0834 | 61.5706 | 122.9781 | 61.4446 | 61.5122 | 123.0484 | 61.4854 | 122.8449 | 61.5713 | 61.5981 | 61.4659 | 61.4927
412.5938 | 123.2941 | -61.4868 | 61.6104 | 0.030283 | -0.040521 | -0.007421 | 0.011611 | 0.040843 | 0.012329 | 0.047159 | 61.6149 | 0.097532 | 61.505 | -0.033101 | 0.029923 | 61.5707 | 0.007721 | 61.3672 | 61.5171 | 61.4463 | 61.4794 | 61.4984 | 61.5277 | 61.4991 | 61.534 | 123.1017 | 61.5843 | 122.9918 | 61.4537 | 61.5167 | 123.0576 | 61.4945 | 122.8541 | 61.585 | 61.6072 | 61.4751 | 61.4973
413.5938 | 123.2941 | -61.496 | 61.6287 | 0.030283 | -0.040521 | -0.016578 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.6058 | 0.10211 | 61.5141 | -0.033101 | 0.029923 | 61.5662 | 0.003143 | 61.3672 | 61.5263 | 61.4555 | 61.4794 | 61.5076 | 61.5414 | 61.4946 | 61.5386 | 123.1017 | 61.5981 | 123.0101 | 61.4629 | 61.5259 | 123.0621 | 61.4991 | 122.8632 | 61.5759 | 61.6026 | 61.4842 | 61.511
414.5938 | 123.3398 | -61.4731 | 61.615 | 0.021127 | -0.040521 | -0.021157 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6104 | 0.10211 | 61.5141 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3672 | 61.4942 | 61.4326 | 61.4519 | 61.4847 | 61.5139 | 61.4763 | 61.5157 | 123.0834 | 61.5752 | 122.9872 | 61.4354 | 61.503 | 123.0484 | 61.4762 | 122.8403 | 61.5804 | 61.6072 | 61.4842 | 61.511
415.5938 | 123.2437 | -61.5234 | 61.6516 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.6012 | 0.097532 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3627 | 61.5491 | 61.4829 | 61.5069 | 61.5259 | 61.5597 | 61.5312 | 61.566 | 123.1246 | 61.621 | 123.033 | 61.4812 | 61.5534 | 123.0988 | 61.522 | 122.8861 | 61.5713 | 61.6026 | 61.4796 | 61.511
416.5938 | 123.4314 | -61.4456 | 61.615 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.6104 | 0.097532 | 61.5096 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3672 | 61.4713 | 61.4005 | 61.4245 | 61.4481 | 61.4865 | 61.4488 | 61.4882 | 123.056 | 61.5432 | 122.9552 | 61.4079 | 61.4755 | 123.0301 | 61.4488 | 122.8129 | 61.5804 | 61.6072 | 61.4796 | 61.5064
417.5938 | 123.2712 | -61.4868 | 61.6425 | 0.021127 | -0.049678 | -0.012 | 0.002454 | 0.040843 | 0.00775 | 0.047159 | 61.5966 | 0.097532 | 61.5141 | -0.042259 | 0.025345 | 61.5753 | 0.003143 | 61.3672 | 61.5079 | 61.4371 | 61.4748 | 61.4893 | 61.5277 | 61.4946 | 61.534 | 123.0834 | 61.5843 | 123.001 | 61.4446 | 61.5122 | 123.0621 | 61.49 | 122.8541 | 61.5713 | 61.5935 | 61.4888 | 61.511
418.5938 | 123.2483 | -61.4822 | 61.6379 | 0.030283 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.051737 | 61.6104 | 0.10669 | 61.5096 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3581 | 61.5125 | 61.4371 | 61.4657 | 61.4893 | 61.5231 | 61.49 | 61.534 | 123.0926 | 61.5889 | 122.9918 | 61.44 | 61.5122 | 123.0576 | 61.49 | 122.8403 | 61.5804 | 61.6026 | 61.4796 | 61.5018
419.5938 | 123.2941 | -61.4914 | 61.6425 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.049999 | 0.00775 | 0.056315 | 61.6012 | 0.097532 | 61.5096 | -0.042259 | 0.025345 | 61.5707 | 0.003143 | 61.3627 | 61.5125 | 61.4509 | 61.4748 | 61.4938 | 61.5414 | 61.4991 | 61.5477 | 123.0926 | 61.5889 | 123.001 | 61.4491 | 61.5167 | 123.0621 | 61.4945 | 122.8541 | 61.5759 | 61.5981 | 61.4842 | 61.5064
420.5938 | 123.2849 | -61.4731 | 61.6333 | 0.034862 | -0.035942 | -0.016578 | 0.007033 | 0.045421 | 0.012329 | 0.042581 | 61.6058 | 0.097532 | 61.5187 | -0.03768 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.5079 | 61.4371 | 61.4565 | 61.4801 | 61.5185 | 61.4854 | 61.5157 | 123.0789 | 61.5706 | 122.9918 | 61.4354 | 61.503 | 123.0484 | 61.4808 | 122.8403 | 61.5759 | 61.5981 | 61.4888 | 61.511
421.5938 | 123.3948 | -61.441 | 61.6058 | 0.016548 | -0.049678 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.6058 | 0.10211 | 61.505 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3718 | 61.4576 | 61.3914 | 61.429 | 61.4435 | 61.4773 | 61.4442 | 61.4836 | 123.0468 | 61.5432 | 122.946 | 61.4034 | 61.471 | 123.0164 | 61.4442 | 122.8129 | 61.5759 | 61.6026 | 61.4751 | 61.5018
422.5938 | 123.3078 | -61.4639 | 61.6425 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.6104 | 0.10211 | 61.5096 | -0.028522 | 0.034501 | 61.5753 | 0.007721 | 61.3718 | 61.4851 | 61.4234 | 61.4519 | 61.4755 | 61.5048 | 61.4717 | 61.5111 | 123.0743 | 61.566 | 122.9735 | 61.4354 | 61.4984 | 123.0392 | 61.4716 | 122.8357 | 61.5759 | 61.6026 | 61.4751 | 61.5018
423.5938 | 123.2712 | -61.4914 | 61.6516 | 0.021127 | -0.0451 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.051737 | 61.6058 | 0.092954 | 61.5096 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3718 | 61.5125 | 61.4463 | 61.4794 | 61.503 | 61.5322 | 61.4991 | 61.5431 | 123.0972 | 61.5843 | 123.001 | 61.4537 | 61.5213 | 123.0667 | 61.4945 | 122.8632 | 61.5759 | 61.6026 | 61.4796 | 61.5064
424.5938 | 123.2529 | -61.4868 | 61.6196 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6012 | 0.092954 | 61.5096 | -0.03768 | 0.034501 | 61.5707 | 0.003143 | 61.3627 | 61.5171 | 61.4463 | 61.4748 | 61.4938 | 61.5322 | 61.49 | 61.534 | 123.088 | 61.5798 | 122.9964 | 61.4491 | 61.5213 | 123.0576 | 61.49 | 122.8495 | 61.5667 | 61.5981 | 61.4751 | 61.5064
425.5938 | 123.2803 | -61.4685 | 61.6333 | 0.025705 | -0.040521 | -0.012 | 0.01619 | 0.040843 | 0.003172 | 0.051737 | 61.6149 | 0.097532 | 61.5187 | -0.03768 | 0.025345 | 61.5662 | 0.007721 | 61.3627 | 61.4942 | 61.428 | 61.4565 | 61.4847 | 61.5093 | 61.4717 | 61.5202 | 123.0834 | 61.566 | 122.9872 | 61.4308 | 61.4939 | 123.0347 | 61.4762 | 122.8312 | 61.5896 | 61.6072 | 61.4934 | 61.511
426.5938 | 123.3078 | -61.4822 | 61.6241 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6058 | 0.10211 | 61.5096 | -0.033101 | 0.029923 | 61.5707 | 0.007721 | 61.3718 | 61.5034 | 61.4463 | 61.4657 | 61.4893 | 61.5277 | 61.4854 | 61.5294 | 123.088 | 61.5844 | 122.9918 | 61.4491 | 61.5122 | 123.053 | 61.49 | 122.8541 | 61.5759 | 61.5981 | 61.4796 | 61.5018
427.5938 | 123.3032 | -61.4731 | 61.6333 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.042581 | 61.6058 | 0.10211 | 61.5141 | -0.03768 | 0.034501 | 61.5707 | 0.003143 | 61.3672 | 61.4988 | 61.4326 | 61.4565 | 61.4847 | 61.5139 | 61.4808 | 61.5157 | 123.0789 | 61.5752 | 122.9872 | 61.4354 | 61.5076 | 123.0438 | 61.4762 | 122.8403 | 61.5713 | 61.6026 | 61.4796 | 61.511
428.5938 | 123.3124 | -61.4731 | 61.647 | 0.021127 | -0.049678 | -0.007421 | 0.01619 | 0.045421 | 0.00775 | 0.051737 | 61.6104 | 0.092954 | 61.5141 | -0.033101 | 0.029923 | 61.5662 | 0.007721 | 61.3627 | 61.4942 | 61.4234 | 61.4657 | 61.4893 | 61.5185 | 61.4808 | 61.5248 | 123.0834 | 61.566 | 122.9872 | 61.44 | 61.503 | 123.0392 | 61.4808 | 122.8357 | 61.5804 | 61.6026 | 61.4842 | 61.5064
429.5938 | 123.3124 | -61.496 | 61.6287 | 0.025705 | -0.049678 | -0.012 | 0.011611 | 0.045421 | 0.003172 | 0.047159 | 61.6104 | 0.10211 | 61.5141 | -0.03768 | 0.034501 | 61.5753 | -0.001436 | 61.3627 | 61.5217 | 61.4463 | 61.484 | 61.5076 | 61.5414 | 61.4991 | 61.5431 | 123.1063 | 61.5981 | 123.0101 | 61.4583 | 61.5305 | 123.0713 | 61.4945 | 122.8586 | 61.5759 | 61.6118 | 61.4796 | 61.5156
430.5938 | 123.3078 | -61.4777 | 61.6425 | 0.025705 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.012329 | 0.051737 | 61.6058 | 0.097532 | 61.5233 | -0.03768 | 0.034501 | 61.5753 | 0.007721 | 61.3672 | 61.5034 | 61.4326 | 61.4702 | 61.4847 | 61.5231 | 61.49 | 61.5294 | 123.0834 | 61.5752 | 123.001 | 61.44 | 61.5122 | 123.053 | 61.4854 | 122.8449 | 61.5713 | 61.5981 | 61.4888 | 61.5156
431.5938 | 123.3078 | -61.4777 | 61.647 | 0.030283 | -0.040521 | -0.016578 | 0.01619 | 0.049999 | 0.00775 | 0.042581 | 61.6149 | 0.088375 | 61.5141 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.5079 | 61.4371 | 61.4611 | 61.4939 | 61.5277 | 61.4854 | 61.5202 | 123.0926 | 61.566 | 122.9918 | 61.4446 | 61.5122 | 123.0576 | 61.4808 | 122.8449 | 61.5804 | 61.6118 | 61.4796 | 61.511
432.5938 | 123.317 | -61.4639 | 61.6653 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.040843 | 0.016907 | 0.042581 | 61.6104 | 0.10669 | 61.5141 | -0.033101 | 0.034501 | 61.5753 | 0.007721 | 61.3627 | 61.4942 | 61.428 | 61.4474 | 61.471 | 61.5048 | 61.4808 | 61.5065 | 123.0743 | 61.5706 | 122.9781 | 61.4308 | 61.4984 | 123.0392 | 61.4716 | 122.8266 | 61.5759 | 61.6026 | 61.4796 | 61.5064
433.5938 | 123.3215 | -61.4685 | 61.647 | 0.025705 | -0.049678 | -0.012 | 0.002454 | 0.040843 | 0.012329 | 0.047159 | 61.6012 | 0.10669 | 61.5279 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3764 | 61.4942 | 61.4188 | 61.4565 | 61.471 | 61.5093 | 61.4808 | 61.5157 | 123.0697 | 61.5752 | 122.9964 | 61.4308 | 61.4984 | 123.0484 | 61.4716 | 122.8449 | 61.5713 | 61.5981 | 61.4979 | 61.5247
434.5938 | 123.317 | -61.496 | 61.6791 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.045421 | -0.001406 | 0.051737 | 61.6058 | 0.10211 | 61.5233 | -0.03768 | 0.029923 | 61.5707 | 0.007721 | 61.3672 | 61.5171 | 61.4555 | 61.484 | 61.503 | 61.5414 | 61.4946 | 61.5477 | 123.1017 | 61.5981 | 123.0193 | 61.4583 | 61.5259 | 123.0667 | 61.5037 | 122.8632 | 61.5759 | 61.5981 | 61.4934 | 61.5156
435.5938 | 123.262 | -61.4822 | 61.6425 | 0.025705 | -0.0451 | -0.012 | 0.011611 | 0.036265 | -0.001406 | 0.047159 | 61.6104 | 0.097532 | 61.5141 | -0.042259 | 0.034501 | 61.5707 | 0.003143 | 61.3718 | 61.5079 | 61.4371 | 61.4702 | 61.4939 | 61.5185 | 61.4808 | 61.5294 | 123.0926 | 61.5798 | 122.9964 | 61.44 | 61.5167 | 123.053 | 61.4854 | 122.8541 | 61.5759 | 61.6072 | 61.4796 | 61.511
436.5938 | 123.3444 | -61.4685 | 61.647 | 0.021127 | -0.0451 | -0.012 | 0.011611 | 0.049999 | 0.012329 | 0.047159 | 61.6149 | 0.10211 | 61.5096 | -0.033101 | 0.029923 | 61.5707 | 0.007721 | 61.3672 | 61.4896 | 61.4234 | 61.4565 | 61.4801 | 61.5185 | 61.4808 | 61.5157 | 123.0834 | 61.5706 | 122.9781 | 61.4354 | 61.4984 | 123.0392 | 61.4762 | 122.8357 | 61.585 | 61.6072 | 61.4796 | 61.5018
437.5938 | 123.3261 | -61.4914 | 61.647 | 0.025705 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.012329 | 0.047159 | 61.6058 | 0.10211 | 61.5187 | -0.042259 | 0.025345 | 61.5753 | 0.007721 | 61.3672 | 61.5171 | 61.4463 | 61.484 | 61.4984 | 61.5368 | 61.5037 | 61.5386 | 123.0972 | 61.5935 | 123.0101 | 61.4491 | 61.5167 | 123.0667 | 61.4991 | 122.8586 | 61.5804 | 61.5981 | 61.4934 | 61.511
438.5938 | 123.3627 | -61.496 | 61.6562 | 0.021127 | -0.049678 | -0.002842 | 0.007033 | 0.040843 | 0.00775 | 0.051737 | 61.6058 | 0.10211 | 61.5187 | -0.042259 | 0.034501 | 61.5753 | 0.003143 | 61.3672 | 61.5171 | 61.4463 | 61.4931 | 61.503 | 61.5368 | 61.5037 | 61.5477 | 123.1017 | 61.5981 | 123.0147 | 61.4537 | 61.5305 | 123.0713 | 61.4991 | 122.8632 | 61.5713 | 61.6026 | 61.4842 | 61.5156
439.5938 | 123.3124 | -61.4822 | 61.647 | 0.025705 | -0.040521 | -0.007421 | 0.011611 | 0.049999 | 0.003172 | 0.042581 | 61.6012 | 0.097532 | 61.5096 | -0.033101 | 0.039079 | 61.5753 | 0.007721 | 61.3672 | 61.5079 | 61.4417 | 61.4748 | 61.4939 | 61.5322 | 61.4854 | 61.5248 | 123.0834 | 61.5798 | 122.9918 | 61.4491 | 61.5213 | 123.0576 | 61.49 | 122.8495 | 61.5621 | 61.5935 | 61.4705 | 61.5018
440.5938 | 123.2941 | -61.4685 | 61.6745 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.056315 | 61.6149 | 0.097532 | 61.5187 | -0.03768 | 0.029923 | 61.5753 | 0.012299 | 61.3672 | 61.4896 | 61.4234 | 61.4565 | 61.4755 | 61.5093 | 61.4763 | 61.5248 | 123.0834 | 61.566 | 122.9872 | 61.4308 | 61.4984 | 123.0438 | 61.4808 | 122.8357 | 61.585 | 61.6026 | 61.4888 | 61.5064
441.5938 | 123.2895 | -61.5005 | 61.6653 | 0.025705 | -0.035942 | -0.012 | 0.007033 | 0.049999 | -0.001406 | 0.038003 | 61.6058 | 0.11127 | 61.5096 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3718 | 61.5263 | 61.4646 | 61.4885 | 61.5076 | 61.5505 | 61.4991 | 61.5386 | 123.1063 | 61.6118 | 123.0101 | 61.4629 | 61.5305 | 123.0713 | 61.5037 | 122.8724 | 61.5759 | 61.6026 | 61.4796 | 61.5064
442.5938 | 123.2849 | -61.4868 | 61.6516 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.051737 | 61.6104 | 0.10211 | 61.5187 | -0.03768 | 0.034501 | 61.5753 | -0.006014 | 61.3718 | 61.5079 | 61.4417 | 61.4702 | 61.4893 | 61.5322 | 61.49 | 61.5386 | 123.0972 | 61.5889 | 123.0055 | 61.4491 | 61.5213 | 123.0621 | 61.4808 | 122.8586 | 61.5759 | 61.6164 | 61.4842 | 61.5247
443.5938 | 123.3032 | -61.4731 | 61.6516 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.056315 | 61.6149 | 0.10211 | 61.5279 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3718 | 61.4988 | 61.4326 | 61.4565 | 61.4847 | 61.5185 | 61.4763 | 61.5294 | 123.088 | 61.5752 | 123.001 | 61.44 | 61.5076 | 123.053 | 61.4762 | 122.8449 | 61.5804 | 61.6118 | 61.4934 | 61.5247
444.5938 | 123.2895 | -61.4868 | 61.6196 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.6012 | 0.10669 | 61.5187 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3672 | 61.5171 | 61.4417 | 61.4748 | 61.4938 | 61.5277 | 61.4946 | 61.534 | 123.088 | 61.5935 | 123.0055 | 61.4491 | 61.5167 | 123.0621 | 61.49 | 122.8541 | 61.5713 | 61.5981 | 61.4888 | 61.5156
445.5938 | 123.317 | -61.4777 | 61.6699 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.6104 | 0.10669 | 61.5233 | -0.023943 | 0.029923 | 61.5707 | 0.007721 | 61.3672 | 61.4988 | 61.4326 | 61.4657 | 61.4847 | 61.5231 | 61.4854 | 61.5248 | 123.088 | 61.5844 | 123.001 | 61.4537 | 61.5076 | 123.0484 | 61.4854 | 122.8449 | 61.5804 | 61.6026 | 61.4934 | 61.5156
446.5938 | 123.317 | -61.4868 | 61.6516 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.051737 | 61.6149 | 0.10669 | 61.5141 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3764 | 61.5125 | 61.4417 | 61.4748 | 61.4938 | 61.5322 | 61.4946 | 61.5386 | 123.1017 | 61.5935 | 123.001 | 61.4491 | 61.5167 | 123.0667 | 61.4945 | 122.8632 | 61.585 | 61.6072 | 61.4842 | 61.5064
447.5938 | 123.2483 | -61.4639 | 61.6608 | 0.025705 | -0.0451 | -0.012 | 0.011611 | 0.036265 | 0.00775 | 0.038003 | 61.6104 | 0.10669 | 61.5187 | -0.042259 | 0.034501 | 61.5799 | 0.003143 | 61.3718 | 61.4896 | 61.4188 | 61.4519 | 61.4755 | 61.5002 | 61.4717 | 61.5019 | 123.0743 | 61.5706 | 122.9826 | 61.4217 | 61.4984 | 123.0438 | 61.4671 | 122.8357 | 61.5759 | 61.6072 | 61.4842 | 61.5156
448.5938 | 123.349 | -61.4777 | 61.6562 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.049999 | 0.003172 | 0.042581 | 61.6104 | 0.10669 | 61.5233 | -0.03768 | 0.039079 | 61.5799 | -0.001436 | 61.3764 | 61.4942 | 61.4417 | 61.4657 | 61.4847 | 61.5277 | 61.4808 | 61.5202 | 123.088 | 61.5844 | 123.001 | 61.44 | 61.5167 | 123.0576 | 61.4762 | 122.8541 | 61.5713 | 61.6118 | 61.4842 | 61.5247
449.5938 | 123.3307 | -61.4914 | 61.6333 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6058 | 0.10669 | 61.5233 | -0.042259 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.5217 | 61.4555 | 61.4794 | 61.4984 | 61.5322 | 61.4991 | 61.534 | 123.0972 | 61.5981 | 123.0147 | 61.4491 | 61.5213 | 123.0713 | 61.4991 | 122.8632 | 61.5759 | 61.5981 | 61.4934 | 61.5156
450.5938 | 123.3032 | -61.4914 | 61.6379 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.00775 | 0.051737 | 61.6195 | 0.10211 | 61.5187 | -0.03768 | 0.029923 | 61.5707 | 0.003143 | 61.3627 | 61.5171 | 61.4509 | 61.4794 | 61.4984 | 61.5368 | 61.4991 | 61.5431 | 123.1109 | 61.5935 | 123.0101 | 61.4537 | 61.5213 | 123.0621 | 61.4945 | 122.8541 | 61.5896 | 61.6164 | 61.4888 | 61.5156
451.5938 | 123.3032 | -61.4868 | 61.6425 | 0.025705 | -0.0451 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.6149 | 0.097532 | 61.5233 | -0.042259 | 0.039079 | 61.5753 | -0.001436 | 61.3718 | 61.5125 | 61.4417 | 61.4702 | 61.4984 | 61.5277 | 61.4946 | 61.534 | 123.1017 | 61.5843 | 123.0101 | 61.4446 | 61.5259 | 123.0621 | 61.4854 | 122.8586 | 61.5759 | 61.6164 | 61.4842 | 61.5247
452.5938 | 123.3124 | -61.4594 | 61.6516 | 0.030283 | -0.0451 | -0.016578 | 0.011611 | 0.049999 | 0.00775 | 0.051737 | 61.6012 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5753 | -0.001436 | 61.3718 | 61.4896 | 61.4143 | 61.4428 | 61.471 | 61.5093 | 61.4671 | 61.5111 | 123.0606 | 61.566 | 122.9826 | 61.4262 | 61.4939 | 123.0347 | 61.4579 | 122.8312 | 61.5667 | 61.6026 | 61.4888 | 61.5247
453.5938 | 123.3124 | -61.4685 | 61.6699 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.045421 | 0.012329 | 0.042581 | 61.6149 | 0.10669 | 61.5279 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3672 | 61.4896 | 61.4234 | 61.4519 | 61.471 | 61.5139 | 61.4808 | 61.5111 | 123.0834 | 61.5752 | 122.9964 | 61.4354 | 61.4984 | 123.0484 | 61.4762 | 122.8357 | 61.585 | 61.6072 | 61.4979 | 61.5202
454.5938 | 123.2529 | -61.4731 | 61.6791 | 0.025705 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.003172 | 0.051737 | 61.6058 | 0.10669 | 61.5187 | -0.03768 | 0.039079 | 61.5707 | 0.007721 | 61.3764 | 61.4988 | 61.4371 | 61.4657 | 61.4847 | 61.5139 | 61.4763 | 61.5248 | 123.0789 | 61.5798 | 122.9918 | 61.4354 | 61.5122 | 123.0438 | 61.4808 | 122.8495 | 61.5667 | 61.5981 | 61.4796 | 61.511
455.5938 | 123.2437 | -61.4868 | 61.6653 | 0.021127 | -0.0451 | -0.007421 | 0.020768 | 0.040843 | 0.00775 | 0.042581 | 61.6058 | 0.10669 | 61.5187 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3627 | 61.5079 | 61.4417 | 61.4794 | 61.5076 | 61.5277 | 61.4946 | 61.5294 | 123.0926 | 61.5935 | 123.0055 | 61.4537 | 61.5213 | 123.0667 | 61.49 | 122.8495 | 61.5713 | 61.6026 | 61.4842 | 61.5156
456.5938 | 123.349 | -61.496 | 61.6562 | 0.021127 | -0.040521 | -0.021157 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6149 | 0.097532 | 61.5279 | -0.042259 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.5171 | 61.4555 | 61.4748 | 61.503 | 61.5368 | 61.5037 | 61.5386 | 123.1109 | 61.5935 | 123.0238 | 61.4537 | 61.5351 | 123.0759 | 61.5037 | 122.8678 | 61.5759 | 61.6072 | 61.4888 | 61.5202
457.5938 | 123.2162 | -61.496 | 61.647 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.047159 | 61.6104 | 0.10669 | 61.5187 | -0.042259 | 0.025345 | 61.5707 | 0.003143 | 61.3672 | 61.5217 | 61.4555 | 61.484 | 61.503 | 61.5368 | 61.5037 | 61.5431 | 123.1063 | 61.6027 | 123.0147 | 61.4537 | 61.5213 | 123.0667 | 61.4991 | 122.8632 | 61.585 | 61.6072 | 61.4934 | 61.5156
458.5938 | 123.3078 | -61.4822 | 61.6516 | 0.021127 | -0.049678 | -0.007421 | 0.007033 | 0.040843 | -0.001406 | 0.051737 | 61.6195 | 0.11127 | 61.5141 | -0.042259 | 0.039079 | 61.5753 | 0.012299 | 61.3672 | 61.5034 | 61.4326 | 61.4748 | 61.4893 | 61.5231 | 61.4808 | 61.534 | 123.1018 | 61.5935 | 122.9964 | 61.44 | 61.5213 | 123.0576 | 61.4945 | 122.8495 | 61.5804 | 61.6072 | 61.4751 | 61.5018
459.5938 | 123.2758 | -61.4822 | 61.647 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.051737 | 61.6149 | 0.10211 | 61.5187 | -0.033101 | 0.039079 | 61.5753 | 0.007721 | 61.3718 | 61.5079 | 61.4371 | 61.4702 | 61.4893 | 61.5277 | 61.4854 | 61.534 | 123.0972 | 61.5844 | 123.001 | 61.4491 | 61.5213 | 123.0576 | 61.49 | 122.8541 | 61.5759 | 61.6072 | 61.4796 | 61.511
460.5938 | 123.3078 | -61.496 | 61.6608 | 0.021127 | -0.049678 | -0.016578 | 0.007033 | 0.054577 | 0.00775 | 0.047159 | 61.6104 | 0.11585 | 61.5187 | -0.03768 | 0.029923 | 61.5753 | 0.007721 | 61.3764 | 61.5171 | 61.4463 | 61.4794 | 61.503 | 61.5505 | 61.5037 | 61.5431 | 123.1063 | 61.6118 | 123.0147 | 61.4583 | 61.5259 | 123.0713 | 61.5037 | 122.8724 | 61.5804 | 61.6026 | 61.4888 | 61.511
461.5938 | 123.262 | -61.4822 | 61.6699 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.049999 | 0.00775 | 0.051737 | 61.6104 | 0.10211 | 61.5141 | -0.042259 | 0.043657 | 61.5707 | 0.007721 | 61.3718 | 61.5079 | 61.4417 | 61.4657 | 61.4847 | 61.5322 | 61.49 | 61.534 | 123.0926 | 61.5844 | 122.9964 | 61.44 | 61.5259 | 123.053 | 61.49 | 122.8541 | 61.5667 | 61.6026 | 61.4705 | 61.5064
462.5938 | 123.3261 | -61.5005 | 61.6516 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.6058 | 0.097532 | 61.5187 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3581 | 61.5263 | 61.4554 | 61.484 | 61.5076 | 61.546 | 61.5037 | 61.5431 | 123.1063 | 61.5981 | 123.0193 | 61.4674 | 61.5396 | 123.0804 | 61.5037 | 122.8586 | 61.5667 | 61.6026 | 61.4796 | 61.5156
463.5938 | 123.3215 | -61.4777 | 61.6562 | 0.034862 | -0.040521 | -0.012 | 0.007033 | 0.049999 | 0.00775 | 0.047159 | 61.6104 | 0.11127 | 61.5187 | -0.033101 | 0.034501 | 61.5707 | 0.012299 | 61.3672 | 61.5125 | 61.4371 | 61.4657 | 61.4847 | 61.5277 | 61.4854 | 61.5248 | 123.088 | 61.5889 | 122.9964 | 61.4446 | 61.5122 | 123.0484 | 61.49 | 122.8449 | 61.5759 | 61.5981 | 61.4842 | 61.5064
464.5938 | 123.2986 | -61.4731 | 61.6425 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.045421 | 0.00775 | 0.047159 | 61.6195 | 0.11127 | 61.5187 | -0.03768 | 0.025345 | 61.5753 | 0.007721 | 61.3672 | 61.4988 | 61.4371 | 61.4611 | 61.4847 | 61.5185 | 61.4808 | 61.5202 | 123.0926 | 61.5844 | 122.9918 | 61.4354 | 61.4984 | 123.0484 | 61.4808 | 122.8403 | 61.5942 | 61.6118 | 61.4934 | 61.511
465.5938 | 123.2895 | -61.4685 | 61.6516 | 0.025705 | -0.040521 | -0.007421 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6195 | 0.10669 | 61.5324 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.4942 | 61.428 | 61.4611 | 61.4755 | 61.5093 | 61.4717 | 61.5202 | 123.088 | 61.5752 | 123.001 | 61.4354 | 61.4984 | 123.0484 | 61.4762 | 122.8403 | 61.5896 | 61.6118 | 61.5025 | 61.5247
466.5938 | 123.2895 | -61.4868 | 61.647 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.045421 | 0.012329 | 0.047159 | 61.6104 | 0.10211 | 61.5233 | -0.03768 | 0.029923 | 61.5753 | -0.001436 | 61.3718 | 61.5125 | 61.4509 | 61.4748 | 61.4984 | 61.5322 | 61.4991 | 61.534 | 123.0972 | 61.5889 | 123.0101 | 61.4491 | 61.5167 | 123.0621 | 61.4854 | 122.8586 | 61.5804 | 61.6118 | 61.4934 | 61.5247
467.5938 | 123.2803 | -61.4868 | 61.6608 | 0.025705 | -0.0451 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.6058 | 0.10211 | 61.5141 | -0.033101 | 0.029923 | 61.5845 | 0.007721 | 61.3718 | 61.5125 | 61.4417 | 61.4748 | 61.4984 | 61.5277 | 61.4946 | 61.534 | 123.0926 | 61.5889 | 123.001 | 61.4537 | 61.5167 | 123.0713 | 61.4945 | 122.8586 | 61.5759 | 61.5981 | 61.4842 | 61.5064
468.5938 | 123.2666 | -61.4822 | 61.647 | 0.025705 | -0.0451 | -0.012 | 0.01619 | 0.049999 | -0.001406 | 0.047159 | 61.6104 | 0.10211 | 61.5233 | -0.033101 | 0.029923 | 61.5662 | 0.003143 | 61.3672 | 61.5079 | 61.4371 | 61.4702 | 61.4984 | 61.5322 | 61.4808 | 61.5294 | 123.0926 | 61.5844 | 123.0055 | 61.4491 | 61.5122 | 123.0484 | 61.4854 | 122.8495 | 61.5804 | 61.6072 | 61.4934 | 61.5202
469.5938 | 123.2941 | -61.4822 | 61.6608 | 0.030283 | -0.040521 | -0.012 | 0.011611 | 0.045421 | 0.00775 | 0.047159 | 61.6195 | 0.10211 | 61.5233 | -0.042259 | 0.039079 | 61.5753 | 0.007721 | 61.3718 | 61.5125 | 61.4417 | 61.4702 | 61.4939 | 61.5277 | 61.49 | 61.5294 | 123.1018 | 61.5844 | 123.0055 | 61.44 | 61.5213 | 123.0576 | 61.49 | 122.8541 | 61.5804 | 61.6118 | 61.4842 | 61.5156
470.5938 | 123.2895 | -61.5005 | 61.6837 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.049999 | 0.00775 | 0.051737 | 61.6104 | 0.11127 | 61.5233 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3672 | 61.5308 | 61.46 | 61.484 | 61.5076 | 61.5505 | 61.5083 | 61.5523 | 123.1109 | 61.6118 | 123.0238 | 61.4674 | 61.535 | 123.085 | 61.5083 | 122.8678 | 61.5759 | 61.6026 | 61.4888 | 61.5156
471.5938 | 123.3215 | -61.4639 | 61.6653 | 0.021127 | -0.0451 | -0.007421 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.6104 | 0.10211 | 61.5279 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.3718 | 61.4851 | 61.4188 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.5111 | 123.0743 | 61.566 | 122.9918 | 61.4262 | 61.4984 | 123.0438 | 61.4625 | 122.8357 | 61.5759 | 61.6118 | 61.4934 | 61.5293
472.5938 | 123.2986 | -61.4731 | 61.647 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.045421 | 0.003172 | 0.042581 | 61.6195 | 0.10669 | 61.5187 | -0.033101 | 0.025345 | 61.5753 | 0.012299 | 61.3672 | 61.4988 | 61.428 | 61.4611 | 61.4755 | 61.5185 | 61.4763 | 61.5157 | 123.0926 | 61.5798 | 122.9918 | 61.44 | 61.4984 | 123.0484 | 61.4854 | 122.8403 | 61.5942 | 61.6072 | 61.4934 | 61.5064
473.5938 | 123.2895 | -61.496 | 61.6653 | 0.021127 | -0.040521 | -0.007421 | 0.007033 | 0.049999 | 0.00775 | 0.051737 | 61.6195 | 0.11585 | 61.5233 | -0.028522 | 0.034501 | 61.5753 | 0.012299 | 61.3718 | 61.5171 | 61.4555 | 61.4886 | 61.503 | 61.546 | 61.5037 | 61.5477 | 123.1155 | 61.6118 | 123.0193 | 61.4674 | 61.5305 | 123.0713 | 61.5083 | 122.8678 | 61.585 | 61.6072 | 61.4888 | 61.511
474.5938 | 123.2849 | -61.5005 | 61.6699 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6195 | 0.097532 | 61.5233 | -0.033101 | 0.034501 | 61.5707 | -0.001436 | 61.3718 | 61.5308 | 61.46 | 61.4794 | 61.5076 | 61.546 | 61.5037 | 61.5477 | 123.1201 | 61.5981 | 123.0238 | 61.4674 | 61.535 | 123.0713 | 61.4991 | 122.8724 | 61.585 | 61.6209 | 61.4888 | 61.5247
475.5938 | 123.262 | -61.4822 | 61.6791 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6058 | 0.11127 | 61.5279 | -0.028522 | 0.025345 | 61.5799 | -0.001436 | 61.3718 | 61.5034 | 61.4371 | 61.4657 | 61.4893 | 61.5231 | 61.49 | 61.5248 | 123.088 | 61.5935 | 123.0101 | 61.4537 | 61.5076 | 123.0621 | 61.4808 | 122.8541 | 61.5804 | 61.6072 | 61.5025 | 61.5293
476.5938 | 123.2666 | -61.4822 | 61.6608 | 0.025705 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.038003 | 61.6149 | 0.10211 | 61.5187 | -0.033101 | 0.025345 | 61.5753 | 0.007721 | 61.3627 | 61.5079 | 61.4417 | 61.4657 | 61.4939 | 61.5185 | 61.4854 | 61.5202 | 123.0972 | 61.5844 | 123.001 | 61.4491 | 61.5076 | 123.0576 | 61.49 | 122.8449 | 61.5896 | 61.6072 | 61.4934 | 61.511
477.5938 | 123.2941 | -61.4868 | 61.6562 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.042581 | 61.6058 | 0.10211 | 61.5187 | -0.042259 | 0.034501 | 61.5753 | 0.003143 | 61.3718 | 61.5079 | 61.4417 | 61.4748 | 61.4893 | 61.5231 | 61.4946 | 61.5294 | 123.0926 | 61.5889 | 123.0055 | 61.4446 | 61.5213 | 123.0621 | 61.49 | 122.8586 | 61.5713 | 61.6026 | 61.4842 | 61.5156
478.5938 | 123.3307 | -61.4685 | 61.6333 | 0.025705 | -0.049678 | -0.012 | -0.002124 | 0.036265 | -0.001406 | 0.051737 | 61.6149 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5845 | 0.003143 | 61.3672 | 61.4942 | 61.4188 | 61.4565 | 61.4664 | 61.5048 | 61.4671 | 61.5202 | 123.0834 | 61.5752 | 122.9918 | 61.4354 | 61.503 | 123.053 | 61.4716 | 122.8357 | 61.5804 | 61.6118 | 61.4888 | 61.5202
479.5938 | 123.3032 | -61.4685 | 61.6745 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6104 | 0.10211 | 61.5187 | -0.03768 | 0.039079 | 61.5799 | 0.007721 | 61.3764 | 61.4942 | 61.4234 | 61.4565 | 61.4755 | 61.5139 | 61.4717 | 61.5157 | 123.0789 | 61.5706 | 122.9872 | 61.4308 | 61.5076 | 123.0484 | 61.4762 | 122.8449 | 61.5713 | 61.6026 | 61.4796 | 61.511
480.5938 | 123.2941 | -61.4731 | 61.6699 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.040843 | -0.001406 | 0.047159 | 61.6104 | 0.10669 | 61.5233 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3764 | 61.4988 | 61.4371 | 61.4611 | 61.4847 | 61.5139 | 61.4717 | 61.5202 | 123.0834 | 61.5798 | 122.9964 | 61.4308 | 61.503 | 123.0484 | 61.4808 | 122.8495 | 61.5804 | 61.6026 | 61.4934 | 61.5156
481.5938 | 123.2712 | -61.4777 | 61.6562 | 0.021127 | -0.054257 | -0.012 | 0.002454 | 0.040843 | 0.00775 | 0.047159 | 61.6149 | 0.11127 | 61.5279 | -0.03768 | 0.039079 | 61.5753 | 0.012299 | 61.3672 | 61.4988 | 61.4234 | 61.4657 | 61.4801 | 61.5185 | 61.4854 | 61.5248 | 123.0926 | 61.5889 | 123.0055 | 61.44 | 61.5167 | 123.053 | 61.49 | 122.8449 | 61.5759 | 61.6026 | 61.4888 | 61.5156
482.5938 | 123.2529 | -61.4777 | 61.6653 | 0.025705 | -0.0451 | -0.007421 | 0.011611 | 0.040843 | 0.00775 | 0.051737 | 61.6149 | 0.10669 | 61.5279 | -0.042259 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.5034 | 61.4326 | 61.4702 | 61.4893 | 61.5185 | 61.4854 | 61.5294 | 123.0926 | 61.5844 | 123.0055 | 61.4354 | 61.5167 | 123.0576 | 61.4808 | 122.8449 | 61.5759 | 61.6118 | 61.4888 | 61.5247
483.5938 | 123.3444 | -61.4914 | 61.647 | 0.021127 | -0.0451 | -0.007421 | 0.002454 | 0.036265 | -0.001406 | 0.051737 | 61.6195 | 0.10669 | 61.5233 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.5125 | 61.4463 | 61.484 | 61.4938 | 61.5277 | 61.49 | 61.5431 | 123.1109 | 61.5981 | 123.0147 | 61.4583 | 61.5213 | 123.0713 | 61.4991 | 122.8632 | 61.5896 | 61.6118 | 61.4934 | 61.5156
484.5938 | 123.3032 | -61.5097 | 61.6608 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | -0.001406 | 0.051737 | 61.6104 | 0.11585 | 61.5233 | -0.033101 | 0.039079 | 61.5799 | 0.012299 | 61.3718 | 61.5354 | 61.4646 | 61.4977 | 61.5167 | 61.5551 | 61.5083 | 61.5614 | 123.1201 | 61.6256 | 123.033 | 61.4766 | 61.5488 | 123.0896 | 61.522 | 122.8815 | 61.5713 | 61.5981 | 61.4842 | 61.511
485.5938 | 123.3215 | -61.4685 | 61.6425 | 0.025705 | -0.049678 | -0.021157 | 0.002454 | 0.049999 | 0.003172 | 0.051737 | 61.6241 | 0.097532 | 61.5187 | -0.03768 | 0.029923 | 61.5707 | 0.007721 | 61.3718 | 61.4942 | 61.4188 | 61.4473 | 61.471 | 61.5185 | 61.4717 | 61.5202 | 123.0926 | 61.566 | 122.9872 | 61.4308 | 61.4984 | 123.0392 | 61.4762 | 122.8403 | 61.5942 | 61.6164 | 61.4888 | 61.511
486.5938 | 123.3078 | -61.4685 | 61.6516 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.047159 | 61.6241 | 0.11585 | 61.5233 | -0.033101 | 0.043657 | 61.5753 | 0.012299 | 61.3718 | 61.4988 | 61.428 | 61.4519 | 61.4755 | 61.5048 | 61.4717 | 61.5157 | 123.0926 | 61.5844 | 122.9918 | 61.4354 | 61.5122 | 123.0438 | 61.4808 | 122.8403 | 61.5804 | 61.6118 | 61.4796 | 61.511
487.5938 | 123.2895 | -61.4639 | 61.6882 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.051737 | 61.6149 | 0.10669 | 61.5187 | -0.042259 | 0.025345 | 61.5845 | 0.003143 | 61.3718 | 61.4851 | 61.4188 | 61.4519 | 61.471 | 61.5093 | 61.4671 | 61.5157 | 123.0789 | 61.5706 | 122.9826 | 61.4217 | 61.4893 | 123.0484 | 61.4671 | 122.8357 | 61.5896 | 61.6118 | 61.4934 | 61.5156
488.5938 | 123.2574 | -61.496 | 61.6562 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.047159 | 61.6195 | 0.11585 | 61.5233 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.5171 | 61.4555 | 61.484 | 61.503 | 61.5368 | 61.4991 | 61.5431 | 123.1155 | 61.6118 | 123.0193 | 61.4583 | 61.5305 | 123.0759 | 61.5037 | 122.8678 | 61.585 | 61.6118 | 61.4888 | 61.5156
489.5938 | 123.2574 | -61.5051 | 61.6608 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6149 | 0.10669 | 61.5233 | -0.028522 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.5308 | 61.46 | 61.4931 | 61.5122 | 61.5505 | 61.5083 | 61.5523 | 123.1201 | 61.6118 | 123.0284 | 61.4766 | 61.5442 | 123.0896 | 61.5083 | 122.8769 | 61.5759 | 61.6118 | 61.4842 | 61.5202
490.5938 | 123.3032 | -61.4822 | 61.6745 | 0.025705 | -0.040521 | -0.007421 | 0.011611 | 0.045421 | 0.003172 | 0.056315 | 61.6195 | 0.10669 | 61.5324 | -0.03768 | 0.034501 | 61.5707 | 0.003143 | 61.3627 | 61.5079 | 61.4417 | 61.4748 | 61.4939 | 61.5277 | 61.4854 | 61.5386 | 123.1018 | 61.5889 | 123.0147 | 61.4446 | 61.5167 | 123.053 | 61.4854 | 122.8449 | 61.585 | 61.6164 | 61.4979 | 61.5293
491.5938 | 123.317 | -61.5005 | 61.6791 | 0.025705 | -0.0451 | -0.012 | 0.01619 | 0.040843 | 0.00775 | 0.042581 | 61.6149 | 0.10669 | 61.5187 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.5263 | 61.4554 | 61.4885 | 61.5167 | 61.5414 | 61.5083 | 61.5431 | 123.1155 | 61.6072 | 123.0193 | 61.4674 | 61.5396 | 123.0804 | 61.5037 | 122.8678 | 61.5759 | 61.6118 | 61.4796 | 61.5156
492.5938 | 123.2986 | -61.4777 | 61.6425 | 0.030283 | -0.040521 | -0.021157 | 0.007033 | 0.040843 | 0.00775 | 0.051737 | 61.6195 | 0.11127 | 61.5233 | -0.033101 | 0.039079 | 61.5799 | -0.001436 | 61.3718 | 61.5079 | 61.4371 | 61.4565 | 61.4847 | 61.5185 | 61.4854 | 61.5294 | 123.0972 | 61.5889 | 123.001 | 61.4446 | 61.5167 | 123.0576 | 61.4762 | 122.8495 | 61.5804 | 61.6209 | 61.4842 | 61.5247
493.5938 | 123.2986 | -61.4731 | 61.6608 | 0.025705 | -0.040521 | -0.012 | 0.011611 | 0.049999 | 0.00775 | 0.047159 | 61.6149 | 0.097532 | 61.5279 | -0.033101 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.4988 | 61.4326 | 61.4611 | 61.4847 | 61.5231 | 61.4808 | 61.5202 | 123.088 | 61.5706 | 123.001 | 61.44 | 61.5076 | 123.0576 | 61.4716 | 122.8449 | 61.5804 | 61.6164 | 61.4934 | 61.5293
494.5938 | 123.2803 | -61.4731 | 61.6516 | 0.025705 | -0.049678 | -0.012 | 0.007033 | 0.049999 | -0.001406 | 0.047159 | 61.6149 | 0.10669 | 61.5096 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3672 | 61.4988 | 61.4234 | 61.4611 | 61.4801 | 61.5231 | 61.4717 | 61.5202 | 123.088 | 61.5798 | 122.9826 | 61.4354 | 61.503 | 123.053 | 61.4762 | 122.8403 | 61.585 | 61.6118 | 61.4796 | 61.5064
495.5938 | 123.2437 | -61.4731 | 61.6791 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.6149 | 0.10669 | 61.5141 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.4942 | 61.428 | 61.4565 | 61.4801 | 61.5185 | 61.4808 | 61.5157 | 123.088 | 61.5798 | 122.9872 | 61.44 | 61.5122 | 123.053 | 61.4808 | 122.8449 | 61.5759 | 61.6072 | 61.4751 | 61.5064
496.5938 | 123.2712 | -61.4914 | 61.6608 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.6104 | 0.11127 | 61.5141 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.5171 | 61.4509 | 61.4748 | 61.4984 | 61.5368 | 61.4991 | 61.534 | 123.1018 | 61.6027 | 123.0055 | 61.4491 | 61.5213 | 123.0667 | 61.4991 | 122.8586 | 61.5804 | 61.6026 | 61.4842 | 61.5064
497.5938 | 123.2803 | -61.5097 | 61.6425 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6149 | 0.097532 | 61.5233 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3627 | 61.5308 | 61.4646 | 61.4931 | 61.5167 | 61.5505 | 61.5129 | 61.5614 | 123.1246 | 61.6072 | 123.033 | 61.472 | 61.5396 | 123.0896 | 61.5128 | 122.8724 | 61.585 | 61.6118 | 61.4934 | 61.5202
498.5938 | 123.2346 | -61.5097 | 61.6699 | 0.025705 | -0.0451 | -0.021157 | 0.01619 | 0.040843 | 0.00775 | 0.042581 | 61.6195 | 0.10211 | 61.5233 | -0.042259 | 0.043657 | 61.5707 | 0.003143 | 61.3718 | 61.5354 | 61.4646 | 61.4885 | 61.5259 | 61.5505 | 61.5175 | 61.5523 | 123.1292 | 61.6118 | 123.033 | 61.4674 | 61.5534 | 123.0804 | 61.5128 | 122.8815 | 61.5759 | 61.6164 | 61.4796 | 61.5202
499.5938 | 123.2758 | -61.4868 | 61.6837 | 0.021127 | -0.040521 | -0.012 | 0.01619 | 0.040843 | 0.00775 | 0.038003 | 61.6241 | 0.10669 | 61.5187 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.5079 | 61.4463 | 61.4748 | 61.503 | 61.5277 | 61.4946 | 61.5248 | 123.1109 | 61.5935 | 123.0055 | 61.4537 | 61.5259 | 123.0667 | 61.49 | 122.8541 | 61.585 | 61.6209 | 61.4796 | 61.5156
500.5938 | 123.2208 | -61.5189 | 61.6562 | 0.021127 | -0.049678 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.042581 | 61.6149 | 0.10211 | 61.5233 | -0.03768 | 0.029923 | 61.5845 | 0.012299 | 61.3764 | 61.54 | 61.4692 | 61.5114 | 61.5213 | 61.5551 | 61.522 | 61.5614 | 123.1338 | 61.621 | 123.0422 | 61.4812 | 61.5488 | 123.1033 | 61.5312 | 122.8953 | 61.585 | 61.6026 | 61.4934 | 61.511
501.5938 | 123.2666 | -61.4777 | 61.6562 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.051737 | 61.6241 | 0.097532 | 61.5233 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3672 | 61.5079 | 61.4326 | 61.4657 | 61.4847 | 61.5185 | 61.4854 | 61.5294 | 123.1018 | 61.5752 | 123.001 | 61.44 | 61.5076 | 123.0576 | 61.4808 | 122.8449 | 61.5942 | 61.6209 | 61.4934 | 61.5202
502.5938 | 123.2712 | -61.5097 | 61.6562 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.6149 | 0.10669 | 61.5187 | -0.033101 | 0.029923 | 61.5753 | 0.003143 | 61.3627 | 61.5308 | 61.4692 | 61.4931 | 61.5167 | 61.5551 | 61.5175 | 61.5569 | 123.1246 | 61.6164 | 123.0284 | 61.4766 | 61.5396 | 123.085 | 61.5128 | 122.8724 | 61.585 | 61.6118 | 61.4888 | 61.5156
503.5938 | 123.3673 | -61.4685 | 61.6699 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.056315 | 61.6195 | 0.11127 | 61.5279 | -0.03768 | 0.034501 | 61.5799 | 0.012299 | 61.3718 | 61.4896 | 61.4234 | 61.4565 | 61.4755 | 61.5093 | 61.4717 | 61.5248 | 123.088 | 61.5798 | 122.9964 | 61.4308 | 61.503 | 123.0484 | 61.4808 | 122.8403 | 61.585 | 61.6072 | 61.4934 | 61.5156
504.5938 | 123.3353 | -61.4914 | 61.6745 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.040843 | -0.001406 | 0.047159 | 61.6104 | 0.11585 | 61.5324 | -0.033101 | 0.034501 | 61.5753 | 0.003143 | 61.3672 | 61.5125 | 61.4509 | 61.4702 | 61.4938 | 61.5322 | 61.49 | 61.5386 | 123.1018 | 61.6072 | 123.0238 | 61.4583 | 61.5259 | 123.0667 | 61.4945 | 122.8586 | 61.5759 | 61.6072 | 61.4979 | 61.5293
505.5938 | 123.2574 | -61.4822 | 61.6608 | 0.016548 | -0.0451 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.042581 | 61.6195 | 0.10211 | 61.5233 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3718 | 61.4988 | 61.4371 | 61.4702 | 61.4893 | 61.5185 | 61.49 | 61.5248 | 123.1018 | 61.5844 | 123.0055 | 61.4446 | 61.5167 | 123.0621 | 61.4854 | 122.8541 | 61.585 | 61.6164 | 61.4888 | 61.5202
506.5938 | 123.2712 | -61.4822 | 61.6562 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.045421 | -0.005985 | 0.042581 | 61.6149 | 0.10669 | 61.5141 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3627 | 61.5079 | 61.4371 | 61.4657 | 61.4893 | 61.5277 | 61.4763 | 61.5248 | 123.0972 | 61.5889 | 122.9964 | 61.4446 | 61.5213 | 123.0621 | 61.4854 | 122.8449 | 61.5759 | 61.6118 | 61.4751 | 61.511
507.5938 | 123.3627 | -61.4639 | 61.6058 | 0.016548 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6104 | 0.097532 | 61.5096 | -0.042259 | 0.029923 | 61.5845 | 0.007721 | 61.3764 | 61.4805 | 61.4188 | 61.4474 | 61.471 | 61.5048 | 61.4717 | 61.5065 | 123.0743 | 61.5615 | 122.9735 | 61.4217 | 61.4939 | 123.0484 | 61.4716 | 122.8403 | 61.5804 | 61.6026 | 61.4796 | 61.5018
508.5938 | 123.2941 | -61.4502 | 61.647 | 0.016548 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6149 | 0.10211 | 61.5233 | -0.033101 | 0.034501 | 61.5753 | 0.007721 | 61.3718 | 61.4667 | 61.4051 | 61.4336 | 61.4572 | 61.4865 | 61.4534 | 61.4928 | 123.0651 | 61.5523 | 122.9735 | 61.4171 | 61.4847 | 123.0255 | 61.4579 | 122.822 | 61.5804 | 61.6072 | 61.4888 | 61.5156
509.5938 | 123.4131 | -61.4548 | 61.615 | 0.01197 | -0.049678 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6104 | 0.11585 | 61.5187 | -0.03768 | 0.034501 | 61.5753 | -0.001436 | 61.3581 | 61.4667 | 61.4051 | 61.4382 | 61.4618 | 61.4956 | 61.4579 | 61.5065 | 123.0651 | 61.5706 | 122.9735 | 61.4171 | 61.4893 | 123.0301 | 61.4533 | 122.8129 | 61.5759 | 61.6118 | 61.4842 | 61.5202
510.5938 | 123.3948 | -61.5005 | 61.5601 | 0.021127 | -0.049678 | -0.016578 | 0.007033 | 0.036265 | -0.005985 | 0.047159 | 61.6149 | 0.10211 | 61.5233 | -0.033101 | 0.029923 | 61.5753 | 0.007721 | 61.3764 | 61.5217 | 61.4509 | 61.484 | 61.5076 | 61.5368 | 61.4946 | 61.5477 | 123.1155 | 61.6027 | 123.0238 | 61.4674 | 61.5305 | 123.0759 | 61.5083 | 122.8769 | 61.585 | 61.6072 | 61.4934 | 61.5156
511.5938 | 123.3673 | -61.4594 | 61.6013 | 0.021127 | -0.0451 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.042581 | 61.6149 | 0.10669 | 61.5279 | -0.028522 | 0.025345 | 61.5845 | 0.007721 | 61.3672 | 61.4805 | 61.4143 | 61.4428 | 61.471 | 61.5048 | 61.4625 | 61.5019 | 123.0743 | 61.566 | 122.9872 | 61.4308 | 61.4847 | 123.0438 | 61.4671 | 122.8266 | 61.5896 | 61.6072 | 61.5025 | 61.5202
512.5938 | 123.2712 | -61.4914 | 61.6241 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.051737 | 61.6149 | 0.10211 | 61.5187 | -0.033101 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.5171 | 61.4509 | 61.4794 | 61.4938 | 61.5277 | 61.4991 | 61.5431 | 123.1063 | 61.5935 | 123.0101 | 61.4583 | 61.5213 | 123.0667 | 61.4991 | 122.8586 | 61.585 | 61.6072 | 61.4888 | 61.511
513.5938 | 123.3765 | -61.4594 | 61.5967 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.045421 | 0.003172 | 0.047159 | 61.6195 | 0.10669 | 61.5187 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3718 | 61.4805 | 61.4188 | 61.4428 | 61.4618 | 61.5048 | 61.4625 | 61.5065 | 123.0789 | 61.566 | 122.9781 | 61.4217 | 61.4984 | 123.0392 | 61.4625 | 122.8312 | 61.5804 | 61.6164 | 61.4796 | 61.5156
514.5938 | 123.4314 | -61.4502 | 61.6379 | 0.021127 | -0.040521 | -0.021157 | 0.011611 | 0.045421 | -0.001406 | 0.042581 | 61.6104 | 0.11585 | 61.5233 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3672 | 61.4713 | 61.4097 | 61.429 | 61.4618 | 61.4956 | 61.4488 | 61.4928 | 123.0606 | 61.566 | 122.9735 | 61.4125 | 61.4801 | 123.0301 | 61.4533 | 122.8174 | 61.5804 | 61.6072 | 61.4934 | 61.5202
515.5938 | 123.3902 | -61.496 | 61.5921 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.6195 | 0.10211 | 61.5279 | -0.042259 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.5171 | 61.4555 | 61.4794 | 61.503 | 61.5414 | 61.4991 | 61.5386 | 123.1155 | 61.5981 | 123.0238 | 61.4537 | 61.5351 | 123.0804 | 61.5037 | 122.8586 | 61.5804 | 61.6118 | 61.4888 | 61.5202
516.5938 | 123.3856 | -61.4822 | 61.6104 | 0.021127 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.042581 | 61.6149 | 0.10211 | 61.5187 | -0.042259 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.5034 | 61.4417 | 61.4657 | 61.4939 | 61.5185 | 61.4854 | 61.5248 | 123.0972 | 61.5844 | 123.001 | 61.44 | 61.5213 | 123.0667 | 61.49 | 122.8449 | 61.5759 | 61.6072 | 61.4796 | 61.511
517.5938 | 123.4222 | -61.4502 | 61.6104 | 0.01197 | -0.0451 | -0.012 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.6149 | 0.097532 | 61.5096 | -0.033101 | 0.043657 | 61.5799 | 0.007721 | 61.3627 | 61.4622 | 61.4051 | 61.4382 | 61.4526 | 61.491 | 61.4534 | 61.4974 | 123.0651 | 61.5477 | 122.9598 | 61.4171 | 61.4939 | 123.0301 | 61.4579 | 122.8129 | 61.5713 | 61.6072 | 61.4659 | 61.5018
518.5938 | 123.3948 | -61.4456 | 61.6196 | 0.01197 | -0.0451 | -0.007421 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6195 | 0.10669 | 61.5141 | -0.033101 | 0.025345 | 61.5753 | 0.003143 | 61.3672 | 61.4576 | 61.4005 | 61.4382 | 61.4527 | 61.491 | 61.4488 | 61.4928 | 123.0651 | 61.5523 | 122.9598 | 61.4125 | 61.471 | 123.0209 | 61.4488 | 122.8129 | 61.5942 | 61.6164 | 61.4888 | 61.511
519.5938 | 123.4177 | -61.4548 | 61.5967 | 0.016548 | -0.054257 | -0.025735 | -0.002124 | 0.040843 | 0.003172 | 0.047159 | 61.6195 | 0.097532 | 61.5187 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3718 | 61.4713 | 61.4005 | 61.429 | 61.4526 | 61.4956 | 61.4579 | 61.5019 | 123.0743 | 61.5523 | 122.9735 | 61.4217 | 61.4893 | 123.0347 | 61.4579 | 122.8266 | 61.585 | 61.6164 | 61.4842 | 61.5156
520.5938 | 123.381 | -61.4227 | 61.6013 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.6287 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5845 | 0.012299 | 61.3718 | 61.4439 | 61.3776 | 61.4107 | 61.4298 | 61.4636 | 61.4259 | 61.4653 | 123.0514 | 61.5294 | 122.946 | 61.3896 | 61.4572 | 123.0072 | 61.435 | 122.7945 | 61.5942 | 61.6164 | 61.4888 | 61.511
521.5938 | 123.4131 | -61.4456 | 61.6333 | 0.01197 | -0.049678 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.6241 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5753 | -0.001436 | 61.3718 | 61.4576 | 61.3959 | 61.429 | 61.4481 | 61.4865 | 61.4488 | 61.4928 | 123.0697 | 61.5523 | 122.9689 | 61.4125 | 61.4801 | 123.0209 | 61.4442 | 122.8174 | 61.5896 | 61.6255 | 61.4888 | 61.5247
522.5938 | 123.3902 | -61.4502 | 61.6287 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6195 | 0.11127 | 61.5324 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.4713 | 61.4051 | 61.4382 | 61.4572 | 61.491 | 61.4534 | 61.5019 | 123.0697 | 61.5615 | 122.9826 | 61.4171 | 61.4847 | 123.0301 | 61.4533 | 122.8174 | 61.585 | 61.6164 | 61.4979 | 61.5293
523.5938 | 123.3444 | -61.4731 | 61.6333 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6195 | 0.11127 | 61.5233 | -0.042259 | 0.039079 | 61.5753 | 0.003143 | 61.3672 | 61.4988 | 61.428 | 61.4611 | 61.4801 | 61.5139 | 61.4808 | 61.5157 | 123.0926 | 61.5844 | 122.9964 | 61.4308 | 61.5122 | 123.0484 | 61.4762 | 122.8403 | 61.5804 | 61.6164 | 61.4842 | 61.5202
524.5938 | 123.3353 | -61.5005 | 61.6287 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.047159 | 61.6195 | 0.10669 | 61.5279 | -0.042259 | 0.034501 | 61.5799 | 0.007721 | 61.3627 | 61.5263 | 61.4554 | 61.484 | 61.5076 | 61.5322 | 61.5083 | 61.5477 | 123.1201 | 61.6072 | 123.0284 | 61.4583 | 61.535 | 123.0804 | 61.5083 | 122.8632 | 61.585 | 61.6118 | 61.4934 | 61.5202
525.5938 | 123.3444 | -61.4822 | 61.6013 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.003172 | 0.042581 | 61.6149 | 0.097532 | 61.5279 | -0.042259 | 0.029923 | 61.5891 | 0.003143 | 61.3672 | 61.5034 | 61.4371 | 61.4657 | 61.4893 | 61.5231 | 61.4854 | 61.5248 | 123.0972 | 61.5798 | 123.0101 | 61.44 | 61.5122 | 123.0713 | 61.4854 | 122.8495 | 61.585 | 61.6118 | 61.4979 | 61.5247
526.5938 | 123.4039 | -61.4914 | 61.6241 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.012329 | 0.042581 | 61.6149 | 0.10211 | 61.5187 | -0.03768 | 0.039079 | 61.5799 | -0.001436 | 61.3627 | 61.5125 | 61.4509 | 61.4748 | 61.4984 | 61.5277 | 61.5037 | 61.534 | 123.1063 | 61.5935 | 123.0101 | 61.4537 | 61.5305 | 123.0713 | 61.49 | 122.8541 | 61.5759 | 61.6164 | 61.4796 | 61.5202
527.5938 | 123.3719 | -61.4777 | 61.5875 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.047159 | 61.6058 | 0.11127 | 61.5141 | -0.033101 | 0.029923 | 61.5799 | 0.003143 | 61.3672 | 61.4988 | 61.4371 | 61.4611 | 61.4755 | 61.5185 | 61.4808 | 61.5248 | 123.0834 | 61.5889 | 122.9918 | 61.4446 | 61.5076 | 123.0576 | 61.4808 | 122.8449 | 61.5759 | 61.6026 | 61.4842 | 61.511
528.5938 | 123.3536 | -61.496 | 61.6013 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.6058 | 0.092954 | 61.5096 | -0.03768 | 0.034501 | 61.5845 | 0.007721 | 61.3718 | 61.5125 | 61.4555 | 61.484 | 61.4984 | 61.5322 | 61.4946 | 61.534 | 123.1017 | 61.5889 | 123.0055 | 61.4583 | 61.5305 | 123.0804 | 61.5037 | 122.8678 | 61.5713 | 61.5981 | 61.4751 | 61.5018
529.5938 | 123.3307 | -61.496 | 61.5921 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.045421 | 0.003172 | 0.051737 | 61.6058 | 0.097532 | 61.5233 | -0.03768 | 0.025345 | 61.5799 | 0.003143 | 61.3627 | 61.5125 | 61.4509 | 61.484 | 61.4984 | 61.5414 | 61.4991 | 61.5477 | 123.1017 | 61.5935 | 123.0193 | 61.4583 | 61.5213 | 123.0759 | 61.4991 | 122.8586 | 61.5804 | 61.6026 | 61.4979 | 61.5202
530.5938 | 123.3398 | -61.4914 | 61.5738 | 0.016548 | -0.0451 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.038003 | 61.6104 | 0.10669 | 61.5187 | -0.033101 | 0.025345 | 61.5799 | 0.003143 | 61.3718 | 61.5079 | 61.4463 | 61.4794 | 61.4984 | 61.5322 | 61.4946 | 61.5294 | 123.1018 | 61.5981 | 123.0101 | 61.4583 | 61.5167 | 123.0713 | 61.4945 | 122.8632 | 61.585 | 61.6072 | 61.4934 | 61.5156
531.5938 | 123.3673 | -61.4868 | 61.5738 | 0.030283 | -0.0451 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.042581 | 61.6149 | 0.11127 | 61.5187 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3627 | 61.5171 | 61.4417 | 61.4702 | 61.4847 | 61.5231 | 61.49 | 61.5294 | 123.1017 | 61.5981 | 123.0055 | 61.4491 | 61.5167 | 123.0667 | 61.4945 | 122.8495 | 61.585 | 61.6072 | 61.4888 | 61.511
532.5938 | 123.3307 | -61.4639 | 61.5784 | 0.025705 | -0.049678 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.6149 | 0.10669 | 61.5096 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.4896 | 61.4143 | 61.4474 | 61.4664 | 61.5048 | 61.4671 | 61.5111 | 123.0789 | 61.5706 | 122.9735 | 61.4262 | 61.4939 | 123.0438 | 61.4716 | 122.8357 | 61.585 | 61.6072 | 61.4796 | 61.5018
533.5938 | 123.3765 | -61.4914 | 61.6196 | 0.025705 | -0.049678 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6104 | 0.11127 | 61.5233 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3764 | 61.5171 | 61.4417 | 61.4794 | 61.4984 | 61.5368 | 61.4946 | 61.5386 | 123.1018 | 61.6027 | 123.0147 | 61.4583 | 61.5259 | 123.0713 | 61.4945 | 122.8678 | 61.5759 | 61.6072 | 61.4888 | 61.5202
534.5938 | 123.3582 | -61.4639 | 61.5875 | 0.016548 | -0.049678 | -0.021157 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.6149 | 0.11127 | 61.5233 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3581 | 61.4805 | 61.4143 | 61.4428 | 61.4664 | 61.5002 | 61.4625 | 61.5019 | 123.0789 | 61.5752 | 122.9872 | 61.4262 | 61.4984 | 123.0438 | 61.4671 | 122.822 | 61.5804 | 61.6118 | 61.4888 | 61.5202
535.5938 | 123.3765 | -61.4594 | 61.5738 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.040843 | -0.005985 | 0.042581 | 61.6149 | 0.12043 | 61.5233 | -0.028522 | 0.029923 | 61.5707 | -0.001436 | 61.3627 | 61.4805 | 61.4188 | 61.4519 | 61.4618 | 61.5002 | 61.4534 | 61.5019 | 123.0743 | 61.5798 | 122.9826 | 61.4308 | 61.4893 | 123.0301 | 61.4579 | 122.822 | 61.585 | 61.6164 | 61.4934 | 61.5247
536.5938 | 123.3994 | -61.4777 | 61.6013 | 0.021127 | -0.049678 | -0.012 | -0.002124 | 0.040843 | 0.003172 | 0.042581 | 61.6241 | 0.10669 | 61.5233 | -0.042259 | 0.029923 | 61.5753 | -0.001436 | 61.3627 | 61.4988 | 61.428 | 61.4657 | 61.4755 | 61.5185 | 61.4808 | 61.5202 | 123.1018 | 61.5844 | 123.001 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8403 | 61.5942 | 61.6255 | 61.4934 | 61.5247
537.5938 | 123.3719 | -61.4777 | 61.5967 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6149 | 0.11127 | 61.5233 | -0.03768 | 0.034501 | 61.5753 | 0.003143 | 61.3672 | 61.4988 | 61.4326 | 61.4657 | 61.4847 | 61.5231 | 61.4808 | 61.5248 | 123.0926 | 61.5889 | 123.001 | 61.44 | 61.5122 | 123.053 | 61.4808 | 122.8449 | 61.5804 | 61.6118 | 61.4888 | 61.5202
538.5938 | 123.317 | -61.4777 | 61.6196 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.056315 | 61.6195 | 0.097532 | 61.5187 | -0.042259 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.4942 | 61.4371 | 61.4657 | 61.4755 | 61.5093 | 61.4854 | 61.534 | 123.0972 | 61.5752 | 122.9964 | 61.4354 | 61.5076 | 123.053 | 61.4854 | 122.8449 | 61.5896 | 61.6118 | 61.4888 | 61.511
539.5938 | 123.381 | -61.4502 | 61.6058 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.00775 | 0.038003 | 61.6149 | 0.10669 | 61.5187 | -0.042259 | 0.029923 | 61.5845 | -0.001436 | 61.3672 | 61.4713 | 61.4051 | 61.4336 | 61.4572 | 61.4865 | 61.4579 | 61.4882 | 123.0651 | 61.5569 | 122.9689 | 61.4079 | 61.4801 | 123.0347 | 61.4488 | 122.8174 | 61.585 | 61.6164 | 61.4888 | 61.5202
540.5938 | 123.4314 | -61.4777 | 61.5463 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6104 | 0.10211 | 61.5187 | -0.046838 | 0.025345 | 61.5799 | 0.003143 | 61.3672 | 61.5034 | 61.4326 | 61.4657 | 61.4847 | 61.5231 | 61.4808 | 61.5248 | 123.088 | 61.5798 | 122.9964 | 61.4308 | 61.503 | 123.0576 | 61.4808 | 122.8449 | 61.585 | 61.6072 | 61.4934 | 61.5156
541.5938 | 123.2895 | -61.5189 | 61.5921 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6195 | 0.10669 | 61.5279 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.5491 | 61.4783 | 61.5069 | 61.5259 | 61.5643 | 61.522 | 61.566 | 123.1384 | 61.6255 | 123.0467 | 61.4858 | 61.5488 | 123.0988 | 61.5266 | 122.8907 | 61.5896 | 61.6118 | 61.4979 | 61.5202
542.5938 | 123.2986 | -61.4868 | 61.6058 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6149 | 0.10211 | 61.5233 | -0.033101 | 0.029923 | 61.5845 | 0.012299 | 61.3718 | 61.5079 | 61.4509 | 61.4702 | 61.4938 | 61.5277 | 61.4946 | 61.5294 | 123.1017 | 61.5889 | 123.0101 | 61.4537 | 61.5167 | 123.0713 | 61.4991 | 122.8586 | 61.585 | 61.6026 | 61.4934 | 61.511
543.5938 | 123.2758 | -61.5097 | 61.6241 | 0.030283 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6149 | 0.10211 | 61.5141 | -0.03768 | 0.025345 | 61.5753 | -0.001436 | 61.3672 | 61.54 | 61.4646 | 61.4931 | 61.5167 | 61.5505 | 61.5175 | 61.5523 | 123.1246 | 61.6118 | 123.0238 | 61.472 | 61.535 | 123.085 | 61.5083 | 122.8769 | 61.5896 | 61.6164 | 61.4888 | 61.5156
544.5938 | 123.3078 | -61.4868 | 61.6333 | 0.021127 | -0.0451 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.047159 | 61.6241 | 0.10669 | 61.5187 | -0.033101 | 0.025345 | 61.5753 | -0.001436 | 61.3764 | 61.5079 | 61.4417 | 61.4702 | 61.4984 | 61.5277 | 61.4946 | 61.534 | 123.1109 | 61.5935 | 123.0055 | 61.4537 | 61.5122 | 123.0621 | 61.4854 | 122.8632 | 61.5987 | 61.6255 | 61.4934 | 61.5202
545.5938 | 123.2758 | -61.496 | 61.6562 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.049999 | 0.012329 | 0.051737 | 61.6241 | 0.10669 | 61.5233 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3764 | 61.5125 | 61.4555 | 61.4794 | 61.503 | 61.546 | 61.5083 | 61.5477 | 123.1201 | 61.6027 | 123.0193 | 61.4629 | 61.5259 | 123.0759 | 61.5037 | 122.8724 | 61.5942 | 61.6164 | 61.4934 | 61.5156
546.5938 | 123.262 | -61.4777 | 61.6425 | 0.021127 | -0.0451 | -0.021157 | 0.011611 | 0.036265 | 0.003172 | 0.051737 | 61.6287 | 0.12043 | 61.537 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.4988 | 61.4326 | 61.4565 | 61.4893 | 61.5139 | 61.4808 | 61.5294 | 123.1063 | 61.5981 | 123.0147 | 61.44 | 61.5076 | 123.0576 | 61.4854 | 122.8495 | 61.5987 | 61.6209 | 61.5071 | 61.5293
547.5938 | 123.2574 | -61.4777 | 61.6425 | 0.021127 | -0.049678 | -0.016578 | 0.007033 | 0.045421 | -0.001406 | 0.047159 | 61.6241 | 0.097532 | 61.5279 | -0.033101 | 0.029923 | 61.5753 | -0.001436 | 61.3672 | 61.4988 | 61.428 | 61.4611 | 61.4847 | 61.5231 | 61.4763 | 61.5248 | 123.1018 | 61.5752 | 123.0055 | 61.4446 | 61.5076 | 123.053 | 61.4762 | 122.8449 | 61.5942 | 61.6255 | 61.4979 | 61.5293
548.5938 | 123.2712 | -61.5005 | 61.6333 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.6149 | 0.10669 | 61.5279 | -0.03768 | 0.025345 | 61.5753 | 0.003143 | 61.3672 | 61.5217 | 61.46 | 61.484 | 61.5076 | 61.5414 | 61.4991 | 61.5477 | 123.1155 | 61.6072 | 123.0284 | 61.4629 | 61.5259 | 123.0759 | 61.5037 | 122.8678 | 61.5896 | 61.6118 | 61.5025 | 61.5247
549.5938 | 123.3032 | -61.4731 | 61.6562 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.6195 | 0.11127 | 61.5187 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3764 | 61.4942 | 61.428 | 61.4565 | 61.4801 | 61.5139 | 61.4808 | 61.5157 | 123.0926 | 61.5844 | 122.9918 | 61.4354 | 61.503 | 123.053 | 61.4808 | 122.8495 | 61.5896 | 61.6118 | 61.4888 | 61.511
550.5938 | 123.2803 | -61.4685 | 61.6516 | 0.021127 | -0.049678 | -0.012 | 0.011611 | 0.040843 | 0.003172 | 0.042581 | 61.6195 | 0.11127 | 61.5416 | -0.033101 | 0.034501 | 61.5891 | 0.007721 | 61.3672 | 61.4896 | 61.4188 | 61.4565 | 61.4801 | 61.5093 | 61.4717 | 61.5111 | 123.088 | 61.5798 | 123.0101 | 61.4354 | 61.503 | 123.0576 | 61.4762 | 122.8357 | 61.585 | 61.6118 | 61.5071 | 61.5339
551.5938 | 123.2941 | -61.4731 | 61.6699 | 0.025705 | -0.049678 | -0.012 | 0.002454 | 0.040843 | -0.001406 | 0.051737 | 61.6195 | 0.10669 | 61.5141 | -0.028522 | 0.029923 | 61.5753 | 0.007721 | 61.3764 | 61.4988 | 61.4234 | 61.4611 | 61.4755 | 61.5139 | 61.4717 | 61.5248 | 123.0926 | 61.5798 | 122.9872 | 61.4446 | 61.503 | 123.0484 | 61.4808 | 122.8495 | 61.5896 | 61.6118 | 61.4842 | 61.5064
552.5938 | 123.2986 | -61.4639 | 61.6516 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.003172 | 0.051737 | 61.6149 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5707 | 0.003143 | 61.3764 | 61.4851 | 61.4234 | 61.4519 | 61.471 | 61.5048 | 61.4671 | 61.5157 | 123.0789 | 61.5706 | 122.9872 | 61.4308 | 61.4984 | 123.0347 | 61.4671 | 122.8403 | 61.5804 | 61.6118 | 61.4888 | 61.5202
553.5938 | 123.3124 | -61.4914 | 61.6425 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.045421 | -0.001406 | 0.047159 | 61.6241 | 0.10669 | 61.5324 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3718 | 61.5171 | 61.4463 | 61.4794 | 61.4984 | 61.5368 | 61.49 | 61.5386 | 123.1155 | 61.5981 | 123.0238 | 61.4537 | 61.5213 | 123.0759 | 61.4945 | 122.8632 | 61.5942 | 61.6209 | 61.5025 | 61.5293
554.5938 | 123.3307 | -61.5051 | 61.647 | 0.025705 | -0.049678 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.6195 | 0.10211 | 61.5233 | -0.03768 | 0.020767 | 61.5799 | -0.001436 | 61.3627 | 61.5308 | 61.4554 | 61.4885 | 61.5122 | 61.5505 | 61.5129 | 61.5523 | 123.1246 | 61.6072 | 123.0284 | 61.4674 | 61.5259 | 123.085 | 61.5037 | 122.8678 | 61.5987 | 61.6209 | 61.5025 | 61.5247
555.5938 | 123.3444 | -61.4822 | 61.6333 | 0.016548 | -0.0451 | -0.021157 | 0.007033 | 0.045421 | 0.003172 | 0.047159 | 61.6241 | 0.11127 | 61.5324 | -0.03768 | 0.034501 | 61.5753 | 0.007721 | 61.3718 | 61.4988 | 61.4371 | 61.4611 | 61.4893 | 61.5277 | 61.4854 | 61.5294 | 123.1063 | 61.5935 | 123.0147 | 61.4446 | 61.5167 | 123.0576 | 61.49 | 122.8541 | 61.5896 | 61.6164 | 61.4979 | 61.5247
556.5938 | 123.3261 | -61.4731 | 61.6241 | 0.021127 | -0.049678 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.047159 | 61.6287 | 0.11127 | 61.5187 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.3718 | 61.4942 | 61.4234 | 61.4565 | 61.4755 | 61.5093 | 61.4808 | 61.5202 | 123.1018 | 61.5844 | 122.9918 | 61.4354 | 61.5076 | 123.0621 | 61.4762 | 122.8449 | 61.5942 | 61.6255 | 61.4842 | 61.5156
557.5938 | 123.3078 | -61.4731 | 61.6745 | 0.025705 | -0.049678 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.042581 | 61.6241 | 0.11585 | 61.5324 | -0.03768 | 0.034501 | 61.5845 | 0.007721 | 61.3718 | 61.4988 | 61.4234 | 61.4565 | 61.4801 | 61.5185 | 61.4808 | 61.5157 | 123.0972 | 61.5889 | 123.0055 | 61.4354 | 61.5076 | 123.0576 | 61.4808 | 122.8449 | 61.5896 | 61.6164 | 61.4979 | 61.5247
558.5938 | 123.3078 | -61.4731 | 61.6653 | 0.030283 | -0.040521 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.042581 | 61.6241 | 0.11585 | 61.5279 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.5034 | 61.4326 | 61.4565 | 61.4847 | 61.5139 | 61.4808 | 61.5157 | 123.0972 | 61.5889 | 123.001 | 61.44 | 61.5122 | 123.053 | 61.4762 | 122.8403 | 61.585 | 61.6209 | 61.4888 | 61.5247
559.5938 | 123.2849 | -61.4914 | 61.6516 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.045421 | 0.003172 | 0.051737 | 61.6241 | 0.12043 | 61.5279 | -0.028522 | 0.039079 | 61.5845 | 0.003143 | 61.3764 | 61.5125 | 61.4509 | 61.4794 | 61.4984 | 61.5368 | 61.4946 | 61.5431 | 123.1155 | 61.6118 | 123.0193 | 61.4629 | 61.5305 | 123.0759 | 61.4945 | 122.8678 | 61.585 | 61.6209 | 61.4888 | 61.5247
560.5938 | 123.3261 | -61.4685 | 61.6516 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.045421 | 0.00775 | 0.038003 | 61.6195 | 0.11127 | 61.5233 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3718 | 61.4896 | 61.428 | 61.4519 | 61.4664 | 61.5139 | 61.4763 | 61.5065 | 123.088 | 61.5798 | 122.9918 | 61.4308 | 61.503 | 123.053 | 61.4716 | 122.8403 | 61.585 | 61.6164 | 61.4888 | 61.5202
561.5938 | 123.2986 | -61.4822 | 61.6425 | 0.030283 | -0.049678 | -0.016578 | 0.007033 | 0.045421 | 0.003172 | 0.042581 | 61.6195 | 0.10669 | 61.5187 | -0.028522 | 0.029923 | 61.5799 | -0.001436 | 61.3718 | 61.5125 | 61.4326 | 61.4657 | 61.4893 | 61.5277 | 61.4854 | 61.5248 | 123.1018 | 61.5889 | 123.001 | 61.4537 | 61.5122 | 123.0621 | 61.4808 | 122.8541 | 61.5896 | 61.6209 | 61.4888 | 61.5202
562.5938 | 123.3078 | -61.4868 | 61.6379 | 0.021127 | -0.0451 | -0.002842 | 0.002454 | 0.040843 | 0.00775 | 0.047159 | 61.6287 | 0.11127 | 61.5187 | -0.042259 | 0.034501 | 61.5753 | 0.003143 | 61.381 | 61.5079 | 61.4417 | 61.484 | 61.4893 | 61.5277 | 61.4946 | 61.534 | 123.1155 | 61.5981 | 123.0055 | 61.4446 | 61.5213 | 123.0621 | 61.49 | 122.8678 | 61.5942 | 61.6255 | 61.4842 | 61.5156
563.5938 | 123.2986 | -61.496 | 61.6516 | 0.025705 | -0.049678 | -0.007421 | 0.007033 | 0.045421 | 0.00775 | 0.047159 | 61.6241 | 0.12043 | 61.5279 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3764 | 61.5217 | 61.4463 | 61.4886 | 61.503 | 61.5414 | 61.5037 | 61.5431 | 123.1201 | 61.6164 | 123.0238 | 61.4629 | 61.5305 | 123.0759 | 61.4991 | 122.8724 | 61.5896 | 61.6209 | 61.4934 | 61.5247
564.5938 | 123.2803 | -61.4639 | 61.647 | 0.021127 | -0.040521 | -0.016578 | 0.011611 | 0.045421 | 0.003172 | 0.047159 | 61.6195 | 0.11585 | 61.5233 | -0.033101 | 0.034501 | 61.5753 | 0.007721 | 61.3627 | 61.4851 | 61.4234 | 61.4474 | 61.4755 | 61.5093 | 61.4671 | 61.5111 | 123.0834 | 61.5798 | 122.9872 | 61.4308 | 61.4984 | 123.0392 | 61.4716 | 122.8266 | 61.585 | 61.6118 | 61.4888 | 61.5156
565.5938 | 123.2712 | -61.4639 | 61.6745 | 0.034862 | -0.0451 | -0.021157 | 0.002454 | 0.049999 | -0.001406 | 0.047159 | 61.6241 | 0.11585 | 61.5279 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3764 | 61.4988 | 61.4188 | 61.4428 | 61.4664 | 61.5139 | 61.4625 | 61.5111 | 123.088 | 61.5798 | 122.9918 | 61.4308 | 61.503 | 123.0484 | 61.4671 | 122.8403 | 61.585 | 61.6209 | 61.4888 | 61.5247
566.5938 | 123.2529 | -61.4639 | 61.6837 | 0.021127 | -0.049678 | -0.021157 | 0.002454 | 0.040843 | 0.00775 | 0.038003 | 61.6149 | 0.11585 | 61.5233 | -0.03768 | 0.034501 | 61.5845 | 0.012299 | 61.3764 | 61.4851 | 61.4143 | 61.4428 | 61.4664 | 61.5048 | 61.4717 | 61.5019 | 123.0789 | 61.5798 | 122.9872 | 61.4262 | 61.4984 | 123.0484 | 61.4762 | 122.8403 | 61.5804 | 61.6026 | 61.4888 | 61.511
567.5938 | 123.3261 | -61.4685 | 61.647 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.045421 | 0.003172 | 0.047159 | 61.6241 | 0.11127 | 61.5279 | -0.03768 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.4896 | 61.4234 | 61.4565 | 61.4664 | 61.5139 | 61.4717 | 61.5157 | 123.0926 | 61.5798 | 122.9964 | 61.4308 | 61.4984 | 123.0438 | 61.4762 | 122.8357 | 61.5942 | 61.6164 | 61.4979 | 61.5202
568.5938 | 123.2529 | -61.5005 | 61.6196 | 0.030283 | -0.049678 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6241 | 0.10211 | 61.537 | -0.03768 | 0.029923 | 61.5845 | 0.012299 | 61.3718 | 61.5308 | 61.4509 | 61.484 | 61.5076 | 61.5414 | 61.4991 | 61.5431 | 123.1246 | 61.6027 | 123.0376 | 61.4629 | 61.5305 | 123.085 | 61.5128 | 122.8724 | 61.5942 | 61.6118 | 61.5071 | 61.5247
569.5938 | 123.3124 | -61.4685 | 61.6516 | 0.030283 | -0.049678 | -0.016578 | 0.007033 | 0.036265 | -0.001406 | 0.047159 | 61.6195 | 0.11127 | 61.5141 | -0.042259 | 0.034501 | 61.5753 | 0.007721 | 61.3718 | 61.4988 | 61.4188 | 61.4519 | 61.4755 | 61.5048 | 61.4671 | 61.5157 | 123.088 | 61.5798 | 122.9826 | 61.4262 | 61.503 | 123.0438 | 61.4762 | 122.8403 | 61.585 | 61.6118 | 61.4796 | 61.5064
570.5938 | 123.3032 | -61.4868 | 61.6333 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6241 | 0.11127 | 61.5187 | -0.042259 | 0.039079 | 61.5845 | 0.012299 | 61.3718 | 61.5079 | 61.4417 | 61.4748 | 61.4938 | 61.5277 | 61.4854 | 61.5294 | 123.1109 | 61.5981 | 123.0055 | 61.4446 | 61.5259 | 123.0713 | 61.4991 | 122.8586 | 61.585 | 61.6118 | 61.4796 | 61.5064
571.5938 | 123.2849 | -61.4868 | 61.6699 | 0.025705 | -0.049678 | -0.016578 | -0.002124 | 0.040843 | 0.003172 | 0.047159 | 61.6149 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.5125 | 61.4371 | 61.4702 | 61.4847 | 61.5277 | 61.49 | 61.534 | 123.1017 | 61.5935 | 123.0101 | 61.4537 | 61.5213 | 123.0667 | 61.49 | 122.8541 | 61.5804 | 61.6118 | 61.4888 | 61.5202
572.5938 | 123.2986 | -61.4731 | 61.6745 | 0.021127 | -0.054257 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.051737 | 61.6241 | 0.11585 | 61.5279 | -0.03768 | 0.039079 | 61.5799 | 0.007721 | 61.3627 | 61.4942 | 61.4188 | 61.4565 | 61.4755 | 61.5093 | 61.4808 | 61.5248 | 123.0972 | 61.5889 | 123.001 | 61.4354 | 61.5122 | 123.053 | 61.4808 | 122.8357 | 61.585 | 61.6164 | 61.4888 | 61.5202
573.5938 | 123.262 | -61.5143 | 61.6791 | 0.025705 | -0.049678 | -0.016578 | 0.011611 | 0.045421 | -0.005985 | 0.042581 | 61.6287 | 0.10211 | 61.5324 | -0.03768 | 0.034501 | 61.5845 | 0.007721 | 61.3718 | 61.54 | 61.4646 | 61.4977 | 61.5259 | 61.5597 | 61.5083 | 61.5569 | 123.143 | 61.6164 | 123.0467 | 61.4766 | 61.5488 | 123.0988 | 61.522 | 122.8861 | 61.5942 | 61.6209 | 61.4979 | 61.5247
574.5938 | 123.3032 | -61.5051 | 61.6791 | 0.021127 | -0.049678 | -0.016578 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.6195 | 0.10211 | 61.5279 | -0.042259 | 0.039079 | 61.5799 | 0.012299 | 61.3627 | 61.5263 | 61.4554 | 61.4885 | 61.5076 | 61.546 | 61.5083 | 61.5523 | 123.1246 | 61.6072 | 123.033 | 61.4629 | 61.5442 | 123.085 | 61.5174 | 122.8678 | 61.5804 | 61.6072 | 61.4888 | 61.5156
575.5938 | 123.3307 | -61.4731 | 61.6653 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6195 | 0.10211 | 61.5187 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3718 | 61.4988 | 61.428 | 61.4565 | 61.4801 | 61.5093 | 61.4763 | 61.5111 | 123.0926 | 61.5752 | 122.9918 | 61.4354 | 61.503 | 123.053 | 61.4762 | 122.8449 | 61.5896 | 61.6164 | 61.4888 | 61.5156
576.5938 | 123.317 | -61.5005 | 61.6608 | 0.016548 | -0.049678 | -0.021157 | 0.002454 | 0.040843 | 0.003172 | 0.047159 | 61.6241 | 0.11127 | 61.5233 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3627 | 61.5171 | 61.4509 | 61.4794 | 61.503 | 61.5414 | 61.5037 | 61.5477 | 123.1246 | 61.6118 | 123.0238 | 61.4629 | 61.535 | 123.0804 | 61.5083 | 122.8632 | 61.5896 | 61.6164 | 61.4888 | 61.5156
577.5938 | 123.2895 | -61.4914 | 61.6791 | 0.030283 | -0.049678 | -0.012 | 0.007033 | 0.036265 | -0.001406 | 0.042581 | 61.6241 | 0.11127 | 61.5279 | -0.042259 | 0.025345 | 61.5845 | 0.003143 | 61.3672 | 61.5217 | 61.4417 | 61.4794 | 61.4984 | 61.5277 | 61.49 | 61.534 | 123.1155 | 61.6027 | 123.0193 | 61.4491 | 61.5167 | 123.0759 | 61.4945 | 122.8586 | 61.5987 | 61.6209 | 61.5025 | 61.5247
578.5938 | 123.2849 | -61.4777 | 61.6653 | 0.016548 | -0.0451 | -0.021157 | 0.007033 | 0.036265 | -0.001406 | 0.047159 | 61.6241 | 0.11585 | 61.537 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.4942 | 61.4326 | 61.4565 | 61.4847 | 61.5139 | 61.4763 | 61.5248 | 123.1018 | 61.5935 | 123.0147 | 61.4446 | 61.5167 | 123.0576 | 61.4854 | 122.8495 | 61.585 | 61.6164 | 61.4979 | 61.5293
579.5938 | 123.2437 | -61.5143 | 61.6653 | 0.021127 | -0.049678 | -0.021157 | 0.011611 | 0.036265 | -0.001406 | 0.042581 | 61.6241 | 0.10211 | 61.5187 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.5354 | 61.4646 | 61.4931 | 61.5259 | 61.5505 | 61.5129 | 61.5569 | 123.1384 | 61.6164 | 123.033 | 61.4766 | 61.5534 | 123.0988 | 61.522 | 122.8769 | 61.585 | 61.6164 | 61.4796 | 61.511
580.5938 | 123.2437 | -61.5234 | 61.6745 | 0.025705 | -0.0451 | -0.012 | 0.01619 | 0.045421 | 0.003172 | 0.047159 | 61.6241 | 0.11127 | 61.5233 | -0.033101 | 0.034501 | 61.5845 | 0.003143 | 61.3672 | 61.5491 | 61.4783 | 61.5114 | 61.5396 | 61.5689 | 61.5266 | 61.5706 | 123.1475 | 61.6347 | 123.0467 | 61.4903 | 61.5579 | 123.1079 | 61.5266 | 122.8907 | 61.5896 | 61.6209 | 61.4888 | 61.5202
581.5938 | 123.3078 | -61.5005 | 61.6699 | 0.021127 | -0.049678 | -0.012 | 0.007033 | 0.040843 | -0.001406 | 0.047159 | 61.6287 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5753 | 0.012299 | 61.3672 | 61.5217 | 61.4509 | 61.4885 | 61.5076 | 61.5414 | 61.4991 | 61.5477 | 123.1292 | 61.6072 | 123.0238 | 61.4674 | 61.535 | 123.0759 | 61.5128 | 122.8678 | 61.5942 | 61.6164 | 61.4888 | 61.511
582.5938 | 123.2666 | -61.5051 | 61.702 | 0.016548 | -0.0451 | -0.021157 | -0.002124 | 0.036265 | -0.001406 | 0.042581 | 61.6287 | 0.11585 | 61.5233 | -0.033101 | 0.029923 | 61.5845 | 0.007721 | 61.3627 | 61.5217 | 61.46 | 61.484 | 61.503 | 61.5414 | 61.5037 | 61.5477 | 123.1338 | 61.621 | 123.0284 | 61.472 | 61.535 | 123.0896 | 61.5128 | 122.8678 | 61.5987 | 61.6209 | 61.4934 | 61.5156
583.5938 | 123.2849 | -61.4914 | 61.6882 | 0.021127 | -0.049678 | -0.016578 | 0.007033 | 0.045421 | -0.001406 | 0.047159 | 61.6195 | 0.11585 | 61.5279 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.5125 | 61.4417 | 61.4748 | 61.4984 | 61.5368 | 61.49 | 61.5386 | 123.1109 | 61.6072 | 123.0193 | 61.4583 | 61.5259 | 123.0713 | 61.4991 | 122.8632 | 61.585 | 61.6118 | 61.4934 | 61.5202
584.5938 | 123.2666 | -61.4777 | 61.6333 | 0.030283 | -0.0451 | -0.021157 | 0.002454 | 0.036265 | -0.001406 | 0.047159 | 61.6195 | 0.10669 | 61.5279 | -0.03768 | 0.039079 | 61.5891 | 0.003143 | 61.3581 | 61.5079 | 61.4326 | 61.4565 | 61.4801 | 61.5139 | 61.4763 | 61.5248 | 123.0972 | 61.5844 | 123.0055 | 61.44 | 61.5167 | 123.0667 | 61.4808 | 122.8357 | 61.5804 | 61.6164 | 61.4888 | 61.5247
585.5938 | 123.3261 | -61.4685 | 61.6516 | 0.016548 | -0.049678 | -0.007421 | 0.007033 | 0.036265 | 0.00775 | 0.047159 | 61.6241 | 0.11127 | 61.5279 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3718 | 61.4851 | 61.4188 | 61.4611 | 61.4755 | 61.5048 | 61.4763 | 61.5157 | 123.0926 | 61.5798 | 122.9964 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8403 | 61.585 | 61.6164 | 61.4888 | 61.5202
586.5938 | 123.2941 | -61.4273 | 61.6058 | 0.021127 | -0.049678 | -0.025735 | -0.002124 | 0.036265 | -0.005985 | 0.047159 | 61.6287 | 0.10669 | 61.5141 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.4484 | 61.3776 | 61.4016 | 61.4252 | 61.4636 | 61.4213 | 61.4745 | 123.056 | 61.534 | 122.9414 | 61.3896 | 61.4618 | 123.0072 | 61.435 | 122.7991 | 61.5942 | 61.6209 | 61.4796 | 61.5064
587.5938 | 123.3765 | -61.4639 | 61.6196 | 0.021127 | -0.054257 | -0.021157 | -0.006703 | 0.031687 | 0.003172 | 0.038003 | 61.6195 | 0.10211 | 61.537 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3764 | 61.4851 | 61.4097 | 61.4428 | 61.4572 | 61.4956 | 61.4671 | 61.5019 | 123.0834 | 61.566 | 123.001 | 61.4308 | 61.503 | 123.0438 | 61.4671 | 122.8403 | 61.5804 | 61.6164 | 61.4979 | 61.5339
588.5938 | 123.3856 | -61.4639 | 61.6104 | 0.021127 | -0.054257 | -0.021157 | 0.007033 | 0.045421 | -0.001406 | 0.042581 | 61.6195 | 0.11585 | 61.5233 | -0.033101 | 0.029923 | 61.5845 | 0.007721 | 61.3718 | 61.4851 | 61.4097 | 61.4428 | 61.471 | 61.5093 | 61.4625 | 61.5065 | 123.0834 | 61.5798 | 122.9872 | 61.4308 | 61.4939 | 123.0484 | 61.4716 | 122.8357 | 61.5896 | 61.6118 | 61.4934 | 61.5156
589.5938 | 123.4222 | -61.4548 | 61.6104 | 0.021127 | -0.054257 | -0.021157 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6195 | 0.10669 | 61.5324 | -0.042259 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.4759 | 61.4005 | 61.4336 | 61.4618 | 61.491 | 61.4579 | 61.4928 | 123.0743 | 61.5615 | 122.9872 | 61.4125 | 61.4893 | 123.0347 | 61.4625 | 122.822 | 61.585 | 61.6118 | 61.4979 | 61.5247
590.5938 | 123.3582 | -61.4731 | 61.615 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.047159 | 61.6195 | 0.11585 | 61.5324 | -0.033101 | 0.043657 | 61.5891 | 0.003143 | 61.3672 | 61.4942 | 61.428 | 61.4565 | 61.4755 | 61.5093 | 61.4671 | 61.5202 | 123.0926 | 61.5889 | 123.0055 | 61.44 | 61.5167 | 123.0621 | 61.4762 | 122.8403 | 61.5759 | 61.6164 | 61.4888 | 61.5293
591.5938 | 123.381 | -61.4456 | 61.6425 | 0.016548 | -0.054257 | -0.016578 | 0.002454 | 0.040843 | -0.001406 | 0.038003 | 61.6287 | 0.12043 | 61.5324 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3627 | 61.4622 | 61.3914 | 61.429 | 61.4481 | 61.4865 | 61.4442 | 61.4836 | 123.0743 | 61.566 | 122.9781 | 61.4079 | 61.4755 | 123.0255 | 61.4488 | 122.8083 | 61.5987 | 61.6255 | 61.5025 | 61.5293
592.5938 | 123.3719 | -61.4914 | 61.6287 | 0.016548 | -0.049678 | -0.021157 | -0.002124 | 0.040843 | -0.001406 | 0.033424 | 61.6241 | 0.11585 | 61.5324 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3672 | 61.5079 | 61.4417 | 61.4702 | 61.4893 | 61.5322 | 61.49 | 61.5248 | 123.1155 | 61.6072 | 123.0238 | 61.4537 | 61.5213 | 123.0713 | 61.4991 | 122.8586 | 61.5942 | 61.6164 | 61.5025 | 61.5247
593.5938 | 123.3398 | -61.4914 | 61.615 | 0.016548 | -0.049678 | -0.021157 | 0.007033 | 0.049999 | 0.003172 | 0.042581 | 61.6149 | 0.12043 | 61.537 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3581 | 61.5079 | 61.4417 | 61.4702 | 61.4984 | 61.5414 | 61.4946 | 61.534 | 123.1063 | 61.6118 | 123.0284 | 61.4537 | 61.5259 | 123.0759 | 61.4945 | 122.8495 | 61.5804 | 61.6118 | 61.5025 | 61.5339
594.5938 | 123.3765 | -61.4502 | 61.6241 | 0.021127 | -0.054257 | -0.021157 | 0.002454 | 0.045421 | -0.005985 | 0.038003 | 61.6149 | 0.11585 | 61.5462 | -0.028522 | 0.034501 | 61.5845 | 0.012299 | 61.3672 | 61.4713 | 61.3959 | 61.429 | 61.4526 | 61.4956 | 61.4442 | 61.4882 | 123.0651 | 61.566 | 122.9964 | 61.4217 | 61.4847 | 123.0347 | 61.4625 | 122.8174 | 61.5804 | 61.6026 | 61.5117 | 61.5339
595.5938 | 123.3353 | -61.4777 | 61.6058 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.040843 | -0.005985 | 0.038003 | 61.6195 | 0.11127 | 61.5279 | -0.033101 | 0.029923 | 61.5753 | 0.007721 | 61.3718 | 61.4942 | 61.4326 | 61.4657 | 61.4755 | 61.5185 | 61.4717 | 61.5157 | 123.0972 | 61.5889 | 123.0055 | 61.4446 | 61.5076 | 123.053 | 61.4854 | 122.8495 | 61.5896 | 61.6118 | 61.4979 | 61.5202
596.5938 | 123.3765 | -61.4685 | 61.5921 | 0.021127 | -0.049678 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.038003 | 61.6241 | 0.10669 | 61.5324 | -0.042259 | 0.025345 | 61.5753 | 0.012299 | 61.3672 | 61.4896 | 61.4188 | 61.4473 | 61.471 | 61.5048 | 61.4717 | 61.5065 | 123.0926 | 61.5752 | 123.001 | 61.4262 | 61.4939 | 123.0438 | 61.4808 | 122.8357 | 61.5987 | 61.6118 | 61.5071 | 61.5202
597.5938 | 123.3582 | -61.496 | 61.6058 | 0.030283 | -0.049678 | -0.021157 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.6241 | 0.10669 | 61.5187 | -0.033101 | 0.039079 | 61.5799 | -0.001436 | 61.3718 | 61.5263 | 61.4463 | 61.4748 | 61.4984 | 61.5231 | 61.4946 | 61.5294 | 123.1201 | 61.6027 | 123.0147 | 61.4629 | 61.5351 | 123.0759 | 61.4945 | 122.8678 | 61.585 | 61.6255 | 61.4796 | 61.5202
598.5938 | 123.2437 | -61.4914 | 61.6791 | 0.025705 | -0.054257 | -0.016578 | -0.006703 | 0.031687 | -0.001406 | 0.033424 | 61.6287 | 0.10211 | 61.5233 | -0.03768 | 0.029923 | 61.5845 | 0.007721 | 61.3718 | 61.5171 | 61.4371 | 61.4748 | 61.4847 | 61.5231 | 61.49 | 61.5248 | 123.1201 | 61.5935 | 123.0147 | 61.4537 | 61.5213 | 123.0759 | 61.4991 | 122.8632 | 61.5987 | 61.6209 | 61.4934 | 61.5156
599.5938 | 123.3444 | -61.4914 | 61.5921 | 0.016548 | -0.0451 | -0.025735 | 0.002454 | 0.040843 | 0.003172 | 0.038003 | 61.6195 | 0.11127 | 61.5187 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3764 | 61.5079 | 61.4463 | 61.4657 | 61.4938 | 61.5322 | 61.4946 | 61.5294 | 123.1109 | 61.6027 | 123.0101 | 61.4537 | 61.5259 | 123.0713 | 61.4991 | 122.8678 | 61.585 | 61.6118 | 61.4842 | 61.511
600.5938 | 123.381 | -61.4868 | 61.6058 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.038003 | 61.6149 | 0.11127 | 61.5187 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.3672 | 61.5171 | 61.4417 | 61.4748 | 61.4893 | 61.5185 | 61.49 | 61.5248 | 123.1017 | 61.5981 | 123.0055 | 61.4491 | 61.5213 | 123.0667 | 61.4854 | 122.8541 | 61.5804 | 61.6164 | 61.4842 | 61.5202
601.5938 | 123.3627 | -61.4777 | 61.5921 | 0.025705 | -0.0451 | -0.021157 | -0.006703 | 0.040843 | -0.005985 | 0.038003 | 61.6195 | 0.11585 | 61.5233 | -0.033101 | 0.034501 | 61.5891 | 0.007721 | 61.3672 | 61.5034 | 61.4326 | 61.4565 | 61.471 | 61.5185 | 61.4717 | 61.5157 | 123.0972 | 61.5935 | 123.001 | 61.4446 | 61.5122 | 123.0667 | 61.4854 | 122.8449 | 61.585 | 61.6118 | 61.4888 | 61.5156
602.5938 | 123.4085 | -61.4731 | 61.5784 | 0.016548 | -0.049678 | -0.025735 | -0.006703 | 0.031687 | -0.001406 | 0.042581 | 61.6287 | 0.10211 | 61.5279 | -0.03768 | 0.025345 | 61.5799 | 0.012299 | 61.3627 | 61.4896 | 61.4234 | 61.4473 | 61.4664 | 61.5048 | 61.4717 | 61.5157 | 123.1018 | 61.5752 | 123.001 | 61.4354 | 61.4984 | 123.053 | 61.4854 | 122.8357 | 61.6033 | 61.6164 | 61.5025 | 61.5156
603.5938 | 123.262 | -61.4685 | 61.6653 | 0.021127 | -0.054257 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.033424 | 61.6287 | 0.10669 | 61.5324 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.381 | 61.4896 | 61.4142 | 61.4519 | 61.471 | 61.5048 | 61.4625 | 61.5019 | 123.0972 | 61.5752 | 123.001 | 61.4354 | 61.5076 | 123.053 | 61.4716 | 122.8495 | 61.5896 | 61.6255 | 61.4934 | 61.5293
604.5938 | 123.3673 | -61.4868 | 61.6058 | 0.021127 | -0.049678 | -0.021157 | 0.002454 | 0.031687 | 0.003172 | 0.042581 | 61.6241 | 0.10211 | 61.5279 | -0.033101 | 0.025345 | 61.5845 | 0.007721 | 61.3627 | 61.5079 | 61.4371 | 61.4657 | 61.4893 | 61.5185 | 61.49 | 61.5294 | 123.1109 | 61.5889 | 123.0147 | 61.4537 | 61.5122 | 123.0713 | 61.4945 | 122.8495 | 61.5987 | 61.6164 | 61.5025 | 61.5202
605.5938 | 123.3994 | -61.4777 | 61.5692 | 0.021127 | -0.0451 | -0.021157 | 0.002454 | 0.031687 | -0.001406 | 0.038003 | 61.6195 | 0.10211 | 61.5187 | -0.03768 | 0.039079 | 61.5891 | 0.007721 | 61.3718 | 61.4988 | 61.4326 | 61.4565 | 61.4801 | 61.5093 | 61.4763 | 61.5157 | 123.0972 | 61.5798 | 122.9964 | 61.44 | 61.5167 | 123.0667 | 61.4854 | 122.8495 | 61.5804 | 61.6118 | 61.4796 | 61.511
606.5938 | 123.3673 | -61.4548 | 61.5967 | 0.016548 | -0.049678 | -0.021157 | 0.002454 | 0.036265 | -0.001406 | 0.038003 | 61.6195 | 0.10669 | 61.5233 | -0.042259 | 0.029923 | 61.5845 | 0.007721 | 61.3627 | 61.4713 | 61.4051 | 61.4336 | 61.4572 | 61.491 | 61.4534 | 61.4928 | 123.0743 | 61.5615 | 122.9781 | 61.4125 | 61.4847 | 123.0392 | 61.4625 | 122.8174 | 61.5896 | 61.6118 | 61.4934 | 61.5156
607.5938 | 123.3078 | -61.5051 | 61.6196 | 0.021127 | -0.049678 | -0.016578 | 0.007033 | 0.040843 | -0.001406 | 0.042581 | 61.6241 | 0.10211 | 61.5141 | -0.042259 | 0.034501 | 61.5799 | -0.001436 | 61.3718 | 61.5263 | 61.4554 | 61.4885 | 61.5122 | 61.546 | 61.5037 | 61.5477 | 123.1292 | 61.6072 | 123.0193 | 61.4629 | 61.5396 | 123.085 | 61.5037 | 122.8769 | 61.5896 | 61.6255 | 61.4796 | 61.5156
608.5938 | 123.2391 | -61.4777 | 61.6562 | 0.021127 | -0.049678 | -0.025735 | 0.002454 | 0.031687 | -0.001406 | 0.047159 | 61.6287 | 0.11127 | 61.5233 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.4988 | 61.428 | 61.4519 | 61.4801 | 61.5093 | 61.4763 | 61.5248 | 123.1063 | 61.5889 | 123.001 | 61.44 | 61.5167 | 123.0576 | 61.4808 | 122.8449 | 61.5896 | 61.6255 | 61.4842 | 61.5202
609.5938 | 123.4863 | -61.4685 | 61.5738 | 0.01197 | -0.054257 | -0.021157 | 0.002454 | 0.040843 | -0.010563 | 0.033424 | 61.6195 | 0.10211 | 61.5187 | -0.042259 | 0.029923 | 61.5799 | -0.001436 | 61.3672 | 61.4805 | 61.4142 | 61.4473 | 61.471 | 61.5093 | 61.4579 | 61.5019 | 123.088 | 61.5706 | 122.9872 | 61.4262 | 61.4984 | 123.0484 | 61.4671 | 122.8357 | 61.5896 | 61.6209 | 61.4888 | 61.5202
610.5938 | 123.4039 | -61.4914 | 61.5875 | 0.030283 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.042581 | 61.6287 | 0.10669 | 61.5233 | -0.042259 | 0.034501 | 61.5845 | 0.003143 | 61.3672 | 61.5217 | 61.4509 | 61.4748 | 61.4984 | 61.5277 | 61.4946 | 61.534 | 123.1201 | 61.5981 | 123.0147 | 61.4491 | 61.5259 | 123.0759 | 61.4945 | 122.8586 | 61.5942 | 61.6255 | 61.4888 | 61.5202
611.5938 | 123.3627 | -61.5005 | 61.5921 | 0.021127 | -0.058836 | -0.016578 | 0.002454 | 0.031687 | -0.005985 | 0.042581 | 61.6287 | 0.11127 | 61.5233 | -0.023943 | 0.034501 | 61.5845 | 0.003143 | 61.3627 | 61.5217 | 61.4417 | 61.484 | 61.503 | 61.5322 | 61.4946 | 61.5431 | 123.1292 | 61.6118 | 123.0238 | 61.4766 | 61.535 | 123.085 | 61.5037 | 122.8632 | 61.5942 | 61.6255 | 61.4888 | 61.5202
612.5938 | 123.3215 | -61.496 | 61.6241 | 0.021127 | -0.0451 | -0.021157 | 0.002454 | 0.031687 | 0.003172 | 0.038003 | 61.6287 | 0.11127 | 61.5324 | -0.033101 | 0.029923 | 61.5845 | 0.003143 | 61.3672 | 61.5171 | 61.4509 | 61.4748 | 61.4984 | 61.5277 | 61.4991 | 61.534 | 123.1246 | 61.6072 | 123.0284 | 61.4629 | 61.5259 | 123.0804 | 61.4991 | 122.8632 | 61.5987 | 61.6255 | 61.5025 | 61.5293
613.5938 | 123.3765 | -61.4731 | 61.615 | 0.030283 | -0.049678 | -0.021157 | -0.002124 | 0.040843 | 0.003172 | 0.042581 | 61.6287 | 0.11585 | 61.537 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.5034 | 61.4234 | 61.4519 | 61.471 | 61.5139 | 61.4763 | 61.5157 | 123.1018 | 61.5889 | 123.0101 | 61.4354 | 61.5076 | 123.053 | 61.4808 | 122.8403 | 61.5942 | 61.6209 | 61.5025 | 61.5293
614.5938 | 123.349 | -61.5097 | 61.6608 | 0.030283 | -0.049678 | -0.021157 | -0.002124 | 0.040843 | -0.001406 | 0.038003 | 61.6195 | 0.11127 | 61.5324 | -0.03768 | 0.029923 | 61.5845 | 0.007721 | 61.3718 | 61.54 | 61.46 | 61.4885 | 61.5076 | 61.5505 | 61.5083 | 61.5477 | 123.1292 | 61.621 | 123.0422 | 61.472 | 61.5396 | 123.0942 | 61.5174 | 122.8815 | 61.5896 | 61.6118 | 61.5025 | 61.5247
615.5938 | 123.262 | -61.5051 | 61.6379 | 0.025705 | -0.054257 | -0.021157 | 0.007033 | 0.036265 | 0.003172 | 0.038003 | 61.6332 | 0.10211 | 61.5233 | -0.03768 | 0.039079 | 61.5799 | 0.007721 | 61.3672 | 61.5308 | 61.4509 | 61.484 | 61.5122 | 61.5414 | 61.5083 | 61.5431 | 123.1384 | 61.6072 | 123.0284 | 61.4674 | 61.5442 | 123.085 | 61.5128 | 122.8724 | 61.5942 | 61.6255 | 61.4842 | 61.5156
616.5938 | 123.4085 | -61.4639 | 61.5784 | 0.025705 | -0.049678 | -0.021157 | 0.002454 | 0.040843 | 0.003172 | 0.038003 | 61.6287 | 0.11127 | 61.5233 | -0.033101 | 0.034501 | 61.5753 | -0.001436 | 61.3718 | 61.4896 | 61.4143 | 61.4428 | 61.4664 | 61.5048 | 61.4671 | 61.5019 | 123.0926 | 61.5752 | 122.9872 | 61.4308 | 61.4984 | 123.0392 | 61.4625 | 122.8357 | 61.5942 | 61.6301 | 61.4888 | 61.5247
617.5938 | 123.2941 | -61.5143 | 61.6196 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.031687 | -0.001406 | 0.042581 | 61.6241 | 0.11127 | 61.5279 | -0.033101 | 0.029923 | 61.5891 | 0.003143 | 61.3627 | 61.5354 | 61.4692 | 61.4977 | 61.5167 | 61.546 | 61.5129 | 61.5569 | 123.1384 | 61.6256 | 123.0422 | 61.4812 | 61.5442 | 123.1033 | 61.5174 | 122.8769 | 61.5942 | 61.6209 | 61.4979 | 61.5247
618.5938 | 123.3307 | -61.496 | 61.6241 | 0.021127 | -0.049678 | -0.030314 | 0.002454 | 0.036265 | -0.001406 | 0.042581 | 61.6287 | 0.10669 | 61.5279 | -0.03768 | 0.034501 | 61.5799 | -0.001436 | 61.3764 | 61.5171 | 61.4463 | 61.4657 | 61.4984 | 61.5322 | 61.4946 | 61.5386 | 123.1246 | 61.6027 | 123.0238 | 61.4583 | 61.5305 | 123.0759 | 61.4945 | 122.8724 | 61.5942 | 61.6301 | 61.4934 | 61.5293
619.5938 | 123.2574 | -61.5097 | 61.6333 | 0.021127 | -0.054257 | -0.021157 | 0.002454 | 0.045421 | -0.001406 | 0.042581 | 61.6241 | 0.10669 | 61.537 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3672 | 61.5308 | 61.4554 | 61.4885 | 61.5122 | 61.5551 | 61.5083 | 61.5523 | 123.1338 | 61.6164 | 123.0467 | 61.4766 | 61.5396 | 123.0896 | 61.5174 | 122.8769 | 61.5942 | 61.6164 | 61.5071 | 61.5293
620.5938 | 123.262 | -61.5005 | 61.6425 | 0.034862 | -0.049678 | -0.021157 | 0.002454 | 0.040843 | -0.001406 | 0.051737 | 61.6424 | 0.12043 | 61.537 | -0.033101 | 0.039079 | 61.5891 | 0.007721 | 61.3718 | 61.5354 | 61.4509 | 61.4794 | 61.503 | 61.5414 | 61.4991 | 61.5523 | 123.143 | 61.621 | 123.0376 | 61.4674 | 61.5396 | 123.0896 | 61.5083 | 122.8724 | 61.6033 | 61.6347 | 61.4979 | 61.5293
621.5938 | 123.2483 | -61.4914 | 61.6379 | 0.025705 | -0.049678 | -0.021157 | 0.011611 | 0.031687 | -0.001406 | 0.042581 | 61.6241 | 0.11585 | 61.5279 | -0.033101 | 0.034501 | 61.5845 | 0.003143 | 61.3718 | 61.5171 | 61.4417 | 61.4702 | 61.503 | 61.5231 | 61.49 | 61.534 | 123.1155 | 61.6072 | 123.0193 | 61.4583 | 61.5259 | 123.0759 | 61.4945 | 122.8632 | 61.5896 | 61.6209 | 61.4934 | 61.5247
622.5938 | 123.2391 | -61.5051 | 61.6516 | 0.025705 | -0.049678 | -0.025735 | -0.002124 | 0.040843 | -0.001406 | 0.038003 | 61.6287 | 0.12043 | 61.5279 | -0.03768 | 0.029923 | 61.5753 | 0.003143 | 61.3672 | 61.5308 | 61.4554 | 61.4794 | 61.503 | 61.546 | 61.5037 | 61.5431 | 123.1338 | 61.6256 | 123.033 | 61.4674 | 61.535 | 123.0804 | 61.5083 | 122.8724 | 61.5987 | 61.6255 | 61.4979 | 61.5247
623.5938 | 123.2941 | -61.5189 | 61.647 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.040843 | -0.001406 | 0.042581 | 61.6332 | 0.12958 | 61.537 | -0.03768 | 0.034501 | 61.5845 | 0.007721 | 61.3672 | 61.5446 | 61.4738 | 61.5023 | 61.5167 | 61.5597 | 61.5175 | 61.5614 | 123.1521 | 61.6484 | 123.0559 | 61.4812 | 61.5534 | 123.1033 | 61.5266 | 122.8861 | 61.5987 | 61.6255 | 61.5025 | 61.5293
624.5938 | 123.2803 | -61.5005 | 61.6287 | 0.021127 | -0.049678 | -0.021157 | 0.007033 | 0.036265 | -0.005985 | 0.042581 | 61.6287 | 0.12043 | 61.5279 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3627 | 61.5217 | 61.4509 | 61.4794 | 61.5076 | 61.5368 | 61.4946 | 61.5431 | 123.1292 | 61.621 | 123.0284 | 61.4674 | 61.5305 | 123.0804 | 61.5083 | 122.8632 | 61.5987 | 61.6209 | 61.4979 | 61.5202
625.5938 | 123.2574 | -61.5189 | 61.6333 | 0.025705 | -0.054257 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.047159 | 61.6195 | 0.12043 | 61.537 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3718 | 61.5446 | 61.4646 | 61.5023 | 61.5213 | 61.5551 | 61.5129 | 61.566 | 123.1384 | 61.6393 | 123.0559 | 61.4812 | 61.5579 | 123.0988 | 61.522 | 122.8907 | 61.5804 | 61.6164 | 61.4979 | 61.5339
626.5938 | 123.2117 | -61.5097 | 61.5875 | 0.025705 | -0.058836 | -0.016578 | -0.002124 | 0.036265 | 0.003172 | 0.042581 | 61.6287 | 0.11127 | 61.5279 | -0.03768 | 0.029923 | 61.5891 | -0.001436 | 61.3672 | 61.5354 | 61.4509 | 61.4931 | 61.5076 | 61.546 | 61.5129 | 61.5523 | 123.1384 | 61.621 | 123.0376 | 61.472 | 61.5396 | 123.0988 | 61.5083 | 122.8769 | 61.5987 | 61.6301 | 61.4979 | 61.5293
627.5938 | 123.3032 | -61.4914 | 61.6333 | 0.025705 | -0.054257 | -0.021157 | 0.002454 | 0.031687 | -0.005985 | 0.042581 | 61.6287 | 0.11127 | 61.5324 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3627 | 61.5171 | 61.4371 | 61.4702 | 61.4938 | 61.5231 | 61.4854 | 61.534 | 123.1201 | 61.6027 | 123.0238 | 61.4583 | 61.5213 | 123.0713 | 61.4991 | 122.8541 | 61.5987 | 61.6209 | 61.5025 | 61.5247
628.5938 | 123.3078 | -61.4731 | 61.6562 | 0.021127 | -0.049678 | -0.016578 | -0.002124 | 0.036265 | -0.005985 | 0.042581 | 61.6287 | 0.10669 | 61.5279 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.4942 | 61.4234 | 61.4565 | 61.471 | 61.5093 | 61.4671 | 61.5157 | 123.1018 | 61.5798 | 123.001 | 61.44 | 61.503 | 123.053 | 61.4808 | 122.8449 | 61.5987 | 61.6209 | 61.4979 | 61.5202
629.5938 | 123.2391 | -61.5051 | 61.647 | 0.025705 | -0.054257 | -0.016578 | -0.002124 | 0.036265 | -0.001406 | 0.038003 | 61.6287 | 0.10211 | 61.5324 | -0.042259 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.5308 | 61.4509 | 61.4885 | 61.503 | 61.5414 | 61.5037 | 61.5431 | 123.1338 | 61.6072 | 123.0376 | 61.4629 | 61.5442 | 123.0896 | 61.5083 | 122.8769 | 61.5896 | 61.6255 | 61.4934 | 61.5293
630.5938 | 123.1293 | -61.5372 | 61.5875 | 0.021127 | -0.049678 | -0.025735 | 0.002454 | 0.036265 | -0.010563 | 0.047159 | 61.6332 | 0.10669 | 61.5279 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3718 | 61.5583 | 61.4875 | 61.5114 | 61.5396 | 61.5734 | 61.5266 | 61.5843 | 123.1704 | 61.6439 | 123.065 | 61.4995 | 61.5717 | 123.1216 | 61.5403 | 122.909 | 61.5987 | 61.6301 | 61.4934 | 61.5247
631.5938 | 123.2666 | -61.5097 | 61.6287 | 0.021127 | -0.054257 | -0.016578 | 0.007033 | 0.031687 | -0.001406 | 0.042581 | 61.6332 | 0.10669 | 61.5324 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.5308 | 61.4554 | 61.4931 | 61.5167 | 61.5414 | 61.5083 | 61.5523 | 123.143 | 61.6164 | 123.0422 | 61.4766 | 61.5442 | 123.0896 | 61.5174 | 122.8815 | 61.5987 | 61.6255 | 61.4979 | 61.5247
632.5938 | 123.2712 | -61.5051 | 61.6425 | 0.025705 | -0.049678 | -0.025735 | -0.002124 | 0.036265 | 0.003172 | 0.038003 | 61.6287 | 0.12043 | 61.5324 | -0.028522 | 0.034501 | 61.5845 | 0.003143 | 61.3627 | 61.5308 | 61.4554 | 61.4794 | 61.503 | 61.5414 | 61.5083 | 61.5431 | 123.1338 | 61.6256 | 123.0376 | 61.4766 | 61.5396 | 123.0896 | 61.5083 | 122.8678 | 61.5942 | 61.6255 | 61.4979 | 61.5293
633.5938 | 123.2895 | -61.5051 | 61.6425 | 0.025705 | -0.049678 | -0.021157 | 0.002454 | 0.040843 | -0.010563 | 0.038003 | 61.6195 | 0.11585 | 61.5279 | -0.03768 | 0.029923 | 61.5845 | 0.007721 | 61.3718 | 61.5308 | 61.4554 | 61.484 | 61.5076 | 61.546 | 61.4946 | 61.5431 | 123.1246 | 61.621 | 123.033 | 61.4674 | 61.535 | 123.0896 | 61.5128 | 122.8769 | 61.5896 | 61.6118 | 61.4979 | 61.5202
634.5938 | 123.3353 | -61.4868 | 61.6379 | 0.025705 | -0.049678 | -0.021157 | -0.006703 | 0.036265 | -0.001406 | 0.038003 | 61.6332 | 0.10669 | 61.5279 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.3718 | 61.5125 | 61.4371 | 61.4657 | 61.4801 | 61.5231 | 61.4854 | 61.5248 | 123.1201 | 61.5935 | 123.0147 | 61.4491 | 61.5167 | 123.0713 | 61.4854 | 122.8586 | 61.6033 | 61.6347 | 61.4979 | 61.5293
635.5938 | 123.3353 | -61.4777 | 61.647 | 0.030283 | -0.054257 | -0.016578 | 0.011611 | 0.036265 | -0.001406 | 0.033424 | 61.6287 | 0.12043 | 61.537 | -0.033101 | 0.034501 | 61.5845 | 0.012299 | 61.3672 | 61.5079 | 61.4234 | 61.4611 | 61.4893 | 61.5139 | 61.4763 | 61.5111 | 123.1063 | 61.5981 | 123.0147 | 61.4446 | 61.5122 | 123.0621 | 61.49 | 122.8449 | 61.5942 | 61.6164 | 61.5025 | 61.5247
636.5938 | 123.2803 | -61.4456 | 61.6516 | 0.025705 | -0.054257 | -0.021157 | -0.002124 | 0.027109 | 0.003172 | 0.042581 | 61.6287 | 0.11585 | 61.5324 | -0.03768 | 0.039079 | 61.5753 | 0.007721 | 61.3672 | 61.4713 | 61.3914 | 61.4245 | 61.4435 | 61.4727 | 61.4488 | 61.4882 | 123.0743 | 61.5615 | 122.9781 | 61.4079 | 61.4847 | 123.0209 | 61.4533 | 122.8129 | 61.5896 | 61.6209 | 61.4934 | 61.5247
637.5938 | 123.2666 | -61.4822 | 61.647 | 0.025705 | -0.054257 | -0.016578 | -0.002124 | 0.036265 | -0.005985 | 0.038003 | 61.6287 | 0.11127 | 61.5324 | -0.033101 | 0.029923 | 61.5845 | 0.016878 | 61.3672 | 61.5079 | 61.428 | 61.4657 | 61.4801 | 61.5185 | 61.4763 | 61.5202 | 123.1109 | 61.5935 | 123.0147 | 61.4491 | 61.5122 | 123.0667 | 61.4991 | 122.8495 | 61.5987 | 61.6118 | 61.5025 | 61.5156
638.5938 | 123.3215 | -61.4822 | 61.6516 | 0.025705 | -0.0451 | -0.025735 | 0.002454 | 0.040843 | 0.003172 | 0.042581 | 61.6241 | 0.11127 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3764 | 61.5079 | 61.4371 | 61.4565 | 61.4847 | 61.5231 | 61.4854 | 61.5248 | 123.1063 | 61.5935 | 123.0147 | 61.4491 | 61.5167 | 123.0667 | 61.49 | 122.8586 | 61.5896 | 61.6164 | 61.4979 | 61.5247
639.5938 | 123.2986 | -61.4594 | 61.6562 | 0.025705 | -0.054257 | -0.025735 | -0.002124 | 0.036265 | -0.001406 | 0.042581 | 61.6332 | 0.11585 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | 0.003143 | 61.3718 | 61.4851 | 61.4051 | 61.4336 | 61.4572 | 61.4956 | 61.4579 | 61.5019 | 123.0926 | 61.5752 | 122.9918 | 61.4262 | 61.4939 | 123.0438 | 61.4625 | 122.8312 | 61.5987 | 61.6301 | 61.4979 | 61.5293
640.5938 | 123.3582 | -61.496 | 61.6516 | 0.030283 | -0.054257 | -0.021157 | -0.006703 | 0.040843 | -0.010563 | 0.038003 | 61.6287 | 0.11585 | 61.5324 | -0.033101 | 0.025345 | 61.5845 | 0.012299 | 61.3764 | 61.5263 | 61.4417 | 61.4748 | 61.4893 | 61.5368 | 61.4854 | 61.534 | 123.1246 | 61.6118 | 123.0284 | 61.4629 | 61.5213 | 123.0804 | 61.5083 | 122.8724 | 61.6033 | 61.6164 | 61.5071 | 61.5202
641.5938 | 123.3353 | -61.4914 | 61.6653 | 0.030283 | -0.049678 | -0.025735 | -0.006703 | 0.027109 | -0.001406 | 0.042581 | 61.6241 | 0.10211 | 61.5233 | -0.046838 | 0.034501 | 61.5799 | 0.007721 | 61.3764 | 61.5217 | 61.4417 | 61.4657 | 61.4847 | 61.5185 | 61.49 | 61.534 | 123.1155 | 61.5935 | 123.0147 | 61.4446 | 61.5259 | 123.0713 | 61.4991 | 122.8678 | 61.5896 | 61.6164 | 61.4888 | 61.5156
642.5938 | 123.2986 | -61.5005 | 61.6562 | 0.025705 | -0.058836 | -0.025735 | 0.002454 | 0.036265 | -0.005985 | 0.033424 | 61.6332 | 0.10669 | 61.5324 | -0.03768 | 0.029923 | 61.5799 | 0.003143 | 61.3718 | 61.5263 | 61.4417 | 61.4748 | 61.503 | 61.5368 | 61.4946 | 61.534 | 123.1338 | 61.6072 | 123.033 | 61.4629 | 61.5305 | 123.0804 | 61.5037 | 122.8724 | 61.6033 | 61.6301 | 61.5025 | 61.5293
643.5938 | 123.317 | -61.5005 | 61.6653 | 0.016548 | -0.054257 | -0.025735 | 0.002454 | 0.040843 | -0.005985 | 0.038003 | 61.6287 | 0.11127 | 61.5324 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3672 | 61.5171 | 61.4463 | 61.4748 | 61.503 | 61.5414 | 61.4946 | 61.5386 | 123.1292 | 61.6118 | 123.033 | 61.4629 | 61.5305 | 123.0804 | 61.5083 | 122.8678 | 61.5987 | 61.6209 | 61.5025 | 61.5247
644.5938 | 123.2986 | -61.4868 | 61.6425 | 0.025705 | -0.054257 | -0.021157 | -0.002124 | 0.031687 | -0.005985 | 0.038003 | 61.6195 | 0.11127 | 61.5279 | -0.033101 | 0.029923 | 61.5845 | 0.007721 | 61.381 | 61.5125 | 61.4326 | 61.4657 | 61.4847 | 61.5185 | 61.4808 | 61.5248 | 123.1063 | 61.5981 | 123.0147 | 61.4537 | 61.5167 | 123.0713 | 61.4945 | 122.8678 | 61.5896 | 61.6118 | 61.4979 | 61.5202
645.5938 | 123.2758 | -61.496 | 61.6745 | 0.021127 | -0.058836 | -0.021157 | -0.002124 | 0.031687 | -0.010563 | 0.038003 | 61.6287 | 0.11127 | 61.5279 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3764 | 61.5171 | 61.4371 | 61.4748 | 61.4938 | 61.5277 | 61.4854 | 61.534 | 123.1246 | 61.6072 | 123.0238 | 61.4629 | 61.5305 | 123.0759 | 61.5037 | 122.8724 | 61.5942 | 61.6209 | 61.4934 | 61.5202
646.5938 | 123.3124 | -61.4685 | 61.6745 | 0.025705 | -0.058836 | -0.016578 | 0.002454 | 0.036265 | -0.005985 | 0.038003 | 61.6195 | 0.12043 | 61.5324 | -0.028522 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.4942 | 61.4097 | 61.4519 | 61.471 | 61.5048 | 61.4625 | 61.5065 | 123.088 | 61.5889 | 123.001 | 61.44 | 61.503 | 123.0484 | 61.4762 | 122.8403 | 61.585 | 61.6118 | 61.4979 | 61.5247
647.5938 | 123.3032 | -61.4822 | 61.6699 | 0.030283 | -0.058836 | -0.016578 | -0.002124 | 0.036265 | -0.001406 | 0.038003 | 61.6287 | 0.12501 | 61.537 | -0.03768 | 0.043657 | 61.5845 | 0.003143 | 61.3764 | 61.5125 | 61.4234 | 61.4657 | 61.4801 | 61.5185 | 61.4808 | 61.5202 | 123.1109 | 61.6072 | 123.0193 | 61.4446 | 61.5259 | 123.0667 | 61.4854 | 122.8586 | 61.585 | 61.6255 | 61.4934 | 61.5339
648.5938 | 123.2025 | -61.5051 | 61.6745 | 0.025705 | -0.054257 | -0.021157 | -0.006703 | 0.040843 | -0.005985 | 0.033424 | 61.6378 | 0.11585 | 61.5233 | -0.03768 | 0.039079 | 61.5936 | 0.003143 | 61.3718 | 61.5308 | 61.4509 | 61.484 | 61.4984 | 61.546 | 61.4991 | 61.5386 | 123.143 | 61.621 | 123.0284 | 61.4674 | 61.5442 | 123.0988 | 61.5083 | 122.8769 | 61.5987 | 61.6347 | 61.4842 | 61.5202
649.5938 | 123.2529 | -61.5051 | 61.6745 | 0.025705 | -0.058836 | -0.016578 | -0.002124 | 0.022531 | -0.005985 | 0.038003 | 61.6332 | 0.11127 | 61.5324 | -0.028522 | 0.034501 | 61.5845 | 0.012299 | 61.3718 | 61.5308 | 61.4463 | 61.4885 | 61.503 | 61.5277 | 61.4991 | 61.5431 | 123.1384 | 61.6164 | 123.0376 | 61.4766 | 61.5396 | 123.0896 | 61.5174 | 122.8769 | 61.5987 | 61.6209 | 61.4979 | 61.5202
650.5938 | 123.2666 | -61.4914 | 61.6882 | 0.021127 | -0.058836 | -0.025735 | -0.002124 | 0.031687 | -0.005985 | 0.047159 | 61.6287 | 0.11585 | 61.5233 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3764 | 61.5125 | 61.4326 | 61.4657 | 61.4893 | 61.5231 | 61.4854 | 61.5386 | 123.1201 | 61.6072 | 123.0147 | 61.4537 | 61.5259 | 123.0713 | 61.4945 | 122.8678 | 61.5942 | 61.6255 | 61.4888 | 61.5202
651.5938 | 123.2849 | -61.4731 | 61.6882 | 0.021127 | -0.054257 | -0.030314 | -0.002124 | 0.031687 | -0.005985 | 0.033424 | 61.6332 | 0.11127 | 61.5187 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3764 | 61.4942 | 61.4188 | 61.4428 | 61.471 | 61.5048 | 61.4671 | 61.5065 | 123.1063 | 61.5844 | 122.9918 | 61.4354 | 61.5122 | 123.053 | 61.4762 | 122.8495 | 61.5942 | 61.6301 | 61.4796 | 61.5156
652.5938 | 123.2529 | -61.5097 | 61.6974 | 0.021127 | -0.063415 | -0.021157 | 0.002454 | 0.031687 | -0.005985 | 0.033424 | 61.6287 | 0.12043 | 61.5279 | -0.028522 | 0.039079 | 61.5707 | 0.003143 | 61.3718 | 61.5308 | 61.4463 | 61.4885 | 61.5122 | 61.5414 | 61.5037 | 61.5431 | 123.1384 | 61.6301 | 123.0376 | 61.4812 | 61.5488 | 123.0804 | 61.5128 | 122.8815 | 61.5896 | 61.6255 | 61.4888 | 61.5247
653.5938 | 123.2574 | -61.5051 | 61.6562 | 0.021127 | -0.054257 | -0.025735 | -0.002124 | 0.031687 | -0.001406 | 0.033424 | 61.6332 | 0.12501 | 61.537 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3718 | 61.5263 | 61.4509 | 61.4794 | 61.503 | 61.5368 | 61.5037 | 61.5386 | 123.1384 | 61.6301 | 123.0422 | 61.472 | 61.5442 | 123.0896 | 61.5128 | 122.8769 | 61.5942 | 61.6255 | 61.4979 | 61.5293
654.5938 | 123.2666 | -61.5005 | 61.702 | 0.016548 | -0.054257 | -0.021157 | -0.002124 | 0.036265 | -0.010563 | 0.028846 | 61.6332 | 0.12043 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3764 | 61.5171 | 61.4463 | 61.4794 | 61.4984 | 61.5368 | 61.49 | 61.5294 | 123.1338 | 61.621 | 123.033 | 61.4674 | 61.535 | 123.085 | 61.5083 | 122.8769 | 61.5987 | 61.6255 | 61.4979 | 61.5247
655.5938 | 123.3948 | -61.4594 | 61.6333 | 0.021127 | -0.054257 | -0.025735 | -0.011281 | 0.027109 | -0.010563 | 0.033424 | 61.6332 | 0.10669 | 61.5233 | -0.033101 | 0.034501 | 61.5891 | 0.007721 | 61.3764 | 61.4805 | 61.4051 | 61.4336 | 61.4481 | 61.4865 | 61.4488 | 61.4928 | 123.0926 | 61.566 | 122.9826 | 61.4262 | 61.4939 | 123.0484 | 61.4671 | 122.8357 | 61.5987 | 61.6255 | 61.4888 | 61.5156
656.5938 | 123.3948 | -61.4822 | 61.6058 | 0.025705 | -0.058836 | -0.025735 | -0.002124 | 0.031687 | -0.005985 | 0.028846 | 61.6332 | 0.11585 | 61.537 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.5079 | 61.4234 | 61.4565 | 61.4801 | 61.5139 | 61.4763 | 61.5111 | 123.1155 | 61.5981 | 123.0193 | 61.4446 | 61.5213 | 123.0621 | 61.4854 | 122.8495 | 61.5942 | 61.6301 | 61.4979 | 61.5339
657.5938 | 123.4085 | -61.4548 | 61.6058 | 0.021127 | -0.054257 | -0.030314 | -0.006703 | 0.027109 | -0.010563 | 0.033424 | 61.6378 | 0.10669 | 61.537 | -0.03768 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.4759 | 61.4005 | 61.4245 | 61.4481 | 61.4819 | 61.4442 | 61.4882 | 123.0926 | 61.5615 | 122.9918 | 61.4171 | 61.4939 | 123.0347 | 61.4625 | 122.8266 | 61.5987 | 61.6301 | 61.4979 | 61.5293
658.5938 | 123.4131 | -61.4822 | 61.6516 | 0.021127 | -0.054257 | -0.030314 | -0.002124 | 0.031687 | -0.005985 | 0.033424 | 61.6332 | 0.11127 | 61.5279 | -0.033101 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.5034 | 61.428 | 61.4519 | 61.4801 | 61.5139 | 61.4763 | 61.5157 | 123.1155 | 61.5935 | 123.0101 | 61.4491 | 61.5167 | 123.0667 | 61.4808 | 122.8541 | 61.5987 | 61.6347 | 61.4934 | 61.5293
659.5938 | 123.3994 | -61.4594 | 61.5967 | 0.021127 | -0.063415 | -0.025735 | -0.011281 | 0.022531 | -0.010563 | 0.028846 | 61.6287 | 0.11585 | 61.5324 | -0.028522 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.4805 | 61.3959 | 61.4336 | 61.4481 | 61.4819 | 61.4488 | 61.4882 | 123.088 | 61.5752 | 122.9918 | 61.4308 | 61.4984 | 123.0392 | 61.4671 | 122.8312 | 61.5896 | 61.6209 | 61.4934 | 61.5247
660.5938 | 123.3994 | -61.4502 | 61.6241 | 0.021127 | -0.054257 | -0.030314 | -0.011281 | 0.022531 | -0.005985 | 0.038003 | 61.6241 | 0.12043 | 61.537 | -0.028522 | 0.039079 | 61.5799 | -0.001436 | 61.3718 | 61.4713 | 61.3959 | 61.4199 | 61.4389 | 61.4727 | 61.4442 | 61.4882 | 123.0743 | 61.5706 | 122.9872 | 61.4217 | 61.4893 | 123.0301 | 61.4488 | 122.822 | 61.585 | 61.6255 | 61.4979 | 61.5385
661.5938 | 123.4085 | -61.4548 | 61.6287 | 0.021127 | -0.058836 | -0.025735 | -0.006703 | 0.027109 | -0.005985 | 0.038003 | 61.6287 | 0.11127 | 61.537 | -0.028522 | 0.034501 | 61.5845 | 0.007721 | 61.3718 | 61.4759 | 61.3959 | 61.429 | 61.4481 | 61.4819 | 61.4488 | 61.4928 | 123.0834 | 61.566 | 122.9918 | 61.4263 | 61.4893 | 123.0392 | 61.4625 | 122.8266 | 61.5942 | 61.6209 | 61.5025 | 61.5293
662.5938 | 123.3719 | -61.4731 | 61.6287 | 0.016548 | -0.067994 | -0.030314 | -0.006703 | 0.022531 | -0.010563 | 0.028846 | 61.6287 | 0.12043 | 61.5279 | -0.03768 | 0.043657 | 61.5799 | 0.003143 | 61.3672 | 61.4896 | 61.4051 | 61.4428 | 61.4664 | 61.4956 | 61.4625 | 61.5019 | 123.1018 | 61.5935 | 123.001 | 61.4354 | 61.5167 | 123.053 | 61.4762 | 122.8403 | 61.585 | 61.6255 | 61.4842 | 61.5247
663.5938 | 123.3765 | -61.4822 | 61.6287 | 0.025705 | -0.049678 | -0.025735 | -0.006703 | 0.031687 | -0.005985 | 0.028846 | 61.6241 | 0.11127 | 61.5279 | -0.028522 | 0.039079 | 61.5753 | 0.012299 | 61.3672 | 61.5079 | 61.4326 | 61.4565 | 61.4755 | 61.5139 | 61.4763 | 61.5111 | 123.1063 | 61.5935 | 123.0101 | 61.4537 | 61.5213 | 123.0576 | 61.4945 | 122.8495 | 61.585 | 61.6118 | 61.4888 | 61.5156
664.5938 | 123.3719 | -61.4868 | 61.6196 | 0.025705 | -0.063415 | -0.025735 | -0.01586 | 0.013375 | -0.005985 | 0.038003 | 61.6241 | 0.11585 | 61.5324 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3627 | 61.5125 | 61.4234 | 61.4611 | 61.471 | 61.5002 | 61.4808 | 61.5248 | 123.1109 | 61.6027 | 123.0193 | 61.4537 | 61.5213 | 123.0667 | 61.4945 | 122.8495 | 61.5896 | 61.6164 | 61.4979 | 61.5247
665.5938 | 123.4039 | -61.4731 | 61.6196 | 0.021127 | -0.054257 | -0.030314 | -0.011281 | 0.031687 | -0.010563 | 0.028846 | 61.6241 | 0.11585 | 61.537 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.4942 | 61.4188 | 61.4428 | 61.4618 | 61.5048 | 61.4625 | 61.5019 | 123.0972 | 61.5889 | 123.0101 | 61.4354 | 61.5122 | 123.0576 | 61.4808 | 122.8403 | 61.585 | 61.6164 | 61.4979 | 61.5293
666.5938 | 123.4131 | -61.4822 | 61.6013 | 0.021127 | -0.054257 | -0.025735 | -0.006703 | 0.022531 | -0.010563 | 0.028846 | 61.6332 | 0.11127 | 61.5279 | -0.033101 | 0.034501 | 61.5891 | 0.016878 | 61.3764 | 61.5034 | 61.428 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.5111 | 123.1155 | 61.5935 | 123.0101 | 61.4491 | 61.5167 | 123.0713 | 61.4991 | 122.8586 | 61.5987 | 61.6164 | 61.4934 | 61.511
667.5938 | 123.3673 | -61.4685 | 61.6196 | 0.021127 | -0.058836 | -0.025735 | -0.006703 | 0.027109 | -0.005985 | 0.028846 | 61.6241 | 0.11127 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3672 | 61.4896 | 61.4097 | 61.4428 | 61.4618 | 61.4956 | 61.4625 | 61.4974 | 123.0926 | 61.5798 | 123.001 | 61.4354 | 61.503 | 123.053 | 61.4762 | 122.8357 | 61.5896 | 61.6164 | 61.4979 | 61.5247
668.5938 | 123.3536 | -61.5097 | 61.6241 | 0.021127 | -0.063415 | -0.025735 | -0.006703 | 0.027109 | -0.010563 | 0.033424 | 61.6287 | 0.10669 | 61.537 | -0.033101 | 0.029923 | 61.5799 | 0.003143 | 61.3672 | 61.5308 | 61.4463 | 61.484 | 61.503 | 61.5368 | 61.4991 | 61.5431 | 123.1384 | 61.6164 | 123.0467 | 61.4766 | 61.5396 | 123.0896 | 61.5128 | 122.8769 | 61.5987 | 61.6255 | 61.5071 | 61.5339
669.5938 | 123.3673 | -61.4777 | 61.5921 | 0.021127 | -0.049678 | -0.025735 | -0.002124 | 0.022531 | -0.015142 | 0.033424 | 61.6241 | 0.12501 | 61.5233 | -0.042259 | 0.034501 | 61.5753 | 0.012299 | 61.3718 | 61.4988 | 61.428 | 61.4519 | 61.4755 | 61.5002 | 61.4625 | 61.5111 | 123.1018 | 61.6027 | 123.001 | 61.4354 | 61.5122 | 123.053 | 61.49 | 122.8495 | 61.5896 | 61.6118 | 61.4888 | 61.511
670.5938 | 123.3948 | -61.4914 | 61.6104 | 0.021127 | -0.054257 | -0.030314 | -0.002124 | 0.022531 | -0.005985 | 0.033424 | 61.6241 | 0.11127 | 61.5233 | -0.03768 | 0.034501 | 61.5891 | 0.007721 | 61.3672 | 61.5125 | 61.4371 | 61.4611 | 61.4893 | 61.5139 | 61.4854 | 61.5248 | 123.1155 | 61.6027 | 123.0147 | 61.4537 | 61.5259 | 123.0804 | 61.4991 | 122.8586 | 61.5896 | 61.6164 | 61.4888 | 61.5156
671.5938 | 123.349 | -61.4777 | 61.5921 | 0.016548 | -0.054257 | -0.025735 | -0.011281 | 0.027109 | -0.010563 | 0.028846 | 61.6378 | 0.11127 | 61.5279 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.4942 | 61.4234 | 61.4519 | 61.4664 | 61.5048 | 61.4671 | 61.5065 | 123.1155 | 61.5889 | 123.0055 | 61.4446 | 61.5122 | 123.0576 | 61.4854 | 122.8495 | 61.6033 | 61.6301 | 61.4934 | 61.5202
672.5938 | 123.3673 | -61.5051 | 61.5875 | 0.030283 | -0.058836 | -0.025735 | -0.011281 | 0.040843 | -0.015142 | 0.033424 | 61.6332 | 0.12043 | 61.5416 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.5354 | 61.4463 | 61.4794 | 61.4938 | 61.546 | 61.49 | 61.5386 | 123.1384 | 61.6256 | 123.0467 | 61.4674 | 61.5396 | 123.085 | 61.5128 | 122.8724 | 61.5987 | 61.6255 | 61.5071 | 61.5339
673.5938 | 123.381 | -61.4594 | 61.5921 | 0.025705 | -0.058836 | -0.030314 | -0.011281 | 0.022531 | -0.010563 | 0.028846 | 61.6287 | 0.10669 | 61.5233 | -0.03768 | 0.029923 | 61.5891 | 0.007721 | 61.3718 | 61.4851 | 61.4005 | 61.429 | 61.4481 | 61.4819 | 61.4488 | 61.4882 | 123.088 | 61.566 | 122.9826 | 61.4217 | 61.4893 | 123.0484 | 61.4671 | 122.8312 | 61.5987 | 61.6209 | 61.4934 | 61.5156
674.5938 | 123.4131 | -61.4685 | 61.6013 | 0.016548 | -0.058836 | -0.025735 | -0.011281 | 0.027109 | -0.005985 | 0.028846 | 61.6287 | 0.12043 | 61.5279 | -0.033101 | 0.034501 | 61.5891 | 0.003143 | 61.3718 | 61.4851 | 61.4097 | 61.4428 | 61.4572 | 61.4956 | 61.4625 | 61.4974 | 123.0972 | 61.5889 | 122.9964 | 61.4354 | 61.503 | 123.0576 | 61.4716 | 122.8403 | 61.5942 | 61.6255 | 61.4934 | 61.5247
675.5938 | 123.4039 | -61.4685 | 61.5738 | 0.021127 | -0.058836 | -0.030314 | -0.006703 | 0.027109 | -0.015142 | 0.028846 | 61.6378 | 0.11585 | 61.5279 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3627 | 61.4896 | 61.4097 | 61.4382 | 61.4618 | 61.4956 | 61.4534 | 61.4974 | 123.1063 | 61.5844 | 122.9964 | 61.4308 | 61.5076 | 123.0484 | 61.4716 | 122.8312 | 61.5987 | 61.6347 | 61.4888 | 61.5247
676.5938 | 123.4177 | -61.4777 | 61.5829 | 0.025705 | -0.058836 | -0.034893 | -0.002124 | 0.031687 | -0.010563 | 0.038003 | 61.6287 | 0.10211 | 61.5233 | -0.023943 | 0.034501 | 61.5845 | 0.003143 | 61.3718 | 61.5034 | 61.4188 | 61.4428 | 61.4755 | 61.5093 | 61.4671 | 61.5157 | 123.1063 | 61.5798 | 123.001 | 61.4537 | 61.5122 | 123.0621 | 61.4808 | 122.8495 | 61.5942 | 61.6255 | 61.4888 | 61.5202
677.5938 | 123.3307 | -61.4914 | 61.6058 | 0.021127 | -0.054257 | -0.030314 | -0.01586 | 0.027109 | -0.01972 | 0.028846 | 61.6332 | 0.11127 | 61.537 | -0.042259 | 0.029923 | 61.5799 | 0.003143 | 61.3764 | 61.5125 | 61.4371 | 61.4611 | 61.4755 | 61.5185 | 61.4717 | 61.5202 | 123.1246 | 61.6027 | 123.0284 | 61.4491 | 61.5213 | 123.0713 | 61.4945 | 122.8678 | 61.6033 | 61.6301 | 61.5071 | 61.5339
678.5938 | 123.3948 | -61.4639 | 61.6287 | 0.021127 | -0.058836 | -0.025735 | -0.011281 | 0.027109 | -0.005985 | 0.033424 | 61.6287 | 0.12043 | 61.5233 | -0.042259 | 0.029923 | 61.5845 | 0.007721 | 61.3627 | 61.4851 | 61.4051 | 61.4382 | 61.4526 | 61.491 | 61.4579 | 61.4974 | 123.0926 | 61.5844 | 122.9872 | 61.4217 | 61.4939 | 123.0484 | 61.4716 | 122.8266 | 61.5987 | 61.6209 | 61.4934 | 61.5156
679.5938 | 123.3719 | -61.4914 | 61.5967 | 0.021127 | -0.063415 | -0.025735 | -0.011281 | 0.027109 | -0.010563 | 0.033424 | 61.6287 | 0.11127 | 61.5233 | -0.033101 | 0.034501 | 61.5753 | 0.007721 | 61.3627 | 61.5125 | 61.428 | 61.4657 | 61.4801 | 61.5185 | 61.4808 | 61.5248 | 123.1201 | 61.6027 | 123.0147 | 61.4583 | 61.5259 | 123.0667 | 61.4991 | 122.8541 | 61.5942 | 61.6209 | 61.4888 | 61.5156
680.5938 | 123.4085 | -61.4685 | 61.5738 | 0.025705 | -0.063415 | -0.025735 | -0.006703 | 0.027109 | -0.010563 | 0.033424 | 61.6332 | 0.12043 | 61.5233 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.3718 | 61.4942 | 61.4051 | 61.4428 | 61.4618 | 61.4956 | 61.4579 | 61.5019 | 123.1018 | 61.5889 | 122.9918 | 61.4308 | 61.503 | 123.0576 | 61.4716 | 122.8403 | 61.5987 | 61.6301 | 61.4888 | 61.5202
681.5938 | 123.436 | -61.4594 | 61.5829 | 0.025705 | -0.058836 | -0.021157 | -0.011281 | 0.031687 | -0.015142 | 0.028846 | 61.6287 | 0.10669 | 61.5416 | -0.03768 | 0.029923 | 61.5799 | 0.012299 | 61.3672 | 61.4851 | 61.4005 | 61.4382 | 61.4481 | 61.491 | 61.4442 | 61.4882 | 123.088 | 61.566 | 123.001 | 61.4217 | 61.4893 | 123.0392 | 61.4716 | 122.8266 | 61.5987 | 61.6164 | 61.5117 | 61.5293
682.5938 | 123.3719 | -61.4731 | 61.5829 | 0.025705 | -0.058836 | -0.034893 | -0.011281 | 0.031687 | -0.010563 | 0.028846 | 61.6287 | 0.10669 | 61.5233 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.4988 | 61.4142 | 61.4382 | 61.4618 | 61.5048 | 61.4625 | 61.5019 | 123.1018 | 61.5798 | 122.9964 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8403 | 61.5942 | 61.6255 | 61.4888 | 61.5202
683.5938 | 123.2895 | -61.4868 | 61.6196 | 0.025705 | -0.054257 | -0.025735 | -0.011281 | 0.027109 | -0.005985 | 0.033424 | 61.6332 | 0.12043 | 61.5416 | -0.03768 | 0.034501 | 61.5845 | 0.012299 | 61.3672 | 61.5125 | 61.4326 | 61.4611 | 61.4755 | 61.5139 | 61.4808 | 61.5202 | 123.1201 | 61.6072 | 123.0284 | 61.4491 | 61.5213 | 123.0713 | 61.4991 | 122.8541 | 61.5987 | 61.6209 | 61.5071 | 61.5293
684.5938 | 123.2574 | -61.5326 | 61.6287 | 0.030283 | -0.063415 | -0.030314 | -0.011281 | 0.027109 | -0.015142 | 0.033424 | 61.6378 | 0.11585 | 61.5324 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.5629 | 61.4692 | 61.5023 | 61.5213 | 61.5597 | 61.5175 | 61.566 | 123.1704 | 61.6484 | 123.065 | 61.4949 | 61.5671 | 123.1125 | 61.5403 | 122.8998 | 61.6033 | 61.6301 | 61.4979 | 61.5247
685.5938 | 123.3536 | -61.4822 | 61.6196 | 0.021127 | -0.063415 | -0.034893 | -0.011281 | 0.031687 | -0.015142 | 0.033424 | 61.6332 | 0.12043 | 61.5279 | -0.028522 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.5034 | 61.4188 | 61.4473 | 61.471 | 61.5139 | 61.4671 | 61.5157 | 123.1155 | 61.6027 | 123.0101 | 61.4537 | 61.5167 | 123.0621 | 61.49 | 122.8495 | 61.5987 | 61.6255 | 61.4934 | 61.5202
686.5938 | 123.3765 | -61.5189 | 61.6196 | 0.025705 | -0.063415 | -0.034893 | -0.011281 | 0.022531 | -0.010563 | 0.033424 | 61.6287 | 0.11127 | 61.5141 | -0.03768 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.5446 | 61.4554 | 61.484 | 61.5076 | 61.5414 | 61.5083 | 61.5523 | 123.1475 | 61.6301 | 123.033 | 61.4812 | 61.5534 | 123.1033 | 61.5174 | 122.8907 | 61.5942 | 61.6301 | 61.4796 | 61.5156
687.5938 | 123.3627 | -61.5097 | 61.6104 | 0.021127 | -0.058836 | -0.034893 | -0.01586 | 0.022531 | -0.005985 | 0.028846 | 61.6378 | 0.10669 | 61.5279 | -0.042259 | 0.034501 | 61.5845 | -0.001436 | 61.3672 | 61.5308 | 61.4509 | 61.4748 | 61.4938 | 61.5322 | 61.5037 | 61.5386 | 123.1475 | 61.6164 | 123.0376 | 61.4674 | 61.5442 | 123.0942 | 61.5083 | 122.8769 | 61.6033 | 61.6393 | 61.4934 | 61.5293
688.5938 | 123.3444 | -61.5097 | 61.6241 | 0.030283 | -0.067994 | -0.030314 | -0.002124 | 0.022531 | -0.010563 | 0.028846 | 61.6332 | 0.11585 | 61.5324 | -0.03768 | 0.039079 | 61.5845 | 0.003143 | 61.3672 | 61.54 | 61.4417 | 61.4794 | 61.5076 | 61.5322 | 61.4991 | 61.5386 | 123.143 | 61.6256 | 123.0422 | 61.472 | 61.5488 | 123.0942 | 61.5128 | 122.8769 | 61.5942 | 61.6301 | 61.4934 | 61.5293
689.5938 | 123.317 | -61.5051 | 61.6287 | 0.021127 | -0.067994 | -0.030314 | -0.01586 | 0.022531 | -0.010563 | 0.028846 | 61.6287 | 0.11585 | 61.5233 | -0.042259 | 0.025345 | 61.5845 | 0.003143 | 61.3672 | 61.5263 | 61.4371 | 61.4748 | 61.4893 | 61.5277 | 61.4946 | 61.534 | 123.1338 | 61.621 | 123.0284 | 61.4629 | 61.5305 | 123.0896 | 61.5083 | 122.8724 | 61.6033 | 61.6255 | 61.4979 | 61.5202
690.5938 | 123.1659 | -61.528 | 61.5738 | 0.025705 | -0.063415 | -0.025735 | -0.006703 | 0.022531 | -0.005985 | 0.033424 | 61.6241 | 0.11127 | 61.5233 | -0.033101 | 0.029923 | 61.5845 | 0.007721 | 61.3718 | 61.5537 | 61.4646 | 61.5023 | 61.5213 | 61.5505 | 61.522 | 61.5614 | 123.1521 | 61.6393 | 123.0513 | 61.4949 | 61.5579 | 123.1125 | 61.5357 | 122.8998 | 61.5942 | 61.6164 | 61.4934 | 61.5156
691.5938 | 123.2529 | -61.5234 | 61.6425 | 0.025705 | -0.054257 | -0.025735 | -0.011281 | 0.027109 | -0.005985 | 0.028846 | 61.6287 | 0.12043 | 61.5279 | -0.046838 | 0.029923 | 61.5845 | 0.007721 | 61.3627 | 61.5491 | 61.4692 | 61.4977 | 61.5122 | 61.5505 | 61.5175 | 61.5523 | 123.1521 | 61.6439 | 123.0513 | 61.4766 | 61.5534 | 123.1079 | 61.5312 | 122.8861 | 61.5987 | 61.6209 | 61.4979 | 61.5202
692.5938 | 123.2895 | -61.5005 | 61.615 | 0.025705 | -0.063415 | -0.034893 | -0.011281 | 0.022531 | -0.010563 | 0.033424 | 61.6332 | 0.11127 | 61.5233 | -0.042259 | 0.034501 | 61.5845 | 0.007721 | 61.3764 | 61.5263 | 61.4371 | 61.4657 | 61.4893 | 61.5231 | 61.49 | 61.534 | 123.1338 | 61.6118 | 123.0238 | 61.4583 | 61.535 | 123.085 | 61.5083 | 122.8769 | 61.5987 | 61.6255 | 61.4888 | 61.5156
693.5938 | 123.2849 | -61.5005 | 61.6333 | 0.016548 | -0.058836 | -0.034893 | -0.011281 | 0.017953 | -0.015142 | 0.024268 | 61.6287 | 0.10669 | 61.5279 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.3627 | 61.5171 | 61.4417 | 61.4657 | 61.4893 | 61.5185 | 61.4854 | 61.5248 | 123.1292 | 61.6072 | 123.0284 | 61.4629 | 61.535 | 123.0896 | 61.5037 | 122.8632 | 61.5942 | 61.6255 | 61.4934 | 61.5247
694.5938 | 123.3627 | -61.5005 | 61.6196 | 0.016548 | -0.063415 | -0.039471 | -0.01586 | 0.022531 | -0.005985 | 0.028846 | 61.6287 | 0.11585 | 61.5187 | -0.033101 | 0.029923 | 61.5799 | 0.003143 | 61.3672 | 61.5171 | 61.4371 | 61.4611 | 61.4847 | 61.5231 | 61.4946 | 61.5294 | 123.1292 | 61.6164 | 123.0193 | 61.4674 | 61.5305 | 123.0804 | 61.5037 | 122.8678 | 61.5987 | 61.6255 | 61.4888 | 61.5156
695.5938 | 123.3124 | -61.496 | 61.6241 | 0.025705 | -0.067994 | -0.030314 | -0.011281 | 0.031687 | -0.01972 | 0.028846 | 61.6332 | 0.11585 | 61.5279 | -0.03768 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.5217 | 61.428 | 61.4657 | 61.4847 | 61.5277 | 61.4763 | 61.5248 | 123.1292 | 61.6118 | 123.0238 | 61.4583 | 61.5305 | 123.0759 | 61.4991 | 122.8632 | 61.5987 | 61.6301 | 61.4934 | 61.5247
696.5938 | 123.3078 | -61.5051 | 61.6196 | 0.025705 | -0.058836 | -0.034893 | -0.01586 | 0.027109 | -0.015142 | 0.028846 | 61.6378 | 0.11585 | 61.5279 | -0.028522 | 0.034501 | 61.5845 | 0.007721 | 61.3718 | 61.5308 | 61.4463 | 61.4702 | 61.4893 | 61.5322 | 61.49 | 61.534 | 123.143 | 61.621 | 123.033 | 61.4766 | 61.5396 | 123.0896 | 61.5128 | 122.8769 | 61.6033 | 61.6301 | 61.4934 | 61.5202
697.5938 | 123.2986 | -61.4639 | 61.615 | 0.021127 | -0.067994 | -0.030314 | -0.006703 | 0.022531 | -0.010563 | 0.024268 | 61.6332 | 0.11585 | 61.5279 | -0.028522 | 0.029923 | 61.5891 | 0.007721 | 61.3672 | 61.4851 | 61.3959 | 61.4336 | 61.4572 | 61.4865 | 61.4534 | 61.4882 | 123.0972 | 61.5798 | 122.9918 | 61.4354 | 61.4939 | 123.053 | 61.4716 | 122.8312 | 61.6033 | 61.6255 | 61.4979 | 61.5202
698.5938 | 123.262 | -61.5005 | 61.6241 | 0.021127 | -0.063415 | -0.030314 | -0.011281 | 0.022531 | -0.015142 | 0.024268 | 61.6378 | 0.12043 | 61.5416 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3718 | 61.5217 | 61.4371 | 61.4702 | 61.4893 | 61.5231 | 61.4854 | 61.5248 | 123.1384 | 61.621 | 123.0422 | 61.4674 | 61.535 | 123.085 | 61.5083 | 122.8724 | 61.6033 | 61.6301 | 61.5071 | 61.5339
699.5938 | 123.2849 | -61.4685 | 61.6516 | 0.021127 | -0.063415 | -0.039471 | -0.01586 | 0.022531 | -0.015142 | 0.024268 | 61.6241 | 0.12958 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.4896 | 61.4051 | 61.429 | 61.4526 | 61.491 | 61.4534 | 61.4928 | 123.0926 | 61.5981 | 123.0101 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8312 | 61.585 | 61.6164 | 61.5025 | 61.5339
700.5938 | 123.2437 | -61.5189 | 61.647 | 0.021127 | -0.067994 | -0.030314 | -0.01586 | 0.022531 | -0.015142 | 0.033424 | 61.6332 | 0.11127 | 61.5324 | -0.028522 | 0.039079 | 61.5845 | -0.001436 | 61.3672 | 61.54 | 61.4509 | 61.4885 | 61.503 | 61.5414 | 61.5037 | 61.5523 | 123.1521 | 61.6301 | 123.0513 | 61.4903 | 61.5579 | 123.1033 | 61.5174 | 122.8861 | 61.5942 | 61.6347 | 61.4934 | 61.5339
701.5938 | 123.2712 | -61.496 | 61.6287 | 0.021127 | -0.067994 | -0.030314 | -0.011281 | 0.013375 | -0.015142 | 0.028846 | 61.6241 | 0.12043 | 61.5324 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.5171 | 61.428 | 61.4657 | 61.4847 | 61.5093 | 61.4808 | 61.5248 | 123.1201 | 61.6164 | 123.0284 | 61.4629 | 61.5351 | 123.0804 | 61.4991 | 122.8678 | 61.585 | 61.6209 | 61.4934 | 61.5293
702.5938 | 123.3078 | -61.496 | 61.6287 | 0.025705 | -0.058836 | -0.030314 | -0.020438 | 0.027109 | -0.010563 | 0.024268 | 61.6378 | 0.12043 | 61.5324 | -0.033101 | 0.029923 | 61.5936 | 0.003143 | 61.3718 | 61.5217 | 61.4371 | 61.4657 | 61.4755 | 61.5231 | 61.4854 | 61.5202 | 123.1338 | 61.6164 | 123.0284 | 61.4629 | 61.5259 | 123.0896 | 61.4991 | 122.8678 | 61.6079 | 61.6347 | 61.5025 | 61.5293
703.5938 | 123.2895 | -61.4868 | 61.6608 | 0.025705 | -0.067994 | -0.034893 | -0.006703 | 0.022531 | -0.024298 | 0.028846 | 61.6332 | 0.11127 | 61.5279 | -0.033101 | 0.029923 | 61.5891 | 0.003143 | 61.3672 | 61.5125 | 61.4188 | 61.4519 | 61.4801 | 61.5093 | 61.4625 | 61.5157 | 123.1201 | 61.5981 | 123.0147 | 61.4537 | 61.5167 | 123.0759 | 61.49 | 122.8541 | 61.6033 | 61.6301 | 61.4979 | 61.5247
704.5938 | 123.3582 | -61.4822 | 61.6241 | 0.01197 | -0.067994 | -0.039471 | -0.01586 | 0.017953 | -0.010563 | 0.015112 | 61.6287 | 0.11127 | 61.537 | -0.033101 | 0.043657 | 61.5845 | 0.021456 | 61.3672 | 61.4942 | 61.4142 | 61.4428 | 61.4664 | 61.5002 | 61.4717 | 61.4974 | 123.1109 | 61.5935 | 123.0193 | 61.4491 | 61.5259 | 123.0667 | 61.5037 | 122.8495 | 61.585 | 61.6072 | 61.4934 | 61.5156
705.5938 | 123.2712 | -61.5234 | 61.6379 | 0.025705 | -0.058836 | -0.039471 | -0.01586 | 0.022531 | -0.01972 | 0.024268 | 61.6378 | 0.12043 | 61.537 | -0.042259 | 0.034501 | 61.5891 | 0.012299 | 61.3627 | 61.5491 | 61.4646 | 61.484 | 61.5076 | 61.546 | 61.5037 | 61.5477 | 123.1613 | 61.6439 | 123.0605 | 61.4812 | 61.5579 | 123.1125 | 61.5357 | 122.8861 | 61.6033 | 61.6255 | 61.5025 | 61.5247
706.5938 | 123.262 | -61.5005 | 61.6196 | 0.025705 | -0.058836 | -0.039471 | -0.01586 | 0.017953 | -0.01972 | 0.024268 | 61.6287 | 0.12043 | 61.537 | -0.03768 | 0.029923 | 61.5707 | -0.001436 | 61.3672 | 61.5263 | 61.4417 | 61.4611 | 61.4847 | 61.5185 | 61.4808 | 61.5248 | 123.1292 | 61.621 | 123.0376 | 61.4629 | 61.5305 | 123.0713 | 61.4991 | 122.8678 | 61.5987 | 61.6301 | 61.5071 | 61.5385
707.5938 | 123.2574 | -61.4914 | 61.6333 | 0.025705 | -0.067994 | -0.04405 | -0.01586 | 0.022531 | -0.015142 | 0.028846 | 61.6287 | 0.10669 | 61.5324 | -0.03768 | 0.029923 | 61.5845 | 0.003143 | 61.3672 | 61.5171 | 61.4234 | 61.4473 | 61.4755 | 61.5139 | 61.4763 | 61.5202 | 123.1201 | 61.5981 | 123.0238 | 61.4537 | 61.5213 | 123.0759 | 61.4945 | 122.8586 | 61.5987 | 61.6255 | 61.5025 | 61.5293
708.5938 | 123.3353 | -61.5143 | 61.6058 | 0.021127 | -0.063415 | -0.039471 | -0.01586 | 0.013375 | -0.015142 | 0.028846 | 61.6378 | 0.12958 | 61.5324 | -0.03768 | 0.029923 | 61.5891 | 0.003143 | 61.3718 | 61.5354 | 61.4509 | 61.4748 | 61.4984 | 61.5277 | 61.4991 | 61.5431 | 123.1521 | 61.6439 | 123.0467 | 61.4766 | 61.5442 | 123.1033 | 61.5174 | 122.8861 | 61.6079 | 61.6347 | 61.5025 | 61.5293
709.5938 | 123.3261 | -61.4731 | 61.615 | 0.025705 | -0.058836 | -0.039471 | -0.01586 | 0.013375 | -0.015142 | 0.024268 | 61.6378 | 0.11585 | 61.5324 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.4988 | 61.4142 | 61.4336 | 61.4572 | 61.4865 | 61.4579 | 61.4974 | 123.1109 | 61.5889 | 123.0055 | 61.44 | 61.5076 | 123.053 | 61.4808 | 122.8403 | 61.6033 | 61.6301 | 61.4979 | 61.5247
710.5938 | 123.2986 | -61.5097 | 61.6196 | 0.025705 | -0.072572 | -0.034893 | -0.01586 | 0.022531 | -0.024298 | 0.01969 | 61.6378 | 0.12043 | 61.537 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3581 | 61.5354 | 61.4371 | 61.4748 | 61.4938 | 61.5322 | 61.4854 | 61.5294 | 123.1475 | 61.6301 | 123.0467 | 61.4766 | 61.5442 | 123.0896 | 61.5128 | 122.8678 | 61.6033 | 61.6347 | 61.5025 | 61.5339
711.5938 | 123.2895 | -61.4914 | 61.6333 | 0.025705 | -0.067994 | -0.034893 | -0.01586 | 0.017953 | -0.015142 | 0.024268 | 61.6424 | 0.11585 | 61.5233 | -0.03768 | 0.039079 | 61.5891 | 0.003143 | 61.3718 | 61.5171 | 61.4234 | 61.4565 | 61.4755 | 61.5093 | 61.4763 | 61.5157 | 123.1338 | 61.6072 | 123.0147 | 61.4537 | 61.5305 | 123.0804 | 61.4945 | 122.8632 | 61.6033 | 61.6393 | 61.4842 | 61.5202
712.5938 | 123.317 | -61.5189 | 61.6425 | 0.025705 | -0.08173 | -0.039471 | -0.01586 | 0.017953 | -0.015142 | 0.01969 | 61.6332 | 0.11585 | 61.5324 | -0.03768 | 0.034501 | 61.5845 | 0.007721 | 61.3672 | 61.5446 | 61.4371 | 61.4794 | 61.503 | 61.5368 | 61.5037 | 61.5385 | 123.1521 | 61.6347 | 123.0513 | 61.4812 | 61.5534 | 123.1033 | 61.5266 | 122.8861 | 61.5987 | 61.6255 | 61.4979 | 61.5247
713.5938 | 123.2803 | -61.4914 | 61.6379 | 0.025705 | -0.063415 | -0.034893 | -0.006703 | 0.017953 | -0.015142 | 0.028846 | 61.6378 | 0.12043 | 61.537 | -0.03768 | 0.034501 | 61.5753 | 0.007721 | 61.3627 | 61.5171 | 61.428 | 61.4565 | 61.4847 | 61.5093 | 61.4763 | 61.5202 | 123.1292 | 61.6118 | 123.0284 | 61.4537 | 61.5259 | 123.0667 | 61.4991 | 122.8541 | 61.6033 | 61.6301 | 61.5025 | 61.5293
714.5938 | 123.2529 | -61.5189 | 61.615 | 0.021127 | -0.063415 | -0.034893 | -0.025017 | 0.013375 | -0.024298 | 0.028846 | 61.6378 | 0.12043 | 61.537 | -0.033101 | 0.029923 | 61.5891 | -0.001436 | 61.3581 | 61.54 | 61.4554 | 61.484 | 61.4938 | 61.5322 | 61.4946 | 61.5477 | 123.1567 | 61.6393 | 123.0559 | 61.4858 | 61.5488 | 123.1079 | 61.5174 | 122.8769 | 61.6079 | 61.6393 | 61.5071 | 61.5385
715.5938 | 123.262 | -61.5051 | 61.6379 | 0.034862 | -0.072572 | -0.039471 | -0.01586 | 0.017953 | -0.015142 | 0.028846 | 61.6287 | 0.12043 | 61.537 | -0.03768 | 0.034501 | 61.5891 | 0.012299 | 61.3581 | 61.54 | 61.4326 | 61.4657 | 61.4893 | 61.5231 | 61.49 | 61.534 | 123.1338 | 61.6256 | 123.0422 | 61.4674 | 61.5396 | 123.0942 | 61.5174 | 122.8632 | 61.5942 | 61.6164 | 61.5025 | 61.5247
716.5938 | 123.2758 | -61.5143 | 61.6379 | 0.021127 | -0.063415 | -0.039471 | -0.01586 | 0.022531 | -0.024298 | 0.01969 | 61.6287 | 0.11127 | 61.5279 | -0.028522 | 0.039079 | 61.5707 | 0.012299 | 61.3672 | 61.5354 | 61.4509 | 61.4748 | 61.4984 | 61.5368 | 61.49 | 61.534 | 123.143 | 61.6256 | 123.0422 | 61.4858 | 61.5534 | 123.085 | 61.5266 | 122.8815 | 61.5896 | 61.6164 | 61.4888 | 61.5156
717.5938 | 123.2712 | -61.5097 | 61.6287 | 0.030283 | -0.072572 | -0.034893 | -0.01586 | 0.013375 | -0.01972 | 0.01969 | 61.6378 | 0.11585 | 61.5324 | -0.03768 | 0.039079 | 61.5891 | 0.003143 | 61.3672 | 61.54 | 61.4371 | 61.4748 | 61.4938 | 61.5231 | 61.49 | 61.5294 | 123.1475 | 61.6256 | 123.0422 | 61.472 | 61.5488 | 123.0988 | 61.5128 | 122.8769 | 61.5987 | 61.6347 | 61.4934 | 61.5293
718.5938 | 123.2849 | -61.5189 | 61.6425 | 0.016548 | -0.058836 | -0.034893 | -0.020438 | 0.022531 | -0.01972 | 0.024268 | 61.6332 | 0.11127 | 61.537 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.3672 | 61.5354 | 61.46 | 61.484 | 61.4984 | 61.5414 | 61.4991 | 61.5431 | 123.1521 | 61.6301 | 123.0559 | 61.4858 | 61.5579 | 123.0988 | 61.5266 | 122.8861 | 61.5942 | 61.6255 | 61.4979 | 61.5293
719.5938 | 123.2666 | -61.4777 | 61.6928 | 0.025705 | -0.063415 | -0.039471 | -0.01586 | 0.013375 | -0.01972 | 0.028846 | 61.6332 | 0.12958 | 61.5416 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3672 | 61.5034 | 61.4142 | 61.4382 | 61.4618 | 61.491 | 61.4579 | 61.5065 | 123.1109 | 61.6072 | 123.0193 | 61.4446 | 61.5076 | 123.0576 | 61.4854 | 122.8449 | 61.6033 | 61.6255 | 61.5117 | 61.5339
720.5938 | 123.2758 | -61.496 | 61.6608 | 0.034862 | -0.072572 | -0.039471 | -0.020438 | 0.013375 | -0.015142 | 0.01969 | 61.6378 | 0.11585 | 61.5324 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.5308 | 61.4234 | 61.4565 | 61.4755 | 61.5093 | 61.4808 | 61.5157 | 123.1338 | 61.6118 | 123.0284 | 61.4583 | 61.5259 | 123.0759 | 61.5037 | 122.8678 | 61.6079 | 61.6301 | 61.5025 | 61.5247
721.5938 | 123.2483 | -61.528 | 61.6287 | 0.025705 | -0.063415 | -0.034893 | -0.01586 | 0.013375 | -0.024298 | 0.01969 | 61.6332 | 0.12958 | 61.5416 | -0.03768 | 0.034501 | 61.5845 | 0.007721 | 61.3718 | 61.5537 | 61.4646 | 61.4931 | 61.5122 | 61.5414 | 61.5037 | 61.5477 | 123.1613 | 61.6576 | 123.0696 | 61.4903 | 61.5625 | 123.1125 | 61.5357 | 122.8998 | 61.5987 | 61.6255 | 61.5071 | 61.5339
722.5938 | 123.2529 | -61.5143 | 61.6516 | 0.021127 | -0.072572 | -0.030314 | -0.011281 | 0.017953 | -0.01972 | 0.015112 | 61.6287 | 0.11585 | 61.5279 | -0.042259 | 0.039079 | 61.5799 | 0.003143 | 61.3718 | 61.5354 | 61.4417 | 61.484 | 61.503 | 61.5322 | 61.4946 | 61.5294 | 123.143 | 61.6301 | 123.0422 | 61.472 | 61.5534 | 123.0942 | 61.5174 | 122.8861 | 61.5896 | 61.6255 | 61.4888 | 61.5247
723.5938 | 123.2117 | -61.5189 | 61.5555 | 0.025705 | -0.08173 | -0.039471 | -0.025017 | 0.013375 | -0.024298 | 0.01969 | 61.6378 | 0.10669 | 61.5279 | -0.03768 | 0.034501 | 61.5891 | 0.007721 | 61.3672 | 61.5446 | 61.4371 | 61.4794 | 61.4938 | 61.5322 | 61.4946 | 61.5385 | 123.1567 | 61.6255 | 123.0467 | 61.4812 | 61.5534 | 123.1079 | 61.5266 | 122.8861 | 61.6033 | 61.6301 | 61.4934 | 61.5202
724.5938 | 123.262 | -61.5097 | 61.647 | 0.025705 | -0.072572 | -0.039471 | -0.025017 | 0.017953 | -0.024298 | 0.028846 | 61.6287 | 0.12043 | 61.5324 | -0.033101 | 0.034501 | 61.5799 | 0.012299 | 61.3764 | 61.5354 | 61.4371 | 61.4702 | 61.4847 | 61.5277 | 61.4854 | 61.5386 | 123.1384 | 61.6301 | 123.0422 | 61.4766 | 61.5442 | 123.0896 | 61.522 | 122.8861 | 61.5942 | 61.6164 | 61.4979 | 61.5202
725.5938 | 123.2986 | -61.4822 | 61.6379 | 0.021127 | -0.072572 | -0.039471 | -0.025017 | 0.022531 | -0.024298 | 0.015112 | 61.6378 | 0.12043 | 61.537 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3718 | 61.5034 | 61.4097 | 61.4428 | 61.4572 | 61.5048 | 61.4579 | 61.4974 | 123.1201 | 61.6027 | 123.0193 | 61.4446 | 61.5213 | 123.0667 | 61.49 | 122.8541 | 61.5987 | 61.6301 | 61.4979 | 61.5293
726.5938 | 123.111 | -61.5189 | 61.5692 | 0.025705 | -0.077151 | -0.039471 | -0.020438 | 0.017953 | -0.024298 | 0.01969 | 61.6378 | 0.12958 | 61.537 | -0.033101 | 0.034501 | 61.5799 | -0.001436 | 61.3718 | 61.5446 | 61.4417 | 61.4794 | 61.4984 | 61.5368 | 61.4946 | 61.5385 | 123.1567 | 61.6484 | 123.0559 | 61.4858 | 61.5534 | 123.0988 | 61.5174 | 122.8907 | 61.6033 | 61.6393 | 61.5025 | 61.5385
727.5938 | 123.2346 | -61.5234 | 61.6516 | 0.025705 | -0.067994 | -0.048628 | -0.011281 | 0.013375 | -0.028877 | 0.015112 | 61.6378 | 0.11585 | 61.5324 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3764 | 61.5491 | 61.4554 | 61.4748 | 61.5122 | 61.5368 | 61.4946 | 61.5385 | 123.1613 | 61.6393 | 123.0559 | 61.4858 | 61.5625 | 123.1079 | 61.5312 | 122.8998 | 61.5987 | 61.6301 | 61.4934 | 61.5247
728.5938 | 123.2483 | -61.5005 | 61.6379 | 0.021127 | -0.067994 | -0.034893 | -0.029595 | 0.008797 | -0.024298 | 0.024268 | 61.6424 | 0.12501 | 61.5324 | -0.028522 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.5217 | 61.4326 | 61.4657 | 61.471 | 61.5093 | 61.4763 | 61.5248 | 123.143 | 61.6256 | 123.033 | 61.472 | 61.535 | 123.0804 | 61.5083 | 122.8724 | 61.6079 | 61.6347 | 61.4979 | 61.5247
729.5938 | 123.2346 | -61.5005 | 61.6333 | 0.021127 | -0.072572 | -0.039471 | -0.025017 | 0.008797 | -0.01972 | 0.01969 | 61.6378 | 0.10669 | 61.5324 | -0.03768 | 0.039079 | 61.5799 | 0.012299 | 61.3764 | 61.5217 | 61.428 | 61.4611 | 61.4755 | 61.5093 | 61.4808 | 61.5202 | 123.1384 | 61.6072 | 123.033 | 61.4629 | 61.5396 | 123.0804 | 61.5128 | 122.8769 | 61.5987 | 61.6255 | 61.4934 | 61.5202
730.5938 | 123.2483 | -61.4868 | 61.6425 | 0.030283 | -0.063415 | -0.039471 | -0.025017 | 0.013375 | -0.028877 | 0.024268 | 61.6424 | 0.12501 | 61.537 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.5171 | 61.4234 | 61.4473 | 61.4618 | 61.5002 | 61.4579 | 61.5111 | 123.1292 | 61.6118 | 123.0238 | 61.4491 | 61.5213 | 123.0667 | 61.4945 | 122.8541 | 61.6079 | 61.6347 | 61.5025 | 61.5293
731.5938 | 123.2803 | -61.4868 | 61.6516 | 0.025705 | -0.08173 | -0.039471 | -0.020438 | 0.017953 | -0.01972 | 0.01969 | 61.6378 | 0.11585 | 61.5279 | -0.03768 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.5125 | 61.4051 | 61.4473 | 61.4664 | 61.5048 | 61.4671 | 61.5065 | 123.1246 | 61.6027 | 123.0147 | 61.4491 | 61.5259 | 123.0667 | 61.4945 | 122.8586 | 61.5987 | 61.6301 | 61.4888 | 61.5202
732.5938 | 123.3032 | -61.4731 | 61.6562 | 0.021127 | -0.077151 | -0.039471 | -0.020438 | 0.004219 | -0.024298 | 0.024268 | 61.6378 | 0.12043 | 61.537 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3672 | 61.4942 | 61.3959 | 61.4336 | 61.4526 | 61.4773 | 61.4488 | 61.4974 | 123.1109 | 61.5935 | 123.0101 | 61.44 | 61.5076 | 123.0576 | 61.4808 | 122.8403 | 61.6033 | 61.6301 | 61.5025 | 61.5293
733.5938 | 123.3353 | -61.4685 | 61.6608 | 0.025705 | -0.077151 | -0.048628 | -0.025017 | 0.013375 | -0.024298 | 0.01969 | 61.6424 | 0.11585 | 61.537 | -0.028522 | 0.043657 | 61.5799 | 0.003143 | 61.3718 | 61.4942 | 61.3914 | 61.4199 | 61.4435 | 61.4819 | 61.4442 | 61.4882 | 123.1109 | 61.5844 | 123.0055 | 61.44 | 61.5122 | 123.0484 | 61.4716 | 122.8403 | 61.5987 | 61.6393 | 61.4934 | 61.5339
734.5938 | 123.3215 | -61.4822 | 61.6516 | 0.021127 | -0.058836 | -0.039471 | -0.034174 | 0.017953 | -0.024298 | 0.015112 | 61.6378 | 0.12958 | 61.5416 | -0.042259 | 0.034501 | 61.5891 | 0.003143 | 61.3764 | 61.5034 | 61.4234 | 61.4428 | 61.4481 | 61.5002 | 61.4579 | 61.4974 | 123.1201 | 61.6118 | 123.0238 | 61.44 | 61.5167 | 123.0713 | 61.4854 | 122.8586 | 61.6033 | 61.6347 | 61.5071 | 61.5385
735.5938 | 123.3307 | -61.4914 | 61.647 | 0.016548 | -0.072572 | -0.048628 | -0.029595 | 0.008797 | -0.024298 | 0.010533 | 61.6424 | 0.11585 | 61.5233 | -0.028522 | 0.034501 | 61.5891 | 0.007721 | 61.3718 | 61.5079 | 61.4188 | 61.4428 | 61.4618 | 61.5002 | 61.4671 | 61.5019 | 123.1338 | 61.6072 | 123.0147 | 61.4629 | 61.5259 | 123.0804 | 61.4991 | 122.8632 | 61.6079 | 61.6347 | 61.4888 | 61.5156
736.5938 | 123.3261 | -61.4914 | 61.6562 | 0.025705 | -0.072572 | -0.048628 | -0.025017 | 0.013375 | -0.024298 | 0.01969 | 61.6424 | 0.12043 | 61.537 | -0.03768 | 0.034501 | 61.5799 | 0.007721 | 61.3718 | 61.5171 | 61.4188 | 61.4428 | 61.4664 | 61.5048 | 61.4671 | 61.5111 | 123.1338 | 61.6118 | 123.0284 | 61.4537 | 61.5259 | 123.0713 | 61.4991 | 122.8632 | 61.6079 | 61.6347 | 61.5025 | 61.5293
737.5938 | 123.262 | -61.4868 | 61.6516 | 0.021127 | -0.077151 | -0.04405 | -0.029595 | 0.008797 | -0.028877 | 0.01969 | 61.6378 | 0.11585 | 61.537 | -0.03768 | 0.029923 | 61.5845 | -0.001436 | 61.3764 | 61.5079 | 61.4097 | 61.4428 | 61.4572 | 61.4956 | 61.4579 | 61.5065 | 123.1246 | 61.6027 | 123.0238 | 61.4491 | 61.5167 | 123.0713 | 61.4854 | 122.8632 | 61.6079 | 61.6393 | 61.5071 | 61.5385
738.5938 | 123.3398 | -61.4777 | 61.6699 | 0.025705 | -0.072572 | -0.04405 | -0.025017 | 0.008797 | -0.01972 | 0.015112 | 61.6378 | 0.12501 | 61.5324 | -0.03768 | 0.039079 | 61.5845 | 0.016878 | 61.3764 | 61.5034 | 61.4051 | 61.4336 | 61.4526 | 61.4865 | 61.4579 | 61.4928 | 123.1155 | 61.6027 | 123.0101 | 61.44 | 61.5167 | 123.0621 | 61.4945 | 122.8541 | 61.5987 | 61.6209 | 61.4934 | 61.5156
739.5938 | 123.2849 | -61.4685 | 61.6791 | 0.016548 | -0.077151 | -0.048628 | -0.025017 | -0.000359 | -0.028877 | 0.015112 | 61.6378 | 0.12043 | 61.5416 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.4851 | 61.3914 | 61.4199 | 61.4435 | 61.4681 | 61.4396 | 61.4836 | 123.1063 | 61.5889 | 123.0101 | 61.4354 | 61.503 | 123.0484 | 61.4716 | 122.8357 | 61.6033 | 61.6347 | 61.5071 | 61.5385
740.5938 | 123.3078 | -61.4777 | 61.6745 | 0.025705 | -0.077151 | -0.04405 | -0.029595 | 0.008797 | -0.024298 | 0.015112 | 61.6424 | 0.11127 | 61.537 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.381 | 61.5034 | 61.4005 | 61.4336 | 61.4481 | 61.4865 | 61.4534 | 61.4928 | 123.1201 | 61.5889 | 123.0147 | 61.4446 | 61.5167 | 123.0576 | 61.4854 | 122.8586 | 61.6033 | 61.6347 | 61.4979 | 61.5293
741.5938 | 123.3215 | -61.4868 | 61.6562 | 0.021127 | -0.072572 | -0.048628 | -0.034174 | 0.004219 | -0.028877 | 0.015112 | 61.6424 | 0.12043 | 61.5279 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3718 | 61.5079 | 61.4142 | 61.4382 | 61.4526 | 61.491 | 61.4579 | 61.5019 | 123.1292 | 61.6072 | 123.0147 | 61.4537 | 61.5259 | 123.0667 | 61.49 | 122.8586 | 61.6033 | 61.6393 | 61.4888 | 61.5247
742.5938 | 123.3444 | -61.4822 | 61.6608 | 0.021127 | -0.077151 | -0.048628 | -0.029595 | 0.008797 | -0.028877 | 0.015112 | 61.6378 | 0.11127 | 61.5324 | -0.03768 | 0.029923 | 61.5891 | -0.001436 | 61.3764 | 61.5034 | 61.4051 | 61.4336 | 61.4526 | 61.491 | 61.4534 | 61.4974 | 123.1201 | 61.5935 | 123.0147 | 61.4446 | 61.5122 | 123.0713 | 61.4808 | 122.8586 | 61.6079 | 61.6393 | 61.5025 | 61.5339
743.5938 | 123.349 | -61.4365 | 61.647 | 0.025705 | -0.090888 | -0.053207 | -0.029595 | 0.004219 | -0.024298 | 0.015112 | 61.6424 | 0.12043 | 61.5416 | -0.03768 | 0.034501 | 61.5936 | -0.001436 | 61.3672 | 61.4622 | 61.3456 | 61.3833 | 61.4069 | 61.4407 | 61.4122 | 61.4516 | 123.0789 | 61.5569 | 122.9781 | 61.3988 | 61.471 | 123.0301 | 61.435 | 122.8037 | 61.6079 | 61.6438 | 61.5071 | 61.543
744.5938 | 123.3627 | -61.4731 | 61.6653 | 0.021127 | -0.077151 | -0.04405 | -0.025017 | 0.004219 | -0.033455 | 0.010533 | 61.6378 | 0.13416 | 61.537 | -0.023943 | 0.039079 | 61.5753 | 0.007721 | 61.3718 | 61.4942 | 61.3959 | 61.429 | 61.4481 | 61.4773 | 61.4396 | 61.4836 | 123.1109 | 61.6072 | 123.0101 | 61.4491 | 61.5122 | 123.0484 | 61.4808 | 122.8449 | 61.5987 | 61.6301 | 61.4979 | 61.5293
745.5938 | 123.2803 | -61.4868 | 61.6745 | 0.025705 | -0.08173 | -0.039471 | -0.029595 | -0.000359 | -0.028877 | 0.010533 | 61.6378 | 0.12501 | 61.5416 | -0.028522 | 0.039079 | 61.5845 | 0.012299 | 61.3764 | 61.5125 | 61.4051 | 61.4473 | 61.4572 | 61.4865 | 61.4579 | 61.4973 | 123.1246 | 61.6118 | 123.0284 | 61.4583 | 61.5259 | 123.0713 | 61.4991 | 122.8632 | 61.5987 | 61.6255 | 61.5025 | 61.5293
746.5938 | 123.3032 | -61.4777 | 61.6745 | 0.021127 | -0.077151 | -0.04405 | -0.038752 | 0.004219 | -0.024298 | 0.015112 | 61.6332 | 0.12043 | 61.5462 | -0.033101 | 0.048236 | 61.5845 | 0.007721 | 61.3764 | 61.4988 | 61.4005 | 61.4336 | 61.4389 | 61.4819 | 61.4534 | 61.4928 | 123.1109 | 61.5981 | 123.0238 | 61.4446 | 61.5259 | 123.0621 | 61.4854 | 122.8541 | 61.585 | 61.6255 | 61.4979 | 61.5385
747.5938 | 123.262 | -61.4822 | 61.6837 | 0.025705 | -0.086309 | -0.048628 | -0.020438 | -0.000359 | -0.033455 | 0.01969 | 61.6424 | 0.12501 | 61.537 | -0.028522 | 0.039079 | 61.5799 | 0.003143 | 61.3718 | 61.5079 | 61.3959 | 61.4336 | 61.4618 | 61.4819 | 61.4488 | 61.5019 | 123.1246 | 61.6072 | 123.0193 | 61.4537 | 61.5213 | 123.0621 | 61.4854 | 122.8541 | 61.6033 | 61.6393 | 61.4979 | 61.5339
748.5938 | 123.3124 | -61.4868 | 61.6699 | 0.025705 | -0.08173 | -0.053207 | -0.025017 | 0.004219 | -0.038034 | 0.010533 | 61.6378 | 0.12501 | 61.537 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.5125 | 61.4051 | 61.4336 | 61.4618 | 61.491 | 61.4488 | 61.4973 | 123.1246 | 61.6118 | 123.0238 | 61.4537 | 61.5213 | 123.0667 | 61.49 | 122.8541 | 61.6033 | 61.6347 | 61.5025 | 61.5339
749.5938 | 123.2941 | -61.4685 | 61.6837 | 0.025705 | -0.077151 | -0.053207 | -0.029595 | 0.008797 | -0.038034 | 0.005955 | 61.6424 | 0.12958 | 61.5462 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.4942 | 61.3914 | 61.4153 | 61.4389 | 61.4773 | 61.4305 | 61.4745 | 123.1109 | 61.5981 | 123.0147 | 61.4308 | 61.5076 | 123.053 | 61.4762 | 122.8312 | 61.6033 | 61.6347 | 61.5071 | 61.5385
750.5938 | 123.349 | -61.4731 | 61.6791 | 0.030283 | -0.08173 | -0.048628 | -0.034174 | 0.004219 | -0.038034 | 0.010533 | 61.6424 | 0.13416 | 61.537 | -0.03768 | 0.029923 | 61.5799 | -0.006014 | 61.3672 | 61.5034 | 61.3914 | 61.4245 | 61.4389 | 61.4773 | 61.435 | 61.4836 | 123.1155 | 61.6072 | 123.0101 | 61.4354 | 61.503 | 123.053 | 61.4671 | 122.8403 | 61.6125 | 61.6484 | 61.5071 | 61.543
751.5938 | 123.2712 | -61.4868 | 61.6608 | 0.025705 | -0.08173 | -0.048628 | -0.029595 | 0.004219 | -0.028877 | 0.001377 | 61.6424 | 0.12043 | 61.5279 | -0.023943 | 0.029923 | 61.5753 | 0.007721 | 61.3718 | 61.5125 | 61.4051 | 61.4382 | 61.4572 | 61.491 | 61.4579 | 61.4882 | 123.1292 | 61.6072 | 123.0147 | 61.4629 | 61.5167 | 123.0621 | 61.4945 | 122.8586 | 61.6125 | 61.6347 | 61.4979 | 61.5202
752.5938 | 123.2803 | -61.4731 | 61.6745 | 0.016548 | -0.077151 | -0.057786 | -0.038752 | 0.004219 | -0.038034 | 0.001377 | 61.6332 | 0.12501 | 61.5416 | -0.03768 | 0.029923 | 61.5799 | 0.007721 | 61.3718 | 61.4896 | 61.3959 | 61.4153 | 61.4343 | 61.4773 | 61.435 | 61.4745 | 123.1063 | 61.5981 | 123.0147 | 61.4354 | 61.503 | 123.053 | 61.4808 | 122.8449 | 61.6033 | 61.6255 | 61.5117 | 61.5339
753.5938 | 123.3398 | -61.4731 | 61.6653 | 0.021127 | -0.077151 | -0.053207 | -0.034174 | -0.004937 | -0.033455 | 0.005955 | 61.6332 | 0.12958 | 61.5416 | -0.028522 | 0.029923 | 61.5753 | 0.007721 | 61.3718 | 61.4942 | 61.3959 | 61.4199 | 61.4389 | 61.4681 | 61.4396 | 61.479 | 123.1063 | 61.6027 | 123.0147 | 61.4446 | 61.503 | 123.0484 | 61.4808 | 122.8449 | 61.6033 | 61.6255 | 61.5117 | 61.5339
754.5938 | 123.2895 | -61.4868 | 61.6653 | 0.016548 | -0.090888 | -0.062364 | -0.038752 | 0.004219 | -0.042612 | 0.005955 | 61.6378 | 0.13416 | 61.5324 | -0.033101 | 0.043657 | 61.5799 | 0.007721 | 61.3718 | 61.5034 | 61.3959 | 61.4245 | 61.4481 | 61.491 | 61.4442 | 61.4928 | 123.1246 | 61.621 | 123.0193 | 61.4537 | 61.5305 | 123.0667 | 61.4945 | 122.8586 | 61.5942 | 61.6301 | 61.4888 | 61.5247
755.5938 | 123.23 | -61.5143 | 61.647 | 0.021127 | -0.086309 | -0.053207 | -0.034174 | -0.004937 | -0.033455 | 0.010533 | 61.6332 | 0.12043 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | -0.001436 | 61.381 | 61.5354 | 61.428 | 61.4611 | 61.4801 | 61.5093 | 61.4808 | 61.5248 | 123.1475 | 61.6347 | 123.0467 | 61.4812 | 61.5488 | 123.0988 | 61.5128 | 122.8953 | 61.5987 | 61.6347 | 61.4979 | 61.5339
756.5938 | 123.2666 | -61.4914 | 61.6882 | 0.025705 | -0.08173 | -0.057786 | -0.038752 | -0.004937 | -0.033455 | 0.005955 | 61.6378 | 0.12043 | 61.5324 | -0.028522 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.5171 | 61.4097 | 61.4336 | 61.4526 | 61.4865 | 61.4579 | 61.4973 | 123.1292 | 61.6118 | 123.0238 | 61.4629 | 61.5305 | 123.0759 | 61.4991 | 122.8586 | 61.5987 | 61.6301 | 61.4934 | 61.5247
757.5938 | 123.2849 | -61.4731 | 61.6974 | 0.016548 | -0.086309 | -0.057786 | -0.043331 | -0.004937 | -0.038034 | 0.010533 | 61.6378 | 0.12043 | 61.537 | -0.033101 | 0.043657 | 61.5891 | 0.007721 | 61.381 | 61.4896 | 61.3868 | 61.4153 | 61.4298 | 61.4681 | 61.435 | 61.4836 | 123.1109 | 61.5935 | 123.0101 | 61.44 | 61.5167 | 123.0621 | 61.4808 | 122.8541 | 61.5942 | 61.6301 | 61.4934 | 61.5293
758.5938 | 123.3398 | -61.4502 | 61.6653 | 0.021127 | -0.086309 | -0.057786 | -0.038752 | -0.009515 | -0.04719 | 0.010533 | 61.6332 | 0.12958 | 61.5416 | -0.028522 | 0.043657 | 61.5845 | -0.001436 | 61.3764 | 61.4713 | 61.3639 | 61.3924 | 61.4114 | 61.4407 | 61.403 | 61.4607 | 123.0834 | 61.5798 | 122.9918 | 61.4217 | 61.4939 | 123.0347 | 61.4488 | 122.8266 | 61.5896 | 61.6347 | 61.4979 | 61.543
759.5938 | 123.3765 | -61.4822 | 61.6241 | 0.021127 | -0.090888 | -0.062364 | -0.047909 | -0.004937 | -0.038034 | -0.003201 | 61.6378 | 0.11127 | 61.5279 | -0.042259 | 0.039079 | 61.5845 | 0.003143 | 61.3672 | 61.5034 | 61.3914 | 61.4199 | 61.4343 | 61.4773 | 61.4442 | 61.479 | 123.1201 | 61.5935 | 123.0101 | 61.44 | 61.5213 | 123.0667 | 61.4854 | 122.8495 | 61.5987 | 61.6347 | 61.4888 | 61.5247
760.5938 | 123.4314 | -61.4685 | 61.647 | 0.021127 | -0.090888 | -0.057786 | -0.043331 | -0.004937 | -0.051769 | -0.003201 | 61.6332 | 0.12501 | 61.537 | -0.033101 | 0.029923 | 61.5891 | 0.007721 | 61.3718 | 61.4896 | 61.3776 | 61.4107 | 61.4252 | 61.4636 | 61.4167 | 61.4653 | 123.1018 | 61.5935 | 123.0055 | 61.4354 | 61.4984 | 123.0576 | 61.4762 | 122.8403 | 61.6033 | 61.6255 | 61.5071 | 61.5293
761.5938 | 123.4314 | -61.4731 | 61.6333 | 0.025705 | -0.090888 | -0.062364 | -0.043331 | -0.018671 | -0.04719 | -0.003201 | 61.6378 | 0.12043 | 61.5324 | -0.033101 | 0.043657 | 61.5845 | 0.007721 | 61.3672 | 61.4988 | 61.3822 | 61.4107 | 61.4298 | 61.4544 | 61.4259 | 61.4699 | 123.1109 | 61.5935 | 123.0055 | 61.44 | 61.5167 | 123.0576 | 61.4808 | 122.8403 | 61.5942 | 61.6301 | 61.4888 | 61.5247
762.5938 | 123.317 | -61.4639 | 61.6608 | 0.016548 | -0.095467 | -0.062364 | -0.043331 | -0.000359 | -0.04719 | 0.005955 | 61.6332 | 0.12501 | 61.5324 | -0.033101 | 0.043657 | 61.5891 | 0.012299 | 61.3672 | 61.4805 | 61.3685 | 61.4016 | 61.4206 | 61.4636 | 61.4167 | 61.4699 | 123.0972 | 61.5889 | 122.9964 | 61.4308 | 61.5076 | 123.053 | 61.4762 | 122.8312 | 61.5896 | 61.6209 | 61.4888 | 61.5202
763.5938 | 123.349 | -61.4456 | 61.647 | 0.021127 | -0.090888 | -0.066943 | -0.052488 | -0.014093 | -0.04719 | 0.001377 | 61.6332 | 0.12043 | 61.5416 | -0.03768 | 0.039079 | 61.5891 | 0.007721 | 61.3718 | 61.4667 | 61.3547 | 61.3787 | 61.3931 | 61.4315 | 61.3984 | 61.447 | 123.0789 | 61.566 | 122.9872 | 61.4079 | 61.4847 | 123.0347 | 61.4533 | 122.8174 | 61.5942 | 61.6255 | 61.5025 | 61.5339
764.5938 | 123.3536 | -61.4777 | 61.6287 | 0.025705 | -0.086309 | -0.062364 | -0.047909 | -0.014093 | -0.042612 | 0.001377 | 61.6378 | 0.12043 | 61.537 | -0.033101 | 0.034501 | 61.5891 | 0.012299 | 61.3627 | 61.5034 | 61.3914 | 61.4153 | 61.4298 | 61.4636 | 61.435 | 61.479 | 123.1155 | 61.5981 | 123.0147 | 61.4446 | 61.5122 | 123.0667 | 61.49 | 122.8403 | 61.6033 | 61.6255 | 61.5025 | 61.5247
765.5938 | 123.4085 | -61.4777 | 61.6196 | 0.016548 | -0.090888 | -0.062364 | -0.043331 | -0.018671 | -0.051769 | -0.007779 | 61.6332 | 0.12501 | 61.5324 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3764 | 61.4942 | 61.3868 | 61.4153 | 61.4343 | 61.459 | 61.4259 | 61.4699 | 123.1109 | 61.6027 | 123.0101 | 61.4446 | 61.5167 | 123.0621 | 61.4854 | 122.8541 | 61.5942 | 61.6255 | 61.4934 | 61.5247
766.5938 | 123.3765 | -61.4914 | 61.6379 | 0.016548 | -0.095467 | -0.062364 | -0.043331 | -0.014093 | -0.04719 | -0.003201 | 61.6378 | 0.11127 | 61.5324 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.3672 | 61.5079 | 61.3959 | 61.429 | 61.4481 | 61.4773 | 61.4442 | 61.4882 | 123.1292 | 61.6027 | 123.0238 | 61.4583 | 61.5305 | 123.0713 | 61.4991 | 122.8586 | 61.5987 | 61.6301 | 61.4934 | 61.5247
767.5938 | 123.3719 | -61.4868 | 61.6425 | 0.021127 | -0.095467 | -0.062364 | -0.052488 | -0.014093 | -0.051769 | 0.001377 | 61.6424 | 0.11127 | 61.5324 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.5079 | 61.3913 | 61.4245 | 61.4343 | 61.4727 | 61.435 | 61.4882 | 123.1292 | 61.5981 | 123.0193 | 61.4537 | 61.5259 | 123.0667 | 61.49 | 122.8541 | 61.6033 | 61.6393 | 61.4934 | 61.5293
768.5938 | 123.4177 | -61.4914 | 61.6379 | 0.021127 | -0.095467 | -0.062364 | -0.052488 | -0.014093 | -0.04719 | -0.003201 | 61.6378 | 0.12501 | 61.5462 | -0.028522 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.5125 | 61.3959 | 61.429 | 61.4389 | 61.4773 | 61.4442 | 61.4882 | 123.1292 | 61.6164 | 123.0376 | 61.4629 | 61.5305 | 123.0759 | 61.4991 | 122.8541 | 61.5987 | 61.6301 | 61.5071 | 61.5385
769.5938 | 123.381 | -61.4136 | 61.6196 | 0.021127 | -0.10004 | -0.066943 | -0.061645 | -0.014093 | -0.051769 | 0.001377 | 61.6287 | 0.12043 | 61.5324 | -0.03768 | 0.034501 | 61.5891 | -0.001436 | 61.3672 | 61.4347 | 61.3135 | 61.3466 | 61.3519 | 61.3995 | 61.3618 | 61.415 | 123.0422 | 61.534 | 122.946 | 61.3759 | 61.4481 | 123.0026 | 61.4121 | 122.7808 | 61.5942 | 61.6301 | 61.4979 | 61.5339
770.5938 | 123.3856 | -61.4639 | 61.6333 | 0.025705 | -0.095467 | -0.071521 | -0.052488 | -0.014093 | -0.060926 | -0.012357 | 61.6424 | 0.12501 | 61.5324 | -0.028522 | 0.034501 | 61.5845 | 0.003143 | 61.3672 | 61.4896 | 61.3685 | 61.3924 | 61.4114 | 61.4498 | 61.403 | 61.4516 | 123.1063 | 61.5889 | 122.9964 | 61.4354 | 61.4984 | 123.0484 | 61.4671 | 122.8312 | 61.6079 | 61.6393 | 61.4979 | 61.5293
771.5938 | 123.3902 | -61.4639 | 61.6196 | 0.01197 | -0.095467 | -0.066943 | -0.047909 | -0.018671 | -0.051769 | -0.007779 | 61.6424 | 0.12501 | 61.5279 | -0.028522 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.4759 | 61.3685 | 61.397 | 61.416 | 61.4453 | 61.4122 | 61.4561 | 123.1063 | 61.5889 | 122.9918 | 61.4354 | 61.503 | 123.0484 | 61.4716 | 122.8312 | 61.6033 | 61.6347 | 61.4888 | 61.5202
772.5938 | 123.3994 | -61.4685 | 61.6333 | 0.021127 | -0.095467 | -0.0761 | -0.052488 | -0.023249 | -0.04719 | -0.003201 | 61.6378 | 0.12501 | 61.5462 | -0.033101 | 0.039079 | 61.5845 | -0.006014 | 61.3672 | 61.4896 | 61.373 | 61.3924 | 61.416 | 61.4453 | 61.4213 | 61.4653 | 123.1063 | 61.5935 | 123.0147 | 61.4354 | 61.5076 | 123.053 | 61.4625 | 122.8357 | 61.5987 | 61.6438 | 61.5071 | 61.5522
773.5938 | 123.3536 | -61.4639 | 61.615 | 0.021127 | -0.10004 | -0.0761 | -0.057066 | -0.018671 | -0.04719 | -0.007779 | 61.6378 | 0.12958 | 61.5416 | -0.028522 | 0.039079 | 61.5799 | 0.012299 | 61.3672 | 61.4851 | 61.3639 | 61.3878 | 61.4069 | 61.4453 | 61.4167 | 61.4561 | 123.1018 | 61.5935 | 123.0055 | 61.4354 | 61.503 | 123.0438 | 61.4762 | 122.8312 | 61.5987 | 61.6255 | 61.5025 | 61.5293
774.5938 | 123.349 | -61.4731 | 61.5967 | 0.021127 | -0.10462 | -0.071521 | -0.052488 | -0.023249 | -0.056347 | -0.012357 | 61.6378 | 0.12043 | 61.5416 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3627 | 61.4942 | 61.3685 | 61.4016 | 61.4206 | 61.4498 | 61.4167 | 61.4607 | 123.1109 | 61.5935 | 123.0147 | 61.44 | 61.5076 | 123.053 | 61.4808 | 122.8357 | 61.6033 | 61.6301 | 61.5071 | 61.5339
775.5938 | 123.3582 | -61.5143 | 61.6241 | 0.021127 | -0.095467 | -0.071521 | -0.052488 | -0.018671 | -0.056347 | -0.012357 | 61.6424 | 0.12043 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.5354 | 61.4188 | 61.4428 | 61.4618 | 61.4956 | 61.4579 | 61.5019 | 123.1567 | 61.6347 | 123.0559 | 61.4812 | 61.5534 | 123.0988 | 61.522 | 122.8769 | 61.6033 | 61.6347 | 61.5025 | 61.5339
776.5938 | 123.3902 | -61.4777 | 61.6058 | 0.016548 | -0.095467 | -0.080679 | -0.052488 | -0.027827 | -0.051769 | -0.003201 | 61.647 | 0.12043 | 61.537 | -0.033101 | 0.034501 | 61.5891 | 0.003143 | 61.3672 | 61.4942 | 61.3822 | 61.397 | 61.4252 | 61.4498 | 61.4259 | 61.4745 | 123.1246 | 61.5981 | 123.0147 | 61.4446 | 61.5122 | 123.0667 | 61.4808 | 122.8449 | 61.6125 | 61.6438 | 61.5025 | 61.5339
777.5938 | 123.3673 | -61.4685 | 61.615 | 0.021127 | -0.10462 | -0.066943 | -0.057066 | -0.023249 | -0.056347 | -0.016936 | 61.6332 | 0.11585 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3718 | 61.4896 | 61.3639 | 61.4016 | 61.4114 | 61.4453 | 61.4122 | 61.4516 | 123.1018 | 61.5844 | 123.0101 | 61.4354 | 61.5076 | 123.053 | 61.4762 | 122.8403 | 61.5942 | 61.6255 | 61.5025 | 61.5339
778.5938 | 123.3856 | -61.4685 | 61.6333 | 0.021127 | -0.10462 | -0.0761 | -0.057066 | -0.018671 | -0.056347 | -0.012357 | 61.6332 | 0.12043 | 61.537 | -0.028522 | 0.029923 | 61.5845 | 0.007721 | 61.3672 | 61.4896 | 61.3639 | 61.3924 | 61.4114 | 61.4498 | 61.4122 | 61.4561 | 123.1018 | 61.5889 | 123.0055 | 61.44 | 61.4984 | 123.053 | 61.4762 | 122.8357 | 61.6033 | 61.6255 | 61.5071 | 61.5293
779.5938 | 123.3856 | -61.4777 | 61.6196 | 0.016548 | -0.10462 | -0.071521 | -0.061645 | -0.014093 | -0.051769 | -0.012357 | 61.6424 | 0.11127 | 61.5324 | -0.028522 | 0.039079 | 61.5936 | 0.003143 | 61.3627 | 61.4942 | 61.373 | 61.4061 | 61.416 | 61.4636 | 61.4259 | 61.4653 | 123.1201 | 61.5889 | 123.0101 | 61.4491 | 61.5167 | 123.0713 | 61.4808 | 122.8403 | 61.6033 | 61.6393 | 61.4934 | 61.5293
780.5938 | 123.3719 | -61.4594 | 61.6058 | 0.021127 | -0.10462 | -0.080679 | -0.057066 | -0.023249 | -0.065504 | -0.012357 | 61.6378 | 0.12043 | 61.5279 | -0.028522 | 0.039079 | 61.5799 | 0.007721 | 61.3672 | 61.4805 | 61.3547 | 61.3787 | 61.4023 | 61.4361 | 61.3938 | 61.447 | 123.0972 | 61.5798 | 122.9872 | 61.4308 | 61.4984 | 123.0392 | 61.4671 | 122.8266 | 61.5987 | 61.6301 | 61.4888 | 61.5202
781.5938 | 123.3627 | -61.4914 | 61.6241 | 0.025705 | -0.11378 | -0.0761 | -0.061645 | -0.018671 | -0.060926 | -0.012357 | 61.647 | 0.12043 | 61.5416 | -0.03768 | 0.039079 | 61.5845 | 0.003143 | 61.3627 | 61.5171 | 61.3776 | 61.4153 | 61.4297 | 61.4727 | 61.4305 | 61.479 | 123.1384 | 61.6118 | 123.033 | 61.4537 | 61.5305 | 123.0759 | 61.4945 | 122.8541 | 61.6079 | 61.6438 | 61.5025 | 61.5385
782.5938 | 123.3673 | -61.4639 | 61.6196 | 0.021127 | -0.1092 | -0.0761 | -0.066223 | -0.027827 | -0.060926 | -0.016936 | 61.6378 | 0.12958 | 61.537 | -0.033101 | 0.039079 | 61.5936 | 0.003143 | 61.3718 | 61.4851 | 61.3547 | 61.3878 | 61.3977 | 61.4361 | 61.403 | 61.447 | 123.1018 | 61.5935 | 123.001 | 61.4308 | 61.503 | 123.0576 | 61.4671 | 122.8357 | 61.5987 | 61.6347 | 61.4979 | 61.5339
783.5938 | 123.4039 | -61.4731 | 61.6333 | 0.021127 | -0.10462 | -0.085257 | -0.057066 | -0.027827 | -0.051769 | -0.012357 | 61.6378 | 0.12043 | 61.5416 | -0.028522 | 0.029923 | 61.5799 | 0.007721 | 61.3672 | 61.4942 | 61.3685 | 61.3878 | 61.416 | 61.4453 | 61.4213 | 61.4607 | 123.1109 | 61.5935 | 123.0147 | 61.4446 | 61.503 | 123.053 | 61.4808 | 122.8403 | 61.6079 | 61.6301 | 61.5117 | 61.5339
784.5938 | 123.3856 | -61.4365 | 61.6516 | 0.025705 | -0.11378 | -0.080679 | -0.061645 | -0.023249 | -0.065504 | -0.021514 | 61.6424 | 0.12043 | 61.537 | -0.028522 | 0.039079 | 61.5845 | 0.012299 | 61.3718 | 61.4622 | 61.3227 | 61.3558 | 61.3748 | 61.4132 | 61.371 | 61.4149 | 123.0789 | 61.5569 | 122.9735 | 61.4079 | 61.4755 | 123.0209 | 61.4488 | 122.8083 | 61.6033 | 61.6301 | 61.4979 | 61.5247
785.5938 | 123.3719 | -61.4822 | 61.6287 | 0.016548 | -0.11378 | -0.080679 | -0.066223 | -0.041561 | -0.060926 | -0.016936 | 61.6378 | 0.11585 | 61.5279 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.4988 | 61.3685 | 61.4016 | 61.416 | 61.4407 | 61.4213 | 61.4653 | 123.1201 | 61.5981 | 123.0101 | 61.4491 | 61.5213 | 123.0621 | 61.4854 | 122.8495 | 61.5987 | 61.6347 | 61.4888 | 61.5247
786.5938 | 123.3902 | -61.4777 | 61.6104 | 0.016548 | -0.11378 | -0.080679 | -0.061645 | -0.032405 | -0.060926 | -0.026092 | 61.647 | 0.12501 | 61.5324 | -0.033101 | 0.039079 | 61.5799 | 0.012299 | 61.3672 | 61.4942 | 61.3639 | 61.397 | 61.416 | 61.4453 | 61.4167 | 61.4516 | 123.1246 | 61.6027 | 123.0101 | 61.4446 | 61.5167 | 123.0576 | 61.49 | 122.8449 | 61.6079 | 61.6347 | 61.4934 | 61.5202
787.5938 | 123.3627 | -61.5005 | 61.647 | 0.021127 | -0.1092 | -0.085257 | -0.066223 | -0.027827 | -0.065504 | -0.021514 | 61.6424 | 0.11585 | 61.5324 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.5217 | 61.3913 | 61.4153 | 61.4343 | 61.4727 | 61.435 | 61.479 | 123.143 | 61.6164 | 123.033 | 61.4629 | 61.5396 | 123.085 | 61.5083 | 122.8632 | 61.6033 | 61.6347 | 61.4934 | 61.5247
788.5938 | 123.3856 | -61.5051 | 61.6058 | 0.021127 | -0.11378 | -0.085257 | -0.070802 | -0.023249 | -0.065504 | -0.016936 | 61.647 | 0.11585 | 61.5324 | -0.033101 | 0.029923 | 61.5891 | 0.003143 | 61.3672 | 61.5263 | 61.3913 | 61.4199 | 61.4343 | 61.4819 | 61.4396 | 61.4882 | 123.1521 | 61.621 | 123.0376 | 61.472 | 61.535 | 123.0942 | 61.5083 | 122.8724 | 61.6171 | 61.6438 | 61.5025 | 61.5293
789.5938 | 123.3536 | -61.4868 | 61.6104 | 0.021127 | -0.1092 | -0.089836 | -0.066223 | -0.036983 | -0.065504 | -0.021514 | 61.6424 | 0.12043 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3581 | 61.5079 | 61.3776 | 61.397 | 61.4206 | 61.4498 | 61.4213 | 61.4653 | 123.1292 | 61.6072 | 123.0193 | 61.4537 | 61.5213 | 123.0713 | 61.4945 | 122.8449 | 61.6079 | 61.6347 | 61.4979 | 61.5247
790.5938 | 123.262 | -61.496 | 61.6425 | 0.021127 | -0.11836 | -0.080679 | -0.061645 | -0.032405 | -0.065504 | -0.021514 | 61.6424 | 0.11127 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | -0.001436 | 61.3718 | 61.5171 | 61.3776 | 61.4153 | 61.4343 | 61.4636 | 61.4305 | 61.4745 | 123.1384 | 61.6072 | 123.0284 | 61.4629 | 61.5305 | 123.0804 | 61.4945 | 122.8678 | 61.6079 | 61.6438 | 61.4979 | 61.5339
791.5938 | 123.381 | -61.4685 | 61.6333 | 0.021127 | -0.11836 | -0.085257 | -0.07538 | -0.032405 | -0.060926 | -0.03067 | 61.6378 | 0.11585 | 61.5279 | -0.033101 | 0.039079 | 61.5891 | 0.007721 | 61.3764 | 61.4896 | 61.3501 | 61.3832 | 61.3931 | 61.4361 | 61.4076 | 61.4378 | 123.1063 | 61.5844 | 122.9964 | 61.4354 | 61.5076 | 123.0576 | 61.4762 | 122.8449 | 61.5987 | 61.6301 | 61.4888 | 61.5202
792.5938 | 123.3261 | -61.4822 | 61.6104 | 0.021127 | -0.11836 | -0.094414 | -0.07538 | -0.036983 | -0.065504 | -0.021514 | 61.6378 | 0.11585 | 61.5279 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3627 | 61.5034 | 61.3639 | 61.3878 | 61.4069 | 61.4453 | 61.4167 | 61.4607 | 123.1201 | 61.5981 | 123.0101 | 61.4446 | 61.5167 | 123.0667 | 61.4854 | 122.8449 | 61.6033 | 61.6347 | 61.4934 | 61.5247
793.5938 | 123.3536 | -61.4914 | 61.6196 | 0.025705 | -0.11836 | -0.10357 | -0.07538 | -0.036983 | -0.074661 | -0.03067 | 61.6424 | 0.12501 | 61.5324 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3627 | 61.5171 | 61.373 | 61.3878 | 61.416 | 61.4544 | 61.4167 | 61.4607 | 123.1338 | 61.6164 | 123.0238 | 61.4583 | 61.5305 | 123.0759 | 61.4945 | 122.8541 | 61.6033 | 61.6393 | 61.4934 | 61.5293
794.5938 | 123.3856 | -61.496 | 61.5921 | 0.025705 | -0.11836 | -0.089836 | -0.07538 | -0.032405 | -0.074661 | -0.026092 | 61.6378 | 0.12958 | 61.5462 | -0.028522 | 0.039079 | 61.5845 | 0.003143 | 61.3672 | 61.5217 | 61.3776 | 61.4061 | 61.4206 | 61.4636 | 61.4213 | 61.4699 | 123.1338 | 61.6256 | 123.0422 | 61.4674 | 61.5351 | 123.0804 | 61.4991 | 122.8632 | 61.5987 | 61.6347 | 61.5071 | 61.543
795.5938 | 123.3994 | -61.496 | 61.6013 | 0.025705 | -0.12294 | -0.094414 | -0.07538 | -0.050716 | -0.074661 | -0.03067 | 61.6424 | 0.12501 | 61.5416 | -0.033101 | 0.039079 | 61.5891 | 0.007721 | 61.3718 | 61.5217 | 61.373 | 61.4016 | 61.4206 | 61.4453 | 61.4213 | 61.4653 | 123.1384 | 61.621 | 123.0376 | 61.4629 | 61.5351 | 123.085 | 61.5037 | 122.8678 | 61.6033 | 61.6347 | 61.5025 | 61.5339
796.5938 | 123.3261 | -61.4777 | 61.6333 | 0.007391 | -0.11836 | -0.089836 | -0.066223 | -0.046138 | -0.074661 | -0.03067 | 61.6424 | 0.12043 | 61.5416 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3627 | 61.4851 | 61.3593 | 61.3878 | 61.4114 | 61.4315 | 61.403 | 61.447 | 123.1201 | 61.5981 | 123.0193 | 61.4446 | 61.5122 | 123.0621 | 61.4854 | 122.8403 | 61.6079 | 61.6347 | 61.5071 | 61.5339
797.5938 | 123.3398 | -61.496 | 61.6287 | 0.016548 | -0.12294 | -0.089836 | -0.07538 | -0.041561 | -0.079239 | -0.035248 | 61.6424 | 0.12501 | 61.5324 | -0.03768 | 0.039079 | 61.5845 | 0.012299 | 61.3627 | 61.5125 | 61.373 | 61.4061 | 61.4206 | 61.4544 | 61.4167 | 61.4607 | 123.1384 | 61.621 | 123.0284 | 61.4583 | 61.5351 | 123.0804 | 61.5083 | 122.8586 | 61.6033 | 61.6301 | 61.4934 | 61.5202
798.5938 | 123.3398 | -61.4456 | 61.5967 | 0.025705 | -0.12752 | -0.089836 | -0.084537 | -0.046138 | -0.074661 | -0.03067 | 61.6424 | 0.12043 | 61.5508 | -0.03768 | 0.034501 | 61.5845 | 0.007721 | 61.3581 | 61.4713 | 61.3181 | 61.3558 | 61.3611 | 61.3995 | 61.371 | 61.4149 | 123.088 | 61.566 | 122.9964 | 61.4079 | 61.4801 | 123.0301 | 61.4533 | 122.8037 | 61.6079 | 61.6347 | 61.5163 | 61.543
799.5938 | 123.3261 | -61.4822 | 61.6425 | 0.016548 | -0.11836 | -0.094414 | -0.084537 | -0.046138 | -0.079239 | -0.039826 | 61.6424 | 0.11585 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.4988 | 61.3639 | 61.3878 | 61.3977 | 61.4361 | 61.403 | 61.4424 | 123.1246 | 61.5981 | 123.0238 | 61.4491 | 61.5213 | 123.0667 | 61.49 | 122.8495 | 61.6033 | 61.6347 | 61.5025 | 61.5339
800.5938 | 123.3215 | -61.4731 | 61.6745 | 0.025705 | -0.1321 | -0.089836 | -0.089116 | -0.041561 | -0.074661 | -0.026092 | 61.647 | 0.13416 | 61.5416 | -0.03768 | 0.034501 | 61.5753 | 0.012299 | 61.3672 | 61.4988 | 61.341 | 61.3832 | 61.384 | 61.4315 | 61.3984 | 61.447 | 123.1201 | 61.6072 | 123.0147 | 61.4354 | 61.5076 | 123.0484 | 61.4854 | 122.8403 | 61.6125 | 61.6347 | 61.5071 | 61.5293
801.5938 | 123.3994 | -61.4868 | 61.615 | 0.021127 | -0.12752 | -0.10815 | -0.079959 | -0.046138 | -0.079239 | -0.039826 | 61.6424 | 0.11585 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3581 | 61.5079 | 61.3593 | 61.3787 | 61.4069 | 61.4407 | 61.4076 | 61.447 | 123.1292 | 61.6027 | 123.0284 | 61.4537 | 61.5259 | 123.0713 | 61.49 | 122.8449 | 61.6033 | 61.6393 | 61.5025 | 61.5385
802.5938 | 123.3994 | -61.4502 | 61.6013 | 0.021127 | -0.12752 | -0.098993 | -0.079959 | -0.041561 | -0.083817 | -0.03067 | 61.6424 | 0.12501 | 61.5416 | -0.03768 | 0.034501 | 61.5891 | 0.003143 | 61.3627 | 61.4713 | 61.3227 | 61.3512 | 61.3702 | 61.4086 | 61.3664 | 61.4195 | 123.0926 | 61.5752 | 122.9918 | 61.4125 | 61.4847 | 123.0392 | 61.4533 | 122.8129 | 61.6079 | 61.6393 | 61.5071 | 61.5385
803.5938 | 123.3444 | -61.4639 | 61.6241 | 0.025705 | -0.12752 | -0.098993 | -0.079959 | -0.046138 | -0.088396 | -0.044405 | 61.6424 | 0.11585 | 61.5279 | -0.03768 | 0.043657 | 61.5753 | 0.012299 | 61.3672 | 61.4896 | 61.3364 | 61.3649 | 61.384 | 61.4178 | 61.3755 | 61.4195 | 123.1063 | 61.5798 | 122.9918 | 61.4262 | 61.5076 | 123.0392 | 61.4762 | 122.8312 | 61.5987 | 61.6301 | 61.4842 | 61.5156
804.5938 | 123.3307 | -61.4685 | 61.615 | 0.021127 | -0.12752 | -0.094414 | -0.084537 | -0.055294 | -0.079239 | -0.035248 | 61.647 | 0.12043 | 61.5416 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3672 | 61.4896 | 61.341 | 61.3741 | 61.384 | 61.4132 | 61.3893 | 61.4333 | 123.1155 | 61.5889 | 123.0101 | 61.4308 | 61.503 | 123.053 | 61.4716 | 122.8357 | 61.6125 | 61.6438 | 61.5071 | 61.5385
805.5938 | 123.3902 | -61.4685 | 61.6241 | 0.021127 | -0.13668 | -0.10357 | -0.089116 | -0.055294 | -0.083817 | -0.035248 | 61.647 | 0.11585 | 61.537 | -0.033101 | 0.043657 | 61.5891 | 0.003143 | 61.3718 | 61.4896 | 61.3318 | 61.3649 | 61.3794 | 61.4132 | 61.3847 | 61.4333 | 123.1155 | 61.5844 | 123.0055 | 61.4354 | 61.5122 | 123.0576 | 61.4716 | 122.8403 | 61.6033 | 61.6438 | 61.4934 | 61.5339
806.5938 | 123.3765 | -61.4777 | 61.5784 | 0.016548 | -0.1321 | -0.10815 | -0.084537 | -0.050716 | -0.088396 | -0.035248 | 61.6332 | 0.12501 | 61.5324 | -0.033101 | 0.034501 | 61.5845 | 0.003143 | 61.3627 | 61.4942 | 61.3456 | 61.3695 | 61.3931 | 61.4269 | 61.3893 | 61.4424 | 123.1109 | 61.6027 | 123.0101 | 61.4446 | 61.5122 | 123.0621 | 61.4808 | 122.8403 | 61.5987 | 61.6301 | 61.4979 | 61.5293
807.5938 | 123.4039 | -61.4777 | 61.6058 | 0.025705 | -0.13668 | -0.10815 | -0.089116 | -0.050716 | -0.083817 | -0.039826 | 61.647 | 0.12043 | 61.5416 | -0.033101 | 0.034501 | 61.5799 | 0.007721 | 61.3672 | 61.5034 | 61.341 | 61.3695 | 61.3885 | 61.4269 | 61.3938 | 61.4378 | 123.1246 | 61.5981 | 123.0193 | 61.4446 | 61.5122 | 123.0576 | 61.4854 | 122.8449 | 61.6125 | 61.6393 | 61.5071 | 61.5339
808.5938 | 123.3078 | -61.496 | 61.615 | 0.021127 | -0.13668 | -0.10357 | -0.089116 | -0.055294 | -0.083817 | -0.044405 | 61.647 | 0.12501 | 61.5416 | -0.033101 | 0.034501 | 61.5845 | 0.007721 | 61.3627 | 61.5171 | 61.3593 | 61.3924 | 61.4069 | 61.4407 | 61.4122 | 61.4516 | 123.143 | 61.621 | 123.0376 | 61.4629 | 61.5305 | 123.0804 | 61.5037 | 122.8586 | 61.6125 | 61.6393 | 61.5071 | 61.5339
809.5938 | 123.4131 | -61.4731 | 61.6196 | 0.021127 | -0.14583 | -0.10815 | -0.089116 | -0.059872 | -0.083817 | -0.048983 | 61.647 | 0.11585 | 61.5462 | -0.028522 | 0.034501 | 61.5753 | -0.001436 | 61.3581 | 61.4942 | 61.3272 | 61.3649 | 61.384 | 61.4132 | 61.3893 | 61.4241 | 123.1201 | 61.5889 | 123.0193 | 61.4446 | 61.5076 | 123.0484 | 61.4716 | 122.8312 | 61.6125 | 61.6484 | 61.5117 | 61.5476
810.5938 | 123.436 | -61.5051 | 61.5646 | 0.021127 | -0.14583 | -0.11273 | -0.093694 | -0.069028 | -0.097553 | -0.044405 | 61.6424 | 0.12501 | 61.5508 | -0.033101 | 0.029923 | 61.5799 | 0.007721 | 61.3672 | 61.5263 | 61.3593 | 61.3924 | 61.4114 | 61.4361 | 61.4076 | 61.4607 | 123.1475 | 61.6301 | 123.0559 | 61.472 | 61.535 | 123.085 | 61.5128 | 122.8724 | 61.6125 | 61.6347 | 61.5208 | 61.543
811.5938 | 123.3765 | -61.4731 | 61.6379 | 0.021127 | -0.14125 | -0.11273 | -0.098273 | -0.059872 | -0.092974 | -0.044405 | 61.6424 | 0.12501 | 61.5324 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3581 | 61.4942 | 61.3318 | 61.3604 | 61.3748 | 61.4132 | 61.3801 | 61.4287 | 123.1155 | 61.5981 | 123.0055 | 61.44 | 61.5122 | 123.0576 | 61.4762 | 122.8312 | 61.6033 | 61.6393 | 61.4934 | 61.5293
812.5938 | 123.3124 | -61.4639 | 61.6241 | 0.021127 | -0.13668 | -0.11273 | -0.098273 | -0.059872 | -0.088396 | -0.048983 | 61.6424 | 0.11585 | 61.537 | -0.023943 | 0.034501 | 61.5799 | 0.012299 | 61.3581 | 61.4851 | 61.3273 | 61.3512 | 61.3657 | 61.4041 | 61.3755 | 61.4149 | 123.1063 | 61.5798 | 123.001 | 61.44 | 61.4984 | 123.0438 | 61.4762 | 122.822 | 61.6079 | 61.6301 | 61.5025 | 61.5247
813.5938 | 123.2941 | -61.5051 | 61.615 | 0.025705 | -0.14583 | -0.12189 | -0.098273 | -0.059872 | -0.092974 | -0.053561 | 61.647 | 0.12501 | 61.5416 | -0.033101 | 0.029923 | 61.5845 | 0.007721 | 61.3627 | 61.5308 | 61.3593 | 61.3832 | 61.4069 | 61.4453 | 61.4122 | 61.4516 | 123.1521 | 61.6301 | 123.0467 | 61.472 | 61.535 | 123.0896 | 61.5128 | 122.8678 | 61.6171 | 61.6393 | 61.5117 | 61.5339
814.5938 | 123.2666 | -61.5097 | 61.6425 | 0.025705 | -0.14583 | -0.11731 | -0.093694 | -0.059872 | -0.092974 | -0.053561 | 61.6424 | 0.12958 | 61.5462 | -0.03768 | 0.034501 | 61.5845 | 0.003143 | 61.3627 | 61.5354 | 61.3639 | 61.3924 | 61.416 | 61.4498 | 61.4167 | 61.4561 | 123.1521 | 61.6393 | 123.0559 | 61.472 | 61.5442 | 123.0942 | 61.5128 | 122.8724 | 61.6079 | 61.6393 | 61.5117 | 61.543
815.5938 | 123.2483 | -61.4822 | 61.6562 | 0.021127 | -0.14583 | -0.12189 | -0.10285 | -0.073606 | -0.10213 | -0.058139 | 61.6516 | 0.12043 | 61.5462 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.3627 | 61.5034 | 61.3364 | 61.3604 | 61.3794 | 61.4086 | 61.3801 | 61.4241 | 123.1338 | 61.6027 | 123.0284 | 61.4491 | 61.5213 | 123.0621 | 61.49 | 122.8449 | 61.6125 | 61.6438 | 61.5071 | 61.5385
816.5938 | 123.2483 | -61.5005 | 61.6516 | 0.016548 | -0.15041 | -0.11731 | -0.098273 | -0.06445 | -0.097553 | -0.053561 | 61.647 | 0.12043 | 61.537 | -0.033101 | 0.039079 | 61.5845 | -0.001436 | 61.3581 | 61.5171 | 61.3501 | 61.3832 | 61.4023 | 61.4361 | 61.403 | 61.447 | 123.1475 | 61.621 | 123.0376 | 61.4674 | 61.5396 | 123.085 | 61.4991 | 122.8586 | 61.6079 | 61.6484 | 61.4979 | 61.5385
817.5938 | 123.2574 | -61.4777 | 61.6791 | 0.021127 | -0.15499 | -0.11731 | -0.10285 | -0.073606 | -0.092974 | -0.053561 | 61.647 | 0.12043 | 61.5508 | -0.028522 | 0.034501 | 61.5799 | -0.001436 | 61.3627 | 61.4988 | 61.3227 | 61.3604 | 61.3748 | 61.4041 | 61.3847 | 61.4241 | 123.1246 | 61.5981 | 123.0284 | 61.4491 | 61.5122 | 123.0576 | 61.4762 | 122.8403 | 61.6125 | 61.6484 | 61.5163 | 61.5522
818.5938 | 123.2391 | -61.5143 | 61.6653 | 0.021127 | -0.15499 | -0.13104 | -0.10743 | -0.069028 | -0.11129 | -0.053561 | 61.647 | 0.12043 | 61.537 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.5354 | 61.3593 | 61.3832 | 61.4069 | 61.4453 | 61.403 | 61.4607 | 123.1613 | 61.6347 | 123.0513 | 61.4812 | 61.5534 | 123.0988 | 61.5174 | 122.8861 | 61.6079 | 61.6438 | 61.4979 | 61.5339
819.5938 | 123.262 | -61.4868 | 61.6653 | 0.025705 | -0.14583 | -0.12646 | -0.10743 | -0.073606 | -0.10213 | -0.053561 | 61.6516 | 0.11585 | 61.5462 | -0.033101 | 0.039079 | 61.5753 | 0.003143 | 61.3672 | 61.5125 | 61.341 | 61.3604 | 61.3794 | 61.4132 | 61.3847 | 61.4333 | 123.1384 | 61.6027 | 123.033 | 61.4537 | 61.5259 | 123.0621 | 61.49 | 122.8541 | 61.6125 | 61.6484 | 61.5071 | 61.543
820.5938 | 123.2758 | -61.4914 | 61.6608 | 0.021127 | -0.15957 | -0.13104 | -0.11201 | -0.078184 | -0.10671 | -0.053561 | 61.6424 | 0.12043 | 61.5462 | -0.028522 | 0.029923 | 61.5845 | -0.001436 | 61.3672 | 61.5125 | 61.3318 | 61.3604 | 61.3794 | 61.4132 | 61.3847 | 61.4378 | 123.1338 | 61.6118 | 123.0376 | 61.4629 | 61.5213 | 123.0759 | 61.49 | 122.8586 | 61.6125 | 61.6438 | 61.5163 | 61.5476
821.5938 | 123.2986 | -61.4822 | 61.6653 | 0.021127 | -0.15499 | -0.13104 | -0.10285 | -0.069028 | -0.10671 | -0.058139 | 61.647 | 0.12501 | 61.5508 | -0.028522 | 0.039079 | 61.5799 | -0.001436 | 61.3672 | 61.5034 | 61.3272 | 61.3512 | 61.3794 | 61.4132 | 61.3755 | 61.4241 | 123.1292 | 61.6072 | 123.033 | 61.4537 | 61.5213 | 123.0621 | 61.4808 | 122.8495 | 61.6079 | 61.6484 | 61.5117 | 61.5522
822.5938 | 123.2849 | -61.4685 | 61.6837 | 0.016548 | -0.15499 | -0.13104 | -0.11659 | -0.082762 | -0.11129 | -0.067295 | 61.647 | 0.11585 | 61.537 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3718 | 61.4851 | 61.3135 | 61.3375 | 61.3519 | 61.3857 | 61.3572 | 61.4012 | 123.1155 | 61.5844 | 123.0055 | 61.4354 | 61.5076 | 123.0484 | 61.4716 | 122.8403 | 61.6079 | 61.6438 | 61.4979 | 61.5339
823.5938 | 123.317 | -61.4685 | 61.6837 | 0.030283 | -0.15041 | -0.13562 | -0.11201 | -0.08734 | -0.11129 | -0.062717 | 61.6516 | 0.12043 | 61.537 | -0.028522 | 0.043657 | 61.5799 | 0.007721 | 61.3672 | 61.4988 | 61.3181 | 61.3329 | 61.3565 | 61.3812 | 61.3572 | 61.4058 | 123.1201 | 61.5889 | 123.0055 | 61.44 | 61.5122 | 123.0484 | 61.4762 | 122.8357 | 61.6079 | 61.6438 | 61.4934 | 61.5293
824.5938 | 123.3078 | -61.4685 | 61.6837 | 0.016548 | -0.16415 | -0.13562 | -0.11659 | -0.082762 | -0.11587 | -0.071874 | 61.6516 | 0.11585 | 61.537 | -0.03768 | 0.034501 | 61.5753 | 0.007721 | 61.3718 | 61.4851 | 61.3044 | 61.3329 | 61.3519 | 61.3857 | 61.3526 | 61.3966 | 123.1201 | 61.5844 | 123.0055 | 61.4308 | 61.503 | 123.0438 | 61.4762 | 122.8403 | 61.6171 | 61.6438 | 61.5025 | 61.5293
825.5938 | 123.317 | -61.4685 | 61.647 | 0.025705 | -0.15957 | -0.13562 | -0.11659 | -0.073606 | -0.12044 | -0.067295 | 61.647 | 0.11585 | 61.5416 | -0.03768 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.4942 | 61.3089 | 61.3329 | 61.3519 | 61.3949 | 61.3481 | 61.4012 | 123.1155 | 61.5844 | 123.0101 | 61.4308 | 61.5076 | 123.053 | 61.4716 | 122.8403 | 61.6079 | 61.6438 | 61.5025 | 61.5385
826.5938 | 123.3261 | -61.441 | 61.6653 | 0.021127 | -0.16415 | -0.1402 | -0.12116 | -0.082762 | -0.11587 | -0.062717 | 61.6516 | 0.12043 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.4622 | 61.2769 | 61.3008 | 61.3199 | 61.3583 | 61.3252 | 61.3783 | 123.0926 | 61.5615 | 122.9826 | 61.4079 | 61.4801 | 123.0255 | 61.4442 | 122.8129 | 61.6125 | 61.6484 | 61.5025 | 61.5385
827.5938 | 123.2986 | -61.4777 | 61.7065 | 0.021127 | -0.16873 | -0.14478 | -0.12116 | -0.091918 | -0.11587 | -0.076452 | 61.6561 | 0.12043 | 61.5462 | -0.033101 | 0.043657 | 61.5845 | 0.007721 | 61.3718 | 61.4988 | 61.3089 | 61.3329 | 61.3565 | 61.3857 | 61.3618 | 61.4012 | 123.1338 | 61.5981 | 123.0238 | 61.4446 | 61.5213 | 123.0621 | 61.4854 | 122.8495 | 61.6125 | 61.6484 | 61.5025 | 61.5385
828.5938 | 123.2437 | -61.5189 | 61.6653 | 0.016548 | -0.17331 | -0.14478 | -0.12574 | -0.08734 | -0.12502 | -0.071874 | 61.647 | 0.12501 | 61.537 | -0.03768 | 0.034501 | 61.5799 | 0.012299 | 61.3718 | 61.5354 | 61.3456 | 61.3741 | 61.3931 | 61.4315 | 61.3938 | 61.447 | 123.1658 | 61.6439 | 123.0559 | 61.4812 | 61.5534 | 123.0988 | 61.5312 | 122.8907 | 61.6125 | 61.6347 | 61.5025 | 61.5247
829.5938 | 123.2712 | -61.5051 | 61.6882 | 0.021127 | -0.16873 | -0.1402 | -0.13032 | -0.091918 | -0.12502 | -0.076452 | 61.6424 | 0.11585 | 61.5462 | -0.03768 | 0.034501 | 61.5845 | 0.012299 | 61.3672 | 61.5263 | 61.3364 | 61.3649 | 61.3748 | 61.4132 | 61.3801 | 61.4287 | 123.1475 | 61.621 | 123.0513 | 61.4674 | 61.5396 | 123.0896 | 61.5174 | 122.8724 | 61.6079 | 61.6301 | 61.5117 | 61.5339
830.5938 | 123.2666 | -61.5097 | 61.6653 | 0.021127 | -0.17331 | -0.14478 | -0.13032 | -0.08734 | -0.1296 | -0.076452 | 61.647 | 0.13416 | 61.5508 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.5308 | 61.3364 | 61.3649 | 61.3794 | 61.4224 | 61.3801 | 61.4333 | 123.1567 | 61.6439 | 123.0605 | 61.4766 | 61.5488 | 123.0942 | 61.5174 | 122.8769 | 61.6079 | 61.6393 | 61.5117 | 61.543
831.5938 | 123.2986 | -61.496 | 61.6653 | 0.021127 | -0.17331 | -0.15394 | -0.12574 | -0.096496 | -0.12044 | -0.08103 | 61.6561 | 0.12043 | 61.5462 | -0.023943 | 0.034501 | 61.5845 | 0.012299 | 61.3718 | 61.5171 | 61.3227 | 61.342 | 61.3702 | 61.3995 | 61.3755 | 61.4149 | 123.1521 | 61.6164 | 123.0422 | 61.472 | 61.5305 | 123.0804 | 61.5083 | 122.8678 | 61.6216 | 61.6438 | 61.5117 | 61.5339
832.5938 | 123.2986 | -61.5189 | 61.6699 | 0.016548 | -0.17788 | -0.1402 | -0.1349 | -0.096496 | -0.13418 | -0.085608 | 61.6561 | 0.12958 | 61.5416 | -0.028522 | 0.034501 | 61.5799 | 0.016878 | 61.3627 | 61.5354 | 61.341 | 61.3787 | 61.384 | 61.4224 | 61.3847 | 61.4333 | 123.175 | 61.6484 | 123.0605 | 61.4903 | 61.5534 | 123.0988 | 61.5357 | 122.8815 | 61.6216 | 61.6393 | 61.5071 | 61.5247
833.5938 | 123.3032 | -61.5005 | 61.6791 | 0.016548 | -0.18246 | -0.14936 | -0.1349 | -0.096496 | -0.1296 | -0.08103 | 61.647 | 0.12501 | 61.5462 | -0.042259 | 0.034501 | 61.5845 | 0.007721 | 61.3627 | 61.5171 | 61.3181 | 61.3512 | 61.3656 | 61.4041 | 61.3709 | 61.4195 | 123.1475 | 61.6256 | 123.0467 | 61.4583 | 61.535 | 123.085 | 61.5083 | 122.8632 | 61.6125 | 61.6393 | 61.5117 | 61.5385
834.5938 | 123.2986 | -61.4639 | 61.6791 | 0.021127 | -0.18704 | -0.16309 | -0.1349 | -0.10107 | -0.13876 | -0.085608 | 61.6516 | 0.12501 | 61.5462 | -0.033101 | 0.043657 | 61.5799 | 0.007721 | 61.3718 | 61.4851 | 61.2769 | 61.3008 | 61.329 | 61.3629 | 61.3252 | 61.3783 | 123.1155 | 61.5889 | 123.0101 | 61.4308 | 61.5076 | 123.0438 | 61.4716 | 122.8357 | 61.6079 | 61.6438 | 61.5025 | 61.5385
835.5938 | 123.3719 | -61.4685 | 61.647 | 0.01197 | -0.18704 | -0.14936 | -0.13948 | -0.10565 | -0.13418 | -0.090186 | 61.6516 | 0.12501 | 61.5324 | -0.03768 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.4805 | 61.2815 | 61.3191 | 61.329 | 61.3629 | 61.3343 | 61.3783 | 123.1201 | 61.5935 | 123.001 | 61.4308 | 61.5076 | 123.053 | 61.4762 | 122.8357 | 61.6125 | 61.6438 | 61.4934 | 61.5247
836.5938 | 123.3948 | -61.4731 | 61.6196 | 0.01197 | -0.18704 | -0.16309 | -0.14406 | -0.096496 | -0.14334 | -0.085608 | 61.647 | 0.11127 | 61.5416 | -0.028522 | 0.039079 | 61.5799 | 0.007721 | 61.3672 | 61.4851 | 61.286 | 61.31 | 61.329 | 61.3766 | 61.3297 | 61.3875 | 123.1201 | 61.5844 | 123.0147 | 61.4446 | 61.5122 | 123.053 | 61.4808 | 122.8403 | 61.6079 | 61.6393 | 61.5025 | 61.5339
837.5938 | 123.3765 | -61.4502 | 61.6379 | 0.021127 | -0.19162 | -0.15851 | -0.14864 | -0.10565 | -0.13418 | -0.085608 | 61.6516 | 0.12501 | 61.5462 | -0.019364 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.4713 | 61.2586 | 61.2917 | 61.3016 | 61.3445 | 61.316 | 61.3646 | 123.1018 | 61.5752 | 122.9964 | 61.4308 | 61.4847 | 123.0301 | 61.4533 | 122.8174 | 61.6171 | 61.6484 | 61.5117 | 61.543
838.5938 | 123.3627 | -61.4548 | 61.6791 | 0.016548 | -0.19162 | -0.15394 | -0.13948 | -0.11023 | -0.13876 | -0.090186 | 61.6516 | 0.13416 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.4713 | 61.2632 | 61.3008 | 61.3153 | 61.3445 | 61.316 | 61.3646 | 123.1063 | 61.5889 | 122.9964 | 61.4217 | 61.4939 | 123.0392 | 61.4579 | 122.8266 | 61.6125 | 61.6484 | 61.5025 | 61.5385
839.5938 | 123.3948 | -61.4548 | 61.6516 | 0.021127 | -0.19162 | -0.16309 | -0.14406 | -0.10107 | -0.13418 | -0.099343 | 61.6516 | 0.12501 | 61.5416 | -0.028522 | 0.039079 | 61.5799 | 0.012299 | 61.3627 | 61.4759 | 61.2632 | 61.2917 | 61.3107 | 61.3537 | 61.3206 | 61.3554 | 123.1063 | 61.5798 | 122.9964 | 61.4263 | 61.4939 | 123.0347 | 61.4671 | 122.8174 | 61.6125 | 61.6393 | 61.5025 | 61.5293
840.5938 | 123.3948 | -61.4639 | 61.6333 | 0.01197 | -0.19162 | -0.16309 | -0.14864 | -0.10565 | -0.14791 | -0.094765 | 61.6516 | 0.13416 | 61.5508 | -0.03768 | 0.039079 | 61.5891 | 0.012299 | 61.3672 | 61.4759 | 61.2723 | 61.3008 | 61.3153 | 61.3583 | 61.316 | 61.3692 | 123.1155 | 61.5981 | 123.0147 | 61.4262 | 61.503 | 123.053 | 61.4762 | 122.8312 | 61.6125 | 61.6393 | 61.5117 | 61.5385
841.5938 | 123.4085 | -61.441 | 61.6516 | 0.021127 | -0.18704 | -0.16767 | -0.13948 | -0.11481 | -0.13876 | -0.10392 | 61.6516 | 0.12043 | 61.5324 | -0.019364 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.4622 | 61.254 | 61.2734 | 61.3016 | 61.3262 | 61.3023 | 61.3371 | 123.0926 | 61.5615 | 122.9735 | 61.4217 | 61.4755 | 123.0209 | 61.4442 | 122.8083 | 61.6171 | 61.6484 | 61.4979 | 61.5293
842.5938 | 123.3673 | -61.4273 | 61.6287 | 0.016548 | -0.19162 | -0.17225 | -0.15321 | -0.11481 | -0.15249 | -0.094765 | 61.6424 | 0.12043 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.012299 | 61.3672 | 61.4439 | 61.2357 | 61.2551 | 61.2741 | 61.3125 | 61.2748 | 61.3325 | 123.0697 | 61.5477 | 122.9689 | 61.3942 | 61.4664 | 123.0118 | 61.4396 | 122.7945 | 61.6033 | 61.6301 | 61.5025 | 61.5293
843.5938 | 123.3673 | -61.4594 | 61.6196 | 0.01197 | -0.19162 | -0.16767 | -0.15779 | -0.11023 | -0.14791 | -0.099343 | 61.647 | 0.12501 | 61.5508 | -0.033101 | 0.034501 | 61.5753 | 0.007721 | 61.3672 | 61.4713 | 61.2677 | 61.2917 | 61.3016 | 61.3491 | 61.3114 | 61.36 | 123.1063 | 61.5844 | 123.0101 | 61.4262 | 61.4939 | 123.0347 | 61.4671 | 122.8266 | 61.6125 | 61.6393 | 61.5163 | 61.543
844.5938 | 123.4039 | -61.4365 | 61.6196 | 0.01197 | -0.1962 | -0.17683 | -0.15321 | -0.11481 | -0.15249 | -0.099343 | 61.6561 | 0.12501 | 61.5553 | -0.028522 | 0.039079 | 61.5799 | 0.007721 | 61.3718 | 61.4484 | 61.2403 | 61.2596 | 61.2832 | 61.3217 | 61.284 | 61.3371 | 123.0926 | 61.5615 | 122.9918 | 61.4079 | 61.4755 | 123.0164 | 61.4442 | 122.8083 | 61.6171 | 61.6484 | 61.5163 | 61.5476
845.5938 | 123.4268 | -61.4273 | 61.647 | 0.01197 | -0.1962 | -0.17225 | -0.15321 | -0.12854 | -0.14791 | -0.10392 | 61.6516 | 0.12043 | 61.5416 | -0.033101 | 0.039079 | 61.5753 | 0.003143 | 61.3672 | 61.4393 | 61.2311 | 61.2551 | 61.2741 | 61.2988 | 61.2794 | 61.3234 | 123.0789 | 61.5477 | 122.9689 | 61.3942 | 61.4664 | 123.0026 | 61.4305 | 122.7945 | 61.6125 | 61.6484 | 61.5025 | 61.5385
846.5938 | 123.3994 | -61.4822 | 61.6333 | 0.021127 | -0.20078 | -0.17683 | -0.16695 | -0.11481 | -0.14791 | -0.1085 | 61.6561 | 0.12958 | 61.5462 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3672 | 61.5034 | 61.2815 | 61.3054 | 61.3153 | 61.3674 | 61.3343 | 61.3737 | 123.1384 | 61.6118 | 123.0284 | 61.4491 | 61.5167 | 123.0621 | 61.4854 | 122.8495 | 61.6216 | 61.653 | 61.5117 | 61.543
847.5938 | 123.436 | -61.4594 | 61.6516 | 0.021127 | -0.20994 | -0.17683 | -0.15779 | -0.12854 | -0.15249 | -0.1085 | 61.6561 | 0.12043 | 61.5508 | -0.028522 | 0.039079 | 61.5845 | 0.003143 | 61.3718 | 61.4805 | 61.2494 | 61.2825 | 61.3016 | 61.3308 | 61.3069 | 61.3509 | 123.1155 | 61.5798 | 123.0101 | 61.4308 | 61.4984 | 123.0438 | 61.4625 | 122.8312 | 61.6171 | 61.653 | 61.5117 | 61.5476
848.5938 | 123.4314 | -61.4731 | 61.6379 | 0.016548 | -0.20078 | -0.18141 | -0.15779 | -0.12396 | -0.15249 | -0.11765 | 61.6516 | 0.12043 | 61.5462 | -0.033101 | 0.034501 | 61.5753 | 0.012299 | 61.3718 | 61.4896 | 61.2723 | 61.2917 | 61.3153 | 61.3491 | 61.3206 | 61.3554 | 123.1246 | 61.5935 | 123.0193 | 61.44 | 61.5076 | 123.0484 | 61.4854 | 122.8449 | 61.6171 | 61.6393 | 61.5117 | 61.5339
849.5938 | 123.381 | -61.4639 | 61.6241 | 0.021127 | -0.20078 | -0.19057 | -0.16237 | -0.1377 | -0.16165 | -0.11765 | 61.6378 | 0.12501 | 61.5508 | -0.033101 | 0.043657 | 61.5799 | 0.007721 | 61.3627 | 61.4851 | 61.2631 | 61.2734 | 61.3016 | 61.3262 | 61.3023 | 61.3463 | 123.1018 | 61.5889 | 123.0147 | 61.4308 | 61.5076 | 123.0438 | 61.4716 | 122.8266 | 61.5942 | 61.6301 | 61.5071 | 61.543
850.5938 | 123.349 | -61.4822 | 61.6333 | 0.01197 | -0.20536 | -0.18599 | -0.16237 | -0.1377 | -0.16165 | -0.11308 | 61.6516 | 0.12043 | 61.5462 | -0.033101 | 0.029923 | 61.5753 | 0.007721 | 61.3672 | 61.4942 | 61.2769 | 61.2963 | 61.3199 | 61.3445 | 61.3206 | 61.3692 | 123.1338 | 61.6027 | 123.0284 | 61.4491 | 61.5122 | 123.0576 | 61.49 | 122.8495 | 61.6216 | 61.6438 | 61.5163 | 61.5385
851.5938 | 123.3948 | -61.4685 | 61.6241 | 0.007391 | -0.2191 | -0.18599 | -0.16695 | -0.12854 | -0.16165 | -0.11765 | 61.6516 | 0.12958 | 61.5462 | -0.033101 | 0.043657 | 61.5799 | 0.007721 | 61.3672 | 61.4759 | 61.2494 | 61.2825 | 61.3016 | 61.34 | 61.3069 | 61.3509 | 123.1201 | 61.5981 | 123.0147 | 61.4354 | 61.5122 | 123.0484 | 61.4762 | 122.8357 | 61.6079 | 61.6438 | 61.5025 | 61.5385
852.5938 | 123.4589 | -61.4639 | 61.6241 | 0.021127 | -0.20994 | -0.19057 | -0.16695 | -0.13312 | -0.16623 | -0.11765 | 61.6516 | 0.12043 | 61.5599 | -0.028522 | 0.034501 | 61.5753 | 0.012299 | 61.3627 | 61.4851 | 61.254 | 61.2734 | 61.297 | 61.3308 | 61.2977 | 61.3463 | 123.1155 | 61.5844 | 123.0238 | 61.4354 | 61.4984 | 123.0392 | 61.4762 | 122.8266 | 61.6171 | 61.6393 | 61.5254 | 61.5476
853.5938 | 123.4177 | -61.4548 | 61.6287 | 0.021127 | -0.21452 | -0.19057 | -0.17153 | -0.14228 | -0.17081 | -0.11765 | 61.6516 | 0.13416 | 61.5508 | -0.033101 | 0.029923 | 61.5753 | 0.007721 | 61.3581 | 61.4759 | 61.2403 | 61.2642 | 61.2832 | 61.3125 | 61.284 | 61.3371 | 123.1063 | 61.5889 | 123.0055 | 61.4217 | 61.4847 | 123.0301 | 61.4625 | 122.8129 | 61.6216 | 61.6438 | 61.5208 | 61.543
854.5938 | 123.4222 | -61.4639 | 61.6425 | 0.016548 | -0.22367 | -0.19514 | -0.17153 | -0.1377 | -0.16623 | -0.12223 | 61.6516 | 0.13416 | 61.5416 | -0.028522 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.4805 | 61.2403 | 61.2688 | 61.2924 | 61.3262 | 61.2977 | 61.3417 | 123.1155 | 61.5981 | 123.0055 | 61.4354 | 61.503 | 123.0484 | 61.4716 | 122.8312 | 61.6125 | 61.6438 | 61.5025 | 61.5339
855.5938 | 123.3719 | -61.441 | 61.6425 | 0.016548 | -0.2191 | -0.19514 | -0.18526 | -0.1377 | -0.16623 | -0.11765 | 61.6516 | 0.13874 | 61.5462 | -0.03768 | 0.048236 | 61.5799 | 0.003143 | 61.3581 | 61.4576 | 61.2219 | 61.2459 | 61.2558 | 61.3033 | 61.2748 | 61.3234 | 123.0926 | 61.5798 | 122.9872 | 61.4034 | 61.4893 | 123.0209 | 61.4442 | 122.7991 | 61.6033 | 61.6484 | 61.4979 | 61.543
856.5938 | 123.3856 | -61.4502 | 61.6562 | 0.01197 | -0.22825 | -0.19514 | -0.17611 | -0.1377 | -0.17539 | -0.12223 | 61.647 | 0.12958 | 61.5416 | -0.033101 | 0.039079 | 61.5845 | 0.012299 | 61.3627 | 61.4622 | 61.2219 | 61.2551 | 61.2741 | 61.3125 | 61.2748 | 61.328 | 123.0972 | 61.5798 | 122.9918 | 61.4171 | 61.4893 | 123.0347 | 61.4625 | 122.8129 | 61.6079 | 61.6347 | 61.5025 | 61.5293
857.5938 | 123.3536 | -61.4594 | 61.615 | 0.021127 | -0.22825 | -0.19972 | -0.17611 | -0.1377 | -0.17081 | -0.13139 | 61.6561 | 0.12501 | 61.5508 | -0.033101 | 0.034501 | 61.5707 | -0.001436 | 61.3581 | 61.4805 | 61.2311 | 61.2596 | 61.2832 | 61.3217 | 61.2885 | 61.328 | 123.1155 | 61.5844 | 123.0101 | 61.4262 | 61.4939 | 123.0301 | 61.4579 | 122.8174 | 61.6216 | 61.6576 | 61.5163 | 61.5522
858.5938 | 123.3948 | -61.4685 | 61.6196 | 0.016548 | -0.2191 | -0.20888 | -0.18069 | -0.1377 | -0.17539 | -0.13139 | 61.6516 | 0.13874 | 61.5553 | -0.028522 | 0.034501 | 61.5799 | 0.007721 | 61.3627 | 61.4851 | 61.2494 | 61.2596 | 61.2878 | 61.3308 | 61.2931 | 61.3371 | 123.1201 | 61.6072 | 123.0238 | 61.44 | 61.503 | 123.0484 | 61.4762 | 122.8312 | 61.6171 | 61.6438 | 61.5208 | 61.5476
859.5938 | 123.4222 | -61.4319 | 61.615 | 0.01197 | -0.22825 | -0.2043 | -0.18984 | -0.14685 | -0.18454 | -0.13139 | 61.6516 | 0.13416 | 61.5508 | -0.033101 | 0.039079 | 61.5799 | 0.007721 | 61.3627 | 61.4439 | 61.2036 | 61.2276 | 61.242 | 61.285 | 61.2473 | 61.3005 | 123.0834 | 61.566 | 122.9826 | 61.3988 | 61.471 | 123.0118 | 61.4396 | 122.7945 | 61.6125 | 61.6438 | 61.5117 | 61.543
860.5938 | 123.4222 | -61.4731 | 61.6333 | 0.01197 | -0.23283 | -0.21346 | -0.18984 | -0.14685 | -0.17539 | -0.12681 | 61.6607 | 0.13416 | 61.5462 | -0.033101 | 0.034501 | 61.5799 | 0.012299 | 61.3581 | 61.4851 | 61.2403 | 61.2596 | 61.2832 | 61.3262 | 61.2977 | 61.3463 | 123.1338 | 61.6072 | 123.0193 | 61.44 | 61.5076 | 123.053 | 61.4854 | 122.8312 | 61.6262 | 61.6484 | 61.5117 | 61.5339
861.5938 | 123.4268 | -61.4502 | 61.6287 | 0.016548 | -0.23283 | -0.21346 | -0.199 | -0.14685 | -0.1937 | -0.13597 | 61.6561 | 0.12043 | 61.5416 | -0.023943 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.4667 | 61.2174 | 61.2367 | 61.2512 | 61.3033 | 61.2565 | 61.3142 | 123.1063 | 61.5706 | 122.9918 | 61.4263 | 61.4893 | 123.0347 | 61.4579 | 122.8129 | 61.6171 | 61.6484 | 61.5025 | 61.5339
862.5938 | 123.3994 | -61.4639 | 61.6379 | 0.01197 | -0.23283 | -0.20888 | -0.19442 | -0.15601 | -0.1937 | -0.13597 | 61.6561 | 0.12501 | 61.5462 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3672 | 61.4759 | 61.2311 | 61.255 | 61.2695 | 61.3079 | 61.2702 | 61.328 | 123.1201 | 61.5889 | 123.0101 | 61.4308 | 61.503 | 123.0484 | 61.4671 | 122.8312 | 61.6171 | 61.653 | 61.5071 | 61.543
863.5938 | 123.3307 | -61.4868 | 61.6104 | 0.021127 | -0.23741 | -0.21804 | -0.19442 | -0.15601 | -0.18912 | -0.14055 | 61.647 | 0.13416 | 61.5553 | -0.033101 | 0.039079 | 61.5753 | 0.012299 | 61.3627 | 61.5079 | 61.2494 | 61.2688 | 61.2924 | 61.3308 | 61.2977 | 61.3463 | 123.1338 | 61.621 | 123.0422 | 61.4537 | 61.5259 | 123.0621 | 61.4991 | 122.8495 | 61.6079 | 61.6347 | 61.5163 | 61.543
864.5938 | 123.4543 | -61.4502 | 61.6287 | 0.016548 | -0.23741 | -0.22262 | -0.19442 | -0.15601 | -0.1937 | -0.14055 | 61.6561 | 0.11585 | 61.5416 | -0.033101 | 0.034501 | 61.5753 | 0.007721 | 61.3672 | 61.4667 | 61.2128 | 61.2276 | 61.2558 | 61.2942 | 61.2565 | 61.3096 | 123.1063 | 61.566 | 122.9918 | 61.4171 | 61.4847 | 123.0255 | 61.4579 | 122.8174 | 61.6216 | 61.6484 | 61.5071 | 61.5339
865.5938 | 123.3398 | -61.4594 | 61.6425 | 0.016548 | -0.24199 | -0.21804 | -0.20816 | -0.16517 | -0.19828 | -0.14512 | 61.647 | 0.12501 | 61.5553 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.4759 | 61.2174 | 61.2413 | 61.2512 | 61.2942 | 61.2611 | 61.3142 | 123.1063 | 61.5844 | 123.0147 | 61.4217 | 61.4984 | 123.0392 | 61.4625 | 122.8266 | 61.6079 | 61.6438 | 61.5163 | 61.5522
866.5938 | 123.381 | -61.441 | 61.6241 | 0.016548 | -0.25115 | -0.22719 | -0.20358 | -0.16974 | -0.20286 | -0.15428 | 61.6561 | 0.12958 | 61.5553 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.4576 | 61.1899 | 61.2138 | 61.2375 | 61.2713 | 61.2382 | 61.2868 | 123.0972 | 61.5706 | 122.9964 | 61.4079 | 61.4801 | 123.0209 | 61.4442 | 122.8083 | 61.6171 | 61.653 | 61.5163 | 61.5522
867.5938 | 123.3856 | -61.4731 | 61.6516 | 0.016548 | -0.25115 | -0.23635 | -0.21274 | -0.16974 | -0.19828 | -0.14512 | 61.6561 | 0.12501 | 61.537 | -0.033101 | 0.039079 | 61.5799 | -0.001436 | 61.3627 | 61.4896 | 61.2219 | 61.2367 | 61.2603 | 61.3033 | 61.2748 | 61.328 | 123.1292 | 61.5981 | 123.0101 | 61.44 | 61.5122 | 123.053 | 61.4716 | 122.8357 | 61.6171 | 61.6576 | 61.4979 | 61.5385
868.5938 | 123.3719 | -61.441 | 61.6241 | 0.01197 | -0.25115 | -0.23635 | -0.21274 | -0.16517 | -0.20286 | -0.15886 | 61.6561 | 0.12043 | 61.5508 | -0.028522 | 0.029923 | 61.5707 | 0.003143 | 61.3627 | 61.453 | 61.1899 | 61.2047 | 61.2283 | 61.2759 | 61.2382 | 61.2822 | 123.0972 | 61.5615 | 122.9918 | 61.4125 | 61.471 | 123.0118 | 61.4442 | 122.8037 | 61.6262 | 61.653 | 61.5208 | 61.5476
869.5938 | 123.349 | -61.4685 | 61.6058 | 0.016548 | -0.24199 | -0.23635 | -0.20816 | -0.16974 | -0.20743 | -0.15886 | 61.6516 | 0.12501 | 61.5462 | -0.03768 | 0.039079 | 61.5799 | 0.003143 | 61.3672 | 61.4851 | 61.2265 | 61.2322 | 61.2603 | 61.2988 | 61.2611 | 61.3096 | 123.1201 | 61.5935 | 123.0147 | 61.4308 | 61.5076 | 123.0484 | 61.4716 | 122.8357 | 61.6125 | 61.6484 | 61.5071 | 61.543
870.5938 | 123.3856 | -61.4639 | 61.615 | 0.01197 | -0.24199 | -0.22262 | -0.199 | -0.16517 | -0.19828 | -0.1497 | 61.6516 | 0.13874 | 61.5599 | -0.03768 | 0.039079 | 61.5753 | 0.007721 | 61.3581 | 61.4759 | 61.2219 | 61.2413 | 61.2649 | 61.2988 | 61.2657 | 61.3142 | 123.1155 | 61.6027 | 123.0238 | 61.4262 | 61.503 | 123.0392 | 61.4716 | 122.822 | 61.6125 | 61.6438 | 61.5208 | 61.5522
871.5938 | 123.3627 | -61.4685 | 61.6013 | 0.01197 | -0.24199 | -0.21804 | -0.20816 | -0.15601 | -0.1937 | -0.15428 | 61.6516 | 0.12043 | 61.5508 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3535 | 61.4805 | 61.2265 | 61.2505 | 61.2603 | 61.3125 | 61.2748 | 61.3142 | 123.1201 | 61.5889 | 123.0193 | 61.4354 | 61.503 | 123.0484 | 61.4716 | 122.822 | 61.6171 | 61.6484 | 61.5163 | 61.5476
872.5938 | 123.3398 | -61.4868 | 61.6104 | 0.016548 | -0.23741 | -0.22262 | -0.21274 | -0.16517 | -0.19828 | -0.14512 | 61.6516 | 0.12043 | 61.5462 | -0.033101 | 0.039079 | 61.5845 | 0.003143 | 61.3581 | 61.5034 | 61.2494 | 61.2642 | 61.2741 | 61.3217 | 61.2885 | 61.3417 | 123.1384 | 61.6072 | 123.033 | 61.4537 | 61.5259 | 123.0713 | 61.49 | 122.8449 | 61.6125 | 61.6484 | 61.5071 | 61.543
873.5938 | 123.3673 | -61.4639 | 61.6104 | 0.016548 | -0.24657 | -0.23177 | -0.20816 | -0.16517 | -0.20286 | -0.15886 | 61.6516 | 0.12958 | 61.5508 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3672 | 61.4805 | 61.2174 | 61.2322 | 61.2558 | 61.2988 | 61.2611 | 61.3051 | 123.1155 | 61.5935 | 123.0147 | 61.4308 | 61.503 | 123.0484 | 61.4716 | 122.8312 | 61.6125 | 61.6438 | 61.5117 | 61.543
874.5938 | 123.3719 | -61.496 | 61.6287 | 0.021127 | -0.24657 | -0.22719 | -0.20358 | -0.16517 | -0.19828 | -0.1497 | 61.6516 | 0.11585 | 61.5462 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 61.3627 | 61.5171 | 61.2494 | 61.2688 | 61.2924 | 61.3308 | 61.2977 | 61.3463 | 123.1475 | 61.6118 | 123.0422 | 61.4629 | 61.5351 | 123.0804 | 61.5037 | 122.8586 | 61.6125 | 61.6438 | 61.5071 | 61.5385
875.5938 | 123.3856 | -61.4594 | 61.6104 | 0.016548 | -0.25115 | -0.23635 | -0.21274 | -0.16517 | -0.20286 | -0.15428 | 61.6561 | 0.12958 | 61.5508 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3581 | 61.4759 | 61.2082 | 61.223 | 61.2466 | 61.2942 | 61.2565 | 61.3051 | 123.1155 | 61.5889 | 123.0101 | 61.4262 | 61.4984 | 123.0392 | 61.4625 | 122.8174 | 61.6171 | 61.653 | 61.5117 | 61.5476
876.5938 | 123.3902 | -61.4822 | 61.5967 | 0.016548 | -0.24657 | -0.23177 | -0.21731 | -0.16974 | -0.21201 | -0.15886 | 61.6561 | 0.13874 | 61.5553 | -0.03768 | 0.034501 | 61.5753 | 0.003143 | 61.3581 | 61.4988 | 61.2357 | 61.2505 | 61.2649 | 61.3125 | 61.2702 | 61.3234 | 123.1384 | 61.621 | 123.0376 | 61.4446 | 61.5167 | 123.0576 | 61.4854 | 122.8403 | 61.6216 | 61.653 | 61.5208 | 61.5522
877.5938 | 123.4039 | -61.4731 | 61.6241 | 0.025705 | -0.25115 | -0.23635 | -0.22189 | -0.16517 | -0.20286 | -0.15428 | 61.6516 | 0.13416 | 61.5553 | -0.033101 | 0.039079 | 61.5753 | -0.001436 | 61.3581 | 61.4988 | 61.2219 | 61.2367 | 61.2512 | 61.3079 | 61.2702 | 61.3188 | 123.1246 | 61.6072 | 123.0284 | 61.44 | 61.5122 | 123.0484 | 61.4716 | 122.8312 | 61.6125 | 61.653 | 61.5163 | 61.5568
878.5938 | 123.3765 | -61.4914 | 61.615 | 0.016548 | -0.25572 | -0.24551 | -0.22189 | -0.16974 | -0.21201 | -0.15428 | 61.6516 | 0.12043 | 61.5416 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3581 | 61.5079 | 61.2357 | 61.2459 | 61.2695 | 61.3217 | 61.2794 | 61.3371 | 123.143 | 61.6118 | 123.033 | 61.4583 | 61.5259 | 123.0713 | 61.4945 | 122.8495 | 61.6171 | 61.6484 | 61.5071 | 61.5385
879.5938 | 123.3673 | -61.4822 | 61.615 | 0.021127 | -0.25572 | -0.24093 | -0.21731 | -0.16974 | -0.21201 | -0.15886 | 61.6516 | 0.12501 | 61.5508 | -0.033101 | 0.034501 | 61.5753 | 0.012299 | 61.3581 | 61.5034 | 61.2265 | 61.2413 | 61.2649 | 61.3125 | 61.2702 | 61.3234 | 123.1338 | 61.6072 | 123.033 | 61.4491 | 61.5167 | 123.0576 | 61.4945 | 122.8403 | 61.6171 | 61.6393 | 61.5163 | 61.5385
880.5938 | 123.3536 | -61.4548 | 61.5372 | 0.01197 | -0.26488 | -0.24093 | -0.22189 | -0.1789 | -0.20743 | -0.16344 | 61.6561 | 0.12043 | 61.5416 | -0.033101 | 0.039079 | 61.5799 | 0.003143 | 61.3581 | 61.4667 | 61.1899 | 61.2138 | 61.2329 | 61.2759 | 61.2473 | 61.2913 | 123.1109 | 61.5752 | 122.9964 | 61.4217 | 61.4939 | 123.0347 | 61.4579 | 122.8129 | 61.6171 | 61.653 | 61.5025 | 61.5385
881.5938 | 123.2483 | -61.4777 | 61.6791 | 0.021127 | -0.26946 | -0.24551 | -0.23105 | -0.1789 | -0.21659 | -0.16801 | 61.6607 | 0.12958 | 61.5553 | -0.028522 | 0.039079 | 61.5753 | 0.007721 | 61.3535 | 61.4988 | 61.2082 | 61.2322 | 61.2466 | 61.2988 | 61.2611 | 61.3096 | 123.1384 | 61.6072 | 123.033 | 61.4491 | 61.5167 | 123.053 | 61.4854 | 122.8312 | 61.6216 | 61.653 | 61.5163 | 61.5476
882.5938 | 123.3444 | -61.5005 | 61.6425 | 0.016548 | -0.26946 | -0.23635 | -0.22189 | -0.18348 | -0.21659 | -0.17259 | 61.6516 | 0.12501 | 61.5462 | -0.033101 | 0.043657 | 61.5753 | 0.003143 | 61.3581 | 61.5171 | 61.2311 | 61.2642 | 61.2787 | 61.3171 | 61.284 | 61.328 | 123.1521 | 61.6256 | 123.0467 | 61.4674 | 61.5442 | 123.0759 | 61.5037 | 122.8586 | 61.6079 | 61.6484 | 61.5025 | 61.543
883.5938 | 123.3124 | -61.4822 | 61.6379 | 0.021127 | -0.26946 | -0.24551 | -0.23105 | -0.18348 | -0.22575 | -0.17259 | 61.6607 | 0.13874 | 61.5645 | -0.028522 | 0.039079 | 61.5799 | -0.001436 | 61.3535 | 61.5034 | 61.2128 | 61.2367 | 61.2512 | 61.2988 | 61.2565 | 61.3096 | 123.143 | 61.621 | 123.0467 | 61.4537 | 61.5213 | 123.0621 | 61.4808 | 122.8357 | 61.6216 | 61.6622 | 61.5254 | 61.5659
884.5938 | 123.2758 | -61.5051 | 61.6653 | 0.025705 | -0.26946 | -0.25009 | -0.22647 | -0.18805 | -0.22575 | -0.17717 | 61.6561 | 0.12043 | 61.5553 | -0.023943 | 0.034501 | 61.5753 | -0.001436 | 61.3581 | 61.5308 | 61.2357 | 61.255 | 61.2787 | 61.3171 | 61.2794 | 61.328 | 123.1613 | 61.6256 | 123.0605 | 61.4812 | 61.5396 | 123.0804 | 61.5037 | 122.8632 | 61.6216 | 61.6576 | 61.5208 | 61.5568
885.5938 | 123.2895 | -61.4822 | 61.6653 | 0.01197 | -0.27404 | -0.24551 | -0.23105 | -0.18805 | -0.22575 | -0.17717 | 61.6653 | 0.12043 | 61.5553 | -0.033101 | 0.034501 | 61.5707 | 0.007721 | 61.3581 | 61.4942 | 61.2082 | 61.2367 | 61.2512 | 61.2942 | 61.2565 | 61.3051 | 123.1475 | 61.6027 | 123.0376 | 61.4491 | 61.5167 | 123.053 | 61.49 | 122.8403 | 61.6308 | 61.6576 | 61.5208 | 61.5476
886.5938 | 123.3856 | -61.4548 | 61.6104 | 0.016548 | -0.27404 | -0.26382 | -0.23563 | -0.19263 | -0.23033 | -0.18175 | 61.6607 | 0.12043 | 61.5508 | -0.028522 | 0.034501 | 61.5753 | 0.003143 | 61.3581 | 61.4713 | 61.1807 | 61.191 | 61.2191 | 61.2621 | 61.2244 | 61.273 | 123.1155 | 61.5752 | 123.0055 | 61.4263 | 61.4893 | 123.0301 | 61.4579 | 122.8129 | 61.6262 | 61.6576 | 61.5163 | 61.5476
887.5938 | 123.262 | -61.4639 | 61.6653 | 0.016548 | -0.28778 | -0.25924 | -0.24021 | -0.20179 | -0.23033 | -0.18175 | 61.6607 | 0.11585 | 61.5508 | -0.033101 | 0.039079 | 61.5707 | 0.003143 | 61.3581 | 61.4805 | 61.1762 | 61.2047 | 61.2237 | 61.2621 | 61.2336 | 61.2822 | 123.1246 | 61.5798 | 123.0147 | 61.4308 | 61.503 | 123.0347 | 61.4671 | 122.822 | 61.6216 | 61.6576 | 61.5117 | 61.5476
888.5938 | 123.2346 | -61.4685 | 61.7065 | 0.021127 | -0.27862 | -0.26382 | -0.23563 | -0.20179 | -0.23033 | -0.18175 | 61.6653 | 0.11585 | 61.5599 | -0.03768 | 0.039079 | 61.5662 | 0.003143 | 61.3489 | 61.4896 | 61.1899 | 61.2047 | 61.2329 | 61.2667 | 61.2382 | 61.2868 | 123.1338 | 61.5844 | 123.0284 | 61.4308 | 61.5076 | 123.0347 | 61.4716 | 122.8174 | 61.6262 | 61.6622 | 61.5208 | 61.5568
889.5938 | 123.23 | -61.4777 | 61.6379 | 0.021127 | -0.2832 | -0.26382 | -0.24021 | -0.19721 | -0.23033 | -0.18633 | 61.6607 | 0.12501 | 61.5416 | -0.042259 | 0.043657 | 61.5707 | 0.007721 | 61.3581 | 61.4988 | 61.1945 | 61.2138 | 61.2375 | 61.2804 | 61.2473 | 61.2913 | 123.1384 | 61.6027 | 123.0193 | 61.4354 | 61.5213 | 123.0484 | 61.4854 | 122.8357 | 61.6171 | 61.653 | 61.4979 | 61.5339
890.5938 | 123.2574 | -61.4822 | 61.6653 | 0.016548 | -0.2832 | -0.27298 | -0.24936 | -0.20637 | -0.2349 | -0.18175 | 61.6607 | 0.11127 | 61.5553 | -0.03768 | 0.034501 | 61.5753 | 0.003143 | 61.3627 | 61.4988 | 61.199 | 61.2093 | 61.2329 | 61.2759 | 61.2473 | 61.3005 | 123.143 | 61.5935 | 123.0376 | 61.4446 | 61.5167 | 123.0576 | 61.4854 | 122.8449 | 61.6262 | 61.6576 | 61.5208 | 61.5522
891.5938 | 123.3856 | -61.4273 | 61.647 | 0.016548 | -0.28778 | -0.27298 | -0.24479 | -0.20179 | -0.23948 | -0.18633 | 61.6699 | 0.12043 | 61.5599 | -0.03768 | 0.034501 | 61.5707 | 0.007721 | 61.3581 | 61.4439 | 61.1395 | 61.1543 | 61.1825 | 61.2255 | 61.1878 | 61.241 | 123.0972 | 61.5477 | 122.9872 | 61.3896 | 61.4618 | 122.998 | 61.435 | 122.7854 | 61.6354 | 61.6622 | 61.5254 | 61.5522
892.5938 | 123.3307 | -61.4502 | 61.6974 | 0.01197 | -0.29236 | -0.2684 | -0.25394 | -0.20179 | -0.24406 | -0.19548 | 61.6653 | 0.12958 | 61.5645 | -0.03768 | 0.043657 | 61.5616 | 0.003143 | 61.3535 | 61.4622 | 61.1578 | 61.1818 | 61.1963 | 61.2484 | 61.2061 | 61.2547 | 123.1155 | 61.5798 | 123.0147 | 61.4125 | 61.4939 | 123.0118 | 61.4533 | 122.8037 | 61.6216 | 61.6622 | 61.5208 | 61.5614
893.5938 | 123.2712 | -61.4868 | 61.6882 | 0.01197 | -0.29236 | -0.28214 | -0.24936 | -0.21094 | -0.25322 | -0.20006 | 61.6745 | 0.12043 | 61.5691 | -0.028522 | 0.034501 | 61.5662 | 0.003143 | 61.3489 | 61.4988 | 61.1945 | 61.2047 | 61.2375 | 61.2759 | 61.2336 | 61.2868 | 123.1613 | 61.6072 | 123.0559 | 61.4583 | 61.5213 | 123.053 | 61.49 | 122.8357 | 61.64 | 61.6713 | 61.5346 | 61.5659
894.5938 | 123.2529 | -61.496 | 61.6562 | 0.016548 | -0.29236 | -0.28214 | -0.2631 | -0.21094 | -0.25322 | -0.19548 | 61.6653 | 0.11585 | 61.5599 | -0.033101 | 0.034501 | 61.5799 | 0.003143 | 61.3627 | 61.5125 | 61.2036 | 61.2138 | 61.2329 | 61.285 | 61.2428 | 61.3005 | 123.1613 | 61.6118 | 123.0559 | 61.4629 | 61.5305 | 123.0759 | 61.4991 | 122.8586 | 61.6308 | 61.6622 | 61.5254 | 61.5568
895.5938 | 123.2666 | -61.4868 | 61.6837 | 0.021127 | -0.30609 | -0.28214 | -0.2631 | -0.21552 | -0.26238 | -0.20006 | 61.6653 | 0.10669 | 61.5553 | -0.03768 | 0.039079 | 61.5707 | 0.012299 | 61.3581 | 61.5079 | 61.1807 | 61.2047 | 61.2237 | 61.2713 | 61.2244 | 61.2868 | 123.1521 | 61.5935 | 123.0422 | 61.4491 | 61.5259 | 123.0576 | 61.4991 | 122.8449 | 61.6262 | 61.653 | 61.5163 | 61.543
896.5938 | 123.2758 | -61.4731 | 61.6653 | 0.016548 | -0.30151 | -0.28672 | -0.26768 | -0.21552 | -0.25322 | -0.20922 | 61.6745 | 0.12501 | 61.5599 | -0.03768 | 0.039079 | 61.5707 | 0.007721 | 61.3581 | 61.4896 | 61.1716 | 61.1864 | 61.2054 | 61.2576 | 61.2199 | 61.2639 | 123.1475 | 61.5981 | 123.033 | 61.4354 | 61.5122 | 123.0438 | 61.4808 | 122.8312 | 61.6354 | 61.6667 | 61.5208 | 61.5522
897.5938 | 123.3032 | -61.4548 | 61.6653 | 0.021127 | -0.30609 | -0.28672 | -0.26768 | -0.21094 | -0.26238 | -0.20464 | 61.6699 | 0.12043 | 61.5599 | -0.046838 | 0.034501 | 61.5707 | -0.001436 | 61.3581 | 61.4759 | 61.1487 | 61.1681 | 61.1871 | 61.2438 | 61.1924 | 61.2501 | 123.1246 | 61.5752 | 123.0147 | 61.4079 | 61.4893 | 123.0255 | 61.4533 | 122.8129 | 61.6354 | 61.6713 | 61.5254 | 61.5614
898.5938 | 123.3261 | -61.441 | 61.7111 | 0.016548 | -0.31067 | -0.29129 | -0.26768 | -0.22468 | -0.26695 | -0.20464 | 61.6836 | 0.13416 | 61.5874 | -0.03768 | 0.043657 | 61.5524 | 0.003143 | 61.3443 | 61.4576 | 61.1304 | 61.1497 | 61.1734 | 61.2164 | 61.1741 | 61.2364 | 123.1247 | 61.5752 | 123.0284 | 61.4034 | 61.4847 | 122.9935 | 61.4442 | 122.7854 | 61.64 | 61.6805 | 61.5437 | 61.5842
899.5938 | 123.3398 | -61.4594 | 61.6882 | 0.021127 | -0.31067 | -0.29587 | -0.26768 | -0.22468 | -0.27153 | -0.2138 | 61.679 | 0.12958 | 61.5737 | -0.03768 | 0.043657 | 61.5616 | 0.007721 | 61.3443 | 61.4805 | 61.1487 | 61.1635 | 61.1917 | 61.2347 | 61.1878 | 61.2456 | 123.1384 | 61.5889 | 123.033 | 61.4217 | 61.503 | 123.0209 | 61.4671 | 122.8037 | 61.6354 | 61.6713 | 61.53 | 61.5659
900.5938 | 123.3307 | -61.4594 | 61.6837 | 0.01197 | -0.31525 | -0.28672 | -0.27226 | -0.2201 | -0.26238 | -0.2138 | 61.6745 | 0.12043 | 61.5691 | -0.042259 | 0.039079 | 61.5524 | -0.001436 | 61.3535 | 61.4713 | 61.1441 | 61.1726 | 61.1871 | 61.2392 | 61.197 | 61.2456 | 123.1338 | 61.5798 | 123.0284 | 61.4171 | 61.4984 | 123.0118 | 61.4579 | 122.8129 | 61.6354 | 61.6759 | 61.53 | 61.5705
901.5938 | 123.262 | -61.4594 | 61.6791 | 0.016548 | -0.31067 | -0.29587 | -0.27226 | -0.2201 | -0.26238 | -0.2138 | 61.6653 | 0.11585 | 61.5508 | -0.033101 | 0.039079 | 61.5707 | 0.003143 | 61.3535 | 61.4759 | 61.1487 | 61.1635 | 61.1871 | 61.2392 | 61.197 | 61.2456 | 123.1246 | 61.5752 | 123.0101 | 61.4262 | 61.4984 | 123.0301 | 61.4625 | 122.8129 | 61.6262 | 61.6622 | 61.5117 | 61.5476
902.5938 | 123.2803 | -61.4594 | 61.6745 | 0.021127 | -0.31525 | -0.30045 | -0.27683 | -0.23383 | -0.27153 | -0.2138 | 61.6699 | 0.11585 | 61.5599 | -0.033101 | 0.039079 | 61.5616 | 0.003143 | 61.3535 | 61.4805 | 61.1441 | 61.1589 | 61.1825 | 61.2255 | 61.1878 | 61.2456 | 123.1292 | 61.5752 | 123.0193 | 61.4262 | 61.4984 | 123.0209 | 61.4625 | 122.8129 | 61.6308 | 61.6667 | 61.5208 | 61.5568
903.5938 | 123.2941 | -61.4502 | 61.6837 | 0.01197 | -0.31983 | -0.30045 | -0.27683 | -0.22926 | -0.27153 | -0.21838 | 61.6882 | 0.12501 | 61.5874 | -0.033101 | 0.039079 | 61.5524 | 0.003143 | 61.3398 | 61.4622 | 61.1304 | 61.1497 | 61.1734 | 61.2209 | 61.1787 | 61.2318 | 123.1384 | 61.5752 | 123.0376 | 61.4171 | 61.4893 | 123.0026 | 61.4533 | 122.79 | 61.6491 | 61.685 | 61.5483 | 61.5842
904.5938 | 123.3261 | -61.4685 | 61.6882 | 0.016548 | -0.33357 | -0.30961 | -0.29057 | -0.23841 | -0.28527 | -0.22295 | 61.679 | 0.12043 | 61.5737 | -0.033101 | 0.034501 | 61.5616 | 0.003143 | 61.3535 | 61.4851 | 61.1349 | 61.1589 | 61.1779 | 61.2301 | 61.1832 | 61.2456 | 123.1475 | 61.5889 | 123.0422 | 61.4354 | 61.503 | 123.0301 | 61.4716 | 122.822 | 61.6445 | 61.6759 | 61.5392 | 61.5705
905.5938 | 123.3307 | -61.4227 | 61.7111 | 0.016548 | -0.33357 | -0.31419 | -0.29057 | -0.24299 | -0.28527 | -0.23211 | 61.7019 | 0.12958 | 61.6011 | -0.033101 | 0.048236 | 61.5341 | 0.012299 | 61.3169 | 61.4393 | 61.0892 | 61.1085 | 61.1322 | 61.1797 | 61.1375 | 61.1906 | 123.1247 | 61.5523 | 123.0239 | 61.3896 | 61.471 | 122.9568 | 61.435 | 122.7396 | 61.6537 | 61.6896 | 61.5529 | 61.5888
906.5938 | 123.3261 | -61.4182 | 61.7157 | 0.016548 | -0.33357 | -0.31419 | -0.29057 | -0.25215 | -0.28069 | -0.24127 | 61.6836 | 0.12043 | 61.5737 | -0.033101 | 0.039079 | 61.5524 | 0.007721 | 61.3398 | 61.4347 | 61.0846 | 61.104 | 61.1276 | 61.166 | 61.1375 | 61.1769 | 123.1018 | 61.5386 | 122.9918 | 61.3851 | 61.4572 | 122.9706 | 61.4259 | 122.7579 | 61.6445 | 61.6759 | 61.5346 | 61.5659
907.5938 | 123.2758 | -61.4365 | 61.6882 | 0.01197 | -0.32899 | -0.31419 | -0.29515 | -0.24299 | -0.28527 | -0.22753 | 61.6928 | 0.12501 | 61.5828 | -0.03768 | 0.039079 | 61.5433 | 0.003143 | 61.3352 | 61.4484 | 61.1075 | 61.1223 | 61.1413 | 61.1935 | 61.1512 | 61.2089 | 123.1292 | 61.5615 | 123.0193 | 61.3988 | 61.4755 | 122.9797 | 61.4396 | 122.7717 | 61.6537 | 61.6896 | 61.5437 | 61.5797
908.5938 | 123.3032 | -61.4319 | 61.6974 | 0.01197 | -0.33814 | -0.32792 | -0.29973 | -0.24757 | -0.28527 | -0.23211 | 61.6836 | 0.11585 | 61.5691 | -0.03768 | 0.039079 | 61.5616 | -0.001436 | 61.3398 | 61.4439 | 61.0937 | 61.104 | 61.1322 | 61.1843 | 61.1466 | 61.1998 | 123.1155 | 61.5477 | 123.001 | 61.3942 | 61.471 | 122.9935 | 61.4304 | 122.7717 | 61.6445 | 61.685 | 61.53 | 61.5705
909.5938 | 123.2849 | -61.4548 | 61.6974 | 0.021127 | -0.33814 | -0.32334 | -0.29973 | -0.25215 | -0.29442 | -0.23669 | 61.6882 | 0.12958 | 61.5828 | -0.042259 | 0.039079 | 61.5478 | 0.007721 | 61.3352 | 61.4759 | 61.1166 | 61.1314 | 61.155 | 61.2026 | 61.1604 | 61.2181 | 123.143 | 61.5844 | 123.0376 | 61.4125 | 61.4939 | 123.0026 | 61.4625 | 122.79 | 61.6491 | 61.6805 | 61.5437 | 61.5751
910.5938 | 123.3261 | -61.4502 | 61.6882 | 0.016548 | -0.3473 | -0.32792 | -0.3043 | -0.26588 | -0.30358 | -0.25042 | 61.679 | 0.11585 | 61.5737 | -0.033101 | 0.034501 | 61.5616 | 0.007721 | 61.3489 | 61.4667 | 61.1029 | 61.1223 | 61.1459 | 61.1843 | 61.1466 | 61.1998 | 123.1292 | 61.566 | 123.0238 | 61.4171 | 61.4847 | 123.0118 | 61.4579 | 122.7991 | 61.6445 | 61.6713 | 61.5392 | 61.5659
911.5938 | 123.349 | -61.4548 | 61.734 | 0.01197 | -0.3473 | -0.33708 | -0.31346 | -0.2613 | -0.30816 | -0.255 | 61.6928 | 0.12501 | 61.5874 | -0.033101 | 0.034501 | 61.5478 | 0.012299 | 61.3352 | 61.4667 | 61.1075 | 61.1177 | 61.1413 | 61.1935 | 61.1466 | 61.1998 | 123.1475 | 61.5798 | 123.0422 | 61.4217 | 61.4893 | 123.0026 | 61.4671 | 122.79 | 61.6583 | 61.6805 | 61.5529 | 61.5751
912.5938 | 123.3353 | -61.4502 | 61.7065 | 0.007391 | -0.36104 | -0.34624 | -0.31804 | -0.2613 | -0.30816 | -0.255 | 61.6928 | 0.12501 | 61.5828 | -0.028522 | 0.039079 | 61.5433 | 0.012299 | 61.3443 | 61.4576 | 61.0892 | 61.104 | 61.1322 | 61.1889 | 61.142 | 61.1952 | 123.143 | 61.5752 | 123.033 | 61.4217 | 61.4893 | 122.9935 | 61.4625 | 122.7945 | 61.6537 | 61.6805 | 61.5437 | 61.5705
913.5938 | 123.3353 | -61.4594 | 61.7386 | 0.01197 | -0.36562 | -0.34624 | -0.3272 | -0.27961 | -0.31732 | -0.26416 | 61.7065 | 0.12958 | 61.6194 | -0.03768 | 0.039079 | 61.5295 | 0.012299 | 61.3169 | 61.4713 | 61.0937 | 61.1131 | 61.1322 | 61.1797 | 61.142 | 61.1952 | 123.1659 | 61.5889 | 123.0788 | 61.4217 | 61.4984 | 122.9889 | 61.4716 | 122.7762 | 61.6674 | 61.6942 | 61.5804 | 61.6071
914.5938 | 123.2849 | -61.4319 | 61.7111 | 0.016548 | -0.36562 | -0.34624 | -0.32262 | -0.28419 | -0.32189 | -0.25958 | 61.6973 | 0.12501 | 61.5828 | -0.042259 | 0.039079 | 61.5433 | 0.003143 | 61.326 | 61.4484 | 61.0663 | 61.0856 | 61.1093 | 61.1477 | 61.11 | 61.1723 | 123.1292 | 61.5569 | 123.0147 | 61.3896 | 61.471 | 122.9752 | 61.435 | 122.7579 | 61.6583 | 61.6942 | 61.5437 | 61.5797
915.5938 | 123.3124 | -61.441 | 61.7249 | 0.01197 | -0.36562 | -0.34624 | -0.33178 | -0.27961 | -0.31732 | -0.26874 | 61.6836 | 0.12043 | 61.5828 | -0.03768 | 0.034501 | 61.5524 | 0.007721 | 61.3398 | 61.453 | 61.0754 | 61.0948 | 61.1093 | 61.1614 | 61.1237 | 61.1723 | 123.1247 | 61.5615 | 123.0239 | 61.4034 | 61.4755 | 122.9935 | 61.4488 | 122.7808 | 61.6491 | 61.6759 | 61.5483 | 61.5751
916.5938 | 123.3673 | -61.4319 | 61.702 | 0.016548 | -0.37477 | -0.35997 | -0.33636 | -0.27961 | -0.32189 | -0.26416 | 61.7065 | 0.12958 | 61.6011 | -0.03768 | 0.034501 | 61.5433 | 0.007721 | 61.3215 | 61.4484 | 61.0571 | 61.0719 | 61.0955 | 61.1523 | 61.11 | 61.1677 | 123.1384 | 61.5615 | 123.033 | 61.3942 | 61.4664 | 122.9752 | 61.4396 | 122.7533 | 61.672 | 61.6988 | 61.5666 | 61.5934
917.5938 | 123.349 | -61.4548 | 61.7065 | 0.016548 | -0.37935 | -0.36455 | -0.34093 | -0.29335 | -0.33563 | -0.28705 | 61.6836 | 0.12958 | 61.5828 | -0.03768 | 0.034501 | 61.557 | 0.003143 | 61.3489 | 61.4713 | 61.0754 | 61.0902 | 61.1138 | 61.1614 | 61.1191 | 61.1677 | 123.1384 | 61.5844 | 123.0376 | 61.4171 | 61.4893 | 123.0118 | 61.4579 | 122.8037 | 61.6491 | 61.6805 | 61.5483 | 61.5797
918.5938 | 123.3261 | -61.3998 | 61.7065 | 0.016548 | -0.39309 | -0.37371 | -0.35009 | -0.3025 | -0.34479 | -0.2962 | 61.6973 | 0.13416 | 61.6011 | -0.033101 | 0.043657 | 61.5387 | 0.003143 | 61.3306 | 61.4164 | 61.0068 | 61.0261 | 61.0498 | 61.0973 | 61.0551 | 61.1036 | 123.0972 | 61.534 | 123.001 | 61.3667 | 61.4435 | 122.9385 | 61.403 | 122.7305 | 61.6537 | 61.6942 | 61.5575 | 61.598
919.5938 | 123.3398 | -61.4365 | 61.734 | 0.016548 | -0.38851 | -0.38287 | -0.35467 | -0.30708 | -0.35852 | -0.2962 | 61.6882 | 0.12958 | 61.5782 | -0.03768 | 0.039079 | 61.5616 | 0.007721 | 61.3443 | 61.453 | 61.048 | 61.0536 | 61.0818 | 61.1294 | 61.0779 | 61.1403 | 123.1247 | 61.566 | 123.0147 | 61.3988 | 61.4755 | 122.998 | 61.4442 | 122.7808 | 61.6491 | 61.6805 | 61.5392 | 61.5705
920.5938 | 123.2666 | -61.4456 | 61.7432 | 0.016548 | -0.40683 | -0.39202 | -0.3684 | -0.32082 | -0.35852 | -0.2962 | 61.6836 | 0.12043 | 61.5691 | -0.042259 | 0.043657 | 61.5616 | 0.007721 | 61.3443 | 61.4622 | 61.0388 | 61.0536 | 61.0772 | 61.1248 | 61.0871 | 61.1494 | 123.1292 | 61.566 | 123.0147 | 61.4034 | 61.4893 | 123.0072 | 61.4533 | 122.79 | 61.64 | 61.6759 | 61.5254 | 61.5614
921.5938 | 123.2346 | -61.4365 | 61.702 | 0.007391 | -0.40225 | -0.38744 | -0.3684 | -0.31624 | -0.3631 | -0.30078 | 61.6928 | 0.11585 | 61.5874 | -0.028522 | 0.043657 | 61.5433 | -0.001436 | 61.3306 | 61.4439 | 61.0342 | 61.049 | 61.0681 | 61.1202 | 61.0734 | 61.1357 | 123.1292 | 61.5523 | 123.0239 | 61.4079 | 61.4801 | 122.9797 | 61.435 | 122.7671 | 61.6491 | 61.6942 | 61.5437 | 61.5888
922.5938 | 123.3353 | -61.4136 | 61.7432 | 0.002813 | -0.41598 | -0.3966 | -0.3684 | -0.32539 | -0.36768 | -0.30994 | 61.7111 | 0.11585 | 61.6057 | -0.03768 | 0.043657 | 61.5158 | 0.007721 | 61.3077 | 61.4164 | 60.9976 | 61.017 | 61.0452 | 61.0882 | 61.0459 | 61.1036 | 123.1247 | 61.5294 | 123.0193 | 61.3759 | 61.4572 | 122.9294 | 61.4213 | 122.7213 | 61.6674 | 61.7034 | 61.562 | 61.598
923.5938 | 123.317 | -61.3998 | 61.7477 | 0.016548 | -0.41141 | -0.39202 | -0.37298 | -0.32539 | -0.3631 | -0.30994 | 61.7111 | 0.12501 | 61.6057 | -0.033101 | 0.039079 | 61.525 | 0.003143 | 61.3123 | 61.4164 | 60.9884 | 61.0078 | 61.0269 | 61.0744 | 61.0367 | 61.0899 | 123.1109 | 61.5248 | 123.0055 | 61.3667 | 61.4389 | 122.9248 | 61.403 | 122.7121 | 61.672 | 61.7079 | 61.5666 | 61.6026
924.5938 | 123.3078 | -61.409 | 61.7432 | 0.007391 | -0.42056 | -0.41034 | -0.38214 | -0.33455 | -0.38141 | -0.31452 | 61.6973 | 0.12958 | 61.5874 | -0.033101 | 0.043657 | 61.5433 | 0.003143 | 61.3306 | 61.4164 | 60.9884 | 60.9987 | 61.0269 | 61.0744 | 61.0276 | 61.0945 | 123.1063 | 61.5386 | 122.9964 | 61.3759 | 61.4527 | 122.9523 | 61.4121 | 122.7396 | 61.6537 | 61.6942 | 61.5437 | 61.5842
925.5938 | 123.349 | -61.4136 | 61.6837 | 0.01197 | -0.42514 | -0.41034 | -0.38214 | -0.34371 | -0.37683 | -0.3191 | 61.6973 | 0.12958 | 61.6011 | -0.033101 | 0.048236 | 61.5433 | 0.003143 | 61.3306 | 61.4255 | 60.9884 | 61.0032 | 61.0314 | 61.0699 | 61.0367 | 61.0945 | 123.1109 | 61.5432 | 123.0147 | 61.3805 | 61.4618 | 122.9568 | 61.4167 | 122.7442 | 61.6491 | 61.6942 | 61.5529 | 61.598
926.5938 | 123.2849 | -61.4594 | 61.7111 | 0.007391 | -0.42056 | -0.41034 | -0.38214 | -0.32997 | -0.37683 | -0.31452 | 61.7065 | 0.12958 | 61.6011 | -0.023943 | 0.039079 | 61.5341 | 0.007721 | 61.3123 | 61.4667 | 61.0388 | 61.049 | 61.0772 | 61.1294 | 61.0825 | 61.1448 | 123.1659 | 61.5889 | 123.0605 | 61.4354 | 61.4984 | 122.9935 | 61.4671 | 122.7717 | 61.6674 | 61.6988 | 61.562 | 61.5934
927.5938 | 123.3124 | -61.4182 | 61.7249 | 0.01197 | -0.42056 | -0.40576 | -0.38214 | -0.33455 | -0.37683 | -0.30994 | 61.7019 | 0.12501 | 61.6011 | -0.028522 | 0.039079 | 61.5387 | 0.012299 | 61.326 | 61.4301 | 60.9976 | 61.0124 | 61.036 | 61.0836 | 61.0413 | 61.1082 | 123.1201 | 61.5432 | 123.0193 | 61.3896 | 61.4572 | 122.9568 | 61.4305 | 122.7442 | 61.6628 | 61.6896 | 61.562 | 61.5888
928.5938 | 123.3398 | -61.4365 | 61.7065 | 0.021127 | -0.4343 | -0.4195 | -0.3913 | -0.34371 | -0.38141 | -0.33283 | 61.6928 | 0.11585 | 61.592 | -0.033101 | 0.039079 | 61.5387 | 0.003143 | 61.3306 | 61.4576 | 61.0022 | 61.017 | 61.0452 | 61.0928 | 61.055 | 61.1036 | 123.1292 | 61.5523 | 123.0284 | 61.4034 | 61.4755 | 122.9752 | 61.4396 | 122.7671 | 61.6537 | 61.6896 | 61.5529 | 61.5888
929.5938 | 123.3261 | -61.4182 | 61.7294 | 0.016548 | -0.42514 | -0.40576 | -0.3913 | -0.33455 | -0.38599 | -0.32367 | 61.6928 | 0.12043 | 61.592 | -0.033101 | 0.043657 | 61.5341 | 0.003143 | 61.3215 | 61.4347 | 60.993 | 61.0124 | 61.0269 | 61.0836 | 61.0322 | 61.0945 | 123.1109 | 61.5386 | 123.0101 | 61.3851 | 61.4618 | 122.9523 | 61.4213 | 122.7396 | 61.6491 | 61.6896 | 61.5483 | 61.5888
930.5938 | 123.3124 | -61.441 | 61.7111 | 0.016548 | -0.4343 | -0.4195 | -0.40045 | -0.33913 | -0.38599 | -0.33741 | 61.6836 | 0.11585 | 61.5737 | -0.03768 | 0.043657 | 61.557 | 0.003143 | 61.3398 | 61.4576 | 61.0067 | 61.0215 | 61.0406 | 61.1019 | 61.055 | 61.1036 | 123.1247 | 61.5569 | 123.0147 | 61.4034 | 61.4847 | 122.998 | 61.4442 | 122.7808 | 61.64 | 61.6805 | 61.53 | 61.5705
931.5938 | 123.2758 | -61.4456 | 61.6974 | 0.01197 | -0.44346 | -0.42865 | -0.40045 | -0.35286 | -0.39057 | -0.33741 | 61.6928 | 0.12958 | 61.5828 | -0.03768 | 0.043657 | 61.5524 | 0.007721 | 61.3306 | 61.4576 | 61.0022 | 61.017 | 61.0452 | 61.0928 | 61.055 | 61.1082 | 123.1384 | 61.5752 | 123.0284 | 61.4079 | 61.4893 | 122.998 | 61.4533 | 122.7762 | 61.6491 | 61.685 | 61.5392 | 61.5751
932.5938 | 123.2941 | -61.4319 | 61.702 | 0.01197 | -0.44346 | -0.43323 | -0.40503 | -0.36202 | -0.40888 | -0.34199 | 61.6882 | 0.12501 | 61.5874 | -0.033101 | 0.039079 | 61.5524 | 0.007721 | 61.3352 | 61.4439 | 60.9884 | 60.9987 | 61.0269 | 61.0699 | 61.023 | 61.0899 | 123.1201 | 61.5569 | 123.0193 | 61.3988 | 61.471 | 122.9843 | 61.4396 | 122.7671 | 61.6491 | 61.6805 | 61.5483 | 61.5797
933.5938 | 123.2391 | -61.4227 | 61.7432 | 0.002813 | -0.44346 | -0.43323 | -0.41419 | -0.36202 | -0.40431 | -0.35114 | 61.7065 | 0.12043 | 61.592 | -0.03768 | 0.034501 | 61.5341 | 0.007721 | 61.326 | 61.4255 | 60.9793 | 60.9895 | 61.0085 | 61.0607 | 61.0184 | 61.0716 | 123.1292 | 61.5432 | 123.0147 | 61.385 | 61.4572 | 122.9568 | 61.4304 | 122.7488 | 61.672 | 61.6988 | 61.5575 | 61.5842
934.5938 | 123.2574 | -61.4319 | 61.734 | 0.002813 | -0.45261 | -0.43781 | -0.41419 | -0.36202 | -0.39973 | -0.34656 | 61.7111 | 0.12501 | 61.592 | -0.03768 | 0.048236 | 61.5387 | 0.003143 | 61.326 | 61.4347 | 60.9793 | 60.9941 | 61.0177 | 61.0699 | 61.0322 | 61.0853 | 123.143 | 61.5569 | 123.0239 | 61.3942 | 61.4801 | 122.9706 | 61.435 | 122.7579 | 61.6628 | 61.7079 | 61.5437 | 61.5888
935.5938 | 123.3307 | -61.4273 | 61.7203 | 0.01197 | -0.45261 | -0.44239 | -0.41877 | -0.37117 | -0.41346 | -0.35572 | 61.679 | 0.12501 | 61.5737 | -0.028522 | 0.039079 | 61.5524 | 0.007721 | 61.3443 | 61.4393 | 60.9747 | 60.9849 | 61.0085 | 61.0561 | 61.0138 | 61.0716 | 123.1063 | 61.5523 | 123.001 | 61.3988 | 61.4664 | 122.9797 | 61.435 | 122.7717 | 61.64 | 61.6713 | 61.5346 | 61.5659
936.5938 | 123.3032 | -61.4548 | 61.7249 | 0.007391 | -0.45261 | -0.44239 | -0.41877 | -0.3666 | -0.40888 | -0.35114 | 61.6745 | 0.12501 | 61.5645 | -0.033101 | 0.039079 | 61.5662 | 0.012299 | 61.3489 | 61.4622 | 61.0022 | 61.0124 | 61.036 | 61.0882 | 61.0459 | 61.1036 | 123.1292 | 61.5798 | 123.0193 | 61.4217 | 61.4939 | 123.0209 | 61.4671 | 122.8037 | 61.6354 | 61.6622 | 61.5254 | 61.5522
937.5938 | 123.2941 | -61.4365 | 61.7432 | 0.007391 | -0.45719 | -0.44697 | -0.41419 | -0.3666 | -0.42262 | -0.35572 | 61.6928 | 0.12958 | 61.5874 | -0.033101 | 0.039079 | 61.5433 | 0.007721 | 61.3306 | 61.4439 | 60.9793 | 60.9895 | 61.0223 | 61.0699 | 61.0138 | 61.0807 | 123.1292 | 61.566 | 123.0239 | 61.4034 | 61.4755 | 122.9797 | 61.4442 | 122.7671 | 61.6537 | 61.685 | 61.5483 | 61.5797
938.5938 | 123.2666 | -61.441 | 61.7386 | 0.007391 | -0.46635 | -0.44239 | -0.42792 | -0.37575 | -0.41804 | -0.36488 | 61.6973 | 0.12501 | 61.592 | -0.028522 | 0.043657 | 61.5433 | 0.003143 | 61.3306 | 61.4484 | 60.9747 | 60.9987 | 61.0131 | 61.0653 | 61.023 | 61.0762 | 123.1384 | 61.566 | 123.033 | 61.4125 | 61.4847 | 122.9843 | 61.4442 | 122.7717 | 61.6537 | 61.6942 | 61.5483 | 61.5888
939.5938 | 123.2483 | -61.4502 | 61.702 | 0.01197 | -0.46177 | -0.44697 | -0.41877 | -0.37575 | -0.41804 | -0.3603 | 61.6973 | 0.13416 | 61.592 | -0.033101 | 0.048236 | 61.5433 | -0.001436 | 61.3352 | 61.4622 | 60.9884 | 61.0032 | 61.0314 | 61.0744 | 61.0322 | 61.0899 | 123.1475 | 61.5844 | 123.0422 | 61.4171 | 61.4984 | 122.9935 | 61.4488 | 122.7854 | 61.6491 | 61.6988 | 61.5437 | 61.5934
940.5938 | 123.2986 | -61.4365 | 61.734 | 0.007391 | -0.45261 | -0.44697 | -0.41877 | -0.36202 | -0.41346 | -0.34656 | 61.6882 | 0.12501 | 61.5828 | -0.03768 | 0.039079 | 61.5524 | 0.012299 | 61.3398 | 61.4439 | 60.9838 | 60.9895 | 61.0177 | 61.0744 | 61.023 | 61.0899 | 123.1247 | 61.5615 | 123.0193 | 61.3988 | 61.4755 | 122.9889 | 61.4488 | 122.7762 | 61.6491 | 61.6759 | 61.5437 | 61.5705
941.5938 | 123.2986 | -61.4685 | 61.7065 | 0.01197 | -0.44804 | -0.43323 | -0.40961 | -0.36202 | -0.40431 | -0.35114 | 61.679 | 0.12501 | 61.5599 | -0.033101 | 0.048236 | 61.5616 | 0.007721 | 61.3489 | 61.4805 | 61.0205 | 61.0353 | 61.0589 | 61.1065 | 61.0642 | 61.1174 | 123.1475 | 61.5935 | 123.0284 | 61.4354 | 61.5167 | 123.0301 | 61.4762 | 122.8174 | 61.6308 | 61.6713 | 61.5117 | 61.5522
942.5938 | 123.2849 | -61.4685 | 61.6974 | 0.016548 | -0.46635 | -0.45154 | -0.42335 | -0.38033 | -0.42262 | -0.36945 | 61.6928 | 0.12958 | 61.5782 | -0.033101 | 0.043657 | 61.5478 | 0.007721 | 61.3398 | 61.4851 | 61.0022 | 61.017 | 61.0452 | 61.0882 | 61.0459 | 61.0991 | 123.1613 | 61.5981 | 123.0467 | 61.4354 | 61.5122 | 123.0164 | 61.4762 | 122.8083 | 61.6491 | 61.685 | 61.5346 | 61.5705
943.5938 | 123.2758 | -61.4639 | 61.702 | 0.007391 | -0.47093 | -0.4607 | -0.4325 | -0.38491 | -0.43178 | -0.37403 | 61.6928 | 0.12958 | 61.592 | -0.028522 | 0.048236 | 61.5433 | 0.007721 | 61.326 | 61.4713 | 60.993 | 61.0032 | 61.0314 | 61.079 | 61.0322 | 61.0899 | 123.1567 | 61.5935 | 123.0559 | 61.4354 | 61.5122 | 123.0072 | 61.4716 | 122.79 | 61.6445 | 61.685 | 61.5437 | 61.5842
944.5938 | 123.2529 | -61.4227 | 61.734 | 0.007391 | -0.48009 | -0.4607 | -0.4325 | -0.38491 | -0.43178 | -0.37403 | 61.6973 | 0.12958 | 61.592 | -0.028522 | 0.039079 | 61.5478 | 0.007721 | 61.326 | 61.4301 | 60.9426 | 60.962 | 60.9902 | 61.0378 | 60.991 | 61.0487 | 123.1201 | 61.5523 | 123.0147 | 61.3942 | 61.4618 | 122.9706 | 61.4304 | 122.7488 | 61.6583 | 61.6896 | 61.5529 | 61.5842
945.5938 | 123.2666 | -61.4319 | 61.7386 | 0.007391 | -0.49382 | -0.47902 | -0.45997 | -0.4078 | -0.45925 | -0.38777 | 61.6928 | 0.13416 | 61.5874 | -0.033101 | 0.043657 | 61.5433 | 0.007721 | 61.3352 | 61.4393 | 60.9381 | 60.9529 | 60.9719 | 61.0241 | 60.9726 | 61.0441 | 123.1247 | 61.566 | 123.0193 | 61.3988 | 61.4755 | 122.9752 | 61.4396 | 122.7671 | 61.6491 | 61.685 | 61.5437 | 61.5797
946.5938 | 123.3582 | -61.4227 | 61.6882 | 0.007391 | -0.4984 | -0.4836 | -0.45997 | -0.41237 | -0.45925 | -0.39692 | 61.6882 | 0.12501 | 61.5782 | -0.033101 | 0.039079 | 61.5478 | 0.012299 | 61.3306 | 61.4301 | 60.9243 | 60.9391 | 60.9628 | 61.0104 | 60.9635 | 61.0258 | 123.1109 | 61.5477 | 123.001 | 61.3896 | 61.4618 | 122.9706 | 61.435 | 122.7533 | 61.6491 | 61.6759 | 61.5392 | 61.5659
947.5938 | 123.381 | -61.409 | 61.647 | 0.002813 | -0.50298 | -0.49733 | -0.46913 | -0.41237 | -0.4684 | -0.41524 | 61.7065 | 0.12043 | 61.5965 | -0.03768 | 0.029923 | 61.525 | 0.007721 | 61.3215 | 61.4118 | 60.906 | 60.9117 | 60.9399 | 60.9966 | 60.9406 | 60.9938 | 123.1155 | 61.5294 | 123.0055 | 61.3713 | 61.4389 | 122.934 | 61.4167 | 122.7305 | 61.6766 | 61.6988 | 61.5666 | 61.5888
948.5938 | 123.3948 | -61.409 | 61.6928 | 0.007391 | -0.51214 | -0.50191 | -0.47829 | -0.43069 | -0.4684 | -0.41524 | 61.6973 | 0.12043 | 61.5828 | -0.033101 | 0.048236 | 61.5478 | 0.003143 | 61.3215 | 61.4164 | 60.8969 | 60.9071 | 60.9307 | 60.9783 | 60.9406 | 60.9938 | 123.1063 | 61.5294 | 122.9918 | 61.3759 | 61.4572 | 122.9568 | 61.4121 | 122.7305 | 61.6491 | 61.6942 | 61.5346 | 61.5797
949.5938 | 123.3627 | -61.4273 | 61.6974 | 0.007391 | -0.5213 | -0.50649 | -0.49202 | -0.43069 | -0.47298 | -0.41524 | 61.6928 | 0.13416 | 61.592 | -0.03768 | 0.034501 | 61.5478 | 0.007721 | 61.3352 | 61.4347 | 60.906 | 60.9208 | 60.9353 | 60.9966 | 60.9543 | 61.0121 | 123.1201 | 61.5615 | 123.0193 | 61.3896 | 61.4618 | 122.9752 | 61.435 | 122.7625 | 61.6583 | 61.685 | 61.5575 | 61.5842
950.5938 | 123.3353 | -61.4227 | 61.6837 | 0.007391 | -0.5213 | -0.50649 | -0.48287 | -0.43069 | -0.47756 | -0.41524 | 61.6836 | 0.12043 | 61.5691 | -0.03768 | 0.043657 | 61.557 | 0.007721 | 61.3443 | 61.4301 | 60.9014 | 60.9162 | 60.9399 | 60.992 | 60.9452 | 61.0075 | 123.1063 | 61.5432 | 122.9918 | 61.385 | 61.4664 | 122.9797 | 61.4304 | 122.7671 | 61.64 | 61.6759 | 61.5254 | 61.5614
951.5938 | 123.3765 | -61.4319 | 61.6791 | 0.002813 | -0.52587 | -0.51107 | -0.49202 | -0.44442 | -0.48214 | -0.42897 | 61.6928 | 0.12501 | 61.5965 | -0.033101 | 0.039079 | 61.5478 | 0.007721 | 61.3352 | 61.4347 | 60.906 | 60.9208 | 60.9399 | 60.9875 | 60.9497 | 61.0029 | 123.1247 | 61.5569 | 123.0284 | 61.3988 | 61.471 | 122.9797 | 61.4396 | 122.7671 | 61.6537 | 61.685 | 61.5575 | 61.5888
952.5938 | 123.3627 | -61.3998 | 61.6928 | 0.002813 | -0.53961 | -0.52022 | -0.4966 | -0.449 | -0.49129 | -0.42897 | 61.6882 | 0.12958 | 61.592 | -0.03768 | 0.039079 | 61.5433 | -0.001436 | 61.3306 | 61.4027 | 60.8602 | 60.8796 | 60.9032 | 60.9508 | 60.9085 | 60.9709 | 123.088 | 61.5294 | 122.9918 | 61.3622 | 61.4389 | 122.9431 | 61.3984 | 122.7305 | 61.6491 | 61.6896 | 61.5529 | 61.5934
953.5938 | 123.3902 | -61.4456 | 61.6745 | 0.007391 | -0.54877 | -0.52938 | -0.51034 | -0.45815 | -0.50503 | -0.43813 | 61.6836 | 0.12043 | 61.5691 | -0.03768 | 0.034501 | 61.5524 | 0.003143 | 61.3398 | 61.453 | 60.8968 | 60.9162 | 60.9353 | 60.9875 | 60.9406 | 61.0075 | 123.1292 | 61.566 | 123.0147 | 61.4079 | 61.4801 | 122.998 | 61.4488 | 122.7854 | 61.6491 | 61.6805 | 61.5346 | 61.5659
954.5938 | 123.3582 | -61.441 | 61.6745 | 0.007391 | -0.54877 | -0.53854 | -0.51034 | -0.47189 | -0.50961 | -0.44728 | 61.6973 | 0.12958 | 61.5874 | -0.033101 | 0.039079 | 61.5478 | 0.003143 | 61.326 | 61.4484 | 60.8923 | 60.9025 | 60.9307 | 60.9692 | 60.9314 | 60.9938 | 123.1384 | 61.5706 | 123.0284 | 61.4079 | 61.4801 | 122.9889 | 61.4442 | 122.7671 | 61.6583 | 61.6942 | 61.5483 | 61.5842
955.5938 | 123.4268 | -61.3861 | 61.6837 | -0.006344 | -0.55335 | -0.54312 | -0.52407 | -0.46731 | -0.51876 | -0.45186 | 61.6973 | 0.13416 | 61.5874 | -0.03768 | 0.039079 | 61.5387 | 0.003143 | 61.3306 | 61.3798 | 60.8328 | 60.843 | 60.862 | 60.9188 | 60.8673 | 60.9342 | 123.0835 | 61.5203 | 122.9735 | 61.3484 | 61.4252 | 122.9248 | 61.3893 | 122.7167 | 61.6583 | 61.6942 | 61.5483 | 61.5842
956.5938 | 123.4314 | -61.4227 | 61.6653 | 0.002813 | -0.54419 | -0.5248 | -0.51492 | -0.449 | -0.50045 | -0.43355 | 61.6882 | 0.12043 | 61.5965 | -0.03768 | 0.039079 | 61.5433 | 0.007721 | 61.3352 | 61.4255 | 60.8785 | 60.8979 | 60.9078 | 60.9737 | 60.9223 | 60.9892 | 123.1109 | 61.5432 | 123.0193 | 61.385 | 61.4618 | 122.966 | 61.4304 | 122.7579 | 61.6491 | 61.6805 | 61.5575 | 61.5888
957.5938 | 123.4131 | -61.3861 | 61.702 | -0.001765 | -0.54419 | -0.52938 | -0.50118 | -0.449 | -0.50045 | -0.43813 | 61.7019 | 0.12043 | 61.5965 | -0.033101 | 0.039079 | 61.5341 | -0.001436 | 61.3077 | 61.3843 | 60.8419 | 60.8567 | 60.8849 | 60.9371 | 60.8857 | 60.948 | 123.088 | 61.5065 | 122.9827 | 61.353 | 61.4252 | 122.9202 | 61.3847 | 122.6938 | 61.6628 | 61.7034 | 61.5575 | 61.598
958.5938 | 123.381 | -61.409 | 61.6974 | -0.001765 | -0.55335 | -0.52938 | -0.51492 | -0.45815 | -0.50503 | -0.44271 | 61.6836 | 0.12501 | 61.5828 | -0.03768 | 0.043657 | 61.5433 | 0.007721 | 61.326 | 61.4072 | 60.8556 | 60.8796 | 60.8941 | 60.9508 | 60.904 | 60.9663 | 123.0926 | 61.534 | 122.9918 | 61.3713 | 61.4527 | 122.9523 | 61.4167 | 122.735 | 61.64 | 61.6759 | 61.5392 | 61.5751
959.5938 | 123.349 | -61.4227 | 61.6653 | -0.001765 | -0.56708 | -0.55685 | -0.53781 | -0.48562 | -0.52792 | -0.4656 | 61.6882 | 0.12043 | 61.5874 | -0.033101 | 0.034501 | 61.5524 | 0.012299 | 61.326 | 61.421 | 60.8556 | 60.8659 | 60.8849 | 60.9371 | 60.8948 | 60.9571 | 123.1109 | 61.5432 | 123.0101 | 61.3896 | 61.4572 | 122.9752 | 61.435 | 122.7488 | 61.6537 | 61.6759 | 61.5529 | 61.5751
960.5938 | 123.3398 | -61.4365 | 61.6791 | -0.001765 | -0.59456 | -0.57975 | -0.5607 | -0.50393 | -0.55081 | -0.48849 | 61.7065 | 0.12501 | 61.6057 | -0.033101 | 0.043657 | 61.5295 | 0.003143 | 61.3077 | 61.4347 | 60.8419 | 60.8567 | 60.8758 | 60.9325 | 60.8856 | 60.948 | 123.143 | 61.5615 | 123.0422 | 61.4034 | 61.4801 | 122.966 | 61.4396 | 122.7442 | 61.6628 | 61.7034 | 61.562 | 61.6026
961.5938 | 123.3353 | -61.4319 | 61.6562 | 0.002813 | -0.60372 | -0.59348 | -0.56986 | -0.51767 | -0.56455 | -0.5068 | 61.6973 | 0.12501 | 61.592 | -0.028522 | 0.034501 | 61.5387 | 0.003143 | 61.326 | 61.4347 | 60.8282 | 60.8384 | 60.862 | 60.9142 | 60.8673 | 60.9251 | 123.1292 | 61.5569 | 123.0239 | 61.4034 | 61.4664 | 122.9706 | 61.435 | 122.7579 | 61.6628 | 61.6942 | 61.5575 | 61.5888
962.5938 | 123.381 | -61.3953 | 61.6699 | 0.002813 | -0.61287 | -0.59806 | -0.57444 | -0.52682 | -0.56455 | -0.50222 | 61.7111 | 0.13416 | 61.6011 | -0.03768 | 0.039079 | 61.5295 | 0.007721 | 61.3123 | 61.3981 | 60.7824 | 60.7972 | 60.8208 | 60.8684 | 60.8307 | 60.893 | 123.1063 | 61.5294 | 122.9964 | 61.3576 | 61.4343 | 122.9248 | 61.403 | 122.7076 | 61.672 | 61.7034 | 61.562 | 61.5934
963.5938 | 123.3582 | -61.4044 | 61.6928 | 0.002813 | -0.60372 | -0.5889 | -0.57901 | -0.52682 | -0.55539 | -0.51596 | 61.7157 | 0.12958 | 61.6149 | -0.03768 | 0.039079 | 61.5204 | 0.003143 | 61.294 | 61.4072 | 60.8007 | 60.8155 | 60.8254 | 60.8776 | 60.849 | 60.8885 | 123.1201 | 61.534 | 123.0193 | 61.3667 | 61.4435 | 122.9248 | 61.4076 | 122.6984 | 61.6766 | 61.7125 | 61.5758 | 61.6117
964.5938 | 123.3948 | -61.441 | 61.6379 | -0.001765 | -0.60372 | -0.59348 | -0.57901 | -0.52225 | -0.56455 | -0.50222 | 61.6973 | 0.12501 | 61.5874 | -0.042259 | 0.039079 | 61.5341 | 0.003143 | 61.3215 | 61.4393 | 60.8373 | 60.8476 | 60.862 | 60.9188 | 60.8765 | 60.9388 | 123.1384 | 61.566 | 123.0284 | 61.3988 | 61.4801 | 122.9752 | 61.4442 | 122.7625 | 61.6583 | 61.6942 | 61.5483 | 61.5842
965.5938 | 123.349 | -61.441 | 61.647 | -0.006344 | -0.48924 | -0.47444 | -0.45082 | -0.40322 | -0.44093 | -0.39692 | 61.6882 | 0.12043 | 61.5737 | -0.046838 | 0.034501 | 61.5524 | 0.003143 | 61.3306 | 61.4347 | 60.9518 | 60.9666 | 60.9902 | 61.0378 | 61.0001 | 61.0441 | 123.1292 | 61.5615 | 123.0147 | 61.3942 | 61.4755 | 122.9935 | 61.4442 | 122.7717 | 61.6537 | 61.685 | 61.5392 | 61.5705
966.5938 | 123.3902 | -61.3953 | 61.6608 | -0.001765 | -0.55335 | -0.5477 | -0.51949 | -0.46731 | -0.51876 | -0.44728 | 61.7065 | 0.11585 | 61.6011 | -0.042259 | 0.043657 | 61.5295 | 0.003143 | 61.3123 | 61.3935 | 60.8419 | 60.8476 | 60.8758 | 60.928 | 60.8765 | 60.948 | 123.1018 | 61.5111 | 122.9964 | 61.353 | 61.4389 | 122.9248 | 61.3984 | 122.7076 | 61.6628 | 61.7034 | 61.5575 | 61.598
967.5938 | 123.4085 | -61.3953 | 61.6516 | 0.002813 | -0.61745 | -0.60264 | -0.58359 | -0.52682 | -0.57371 | -0.51138 | 61.7111 | 0.12501 | 61.6149 | -0.042259 | 0.034501 | 61.5204 | -0.001436 | 61.3031 | 61.3981 | 60.7778 | 60.7926 | 60.8117 | 60.8684 | 60.8216 | 60.8839 | 123.1063 | 61.5203 | 123.0101 | 61.353 | 61.4298 | 122.9156 | 61.3938 | 122.6984 | 61.6766 | 61.7125 | 61.5804 | 61.6163
968.5938 | 123.3582 | -61.4319 | 61.6608 | -0.006344 | -0.60372 | -0.59806 | -0.56528 | -0.51309 | -0.55997 | -0.50222 | 61.7157 | 0.12501 | 61.5965 | -0.03768 | 0.034501 | 61.525 | 0.007721 | 61.3169 | 61.4255 | 60.8282 | 60.8338 | 60.8666 | 60.9188 | 60.8719 | 60.9297 | 123.1475 | 61.5569 | 123.0284 | 61.3942 | 61.4664 | 122.9568 | 61.4396 | 122.7488 | 61.6812 | 61.7079 | 61.562 | 61.5888
969.5938 | 123.3856 | -61.409 | 61.6745 | -0.001765 | -0.58082 | -0.57059 | -0.55612 | -0.49478 | -0.53708 | -0.48849 | 61.7111 | 0.12501 | 61.6057 | -0.042259 | 0.034501 | 61.5204 | 0.003143 | 61.3031 | 61.4072 | 60.8282 | 60.8384 | 60.8529 | 60.9142 | 60.8719 | 60.9205 | 123.1201 | 61.534 | 123.0147 | 61.3667 | 61.4435 | 122.9294 | 61.4121 | 122.7121 | 61.6766 | 61.7079 | 61.5712 | 61.6026
970.5938 | 123.381 | -61.4227 | 61.6562 | -0.001765 | -0.57166 | -0.54312 | -0.53781 | -0.47647 | -0.51876 | -0.45644 | 61.7019 | 0.12958 | 61.592 | -0.03768 | 0.034501 | 61.5295 | 0.003143 | 61.3169 | 61.421 | 60.8511 | 60.8796 | 60.8849 | 60.9463 | 60.904 | 60.9663 | 123.1247 | 61.5523 | 123.0147 | 61.385 | 61.4572 | 122.9523 | 61.4259 | 122.7396 | 61.6674 | 61.6988 | 61.5575 | 61.5888
971.5938 | 123.3627 | -61.4182 | 61.6653 | 0.002813 | -0.55793 | -0.53396 | -0.51949 | -0.46731 | -0.50503 | -0.45186 | 61.6928 | 0.12501 | 61.5874 | -0.03768 | 0.034501 | 61.5387 | 0.003143 | 61.3215 | 61.421 | 60.8602 | 60.8842 | 60.8987 | 60.9508 | 60.9131 | 60.9663 | 123.1109 | 61.5432 | 123.0055 | 61.3805 | 61.4527 | 122.9568 | 61.4213 | 122.7396 | 61.6583 | 61.6896 | 61.5529 | 61.5842
972.5938 | 123.2483 | -61.4594 | 61.6974 | -0.001765 | -0.56251 | -0.5477 | -0.52407 | -0.47189 | -0.51876 | -0.45644 | 61.6836 | 0.12958 | 61.5737 | -0.033101 | 0.039079 | 61.5478 | 0.007721 | 61.3443 | 61.4576 | 60.8968 | 60.9117 | 60.9353 | 60.9875 | 60.9406 | 61.0029 | 123.143 | 61.5889 | 123.033 | 61.4262 | 61.4984 | 123.0072 | 61.4671 | 122.8037 | 61.6445 | 61.6759 | 61.5346 | 61.5659
973.5938 | 123.3307 | -61.4227 | 61.7065 | -0.001765 | -0.56251 | -0.53854 | -0.52407 | -0.47647 | -0.51876 | -0.45186 | 61.7157 | 0.12043 | 61.6057 | -0.03768 | 0.043657 | 61.5204 | -0.001436 | 61.3031 | 61.421 | 60.8602 | 60.8842 | 60.8987 | 60.9463 | 60.904 | 60.9709 | 123.1384 | 61.5432 | 123.0284 | 61.385 | 61.4664 | 122.9431 | 61.4213 | 122.7259 | 61.672 | 61.7171 | 61.562 | 61.6071
974.5938 | 123.2758 | -61.4502 | 61.7111 | -0.001765 | -0.55335 | -0.5477 | -0.52407 | -0.47647 | -0.51876 | -0.45644 | 61.7111 | 0.12501 | 61.6011 | -0.042259 | 0.034501 | 61.5295 | 0.007721 | 61.3123 | 61.4484 | 60.8968 | 60.9025 | 60.9261 | 60.9737 | 60.9314 | 60.9938 | 123.1613 | 61.5752 | 123.0513 | 61.4079 | 61.4847 | 122.9797 | 61.4579 | 122.7625 | 61.6766 | 61.7034 | 61.5666 | 61.5934
975.5938 | 123.2574 | -61.4868 | 61.702 | -0.001765 | -0.56251 | -0.5477 | -0.51949 | -0.46273 | -0.51419 | -0.44728 | 61.6928 | 0.13416 | 61.5828 | -0.028522 | 0.034501 | 61.5433 | 0.007721 | 61.3306 | 61.4851 | 60.9243 | 60.9391 | 60.9673 | 61.0241 | 60.9726 | 61.0395 | 123.1796 | 61.621 | 123.0696 | 61.4583 | 61.5213 | 123.0301 | 61.4945 | 122.8174 | 61.6583 | 61.685 | 61.5483 | 61.5751
976.5938 | 123.2162 | -61.4777 | 61.6837 | 0.002813 | -0.54419 | -0.53854 | -0.51034 | -0.46273 | -0.50503 | -0.45186 | 61.7111 | 0.12501 | 61.6011 | -0.028522 | 0.039079 | 61.5295 | 0.003143 | 61.3169 | 61.4805 | 60.9335 | 60.9391 | 60.9673 | 61.0149 | 60.9726 | 61.0258 | 123.1887 | 61.6027 | 123.0788 | 61.4491 | 61.5167 | 123.0072 | 61.4808 | 122.7945 | 61.672 | 61.7079 | 61.562 | 61.598
977.5938 | 123.3398 | -61.4227 | 61.6653 | 0.002813 | -0.53503 | -0.51565 | -0.50118 | -0.45815 | -0.49587 | -0.43355 | 61.6973 | 0.12958 | 61.5828 | -0.042259 | 0.039079 | 61.5341 | 0.007721 | 61.3169 | 61.4255 | 60.8877 | 60.9071 | 60.9215 | 60.9646 | 60.9269 | 60.9892 | 123.1201 | 61.5523 | 123.0055 | 61.3805 | 61.4618 | 122.9568 | 61.4304 | 122.7396 | 61.6583 | 61.6896 | 61.5437 | 61.5751
978.5938 | 123.2254 | -61.4639 | 61.6928 | 0.007391 | -0.52587 | -0.51107 | -0.48745 | -0.43984 | -0.48214 | -0.42439 | 61.6882 | 0.12501 | 61.5782 | -0.033101 | 0.034501 | 61.5524 | 0.003143 | 61.3306 | 61.4713 | 60.9381 | 60.9529 | 60.9765 | 61.0241 | 60.9818 | 61.0395 | 123.1521 | 61.5889 | 123.0422 | 61.4308 | 61.4984 | 123.0164 | 61.4671 | 122.7945 | 61.6537 | 61.685 | 61.5437 | 61.5751
979.5938 | 123.2803 | -61.4594 | 61.7065 | 0.01197 | -0.5213 | -0.50649 | -0.48287 | -0.43069 | -0.47298 | -0.41981 | 61.7202 | 0.12501 | 61.6011 | -0.033101 | 0.039079 | 61.525 | 0.007721 | 61.3123 | 61.4713 | 60.9381 | 60.9529 | 60.9765 | 61.0287 | 60.9864 | 61.0395 | 123.1796 | 61.5844 | 123.0605 | 61.4262 | 61.4984 | 122.9843 | 61.4671 | 122.7717 | 61.6812 | 61.7125 | 61.562 | 61.5934
980.5938 | 123.2437 | -61.4548 | 61.6928 | -0.001765 | -0.50298 | -0.49275 | -0.46455 | -0.41695 | -0.46382 | -0.4015 | 61.7065 | 0.12043 | 61.5965 | -0.028522 | 0.039079 | 61.5341 | 0.007721 | 61.3215 | 61.453 | 60.9518 | 60.962 | 60.9902 | 61.0378 | 60.9909 | 61.0533 | 123.1613 | 61.5752 | 123.0513 | 61.4263 | 61.4939 | 122.9889 | 61.4625 | 122.7762 | 61.6674 | 61.6988 | 61.5575 | 61.5888
981.5938 | 123.3307 | -61.3953 | 61.7249 | 0.002813 | -0.46635 | -0.45612 | -0.4325 | -0.38033 | -0.42262 | -0.3603 | 61.7157 | 0.13416 | 61.6149 | -0.03768 | 0.039079 | 61.5158 | 0.003143 | 61.3077 | 61.3981 | 60.9289 | 60.9391 | 60.9628 | 61.0149 | 60.9726 | 61.035 | 123.1109 | 61.5294 | 123.0101 | 61.3576 | 61.4343 | 122.9111 | 61.3984 | 122.703 | 61.6766 | 61.7125 | 61.5758 | 61.6117
982.5938 | 123.4085 | -61.441 | 61.6791 | 0.002813 | -0.44804 | -0.43323 | -0.41419 | -0.35744 | -0.40888 | -0.35114 | 61.6928 | 0.14332 | 61.592 | -0.03768 | 0.048236 | 61.5433 | 0.007721 | 61.3306 | 61.4439 | 60.993 | 61.0078 | 61.0269 | 61.0836 | 61.0322 | 61.0899 | 123.1338 | 61.5844 | 123.033 | 61.4034 | 61.4893 | 122.9843 | 61.4488 | 122.7717 | 61.6445 | 61.685 | 61.5437 | 61.5842
983.5938 | 123.2574 | -61.4685 | 61.6653 | -0.001765 | -0.45261 | -0.43781 | -0.41877 | -0.3666 | -0.40888 | -0.3603 | 61.6973 | 0.13416 | 61.592 | -0.03768 | 0.039079 | 61.5478 | 0.007721 | 61.3215 | 61.4667 | 61.0159 | 61.0307 | 61.0497 | 61.1019 | 61.0596 | 61.1082 | 123.1659 | 61.6027 | 123.0605 | 61.4308 | 61.5076 | 123.0164 | 61.4762 | 122.79 | 61.6583 | 61.6896 | 61.5529 | 61.5842
984.5938 | 123.2758 | -61.4639 | 61.6974 | 0.002813 | -0.44804 | -0.43781 | -0.40961 | -0.3666 | -0.40431 | -0.35114 | 61.6973 | 0.11585 | 61.5828 | -0.033101 | 0.034501 | 61.5433 | 0.003143 | 61.326 | 61.4667 | 61.0159 | 61.0261 | 61.0543 | 61.0973 | 61.0596 | 61.1128 | 123.1613 | 61.5798 | 123.0467 | 61.4308 | 61.4984 | 123.0072 | 61.4671 | 122.79 | 61.6628 | 61.6942 | 61.5483 | 61.5797
985.5938 | 123.2849 | -61.4365 | 61.6837 | 0.01197 | -0.45261 | -0.45154 | -0.41419 | -0.37117 | -0.41346 | -0.35572 | 61.679 | 0.12958 | 61.5645 | -0.03768 | 0.043657 | 61.557 | 0.003143 | 61.3398 | 61.4484 | 60.9838 | 60.9849 | 61.0223 | 61.0653 | 61.023 | 61.0807 | 123.1155 | 61.566 | 123.001 | 61.3988 | 61.4801 | 122.9935 | 61.4396 | 122.7762 | 61.6354 | 61.6759 | 61.5208 | 61.5614
986.5938 | 123.262 | -61.441 | 61.6791 | 0.01197 | -0.45719 | -0.43781 | -0.40961 | -0.3666 | -0.40431 | -0.34656 | 61.6836 | 0.12501 | 61.5737 | -0.033101 | 0.043657 | 61.557 | 0.007721 | 61.3443 | 61.453 | 60.9838 | 61.0032 | 61.0314 | 61.0744 | 61.0367 | 61.0945 | 123.1247 | 61.566 | 123.0147 | 61.4079 | 61.4847 | 122.998 | 61.4488 | 122.7854 | 61.64 | 61.6759 | 61.53 | 61.5659
987.5938 | 123.4268 | -61.4227 | 61.6608 | 0.002813 | -0.43888 | -0.43781 | -0.40503 | -0.35286 | -0.39973 | -0.33741 | 61.7065 | 0.12958 | 61.592 | -0.033101 | 0.034501 | 61.5387 | 0.003143 | 61.3123 | 61.4255 | 60.9839 | 60.9849 | 61.0177 | 61.0699 | 61.023 | 61.0853 | 123.1292 | 61.5523 | 123.0147 | 61.3896 | 61.4572 | 122.9614 | 61.4259 | 122.735 | 61.672 | 61.7034 | 61.5575 | 61.5888
988.5938 | 123.3124 | -61.3632 | 61.7844 | 0.01197 | -0.43888 | -0.41492 | -0.40045 | -0.34828 | -0.39515 | -0.33741 | 61.7614 | 0.12958 | 61.6606 | -0.03768 | 0.029923 | 61.4838 | 0.003143 | 61.2619 | 61.3752 | 60.9243 | 60.9483 | 60.9628 | 61.0149 | 60.9681 | 61.0258 | 123.1247 | 61.4928 | 123.0239 | 61.3255 | 61.3931 | 122.847 | 61.3664 | 122.6252 | 61.7315 | 61.7583 | 61.6307 | 61.6575
989.5938 | 123.3215 | -61.4044 | 61.7386 | 0.002813 | -0.4343 | -0.42407 | -0.40045 | -0.35286 | -0.39515 | -0.33741 | 61.7157 | 0.12958 | 61.6057 | -0.033101 | 0.029923 | 61.5295 | 0.003143 | 61.3169 | 61.4072 | 60.9701 | 60.9803 | 61.004 | 61.0516 | 61.0093 | 61.067 | 123.1201 | 61.534 | 123.0101 | 61.3713 | 61.4343 | 122.934 | 61.4076 | 122.7213 | 61.6857 | 61.7125 | 61.5758 | 61.6026
990.5938 | 123.2986 | -61.3953 | 61.7432 | 0.002813 | -0.43888 | -0.42865 | -0.40503 | -0.35744 | -0.39973 | -0.33741 | 61.7111 | 0.12958 | 61.6057 | -0.033101 | 0.039079 | 61.5204 | 0.003143 | 61.326 | 61.3981 | 60.9564 | 60.9666 | 60.9902 | 61.0378 | 60.9955 | 61.0579 | 123.1063 | 61.5248 | 123.001 | 61.3622 | 61.4343 | 122.9156 | 61.3984 | 122.7213 | 61.672 | 61.7079 | 61.5666 | 61.6026
991.5938 | 123.3032 | -61.3907 | 61.7798 | 0.002813 | -0.43888 | -0.42407 | -0.40961 | -0.35286 | -0.39973 | -0.33283 | 61.7523 | 0.13416 | 61.6515 | -0.033101 | 0.039079 | 61.4792 | 0.007721 | 61.2619 | 61.3935 | 60.9518 | 60.9666 | 60.9811 | 61.0378 | 60.991 | 61.0579 | 123.143 | 61.5248 | 123.0422 | 61.3576 | 61.4298 | 122.8699 | 61.3984 | 122.6526 | 61.7132 | 61.7446 | 61.6124 | 61.6438
992.5938 | 123.2986 | -61.4227 | 61.7432 | 0.01197 | -0.4343 | -0.42865 | -0.39587 | -0.35286 | -0.39515 | -0.33741 | 61.7111 | 0.12958 | 61.6057 | -0.042259 | 0.052814 | 61.5295 | 0.003143 | 61.3169 | 61.4347 | 60.9884 | 60.9941 | 61.0269 | 61.0699 | 61.0276 | 61.0853 | 123.1338 | 61.5523 | 123.0284 | 61.3805 | 61.4755 | 122.9523 | 61.4259 | 122.7396 | 61.6583 | 61.7079 | 61.5529 | 61.6026
993.5938 | 123.2941 | -61.4044 | 61.7249 | 0.002813 | -0.45719 | -0.44697 | -0.42335 | -0.38033 | -0.41804 | -0.3603 | 61.7111 | 0.12958 | 61.6103 | -0.03768 | 0.043657 | 61.5158 | 0.003143 | 61.3077 | 61.4072 | 60.9472 | 60.9575 | 60.9811 | 61.0241 | 60.9864 | 61.0441 | 123.1155 | 61.534 | 123.0147 | 61.3667 | 61.4481 | 122.9202 | 61.4076 | 122.7121 | 61.6674 | 61.7079 | 61.5666 | 61.6071
994.5938 | 123.2941 | -61.4044 | 61.7065 | 0.002813 | -0.49382 | -0.47444 | -0.45539 | -0.40322 | -0.45467 | -0.38777 | 61.6973 | 0.12501 | 61.592 | -0.028522 | 0.034501 | 61.5387 | 0.007721 | 61.326 | 61.4072 | 60.9106 | 60.93 | 60.949 | 61.0012 | 60.9498 | 61.0167 | 123.1018 | 61.5294 | 122.9964 | 61.3759 | 61.4389 | 122.9431 | 61.4121 | 122.7305 | 61.6628 | 61.6896 | 61.5575 | 61.5842
995.5938 | 123.2986 | -61.4227 | 61.7203 | -0.001765 | -0.4984 | -0.47902 | -0.45997 | -0.4078 | -0.45467 | -0.39692 | 61.6928 | 0.12501 | 61.592 | -0.028522 | 0.039079 | 61.5433 | -0.001436 | 61.3306 | 61.421 | 60.9243 | 60.9437 | 60.9628 | 61.0149 | 60.9681 | 61.0258 | 123.1155 | 61.5477 | 123.0147 | 61.3942 | 61.4618 | 122.966 | 61.4213 | 122.7533 | 61.6537 | 61.6942 | 61.5529 | 61.5934
996.5938 | 123.2895 | -61.4365 | 61.7157 | -0.006344 | -0.51672 | -0.50649 | -0.48287 | -0.43984 | -0.48214 | -0.41981 | 61.7202 | 0.12958 | 61.6057 | -0.033101 | 0.043657 | 61.5204 | 0.007721 | 61.3031 | 61.4301 | 60.9197 | 60.93 | 60.9536 | 60.9966 | 60.9543 | 61.0166 | 123.1567 | 61.566 | 123.0422 | 61.4034 | 61.4801 | 122.9568 | 61.4442 | 122.7396 | 61.6766 | 61.7125 | 61.562 | 61.598
997.5938 | 123.3124 | -61.4227 | 61.7249 | -0.006344 | -0.53503 | -0.52938 | -0.50118 | -0.45358 | -0.49587 | -0.43813 | 61.7111 | 0.12043 | 61.6011 | -0.033101 | 0.043657 | 61.525 | 0.003143 | 61.3123 | 61.4164 | 60.8877 | 60.8933 | 60.9215 | 60.9692 | 60.9269 | 60.9846 | 123.1338 | 61.5432 | 123.0239 | 61.3896 | 61.4664 | 122.9477 | 61.4259 | 122.735 | 61.6674 | 61.7079 | 61.5575 | 61.598
998.5938 | 123.3215 | -61.4319 | 61.7065 | -0.006344 | -0.53503 | -0.5248 | -0.50118 | -0.449 | -0.49587 | -0.42439 | 61.7157 | 0.12958 | 61.6194 | -0.03768 | 0.043657 | 61.5112 | -0.001436 | 61.3077 | 61.4255 | 60.8969 | 60.9071 | 60.9307 | 60.9829 | 60.936 | 61.0075 | 123.1475 | 61.5615 | 123.0513 | 61.3942 | 61.4755 | 122.9431 | 61.4304 | 122.7396 | 61.672 | 61.7171 | 61.5758 | 61.6209
999.5938 | 123.3261 | -61.3998 | 61.734 | -0.006344 | -0.55793 | -0.53854 | -0.51492 | -0.47189 | -0.50503 | -0.45186 | 61.7386 | 0.13416 | 61.6194 | -0.033101 | 0.048236 | 61.4975 | 0.003143 | 61.294 | 61.3935 | 60.8419 | 60.8613 | 60.8849 | 60.928 | 60.8948 | 60.948 | 123.1384 | 61.534 | 123.0193 | 61.3667 | 61.4481 | 122.8973 | 61.403 | 122.6938 | 61.6903 | 61.7354 | 61.5712 | 61.6163
1000.5938 | 123.2986 | -61.4273 | 61.7111 | -0.006344 | -0.52587 | -0.50649 | -0.48745 | -0.43069 | -0.47298 | -0.41981 | 61.7202 | 0.12501 | 61.6103 | -0.033101 | 0.034501 | 61.5158 | 0.007721 | 61.3077 | 61.421 | 60.9014 | 60.9208 | 60.9399 | 60.9966 | 60.9543 | 61.0075 | 123.1475 | 61.5523 | 123.0376 | 61.3942 | 61.4618 | 122.9431 | 61.435 | 122.735 | 61.6857 | 61.7125 | 61.5758 | 61.6026
1001.5938 | 123.3078 | -61.4227 | 61.7065 | -0.006344 | -0.50298 | -0.4836 | -0.46913 | -0.43069 | -0.4684 | -0.4015 | 61.7065 | 0.12501 | 61.5965 | -0.03768 | 0.039079 | 61.5341 | 0.007721 | 61.3215 | 61.4164 | 60.9197 | 60.9391 | 60.9536 | 60.992 | 60.9543 | 61.0212 | 123.1292 | 61.5477 | 123.0193 | 61.385 | 61.4618 | 122.9568 | 61.4304 | 122.7442 | 61.6674 | 61.6988 | 61.5575 | 61.5888
1002.5938 | 123.262 | -61.4182 | 61.7661 | -0.010922 | -0.48467 | -0.47444 | -0.45539 | -0.40322 | -0.44551 | -0.38319 | 61.7202 | 0.12958 | 61.6057 | -0.042259 | 0.034501 | 61.5204 | 0.003143 | 61.3077 | 61.4072 | 60.9335 | 60.9437 | 60.9628 | 61.0149 | 60.9726 | 61.035 | 123.1384 | 61.5477 | 123.0239 | 61.3759 | 61.4527 | 122.9385 | 61.4213 | 122.7259 | 61.6857 | 61.7171 | 61.5712 | 61.6026
1003.5938 | 123.2483 | -61.4182 | 61.7203 | -0.006344 | -0.4984 | -0.47902 | -0.45082 | -0.40322 | -0.45009 | -0.38777 | 61.7111 | 0.12958 | 61.592 | -0.033101 | 0.039079 | 61.5295 | 0.012299 | 61.326 | 61.4118 | 60.9198 | 60.9391 | 60.9673 | 61.0149 | 60.9681 | 61.0304 | 123.1292 | 61.5477 | 123.0101 | 61.3851 | 61.4572 | 122.9477 | 61.4305 | 122.7442 | 61.672 | 61.6988 | 61.5529 | 61.5797
1004.5938 | 123.2941 | -61.4182 | 61.7386 | -0.001765 | -0.49382 | -0.4836 | -0.46455 | -0.4078 | -0.45925 | -0.39692 | 61.7386 | 0.12043 | 61.6286 | -0.028522 | 0.039079 | 61.5066 | 0.003143 | 61.3031 | 61.4164 | 60.9243 | 60.9346 | 60.9536 | 61.0104 | 60.9589 | 61.0212 | 123.1567 | 61.5386 | 123.0467 | 61.3896 | 61.4572 | 122.9248 | 61.4213 | 122.7213 | 61.6995 | 61.7354 | 61.5895 | 61.6255
1005.5938 | 123.317 | -61.409 | 61.7523 | -0.006344 | -0.53961 | -0.51565 | -0.4966 | -0.45358 | -0.48672 | -0.42897 | 61.7294 | 0.14332 | 61.6332 | -0.03768 | 0.034501 | 61.5066 | 0.007721 | 61.3031 | 61.4027 | 60.8694 | 60.8934 | 60.9124 | 60.9554 | 60.9223 | 60.98 | 123.1384 | 61.5523 | 123.0422 | 61.3713 | 61.4435 | 122.9156 | 61.4167 | 122.7121 | 61.6949 | 61.7217 | 61.5987 | 61.6255
1006.5938 | 123.2895 | -61.3724 | 61.7752 | -0.006344 | -0.55335 | -0.53854 | -0.51034 | -0.46273 | -0.50503 | -0.44271 | 61.7431 | 0.12501 | 61.6377 | -0.033101 | 0.039079 | 61.4838 | 0.003143 | 61.294 | 61.366 | 60.819 | 60.8338 | 60.862 | 60.9096 | 60.8673 | 60.9297 | 123.1155 | 61.4974 | 123.0101 | 61.3393 | 61.4115 | 122.8561 | 61.3755 | 122.6664 | 61.7041 | 61.74 | 61.5987 | 61.6346
1007.5938 | 123.2712 | -61.4227 | 61.7798 | -0.006344 | -0.55793 | -0.53854 | -0.51492 | -0.47189 | -0.52334 | -0.45186 | 61.7202 | 0.12043 | 61.6103 | -0.033101 | 0.039079 | 61.5158 | -0.006014 | 61.3215 | 61.4164 | 60.8648 | 60.8842 | 60.9078 | 60.9508 | 60.8994 | 60.9709 | 123.143 | 61.5432 | 123.033 | 61.3896 | 61.4618 | 122.9385 | 61.4167 | 122.7442 | 61.6812 | 61.7263 | 61.5712 | 61.6163
1008.5938 | 123.2483 | -61.4502 | 61.7203 | -0.001765 | -0.54877 | -0.5248 | -0.51034 | -0.45358 | -0.49587 | -0.44728 | 61.7111 | 0.12958 | 61.6011 | -0.03768 | 0.048236 | 61.5295 | -0.001436 | 61.326 | 61.4484 | 60.9014 | 60.9254 | 60.9399 | 60.9966 | 60.9543 | 61.0029 | 123.1613 | 61.5798 | 123.0513 | 61.4125 | 61.4984 | 122.9797 | 61.4488 | 122.7762 | 61.6628 | 61.7125 | 61.5529 | 61.6026
1009.5938 | 123.2574 | -61.4136 | 61.7294 | -0.010922 | -0.56251 | -0.54312 | -0.51949 | -0.47647 | -0.51876 | -0.45644 | 61.7111 | 0.12043 | 61.5965 | -0.042259 | 0.039079 | 61.5295 | 0.003143 | 61.3306 | 61.4027 | 60.8511 | 60.8705 | 60.8941 | 60.9371 | 60.8948 | 60.9571 | 123.1247 | 61.534 | 123.0101 | 61.3713 | 61.4527 | 122.9431 | 61.4167 | 122.7442 | 61.672 | 61.7079 | 61.5575 | 61.5934
1010.5938 | 123.3124 | -61.3678 | 61.7615 | -0.010922 | -0.55793 | -0.54312 | -0.51949 | -0.47647 | -0.51876 | -0.45644 | 61.7294 | 0.12043 | 61.624 | -0.03768 | 0.043657 | 61.5112 | -0.001436 | 61.3123 | 61.3569 | 60.8099 | 60.8247 | 60.8483 | 60.8913 | 60.849 | 60.9114 | 123.0972 | 61.4882 | 122.9918 | 61.3301 | 61.4115 | 122.879 | 61.3664 | 122.6801 | 61.6857 | 61.7308 | 61.5804 | 61.6255
1011.5938 | 123.2666 | -61.3815 | 61.7706 | -0.015501 | -0.57166 | -0.55685 | -0.52865 | -0.48105 | -0.52792 | -0.4656 | 61.7386 | 0.13416 | 61.624 | -0.042259 | 0.043657 | 61.5021 | 0.003143 | 61.3077 | 61.366 | 60.8099 | 60.8247 | 60.8529 | 60.9005 | 60.8536 | 60.9159 | 123.1201 | 61.5157 | 123.0055 | 61.3393 | 61.4252 | 122.8836 | 61.3847 | 122.6893 | 61.6949 | 61.7354 | 61.5804 | 61.6209
1012.5938 | 123.2529 | -61.4273 | 61.7935 | -0.015501 | -0.58998 | -0.57517 | -0.54697 | -0.49936 | -0.54624 | -0.48849 | 61.7065 | 0.13416 | 61.6149 | -0.042259 | 0.043657 | 61.5204 | 0.007721 | 61.3352 | 61.4118 | 60.8373 | 60.8521 | 60.8803 | 60.928 | 60.8811 | 60.9388 | 123.1338 | 61.5615 | 123.0422 | 61.385 | 61.471 | 122.9477 | 61.435 | 122.7625 | 61.6628 | 61.6988 | 61.5712 | 61.6071
1013.5938 | 123.23 | -61.4044 | 61.7615 | -0.015501 | -0.65866 | -0.64385 | -0.60649 | -0.56803 | -0.60575 | -0.548 | 61.734 | 0.13416 | 61.6286 | -0.03768 | 0.039079 | 61.5112 | -0.001436 | 61.3123 | 61.3889 | 60.7458 | 60.7606 | 60.7979 | 60.8364 | 60.7987 | 60.8564 | 123.1384 | 61.5386 | 123.033 | 61.3667 | 61.4435 | 122.9156 | 61.403 | 122.7167 | 61.6949 | 61.7354 | 61.5895 | 61.63
1014.5938 | 123.2574 | -61.3632 | 61.7889 | -0.015501 | -0.70445 | -0.68963 | -0.66601 | -0.61381 | -0.65612 | -0.59836 | 61.7523 | 0.13416 | 61.6423 | -0.03768 | 0.039079 | 61.4838 | 0.007721 | 61.2848 | 61.3477 | 60.6588 | 60.6736 | 60.6972 | 60.7494 | 60.7071 | 60.7649 | 123.1155 | 61.4974 | 123.0055 | 61.3255 | 61.4023 | 122.847 | 61.3709 | 122.6481 | 61.7132 | 61.7446 | 61.6032 | 61.6346
1015.5938 | 123.3032 | -61.3495 | 61.8118 | -0.024657 | -0.70903 | -0.70337 | -0.67058 | -0.61381 | -0.66069 | -0.60294 | 61.7569 | 0.12043 | 61.6423 | -0.03768 | 0.043657 | 61.4883 | 0.003143 | 61.2848 | 61.3248 | 60.6405 | 60.6461 | 60.6789 | 60.7357 | 60.6888 | 60.7465 | 123.1064 | 61.4699 | 122.9918 | 61.3118 | 61.3931 | 122.8378 | 61.3526 | 122.6343 | 61.7132 | 61.7537 | 61.5987 | 61.6392
1016.5938 | 123.381 | -61.3678 | 61.702 | -0.029236 | -0.70903 | -0.70337 | -0.67974 | -0.61838 | -0.66527 | -0.59836 | 61.734 | 0.14332 | 61.624 | -0.03768 | 0.043657 | 61.5021 | 0.007721 | 61.2894 | 61.3386 | 60.6588 | 60.6644 | 60.6881 | 60.7494 | 60.7025 | 60.7694 | 123.1018 | 61.5111 | 122.9918 | 61.3301 | 61.4115 | 122.8699 | 61.3755 | 122.6572 | 61.6903 | 61.7263 | 61.5804 | 61.6163
1017.5938 | 123.4085 | -61.3586 | 61.7111 | -0.020079 | -0.72276 | -0.70795 | -0.6889 | -0.62296 | -0.67901 | -0.61668 | 61.7202 | 0.12958 | 61.6149 | -0.03768 | 0.039079 | 61.5112 | 0.003143 | 61.3031 | 61.3386 | 60.6359 | 60.6507 | 60.6697 | 60.7357 | 60.6796 | 60.742 | 123.0789 | 61.4882 | 122.9735 | 61.321 | 61.3977 | 122.8699 | 61.3618 | 122.6618 | 61.6812 | 61.7171 | 61.5758 | 61.6117
1018.5938 | 123.3444 | -61.3724 | 61.7294 | -0.029236 | -0.7365 | -0.72168 | -0.70263 | -0.64585 | -0.69274 | -0.63499 | 61.7202 | 0.13416 | 61.624 | -0.03768 | 0.039079 | 61.5112 | 0.003143 | 61.3031 | 61.3431 | 60.6359 | 60.6507 | 60.6697 | 60.7265 | 60.6796 | 60.7374 | 123.0926 | 61.5065 | 122.9964 | 61.3347 | 61.4115 | 122.8836 | 61.3755 | 122.6755 | 61.6812 | 61.7171 | 61.5849 | 61.6209
1019.5938 | 123.349 | -61.3815 | 61.7157 | -0.029236 | -0.7365 | -0.72626 | -0.70263 | -0.64585 | -0.69274 | -0.63041 | 61.7065 | 0.12501 | 61.592 | -0.03768 | 0.039079 | 61.525 | 0.012299 | 61.3169 | 61.3523 | 60.645 | 60.6553 | 60.6789 | 60.7357 | 60.6888 | 60.7511 | 123.088 | 61.5065 | 122.9735 | 61.3439 | 61.4206 | 122.9065 | 61.3938 | 122.6984 | 61.6674 | 61.6942 | 61.5529 | 61.5797
1020.5938 | 123.3582 | -61.3815 | 61.7386 | -0.038393 | -0.72276 | -0.7171 | -0.6889 | -0.63212 | -0.68359 | -0.62125 | 61.7386 | 0.12501 | 61.6286 | -0.03768 | 0.034501 | 61.4929 | -0.001436 | 61.2803 | 61.3431 | 60.6588 | 60.6644 | 60.6926 | 60.7494 | 60.6979 | 60.7603 | 123.1201 | 61.5065 | 123.0101 | 61.3439 | 61.416 | 122.8744 | 61.3801 | 122.6618 | 61.7041 | 61.74 | 61.5941 | 61.63
1021.5938 | 123.3536 | -61.3541 | 61.7157 | -0.029236 | -0.74566 | -0.73084 | -0.71179 | -0.65043 | -0.69732 | -0.63499 | 61.7477 | 0.13874 | 61.6469 | -0.03768 | 0.029923 | 61.4838 | 0.003143 | 61.2665 | 61.3248 | 60.6084 | 60.6232 | 60.6423 | 60.7036 | 60.6567 | 60.7191 | 123.1018 | 61.4928 | 123.001 | 61.3164 | 61.384 | 122.8378 | 61.3572 | 122.6206 | 61.7178 | 61.7446 | 61.617 | 61.6438
1022.5938 | 123.4039 | -61.3312 | 61.7752 | -0.038393 | -0.77313 | -0.76747 | -0.73926 | -0.68705 | -0.72937 | -0.66704 | 61.7431 | 0.12501 | 61.6332 | -0.033101 | 0.039079 | 61.4883 | 0.007721 | 61.2711 | 61.2928 | 60.558 | 60.5637 | 60.5919 | 60.6441 | 60.6018 | 60.6641 | 123.0743 | 61.4562 | 122.9643 | 61.2981 | 61.3703 | 122.8195 | 61.3389 | 122.6023 | 61.7041 | 61.7354 | 61.5941 | 61.6255
1023.5938 | 123.3582 | -61.3678 | 61.7203 | -0.047549 | -0.80976 | -0.79494 | -0.76673 | -0.71452 | -0.75226 | -0.69451 | 61.7569 | 0.13416 | 61.6515 | -0.03768 | 0.039079 | 61.4838 | 0.007721 | 61.2619 | 61.3202 | 60.558 | 60.5729 | 60.6011 | 60.6533 | 60.6155 | 60.6733 | 123.1247 | 61.502 | 123.0193 | 61.3301 | 61.4069 | 122.8516 | 61.3755 | 122.6297 | 61.7178 | 61.7491 | 61.6124 | 61.6438
1024.5938 | 123.3673 | -61.3678 | 61.7523 | -0.047549 | -0.86471 | -0.85446 | -0.83083 | -0.77861 | -0.81178 | -0.7586 | 61.7614 | 0.12958 | 61.6515 | -0.033101 | 0.039079 | 61.4792 | -0.001436 | 61.2574 | 61.3202 | 60.5031 | 60.5133 | 60.537 | 60.5892 | 60.556 | 60.6092 | 123.1292 | 61.4974 | 123.0193 | 61.3347 | 61.4069 | 122.847 | 61.3664 | 122.6252 | 61.7224 | 61.7629 | 61.6124 | 61.6529
1025.5938 | 123.4222 | -61.3266 | 61.7523 | -0.033814 | -0.8876 | -0.8682 | -0.84915 | -0.78777 | -0.84383 | -0.77233 | 61.7706 | 0.12501 | 61.6606 | -0.033101 | 0.039079 | 61.47 | 0.003143 | 61.2482 | 61.2928 | 60.439 | 60.4584 | 60.4775 | 60.5388 | 60.4828 | 60.5543 | 123.0972 | 61.4516 | 122.9872 | 61.2935 | 61.3657 | 122.7966 | 61.3297 | 122.5748 | 61.7315 | 61.7675 | 61.6216 | 61.6575
1026.5938 | 123.4085 | -61.2991 | 61.7661 | -0.042971 | -0.9105 | -0.90483 | -0.87662 | -0.81524 | -0.86672 | -0.80896 | 61.7981 | 0.12501 | 61.679 | -0.03768 | 0.034501 | 61.4288 | 0.003143 | 61.2207 | 61.2562 | 60.3886 | 60.3943 | 60.4225 | 60.4839 | 60.4324 | 60.4902 | 123.0972 | 61.4241 | 122.9781 | 61.2615 | 61.3336 | 122.728 | 61.3023 | 122.5199 | 61.7636 | 61.7949 | 61.6445 | 61.6758
1027.5938 | 123.4085 | -61.3586 | 61.7203 | -0.047549 | -0.92423 | -0.90941 | -0.89035 | -0.82439 | -0.88046 | -0.81812 | 61.7569 | 0.13874 | 61.6515 | -0.028522 | 0.043657 | 61.4746 | 0.003143 | 61.2574 | 61.3111 | 60.4344 | 60.4492 | 60.4683 | 60.5343 | 60.4782 | 60.5405 | 123.1155 | 61.4974 | 123.0101 | 61.3301 | 61.4023 | 122.8332 | 61.3618 | 122.616 | 61.7132 | 61.7537 | 61.6078 | 61.6483
1028.5938 | 123.3627 | -61.3678 | 61.734 | -0.052128 | -0.94713 | -0.9323 | -0.90867 | -0.85644 | -0.89877 | -0.83643 | 61.7569 | 0.12958 | 61.6561 | -0.03768 | 0.039079 | 61.47 | 0.007721 | 61.2574 | 61.3157 | 60.4207 | 60.4355 | 60.4591 | 60.5114 | 60.469 | 60.5314 | 123.1247 | 61.4974 | 123.0239 | 61.3301 | 61.4069 | 122.8378 | 61.3755 | 122.6252 | 61.7178 | 61.7491 | 61.617 | 61.6483
1029.5938 | 123.3582 | -61.3403 | 61.7523 | -0.047549 | -0.9746 | -0.95977 | -0.93614 | -0.87933 | -0.93082 | -0.8639 | 61.7798 | 0.11585 | 61.6744 | -0.03768 | 0.039079 | 61.4471 | 0.007721 | 61.2299 | 61.2928 | 60.3657 | 60.3806 | 60.4042 | 60.461 | 60.4095 | 60.4764 | 123.1201 | 61.4562 | 123.0147 | 61.3027 | 61.3794 | 122.7875 | 61.3481 | 122.5702 | 61.7407 | 61.772 | 61.6353 | 61.6667
1030.5938 | 123.3307 | -61.3586 | 61.7432 | -0.070441 | -1.0845 | -1.0742 | -1.0506 | -0.9892 | -1.0453 | -0.98293 | 61.766 | 0.12501 | 61.6652 | -0.03768 | 0.034501 | 61.4563 | 0.003143 | 61.2391 | 61.2882 | 60.2742 | 60.2844 | 60.308 | 60.3694 | 60.3134 | 60.3757 | 123.1247 | 61.4836 | 123.0239 | 61.321 | 61.3931 | 122.8149 | 61.3618 | 122.5977 | 61.7315 | 61.7629 | 61.6307 | 61.6621
1031.5938 | 123.3398 | -61.3266 | 61.7477 | -0.070441 | -1.1165 | -1.1063 | -1.0735 | -1.0121 | -1.0682 | -1.0058 | 61.8027 | 0.13416 | 61.6881 | -0.03768 | 0.043657 | 61.4334 | 0.007721 | 61.2207 | 61.2562 | 60.2101 | 60.2203 | 60.2531 | 60.3145 | 60.2584 | 60.3208 | 123.1293 | 61.4608 | 123.0147 | 61.2889 | 61.3703 | 122.76 | 61.3343 | 122.5473 | 61.759 | 61.7949 | 61.6445 | 61.6804
1032.5938 | 123.3673 | -61.3861 | 61.7249 | -0.079598 | -1.2356 | -1.2208 | -1.1925 | -1.1403 | -1.1964 | -1.1203 | 61.7569 | 0.12043 | 61.6469 | -0.03768 | 0.029923 | 61.4838 | 0.003143 | 61.2665 | 61.3065 | 60.1505 | 60.1654 | 60.1936 | 60.2458 | 60.1897 | 60.2658 | 123.143 | 61.5065 | 123.033 | 61.3484 | 61.416 | 122.8699 | 61.3893 | 122.6526 | 61.7269 | 61.7537 | 61.617 | 61.6438
1033.5938 | 123.3353 | -61.3861 | 61.7111 | -0.07502 | -1.1944 | -1.1795 | -1.1605 | -1.0991 | -1.1506 | -1.0928 | 61.7477 | 0.12958 | 61.6286 | -0.033101 | 0.048236 | 61.4929 | 0.003143 | 61.2711 | 61.3111 | 60.1917 | 60.2066 | 60.2256 | 60.287 | 60.2355 | 60.2933 | 123.1338 | 61.5157 | 123.0147 | 61.353 | 61.4343 | 122.879 | 61.3893 | 122.6572 | 61.6995 | 61.7446 | 61.5804 | 61.6255
1034.5938 | 123.3353 | -61.3678 | 61.7203 | -0.07502 | -1.1852 | -1.1795 | -1.1559 | -1.0899 | -1.1506 | -1.0837 | 61.7569 | 0.12043 | 61.6561 | -0.033101 | 0.039079 | 61.4654 | 0.003143 | 61.2528 | 61.2928 | 60.1826 | 60.1883 | 60.2119 | 60.2779 | 60.2172 | 60.2841 | 123.1247 | 61.4882 | 123.0239 | 61.3347 | 61.4069 | 122.8332 | 61.3709 | 122.6206 | 61.7178 | 61.7537 | 61.617 | 61.6529
1035.5938 | 123.3261 | -61.377 | 61.7203 | -0.079598 | -1.2264 | -1.2162 | -1.188 | -1.1357 | -1.1872 | -1.1111 | 61.7523 | 0.12043 | 61.6423 | -0.033101 | 0.039079 | 61.4746 | 0.003143 | 61.2665 | 61.2974 | 60.1505 | 60.1608 | 60.189 | 60.2413 | 60.1897 | 60.2658 | 123.1292 | 61.4974 | 123.0193 | 61.3439 | 61.416 | 122.8516 | 61.3801 | 122.6435 | 61.7132 | 61.7491 | 61.6032 | 61.6392
1036.5938 | 123.3582 | -61.3998 | 61.7111 | -0.079598 | -1.1761 | -1.1704 | -1.1513 | -1.0899 | -1.1414 | -1.0745 | 61.7431 | 0.12958 | 61.6469 | -0.033101 | 0.039079 | 61.4883 | 0.007721 | 61.2665 | 61.3202 | 60.2238 | 60.2295 | 60.2485 | 60.3099 | 60.2584 | 60.3253 | 123.143 | 61.5294 | 123.0467 | 61.3667 | 61.4389 | 122.8882 | 61.4076 | 122.6664 | 61.7041 | 61.7354 | 61.6078 | 61.6392
1037.5938 | 123.3719 | -61.3358 | 61.7249 | -0.07502 | -1.2035 | -1.1841 | -1.1605 | -1.1128 | -1.1643 | -1.102 | 61.7752 | 0.12043 | 61.6652 | -0.03768 | 0.034501 | 61.4517 | 0.003143 | 61.2482 | 61.2607 | 60.1322 | 60.1516 | 60.1753 | 60.223 | 60.1714 | 60.2338 | 123.1109 | 61.4562 | 123.001 | 61.2981 | 61.3703 | 122.7875 | 61.3389 | 122.584 | 61.7407 | 61.772 | 61.6307 | 61.6621
1038.5938 | 123.3902 | -61.3358 | 61.6974 | -0.070441 | -1.231 | -1.2162 | -1.188 | -1.1448 | -1.1872 | -1.1249 | 61.7798 | 0.12958 | 61.679 | -0.033101 | 0.039079 | 61.4609 | 0.003143 | 61.2391 | 61.2653 | 60.1047 | 60.1196 | 60.1478 | 60.1909 | 60.1485 | 60.2109 | 123.1155 | 61.4653 | 123.0147 | 61.3027 | 61.3748 | 122.7966 | 61.3389 | 122.5748 | 61.7407 | 61.7766 | 61.6399 | 61.6758
1039.5938 | 123.3353 | -61.3815 | 61.734 | -0.079598 | -1.1623 | -1.1475 | -1.1239 | -1.0716 | -1.1231 | -1.0562 | 61.7614 | 0.13416 | 61.6423 | -0.042259 | 0.039079 | 61.47 | 0.012299 | 61.2757 | 61.3019 | 60.2192 | 60.234 | 60.2577 | 60.3099 | 60.2584 | 60.3254 | 123.143 | 61.5157 | 123.0239 | 61.3393 | 61.4206 | 122.8516 | 61.3938 | 122.6572 | 61.7224 | 61.7491 | 61.6032 | 61.63
1040.5938 | 123.349 | -61.3678 | 61.6699 | -0.079598 | -1.2173 | -1.1979 | -1.1788 | -1.1174 | -1.1826 | -1.1157 | 61.7431 | 0.12501 | 61.6423 | -0.03768 | 0.039079 | 61.4929 | -0.001436 | 61.2986 | 61.2882 | 60.1505 | 60.1699 | 60.189 | 60.2504 | 60.1852 | 60.2521 | 123.1109 | 61.4928 | 123.0101 | 61.3301 | 61.4069 | 122.8607 | 61.3664 | 122.6664 | 61.7041 | 61.7446 | 61.6032 | 61.6438
1041.5938 | 123.3627 | -61.3495 | 61.7249 | -0.088755 | -1.2219 | -1.2116 | -1.188 | -1.1403 | -1.1781 | -1.1203 | 61.766 | 0.12958 | 61.6606 | -0.042259 | 0.039079 | 61.4654 | -0.001436 | 61.2482 | 61.2607 | 60.1276 | 60.1379 | 60.1615 | 60.2092 | 60.1714 | 60.2292 | 123.1155 | 61.4791 | 123.0101 | 61.3072 | 61.3886 | 122.8149 | 61.3481 | 122.5977 | 61.7269 | 61.7675 | 61.6216 | 61.6621
1042.5938 | 123.3582 | -61.3815 | 61.6791 | -0.097912 | -1.3226 | -1.3032 | -1.2749 | -1.2227 | -1.2788 | -1.2164 | 61.734 | 0.12043 | 61.6194 | -0.042259 | 0.039079 | 61.5021 | -0.001436 | 61.2894 | 61.2836 | 60.0589 | 60.0784 | 60.1066 | 60.1589 | 60.1028 | 60.1651 | 123.1155 | 61.502 | 123.001 | 61.3393 | 61.4206 | 122.8836 | 61.3801 | 122.6709 | 61.6949 | 61.7354 | 61.5804 | 61.6209
1043.5938 | 123.317 | -61.377 | 61.6745 | -0.097912 | -1.3592 | -1.3444 | -1.3253 | -1.2776 | -1.3291 | -1.2622 | 61.766 | 0.12501 | 61.6515 | -0.03768 | 0.039079 | 61.4654 | 0.003143 | 61.2619 | 61.279 | 60.0177 | 60.0326 | 60.0516 | 60.0993 | 60.0478 | 60.1148 | 123.143 | 61.502 | 123.0284 | 61.3393 | 61.416 | 122.8424 | 61.3801 | 122.6389 | 61.7269 | 61.7629 | 61.6124 | 61.6483
1044.5938 | 123.4085 | -61.3632 | 61.7111 | -0.097912 | -1.4279 | -1.4131 | -1.3848 | -1.3371 | -1.3887 | -1.3171 | 61.7706 | 0.12958 | 61.6698 | -0.033101 | 0.039079 | 61.4654 | 0.007721 | 61.2574 | 61.2653 | 59.9353 | 59.9502 | 59.9784 | 60.0261 | 59.9746 | 60.0461 | 123.1338 | 61.4928 | 123.033 | 61.3301 | 61.4023 | 122.8287 | 61.3709 | 122.6206 | 61.7315 | 61.7629 | 61.6307 | 61.6621
1045.5938 | 123.3856 | -61.3358 | 61.7249 | -0.10707 | -1.4187 | -1.4176 | -1.3848 | -1.3371 | -1.3887 | -1.3217 | 61.7706 | 0.12501 | 61.6561 | -0.03768 | 0.043657 | 61.4654 | -0.001436 | 61.2482 | 61.2287 | 59.917 | 59.9181 | 59.9509 | 59.9986 | 59.9471 | 60.014 | 123.1064 | 61.4608 | 122.9918 | 61.2981 | 61.3794 | 122.8012 | 61.3343 | 122.584 | 61.7269 | 61.772 | 61.6124 | 61.6575
1046.5938 | 123.3902 | -61.3312 | 61.7294 | -0.11622 | -1.5103 | -1.5 | -1.4718 | -1.4241 | -1.4756 | -1.4087 | 61.7843 | 0.12043 | 61.6744 | -0.03768 | 0.029923 | 61.4471 | 0.003143 | 61.2436 | 61.215 | 59.8209 | 59.8311 | 59.8594 | 59.9071 | 59.8555 | 59.9225 | 123.1155 | 61.4516 | 123.0056 | 61.2935 | 61.3611 | 122.7783 | 61.3343 | 122.5748 | 61.7544 | 61.7812 | 61.6445 | 61.6712
1047.5938 | 123.381 | -61.322 | 61.7249 | -0.11165 | -1.4554 | -1.468 | -1.426 | -1.3737 | -1.4344 | -1.3721 | 61.7752 | 0.11585 | 61.6606 | -0.03768 | 0.039079 | 61.4563 | -0.001436 | 61.2436 | 61.2104 | 59.8666 | 59.854 | 59.896 | 59.9483 | 59.8876 | 59.9499 | 123.0972 | 61.4379 | 122.9827 | 61.2843 | 61.3611 | 122.7783 | 61.3206 | 122.5657 | 61.7361 | 61.7766 | 61.6216 | 61.6621
1048.5938 | 123.3673 | -61.3266 | 61.7477 | -0.11165 | -1.4737 | -1.4634 | -1.426 | -1.3783 | -1.4344 | -1.3583 | 61.7752 | 0.12043 | 61.6744 | -0.042259 | 0.034501 | 61.4471 | 0.007721 | 61.2345 | 61.215 | 59.8529 | 59.8632 | 59.9006 | 59.9483 | 59.8922 | 59.9683 | 123.1018 | 61.447 | 123.001 | 61.2843 | 61.3611 | 122.7737 | 61.3343 | 122.5611 | 61.7407 | 61.7675 | 61.6399 | 61.6667
1049.5938 | 123.3582 | -61.3358 | 61.7432 | -0.1208 | -1.5057 | -1.5 | -1.4672 | -1.4149 | -1.4665 | -1.4041 | 61.7752 | 0.12958 | 61.6744 | -0.03768 | 0.034501 | 61.4517 | 0.007721 | 61.2391 | 61.215 | 59.83 | 59.8357 | 59.8685 | 59.9208 | 59.8693 | 59.9316 | 123.1109 | 61.4653 | 123.0101 | 61.2981 | 61.3703 | 122.7875 | 61.3435 | 122.5748 | 61.7407 | 61.7675 | 61.6399 | 61.6667
1050.5938 | 123.3032 | -61.3586 | 61.7249 | -0.1208 | -1.4462 | -1.4359 | -1.4031 | -1.3554 | -1.4116 | -1.3446 | 61.7706 | 0.12958 | 61.6698 | -0.03768 | 0.039079 | 61.4563 | 0.007721 | 61.2528 | 61.2378 | 59.9124 | 59.9227 | 59.9555 | 60.0032 | 59.9471 | 60.014 | 123.1292 | 61.4882 | 123.0284 | 61.321 | 61.3977 | 122.8149 | 61.3664 | 122.6114 | 61.7315 | 61.7629 | 61.6307 | 61.6621
1051.5938 | 123.23 | -61.3815 | 61.7523 | -0.11622 | -1.3638 | -1.349 | -1.3162 | -1.273 | -1.3246 | -1.2668 | 61.766 | 0.12043 | 61.6515 | -0.03768 | 0.039079 | 61.47 | 0.007721 | 61.2528 | 61.2653 | 60.0177 | 60.0326 | 60.0654 | 60.1085 | 60.057 | 60.1148 | 123.1476 | 61.502 | 123.033 | 61.3439 | 61.4206 | 122.8516 | 61.3893 | 122.6343 | 61.7269 | 61.7583 | 61.6124 | 61.6438
1052.5938 | 123.2666 | -61.3724 | 61.7477 | -0.12538 | -1.4416 | -1.4359 | -1.3986 | -1.36 | -1.407 | -1.3492 | 61.7614 | 0.12958 | 61.6606 | -0.033101 | 0.043657 | 61.4609 | 0.003143 | 61.2482 | 61.247 | 59.9307 | 59.9364 | 59.9738 | 60.0124 | 59.9654 | 60.0232 | 123.1338 | 61.502 | 123.033 | 61.3393 | 61.416 | 122.8332 | 61.3755 | 122.6206 | 61.7178 | 61.7583 | 61.617 | 61.6575
1053.5938 | 123.3032 | -61.377 | 61.7249 | -0.14369 | -1.5103 | -1.5046 | -1.4627 | -1.4149 | -1.4711 | -1.4041 | 61.7752 | 0.12958 | 61.6606 | -0.03768 | 0.034501 | 61.4654 | -0.001436 | 61.2436 | 61.2333 | 59.8666 | 59.8723 | 59.9143 | 59.962 | 59.9059 | 59.9728 | 123.1521 | 61.5065 | 123.0376 | 61.3393 | 61.4115 | 122.8424 | 61.3755 | 122.6206 | 61.7407 | 61.7766 | 61.6261 | 61.6621
1054.5938 | 123.3719 | -61.3495 | 61.7249 | -0.12996 | -1.4371 | -1.4268 | -1.3986 | -1.3509 | -1.4024 | -1.3354 | 61.7798 | 0.13416 | 61.6698 | -0.033101 | 0.039079 | 61.4517 | -0.001436 | 61.2436 | 61.2195 | 59.9124 | 59.9227 | 59.9509 | 59.9986 | 59.9471 | 60.014 | 123.1292 | 61.4837 | 123.0193 | 61.3164 | 61.3886 | 122.8012 | 61.3481 | 122.5931 | 61.7407 | 61.7812 | 61.6307 | 61.6712
1055.5938 | 123.2254 | -61.377 | 61.7752 | -0.1208 | -1.4554 | -1.4405 | -1.4077 | -1.36 | -1.4116 | -1.34 | 61.7706 | 0.11127 | 61.6606 | -0.03768 | 0.039079 | 61.4563 | 0.007721 | 61.2482 | 61.2561 | 59.9216 | 59.9364 | 59.9692 | 60.0169 | 59.9654 | 60.0369 | 123.1476 | 61.4882 | 123.0376 | 61.3393 | 61.416 | 122.8332 | 61.3847 | 122.6252 | 61.7315 | 61.7629 | 61.6216 | 61.6529
1056.5938 | 123.2391 | -61.3861 | 61.7752 | -0.12996 | -1.4004 | -1.381 | -1.3574 | -1.3142 | -1.3566 | -1.2942 | 61.7798 | 0.12501 | 61.6652 | -0.03768 | 0.043657 | 61.4563 | -0.001436 | 61.2482 | 61.2561 | 59.9857 | 60.0051 | 60.0287 | 60.0719 | 60.0295 | 60.0919 | 123.1659 | 61.5111 | 123.0513 | 61.3484 | 61.4298 | 122.8424 | 61.3847 | 122.6343 | 61.7361 | 61.7812 | 61.6216 | 61.6667
1057.5938 | 123.262 | -61.377 | 61.7569 | -0.12996 | -1.4004 | -1.3947 | -1.3574 | -1.3188 | -1.3703 | -1.3034 | 61.7569 | 0.13416 | 61.6423 | -0.042259 | 0.048236 | 61.4746 | 0.007721 | 61.2711 | 61.247 | 59.9765 | 59.9822 | 60.0196 | 60.0581 | 60.0066 | 60.0736 | 123.1338 | 61.5111 | 123.0193 | 61.3347 | 61.4252 | 122.8516 | 61.3847 | 122.6481 | 61.7086 | 61.7491 | 61.5941 | 61.6346
1058.5938 | 123.2803 | -61.3586 | 61.7798 | -0.13454 | -1.3821 | -1.3673 | -1.3299 | -1.2913 | -1.3429 | -1.2714 | 61.7614 | 0.12501 | 61.6469 | -0.033101 | 0.039079 | 61.4746 | 0.012299 | 61.2711 | 61.2241 | 59.9765 | 59.9914 | 60.0288 | 60.0673 | 60.0158 | 60.0873 | 123.1201 | 61.4836 | 123.0055 | 61.3255 | 61.3977 | 122.8332 | 61.3709 | 122.6297 | 61.7224 | 61.7491 | 61.6078 | 61.6346
1059.5938 | 123.3856 | -61.3815 | 61.6928 | -0.12538 | -1.3043 | -1.2986 | -1.2704 | -1.2273 | -1.2742 | -1.2073 | 61.7569 | 0.12501 | 61.6561 | -0.028522 | 0.043657 | 61.4838 | 0.007721 | 61.2574 | 61.2561 | 60.0773 | 60.0829 | 60.1112 | 60.1543 | 60.1073 | 60.1743 | 123.1384 | 61.5065 | 123.0376 | 61.353 | 61.4252 | 122.8653 | 61.3893 | 122.6389 | 61.7132 | 61.7491 | 61.6124 | 61.6483
1060.5938 | 123.2437 | -61.3953 | 61.7569 | -0.14827 | -1.4325 | -1.4222 | -1.3848 | -1.3463 | -1.3978 | -1.3309 | 61.7569 | 0.12501 | 61.6515 | -0.03768 | 0.039079 | 61.4792 | -0.001436 | 61.2665 | 61.247 | 59.9628 | 59.9731 | 60.0104 | 60.049 | 59.9974 | 60.0644 | 123.1521 | 61.5203 | 123.0467 | 61.3576 | 61.4343 | 122.8744 | 61.3938 | 122.6618 | 61.7178 | 61.7583 | 61.6124 | 61.6529
1061.5938 | 123.2666 | -61.3495 | 61.7798 | -0.15285 | -1.5149 | -1.5092 | -1.4718 | -1.4333 | -1.4802 | -1.4224 | 61.7706 | 0.12958 | 61.6561 | -0.03768 | 0.048236 | 61.47 | -0.006014 | 61.2482 | 61.1966 | 59.8346 | 59.8403 | 59.8777 | 59.9162 | 59.8693 | 59.9271 | 123.1201 | 61.4791 | 123.0055 | 61.3118 | 61.3977 | 122.8195 | 61.3435 | 122.5977 | 61.7224 | 61.7766 | 61.6078 | 61.6621
1062.5938 | 123.2666 | -61.3358 | 61.7889 | -0.16659 | -1.5882 | -1.5825 | -1.5588 | -1.5065 | -1.5626 | -1.4865 | 61.7935 | 0.13874 | 61.6881 | -0.03768 | 0.039079 | 61.4426 | 0.003143 | 61.2253 | 61.1692 | 59.7476 | 59.7533 | 59.7769 | 59.8292 | 59.7731 | 59.8492 | 123.1292 | 61.4745 | 123.0239 | 61.2981 | 61.3748 | 122.7783 | 61.3389 | 122.5611 | 61.7544 | 61.7904 | 61.649 | 61.685
1063.5938 | 123.2712 | -61.3266 | 61.8393 | -0.20321 | -1.872 | -1.8663 | -1.8381 | -1.8041 | -1.8511 | -1.7795 | 61.8118 | 0.12501 | 61.7018 | -0.033101 | 0.043657 | 61.4197 | 0.003143 | 61.207 | 61.1234 | 59.4546 | 59.4603 | 59.4885 | 59.5225 | 59.4755 | 59.5471 | 123.1384 | 61.4516 | 123.0284 | 61.2935 | 61.3703 | 122.7463 | 61.3297 | 122.5336 | 61.7682 | 61.8087 | 61.6582 | 61.6987
1064.5938 | 123.4177 | -61.2808 | 61.7981 | -0.249 | -2.22 | -2.2052 | -2.1723 | -2.1428 | -2.199 | -2.1183 | 61.821 | 0.12043 | 61.711 | -0.03768 | 0.039079 | 61.4151 | 0.007721 | 61.1978 | 61.0318 | 59.0608 | 59.0757 | 59.1085 | 59.138 | 59.0818 | 59.1625 | 123.1018 | 61.4012 | 122.9918 | 61.2431 | 61.3199 | 122.6959 | 61.2885 | 122.4787 | 61.7819 | 61.8132 | 61.6719 | 61.7033
1065.5938 | 123.2574 | -61.3174 | 61.8622 | -0.27647 | -2.4444 | -2.4387 | -2.4013 | -2.3717 | -2.428 | -2.3472 | 61.821 | 0.13416 | 61.7156 | -0.033101 | 0.039079 | 61.4197 | 0.003143 | 61.207 | 61.041 | 58.873 | 58.8788 | 58.9162 | 58.9457 | 58.8895 | 58.9702 | 123.1384 | 61.4516 | 123.033 | 61.2843 | 61.3565 | 122.7371 | 61.3206 | 122.5244 | 61.7819 | 61.8178 | 61.6765 | 61.7124
1066.5938 | 123.3261 | -61.2854 | 61.8484 | -0.30394 | -2.5863 | -2.576 | -2.5432 | -2.4953 | -2.5653 | -2.4754 | 61.821 | 0.12958 | 61.7202 | -0.033101 | 0.034501 | 61.4105 | 0.012299 | 61.1978 | 60.9815 | 58.6991 | 58.7094 | 58.7422 | 58.7901 | 58.7201 | 58.81 | 123.1064 | 61.415 | 123.0056 | 61.2523 | 61.3199 | 122.6959 | 61.2977 | 122.4832 | 61.7865 | 61.8087 | 61.6857 | 61.7079
1067.5938 | 123.3124 | -61.3083 | 61.8301 | -0.31767 | -2.6276 | -2.6172 | -2.5798 | -2.5457 | -2.6111 | -2.5304 | 61.8072 | 0.13416 | 61.7064 | -0.033101 | 0.039079 | 61.4197 | 0.007721 | 61.2116 | 60.9906 | 58.6807 | 58.6911 | 58.7285 | 58.7626 | 58.6972 | 58.7779 | 123.1155 | 61.4425 | 123.0147 | 61.2752 | 61.3474 | 122.728 | 61.316 | 122.5199 | 61.7682 | 61.7995 | 61.6673 | 61.6987
1068.5938 | 123.2529 | -61.3312 | 61.8256 | -0.30852 | -2.6184 | -2.6126 | -2.5798 | -2.5457 | -2.6157 | -2.5304 | 61.8118 | 0.12501 | 61.6973 | -0.033101 | 0.048236 | 61.4242 | 0.007721 | 61.207 | 61.0227 | 58.7128 | 58.7185 | 58.7514 | 58.7855 | 58.7155 | 58.8008 | 123.143 | 61.4562 | 123.0284 | 61.2981 | 61.3794 | 122.7554 | 61.3389 | 122.5382 | 61.7636 | 61.8041 | 61.649 | 61.6895
1069.6094 | 123.2391 | -61.29 | 61.8668 | -0.34514 | -2.8061 | -2.8004 | -2.763 | -2.7242 | -2.8034 | -2.7043 | 61.8393 | 0.13874 | 61.7293 | -0.03768 | 0.039079 | 61.3968 | 0.007721 | 61.1887 | 60.9448 | 58.4839 | 58.4896 | 58.527 | 58.5657 | 58.4866 | 58.5857 | 123.1293 | 61.4287 | 123.0193 | 61.2523 | 61.3291 | 122.6867 | 61.2977 | 122.4787 | 61.8002 | 61.8316 | 61.6902 | 61.7216
1070.5938 | 123.2254 | -61.3083 | 61.8622 | -0.39093 | -3.0854 | -3.0797 | -3.0422 | -3.0081 | -3.0689 | -2.9927 | 61.8439 | 0.12501 | 61.743 | -0.033101 | 0.039079 | 61.383 | 0.003143 | 61.175 | 60.9174 | 58.2229 | 58.2286 | 58.266 | 58.3002 | 58.2394 | 58.3155 | 123.1521 | 61.4333 | 123.0513 | 61.2752 | 61.3474 | 122.6913 | 61.3114 | 122.4832 | 61.8048 | 61.8407 | 61.704 | 61.7399
1071.5938 | 123.2529 | -61.2717 | 61.8942 | -0.41382 | -3.2457 | -3.2262 | -3.1979 | -3.1637 | -3.2383 | -3.1438 | 61.8622 | 0.13416 | 61.7568 | -0.028522 | 0.034501 | 61.3739 | 0.003143 | 61.1658 | 60.8578 | 58.026 | 58.0455 | 58.0738 | 58.1079 | 58.0333 | 58.1278 | 123.1338 | 61.4058 | 123.0285 | 61.2431 | 61.3062 | 122.6455 | 61.2748 | 122.4375 | 61.8277 | 61.859 | 61.7223 | 61.7536
1072.5938 | 123.3078 | -61.2762 | 61.853 | -0.43213 | -3.3739 | -3.3544 | -3.3215 | -3.2828 | -3.3619 | -3.272 | 61.8484 | 0.13416 | 61.7476 | -0.033101 | 0.043657 | 61.3785 | 0.003143 | 61.1704 | 60.8441 | 57.9023 | 57.9219 | 57.9547 | 57.9935 | 57.9143 | 58.0042 | 123.1247 | 61.4104 | 123.0239 | 61.2431 | 61.3199 | 122.6547 | 61.2794 | 122.4466 | 61.8048 | 61.8453 | 61.704 | 61.7445
1073.5938 | 123.2941 | -61.2488 | 61.8576 | -0.4596 | -3.5067 | -3.5055 | -3.468 | -3.4338 | -3.5085 | -3.4139 | 61.8805 | 0.12958 | 61.7705 | -0.03768 | 0.039079 | 61.351 | 0.003143 | 61.1383 | 60.7892 | 57.7421 | 57.7433 | 57.7807 | 57.815 | 57.7403 | 57.8348 | 123.1293 | 61.3784 | 123.0193 | 61.2111 | 61.2879 | 122.5998 | 61.2519 | 122.3871 | 61.8414 | 61.8773 | 61.7314 | 61.7674
1074.6094 | 123.3994 | -61.2213 | 61.8713 | -0.48707 | -3.6761 | -3.6703 | -3.6329 | -3.6078 | -3.6824 | -3.5833 | 61.8851 | 0.12958 | 61.7705 | -0.033101 | 0.039079 | 61.351 | 0.007721 | 61.1429 | 60.7342 | 57.5452 | 57.551 | 57.5884 | 57.6135 | 57.5389 | 57.638 | 123.1064 | 61.3509 | 122.9918 | 61.1882 | 61.2604 | 122.5723 | 61.229 | 122.3642 | 61.846 | 61.8773 | 61.7314 | 61.7628
1075.5938 | 123.2483 | -61.2717 | 61.8576 | -0.50081 | -3.6807 | -3.6703 | -3.642 | -3.6032 | -3.687 | -3.5879 | 61.8713 | 0.14332 | 61.7659 | -0.033101 | 0.034501 | 61.3739 | 0.007721 | 61.1658 | 60.7709 | 57.591 | 57.6014 | 57.6296 | 57.6685 | 57.5847 | 57.6838 | 123.143 | 61.415 | 123.0376 | 61.2386 | 61.3062 | 122.6455 | 61.2794 | 122.4375 | 61.8368 | 61.8636 | 61.7314 | 61.7582
1076.5938 | 123.2712 | -61.2762 | 61.8668 | -0.50997 | -3.7539 | -3.7481 | -3.7153 | -3.6902 | -3.7603 | -3.6657 | 61.8439 | 0.13874 | 61.7339 | -0.028522 | 0.043657 | 61.3922 | 0.012299 | 61.1795 | 60.7663 | 57.5223 | 57.5281 | 57.561 | 57.5861 | 57.516 | 57.6105 | 123.1201 | 61.415 | 123.0101 | 61.2477 | 61.3199 | 122.6684 | 61.2885 | 122.4558 | 61.8002 | 61.8316 | 61.6902 | 61.7216
1077.5938 | 123.2849 | -61.2442 | 61.8988 | -0.55575 | -3.96 | -3.9542 | -3.9213 | -3.8825 | -3.9663 | -3.8718 | 61.8713 | 0.14332 | 61.7705 | -0.046838 | 0.048236 | 61.3647 | -0.001436 | 61.1566 | 60.6885 | 57.2842 | 57.29 | 57.3229 | 57.3617 | 57.2779 | 57.3724 | 123.1155 | 61.3875 | 123.0147 | 61.1974 | 61.2924 | 122.6089 | 61.2428 | 122.4008 | 61.8231 | 61.8728 | 61.7223 | 61.772
1078.5938 | 123.2986 | -61.2671 | 61.8759 | -0.57864 | -4.079 | -4.0732 | -4.0358 | -4.0061 | -4.0808 | -3.9908 | 61.8759 | 0.13874 | 61.7659 | -0.033101 | 0.039079 | 61.3601 | 0.007721 | 61.1475 | 60.6884 | 57.1881 | 57.1939 | 57.2313 | 57.261 | 57.1863 | 57.2763 | 123.143 | 61.4058 | 123.033 | 61.234 | 61.3062 | 122.6272 | 61.2748 | 122.4146 | 61.8368 | 61.8682 | 61.7269 | 61.7582
1079.6094 | 123.2666 | -61.2396 | 61.9171 | -0.59696 | -4.1569 | -4.1556 | -4.1182 | -4.0885 | -4.1632 | -4.064 | 61.8851 | 0.13416 | 61.7705 | -0.03768 | 0.039079 | 61.3601 | 0.003143 | 61.1429 | 60.6427 | 57.0827 | 57.084 | 57.1214 | 57.1511 | 57.0765 | 57.1756 | 123.1247 | 61.3738 | 123.0101 | 61.2019 | 61.2787 | 122.5998 | 61.2428 | 122.3825 | 61.846 | 61.8819 | 61.7314 | 61.7674
1080.5938 | 123.4085 | -61.1847 | 61.9034 | -0.63816 | -4.3904 | -4.3891 | -4.3517 | -4.322 | -4.4012 | -4.3067 | 61.8942 | 0.12958 | 61.7934 | -0.033101 | 0.048236 | 61.3235 | 0.012299 | 61.1154 | 60.5465 | 56.7943 | 56.7955 | 56.833 | 56.8627 | 56.7835 | 56.878 | 123.0789 | 61.3143 | 122.9781 | 61.1516 | 61.2329 | 122.5082 | 61.197 | 122.3001 | 61.846 | 61.8819 | 61.7452 | 61.7811
1081.5938 | 123.2574 | -61.1938 | 62.0087 | -0.69768 | -4.7384 | -4.728 | -4.6997 | -4.6607 | -4.7446 | -4.6409 | 61.9171 | 0.13874 | 61.8209 | -0.028522 | 0.039079 | 61.3189 | 0.007721 | 61.0971 | 60.4962 | 56.4555 | 56.4659 | 56.4942 | 56.5331 | 56.4492 | 56.553 | 123.111 | 61.3326 | 123.0147 | 61.1653 | 61.2329 | 122.5128 | 61.2016 | 122.291 | 61.878 | 61.9094 | 61.7818 | 61.8132
1082.5938 | 123.3582 | -61.203 | 61.8896 | -0.72057 | -4.7979 | -4.7921 | -4.7638 | -4.734 | -4.8087 | -4.7004 | 61.9171 | 0.12501 | 61.8071 | -0.033101 | 0.043657 | 61.3144 | 0.007721 | 61.1063 | 60.4824 | 56.4051 | 56.4109 | 56.4392 | 56.469 | 56.3943 | 56.5026 | 123.1201 | 61.328 | 123.0101 | 61.1699 | 61.2467 | 122.5174 | 61.2107 | 122.3093 | 61.8735 | 61.9094 | 61.7635 | 61.7994
1083.5938 | 123.3124 | -61.1893 | 61.9583 | -0.76636 | -5.0269 | -5.0118 | -4.9927 | -4.9583 | -5.0331 | -4.9247 | 61.9263 | 0.12501 | 61.8117 | -0.028522 | 0.039079 | 61.3052 | 0.003143 | 61.088 | 60.4229 | 56.1624 | 56.1774 | 56.1966 | 56.231 | 56.1562 | 56.2645 | 123.1155 | 61.3143 | 123.001 | 61.1607 | 61.2283 | 122.4945 | 61.1924 | 122.2772 | 61.8872 | 61.9231 | 61.7726 | 61.8086
1084.6094 | 123.3856 | -61.1481 | 61.9125 | -0.82588 | -5.3611 | -5.3644 | -5.3269 | -5.3016 | -5.381 | -5.2635 | 61.9537 | 0.12501 | 61.8438 | -0.042259 | 0.034501 | 61.2777 | 0.012299 | 61.0697 | 60.3222 | 55.787 | 55.7837 | 55.8212 | 55.8464 | 55.7671 | 55.8845 | 123.1018 | 61.2731 | 122.9918 | 61.1058 | 61.1826 | 122.4258 | 61.1604 | 122.2177 | 61.9192 | 61.9414 | 61.8093 | 61.8315
1085.5938 | 123.436 | -61.1801 | 61.9125 | -0.81672 | -5.2695 | -5.2545 | -5.2262 | -5.1963 | -5.2711 | -5.1674 | 61.9354 | 0.13416 | 61.8209 | -0.03768 | 0.043657 | 61.2961 | 0.007721 | 61.088 | 60.3634 | 55.9106 | 55.9256 | 55.9539 | 55.9838 | 55.909 | 56.0127 | 123.1155 | 61.3143 | 123.001 | 61.1424 | 61.2238 | 122.4762 | 61.1878 | 122.2681 | 61.8918 | 61.9277 | 61.7772 | 61.8132
1086.5938 | 123.3582 | -61.1847 | 61.8759 | -0.8625 | -5.4435 | -5.4239 | -5.4093 | -5.3657 | -5.4634 | -5.3414 | 61.9263 | 0.12501 | 61.8163 | -0.033101 | 0.034501 | 61.3006 | 0.003143 | 61.088 | 60.3222 | 55.7412 | 55.7608 | 55.7754 | 55.819 | 55.7213 | 55.8433 | 123.111 | 61.3097 | 123.001 | 61.1516 | 61.2192 | 122.4853 | 61.1878 | 122.2727 | 61.8918 | 61.9231 | 61.7818 | 61.8132
1087.5938 | 123.3673 | -61.2167 | 61.9034 | -0.88997 | -5.5946 | -5.5887 | -5.5604 | -5.526 | -5.6145 | -5.5016 | 61.9217 | 0.13874 | 61.8209 | -0.033101 | 0.039079 | 61.3052 | 0.007721 | 61.1017 | 60.3268 | 55.6221 | 55.628 | 55.6563 | 55.6908 | 55.6022 | 55.7151 | 123.1384 | 61.3555 | 123.0376 | 61.1836 | 61.2558 | 122.5219 | 61.2245 | 122.3184 | 61.8826 | 61.914 | 61.7818 | 61.8132
1088.5938 | 123.3398 | -61.1526 | 61.9308 | -0.93576 | -5.764 | -5.7444 | -5.7252 | -5.6862 | -5.7839 | -5.6618 | 61.9583 | 0.13416 | 61.8484 | -0.042259 | 0.043657 | 61.2823 | 0.003143 | 61.0605 | 60.2169 | 55.3886 | 55.4082 | 55.4274 | 55.4665 | 55.3687 | 55.4908 | 123.111 | 61.2868 | 123.001 | 61.1104 | 61.1963 | 122.435 | 61.1558 | 122.2132 | 61.9147 | 61.9552 | 61.8047 | 61.8452
1089.6094 | 123.3261 | -61.1526 | 61.94 | -1.0319 | -6.2357 | -6.216 | -6.2014 | -6.1623 | -6.2555 | -6.138 | 61.9812 | 0.12043 | 61.8667 | -0.03768 | 0.034501 | 61.2457 | 0.007721 | 61.0376 | 60.1207 | 54.917 | 54.9366 | 54.9512 | 54.9904 | 54.8972 | 55.0147 | 123.1339 | 61.2731 | 123.0193 | 61.115 | 61.1871 | 122.3983 | 61.1604 | 122.1903 | 61.9467 | 61.9735 | 61.8322 | 61.8589
1090.5938 | 123.3353 | -61.1389 | 61.9354 | -1.0502 | -6.2769 | -6.2664 | -6.238 | -6.2035 | -6.3104 | -6.1746 | 61.9675 | 0.12958 | 61.8575 | -0.03768 | 0.039079 | 61.2732 | -0.006014 | 61.0559 | 60.0887 | 54.862 | 54.8725 | 54.9009 | 54.9354 | 54.8285 | 54.9643 | 123.1064 | 61.2685 | 122.9964 | 61.1012 | 61.178 | 122.4121 | 61.1329 | 122.1948 | 61.9284 | 61.9735 | 61.8184 | 61.8635
1091.5938 | 123.3353 | -61.1664 | 61.9583 | -1.0868 | -6.428 | -6.4129 | -6.3845 | -6.3363 | -6.4478 | -6.3165 | 61.9858 | 0.12501 | 61.8758 | -0.03768 | 0.039079 | 61.2411 | -0.001436 | 61.0239 | 60.0795 | 54.7384 | 54.7535 | 54.7818 | 54.8301 | 54.7186 | 54.8499 | 123.1522 | 61.2914 | 123.0422 | 61.1287 | 61.2055 | 122.4075 | 61.1649 | 122.1903 | 61.9467 | 61.9872 | 61.8367 | 61.8773
1092.5938 | 123.3032 | -61.1526 | 61.9308 | -1.128 | -6.5974 | -6.5823 | -6.5585 | -6.5148 | -6.6126 | -6.4951 | 61.9812 | 0.12501 | 61.8758 | -0.042259 | 0.039079 | 61.2411 | 0.003143 | 61.0468 | 60.0246 | 54.5553 | 54.5704 | 54.5941 | 54.6379 | 54.54 | 54.6576 | 123.1339 | 61.2777 | 123.0285 | 61.1104 | 61.1917 | 122.3938 | 61.1558 | 122.1994 | 61.9421 | 61.9781 | 61.8367 | 61.8727
1093.5938 | 123.3444 | -61.1618 | 61.9263 | -1.1143 | -6.4554 | -6.4495 | -6.4212 | -6.382 | -6.4798 | -6.3577 | 61.9675 | 0.13874 | 61.8667 | -0.03768 | 0.039079 | 61.264 | 0.007721 | 61.0559 | 60.0475 | 54.7064 | 54.7123 | 54.7406 | 54.7798 | 54.682 | 54.8041 | 123.1293 | 61.3005 | 123.0285 | 61.1241 | 61.2009 | 122.4258 | 61.1695 | 122.2177 | 61.9284 | 61.9598 | 61.8276 | 61.8589
1094.5938 | 123.381 | -61.1526 | 61.9354 | -1.0548 | -6.0296 | -6.0283 | -6.0045 | -5.9654 | -6.0632 | -5.9548 | 61.9675 | 0.13416 | 61.8575 | -0.033101 | 0.039079 | 61.2686 | 0.003143 | 61.0559 | 60.0979 | 55.123 | 55.1244 | 55.1481 | 55.1872 | 55.0895 | 55.1978 | 123.1201 | 61.2868 | 123.0102 | 61.1195 | 61.1917 | 122.4212 | 61.1558 | 122.2086 | 61.9284 | 61.9643 | 61.8184 | 61.8544
1095.5938 | 123.3536 | -61.1389 | 61.9263 | -1.1326 | -6.4051 | -6.3991 | -6.3754 | -6.3363 | -6.4295 | -6.3073 | 61.9446 | 0.13416 | 61.8392 | -0.042259 | 0.034501 | 61.2869 | -0.001436 | 61.0651 | 60.0063 | 54.7338 | 54.7398 | 54.7635 | 54.8027 | 54.7095 | 54.8316 | 123.0835 | 61.2731 | 122.9781 | 61.0967 | 61.1734 | 122.4258 | 61.1375 | 122.204 | 61.9101 | 61.946 | 61.8047 | 61.8406
1096.5938 | 123.3032 | -61.1389 | 61.9812 | -1.1876 | -6.6065 | -6.596 | -6.5631 | -6.5331 | -6.6355 | -6.5088 | 61.9812 | 0.13416 | 61.8758 | -0.042259 | 0.039079 | 61.2411 | 0.007721 | 61.0285 | 59.9513 | 54.5324 | 54.5429 | 54.5758 | 54.6058 | 54.5034 | 54.6301 | 123.1201 | 61.2731 | 123.0147 | 61.0967 | 61.178 | 122.38 | 61.1466 | 122.1674 | 61.9421 | 61.9735 | 61.8367 | 61.8681
1097.5938 | 123.3673 | -61.1481 | 61.9125 | -1.2288 | -6.7668 | -6.7563 | -6.7371 | -6.7025 | -6.8095 | -6.6782 | 61.9949 | 0.13416 | 61.8804 | -0.033101 | 0.043657 | 61.2411 | 0.012299 | 61.0285 | 59.9193 | 54.3813 | 54.3918 | 54.411 | 54.4456 | 54.3386 | 54.4699 | 123.143 | 61.2822 | 123.0285 | 61.115 | 61.1917 | 122.3892 | 61.1604 | 122.1765 | 61.9513 | 61.9826 | 61.8367 | 61.8681
1098.5938 | 123.262 | -61.1526 | 61.9354 | -1.1189 | -6.1716 | -6.1519 | -6.1373 | -6.0982 | -6.1868 | -6.0739 | 61.9812 | 0.13416 | 61.8712 | -0.033101 | 0.039079 | 61.2457 | -0.001436 | 61.033 | 60.0338 | 54.9811 | 55.0007 | 55.0153 | 55.0544 | 54.9658 | 55.0788 | 123.1339 | 61.2868 | 123.0239 | 61.1195 | 61.1917 | 122.3983 | 61.1512 | 122.1857 | 61.9421 | 61.9826 | 61.8322 | 61.8727
1099.5938 | 123.3124 | -61.1526 | 61.9446 | -1.1555 | -6.2448 | -6.2343 | -6.206 | -6.1714 | -6.2738 | -6.1471 | 61.9583 | 0.13416 | 61.8529 | -0.03768 | 0.034501 | 61.2594 | 0.012299 | 61.0422 | 59.9971 | 54.9078 | 54.9183 | 54.9467 | 54.9812 | 54.8789 | 55.0055 | 123.111 | 61.2868 | 123.0056 | 61.115 | 61.1871 | 122.4121 | 61.1649 | 122.1948 | 61.9238 | 61.946 | 61.8184 | 61.8406
1100.5938 | 123.23 | -61.1847 | 61.9766 | -1.1967 | -6.3593 | -6.3488 | -6.3342 | -6.2905 | -6.3928 | -6.2661 | 61.9721 | 0.13874 | 61.8575 | -0.03768 | 0.039079 | 61.2503 | 0.007721 | 61.0422 | 59.988 | 54.8254 | 54.8359 | 54.8505 | 54.8942 | 54.7919 | 54.9185 | 123.1567 | 61.3234 | 123.0422 | 61.147 | 61.2238 | 122.435 | 61.1924 | 122.2269 | 61.933 | 61.9643 | 61.8184 | 61.8498
1101.5938 | 123.3536 | -61.1618 | 61.94 | -1.2379 | -6.5333 | -6.5182 | -6.499 | -6.4599 | -6.5577 | -6.4401 | 61.9766 | 0.13416 | 61.8667 | -0.042259 | 0.043657 | 61.2503 | -0.001436 | 61.0376 | 59.9239 | 54.6285 | 54.6436 | 54.6628 | 54.7019 | 54.6041 | 54.7217 | 123.1384 | 61.296 | 123.0285 | 61.1195 | 61.2055 | 122.4121 | 61.1604 | 122.1994 | 61.933 | 61.9781 | 61.823 | 61.8681
1102.5938 | 123.2712 | -61.1481 | 61.9446 | -1.2883 | -6.6706 | -6.6556 | -6.6364 | -6.6064 | -6.7087 | -6.582 | 61.9949 | 0.12501 | 61.8804 | -0.042259 | 0.034501 | 61.2365 | 0.003143 | 61.0147 | 59.8598 | 54.4774 | 54.4925 | 54.5117 | 54.5417 | 54.4393 | 54.566 | 123.143 | 61.2731 | 123.0285 | 61.1058 | 61.1826 | 122.3846 | 61.1512 | 122.1628 | 61.9604 | 61.9918 | 61.8459 | 61.8773
1103.5938 | 123.2483 | -61.1618 | 61.9766 | -1.3478 | -6.9133 | -6.8936 | -6.8744 | -6.8353 | -6.9331 | -6.8155 | 61.9766 | 0.12958 | 61.8667 | -0.033101 | 0.043657 | 61.2594 | 0.007721 | 61.0285 | 59.814 | 54.2485 | 54.2682 | 54.2874 | 54.3266 | 54.2287 | 54.3463 | 123.1384 | 61.2914 | 123.0285 | 61.1287 | 61.2055 | 122.4212 | 61.1695 | 122.1903 | 61.933 | 61.9689 | 61.823 | 61.8589
1104.5938 | 123.3536 | -61.0977 | 61.9766 | -1.3249 | -6.7302 | -6.7059 | -6.6959 | -6.6521 | -6.75 | -6.6324 | 61.9949 | 0.13874 | 61.885 | -0.042259 | 0.039079 | 61.232 | 0.007721 | 61.0147 | 59.7728 | 54.3675 | 54.3918 | 54.4018 | 54.4456 | 54.3478 | 54.4653 | 123.0927 | 61.2365 | 122.9827 | 61.0555 | 61.1368 | 122.3297 | 61.1054 | 122.1124 | 61.9559 | 61.9872 | 61.8459 | 61.8773
1105.5938 | 123.3856 | -61.1526 | 61.908 | -1.3707 | -6.8538 | -6.8524 | -6.8287 | -6.794 | -6.8965 | -6.7652 | 61.9858 | 0.13416 | 61.8712 | -0.03768 | 0.043657 | 61.2457 | 0.007721 | 61.0239 | 59.7819 | 54.2988 | 54.3002 | 54.324 | 54.3586 | 54.2562 | 54.3875 | 123.1384 | 61.2868 | 123.0239 | 61.115 | 61.1963 | 122.3983 | 61.1604 | 122.1765 | 61.9421 | 61.9781 | 61.8276 | 61.8635
1106.5938 | 123.23 | -61.1938 | 61.9629 | -1.389 | -6.8355 | -6.8295 | -6.8012 | -6.762 | -6.8736 | -6.7423 | 61.9812 | 0.13416 | 61.8712 | -0.03768 | 0.034501 | 61.2503 | -0.001436 | 61.033 | 59.8048 | 54.3584 | 54.3643 | 54.3927 | 54.4318 | 54.3203 | 54.4516 | 123.1751 | 61.328 | 123.0651 | 61.1562 | 61.2283 | 122.4441 | 61.1924 | 122.2269 | 61.9467 | 61.9826 | 61.8367 | 61.8727
1107.5938 | 123.2895 | -61.1343 | 62.0041 | -1.4211 | -6.8996 | -6.8845 | -6.8699 | -6.8353 | -6.9331 | -6.8109 | 61.9949 | 0.13416 | 61.8804 | -0.03768 | 0.043657 | 61.2365 | -0.001436 | 61.0285 | 59.7133 | 54.2347 | 54.2499 | 54.2645 | 54.2991 | 54.2013 | 54.3234 | 123.1293 | 61.2685 | 123.0147 | 61.0967 | 61.178 | 122.3709 | 61.1329 | 122.1628 | 61.9513 | 61.9964 | 61.8367 | 61.8818
1108.5938 | 123.2391 | -61.1481 | 61.9858 | -1.4394 | -6.8904 | -6.8753 | -6.8607 | -6.8215 | -6.9239 | -6.7972 | 61.9812 | 0.12958 | 61.8667 | -0.033101 | 0.048236 | 61.2549 | 0.007721 | 61.0285 | 59.7087 | 54.2576 | 54.2727 | 54.2874 | 54.3266 | 54.2241 | 54.3509 | 123.1293 | 61.2777 | 123.0147 | 61.115 | 61.1963 | 122.4029 | 61.1558 | 122.1765 | 61.933 | 61.9735 | 61.8184 | 61.8589
1109.5938 | 123.4131 | -61.1206 | 61.908 | -1.4623 | -6.8859 | -6.8662 | -6.847 | -6.8124 | -6.9148 | -6.7835 | 61.9949 | 0.13416 | 61.885 | -0.033101 | 0.039079 | 61.232 | 0.007721 | 61.0193 | 59.6583 | 54.2348 | 54.2544 | 54.2736 | 54.3082 | 54.2058 | 54.3371 | 123.1156 | 61.2548 | 123.0056 | 61.0875 | 61.1597 | 122.3526 | 61.1283 | 122.1399 | 61.9559 | 61.9872 | 61.8459 | 61.8773
1110.5938 | 123.2208 | -61.1343 | 62.0041 | -1.5126 | -7.037 | -7.0173 | -7.0026 | -6.968 | -7.0659 | -6.9437 | 62.0041 | 0.12501 | 61.8987 | -0.033101 | 0.039079 | 61.2228 | 0.007721 | 61.0101 | 59.6217 | 54.0974 | 54.1171 | 54.1317 | 54.1663 | 54.0685 | 54.1906 | 123.1384 | 61.2593 | 123.0331 | 61.1012 | 61.1734 | 122.3571 | 61.1421 | 122.1445 | 61.965 | 61.9964 | 61.8596 | 61.891
1111.5938 | 123.2437 | -61.116 | 61.9675 | -1.5172 | -6.9637 | -6.9394 | -6.9294 | -6.8902 | -6.9834 | -6.8613 | 61.9858 | 0.14332 | 61.885 | -0.042259 | 0.043657 | 61.2411 | -0.001436 | 61.0239 | 59.5988 | 54.1523 | 54.1766 | 54.1866 | 54.2258 | 54.1326 | 54.2547 | 123.1018 | 61.2593 | 123.001 | 61.0738 | 61.1597 | 122.3571 | 61.1146 | 122.1399 | 61.9421 | 61.9872 | 61.8413 | 61.8864
1112.5938 | 123.262 | -61.116 | 61.9812 | -1.5493 | -7.0141 | -6.9944 | -6.9706 | -6.9405 | -7.043 | -6.9208 | 61.9904 | 0.13416 | 61.885 | -0.033101 | 0.043657 | 61.2365 | -0.001436 | 61.0285 | 59.5668 | 54.102 | 54.1217 | 54.1454 | 54.1755 | 54.0731 | 54.1952 | 123.1064 | 61.2502 | 123.001 | 61.0829 | 61.1597 | 122.3526 | 61.1146 | 122.1445 | 61.9467 | 61.9918 | 61.8413 | 61.8864
1113.5938 | 123.2803 | -61.1389 | 61.972 | -1.595 | -7.1377 | -7.1226 | -7.0988 | -7.0641 | -7.1666 | -7.0399 | 62.0087 | 0.12501 | 61.9079 | -0.042259 | 0.048236 | 61.2182 | -0.001436 | 61.001 | 59.5439 | 54.0012 | 54.0163 | 54.0401 | 54.0748 | 53.9723 | 54.0991 | 123.1476 | 61.2639 | 123.0468 | 61.0967 | 61.1872 | 122.3571 | 61.1375 | 122.1399 | 61.9604 | 62.0101 | 61.8596 | 61.9093
1114.5938 | 123.3536 | -61.1435 | 61.9492 | -1.6134 | -7.1148 | -7.0905 | -7.0805 | -7.0367 | -7.1391 | -7.017 | 61.9949 | 0.13874 | 61.8896 | -0.03768 | 0.039079 | 61.232 | 0.007721 | 61.0239 | 59.5301 | 54.0287 | 54.053 | 54.063 | 54.1068 | 54.0044 | 54.1265 | 123.1384 | 61.2822 | 123.033 | 61.1058 | 61.1826 | 122.3755 | 61.1512 | 122.1674 | 61.9559 | 61.9872 | 61.8505 | 61.8818
1115.5938 | 123.3032 | -61.116 | 62.0132 | -1.6362 | -7.1377 | -7.118 | -7.1034 | -7.0733 | -7.1666 | -7.049 | 62.0087 | 0.13416 | 61.9079 | -0.033101 | 0.048236 | 61.2228 | 0.003143 | 61.0147 | 59.4798 | 53.9783 | 53.998 | 54.0127 | 54.0427 | 53.9494 | 54.067 | 123.1247 | 61.2502 | 123.0239 | 61.0829 | 61.1643 | 122.3388 | 61.1192 | 122.1307 | 61.9604 | 62.0055 | 61.8596 | 61.9047
1116.5938 | 123.3124 | -61.0657 | 62.0453 | -1.6088 | -6.9408 | -6.9211 | -6.8973 | -6.8673 | -6.9743 | -6.8476 | 62.0362 | 0.13416 | 61.9262 | -0.033101 | 0.039079 | 61.1953 | 0.003143 | 60.9873 | 59.4569 | 54.1249 | 54.1446 | 54.1683 | 54.1984 | 54.0914 | 54.2181 | 123.1018 | 61.1998 | 122.9919 | 61.0326 | 61.1048 | 122.261 | 61.0688 | 122.0529 | 61.9971 | 62.033 | 61.8871 | 61.923
1117.5938 | 123.2208 | -61.1252 | 61.972 | -1.6225 | -6.9179 | -6.8936 | -6.8699 | -6.8398 | -6.9377 | -6.8109 | 61.9949 | 0.13874 | 61.8896 | -0.033101 | 0.034501 | 61.2365 | 0.003143 | 61.0147 | 59.5027 | 54.2073 | 54.2315 | 54.2553 | 54.2854 | 54.1875 | 54.3142 | 123.1201 | 61.2639 | 123.0147 | 61.0921 | 61.1597 | 122.3617 | 61.1283 | 122.1399 | 61.9604 | 61.9918 | 61.8551 | 61.8864
1118.5938 | 123.2895 | -61.0931 | 62.0499 | -1.682 | -7.0324 | -7.0218 | -6.9981 | -6.9726 | -7.0704 | -6.9437 | 62.0362 | 0.13874 | 61.917 | -0.033101 | 0.039079 | 61.1999 | 0.007721 | 60.9918 | 59.4111 | 54.0608 | 54.0713 | 54.0951 | 54.1205 | 54.0227 | 54.1494 | 123.1293 | 61.2319 | 123.0102 | 61.06 | 61.1322 | 122.2931 | 61.1009 | 122.085 | 61.9971 | 62.0284 | 61.8779 | 61.9093
1119.5938 | 123.317 | -61.0886 | 61.9766 | -1.7049 | -7.037 | -7.0264 | -7.0026 | -6.9726 | -7.0659 | -6.9529 | 62.0224 | 0.12958 | 61.9033 | -0.03768 | 0.048236 | 61.2091 | 0.007721 | 60.9918 | 59.3836 | 54.0516 | 54.0621 | 54.0859 | 54.116 | 54.0227 | 54.1357 | 123.111 | 61.2181 | 122.9919 | 61.0509 | 61.1368 | 122.2976 | 61.0963 | 122.0804 | 61.9742 | 62.0147 | 61.8551 | 61.8956
1120.5938 | 123.23 | -61.116 | 62.0224 | -1.7416 | -7.1194 | -7.0951 | -7.0805 | -7.0413 | -7.1528 | -7.0261 | 62.0224 | 0.13416 | 61.9216 | -0.03768 | 0.043657 | 61.1999 | 0.007721 | 60.9873 | 59.3745 | 53.9967 | 54.0209 | 54.0356 | 54.0748 | 53.9632 | 54.0899 | 123.1384 | 61.2502 | 123.0376 | 61.0783 | 61.1597 | 122.3159 | 61.1237 | 122.1033 | 61.9788 | 62.0147 | 61.8779 | 61.9139
1121.5938 | 123.2483 | -61.0931 | 62.0087 | -1.7461 | -7.0324 | -7.0173 | -6.9935 | -6.968 | -7.0567 | -6.9346 | 62.0087 | 0.13874 | 61.9079 | -0.033101 | 0.039079 | 61.2182 | -0.001436 | 60.9964 | 59.347 | 54.0608 | 54.0759 | 54.0997 | 54.1251 | 54.0364 | 54.1586 | 123.1018 | 61.2319 | 123.001 | 61.06 | 61.1322 | 122.3114 | 61.0917 | 122.0895 | 61.9696 | 62.0101 | 61.8688 | 61.9093
1122.5938 | 123.262 | -61.0977 | 62.0453 | -1.824 | -7.243 | -7.2233 | -7.1995 | -7.1649 | -7.2673 | -7.1452 | 62.0224 | 0.13416 | 61.9216 | -0.046838 | 0.039079 | 61.1908 | 0.003143 | 60.9827 | 59.2738 | 53.8547 | 53.8744 | 53.8982 | 53.9329 | 53.8304 | 53.9526 | 123.1201 | 61.2319 | 123.0193 | 61.0509 | 61.1368 | 122.2885 | 61.1009 | 122.0804 | 61.9833 | 62.0193 | 61.8825 | 61.9185
1123.5938 | 123.317 | -61.084 | 62.0224 | -1.8102 | -7.1102 | -7.0997 | -7.0759 | -7.0413 | -7.1483 | -7.0215 | 62.027 | 0.12958 | 61.9124 | -0.042259 | 0.048236 | 61.1999 | 0.007721 | 60.9827 | 59.2738 | 53.9738 | 53.9843 | 54.0081 | 54.0427 | 53.9357 | 54.0624 | 123.111 | 61.2136 | 122.9964 | 61.0417 | 61.1322 | 122.2839 | 61.0917 | 122.0667 | 61.9788 | 62.0193 | 61.8642 | 61.9047
1124.5938 | 123.2803 | -61.1114 | 62.059 | -1.7919 | -6.9683 | -6.944 | -6.9157 | -6.8993 | -6.9926 | -6.8796 | 62.027 | 0.12958 | 61.9124 | -0.042259 | 0.043657 | 61.2136 | 0.003143 | 60.9964 | 59.3195 | 54.1432 | 54.1674 | 54.1958 | 54.2121 | 54.1188 | 54.2318 | 123.1384 | 61.241 | 123.0239 | 61.0692 | 61.1551 | 122.3251 | 61.1146 | 122.1079 | 61.9833 | 62.0239 | 61.8688 | 61.9093
1125.5938 | 123.3398 | -61.1069 | 62.027 | -1.8148 | -6.9179 | -6.8982 | -6.879 | -6.849 | -6.9514 | -6.8155 | 62.0224 | 0.13874 | 61.9124 | -0.033101 | 0.043657 | 61.2091 | 0.012299 | 60.9964 | 59.2921 | 54.189 | 54.2087 | 54.2278 | 54.2579 | 54.1555 | 54.2914 | 123.1293 | 61.2456 | 123.0193 | 61.0738 | 61.1505 | 122.3159 | 61.1192 | 122.1033 | 61.9788 | 62.0101 | 61.8688 | 61.9001
1126.5938 | 123.3032 | -61.1114 | 61.9995 | -1.7644 | -6.6615 | -6.6464 | -6.6135 | -6.5926 | -6.695 | -6.5683 | 61.9858 | 0.13874 | 61.8758 | -0.028522 | 0.043657 | 61.2503 | 0.003143 | 61.0285 | 59.347 | 54.45 | 54.4651 | 54.498 | 54.5188 | 54.4164 | 54.5431 | 123.0972 | 61.2502 | 122.9873 | 61.0829 | 61.1551 | 122.3617 | 61.1146 | 122.1399 | 61.9421 | 61.9826 | 61.8322 | 61.8727
1127.5938 | 123.2437 | -61.116 | 62.027 | -1.7919 | -6.634 | -6.6052 | -6.5814 | -6.5606 | -6.6584 | -6.5317 | 61.9995 | 0.12501 | 61.8987 | -0.03768 | 0.034501 | 61.2136 | -0.006014 | 61.0101 | 59.3241 | 54.482 | 54.5108 | 54.5346 | 54.5555 | 54.4576 | 54.5844 | 123.1156 | 61.241 | 123.0147 | 61.0783 | 61.1505 | 122.3297 | 61.11 | 122.1262 | 61.965 | 62.0055 | 61.8642 | 61.9047
1128.5938 | 123.3627 | -61.0977 | 61.9904 | -1.8011 | -6.6249 | -6.596 | -6.5768 | -6.556 | -6.6446 | -6.5225 | 61.9949 | 0.14332 | 61.8941 | -0.042259 | 0.043657 | 61.2182 | 0.003143 | 61.0101 | 59.2966 | 54.4729 | 54.5017 | 54.5209 | 54.5417 | 54.4531 | 54.5752 | 123.0927 | 61.241 | 122.9919 | 61.0555 | 61.1414 | 122.3159 | 61.1009 | 122.1079 | 61.9513 | 61.9918 | 61.8505 | 61.891
1129.5938 | 123.3582 | -61.1114 | 61.9629 | -1.8606 | -6.7531 | -6.7288 | -6.7142 | -6.6796 | -6.782 | -6.6553 | 62.0041 | 0.13874 | 61.8804 | -0.033101 | 0.043657 | 61.2274 | 0.007721 | 61.001 | 59.2509 | 54.3584 | 54.3826 | 54.3973 | 54.4318 | 54.3295 | 54.4562 | 123.1156 | 61.2502 | 122.9918 | 61.0783 | 61.1551 | 122.3388 | 61.1192 | 122.1124 | 61.9604 | 61.9964 | 61.8367 | 61.8727
1130.5938 | 123.2346 | -61.1206 | 62.0178 | -1.9064 | -6.7989 | -6.7746 | -6.7554 | -6.73 | -6.8232 | -6.6965 | 61.9949 | 0.12043 | 61.885 | -0.03768 | 0.052814 | 61.2274 | 0.007721 | 61.0101 | 59.2142 | 54.3217 | 54.346 | 54.3652 | 54.3906 | 54.2974 | 54.4241 | 123.1156 | 61.241 | 123.0056 | 61.0829 | 61.1734 | 122.348 | 61.1283 | 122.1307 | 61.9421 | 61.9872 | 61.8322 | 61.8773
1131.5938 | 123.2758 | -61.1206 | 62.0224 | -1.9293 | -6.8126 | -6.7883 | -6.7646 | -6.7437 | -6.8324 | -6.7331 | 62.0224 | 0.14332 | 61.917 | -0.033101 | 0.048236 | 61.2045 | -0.001436 | 60.9873 | 59.1913 | 54.308 | 54.3323 | 54.356 | 54.3769 | 54.2882 | 54.3875 | 123.143 | 61.2639 | 123.0376 | 61.0875 | 61.1688 | 122.3251 | 61.1192 | 122.1079 | 61.9742 | 62.0239 | 61.8688 | 61.9185
1132.5938 | 123.2574 | -61.1252 | 61.9675 | -1.8606 | -6.4417 | -6.422 | -6.4029 | -6.3775 | -6.4798 | -6.3577 | 61.9675 | 0.13874 | 61.8621 | -0.028522 | 0.048236 | 61.264 | 0.012299 | 61.033 | 59.2646 | 54.6835 | 54.7031 | 54.7223 | 54.7477 | 54.6454 | 54.7675 | 123.0927 | 61.2639 | 122.9873 | 61.0967 | 61.1734 | 122.3892 | 61.1375 | 122.1582 | 61.9192 | 61.9552 | 61.8138 | 61.8498
1133.5938 | 123.2941 | -61.1389 | 62.027 | -1.9064 | -6.5653 | -6.5502 | -6.5356 | -6.5011 | -6.5989 | -6.4813 | 61.9812 | 0.13416 | 61.8667 | -0.03768 | 0.043657 | 61.2365 | -0.001436 | 61.0239 | 59.2325 | 54.5736 | 54.5887 | 54.6033 | 54.6379 | 54.5401 | 54.6576 | 123.1201 | 61.2731 | 123.0056 | 61.1012 | 61.1826 | 122.3755 | 61.1375 | 122.1628 | 61.9376 | 61.9826 | 61.823 | 61.8681
1134.5938 | 123.3215 | -61.1023 | 61.9034 | -1.9384 | -6.6111 | -6.596 | -6.5723 | -6.5423 | -6.6401 | -6.5225 | 61.9995 | 0.13416 | 61.8941 | -0.033101 | 0.048236 | 61.2136 | 0.003143 | 61.0101 | 59.1639 | 54.4912 | 54.5063 | 54.53 | 54.56 | 54.4622 | 54.5798 | 123.1018 | 61.2365 | 122.9964 | 61.0692 | 61.1505 | 122.3159 | 61.1054 | 122.1124 | 61.9513 | 61.9964 | 61.8459 | 61.891
1135.5938 | 123.3582 | -61.1435 | 61.9492 | -1.8926 | -6.3639 | -6.3488 | -6.3204 | -6.3088 | -6.3928 | -6.2799 | 61.9766 | 0.12958 | 61.8621 | -0.033101 | 0.039079 | 61.2411 | 0.003143 | 61.033 | 59.2509 | 54.7796 | 54.7947 | 54.823 | 54.8347 | 54.7507 | 54.8636 | 123.1201 | 61.2731 | 123.0056 | 61.1104 | 61.1826 | 122.3846 | 61.1466 | 122.1765 | 61.9376 | 61.9735 | 61.823 | 61.8589
1136.5938 | 123.3902 | -61.116 | 61.9537 | -1.8881 | -6.2586 | -6.2389 | -6.2151 | -6.1898 | -6.283 | -6.1654 | 61.9766 | 0.13874 | 61.8621 | -0.028522 | 0.043657 | 61.2503 | 0.003143 | 61.0376 | 59.228 | 54.8575 | 54.8771 | 54.9009 | 54.9263 | 54.8331 | 54.9506 | 123.0927 | 61.2548 | 122.9781 | 61.0875 | 61.1597 | 122.3663 | 61.1192 | 122.1536 | 61.933 | 61.9735 | 61.8184 | 61.8589
1137.5938 | 123.262 | -61.116 | 62.0178 | -1.9338 | -6.3547 | -6.3442 | -6.3159 | -6.2951 | -6.3928 | -6.2707 | 61.9995 | 0.12958 | 61.885 | -0.042259 | 0.043657 | 61.2274 | 0.012299 | 61.001 | 59.1822 | 54.7613 | 54.7718 | 54.8002 | 54.821 | 54.7232 | 54.8453 | 123.1156 | 61.2456 | 123.001 | 61.0738 | 61.1597 | 122.3434 | 61.1283 | 122.117 | 61.9559 | 61.9872 | 61.8413 | 61.8727
1138.5938 | 123.3353 | -61.1069 | 61.9858 | -1.9384 | -6.286 | -6.2664 | -6.2472 | -6.231 | -6.3104 | -6.202 | 61.9812 | 0.13416 | 61.8667 | -0.03768 | 0.039079 | 61.232 | 0.003143 | 61.0101 | 59.1684 | 54.8208 | 54.8405 | 54.8597 | 54.8759 | 54.7964 | 54.9048 | 123.0881 | 61.241 | 122.9735 | 61.0692 | 61.146 | 122.3388 | 61.11 | 122.117 | 61.9421 | 61.9781 | 61.8276 | 61.8635
1139.5938 | 123.3398 | -61.0931 | 61.9171 | -1.9705 | -6.3272 | -6.3076 | -6.2884 | -6.2538 | -6.3516 | -6.2295 | 61.9858 | 0.13416 | 61.8758 | -0.03768 | 0.029923 | 61.232 | 0.003143 | 61.0056 | 59.1227 | 54.7659 | 54.7856 | 54.8047 | 54.8393 | 54.7415 | 54.8636 | 123.0789 | 61.2273 | 122.969 | 61.0555 | 61.1231 | 122.3251 | 61.0963 | 122.0987 | 61.9559 | 61.9826 | 61.8459 | 61.8727
1140.5938 | 123.3398 | -61.0977 | 61.9308 | -2.062 | -6.5516 | -6.5365 | -6.5173 | -6.4919 | -6.5805 | -6.4538 | 61.9812 | 0.12501 | 61.8667 | -0.03768 | 0.039079 | 61.2274 | 0.003143 | 61.0056 | 59.0357 | 54.5461 | 54.5612 | 54.5804 | 54.6058 | 54.5172 | 54.6439 | 123.0789 | 61.2227 | 122.9644 | 61.06 | 61.1368 | 122.3251 | 61.1009 | 122.1033 | 61.9421 | 61.9781 | 61.8276 | 61.8635
1141.5938 | 123.3765 | -61.0977 | 61.9766 | -2.0987 | -6.602 | -6.5777 | -6.5631 | -6.524 | -6.6263 | -6.5042 | 61.9995 | 0.1479 | 61.8941 | -0.03768 | 0.043657 | 61.2136 | 0.012299 | 61.0056 | 58.9991 | 54.4958 | 54.52 | 54.5346 | 54.5738 | 54.4714 | 54.5935 | 123.0972 | 61.2456 | 122.9919 | 61.06 | 61.1414 | 122.3114 | 61.11 | 122.1033 | 61.9559 | 61.9872 | 61.8505 | 61.8818
1142.5938 | 123.3673 | -61.1252 | 61.9446 | -2.1261 | -6.602 | -6.5915 | -6.5814 | -6.5423 | -6.6401 | -6.5134 | 61.9949 | 0.13874 | 61.8667 | -0.033101 | 0.048236 | 61.2274 | 0.003143 | 60.9918 | 58.999 | 54.5232 | 54.5337 | 54.5438 | 54.5829 | 54.4851 | 54.6118 | 123.1201 | 61.2639 | 122.9918 | 61.0921 | 61.1734 | 122.3526 | 61.1283 | 122.117 | 61.9467 | 61.9918 | 61.8184 | 61.8635
1143.5938 | 123.2483 | -61.1114 | 62.0087 | -2.2543 | -6.9271 | -6.9165 | -6.8882 | -6.8627 | -6.9651 | -6.8338 | 61.9995 | 0.13416 | 61.8987 | -0.033101 | 0.039079 | 61.2136 | 0.007721 | 60.9918 | 58.8571 | 54.1844 | 54.1949 | 54.2233 | 54.2487 | 54.1463 | 54.2776 | 123.111 | 61.2456 | 123.0102 | 61.0783 | 61.1505 | 122.3251 | 61.1192 | 122.1033 | 61.9604 | 61.9918 | 61.8596 | 61.891
1144.5938 | 123.2391 | -61.116 | 62.0499 | -2.2269 | -6.7851 | -6.7654 | -6.7462 | -6.7208 | -6.8232 | -6.6873 | 61.9904 | 0.14332 | 61.885 | -0.033101 | 0.039079 | 61.2182 | 0.007721 | 61.0101 | 58.8892 | 54.3309 | 54.3506 | 54.3698 | 54.3952 | 54.2928 | 54.4287 | 123.1064 | 61.2593 | 123.001 | 61.0829 | 61.1551 | 122.3343 | 61.1237 | 122.1262 | 61.9513 | 61.9827 | 61.8459 | 61.8773
1145.5938 | 123.3353 | -61.0703 | 61.9812 | -2.2543 | -6.8172 | -6.7883 | -6.7691 | -6.7528 | -6.8415 | -6.7148 | 62.0133 | 0.12958 | 61.8941 | -0.03768 | 0.052814 | 61.2045 | 0.016878 | 60.9873 | 58.8159 | 54.2531 | 54.2819 | 54.3011 | 54.3174 | 54.2287 | 54.3554 | 123.0835 | 61.1998 | 122.9644 | 61.0326 | 61.1231 | 122.2747 | 61.0871 | 122.0575 | 61.9604 | 61.9964 | 61.8413 | 61.8773
1146.5938 | 123.2986 | -61.0382 | 61.9583 | -2.2955 | -6.8767 | -6.857 | -6.8424 | -6.8078 | -6.9148 | -6.7835 | 62.0041 | 0.14332 | 61.8941 | -0.023943 | 0.048236 | 61.2136 | -0.001436 | 60.9918 | 58.7427 | 54.1615 | 54.1812 | 54.1958 | 54.2304 | 54.1234 | 54.2547 | 123.0423 | 61.1815 | 122.9323 | 61.0143 | 61.0864 | 122.2519 | 61.0368 | 122.03 | 61.9559 | 62.0055 | 61.8459 | 61.8956
1147.5938 | 123.2117 | -61.1023 | 61.9995 | -2.323 | -6.8904 | -6.8891 | -6.8561 | -6.8307 | -6.9285 | -6.8064 | 61.9858 | 0.13416 | 61.8667 | -0.028522 | 0.043657 | 61.2274 | 0.007721 | 61.0056 | 58.7793 | 54.2119 | 54.2132 | 54.2462 | 54.2716 | 54.1738 | 54.2959 | 123.0881 | 61.2365 | 122.969 | 61.0738 | 61.146 | 122.3297 | 61.11 | 122.1079 | 61.9421 | 61.9781 | 61.823 | 61.8589
1148.5938 | 123.2849 | -61.1069 | 61.9446 | -2.4054 | -7.0553 | -7.0539 | -7.0164 | -6.9909 | -7.0933 | -6.962 | 61.9766 | 0.12958 | 61.8712 | -0.042259 | 0.034501 | 61.2182 | 0.007721 | 61.001 | 58.7015 | 54.0516 | 54.053 | 54.0905 | 54.116 | 54.0135 | 54.1448 | 123.0835 | 61.2365 | 122.9781 | 61.0646 | 61.1414 | 122.3251 | 61.1146 | 122.1079 | 61.9421 | 61.9689 | 61.8367 | 61.8635
1149.5938 | 123.23 | -61.084 | 62.0636 | -2.5153 | -7.3117 | -7.292 | -7.2728 | -7.2427 | -7.3406 | -7.2138 | 62.0224 | 0.13416 | 61.9033 | -0.03768 | 0.039079 | 61.1862 | 0.007721 | 60.9689 | 58.5687 | 53.7723 | 53.792 | 53.8112 | 53.8413 | 53.7434 | 53.8702 | 123.1064 | 61.2181 | 122.9873 | 61.0463 | 61.1231 | 122.2702 | 61.0917 | 122.0529 | 61.9833 | 62.0147 | 61.8642 | 61.8956
1150.5938 | 123.3353 | -61.1023 | 61.9446 | -2.4375 | -7.037 | -7.0127 | -7.0026 | -6.9634 | -7.0704 | -6.9437 | 61.9812 | 0.13874 | 61.8712 | -0.033101 | 0.034501 | 61.2136 | 0.003143 | 60.9964 | 58.6648 | 54.0653 | 54.0896 | 54.0997 | 54.1389 | 54.0319 | 54.1586 | 123.0835 | 61.241 | 122.9735 | 61.0692 | 61.1368 | 122.3159 | 61.1054 | 122.0987 | 61.9467 | 61.9781 | 61.8367 | 61.8681
1151.5938 | 123.3307 | -61.0657 | 61.9766 | -2.41 | -6.895 | -6.8799 | -6.8607 | -6.8353 | -6.9377 | -6.8109 | 61.9995 | 0.12958 | 61.8896 | -0.03768 | 0.043657 | 61.1953 | 0.007721 | 60.9781 | 58.6557 | 54.1707 | 54.1858 | 54.205 | 54.2304 | 54.128 | 54.2547 | 123.0652 | 61.1953 | 122.9552 | 61.028 | 61.1093 | 122.261 | 61.0734 | 122.0438 | 61.9559 | 61.9918 | 61.8459 | 61.8818
1152.5938 | 123.3078 | -61.0748 | 61.972 | -2.3963 | -6.7805 | -6.7654 | -6.7371 | -6.7162 | -6.8186 | -6.6965 | 61.9949 | 0.13874 | 61.885 | -0.03768 | 0.034501 | 61.1953 | 0.007721 | 60.9827 | 58.6786 | 54.2943 | 54.3094 | 54.3377 | 54.3586 | 54.2562 | 54.3783 | 123.0698 | 61.2136 | 122.9598 | 61.0371 | 61.1093 | 122.2702 | 61.0825 | 122.0575 | 61.9604 | 61.9872 | 61.8505 | 61.8773
1153.5938 | 123.3124 | -61.1114 | 61.9537 | -2.4649 | -6.9179 | -6.912 | -6.8882 | -6.8536 | -6.9606 | -6.8293 | 61.9629 | 0.13874 | 61.8484 | -0.033101 | 0.034501 | 61.2274 | 0.007721 | 61.0101 | 58.6465 | 54.1935 | 54.1995 | 54.2233 | 54.2579 | 54.1509 | 54.2822 | 123.0743 | 61.2502 | 122.9598 | 61.0783 | 61.146 | 122.3388 | 61.1192 | 122.1216 | 61.9284 | 61.9552 | 61.8139 | 61.8406
1154.5938 | 123.3719 | -61.084 | 61.9629 | -2.497 | -6.9271 | -6.9165 | -6.8928 | -6.8765 | -6.9606 | -6.8338 | 61.9721 | 0.13416 | 61.8529 | -0.033101 | 0.043657 | 61.2228 | 0.003143 | 60.9964 | 58.587 | 54.1569 | 54.1675 | 54.1912 | 54.2075 | 54.1234 | 54.2501 | 123.056 | 61.2181 | 122.9369 | 61.0509 | 61.1276 | 122.3068 | 61.0871 | 122.0804 | 61.9284 | 61.9689 | 61.8093 | 61.8498
1155.6094 | 123.317 | -61.084 | 61.9354 | -2.5473 | -7.0461 | -7.031 | -7.0072 | -6.9863 | -7.0796 | -6.9529 | 61.9721 | 0.12958 | 61.8621 | -0.03768 | 0.039079 | 61.2091 | 0.012299 | 60.9827 | 58.5366 | 54.0379 | 54.053 | 54.0768 | 54.0977 | 54.0044 | 54.1311 | 123.056 | 61.2136 | 122.9461 | 61.0463 | 61.1231 | 122.2931 | 61.0963 | 122.0667 | 61.933 | 61.9598 | 61.823 | 61.8498
1156.5938 | 123.2346 | -61.0519 | 62.0178 | -2.6023 | -7.1194 | -7.118 | -7.0851 | -7.0641 | -7.1712 | -7.0353 | 62.0087 | 0.13874 | 61.9033 | -0.033101 | 0.043657 | 61.177 | 0.003143 | 60.9598 | 58.4497 | 53.9326 | 53.9339 | 53.9669 | 53.9878 | 53.8808 | 54.0167 | 123.0606 | 61.1907 | 122.9552 | 61.0188 | 61.0956 | 122.229 | 61.0551 | 122.0117 | 61.965 | 62.0055 | 61.8596 | 61.9001
1157.5938 | 123.3124 | -61.0748 | 61.9766 | -2.671 | -7.243 | -7.2279 | -7.2133 | -7.1878 | -7.281 | -7.1635 | 61.9949 | 0.13416 | 61.8712 | -0.03768 | 0.039079 | 61.1862 | 0.003143 | 60.9552 | 58.4039 | 53.8318 | 53.847 | 53.8616 | 53.8871 | 53.7938 | 53.9114 | 123.0698 | 61.209 | 122.9461 | 61.0371 | 61.1139 | 122.261 | 61.078 | 122.03 | 61.9559 | 61.9918 | 61.8322 | 61.8681
1158.5938 | 123.3307 | -61.0886 | 61.9217 | -2.6023 | -7.0278 | -7.0127 | -6.9889 | -6.9772 | -7.0659 | -6.93 | 61.9766 | 0.13416 | 61.8667 | -0.03768 | 0.039079 | 61.1999 | -0.001436 | 60.9781 | 58.4863 | 54.0608 | 54.0759 | 54.0997 | 54.1114 | 54.0227 | 54.1586 | 123.0652 | 61.2227 | 122.9552 | 61.0509 | 61.1276 | 122.2885 | 61.0871 | 122.0667 | 61.9376 | 61.9781 | 61.8276 | 61.8681
1159.5938 | 123.2162 | -61.0931 | 62.0361 | -2.6389 | -7.0415 | -7.0264 | -6.9981 | -6.9863 | -7.0796 | -6.9483 | 61.9812 | 0.14332 | 61.8667 | -0.033101 | 0.043657 | 61.1953 | 0.007721 | 60.9781 | 58.4542 | 54.0516 | 54.0667 | 54.0951 | 54.1068 | 54.0135 | 54.1448 | 123.0744 | 61.2365 | 122.9598 | 61.06 | 61.1368 | 122.2885 | 61.1009 | 122.0712 | 61.9376 | 61.9735 | 61.823 | 61.8589
1160.5938 | 123.2895 | -61.0565 | 61.9537 | -2.5473 | -6.7714 | -6.7609 | -6.7417 | -6.7162 | -6.8095 | -6.6873 | 61.9766 | 0.13416 | 61.8621 | -0.033101 | 0.034501 | 61.1999 | -0.001436 | 60.9644 | 58.5092 | 54.2851 | 54.2957 | 54.3148 | 54.3403 | 54.2471 | 54.3692 | 123.0332 | 61.1907 | 122.9186 | 61.0234 | 61.091 | 122.2564 | 61.0551 | 122.0209 | 61.9421 | 61.9781 | 61.8276 | 61.8635
1161.5938 | 123.2758 | -61.0657 | 61.9537 | -2.6206 | -6.8996 | -6.8936 | -6.8561 | -6.8444 | -6.9377 | -6.8018 | 61.9812 | 0.14332 | 61.8575 | -0.03768 | 0.029923 | 61.1953 | 0.003143 | 60.9689 | 58.4451 | 54.1661 | 54.172 | 54.2095 | 54.2213 | 54.128 | 54.2639 | 123.0469 | 61.209 | 122.9232 | 61.028 | 61.0956 | 122.261 | 61.0688 | 122.0346 | 61.9513 | 61.9781 | 61.8276 | 61.8544
1162.5938 | 123.2941 | -61.084 | 61.9217 | -2.6389 | -6.8859 | -6.8662 | -6.8516 | -6.8398 | -6.9377 | -6.7972 | 61.9766 | 0.12043 | 61.8575 | -0.033101 | 0.039079 | 61.1862 | 0.007721 | 60.9552 | 58.4451 | 54.1981 | 54.2178 | 54.2324 | 54.2442 | 54.1463 | 54.2868 | 123.0606 | 61.2044 | 122.9415 | 61.0509 | 61.1231 | 122.2702 | 61.0917 | 122.0392 | 61.9376 | 61.9689 | 61.8184 | 61.8498
1163.5938 | 123.2803 | -61.0931 | 61.908 | -2.6664 | -6.9087 | -6.9028 | -6.8699 | -6.8536 | -6.9468 | -6.8155 | 61.9583 | 0.13874 | 61.8346 | -0.03768 | 0.034501 | 61.2045 | 0.007721 | 60.9689 | 58.4268 | 54.1844 | 54.1903 | 54.2233 | 54.2396 | 54.1463 | 54.2776 | 123.0515 | 61.2319 | 122.9278 | 61.0555 | 61.1276 | 122.2976 | 61.1009 | 122.0621 | 61.9238 | 61.9506 | 61.8001 | 61.8269
1164.5938 | 123.2254 | -61.0336 | 61.972 | -2.6984 | -6.9179 | -6.8936 | -6.8744 | -6.8581 | -6.9468 | -6.8155 | 61.9629 | 0.12958 | 61.8209 | -0.028522 | 0.043657 | 61.1816 | 0.003143 | 60.9369 | 58.3352 | 54.1157 | 54.14 | 54.1592 | 54.1755 | 54.0868 | 54.2181 | 122.9965 | 61.1632 | 122.8545 | 61.0051 | 61.0773 | 122.2152 | 61.0368 | 121.9705 | 61.9192 | 61.9598 | 61.7772 | 61.8177
1165.5938 | 123.2941 | -61.1847 | 61.7981 | -1.8514 | -4.83 | -4.7921 | -4.7912 | -4.7385 | -4.8224 | -4.7416 | 61.8576 | 0.1479 | 61.7385 | -0.03768 | 0.039079 | 61.2732 | 0.007721 | 61.033 | 59.3333 | 56.3547 | 56.3926 | 56.3935 | 56.4461 | 56.3622 | 56.4431 | 123.0423 | 61.3326 | 122.9232 | 61.147 | 61.2238 | 122.4579 | 61.1924 | 122.2177 | 61.8185 | 61.8499 | 61.6994 | 61.7308
1166.5938 | 123.2025 | -61.203 | 61.8118 | -2.7854 | -6.9774 | -6.9852 | -6.9477 | -6.9451 | -7.0384 | -6.8842 | 61.9446 | 0.13416 | 61.7888 | -0.033101 | 0.043657 | 61.1496 | -0.006014 | 60.9232 | 58.4176 | 54.2256 | 54.2178 | 54.2553 | 54.2579 | 54.1646 | 54.3188 | 123.1476 | 61.3372 | 122.9918 | 61.1699 | 61.2467 | 122.3526 | 61.197 | 122.1262 | 61.9009 | 61.9506 | 61.7452 | 61.7948
1167.5938 | 123.2895 | -61.1664 | 61.7569 | -1.9155 | -4.8437 | -4.8424 | -4.8004 | -4.7752 | -4.8591 | -4.7462 | 61.8439 | 0.13874 | 61.7247 | -0.033101 | 0.043657 | 61.2915 | 0.003143 | 61.0513 | 59.2508 | 56.3227 | 56.324 | 56.366 | 56.3912 | 56.3073 | 56.4202 | 123.0102 | 61.3051 | 122.8911 | 61.1333 | 61.21 | 122.4579 | 61.1695 | 122.2177 | 61.8002 | 61.8407 | 61.6811 | 61.7216
1168.5938 | 123.1522 | -61.1298 | 61.8942 | -2.0575 | -5.1413 | -5.14 | -5.1071 | -5.0773 | -5.1704 | -5.0529 | 61.8896 | 0.14332 | 61.7705 | -0.03768 | 0.039079 | 61.2411 | 0.003143 | 61.0101 | 59.0723 | 55.9884 | 55.9897 | 56.0226 | 56.0524 | 55.9594 | 56.0768 | 123.0194 | 61.2731 | 122.9003 | 61.0921 | 61.1688 | 122.3709 | 61.1329 | 122.1399 | 61.8506 | 61.8865 | 61.7314 | 61.7674
1169.5938 | 123.1796 | -61.1114 | 61.9263 | -2.204 | -5.4573 | -5.4422 | -5.4093 | -5.3886 | -5.4817 | -5.3688 | 61.8942 | 0.14332 | 61.7751 | -0.028522 | 0.043657 | 61.2365 | 0.007721 | 61.0101 | 58.9075 | 55.6542 | 55.6692 | 55.7021 | 55.7228 | 55.6297 | 55.7426 | 123.0057 | 61.2548 | 122.8865 | 61.0829 | 61.1551 | 122.348 | 61.1192 | 122.1216 | 61.8506 | 61.8865 | 61.7314 | 61.7674
1170.5938 | 123.1384 | -61.1343 | 61.8942 | -2.3001 | -5.6221 | -5.6162 | -5.5696 | -5.5626 | -5.6511 | -5.5291 | 61.9034 | 0.13416 | 61.7888 | -0.033101 | 0.043657 | 61.2182 | 0.007721 | 60.9918 | 58.8342 | 55.5122 | 55.5181 | 55.5648 | 55.5718 | 55.4832 | 55.6053 | 123.0377 | 61.2685 | 122.9232 | 61.1012 | 61.178 | 122.3526 | 61.1421 | 122.1262 | 61.8597 | 61.8957 | 61.7452 | 61.7811
1171.5938 | 123.1979 | -61.1252 | 61.8301 | -2.3963 | -5.8144 | -5.8177 | -5.7802 | -5.7594 | -5.848 | -5.7305 | 61.9125 | 0.15706 | 61.7751 | -0.03768 | 0.039079 | 61.232 | 0.003143 | 61.0056 | 58.7289 | 55.3108 | 55.3075 | 55.345 | 55.3658 | 55.2772 | 55.3947 | 123.0377 | 61.2822 | 122.9003 | 61.0875 | 61.1643 | 122.3571 | 61.1283 | 122.1307 | 61.8735 | 61.9094 | 61.736 | 61.772
1172.5938 | 123.2025 | -61.0931 | 61.9034 | -2.5748 | -6.1899 | -6.184 | -6.1602 | -6.1257 | -6.2189 | -6.0968 | 61.9217 | 0.14332 | 61.8026 | -0.033101 | 0.039079 | 61.2045 | -0.001436 | 60.9735 | 58.5183 | 54.9033 | 54.9092 | 54.9329 | 54.9675 | 54.8743 | 54.9964 | 123.0148 | 61.2365 | 122.8957 | 61.06 | 61.1322 | 122.2976 | 61.0917 | 122.0667 | 61.8826 | 61.9231 | 61.7635 | 61.804
1173.5938 | 123.1567 | -61.0977 | 61.9308 | -2.703 | -6.46 | -6.4587 | -6.4303 | -6.4003 | -6.5027 | -6.3714 | 61.9308 | 0.12958 | 61.8071 | -0.033101 | 0.043657 | 61.1953 | 0.003143 | 60.9644 | 58.3947 | 54.6377 | 54.639 | 54.6674 | 54.6974 | 54.595 | 54.7263 | 123.0286 | 61.2273 | 122.9049 | 61.0646 | 61.1414 | 122.2931 | 61.1009 | 122.0621 | 61.8872 | 61.9277 | 61.7635 | 61.804
1174.5938 | 123.2162 | -61.0931 | 61.9629 | -2.7946 | -6.634 | -6.6281 | -6.5997 | -6.5652 | -6.6675 | -6.5408 | 61.9446 | 0.13874 | 61.8209 | -0.033101 | 0.039079 | 61.1724 | 0.007721 | 60.9506 | 58.2986 | 54.4591 | 54.4651 | 54.4934 | 54.528 | 54.4256 | 54.5523 | 123.0377 | 61.2319 | 122.914 | 61.06 | 61.1322 | 122.2656 | 61.1009 | 122.0438 | 61.9055 | 61.9369 | 61.7818 | 61.8132
1175.5938 | 123.1659 | -61.0794 | 61.9446 | -2.8816 | -6.7714 | -6.77 | -6.7417 | -6.7162 | -6.8186 | -6.6873 | 61.9583 | 0.1479 | 61.8346 | -0.033101 | 0.039079 | 61.1633 | -0.001436 | 60.9277 | 58.1978 | 54.308 | 54.3094 | 54.3377 | 54.3632 | 54.2608 | 54.3921 | 123.0377 | 61.2273 | 122.914 | 61.0463 | 61.1185 | 122.2427 | 61.078 | 122.0071 | 61.9192 | 61.9598 | 61.7955 | 61.8361
1176.5938 | 123.1659 | -61.0611 | 61.9537 | -2.9365 | -6.8538 | -6.8479 | -6.8241 | -6.7849 | -6.8873 | -6.756 | 61.9537 | 0.1479 | 61.8346 | -0.028522 | 0.048236 | 61.1724 | 0.007721 | 60.9415 | 58.1246 | 54.2073 | 54.2132 | 54.237 | 54.2762 | 54.1738 | 54.3051 | 123.0148 | 61.209 | 122.8957 | 61.0326 | 61.1093 | 122.2335 | 61.0688 | 122.0026 | 61.9055 | 61.946 | 61.7864 | 61.8269
1177.5938 | 123.1338 | -61.0428 | 61.9858 | -3.0784 | -7.124 | -7.1134 | -7.0896 | -7.0641 | -7.1574 | -7.0307 | 61.9629 | 0.13874 | 61.8346 | -0.033101 | 0.048236 | 61.1541 | 0.003143 | 60.9232 | 57.9643 | 53.9188 | 53.9294 | 53.9532 | 53.9786 | 53.8854 | 54.0121 | 123.0057 | 61.1815 | 122.8774 | 61.0097 | 61.091 | 122.1969 | 61.0459 | 121.9659 | 61.9147 | 61.9598 | 61.7864 | 61.8315
1178.5938 | 123.1659 | -60.8185 | 62.1506 | -4.4748 | -10.2421 | -10.2498 | -10.2213 | -10.2184 | -10.3257 | -10.1576 | 62.1369 | 0.13874 | 61.9765 | -0.033101 | 0.039079 | 60.9573 | 0.007721 | 60.6988 | 56.3436 | 50.5764 | 50.5687 | 50.5972 | 50.6001 | 50.4928 | 50.6609 | 122.9554 | 60.9572 | 122.795 | 60.7854 | 60.8576 | 121.7758 | 60.8262 | 121.5173 | 62.0978 | 62.1292 | 61.9375 | 61.9688
1179.5938 | 123.1659 | -60.6903 | 62.2101 | -5.7522 | -13.0718 | -13.0656 | -13.0737 | -13.0475 | -13.1414 | -12.9915 | 62.2147 | 0.13874 | 62.0269 | -0.028522 | 0.043657 | 60.8245 | 0.003143 | 60.5203 | 54.9381 | 47.6185 | 47.6247 | 47.6166 | 47.6428 | 47.5489 | 47.6988 | 122.905 | 60.8291 | 122.7172 | 60.6618 | 60.734 | 121.5148 | 60.6935 | 121.2106 | 62.1711 | 62.2116 | 61.9832 | 62.0238
1180.5938 | 123.0881 | -60.6949 | 62.2833 | -6.1093 | -13.8319 | -13.8211 | -13.8292 | -13.8121 | -13.8968 | -13.7469 | 62.2926 | 0.1479 | 62.1688 | -0.033101 | 0.043657 | 60.7742 | -0.001436 | 60.5523 | 54.5855 | 46.863 | 46.8738 | 46.8657 | 46.8828 | 46.7981 | 46.948 | 122.9874 | 60.8428 | 122.8637 | 60.6618 | 60.7385 | 121.469 | 60.6934 | 121.2472 | 62.2489 | 62.294 | 62.1252 | 62.1703
1181.5938 | 123.1476 | -60.672 | 62.265 | -5.9903 | -13.5114 | -13.4914 | -13.5041 | -13.4824 | -13.5717 | -13.4218 | 62.2788 | 0.14332 | 62.1414 | -0.033101 | 0.039079 | 60.8016 | 0.007721 | 60.5706 | 54.6817 | 47.1606 | 47.1806 | 47.1679 | 47.1895 | 47.1002 | 47.2502 | 122.9508 | 60.8153 | 122.8134 | 60.6389 | 60.7111 | 121.4736 | 60.6797 | 121.2426 | 62.2397 | 62.2711 | 62.1023 | 62.1336
1182.5938 | 123.1064 | -60.6445 | 62.3154 | -6.0407 | -13.5343 | -13.5189 | -13.5316 | -13.5008 | -13.5855 | -13.4401 | 62.2834 | 0.14332 | 62.1688 | -0.028522 | 0.048236 | 60.7879 | 0.007721 | 60.5569 | 54.6039 | 47.1102 | 47.1257 | 47.113 | 47.1438 | 47.059 | 47.2044 | 122.9279 | 60.7879 | 122.8134 | 60.616 | 60.6928 | 121.4324 | 60.6523 | 121.2014 | 62.2352 | 62.2757 | 62.1206 | 62.1611
1183.5938 | 123.1201 | -60.6949 | 62.2833 | -6.0498 | -13.4473 | -13.4273 | -13.44 | -13.4275 | -13.5031 | -13.3532 | 62.2788 | 0.14332 | 62.1505 | -0.028522 | 0.043657 | 60.797 | 0.003143 | 60.5706 | 54.6451 | 47.2476 | 47.2676 | 47.2549 | 47.2674 | 47.1918 | 47.3417 | 122.9737 | 60.8382 | 122.8454 | 60.6664 | 60.7385 | 121.4919 | 60.698 | 121.2655 | 62.2352 | 62.2757 | 62.1069 | 62.1474
1184.5938 | 123.0835 | -60.6995 | 62.2787 | -6.1002 | -13.4702 | -13.4548 | -13.4629 | -13.4504 | -13.5397 | -13.376 | 62.2697 | 0.14332 | 62.1505 | -0.033101 | 0.039079 | 60.797 | 0.003143 | 60.5569 | 54.5993 | 47.2293 | 47.2447 | 47.2366 | 47.2491 | 47.1598 | 47.3234 | 122.9691 | 60.8428 | 122.85 | 60.6664 | 60.7385 | 121.4965 | 60.7026 | 121.2564 | 62.2306 | 62.2665 | 62.1114 | 62.1474
1185.5938 | 123.1476 | -60.6949 | 62.265 | -6.146 | -13.4839 | -13.4777 | -13.4858 | -13.4687 | -13.5443 | -13.3989 | 62.2605 | 0.15248 | 62.1414 | -0.033101 | 0.039079 | 60.8062 | 0.007721 | 60.5661 | 54.5489 | 47.211 | 47.2172 | 47.2091 | 47.2262 | 47.1506 | 47.2959 | 122.9554 | 60.8474 | 122.8362 | 60.6618 | 60.734 | 121.5011 | 60.7026 | 121.2609 | 62.2214 | 62.2528 | 62.1023 | 62.1336
1186.5938 | 123.143 | -60.6995 | 62.2696 | -6.1276 | -13.3237 | -13.322 | -13.3301 | -13.3131 | -13.3978 | -13.2433 | 62.2559 | 0.14332 | 62.1139 | -0.033101 | 0.048236 | 60.8154 | 0.003143 | 60.5844 | 54.5718 | 47.3758 | 47.3775 | 47.3693 | 47.3864 | 47.3017 | 47.4562 | 122.9554 | 60.8428 | 122.8134 | 60.6664 | 60.7477 | 121.5148 | 60.7026 | 121.2838 | 62.2077 | 62.2528 | 62.0657 | 62.1107
1187.5938 | 123.1476 | -60.6766 | 62.2971 | -6.2558 | -13.5297 | -13.528 | -13.5407 | -13.5236 | -13.6084 | -13.4401 | 62.2742 | 0.13874 | 62.1322 | -0.03768 | 0.039079 | 60.7879 | 0.003143 | 60.5477 | 54.4207 | 47.1469 | 47.1485 | 47.1358 | 47.1529 | 47.0682 | 47.2364 | 122.9508 | 60.8153 | 122.8088 | 60.6389 | 60.7157 | 121.4645 | 60.6797 | 121.2243 | 62.2352 | 62.2711 | 62.0931 | 62.1291
1188.5938 | 123.0743 | -60.7132 | 62.2375 | -6.3245 | -13.5663 | -13.5647 | -13.5819 | -13.5557 | -13.645 | -13.4768 | 62.2376 | 0.14332 | 62.1047 | -0.033101 | 0.043657 | 60.8108 | 0.007721 | 60.5752 | 54.3887 | 47.1468 | 47.1485 | 47.1313 | 47.1575 | 47.0682 | 47.2364 | 122.9508 | 60.8565 | 122.8179 | 60.6801 | 60.7569 | 121.524 | 60.7209 | 121.2884 | 62.194 | 62.2299 | 62.0611 | 62.097
1189.5938 | 123.1018 | -60.6766 | 62.2467 | -6.3749 | -13.5755 | -13.5738 | -13.5774 | -13.5648 | -13.6542 | -13.4859 | 62.233 | 0.13874 | 62.1002 | -0.033101 | 0.039079 | 60.8108 | 0.003143 | 60.5752 | 54.3017 | 47.1011 | 47.1028 | 47.0992 | 47.1117 | 47.0224 | 47.1907 | 122.9096 | 60.8153 | 122.7767 | 60.6435 | 60.7157 | 121.4874 | 60.6797 | 121.2518 | 62.194 | 62.2299 | 62.0611 | 62.097
1190.5938 | 123.056 | -60.7407 | 62.2055 | -6.233 | -13.2367 | -13.2167 | -13.2386 | -13.2123 | -13.2925 | -13.1426 | 62.2101 | 0.13874 | 62.0635 | -0.033101 | 0.039079 | 60.8154 | 0.007721 | 60.5615 | 54.5077 | 47.504 | 47.524 | 47.5021 | 47.5283 | 47.4482 | 47.5981 | 122.9508 | 60.8794 | 122.8042 | 60.7076 | 60.7797 | 121.556 | 60.7484 | 121.3021 | 62.1711 | 62.2024 | 62.0245 | 62.0558
1191.5938 | 122.9462 | -60.8276 | 61.9629 | -4.8457 | -10.3017 | -10.2726 | -10.2854 | -10.2458 | -10.3394 | -10.2034 | 62.0087 | 0.1479 | 61.6881 | -0.033101 | 0.039079 | 60.8978 | 0.003143 | 60.4791 | 55.9819 | 50.526 | 50.555 | 50.5422 | 50.5818 | 50.4882 | 50.6243 | 122.8363 | 60.9755 | 122.5157 | 60.7945 | 60.8667 | 121.7254 | 60.8308 | 121.3067 | 61.9696 | 62.0055 | 61.649 | 61.685
1192.5938 | 122.9141 | -60.8597 | 61.9125 | -4.1086 | -8.6487 | -8.6518 | -8.6372 | -8.6023 | -8.7049 | -8.5552 | 61.8988 | 0.12958 | 61.6606 | -0.033101 | 0.039079 | 60.9619 | 0.007721 | 60.6393 | 56.7511 | 52.211 | 52.2079 | 52.2225 | 52.2573 | 52.1548 | 52.3045 | 122.7585 | 60.9893 | 122.5203 | 60.8266 | 60.8988 | 121.8215 | 60.8674 | 121.499 | 61.8597 | 61.8911 | 61.6216 | 61.6529
1193.5938 | 122.8775 | -60.878 | 61.8622 | -4.1086 | -8.5617 | -8.5557 | -8.5456 | -8.5108 | -8.6179 | -8.4591 | 61.853 | 0.14332 | 61.5874 | -0.033101 | 0.043657 | 60.9664 | 0.003143 | 60.6027 | 56.7694 | 52.3163 | 52.3223 | 52.3324 | 52.3672 | 52.2601 | 52.4189 | 122.731 | 61.0213 | 122.4654 | 60.8449 | 60.9216 | 121.8444 | 60.8811 | 121.4807 | 61.8094 | 61.8499 | 61.5437 | 61.5842
1194.5938 | 122.7814 | -60.791 | 61.853 | -4.4611 | -9.2119 | -9.2196 | -9.1957 | -9.1654 | -9.2726 | -9.1138 | 61.8347 | 0.13416 | 61.4684 | -0.03768 | 0.043657 | 60.9069 | 0.003143 | 60.447 | 56.3299 | 51.5791 | 51.5714 | 51.5953 | 51.6256 | 51.5184 | 51.6773 | 122.6257 | 60.9252 | 122.2594 | 60.7533 | 60.8347 | 121.6979 | 60.7942 | 121.238 | 61.791 | 61.8316 | 61.4247 | 61.4652
1195.5938 | 122.7722 | -60.7315 | 61.8301 | -4.7129 | -9.6881 | -9.6683 | -9.6719 | -9.6187 | -9.7305 | -9.5807 | 61.8668 | 0.13874 | 61.5645 | -0.03768 | 0.048236 | 60.8199 | 0.007721 | 60.4287 | 56.0186 | 51.0434 | 51.0632 | 51.0596 | 51.1129 | 51.001 | 51.1508 | 122.5983 | 60.8702 | 122.296 | 60.6938 | 60.7797 | 121.5514 | 60.7392 | 121.1602 | 61.8185 | 61.859 | 61.5163 | 61.5568
1196.5938 | 122.7768 | -60.6583 | 61.9583 | -5.3356 | -10.8603 | -10.8496 | -10.8532 | -10.8135 | -10.9071 | -10.7711 | 61.9446 | 0.1479 | 61.7522 | -0.033101 | 0.039079 | 60.797 | 0.003143 | 60.5065 | 55.3227 | 49.798 | 49.8087 | 49.8051 | 49.8448 | 49.7511 | 49.8872 | 122.6029 | 60.8062 | 122.4105 | 60.6252 | 60.6973 | 121.4553 | 60.6614 | 121.1648 | 61.9055 | 61.9414 | 61.7131 | 61.7491
1197.5938 | 122.7173 | -60.64 | 61.9492 | -5.5508 | -11.2037 | -11.2296 | -11.2149 | -11.1706 | -11.278 | -11.1098 | 61.9171 | 0.13874 | 61.5737 | -0.033101 | 0.039079 | 60.7696 | 0.003143 | 60.3234 | 55.0892 | 49.4363 | 49.4104 | 49.4251 | 49.4694 | 49.362 | 49.5301 | 122.5571 | 60.7787 | 122.2136 | 60.6069 | 60.679 | 121.4095 | 60.6431 | 120.9634 | 61.878 | 61.914 | 61.5346 | 61.5705
1198.5938 | 122.6212 | -60.5484 | 61.9354 | -5.5279 | -11.0984 | -11.0876 | -11.0958 | -11.0424 | -11.1452 | -10.9954 | 61.8805 | 0.13874 | 61.3905 | -0.028522 | 0.043657 | 60.7009 | 0.007721 | 60.0991 | 55.0205 | 49.45 | 49.4608 | 49.4526 | 49.506 | 49.4032 | 49.553 | 122.4289 | 60.6871 | 121.9389 | 60.5199 | 60.5921 | 121.2493 | 60.5561 | 120.6475 | 61.8368 | 61.8728 | 61.3469 | 61.3828
1199.5938 | 122.5708 | -60.6583 | 61.7935 | -4.777 | -9.5461 | -9.5447 | -9.5346 | -9.4813 | -9.5886 | -9.4388 | 61.7431 | 0.14332 | 61.2761 | -0.042259 | 0.039079 | 60.7787 | 0.007721 | 60.2319 | 55.8812 | 51.1121 | 51.1136 | 51.1237 | 51.177 | 51.0697 | 51.2194 | 122.4014 | 60.8016 | 121.9343 | 60.616 | 60.6973 | 121.437 | 60.666 | 120.8901 | 61.7041 | 61.7354 | 61.237 | 61.2683
1200.5938 | 122.5342 | -60.6491 | 61.6882 | -4.658 | -9.2577 | -9.2516 | -9.2507 | -9.2066 | -9.3001 | -9.155 | 61.6745 | 0.13874 | 61.07 | -0.033101 | 0.048236 | 60.7375 | -0.001436 | 60.0945 | 55.9911 | 51.3914 | 51.3975 | 51.3984 | 51.4425 | 51.349 | 51.4941 | 122.3236 | 60.7879 | 121.7192 | 60.616 | 60.6973 | 121.3866 | 60.6477 | 120.7436 | 61.6262 | 61.6759 | 61.0218 | 61.0715
1201.5938 | 122.2733 | -60.5072 | 61.6608 | -5.5462 | -10.9381 | -10.9182 | -10.9173 | -10.8776 | -10.9804 | -10.8352 | 61.6424 | 0.14332 | 60.7221 | -0.03768 | 0.039079 | 60.6048 | 0.007721 | 59.5818 | 54.961 | 49.5691 | 49.589 | 49.5899 | 49.6296 | 49.5268 | 49.672 | 122.1496 | 60.6505 | 121.2293 | 60.4695 | 60.5463 | 121.112 | 60.5149 | 120.089 | 61.6033 | 61.6347 | 60.683 | 60.7144
1202.5938 | 121.8201 | -60.2646 | 61.4548 | -5.7385 | -11.222 | -11.2067 | -11.2194 | -11.166 | -11.2871 | -11.119 | 61.4547 | 0.14332 | 59.779 | -0.033101 | 0.043657 | 60.3759 | -0.001436 | 58.6707 | 54.5261 | 49.0426 | 49.0579 | 49.0451 | 49.0986 | 48.9775 | 49.1456 | 121.7193 | 60.4079 | 120.0436 | 60.2315 | 60.3082 | 120.6405 | 60.2632 | 118.9353 | 61.411 | 61.4561 | 59.7353 | 59.7804
1203.5938 | 122.4792 | -55.8929 | 66.4398 | -13.9384 | -26.5885 | -26.5771 | -26.649 | -26.5479 | -26.5881 | -26.5017 | 66.3949 | 0.14332 | -8.2177 | -0.042259 | 0.043657 | 55.9168 | 0.003143 | 55.6354 | 41.9546 | 29.3044 | 29.3159 | 29.244 | 29.345 | 29.3048 | 29.3913 | 122.2878 | 56.0363 | 47.6753 | 55.8507 | 55.9366 | 111.8098 | 55.8961 | 111.5283 | 66.3512 | 66.3917 | -8.2613 | -8.2208
1204.5938 | 122.438 | -56.3507 | 65.95 | -13.6225 | -25.9749 | -25.9544 | -26.0126 | -25.9299 | -25.9609 | -25.879 | 65.7264 | 0.14332 | -8.5381 | -0.03768 | 0.039079 | 56.4067 | 0.003143 | 55.9375 | 42.7282 | 30.3758 | 30.3963 | 30.3382 | 30.4208 | 30.3898 | 30.4717 | 122.0771 | 56.494 | 47.8126 | 56.313 | 56.3898 | 112.7574 | 56.3539 | 112.2882 | 65.6873 | 65.7233 | -8.5772 | -8.5413
1205.5938 | 122.5708 | -56.1035 | 66.3757 | -14.822 | -28.0629 | -28.0422 | -28.1187 | -28.0175 | -28.0395 | -27.9667 | 66.372 | 0.1479 | -8.4008 | -0.033101 | 0.039079 | 56.1869 | 0.007721 | 55.965 | 41.2815 | 28.0406 | 28.0613 | 27.9849 | 28.0861 | 28.0641 | 28.1368 | 122.4755 | 56.2514 | 47.7027 | 56.0704 | 56.1426 | 112.2904 | 56.1112 | 112.0685 | 66.3329 | 66.3643 | -8.4399 | -8.4085
1206.5938 | 122.6028 | -56.3599 | 66.1743 | -15.1013 | -28.4475 | -28.4222 | -28.4987 | -28.4066 | -28.4103 | -28.3513 | 66.1522 | 0.15248 | -8.4054 | -0.03768 | 0.048236 | 56.4387 | 0.012299 | 56.226 | 41.2586 | 27.9124 | 27.9376 | 27.8612 | 27.9533 | 27.9496 | 28.0086 | 122.5121 | 56.5123 | 47.9545 | 56.3222 | 56.4081 | 112.7986 | 56.3722 | 112.5858 | 66.104 | 66.1399 | -8.4536 | -8.4177
1207.5938 | 122.6807 | -56.8176 | 65.6891 | -15.376 | -28.7955 | -28.7748 | -28.8512 | -28.7545 | -28.772 | -28.7038 | 65.7264 | 0.13874 | -8.4054 | -0.033101 | 0.048236 | 56.8874 | 0.007721 | 56.6609 | 41.4416 | 28.0221 | 28.0428 | 27.9664 | 28.0631 | 28.0456 | 28.1139 | 122.544 | 56.9564 | 48.4123 | 56.7845 | 56.8659 | 113.705 | 56.8253 | 113.4785 | 65.6782 | 65.7187 | -8.4536 | -8.4131
1208.5938 | 122.6349 | -57.4265 | 65.1123 | -15.6919 | -29.1939 | -29.1731 | -29.2404 | -29.1574 | -29.1612 | -29.0975 | 65.1129 | 0.1479 | -8.4054 | -0.03768 | 0.039079 | 57.4688 | 0.007721 | 57.2148 | 41.7346 | 28.2326 | 28.2533 | 28.1861 | 28.2691 | 28.2653 | 28.329 | 122.5394 | 57.5744 | 49.0211 | 57.3888 | 57.4655 | 114.8952 | 57.4342 | 114.6413 | 65.0738 | 65.1052 | -8.4444 | -8.4131
1209.5938 | 122.6761 | -57.9483 | 64.595 | -16.2138 | -29.9494 | -29.9377 | -30.0096 | -29.9265 | -29.9303 | -29.8666 | 64.5818 | 0.13874 | -8.4099 | -0.03768 | 0.043657 | 58.009 | -0.001436 | 57.7596 | 41.7345 | 27.9989 | 28.0106 | 27.9387 | 28.0218 | 28.018 | 28.0817 | 122.5301 | 58.087 | 49.5384 | 57.9106 | 57.992 | 115.9573 | 57.9469 | 115.7079 | 64.5381 | 64.5832 | -8.4536 | -8.4085
1210.5938 | 122.7402 | -58.5571 | 63.9496 | -16.4794 | -30.2699 | -30.2628 | -30.3438 | -30.2515 | -30.2554 | -30.1871 | 63.9637 | 0.13874 | -8.4054 | -0.033101 | 0.043657 | 58.6454 | -0.001436 | 58.4052 | 42.0777 | 28.2873 | 28.2943 | 28.2133 | 28.3056 | 28.3017 | 28.37 | 122.5208 | 58.6959 | 50.1518 | 58.524 | 58.6008 | 117.2025 | 58.5557 | 116.9623 | 63.92 | 63.9651 | -8.449 | -8.4039
1211.5938 | 122.6898 | -58.3923 | 64.1281 | -16.8228 | -30.7186 | -30.707 | -30.7925 | -30.7093 | -30.7087 | -30.6358 | 63.8721 | 0.13874 | -8.4099 | -0.033101 | 0.039079 | 58.7506 | 0.007721 | 58.5013 | 41.5696 | 27.6737 | 27.6854 | 27.5998 | 27.683 | 27.6837 | 27.7566 | 122.2645 | 58.5311 | 49.9824 | 58.3592 | 58.4314 | 117.143 | 58.4001 | 116.8936 | 63.8331 | 63.8644 | -8.449 | -8.4177
1212.5938 | 122.6852 | -57.9712 | 64.595 | -16.9098 | -30.714 | -30.7024 | -30.7879 | -30.7001 | -30.6995 | -30.6266 | 64.1011 | 0.1479 | -8.4099 | -0.03768 | 0.043657 | 58.5034 | 0.003143 | 58.2495 | 41.0614 | 27.2572 | 27.2688 | 27.1833 | 27.271 | 27.2717 | 27.3446 | 122.0722 | 58.1191 | 49.5612 | 57.9335 | 58.0148 | 116.4746 | 57.9743 | 116.2207 | 64.0574 | 64.0979 | -8.4536 | -8.4131
1213.5938 | 122.612 | -56.9321 | 65.5838 | -16.5526 | -29.8761 | -29.8599 | -29.9363 | -29.8532 | -29.8617 | -29.7842 | 65.4517 | 0.13874 | -8.4054 | -0.028522 | 0.043657 | 57.1392 | 0.003143 | 56.8623 | 40.3794 | 27.056 | 27.0722 | 26.9957 | 27.0788 | 27.0704 | 27.1479 | 122.3838 | 57.0708 | 48.5267 | 56.9035 | 56.9757 | 114.0712 | 56.9352 | 113.7944 | 65.4081 | 65.4486 | -8.449 | -8.4085
1214.5938 | 122.6349 | -56.4331 | 66.1285 | -16.3878 | -29.3816 | -29.37 | -29.4464 | -29.3771 | -29.3809 | -29.2989 | 66.1385 | 0.1479 | -8.4099 | -0.028522 | 0.048236 | 56.4204 | 0.012299 | 56.1527 | 40.0453 | 27.0515 | 27.0631 | 26.9867 | 27.056 | 27.0522 | 27.1342 | 122.5716 | 56.581 | 48.0232 | 56.4046 | 56.4813 | 112.8535 | 56.4454 | 112.5858 | 66.0903 | 66.1262 | -8.4582 | -8.4222
1215.5938 | 122.7264 | -58.2001 | 64.3387 | -17.1845 | -30.6179 | -30.6108 | -30.6918 | -30.6086 | -30.6125 | -30.5213 | 64.3071 | 0.13416 | -8.4145 | -0.033101 | 0.048236 | 58.2608 | 0.003143 | 57.9977 | 41.0156 | 27.5822 | 27.5893 | 27.5083 | 27.5915 | 27.5876 | 27.6788 | 122.5072 | 58.3342 | 49.7856 | 58.167 | 58.2483 | 116.4609 | 58.2032 | 116.1978 | 64.2589 | 64.3039 | -8.4628 | -8.4177
1216.5938 | 122.7997 | -59.4955 | 62.9745 | -17.8987 | -31.6344 | -31.6364 | -31.7174 | -31.6386 | -31.6472 | -31.5514 | 63.1029 | 0.14332 | -8.4054 | -0.033101 | 0.039079 | 59.5015 | 0.003143 | 59.243 | 41.5969 | 27.8612 | 27.8591 | 27.7782 | 27.8569 | 27.8483 | 27.9442 | 122.5985 | 59.6389 | 51.0902 | 59.4624 | 59.5346 | 118.997 | 59.4987 | 118.7385 | 63.0639 | 63.0998 | -8.4444 | -8.4085
1217.5938 | 122.7631 | -59.6786 | 62.7914 | -18.0543 | -31.7076 | -31.7142 | -31.7952 | -31.7119 | -31.7159 | -31.6292 | 62.787 | 0.1479 | -8.4099 | -0.033101 | 0.043657 | 59.8128 | 0.007721 | 59.5451 | 41.6243 | 27.971 | 27.9644 | 27.8835 | 27.9668 | 27.9628 | 28.0494 | 122.4657 | 59.8265 | 51.2687 | 59.6455 | 59.7223 | 119.4914 | 59.6864 | 119.2238 | 62.7434 | 62.7793 | -8.4536 | -8.4177
1218.5938 | 122.6074 | -59.967 | 62.471 | -18.123 | -31.6573 | -31.6547 | -31.7448 | -31.6569 | -31.6655 | -31.5834 | 62.3841 | 0.1479 | -8.4145 | -0.028522 | 0.039079 | 60.1561 | 0.007721 | 59.8427 | 41.844 | 28.3098 | 28.3123 | 28.2222 | 28.3101 | 28.3015 | 28.3836 | 122.3512 | 60.1149 | 51.5525 | 59.9385 | 60.0061 | 120.1232 | 59.9748 | 119.8098 | 62.345 | 62.3764 | -8.4536 | -8.4222
1219.5938 | 122.5891 | -57.5226 | 64.9063 | -16.9281 | -29.4457 | -29.4295 | -29.5197 | -29.4458 | -29.4404 | -29.3676 | 64.4353 | 0.13874 | -8.4145 | -0.033101 | 0.039079 | 57.9495 | 0.007721 | 57.5628 | 40.5945 | 28.0769 | 28.0931 | 28.0029 | 28.0768 | 28.0821 | 28.155 | 121.9579 | 57.6613 | 49.1081 | 57.4895 | 57.5617 | 115.4721 | 57.5303 | 115.0854 | 64.3962 | 64.4276 | -8.4536 | -8.4222
1220.5938 | 122.3785 | -59.0378 | 63.2263 | -16.3924 | -28.2918 | -28.2986 | -28.3613 | -28.2967 | -28.3187 | -28.2139 | 63.0709 | 0.13874 | -8.4191 | -0.028522 | 0.043657 | 58.8147 | 0.016878 | 58.1305 | 42.6454 | 30.746 | 30.7392 | 30.6765 | 30.7411 | 30.719 | 30.8239 | 122.1087 | 59.1765 | 50.6187 | 59.0093 | 59.0814 | 117.8525 | 59.0547 | 117.1683 | 63.0272 | 63.054 | -8.4628 | -8.436
1221.5938 | 122.0352 | -61.6287 | 60.2921 | -15.5317 | -26.6343 | -26.6595 | -26.6856 | -26.6395 | -26.6705 | -26.5474 | 59.7378 | 0.14332 | -8.4237 | -0.033101 | 0.039079 | 61.5845 | 0.007721 | 60.6118 | 46.0971 | 34.9944 | 34.9693 | 34.9431 | 34.9892 | 34.9582 | 35.0813 | 121.3665 | 61.772 | 53.205 | 61.5956 | 61.6678 | 123.2132 | 61.6364 | 122.2406 | 59.6987 | 59.73 | -8.4628 | -8.4314
1222.5938 | 122.4838 | -61.4731 | 60.7178 | -19.5194 | -33.095 | -33.1199 | -33.1962 | -33.1036 | -33.1169 | -33.0301 | 60.5344 | 0.14332 | -8.4145 | -0.028522 | 0.043657 | 61.5982 | 0.007721 | 61.2253 | 41.9537 | 28.3781 | 28.3532 | 28.2769 | 28.3695 | 28.3562 | 28.4429 | 122.0075 | 61.6164 | 53.0586 | 61.4446 | 61.5167 | 123.0713 | 61.4808 | 122.6984 | 60.4908 | 60.5267 | -8.4582 | -8.4222
1223.5938 | 122.4792 | -60.1456 | 62.1414 | -19.0204 | -32.1655 | -32.2087 | -32.2622 | -32.1971 | -32.1966 | -32.087 | 62.5352 | 0.13416 | -8.4145 | -0.033101 | 0.043657 | 59.6617 | 0.007721 | 59.2933 | 41.1252 | 27.9801 | 27.9368 | 27.8834 | 27.9484 | 27.9489 | 28.0585 | 122.6808 | 60.2797 | 51.731 | 60.1125 | 60.1892 | 119.8073 | 60.1533 | 119.4389 | 62.4916 | 62.5275 | -8.4582 | -8.4222
1224.5938 | 122.4884 | -59.1385 | 63.2217 | -19.0708 | -32.0465 | -32.0668 | -32.1523 | -32.0735 | -32.0776 | -31.9772 | 63.2311 | 0.14332 | -8.4191 | -0.033101 | 0.048236 | 59.062 | -0.006014 | 58.7348 | 40.0677 | 27.092 | 27.0717 | 26.9862 | 27.065 | 27.0609 | 27.1613 | 122.3696 | 59.2818 | 50.7194 | 59.1054 | 59.1867 | 118.2004 | 59.1325 | 117.8733 | 63.1829 | 63.2372 | -8.4673 | -8.4131
1225.5938 | 122.525 | -59.4269 | 62.8235 | -20.1146 | -33.5987 | -33.6052 | -33.6998 | -33.6163 | -33.6114 | -33.5246 | 62.059 | 0.13874 | -8.4145 | -0.033101 | 0.048236 | 60.2431 | 0.003143 | 59.916 | 39.3123 | 25.8282 | 25.8217 | 25.727 | 25.8106 | 25.8155 | 25.9023 | 121.4859 | 59.5656 | 51.0124 | 59.3938 | 59.4751 | 119.67 | 59.43 | 119.3428 | 62.0108 | 62.0559 | -8.4628 | -8.4177
1226.5938 | 122.4243 | -57.9163 | 64.2334 | -18.8098 | -31.3138 | -31.3205 | -31.406 | -31.3228 | -31.3405 | -31.2492 | 63.3868 | 0.13416 | -8.4099 | -0.028522 | 0.039079 | 58.5034 | 0.007721 | 57.929 | 39.1065 | 26.6024 | 26.5958 | 26.5102 | 26.5935 | 26.5758 | 26.667 | 121.3031 | 58.0504 | 49.5063 | 57.8877 | 57.9553 | 116.4197 | 57.924 | 115.8453 | 63.3477 | 63.3791 | -8.449 | -8.4177
1227.5938 | 122.5662 | -58.3145 | 63.9771 | -20.5313 | -33.8734 | -33.8891 | -33.9791 | -33.8818 | -33.8906 | -33.7947 | 64.1697 | 0.1479 | -8.4237 | -0.03768 | 0.043657 | 58.215 | 0.012299 | 57.9519 | 37.7833 | 24.4411 | 24.4254 | 24.3354 | 24.4327 | 24.4239 | 24.5198 | 122.4842 | 58.4624 | 49.8908 | 58.2768 | 58.3582 | 116.5295 | 58.3268 | 116.2664 | 64.1261 | 64.1574 | -8.4673 | -8.436
1228.5938 | 122.5983 | -55.9158 | 66.4307 | -19.7392 | -32.4631 | -32.4606 | -32.5598 | -32.4718 | -32.4668 | -32.3892 | 66.317 | 0.14332 | -8.4191 | -0.033101 | 0.039079 | 56.0816 | 0.003143 | 55.7956 | 36.1766 | 23.4527 | 23.4553 | 23.356 | 23.444 | 23.4491 | 23.5266 | 122.2329 | 56.0592 | 47.4967 | 55.8827 | 55.9549 | 111.9975 | 55.919 | 111.7114 | 66.278 | 66.3139 | -8.4582 | -8.4222
1229.5938 | 122.493 | -55.6229 | 66.7099 | -19.5377 | -31.9045 | -31.9157 | -32.0104 | -31.9133 | -31.9173 | -31.8307 | 66.5918 | 0.1479 | -8.4237 | -0.03768 | 0.043657 | 55.7429 | 0.003143 | 55.4293 | 36.0851 | 23.7184 | 23.7072 | 23.6125 | 23.7096 | 23.7055 | 23.7922 | 122.2146 | 55.7708 | 47.1992 | 55.5852 | 55.6665 | 111.3657 | 55.626 | 111.0522 | 66.5481 | 66.5886 | -8.4673 | -8.4268
1230.5938 | 122.5983 | -55.4352 | 66.8747 | -19.9269 | -32.3624 | -32.369 | -32.4499 | -32.3711 | -32.366 | -32.2839 | 66.7978 | 0.14332 | -8.4099 | -0.033101 | 0.048236 | 55.5643 | -0.001436 | 55.2645 | 35.5083 | 23.0728 | 23.0662 | 22.9853 | 23.0641 | 23.0692 | 23.1513 | 122.233 | 55.5785 | 47.0252 | 55.4021 | 55.4834 | 110.9995 | 55.4337 | 110.6997 | 66.7496 | 66.7992 | -8.4582 | -8.4085
1231.5938 | 122.5891 | -55.3986 | 66.8518 | -20.0414 | -32.3395 | -32.3507 | -32.4453 | -32.3619 | -32.3569 | -32.2702 | 66.7886 | 0.14332 | -8.4237 | -0.03768 | 0.039079 | 55.5506 | 0.003143 | 55.2279 | 35.3572 | 23.0591 | 23.0479 | 22.9532 | 23.0366 | 23.0417 | 23.1284 | 122.1872 | 55.5419 | 46.9749 | 55.3609 | 55.4376 | 110.9491 | 55.4017 | 110.6265 | 66.7496 | 66.7855 | -8.4628 | -8.4268
1232.5938 | 122.5067 | -55.5405 | 66.7419 | -20.0688 | -32.1701 | -32.1858 | -32.2622 | -32.1743 | -32.1829 | -32.0825 | 66.6742 | 0.14332 | -8.4145 | -0.033101 | 0.043657 | 55.6147 | 0.012299 | 55.2645 | 35.4716 | 23.3704 | 23.3546 | 23.2783 | 23.3662 | 23.3576 | 23.458 | 122.2146 | 55.6838 | 47.1259 | 55.5074 | 55.5841 | 111.1551 | 55.5528 | 110.805 | 66.6305 | 66.6619 | -8.4582 | -8.4268
1233.5938 | 122.5388 | -55.5679 | 66.6641 | -20.0688 | -31.9686 | -31.9844 | -32.0745 | -31.982 | -31.986 | -31.8948 | 66.5322 | 0.12958 | -8.4283 | -0.023943 | 0.043657 | 55.6879 | 0.003143 | 55.2783 | 35.4991 | 23.5993 | 23.5836 | 23.4934 | 23.586 | 23.5819 | 23.6732 | 122.1002 | 55.6975 | 47.1397 | 55.544 | 55.6116 | 111.2559 | 55.5711 | 110.8462 | 66.4886 | 66.5291 | -8.4719 | -8.4314
1234.5938 | 122.4426 | -55.5496 | 66.6458 | -20.2062 | -31.9961 | -32.0164 | -32.0928 | -32.014 | -32.0272 | -31.9268 | 66.459 | 0.15248 | -8.4283 | -0.03768 | 0.048236 | 55.6925 | 0.016878 | 55.2783 | 35.3434 | 23.5535 | 23.5332 | 23.4568 | 23.5356 | 23.5224 | 23.6228 | 122.0086 | 55.7021 | 47.1214 | 55.5119 | 55.5979 | 111.2421 | 55.5665 | 110.8279 | 66.4107 | 66.4421 | -8.4765 | -8.4451
1235.5938 | 122.4838 | -55.5954 | 66.5176 | -20.1329 | -31.7168 | -31.728 | -31.8044 | -31.7256 | -31.7388 | -31.6384 | 66.372 | 0.13416 | -8.4237 | -0.03768 | 0.048236 | 55.72 | 0.003143 | 55.2691 | 35.4625 | 23.8786 | 23.8674 | 23.791 | 23.8698 | 23.8566 | 23.957 | 121.9674 | 55.7296 | 47.1717 | 55.5577 | 55.6436 | 111.3154 | 55.5985 | 110.8645 | 66.3238 | 66.3688 | -8.4719 | -8.4268
1236.5938 | 122.4747 | -55.3253 | 66.9388 | -21.3004 | -33.2324 | -33.2618 | -33.3427 | -33.2501 | -33.2634 | -33.1629 | 66.8665 | 0.13416 | -8.4191 | -0.033101 | 0.039079 | 55.4453 | 0.012299 | 55.1547 | 34.0249 | 22.0929 | 22.0635 | 21.9826 | 22.0752 | 22.0619 | 22.1624 | 122.1918 | 55.4595 | 46.9062 | 55.2922 | 55.3644 | 110.7706 | 55.3376 | 110.48 | 66.8274 | 66.8542 | -8.4582 | -8.4314
1237.5938 | 122.3282 | -55.9616 | 66.0782 | -19.405 | -30.1875 | -30.1896 | -30.2751 | -30.2012 | -30.2233 | -30.1093 | 65.5616 | 0.14332 | -8.4191 | -0.033101 | 0.039079 | 56.1045 | 0.007721 | 55.3744 | 36.5566 | 25.7742 | 25.772 | 25.6865 | 25.7605 | 25.7383 | 25.8523 | 121.5232 | 56.1049 | 47.5425 | 55.9285 | 56.0007 | 112.0661 | 55.9693 | 111.336 | 65.5225 | 65.5539 | -8.4582 | -8.4268
1238.5938 | 122.1176 | -55.751 | 66.0828 | -18.5534 | -28.6581 | -28.7061 | -28.7459 | -28.7133 | -28.7399 | -28.5985 | 64.7833 | 0.13874 | -8.4099 | -0.033101 | 0.043657 | 56.3151 | 0.007721 | 55.2691 | 37.1976 | 27.0929 | 27.0449 | 27.0051 | 27.0377 | 27.0111 | 27.1526 | 120.5343 | 55.8898 | 47.3411 | 55.7179 | 55.7947 | 112.0662 | 55.7588 | 111.0202 | 64.7396 | 64.7755 | -8.4536 | -8.4177
1239.5938 | 122.4014 | -55.1743 | 66.9342 | -21.978 | -33.7223 | -33.7563 | -33.8418 | -33.7582 | -33.7624 | -33.6574 | 66.8894 | 0.1479 | -8.4191 | -0.028522 | 0.039079 | 55.3354 | 0.012299 | 55.0494 | 33.1962 | 21.452 | 21.418 | 21.3325 | 21.416 | 21.4118 | 21.5169 | 122.0636 | 55.3222 | 46.7552 | 55.1457 | 55.2133 | 110.5097 | 55.1866 | 110.2236 | 66.8503 | 66.8771 | -8.4582 | -8.4314
1240.5938 | 122.4106 | -55.2429 | 66.9205 | -22.2573 | -33.9329 | -33.9852 | -34.0524 | -33.978 | -33.9822 | -33.8679 | 66.9031 | 0.13416 | -8.4145 | -0.033101 | 0.048236 | 55.3583 | -0.001436 | 55.0677 | 32.9856 | 21.31 | 21.2577 | 21.1905 | 21.265 | 21.2607 | 21.375 | 122.146 | 55.3771 | 46.8284 | 55.2098 | 55.2912 | 110.6012 | 55.2415 | 110.3106 | 66.8549 | 66.9045 | -8.4628 | -8.4131
1241.5938 | 122.4976 | -55.2246 | 66.9479 | -22.6694 | -34.4 | -34.4339 | -34.524 | -34.4403 | -34.4355 | -34.3349 | 66.9306 | 0.1479 | -8.4283 | -0.033101 | 0.039079 | 55.3537 | 0.007721 | 55.0585 | 32.5552 | 20.8246 | 20.7907 | 20.7006 | 20.7843 | 20.7891 | 20.8897 | 122.1552 | 55.3725 | 46.7964 | 55.1915 | 55.2637 | 110.5783 | 55.2323 | 110.2831 | 66.8915 | 66.9228 | -8.4673 | -8.436
1242.5938 | 122.5021 | -55.3024 | 66.8243 | -22.4221 | -33.8505 | -33.8845 | -33.9654 | -33.891 | -33.8952 | -33.781 | 66.7566 | 0.13416 | -8.4145 | -0.03768 | 0.039079 | 55.459 | -0.001436 | 55.1089 | 32.8803 | 21.4519 | 21.4179 | 21.337 | 21.4114 | 21.4072 | 21.5215 | 122.059 | 55.4366 | 46.8879 | 55.2647 | 55.3415 | 110.7614 | 55.301 | 110.4113 | 66.7175 | 66.758 | -8.4536 | -8.4131
1243.5938 | 122.4976 | -55.2521 | 66.9571 | -23.0585 | -34.606 | -34.6491 | -34.7346 | -34.6509 | -34.6506 | -34.5501 | 66.9718 | 0.13416 | -8.4145 | -0.033101 | 0.048236 | 55.3354 | 0.007721 | 55.0585 | 32.1935 | 20.6461 | 20.6029 | 20.5175 | 20.6011 | 20.6014 | 20.702 | 122.2238 | 55.3862 | 46.8376 | 55.219 | 55.3003 | 110.5875 | 55.2598 | 110.3106 | 66.9235 | 66.9641 | -8.4628 | -8.4222
1244.5938 | 122.4701 | -55.2383 | 66.9846 | -23.2646 | -34.7067 | -34.7453 | -34.8216 | -34.7471 | -34.7422 | -34.6417 | 66.958 | 0.13874 | -8.4099 | -0.033101 | 0.048236 | 55.3583 | 0.003143 | 55.086 | 31.9738 | 20.5316 | 20.4931 | 20.4168 | 20.4913 | 20.4961 | 20.5967 | 122.1964 | 55.3771 | 46.8284 | 55.2052 | 55.2866 | 110.5966 | 55.2415 | 110.3243 | 66.9098 | 66.9549 | -8.4582 | -8.4131
1245.5938 | 122.3785 | -55.2704 | 66.9571 | -23.173 | -34.4045 | -34.4385 | -34.5331 | -34.4541 | -34.4446 | -34.3441 | 66.9123 | 0.12958 | -8.4328 | -0.028522 | 0.043657 | 55.3949 | 0.012299 | 55.0951 | 32.0974 | 20.8658 | 20.8319 | 20.7373 | 20.8163 | 20.8258 | 20.9263 | 122.1826 | 55.4 | 46.8376 | 55.2419 | 55.314 | 110.6653 | 55.2827 | 110.3655 | 66.8686 | 66.9 | -8.4765 | -8.4451
1246.5938 | 122.3557 | -55.3574 | 66.8793 | -23.4614 | -34.6426 | -34.6629 | -34.7621 | -34.6601 | -34.669 | -34.573 | 66.8802 | 0.14332 | -8.4191 | -0.03768 | 0.043657 | 55.4041 | 0.007721 | 55.086 | 31.8959 | 20.7147 | 20.6945 | 20.5953 | 20.6973 | 20.6884 | 20.7844 | 122.2376 | 55.5007 | 46.9383 | 55.3197 | 55.401 | 110.7614 | 55.3651 | 110.4433 | 66.8365 | 66.8725 | -8.4628 | -8.4268
1247.5938 | 122.4655 | -55.2612 | 66.9296 | -23.8689 | -35.0273 | -35.0475 | -35.1467 | -35.0584 | -35.0581 | -34.953 | 66.9809 | 0.1479 | -8.4191 | -0.03768 | 0.043657 | 55.3125 | 0.003143 | 55.0219 | 31.3923 | 20.234 | 20.2138 | 20.1146 | 20.2029 | 20.2031 | 20.3083 | 122.2422 | 55.4091 | 46.8421 | 55.2235 | 55.3049 | 110.5738 | 55.2644 | 110.2831 | 66.9373 | 66.9778 | -8.4628 | -8.4222
1248.5938 | 122.3969 | -55.3391 | 66.8427 | -23.4431 | -34.1985 | -34.2371 | -34.3134 | -34.2298 | -34.2386 | -34.1243 | 66.72 | 0.1479 | -8.4237 | -0.03768 | 0.043657 | 55.4682 | 0.003143 | 55.1043 | 31.8959 | 21.1406 | 21.102 | 21.0257 | 21.1093 | 21.1005 | 21.2147 | 122.059 | 55.4869 | 46.9154 | 55.3014 | 55.3827 | 110.8072 | 55.3422 | 110.4433 | 66.6763 | 66.7168 | -8.4673 | -8.4268
1249.5938 | 122.4426 | -55.3619 | 66.7694 | -23.4523 | -33.9787 | -34.0219 | -34.0936 | -34.0192 | -34.0326 | -33.9183 | 66.6375 | 0.1479 | -8.4191 | -0.033101 | 0.039079 | 55.5048 | 0.003143 | 55.1272 | 31.9097 | 21.3832 | 21.3401 | 21.2683 | 21.3428 | 21.3294 | 21.4436 | 121.9995 | 55.5098 | 46.9428 | 55.3288 | 55.401 | 110.8667 | 55.3651 | 110.4891 | 66.5985 | 66.6344 | -8.4582 | -8.4222
1250.5938 | 122.2458 | -55.8289 | 66.2704 | -22.7609 | -32.8661 | -32.8497 | -32.9673 | -32.8655 | -32.8925 | -32.7875 | 66.0835 | 0.13874 | -8.4328 | -0.042259 | 0.039079 | 55.8024 | 0.007721 | 55.2371 | 33.0679 | 22.9628 | 22.9791 | 22.8616 | 22.9633 | 22.9363 | 23.0414 | 121.9124 | 55.9676 | 47.396 | 55.7866 | 55.8679 | 111.6312 | 55.8366 | 111.0659 | 66.0445 | 66.0758 | -8.4719 | -8.4406
1251.5938 | 122.0581 | -56.0165 | 65.6616 | -21.511 | -30.8743 | -30.9084 | -30.9756 | -30.9153 | -30.9422 | -30.8143 | 64.971 | 0.13874 | -8.4191 | -0.042259 | 0.039079 | 56.1915 | 0.003143 | 55.205 | 34.5055 | 25.1423 | 25.1081 | 25.0409 | 25.1012 | 25.0744 | 25.2022 | 120.9875 | 56.1553 | 47.5974 | 55.9743 | 56.0556 | 112.2081 | 56.0197 | 111.2216 | 64.9319 | 64.9678 | -8.4582 | -8.4222
1252.5938 | 121.7056 | -56.3187 | 65.2954 | -20.5541 | -29.3404 | -29.3746 | -29.4327 | -29.3725 | -29.3947 | -29.2715 | 64.4078 | 0.13416 | -8.4237 | -0.03768 | 0.048236 | 56.3701 | 0.007721 | 55.2142 | 35.7645 | 26.9783 | 26.9441 | 26.886 | 26.9461 | 26.924 | 27.0472 | 120.7265 | 56.4528 | 47.895 | 56.281 | 56.3669 | 112.6887 | 56.3264 | 111.5328 | 64.3596 | 64.4001 | -8.4719 | -8.4314
1253.5938 | 121.8567 | -55.8655 | 65.7303 | -22.2436 | -31.529 | -31.5769 | -31.6349 | -31.5791 | -31.5831 | -31.4644 | 64.9847 | 0.1479 | -8.4283 | -0.033101 | 0.048236 | 55.9901 | 0.012299 | 54.999 | 33.6219 | 24.3364 | 24.2886 | 24.2305 | 24.2864 | 24.2824 | 24.4011 | 120.8502 | 56.0134 | 47.4372 | 55.8324 | 55.9137 | 111.8556 | 55.8778 | 110.8645 | 64.9365 | 64.9724 | -8.4765 | -8.4406
1254.5938 | 121.8567 | -55.7007 | 65.799 | -22.8983 | -32.3303 | -32.3736 | -32.4453 | -32.394 | -32.4027 | -32.2747 | 64.9984 | 0.1479 | -8.4191 | -0.03768 | 0.048236 | 55.8894 | 0.007721 | 54.8845 | 32.8024 | 23.3703 | 23.3271 | 23.2553 | 23.3067 | 23.298 | 23.4259 | 120.6991 | 55.8486 | 47.2816 | 55.663 | 55.7489 | 111.59 | 55.7084 | 110.5852 | 64.9502 | 64.9907 | -8.4673 | -8.4268
1255.5938 | 121.8521 | -55.2933 | 66.5085 | -25.4805 | -35.7645 | -35.8304 | -35.925 | -35.8458 | -35.8364 | -35.7038 | 65.9553 | 0.14332 | -8.4283 | -0.03768 | 0.048236 | 55.3995 | 0.003143 | 54.7426 | 29.8128 | 19.5288 | 19.4629 | 19.3683 | 19.4475 | 19.4568 | 19.5895 | 121.2486 | 55.4366 | 46.865 | 55.2556 | 55.3415 | 110.6928 | 55.2964 | 110.0359 | 65.9071 | 65.9522 | -8.4765 | -8.4314
1256.5938 | 121.6141 | -56.131 | 65.3 | -23.7865 | -33.4155 | -33.3534 | -33.5396 | -33.4057 | -33.4007 | -33.3277 | 64.7054 | 0.1479 | -8.4191 | -0.042259 | 0.043657 | 55.9809 | 0.003143 | 54.8021 | 32.3445 | 22.7155 | 22.7776 | 22.5914 | 22.7253 | 22.7302 | 22.8033 | 120.8364 | 56.2789 | 47.7119 | 56.0887 | 56.1746 | 112.1119 | 56.1341 | 110.9331 | 64.6618 | 64.7023 | -8.4628 | -8.4222
1257.5938 | 121.5637 | -57.2296 | 64.0274 | -15.5912 | -21.8265 | -21.7833 | -21.8461 | -21.8006 | -21.8449 | -21.7541 | 63.048 | 0.1479 | -6.5786 | -0.03768 | 0.039079 | 57.3223 | 0.007721 | 56.0154 | 41.6384 | 35.4031 | 35.4464 | 35.3835 | 35.429 | 35.3847 | 35.4755 | 120.2776 | 57.3775 | 50.651 | 57.1919 | 57.2687 | 114.5519 | 57.2373 | 113.245 | 63.0089 | 63.0403 | -6.6177 | -6.5864
1258.5938 | 121.7972 | -57.6096 | 64.064 | -17.569 | -24.4548 | -24.4388 | -24.5474 | -24.4146 | -24.4592 | -24.3499 | 63.8355 | 0.1479 | 3.1914 | -0.03768 | 0.048236 | 57.6244 | 0.003143 | 57.1645 | 40.0405 | 33.1548 | 33.1707 | 33.0621 | 33.1949 | 33.1504 | 33.2596 | 121.4451 | 57.7575 | 60.801 | 57.5719 | 57.6578 | 115.234 | 57.6127 | 114.774 | 63.7873 | 63.8324 | 3.1432 | 3.1883
1259.5938 | 121.8201 | -55.4398 | 66.0324 | -27.2844 | -37.7746 | -37.7626 | -37.9991 | -37.8189 | -37.7777 | -37.6907 | 65.1404 | 0.15248 | -8.4237 | -0.03768 | 0.039079 | 55.8115 | 0.012299 | 54.9166 | 28.1554 | 17.6652 | 17.6772 | 17.4407 | 17.6209 | 17.6621 | 17.749 | 120.5801 | 55.5922 | 47.0161 | 55.4021 | 55.4788 | 111.2513 | 55.4521 | 110.3564 | 65.1013 | 65.1281 | -8.4628 | -8.436
1260.5938 | 121.7789 | -56.7902 | 64.6957 | -18.1368 | -24.8165 | -24.8418 | -24.8817 | -24.8449 | -24.8712 | -24.762 | 64.3391 | 0.14332 | -8.3321 | -0.03768 | 0.048236 | 56.805 | 0.007721 | 56.1435 | 38.6534 | 31.9737 | 31.9484 | 31.9085 | 31.9452 | 31.919 | 32.0282 | 121.1293 | 56.9335 | 48.458 | 56.7525 | 56.8384 | 113.5951 | 56.7979 | 112.9337 | 64.2909 | 64.3314 | -8.3803 | -8.3398
1261.5938 | 121.5729 | -56.6116 | 64.7141 | -18.503 | -25.2149 | -25.2309 | -25.2617 | -25.289 | -25.2833 | -25.1694 | 63.8401 | 0.14332 | -8.4191 | -0.033101 | 0.029923 | 56.7775 | 0.007721 | 55.7178 | 38.1086 | 31.3968 | 31.3807 | 31.35 | 31.3226 | 31.3284 | 31.4422 | 120.4517 | 56.755 | 48.1925 | 56.5785 | 56.6416 | 113.3891 | 56.6194 | 112.3294 | 63.8102 | 63.8324 | -8.449 | -8.4268
1262.5938 | 121.3211 | -55.6412 | 65.4694 | -26.648 | -36.1445 | -36.2608 | -36.3142 | -36.3906 | -36.3034 | -36.1341 | 64.0873 | 0.13874 | -8.4237 | -0.033101 | 0.048236 | 55.8024 | 0.003143 | 54.3077 | 28.9932 | 19.4967 | 19.3804 | 19.327 | 19.2506 | 19.3377 | 19.507 | 119.7285 | 55.7799 | 47.2175 | 55.6081 | 55.6894 | 111.4435 | 55.6443 | 109.9489 | 64.0391 | 64.0842 | -8.4719 | -8.4268
1263.5938 | 121.6873 | -67.1997 | 54.3823 | 33.4388 | 44.6625 | 44.7805 | 45.151 | 44.7675 | 44.647 | 44.6889 | 54.4084 | 0.1479 | 49.6152 | -0.033101 | 0.043657 | 67.1789 | 0.003143 | -8.7246 | 100.6385 | 111.8622 | 111.9802 | 112.3507 | 111.9672 | 111.8467 | 111.8886 | 121.6081 | 67.3476 | 116.8149 | 67.1666 | 67.2434 | 134.3786 | 67.2028 | 58.4751 | 54.3647 | 54.4052 | 49.5715 | 49.612
1264.5938 | 121.8018 | -66.925 | 54.7302 | 31.6624 | 42.4784 | 42.569 | 42.9304 | 42.5106 | 42.4219 | 42.5097 | 54.6739 | 0.1479 | 47.6053 | -0.033101 | 0.048236 | 66.8447 | 0.003143 | -8.9306 | 98.5874 | 109.4034 | 109.4941 | 109.8555 | 109.4356 | 109.347 | 109.4348 | 121.599 | 67.0729 | 114.5304 | 66.8919 | 66.9733 | 133.7697 | 66.9282 | 57.9944 | 54.6257 | 54.6708 | 47.5571 | 47.6022
1265.5938 | 121.9391 | -66.8472 | 54.8401 | 31.8913 | 42.7531 | 42.8071 | 43.2006 | 42.7303 | 42.6509 | 42.7615 | 54.6648 | 0.13874 | 47.7885 | -0.033101 | 0.043657 | 66.9408 | 0.003143 | -8.9398 | 98.7385 | 109.6003 | 109.6543 | 110.0478 | 109.5775 | 109.4981 | 109.6087 | 121.512 | 66.986 | 114.6357 | 66.8141 | 66.8909 | 133.788 | 66.8504 | 57.9075 | 54.6211 | 54.6616 | 47.7448 | 47.7853
1266.5938 | 121.7834 | -66.4581 | 55.22 | 29.5059 | 39.5021 | 39.5471 | 39.9498 | 39.4067 | 39.3407 | 39.4973 | 55.0082 | 0.15248 | 45.742 | -0.042259 | 0.043657 | 66.3502 | 0.016878 | -9.0725 | 95.9641 | 105.9603 | 106.0053 | 106.408 | 105.8648 | 105.7988 | 105.9554 | 121.4663 | 66.6106 | 112.2001 | 66.4159 | 66.5018 | 132.8084 | 66.475 | 57.3856 | 54.9645 | 54.9913 | 45.6983 | 45.7251
1267.5938 | 121.9162 | -67.1951 | 54.538 | 33.48 | 44.4106 | 44.4966 | 44.8809 | 44.4104 | 44.322 | 44.4097 | 54.4313 | 0.15248 | 49.8578 | -0.033101 | 0.052814 | 67.1331 | 0.003143 | -8.926 | 100.6751 | 111.6058 | 111.6917 | 112.076 | 111.6055 | 111.5171 | 111.6048 | 121.6264 | 67.3476 | 117.053 | 67.162 | 67.2479 | 134.3282 | 67.1983 | 58.2691 | 54.3785 | 54.4281 | 49.805 | 49.8547
1268.5938 | 121.9025 | -67.2638 | 54.483 | 33.1687 | 43.7147 | 43.819 | 44.1849 | 43.7558 | 43.6627 | 43.7229 | 54.4725 | 0.13874 | 49.4458 | -0.033101 | 0.048236 | 67.1285 | 0.007721 | -8.9398 | 100.4324 | 110.9785 | 111.0828 | 111.4487 | 111.0196 | 110.9265 | 110.9867 | 121.7363 | 67.4025 | 116.7096 | 67.2307 | 67.312 | 134.3923 | 67.2715 | 58.324 | 54.4242 | 54.4648 | 49.3976 | 49.4381
1269.5938 | 121.9986 | -67.3233 | 54.5151 | 33.9836 | 44.5938 | 44.6935 | 45.0686 | 44.6256 | 44.5372 | 44.6111 | 54.3901 | 0.13874 | 50.1554 | -0.03768 | 0.039079 | 67.2659 | 0.007721 | -8.9352 | 101.3069 | 111.9171 | 112.0168 | 112.3919 | 111.9489 | 111.8605 | 111.9344 | 121.7134 | 67.462 | 117.4787 | 67.2856 | 67.3624 | 134.5892 | 67.331 | 58.3881 | 54.351 | 54.3823 | 50.1163 | 50.1477
1270.5938 | 121.9254 | -67.1219 | 54.6707 | 33.2556 | 43.3987 | 43.4985 | 43.869 | 43.4307 | 43.3376 | 43.407 | 54.5549 | 0.1479 | 49.3771 | -0.023943 | 0.048236 | 67.0873 | 0.012299 | -8.9855 | 100.3775 | 110.5206 | 110.6203 | 110.9909 | 110.5526 | 110.4595 | 110.5289 | 121.6768 | 67.2698 | 116.499 | 67.0979 | 67.1701 | 134.2092 | 67.1342 | 58.1363 | 54.5067 | 54.5426 | 49.3289 | 49.3648
1271.5938 | 121.875 | -67.012 | 54.776 | 32.8299 | 42.5654 | 42.7155 | 43.0403 | 42.6113 | 42.5135 | 42.5784 | 54.6327 | 0.13416 | 48.9376 | -0.028522 | 0.039079 | 66.9774 | 0.012299 | -9.0268 | 99.8419 | 109.5774 | 109.7275 | 110.0523 | 109.6233 | 109.5255 | 109.5904 | 121.6448 | 67.1462 | 115.9496 | 66.9835 | 67.0511 | 133.9895 | 67.0243 | 57.9853 | 54.5936 | 54.6204 | 48.8985 | 48.9253
1272.5938 | 121.9666 | -67.0441 | 54.7623 | 32.8161 | 42.3639 | 42.4683 | 42.8526 | 42.387 | 42.2983 | 42.3769 | 54.6556 | 0.1479 | 49.02 | -0.023943 | 0.043657 | 66.9957 | 0.007721 | -8.9672 | 99.8602 | 109.408 | 109.5123 | 109.8967 | 109.431 | 109.3424 | 109.421 | 121.6997 | 67.192 | 116.0641 | 67.0201 | 67.0877 | 134.0398 | 67.0518 | 58.0768 | 54.612 | 54.6479 | 48.9764 | 49.0123
1273.5938 | 121.9894 | -67.3462 | 54.483 | 33.9836 | 43.5544 | 43.7091 | 44.0522 | 43.6596 | 43.5436 | 43.581 | 54.4679 | 0.14332 | 50.0272 | -0.033101 | 0.039079 | 67.2704 | 0.003143 | -8.9855 | 101.3298 | 110.9006 | 111.0553 | 111.3983 | 111.0058 | 110.8898 | 110.9272 | 121.8141 | 67.4895 | 117.3734 | 67.3131 | 67.3853 | 134.6166 | 67.3493 | 58.3606 | 54.4288 | 54.4648 | 49.9882 | 50.0241
1274.5938 | 121.9574 | -66.7328 | 55.0461 | 31.8867 | 40.8254 | 40.907 | 41.2822 | 40.803 | 40.7325 | 40.8295 | 54.8159 | 0.1479 | 48.0128 | -0.023943 | 0.043657 | 66.8172 | 0.012299 | -8.9581 | 98.6195 | 107.5582 | 107.6398 | 108.015 | 107.5358 | 107.4653 | 107.5623 | 121.5487 | 66.8807 | 114.7456 | 66.7088 | 66.7764 | 133.55 | 66.7451 | 57.7747 | 54.7722 | 54.8036 | 47.9691 | 48.0005
1275.5938 | 121.8658 | -66.6641 | 55.0781 | 30.1652 | 38.3895 | 38.494 | 38.8464 | 38.395 | 38.3105 | 38.3939 | 55.0219 | 0.1479 | 46.6256 | -0.033101 | 0.048236 | 66.4006 | 0.003143 | -8.9443 | 96.8294 | 105.0536 | 105.1582 | 105.5105 | 105.0591 | 104.9747 | 105.0581 | 121.686 | 66.812 | 113.2897 | 66.631 | 66.7124 | 133.0647 | 66.6673 | 57.7198 | 54.9737 | 55.0188 | 46.5773 | 46.6224
1276.5938 | 121.8567 | -66.5405 | 55.22 | 30.0691 | 38.0415 | 38.1919 | 38.5076 | 38.0516 | 37.9717 | 38.0506 | 55.0219 | 0.13874 | 46.7171 | -0.033101 | 0.048236 | 66.3136 | 0.007721 | -8.9627 | 96.6096 | 104.582 | 104.7324 | 105.0481 | 104.5922 | 104.5123 | 104.5911 | 121.5624 | 66.6793 | 113.2577 | 66.5074 | 66.5888 | 132.8541 | 66.5482 | 57.5779 | 54.9737 | 55.0142 | 46.6689 | 46.7094
1277.5938 | 121.7514 | -66.3574 | 55.3482 | 29.3961 | 37.0342 | 37.1571 | 37.5003 | 37.0628 | 36.9828 | 37.0434 | 55.0768 | 0.15248 | 46.3371 | -0.033101 | 0.048236 | 66.1259 | 0.007721 | -8.9535 | 95.7535 | 103.3916 | 103.5145 | 103.8578 | 103.4202 | 103.3402 | 103.4008 | 121.4343 | 66.5099 | 112.6946 | 66.3243 | 66.4057 | 132.4833 | 66.3651 | 57.4039 | 55.0286 | 55.0691 | 46.2889 | 46.3294
1278.5938 | 121.7377 | -66.0416 | 55.5725 | 28.7551 | 36.1047 | 36.1819 | 36.5343 | 36.0419 | 35.9985 | 36.0865 | 55.173 | 0.14332 | 45.7511 | -0.03768 | 0.043657 | 65.9016 | 0.007721 | -8.9627 | 94.7967 | 102.1462 | 102.2234 | 102.5758 | 102.0835 | 102.04 | 102.1281 | 121.2146 | 66.1849 | 111.7927 | 66.0039 | 66.0852 | 131.9432 | 66.0493 | 57.0789 | 55.1293 | 55.1653 | 45.7075 | 45.7434
1279.5938 | 121.6599 | -65.744 | 55.8151 | 28.6361 | 35.7521 | 35.843 | 36.2046 | 35.6848 | 35.6276 | 35.7294 | 55.0952 | 0.14332 | 45.893 | -0.03768 | 0.048236 | 65.7551 | 0.007721 | -9.0222 | 94.3801 | 101.4961 | 101.5871 | 101.9486 | 101.4288 | 101.3716 | 101.4735 | 120.8392 | 65.8873 | 111.6371 | 65.7063 | 65.7923 | 131.4991 | 65.7517 | 56.7218 | 55.0469 | 55.0874 | 45.8448 | 45.8853
1280.5938 | 121.7331 | -66.2155 | 55.1971 | 29.0893 | 36.0909 | 36.2322 | 36.5617 | 36.0923 | 36.0213 | 36.082 | 54.9441 | 0.13874 | 46.3234 | -0.033101 | 0.043657 | 65.778 | 0.007721 | -8.9581 | 95.3048 | 102.3064 | 102.4477 | 102.7773 | 102.3078 | 102.2369 | 102.2975 | 121.1596 | 66.3543 | 112.5389 | 66.1824 | 66.2592 | 131.9935 | 66.2232 | 57.2574 | 54.9004 | 54.9363 | 46.2797 | 46.3157
1281.5938 | 121.6873 | -66.0233 | 55.3802 | 28.4804 | 35.2072 | 35.344 | 35.6689 | 35.1584 | 35.0782 | 35.1755 | 54.9715 | 0.13416 | 45.7008 | -0.033101 | 0.043657 | 65.5903 | -0.001436 | -9.1137 | 94.5036 | 101.2305 | 101.3672 | 101.6922 | 101.1816 | 101.1015 | 101.1987 | 120.9948 | 66.1574 | 111.724 | 65.9902 | 66.0669 | 131.6135 | 66.0218 | 56.9095 | 54.9279 | 54.973 | 45.6571 | 45.7022
1282.5938 | 121.6049 | -65.5655 | 55.751 | 27.2351 | 33.7191 | 33.7415 | 34.1534 | 33.5103 | 33.5032 | 33.651 | 55.086 | 0.15248 | 44.7622 | -0.03768 | 0.048236 | 65.3064 | 0.003143 | -9.0908 | 92.8006 | 99.2846 | 99.3069 | 99.7189 | 99.0758 | 99.0687 | 99.2164 | 120.6515 | 65.718 | 110.3277 | 65.5278 | 65.6137 | 130.8719 | 65.5686 | 56.4746 | 55.0378 | 55.0829 | 44.714 | 44.7591
1283.5938 | 121.7697 | -66.8564 | 54.6433 | 33.3747 | 40.8575 | 40.9802 | 41.3463 | 40.8579 | 40.7783 | 40.8433 | 54.4084 | 0.1479 | 49.0246 | -0.03768 | 0.039079 | 66.6524 | 0.007721 | -8.981 | 100.2311 | 107.7139 | 107.8366 | 108.2027 | 107.7143 | 107.6347 | 107.6996 | 121.2648 | 67.0043 | 115.881 | 66.8187 | 66.8955 | 133.5088 | 66.8641 | 57.8754 | 54.3693 | 54.4007 | 48.9855 | 49.0169
1284.5938 | 121.5775 | -65.5792 | 55.7053 | 27.6563 | 33.8794 | 33.9795 | 34.3595 | 33.7392 | 33.7138 | 33.8249 | 54.9899 | 0.14332 | 44.9408 | -0.028522 | 0.043657 | 65.3064 | 0.003143 | -9.0542 | 93.2355 | 99.4586 | 99.5588 | 99.9387 | 99.3184 | 99.2931 | 99.4041 | 120.5691 | 65.7225 | 110.52 | 65.5507 | 65.6229 | 130.8857 | 65.5824 | 56.525 | 54.9462 | 54.9867 | 44.8971 | 44.9376
1285.5938 | 121.4722 | -65.6067 | 55.5542 | 26.8139 | 32.7621 | 32.8441 | 33.2423 | 32.5855 | 32.5784 | 32.685 | 54.912 | 0.14332 | 44.4555 | -0.028522 | 0.048236 | 64.9768 | 0.007721 | -9.0222 | 92.4205 | 98.3688 | 98.4507 | 98.849 | 98.1922 | 98.1851 | 98.2916 | 120.5187 | 65.75 | 110.0622 | 65.5782 | 65.6549 | 130.5835 | 65.6144 | 56.5845 | 54.8638 | 54.9043 | 44.4072 | 44.4477
1286.5938 | 121.3898 | -65.4831 | 55.5862 | 28.0088 | 33.9847 | 34.0986 | 34.4877 | 33.8399 | 33.8237 | 33.9302 | 54.738 | 0.1479 | 45.2063 | -0.033101 | 0.048236 | 65.0821 | 0.003143 | -8.9855 | 93.4919 | 99.4678 | 99.5817 | 99.9708 | 99.323 | 99.3068 | 99.4133 | 120.2211 | 65.631 | 110.6894 | 65.45 | 65.5313 | 130.5652 | 65.4862 | 56.4975 | 54.6898 | 54.7349 | 45.1581 | 45.2032
1287.5938 | 121.6095 | -66.9571 | 54.3869 | 35.3251 | 42.4555 | 42.6331 | 42.9808 | 42.5243 | 42.4128 | 42.4456 | 54.0284 | 0.15706 | 49.7434 | -0.028522 | 0.043657 | 66.7531 | 0.007721 | -8.9855 | 102.2822 | 109.4126 | 109.5902 | 109.9379 | 109.4814 | 109.3699 | 109.4027 | 120.9855 | 67.1141 | 116.7005 | 66.9286 | 67.0007 | 133.7102 | 66.9648 | 57.9715 | 53.9847 | 54.0206 | 49.6997 | 49.7357
1288.5938 | 121.5729 | -66.861 | 54.4235 | 34.5147 | 41.4756 | 41.6029 | 41.9964 | 41.4302 | 41.3643 | 41.4338 | 54.1154 | 0.13874 | 49.1894 | -0.03768 | 0.048236 | 66.5746 | 0.007721 | -8.9993 | 101.3757 | 108.3366 | 108.4639 | 108.8574 | 108.2911 | 108.2253 | 108.2948 | 120.9763 | 66.9997 | 116.0504 | 66.8233 | 66.9092 | 133.4355 | 66.8687 | 57.8617 | 54.0671 | 54.1076 | 49.1412 | 49.1817
1289.5938 | 121.4722 | -66.8289 | 54.5288 | 33.7181 | 40.45 | 40.559 | 40.9937 | 40.3406 | 40.3021 | 40.3946 | 54.2207 | 0.15706 | 48.608 | -0.033101 | 0.043657 | 66.4052 | 0.012299 | -8.9672 | 100.547 | 107.2789 | 107.3879 | 107.8226 | 107.1695 | 107.1311 | 107.2235 | 121.0496 | 66.986 | 115.4369 | 66.7958 | 66.8726 | 133.2341 | 66.8412 | 57.8617 | 54.177 | 54.2084 | 48.5643 | 48.5957
1290.5938 | 121.431 | -66.0461 | 55.0827 | 30.8978 | 36.9746 | 37.0518 | 37.4958 | 36.7652 | 36.7722 | 36.8831 | 54.3946 | 0.15706 | 46.5935 | -0.03768 | 0.043657 | 65.7002 | 0.007721 | -9.1229 | 96.9439 | 103.0208 | 103.0979 | 103.5419 | 102.8114 | 102.8183 | 102.9293 | 120.4408 | 66.2032 | 112.6397 | 66.0085 | 66.0898 | 131.7463 | 66.0539 | 56.9233 | 54.351 | 54.3869 | 46.5499 | 46.5858
1291.5938 | 121.3623 | -66.2704 | 54.8721 | 31.6395 | 37.6386 | 37.8164 | 38.2192 | 37.5343 | 37.4956 | 37.5653 | 54.2756 | 0.14332 | 46.9598 | -0.033101 | 0.048236 | 65.8283 | 0.012299 | -9.0771 | 97.9099 | 103.909 | 104.0869 | 104.4896 | 103.8048 | 103.766 | 103.8357 | 120.5461 | 66.4138 | 113.2302 | 66.2373 | 66.3187 | 132.0988 | 66.2827 | 57.1933 | 54.2274 | 54.2633 | 46.9115 | 46.9475
1292.5938 | 121.2112 | -65.3549 | 55.6686 | 27.0886 | 32.5515 | 32.5007 | 33.0912 | 32.0454 | 32.1526 | 32.3645 | 54.6831 | 0.13874 | 44.1167 | -0.033101 | 0.043657 | 64.7845 | 0.007721 | -9.1275 | 92.4435 | 97.9064 | 97.8556 | 98.4462 | 97.4003 | 97.5075 | 97.7194 | 120.038 | 65.4937 | 109.4716 | 65.3218 | 65.3986 | 130.1395 | 65.3626 | 56.2274 | 54.6394 | 54.6754 | 44.073 | 44.1089
1293.5938 | 121.3074 | -66.1102 | 54.9774 | 32.2392 | 38.2979 | 38.3292 | 38.851 | 38.0104 | 38.0267 | 38.1742 | 54.184 | 0.15706 | 47.1063 | -0.023943 | 0.043657 | 65.9199 | 0.007721 | -9.0313 | 98.3495 | 104.4081 | 104.4394 | 104.9612 | 104.1207 | 104.1369 | 104.2844 | 120.2943 | 66.2673 | 113.2165 | 66.0863 | 66.1539 | 132.0301 | 66.118 | 57.0789 | 54.1404 | 54.1763 | 47.0626 | 47.0986
1294.5938 | 121.2433 | -66.3574 | 54.689 | 31.5204 | 37.2906 | 37.354 | 37.862 | 36.9987 | 37.0378 | 37.1624 | 54.2207 | 0.1479 | 46.4974 | -0.033101 | 0.039079 | 65.7093 | 0.003143 | -8.9764 | 97.8779 | 103.648 | 103.7114 | 104.2195 | 103.3561 | 103.3952 | 103.5198 | 120.5781 | 66.5053 | 112.8548 | 66.3243 | 66.3965 | 132.0667 | 66.3606 | 57.381 | 54.1816 | 54.2175 | 46.4583 | 46.4942
1295.5938 | 121.2662 | -66.1331 | 54.9133 | 31.3419 | 37.0616 | 37.0747 | 37.6468 | 36.6874 | 36.7218 | 36.906 | 54.2436 | 0.15248 | 46.3829 | -0.03768 | 0.039079 | 65.6452 | 0.007721 | -9.1229 | 97.475 | 103.1948 | 103.2078 | 103.78 | 102.8205 | 102.855 | 103.0391 | 120.3767 | 66.2856 | 112.516 | 66.0954 | 66.1722 | 131.7783 | 66.1408 | 57.0102 | 54.2045 | 54.2358 | 46.3438 | 46.3752
1296.5938 | 121.4813 | -67.2821 | 53.9566 | 37.0603 | 43.4308 | 43.5122 | 44.0247 | 43.2705 | 43.2506 | 43.3292 | 53.7582 | 0.14332 | 49.6152 | -0.033101 | 0.039079 | 66.9271 | 0.012299 | -8.9627 | 104.3424 | 110.7129 | 110.7943 | 111.3068 | 110.5526 | 110.5327 | 110.6113 | 121.0403 | 67.4254 | 116.8973 | 67.249 | 67.3212 | 134.2092 | 67.2944 | 58.3194 | 53.7192 | 53.7459 | 49.5761 | 49.6029
1297.5938 | 121.376 | -66.6916 | 54.4189 | 34.4094 | 40.308 | 40.4171 | 40.9342 | 40.011 | 40.0458 | 40.1657 | 53.9826 | 0.15706 | 47.8709 | -0.03768 | 0.039079 | 66.3045 | 0.003143 | -9.1137 | 101.101 | 106.9996 | 107.1086 | 107.6258 | 106.7026 | 106.7373 | 106.8573 | 120.6742 | 66.8486 | 114.5624 | 66.6539 | 66.7307 | 132.996 | 66.6947 | 57.5779 | 53.9435 | 53.9794 | 47.8318 | 47.8677
1298.5938 | 121.2799 | -66.394 | 54.5654 | 32.5185 | 38.0278 | 38.1049 | 38.6999 | 37.6671 | 37.7337 | 37.8583 | 54.1016 | 0.13416 | 46.5569 | -0.033101 | 0.039079 | 65.8146 | 0.007721 | -9.1366 | 98.9126 | 104.4218 | 104.4989 | 105.0939 | 104.0611 | 104.1277 | 104.2523 | 120.4957 | 66.5282 | 112.9509 | 66.3609 | 66.4331 | 132.2086 | 66.4018 | 57.2574 | 54.0625 | 54.0939 | 46.5178 | 46.5492
1299.5938 | 121.1929 | -66.0599 | 54.8355 | 30.971 | 36.1321 | 36.2231 | 36.8227 | 35.7215 | 35.8016 | 35.9355 | 54.1611 | 0.1479 | 45.5268 | -0.033101 | 0.048236 | 65.3751 | 0.003143 | -9.1412 | 97.0309 | 102.192 | 102.2829 | 102.8826 | 101.7813 | 101.8615 | 101.9953 | 120.221 | 66.2078 | 111.5867 | 66.0268 | 66.1081 | 131.435 | 66.063 | 56.9187 | 54.1129 | 54.158 | 45.4785 | 45.5236
1300.5938 | 120.932 | -65.5701 | 55.1559 | 27.1984 | 31.8097 | 31.8825 | 32.5556 | 31.2076 | 31.3651 | 31.5221 | 54.3168 | 0.13874 | 43.1094 | -0.033101 | 0.039079 | 64.4275 | 0.003143 | -9.1412 | 92.7685 | 97.3798 | 97.4526 | 98.1256 | 96.7777 | 96.9352 | 97.0922 | 119.8869 | 65.7088 | 108.6795 | 65.537 | 65.6091 | 129.9975 | 65.5732 | 56.4289 | 54.2777 | 54.3137 | 43.0704 | 43.1063
1301.5938 | 121.1792 | -66.6595 | 54.1946 | 34.2446 | 39.6029 | 39.7257 | 40.3161 | 39.3014 | 39.3315 | 39.4286 | 53.7353 | 0.1479 | 47.1154 | -0.042259 | 0.029923 | 66.0527 | 0.003143 | -8.981 | 100.9041 | 106.2624 | 106.3852 | 106.9757 | 105.961 | 105.9911 | 106.0882 | 120.3949 | 66.8074 | 113.775 | 66.6173 | 66.6895 | 132.7122 | 66.6627 | 57.6786 | 53.7054 | 53.7322 | 47.0855 | 47.1123
1302.5938 | 121.1609 | -66.5909 | 54.3182 | 33.5807 | 38.884 | 38.9473 | 39.5835 | 38.4774 | 38.5486 | 38.6778 | 53.7857 | 0.14332 | 46.7629 | -0.03768 | 0.039079 | 65.9107 | 0.003143 | -8.9855 | 100.1716 | 105.4749 | 105.5382 | 106.1744 | 105.0683 | 105.1395 | 105.2687 | 120.3766 | 66.7342 | 113.3538 | 66.5532 | 66.63 | 132.5016 | 66.594 | 57.6053 | 53.7466 | 53.7826 | 46.7238 | 46.7598
1303.5938 | 121.2067 | -66.861 | 54.1122 | 36.2133 | 41.7229 | 41.809 | 42.3947 | 41.4302 | 41.4467 | 41.5666 | 53.6117 | 0.15706 | 48.1684 | -0.028522 | 0.043657 | 66.4967 | 0.007721 | -9.0039 | 103.0742 | 108.5838 | 108.6699 | 109.2557 | 108.2911 | 108.3077 | 108.4276 | 120.4727 | 67.018 | 115.0294 | 66.8324 | 66.9046 | 133.3577 | 66.8687 | 57.8571 | 53.5681 | 53.604 | 48.1248 | 48.1607
1304.5938 | 120.9503 | -65.7166 | 54.9911 | 29.4785 | 34.1083 | 34.1993 | 34.8402 | 33.524 | 33.6681 | 33.8341 | 54.0513 | 0.1479 | 44.2632 | -0.033101 | 0.039079 | 64.8898 | 0.003143 | -9.1366 | 95.195 | 99.8249 | 99.9159 | 100.5568 | 99.2406 | 99.3846 | 99.5506 | 119.7678 | 65.8645 | 109.9797 | 65.6835 | 65.7556 | 130.6064 | 65.7197 | 56.5799 | 54.0122 | 54.0481 | 44.2241 | 44.26
1305.5938 | 121.0373 | -66.5131 | 54.2542 | 33.3838 | 38.2979 | 38.4254 | 39.0295 | 37.9463 | 37.9946 | 38.0964 | 53.6438 | 0.1479 | 46.3875 | -0.033101 | 0.043657 | 65.7185 | 0.003143 | -9.0313 | 99.8969 | 104.811 | 104.9384 | 105.5426 | 104.4594 | 104.5077 | 104.6094 | 120.1568 | 66.661 | 112.9006 | 66.48 | 66.5567 | 132.2315 | 66.5162 | 57.4817 | 53.6001 | 53.6406 | 46.3438 | 46.3844
1306.5938 | 121.1243 | -67.0898 | 53.7964 | 37.4037 | 42.7897 | 42.8895 | 43.4432 | 42.593 | 42.5547 | 42.6608 | 53.392 | 0.13874 | 48.6537 | -0.03768 | 0.034501 | 66.7027 | 0.003143 | -8.9718 | 104.4935 | 109.8796 | 109.9793 | 110.5331 | 109.6828 | 109.6446 | 109.7506 | 120.4818 | 67.2286 | 115.7436 | 67.0522 | 67.1243 | 133.7926 | 67.093 | 58.118 | 53.3575 | 53.3888 | 48.6192 | 48.6506
1307.5938 | 121.2158 | -66.98 | 53.8559 | 36.3232 | 41.526 | 41.635 | 42.2391 | 41.247 | 41.2499 | 41.356 | 53.4011 | 0.15248 | 47.9075 | -0.028522 | 0.039079 | 66.4326 | 0.012299 | -8.9901 | 103.3031 | 108.506 | 108.6149 | 109.2191 | 108.227 | 108.2298 | 108.336 | 120.3811 | 67.1325 | 114.8875 | 66.9515 | 67.0191 | 133.4126 | 66.9923 | 57.9899 | 53.362 | 53.3888 | 47.8684 | 47.8952
1308.5938 | 121.0327 | -66.6779 | 54.0756 | 34.7848 | 39.8272 | 39.8905 | 40.5359 | 39.4388 | 39.4735 | 39.6209 | 53.4927 | 0.14332 | 47.0376 | -0.03768 | 0.043657 | 66.1213 | 0.003143 | -8.9764 | 101.4627 | 106.5051 | 106.5684 | 107.2137 | 106.1166 | 106.1513 | 106.2987 | 120.1705 | 66.8212 | 113.7155 | 66.6402 | 66.7215 | 132.7992 | 66.681 | 57.7015 | 53.449 | 53.4895 | 46.994 | 47.0345
1309.5938 | 120.8542 | -66.4993 | 54.1855 | 33.8646 | 38.7283 | 38.8008 | 39.4599 | 38.2897 | 38.3426 | 38.4901 | 53.4927 | 0.1479 | 46.4012 | -0.042259 | 0.043657 | 65.8695 | -0.001436 | -8.9947 | 100.3639 | 105.2277 | 105.3001 | 105.9593 | 104.789 | 104.8419 | 104.9894 | 119.992 | 66.6472 | 112.9006 | 66.4571 | 66.543 | 132.3689 | 66.4979 | 57.5046 | 53.449 | 53.4941 | 46.3576 | 46.4027
1310.5938 | 120.9732 | -66.5176 | 54.1901 | 34.4231 | 39.2778 | 39.3686 | 39.9773 | 38.9123 | 38.924 | 39.0761 | 53.4286 | 0.13874 | 46.6897 | -0.03768 | 0.048236 | 65.9931 | -0.001436 | -9.0268 | 100.9408 | 105.7954 | 105.8862 | 106.4949 | 105.4299 | 105.4417 | 105.5937 | 119.9462 | 66.6564 | 113.2073 | 66.48 | 66.5659 | 132.5108 | 66.5162 | 57.4909 | 53.3803 | 53.43 | 46.6414 | 46.6911
1311.5938 | 120.8542 | -66.3528 | 54.277 | 32.958 | 37.5882 | 37.7019 | 38.3336 | 37.1269 | 37.1659 | 37.3318 | 53.4835 | 0.1479 | 45.8015 | -0.03768 | 0.039079 | 65.6544 | 0.007721 | -9.0268 | 99.3109 | 103.941 | 104.0548 | 104.6865 | 103.4797 | 103.5188 | 103.6846 | 119.8364 | 66.5007 | 112.1543 | 66.3152 | 66.3919 | 132.0072 | 66.3606 | 57.3261 | 53.4444 | 53.4758 | 45.7624 | 45.7938
1312.5938 | 120.8221 | -66.0645 | 54.538 | 33.7272 | 38.4078 | 38.4895 | 39.0891 | 38.0333 | 38.0633 | 38.2017 | 53.3828 | 0.13874 | 46.2181 | -0.03768 | 0.048236 | 65.8192 | 0.007721 | -8.9718 | 99.7917 | 104.4723 | 104.5539 | 105.1535 | 104.0978 | 104.1278 | 104.2661 | 119.4473 | 66.2032 | 112.2826 | 66.0268 | 66.1127 | 131.8836 | 66.0722 | 57.0926 | 53.3346 | 53.3751 | 46.1699 | 46.2104
1313.5938 | 120.6345 | -65.5472 | 54.8218 | 28.3476 | 32.5515 | 32.6014 | 33.3522 | 31.7661 | 31.9603 | 32.1722 | 53.6163 | 0.1479 | 43.2651 | -0.033101 | 0.043657 | 64.4732 | -0.001436 | -9.1183 | 93.8948 | 98.0987 | 98.1486 | 98.8994 | 97.3133 | 97.5075 | 97.7194 | 119.1635 | 65.6951 | 108.8123 | 65.5141 | 65.5908 | 130.0204 | 65.5457 | 56.4289 | 53.5726 | 53.6177 | 43.2215 | 43.2665
1314.5938 | 120.7489 | -65.8356 | 54.5425 | 30.2843 | 34.6074 | 34.703 | 35.3759 | 34.0322 | 34.1534 | 34.3377 | 53.337 | 0.14332 | 44.3547 | -0.028522 | 0.039079 | 64.9127 | 0.003143 | -8.9718 | 96.1198 | 100.443 | 100.5385 | 101.2115 | 99.8678 | 99.9889 | 100.1732 | 119.1726 | 65.9789 | 110.1903 | 65.807 | 65.8747 | 130.7483 | 65.8387 | 56.8638 | 53.2979 | 53.3339 | 44.3157 | 44.3516
1315.5938 | 120.4742 | -63.5468 | 56.5842 | 18.6918 | 21.947 | 21.8508 | 22.7347 | 20.6371 | 21.0271 | 21.3952 | 54.0238 | 0.14332 | 42.3037 | -0.03768 | 0.039079 | 62.6054 | -0.001436 | -8.047 | 82.2385 | 85.4937 | 85.3976 | 86.2814 | 84.1838 | 84.5739 | 84.9419 | 117.5705 | 63.6901 | 105.8504 | 63.5091 | 63.5858 | 126.1521 | 63.5453 | 55.4997 | 53.9847 | 54.0252 | 42.2646 | 42.3051
1316.5938 | 120.3003 | -65.1947 | 54.8767 | 25.6189 | 29.2914 | 29.4788 | 30.2343 | 28.3876 | 28.6639 | 28.8347 | 53.2958 | 0.1479 | 42.8943 | -0.033101 | 0.039079 | 63.5851 | 0.003143 | -9.1366 | 90.8136 | 94.4861 | 94.6735 | 95.429 | 93.5823 | 93.8586 | 94.0294 | 118.4905 | 65.3426 | 108.089 | 65.1616 | 65.2338 | 128.7798 | 65.1978 | 56.0581 | 53.2567 | 53.2927 | 42.8552 | 42.8911
1317.5938 | 121.051 | -48.3444 | 72.4777 | -42.7914 | -47.8205 | -47.8492 | -48.0214 | -47.9957 | -47.8639 | -47.781 | -8.5459 | 0.15248 | -8.4557 | -0.03768 | 0.043657 | 48.4454 | 0.003143 | 48.2599 | 5.553 | 0.52394 | 0.49518 | 0.32304 | 0.34874 | 0.48055 | 0.5634 | 39.7985 | 48.4969 | 39.8887 | 48.3067 | 48.3881 | 96.7898 | 48.3476 | 96.6044 | -8.5896 | -8.5491 | -8.4994 | -8.4589
1318.5938 | 121.17 | -48.3948 | 72.5372 | -42.9196 | -48.0311 | -48.069 | -48.2228 | -48.2566 | -48.047 | -47.9779 | -8.6604 | 0.15248 | -8.4008 | -0.033101 | 0.039079 | 48.5004 | 0.003143 | 48.4476 | 5.4752 | 0.36367 | 0.32576 | 0.17194 | 0.13815 | 0.34777 | 0.4169 | 39.7344 | 48.5473 | 39.994 | 48.3617 | 48.4339 | 96.8951 | 48.3979 | 96.8424 | -8.6995 | -8.6635 | -8.4399 | -8.4039
1319.5938 | 121.257 | -48.4085 | 72.5876 | -42.8738 | -48.0265 | -48.0827 | -48.2091 | -48.252 | -48.0607 | -47.9962 | -8.665 | 0.1479 | -8.4099 | -0.03768 | 0.039079 | 48.5324 | 0.003143 | 48.4797 | 5.5347 | 0.38198 | 0.32576 | 0.19941 | 0.15646 | 0.34776 | 0.41232 | 39.7435 | 48.5564 | 39.9986 | 48.3708 | 48.4476 | 96.9409 | 48.4117 | 96.8882 | -8.704 | -8.6681 | -8.449 | -8.4131
1320.5938 | 121.3074 | -48.4085 | 72.6288 | -42.8967 | -48.0494 | -48.1148 | -48.2366 | -48.252 | -48.0836 | -48.0191 | -8.6695 | 0.1479 | -8.4099 | -0.033101 | 0.043657 | 48.537 | -0.001436 | 48.4934 | 5.5118 | 0.35909 | 0.29371 | 0.17194 | 0.15646 | 0.32487 | 0.38943 | 39.739 | 48.5564 | 39.9986 | 48.3754 | 48.4522 | 96.9455 | 48.4071 | 96.9019 | -8.7132 | -8.6681 | -8.4536 | -8.4085
1321.5938 | 121.3898 | -48.4406 | 72.6288 | -43.1073 | -48.0403 | -48.0553 | -48.2228 | -48.2566 | -48.0791 | -48.0053 | -8.6695 | 0.1479 | -8.4145 | -0.033101 | 0.039079 | 48.5461 | -0.001436 | 48.5072 | 5.3333 | 0.40029 | 0.38528 | 0.21772 | 0.18393 | 0.36149 | 0.4352 | 39.771 | 48.5885 | 40.026 | 48.4075 | 48.4796 | 96.9867 | 48.4391 | 96.9477 | -8.7086 | -8.6681 | -8.4536 | -8.4131
1322.5938 | 121.4081 | -48.4131 | 72.6791 | -43.2263 | -48.0174 | -48.0278 | -48.1999 | -48.22 | -48.0607 | -47.987 | -8.6741 | 0.13874 | -8.4099 | -0.03768 | 0.039079 | 48.5324 | 0.003143 | 48.4934 | 5.1868 | 0.39572 | 0.38528 | 0.21314 | 0.19309 | 0.35234 | 0.42605 | 39.739 | 48.5518 | 40.0031 | 48.3754 | 48.4522 | 96.9455 | 48.4162 | 96.9065 | -8.7132 | -8.6773 | -8.449 | -8.4131
1323.5938 | 121.3623 | -48.4222 | 72.702 | -43.3408 | -48.0036 | -48.0186 | -48.1908 | -48.1971 | -48.0333 | -47.955 | -8.6741 | 0.15706 | -8.4145 | -0.033101 | 0.043657 | 48.5232 | 0.007721 | 48.4843 | 5.0815 | 0.41861 | 0.40359 | 0.23145 | 0.22513 | 0.38897 | 0.46725 | 39.7481 | 48.5793 | 40.0077 | 48.3891 | 48.4659 | 96.9455 | 48.43 | 96.9065 | -8.7178 | -8.6818 | -8.4582 | -8.4222
1324.5938 | 121.4172 | -48.3856 | 72.7295 | -43.4461 | -47.9853 | -48.0095 | -48.1679 | -48.1742 | -48.015 | -47.9367 | -8.6833 | 0.14332 | -8.4191 | -0.033101 | 0.034501 | 48.5095 | 0.003143 | 48.4705 | 4.9395 | 0.4003 | 0.37613 | 0.21773 | 0.2114 | 0.37066 | 0.44895 | 39.7023 | 48.5289 | 39.9665 | 48.3525 | 48.4201 | 96.8951 | 48.3888 | 96.8561 | -8.7178 | -8.6864 | -8.4536 | -8.4222
1325.5938 | 121.4447 | -48.4131 | 72.7661 | -43.5697 | -47.9716 | -48.0095 | -48.1633 | -48.1605 | -48.0104 | -47.9275 | -8.6741 | 0.15248 | -8.4191 | -0.033101 | 0.043657 | 48.5187 | 0.007721 | 48.4659 | 4.8434 | 0.44151 | 0.4036 | 0.24977 | 0.2526 | 0.4027 | 0.48557 | 39.739 | 48.5656 | 39.994 | 48.38 | 48.4567 | 96.9318 | 48.4208 | 96.879 | -8.7178 | -8.6818 | -8.4628 | -8.4268
1326.5938 | 121.4905 | -48.3994 | 72.8073 | -43.6338 | -47.9029 | -47.9408 | -48.1175 | -48.046 | -47.928 | -47.8451 | -8.6833 | 0.15248 | -8.4099 | -0.028522 | 0.048236 | 48.4912 | 0.007721 | 48.4431 | 4.7656 | 0.49646 | 0.45854 | 0.28182 | 0.35332 | 0.47138 | 0.55424 | 39.7161 | 48.5518 | 39.9894 | 48.3708 | 48.4476 | 96.8906 | 48.4071 | 96.8424 | -8.7315 | -8.691 | -8.4582 | -8.4177
1327.5938 | 121.5042 | -48.349 | 72.8302 | -43.5972 | -47.7701 | -47.8263 | -48.0305 | -47.808 | -47.7631 | -47.6574 | -8.6833 | 0.13416 | -8.4145 | -0.033101 | 0.039079 | 48.4866 | 0.012299 | 48.4522 | 4.7518 | 0.57889 | 0.52265 | 0.31846 | 0.54102 | 0.58585 | 0.69159 | 39.6657 | 48.4832 | 39.9345 | 48.3159 | 48.3881 | 96.8356 | 48.3613 | 96.8012 | -8.7224 | -8.6956 | -8.4536 | -8.4268
1328.5938 | 121.55 | -48.317 | 72.8577 | -43.6704 | -47.7152 | -47.7851 | -47.9848 | -47.721 | -47.6899 | -47.5887 | -8.6833 | 0.15248 | -8.4145 | -0.033101 | 0.043657 | 48.4592 | 0.003143 | 48.4156 | 4.6465 | 0.60179 | 0.53182 | 0.3322 | 0.59596 | 0.62706 | 0.72822 | 39.6337 | 48.4694 | 39.9024 | 48.2839 | 48.3606 | 96.7761 | 48.3201 | 96.7325 | -8.7269 | -8.6864 | -8.4582 | -8.4177
1329.5938 | 121.5363 | -48.3124 | 72.9355 | -43.7712 | -47.6877 | -47.7622 | -47.9664 | -47.6935 | -47.6762 | -47.5658 | -8.6879 | 0.13874 | -8.4145 | -0.03768 | 0.043657 | 48.4408 | 0.003143 | 48.4019 | 4.5412 | 0.62469 | 0.55013 | 0.34594 | 0.61885 | 0.63622 | 0.74654 | 39.6245 | 48.4511 | 39.8979 | 48.2747 | 48.356 | 96.7532 | 48.3155 | 96.7142 | -8.7315 | -8.691 | -8.4582 | -8.4177
1330.5938 | 121.5271 | -48.3398 | 72.9263 | -43.8581 | -47.6602 | -47.7348 | -47.939 | -47.6752 | -47.6487 | -47.5338 | -8.6879 | 0.15248 | -8.4191 | -0.03768 | 0.043657 | 48.4225 | 0.007721 | 48.379 | 4.4817 | 0.67962 | 0.60507 | 0.40087 | 0.66462 | 0.69116 | 0.80605 | 39.652 | 48.4923 | 39.9207 | 48.3022 | 48.3835 | 96.7624 | 48.3476 | 96.7188 | -8.7315 | -8.6956 | -8.4628 | -8.4268
1331.5938 | 121.5546 | -48.2758 | 72.9675 | -43.9222 | -47.6007 | -47.6844 | -47.8657 | -47.6386 | -47.6258 | -47.4834 | -8.6833 | 0.12958 | -8.4191 | -0.033101 | 0.043657 | 48.4088 | 0.003143 | 48.3606 | 4.3535 | 0.67506 | 0.59135 | 0.41004 | 0.63716 | 0.64996 | 0.79232 | 39.5925 | 48.4053 | 39.8567 | 48.2427 | 48.3194 | 96.6846 | 48.2789 | 96.6364 | -8.7269 | -8.6864 | -8.4628 | -8.4222
1332.5938 | 121.5729 | -48.2346 | 72.995 | -43.9634 | -47.532 | -47.6295 | -47.7833 | -47.5837 | -47.5663 | -47.4239 | -8.6924 | 0.14332 | -8.4191 | -0.033101 | 0.043657 | 48.3768 | 0.003143 | 48.3286 | 4.2711 | 0.70255 | 0.60509 | 0.45126 | 0.6509 | 0.66828 | 0.81064 | 39.5421 | 48.3779 | 39.8155 | 48.2015 | 48.2782 | 96.6113 | 48.2377 | 96.5632 | -8.7361 | -8.6956 | -8.4628 | -8.4222
1333.5938 | 121.6278 | -48.2208 | 73.0545 | -43.9863 | -47.445 | -47.5516 | -47.6826 | -47.5196 | -47.493 | -47.3507 | -8.6833 | 0.13416 | -8.4191 | -0.033101 | 0.039079 | 48.3584 | 0.003143 | 48.3149 | 4.2345 | 0.77581 | 0.66919 | 0.53825 | 0.70126 | 0.7278 | 0.87016 | 39.5375 | 48.355 | 39.8017 | 48.1877 | 48.2599 | 96.5793 | 48.224 | 96.5357 | -8.7224 | -8.6864 | -8.4582 | -8.4222
1334.5938 | 121.6187 | -48.23 | 73.1094 | -44.0092 | -47.3443 | -47.4601 | -47.5544 | -47.4417 | -47.4198 | -47.2637 | -8.6833 | 0.1479 | -8.4191 | -0.03768 | 0.043657 | 48.3401 | 0.007721 | 48.2874 | 4.2207 | 0.8857 | 0.76992 | 0.6756 | 0.78824 | 0.81021 | 0.9663 | 39.5467 | 48.3779 | 39.8109 | 48.1923 | 48.2736 | 96.5701 | 48.2377 | 96.5174 | -8.7269 | -8.691 | -8.4628 | -8.4268
1335.5938 | 121.5546 | -48.2162 | 73.1186 | -44.0825 | -47.3397 | -47.4555 | -47.5315 | -47.4234 | -47.4106 | -47.2408 | -8.6879 | 0.1479 | -8.4191 | -0.03768 | 0.043657 | 48.3172 | 0.007721 | 48.2737 | 4.1338 | 0.87655 | 0.76077 | 0.68476 | 0.79282 | 0.80564 | 0.97546 | 39.5284 | 48.3641 | 39.7971 | 48.1786 | 48.2599 | 96.5335 | 48.224 | 96.4899 | -8.7315 | -8.6956 | -8.4628 | -8.4268
1336.5938 | 121.5408 | -48.2025 | 73.1461 | -44.1374 | -47.3077 | -47.4372 | -47.504 | -47.4005 | -47.3877 | -47.2225 | -8.697 | 0.15248 | -8.4237 | -0.03768 | 0.034501 | 48.2943 | 0.007721 | 48.2508 | 4.0651 | 0.89486 | 0.76535 | 0.6985 | 0.80197 | 0.81479 | 0.98004 | 39.5055 | 48.355 | 39.7788 | 48.1648 | 48.237 | 96.4969 | 48.2102 | 96.4533 | -8.7315 | -8.7047 | -8.4582 | -8.4314
1337.5938 | 121.6415 | -48.1934 | 73.1369 | -44.1969 | -47.3031 | -47.4417 | -47.5132 | -47.3914 | -47.3831 | -47.2133 | -8.6833 | 0.14332 | -8.4191 | -0.03768 | 0.039079 | 48.2623 | 0.003143 | 48.2233 | 3.9964 | 0.89029 | 0.75162 | 0.68019 | 0.80197 | 0.81022 | 0.98004 | 39.5101 | 48.3367 | 39.7743 | 48.1557 | 48.2324 | 96.4557 | 48.1965 | 96.4167 | -8.7224 | -8.6864 | -8.4582 | -8.4222
1338.5938 | 121.6553 | -48.1247 | 73.1918 | -44.2336 | -47.2802 | -47.4051 | -47.4811 | -47.3685 | -47.3648 | -47.195 | -8.6833 | 0.13874 | -8.4145 | -0.033101 | 0.043657 | 48.2531 | -0.001436 | 48.2141 | 3.8911 | 0.84452 | 0.71958 | 0.64358 | 0.7562 | 0.75987 | 0.92968 | 39.4414 | 48.2634 | 39.7102 | 48.0916 | 48.1684 | 96.3778 | 48.1233 | 96.3388 | -8.7269 | -8.6818 | -8.4582 | -8.4131
1339.5938 | 121.6736 | -48.1018 | 73.2605 | -44.261 | -47.2344 | -47.3731 | -47.4445 | -47.3227 | -47.3282 | -47.1492 | -8.6879 | 0.15706 | -8.4191 | -0.042259 | 0.039079 | 48.2165 | 0.007721 | 48.1775 | 3.8408 | 0.86742 | 0.72874 | 0.65732 | 0.77909 | 0.77361 | 0.95258 | 39.4139 | 48.2589 | 39.6827 | 48.0595 | 48.1409 | 96.3183 | 48.1095 | 96.2793 | -8.7269 | -8.6956 | -8.4582 | -8.4268
1340.5938 | 121.6736 | -48.0469 | 73.2834 | -44.3114 | -47.1978 | -47.341 | -47.4033 | -47.2815 | -47.2916 | -47.1172 | -8.6879 | 0.14332 | -8.4191 | -0.03768 | 0.043657 | 48.1891 | 0.007721 | 48.1409 | 3.7355 | 0.84912 | 0.70586 | 0.64359 | 0.76536 | 0.7553 | 0.92969 | 39.359 | 48.1902 | 39.6278 | 48.0092 | 48.0905 | 96.2359 | 48.0546 | 96.1878 | -8.7315 | -8.6956 | -8.4628 | -8.4268
1341.5938 | 121.6827 | -48.0606 | 73.3292 | -44.3435 | -47.1657 | -47.309 | -47.3667 | -47.2357 | -47.2504 | -47.076 | -8.6879 | 0.13874 | -8.4191 | -0.023943 | 0.034501 | 48.1616 | -0.001436 | 48.118 | 3.7172 | 0.8949 | 0.75164 | 0.69395 | 0.82487 | 0.81024 | 0.98463 | 39.3727 | 48.1994 | 39.6415 | 48.0367 | 48.0951 | 96.2222 | 48.0592 | 96.1786 | -8.7224 | -8.6864 | -8.4536 | -8.4177
1342.5938 | 121.5866 | -48.0469 | 73.4299 | -44.3892 | -47.1245 | -47.2815 | -47.3392 | -47.2037 | -47.2229 | -47.0439 | -8.6924 | 0.15248 | -8.4237 | -0.03768 | 0.043657 | 48.1295 | -0.001436 | 48.086 | 3.6576 | 0.92238 | 0.76538 | 0.70769 | 0.84318 | 0.82398 | 1.0029 | 39.3544 | 48.1994 | 39.6232 | 48.0092 | 48.0905 | 96.1764 | 48.0454 | 96.1328 | -8.7361 | -8.691 | -8.4673 | -8.4222
1343.5938 | 121.6003 | -48.0286 | 73.439 | -44.4762 | -47.1474 | -47.3044 | -47.3621 | -47.2083 | -47.2321 | -47.0485 | -8.697 | 0.15248 | -8.4283 | -0.03768 | 0.039079 | 48.125 | 0.007721 | 48.0722 | 3.5523 | 0.88117 | 0.72418 | 0.66649 | 0.8203 | 0.79651 | 0.98006 | 39.3315 | 48.181 | 39.6003 | 47.9909 | 48.0676 | 96.1535 | 48.0363 | 96.1008 | -8.7361 | -8.7047 | -8.4673 | -8.436
1344.5938 | 121.7102 | -47.9828 | 73.4482 | -44.5037 | -47.1153 | -47.2815 | -47.3255 | -47.1762 | -47.2183 | -47.021 | -8.6924 | 0.14332 | -8.4191 | -0.033101 | 0.039079 | 48.1066 | 0.003143 | 48.0585 | 3.4791 | 0.86745 | 0.7013 | 0.65734 | 0.80657 | 0.76447 | 0.96175 | 39.2904 | 48.1261 | 39.5637 | 47.9497 | 48.0219 | 96.0894 | 47.9859 | 96.0413 | -8.7315 | -8.6956 | -8.4582 | -8.4222
1345.5938 | 121.701 | -47.9599 | 73.439 | -44.522 | -47.0879 | -47.254 | -47.3071 | -47.1396 | -47.1863 | -46.989 | -8.6924 | 0.15248 | -8.4237 | -0.03768 | 0.043657 | 48.0746 | 0.003143 | 47.825 | 3.4379 | 0.87203 | 0.70588 | 0.65276 | 0.8203 | 0.77363 | 0.97091 | 39.2675 | 48.1124 | 39.5362 | 47.9222 | 48.0036 | 96.0345 | 47.963 | 95.7849 | -8.7361 | -8.6956 | -8.4673 | -8.4268
1346.5938 | 121.7285 | -47.9187 | 73.5306 | -44.7692 | -47.3489 | -47.4738 | -47.6276 | -47.3181 | -47.3603 | -47.2042 | -8.6924 | 0.15706 | -8.4328 | -0.033101 | 0.043657 | 48.0288 | 0.012299 | 47.7838 | 3.1495 | 0.56984 | 0.44491 | 0.29107 | 0.60056 | 0.55845 | 0.71453 | 39.2263 | 48.0758 | 39.4859 | 47.8856 | 47.9624 | 95.9475 | 47.931 | 95.7025 | -8.7361 | -8.7047 | -8.4765 | -8.4451
1347.5938 | 121.7194 | -47.8821 | 73.5626 | -44.9066 | -47.4954 | -47.5928 | -47.8062 | -47.3914 | -47.4518 | -47.3095 | -8.697 | 0.16164 | -8.4237 | -0.03768 | 0.039079 | 48.0105 | 0.007721 | 47.7609 | 2.9755 | 0.3867 | 0.28924 | 0.075887 | 0.49069 | 0.43026 | 0.57261 | 39.1851 | 48.0437 | 39.4584 | 47.8444 | 47.9212 | 95.8926 | 47.8898 | 95.643 | -8.7361 | -8.7047 | -8.4628 | -8.4314
1348.5938 | 121.6873 | -47.8958 | 73.5947 | -44.9295 | -47.4633 | -47.5745 | -47.7879 | -47.3731 | -47.4518 | -47.2866 | -8.697 | 0.14332 | -8.4237 | -0.033101 | 0.039079 | 47.9922 | 0.003143 | 47.7426 | 2.9663 | 0.43248 | 0.32129 | 0.10793 | 0.52274 | 0.44399 | 0.60924 | 39.1988 | 48.0391 | 39.4721 | 47.8627 | 47.9349 | 95.888 | 47.899 | 95.6384 | -8.7361 | -8.7002 | -8.4628 | -8.4268
1349.5938 | 121.637 | -47.8363 | 73.6679 | -44.8745 | -47.3809 | -47.4875 | -47.6734 | -47.2815 | -47.3603 | -47.2133 | -8.697 | 0.15248 | -8.4237 | -0.03768 | 0.039079 | 47.9373 | 0.012299 | 47.6922 | 2.9618 | 0.45539 | 0.34877 | 0.16289 | 0.55479 | 0.47605 | 0.62298 | 39.1393 | 47.9888 | 39.4126 | 47.7986 | 47.8754 | 95.7736 | 47.8486 | 95.5285 | -8.7361 | -8.7093 | -8.4628 | -8.436
1350.5938 | 121.6873 | -47.8317 | 73.7137 | -44.8517 | -47.1245 | -47.2632 | -47.3804 | -47.0938 | -47.1725 | -46.9798 | -8.697 | 0.1479 | -8.4237 | -0.023943 | 0.039079 | 47.9189 | 0.003143 | 47.6785 | 2.9801 | 0.70723 | 0.56855 | 0.45133 | 0.73791 | 0.65919 | 0.85189 | 39.1347 | 47.9796 | 39.408 | 47.8078 | 47.8708 | 95.7507 | 47.8349 | 95.5102 | -8.7361 | -8.7002 | -8.4628 | -8.4268
1351.5938 | 121.7239 | -47.7859 | 73.7549 | -45.0119 | -47.184 | -47.3273 | -47.4765 | -47.1396 | -47.2275 | -47.0439 | -8.6924 | 0.15706 | -8.4328 | -0.028522 | 0.039079 | 47.8961 | 0.007721 | 47.6648 | 2.7741 | 0.60193 | 0.45867 | 0.30941 | 0.64635 | 0.55847 | 0.74202 | 39.0935 | 47.943 | 39.3531 | 47.7574 | 47.825 | 95.682 | 47.7937 | 95.4507 | -8.7315 | -8.7002 | -8.4719 | -8.4406
1352.5938 | 121.7514 | -47.7448 | 73.7549 | -45.2042 | -47.3397 | -47.4555 | -47.6551 | -47.2403 | -47.3328 | -47.1584 | -8.6924 | 0.13874 | -8.4237 | -0.03768 | 0.043657 | 47.864 | 0.003143 | 47.6144 | 2.5406 | 0.40505 | 0.28927 | 0.089649 | 0.50444 | 0.41197 | 0.58637 | 39.0523 | 47.8835 | 39.3211 | 47.7071 | 47.7884 | 95.6088 | 47.7479 | 95.3592 | -8.7361 | -8.6956 | -8.4673 | -8.4268
1353.5938 | 121.7697 | -47.7448 | 73.7961 | -45.2317 | -47.2939 | -47.4051 | -47.6002 | -47.1854 | -47.2778 | -47.1126 | -8.697 | 0.1479 | -8.4283 | -0.033101 | 0.039079 | 47.8274 | 0.007721 | 47.5915 | 2.5131 | 0.45084 | 0.33964 | 0.14459 | 0.55937 | 0.46691 | 0.63215 | 39.0477 | 47.8927 | 39.3165 | 47.7116 | 47.7838 | 95.5721 | 47.7525 | 95.3363 | -8.7361 | -8.7047 | -8.4673 | -8.436
1354.5938 | 121.7743 | -47.6761 | 73.851 | -45.1584 | -47.1199 | -47.2494 | -47.4033 | -47.0251 | -47.1496 | -46.9478 | -8.6924 | 0.13874 | -8.4099 | -0.033101 | 0.039079 | 47.777 | -0.001436 | 47.532 | 2.5177 | 0.55617 | 0.42664 | 0.2728 | 0.65094 | 0.52644 | 0.7283 | 38.9836 | 47.8148 | 39.2661 | 47.643 | 47.7152 | 95.4531 | 47.6746 | 95.2081 | -8.7315 | -8.691 | -8.449 | -8.4085
1355.5938 | 121.7834 | -47.6898 | 73.851 | -44.8104 | -46.5796 | -46.8099 | -46.7577 | -46.6406 | -46.788 | -46.4991 | -8.6924 | 0.14332 | -8.4237 | -0.033101 | 0.039079 | 47.7862 | 0.007721 | 47.5457 | 2.8794 | 1.1102 | 0.87992 | 0.9321 | 1.0492 | 0.90187 | 1.1907 | 38.9974 | 47.8331 | 39.2661 | 47.6567 | 47.7289 | 95.476 | 47.6975 | 95.2356 | -8.7315 | -8.7002 | -8.4628 | -8.4314
1356.5938 | 121.8155 | -47.5937 | 73.9288 | -44.8425 | -46.5659 | -46.7916 | -46.7302 | -46.6223 | -46.7651 | -46.4808 | -8.697 | 0.15706 | -8.4283 | -0.033101 | 0.043657 | 47.7404 | 0.012299 | 47.5091 | 2.7512 | 1.0278 | 0.80211 | 0.86344 | 0.9714 | 0.82863 | 1.1129 | 38.8967 | 47.7507 | 39.1654 | 47.5606 | 47.6373 | 95.3341 | 47.606 | 95.1028 | -8.7407 | -8.7093 | -8.4719 | -8.4406
1357.5938 | 121.7422 | -47.6349 | 73.9792 | -44.8288 | -46.5155 | -46.755 | -46.6845 | -46.5948 | -46.7422 | -46.435 | -8.697 | 0.13874 | -8.4283 | -0.033101 | 0.048236 | 47.7175 | 0.012299 | 47.4816 | 2.8061 | 1.1194 | 0.87993 | 0.95043 | 1.0401 | 0.89272 | 1.1999 | 38.9379 | 47.7736 | 39.2066 | 47.6018 | 47.6831 | 95.3524 | 47.6472 | 95.1165 | -8.7453 | -8.7093 | -8.4765 | -8.4406
1358.5938 | 121.8338 | -47.5479 | 73.9883 | -44.8013 | -46.4606 | -46.6954 | -46.6249 | -46.5399 | -46.6826 | -46.3801 | -8.7016 | 0.15248 | -8.4237 | -0.033101 | 0.048236 | 47.6717 | 0.007721 | 47.4175 | 2.7466 | 1.0873 | 0.85248 | 0.92297 | 1.008 | 0.86526 | 1.1678 | 38.8463 | 47.7004 | 39.1242 | 47.5148 | 47.5961 | 95.2196 | 47.5556 | 94.9655 | -8.7498 | -8.7093 | -8.4719 | -8.4314
1359.5938 | 121.8155 | -47.5708 | 73.9792 | -44.8425 | -46.4697 | -46.7183 | -46.6387 | -46.5719 | -46.6872 | -46.4076 | -8.6924 | 0.14332 | -8.4237 | -0.033101 | 0.039079 | 47.6809 | 0.003143 | 47.4267 | 2.7283 | 1.1011 | 0.85248 | 0.93213 | 0.99887 | 0.88357 | 1.1632 | 38.8784 | 47.7141 | 39.1471 | 47.5377 | 47.6099 | 95.2517 | 47.5739 | 94.9975 | -8.7315 | -8.6956 | -8.4628 | -8.4268
1360.5938 | 121.843 | -47.5067 | 74.0387 | -44.8929 | -46.5338 | -46.6725 | -46.7074 | -46.5811 | -46.6918 | -46.435 | -8.697 | 0.1479 | -8.4283 | -0.03768 | 0.039079 | 47.6122 | 0.003143 | 47.3626 | 2.6139 | 0.97288 | 0.83418 | 0.79936 | 0.92563 | 0.81491 | 1.0717 | 38.8097 | 47.6546 | 39.0785 | 47.469 | 47.5458 | 95.1189 | 47.5099 | 94.8693 | -8.7361 | -8.7002 | -8.4673 | -8.4314
1361.5938 | 121.8201 | -47.4472 | 74.1302 | -44.9295 | -46.5384 | -46.6405 | -46.7028 | -46.6223 | -46.6918 | -46.4533 | -8.7016 | 0.15706 | -8.4283 | -0.033101 | 0.043657 | 47.5939 | 0.007721 | 47.3489 | 2.5177 | 0.9088 | 0.80672 | 0.74443 | 0.82492 | 0.7554 | 0.99386 | 38.7456 | 47.6043 | 39.0189 | 47.4141 | 47.4909 | 95.0411 | 47.4549 | 94.7961 | -8.7453 | -8.7093 | -8.4719 | -8.436
1362.5938 | 121.8521 | -47.493 | 74.0982 | -44.9753 | -46.5521 | -46.6588 | -46.7074 | -46.6269 | -46.701 | -46.4762 | -8.7016 | 0.14332 | -8.4328 | -0.033101 | 0.039079 | 47.571 | 0.007721 | 47.3397 | 2.5177 | 0.94083 | 0.83418 | 0.78563 | 0.86611 | 0.79202 | 1.0167 | 38.7914 | 47.6363 | 39.0601 | 47.4599 | 47.5321 | 95.064 | 47.5007 | 94.8327 | -8.7407 | -8.7093 | -8.4719 | -8.4406
1363.5938 | 121.7651 | -47.4747 | 74.176 | -44.9982 | -46.5155 | -46.6313 | -46.6845 | -46.5994 | -46.6872 | -46.4533 | -8.6924 | 0.15706 | -8.4283 | -0.033101 | 0.039079 | 47.5481 | 0.003143 | 47.3031 | 2.4765 | 0.95916 | 0.84334 | 0.79021 | 0.87527 | 0.78744 | 1.0213 | 38.7822 | 47.6317 | 39.0464 | 47.4416 | 47.5137 | 95.0228 | 47.4778 | 94.7778 | -8.7315 | -8.6956 | -8.4673 | -8.4314
1364.5938 | 121.7606 | -47.4152 | 74.2218 | -44.9341 | -46.4285 | -46.5398 | -46.5929 | -46.5124 | -46.6002 | -46.3618 | -8.6924 | 0.1479 | -8.4374 | -0.033101 | 0.048236 | 47.5069 | 0.007721 | 47.2619 | 2.4811 | 0.98664 | 0.8754 | 0.82227 | 0.90274 | 0.81492 | 1.0534 | 38.7227 | 47.5631 | 38.9777 | 47.3821 | 47.4634 | 94.9221 | 47.4229 | 94.677 | -8.7407 | -8.7002 | -8.4856 | -8.4451
1365.5938 | 121.8842 | -47.374 | 74.1852 | -45.4285 | -46.4148 | -46.5169 | -46.5792 | -46.4941 | -46.6002 | -46.3526 | -8.6924 | 0.15248 | -8.4237 | -0.03768 | 0.048236 | 47.5069 | 0.003143 | 47.2665 | 1.9454 | 0.95918 | 0.8571 | 0.79481 | 0.87985 | 0.77372 | 1.0213 | 38.6815 | 47.5264 | 38.9503 | 47.3363 | 47.4222 | 94.8809 | 47.3771 | 94.6404 | -8.7407 | -8.6956 | -8.4719 | -8.4268
1366.5938 | 121.8704 | -47.4152 | 74.1806 | -45.9322 | -46.4239 | -46.526 | -46.5792 | -46.4895 | -46.614 | -46.3572 | -8.7016 | 0.15706 | -8.4237 | -0.028522 | 0.043657 | 47.5023 | 0.003143 | 47.2665 | 1.483 | 0.99122 | 0.88914 | 0.83601 | 0.92563 | 0.80119 | 1.058 | 38.7136 | 47.5722 | 38.9915 | 47.3866 | 47.4588 | 94.9175 | 47.4183 | 94.6816 | -8.7453 | -8.7047 | -8.4673 | -8.4268
1367.5938 | 121.8933 | -47.3465 | 74.2447 | -45.8497 | -46.4148 | -46.4986 | -46.5563 | -46.4712 | -46.5773 | -46.3389 | -8.7016 | 0.1479 | -8.4283 | -0.033101 | 0.048236 | 47.4749 | 0.003143 | 47.2344 | 1.4968 | 0.93172 | 0.84795 | 0.79023 | 0.87528 | 0.76915 | 1.0076 | 38.6449 | 47.4944 | 38.9182 | 47.3134 | 47.3947 | 94.8214 | 47.3496 | 94.5809 | -8.7498 | -8.7047 | -8.4765 | -8.4314
1368.5938 | 121.8979 | -47.3465 | 74.231 | -45.749 | -46.4102 | -46.4986 | -46.5608 | -46.4712 | -46.5865 | -46.3389 | -8.697 | 0.13874 | -8.4237 | -0.033101 | 0.039079 | 47.4749 | 0.007721 | 47.2298 | 1.5975 | 0.9363 | 0.84795 | 0.78565 | 0.87528 | 0.75999 | 1.0076 | 38.6495 | 47.4852 | 38.9228 | 47.3134 | 47.3856 | 94.8214 | 47.3542 | 94.5763 | -8.7361 | -8.7047 | -8.4628 | -8.4314
1369.5938 | 121.8979 | -47.3282 | 74.2676 | -45.6162 | -46.3827 | -46.4711 | -46.5379 | -46.4529 | -46.5545 | -46.316 | -8.7016 | 0.13874 | -8.4283 | -0.028522 | 0.048236 | 47.4337 | -0.006014 | 47.1932 | 1.7119 | 0.94546 | 0.85711 | 0.79024 | 0.87528 | 0.77373 | 1.0122 | 38.6266 | 47.4669 | 38.8999 | 47.2997 | 47.3764 | 94.7619 | 47.3222 | 94.5214 | -8.7498 | -8.6956 | -8.4765 | -8.4222
1370.5938 | 121.8109 | -47.3282 | 74.382 | -45.163 | -46.3507 | -46.439 | -46.4967 | -46.4071 | -46.4949 | -46.2702 | -8.6879 | 0.15706 | -8.4328 | -0.033101 | 0.043657 | 47.397 | 0.007721 | 47.1474 | 2.1652 | 0.97751 | 0.88916 | 0.83144 | 0.92106 | 0.83325 | 1.058 | 38.6403 | 47.4852 | 38.8954 | 47.2951 | 47.3718 | 94.7252 | 47.3359 | 94.4756 | -8.7315 | -8.6956 | -8.4765 | -8.4406
1371.5938 | 121.8063 | -47.2504 | 74.4186 | -45.5888 | -46.2042 | -46.2467 | -46.309 | -46.2332 | -46.2935 | -46.11 | -8.6924 | 0.14332 | -8.4191 | -0.03768 | 0.043657 | 47.3192 | 0.007721 | 47.0833 | 1.6616 | 1.0462 | 1.0036 | 0.94134 | 1.0172 | 0.95688 | 1.1404 | 38.5579 | 47.3937 | 38.8313 | 47.2127 | 47.294 | 94.5696 | 47.2581 | 94.3337 | -8.7361 | -8.7002 | -8.4628 | -8.4268
1372.5938 | 121.9345 | -47.1451 | 74.5102 | -46.1977 | -46.2545 | -46.2696 | -46.3319 | -46.2561 | -46.3118 | -46.1466 | -8.7016 | 0.15248 | -8.4328 | -0.03768 | 0.043657 | 47.2505 | 0.003143 | 47.0192 | 0.94738 | 0.89056 | 0.87546 | 0.81316 | 0.88903 | 0.83328 | 0.99847 | 38.4435 | 47.2976 | 38.7122 | 47.1074 | 47.1887 | 94.3956 | 47.1482 | 94.1643 | -8.7453 | -8.7047 | -8.4765 | -8.436
1373.5938 | 121.9528 | -47.1039 | 74.5239 | -46.0329 | -46.108 | -46.1048 | -46.1625 | -46.0867 | -46.1516 | -45.991 | -8.7062 | 0.1479 | -8.4237 | -0.033101 | 0.039079 | 47.2231 | 0.012299 | 46.978 | 1.071 | 0.99588 | 0.99909 | 0.94137 | 1.0172 | 0.95233 | 1.1129 | 38.3977 | 47.2518 | 38.6802 | 47.0708 | 47.143 | 94.327 | 47.1162 | 94.0819 | -8.7453 | -8.7185 | -8.4628 | -8.436
1374.5938 | 121.9528 | -47.0673 | 74.5926 | -46.0603 | -46.1172 | -46.1323 | -46.1946 | -46.105 | -46.1241 | -46.0093 | -8.7016 | 0.14332 | -8.4283 | -0.028522 | 0.039079 | 47.1773 | -0.001436 | 46.946 | 1.0069 | 0.9501 | 0.935 | 0.8727 | 0.96228 | 0.94318 | 1.058 | 38.3657 | 47.2106 | 38.639 | 47.0387 | 47.1063 | 94.2446 | 47.0658 | 94.0133 | -8.7407 | -8.7002 | -8.4673 | -8.4268
1375.5938 | 121.9574 | -47.0489 | 74.6063 | -46.0603 | -46.1172 | -46.1231 | -46.19 | -46.1096 | -46.1241 | -46.0138 | -8.7062 | 0.15706 | -8.4328 | -0.03768 | 0.039079 | 47.1544 | 0.003143 | 46.9185 | 0.9886 | 0.93179 | 0.92584 | 0.85897 | 0.93939 | 0.92486 | 1.0351 | 38.3428 | 47.206 | 38.6161 | 47.0113 | 47.088 | 94.2034 | 47.0521 | 93.9675 | -8.7453 | -8.7093 | -8.4719 | -8.436
1376.5938 | 121.9574 | -46.994 | 74.6567 | -45.9917 | -46.0622 | -46.0727 | -46.1305 | -46.0455 | -46.06 | -45.9635 | -8.7016 | 0.16622 | -8.4283 | -0.033101 | 0.039079 | 47.1132 | 0.003143 | 46.8727 | 1.0023 | 0.93181 | 0.92128 | 0.86356 | 0.94855 | 0.93403 | 1.0305 | 38.2924 | 47.1602 | 38.5658 | 46.9609 | 47.0331 | 94.1072 | 46.9972 | 93.8668 | -8.7407 | -8.7047 | -8.4673 | -8.4314
1377.5938 | 121.8567 | -46.9803 | 74.7391 | -45.9963 | -46.0622 | -46.0727 | -46.1305 | -46.0455 | -46.0554 | -45.9635 | -8.7062 | 0.15248 | -8.4283 | -0.03768 | 0.048236 | 47.0766 | 0.007721 | 46.8453 | 0.98404 | 0.91807 | 0.90754 | 0.84982 | 0.93482 | 0.92488 | 1.0168 | 38.2741 | 47.1328 | 38.552 | 46.9426 | 47.0285 | 94.0569 | 46.988 | 93.8256 | -8.7544 | -8.7139 | -8.4765 | -8.436
1378.5938 | 121.9208 | -46.9803 | 74.7116 | -46.0146 | -46.0805 | -46.0773 | -46.1305 | -46.0546 | -46.0691 | -45.9726 | -8.6924 | 0.1479 | -8.4328 | -0.033101 | 0.048236 | 47.0628 | 0.007721 | 46.8224 | 0.96572 | 0.89976 | 0.90297 | 0.84982 | 0.92566 | 0.91114 | 1.0076 | 38.2878 | 47.1282 | 38.5475 | 46.9472 | 47.0285 | 94.0431 | 46.988 | 93.8027 | -8.7407 | -8.7002 | -8.4811 | -8.4406
1379.5938 | 121.9849 | -46.9254 | 74.7437 | -46.0146 | -46.0805 | -46.0682 | -46.1305 | -46.0546 | -46.0691 | -45.991 | -8.7062 | 0.1479 | -8.4328 | -0.033101 | 0.043657 | 47.0354 | 0.007721 | 46.8041 | 0.91079 | 0.84483 | 0.85719 | 0.79489 | 0.87073 | 0.85621 | 0.9344 | 38.2192 | 47.0733 | 38.4925 | 46.8923 | 46.969 | 93.9607 | 46.9331 | 93.7294 | -8.7498 | -8.7139 | -8.4765 | -8.4406
1380.5938 | 121.9894 | -46.8704 | 74.8077 | -45.9734 | -46.0347 | -46.0315 | -46.0938 | -46.0043 | -46.0234 | -45.9406 | -8.7016 | 0.14332 | -8.4237 | -0.033101 | 0.034501 | 46.9988 | 0.007721 | 46.772 | 0.89706 | 0.83568 | 0.83889 | 0.77659 | 0.86616 | 0.84706 | 0.92983 | 38.1688 | 47.0137 | 38.4467 | 46.8373 | 46.9049 | 93.8692 | 46.8781 | 93.6424 | -8.7361 | -8.7093 | -8.4582 | -8.4314
1381.5938 | 122.0078 | -46.8109 | 74.8581 | -45.9184 | -45.9752 | -45.9766 | -46.0297 | -45.9448 | -45.9638 | -45.8811 | -8.7062 | 0.14332 | -8.4283 | -0.03768 | 0.043657 | 46.9301 | 0.007721 | 46.7079 | 0.8925 | 0.8357 | 0.83432 | 0.78118 | 0.86616 | 0.84707 | 0.92984 | 38.1047 | 46.9542 | 38.3827 | 46.7732 | 46.8546 | 93.741 | 46.8186 | 93.5188 | -8.7498 | -8.7139 | -8.4719 | -8.436
1382.5938 | 121.9986 | -46.7972 | 74.8947 | -45.9047 | -45.9569 | -45.9491 | -46.0068 | -45.9264 | -45.941 | -45.8628 | -8.7062 | 0.15248 | -8.4283 | -0.033101 | 0.048236 | 46.9072 | 0.003143 | 46.6713 | 0.8925 | 0.84028 | 0.84806 | 0.79034 | 0.87074 | 0.85623 | 0.93442 | 38.091 | 46.9497 | 38.3689 | 46.7641 | 46.8454 | 93.7044 | 46.8003 | 93.4685 | -8.7544 | -8.7093 | -8.4765 | -8.4314
1383.5938 | 121.9894 | -46.7926 | 74.881 | -45.9184 | -45.9706 | -45.9537 | -46.016 | -45.9356 | -45.9455 | -45.8673 | -8.7016 | 0.13874 | -8.4237 | -0.033101 | 0.039079 | 46.9118 | -0.001436 | 46.6896 | 0.87419 | 0.82197 | 0.83891 | 0.7766 | 0.85701 | 0.84707 | 0.92526 | 38.091 | 46.9313 | 38.3689 | 46.7595 | 46.8317 | 93.7044 | 46.7912 | 93.4822 | -8.7407 | -8.7002 | -8.4628 | -8.4222
1384.5938 | 121.9254 | -46.8018 | 74.9268 | -45.9093 | -45.9706 | -45.9445 | -46.0068 | -45.9173 | -45.941 | -45.8719 | -8.7062 | 0.1479 | -8.4374 | -0.03768 | 0.034501 | 46.8843 | -0.001436 | 46.6576 | 0.8925 | 0.83112 | 0.85722 | 0.79491 | 0.88447 | 0.86081 | 0.92984 | 38.0956 | 46.9497 | 38.3643 | 46.7641 | 46.8363 | 93.6861 | 46.8003 | 93.4593 | -8.7407 | -8.7047 | -8.4719 | -8.436
1385.5938 | 122.0032 | -46.7514 | 74.9725 | -45.8772 | -45.9432 | -45.9171 | -45.984 | -45.8852 | -45.9226 | -45.8307 | -8.7016 | 0.15248 | -8.4283 | -0.03768 | 0.043657 | 46.866 | 0.003143 | 46.6209 | 0.87419 | 0.80824 | 0.83434 | 0.76745 | 0.86617 | 0.82877 | 0.92069 | 38.0498 | 46.9039 | 38.3231 | 46.7137 | 46.7951 | 93.6174 | 46.7545 | 93.3723 | -8.7453 | -8.7047 | -8.4719 | -8.4314
1386.5938 | 122.0032 | -46.6919 | 74.9725 | -45.836 | -45.8974 | -45.8804 | -45.9336 | -45.8532 | -45.8723 | -45.7804 | -8.7062 | 0.1479 | -8.4328 | -0.033101 | 0.034501 | 46.8156 | 0.003143 | 46.5843 | 0.85589 | 0.79452 | 0.81146 | 0.75831 | 0.8387 | 0.81962 | 0.91154 | 37.9857 | 46.8398 | 38.2591 | 46.6588 | 46.7264 | 93.5075 | 46.695 | 93.2762 | -8.7407 | -8.7093 | -8.4673 | -8.436
1387.5938 | 122.0352 | -46.6324 | 75.0687 | -45.8085 | -45.8699 | -45.8438 | -45.9107 | -45.8257 | -45.8448 | -45.7529 | -8.7062 | 0.14332 | -8.4237 | -0.03768 | 0.043657 | 46.7607 | 0.007721 | 46.5202 | 0.82385 | 0.76248 | 0.78857 | 0.72169 | 0.80666 | 0.78758 | 0.8795 | 37.9262 | 46.7757 | 38.2087 | 46.5947 | 46.676 | 93.3931 | 46.6401 | 93.1526 | -8.7498 | -8.7139 | -8.4673 | -8.4314
1388.5938 | 122.0398 | -46.582 | 75.1556 | -45.7628 | -45.8287 | -45.8072 | -45.8649 | -45.7754 | -45.799 | -45.7071 | -8.7062 | 0.15248 | -8.4283 | -0.033101 | 0.039079 | 46.7195 | 0.012299 | 46.4882 | 0.81928 | 0.75334 | 0.77485 | 0.71712 | 0.80666 | 0.78301 | 0.87493 | 37.8759 | 46.7345 | 38.1538 | 46.5489 | 46.6211 | 93.3015 | 46.5943 | 93.0702 | -8.7453 | -8.7185 | -8.4673 | -8.4406
1389.5938 | 122.0032 | -46.5637 | 75.1144 | -45.6895 | -45.7554 | -45.7248 | -45.7917 | -45.7067 | -45.7258 | -45.6339 | -8.7062 | 0.1479 | -8.4283 | -0.03768 | 0.043657 | 46.6737 | 0.003143 | 46.4424 | 0.87422 | 0.80829 | 0.83895 | 0.77207 | 0.85702 | 0.83796 | 0.92987 | 37.8575 | 46.7116 | 38.1355 | 46.526 | 46.6074 | 93.2374 | 46.5669 | 93.0061 | -8.7498 | -8.7093 | -8.4719 | -8.4314
1390.5938 | 122.0352 | -46.55 | 75.1923 | -45.7536 | -45.815 | -45.7843 | -45.8512 | -45.7708 | -45.7853 | -45.6888 | -8.7016 | 0.15706 | -8.442 | -0.028522 | 0.039079 | 46.66 | 0.007721 | 46.4195 | 0.79639 | 0.73503 | 0.7657 | 0.69881 | 0.7792 | 0.7647 | 0.8612 | 37.8484 | 46.707 | 38.108 | 46.5215 | 46.5891 | 93.21 | 46.5577 | 92.9695 | -8.7407 | -8.7093 | -8.4811 | -8.4497
1391.5938 | 121.9803 | -46.5637 | 75.2289 | -45.7032 | -45.7646 | -45.7477 | -45.8145 | -45.7204 | -45.7349 | -45.6384 | -8.7062 | 0.15706 | -8.4374 | -0.03768 | 0.043657 | 46.6417 | 0.007721 | 46.4058 | 0.86049 | 0.79913 | 0.81606 | 0.74917 | 0.84329 | 0.8288 | 0.92529 | 37.8575 | 46.7208 | 38.1263 | 46.526 | 46.6074 | 93.2054 | 46.5714 | 92.9695 | -8.7498 | -8.7139 | -8.4811 | -8.4451
1392.5938 | 122.0627 | -46.5271 | 75.2243 | -45.6758 | -45.7371 | -45.7156 | -45.7733 | -45.6975 | -45.7075 | -45.6155 | -8.7108 | 0.13874 | -8.4328 | -0.033101 | 0.043657 | 46.6371 | 0.003143 | 46.3966 | 0.85134 | 0.78998 | 0.81149 | 0.75376 | 0.82956 | 0.81965 | 0.91156 | 37.8163 | 46.6658 | 38.0943 | 46.494 | 46.5708 | 93.1642 | 46.5302 | 92.9237 | -8.7544 | -8.7139 | -8.4765 | -8.436
1393.5938 | 122.0581 | -46.4767 | 75.2747 | -45.5979 | -45.6547 | -45.6286 | -45.6955 | -45.606 | -45.6296 | -45.5286 | -8.7062 | 0.15248 | -8.4283 | -0.028522 | 0.043657 | 46.5913 | 0.003143 | 46.3508 | 0.87882 | 0.82205 | 0.84813 | 0.78124 | 0.87076 | 0.84713 | 0.94819 | 37.7706 | 46.6292 | 38.0485 | 46.4482 | 46.5204 | 93.0681 | 46.4799 | 92.8276 | -8.7498 | -8.7093 | -8.4719 | -8.4314
1394.5938 | 122.0764 | -46.4081 | 75.3387 | -45.5201 | -45.5814 | -45.5554 | -45.6223 | -45.5327 | -45.5518 | -45.4599 | -8.7016 | 0.1479 | -8.4283 | -0.033101 | 0.043657 | 46.5501 | 0.007721 | 46.3051 | 0.88798 | 0.82664 | 0.85272 | 0.78583 | 0.87535 | 0.85629 | 0.9482 | 37.7065 | 46.556 | 37.9798 | 46.375 | 46.4517 | 92.9582 | 46.4158 | 92.7131 | -8.7453 | -8.7093 | -8.4719 | -8.436
1395.5938 | 122.0398 | -46.4264 | 75.293 | -45.4697 | -45.5311 | -45.4958 | -45.5627 | -45.4824 | -45.4923 | -45.4095 | -8.697 | 0.15248 | -8.4374 | -0.028522 | 0.029923 | 46.5318 | 0.003143 | 46.2959 | 0.95666 | 0.89532 | 0.93055 | 0.86366 | 0.94401 | 0.93412 | 1.0169 | 37.7294 | 46.5789 | 37.989 | 46.3979 | 46.4563 | 92.9582 | 46.4295 | 92.7223 | -8.7269 | -8.7002 | -8.4673 | -8.4406
1396.5938 | 122.0856 | -46.4127 | 75.3571 | -45.4468 | -45.5082 | -45.4821 | -45.5398 | -45.4549 | -45.4831 | -45.3866 | -8.7062 | 0.14332 | -8.4283 | -0.033101 | 0.034501 | 46.5181 | 0.007721 | 46.2776 | 0.96582 | 0.90448 | 0.93056 | 0.87282 | 0.95775 | 0.92955 | 1.026 | 37.7065 | 46.556 | 37.9844 | 46.3796 | 46.4472 | 92.9307 | 46.4204 | 92.6902 | -8.7407 | -8.7139 | -8.4628 | -8.436
1397.5938 | 122.0764 | -46.344 | 75.4028 | -45.4056 | -45.4578 | -45.4363 | -45.4986 | -45.4183 | -45.4373 | -45.3546 | -8.7108 | 0.16164 | -8.4283 | -0.03768 | 0.039079 | 46.486 | 0.003143 | 46.241 | 0.93836 | 0.88619 | 0.90768 | 0.84536 | 0.92571 | 0.90667 | 0.98941 | 37.6332 | 46.5056 | 37.9157 | 46.3063 | 46.3831 | 92.83 | 46.3471 | 92.5849 | -8.7498 | -8.7139 | -8.4673 | -8.4314
1398.5938 | 121.9986 | -46.3806 | 75.4532 | -45.3873 | -45.4487 | -45.4272 | -45.4941 | -45.4046 | -45.4236 | -45.3409 | -8.7108 | 0.15248 | -8.4328 | -0.03768 | 0.039079 | 46.4723 | 0.012299 | 46.2272 | 0.99329 | 0.93196 | 0.95346 | 0.88656 | 0.97606 | 0.95702 | 1.0398 | 37.6699 | 46.5331 | 37.9478 | 46.3429 | 46.4197 | 92.8529 | 46.3929 | 92.6078 | -8.7498 | -8.7231 | -8.4719 | -8.4451
1399.5938 | 122.0581 | -46.3394 | 75.4852 | -45.3461 | -45.4074 | -45.3814 | -45.4528 | -45.3588 | -45.3732 | -45.2996 | -8.7062 | 0.14332 | -8.4328 | -0.028522 | 0.039079 | 46.4402 | 0.007721 | 46.1998 | 0.9933 | 0.93198 | 0.95804 | 0.88657 | 0.98064 | 0.96619 | 1.0398 | 37.6332 | 46.4827 | 37.9066 | 46.3109 | 46.3785 | 92.7796 | 46.3471 | 92.5392 | -8.7453 | -8.7139 | -8.4719 | -8.4406
1400.5938 | 122.0718 | -46.3165 | 75.4715 | -45.3141 | -45.3662 | -45.3356 | -45.4025 | -45.3176 | -45.3412 | -45.2584 | -8.7016 | 0.15248 | -8.4374 | -0.03768 | 0.048236 | 46.3899 | 0.003143 | 46.1402 | 1.0025 | 0.9503 | 0.98094 | 0.91405 | 0.99896 | 0.97535 | 1.0581 | 37.6149 | 46.469 | 37.8791 | 46.2788 | 46.3648 | 92.7064 | 46.3197 | 92.4568 | -8.7498 | -8.7047 | -8.4856 | -8.4406
1401.5938 | 122.0947 | -46.2616 | 75.5219 | -45.2958 | -45.3525 | -45.3264 | -45.3933 | -45.3084 | -45.3274 | -45.2539 | -8.7153 | 0.1479 | -8.4374 | -0.03768 | 0.039079 | 46.367 | 0.007721 | 46.1265 | 0.96584 | 0.9091 | 0.93517 | 0.86827 | 0.95318 | 0.93415 | 1.0077 | 37.5463 | 46.4095 | 37.8242 | 46.2239 | 46.3007 | 92.6286 | 46.2693 | 92.3881 | -8.7544 | -8.7231 | -8.4765 | -8.4451
1402.5938 | 122.0947 | -46.1975 | 75.5951 | -45.2271 | -45.2884 | -45.2761 | -45.3292 | -45.2443 | -45.2679 | -45.1989 | -8.7062 | 0.15706 | -8.4374 | -0.033101 | 0.034501 | 46.3075 | 0.007721 | 46.0807 | 0.97043 | 0.90912 | 0.92145 | 0.86828 | 0.95319 | 0.92958 | 0.99858 | 37.4913 | 46.3546 | 37.7601 | 46.1644 | 46.232 | 92.505 | 46.2052 | 92.2782 | -8.7407 | -8.7139 | -8.4719 | -8.4451
1403.5938 | 122.0764 | -46.1929 | 75.6088 | -45.2271 | -45.2655 | -45.2532 | -45.3109 | -45.2306 | -45.245 | -45.1806 | -8.7108 | 0.15248 | -8.4328 | -0.03768 | 0.043657 | 46.3029 | 0.003143 | 46.0578 | 0.96585 | 0.92743 | 0.93976 | 0.88202 | 0.96234 | 0.9479 | 1.0123 | 37.4822 | 46.3454 | 37.7601 | 46.1553 | 46.2366 | 92.4958 | 46.1961 | 92.2508 | -8.7544 | -8.7139 | -8.4765 | -8.436
1404.5938 | 122.0535 | -46.1792 | 75.6683 | -45.163 | -45.2289 | -45.2028 | -45.2697 | -45.1848 | -45.2038 | -45.1394 | -8.7062 | 0.13416 | -8.4328 | -0.028522 | 0.043657 | 46.2525 | 0.003143 | 46.0075 | 1.0162 | 0.95033 | 0.97639 | 0.90949 | 0.99439 | 0.97537 | 1.0398 | 37.473 | 46.3134 | 37.7464 | 46.1507 | 46.2229 | 92.4317 | 46.1823 | 92.1867 | -8.7498 | -8.7093 | -8.4765 | -8.436
1405.5938 | 121.9345 | -46.17 | 75.7004 | -45.1401 | -45.206 | -45.1845 | -45.2468 | -45.1573 | -45.1764 | -45.1165 | -8.7062 | 0.15248 | -8.4374 | -0.033101 | 0.048236 | 46.2251 | 0.003143 | 45.9892 | 1.03 | 0.96407 | 0.98555 | 0.92323 | 1.0127 | 0.99368 | 1.0535 | 37.4639 | 46.3225 | 37.7326 | 46.1369 | 46.2183 | 92.3951 | 46.1732 | 92.1592 | -8.7544 | -8.7093 | -8.4856 | -8.4406
1406.5938 | 122.0535 | -46.0144 | 75.7874 | -45.0531 | -45.1052 | -45.0838 | -45.1415 | -45.0521 | -45.0756 | -45.0158 | -8.7108 | 0.15248 | -8.4283 | -0.028522 | 0.043657 | 46.1427 | 0.003143 | 45.893 | 0.9613 | 0.90916 | 0.93064 | 0.8729 | 0.96235 | 0.93877 | 0.9986 | 37.3037 | 46.1669 | 37.5861 | 45.9859 | 46.0581 | 92.1571 | 46.0175 | 91.9074 | -8.7544 | -8.7139 | -8.4719 | -8.4314
1407.5938 | 122.0215 | -46.0327 | 75.8423 | -45.0302 | -45.0915 | -45.07 | -45.1278 | -45.0475 | -45.0665 | -45.0066 | -8.7153 | 0.15248 | -8.4283 | -0.03768 | 0.048236 | 46.1289 | 0.012299 | 45.8839 | 1.0025 | 0.94121 | 0.96269 | 0.90494 | 0.98524 | 0.96624 | 1.0261 | 37.3174 | 46.1852 | 37.6045 | 45.995 | 46.081 | 92.1616 | 46.045 | 91.9166 | -8.7636 | -8.7276 | -8.4765 | -8.4406
1408.5938 | 122.0078 | -46.0144 | 75.8469 | -45.0165 | -45.0732 | -45.0517 | -45.1095 | -45.0292 | -45.0436 | -44.9883 | -8.7062 | 0.14332 | -8.4374 | -0.03768 | 0.043657 | 46.1106 | 0.003143 | 45.8655 | 0.99793 | 0.94122 | 0.96269 | 0.90494 | 0.98524 | 0.97082 | 1.0261 | 37.3082 | 46.1577 | 37.577 | 45.9767 | 46.0581 | 92.125 | 46.0175 | 91.88 | -8.7498 | -8.7093 | -8.4811 | -8.4406
1409.5938 | 122.0123 | -46.0373 | 75.8926 | -45.0211 | -45.0778 | -45.0517 | -45.114 | -45.02 | -45.0573 | -45.0021 | -8.7108 | 0.15248 | -8.4328 | -0.033101 | 0.039079 | 46.0923 | 0.007721 | 45.8564 | 1.0162 | 0.95952 | 0.98558 | 0.92325 | 1.0173 | 0.97997 | 1.0352 | 37.3265 | 46.1898 | 37.6045 | 46.0042 | 46.0764 | 92.1296 | 46.045 | 91.8937 | -8.7498 | -8.7185 | -8.4719 | -8.4406
1410.5938 | 122.0261 | -45.9915 | 75.9155 | -45.0119 | -45.064 | -45.0426 | -45.1049 | -45.0246 | -45.0436 | -44.9975 | -8.7108 | 0.1479 | -8.442 | -0.028522 | 0.043657 | 46.0831 | 0.012299 | 45.8472 | 0.97962 | 0.92749 | 0.94896 | 0.88663 | 0.96693 | 0.94793 | 0.99403 | 37.2808 | 46.1394 | 37.5495 | 45.963 | 46.0352 | 92.0747 | 46.0038 | 91.8387 | -8.7544 | -8.7231 | -8.4856 | -8.4543
1411.5938 | 122.081 | -45.9 | 76.0071 | -44.9615 | -45.0274 | -45.0013 | -45.0454 | -44.9742 | -44.9978 | -44.9425 | -8.7062 | 0.15706 | -8.4374 | -0.033101 | 0.043657 | 46.0282 | 0.003143 | 45.7969 | 0.93843 | 0.87256 | 0.89861 | 0.8546 | 0.92574 | 0.90216 | 0.95741 | 37.1938 | 46.057 | 37.4626 | 45.8669 | 45.9436 | 91.9282 | 45.9031 | 91.6968 | -8.7498 | -8.7093 | -8.4811 | -8.4406
1412.5938 | 122.0718 | -45.8725 | 76.0345 | -44.9158 | -44.9862 | -44.9556 | -45.0179 | -44.933 | -44.952 | -44.9059 | -8.7153 | 0.15706 | -8.4328 | -0.033101 | 0.043657 | 45.9916 | 0.007721 | 45.7602 | 0.95675 | 0.88631 | 0.91694 | 0.85461 | 0.93948 | 0.92048 | 0.96657 | 37.1572 | 46.0296 | 37.4397 | 45.8394 | 45.9162 | 91.8641 | 45.8802 | 91.6327 | -8.759 | -8.7231 | -8.4765 | -8.4406
1413.5938 | 122.0764 | -45.8267 | 76.0712 | -44.8654 | -44.9267 | -44.9006 | -44.9538 | -44.8781 | -44.8971 | -44.8373 | -8.7108 | 0.1479 | -8.442 | -0.033101 | 0.043657 | 45.9321 | 0.007721 | 45.7053 | 0.96133 | 0.90006 | 0.9261 | 0.87293 | 0.94863 | 0.92964 | 0.98947 | 37.116 | 45.9746 | 37.3847 | 45.7936 | 45.8704 | 91.7588 | 45.8344 | 91.532 | -8.7544 | -8.7185 | -8.4856 | -8.4497
1414.5938 | 122.0856 | -45.8221 | 76.0895 | -44.8471 | -44.8992 | -44.8823 | -44.9401 | -44.8598 | -44.8742 | -44.8235 | -8.7108 | 0.15248 | -8.442 | -0.023943 | 0.048236 | 45.9275 | -0.001436 | 45.6962 | 0.97507 | 0.92295 | 0.93984 | 0.88209 | 0.96237 | 0.94796 | 0.99863 | 37.1114 | 45.9746 | 37.3802 | 45.7982 | 45.8704 | 91.7496 | 45.8207 | 91.5183 | -8.759 | -8.7093 | -8.4902 | -8.4406
1415.5938 | 122.0901 | -45.7764 | 76.1307 | -44.815 | -44.8717 | -44.8548 | -44.908 | -44.8323 | -44.8421 | -44.796 | -8.7153 | 0.15248 | -8.442 | -0.03768 | 0.039079 | 45.8954 | 0.003143 | 45.6687 | 0.96134 | 0.90465 | 0.92153 | 0.86836 | 0.94406 | 0.93423 | 0.98032 | 37.061 | 45.9288 | 37.3344 | 45.7387 | 45.8154 | 91.6718 | 45.7795 | 91.4451 | -8.7544 | -8.7185 | -8.4811 | -8.4451
1416.5938 | 122.1085 | -45.7352 | 76.1993 | -44.7738 | -44.8305 | -44.809 | -44.876 | -44.782 | -44.7964 | -44.7548 | -8.7062 | 0.15706 | -8.4328 | -0.028522 | 0.043657 | 45.8542 | 0.007721 | 45.6229 | 0.96135 | 0.90466 | 0.92612 | 0.85921 | 0.95322 | 0.93881 | 0.98032 | 37.029 | 45.8922 | 37.3023 | 45.7066 | 45.7788 | 91.5894 | 45.7429 | 91.3581 | -8.7498 | -8.7139 | -8.4765 | -8.4406
1417.5938 | 122.049 | -45.7077 | 76.2451 | -44.7463 | -44.8076 | -44.7816 | -44.8439 | -44.7591 | -44.778 | -44.7411 | -8.7153 | 0.16164 | -8.4328 | -0.033101 | 0.052814 | 45.813 | 0.012299 | 45.5909 | 0.96135 | 0.90009 | 0.92613 | 0.8638 | 0.94864 | 0.92966 | 0.96659 | 36.9924 | 45.8693 | 37.2749 | 45.6746 | 45.7605 | 91.5207 | 45.72 | 91.2986 | -8.7681 | -8.7276 | -8.4856 | -8.4451
1418.5938 | 122.1039 | -45.6573 | 76.3138 | -44.7051 | -44.7664 | -44.7495 | -44.8119 | -44.7224 | -44.7414 | -44.6908 | -8.7153 | 0.1479 | -8.4466 | -0.028522 | 0.048236 | 45.7581 | 0.007721 | 45.5268 | 0.95221 | 0.89094 | 0.90782 | 0.84549 | 0.93491 | 0.91594 | 0.9666 | 36.942 | 45.8052 | 37.2108 | 45.6288 | 45.7056 | 91.4154 | 45.6651 | 91.1841 | -8.7636 | -8.7231 | -8.4948 | -8.4543
1419.5938 | 122.1451 | -45.5933 | 76.3367 | -44.6823 | -44.7389 | -44.7083 | -44.7752 | -44.6858 | -44.7048 | -44.6633 | -8.7016 | 0.15706 | -8.4328 | -0.033101 | 0.043657 | 45.7169 | 0.003143 | 45.4856 | 0.91101 | 0.85433 | 0.88495 | 0.81803 | 0.90745 | 0.88848 | 0.92998 | 36.8917 | 45.7503 | 37.1604 | 45.5602 | 45.6369 | 91.3102 | 45.5964 | 91.0788 | -8.7453 | -8.7047 | -8.4765 | -8.436
1420.5938 | 122.0718 | -45.5978 | 76.474 | -44.6731 | -44.7206 | -44.6946 | -44.7569 | -44.6767 | -44.6956 | -44.645 | -8.697 | 0.16164 | -8.442 | -0.028522 | 0.048236 | 45.694 | 0.016878 | 45.4672 | 0.92474 | 0.87722 | 0.90326 | 0.84092 | 0.92118 | 0.90221 | 0.95287 | 36.9008 | 45.7595 | 37.1558 | 45.5693 | 45.6461 | 91.2918 | 45.6147 | 91.0651 | -8.7453 | -8.7139 | -8.4902 | -8.4589
1421.5938 | 122.0718 | -45.5704 | 76.4053 | -44.6365 | -44.6977 | -44.6671 | -44.7294 | -44.6492 | -44.6682 | -44.6175 | -8.7062 | 0.14332 | -8.442 | -0.028522 | 0.043657 | 45.662 | 0.003143 | 45.4352 | 0.93391 | 0.87265 | 0.90326 | 0.84093 | 0.92119 | 0.90222 | 0.95287 | 36.8642 | 45.7137 | 37.1284 | 45.5419 | 45.614 | 91.2323 | 45.5735 | 91.0056 | -8.7498 | -8.7093 | -8.4856 | -8.4451
1422.5938 | 122.0856 | -45.5475 | 76.4191 | -44.6319 | -44.6931 | -44.6717 | -44.7294 | -44.6446 | -44.6636 | -44.6175 | -8.7153 | 0.15706 | -8.4328 | -0.028522 | 0.048236 | 45.6574 | 0.012299 | 45.4215 | 0.9156 | 0.85434 | 0.8758 | 0.81804 | 0.90287 | 0.8839 | 0.92999 | 36.8322 | 45.7045 | 37.1147 | 45.519 | 45.5957 | 91.2049 | 45.5598 | 90.9689 | -8.7636 | -8.7276 | -8.4811 | -8.4451
1423.5938 | 122.1359 | -45.4651 | 76.474 | -44.5724 | -44.6382 | -44.6076 | -44.6699 | -44.5943 | -44.6041 | -44.558 | -8.7108 | 0.15706 | -8.4374 | -0.023943 | 0.043657 | 45.5796 | 0.012299 | 45.3436 | 0.89272 | 0.82689 | 0.8575 | 0.79517 | 0.87083 | 0.86103 | 0.90711 | 36.7543 | 45.6221 | 37.0277 | 45.4411 | 45.5087 | 91.0446 | 45.4774 | 90.8087 | -8.7544 | -8.7231 | -8.4811 | -8.4497
1424.5938 | 122.1909 | -45.3873 | 76.5244 | -44.5403 | -44.597 | -44.5755 | -44.6425 | -44.5439 | -44.5629 | -44.5168 | -8.7153 | 0.15248 | -8.442 | -0.033101 | 0.043657 | 45.52 | 0.016878 | 45.2887 | 0.84694 | 0.79028 | 0.81173 | 0.74482 | 0.84337 | 0.82441 | 0.87049 | 36.6719 | 45.5397 | 36.9453 | 45.3542 | 45.4309 | 90.9073 | 45.4041 | 90.676 | -8.759 | -8.7322 | -8.4856 | -8.4589
1425.5938 | 122.2229 | -45.3644 | 76.5564 | -44.522 | -44.5741 | -44.5526 | -44.6104 | -44.5302 | -44.54 | -44.4985 | -8.7016 | 0.16164 | -8.4328 | -0.028522 | 0.048236 | 45.4926 | 0.007721 | 45.2612 | 0.84237 | 0.79028 | 0.81173 | 0.75398 | 0.83422 | 0.82442 | 0.86591 | 36.6628 | 45.526 | 36.9315 | 45.3359 | 45.4126 | 90.857 | 45.3721 | 90.6256 | -8.7498 | -8.7093 | -8.4811 | -8.4406
1426.5938 | 122.2458 | -45.3918 | 76.5335 | -44.5586 | -44.6153 | -44.603 | -44.647 | -44.5759 | -44.5903 | -44.5442 | -8.7153 | 0.14332 | -8.4328 | -0.033101 | 0.039079 | 45.5155 | 0.007721 | 45.275 | 0.83321 | 0.77654 | 0.78884 | 0.74482 | 0.8159 | 0.80152 | 0.8476 | 36.6765 | 45.5352 | 36.959 | 45.3587 | 45.4309 | 90.9073 | 45.3996 | 90.6668 | -8.7544 | -8.7231 | -8.4719 | -8.4406
1427.5938 | 122.1771 | -45.3323 | 76.6388 | -44.5266 | -44.5833 | -44.5618 | -44.6196 | -44.5302 | -44.5491 | -44.5076 | -8.7108 | 0.15706 | -8.4374 | -0.028522 | 0.052814 | 45.4605 | 0.007721 | 45.2246 | 0.80575 | 0.74908 | 0.77053 | 0.71278 | 0.80217 | 0.78322 | 0.82471 | 36.6216 | 45.4894 | 36.8949 | 45.3038 | 45.3851 | 90.7929 | 45.3401 | 90.5569 | -8.7636 | -8.7185 | -8.4902 | -8.4451
1428.5938 | 122.2046 | -45.3461 | 76.593 | -44.5541 | -44.6199 | -44.5984 | -44.6562 | -44.5668 | -44.5949 | -44.5442 | -8.7153 | 0.17079 | -8.4374 | -0.033101 | 0.048236 | 45.4834 | 0.012299 | 45.2475 | 0.79201 | 0.72618 | 0.74764 | 0.68988 | 0.77928 | 0.75117 | 0.80182 | 36.6307 | 45.5169 | 36.9087 | 45.313 | 45.3943 | 90.8295 | 45.3584 | 90.5936 | -8.7636 | -8.7276 | -8.4856 | -8.4497
1429.5938 | 122.2321 | -45.3232 | 76.6068 | -44.5678 | -44.6245 | -44.6076 | -44.6699 | -44.5805 | -44.5949 | -44.5534 | -8.7108 | 0.1479 | -8.4374 | -0.03768 | 0.043657 | 45.4743 | 0.012299 | 45.2338 | 0.75539 | 0.69872 | 0.71559 | 0.65326 | 0.74266 | 0.72828 | 0.76978 | 36.6124 | 45.4711 | 36.8858 | 45.2855 | 45.3668 | 90.7974 | 45.3355 | 90.5569 | -8.7544 | -8.7231 | -8.4811 | -8.4497
1430.5938 | 122.2183 | -45.2911 | 76.6617 | -44.5586 | -44.6153 | -44.5893 | -44.6516 | -44.5759 | -44.5857 | -44.5397 | -8.7153 | 0.15248 | -8.4328 | -0.033101 | 0.048236 | 45.4376 | 0.007721 | 45.2063 | 0.7325 | 0.67583 | 0.70186 | 0.63953 | 0.7152 | 0.70539 | 0.75147 | 36.5758 | 45.4436 | 36.8583 | 45.258 | 45.3394 | 90.7288 | 45.2989 | 90.4974 | -8.7636 | -8.7231 | -8.4811 | -8.4406
1431.5938 | 122.2412 | -45.3049 | 76.6479 | -44.5312 | -44.5833 | -44.571 | -44.6333 | -44.5485 | -44.5674 | -44.5168 | -8.7199 | 0.16622 | -8.4374 | -0.042259 | 0.048236 | 45.4239 | 0.012299 | 45.1788 | 0.7737 | 0.72162 | 0.73391 | 0.67157 | 0.7564 | 0.73744 | 0.78809 | 36.585 | 45.4711 | 36.8675 | 45.2626 | 45.3531 | 90.7288 | 45.3172 | 90.4837 | -8.7681 | -8.7322 | -8.4856 | -8.4497
1432.5938 | 122.2458 | -45.2637 | 76.6846 | -44.5129 | -44.5741 | -44.5618 | -44.615 | -44.521 | -44.5445 | -44.503 | -8.7108 | 0.1479 | -8.4374 | -0.028522 | 0.043657 | 45.3873 | 0.012299 | 45.1422 | 0.75082 | 0.68957 | 0.70187 | 0.64869 | 0.74267 | 0.71913 | 0.76063 | 36.5529 | 45.4116 | 36.8263 | 45.2351 | 45.3073 | 90.6509 | 45.276 | 90.4059 | -8.7544 | -8.7231 | -8.4811 | -8.4497
1433.5938 | 122.2366 | -45.2362 | 76.7349 | -44.4991 | -44.5558 | -44.5343 | -44.5921 | -44.5119 | -44.5308 | -44.4756 | -8.7062 | 0.14332 | -8.442 | -0.03768 | 0.043657 | 45.3461 | 0.007721 | 45.1056 | 0.73709 | 0.68042 | 0.70188 | 0.64412 | 0.72436 | 0.7054 | 0.76063 | 36.53 | 45.3795 | 36.7942 | 45.1985 | 45.2799 | 90.5823 | 45.2439 | 90.3418 | -8.7498 | -8.7139 | -8.4856 | -8.4497
1434.5938 | 122.2595 | -45.1401 | 76.8311 | -44.4396 | -44.4963 | -44.4748 | -44.5371 | -44.4569 | -44.4667 | -44.4206 | -8.7199 | 0.16164 | -8.442 | -0.03768 | 0.039079 | 45.2774 | 0.003143 | 45.0415 | 0.70048 | 0.64382 | 0.66527 | 0.60293 | 0.68316 | 0.67337 | 0.71944 | 36.4202 | 45.3017 | 36.6981 | 45.1024 | 45.1792 | 90.4175 | 45.1432 | 90.1816 | -8.759 | -8.7231 | -8.4811 | -8.4451
1435.5938 | 122.2412 | -45.108 | 76.8265 | -44.4442 | -44.51 | -44.4794 | -44.5326 | -44.4569 | -44.4713 | -44.4252 | -8.7245 | 0.15248 | -8.4283 | -0.033101 | 0.039079 | 45.2637 | 0.012299 | 45.0323 | 0.66386 | 0.59804 | 0.62864 | 0.57546 | 0.65112 | 0.63674 | 0.68282 | 36.3835 | 45.2605 | 36.6798 | 45.0749 | 45.1471 | 90.3717 | 45.1203 | 90.1403 | -8.7636 | -8.7368 | -8.4673 | -8.4406
1436.5938 | 122.2549 | -45.108 | 76.8723 | -44.4121 | -44.4734 | -44.4473 | -44.5005 | -44.4294 | -44.4392 | -44.3932 | -8.7153 | 0.15248 | -8.4374 | -0.033101 | 0.034501 | 45.227 | 0.007721 | 44.982 | 0.6959 | 0.63467 | 0.6607 | 0.60751 | 0.67858 | 0.66879 | 0.71486 | 36.3927 | 45.2605 | 36.6706 | 45.0749 | 45.1425 | 90.3351 | 45.1158 | 90.09 | -8.7498 | -8.7231 | -8.4719 | -8.4451
1437.5938 | 122.1863 | -45.0623 | 76.9501 | -44.348 | -44.4093 | -44.3924 | -44.4502 | -44.3654 | -44.3797 | -44.3382 | -8.7108 | 0.1479 | -8.4328 | -0.033101 | 0.039079 | 45.163 | 0.007721 | 44.9224 | 0.71423 | 0.653 | 0.66986 | 0.6121 | 0.6969 | 0.68254 | 0.72402 | 36.3515 | 45.2102 | 36.6294 | 45.0292 | 45.1013 | 90.2252 | 45.07 | 89.9847 | -8.7498 | -8.7185 | -8.4719 | -8.4406
1438.5938 | 122.2504 | -45.0119 | 76.9501 | -44.3435 | -44.4093 | -44.3787 | -44.4364 | -44.3608 | -44.3751 | -44.3337 | -8.7153 | 0.14332 | -8.4328 | -0.028522 | 0.048236 | 45.1446 | 0.012299 | 44.9087 | 0.66845 | 0.60264 | 0.63324 | 0.57548 | 0.65112 | 0.63676 | 0.67825 | 36.2966 | 45.1552 | 36.5791 | 44.9834 | 45.0601 | 90.1565 | 45.0242 | 89.9206 | -8.7636 | -8.7276 | -8.4811 | -8.4451
1439.5938 | 122.2733 | -44.9844 | 77.0096 | -44.3022 | -44.3635 | -44.3329 | -44.3998 | -44.315 | -44.3339 | -44.2879 | -8.7108 | 0.17995 | -8.4283 | -0.13842 | 0.043657 | 45.1034 | 0.007721 | 44.8492 | 0.68219 | 0.62097 | 0.65156 | 0.58464 | 0.66944 | 0.6505 | 0.69656 | 36.2737 | 45.1644 | 36.5562 | 44.846 | 45.0281 | 90.0879 | 44.9922 | 89.8336 | -8.7544 | -8.7185 | -8.4719 | -8.436
1440.5938 | 122.2778 | -44.9615 | 77.0096 | -44.2839 | -44.3452 | -44.3146 | -44.3723 | -44.2921 | -44.3156 | -44.2741 | -8.7108 | 0.13874 | -8.4145 | -0.14758 | 0.048236 | 45.0851 | -0.001436 | 44.8217 | 0.67762 | 0.61639 | 0.64699 | 0.58923 | 0.66944 | 0.64592 | 0.68741 | 36.2508 | 45.1003 | 36.547 | 44.814 | 45.0098 | 90.0467 | 44.9601 | 89.7833 | -8.759 | -8.7093 | -8.4628 | -8.4131

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.199 | 24.2804
0.801 | 24.2745
1.801 | 24.2792
2.801 | 24.3522
3.801 | 24.9744
4.801 | 26.3997
5.801 | 28.5885
6.801 | 31.4157
7.801 | 34.7637
8.801 | 38.523
9.801 | 42.6383
10.801 | 47.0225
11.801 | 51.6405
12.801 | 56.4997
13.801 | 61.5105
14.801 | 66.7086
15.801 | 72.0575
16.801 | 77.5417
17.801 | 83.1152
18.801 | 88.7523
19.801 | 94.5052
20.801 | 100.2787
21.801 | 106.1968
22.801 | 112.0482
23.801 | 117.9317
24.801 | 123.8906
25.801 | 129.9102
26.801 | 135.9262
27.801 | 141.9281
28.801 | 147.8504
29.801 | 153.841
30.801 | 159.7943
31.801 | 165.743
32.801 | 171.7328
33.801 | 177.6094
34.801 | 183.4951
35.801 | 189.3661
36.801 | 195.2683
37.801 | 201.1354
38.801 | 206.9957
39.801 | 212.9361
40.801 | 218.7753
41.801 | 224.6802
42.801 | 230.5222
43.801 | 236.4373
44.801 | 242.3096
45.801 | 248.197
46.801 | 254.047
47.801 | 259.8769
48.801 | 265.4779
49.801 | 271.0528
50.801 | 276.6041
51.801 | 282.1592
52.801 | 287.7195
53.801 | 293.1475
54.801 | 298.7088
55.801 | 304.3007
56.801 | 309.7029
57.801 | 315.0776
58.801 | 320.4041
59.801 | 325.8901
60.801 | 331.2331
61.801 | 336.3497
62.801 | 341.5426
63.801 | 346.8194
64.801 | 352.1353
65.801 | 357.3993
66.801 | 362.5984
67.801 | 367.8046
68.801 | 373.0385
69.801 | 378.2586
70.801 | 383.1193
71.801 | 387.9679
72.801 | 393.0132
73.801 | 398.0241
74.801 | 402.6974
75.801 | 407.5545
76.801 | 412.352
77.801 | 417.12
78.801 | 421.669
79.801 | 426.0901
80.801 | 429.9899
81.801 | 433.4174
82.801 | 436.5488
83.801 | 439.7795
84.801 | 442.6534
85.801 | 445.3207
86.801 | 448.0917
87.801 | 450.9088
88.801 | 453.5683
89.801 | 455.8198
90.801 | 457.9853
91.801 | 459.9907
92.801 | 461.8322
93.801 | 463.2246
94.801 | 464.5056
95.801 | 465.6568
96.801 | 466.4596
97.801 | 467.0016
98.801 | 467.5299
99.801 | 467.8587
100.801 | 468.2521
101.801 | 468.5045
102.801 | 468.6801
103.801 | 468.8659
104.801 | 469.1949
105.801 | 469.3567
106.801 | 469.4014
107.801 | 469.5646
108.801 | 469.7373
109.801 | 469.9128
110.801 | 469.9828
111.801 | 470.015
112.801 | 470.1224
113.801 | 470.1981
114.801 | 470.14
115.801 | 470.3012
116.801 | 470.4783
117.801 | 470.7123
118.801 | 470.78
119.801 | 470.8347
120.801 | 470.9046
121.801 | 471.2301
122.801 | 471.5353
123.801 | 471.7599
124.801 | 472.0383
125.801 | 472.1015
126.801 | 472.2043
127.801 | 472.1755
128.801 | 472.2485
129.801 | 472.3524
130.801 | 472.4411
131.801 | 472.5754
132.801 | 472.6596
133.801 | 472.8559
134.801 | 473.085
135.801 | 473.2796
136.801 | 473.4694
137.801 | 473.6807
138.801 | 473.6134
139.801 | 473.4428
140.801 | 473.3899
141.801 | 473.6533
142.801 | 473.7874
143.801 | 474.0127
144.801 | 474.1848
145.801 | 474.2866
146.801 | 474.2363
147.801 | 474.3251
148.801 | 474.4272
149.801 | 474.5544
150.801 | 474.6734
151.801 | 474.7542
152.801 | 474.8651
153.801 | 474.8587
154.801 | 474.699
155.801 | 474.9359
156.801 | 475.2082
157.801 | 475.6506
158.801 | 475.953
159.801 | 476.1116
160.801 | 476.2785
161.801 | 476.2769
162.801 | 476.36
163.801 | 476.2016
164.801 | 475.9196
165.801 | 475.8173
166.801 | 475.6918
167.801 | 475.5674
168.801 | 475.4898
169.801 | 475.5027
170.801 | 475.645
171.801 | 475.8566
172.801 | 475.9433
173.801 | 475.9954
174.801 | 475.9067
175.801 | 475.8141
176.801 | 475.8509
177.801 | 475.8264
178.801 | 475.8116
179.801 | 475.6778
180.801 | 475.7485
181.801 | 475.7356
182.801 | 475.8162
183.801 | 475.9203
184.801 | 475.897
185.801 | 475.9232
186.801 | 475.8851
187.801 | 475.7883
188.801 | 475.6182
189.801 | 475.4607
190.801 | 475.3109
191.801 | 475.2852
192.801 | 475.1807
193.801 | 475.2235
194.801 | 475.3641
195.801 | 475.3851
196.801 | 475.4636
197.801 | 475.4774
198.801 | 475.4275
199.801 | 475.5327
200.801 | 475.6982
201.801 | 475.6613
202.801 | 475.6076
203.801 | 475.3882
204.801 | 475.2843
205.801 | 475.2764
206.801 | 475.3769
207.801 | 475.3426
208.801 | 475.181
209.801 | 475.1992
210.801 | 475.274
211.801 | 475.2381
212.801 | 474.9887
213.801 | 474.81
214.801 | 474.6321
215.801 | 474.7313
216.801 | 474.6799
217.801 | 474.6436
218.801 | 474.4628
219.801 | 474.4567
220.801 | 474.4263
221.801 | 474.4595
222.801 | 474.6362
223.801 | 474.6727
224.801 | 474.711
225.801 | 474.719
226.801 | 474.8383
227.801 | 474.8719
228.801 | 474.6526
229.801 | 474.5995
230.801 | 474.7858
231.801 | 474.8998
232.801 | 475.1565
233.801 | 475.278
234.801 | 475.4229
235.801 | 475.3742
236.801 | 475.2645
237.801 | 475.112
238.801 | 475.2169
239.801 | 475.3818
240.801 | 475.5971
241.801 | 475.7383
242.801 | 475.7868
243.801 | 475.8102
244.801 | 475.7558
245.801 | 475.7316
246.801 | 475.8919
247.801 | 475.9837
248.801 | 475.8828
249.801 | 475.7644
250.801 | 475.6919
251.801 | 475.796
252.801 | 475.801
253.801 | 475.7368
254.801 | 475.7277
255.801 | 475.5525
256.801 | 475.3755
257.801 | 475.5444
258.801 | 475.6565
259.801 | 475.681
260.801 | 475.7565
261.801 | 475.6549
262.801 | 475.5185
263.801 | 475.6695
264.801 | 475.6801
265.801 | 475.6787
266.801 | 475.617
267.801 | 475.4223
268.801 | 475.2382
269.801 | 475.2235
270.801 | 475.1239
271.801 | 475.0934
272.801 | 475.2371
273.801 | 475.2048
274.801 | 475.0923
275.801 | 475.0353
276.801 | 475.0092
277.801 | 475.0373
278.801 | 475.0652
279.801 | 475.1282
280.801 | 475.1983
281.801 | 475.1537
282.801 | 475.2358
283.801 | 475.072
284.801 | 474.8963
285.801 | 474.6939
286.801 | 474.6529
287.801 | 474.7043
288.801 | 474.6496
289.801 | 474.7113
290.801 | 474.7216
291.801 | 474.6375
292.801 | 474.737
293.801 | 474.8239
294.801 | 474.8511
295.801 | 474.7849
296.801 | 474.7396
297.801 | 474.6184
298.801 | 474.5598
299.801 | 474.6563
300.801 | 474.6418
301.801 | 474.6233
302.801 | 474.5783
303.801 | 474.4237
304.801 | 474.3396
305.801 | 474.1118
306.801 | 473.9972
307.801 | 473.9634
308.801 | 473.8788
309.801 | 473.7938
310.801 | 473.9529
311.801 | 474.0633
312.801 | 474.2786
313.801 | 474.2238
314.801 | 474.1926
315.801 | 474.391
316.801 | 474.5072
317.801 | 474.3304
318.801 | 474.2668
319.801 | 474.5847
320.801 | 474.7118
321.801 | 474.635
322.801 | 474.5008
323.801 | 474.4999
324.801 | 474.4542
325.801 | 474.5115
326.801 | 474.329
327.801 | 474.1054
328.801 | 474.0422
329.801 | 473.8757
330.801 | 473.8949
331.801 | 473.9711
332.801 | 473.9244
333.801 | 473.8775
334.801 | 473.7773
335.801 | 473.8845
336.801 | 473.9139
337.801 | 473.8302
338.801 | 473.8643
339.801 | 473.8351
340.801 | 473.8649
341.801 | 473.9895
342.801 | 474.0553
343.801 | 474.0284
344.801 | 474.1195
345.801 | 474.1699
346.801 | 474.2509
347.801 | 474.3149
348.801 | 474.3799
349.801 | 474.4545
350.801 | 474.3505
351.801 | 474.3959
352.801 | 474.4864
353.801 | 474.5977
354.801 | 474.5454
355.801 | 474.408
356.801 | 474.339
357.801 | 474.3538
358.801 | 474.4265
359.801 | 474.3208
360.801 | 474.1444
361.801 | 474.0707
362.801 | 474.0482
363.801 | 473.9366
364.801 | 473.6918
365.801 | 473.5935
366.801 | 473.7453
367.801 | 473.703
368.801 | 473.651
369.801 | 473.6067
370.801 | 473.5287
371.801 | 473.5821
372.801 | 473.5758
373.801 | 473.7607
374.801 | 473.8933
375.801 | 473.9333
376.801 | 473.9938
377.801 | 473.8439
378.801 | 473.747
379.801 | 473.8099
380.801 | 473.7912
381.801 | 473.6646
382.801 | 473.5662
383.801 | 473.455
384.801 | 473.511
385.801 | 473.4895
386.801 | 473.5611
387.801 | 473.5928
388.801 | 473.6163
389.801 | 473.5543
390.801 | 473.6237
391.801 | 473.9058
392.801 | 474.0454
393.801 | 474.1681
394.801 | 474.2541
395.801 | 474.3313
396.801 | 474.3424
397.801 | 474.3128
398.801 | 474.3138
399.801 | 474.2811
400.801 | 474.15
401.801 | 474.0706
402.801 | 474.0498
403.801 | 473.9508
404.801 | 473.8444
405.801 | 473.6362
406.801 | 473.7547
407.801 | 474.0188
408.801 | 474.0768
409.8167 | 473.9962
410.801 | 474.0936
411.801 | 474.2286
412.801 | 474.3784
413.801 | 474.4561
414.801 | 474.492
415.801 | 474.6079
416.801 | 474.6958
417.801 | 474.6637
418.801 | 474.6465
419.801 | 474.7139
420.801 | 474.7402
421.801 | 474.7549
422.801 | 474.6204
423.801 | 474.4947
424.801 | 474.5232
425.801 | 474.5083
426.801 | 474.2653
427.801 | 474.2197
428.801 | 474.154
429.801 | 474.1889
430.801 | 474.2779
431.801 | 474.1921
432.801 | 474.1658
433.801 | 474.0516
434.801 | 474.0912
435.801 | 474.193
436.801 | 474.0906
437.801 | 474.042
438.801 | 473.9425
439.801 | 474.1003
440.801 | 474.2064
441.801 | 474.272
442.801 | 474.2292
443.8167 | 474.2992
444.801 | 474.1791
445.801 | 474.1088
446.801 | 474.0989
447.801 | 473.9981
448.801 | 473.881
449.801 | 473.9181
450.801 | 473.9178
451.801 | 474.0257
452.801 | 473.9995
453.801 | 473.9502
454.801 | 473.8941
455.801 | 473.9264
456.801 | 473.9341
457.801 | 473.7901
458.801 | 473.8306
459.801 | 473.7722
460.801 | 473.563
461.801 | 473.3635
462.801 | 473.2204
463.801 | 473.2783
464.801 | 473.4703
465.801 | 473.6725
466.801 | 473.7181
467.801 | 473.7304
468.801 | 473.8917
469.801 | 473.747
470.801 | 473.74
471.801 | 473.8438
472.801 | 473.7126
473.801 | 473.7435
474.801 | 473.8017
475.801 | 473.9353
476.801 | 473.9591
477.801 | 473.889
478.801 | 473.8769
479.801 | 473.7727
480.801 | 473.6919
481.801 | 473.7491
482.801 | 473.8876
483.801 | 474.017
484.801 | 474.1834
485.801 | 474.1845
486.801 | 474.2844
487.801 | 474.2462
488.801 | 474.1992
489.801 | 474.098
490.801 | 474.18
491.801 | 474.2314
492.801 | 474.3844
493.801 | 474.5325
494.801 | 474.577
495.801 | 474.4175
496.801 | 474.2638
497.801 | 474.3012
498.801 | 474.3232
499.801 | 474.4376
500.801 | 474.4608
501.801 | 474.5521
502.801 | 474.4996
503.801 | 474.5152
504.801 | 474.2214
505.801 | 473.943
506.801 | 473.8987
507.801 | 473.8615
508.801 | 473.8183
509.801 | 473.7155
510.801 | 473.7928
511.801 | 473.8064
512.801 | 473.8448
513.801 | 473.9657
514.801 | 473.9477
515.801 | 474.0232
516.801 | 474.1454
517.801 | 474.244
518.801 | 474.185
519.801 | 474.0811
520.801 | 474.0376
521.801 | 474.0417
522.801 | 474.0504
523.801 | 474.1883
524.801 | 474.2665
525.801 | 474.3062
526.801 | 474.2665
527.801 | 474.3333
528.801 | 474.398
529.801 | 474.2483
530.801 | 473.9993
531.801 | 473.9529
532.801 | 473.9665
533.801 | 473.9815
534.801 | 474.0574
535.801 | 473.9434
536.801 | 473.8317
537.801 | 473.8293
538.801 | 473.8551
539.801 | 473.9402
540.801 | 473.9466
541.801 | 474.094
542.801 | 474.0505
543.801 | 473.9132
544.801 | 473.792
545.801 | 473.8828
546.801 | 473.9561
547.801 | 473.7104
548.801 | 473.6712
549.801 | 473.6486
550.801 | 473.5794
551.801 | 473.6632
552.801 | 473.7493
553.801 | 473.5127
554.801 | 473.4161
555.801 | 473.3374
556.801 | 473.3425
557.801 | 473.2885
558.801 | 473.1263
559.801 | 473.049
560.801 | 473.219
561.801 | 473.3949
562.801 | 473.4049
563.801 | 473.5684
564.801 | 473.5901
565.801 | 473.6152
566.801 | 473.6034
567.801 | 473.69
568.801 | 473.7643
569.801 | 473.7809
570.801 | 473.7831
571.801 | 473.7449
572.801 | 473.6342
573.801 | 473.6367
574.801 | 473.7036
575.801 | 473.688
576.801 | 473.7377
577.801 | 473.7433
578.801 | 473.7577
579.801 | 473.7313
580.801 | 473.6154
581.801 | 473.4084
582.801 | 473.313
583.801 | 473.2692
584.801 | 473.1955
585.801 | 473.0364
586.801 | 472.9489
587.801 | 472.9462
588.801 | 472.8573
589.801 | 473.0293
590.801 | 473.019
591.801 | 472.8881
592.801 | 472.9031
593.801 | 472.9286
594.801 | 473.0104
595.801 | 473.1024
596.801 | 473.2408
597.801 | 473.433
598.801 | 473.4315
599.801 | 473.4827
600.801 | 473.3567
601.801 | 473.4683
602.801 | 473.6743
603.801 | 473.8018
604.801 | 473.7734
605.801 | 473.7073
606.801 | 473.7556
607.801 | 473.8407
608.801 | 473.8542
609.801 | 473.67
610.801 | 473.5607
611.801 | 473.4269
612.801 | 473.3274
613.801 | 473.2835
614.801 | 473.2924
615.801 | 473.1483
616.801 | 473.0943
617.801 | 473.0387
618.801 | 472.9867
619.801 | 473.0431
620.801 | 473.1026
621.801 | 473.1352
622.801 | 473.1551
623.801 | 473.4675
624.801 | 473.4904
625.801 | 473.4676
626.801 | 473.7197
627.801 | 473.8499
628.801 | 473.9343
629.801 | 474.0306
630.801 | 474.1286
631.801 | 474.0983
632.801 | 474.223
633.801 | 474.2538
634.801 | 474.3197
635.801 | 474.2587
636.801 | 474.3176
637.801 | 474.1642
638.801 | 474.1637
639.801 | 474.2945
640.801 | 474.3567
641.801 | 474.3683
642.801 | 474.367
643.801 | 474.3546
644.801 | 474.3482
645.801 | 474.3853
646.801 | 474.4348
647.801 | 474.3122
648.801 | 474.2802
649.801 | 474.1655
650.801 | 474.1466
651.801 | 474.1749
652.801 | 474.168
653.801 | 474.1979
654.801 | 473.991
655.801 | 473.8616
656.801 | 473.7528
657.801 | 473.5819
658.801 | 473.5185
659.801 | 473.5393
660.801 | 473.6858
661.801 | 473.784
662.801 | 473.8493
663.801 | 473.9255
664.801 | 474.0567
665.801 | 474.0874
666.801 | 474.0592
667.801 | 474.0885
668.801 | 474.1089
669.801 | 473.966
670.801 | 473.7951
671.801 | 473.8565
672.801 | 473.928
673.801 | 473.7902
674.801 | 473.7927
675.801 | 473.812
676.801 | 473.8483
677.801 | 473.9462
678.801 | 473.9372
679.801 | 473.9317
680.801 | 473.8603
681.801 | 473.8539
682.801 | 473.8361
683.801 | 473.8256
684.801 | 473.7645
685.801 | 473.7758
686.801 | 473.7646
687.801 | 473.817
688.801 | 473.7575
689.801 | 473.5746
690.801 | 473.4111
691.801 | 473.1871
692.801 | 473.11
693.801 | 472.97
694.801 | 472.9672
695.801 | 472.9251
696.801 | 472.7889
697.801 | 472.9046
698.801 | 472.9875
699.801 | 473.0414
700.801 | 473.1444
701.801 | 473.1875
702.801 | 473.3438
703.801 | 473.568
704.801 | 473.565
705.801 | 473.5673
706.801 | 473.5844
707.801 | 473.6136
708.801 | 473.7117
709.801 | 473.5961
710.801 | 473.4965
711.801 | 473.4235
712.801 | 473.4391
713.801 | 473.4142
714.801 | 473.5605
715.801 | 473.7244
716.801 | 473.9104
717.801 | 474.0455
718.801 | 474.1875
719.801 | 474.2334
720.801 | 474.2627
721.801 | 474.1316
722.801 | 473.9799
723.801 | 473.8109
724.801 | 473.7528
725.801 | 473.8451
726.801 | 474.0015
727.801 | 474.0856
728.801 | 474.1088
729.801 | 474.0907
730.801 | 474.0316
731.801 | 473.8872
732.801 | 473.8343
733.801 | 473.8226
734.801 | 473.8994
735.801 | 473.9271
736.801 | 473.9775
737.801 | 473.8514
738.801 | 473.8547
739.801 | 473.7807
740.801 | 473.5466
741.801 | 473.4532
742.801 | 473.3764
743.801 | 473.2954
744.801 | 473.2325
745.801 | 473.1783
746.801 | 473.1194
747.801 | 473.0179
748.801 | 472.9884
749.801 | 472.9214
750.801 | 472.8167
751.801 | 472.7985
752.801 | 472.9461
753.801 | 473.0675
754.801 | 473.2645
755.801 | 473.4037
756.801 | 473.4505
757.801 | 473.4885
758.801 | 473.5226
759.801 | 473.4818
760.801 | 473.356
761.801 | 473.3295
762.801 | 473.2383
763.801 | 473.0817
764.801 | 473.0909
765.801 | 473.0414
766.801 | 473.031
767.801 | 473.1046
768.801 | 473.0622
769.801 | 473.0925
770.801 | 473.2162
771.801 | 473.3412
772.801 | 473.5672
773.801 | 473.6549
774.801 | 473.5211
775.801 | 473.4572
776.801 | 473.5889
777.801 | 473.6358
778.801 | 473.6279
779.801 | 473.6869
780.801 | 473.8061
781.801 | 473.8765
782.801 | 473.8506
783.801 | 473.9045
784.801 | 473.9352
785.801 | 474.105
786.801 | 474.0883
787.801 | 473.9056
788.801 | 473.8323
789.801 | 473.7065
790.801 | 473.802
791.801 | 473.8568
792.801 | 473.9385
793.801 | 474.02
794.801 | 474.1016
795.801 | 474.0946
796.801 | 474.1743
797.801 | 474.2683
798.801 | 474.2197
799.801 | 474.2813
800.801 | 474.2237
801.801 | 474.3075
802.801 | 474.2888
803.801 | 474.1401
804.801 | 473.9904
805.801 | 473.9758
806.801 | 473.9023
807.801 | 473.8152
808.801 | 473.7844
809.801 | 473.84
810.801 | 473.9621
811.801 | 474.0567
812.801 | 474.0454
813.801 | 473.8743
814.801 | 473.5899
815.801 | 473.6049
816.801 | 473.6741
817.801 | 473.7418
818.801 | 473.6883
819.801 | 473.5486
820.801 | 473.4908
821.801 | 473.5542
822.801 | 473.6663
823.801 | 473.858
824.801 | 474.0009
825.801 | 474.0564
826.801 | 474.0756
827.801 | 474.1551
828.801 | 474.2687
829.801 | 474.3772
830.801 | 474.3413
831.801 | 474.4351
832.801 | 474.2405
833.801 | 474.1129
834.801 | 474.054
835.801 | 474.0591
836.801 | 474.0803
837.801 | 473.9662
838.801 | 473.8181
839.801 | 473.8464
840.801 | 473.8616
841.801 | 473.8997
842.801 | 473.8766
843.801 | 473.8121
844.801 | 473.7191
845.801 | 473.585
846.801 | 473.6549
847.801 | 473.6417
848.801 | 473.4292
849.801 | 473.1465
850.801 | 472.9888
851.801 | 473.0037
852.801 | 473.1673
853.801 | 473.3076
854.801 | 473.2905
855.801 | 473.3391
856.801 | 473.3962
857.801 | 473.2988
858.801 | 473.3303
859.801 | 473.5867
860.801 | 473.6596
861.801 | 473.5245
862.801 | 473.4899
863.801 | 473.3158
864.801 | 473.3653
865.801 | 473.2295
866.801 | 473.2057
867.801 | 473.2367
868.801 | 473.1853
869.801 | 473.223
870.801 | 473.3288
871.801 | 473.3321
872.801 | 473.2472
873.801 | 473.2288
874.801 | 473.0786
875.801 | 473.0789
876.801 | 473.0671
877.801 | 472.9557
878.801 | 473.1
879.801 | 473.2804
880.801 | 473.4744
881.801 | 473.7084
882.801 | 473.7901
883.801 | 473.8766
884.801 | 474.0713
885.801 | 474.1798
886.801 | 474.2235
887.801 | 474.3448
888.801 | 474.5507
889.801 | 474.6047
890.801 | 474.5272
891.801 | 474.4716
892.801 | 474.4955
893.801 | 474.4709
894.801 | 474.5419
895.801 | 474.4386
896.801 | 474.3939
897.801 | 474.4221
898.801 | 474.4111
899.801 | 474.4488
900.801 | 474.4733
901.801 | 474.3072
902.801 | 474.1964
903.801 | 474.0042
904.801 | 473.8204
905.801 | 473.703
906.801 | 473.7501
907.801 | 473.8412
908.801 | 473.8489
909.801 | 473.9423
910.801 | 473.9282
911.801 | 473.8028
912.801 | 473.7494
913.801 | 473.6913
914.801 | 473.5595
915.801 | 473.5304
916.801 | 473.4366
917.801 | 473.35
918.801 | 473.3391
919.801 | 473.3541
920.801 | 473.2886
921.801 | 473.2699
922.801 | 473.2397
923.801 | 473.2777
924.801 | 473.1615
925.801 | 472.9983
926.801 | 472.845
927.801 | 472.5806
928.801 | 472.4551
929.801 | 472.4957
930.801 | 472.4243
931.801 | 472.3772
932.801 | 472.2989
933.801 | 472.1741
934.801 | 471.9278
935.801 | 471.7411
936.801 | 471.5951
937.801 | 471.4856
938.801 | 471.5448
939.801 | 471.4987
940.801 | 471.3776
941.801 | 471.3304
942.801 | 471.2993
943.801 | 471.1966
944.801 | 471.2615
945.801 | 471.302
946.801 | 471.2448
947.801 | 471.2122
948.801 | 471.1016
949.801 | 471.0639
950.801 | 471.0308
951.801 | 471.0357
952.801 | 471.0917
953.801 | 471.1888
954.801 | 471.3046
955.801 | 471.3142
956.801 | 471.333
957.801 | 471.2347
958.801 | 471.2034
959.801 | 471.2293
960.801 | 471.2991
961.801 | 471.1122
962.801 | 470.9515
963.801 | 470.8387
964.801 | 470.8305
965.801 | 470.9031
966.801 | 470.9755
967.801 | 470.9596
968.801 | 470.9459
969.801 | 470.8338
970.801 | 470.8593
971.801 | 470.9594
972.801 | 470.8719
973.801 | 470.8006
974.801 | 470.7085
975.801 | 470.6414
976.801 | 470.7309
977.801 | 470.757
978.801 | 470.8126
979.801 | 470.8637
980.801 | 470.8941
981.801 | 470.7203
982.801 | 470.8886
983.801 | 470.946
984.801 | 470.9855
985.801 | 470.9705
986.801 | 470.8981
987.801 | 471.0372
988.801 | 471.0872
989.801 | 470.9539
990.801 | 470.9573
991.801 | 471.0319
992.801 | 471.0007
993.801 | 471.0275
994.801 | 470.8861
995.801 | 470.9375
996.801 | 470.9715
997.801 | 470.8496
998.801 | 470.7803
999.801 | 470.7236
1000.801 | 470.7242
1001.801 | 470.6768
1002.801 | 470.728
1003.801 | 470.7533
1004.801 | 470.6884
1005.801 | 470.6508
1006.801 | 470.7221
1007.801 | 470.6178
1008.801 | 470.6287
1009.801 | 470.4801
1010.801 | 470.371
1011.801 | 470.3237
1012.801 | 470.2213
1013.801 | 470.2078
1014.801 | 470.1156
1015.801 | 470.0484
1016.801 | 469.966
1017.801 | 469.9911
1018.801 | 469.9739
1019.801 | 469.9786
1020.801 | 469.7767
1021.801 | 469.5679
1022.801 | 469.4224
1023.801 | 469.3944
1024.801 | 469.3535
1025.801 | 469.2838
1026.801 | 469.2839
1027.801 | 469.2493
1028.801 | 469.2275
1029.801 | 469.2801
1030.801 | 469.3949
1031.801 | 469.5987
1032.801 | 469.5207
1033.801 | 469.5189
1034.801 | 469.522
1035.801 | 469.539
1036.801 | 469.4606
1037.801 | 469.4015
1038.801 | 469.4097
1039.801 | 469.3908
1040.801 | 469.3895
1041.801 | 469.5112
1042.801 | 469.4477
1043.801 | 469.3863
1044.801 | 469.4293
1045.801 | 469.3958
1046.801 | 469.3288
1047.801 | 469.2861
1048.801 | 469.2247
1049.801 | 469.111
1050.801 | 468.9731
1051.801 | 468.8096
1052.801 | 468.6293
1053.801 | 468.565
1054.801 | 468.3777
1055.801 | 468.2795
1056.801 | 468.2113
1057.801 | 468.1631
1058.801 | 468.1996
1059.801 | 468.1205
1060.801 | 468.1651
1061.801 | 468.1686
1062.801 | 468.3107
1063.801 | 468.4946
1064.801 | 468.4732
1065.801 | 468.1952
1066.801 | 467.9328
1067.801 | 467.9243
1068.801 | 467.736
1069.801 | 467.733
1070.801 | 467.7078
1071.801 | 467.7342
1072.801 | 467.7992
1073.801 | 467.7269
1074.801 | 467.6568
1075.801 | 467.6652
1076.801 | 467.6958
1077.801 | 467.8301
1078.801 | 467.7809
1079.801 | 467.8445
1080.801 | 467.9318
1081.801 | 467.9141
1082.801 | 467.8641
1083.801 | 467.6693
1084.801 | 467.6463
1085.801 | 467.7163
1086.801 | 467.7926
1087.801 | 467.827
1088.801 | 467.7601
1089.801 | 467.74
1090.801 | 467.755
1091.801 | 467.7093
1092.801 | 467.6497
1093.801 | 467.4944
1094.801 | 467.5138
1095.801 | 467.4983
1096.801 | 467.5087
1097.801 | 467.582
1098.801 | 467.6502
1099.801 | 467.684
1100.801 | 467.7006
1101.801 | 467.7658
1102.801 | 467.6005
1103.801 | 467.4491
1104.801 | 467.4448
1105.801 | 467.4149
1106.801 | 467.2691
1107.801 | 467.2354
1108.801 | 467.3632
1109.801 | 467.3087
1110.801 | 467.2941
1111.801 | 467.1977
1112.801 | 467.2149
1113.801 | 467.2951
1114.801 | 467.4255
1115.801 | 467.4144
1116.801 | 467.2849
1117.801 | 467.1165
1118.801 | 467.0607
1119.801 | 467.1134
1120.801 | 467.0842
1121.801 | 466.8834
1122.801 | 466.7846
1123.801 | 466.8084
1124.801 | 466.9093
1125.801 | 466.9405
1126.801 | 467.0204
1127.801 | 467.041
1128.801 | 466.936
1129.801 | 466.8697
1130.801 | 466.9151
1131.801 | 466.7905
1132.801 | 466.8793
1133.801 | 466.9171
1134.801 | 466.9923
1135.801 | 466.8263
1136.801 | 466.8184
1137.801 | 466.8362
1138.801 | 466.8361
1139.801 | 466.6476
1140.801 | 466.6569
1141.801 | 466.7529
1142.801 | 466.6926
1143.801 | 466.7455
1144.801 | 466.8761
1145.801 | 466.9075
1146.801 | 466.8087
1147.801 | 466.6855
1148.801 | 466.6056
1149.801 | 466.6886
1150.801 | 466.8443
1151.801 | 466.9382
1152.801 | 466.9489
1153.801 | 467.0506
1154.801 | 467.1216
1155.801 | 467.1433
1156.801 | 467.0431
1157.801 | 467.1614
1158.801 | 467.1499
1159.801 | 467.1503
1160.801 | 467.134
1161.801 | 467.0898
1162.801 | 467.1612
1163.801 | 467.0619
1164.801 | 466.8657
1165.801 | 466.9786
1166.801 | 467.0917
1167.801 | 467.0569
1168.801 | 466.8496
1169.801 | 466.7101
1170.801 | 466.7877
1171.801 | 466.84
1172.801 | 466.8541
1173.801 | 466.9571
1174.801 | 466.8637
1175.801 | 466.9844
1176.801 | 467.0951
1177.801 | 467.2973
1178.801 | 467.3173
1179.801 | 467.2399
1180.801 | 467.2271
1181.801 | 467.3103
1182.801 | 467.3972
1183.801 | 467.3637
1184.801 | 467.3346
1185.801 | 467.4003
1186.801 | 467.4902
1187.801 | 467.598
1188.801 | 467.6546
1189.801 | 467.668
1190.801 | 467.7224
1191.801 | 467.7605
1192.801 | 467.8201
1193.801 | 467.7633
1194.801 | 467.7933
1195.801 | 467.7208
1196.801 | 467.9047
1197.801 | 467.9095
1198.801 | 467.8403
1199.801 | 467.8831
1200.801 | 468.0193
1201.801 | 468.1222
1202.801 | 468.139
1203.801 | 468.1713
1204.801 | 468.2098
1205.801 | 468.3247
1206.801 | 468.4068
1207.801 | 468.4696
1208.801 | 468.6097
1209.801 | 468.582
1210.801 | 468.5762
1211.801 | 468.49
1212.801 | 468.4033
1213.801 | 468.1485
1214.801 | 468.1731
1215.801 | 468.2269
1216.801 | 468.2513
1217.801 | 468.255
1218.801 | 468.3195
1219.801 | 468.314
1220.801 | 468.4036
1221.801 | 468.4362
1222.801 | 468.5589
1223.801 | 468.6851
1224.801 | 468.7308
1225.801 | 468.8177
1226.801 | 469.0488
1227.801 | 469.0657
1228.801 | 469.0674
1229.801 | 469.1717
1230.801 | 469.201
1231.801 | 469.2951
1232.801 | 469.4583
1233.801 | 469.4311
1234.801 | 469.514
1235.801 | 469.628
1236.801 | 469.7181
1237.801 | 469.7314
1238.801 | 469.7043
1239.801 | 469.687
1240.801 | 469.7198
1241.801 | 469.872
1242.801 | 470.0374
1243.801 | 470.1178
1244.801 | 470.1938
1245.801 | 470.17
1246.801 | 470.0876
1247.801 | 470.0504
1248.801 | 470.0919
1249.801 | 470.1431
1250.801 | 470.1932
1251.801 | 470.2898
1252.801 | 470.4164
1253.801 | 470.4016
1254.801 | 470.4662
1255.801 | 470.5355
1256.801 | 470.5887
1257.801 | 470.6674
1258.801 | 470.6889
1259.801 | 470.8044
1260.801 | 470.9104
1261.801 | 470.9867
1262.801 | 470.8893
1263.801 | 470.8516
1264.801 | 470.8677
1265.801 | 471.0302
1266.801 | 471.1657
1267.801 | 471.2986
1268.801 | 471.3221
1269.801 | 471.35
1270.801 | 471.4157
1271.801 | 471.3354
1272.801 | 471.3972
1273.801 | 471.5201
1274.801 | 471.4164
1275.801 | 471.4338
1276.801 | 471.5566
1277.801 | 471.732
1278.801 | 471.7816
1279.801 | 471.6324
1280.801 | 471.7195
1281.801 | 471.6554
1282.801 | 471.6083
1283.801 | 471.6856
1284.801 | 471.6176
1285.801 | 471.6269
1286.801 | 471.7363
1287.801 | 471.6603
1288.801 | 471.732
1289.801 | 471.765
1290.801 | 471.8064
1291.801 | 471.9172
1292.801 | 471.9187
1293.801 | 471.8968
1294.801 | 471.8023
1295.801 | 471.7624
1296.801 | 471.8123
1297.801 | 471.7791
1298.801 | 471.7297
1299.801 | 471.5585
1300.801 | 471.5517
1301.801 | 471.6987
1302.801 | 471.7471
1303.801 | 471.8994
1304.801 | 471.8636
1305.801 | 471.7918
1306.801 | 471.7586
1307.801 | 471.8623
1308.801 | 471.9237
1309.801 | 471.9145
1310.801 | 471.8553
1311.801 | 471.9084
1312.801 | 471.9009
1313.801 | 471.9713
1314.801 | 471.9386
1315.801 | 471.8612
1316.801 | 471.8665
1317.801 | 472.0166
1318.801 | 472.0659
1319.801 | 472.1741
1320.801 | 472.1514
1321.801 | 472.1994
1322.801 | 472.124
1323.801 | 471.9628
1324.801 | 471.7496
1325.801 | 471.6432
1326.801 | 471.4942
1327.801 | 471.3536
1328.801 | 471.347
1329.801 | 471.3378
1330.801 | 471.3401
1331.801 | 471.3199
1332.801 | 471.2146
1333.801 | 471.1807
1334.801 | 471.1891
1335.801 | 471.2266
1336.801 | 471.2701
1337.801 | 471.1403
1338.801 | 471.1358
1339.801 | 471.1378
1340.801 | 471.2412
1341.801 | 471.322
1342.801 | 471.2498
1343.801 | 471.2784
1344.801 | 471.3093
1345.801 | 471.5303
1346.801 | 471.6105
1347.801 | 471.6146
1348.801 | 471.5971
1349.801 | 471.5087
1350.801 | 471.4191
1351.801 | 471.2901
1352.801 | 471.1219
1353.801 | 471.0594
1354.801 | 471.0364
1355.801 | 471.0843
1356.801 | 471.0329
1357.801 | 471.0807
1358.801 | 471.0932
1359.801 | 471.0495
1360.801 | 471.0461
1361.801 | 471.0842
1362.801 | 471.164
1363.801 | 471.2426
1364.801 | 471.2215
1365.801 | 471.3679
1366.801 | 471.3727
1367.801 | 471.4023
1368.801 | 471.5287
1369.801 | 471.4887
1370.801 | 471.5723
1371.801 | 471.5665
1372.801 | 471.4467
1373.801 | 471.5329
1374.801 | 471.637
1375.801 | 471.6929
1376.801 | 471.7329
1377.801 | 471.8083
1378.801 | 471.9131
1379.801 | 471.9836
1380.801 | 471.9534
1381.801 | 471.7959
1382.801 | 471.8002
1383.801 | 471.8203
1384.801 | 471.7903
1385.801 | 471.7254
1386.801 | 471.6151
1387.801 | 471.5576
1388.801 | 471.346
1389.801 | 471.3308
1390.801 | 471.362
1391.801 | 471.2734
1392.801 | 471.1675
1393.801 | 470.9938
1394.801 | 470.8423
1395.801 | 470.768
1396.801 | 470.8302
1397.801 | 470.878
1398.801 | 470.921
1399.801 | 470.9796
1400.801 | 471.2
1401.801 | 471.0931
1402.801 | 470.9523
1403.801 | 470.9258
1404.801 | 470.9026
1405.801 | 471.0125
1406.801 | 471.1682
1407.801 | 471.2713
1408.801 | 471.2025
1409.801 | 471.2228
1410.801 | 471.3854
1411.801 | 471.3039
1412.801 | 471.0727
1413.801 | 471.0075
1414.801 | 470.9767
1415.801 | 470.8631
1416.801 | 470.9328
1417.801 | 470.8639
1418.801 | 470.7753
1419.801 | 470.7329
1420.801 | 470.7512
1421.801 | 470.8725
1422.801 | 470.8886
1423.801 | 470.9302
1424.801 | 471.0307
1425.801 | 471.0385
1426.801 | 471.037
1427.801 | 471.097
1428.801 | 470.9995
1429.801 | 470.9367
1430.801 | 471.1934
1431.801 | 471.4418
1432.801 | 471.535
1433.801 | 471.5499
1434.801 | 471.4816
1435.801 | 471.4638
1436.801 | 471.4269
1437.801 | 471.5526
1438.801 | 471.5626
1439.801 | 471.5551
1440.801 | 471.4437