## Test Conditions
DESIREE-FIRE Test Number 6 - Circuit Data Data Only
Test Date: | 2009-07-22
DCSim DAQ Start Time | 15:39
DCSim Time for Synchronization | 15:51
Heat Source Synchronization | 6:53 | hours:minutes:seconds
Heat Source DAQ Start Time | 15:44
Fire Time | 15:53
Offset | 0:14 | hours:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 815 | seconds
Heat Source Offset | 0:09 | hours:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 533 | seconds
Heat Source Stop Time | 16:14
Test Duration | 0:21 | hours:minutes:seconds
| 1270 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Not Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
1" Solenoid Valve | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
Large Coil | XLPE, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | 1"Coil_CT500 | 1"Coil_CT35_1_P | 1"Coil_CT35_2_G | 1"Coil_CT35_3_R | 1"Coil_CT35_4_N2 | 1"Coil_CT35_5_S | 1"Coil_CT35_6_N1 | LgCoil_CT500 | LgCoil_CT35_1_P | LgCoil_CT35_2_G | LgCoil_CT35_3_N2 | LgCoil_CT35_4_S | LgCoil_CT35_5_N1 | 1"Coil_VT7_1_G | 1"Coil_VT7_2_R | 1"Coil_VT7_3_SP | 1"Coil_VT7_4_S | 1"Coil_VTU_1_P | 1"Coil_VTU_2_N2 | 1"Coil_VTU_3_N1 | LgCoil_VT7_1_R | LgCoil_VT7_2_SP | LgCoil_VT7_3_S | LgCoil_VTU_1_P | LgCoil_VTU_2_G | LgCoil_VTU_3_N2 | LgCoil_VTU_4_N1 | {1"Valve} V(N2) - V(Batt -) | {1"Valve} V(N1) - V(Batt -) | {1"Valve} V(P) - V(Batt +) | {1"Valve} V(R) - V(Batt -) | {1"Valve} V(S) - V(Batt -) | {1"Valve} V(S) - V(N1) | {1"Valve} V(G) - V(Batt +) | {LgCoil} V(N2) - V(Batt -) | {LgCoil} V(N1) - V(Batt -) | {LgCoil} V(P) - V(Batt +) | {LgCoil} V(R) - V(Batt -) | {LgCoil} V(S) - V(Batt -) | {LgCoil} V(S) - V(N1) | {LgCoil} V(G) - V(Batt +) | {1"Valve} V(P) - V(Batt -) | {1"Valve} V(G) - V(Batt -) | {1"Valve} V(SP) - V(Batt -) | {1"Valve} V(N1) - V(Batt +) | {LgCoil} V(P) - V(Batt -) | {LgCoil} V(G) - V(Batt -) | {LgCoil} V(SP) - V(Batt -) | {LgCoil} V(N1) - V(Batt +)
-0.3125 | 123.349 | -59.1019 | 64.0228 | -0.19462 | 0.025802 | 0.057146 | 0.071806 | 0.1324 | 0.015508 | 0.001822 | -0.23443 | 0.0032668 | 0.071611 | 0.073193 | -0.0013612 | -0.0018224 | 64.0457 | 64.1281 | 0.009155 | -59.2896 | 64.0732 | -59.111 | -59.1522 | -59.0607 | 0.068665 | -59.3628 | 64.0686 | 64.0045 | -59.1568 | -59.2575 | -0.009155 | -0.050354 | 0.050354 | 123.23 | -0.18768 | -0.13733 | 0.022888 | -0.054931 | -0.15564 | 0.045777 | 0.041199 | -0.26093 | -0.10529 | -0.01831 | 123.175 | 123.1476 | 59.111 | -123.175 | 123.1705 | 123.1064 | 59.1705 | -123.2803
0.6875 | 123.3124 | -59.1385 | 64.0228 | -0.14884 | 0.022598 | 0.059282 | 0.070738 | 0.13346 | 0.00055539 | 0.013571 | -0.066579 | 0.0096758 | 0.073747 | 0.056103 | -0.0056342 | 0.0013826 | 64.032 | 64.1464 | -0.013733 | -59.3033 | 64.0457 | -59.1019 | -59.1614 | -59.0836 | 0.036621 | -59.3811 | 64.0503 | 63.9999 | -59.1614 | -59.23 | 0.036621 | -0.022888 | 0.022888 | 123.2849 | -0.16479 | -0.14191 | 0.009155 | -0.022888 | -0.091553 | 0.027466 | 0.054932 | -0.24262 | -0.15106 | -0.022888 | 123.1842 | 123.1705 | 59.1248 | -123.1842 | 123.1888 | 123.1384 | 59.1751 | -123.2529
1.6875 | 123.3765 | -59.1156 | 63.9679 | 0.47677 | 0.005508 | 0.058214 | 0.071806 | 0.14308 | 0.00055539 | 0.011435 | 0.17756 | 0.0032668 | 0.06093 | 0.06892 | -0.0024292 | 0.0099276 | 64.0045 | 64.1373 | -0.073242 | -59.2987 | 63.9908 | -59.1156 | -59.1568 | -59.0881 | 0.064087 | -59.3445 | 63.9679 | 63.9313 | -59.1568 | -59.2346 | 0 | -0.041198 | 0.022888 | 123.2529 | -0.18311 | -0.14191 | 0.036621 | -0.041198 | -0.11902 | 0 | 0.027466 | -0.22888 | -0.10986 | -0.036622 | 123.1064 | 123.1201 | 59.0424 | -123.1247 | 123.0835 | 123.0469 | 59.1797 | -123.2025
2.6875 | 123.2986 | -59.1293 | 64.0091 | -0.042028 | 0.035415 | 0.063554 | 0.077146 | 0.14415 | 0.0069634 | 0.00075395 | -0.020803 | 0.0096758 | 0.069475 | 0.073193 | 0.0039788 | 0.0035186 | 64.064 | 64.1098 | -0.022888 | -59.3079 | 64.0366 | -59.1476 | -59.1751 | -59.0973 | 0.013733 | -59.4131 | 64.0869 | 64.0274 | -59.1339 | -59.2804 | -0.018311 | -0.045777 | 0.027466 | 123.2391 | -0.17853 | -0.13275 | 0.054932 | -0.004578 | -0.15106 | 0.07782 | 0.032043 | -0.28381 | -0.13275 | 0.018311 | 123.1659 | 123.1934 | 59.1064 | -123.1842 | 123.2162 | 123.1567 | 59.1431 | -123.2895
3.6875 | 123.2986 | -59.1339 | 64.0366 | -0.072545 | 0.018326 | 0.050737 | 0.063261 | 0.12919 | 0.0058954 | -0.004587 | -0.005544 | 0.0054038 | 0.081224 | 0.071057 | 0.011456 | -0.0018224 | 64.0549 | 64.1098 | -0.022888 | -59.3124 | 64.0274 | -59.1614 | -59.1568 | -59.0744 | 0.004578 | -59.3994 | 64.0686 | 63.9908 | -59.1751 | -59.2621 | -0.027466 | -0.022888 | -0.009155 | 123.2437 | -0.17853 | -0.15564 | 0.018311 | -0.041199 | -0.12817 | 0.032044 | 0.059509 | -0.2655 | -0.13733 | -0.045776 | 123.1613 | 123.1888 | 59.111 | -123.1934 | 123.2025 | 123.1247 | 59.1385 | -123.2986
4.6875 | 123.2941 | -59.1202 | 64.0228 | -0.042028 | 0.02687 | 0.058214 | 0.081419 | 0.13667 | 0.0080314 | 0.006095 | -0.081838 | 0.010744 | 0.076952 | 0.059307 | 0.0039788 | 0.0013826 | 64.032 | 64.119 | -0.032043 | -59.3079 | 64.0182 | -59.1476 | -59.1522 | -59.0836 | 0.009155 | -59.4086 | 64.0503 | 64.0091 | -59.1705 | -59.2529 | -0.027466 | -0.032044 | -0.004577 | 123.2391 | -0.18768 | -0.15564 | 0.009155 | -0.050354 | -0.13275 | 0.027466 | 0.036621 | -0.28839 | -0.15564 | -0.013733 | 123.1384 | 123.1522 | 59.0881 | -123.175 | 123.1705 | 123.1293 | 59.1293 | -123.2758
5.6875 | 123.2666 | -59.1248 | 64.0366 | 0.15634 | 0.030075 | 0.052873 | 0.093168 | 0.13667 | 0.00055539 | 0.009299 | 0.14704 | 0.0043348 | 0.075884 | 0.06892 | 0.0018428 | 0.015268 | 63.9954 | 64.0228 | -0.10071 | -59.3445 | 64.032 | -59.1476 | -59.1751 | -59.1568 | -0.091553 | -59.4772 | 64.0594 | 64.0411 | -59.1843 | -59.2712 | -0.022888 | -0.050354 | -0.004578 | 123.1476 | -0.21973 | -0.16937 | -0.041199 | -0.059509 | -0.14648 | 0.022888 | -0.032043 | -0.35248 | -0.20599 | 0.004578 | 123.1567 | 123.1201 | 59.024 | -123.2117 | 123.1842 | 123.1659 | 59.0332 | -123.3078
6.6875 | 123.2483 | -59.1431 | 64.0182 | 0.36996 | 0.003372 | 0.062486 | 0.073942 | 0.14949 | 0.011236 | -0.003518 | 0.20808 | 0.0096758 | 0.082292 | 0.075329 | 0.0029108 | -0.0039584 | 63.9954 | 64.0228 | -0.11902 | -59.3399 | 64.0228 | -59.1431 | -59.1934 | -59.1614 | -0.091553 | -59.4772 | 64.0594 | 64.0045 | -59.1705 | -59.2896 | 0 | -0.050354 | 0.004577 | 123.1659 | -0.19684 | -0.14648 | -0.022889 | -0.027466 | -0.14649 | 0.041198 | -0.018311 | -0.33417 | -0.18768 | -0.013733 | 123.1659 | 123.1384 | 59.024 | -123.2117 | 123.2025 | 123.1476 | 59.0515 | -123.3078
7.6875 | 123.2666 | -59.1385 | 63.9999 | 0.034266 | 0.049301 | 0.057146 | 0.076078 | 0.12492 | 0.0080314 | 0.006095 | 0.22334 | 0.0043348 | 0.091905 | 0.074261 | -0.0024292 | 0.0035186 | 63.9679 | 64.0366 | -0.1236 | -59.3628 | 64.0137 | -59.1339 | -59.1888 | -59.1705 | -0.073242 | -59.4864 | 64.0457 | 64.0091 | -59.1797 | -59.2575 | 0.004578 | -0.050354 | 0.013733 | 123.175 | -0.2243 | -0.17395 | -0.032043 | -0.041198 | -0.11902 | 0.045776 | -0.032043 | -0.3479 | -0.22888 | 0.009155 | 123.1522 | 123.1064 | 59.0149 | -123.1888 | 123.1842 | 123.1476 | 59.0652 | -123.2574
8.6875 | 123.3902 | -59.1064 | 63.9908 | 0.40048 | 0.016189 | 0.059282 | 0.053648 | 0.13346 | 0.0026914 | 0.003958 | 0.43696 | -0.012754 | 0.070543 | 0.073193 | -0.0002932 | 0.0099276 | 63.9954 | 64.0732 | -0.10071 | -59.3399 | 64.0182 | -59.1614 | -59.1797 | -59.111 | 0.086975 | -59.436 | 64.0274 | 63.9679 | -59.1751 | -59.2346 | -0.054932 | -0.073242 | 0.027466 | 123.1796 | -0.23346 | -0.16022 | 0.004577 | -0.068665 | -0.12817 | 0.036621 | -0.004578 | -0.32959 | -0.20142 | -0.022888 | 123.1247 | 123.1018 | 59.0057 | -123.1705 | 123.1338 | 123.0743 | 59.1934 | -123.2254
9.7031 | 123.2712 | -59.1568 | 64.0091 | 0.41574 | 0.02687 | 0.06035 | 0.084623 | 0.13453 | 0.0058954 | 0.007163 | 0.2386 | 0.011812 | 0.089769 | 0.059307 | -0.010974 | 0.0088586 | 63.9862 | 64.0274 | -0.1236 | -59.3628 | 64.0366 | -59.1705 | -59.1797 | -59.1293 | -0.091553 | -59.4589 | 64.0732 | 64.0045 | -59.166 | -59.2941 | -0.013733 | -0.022888 | 0.027466 | 123.1842 | -0.20599 | -0.18311 | -0.022888 | -0.009156 | -0.13733 | 0.064087 | 0.027466 | -0.30212 | -0.16479 | -0.004577 | 123.1934 | 123.143 | 59.0332 | -123.1888 | 123.23 | 123.1613 | 59.0652 | -123.3032
10.7031 | 123.2803 | -59.1202 | 64.0457 | -0.45401 | 0.009781 | 0.075304 | 0.060057 | 0.13453 | 0.00055539 | -0.004587 | -0.3565 | 0.0064718 | 0.064134 | 0.066784 | -0.0013612 | 0.0013826 | 64.0045 | 64.0915 | -0.027466 | -59.317 | 64.0503 | -59.1293 | -59.1431 | -59.0973 | 0.045776 | -59.3948 | 64.0961 | 64.0411 | -59.1431 | -59.2255 | -0.009155 | -0.022888 | 0.004578 | 123.2117 | -0.19684 | -0.17395 | -0.041198 | -0.022888 | -0.10529 | 0.050354 | 0.022888 | -0.27466 | -0.16937 | -0.004577 | 123.1705 | 123.1247 | 59.0927 | -123.1888 | 123.2162 | 123.1613 | 59.166 | -123.2712
11.6875 | 123.381 | -59.1019 | 63.9587 | 0.40048 | 0.025802 | 0.067827 | 0.072874 | 0.14201 | 0.00055539 | -0.003518 | -0.005544 | 0.0021988 | 0.079088 | 0.061444 | -0.0067022 | 0.00031457 | 63.858 | 64.2014 | -0.045776 | -59.3628 | 63.9816 | -59.1248 | -59.1843 | -59.0149 | 0.004578 | -59.3536 | 64.0182 | 63.9267 | -59.166 | -59.2529 | -0.022888 | -0.082397 | 0.022888 | 123.3032 | -0.26093 | -0.17853 | -0.10071 | -0.064087 | -0.15106 | 0.05951 | 0.086975 | -0.25177 | -0.10071 | -0.032043 | 123.0835 | 122.9599 | 59.0561 | -123.143 | 123.1201 | 123.0286 | 59.1064 | -123.2117
12.6875 | 123.2986 | -59.1568 | 63.9816 | 0.20211 | 0.016189 | 0.08278 | 0.070738 | 0.1356 | 0.0069634 | 0.009299 | 0.26911 | 0.0032668 | 0.064134 | 0.067852 | 0.0007748 | 0.0067226 | 63.9679 | 64.0274 | -0.12817 | -59.3491 | 64.0228 | -59.1614 | -59.166 | -59.1339 | -0.07782 | -59.4589 | 64.0549 | 64.0274 | -59.1705 | -59.2712 | -0.004578 | -0.009156 | 0.041199 | 123.1842 | -0.19226 | -0.18311 | -0.013732 | -0.013733 | -0.11444 | 0.073243 | 0.022888 | -0.30212 | -0.18768 | 0.045777 | 123.1796 | 123.1247 | 59.0286 | -123.1476 | 123.2117 | 123.1842 | 59.079 | -123.2529
13.6875 | 123.3994 | -59.111 | 63.9496 | 0.72091 | 0.010849 | 0.052873 | 0.051512 | 0.14094 | -0.0026496 | -0.003518 | 0.51325 | 0.0064718 | 0.074815 | 0.069989 | 0.0061158 | 0.0077906 | 64.0411 | 64.1647 | -0.027466 | -59.2896 | 63.9862 | -59.1431 | -59.1705 | -59.0286 | 0.032043 | -59.3399 | 64.0091 | 63.9587 | -59.1614 | -59.23 | -0.032043 | -0.059509 | 0.036621 | 123.2758 | -0.17853 | -0.11902 | 0.091553 | -0.050354 | -0.11902 | 0.059509 | 0.082398 | -0.22888 | -0.10986 | 0.009155 | 123.0972 | 123.1522 | 59.0836 | -123.1201 | 123.1201 | 123.0698 | 59.1431 | -123.1796
14.6875 | 123.4085 | -59.0836 | 63.9542 | 0.40048 | 0.007644 | 0.061418 | 0.067533 | 0.13881 | -0.0047856 | -0.013132 | 0.52851 | -0.0010052 | 0.081224 | 0.078533 | -0.0002932 | 0.0099276 | 64.0594 | 64.1739 | -0.009155 | -59.285 | 63.9725 | -59.1156 | -59.166 | -59.0149 | 0.050354 | -59.317 | 63.9816 | 63.9542 | -59.1476 | -59.2392 | -0.032044 | -0.082398 | 0.01831 | 123.2574 | -0.20142 | -0.11902 | 0.10529 | -0.064087 | -0.15564 | 0.027465 | 0.068664 | -0.23346 | -0.07782 | 0 | 123.056 | 123.143 | 59.0744 | -123.1201 | 123.0652 | 123.0377 | 59.1339 | -123.1934
15.7031 | 123.3719 | -59.0881 | 63.9999 | -0.4235 | -0.005173 | 0.074235 | 0.054716 | 0.13133 | -0.02508 | -0.008859 | -0.31072 | -0.0020732 | 0.055589 | 0.064648 | -0.0045652 | -0.0092984 | 64.0961 | 64.2105 | 0.10071 | -59.2621 | 64.0228 | -59.1019 | -59.1339 | -59.0149 | 0.15564 | -59.3079 | 64.064 | 63.9954 | -59.1248 | -59.2026 | -0.013733 | -0.045776 | 0.022888 | 123.2986 | -0.17395 | -0.12817 | 0.09613 | -0.036621 | -0.11444 | 0.064087 | 0.073242 | -0.21973 | -0.10529 | -0.004578 | 123.111 | 123.1842 | 59.1888 | -123.1338 | 123.1522 | 123.0835 | 59.2438 | -123.2025
16.6875 | 123.3856 | -59.1156 | 63.9313 | 0.32418 | -0.006241 | 0.066759 | 0.055784 | 0.14094 | 0.00055539 | -0.006723 | 0.4217 | -0.011686 | 0.057726 | 0.053967 | -0.0013612 | 0.0013826 | 64.0686 | 64.1739 | -0.022888 | -59.3079 | 63.9954 | -59.1431 | -59.1705 | -59.0149 | 0.050354 | -59.3399 | 63.9954 | 63.945 | -59.1614 | -59.2575 | -0.027465 | -0.054931 | 0.064087 | 123.2895 | -0.19226 | -0.13733 | 0.13733 | -0.045776 | -0.14191 | 0.064087 | 0.10071 | -0.2243 | -0.082398 | 0.013733 | 123.111 | 123.1842 | 59.0927 | -123.1018 | 123.111 | 123.0606 | 59.166 | -123.1888
17.6875 | 123.4039 | -59.1202 | 63.9496 | 0.38522 | 0.025802 | 0.074235 | 0.060057 | 0.14201 | -0.0047856 | -0.001382 | 0.31489 | -0.0042092 | 0.072679 | 0.060376 | -0.0099062 | 0.0013826 | 64.0961 | 64.1556 | -0.036621 | -59.2896 | 63.9954 | -59.1248 | -59.1705 | -59.0149 | 0.045776 | -59.3353 | 63.9816 | 63.9313 | -59.1476 | -59.2575 | -0.004578 | -0.050354 | 0.045776 | 123.2758 | -0.16937 | -0.11902 | 0.14648 | -0.027466 | -0.13733 | 0.032043 | 0.10529 | -0.21515 | -0.07782 | -0.018311 | 123.1155 | 123.2162 | 59.0836 | -123.1201 | 123.1018 | 123.0515 | 59.166 | -123.2071
18.6875 | 123.3948 | -59.0927 | 63.9679 | 0.41574 | 0.006576 | 0.062486 | 0.062193 | 0.13881 | 0.00055539 | -0.006723 | 0.43696 | 0.0021988 | 0.072679 | 0.066784 | -0.0002932 | -0.0028904 | 64.0869 | 64.1739 | -0.027466 | -59.285 | 63.9771 | -59.1339 | -59.1614 | -59.0103 | 0.027466 | -59.3353 | 63.9908 | 63.9359 | -59.1568 | -59.2484 | -0.041199 | -0.068665 | 0.009155 | 123.2666 | -0.19226 | -0.1236 | 0.11902 | -0.064087 | -0.15564 | 0.022888 | 0.082397 | -0.24262 | -0.086975 | -0.032044 | 123.0698 | 123.1796 | 59.0652 | -123.1293 | 123.0835 | 123.0286 | 59.1202 | -123.2162
19.6875 | 123.3948 | -59.0927 | 63.9267 | 0.36996 | 0.002304 | 0.074235 | 0.068601 | 0.14201 | -0.0058536 | 0.005026 | 0.43696 | -0.0074142 | 0.065202 | 0.057171 | -0.0034972 | 0.0045866 | 64.0961 | 64.1693 | -0.032043 | -59.285 | 63.9679 | -59.1339 | -59.1843 | -59.0012 | 0.027466 | -59.3353 | 64.0045 | 63.9359 | -59.1522 | -59.2392 | -0.041199 | -0.091553 | 0.041199 | 123.262 | -0.19226 | -0.10071 | 0.16937 | -0.05951 | -0.14648 | 0.07782 | 0.091552 | -0.24262 | -0.09613 | 0.009155 | 123.0606 | 123.1888 | 59.0607 | -123.111 | 123.0972 | 123.0286 | 59.1202 | -123.1659
20.7031 | 123.4177 | -59.0836 | 64.032 | -0.53031 | -0.006241 | 0.074235 | 0.073942 | 0.14628 | -0.012263 | -0.009927 | -0.3565 | 0.0011308 | 0.04384 | 0.055035 | 0.0007748 | 0.0013826 | 64.1006 | 64.1968 | 0.082397 | -59.2484 | 64.0182 | -59.1156 | -59.1202 | -59.0149 | 0.13275 | -59.3308 | 64.0686 | 64.0137 | -59.1202 | -59.2026 | -0.032044 | -0.036621 | -0.013732 | 123.2803 | -0.16479 | -0.12817 | 0.068665 | -0.036621 | -0.11902 | 0.036622 | 0.068664 | -0.24719 | -0.12817 | -0.01831 | 123.1018 | 123.1842 | 59.166 | -123.1522 | 123.1522 | 123.0972 | 59.2163 | -123.2346
21.6875 | 123.3261 | -59.1064 | 63.9633 | 0.23263 | 0.002304 | 0.075304 | 0.065397 | 0.13774 | -0.010127 | -0.001382 | 0.25385 | -0.0095502 | 0.061998 | 0.056103 | -0.0024292 | 0.0056546 | 63.9816 | 64.1235 | -0.036621 | -59.3124 | 63.9908 | -59.1385 | -59.1431 | -59.0378 | 0.022888 | -59.3674 | 64.0045 | 63.9175 | -59.166 | -59.2438 | -0.032044 | -0.036621 | 0.027466 | 123.23 | -0.20599 | -0.16937 | 0.01831 | -0.05951 | -0.13733 | 0.041199 | 0.068664 | -0.26093 | -0.1236 | -0.045776 | 123.0972 | 123.0881 | 59.0698 | -123.1064 | 123.111 | 123.024 | 59.1293 | -123.2071
22.6875 | 123.3353 | -59.0927 | 63.9862 | 0.095301 | -0.006241 | 0.073167 | 0.066465 | 0.13881 | -0.013331 | 0.011435 | -0.036062 | -0.0074142 | 0.064134 | 0.065716 | 0.0029108 | 0.0045866 | 63.9221 | 64.1602 | -0.013733 | -59.3262 | 63.9862 | -59.1202 | -59.1339 | -59.0286 | 0.027466 | -59.3628 | 64.0228 | 63.9359 | -59.1568 | -59.2392 | -0.027466 | -0.041199 | 0 | 123.2529 | -0.23346 | -0.19226 | -0.064087 | -0.064087 | -0.14648 | 0.036621 | 0.064087 | -0.27008 | -0.1236 | -0.050354 | 123.0789 | 123.0148 | 59.079 | -123.1201 | 123.1155 | 123.0286 | 59.1202 | -123.2254
23.6875 | 123.3856 | -59.0836 | 63.9771 | 0.11056 | -0.023331 | 0.067827 | 0.065397 | 0.14308 | -0.0079896 | 0.001822 | 0.07075 | -0.0063462 | 0.053453 | 0.060376 | -0.0067022 | 0.00031457 | 64.0411 | 64.119 | -0.032043 | -59.3124 | 64.0045 | -59.1293 | -59.1705 | -59.0378 | 0.036621 | -59.3399 | 64.0457 | 63.9404 | -59.1522 | -59.2575 | -0.045776 | -0.086975 | 0.027466 | 123.2025 | -0.22888 | -0.14191 | 0.064087 | -0.068665 | -0.17395 | 0.068664 | 0.045776 | -0.25635 | -0.082398 | -0.036621 | 123.0881 | 123.1247 | 59.0515 | -123.1476 | 123.1293 | 123.024 | 59.1202 | -123.2346
24.6875 | 125.4547 | -59.0561 | 63.9313 | 0.44625 | 0.016189 | 0.073167 | 0.073942 | 0.14094 | 0.0026914 | 0.003958 | 0.39118 | 0.0075398 | 0.047044 | 0.048626 | -0.0077702 | 0.0024506 | 64.2471 | 65.8905 | 1.3412 | -57.7744 | 63.9725 | -59.1064 | -59.1248 | -56.6071 | 1.0345 | -58.7128 | 63.9954 | 63.9313 | -59.1385 | -59.2438 | -0.050354 | -0.068665 | 0.041199 | 124.9466 | 1.2817 | 1.3504 | 0.31586 | -0.082398 | -0.18768 | 0.064087 | 2.449 | 0.34332 | 0.53101 | 0 | 123.0286 | 123.3032 | 60.3973 | -123.056 | 123.0515 | 122.9874 | 60.0906 | -123.175
25.7031 | 123.2574 | -59.1019 | 64.064 | -0.46927 | 0.00444 | 0.075304 | 0.066465 | 0.13346 | 0.0026914 | -0.010995 | -0.50908 | 0.0021988 | 0.058794 | 0.061444 | -0.0002932 | -0.012503 | 64.0411 | 64.1098 | 0.004578 | -59.3308 | 64.0457 | -59.1248 | -59.166 | -59.0561 | 0.07782 | -59.3994 | 64.1006 | 64.0045 | -59.1522 | -59.2529 | -0.022888 | -0.064087 | -0.018311 | 123.2117 | -0.22888 | -0.1648 | -0.022888 | -0.050354 | -0.15106 | 0.036621 | 0.045777 | -0.29755 | -0.14648 | -0.059509 | 123.1476 | 123.143 | 59.1064 | -123.23 | 123.2025 | 123.1064 | 59.1797 | -123.317
26.6875 | 123.381 | -59.0652 | 63.9908 | -0.057287 | -0.01799 | 0.084917 | 0.048307 | 0.1324 | -0.010127 | -0.00031405 | 0.07075 | 6.2833e-05 | 0.079088 | 0.058239 | -0.0056342 | -0.0028904 | 64.064 | 64.1876 | 0.013733 | -59.2758 | 63.9999 | -59.0927 | -59.1522 | -58.9828 | 0.10986 | -59.3033 | 64.032 | 63.9313 | -59.1431 | -59.2163 | -0.027465 | -0.086975 | 0.009155 | 123.2529 | -0.21057 | -0.1236 | 0.073242 | -0.077819 | -0.15106 | 0.041198 | 0.082398 | -0.23804 | -0.086975 | -0.05951 | 123.0652 | 123.1293 | 59.079 | -123.143 | 123.0972 | 122.9965 | 59.1751 | -123.2071
27.6875 | 123.3627 | -59.1019 | 63.9404 | 0.47677 | 0.002304 | 0.067827 | 0.082487 | 0.13346 | 0.0091004 | -0.003518 | 0.29963 | 6.2833e-05 | 0.066271 | 0.079602 | -0.0034972 | -0.0039584 | 64.0869 | 64.183 | -0.004578 | -59.2941 | 63.9679 | -59.1431 | -59.1476 | -58.992 | 0.045776 | -59.3353 | 64.0137 | 63.8992 | -59.1476 | -59.2575 | -0.041198 | -0.045776 | 0.027466 | 123.2849 | -0.19226 | -0.14648 | 0.14648 | -0.045776 | -0.15564 | 0.073242 | 0.10986 | -0.23346 | -0.07782 | -0.041199 | 123.0698 | 123.1888 | 59.0973 | -123.0881 | 123.1155 | 123.0011 | 59.1476 | -123.1979
28.6875 | 123.3536 | -59.1156 | 63.9587 | 0.27841 | -0.006241 | 0.066759 | 0.081419 | 0.13453 | 0.0058954 | 0.007163 | 0.2386 | 0.0086078 | 0.069475 | 0.064648 | 0.0050478 | 0.0077906 | 64.064 | 64.1327 | -0.041199 | -59.3353 | 63.9908 | -59.1156 | -59.1705 | -59.0195 | 0.032043 | -59.3445 | 64.0182 | 63.945 | -59.1385 | -59.2529 | 0 | -0.054931 | 0.032044 | 123.2483 | -0.21973 | -0.16479 | 0.10529 | -0.022888 | -0.13733 | 0.05951 | 0.096131 | -0.22888 | -0.091552 | -0.013733 | 123.1064 | 123.1796 | 59.0744 | -123.1293 | 123.1339 | 123.0606 | 59.1476 | -123.2117
29.6875 | 123.3582 | -59.1019 | 63.9725 | 0.26315 | -0.010514 | 0.06035 | 0.067533 | 0.1356 | -0.0015816 | 0.001822 | 0.14704 | 0.0011308 | 0.06093 | 0.058239 | 0.0007748 | -0.0018224 | 63.9221 | 64.1785 | -0.004578 | -59.3262 | 63.9908 | -59.111 | -59.1843 | -59.0103 | 0.009155 | -59.3491 | 64.0411 | 63.945 | -59.1385 | -59.2484 | -0.009155 | -0.082397 | 0.018311 | 123.2803 | -0.2243 | -0.14191 | -0.050354 | -0.036621 | -0.14648 | 0.068665 | 0.091553 | -0.24719 | -0.10071 | -0.027466 | 123.0927 | 123.024 | 59.0973 | -123.1567 | 123.143 | 123.0469 | 59.111 | -123.2208
30.6875 | 123.3444 | -59.0744 | 63.9862 | 0.20211 | -0.013718 | 0.075304 | 0.064329 | 0.14415 | -0.011195 | -0.001382 | 0.040232 | 0.0021988 | 0.050249 | 0.057171 | -0.0002932 | 0.0024506 | 64.0366 | 64.1235 | -0.036621 | -59.3216 | 63.9954 | -59.1202 | -59.1431 | -59.0378 | 0.045776 | -59.3491 | 64.0457 | 63.9679 | -59.1293 | -59.2163 | -0.045776 | -0.068664 | 0.009155 | 123.1979 | -0.24719 | -0.17853 | 0.050354 | -0.054931 | -0.14191 | 0.059509 | 0.036621 | -0.27466 | -0.13275 | -0.01831 | 123.0698 | 123.111 | 59.0378 | -123.1293 | 123.1201 | 123.0423 | 59.1202 | -123.2025
31.6875 | 123.2941 | -59.1064 | 64.0228 | -0.48453 | 0.02153 | 0.057146 | 0.079283 | 0.1324 | 0.013372 | -0.003518 | -0.69219 | 0.0064718 | 0.066271 | 0.060376 | 0.0050478 | -0.010367 | 64.0594 | 64.1144 | -0.004578 | -59.3308 | 64.0823 | -59.1248 | -59.1522 | -59.0744 | 0.059509 | -59.3994 | 64.1052 | 64.0091 | -59.1522 | -59.2667 | -0.018311 | -0.045777 | 0.059509 | 123.2208 | -0.22431 | -0.17853 | 0.036621 | -0.045777 | -0.16022 | 0.082398 | 0.032043 | -0.29297 | -0.13275 | -0.013733 | 123.1888 | 123.1659 | 59.1019 | -123.175 | 123.2117 | 123.1155 | 59.166 | -123.2895
32.6875 | 123.3856 | -59.1156 | 63.9633 | 0.36996 | -0.011582 | 0.066759 | 0.064329 | 0.13774 | 0.0026914 | 0.006095 | 0.25385 | -0.0031412 | 0.059862 | 0.066784 | 0.0082518 | 0.0056546 | 64.0686 | 64.1968 | 0.004578 | -59.2941 | 63.9816 | -59.1293 | -59.1476 | -58.9783 | 0.036621 | -59.317 | 64.0091 | 63.9313 | -59.1705 | -59.2529 | -0.013732 | -0.032043 | 0.01831 | 123.3124 | -0.17853 | -0.14648 | 0.10529 | -0.054931 | -0.13733 | 0.045776 | 0.13733 | -0.20142 | -0.064087 | -0.032044 | 123.0972 | 123.1842 | 59.1202 | -123.111 | 123.1247 | 123.0469 | 59.1522 | -123.2162
33.6875 | 123.3215 | -59.0836 | 63.9771 | 0.30892 | 0.017257 | 0.06569 | 0.05792 | 0.14949 | 0.0037594 | 0.003958 | 0.31489 | 0.0021988 | 0.063066 | 0.067852 | -0.0045652 | -0.015707 | 64.064 | 64.1785 | -0.013733 | -59.3216 | 63.9587 | -59.111 | -59.1476 | -58.9371 | 0.16022 | -59.4269 | 64.0045 | 63.913 | -59.1293 | -59.2392 | -0.027466 | -0.064087 | -0.018311 | 123.262 | -0.23804 | -0.17395 | 0.086975 | -0.045776 | -0.15564 | 0.027466 | 0.14648 | -0.34332 | -0.18768 | -0.064087 | 123.0423 | 123.1476 | 59.0698 | -123.1247 | 123.0881 | 122.9965 | 59.2438 | -123.2162
34.6875 | 123.3444 | -59.1156 | 63.9771 | 0.38522 | 0.005508 | 0.073167 | 0.067533 | 0.13133 | -0.0079896 | -0.012063 | 0.25385 | -0.0052782 | 0.055589 | 0.060376 | -0.0045652 | -0.0082304 | 64.0411 | 64.1418 | -0.045776 | -59.3216 | 63.9771 | -59.1248 | -59.1568 | -59.0424 | 0.022888 | -59.3582 | 64.0228 | 63.9359 | -59.1568 | -59.2346 | -0.009155 | -0.041198 | 0 | 123.2574 | -0.20599 | -0.16479 | 0.064087 | -0.041198 | -0.11902 | 0.045776 | 0.073243 | -0.24261 | -0.1236 | -0.041199 | 123.0927 | 123.1567 | 59.0698 | -123.1338 | 123.1384 | 123.0515 | 59.1385 | -123.2117
35.6875 | 123.349 | -59.1019 | 63.9816 | 0.15634 | -0.001969 | 0.062486 | 0.070738 | 0.13026 | -0.0037176 | -0.003518 | 0.040232 | -0.0084822 | 0.066271 | 0.053967 | -0.0077702 | 0.0035186 | 64.0366 | 64.1418 | -0.027466 | -59.3033 | 63.9954 | -59.1202 | -59.1476 | -59.0286 | 0.059509 | -59.3308 | 64.0274 | 63.9313 | -59.1339 | -59.2438 | -0.01831 | -0.045776 | 0.013733 | 123.2437 | -0.20142 | -0.15564 | 0.054932 | -0.032043 | -0.14191 | 0.045777 | 0.073243 | -0.22888 | -0.086976 | -0.050354 | 123.0972 | 123.1384 | 59.0744 | -123.1293 | 123.1293 | 123.0331 | 59.1614 | -123.2254
36.6875 | 123.2483 | -59.0973 | 64.0411 | -0.46927 | -0.016922 | 0.062486 | 0.05258 | 0.1356 | -0.0047856 | -0.004587 | -0.05132 | 0.0054038 | 0.052385 | 0.058239 | -0.0045652 | -0.0028904 | 64.0961 | 64.1922 | 0.036621 | -59.2621 | 64.032 | -59.1156 | -59.1476 | -59.0652 | 0.059509 | -59.3719 | 64.1098 | 63.9954 | -59.1614 | -59.2438 | -0.018311 | -0.050354 | -0.009156 | 123.2895 | -0.16479 | -0.11444 | 0.054931 | -0.064087 | -0.14648 | 0.068664 | 0.032043 | -0.27466 | -0.12817 | -0.045777 | 123.1293 | 123.1934 | 59.1339 | -123.1888 | 123.2071 | 123.0927 | 59.1568 | -123.2849
37.6875 | 123.3444 | -59.0973 | 63.9679 | 0.33944 | -0.004105 | 0.066759 | 0.068601 | 0.13774 | -0.0047856 | 0.005026 | 0.25385 | 0.0021988 | 0.063066 | 0.059307 | -0.0013612 | 0.00031457 | 64.0274 | 64.183 | -0.013733 | -59.2987 | 63.9862 | -59.1156 | -59.1293 | -58.9645 | -0.018311 | -59.3674 | 64.0182 | 63.9084 | -59.1431 | -59.2438 | -0.018311 | -0.032043 | 0.01831 | 123.2803 | -0.20142 | -0.16937 | 0.059509 | -0.045776 | -0.14648 | 0.050354 | 0.13275 | -0.27008 | -0.1236 | -0.05951 | 123.0835 | 123.1247 | 59.0836 | -123.0972 | 123.1155 | 123.0057 | 59.079 | -123.2117
38.6875 | 123.3215 | -59.0927 | 63.9725 | 0.12582 | -0.007309 | 0.066759 | 0.072874 | 0.1356 | -0.0069216 | -0.008859 | 0.25385 | 0.0032668 | 0.076952 | 0.064648 | -0.0099062 | 0.0035186 | 64.0457 | 64.1647 | -0.036621 | -59.3079 | 63.9999 | -59.1019 | -59.1797 | -59.0378 | 0.022888 | -59.3628 | 64.0457 | 63.9221 | -59.1385 | -59.2484 | -0.009156 | -0.086975 | 0.027466 | 123.2574 | -0.21515 | -0.12817 | 0.073242 | -0.045777 | -0.15564 | 0.073242 | 0.054931 | -0.27008 | -0.11444 | -0.050354 | 123.0927 | 123.1384 | 59.0561 | -123.1522 | 123.1384 | 123.0148 | 59.1156 | -123.2208
39.6875 | 123.3536 | -59.0881 | 63.9908 | 1.5449 | -0.004105 | 0.064622 | 0.065397 | 0.13881 | -0.014399 | -0.009927 | 0.1623 | -0.0084822 | 0.065202 | 0.060376 | -0.0034972 | 0.00031457 | 64.0366 | 64.1464 | -0.045776 | -59.3216 | 63.9771 | -59.1202 | -59.1751 | -59.024 | 0.036621 | -59.3536 | 64.0228 | 63.945 | -59.1476 | -59.2346 | -0.032043 | -0.086975 | -0.013733 | 123.2346 | -0.23346 | -0.14648 | 0.045776 | -0.059509 | -0.14648 | 0.032043 | 0.064087 | -0.2655 | -0.11902 | -0.045777 | 123.0652 | 123.1247 | 59.0424 | -123.1659 | 123.111 | 123.0331 | 59.1248 | -123.2254
40.6875 | 123.3582 | -59.0973 | 63.9587 | 0.46151 | 0.00444 | 0.06569 | 0.060057 | 0.13881 | -0.00051261 | 0.007163 | 0.25385 | -0.010618 | 0.084429 | 0.066784 | -0.0099062 | -0.0018224 | 64.0915 | 64.1785 | -0.022888 | -59.285 | 64.0091 | -59.1248 | -59.1568 | -59.0012 | 0.054932 | -59.3308 | 64.0045 | 63.913 | -59.1705 | -59.23 | -0.027466 | -0.059509 | 0.050354 | 123.2758 | -0.18768 | -0.12817 | 0.13275 | -0.073242 | -0.13275 | 0.045777 | 0.09613 | -0.23346 | -0.10071 | -0.045776 | 123.1064 | 123.1888 | 59.0744 | -123.1155 | 123.1018 | 123.0103 | 59.1522 | -123.1888
41.6875 | 123.4039 | -59.0607 | 63.9725 | -0.057287 | -0.015854 | 0.072099 | 0.068601 | 0.13453 | -0.0090576 | 0.001822 | -0.036062 | -0.013823 | 0.065202 | 0.06358 | -0.0013612 | 0.012064 | 64.1052 | 64.2471 | 0.027466 | -59.2667 | 64.0091 | -59.0881 | -59.1614 | -58.9645 | 0.12817 | -59.2804 | 64.0228 | 63.9175 | -59.1522 | -59.2026 | -0.027466 | -0.10071 | 0.036621 | 123.3078 | -0.20599 | -0.10529 | 0.13275 | -0.091553 | -0.14191 | 0.050354 | 0.09613 | -0.21973 | -0.07782 | -0.054931 | 123.0698 | 123.1659 | 59.0881 | -123.1338 | 123.0835 | 122.9782 | 59.1888 | -123.175
42.6875 | 123.3627 | -59.0836 | 63.9771 | 0.1716 | -0.011582 | 0.067827 | 0.062193 | 0.12706 | -0.011195 | 0.00075395 | 0.055491 | -0.0042092 | 0.071611 | 0.044354 | 0.0018428 | 0.0013826 | 64.032 | 64.1647 | -0.022888 | -59.3216 | 63.9954 | -59.1156 | -59.1339 | -59.0286 | 0.027466 | -59.3445 | 64.0366 | 63.913 | -59.1522 | -59.2484 | -0.032044 | -0.050354 | 0.01831 | 123.2483 | -0.23804 | -0.18768 | 0.054931 | -0.068665 | -0.16479 | 0.059509 | 0.054932 | -0.26093 | -0.09613 | -0.064087 | 123.0789 | 123.1155 | 59.0607 | -123.111 | 123.1201 | 122.9965 | 59.111 | -123.2254
43.6875 | 123.3902 | -59.0927 | 63.9679 | -0.042028 | -0.022263 | 0.057146 | 0.063261 | 0.13987 | -0.0047856 | 0.00075395 | -0.18865 | -0.012754 | 0.072679 | 0.058239 | -0.0024292 | 0.0013826 | 64.0869 | 64.2059 | 0.036621 | -59.2712 | 64.0366 | -59.111 | -59.1293 | -58.9691 | 0.1236 | -59.2941 | 64.0411 | 63.9175 | -59.1339 | -59.2346 | -0.018311 | -0.036621 | 0.068664 | 123.2986 | -0.17853 | -0.14191 | 0.11902 | -0.041199 | -0.14191 | 0.073242 | 0.1236 | -0.20142 | -0.059509 | -0.050354 | 123.1293 | 123.1796 | 59.1293 | -123.0972 | 123.1338 | 123.0103 | 59.2163 | -123.2025
44.6875 | 123.3673 | -59.1064 | 63.9313 | 0.41574 | 0.00016795 | 0.06569 | 0.064329 | 0.14735 | 0.013372 | -0.005655 | 0.25385 | -0.0010052 | 0.057726 | 0.078533 | 0.0039788 | -0.0018224 | 64.0869 | 64.2151 | -0.004578 | -59.2987 | 63.9725 | -59.1248 | -59.1705 | -58.9874 | 0.045776 | -59.3216 | 64.0228 | 63.8718 | -59.1522 | -59.2484 | -0.018311 | -0.064087 | 0.041199 | 123.3215 | -0.19226 | -0.12817 | 0.15564 | -0.045777 | -0.14191 | 0.091553 | 0.11902 | -0.21515 | -0.073242 | -0.059509 | 123.0789 | 123.1934 | 59.1019 | -123.1018 | 123.1293 | 122.9782 | 59.1522 | -123.1796
45.6875 | 123.3902 | -59.0836 | 63.9496 | 0.36996 | 0.009781 | 0.064622 | 0.068601 | 0.14201 | 0.017644 | 0.007163 | 0.20808 | 0.0011308 | 0.066271 | 0.06358 | 0.012524 | -0.011435 | 64.1006 | 64.1968 | -0.013733 | -59.2804 | 63.9908 | -59.1339 | -59.166 | -58.992 | 0.022888 | -59.3216 | 64.0366 | 63.8809 | -59.1476 | -59.23 | -0.050354 | -0.082398 | 0.041199 | 123.2803 | -0.19684 | -0.11444 | 0.15106 | -0.064087 | -0.14648 | 0.086975 | 0.091553 | -0.23804 | -0.091552 | -0.068665 | 123.0743 | 123.1842 | 59.0698 | -123.1155 | 123.1201 | 122.9645 | 59.1064 | -123.1796
46.6875 | 123.3536 | -59.1156 | 63.9908 | 0.0037495 | -0.00090105 | 0.067827 | 0.067533 | 0.1356 | -0.0079896 | 0.001822 | -0.005544 | 0.0043348 | 0.065202 | 0.060376 | -0.0045652 | 0.00031457 | 64.032 | 64.151 | -0.004578 | -59.2987 | 64.0228 | -59.0973 | -59.1751 | -59.0012 | 0.073242 | -59.3079 | 64.0137 | 63.9542 | -59.1568 | -59.2346 | 0.018311 | -0.059509 | 0.032043 | 123.2666 | -0.18311 | -0.1236 | 0.041198 | -0.041198 | -0.11902 | 0.022888 | 0.11444 | -0.19226 | -0.073242 | -0.036621 | 123.1384 | 123.1476 | 59.111 | -123.1659 | 123.1293 | 123.0698 | 59.1888 | -123.2254
47.6875 | 123.3307 | -59.1019 | 63.9954 | 0.24789 | -0.020127 | 0.064622 | 0.064329 | 0.13346 | 0.010168 | 0.009299 | 0.19282 | 0.0075398 | 0.053453 | 0.061444 | -0.0034972 | -0.0039584 | 64.0411 | 64.151 | -0.022888 | -59.3308 | 63.9908 | -59.1064 | -59.1522 | -59.0195 | 0.050354 | -59.3491 | 64.0366 | 63.913 | -59.1293 | -59.2392 | -0.004577 | -0.050354 | -0.004577 | 123.2529 | -0.22888 | -0.17853 | 0.045777 | -0.027465 | -0.13733 | 0.041199 | 0.082398 | -0.24719 | -0.10986 | -0.082397 | 123.0927 | 123.143 | 59.079 | -123.1476 | 123.1384 | 123.0148 | 59.1522 | -123.2346
48.6875 | 123.3673 | -59.0881 | 63.9771 | 0.0037495 | -0.016922 | 0.067827 | 0.061125 | 0.14415 | 0.00055539 | -0.003518 | -0.15813 | -0.0063462 | 0.051317 | 0.051831 | -0.0067022 | 0.0024506 | 64.0961 | 64.1968 | 0.032043 | -59.2667 | 63.9999 | -59.1019 | -59.1385 | -58.9691 | 0.13733 | -59.3079 | 64.0228 | 63.9175 | -59.1293 | -59.2255 | -0.013733 | -0.050354 | 0.022888 | 123.2849 | -0.17853 | -0.12817 | 0.11902 | -0.041198 | -0.13733 | 0.045776 | 0.11902 | -0.21973 | -0.082397 | -0.059509 | 123.0881 | 123.1842 | 59.1202 | -123.1155 | 123.111 | 123.0057 | 59.2255 | -123.2025
49.6875 | 123.3536 | -59.1064 | 63.9542 | 0.30892 | 0.010849 | 0.058214 | 0.060057 | 0.12812 | 0.0026914 | -0.004587 | 0.19282 | -0.0042092 | 0.061998 | 0.06358 | -0.0034972 | -0.010367 | 64.0915 | 64.183 | -0.009155 | -59.2987 | 63.9725 | -59.1385 | -59.1522 | -58.992 | 0.041199 | -59.317 | 64.0228 | 63.8947 | -59.1614 | -59.2438 | -0.032044 | -0.045777 | 0.01831 | 123.2895 | -0.19226 | -0.14648 | 0.13733 | -0.054932 | -0.13733 | 0.068664 | 0.11444 | -0.21057 | -0.073243 | -0.05951 | 123.0789 | 123.1979 | 59.0973 | -123.1064 | 123.1293 | 123.0011 | 59.1476 | -123.1979
50.6875 | 123.3536 | -59.1019 | 63.9725 | 0.32418 | -0.008377 | 0.075304 | 0.072874 | 0.12385 | -0.0037176 | 0.00289 | 0.28437 | 0.0064718 | 0.057726 | 0.057171 | -0.0088382 | 0.0035186 | 64.1785 | 64.0549 | -0.054932 | -59.3124 | 63.9862 | -59.0973 | -59.1843 | -59.0286 | 0.036621 | -59.3399 | 64.0366 | 63.9175 | -59.1568 | -59.2209 | 0.004578 | -0.082397 | 0.013733 | 123.1567 | -0.21057 | -0.12817 | 0.20599 | -0.054931 | -0.11902 | 0.064087 | 0.073243 | -0.23804 | -0.11902 | -0.054931 | 123.0881 | 123.2803 | 59.0469 | -123.1567 | 123.1384 | 123.0194 | 59.1385 | -123.1934
51.6875 | 123.3627 | -59.0973 | 63.9816 | -0.026769 | -0.009445 | 0.059282 | 0.068601 | 0.13881 | -0.0069216 | -0.005655 | -0.097097 | 0.0011308 | 0.06093 | 0.066784 | 0.0039788 | -0.0018224 | 64.0457 | 64.1785 | 0.018311 | -59.2896 | 64.0274 | -59.1019 | -59.1522 | -58.9828 | 0.10529 | -59.2941 | 64.0366 | 63.9038 | -59.1476 | -59.2255 | -0.004578 | -0.054932 | 0.045777 | 123.2758 | -0.19226 | -0.13733 | 0.064087 | -0.050354 | -0.12817 | 0.054932 | 0.11444 | -0.19684 | -0.068664 | -0.077819 | 123.1247 | 123.143 | 59.1156 | -123.1338 | 123.1338 | 123.0011 | 59.2026 | -123.2071
52.6875 | 123.3902 | -59.0927 | 63.9496 | -0.10306 | 0.011917 | 0.06569 | 0.066465 | 0.13774 | 0.016576 | -0.00031405 | 0.20808 | 0.0021988 | 0.055589 | 0.069989 | 0.0018428 | -0.0071624 | 64.0869 | 64.1876 | -0.022888 | -59.2941 | 63.9771 | -59.1339 | -59.1568 | -58.9874 | 0.027466 | -59.3262 | 64.0182 | 63.8763 | -59.1705 | -59.2575 | -0.041199 | -0.064087 | 0.027466 | 123.2803 | -0.20142 | -0.13733 | 0.13733 | -0.07782 | -0.16479 | 0.068665 | 0.10529 | -0.23346 | -0.068665 | -0.073242 | 123.0698 | 123.1796 | 59.0698 | -123.1064 | 123.111 | 122.9691 | 59.1202 | -123.2071
53.6875 | 123.3078 | -59.1202 | 64.0228 | -0.1641 | 0.00016795 | 0.051805 | 0.081419 | 0.1356 | 0.033666 | 0.012503 | -0.37176 | 0.022493 | 0.074815 | 0.064648 | 0.013592 | -0.0039584 | 64.1052 | 64.1602 | 0 | -59.2987 | 64.0503 | -59.1431 | -59.1476 | -59.0195 | 0.082397 | -59.3582 | 64.0549 | 63.9633 | -59.1614 | -59.2621 | -0.022888 | -0.027466 | 0.027466 | 123.2803 | -0.17853 | -0.15106 | 0.082398 | -0.041199 | -0.14191 | 0.032044 | 0.10071 | -0.23804 | -0.09613 | -0.059509 | 123.1705 | 123.2254 | 59.1202 | -123.1705 | 123.175 | 123.0835 | 59.2026 | -123.2849
54.6875 | 123.3719 | -59.0836 | 63.9679 | 0.33944 | -0.001969 | 0.061418 | 0.072874 | 0.1356 | -0.0015816 | -0.00031405 | 0.37593 | 0.0011308 | 0.059862 | 0.062512 | 0.0007748 | 0.013132 | 64.0457 | 64.1968 | -0.009155 | -59.3124 | 63.9542 | -59.1248 | -59.1568 | -59.0057 | 0.045776 | -59.3124 | 64.032 | 63.9175 | -59.1385 | -59.2392 | -0.041199 | -0.073242 | -0.013733 | 123.2803 | -0.22888 | -0.15564 | 0.077819 | -0.054932 | -0.15564 | 0.064086 | 0.07782 | -0.22888 | -0.073242 | -0.050354 | 123.0377 | 123.1293 | 59.0744 | -123.1247 | 123.1155 | 123.0011 | 59.1293 | -123.2071
55.6875 | 123.3353 | -59.1019 | 63.9908 | 0.14108 | -0.001969 | 0.062486 | 0.066465 | 0.13026 | -0.0015816 | -0.00245 | 0.1623 | -0.0031412 | 0.041704 | 0.057171 | 0.0007748 | -0.0039584 | 64.0366 | 64.151 | -0.018311 | -59.317 | 64.0091 | -59.1248 | -59.1751 | -59.0378 | 0.041199 | -59.3582 | 64.0503 | 63.9221 | -59.1385 | -59.2346 | -0.022888 | -0.073242 | 0.01831 | 123.2529 | -0.21515 | -0.14191 | 0.045776 | -0.036621 | -0.13275 | 0.059509 | 0.064087 | -0.25635 | -0.1236 | -0.068665 | 123.111 | 123.1384 | 59.0836 | -123.1659 | 123.1522 | 123.024 | 59.1431 | -123.2254
56.6875 | 123.2803 | -59.1156 | 64.0732 | -0.43876 | 0.001236 | 0.067827 | 0.070738 | 0.13774 | 0.0048274 | -0.007791 | -0.49383 | -0.0063462 | 0.053453 | 0.060376 | -0.0067022 | 0.0024506 | 64.0778 | 64.1373 | 0.004578 | -59.3262 | 64.064 | -59.1202 | -59.1797 | -59.0836 | 0.064087 | -59.3674 | 64.1098 | 63.9954 | -59.1705 | -59.2346 | -0.004577 | -0.064086 | -0.009155 | 123.2529 | -0.21057 | -0.14648 | 0.004578 | -0.054931 | -0.11902 | 0.036621 | 0.032044 | -0.25177 | -0.13275 | -0.07782 | 123.1796 | 123.1934 | 59.1202 | -123.2529 | 123.2254 | 123.111 | 59.1797 | -123.3078
57.6875 | 123.349 | -59.0973 | 63.9404 | 0.3547 | -0.019058 | 0.062486 | 0.068601 | 0.13774 | -0.0015816 | 0.009299 | 0.28437 | -0.0063462 | 0.064134 | 0.064648 | 0.0029108 | 0.0067226 | 64.064 | 64.183 | -0.009155 | -59.2987 | 63.9679 | -59.1385 | -59.1568 | -58.9828 | 0.054932 | -59.317 | 64.0091 | 63.8901 | -59.1431 | -59.2484 | -0.041199 | -0.059509 | 0.027466 | 123.2803 | -0.20142 | -0.14191 | 0.1236 | -0.045776 | -0.15106 | 0.068664 | 0.11444 | -0.21973 | -0.068665 | -0.050354 | 123.0652 | 123.1613 | 59.0881 | -123.0972 | 123.1064 | 122.9874 | 59.1522 | -123.1888
58.6875 | 123.3307 | -59.1019 | 63.9633 | 0.44625 | -0.004105 | 0.06569 | 0.061125 | 0.1324 | -0.0015816 | 0.008231 | 0.29963 | 0.0021988 | 0.073747 | 0.061444 | -0.0002932 | 0.00031457 | 64.0778 | 64.183 | -0.004578 | -59.3033 | 63.9954 | -59.1156 | -59.1934 | -58.9966 | 0.054932 | -59.3216 | 63.9999 | 63.913 | -59.1568 | -59.2392 | -0.013733 | -0.091552 | 0.032043 | 123.2849 | -0.20142 | -0.10986 | 0.11444 | -0.054931 | -0.13733 | 0.036621 | 0.10529 | -0.21973 | -0.082397 | -0.050354 | 123.0972 | 123.1796 | 59.0973 | -123.1567 | 123.1018 | 123.0148 | 59.1568 | -123.2025
59.6875 | 123.3536 | -59.1019 | 63.9633 | 0.38522 | 0.015121 | 0.061418 | 0.063261 | 0.12812 | -0.0047856 | 0.00075395 | 0.28437 | 6.2833e-05 | 0.058794 | 0.065716 | -0.0002932 | -0.0028904 | 64.0823 | 64.1876 | -0.013733 | -59.2987 | 63.9725 | -59.1293 | -59.1431 | -59.0012 | 0.032043 | -59.3033 | 64.0274 | 63.9084 | -59.1614 | -59.2209 | -0.027465 | -0.041198 | 0.009155 | 123.2895 | -0.19684 | -0.15564 | 0.11902 | -0.059509 | -0.11902 | 0.064087 | 0.10071 | -0.20142 | -0.082398 | -0.054932 | 123.0743 | 123.1842 | 59.0881 | -123.1064 | 123.1293 | 123.0103 | 59.1339 | -123.1842
60.6875 | 123.3398 | -59.1064 | 63.9267 | 0.44625 | 0.00016795 | 0.056077 | 0.06967 | 0.12706 | 0.0037594 | 0.003958 | 0.28437 | 0.0054038 | 0.072679 | 0.069989 | 0.0050478 | 0.0013826 | 64.0732 | 64.1876 | -0.018311 | -59.2987 | 63.9862 | -59.1019 | -59.1705 | -58.9783 | 0.054932 | -59.3124 | 64.0045 | 63.9175 | -59.1614 | -59.2529 | 0.004577 | -0.064087 | 0.059509 | 123.2941 | -0.19226 | -0.12817 | 0.14648 | -0.054932 | -0.14648 | 0.07782 | 0.12817 | -0.20599 | -0.059509 | -0.009155 | 123.0927 | 123.1796 | 59.0881 | -123.0972 | 123.111 | 123.024 | 59.1614 | -123.1796
61.6875 | 123.3124 | -59.0927 | 63.9679 | 0.14108 | -0.008377 | 0.07744 | 0.068601 | 0.13133 | -0.012263 | -0.009927 | 0.1623 | -0.0010052 | 0.064134 | 0.052899 | -0.0088382 | -0.0018224 | 64.0457 | 64.1373 | -0.036621 | -59.317 | 63.9954 | -59.1293 | -59.1476 | -59.024 | 0.054932 | -59.3353 | 64.0503 | 63.9175 | -59.1339 | -59.2117 | -0.036621 | -0.054932 | 0.027465 | 123.23 | -0.22431 | -0.16937 | 0.077819 | -0.041199 | -0.11902 | 0.082397 | 0.068664 | -0.24262 | -0.1236 | -0.050354 | 123.0881 | 123.1384 | 59.0561 | -123.1155 | 123.143 | 123.0103 | 59.1476 | -123.1796
62.6875 | 123.3261 | -59.0698 | 63.9679 | 0.3547 | 0.006576 | 0.063554 | 0.073942 | 0.13881 | -0.00051261 | -0.006723 | 0.80317 | -0.0042092 | 0.066271 | 0.065716 | -0.0024292 | 0.00031457 | 64.0594 | 64.1556 | -0.032043 | -59.3079 | 63.9862 | -59.1248 | -59.1568 | -59.0378 | 0.027466 | -59.3491 | 64.0091 | 63.913 | -59.166 | -59.2529 | -0.054932 | -0.086975 | 0.01831 | 123.2254 | -0.23804 | -0.15106 | 0.091552 | -0.096131 | -0.18311 | 0.041198 | 0.032043 | -0.27924 | -0.09613 | -0.054932 | 123.056 | 123.1293 | 59.0378 | -123.1247 | 123.0789 | 122.9828 | 59.0973 | -123.2208
63.6875 | 123.3307 | -59.1064 | 63.9862 | 0.14108 | -0.023331 | 0.056077 | 0.05792 | 0.12812 | -0.0015816 | -0.00031405 | 0.11653 | 0.0054038 | 0.057726 | 0.081738 | -0.0056342 | 0.0088586 | 64.0366 | 64.1327 | -0.036621 | -59.3079 | 64.0228 | -59.1293 | -59.1522 | -59.0378 | 0.032043 | -59.3353 | 64.0366 | 63.9038 | -59.1202 | -59.2392 | -0.022888 | -0.045777 | 0.036621 | 123.2391 | -0.20142 | -0.15564 | 0.050354 | -0.013733 | -0.13275 | 0.050354 | 0.068664 | -0.22888 | -0.09613 | -0.082397 | 123.1293 | 123.143 | 59.0698 | -123.1384 | 123.143 | 123.0103 | 59.1385 | -123.2254
64.6875 | 123.381 | -59.0836 | 63.9816 | -0.042028 | -0.008377 | 0.073167 | 0.062193 | 0.12599 | -0.0026496 | 0.011435 | 0.040232 | 0.0011308 | 0.048113 | 0.050762 | -0.0034972 | -0.0028904 | 64.0411 | 64.1602 | -0.004578 | -59.2896 | 64.0091 | -59.1156 | -59.1339 | -59.0012 | 0.09613 | -59.3079 | 64.0411 | 63.9175 | -59.1568 | -59.23 | -0.032044 | -0.050354 | 0.027466 | 123.2437 | -0.20599 | -0.15564 | 0.05951 | -0.073242 | -0.14648 | 0.05951 | 0.082397 | -0.2243 | -0.077819 | -0.064086 | 123.0927 | 123.1247 | 59.079 | -123.1155 | 123.1247 | 123.0011 | 59.1797 | -123.2117
65.6875 | 123.3124 | -59.0973 | 63.9542 | 0.29367 | -0.004105 | 0.056077 | 0.071806 | 0.13346 | -0.0037176 | -0.001382 | 0.22334 | 0.0032668 | 0.053453 | 0.061444 | -0.0002932 | -0.0071624 | 64.0732 | 64.1647 | -0.013733 | -59.3079 | 63.9908 | -59.1385 | -59.1385 | -59.0424 | 0.24261 | -59.3308 | 64.0091 | 63.9084 | -59.1522 | -59.2392 | -0.041199 | -0.041199 | 0.036621 | 123.262 | -0.21057 | -0.16937 | 0.11902 | -0.054932 | -0.14191 | 0.054931 | 0.054932 | -0.23346 | -0.091553 | -0.045777 | 123.0881 | 123.1705 | 59.0836 | -123.0927 | 123.1064 | 123.0057 | 59.3399 | -123.1934
66.6875 | 123.4131 | -59.0836 | 63.9999 | -0.087804 | -0.010514 | 0.072099 | 0.078214 | 0.12919 | -0.013331 | -0.00031405 | 0.040232 | 6.2833e-05 | 0.059862 | 0.065716 | 0.0007748 | -0.0039584 | 64.0778 | 64.2014 | 0.041199 | -59.2438 | 64.0045 | -59.1064 | -59.1476 | -58.9645 | 0.15106 | -59.2529 | 64.0366 | 63.9221 | -59.1156 | -59.2117 | -0.022888 | -0.064087 | 0.004578 | 123.2849 | -0.16022 | -0.09613 | 0.07782 | -0.032044 | -0.12817 | 0.036621 | 0.11902 | -0.16937 | -0.041199 | -0.07782 | 123.0881 | 123.1613 | 59.1248 | -123.1476 | 123.1201 | 123.0057 | 59.2346 | -123.2117
67.6875 | 123.349 | -59.0881 | 63.9771 | -0.057287 | 0.003372 | 0.06569 | 0.076078 | 0.1324 | -0.010127 | -0.003518 | 0.009715 | -0.0084822 | 0.061998 | 0.061444 | 0.0018428 | 0.0045866 | 64.032 | 64.1418 | -0.045776 | -59.2987 | 63.9999 | -59.1202 | -59.1614 | -59.0469 | 0.032043 | -59.3582 | 64.0274 | 63.9175 | -59.1614 | -59.2575 | -0.032043 | -0.073242 | 0.022888 | 123.23 | -0.21057 | -0.13733 | 0.054931 | -0.073242 | -0.16937 | 0.050354 | 0.041199 | -0.27008 | -0.10071 | -0.059509 | 123.0881 | 123.1201 | 59.0424 | -123.1384 | 123.1155 | 123.0057 | 59.1202 | -123.2346
68.6875 | 123.3353 | -59.0561 | 63.9542 | 0.40048 | 0.022598 | 0.073167 | 0.070738 | 0.13667 | 0.0069634 | 0.00289 | 0.29963 | -0.0042092 | 0.067339 | 0.06892 | 0.0029108 | -0.0018224 | 64.064 | 64.183 | -0.022888 | -59.3124 | 63.9633 | -59.1431 | -59.1431 | -58.992 | 0.041199 | -59.3308 | 64.0091 | 63.9084 | -59.1614 | -59.2529 | -0.086975 | -0.086975 | 0.009155 | 123.2391 | -0.25635 | -0.16937 | 0.10986 | -0.10529 | -0.19684 | 0.054931 | 0.064087 | -0.27466 | -0.07782 | -0.045777 | 123.0194 | 123.1201 | 59.0332 | -123.0972 | 123.0652 | 122.9645 | 59.0973 | -123.2071
69.6875 | 123.3582 | -59.0744 | 63.9771 | 0.62936 | -0.007309 | 0.068895 | 0.072874 | 0.14842 | -0.0037176 | 0.00075395 | 0.14704 | 0.0021988 | 0.059862 | 0.065716 | -0.0034972 | 0.0045866 | 64.0594 | 64.1464 | -0.027466 | -59.3033 | 64.0137 | -59.1156 | -59.1522 | -59.0286 | 0.027466 | -59.3399 | 64.0228 | 63.9175 | -59.1385 | -59.2484 | -0.041199 | -0.07782 | 0.036621 | 123.2208 | -0.22888 | -0.15106 | 0.082397 | -0.064087 | -0.17395 | 0.045776 | 0.045777 | -0.2655 | -0.091553 | -0.059509 | 123.0881 | 123.1338 | 59.0469 | -123.1293 | 123.0972 | 122.9919 | 59.1019 | -123.2254
70.6875 | 123.3444 | -59.111 | 63.9908 | 0.15634 | -0.003037 | 0.071031 | 0.073942 | 0.13026 | -0.010127 | -0.001382 | -0.020803 | 0.0054038 | 0.055589 | 0.056103 | -0.0002932 | 0.0024506 | 64.0594 | 64.1464 | -0.036621 | -59.3079 | 63.9908 | -59.1156 | -59.1705 | -59.0378 | 0.018311 | -59.3491 | 64.0503 | 63.9267 | -59.1797 | -59.2484 | -0.004578 | -0.059509 | 0 | 123.2574 | -0.19684 | -0.13733 | 0.068664 | -0.068664 | -0.13733 | 0.059509 | 0.073242 | -0.23804 | -0.10071 | -0.064087 | 123.1018 | 123.1705 | 59.0744 | -123.1613 | 123.1613 | 123.0377 | 59.1293 | -123.2391
71.6875 | 123.3719 | -59.079 | 63.9862 | 0.064784 | -0.016922 | 0.06035 | 0.066465 | 0.13346 | -0.020808 | 0.00289 | -0.036062 | 0.0043348 | 0.055589 | 0.058239 | 0.0029108 | 0.0013826 | 64.0228 | 64.151 | -0.032043 | -59.2987 | 64.0228 | -59.1202 | -59.1614 | -59.0103 | 0.068665 | -59.3124 | 64.032 | 63.9313 | -59.1476 | -59.2255 | -0.041199 | -0.082398 | 0.036621 | 123.23 | -0.21973 | -0.13733 | 0.036621 | -0.068665 | -0.14649 | 0.045776 | 0.068664 | -0.23346 | -0.086975 | -0.054932 | 123.1018 | 123.1018 | 59.0469 | -123.1476 | 123.111 | 123.0103 | 59.1476 | -123.2117
72.6875 | 123.3353 | -59.1019 | 63.9633 | 0.30892 | 0.008713 | 0.068895 | 0.068601 | 0.1356 | -0.0058536 | -0.004587 | 0.024973 | -0.0095502 | 0.064134 | 0.06892 | 0.017865 | -0.0071624 | 64.0411 | 64.1556 | -0.036621 | -59.3079 | 63.9954 | -59.1248 | -59.1431 | -59.0103 | 0.022888 | -59.3491 | 64.0457 | 63.9175 | -59.1614 | -59.2346 | -0.022888 | -0.041198 | 0.032043 | 123.2574 | -0.20599 | -0.1648 | 0.07782 | -0.059509 | -0.13275 | 0.082397 | 0.091553 | -0.24719 | -0.11444 | -0.045776 | 123.0972 | 123.143 | 59.0652 | -123.1064 | 123.1476 | 123.0194 | 59.1248 | -123.1979
73.6875 | 123.4406 | -59.0927 | 63.9725 | 0.23263 | 0.010849 | 0.069963 | 0.068601 | 0.13774 | 0.0058954 | 0.00289 | 0.2386 | 0.0011308 | 0.076952 | 0.071057 | 0.0071838 | 0.0013826 | 64.0594 | 64.183 | -0.018311 | -59.2987 | 63.9725 | -59.1293 | -59.1797 | -58.9966 | 0.041199 | -59.3308 | 64.0091 | 63.9221 | -59.1797 | -59.2484 | -0.036621 | -0.086975 | 0 | 123.2758 | -0.20599 | -0.11902 | 0.086975 | -0.086975 | -0.15564 | 0.036621 | 0.09613 | -0.23804 | -0.082398 | -0.050354 | 123.0652 | 123.1522 | 59.0744 | -123.1522 | 123.1018 | 123.0148 | 59.1339 | -123.2208
74.6875 | 123.3582 | -59.0836 | 64.0045 | 0.23263 | 0.008713 | 0.081712 | 0.064329 | 0.12919 | 0.0091004 | 0.007163 | 0.055491 | -0.0063462 | 0.061998 | 0.058239 | 0.0061158 | 0.0024506 | 64.0457 | 64.1602 | -0.036621 | -59.3124 | 63.9862 | -59.1202 | -59.1385 | -59.0286 | 0.032043 | -59.3582 | 64.0366 | 63.9175 | -59.1476 | -59.2346 | -0.036621 | -0.054932 | -0.018311 | 123.2437 | -0.22888 | -0.17395 | 0.041198 | -0.064087 | -0.15106 | 0.032043 | 0.054932 | -0.27466 | -0.1236 | -0.086975 | 123.0698 | 123.1293 | 59.0469 | -123.143 | 123.1201 | 123.0011 | 59.1156 | -123.2391
75.6875 | 123.381 | -59.0836 | 63.9908 | 0.21737 | -0.005173 | 0.076372 | 0.073942 | 0.13453 | 0.0026914 | -0.00245 | 0.11653 | -0.0031412 | 0.066271 | 0.058239 | -0.0013612 | -0.0028904 | 64.0274 | 64.1235 | -0.022888 | -59.317 | 64.0274 | -59.1202 | -59.1751 | -59.0286 | 0.022888 | -59.3582 | 64.0182 | 63.9175 | -59.1385 | -59.23 | -0.036621 | -0.091553 | 0.036621 | 123.2071 | -0.23346 | -0.14191 | 0.036621 | -0.054932 | -0.14648 | 0.027466 | 0.054932 | -0.27466 | -0.12817 | -0.073242 | 123.111 | 123.111 | 59.0607 | -123.1659 | 123.1018 | 123.0011 | 59.1064 | -123.2208
76.6875 | 123.3673 | -59.0698 | 63.9725 | -0.057287 | -0.01265 | 0.066759 | 0.056852 | 0.12599 | 0.0048274 | -0.00245 | -0.24969 | 0.0054038 | 0.058794 | 0.049694 | -0.0002932 | -0.0082304 | 64.0823 | 64.2014 | 0.036621 | -59.2804 | 64.0228 | -59.1064 | -59.1476 | -58.9645 | 0.15564 | -59.285 | 64.0228 | 63.9221 | -59.1476 | -59.2392 | -0.036621 | -0.07782 | 0.050354 | 123.2712 | -0.21057 | -0.13275 | 0.10986 | -0.07782 | -0.16937 | 0.050354 | 0.10528 | -0.21515 | -0.045776 | -0.050354 | 123.0927 | 123.1522 | 59.1064 | -123.1201 | 123.0927 | 122.9919 | 59.2255 | -123.2117
77.6875 | 123.3627 | -59.0973 | 63.9908 | 0.12582 | -0.004105 | 0.064622 | 0.05258 | 0.13026 | 0.00055539 | -0.006723 | -0.005544 | -0.0074142 | 0.054521 | 0.062512 | -0.0034972 | -0.010367 | 64.0274 | 64.151 | -0.027466 | -59.2987 | 64.0091 | -59.1248 | -59.1476 | -59.0057 | 0.068665 | -59.3308 | 64.0503 | 63.9175 | -59.1476 | -59.2438 | -0.027466 | -0.050354 | 0.01831 | 123.2483 | -0.20142 | -0.15106 | 0.036621 | -0.050354 | -0.14648 | 0.059509 | 0.091553 | -0.23346 | -0.086976 | -0.073242 | 123.1064 | 123.1247 | 59.0698 | -123.1384 | 123.1476 | 123.0148 | 59.166 | -123.2346
78.6875 | 123.3856 | -59.1064 | 64.0045 | 0.1716 | 0.008713 | 0.069963 | 0.063261 | 0.13667 | 0.0058954 | 0.001822 | -0.066579 | 0.0011308 | 0.051317 | 0.065716 | -0.0002932 | 0.00031457 | 64.0274 | 64.1464 | -0.027466 | -59.2941 | 63.9954 | -59.1064 | -59.1614 | -59.0103 | 0.064087 | -59.3262 | 64.0457 | 63.9175 | -59.1339 | -59.2392 | 0 | -0.054932 | -0.009156 | 123.2529 | -0.18768 | -0.13275 | 0.022888 | -0.027466 | -0.13275 | 0.041198 | 0.09613 | -0.21973 | -0.086975 | -0.086975 | 123.1018 | 123.1338 | 59.079 | -123.1659 | 123.1522 | 123.024 | 59.1705 | -123.2437
79.6875 | 123.349 | -59.0927 | 63.9816 | 0.12582 | 0.009781 | 0.078508 | 0.061125 | 0.12599 | -0.00051261 | 0.00075395 | 0.009715 | 0.0011308 | 0.051317 | 0.053967 | -0.0056342 | 0.0024506 | 64.0503 | 64.151 | -0.018311 | -59.2896 | 64.0182 | -59.0744 | -59.1843 | -59.0149 | 0.054932 | -59.3353 | 64.032 | 63.9221 | -59.1431 | -59.2484 | 0.01831 | -0.091553 | 0.036622 | 123.2437 | -0.19684 | -0.10529 | 0.068665 | -0.050354 | -0.15564 | 0.050354 | 0.077819 | -0.24262 | -0.086975 | -0.059509 | 123.111 | 123.143 | 59.0744 | -123.1659 | 123.1247 | 123.0148 | 59.1476 | -123.23
80.6875 | 123.3582 | -59.079 | 63.9633 | 0.12582 | -0.011582 | 0.073167 | 0.065397 | 0.1324 | -0.0069216 | -0.007791 | -0.005544 | 0.0054038 | 0.039568 | 0.041149 | -0.0056342 | -0.00075443 | 64.0411 | 64.1602 | -0.018311 | -59.2941 | 63.9999 | -59.1293 | -59.1751 | -59.0195 | 0.050354 | -59.3308 | 64.0274 | 63.913 | -59.1385 | -59.2438 | -0.050354 | -0.096131 | 0.036621 | 123.2391 | -0.21515 | -0.11902 | 0.07782 | -0.05951 | -0.1648 | 0.064087 | 0.059509 | -0.25177 | -0.086976 | -0.050354 | 123.0789 | 123.1201 | 59.0607 | -123.1384 | 123.1064 | 122.9919 | 59.1293 | -123.2071
81.6875 | 123.4222 | -59.0424 | 63.9862 | -0.14884 | -0.008377 | 0.068895 | 0.062193 | 0.12385 | 0.0080314 | 0.001822 | -0.31072 | -0.0010052 | 0.053453 | 0.060376 | 0.0071838 | -0.0039584 | 64.119 | 64.2517 | 0.073242 | -59.2484 | 64.032 | -59.0927 | -59.1339 | -58.9279 | 0.18768 | -59.2346 | 64.0366 | 63.9359 | -59.1156 | -59.2117 | -0.050354 | -0.091553 | 0.045776 | 123.2941 | -0.20599 | -0.11444 | 0.13275 | -0.073243 | -0.16937 | 0.050354 | 0.11444 | -0.19226 | -0.022888 | -0.050354 | 123.0743 | 123.1613 | 59.1156 | -123.1201 | 123.0789 | 122.9782 | 59.23 | -123.1979
82.6875 | 123.3948 | -59.0332 | 63.9816 | -0.1641 | 0.008713 | 0.071031 | 0.067533 | 0.13987 | 0.01444 | -0.004587 | -0.20391 | -0.0063462 | 0.064134 | 0.065716 | -0.0067022 | -0.0039584 | 64.1144 | 64.2517 | 0.068665 | -59.2484 | 64.0137 | -59.1019 | -59.1156 | -58.9279 | 0.18768 | -59.2392 | 64.0411 | 63.9221 | -59.1614 | -59.2209 | -0.068665 | -0.082398 | 0.032044 | 123.2849 | -0.21515 | -0.13275 | 0.13275 | -0.12817 | -0.18768 | 0.05951 | 0.10529 | -0.20599 | -0.018311 | -0.059509 | 123.0469 | 123.1476 | 59.1019 | -123.0972 | 123.0743 | 122.9553 | 59.2209 | -123.2025
83.6875 | 123.3582 | -59.024 | 63.9908 | -0.30143 | -0.005173 | 0.078508 | 0.062193 | 0.1324 | -0.00051261 | -0.00245 | -0.40227 | -0.0031412 | 0.055589 | 0.060376 | 0.0050478 | -0.0050264 | 64.0961 | 64.27 | 0.11444 | -59.2438 | 64.0274 | -59.0744 | -59.1431 | -58.96 | 0.17395 | -59.2575 | 64.0457 | 63.8992 | -59.1385 | -59.2255 | -0.050354 | -0.11902 | 0.036621 | 123.2941 | -0.21973 | -0.10071 | 0.10529 | -0.11444 | -0.20142 | 0.054931 | 0.064087 | -0.23346 | -0.032043 | -0.091553 | 123.0515 | 123.1201 | 59.1385 | -123.1338 | 123.0698 | 122.9233 | 59.198 | -123.2162
84.6875 | 123.3215 | -59.0744 | 63.9999 | -0.39298 | -0.004105 | 0.075304 | 0.076078 | 0.1356 | 0.0048274 | 0.003958 | -0.47857 | 0.0011308 | 0.059862 | 0.057171 | 0.0039788 | -0.0028904 | 64.1052 | 64.2426 | 0.10071 | -59.2484 | 64.0228 | -59.0881 | -59.1476 | -59.0652 | 0.24719 | -59.3124 | 64.0778 | 63.9084 | -59.1339 | -59.2438 | -0.013733 | -0.073242 | 0.022888 | 123.317 | -0.17395 | -0.10071 | 0.10529 | -0.059509 | -0.16937 | 0.07782 | 0.009155 | -0.23804 | -0.068665 | -0.091553 | 123.0972 | 123.1796 | 59.1751 | -123.1476 | 123.1522 | 122.9828 | 59.3216 | -123.2437
85.6875 | 123.4634 | -59.0515 | 63.9954 | 0.095301 | -0.004105 | 0.076372 | 0.071806 | 0.13667 | -0.00051261 | -0.00245 | -0.05132 | -0.0031412 | 0.061998 | 0.059307 | -0.0013612 | -0.00075443 | 64.0366 | 64.1739 | -0.004578 | -59.2987 | 64.0503 | -59.1248 | -59.1888 | -58.992 | 0.073242 | -59.3033 | 64.0411 | 63.9267 | -59.1293 | -59.2529 | -0.073242 | -0.13733 | 0.054932 | 123.2254 | -0.24719 | -0.10986 | 0.041199 | -0.077819 | -0.20142 | 0.045777 | 0.05951 | -0.25177 | -0.050354 | -0.068664 | 123.1018 | 123.0881 | 59.0469 | -123.1842 | 123.0927 | 122.9782 | 59.1248 | -123.2483
86.6875 | 123.3078 | -59.0881 | 63.9862 | 0.064784 | -0.007309 | 0.076372 | 0.063261 | 0.13774 | 0.0037594 | -0.00245 | 0.11653 | -0.0020732 | 0.058794 | 0.064648 | 0.011456 | 0.0013826 | 64.0045 | 64.1464 | -0.036621 | -59.3033 | 64.0091 | -59.1202 | -59.1431 | -59.0195 | 0.041199 | -59.3399 | 64.0366 | 63.913 | -59.1522 | -59.2392 | -0.032043 | -0.054931 | 0.022888 | 123.2346 | -0.21515 | -0.16022 | 0.018311 | -0.064087 | -0.15106 | 0.050354 | 0.068665 | -0.25177 | -0.10071 | -0.073242 | 123.0972 | 123.0927 | 59.0515 | -123.1293 | 123.1247 | 123.0011 | 59.1293 | -123.2254
87.6875 | 123.3215 | -59.0652 | 63.9542 | 0.21737 | -0.007309 | 0.062486 | 0.076078 | 0.12385 | 0.0016234 | 0.001822 | 0.086009 | -0.0052782 | 0.053453 | 0.049694 | -0.0013612 | 0.0013826 | 64.0274 | 64.1647 | -0.036621 | -59.3079 | 63.9862 | -59.1202 | -59.1476 | -59.0286 | 0.036621 | -59.3353 | 64.064 | 63.9038 | -59.1522 | -59.2621 | -0.054931 | -0.082397 | 0.032043 | 123.23 | -0.24261 | -0.16022 | 0.073242 | -0.086975 | -0.19684 | 0.10986 | 0.036622 | -0.27008 | -0.073242 | -0.050354 | 123.0515 | 123.0927 | 59.0286 | -123.1018 | 123.1293 | 122.9691 | 59.1019 | -123.2162
88.6875 | 123.3444 | -59.079 | 63.9999 | 0.14108 | -0.016922 | 0.059282 | 0.062193 | 0.14094 | -0.0015816 | 0.001822 | -0.005544 | -0.0020732 | 0.059862 | 0.072125 | 0.010388 | -0.0071624 | 64.0274 | 64.1464 | -0.032043 | -59.2941 | 64.0137 | -59.1248 | -59.1614 | -59.0149 | 0.059509 | -59.3216 | 64.0503 | 63.9313 | -59.1476 | -59.2438 | -0.045777 | -0.082398 | 0.013733 | 123.2254 | -0.21515 | -0.13275 | 0.027466 | -0.068665 | -0.1648 | 0.050354 | 0.064086 | -0.24262 | -0.07782 | -0.068665 | 123.0927 | 123.1064 | 59.0469 | -123.1613 | 123.1293 | 123.0103 | 59.1385 | -123.2437
89.6875 | 123.4039 | -59.0561 | 63.9221 | 0.080043 | -0.030808 | 0.075304 | 0.071806 | 0.12065 | -0.00051261 | 0.009299 | -0.11236 | -0.0010052 | 0.061998 | 0.055035 | 0.0061158 | 0.00031457 | 64.0549 | 64.1922 | 0.018311 | -59.2712 | 64.0045 | -59.0927 | -59.1476 | -58.9737 | 0.11902 | -59.2804 | 64.0732 | 63.9908 | -59.0881 | -59.1705 | -0.036621 | -0.091553 | 0.082398 | 123.2483 | -0.21515 | -0.1236 | 0.13275 | -0.032044 | -0.11444 | 0.15106 | 0.082397 | -0.22431 | -0.10986 | 0.068665 | 123.0606 | 123.111 | 59.0744 | -123.0698 | 123.1293 | 123.0469 | 59.1751 | -123.0927
90.6875 | 123.3719 | -59.0744 | 64.0045 | 0.019007 | -0.019058 | 0.080644 | 0.070738 | 0.12706 | -0.0026496 | 0.003958 | -0.097097 | 6.2833e-05 | 0.047044 | 0.072125 | -0.0013612 | 0.0067226 | 64.0549 | 64.1876 | 0 | -59.285 | 64.0045 | -59.111 | -59.1385 | -58.9828 | 0.10986 | -59.2896 | 64.0274 | 63.9175 | -59.1248 | -59.2163 | -0.036621 | -0.064087 | 0 | 123.262 | -0.21057 | -0.14648 | 0.050354 | -0.050354 | -0.14191 | 0.022888 | 0.091553 | -0.21515 | -0.073242 | -0.086975 | 123.0789 | 123.1293 | 59.0744 | -123.143 | 123.1018 | 122.9919 | 59.1843 | -123.2208
91.6875 | 123.3582 | -59.0744 | 64.0137 | -0.026769 | 0.00444 | 0.074235 | 0.076078 | 0.12385 | 0.0058954 | 0.00075395 | -0.097097 | 0.0054038 | 0.053453 | 0.062512 | -0.0056342 | -0.0018224 | 64.0411 | 64.1922 | 0.004578 | -59.2712 | 64.0228 | -59.111 | -59.1568 | -59.0012 | 0.10986 | -59.2987 | 64.0594 | 63.8992 | -59.1476 | -59.23 | -0.036621 | -0.082397 | 0.009155 | 123.2666 | -0.19684 | -0.11444 | 0.027466 | -0.073242 | -0.15564 | 0.045776 | 0.073242 | -0.2243 | -0.068664 | -0.11444 | 123.0972 | 123.1155 | 59.079 | -123.1705 | 123.1338 | 122.9736 | 59.1843 | -123.2437
92.6875 | 123.3765 | -59.0698 | 63.9862 | 0.034266 | -0.027603 | 0.062486 | 0.070738 | 0.14094 | 0.0016234 | -0.00245 | -0.066579 | -0.015959 | 0.051317 | 0.052899 | -0.0013612 | 0.0024506 | 64.0411 | 64.1647 | 0.009155 | -59.2804 | 64.0045 | -59.111 | -59.1522 | -58.9828 | 0.10071 | -59.3079 | 64.0549 | 63.8947 | -59.1568 | -59.2346 | -0.041199 | -0.082398 | 0.018311 | 123.2346 | -0.21057 | -0.12817 | 0.054932 | -0.086975 | -0.1648 | 0.068665 | 0.086975 | -0.23804 | -0.073242 | -0.091553 | 123.0743 | 123.111 | 59.079 | -123.1384 | 123.1247 | 122.9645 | 59.1705 | -123.2208
93.6875 | 123.3124 | -59.1064 | 63.9725 | 0.40048 | -0.006241 | 0.075304 | 0.060057 | 0.13133 | 0.0069634 | 0.001822 | 0.31489 | -0.0031412 | 0.058794 | 0.06358 | 0.012524 | 0.00031457 | 63.9679 | 64.4806 | 0.086975 | -59.3719 | 64.0366 | -59.0973 | -59.1522 | -59.0103 | 0.009155 | -59.3445 | 64.0366 | 63.9084 | -59.1385 | -59.2484 | 0.009155 | -0.045777 | 0.064087 | 123.587 | -0.2655 | -0.21973 | -0.004577 | -0.032044 | -0.14191 | 0.064087 | 0.09613 | -0.23804 | -0.09613 | -0.064087 | 123.143 | 123.0743 | 59.1934 | -123.1247 | 123.143 | 123.0148 | 59.1156 | -123.2208
94.6875 | 123.3307 | -59.0927 | 63.9771 | 0.080043 | -0.01265 | 0.07744 | 0.067533 | 0.12599 | 0.00055539 | 0.00289 | 0.14704 | 0.0032668 | 0.036363 | 0.06358 | 0.016797 | 0.0013826 | 64.0274 | 64.1373 | -0.041199 | -59.3033 | 63.9908 | -59.111 | -59.1476 | -59.0698 | -0.018311 | -59.3491 | 64.0366 | 63.8855 | -59.1751 | -59.2484 | -0.018311 | -0.054932 | 0.013733 | 123.23 | -0.21057 | -0.15564 | 0.050354 | -0.082398 | -0.15564 | 0.059509 | 0.022888 | -0.25635 | -0.10071 | -0.091553 | 123.0835 | 123.1201 | 59.0515 | -123.1247 | 123.1293 | 122.9782 | 59.0744 | -123.2254
95.6875 | 123.3627 | -59.0698 | 63.9954 | 0.18685 | -0.01265 | 0.066759 | 0.061125 | 0.13453 | 0.0037594 | -0.004587 | -0.005544 | -0.0084822 | 0.053453 | 0.062512 | -0.0067022 | 0.0088586 | 64.0137 | 64.1373 | -0.022888 | -59.2987 | 64.0274 | -59.1339 | -59.1339 | -59.0286 | 0.07782 | -59.3216 | 64.0549 | 63.9267 | -59.1614 | -59.2255 | -0.064087 | -0.064087 | 0.032044 | 123.2071 | -0.22888 | -0.1648 | 0.018311 | -0.091553 | -0.15564 | 0.05951 | 0.041199 | -0.25177 | -0.09613 | -0.068664 | 123.0972 | 123.0835 | 59.0469 | -123.1293 | 123.1247 | 122.9965 | 59.1476 | -123.2208
96.7031 | 123.3078 | -59.0881 | 64.0091 | -0.30143 | 0.02687 | 0.057146 | 0.064329 | 0.12172 | 0.034734 | -0.00031405 | -0.40227 | 0.0086078 | 0.064134 | 0.053967 | 0.014661 | -0.022116 | 64.0961 | 64.1556 | 0.009155 | -59.2758 | 64.0732 | -59.1202 | -59.1705 | -59.0012 | 0.086975 | -59.3719 | 64.0823 | 63.9587 | -59.166 | -59.2484 | -0.032043 | -0.082397 | 0.064087 | 123.2437 | -0.18768 | -0.10529 | 0.086975 | -0.07782 | -0.16022 | 0.073242 | 0.086975 | -0.28381 | -0.1236 | -0.050354 | 123.1613 | 123.1842 | 59.0973 | -123.1796 | 123.1705 | 123.0469 | 59.1751 | -123.2574
97.6875 | 123.3673 | -59.0561 | 63.9771 | -0.19462 | -0.023331 | 0.063554 | 0.060057 | 0.12812 | -0.017603 | -0.00245 | -0.20391 | -0.0010052 | 0.055589 | 0.066784 | 0.0061158 | -0.0039584 | 64.0594 | 64.2105 | 0.036621 | -59.2804 | 64.032 | -59.1019 | -59.1339 | -58.9737 | 0.14648 | -59.2667 | 64.0274 | 63.9221 | -59.1248 | -59.2163 | -0.045777 | -0.07782 | 0.054931 | 123.2666 | -0.22431 | -0.14649 | 0.082397 | -0.068665 | -0.16022 | 0.050354 | 0.082397 | -0.21057 | -0.050354 | -0.054932 | 123.0881 | 123.1155 | 59.0927 | -123.111 | 123.0835 | 122.9782 | 59.2026 | -123.1934
98.6875 | 123.3856 | -59.0652 | 63.9908 | -0.13358 | -0.016922 | 0.076372 | 0.06967 | 0.12812 | -0.00051261 | 0.00075395 | -0.036062 | 0.0086078 | 0.055589 | 0.065716 | -0.0067022 | -0.00075443 | 64.0686 | 64.1922 | 0.013733 | -59.2667 | 64.0137 | -59.1064 | -59.1568 | -58.96 | 0.14191 | -59.2667 | 64.0457 | 63.9313 | -59.1385 | -59.23 | -0.041198 | -0.091552 | 0.022888 | 123.2574 | -0.20142 | -0.10986 | 0.07782 | -0.073242 | -0.16479 | 0.054931 | 0.10529 | -0.20142 | -0.036621 | -0.05951 | 123.0789 | 123.1339 | 59.079 | -123.1476 | 123.111 | 122.9965 | 59.2072 | -123.2208
99.6875 | 123.4039 | -59.0424 | 63.9954 | -0.026769 | -0.00090105 | 0.072099 | 0.053648 | 0.13453 | -0.022944 | -0.009927 | -0.11236 | 0.0021988 | 0.056658 | 0.059307 | -0.0088382 | 0.0056546 | 64.0549 | 64.2334 | 0.032043 | -59.2712 | 64.0228 | -59.111 | -59.1339 | -58.9737 | 0.11444 | -59.2712 | 64.0411 | 63.913 | -59.1339 | -59.2072 | -0.068665 | -0.091553 | 0.027466 | 123.2758 | -0.22888 | -0.13733 | 0.05951 | -0.091553 | -0.16479 | 0.045777 | 0.068664 | -0.22888 | -0.064087 | -0.082397 | 123.0652 | 123.0972 | 59.0744 | -123.1293 | 123.0835 | 122.9553 | 59.1568 | -123.2025
100.6875 | 123.3582 | -59.0698 | 63.9862 | 0.034266 | -0.014786 | 0.084917 | 0.061125 | 0.13453 | 0.0058954 | -0.005655 | -0.26494 | -0.0010052 | 0.061998 | 0.061444 | 0.0082518 | -0.00075443 | 64.0091 | 64.2975 | 0.07782 | -59.2621 | 64.0228 | -59.111 | -59.1476 | -59.0195 | 0.073242 | -59.3033 | 64.0228 | 63.9038 | -59.1568 | -59.2209 | -0.041199 | -0.07782 | 0.036621 | 123.3673 | -0.19226 | -0.11444 | 0.022888 | -0.086975 | -0.15106 | 0.036621 | 0.050354 | -0.23346 | -0.082398 | -0.082397 | 123.0927 | 123.0789 | 59.1476 | -123.1338 | 123.0927 | 122.9736 | 59.1431 | -123.2071
101.7031 | 123.1842 | -59.0973 | 64.0778 | -0.46927 | 0.011917 | 0.083848 | 0.0921 | 0.13881 | 0.0091004 | 0.011435 | -0.63115 | 0.0064718 | 0.086565 | 0.06892 | 0.011456 | -0.0060944 | 64.0274 | 64.1052 | -0.013733 | -59.3079 | 64.0732 | -59.111 | -59.1614 | -59.0652 | 0.059509 | -59.3903 | 64.1418 | 63.9771 | -59.1568 | -59.2484 | -0.013733 | -0.064087 | -0.004578 | 123.2025 | -0.21057 | -0.14648 | -0.050354 | -0.059509 | -0.15106 | 0.064087 | 0.032043 | -0.29297 | -0.14191 | -0.10071 | 123.1705 | 123.1247 | 59.0836 | -123.2391 | 123.2391 | 123.0743 | 59.1568 | -123.3261
102.6875 | 123.3673 | -59.0744 | 63.9679 | -0.072545 | -0.019058 | 0.073167 | 0.070738 | 0.12919 | -0.0090576 | 0.008231 | -0.20391 | -0.0074142 | 0.052385 | 0.057171 | -0.0045652 | 0.0088586 | 64.0503 | 64.1922 | 0.022888 | -59.2712 | 64.0274 | -59.0927 | -59.1522 | -58.96 | 0.13733 | -59.2667 | 64.0366 | 63.9313 | -59.1339 | -59.2392 | -0.01831 | -0.07782 | 0.059509 | 123.2666 | -0.19684 | -0.11902 | 0.082397 | -0.059509 | -0.16479 | 0.068664 | 0.11444 | -0.19226 | -0.027466 | -0.036622 | 123.1018 | 123.1247 | 59.0973 | -123.1201 | 123.111 | 123.0057 | 59.2117 | -123.2071
103.6875 | 123.3719 | -59.0744 | 63.9908 | -0.087804 | 0.005508 | 0.074235 | 0.051512 | 0.13346 | -0.0079896 | -0.003518 | -0.38701 | -0.0010052 | 0.057726 | 0.049694 | -0.0024292 | -0.00075443 | 64.1052 | 64.2883 | 0.10986 | -59.2392 | 64.0182 | -59.0744 | -59.1248 | -58.9417 | 0.18768 | -59.2438 | 64.0228 | 63.9084 | -59.1385 | -59.2209 | 0 | -0.050354 | 0.027466 | 123.3627 | -0.16479 | -0.11444 | 0.11444 | -0.064087 | -0.14648 | 0.032043 | 0.13275 | -0.16937 | -0.022888 | -0.082398 | 123.0927 | 123.1796 | 59.1843 | -123.1155 | 123.0972 | 122.9828 | 59.2621 | -123.2117
104.6875 | 123.3765 | -59.0332 | 64.0137 | -0.11832 | -0.023331 | 0.072099 | 0.072874 | 0.13774 | -0.0047856 | -0.010995 | -0.32598 | -0.0031412 | 0.057726 | 0.044354 | 0.0018428 | -0.0018224 | 64.0915 | 64.2883 | 0.10071 | -59.2346 | 64.0274 | -59.0836 | -59.1248 | -58.9462 | 0.19226 | -59.2392 | 64.0594 | 63.9175 | -59.079 | -59.2163 | -0.050354 | -0.091553 | 0.013733 | 123.3215 | -0.20142 | -0.10986 | 0.07782 | -0.045776 | -0.18311 | 0.045776 | 0.086975 | -0.20599 | -0.022888 | -0.09613 | 123.0606 | 123.1247 | 59.1339 | -123.1384 | 123.0927 | 122.9507 | 59.2255 | -123.23
105.6875 | 123.3765 | -59.0698 | 64.0045 | -0.042028 | -0.013718 | 0.075304 | 0.062193 | 0.1324 | -0.011195 | 0.00075395 | -0.49383 | 0.0032668 | 0.048113 | 0.057171 | 0.0061158 | -0.0050264 | 64.119 | 64.2792 | 0.09613 | -59.2209 | 64.0091 | -59.0561 | -59.1385 | -58.9462 | 0.19684 | -59.2484 | 64.0549 | 63.9084 | -59.1248 | -59.2255 | 0.013733 | -0.068665 | 0.004577 | 123.349 | -0.15106 | -0.082397 | 0.11444 | -0.054932 | -0.15564 | 0.050354 | 0.1236 | -0.17853 | -0.022888 | -0.096131 | 123.0789 | 123.1888 | 59.166 | -123.143 | 123.1247 | 122.9782 | 59.2667 | -123.23
106.7031 | 123.3215 | -59.079 | 64.0366 | -0.36246 | 0.020462 | 0.06569 | 0.082487 | 0.13346 | 0.022985 | 0.007163 | -0.60064 | 0.0032668 | 0.081224 | 0.060376 | 0.012524 | -0.014639 | 64.0503 | 64.1373 | -0.004578 | -59.285 | 64.0594 | -59.1339 | -59.1431 | -59.0424 | 0.064087 | -59.3628 | 64.0823 | 63.9359 | -59.166 | -59.23 | -0.054932 | -0.064087 | 0.022888 | 123.2162 | -0.20599 | -0.14191 | 0.013733 | -0.086976 | -0.15106 | 0.045776 | 0.036621 | -0.28381 | -0.13275 | -0.10071 | 123.1384 | 123.1293 | 59.0744 | -123.1796 | 123.1613 | 123.0148 | 59.1431 | -123.2666
107.6875 | 123.3536 | -59.0698 | 63.9999 | -0.20987 | 0.016189 | 0.079576 | 0.063261 | 0.13774 | -0.017603 | -0.004587 | -0.11236 | -0.0095502 | 0.052385 | 0.066784 | -0.0056342 | -0.0082304 | 64.0366 | 64.2014 | 0.032043 | -59.2621 | 64.0137 | -59.1202 | -59.1522 | -58.992 | 0.12817 | -59.2712 | 64.0045 | 63.9084 | -59.1202 | -59.2072 | -0.050354 | -0.082398 | 0.013733 | 123.2712 | -0.19226 | -0.10986 | 0.036621 | -0.050354 | -0.13733 | 0.004578 | 0.07782 | -0.20142 | -0.064087 | -0.091553 | 123.0835 | 123.1064 | 59.1019 | -123.1522 | 123.0743 | 122.9782 | 59.198 | -123.2071
108.6875 | 123.3856 | -59.0927 | 63.9633 | -0.10306 | -0.020127 | 0.074235 | 0.068601 | 0.14308 | -0.011195 | -0.00031405 | -0.005544 | -0.0010052 | 0.036363 | 0.062512 | -0.0045652 | -0.0050264 | 64.0457 | 64.1968 | 0.022888 | -59.2941 | 63.9999 | -59.0973 | -59.1431 | -58.9737 | 0.11444 | -59.2667 | 64.032 | 63.9175 | -59.1248 | -59.2209 | -0.004578 | -0.050354 | 0.036621 | 123.2895 | -0.20142 | -0.15106 | 0.082397 | -0.032044 | -0.12817 | 0.068664 | 0.11902 | -0.17395 | -0.045777 | -0.045776 | 123.0927 | 123.1384 | 59.1156 | -123.1064 | 123.1247 | 123.0103 | 59.2072 | -123.1842
109.6875 | 123.3719 | -59.0469 | 64.0137 | -1.6442 | 0.018326 | 0.072099 | 0.064329 | 0.13774 | -0.0069216 | -0.001382 | -0.44805 | -0.0042092 | 0.055589 | 0.06892 | 0.0082518 | -0.0050264 | 64.1006 | 64.2471 | 0.10986 | -59.2438 | 64.0182 | -59.0744 | -59.1202 | -58.9508 | 0.1831 | -59.2621 | 64.0411 | 63.9221 | -59.1339 | -59.2163 | -0.027466 | -0.073242 | 0.004578 | 123.2941 | -0.19684 | -0.1236 | 0.086975 | -0.086975 | -0.16937 | 0.027466 | 0.09613 | -0.21515 | -0.045776 | -0.091553 | 123.0652 | 123.1476 | 59.1568 | -123.1338 | 123.0881 | 122.9691 | 59.23 | -123.23
110.6875 | 123.3627 | -59.0652 | 63.9725 | -0.91178 | -0.01265 | 0.072099 | 0.064329 | 0.14201 | -0.0069216 | -0.008859 | -0.46331 | 0.0043348 | 0.06093 | 0.049694 | -0.0002932 | -0.0039584 | 64.1144 | 64.2563 | 0.091553 | -59.2346 | 64.0091 | -59.0927 | -59.1156 | -58.9691 | 0.20142 | -59.2575 | 64.0457 | 63.9084 | -59.1522 | -59.2209 | -0.027465 | -0.050354 | 0.036621 | 123.3215 | -0.16937 | -0.11902 | 0.14191 | -0.086975 | -0.15564 | 0.073242 | 0.096131 | -0.19226 | -0.036621 | -0.064087 | 123.0743 | 123.1796 | 59.1568 | -123.0881 | 123.111 | 122.9736 | 59.2667 | -123.1934
111.7031 | 123.2666 | -59.1339 | 63.9816 | -0.057287 | 0.070663 | 0.061418 | 0.091032 | 0.13133 | 0.044347 | 0.009299 | -0.31072 | 0.0021988 | 0.069475 | 0.062512 | 0.015729 | -0.012503 | 64.0686 | 64.1327 | -0.036621 | -59.3124 | 64.0594 | -59.1339 | -59.1614 | -59.0424 | 0.045776 | -59.3811 | 64.0915 | 63.9175 | -59.1614 | -59.2758 | 0 | -0.027466 | 0.07782 | 123.2666 | -0.17853 | -0.15106 | 0.086976 | -0.027466 | -0.14191 | 0.10986 | 0.091553 | -0.24719 | -0.10529 | -0.064086 | 123.1934 | 123.2025 | 59.0973 | -123.143 | 123.2254 | 123.0515 | 59.1797 | -123.2574
112.6875 | 123.3673 | -59.0378 | 63.9999 | 0.034266 | -0.024399 | 0.066759 | 0.066465 | 0.12599 | -0.00051261 | 0.007163 | -0.29546 | 0.0054038 | 0.053453 | 0.069989 | -0.0045652 | -0.0028904 | 64.0549 | 64.2471 | 0.091553 | -59.2163 | 64.0274 | -59.079 | -59.1385 | -58.96 | 0.19226 | -59.2392 | 64.0366 | 63.9542 | -59.1156 | -59.2163 | -0.041198 | -0.10071 | 0.027466 | 123.2849 | -0.17853 | -0.07782 | 0.054932 | -0.07782 | -0.17853 | 0.036621 | 0.07782 | -0.20142 | -0.022888 | -0.045776 | 123.0652 | 123.0927 | 59.1293 | -123.1384 | 123.0743 | 122.9919 | 59.23 | -123.2162
113.6875 | 123.3582 | -59.0515 | 63.9908 | -0.9423 | 0.006576 | 0.07744 | 0.062193 | 0.12278 | -0.0090576 | -0.007791 | -0.3565 | 6.2833e-05 | 0.049181 | 0.044354 | 0.0050478 | -0.013571 | 64.0594 | 64.2471 | 0.086975 | -59.2209 | 63.9999 | -59.0744 | -59.1385 | -58.96 | 0.18768 | -59.2392 | 64.0594 | 63.9084 | -59.1385 | -59.2072 | -0.022888 | -0.086975 | 0.009155 | 123.2986 | -0.16937 | -0.082397 | 0.068664 | -0.086975 | -0.15564 | 0.068664 | 0.091553 | -0.18768 | -0.032044 | -0.082398 | 123.0515 | 123.111 | 59.1385 | -123.1293 | 123.111 | 122.9599 | 59.2392 | -123.1979
114.6875 | 123.4039 | -59.0469 | 63.9999 | -0.19462 | 0.00016795 | 0.073167 | 0.050443 | 0.13346 | -0.0047856 | -0.005655 | -0.005544 | -0.0020732 | 0.042772 | 0.06358 | -0.010974 | 0.0013826 | 64.0869 | 64.2151 | 0.068665 | -59.2712 | 64.0137 | -59.1019 | -59.1339 | -58.9417 | 0.19226 | -59.2209 | 64.0457 | 63.9587 | -59.1202 | -59.2209 | -0.054932 | -0.086975 | 0.013733 | 123.262 | -0.2243 | -0.13733 | 0.086975 | -0.073242 | -0.17395 | 0.045776 | 0.10529 | -0.17395 | 0 | -0.041199 | 123.0606 | 123.1338 | 59.1156 | -123.1338 | 123.0927 | 123.0057 | 59.2392 | -123.2208
115.6875 | 123.381 | -59.0332 | 64.0274 | -5.6725 | -0.00090105 | 0.062486 | 0.045103 | 0.12278 | 0.0048274 | -0.001382 | -0.23443 | -0.0042092 | 0.064134 | 0.06892 | -0.0024292 | -0.0050264 | 64.0549 | 64.27 | 0.050354 | -59.2529 | 64.0091 | -59.111 | -59.1431 | -58.9554 | 0.19226 | -59.2392 | 64.0549 | 63.8901 | -59.1248 | -59.1934 | -0.07782 | -0.10986 | -0.018311 | 123.3032 | -0.21973 | -0.10986 | 0.027466 | -0.091553 | -0.16022 | 0.027466 | 0.07782 | -0.20599 | -0.045777 | -0.13733 | 123.0423 | 123.0881 | 59.0836 | -123.1705 | 123.0881 | 122.9233 | 59.2255 | -123.2208
116.7031 | 123.2849 | -59.1064 | 63.9954 | -0.20987 | 0.058914 | 0.056077 | 0.099577 | 0.13133 | 0.027258 | 0.014639 | -0.34124 | 0.0032668 | 0.065202 | 0.065716 | 0.010388 | -0.013571 | 64.0686 | 64.151 | -0.004578 | -59.2758 | 64.0594 | -59.1064 | -59.166 | -59.0195 | 0.045776 | -59.3719 | 64.0457 | 63.9267 | -59.1843 | -59.2758 | 0 | -0.05951 | 0.064087 | 123.2574 | -0.16937 | -0.10986 | 0.073243 | -0.07782 | -0.16937 | 0.050354 | 0.086975 | -0.2655 | -0.09613 | -0.068664 | 123.1659 | 123.175 | 59.1019 | -123.1613 | 123.1522 | 123.0331 | 59.1522 | -123.2712
117.6875 | 123.349 | -59.0698 | 64.0137 | -0.36246 | -0.001969 | 0.074235 | 0.077146 | 0.13453 | -0.012263 | 0.007163 | -0.32598 | -0.0063462 | 0.052385 | 0.059307 | -0.0045652 | 0.0013826 | 64.0778 | 64.2242 | 0.10529 | -59.2484 | 64.0137 | -59.111 | -59.1476 | -58.992 | 0.19684 | -59.2804 | 64.0503 | 63.9313 | -59.1431 | -59.2026 | -0.041199 | -0.07782 | 0 | 123.2941 | -0.17853 | -0.10071 | 0.064087 | -0.073242 | -0.13275 | 0.036621 | 0.07782 | -0.21057 | -0.07782 | -0.082398 | 123.0835 | 123.1476 | 59.1751 | -123.1613 | 123.1201 | 123.0011 | 59.2667 | -123.2162
118.6875 | 123.3261 | -59.0469 | 64.0137 | -0.37772 | 0.016189 | 0.068895 | 0.068601 | 0.13346 | -0.012263 | 0.008231 | -0.41753 | -0.017027 | 0.065202 | 0.050762 | -0.0045652 | -0.0018224 | 64.0732 | 64.238 | 0.09613 | -59.2346 | 64.0091 | -59.0881 | -59.1248 | -58.992 | 0.1831 | -59.2712 | 64.0411 | 63.9175 | -59.111 | -59.2163 | -0.041199 | -0.07782 | -0.004578 | 123.2849 | -0.18768 | -0.10986 | 0.059509 | -0.064087 | -0.16937 | 0.027466 | 0.054932 | -0.2243 | -0.054931 | -0.09613 | 123.056 | 123.1201 | 59.1431 | -123.1384 | 123.0881 | 122.9645 | 59.23 | -123.23
119.6875 | 123.3673 | -59.0561 | 64.0182 | -0.25565 | -0.013718 | 0.069963 | 0.064329 | 0.12599 | -0.017603 | -0.006723 | -0.34124 | -0.0084822 | 0.056658 | 0.053967 | 0.0029108 | -0.0050264 | 64.064 | 64.2334 | 0.09613 | -59.2346 | 63.9999 | -59.0881 | -59.1202 | -58.9737 | 0.16937 | -59.2712 | 64.0366 | 63.9267 | -59.1431 | -59.2026 | -0.032044 | -0.064087 | -0.018311 | 123.2895 | -0.17853 | -0.11444 | 0.045776 | -0.086975 | -0.14648 | 0.01831 | 0.082397 | -0.21515 | -0.068664 | -0.091553 | 123.056 | 123.1201 | 59.1522 | -123.1384 | 123.0927 | 122.9828 | 59.2255 | -123.2208
120.6875 | 123.3719 | -59.0698 | 63.9816 | -0.026769 | -0.015854 | 0.061418 | 0.061125 | 0.13453 | -0.020808 | -0.009927 | -0.20391 | -0.03198 | 0.044908 | 0.08601 | -0.0002932 | -0.0018224 | 64.119 | 64.2929 | 0.10529 | -59.2438 | 64.0228 | -59.0881 | -59.111 | -58.9554 | 0.1236 | -59.2529 | 64.0366 | 63.9175 | -59.1431 | -59.23 | -0.018311 | -0.041199 | 0.041199 | 123.3627 | -0.17395 | -0.13275 | 0.13733 | -0.073242 | -0.16022 | 0.054932 | 0.11444 | -0.18311 | -0.022888 | -0.064086 | 123.0927 | 123.1888 | 59.1751 | -123.0927 | 123.1064 | 122.9874 | 59.1934 | -123.2117
121.7031 | 123.2666 | -59.0927 | 64.0091 | 0.30892 | 0.037552 | 0.059282 | 0.070738 | 0.13133 | 0.027258 | -0.001382 | 0.086009 | -0.0084822 | 0.071611 | 0.050762 | 0.0071838 | 0.0013826 | 64.0045 | 64.0503 | -0.10529 | -59.3674 | 64.0503 | -59.1614 | -59.2163 | -59.0927 | -0.086975 | -59.4223 | 64.0732 | 63.945 | -59.1751 | -59.2758 | -0.068665 | -0.1236 | 0.041199 | 123.143 | -0.27466 | -0.15106 | -0.004577 | -0.082398 | -0.18311 | 0.064087 | 0 | -0.32959 | -0.14648 | -0.064087 | 123.143 | 123.0972 | 58.9874 | -123.2254 | 123.1659 | 123.0377 | 59.0057 | -123.2849
122.6875 | 123.3948 | -59.0469 | 63.9908 | -0.31669 | 0.007644 | 0.080644 | 0.073942 | 0.12385 | -0.016535 | 0.001822 | -0.34124 | -0.0010052 | 0.051317 | 0.056103 | -0.0056342 | -0.0071624 | 64.0869 | 64.2517 | 0.09613 | -59.2346 | 63.9954 | -59.0744 | -59.1476 | -58.9783 | 0.19226 | -59.2438 | 64.0366 | 63.9313 | -59.1064 | -59.2163 | -0.027466 | -0.10071 | 0.004577 | 123.2986 | -0.18768 | -0.086975 | 0.09613 | -0.059509 | -0.16937 | 0.045776 | 0.068665 | -0.19684 | -0.027465 | -0.05951 | 123.0423 | 123.1338 | 59.1431 | -123.1384 | 123.0835 | 122.9782 | 59.2392 | -123.2071
123.6875 | 123.3582 | -59.0698 | 64.032 | -0.46927 | 0.002304 | 0.067827 | 0.067533 | 0.13881 | -0.0026496 | 0.013571 | -0.43279 | -0.0063462 | 0.070543 | 0.053967 | -0.0024292 | -0.00075443 | 64.0686 | 64.238 | 0.073242 | -59.2529 | 64.0274 | -59.0973 | -59.1202 | -59.0103 | 0.16022 | -59.3033 | 64.0823 | 63.9404 | -59.1339 | -59.2209 | -0.027466 | -0.050354 | -0.004577 | 123.3078 | -0.18311 | -0.13275 | 0.036622 | -0.064087 | -0.15106 | 0.050354 | 0.059509 | -0.23346 | -0.082398 | -0.091552 | 123.0972 | 123.1384 | 59.1431 | -123.1522 | 123.1522 | 123.0103 | 59.23 | -123.2529
124.6875 | 123.3673 | -59.0652 | 64.0182 | -0.36246 | -0.001969 | 0.061418 | 0.073942 | 0.14628 | -0.0090576 | 0.006095 | -0.58538 | -0.0074142 | 0.056658 | 0.057171 | 0.0018428 | 0.00031457 | 64.0686 | 64.2242 | 0.10071 | -59.23 | 64.0274 | -59.0881 | -59.1293 | -58.992 | 0.17853 | -59.285 | 64.064 | 63.9404 | -59.1293 | -59.2438 | -0.022888 | -0.064086 | 0.009155 | 123.2895 | -0.16479 | -0.10071 | 0.050354 | -0.064086 | -0.17853 | 0.045776 | 0.073243 | -0.21973 | -0.041199 | -0.07782 | 123.0927 | 123.1339 | 59.166 | -123.1476 | 123.1293 | 123.0057 | 59.2438 | -123.262
125.6875 | 123.3444 | -59.0698 | 64.0045 | -0.39298 | 0.033279 | 0.064622 | 0.072874 | 0.11851 | -0.0069216 | 0.00289 | -0.41753 | -0.0042092 | 0.047044 | 0.053967 | 0.0018428 | 0.0013826 | 64.0869 | 64.238 | 0.10529 | -59.2209 | 64.032 | -59.0836 | -59.1339 | -58.992 | 0.1831 | -59.2712 | 64.0182 | 63.9221 | -59.1293 | -59.2163 | -0.013733 | -0.064087 | 0.027465 | 123.3078 | -0.15106 | -0.086975 | 0.082397 | -0.059509 | -0.14649 | 0.013733 | 0.07782 | -0.20142 | -0.054931 | -0.082398 | 123.1018 | 123.1567 | 59.1751 | -123.1384 | 123.0881 | 122.9919 | 59.2529 | -123.2208
126.6875 | 123.4039 | -59.0332 | 63.9908 | 0.65988 | -0.006241 | 0.076372 | 0.073942 | 0.14094 | -0.0058536 | -0.009927 | -0.32598 | -0.0074142 | 0.064134 | 0.065716 | -0.0099062 | -0.0060944 | 64.0778 | 64.2563 | 0.09613 | -59.2346 | 64.0228 | -59.0881 | -59.1339 | -58.9554 | 0.17395 | -59.2575 | 64.0503 | 63.9267 | -59.1248 | -59.2026 | -0.054932 | -0.10071 | 0.032043 | 123.2895 | -0.20142 | -0.10071 | 0.086975 | -0.091553 | -0.16937 | 0.059509 | 0.07782 | -0.2243 | -0.054931 | -0.064087 | 123.056 | 123.111 | 59.1293 | -123.1247 | 123.0835 | 122.9599 | 59.2072 | -123.1934
127.6875 | 123.3902 | -59.0469 | 63.9816 | -0.072545 | -0.007309 | 0.073167 | 0.07501 | 0.14308 | -0.010127 | 0.003958 | -0.097097 | 0.0043348 | 0.064134 | 0.060376 | 0.0018428 | -0.00075443 | 64.0869 | 64.2197 | 0.059509 | -59.2438 | 64.0228 | -59.0927 | -59.1339 | -58.9645 | 0.20142 | -59.2072 | 64.0503 | 63.9267 | -59.1248 | -59.198 | -0.045776 | -0.086975 | 0.041199 | 123.2666 | -0.19684 | -0.10986 | 0.10529 | -0.07782 | -0.15106 | 0.068665 | 0.082397 | -0.16022 | -0.009155 | -0.054931 | 123.0698 | 123.1338 | 59.1064 | -123.1155 | 123.0972 | 122.9736 | 59.2484 | -123.1796
128.6875 | 123.3673 | -59.0973 | 63.9725 | -0.13358 | -0.01799 | 0.071031 | 0.076078 | 0.14735 | -0.015467 | -0.009927 | -0.23443 | -0.012754 | 0.063066 | 0.06358 | -0.0002932 | -0.0050264 | 64.0732 | 64.1968 | 0.032043 | -59.2621 | 64.0091 | -59.1019 | -59.1385 | -58.9737 | 0.12817 | -59.2529 | 64.0366 | 63.9267 | -59.1156 | -59.2346 | -0.004578 | -0.041199 | 0.036621 | 123.2941 | -0.16479 | -0.1236 | 0.10071 | -0.018311 | -0.13733 | 0.064087 | 0.1236 | -0.15564 | -0.018311 | -0.045776 | 123.1064 | 123.1705 | 59.1293 | -123.111 | 123.1338 | 123.024 | 59.2255 | -123.2071
129.6875 | 123.381 | -59.0424 | 63.9633 | -0.28617 | -0.016922 | 0.081712 | 0.076078 | 0.1324 | -0.016535 | -0.016336 | -0.2802 | -0.0052782 | 0.055589 | 0.069989 | -0.031268 | 0.0024506 | 64.1144 | 64.2746 | 0.09613 | -59.2117 | 64.032 | -59.0927 | -59.1064 | -58.7311 | -0.15564 | -59.3491 | 64.0594 | 63.9313 | -59.1202 | -59.2117 | -0.050354 | -0.064087 | 0.068664 | 123.317 | -0.16937 | -0.10529 | 0.15106 | -0.07782 | -0.16937 | 0.09613 | 0.31128 | -0.3067 | -0.13733 | -0.032044 | 123.0743 | 123.1567 | 59.1385 | -123.0698 | 123.1018 | 122.9736 | 58.8867 | -123.175
130.6875 | 123.3719 | -59.0286 | 64.0045 | 0.50729 | -0.007309 | 0.064622 | 0.078214 | 0.13881 | 0.0048274 | -0.003518 | -0.34124 | -0.020231 | 0.066271 | 0.04649 | -0.0034972 | -0.0039584 | 64.0869 | 64.2517 | 0.091553 | -59.2484 | 64.0091 | -59.1156 | -59.1385 | -58.9554 | 0.20599 | -59.2529 | 64.0366 | 63.945 | -59.1248 | -59.2117 | -0.086976 | -0.10986 | 0.004577 | 123.2803 | -0.21973 | -0.10986 | 0.082397 | -0.096131 | -0.18311 | 0.032043 | 0.073242 | -0.22431 | -0.041199 | -0.05951 | 123.0377 | 123.1155 | 59.1202 | -123.143 | 123.0652 | 122.9736 | 59.2346 | -123.2162
131.6875 | 123.4131 | -59.0424 | 63.9954 | -6.2676 | -0.005173 | 0.06569 | 0.054716 | 0.1356 | 0.0058954 | -0.013132 | -0.46331 | -0.0031412 | 0.061998 | 0.056103 | 0.0007748 | -0.0092984 | 64.1235 | 64.183 | 0.068665 | -59.2621 | 64.0137 | -59.1248 | -59.1568 | -58.9554 | 0.17853 | -59.2529 | 64.0411 | 63.9359 | -59.1385 | -59.2163 | -0.082398 | -0.11444 | 0.018311 | 123.2254 | -0.21973 | -0.10529 | 0.12817 | -0.096131 | -0.17395 | 0.045777 | 0.086975 | -0.21057 | -0.036621 | -0.059509 | 123.056 | 123.1659 | 59.111 | -123.1522 | 123.0835 | 122.9782 | 59.2209 | -123.2117
132.6875 | 123.3765 | -59.0424 | 64.0091 | -0.66764 | -0.01799 | 0.072099 | 0.070738 | 0.13667 | 0.0026914 | -0.007791 | 0.57429 | -0.0063462 | 0.049181 | 0.075329 | 0.0018428 | -0.0082304 | 64.1373 | 63.9862 | 0.23346 | -58.9554 | 64.0915 | -59.0561 | -59.1202 | -58.9554 | 0.16479 | -59.2438 | 64.0274 | 63.9175 | -59.1385 | -59.2072 | -0.013733 | -0.07782 | 0.082398 | 123.0286 | 0.086975 | 0.1648 | 0.12817 | -0.096131 | -0.16479 | 0.018311 | 0.086975 | -0.20142 | -0.036621 | -0.091552 | 123.1338 | 123.1796 | 59.2758 | -123.1293 | 123.0698 | 122.9599 | 59.2072 | -123.2162
133.6875 | 123.4085 | -59.0698 | 63.9862 | -0.14884 | -0.007309 | 0.073167 | 0.061125 | 0.13026 | -0.0047856 | -0.007791 | -0.34124 | -0.0074142 | 0.053453 | 0.076397 | 0.0082518 | 0.0013826 | 64.0823 | 64.2792 | 0.10529 | -59.2255 | 64.032 | -59.0973 | -59.1156 | -59.0103 | 0.1236 | -59.2621 | 64.0274 | 63.9084 | -59.1431 | -59.23 | -0.027466 | -0.045777 | 0.045776 | 123.349 | -0.15564 | -0.10986 | 0.09613 | -0.073242 | -0.16022 | 0.041199 | 0.059509 | -0.19226 | -0.032043 | -0.07782 | 123.1018 | 123.1522 | 59.1751 | -123.1018 | 123.0972 | 122.9782 | 59.1934 | -123.2162
134.6875 | 123.3856 | -59.0973 | 63.9954 | -0.13358 | -0.009445 | 0.071031 | 0.063261 | 0.13453 | -0.0069216 | -0.006723 | -0.26494 | -0.011686 | 0.07802 | 0.060376 | 0.0007748 | -0.00075443 | 64.032 | 64.1693 | 0.009155 | -59.2804 | 64.0228 | -59.1202 | -59.1476 | -58.992 | 0.082397 | -59.2896 | 64.0366 | 63.9175 | -59.1339 | -59.2255 | -0.022888 | -0.050354 | 0.027466 | 123.2666 | -0.18311 | -0.13275 | 0.036621 | -0.036621 | -0.12817 | 0.041199 | 0.10529 | -0.19226 | -0.064087 | -0.077819 | 123.1201 | 123.1293 | 59.1064 | -123.143 | 123.1338 | 123.0148 | 59.1797 | -123.2208
135.6875 | 123.3627 | -59.0881 | 63.9725 | 0.034266 | 0.006576 | 0.076372 | 0.078214 | 0.13133 | 0.0016234 | -0.001382 | -0.097097 | -0.0084822 | 0.055589 | 0.055035 | -0.0013612 | -0.0039584 | 64.032 | 64.1556 | -0.004578 | -59.285 | 64.0274 | -59.1202 | -59.1431 | -58.9966 | 0.10071 | -59.2941 | 64.0274 | 63.913 | -59.1476 | -59.2346 | -0.032043 | -0.054931 | 0.054932 | 123.2437 | -0.19684 | -0.14191 | 0.059509 | -0.059509 | -0.14648 | 0.054932 | 0.091553 | -0.20599 | -0.059509 | -0.059509 | 123.1155 | 123.1201 | 59.0836 | -123.1155 | 123.1155 | 123.0011 | 59.1888 | -123.2071
136.6875 | 123.3902 | -59.0515 | 63.9725 | -0.11832 | -0.005173 | 0.053941 | 0.077146 | 0.1324 | -0.0079896 | 0.003958 | -0.18865 | -0.0042092 | 0.041704 | 0.066784 | 0.0071838 | -0.0018224 | 64.0869 | 64.1968 | 0.050354 | -59.2758 | 64.0274 | -59.1019 | -59.1431 | -58.9554 | 0.13733 | -59.2758 | 64.0549 | 63.913 | -59.1385 | -59.2117 | -0.050354 | -0.091552 | 0.054932 | 123.2483 | -0.2243 | -0.13275 | 0.11444 | -0.086975 | -0.16022 | 0.082398 | 0.096131 | -0.2243 | -0.064087 | -0.059509 | 123.0789 | 123.1384 | 59.1019 | -123.1155 | 123.1064 | 122.9645 | 59.1888 | -123.1842
137.6875 | 123.3719 | -59.0286 | 63.9816 | -0.71341 | -0.003037 | 0.076372 | 0.078214 | 0.13133 | 0.0037594 | -0.006723 | -0.32598 | 0.0043348 | 0.061998 | 0.06358 | -0.0013612 | -0.0082304 | 64.5401 | 63.9633 | -0.041199 | -59.2667 | 63.9999 | -59.0927 | -59.1385 | -58.9508 | 0.17853 | -59.2529 | 64.0503 | 63.9267 | -59.1293 | -59.2117 | -0.064087 | -0.10986 | 0.018311 | 122.9919 | -0.23804 | -0.12817 | 0.55847 | -0.10071 | -0.18311 | 0.068665 | 0.077819 | -0.22431 | -0.041199 | -0.054931 | 123.0286 | 123.5687 | 58.9874 | -123.1201 | 123.0789 | 122.9553 | 59.2072 | -123.1934
138.6875 | 123.3627 | -59.0698 | 64.0137 | -0.11832 | -0.00090105 | 0.073167 | 0.076078 | 0.13987 | -0.0058536 | -0.00245 | -0.14287 | 0.0054038 | 0.063066 | 0.065716 | 0.0018428 | -0.0050264 | 64.1281 | 64.2838 | 0.10071 | -59.23 | 64.032 | -59.0836 | -59.1202 | -58.9737 | 0.14648 | -59.2575 | 64.0137 | 63.9175 | -59.1339 | -59.2117 | -0.013733 | -0.050354 | 0.01831 | 123.3536 | -0.16022 | -0.10986 | 0.11444 | -0.064087 | -0.14191 | 0 | 0.09613 | -0.18768 | -0.045776 | -0.09613 | 123.1018 | 123.1979 | 59.1705 | -123.1338 | 123.0835 | 122.9874 | 59.2163 | -123.2254
139.6875 | 123.3856 | -59.0881 | 63.9908 | -0.17936 | 0.010849 | 0.079576 | 0.062193 | 0.13133 | 0.0069634 | 0.005026 | -0.24969 | -0.010618 | 0.054521 | 0.064648 | -0.0002932 | -0.0050264 | 64.1052 | 64.2197 | 0.064087 | -59.2529 | 64.0091 | -59.0973 | -59.1522 | -58.6487 | 0.009155 | -59.3628 | 64.0686 | 63.9175 | -59.1476 | -59.2346 | -0.009155 | -0.064087 | 0.01831 | 123.3078 | -0.16479 | -0.10071 | 0.11444 | -0.059509 | -0.14648 | 0.07782 | 0.43945 | -0.27466 | -0.12817 | -0.073242 | 123.0972 | 123.1934 | 59.1522 | -123.143 | 123.1567 | 123.0057 | 59.0973 | -123.2254
140.6875 | 123.5825 | -58.992 | 64.0457 | -0.19462 | -0.001969 | 0.072099 | 0.062193 | 0.12278 | -0.0079896 | -0.00031405 | -0.081838 | -0.0074142 | 0.063066 | 0.062512 | -0.01311 | 0.0013826 | 64.0823 | 64.2471 | 0.059509 | -59.2392 | 64.0045 | -59.079 | -59.1476 | -58.9371 | 0.20142 | -59.2209 | 64.0274 | 63.913 | -59.1385 | -59.2026 | -0.086975 | -0.15564 | -0.041198 | 123.2391 | -0.24719 | -0.091553 | 0.036621 | -0.14648 | -0.21057 | -0.01831 | 0.054931 | -0.22888 | -0.01831 | -0.13275 | 122.9965 | 123.0743 | 59.0515 | -123.1934 | 123.0194 | 122.905 | 59.1934 | -123.2483
141.6875 | 123.3536 | -59.0836 | 63.9633 | 0.034266 | -0.005173 | 0.075304 | 0.070738 | 0.1324 | 0.0026914 | -0.012063 | -0.097097 | -0.0042092 | 0.056658 | 0.04649 | -0.0067022 | -0.0018224 | 64.0137 | 64.151 | -0.009155 | -59.285 | 64.0091 | -59.1385 | -59.1476 | -58.9966 | 0.07782 | -59.3079 | 64.032 | 63.9084 | -59.1568 | -59.2255 | -0.054932 | -0.064087 | 0.045776 | 123.2346 | -0.20142 | -0.13733 | 0.050354 | -0.073242 | -0.14191 | 0.068664 | 0.086975 | -0.2243 | -0.082397 | -0.054932 | 123.0927 | 123.0972 | 59.0744 | -123.111 | 123.1155 | 122.9919 | 59.1614 | -123.1888
142.6875 | 123.317 | -59.0698 | 63.9679 | -0.026769 | -0.010514 | 0.068895 | 0.065397 | 0.13453 | -0.0079896 | -0.003518 | -0.097097 | -0.0052782 | 0.061998 | 0.052899 | -0.0067022 | -0.0060944 | 64.0182 | 64.1327 | -0.036621 | -59.2896 | 64.0274 | -59.1293 | -59.1568 | -59.0057 | 0.064087 | -59.3033 | 64.0366 | 63.9359 | -59.1431 | -59.2255 | -0.059509 | -0.086975 | 0.059509 | 123.2025 | -0.21973 | -0.13275 | 0.050354 | -0.073242 | -0.15564 | 0.068664 | 0.064087 | -0.23346 | -0.07782 | -0.032044 | 123.0972 | 123.0881 | 59.0332 | -123.1247 | 123.1064 | 123.0057 | 59.1339 | -123.1934
143.6875 | 123.3765 | -59.0561 | 63.9954 | 0.019007 | -0.001969 | 0.07744 | 0.065397 | 0.1356 | -0.0015816 | -0.010995 | -1.2262 | 0.0064718 | 0.059862 | 0.056103 | 0.0082518 | -0.013571 | 64.1418 | 64.2517 | 0.082397 | -59.23 | 64.0045 | -59.0881 | -59.1293 | -58.9737 | 0.19226 | -59.3033 | 64.0091 | 63.8809 | -59.1431 | -59.2072 | -0.032044 | -0.073242 | 0.009156 | 123.3078 | -0.17395 | -0.10071 | 0.14648 | -0.086975 | -0.15106 | 0.013733 | 0.082397 | -0.24719 | -0.096131 | -0.11444 | 123.0606 | 123.1979 | 59.1385 | -123.1247 | 123.0652 | 122.937 | 59.2484 | -123.2025
144.6875 | 123.349 | -59.0607 | 63.9771 | -0.13358 | -0.005173 | 0.071031 | 0.063261 | 0.13346 | 0.0091004 | 0.003958 | -0.47857 | 0.0043348 | 0.048113 | 0.053967 | -0.034473 | -0.0092984 | 64.0869 | 64.2334 | 0.091553 | -59.23 | 64.0182 | -59.0881 | -59.1385 | -58.8821 | -0.1236 | -59.2758 | 64.0091 | 63.8947 | -59.1385 | -59.2163 | -0.027466 | -0.07782 | 0.041199 | 123.2941 | -0.16937 | -0.091553 | 0.10986 | -0.07782 | -0.15564 | 0.032043 | 0.17853 | -0.21515 | -0.059509 | -0.082398 | 123.0789 | 123.1476 | 59.1522 | -123.1155 | 123.0698 | 122.9553 | 58.9371 | -123.1934
145.6875 | 123.2483 | -59.0149 | 63.9587 | -0.25565 | -0.005173 | 0.066759 | 0.07501 | 0.12919 | 0.0058954 | -0.008859 | -0.40227 | -0.0084822 | 0.056658 | 0.059307 | 0.0039788 | 0.00031457 | 64.1052 | 64.238 | 0.073242 | -59.2575 | 64.0274 | -59.111 | -59.1431 | -58.9325 | 0.21515 | -59.2209 | 64.0411 | 63.8992 | -59.1339 | -59.1751 | -0.09613 | -0.12817 | 0.068665 | 123.2529 | -0.24261 | -0.11444 | 0.14649 | -0.11902 | -0.16022 | 0.082398 | 0.082398 | -0.20599 | -0.045776 | -0.059509 | 123.0423 | 123.1201 | 59.0881 | -123.1018 | 123.056 | 122.9141 | 59.23 | -123.1338
146.6875 | 123.3856 | -59.0469 | 63.9862 | -0.24039 | -0.007309 | 0.080644 | 0.065397 | 0.13453 | -0.0015816 | -0.004587 | -0.11236 | -0.0095502 | 0.055589 | 0.050762 | -0.0045652 | -0.013571 | 64.0686 | 64.2242 | 0.068665 | -59.2438 | 64.0274 | -59.1019 | -59.1476 | -58.9279 | 0.19684 | -59.23 | 64.0457 | 63.8992 | -59.1293 | -59.2026 | -0.054932 | -0.10071 | 0.041199 | 123.2712 | -0.19684 | -0.09613 | 0.082398 | -0.082397 | -0.15564 | 0.059509 | 0.11902 | -0.18311 | -0.027466 | -0.086975 | 123.0743 | 123.1155 | 59.1156 | -123.1338 | 123.0927 | 122.9462 | 59.2438 | -123.1888
147.6875 | 123.3765 | -59.0424 | 63.9862 | -0.1641 | -0.019058 | 0.076372 | 0.073942 | 0.12599 | -0.00051261 | -0.00245 | -0.21917 | -0.018095 | 0.051317 | 0.06358 | -0.0013612 | -0.0050264 | 64.0961 | 64.2151 | 0.054932 | -59.2712 | 64.0366 | -59.1019 | -59.1339 | -58.9417 | 0.14648 | -59.2667 | 64.032 | 63.8992 | -59.1431 | -59.2163 | -0.05951 | -0.091553 | 0.050354 | 123.2574 | -0.22888 | -0.13733 | 0.10986 | -0.10071 | -0.17395 | 0.045776 | 0.10071 | -0.22431 | -0.050354 | -0.086975 | 123.0789 | 123.1384 | 59.0973 | -123.1201 | 123.0743 | 122.9416 | 59.1888 | -123.2025
148.6875 | 123.3444 | -59.0424 | 63.9862 | -0.11832 | -0.015854 | 0.075304 | 0.068601 | 0.12812 | 0.0048274 | -0.004587 | -0.21917 | -0.0042092 | 0.057726 | 0.053967 | 0.0029108 | -0.0082304 | 64.0778 | 64.2059 | 0.041199 | -59.2529 | 64.0274 | -59.1019 | -59.1293 | -58.9508 | 0.16937 | -59.2758 | 64.032 | 63.913 | -59.1568 | -59.198 | -0.05951 | -0.086975 | 0.041199 | 123.2483 | -0.21057 | -0.1236 | 0.091553 | -0.11444 | -0.15564 | 0.045776 | 0.091552 | -0.23346 | -0.07782 | -0.073242 | 123.0698 | 123.1201 | 59.0836 | -123.1155 | 123.0743 | 122.9553 | 59.2117 | -123.1842
149.6875 | 123.3398 | -59.079 | 63.9816 | 0.14108 | -0.004105 | 0.066759 | 0.07501 | 0.13881 | -0.0026496 | -0.003518 | -0.036062 | -0.0063462 | 0.050249 | 0.051831 | -0.0056342 | 0.00031457 | 64.0228 | 64.1464 | -0.027466 | -59.2896 | 64.0228 | -59.1202 | -59.166 | -58.9966 | 0.059509 | -59.3079 | 64.032 | 63.8992 | -59.1431 | -59.2255 | -0.041199 | -0.086976 | 0.041199 | 123.2254 | -0.21057 | -0.1236 | 0.041199 | -0.064087 | -0.14649 | 0.050354 | 0.082397 | -0.22888 | -0.082397 | -0.082397 | 123.1018 | 123.1018 | 59.0515 | -123.1476 | 123.111 | 122.9782 | 59.1385 | -123.2071
150.6875 | 123.3673 | -59.0424 | 63.9633 | -0.057287 | 0.005508 | 0.081712 | 0.072874 | 0.12492 | 0.0037594 | 0.003958 | -0.20391 | -0.0010052 | 0.056658 | 0.048626 | 0.0029108 | -0.0060944 | 64.064 | 64.2059 | 0.027466 | -59.2575 | 64.0182 | -59.0973 | -59.166 | -58.9828 | 0.13275 | -59.2529 | 64.0274 | 63.913 | -59.1339 | -59.2209 | -0.054932 | -0.1236 | 0.054932 | 123.2483 | -0.21515 | -0.091552 | 0.10071 | -0.091553 | -0.17853 | 0.064087 | 0.059509 | -0.21057 | -0.032044 | -0.050354 | 123.0606 | 123.1064 | 59.0698 | -123.1293 | 123.0698 | 122.9553 | 59.1751 | -123.1842
151.6875 | 123.3948 | -59.0698 | 63.9771 | 0.019007 | -0.003037 | 0.072099 | 0.055784 | 0.14949 | 0.0069634 | 0.00289 | -0.32598 | -0.0063462 | 0.056658 | 0.052899 | 0.0071838 | -0.027456 | 64.0869 | 64.2654 | 0.11444 | -59.2209 | 64.032 | -59.079 | -59.1248 | -58.8547 | 0.54016 | -59.4498 | 64.0594 | 63.9221 | -59.1248 | -59.2163 | -0.009155 | -0.054932 | 0.054931 | 123.3353 | -0.15106 | -0.09613 | 0.10986 | -0.054932 | -0.14649 | 0.082397 | 0.21515 | -0.37994 | -0.23346 | -0.054932 | 123.1018 | 123.1567 | 59.1843 | -123.1018 | 123.1293 | 122.9919 | 59.61 | -123.1934
152.6875 | 123.317 | -59.0195 | 63.9862 | -0.14884 | -0.011582 | 0.084917 | 0.065397 | 0.14094 | -0.00051261 | 0.006095 | -0.44805 | 6.2833e-05 | 0.04384 | 0.052899 | -0.0002932 | -0.0071624 | 64.0686 | 64.2654 | 0.07782 | -59.2117 | 64.0182 | -59.0881 | -59.1385 | -58.9142 | 0.19226 | -59.2072 | 64.0457 | 63.8992 | -59.1293 | -59.2117 | -0.068665 | -0.11902 | 0.032044 | 123.2849 | -0.19226 | -0.073242 | 0.082398 | -0.10986 | -0.19226 | 0.059509 | 0.10528 | -0.18768 | 0.004578 | -0.086975 | 123.0377 | 123.0881 | 59.0973 | -123.1247 | 123.0652 | 122.9187 | 59.2117 | -123.1979
153.6875 | 123.4039 | -59.0561 | 63.9816 | -0.11832 | 0.00444 | 0.069963 | 0.064329 | 0.11744 | -0.013331 | 0.00075395 | -0.49383 | -0.0031412 | 0.057726 | 0.064648 | -0.0024292 | -0.0039584 | 64.0915 | 64.238 | 0.068665 | -59.2529 | 64.0366 | -59.1156 | -59.1339 | -58.9279 | 0.20599 | -59.23 | 64.0274 | 63.8901 | -59.1293 | -59.2072 | -0.05951 | -0.07782 | 0.054932 | 123.2941 | -0.19684 | -0.11902 | 0.10986 | -0.073242 | -0.15106 | 0.045777 | 0.12817 | -0.17395 | -0.022889 | -0.091552 | 123.0927 | 123.1476 | 59.1248 | -123.1155 | 123.0835 | 122.9462 | 59.2621 | -123.1888
154.6875 | 123.4085 | -59.0286 | 63.9771 | -0.19462 | -0.001969 | 0.072099 | 0.068601 | 0.1356 | -0.0069216 | -0.004587 | 0.040232 | -0.0010052 | 0.050249 | 0.055035 | 0.0093198 | -0.015707 | 64.0823 | 64.2288 | 0.073242 | -59.2438 | 64.0137 | -59.0836 | -59.1248 | -58.905 | 0.17853 | -59.2163 | 64.0274 | 63.8901 | -59.1202 | -59.2255 | -0.054932 | -0.096131 | 0.036621 | 123.2574 | -0.21515 | -0.11902 | 0.10528 | -0.091553 | -0.19684 | 0.050354 | 0.1236 | -0.18768 | 0.009155 | -0.086975 | 123.0423 | 123.111 | 59.1019 | -123.1018 | 123.056 | 122.9187 | 59.2072 | -123.2025
155.6875 | 123.3444 | -59.0378 | 63.9816 | -0.01151 | -0.022263 | 0.072099 | 0.089964 | 0.12919 | -0.0058536 | -0.00245 | -0.23443 | 0.0043348 | 0.054521 | 0.059307 | -0.010974 | 0.0067226 | 64.032 | 64.1693 | 0.009155 | -59.2896 | 64.0045 | -59.1248 | -59.1476 | -58.9691 | 0.091553 | -59.2804 | 64.0274 | 63.8992 | -59.1248 | -59.2346 | -0.086975 | -0.10986 | 0.022889 | 123.2071 | -0.25177 | -0.14191 | 0.050354 | -0.086975 | -0.19684 | 0.045777 | 0.068665 | -0.24262 | -0.045777 | -0.082397 | 123.0423 | 123.0698 | 59.0469 | -123.1293 | 123.0652 | 122.937 | 59.1293 | -123.2162
156.6875 | 123.3719 | -59.0515 | 63.9908 | -0.026769 | 0.006576 | 0.053941 | 0.070738 | 0.13667 | 0.00055539 | -0.004587 | -0.17339 | -0.012754 | 0.064134 | 0.06358 | -0.012042 | -0.011435 | 64.064 | 64.2334 | 0.068665 | -59.2484 | 64.0137 | -59.1064 | -59.166 | -58.9462 | 0.12817 | -59.2621 | 64.0457 | 63.9221 | -59.1522 | -59.2346 | -0.054931 | -0.11444 | 0.022888 | 123.2849 | -0.19684 | -0.082397 | 0.073242 | -0.10071 | -0.18311 | 0.054931 | 0.10529 | -0.21057 | -0.027466 | -0.068665 | 123.0652 | 123.1155 | 59.1202 | -123.1567 | 123.0972 | 122.9736 | 59.1797 | -123.2254
157.6875 | 123.3719 | -59.079 | 63.9633 | -0.17936 | 0.010849 | 0.078508 | 0.068601 | 0.12706 | 0.0037594 | 0.001822 | -1.0126 | -0.0084822 | 0.044908 | 0.055035 | -0.0056342 | -0.00075443 | 64.1098 | 64.27 | 0.10529 | -59.2667 | 64.0091 | -59.0973 | -59.1019 | -58.9783 | 0.19684 | -59.2346 | 64.0182 | 63.9084 | -59.1385 | -59.1934 | -0.018311 | -0.022889 | 0.045776 | 123.349 | -0.18768 | -0.16479 | 0.14648 | -0.05951 | -0.11444 | 0.054932 | 0.10071 | -0.15564 | -0.041199 | -0.054932 | 123.0881 | 123.1888 | 59.1843 | -123.0652 | 123.0972 | 122.9874 | 59.2758 | -123.1567
158.6875 | 123.4222 | -59.0607 | 63.9954 | -0.82023 | -0.009445 | 0.076372 | 0.067533 | 0.12706 | -0.0069216 | -0.00245 | -0.31072 | -0.0095502 | 0.057726 | 0.064648 | 0.0093198 | -0.0092984 | 64.1281 | 64.2746 | 0.10071 | -59.2209 | 64.0228 | -59.0836 | -59.0973 | -58.905 | 0.12817 | -59.2346 | 64.0411 | 63.8992 | -59.1431 | -59.2255 | -0.022888 | -0.036621 | 0.027466 | 123.3353 | -0.16022 | -0.1236 | 0.13275 | -0.082397 | -0.1648 | 0.045777 | 0.15564 | -0.17395 | -0.009155 | -0.09613 | 123.0835 | 123.1888 | 59.1614 | -123.0927 | 123.1018 | 122.9599 | 59.1888 | -123.2208
159.6875 | 123.3856 | -59.0881 | 63.9771 | -0.19462 | -0.011582 | 0.071031 | 0.076078 | 0.14842 | 0.0016234 | 0.009299 | -0.29546 | 0.0011308 | 0.052385 | 0.066784 | 0.0050478 | -0.0071624 | 64.1006 | 64.2792 | 0.10071 | -59.2072 | 64.0137 | -59.1064 | -59.111 | -58.8135 | 0.4715 | -59.4543 | 64.0732 | 63.913 | -59.1248 | -59.2117 | -0.01831 | -0.022888 | 0.036621 | 123.3673 | -0.11902 | -0.09613 | 0.1236 | -0.036621 | -0.1236 | 0.09613 | 0.27466 | -0.36621 | -0.24262 | -0.064087 | 123.1018 | 123.1888 | 59.1888 | -123.0881 | 123.1613 | 123.0011 | 59.5596 | -123.1888
160.6875 | 123.2895 | -59.0469 | 63.9725 | -0.24039 | -0.01265 | 0.084917 | 0.07501 | 0.12599 | -0.0069216 | -0.00031405 | -0.57012 | -0.0063462 | 0.066271 | 0.053967 | 0.0007748 | -0.014639 | 64.064 | 64.2792 | 0.091553 | -59.2163 | 64.0228 | -59.0836 | -59.111 | -58.9142 | 0.19226 | -59.2209 | 64.032 | 63.9359 | -59.1248 | -59.198 | -0.036621 | -0.064087 | 0.050354 | 123.3261 | -0.16937 | -0.10529 | 0.091553 | -0.07782 | -0.15106 | 0.059509 | 0.13275 | -0.17395 | -0.022888 | -0.036621 | 123.0698 | 123.111 | 59.1385 | -123.0835 | 123.0789 | 122.9828 | 59.2392 | -123.1705
161.6875 | 123.3582 | -59.0698 | 63.9725 | -0.057287 | -0.013718 | 0.06569 | 0.073942 | 0.13987 | -0.0026496 | -0.004587 | -0.11236 | -0.0042092 | 0.06093 | 0.072125 | -0.0067022 | 0.0045866 | 64.0274 | 64.1922 | 0.004578 | -59.285 | 64.0137 | -59.1248 | -59.1476 | -58.9737 | 0.11902 | -59.2667 | 64.0411 | 63.8855 | -59.1705 | -59.2255 | -0.054932 | -0.07782 | 0.041199 | 123.262 | -0.21515 | -0.13733 | 0.054932 | -0.10071 | -0.15564 | 0.068665 | 0.09613 | -0.19684 | -0.041199 | -0.086975 | 123.0835 | 123.0972 | 59.0744 | -123.1201 | 123.111 | 122.9553 | 59.1888 | -123.1979
162.6875 | 123.3215 | -59.0744 | 63.9771 | 0.0037495 | -0.007309 | 0.072099 | 0.065397 | 0.12385 | -0.010127 | 0.00075395 | -0.066579 | -0.010618 | 0.050249 | 0.045422 | -0.0056342 | -0.0028904 | 64.0137 | 64.183 | -0.004578 | -59.2667 | 64.0274 | -59.0927 | -59.1522 | -58.992 | 0.091553 | -59.285 | 64.0457 | 63.9038 | -59.1431 | -59.23 | -0.01831 | -0.07782 | 0.050354 | 123.2574 | -0.19226 | -0.11444 | 0.036621 | -0.068664 | -0.15564 | 0.068664 | 0.082398 | -0.21057 | -0.054931 | -0.073242 | 123.1018 | 123.0881 | 59.0698 | -123.1293 | 123.1201 | 122.9782 | 59.166 | -123.2071
163.6875 | 123.3856 | -59.0607 | 63.9862 | -0.19462 | -0.010514 | 0.064622 | 0.083555 | 0.12599 | 0.0026914 | 0.00289 | -0.14287 | -0.0095502 | 0.050249 | 0.061444 | -0.010974 | -0.0050264 | 64.0823 | 64.2151 | 0.045776 | -59.2575 | 64.0274 | -59.0973 | -59.1202 | -58.9279 | 0.14648 | -59.2529 | 63.9999 | 63.913 | -59.1248 | -59.2346 | -0.036621 | -0.059509 | 0.041199 | 123.2758 | -0.19684 | -0.13733 | 0.09613 | -0.064087 | -0.17395 | 0.013733 | 0.13275 | -0.19226 | -0.018311 | -0.073242 | 123.0881 | 123.143 | 59.1064 | -123.1064 | 123.0606 | 122.9736 | 59.2072 | -123.2208
164.6875 | 123.3994 | -59.0469 | 63.9999 | -0.30143 | 0.014053 | 0.06569 | 0.064329 | 0.12919 | 0.00055539 | -0.006723 | -1.7603 | -0.012754 | 0.061998 | 0.048626 | 0.011456 | -0.0050264 | 64.119 | 64.2883 | 0.09613 | -59.1843 | 64.032 | -59.0881 | -59.0836 | -58.9645 | 0.18768 | -59.2346 | 64.0411 | 63.8855 | -59.1522 | -59.2072 | -0.041199 | -0.036621 | 0.032043 | 123.3353 | -0.13733 | -0.10071 | 0.11902 | -0.10529 | -0.16022 | 0.041199 | 0.082397 | -0.18768 | -0.027466 | -0.11444 | 123.0789 | 123.1659 | 59.1431 | -123.0835 | 123.0881 | 122.9324 | 59.2346 | -123.2071
165.6875 | 123.3536 | -59.0607 | 63.9816 | -0.62186 | -0.013718 | 0.072099 | 0.062193 | 0.13453 | -0.0047856 | -0.009927 | -0.41753 | -0.0084822 | 0.022478 | 0.055035 | 0.0082518 | 0.0035186 | 64.1098 | 64.2975 | 0.11902 | -59.2117 | 64.0274 | -59.0698 | -59.1293 | -59.0836 | 0.22888 | -59.2896 | 64.032 | 63.8718 | -59.1522 | -59.23 | -0.009155 | -0.068664 | 0.045777 | 123.3582 | -0.15106 | -0.082398 | 0.12817 | -0.091553 | -0.16937 | 0.050354 | -0.022888 | -0.22888 | -0.059509 | -0.10986 | 123.0881 | 123.1705 | 59.1797 | -123.111 | 123.0927 | 122.9324 | 59.2896 | -123.2117
166.6875 | 123.3627 | -59.0378 | 63.9816 | -0.11832 | -0.016922 | 0.071031 | 0.053648 | 0.12065 | 0.0048274 | 0.003958 | -0.37176 | -0.0052782 | 0.056658 | 0.056103 | 0.0029108 | -0.012503 | 64.1098 | 64.2975 | 0.10529 | -59.2072 | 63.9999 | -59.0927 | -59.1293 | -58.9188 | 0.11902 | -58.9737 | 64.1052 | 63.9587 | -59.1019 | -59.2163 | -0.054931 | -0.091552 | 0.018311 | 123.3353 | -0.16937 | -0.07782 | 0.12817 | -0.064087 | -0.17853 | 0.1236 | 0.11902 | 0.064087 | 0.24262 | -0.022888 | 123.0377 | 123.1476 | 59.1431 | -123.111 | 123.143 | 122.9965 | 59.1568 | -123.1979
167.6875 | 123.262 | -59.0286 | 64.0274 | -0.14884 | -0.008377 | 0.074235 | 0.071806 | 0.13667 | 0.0037594 | 0.003958 | -0.32598 | -0.0095502 | 0.044908 | 0.057171 | 0.012524 | -0.0050264 | 64.064 | 64.2426 | 0.073242 | -59.2346 | 63.9816 | -59.1156 | -59.1476 | -58.9096 | 0.18768 | -59.2346 | 64.0411 | 63.8855 | -59.1202 | -59.2255 | -0.086976 | -0.11902 | -0.045777 | 123.2712 | -0.20599 | -0.086975 | 0.036621 | -0.091553 | -0.19684 | 0.013733 | 0.11902 | -0.20599 | -0.009155 | -0.14191 | 123.0103 | 123.0927 | 59.1019 | -123.175 | 123.0698 | 122.9141 | 59.2163 | -123.2529
168.6875 | 123.3536 | -59.0469 | 63.9725 | 0.0037495 | -0.007309 | 0.071031 | 0.067533 | 0.12492 | -0.0037176 | 0.001822 | -0.036062 | 0.0011308 | 0.055589 | 0.060376 | -0.0099062 | 0.0024506 | 64.0366 | 64.1693 | 0 | -59.2758 | 64.0091 | -59.1064 | -59.1293 | -58.9737 | 0.10071 | -59.2804 | 64.0411 | 63.8626 | -59.1522 | -59.2255 | -0.059509 | -0.082397 | 0.036621 | 123.2162 | -0.22888 | -0.14648 | 0.064087 | -0.10529 | -0.17853 | 0.068665 | 0.073242 | -0.23346 | -0.054932 | -0.10986 | 123.056 | 123.0835 | 59.0469 | -123.1018 | 123.0881 | 122.9095 | 59.1476 | -123.1979
169.6875 | 123.3856 | -59.0698 | 63.9862 | -0.01151 | 0.002304 | 0.07744 | 0.07501 | 0.12812 | -0.00051261 | -0.00245 | -0.17339 | -0.0010052 | 0.063066 | 0.059307 | 0.0050478 | 0.00031457 | 64.0228 | 64.1693 | 0 | -59.2804 | 64.0274 | -59.111 | -59.1385 | -58.9874 | 0.091553 | -59.2712 | 64.032 | 63.8947 | -59.1293 | -59.2346 | -0.041199 | -0.068665 | 0.041199 | 123.2391 | -0.21057 | -0.14191 | 0.036621 | -0.059509 | -0.1648 | 0.045776 | 0.082397 | -0.20142 | -0.036621 | -0.091553 | 123.0972 | 123.0927 | 59.0698 | -123.1247 | 123.1018 | 122.9645 | 59.1614 | -123.2208
170.7031 | 123.3032 | -59.1202 | 64.0045 | 0.080043 | 0.06105 | 0.067827 | 0.083555 | 0.13453 | 0.03153 | -0.00245 | -0.2802 | 0.0043348 | 0.081224 | 0.069989 | 0.0071838 | -0.011435 | 64.0182 | 64.1006 | -0.059509 | -59.3124 | 64.0457 | -59.1293 | -59.2026 | -59.0836 | 0.004578 | -59.404 | 64.0778 | 63.9587 | -59.1797 | -59.2667 | -0.009155 | -0.082398 | 0.041198 | 123.2208 | -0.19226 | -0.10986 | 0.013733 | -0.059509 | -0.14648 | 0.073242 | 0.036621 | -0.28381 | -0.13733 | -0.045777 | 123.1659 | 123.1384 | 59.0607 | -123.2071 | 123.1979 | 123.0789 | 59.1248 | -123.2712
171.7031 | 123.2941 | -59.079 | 64.0045 | -0.40824 | 0.007644 | 0.081712 | 0.066465 | 0.12919 | -0.0079896 | 0.007163 | -0.47857 | -0.0084822 | 0.049181 | 0.058239 | -0.0045652 | 0.00031457 | 64.0823 | 64.2151 | 0.082397 | -59.2438 | 63.9908 | -59.1019 | -59.1431 | -58.9828 | 0.15564 | -59.2987 | 64.0549 | 63.9496 | -59.1385 | -59.2209 | -0.022889 | -0.064087 | -0.013733 | 123.2941 | -0.1648 | -0.10071 | 0.077819 | -0.05951 | -0.14191 | 0.050354 | 0.09613 | -0.21973 | -0.07782 | -0.054932 | 123.0698 | 123.1613 | 59.1614 | -123.1476 | 123.1338 | 123.0286 | 59.2346 | -123.2254
172.7031 | 123.2666 | -59.0927 | 63.9862 | -0.40824 | 0.010849 | 0.068895 | 0.07501 | 0.13453 | 0.010168 | -0.00245 | -0.55486 | 0.0054038 | 0.056658 | 0.048626 | 0.016797 | -0.0082304 | 64.0091 | 64.1052 | -0.027466 | -59.2804 | 64.0823 | -59.1202 | -59.1843 | -59.0469 | 0.073242 | -59.3582 | 64.1098 | 63.945 | -59.1797 | -59.2484 | -0.027466 | -0.091553 | 0.09613 | 123.1979 | -0.18768 | -0.096131 | 0.022888 | -0.086975 | -0.15564 | 0.1236 | 0.045776 | -0.2655 | -0.10986 | -0.041199 | 123.175 | 123.1018 | 59.0652 | -123.1705 | 123.2025 | 123.0377 | 59.166 | -123.2346
173.6875 | 123.2391 | -59.0927 | 64.064 | -0.4235 | 0.022598 | 0.06035 | 0.082487 | 0.13133 | 0.0026914 | 0.009299 | -0.020803 | 0.0021988 | 0.068407 | 0.061444 | -0.0034972 | -0.0060944 | 63.9862 | 64.2426 | 0.15564 | -59.2987 | 64.0915 | -59.111 | -59.1797 | -59.0652 | 0.064087 | -59.3536 | 64.119 | 63.9908 | -59.1705 | -59.2529 | -0.018311 | -0.086975 | 0.027466 | 123.3353 | -0.20599 | -0.11902 | -0.07782 | -0.07782 | -0.16022 | 0.054932 | 0.027465 | -0.26093 | -0.10071 | -0.073242 | 123.1842 | 123.0789 | 59.2484 | -123.2437 | 123.2117 | 123.0835 | 59.1568 | -123.317
174.6875 | 123.3673 | -59.0561 | 63.945 | -0.042028 | -0.007309 | 0.066759 | 0.063261 | 0.14094 | -0.015467 | -0.006723 | -0.24969 | -0.0063462 | 0.055589 | 0.053967 | -0.023792 | 0.0067226 | 64.0823 | 64.2426 | 0.10071 | -59.2392 | 63.9816 | -59.0744 | -59.1202 | -58.9279 | -0.10986 | -59.2392 | 64.0274 | 63.9221 | -59.1476 | -59.2026 | -0.018311 | -0.064087 | 0.036621 | 123.2986 | -0.18311 | -0.11902 | 0.13733 | -0.091553 | -0.14648 | 0.082398 | 0.12817 | -0.18311 | -0.036621 | -0.022888 | 123.0377 | 123.1384 | 59.1568 | -123.0652 | 123.0835 | 122.9782 | 58.9462 | -123.1476
175.6875 | 123.3673 | -59.0607 | 63.9816 | -0.10306 | -0.03508 | 0.066759 | 0.070738 | 0.11744 | -0.020808 | -0.001382 | 0.024973 | -0.0095502 | 0.071611 | 0.067852 | -0.0045652 | 0.0013826 | 64.0228 | 64.2014 | 0.022888 | -59.2621 | 64.0274 | -59.1019 | -59.1568 | -58.9874 | 0.1236 | -59.2621 | 64.0503 | 63.9084 | -59.1568 | -59.2209 | -0.041199 | -0.09613 | 0.045777 | 123.262 | -0.20142 | -0.10529 | 0.041199 | -0.09613 | -0.16022 | 0.068665 | 0.073242 | -0.20142 | -0.041199 | -0.073242 | 123.0881 | 123.0835 | 59.0836 | -123.1384 | 123.111 | 122.9691 | 59.1843 | -123.2025
176.6875 | 123.3673 | -59.0607 | 63.9862 | -0.087804 | -0.027603 | 0.069963 | 0.078214 | 0.12919 | -0.0015816 | -0.008859 | -0.081838 | -0.0063462 | 0.052385 | 0.058239 | -0.0077702 | 0.0035186 | 64.0182 | 64.1876 | 0.013733 | -59.2804 | 64.0228 | -59.1293 | -59.166 | -58.9828 | 0.11902 | -59.2712 | 64.064 | 63.913 | -59.1476 | -59.2209 | -0.068664 | -0.10529 | 0.036621 | 123.2483 | -0.21973 | -0.11444 | 0.032044 | -0.086975 | -0.16022 | 0.07782 | 0.07782 | -0.21057 | -0.050354 | -0.073242 | 123.0835 | 123.0789 | 59.0744 | -123.1522 | 123.1247 | 122.9736 | 59.1797 | -123.2071
177.6875 | 123.2712 | -59.0286 | 64.032 | -0.13358 | 0.00444 | 0.080644 | 0.07501 | 0.13453 | -0.0090576 | -0.006723 | -0.50908 | -0.0020732 | 0.074815 | 0.053967 | -0.0034972 | -0.00075443 | 64.0778 | 64.2288 | 0.073242 | -59.2392 | 64.0274 | -59.1019 | -59.1522 | -58.9325 | 0.21057 | -59.2255 | 64.0366 | 63.8992 | -59.1156 | -59.2117 | -0.073243 | -0.1236 | -0.004577 | 123.2574 | -0.21057 | -0.086975 | 0.045777 | -0.086976 | -0.18311 | 0.004578 | 0.09613 | -0.19684 | -0.013733 | -0.13275 | 123.056 | 123.1064 | 59.1019 | -123.1842 | 123.0652 | 122.9279 | 59.2392 | -123.2437
178.6875 | 123.3444 | -59.0469 | 63.9816 | -1.5526 | 0.018326 | 0.072099 | 0.064329 | 0.13133 | -0.0047856 | -0.013132 | -0.43279 | -0.0063462 | 0.063066 | 0.053967 | -0.0034972 | -0.013571 | 64.0869 | 64.2517 | 0.09613 | -59.2392 | 64.0137 | -59.0652 | -59.1248 | -58.9737 | 0.19226 | -59.2392 | 64.0549 | 63.8992 | -59.1431 | -59.2026 | -0.018311 | -0.07782 | 0.032044 | 123.2986 | -0.19226 | -0.11444 | 0.10529 | -0.09613 | -0.15564 | 0.073243 | 0.073242 | -0.19226 | -0.036621 | -0.082397 | 123.0606 | 123.1338 | 59.1431 | -123.1064 | 123.1018 | 122.9462 | 59.2392 | -123.1842
179.6875 | 123.3536 | -59.0424 | 63.9862 | 6.0767 | 0.001236 | 0.057146 | 0.061125 | 0.13346 | -0.0037176 | -0.008859 | -0.3565 | -0.011686 | 0.06093 | 0.072125 | 0.0050478 | -0.016775 | 64.0274 | 64.2471 | 0.086975 | -59.2346 | 64.0045 | -59.0881 | -59.1431 | -58.9462 | 0.17853 | -59.2575 | 64.0457 | 63.9267 | -59.1293 | -59.2026 | -0.045777 | -0.10071 | 0.018311 | 123.2895 | -0.19226 | -0.091553 | 0.041199 | -0.086975 | -0.16022 | 0.059509 | 0.09613 | -0.21515 | -0.054931 | -0.059509 | 123.0469 | 123.0698 | 59.1293 | -123.1293 | 123.0881 | 122.9691 | 59.2209 | -123.1888
180.6875 | 123.381 | -59.0286 | 63.9679 | -0.36246 | -0.042557 | 0.069963 | 0.068601 | 0.13133 | -0.0058536 | 0.00075395 | -0.6159 | -0.0020732 | 0.051317 | 0.052899 | 0.0007748 | -0.0050264 | 64.0823 | 64.2609 | 0.11444 | -59.2667 | 64.0091 | -59.0927 | -59.1431 | -58.9508 | 0.19684 | -59.2438 | 64.0457 | 63.9038 | -59.1385 | -59.2209 | -0.064087 | -0.11444 | 0.041198 | 123.2895 | -0.23804 | -0.1236 | 0.11444 | -0.10986 | -0.19226 | 0.077819 | 0.077819 | -0.21515 | -0.022888 | -0.064087 | 123.0377 | 123.111 | 59.1431 | -123.111 | 123.0743 | 122.9324 | 59.2255 | -123.1888
181.6875 | 123.3215 | -59.0469 | 63.9816 | -0.30143 | 0.002304 | 0.090257 | 0.063261 | 0.1324 | -0.018671 | 0.006095 | -0.55486 | -0.0042092 | 0.06093 | 0.052899 | 0.0061158 | -0.014639 | 64.0228 | 64.1235 | 0.050354 | -59.2941 | 63.9999 | -59.111 | -59.1293 | -58.9462 | 0.18768 | -59.2438 | 64.0503 | 63.8992 | -59.1202 | -59.2117 | -0.064087 | -0.082397 | 0.018311 | 123.1705 | -0.24719 | -0.16479 | 0.041199 | -0.073242 | -0.16479 | 0.068665 | 0.10071 | -0.19684 | -0.032043 | -0.082397 | 123.0469 | 123.0698 | 59.0973 | -123.111 | 123.0972 | 122.9462 | 59.2346 | -123.1934
182.6875 | 123.3994 | -59.079 | 64.0182 | 0.019007 | -0.010514 | 0.078508 | 0.068601 | 0.13881 | -0.016535 | 0.005026 | -0.17339 | -0.017027 | 0.053453 | 0.050762 | -0.0034972 | -0.0082304 | 64.0457 | 64.1922 | 0.054932 | -59.2575 | 64.032 | -59.0927 | -59.1522 | -58.96 | 0.15106 | -59.2484 | 64.0366 | 63.9038 | -59.1339 | -59.2209 | -0.013733 | -0.073243 | 0.013732 | 123.2712 | -0.17853 | -0.10528 | 0.027465 | -0.054932 | -0.14191 | 0.01831 | 0.11902 | -0.16937 | -0.027466 | -0.11444 | 123.111 | 123.1247 | 59.1339 | -123.1705 | 123.1155 | 122.9828 | 59.23 | -123.2391
183.6875 | 123.3994 | -59.0469 | 63.9633 | -0.17936 | 0.001236 | 0.062486 | 0.072874 | 0.13881 | -0.0079896 | 0.005026 | -0.15813 | -0.0084822 | 0.056658 | 0.055035 | 0.0007748 | -0.0092984 | 64.0503 | 64.2014 | 0.041199 | -59.2529 | 64.0137 | -59.079 | -59.1385 | -58.9554 | 0.14191 | -59.2392 | 64.0366 | 63.9221 | -59.1431 | -59.2346 | -0.032043 | -0.091553 | 0.050354 | 123.2483 | -0.20599 | -0.11444 | 0.086975 | -0.09613 | -0.18768 | 0.073242 | 0.091553 | -0.19226 | -0.004578 | -0.041199 | 123.0606 | 123.0972 | 59.0881 | -123.1018 | 123.0835 | 122.9691 | 59.1888 | -123.1979
184.6875 | 123.3261 | -59.0836 | 63.9908 | -0.33194 | -0.005173 | 0.072099 | 0.086759 | 0.14415 | 0.0016234 | -0.001382 | -0.38701 | -0.0063462 | 0.067339 | 0.053967 | -0.0056342 | -0.014639 | 64.0732 | 64.2242 | 0.086975 | -59.2392 | 64.0228 | -59.0881 | -59.1293 | -58.9874 | 0.1831 | -59.2575 | 64.0549 | 63.913 | -59.1339 | -59.23 | -0.004578 | -0.045776 | 0.032043 | 123.3078 | -0.15564 | -0.10986 | 0.082397 | -0.050354 | -0.14648 | 0.064087 | 0.09613 | -0.17395 | -0.027465 | -0.07782 | 123.1064 | 123.1567 | 59.1705 | -123.1201 | 123.1384 | 122.9965 | 59.2667 | -123.2208
185.6875 | 123.3307 | -59.0652 | 64.0091 | -0.40824 | 0.007644 | 0.075304 | 0.065397 | 0.13453 | -0.0037176 | -0.004587 | -0.52434 | -0.0084822 | 0.064134 | 0.053967 | 0.0018428 | -0.0050264 | 64.0869 | 64.2563 | 0.09613 | -59.2255 | 64.0137 | -59.0973 | -59.1476 | -58.9691 | 0.18768 | -59.2529 | 64.0686 | 63.9221 | -59.1202 | -59.2072 | -0.032043 | -0.082397 | 0.004578 | 123.3215 | -0.16022 | -0.07782 | 0.07782 | -0.054931 | -0.14191 | 0.05951 | 0.096131 | -0.18768 | -0.045777 | -0.086975 | 123.0789 | 123.1522 | 59.1614 | -123.1567 | 123.1339 | 122.9874 | 59.2529 | -123.2162
186.6875 | 123.3536 | -59.0424 | 63.9771 | -0.19462 | -0.022263 | 0.076372 | 0.070738 | 0.12812 | -0.00051261 | -0.00031405 | -0.41753 | -0.0084822 | 0.054521 | 0.044354 | 0.0029108 | -0.0050264 | 64.0732 | 64.2426 | 0.09613 | -59.23 | 63.9954 | -59.0881 | -59.1339 | -58.9645 | 0.19226 | -59.2621 | 64.0686 | 63.913 | -59.1248 | -59.2255 | -0.045777 | -0.091553 | 0.01831 | 123.2849 | -0.18768 | -0.096131 | 0.09613 | -0.082398 | -0.18311 | 0.091553 | 0.077819 | -0.21973 | -0.036621 | -0.064087 | 123.0377 | 123.1155 | 59.1385 | -123.111 | 123.111 | 122.9553 | 59.2346 | -123.2025
187.6875 | 123.3536 | -59.0424 | 63.9954 | -0.57608 | 0.006576 | 0.083848 | 0.073942 | 0.1324 | -0.0015816 | 0.005026 | -0.43279 | -0.0074142 | 0.055589 | 0.052899 | 0.0029108 | -0.0039584 | 64.0823 | 64.2517 | 0.10529 | -59.2346 | 64.032 | -59.0469 | -59.1385 | -58.9554 | 0.18768 | -59.2484 | 64.0411 | 63.9175 | -59.1431 | -59.2209 | -0.004578 | -0.096131 | 0.036621 | 123.2941 | -0.19226 | -0.09613 | 0.086975 | -0.10071 | -0.17853 | 0.045777 | 0.086975 | -0.20599 | -0.027466 | -0.077819 | 123.0743 | 123.1247 | 59.1476 | -123.1338 | 123.0835 | 122.9599 | 59.23 | -123.2162
188.6875 | 123.3582 | -59.0469 | 63.9771 | -1.4153 | -0.006241 | 0.064622 | 0.066465 | 0.12385 | -0.0026496 | -0.004587 | -0.32598 | -0.0084822 | 0.063066 | 0.056103 | 0.0071838 | -0.0039584 | 64.0961 | 64.2563 | 0.10986 | -59.2392 | 64.0228 | -59.0744 | -59.1293 | -58.9645 | 0.1831 | -59.2438 | 64.0411 | 63.9175 | -59.1156 | -59.2026 | -0.027466 | -0.082397 | 0.045776 | 123.3032 | -0.19226 | -0.10986 | 0.11902 | -0.068665 | -0.15564 | 0.064087 | 0.082397 | -0.19684 | -0.041198 | -0.059509 | 123.0698 | 123.143 | 59.1568 | -123.1064 | 123.0881 | 122.9645 | 59.23 | -123.1796
189.75 | 123.3307 | -59.0652 | 63.9908 | 0.75143 | 0.006576 | 0.075304 | 0.073942 | 0.13026 | -0.01974 | -0.005655 | 0.024973 | -0.0095502 | 0.059862 | 0.058239 | -0.0077702 | -0.0028904 | 64.0045 | 64.1052 | -0.041199 | -59.3216 | 64.0182 | -59.1339 | -59.1705 | -59.0149 | 0.041199 | -59.3079 | 64.0091 | 63.9175 | -59.1568 | -59.2346 | -0.068664 | -0.10529 | 0.027466 | 123.1705 | -0.25635 | -0.15106 | 0.013733 | -0.091552 | -0.16937 | 0.01831 | 0.050354 | -0.24261 | -0.073242 | -0.073242 | 123.0835 | 123.0698 | 59.024 | -123.1613 | 123.0743 | 122.9828 | 59.1064 | -123.2254
190.6875 | 123.4039 | -59.0378 | 63.9954 | -0.11832 | -0.003037 | 0.076372 | 0.067533 | 0.13346 | -0.0026496 | 0.00075395 | -0.12761 | -0.010618 | 0.068407 | 0.073193 | 0.0029108 | -0.0028904 | 64.0778 | 64.2014 | 0.050354 | -59.2575 | 64.0091 | -59.079 | -59.1156 | -58.9462 | 0.14191 | -59.2346 | 64.0274 | 63.9084 | -59.1339 | -59.2026 | -0.041198 | -0.07782 | 0.013733 | 123.2391 | -0.21973 | -0.14191 | 0.082398 | -0.09613 | -0.16479 | 0.032044 | 0.091553 | -0.19684 | -0.032043 | -0.086975 | 123.0469 | 123.1155 | 59.0881 | -123.111 | 123.0652 | 122.9462 | 59.1797 | -123.1979
191.6875 | 123.3673 | -59.0469 | 63.9908 | -0.33194 | -0.006241 | 0.079576 | 0.071806 | 0.11317 | -0.0037176 | 0.00075395 | -0.38701 | -0.0084822 | 0.061998 | 0.064648 | -0.0056342 | -0.0039584 | 64.1098 | 64.4852 | 0.35248 | -59.0378 | 64.0778 | -59.0515 | -59.1156 | -58.9554 | 0.21057 | -59.2255 | 64.0411 | 63.9038 | -59.1385 | -59.2072 | -0.004578 | -0.068665 | 0.086975 | 123.5321 | 0.009155 | 0.07782 | 0.11902 | -0.091553 | -0.16022 | 0.050354 | 0.091553 | -0.17853 | -0.018311 | -0.086975 | 123.1247 | 123.1567 | 59.3994 | -123.1064 | 123.0881 | 122.9507 | 59.2575 | -123.1979
192.6875 | 123.3582 | -59.0378 | 63.9908 | -0.30143 | -0.009445 | 0.078508 | 0.081419 | 0.14415 | -0.00051261 | -0.006723 | -0.44805 | -0.0042092 | 0.051317 | 0.059307 | 0.0061158 | -0.0082304 | 64.0778 | 64.238 | 0.082397 | -59.2392 | 64.0274 | -59.0927 | -59.1293 | -58.9691 | 0.19226 | -59.2575 | 64.0503 | 63.9404 | -59.1385 | -59.2209 | -0.054931 | -0.091552 | 0.036621 | 123.2758 | -0.20142 | -0.10986 | 0.086975 | -0.10071 | -0.1831 | 0.059509 | 0.068665 | -0.21973 | -0.036621 | -0.050354 | 123.0652 | 123.1155 | 59.1202 | -123.1201 | 123.0881 | 122.9782 | 59.23 | -123.2117
193.6875 | 123.3444 | -59.0424 | 63.9862 | -0.39298 | -0.004105 | 0.073167 | 0.086759 | 0.1324 | 0.0016234 | 0.009299 | -0.37176 | -0.0074142 | 0.053453 | 0.042218 | -0.0013612 | -0.01998 | 64.0869 | 64.2426 | 0.09613 | -59.2438 | 64.0274 | -59.0836 | -59.1385 | -58.9737 | 0.19226 | -59.2392 | 64.0274 | 63.913 | -59.1202 | -59.2163 | -0.041199 | -0.096131 | 0.041199 | 123.2849 | -0.20142 | -0.10529 | 0.10071 | -0.07782 | -0.17395 | 0.041199 | 0.068664 | -0.19684 | -0.022888 | -0.073242 | 123.0698 | 123.1293 | 59.1385 | -123.1247 | 123.0698 | 122.9553 | 59.2346 | -123.2025
194.6875 | 123.3765 | -59.0424 | 63.9908 | -0.14884 | -0.010514 | 0.073167 | 0.055784 | 0.11851 | 0.00055539 | -0.001382 | -0.40227 | -0.013823 | 0.056658 | 0.052899 | 0.0039788 | -0.012503 | 64.0778 | 64.2517 | 0.11444 | -59.2392 | 64.0411 | -59.0836 | -59.1339 | -58.9691 | 0.18768 | -59.2529 | 64.0366 | 63.8901 | -59.1064 | -59.2117 | -0.041199 | -0.091553 | 0.050354 | 123.2941 | -0.19684 | -0.10529 | 0.086975 | -0.064087 | -0.16937 | 0.045776 | 0.073242 | -0.21057 | -0.041199 | -0.10071 | 123.0835 | 123.1201 | 59.1568 | -123.1247 | 123.0789 | 122.9324 | 59.23 | -123.2025
195.6875 | 123.3719 | -59.0652 | 64.0045 | -0.89652 | 0.003372 | 0.072099 | 0.061125 | 0.13667 | -0.0090576 | -0.006723 | -0.29546 | -0.010618 | 0.068407 | 0.059307 | 0.0050478 | 0.0099276 | 64.0869 | 64.2334 | 0.091553 | -59.23 | 64.0366 | -59.0561 | -59.1385 | -58.9645 | 0.18768 | -59.2484 | 64.0549 | 63.8901 | -59.1293 | -59.2117 | 0.009156 | -0.073242 | 0.032043 | 123.2986 | -0.16479 | -0.091553 | 0.082397 | -0.064086 | -0.14648 | 0.050354 | 0.10071 | -0.1831 | -0.036621 | -0.11444 | 123.1018 | 123.1522 | 59.1568 | -123.143 | 123.1201 | 122.9553 | 59.2529 | -123.2162
196.6875 | 123.4177 | -59.0515 | 63.9954 | -0.1641 | 0.001236 | 0.067827 | 0.06967 | 0.12812 | -0.010127 | -0.010995 | -0.29546 | -0.017027 | 0.049181 | 0.039013 | -0.0024292 | -0.010367 | 64.064 | 64.2288 | 0.07782 | -59.2346 | 64.0182 | -59.0836 | -59.1202 | -58.9188 | 0.1831 | -59.2255 | 64.032 | 63.8901 | -59.0973 | -59.2117 | -0.032043 | -0.068664 | 0.022889 | 123.2803 | -0.18311 | -0.11444 | 0.068665 | -0.045776 | -0.16022 | 0.036621 | 0.13275 | -0.17395 | -0.013733 | -0.10529 | 123.0698 | 123.1155 | 59.1293 | -123.1155 | 123.0835 | 122.9416 | 59.2346 | -123.2071
197.7031 | 123.262 | -59.0973 | 64.0045 | -0.36246 | 0.014053 | 0.056077 | 0.088896 | 0.13026 | 0.033666 | 0.006095 | -0.63115 | 0.0086078 | 0.061998 | 0.055035 | 0.014661 | -0.021048 | 64.0274 | 64.1006 | -0.013733 | -59.2758 | 64.0778 | -59.1339 | -59.1568 | -59.0286 | 0.091553 | -59.3399 | 64.0823 | 63.9633 | -59.1797 | -59.2346 | -0.036621 | -0.059509 | 0.073242 | 123.1979 | -0.17853 | -0.11902 | 0.022888 | -0.082397 | -0.13733 | 0.077819 | 0.068665 | -0.24262 | -0.10529 | -0.041199 | 123.175 | 123.1247 | 59.0836 | -123.1613 | 123.1796 | 123.0606 | 59.1888 | -123.2391
198.6875 | 123.2941 | -59.0744 | 64.032 | -0.43876 | -0.005173 | 0.071031 | 0.06967 | 0.13881 | -0.00051261 | 0.005026 | -0.44805 | -0.010618 | 0.056658 | 0.06358 | 0.0018428 | -0.0092984 | 64.0366 | 64.2242 | 0.073242 | -59.2346 | 64.032 | -59.1202 | -59.1385 | -58.992 | 0.14648 | -59.285 | 64.0594 | 63.9221 | -59.1339 | -59.23 | -0.045776 | -0.064087 | 0 | 123.2986 | -0.16022 | -0.09613 | 0.004578 | -0.059509 | -0.15564 | 0.027466 | 0.082398 | -0.21057 | -0.054931 | -0.10986 | 123.1064 | 123.111 | 59.1476 | -123.1705 | 123.1338 | 122.9965 | 59.2209 | -123.262
199.6875 | 123.349 | -59.079 | 64.0091 | -0.31669 | 0.012985 | 0.08278 | 0.062193 | 0.13133 | -0.0058536 | 0.00289 | -0.43279 | 0.0043348 | 0.055589 | 0.058239 | -0.0077702 | -0.0092984 | 64.0411 | 64.2242 | 0.082397 | -59.2346 | 64.0182 | -59.1064 | -59.1339 | -59.0012 | 0.16479 | -59.3033 | 64.0411 | 63.9404 | -59.1614 | -59.2117 | -0.027466 | -0.054932 | 0.009156 | 123.3032 | -0.15564 | -0.10071 | 0.032044 | -0.082398 | -0.13275 | 0.032044 | 0.077819 | -0.22431 | -0.091553 | -0.068664 | 123.0972 | 123.1201 | 59.1614 | -123.143 | 123.1201 | 123.0194 | 59.2438 | -123.2208
200.6875 | 123.3353 | -59.0469 | 64.0137 | -0.39298 | -0.004105 | 0.063554 | 0.080351 | 0.14201 | -0.011195 | 0.00289 | -0.44805 | -0.0063462 | 0.065202 | 0.057171 | 0.0007748 | -0.0082304 | 64.0503 | 64.2059 | 0.091553 | -59.2392 | 64.0411 | -59.0973 | -59.1476 | -58.9966 | 0.16022 | -59.2804 | 64.0778 | 63.913 | -59.1385 | -59.2163 | -0.050354 | -0.10071 | 0.027466 | 123.2529 | -0.19226 | -0.091553 | 0.036621 | -0.091553 | -0.16937 | 0.064087 | 0.050354 | -0.23346 | -0.064087 | -0.10071 | 123.0881 | 123.0972 | 59.1385 | -123.1613 | 123.1247 | 122.9599 | 59.2072 | -123.23
201.6875 | 123.3307 | -59.0424 | 64.0182 | -0.4235 | -0.005173 | 0.062486 | 0.065397 | 0.12278 | -0.0058536 | -0.00031405 | -0.49383 | -0.0031412 | 0.068407 | 0.053967 | -0.0013612 | -0.0071624 | 64.0732 | 64.2197 | 0.073242 | -59.2255 | 64.0137 | -59.0881 | -59.1431 | -58.9966 | 0.16479 | -59.2667 | 64.064 | 63.9313 | -59.1293 | -59.2255 | -0.045777 | -0.10071 | -0.004578 | 123.262 | -0.18311 | -0.082398 | 0.054931 | -0.086975 | -0.18311 | 0.045776 | 0.045776 | -0.22431 | -0.041199 | -0.086976 | 123.056 | 123.1155 | 59.1156 | -123.1613 | 123.1064 | 122.9736 | 59.2072 | -123.2437
202.7031 | 123.2391 | -59.0881 | 64.0045 | -0.65238 | 0.03862 | 0.056077 | 0.087828 | 0.12492 | 0.025121 | 0.012503 | -0.26494 | 0.0021988 | 0.066271 | 0.055035 | 0.0071838 | -0.01998 | 64.064 | 64.1418 | 0 | -59.2712 | 64.0549 | -59.1156 | -59.1705 | -59.0469 | 0.045776 | -59.3536 | 64.0732 | 63.945 | -59.1431 | -59.2575 | -0.027466 | -0.082397 | 0.050354 | 123.23 | -0.1831 | -0.10071 | 0.059509 | -0.054931 | -0.16937 | 0.068664 | 0.041199 | -0.2655 | -0.096131 | -0.05951 | 123.143 | 123.1522 | 59.0881 | -123.175 | 123.1613 | 123.0331 | 59.1339 | -123.262
203.6875 | 123.3765 | -59.0607 | 63.9816 | -0.33194 | -0.00090105 | 0.062486 | 0.076078 | 0.12706 | -0.020808 | 0.00075395 | -0.86004 | -0.0052782 | 0.053453 | 0.051831 | -0.0024292 | -0.0060944 | 63.9816 | 64.65 | 0.36163 | -59.3765 | 64.032 | -59.0836 | -59.1339 | -58.9828 | 0.19226 | -59.23 | 64.0228 | 63.945 | -59.1339 | -59.2072 | -0.022888 | -0.073242 | 0.050354 | 123.7106 | -0.31586 | -0.24262 | 0 | -0.073242 | -0.14648 | 0.041199 | 0.07782 | -0.16937 | -0.022889 | -0.036621 | 123.0927 | 123.0423 | 59.4223 | -123.1155 | 123.0835 | 123.0057 | 59.2529 | -123.1888
204.6875 | 123.3307 | -59.0744 | 64.0091 | -0.33194 | 0.008713 | 0.064622 | 0.082487 | 0.1324 | 0.0048274 | 0.00075395 | -0.38701 | -0.011686 | 0.067339 | 0.056103 | 0.0039788 | -0.0018224 | 64.0549 | 64.2059 | 0.09613 | -59.2255 | 64.0366 | -59.0973 | -59.1339 | -59.0057 | 0.16479 | -59.2804 | 64.064 | 63.945 | -59.1431 | -59.2026 | -0.022888 | -0.059509 | 0.027466 | 123.2803 | -0.15106 | -0.091553 | 0.045777 | -0.068664 | -0.12817 | 0.054932 | 0.068665 | -0.20599 | -0.07782 | -0.064087 | 123.111 | 123.1293 | 59.1705 | -123.143 | 123.1384 | 123.0194 | 59.2392 | -123.2117
205.6875 | 123.2666 | -59.0836 | 64.0503 | -0.46927 | 0.010849 | 0.067827 | 0.064329 | 0.14094 | 0.00055539 | -0.00031405 | -0.18865 | 0.0043348 | 0.051317 | 0.064648 | -0.0045652 | -0.00075443 | 64.0137 | 64.1418 | 0.013733 | -59.285 | 64.064 | -59.111 | -59.1614 | -59.0103 | 0.059509 | -59.3536 | 64.0869 | 63.9816 | -59.1385 | -59.2484 | -0.027466 | -0.07782 | 0.013733 | 123.2254 | -0.20142 | -0.1236 | -0.036621 | -0.054932 | -0.16479 | 0.036621 | 0.073242 | -0.27008 | -0.10529 | -0.068665 | 123.1476 | 123.0972 | 59.0973 | -123.2117 | 123.1705 | 123.0652 | 59.1431 | -123.2986
206.6875 | 123.2437 | -59.1064 | 64.0686 | -0.43876 | 0.003372 | 0.063554 | 0.070738 | 0.13453 | 0.0016234 | 0.00075395 | -0.2802 | -0.0063462 | 0.057726 | 0.06358 | -0.0056342 | -0.0092984 | 64.0045 | 64.1373 | 0.013733 | -59.2667 | 64.0778 | -59.111 | -59.1614 | -59.0195 | 0.036621 | -59.3399 | 64.1052 | 63.9954 | -59.1568 | -59.2346 | -0.004578 | -0.054932 | 0.009155 | 123.2437 | -0.16022 | -0.10529 | -0.064087 | -0.050354 | -0.12817 | 0.036621 | 0.086975 | -0.23346 | -0.10529 | -0.073243 | 123.1842 | 123.111 | 59.1202 | -123.23 | 123.2117 | 123.1018 | 59.1431 | -123.3032
207.7031 | 123.2162 | -59.1339 | 64.0045 | 0.11056 | 0.02687 | 0.071031 | 0.094236 | 0.13346 | 0.0091004 | 0.011435 | -0.066579 | 0.0075398 | 0.08336 | 0.069989 | 0.011456 | 0.0088586 | 63.9587 | 63.9954 | -0.12817 | -59.3536 | 64.064 | -59.1431 | -59.2026 | -59.2529 | -0.25177 | -59.2209 | 64.0457 | 63.9542 | -59.1614 | -59.2667 | -0.009155 | -0.068665 | 0.059509 | 123.1293 | -0.21973 | -0.15106 | -0.045777 | -0.027466 | -0.13275 | 0.041198 | -0.11902 | -0.086975 | 0.045777 | -0.050354 | 123.1979 | 123.0927 | 59.0057 | -123.2071 | 123.1796 | 123.0881 | 58.8821 | -123.2712
208.6875 | 123.2391 | -59.0836 | 64.0137 | -0.45401 | 0.007644 | 0.069963 | 0.072874 | 0.13667 | -0.0047856 | -0.007791 | -0.24969 | 0.0043348 | 0.063066 | 0.050762 | -0.016315 | 0.0035186 | 63.9908 | 64.1327 | 0.013733 | -59.285 | 64.0457 | -59.1019 | -59.198 | -59.0378 | 0.045776 | -59.3216 | 64.0869 | 63.9725 | -59.1614 | -59.2117 | -0.018311 | -0.11444 | 0.032043 | 123.2162 | -0.20142 | -0.086975 | -0.022888 | -0.07782 | -0.12817 | 0.073242 | 0.045776 | -0.23804 | -0.10986 | -0.041199 | 123.1293 | 123.0743 | 59.0973 | -123.2117 | 123.1705 | 123.056 | 59.1293 | -123.2254
209.6875 | 123.3215 | -59.0515 | 64.0411 | -0.36246 | -0.004105 | 0.071031 | 0.073942 | 0.13987 | -0.010127 | -0.006723 | -0.38701 | 0.0086078 | 0.044908 | 0.042218 | -0.0077702 | -0.0060944 | 64.0457 | 64.2197 | 0.10071 | -59.2529 | 64.0457 | -59.0973 | -59.1431 | -58.992 | 0.16022 | -59.2804 | 64.0823 | 63.945 | -59.1522 | -59.2392 | -0.045776 | -0.091552 | 0.004577 | 123.2712 | -0.20142 | -0.10986 | 0.004577 | -0.10071 | -0.18768 | 0.041198 | 0.05951 | -0.22888 | -0.041199 | -0.096131 | 123.0972 | 123.0972 | 59.1522 | -123.1842 | 123.1338 | 122.9965 | 59.2117 | -123.2803
210.6875 | 123.317 | -59.0469 | 64.0137 | -0.45401 | -0.006241 | 0.075304 | 0.064329 | 0.13667 | -0.016535 | -0.00245 | -0.41753 | -0.0052782 | 0.063066 | 0.062512 | -0.0034972 | -0.0060944 | 64.0457 | 64.2105 | 0.086975 | -59.2346 | 64.0366 | -59.0881 | -59.1339 | -59.0057 | 0.16937 | -59.285 | 64.064 | 63.9359 | -59.1339 | -59.2346 | -0.041199 | -0.086975 | 0.022888 | 123.2574 | -0.18768 | -0.10071 | 0.032043 | -0.086975 | -0.18768 | 0.050354 | 0.041199 | -0.23804 | -0.050354 | -0.07782 | 123.0835 | 123.0927 | 59.1339 | -123.1476 | 123.111 | 122.9828 | 59.2163 | -123.2483
211.6875 | 123.2346 | -59.0698 | 64.0411 | -0.43876 | -0.011582 | 0.072099 | 0.071806 | 0.13346 | -0.0090576 | -0.005655 | -0.29546 | -0.015959 | 0.063066 | 0.048626 | 0.0007748 | -0.0071624 | 63.9954 | 64.1556 | 0.013733 | -59.285 | 64.0366 | -59.111 | -59.1705 | -59.0698 | 0.059509 | -59.3353 | 64.1006 | 63.9771 | -59.1614 | -59.2484 | -0.041199 | -0.10071 | -0.004578 | 123.2254 | -0.21515 | -0.11444 | -0.045777 | -0.091553 | -0.17853 | 0.059509 | 0 | -0.2655 | -0.086975 | -0.064087 | 123.1064 | 123.0652 | 59.0836 | -123.2117 | 123.1705 | 123.0469 | 59.1293 | -123.2895
212.7031 | 123.2712 | -59.1293 | 63.9954 | 0.36996 | 0.048233 | 0.063554 | 0.079283 | 0.12492 | 0.0058954 | -0.005655 | 0.10127 | 0.0064718 | 0.068407 | 0.043286 | 0.0029108 | -0.0018224 | 63.9587 | 64.0457 | -0.11902 | -59.3445 | 64.0823 | -59.1385 | -59.1934 | -59.0927 | -0.07782 | -59.404 | 64.0778 | 63.9313 | -59.1888 | -59.2758 | -0.009156 | -0.064087 | 0.086975 | 123.175 | -0.21515 | -0.15106 | -0.036621 | -0.05951 | -0.14648 | 0.082398 | 0.036621 | -0.27466 | -0.12817 | -0.064087 | 123.2117 | 123.0881 | 59.0103 | -123.1888 | 123.2071 | 123.0606 | 59.0515 | -123.2712
213.6875 | 123.2483 | -59.1248 | 64.0228 | -0.43876 | 0.014053 | 0.083848 | 0.079283 | 0.12812 | -0.0015816 | 0.006095 | -0.55486 | 0.0054038 | 0.045976 | 0.064648 | 0.0093198 | -0.0092984 | 64.0045 | 64.0411 | -0.050354 | -59.3079 | 64.064 | -59.1293 | -59.1888 | -59.079 | 0.054932 | -59.3628 | 64.0915 | 64.0091 | -59.1614 | -59.2346 | -0.004577 | -0.064087 | 0.041199 | 123.1659 | -0.18311 | -0.11902 | -0.01831 | -0.036621 | -0.10986 | 0.068665 | 0.045777 | -0.23804 | -0.12817 | -0.013733 | 123.1888 | 123.1293 | 59.0744 | -123.2117 | 123.2162 | 123.1338 | 59.1797 | -123.2574
214.6875 | 123.2483 | -59.1019 | 64.064 | -0.4235 | 0.016189 | 0.083848 | 0.070738 | 0.13774 | -0.0015816 | -0.001382 | -0.50908 | -0.0031412 | 0.063066 | 0.057171 | 0.0061158 | -0.016775 | 63.9908 | 64.0503 | -0.054932 | -59.3079 | 64.0686 | -59.1202 | -59.1614 | -59.079 | 0.059509 | -59.3582 | 64.1052 | 63.9999 | -59.1476 | -59.2484 | -0.01831 | -0.059509 | 0.004578 | 123.1522 | -0.20599 | -0.14648 | -0.073242 | -0.045776 | -0.14648 | 0.041199 | 0.022889 | -0.25635 | -0.10986 | -0.064087 | 123.1705 | 123.0927 | 59.0469 | -123.2254 | 123.2071 | 123.1018 | 59.1614 | -123.3124
215.6875 | 123.2391 | -59.079 | 64.0366 | -0.45401 | 0.019394 | 0.074235 | 0.079283 | 0.14094 | 0.0080314 | 0.010367 | -0.60064 | 0.0043348 | 0.067339 | 0.051831 | -0.0077702 | -0.0092984 | 63.8443 | 64.1006 | -0.004578 | -59.3628 | 64.0915 | -59.1019 | -59.2072 | -59.0927 | 0.045776 | -59.3536 | 64.0869 | 63.9587 | -59.1522 | -59.2484 | -0.022889 | -0.12817 | 0.054932 | 123.1796 | -0.28381 | -0.15564 | -0.19226 | -0.073243 | -0.16937 | 0.050354 | -0.013733 | -0.27466 | -0.10529 | -0.07782 | 123.1705 | 122.9233 | 59.0744 | -123.2437 | 123.1659 | 123.0377 | 59.1248 | -123.2849
216.6875 | 123.2254 | -59.0927 | 64.0182 | -0.49979 | 0.011917 | 0.07744 | 0.064329 | 0.13881 | 0.0016234 | -0.007791 | -0.26494 | -0.0020732 | 0.070543 | 0.048626 | -0.0013612 | 0.00031457 | 63.9999 | 64.1556 | 0.027466 | -59.2896 | 64.0457 | -59.1064 | -59.1522 | -59.0424 | 0.054932 | -59.3353 | 64.1144 | 63.9908 | -59.1614 | -59.2392 | -0.013733 | -0.05951 | 0.027465 | 123.2483 | -0.19684 | -0.13733 | -0.018311 | -0.068665 | -0.14648 | 0.09613 | 0.050354 | -0.24262 | -0.09613 | -0.027466 | 123.1384 | 123.0927 | 59.1202 | -123.1705 | 123.2071 | 123.0835 | 59.1476 | -123.2574
217.7031 | 123.3124 | -59.1156 | 63.9679 | 0.44625 | 0.019394 | 0.062486 | 0.078214 | 0.12492 | 0.012304 | 0.007163 | 0.2386 | -0.0042092 | 0.070543 | 0.051831 | 0.011456 | 0.0045866 | 63.9679 | 64.0503 | -0.082397 | -59.3216 | 64.0091 | -59.1248 | -59.2026 | -59.0286 | -0.022888 | -59.3308 | 64.0137 | 63.9175 | -59.1934 | -59.2621 | -0.009155 | -0.086975 | 0.041198 | 123.1659 | -0.20599 | -0.11902 | 0 | -0.077819 | -0.14648 | 0.045776 | 0.086976 | -0.21515 | -0.068665 | -0.050354 | 123.1247 | 123.0835 | 59.0332 | -123.1705 | 123.1293 | 123.0331 | 59.0927 | -123.23
218.6875 | 123.2391 | -59.0836 | 64.0228 | -0.43876 | 0.005508 | 0.072099 | 0.077146 | 0.14521 | -0.012263 | 0.005026 | -0.15813 | 0.0011308 | 0.052385 | 0.060376 | -0.0077702 | -0.0060944 | 63.9084 | 63.9999 | -0.068665 | -59.3033 | 64.0778 | -59.1339 | -59.1888 | -59.079 | 0.054932 | -59.3674 | 64.1052 | 64.0091 | -59.1751 | -59.23 | -0.050354 | -0.10529 | 0.054932 | 123.0835 | -0.21973 | -0.11444 | -0.11444 | -0.091553 | -0.14648 | 0.082398 | 0.004578 | -0.28381 | -0.13733 | -0.013733 | 123.1613 | 122.9919 | 59.0149 | -123.2117 | 123.1888 | 123.0927 | 59.1385 | -123.2529
219.6875 | 123.2803 | -59.0744 | 64.0228 | -0.28617 | 0.022598 | 0.072099 | 0.076078 | 0.13774 | 0.0016234 | -0.008859 | -0.52434 | 0.0043348 | 0.067339 | 0.045422 | -0.0024292 | -0.0028904 | 63.9862 | 64.1006 | -0.022888 | -59.285 | 64.0549 | -59.1202 | -59.166 | -59.0607 | 0.073242 | -59.3536 | 64.0915 | 63.9679 | -59.1751 | -59.2438 | -0.045776 | -0.091553 | 0.032044 | 123.175 | -0.21057 | -0.11902 | -0.036621 | -0.10071 | -0.16937 | 0.068665 | 0.013733 | -0.27924 | -0.10986 | -0.054931 | 123.1293 | 123.0606 | 59.0515 | -123.1888 | 123.1659 | 123.0423 | 59.1476 | -123.2666
220.6875 | 123.2849 | -59.0836 | 64.032 | -0.3472 | 0.020462 | 0.064622 | 0.072874 | 0.13453 | 0.00055539 | 0.00289 | -0.60064 | -0.0042092 | 0.069475 | 0.048626 | 0.0082518 | -0.0039584 | 63.9725 | 64.0869 | -0.018311 | -59.2804 | 64.0503 | -59.1156 | -59.1934 | -59.0698 | 0.073242 | -59.3536 | 64.0823 | 64.0045 | -59.1705 | -59.2484 | -0.032044 | -0.10986 | 0.018311 | 123.1705 | -0.19684 | -0.086976 | -0.059509 | -0.086975 | -0.16479 | 0.050354 | 0.013733 | -0.27008 | -0.10529 | -0.027465 | 123.1338 | 123.056 | 59.0652 | -123.2254 | 123.1659 | 123.0881 | 59.1568 | -123.2803
221.6875 | 123.2895 | -59.1064 | 64.0503 | -0.37772 | 0.02687 | 0.066759 | 0.086759 | 0.1324 | -0.0058536 | 0.001822 | -0.44805 | 0.0021988 | 0.072679 | 0.056103 | 0.0050478 | -0.011435 | 63.9679 | 64.1006 | -0.022888 | -59.285 | 64.0549 | -59.1385 | -59.1797 | -59.0652 | 0.086975 | -59.3445 | 64.0732 | 63.9679 | -59.1522 | -59.2575 | -0.032044 | -0.073242 | 0.004578 | 123.2071 | -0.17853 | -0.10529 | -0.082397 | -0.045777 | -0.15106 | 0.022888 | 0.041198 | -0.23804 | -0.086975 | -0.082397 | 123.1613 | 123.0743 | 59.0836 | -123.23 | 123.1796 | 123.0743 | 59.1934 | -123.3078
222.6875 | 123.2803 | -59.0973 | 64.0228 | -0.36246 | 0.015121 | 0.06569 | 0.082487 | 0.12812 | 0.0048274 | 0.011435 | -0.46331 | -0.0020732 | 0.068407 | 0.062512 | -0.0002932 | -0.0092984 | 63.9633 | 64.0915 | -0.036621 | -59.2804 | 64.0457 | -59.0973 | -59.1522 | -59.0744 | 0.068665 | -59.3674 | 64.0869 | 63.9954 | -59.1751 | -59.2484 | 0 | -0.054932 | 0.022888 | 123.1888 | -0.18311 | -0.12817 | -0.059509 | -0.07782 | -0.15106 | 0.064087 | 0.022888 | -0.27008 | -0.11902 | -0.027466 | 123.143 | 123.0606 | 59.0607 | -123.175 | 123.1842 | 123.0927 | 59.166 | -123.2712
223.6875 | 123.23 | -59.0927 | 64.0457 | -0.45401 | 0.002304 | 0.068895 | 0.080351 | 0.12812 | -0.0090576 | -0.00031405 | -0.20391 | -0.0052782 | 0.066271 | 0.058239 | 0.0071838 | -0.016775 | 63.9175 | 63.9816 | -0.086975 | -59.2941 | 64.0686 | -59.1431 | -59.1751 | -59.0881 | 0.059509 | -59.3628 | 64.0961 | 63.9908 | -59.1888 | -59.2621 | -0.050354 | -0.082398 | 0.022889 | 123.0743 | -0.20142 | -0.11902 | -0.12817 | -0.096131 | -0.16937 | 0.050354 | 0.004577 | -0.27008 | -0.10071 | -0.054931 | 123.1613 | 123.0103 | 59.0057 | -123.2208 | 123.1888 | 123.0835 | 59.1522 | -123.3078
224.6875 | 123.2208 | -59.0881 | 64.0549 | -0.40824 | 0.00444 | 0.073167 | 0.089964 | 0.14415 | -0.0026496 | 0.006095 | -0.52434 | -0.0042092 | 0.069475 | 0.04649 | 0.0071838 | -0.0050264 | 63.8489 | 64.064 | 0.009155 | -59.3491 | 64.0778 | -59.1476 | -59.1843 | -59.0973 | 0.045776 | -59.3674 | 64.0961 | 63.9908 | -59.1797 | -59.2575 | -0.059509 | -0.09613 | 0.022888 | 123.1522 | -0.26093 | -0.16479 | -0.20599 | -0.091552 | -0.16937 | 0.041198 | -0.009155 | -0.27924 | -0.10986 | -0.064087 | 123.1659 | 122.937 | 59.0973 | -123.2391 | 123.1842 | 123.0789 | 59.1339 | -123.3124
225.6875 | 123.2986 | -59.0698 | 63.9679 | -0.27091 | 0.032211 | 0.074235 | 0.068601 | 0.12706 | 0.010168 | -0.001382 | -0.32598 | -0.0031412 | 0.06093 | 0.061444 | 0.0039788 | -0.013571 | 63.9999 | 64.1006 | -0.013733 | -59.2896 | 64.0457 | -59.111 | -59.1614 | -59.0424 | 0.07782 | -59.3353 | 64.0732 | 63.9954 | -59.1568 | -59.2392 | -0.041199 | -0.091553 | 0.077819 | 123.1705 | -0.21973 | -0.12817 | 0.032043 | -0.086975 | -0.16937 | 0.10529 | 0.027466 | -0.2655 | -0.09613 | 0.027465 | 123.1155 | 123.0698 | 59.0561 | -123.1293 | 123.143 | 123.0652 | 59.1476 | -123.2071
226.6875 | 123.2391 | -59.111 | 63.9999 | -0.4235 | 0.048233 | 0.068895 | 0.086759 | 0.13774 | 0.0037594 | -0.00031405 | -0.32598 | 0.0096758 | 0.072679 | 0.058239 | 0.0082518 | -0.00075443 | 64.0045 | 64.0778 | -0.004578 | -59.2484 | 64.0778 | -59.111 | -59.1797 | -59.0424 | 0.091553 | -59.3445 | 64.0778 | 63.9771 | -59.1751 | -59.2758 | 0 | -0.068664 | 0.07782 | 123.1888 | -0.13733 | -0.068665 | 0.004578 | -0.064087 | -0.16479 | 0.07782 | 0.068665 | -0.23346 | -0.068664 | -0.022888 | 123.1888 | 123.1155 | 59.1064 | -123.1796 | 123.1888 | 123.0881 | 59.2026 | -123.2758
227.6875 | 123.2712 | -59.1064 | 64.0274 | -0.30143 | 0.046097 | 0.071031 | 0.07501 | 0.13881 | -0.0015816 | 0.005026 | -0.21917 | 0.0054038 | 0.081224 | 0.06892 | 0.0029108 | -0.0060944 | 63.9816 | 64.1464 | 0.018311 | -59.2621 | 64.0823 | -59.111 | -59.1476 | -59.0378 | 0.07782 | -59.3399 | 64.0686 | 63.9908 | -59.1705 | -59.2941 | -0.004578 | -0.041199 | 0.054931 | 123.2529 | -0.15564 | -0.11444 | -0.045777 | -0.064087 | -0.18768 | 0.041199 | 0.068664 | -0.23346 | -0.045777 | -0.036621 | 123.1888 | 123.0881 | 59.1248 | -123.175 | 123.175 | 123.0972 | 59.1843 | -123.3215
228.6875 | 123.3215 | -59.079 | 63.9999 | -0.20987 | 0.049301 | 0.063554 | 0.064329 | 0.1324 | -0.00051261 | 0.003958 | -0.17339 | 0.0043348 | 0.069475 | 0.044354 | 0.0039788 | -0.0060944 | 64.0274 | 64.0961 | -0.009155 | -59.2529 | 64.0594 | -59.1064 | -59.1934 | -59.0469 | 0.13733 | -59.5184 | 64.0366 | 63.9587 | -59.1843 | -59.2804 | -0.027466 | -0.11444 | 0.059509 | 123.175 | -0.17395 | -0.05951 | 0.027466 | -0.10529 | -0.20142 | 0.036621 | 0.032043 | -0.43945 | -0.23804 | -0.041199 | 123.1384 | 123.1064 | 59.0698 | -123.1934 | 123.1155 | 123.0377 | 59.2163 | -123.2803
229.6875 | 123.2712 | -59.0927 | 64.0091 | -0.28617 | 0.067459 | 0.053941 | 0.071806 | 0.13026 | 0.00055539 | 0.001822 | -0.21917 | 6.2833e-05 | 0.070543 | 0.065716 | 0.0071838 | -0.013571 | 64.0137 | 64.1098 | 0.004578 | -59.2804 | 64.0549 | -59.1156 | -59.1522 | -59.0378 | -0.11444 | -59.4223 | 64.032 | 63.9633 | -59.1751 | -59.2621 | -0.022889 | -0.05951 | 0.045777 | 123.2025 | -0.18768 | -0.12817 | 0.004578 | -0.082398 | -0.16937 | 0.022888 | 0.054931 | -0.32959 | -0.16022 | -0.045776 | 123.1476 | 123.1064 | 59.0973 | -123.1613 | 123.1247 | 123.056 | 58.9783 | -123.2712
230.6875 | 123.2803 | -59.079 | 64.0366 | -0.22513 | 0.052505 | 0.063554 | 0.080351 | 0.11958 | -0.0047856 | -0.012063 | -0.32598 | 0.0021988 | 0.064134 | 0.060376 | -0.0077702 | 0.0013826 | 63.9908 | 64.1006 | 0.009155 | -59.2804 | 64.0411 | -59.1248 | -59.1705 | -59.0607 | -0.09613 | -59.4315 | 64.0182 | 63.9679 | -59.1797 | -59.2667 | -0.045777 | -0.091553 | 0.004578 | 123.1796 | -0.20142 | -0.10986 | -0.045776 | -0.10071 | -0.18768 | -0.01831 | 0.01831 | -0.35248 | -0.16479 | -0.068664 | 123.1201 | 123.0698 | 59.0881 | -123.2071 | 123.0972 | 123.0469 | 58.9828 | -123.3032
231.6875 | 123.2758 | -59.079 | 64.0182 | -0.37772 | 0.023666 | 0.075304 | 0.079283 | 0.1324 | 0.0069634 | -0.001382 | -0.49383 | 6.2833e-05 | 0.070543 | 0.060376 | 0.0050478 | -0.0060944 | 63.9679 | 64.0823 | -0.013733 | -59.3033 | 64.0411 | -59.1156 | -59.1843 | -59.0698 | 0.091553 | -59.3445 | 64.0732 | 64.0045 | -59.166 | -59.23 | -0.036622 | -0.10529 | 0.022888 | 123.1613 | -0.22431 | -0.11902 | -0.050354 | -0.086976 | -0.15106 | 0.054931 | 0.009155 | -0.2655 | -0.11444 | -0.013733 | 123.1201 | 123.0469 | 59.0652 | -123.2025 | 123.1522 | 123.0835 | 59.1705 | -123.2483
232.6875 | 123.3078 | -59.0973 | 64.032 | -0.17936 | 0.047165 | 0.072099 | 0.084623 | 0.12706 | -0.0079896 | -0.006723 | -0.05132 | 0.0021988 | 0.071611 | 0.069989 | 0.0082518 | -0.012503 | 64.0182 | 64.1098 | -0.013733 | -59.285 | 64.0228 | -59.1248 | -59.1843 | -59.0698 | 0.036621 | -59.3674 | 64.0457 | 63.9954 | -59.1888 | -59.2529 | -0.027466 | -0.086975 | -0.009155 | 123.2071 | -0.18768 | -0.10071 | -0.013732 | -0.091553 | -0.15564 | 0.013733 | 0.027466 | -0.27008 | -0.11444 | -0.036621 | 123.1201 | 123.1155 | 59.0836 | -123.2162 | 123.143 | 123.0927 | 59.1339 | -123.2849
233.6875 | 123.262 | -59.1019 | 63.9816 | -0.087804 | 0.02153 | 0.056077 | 0.088896 | 0.13774 | 0.0091004 | 0.010367 | -0.036062 | 0.0054038 | 0.075884 | 0.061444 | 0.0029108 | 0.0024506 | 64.0045 | 64.119 | -0.022888 | -59.2896 | 64.032 | -59.1293 | -59.1568 | -59.0836 | 0.032043 | -59.3765 | 64.0686 | 63.9771 | -59.1934 | -59.2758 | -0.027465 | -0.054931 | 0.050354 | 123.2208 | -0.18768 | -0.13275 | 0.022889 | -0.091552 | -0.17395 | 0.086976 | 0.018311 | -0.27466 | -0.10071 | -0.004577 | 123.1338 | 123.1064 | 59.079 | -123.1384 | 123.1705 | 123.0789 | 59.1339 | -123.2574
234.6875 | 123.2895 | -59.079 | 63.9954 | -0.14884 | 0.018326 | 0.064622 | 0.072874 | 0.13346 | 0.0026914 | 0.007163 | -0.097097 | 0.0064718 | 0.076952 | 0.062512 | -0.0013612 | -0.0039584 | 63.9999 | 64.119 | -0.009155 | -59.2896 | 64.0228 | -59.111 | -59.1568 | -59.0744 | 0.027466 | -59.3674 | 64.0594 | 64.0137 | -59.1522 | -59.2575 | -0.032044 | -0.07782 | 0.027466 | 123.1979 | -0.21057 | -0.13275 | 0.004578 | -0.073243 | -0.17853 | 0.064087 | 0.004577 | -0.28839 | -0.10986 | 0.018311 | 123.1018 | 123.0789 | 59.0698 | -123.1522 | 123.1384 | 123.0927 | 59.1064 | -123.2529
235.6875 | 123.2666 | -59.0973 | 64.0137 | -0.11832 | 0.014053 | 0.066759 | 0.079283 | 0.13667 | 0.0058954 | -0.003518 | -0.12761 | 6.2833e-05 | 0.085497 | 0.061444 | 0.013592 | -0.0060944 | 63.9999 | 64.1052 | -0.027466 | -59.3079 | 64.0457 | -59.1202 | -59.166 | -59.0744 | 0.018311 | -59.3719 | 64.0503 | 64.0045 | -59.1705 | -59.285 | -0.022888 | -0.068665 | 0.032043 | 123.2025 | -0.21057 | -0.14191 | -0.013733 | -0.073242 | -0.18768 | 0.036621 | 0.022888 | -0.27466 | -0.086975 | -0.009155 | 123.143 | 123.0972 | 59.0698 | -123.1796 | 123.1476 | 123.1018 | 59.1156 | -123.2986
236.6875 | 123.2529 | -59.0973 | 64.0137 | -0.087804 | 0.023666 | 0.068895 | 0.083555 | 0.1324 | 0.0037594 | -0.001382 | -0.097097 | 0.0021988 | 0.065202 | 0.062512 | 0.0071838 | -0.0050264 | 63.9999 | 64.1144 | -0.027466 | -59.2941 | 64.0228 | -59.1248 | -59.1614 | -59.0698 | 0.027466 | -59.3765 | 64.0457 | 64.0091 | -59.1934 | -59.2621 | -0.027466 | -0.064087 | 0.009155 | 123.2117 | -0.19684 | -0.13275 | -0.013733 | -0.09613 | -0.16479 | 0.032043 | 0.027466 | -0.27924 | -0.11444 | -0.004578 | 123.1201 | 123.0972 | 59.0698 | -123.175 | 123.143 | 123.1064 | 59.1248 | -123.2758
237.6875 | 123.3078 | -59.079 | 64.0182 | -0.1641 | 0.020462 | 0.078508 | 0.076078 | 0.13881 | 0.0016234 | 0.00289 | 1.1694 | 0.0043348 | 0.086565 | 0.045422 | 0.0050478 | -0.018912 | 63.9862 | 64.1052 | 0.004578 | -59.285 | 64.0366 | -59.1385 | -59.1614 | -59.0469 | 0.091553 | -59.3308 | 64.0915 | 64.0137 | -59.1797 | -59.2621 | -0.05951 | -0.082398 | 0.01831 | 123.1842 | -0.20599 | -0.1236 | -0.032044 | -0.10071 | -0.18311 | 0.073242 | 0.032043 | -0.25177 | -0.068665 | -0.004578 | 123.1155 | 123.0652 | 59.0836 | -123.1796 | 123.1705 | 123.0927 | 59.1705 | -123.2803
238.6875 | 123.262 | -59.1019 | 63.9771 | -0.19462 | 0.030075 | 0.067827 | 0.084623 | 0.12919 | 0.0058954 | 0.005026 | -0.097097 | -0.0020732 | 0.068407 | 0.061444 | 0.0071838 | -0.0092984 | 64.0091 | 64.0823 | -0.041199 | -59.2987 | 64.0274 | -59.1202 | -59.1476 | -59.079 | 0.027466 | -59.3765 | 64.0732 | 64.0091 | -59.1934 | -59.2667 | -0.01831 | -0.045776 | 0.050354 | 123.1842 | -0.19684 | -0.15106 | 0.032043 | -0.091552 | -0.16479 | 0.09613 | 0.022889 | -0.27466 | -0.10986 | 0.032043 | 123.1293 | 123.111 | 59.0607 | -123.1247 | 123.175 | 123.111 | 59.1293 | -123.2437
239.6875 | 123.2117 | -59.1202 | 63.9999 | 0.11056 | 0.025802 | 0.06035 | 0.080351 | 0.13133 | 0.0016234 | 0.00289 | 0.024973 | 0.0021988 | 0.07802 | 0.067852 | -0.0056342 | -0.0018224 | 63.945 | 64.0228 | -0.086975 | -59.3262 | 64.032 | -59.1156 | -59.1705 | -59.1248 | -0.064087 | -59.4406 | 64.0366 | 63.9954 | -59.1888 | -59.2987 | 0.004577 | -0.050354 | 0.032043 | 123.143 | -0.20599 | -0.15564 | -0.054932 | -0.068665 | -0.17853 | 0.036621 | -0.004578 | -0.32043 | -0.14191 | -0.004578 | 123.1522 | 123.0652 | 59.0332 | -123.1705 | 123.1567 | 123.1155 | 59.0561 | -123.2986
240.6875 | 123.2071 | -59.0973 | 64.0091 | 0.080043 | 0.030075 | 0.063554 | 0.078214 | 0.1324 | 0.0091004 | -0.001382 | 0.055491 | 0.0021988 | 0.08336 | 0.065716 | 0.0071838 | -0.0060944 | 63.9542 | 64.0091 | -0.091553 | -59.3262 | 64.0503 | -59.1339 | -59.1522 | -59.1385 | -0.073242 | -59.436 | 64.0549 | 63.9954 | -59.2163 | -59.3079 | -0.036621 | -0.054932 | 0.041199 | 123.1064 | -0.22888 | -0.17395 | -0.054931 | -0.11902 | -0.21057 | 0.045777 | -0.041199 | -0.33874 | -0.12817 | -0.013733 | 123.1476 | 123.0515 | 59.0057 | -123.1613 | 123.1522 | 123.0927 | 59.024 | -123.317
241.6875 | 123.2254 | -59.1156 | 63.9999 | 0.11056 | 0.052505 | 0.06035 | 0.073942 | 0.13774 | 0.0016234 | 0.001822 | -0.097097 | 0.013948 | 0.089769 | 0.04649 | 0.0061158 | -0.0018224 | 63.9496 | 64.0137 | -0.10071 | -59.3079 | 64.0457 | -59.1385 | -59.1751 | -59.1385 | -0.091553 | -59.4452 | 64.0594 | 64.0045 | -59.1934 | -59.2758 | -0.022888 | -0.059509 | 0.045776 | 123.1293 | -0.19226 | -0.13275 | -0.050354 | -0.077819 | -0.16022 | 0.059509 | -0.022888 | -0.32959 | -0.16937 | 0.004578 | 123.1613 | 123.0652 | 59.0149 | -123.175 | 123.175 | 123.1201 | 59.024 | -123.2758
242.6875 | 123.23 | -59.1156 | 63.9862 | 0.095301 | 0.045028 | 0.06035 | 0.079283 | 0.13453 | 0.0037594 | 0.001822 | 0.498 | 0.0043348 | 0.085497 | 0.055035 | 0.0018428 | -0.0050264 | 63.945 | 64.0045 | -0.091553 | -59.3308 | 64.0366 | -59.1202 | -59.1797 | -59.1522 | -0.10071 | -59.4315 | 64.0915 | 63.9908 | -59.198 | -59.2896 | -0.004577 | -0.064086 | 0.050354 | 123.1201 | -0.21515 | -0.15106 | -0.041199 | -0.082397 | -0.17395 | 0.10529 | -0.036621 | -0.31586 | -0.14191 | 0.004578 | 123.1522 | 123.0606 | 59.024 | -123.1659 | 123.2071 | 123.1064 | 59.0149 | -123.2758
243.6875 | 123.2437 | -59.0973 | 63.9725 | -0.087804 | 0.052505 | 0.068895 | 0.073942 | 0.13346 | 0.010168 | -0.001382 | -0.12761 | 6.2833e-05 | 0.068407 | 0.062512 | 0.0039788 | -0.0082304 | 63.9908 | 64.0732 | -0.036621 | -59.2987 | 64.0274 | -59.1156 | -59.1843 | -59.0927 | 0.004578 | -59.3857 | 64.0594 | 64.0045 | -59.1843 | -59.2575 | -0.018311 | -0.086975 | 0.054932 | 123.1705 | -0.20142 | -0.11444 | 0.018311 | -0.086975 | -0.16022 | 0.086975 | 0.004578 | -0.28839 | -0.12817 | 0.032044 | 123.1247 | 123.0881 | 59.0607 | -123.1567 | 123.1567 | 123.1018 | 59.1019 | -123.23
244.6875 | 123.2574 | -59.1064 | 64.032 | -0.087804 | 0.030075 | 0.067827 | 0.070738 | 0.13346 | 0.0048274 | -0.00031405 | 0.024973 | 0.0011308 | 0.08336 | 0.053967 | 0.0082518 | -0.010367 | 63.9816 | 64.0594 | -0.041199 | -59.3033 | 64.032 | -59.1339 | -59.1705 | -59.0973 | -0.004578 | -59.3811 | 64.0411 | 63.9816 | -59.1888 | -59.2712 | -0.027466 | -0.064087 | 0 | 123.1659 | -0.19684 | -0.13275 | -0.050354 | -0.082398 | -0.16479 | 0.009156 | 0.009155 | -0.27466 | -0.10986 | -0.050354 | 123.1384 | 123.0881 | 59.0652 | -123.2025 | 123.1476 | 123.0881 | 59.1019 | -123.3032
245.6875 | 123.1842 | -59.111 | 63.9999 | 0.11056 | 0.033279 | 0.06035 | 0.080351 | 0.12706 | 0.0016234 | 0.007163 | 0.07075 | -0.0010052 | 0.059862 | 0.04649 | 0.0050478 | 0.0013826 | 63.9313 | 63.9999 | -0.10071 | -59.3399 | 64.0366 | -59.1614 | -59.198 | -59.1476 | -0.07782 | -59.4452 | 64.0869 | 63.9862 | -59.1751 | -59.2758 | -0.050354 | -0.086975 | 0.036621 | 123.111 | -0.22888 | -0.14191 | -0.068665 | -0.064087 | -0.16479 | 0.086975 | -0.036621 | -0.33417 | -0.16937 | -0.013733 | 123.1476 | 123.0423 | 59.0103 | -123.1979 | 123.1979 | 123.0972 | 59.0332 | -123.2758
246.6875 | 123.2208 | -59.1339 | 64.0045 | 1.4076 | 0.009781 | 0.07744 | 0.082487 | 0.12172 | 0.0058954 | -0.017404 | 0.31489 | 0.0064718 | 0.071611 | 0.064648 | -0.0034972 | 0.0035186 | 63.8855 | 64.0366 | -0.10986 | -59.3308 | 64.0274 | -59.1339 | -59.198 | -59.1293 | -0.082397 | -59.4177 | 64.0457 | 64.0091 | -59.2163 | -59.2758 | 0 | -0.064087 | 0.022888 | 123.1705 | -0.19684 | -0.13275 | -0.11902 | -0.082398 | -0.14191 | 0.041198 | 0.004578 | -0.28381 | -0.14191 | 0.004577 | 123.1613 | 123.0194 | 59.024 | -123.2025 | 123.1796 | 123.143 | 59.0515 | -123.2803
247.6875 | 123.2666 | -59.111 | 64.0045 | 0.32418 | 0.050369 | 0.059282 | 0.10385 | 0.1324 | 0.0016234 | -0.006723 | 0.22334 | 0.0054038 | 0.085497 | 0.061444 | -0.0045652 | -0.0039584 | 63.9816 | 63.9725 | -0.13733 | -59.317 | 64.0503 | -59.1385 | -59.1751 | -59.1385 | -0.086975 | -59.3994 | 64.0594 | 64.0228 | -59.2072 | -59.2667 | -0.027466 | -0.064087 | 0.045776 | 123.0835 | -0.20599 | -0.14191 | -0.022889 | -0.09613 | -0.15564 | 0.054931 | -0.027466 | -0.28839 | -0.13275 | 0.01831 | 123.1613 | 123.0927 | 58.9737 | -123.1796 | 123.1705 | 123.1339 | 59.024 | -123.2712
248.6875 | 123.2071 | -59.1156 | 63.9816 | 0.29367 | 0.012985 | 0.062486 | 0.05258 | 0.11531 | -0.014399 | -0.007791 | 0.40644 | -0.0084822 | 0.086565 | 0.051831 | 0.012524 | 0.0067226 | 63.8901 | 64.0549 | -0.10071 | -59.3491 | 64.064 | -59.1431 | -59.198 | -59.111 | -0.086975 | -59.404 | 64.0503 | 64.0091 | -59.1934 | -59.2758 | -0.027465 | -0.082397 | 0.082398 | 123.1705 | -0.23346 | -0.15106 | -0.091552 | -0.077819 | -0.16022 | 0.068665 | 0.004578 | -0.28839 | -0.12817 | 0.027466 | 123.1796 | 123.0057 | 59.0149 | -123.1796 | 123.1659 | 123.1247 | 59.0286 | -123.2574
249.6875 | 123.2574 | -59.1019 | 63.9908 | 0.26315 | 0.046097 | 0.073167 | 0.080351 | 0.13881 | 0.00055539 | 0.00075395 | 0.498 | 0.0021988 | 0.072679 | 0.087078 | 0.0071838 | -0.0039584 | 64.0869 | 64.0686 | -0.11444 | -59.3124 | 64.0457 | -59.1431 | -59.1888 | -59.1248 | -0.086975 | -59.4315 | 64.0366 | 64.0137 | -59.198 | -59.2712 | -0.041198 | -0.086975 | 0.054931 | 123.1705 | -0.21057 | -0.1236 | 0.09613 | -0.09613 | -0.16937 | 0.045776 | -0.022888 | -0.32959 | -0.16022 | 0.022888 | 123.1476 | 123.1888 | 58.9874 | -123.1796 | 123.1384 | 123.1155 | 59.0149 | -123.262
250.6875 | 123.2162 | -59.1202 | 63.9999 | 0.049525 | 0.042892 | 0.06569 | 0.078214 | 0.13346 | 0.011236 | -0.0142 | 0.024973 | 0.0011308 | 0.069475 | 0.064648 | 0.0082518 | 0.0013826 | 63.9542 | 63.9999 | -0.09613 | -59.3491 | 64.0594 | -59.1385 | -59.1797 | -59.1339 | -0.073242 | -59.4452 | 64.0549 | 64.0228 | -59.1934 | -59.2758 | -0.018311 | -0.059509 | 0.059509 | 123.1201 | -0.22888 | -0.16937 | -0.045776 | -0.073242 | -0.15564 | 0.054932 | -0.013733 | -0.32501 | -0.16937 | 0.022888 | 123.1796 | 123.0743 | 59.024 | -123.1796 | 123.175 | 123.143 | 59.0469 | -123.2758
251.6875 | 123.1705 | -59.111 | 64.0091 | 0.11056 | 0.048233 | 0.069963 | 0.07501 | 0.12492 | 0.0016234 | -0.00031405 | 0.14704 | -0.0010052 | 0.09511 | 0.069989 | -0.0002932 | -0.0028904 | 63.9496 | 64.0091 | -0.073242 | -59.3262 | 64.0366 | -59.1385 | -59.1797 | -59.1476 | -0.050354 | -59.4406 | 64.064 | 64.0274 | -59.1843 | -59.2621 | -0.027466 | -0.068664 | 0.027466 | 123.1201 | -0.21515 | -0.14648 | -0.059509 | -0.073242 | -0.15106 | 0.054932 | -0.036621 | -0.32959 | -0.17853 | 0.018311 | 123.1476 | 123.0606 | 59.0378 | -123.1888 | 123.175 | 123.1384 | 59.0607 | -123.2712
252.6875 | 123.2117 | -59.1064 | 63.9862 | 0.26315 | 0.024734 | 0.062486 | 0.068601 | 0.12385 | 0.0091004 | -0.006723 | -0.036062 | -0.020231 | 0.068407 | 0.071057 | -0.0024292 | -0.0071624 | 63.8992 | 63.9725 | -0.12817 | -59.3491 | 64.032 | -59.1568 | -59.1888 | -59.0881 | -0.073242 | -59.3903 | 64.0823 | 64.032 | -59.198 | -59.2667 | -0.050354 | -0.082398 | 0.045776 | 123.0789 | -0.24262 | -0.16022 | -0.086975 | -0.091553 | -0.16022 | 0.09613 | 0.01831 | -0.28381 | -0.1236 | 0.045776 | 123.1384 | 123.0057 | 58.9783 | -123.175 | 123.1888 | 123.1384 | 59.0332 | -123.2529
253.6875 | 123.2803 | -59.0836 | 63.9771 | 0.24789 | 0.031143 | 0.061418 | 0.080351 | 0.12706 | -0.0047856 | -0.00245 | 0.34541 | 0.0032668 | 0.075884 | 0.073193 | -0.0077702 | 0.0013826 | 63.9542 | 63.9999 | -0.12817 | -59.3353 | 64.0228 | -59.1385 | -59.1568 | -59.0881 | -0.073242 | -59.404 | 64.032 | 64.0045 | -59.1934 | -59.2392 | -0.054932 | -0.073242 | 0.045776 | 123.0835 | -0.25177 | -0.17853 | -0.022888 | -0.10986 | -0.15564 | 0.054931 | -0.004578 | -0.32044 | -0.1648 | 0.027466 | 123.1064 | 123.0377 | 58.9554 | -123.1338 | 123.1155 | 123.0881 | 59.0103 | -123.2162
254.6875 | 123.2529 | -59.111 | 63.9679 | 0.3547 | 0.057846 | 0.076372 | 0.067533 | 0.12492 | 0.0026914 | -0.00245 | 0.33015 | -0.0031412 | 0.072679 | 0.065716 | 0.0029108 | 0.0013826 | 63.9587 | 64.0045 | -0.13733 | -59.3399 | 64.0366 | -59.1431 | -59.1843 | -59.111 | -0.059509 | -59.4269 | 64.0274 | 63.9816 | -59.1888 | -59.2758 | -0.032043 | -0.073242 | 0.068664 | 123.1155 | -0.22888 | -0.15564 | -0.009156 | -0.07782 | -0.16479 | 0.059509 | 0 | -0.31586 | -0.15106 | 0.013732 | 123.1476 | 123.0698 | 58.9737 | -123.1522 | 123.1384 | 123.0927 | 59.0515 | -123.2437
255.6875 | 123.2666 | -59.1339 | 63.9633 | 0.33944 | 0.02687 | 0.072099 | 0.080351 | 0.12492 | -0.00051261 | 0.00075395 | 0.26911 | 0.0064718 | 0.069475 | 0.064648 | -0.0013612 | -0.0071624 | 63.9313 | 63.9999 | -0.13733 | -59.3445 | 64.0366 | -59.1476 | -59.1888 | -59.1202 | -0.091553 | -59.404 | 64.0411 | 64.0045 | -59.1888 | -59.2438 | -0.013733 | -0.054932 | 0.073242 | 123.1338 | -0.21057 | -0.15564 | -0.032044 | -0.054932 | -0.10986 | 0.07782 | 0.013733 | -0.27008 | -0.16022 | 0.041199 | 123.1705 | 123.0652 | 58.9966 | -123.1522 | 123.175 | 123.1384 | 59.0424 | -123.2071
256.6875 | 123.2346 | -59.1202 | 63.9725 | -1.3848 | 0.034347 | 0.06569 | 0.064329 | 0.1356 | 0.0091004 | 0.00289 | 0.34541 | -0.0084822 | 0.079088 | 0.069989 | 0.0050478 | 0.0024506 | 63.9587 | 63.9816 | -0.14191 | -59.3399 | 64.0366 | -59.1522 | -59.1843 | -59.1156 | -0.10071 | -59.4315 | 64.0686 | 64.0182 | -59.1934 | -59.2896 | -0.032044 | -0.064087 | 0.064087 | 123.1018 | -0.21973 | -0.15564 | -0.013733 | -0.073242 | -0.16937 | 0.096131 | 0.004577 | -0.31128 | -0.14191 | 0.045777 | 123.1567 | 123.0789 | 58.9783 | -123.1567 | 123.1888 | 123.1384 | 59.0195 | -123.262
257.6875 | 123.2346 | -59.1202 | 63.9954 | 0.095301 | 0.041824 | 0.063554 | 0.081419 | 0.14201 | 0.0080314 | 0.001822 | 0.009715 | 0.0043348 | 0.08336 | 0.059307 | 0.0050478 | 0.0013826 | 63.9496 | 63.9999 | -0.09613 | -59.3308 | 64.0366 | -59.1431 | -59.198 | -59.1476 | -0.07782 | -59.4269 | 64.0503 | 64.0274 | -59.2117 | -59.2712 | -0.022888 | -0.07782 | 0.041199 | 123.1201 | -0.21057 | -0.13275 | -0.045776 | -0.091553 | -0.15106 | 0.054932 | -0.027466 | -0.3067 | -0.15564 | 0.032044 | 123.1567 | 123.0698 | 59.024 | -123.1934 | 123.1705 | 123.1476 | 59.0424 | -123.2666
258.6875 | 123.2391 | -59.0836 | 63.9816 | 0.33944 | 0.046097 | 0.064622 | 0.073942 | 0.13346 | 0.012304 | 0.003958 | 1.5661 | -0.0020732 | 0.070543 | 0.078533 | 0.0018428 | -0.0039584 | 63.913 | 63.9679 | -0.13275 | -59.3308 | 64.0137 | -59.1293 | -59.2072 | -59.0881 | -0.073242 | -59.4223 | 64.0778 | 64.0182 | -59.198 | -59.2667 | -0.045776 | -0.1236 | 0.032044 | 123.0515 | -0.24719 | -0.1236 | -0.068664 | -0.11444 | -0.18311 | 0.096131 | -0.004578 | -0.33875 | -0.15564 | 0.036622 | 123.0972 | 122.9965 | 58.9508 | -123.1888 | 123.1613 | 123.1018 | 59.0103 | -123.2483
259.6875 | 123.2483 | -59.111 | 63.9954 | 0.15634 | 0.024734 | 0.06569 | 0.073942 | 0.12172 | 0.016576 | 0.00289 | 0.25385 | 0.0021988 | 0.08336 | 0.058239 | 0.027478 | -0.0018224 | 63.9175 | 63.9633 | -0.14648 | -59.3491 | 64.0366 | -59.1522 | -59.2026 | -59.1614 | 0.24719 | -59.4223 | 64.0732 | 64.0411 | -59.1888 | -59.2484 | -0.041199 | -0.091553 | 0.041199 | 123.0743 | -0.23804 | -0.14648 | -0.077819 | -0.07782 | -0.13733 | 0.07782 | -0.050354 | -0.31128 | -0.17395 | 0.045777 | 123.1476 | 123.0286 | 58.9645 | -123.1979 | 123.1842 | 123.1522 | 59.3582 | -123.2437
260.6875 | 123.2529 | -59.1019 | 63.9771 | 0.40048 | 0.036484 | 0.06035 | 0.073942 | 0.12385 | -0.0069216 | -0.00245 | 0.26911 | 6.2833e-05 | 0.067339 | 0.059307 | 0.0018428 | -0.0071624 | 63.9267 | 63.9862 | -0.14648 | -59.3399 | 64.0228 | -59.1202 | -59.1843 | -59.0973 | -0.07782 | -59.4131 | 64.0366 | 64.0091 | -59.1843 | -59.2667 | -0.01831 | -0.082397 | 0.045776 | 123.0881 | -0.23804 | -0.15564 | -0.050354 | -0.082397 | -0.16479 | 0.059509 | 0.004578 | -0.31128 | -0.14648 | 0.032043 | 123.1247 | 123.0286 | 58.9554 | -123.1613 | 123.1384 | 123.111 | 59.024 | -123.2437
261.6875 | 123.23 | -59.1156 | 63.9771 | 1.6059 | 0.020462 | 0.072099 | 0.068601 | 0.12919 | 0.00055539 | -0.003518 | 0.20808 | 0.0021988 | 0.070543 | 0.067852 | -0.0024292 | 0.0013826 | 63.9313 | 63.9862 | -0.13733 | -59.3491 | 64.0503 | -59.1385 | -59.1797 | -59.0973 | -0.09613 | -59.4177 | 64.064 | 64.0182 | -59.1934 | -59.2712 | -0.022888 | -0.064086 | 0.073242 | 123.1018 | -0.23346 | -0.16937 | -0.045777 | -0.077819 | -0.15564 | 0.086975 | 0.018311 | -0.30212 | -0.14648 | 0.041199 | 123.1659 | 123.0469 | 58.9783 | -123.1567 | 123.1796 | 123.1339 | 59.0195 | -123.2483
262.6875 | 123.2529 | -59.1019 | 63.9954 | 7.7094 | 0.02687 | 0.078508 | 0.083555 | 0.14628 | -0.0015816 | 0.00289 | 0.14704 | -0.0052782 | 0.071611 | 0.058239 | -0.0024292 | -0.0018224 | 63.945 | 64.0594 | -0.09613 | -59.3445 | 64.0503 | -59.1431 | -59.1843 | -59.1202 | -0.068665 | -59.4177 | 64.0503 | 64.0091 | -59.198 | -59.285 | -0.041198 | -0.082397 | 0.054932 | 123.1613 | -0.24261 | -0.16022 | -0.050354 | -0.09613 | -0.1831 | 0.054932 | -0.01831 | -0.31586 | -0.13275 | 0.013733 | 123.1522 | 123.0469 | 59.0057 | -123.1796 | 123.1522 | 123.111 | 59.0332 | -123.2803
263.6875 | 123.2437 | -59.1202 | 63.9862 | 0.30892 | 0.03862 | 0.06569 | 0.078214 | 0.12278 | -0.0079896 | -0.015268 | 0.48274 | 0.010744 | 0.084429 | 0.056103 | 0.0050478 | -0.00075443 | 64.1006 | 64.0594 | -0.13733 | -59.3033 | 64.064 | -59.1293 | -59.2026 | -59.1156 | -0.07782 | -59.4315 | 64.0686 | 64.0182 | -59.198 | -59.2941 | -0.009155 | -0.082398 | 0.07782 | 123.1796 | -0.18311 | -0.10071 | 0.11444 | -0.07782 | -0.17395 | 0.082398 | 0.004577 | -0.31128 | -0.13733 | 0.032044 | 123.1842 | 123.2208 | 58.9828 | -123.1888 | 123.1888 | 123.1384 | 59.0424 | -123.2803
264.6875 | 123.23 | -59.1202 | 64.0274 | 0.12582 | 0.031143 | 0.064622 | 0.083555 | 0.12278 | 0.0048274 | -0.00245 | 0.009715 | 0.0032668 | 0.067339 | 0.062512 | 0.0039788 | -0.0071624 | 63.9404 | 64.0137 | -0.09613 | -59.3124 | 64.0366 | -59.1293 | -59.1843 | -59.1202 | -0.068665 | -59.4269 | 64.064 | 64.0228 | -59.1705 | -59.2392 | -0.009155 | -0.064087 | 0.009155 | 123.1338 | -0.19226 | -0.12817 | -0.086975 | -0.050354 | -0.11902 | 0.036621 | 0 | -0.3067 | -0.18768 | -0.004578 | 123.1567 | 123.0606 | 59.024 | -123.2117 | 123.1842 | 123.143 | 59.0515 | -123.2666
265.6875 | 123.2208 | -59.1339 | 63.9862 | 0.064784 | 0.06105 | 0.059282 | 0.054716 | 0.13453 | 0.0058954 | -0.003518 | 0.040232 | -0.0074142 | 0.088701 | 0.071057 | 0.0018428 | -0.0018224 | 63.9542 | 64.0411 | -0.073242 | -59.3216 | 64.0045 | -59.1248 | -59.1934 | -59.1202 | -0.045776 | -59.4269 | 64.0732 | 64.0137 | -59.1934 | -59.2758 | 0.009155 | -0.059509 | 0.018311 | 123.175 | -0.18768 | -0.12817 | -0.032043 | -0.059509 | -0.14191 | 0.086975 | 0.013733 | -0.29297 | -0.15106 | 0.027466 | 123.1384 | 123.0881 | 59.0607 | -123.1796 | 123.2071 | 123.1476 | 59.0881 | -123.262
266.6875 | 123.2071 | -59.111 | 63.9999 | 0.15634 | 0.024734 | 0.072099 | 0.078214 | 0.13774 | 0.011236 | -0.01954 | 3.8702 | 0.010744 | 0.070543 | 0.055035 | 0.010388 | 0.00031457 | 63.8947 | 63.9679 | -0.14191 | -59.3399 | 64.0411 | -59.1385 | -59.1751 | -59.1431 | -0.022888 | -59.4315 | 64.0778 | 64.0411 | -59.1843 | -59.2758 | -0.027466 | -0.064087 | 0.041199 | 123.0789 | -0.22888 | -0.1648 | -0.10529 | -0.073242 | -0.16479 | 0.07782 | -0.032043 | -0.32043 | -0.15564 | 0.041199 | 123.1522 | 123.0057 | 58.9691 | -123.175 | 123.1888 | 123.1522 | 59.0881 | -123.2758
267.6875 | 123.2117 | -59.1064 | 63.9725 | 0.36996 | 0.058914 | 0.062486 | 0.088896 | 0.13774 | 0.0016234 | -0.006723 | 0.29963 | -0.0042092 | 0.063066 | 0.047558 | 0.011456 | 0.0024506 | 63.9359 | 63.9954 | -0.12817 | -59.3445 | 64.032 | -59.1339 | -59.1751 | -59.0927 | -0.09613 | -59.404 | 64.0366 | 64.0045 | -59.198 | -59.2667 | -0.027466 | -0.068665 | 0.059509 | 123.1018 | -0.23804 | -0.16937 | -0.036621 | -0.091553 | -0.16022 | 0.064087 | 0.013733 | -0.29755 | -0.13733 | 0.032044 | 123.1384 | 123.0423 | 58.9783 | -123.1476 | 123.143 | 123.111 | 59.0103 | -123.2391
268.6875 | 123.2391 | -59.1385 | 63.9587 | 0.49203 | 0.031143 | 0.063554 | 0.071806 | 0.12812 | -0.0015816 | 0.005026 | 0.29963 | -0.0010052 | 0.075884 | 0.065716 | -0.0067022 | -0.0028904 | 63.9404 | 63.9816 | -0.14191 | -59.3262 | 64.0182 | -59.1522 | -59.2117 | -59.1064 | -0.09613 | -59.4131 | 64.0457 | 64.0045 | -59.1705 | -59.2529 | -0.013733 | -0.073242 | 0.05951 | 123.1201 | -0.18768 | -0.11444 | -0.01831 | -0.032043 | -0.11444 | 0.086975 | 0.032044 | -0.27466 | -0.16022 | 0.045777 | 123.1567 | 123.0789 | 58.9966 | -123.1705 | 123.1842 | 123.143 | 59.0424 | -123.2117
269.6875 | 123.1979 | -59.1202 | 63.9908 | 1.377 | 0.036484 | 0.055009 | 0.077146 | 0.1356 | -0.00051261 | -0.012063 | 0.28437 | -0.0042092 | 0.091905 | 0.062512 | 0.0007748 | 0.00031457 | 63.9221 | 63.9816 | -0.13733 | -59.3353 | 64.0411 | -59.1522 | -59.1751 | -59.111 | -0.082397 | -59.404 | 64.0594 | 64.0091 | -59.1934 | -59.2758 | -0.032044 | -0.054932 | 0.050354 | 123.1018 | -0.21515 | -0.16022 | -0.068665 | -0.073242 | -0.15564 | 0.068664 | 0.009155 | -0.28381 | -0.12817 | 0.01831 | 123.1613 | 123.0423 | 58.9828 | -123.1659 | 123.1796 | 123.1293 | 59.0378 | -123.2666
270.6875 | 123.2254 | -59.1476 | 63.9771 | 0.23263 | 0.050369 | 0.068895 | 0.082487 | 0.13453 | 0.0069634 | -0.00031405 | 0.52851 | -0.0020732 | 0.088701 | 0.047558 | -0.0034972 | -0.011435 | 63.913 | 64.0228 | -0.13275 | -59.317 | 64.0594 | -59.1385 | -59.1705 | -59.1248 | -0.10071 | -59.4086 | 64.0549 | 63.9816 | -59.2026 | -59.2758 | 0.009155 | -0.022888 | 0.082397 | 123.1705 | -0.16937 | -0.14648 | -0.064087 | -0.054932 | -0.12817 | 0.07782 | 0.022888 | -0.26093 | -0.13275 | 0.004577 | 123.2071 | 123.0606 | 59.0149 | -123.1476 | 123.2025 | 123.1293 | 59.0469 | -123.2529
271.6875 | 123.1796 | -59.111 | 63.9908 | 0.11056 | 0.046097 | 0.064622 | 0.078214 | 0.13667 | 0.0080314 | 0.010367 | 0.11653 | -0.0020732 | 0.074815 | 0.050762 | 0.0007748 | -0.0082304 | 63.9496 | 64.0137 | -0.09613 | -59.3262 | 64.0137 | -59.1248 | -59.2026 | -59.1339 | -0.041199 | -59.4269 | 64.064 | 63.9999 | -59.1888 | -59.2621 | -0.013733 | -0.091553 | 0.022888 | 123.1247 | -0.21515 | -0.1236 | -0.041199 | -0.07782 | -0.15106 | 0.073242 | -0.022888 | -0.31586 | -0.16479 | 0.009155 | 123.1247 | 123.0606 | 59.0149 | -123.1934 | 123.175 | 123.111 | 59.0698 | -123.2529
272.6875 | 123.1979 | -59.079 | 64.0137 | 0.034266 | 0.034347 | 0.053941 | 0.066465 | 0.12385 | 0.0091004 | -0.005655 | 0.055491 | 0.0086078 | 0.087633 | 0.051831 | 0.0061158 | 0.0067226 | 63.9496 | 64.0411 | -0.082397 | -59.3262 | 64.0274 | -59.1156 | -59.1888 | -59.1248 | -0.050354 | -59.4131 | 64.0549 | 64.0091 | -59.1934 | -59.2712 | -0.036622 | -0.10986 | 0.013733 | 123.1201 | -0.24719 | -0.13733 | -0.064087 | -0.11444 | -0.19226 | 0.041199 | -0.045777 | -0.33417 | -0.14191 | -0.004578 | 123.1064 | 123.0286 | 58.9966 | -123.2025 | 123.1338 | 123.0881 | 59.0286 | -123.2849
273.6875 | 123.2758 | -59.1202 | 63.945 | 0.44625 | 0.05571 | 0.056077 | 0.079283 | 0.12065 | -0.0079896 | -0.012063 | 0.29963 | 0.0043348 | 0.068407 | 0.06892 | -0.0067022 | -0.00075443 | 63.9038 | 64.0091 | -0.1236 | -59.3262 | 64.0503 | -59.1431 | -59.166 | -59.1156 | -0.07782 | -59.4177 | 64.0411 | 63.9771 | -59.1888 | -59.2896 | -0.022888 | -0.045777 | 0.10529 | 123.1293 | -0.20599 | -0.16022 | -0.041198 | -0.068665 | -0.16937 | 0.096131 | 0.004577 | -0.29755 | -0.12817 | 0.032044 | 123.1705 | 123.024 | 58.9966 | -123.111 | 123.1613 | 123.0972 | 59.0424 | -123.2346
274.6875 | 123.3215 | -59.079 | 63.9679 | 0.431 | 0.010849 | 0.06035 | 0.080351 | 0.12599 | 0.00055539 | -0.008859 | 0.31489 | -0.0031412 | 0.074815 | 0.056103 | 0.0018428 | -0.017843 | 63.945 | 64.0457 | -0.1236 | -59.3262 | 64.032 | -59.1476 | -59.2072 | -59.0469 | -0.018311 | -59.3491 | 64.0182 | 63.9679 | -59.198 | -59.2621 | -0.068665 | -0.12817 | 0.064086 | 123.1247 | -0.24719 | -0.11902 | -0.022889 | -0.11902 | -0.18311 | 0.050354 | 0.032043 | -0.27008 | -0.086975 | 0 | 123.111 | 123.024 | 58.9554 | -123.175 | 123.0972 | 123.0469 | 59.0607 | -123.23
275.6875 | 123.2391 | -59.1156 | 63.9908 | 3.7422 | 0.071731 | 0.084917 | 0.061125 | 0.1356 | 0.012304 | 0.00075395 | 0.26911 | 0.0043348 | 0.076952 | 0.056103 | 0.0071838 | -0.012503 | 63.9359 | 64.032 | -0.10986 | -59.3445 | 64.0594 | -59.1385 | -59.1705 | -59.1202 | -0.07782 | -59.4315 | 64.0549 | 64.0228 | -59.2163 | -59.2484 | -0.022888 | -0.054931 | 0.068664 | 123.1476 | -0.22888 | -0.17395 | -0.054932 | -0.10071 | -0.13275 | 0.064087 | -0.004577 | -0.31586 | -0.18311 | 0.032043 | 123.175 | 123.0515 | 59.0057 | -123.1613 | 123.1705 | 123.1384 | 59.0378 | -123.2391
276.6875 | 123.2254 | -59.1293 | 63.9908 | 0.27841 | 0.051437 | 0.06569 | 0.071806 | 0.12385 | 0.0026914 | 0.03707 | -0.90581 | 0.0032668 | 0.069475 | 0.083874 | 0.0039788 | -0.0018224 | 63.7115 | 63.9221 | -0.036621 | -59.23 | 64.0457 | -59.1156 | -59.1843 | -59.1339 | -0.086975 | -59.4131 | 64.0915 | 64.0045 | -59.2026 | -59.2987 | 0.013732 | -0.054932 | 0.054931 | 123.0515 | -0.10071 | -0.045777 | -0.27924 | -0.073243 | -0.16937 | 0.10071 | -0.004578 | -0.28381 | -0.11444 | 0.013733 | 123.175 | 122.8409 | 59.0927 | -123.175 | 123.2208 | 123.1339 | 59.0424 | -123.2895
277.6875 | 123.2483 | -59.1293 | 63.9816 | 0.20211 | 0.036484 | 0.061418 | 0.068601 | 0.12919 | 0.0080314 | -0.003518 | 0.36067 | -0.0052782 | 0.081224 | 0.049694 | 0.0029108 | -0.0060944 | 63.9175 | 63.9633 | -0.13733 | -59.3582 | 64.0411 | -59.1385 | -59.198 | -59.0927 | -0.054932 | -59.4086 | 64.0915 | 64.032 | -59.1797 | -59.2896 | -0.009156 | -0.068665 | 0.05951 | 123.0927 | -0.22888 | -0.16022 | -0.064086 | -0.050354 | -0.16022 | 0.10986 | 0.036621 | -0.27924 | -0.11902 | 0.050354 | 123.1705 | 123.0469 | 58.992 | -123.1796 | 123.2208 | 123.1613 | 59.0744 | -123.2712
278.6875 | 123.23 | -59.1202 | 64.0091 | -0.057287 | 0.047165 | 0.059282 | 0.078214 | 0.13881 | 0.0058954 | 0.001822 | 0.009715 | 0.0043348 | 0.069475 | 0.059307 | 0.0071838 | -0.0071624 | 63.9633 | 64.0457 | -0.059509 | -59.3079 | 64.0457 | -59.1339 | -59.166 | -59.1202 | -0.036621 | -59.4177 | 64.0549 | 64.0228 | -59.1705 | -59.2758 | -0.013733 | -0.045777 | 0.036621 | 123.1659 | -0.18768 | -0.14191 | -0.045776 | -0.050354 | -0.15564 | 0.045777 | 0 | -0.29755 | -0.14191 | 0.013733 | 123.1659 | 123.0835 | 59.0607 | -123.175 | 123.175 | 123.143 | 59.0836 | -123.2849
279.6875 | 123.3307 | -59.1385 | 63.9999 | 0.23263 | 0.035415 | 0.08278 | 0.060057 | 0.13667 | -0.00051261 | -0.00031405 | 0.17756 | 0.0032668 | 0.082292 | 0.052899 | 0.011456 | -0.0039584 | 63.913 | 63.9771 | -0.13733 | -59.3308 | 64.032 | -59.1476 | -59.1797 | -59.1293 | -0.064087 | -59.4269 | 64.0457 | 64.0228 | -59.2209 | -59.3124 | -0.009155 | -0.041198 | 0.032043 | 123.1155 | -0.19226 | -0.15106 | -0.086975 | -0.082397 | -0.17395 | 0.045776 | 0.009156 | -0.28839 | -0.11444 | 0.022888 | 123.1705 | 123.0515 | 59.0012 | -123.1796 | 123.1842 | 123.1613 | 59.0744 | -123.3124
280.6875 | 123.2346 | -59.1248 | 63.9862 | 3.7269 | 0.014053 | 0.075304 | 0.081419 | 0.13667 | -0.020808 | -0.006723 | 0.29963 | -0.0010052 | 0.071611 | 0.052899 | -0.0034972 | 0.0035186 | 63.9084 | 64.0411 | -0.10071 | -59.3399 | 64.032 | -59.111 | -59.1934 | -59.111 | -0.07782 | -59.4086 | 64.0411 | 63.9908 | -59.2026 | -59.2941 | 0.013733 | -0.068664 | 0.045776 | 123.1659 | -0.21515 | -0.14648 | -0.07782 | -0.07782 | -0.16937 | 0.054932 | 0.013733 | -0.28381 | -0.11444 | 0.004578 | 123.1567 | 123.0331 | 59.024 | -123.1796 | 123.1659 | 123.1155 | 59.0469 | -123.2803
281.6875 | 123.2391 | -59.1156 | 63.9771 | 0.33944 | 0.016189 | 0.062486 | 0.07501 | 0.12492 | 0.035802 | 0.012503 | 0.086009 | -0.0031412 | 0.079088 | 0.061444 | 0.0050478 | 0.0024506 | 63.6108 | 64.3204 | 0.022888 | -59.3079 | 64.032 | -59.1568 | -59.1705 | -59.1248 | -0.091553 | -59.3994 | 64.0594 | 63.9999 | -59.198 | -59.2758 | -0.041198 | -0.054931 | 0.054931 | 123.436 | -0.19226 | -0.13733 | -0.36621 | -0.082397 | -0.16022 | 0.082397 | -0.009155 | -0.28381 | -0.1236 | 0.022888 | 123.1476 | 122.7264 | 59.1385 | -123.1476 | 123.175 | 123.1155 | 59.024 | -123.2529
282.6875 | 123.2254 | -59.1248 | 64.0091 | 0.24789 | 0.045028 | 0.072099 | 0.067533 | 0.11958 | -0.0037176 | 0.001822 | -2.2791 | 0.0021988 | 0.057726 | 0.059307 | 0.011456 | -0.011435 | 63.9221 | 63.9542 | -0.1236 | -59.3445 | 64.032 | -59.1522 | -59.198 | -59.0973 | -0.036621 | -59.4086 | 64.0594 | 64.0457 | -59.1888 | -59.2667 | -0.027466 | -0.073242 | 0.022888 | 123.0789 | -0.21973 | -0.14648 | -0.086975 | -0.064087 | -0.14191 | 0.050354 | 0.027466 | -0.28381 | -0.14191 | 0.036621 | 123.1567 | 123.0469 | 59.0012 | -123.2071 | 123.1842 | 123.1705 | 59.0881 | -123.2758
283.6875 | 123.1934 | -59.111 | 63.9862 | 0.32418 | 0.046097 | 0.069963 | 0.072874 | 0.12812 | -0.0069216 | 0.00075395 | 0.19282 | 0.0064718 | 0.071611 | 0.06358 | 0.016797 | -0.0071624 | 63.9221 | 63.9633 | -0.14648 | -59.3353 | 64.0411 | -59.1385 | -59.198 | -59.2346 | -0.37079 | -59.2117 | 64.0274 | 64.0045 | -59.1843 | -59.23 | -0.027466 | -0.086975 | 0.054932 | 123.0743 | -0.2243 | -0.13733 | -0.064087 | -0.073242 | -0.11902 | 0.041199 | -0.1236 | -0.10071 | 0.018311 | 0.018311 | 123.1522 | 123.0331 | 58.9645 | -123.1842 | 123.1384 | 123.1155 | 58.7402 | -123.2162
284.6875 | 123.0194 | -59.1476 | 63.9267 | 0.18685 | 0.067459 | 0.076372 | 0.073942 | 0.12919 | 0.0048274 | -0.004587 | 0.055491 | 0.0086078 | 0.066271 | 0.06358 | 0.0050478 | -0.0060944 | 63.9221 | 63.9771 | -0.11444 | -59.3445 | 64.032 | -59.1248 | -59.2117 | -59.1522 | -0.10071 | -59.4315 | 64.0411 | 63.9999 | -59.1934 | -59.2712 | 0.022888 | -0.064087 | 0.10529 | 123.1247 | -0.19684 | -0.13275 | -0.004578 | -0.045776 | -0.1236 | 0.11444 | -0.004578 | -0.28381 | -0.16022 | 0.073242 | 123.1796 | 123.0698 | 59.0332 | -123.1384 | 123.1888 | 123.1476 | 59.0469 | -123.1979
285.6875 | 123.2529 | -59.0973 | 63.9725 | -0.042028 | 0.036484 | 0.063554 | 0.080351 | 0.13346 | 0.010168 | -0.005655 | -0.097097 | -0.0052782 | 0.084429 | 0.06358 | 0.011456 | -0.011435 | 63.9999 | 64.0778 | -0.041199 | -59.2987 | 64.032 | -59.1064 | -59.166 | -59.0836 | 0 | -59.3811 | 64.0778 | 64.0228 | -59.1934 | -59.2804 | -0.009155 | -0.068665 | 0.059509 | 123.175 | -0.20142 | -0.13275 | 0.027466 | -0.09613 | -0.18311 | 0.10529 | 0.013733 | -0.28381 | -0.10071 | 0.050354 | 123.1293 | 123.0972 | 59.0561 | -123.1384 | 123.175 | 123.1201 | 59.0973 | -123.2529
286.6875 | 123.1979 | -59.0881 | 63.9999 | 0.049525 | 0.041824 | 0.056077 | 0.072874 | 0.12706 | 0.00055539 | -0.008859 | 0.040232 | -0.0042092 | 0.079088 | 0.057171 | 0.0029108 | -0.0028904 | 63.9542 | 64.0182 | -0.082397 | -59.3353 | 64.0411 | -59.1248 | -59.1843 | -59.1339 | -0.068665 | -59.4131 | 64.064 | 64.032 | -59.1934 | -59.2758 | -0.036621 | -0.09613 | 0.041199 | 123.1064 | -0.24719 | -0.15106 | -0.045776 | -0.10529 | -0.18768 | 0.064087 | -0.045776 | -0.32501 | -0.13733 | 0.032043 | 123.1293 | 123.0423 | 59.0057 | -123.1842 | 123.1522 | 123.1201 | 59.0195 | -123.2758
287.6875 | 123.2117 | -59.1019 | 63.9816 | 0.29367 | 0.040756 | 0.074235 | 0.066465 | 0.12919 | 0.0048274 | -0.009927 | 3.1072 | -0.0042092 | 0.064134 | 0.06358 | -0.0045652 | -0.0028904 | 63.913 | 63.9496 | -0.14648 | -59.3399 | 64.0457 | -59.166 | -59.1934 | -59.0836 | -0.10529 | -59.3765 | 64.0961 | 64.0594 | -59.2072 | -59.2529 | -0.064087 | -0.091552 | 0.064087 | 123.0515 | -0.23804 | -0.14648 | -0.068664 | -0.10528 | -0.15106 | 0.11444 | 0.018311 | -0.27466 | -0.1236 | 0.07782 | 123.1476 | 123.0148 | 58.9554 | -123.175 | 123.1979 | 123.1613 | 58.9966 | -123.2346
288.6875 | 123.2254 | -59.0881 | 64.0091 | 0.27841 | 0.042892 | 0.066759 | 0.083555 | 0.11424 | -0.00051261 | -0.003518 | 0.14704 | 6.2833e-05 | 0.074815 | 0.064648 | -0.0013612 | -0.0050264 | 63.9313 | 63.9587 | -0.1236 | -59.3399 | 64.0411 | -59.1339 | -59.2163 | -59.1248 | -0.38452 | -59.6237 | 63.9908 | 63.9633 | -59.2117 | -59.2758 | -0.045776 | -0.12817 | 0.032044 | 123.0469 | -0.25177 | -0.1236 | -0.07782 | -0.1236 | -0.18768 | -0.01831 | -0.036621 | -0.53558 | -0.3479 | -0.045776 | 123.1293 | 123.0194 | 58.9645 | -123.2254 | 123.0789 | 123.0515 | 58.7036 | -123.2849
289.6875 | 123.3032 | -59.1431 | 63.9587 | 0.12582 | 0.014053 | 0.057146 | 0.071806 | 0.12599 | 0.010168 | -0.007791 | 0.22334 | -0.010618 | 0.069475 | 0.056103 | 0.0082518 | -0.0039584 | 63.9221 | 63.9908 | -0.11444 | -59.3399 | 64.0457 | -59.1385 | -59.2026 | -59.1476 | -0.082397 | -59.4406 | 64.0457 | 64.0228 | -59.1797 | -59.2667 | 0.004577 | -0.05951 | 0.086975 | 123.1338 | -0.19684 | -0.13733 | -0.036621 | -0.036621 | -0.1236 | 0.086975 | -0.004578 | -0.29755 | -0.17395 | 0.064087 | 123.1888 | 123.0652 | 59.0286 | -123.1613 | 123.1888 | 123.1659 | 59.0607 | -123.2254
290.6875 | 123.2117 | -59.1202 | 64.0137 | 5.4817 | 0.058914 | 0.09453 | 0.078214 | 0.14094 | -0.0069216 | 0.001822 | 0.25385 | 0.0021988 | 0.073747 | 0.050762 | 0.0071838 | 0.0056546 | 63.9587 | 64.0274 | -0.10529 | -59.3262 | 64.0594 | -59.111 | -59.1843 | -59.1248 | -0.073242 | -59.4223 | 64.0549 | 64.0182 | -59.198 | -59.285 | 0.009155 | -0.064087 | 0.045776 | 123.1476 | -0.20599 | -0.14191 | -0.054932 | -0.07782 | -0.16479 | 0.041199 | -0.004578 | -0.30212 | -0.13733 | 0.004578 | 123.1796 | 123.0789 | 59.0149 | -123.1979 | 123.175 | 123.1384 | 59.0469 | -123.2986
291.6875 | 123.2117 | -59.0881 | 63.9771 | -0.10306 | 0.050369 | 0.064622 | 0.086759 | 0.12492 | 0.0058954 | -0.00031405 | -0.036062 | 0.0086078 | 0.067339 | 0.066784 | 0.0050478 | -0.0060944 | 64.0045 | 64.0823 | -0.036621 | -59.2987 | 64.0503 | -59.1339 | -59.166 | -59.0652 | 0 | -59.3857 | 64.0732 | 64.0274 | -59.198 | -59.2667 | -0.045776 | -0.07782 | 0.073242 | 123.1705 | -0.21057 | -0.13275 | 0.027466 | -0.10986 | -0.17853 | 0.09613 | 0.022888 | -0.29755 | -0.11902 | 0.050354 | 123.1384 | 123.0927 | 59.0515 | -123.143 | 123.1613 | 123.1155 | 59.0881 | -123.2437
292.6875 | 123.2208 | -59.0973 | 63.9862 | -0.072545 | 0.051437 | 0.064622 | 0.06967 | 0.12919 | -0.00051261 | -0.00031405 | -0.11236 | -0.0020732 | 0.071611 | 0.064648 | 0.0029108 | -0.011435 | 64.0045 | 64.0686 | -0.018311 | -59.2987 | 64.0503 | -59.0973 | -59.1614 | -59.0744 | 0.022888 | -59.3719 | 64.0457 | 64.0045 | -59.1888 | -59.23 | 0 | -0.064087 | 0.064087 | 123.1659 | -0.20142 | -0.13733 | 0.018311 | -0.091553 | -0.13275 | 0.059509 | 0.022888 | -0.27466 | -0.14191 | 0.018311 | 123.1476 | 123.1018 | 59.079 | -123.1476 | 123.143 | 123.1018 | 59.1202 | -123.2162
293.7031 | 123.3353 | -59.0424 | 63.9862 | -0.057287 | -0.019058 | 0.083848 | 0.070738 | 0.12812 | -0.037898 | -0.016336 | 0.13178 | -0.018095 | 0.056658 | 0.052899 | -0.0045652 | -0.0092984 | 63.9725 | 64.1281 | 0.032043 | -59.2392 | 63.9908 | -59.0973 | -59.1476 | -59.0057 | 0.1236 | -59.2575 | 64.0503 | 63.9816 | -59.166 | -59.2117 | -0.054932 | -0.10529 | 0.004578 | 123.1705 | -0.19684 | -0.091553 | -0.013733 | -0.1236 | -0.16937 | 0.064087 | 0.036621 | -0.21515 | -0.045776 | -0.004578 | 123.0331 | 123.0148 | 59.0744 | -123.1338 | 123.0927 | 123.024 | 59.166 | -123.1979
294.6875 | 123.2117 | -59.1293 | 63.9862 | 0.18685 | 0.020462 | 0.080644 | 0.085691 | 0.14201 | 0.01444 | -0.006723 | 6.7999 | -0.010618 | 0.080156 | 0.052899 | 0.0082518 | -0.011435 | 63.9038 | 63.9862 | -0.13275 | -59.3719 | 64.0549 | -59.1202 | -59.1797 | -59.1156 | -0.054932 | -59.4223 | 64.0823 | 64.0228 | -59.2026 | -59.2758 | 0.009155 | -0.050354 | 0.068665 | 123.1155 | -0.24262 | -0.19226 | -0.082397 | -0.073243 | -0.14648 | 0.09613 | 0.013732 | -0.29297 | -0.14648 | 0.036621 | 123.1842 | 123.0331 | 58.9966 | -123.1659 | 123.2117 | 123.1522 | 59.0744 | -123.262
295.6875 | 123.2346 | -59.0973 | 64.0045 | 0.18685 | 0.056778 | 0.074235 | 0.083555 | 0.12278 | 0.0037594 | -0.00031405 | 0.25385 | 0.0021988 | 0.064134 | 0.065716 | -0.0099062 | -0.010367 | 63.9038 | 63.9725 | -0.13733 | -59.3445 | 64.032 | -59.1431 | -59.1797 | -58.9783 | -0.10529 | -59.404 | 64.0823 | 64.0366 | -59.1934 | -59.2438 | -0.045776 | -0.082397 | 0.027465 | 123.0698 | -0.24719 | -0.16479 | -0.10071 | -0.09613 | -0.14648 | 0.077819 | 0.11902 | -0.3067 | -0.16022 | 0.032043 | 123.1293 | 123.0011 | 58.96 | -123.1842 | 123.1796 | 123.1338 | 58.992 | -123.2483
296.6875 | 123.2346 | -59.0927 | 64.0274 | 0.095301 | 0.025802 | 0.063554 | 0.07501 | 0.12919 | 0.012304 | -0.001382 | 0.22334 | -0.0063462 | 0.086565 | 0.055035 | 0.013592 | 0.0088586 | 63.9359 | 63.9771 | -0.14191 | -59.3445 | 64.0503 | -59.1431 | -59.1751 | -59.3033 | 0.1831 | -59.3033 | 64.064 | 64.0274 | -59.2026 | -59.2575 | -0.050354 | -0.082398 | 0.022888 | 123.0698 | -0.25177 | -0.16937 | -0.091553 | -0.10986 | -0.16479 | 0.036621 | -0.21057 | -0.21057 | -0.045777 | 0 | 123.143 | 123.0286 | 58.9508 | -123.2025 | 123.1567 | 123.1201 | 59.2758 | -123.2849
297.6875 | 123.2483 | -59.1019 | 63.9908 | 0.23263 | 0.039688 | 0.062486 | 0.076078 | 0.1121 | 0.011236 | 0.006095 | 0.20808 | 0.0032668 | 0.075884 | 0.060376 | 0.020001 | 0.0024506 | 63.9404 | 63.9633 | -0.12817 | -59.3491 | 64.0411 | -59.1522 | -59.1751 | -59.111 | -0.032043 | -59.7015 | 64.0137 | 63.9359 | -59.2255 | -59.2896 | -0.050354 | -0.073242 | 0.050354 | 123.0652 | -0.24719 | -0.17395 | -0.050354 | -0.1236 | -0.18768 | 0.022888 | -0.009155 | -0.59967 | -0.41199 | -0.054932 | 123.143 | 123.0423 | 58.9737 | -123.1659 | 123.1155 | 123.0377 | 59.0698 | -123.2803
298.7031 | 123.3398 | -59.0561 | 63.9725 | 0.049525 | 0.009781 | 0.036851 | 0.061125 | 0.13026 | -0.047511 | -0.0142 | 0.19282 | -0.011686 | 0.070543 | 0.051831 | -0.019519 | -0.0050264 | 63.9587 | 64.0961 | 0.004578 | -59.2804 | 64.0045 | -59.1339 | -59.1339 | -59.0469 | 0.086975 | -59.2896 | 64.0274 | 63.9908 | -59.1431 | -59.2438 | -0.07782 | -0.07782 | 0.032044 | 123.1522 | -0.22431 | -0.14649 | -0.013733 | -0.086975 | -0.18768 | 0.054932 | 0.009155 | -0.23346 | -0.045777 | 0.018311 | 123.0606 | 123.0148 | 59.0607 | -123.1064 | 123.0835 | 123.0469 | 59.1431 | -123.2162
299.6875 | 123.1888 | -59.1064 | 64.0091 | 0.019007 | 0.040756 | 0.059282 | 0.072874 | 0.12599 | 0.021917 | -0.001382 | 0.024973 | -0.0020732 | 0.072679 | 0.056103 | 0.016797 | -0.015707 | 63.9908 | 64.0503 | -0.032043 | -59.3124 | 64.0503 | -59.1019 | -59.1888 | -59.1064 | -0.004578 | -59.3948 | 64.0869 | 63.9999 | -59.2209 | -59.2758 | 0.004577 | -0.082398 | 0.041199 | 123.1567 | -0.20599 | -0.1236 | -0.01831 | -0.11444 | -0.16937 | 0.07782 | 0 | -0.28839 | -0.11902 | -0.009155 | 123.1567 | 123.0972 | 59.0744 | -123.1979 | 123.1934 | 123.1064 | 59.1019 | -123.2849
300.6875 | 123.1796 | -59.1156 | 63.9954 | 0.15634 | 0.036484 | 0.063554 | 0.082487 | 0.13133 | 0.016576 | -0.006723 | 0.10127 | -0.012754 | 0.070543 | 0.065716 | 0.011456 | -0.010367 | 63.9221 | 64.0182 | -0.13275 | -59.3399 | 64.0228 | -59.1614 | -59.1843 | -59.1293 | -0.082397 | -59.436 | 64.0686 | 63.9954 | -59.1934 | -59.2896 | -0.045776 | -0.068664 | 0.027466 | 123.1339 | -0.2243 | -0.15564 | -0.073242 | -0.077819 | -0.17395 | 0.073243 | -0.013732 | -0.32043 | -0.14648 | 0 | 123.1384 | 123.0377 | 58.9828 | -123.1796 | 123.1842 | 123.111 | 59.0332 | -123.2849
301.6875 | 123.2254 | -59.1293 | 63.9954 | 0.38522 | 0.046097 | 0.059282 | 0.082487 | 0.13453 | 0.0037594 | -0.004587 | 0.48274 | -0.0042092 | 0.075884 | 0.059307 | -0.0013612 | 0.0035186 | 63.9038 | 64.0366 | -0.13275 | -59.317 | 64.0778 | -59.1248 | -59.1934 | -59.0973 | -0.09613 | -59.404 | 64.0732 | 63.9908 | -59.1797 | -59.2804 | 0.004577 | -0.064087 | 0.082398 | 123.1659 | -0.18768 | -0.1236 | -0.091552 | -0.050354 | -0.15106 | 0.07782 | 0.032043 | -0.27466 | -0.1236 | -0.004577 | 123.2071 | 123.0331 | 58.9966 | -123.1888 | 123.2025 | 123.1201 | 59.0332 | -123.2758
302.6875 | 123.2117 | -59.0973 | 63.9862 | 0.29367 | 0.031143 | 0.061418 | 0.086759 | 0.13774 | 0.020849 | 0.008231 | -0.41753 | -0.0020732 | 0.074815 | 0.064648 | -0.0002932 | 0.0045866 | 63.588 | 64.3478 | 0.036621 | -59.3124 | 64.0457 | -59.1431 | -59.1934 | -59.1064 | -0.082397 | -59.4315 | 64.0457 | 63.9862 | -59.2026 | -59.2346 | -0.045776 | -0.09613 | 0.059509 | 123.4451 | -0.21515 | -0.11902 | -0.39825 | -0.10529 | -0.13733 | 0.059509 | -0.009155 | -0.33417 | -0.19684 | 0 | 123.143 | 122.6852 | 59.1339 | -123.1796 | 123.143 | 123.0835 | 59.0149 | -123.2208
303.7031 | 123.3444 | -59.0424 | 63.9679 | -0.10306 | 0.006576 | 0.087053 | 0.056852 | 0.12278 | -0.037898 | -0.012063 | 0.055491 | -0.0063462 | 0.066271 | 0.06358 | -0.0067022 | -0.0018224 | 63.9771 | 64.1785 | 0.045776 | -59.2438 | 64.0045 | -59.111 | -59.1522 | -58.992 | 0.14191 | -59.2484 | 64.0274 | 63.9954 | -59.1522 | -59.2026 | -0.068665 | -0.10986 | 0.036621 | 123.2208 | -0.20142 | -0.091552 | 0.009155 | -0.10986 | -0.16022 | 0.059509 | 0.050354 | -0.20599 | -0.045776 | 0.027465 | 123.0469 | 123.0194 | 59.0881 | -123.1201 | 123.0698 | 123.0377 | 59.1843 | -123.1705
304.6875 | 123.2437 | -59.111 | 64.0137 | 0.29367 | 0.015121 | 0.058214 | 0.083555 | 0.12278 | 0.01444 | -0.009927 | 0.26911 | -0.0020732 | 0.072679 | 0.095623 | 0.015729 | -0.018912 | 63.9359 | 63.9954 | -0.13733 | -59.3399 | 64.0457 | -59.1339 | -59.2163 | -59.1339 | 0.16937 | -59.4177 | 64.0915 | 64.0091 | -59.166 | -59.2575 | -0.022888 | -0.10529 | 0.032043 | 123.1064 | -0.22888 | -0.1236 | -0.07782 | -0.054932 | -0.14648 | 0.07782 | -0.022888 | -0.3067 | -0.16022 | -0.004578 | 123.1567 | 123.0469 | 58.9737 | -123.23 | 123.2025 | 123.1201 | 59.2804 | -123.2712
305.6875 | 123.2025 | -59.1156 | 63.9954 | 0.049525 | 0.023666 | 0.057146 | 0.076078 | 0.13881 | 0.013372 | -0.007791 | -0.066579 | 0.0032668 | 0.072679 | 0.061444 | 0.010388 | -0.0071624 | 63.9725 | 64.0366 | -0.068665 | -59.317 | 64.032 | -59.1522 | -59.1751 | -59.1202 | -0.059509 | -59.4406 | 64.0732 | 64.0228 | -59.1888 | -59.2667 | -0.036621 | -0.059509 | 0.036621 | 123.1522 | -0.20142 | -0.14191 | -0.022888 | -0.073242 | -0.15106 | 0.07782 | -0.004577 | -0.32501 | -0.17395 | 0.027466 | 123.1476 | 123.0881 | 59.0469 | -123.1705 | 123.1888 | 123.1384 | 59.0561 | -123.262
306.6875 | 123.1979 | -59.1019 | 63.9542 | 0.24789 | 0.027939 | 0.071031 | 0.07501 | 0.12919 | 0.015508 | -0.001382 | 0.26911 | -0.0031412 | 0.071611 | 0.061444 | 0.010388 | -0.0039584 | 63.9267 | 63.9542 | -0.11902 | -59.3445 | 64.0457 | -59.1431 | -59.198 | -59.1156 | -0.09613 | -59.4177 | 64.0594 | 63.9999 | -59.2163 | -59.2712 | -0.041198 | -0.09613 | 0.091552 | 123.056 | -0.24261 | -0.14648 | -0.027466 | -0.11444 | -0.16937 | 0.10529 | -0.013733 | -0.31586 | -0.14648 | 0.045776 | 123.1476 | 123.0286 | 58.9828 | -123.1522 | 123.1613 | 123.1018 | 59.0057 | -123.2254
307.6875 | 123.2529 | -59.1064 | 63.9816 | 4.3678 | 0.054641 | 0.062486 | 0.096372 | 0.12706 | 0.00055539 | -0.008859 | 0.17756 | -0.0042092 | 0.067339 | 0.06358 | 0.0007748 | -0.0071624 | 63.9725 | 64.0228 | -0.10529 | -59.3216 | 64.0549 | -59.1431 | -59.1888 | -59.0836 | -0.068665 | -59.4086 | 64.0549 | 63.9954 | -59.2026 | -59.2896 | -0.036621 | -0.082398 | 0.073243 | 123.1293 | -0.21515 | -0.13275 | -0.009155 | -0.096131 | -0.18311 | 0.073243 | 0.022888 | -0.30212 | -0.11902 | 0.013733 | 123.1613 | 123.0789 | 59.0012 | -123.1705 | 123.1613 | 123.1018 | 59.0378 | -123.2712
308.7031 | 123.3353 | -59.0515 | 63.9771 | -0.042028 | 0.025802 | 0.074235 | 0.071806 | 0.12385 | -0.026148 | -0.0142 | 0.19282 | -0.011686 | 0.059862 | 0.059307 | -0.0056342 | 0.0045866 | 63.9725 | 64.1235 | 0.004578 | -59.2667 | 63.9908 | -59.1156 | -59.1568 | -59.0057 | 0.09613 | -59.2667 | 64.0411 | 63.9771 | -59.1522 | -59.23 | -0.064087 | -0.10529 | 0.013733 | 123.175 | -0.21515 | -0.10986 | -0.004578 | -0.10071 | -0.17853 | 0.064087 | 0.045777 | -0.21515 | -0.036621 | 0 | 123.0423 | 123.024 | 59.0561 | -123.1338 | 123.0927 | 123.0286 | 59.1476 | -123.2071
309.6875 | 123.2574 | -59.1064 | 63.9725 | 0.24789 | 0.037552 | 0.081712 | 0.085691 | 0.11958 | 0.015508 | -0.007791 | 0.63532 | -0.0010052 | 0.058794 | 0.060376 | 0.0082518 | -0.0071624 | 63.9404 | 63.9771 | -0.13733 | -59.3903 | 64.0411 | -59.1522 | -59.2026 | -59.079 | -0.073242 | -59.404 | 64.0686 | 63.9999 | -59.2117 | -59.2896 | -0.045777 | -0.096131 | 0.068665 | 123.0835 | -0.28381 | -0.18768 | -0.032043 | -0.10529 | -0.18311 | 0.096131 | 0.027466 | -0.29755 | -0.11444 | 0.027466 | 123.1476 | 123.0469 | 58.9691 | -123.175 | 123.175 | 123.1064 | 59.0332 | -123.262
310.6875 | 123.2483 | -59.079 | 63.9999 | 0.33944 | 0.029007 | 0.06035 | 0.080351 | 0.12278 | 0.0080314 | 0.006095 | 0.13178 | 0.017153 | 0.064134 | 0.06358 | -0.0013612 | -0.011435 | 63.9359 | 63.9816 | -0.14191 | -59.3353 | 64.0457 | -59.1293 | -59.2026 | -59.0515 | -0.045776 | -59.3857 | 64.0778 | 63.9954 | -59.1843 | -59.2529 | -0.050354 | -0.1236 | 0.045776 | 123.0606 | -0.25635 | -0.13275 | -0.064087 | -0.10529 | -0.17395 | 0.07782 | 0.027465 | -0.3067 | -0.13275 | -0.004578 | 123.1247 | 123.0148 | 58.9371 | -123.2025 | 123.1567 | 123.0743 | 59.0332 | -123.2529
311.6875 | 123.262 | -59.1019 | 64.0137 | 0.29367 | 0.047165 | 0.069963 | 0.079283 | 0.13133 | 0.013372 | -0.003518 | 0.26911 | -0.0042092 | 0.066271 | 0.066784 | -0.0034972 | -0.0028904 | 63.9267 | 63.9816 | -0.13733 | -59.3353 | 64.032 | -59.1293 | -59.198 | -59.111 | -0.13275 | -59.5917 | 63.9908 | 63.945 | -59.23 | -59.285 | -0.027465 | -0.09613 | 0.01831 | 123.0835 | -0.23346 | -0.13733 | -0.086975 | -0.12817 | -0.1831 | -0.022888 | -0.009155 | -0.48981 | -0.3067 | -0.068665 | 123.1338 | 123.0286 | 58.9645 | -123.2117 | 123.0927 | 123.0469 | 58.9691 | -123.2986
312.6875 | 123.23 | -59.1156 | 63.9771 | 0.064784 | 0.04396 | 0.069963 | 0.083555 | 0.13026 | 0.010168 | -0.004587 | 0.20808 | 0.0054038 | 0.085497 | 0.058239 | 0.0061158 | -0.0082304 | 63.9359 | 64.0045 | -0.086975 | -59.317 | 64.0411 | -59.1431 | -59.1888 | -59.1339 | -0.07782 | -59.4269 | 64.064 | 64.0091 | -59.2209 | -59.2941 | -0.027465 | -0.073242 | 0.064087 | 123.1201 | -0.20142 | -0.12817 | -0.041199 | -0.10529 | -0.17853 | 0.086975 | -0.01831 | -0.31128 | -0.13275 | 0.032043 | 123.1567 | 123.0515 | 59.0286 | -123.1659 | 123.1796 | 123.1247 | 59.0378 | -123.2712
313.7031 | 123.3078 | -59.0607 | 63.9587 | 0.20211 | 0.032211 | 0.073167 | 0.082487 | 0.12492 | -0.030421 | -0.004587 | 0.43696 | -0.012754 | 0.070543 | 0.040081 | -0.0045652 | -0.0050264 | 63.9862 | 64.0549 | -0.050354 | -59.3033 | 64.0091 | -59.0973 | -59.1568 | -59.0515 | 0.032043 | -59.317 | 64.0091 | 63.9587 | -59.1705 | -59.2484 | -0.036621 | -0.09613 | 0.050354 | 123.1155 | -0.24262 | -0.14648 | 0.027466 | -0.10986 | -0.18768 | 0.050354 | 0.009155 | -0.25635 | -0.068665 | 0 | 123.0698 | 123.0469 | 59.0103 | -123.1155 | 123.0698 | 123.0194 | 59.0927 | -123.2071
314.6875 | 123.2529 | -59.1019 | 63.9771 | 0.36996 | 0.022598 | 0.071031 | 0.088896 | 0.11531 | 0.015508 | -0.007791 | 0.40644 | 0.0021988 | 0.061998 | 0.064648 | 0.0039788 | -0.012503 | 64.1052 | 64.0137 | -0.1236 | -59.2804 | 64.0411 | -59.1476 | -59.1797 | -59.0607 | -0.068665 | -59.3765 | 64.0823 | 63.9633 | -59.2163 | -59.2438 | -0.045776 | -0.077819 | 0.064087 | 123.1155 | -0.17853 | -0.10071 | 0.12817 | -0.11444 | -0.14191 | 0.10528 | 0.041199 | -0.27466 | -0.13275 | -0.013733 | 123.143 | 123.2071 | 58.9783 | -123.1567 | 123.1842 | 123.0652 | 59.0332 | -123.2208
315.6875 | 123.23 | -59.1156 | 63.9862 | 0.32418 | 0.032211 | 0.067827 | 0.081419 | 0.12278 | 0.013372 | 0.001822 | 1.1083 | -0.0095502 | 0.054521 | 0.044354 | 0.0071838 | -0.015707 | 63.945 | 63.9954 | -0.15106 | -59.3674 | 64.032 | -59.1614 | -59.2346 | -59.0652 | -0.073242 | -59.3948 | 64.0366 | 64.0091 | -59.1797 | -59.2667 | -0.045776 | -0.11902 | 0.045776 | 123.111 | -0.25177 | -0.13275 | -0.041199 | -0.064086 | -0.15106 | 0.050354 | 0.050354 | -0.27923 | -0.12817 | 0.022888 | 123.1476 | 123.0606 | 58.9645 | -123.2208 | 123.1522 | 123.1247 | 59.0424 | -123.2529
316.6875 | 123.3078 | -59.1019 | 63.9633 | 0.36996 | 0.017257 | 0.068895 | 0.073942 | 0.13346 | -0.0047856 | 0.00289 | 0.36067 | -0.0042092 | 0.057726 | 0.053967 | 0.010388 | -0.0028904 | 63.9587 | 64.0228 | -0.11444 | -59.3124 | 64.0228 | -59.1156 | -59.2209 | -59.0424 | -0.022888 | -59.3491 | 64.0228 | 63.9542 | -59.1522 | -59.2712 | -0.013733 | -0.11902 | 0.059509 | 123.1247 | -0.21057 | -0.091553 | -0.004578 | -0.050354 | -0.16937 | 0.059509 | 0.05951 | -0.24719 | -0.07782 | -0.009155 | 123.1247 | 123.0606 | 58.9874 | -123.1842 | 123.1247 | 123.056 | 59.079 | -123.2346
317.6875 | 123.2803 | -59.0881 | 63.9999 | 0.36996 | 0.030075 | 0.076372 | 0.077146 | 0.12919 | 0.0016234 | -0.009927 | 0.29963 | 0.0011308 | 0.080156 | 0.045422 | 0.0050478 | -0.011435 | 63.9175 | 63.9908 | -0.14191 | -59.3353 | 64.0366 | -59.1568 | -59.2026 | -59.0744 | -0.32501 | -59.5413 | 64.0045 | 63.9587 | -59.2163 | -59.2575 | -0.068664 | -0.11444 | 0.036621 | 123.0789 | -0.24719 | -0.13275 | -0.082397 | -0.12817 | -0.16937 | 0.004578 | 0.013733 | -0.45319 | -0.28381 | -0.041199 | 123.1247 | 123.0057 | 58.9462 | -123.2025 | 123.0927 | 123.0469 | 58.7631 | -123.2574
318.6875 | 123.2483 | -59.1568 | 63.945 | 0.27841 | 0.05571 | 0.078508 | 0.070738 | 0.12492 | 0.01444 | -0.003518 | 0.17756 | 0.0096758 | 0.071611 | 0.064648 | 0.013592 | -0.015707 | 63.9267 | 63.9816 | -0.1236 | -59.3308 | 64.0274 | -59.1476 | -59.198 | -59.0927 | -0.091553 | -59.4177 | 64.0411 | 64.0045 | -59.1751 | -59.2941 | 0.009155 | -0.041199 | 0.082398 | 123.1384 | -0.17395 | -0.13275 | -0.01831 | -0.018311 | -0.13733 | 0.096131 | 0.064087 | -0.26093 | -0.1236 | 0.05951 | 123.1842 | 123.0835 | 59.0332 | -123.143 | 123.1979 | 123.1613 | 59.0652 | -123.2391
319.6875 | 123.2437 | -59.1293 | 63.9679 | 0.034266 | 0.040756 | 0.06035 | 0.080351 | 0.13453 | 0.0037594 | 0.00075395 | 0.040232 | 0.0032668 | 0.07802 | 0.056103 | 0.011456 | -0.011435 | 63.9359 | 64.0274 | -0.082397 | -59.2987 | 64.0457 | -59.1202 | -59.1797 | -59.1019 | -0.082397 | -59.4315 | 64.0549 | 64.0137 | -59.2117 | -59.2804 | 0.009155 | -0.050354 | 0.077819 | 123.1567 | -0.16937 | -0.11902 | -0.032044 | -0.082398 | -0.15106 | 0.086975 | 0.027465 | -0.30212 | -0.15106 | 0.045776 | 123.175 | 123.0652 | 59.0469 | -123.1476 | 123.1842 | 123.143 | 59.0469 | -123.2483
320.6875 | 123.23 | -59.111 | 64.0045 | 0.24789 | 0.03862 | 0.061418 | 0.06967 | 0.12919 | 0.0080314 | -0.003518 | 0.26911 | -0.0074142 | 0.070543 | 0.064648 | 0.0082518 | 0.0024506 | 63.8992 | 63.9496 | -0.14648 | -59.3582 | 64.032 | -59.1339 | -59.1888 | -59.1156 | -0.09613 | -59.4269 | 64.064 | 63.9954 | -59.198 | -59.2804 | -0.022888 | -0.07782 | 0.027465 | 123.0606 | -0.24719 | -0.16937 | -0.10529 | -0.086975 | -0.16937 | 0.059509 | -0.004578 | -0.31586 | -0.14648 | -0.009156 | 123.143 | 123.0103 | 58.9645 | -123.1934 | 123.175 | 123.1064 | 59.0149 | -123.2849
321.6875 | 123.2483 | -59.111 | 63.9725 | 0.41574 | 0.036484 | 0.068895 | 0.070738 | 0.13881 | -0.0069216 | -0.005655 | -0.11236 | 6.2833e-05 | 0.057726 | 0.071057 | -0.0077702 | -0.0092984 | 63.9221 | 63.8626 | -0.29297 | -59.4635 | 63.9862 | -59.1797 | -59.2026 | -59.0927 | -0.068665 | -59.3719 | 64.0457 | 63.9816 | -59.2117 | -59.2667 | -0.068664 | -0.091553 | 0.013733 | 122.9736 | -0.35248 | -0.26093 | -0.050354 | -0.10071 | -0.15564 | 0.073242 | 0.018311 | -0.26093 | -0.10529 | 0.009155 | 123.0972 | 123.0331 | 58.8181 | -123.175 | 123.1567 | 123.0927 | 59.0424 | -123.2391
322.6875 | 123.262 | -59.1064 | 63.9862 | 0.3547 | 0.045028 | 0.06569 | 0.083555 | 0.12706 | 0.0048274 | 0.003958 | 3.6108 | 0.0043348 | 0.068407 | 0.062512 | 0.010388 | 0.00031457 | 63.9267 | 63.9954 | -0.13275 | -59.3353 | 64.0457 | -59.1431 | -59.1888 | -59.079 | -0.073242 | -59.3857 | 64.0869 | 64.0045 | -59.1751 | -59.2804 | -0.036621 | -0.082398 | 0.059509 | 123.1018 | -0.22888 | -0.14648 | -0.059509 | -0.068665 | -0.17395 | 0.10071 | 0.027466 | -0.27924 | -0.10528 | 0.018311 | 123.1522 | 123.0331 | 58.9737 | -123.175 | 123.1934 | 123.111 | 59.0332 | -123.2666
323.6875 | 123.2391 | -59.111 | 63.9771 | 0.32418 | 0.030075 | 0.061418 | 0.07501 | 0.12065 | 0.0016234 | -0.010995 | 0.20808 | -0.0031412 | 0.072679 | 0.069989 | 0.0050478 | -0.0082304 | 63.9359 | 63.9862 | -0.13733 | -59.3399 | 64.0228 | -59.1293 | -59.1843 | -59.0881 | 0.14191 | -59.404 | 64.0686 | 64.0045 | -59.1934 | -59.2575 | -0.01831 | -0.073242 | 0.045776 | 123.0972 | -0.22888 | -0.15564 | -0.041199 | -0.082397 | -0.14648 | 0.091553 | 0.022888 | -0.29297 | -0.14649 | 0.027466 | 123.1339 | 123.0469 | 58.9737 | -123.1613 | 123.1796 | 123.1155 | 59.2529 | -123.2346
324.6875 | 123.3124 | -59.0927 | 63.9771 | 0.52255 | 0.02687 | 0.051805 | 0.078214 | 0.12492 | -0.0015816 | 0.010367 | 0.33015 | 0.0043348 | 0.070543 | 0.049694 | 0.010388 | -0.0028904 | 63.9267 | 64.0274 | -0.12817 | -59.317 | 63.9999 | -59.1385 | -59.166 | -59.0698 | -0.041199 | -59.3491 | 64.0182 | 63.9908 | -59.198 | -59.2438 | -0.045777 | -0.073243 | 0.022888 | 123.1201 | -0.22431 | -0.15106 | -0.050354 | -0.10529 | -0.15106 | 0.041199 | 0.022888 | -0.25635 | -0.10529 | 0.013733 | 123.0927 | 123.0194 | 58.9645 | -123.143 | 123.111 | 123.0835 | 59.0515 | -123.2208
325.6875 | 123.317 | -59.1293 | 63.9954 | 0.41574 | 0.036484 | 0.069963 | 0.072874 | 0.11958 | 0.0058954 | -0.005655 | 0.22334 | -0.0042092 | 0.064134 | 0.057171 | 0.0050478 | -0.014639 | 63.9267 | 63.9954 | -0.14648 | -59.3308 | 64.0274 | -59.1476 | -59.1843 | -59.1156 | -0.086975 | -59.4086 | 64.0503 | 63.9816 | -59.1888 | -59.285 | -0.018311 | -0.054932 | 0.032044 | 123.1247 | -0.20142 | -0.14648 | -0.068664 | -0.05951 | -0.15564 | 0.054932 | 0.013732 | -0.27924 | -0.1236 | -0.013733 | 123.1567 | 123.056 | 58.9828 | -123.1796 | 123.1796 | 123.111 | 59.0424 | -123.2803
326.6875 | 123.1934 | -59.0973 | 64.0045 | 0.12582 | 0.040756 | 0.058214 | 0.082487 | 0.11103 | 0.011236 | 0.006095 | 0.009715 | 0.0054038 | 0.065202 | 0.049694 | 0.0061158 | -0.016775 | 63.9404 | 64.0045 | -0.09613 | -59.3124 | 64.064 | -59.1202 | -59.1797 | -59.1248 | -0.086975 | -59.436 | 64.0732 | 64.0182 | -59.2117 | -59.2804 | -0.022888 | -0.082397 | 0.059509 | 123.1018 | -0.21515 | -0.13275 | -0.064087 | -0.11444 | -0.18311 | 0.068664 | -0.027466 | -0.33874 | -0.15564 | 0.013733 | 123.1613 | 123.0377 | 59.0012 | -123.1842 | 123.1705 | 123.1155 | 59.0103 | -123.2849
327.6875 | 123.317 | -59.1339 | 63.9404 | 0.20211 | 0.04396 | 0.066759 | 0.093168 | 0.12172 | 0.0080314 | -0.006723 | 0.2386 | -0.0010052 | 0.066271 | 0.06358 | 0.0050478 | -0.0028904 | 63.9175 | 63.9771 | -0.13733 | -59.3308 | 64.0411 | -59.1248 | -59.1751 | -59.1202 | -0.086975 | -59.4223 | 64.0457 | 63.9954 | -59.1934 | -59.2667 | 0.009155 | -0.041199 | 0.10071 | 123.111 | -0.19684 | -0.15564 | -0.022888 | -0.059509 | -0.13275 | 0.10529 | 0.013733 | -0.28839 | -0.15564 | 0.054931 | 123.175 | 123.0515 | 58.9966 | -123.1155 | 123.1796 | 123.1293 | 59.0469 | -123.2071
328.6875 | 123.3444 | -59.0652 | 63.913 | 0.38522 | 0.032211 | 0.07744 | 0.067533 | 0.13453 | -0.0079896 | 0.00075395 | 0.62007 | -0.010618 | 0.065202 | 0.069989 | -0.0024292 | -0.0028904 | 63.9771 | 64.0823 | -0.054932 | -59.2758 | 63.9816 | -59.111 | -59.1339 | -59.0149 | 0.032043 | -59.2987 | 63.9862 | 63.9771 | -59.1934 | -59.2438 | -0.045776 | -0.068664 | 0.068664 | 123.1476 | -0.21057 | -0.14191 | 0.064087 | -0.12817 | -0.17853 | 0.073242 | 0.050354 | -0.23346 | -0.054932 | 0.064087 | 123.0469 | 123.0423 | 59.0103 | -123.0469 | 123.0515 | 123.0423 | 59.0973 | -123.1567
329.6875 | 123.2346 | -59.0881 | 63.9816 | 0.84298 | 0.031143 | 0.071031 | 0.06967 | 0.13346 | 0.0080314 | -0.007791 | 0.28437 | -0.0042092 | 0.072679 | 0.060376 | 0.017865 | 0.0013826 | 63.9313 | 64.0045 | -0.13733 | -59.3399 | 64.0457 | -59.1248 | -59.166 | -59.079 | -0.068665 | -59.3765 | 64.0457 | 63.9771 | -59.198 | -59.2804 | -0.036621 | -0.07782 | 0.064087 | 123.0927 | -0.25177 | -0.17395 | -0.050354 | -0.10986 | -0.19226 | 0.064087 | 0.009156 | -0.28839 | -0.09613 | -0.004577 | 123.1338 | 123.0194 | 58.9508 | -123.1476 | 123.1338 | 123.0652 | 59.0195 | -123.262
330.6875 | 123.2666 | -59.0927 | 63.9771 | -0.087804 | 0.020462 | 0.068895 | 0.073942 | 0.13453 | -0.00051261 | -0.00031405 | 0.29963 | 0.0011308 | 0.051317 | 0.051831 | 0.0061158 | -0.0039584 | 63.9404 | 64.0182 | -0.1236 | -59.3353 | 64.0457 | -59.1385 | -59.198 | -59.0927 | -0.059509 | -59.3765 | 64.0457 | 63.9679 | -59.1705 | -59.2575 | -0.045777 | -0.10529 | 0.068664 | 123.111 | -0.24262 | -0.13733 | -0.036621 | -0.07782 | -0.16479 | 0.068664 | 0 | -0.28381 | -0.11902 | -0.009155 | 123.1384 | 123.0331 | 58.9691 | -123.175 | 123.1384 | 123.0606 | 59.0332 | -123.2346
331.6875 | 123.2346 | -59.1064 | 63.9679 | -0.37772 | 0.031143 | 0.067827 | 0.066465 | 0.11851 | -0.00051261 | -0.010995 | 0.34541 | 0.0086078 | 0.06093 | 0.06358 | 0.0050478 | -0.0028904 | 63.9359 | 64.0091 | -0.11902 | -59.3308 | 64.0366 | -59.1293 | -59.1843 | -59.0607 | -0.07782 | -59.3628 | 64.0549 | 63.9954 | -59.1888 | -59.2758 | -0.022888 | -0.07782 | 0.068664 | 123.1155 | -0.22431 | -0.14648 | -0.032044 | -0.082398 | -0.16937 | 0.086975 | 0.045776 | -0.25635 | -0.086975 | 0.027465 | 123.143 | 123.0423 | 58.9874 | -123.1522 | 123.1613 | 123.1018 | 59.0286 | -123.2437
332.6875 | 123.3261 | -59.0607 | 63.9313 | 0.431 | 0.031143 | 0.064622 | 0.068601 | 0.12599 | 0.0016234 | -0.00245 | 0.46748 | -0.0010052 | 0.068407 | 0.040081 | 0.0029108 | -0.0082304 | 63.9816 | 64.1006 | -0.050354 | -59.2621 | 63.9908 | -59.1248 | -59.166 | -59.0195 | 0.013733 | -59.2987 | 64.0182 | 63.945 | -59.1934 | -59.2758 | -0.064087 | -0.10529 | 0.05951 | 123.1613 | -0.20142 | -0.09613 | 0.050354 | -0.13275 | -0.21515 | 0.086976 | 0.041199 | -0.23804 | -0.022888 | 0.013733 | 123.0515 | 123.0423 | 59.0103 | -123.0972 | 123.0789 | 123.0057 | 59.0744 | -123.2071
333.6875 | 123.2529 | -59.079 | 63.9771 | 0.49203 | 0.033279 | 0.08278 | 0.076078 | 0.12919 | 0.0026914 | -0.013132 | 0.31489 | -0.010618 | 0.071611 | 0.055035 | 0.0039788 | -0.0018224 | 63.9496 | 64.0137 | -0.11902 | -59.3124 | 64.0503 | -59.111 | -59.1934 | -59.079 | -0.036621 | -59.3582 | 64.0366 | 63.9496 | -59.2072 | -59.2621 | -0.032044 | -0.11444 | 0.073242 | 123.0927 | -0.23346 | -0.11902 | -0.027466 | -0.12817 | -0.18311 | 0.059509 | 0 | -0.27924 | -0.09613 | -0.027466 | 123.1293 | 123.0286 | 58.96 | -123.1705 | 123.1155 | 123.0286 | 59.0424 | -123.2391
334.6875 | 123.262 | -59.0973 | 63.9633 | 0.30892 | 0.020462 | 0.06035 | 0.079283 | 0.13026 | 0.0058954 | -0.00031405 | 0.39118 | 0.0011308 | 0.08336 | 0.057171 | 0.012524 | -0.016775 | 63.9084 | 64.0228 | -0.11444 | -59.3353 | 64.0366 | -59.1293 | -59.1934 | -59.0561 | -0.041199 | -59.3674 | 64.0274 | 63.9542 | -59.1934 | -59.2575 | -0.032043 | -0.09613 | 0.073242 | 123.1201 | -0.23804 | -0.14191 | -0.054932 | -0.09613 | -0.16022 | 0.064087 | 0.041199 | -0.27008 | -0.10986 | -0.009155 | 123.1338 | 123.0057 | 58.9828 | -123.1567 | 123.1247 | 123.0515 | 59.0561 | -123.2208
335.6875 | 123.3353 | -59.0561 | 63.9542 | 0.38522 | 0.037552 | 0.068895 | 0.077146 | 0.12492 | 0.0016234 | 0.00289 | 0.43696 | -0.0020732 | 0.072679 | 0.051831 | -0.0013612 | -0.010367 | 63.9908 | 64.1281 | -0.022888 | -59.2529 | 63.9954 | -59.0973 | -59.1476 | -59.0149 | 0.027466 | -59.2941 | 64.0137 | 63.9404 | -59.1843 | -59.2346 | -0.041199 | -0.091553 | 0.041198 | 123.1842 | -0.19684 | -0.10529 | 0.036621 | -0.12817 | -0.17853 | 0.059509 | 0.041198 | -0.23804 | -0.059509 | -0.013733 | 123.0515 | 123.0469 | 59.0332 | -123.1018 | 123.0698 | 122.9965 | 59.0836 | -123.1888
336.6875 | 123.3215 | -59.0698 | 63.945 | 0.40048 | 0.040756 | 0.067827 | 0.087828 | 0.12812 | 0.0016234 | -0.009927 | 0.36067 | -0.012754 | 0.074815 | 0.074261 | 0.0061158 | -0.0060944 | 64.0137 | 64.1235 | -0.013733 | -59.2621 | 63.9908 | -59.1019 | -59.1568 | -59.0012 | 0.036621 | -59.2987 | 63.9954 | 63.9221 | -59.1843 | -59.2392 | -0.032044 | -0.086975 | 0.045777 | 123.1934 | -0.19226 | -0.10529 | 0.068665 | -0.11444 | -0.16937 | 0.050354 | 0.068664 | -0.22888 | -0.059509 | -0.022888 | 123.0606 | 123.0835 | 59.0561 | -123.1018 | 123.0652 | 122.9919 | 59.1064 | -123.1842
337.6875 | 123.3444 | -59.0698 | 63.9496 | 0.46151 | 0.065323 | 0.068895 | 0.07501 | 0.1324 | -0.0069216 | -0.006723 | 0.43696 | -0.0074142 | 0.059862 | 0.050762 | 0.0082518 | -0.012503 | 64.0137 | 64.1235 | -0.032043 | -59.2529 | 63.9816 | -59.111 | -59.1476 | -58.9966 | 0.032043 | -59.2987 | 64.0137 | 63.9313 | -59.1705 | -59.2438 | -0.041199 | -0.07782 | 0.032043 | 123.1934 | -0.18311 | -0.10529 | 0.064087 | -0.10071 | -0.17395 | 0.064087 | 0.073242 | -0.22888 | -0.054932 | -0.018311 | 123.0515 | 123.0835 | 59.0378 | -123.0972 | 123.0835 | 123.0011 | 59.1019 | -123.1934
338.6875 | 123.3261 | -59.0836 | 63.9404 | 0.095301 | 0.046097 | 0.063554 | 0.079283 | 0.12706 | -0.0037176 | 0.00075395 | 0.48274 | -0.010618 | 0.073747 | 0.061444 | 0.0093198 | -0.0082304 | 64.0045 | 64.1327 | -0.018311 | -59.2529 | 63.9725 | -59.111 | -59.1248 | -59.0149 | 0.054932 | -59.2941 | 64.0274 | 63.9221 | -59.1888 | -59.2438 | -0.027466 | -0.041199 | 0.032043 | 123.2162 | -0.16937 | -0.12817 | 0.064087 | -0.10529 | -0.16022 | 0.086975 | 0.068664 | -0.21057 | -0.050354 | -0.018311 | 123.056 | 123.0881 | 59.0652 | -123.0652 | 123.111 | 123.0057 | 59.1385 | -123.1842
339.6875 | 123.2986 | -59.0698 | 63.9496 | 0.47677 | 0.027939 | 0.069963 | 0.077146 | 0.12706 | 0.0058954 | -0.010995 | 0.33015 | 0.0086078 | 0.066271 | 0.064648 | 0.012524 | -0.011435 | 63.9587 | 64.0594 | -0.082397 | -59.2896 | 64.0137 | -59.0881 | -59.1705 | -59.0195 | -0.004578 | -59.3216 | 64.0366 | 63.945 | -59.1751 | -59.23 | -0.018311 | -0.10071 | 0.064087 | 123.1293 | -0.21973 | -0.11902 | 0.009155 | -0.10529 | -0.16022 | 0.086975 | 0.050354 | -0.25177 | -0.091552 | -0.004578 | 123.0835 | 123.0286 | 58.9874 | -123.1201 | 123.1064 | 123.0148 | 59.0652 | -123.1796
340.6875 | 123.3124 | -59.0973 | 63.9221 | 0.46151 | 0.03862 | 0.063554 | 0.080351 | 0.11744 | 0.0069634 | -0.00245 | 0.29963 | -0.0095502 | 0.063066 | 0.06358 | 0.0050478 | -0.013571 | 63.9771 | 64.0686 | -0.07782 | -59.3079 | 64.0274 | -59.1293 | -59.1843 | -59.0012 | 0.045776 | -59.317 | 64.0137 | 63.9542 | -59.1614 | -59.285 | -0.032043 | -0.086975 | 0.10529 | 123.1659 | -0.21057 | -0.1236 | 0.054932 | -0.064087 | -0.18768 | 0.091553 | 0.09613 | -0.21973 | -0.032044 | 0.032044 | 123.1247 | 123.0743 | 59.0195 | -123.1064 | 123.111 | 123.0515 | 59.1431 | -123.2071
341.6875 | 123.3353 | -59.0607 | 63.9496 | 0.431 | 0.015121 | 0.066759 | 0.066465 | 0.14201 | 0.0016234 | 0.005026 | 0.37593 | -0.0063462 | 0.071611 | 0.051831 | -0.0034972 | -0.0082304 | 64.0091 | 64.1235 | -0.018311 | -59.2575 | 63.9816 | -59.0881 | -59.1476 | -58.9554 | -0.21973 | -59.2438 | 63.9725 | 63.9175 | -59.1843 | -59.2529 | -0.027466 | -0.086975 | 0.032043 | 123.1842 | -0.19684 | -0.10986 | 0.059509 | -0.1236 | -0.19226 | 0.022888 | 0.10529 | -0.18311 | 0.009156 | -0.032043 | 123.0423 | 123.0698 | 59.0424 | -123.0972 | 123.0331 | 122.9782 | 58.8409 | -123.2025
342.6875 | 123.2986 | -59.079 | 63.9542 | 0.30892 | 0.008713 | 0.066759 | 0.080351 | 0.12599 | -0.018671 | -0.0142 | 0.40644 | -0.020231 | 0.070543 | 0.069989 | 0.0039788 | -0.0092984 | 63.9862 | 64.1327 | -0.027466 | -59.2712 | 63.9725 | -59.1019 | -59.1202 | -59.0149 | 0.027466 | -59.3124 | 63.9954 | 63.9404 | -59.1797 | -59.2438 | -0.022889 | -0.041199 | 0.01831 | 123.2117 | -0.19226 | -0.15106 | 0.032043 | -0.10071 | -0.1648 | 0.041198 | 0.064086 | -0.23346 | -0.068665 | -0.013733 | 123.0515 | 123.0652 | 59.0515 | -123.0743 | 123.0743 | 123.0194 | 59.1064 | -123.1979
343.6875 | 123.2803 | -59.0652 | 63.9587 | 0.27841 | 0.018326 | 0.067827 | 0.070738 | 0.12385 | -0.013331 | -0.0142 | 0.39118 | -0.014891 | 0.065202 | 0.043286 | 0.0039788 | -0.0028904 | 64.0182 | 64.1235 | -0.018311 | -59.2758 | 63.9816 | -59.0881 | -59.1522 | -59.0012 | 0.018311 | -59.2941 | 63.9999 | 63.9267 | -59.1568 | -59.2392 | -0.022888 | -0.086975 | 0.022888 | 123.1888 | -0.21057 | -0.1236 | 0.05951 | -0.091552 | -0.17395 | 0.041199 | 0.064087 | -0.22888 | -0.054931 | -0.032043 | 123.0469 | 123.0835 | 59.0469 | -123.111 | 123.0652 | 122.9919 | 59.0836 | -123.1979
344.6875 | 123.2941 | -59.0698 | 63.9679 | 0.26315 | 0.025802 | 0.06569 | 0.06967 | 0.12278 | -0.0069216 | -0.018472 | 0.26911 | -0.019163 | 0.059862 | 0.059307 | 0.0029108 | -0.015707 | 63.9954 | 64.1327 | -0.032043 | -59.2941 | 63.9999 | -59.1019 | -59.1705 | -59.0057 | 0.027466 | -59.3216 | 64.0228 | 63.9404 | -59.166 | -59.2346 | -0.032044 | -0.10071 | 0.032043 | 123.2025 | -0.2243 | -0.1236 | 0.027465 | -0.096131 | -0.1648 | 0.054931 | 0.064087 | -0.25177 | -0.086975 | -0.027466 | 123.0698 | 123.0652 | 59.0378 | -123.1384 | 123.0927 | 123.0103 | 59.0973 | -123.2025
345.6875 | 123.2849 | -59.0698 | 63.9633 | 0.27841 | 0.018326 | 0.064622 | 0.079283 | 0.11531 | -0.0069216 | -0.020608 | 0.28437 | -0.0063462 | 0.064134 | 0.049694 | -0.0056342 | -0.014639 | 63.9908 | 64.1144 | -0.032043 | -59.2941 | 64.0091 | -59.111 | -59.1568 | -59.0149 | 0.027466 | -59.3033 | 64.0366 | 63.9359 | -59.1568 | -59.2438 | -0.041199 | -0.086975 | 0.045776 | 123.1842 | -0.2243 | -0.13733 | 0.027466 | -0.086975 | -0.17395 | 0.073242 | 0.054931 | -0.23346 | -0.05951 | -0.027466 | 123.0789 | 123.0606 | 59.0378 | -123.1201 | 123.1064 | 123.0057 | 59.0973 | -123.2071
346.6875 | 123.3078 | -59.0515 | 63.945 | 0.50729 | 0.010849 | 0.075304 | 0.073942 | 0.13346 | 0.0037594 | -0.013132 | 0.28437 | -0.0063462 | 0.055589 | 0.072125 | 0.0061158 | -0.0039584 | 64.0274 | 64.1373 | -0.004578 | -59.2621 | 63.9862 | -59.0881 | -59.1293 | -58.9874 | 0.032043 | -59.2896 | 64.032 | 63.9221 | -59.198 | -59.2209 | -0.036621 | -0.077819 | 0.041199 | 123.1888 | -0.21057 | -0.13275 | 0.082398 | -0.14648 | -0.16937 | 0.086975 | 0.064087 | -0.23804 | -0.068665 | -0.022888 | 123.0377 | 123.0789 | 59.0469 | -123.0743 | 123.0835 | 122.9736 | 59.0836 | -123.1659
347.6875 | 123.2986 | -59.0332 | 63.9359 | 0.30892 | -0.00090105 | 0.07744 | 0.066465 | 0.12919 | -0.0058536 | -0.015268 | 0.25385 | -0.011686 | 0.06093 | 0.055035 | 0.0050478 | -0.0092984 | 64.0274 | 64.1418 | -0.018311 | -59.2667 | 63.9862 | -59.111 | -59.1385 | -58.9737 | 0.036621 | -59.2987 | 64.0091 | 63.9221 | -59.1888 | -59.2346 | -0.07782 | -0.10529 | 0.050354 | 123.175 | -0.23346 | -0.12817 | 0.091553 | -0.15564 | -0.20142 | 0.073242 | 0.059509 | -0.2655 | -0.064087 | -0.013733 | 123.0194 | 123.0606 | 59.0149 | -123.0743 | 123.0423 | 122.9553 | 59.0698 | -123.1705
348.6875 | 123.2895 | -59.0881 | 63.9771 | 0.20211 | 0.017257 | 0.072099 | 0.067533 | 0.11958 | -0.02508 | -0.010995 | 0.14704 | 0.0032668 | 0.063066 | 0.059307 | 0.0018428 | -0.0050264 | 63.9542 | 64.1098 | -0.036621 | -59.2804 | 64.0137 | -59.0836 | -59.1476 | -59.0195 | 0.018311 | -59.3124 | 64.0549 | 63.9221 | -59.1568 | -59.2117 | 0.004578 | -0.059509 | 0.036621 | 123.1979 | -0.19226 | -0.13275 | -0.022888 | -0.068664 | -0.1236 | 0.07782 | 0.068665 | -0.2243 | -0.10071 | -0.054932 | 123.1018 | 123.0423 | 59.0515 | -123.1247 | 123.143 | 123.0103 | 59.1064 | -123.1888
349.6875 | 123.317 | -59.0469 | 63.9633 | 1.0719 | -0.011582 | 0.061418 | 0.072874 | 0.12385 | -0.00051261 | -0.007791 | 0.009715 | -0.0084822 | 0.059862 | 0.056103 | -0.0099062 | -0.0018224 | 63.9725 | 64.0961 | -0.013733 | -59.2758 | 64.0045 | -59.1064 | -59.111 | -59.0195 | 0.059509 | -59.2896 | 64.0366 | 63.9542 | -59.1522 | -59.23 | -0.059509 | -0.064087 | 0.041199 | 123.143 | -0.22888 | -0.16479 | 0.009155 | -0.10529 | -0.18311 | 0.073242 | 0.027466 | -0.24262 | -0.059509 | -0.009155 | 123.0515 | 123.0194 | 59.0332 | -123.0743 | 123.0835 | 123.0011 | 59.1064 | -123.1934
350.6875 | 123.3444 | -59.0607 | 63.9816 | 0.36996 | -0.00090105 | 0.067827 | 0.079283 | 0.11958 | -0.012263 | -0.003518 | -0.081838 | -0.015959 | 0.06093 | 0.050762 | -0.0034972 | -0.012503 | 63.9954 | 64.1418 | -0.004578 | -59.2621 | 64.0366 | -59.0927 | -59.1339 | -59.0012 | 0.09613 | -59.285 | 64.0411 | 63.945 | -59.1385 | -59.2255 | -0.032043 | -0.073242 | 0.054932 | 123.2025 | -0.20142 | -0.12817 | 0.013733 | -0.07782 | -0.1648 | 0.05951 | 0.059509 | -0.2243 | -0.059509 | -0.036621 | 123.0972 | 123.056 | 59.0561 | -123.1155 | 123.1018 | 123.0057 | 59.1568 | -123.2071
351.6875 | 123.3398 | -59.0469 | 63.9679 | 0.019007 | -0.014786 | 0.083848 | 0.054716 | 0.1356 | -0.0058536 | -0.005655 | -0.26494 | -0.0095502 | 0.071611 | 0.058239 | 0.0050478 | -0.014639 | 63.9999 | 64.151 | -0.013733 | -59.2484 | 64.0228 | -59.0836 | -59.1614 | -58.9737 | 0.10071 | -59.2758 | 64.0549 | 63.9542 | -59.1522 | -59.2392 | -0.036621 | -0.11444 | 0.054931 | 123.1979 | -0.20142 | -0.086975 | 0.032043 | -0.10529 | -0.19226 | 0.086975 | 0.073242 | -0.22888 | -0.036621 | -0.013733 | 123.0698 | 123.0469 | 59.0332 | -123.1293 | 123.1018 | 123.0011 | 59.1476 | -123.2071
352.6875 | 123.3444 | -59.0332 | 63.9771 | -0.026769 | -0.01265 | 0.059282 | 0.083555 | 0.12278 | -0.0090576 | -0.008859 | -0.097097 | -0.014891 | 0.050249 | 0.051831 | -0.0024292 | -0.0082304 | 64.0091 | 64.1602 | 0.013733 | -59.2438 | 64.0457 | -59.079 | -59.1293 | -58.96 | 0.11444 | -59.2667 | 64.032 | 63.9084 | -59.1339 | -59.2072 | -0.045776 | -0.09613 | 0.068664 | 123.1934 | -0.21057 | -0.11444 | 0.032043 | -0.10071 | -0.17395 | 0.054931 | 0.073242 | -0.23346 | -0.05951 | -0.068665 | 123.0789 | 123.0423 | 59.0469 | -123.1064 | 123.0652 | 122.9416 | 59.1476 | -123.1842
353.6875 | 123.3307 | -59.0561 | 63.9862 | 0.019007 | 0.003372 | 0.063554 | 0.070738 | 0.12706 | -0.0069216 | -0.004587 | 0.22334 | -0.014891 | 0.061998 | 0.045422 | 0.0093198 | -0.015707 | 63.913 | 64.1281 | -0.027466 | -59.2712 | 64.0411 | -59.111 | -59.1614 | -59.0057 | 0.059509 | -59.2987 | 64.0686 | 63.9267 | -59.1705 | -59.23 | -0.054932 | -0.10529 | 0.054932 | 123.1842 | -0.21515 | -0.10986 | -0.073242 | -0.11444 | -0.17395 | 0.082398 | 0.050354 | -0.24262 | -0.068664 | -0.059509 | 123.0972 | 122.9691 | 59.0286 | -123.1476 | 123.1247 | 122.9828 | 59.1156 | -123.2162
354.6875 | 123.3032 | -59.0332 | 63.9542 | 1.0719 | -0.009445 | 0.073167 | 0.072874 | 0.11851 | -0.015467 | -0.009927 | 0.009715 | 6.2833e-05 | 0.0385 | 0.067852 | -0.0013612 | -0.010367 | 63.9771 | 64.1327 | -0.032043 | -59.2712 | 64.0457 | -59.111 | -59.1568 | -58.9966 | 0.073242 | -59.2987 | 64.0457 | 63.9359 | -59.1568 | -59.2392 | -0.07782 | -0.1236 | 0.091552 | 123.1659 | -0.23804 | -0.11444 | 0.022888 | -0.1236 | -0.20599 | 0.091552 | 0.036621 | -0.2655 | -0.059509 | -0.018311 | 123.0789 | 123.0103 | 59.0012 | -123.111 | 123.0789 | 122.9691 | 59.1064 | -123.1934
355.6875 | 123.381 | -59.0057 | 63.9771 | -0.13358 | -0.008377 | 0.059282 | 0.061125 | 0.12599 | 0.0058954 | -0.010995 | -0.17339 | -0.0074142 | 0.0385 | 0.057171 | -0.0056342 | -0.021048 | 64.0457 | 64.2014 | 0.041199 | -59.2392 | 64.0457 | -59.0881 | -59.1476 | -58.9417 | 0.15564 | -59.2117 | 64.064 | 63.9267 | -59.1385 | -59.2072 | -0.082398 | -0.14191 | 0.068664 | 123.2071 | -0.23346 | -0.091553 | 0.068664 | -0.13275 | -0.20142 | 0.086975 | 0.064087 | -0.20599 | -0.004578 | -0.050354 | 123.0515 | 123.0515 | 59.0469 | -123.1247 | 123.0698 | 122.9324 | 59.1614 | -123.1842
356.6875 | 123.349 | -59.0149 | 63.9908 | -0.3472 | -0.010514 | 0.088121 | 0.07501 | 0.13346 | -0.0069216 | 0.003958 | -3.4693 | -0.011686 | 0.059862 | 0.060376 | 0.0093198 | -0.010367 | 64.0778 | 64.2517 | 0.10986 | -59.2209 | 64.0045 | -59.0744 | -59.1156 | -58.9645 | 0.19684 | -59.2529 | 64.032 | 63.9084 | -59.1385 | -59.2209 | -0.059509 | -0.10071 | 0.013733 | 123.2666 | -0.20599 | -0.10529 | 0.086975 | -0.1236 | -0.20599 | 0.041198 | 0.050354 | -0.23804 | -0.032044 | -0.082398 | 123.0194 | 123.0927 | 59.1248 | -123.1064 | 123.0469 | 122.9233 | 59.2117 | -123.2117
357.6875 | 123.3398 | -59.0515 | 63.9862 | -0.3472 | 0.015121 | 0.06035 | 0.079283 | 0.12706 | 0.0048274 | -0.012063 | -0.29546 | -0.0063462 | 0.051317 | 0.052899 | 0.013592 | -0.018912 | 64.064 | 64.2426 | -0.036621 | -59.0149 | 64.0686 | -59.0515 | -59.1156 | -58.9508 | 0.15564 | -59.2255 | 64.0549 | 63.9313 | -59.1431 | -59.2209 | 0 | -0.064087 | 0.082398 | 123.2941 | 0.036621 | 0.10071 | 0.07782 | -0.091552 | -0.16937 | 0.068665 | 0.10071 | -0.17395 | -0.004578 | -0.054932 | 123.1201 | 123.1155 | 59.0149 | -123.1018 | 123.1064 | 122.9828 | 59.2072 | -123.2071
358.6875 | 123.2071 | -59.0515 | 64.0457 | -0.63712 | 0.022598 | 0.07744 | 0.086759 | 0.13987 | 0.0069634 | -0.001382 | -0.57012 | -0.0020732 | 0.061998 | 0.051831 | 0.0082518 | -0.01998 | 63.9816 | 64.1052 | 0.004578 | -59.2804 | 64.0732 | -59.1156 | -59.1522 | -59.0424 | 0.068665 | -59.3445 | 64.1098 | 63.9862 | -59.1751 | -59.2392 | -0.064087 | -0.10071 | 0.027466 | 123.1567 | -0.22888 | -0.12817 | -0.064087 | -0.1236 | -0.18768 | 0.064087 | 0.009156 | -0.29297 | -0.10529 | -0.059509 | 123.1247 | 123.0331 | 59.0561 | -123.1979 | 123.1613 | 123.0377 | 59.1202 | -123.2849
359.6875 | 123.3444 | -59.0424 | 64.0182 | -0.39298 | 0.018326 | 0.097734 | 0.079283 | 0.12065 | 0.0058954 | -0.008859 | -0.5396 | -0.0063462 | 0.051317 | 0.050762 | 0.0029108 | -0.013571 | 64.1006 | 64.1464 | 0.068665 | -59.1934 | 64.0228 | -59.0744 | -59.1568 | -58.9417 | 0.18768 | -59.2484 | 64.0503 | 63.9267 | -59.1248 | -59.198 | -0.032044 | -0.11444 | 0.004577 | 123.1888 | -0.15106 | -0.036621 | 0.082397 | -0.082398 | -0.15564 | 0.032043 | 0.10071 | -0.20599 | -0.050354 | -0.091553 | 123.0652 | 123.143 | 59.111 | -123.175 | 123.0927 | 122.9691 | 59.23 | -123.2162
360.6875 | 123.3582 | -59.0286 | 63.9862 | -0.042028 | -0.004105 | 0.081712 | 0.080351 | 0.12492 | -0.014399 | -0.008859 | -0.32598 | -0.0074142 | 0.048113 | 0.051831 | -0.0013612 | -0.0082304 | 64.0594 | 64.27 | 0.10071 | -59.1843 | 64.0503 | -59.0607 | -59.1293 | -58.9371 | 0.19226 | -59.198 | 64.032 | 63.9313 | -59.1431 | -59.2163 | -0.032044 | -0.10071 | 0.064087 | 123.2986 | -0.15564 | -0.054932 | 0.073242 | -0.11444 | -0.18768 | 0.045776 | 0.091552 | -0.16937 | 0.018311 | -0.054932 | 123.0789 | 123.0881 | 59.1293 | -123.1155 | 123.0606 | 122.9599 | 59.2209 | -123.2025
361.6875 | 123.3261 | -59.0424 | 64.0045 | 1.1024 | -0.007309 | 0.067827 | 0.071806 | 0.12919 | 0.0069634 | 0.001822 | -0.32598 | -0.0095502 | 0.06093 | 0.049694 | 0.0071838 | -0.014639 | 64.0411 | 64.2334 | 0.10986 | -59.2209 | 64.0274 | -59.0744 | -59.0973 | -58.9554 | 0.1831 | -59.2438 | 64.0686 | 63.913 | -59.1385 | -59.2117 | -0.032044 | -0.054932 | 0.022888 | 123.2758 | -0.17853 | -0.1236 | 0.036621 | -0.096131 | -0.16937 | 0.064087 | 0.086975 | -0.20142 | -0.032043 | -0.091553 | 123.0698 | 123.0835 | 59.1522 | -123.1018 | 123.111 | 122.9553 | 59.2255 | -123.2162
362.6875 | 123.2254 | -59.0744 | 64.0228 | -0.46927 | 0.020462 | 0.076372 | 0.079283 | 0.12706 | 0.0058954 | -0.00245 | -0.55486 | -0.010618 | 0.066271 | 0.040081 | 0.0061158 | -0.011435 | 64.0091 | 64.1739 | 0.041199 | -59.2484 | 64.0732 | -59.0744 | -59.1431 | -59.024 | 0.13275 | -59.2987 | 64.1052 | 63.9633 | -59.1522 | -59.2438 | 0 | -0.068664 | 0.050354 | 123.2483 | -0.17395 | -0.10529 | -0.013733 | -0.07782 | -0.16937 | 0.082398 | 0.050354 | -0.2243 | -0.054932 | -0.059509 | 123.1476 | 123.0835 | 59.1156 | -123.1659 | 123.1796 | 123.0377 | 59.2072 | -123.2666
363.6875 | 123.2437 | -59.0561 | 64.0503 | -0.43876 | 0.024734 | 0.074235 | 0.083555 | 0.13346 | -0.0037176 | -0.0142 | -0.40227 | -0.0042092 | 0.059862 | 0.055035 | 0.0007748 | -0.014639 | 64.0045 | 64.151 | 0.041199 | -59.2346 | 64.0732 | -59.0973 | -59.1431 | -59.0149 | 0.054932 | -59.3216 | 64.1144 | 63.9862 | -59.1614 | -59.2255 | -0.041199 | -0.086975 | 0.022888 | 123.2071 | -0.17853 | -0.091553 | -0.045776 | -0.10529 | -0.16937 | 0.064087 | 0.041198 | -0.2655 | -0.09613 | -0.064087 | 123.1293 | 123.0606 | 59.0973 | -123.1934 | 123.1705 | 123.0423 | 59.111 | -123.2758
364.6875 | 123.2117 | -59.0744 | 64.0457 | -0.40824 | 0.016189 | 0.078508 | 0.078214 | 0.12492 | -0.0026496 | 0.001822 | -0.60064 | -0.0074142 | 0.056658 | 0.060376 | -0.0067022 | -0.0071624 | 63.9954 | 64.1739 | 0.009155 | -59.2484 | 64.0869 | -59.0744 | -59.1293 | -59.0149 | 0.1236 | -59.3308 | 64.0869 | 63.9404 | -59.1522 | -59.2438 | 0 | -0.054931 | 0.041199 | 123.2483 | -0.17395 | -0.11902 | -0.050354 | -0.07782 | -0.16937 | 0.041199 | 0.059509 | -0.25635 | -0.086976 | -0.10529 | 123.1613 | 123.0698 | 59.0836 | -123.175 | 123.1613 | 123.0148 | 59.198 | -123.2895
365.6875 | 123.2574 | -59.0469 | 64.0228 | -0.46927 | 0.019394 | 0.072099 | 0.065397 | 0.13453 | 0.0037594 | -0.003518 | -0.24969 | -0.012754 | 0.070543 | 0.056103 | 0.0061158 | -0.0082304 | 63.9816 | 64.1418 | -0.004578 | -59.2712 | 64.1098 | -59.0836 | -59.1476 | -59.0515 | 0.082397 | -59.3262 | 64.1235 | 63.9771 | -59.1614 | -59.23 | -0.036621 | -0.10071 | 0.086975 | 123.1888 | -0.2243 | -0.1236 | -0.041199 | -0.11444 | -0.18311 | 0.10071 | -0.004578 | -0.27924 | -0.09613 | -0.045776 | 123.1567 | 123.0286 | 59.0424 | -123.1705 | 123.1705 | 123.024 | 59.1293 | -123.2529
366.6875 | 123.2346 | -59.0561 | 64.0503 | -0.48453 | 0.012985 | 0.076372 | 0.071806 | 0.12812 | -0.0047856 | -0.003518 | -0.5396 | 6.2833e-05 | 0.051317 | 0.052899 | 0.0039788 | -0.0050264 | 63.9679 | 64.1235 | 0.004578 | -59.2896 | 64.064 | -59.111 | -59.1248 | -59.0424 | 0.091553 | -59.3262 | 64.1098 | 63.9771 | -59.1431 | -59.2392 | -0.054932 | -0.068665 | 0.013733 | 123.1796 | -0.23346 | -0.1648 | -0.082397 | -0.086975 | -0.18311 | 0.059509 | 0.013733 | -0.27008 | -0.086975 | -0.073242 | 123.1201 | 123.024 | 59.0607 | -123.175 | 123.1659 | 123.0331 | 59.1476 | -123.2895
367.6875 | 123.3078 | -59.0607 | 64.0137 | -0.39298 | -0.006241 | 0.08278 | 0.077146 | 0.12706 | -0.0079896 | -0.003518 | -0.43279 | -0.0074142 | 0.053453 | 0.044354 | -0.0024292 | -0.021048 | 64.0366 | 64.2151 | 0.07782 | -59.2117 | 64.0274 | -59.0561 | -59.1156 | -59.0057 | 0.16022 | -59.2575 | 64.0823 | 63.9496 | -59.1339 | -59.2209 | 0.004578 | -0.054932 | 0.013733 | 123.2758 | -0.15106 | -0.09613 | 0.022888 | -0.073242 | -0.16022 | 0.068664 | 0.054932 | -0.19684 | -0.036621 | -0.064087 | 123.0881 | 123.0972 | 59.1385 | -123.1293 | 123.143 | 123.0103 | 59.2209 | -123.2346
368.6875 | 123.2437 | -59.0607 | 64.0549 | -0.43876 | 0.007644 | 0.075304 | 0.071806 | 0.13346 | -0.0015816 | -0.006723 | -0.67693 | -0.0074142 | 0.065202 | 0.052899 | -0.0056342 | -0.0028904 | 63.9999 | 64.1968 | 0.032043 | -59.2804 | 64.0961 | -59.0973 | -59.1476 | -59.0332 | 0.086975 | -59.3399 | 64.1602 | 63.9908 | -59.1797 | -59.2392 | -0.036621 | -0.086975 | 0.041198 | 123.2574 | -0.21973 | -0.13275 | -0.054932 | -0.11902 | -0.17853 | 0.10528 | 0.027466 | -0.27924 | -0.10071 | -0.064087 | 123.1567 | 123.0606 | 59.0927 | -123.2025 | 123.2208 | 123.0515 | 59.1476 | -123.2941
369.6875 | 123.2391 | -59.079 | 64.0228 | 0.095301 | 0.037552 | 0.068895 | 0.077146 | 0.11958 | 0.0069634 | -0.004587 | -0.57012 | -0.0052782 | 0.052385 | 0.065716 | -0.0013612 | -0.010367 | 63.945 | 64.0823 | -0.041199 | -59.2804 | 64.1052 | -59.1156 | -59.1705 | -59.0744 | 0.059509 | -59.3491 | 64.119 | 63.9816 | -59.1797 | -59.2346 | -0.036622 | -0.091553 | 0.082398 | 123.1613 | -0.20142 | -0.10986 | -0.07782 | -0.10071 | -0.15564 | 0.096131 | 0.004577 | -0.27008 | -0.11444 | -0.041199 | 123.1842 | 123.024 | 59.0378 | -123.1934 | 123.1979 | 123.0606 | 59.1385 | -123.2574
370.6875 | 123.2712 | -59.0469 | 64.0594 | -0.69816 | 0.012985 | 0.083848 | 0.077146 | 0.12492 | 0.0026914 | 0.001822 | -0.44805 | 6.2833e-05 | 0.067339 | 0.039013 | 0.011456 | -0.011435 | 63.9496 | 64.0915 | -0.022888 | -59.2529 | 64.0869 | -59.1202 | -59.166 | -59.0515 | 0.054932 | -59.3399 | 64.1052 | 63.9862 | -59.1797 | -59.2438 | -0.073242 | -0.11902 | 0.027466 | 123.1384 | -0.20599 | -0.086975 | -0.10986 | -0.13275 | -0.19684 | 0.045777 | -0.004578 | -0.29297 | -0.096131 | -0.073242 | 123.1338 | 122.9965 | 59.024 | -123.2254 | 123.1522 | 123.0331 | 59.1019 | -123.3032
371.6875 | 123.2346 | -59.0698 | 64.0366 | -0.37772 | 0.015121 | 0.076372 | 0.088896 | 0.13881 | -0.0037176 | -0.001382 | -0.49383 | 0.0043348 | 0.053453 | 0.057171 | 0.0018428 | -0.0050264 | 63.9679 | 64.1006 | -0.022888 | -59.2575 | 64.0961 | -59.1202 | -59.1568 | -59.0561 | 0.068665 | -59.3399 | 64.1052 | 63.9954 | -59.1888 | -59.2163 | -0.050354 | -0.086975 | 0.059509 | 123.1705 | -0.18768 | -0.10071 | -0.068664 | -0.11902 | -0.14649 | 0.068665 | 0.013733 | -0.27008 | -0.1236 | -0.041199 | 123.1659 | 123.0377 | 59.0469 | -123.1934 | 123.175 | 123.0652 | 59.1385 | -123.2529
372.6875 | 123.2712 | -59.0607 | 64.0045 | -0.33194 | 0.053573 | 0.067827 | 0.077146 | 0.13667 | 0.0091004 | -0.00245 | -0.40227 | -0.0010052 | 0.069475 | 0.055035 | 0.0061158 | -0.011435 | 63.9862 | 64.1327 | 0.004578 | -59.2392 | 64.0869 | -59.1202 | -59.1293 | -59.024 | 0.10071 | -59.3079 | 64.0915 | 63.9999 | -59.1614 | -59.2529 | -0.059509 | -0.068664 | 0.082397 | 123.1934 | -0.17853 | -0.10986 | -0.018311 | -0.10071 | -0.19226 | 0.086975 | 0.036621 | -0.24719 | -0.054931 | -0.004578 | 123.1476 | 123.0469 | 59.0652 | -123.1339 | 123.1522 | 123.0606 | 59.1614 | -123.2574
373.6875 | 123.1979 | -59.1019 | 64.0594 | -0.59134 | 0.039688 | 0.079576 | 0.097441 | 0.13346 | -0.013331 | -0.00245 | -0.41753 | -0.0052782 | 0.061998 | 0.043286 | 0.0039788 | -0.015707 | 63.9633 | 64.0869 | -0.018311 | -59.2804 | 64.0732 | -59.111 | -59.1705 | -59.1019 | 0.3479 | -59.4086 | 64.1556 | 64.0137 | -59.1705 | -59.2392 | -0.009155 | -0.068664 | 0.013733 | 123.1888 | -0.17853 | -0.10986 | -0.09613 | -0.068664 | -0.13733 | 0.096131 | 0 | -0.3067 | -0.16937 | -0.045776 | 123.175 | 123.0652 | 59.0836 | -123.23 | 123.2574 | 123.1155 | 59.4498 | -123.2986
374.6875 | 123.2483 | -59.0927 | 64.0137 | -0.46927 | 0.010849 | 0.096666 | 0.076078 | 0.12278 | -0.0037176 | -0.013132 | -0.47857 | 0.0021988 | 0.063066 | 0.061444 | -0.0013612 | -0.0028904 | 63.9359 | 64.1052 | -0.022888 | -59.2712 | 64.0869 | -59.0881 | -59.1476 | -59.1202 | -0.022888 | -59.3399 | 64.1235 | 63.9999 | -59.1614 | -59.2529 | 0.004577 | -0.054932 | 0.073242 | 123.1979 | -0.17853 | -0.1236 | -0.07782 | -0.068665 | -0.16022 | 0.10986 | -0.027466 | -0.24719 | -0.086975 | -0.013733 | 123.1796 | 123.0286 | 59.0698 | -123.1613 | 123.2162 | 123.0927 | 59.0698 | -123.2666
375.6875 | 123.2941 | -59.0744 | 64.0137 | -0.31669 | 0.045028 | 0.069963 | 0.083555 | 0.12919 | 0.016576 | -0.003518 | -0.3565 | -0.0095502 | 0.063066 | 0.053967 | -0.0067022 | -0.021048 | 64.0182 | 64.1373 | 0.022888 | -59.2575 | 64.0686 | -59.1019 | -59.1476 | -59.024 | 0.07782 | -59.3124 | 64.0915 | 63.9816 | -59.1705 | -59.2117 | -0.027466 | -0.073242 | 0.054932 | 123.2117 | -0.1831 | -0.10986 | 0.004578 | -0.09613 | -0.13733 | 0.07782 | 0.050354 | -0.23804 | -0.10071 | -0.032044 | 123.143 | 123.0927 | 59.0973 | -123.1613 | 123.1659 | 123.056 | 59.1522 | -123.2254
376.6875 | 123.2666 | -59.0378 | 64.0274 | -0.51505 | 0.033279 | 0.057146 | 0.093168 | 0.11958 | 0.0016234 | 0.003958 | -0.21917 | -0.0042092 | 0.070543 | 0.050762 | 0.0029108 | -0.011435 | 64.0137 | 64.1235 | 0 | -59.2392 | 64.1052 | -59.1202 | -59.1568 | -59.0286 | 0.082397 | -59.3124 | 64.1006 | 63.9954 | -59.1156 | -59.2438 | -0.082397 | -0.11902 | 0.07782 | 123.1613 | -0.20142 | -0.082398 | -0.013733 | -0.07782 | -0.20599 | 0.073242 | 0.009156 | -0.27466 | -0.068665 | -0.032044 | 123.143 | 123.0515 | 59.0378 | -123.1842 | 123.1384 | 123.0331 | 59.1202 | -123.2712
377.6875 | 123.2071 | -59.0881 | 64.0228 | -0.28617 | 0.049301 | 0.07744 | 0.070738 | 0.11958 | 0.0026914 | 0.003958 | -0.24969 | 0.0021988 | 0.074815 | 0.059307 | 0.0093198 | -0.010367 | 64.0045 | 64.1327 | 0.027466 | -59.2438 | 64.0823 | -59.079 | -59.1568 | -59.0286 | 0.073242 | -59.3124 | 64.0823 | 63.9862 | -59.1568 | -59.2529 | 0.009156 | -0.068664 | 0.059509 | 123.2208 | -0.15564 | -0.086975 | -0.01831 | -0.068664 | -0.16479 | 0.059509 | 0.05951 | -0.2243 | -0.059509 | -0.036621 | 123.1705 | 123.0927 | 59.1156 | -123.1796 | 123.1705 | 123.0743 | 59.1614 | -123.2758
378.6875 | 123.2483 | -59.0286 | 64.032 | -0.22513 | 0.029007 | 0.064622 | 0.083555 | 0.13026 | 0.0069634 | 0.009299 | -0.15813 | 0.0011308 | 0.056658 | 0.044354 | 0.0018428 | -0.0082304 | 64.0137 | 64.1281 | 0.018311 | -59.2484 | 64.0732 | -59.0881 | -59.1431 | -59.0836 | 0.004578 | -59.2941 | 64.0778 | 63.9908 | -59.166 | -59.2072 | -0.05951 | -0.11444 | 0.041199 | 123.1567 | -0.21973 | -0.10529 | -0.01831 | -0.13733 | -0.17853 | 0.045777 | -0.054932 | -0.2655 | -0.086975 | -0.041198 | 123.1018 | 123.0423 | 59.0469 | -123.175 | 123.1064 | 123.0194 | 59.0332 | -123.2391
379.6875 | 123.2437 | -59.0561 | 64.0137 | -0.13358 | 0.042892 | 0.06569 | 0.077146 | 0.12812 | 0.0058954 | 0.006095 | -0.81426 | 0.0032668 | 0.068407 | 0.053967 | 0.0039788 | -0.00075443 | 63.9908 | 64.1144 | 0.018311 | -59.2621 | 64.0686 | -59.1156 | -59.1843 | -59.0195 | 0.059509 | -59.2987 | 64.1052 | 63.9862 | -59.1522 | -59.2438 | -0.05951 | -0.12817 | 0.054932 | 123.1705 | -0.20599 | -0.07782 | -0.022888 | -0.096131 | -0.18768 | 0.091553 | 0.036621 | -0.24262 | -0.054932 | -0.027466 | 123.1247 | 123.0469 | 59.0744 | -123.1979 | 123.1613 | 123.0423 | 59.1156 | -123.2574
380.6875 | 123.2529 | -59.0698 | 64.0091 | -0.026769 | 0.057846 | 0.072099 | 0.085691 | 0.12599 | 0.0080314 | 0.010367 | 0.009715 | 0.010744 | 0.071611 | 0.051831 | -0.0024292 | -0.0050264 | 63.9221 | 64.1602 | 0.009155 | -59.2392 | 64.064 | -59.111 | -59.166 | -59.0515 | 0.054932 | -59.3124 | 64.1006 | 63.9862 | -59.166 | -59.2209 | -0.041199 | -0.096131 | 0.054932 | 123.23 | -0.16937 | -0.073242 | -0.086975 | -0.096131 | -0.15106 | 0.091553 | 0.01831 | -0.24262 | -0.091553 | -0.022888 | 123.1338 | 122.9919 | 59.079 | -123.175 | 123.1705 | 123.056 | 59.1248 | -123.23
381.6875 | 123.2574 | -59.0561 | 64.0091 | -0.19462 | 0.02153 | 0.071031 | 0.080351 | 0.13881 | -0.00051261 | 0.007163 | -0.29546 | 6.2833e-05 | 0.07802 | 0.066784 | 0.0050478 | 0.0035186 | 63.9999 | 64.1052 | 0.018311 | -59.2438 | 64.0869 | -59.1156 | -59.1797 | -59.0378 | 0.091553 | -59.2896 | 64.0778 | 64.0137 | -59.166 | -59.2255 | -0.05951 | -0.1236 | 0.07782 | 123.1613 | -0.18768 | -0.064087 | -0.009155 | -0.10986 | -0.16937 | 0.068665 | 0.01831 | -0.23346 | -0.064087 | 0.004578 | 123.143 | 123.056 | 59.0744 | -123.1888 | 123.1338 | 123.0698 | 59.1476 | -123.2346
382.6875 | 123.2162 | -59.079 | 64.0228 | -0.22513 | 0.037552 | 0.080644 | 0.085691 | 0.12599 | 0.0058954 | -0.001382 | -0.18865 | -0.0020732 | 0.067339 | 0.051831 | 0.0018428 | -0.010367 | 63.9771 | 64.0961 | -0.004578 | -59.2575 | 64.0594 | -59.1019 | -59.166 | -59.0515 | 0.022888 | -59.3262 | 64.1006 | 63.9862 | -59.1614 | -59.2392 | -0.022889 | -0.086976 | 0.036621 | 123.175 | -0.17853 | -0.091552 | -0.045776 | -0.082398 | -0.16022 | 0.07782 | 0.027465 | -0.24719 | -0.086975 | -0.036621 | 123.1384 | 123.056 | 59.0744 | -123.1888 | 123.1796 | 123.0652 | 59.1019 | -123.262
383.6875 | 123.1979 | -59.0927 | 63.9954 | -0.01151 | 0.042892 | 0.071031 | 0.068601 | 0.1356 | 0.013372 | -0.003518 | 0.31489 | -0.0042092 | 0.073747 | 0.043286 | -0.0056342 | -0.0071624 | 63.945 | 64.0366 | -0.091553 | -59.2896 | 64.0732 | -59.1064 | -59.1522 | -59.1202 | -0.082397 | -59.4177 | 64.0869 | 64.0091 | -59.2026 | -59.2621 | -0.013733 | -0.05951 | 0.07782 | 123.1293 | -0.19684 | -0.13733 | -0.050354 | -0.10986 | -0.16937 | 0.091553 | -0.027466 | -0.32501 | -0.15564 | 0.013733 | 123.1659 | 123.0377 | 59.0012 | -123.1476 | 123.1796 | 123.1018 | 59.0103 | -123.2574
384.7031 | 123.3673 | -59.0103 | 64.0045 | -0.072545 | -0.005173 | -0.20775 | 0.065397 | 0.12065 | -0.038966 | -0.007791 | 0.040232 | -0.010618 | 0.042772 | 0.050762 | -0.010974 | -0.0050264 | 64.0045 | 64.1922 | 0.059509 | -59.2117 | 64.0411 | -59.0515 | -59.1248 | -58.96 | 0.19684 | -59.1888 | 64.0594 | 64.0045 | -59.1248 | -59.1705 | -0.041199 | -0.11444 | 0.036621 | 123.2025 | -0.20142 | -0.086975 | 0 | -0.11444 | -0.16022 | 0.054931 | 0.050354 | -0.17853 | -0.018311 | 0 | 123.0515 | 123.0148 | 59.0698 | -123.1293 | 123.0698 | 123.0148 | 59.2072 | -123.175
385.6875 | 123.175 | -59.0927 | 63.9999 | 0.080043 | 0.027939 | 0.068895 | 0.084623 | 0.13774 | 0.013372 | -0.004587 | 0.14704 | -0.0042092 | 0.071611 | 0.059307 | 0.0093198 | -0.0039584 | 63.9404 | 63.9633 | -0.11444 | -59.3308 | 64.0823 | -59.1339 | -59.1843 | -59.111 | -0.082397 | -59.3994 | 64.0823 | 64.0228 | -59.2117 | -59.2392 | -0.041199 | -0.091553 | 0.082397 | 123.056 | -0.23804 | -0.14648 | -0.059509 | -0.11902 | -0.14648 | 0.082397 | -0.018311 | -0.3067 | -0.16022 | 0.022888 | 123.175 | 123.0331 | 58.9783 | -123.1842 | 123.175 | 123.1155 | 59.0103 | -123.2391
386.6875 | 123.1659 | -59.1156 | 63.9587 | 0.21737 | 0.048233 | 0.06569 | 0.082487 | 0.13133 | 0.01444 | -0.005655 | 0.19282 | 0.0011308 | 0.067339 | 0.059307 | 0.011456 | -0.018912 | 63.9359 | 63.9771 | -0.12817 | -59.3262 | 64.0823 | -59.111 | -59.1797 | -59.1156 | -0.091553 | -59.3903 | 64.0915 | 63.9999 | -59.2026 | -59.2667 | 0.004578 | -0.064086 | 0.1236 | 123.0927 | -0.21057 | -0.14648 | -0.022888 | -0.086975 | -0.15106 | 0.13275 | 0 | -0.27466 | -0.1236 | 0.041199 | 123.1979 | 123.0515 | 58.9874 | -123.1384 | 123.2071 | 123.1155 | 59.024 | -123.2254
387.6875 | 123.2162 | -59.0744 | 64.0091 | -0.042028 | 0.036484 | 0.06569 | 0.093168 | 0.11638 | 0.010168 | 0.00075395 | 0.07075 | -0.0031412 | 0.070543 | 0.061444 | 0.0039788 | -0.017843 | 63.9587 | 64.0366 | -0.064087 | -59.285 | 64.0732 | -59.1019 | -59.1568 | -59.0927 | -0.032043 | -59.3765 | 64.0915 | 64.0411 | -59.1843 | -59.2621 | -0.027466 | -0.082397 | 0.064087 | 123.111 | -0.21057 | -0.12817 | -0.050354 | -0.10986 | -0.18768 | 0.082398 | -0.01831 | -0.30212 | -0.11444 | 0.032044 | 123.1476 | 123.0331 | 59.0103 | -123.1659 | 123.1659 | 123.1155 | 59.0424 | -123.2712
388.6875 | 123.1934 | -59.0744 | 64.0091 | 0.27841 | 0.025802 | 0.057146 | 0.071806 | 0.11851 | 0.0016234 | -0.001382 | 0.19282 | -0.015959 | 0.072679 | 0.049694 | -0.0099062 | 0.00031457 | 63.9313 | 63.9999 | -0.11444 | -59.3124 | 64.0778 | -59.1202 | -59.166 | -59.1293 | -0.009155 | -59.3765 | 64.1006 | 64.032 | -59.1888 | -59.2438 | -0.045776 | -0.091553 | 0.068665 | 123.0743 | -0.23804 | -0.14648 | -0.07782 | -0.11444 | -0.16937 | 0.091553 | -0.054931 | -0.30212 | -0.13275 | 0.022888 | 123.1522 | 123.0057 | 58.96 | -123.175 | 123.175 | 123.1064 | 59.0652 | -123.2529
389.7031 | 123.3673 | -59.0286 | 63.9908 | -0.11832 | 0.022598 | 0.080644 | 0.062193 | 0.12919 | -0.04217 | -0.005655 | 0.024973 | -0.011686 | 0.054521 | 0.057171 | -0.0099062 | 0.00031457 | 64.0182 | 64.1464 | 0.064087 | -59.2209 | 64.0274 | -59.0836 | -59.111 | -58.9554 | 0.11444 | -59.2163 | 64.032 | 64.0091 | -59.1156 | -59.1843 | -0.054932 | -0.082398 | 0.036621 | 123.175 | -0.19226 | -0.10986 | 0.027466 | -0.086976 | -0.15564 | 0.041198 | 0.073242 | -0.18768 | -0.032044 | 0.01831 | 123.056 | 123.0469 | 59.0927 | -123.1018 | 123.0606 | 123.0377 | 59.1431 | -123.175
390.6875 | 123.3261 | -59.0607 | 63.9496 | -0.087804 | 0.014053 | 0.063554 | 0.083555 | 0.1324 | -0.0090576 | -0.00245 | 0.40644 | -0.0063462 | 0.064134 | 0.0294 | 0.010388 | -0.011435 | 64.0366 | 64.1327 | 0.013733 | -59.2255 | 63.9954 | -59.0744 | -59.1522 | -58.9874 | 0.027466 | -59.2758 | 64.0274 | 63.9359 | -59.1705 | -59.2346 | -0.013733 | -0.091553 | 0.045776 | 123.1934 | -0.1648 | -0.073242 | 0.086975 | -0.10986 | -0.17395 | 0.07782 | 0.073242 | -0.21515 | -0.041199 | -0.013733 | 123.056 | 123.0972 | 59.0744 | -123.1018 | 123.0881 | 122.9965 | 59.0881 | -123.1842
391.6875 | 123.2758 | -59.0378 | 63.9816 | 0.41574 | 0.033279 | 0.066759 | 0.093168 | 0.13133 | 0.0037594 | -0.004587 | 0.34541 | -0.0052782 | 0.075884 | 0.061444 | 0.0029108 | -0.018912 | 63.9725 | 64.0503 | -0.059509 | -59.2804 | 64.0411 | -59.1064 | -59.1522 | -59.0149 | -0.009155 | -59.3033 | 64.0457 | 63.9725 | -59.1705 | -59.2484 | -0.068664 | -0.11444 | 0.05951 | 123.0881 | -0.24262 | -0.12817 | -0.009155 | -0.13275 | -0.21057 | 0.064087 | 0.022888 | -0.2655 | -0.054932 | -0.009155 | 123.0789 | 123.0103 | 58.9783 | -123.1338 | 123.0835 | 123.0103 | 59.0286 | -123.23
392.6875 | 123.3215 | -59.0652 | 63.9679 | 0.38522 | 0.022598 | 0.053941 | 0.077146 | 0.13667 | -0.0015816 | 0.007163 | 0.39118 | -0.0042092 | 0.066271 | 0.052899 | 0.0071838 | -0.013571 | 63.9816 | 64.0686 | -0.045776 | -59.2987 | 64.0274 | -59.1156 | -59.1888 | -58.9966 | 0 | -59.2896 | 64.0274 | 63.9862 | -59.1522 | -59.23 | -0.050354 | -0.1236 | 0.059509 | 123.1339 | -0.23346 | -0.10986 | 0.013732 | -0.086975 | -0.16479 | 0.059509 | 0.068665 | -0.2243 | -0.059509 | 0.01831 | 123.0927 | 123.0469 | 59.0195 | -123.1567 | 123.0927 | 123.0515 | 59.0652 | -123.1979
393.6875 | 123.317 | -59.079 | 63.9496 | 0.431 | 0.041824 | 0.058214 | 0.080351 | 0.13346 | -0.0015816 | -0.00031405 | 0.33015 | -0.0042092 | 0.055589 | 0.044354 | 0.0039788 | -0.0092984 | 64.0091 | 64.0549 | -0.036621 | -59.2758 | 64.0182 | -59.0927 | -59.166 | -58.9966 | -0.018311 | -59.3445 | 64.0411 | 63.945 | -59.1797 | -59.2392 | -0.013733 | -0.086976 | 0.068665 | 123.1338 | -0.19684 | -0.10986 | 0.059509 | -0.10071 | -0.16022 | 0.091553 | 0.082397 | -0.2655 | -0.10529 | -0.004578 | 123.0972 | 123.0881 | 59.0424 | -123.1155 | 123.1201 | 123.024 | 59.0607 | -123.1888
394.7031 | 123.2437 | -59.0515 | 64.0457 | -0.45401 | 0.029007 | 0.069963 | 0.073942 | 0.13026 | -0.010127 | -0.0142 | -0.40227 | -0.0031412 | 0.072679 | 0.066784 | -0.01311 | -0.011435 | 64.032 | 64.1602 | 0.10529 | -59.2346 | 64.0503 | -59.0698 | -59.1385 | -59.0332 | 0.10071 | -59.3033 | 64.1006 | 64.032 | -59.1476 | -59.2392 | -0.01831 | -0.086975 | 0.004578 | 123.2117 | -0.18311 | -0.09613 | -0.013733 | -0.09613 | -0.18768 | 0.054932 | 0.018311 | -0.25177 | -0.064087 | -0.013733 | 123.1018 | 123.0835 | 59.1568 | -123.1842 | 123.1522 | 123.0835 | 59.1522 | -123.2849
395.6875 | 123.2483 | -59.0744 | 63.9908 | 0.30892 | 0.034347 | 0.066759 | 0.073942 | 0.12919 | 0.0091004 | -0.0142 | 0.2386 | -0.0020732 | 0.061998 | 0.056103 | 0.012524 | -0.010367 | 63.945 | 64.0411 | -0.068665 | -59.317 | 64.0457 | -59.1019 | -59.1705 | -59.0744 | -0.064087 | -59.3674 | 64.0503 | 63.9496 | -59.1797 | -59.2529 | -0.027466 | -0.09613 | 0.054931 | 123.1155 | -0.24262 | -0.14648 | -0.045777 | -0.10529 | -0.17853 | 0.059509 | 0 | -0.29297 | -0.11444 | -0.041199 | 123.1201 | 123.0194 | 59.0057 | -123.1613 | 123.1247 | 123.024 | 59.0103 | -123.2437
396.6875 | 123.3261 | -59.0561 | 63.9542 | 0.36996 | 0.029007 | 0.074235 | 0.082487 | 0.11958 | -0.0058536 | -0.015268 | 0.29963 | -0.010618 | 0.068407 | 0.039013 | 0.0050478 | -0.010367 | 64.1006 | 64.1464 | 0.045776 | -59.2117 | 63.9999 | -59.0973 | -59.1476 | -58.96 | 0.050354 | -59.2758 | 64.0182 | 63.9404 | -59.1568 | -59.2438 | -0.041199 | -0.091553 | 0.045776 | 123.2025 | -0.15564 | -0.064087 | 0.14648 | -0.10071 | -0.18768 | 0.064087 | 0.09613 | -0.21973 | -0.032044 | -0.013733 | 123.056 | 123.1567 | 59.1019 | -123.1018 | 123.0743 | 122.9965 | 59.1064 | -123.1979
397.6875 | 123.3307 | -59.0652 | 63.9175 | 2.3383 | 0.040756 | 0.084917 | 0.065397 | 0.13346 | -0.012263 | -0.001382 | 0.48274 | -0.015959 | 0.064134 | 0.048626 | -0.0002932 | -0.017843 | 64.0457 | 64.1373 | 0.07782 | -59.2392 | 63.9908 | -59.0836 | -59.1385 | -58.9874 | 0.045776 | -59.2804 | 64.0091 | 63.9221 | -59.1843 | -59.2484 | -0.01831 | -0.073242 | 0.073242 | 123.2025 | -0.17395 | -0.10071 | 0.12817 | -0.11902 | -0.1831 | 0.091552 | 0.07782 | -0.21515 | -0.032044 | 0.004577 | 123.056 | 123.111 | 59.1431 | -123.056 | 123.0743 | 122.9874 | 59.111 | -123.1659
398.6875 | 123.2895 | -59.0881 | 63.9542 | 0.33944 | 0.02687 | 0.063554 | 0.080351 | 0.12599 | -0.010127 | -0.013132 | 0.29963 | -0.014891 | 0.050249 | 0.052899 | -0.0013612 | -0.0060944 | 63.9908 | 64.1006 | 0.064087 | -59.2804 | 64.0182 | -59.1019 | -59.1705 | -59.0195 | 0.022888 | -59.3079 | 64.0274 | 63.9816 | -59.1797 | -59.23 | -0.013733 | -0.082397 | 0.064087 | 123.1888 | -0.19226 | -0.10986 | 0.036621 | -0.091552 | -0.14191 | 0.073242 | 0.068665 | -0.21973 | -0.077819 | 0.027465 | 123.1064 | 123.0789 | 59.1522 | -123.1247 | 123.1155 | 123.0698 | 59.111 | -123.1842
399.7031 | 123.3261 | -59.024 | 63.9999 | -0.31669 | 0.007644 | 0.063554 | 0.072874 | 0.13346 | -0.026148 | -0.010995 | 2.4969 | -0.014891 | 0.053453 | 0.065716 | -0.0067022 | -0.015707 | 64.064 | 64.2014 | 0.22888 | -59.2117 | 64.0137 | -59.0698 | -59.1156 | -58.9554 | 0.11444 | -59.2438 | 64.0366 | 63.9679 | -59.1522 | -59.198 | -0.045776 | -0.091553 | 0.013733 | 123.2254 | -0.18768 | -0.09613 | 0.064087 | -0.12817 | -0.17395 | 0.036621 | 0.068665 | -0.21973 | -0.045776 | -0.032043 | 123.0377 | 123.0881 | 59.2529 | -123.1155 | 123.0606 | 122.9919 | 59.1385 | -123.1979
400.6875 | 123.2986 | -59.0469 | 63.9404 | 0.49203 | 0.018326 | 0.075304 | 0.080351 | 0.13346 | 0.0026914 | -0.006723 | 0.29963 | -0.010618 | 0.056658 | 0.043286 | 0.0093198 | -0.012503 | 64.032 | 64.1418 | 0.13733 | -59.2621 | 64.0045 | -59.1202 | -59.1293 | -58.9874 | 0.045776 | -59.2987 | 63.9908 | 63.9221 | -59.1934 | -59.2529 | -0.073242 | -0.082397 | 0.064087 | 123.1888 | -0.21515 | -0.13275 | 0.091552 | -0.14648 | -0.20599 | 0.050354 | 0.059509 | -0.25177 | -0.045776 | -0.018311 | 123.0515 | 123.0789 | 59.1843 | -123.0698 | 123.0377 | 122.9691 | 59.0927 | -123.1934
401.6875 | 123.3398 | -59.0561 | 63.9679 | 0.33944 | 0.022598 | 0.06569 | 0.071806 | 0.11958 | 0.0048274 | -0.00245 | 0.29963 | -0.0010052 | 0.054521 | 0.050762 | -0.0034972 | -0.021048 | 64.032 | 64.1327 | 0.14191 | -59.2529 | 63.9999 | -59.111 | -59.198 | -58.9508 | -0.25177 | -59.2163 | 63.9954 | 63.9221 | -59.1843 | -59.2255 | -0.054932 | -0.14191 | 0.032043 | 123.1888 | -0.19684 | -0.054932 | 0.064086 | -0.12817 | -0.16937 | 0.027465 | 0.10529 | -0.16022 | 0.009155 | -0.045777 | 123.056 | 123.0881 | 59.198 | -123.1659 | 123.0515 | 122.9782 | 58.8043 | -123.1934
402.6875 | 123.3398 | -59.0332 | 63.9542 | 0.50729 | 0.012985 | 0.067827 | 0.076078 | 0.12919 | 0.0080314 | -0.003518 | 0.33015 | -0.0010052 | 0.063066 | 0.057171 | 0.013592 | -0.012503 | 64.0411 | 64.1373 | 0.15564 | -59.2529 | 63.9862 | -59.1064 | -59.1705 | -58.9417 | 0.17395 | -59.2575 | 64.0182 | 63.9359 | -59.1614 | -59.2255 | -0.073242 | -0.13733 | 0.032043 | 123.1705 | -0.21973 | -0.082398 | 0.086975 | -0.12817 | -0.19226 | 0.064087 | 0.091553 | -0.2243 | -0.032043 | -0.018311 | 123.0194 | 123.0743 | 59.1888 | -123.1247 | 123.0515 | 122.9691 | 59.2072 | -123.1796
403.6875 | 123.3032 | -59.0378 | 63.9633 | 0.29367 | 0.002304 | 0.06035 | 0.077146 | 0.11103 | -0.0026496 | -0.012063 | 0.07075 | -0.0074142 | 0.051317 | 0.062512 | -0.0024292 | -0.0039584 | 63.9908 | 64.119 | 0.17853 | -59.2712 | 64.0137 | -59.0973 | -59.1385 | -59.0195 | 0.036621 | -59.3124 | 64.032 | 63.945 | -59.1476 | -59.2438 | -0.059509 | -0.10071 | 0.050354 | 123.1567 | -0.23346 | -0.13275 | 0.027466 | -0.10986 | -0.20599 | 0.068664 | 0.018311 | -0.27466 | -0.068665 | -0.018311 | 123.0515 | 123.0286 | 59.2163 | -123.1018 | 123.0698 | 122.9828 | 59.0744 | -123.2071
404.7031 | 123.262 | -59.0515 | 63.9862 | -0.33194 | 0.039688 | 0.071031 | 0.0921 | 0.12065 | 0.01444 | 0.00289 | -0.44805 | -0.0042092 | 0.068407 | 0.058239 | 0.011456 | -0.027456 | 64.0274 | 64.0869 | 0.26093 | -59.2392 | 64.0915 | -59.0927 | -59.166 | -59.024 | 0.1236 | -59.3262 | 64.0778 | 64.0182 | -59.1568 | -59.2392 | -0.041198 | -0.11444 | 0.10529 | 123.1384 | -0.18768 | -0.073242 | 0.041199 | -0.10529 | -0.18768 | 0.091553 | 0.027466 | -0.27466 | -0.086975 | 0.032044 | 123.143 | 123.0789 | 59.3124 | -123.1522 | 123.1293 | 123.0698 | 59.1751 | -123.2254
405.6875 | 123.2712 | -59.0881 | 63.9816 | 0.21737 | -0.010514 | 0.083848 | 0.071806 | 0.11424 | -0.020808 | -0.008859 | 0.20808 | -0.0042092 | 0.048113 | 0.052899 | -0.0067022 | -0.0060944 | 63.9359 | 64.1052 | 0.27466 | -59.2941 | 64.0045 | -59.1019 | -59.1522 | -59.0378 | 0.036621 | -59.3079 | 64.0274 | 63.9633 | -59.1751 | -59.2621 | -0.013733 | -0.064087 | 0.022889 | 123.1934 | -0.20599 | -0.14191 | -0.045776 | -0.086975 | -0.17395 | 0.045777 | 0.050354 | -0.21973 | -0.045776 | -0.01831 | 123.0927 | 123.024 | 59.3628 | -123.1338 | 123.1155 | 123.0515 | 59.1248 | -123.2437
406.6875 | 123.3261 | -59.0652 | 63.9816 | 0.41574 | 0.003372 | 0.079576 | 0.077146 | 0.14094 | -0.013331 | -0.010995 | 0.14704 | -0.013823 | 0.064134 | 0.053967 | -0.0013612 | -0.0082304 | 63.9542 | 64.1281 | 0.37994 | -59.2621 | 64.0457 | -59.0927 | -59.1385 | -59.0012 | 0.073242 | -59.2758 | 64.0411 | 63.9587 | -59.1568 | -59.23 | -0.027465 | -0.073242 | 0.064087 | 123.1934 | -0.19684 | -0.1236 | -0.027465 | -0.091552 | -0.16479 | 0.05951 | 0.064087 | -0.21057 | -0.045776 | -0.022888 | 123.111 | 123.0194 | 59.4452 | -123.1201 | 123.1064 | 123.024 | 59.1385 | -123.2117
407.6875 | 123.3032 | -59.0698 | 63.9633 | 0.095301 | 0.016189 | 0.081712 | 0.080351 | 0.12065 | 0.0016234 | -0.0142 | 0.17756 | -0.017027 | 0.071611 | 0.056103 | -0.0056342 | -0.0082304 | 63.9633 | 64.0961 | 0.44403 | -59.2896 | 64.0549 | -59.0973 | -59.1293 | -59.0332 | 0.027466 | -59.317 | 64.032 | 63.9359 | -59.1705 | -59.2758 | -0.027466 | -0.059509 | 0.091553 | 123.1659 | -0.21973 | -0.16022 | 0 | -0.10071 | -0.20599 | 0.068664 | 0.036621 | -0.24719 | -0.041199 | -0.027466 | 123.1247 | 123.0331 | 59.5139 | -123.0927 | 123.1018 | 123.0057 | 59.0973 | -123.2391
408.6875 | 123.2803 | -59.0561 | 63.9542 | 0.38522 | 0.011917 | 0.055009 | 0.086759 | 0.12812 | -0.011195 | -0.00245 | 0.20808 | -0.0052782 | 0.04384 | 0.052899 | -0.0056342 | -0.0028904 | 63.9954 | 64.119 | 0.57678 | -59.2758 | 63.9862 | -59.1064 | -59.1797 | -59.0012 | 0.036621 | -59.3079 | 64.0137 | 63.9313 | -59.1614 | -59.2712 | -0.050354 | -0.1236 | 0.032043 | 123.175 | -0.21973 | -0.096131 | 0.041198 | -0.10529 | -0.21515 | 0.059509 | 0.054931 | -0.25177 | -0.036621 | -0.022889 | 123.0423 | 123.0515 | 59.6329 | -123.1338 | 123.0698 | 122.9874 | 59.0927 | -123.2254
409.6875 | 123.2803 | -59.0469 | 63.9633 | -0.01151 | -0.001969 | 0.06035 | 0.066465 | 0.11851 | -0.0090576 | -0.013132 | 0.10127 | -0.020231 | 0.06093 | 0.056103 | 0.012524 | -0.013571 | 63.9771 | 64.0915 | 0.69122 | -59.2804 | 64.0091 | -59.1064 | -59.1568 | -59.0286 | 0.041199 | -59.3308 | 64.064 | 63.9221 | -59.1614 | -59.2392 | -0.059509 | -0.10986 | 0.045776 | 123.1384 | -0.23346 | -0.1236 | 0.013733 | -0.11444 | -0.19226 | 0.10071 | 0.018311 | -0.28381 | -0.091553 | -0.041199 | 123.056 | 123.024 | 59.7382 | -123.1201 | 123.111 | 122.9691 | 59.0881 | -123.2025
410.6875 | 123.3398 | -59.0424 | 63.9587 | 0.049525 | -0.003037 | 0.066759 | 0.072874 | 0.12919 | -0.011195 | -0.023813 | -0.005544 | -0.023436 | 0.054521 | 0.06892 | -0.0002932 | -0.012503 | 63.9816 | 64.1052 | 0.83313 | -59.2758 | 64.0182 | -59.0881 | -59.1522 | -59.0012 | 0.091553 | -59.2804 | 64.0549 | 63.9587 | -59.166 | -59.2484 | -0.045777 | -0.10986 | 0.05951 | 123.1476 | -0.23346 | -0.1236 | 0.022888 | -0.1236 | -0.20599 | 0.096131 | 0.041198 | -0.23804 | -0.032044 | 0 | 123.0606 | 123.024 | 59.8755 | -123.111 | 123.0972 | 123.0011 | 59.1339 | -123.2071
411.6875 | 123.3627 | -59.0698 | 63.9633 | 0.0037495 | -0.001969 | 0.075304 | 0.076078 | 0.11851 | -0.0026496 | -0.016336 | -0.081838 | -0.012754 | 0.053453 | 0.050762 | 0.0029108 | -0.0092984 | 63.9862 | 64.1144 | 0.97504 | -59.2758 | 64.0091 | -59.111 | -59.1797 | -59.0012 | 0.10071 | -59.2712 | 64.0274 | 63.9359 | -59.1705 | -59.2346 | -0.041199 | -0.10986 | 0.045776 | 123.1842 | -0.20599 | -0.096131 | 0.022888 | -0.10071 | -0.1648 | 0.064087 | 0.068664 | -0.20142 | -0.036621 | -0.027466 | 123.0789 | 123.056 | 60.0449 | -123.143 | 123.0972 | 123.0057 | 59.1705 | -123.1979
412.6875 | 123.3398 | -59.0607 | 63.9679 | 0.095301 | 0.002304 | 0.06569 | 0.060057 | 0.10676 | -0.017603 | -0.013132 | -0.14287 | -0.017027 | 0.049181 | 0.059307 | -0.0024292 | -0.0092984 | 63.9725 | 64.119 | 1.0757 | -59.2621 | 64.0045 | -59.1202 | -59.1476 | -58.9828 | 0.10986 | -59.2758 | 64.032 | 63.9267 | -59.1614 | -59.2438 | -0.059509 | -0.086975 | 0.036621 | 123.1796 | -0.20142 | -0.11444 | 0.004577 | -0.10071 | -0.18311 | 0.064086 | 0.07782 | -0.21515 | -0.032044 | -0.041199 | 123.0652 | 123.0331 | 60.1364 | -123.1155 | 123.0927 | 122.9874 | 59.1705 | -123.2117
413.6875 | 123.3536 | -59.0469 | 63.9404 | 0.0037495 | -0.00090105 | 0.071031 | 0.079283 | 0.11958 | -0.0079896 | -0.005655 | -0.11236 | -0.015959 | 0.057726 | 0.059307 | 0.0018428 | -0.011435 | 63.9954 | 64.1281 | 1.1719 | -59.2667 | 64.0366 | -59.0973 | -59.1522 | -58.9966 | 0.10071 | -59.2667 | 64.0366 | 63.9221 | -59.1751 | -59.2667 | -0.050354 | -0.10529 | 0.09613 | 123.175 | -0.21973 | -0.11444 | 0.054931 | -0.12817 | -0.21973 | 0.09613 | 0.050354 | -0.21973 | 0 | -0.018311 | 123.0835 | 123.0423 | 60.2188 | -123.0927 | 123.0835 | 122.9691 | 59.1476 | -123.2071
414.6875 | 123.3078 | -59.0561 | 63.9816 | 0.11056 | 0.007644 | 0.069963 | 0.078214 | 0.12919 | -0.010127 | -0.010995 | 1.322 | -0.010618 | 0.048113 | 0.051831 | 0.0050478 | -0.0060944 | 63.9587 | 64.1144 | 1.2131 | -59.285 | 64.0228 | -59.1064 | -59.1522 | -59.0332 | 0.045776 | -59.3216 | 64.0366 | 63.9221 | -59.1705 | -59.2484 | -0.050354 | -0.096131 | 0.041199 | 123.1705 | -0.22888 | -0.13275 | -0.022888 | -0.11444 | -0.19226 | 0.054932 | 0.022888 | -0.2655 | -0.073242 | -0.059509 | 123.0789 | 123.0148 | 60.2692 | -123.1338 | 123.0927 | 122.9782 | 59.1019 | -123.23
415.6875 | 123.2895 | -59.0607 | 63.9908 | 0.14108 | -0.01265 | 0.074235 | 0.068601 | 0.12492 | -0.0058536 | -0.00031405 | 0.69636 | -0.010618 | 0.048113 | 0.060376 | 0.0061158 | -0.0092984 | 63.9725 | 64.1006 | 1.2497 | -59.2667 | 64.064 | -59.0881 | -59.1522 | -59.0195 | 0.027466 | -59.2941 | 64.0274 | 63.9313 | -59.1705 | -59.2255 | -0.027466 | -0.091553 | 0.073242 | 123.1613 | -0.20599 | -0.11444 | -0.018311 | -0.10986 | -0.1648 | 0.036621 | 0.041199 | -0.23346 | -0.068664 | -0.05951 | 123.1247 | 123.0331 | 60.3104 | -123.143 | 123.0881 | 122.9919 | 59.0881 | -123.2162
416.6875 | 123.3582 | -59.0469 | 63.9771 | -0.072545 | -0.01265 | 0.069963 | 0.079283 | 0.12172 | -0.0090576 | -0.00245 | -0.23443 | -0.012754 | 0.056658 | 0.058239 | 0.0007748 | -0.014639 | 64.0228 | 64.1418 | 1.2543 | -59.2484 | 64.0274 | -59.0881 | -59.1248 | -58.9645 | 0.10529 | -59.2484 | 64.0594 | 63.913 | -59.1339 | -59.2392 | -0.041199 | -0.07782 | 0.050354 | 123.1888 | -0.20142 | -0.1236 | 0.045776 | -0.086975 | -0.19226 | 0.082397 | 0.082397 | -0.20142 | -0.009155 | -0.064087 | 123.0743 | 123.0698 | 60.3012 | -123.1018 | 123.1064 | 122.9599 | 59.1522 | -123.2162
417.6875 | 123.3765 | -59.024 | 63.9862 | -0.072545 | -0.004105 | 0.073167 | 0.076078 | 0.12172 | -0.0026496 | -0.016336 | -0.21917 | -0.0020732 | 0.032091 | 0.035809 | 0.0050478 | -0.014639 | 64.0869 | 64.2471 | 1.3367 | -59.1843 | 64.0366 | -59.0698 | -59.1248 | -58.9371 | 0.16022 | -59.2163 | 64.064 | 63.9221 | -59.1568 | -59.2163 | -0.045776 | -0.10071 | 0.050354 | 123.2712 | -0.16022 | -0.059509 | 0.10071 | -0.13275 | -0.19226 | 0.07782 | 0.086975 | -0.19226 | 0 | -0.064087 | 123.0606 | 123.111 | 60.3607 | -123.111 | 123.0881 | 122.9462 | 59.1843 | -123.2025
418.6875 | 123.3536 | -59.0012 | 64.0228 | -0.072545 | -0.010514 | 0.084917 | 0.087828 | 0.11851 | 0.0016234 | -0.00031405 | -0.38701 | -0.0084822 | 0.049181 | 0.045422 | 0.0071838 | -0.015707 | 64.0823 | 64.2471 | 1.3687 | -59.198 | 64.0411 | -59.079 | -59.1522 | -58.9325 | 0.16022 | -59.2163 | 64.064 | 63.9313 | -59.1431 | -59.2072 | -0.077819 | -0.15106 | 0.018311 | 123.2483 | -0.19684 | -0.045776 | 0.059509 | -0.14191 | -0.20599 | 0.041199 | 0.068665 | -0.21515 | -0.009156 | -0.091553 | 123.0423 | 123.0835 | 60.3699 | -123.175 | 123.0652 | 122.9324 | 59.1614 | -123.23
419.6875 | 123.4543 | -59.0012 | 64.0411 | -0.45401 | 0.009781 | 0.078508 | 0.056852 | 0.12492 | -0.0058536 | -0.007791 | -0.40227 | -0.010618 | 0.056658 | 0.045422 | 0.0018428 | -0.012503 | 64.1098 | 64.2654 | 1.4328 | -59.2026 | 64.0503 | -59.0607 | -59.1202 | -58.9325 | 0.16022 | -59.2026 | 64.0457 | 63.9359 | -59.1293 | -59.2117 | -0.059509 | -0.11902 | 0.009155 | 123.2666 | -0.20142 | -0.082398 | 0.068664 | -0.12817 | -0.21057 | 0.004577 | 0.068665 | -0.20142 | 0.009155 | -0.10529 | 123.0515 | 123.111 | 60.434 | -123.1613 | 123.0469 | 122.937 | 59.1614 | -123.2529
420.6875 | 123.2483 | -59.0057 | 63.9999 | -0.31669 | 0.012985 | 0.075304 | 0.064329 | 0.13133 | 0.0016234 | -0.007791 | -0.40227 | -0.013823 | 0.036363 | 0.049694 | -0.0056342 | -0.016775 | 64.0961 | 64.2746 | 1.4236 | -59.166 | 64.064 | -59.0515 | -59.1248 | -58.9188 | 0.13275 | -59.2026 | 64.0778 | 63.9587 | -59.0881 | -59.166 | -0.045777 | -0.11902 | 0.064087 | 123.2803 | -0.16022 | -0.041199 | 0.09613 | -0.082398 | -0.16022 | 0.07782 | 0.086975 | -0.19684 | -0.036621 | -0.041199 | 123.0698 | 123.1018 | 60.4294 | -123.1247 | 123.0835 | 122.9645 | 59.1385 | -123.1659
421.6875 | 123.3536 | -59.0195 | 63.9771 | -0.11832 | 0.010849 | 0.081712 | 0.073942 | 0.12812 | -0.0090576 | -0.00245 | -0.15813 | -0.017027 | 0.049181 | 0.050762 | 0.0018428 | -0.016775 | 64.064 | 64.2105 | 1.4053 | -59.2255 | 64.0732 | -59.0652 | -59.1202 | -58.9279 | 0.07782 | -59.2209 | 64.032 | 63.9313 | -59.1339 | -59.1934 | -0.045777 | -0.10071 | 0.09613 | 123.23 | -0.20599 | -0.10529 | 0.086975 | -0.11444 | -0.17395 | 0.054931 | 0.091553 | -0.20142 | -0.027466 | -0.045777 | 123.0927 | 123.0835 | 60.4248 | -123.0972 | 123.0515 | 122.9507 | 59.0973 | -123.1705
422.6875 | 123.3536 | -58.9783 | 64.0045 | -0.14884 | -0.004105 | 0.069963 | 0.058988 | 0.1089 | -0.0026496 | -0.006723 | -0.12761 | -0.0074142 | 0.059862 | 0.048626 | 0.0007748 | -0.014639 | 64.0411 | 64.2151 | 1.4236 | -59.1934 | 64.0686 | -59.0698 | -59.1156 | -58.905 | 0.022888 | -59.1934 | 64.0503 | 63.9221 | -59.1568 | -59.1888 | -0.091553 | -0.13733 | 0.064087 | 123.1934 | -0.21515 | -0.077819 | 0.036621 | -0.17853 | -0.21057 | 0.045776 | 0.073242 | -0.21515 | -0.004577 | -0.082398 | 123.0469 | 123.0194 | 60.4019 | -123.1201 | 123.0286 | 122.9004 | 59.0012 | -123.1934
423.6875 | 123.2895 | -59.0332 | 64.0182 | -0.33194 | 0.014053 | 0.088121 | 0.083555 | 0.12065 | 0.0069634 | 0.005026 | -0.52434 | -0.015959 | 0.047044 | 0.043286 | 0.0029108 | -0.021048 | 64.0549 | 64.2288 | 1.4786 | -59.1934 | 64.0823 | -59.0515 | -59.0927 | -58.9371 | 0.073242 | -59.2392 | 64.1006 | 63.9725 | -59.1431 | -59.1934 | -0.018311 | -0.059509 | 0.064086 | 123.262 | -0.16022 | -0.10071 | 0.036621 | -0.10986 | -0.16022 | 0.082397 | 0.09613 | -0.20599 | -0.045777 | -0.045777 | 123.1155 | 123.0881 | 60.5118 | -123.111 | 123.1338 | 123.0057 | 59.1064 | -123.2117
424.6875 | 123.3124 | -59.0195 | 64.0366 | -0.36246 | 0.016189 | 0.074235 | 0.087828 | 0.12812 | 0.0026914 | -0.004587 | -0.55486 | -0.012754 | 0.0385 | 0.059307 | -0.0034972 | -0.018912 | 64.0549 | 64.2197 | 1.506 | -59.198 | 64.0823 | -59.0515 | -59.1019 | -58.9554 | 0.059509 | -59.2529 | 64.1052 | 63.9771 | -59.1293 | -59.2026 | -0.032044 | -0.082398 | 0.045776 | 123.2391 | -0.17853 | -0.09613 | 0.018311 | -0.10986 | -0.18311 | 0.068665 | 0.064087 | -0.23346 | -0.050354 | -0.059509 | 123.1018 | 123.0743 | 60.5255 | -123.1384 | 123.1247 | 122.9965 | 59.079 | -123.2391
425.6875 | 123.2483 | -59.024 | 64.0549 | -0.4235 | 0.00016795 | 0.073167 | 0.068601 | 0.13133 | 0.0037594 | -0.00245 | -0.60064 | -0.011686 | 0.048113 | 0.051831 | 0.0039788 | -0.017843 | 64.0594 | 64.2197 | 1.5198 | -59.1843 | 64.0915 | -59.0698 | -59.1156 | -58.9645 | 0.054932 | -59.2667 | 64.1098 | 64.0228 | -59.1202 | -59.1934 | -0.045776 | -0.091553 | 0.036621 | 123.2437 | -0.16022 | -0.068664 | 0.004577 | -0.09613 | -0.16937 | 0.054931 | 0.059509 | -0.24262 | -0.073243 | -0.032044 | 123.1155 | 123.0835 | 60.5438 | -123.1705 | 123.1338 | 123.0469 | 59.079 | -123.2483
426.6875 | 123.2529 | -59.0012 | 64.0686 | -0.45401 | 0.016189 | 0.068895 | 0.082487 | 0.13133 | -0.00051261 | -0.007791 | -0.52434 | -0.0042092 | 0.050249 | 0.047558 | 0.0082518 | -0.014639 | 64.0503 | 64.238 | 1.4648 | -59.1888 | 64.1098 | -59.0607 | -59.079 | -58.9691 | 0.013733 | -59.2621 | 64.1235 | 63.9999 | -59.111 | -59.1934 | -0.059509 | -0.077819 | 0.041198 | 123.2391 | -0.18768 | -0.10986 | -0.018311 | -0.10986 | -0.19226 | 0.054931 | 0.032044 | -0.26093 | -0.068665 | -0.068665 | 123.111 | 123.0515 | 60.466 | -123.1476 | 123.1247 | 123.0011 | 59.0149 | -123.262
427.6875 | 123.2391 | -59.0195 | 64.0823 | -0.49979 | 0.029007 | 0.069963 | 0.079283 | 0.12599 | -0.0026496 | -0.00245 | -0.50908 | -0.0052782 | 0.058794 | 0.059307 | 0.0018428 | -0.022116 | 64.0366 | 64.2151 | 1.5381 | -59.1888 | 64.0961 | -59.0698 | -59.111 | -58.9783 | 0.004578 | -59.2529 | 64.1418 | 63.9954 | -59.1293 | -59.2072 | -0.050354 | -0.091553 | 0.013733 | 123.2346 | -0.16937 | -0.07782 | -0.045776 | -0.10986 | -0.18768 | 0.05951 | 0.041199 | -0.23346 | -0.045777 | -0.086975 | 123.1155 | 123.056 | 60.5576 | -123.1934 | 123.1613 | 123.0148 | 59.024 | -123.2895
428.6875 | 123.3078 | -59.0103 | 64.0549 | -0.62186 | 0.031143 | 0.078508 | 0.077146 | 0.11851 | 0.00055539 | -0.00245 | -0.43279 | -0.0074142 | 0.048113 | 0.048626 | 0.0007748 | -0.014639 | 64.0686 | 64.2471 | 1.5747 | -59.1614 | 64.0915 | -59.0515 | -59.1064 | -58.9279 | 0.091553 | -59.2026 | 64.1235 | 63.9862 | -59.0973 | -59.1888 | -0.041199 | -0.09613 | 0.036621 | 123.2574 | -0.15106 | -0.054932 | 0.013733 | -0.086975 | -0.17853 | 0.068664 | 0.082398 | -0.19226 | -0.013733 | -0.068665 | 123.1018 | 123.0789 | 60.585 | -123.1613 | 123.1338 | 122.9965 | 59.1019 | -123.2437
429.6875 | 123.317 | -58.9783 | 64.0594 | -0.3472 | 0.00016795 | 0.076372 | 0.079283 | 0.12278 | -0.0058536 | 0.008231 | -0.41753 | -0.0074142 | 0.057726 | 0.037945 | 0.012524 | -0.0092984 | 64.0869 | 64.2609 | 1.5839 | -59.1522 | 64.0915 | -59.0469 | -59.0652 | -58.9188 | 0.082397 | -59.2026 | 64.151 | 63.9816 | -59.0881 | -59.1888 | -0.068665 | -0.086976 | 0.032044 | 123.2391 | -0.17395 | -0.086975 | 0.027466 | -0.10986 | -0.21057 | 0.091553 | 0.059509 | -0.22431 | -0.013733 | -0.07782 | 123.0698 | 123.0652 | 60.5621 | -123.1247 | 123.1293 | 122.9599 | 59.0607 | -123.2483
430.6875 | 123.2071 | -59.0012 | 64.0915 | -0.4235 | 0.017257 | 0.073167 | 0.081419 | 0.12172 | 0.00055539 | -0.005655 | -0.20391 | -0.011686 | 0.056658 | 0.062512 | 0.0061158 | -0.017843 | 64.0366 | 64.1647 | 1.5976 | -59.2163 | 64.1373 | -59.0424 | -59.0927 | -58.9783 | 0.013733 | -59.2712 | 64.1876 | 64.0594 | -59.1019 | -59.198 | -0.041198 | -0.091552 | 0.045776 | 123.1659 | -0.21515 | -0.1236 | -0.054932 | -0.10071 | -0.19684 | 0.09613 | 0.022889 | -0.27008 | -0.073242 | -0.032044 | 123.1384 | 123.0377 | 60.5988 | -123.1842 | 123.1888 | 123.0606 | 59.0149 | -123.2895
431.6875 | 123.2025 | -59.0149 | 64.0961 | -0.40824 | 0.031143 | 0.076372 | 0.098509 | 0.12706 | 0.025121 | 0.001822 | -0.75323 | -0.0020732 | 0.055589 | 0.04649 | -0.0024292 | -0.017843 | 63.9221 | 64.1144 | 1.5656 | -59.2392 | 64.1373 | -59.0698 | -59.0973 | -58.9966 | -0.041199 | -59.2896 | 64.1739 | 64.0274 | -59.1202 | -59.1797 | -0.054931 | -0.082397 | 0.041199 | 123.1293 | -0.2243 | -0.14191 | -0.17395 | -0.10529 | -0.16479 | 0.07782 | 0.018311 | -0.27466 | -0.10986 | -0.068664 | 123.1522 | 122.937 | 60.5804 | -123.1934 | 123.1888 | 123.0423 | 58.9737 | -123.2758
432.6875 | 123.2346 | -59.0149 | 64.1052 | 0.24789 | 0.016189 | 0.063554 | 0.076078 | 0.14094 | 0.0048274 | -0.009927 | -0.55486 | -0.0063462 | 0.068407 | 0.061444 | 0.0061158 | -0.016775 | 64.0045 | 64.1373 | 1.5335 | -59.2163 | 64.1418 | -59.0652 | -59.1019 | -58.9645 | -0.050354 | -59.2758 | 64.183 | 64.0549 | -59.1385 | -59.1888 | -0.050354 | -0.086975 | 0.036621 | 123.1522 | -0.20142 | -0.11444 | -0.10071 | -0.1236 | -0.17395 | 0.077819 | 0.050354 | -0.26093 | -0.086975 | -0.050354 | 123.1567 | 123.0194 | 60.5484 | -123.2071 | 123.1979 | 123.0698 | 58.9645 | -123.2941
433.6875 | 123.2529 | -59.0012 | 64.1052 | -0.54557 | 0.036484 | 0.062486 | 0.081419 | 0.12385 | 0.0058954 | 0.00289 | -0.57012 | 0.0032668 | 0.074815 | 0.056103 | -0.0024292 | -0.013571 | 64.0137 | 64.1556 | 1.5564 | -59.1934 | 64.1418 | -59.0378 | -59.079 | -58.9966 | -0.013733 | -59.285 | 64.1647 | 64.0686 | -59.0973 | -59.1614 | -0.036621 | -0.077819 | 0.036621 | 123.1567 | -0.19226 | -0.11444 | -0.091553 | -0.09613 | -0.16022 | 0.059509 | 0.004578 | -0.28381 | -0.1236 | -0.036621 | 123.143 | 123.0148 | 60.5576 | -123.1842 | 123.1659 | 123.0698 | 58.9874 | -123.2666
434.6875 | 123.2712 | -59.0012 | 64.1052 | -0.4235 | 0.049301 | 0.06035 | 0.070738 | 0.12812 | 0.00055539 | 0.00075395 | -0.52434 | 0.0011308 | 0.073747 | 0.059307 | 0.010388 | -0.024252 | 64.0045 | 64.1602 | 1.506 | -59.1843 | 64.1602 | -59.0378 | -59.0927 | -58.9828 | -0.041199 | -59.2575 | 64.1739 | 64.0411 | -59.1064 | -59.1751 | -0.036621 | -0.091552 | 0.054931 | 123.1613 | -0.18311 | -0.091553 | -0.10071 | -0.10529 | -0.17395 | 0.068664 | 0.018311 | -0.25635 | -0.082397 | -0.064087 | 123.1613 | 123.0057 | 60.5072 | -123.1979 | 123.175 | 123.0423 | 58.96 | -123.2803
435.6875 | 123.2071 | -59.0057 | 64.1144 | -0.48453 | 0.017257 | 0.075304 | 0.082487 | 0.12065 | 0.0026914 | -0.00031405 | 1.0473 | -0.0031412 | 0.066271 | 0.050762 | -0.0013612 | -0.015707 | 64.0228 | 64.1647 | 1.5198 | -59.2026 | 64.1693 | -59.024 | -59.0881 | -58.9828 | -0.054932 | -59.2575 | 64.183 | 64.0411 | -59.0881 | -59.1705 | -0.018311 | -0.082398 | 0.054932 | 123.1705 | -0.19684 | -0.11444 | -0.091553 | -0.082398 | -0.16479 | 0.068664 | 0.022888 | -0.25177 | -0.086975 | -0.073242 | 123.175 | 123.0286 | 60.5255 | -123.2025 | 123.1888 | 123.0469 | 58.9508 | -123.2849
436.6875 | 123.23 | -58.9828 | 64.1281 | -0.48453 | 0.037552 | 0.079576 | 0.071806 | 0.13133 | -0.014399 | -0.013132 | -0.15813 | -0.0031412 | 0.071611 | 0.043286 | -0.0034972 | -0.012503 | 63.9999 | 64.0961 | 1.4008 | -59.1705 | 64.1922 | -59.0103 | -59.0698 | -58.9691 | -0.041199 | -59.2484 | 64.2014 | 64.0823 | -59.079 | -59.1614 | -0.027466 | -0.086975 | 0.064087 | 123.0789 | -0.18768 | -0.10071 | -0.12817 | -0.09613 | -0.17853 | 0.073242 | 0.013733 | -0.2655 | -0.086975 | -0.045777 | 123.175 | 122.9828 | 60.3836 | -123.1979 | 123.1842 | 123.0652 | 58.9417 | -123.2895
437.6875 | 123.2758 | -58.9874 | 64.1144 | -0.20987 | 0.039688 | 0.068895 | 0.070738 | 0.13453 | 0.01444 | 0.003958 | -0.29546 | 0.0011308 | 0.053453 | 0.044354 | 0.0071838 | -0.011435 | 64.0778 | 64.2242 | 1.4603 | -59.1522 | 64.1693 | -58.9828 | -59.079 | -58.905 | -0.059509 | -59.2209 | 64.1739 | 64.032 | -59.111 | -59.1751 | 0.004578 | -0.091552 | 0.054932 | 123.2117 | -0.1648 | -0.073243 | -0.036621 | -0.1236 | -0.18768 | 0.059509 | 0.082398 | -0.23346 | -0.045776 | -0.082398 | 123.1567 | 123.0652 | 60.4477 | -123.1934 | 123.1613 | 123.0194 | 58.9279 | -123.2895
438.6875 | 123.3032 | -58.9783 | 64.0961 | -0.25565 | 0.02687 | 0.072099 | 0.093168 | 0.12278 | 0.010168 | 0.005026 | 2.1154 | -0.0074142 | 0.06093 | 0.050762 | 0.0007748 | -0.0082304 | 64.0869 | 64.2242 | 1.4282 | -59.1522 | 64.1464 | -58.9966 | -59.0652 | -58.8821 | -0.09613 | -59.2163 | 64.1922 | 64.0778 | -59.0927 | -59.1431 | -0.018311 | -0.086976 | 0.050354 | 123.2025 | -0.17395 | -0.086975 | -0.009155 | -0.11444 | -0.16479 | 0.096131 | 0.09613 | -0.23804 | -0.073243 | -0.01831 | 123.1247 | 123.0652 | 60.4065 | -123.1613 | 123.1705 | 123.056 | 58.8821 | -123.2391
439.6875 | 123.2483 | -58.9462 | 64.1281 | -0.14884 | 0.04396 | 0.073167 | 0.083555 | 0.13346 | 0.039007 | -0.006723 | -0.15813 | -0.0084822 | 0.069475 | 0.053967 | 0.0018428 | -0.014639 | 63.9816 | 64.2746 | 1.4191 | -59.1339 | 64.183 | -58.9966 | -59.0378 | -58.9005 | -0.068665 | -59.2072 | 64.183 | 64.0915 | -59.0652 | -59.1522 | -0.050354 | -0.091553 | 0.054931 | 123.2208 | -0.18768 | -0.09613 | -0.14648 | -0.11902 | -0.20599 | 0.054931 | 0.045776 | -0.26093 | -0.054931 | -0.036621 | 123.1293 | 122.9279 | 60.3653 | -123.1659 | 123.1293 | 123.0377 | 58.8776 | -123.2803
440.6875 | 123.2529 | -58.9783 | 64.0961 | -0.62186 | 0.033279 | 0.061418 | 0.071806 | 0.12919 | 0.0016234 | 0.00075395 | -0.11236 | 0.0043348 | 0.069475 | 0.044354 | 0.0029108 | -0.012503 | 64.0961 | 64.2059 | 1.8585 | -59.1522 | 64.151 | -59.0012 | -59.0744 | -58.9325 | -0.091553 | -59.2255 | 64.1876 | 64.0778 | -59.1202 | -59.1705 | -0.022889 | -0.096131 | 0.054932 | 123.1842 | -0.17395 | -0.07782 | 0 | -0.14191 | -0.19226 | 0.091553 | 0.045776 | -0.24719 | -0.054932 | -0.01831 | 123.1293 | 123.0743 | 60.8368 | -123.1705 | 123.1659 | 123.056 | 58.8867 | -123.2666
441.6875 | 123.2391 | -58.992 | 64.0686 | -0.057287 | 0.056778 | 0.067827 | 0.086759 | 0.12065 | 0.00055539 | 0.00289 | -0.12761 | 0.0011308 | 0.071611 | 0.047558 | 0.0071838 | 0.00031457 | 64.064 | 64.1876 | 1.973 | -59.1568 | 64.1693 | -58.9966 | -59.0607 | -58.9325 | -0.1236 | -59.23 | 64.183 | 64.0686 | -59.0927 | -59.1431 | -0.004578 | -0.068665 | 0.10071 | 123.1796 | -0.16479 | -0.09613 | -0.004578 | -0.10071 | -0.15106 | 0.11444 | 0.059509 | -0.23804 | -0.086976 | 0 | 123.1613 | 123.056 | 60.965 | -123.1293 | 123.175 | 123.0606 | 58.8684 | -123.2117
442.6875 | 123.2849 | -58.9874 | 64.1327 | -0.17936 | 0.049301 | 0.067827 | 0.078214 | 0.13667 | 0.00055539 | 0.00075395 | -0.6159 | -0.0031412 | 0.067339 | 0.051831 | 0.0061158 | -0.017843 | 64.1006 | 64.1922 | 2.1423 | -59.1293 | 64.1556 | -59.0103 | -59.0744 | -58.9096 | -0.082397 | -59.2026 | 64.1922 | 64.0961 | -59.0836 | -59.1339 | -0.022888 | -0.086975 | 0.022889 | 123.1796 | -0.14191 | -0.054931 | -0.032043 | -0.09613 | -0.14648 | 0.05951 | 0.07782 | -0.21515 | -0.068665 | -0.036621 | 123.143 | 123.0881 | 61.1298 | -123.2071 | 123.1796 | 123.0835 | 58.905 | -123.2666
443.6875 | 123.262 | -58.9737 | 64.1235 | -0.13358 | 0.04396 | 0.048601 | 0.070738 | 0.12065 | 0.0016234 | -0.00245 | -0.066579 | -0.0042092 | 0.067339 | 0.058239 | 0.015729 | -0.0050264 | 64.1281 | 64.2151 | 2.2842 | -59.1339 | 64.1785 | -59.0057 | -59.0469 | -58.9279 | -0.068665 | -59.2163 | 64.183 | 64.0961 | -59.0561 | -59.1385 | -0.032043 | -0.073242 | 0.054932 | 123.1888 | -0.16022 | -0.086975 | 0.004578 | -0.082397 | -0.16479 | 0.059509 | 0.045777 | -0.24262 | -0.07782 | -0.027466 | 123.1522 | 123.1018 | 61.2579 | -123.1705 | 123.1567 | 123.0698 | 58.905 | -123.262
444.6875 | 123.1934 | -59.024 | 64.1281 | 0.36996 | 0.051437 | 0.062486 | 0.077146 | 0.11317 | -0.0037176 | -0.00245 | 0.28437 | -0.0031412 | 0.073747 | 0.060376 | 0.0007748 | 0.00031457 | 63.9908 | 64.0686 | 2.4765 | -59.2209 | 64.1418 | -59.0378 | -59.0698 | -59.0424 | -0.50354 | -59.1202 | 64.1418 | 64.0686 | -59.1156 | -59.166 | -0.013733 | -0.045776 | 0.013733 | 123.0927 | -0.19684 | -0.15106 | -0.13733 | -0.091553 | -0.14191 | 0.013733 | -0.01831 | -0.09613 | 0.045777 | -0.059509 | 123.1659 | 123.0148 | 61.5005 | -123.1979 | 123.1659 | 123.0927 | 58.5205 | -123.2941
445.6875 | 123.2208 | -58.992 | 64.0778 | 0.33944 | 0.042892 | 0.058214 | 0.060057 | 0.12919 | -0.0026496 | -0.007791 | -1.0279 | -0.0042092 | 0.061998 | 0.073193 | -0.0056342 | -0.015707 | 64.0091 | 64.0915 | 2.6367 | -59.1934 | 64.151 | -59.024 | -59.111 | -58.9554 | -0.041199 | -59.2712 | 64.1739 | 64.1281 | -59.0927 | -59.1751 | -0.032044 | -0.11902 | 0.073242 | 123.0835 | -0.20142 | -0.082397 | -0.068665 | -0.10071 | -0.18311 | 0.09613 | 0.036621 | -0.27924 | -0.09613 | 0.050354 | 123.143 | 123.0011 | 61.6287 | -123.1888 | 123.1659 | 123.1201 | 58.9508 | -123.2529
446.6875 | 123.2346 | -58.9966 | 64.0778 | 0.29367 | 0.03862 | 0.046464 | 0.062193 | 0.12065 | -0.015467 | -0.008859 | 0.26911 | -0.0095502 | 0.068407 | 0.044354 | 0.0018428 | -0.010367 | 64.0732 | 64.1739 | 2.7603 | -59.1934 | 64.1785 | -59.0332 | -59.0744 | -58.9554 | -0.050354 | -59.2804 | 64.1922 | 64.1281 | -59.1019 | -59.1705 | -0.036621 | -0.07782 | 0.10071 | 123.1705 | -0.19684 | -0.11902 | -0.004578 | -0.10529 | -0.17395 | 0.11444 | 0.041199 | -0.28381 | -0.10986 | 0.050354 | 123.175 | 123.0698 | 61.7569 | -123.1522 | 123.1888 | 123.1247 | 58.9462 | -123.2483
447.6875 | 123.2666 | -58.9783 | 64.0915 | -0.62186 | 0.03862 | 0.071031 | 0.079283 | 0.12599 | 0.0037594 | -0.0142 | 0.29963 | -0.0010052 | 0.049181 | 0.048626 | 0.0018428 | -0.0071624 | 64.0274 | 64.0732 | 2.8976 | -59.2072 | 64.151 | -59.0332 | -59.0607 | -58.9508 | -0.045776 | -59.2804 | 64.183 | 64.119 | -59.0881 | -59.1614 | -0.054932 | -0.082398 | 0.059509 | 123.0515 | -0.22888 | -0.14648 | -0.064087 | -0.10986 | -0.18311 | 0.091552 | 0.027465 | -0.30213 | -0.11902 | 0.027466 | 123.1293 | 123.0057 | 61.8759 | -123.1522 | 123.1613 | 123.0972 | 58.9325 | -123.2529
448.6875 | 123.2437 | -58.9783 | 64.1144 | 0.36996 | 0.025802 | 0.075304 | 0.083555 | 0.11424 | -0.00051261 | -0.013132 | 0.33015 | -0.0031412 | 0.07802 | 0.050762 | -0.0024292 | -0.0050264 | 64.0366 | 64.1144 | 3.0212 | -59.2026 | 64.151 | -59.0012 | -59.0652 | -58.9371 | -0.027466 | -59.2438 | 64.1602 | 64.1281 | -59.0973 | -59.1614 | -0.022889 | -0.086976 | 0.036621 | 123.0927 | -0.22431 | -0.13733 | -0.07782 | -0.11902 | -0.18311 | 0.045776 | 0.041198 | -0.2655 | -0.082397 | 0.013733 | 123.1293 | 123.0148 | 61.9995 | -123.1796 | 123.1384 | 123.1064 | 58.9508 | -123.2758
449.6875 | 123.23 | -58.9783 | 64.0915 | 0.27841 | 0.059982 | 0.064622 | 0.070738 | 0.12812 | 0.0091004 | -0.009927 | 2.0697 | 0.0011308 | 0.074815 | 0.052899 | 0.0018428 | -0.00075443 | 64.0366 | 64.0869 | 3.2043 | -59.198 | 64.1876 | -59.0332 | -59.0652 | -58.9874 | 0.013733 | -59.2804 | 64.1968 | 64.1281 | -59.0836 | -59.1751 | -0.054932 | -0.086976 | 0.09613 | 123.0652 | -0.21973 | -0.13275 | -0.054932 | -0.10529 | -0.19684 | 0.10528 | -0.009156 | -0.30213 | -0.10529 | 0.036621 | 123.1659 | 123.0148 | 62.1826 | -123.1567 | 123.175 | 123.1064 | 58.992 | -123.2666
450.6875 | 123.2895 | -58.9554 | 64.0732 | 0.3547 | 0.046097 | 0.075304 | 0.079283 | 0.13026 | 0.0016234 | -0.009927 | 0.46748 | -0.014891 | 0.067339 | 0.060376 | 0.0093198 | -0.0092984 | 64.0594 | 64.1373 | 3.2959 | -59.1705 | 64.1418 | -58.9966 | -59.0607 | -58.8913 | -0.041199 | -59.2163 | 64.1739 | 64.1006 | -59.0836 | -59.1614 | -0.041199 | -0.10529 | 0.068665 | 123.0927 | -0.21515 | -0.10986 | -0.013733 | -0.12817 | -0.20599 | 0.10071 | 0.064087 | -0.26093 | -0.054932 | 0.027466 | 123.0972 | 123.0148 | 62.2513 | -123.1338 | 123.1293 | 123.056 | 58.9142 | -123.2346
451.6875 | 123.349 | -58.9783 | 64.0091 | 1.1482 | 0.04396 | 0.06569 | 0.062193 | 0.13346 | -0.015467 | -0.00245 | 0.4217 | -0.015959 | 0.058794 | 0.057171 | 0.0082518 | -0.015707 | 64.1006 | 64.2471 | 3.5522 | -59.0927 | 64.119 | -59.0012 | -59.0103 | -58.8364 | 0.027466 | -59.1522 | 64.1281 | 64.1098 | -59.0515 | -59.1431 | -0.022889 | -0.032044 | 0.10986 | 123.2254 | -0.11444 | -0.082397 | 0.091553 | -0.073243 | -0.16479 | 0.11902 | 0.14191 | -0.17395 | -0.009156 | 0.10071 | 123.0972 | 123.0789 | 62.5305 | -123.0194 | 123.1064 | 123.0881 | 59.0057 | -123.1522
452.6875 | 123.349 | -58.9188 | 64.0732 | 0.431 | 0.032211 | 0.053941 | 0.073942 | 0.12706 | -0.0026496 | -0.015268 | 0.46748 | -0.017027 | 0.064134 | 0.065716 | 0.010388 | -0.010367 | 64.1281 | 64.2334 | 3.7033 | -59.1019 | 64.1235 | -58.9828 | -59.0103 | -58.8684 | 0.19684 | -59.111 | 64.151 | 64.0594 | -59.0561 | -59.1293 | -0.064087 | -0.091553 | 0.050354 | 123.1522 | -0.18311 | -0.091553 | 0.054932 | -0.13733 | -0.21057 | 0.07782 | 0.050354 | -0.19226 | 0.01831 | -0.013733 | 123.0423 | 123.0469 | 62.6221 | -123.0835 | 123.0698 | 122.9782 | 59.1156 | -123.2025
453.6875 | 123.3444 | -58.9325 | 64.0594 | 0.44625 | 0.012985 | 0.069963 | 0.073942 | 0.12919 | -0.0058536 | -0.013132 | 0.07075 | -0.025572 | 0.055589 | 0.044354 | 0.0039788 | -0.018912 | 64.1373 | 64.2288 | 3.8223 | -59.1064 | 64.1098 | -58.9508 | -59.0561 | -58.7814 | 0.041199 | -59.1248 | 64.1693 | 64.0915 | -59.0103 | -59.0973 | -0.018311 | -0.1236 | 0.050354 | 123.1613 | -0.17395 | -0.050354 | 0.07782 | -0.07782 | -0.16479 | 0.10986 | 0.15106 | -0.19226 | -0.027466 | 0.032044 | 123.0423 | 123.0698 | 62.7548 | -123.1155 | 123.1018 | 123.024 | 58.9737 | -123.1567
454.6875 | 123.3032 | -58.9142 | 64.0915 | 0.27841 | 0.02153 | 0.06035 | 0.07501 | 0.12278 | -0.020808 | -0.020608 | 0.46748 | -0.0042092 | 0.065202 | 0.048626 | -0.0002932 | -0.00075443 | 64.1373 | 64.2517 | 3.772 | -59.1064 | 64.1144 | -58.9462 | -59.0057 | -58.8135 | -0.082397 | -59.1568 | 64.1693 | 64.0961 | -59.0378 | -59.1156 | -0.032043 | -0.091552 | 0.022888 | 123.1659 | -0.19226 | -0.10071 | 0.045776 | -0.1236 | -0.20142 | 0.07782 | 0.10071 | -0.24261 | -0.041198 | 0.004577 | 123.0286 | 123.0515 | 62.6862 | -123.0972 | 123.0835 | 123.0103 | 58.8318 | -123.2071
455.6875 | 123.3444 | -58.905 | 64.0915 | 0.30892 | 0.024734 | 0.066759 | 0.079283 | 0.13453 | 0.0091004 | -0.0142 | 0.36067 | -0.0063462 | 0.061998 | 0.034741 | 0.013592 | -0.0092984 | 64.1373 | 64.2654 | 3.7308 | -59.0652 | 64.1647 | -58.9371 | -59.0195 | -58.7906 | -0.064087 | -59.1293 | 64.1647 | 64.1006 | -59.0286 | -59.0881 | -0.032044 | -0.11444 | 0.073242 | 123.1705 | -0.16022 | -0.045777 | 0.045776 | -0.1236 | -0.18311 | 0.073242 | 0.11444 | -0.2243 | -0.041198 | 0.009155 | 123.0698 | 123.0423 | 62.6358 | -123.111 | 123.0698 | 123.0057 | 58.8409 | -123.1796
456.6875 | 123.3536 | -58.8959 | 64.0869 | 1.316 | 0.024734 | 0.053941 | 0.083555 | 0.12919 | 0.015508 | -0.003518 | 0.29963 | -0.0063462 | 0.072679 | 0.039013 | 0.011456 | -0.013571 | 64.2014 | 64.2609 | 3.6713 | -59.0881 | 64.1327 | -58.9691 | -59.0149 | -58.7723 | -0.13275 | -59.1476 | 64.1602 | 64.1098 | -59.024 | -59.0836 | -0.073242 | -0.11902 | 0.045776 | 123.1567 | -0.19226 | -0.073242 | 0.11444 | -0.12817 | -0.18768 | 0.073242 | 0.1236 | -0.25177 | -0.064087 | 0.022888 | 123.0286 | 123.0972 | 62.5671 | -123.1018 | 123.056 | 123.0057 | 58.7631 | -123.1705
457.6875 | 123.3261 | -58.8913 | 64.1052 | 0.20211 | 0.009781 | 0.06035 | 0.084623 | 0.12812 | -0.0079896 | -0.010995 | 0.39118 | -0.0042092 | 0.064134 | 0.044354 | 0.0050478 | -0.01998 | 64.1693 | 64.2792 | 3.717 | -59.0652 | 64.1464 | -58.905 | -58.992 | -58.7448 | -0.18768 | -59.111 | 64.1968 | 64.1006 | -59.0057 | -59.1064 | -0.013733 | -0.10071 | 0.041198 | 123.1705 | -0.17395 | -0.073243 | 0.064087 | -0.11444 | -0.21515 | 0.091552 | 0.14648 | -0.21973 | -0.004578 | -0.004578 | 123.0377 | 123.0606 | 62.6083 | -123.0972 | 123.0881 | 122.9919 | 58.7036 | -123.2117
458.6875 | 123.2849 | -58.873 | 64.1327 | 0.29367 | 0.048233 | 0.06569 | 0.070738 | 0.11744 | -0.0090576 | -0.003518 | 0.1623 | -0.014891 | 0.047044 | 0.047558 | -0.0002932 | -0.0092984 | 64.1418 | 64.2563 | 3.717 | -59.0881 | 64.2059 | -58.9142 | -58.992 | -58.786 | -0.30212 | -59.1339 | 64.2059 | 64.1556 | -59.0103 | -59.0607 | -0.041199 | -0.11902 | 0.073243 | 123.1293 | -0.21515 | -0.096131 | 0.009156 | -0.13733 | -0.18768 | 0.073243 | 0.086975 | -0.26093 | -0.073242 | 0.022889 | 123.0789 | 123.0148 | 62.59 | -123.1247 | 123.0789 | 123.0286 | 58.5709 | -123.1934
459.6875 | 123.2849 | -58.8867 | 64.151 | 0.21737 | 0.025802 | 0.066759 | 0.084623 | 0.11531 | -0.0079896 | -0.0142 | 0.498 | -0.010618 | 0.049181 | 0.050762 | 0.0039788 | -0.011435 | 64.1739 | 64.2517 | 3.804 | -59.0652 | 64.2059 | -58.905 | -58.96 | -58.7677 | -0.41199 | -59.1431 | 64.2334 | 64.1464 | -59.0012 | -59.0652 | -0.01831 | -0.073242 | 0.054932 | 123.1384 | -0.17853 | -0.10529 | 0.022888 | -0.11444 | -0.17853 | 0.082397 | 0.11902 | -0.25635 | -0.077819 | -0.004578 | 123.0927 | 123.0606 | 62.6907 | -123.111 | 123.1201 | 123.0331 | 58.4747 | -123.2162
460.6875 | 123.2803 | -58.873 | 64.1739 | 0.29367 | 0.019394 | 0.081712 | 0.073942 | 0.1121 | -0.0037176 | -0.005655 | 0.19282 | -0.015959 | 0.051317 | 0.051831 | 0.0029108 | -0.010367 | 64.1876 | 64.3066 | 3.6209 | -59.0469 | 64.2334 | -58.8867 | -58.9417 | -58.7357 | -0.46692 | -59.1202 | 64.2288 | 64.1464 | -58.9966 | -59.0332 | -0.013733 | -0.068664 | 0.059509 | 123.1796 | -0.17395 | -0.10529 | 0.013733 | -0.1236 | -0.16022 | 0.054932 | 0.13733 | -0.24719 | -0.086975 | -0.027466 | 123.1064 | 123.0606 | 62.4939 | -123.1155 | 123.1018 | 123.0194 | 58.4061 | -123.2071
461.6875 | 123.2986 | -58.8409 | 64.1464 | 0.11056 | -0.003037 | 0.068895 | 0.076078 | 0.13133 | -0.0026496 | -0.01954 | 0.1623 | -0.023436 | 0.054521 | 0.053967 | 0.0029108 | -0.013571 | 64.1693 | 64.2975 | 3.6438 | -59.0469 | 64.2471 | -58.8638 | -58.9462 | -58.7219 | -0.54932 | -59.0927 | 64.2471 | 64.1556 | -58.9737 | -59.0332 | -0.022889 | -0.10529 | 0.10071 | 123.1384 | -0.20599 | -0.10071 | 0.022889 | -0.13275 | -0.19226 | 0.10071 | 0.11902 | -0.25177 | -0.059509 | 0.009156 | 123.0881 | 123.0103 | 62.4847 | -123.0927 | 123.0881 | 122.9965 | 58.2916 | -123.1796
462.6875 | 123.2941 | -58.8364 | 64.2014 | 0.56832 | -0.007309 | 0.071031 | 0.06967 | 0.11317 | -0.0015816 | -0.017404 | 0.11653 | -0.018095 | 0.064134 | 0.057171 | 0.0071838 | -0.010367 | 64.2014 | 64.3066 | 3.717 | -59.0378 | 64.238 | -58.8593 | -58.9417 | -58.7173 | -0.55847 | -59.0881 | 64.27 | 64.1739 | -58.96 | -59.0378 | -0.022888 | -0.10529 | 0.036621 | 123.143 | -0.20142 | -0.096131 | 0 | -0.1236 | -0.20142 | 0.068665 | 0.11902 | -0.25177 | -0.050354 | -0.027466 | 123.0743 | 123.0377 | 62.5534 | -123.143 | 123.1064 | 123.0103 | 58.2779 | -123.2391
463.6875 | 123.3078 | -58.8364 | 64.1876 | 0.3547 | 0.012985 | 0.059282 | 0.078214 | 0.12385 | -0.0069216 | -0.006723 | 0.20808 | -0.0063462 | 0.055589 | 0.057171 | -0.0045652 | -0.018912 | 64.2197 | 64.3478 | 3.7354 | -59.024 | 64.2334 | -58.8776 | -58.905 | -58.6853 | -0.62714 | -59.079 | 64.2563 | 64.1876 | -58.9417 | -59.0286 | -0.041198 | -0.068664 | 0.045776 | 123.1842 | -0.18768 | -0.11902 | 0.032044 | -0.10529 | -0.19226 | 0.068665 | 0.15106 | -0.24261 | -0.050354 | 0 | 123.0698 | 123.056 | 62.5717 | -123.0927 | 123.0927 | 123.024 | 58.2092 | -123.2162
464.6875 | 123.2895 | -58.8089 | 64.2014 | 0.1716 | 0.011917 | 0.066759 | 0.064329 | 0.12492 | -0.0090576 | -0.007791 | -0.097097 | -0.019163 | 0.056658 | 0.06358 | -0.0024292 | -0.011435 | 64.2105 | 64.3158 | 3.7262 | -58.9966 | 64.2654 | -58.8501 | -58.9371 | -58.6899 | -0.9613 | -59.079 | 64.2883 | 64.1968 | -58.9371 | -58.992 | -0.041199 | -0.12817 | 0.064087 | 123.1247 | -0.18768 | -0.059509 | 0.009155 | -0.12817 | -0.18311 | 0.086975 | 0.11902 | -0.27008 | -0.086975 | -0.004578 | 123.0743 | 123.0194 | 62.5351 | -123.1384 | 123.0972 | 123.0057 | 57.8476 | -123.1934
465.6875 | 123.3124 | -58.8043 | 64.2059 | 0.0037495 | 0.003372 | 0.075304 | 0.07501 | 0.11744 | -0.015467 | -0.001382 | -0.036062 | -0.024504 | 0.06093 | 0.056103 | 0.0018428 | -0.016775 | 64.2563 | 64.3982 | 3.7445 | -58.9508 | 64.2883 | -58.8409 | -58.8913 | -58.6258 | -0.95673 | -59.0057 | 64.3204 | 64.2105 | -58.9279 | -58.9783 | -0.036621 | -0.086975 | 0.082397 | 123.2025 | -0.14648 | -0.05951 | 0.050354 | -0.1236 | -0.17395 | 0.11444 | 0.17853 | -0.20142 | -0.027466 | 0.004577 | 123.0927 | 123.0606 | 62.5488 | -123.0972 | 123.1247 | 123.0148 | 57.8476 | -123.1842
466.6875 | 123.2895 | -58.7585 | 64.2426 | -0.13358 | -0.00090105 | 0.07744 | 0.070738 | 0.13026 | -0.0037176 | -0.003518 | -0.15813 | -0.019163 | 0.059862 | 0.055035 | -0.0024292 | -0.012503 | 64.2975 | 64.4165 | 3.7033 | -58.9371 | 64.3021 | -58.8318 | -58.9142 | -58.5846 | -0.91553 | -58.9966 | 64.3112 | 64.1922 | -58.905 | -58.9554 | -0.073242 | -0.15564 | 0.059509 | 123.175 | -0.17853 | -0.022888 | 0.054931 | -0.14648 | -0.19684 | 0.068664 | 0.17395 | -0.23804 | -0.041199 | -0.050354 | 123.0606 | 123.056 | 62.4619 | -123.1567 | 123.0698 | 122.9507 | 57.843 | -123.1979
467.6875 | 123.3307 | -58.7448 | 64.2242 | -0.10306 | -0.005173 | 0.084917 | 0.06967 | 0.12385 | -0.0058536 | -0.005655 | -0.14287 | -0.013823 | 0.056658 | 0.035809 | -0.0013612 | -0.011435 | 64.2838 | 64.4028 | 3.7491 | -58.9279 | 64.2929 | -58.7952 | -58.8455 | -58.5663 | -0.9613 | -58.9691 | 64.325 | 64.2014 | -58.9142 | -58.9645 | -0.050354 | -0.10071 | 0.068665 | 123.1476 | -0.1831 | -0.082397 | 0.059509 | -0.16937 | -0.21973 | 0.10071 | 0.17853 | -0.2243 | -0.004577 | -0.022888 | 123.0377 | 123.0286 | 62.4939 | -123.0698 | 123.0698 | 122.9462 | 57.7835 | -123.1888
468.6875 | 123.3261 | -58.7494 | 64.2426 | -0.13358 | -0.004105 | 0.067827 | 0.065397 | 0.12065 | -0.014399 | -0.012063 | -0.20391 | -0.018095 | 0.051317 | 0.036877 | 0.0039788 | -0.014639 | 64.3066 | 64.4714 | 3.7445 | -58.9325 | 64.3112 | -58.8364 | -58.8959 | -58.5571 | -0.99335 | -58.9645 | 64.3341 | 64.2105 | -58.873 | -58.9737 | -0.086975 | -0.14648 | 0.068664 | 123.2208 | -0.18311 | -0.036621 | 0.064087 | -0.1236 | -0.2243 | 0.091552 | 0.19226 | -0.21515 | 0.009155 | -0.032044 | 123.0606 | 123.056 | 62.4939 | -123.1384 | 123.0835 | 122.9599 | 57.756 | -123.2162
469.6875 | 123.3124 | -58.7494 | 64.2654 | -0.026769 | 0.009781 | 0.071031 | 0.073942 | 0.11744 | 0.00055539 | -0.007791 | -0.12761 | -0.020231 | 0.048113 | 0.052899 | 0.0039788 | -0.015707 | 64.2838 | 64.4394 | 3.6575 | -58.9096 | 64.325 | -58.7906 | -58.8638 | -58.5709 | -1.0254 | -58.9783 | 64.3524 | 64.2242 | -58.8684 | -58.9371 | -0.041198 | -0.11444 | 0.059509 | 123.1888 | -0.16022 | -0.045776 | 0.01831 | -0.11902 | -0.18768 | 0.086975 | 0.17853 | -0.22888 | -0.041198 | -0.041199 | 123.0743 | 123.0331 | 62.4069 | -123.1293 | 123.1018 | 122.9736 | 57.724 | -123.2025
470.7031 | 123.2529 | -58.786 | 64.2975 | 0.23263 | 0.04396 | 0.080644 | 0.078214 | 0.12706 | 0.015508 | -0.00031405 | -0.066579 | -0.0074142 | 0.064134 | 0.053967 | 0.045636 | -0.023184 | 64.2426 | 64.3066 | 3.5889 | -58.9737 | 64.3799 | -58.8455 | -58.8867 | -58.8089 | -0.85602 | -59.0607 | 64.3753 | 64.2609 | -58.8959 | -58.9554 | -0.059509 | -0.10071 | 0.082398 | 123.0927 | -0.18768 | -0.086975 | -0.054931 | -0.10986 | -0.16937 | 0.07782 | -0.022888 | -0.27466 | -0.10529 | -0.036621 | 123.1659 | 123.0286 | 62.3749 | -123.1842 | 123.1613 | 123.0469 | 57.93 | -123.2529
471.6875 | 123.3078 | -58.7265 | 64.3204 | -0.39298 | 0.019394 | 0.084917 | 0.083555 | 0.12492 | -0.0069216 | -0.004587 | -0.5396 | -0.012754 | 0.047044 | 0.044354 | 0.0050478 | -0.013571 | 64.4028 | 64.4531 | 3.7582 | -58.8547 | 64.3158 | -58.786 | -58.8318 | -58.5114 | -0.8606 | -58.9279 | 64.357 | 64.2792 | -58.8181 | -58.905 | -0.05951 | -0.10529 | -0.004578 | 123.1796 | -0.12817 | -0.022888 | 0.082397 | -0.091553 | -0.17853 | 0.036621 | 0.21515 | -0.20142 | -0.022888 | -0.041199 | 123.0423 | 123.1293 | 62.4847 | -123.1522 | 123.0835 | 123.0057 | 57.8659 | -123.2254
472.6875 | 123.2208 | -58.7448 | 64.3524 | -0.49979 | 0.002304 | 0.075304 | 0.071806 | 0.11744 | -0.0037176 | 0.00289 | -0.50908 | -0.018095 | 0.050249 | 0.052899 | -0.0067022 | -0.013571 | 64.3204 | 64.4852 | 3.8498 | -58.8501 | 64.3753 | -58.7677 | -58.8318 | -58.5754 | -0.91553 | -58.9966 | 64.389 | 64.2883 | -58.8501 | -58.9142 | -0.022888 | -0.086975 | 0.022888 | 123.23 | -0.10529 | -0.018311 | -0.032043 | -0.10529 | -0.16937 | 0.036621 | 0.16937 | -0.25177 | -0.082397 | -0.064087 | 123.1201 | 123.0652 | 62.5946 | -123.1842 | 123.1338 | 123.0331 | 57.8293 | -123.2666
473.6875 | 123.3215 | -58.699 | 64.325 | 0.11056 | 0.019394 | 0.074235 | 0.071806 | 0.12278 | -0.0047856 | -0.016336 | -0.34124 | -0.014891 | 0.049181 | 0.053967 | -0.0024292 | -0.012503 | 64.3616 | 64.5309 | 3.891 | -58.8272 | 64.3845 | -58.7631 | -58.8272 | -58.5205 | -0.75989 | -58.9005 | 64.4073 | 64.2746 | -58.8135 | -58.9417 | -0.064087 | -0.12817 | 0.059509 | 123.23 | -0.12817 | 0 | 0.036621 | -0.11444 | -0.24261 | 0.082398 | 0.17853 | -0.20142 | 0.041198 | -0.050354 | 123.0835 | 123.0606 | 62.59 | -123.1522 | 123.1064 | 122.9736 | 57.9391 | -123.2666
474.6875 | 123.3032 | -58.6761 | 64.3662 | -0.4235 | 0.025802 | 0.072099 | 0.086759 | 0.12385 | -0.0047856 | -0.009927 | -0.44805 | -0.012754 | 0.052385 | 0.057171 | -0.0013612 | -0.010367 | 64.3524 | 64.5355 | 3.9459 | -58.8318 | 64.3707 | -58.7357 | -58.8226 | -58.5068 | -0.76446 | -58.9096 | 64.3982 | 64.2746 | -58.8364 | -58.8821 | -0.05951 | -0.14648 | 0.004578 | 123.2117 | -0.15564 | -0.009155 | -0.013733 | -0.16022 | -0.20599 | 0.032043 | 0.16937 | -0.23346 | -0.027466 | -0.091553 | 123.0469 | 123.0286 | 62.6221 | -123.1888 | 123.0743 | 122.9507 | 57.9117 | -123.2483
475.7031 | 123.2162 | -58.7494 | 64.3021 | 0.23263 | 0.042892 | 0.067827 | 0.098509 | 0.1121 | 0.018713 | 0.008231 | -0.020803 | 6.2833e-05 | 0.064134 | 0.064648 | 0.018933 | -0.011435 | 64.2517 | 64.357 | 3.8177 | -58.9279 | 64.4302 | -58.8135 | -58.873 | -58.5892 | -1.03 | -59.0424 | 64.4073 | 64.2654 | -58.8776 | -58.9325 | -0.064087 | -0.1236 | 0.12817 | 123.1064 | -0.17853 | -0.054931 | -0.050354 | -0.12817 | -0.18311 | 0.10529 | 0.16022 | -0.29297 | -0.10986 | -0.036621 | 123.1796 | 123.0011 | 62.5671 | -123.175 | 123.1567 | 123.0148 | 57.7194 | -123.2346
476.6875 | 123.349 | -58.7082 | 64.3341 | -0.40824 | 0.033279 | 0.081712 | 0.073942 | 0.12065 | -0.014399 | 0.00075395 | 0.90998 | 0.0021988 | 0.052385 | 0.060376 | -0.0013612 | -0.015707 | 64.3616 | 64.563 | 4.0375 | -58.7769 | 64.389 | -58.7265 | -58.8135 | -58.4747 | -0.80566 | -58.9005 | 64.3616 | 64.3021 | -58.7906 | -58.8959 | -0.01831 | -0.10529 | 0.054932 | 123.2712 | -0.068664 | 0.036622 | 0.027466 | -0.082397 | -0.18768 | 0.027466 | 0.23346 | -0.19226 | -0.004578 | -0.032043 | 123.0972 | 123.0698 | 62.7457 | -123.1476 | 123.0698 | 123.0103 | 57.9025 | -123.23
477.6875 | 123.3261 | -58.6945 | 64.325 | -0.28617 | 0.00016795 | 0.075304 | 0.083555 | 0.12599 | -0.0047856 | -0.004587 | 1.2762 | -0.017027 | 0.055589 | 0.047558 | -0.0013612 | -0.018912 | 64.3616 | 64.5676 | 4.1428 | -58.6075 | 64.4348 | -58.7219 | -58.7723 | -58.4702 | -0.87891 | -58.873 | 64.3799 | 64.2746 | -58.8043 | -58.8867 | -0.027466 | -0.07782 | 0.10986 | 123.262 | 0.086975 | 0.16479 | 0.036621 | -0.10986 | -0.19226 | 0.054932 | 0.2243 | -0.17853 | 0.013733 | -0.050354 | 123.1293 | 123.056 | 62.8372 | -123.0972 | 123.0743 | 122.9691 | 57.8156 | -123.2117
478.6875 | 123.2025 | -58.7219 | 64.3936 | -0.072545 | 0.025802 | 0.068895 | 0.086759 | 0.12812 | 0.00055539 | -0.003518 | -0.57012 | -0.0052782 | 0.054521 | 0.055035 | -0.0002932 | -0.014639 | 64.3524 | 64.444 | 4.1428 | -58.8409 | 64.4623 | -58.7265 | -58.8089 | -58.5434 | -1.0803 | -58.9783 | 64.4897 | 64.3341 | -58.8364 | -58.8684 | -0.004577 | -0.086975 | 0.068664 | 123.1659 | -0.11902 | -0.032043 | -0.041199 | -0.11444 | -0.14648 | 0.09613 | 0.17853 | -0.25635 | -0.10986 | -0.05951 | 123.1842 | 123.0743 | 62.8647 | -123.2025 | 123.2117 | 123.056 | 57.6416 | -123.262
479.6875 | 123.2483 | -58.6395 | 64.4531 | -1.4306 | 0.002304 | 0.073167 | 0.081419 | 0.12065 | 0.0026914 | -0.006723 | -0.52434 | -0.0052782 | 0.071611 | 0.057171 | 0.0071838 | -0.011435 | 64.3021 | 64.4989 | 4.2847 | -58.8364 | 64.4806 | -58.7082 | -58.7769 | -58.5159 | -1.0254 | -58.9554 | 64.4989 | 64.3662 | -58.8043 | -58.8455 | -0.068665 | -0.13733 | 0.027466 | 123.1384 | -0.19684 | -0.05951 | -0.15106 | -0.1648 | -0.20599 | 0.045776 | 0.1236 | -0.31586 | -0.10986 | -0.086975 | 123.1201 | 122.9416 | 62.9242 | -123.23 | 123.1384 | 123.0057 | 57.6141 | -123.2986
480.7031 | 123.1613 | -58.7265 | 64.389 | 0.12582 | 0.046097 | 0.073167 | 0.087828 | 0.13026 | 0.021917 | 0.001822 | -0.097097 | 0.0011308 | 0.081224 | 0.072125 | 0.0061158 | -0.021048 | 64.3112 | 64.4073 | 4.3854 | -58.8593 | 64.4623 | -58.7357 | -58.786 | -58.58 | -1.0712 | -59.0286 | 64.4714 | 64.3341 | -58.8135 | -58.8959 | -0.009156 | -0.05951 | 0.073242 | 123.1338 | -0.13275 | -0.073242 | -0.07782 | -0.086976 | -0.16937 | 0.082398 | 0.14648 | -0.30212 | -0.13275 | -0.054932 | 123.1888 | 123.0377 | 63.1119 | -123.175 | 123.1979 | 123.0606 | 57.6553 | -123.2849
481.6875 | 123.2162 | -58.6899 | 64.4348 | -0.48453 | 0.049301 | 0.069963 | 0.068601 | 0.11744 | -0.013331 | -0.007791 | -0.46331 | -0.0031412 | 0.051317 | 0.043286 | -0.0067022 | -0.010367 | 64.3341 | 64.4897 | 4.5685 | -58.786 | 64.5172 | -58.6899 | -58.7677 | -58.5526 | -1.0025 | -58.96 | 64.4989 | 64.4119 | -58.7631 | -58.8455 | 0 | -0.07782 | 0.082398 | 123.1796 | -0.096131 | -0.018311 | -0.10071 | -0.073243 | -0.15564 | 0.064087 | 0.13733 | -0.27008 | -0.11444 | -0.022888 | 123.2071 | 123.024 | 63.2584 | -123.2025 | 123.1888 | 123.1018 | 57.6874 | -123.2803
482.6875 | 123.2391 | -58.6304 | 64.444 | -0.45401 | 0.016189 | 0.07744 | 0.083555 | 0.12812 | -0.0026496 | -0.005655 | 0.46748 | -0.0063462 | 0.08336 | 0.043286 | 0.0029108 | -0.010367 | 64.3433 | 64.4989 | 4.7058 | -58.7769 | 64.5264 | -58.699 | -58.7631 | -58.5068 | -0.94299 | -58.9417 | 64.4943 | 64.3936 | -58.8043 | -58.8409 | -0.068665 | -0.13275 | 0.082397 | 123.1293 | -0.14648 | -0.013732 | -0.10071 | -0.17395 | -0.21057 | 0.050354 | 0.1236 | -0.31128 | -0.10071 | -0.050354 | 123.1567 | 122.9736 | 63.3362 | -123.2071 | 123.1247 | 123.024 | 57.6874 | -123.2849
483.6875 | 123.2208 | -58.6487 | 64.4714 | -0.45401 | 0.036484 | 0.074235 | 0.085691 | 0.12492 | -0.012263 | -0.004587 | -0.18865 | -0.0063462 | 0.070543 | 0.056103 | 0.0007748 | -0.013571 | 64.3707 | 64.5355 | 4.921 | -58.754 | 64.5081 | -58.6578 | -58.7265 | -58.4656 | -0.75073 | -58.8684 | 64.5401 | 64.4394 | -58.7677 | -58.8226 | -0.009155 | -0.077819 | 0.036621 | 123.1842 | -0.10529 | -0.027466 | -0.10071 | -0.11902 | -0.17395 | 0.068664 | 0.18311 | -0.21973 | -0.045776 | -0.032044 | 123.1567 | 123.0194 | 63.5696 | -123.1979 | 123.1888 | 123.0881 | 57.898 | -123.2941
484.6875 | 123.2117 | -58.6258 | 64.4852 | -0.43876 | 0.019394 | 0.092393 | 0.073942 | 0.12065 | 0.0016234 | 0.009299 | -0.66167 | 0.0011308 | 0.056658 | 0.039013 | -0.0024292 | -0.017843 | 64.3753 | 64.4577 | 5.1498 | -58.7402 | 64.5264 | -58.6899 | -58.7357 | -58.461 | -0.79193 | -58.9142 | 64.5538 | 64.4485 | -58.7357 | -58.7952 | -0.064087 | -0.10986 | 0.041199 | 123.0835 | -0.11444 | -0.004577 | -0.10986 | -0.10986 | -0.16937 | 0.068665 | 0.16479 | -0.28839 | -0.11902 | -0.036621 | 123.1522 | 123.0011 | 63.7756 | -123.2208 | 123.1796 | 123.0743 | 57.8339 | -123.2803
485.7031 | 123.2025 | -58.6395 | 64.4623 | 0.27841 | 0.040756 | 0.069963 | 0.085691 | 0.12278 | 0.0091004 | 0.00289 | 5.0604 | -0.0063462 | 0.063066 | 0.052899 | 0.018933 | -0.0060944 | 64.3707 | 64.4669 | 5.3741 | -58.754 | 64.5309 | -58.6716 | -58.7448 | -58.429 | -0.82855 | -58.9005 | 64.5538 | 64.4302 | -58.7357 | -58.8089 | -0.032044 | -0.10529 | 0.068665 | 123.1064 | -0.11444 | -0.009155 | -0.091552 | -0.096131 | -0.16937 | 0.091553 | 0.21057 | -0.26093 | -0.091553 | -0.032043 | 123.1705 | 123.0103 | 64.0137 | -123.2071 | 123.1934 | 123.0698 | 57.811 | -123.2712
486.6875 | 123.2437 | -58.5892 | 64.4623 | -0.37772 | 0.048233 | 0.07744 | 0.079283 | 0.12065 | 0.011236 | 0.00289 | -0.38701 | 0.0054038 | 0.057726 | 0.053967 | 0.0007748 | -0.012503 | 64.4531 | 64.5767 | 5.5389 | -58.6807 | 64.595 | -58.6395 | -58.6945 | -58.4015 | -0.75531 | -58.8272 | 64.5493 | 64.4897 | -58.6807 | -58.7631 | -0.050354 | -0.10529 | 0.13275 | 123.1659 | -0.091553 | 0.013733 | -0.009155 | -0.091553 | -0.17395 | 0.086975 | 0.18768 | -0.23804 | -0.064086 | 0.027466 | 123.1842 | 123.0423 | 64.1281 | -123.1567 | 123.1384 | 123.0789 | 57.8339 | -123.2254
487.6875 | 123.2346 | -58.58 | 64.4989 | -0.36246 | 0.029007 | 0.075304 | 0.087828 | 0.12385 | 0.00055539 | 0.00075395 | -0.20391 | -0.0020732 | 0.072679 | 0.047558 | 0.0050478 | -0.01998 | 64.4531 | 64.5813 | 5.809 | -58.6716 | 64.5447 | -58.6166 | -58.667 | -58.3832 | -0.74616 | -58.8135 | 64.5401 | 64.476 | -58.7128 | -58.786 | -0.036621 | -0.086975 | 0.045777 | 123.1613 | -0.091553 | -0.004578 | -0.045776 | -0.13275 | -0.20599 | 0.041199 | 0.19684 | -0.23346 | -0.027466 | -0.022888 | 123.1247 | 123.0331 | 64.389 | -123.1659 | 123.1201 | 123.056 | 57.8339 | -123.2849
488.6875 | 123.262 | -58.5709 | 64.5126 | -0.13358 | 0.020462 | 0.071031 | 0.081419 | 0.12278 | 0.0058954 | 0.013571 | -0.29546 | 6.2833e-05 | 0.057726 | 0.043286 | 0.0082518 | -0.028525 | 64.3662 | 64.5996 | 6.189 | -58.6487 | 64.5767 | -58.6121 | -58.6853 | -58.3466 | -0.82855 | -58.8226 | 64.5584 | 64.4577 | -58.6807 | -58.7631 | -0.041199 | -0.11444 | 0.064087 | 123.1705 | -0.07782 | 0.036621 | -0.14648 | -0.10986 | -0.19226 | 0.045777 | 0.2243 | -0.25177 | -0.059509 | -0.054931 | 123.1476 | 122.937 | 64.7598 | -123.1979 | 123.1293 | 123.0286 | 57.7423 | -123.2758
489.6875 | 123.2803 | -58.58 | 64.4852 | -0.27091 | 0.037552 | 0.059282 | 0.081419 | 0.11317 | -0.010127 | 0.00075395 | -0.20391 | 6.2833e-05 | 0.06093 | 0.057171 | 0.014661 | -0.016775 | 64.4394 | 64.5996 | 6.5506 | -58.6487 | 64.563 | -58.6166 | -58.6899 | -58.3282 | -0.91553 | -58.8226 | 64.5813 | 64.4989 | -58.6899 | -58.7494 | -0.036621 | -0.10986 | 0.07782 | 123.1796 | -0.068665 | 0.041198 | -0.045776 | -0.10986 | -0.16937 | 0.096131 | 0.25177 | -0.24262 | -0.073242 | 0.013733 | 123.143 | 123.0194 | 65.1306 | -123.175 | 123.1613 | 123.0789 | 57.6645 | -123.2346
490.7031 | 123.2986 | -58.5892 | 64.4302 | 0.23263 | 0.024734 | 0.056077 | 0.066465 | 0.13346 | -0.027216 | -0.007791 | 0.46748 | -0.017027 | 0.066271 | 0.047558 | -0.0088382 | 0.0056546 | 64.444 | 64.6271 | 6.9946 | -58.6395 | 64.4577 | -58.6258 | -58.667 | -58.3054 | -1.0941 | -58.7677 | 64.5218 | 64.4211 | -58.7082 | -58.7402 | -0.036621 | -0.07782 | 0.027466 | 123.2162 | -0.050354 | 0.027466 | 0.013733 | -0.11902 | -0.15106 | 0.091553 | 0.28381 | -0.17853 | -0.027466 | -0.009155 | 123.0469 | 123.0331 | 65.5838 | -123.0972 | 123.111 | 123.0103 | 57.4951 | -123.1705
491.6875 | 123.2895 | -58.5571 | 64.5172 | -0.56083 | 0.025802 | 0.07744 | 0.076078 | 0.12492 | 0.010168 | 0.001822 | -0.34124 | -0.0074142 | 0.072679 | 0.056103 | 0.0061158 | -0.016775 | 64.5035 | 64.6042 | 7.2647 | -58.5983 | 64.5996 | -58.5892 | -58.6807 | -58.287 | -1.1353 | -58.8043 | 64.5996 | 64.5035 | -58.6578 | -58.7219 | -0.032043 | -0.1236 | 0.082397 | 123.1613 | -0.041199 | 0.082397 | -0.013733 | -0.10071 | -0.16479 | 0.082397 | 0.27008 | -0.24719 | -0.082397 | -0.013733 | 123.1567 | 123.0606 | 65.8218 | -123.1979 | 123.1567 | 123.0606 | 57.4219 | -123.2391
492.6875 | 123.2208 | -58.548 | 64.5035 | -0.4235 | 0.041824 | 0.06569 | 0.077146 | 0.12385 | 0.019781 | -0.007791 | -0.15813 | -0.0042092 | 0.064134 | 0.052899 | 0.0093198 | -0.016775 | 64.4989 | 64.6133 | 7.3929 | -58.6029 | 64.595 | -58.58 | -58.6761 | -58.2916 | -1.1627 | -58.8043 | 64.6179 | 64.5126 | -58.6761 | -58.7448 | -0.032043 | -0.12817 | 0.091553 | 123.1613 | -0.054931 | 0.073242 | -0.004578 | -0.12817 | -0.19684 | 0.11444 | 0.25635 | -0.25635 | -0.059509 | 0.009155 | 123.143 | 123.0469 | 65.9409 | -123.1796 | 123.1659 | 123.0606 | 57.3853 | -123.2483
493.6875 | 123.2391 | -58.5754 | 64.5035 | 0.52255 | 0.054641 | 0.08278 | 0.079283 | 0.12385 | 0.0037594 | -0.00031405 | -0.17339 | -0.0010052 | 0.070543 | 0.049694 | 0.0050478 | -0.010367 | 64.4806 | 64.6042 | 7.5577 | -58.6212 | 64.5493 | -58.5663 | -58.6578 | -58.3145 | -1.236 | -58.8364 | 64.6042 | 64.5035 | -58.6807 | -58.7402 | 0.009155 | -0.082398 | 0.045776 | 123.1796 | -0.045777 | 0.036621 | -0.022888 | -0.10529 | -0.16479 | 0.10071 | 0.26093 | -0.26093 | -0.096131 | 0 | 123.1247 | 123.056 | 66.1331 | -123.1613 | 123.1796 | 123.0789 | 57.3395 | -123.2437
494.6875 | 123.2712 | -58.548 | 64.5126 | -0.51505 | 0.030075 | 0.061418 | 0.077146 | 0.11744 | 0.0048274 | -0.007791 | -0.14287 | -0.0020732 | 0.072679 | 0.043286 | 0.0018428 | -0.0092984 | 64.4852 | 64.6042 | 7.695 | -58.6166 | 64.595 | -58.5846 | -58.6578 | -58.3008 | -1.3412 | -58.8181 | 64.5905 | 64.5401 | -58.6853 | -58.7402 | -0.036621 | -0.10986 | 0.082398 | 123.1522 | -0.068664 | 0.041199 | -0.027466 | -0.13733 | -0.19226 | 0.07782 | 0.24719 | -0.27008 | -0.07782 | 0.027466 | 123.143 | 123.0331 | 66.243 | -123.1705 | 123.1384 | 123.0881 | 57.2067 | -123.2529
495.6875 | 123.2254 | -58.5388 | 64.5447 | -0.53031 | 0.052505 | 0.066759 | 0.086759 | 0.13026 | 0.0091004 | -0.00245 | -0.20391 | -0.0031412 | 0.063066 | 0.053967 | 0.014661 | -0.011435 | 64.5126 | 64.6271 | 7.9605 | -58.5754 | 64.5813 | -58.5846 | -58.6395 | -58.287 | -1.4191 | -58.8043 | 64.6042 | 64.5401 | -58.6624 | -58.7173 | -0.045777 | -0.10071 | 0.036621 | 123.1659 | -0.036621 | 0.064087 | -0.032044 | -0.1236 | -0.17853 | 0.059509 | 0.25177 | -0.2655 | -0.086975 | -0.004578 | 123.1201 | 123.0515 | 66.4993 | -123.1842 | 123.143 | 123.0789 | 57.1198 | -123.262
496.6875 | 123.262 | -58.5251 | 64.5264 | -0.11832 | 0.034347 | 0.069963 | 0.096372 | 0.1121 | 0.0026914 | 0.001822 | -0.18865 | -0.0095502 | 0.080156 | 0.053967 | -0.0034972 | -0.0018224 | 64.5126 | 64.6408 | 8.1985 | -58.5388 | 64.6042 | -58.5526 | -58.6304 | -58.2458 | -1.6434 | -58.7906 | 64.6317 | 64.5676 | -58.667 | -58.6945 | -0.027466 | -0.10529 | 0.07782 | 123.1659 | -0.013733 | 0.091553 | -0.013733 | -0.14191 | -0.16937 | 0.10529 | 0.27923 | -0.2655 | -0.09613 | 0.041199 | 123.1293 | 123.0377 | 66.7236 | -123.1567 | 123.1567 | 123.0927 | 56.8817 | -123.2208
497.6875 | 123.2666 | -58.5205 | 64.5721 | -0.17936 | 0.04396 | 0.058214 | 0.082487 | 0.13453 | 0.0069634 | -0.008859 | -0.2802 | 6.2833e-05 | 0.073747 | 0.04649 | 0.0007748 | -0.0039584 | 64.5081 | 64.6408 | 8.4457 | -58.5388 | 64.6317 | -58.5434 | -58.6166 | -58.2092 | -1.6846 | -58.754 | 64.6362 | 64.5401 | -58.6395 | -58.7128 | -0.022888 | -0.09613 | 0.059509 | 123.1613 | -0.01831 | 0.07782 | -0.064087 | -0.11902 | -0.19226 | 0.064086 | 0.31128 | -0.23346 | -0.041198 | -0.032044 | 123.1522 | 123.0286 | 66.9662 | -123.1888 | 123.1567 | 123.0606 | 56.8359 | -123.2849
498.6875 | 123.2574 | -58.5159 | 64.5355 | 0.034266 | 0.04396 | 0.075304 | 0.066465 | 0.12492 | 0.010168 | -0.00031405 | -0.066579 | -0.0052782 | 0.069475 | 0.044354 | 0.010388 | -0.0071624 | 64.5264 | 64.6271 | 8.5739 | -58.5297 | 64.6133 | -58.5663 | -58.6075 | -58.2321 | -1.9135 | -58.7769 | 64.6408 | 64.563 | -58.6395 | -58.7082 | -0.050354 | -0.091553 | 0.07782 | 123.143 | -0.013733 | 0.07782 | -0.009155 | -0.1236 | -0.19226 | 0.10529 | 0.28381 | -0.26093 | -0.068664 | 0.027466 | 123.1293 | 123.0423 | 67.0898 | -123.143 | 123.1567 | 123.0789 | 56.6025 | -123.2437
499.6875 | 123.1934 | -58.5251 | 64.5676 | 0.12582 | 0.050369 | 0.055009 | 0.083555 | 0.12492 | 0.011236 | -0.00031405 | 0.086009 | -0.0052782 | 0.066271 | 0.057171 | 0.0029108 | -0.0092984 | 64.5172 | 64.5905 | 8.7479 | -58.5205 | 64.6317 | -58.5342 | -58.5983 | -58.2642 | -2.1011 | -58.8364 | 64.6683 | 64.5859 | -58.6349 | -58.7082 | -0.009156 | -0.073243 | 0.064087 | 123.1155 | 0.004577 | 0.07782 | -0.050354 | -0.10986 | -0.18311 | 0.10071 | 0.26093 | -0.31128 | -0.12817 | 0.01831 | 123.1567 | 123.0423 | 67.2729 | -123.1659 | 123.1934 | 123.111 | 56.4239 | -123.2758
500.6875 | 123.1979 | -58.5342 | 64.5996 | 0.080043 | 0.040756 | 0.06569 | 0.077146 | 0.12919 | 0.0058954 | 0.00075395 | 0.024973 | -0.0031412 | 0.072679 | 0.057171 | 0.0061158 | -0.013571 | 64.4943 | 64.5584 | 8.8989 | -58.5251 | 64.6362 | -58.548 | -58.6258 | -58.2596 | -1.5198 | -58.8409 | 64.6683 | 64.595 | -58.6304 | -58.7082 | -0.013733 | -0.091552 | 0.036621 | 123.0927 | 0.009156 | 0.10071 | -0.10528 | -0.09613 | -0.17395 | 0.068665 | 0.27466 | -0.3067 | -0.13275 | -0.004577 | 123.1705 | 123.0286 | 67.4332 | -123.2254 | 123.2025 | 123.1293 | 57.0145 | -123.3078
501.6875 | 123.1934 | -58.5159 | 64.5996 | 0.019007 | 0.042892 | 0.064622 | 0.0921 | 0.11958 | 0.0048274 | -0.008859 | 0.10127 | -0.0074142 | 0.070543 | 0.062512 | 0.0007748 | -0.012503 | 64.4806 | 64.5859 | 9.0775 | -58.5068 | 64.6317 | -58.5434 | -58.5892 | -58.2275 | -1.3504 | -58.8135 | 64.6591 | 64.5859 | -58.6258 | -58.6853 | -0.027466 | -0.073242 | 0.032044 | 123.1018 | 0.009155 | 0.082397 | -0.11902 | -0.10986 | -0.16937 | 0.05951 | 0.28839 | -0.29755 | -0.12817 | -0.013733 | 123.1476 | 122.9965 | 67.5934 | -123.1888 | 123.175 | 123.1018 | 57.1655 | -123.2849
502.6875 | 123.2208 | -58.5251 | 64.5721 | 0.11056 | 0.040756 | 0.061418 | 0.085691 | 0.12172 | 0.0048274 | -0.003518 | 0.13178 | -0.0063462 | 0.059862 | 0.058239 | 0.0007748 | -0.0082304 | 64.476 | 64.5721 | 9.1507 | -58.5388 | 64.6362 | -58.5434 | -58.6121 | -58.255 | -1.4877 | -58.8364 | 64.6637 | 64.5859 | -58.6304 | -58.7173 | -0.018311 | -0.086976 | 0.064086 | 123.0972 | -0.013733 | 0.073243 | -0.096131 | -0.10529 | -0.19226 | 0.091552 | 0.27008 | -0.31128 | -0.11902 | 0.013732 | 123.1613 | 123.0011 | 67.6758 | -123.1842 | 123.1888 | 123.111 | 57.0374 | -123.2895
503.6875 | 123.1796 | -58.5297 | 64.5584 | 0.14108 | 0.050369 | 0.072099 | 0.077146 | 0.12812 | 0.011236 | -0.001382 | 0.22334 | 0.0011308 | 0.076952 | 0.051831 | 0.0071838 | -0.0082304 | 64.4669 | 64.5309 | 9.3567 | -58.5342 | 64.6317 | -58.5709 | -58.6212 | -58.2413 | -1.5198 | -58.8455 | 64.6317 | 64.5859 | -58.6349 | -58.7173 | -0.041199 | -0.091553 | 0.073242 | 123.0606 | -0.004578 | 0.086975 | -0.091553 | -0.10529 | -0.18768 | 0.073242 | 0.28839 | -0.31586 | -0.12817 | 0.027465 | 123.1613 | 122.9965 | 67.8864 | -123.1796 | 123.1613 | 123.1155 | 57.0099 | -123.2758
504.6875 | 123.2071 | -58.5297 | 64.5813 | 0.034266 | 0.070663 | 0.073167 | 0.080351 | 0.11424 | 0.0016234 | 0.001822 | -0.066579 | -0.010618 | 0.071611 | 0.048626 | 0.0082518 | -0.010367 | 64.5172 | 64.6088 | 9.6497 | -58.4839 | 64.6317 | -58.5434 | -58.5846 | -58.1726 | -1.6983 | -58.786 | 64.6408 | 64.5996 | -58.6395 | -58.6945 | -0.013733 | -0.054932 | 0.050354 | 123.1384 | 0.045776 | 0.10071 | -0.064087 | -0.10986 | -0.16479 | 0.059509 | 0.35706 | -0.25635 | -0.091553 | 0.01831 | 123.1613 | 123.0469 | 68.1793 | -123.1659 | 123.1705 | 123.1293 | 56.8314 | -123.2758
505.6875 | 123.2208 | -58.4976 | 64.5996 | -0.56083 | 0.050369 | 0.073167 | 0.094236 | 0.12172 | 0.013372 | -0.006723 | 0.20808 | -0.0031412 | 0.082292 | 0.056103 | 0.0039788 | -0.0028904 | 64.5264 | 64.5767 | 9.787 | -58.4702 | 64.6454 | -58.5251 | -58.5709 | -58.1268 | -1.8311 | -58.7677 | 64.6683 | 64.6179 | -58.6166 | -58.667 | -0.027465 | -0.073242 | 0.045777 | 123.0743 | 0.027466 | 0.10071 | -0.073242 | -0.11902 | -0.16937 | 0.068665 | 0.37079 | -0.27008 | -0.10071 | 0.018311 | 123.143 | 123.024 | 68.2846 | -123.1705 | 123.1659 | 123.1155 | 56.6666 | -123.2666
506.6875 | 123.262 | -58.5205 | 64.5447 | 0.3547 | 0.040756 | 0.073167 | 0.079283 | 0.11531 | -0.0069216 | -0.006723 | 0.31489 | -0.018095 | 0.075884 | 0.056103 | 0.0061158 | -0.0050264 | 64.4623 | 64.5813 | 9.7641 | -58.4839 | 64.6179 | -58.5434 | -58.6212 | -58.1451 | -1.9684 | -58.7906 | 64.6317 | 64.5676 | -58.6624 | -58.7219 | -0.022888 | -0.10071 | 0.073242 | 123.1018 | 0.036621 | 0.13733 | -0.082398 | -0.14191 | -0.20142 | 0.086975 | 0.37537 | -0.27008 | -0.068664 | 0.022888 | 123.1384 | 122.9828 | 68.2846 | -123.1659 | 123.1522 | 123.0881 | 56.5521 | -123.2666
507.6875 | 123.2437 | -58.4656 | 64.5905 | 0.21737 | 0.048233 | 0.068895 | 0.082487 | 0.12919 | 0.00055539 | -0.006723 | 0.33015 | -0.0031412 | 0.066271 | 0.056103 | 0.0061158 | -0.0039584 | 64.5355 | 64.5996 | 9.8969 | -58.4152 | 64.6683 | -58.5159 | -58.58 | -58.0765 | -2.0874 | -58.7585 | 64.6591 | 64.6088 | -58.6029 | -58.6624 | -0.050354 | -0.11444 | 0.07782 | 123.0652 | 0.050354 | 0.16479 | -0.054932 | -0.13733 | -0.19684 | 0.068665 | 0.3891 | -0.29297 | -0.09613 | 0.018311 | 123.1338 | 123.0011 | 68.3624 | -123.1705 | 123.1247 | 123.0743 | 56.3782 | -123.2529
508.6875 | 123.2758 | -58.4381 | 64.5813 | 0.27841 | 0.023666 | 0.072099 | 0.098509 | 0.13453 | 0.0026914 | -0.008859 | 0.37593 | -0.0042092 | 0.068407 | 0.058239 | -0.0067022 | -0.015707 | 64.5447 | 64.6362 | 9.9014 | -58.4198 | 64.6637 | -58.5022 | -58.5526 | -58.0399 | -2.2888 | -58.7128 | 64.6866 | 64.6179 | -58.5892 | -58.6578 | -0.064087 | -0.11444 | 0.082397 | 123.0743 | 0.01831 | 0.13275 | -0.036621 | -0.15106 | -0.21973 | 0.10528 | 0.39825 | -0.27466 | -0.054932 | 0.036621 | 123.1018 | 122.9828 | 68.3395 | -123.1338 | 123.1247 | 123.056 | 56.1493 | -123.2391
509.6875 | 123.2758 | -58.3832 | 64.6545 | 0.29367 | 0.053573 | 0.075304 | 0.077146 | 0.12385 | 0.0048274 | 0.00289 | 0.4217 | -0.0074142 | 0.068407 | 0.057171 | 0.0061158 | -0.012503 | 64.6042 | 64.6729 | 10.1669 | -58.3328 | 64.7278 | -58.4473 | -58.4793 | -57.9575 | -2.3941 | -58.6578 | 64.7507 | 64.6957 | -58.5068 | -58.5709 | -0.064087 | -0.09613 | 0.073242 | 123.056 | 0.050354 | 0.14648 | -0.050354 | -0.1236 | -0.18768 | 0.09613 | 0.42572 | -0.27466 | -0.086975 | 0.041199 | 123.111 | 122.9874 | 68.5501 | -123.1338 | 123.1338 | 123.0789 | 55.9891 | -123.2254
510.6875 | 123.2483 | -58.3008 | 64.7781 | 0.36996 | 0.039688 | 0.068895 | 0.071806 | 0.12599 | 0.024053 | 0.003958 | -0.2802 | 0.0043348 | 0.06093 | 0.071057 | 0.0071838 | -0.017843 | 64.4257 | 65.1077 | 10.405 | -58.1635 | 64.8651 | -58.3191 | -58.3694 | -57.8705 | -2.6001 | -58.5846 | 64.888 | 64.8285 | -58.4061 | -58.4656 | -0.018311 | -0.068665 | 0.086975 | 123.4085 | 0.13733 | 0.20599 | -0.35248 | -0.10529 | -0.16479 | 0.10986 | 0.4303 | -0.28381 | -0.11902 | 0.050354 | 123.1659 | 122.7264 | 68.7057 | -123.1476 | 123.1888 | 123.1293 | 55.7007 | -123.2437
511.6875 | 123.2117 | -58.2458 | 64.8193 | 0.32418 | 0.05571 | 0.076372 | 0.096372 | 0.12065 | 0.012304 | 0.001822 | 0.46748 | -0.0010052 | 0.076952 | 0.059307 | 0.0007748 | -0.00075443 | 64.7919 | 64.8239 | 10.0983 | -58.1085 | 64.9338 | -58.2779 | -58.3374 | -57.7744 | -2.7054 | -58.5297 | 64.9384 | 64.856 | -58.3603 | -58.4198 | -0.032043 | -0.091552 | 0.11444 | 123.0698 | 0.13733 | 0.22888 | -0.027466 | -0.11444 | -0.17395 | 0.11902 | 0.4715 | -0.28381 | -0.10986 | 0.036621 | 123.1796 | 123.0377 | 68.3441 | -123.1567 | 123.1842 | 123.1018 | 55.5405 | -123.2391
512.6875 | 123.3261 | -58.2367 | 64.7644 | 0.019007 | 0.023666 | 0.066759 | 0.072874 | 0.12706 | -0.015467 | 0.001822 | 0.46748 | -0.021299 | 0.056658 | 0.057171 | 0.0050478 | -0.0039584 | 64.8102 | 64.9475 | 10.4141 | -58.0811 | 64.8285 | -58.2733 | -58.3145 | -57.6782 | -1.9775 | -58.4381 | 64.856 | 64.7873 | -58.3603 | -58.4198 | -0.036621 | -0.07782 | 0.064087 | 123.1842 | 0.15564 | 0.23346 | 0.045777 | -0.1236 | -0.18311 | 0.091553 | 0.55847 | -0.20142 | -0.01831 | 0.022888 | 123.0652 | 123.0469 | 68.6508 | -123.0789 | 123.0927 | 123.024 | 56.2592 | -123.1842
513.6875 | 123.3765 | -58.0627 | 64.9567 | 0.55307 | 0.048233 | 0.066759 | 0.084623 | 0.12706 | 0.0026914 | 0.00289 | 0.46748 | -0.0084822 | 0.053453 | 0.056103 | -0.0024292 | -0.0039584 | 64.9979 | 65.0848 | 10.4095 | -57.8567 | 64.9796 | -58.1131 | -58.1497 | -57.4539 | -2.1698 | -58.2001 | 64.9796 | 64.9338 | -58.1955 | -58.2413 | -0.050354 | -0.086975 | 0.022888 | 123.1476 | 0.20599 | 0.29297 | 0.041199 | -0.13275 | -0.17853 | 0.022888 | 0.60883 | -0.13733 | 0.041199 | -0.022888 | 123.0423 | 123.0606 | 68.4723 | -123.1064 | 123.0423 | 122.9965 | 55.8929 | -123.1979
514.6875 | 123.3307 | -57.9712 | 65.0482 | 0.36996 | 0.019394 | 0.058214 | 0.07501 | 0.12599 | 0.0016234 | -0.012063 | 0.46748 | -0.023436 | 0.076952 | 0.043286 | -0.0002932 | -0.026388 | 65.0803 | 65.1718 | 10.3088 | -57.7606 | 65.0436 | -58.0078 | -58.0719 | -57.3257 | -1.8677 | -58.1726 | 65.0848 | 65.0574 | -58.0902 | -58.1635 | -0.036621 | -0.10071 | -0.004578 | 123.143 | 0.21057 | 0.31128 | 0.032043 | -0.11902 | -0.19226 | 0.036621 | 0.64545 | -0.20142 | -0.009155 | 0.009155 | 123.0148 | 123.0515 | 68.28 | -123.1201 | 123.056 | 123.0286 | 56.1035 | -123.2117
515.6875 | 123.349 | -57.9391 | 65.0299 | 0.36996 | 0.029007 | 0.083848 | 0.068601 | 0.11531 | -0.0058536 | -0.006723 | 2.5274 | -0.0084822 | 0.064134 | 0.060376 | -0.0013612 | -0.017843 | 65.1031 | 65.2084 | 10.5423 | -57.7286 | 65.0894 | -58.0261 | -58.0627 | -57.3257 | -1.886 | -58.168 | 65.1215 | 65.0345 | -58.0902 | -58.1177 | -0.086975 | -0.1236 | 0.05951 | 123.1476 | 0.21057 | 0.33417 | 0.073242 | -0.15106 | -0.17853 | 0.091553 | 0.6134 | -0.22888 | -0.050354 | 0.004578 | 123.0286 | 123.0423 | 68.4814 | -123.0927 | 123.0606 | 122.9736 | 56.0532 | -123.1476
516.6875 | 123.317 | -57.8339 | 65.1855 | 0.41574 | 0.042892 | 0.081712 | 0.067533 | 0.11851 | -0.0079896 | 0.003958 | 1.0473 | -0.027708 | 0.073747 | 0.042218 | 0.0061158 | -0.014639 | 65.2176 | 65.3549 | 10.5286 | -57.6691 | 65.1993 | -57.8979 | -57.9437 | -57.1472 | -1.8906 | -58.0307 | 65.2267 | 65.1718 | -57.9437 | -58.0261 | -0.064087 | -0.10986 | 0.013733 | 123.1888 | 0.1648 | 0.27466 | 0.032043 | -0.10986 | -0.19226 | 0.041199 | 0.68665 | -0.19684 | -0.004578 | -0.013733 | 123.0331 | 123.0515 | 68.3624 | -123.1293 | 123.0606 | 123.0057 | 55.9433 | -123.2117
517.6875 | 123.3353 | -57.6553 | 65.2771 | 0.36996 | 0.04396 | 0.080644 | 0.0921 | 0.12706 | 0.0016234 | -0.001382 | 0.36067 | -0.0052782 | 0.059862 | 0.055035 | 0.012524 | -0.013571 | 65.3503 | 65.4556 | 10.7574 | -57.4493 | 65.4144 | -57.7286 | -57.8018 | -57.019 | -1.8768 | -57.9163 | 65.387 | 65.2954 | -57.8247 | -57.8888 | -0.073243 | -0.14648 | 0.13733 | 123.111 | 0.20599 | 0.35248 | 0.073242 | -0.16937 | -0.23346 | 0.10986 | 0.63629 | -0.26093 | -0.027466 | 0.01831 | 123.0698 | 123.0057 | 68.4128 | -123.0789 | 123.0423 | 122.9507 | 55.7785 | -123.1659
518.6875 | 123.3261 | -57.6096 | 65.4053 | 0.49203 | 0.008713 | 0.066759 | 0.064329 | 0.14094 | -0.013331 | -0.012063 | 0.43696 | -0.014891 | 0.064134 | 0.051831 | 0.014661 | -0.017843 | 65.5426 | 65.5655 | 10.35 | -57.3074 | 65.4465 | -57.6462 | -57.7103 | -56.8909 | -1.8539 | -57.8293 | 65.451 | 65.4053 | -57.7148 | -57.8339 | -0.036621 | -0.10071 | 0.041199 | 123.175 | 0.30212 | 0.40283 | 0.13733 | -0.10529 | -0.2243 | 0.045777 | 0.71869 | -0.21973 | 0.004577 | 0 | 123.056 | 123.1522 | 67.9596 | -123.1155 | 123.0606 | 123.0148 | 55.7556 | -123.2391
519.6875 | 123.3078 | -57.5089 | 65.4694 | 0.33944 | 0.02687 | 0.068895 | 0.06967 | 0.11638 | -0.017603 | -0.009927 | 0.36067 | -0.017027 | 0.058794 | 0.050762 | -0.0045652 | -0.0092984 | 65.5243 | 65.6113 | 9.1187 | -57.3029 | 65.5472 | -57.5455 | -57.6233 | -56.7856 | -1.7944 | -57.6828 | 65.6067 | 65.5426 | -57.6004 | -57.6828 | -0.036621 | -0.11444 | 0.07782 | 123.1201 | 0.20599 | 0.32044 | 0.054932 | -0.091553 | -0.17395 | 0.13733 | 0.72327 | -0.17395 | 0 | 0.073243 | 123.056 | 123.0331 | 66.6275 | -123.0927 | 123.1155 | 123.0515 | 55.7144 | -123.1522
520.6875 | 123.2849 | -57.3578 | 65.6799 | 0.32418 | 0.017257 | 0.068895 | 0.062193 | 0.12385 | -0.017603 | -0.015268 | 0.37593 | -0.012754 | 0.075884 | 0.060376 | -0.0002932 | -0.0092984 | 65.6982 | 65.8081 | 5.0858 | -57.0786 | 65.7303 | -57.399 | -57.4219 | -56.6025 | -1.8494 | -57.5821 | 65.744 | 65.6754 | -57.4631 | -57.5226 | -0.041199 | -0.064087 | 0.050354 | 123.1659 | 0.27924 | 0.34332 | 0.01831 | -0.10529 | -0.16479 | 0.064087 | 0.75531 | -0.2243 | -0.059509 | -0.004578 | 123.0881 | 123.056 | 62.4435 | -123.1018 | 123.1018 | 123.0331 | 55.5084 | -123.2025
521.6875 | 123.3398 | -57.4951 | 65.5289 | 0.33944 | 0.023666 | 0.075304 | 0.081419 | 0.11958 | -0.01974 | -0.010995 | 0.2386 | -0.020231 | 0.058794 | 0.048626 | 0.0007748 | -0.012503 | 65.5289 | 65.6433 | 10.4919 | -58.8547 | 65.5197 | -57.5729 | -57.6233 | -56.7398 | -2.037 | -57.7423 | 65.5884 | 65.5289 | -57.637 | -57.7011 | -0.07782 | -0.12817 | -0.009156 | 123.1384 | -1.3596 | -1.2314 | 0 | -0.14191 | -0.20599 | 0.059509 | 0.75531 | -0.24719 | -0.041199 | 0 | 123.0148 | 123.024 | 67.9871 | -123.1522 | 123.0835 | 123.024 | 55.4581 | -123.23
522.6875 | 123.2941 | -57.3349 | 65.6708 | 0.27841 | 0.007644 | 0.067827 | 0.072874 | 0.12172 | -0.0037176 | -0.012063 | 0.13178 | -0.019163 | 0.051317 | 0.050762 | 0.0039788 | -0.0092984 | 65.7028 | 65.8035 | 10.2905 | -57.0328 | 65.7349 | -57.3715 | -57.4585 | -56.5338 | -1.9455 | -57.5912 | 65.7578 | 65.6937 | -57.4448 | -57.55 | -0.036621 | -0.1236 | 0.064087 | 123.1384 | 0.30212 | 0.42572 | 0.032044 | -0.10986 | -0.21515 | 0.086975 | 0.80109 | -0.25635 | -0.041199 | 0.022889 | 123.0698 | 123.0377 | 67.6254 | -123.1293 | 123.0927 | 123.0286 | 55.3894 | -123.2208
523.6875 | 123.3032 | -56.8359 | 66.1652 | 0.32418 | 0.016189 | 0.081712 | 0.087828 | 0.12385 | -0.00051261 | -0.0142 | 0.33015 | -0.021299 | 0.054521 | 0.048626 | 0.013592 | -0.015707 | 66.188 | 66.2933 | 9.343 | -56.5842 | 66.2384 | -56.9046 | -56.9321 | -56.0211 | -1.7715 | -57.1152 | 66.2567 | 66.1377 | -56.9595 | -57.0374 | -0.068665 | -0.096131 | 0.073242 | 123.1293 | 0.25177 | 0.3479 | 0.022888 | -0.1236 | -0.20142 | 0.091553 | 0.81482 | -0.27924 | -0.077819 | -0.027466 | 123.0743 | 123.024 | 66.1789 | -123.0972 | 123.0927 | 122.9736 | 55.0644 | -123.2025
524.6875 | 123.2986 | -57.2845 | 65.7028 | 0.32418 | 0.02153 | 0.073167 | 0.067533 | 0.11638 | 0.0069634 | -0.00031405 | 0.2386 | -0.011686 | 0.066271 | 0.056103 | 0.0039788 | -0.024252 | 65.7715 | 65.8676 | 11.174 | -56.9504 | 65.7669 | -57.3761 | -57.3853 | -56.4011 | -2.1423 | -57.5317 | 65.7761 | 65.6937 | -57.4265 | -57.4997 | -0.091553 | -0.10071 | 0.064087 | 123.1522 | 0.33417 | 0.43488 | 0.068664 | -0.14191 | -0.21515 | 0.073242 | 0.88348 | -0.24719 | -0.032043 | -0.009155 | 123.0515 | 123.056 | 68.4586 | -123.0881 | 123.0606 | 122.9782 | 55.1422 | -123.2025
525.6875 | 123.2529 | -57.1518 | 65.8768 | 0.1716 | 0.015121 | 0.068895 | 0.080351 | 0.13133 | -0.0037176 | -0.016336 | 0.14704 | -0.0063462 | 0.053453 | 0.051831 | 0.0061158 | -0.012503 | 65.8813 | 65.9912 | 11.1282 | -56.6986 | 65.9454 | -57.1747 | -57.2525 | -56.2317 | -2.1103 | -57.3944 | 65.9546 | 65.8722 | -57.2525 | -57.3349 | -0.022889 | -0.10071 | 0.068665 | 123.143 | 0.45319 | 0.55389 | 0.004578 | -0.10071 | -0.18311 | 0.07782 | 0.9201 | -0.24262 | -0.059509 | -0.004578 | 123.0972 | 123.0331 | 68.28 | -123.1293 | 123.1064 | 123.024 | 55.0415 | -123.2117
526.6875 | 123.317 | -57.1472 | 65.8356 | 0.65988 | 0.012985 | 0.073167 | 0.071806 | 0.12599 | -0.012263 | -0.015268 | -0.05132 | -0.0063462 | 0.06093 | 0.047558 | 0.0007748 | -0.011435 | 65.8493 | 65.9821 | 12.2223 | -56.7993 | 65.918 | -57.2205 | -57.28 | -56.218 | -2.1927 | -57.3944 | 65.9592 | 65.8493 | -57.2891 | -57.3532 | -0.073242 | -0.13275 | 0.082398 | 123.1293 | 0.3479 | 0.48065 | 0.013733 | -0.14191 | -0.20599 | 0.1236 | 0.92926 | -0.24719 | -0.041199 | 0.013733 | 123.0652 | 122.9965 | 69.3695 | -123.1155 | 123.1064 | 122.9965 | 54.9545 | -123.1888
527.6875 | 123.3307 | -57.1976 | 65.7715 | 0.0037495 | 0.005508 | 0.068895 | 0.082487 | 0.12385 | -0.014399 | -0.008859 | -0.081838 | -0.018095 | 0.064134 | 0.053967 | -0.0099062 | -0.015707 | 65.8127 | 65.9546 | 12.2177 | -56.8085 | 65.8905 | -57.2525 | -57.3257 | -56.2088 | -2.3987 | -57.4081 | 65.8905 | 65.7898 | -57.312 | -57.3898 | -0.054931 | -0.12817 | 0.11902 | 123.1522 | 0.3891 | 0.51727 | 0.041199 | -0.11444 | -0.19226 | 0.11902 | 0.98877 | -0.21057 | -0.01831 | 0.018311 | 123.0881 | 123.0103 | 69.4153 | -123.0972 | 123.0881 | 122.9874 | 54.7989 | -123.1613
528.6875 | 123.3856 | -56.9183 | 66.069 | -0.13358 | 0.015121 | 0.083848 | 0.073942 | 0.11424 | -0.0015816 | -0.013132 | -0.11236 | -0.018095 | 0.065202 | 0.050762 | 0.0061158 | -0.017843 | 66.1377 | 66.2796 | 11.1923 | -56.4972 | 66.1377 | -56.9778 | -57.0557 | -55.8289 | -2.0645 | -57.0923 | 66.1285 | 66.0599 | -57.0282 | -57.1152 | -0.059509 | -0.13733 | 0.068664 | 123.1979 | 0.42114 | 0.55847 | 0.068664 | -0.10986 | -0.19684 | 0.059509 | 1.0895 | -0.17395 | 0.022888 | -0.009156 | 123.056 | 123.056 | 68.1107 | -123.1247 | 123.0469 | 122.9782 | 54.8538 | -123.1842
529.6875 | 123.317 | -56.955 | 66.0461 | 0.019007 | 0.005508 | 0.071031 | 0.071806 | 0.12065 | 0.0016234 | -0.00031405 | -0.18865 | -0.015959 | 0.044908 | 0.058239 | -0.010974 | -0.022116 | 66.069 | 66.2247 | 13.0005 | -56.5201 | 66.1377 | -57.0282 | -57.0557 | -55.8701 | -2.1561 | -57.193 | 66.1377 | 66.0187 | -57.106 | -57.1564 | -0.073242 | -0.10071 | 0.091552 | 123.1796 | 0.43488 | 0.53558 | 0.022888 | -0.15106 | -0.20142 | 0.091552 | 1.0849 | -0.23804 | -0.036621 | -0.027466 | 123.0927 | 123.024 | 69.9554 | -123.1018 | 123.0927 | 122.9736 | 54.7989 | -123.2025
530.6875 | 123.3215 | -56.8359 | 66.1652 | -0.087804 | 0.029007 | 0.076372 | 0.068601 | 0.12278 | -0.0015816 | 0.003958 | -0.17339 | -0.013823 | 0.067339 | 0.044354 | -0.0077702 | -0.02532 | 66.188 | 66.3437 | 15.7104 | -56.3919 | 66.2338 | -56.9046 | -56.9595 | -55.7281 | -1.9135 | -57.0419 | 66.2292 | 66.1011 | -56.9595 | -57.0419 | -0.068665 | -0.1236 | 0.068665 | 123.1796 | 0.44403 | 0.56763 | 0.022888 | -0.1236 | -0.20599 | 0.064087 | 1.1078 | -0.20599 | 0 | -0.064087 | 123.0698 | 123.024 | 72.5464 | -123.1247 | 123.0652 | 122.937 | 54.9225 | -123.2071
531.6875 | 123.2941 | -56.6437 | 66.3528 | 0.034266 | 0.008713 | 0.092393 | 0.07501 | 0.11744 | 0.0048274 | -0.007791 | -0.066579 | -0.030912 | 0.066271 | 0.051831 | 0.0018428 | -0.017843 | 66.3391 | 66.4948 | 13.3621 | -56.1905 | 66.4124 | -56.7123 | -56.7856 | -55.4947 | -1.9089 | -56.8817 | 66.4444 | 66.3254 | -56.781 | -56.8588 | -0.068664 | -0.14191 | 0.05951 | 123.1384 | 0.45319 | 0.59509 | -0.013733 | -0.13733 | -0.21515 | 0.091553 | 1.149 | -0.23804 | -0.022888 | -0.027466 | 123.056 | 122.9828 | 70.0058 | -123.1384 | 123.0881 | 122.9691 | 54.7348 | -123.2117
532.6875 | 123.3215 | -56.6437 | 66.3254 | -0.11832 | 0.00444 | 0.081712 | 0.085691 | 0.12599 | 0.0058954 | -0.0142 | -0.11236 | -0.021299 | 0.051317 | 0.057171 | 0.015729 | -0.0092984 | 66.3712 | 66.5451 | 15.7059 | -56.1539 | 66.4032 | -56.7078 | -56.7856 | -55.4352 | -1.8631 | -56.8634 | 66.4169 | 66.2888 | -56.7856 | -56.8634 | -0.064087 | -0.14191 | 0.07782 | 123.1888 | 0.48981 | 0.63171 | 0.045777 | -0.14191 | -0.21973 | 0.091553 | 1.2085 | -0.21973 | 0 | -0.036621 | 123.0469 | 123.0148 | 72.3495 | -123.111 | 123.0606 | 122.9324 | 54.7806 | -123.1888
533.6875 | 123.2895 | -56.662 | 66.3803 | -0.27091 | -0.014786 | 0.076372 | 0.078214 | 0.11851 | -0.0058536 | -0.015268 | -0.37176 | -0.0074142 | 0.04384 | 0.048626 | 0.0061158 | -0.018912 | 66.4673 | 66.6183 | 16.571 | -56.0761 | 66.4536 | -56.6711 | -56.7352 | -55.3894 | -1.4877 | -56.6666 | 66.4948 | 66.3666 | -56.7444 | -56.8222 | -0.009156 | -0.073242 | 0.073242 | 123.2803 | 0.58594 | 0.65918 | 0.086975 | -0.082398 | -0.16022 | 0.11444 | 1.2726 | -0.004578 | 0.15564 | -0.013733 | 123.1155 | 123.1293 | 73.233 | -123.1155 | 123.1567 | 123.0286 | 55.1743 | -123.2025
534.6875 | 123.3124 | -56.5979 | 66.4169 | -0.30143 | 0.001236 | 0.083848 | 0.085691 | 0.11958 | -0.0026496 | 0.007163 | -0.43279 | -0.011686 | 0.029955 | 0.045422 | 0.018933 | -0.013571 | 66.481 | 66.6504 | 16.6672 | -56.012 | 66.4719 | -56.6299 | -56.694 | -55.4306 | -1.6159 | -56.8222 | 66.4856 | 66.3437 | -56.7169 | -56.7993 | -0.032044 | -0.096131 | 0.054932 | 123.2483 | 0.58594 | 0.68207 | 0.064087 | -0.11902 | -0.20142 | 0.068665 | 1.1673 | -0.2243 | -0.022889 | -0.073242 | 123.0698 | 123.0789 | 73.2651 | -123.111 | 123.0835 | 122.9416 | 54.982 | -123.2162
535.6875 | 123.3353 | -56.3965 | 66.6 | -0.40824 | -0.01265 | 0.06569 | 0.080351 | 0.11638 | 0.0048274 | -0.00245 | 4.7247 | -0.014891 | 0.055589 | 0.049694 | 0.0018428 | -0.023184 | 66.6367 | 66.8106 | 16.6168 | -55.8334 | 66.6733 | -56.4789 | -56.5292 | -55.0323 | -1.6251 | -56.6116 | 66.6504 | 66.5131 | -56.543 | -56.5933 | -0.082398 | -0.13275 | 0.073242 | 123.2071 | 0.56305 | 0.6958 | 0.036621 | -0.14648 | -0.19684 | 0.050354 | 1.3641 | -0.21515 | -0.01831 | -0.086975 | 123.0698 | 123.0331 | 73.0133 | -123.1293 | 123.0469 | 122.9095 | 54.7714 | -123.1934
536.6875 | 123.2574 | -56.3416 | 66.7099 | -0.4235 | 0.037552 | 0.074235 | 0.083555 | 0.14201 | 0.0048274 | -0.003518 | -0.52434 | -0.010618 | 0.064134 | 0.051831 | 0.0071838 | -0.024252 | 66.7191 | 66.8701 | 16.0767 | -55.7236 | 66.7648 | -56.3782 | -56.4239 | -54.9911 | -1.5289 | -56.575 | 66.7923 | 66.6504 | -56.4651 | -56.5063 | -0.036621 | -0.082397 | 0.054932 | 123.2117 | 0.61798 | 0.70038 | 0.009155 | -0.1236 | -0.1648 | 0.082397 | 1.3504 | -0.23346 | -0.068664 | -0.059509 | 123.1064 | 123.0606 | 72.4182 | -123.1338 | 123.1338 | 122.9919 | 54.8126 | -123.2162
537.6875 | 123.3078 | -56.0394 | 66.9617 | -0.3472 | 0.00016795 | 0.12551 | 0.06967 | 0.12278 | 0.016576 | -0.00245 | -0.50908 | -0.023436 | 0.057726 | 0.044354 | 0.012524 | -0.0071624 | 67.0532 | 67.1173 | 13.6826 | -55.4169 | 67.0212 | -56.0898 | -56.1813 | -54.6021 | -1.2772 | -56.25 | 67.0532 | 66.9022 | -56.1722 | -56.2225 | -0.050354 | -0.14191 | 0.059509 | 123.1567 | 0.62256 | 0.76446 | 0.091553 | -0.13275 | -0.18311 | 0.091553 | 1.4374 | -0.21057 | -0.027466 | -0.059509 | 123.0606 | 123.0927 | 69.722 | -123.143 | 123.0927 | 122.9416 | 54.7623 | -123.1842
538.6875 | 123.2986 | -56.1401 | 66.8747 | -0.13358 | 0.025802 | 0.080644 | 0.084623 | 0.12706 | -0.0079896 | -0.00031405 | -0.21917 | -0.023436 | 0.061998 | 0.053967 | -0.0024292 | -0.017843 | 66.9205 | 67.1173 | 15.7379 | -55.4764 | 66.9434 | -56.1768 | -56.2363 | -54.5975 | -1.2726 | -56.3095 | 66.9434 | 66.8198 | -56.2729 | -56.3324 | -0.036621 | -0.09613 | 0.068664 | 123.2574 | 0.66376 | 0.75989 | 0.045776 | -0.13275 | -0.19226 | 0.068664 | 1.5427 | -0.16937 | 0.022888 | -0.054932 | 123.0835 | 123.0606 | 71.8781 | -123.111 | 123.0835 | 122.9599 | 54.8676 | -123.2071
539.6875 | 123.2712 | -56.0761 | 66.9617 | -0.53031 | 0.009781 | 0.080644 | 0.072874 | 0.12385 | 0.0091004 | -0.001382 | -0.38701 | -0.011686 | 0.056658 | 0.043286 | 0.0018428 | -0.029593 | 66.9662 | 67.1585 | 15.3809 | -55.3894 | 66.9754 | -56.1493 | -56.1996 | -54.5151 | -1.2222 | -56.2729 | 67.0074 | 66.8472 | -56.2088 | -56.2637 | -0.073242 | -0.1236 | 0.013733 | 123.2346 | 0.68665 | 0.81024 | 0.004578 | -0.13275 | -0.18768 | 0.045776 | 1.561 | -0.19684 | -0.009155 | -0.11444 | 123.0515 | 123.0423 | 71.4569 | -123.1613 | 123.0835 | 122.9233 | 54.8538 | -123.2254
540.6875 | 123.2071 | -56.0532 | 67.0166 | -0.54557 | 0.032211 | 0.085985 | 0.083555 | 0.12278 | 0.00055539 | 0.00075395 | -1.1347 | -0.022367 | 0.052385 | 0.050762 | -0.0002932 | -0.030661 | 66.9571 | 67.1219 | 14.4745 | -55.394 | 67.0807 | -56.1035 | -56.163 | -54.4739 | -1.1581 | -56.3278 | 67.1036 | 66.9708 | -56.2134 | -56.2592 | -0.050354 | -0.10986 | 0.064086 | 123.175 | 0.65918 | 0.76904 | -0.05951 | -0.16022 | -0.20599 | 0.086975 | 1.5793 | -0.27466 | -0.068665 | -0.045777 | 123.1338 | 123.0103 | 70.5276 | -123.1796 | 123.1567 | 123.024 | 54.895 | -123.2758
541.6875 | 123.1888 | -55.7556 | 67.337 | -0.51505 | 0.022598 | 0.072099 | 0.085691 | 0.12812 | 0.010168 | 0.008231 | -0.44805 | -0.013823 | 0.067339 | 0.051831 | 0.0018428 | -0.0071624 | 67.2272 | 67.4469 | 14.2364 | -55.0278 | 67.3965 | -55.7693 | -55.838 | -54.0985 | -1.0025 | -56.0211 | 67.4377 | 67.2729 | -55.8655 | -55.9341 | -0.013733 | -0.082398 | 0.059509 | 123.2025 | 0.72784 | 0.81024 | -0.10986 | -0.10986 | -0.17853 | 0.10071 | 1.6571 | -0.2655 | -0.086975 | -0.064087 | 123.1522 | 122.9828 | 69.9921 | -123.175 | 123.1934 | 123.0286 | 54.7531 | -123.2712
542.6875 | 123.2071 | -55.6412 | 67.4469 | -0.27091 | 0.030075 | 0.087053 | 0.084623 | 0.12919 | 0.0026914 | -0.003518 | -0.63115 | -0.020231 | 0.052385 | 0.043286 | 0.0018428 | -0.018912 | 67.3462 | 67.5064 | 13.9755 | -54.9133 | 67.4927 | -55.6824 | -55.7556 | -53.9658 | -0.85602 | -55.9067 | 67.543 | 67.4011 | -55.7556 | -55.838 | -0.041199 | -0.11444 | 0.045777 | 123.1476 | 0.72784 | 0.84228 | -0.10071 | -0.11444 | -0.19684 | 0.096131 | 1.6754 | -0.2655 | -0.068664 | -0.045776 | 123.1338 | 122.9874 | 69.6167 | -123.2025 | 123.1842 | 123.0423 | 54.7852 | -123.2849
543.6875 | 123.2529 | -55.5405 | 67.5705 | -0.59134 | 0.016189 | 0.072099 | 0.093168 | 0.11638 | 0.011236 | -0.00245 | -0.63115 | -0.0052782 | 0.071611 | 0.051831 | 0.012524 | -0.0092984 | 67.424 | 67.5797 | 12.4558 | -54.808 | 67.5842 | -55.5862 | -55.6686 | -53.8376 | -0.79651 | -55.838 | 67.6575 | 67.4652 | -55.6778 | -55.7327 | -0.045777 | -0.12817 | 0.013733 | 123.1201 | 0.73242 | 0.8606 | -0.14649 | -0.13733 | -0.19226 | 0.086975 | 1.7029 | -0.29755 | -0.10529 | -0.10529 | 123.1247 | 122.9645 | 67.9962 | -123.2391 | 123.1979 | 123.0057 | 54.744 | -123.3032
544.6875 | 123.2208 | -55.8563 | 67.2363 | -0.37772 | 0.057846 | 0.090257 | 0.0921 | 0.12812 | 0.019781 | 0.006095 | -0.43279 | -0.0063462 | 0.074815 | 0.04649 | 0.0039788 | -0.021048 | 67.1448 | 67.2775 | 14.0533 | -55.0186 | 67.3096 | -55.8838 | -55.9433 | -54.0253 | -0.9201 | -56.0989 | 67.337 | 67.186 | -55.9662 | -56.0349 | -0.027466 | -0.086975 | 0.073242 | 123.1339 | 0.83771 | 0.92468 | -0.091553 | -0.10986 | -0.17853 | 0.10071 | 1.8311 | -0.24261 | -0.064087 | -0.050354 | 123.1659 | 123.0011 | 69.9097 | -123.1796 | 123.1934 | 123.0423 | 54.9362 | -123.2712
545.6875 | 123.1979 | -55.4031 | 67.6987 | -0.48453 | 0.018326 | 0.085985 | 0.087828 | 0.12278 | -0.0015816 | 0.006095 | -0.3565 | -0.0031412 | 0.057726 | 0.04649 | 0.0039788 | -0.012503 | 67.6025 | 67.7994 | 13.7741 | -54.5197 | 67.7261 | -55.4214 | -55.481 | -53.508 | -0.59052 | -55.6229 | 67.7856 | 67.6529 | -55.5084 | -55.5679 | -0.018311 | -0.07782 | 0.027466 | 123.2025 | 0.88348 | 0.9613 | -0.09613 | -0.10529 | -0.16479 | 0.086976 | 1.8951 | -0.21973 | -0.054932 | -0.045776 | 123.1293 | 123.0057 | 69.1772 | -123.1796 | 123.1888 | 123.056 | 54.8126 | -123.2666
546.6875 | 123.2025 | -55.3207 | 67.7719 | -0.43876 | 0.03862 | 0.081712 | 0.10705 | 0.12278 | -0.0037176 | 0.00289 | -0.49383 | -0.0031412 | 0.057726 | 0.053967 | -0.0002932 | -0.010367 | 67.6575 | 67.7856 | 13.6871 | -54.2953 | 67.8589 | -55.3207 | -55.4077 | -53.3936 | -0.52643 | -55.5862 | 67.8589 | 67.7124 | -55.4535 | -55.545 | 0 | -0.086975 | 0.086975 | 123.1064 | 1.0254 | 1.1124 | -0.11444 | -0.13275 | -0.2243 | 0.086975 | 1.9272 | -0.2655 | -0.041199 | -0.05951 | 123.1796 | 122.9782 | 69.0079 | -123.1796 | 123.1796 | 123.0331 | 54.7943 | -123.317
547.6875 | 123.2483 | -55.4398 | 67.6529 | -0.37772 | 0.046097 | 0.079576 | 0.082487 | 0.12706 | 0.022985 | 0.006095 | -0.63115 | -0.0010052 | 0.069475 | 0.043286 | 0.014661 | -0.021048 | 67.5613 | 67.7216 | 13.1836 | -54.5059 | 67.717 | -55.4947 | -55.5588 | -53.3752 | -0.48981 | -55.6641 | 67.7216 | 67.6071 | -55.5267 | -55.6229 | -0.054932 | -0.11902 | 0.064087 | 123.1613 | 0.93384 | 1.0529 | -0.091553 | -0.086975 | -0.18311 | 0.068665 | 2.0645 | -0.2243 | -0.041198 | -0.045776 | 123.1567 | 123.0011 | 68.6234 | -123.2117 | 123.1613 | 123.0469 | 54.95 | -123.2758
548.6875 | 123.2117 | -55.3116 | 67.7719 | -0.4235 | 0.064255 | 0.08278 | 0.078214 | 0.12172 | 0.017644 | 0.017844 | -0.44805 | -0.014891 | 0.065202 | 0.055035 | 0.0018428 | -0.022116 | 67.7261 | 67.868 | 12.291 | -54.3503 | 67.8772 | -55.3207 | -55.3802 | -53.1601 | -0.37079 | -55.5359 | 67.8635 | 67.749 | -55.426 | -55.4672 | -0.009156 | -0.068665 | 0.10528 | 123.1796 | 0.9613 | 1.03 | -0.045777 | -0.11444 | -0.15564 | 0.091552 | 2.1515 | -0.2243 | -0.068665 | -0.022889 | 123.1888 | 123.0377 | 67.6025 | -123.1522 | 123.175 | 123.0606 | 54.9408 | -123.2391
549.6875 | 123.2574 | -55.2933 | 67.7765 | -0.36246 | 0.045028 | 0.080644 | 0.086759 | 0.11958 | 0.015508 | 0.011435 | -0.29546 | -0.0084822 | 0.075884 | 0.049694 | 0.0093198 | -0.014639 | 67.6895 | 67.8452 | 14.1678 | -54.3045 | 67.8314 | -55.3391 | -55.4123 | -53.0914 | -0.3891 | -55.5267 | 67.8406 | 67.749 | -55.3894 | -55.5084 | -0.045776 | -0.11902 | 0.054932 | 123.1384 | 0.98877 | 1.1078 | -0.086975 | -0.09613 | -0.21515 | 0.064087 | 2.2018 | -0.23346 | -0.01831 | -0.027466 | 123.1247 | 122.9828 | 69.4611 | -123.1888 | 123.1338 | 123.0423 | 54.9042 | -123.2849
550.6875 | 123.2162 | -55.0735 | 67.9459 | -0.30143 | 0.046097 | 0.078508 | 0.083555 | 0.12706 | 0.010168 | 0.017844 | -0.2802 | -0.0010052 | 0.074815 | 0.04649 | 0.0071838 | -0.015707 | 67.9459 | 68.0923 | 12.8128 | -54.0665 | 68.0603 | -55.0964 | -55.2017 | -52.771 | -0.21973 | -55.3024 | 68.0649 | 67.9596 | -55.2109 | -55.2658 | -0.022889 | -0.12817 | 0.11444 | 123.1659 | 1.0071 | 1.1353 | 0 | -0.13733 | -0.19226 | 0.11902 | 2.3026 | -0.22888 | -0.036621 | 0.013733 | 123.1338 | 123.0194 | 67.8864 | -123.1476 | 123.1384 | 123.0331 | 54.8538 | -123.2117
551.6875 | 123.23 | -55.4031 | 67.7124 | -0.37772 | 0.039688 | 0.072099 | 0.085691 | 0.12065 | 0.0048274 | 0.010367 | -0.50908 | 0.0043348 | 0.073747 | 0.043286 | 0.0029108 | -0.012503 | 67.5659 | 67.7032 | 19.1391 | -54.3732 | 67.7536 | -55.4306 | -55.5176 | -53.0319 | -0.48523 | -55.6229 | 67.7856 | 67.6666 | -55.4901 | -55.5725 | -0.027466 | -0.11444 | 0.041199 | 123.1064 | 1.03 | 1.1444 | -0.14648 | -0.086975 | -0.16937 | 0.073243 | 2.3712 | -0.21973 | -0.050354 | -0.045776 | 123.1567 | 122.9691 | 74.5422 | -123.23 | 123.1888 | 123.0698 | 54.9179 | -123.2849
552.6875 | 123.2117 | -54.9728 | 68.0832 | -0.28617 | 0.054641 | 0.078508 | 0.093168 | 0.1324 | 0.016576 | 0.013571 | -0.2802 | -0.0010052 | 0.06093 | 0.056103 | 0.011456 | -0.0071624 | 68.0832 | 68.248 | 12.9868 | -53.7918 | 68.2159 | -54.95 | -55.0323 | -52.4323 | -0.17395 | -55.1559 | 68.2159 | 68.1198 | -55.0598 | -55.1743 | 0.022888 | -0.05951 | 0.13275 | 123.2208 | 1.181 | 1.2405 | 0 | -0.086975 | -0.20142 | 0.13275 | 2.5406 | -0.18311 | 0.01831 | 0.036621 | 123.1888 | 123.056 | 67.9596 | -123.1155 | 123.1888 | 123.0927 | 54.7989 | -123.2574
553.6875 | 123.2117 | -55.1743 | 67.9001 | 0.27841 | 0.053573 | 0.085985 | 0.095304 | 0.12706 | 0.020849 | 0.017844 | -0.11236 | 0.0096758 | 0.061998 | 0.062512 | 0.0093198 | -0.016775 | 67.8497 | 67.9871 | 14.5203 | -54.0985 | 67.9367 | -55.2063 | -55.2887 | -52.6199 | -0.46692 | -55.4123 | 67.9825 | 67.8772 | -55.2658 | -55.3757 | -0.032044 | -0.11444 | 0.036622 | 123.1613 | 1.0757 | 1.1902 | -0.050354 | -0.091553 | -0.20142 | 0.082398 | 2.5543 | -0.23804 | -0.036621 | -0.022888 | 123.111 | 123.024 | 69.6945 | -123.1888 | 123.1567 | 123.0515 | 54.7073 | -123.2758
554.6875 | 123.1796 | -55.2017 | 67.8864 | 0.049525 | 0.081344 | 0.085985 | 0.10385 | 0.12492 | 0.0058954 | 0.006095 | -0.036062 | -0.0052782 | 0.08336 | 0.060376 | 0.017865 | -0.012503 | 67.7536 | 67.9001 | 15.2893 | -54.0665 | 67.9459 | -55.2475 | -55.2979 | -52.5879 | -0.62714 | -55.513 | 67.955 | 67.868 | -55.3299 | -55.3894 | -0.045777 | -0.096131 | 0.059509 | 123.1018 | 1.1353 | 1.2314 | -0.13275 | -0.12817 | -0.18768 | 0.068664 | 2.6138 | -0.31128 | -0.1236 | -0.018311 | 123.1476 | 122.9553 | 70.491 | -123.1842 | 123.1567 | 123.0698 | 54.5746 | -123.2758
555.6875 | 123.1796 | -54.8676 | 68.2205 | -0.026769 | 0.053573 | 0.080644 | 0.088896 | 0.12172 | 0.026189 | 0.015708 | 0.009715 | -0.013823 | 0.069475 | 0.061444 | 0.0093198 | -0.018912 | 68.1564 | 68.2755 | 16.5939 | -53.6682 | 68.28 | -54.9042 | -54.9316 | -52.0935 | -0.3479 | -55.1102 | 68.3212 | 68.2251 | -54.9774 | -55.0278 | -0.036621 | -0.064087 | 0.059509 | 123.143 | 1.1993 | 1.2634 | -0.064087 | -0.10986 | -0.16022 | 0.10071 | 2.774 | -0.24261 | -0.082397 | 0.004578 | 123.1476 | 123.024 | 71.4615 | -123.1522 | 123.1888 | 123.0927 | 54.5197 | -123.2483
556.6875 | 123.1934 | -54.9728 | 68.1244 | 0.019007 | 0.052505 | 0.08278 | 0.10385 | 0.12492 | 0.0091004 | 0.011435 | -0.005544 | -0.0063462 | 0.069475 | 0.064648 | 0.0082518 | -0.014639 | 68.0603 | 68.1747 | 18.4662 | -53.7186 | 68.1976 | -54.9683 | -55.0369 | -52.0935 | -0.45319 | -55.2109 | 68.2114 | 68.1244 | -55.0873 | -55.1514 | 0.004577 | -0.064087 | 0.073242 | 123.1476 | 1.2543 | 1.3184 | -0.064087 | -0.11444 | -0.17853 | 0.086975 | 2.8793 | -0.23804 | -0.059509 | 0 | 123.1705 | 123.0331 | 73.439 | -123.1613 | 123.1842 | 123.0972 | 54.5197 | -123.2758
557.6875 | 123.1888 | -54.5563 | 68.541 | -0.01151 | 0.063186 | 0.081712 | 0.094236 | 0.12492 | 0.020849 | 0.008231 | 0.040232 | -0.0052782 | 0.068407 | 0.049694 | 0.0082518 | -0.02532 | 68.454 | 68.5547 | 17.775 | -53.3295 | 68.5959 | -54.5792 | -54.6295 | -51.6037 | -0.1831 | -54.8264 | 68.6234 | 68.5318 | -54.6799 | -54.7394 | -0.022889 | -0.073243 | 0.054931 | 123.111 | 1.2268 | 1.3 | -0.086976 | -0.1236 | -0.18311 | 0.082397 | 2.9526 | -0.27008 | -0.086975 | -0.009156 | 123.1522 | 123.0103 | 72.3312 | -123.1705 | 123.1796 | 123.0881 | 54.3732 | -123.2803
558.6875 | 123.1934 | -54.3228 | 68.7881 | 0.49203 | 0.030075 | 0.075304 | 0.088896 | 0.13133 | 0.012304 | 0.017844 | -0.12761 | -0.0031412 | 0.073747 | 0.057171 | 0.0093198 | -0.018912 | 68.66 | 68.811 | 17.601 | -53.2104 | 68.7927 | -54.3823 | -54.4373 | -51.2238 | 0.018311 | -54.5242 | 68.8522 | 68.779 | -54.4281 | -54.483 | -0.059509 | -0.11444 | 0.004578 | 123.1338 | 1.1124 | 1.2268 | -0.12817 | -0.10529 | -0.16022 | 0.064087 | 3.0991 | -0.20142 | -0.041199 | -0.009155 | 123.1155 | 122.9828 | 71.9238 | -123.2254 | 123.175 | 123.1018 | 54.3411 | -123.2712
559.6875 | 123.1659 | -54.1992 | 68.8889 | 0.080043 | 0.06105 | 0.079576 | 0.088896 | 0.13774 | 0.010168 | 0.003958 | -0.05132 | -0.0020732 | 0.076952 | 0.072125 | 0.0050478 | -0.016775 | 68.7149 | 68.8385 | 17.514 | -52.803 | 68.9209 | -54.277 | -54.3274 | -51.0086 | -0.086975 | -54.4601 | 68.9987 | 68.9072 | -54.2908 | -54.364 | -0.07782 | -0.12817 | 0.032043 | 123.0377 | 1.3962 | 1.5244 | -0.17395 | -0.091552 | -0.16479 | 0.10986 | 3.1906 | -0.26093 | -0.09613 | 0.018311 | 123.1201 | 122.9141 | 71.7133 | -123.2162 | 123.1979 | 123.1064 | 54.1122 | -123.2529
560.6875 | 123.2162 | -54.2999 | 68.779 | 0.24789 | 0.065323 | 0.084917 | 0.087828 | 0.12278 | 0.011236 | 0.012503 | 0.26911 | -0.011686 | 0.074815 | 0.083874 | 0.021069 | -0.011435 | 68.6279 | 68.7103 | 17.8528 | -53.0685 | 68.8568 | -54.2679 | -54.2679 | -51.0818 | 0.059509 | -54.6021 | 68.8614 | 68.811 | -54.3777 | -54.4556 | 0.032044 | 0.032044 | 0.07782 | 123.0103 | 1.2314 | 1.1993 | -0.15106 | -0.07782 | -0.15564 | 0.082397 | 3.2181 | -0.30212 | -0.14649 | 0.032043 | 123.1567 | 122.9279 | 72.1527 | -123.0469 | 123.1613 | 123.111 | 54.3594 | -123.2346
561.6875 | 123.1842 | -54.5471 | 68.5501 | 0.24789 | 0.049301 | 0.081712 | 0.087828 | 0.13026 | 0.0091004 | 0.017844 | 3.565 | 0.0032668 | 0.076952 | 0.066784 | 0.0061158 | -0.011435 | 68.3945 | 68.4586 | 18.6813 | -53.0136 | 68.5867 | -54.6066 | -54.6616 | -51.1459 | -0.52185 | -54.7531 | 68.6554 | 68.5913 | -54.6433 | -54.7073 | -0.059509 | -0.11444 | 0.036621 | 123.0057 | 1.5335 | 1.6479 | -0.15564 | -0.096131 | -0.16022 | 0.10529 | 3.4012 | -0.20599 | -0.045777 | 0.041199 | 123.1338 | 122.9416 | 73.2285 | -123.2117 | 123.2025 | 123.1384 | 54.0253 | -123.2574
562.6875 | 123.2574 | -54.2038 | 68.8293 | 0.26315 | 0.040756 | 0.089189 | 0.098509 | 0.13346 | 0.0069634 | 0.00289 | 0.40644 | -0.0095502 | 0.068407 | 0.056103 | -0.0034972 | -0.0092984 | 68.7927 | 68.8568 | 20.3201 | -52.6108 | 68.9163 | -54.2313 | -54.3137 | -50.6561 | -0.2243 | -54.4006 | 68.9575 | 68.9026 | -54.2816 | -54.3411 | -0.027466 | -0.10986 | 0.086975 | 123.0606 | 1.593 | 1.7029 | -0.036621 | -0.07782 | -0.13733 | 0.12817 | 3.5477 | -0.19684 | -0.05951 | 0.073242 | 123.1201 | 122.9965 | 74.5239 | -123.143 | 123.1613 | 123.1064 | 53.9795 | -123.1705
563.6875 | 123.1979 | -53.4897 | 69.5984 | 0.29367 | 0.036484 | 0.090257 | 0.082487 | 0.13133 | 0.0058954 | 0.016776 | -0.60064 | -0.0042092 | 0.068407 | 0.049694 | -0.0002932 | 0.00031457 | 69.223 | 69.8227 | 16.0629 | -53.009 | 69.6899 | -53.4851 | -53.5721 | -49.9329 | 0.17853 | -53.7689 | 69.6899 | 69.5984 | -53.6224 | -53.6819 | 0.004578 | -0.082398 | 0.091552 | 123.3124 | 0.48065 | 0.56305 | -0.37537 | -0.13275 | -0.19226 | 0.091552 | 3.5568 | -0.27924 | -0.086975 | 0 | 123.1796 | 122.7127 | 69.5526 | -123.1705 | 123.1796 | 123.0881 | 53.6682 | -123.2803
564.6875 | 123.175 | -53.508 | 69.5618 | 0.24789 | 0.05571 | 0.093461 | 0.096372 | 0.13453 | 0.0080314 | 0.001822 | 0.055491 | -0.0020732 | 0.053453 | 0.052899 | 0.013592 | -0.010367 | 69.6854 | 69.4565 | 17.3813 | -52.0615 | 69.6304 | -53.5629 | -53.5995 | -49.8413 | 0.13733 | -53.7872 | 69.6396 | 69.5847 | -53.6545 | -53.7048 | -0.054931 | -0.091552 | 0.068664 | 122.9645 | 1.4465 | 1.5381 | 0.1236 | -0.14648 | -0.19684 | 0.077819 | 3.6667 | -0.27923 | -0.082397 | 0.022888 | 123.1384 | 123.1934 | 70.8893 | -123.1613 | 123.1476 | 123.0927 | 53.6453 | -123.2666
565.6875 | 123.143 | -53.2196 | 69.8868 | 0.080043 | 0.06105 | 0.079576 | 0.10812 | 0.1356 | 0.024053 | 0.009299 | 0.07075 | 0.0011308 | 0.071611 | 0.071057 | 0.0039788 | -0.015707 | 69.7311 | 69.8273 | 17.2073 | -49.5575 | 69.928 | -53.2837 | -53.3386 | -49.5392 | 0.29755 | -53.5126 | 69.8685 | 69.8639 | -53.3066 | -53.4119 | -0.064087 | -0.11902 | 0.041199 | 123.0469 | 3.6621 | 3.7811 | -0.15564 | -0.086976 | -0.19226 | -0.018311 | 3.6804 | -0.29297 | -0.10071 | -0.022888 | 123.1476 | 122.9507 | 70.4269 | -123.2254 | 123.0881 | 123.0835 | 53.5171 | -123.2986
566.7031 | 123.2712 | -52.7252 | 70.3125 | 0.14108 | 0.005508 | 0.10735 | 0.07501 | 0.13346 | -0.01974 | 0.009299 | 0.37593 | -0.024504 | 0.059862 | 0.052899 | -0.0045652 | -0.010367 | 70.2484 | 70.3995 | 16.2781 | -51.2009 | 70.4041 | -52.7252 | -52.771 | -48.674 | 0.59509 | -52.89 | 70.3995 | 70.3445 | -52.8122 | -52.8717 | 0 | -0.045776 | 0.091553 | 123.1247 | 1.5244 | 1.5701 | -0.064087 | -0.086975 | -0.14648 | 0.086975 | 4.0512 | -0.16479 | -0.018311 | 0.032043 | 123.1293 | 122.9736 | 69.0033 | -123.0835 | 123.1247 | 123.0698 | 53.3203 | -123.1842
567.6875 | 123.2895 | -52.8946 | 70.0974 | 0.44625 | 0.02153 | 0.091325 | 0.10065 | 0.15055 | 0.011236 | 0.011435 | 0.34541 | -0.010618 | 0.064134 | 0.041149 | -0.0002932 | -0.0082304 | 70.0333 | 70.1157 | 16.2415 | -51.1963 | 70.166 | -52.9678 | -53.0548 | -48.88 | 0.24261 | -53.1326 | 70.1248 | 70.079 | -53.0777 | -53.1143 | -0.073242 | -0.16022 | 0.068665 | 123.0103 | 1.6983 | 1.8585 | -0.064087 | -0.18311 | -0.21973 | 0.027466 | 4.0146 | -0.23804 | -0.01831 | -0.01831 | 123.0606 | 122.9279 | 69.136 | -123.1522 | 123.0194 | 122.9736 | 53.1372 | -123.2117
568.6875 | 123.2849 | -52.4597 | 70.5368 | 0.44625 | 0.034347 | 0.075304 | 0.096372 | 0.1324 | 0.018713 | 0.01998 | 0.36067 | -0.0063462 | 0.084429 | 0.044354 | 0.0029108 | -0.0039584 | 70.5276 | 70.5963 | 15.8386 | -49.5804 | 70.6284 | -52.5192 | -52.5604 | -48.2437 | 0.09613 | -52.652 | 70.5917 | 70.5551 | -52.6108 | -52.6611 | -0.059509 | -0.10071 | 0.091553 | 123.056 | 2.8793 | 2.98 | -0.009155 | -0.15106 | -0.20142 | 0.054932 | 4.216 | -0.19226 | 0.009155 | 0.018311 | 123.0881 | 122.9874 | 68.2983 | -123.0972 | 123.0515 | 123.0148 | 52.5558 | -123.1979
569.6875 | 123.2803 | -52.0111 | 70.9671 | 0.44625 | 0.05571 | 0.090257 | 0.11346 | 0.14094 | 0.020849 | 0.013571 | 0.40644 | -0.013823 | 0.069475 | 0.064648 | 0.0071838 | -0.012503 | 71.3242 | 71.3974 | 14.8178 | -48.056 | 71.4157 | -51.7273 | -51.8417 | -47.6212 | 0.43945 | -52.2491 | 71.0953 | 71.0312 | -52.1301 | -52.1942 | 0.28381 | 0.16937 | 0.44861 | 123.4085 | 3.9551 | 3.7857 | 0.35706 | -0.11902 | -0.18311 | 0.12817 | 4.39 | -0.23804 | -0.054932 | 0.064087 | 123.4268 | 123.3353 | 66.8289 | -122.8088 | 123.1064 | 123.0423 | 52.4506 | -123.1613
570.6875 | 123.3444 | -51.5945 | 71.3882 | 0.3547 | 0.030075 | 0.085985 | 0.099577 | 0.13881 | 0.015508 | 0.015708 | 0.43696 | -0.012754 | 0.070543 | 0.050762 | 0.0061158 | -0.018912 | 71.1914 | 71.315 | 13.6505 | -48.9166 | 71.2372 | -51.86 | -51.8372 | -46.8658 | 0.8606 | -51.5991 | 71.6217 | 71.5622 | -51.5854 | -51.6815 | -0.2655 | -0.24262 | -0.15106 | 122.9095 | 2.6779 | 2.9205 | -0.19684 | 0.009155 | -0.086976 | 0.23346 | 4.7287 | -0.004578 | 0.082398 | 0.17395 | 122.8317 | 122.7859 | 65.2451 | -123.2254 | 123.2162 | 123.1567 | 52.4551 | -123.0698
571.7031 | 123.2758 | -51.5259 | 71.4798 | 0.049525 | -0.008377 | 0.098802 | 0.11453 | 0.14094 | -0.016535 | -0.001382 | -0.005544 | -0.010618 | 0.052385 | 0.057171 | -0.0013612 | -0.011435 | 71.4478 | 71.6034 | 12.4191 | -48.0469 | 71.5439 | -51.5442 | -51.622 | -46.8521 | 0.73242 | -51.6998 | 71.5622 | 71.5118 | -51.6266 | -51.7044 | -0.01831 | -0.09613 | 0.064087 | 123.1293 | 3.479 | 3.5751 | -0.032043 | -0.10071 | -0.17853 | 0.082398 | 4.6738 | -0.17395 | 0.004578 | 0.032044 | 123.0698 | 122.9736 | 63.945 | -123.1018 | 123.0881 | 123.0377 | 52.2583 | -123.1842
572.6875 | 123.2162 | -51.7273 | 71.3562 | 0.33944 | 0.064255 | 0.096666 | 0.11133 | 0.13774 | 0.035802 | 0.005026 | 0.20808 | -0.0063462 | 0.084429 | 0.053967 | 0.0050478 | -0.017843 | 71.2555 | 71.3745 | 13.2019 | -47.9782 | 71.4523 | -51.7685 | -51.7731 | -46.9116 | 0.12817 | -51.9608 | 71.4249 | 71.3745 | -51.8234 | -51.9058 | -0.041199 | -0.045776 | 0.096131 | 123.1018 | 3.7491 | 3.7949 | -0.10071 | -0.09613 | -0.17853 | 0.068665 | 4.8157 | -0.23346 | -0.054931 | 0.018311 | 123.1796 | 122.9828 | 64.9292 | -123.1293 | 123.1522 | 123.1018 | 51.8555 | -123.262
573.6875 | 123.3078 | -51.2924 | 71.7087 | 0.41574 | 0.048233 | 0.08278 | 0.11133 | 0.13987 | 0.03153 | 0.011435 | 0.34541 | -0.0042092 | 0.061998 | 0.052899 | 0.013592 | -0.01998 | 71.6858 | 71.727 | 15.152 | -48.1293 | 71.7819 | -51.3611 | -51.4069 | -46.3348 | 0.42114 | -51.4938 | 71.7865 | 71.7453 | -51.4206 | -51.4847 | -0.068665 | -0.11444 | 0.073242 | 123.0194 | 3.1631 | 3.2776 | -0.022888 | -0.12817 | -0.19226 | 0.07782 | 4.9576 | -0.20142 | -0.009155 | 0.036621 | 123.0743 | 122.9782 | 66.4444 | -123.1155 | 123.0789 | 123.0377 | 51.7136 | -123.1934
574.6875 | 123.3032 | -51.535 | 71.434 | 0.36996 | 0.035415 | 0.090257 | 0.10171 | 0.15162 | 0.022985 | 0.017844 | 0.4217 | -0.0031412 | 0.068407 | 0.053967 | 0.0039788 | -0.013571 | 71.5256 | 71.6263 | 17.5507 | -48.0103 | 71.5393 | -51.5259 | -51.5991 | -46.3257 | 0.15106 | -51.6678 | 71.5713 | 71.5027 | -51.622 | -51.709 | 0.009155 | -0.064087 | 0.10529 | 123.1613 | 3.5248 | 3.5889 | 0.091553 | -0.086975 | -0.17395 | 0.13733 | 5.2094 | -0.13275 | 0.041198 | 0.068665 | 123.0743 | 123.0606 | 69.0857 | -123.0331 | 123.1064 | 123.0377 | 51.6861 | -123.143
575.6875 | 123.3536 | -51.4343 | 71.5576 | 0.41574 | 0.062118 | 0.09987 | 0.11239 | 0.15376 | 0.017644 | 0.013571 | 0.45222 | -0.0010052 | 0.068407 | 0.056103 | 0.0071838 | -0.013571 | 71.608 | 71.7133 | 18.0634 | -47.8363 | 71.6354 | -51.4252 | -51.503 | -46.0373 | -0.050354 | -51.5533 | 71.6995 | 71.6171 | -51.5076 | -51.6083 | 0.009155 | -0.068665 | 0.07782 | 123.1476 | 3.598 | 3.6667 | 0.050354 | -0.073242 | -0.17395 | 0.14191 | 5.397 | -0.11902 | 0.054931 | 0.059509 | 123.0698 | 123.0423 | 69.4977 | -123.0606 | 123.1338 | 123.0515 | 51.384 | -123.1659
576.7031 | 123.1934 | -49.9283 | 73.1461 | -0.53031 | 0.035415 | 0.10308 | 0.11774 | 0.14094 | 0.020849 | 0.007163 | -0.5396 | -0.0042092 | 0.071611 | 0.060376 | -0.0045652 | -0.014639 | 73.0774 | 73.1415 | 17.3264 | -45.8954 | 73.2422 | -49.9374 | -49.9924 | -44.4534 | 1.3687 | -50.0565 | 73.3429 | 73.2788 | -49.9649 | -50.0565 | -0.009155 | -0.064087 | 0.09613 | 123.0698 | 4.0329 | 4.097 | -0.068664 | -0.036621 | -0.12817 | 0.19684 | 5.4749 | -0.12817 | 0 | 0.13275 | 123.1705 | 123.0057 | 67.2546 | -123.1384 | 123.2712 | 123.2071 | 51.297 | -123.2025
577.6875 | 123.3582 | -49.3469 | 73.6633 | 0.38522 | 0.041824 | 0.10628 | 0.10812 | 0.15483 | 0.022985 | 0.013571 | 0.34541 | -0.021299 | 0.072679 | 0.072125 | 0.016797 | -0.01998 | 73.5626 | 73.7137 | 18.8278 | -45.5841 | 73.6176 | -49.4385 | -49.5163 | -43.7393 | 1.4648 | -49.4843 | 73.7412 | 73.6771 | -49.4751 | -49.5483 | -0.091553 | -0.16937 | -0.045776 | 123.0606 | 3.7628 | 3.9322 | -0.10071 | -0.12817 | -0.20142 | 0.07782 | 5.6076 | -0.13733 | 0.064087 | 0.013733 | 122.9645 | 122.9095 | 68.1747 | -123.1796 | 123.0881 | 123.024 | 50.8118 | -123.2117
578.6875 | 123.3032 | -50.0198 | 72.963 | 0.49203 | 0.062118 | 0.096666 | 0.1156 | 0.14521 | 0.022985 | 0.010367 | 0.40644 | -0.0063462 | 0.075884 | 0.050762 | 0.011456 | -0.015707 | 72.908 | 73.0408 | 19.8578 | -44.5633 | 72.9584 | -50.1251 | -50.2075 | -44.2612 | 0.50812 | -50.1938 | 73.0179 | 72.9492 | -50.1801 | -50.2396 | -0.10529 | -0.18768 | -0.004578 | 123.0606 | 5.4565 | 5.6442 | -0.054932 | -0.16022 | -0.21973 | 0.054931 | 5.7587 | -0.17395 | 0.045776 | -0.013733 | 122.9782 | 122.9279 | 69.8776 | -123.1705 | 123.0377 | 122.9691 | 50.528 | -123.2025
579.6875 | 123.2941 | -49.5438 | 73.4711 | 0.46151 | 0.04396 | 0.10094 | 0.11239 | 0.14308 | 0.036871 | 0.025321 | 0.36067 | -0.0052782 | 0.061998 | 0.049694 | 0.012524 | -0.013571 | 73.3887 | 73.4894 | 21.199 | -45.575 | 73.5123 | -49.6033 | -49.6857 | -43.6432 | 0.57678 | -49.7498 | 73.5352 | 73.4711 | -49.6582 | -49.7498 | -0.059509 | -0.14191 | 0.041199 | 123.0331 | 3.9688 | 4.1107 | -0.082397 | -0.11444 | -0.20599 | 0.064087 | 5.9006 | -0.20599 | 0 | 0 | 123.056 | 122.9324 | 70.7428 | -123.1567 | 123.0789 | 123.0148 | 50.1205 | -123.2208
580.6875 | 123.317 | -49.3011 | 73.6771 | 0.52255 | 0.045028 | 0.11162 | 0.12521 | 0.1623 | 0.03153 | 0.023184 | 0.39118 | -0.019163 | 0.073747 | 0.057171 | 0.0082518 | -0.0060944 | 73.6954 | 73.8052 | 15.9348 | -44.8975 | 73.7137 | -49.3469 | -49.4293 | -43.4097 | 0.6134 | -49.3881 | 73.7412 | 73.6633 | -49.4064 | -49.4659 | -0.045777 | -0.12817 | 0.036621 | 123.1064 | 4.4037 | 4.5319 | 0.018311 | -0.10529 | -0.16479 | 0.064087 | 5.8914 | -0.086976 | 0.077819 | -0.013733 | 123.0148 | 122.9965 | 65.2359 | -123.1064 | 123.0423 | 122.9645 | 49.9145 | -123.143
581.7031 | 123.2208 | -49.1501 | 73.8785 | -0.49979 | 0.042892 | 0.11162 | 0.12948 | 0.15803 | 0.013372 | 0.01998 | -0.41753 | -0.0074142 | 0.066271 | 0.056103 | 0.0007748 | -0.0082304 | 73.819 | 73.9563 | 16.6718 | -44.4901 | 73.9014 | -49.2142 | -49.2828 | -43.0206 | 0.55389 | -49.3744 | 73.938 | 73.8602 | -49.3378 | -49.3652 | -0.064087 | -0.13275 | 0.022888 | 123.1064 | 4.66 | 4.7928 | -0.059509 | -0.18768 | -0.21515 | 0.059509 | 6.1295 | -0.22431 | -0.009156 | -0.018311 | 123.0515 | 122.9691 | 65.8218 | -123.1613 | 123.0881 | 123.0103 | 49.704 | -123.2437
582.6875 | 123.2574 | -48.8388 | 74.1348 | 0.30892 | 0.034347 | 0.11696 | 0.14123 | 0.1591 | 0.0091004 | 0.01998 | 0.34541 | -0.012754 | 0.054521 | 0.059307 | 0.0018428 | -0.0071624 | 74.1302 | 74.2859 | 12.3138 | -44.5862 | 74.1898 | -48.8525 | -48.9304 | -42.4622 | 0.82398 | -49.0219 | 74.2447 | 74.1577 | -48.967 | -49.0631 | -0.013733 | -0.091553 | 0.054931 | 123.1247 | 4.2526 | 4.3442 | -0.004578 | -0.12817 | -0.2243 | 0.10986 | 6.3766 | -0.18311 | 0.041198 | 0.022888 | 123.0286 | 122.9691 | 61.1526 | -123.0652 | 123.0835 | 122.9965 | 49.6628 | -123.1979
583.6875 | 123.2346 | -47.0764 | 75.9155 | 0.3547 | 0.012985 | 0.1223 | 0.12308 | 0.14308 | 0.012304 | 0.034934 | 0.28437 | -0.011686 | 0.065202 | 0.06358 | -0.0013612 | -0.00075443 | 75.9018 | 76.0757 | -7.1411 | -43.2083 | 75.9842 | -47.081 | -47.168 | -40.5579 | 1.8356 | -47.2687 | 76.03 | 75.9109 | -47.1817 | -47.2641 | -0.004578 | -0.091553 | 0.068665 | 123.1522 | 3.8681 | 3.9597 | -0.013733 | -0.10529 | -0.18768 | 0.11444 | 6.5186 | -0.19226 | -0.004578 | -0.004577 | 123.0606 | 122.9782 | 39.9353 | -123.0835 | 123.1064 | 122.9874 | 48.912 | -123.1796
584.6875 | 123.2529 | -48.674 | 74.3179 | 0.1716 | 0.030075 | 0.1191 | 0.13162 | 0.16017 | 0.0069634 | 0.026389 | 0.10127 | -0.010618 | 0.072679 | 0.057171 | -0.0056342 | -0.012503 | 74.3179 | 74.4415 | 5.0766 | -43.8766 | 74.4278 | -48.6557 | -48.7244 | -41.9907 | 1.1444 | -48.8708 | 74.4049 | 74.3317 | -48.7839 | -48.8525 | 0.01831 | -0.050354 | 0.10986 | 123.1155 | 4.7974 | 4.8477 | 0 | -0.10986 | -0.17853 | 0.086975 | 6.6833 | -0.19684 | -0.018311 | 0.013733 | 123.1018 | 122.9919 | 53.7506 | -123.0423 | 123.0789 | 123.0057 | 49.8184 | -123.1705
585.6875 | 123.2986 | -48.6877 | 74.2538 | 0.44625 | 0.034347 | 0.12657 | 0.15405 | 0.17833 | 0.042211 | 0.025321 | -0.26494 | -0.0095502 | 0.053453 | 0.042218 | 0.013592 | -0.012503 | 74.2905 | 74.2538 | 7.6447 | -43.9316 | 74.2996 | -48.7976 | -48.8571 | -41.7526 | -0.091553 | -48.8434 | 74.3729 | 74.2813 | -48.7885 | -48.8434 | -0.10986 | -0.16937 | 0.045777 | 122.9416 | 4.7562 | 4.9255 | 0.036621 | -0.10071 | -0.15564 | 0.11902 | 6.9351 | -0.15564 | 0 | 0.027466 | 122.9874 | 122.9782 | 56.3324 | -123.111 | 123.0606 | 122.9691 | 48.5962 | -123.0972
586.7031 | 123.2437 | -48.9212 | 74.0799 | 0.24789 | 0.073868 | 0.12657 | 0.13696 | 0.17833 | 0.027258 | 0.040274 | -0.46331 | -0.014891 | 0.086565 | 0.051831 | 0.0082518 | -0.016775 | 74.057 | 74.2172 | 8.812 | -44.2749 | 74.1165 | -48.9624 | -49.0219 | -41.8259 | -0.38452 | -49.054 | 74.2126 | 74.1119 | -49.0356 | -49.0677 | -0.041198 | -0.10071 | 0.036621 | 123.1384 | 4.6463 | 4.747 | -0.022888 | -0.11444 | -0.14648 | 0.13275 | 7.0953 | -0.13275 | 0.013733 | 0.032043 | 123.0377 | 122.9782 | 57.7332 | -123.1018 | 123.1339 | 123.0331 | 48.5367 | -123.1476
587.6875 | 123.2208 | -49.3286 | 73.7 | 0.24789 | 0.041824 | 0.13405 | 0.14444 | 0.17833 | 0.029394 | 0.038138 | 0.29963 | -0.0031412 | 0.069475 | 0.055035 | 0.012524 | -0.0071624 | 73.6816 | 73.8876 | 5.1727 | -43.7759 | 73.7869 | -49.2783 | -49.3286 | -42.1051 | -8.1528 | -49.4888 | 73.7503 | 73.6588 | -49.4522 | -49.5026 | 0.050354 | 0 | 0.086975 | 123.2162 | 5.5527 | 5.5527 | -0.01831 | -0.1236 | -0.17395 | 0.050354 | 7.2235 | -0.16022 | 0.013732 | -0.041199 | 123.1155 | 123.0103 | 54.5013 | -123.0286 | 123.0789 | 122.9874 | 41.1758 | -123.2025
588.6875 | 123.2391 | -48.8937 | 74.1302 | 0.15634 | 0.015121 | 0.12444 | 0.14871 | 0.17833 | 0.021917 | 0.029593 | 0.086009 | -0.017027 | 0.058794 | 0.06892 | 0.0018428 | -0.01998 | 74.1119 | 74.2493 | 1.5564 | -43.5471 | 74.176 | -48.88 | -48.9487 | -41.5009 | -8.0017 | -49.0585 | 74.2081 | 74.1211 | -48.999 | -49.0677 | 0.013733 | -0.054931 | 0.045776 | 123.143 | 5.3467 | 5.4016 | -0.018311 | -0.10529 | -0.17395 | 0.07782 | 7.3929 | -0.16479 | 0.009155 | -0.009155 | 123.0698 | 123.0057 | 50.4501 | -123.0789 | 123.1018 | 123.0148 | 40.892 | -123.1979
589.6875 | 123.2346 | -49.5438 | 73.5077 | 0.21737 | 0.029007 | 0.14153 | 0.15405 | 0.18901 | 0.024053 | 0.044547 | 0.10127 | -0.0084822 | 0.074815 | 0.057171 | 0.014661 | -0.0082304 | 73.407 | 73.4756 | 3.4882 | -43.9911 | 73.4665 | -49.6216 | -49.6902 | -41.7435 | -5.7037 | -49.7864 | 73.4848 | 73.3658 | -49.7131 | -49.7314 | -0.07782 | -0.14648 | -0.041198 | 123.0194 | 5.5527 | 5.6992 | -0.10071 | -0.16937 | -0.18768 | -0.022888 | 7.8003 | -0.24262 | -0.054932 | -0.14191 | 123.0103 | 122.9507 | 53.0319 | -123.1979 | 123.0286 | 122.9095 | 43.84 | -123.2391
590.6875 | 123.2346 | -49.3652 | 73.6084 | 0.034266 | 0.031143 | 0.12551 | 0.15405 | 0.17833 | 0.021917 | 0.031729 | -0.05132 | -0.0042092 | 0.070543 | 0.045422 | 0.0029108 | -0.0060944 | 73.6084 | 73.7183 | 2.4536 | -43.6798 | 73.6908 | -49.4019 | -49.4522 | -41.3269 | -6.2622 | -49.4934 | 73.7503 | 73.613 | -49.4522 | -49.5529 | -0.036621 | -0.086975 | 0.082398 | 123.0835 | 5.6854 | 5.7724 | 0 | -0.086975 | -0.18768 | 0.14191 | 8.0383 | -0.12817 | 0.059509 | 0.004578 | 123.056 | 122.9736 | 51.8188 | -123.0606 | 123.1155 | 122.9782 | 43.103 | -123.1613
591.6875 | 123.2254 | -49.5483 | 73.4573 | 0.1716 | 0.017257 | 0.12871 | 0.16046 | 0.19221 | 0.034734 | 0.043479 | 0.10127 | -0.0074142 | 0.064134 | 0.051831 | -0.0013612 | -0.012503 | 73.3841 | 73.5168 | 4.3213 | -43.8721 | 73.4985 | -49.585 | -49.6582 | -41.3452 | -4.2847 | -49.704 | 73.5123 | 73.4161 | -49.6811 | -49.7269 | -0.036621 | -0.10986 | 0.041199 | 123.0652 | 5.6763 | 5.7861 | -0.073242 | -0.13275 | -0.17853 | 0.054932 | 8.2031 | -0.15564 | 0.022889 | -0.041198 | 123.0469 | 122.9324 | 53.8696 | -123.1155 | 123.0606 | 122.9645 | 45.2637 | -123.1842
592.6875 | 123.262 | -49.4888 | 73.494 | 0.080043 | 0.034347 | 0.12871 | 0.16046 | 0.17939 | 0.027258 | 0.050955 | 0.14704 | 0.0043348 | 0.058794 | 0.067852 | 0.0082518 | -0.012503 | 73.3704 | 73.5306 | 4.2206 | -43.3365 | 73.558 | -49.5346 | -49.5895 | -41.1255 | -0.68207 | -49.6536 | 73.6084 | 73.4848 | -49.6033 | -49.6811 | -0.045776 | -0.10071 | 0.064086 | 123.0194 | 6.1523 | 6.2531 | -0.1236 | -0.11444 | -0.19226 | 0.11444 | 8.3633 | -0.16479 | 0.027466 | -0.009156 | 123.0469 | 122.8592 | 53.7094 | -123.0835 | 123.0972 | 122.9736 | 48.8068 | -123.175
593.6875 | 123.2254 | -46.9345 | 76.0071 | 0.27841 | 0.041824 | 0.1426 | 0.15832 | 0.1623 | 0.03153 | 0.082999 | 0.2386 | -0.010618 | 0.067339 | 0.041149 | 0.0071838 | -0.018912 | 75.9613 | 76.1215 | -37.2757 | -41.1346 | 76.0391 | -46.9666 | -47.0581 | -38.4933 | -2.5772 | -47.1634 | 76.1032 | 75.975 | -47.113 | -47.1588 | -0.032044 | -0.1236 | 0.032044 | 123.056 | 5.7999 | 5.9235 | -0.045776 | -0.17853 | -0.2243 | 0.09613 | 8.4412 | -0.22888 | -0.004578 | -0.032043 | 122.9736 | 122.8958 | 9.6588 | -123.0652 | 123.0377 | 122.9095 | 44.3573 | -123.1659
594.6875 | 123.2574 | -46.7972 | 76.0025 | -1.1559 | 0.002304 | 0.18105 | 0.17221 | 0.16764 | 0.010168 | 0.10329 | -0.081838 | -0.0074142 | 0.068407 | 0.073193 | 0.010388 | -0.0071624 | 76.2085 | 76.4145 | -35.6598 | -42.6819 | 76.3641 | -46.7056 | -46.7697 | -37.9669 | -0.33417 | -46.6599 | 76.5244 | 76.4099 | -46.6599 | -46.7422 | 0.091553 | 0.027466 | 0.36163 | 123.2117 | 4.1153 | 4.0878 | 0.20599 | 0.13733 | 0.054931 | 0.52185 | 8.8303 | 0.13733 | 0.082398 | 0.40741 | 123.1613 | 123.0057 | 11.1374 | -122.7722 | 123.3215 | 123.2071 | 46.463 | -122.7448
595.6875 | 123.2529 | -47.1313 | 75.8377 | -3.0785 | 0.019394 | 0.16503 | 0.16366 | 0.17085 | 0.016576 | 0.090476 | -0.066579 | -0.015959 | 0.061998 | 0.062512 | 0.012524 | -0.01998 | 75.769 | 75.9293 | -38.0905 | -43.1122 | 75.9247 | -47.1954 | -47.2321 | -38.4521 | -2.2888 | -47.3099 | 75.9201 | 75.7919 | -47.2961 | -47.3602 | -0.064087 | -0.10071 | 0.086975 | 123.0606 | 4.0192 | 4.1199 | -0.068665 | -0.16479 | -0.22888 | 0.082397 | 8.6792 | -0.17853 | 0.050354 | -0.045777 | 123.056 | 122.9004 | 9.0408 | -123.0698 | 123.0515 | 122.9233 | 44.8425 | -123.1979
596.6875 | 123.2712 | -47.1359 | 75.7965 | 0.095301 | 0.00016795 | 0.1725 | 0.18182 | 0.17939 | 0.029394 | 0.10329 | -0.081838 | -0.011686 | 0.067339 | 0.066784 | 0.0061158 | -0.015707 | 75.7187 | 75.8972 | -37.7792 | -42.4942 | 75.8789 | -47.1954 | -47.2687 | -38.3835 | -1.2405 | -47.3145 | 75.9018 | 75.7645 | -47.3328 | -47.374 | -0.05951 | -0.13275 | 0.082397 | 123.0331 | 4.6417 | 4.7745 | -0.07782 | -0.19684 | -0.23804 | 0.10528 | 8.7524 | -0.17853 | 0.059509 | -0.032044 | 123.0148 | 122.8546 | 9.3567 | -123.0652 | 123.0377 | 122.9004 | 45.8954 | -123.1705
597.6875 | 123.2712 | -45.8954 | 77.0645 | -0.042028 | 0.031143 | 0.012285 | 0.67956 | 0.24134 | 0.39255 | 0.061637 | -0.097097 | -0.013823 | 0.061998 | 0.051831 | 0.012524 | -0.0050264 | -11.4029 | 77.0416 | -41.1163 | 28.8162 | 77.092 | -45.9412 | -45.9915 | -36.9873 | -2.2751 | -45.9824 | 77.1561 | 77.0416 | -46.019 | -46.0739 | -0.045776 | -0.09613 | 0.027466 | 122.937 | 74.7116 | 74.8077 | -88.4674 | -0.1236 | -0.17853 | 0.091553 | 8.9081 | -0.086975 | 0.091553 | -0.022888 | 122.9874 | 34.4925 | 4.7791 | -123.056 | 123.0515 | 122.937 | 43.6203 | -123.1384
598.6875 | 123.1842 | -43.6615 | 79.2389 | -0.01151 | 0.030075 | 0.0048081 | 1.2852 | 1.051 | 0.17359 | 0.039206 | 0.055491 | -0.0074142 | 0.065202 | 0.069989 | 0.012524 | -0.0060944 | -11.0367 | 79.1748 | -36.5112 | -15.4907 | 79.2206 | -43.6066 | -43.6935 | -34.7351 | 0.068665 | -43.808 | 79.3579 | 79.2023 | -43.7851 | -43.8446 | 0.054932 | -0.032043 | -0.018311 | 122.8363 | 28.1708 | 28.2028 | -90.2756 | -0.1236 | -0.1831 | 0.11902 | 8.9264 | -0.14648 | 0.036621 | -0.036621 | 122.8821 | 32.6248 | 7.1503 | -122.9324 | 123.0194 | 122.8638 | 43.7302 | -123.0835
599.6875 | 123.1247 | -51.4343 | 71.489 | 0.29367 | 0.02687 | 0.14153 | 1.7359 | 1.6918 | 0.087072 | 0.079795 | -0.097097 | -0.012754 | 0.079088 | 0.069989 | 0.0029108 | -0.013571 | 72.3633 | 72.3816 | -2.5726 | -35.9116 | 72.4457 | -50.2213 | -50.3448 | -42.6773 | -8.5464 | -51.5442 | 71.4752 | 71.3882 | -51.5396 | -51.6037 | 1.2131 | 1.0895 | 0.95673 | 123.8159 | 15.5228 | 14.4333 | 0.87433 | -0.10529 | -0.16937 | -0.013733 | 8.757 | -0.10986 | 0.05951 | -0.10071 | 123.88 | 123.7976 | 48.8617 | -121.8338 | 122.9095 | 122.8226 | 42.8879 | -123.0927
600.6875 | 123.1522 | -51.265 | 71.6034 | 0.44625 | 0.047165 | 0.15969 | 0.20959 | 0.22853 | 0.011236 | 0.13427 | -0.020803 | -0.0095502 | 0.053453 | 0.055035 | 0.013592 | -0.011435 | 71.6034 | 71.7178 | -22.4945 | -50.8392 | 71.7087 | -51.2878 | -51.3199 | -42.3248 | -9.8282 | -51.3611 | 71.7178 | 71.608 | -51.3702 | -51.4389 | -0.022888 | -0.054931 | 0.10529 | 122.9828 | 0.42572 | 0.48065 | 0 | -0.10528 | -0.17395 | 0.11444 | 8.9401 | -0.09613 | 0.07782 | 0.004577 | 122.9736 | 122.8683 | 28.7704 | -122.9233 | 122.9828 | 122.8729 | 41.4368 | -123.0423
601.6875 | 123.2254 | -48.0331 | 74.8215 | -0.01151 | 0.13475 | 0.13832 | 0.14657 | 0.21891 | 0.012304 | 0.1599 | -0.23443 | -0.0042092 | 0.056658 | 0.060376 | 0.010388 | -0.0060944 | 72.4915 | 72.6562 | 43.4692 | -50.1205 | 72.5327 | -50.354 | -50.0107 | -38.8092 | -4.9438 | -48.0606 | 74.9268 | 74.7849 | -48.1842 | -48.2529 | -2.3209 | -1.9775 | -2.2888 | 120.6894 | -2.0874 | -0.10986 | -2.33 | -0.15106 | -0.21973 | 0.10529 | 9.2239 | -0.027466 | 0.19226 | -0.036621 | 120.5658 | 120.5246 | 91.5024 | -124.8322 | 122.9599 | 122.818 | 43.0893 | -123.0743
602.6875 | 123.1979 | -56.8863 | 66.0004 | -0.026769 | 0.16893 | 0.10628 | 0.18823 | 0.25523 | -0.0037176 | 0.12786 | -0.26494 | -0.0084822 | 0.056658 | 0.06358 | 0.0071838 | -0.0060944 | 65.9866 | 66.1469 | 65.3961 | -56.3873 | 66.0095 | -56.9916 | -57.019 | -47.438 | -13.3896 | -56.9183 | 66.0416 | 65.9546 | -57.0374 | -57.1014 | -0.10529 | -0.13275 | 0.009155 | 123.0331 | 0.49896 | 0.63171 | -0.013733 | -0.15106 | -0.21515 | 0.041199 | 9.4482 | -0.032043 | 0.1831 | -0.045776 | 122.8958 | 122.8729 | 122.2824 | -123.0194 | 122.9279 | 122.8409 | 43.4967 | -123.1018
603.6875 | 123.2712 | -53.6865 | 69.2047 | -0.25565 | 0.10698 | 0.10201 | 0.13803 | 0.21785 | -0.00051261 | 0.084067 | -0.23443 | -0.0031412 | 0.06093 | 0.044354 | 0.0029108 | -0.012503 | 69.278 | 69.4244 | 69.1772 | -53.1784 | 69.3146 | -53.6911 | -53.7598 | -43.808 | -8.4503 | -53.714 | 69.3192 | 69.1864 | -53.8193 | -53.8834 | -0.004578 | -0.073243 | 0.10986 | 123.111 | 0.50812 | 0.58136 | 0.073242 | -0.13275 | -0.19684 | 0.11444 | 9.8785 | -0.027466 | 0.16937 | -0.018311 | 123.0011 | 122.9645 | 122.8638 | -122.9645 | 123.0057 | 122.8729 | 45.2362 | -123.0881
604.6875 | 123.262 | -57.9391 | 64.9429 | -0.026769 | 0.11232 | 0.10201 | 0.19891 | 0.25737 | -0.0058536 | 0.090476 | -0.26494 | -0.012754 | 0.069475 | 0.066784 | 0.011456 | -0.0050264 | 64.9841 | 65.1398 | 64.9933 | -57.3349 | 65.0162 | -57.9666 | -57.9437 | -48.3856 | -14.1998 | -57.9117 | 65.0391 | 64.9155 | -58.049 | -58.1314 | -0.027466 | -0.004578 | 0.073242 | 123.0789 | 0.60425 | 0.60883 | 0.041199 | -0.10986 | -0.19226 | 0.09613 | 9.5535 | 0.027466 | 0.21973 | -0.027466 | 122.9553 | 122.9233 | 122.9324 | -122.8867 | 122.9782 | 122.8546 | 43.7393 | -123.0743
605.6875 | 123.2529 | -58.0353 | 64.8788 | -0.20987 | 0.098434 | 0.10521 | 0.20318 | 0.26057 | -0.0026496 | 0.084067 | -0.21917 | -0.0020732 | 0.074815 | 0.051831 | 0.0093198 | -0.0092984 | 64.9155 | 65.0665 | 64.9704 | -57.3074 | 64.9658 | -58.0444 | -58.1085 | -48.4863 | -15.0009 | -57.9987 | 64.9475 | 64.8102 | -58.1635 | -58.2275 | -0.009156 | -0.073243 | 0.086975 | 123.1018 | 0.72784 | 0.80109 | 0.036621 | -0.12817 | -0.19226 | 0.068665 | 9.5489 | 0.036621 | 0.22888 | -0.068664 | 123.0011 | 122.9507 | 123.0057 | -122.9874 | 122.9828 | 122.8455 | 43.0344 | -123.1064
606.6875 | 123.2574 | -55.6824 | 67.1997 | 0.1716 | 0.090957 | 0.10842 | 0.31534 | 0.38661 | 0.0058954 | 0.084067 | -0.11236 | -0.019163 | 0.068407 | 0.064648 | 0.012524 | 0.0067226 | 67.1036 | 67.2638 | 67.1906 | -53.9474 | 67.2546 | -55.7419 | -55.806 | -46.0922 | -11.998 | -55.7098 | 67.3096 | 67.186 | -55.8151 | -55.8563 | -0.059509 | -0.1236 | 0.054932 | 122.9462 | 1.7349 | 1.8585 | -0.09613 | -0.13275 | -0.17395 | 0.10986 | 9.5901 | -0.027466 | 0.14648 | -0.013733 | 122.937 | 122.7859 | 122.8729 | -123.0057 | 122.9919 | 122.8683 | 43.6844 | -123.056
607.6875 | 123.2849 | -51.178 | 71.7133 | -0.17936 | 0.12086 | 0.11589 | 0.1626 | 0.2563 | 0.0091004 | 0.095816 | -0.15813 | -0.0074142 | 0.053453 | 0.050762 | 0.011456 | -0.00075443 | 71.4478 | 71.6354 | 71.5485 | -50.5646 | 71.553 | -51.4206 | -51.4801 | -41.7023 | -6.7474 | -51.178 | 71.7178 | 71.6034 | -51.3382 | -51.4023 | -0.24261 | -0.30212 | -0.16022 | 122.8134 | 0.6134 | 0.91553 | -0.2655 | -0.16022 | -0.2243 | 0.004577 | 9.4757 | 0 | 0.2243 | -0.10986 | 122.731 | 122.6257 | 122.7264 | -123.1934 | 122.8958 | 122.7814 | 44.4305 | -123.1155
608.6875 | 123.1842 | -50.9766 | 71.9238 | -0.30143 | 0.17107 | 0.11589 | 0.15619 | 0.26805 | 0.01444 | 0.12359 | -0.41753 | -0.0052782 | 0.088701 | 0.074261 | 0.0082518 | -0.018912 | 71.9376 | 72.1115 | 71.9879 | -50.1572 | 71.9833 | -51.0178 | -51.0818 | -41.2766 | -7.3746 | -51.0361 | 71.9604 | 71.8323 | -51.1505 | -51.1826 | -0.041199 | -0.10529 | 0.059509 | 123.0881 | 0.8194 | 0.92468 | 0.013733 | -0.17395 | -0.20599 | 0.036621 | 9.7 | -0.05951 | 0.14648 | -0.091553 | 122.9599 | 122.9141 | 122.9645 | -123.0057 | 122.937 | 122.8088 | 43.602 | -123.1064
609.6875 | 123.2117 | -51.6586 | 71.2326 | -0.33194 | 0.16038 | 0.11269 | 0.15085 | 0.26912 | 0.0069634 | 0.089408 | -0.43279 | -0.0095502 | 0.073747 | 0.050762 | -0.0056342 | -0.0060944 | 71.2463 | 71.434 | 71.2967 | -50.8392 | 71.2784 | -51.709 | -51.7639 | -42.1463 | -7.2235 | -51.6632 | 71.315 | 71.1639 | -51.8188 | -51.86 | -0.050354 | -0.10529 | 0.045776 | 123.0927 | 0.8194 | 0.92468 | 0.013733 | -0.16022 | -0.20142 | 0.082397 | 9.5123 | -0.004578 | 0.19684 | -0.068665 | 122.937 | 122.905 | 122.9553 | -122.9965 | 122.9736 | 122.8226 | 44.4351 | -123.0927
610.6875 | 123.1888 | -83.5464 | 39.2624 | -0.31669 | 0.051437 | 0.018693 | 0.016264 | -0.0064582 | 0.0026914 | 0.012503 | 0.20808 | -0.010618 | 0.061998 | 0.060376 | 0.027478 | -0.0050264 | 39.1617 | 39.3311 | 39.1937 | 36.1954 | 39.1525 | 8.6243 | 8.7982 | -74.0067 | -36.5158 | -83.4091 | 39.3539 | 39.2395 | -83.7433 | -83.8028 | 92.1707 | 92.3447 | -0.10986 | 122.8775 | 119.7418 | 27.3972 | -0.10071 | -0.19684 | -0.25635 | 0.091553 | 9.5398 | 0.13733 | 0.39368 | -0.022888 | 122.699 | 122.7081 | 122.7402 | -30.4642 | 122.9004 | 122.7859 | 47.0306 | -123.0652
611.6875 | 123.2254 | -84.2468 | 38.681 | -0.43876 | 0.057846 | 0.010148 | 0.028013 | -0.0075262 | -0.0026496 | 0.018912 | -5.8497 | -0.010618 | 0.067339 | 0.06892 | 0.0093198 | -0.010367 | 38.5254 | 38.6902 | 38.5574 | 35.8566 | 38.5025 | 8.638 | 8.7982 | -74.7665 | -36.8088 | -84.0591 | 38.7131 | 38.5986 | -84.4025 | -84.462 | 92.8848 | 93.045 | -0.17853 | 122.937 | 120.1035 | 27.0584 | -0.15564 | -0.15564 | -0.21515 | 0.032044 | 9.4803 | 0.18768 | 0.40283 | -0.082397 | 122.7493 | 122.7722 | 122.8043 | -29.8828 | 122.9599 | 122.8455 | 47.438 | -123.143
612.6875 | 123.2391 | -84.5215 | 38.4064 | -0.46927 | 0.06105 | 0.019762 | 0.021604 | -0.0085942 | 0.0091004 | 0.017844 | -0.47857 | -0.0074142 | 0.076952 | 0.055035 | 0.015729 | -0.0082304 | 38.063 | 38.2004 | 38.063 | 35.6186 | 38.0219 | 8.6472 | 8.8028 | -74.2767 | -38.1866 | -84.3933 | 38.4338 | 38.3469 | -84.6817 | -84.7458 | 93.1686 | 93.3243 | -0.38452 | 122.7219 | 120.1401 | 26.8158 | -0.34332 | -0.16022 | -0.22431 | 0.027466 | 10.2448 | 0.12817 | 0.35248 | -0.059509 | 122.5433 | 122.5845 | 122.5845 | -29.6036 | 122.9553 | 122.8683 | 46.3348 | -123.1522
613.6875 | 123.2849 | -84.8373 | 38.0814 | -0.11832 | 0.045028 | 0.012285 | 0.023741 | -0.0032532 | 0.0048274 | 0.017844 | -0.23443 | -0.012754 | 0.074815 | 0.065716 | 0.0039788 | -0.015707 | 38.1592 | 38.2965 | 38.1592 | 35.8154 | 38.1134 | 8.6426 | 8.8028 | -74.9588 | -34.1217 | -84.5947 | 38.15 | 38.0402 | -84.9747 | -85.0571 | 93.4799 | 93.6401 | 0.032043 | 123.1338 | 120.6528 | 27.0126 | 0.07782 | -0.13733 | -0.21973 | 0.068664 | 9.8785 | 0.24261 | 0.46234 | -0.041199 | 122.9507 | 122.9965 | 122.9965 | -29.2786 | 122.9874 | 122.8775 | 50.7156 | -123.1384
614.6875 | 123.2574 | -84.9792 | 37.9852 | -0.39298 | 0.06105 | 0.011217 | 0.022672 | -0.0096622 | -0.0090576 | 0.023184 | 4.3432 | -0.010618 | 0.076952 | 0.060376 | 0.010388 | -0.015707 | 38.0356 | 38.1866 | 38.063 | 35.9894 | 38.0173 | 8.6426 | 8.8074 | -74.1302 | -32.4188 | -84.7916 | 38.0264 | 37.9257 | -85.1303 | -85.1624 | 93.6218 | 93.7866 | 0.032044 | 123.1659 | 120.9686 | 27.182 | 0.050354 | -0.15106 | -0.18311 | 0.041199 | 10.849 | 0.18768 | 0.37079 | -0.059509 | 122.9965 | 123.0148 | 123.0423 | -29.1779 | 123.0057 | 122.905 | 52.5604 | -123.1476
615.6875 | 123.1796 | -84.8328 | 38.1821 | -0.39298 | 0.068527 | 0.013353 | 0.023741 | -0.01073 | -0.0069216 | 0.031729 | -0.72271 | -0.0052782 | 0.085497 | 0.049694 | 0.023206 | -0.0050264 | 38.1821 | 38.324 | 38.1821 | 36.0992 | 38.1775 | 8.6334 | 8.7982 | -75.1053 | -31.4163 | -84.6222 | 38.2187 | 38.1409 | -84.9792 | -85.025 | 93.4662 | 93.631 | -0.004578 | 123.1567 | 120.932 | 27.301 | 0 | -0.14648 | -0.19226 | 0.036621 | 9.7275 | 0.21057 | 0.40283 | -0.041199 | 123.0103 | 123.0148 | 123.0148 | -29.3839 | 123.0515 | 122.9736 | 53.4164 | -123.2071
616.6875 | 123.1476 | -84.906 | 38.1088 | -0.43876 | 0.073868 | -0.0037369 | 0.014128 | -0.0096622 | -0.0090576 | 0.023184 | -0.67693 | -0.015959 | 0.071611 | 0.052899 | 0.015729 | -0.014639 | 38.1226 | 38.269 | 38.1271 | 36.0764 | 38.1363 | 8.638 | 8.8028 | -74.3591 | -36.7584 | -84.6725 | 38.1683 | 38.0539 | -85.0342 | -85.0891 | 93.544 | 93.7088 | 0.027466 | 123.175 | 120.9824 | 27.2736 | 0.013733 | -0.12817 | -0.1831 | 0.059509 | 10.5469 | 0.23346 | 0.41657 | -0.054932 | 123.0423 | 123.0286 | 123.0331 | -29.306 | 123.0743 | 122.9599 | 48.1476 | -123.1979
617.6875 | 123.1842 | -84.2377 | 38.7817 | -0.40824 | 0.086685 | 0.012285 | 0.026945 | -0.013935 | -0.0090576 | 0.023184 | -0.75323 | -0.0074142 | 0.082292 | 0.057171 | 0.011456 | -0.0071624 | 38.8092 | 38.8916 | 38.7909 | 36.7355 | 38.7817 | 8.638 | 8.7982 | -74.5331 | -28.7979 | -84.0363 | 38.8458 | 38.7177 | -84.3613 | -84.4208 | 92.8757 | 93.0359 | 0 | 123.1293 | 120.9732 | 27.9373 | 0.027466 | -0.1236 | -0.1831 | 0.064087 | 9.7046 | 0.20142 | 0.38452 | -0.064087 | 123.0194 | 123.0469 | 123.0286 | -29.9835 | 123.0835 | 122.9553 | 55.4398 | -123.2025
618.6875 | 123.1705 | -84.8969 | 38.1088 | -0.3472 | 0.066391 | 0.027238 | 0.023741 | -0.019275 | -0.014399 | 0.030661 | -0.75323 | -0.0031412 | 0.085497 | 0.062512 | 0.016797 | -0.0082304 | 38.0905 | 38.2278 | 38.1042 | 36.0855 | 38.1134 | 8.6426 | 8.8028 | -75.2518 | -34.3735 | -84.7458 | 38.1363 | 38.0264 | -85.0525 | -85.112 | 93.5394 | 93.6996 | 0.004577 | 123.1247 | 120.9824 | 27.2827 | -0.018311 | -0.15564 | -0.21515 | 0.027466 | 9.6451 | 0.15106 | 0.36621 | -0.082398 | 123.0103 | 122.9874 | 123.0011 | -29.306 | 123.0331 | 122.9233 | 50.5234 | -123.2208
619.6875 | 123.175 | -84.7641 | 38.2507 | -0.48453 | 0.07814 | 0.0058761 | 0.0055833 | -0.0064582 | -0.011195 | 0.022116 | -0.75323 | -0.014891 | 0.073747 | 0.065716 | 0.016797 | -0.014639 | 38.2233 | 38.356 | 38.2233 | 36.2961 | 38.237 | 8.638 | 8.8028 | -74.0753 | -31.4804 | -84.5856 | 38.2965 | 38.1683 | -84.9152 | -84.9609 | 93.4021 | 93.5669 | -0.013732 | 123.1201 | 121.0602 | 27.4933 | -0.027465 | -0.15106 | -0.19684 | 0.045777 | 10.6888 | 0.17853 | 0.37537 | -0.082397 | 123.0011 | 122.9874 | 122.9874 | -29.4479 | 123.0606 | 122.9324 | 53.2837 | -123.2117
620.6875 | 123.2941 | -85.6705 | 37.3123 | -0.36246 | 0.058914 | 0.00053514 | 0.031217 | -0.0085942 | -0.011195 | 0.033866 | 1.2152 | -0.0084822 | 0.073747 | 0.055035 | 0.021069 | -0.0082304 | 37.3398 | 37.5092 | 37.3856 | 35.4218 | 37.3352 | 8.6517 | 8.8028 | -75 | -31.7047 | -85.3638 | 37.3627 | 37.2299 | -85.7986 | -85.8673 | 94.3222 | 94.4733 | 0.022888 | 123.1796 | 121.0922 | 26.619 | 0.027466 | -0.12817 | -0.19684 | 0.050354 | 10.6705 | 0.3067 | 0.50354 | -0.082398 | 123.0057 | 123.0103 | 123.056 | -28.5095 | 123.0331 | 122.9004 | 53.9658 | -123.1796
621.6875 | 123.2071 | -86.2427 | 36.8225 | -0.39298 | 0.06105 | 0.018693 | 0.029081 | -0.0032532 | 0.0026914 | 0.028525 | -0.73797 | -0.0031412 | 0.091905 | 0.06358 | 0.021069 | -0.010367 | 36.7767 | 36.9186 | 36.795 | 35.0327 | 36.7722 | 8.638 | 8.8028 | -75.3159 | -25.6622 | -85.9589 | 36.8729 | 36.7447 | -86.348 | -86.412 | 94.8807 | 95.0455 | -0.050354 | 123.1613 | 121.2753 | 26.2299 | -0.045777 | -0.10528 | -0.16937 | 0.050354 | 10.9268 | 0.28381 | 0.45319 | -0.07782 | 123.0148 | 123.0194 | 123.0377 | -28.0197 | 123.1155 | 122.9874 | 60.5804 | -123.2346
622.6875 | 123.1522 | -86.2701 | 36.7813 | -0.087804 | 0.077072 | 0.021898 | 0.024809 | -0.0064582 | 0.0069634 | 0.030661 | -0.78374 | 6.2833e-05 | 0.081224 | 0.060376 | 0.013592 | -0.010367 | 36.6623 | 36.7722 | 36.6623 | 35.0006 | 36.7996 | 8.6426 | 8.7982 | -75.9659 | -32.5974 | -86.0458 | 36.8408 | 36.7172 | -86.412 | -86.4761 | 94.9127 | 95.0684 | 0.018311 | 123.0423 | 121.2708 | 26.2024 | -0.11902 | -0.14191 | -0.20599 | 0.059509 | 10.3043 | 0.22431 | 0.4303 | -0.064087 | 123.0698 | 122.9324 | 122.9324 | -27.9831 | 123.111 | 122.9874 | 53.6728 | -123.2574
623.6875 | 123.1476 | -86.4487 | 36.6074 | 0.080043 | 0.068527 | 0.013353 | 0.025877 | -4.9167e-05 | -0.00051261 | 0.036002 | -0.78374 | -0.0074142 | 0.085497 | 0.055035 | 0.024274 | -0.017843 | 36.4883 | 36.6074 | 36.4838 | 34.758 | 36.5707 | 8.638 | 8.8074 | -75.9201 | -31.6132 | -86.1923 | 36.6669 | 36.5387 | -86.586 | -86.6318 | 95.0867 | 95.256 | -0.036621 | 123.056 | 121.2067 | 25.9506 | -0.11902 | -0.13733 | -0.18311 | 0.059509 | 10.5286 | 0.25635 | 0.43945 | -0.068665 | 123.0194 | 122.937 | 122.9324 | -27.8 | 123.1155 | 122.9874 | 54.8355 | -123.2391
624.6875 | 123.1567 | -87.8082 | 35.2203 | -0.087804 | 0.072799 | 0.0048081 | 0.031217 | 0.0063598 | -0.0037176 | 0.040274 | -0.76848 | 0.0011308 | 0.092973 | 0.06892 | 0.020001 | -0.0039584 | 35.0601 | 35.1746 | 35.0601 | 33.4122 | 35.1746 | 8.6472 | 8.8074 | -76.9775 | -31.0089 | -87.5427 | 35.2753 | 35.1471 | -87.973 | -88.0188 | 96.4554 | 96.6156 | -0.045776 | 122.9828 | 121.2204 | 24.6048 | -0.16022 | -0.16479 | -0.21057 | 0.054932 | 10.8307 | 0.2655 | 0.47607 | -0.073242 | 122.9828 | 122.8683 | 122.8683 | -26.413 | 123.0835 | 122.9553 | 56.7993 | -123.2391
625.6875 | 123.1567 | -88.1241 | 34.9503 | -0.3472 | 0.080276 | 0.00053514 | 0.011991 | -0.0064582 | -0.0047856 | 0.034934 | -0.82952 | -0.0052782 | 0.09511 | 0.060376 | 0.018933 | 0.0056546 | 34.8129 | 34.9182 | 34.7946 | 33.2474 | 34.9045 | 8.6426 | 8.7936 | -78.3554 | -27.7267 | -87.7167 | 34.9869 | 34.8953 | -88.266 | -88.3026 | 96.7667 | 96.9177 | -0.045776 | 123.0423 | 121.3715 | 24.4537 | -0.13733 | -0.14191 | -0.17853 | 0.036621 | 9.7687 | 0.40741 | 0.58594 | -0.054931 | 123.0286 | 122.937 | 122.9187 | -26.1566 | 123.111 | 123.0194 | 60.3973 | -123.2529
626.6875 | 123.23 | -88.3255 | 34.726 | -0.43876 | 0.057846 | 0.016557 | 0.026945 | -4.9167e-05 | -0.012263 | 0.025321 | -0.66167 | -0.014891 | 0.091905 | 0.071057 | 0.010388 | 0.0024506 | 34.6069 | 34.726 | 34.6298 | 33.165 | 34.6481 | 8.6517 | 8.8074 | -79.2709 | -30.7297 | -87.9547 | 34.726 | 34.6161 | -88.4903 | -88.5361 | 96.9772 | 97.1329 | -0.07782 | 123.0515 | 121.4905 | 24.3576 | -0.11902 | -0.16479 | -0.21057 | 0 | 9.0546 | 0.37079 | 0.58136 | -0.10986 | 122.9736 | 122.9324 | 122.9553 | -25.9186 | 123.0515 | 122.9416 | 57.5958 | -123.262
627.6875 | 123.1796 | -88.4399 | 34.6298 | -0.45401 | 0.06105 | 0.021898 | 0.023741 | -0.0032532 | -0.012263 | 0.030661 | -0.67693 | -0.0020732 | 0.109 | 0.087078 | 0.010388 | 0.0013826 | 34.5337 | 34.6527 | 34.5245 | 32.7942 | 34.5566 | 8.6472 | 8.8074 | -79.4403 | -23.172 | -88.0096 | 34.6573 | 34.5566 | -88.5498 | -88.623 | 97.0871 | 97.2473 | -0.073242 | 123.0927 | 121.2341 | 23.9868 | -0.096131 | -0.10986 | -0.18311 | 0.027466 | 8.9996 | 0.4303 | 0.6134 | -0.073242 | 122.9965 | 122.9736 | 122.9645 | -25.8224 | 123.0972 | 122.9965 | 65.2679 | -123.2529
628.6875 | 123.1613 | -88.7787 | 34.3185 | -0.98807 | 0.082412 | 0.010148 | 0.017332 | 0.0010188 | -0.00051261 | 0.021048 | -0.70745 | 0.0011308 | 0.1154 | 0.087078 | 0.012524 | 0.0067226 | 34.1217 | 34.2407 | 34.1217 | 32.4234 | 34.2682 | 8.6472 | 8.812 | -79.0237 | -24.7696 | -88.4216 | 34.346 | 34.2224 | -88.8977 | -88.9664 | 97.4258 | 97.5906 | -0.050354 | 123.0194 | 121.2021 | 23.6114 | -0.19684 | -0.11902 | -0.18768 | 0.027466 | 9.7549 | 0.35706 | 0.54474 | -0.09613 | 123.0469 | 122.9004 | 122.9004 | -25.5066 | 123.1247 | 123.0011 | 64.0091 | -123.2849
629.6875 | 123.1842 | -88.9481 | 34.1217 | 1.8195 | 0.079208 | -0.00053286 | 0.030149 | 0.0042228 | 0.0058954 | 0.028525 | -0.66167 | 0.0064718 | 0.12181 | 0.08601 | 0.014661 | 0.0035186 | 33.9432 | 34.0622 | 33.9294 | 32.2586 | 34.0576 | 8.6472 | 8.8074 | -79.8935 | -28.1982 | -88.5727 | 34.1583 | 34.0576 | -89.0808 | -89.1541 | 97.5952 | 97.7554 | -0.064087 | 123.0103 | 121.2067 | 23.4512 | -0.17853 | -0.13275 | -0.20599 | 0.036621 | 9.0546 | 0.37537 | 0.58136 | -0.064087 | 123.0057 | 122.8912 | 122.8775 | -25.3143 | 123.1064 | 123.0057 | 60.7498 | -123.2758
630.6875 | 123.1705 | -89.3188 | 33.7509 | -0.36246 | 0.097366 | 0.012285 | 0.04083 | -0.0032532 | 0.0091004 | 0.038138 | -0.67693 | -0.0063462 | 0.10472 | 0.08067 | 0.013592 | 0.0024506 | 33.6136 | 33.7051 | 33.5724 | 31.9794 | 33.7418 | 8.6472 | 8.8074 | -79.8294 | -29.6219 | -88.9801 | 33.8287 | 33.728 | -89.4379 | -89.4882 | 97.966 | 98.1262 | -0.009156 | 123.024 | 121.2982 | 23.172 | -0.13733 | -0.11902 | -0.16937 | 0.077819 | 9.4894 | 0.33875 | 0.50812 | -0.022889 | 123.0606 | 122.9324 | 122.8912 | -24.9435 | 123.1476 | 123.0469 | 59.697 | -123.2391
631.6875 | 123.175 | -89.1998 | 33.8562 | -3.7347 | 0.068527 | 0.016557 | 0.0023783 | -0.0043222 | -0.0015816 | 0.015708 | -0.66167 | 0.0064718 | 0.11113 | 0.073193 | 0.017865 | 0.0035186 | 33.7463 | 33.8379 | 33.728 | 32.1579 | 33.8699 | 8.6426 | 8.7936 | -79.4495 | -25.8316 | -88.8977 | 33.8882 | 33.815 | -89.3417 | -89.3967 | 97.8424 | 97.9935 | 0.013733 | 123.0377 | 121.3577 | 23.3643 | -0.10986 | -0.14191 | -0.19684 | 0.032044 | 9.7504 | 0.30212 | 0.49896 | -0.041199 | 123.0698 | 122.9462 | 122.9279 | -25.0626 | 123.0881 | 123.0148 | 63.3682 | -123.2529
632.6875 | 123.2162 | -89.3829 | 33.7006 | -0.37772 | 0.090957 | 0.0090801 | 0.03549 | 0.0074278 | 0.0026914 | 0.028525 | -0.70745 | -0.0052782 | 0.10472 | 0.064648 | 0.012524 | 0.00031457 | 33.609 | 33.7189 | 33.5907 | 32.0618 | 33.7051 | 8.6472 | 8.8028 | -81.308 | -27.2141 | -88.9481 | 33.7097 | 33.6273 | -89.4928 | -89.566 | 98.0301 | 98.1857 | 0.004577 | 123.1018 | 121.4447 | 23.259 | -0.091553 | -0.10986 | -0.1831 | 0.009155 | 8.075 | 0.43488 | 0.61798 | -0.073243 | 123.0881 | 122.9919 | 122.9736 | -24.8978 | 123.0927 | 123.0103 | 62.1689 | -123.2666
633.6875 | 123.1842 | -90.2802 | 32.8033 | -0.22513 | 0.071731 | 0.016557 | 0.017332 | -0.0085942 | -0.026148 | 0.027457 | -0.58538 | 0.0086078 | 0.11327 | 0.069989 | 0.0071838 | 0.0067226 | 32.7209 | 32.7484 | 32.6523 | 31.3202 | 32.8033 | 8.6472 | 8.7982 | -81.9672 | -27.7359 | -89.8773 | 32.8445 | 32.7484 | -90.4221 | -90.4678 | 98.9273 | 99.0784 | 0 | 123.0286 | 121.6003 | 22.522 | -0.082398 | -0.14191 | -0.18768 | 0.041198 | 8.313 | 0.40283 | 0.59051 | -0.054932 | 123.0835 | 123.0011 | 122.9324 | -24.0051 | 123.1247 | 123.0286 | 62.5443 | -123.2712
634.6875 | 123.1796 | -90.8524 | 32.2266 | -0.48453 | 0.069595 | 0.033647 | 0.034422 | -0.017139 | -0.0069216 | 0.029593 | -0.44805 | -0.0010052 | 0.10793 | 0.072125 | 0.016797 | 0.010996 | 32.103 | 32.2769 | 32.1716 | 30.8304 | 32.2449 | 8.6517 | 8.812 | -83.6426 | -27.5986 | -90.3671 | 32.2952 | 32.1945 | -91.0126 | -91.0172 | 99.5041 | 99.6643 | 0.018311 | 123.1293 | 121.6827 | 22.0184 | -0.1236 | -0.16022 | -0.16479 | 0.068665 | 7.2098 | 0.48523 | 0.65002 | -0.032043 | 123.0972 | 122.9553 | 123.024 | -23.4146 | 123.1476 | 123.0469 | 63.2538 | -123.2437
635.6875 | 123.1934 | -90.8798 | 32.2037 | -0.3472 | 0.092026 | 0.017625 | 0.042967 | -0.0085942 | 0.0091004 | 0.036002 | -0.66167 | -0.0020732 | 0.12288 | 0.075329 | 0.025342 | 0.012064 | 32.0984 | 32.1991 | 32.0892 | 30.6381 | 32.2174 | 8.6426 | 8.8074 | -83.0109 | -25.9186 | -90.3397 | 32.2586 | 32.1487 | -90.9943 | -91.0538 | 99.5224 | 99.6872 | 0.013733 | 123.0789 | 121.5179 | 21.8308 | -0.10529 | -0.11444 | -0.17395 | 0.054932 | 7.869 | 0.54016 | 0.71411 | -0.054931 | 123.0972 | 122.9782 | 122.9691 | -23.3963 | 123.1384 | 123.0286 | 64.9612 | -123.2574
636.6875 | 123.2071 | -90.8524 | 32.222 | -0.24039 | 0.07814 | 0.0037401 | 0.026945 | -4.9167e-05 | 0.0080314 | 0.034934 | -0.60064 | 0.0021988 | 0.11968 | 0.082806 | 0.028546 | 0.018473 | 32.1167 | 32.1991 | 32.1075 | 30.6747 | 32.2174 | 8.6426 | 8.7982 | -83.8623 | -24.3851 | -90.4083 | 32.2632 | 32.1625 | -91.0034 | -91.0538 | 99.4949 | 99.6506 | -0.004578 | 123.0515 | 121.5271 | 21.8765 | -0.10529 | -0.15106 | -0.20142 | 0.041199 | 6.9901 | 0.44403 | 0.64545 | -0.059509 | 123.0698 | 122.9691 | 122.9599 | -23.4238 | 123.1155 | 123.0148 | 66.4673 | -123.2758
637.6875 | 123.1842 | -91.1682 | 31.8924 | -0.4235 | 0.058914 | 0.0090801 | 0.03549 | -0.0021852 | -0.0079896 | 0.024253 | -0.58538 | -0.0095502 | 0.12181 | 0.081738 | 0.028546 | 0.0013826 | 31.7688 | 31.8512 | 31.7642 | 30.3909 | 31.9199 | 8.6472 | 8.8074 | -85.5194 | -28.1708 | -90.6647 | 31.9244 | 31.8512 | -91.3101 | -91.3742 | 99.8154 | 99.9756 | 0.027466 | 123.0194 | 121.5591 | 21.5836 | -0.1236 | -0.14191 | -0.20599 | 0.032043 | 5.6488 | 0.50354 | 0.70953 | -0.041199 | 123.0881 | 122.937 | 122.9324 | -23.085 | 123.0927 | 123.0194 | 62.9974 | -123.2666
638.6875 | 123.2117 | -91.3513 | 31.7276 | -0.57608 | 0.094162 | 0.0090801 | 0.036558 | -0.0021852 | -0.0037176 | 0.028525 | -0.58538 | -0.0052782 | 0.11434 | 0.08067 | 0.023206 | 0.0077906 | 31.604 | 31.7139 | 31.6086 | 30.2307 | 31.7368 | 8.6472 | 8.8074 | -85.73 | -29.3472 | -90.802 | 31.7642 | 31.6956 | -91.507 | -91.5573 | 99.9985 | 100.1587 | 0.009155 | 123.0652 | 121.582 | 21.4233 | -0.1236 | -0.15564 | -0.20599 | 0.036621 | 5.6213 | 0.54932 | 0.75531 | -0.032043 | 123.0881 | 122.9553 | 122.9599 | -22.9202 | 123.1155 | 123.0469 | 62.0041 | -123.2849
639.6875 | 123.1796 | -91.2964 | 31.7825 | 0.3547 | 0.089889 | 0.0016041 | 0.032286 | -0.0096622 | 0.0016234 | 0.028525 | -0.5396 | -0.0052782 | 0.11861 | 0.091351 | 0.027478 | 0.0067226 | 31.6635 | 31.7459 | 31.6635 | 30.3177 | 31.7871 | 8.6472 | 8.8074 | -86.3663 | -33.4351 | -90.7791 | 31.8329 | 31.7505 | -91.4154 | -91.4749 | 99.9435 | 100.1038 | 0.004577 | 123.0423 | 121.6141 | 21.5103 | -0.11902 | -0.11902 | -0.17853 | 0.050354 | 4.9301 | 0.51727 | 0.6958 | -0.032044 | 123.0835 | 122.9599 | 122.9599 | -22.9752 | 123.1293 | 123.0469 | 57.8613 | -123.2574
640.6875 | 123.1888 | -91.4978 | 31.6177 | -0.3472 | 0.073868 | 0.0080121 | 0.039762 | -0.0011172 | 0.0037594 | 0.031729 | -0.57012 | 0.0021988 | 0.12502 | 0.075329 | 0.022137 | 0.0035186 | 31.4941 | 31.5765 | 31.4575 | 30.217 | 31.5994 | 8.6426 | 8.812 | -86.618 | -35.4538 | -90.9576 | 31.6498 | 31.5811 | -91.6306 | -91.658 | 100.1404 | 100.3098 | -0.018311 | 123.0743 | 121.7148 | 21.405 | -0.1236 | -0.13275 | -0.16022 | 0.032043 | 4.8798 | 0.54016 | 0.70038 | -0.036621 | 123.0972 | 122.9919 | 122.9553 | -22.8058 | 123.1476 | 123.0789 | 56.044 | -123.2758
641.6875 | 123.1888 | -91.4841 | 31.5948 | -0.43876 | 0.076004 | -0.0016009 | 0.032286 | 0.0020868 | -0.0047856 | 0.03707 | -0.18865 | 0.0011308 | 0.11327 | 0.088147 | 0.021069 | 0.0056546 | 31.398 | 31.7688 | 31.5994 | 30.1483 | 31.6406 | 8.6472 | 8.8074 | -87.1674 | -34.5566 | -90.9119 | 31.6406 | 31.5537 | -91.6168 | -91.658 | 100.1312 | 100.2914 | 0.045776 | 123.2529 | 121.6324 | 21.3409 | -0.19684 | -0.13275 | -0.17395 | 0.045776 | 4.3167 | 0.5722 | 0.74615 | -0.041199 | 123.1247 | 122.8821 | 123.0835 | -22.7875 | 123.1247 | 123.0377 | 56.9275 | -123.2529
642.6875 | 123.2162 | -91.745 | 31.2973 | -0.1641 | 0.10377 | 0.010148 | 0.036558 | -0.0085942 | 0.013372 | 0.036002 | -0.38701 | 0.0054038 | 0.12288 | 0.087078 | 0.037091 | 0.0035186 | 31.2469 | 31.3568 | 31.2424 | 29.9881 | 31.3156 | 8.6517 | 8.812 | -87.3917 | -33.9844 | -91.1499 | 31.3522 | 31.2698 | -91.8549 | -91.9235 | 100.3967 | 100.5569 | 0.018311 | 123.1018 | 121.7331 | 21.1761 | -0.050354 | -0.10986 | -0.17853 | 0.054932 | 4.3533 | 0.59509 | 0.77362 | -0.027466 | 123.0606 | 122.9919 | 122.9874 | -22.4854 | 123.0972 | 123.0148 | 57.7606 | -123.2208
643.6875 | 123.2025 | -91.7679 | 31.3156 | -0.36246 | 0.089889 | 0.0080121 | 0.038694 | -0.0064582 | 0.0016234 | 0.030661 | -0.57012 | -0.0020732 | 0.13356 | 0.074261 | 0.03175 | 0.0056546 | 31.192 | 31.2836 | 31.1874 | 29.9194 | 31.3202 | 8.6472 | 8.8074 | -87.1811 | -35.0098 | -91.1316 | 31.3614 | 31.2424 | -91.9052 | -91.9418 | 100.415 | 100.5753 | 0.004577 | 123.0515 | 121.6873 | 21.1121 | -0.1236 | -0.13733 | -0.17395 | 0.045776 | 4.5868 | 0.63629 | 0.81024 | -0.073242 | 123.0881 | 122.9599 | 122.9553 | -22.5082 | 123.1293 | 123.0103 | 56.7581 | -123.2574
644.6875 | 123.1934 | -92.2302 | 30.8166 | -0.49979 | 0.088821 | -0.0016009 | 0.028013 | -0.0085942 | -0.016535 | 0.033866 | -0.58538 | -0.014891 | 0.12715 | 0.092419 | 0.020001 | 0.0067226 | 30.7159 | 30.7892 | 30.6747 | 29.6951 | 30.8166 | 8.6517 | 8.8165 | -87.822 | -35.6644 | -91.6351 | 30.8762 | 30.7663 | -92.4088 | -92.45 | 100.882 | 101.0468 | 0 | 123.0194 | 121.9254 | 20.8786 | -0.10071 | -0.17853 | -0.21973 | 0.05951 | 4.4083 | 0.59509 | 0.81482 | -0.050354 | 123.0469 | 122.9462 | 122.905 | -22.0001 | 123.1064 | 122.9965 | 56.5659 | -123.2666
645.6875 | 123.1979 | -93.6447 | 29.4388 | -0.30143 | 0.11873 | -0.0037369 | 0.033354 | -0.0075262 | -0.0047856 | 0.030661 | -0.5396 | -0.0052782 | 0.13463 | 0.088147 | 0.014661 | 0.013132 | 29.3335 | 29.3884 | 29.3152 | 29.3838 | 29.4159 | 8.6426 | 8.8028 | -88.8611 | -28.6469 | -93.0496 | 29.4662 | 29.4296 | -93.782 | -93.8232 | 102.2873 | 102.4475 | -0.022888 | 123.0331 | 123.0286 | 20.5811 | -0.10529 | -0.13733 | -0.17853 | 0.027466 | 4.7836 | 0.59509 | 0.77362 | -0.009156 | 123.0606 | 122.9782 | 122.9599 | -20.636 | 123.111 | 123.0743 | 64.9979 | -123.262
646.6875 | 123.1888 | -93.9514 | 29.1412 | -1.1101 | 0.097366 | -0.0026689 | 0.029081 | 0.010632 | 0.012304 | 0.026389 | -0.66167 | 6.2833e-05 | 0.12929 | 0.084942 | 0.02641 | 0.0013826 | 29.0176 | 29.0817 | 28.9719 | 29.0955 | 29.1321 | 8.6426 | 8.812 | -88.4583 | -28.9398 | -93.2419 | 29.2191 | 29.155 | -94.0659 | -94.1162 | 102.594 | 102.7634 | -0.009155 | 123.0331 | 123.0469 | 20.2835 | -0.1236 | -0.11444 | -0.1648 | 0.07782 | 5.4932 | 0.70953 | 0.87433 | 0.013733 | 123.0835 | 122.9691 | 122.9233 | -20.3293 | 123.1705 | 123.1064 | 65.0116 | -123.2574
647.6875 | 123.1888 | -93.7637 | 29.3289 | -0.057287 | 0.07814 | 0.0090801 | 0.026945 | -0.016071 | -0.017603 | 0.036002 | -0.52434 | -0.0010052 | 0.12715 | 0.099896 | 0.020001 | 0.019541 | 29.2007 | 29.3289 | 29.2145 | 29.3106 | 29.3655 | 8.6426 | 8.8074 | -88.9343 | -29.1916 | -93.1549 | 29.3701 | 29.2877 | -93.8828 | -93.924 | 102.4063 | 102.5711 | 0.036622 | 123.0927 | 123.0743 | 20.5032 | -0.12817 | -0.11902 | -0.16022 | 0.041199 | 4.8294 | 0.60883 | 0.76904 | -0.041198 | 123.1293 | 122.9645 | 122.9782 | -20.5215 | 123.1338 | 123.0515 | 64.5721 | -123.2529
648.6875 | 123.23 | -93.7958 | 29.2694 | -0.37772 | 0.10591 | 0.0037401 | 0.03549 | -0.0032532 | 0.0058954 | 0.027457 | -0.55486 | -0.0010052 | 0.13036 | 0.082806 | 0.015729 | 0.0099276 | 29.187 | 29.2557 | 29.1733 | 29.2969 | 29.274 | 8.6472 | 8.8074 | -89.1357 | -24.0967 | -93.2144 | 29.2831 | 29.2374 | -93.9514 | -93.9835 | 102.4429 | 102.6031 | 0.004578 | 123.0515 | 123.0927 | 20.4895 | -0.082397 | -0.15564 | -0.18768 | 0.013733 | 4.66 | 0.58136 | 0.76904 | -0.032043 | 123.0698 | 122.9828 | 122.9691 | -20.462 | 123.0789 | 123.0331 | 69.6991 | -123.2529
649.6875 | 123.2208 | -93.9377 | 29.1412 | -0.36246 | 0.11232 | 0.0058761 | 0.034422 | 0.0010188 | -0.0015816 | 0.033866 | -0.58538 | 0.0021988 | 0.12395 | 0.088147 | 0.030682 | 0.015268 | 29.0039 | 29.1046 | 29.0085 | 29.1092 | 29.0817 | 8.6517 | 8.812 | -89.7217 | -25.3601 | -93.3838 | 29.1779 | 29.0863 | -94.0887 | -94.1299 | 102.5894 | 102.7496 | -0.059509 | 123.0423 | 123.0469 | 20.2972 | -0.13733 | -0.15106 | -0.19226 | 0.036621 | 4.216 | 0.55389 | 0.74616 | -0.054931 | 123.0194 | 122.9416 | 122.9462 | -20.3293 | 123.1155 | 123.024 | 68.5776 | -123.2712
650.6875 | 123.2025 | -94.0842 | 28.9856 | -0.20987 | 0.11125 | -0.0048049 | 0.047239 | -0.0053902 | 0.0026914 | 0.029593 | -0.47857 | 0.010744 | 0.15065 | 0.077465 | 0.017865 | 0.024881 | 28.9169 | 28.9948 | 28.9032 | 28.9993 | 28.9444 | 8.6563 | 8.8028 | -89.9826 | -23.671 | -93.4662 | 28.9902 | 28.9169 | -94.2215 | -94.2719 | 102.7405 | 102.887 | -0.041199 | 123.0789 | 123.0835 | 20.1965 | -0.068665 | -0.13733 | -0.18768 | 0.004577 | 4.1016 | 0.61798 | 0.80566 | -0.068665 | 123.0286 | 123.0011 | 122.9874 | -20.1828 | 123.0743 | 123.0011 | 70.4132 | -123.2574
651.6875 | 123.2254 | -94.3314 | 28.7292 | -0.33194 | 0.09523 | 0.013353 | 0.019468 | -0.018207 | 0.0016234 | 0.027457 | -0.58538 | 0.0011308 | 0.14638 | 0.076397 | 0.029614 | 0.025949 | 28.6377 | 28.7018 | 28.5965 | 28.743 | 28.7384 | 8.6472 | 8.8074 | -90.2618 | -16.1316 | -93.7271 | 28.7521 | 28.7109 | -94.4733 | -94.5328 | 102.9785 | 103.1387 | 0.009155 | 123.0331 | 123.0743 | 19.9356 | -0.091553 | -0.14191 | -0.20142 | 0.022888 | 4.0695 | 0.60425 | 0.80566 | -0.018311 | 123.0698 | 122.9691 | 122.9279 | -19.9219 | 123.0835 | 123.0423 | 78.1998 | -123.262
652.6875 | 123.2254 | -94.3634 | 28.6789 | -0.28617 | 0.068527 | 0.0069441 | 0.026945 | -0.0064582 | -0.00051261 | 0.027457 | -0.52434 | 0.0096758 | 0.12715 | 0.083874 | 0.027478 | 0.030222 | 28.569 | 28.656 | 28.5645 | 28.7018 | 28.6835 | 8.6517 | 8.8028 | -90.2206 | -12.5336 | -93.6127 | 28.7292 | 28.6789 | -94.5007 | -94.5648 | 103.0151 | 103.1662 | 0.004578 | 123.0194 | 123.0652 | 19.899 | -0.10986 | -0.13733 | -0.20142 | 0.050354 | 4.1428 | 0.75073 | 0.95215 | 0 | 123.0469 | 122.9324 | 122.9279 | -19.8761 | 123.0927 | 123.0423 | 81.8298 | -123.2437
653.6875 | 123.1979 | -94.368 | 28.7109 | -0.40824 | 0.082412 | -0.00053286 | 0.030149 | -0.015003 | -0.0026496 | 0.021048 | -0.50908 | 0.0021988 | 0.14424 | 0.079602 | 0.027478 | 0.027017 | 28.5919 | 28.656 | 28.5782 | 28.7018 | 28.7018 | 8.6517 | 8.8074 | -90.6326 | -7.7087 | -93.6722 | 28.7567 | 28.6789 | -94.519 | -94.5374 | 103.0197 | 103.1754 | -0.009155 | 123.024 | 123.0698 | 19.8944 | -0.11902 | -0.15106 | -0.16937 | 0.045777 | 3.7354 | 0.6958 | 0.86517 | -0.032043 | 123.0698 | 122.9599 | 122.9462 | -19.9036 | 123.1247 | 123.0469 | 86.6592 | -123.2483
654.6875 | 123.1842 | -94.4046 | 28.6697 | -0.48453 | 0.087753 | 0.0090801 | 0.030149 | -0.0021852 | -0.015467 | 0.016776 | -0.67693 | 0.020357 | 0.16561 | 0.095623 | 0.023206 | 0.034494 | 28.5278 | 28.5828 | 28.4912 | 28.6057 | 28.6331 | 8.6517 | 8.8074 | -90.9714 | -8.8669 | -93.7042 | 28.7155 | 28.6331 | -94.5419 | -94.6014 | 103.0563 | 103.212 | -0.036621 | 122.9874 | 123.0103 | 19.7983 | -0.14191 | -0.13733 | -0.19684 | 0.045776 | 3.4332 | 0.70038 | 0.89722 | -0.036621 | 123.0377 | 122.9324 | 122.8958 | -19.8624 | 123.1201 | 123.0377 | 85.5377 | -123.2712
655.6875 | 123.1659 | -94.8166 | 28.2486 | -0.45401 | 0.094162 | 0.02083 | 0.034422 | 0.0031548 | -0.0090576 | 0.01998 | -3.2862 | 0.0021988 | 0.15706 | 0.10203 | 0.025342 | 0.032358 | 28.125 | 28.1845 | 28.0792 | 28.2211 | 28.244 | 8.6517 | 8.8074 | -91.5115 | -6.546 | -94.1345 | 28.3264 | 28.244 | -94.9768 | -95.0043 | 103.4683 | 103.624 | -0.004577 | 123.0011 | 123.0377 | 19.4138 | -0.1236 | -0.16022 | -0.18768 | 0.07782 | 3.3051 | 0.68207 | 0.86975 | -0.004577 | 123.0606 | 122.9416 | 122.8958 | -19.4412 | 123.143 | 123.0606 | 88.2706 | -123.2529
656.6875 | 123.2071 | -94.8212 | 28.2257 | -0.57608 | 0.11552 | -0.00053286 | 0.028013 | -4.9167e-05 | 0.015508 | 0.024253 | -0.41753 | 6.2833e-05 | 0.16347 | 0.089215 | 0.034955 | 0.024881 | 28.1891 | 28.2532 | 28.1479 | 28.2394 | 28.2394 | 8.6517 | 8.8074 | -92.0929 | -5.3009 | -94.0842 | 28.2623 | 28.2028 | -94.9677 | -95.0043 | 103.4729 | 103.6285 | 0.013733 | 123.0743 | 123.0606 | 19.4321 | -0.036621 | -0.14648 | -0.1831 | 0.036621 | 2.7283 | 0.737 | 0.92011 | -0.022888 | 123.0606 | 123.0103 | 122.9691 | -19.4183 | 123.0835 | 123.024 | 89.5203 | -123.23
657.6875 | 123.2162 | -95.1141 | 27.9419 | -0.072545 | 0.087753 | 0.0026721 | 0.028013 | 0.0031548 | -0.0058536 | 0.025321 | -0.41753 | 0.0043348 | 0.16774 | 0.08067 | 0.029614 | 0.034494 | 27.8732 | 27.9602 | 27.8549 | 27.9602 | 27.9327 | 8.6517 | 8.8074 | -92.5964 | -3.1586 | -94.4092 | 27.9556 | 27.9007 | -95.2423 | -95.3156 | 103.7659 | 103.9215 | -0.009156 | 123.0743 | 123.0743 | 19.1528 | -0.068665 | -0.12817 | -0.20142 | 0.013732 | 2.5177 | 0.70496 | 0.90637 | -0.041199 | 123.0469 | 122.9874 | 122.9691 | -19.1345 | 123.0698 | 123.0148 | 91.9556 | -123.2574
658.6875 | 123.2025 | -95.105 | 27.9602 | -0.072545 | 0.11232 | 0.0026721 | 0.025877 | -0.0053902 | 0.00055539 | 0.033866 | 1.9781 | 0.0064718 | 0.15279 | 0.096691 | 0.025342 | 0.035562 | 27.9053 | 27.951 | 27.8641 | 27.9602 | 27.951 | 8.6472 | 8.812 | -92.3492 | -1.1993 | -94.3314 | 27.9922 | 27.9602 | -95.2377 | -95.2881 | 103.7521 | 103.9169 | -0.009155 | 123.056 | 123.0652 | 19.1483 | -0.054932 | -0.13275 | -0.18311 | 0.032044 | 2.7557 | 0.77362 | 0.95673 | 0 | 123.056 | 123.0103 | 122.9691 | -19.1483 | 123.0972 | 123.0652 | 93.9056 | -123.2483
659.6875 | 123.2117 | -95.2515 | 27.8046 | -0.30143 | 0.087753 | 0.010148 | 0.025877 | -0.0085942 | 0.0037594 | 0.033866 | -0.3565 | 0.0096758 | 0.15813 | 0.081738 | 0.029614 | 0.023813 | 27.681 | 27.7863 | 27.681 | 27.7954 | 27.7542 | 8.6517 | 8.8165 | -92.5644 | 0.38452 | -94.3497 | 27.8503 | 27.7817 | -95.3796 | -95.4529 | 103.9032 | 104.068 | -0.050354 | 123.0377 | 123.0469 | 18.9789 | -0.1236 | -0.12817 | -0.20142 | 0.045777 | 2.6871 | 0.90179 | 1.1032 | -0.022888 | 123.0057 | 122.9324 | 122.9324 | -18.988 | 123.1018 | 123.0331 | 95.636 | -123.2574
660.6875 | 123.2254 | -95.4163 | 27.6627 | -0.22513 | 0.097366 | 0.0037401 | 0.011991 | 0.0042228 | 0.010168 | 0.027457 | -0.3565 | -0.0052782 | 0.15065 | 0.077465 | 0.040295 | 0.034494 | 27.594 | 27.6398 | 27.5574 | 27.6535 | 27.626 | 8.6563 | 8.8165 | -92.9031 | 1.6525 | -94.519 | 27.6993 | 27.6398 | -95.5399 | -95.6085 | 104.0726 | 104.2328 | -0.036621 | 123.056 | 123.0698 | 18.837 | -0.068665 | -0.1236 | -0.19226 | 0.036621 | 2.5131 | 0.89722 | 1.0895 | -0.022888 | 123.0423 | 123.0103 | 122.9736 | -18.8461 | 123.1155 | 123.056 | 97.0688 | -123.2712
661.6875 | 123.23 | -95.8878 | 27.2095 | -0.89652 | 0.11339 | -0.00053286 | 0.023741 | -0.01073 | -0.00051261 | 0.021048 | -0.6159 | 0.0054038 | 0.16027 | 0.095623 | 0.037091 | 0.025949 | 27.0355 | 27.1408 | 27.0721 | 27.1866 | 27.1912 | 8.6472 | 8.812 | -92.4774 | 2.5772 | -94.6198 | 27.2415 | 27.1866 | -96.0068 | -96.0297 | 104.5349 | 104.6997 | -0.018311 | 123.0286 | 123.0743 | 18.3746 | -0.17395 | -0.11902 | -0.14191 | 0.032043 | 3.4103 | 1.268 | 1.4099 | -0.022889 | 123.0789 | 122.9233 | 122.9599 | -18.3975 | 123.1293 | 123.0743 | 98.465 | -123.2391
662.7031 | 123.2712 | -95.9244 | 27.1042 | 0.52255 | 0.11232 | 0.0037401 | 0.024809 | -0.0043222 | -0.012263 | 0.033866 | 0.26911 | 0.0075398 | 0.18056 | 0.091351 | 0.039227 | 0.035562 | 27.0172 | 27.0721 | 27.0081 | 27.0859 | 27.0996 | 8.6517 | 8.8074 | -92.6651 | 0.36621 | -94.8212 | 27.0996 | 27.0538 | -96.08 | -96.1212 | 104.5761 | 104.7318 | -0.004578 | 122.9965 | 123.0103 | 18.2785 | -0.086975 | -0.15564 | -0.19684 | -0.004578 | 3.2593 | 1.1032 | 1.3 | -0.050354 | 123.024 | 122.9416 | 122.9324 | -18.2968 | 123.024 | 122.9782 | 96.2906 | -123.2254
663.6875 | 123.175 | -95.7825 | 27.301 | -0.17936 | 0.13902 | 0.0048081 | 0.039762 | -0.0085942 | 0.015508 | 0.030661 | -0.24969 | 0.015017 | 0.16988 | 0.096691 | 0.042432 | 0.022745 | 27.2003 | 27.2186 | 27.1317 | 27.2232 | 27.2049 | 8.6472 | 8.8074 | -92.5781 | -13.916 | -94.7845 | 27.2552 | 27.2186 | -95.9335 | -95.9839 | 104.4296 | 104.5898 | -0.09613 | 123.0011 | 123.0057 | 18.4158 | -0.10071 | -0.15106 | -0.20142 | -0.045776 | 3.2043 | 0.99792 | 1.1993 | -0.082397 | 122.9874 | 122.9828 | 122.9141 | -18.4937 | 123.0377 | 123.0011 | 81.8665 | -123.2849
664.6875 | 123.2208 | -95.9976 | 27.0905 | -0.1641 | 0.10271 | 0.0026721 | 0.033354 | -0.0096622 | 0.0016234 | 0.028525 | -0.2802 | 0.011812 | 0.1624 | 0.08601 | 0.027478 | 0.024881 | 26.9669 | 27.0126 | 26.944 | 27.0172 | 26.9989 | 8.6517 | 8.812 | -92.5735 | -14.7949 | -94.8624 | 27.0584 | 27.0126 | -96.1578 | -96.2219 | 104.6494 | 104.8096 | -0.091553 | 123.0103 | 123.0148 | 18.2053 | -0.1236 | -0.16022 | -0.2243 | -0.032043 | 3.4241 | 1.1353 | 1.3596 | -0.07782 | 122.9965 | 122.9645 | 122.9416 | -18.2785 | 123.056 | 123.0103 | 81.2027 | -123.3124
665.6875 | 123.1842 | -95.842 | 27.1957 | -0.072545 | 0.088821 | 0.010148 | 0.036558 | 0.0052918 | 0.0091004 | 0.031729 | -0.34124 | 0.0064718 | 0.16881 | 0.10203 | 0.042432 | 0.024881 | 27.095 | 27.15 | 27.0538 | 27.1454 | 27.1454 | 8.6563 | 8.812 | -92.0105 | -16.0675 | -94.7159 | 27.2003 | 27.1088 | -96.0617 | -96.0892 | 104.4983 | 104.6539 | -0.050354 | 122.9919 | 122.9874 | 18.3334 | -0.10071 | -0.21973 | -0.24719 | 0.004577 | 3.8315 | 1.1261 | 1.3733 | -0.086975 | 122.9874 | 122.937 | 122.8958 | -18.3838 | 123.0423 | 122.9507 | 79.7745 | -123.2849
666.6875 | 123.1659 | -96.1212 | 26.9531 | -0.20987 | 0.11339 | 0.0026721 | 0.031217 | -0.013935 | 0.0048274 | 0.030661 | -0.31072 | 0.0054038 | 0.17095 | 0.10203 | 0.042432 | 0.028086 | 26.7975 | 26.8524 | 26.7609 | 26.857 | 26.825 | 8.6517 | 8.812 | -92.2623 | -17.9901 | -94.9768 | 26.8799 | 26.8341 | -96.3135 | -96.3684 | 104.7729 | 104.9332 | -0.12817 | 122.9736 | 122.9782 | 18.045 | -0.15564 | -0.19226 | -0.24719 | -0.073242 | 3.8589 | 1.1444 | 1.3916 | -0.11902 | 122.9462 | 122.9187 | 122.8821 | -18.1412 | 123.0011 | 122.9553 | 78.1311 | -123.3215
667.7031 | 123.3124 | -96.1945 | 26.8021 | 0.27841 | 0.10057 | 0.010148 | 0.013059 | -0.0021852 | -0.0015816 | 0.024253 | 0.36067 | 0.011812 | 0.13997 | 0.08601 | 0.041363 | 0.038767 | 26.7334 | 26.9165 | 26.8204 | 26.8524 | 26.7563 | 8.6517 | 8.8028 | -91.9601 | -19.8944 | -94.9585 | 26.8341 | 26.7883 | -96.3364 | -96.3638 | 104.8462 | 104.9973 | -0.045776 | 123.111 | 123.0469 | 18.0496 | -0.068665 | -0.14191 | -0.16937 | 0.032043 | 4.2343 | 1.236 | 1.4053 | -0.013733 | 122.9507 | 122.9279 | 123.0148 | -17.9993 | 123.0286 | 122.9828 | 76.3 | -123.1659
668.6875 | 123.2071 | -96.5149 | 26.532 | -0.39298 | 0.10698 | 0.013353 | 0.038694 | -0.01073 | 0.0058954 | 0.031729 | -0.47857 | 0.010744 | 0.15813 | 0.08067 | 0.050977 | 0.012064 | 26.4679 | 26.4816 | 26.4267 | 26.5137 | 26.5411 | 8.6563 | 8.8028 | -91.8915 | -18.2053 | -95.2606 | 26.5869 | 26.5366 | -96.6568 | -96.698 | 105.1712 | 105.3177 | 0.009156 | 122.9965 | 123.0286 | 17.7109 | -0.064086 | -0.14191 | -0.1831 | 0.054932 | 4.6234 | 1.2543 | 1.4374 | 0.004578 | 123.056 | 122.9828 | 122.9416 | -17.7292 | 123.1018 | 123.0515 | 78.3096 | -123.23
669.6875 | 123.1888 | -97.3206 | 25.7538 | -0.1641 | 0.10911 | 0.0037401 | 0.020536 | 0.0095638 | -0.00051261 | 0.029593 | -0.15813 | 0.013948 | 0.19231 | 0.094555 | 0.047772 | 0.034494 | 25.6805 | 25.7126 | 25.6256 | 25.7034 | 25.7172 | 8.6517 | 8.8074 | -92.1707 | -17.9123 | -96.0068 | 25.7767 | 25.7263 | -97.467 | -97.4991 | 105.9723 | 106.1279 | -0.036621 | 123.0331 | 123.024 | 16.8961 | -0.073242 | -0.14648 | -0.17853 | 0.022888 | 5.1498 | 1.3138 | 1.4923 | -0.027466 | 123.0377 | 123.0011 | 122.9462 | -16.9464 | 123.0972 | 123.0469 | 79.4083 | -123.2529
670.6875 | 123.1247 | -97.4991 | 25.589 | 0.18685 | 0.086685 | -0.0058729 | 0.015196 | -0.016071 | 0.018713 | 0.030661 | -0.05132 | 0.016085 | 0.19444 | 0.092419 | 0.052045 | 0.027017 | 25.4608 | 25.4654 | 25.415 | 25.5203 | 25.5661 | 8.6472 | 8.8074 | -92.1799 | -20.2835 | -96.199 | 25.6393 | 25.5844 | -97.6501 | -97.6501 | 106.1462 | 106.3065 | -0.022888 | 122.9645 | 123.0194 | 16.713 | -0.12817 | -0.15106 | -0.15106 | 0.050354 | 5.3192 | 1.3 | 1.4511 | -0.004577 | 123.0652 | 122.9599 | 122.9141 | -16.7816 | 123.1384 | 123.0835 | 77.2156 | -123.2391
671.6875 | 123.1613 | -97.76 | 25.3235 | -0.042028 | 0.09523 | 0.0016041 | 0.032286 | 0.0042228 | 0.0091004 | 0.040274 | -0.18865 | 0.023562 | 0.16988 | 0.1063 | 0.042432 | 0.034494 | 25.264 | 25.2731 | 25.1907 | 25.2823 | 25.2823 | 8.6472 | 8.8074 | -92.9123 | -21.7667 | -96.5607 | 25.3326 | 25.3143 | -97.9065 | -97.9385 | 106.4072 | 106.5674 | -0.041198 | 123.0331 | 123.0423 | 16.4749 | -0.059509 | -0.14648 | -0.17853 | 0.009156 | 4.8477 | 1.1993 | 1.3779 | -0.009155 | 123.0423 | 123.024 | 122.9507 | -16.5161 | 123.0927 | 123.0743 | 75.9933 | -123.262
672.7031 | 123.2941 | -97.934 | 25.0946 | 0.30892 | 0.077072 | 0.011217 | 0.016264 | -0.015003 | -0.037898 | 0.025321 | 0.31489 | 0.0064718 | 0.17201 | 0.094555 | 0.029614 | 0.045175 | 25.0168 | 25.1083 | 25.0397 | 25.0671 | 25.0031 | 8.6563 | 8.8165 | -92.894 | -22.2885 | -96.6614 | 25.0854 | 25.0397 | -98.0804 | -98.1262 | 106.5903 | 106.7505 | -0.091552 | 123.0423 | 123.0011 | 16.2506 | -0.077819 | -0.14648 | -0.19226 | -0.009155 | 5.04 | 1.2726 | 1.4648 | -0.054931 | 122.937 | 122.9507 | 122.9736 | -16.2781 | 123.0194 | 122.9736 | 75.6454 | -123.2208
673.6875 | 123.1522 | -98.4192 | 24.6506 | 0.0037495 | 0.12514 | 0.0048081 | 0.029081 | -0.0021852 | 0.017644 | 0.023184 | -0.24969 | 0.013948 | 0.17629 | 0.09776 | 0.050977 | 0.03129 | 24.5865 | 24.5911 | 24.5178 | 24.5956 | 24.6231 | 8.6426 | 8.8074 | -92.8574 | -22.6044 | -96.9955 | 24.6597 | 24.6414 | -98.5519 | -98.6069 | 107.0618 | 107.2266 | -0.027466 | 123.0103 | 123.0148 | 15.7883 | -0.064087 | -0.13275 | -0.18768 | 0.009155 | 5.5618 | 1.4236 | 1.6113 | -0.009156 | 123.0423 | 123.0057 | 122.937 | -15.8432 | 123.0789 | 123.0606 | 75.8148 | -123.2574
674.6875 | 123.1796 | -98.6893 | 24.4034 | -0.11832 | 0.10805 | 0.014421 | 0.036558 | -0.0021852 | 0.010168 | 0.029593 | -0.31072 | 0.013948 | 0.19444 | 0.11164 | 0.059521 | 0.028086 | 24.3118 | 24.3301 | 24.2477 | 24.3256 | 24.321 | 8.6517 | 8.8028 | -92.7887 | -22.0917 | -97.1558 | 24.3622 | 24.3347 | -98.7946 | -98.8358 | 107.341 | 107.4921 | -0.082397 | 123.0194 | 123.0148 | 15.5228 | -0.091552 | -0.10529 | -0.14648 | -0.041198 | 5.9006 | 1.5335 | 1.68 | -0.068664 | 123.0103 | 123.0011 | 122.937 | -15.6006 | 123.0515 | 123.024 | 76.5976 | -123.2391
675.6875 | 123.2208 | -98.5794 | 24.5132 | -0.17936 | 0.096298 | 0.015489 | 0.016264 | -0.0021852 | 0.011236 | 0.039206 | -0.29546 | 0.034243 | 0.19231 | 0.10844 | 0.050977 | 0.063333 | 24.3896 | 24.4171 | 24.3393 | 24.3896 | 24.4125 | 8.6517 | 8.8074 | -92.6102 | -20.8008 | -97.0505 | 24.4537 | 24.408 | -98.6893 | -98.7396 | 107.2311 | 107.3868 | -0.10071 | 122.9965 | 122.9691 | 15.5823 | -0.1236 | -0.10986 | -0.16022 | -0.05951 | 5.9692 | 1.5289 | 1.6891 | -0.10529 | 122.9919 | 122.9691 | 122.9187 | -15.7059 | 123.0331 | 122.9874 | 77.7786 | -123.2529
676.6875 | 123.0515 | -112.1109 | 10.9222 | 0.095301 | 0.10271 | -0.00053286 | 0.013059 | 0.0042228 | 0.011236 | 0.036002 | 0.024973 | 0.022493 | -0.0052926 | 0.0048338 | -0.0088382 | 0.046244 | 10.7941 | 10.762 | 10.7025 | 10.7941 | 10.968 | 8.5648 | 8.6197 | 9.9472 | 10.2127 | 9.9335 | 10.9772 | 10.9314 | 8.432 | 8.3496 | 120.6757 | 120.7306 | 0.045777 | 122.8729 | 122.905 | 2.1744 | -0.12817 | 120.5429 | 120.4605 | 0.054932 | 122.0581 | 122.0444 | 1.5839 | 0.009155 | 123.0789 | 122.905 | 122.8134 | -2.3026 | 123.0881 | 123.0423 | 122.3236 | -2.5726
677.7031 | 123.2025 | -112.1933 | 10.817 | 0.11056 | 0.05571 | 0.015489 | 0.013059 | -0.015003 | -0.030421 | 0.027457 | 0.17756 | 0.0096758 | -0.0031566 | 0.0080378 | -0.014179 | 0.063333 | 10.7117 | 10.762 | 10.7025 | 10.7483 | 10.8398 | 8.551 | 8.6151 | 10.2905 | 10.4553 | 10.3592 | 10.8353 | 10.8124 | 8.5144 | 8.4183 | 120.7443 | 120.8084 | 0.022888 | 122.9553 | 122.9416 | 2.1332 | -0.10529 | 120.7077 | 120.6116 | 0.01831 | 122.4838 | 122.5525 | 1.9409 | -0.004578 | 123.0331 | 122.905 | 122.8958 | -2.2018 | 123.0286 | 123.0057 | 122.6486 | -2.3987
678.6875 | 123.1705 | -110.4858 | 12.616 | 0.30892 | 0.10484 | 0.0048081 | 0.025877 | 0.0010188 | 0.00055539 | 0.030661 | 0.055491 | 0.020357 | 0.0053884 | 0.0091058 | 0.016797 | 0.039835 | 12.4741 | 12.442 | 12.3962 | 12.4878 | 12.6251 | 8.6472 | 8.7891 | -0.14191 | 0.1831 | -0.14191 | 0.10071 | 0.073242 | -0.17395 | -0.22888 | 119.133 | 119.2749 | 0.009155 | 122.9279 | 122.9736 | 3.6987 | -0.14191 | 110.3119 | 110.257 | -12.5153 | 110.3439 | 110.3439 | 0.086975 | -12.5427 | 123.111 | 122.9599 | 122.8821 | -3.8269 | 110.5865 | 110.5591 | 110.6689 | -12.8448
679.6875 | 123.1338 | -110.6781 | 12.4329 | 0.1716 | 0.10377 | 0.0026721 | 0.034422 | -0.0096622 | 0.0026914 | 0.034934 | 0.040232 | 0.026766 | 0.016069 | -0.01012 | 0.0039788 | 0.039835 | 12.3184 | 12.2772 | 12.236 | 12.3322 | 12.4512 | 8.638 | 8.7708 | -0.10986 | -0.10986 | -0.16479 | 0.1236 | 0.086975 | -0.1831 | -0.24719 | 119.3161 | 119.4489 | 0.018311 | 122.9553 | 123.0103 | 3.5614 | -0.11444 | 110.495 | 110.4309 | -12.3093 | 110.5682 | 110.5133 | 0.082397 | -12.3459 | 123.1293 | 122.9965 | 122.9141 | -3.6621 | 110.8017 | 110.7651 | 110.5682 | -12.6801
680.6875 | 123.143 | -110.7651 | 12.3688 | 0.064784 | 0.10057 | -0.00053286 | 0.029081 | 0.0074278 | 0.011236 | 0.027457 | -0.020803 | 0.02997 | -0.0095656 | 0.0037648 | 0.016797 | 0.040903 | 12.2223 | 12.1948 | 12.1582 | 12.2681 | 12.3871 | 8.638 | 8.7708 | -0.10986 | -0.11444 | -0.17853 | 0.12817 | 0.09613 | -0.1831 | -0.25177 | 119.4031 | 119.5358 | 0.018311 | 122.9599 | 123.0331 | 3.4973 | -0.14648 | 110.582 | 110.5133 | -12.2406 | 110.6552 | 110.5865 | 0.073242 | -12.2726 | 123.1522 | 122.9874 | 122.9233 | -3.598 | 110.8932 | 110.8612 | 110.6506 | -12.6205
681.6875 | 123.175 | -111.0168 | 12.0575 | 0.034266 | 0.10484 | -0.00053286 | 0.029081 | -0.0064582 | 0.0091004 | 0.024253 | -0.14287 | 0.02997 | 0.0032524 | 0.017651 | 0.0039788 | 0.040903 | 12.0117 | 11.9888 | 11.9156 | 12.0026 | 12.1078 | 8.6288 | 8.7433 | -0.036621 | -0.045776 | -0.10071 | 0.10986 | 0.082397 | -0.16937 | -0.23346 | 119.6457 | 119.7601 | 0.050354 | 123.0057 | 123.0194 | 3.2593 | -0.045776 | 110.8475 | 110.7834 | -11.9476 | 110.9802 | 110.9161 | 0.13275 | -11.9751 | 123.1247 | 123.0286 | 122.9324 | -3.3142 | 111.1267 | 111.0992 | 110.9711 | -12.291
682.6875 | 123.3032 | -111.0626 | 11.9659 | 0.41574 | 0.10484 | 0.0069441 | 0.017332 | -4.9167e-05 | -0.0079896 | 0.032797 | 0.39118 | 0.020357 | -0.0095656 | 0.0080378 | -0.0056342 | 0.045175 | 11.9614 | 11.9568 | 11.9247 | 11.9614 | 11.9843 | 8.6334 | 8.7433 | 0.041199 | 0.054932 | 0.004578 | 0.10071 | 0.018311 | -0.13733 | -0.19684 | 119.696 | 119.8059 | 0.018311 | 123.0194 | 123.024 | 3.2181 | -0.004577 | 110.9253 | 110.8658 | -11.8652 | 111.1038 | 111.0672 | 0.20142 | -11.9476 | 123.0469 | 123.024 | 122.9874 | -3.2227 | 111.1633 | 111.0809 | 111.1176 | -12.1628
683.6875 | 123.1064 | -111.2274 | 11.8698 | 0.26315 | 0.10484 | -0.00053286 | 0.022672 | -0.0043222 | 0.010168 | 0.021048 | 0.07075 | 0.02463 | -0.0010206 | 0.018719 | -0.0024292 | 0.044107 | 11.7554 | 11.7188 | 11.6776 | 11.7691 | 11.879 | 8.6334 | 8.7387 | -0.059509 | -0.086975 | -0.12817 | 0.14191 | 0.07782 | -0.17395 | -0.23346 | 119.8608 | 119.9661 | 0.009155 | 122.9462 | 122.9965 | 3.0304 | -0.11444 | 111.0535 | 110.994 | -11.7279 | 111.1679 | 111.0992 | 0.10528 | -11.792 | 123.1064 | 122.9828 | 122.905 | -3.1311 | 111.3693 | 111.3052 | 111.1404 | -12.1033
684.6875 | 123.23 | -111.4792 | 11.673 | 0.27841 | 0.093094 | 0.0080121 | 0.023741 | -4.9167e-05 | 0.0048274 | 0.022116 | 0.1623 | 0.028902 | -0.01277 | 0.017651 | 0.0039788 | 0.044107 | 11.5219 | 11.4853 | 11.4487 | 11.5402 | 11.673 | 8.6105 | 8.7204 | -0.059509 | -0.086975 | -0.1236 | 0.12817 | 0.091553 | -0.15106 | -0.2243 | 120.0897 | 120.1996 | 0 | 122.9645 | 123.0194 | 2.8198 | -0.15106 | 111.3281 | 111.2549 | -11.5448 | 111.4197 | 111.3556 | 0.10071 | -11.5814 | 123.1522 | 123.0011 | 122.9279 | -2.9526 | 111.6074 | 111.5707 | 111.3922 | -11.8973
685.6875 | 123.1842 | -111.5662 | 11.5677 | 0.32418 | 0.081344 | -0.0058729 | 0.0184 | -0.013935 | 0.0026914 | 0.038138 | 0.20808 | 0.018221 | -0.0042246 | 0.016583 | -0.0045652 | 0.043039 | 11.4395 | 11.3709 | 11.3617 | 11.4487 | 11.5952 | 8.6105 | 8.7112 | -0.054932 | -0.10071 | -0.11902 | 0.14648 | 0.10071 | -0.15106 | -0.21973 | 120.1767 | 120.2774 | 0.027466 | 122.937 | 123.0148 | 2.7374 | -0.12817 | 111.4151 | 111.3464 | -11.4212 | 111.5112 | 111.4471 | 0.10071 | -11.467 | 123.1613 | 123.0057 | 122.9279 | -2.8564 | 111.7126 | 111.6669 | 111.4655 | -11.7874
686.6875 | 123.2529 | -112.0605 | 11.0184 | -0.56083 | 0.096298 | 0.016557 | 0.028013 | -0.01073 | -0.0037176 | 0.034934 | 0.17756 | 0.035311 | 0.0011164 | 0.010174 | 0.010388 | 0.041971 | 10.936 | 10.8902 | 10.849 | 10.9177 | 11.0779 | 8.5693 | 8.638 | -0.018311 | -0.050354 | -0.082397 | 0.13275 | 0.068665 | -0.13733 | -0.21973 | 120.6299 | 120.6985 | 0.059509 | 122.9507 | 122.9782 | 2.2797 | -0.082398 | 111.9232 | 111.8408 | -10.8856 | 112.0422 | 111.9781 | 0.13733 | -10.9497 | 123.1384 | 122.9965 | 122.9095 | -2.3804 | 112.1933 | 112.1292 | 112.0102 | -11.2381
687.6875 | 123.1888 | -112.2803 | 10.8398 | 0.21737 | 0.093094 | 0.0058761 | 0.031217 | -0.0064582 | 0.0080314 | 0.017844 | 0.1623 | 0.022493 | 0.0021844 | 0.015515 | 0.0007748 | 0.059061 | 10.7025 | 10.643 | 10.6155 | 10.7117 | 10.8719 | 8.551 | 8.6105 | -0.045776 | -0.082397 | -0.11444 | 0.15564 | 0.10071 | -0.16022 | -0.21973 | 120.8313 | 120.8908 | 0.032043 | 122.9233 | 122.9919 | 2.1011 | -0.13733 | 112.1201 | 112.0605 | -10.6842 | 112.2345 | 112.1658 | 0.10529 | -10.7391 | 123.1522 | 122.9828 | 122.8958 | -2.2293 | 112.4359 | 112.381 | 112.1979 | -11.0596
688.6875 | 123.175 | -112.3398 | 10.7941 | 0.064784 | 0.092026 | 0.011217 | 0.022672 | -0.0064582 | 0.0048274 | 0.021048 | -0.11236 | 0.028902 | -0.013838 | 0.0059018 | 0.0039788 | 0.045175 | 10.643 | 10.6476 | 10.5881 | 10.6659 | 10.8078 | 8.551 | 8.606 | -0.045776 | -0.041199 | -0.09613 | 0.15106 | 0.09613 | -0.16022 | -0.20599 | 120.8908 | 120.9457 | 0.013733 | 122.9874 | 123.0057 | 2.0599 | -0.15106 | 112.1796 | 112.1338 | -10.643 | 112.294 | 112.2437 | 0.10986 | -10.6979 | 123.1476 | 122.9828 | 122.9279 | -2.1881 | 112.4908 | 112.4359 | 112.2986 | -11.0001
689.6875 | 123.1934 | -112.4313 | 10.7437 | 0.095301 | 0.10698 | -0.0069409 | 0.028013 | 0.0010188 | 0.0037594 | 0.041342 | -0.081838 | 0.032106 | 0.0085924 | 0.0069698 | 0.0050478 | 0.03663 | 10.5927 | 10.5743 | 10.524 | 10.5972 | 10.7346 | 8.5373 | 8.5922 | -0.073242 | -0.027466 | -0.091553 | 0.15564 | 0.11444 | -0.15564 | -0.2243 | 120.9686 | 121.0236 | -0.009155 | 123.0057 | 123.0286 | 2.005 | -0.15106 | 112.2757 | 112.207 | -10.5881 | 112.3581 | 112.3398 | 0.13275 | -10.6293 | 123.1659 | 123.024 | 122.9553 | -2.1515 | 112.587 | 112.5458 | 112.4039 | -10.968
690.6875 | 123.2391 | -112.5641 | 10.5606 | 0.33944 | 0.10484 | -0.0080089 | -0.012575 | -0.0064582 | -0.0079896 | 0.027457 | 0.07075 | 0.02463 | 0.0053884 | 0.0091058 | -0.0024292 | 0.052652 | 10.524 | 10.4507 | 10.3912 | 10.4507 | 10.5972 | 8.5236 | 8.5648 | -0.022888 | -0.022888 | -0.068665 | 0.15106 | 0.09613 | -0.13733 | -0.18768 | 121.0876 | 121.1288 | 0.036621 | 123.0148 | 123.0148 | 1.886 | -0.036621 | 112.4268 | 112.3764 | -10.4095 | 112.5412 | 112.4954 | 0.11902 | -10.4645 | 123.1613 | 123.0881 | 122.9553 | -1.9959 | 112.7151 | 112.6602 | 112.5412 | -10.7483
691.6875 | 123.23 | -112.8433 | 10.2722 | 0.36996 | 0.090957 | 0.013353 | 0.0184 | -0.0096622 | 0.0016234 | 0.013571 | 0.25385 | 0.026766 | -0.021315 | 0.0069698 | -0.0013612 | 0.045175 | 10.3363 | 10.0571 | 10.0708 | 10.1944 | 10.3226 | 8.4778 | 8.4961 | -0.013733 | -0.032043 | -0.054932 | 0.16479 | 0.10071 | -0.1236 | -0.18768 | 121.3211 | 121.3394 | 0.050354 | 122.9004 | 123.0377 | 1.6983 | 0.064087 | 112.7197 | 112.6556 | -10.1074 | 112.8296 | 112.7884 | 0.13275 | -10.1715 | 123.1659 | 123.1796 | 122.9141 | -1.7761 | 113.0081 | 112.944 | 112.8113 | -10.4599
692.6875 | 123.2346 | -113.3835 | 9.7595 | 0.32418 | 0.092026 | 0.0069441 | 0.020536 | -0.0064582 | -0.0026496 | 0.025321 | -0.57012 | 0.031038 | -0.0020886 | 0.014447 | 0.0071838 | 0.050516 | 9.5581 | 9.7916 | 9.6863 | 9.668 | 9.7916 | 8.3725 | 8.3496 | -0.018311 | -0.041199 | -0.068665 | 0.16022 | 0.10529 | -0.12817 | -0.18768 | 121.756 | 121.7331 | 0.032044 | 123.175 | 123.0515 | 1.3184 | -0.20142 | 113.2553 | 113.1958 | -9.5993 | 113.3652 | 113.3148 | 0.11902 | -9.6542 | 123.175 | 122.9416 | 123.0698 | -1.4099 | 113.5437 | 113.4888 | 113.3423 | -9.9472
693.6875 | 123.2483 | -113.4796 | 9.6405 | 0.32418 | 0.1198 | 0.0069441 | 0.022672 | -0.0053902 | -0.00051261 | 0.022116 | -0.14287 | 0.0075398 | -0.0020886 | 0.015515 | -0.0045652 | 0.04838 | 9.4894 | 9.4528 | 9.4162 | 9.4757 | 9.6817 | 8.3359 | 8.3176 | -0.013733 | -0.032043 | -0.086975 | 0.18768 | 0.11902 | -0.14648 | -0.21515 | 121.8155 | 121.7972 | 0.041199 | 122.9324 | 122.9553 | 1.1581 | -0.15106 | 113.3331 | 113.2645 | -9.4528 | 113.4659 | 113.3926 | 0.12817 | -9.5215 | 123.1613 | 122.9691 | 122.8958 | -1.3229 | 113.6673 | 113.5986 | 113.4476 | -9.8557
694.6875 | 123.3307 | -113.8184 | 9.2651 | 0.47677 | 0.087753 | 0.0016041 | 0.015196 | -0.0053902 | -0.00051261 | 0.022116 | 0.29963 | 0.019289 | -0.0010206 | 0.0059018 | 0.0061158 | 0.040903 | 9.1873 | 9.169 | 9.1278 | 9.1965 | 9.3109 | 8.226 | 8.1665 | 0.054932 | 0.050354 | 0.027466 | 0.1236 | 0.09613 | -0.09613 | -0.1831 | 122.0444 | 121.9849 | 0.045776 | 122.9874 | 123.0148 | 1.03 | -0.07782 | 113.7222 | 113.6353 | -9.1415 | 113.8733 | 113.8458 | 0.21057 | -9.169 | 123.1293 | 123.0057 | 122.9462 | -1.0986 | 113.942 | 113.9145 | 113.8687 | -9.4482
695.6875 | 123.2025 | -114.5004 | 8.6655 | 0.50729 | 0.099502 | -0.0037369 | 0.021604 | -0.0064582 | 0.022985 | 0.026389 | 0.055491 | 0.019289 | -0.0063606 | 0.01231 | -0.0002932 | 0.052652 | 8.5144 | 8.4686 | 8.432 | 8.5373 | 8.6929 | 7.9376 | 7.8278 | -0.050354 | -0.073242 | -0.10071 | 0.15564 | 0.10529 | -0.12817 | -0.20142 | 122.438 | 122.3282 | 0.027466 | 122.9691 | 123.0377 | 0.70953 | -0.15106 | 114.3723 | 114.299 | -8.5098 | 114.4501 | 114.3997 | 0.10071 | -8.5602 | 123.1934 | 123.0148 | 122.9324 | -0.83771 | 114.6561 | 114.6057 | 114.4272 | -8.8669
696.6875 | 123.2483 | -114.4135 | 8.7296 | 0.29367 | 0.10698 | 0.0016041 | 0.024809 | -0.0043222 | 0.0037594 | 0.03707 | -2.2486 | 0.023562 | 0.0021844 | 0.015515 | -0.0024292 | 0.051584 | 8.5831 | 8.5419 | 8.4869 | 8.5693 | 8.7524 | 7.9559 | 7.8506 | -0.018311 | -0.004578 | -0.064087 | 0.17853 | 0.12817 | -0.11444 | -0.15564 | 122.3694 | 122.2641 | 0.022888 | 122.9553 | 122.9828 | 0.71869 | -0.14648 | 114.299 | 114.2578 | -8.551 | 114.3951 | 114.3494 | 0.091553 | -8.6014 | 123.1659 | 122.9965 | 122.9004 | -0.87891 | 114.592 | 114.5416 | 114.4089 | -8.8852
697.6875 | 123.3307 | -114.4684 | 8.6243 | 0.38522 | 0.10591 | -0.0090779 | 0.025877 | 0.0084958 | -0.0058536 | 0.021048 | 0.19282 | 0.020357 | -0.0042246 | 0.018719 | 0.0050478 | 0.047312 | 8.5144 | 8.4961 | 8.4457 | 8.5281 | 8.6746 | 7.9193 | 7.8094 | 0.045776 | 0.027466 | 0.004578 | 0.1236 | 0.091553 | -0.09613 | -0.16937 | 122.3877 | 122.2778 | 0.050354 | 122.9645 | 122.9965 | 0.71869 | -0.10986 | 114.3723 | 114.299 | -8.5007 | 114.5142 | 114.473 | 0.17395 | -8.5327 | 123.143 | 122.9828 | 122.9141 | -0.81482 | 114.592 | 114.5599 | 114.4959 | -8.7936
698.6875 | 123.317 | -114.5004 | 8.6014 | 0.431 | 0.079208 | 0.0090801 | 0.032286 | -4.9167e-05 | -0.0047856 | 0.027457 | 0.29963 | 0.019289 | -0.011702 | 0.015515 | 0.0029108 | 0.046244 | 8.519 | 8.4869 | 8.4503 | 8.519 | 8.6426 | 7.9147 | 7.8003 | 0.032043 | 0.013733 | 0 | 0.1236 | 0.082397 | -0.10071 | -0.1831 | 122.4152 | 122.3007 | 0.041199 | 122.9874 | 123.0194 | 0.71869 | -0.082397 | 114.3997 | 114.3173 | -8.4778 | 114.5325 | 114.5004 | 0.1831 | -8.519 | 123.143 | 123.0194 | 122.9507 | -0.80109 | 114.624 | 114.5828 | 114.5142 | -8.7845
699.6875 | 123.3078 | -114.6606 | 8.4641 | 0.24789 | 0.10484 | -0.0080089 | 0.024809 | -0.0085942 | -0.00051261 | 0.017844 | 0.22334 | 0.026766 | -0.0052926 | 0.00056082 | 0.0050478 | 0.033426 | 8.3496 | 8.313 | 8.2764 | 8.345 | 8.4869 | 7.8232 | 7.7042 | 0.050354 | 0.022888 | -0.013733 | 0.12817 | 0.086975 | -0.09613 | -0.15564 | 122.4838 | 122.3648 | 0.022888 | 122.9736 | 123.0057 | 0.64087 | -0.11444 | 114.5645 | 114.505 | -8.3359 | 114.711 | 114.6469 | 0.14191 | -8.3771 | 123.1476 | 123.0103 | 122.937 | -0.75989 | 114.7888 | 114.7476 | 114.6835 | -8.6197
700.6875 | 123.3215 | -115.0085 | 8.1345 | 0.431 | 0.077072 | 0.0080121 | 0.031217 | -0.0075262 | -0.0037176 | 0.01998 | 0.28437 | 0.02463 | 0.0021844 | 0.010174 | 0.0082518 | 0.04838 | 8.0109 | 7.988 | 7.9376 | 8.0154 | 8.1528 | 7.5897 | 7.457 | 0.032043 | 0.018311 | -0.013733 | 0.14191 | 0.10071 | -0.10529 | -0.16937 | 122.5983 | 122.4655 | 0.018311 | 122.9965 | 123.024 | 0.55847 | -0.1236 | 114.9033 | 114.8392 | -7.9926 | 115.0406 | 114.9948 | 0.15564 | -8.0338 | 123.1613 | 123.0194 | 122.9462 | -0.67749 | 115.1505 | 115.1093 | 115.0269 | -8.3038
701.6875 | 123.317 | -115.4343 | 7.6813 | 0.21737 | 0.10484 | 0.0016041 | 0.023741 | -0.013935 | -0.0037176 | 0.015708 | 0.25385 | 0.019289 | -0.0031566 | 0.0080378 | 0.0018428 | 0.045175 | 7.5851 | 7.5256 | 7.4982 | 7.5668 | 7.7133 | 7.2739 | 7.1228 | 0.022888 | 0.018311 | -0.018311 | 0.14648 | 0.086975 | -0.11444 | -0.19684 | 122.7081 | 122.5571 | 0.032044 | 122.9599 | 123.0011 | 0.44403 | -0.09613 | 115.3198 | 115.2374 | -7.5348 | 115.4572 | 115.416 | 0.17853 | -7.5943 | 123.1476 | 123.0194 | 122.9324 | -0.55847 | 115.5807 | 115.5212 | 115.4526 | -7.8781
702.6875 | 123.2986 | -115.9012 | 7.2372 | 0.38522 | 0.10164 | 0.0026721 | 0.014128 | -0.0096622 | -0.00051261 | 0.030661 | 0.2386 | 0.0096758 | -0.0020886 | 0.021923 | 0.0029108 | 0.050516 | 7.1411 | 7.1091 | 7.0587 | 7.1365 | 7.2739 | 6.8939 | 6.752 | 0.032043 | 0.018311 | -0.027466 | 0.14648 | 0.091553 | -0.10986 | -0.16479 | 122.7951 | 122.6532 | 0.036621 | 123.0103 | 123.0377 | 0.38452 | -0.096131 | 115.7913 | 115.7364 | -7.0908 | 115.9332 | 115.8737 | 0.13733 | -7.1457 | 123.175 | 123.0423 | 122.9599 | -0.48523 | 116.0477 | 115.9927 | 115.9195 | -7.402
703.6875 | 123.2986 | -116.1667 | 6.9443 | 0.30892 | 0.088821 | -0.0058729 | 0.021604 | 0.0063598 | 0.00055539 | 0.022116 | 0.28437 | 0.025698 | 0.0021844 | 0.010174 | -0.0045652 | 0.041971 | 6.8436 | 6.7932 | 6.7566 | 6.8115 | 6.9809 | 6.6284 | 6.4728 | 0.027466 | 0.009155 | -0.027466 | 0.14648 | 0.09613 | -0.10071 | -0.17853 | 122.7951 | 122.6395 | 0.036621 | 122.9599 | 122.9782 | 0.33875 | -0.10071 | 116.066 | 115.9882 | -6.7978 | 116.1942 | 116.1392 | 0.15106 | -6.8481 | 123.1476 | 123.0103 | 122.9233 | -0.4715 | 116.3132 | 116.2628 | 116.1758 | -7.1228
704.6875 | 123.3444 | -116.4185 | 6.6788 | 0.40048 | 0.092026 | -0.012282 | 0.016264 | 0.0084958 | -0.010127 | 0.026389 | 0.31489 | 0.023562 | -0.013838 | 0.018719 | 0.011456 | 0.052652 | 6.6284 | 6.6467 | 6.5872 | 6.6284 | 6.6879 | 6.4133 | 6.2576 | 0.032043 | 0.20599 | 0.050354 | 0.10986 | 0.050354 | -0.1236 | -0.1831 | 122.8317 | 122.6761 | 0.009155 | 123.0652 | 123.0469 | 0.37079 | -0.050354 | 116.2949 | 116.2354 | -6.5689 | 116.4505 | 116.4688 | 0.23346 | -6.6284 | 123.1064 | 123.0469 | 123.0057 | -0.42114 | 116.5283 | 116.4688 | 116.6245 | -6.8619
705.6875 | 123.3582 | -116.5741 | 6.5231 | 0.41574 | 0.082412 | 0.0016041 | 0.022672 | -0.0064582 | -0.0015816 | 0.027457 | 0.36067 | 0.016085 | -0.0095656 | 0.011242 | 0.0029108 | 0.045175 | 6.4865 | 6.4728 | 6.427 | 6.4407 | 6.5506 | 6.2576 | 6.102 | 0.07782 | 0.073242 | 0.041199 | 0.11902 | 0.059509 | -0.082397 | -0.13275 | 122.8317 | 122.6761 | 0.027466 | 123.0469 | 123.0148 | 0.33875 | -0.036621 | 116.4917 | 116.4413 | -6.4041 | 116.6519 | 116.6153 | 0.17395 | -6.4636 | 123.1247 | 123.0606 | 123.0011 | -0.42114 | 116.6931 | 116.6336 | 116.6473 | -6.6559
706.6875 | 123.3582 | -116.748 | 6.3583 | 0.38522 | 0.077072 | 0.0048081 | 0.030149 | 0.010632 | -0.010127 | 0.023184 | -0.12761 | 0.017153 | -0.013838 | -0.0090522 | 0.0039788 | 0.049448 | 6.308 | 6.2805 | 6.2347 | 6.2942 | 6.3583 | 6.0883 | 5.9372 | 0.082397 | 0.10071 | 0.018311 | 0.1236 | 0.059509 | -0.073242 | -0.15106 | 122.8363 | 122.6852 | 0 | 123.0286 | 123.0423 | 0.35705 | -0.050354 | 116.6748 | 116.597 | -6.2347 | 116.8304 | 116.7664 | 0.16937 | -6.2988 | 123.1064 | 123.056 | 122.9828 | -0.42114 | 116.8716 | 116.8076 | 116.8488 | -6.5094
707.6875 | 123.3627 | -116.8991 | 6.221 | 0.41574 | 0.10271 | 0.00053514 | 0.021604 | 0.0042228 | -0.0058536 | 0.025321 | 1.2609 | 0.023562 | -0.022383 | 0.00056082 | 0.0018428 | 0.045175 | 6.1523 | 6.1386 | 6.0883 | 6.1478 | 6.2256 | 5.9509 | 5.8044 | 0.086975 | 0.082397 | 0.036621 | 0.12817 | 0.07782 | -0.07782 | -0.14648 | 122.85 | 122.7036 | 0.004578 | 123.0377 | 123.0469 | 0.34332 | -0.068664 | 116.8213 | 116.7526 | -6.0928 | 116.9861 | 116.9357 | 0.18311 | -6.1432 | 123.1247 | 123.0515 | 122.9874 | -0.41657 | 117.0273 | 116.9769 | 116.9815 | -6.3675
708.6875 | 123.2712 | -117.1921 | 5.9784 | -3.933 | 0.092026 | -0.011214 | 0.023741 | -0.0032532 | 0.00055539 | 0.025321 | 0.1623 | 0.028902 | 0.0011164 | 0.014447 | -0.0013612 | 0.043039 | 5.8502 | 5.7678 | 5.722 | 5.809 | 6.0242 | 5.6992 | 5.5527 | 0.013733 | -0.027466 | -0.054932 | 0.16022 | 0.10986 | -0.1236 | -0.1831 | 122.8912 | 122.7448 | 0.045776 | 122.9599 | 123.0011 | 0.25635 | -0.12817 | 117.0685 | 117.009 | -5.8182 | 117.2058 | 117.1371 | 0.12817 | -5.8685 | 123.2162 | 123.0423 | 122.9141 | -0.42572 | 117.3523 | 117.3019 | 117.1646 | -6.1615
709.6875 | 123.2666 | -117.3798 | 5.777 | 0.33944 | 0.093094 | -0.00053286 | 0.03549 | -0.0043222 | 0.0016234 | 0.028525 | 0.17756 | 0.025698 | -0.0020886 | 0.0080378 | 0.0007748 | 0.045175 | 5.6442 | 5.5801 | 5.5344 | 5.6305 | 5.8319 | 5.5161 | 5.3558 | -0.004578 | -0.022888 | -0.054932 | 0.16022 | 0.11444 | -0.10986 | -0.1831 | 122.8958 | 122.7356 | 0.054931 | 122.9599 | 123.0103 | 0.27466 | -0.13275 | 117.2699 | 117.1967 | -5.6168 | 117.3752 | 117.3248 | 0.12817 | -5.6625 | 123.2117 | 123.024 | 122.9141 | -0.42114 | 117.54 | 117.4942 | 117.3569 | -5.9601
710.6875 | 123.3536 | -117.4484 | 5.7037 | 0.431 | 0.087753 | 0.013353 | 0.021604 | -0.0021852 | -0.011195 | 0.01998 | 0.31489 | 0.013948 | -0.014906 | 0.019787 | 0.0007748 | 0.044107 | 5.6396 | 5.6625 | 5.5939 | 5.6396 | 5.7083 | 5.484 | 5.3284 | 0.086975 | 0.091553 | 0.041199 | 0.1236 | 0.073242 | -0.07782 | -0.13275 | 122.9324 | 122.7768 | 0.004578 | 123.111 | 123.0881 | 0.31128 | -0.064087 | 117.3706 | 117.3157 | -5.5801 | 117.5354 | 117.4896 | 0.17395 | -5.6305 | 123.1567 | 123.0881 | 123.0423 | -0.37537 | 117.572 | 117.5217 | 117.54 | -5.8365
711.6875 | 123.3536 | -117.3477 | 5.7495 | 0.49203 | 0.069595 | -0.011214 | 0.030149 | -0.0053902 | 0.0026914 | 0.025321 | 0.25385 | 0.011812 | -0.014906 | 0.0026968 | -0.0056342 | 0.043039 | 5.7037 | 5.7175 | 5.6625 | 5.6854 | 5.7587 | 5.5298 | 5.3833 | 0.086975 | 0.10071 | 0.050354 | 0.11444 | 0.068665 | -0.09613 | -0.15106 | 122.8775 | 122.731 | 0.009155 | 123.0652 | 123.0331 | 0.30212 | -0.045777 | 117.2516 | 117.1967 | -5.6351 | 117.4347 | 117.3981 | 0.20142 | -5.6808 | 123.1064 | 123.0515 | 123.0103 | -0.36621 | 117.4622 | 117.4164 | 117.4484 | -5.9006
712.6875 | 123.3765 | -117.5766 | 5.5344 | 0.32418 | 0.089889 | -0.0037369 | 0.023741 | -0.0085942 | 0.0016234 | 0.025321 | 0.31489 | 0.022493 | -0.0042246 | 0.0059018 | 0.0029108 | 0.045175 | 5.5023 | 5.4932 | 5.4428 | 5.4703 | 5.5527 | 5.3375 | 5.1727 | 0.10071 | 0.091553 | 0.036621 | 0.11444 | 0.07782 | -0.086975 | -0.14648 | 122.9141 | 122.7493 | 0.01831 | 123.0698 | 123.0469 | 0.29755 | -0.032044 | 117.4896 | 117.4301 | -5.4199 | 117.6773 | 117.6132 | 0.18311 | -5.4565 | 123.1293 | 123.0789 | 123.0194 | -0.36163 | 117.691 | 117.6544 | 117.6682 | -5.6808
713.6875 | 123.3582 | -117.8467 | 5.278 | 0.3547 | 0.080276 | 0.00053514 | 0.019468 | 0.019177 | 0.0016234 | 0.029593 | 0.26911 | 0.02463 | -0.017042 | 0.01231 | 0.0050478 | 0.046244 | 5.2094 | 5.2368 | 5.1453 | 5.2048 | 5.2597 | 5.0537 | 4.9118 | 0.091553 | 0.086975 | 0.054932 | 0.1236 | 0.073242 | -0.082397 | -0.16479 | 122.9004 | 122.7585 | -0.01831 | 123.0835 | 123.0515 | 0.29297 | -0.068664 | 117.7643 | 117.6819 | -5.1544 | 117.9382 | 117.9016 | 0.21973 | -5.2048 | 123.1064 | 123.056 | 122.9919 | -0.36621 | 117.9703 | 117.9199 | 117.9337 | -5.4428
714.6875 | 123.3673 | -118.0115 | 5.1178 | 0.32418 | 0.088821 | 0.00053514 | 0.025877 | 0.0031548 | -0.0015816 | 0.033866 | 0.31489 | 0.0032668 | -0.0031566 | 0.017651 | -0.0034972 | 0.040903 | 5.0583 | 5.072 | 4.9988 | 5.04 | 5.127 | 4.921 | 4.7516 | 0.10529 | 0.09613 | 0.041199 | 0.11902 | 0.068665 | -0.091553 | -0.16022 | 122.9324 | 122.7631 | 0.009155 | 123.0835 | 123.0515 | 0.28839 | -0.059509 | 117.9199 | 117.8513 | -4.9988 | 118.1168 | 118.0527 | 0.20142 | -5.0491 | 123.1384 | 123.0698 | 123.0103 | -0.36621 | 118.1305 | 118.0801 | 118.1076 | -5.278
715.6875 | 123.3673 | -118.1442 | 5.0034 | 0.3547 | 0.094162 | -0.0037369 | 0.034422 | -0.01073 | 0.0016234 | 0.01998 | 0.25385 | 0.022493 | -0.013838 | -0.013324 | -0.0034972 | 0.056925 | 4.8981 | 4.8706 | 4.8294 | 4.8843 | 5.0079 | 4.7607 | 4.6143 | 0.082397 | 0.07782 | 0.013733 | 0.14191 | 0.07782 | -0.082397 | -0.16022 | 122.905 | 122.7585 | 0.004578 | 123.0148 | 123.0286 | 0.27008 | -0.10529 | 118.0618 | 117.984 | -4.8615 | 118.2266 | 118.158 | 0.17395 | -4.9255 | 123.1522 | 123.0423 | 122.9736 | -0.3891 | 118.2861 | 118.222 | 118.222 | -5.1636
716.6875 | 123.3307 | -118.2449 | 4.8523 | 0.38522 | 0.086685 | -0.0026689 | 0.025877 | 0.0010188 | 0.0048274 | 0.030661 | 0.22334 | 0.020357 | -0.01277 | 0.013378 | 0.0039788 | 0.032358 | 4.7699 | 4.7424 | 4.6829 | 4.7562 | 4.866 | 4.6417 | 4.4861 | 0.082397 | 0.073242 | 0.004578 | 0.14648 | 0.091553 | -0.086975 | -0.14191 | 122.8867 | 122.731 | 0.013733 | 122.9874 | 123.0011 | 0.27008 | -0.082398 | 118.158 | 118.103 | -4.7058 | 118.3273 | 118.2495 | 0.14649 | -4.7607 | 123.111 | 123.0148 | 122.9279 | -0.36621 | 118.3914 | 118.3365 | 118.3182 | -4.9942
717.6875 | 123.3353 | -118.3502 | 4.7745 | -0.51505 | 0.088821 | 0.011217 | 0.0087873 | -0.013935 | -0.020808 | 0.023184 | 0.29963 | 0.0032668 | -0.013838 | 0.00056082 | -0.0077702 | 0.049448 | 4.7058 | 4.7195 | 4.6371 | 4.6692 | 4.7607 | 4.541 | 4.4037 | 0.086975 | 0.059509 | 0.041199 | 0.12817 | 0.091553 | -0.086975 | -0.13733 | 122.8912 | 122.7539 | -0.013733 | 123.0698 | 123.0194 | 0.2655 | -0.068664 | 118.2632 | 118.2129 | -4.6463 | 118.4372 | 118.3914 | 0.17853 | -4.6829 | 123.111 | 123.056 | 122.9874 | -0.37079 | 118.4784 | 118.4418 | 118.4097 | -4.9118
718.6875 | 123.3261 | -118.5425 | 4.6143 | 0.70565 | 0.079208 | -0.0037369 | 0.024809 | -0.0043222 | -0.013331 | 0.023184 | 0.25385 | 0.01288 | -0.022383 | 0.0048338 | -0.0067022 | 0.039835 | 4.541 | 4.541 | 4.4998 | 4.5181 | 4.6005 | 4.39 | 4.2252 | 0.086975 | 0.07782 | 0.036621 | 0.14191 | 0.09613 | -0.07782 | -0.13275 | 122.9324 | 122.7676 | -0.013733 | 123.0835 | 123.0606 | 0.29297 | -0.073242 | 118.4647 | 118.4097 | -4.4724 | 118.6295 | 118.5791 | 0.16937 | -4.5181 | 123.143 | 123.0835 | 123.0423 | -0.3891 | 118.6844 | 118.6386 | 118.6203 | -4.747
719.6875 | 123.317 | -118.6249 | 4.4998 | 0.40048 | 0.062118 | 0.0048081 | 0.019468 | -0.0053902 | -0.0047856 | 0.012503 | 0.2386 | 0.015017 | -0.013838 | 0.011242 | -0.0024292 | 0.05372 | 4.4357 | 4.4678 | 4.39 | 4.4128 | 4.5319 | 4.303 | 4.1565 | 0.09613 | 0.09613 | 0.050354 | 0.11444 | 0.091553 | -0.07782 | -0.14648 | 122.9279 | 122.7814 | 0.032043 | 123.0927 | 123.0377 | 0.25635 | -0.064087 | 118.5471 | 118.4784 | -4.3854 | 118.721 | 118.6752 | 0.19684 | -4.4083 | 123.1567 | 123.0606 | 123.0148 | -0.34332 | 118.7393 | 118.7164 | 118.721 | -4.6463
720.6875 | 123.3398 | -118.6935 | 4.4632 | 0.1716 | 0.069595 | 0.0037401 | 0.024809 | -0.0096622 | -0.010127 | 0.024253 | 0.13178 | 0.018221 | -0.0010206 | -0.01012 | -0.0045652 | 0.040903 | 4.3808 | 4.3671 | 4.3121 | 4.335 | 4.4586 | 4.2252 | 4.0878 | 0.10071 | 0.068665 | 0.027466 | 0.14648 | 0.07782 | -0.07782 | -0.13275 | 122.9187 | 122.7814 | -0.004578 | 123.0606 | 123.0286 | 0.24719 | -0.082398 | 118.6157 | 118.5608 | -4.3167 | 118.7942 | 118.721 | 0.16022 | -4.3854 | 123.1522 | 123.0743 | 123.0057 | -0.37537 | 118.84 | 118.7714 | 118.7622 | -4.5959
721.6875 | 123.3353 | -118.8492 | 4.303 | 0.27841 | 0.062118 | 0.0058761 | 0.024809 | -0.0021852 | -0.0037176 | 0.01998 | 0.22334 | 0.018221 | -0.013838 | 0.016583 | -0.0067022 | 0.039835 | 4.2068 | 4.2343 | 4.1702 | 4.184 | 4.2847 | 4.0924 | 3.923 | 0.082397 | 0.07782 | 0.041199 | 0.15564 | 0.10529 | -0.054932 | -0.12817 | 122.9416 | 122.7722 | -0.018311 | 123.0835 | 123.0331 | 0.26092 | -0.096131 | 118.7943 | 118.721 | -4.1473 | 118.9316 | 118.8904 | 0.16937 | -4.1977 | 123.1338 | 123.056 | 123.0194 | -0.37994 | 119.0048 | 118.9545 | 118.927 | -4.4312
722.6875 | 123.3719 | -119.0186 | 4.1153 | 0.41574 | 0.084549 | -0.012282 | 0.021604 | 0.0052918 | -0.00051261 | 0.027457 | 0.14704 | 0.013948 | -0.010634 | 0.015515 | 0.0082518 | 0.030222 | 4.0924 | 4.0878 | 4.0009 | 4.0329 | 4.1199 | 3.923 | 3.7811 | 0.10071 | 0.19226 | 0.054932 | 0.10986 | 0.068665 | -0.10986 | -0.16937 | 122.9416 | 122.7997 | 0.004578 | 123.1064 | 123.0515 | 0.25177 | -0.022888 | 118.9087 | 118.8492 | -4.0054 | 119.1193 | 119.0735 | 0.22431 | -4.0466 | 123.1384 | 123.111 | 123.0194 | -0.33417 | 119.1284 | 119.0872 | 119.2108 | -4.2847
723.6875 | 123.3215 | -119.1559 | 4.0009 | 0.30892 | 0.068527 | 0.0069441 | 0.0034463 | -0.0085942 | -0.016535 | 0.024253 | 0.1623 | 0.01288 | -0.011702 | 0.014447 | -0.0034972 | 0.041971 | 3.9185 | 3.9276 | 3.8544 | 3.8727 | 3.9963 | 3.7903 | 3.6392 | 0.086975 | 0.068665 | 0.036621 | 0.15106 | 0.086975 | -0.064087 | -0.13733 | 122.9462 | 122.7951 | -0.004577 | 123.0835 | 123.0286 | 0.23346 | -0.082397 | 119.0918 | 119.0186 | -3.8498 | 119.2429 | 119.1925 | 0.17395 | -3.9139 | 123.1522 | 123.0743 | 123.0103 | -0.36163 | 119.3069 | 119.2429 | 119.2245 | -4.1382
724.6875 | 123.3307 | -119.2703 | 3.8818 | 0.049525 | 0.056778 | -0.0037369 | 0.023741 | -0.0011172 | -0.011195 | 0.015708 | 0.055491 | 0.013948 | -0.023451 | 0.010174 | -0.0024292 | 0.047312 | 3.772 | 3.7537 | 3.7079 | 3.7537 | 3.9047 | 3.6667 | 3.5431 | 0.050354 | 0.054932 | 0.018311 | 0.15564 | 0.091553 | -0.09613 | -0.14648 | 122.937 | 122.8134 | 0.022888 | 123.024 | 123.024 | 0.21057 | -0.10986 | 119.1742 | 119.1238 | -3.7262 | 119.3207 | 119.2886 | 0.16479 | -3.7903 | 123.175 | 123.0423 | 122.9782 | -0.33874 | 119.426 | 119.3619 | 119.3253 | -4.0283
725.6875 | 123.3261 | -119.3298 | 3.8544 | 0.1716 | 0.081344 | 0.0048081 | 0.022672 | -0.01073 | -0.014399 | 0.013571 | 0.009715 | 0.0096758 | -0.017042 | -0.0015752 | -0.0024292 | 0.040903 | 3.7033 | 3.7033 | 3.6438 | 3.6804 | 3.8269 | 3.6118 | 3.479 | 0.064087 | 0.054932 | 0.018311 | 0.13733 | 0.10986 | -0.073242 | -0.12817 | 122.9416 | 122.8088 | -0.027466 | 123.0331 | 123.0103 | 0.20142 | -0.15106 | 119.2566 | 119.2017 | -3.717 | 119.3939 | 119.3481 | 0.14649 | -3.7445 | 123.1567 | 123.0331 | 122.9736 | -0.37537 | 119.4672 | 119.4397 | 119.3848 | -3.9825
726.6875 | 123.3307 | -119.4443 | 3.717 | 0.11056 | 0.053573 | 0.0037401 | 0.014128 | -0.01073 | -0.0079896 | 0.023184 | 0.024973 | 0.0075398 | -0.018111 | 0.0048338 | -0.0013612 | 0.046244 | 3.6026 | 3.5889 | 3.5339 | 3.566 | 3.7308 | 3.5019 | 3.3691 | 0.059509 | 0.054932 | 0.022888 | 0.14191 | 0.082397 | -0.073242 | -0.14191 | 122.9462 | 122.8134 | 0.013733 | 123.0331 | 123.0103 | 0.19684 | -0.11444 | 119.371 | 119.3024 | -3.5751 | 119.5038 | 119.4672 | 0.16479 | -3.6346 | 123.175 | 123.0469 | 122.9782 | -0.3479 | 119.5862 | 119.5267 | 119.4992 | -3.8589
727.6875 | 123.3307 | -119.5084 | 3.6575 | 0.11056 | 0.064255 | 0.0048081 | 0.016264 | -0.022479 | -0.016535 | 0.017844 | -0.005544 | 0.017153 | -0.011702 | 0.0026968 | 0.0029108 | 0.04838 | 3.511 | 3.5385 | 3.4515 | 3.5065 | 3.653 | 3.4332 | 3.2959 | 0.059509 | 0.054932 | 0.022888 | 0.13733 | 0.11444 | -0.068665 | -0.14191 | 122.9416 | 122.8043 | -0.004578 | 123.0469 | 123.0148 | 0.21057 | -0.14648 | 119.4397 | 119.3665 | -3.5202 | 119.5679 | 119.5312 | 0.16479 | -3.5431 | 123.1613 | 123.0194 | 122.9599 | -0.36163 | 119.6457 | 119.6228 | 119.5633 | -3.7994
728.6875 | 123.3353 | -119.6136 | 3.5294 | 0.034266 | 0.059982 | 0.0048081 | 0.0184 | -4.9167e-05 | -0.0026496 | 0.025321 | -0.05132 | 0.020357 | -0.014906 | -0.0015752 | -0.012042 | 0.041971 | 3.4287 | 3.4561 | 3.3829 | 3.4149 | 3.5568 | 3.3646 | 3.186 | 0.050354 | 0.064087 | 0.032043 | 0.16022 | 0.086975 | -0.086975 | -0.14648 | 122.9782 | 122.7997 | 0.027466 | 123.0698 | 123.0286 | 0.22888 | -0.10071 | 119.5267 | 119.4672 | -3.3691 | 119.664 | 119.6457 | 0.17853 | -3.4424 | 123.1705 | 123.0423 | 122.9965 | -0.34332 | 119.7739 | 119.7006 | 119.6777 | -3.6758
729.6875 | 123.3307 | -119.6732 | 3.5065 | 0.21737 | 0.053573 | 0.00053514 | 0.032286 | -0.0011172 | -0.0037176 | 0.029593 | 0.086009 | 0.020357 | -0.014906 | 0.016583 | -0.0024292 | 0.03663 | 3.4103 | 3.4241 | 3.3554 | 3.3783 | 3.5202 | 3.3005 | 3.1631 | 0.09613 | 0.045776 | 0.013733 | 0.14191 | 0.086975 | -0.068665 | -0.15106 | 122.9736 | 122.8363 | 0.013733 | 123.0972 | 123.0515 | 0.21515 | -0.096131 | 119.6045 | 119.5221 | -3.3646 | 119.7693 | 119.6869 | 0.16479 | -3.4195 | 123.1934 | 123.0835 | 123.0286 | -0.34332 | 119.8151 | 119.7601 | 119.7189 | -3.6575
730.6875 | 123.3215 | -119.8334 | 3.3646 | 0.095301 | 0.050369 | 0.0048081 | 0.011991 | -0.0032532 | -0.0079896 | 0.025321 | -0.05132 | 0.019289 | -0.011702 | 0.00056082 | -0.0002932 | 0.034494 | 3.3417 | 3.3325 | 3.2684 | 3.3234 | 3.4607 | 3.2455 | 3.1128 | 0.064087 | 0.073242 | 0.022888 | 0.16479 | 0.09613 | -0.07782 | -0.13733 | 123.0789 | 122.9462 | 0.09613 | 123.1659 | 123.1567 | 0.21057 | -0.022888 | 119.7556 | 119.696 | -3.1998 | 119.8975 | 119.8563 | 0.16022 | -3.2684 | 123.2941 | 123.175 | 123.1018 | -0.25177 | 119.9982 | 119.9295 | 119.9066 | -3.5019
731.6875 | 123.3856 | -119.8059 | 3.36 | -0.13358 | 0.048233 | -0.0026689 | 0.019468 | -0.01073 | -0.0069216 | 0.021048 | -0.23443 | 0.011812 | -0.022383 | 0.0037648 | -0.0056342 | 0.045175 | 3.2364 | 3.2959 | 3.1906 | 3.2318 | 3.3646 | 3.1448 | 2.9984 | 0.10986 | 0.12817 | 0.073242 | 0.15564 | 0.10529 | -0.068665 | -0.11902 | 122.9507 | 122.8043 | 0.004578 | 123.1018 | 123.0377 | 0.23346 | -0.1236 | 119.7372 | 119.6869 | -3.2043 | 119.9158 | 119.8791 | 0.19226 | -3.2547 | 123.1705 | 123.0423 | 122.9965 | -0.36163 | 119.9615 | 119.9112 | 119.9341 | -3.479
732.6875 | 123.3673 | -119.8563 | 3.3051 | -0.01151 | 0.063186 | 0.0026721 | 0.0077193 | -0.019275 | -0.0090576 | 0.017844 | -0.15813 | 0.0075398 | -0.023451 | 0.0016288 | -0.01311 | 0.047312 | 3.1906 | 3.2455 | 3.1357 | 3.1906 | 3.3554 | 3.0945 | 2.9572 | 0.10529 | 0.11902 | 0.064087 | 0.18768 | 0.086975 | -0.050354 | -0.14648 | 122.9507 | 122.8134 | 0.050354 | 123.1018 | 123.0469 | 0.23346 | -0.11444 | 119.8059 | 119.7098 | -3.1174 | 119.9615 | 119.9203 | 0.21057 | -3.2181 | 123.2117 | 123.0469 | 122.9919 | -0.3479 | 120.0439 | 119.9432 | 119.9753 | -3.4515
733.6875 | 123.3765 | -119.8654 | 3.3005 | -0.01151 | 0.046097 | -0.0026689 | 0.020536 | -0.01073 | -0.010127 | 0.026389 | -0.18865 | 0.016085 | -0.027724 | 0.011242 | -0.0067022 | 0.03663 | 3.1723 | 3.2089 | 3.1357 | 3.1723 | 3.3279 | 3.0716 | 2.9343 | 0.11902 | 0.10986 | 0.059509 | 0.16479 | 0.10071 | -0.068665 | -0.1236 | 122.937 | 122.7997 | 0.027466 | 123.0743 | 123.0377 | 0.23804 | -0.12817 | 119.7968 | 119.7418 | -3.1357 | 119.9844 | 119.9249 | 0.1831 | -3.1998 | 123.1934 | 123.0377 | 123.0011 | -0.36621 | 120.0302 | 119.9661 | 119.9753 | -3.4241
734.6875 | 123.3627 | -120.0211 | 3.1265 | 0.064784 | 0.052505 | 0.0090801 | 0.023741 | -0.011798 | -0.0079896 | 0.017844 | -0.23443 | 0.018221 | -0.020247 | -0.0015752 | -0.0034972 | 0.037699 | 3.035 | 3.0808 | 2.9938 | 3.0212 | 3.154 | 2.9343 | 2.7832 | 0.10986 | 0.11444 | 0.064087 | 0.16937 | 0.10986 | -0.045776 | -0.12817 | 122.9553 | 122.8043 | 0.027466 | 123.1018 | 123.0423 | 0.23804 | -0.091553 | 119.9753 | 119.8929 | -2.9572 | 120.1309 | 120.0851 | 0.19226 | -3.0167 | 123.175 | 123.056 | 123.0148 | -0.34332 | 120.1904 | 120.1309 | 120.1355 | -3.2547
735.6875 | 123.3765 | -120.0165 | 3.1174 | 0.20211 | 0.080276 | 0.010148 | 0.016264 | -0.0096622 | -0.0047856 | 0.029593 | -0.2802 | 0.0054038 | -0.01277 | -0.0047802 | -0.0034972 | 0.032358 | 3.0121 | 3.0441 | 2.9572 | 2.9938 | 3.1265 | 2.8976 | 2.7695 | 0.11902 | 0.09613 | 0.059509 | 0.14191 | 0.09613 | -0.068665 | -0.10529 | 122.9141 | 122.7859 | 0.009155 | 123.0606 | 123.0103 | 0.2243 | -0.10529 | 119.9478 | 119.9112 | -2.9755 | 120.1355 | 120.076 | 0.16479 | -3.0212 | 123.143 | 123.0286 | 122.9736 | -0.3479 | 120.1584 | 120.1126 | 120.1126 | -3.2227
736.6875 | 123.3627 | -120.2087 | 3.0029 | 0.0037495 | 0.051437 | 0.0016041 | 0.0066513 | -0.024616 | 0.00055539 | 0.030661 | 0.024973 | 0.0021988 | -0.014906 | -0.00050718 | -0.0013612 | 0.037699 | 2.9114 | 2.9572 | 2.861 | 2.9114 | 3.0624 | 2.8519 | 2.7145 | 0.082397 | 0.073242 | 0.018311 | 0.16022 | 0.068665 | -0.09613 | -0.13275 | 123.0606 | 122.9233 | 0.059509 | 123.1659 | 123.1201 | 0.19684 | -0.091553 | 120.1126 | 120.076 | -2.8427 | 120.2911 | 120.2271 | 0.15106 | -2.9343 | 123.2712 | 123.1201 | 123.0698 | -0.28839 | 120.369 | 120.2774 | 120.282 | -3.1357
737.6875 | 123.381 | -120.1309 | 3.0258 | -0.01151 | 0.083481 | 0.0016041 | 0.016264 | -0.015003 | -0.0079896 | 0.025321 | -0.24969 | 0.016085 | -0.013838 | 0.013378 | 0.0061158 | 0.037699 | 2.8885 | 2.9251 | 2.8427 | 2.8793 | 3.0121 | 2.7924 | 2.6459 | 0.09613 | 0.11902 | 0.068665 | 0.15564 | 0.11902 | -0.054932 | -0.11444 | 122.9233 | 122.7768 | -0.013733 | 123.056 | 123.0103 | 0.23346 | -0.13733 | 120.076 | 120.0165 | -2.8702 | 120.2271 | 120.1996 | 0.18311 | -2.9068 | 123.143 | 123.0194 | 122.9736 | -0.37994 | 120.2866 | 120.2499 | 120.2499 | -3.1403
738.6875 | 123.4131 | -120.2133 | 2.9388 | -0.11832 | 0.080276 | 0.010148 | 0.00024232 | -0.0085942 | -0.0015816 | 0.013571 | -0.17339 | 0.0064718 | -0.031996 | -0.0047802 | -0.0034972 | 0.03129 | 2.8839 | 2.9572 | 2.8427 | 2.8427 | 2.9846 | 2.7557 | 2.6321 | 0.16479 | 0.16937 | 0.11902 | 0.15564 | 0.082397 | -0.054932 | -0.1236 | 122.9691 | 122.8455 | 0.045776 | 123.1705 | 123.056 | 0.21057 | -0.054932 | 120.1584 | 120.0897 | -2.7832 | 120.3781 | 120.3323 | 0.24261 | -2.8564 | 123.1979 | 123.0972 | 123.056 | -0.3067 | 120.369 | 120.2957 | 120.3827 | -3.0624
739.6875 | 123.4085 | -120.2316 | 2.9434 | -0.14884 | 0.066391 | 0.010148 | 0.015196 | -0.0064582 | -0.0079896 | 0.025321 | -0.17339 | 0.019289 | -0.026655 | -0.0058482 | -0.0067022 | 0.038767 | 2.8793 | 2.9343 | 2.8244 | 2.8427 | 2.948 | 2.7649 | 2.6047 | 0.16479 | 0.17395 | 0.11902 | 0.14648 | 0.09613 | -0.054932 | -0.13275 | 122.9965 | 122.8363 | 0.004578 | 123.1659 | 123.0743 | 0.23804 | -0.064087 | 120.1767 | 120.0989 | -2.7969 | 120.3964 | 120.3506 | 0.25177 | -2.8473 | 123.1796 | 123.111 | 123.056 | -0.33875 | 120.3781 | 120.3278 | 120.4056 | -3.0762
740.6875 | 123.4085 | -120.282 | 2.8564 | -0.1641 | 0.056778 | 0.0058761 | 0.013059 | -0.0021852 | -0.0037176 | 0.025321 | -0.17339 | 0.018221 | -0.014906 | -0.00050718 | -0.0013612 | 0.035562 | 2.8015 | 2.8656 | 2.742 | 2.7603 | 2.8839 | 2.6688 | 2.5177 | 0.16479 | 0.17395 | 0.11444 | 0.15564 | 0.086975 | -0.050354 | -0.1236 | 122.9507 | 122.7997 | 0.027466 | 123.1476 | 123.0423 | 0.24261 | -0.054931 | 120.2316 | 120.1584 | -2.7008 | 120.4468 | 120.3964 | 0.23804 | -2.7695 | 123.1659 | 123.0835 | 123.024 | -0.33874 | 120.4376 | 120.369 | 120.4559 | -2.98
741.6875 | 123.3994 | -120.3918 | 2.7878 | -0.11832 | 0.059982 | 0.0048081 | 0.031217 | -0.01073 | -0.0069216 | 0.027457 | -0.26494 | 0.01288 | -0.0084976 | 0.00056082 | -0.0034972 | 0.037699 | 2.7191 | 2.7832 | 2.6642 | 2.6871 | 2.8061 | 2.6047 | 2.4536 | 0.17395 | 0.18768 | 0.10986 | 0.15106 | 0.082397 | -0.054932 | -0.12817 | 122.9965 | 122.8455 | 0.01831 | 123.175 | 123.0789 | 0.23346 | -0.068665 | 120.3369 | 120.2637 | -2.6367 | 120.5658 | 120.5017 | 0.23804 | -2.7054 | 123.1979 | 123.111 | 123.056 | -0.33417 | 120.5429 | 120.4742 | 120.5795 | -2.916
742.6875 | 123.3994 | -120.4056 | 2.742 | -0.13358 | 0.06105 | 0.0026721 | 0.021604 | -0.01073 | -0.0090576 | 0.025321 | -0.20391 | 0.01288 | -0.011702 | 0.0048338 | -0.0056342 | 0.038767 | 2.6642 | 2.742 | 2.623 | 2.655 | 2.7649 | 2.5681 | 2.4353 | 0.16937 | 0.19684 | 0.12817 | 0.14648 | 0.091553 | -0.059509 | -0.12817 | 122.9736 | 122.8409 | 0.022889 | 123.1476 | 123.0606 | 0.21973 | -0.077819 | 120.3461 | 120.2774 | -2.5955 | 120.575 | 120.5338 | 0.25635 | -2.6505 | 123.1705 | 123.0698 | 123.0286 | -0.3067 | 120.5521 | 120.4971 | 120.6024 | -2.8702
743.6875 | 123.3719 | -120.4651 | 2.7145 | -0.072545 | 0.076004 | 0.0090801 | 0.025877 | -0.019275 | 0.0016234 | 0.027457 | -0.20391 | 0.01288 | -0.013838 | 0.0037648 | -0.012042 | 0.035562 | 2.5635 | 2.6413 | 2.5314 | 2.5726 | 2.71 | 2.4811 | 2.3529 | 0.086975 | 0.11902 | 0.064087 | 0.14648 | 0.082397 | -0.073242 | -0.11444 | 122.9462 | 122.818 | -0.004578 | 123.1064 | 123.0377 | 0.21973 | -0.15106 | 120.3918 | 120.3506 | -2.5681 | 120.5521 | 120.5292 | 0.17853 | -2.6321 | 123.175 | 123.0286 | 122.9965 | -0.36163 | 120.6116 | 120.5475 | 120.5841 | -2.829
744.6875 | 123.4039 | -120.4971 | 2.655 | -0.30143 | 0.066391 | 0.0037401 | 0.010923 | -0.011798 | -0.0047856 | 0.016776 | -0.60064 | 0.0086078 | -0.017042 | -0.011188 | 0.0039788 | 0.046244 | 2.6047 | 2.6779 | 2.5589 | 2.5772 | 2.6825 | 2.4811 | 2.3254 | 0.11902 | 0.17395 | 0.16479 | 0.14191 | 0.09613 | -0.059509 | -0.12817 | 122.9782 | 122.8226 | 0.027466 | 123.175 | 123.0743 | 0.25177 | -0.050354 | 120.4376 | 120.369 | -2.5131 | 120.6161 | 120.6619 | 0.29297 | -2.5589 | 123.1796 | 123.1018 | 123.056 | -0.32959 | 120.639 | 120.5933 | 120.6711 | -2.7832
745.6875 | 123.4085 | -120.5566 | 2.5909 | -0.33194 | 0.073868 | 0.017625 | 0.0184 | -0.012866 | -0.0026496 | 0.031729 | -0.5396 | 0.0032668 | -0.026655 | -0.0079842 | 0.0039788 | 0.029154 | 2.5589 | 2.6367 | 2.4948 | 2.5085 | 2.623 | 2.4353 | 2.2842 | 0.11902 | 0.19226 | 0.086975 | 0.15564 | 0.07782 | -0.050354 | -0.1236 | 122.9919 | 122.8409 | 0.032044 | 123.1934 | 123.0652 | 0.2243 | -0.032043 | 120.5063 | 120.433 | -2.4353 | 120.6757 | 120.6436 | 0.21057 | -2.5131 | 123.1796 | 123.1155 | 123.0515 | -0.3067 | 120.7123 | 120.6345 | 120.7489 | -2.7145
746.6875 | 123.3994 | -120.5475 | 2.6459 | -0.30143 | 0.063186 | 0.011217 | 0.016264 | -0.0011172 | 0.0016234 | 0.015708 | -0.44805 | 0.0043348 | -0.0095656 | 0.0016288 | -0.012042 | 0.039835 | 2.5635 | 2.6459 | 2.5269 | 2.536 | 2.6459 | 2.4536 | 2.3117 | 0.1236 | 0.16479 | 0.10529 | 0.15564 | 0.086975 | -0.059509 | -0.10986 | 123.0011 | 122.8592 | 0 | 123.1934 | 123.0835 | 0.2243 | -0.082397 | 120.488 | 120.4376 | -2.4902 | 120.6711 | 120.6528 | 0.21515 | -2.5589 | 123.1934 | 123.111 | 123.0743 | -0.33417 | 120.7031 | 120.6345 | 120.7123 | -2.7557
747.6875 | 123.2941 | -120.639 | 2.5314 | -0.3472 | 0.046097 | 0.0080121 | 0.030149 | -0.0053902 | -0.010127 | 0.032797 | -0.49383 | -0.0031412 | -0.01277 | 0.00056082 | 0.0018428 | 0.033426 | 2.4765 | 2.5589 | 2.4445 | 2.4536 | 2.5543 | 2.3438 | 2.2064 | 0.1236 | 0.17395 | 0.10071 | 0.14648 | 0.07782 | -0.059509 | -0.13275 | 122.9828 | 122.8455 | 0.022888 | 123.1979 | 123.0927 | 0.24719 | -0.054932 | 120.5795 | 120.5063 | -2.3849 | 120.7626 | 120.7397 | 0.23346 | -2.4536 | 123.1934 | 123.1155 | 123.0835 | -0.32501 | 120.7855 | 120.7169 | 120.813 | -2.6642
748.6875 | 123.4085 | -120.607 | 2.5314 | -0.37772 | 0.065323 | 0.0090801 | 0.0066513 | -0.0021852 | -0.0079896 | 0.024253 | -0.46331 | 0.0075398 | -0.015974 | -0.013324 | 0.0029108 | 0.051584 | 2.4948 | 2.5818 | 2.4628 | 2.4628 | 2.5452 | 2.3529 | 2.2293 | 0.12817 | 0.17853 | 0.10986 | 0.16022 | 0.09613 | -0.041199 | -0.13275 | 122.9599 | 122.8363 | 0.013733 | 123.1888 | 123.0698 | 0.23346 | -0.036621 | 120.5658 | 120.4742 | -2.3712 | 120.7352 | 120.7169 | 0.24261 | -2.4353 | 123.1522 | 123.1018 | 123.0698 | -0.30212 | 120.7672 | 120.7031 | 120.7855 | -2.6642
749.6875 | 123.3948 | -120.6711 | 2.4765 | -0.1641 | 0.059982 | -0.0069409 | 0.021604 | -0.0064582 | -0.0058536 | 0.033866 | -0.24969 | 0.0075398 | -0.023451 | 0.015515 | -0.0056342 | 0.035562 | 2.3849 | 2.4811 | 2.3621 | 2.3849 | 2.5223 | 2.3117 | 2.1606 | 0.11902 | 0.15106 | 0.09613 | 0.16479 | 0.10986 | -0.041199 | -0.10071 | 122.9828 | 122.8317 | 0.045777 | 123.1522 | 123.056 | 0.2243 | -0.091552 | 120.6299 | 120.5704 | -2.3117 | 120.7901 | 120.7672 | 0.19684 | -2.3666 | 123.1934 | 123.056 | 123.0331 | -0.31586 | 120.8359 | 120.7809 | 120.8221 | -2.5772
750.6875 | 123.4177 | -120.7077 | 2.4719 | -0.54557 | 0.050369 | 0.0090801 | 0.014128 | -0.024616 | -0.0058536 | 0.029593 | -0.5396 | 0.010744 | -0.017042 | -0.0058482 | -0.0024292 | 0.034494 | 2.4078 | 2.4719 | 2.3621 | 2.3712 | 2.4719 | 2.2842 | 2.1194 | 0.12817 | 0.16937 | 0.10529 | 0.14191 | 0.086975 | -0.045776 | -0.11902 | 122.9919 | 122.8271 | 0 | 123.1796 | 123.0789 | 0.25177 | -0.064087 | 120.6619 | 120.5887 | -2.33 | 120.8359 | 120.813 | 0.22431 | -2.3849 | 123.1796 | 123.1155 | 123.0698 | -0.35248 | 120.8496 | 120.7947 | 120.8771 | -2.5909
751.6875 | 123.3948 | -120.7214 | 2.4445 | -0.46927 | 0.085617 | 0.016557 | 0.019468 | -0.0032532 | 0.010168 | 0.03707 | -0.34124 | 0.015017 | -0.010634 | -0.0037112 | -0.0077702 | 0.037699 | 2.2064 | 2.4536 | 2.3071 | 2.3346 | 2.4399 | 2.2522 | 2.1057 | 0.1236 | 0.16479 | 0.082397 | 0.16479 | 0.091553 | -0.064087 | -0.13275 | 122.9736 | 122.8271 | -0.004578 | 123.175 | 123.056 | 0.22888 | -0.23804 | 120.6573 | 120.5887 | -2.2797 | 120.845 | 120.8038 | 0.21515 | -2.3529 | 123.1613 | 122.9279 | 123.0286 | -0.33874 | 120.8862 | 120.813 | 120.8862 | -2.5772
752.6875 | 123.3124 | -120.8084 | 2.4353 | -0.40824 | 0.10271 | 0.0080121 | 0.017332 | -0.0011172 | 0.0037594 | 0.031729 | -0.70745 | 0.018221 | -0.014906 | 0.0016288 | 0.0071838 | 0.033426 | 2.2842 | 2.3621 | 2.2293 | 2.2797 | 2.417 | 2.2064 | 2.0645 | 0.050354 | 0.091553 | 0.022888 | 0.20142 | 0.12817 | -0.082397 | -0.13275 | 123.0148 | 122.8729 | -0.018311 | 123.1705 | 123.0881 | 0.21515 | -0.15106 | 120.726 | 120.6757 | -2.2339 | 120.8588 | 120.8313 | 0.15564 | -2.3071 | 123.2254 | 123.0927 | 123.0377 | -0.37079 | 121.0098 | 120.9366 | 120.9 | -2.5681
753.6875 | 123.3902 | -120.8405 | 2.3712 | -0.37772 | 0.067459 | 0.0048081 | 0.017332 | 0.0042228 | -0.0090576 | 0.018912 | -0.020803 | 0.023562 | -0.021315 | 0.0048338 | 0.0071838 | 0.043039 | 2.2568 | 2.3758 | 2.1469 | 2.2202 | 2.3666 | 2.1515 | 1.9958 | 0.10529 | 0.17853 | 0.10071 | 0.14648 | 0.09613 | -0.054932 | -0.11444 | 122.9919 | 122.8363 | -0.004578 | 123.2162 | 123.0606 | 0.2243 | -0.11444 | 120.7855 | 120.726 | -2.2247 | 120.9457 | 120.9412 | 0.21515 | -2.2751 | 123.2071 | 123.0972 | 122.9874 | -0.37537 | 120.9869 | 120.9366 | 121.019 | -2.4857
754.6875 | 123.381 | -120.8359 | 2.3483 | -0.31669 | 0.079208 | 0.010148 | 0.0184 | -0.011798 | -0.00051261 | 0.028525 | 4.4348 | 0.01288 | -0.024519 | 0.01231 | -0.0056342 | 0.034494 | 2.243 | 2.33 | 2.2293 | 2.2476 | 2.3575 | 2.1561 | 2.0187 | 0.11902 | 0.13275 | 0.09613 | 0.14191 | 0.086975 | -0.068665 | -0.12817 | 122.9919 | 122.8546 | 0.009155 | 123.1659 | 123.0835 | 0.22888 | -0.10529 | 120.7672 | 120.7077 | -2.2064 | 120.9549 | 120.932 | 0.2243 | -2.2614 | 123.1934 | 123.0789 | 123.0652 | -0.32959 | 120.9778 | 120.9229 | 120.9686 | -2.4765
755.6875 | 123.3948 | -120.8633 | 2.2797 | -0.37772 | 0.082412 | 0.0080121 | 0.016264 | -0.01073 | 0.0080314 | 0.029593 | -0.5396 | -0.0063462 | -0.017042 | 0.013378 | 0.0061158 | 0.047312 | 2.1881 | 2.2888 | 2.179 | 2.1835 | 2.2751 | 2.0966 | 1.9501 | 0.16479 | 0.10529 | 0.091553 | 0.16937 | 0.064087 | -0.082397 | -0.15106 | 122.9599 | 122.8134 | -0.004578 | 123.1522 | 123.0469 | 0.23346 | -0.091553 | 120.7809 | 120.7123 | -2.1103 | 121.0281 | 120.9549 | 0.24261 | -2.2156 | 123.1384 | 123.0515 | 123.0423 | -0.32959 | 121.0327 | 120.9274 | 120.9686 | -2.4307
756.6875 | 123.4177 | -120.8679 | 2.2842 | -0.33194 | 0.069595 | 0.0090801 | 0.021604 | -0.021411 | -0.0047856 | 0.027457 | -0.2802 | 0.0032668 | -0.020247 | 0.0026968 | -0.0056342 | 0.049448 | 2.1973 | 2.2842 | 2.1652 | 2.1881 | 2.3117 | 2.124 | 1.9638 | 0.16937 | 0.16937 | 0.12817 | 0.15564 | 0.073242 | -0.064087 | -0.1236 | 122.9919 | 122.8317 | 0.027466 | 123.1522 | 123.056 | 0.2243 | -0.086975 | 120.8038 | 120.7443 | -2.1286 | 121.0373 | 120.9961 | 0.25177 | -2.211 | 123.1796 | 123.0652 | 123.0331 | -0.32044 | 121.0236 | 120.9412 | 121.0373 | -2.4078
757.6875 | 123.3994 | -120.9412 | 2.2385 | -0.087804 | 0.052505 | 0.012285 | 0.0077193 | -0.0043222 | -0.0069216 | 0.024253 | -0.32598 | 0.013948 | -0.024519 | -0.0015752 | -0.0034972 | 0.041971 | 2.179 | 2.2385 | 2.1286 | 2.1378 | 2.2705 | 2.0691 | 1.9226 | 0.14191 | 0.15564 | 0.1236 | 0.16479 | 0.10986 | -0.050354 | -0.11444 | 123.0103 | 122.8638 | 0.032044 | 123.1796 | 123.0789 | 0.21515 | -0.059509 | 120.8908 | 120.8267 | -2.0737 | 121.0831 | 121.0648 | 0.23804 | -2.1286 | 123.2117 | 123.1201 | 123.0698 | -0.31586 | 121.106 | 121.051 | 121.0968 | -2.3529
758.6875 | 123.3719 | -120.9915 | 2.2247 | 0.11056 | 0.070663 | 0.0058761 | 0.026945 | -0.015003 | -0.0015816 | 0.025321 | -0.55486 | 0.011812 | -0.015974 | -0.00050718 | 0.0039788 | 0.034494 | 2.1194 | 2.1973 | 2.0874 | 2.1057 | 2.2064 | 2.0233 | 1.8677 | 0.086975 | 0.14191 | 0.059509 | 0.16479 | 0.082397 | -0.082397 | -0.1236 | 123.0148 | 122.8592 | -0.01831 | 123.1888 | 123.0972 | 0.23804 | -0.10528 | 120.9091 | 120.8679 | -2.0599 | 121.0785 | 121.051 | 0.1831 | -2.1423 | 123.1979 | 123.111 | 123.0789 | -0.35705 | 121.1563 | 121.0739 | 121.1334 | -2.3483
759.6875 | 123.3627 | -120.9961 | 2.2018 | 0.62936 | 0.063186 | -0.00053286 | 0.0087873 | -0.0032532 | -0.0037176 | 0.024253 | -0.49383 | 0.020357 | -0.01277 | 0.0037648 | -0.0002932 | 0.023813 | 2.1011 | 2.1973 | 2.0737 | 2.0966 | 2.1973 | 2.0142 | 1.8539 | 0.11444 | 0.16022 | 0.064087 | 0.15106 | 0.10529 | -0.068665 | -0.11902 | 123.0103 | 122.85 | -0.004577 | 123.1934 | 123.0927 | 0.24262 | -0.10071 | 120.9274 | 120.8771 | -2.0508 | 121.1105 | 121.0602 | 0.18311 | -2.0966 | 123.1934 | 123.0972 | 123.0698 | -0.3479 | 121.1472 | 121.1014 | 121.1563 | -2.3209
760.6875 | 123.3719 | -121.0373 | 2.1378 | 2.9945 | 0.065323 | 0.017625 | 0.024809 | -0.0021852 | -0.00051261 | 0.027457 | -0.55486 | 0.013948 | -0.040541 | -0.014393 | 0.0029108 | 0.032358 | 2.037 | 2.1378 | 2.0187 | 2.0279 | 2.1515 | 1.9592 | 1.799 | 0.10529 | 0.15106 | 0.086975 | 0.14648 | 0.082397 | -0.064087 | -0.11444 | 122.9965 | 122.8363 | 0.013733 | 123.175 | 123.0652 | 0.22888 | -0.10071 | 120.9732 | 120.9229 | -1.9913 | 121.1426 | 121.1243 | 0.20142 | -2.0554 | 123.1888 | 123.0743 | 123.056 | -0.33875 | 121.1838 | 121.1197 | 121.1884 | -2.2522
761.6875 | 123.3719 | -121.0831 | 2.1286 | -3.933 | 0.049301 | -0.0037369 | 0.026945 | -0.018207 | 0.0026914 | 0.032797 | -0.46331 | 0.015017 | -0.0095656 | 0.0016288 | 0.012524 | 0.027017 | 2.005 | 2.0691 | 1.9821 | 2.0233 | 2.1011 | 1.9272 | 1.7944 | 0.10986 | 0.16022 | 0.07782 | 0.15564 | 0.07782 | -0.082397 | -0.1236 | 123.0103 | 122.8775 | -0.027466 | 123.1522 | 123.1064 | 0.22888 | -0.1236 | 121.0007 | 120.9595 | -1.973 | 121.1929 | 121.1609 | 0.20142 | -2.0508 | 123.1842 | 123.0881 | 123.0652 | -0.33417 | 121.2387 | 121.1609 | 121.2433 | -2.2522
762.6875 | 123.3856 | -121.0785 | 2.1286 | -7.9003 | 0.070663 | -0.018691 | 0.011991 | -0.0064582 | -0.0069216 | 0.036002 | -0.41753 | 0.013948 | -0.028792 | -0.014393 | 0.0050478 | 0.037699 | 1.973 | 2.0645 | 1.9638 | 1.9913 | 2.0966 | 1.9135 | 1.7715 | 0.10071 | 0.16479 | 0.082397 | 0.17853 | 0.10986 | -0.064087 | -0.11902 | 122.9919 | 122.85 | -0.032043 | 123.143 | 123.0698 | 0.21973 | -0.15564 | 121.0144 | 120.9595 | -1.9501 | 121.1792 | 121.1609 | 0.20142 | -2.0187 | 123.175 | 123.0515 | 123.0423 | -0.35706 | 121.257 | 121.1884 | 121.2433 | -2.2476
763.7031 | 123.317 | -121.1288 | 2.1515 | -0.25565 | 0.10271 | -0.0026689 | 0.053648 | 0.0031548 | 0.027258 | 0.033866 | -0.52434 | 0.027834 | -0.0042246 | 0.0016288 | 0.010388 | 0.03663 | 1.9867 | 1.9775 | 1.8768 | 1.9318 | 2.1057 | 1.8539 | 1.7166 | 0.07782 | 0.1236 | 0.07782 | 0.19684 | 0.1236 | -0.059509 | -0.13275 | 122.9828 | 122.8455 | -0.045776 | 123.1064 | 123.0606 | 0.21515 | -0.1648 | 121.0693 | 120.9961 | -1.9547 | 121.2067 | 121.2067 | 0.21057 | -2.0279 | 123.2346 | 123.1155 | 123.0057 | -0.43488 | 121.3257 | 121.2524 | 121.2524 | -2.2842
764.6875 | 123.3994 | -121.1243 | 2.0416 | -0.026769 | 0.068527 | 0.0069441 | 0.021604 | -0.026752 | -0.020808 | 0.027457 | -0.41753 | 0.015017 | -0.017042 | 0.0037648 | -0.010974 | 0.037699 | 1.9455 | 2.0599 | 1.9318 | 1.9501 | 2.0554 | 1.8539 | 1.712 | 0.10986 | 0.19226 | 0.10529 | 0.16022 | 0.086975 | -0.054932 | -0.10986 | 122.9782 | 122.8363 | 0.013733 | 123.1842 | 123.0743 | 0.23804 | -0.09613 | 121.0693 | 121.0144 | -1.8814 | 121.2341 | 121.2296 | 0.21515 | -1.9547 | 123.1796 | 123.0698 | 123.056 | -0.32959 | 121.2845 | 121.2112 | 121.3165 | -2.1515
765.6875 | 123.3307 | -121.225 | 2.037 | -0.48453 | 0.085617 | 0.010148 | 0.0087873 | -0.011798 | 0.0016234 | 0.03707 | -0.6159 | 0.013948 | -0.01277 | -0.0015752 | -0.0013612 | 0.034494 | 1.8814 | 1.9501 | 1.8356 | 1.8906 | 2.0187 | 1.8127 | 1.6571 | 0.050354 | 0.091553 | 0.018311 | 0.19684 | 0.10986 | -0.073242 | -0.15564 | 123.0377 | 122.8821 | -0.01831 | 123.175 | 123.1155 | 0.23346 | -0.15564 | 121.1517 | 121.0693 | -1.8402 | 121.2753 | 121.2433 | 0.17395 | -1.9272 | 123.2437 | 123.1064 | 123.0606 | -0.37994 | 121.4218 | 121.3348 | 121.3165 | -2.1927
766.6875 | 123.317 | -121.225 | 1.9958 | -0.46927 | 0.077072 | 0.0090801 | 0.014128 | -0.0032532 | 0.0016234 | 0.017844 | -0.63115 | 0.019289 | 0.0011164 | 0.0026968 | 0.0029108 | 0.03129 | 1.8494 | 1.9318 | 1.8082 | 1.8539 | 2.0004 | 1.7807 | 1.6388 | 0.054932 | 0.09613 | 0.022888 | 0.17853 | 0.11444 | -0.064087 | -0.13733 | 123.0057 | 122.8638 | 0.004577 | 123.1567 | 123.0789 | 0.21515 | -0.14648 | 121.1609 | 121.0876 | -1.8173 | 121.2799 | 121.2479 | 0.16022 | -1.8814 | 123.2254 | 123.0743 | 123.0331 | -0.35706 | 121.4035 | 121.3394 | 121.3211 | -2.1332
767.6875 | 123.3261 | -121.2936 | 1.9684 | -0.43876 | 0.081344 | 0.0048081 | 0.024809 | -0.025684 | -0.0015816 | 0.026389 | -0.63115 | 0.018221 | -0.025587 | 0.01231 | -0.0002932 | 0.039835 | 1.799 | 1.9043 | 1.7715 | 1.8265 | 1.9547 | 1.7441 | 1.6022 | 0.054932 | 0.10529 | 0.022888 | 0.19226 | 0.10986 | -0.082397 | -0.13733 | 123.0377 | 122.8958 | -0.013733 | 123.1979 | 123.1201 | 0.2243 | -0.16937 | 121.2112 | 121.1563 | -1.7761 | 121.3486 | 121.3165 | 0.16022 | -1.8585 | 123.2483 | 123.0927 | 123.0652 | -0.36621 | 121.4859 | 121.4035 | 121.3989 | -2.1057
768.7031 | 123.4039 | -121.3028 | 1.8906 | 0.36996 | 0.080276 | -0.0058729 | 0.019468 | -0.0064582 | 0.012304 | 0.033866 | -0.17339 | 0.023562 | -0.0063606 | 0.0026968 | 0.0039788 | 0.029154 | 1.7715 | 1.8219 | 1.7303 | 1.7715 | 1.8951 | 1.7166 | 1.5564 | 0.10071 | 0.082397 | 0.054932 | 0.13275 | 0.07782 | -0.064087 | -0.13275 | 123.0194 | 122.8592 | 0.004578 | 123.1247 | 123.0743 | 0.21515 | -0.11902 | 121.2387 | 121.17 | -1.7578 | 121.4035 | 121.3577 | 0.18768 | -1.8127 | 123.1979 | 123.0743 | 123.0331 | -0.33417 | 121.4355 | 121.3806 | 121.3852 | -2.0233
769.6875 | 123.3215 | -121.3577 | 1.8768 | -0.37772 | 0.07814 | 0.0090801 | 0.023741 | -0.0096622 | -0.016535 | 0.026389 | -0.63115 | 0.0096758 | -0.01277 | -0.0047802 | 0.0029108 | 0.03129 | 1.7441 | 1.7944 | 1.7075 | 1.7487 | 1.8585 | 1.6754 | 1.5335 | 0.064087 | 0.10986 | 0.032043 | 0.17853 | 0.11444 | -0.073242 | -0.12817 | 123.0331 | 122.8912 | -0.01831 | 123.1522 | 123.1064 | 0.21515 | -0.13275 | 121.2845 | 121.2296 | -1.6983 | 121.4218 | 121.3898 | 0.16022 | -1.7624 | 123.2162 | 123.1018 | 123.0652 | -0.34332 | 121.5363 | 121.4722 | 121.4676 | -2.005
770.6875 | 123.3444 | -121.3852 | 1.8631 | -0.36246 | 0.053573 | 0.0048081 | 0.013059 | -0.0011172 | -0.0090576 | 0.015708 | -0.6159 | 0.016085 | -0.02986 | -0.00050718 | -0.0024292 | 0.034494 | 1.7029 | 1.7944 | 1.6663 | 1.7166 | 1.8311 | 1.6388 | 1.4832 | 0.064087 | 0.10071 | 0.032043 | 0.16937 | 0.09613 | -0.07782 | -0.1236 | 123.024 | 122.8683 | -0.032043 | 123.1796 | 123.1018 | 0.23346 | -0.16022 | 121.3074 | 121.2616 | -1.6937 | 121.4493 | 121.4172 | 0.15564 | -1.767 | 123.2162 | 123.0881 | 123.0515 | -0.37994 | 121.5546 | 121.4813 | 121.4859 | -1.9867
771.6875 | 123.4085 | -121.3852 | 1.7853 | -0.33194 | 0.079208 | 0.012285 | 0.024809 | 0.0042228 | -0.016535 | 0.025321 | -0.95159 | 0.02463 | -0.020247 | 0.0091058 | -0.0024292 | 0.044107 | 1.6754 | 1.7853 | 1.6708 | 1.6983 | 1.7853 | 1.6022 | 1.4648 | 0.068665 | 0.1831 | 0.059509 | 0.14191 | 0.091553 | -0.068665 | -0.14191 | 122.9874 | 122.85 | 0 | 123.1705 | 123.0835 | 0.23346 | -0.10986 | 121.3165 | 121.2433 | -1.6434 | 121.4539 | 121.4447 | 0.20142 | -1.6937 | 123.1705 | 123.0606 | 123.056 | -0.32043 | 121.5271 | 121.4767 | 121.5683 | -1.9272
772.6875 | 123.2758 | -121.4859 | 1.8127 | -0.22513 | 0.084549 | 0.017625 | 0.032286 | -0.0032532 | 0.0016234 | 0.024253 | -0.57012 | 0.021425 | -0.017042 | -0.0037112 | -0.0077702 | 0.041971 | 1.6388 | 1.6159 | 1.5244 | 1.6113 | 1.8265 | 1.561 | 1.4099 | 0.004578 | 0.041199 | -0.032043 | 0.20599 | 0.11902 | -0.091553 | -0.16022 | 123.0469 | 122.8958 | 0.013733 | 123.1018 | 123.0972 | 0.20142 | -0.17395 | 121.3943 | 121.3257 | -1.6067 | 121.4905 | 121.4539 | 0.12817 | -1.6937 | 123.3124 | 123.1247 | 123.0103 | -0.40283 | 121.6919 | 121.6049 | 121.5271 | -1.973
773.7031 | 123.2803 | -121.4813 | 1.7761 | 0.12582 | 0.10698 | 0.0090801 | 0.0184 | -0.0075262 | 0.029394 | 0.026389 | -0.31072 | 0.025698 | 0.0075244 | 0.0048338 | 0.017865 | 0.030222 | 1.5793 | 1.6022 | 1.5015 | 1.5884 | 1.7899 | 1.5335 | 1.3916 | -0.022888 | -0.013733 | -0.082397 | 0.16937 | 0.10529 | -0.10529 | -0.16479 | 123.0148 | 122.8729 | 0.013733 | 123.0835 | 123.0698 | 0.19684 | -0.19684 | 121.376 | 121.3165 | -1.6067 | 121.4584 | 121.3989 | 0.082398 | -1.6708 | 123.2712 | 123.0606 | 122.9828 | -0.38452 | 121.6507 | 121.5866 | 121.4676 | -1.9409
774.6875 | 123.2803 | -121.5179 | 1.7624 | -0.13358 | 0.083481 | 0.010148 | 0.023741 | 0.0042228 | -0.0047856 | 0.025321 | -0.63115 | 0.028902 | -0.0095656 | -0.0037112 | 0.0007748 | 0.041971 | 1.5427 | 1.5839 | 1.4832 | 1.5472 | 1.7761 | 1.5152 | 1.3596 | 0.004578 | 0.045776 | -0.022888 | 0.1831 | 0.13733 | -0.091553 | -0.15564 | 123.0331 | 122.8775 | 0.013733 | 123.1018 | 123.0652 | 0.18768 | -0.21973 | 121.4264 | 121.3623 | -1.5793 | 121.5225 | 121.4951 | 0.13275 | -1.6251 | 123.2941 | 123.0606 | 123.0011 | -0.40283 | 121.701 | 121.6553 | 121.5637 | -1.918
775.6875 | 123.2895 | -121.5546 | 1.7578 | -0.88126 | 0.096298 | 0.013353 | 0.019468 | -0.0043222 | 0.0026914 | 0.033866 | -0.60064 | 0.020357 | -0.020247 | 0.0059018 | 0.0018428 | 0.037699 | 1.4877 | 1.5518 | 1.4465 | 1.5106 | 1.7303 | 1.4694 | 1.3321 | -0.004578 | 0.041199 | -0.032043 | 0.19684 | 0.15106 | -0.10529 | -0.17395 | 123.024 | 122.8867 | -0.027465 | 123.1064 | 123.0652 | 0.17853 | -0.27008 | 121.4493 | 121.3806 | -1.561 | 121.55 | 121.5225 | 0.14191 | -1.6067 | 123.2849 | 123.0423 | 123.0011 | -0.42572 | 121.7514 | 121.7056 | 121.5958 | -1.9318
776.6875 | 123.2849 | -121.6003 | 1.7212 | -0.48453 | 0.069595 | 0.02083 | 0.021604 | -0.013935 | -0.0058536 | 0.028525 | -0.70745 | 0.021425 | -0.024519 | 0.0059018 | 0.0029108 | 0.038767 | 1.4648 | 1.5289 | 1.4236 | 1.4877 | 1.7166 | 1.4557 | 1.3138 | -0.004578 | 0.036621 | -0.041199 | 0.20142 | 0.13275 | -0.09613 | -0.16479 | 123.056 | 122.9141 | -0.004577 | 123.1293 | 123.0881 | 0.17395 | -0.25635 | 121.5042 | 121.4355 | -1.5198 | 121.5958 | 121.5591 | 0.1236 | -1.5884 | 123.317 | 123.0652 | 123.024 | -0.40741 | 121.8018 | 121.7331 | 121.637 | -1.886
777.6875 | 123.3078 | -121.5775 | 1.68 | -0.48453 | 0.064255 | 0.016557 | 0.025877 | -0.011798 | -0.012263 | 0.011435 | -0.5396 | 0.018221 | -0.011702 | -0.0079842 | -0.0045652 | 0.032358 | 1.4923 | 1.5793 | 1.4603 | 1.5106 | 1.6708 | 1.4648 | 1.3 | 0.009155 | 0.073242 | 0.009155 | 0.17853 | 0.11444 | -0.10529 | -0.14648 | 123.0423 | 122.8775 | -0.009156 | 123.1567 | 123.0881 | 0.21057 | -0.18768 | 121.4722 | 121.431 | -1.5015 | 121.5866 | 121.5866 | 0.15564 | -1.5656 | 123.2483 | 123.0698 | 123.0377 | -0.37994 | 121.756 | 121.6919 | 121.6507 | -1.8265
778.7031 | 123.4131 | -121.5591 | 1.6479 | 0.78195 | 0.077072 | -0.0048049 | 0.0087873 | -0.01073 | -0.00051261 | 0.038138 | 0.17756 | 0.015017 | -0.0095656 | -0.0037112 | 0.011456 | 0.040903 | 1.5244 | 1.593 | 1.4969 | 1.5289 | 1.6434 | 1.4694 | 1.3367 | 0.09613 | 0.1236 | 0.059509 | 0.14191 | 0.073242 | -0.054932 | -0.1236 | 123.0286 | 122.8958 | -0.004577 | 123.1522 | 123.0881 | 0.19226 | -0.1236 | 121.5042 | 121.4355 | -1.506 | 121.6553 | 121.6187 | 0.1831 | -1.5747 | 123.2025 | 123.0835 | 123.056 | -0.31128 | 121.7011 | 121.6324 | 121.6827 | -1.7715
779.6875 | 123.3124 | -121.6507 | 1.6388 | -0.36246 | 0.087753 | 0.0080121 | 0.021604 | -0.0096622 | 0.00055539 | 0.032797 | -0.55486 | 0.023562 | -0.017042 | 0.00056082 | 0.010388 | 0.037699 | 1.4328 | 1.442 | 1.355 | 1.4328 | 1.6525 | 1.3733 | 1.2543 | -0.004578 | 0.032043 | -0.041199 | 0.19226 | 0.13275 | -0.068665 | -0.14648 | 123.024 | 122.905 | 0.013733 | 123.0927 | 123.0835 | 0.17853 | -0.20599 | 121.582 | 121.5042 | -1.4465 | 121.6461 | 121.6095 | 0.10529 | -1.506 | 123.3032 | 123.0835 | 123.0057 | -0.38452 | 121.843 | 121.7834 | 121.6827 | -1.7853
780.6875 | 123.3261 | -121.6461 | 1.6113 | -0.39298 | 0.083481 | 0.0048081 | 0.023741 | -0.0075262 | 0.0058954 | 0.023184 | -0.60064 | 0.017153 | -0.0063606 | 0.01231 | -0.0034972 | 0.039835 | 1.4145 | 1.4282 | 1.3275 | 1.4099 | 1.6251 | 1.3641 | 1.2177 | 0 | 0.045776 | -0.018311 | 0.18768 | 0.13275 | -0.082397 | -0.15106 | 123.0103 | 122.8638 | 0.013733 | 123.0743 | 123.056 | 0.19226 | -0.19684 | 121.5637 | 121.4951 | -1.4236 | 121.6461 | 121.6278 | 0.13275 | -1.4786 | 123.2712 | 123.0606 | 122.9736 | -0.39368 | 121.8338 | 121.7789 | 121.6919 | -1.7624
781.6875 | 123.3444 | -121.6827 | 1.5884 | -0.40824 | 0.07814 | 0.0026721 | 0.044035 | -0.0075262 | 0.0016234 | 0.031729 | -0.69219 | 0.010744 | -0.024519 | 0.00056082 | 0.0061158 | 0.025949 | 1.3733 | 1.4099 | 1.2909 | 1.3916 | 1.6022 | 1.3412 | 1.2039 | 0.013733 | 0.050354 | -0.018311 | 0.17853 | 0.10529 | -0.09613 | -0.15106 | 123.024 | 122.8867 | 0.013733 | 123.0927 | 123.0743 | 0.18768 | -0.21515 | 121.5866 | 121.5317 | -1.4099 | 121.6965 | 121.6644 | 0.13275 | -1.4832 | 123.2849 | 123.056 | 122.9736 | -0.38452 | 121.8613 | 121.788 | 121.7331 | -1.7395
782.6875 | 123.3536 | -121.7239 | 1.5656 | -0.3472 | 0.12407 | 0.0048081 | 0.023741 | 0.0042228 | 0.013372 | 0.030661 | -0.38701 | 0.019289 | -0.011702 | -0.0047802 | 0.010388 | 0.044107 | 1.3916 | 1.442 | 1.3412 | 1.3779 | 1.5656 | 1.3229 | 1.1948 | 0.045776 | 0.082397 | 0 | 0.1831 | 0.12817 | -0.082397 | -0.16937 | 123.0469 | 122.9187 | 0 | 123.1659 | 123.1018 | 0.18311 | -0.17395 | 121.6415 | 121.5546 | -1.3824 | 121.7697 | 121.7239 | 0.16937 | -1.4374 | 123.2895 | 123.1155 | 123.0652 | -0.37079 | 121.907 | 121.8521 | 121.8063 | -1.7349
783.6875 | 123.3902 | -121.7239 | 1.5335 | 0.41574 | 0.10057 | 0.0058761 | 0.028013 | -0.011798 | -0.031489 | 0.025321 | 0.29963 | 0.011812 | -0.01277 | 0.011242 | -0.0024292 | 0.040903 | 1.3824 | 1.4694 | 1.387 | 1.4053 | 1.5152 | 1.3229 | 1.2177 | 0.086975 | 0.11902 | 0.07782 | 0.15564 | 0.10071 | -0.064087 | -0.11902 | 123.0469 | 122.9416 | -0.01831 | 123.1934 | 123.1293 | 0.18768 | -0.15106 | 121.6599 | 121.6049 | -1.3779 | 121.8109 | 121.8018 | 0.19684 | -1.4328 | 123.2391 | 123.1064 | 123.111 | -0.31586 | 121.8796 | 121.8246 | 121.843 | -1.6525
784.6875 | 123.3124 | -121.7606 | 1.5335 | 1.3465 | 0.10271 | 0.0026721 | 0.031217 | -0.011798 | -0.0026496 | 0.030661 | -0.60064 | 0.026766 | -0.0042246 | 0.00056082 | -0.0024292 | 0.028086 | 1.3092 | 1.3229 | 1.2451 | 1.3275 | 1.5793 | 1.2863 | 1.1719 | -0.009155 | 0.027466 | -0.032043 | 0.21515 | 0.13733 | -0.10529 | -0.15564 | 123.0469 | 122.9324 | 0.045777 | 123.0835 | 123.0881 | 0.15564 | -0.2243 | 121.6553 | 121.6049 | -1.3184 | 121.7514 | 121.7285 | 0.1236 | -1.3962 | 123.3398 | 123.0698 | 123.0057 | -0.36163 | 121.9757 | 121.8979 | 121.788 | -1.6891
785.6875 | 123.3261 | -121.788 | 1.5106 | -0.30143 | 0.10698 | 0.012285 | 0.036558 | 0.010632 | 0.00055539 | 0.028525 | -0.38701 | 0.025698 | -0.018111 | 0.0037648 | 0.0071838 | 0.037699 | 1.3275 | 1.3458 | 1.2543 | 1.3367 | 1.5289 | 1.2772 | 1.1353 | 0.032043 | 0.054932 | 0.004578 | 0.1831 | 0.1236 | -0.091553 | -0.14191 | 123.0652 | 122.9233 | 0.018311 | 123.1339 | 123.1247 | 0.20142 | -0.18311 | 121.6965 | 121.6461 | -1.3275 | 121.8201 | 121.7926 | 0.14649 | -1.387 | 123.317 | 123.1155 | 123.0423 | -0.37537 | 121.9711 | 121.9116 | 121.843 | -1.6525
786.6875 | 123.3353 | -121.7789 | 1.4969 | -0.19462 | 0.1262 | -0.0026689 | 0.024809 | -0.016071 | 0.019781 | 0.026389 | -0.6159 | 0.026766 | 0.0011164 | -0.00050718 | 0.0018428 | 0.049448 | 1.3321 | 1.3504 | 1.2543 | 1.3138 | 1.5106 | 1.2634 | 1.1032 | 0.032043 | 0.073242 | 0 | 0.20142 | 0.14191 | -0.064087 | -0.11902 | 123.0423 | 122.8821 | 0.013733 | 123.1293 | 123.0927 | 0.21057 | -0.1648 | 121.7148 | 121.6599 | -1.2955 | 121.8109 | 121.7789 | 0.11902 | -1.355 | 123.2895 | 123.111 | 123.0331 | -0.39368 | 121.9803 | 121.9208 | 121.8521 | -1.6159
787.6875 | 123.3353 | -121.788 | 1.4465 | -0.14884 | 0.093094 | 0.0026721 | 0.025877 | -0.0053902 | 0.0037594 | 0.024253 | -0.63115 | 0.026766 | 0.0011164 | -0.0037112 | 0.0050478 | 0.035562 | 1.5289 | 1.506 | 1.2955 | 1.3367 | 1.5472 | 1.3092 | 1.1398 | 0.032043 | 0.054932 | -0.009155 | 0.18768 | 0.1236 | -0.073242 | -0.14191 | 123.0972 | 122.9279 | 0.10071 | 123.2941 | 123.1247 | 0.19684 | 0.082398 | 121.7148 | 121.6461 | -1.2589 | 121.8201 | 121.7789 | 0.13275 | -1.3229 | 123.3353 | 123.317 | 123.0835 | -0.3067 | 121.9757 | 121.9116 | 121.843 | -1.5884
788.6875 | 123.3078 | -121.8475 | 1.4511 | 1.6059 | 0.13261 | 0.015489 | 0.026945 | -0.0011172 | 0.0080314 | 0.031729 | -0.21917 | 0.021425 | -0.010634 | 0.019787 | 0.0061158 | 0.03663 | 1.3092 | 1.3458 | 1.2268 | 1.2955 | 1.5244 | 1.2817 | 1.1215 | 0.036621 | 0.050354 | -0.018311 | 0.1831 | 0.14191 | -0.10986 | -0.15564 | 123.1293 | 122.9691 | 0.073242 | 123.1934 | 123.143 | 0.17395 | -0.14191 | 121.7377 | 121.6919 | -1.268 | 121.8842 | 121.8292 | 0.13733 | -1.3092 | 123.3719 | 123.1567 | 123.0743 | -0.32959 | 122.0306 | 121.9894 | 121.8979 | -1.6068
789.6875 | 123.3215 | -121.8384 | 1.4694 | 0.23263 | 0.13048 | 0.0058761 | 0.022672 | -0.0064582 | -0.0026496 | 0.034934 | 0.14704 | 0.023562 | -0.013838 | 0.0016288 | 0.0007748 | 0.043039 | 1.1902 | 1.2039 | 1.1169 | 1.2039 | 1.4511 | 1.2039 | 1.0345 | -0.009155 | -0.1831 | -0.11444 | 0.17395 | 0.1236 | -0.082397 | -0.16022 | 123.0423 | 122.8729 | -0.01831 | 123.0423 | 123.0423 | 0.16937 | -0.27924 | 121.756 | 121.6782 | -1.2955 | 121.8292 | 121.7239 | 0.045776 | -1.3458 | 123.2895 | 123.0286 | 122.9553 | -0.43488 | 122.0123 | 121.962 | 121.6553 | -1.6296
790.6875 | 123.349 | -121.8155 | 1.5015 | -0.1641 | 0.12193 | 0.0069441 | 0.022672 | 0.0063598 | 0.0080314 | 0.03707 | -0.26494 | 0.023562 | -0.0031566 | -0.0015752 | 0.0007748 | 0.029154 | 1.2543 | 1.2543 | 1.1765 | 1.2405 | 1.4191 | 1.1948 | 1.0437 | 0.036621 | 0.10986 | 0.091553 | 0.20142 | 0.13733 | -0.054932 | -0.10529 | 123.0103 | 122.8592 | -0.082398 | 123.0698 | 123.056 | 0.19684 | -0.24719 | 121.7606 | 121.7102 | -1.3 | 121.8521 | 121.907 | 0.19684 | -1.3641 | 123.2346 | 123.0698 | 122.9919 | -0.45776 | 122.0169 | 121.9528 | 121.9254 | -1.6068
791.6875 | 123.3582 | -121.875 | 1.4328 | -0.1641 | 0.11232 | 0.0048081 | 0.025877 | -0.011798 | 0.0058954 | 0.031729 | -0.23443 | 0.016085 | 0.010729 | 0.01231 | 0.0050478 | 0.037699 | 1.2405 | 1.2543 | 1.1719 | 1.2268 | 1.4145 | 1.1581 | 1.03 | 0.07782 | 0.068665 | 0.022888 | 0.22888 | 0.17395 | -0.054932 | -0.11444 | 123.0331 | 122.905 | -0.01831 | 123.1293 | 123.1018 | 0.19684 | -0.19226 | 121.8201 | 121.7606 | -1.2039 | 121.9528 | 121.8979 | 0.13733 | -1.2589 | 123.2895 | 123.1155 | 123.0469 | -0.40283 | 122.1039 | 122.049 | 121.9437 | -1.5472
792.6875 | 123.2803 | -121.9162 | 1.3962 | 0.14108 | 0.10271 | -0.0026689 | 0.0066513 | -0.016071 | 0.01444 | 0.023184 | -0.020803 | 0.019289 | 0.0043204 | 0.0091058 | -0.0002932 | 0.043039 | 1.1307 | 1.1581 | 1.0666 | 1.1719 | 1.4191 | 1.1398 | 1.0208 | -0.027466 | -0.027466 | -0.054932 | 0.17395 | 0.14648 | -0.09613 | -0.16022 | 123.056 | 122.937 | 0.022888 | 123.0743 | 123.0881 | 0.15106 | -0.2655 | 121.8201 | 121.756 | -1.2222 | 121.8887 | 121.8613 | 0.10528 | -1.2497 | 123.3353 | 123.0469 | 122.9828 | -0.37537 | 122.0901 | 122.0627 | 121.8887 | -1.5564
793.6875 | 123.2803 | -121.9391 | 1.3733 | 0.52255 | 0.10698 | -0.00053286 | 0.029081 | -0.0021852 | 0.0016234 | 0.036002 | 0.07075 | 0.02463 | 4.7432e-05 | 0.0026968 | 0.0018428 | 0.043039 | 1.1444 | 1.1032 | 1.0529 | 1.149 | 1.3916 | 1.1353 | 0.97504 | -0.036621 | -0.022888 | -0.068665 | 0.18768 | 0.13733 | -0.10071 | -0.16479 | 123.0743 | 122.9141 | 0.018311 | 123.0423 | 123.0881 | 0.17395 | -0.22888 | 121.8384 | 121.7743 | -1.1856 | 121.9025 | 121.8704 | 0.09613 | -1.236 | 123.3307 | 123.0835 | 122.9919 | -0.39825 | 122.1268 | 122.0764 | 121.9162 | -1.5381
794.6875 | 123.3215 | -121.9254 | 1.3458 | -2.8649 | 0.11018 | 0.0037401 | 0.031217 | -0.019275 | -0.0037176 | 0.022116 | 0.1623 | 0.037447 | -0.0063606 | 0.017651 | -0.0045652 | 0.047312 | 1.149 | 1.1169 | 1.062 | 1.149 | 1.4053 | 1.1124 | 0.97504 | 0.004578 | -0.018311 | -0.041199 | 0.18768 | 0.11444 | -0.10071 | -0.16937 | 123.0377 | 122.9004 | 0.059509 | 123.0423 | 123.0743 | 0.17395 | -0.19684 | 121.8246 | 121.756 | -1.1581 | 121.9299 | 121.8842 | 0.12817 | -1.2314 | 123.3307 | 123.0743 | 122.9874 | -0.37079 | 122.113 | 122.0398 | 121.907 | -1.5152
795.6875 | 123.2986 | -121.9528 | 1.3596 | 0.21737 | 0.10057 | 0.012285 | 0.032286 | -0.0085942 | 0.0026914 | 0.021048 | 0.10127 | 0.021425 | 4.7432e-05 | 0.017651 | 0.0029108 | 0.041971 | 1.0941 | 1.0757 | 1.03 | 1.1032 | 1.3687 | 1.1078 | 0.95673 | -0.036621 | -0.045776 | -0.07782 | 0.19226 | 0.12817 | -0.10071 | -0.16937 | 123.0606 | 122.9095 | 0.009155 | 123.0286 | 123.056 | 0.14648 | -0.2655 | 121.8521 | 121.7834 | -1.1673 | 121.9162 | 121.875 | 0.091553 | -1.2314 | 123.3215 | 123.0469 | 122.9828 | -0.40283 | 122.1451 | 122.081 | 121.907 | -1.5289
796.6875 | 123.4131 | -121.9254 | 1.3458 | 0.18685 | 0.10805 | -0.0016009 | 0.036558 | -0.019275 | -0.0037176 | 0.033866 | 0.14704 | 0.021425 | 0.0043204 | 0.0048338 | 0.0039788 | 0.035562 | 1.1032 | 1.0849 | 1.0345 | 1.0941 | 1.3504 | 1.0803 | 0.93842 | -0.018311 | -0.036621 | -0.059509 | 0.18768 | 0.15564 | -0.10529 | -0.15106 | 123.0057 | 122.8638 | 0.004578 | 123.0103 | 123.0194 | 0.15564 | -0.24262 | 121.8201 | 121.7743 | -1.1581 | 121.907 | 121.8658 | 0.091553 | -1.1902 | 123.2758 | 123.0286 | 122.9599 | -0.40741 | 122.113 | 122.081 | 121.8887 | -1.4969
797.6875 | 123.2895 | -121.9894 | 1.3138 | 0.0037495 | 0.089889 | 0.0026721 | 0.0184 | 0.0020868 | 0.018713 | 0.029593 | -0.036062 | 0.017153 | 0.0032524 | 0.010174 | 0.0018428 | 0.047312 | 1.0803 | 1.0757 | 1.0208 | 1.0895 | 1.2817 | 1.0666 | 0.93384 | -0.050354 | -0.036621 | -0.073242 | 0.1831 | 0.13275 | -0.10986 | -0.15564 | 123.056 | 122.9233 | -0.032044 | 123.0652 | 123.0789 | 0.15564 | -0.23346 | 121.8796 | 121.8338 | -1.1307 | 121.9391 | 121.9162 | 0.082398 | -1.181 | 123.2712 | 123.0698 | 123.0103 | -0.37994 | 122.1725 | 122.1222 | 121.9528 | -1.4694
798.6875 | 123.2849 | -121.9849 | 1.3184 | 0.019007 | 0.10484 | 0.00053514 | 0.025877 | 0.0042228 | 0.0037594 | 0.021048 | -0.020803 | 0.026766 | 0.013933 | 0.0048338 | 0.0018428 | 0.040903 | 1.0757 | 1.0483 | 0.99792 | 1.0712 | 1.2863 | 1.0483 | 0.91095 | -0.032043 | -0.027466 | -0.082397 | 0.18768 | 0.15106 | -0.10529 | -0.16937 | 123.0331 | 122.8958 | -0.032043 | 123.0331 | 123.056 | 0.16022 | -0.24261 | 121.8796 | 121.8155 | -1.1307 | 121.9528 | 121.9025 | 0.086976 | -1.1673 | 123.2712 | 123.0606 | 122.9828 | -0.40741 | 122.1725 | 122.1359 | 121.9574 | -1.4877
799.6875 | 123.4131 | -121.9528 | 1.2589 | 0.41574 | 0.090957 | 0.010148 | 0.013059 | 0.0010188 | -0.021876 | 0.04241 | 0.28437 | 0.01288 | -0.01277 | 0.0059018 | -0.015247 | 0.04838 | 0.86517 | 1.2268 | 1.149 | 1.1765 | 1.2222 | 1.0574 | 0.92926 | 0.09613 | 0.10986 | 0.068665 | 0.13733 | 0.082397 | -0.073242 | -0.10529 | 123.0103 | 122.8821 | -0.036621 | 123.1796 | 123.1293 | 0.24719 | -0.39368 | 121.8796 | 121.8475 | -1.1215 | 122.049 | 122.0215 | 0.17395 | -1.1765 | 123.175 | 122.818 | 123.1018 | -0.32959 | 122.0901 | 122.0352 | 122.0627 | -1.3641
800.6875 | 123.3719 | -121.9894 | 1.2497 | 0.40048 | 0.10164 | 0.012285 | 0.016264 | -0.021411 | -0.0069216 | 0.016776 | 0.26911 | 0.020357 | 0.0011164 | -0.0026432 | 0.0029108 | 0.050516 | 1.0803 | 1.0712 | 1.0162 | 1.062 | 1.2955 | 1.0529 | 0.90179 | 0.027466 | 0.027466 | 0 | 0.16937 | 0.11444 | -0.07782 | -0.1236 | 123.0423 | 122.8912 | 0.045776 | 123.0606 | 123.0515 | 0.16022 | -0.16937 | 121.9116 | 121.8658 | -1.0803 | 122.0169 | 121.9894 | 0.1236 | -1.1353 | 123.2849 | 123.0698 | 123.0057 | -0.3479 | 122.1588 | 122.1039 | 122.0169 | -1.3733
801.6875 | 123.3765 | -121.9894 | 1.2405 | 0.431 | 0.086685 | 0.0037401 | 0.028013 | -0.0064582 | 0.0048274 | 0.010367 | 0.2386 | 0.028902 | -0.013838 | 0.020855 | 0.0082518 | 0.045175 | 1.0803 | 1.0666 | 1.0025 | 1.0574 | 1.2497 | 1.03 | 0.90637 | 0.045776 | 0.032043 | 0.018311 | 0.17395 | 0.11444 | -0.091553 | -0.13733 | 123.0194 | 122.8958 | 0.009155 | 123.056 | 123.0469 | 0.15106 | -0.16022 | 121.8979 | 121.8521 | -1.0666 | 122.0352 | 122.0078 | 0.15564 | -1.1261 | 123.2391 | 123.0698 | 122.9919 | -0.33417 | 122.1634 | 122.1039 | 122.0215 | -1.3779
802.6875 | 123.3948 | -122.0032 | 1.2314 | 0.38522 | 0.10164 | -0.0016009 | 0.030149 | -0.020343 | -0.0079896 | 0.024253 | 0.22334 | 0.015017 | -0.0052926 | 0.011242 | 0.0018428 | 0.040903 | 1.0712 | 1.0483 | 1.0025 | 1.0666 | 1.2634 | 1.03 | 0.89722 | 0.064087 | 0.059509 | 0.032043 | 0.14648 | 0.10986 | -0.059509 | -0.14648 | 123.0331 | 122.9004 | 0.032044 | 123.0515 | 123.0698 | 0.16937 | -0.16022 | 121.9437 | 121.8567 | -1.0849 | 122.0673 | 122.0352 | 0.17853 | -1.1215 | 123.2666 | 123.0743 | 123.0057 | -0.33417 | 122.1497 | 122.113 | 122.0627 | -1.3779
803.6875 | 123.4314 | -122.0169 | 1.2085 | 0.38522 | 0.092026 | -0.0026689 | 0.029081 | 0.0084958 | -0.00051261 | 0.025321 | 0.33015 | 0.013948 | -0.023451 | 0.01231 | -0.0002932 | 0.04838 | 1.0712 | 1.0574 | 1.0025 | 1.0483 | 1.2497 | 1.03 | 0.88348 | 0.064087 | 0.086975 | 0.045776 | 0.14648 | 0.10986 | -0.068665 | -0.1236 | 123.0469 | 122.9004 | 0.041199 | 123.0743 | 123.0652 | 0.16479 | -0.13733 | 121.9482 | 121.8933 | -1.062 | 122.081 | 122.0627 | 0.16937 | -1.0986 | 123.2666 | 123.0881 | 123.0194 | -0.32501 | 122.1634 | 122.1268 | 122.1039 | -1.3321
804.7031 | 123.4268 | -122.0261 | 1.2314 | -0.026769 | 0.067459 | 0.0037401 | 0.029081 | -0.022479 | -0.024012 | 0.017844 | -0.036062 | 0.017153 | -0.027724 | -0.0026432 | -0.0013612 | 0.039835 | 1.062 | 1.1444 | 1.0529 | 1.1032 | 1.2268 | 1.0254 | 0.88806 | 0.086975 | 0.1236 | 0.09613 | 0.16479 | 0.10986 | -0.082397 | -0.11902 | 123.0515 | 122.9141 | -0.004577 | 123.1705 | 123.1293 | 0.21515 | -0.16937 | 121.9437 | 121.907 | -1.0666 | 122.113 | 122.1222 | 0.21515 | -1.1215 | 123.2529 | 123.0881 | 123.0789 | -0.34332 | 122.1909 | 122.1359 | 122.1497 | -1.3504
805.6875 | 123.3398 | -122.0581 | 1.2177 | 0.23263 | 0.099502 | -0.0037369 | 0.014128 | -0.0021852 | 0.0091004 | 0.01998 | 0.13178 | 0.02463 | -0.0031566 | -0.0015752 | 0.0050478 | 0.037699 | 1.03 | 1.0208 | 0.93842 | 1.0025 | 1.236 | 0.98877 | 0.82398 | 0.013733 | -0.004578 | -0.050354 | 0.17395 | 0.1236 | -0.09613 | -0.15564 | 123.0469 | 122.8821 | 0.018311 | 123.0789 | 123.0606 | 0.17853 | -0.18768 | 121.962 | 121.9025 | -1.0437 | 122.0718 | 122.0078 | 0.10529 | -1.0941 | 123.2941 | 123.0881 | 122.9965 | -0.39368 | 122.2321 | 122.1817 | 122.0535 | -1.3733
806.6875 | 123.4177 | -122.0444 | 1.1719 | 0.41574 | 0.082412 | -0.01335 | 0.022672 | -0.0043222 | -0.013331 | 0.013571 | -0.34124 | 0.028902 | -0.024519 | 0.011242 | -0.0045652 | 0.043039 | 1.0986 | 0.84686 | 0.86975 | 1.0391 | 1.1536 | 0.97961 | 0.84228 | 0.10071 | 0.091553 | 0.07782 | 0.13275 | 0.09613 | -0.059509 | -0.11902 | 123.024 | 122.8867 | -0.018311 | 122.8912 | 123.0835 | 0.19684 | -0.073242 | 121.9849 | 121.9254 | -1.0391 | 122.1451 | 122.1222 | 0.19684 | -1.0757 | 123.1979 | 123.143 | 122.9141 | -0.32959 | 122.1771 | 122.1405 | 122.1359 | -1.2909
807.6875 | 123.4222 | -122.0581 | 1.1948 | 0.38522 | 0.083481 | 0.0016041 | 0.0184 | -0.018207 | -0.0079896 | 0.018912 | 0.10127 | 6.2833e-05 | -0.0063606 | -0.0026432 | -0.0067022 | 0.032358 | 1.1307 | 1.0986 | 1.0391 | 1.0712 | 1.149 | 0.9613 | 0.83771 | 0.10986 | 0.10529 | 0.059509 | 0.14648 | 0.091553 | -0.059509 | -0.11902 | 123.0194 | 122.8958 | -0.045776 | 123.1567 | 123.1293 | 0.23346 | -0.064087 | 121.9986 | 121.9391 | -1.0483 | 122.168 | 122.1176 | 0.17853 | -1.1032 | 123.2071 | 123.1888 | 123.0972 | -0.35706 | 122.2046 | 122.1497 | 122.1634 | -1.3138
808.6875 | 123.4222 | -122.0627 | 1.1765 | -1.5832 | 0.09523 | -0.0026689 | 0.014128 | -0.012866 | -0.012263 | 0.017844 | 0.11653 | 0.010744 | -0.019179 | 0.0048338 | -0.0002932 | 0.037699 | 1.0712 | 1.1307 | 1.0437 | 1.0712 | 1.1581 | 0.99792 | 0.84228 | 0.11444 | 0.091553 | 0.059509 | 0.1236 | 0.10071 | -0.054932 | -0.12817 | 123.0606 | 122.905 | -0.018311 | 123.1934 | 123.1339 | 0.22888 | -0.10529 | 122.0078 | 121.9345 | -1.0529 | 122.1771 | 122.1222 | 0.18768 | -1.0757 | 123.2208 | 123.1339 | 123.1064 | -0.33417 | 122.1863 | 122.1634 | 122.1542 | -1.3046
809.7031 | 123.349 | -122.113 | 1.1765 | -0.36246 | 0.10271 | -0.00053286 | 0.031217 | -0.0075262 | 0.016576 | 0.018912 | -0.66167 | 6.2833e-05 | 4.7432e-05 | -0.0069162 | 0.0018428 | 0.027017 | 0.98877 | 0.98877 | 0.91095 | 1.0025 | 1.2085 | 0.93384 | 0.78735 | 0.018311 | 0.059509 | -0.041199 | 0.18768 | 0.11444 | -0.10529 | -0.16479 | 123.0469 | 122.9004 | 0.032043 | 123.1018 | 123.1155 | 0.21515 | -0.18768 | 122.0078 | 121.9482 | -0.98877 | 122.1313 | 122.0718 | 0.1236 | -1.062 | 123.3215 | 123.1018 | 123.024 | -0.3891 | 122.3007 | 122.2275 | 122.1725 | -1.3412
810.6875 | 123.3948 | -122.0627 | 1.1627 | 0.24789 | 0.088821 | 0.0080121 | 0.0087873 | -0.015003 | -0.011195 | 0.016776 | 0.2386 | 0.0054038 | -0.021315 | 0.0059018 | 0.0007748 | 0.043039 | 1.0391 | 1.0895 | 1.0117 | 1.0391 | 1.1398 | 0.97961 | 0.84686 | 0.10529 | 0.09613 | 0.064087 | 0.13733 | 0.10986 | -0.045776 | -0.10986 | 123.0423 | 122.9095 | -0.022888 | 123.1522 | 123.1018 | 0.19226 | -0.1236 | 122.0169 | 121.9528 | -1.0254 | 122.168 | 122.1268 | 0.17395 | -1.0529 | 123.2025 | 123.1018 | 123.0743 | -0.31586 | 122.2 | 122.1725 | 122.1588 | -1.2726
811.6875 | 123.4222 | -122.1176 | 1.0895 | 0.44625 | 0.097366 | 0.0080121 | 0.020536 | -0.01073 | 0.0037594 | 0.028525 | 0.2386 | 0.022493 | -0.0010206 | -0.0037112 | -0.0002932 | 0.040903 | 1.0483 | 1.0895 | 1.0117 | 1.0483 | 1.1444 | 0.97961 | 0.81482 | -0.027466 | -0.045776 | 0.1236 | 0.10986 | 0.059509 | -0.086975 | -0.14648 | 123.0972 | 122.9324 | 0.054931 | 123.2071 | 123.1659 | 0.23346 | -0.041199 | 122.0306 | 121.9711 | -0.97961 | 122.0901 | 122.2412 | 0.27008 | -1.03 | 123.262 | 123.1659 | 123.1293 | -0.27466 | 122.2275 | 122.1771 | 122.0718 | -1.236
812.6875 | 123.3948 | -122.0856 | 1.149 | 0.3547 | 0.076004 | 0.013353 | 0.023741 | -0.0096622 | -0.011195 | 0.023184 | 0.19282 | 0.022493 | 0.0096604 | 0.0080378 | -0.0056342 | 0.038767 | 1.0483 | 1.0757 | 0.99792 | 1.0208 | 1.1398 | 0.97961 | 0.81482 | 0.09613 | 0.09613 | 0.059509 | 0.14191 | 0.10529 | -0.054932 | -0.11902 | 123.0652 | 122.9004 | -0.009155 | 123.1613 | 123.1064 | 0.20599 | -0.10071 | 122.0306 | 121.9666 | -1.0071 | 122.1817 | 122.1451 | 0.17853 | -1.0437 | 123.2254 | 123.1338 | 123.0835 | -0.33417 | 122.2275 | 122.1909 | 122.1817 | -1.268
813.6875 | 123.3948 | -122.1359 | 1.149 | 0.24789 | 0.089889 | 0.013353 | 0.0098553 | -0.0085942 | -0.018671 | 0.01998 | 0.086009 | 0.0064718 | -0.0063606 | -0.014393 | -0.0056342 | 0.043039 | 0.98419 | 1.0391 | 0.96588 | 0.97961 | 1.1581 | 0.9613 | 0.82855 | 0.068665 | 0.068665 | 0.022888 | 0.15564 | 0.10071 | -0.059509 | -0.11902 | 123.0972 | 122.9645 | 0.009155 | 123.175 | 123.1155 | 0.15106 | -0.1648 | 122.0764 | 122.0169 | -0.99335 | 122.2046 | 122.1588 | 0.14191 | -1.0483 | 123.2941 | 123.1201 | 123.1018 | -0.32044 | 122.2916 | 122.2366 | 122.2046 | -1.268
814.7031 | 123.3307 | -122.1725 | 1.1307 | 0.27841 | 0.13475 | -0.0048049 | 0.054716 | -0.0032532 | 0.018713 | 0.03707 | -0.05132 | 0.021425 | -0.0020886 | 0.0037648 | 0.014661 | 0.024881 | 0.98877 | 0.88806 | 0.83771 | 0.93842 | 1.1765 | 0.9201 | 0.75531 | 0.009155 | -0.032043 | -0.068665 | 0.16937 | 0.13275 | -0.10529 | -0.15564 | 123.0927 | 122.9279 | 0.045777 | 123.0606 | 123.111 | 0.18311 | -0.14191 | 122.0673 | 122.0169 | -0.9613 | 122.1817 | 122.1039 | 0.086975 | -0.99792 | 123.349 | 123.1613 | 123.0103 | -0.37537 | 122.3419 | 122.3053 | 122.1405 | -1.2863
815.6875 | 123.4589 | -122.2641 | 1.0757 | 0.24789 | 0.094162 | -0.0026689 | 0.015196 | -0.0075262 | -0.026148 | 0.017844 | 0.07075 | 0.010744 | -0.026655 | 0.0048338 | 0.0007748 | 0.04838 | 0.95673 | 1.0025 | 0.92926 | 0.9613 | 1.1032 | 0.92468 | 0.7782 | 0.059509 | 0.068665 | 0.027466 | 0.16022 | 0.10986 | -0.041199 | -0.14648 | 123.1888 | 123.0423 | 0.027465 | 123.2666 | 123.2254 | 0.18311 | -0.11902 | 122.2229 | 122.1176 | -0.91553 | 122.3236 | 122.2916 | 0.17395 | -0.96588 | 123.3673 | 123.2208 | 123.1934 | -0.29755 | 122.4243 | 122.374 | 122.3328 | -1.2222
816.6875 | 123.3902 | -122.1771 | 1.0208 | 0.14108 | 0.065323 | 0.015489 | 0.015196 | -0.012866 | -0.010127 | 0.013571 | 0.086009 | 0.018221 | -0.021315 | 0.017651 | 0.0029108 | 0.045175 | 0.9613 | 0.98419 | 0.91553 | 0.95673 | 1.1215 | 0.94299 | 0.7782 | 0.064087 | 0.064087 | 0.041199 | 0.16022 | 0.086975 | -0.10986 | -0.17395 | 123.1201 | 122.9553 | 0.10071 | 123.1613 | 123.1339 | 0.17853 | -0.059509 | 122.0673 | 122.0032 | -0.8606 | 122.2412 | 122.2183 | 0.21515 | -0.93384 | 123.2986 | 123.1384 | 123.0927 | -0.24262 | 122.3373 | 122.2641 | 122.2412 | -1.1948
817.6875 | 123.4177 | -122.1313 | 1.1078 | 0.034266 | 0.072799 | 0.0069441 | 0.014128 | -0.013935 | -0.018671 | 0.021048 | -0.18865 | -0.0020732 | -0.02986 | 0.0091058 | 0.0082518 | 0.050516 | 0.95673 | 0.98419 | 0.91553 | 0.95673 | 1.1124 | 0.9201 | 0.78278 | 0.09613 | 0.11902 | 0.068665 | 0.16479 | 0.10986 | -0.064087 | -0.11444 | 123.0515 | 122.9141 | 0.004578 | 123.1155 | 123.0881 | 0.17395 | -0.15106 | 122.0673 | 122.0169 | -0.94299 | 122.2275 | 122.2 | 0.18311 | -0.99792 | 123.2437 | 123.0881 | 123.0469 | -0.32501 | 122.2961 | 122.2412 | 122.2504 | -1.2222
818.6875 | 123.4818 | -122.1405 | 1.1078 | -0.20987 | 0.059982 | 0.0069441 | 0.026945 | -0.018207 | -0.015467 | 0.011435 | -0.75323 | 0.01288 | -0.033064 | 0.00056082 | -0.0077702 | 0.03663 | 1.0162 | 1.0712 | 0.97504 | 0.97504 | 1.1169 | 0.93842 | 0.76446 | 0.14648 | 0.1831 | 0.11902 | 0.15564 | 0.09613 | -0.045776 | -0.10986 | 123.0789 | 122.905 | 0.009155 | 123.2117 | 123.1155 | 0.21057 | -0.091553 | 122.0947 | 122.0306 | -0.95215 | 122.287 | 122.2595 | 0.22888 | -1.0117 | 123.2574 | 123.1567 | 123.1155 | -0.34332 | 122.2961 | 122.2366 | 122.3236 | -1.2177
819.7031 | 123.4497 | -122.1268 | 1.1169 | -0.1641 | 0.050369 | 0.018693 | 0.0023783 | -0.033161 | -0.011195 | 0.017844 | -0.31072 | -0.0020732 | -0.024519 | -0.0069162 | -0.0045652 | 0.043039 | 0.97961 | 1.0483 | 0.94299 | 0.96588 | 1.1307 | 0.9201 | 0.77362 | 0.13275 | 0.16479 | 0.10071 | 0.15564 | 0.09613 | -0.041199 | -0.10986 | 123.0469 | 122.9004 | 0.013733 | 123.175 | 123.0927 | 0.19226 | -0.13733 | 122.0856 | 122.0169 | -0.9613 | 122.2595 | 122.2275 | 0.21057 | -1.0208 | 123.2574 | 123.1064 | 123.0698 | -0.34332 | 122.2824 | 122.2229 | 122.2916 | -1.2268
820.6875 | 123.4543 | -122.1634 | 1.0941 | -0.042028 | 0.10698 | 0.010148 | 0.0045153 | -0.020343 | -0.0037176 | 0.017844 | -0.12761 | 0.0043348 | -0.020247 | 0.0037648 | 0.0018428 | 0.044107 | 0.95215 | 0.99335 | 0.92468 | 0.95673 | 1.1124 | 0.89722 | 0.74616 | 0.11902 | 0.1236 | 0.086975 | 0.16479 | 0.10071 | -0.050354 | -0.11444 | 123.0606 | 122.9095 | 0.018311 | 123.1567 | 123.1201 | 0.21057 | -0.14191 | 122.113 | 122.049 | -0.92926 | 122.2824 | 122.2504 | 0.20142 | -0.99335 | 123.2758 | 123.1155 | 123.0881 | -0.3479 | 122.3282 | 122.2641 | 122.287 | -1.2085
821.6875 | 123.4543 | -122.1588 | 1.0757 | -0.13358 | 0.053573 | 0.0037401 | 0.0184 | -0.023548 | -0.0079896 | 0.022116 | -0.20391 | 0.0054038 | -0.025587 | -0.01012 | -0.0077702 | 0.035562 | 0.9613 | 1.0162 | 0.9201 | 0.95673 | 1.0849 | 0.88806 | 0.75073 | 0.1236 | 0.14648 | 0.086975 | 0.16479 | 0.11444 | -0.041199 | -0.10529 | 123.0469 | 122.9095 | 0.009155 | 123.175 | 123.1155 | 0.20599 | -0.11444 | 122.1176 | 122.0535 | -0.91095 | 122.2824 | 122.2458 | 0.19226 | -0.9613 | 123.2437 | 123.1201 | 123.0789 | -0.32501 | 122.3236 | 122.2733 | 122.3053 | -1.181
822.6875 | 123.4406 | -122.1542 | 1.0574 | -0.53031 | 0.045028 | 0.0026721 | 0.023741 | -4.9167e-05 | 0.00055539 | 0.022116 | -0.43279 | 0.0086078 | -0.022383 | -0.014393 | -0.0034972 | 0.029154 | 0.98419 | 1.0757 | 0.94757 | 0.9613 | 1.0712 | 0.88348 | 0.74158 | 0.1236 | 0.15564 | 0.086975 | 0.13733 | 0.082397 | -0.050354 | -0.1236 | 123.0377 | 122.8958 | 0.013733 | 123.23 | 123.1155 | 0.21973 | -0.073242 | 122.1039 | 122.0306 | -0.9201 | 122.2778 | 122.2412 | 0.21057 | -0.97504 | 123.2254 | 123.1384 | 123.1018 | -0.31586 | 122.2916 | 122.2366 | 122.3099 | -1.181
823.6875 | 123.3994 | -122.1817 | 1.0483 | 0.75143 | 0.07814 | 0.012285 | 0.036558 | 0.0020868 | 0.0016234 | 0.023184 | -0.52434 | 0.0086078 | -0.0095656 | 0.0048338 | 0.0029108 | 0.030222 | 0.97504 | 1.0345 | 0.92926 | 0.95215 | 1.0529 | 0.86975 | 0.73242 | 0.10071 | 0.16479 | 0.059509 | 0.16479 | 0.11444 | -0.059509 | -0.1236 | 123.0515 | 122.9141 | 0.004577 | 123.2162 | 123.1338 | 0.21973 | -0.073242 | 122.1222 | 122.0581 | -0.88348 | 122.2824 | 122.2412 | 0.1831 | -0.93384 | 123.2346 | 123.1567 | 123.111 | -0.31586 | 122.3465 | 122.2961 | 122.3465 | -1.1719
824.7031 | 123.4497 | -122.1817 | 1.0437 | -0.36246 | 0.071731 | 0.012285 | 0.0045153 | -0.013935 | -0.0026496 | 0.01998 | -2.2486 | 0.010744 | -0.01277 | -0.013324 | 0.0071838 | 0.03663 | 0.9613 | 1.0529 | 0.93842 | 0.94757 | 1.0529 | 0.88348 | 0.73242 | 0.09613 | 0.20142 | 0.059509 | 0.14191 | 0.068665 | -0.068665 | -0.13733 | 123.0652 | 122.9141 | 0.009155 | 123.2346 | 123.1293 | 0.21515 | -0.082397 | 122.113 | 122.0444 | -0.90179 | 122.2778 | 122.2412 | 0.19684 | -0.97504 | 123.2346 | 123.143 | 123.1201 | -0.31128 | 122.3236 | 122.2504 | 122.3831 | -1.181
825.6875 | 123.4772 | -122.1771 | 1.0391 | -0.13358 | 0.058914 | 0.0069441 | 0.016264 | -0.016071 | -0.0058536 | 0.025321 | -0.21917 | 0.0032668 | -0.015974 | -0.0069162 | -0.0024292 | 0.035562 | 0.94757 | 1.0162 | 0.90637 | 0.94299 | 1.0437 | 0.88806 | 0.72784 | 0.13733 | 0.15564 | 0.091553 | 0.16479 | 0.09613 | -0.050354 | -0.11444 | 123.0652 | 122.905 | 0.004577 | 123.1934 | 123.1201 | 0.21515 | -0.091553 | 122.1268 | 122.0627 | -0.87433 | 122.3145 | 122.2687 | 0.20599 | -0.94299 | 123.2208 | 123.1247 | 123.0835 | -0.31128 | 122.3419 | 122.2733 | 122.3328 | -1.1536
826.6875 | 123.4314 | -122.2046 | 1.0208 | -0.19462 | 0.050369 | 0.016557 | 0.020536 | -0.012866 | -0.0090576 | 0.023184 | -0.46331 | 0.01288 | -0.018111 | -0.012256 | -0.0024292 | 0.027017 | 0.97961 | 1.0574 | 0.91553 | 0.94757 | 1.0529 | 0.84686 | 0.71869 | 0.1236 | 0.14191 | 0.17395 | 0.14648 | 0.09613 | -0.068665 | -0.14648 | 123.0515 | 122.9233 | 0.032043 | 123.262 | 123.1522 | 0.22888 | -0.041199 | 122.1359 | 122.0581 | -0.87433 | 122.3282 | 122.3785 | 0.32043 | -0.92468 | 123.2574 | 123.1842 | 123.1201 | -0.30212 | 122.3511 | 122.3007 | 122.3465 | -1.1673
827.6875 | 123.3124 | -122.2458 | 1.0666 | -0.43876 | 0.093094 | 0.012285 | 0.031217 | 0.0084958 | 0.012304 | 0.036002 | -0.49383 | 0.0054038 | -0.022383 | -0.0015752 | -0.0013612 | 0.037699 | 0.89264 | 0.94299 | 0.80109 | 0.88348 | 1.0666 | 0.8194 | 0.68665 | 0.004578 | 0.12817 | -0.022888 | 0.17853 | 0.13275 | -0.10529 | -0.15564 | 123.0652 | 122.9324 | 0 | 123.1888 | 123.1293 | 0.19684 | -0.17395 | 122.1405 | 122.0901 | -0.88806 | 122.2504 | 122.2229 | 0.13275 | -0.93384 | 123.3124 | 123.1384 | 123.0469 | -0.37994 | 122.4243 | 122.3785 | 122.374 | -1.2222
828.6875 | 123.436 | -122.2275 | 1.0025 | -0.36246 | 0.069595 | 0.010148 | 0.014128 | -0.011798 | -0.011195 | 0.017844 | -0.52434 | 0.0032668 | -0.015974 | 0.0059018 | -0.015247 | 0.022745 | 0.93384 | 1.03 | 0.90637 | 0.91095 | 1.0391 | 0.84228 | 0.70496 | 0.21057 | -0.16479 | 0.10071 | 0.12817 | 0.07782 | -0.068665 | -0.14191 | 123.0698 | 122.9324 | 0.036622 | 123.2574 | 123.1384 | 0.20599 | -0.068664 | 122.1588 | 122.0856 | -0.87433 | 122.438 | 122.3282 | 0.24262 | -0.92468 | 123.2666 | 123.1613 | 123.1339 | -0.29755 | 122.3557 | 122.3053 | 122.0627 | -1.1444
829.7031 | 123.4451 | -122.2137 | 1.0345 | 0.0037495 | 0.058914 | 0.012285 | 0.0013103 | -0.020343 | -0.0079896 | 0.018912 | -0.23443 | 0.015017 | -0.019179 | 0.011242 | 0.0007748 | 0.044107 | 0.87891 | 0.9613 | 0.8606 | 0.90179 | 1.03 | 0.84686 | 0.70496 | 0.11444 | 0.11902 | 0.082397 | 0.15106 | 0.10071 | -0.050354 | -0.10986 | 123.0606 | 122.9187 | -0.004578 | 123.175 | 123.1155 | 0.19684 | -0.15564 | 122.1634 | 122.1039 | -0.88348 | 122.3282 | 122.2961 | 0.19226 | -0.93384 | 123.2437 | 123.0927 | 123.0743 | -0.32959 | 122.3648 | 122.3145 | 122.3328 | -1.1444
830.6875 | 123.2941 | -122.2687 | 1.0437 | -0.54557 | 0.046097 | 0.0058761 | 0.028013 | -4.9167e-05 | 0.0026914 | 0.018912 | -0.31072 | 0.018221 | -0.021315 | 0.0016288 | 0.0093198 | 0.033426 | 0.84228 | 0.87891 | 0.78278 | 0.83313 | 1.0483 | 0.80109 | 0.65918 | 0.018311 | 0.032043 | -0.032043 | 0.17853 | 0.13733 | -0.091553 | -0.16022 | 123.0698 | 122.9279 | 0.004578 | 123.1476 | 123.1018 | 0.17395 | -0.20142 | 122.1771 | 122.1085 | -0.86517 | 122.287 | 122.2366 | 0.12817 | -0.90637 | 123.317 | 123.111 | 123.0515 | -0.38452 | 122.4472 | 122.406 | 122.3007 | -1.2039
831.6875 | 123.3261 | -122.2961 | 1.0345 | -0.51505 | 0.088821 | 0.011217 | 0.0184 | -0.0064582 | -0.0026496 | 0.031729 | -0.41753 | 0.021425 | -0.0074286 | -0.014393 | 0.0029108 | 0.032358 | 0.82398 | 0.92926 | 0.79651 | 0.82855 | 1.0529 | 0.81024 | 0.64087 | 0.009155 | 0.022888 | -0.032043 | 0.19226 | 0.14191 | -0.11444 | -0.16022 | 123.1064 | 122.937 | 0.01831 | 123.2254 | 123.1247 | 0.18768 | -0.21057 | 122.1817 | 122.1359 | -0.84228 | 122.3053 | 122.2641 | 0.12817 | -0.89264 | 123.349 | 123.1201 | 123.0927 | -0.39368 | 122.4884 | 122.4381 | 122.319 | -1.1948
832.6875 | 123.4406 | -122.2733 | 0.99792 | -0.36246 | 0.069595 | 0.013353 | 0.026945 | -0.011798 | -0.018671 | 0.007163 | 0.55903 | 0.010744 | -0.019179 | -0.013324 | 0.0029108 | 0.03663 | 0.97046 | 0.90637 | 0.76446 | 0.84228 | 0.99335 | 0.78735 | 0.65918 | 0.11902 | 0.16479 | 0.09613 | 0.15106 | 0.10071 | -0.054932 | -0.11444 | 123.0606 | 122.9324 | -0.004578 | 123.1796 | 123.1155 | 0.1831 | -0.027466 | 122.2183 | 122.1588 | -0.84686 | 122.3923 | 122.3694 | 0.21057 | -0.89722 | 123.2666 | 123.2437 | 123.0377 | -0.33874 | 122.4243 | 122.374 | 122.438 | -1.1124
833.6875 | 123.3719 | -122.2778 | 1.0025 | -0.48453 | 0.090957 | 0.0058761 | 0.017332 | -0.025684 | -0.0069216 | 0.021048 | -0.6159 | 0.023562 | -0.01277 | 0.0016288 | -0.0067022 | 0.032358 | 0.85602 | 0.95215 | 0.82855 | 0.89722 | 1.0254 | 0.79193 | 0.66834 | 0.054932 | 0.091553 | 0.009155 | 0.18768 | 0.10986 | -0.07782 | -0.15106 | 123.0698 | 122.9462 | 0.022889 | 123.23 | 123.175 | 0.22888 | -0.14648 | 122.2 | 122.1268 | -0.81482 | 122.3328 | 122.287 | 0.16022 | -0.89264 | 123.3032 | 123.1339 | 123.1064 | -0.33417 | 122.4655 | 122.3877 | 122.3694 | -1.1536
834.7031 | 123.4222 | -122.2595 | 1.0254 | -0.53031 | 0.073868 | 0.016557 | 0.015196 | -0.013935 | 0.0037594 | 0.016776 | -0.55486 | 0.0011308 | -0.020247 | 0.013378 | -0.0067022 | 0.039835 | 0.87433 | 0.97046 | 0.85602 | 0.90637 | 0.99335 | 0.80566 | 0.66376 | 0.091553 | 0.15564 | 0.064087 | 0.15106 | 0.11444 | -0.068665 | -0.13733 | 123.0652 | 122.9233 | -0.032044 | 123.23 | 123.1659 | 0.24261 | -0.15106 | 122.1909 | 122.1222 | -0.87433 | 122.3511 | 122.3236 | 0.20142 | -0.91095 | 123.2529 | 123.1339 | 123.1155 | -0.36163 | 122.4106 | 122.374 | 122.4152 | -1.1627
835.6875 | 123.3765 | -122.3099 | 0.99792 | -0.36246 | 0.12941 | -0.0058729 | 0.033354 | -0.0064582 | 0.016576 | 0.030661 | -0.52434 | 0.021425 | -0.0052926 | 0.0026968 | 0.012524 | 0.025949 | 0.83313 | 0.87433 | 0.75531 | 0.83313 | 1.0071 | 0.77362 | 0.62256 | 0.027466 | 0.091553 | 0.009155 | 0.1831 | 0.11902 | -0.082397 | -0.15564 | 123.0835 | 122.9324 | 0.009155 | 123.1842 | 123.143 | 0.21057 | -0.16479 | 122.2275 | 122.1542 | -0.81482 | 122.3373 | 122.319 | 0.16479 | -0.87891 | 123.317 | 123.143 | 123.0652 | -0.37537 | 122.493 | 122.4289 | 122.4014 | -1.1536
836.6875 | 123.3582 | -122.319 | 1.0254 | -0.51505 | 0.099502 | 0.024034 | 0.023741 | -0.016071 | -0.016535 | 0.023184 | -0.63115 | 0.010744 | -0.018111 | 0.0026968 | 0.0007748 | 0.032358 | 0.8194 | 0.91553 | 0.78735 | 0.83313 | 1.0208 | 0.7782 | 0.64087 | 0.018311 | 0.068665 | -0.004578 | 0.18768 | 0.1236 | -0.07782 | -0.16479 | 123.0972 | 122.9599 | -0.004578 | 123.2346 | 123.1522 | 0.19226 | -0.20599 | 122.2412 | 122.1542 | -0.83771 | 122.3373 | 122.3145 | 0.16022 | -0.90179 | 123.3398 | 123.1384 | 123.1064 | -0.38452 | 122.5067 | 122.4426 | 122.3877 | -1.1902
837.6875 | 123.3307 | -122.3145 | 1.0117 | -0.40824 | 0.083481 | 0.0080121 | 0.034422 | 0.0020868 | 0.0016234 | 0.027457 | -4.3238 | 0.011812 | -0.0063606 | -0.0047802 | -0.0045652 | 0.033426 | 0.77362 | 0.83771 | 0.71869 | 0.78735 | 1.0254 | 0.74616 | 0.6134 | 0.013733 | -0.004578 | -0.036621 | 0.23346 | 0.15106 | -0.064087 | -0.13275 | 123.0606 | 122.9279 | 0.013733 | 123.1522 | 123.1018 | 0.17395 | -0.23804 | 122.2504 | 122.1817 | -0.7782 | 122.3282 | 122.2778 | 0.09613 | -0.8606 | 123.3398 | 123.0881 | 123.0331 | -0.39825 | 122.5479 | 122.4655 | 122.3099 | -1.1444
838.6875 | 123.3398 | -122.3419 | 1.0025 | -0.48453 | 0.093094 | 0.010148 | 0.033354 | -0.012866 | 0.00055539 | 0.024253 | 1.5661 | 0.020357 | -0.0020886 | 0.0069698 | -0.0056342 | 0.043039 | 0.75531 | 0.81482 | 0.70496 | 0.77362 | 1.0162 | 0.737 | 0.59052 | -0.009155 | 0.036621 | -0.045776 | 0.20142 | 0.15106 | -0.059509 | -0.15106 | 123.0789 | 122.9324 | 0.013733 | 123.1567 | 123.1155 | 0.18311 | -0.24719 | 122.2824 | 122.1909 | -0.80109 | 122.3328 | 122.2961 | 0.10529 | -0.85144 | 123.3582 | 123.0972 | 123.0469 | -0.41199 | 122.5433 | 122.493 | 122.3785 | -1.1536
839.7031 | 123.468 | -122.3099 | 0.91553 | 0.38522 | 0.090957 | -0.0090779 | 0.014128 | -0.01073 | -0.0026496 | 0.031729 | 0.22334 | 0.015017 | -0.0031566 | -0.0090522 | -0.0045652 | 0.038767 | 0.85144 | 0.91553 | 0.8194 | 0.86517 | 0.96588 | 0.79193 | 0.62714 | 0.1236 | 0.10986 | 0.086975 | 0.12817 | 0.059509 | -0.082397 | -0.14191 | 123.1018 | 122.937 | 0.050354 | 123.2254 | 123.175 | 0.23804 | -0.064087 | 122.2275 | 122.168 | -0.78735 | 122.4335 | 122.3969 | 0.22888 | -0.85602 | 123.2758 | 123.1613 | 123.1293 | -0.28839 | 122.438 | 122.3694 | 122.4197 | -1.0574
840.7031 | 123.3673 | -122.3099 | 0.96588 | -0.072545 | 0.090957 | 0.00053514 | 0.037626 | -0.01073 | 0.01444 | 0.027457 | -0.44805 | 0.028902 | -0.0074286 | 0.0026968 | 0.0071838 | 0.029154 | 0.83771 | 0.88348 | 0.75989 | 0.82398 | 1.0529 | 0.81482 | 0.64087 | 0.045776 | 0.07782 | -0.013733 | 0.17853 | 0.11902 | -0.091553 | -0.15106 | 123.1247 | 122.9507 | 0.086975 | 123.1934 | 123.1339 | 0.18311 | -0.12817 | 122.2183 | 122.1588 | -0.78735 | 122.3557 | 122.2961 | 0.13733 | -0.84686 | 123.3627 | 123.1476 | 123.0698 | -0.32501 | 122.4884 | 122.4289 | 122.3877 | -1.1169
841.6875 | 123.3215 | -122.3511 | 0.98419 | -0.43876 | 0.077072 | 0.017625 | 0.016264 | -0.01073 | 0.0026914 | 0.030661 | 1.8103 | 0.01288 | -0.024519 | 0.0091058 | 0.0007748 | 0.039835 | 0.74158 | 0.77362 | 0.68207 | 0.75531 | 0.99335 | 0.70953 | 0.57678 | -0.013733 | 0.045776 | -0.036621 | 0.22888 | 0.1831 | -0.073242 | -0.14648 | 123.0606 | 122.9279 | 0.009155 | 123.1247 | 123.1064 | 0.17853 | -0.24261 | 122.2778 | 122.2046 | -0.75531 | 122.3373 | 122.3145 | 0.10986 | -0.80109 | 123.3444 | 123.0927 | 123.0331 | -0.40741 | 122.58 | 122.5342 | 122.3969 | -1.1307
842.6875 | 123.3765 | -122.3511 | 0.97504 | -0.40824 | 0.10271 | 0.0037401 | 0.032286 | -0.0053902 | 0.0016234 | 0.014639 | -0.58538 | 0.022493 | -0.020247 | 0.014447 | -0.0002932 | 0.03663 | 0.72327 | 0.79193 | 0.69122 | 0.77362 | 1.0071 | 0.72327 | 0.57678 | -0.004578 | 0.045776 | -0.036621 | 0.1831 | 0.13275 | -0.09613 | -0.15564 | 123.0743 | 122.9279 | 0.032043 | 123.143 | 123.1247 | 0.19684 | -0.25177 | 122.2549 | 122.1954 | -0.79193 | 122.3465 | 122.3145 | 0.11902 | -0.84229 | 123.3582 | 123.0743 | 123.0423 | -0.39826 | 122.5342 | 122.4838 | 122.3969 | -1.1307
843.6875 | 123.3627 | -122.3465 | 0.97961 | -0.33194 | 0.096298 | -0.00053286 | 0.022672 | -0.018207 | 0.011236 | 0.026389 | -0.44805 | 0.017153 | -0.014906 | -0.0037112 | 0.0039788 | 0.032358 | 0.76904 | 0.81024 | 0.71411 | 0.80566 | 0.97961 | 0.72327 | 0.57678 | 0.045776 | 0.073242 | 0 | 0.18768 | 0.11902 | -0.09613 | -0.16479 | 123.0698 | 122.9233 | 0 | 123.1567 | 123.1522 | 0.22888 | -0.21057 | 122.2504 | 122.1817 | -0.79193 | 122.3923 | 122.3465 | 0.16479 | -0.86059 | 123.3261 | 123.1155 | 123.0606 | -0.40283 | 122.5342 | 122.4655 | 122.4197 | -1.1444
844.7031 | 123.3398 | -122.374 | 0.9613 | 6.4277 | 0.10164 | -0.0069409 | 0.051512 | -0.0032532 | 0.0058954 | 0.024253 | -0.066579 | 0.019289 | -0.011702 | 0.0037648 | -0.0034972 | 0.05372 | 0.74616 | 0.74158 | 0.66834 | 0.75073 | 0.99792 | 0.72784 | 0.55847 | 0 | 0 | -0.032043 | 0.1831 | 0.11902 | -0.073242 | -0.16937 | 123.1018 | 122.9324 | 0.036621 | 123.1155 | 123.1247 | 0.19226 | -0.21515 | 122.3007 | 122.2046 | -0.7782 | 122.374 | 122.3419 | 0.13733 | -0.84229 | 123.3719 | 123.1201 | 123.0423 | -0.40283 | 122.5571 | 122.493 | 122.374 | -1.1307
845.6875 | 123.3398 | -122.3648 | 0.97046 | -0.48453 | 0.092026 | 0.011217 | 0.016264 | -0.0021852 | -0.024012 | 0.028525 | -0.47857 | 0.015017 | -0.025587 | 0.0080378 | -0.014179 | 0.029154 | 0.75531 | 0.82855 | 0.72784 | 0.80109 | 0.97046 | 0.737 | 0.58594 | 0.009155 | 0.064087 | 0.004578 | 0.18768 | 0.13275 | -0.082397 | -0.15564 | 123.1018 | 122.9507 | 0 | 123.1934 | 123.1659 | 0.21515 | -0.21515 | 122.2824 | 122.2092 | -0.78278 | 122.374 | 122.3694 | 0.16022 | -0.83771 | 123.3353 | 123.1201 | 123.0927 | -0.38452 | 122.5525 | 122.4976 | 122.4289 | -1.1261
846.6875 | 123.3032 | -122.3557 | 1.0071 | -0.45401 | 0.074936 | 0.0069441 | 0.032286 | -0.01073 | -0.013331 | 0.023184 | -0.60064 | 0.011812 | -0.013838 | 0.0048338 | -0.0077702 | 0.035562 | 0.72327 | 0.76446 | 0.65918 | 0.737 | 0.97961 | 0.71411 | 0.54932 | -0.013733 | 0.032043 | -0.041199 | 0.19684 | 0.13733 | -0.073242 | -0.16022 | 123.0698 | 122.905 | -0.027466 | 123.1201 | 123.0927 | 0.18768 | -0.28381 | 122.2824 | 122.1954 | -0.81024 | 122.3419 | 122.3145 | 0.11902 | -0.86975 | 123.3353 | 123.0789 | 123.0148 | -0.45776 | 122.5525 | 122.493 | 122.3877 | -1.1673
847.6875 | 123.3582 | -122.3831 | 0.94757 | -0.36246 | 0.080276 | 0.011217 | 0.030149 | -0.0032532 | 0.0091004 | 0.032797 | -0.6159 | 0.0086078 | -0.013838 | 0.0048338 | 0.0039788 | 0.035562 | 0.72327 | 0.78278 | 0.67749 | 0.75989 | 0.94299 | 0.69122 | 0.55847 | 0.018311 | 0.045776 | -0.018311 | 0.19226 | 0.13275 | -0.09613 | -0.16479 | 123.0743 | 122.9416 | -0.004578 | 123.1659 | 123.143 | 0.20142 | -0.2243 | 122.287 | 122.2183 | -0.75531 | 122.4014 | 122.3648 | 0.14648 | -0.81482 | 123.3261 | 123.1064 | 123.0606 | -0.3891 | 122.5754 | 122.5159 | 122.4289 | -1.1124
848.6875 | 123.4131 | -122.2824 | 0.99792 | -0.14884 | 0.090957 | 0.0016041 | 0.020536 | -0.0096622 | 0.0058954 | 0.028525 | -0.3565 | 0.020357 | -0.0063606 | 0.0037648 | 0.0061158 | 0.024881 | 0.75989 | 0.78735 | 0.67749 | 0.78735 | 0.93384 | 0.71411 | 0.54932 | 0.036621 | 0.073242 | 0.009155 | 0.20142 | 0.1236 | -0.068665 | -0.11902 | 122.9965 | 122.8317 | -0.064087 | 123.0698 | 123.0698 | 0.23804 | -0.23804 | 122.2137 | 122.1634 | -0.79651 | 122.319 | 122.2916 | 0.12817 | -0.87433 | 123.2162 | 123.0423 | 122.9599 | -0.44861 | 122.4838 | 122.406 | 122.3557 | -1.1169
849.7031 | 123.4406 | -122.3694 | 0.91095 | 0.46151 | 0.093094 | 0.00053514 | 0.021604 | -4.9167e-05 | 0.00055539 | 0.022116 | 0.17756 | 0.016085 | -0.0063606 | 0.010174 | 0.0039788 | 0.038767 | 0.73242 | 0.78735 | 0.71411 | 0.75531 | 0.91095 | 0.70953 | 0.57678 | 0.086975 | 0.11444 | 0.064087 | 0.14191 | 0.10071 | -0.059509 | -0.11902 | 123.0789 | 122.9462 | 0 | 123.1567 | 123.1247 | 0.17853 | -0.17853 | 122.3099 | 122.2504 | -0.76904 | 122.4564 | 122.4335 | 0.18311 | -0.81024 | 123.2803 | 123.1018 | 123.0835 | -0.33417 | 122.5113 | 122.4701 | 122.4838 | -1.03
850.6875 | 123.3444 | -122.4289 | 0.9201 | -0.53031 | 0.081344 | 0.00053514 | 0.024809 | -0.021411 | -0.020808 | 0.027457 | -0.17339 | 0.020357 | -0.0042246 | 0.0080378 | -0.0013612 | 0.044107 | 0.66376 | 1.0849 | 0.78278 | 0.6958 | 0.99792 | 0.70496 | 0.58594 | -0.018311 | 0.018311 | -0.036621 | 0.20142 | 0.13733 | -0.10071 | -0.15106 | 123.1338 | 123.0148 | 0.07782 | 123.5138 | 123.1247 | 0.10986 | -0.25635 | 122.3282 | 122.2778 | -0.71869 | 122.4106 | 122.3923 | 0.11444 | -0.78278 | 123.4268 | 123.0927 | 123.2117 | -0.33417 | 122.6303 | 122.5662 | 122.4472 | -1.0712
851.6875 | 123.3765 | -122.406 | 0.92468 | -0.3472 | 0.10377 | 0.012285 | 0.022672 | 0.0020868 | 0.0048274 | 0.029593 | -0.46331 | 0.02463 | -0.0063606 | 0.0048338 | 0.011456 | 0.038767 | 0.71869 | 0.75989 | 0.66834 | 0.74616 | 0.93384 | 0.69122 | 0.53101 | 0.022888 | 0.068665 | 0.009155 | 0.16937 | 0.12817 | -0.068665 | -0.16022 | 123.0972 | 122.937 | 0.009155 | 123.1659 | 123.1522 | 0.21515 | -0.20599 | 122.3373 | 122.2458 | -0.75531 | 122.4289 | 122.4152 | 0.16937 | -0.79651 | 123.3398 | 123.1247 | 123.0743 | -0.39368 | 122.5754 | 122.5342 | 122.4747 | -1.0849
852.6875 | 123.3307 | -122.4014 | 0.97961 | -0.53031 | 0.072799 | 0.010148 | 0.024809 | -0.0085942 | -0.014399 | 0.016776 | -0.6159 | 0.020357 | -0.013838 | -0.0026432 | -0.0045652 | 0.030222 | 0.65918 | 0.75073 | 0.62714 | 0.6958 | 0.93842 | 0.66376 | 0.53101 | 0.086975 | 0.018311 | -0.086975 | 0.2243 | 0.16022 | -0.059509 | -0.1236 | 123.0652 | 122.9324 | -0.041198 | 123.1522 | 123.0972 | 0.1648 | -0.32043 | 122.3419 | 122.2778 | -0.75531 | 122.4884 | 122.3145 | 0.036621 | -0.8194 | 123.3398 | 123.0606 | 123.0286 | -0.44861 | 122.6257 | 122.5616 | 122.4197 | -1.1032
853.6875 | 123.3124 | -122.3648 | 0.96588 | -0.39298 | 0.089889 | 0.0037401 | 0.020536 | -0.0032532 | -0.018671 | 0.016776 | -0.55486 | 0.013948 | -0.01277 | 0.0026968 | 0.0007748 | 0.035562 | 0.67291 | 0.72784 | 0.64087 | 0.6958 | 0.92926 | 0.68207 | 0.53558 | -0.022888 | 0.013733 | -0.027466 | 0.20142 | 0.14648 | -0.091553 | -0.13275 | 123.0469 | 122.9004 | -0.036621 | 123.0927 | 123.0606 | 0.16022 | -0.29297 | 122.2733 | 122.2321 | -0.76446 | 122.3419 | 122.3373 | 0.10529 | -0.8194 | 123.2941 | 123.0377 | 123.0057 | -0.4303 | 122.5662 | 122.5113 | 122.3785 | -1.0986
854.7031 | 123.3856 | -122.3923 | 0.90637 | 0.30892 | 0.11018 | -0.0090779 | 0.0023783 | -0.016071 | 0.0058954 | 0.023184 | 0.25385 | 0.019289 | 0.010729 | 0.022991 | -0.0024292 | 0.043039 | 0.67291 | 0.71869 | 0.62256 | 0.69122 | 0.93842 | 0.67749 | 0.53101 | 0.022888 | 0.004578 | -0.009155 | 0.15564 | 0.1236 | -0.082397 | -0.15564 | 123.0698 | 122.9233 | 0.032044 | 123.111 | 123.0835 | 0.16022 | -0.23346 | 122.3099 | 122.2366 | -0.75073 | 122.4152 | 122.3831 | 0.14649 | -0.78278 | 123.3307 | 123.0652 | 123.0148 | -0.37537 | 122.5479 | 122.5159 | 122.3969 | -1.062
855.6875 | 123.3627 | -122.4197 | 0.90637 | -0.3472 | 0.098434 | 0.013353 | 0.03549 | -0.015003 | -0.0037176 | 0.031729 | -0.58538 | 0.023562 | 0.0032524 | -0.0015752 | -0.0002932 | 0.03663 | 0.6958 | 0.71411 | 0.62714 | 0.71869 | 0.91553 | 0.6546 | 0.52185 | 0 | 0.054932 | -0.009155 | 0.1831 | 0.12817 | -0.10071 | -0.16479 | 123.0743 | 122.9416 | 0.009155 | 123.1339 | 123.1384 | 0.19684 | -0.21057 | 122.319 | 122.2549 | -0.72327 | 122.4197 | 122.4106 | 0.15564 | -0.7782 | 123.3353 | 123.1155 | 123.0469 | -0.38452 | 122.6028 | 122.5479 | 122.4747 | -1.0712
856.6875 | 123.317 | -122.2916 | 0.95215 | -0.20987 | 0.11232 | -0.014418 | 0.013059 | -0.0043222 | 0.0048274 | 0.030661 | -0.38701 | 0.021425 | -0.019179 | 0.0080378 | -0.0002932 | 0.037699 | 0.73242 | 0.76446 | 0.64087 | 0.72784 | 0.90637 | 0.66376 | 0.53101 | 0.036621 | 0.064087 | -0.013733 | 0.1831 | 0.12817 | -0.082397 | -0.15106 | 122.9553 | 122.8226 | -0.045776 | 123.056 | 123.0194 | 0.19684 | -0.21973 | 122.2092 | 122.1405 | -0.76904 | 122.3282 | 122.2778 | 0.13733 | -0.82397 | 123.1979 | 123.024 | 122.9324 | -0.42114 | 122.4747 | 122.4197 | 122.3557 | -1.1032
857.6875 | 123.3719 | -122.4564 | 0.89264 | -0.36246 | 0.11446 | 0.0037401 | 0.038694 | -0.015003 | -0.0026496 | 0.029593 | -0.44805 | 0.011812 | -0.01277 | 0.0016288 | -0.0067022 | 0.03663 | 0.66834 | 0.6958 | 0.60883 | 0.69122 | 0.91095 | 0.65002 | 0.50354 | 0 | 0.041199 | -0.022888 | 0.18768 | 0.12817 | -0.09613 | -0.15106 | 123.1064 | 122.9599 | 0.018311 | 123.1522 | 123.1476 | 0.18768 | -0.2243 | 122.3602 | 122.3053 | -0.70496 | 122.4564 | 122.4335 | 0.12817 | -0.76446 | 123.3673 | 123.1247 | 123.0652 | -0.3891 | 122.644 | 122.5845 | 122.4976 | -1.0437
858.6875 | 123.3719 | -122.4609 | 0.90179 | -0.40824 | 0.10698 | 0.013353 | 0.034422 | -0.013935 | 0.00055539 | 0.01998 | -0.55486 | 0.023562 | 4.7432e-05 | 0.010174 | 0.0007748 | 0.033426 | 0.65918 | 0.70038 | 0.6134 | 0.70496 | 0.90637 | 0.63171 | 0.49439 | -0.013733 | 0.041199 | -0.027466 | 0.1831 | 0.1236 | -0.10529 | -0.17395 | 123.0927 | 122.9553 | 0.004578 | 123.1613 | 123.1659 | 0.21057 | -0.24261 | 122.3557 | 122.287 | -0.71869 | 122.4472 | 122.4335 | 0.14648 | -0.7782 | 123.3673 | 123.1201 | 123.0743 | -0.40741 | 122.644 | 122.5845 | 122.5021 | -1.0757
859.7031 | 123.4451 | -122.3877 | 0.89722 | 0.0037495 | 0.058914 | -0.20881 | 0.021604 | -0.01073 | -0.043238 | 0.01998 | -0.097097 | 0.010744 | -0.023451 | -0.0047802 | -0.0099062 | 0.047312 | 0.68207 | 0.79651 | 0.70496 | 0.75073 | 0.89722 | 0.67291 | 0.54016 | 0.073242 | 0.10986 | 0.10071 | 0.16937 | 0.10986 | -0.041199 | -0.1236 | 123.0606 | 122.9279 | 0 | 123.1842 | 123.1384 | 0.21057 | -0.21515 | 122.3465 | 122.2641 | -0.72784 | 122.4609 | 122.4884 | 0.2243 | -0.78735 | 123.2849 | 123.0698 | 123.0927 | -0.35706 | 122.5571 | 122.4976 | 122.4976 | -1.0208
860.6875 | 123.381 | -122.4472 | 0.86975 | -0.11832 | 0.11766 | 0.0090801 | 0.037626 | -0.0053902 | 0.013372 | 0.026389 | -0.24969 | 0.022493 | 4.7432e-05 | 0.0048338 | 0.0093198 | 0.028086 | 0.76446 | 0.75989 | 0.67749 | 0.74158 | 0.93842 | 0.70496 | 0.56763 | 0.022888 | 0.054932 | -0.018311 | 0.1831 | 0.12817 | -0.09613 | -0.16479 | 123.1522 | 123.0148 | 0.068665 | 123.2071 | 123.1888 | 0.17395 | -0.10529 | 122.3511 | 122.2824 | -0.68665 | 122.4701 | 122.4289 | 0.14648 | -0.74158 | 123.3856 | 123.2117 | 123.1247 | -0.30212 | 122.6303 | 122.5754 | 122.5021 | -1.0345
861.6875 | 123.3765 | -122.4472 | 0.86517 | -0.39298 | 0.086685 | -0.0080089 | 0.031217 | -0.0011172 | 0.0026914 | 0.024253 | -0.55486 | 0.021425 | -0.0074286 | -0.0079842 | -0.0045652 | 0.030222 | 0.66376 | 0.67749 | 0.58594 | 0.68665 | 0.89722 | 0.63171 | 0.4715 | -0.013733 | 0.041199 | -0.022888 | 0.19684 | 0.13733 | -0.091553 | -0.14191 | 123.0789 | 122.9187 | 0.032044 | 123.1247 | 123.1339 | 0.21515 | -0.20142 | 122.3557 | 122.3053 | -0.66833 | 122.4335 | 122.4243 | 0.11902 | -0.72784 | 123.3444 | 123.111 | 123.0331 | -0.39368 | 122.644 | 122.5845 | 122.4884 | -1.0071
862.6875 | 123.381 | -122.4518 | 0.86975 | -0.19462 | 0.10698 | 0.0048081 | 0.028013 | 0.0010188 | 0.0058954 | 0.026389 | -0.2802 | 0.016085 | -0.0031566 | -0.00050718 | -0.01311 | 0.044107 | 0.69122 | 0.71869 | 0.63171 | 0.71411 | 0.88806 | 0.65002 | 0.48981 | 0.022888 | 0.064087 | 0.004578 | 0.16937 | 0.12817 | -0.10529 | -0.15106 | 123.1018 | 122.9416 | 0.018311 | 123.1705 | 123.1659 | 0.2243 | -0.17853 | 122.3465 | 122.3007 | -0.70038 | 122.4747 | 122.4564 | 0.15564 | -0.74158 | 123.3398 | 123.143 | 123.0835 | -0.37994 | 122.6212 | 122.58 | 122.5159 | -1.0208
863.6875 | 123.3536 | -122.4518 | 0.86517 | -0.14884 | 0.12727 | 0.00053514 | 0.030149 | 0.0031548 | -0.00051261 | 0.055228 | -0.5396 | 0.025698 | -0.0052926 | 0.0069698 | -0.0024292 | 0.03129 | 0.90637 | 0.88348 | 0.6958 | 0.70496 | 0.93384 | 0.70496 | 0.54474 | 0.022888 | 0.050354 | -0.018311 | 0.16937 | 0.13275 | -0.082397 | -0.13733 | 123.1567 | 122.9965 | 0.068665 | 123.3353 | 123.1567 | 0.16022 | 0.041199 | 122.3694 | 122.3145 | -0.6958 | 122.4747 | 122.4335 | 0.11902 | -0.73242 | 123.3856 | 123.3582 | 123.1476 | -0.32043 | 122.6212 | 122.5845 | 122.5021 | -1.0025
864.7031 | 123.4039 | -122.4472 | 0.85144 | -0.39298 | 0.057846 | 0.011217 | 0.020536 | -0.0075262 | -0.022944 | 0.011435 | -0.43279 | 0.0032668 | -0.027724 | -0.0047802 | -0.0045652 | 0.037699 | 0.70038 | 0.78278 | 0.68207 | 0.74158 | 0.85144 | 0.66376 | 0.52185 | 0.036621 | 0.11902 | 0.054932 | 0.16022 | 0.10071 | -0.073242 | -0.12817 | 123.111 | 122.9691 | 0 | 123.23 | 123.1888 | 0.21973 | -0.15106 | 122.374 | 122.319 | -0.69122 | 122.4838 | 122.5021 | 0.18311 | -0.75073 | 123.2986 | 123.1476 | 123.1293 | -0.32959 | 122.6074 | 122.5479 | 122.5662 | -0.97961
865.6875 | 123.3627 | -122.4747 | 0.86975 | -0.39298 | 0.10484 | 0.0090801 | 0.032286 | -0.0075262 | 0.010168 | 0.015708 | -0.43279 | 0.017153 | -0.01277 | 0.0069698 | -0.0045652 | 0.032358 | 0.66376 | 0.70038 | 0.6134 | 0.67749 | 0.87433 | 0.63171 | 0.47607 | 0.022888 | 0.064087 | -0.013733 | 0.17395 | 0.13733 | -0.09613 | -0.16479 | 123.1064 | 122.9507 | 0.004578 | 123.175 | 123.1522 | 0.20142 | -0.20599 | 122.3785 | 122.3099 | -0.6958 | 122.4976 | 122.4609 | 0.15106 | -0.73242 | 123.349 | 123.1384 | 123.0881 | -0.39368 | 122.6486 | 122.612 | 122.5388 | -1.0345
866.6875 | 123.381 | -122.5067 | 0.8606 | -0.37772 | 0.10591 | 0.017625 | 0.031217 | -0.016071 | -0.0069216 | 0.01998 | -0.49383 | 0.023562 | -0.0074286 | -0.0026432 | -0.012042 | 0.039835 | 0.61798 | 0.66834 | 0.5722 | 0.66834 | 0.87433 | 0.60425 | 0.44403 | -0.032043 | 0.032043 | -0.050354 | 0.19226 | 0.13275 | -0.091553 | -0.17395 | 123.111 | 122.9507 | 0.013733 | 123.175 | 123.175 | 0.2243 | -0.24262 | 122.4152 | 122.3328 | -0.66834 | 122.4747 | 122.4564 | 0.1236 | -0.72785 | 123.381 | 123.1247 | 123.0789 | -0.41657 | 122.699 | 122.6395 | 122.5388 | -1.0345
867.6875 | 123.3856 | -122.4518 | 0.86517 | -0.14884 | 0.12086 | 0.00053514 | 0.036558 | -0.0075262 | 0.0016234 | 0.017844 | -0.37176 | 0.015017 | -0.0031566 | -0.0047802 | 0.0039788 | 0.030222 | 0.68207 | 0.71411 | 0.62256 | 0.70038 | 0.85144 | 0.63171 | 0.4715 | 0.036621 | 0.091553 | 0.004578 | 0.23346 | 0.1831 | -0.059509 | -0.11444 | 123.0835 | 122.9233 | -0.013733 | 123.1659 | 123.1522 | 0.22888 | -0.1831 | 122.3923 | 122.3373 | -0.63171 | 122.4884 | 122.4564 | 0.11902 | -0.68207 | 123.3032 | 123.1338 | 123.0743 | -0.39368 | 122.6852 | 122.6349 | 122.5433 | -0.97961
868.6875 | 123.381 | -122.4564 | 0.88348 | -0.13358 | 0.080276 | -0.0048049 | 0.026945 | -0.0043222 | -0.0015816 | 0.028525 | -0.31072 | 0.051333 | 4.7432e-05 | 0.014447 | 0.0039788 | 0.027017 | 0.68207 | 0.72784 | 0.62256 | 0.68665 | 0.8606 | 0.64087 | 0.46692 | 0.036621 | 0.10071 | 0.004578 | 0.22888 | 0.16479 | -0.050354 | -0.10986 | 123.0972 | 122.9233 | -0.022888 | 123.1842 | 123.143 | 0.21973 | -0.20142 | 122.406 | 122.3465 | -0.6546 | 122.493 | 122.4609 | 0.11444 | -0.71869 | 123.317 | 123.1384 | 123.0789 | -0.41657 | 122.6852 | 122.6212 | 122.5571 | -0.99335
869.7031 | 123.4543 | -122.4289 | 0.84686 | -0.11832 | 0.051437 | -0.20775 | 0.016264 | -0.019275 | -0.033625 | 0.015708 | 0.086009 | 0.01288 | -0.033064 | 0.0059018 | -0.0088382 | 0.050516 | 0.66376 | 0.78735 | 0.6958 | 0.72327 | 0.83771 | 0.66376 | 0.51727 | 0.10071 | 0.16022 | 0.10529 | 0.16479 | 0.10071 | -0.064087 | -0.11444 | 123.0927 | 122.9462 | -0.009155 | 123.2162 | 123.1522 | 0.20599 | -0.18311 | 122.3648 | 122.3145 | -0.68207 | 122.5296 | 122.5342 | 0.21973 | -0.74616 | 123.2666 | 123.0927 | 123.1247 | -0.32959 | 122.5937 | 122.5296 | 122.5891 | -0.9613
870.6875 | 123.349 | -122.4655 | 0.83313 | -0.072545 | 0.11125 | -0.0058729 | 0.034422 | -0.012866 | 0.012304 | 0.027457 | -0.24969 | 0.019289 | 0.010729 | 0.01231 | 0.013592 | 0.034494 | 0.67749 | 0.68665 | 0.58594 | 0.66376 | 0.84686 | 0.59509 | 0.47607 | 0 | 0.013733 | -0.045776 | 0.15106 | 0.11444 | -0.10071 | -0.16479 | 123.0606 | 122.9416 | 0.013733 | 123.1522 | 123.1293 | 0.18768 | -0.15564 | 122.3648 | 122.3007 | -0.68207 | 122.4655 | 122.4197 | 0.11902 | -0.71869 | 123.3124 | 123.143 | 123.0515 | -0.35706 | 122.6166 | 122.58 | 122.4792 | -0.99793
871.6875 | 123.3353 | -122.4884 | 0.82398 | -0.057287 | 0.096298 | 0.0080121 | 0.034422 | -0.0043222 | 0.010168 | 0.026389 | -0.26494 | 0.023562 | -0.0084976 | 0.011242 | 0.0071838 | 0.029154 | 0.67291 | 0.68665 | 0.58136 | 0.65918 | 0.85144 | 0.59509 | 0.46692 | 0 | 0.013733 | -0.064087 | 0.17395 | 0.1236 | -0.10986 | -0.16937 | 123.0835 | 122.9553 | 0.027465 | 123.175 | 123.1476 | 0.19226 | -0.15106 | 122.3785 | 122.319 | -0.65003 | 122.4884 | 122.4243 | 0.10529 | -0.70038 | 123.3398 | 123.1613 | 123.0698 | -0.35706 | 122.6624 | 122.612 | 122.5021 | -0.99335
872.6875 | 123.3948 | -122.5113 | 0.83771 | -0.36246 | 0.12407 | 0.0026721 | 0.029081 | -0.0053902 | -0.00051261 | 0.027457 | -0.50908 | 0.019289 | -0.011702 | 0.0069698 | -0.0002932 | 0.034494 | 0.64087 | 0.64087 | 0.57678 | 0.65002 | 0.85144 | 0.59052 | 0.46234 | 0.013733 | 0.036621 | -0.018311 | 0.17853 | 0.1236 | -0.091553 | -0.14648 | 123.1018 | 122.9736 | 0.013732 | 123.1522 | 123.1613 | 0.18768 | -0.19684 | 122.4197 | 122.3648 | -0.65918 | 122.525 | 122.493 | 0.12817 | -0.71411 | 123.3627 | 123.1522 | 123.0881 | -0.37537 | 122.6898 | 122.6349 | 122.5479 | -0.98419
873.6875 | 123.3582 | -122.493 | 0.83771 | -2.2698 | 0.07814 | -0.0037369 | 0.032286 | -0.0096622 | -0.0047856 | 0.023184 | -0.47857 | 0.01288 | -0.0010206 | 0.0048338 | -0.0056342 | 0.03663 | 0.59967 | 0.66376 | 0.56305 | 0.64545 | 0.88806 | 0.61798 | 0.48065 | -0.027466 | 0.022888 | -0.045776 | 0.19684 | 0.14648 | -0.11444 | -0.16937 | 123.111 | 122.9736 | 0.050354 | 123.1567 | 123.1384 | 0.16479 | -0.23804 | 122.3785 | 122.3236 | -0.64087 | 122.4655 | 122.4472 | 0.1236 | -0.69122 | 123.381 | 123.0927 | 123.056 | -0.35706 | 122.6898 | 122.6395 | 122.5159 | -1.0071
874.7031 | 123.4451 | -122.4609 | 0.83771 | 0.14108 | 0.070663 | -0.20988 | 0.0087873 | -0.012866 | -0.026148 | 0.01998 | 0.28437 | 0.0064718 | -0.019179 | -0.016529 | -0.0077702 | 0.047312 | 0.51727 | 0.71411 | 0.60425 | 0.6546 | 0.7782 | 0.55847 | 0.42572 | 0.045776 | 0.073242 | 0.050354 | 0.17395 | 0.1236 | -0.07782 | -0.15106 | 123.0194 | 122.8867 | -0.05951 | 123.175 | 123.1155 | 0.22888 | -0.32044 | 122.3831 | 122.3099 | -0.66376 | 122.5067 | 122.5113 | 0.20142 | -0.71411 | 123.2391 | 122.9782 | 123.0652 | -0.41199 | 122.6349 | 122.5845 | 122.5342 | -0.98877
875.6875 | 123.3582 | -122.4884 | 0.81024 | 0.29367 | 0.11125 | -0.0026689 | 0.030149 | -0.0043222 | 0.011236 | 0.022116 | -0.31072 | 0.018221 | -0.0031566 | -0.011188 | -0.0013612 | 0.027017 | 0.67291 | 0.66376 | 0.57678 | 0.63629 | 0.85144 | 0.60425 | 0.44861 | 0.018311 | 0.027466 | -0.022888 | 0.17853 | 0.11444 | -0.091553 | -0.15564 | 123.0927 | 122.937 | 0.041198 | 123.1522 | 123.1247 | 0.18768 | -0.13733 | 122.3969 | 122.3328 | -0.63171 | 122.5067 | 122.4655 | 0.13275 | -0.6958 | 123.3398 | 123.1613 | 123.0652 | -0.36163 | 122.6669 | 122.6028 | 122.5159 | -0.96588
876.6875 | 123.3948 | -122.493 | 0.82398 | -0.14884 | 0.09523 | -0.0037369 | 0.020536 | -0.0053902 | 0.0091004 | 0.027457 | -0.43279 | 0.015017 | -0.019179 | -0.0090522 | 0.0029108 | 0.029154 | 0.65002 | 0.66834 | 0.59509 | 0.6546 | 0.83313 | 0.59052 | 0.45776 | 0.036621 | 0.064087 | -0.009155 | 0.16937 | 0.11902 | -0.086975 | -0.14648 | 123.0835 | 122.9507 | 0.009155 | 123.1613 | 123.1476 | 0.19684 | -0.17395 | 122.406 | 122.3465 | -0.6546 | 122.5296 | 122.4838 | 0.13733 | -0.70496 | 123.3261 | 123.143 | 123.0881 | -0.36621 | 122.6624 | 122.612 | 122.5571 | -0.97046
877.6875 | 123.3902 | -122.5113 | 0.82398 | -0.28617 | 0.10377 | -0.010146 | 0.026945 | -0.0032532 | 0.0091004 | 0.030661 | -0.43279 | 0.0096758 | -0.014906 | -0.0037112 | 0.0018428 | 0.033426 | 0.65918 | 0.67749 | 0.59509 | 0.65918 | 0.83771 | 0.59967 | 0.43945 | 0.036621 | 0.045776 | -0.004578 | 0.17853 | 0.1236 | -0.091553 | -0.15564 | 123.111 | 122.9507 | 0.013733 | 123.1888 | 123.1705 | 0.21973 | -0.1648 | 122.4197 | 122.3557 | -0.64545 | 122.5479 | 122.5067 | 0.15106 | -0.70038 | 123.349 | 123.1705 | 123.1064 | -0.38452 | 122.6898 | 122.6349 | 122.5571 | -0.97962
878.6875 | 123.3627 | -122.5204 | 0.82855 | -1.5526 | 0.097366 | 0.014421 | 0.025877 | -0.0085942 | 0.011236 | 0.024253 | -0.18865 | 0.010744 | -0.01277 | 0.00056082 | 0.010388 | 0.037699 | 0.68207 | 0.68207 | 0.60425 | 0.65002 | 0.85602 | 0.63171 | 0.47607 | 0.018311 | 0.041199 | -0.036621 | 0.17853 | 0.12817 | -0.09613 | -0.16937 | 123.1522 | 122.9965 | 0.027466 | 123.2025 | 123.1705 | 0.17395 | -0.14648 | 122.4243 | 122.3511 | -0.65002 | 122.5388 | 122.4838 | 0.13275 | -0.70038 | 123.3765 | 123.2025 | 123.1247 | -0.35248 | 122.699 | 122.6486 | 122.5616 | -0.99792
879.7031 | 123.3582 | -122.5296 | 0.85144 | -0.24039 | 0.080276 | -0.0026689 | 0.017332 | -0.0011172 | -0.01974 | 0.023184 | -0.46331 | 0.0075398 | -0.0095656 | -0.01012 | -0.0056342 | 0.03663 | 0.52643 | 0.65918 | 0.55389 | 0.6134 | 0.84686 | 0.57678 | 0.43945 | -0.022888 | 0.018311 | -0.036621 | 0.20599 | 0.14191 | -0.10986 | -0.16937 | 123.1064 | 122.9691 | -0.004577 | 123.1888 | 123.143 | 0.17395 | -0.32501 | 122.4197 | 122.3602 | -0.64545 | 122.5067 | 122.493 | 0.13275 | -0.70953 | 123.3765 | 123.056 | 123.0835 | -0.41199 | 122.7356 | 122.6715 | 122.5479 | -1.0208
880.6875 | 123.3902 | -122.5204 | 0.81482 | -0.39298 | 0.097366 | -0.010146 | 0.019468 | -0.011798 | -0.0047856 | 0.014639 | -0.55486 | 0.0086078 | 0.0021844 | -0.0015752 | -0.0056342 | 0.028086 | 0.58136 | 0.61798 | 0.53101 | 0.63629 | 0.81482 | 0.57678 | 0.41657 | -0.018311 | 0.027466 | -0.032043 | 0.17853 | 0.12817 | -0.11902 | -0.16479 | 123.0972 | 122.937 | 0 | 123.1384 | 123.1567 | 0.21973 | -0.23346 | 122.4014 | 122.3557 | -0.63629 | 122.5021 | 122.4884 | 0.13275 | -0.68664 | 123.3353 | 123.1018 | 123.0515 | -0.39825 | 122.699 | 122.6486 | 122.5479 | -0.97961
881.6875 | 123.3627 | -122.5159 | 0.79193 | -0.1641 | 0.09523 | 0.0048081 | 0.0045153 | -0.01073 | 0.0091004 | 0.023184 | -0.34124 | 0.019289 | 0.0096604 | 0.0048338 | 0.0018428 | 0.028086 | 0.64087 | 0.70953 | 0.60425 | 0.66376 | 0.88806 | 0.64545 | 0.50354 | 0.018311 | 0.050354 | -0.027466 | 0.16937 | 0.11902 | -0.09613 | -0.16479 | 123.1613 | 123.0194 | 0.096131 | 123.2254 | 123.1796 | 0.16022 | -0.15106 | 122.4197 | 122.3511 | -0.62256 | 122.5342 | 122.4884 | 0.13733 | -0.67291 | 123.4039 | 123.1567 | 123.1201 | -0.28839 | 122.6852 | 122.6349 | 122.5662 | -0.95673
882.6875 | 123.3398 | -122.5296 | 0.81024 | 0.034266 | 0.09523 | 0.00053514 | 0.025877 | 0.0010188 | 0.0058954 | 0.022116 | -0.20391 | 0.013948 | -0.011702 | 0.010174 | 0.0082518 | 0.033426 | 0.58594 | 0.6134 | 0.53558 | 0.61798 | 0.82398 | 0.55389 | 0.41657 | -0.027466 | -0.013733 | -0.082397 | 0.16937 | 0.1236 | -0.10529 | -0.1831 | 123.0835 | 122.9462 | 0.013733 | 123.143 | 123.1476 | 0.20142 | -0.2243 | 122.4243 | 122.3465 | -0.64087 | 122.5021 | 122.4472 | 0.10071 | -0.68665 | 123.3536 | 123.1155 | 123.0652 | -0.39368 | 122.699 | 122.6532 | 122.5159 | -0.99335
883.6875 | 123.349 | -122.5296 | 0.79193 | 0.034266 | 0.11232 | 0.012285 | 0.021604 | -0.0085942 | 0.0037594 | 0.01998 | -0.05132 | 0.015017 | -0.0020886 | 0.0091058 | -0.0056342 | 0.033426 | 0.60425 | 0.59967 | 0.53101 | 0.59509 | 0.82855 | 0.55847 | 0.40741 | -0.027466 | -0.027466 | -0.064087 | 0.17395 | 0.13275 | -0.09613 | -0.16479 | 123.0881 | 122.937 | 0.036621 | 123.1293 | 123.1247 | 0.18768 | -0.18768 | 122.4335 | 122.3648 | -0.61798 | 122.5021 | 122.4655 | 0.10071 | -0.65918 | 123.3582 | 123.1338 | 123.0606 | -0.38452 | 122.7036 | 122.6624 | 122.5021 | -0.95673
884.6875 | 123.3398 | -122.5571 | 0.80566 | 0.11056 | 0.10057 | -0.0058729 | 0.037626 | -0.011798 | 0.01444 | 0.031729 | -0.005544 | 0.020357 | -0.0020886 | 0.0059018 | 0.0029108 | 0.040903 | 0.56305 | 0.54932 | 0.49439 | 0.59509 | 0.80566 | 0.55389 | 0.41199 | -0.059509 | -0.050354 | -0.09613 | 0.16479 | 0.12817 | -0.10986 | -0.15564 | 123.111 | 122.9691 | 0 | 123.1064 | 123.1522 | 0.18311 | -0.24262 | 122.4472 | 122.4014 | -0.64087 | 122.4976 | 122.4609 | 0.05951 | -0.67749 | 123.3627 | 123.1201 | 123.0515 | -0.39368 | 122.7219 | 122.6852 | 122.5067 | -0.9613
885.6875 | 123.3719 | -122.5159 | 0.8194 | -0.1641 | 0.087753 | 0.0026721 | 0.037626 | -0.017139 | 0.0048274 | 0.028525 | -0.47857 | 0.025698 | 0.0043204 | -0.0015752 | 0.0018428 | 0.030222 | 0.64087 | 0.64545 | 0.55847 | 0.64087 | 0.80109 | 0.56305 | 0.42114 | 0.054932 | 0.082397 | 0.009155 | 0.23346 | 0.17395 | -0.054932 | -0.11902 | 123.0789 | 122.937 | -0.018311 | 123.1613 | 123.1567 | 0.21973 | -0.17853 | 122.4609 | 122.3969 | -0.58594 | 122.5708 | 122.525 | 0.12817 | -0.64545 | 123.317 | 123.1567 | 123.0743 | -0.39825 | 122.7493 | 122.6898 | 122.5983 | -0.93842
886.6875 | 123.3994 | -122.5204 | 0.83313 | -0.20987 | 0.088821 | 0.0048081 | 0.026945 | -0.01073 | 0.011236 | 0.024253 | -0.24969 | 0.018221 | -0.0010206 | 0.0059018 | 0.0018428 | 0.03663 | 0.62256 | 0.65002 | 0.56305 | 0.63171 | 0.81024 | 0.55847 | 0.4303 | 0.082397 | 0.050354 | 0.013733 | 0.23804 | 0.17853 | -0.045776 | -0.10071 | 123.0789 | 122.9507 | -0.022888 | 123.1705 | 123.1522 | 0.20142 | -0.21057 | 122.4747 | 122.4197 | -0.59509 | 122.6028 | 122.5342 | 0.11444 | -0.6546 | 123.3307 | 123.143 | 123.0835 | -0.40283 | 122.7585 | 122.699 | 122.5708 | -0.93384
887.6875 | 123.3673 | -122.5525 | 0.80109 | 0.034266 | 0.13048 | 0.0069441 | 0.032286 | -0.0053902 | 0.0058954 | 0.021048 | -0.21917 | 0.018221 | 0.0053884 | 0.0069698 | -0.0013612 | 0.032358 | 0.6134 | 0.63171 | 0.54932 | 0.61798 | 0.78735 | 0.56305 | 0.40741 | -0.009155 | 0.004578 | -0.050354 | 0.16479 | 0.13733 | -0.12817 | -0.18768 | 123.1155 | 122.9599 | -0.013732 | 123.1842 | 123.1705 | 0.21057 | -0.18768 | 122.4243 | 122.3648 | -0.63629 | 122.5433 | 122.5021 | 0.13733 | -0.66376 | 123.3398 | 123.1659 | 123.1018 | -0.39368 | 122.7173 | 122.6898 | 122.5571 | -0.98877
888.6875 | 123.3261 | -122.5708 | 0.80566 | 0.11056 | 0.084549 | -0.0048049 | 0.024809 | -0.013935 | 0.012304 | 0.028525 | -0.066579 | 0.023562 | 0.0053884 | 0.015515 | -0.0034972 | 0.032358 | 0.56305 | 0.55847 | 0.48981 | 0.57678 | 0.7782 | 0.55389 | 0.40283 | -0.045776 | -0.027466 | -0.09613 | 0.17395 | 0.14191 | -0.10529 | -0.17395 | 123.1247 | 122.9736 | -0.027466 | 123.1293 | 123.1476 | 0.17395 | -0.24262 | 122.4655 | 122.3969 | -0.63171 | 122.525 | 122.4747 | 0.07782 | -0.66376 | 123.349 | 123.1339 | 123.0606 | -0.40283 | 122.7448 | 122.7127 | 122.5433 | -0.97961
889.7031 | 123.4406 | -122.4976 | 0.78278 | 0.40048 | 0.065323 | 0.0048081 | 0.011991 | -0.017139 | -0.018671 | 0.015708 | 0.498 | 0.020357 | -0.018111 | -0.0026432 | -0.01311 | 0.050516 | 0.61798 | 0.68665 | 0.62256 | 0.63629 | 0.77362 | 0.59967 | 0.44861 | 0.07782 | 0.10071 | 0.064087 | 0.13733 | 0.10071 | -0.064087 | -0.12817 | 123.0972 | 122.9462 | -0.009155 | 123.1842 | 123.1339 | 0.18768 | -0.1648 | 122.4335 | 122.3694 | -0.64545 | 122.5754 | 122.5616 | 0.19226 | -0.68207 | 123.2712 | 123.1155 | 123.1201 | -0.33417 | 122.6349 | 122.5983 | 122.5983 | -0.91095
890.6875 | 123.381 | -122.5571 | 0.76904 | 0.0037495 | 0.098434 | -0.011214 | 0.019468 | -0.012866 | 0.01444 | 0.013571 | -0.2802 | 0.02463 | 4.7432e-05 | -0.011188 | 0.0050478 | 0.020609 | 0.62714 | 0.62714 | 0.54016 | 0.60883 | 0.80566 | 0.55389 | 0.41657 | 0.022888 | 0.013733 | -0.041199 | 0.17395 | 0.10986 | -0.091553 | -0.16022 | 123.111 | 122.9736 | 0.036621 | 123.1842 | 123.1659 | 0.19226 | -0.14191 | 122.4655 | 122.3969 | -0.59509 | 122.58 | 122.5159 | 0.11902 | -0.65918 | 123.3627 | 123.1842 | 123.0972 | -0.35248 | 122.731 | 122.6669 | 122.5708 | -0.92926
891.6875 | 123.3398 | -122.612 | 0.7782 | 0.034266 | 0.10377 | -0.0026689 | 0.020536 | -0.0021852 | 0.00055539 | 0.024253 | -0.14287 | 0.013948 | 0.0085924 | 0.0069698 | 0.011456 | 0.040903 | 0.58136 | 0.56305 | 0.50812 | 0.56763 | 0.7782 | 0.54016 | 0.39825 | -0.045776 | -0.018311 | -0.082397 | 0.16937 | 0.1236 | -0.11444 | -0.17395 | 123.1522 | 123.0103 | 0 | 123.175 | 123.1796 | 0.16937 | -0.19684 | 122.4976 | 122.438 | -0.60882 | 122.5662 | 122.5296 | 0.091553 | -0.6546 | 123.3902 | 123.1934 | 123.1201 | -0.37994 | 122.7814 | 122.7356 | 122.5937 | -0.95215
892.6875 | 123.3765 | -122.5525 | 0.77362 | -1.1864 | 0.10911 | 0.0058761 | 0.028013 | -0.0064582 | 0.013372 | 0.045615 | -0.15813 | 0.022493 | 0.0043204 | 0.0016288 | 0.0029108 | 0.030222 | 0.63629 | 0.63629 | 0.54474 | 0.59509 | 0.82398 | 0.57678 | 0.44861 | 0.022888 | 0.041199 | -0.041199 | 0.17395 | 0.11902 | -0.09613 | -0.15564 | 123.1293 | 123.0011 | 0.050354 | 123.1888 | 123.1476 | 0.14648 | -0.13733 | 122.4564 | 122.3969 | -0.59967 | 122.5754 | 122.5113 | 0.11444 | -0.6546 | 123.3765 | 123.1888 | 123.0972 | -0.32501 | 122.7264 | 122.6715 | 122.5937 | -0.92926
893.6875 | 123.381 | -122.5616 | 0.75989 | 0.99557 | 0.10698 | -0.0016009 | 0.026945 | -0.0053902 | 0.0037594 | 0.028525 | -0.20391 | 0.018221 | -0.018111 | 0.0037648 | 0.0071838 | 0.032358 | 0.64087 | 0.64087 | 0.55847 | 0.60883 | 0.83313 | 0.58136 | 0.45319 | 0.022888 | 0.054932 | -0.018311 | 0.20142 | 0.10986 | -0.10529 | -0.16479 | 123.143 | 123.0148 | 0.073242 | 123.2025 | 123.1705 | 0.15564 | -0.11902 | 122.4564 | 122.3969 | -0.55847 | 122.5845 | 122.5433 | 0.14648 | -0.65002 | 123.3948 | 123.2025 | 123.1201 | -0.3067 | 122.7631 | 122.6715 | 122.6166 | -0.92468
894.7031 | 123.4314 | -122.5525 | 0.75531 | 0.24789 | 0.063186 | 0.022966 | 0.0098553 | -0.011798 | -0.029353 | 0.012503 | 0.22334 | 0.0075398 | -0.020247 | -0.0037112 | -0.012042 | 0.04838 | 0.58594 | 0.6546 | 0.5722 | 0.6134 | 0.76904 | 0.5722 | 0.42572 | 0.041199 | 0.041199 | 0.036621 | 0.16022 | 0.10529 | -0.068665 | -0.13275 | 123.1247 | 122.9782 | 0.013733 | 123.2071 | 123.1659 | 0.18768 | -0.16937 | 122.4838 | 122.4197 | -0.59509 | 122.5937 | 122.5891 | 0.16937 | -0.65002 | 123.3215 | 123.1384 | 123.1247 | -0.32959 | 122.7127 | 122.6578 | 122.5937 | -0.88806
895.6875 | 123.349 | -122.5983 | 0.78278 | 0.1716 | 0.1262 | 0.0080121 | 0.030149 | -0.029956 | 0.012304 | 0.031729 | 0.040232 | 0.0032668 | -0.0052926 | -0.0026432 | 0.015729 | 0.023813 | 0.5127 | 0.5127 | 0.46234 | 0.54016 | 0.79193 | 0.55389 | 0.3891 | -0.027466 | -0.032043 | -0.086975 | 0.19226 | 0.11902 | -0.11444 | -0.17395 | 123.1522 | 122.9874 | 0.009155 | 123.111 | 123.1384 | 0.15106 | -0.27008 | 122.4838 | 122.4243 | -0.59052 | 122.5708 | 122.5113 | 0.086975 | -0.66376 | 123.3902 | 123.111 | 123.0606 | -0.39368 | 122.7905 | 122.7173 | 122.5662 | -0.95673
896.6875 | 123.3582 | -122.612 | 0.76904 | 0.24789 | 0.10484 | -0.0037369 | -0.0093707 | -0.012866 | -0.0069216 | 0.028525 | 0.29963 | 0.027834 | -0.01277 | 0.0026968 | -0.0045652 | 0.037699 | 0.49439 | 0.56763 | 0.48523 | 0.5722 | 0.80566 | 0.54932 | 0.39368 | -0.009155 | -0.041199 | -0.054932 | 0.16937 | 0.1236 | -0.09613 | -0.16479 | 123.1613 | 123.0057 | 0.036621 | 123.1796 | 123.1842 | 0.17853 | -0.27466 | 122.5159 | 122.4472 | -0.59967 | 122.6028 | 122.5571 | 0.10986 | -0.64545 | 123.4177 | 123.1064 | 123.0972 | -0.37537 | 122.7814 | 122.7356 | 122.5708 | -0.93384
897.6875 | 123.349 | -122.5983 | 0.77362 | 0.1716 | 0.11659 | 0.0016041 | 0.038694 | -0.011798 | 0.0091004 | 0.043479 | -0.005544 | 0.02997 | -0.0020886 | 0.0026968 | 0.0082518 | 0.039835 | 0.53558 | 0.48523 | 0.45319 | 0.54474 | 0.76904 | 0.51727 | 0.36621 | -0.050354 | -0.064087 | -0.11444 | 0.1831 | 0.13733 | -0.10529 | -0.16022 | 123.1155 | 122.9645 | -0.004578 | 123.0835 | 123.143 | 0.17853 | -0.23804 | 122.493 | 122.4381 | -0.59052 | 122.5479 | 122.4838 | 0.045776 | -0.63629 | 123.3673 | 123.1339 | 123.0515 | -0.40741 | 122.7814 | 122.7356 | 122.5342 | -0.93384
898.6875 | 123.3536 | -122.6028 | 0.75073 | -0.042028 | 0.096298 | 0.022966 | 0.031217 | -0.015003 | 0.0058954 | 0.029593 | -0.17339 | 0.016085 | -0.0031566 | 0.014447 | 0.0039788 | 0.027017 | 0.59052 | 0.57678 | 0.49896 | 0.5722 | 0.77362 | 0.50812 | 0.37537 | -0.009155 | -0.004578 | -0.059509 | 0.16937 | 0.11902 | -0.10071 | -0.16022 | 123.111 | 122.9782 | 0.022889 | 123.1796 | 123.175 | 0.19684 | -0.16022 | 122.5021 | 122.4426 | -0.58136 | 122.5937 | 122.5433 | 0.10071 | -0.63171 | 123.3765 | 123.1934 | 123.1018 | -0.37537 | 122.7722 | 122.7219 | 122.5983 | -0.91095
899.7031 | 123.4268 | -122.5433 | 0.74616 | 0.049525 | 0.09523 | 0.02083 | 0.0184 | -0.031024 | -0.041102 | 0.021048 | 0.17756 | 0.0043348 | -0.026655 | 0.010174 | -0.01311 | 0.049448 | 0.54016 | 0.62256 | 0.55389 | 0.57678 | 0.737 | 0.53558 | 0.41199 | 0.036621 | 0.068665 | 0.027466 | 0.16479 | 0.11902 | -0.086975 | -0.11902 | 123.0789 | 122.9553 | -0.009155 | 123.1659 | 123.1201 | 0.1648 | -0.20599 | 122.4564 | 122.4243 | -0.58136 | 122.58 | 122.5708 | 0.14649 | -0.62714 | 123.2803 | 123.0835 | 123.0972 | -0.33417 | 122.7081 | 122.6624 | 122.612 | -0.86517
900.6875 | 123.3353 | -122.4976 | 0.79651 | -0.11832 | 0.11232 | 0.0026721 | 0.015196 | -0.011798 | 0.015508 | 0.032797 | -0.41753 | 0.020357 | -0.019179 | 0.0048338 | 0.0007748 | 0.028086 | 0.58594 | 0.6134 | 0.5127 | 0.58136 | 0.75531 | 0.50812 | 0.36621 | 0.036621 | 0.054932 | -0.027466 | 0.17395 | 0.1236 | -0.091553 | -0.16022 | 123.0057 | 122.8638 | -0.041199 | 123.111 | 123.0789 | 0.21515 | -0.21057 | 122.406 | 122.3373 | -0.62256 | 122.5342 | 122.4701 | 0.13275 | -0.67291 | 123.2529 | 123.0835 | 123.0103 | -0.4303 | 122.6715 | 122.6212 | 122.5525 | -0.95673
901.6875 | 123.3856 | -122.5891 | 0.74158 | -0.69816 | 0.09523 | 0.0090801 | 0.029081 | -0.016071 | 0.0091004 | 0.021048 | -0.29546 | 0.017153 | -0.0063606 | -0.00050718 | 0.010388 | 0.022745 | 0.59052 | 0.58594 | 0.49896 | 0.56305 | 0.80109 | 0.52643 | 0.39825 | 0.027466 | 0.022888 | -0.036621 | 0.16479 | 0.11902 | -0.10986 | -0.16022 | 123.1155 | 122.9874 | 0.059509 | 123.175 | 123.1522 | 0.1648 | -0.15106 | 122.4792 | 122.4289 | -0.57678 | 122.6166 | 122.5525 | 0.1236 | -0.62256 | 123.3902 | 123.1796 | 123.0881 | -0.34332 | 122.7539 | 122.7081 | 122.612 | -0.90179
902.6875 | 123.3536 | -122.6303 | 0.73242 | 0.049525 | 0.14116 | 0.0080121 | 0.036558 | -0.01073 | 0.0069634 | 0.027457 | -0.17339 | 0.021425 | -0.0052926 | -0.0037112 | -0.0077702 | 0.028086 | 0.54474 | 0.54474 | 0.46234 | 0.54932 | 0.75073 | 0.48523 | 0.34332 | -0.032043 | -0.013733 | -0.086975 | 0.1831 | 0.1236 | -0.10986 | -0.1831 | 123.1155 | 122.9736 | 0.01831 | 123.175 | 123.1796 | 0.20599 | -0.18768 | 122.5204 | 122.4472 | -0.54932 | 122.5983 | 122.5433 | 0.09613 | -0.60883 | 123.381 | 123.175 | 123.0927 | -0.3891 | 122.8134 | 122.7539 | 122.6166 | -0.91553
903.6875 | 123.3261 | -122.6303 | 0.74616 | 0.080043 | 0.12514 | 0.0037401 | 0.025877 | -0.0043222 | 0.016576 | 0.024253 | -0.081838 | 0.01288 | -0.013838 | 0.0016288 | 0.0039788 | 0.034494 | 0.48981 | 0.4715 | 0.43488 | 0.5127 | 0.75989 | 0.48981 | 0.35706 | -0.022888 | -0.027466 | -0.082397 | 0.19226 | 0.13733 | -0.10986 | -0.17395 | 123.1201 | 122.9874 | 0.013733 | 123.1018 | 123.143 | 0.15564 | -0.25635 | 122.5204 | 122.4564 | -0.55389 | 122.6074 | 122.5479 | 0.091553 | -0.60883 | 123.3902 | 123.1201 | 123.0652 | -0.3891 | 122.8226 | 122.7676 | 122.6028 | -0.9201
904.7031 | 123.4039 | -122.6761 | 0.66376 | 0.095301 | 0.086685 | 0.011217 | 0.021604 | -0.023548 | -0.037898 | 0.015708 | 0.11653 | 0.0021988 | -0.014906 | 0.0016288 | 0.0039788 | 0.041971 | 0.53558 | 0.59052 | 0.53101 | 0.57678 | 0.73242 | 0.53101 | 0.37537 | 0.036621 | 0.068665 | 0.032043 | 0.14648 | 0.09613 | -0.07782 | -0.14648 | 123.2071 | 123.0515 | 0.068665 | 123.2666 | 123.2529 | 0.20142 | -0.12817 | 122.5983 | 122.5296 | -0.51727 | 122.7127 | 122.7081 | 0.17853 | -0.56763 | 123.4085 | 123.2117 | 123.2071 | -0.28839 | 122.8226 | 122.7722 | 122.7448 | -0.81024
905.6875 | 123.3765 | -122.6212 | 0.737 | -0.057287 | 0.092026 | 0.0026721 | 0.031217 | -0.0064582 | 0.018713 | 0.027457 | -0.20391 | 0.011812 | -0.0042246 | 0.01231 | 0.011456 | 0.028086 | 0.57678 | 0.5722 | 0.48523 | 0.55847 | 0.71869 | 0.49439 | 0.33875 | -0.004578 | 0.013733 | -0.059509 | 0.16479 | 0.11444 | -0.11444 | -0.16937 | 123.1155 | 122.9599 | -0.018311 | 123.1934 | 123.1796 | 0.21973 | -0.16022 | 122.5067 | 122.4518 | -0.5722 | 122.6166 | 122.5616 | 0.10986 | -0.62256 | 123.3398 | 123.1979 | 123.1064 | -0.39825 | 122.7859 | 122.7356 | 122.6349 | -0.90637
906.6875 | 123.3398 | -122.6395 | 0.737 | 0.080043 | 0.099502 | 0.0069441 | 0.025877 | -0.012866 | -0.0015816 | 0.022116 | 0.009715 | 0.02463 | -0.011702 | 0.0091058 | 0.0061158 | 0.03663 | 0.53101 | 0.52185 | 0.43945 | 0.51727 | 0.73242 | 0.48981 | 0.33417 | -0.027466 | -0.032043 | -0.073242 | 0.16937 | 0.1236 | -0.11444 | -0.17853 | 123.1293 | 122.9736 | -0.004578 | 123.1613 | 123.1567 | 0.18311 | -0.20599 | 122.525 | 122.4609 | -0.56763 | 122.612 | 122.5662 | 0.10529 | -0.6134 | 123.3719 | 123.1705 | 123.0789 | -0.40283 | 122.8088 | 122.7631 | 122.6074 | -0.91553
907.6875 | 123.3719 | -122.6532 | 0.737 | 0.034266 | 0.10911 | -0.0026689 | 0.025877 | -0.0032532 | 0.013372 | 0.021048 | -0.12761 | 0.016085 | -0.0010206 | 0.011242 | 0.0061158 | 0.025949 | 0.52643 | 0.53101 | 0.45776 | 0.53101 | 0.72784 | 0.48065 | 0.32959 | -0.022888 | -0.009155 | -0.073242 | 0.17853 | 0.10071 | -0.11902 | -0.16479 | 123.1339 | 122.9828 | -0.009156 | 123.1842 | 123.1842 | 0.20142 | -0.21057 | 122.5342 | 122.4884 | -0.55847 | 122.6303 | 122.58 | 0.091553 | -0.63629 | 123.381 | 123.1796 | 123.111 | -0.40741 | 122.8317 | 122.7539 | 122.644 | -0.9018
908.6875 | 123.3444 | -122.6212 | 0.72327 | 0.14108 | 0.10484 | -0.0016009 | 0.030149 | -0.015003 | 0.0026914 | 0.018912 | 0.14704 | 0.011812 | -0.0010206 | 0.0037648 | 0.0039788 | 0.037699 | 0.5127 | 0.48523 | 0.41657 | 0.51727 | 0.75531 | 0.46692 | 0.31128 | -0.059509 | -0.050354 | -0.10986 | 0.19226 | 0.15564 | -0.086975 | -0.16022 | 123.0881 | 122.9324 | 0.032043 | 123.1064 | 123.1384 | 0.20599 | -0.21057 | 122.5342 | 122.4609 | -0.53101 | 122.5616 | 122.5113 | 0.050354 | -0.56763 | 123.3765 | 123.1338 | 123.0377 | -0.41199 | 122.8134 | 122.7768 | 122.5708 | -0.88348
909.7031 | 123.468 | -122.5754 | 0.70038 | 0.41574 | 0.053573 | 0.011217 | 0.0023783 | -0.012866 | -0.014399 | 0.017844 | 0.1623 | 0.011812 | -0.0095656 | 0.0069698 | 0.0007748 | 0.046244 | 0.63629 | 0.63629 | 0.55389 | 0.59052 | 0.6546 | 0.48523 | 0.35248 | 0.086975 | 0.11444 | 0.054932 | 0.14648 | 0.091553 | -0.059509 | -0.1236 | 123.0606 | 122.9279 | -0.045776 | 123.2117 | 123.1659 | 0.23804 | -0.064086 | 122.5159 | 122.4518 | -0.55389 | 122.6624 | 122.6303 | 0.17853 | -0.60882 | 123.23 | 123.2117 | 123.1293 | -0.3479 | 122.7219 | 122.6669 | 122.6898 | -0.82397
910.6875 | 123.3124 | -122.6395 | 0.70496 | -0.01151 | 0.11232 | 0.0058761 | 0.024809 | -0.0021852 | 0.0058954 | 0.026389 | -0.14287 | 0.015017 | 0.0075244 | -0.0026432 | 0.010388 | 0.028086 | 0.53558 | 0.48523 | 0.42572 | 0.49896 | 0.73242 | 0.45776 | 0.32959 | -0.027466 | -0.050354 | -0.091553 | 0.1831 | 0.11902 | -0.11444 | -0.17395 | 123.0972 | 122.9691 | 0.027466 | 123.1247 | 123.1384 | 0.16937 | -0.16937 | 122.525 | 122.4655 | -0.52185 | 122.612 | 122.5479 | 0.082397 | -0.58594 | 123.3719 | 123.175 | 123.0652 | -0.37537 | 122.8226 | 122.7585 | 122.5891 | -0.87891
911.6875 | 123.3124 | -122.58 | 0.72784 | -0.01151 | 0.10698 | -0.00053286 | 0.023741 | -0.0043222 | -0.0026496 | 0.017844 | 0.07075 | 0.020357 | -0.014906 | 0.0026968 | -0.010974 | 0.040903 | 0.49439 | 0.45776 | 0.39368 | 0.50812 | 0.737 | 0.4715 | 0.33875 | -0.018311 | -0.054932 | -0.07782 | 0.18768 | 0.11902 | -0.11902 | -0.17395 | 123.0515 | 122.9187 | 0.009156 | 123.0377 | 123.0881 | 0.16937 | -0.23346 | 122.4609 | 122.406 | -0.54016 | 122.5616 | 122.5021 | 0.09613 | -0.60883 | 123.317 | 123.0743 | 122.9736 | -0.3891 | 122.7676 | 122.699 | 122.525 | -0.90179
912.6875 | 123.3353 | -122.6486 | 0.72784 | 0.26315 | 0.11766 | -0.0080089 | 0.013059 | -0.011798 | 0.0069634 | 0.025321 | 0.086009 | 0.016085 | 0.0096604 | -0.0026432 | 0.0018428 | 0.045175 | 0.48523 | 0.44861 | 0.40741 | 0.50354 | 0.73242 | 0.45776 | 0.3067 | -0.022888 | -0.036621 | -0.082397 | 0.16479 | 0.12817 | -0.10986 | -0.16937 | 123.1064 | 122.9553 | 0.004578 | 123.0972 | 123.1522 | 0.19684 | -0.24262 | 122.5388 | 122.4792 | -0.56305 | 122.6257 | 122.5662 | 0.086976 | -0.59967 | 123.381 | 123.1339 | 123.056 | -0.42114 | 122.8134 | 122.7768 | 122.612 | -0.89722
913.6875 | 123.3765 | -122.6532 | 0.71869 | -0.087804 | 0.11125 | 0.0080121 | 0.029081 | -0.018207 | 0.0080314 | 0.032797 | -0.036062 | 0.018221 | -0.0042246 | 0.01231 | 0.011456 | 0.039835 | 0.55389 | 0.52643 | 0.44403 | 0.53101 | 0.72327 | 0.48981 | 0.33875 | -0.009155 | 0.004578 | -0.059509 | 0.17395 | 0.13733 | -0.10986 | -0.16479 | 123.143 | 122.9919 | 0.004578 | 123.1796 | 123.1842 | 0.19226 | -0.1648 | 122.5433 | 122.4884 | -0.54474 | 122.644 | 122.5937 | 0.10529 | -0.58136 | 123.3765 | 123.2071 | 123.0972 | -0.37994 | 122.8271 | 122.7905 | 122.6578 | -0.88348
914.7031 | 123.436 | -122.5845 | 0.70496 | 0.30892 | 0.058914 | 0.0069441 | -0.0040297 | -0.021411 | -0.027216 | 0.01998 | 0.40644 | -0.0020732 | -0.0095656 | 0.0069698 | -0.0024292 | 0.037699 | 0.5722 | 0.62256 | 0.54932 | 0.5722 | 0.68665 | 0.52643 | 0.37079 | 0.068665 | 0.086975 | 0.059509 | 0.16022 | 0.1236 | -0.073242 | -0.13275 | 123.111 | 122.9553 | -0.01831 | 123.2071 | 123.1567 | 0.20142 | -0.13275 | 122.5113 | 122.4518 | -0.54474 | 122.6532 | 122.644 | 0.19226 | -0.58136 | 123.2712 | 123.1567 | 123.1339 | -0.33417 | 122.7448 | 122.7081 | 122.6715 | -0.83771
915.6875 | 123.4451 | -122.5479 | 0.78735 | -0.22513 | 0.1198 | 0.0026721 | 0.03549 | -0.016071 | 0.010168 | 0.023184 | -0.38701 | 0.0075398 | -0.0020886 | 0.011242 | 0.0082518 | 0.030222 | 0.5722 | 0.54932 | 0.4715 | 0.54932 | 0.72327 | 0.4715 | 0.33417 | 0.032043 | 0.059509 | -0.022888 | 0.17853 | 0.12817 | -0.07782 | -0.13733 | 123.0194 | 122.8821 | -0.064087 | 123.0972 | 123.0972 | 0.21515 | -0.21515 | 122.4701 | 122.4106 | -0.60883 | 122.58 | 122.525 | 0.11444 | -0.65918 | 123.2712 | 123.1201 | 123.0194 | -0.45319 | 122.7264 | 122.6761 | 122.6074 | -0.92468
916.6875 | 123.3902 | -122.6395 | 0.74158 | 0.38522 | 0.11339 | 0.0090801 | 0.033354 | -0.018207 | 0.013372 | 0.028525 | 0.055491 | 0.023562 | 4.7432e-05 | -0.00050718 | 0.0039788 | 0.039835 | 0.4715 | 0.43488 | 0.39825 | 0.48523 | 0.73242 | 0.4715 | 0.32959 | -0.013733 | 0.059509 | -0.15564 | 0.20142 | 0.14191 | -0.07782 | -0.14648 | 123.111 | 122.9691 | -0.009155 | 123.0743 | 123.1247 | 0.15564 | -0.27008 | 122.5616 | 122.493 | -0.54016 | 122.6257 | 122.4838 | -0.009156 | -0.59967 | 123.3719 | 123.111 | 123.0377 | -0.41199 | 122.8409 | 122.7814 | 122.699 | -0.88806
917.6875 | 123.3765 | -122.644 | 0.70953 | 2.4604 | 0.10377 | -0.0058729 | 0.037626 | -0.012866 | 0.011236 | 0.028525 | -0.29546 | 0.026766 | -0.0063606 | 0.0069698 | 0.0050478 | 0.033426 | 0.56305 | 0.57678 | 0.48523 | 0.54016 | 0.77362 | 0.52185 | 0.36163 | 0.009155 | 0.045776 | -0.027466 | 0.16937 | 0.13275 | -0.10529 | -0.16022 | 123.1659 | 123.0057 | 0.064087 | 123.2208 | 123.1842 | 0.17853 | -0.14648 | 122.5388 | 122.4838 | -0.54016 | 122.6532 | 122.6166 | 0.13275 | -0.57678 | 123.4177 | 123.2071 | 123.1293 | -0.3479 | 122.8134 | 122.7768 | 122.6898 | -0.86975
918.6875 | 123.3627 | -122.6532 | 0.70038 | -0.10306 | 0.14757 | -0.00053286 | 0.030149 | -0.012866 | 0.00055539 | 0.026389 | -0.12761 | 0.018221 | -0.0020886 | -0.00050718 | 0.0029108 | 0.030222 | 0.50354 | 0.49896 | 0.42572 | 0.50812 | 0.71411 | 0.45319 | 0.3067 | -0.027466 | -0.004578 | -0.07782 | 0.16937 | 0.11902 | -0.1236 | -0.17853 | 123.1064 | 122.9599 | 0.013733 | 123.1522 | 123.1613 | 0.20142 | -0.19684 | 122.5296 | 122.4747 | -0.531 | 122.6257 | 122.5754 | 0.10071 | -0.58136 | 123.3673 | 123.1567 | 123.0789 | -0.39368 | 122.8226 | 122.7722 | 122.6486 | -0.87891
919.7031 | 123.4268 | -122.6028 | 0.67749 | 0.33944 | 0.077072 | 0.010148 | 0.0098553 | -0.0096622 | -0.033625 | 0.01998 | 0.31489 | 0.011812 | -0.022383 | 0.0059018 | -0.0045652 | 0.039835 | 0.53101 | 0.59967 | 0.51727 | 0.54474 | 0.66834 | 0.49896 | 0.35706 | 0.059509 | 0.064087 | 0.036621 | 0.17395 | 0.09613 | -0.059509 | -0.13275 | 123.1018 | 122.9599 | -0.009155 | 123.2025 | 123.1476 | 0.18768 | -0.14648 | 122.5433 | 122.4701 | -0.50354 | 122.6624 | 122.6395 | 0.16937 | -0.58136 | 123.2712 | 123.1339 | 123.1201 | -0.32043 | 122.7768 | 122.699 | 122.6669 | -0.81024
920.6875 | 123.3444 | -122.644 | 0.6958 | 0.14108 | 0.11018 | -0.0048049 | 0.020536 | -0.023548 | 0.0080314 | 0.021048 | 0.13178 | 0.020357 | 0.0096604 | -0.0047802 | 0.012524 | 0.035562 | 0.49439 | 0.44403 | 0.3891 | 0.48523 | 0.70953 | 0.43945 | 0.29755 | -0.054932 | -0.045776 | -0.10071 | 0.1831 | 0.13275 | -0.10529 | -0.16937 | 123.0835 | 122.9416 | 0.013733 | 123.0881 | 123.1293 | 0.18768 | -0.20142 | 122.5388 | 122.4747 | -0.5127 | 122.5891 | 122.5433 | 0.068665 | -0.56305 | 123.3536 | 123.1384 | 123.0331 | -0.39826 | 122.8271 | 122.7768 | 122.5983 | -0.86517
921.6875 | 123.3902 | -122.6578 | 0.69122 | -0.25565 | 0.094162 | 0.0026721 | 0.022672 | -0.0064582 | 0.0048274 | 0.023184 | -1.9129 | 0.019289 | 0.0011164 | -0.00050718 | 0.0018428 | 0.029154 | 0.54932 | 0.53101 | 0.45319 | 0.53101 | 0.70038 | 0.44403 | 0.32959 | 0.054932 | 0.073242 | -0.009155 | 0.20142 | 0.15564 | -0.059509 | -0.15106 | 123.1018 | 122.9874 | 0.009155 | 123.1888 | 123.1888 | 0.20142 | -0.14191 | 122.5983 | 122.5067 | -0.48981 | 122.7127 | 122.6486 | 0.14191 | -0.53558 | 123.3582 | 123.2071 | 123.111 | -0.36163 | 122.8592 | 122.8134 | 122.731 | -0.84229
922.6875 | 123.3902 | -122.6578 | 0.70496 | 0.019007 | 0.09523 | 0.0069441 | 0.0184 | -0.0032532 | 0.0037594 | 0.025321 | -0.23443 | 0.028902 | 0.0032524 | 0.016583 | 0.011456 | 0.032358 | 0.52185 | 0.51727 | 0.43488 | 0.50812 | 0.70953 | 0.45319 | 0.30212 | -0.009155 | 0.009155 | -0.054932 | 0.16479 | 0.12817 | -0.12817 | -0.17853 | 123.111 | 122.9599 | 0.004578 | 123.175 | 123.1659 | 0.20599 | -0.18311 | 122.5296 | 122.4792 | -0.54016 | 122.6486 | 122.6028 | 0.1236 | -0.57678 | 123.3673 | 123.1796 | 123.0927 | -0.40283 | 122.8226 | 122.7859 | 122.6669 | -0.88348
923.6875 | 123.349 | -122.6532 | 0.68665 | 0.049525 | 0.11873 | -0.0058729 | 0.024809 | 0.0020868 | 0.0091004 | 0.021048 | -0.12761 | 0.015017 | -0.0042246 | -0.0047802 | -0.0002932 | 0.037699 | 0.4715 | 0.45776 | 0.38452 | 0.47607 | 0.69122 | 0.45319 | 0.29297 | -0.054932 | -0.027466 | -0.082397 | 0.1831 | 0.14191 | -0.10986 | -0.17395 | 123.1064 | 122.9462 | 0.004577 | 123.111 | 123.1293 | 0.18311 | -0.21515 | 122.5433 | 122.4792 | -0.50354 | 122.5983 | 122.5708 | 0.091553 | -0.54474 | 123.3444 | 123.1247 | 123.0377 | -0.39368 | 122.8363 | 122.7951 | 122.6257 | -0.8606
924.7031 | 123.4451 | -122.6212 | 0.68665 | 0.080043 | 0.05571 | 0.032579 | 0.0066513 | -0.018207 | -0.026148 | 0.017844 | 0.17756 | 0.0096758 | -0.023451 | -0.00050718 | -0.016315 | 0.050516 | 0.44403 | 0.54016 | 0.46234 | 0.51727 | 0.61798 | 0.44861 | 0.31128 | 0.032043 | 0.086975 | 0.050354 | 0.16022 | 0.09613 | -0.073242 | -0.10986 | 123.0698 | 122.9324 | -0.068665 | 123.1613 | 123.1384 | 0.20599 | -0.24261 | 122.5479 | 122.5113 | -0.52643 | 122.6532 | 122.6715 | 0.16022 | -0.59052 | 123.2391 | 123.0652 | 123.0835 | -0.37537 | 122.7814 | 122.7173 | 122.7081 | -0.79651
925.6875 | 123.3765 | -122.6669 | 0.67291 | -0.20987 | 0.099502 | -0.014418 | 0.019468 | -0.0032532 | 0.021917 | 0.028525 | -0.29546 | 0.01288 | -0.011702 | 0.011242 | 0.010388 | 0.022745 | 0.54474 | 0.53101 | 0.43488 | 0.51727 | 0.72327 | 0.46692 | 0.31586 | 0.009155 | 0.018311 | -0.036621 | 0.17395 | 0.11902 | -0.11444 | -0.16937 | 123.1339 | 122.9828 | 0.050354 | 123.1979 | 123.1842 | 0.20142 | -0.12817 | 122.5525 | 122.4976 | -0.49896 | 122.6761 | 122.6303 | 0.13275 | -0.55389 | 123.3902 | 123.2117 | 123.1018 | -0.35706 | 122.8409 | 122.7859 | 122.6852 | -0.84229
926.6875 | 123.3627 | -122.6761 | 0.67291 | -0.072545 | 0.11125 | -0.0080089 | 0.024809 | -0.0053902 | 0.016576 | 0.025321 | -0.066579 | 0.021425 | -0.0074286 | 0.016583 | -0.0024292 | 0.020609 | 0.49439 | 0.47607 | 0.37994 | 0.48065 | 0.71411 | 0.42114 | 0.30212 | -0.041199 | -0.027466 | -0.09613 | 0.16022 | 0.10986 | -0.11902 | -0.1831 | 123.0972 | 122.9782 | 0.041198 | 123.1522 | 123.1567 | 0.17853 | -0.17853 | 122.5571 | 122.493 | -0.5127 | 122.6349 | 122.58 | 0.086975 | -0.56305 | 123.3902 | 123.1705 | 123.056 | -0.37079 | 122.8363 | 122.7859 | 122.6486 | -0.85602
927.6875 | 123.381 | -122.6807 | 0.66834 | -0.66764 | 0.10057 | -0.0080089 | 0.019468 | -4.9167e-05 | 0.0069634 | 0.024253 | -0.18865 | 0.020357 | -0.0074286 | 0.00056082 | 0.0029108 | 0.028086 | 0.55847 | 0.53101 | 0.42572 | 0.50812 | 0.71411 | 0.4715 | 0.32501 | 0.009155 | 0.036621 | -0.022888 | 0.16937 | 0.10986 | -0.10529 | -0.16937 | 123.1522 | 123.0057 | 0.045776 | 123.2117 | 123.1888 | 0.18311 | -0.10986 | 122.5754 | 122.5113 | -0.49896 | 122.6898 | 122.6578 | 0.14649 | -0.55847 | 123.3948 | 123.2391 | 123.1064 | -0.34332 | 122.85 | 122.7905 | 122.7173 | -0.83771
928.6875 | 123.3582 | -122.6761 | 0.68665 | 0.0037495 | 0.1198 | -0.0037369 | 0.04083 | -0.0085942 | 0.01444 | 0.030661 | -0.20391 | 0.022493 | -0.0074286 | 0.0048338 | -0.0002932 | 0.027017 | 0.47607 | 0.47607 | 0.41657 | 0.49439 | 0.70038 | 0.43488 | 0.27924 | -0.036621 | -0.013733 | -0.07782 | 0.16479 | 0.14191 | -0.11444 | -0.1831 | 123.111 | 122.9553 | 0.013732 | 123.1522 | 123.1705 | 0.21515 | -0.21057 | 122.5616 | 122.493 | -0.52185 | 122.6395 | 122.5983 | 0.10528 | -0.54474 | 123.3765 | 123.1522 | 123.0927 | -0.40741 | 122.8409 | 122.818 | 122.6624 | -0.86975
929.7031 | 123.4451 | -122.6532 | 0.67291 | 0.32418 | 0.059982 | 0.014421 | 0.014128 | -0.013935 | -0.033625 | 0.014639 | 0.25385 | 0.01288 | -0.017042 | -0.011188 | -0.0045652 | 0.052652 | 0.48523 | 0.57678 | 0.49896 | 0.53101 | 0.66376 | 0.48065 | 0.32959 | 0.050354 | 0.059509 | 0.018311 | 0.14648 | 0.11902 | -0.086975 | -0.12817 | 123.1339 | 122.9828 | -0.009156 | 123.23 | 123.1842 | 0.20142 | -0.18768 | 122.5662 | 122.525 | -0.52643 | 122.7036 | 122.6715 | 0.14649 | -0.55389 | 123.317 | 123.1384 | 123.1522 | -0.34332 | 122.7997 | 122.7722 | 122.7127 | -0.80109
930.6875 | 123.3673 | -122.6807 | 0.66376 | -0.026769 | 0.12086 | 0.00053514 | 0.034422 | -0.0053902 | 0.022985 | 0.022116 | -0.20391 | 0.017153 | 0.011797 | -0.01012 | 0.0018428 | 0.032358 | 0.50812 | 0.4715 | 0.40741 | 0.49439 | 0.69122 | 0.43945 | 0.28381 | -0.036621 | -0.018311 | -0.073242 | 0.16479 | 0.11444 | -0.11444 | -0.17395 | 123.1201 | 122.9645 | 0.027466 | 123.1522 | 123.175 | 0.21057 | -0.15564 | 122.5662 | 122.5067 | -0.49896 | 122.644 | 122.6074 | 0.10071 | -0.54932 | 123.3719 | 123.1888 | 123.0881 | -0.37994 | 122.8455 | 122.7951 | 122.6624 | -0.83771
931.6875 | 123.3353 | -122.6852 | 0.69122 | 0.20211 | 0.11873 | -0.0016009 | 0.034422 | -0.015003 | 0.016576 | 0.015708 | 0.009715 | 0.020357 | -0.0042246 | 0.01231 | 0.0007748 | 0.035562 | 0.4715 | 0.4303 | 0.37079 | 0.46692 | 0.70038 | 0.43488 | 0.28839 | -0.027466 | -0.041199 | -0.07782 | 0.19226 | 0.12817 | -0.10529 | -0.17853 | 123.1201 | 122.9736 | 0.009155 | 123.1155 | 123.1522 | 0.17853 | -0.21973 | 122.58 | 122.5067 | -0.49896 | 122.6578 | 122.6074 | 0.10071 | -0.56305 | 123.3856 | 123.1567 | 123.056 | -0.40283 | 122.8775 | 122.8134 | 122.644 | -0.86975
932.6875 | 123.3902 | -122.6807 | 0.68665 | 5.9699 | 0.10164 | 0.013353 | 0.029081 | -0.0075262 | -0.0037176 | 0.023184 | 0.086009 | 0.023562 | 0.0032524 | 0.014447 | 0.0029108 | 0.044107 | 0.4715 | 0.47607 | 0.3891 | 0.46692 | 0.6958 | 0.43488 | 0.30212 | -0.004578 | -0.036621 | -0.068665 | 0.17853 | 0.12817 | -0.11902 | -0.17395 | 123.1155 | 122.9828 | 0.009155 | 123.1567 | 123.1476 | 0.16479 | -0.21515 | 122.5616 | 122.5067 | -0.50812 | 122.6761 | 122.612 | 0.10528 | -0.55847 | 123.3765 | 123.1522 | 123.0698 | -0.38452 | 122.8592 | 122.8088 | 122.644 | -0.8606
933.6875 | 123.3582 | -122.6898 | 0.66834 | -0.087804 | 0.090957 | -0.0026689 | 0.026945 | -0.016071 | 0.0091004 | 0.028525 | -0.11236 | 0.01288 | 0.0032524 | -0.0015752 | 0.0039788 | 0.03129 | 0.50354 | 0.47607 | 0.40741 | 0.48065 | 0.69122 | 0.42572 | 0.28381 | -0.013733 | -0.013733 | -0.073242 | 0.17395 | 0.12817 | -0.11902 | -0.17395 | 123.1155 | 122.9736 | 0.022888 | 123.1659 | 123.1705 | 0.19684 | -0.1648 | 122.5708 | 122.5159 | -0.49439 | 122.6761 | 122.6166 | 0.10071 | -0.54016 | 123.381 | 123.1934 | 123.0972 | -0.38452 | 122.8638 | 122.818 | 122.6761 | -0.84228
934.6875 | 123.3582 | -122.699 | 0.68665 | 0.064784 | 0.10805 | 0.018693 | 0.032286 | -0.0064582 | 0.0048274 | 0.022116 | 0.040232 | 0.018221 | -0.010634 | 0.017651 | 0.0082518 | 0.032358 | 0.46692 | 0.42572 | 0.37537 | 0.49439 | 0.68207 | 0.41657 | 0.30212 | -0.050354 | -0.045776 | -0.10529 | 0.18768 | 0.14191 | -0.10529 | -0.16937 | 123.1155 | 123.0011 | -0.004578 | 123.1247 | 123.1934 | 0.19226 | -0.21973 | 122.5937 | 122.5296 | -0.49896 | 122.6486 | 122.5937 | 0.064087 | -0.54474 | 123.381 | 123.1659 | 123.0743 | -0.38452 | 122.8867 | 122.8409 | 122.6532 | -0.85602
935.6875 | 123.3398 | -122.6944 | 0.6958 | 0.080043 | 0.092026 | -0.0058729 | 0.011991 | -0.016071 | 0.00055539 | 0.022116 | 0.040232 | 0.0086078 | -0.013838 | 0.017651 | 0.0061158 | 0.03663 | 0.43945 | 0.4303 | 0.36621 | 0.46692 | 0.68207 | 0.43488 | 0.28381 | -0.064087 | -0.032043 | -0.10071 | 0.19684 | 0.15106 | -0.10986 | -0.16937 | 123.1293 | 122.9782 | -0.013733 | 123.1247 | 123.1613 | 0.18311 | -0.25635 | 122.5845 | 122.525 | -0.49896 | 122.6303 | 122.5937 | 0.068665 | -0.54474 | 123.3765 | 123.1338 | 123.0606 | -0.41199 | 122.8912 | 122.8455 | 122.6624 | -0.86517
936.6875 | 123.349 | -122.6852 | 0.66376 | 0.21737 | 0.10271 | 0.00053514 | 0.016264 | -0.016071 | -0.00051261 | 0.029593 | -1.1347 | 0.020357 | -0.0010206 | 0.0069698 | 0.011456 | 0.037699 | 0.37079 | 0.5722 | 0.48981 | 0.48981 | 0.71869 | 0.46234 | 0.32044 | -0.036621 | -0.036621 | -0.059509 | 0.1831 | 0.13733 | -0.09613 | -0.17395 | 123.1476 | 123.0057 | 0.054932 | 123.2574 | 123.175 | 0.16937 | -0.29297 | 122.5891 | 122.5113 | -0.48065 | 122.6486 | 122.6257 | 0.11444 | -0.52643 | 123.4039 | 123.056 | 123.175 | -0.34332 | 122.8683 | 122.8226 | 122.6486 | -0.83771
937.6875 | 123.4131 | -122.6624 | 0.64087 | 0.36996 | 0.11339 | 0.0026721 | 0.030149 | -0.01073 | -0.0069216 | 0.031729 | 0.22334 | 0.018221 | -0.0042246 | -0.00050718 | 0.0018428 | 0.040903 | 0.47607 | 0.46234 | 0.37994 | 0.45776 | 0.6958 | 0.44403 | 0.29755 | 0 | 0.009155 | -0.013733 | 0.16479 | 0.10529 | -0.091553 | -0.14648 | 123.1064 | 122.9599 | 0.054932 | 123.1247 | 123.1201 | 0.16022 | -0.1648 | 122.5708 | 122.5159 | -0.47607 | 122.6624 | 122.6486 | 0.13275 | -0.53558 | 123.3582 | 123.1384 | 123.0423 | -0.34332 | 122.8271 | 122.7676 | 122.6715 | -0.78735
938.6875 | 123.3398 | -122.6898 | 0.68665 | 0.11056 | 0.098434 | -0.0069409 | 0.0098553 | -0.019275 | 0.011236 | 0.031729 | -0.097097 | 0.027834 | 0.0021844 | 0.0048338 | 0.0093198 | 0.030222 | 0.44403 | 0.43488 | 0.37079 | 0.44403 | 0.68207 | 0.41657 | 0.27466 | -0.059509 | -0.045776 | -0.10529 | 0.19226 | 0.11444 | -0.11444 | -0.1831 | 123.1064 | 122.9645 | -0.004578 | 123.1247 | 123.1338 | 0.16937 | -0.24261 | 122.5754 | 122.5067 | -0.49438 | 122.6303 | 122.5845 | 0.077819 | -0.5722 | 123.3719 | 123.1338 | 123.0606 | -0.41199 | 122.8821 | 122.8043 | 122.644 | -0.86975
939.7031 | 123.4543 | -122.6532 | 0.65002 | 0.15634 | 0.068527 | 0.010148 | 0.013059 | -0.025684 | -0.045374 | 0.013571 | 0.14704 | 0.0032668 | -0.023451 | -0.01012 | -0.0034972 | 0.04838 | 0.45776 | 0.52185 | 0.45776 | 0.52643 | 0.66376 | 0.4715 | 0.32959 | 0.018311 | 0.064087 | 0.032043 | 0.16022 | 0.1236 | -0.10071 | -0.15106 | 123.1247 | 122.9828 | 0.013733 | 123.175 | 123.1796 | 0.19684 | -0.19226 | 122.5525 | 122.5021 | -0.48981 | 122.6715 | 122.6852 | 0.18311 | -0.52643 | 123.317 | 123.111 | 123.111 | -0.32043 | 122.8134 | 122.7768 | 122.7173 | -0.80109
940.6875 | 123.4909 | -122.6669 | 0.64545 | 0.36996 | 0.096298 | 0.0037401 | 0.032286 | -0.0032532 | -0.0079896 | 0.015708 | 0.2386 | 0.013948 | 0.0011164 | -0.016529 | -0.0034972 | 0.035562 | 0.55389 | 0.52643 | 0.48523 | 0.52643 | 0.65918 | 0.45319 | 0.31586 | 0.082397 | 0.07782 | 0.059509 | 0.14648 | 0.082397 | -0.068665 | -0.12817 | 123.1201 | 122.9828 | 0.013733 | 123.1934 | 123.1934 | 0.21057 | -0.091553 | 122.5983 | 122.5388 | -0.49896 | 122.7493 | 122.7264 | 0.18768 | -0.56305 | 123.3261 | 123.2208 | 123.1522 | -0.32959 | 122.8134 | 122.7493 | 122.7448 | -0.77362
941.6875 | 123.4039 | -122.7219 | 0.65002 | -0.087804 | 0.11659 | -0.0069409 | 0.037626 | -0.017139 | 0.0091004 | 0.01998 | -0.20391 | 0.010744 | -0.011702 | -0.01012 | 0.013592 | 0.019541 | 0.53101 | 0.48065 | 0.41199 | 0.47607 | 0.67291 | 0.4303 | 0.2655 | 0 | 0.018311 | -0.059509 | 0.16937 | 0.11444 | -0.10071 | -0.1831 | 123.1522 | 122.9874 | 0.022889 | 123.2025 | 123.1979 | 0.21057 | -0.11902 | 122.6212 | 122.5388 | -0.48065 | 122.7219 | 122.6624 | 0.1236 | -0.53558 | 123.3948 | 123.2529 | 123.1338 | -0.38452 | 122.8912 | 122.8363 | 122.7402 | -0.83313
942.6875 | 123.3627 | -122.6898 | 0.67749 | 0.21737 | 0.10271 | 0.0026721 | 0.023741 | -0.0053902 | 0.0048274 | 0.024253 | 0.11653 | 0.018221 | 0.0096604 | -0.0026432 | -0.0077702 | 0.028086 | 0.44403 | 0.41657 | 0.37079 | 0.43488 | 0.67749 | 0.42572 | 0.27008 | 0.073242 | -0.09613 | -0.041199 | 0.1831 | 0.14648 | -0.091553 | -0.16479 | 123.1155 | 122.9599 | 0 | 123.1064 | 123.1247 | 0.16479 | -0.23346 | 122.5983 | 122.525 | -0.49439 | 122.7631 | 122.6486 | 0.1236 | -0.53101 | 123.3673 | 123.1338 | 123.0606 | -0.40741 | 122.8729 | 122.8363 | 122.5937 | -0.84229
943.6875 | 123.3994 | -122.699 | 0.63629 | 0.3547 | 0.10591 | 0.0090801 | 0.022672 | -0.023548 | 0.0026914 | 0.026389 | 0.17756 | 0.0096758 | 0.022478 | 0.0037648 | 0.0018428 | 0.037699 | 0.45776 | 0.43488 | 0.37079 | 0.45776 | 0.66834 | 0.42114 | 0.27466 | 0.004578 | -0.018311 | -0.050354 | 0.16479 | 0.13275 | -0.10986 | -0.15564 | 123.1201 | 122.9736 | 0.032043 | 123.1339 | 123.1567 | 0.18311 | -0.17853 | 122.5891 | 122.5433 | -0.4715 | 122.7036 | 122.6486 | 0.10529 | -0.50354 | 123.3673 | 123.1567 | 123.0698 | -0.36163 | 122.8638 | 122.8317 | 122.6807 | -0.79193
944.7031 | 123.4589 | -122.6715 | 0.66834 | 0.064784 | 0.063186 | 0.035783 | 0.025877 | -0.020343 | -0.058192 | 0.018912 | 0.17756 | 0.016085 | -0.028792 | 0.015515 | -0.0056342 | 0.041971 | 0.42572 | 0.48981 | 0.42572 | 0.48065 | 0.59509 | 0.39825 | 0.25177 | 0.022888 | 0.086975 | 0.041199 | 0.13275 | 0.11902 | -0.073242 | -0.13733 | 123.0698 | 122.9233 | -0.073242 | 123.1613 | 123.1522 | 0.22888 | -0.24262 | 122.5983 | 122.5342 | -0.53558 | 122.6944 | 122.7127 | 0.17853 | -0.54932 | 123.2666 | 123.0972 | 123.0972 | -0.41657 | 122.8043 | 122.7905 | 122.7585 | -0.80566
945.6875 | 123.3994 | -122.7081 | 0.66376 | 0.38522 | 0.10805 | 0.0026721 | 0.032286 | -0.019275 | 0.013372 | 0.01998 | 0.055491 | 0.023562 | -0.0020886 | -0.0090522 | 0.0050478 | 0.027017 | 0.45319 | 0.42114 | 0.37994 | 0.44403 | 0.67749 | 0.39825 | 0.26093 | 0.009155 | -0.027466 | -0.050354 | 0.17395 | 0.15106 | -0.09613 | -0.17853 | 123.1064 | 122.9691 | 0.013733 | 123.1293 | 123.1522 | 0.18311 | -0.21057 | 122.612 | 122.5296 | -0.48981 | 122.7173 | 122.6578 | 0.12817 | -0.5127 | 123.3856 | 123.1613 | 123.0881 | -0.40283 | 122.8821 | 122.8592 | 122.6807 | -0.84229
946.6875 | 123.4589 | -122.6715 | 0.62256 | 0.41574 | 0.10591 | 0.0080121 | 0.025877 | -0.011798 | -0.0058536 | 0.015708 | 0.19282 | 0.01288 | -0.0020886 | -0.0079842 | -0.0034972 | 0.030222 | 0.48981 | 0.4715 | 0.39825 | 0.47607 | 0.65918 | 0.41199 | 0.27008 | 0.073242 | 0.050354 | 0.022888 | 0.15564 | 0.11444 | -0.059509 | -0.13733 | 123.0835 | 122.9416 | 0.036621 | 123.143 | 123.1476 | 0.20599 | -0.13275 | 122.612 | 122.5342 | -0.46692 | 122.7448 | 122.6944 | 0.16022 | -0.50812 | 123.3307 | 123.1613 | 123.0698 | -0.35248 | 122.8271 | 122.7859 | 122.7219 | -0.75989
947.6875 | 123.3856 | -122.7127 | 0.66376 | 0.034266 | 0.11018 | -0.00053286 | 0.029081 | -0.0096622 | 0.0058954 | 0.036002 | 0.009715 | 0.0086078 | -0.0095656 | 0.0069698 | 0.0007748 | 0.024881 | 0.47607 | 0.41657 | 0.3479 | 0.44403 | 0.6958 | 0.41199 | 0.25177 | -0.004578 | -0.041199 | -0.064087 | 0.17853 | 0.13275 | -0.13275 | -0.17395 | 123.1247 | 122.9645 | 0.032044 | 123.1293 | 123.1567 | 0.19226 | -0.18768 | 122.58 | 122.5388 | -0.48523 | 122.7081 | 122.6486 | 0.10986 | -0.53101 | 123.4085 | 123.1888 | 123.0606 | -0.41199 | 122.8912 | 122.8455 | 122.6715 | -0.83771
948.6875 | 123.3627 | -122.7173 | 0.65918 | -3.109 | 0.11018 | 0.0090801 | 0.022672 | -0.0011172 | -0.0015816 | 0.021048 | 0.07075 | 0.02463 | -0.010634 | 0.017651 | 0.0039788 | 0.019541 | 0.48523 | 0.40741 | 0.33875 | 0.43945 | 0.68207 | 0.40741 | 0.26093 | -0.004578 | -0.022888 | -0.054932 | 0.1831 | 0.12817 | -0.10529 | -0.17395 | 123.1247 | 122.9782 | 0.022888 | 123.1247 | 123.1567 | 0.17853 | -0.17395 | 122.612 | 122.5433 | -0.47608 | 122.7127 | 122.6624 | 0.11902 | -0.53101 | 123.3994 | 123.2025 | 123.056 | -0.39825 | 122.9004 | 122.8455 | 122.6944 | -0.83313
949.7031 | 123.4863 | -122.6807 | 0.63171 | -0.25565 | 0.090957 | 0.010148 | 0.0184 | -0.020343 | -0.021876 | 0.01998 | 0.29963 | 0.017153 | -0.023451 | -0.0015752 | 0.0082518 | 0.041971 | 0.52643 | 0.54474 | 0.48065 | 0.52185 | 0.62256 | 0.44861 | 0.31128 | 0.10071 | 0.086975 | 0.059509 | 0.13733 | 0.086975 | -0.082397 | -0.11444 | 123.1293 | 122.9919 | -0.009155 | 123.2254 | 123.2025 | 0.21057 | -0.10529 | 122.5983 | 122.5662 | -0.49438 | 122.7814 | 122.7402 | 0.17395 | -0.54474 | 123.3032 | 123.2071 | 123.1613 | -0.32044 | 122.818 | 122.7676 | 122.7676 | -0.74616
950.6875 | 123.3627 | -122.7356 | 0.65918 | 0.26315 | 0.097366 | 0.0090801 | 0.025877 | -0.011798 | 0.026189 | -0.00031405 | -0.31072 | 0.0086078 | 0.0053884 | 0.0037648 | 0.0029108 | 0.022745 | 0.29297 | 0.68665 | 0.44403 | 0.44403 | 0.69122 | 0.42572 | 0.28839 | -0.027466 | -0.050354 | -0.086975 | 0.20142 | 0.1236 | -0.11444 | -0.16479 | 123.1613 | 123.024 | 0.032043 | 123.4222 | 123.1796 | 0.15564 | -0.36621 | 122.6212 | 122.5708 | -0.45776 | 122.7081 | 122.6486 | 0.07782 | -0.53558 | 123.4268 | 123.0286 | 123.1796 | -0.37079 | 122.937 | 122.8592 | 122.6852 | -0.82398
951.6875 | 123.4222 | -122.7173 | 0.63629 | 0.30892 | 0.10805 | -0.0037369 | 0.033354 | -0.015003 | 0.0016234 | 0.022116 | 0.22334 | 0.022493 | 0.0053884 | 0.010174 | -0.0002932 | 0.034494 | 0.46692 | 0.42114 | 0.36163 | 0.44861 | 0.66834 | 0.41199 | 0.25635 | 0.027466 | -0.004578 | -0.013733 | 0.16937 | 0.10529 | -0.091553 | -0.15106 | 123.1293 | 122.9736 | 0.032043 | 123.1384 | 123.1659 | 0.19226 | -0.16937 | 122.6257 | 122.5662 | -0.46692 | 122.7448 | 122.7036 | 0.13733 | -0.53101 | 123.3856 | 123.1842 | 123.0789 | -0.37994 | 122.8867 | 122.8226 | 122.7127 | -0.78735
952.6875 | 123.5138 | -122.6761 | 0.60425 | 0.431 | 0.086685 | 0.010148 | 0.0098553 | -0.012866 | -0.012263 | 0.025321 | -0.020803 | 0.017153 | 0.0011164 | -0.0037112 | 0.0050478 | 0.029154 | 0.51727 | 0.50354 | 0.44861 | 0.50812 | 0.64545 | 0.43488 | 0.27466 | 0.091553 | 0.091553 | 0.059509 | 0.13275 | 0.091553 | -0.068665 | -0.13275 | 123.111 | 122.9507 | 0.041199 | 123.1796 | 123.1842 | 0.23346 | -0.086975 | 122.6074 | 122.5433 | -0.4715 | 122.7676 | 122.7356 | 0.19226 | -0.5127 | 123.3215 | 123.1934 | 123.1247 | -0.32959 | 122.8088 | 122.7676 | 122.7676 | -0.737
953.6875 | 123.349 | -122.7081 | 0.65002 | 0.26315 | 0.10377 | 0.0069441 | 0.020536 | -0.0064582 | 0.011236 | 0.027457 | 0.14704 | 0.017153 | 0.0043204 | 0.017651 | -0.0002932 | 0.043039 | 0.43488 | 0.37994 | 0.32959 | 0.42114 | 0.66376 | 0.39825 | 0.25635 | 0.07782 | -0.19684 | 0.09613 | 0.17853 | 0.14648 | -0.086975 | -0.15564 | 123.1064 | 122.9645 | 0.013733 | 123.0881 | 123.1293 | 0.16479 | -0.21515 | 122.6212 | 122.5525 | -0.4715 | 122.7859 | 122.8043 | 0.25177 | -0.50354 | 123.3719 | 123.143 | 123.0377 | -0.39368 | 122.8867 | 122.8546 | 122.5113 | -0.80566
954.6875 | 123.4589 | -122.731 | 0.55389 | 0.11056 | 0.070663 | 0.0048081 | 0.0077193 | -0.022479 | -0.038966 | 0.022116 | 0.13178 | 0.0096758 | -0.017042 | 0.0026968 | -0.010974 | 0.047312 | 0.44403 | 0.50812 | 0.4303 | 0.48523 | 0.62256 | 0.42572 | 0.2655 | -0.24261 | 0.004578 | -0.059509 | 0.10986 | 0.073242 | -0.13275 | -0.20599 | 123.1567 | 122.9965 | 0.068665 | 123.2391 | 123.2162 | 0.21973 | -0.10986 | 122.5983 | 122.525 | -0.44403 | 122.4884 | 122.6715 | 0.14649 | -0.48065 | 123.3536 | 123.175 | 123.1613 | -0.28839 | 122.8409 | 122.8043 | 122.7356 | -0.75989
955.7031 | 123.4634 | -122.6624 | 0.62714 | 0.36996 | 0.056778 | 0.019762 | 0.013059 | -0.020343 | -0.011195 | 0.014639 | 0.29963 | 0.017153 | -0.019179 | -0.0047802 | -0.0045652 | 0.03129 | 0.5127 | 0.53101 | 0.4715 | 0.51727 | 0.61798 | 0.43488 | 0.28381 | 0.09613 | 0.091553 | 0.068665 | 0.15106 | 0.082397 | -0.086975 | -0.13275 | 123.0972 | 122.9462 | -0.009155 | 123.1934 | 123.1796 | 0.23346 | -0.11444 | 122.5754 | 122.5296 | -0.47607 | 122.7585 | 122.731 | 0.20142 | -0.54474 | 123.2803 | 123.175 | 123.1339 | -0.34332 | 122.8134 | 122.7448 | 122.7539 | -0.75989
956.7031 | 123.4955 | -122.6944 | 0.6134 | -0.36246 | 0.066391 | 0.0090801 | 0.013059 | -0.0021852 | -0.018671 | 0.018912 | 0.66584 | -0.0063462 | -0.0042246 | -0.0090522 | 0.0071838 | 0.027017 | 0.53101 | 0.31128 | 0.41657 | 0.56305 | 0.61798 | 0.4303 | 0.27008 | 0.09613 | 0.14648 | 0.07782 | 0.15564 | 0.086975 | -0.07782 | -0.11902 | 123.1247 | 122.9645 | 0.004578 | 123.0057 | 123.2574 | 0.29297 | -0.082397 | 122.6166 | 122.5754 | -0.45776 | 122.7905 | 122.7722 | 0.19684 | -0.52643 | 123.3124 | 123.2254 | 123.111 | -0.34332 | 122.85 | 122.7814 | 122.8409 | -0.73242
957.7656 | 123.4818 | -122.6669 | 0.59967 | 0.44625 | 0.10057 | 0.0016041 | 0.025877 | -0.019275 | 0.0026914 | 0.007163 | 0.26911 | 0.013948 | -0.010634 | -0.0079842 | 0.0061158 | 0.019541 | 0.50354 | 0.46692 | 0.39368 | 0.46234 | 0.63171 | 0.41657 | 0.25635 | 0.082397 | 0.041199 | 0.013733 | 0.13275 | 0.10071 | -0.073242 | -0.13733 | 123.0835 | 122.9233 | 0.032044 | 123.1339 | 123.1293 | 0.20599 | -0.09613 | 122.5937 | 122.5296 | -0.46692 | 122.7493 | 122.6807 | 0.15106 | -0.49896 | 123.2986 | 123.1705 | 123.0606 | -0.34332 | 122.7997 | 122.7676 | 122.7081 | -0.737
958.6875 | 123.3582 | -122.7585 | 0.63629 | 0.33944 | 0.10164 | 0.0080121 | 0.036558 | -0.022479 | 0.068914 | 0.036002 | -0.081838 | 0.017153 | -0.0042246 | -0.0015752 | 0.0050478 | 0.034494 | 0.24261 | 0.60883 | 0.37994 | 0.4303 | 0.67291 | 0.41657 | 0.27008 | -0.009155 | -0.059509 | -0.082397 | 0.1831 | 0.11902 | -0.10529 | -0.16022 | 123.175 | 123.0286 | 0.036621 | 123.3673 | 123.1888 | 0.16022 | -0.39368 | 122.6532 | 122.5983 | -0.45319 | 122.7493 | 122.6761 | 0.07782 | -0.51727 | 123.4314 | 123.0011 | 123.1384 | -0.36621 | 122.9416 | 122.8775 | 122.699 | -0.79651
959.6875 | 123.5184 | -122.6761 | 0.60425 | 0.46151 | 0.11552 | -0.0026689 | 0.011991 | -0.0064582 | -0.0026496 | 0.014639 | 0.2386 | 0.010744 | -0.0084976 | -0.0069162 | 0.0093198 | 0.020609 | 0.54016 | 0.4715 | 0.43488 | 0.52643 | 0.63171 | 0.41657 | 0.27008 | 0.10071 | 0.091553 | 0.045776 | 0.14191 | 0.073242 | -0.064087 | -0.1236 | 123.0927 | 122.9462 | 0.027466 | 123.1476 | 123.2025 | 0.25635 | -0.064087 | 122.612 | 122.5525 | -0.46234 | 122.7768 | 122.7219 | 0.16937 | -0.53101 | 123.3078 | 123.2162 | 123.111 | -0.33417 | 122.818 | 122.7493 | 122.7676 | -0.72784
960.7031 | 123.5092 | -122.6486 | 0.63171 | -0.13358 | 0.05571 | -0.20775 | 0.013059 | -0.017139 | -0.033625 | 0.017844 | -0.097097 | 0.0086078 | -0.018111 | 0.00056082 | -0.0056342 | 0.027017 | 0.49896 | 0.54932 | 0.47607 | 0.51727 | 0.62714 | 0.43945 | 0.29755 | 0.091553 | 0.12817 | 0.073242 | 0.14648 | 0.10071 | -0.045776 | -0.10529 | 123.0881 | 122.9462 | -0.004578 | 123.1979 | 123.1659 | 0.21973 | -0.13275 | 122.6028 | 122.5433 | -0.48523 | 122.7402 | 122.7219 | 0.17853 | -0.53101 | 123.2758 | 123.1476 | 123.1247 | -0.33417 | 122.7951 | 122.7493 | 122.7768 | -0.737
961.6875 | 123.3627 | -122.7585 | 0.63629 | 0.0037495 | 0.13261 | 0.0037401 | 0.028013 | -0.012866 | 0.022985 | 0.034934 | -0.17339 | 0.011812 | -0.020247 | -0.0015752 | 0.011456 | 0.020609 | 0.46234 | 0.41657 | 0.3479 | 0.4303 | 0.63171 | 0.38452 | 0.22888 | -0.018311 | -0.027466 | -0.10071 | 0.17853 | 0.10986 | -0.11444 | -0.17853 | 123.143 | 122.9874 | -0.004578 | 123.175 | 123.1888 | 0.20142 | -0.17395 | 122.644 | 122.58 | -0.45776 | 122.7402 | 122.6578 | 0.07782 | -0.52643 | 123.3902 | 123.2208 | 123.1064 | -0.40741 | 122.937 | 122.8683 | 122.731 | -0.81482
962.6875 | 123.3032 | -122.7402 | 0.64545 | 0.049525 | 0.10805 | -0.0016009 | 0.019468 | -0.018207 | 0.0091004 | 0.029593 | -0.05132 | 0.031038 | -0.0084976 | -0.0026432 | 0.012524 | 0.015268 | 0.40741 | 0.37079 | 0.29755 | 0.40741 | 0.64087 | 0.37994 | 0.22888 | -0.027466 | -0.041199 | -0.07782 | 0.17853 | 0.1236 | -0.10529 | -0.16479 | 123.1201 | 122.9691 | -0.004578 | 123.111 | 123.1476 | 0.17853 | -0.23804 | 122.6349 | 122.5754 | -0.46692 | 122.7127 | 122.6624 | 0.086975 | -0.52185 | 123.381 | 123.1476 | 123.0377 | -0.41656 | 122.9187 | 122.8638 | 122.699 | -0.81024
963.6875 | 123.3856 | -122.7356 | 0.62714 | 3.4065 | 0.10164 | 0.012285 | 0.021604 | -0.0021852 | 0.0091004 | 0.023184 | 0.086009 | 0.010744 | -0.0042246 | 0.015515 | -0.0024292 | 0.03663 | 0.40283 | 0.43945 | 0.33417 | 0.42114 | 0.65918 | 0.40741 | 0.21973 | -0.013733 | -0.027466 | -0.064087 | 0.1831 | 0.1236 | -0.10986 | -0.16937 | 123.143 | 122.9553 | 0.032044 | 123.175 | 123.1567 | 0.20142 | -0.2243 | 122.6257 | 122.5662 | -0.44403 | 122.7219 | 122.6715 | 0.10529 | -0.50354 | 123.3948 | 123.1384 | 123.0698 | -0.40741 | 122.9187 | 122.8592 | 122.7081 | -0.79651
964.6875 | 123.4543 | -122.7402 | 0.61798 | 0.32418 | 0.11446 | -0.0048049 | 0.025877 | -0.021411 | -0.0069216 | 0.025321 | 0.19282 | 0.023562 | -0.01277 | -0.013324 | 0.0050478 | 0.033426 | 0.43945 | 0.41657 | 0.35248 | 0.42572 | 0.64545 | 0.3891 | 0.23346 | 0.036621 | 0.009155 | -0.018311 | 0.15106 | 0.1236 | -0.086975 | -0.15106 | 123.1293 | 122.9736 | 0.027466 | 123.1567 | 123.1659 | 0.19226 | -0.17853 | 122.6532 | 122.5891 | -0.46692 | 122.7768 | 122.7219 | 0.13275 | -0.49439 | 123.3856 | 123.1796 | 123.0927 | -0.38452 | 122.8912 | 122.8638 | 122.7493 | -0.76904
965.7031 | 123.4955 | -122.6852 | 0.60883 | -0.087804 | 0.064255 | 0.028306 | 0.0098553 | -0.01073 | -0.037898 | 0.01998 | -0.17339 | 0.0064718 | -0.037337 | -0.0079842 | -0.012042 | 0.03663 | 0.4715 | 0.54474 | 0.46234 | 0.50354 | 0.64545 | 0.42572 | 0.2655 | 0.09613 | 0.13733 | 0.09613 | 0.15106 | 0.09613 | -0.068665 | -0.13733 | 123.111 | 122.9507 | 0.036621 | 123.23 | 123.1888 | 0.23804 | -0.13733 | 122.6166 | 122.5479 | -0.45776 | 122.7814 | 122.7814 | 0.23346 | -0.5127 | 123.3307 | 123.1567 | 123.1476 | -0.34332 | 122.8363 | 122.7814 | 122.8226 | -0.74616
966.6875 | 123.4085 | -122.7539 | 0.63171 | 0.46151 | 0.10698 | 0.0069441 | 0.020536 | -0.011798 | 0.011236 | 0.030661 | 0.024973 | 0.010744 | 4.7432e-05 | 0.0080378 | 0.0082518 | 0.063333 | 0.42114 | 0.3479 | 0.31128 | 0.42114 | 0.65002 | 0.37994 | 0.21973 | 0.009155 | 0.068665 | 0.036621 | 0.19226 | 0.11902 | -0.073242 | -0.15564 | 123.1338 | 122.9736 | 0.01831 | 123.1018 | 123.175 | 0.20142 | -0.21057 | 122.6807 | 122.5983 | -0.43945 | 122.7631 | 122.7905 | 0.19226 | -0.5127 | 123.4039 | 123.175 | 123.0652 | -0.41199 | 122.9462 | 122.8729 | 122.8226 | -0.78735
967.6875 | 123.4177 | -122.7036 | 0.65002 | 0.76669 | 0.099502 | 0.00053514 | 0.0184 | -0.019275 | 0.017644 | 0.026389 | 0.024973 | 0.025698 | -0.0020886 | 0.018719 | 0.0018428 | 0.030222 | 0.39825 | 0.36621 | 0.29755 | 0.41199 | 0.65002 | 0.38452 | 0.22888 | -0.027466 | -0.041199 | -0.091553 | 0.18768 | 0.12817 | -0.11902 | -0.16022 | 123.0881 | 122.9324 | 0 | 123.0698 | 123.1155 | 0.1831 | -0.25177 | 122.5845 | 122.5433 | -0.46234 | 122.6761 | 122.612 | 0.068664 | -0.52185 | 123.3536 | 123.1018 | 123.0011 | -0.42114 | 122.8912 | 122.8317 | 122.6624 | -0.81024
968.6875 | 123.3398 | -122.7676 | 0.64087 | 0.11056 | 0.11339 | 0.00053514 | 0.042967 | -0.022479 | 0.0048274 | 0.022116 | -0.066579 | 0.025698 | 0.0085924 | -0.0037112 | 0.0082518 | 0.038767 | 0.43488 | 0.35706 | 0.31128 | 0.41657 | 0.63629 | 0.3891 | 0.23346 | -0.036621 | -0.036621 | -0.09613 | 0.18768 | 0.14191 | -0.1236 | -0.17395 | 123.1567 | 123.0011 | -0.004577 | 123.1247 | 123.1842 | 0.18311 | -0.20599 | 122.644 | 122.5937 | -0.45319 | 122.731 | 122.6715 | 0.07782 | -0.49896 | 123.4039 | 123.2025 | 123.0789 | -0.40741 | 122.9553 | 122.9095 | 122.731 | -0.81482
969.7031 | 123.4955 | -122.7127 | 0.60883 | -0.042028 | 0.081344 | -0.0037369 | 0.010923 | -0.023548 | -0.01974 | 0.025321 | 0.33015 | 0.011812 | -0.015974 | 0.0016288 | -0.0034972 | 0.037699 | 0.50354 | 0.53101 | 0.45776 | 0.50354 | 0.58136 | 0.41657 | 0.26093 | 0.09613 | 0.11444 | 0.073242 | 0.14191 | 0.10529 | -0.064087 | -0.10986 | 123.1293 | 122.9736 | -0.027466 | 123.2437 | 123.2162 | 0.24261 | -0.10529 | 122.6486 | 122.6028 | -0.46692 | 122.8088 | 122.7859 | 0.18311 | -0.50354 | 123.2941 | 123.2162 | 123.1705 | -0.3479 | 122.8546 | 122.818 | 122.8271 | -0.71869
970.7031 | 123.4726 | -122.7264 | 0.6134 | 0.049525 | 0.062118 | 0.022966 | 0.0066513 | -0.028888 | -0.033625 | 0.006095 | 0.040232 | 0.0075398 | -0.020247 | -0.01012 | -0.014179 | 0.037699 | 0.43945 | 0.48065 | 0.42572 | 0.45776 | 0.6134 | 0.40741 | 0.25177 | 0.059509 | 0.10986 | 0.045776 | 0.16022 | 0.10529 | -0.073242 | -0.14191 | 123.1338 | 122.9782 | 0 | 123.2071 | 123.1842 | 0.20599 | -0.17395 | 122.6532 | 122.5845 | -0.45319 | 122.7859 | 122.7722 | 0.18768 | -0.50812 | 123.3398 | 123.1659 | 123.1522 | -0.36163 | 122.8867 | 122.8317 | 122.8363 | -0.75531
971.6875 | 123.381 | -122.7859 | 0.6546 | 0.20211 | 0.10164 | 0.0016041 | 0.029081 | -0.021411 | 0.020849 | 0.016776 | 0.07075 | 0.02997 | 0.0021844 | -0.011188 | -0.0088382 | 0.027017 | 0.42572 | 0.37537 | 0.3067 | 0.40741 | 0.65002 | 0.37994 | 0.2243 | -0.045776 | 0.027466 | -0.068665 | 0.19226 | 0.13733 | -0.09613 | -0.16022 | 123.1659 | 123.0103 | -0.004578 | 123.1613 | 123.1934 | 0.18311 | -0.22888 | 122.6898 | 122.6257 | -0.46234 | 122.7402 | 122.7173 | 0.091552 | -0.51727 | 123.436 | 123.2117 | 123.0927 | -0.4303 | 122.9782 | 122.9233 | 122.8134 | -0.81482
972.6875 | 123.3994 | -122.7585 | 0.59967 | 0.23263 | 0.14116 | 0.0016041 | 0.034422 | -0.0021852 | 0.0080314 | 0.011435 | 0.14704 | 0.0096758 | -0.0052926 | 0.016583 | 0.0071838 | 0.027017 | 0.4303 | 0.37537 | 0.33417 | 0.42114 | 0.63171 | 0.36621 | 0.21515 | 0.009155 | -0.018311 | -0.045776 | 0.19684 | 0.11444 | -0.086975 | -0.16479 | 123.1247 | 122.9736 | 0.032044 | 123.1338 | 123.1796 | 0.20599 | -0.16937 | 122.6715 | 122.5937 | -0.40283 | 122.7676 | 122.7127 | 0.11902 | -0.48523 | 123.3902 | 123.1888 | 123.0927 | -0.38452 | 122.9553 | 122.8729 | 122.7402 | -0.76447
973.6875 | 123.5001 | -122.7127 | 0.59052 | 0.47677 | 0.093094 | 0.0026721 | 0.0045153 | -0.011798 | -0.010127 | 0.025321 | 0.2386 | 0.016085 | -0.0074286 | -0.0026432 | 0.0071838 | 0.039835 | 0.44861 | 0.44861 | 0.38452 | 0.44861 | 0.6134 | 0.3891 | 0.22888 | 0.07782 | 0.059509 | 0.054932 | 0.14191 | 0.082397 | -0.068665 | -0.15106 | 123.1018 | 122.9416 | 0.022888 | 123.1613 | 123.1613 | 0.21973 | -0.14191 | 122.644 | 122.5616 | -0.44861 | 122.7905 | 122.7676 | 0.20599 | -0.50812 | 123.3261 | 123.1613 | 123.0972 | -0.36163 | 122.8546 | 122.7951 | 122.7722 | -0.74158
974.6875 | 123.3994 | -122.7539 | 0.61798 | -0.6829 | 0.099502 | 0.0016041 | 0.017332 | -0.022479 | 0.0069634 | 0.016776 | 0.086009 | 0.019289 | -0.015974 | -0.0037112 | 0.0029108 | 0.03663 | 0.41657 | 0.35706 | 0.31586 | 0.41657 | 0.64087 | 0.36163 | 0.24261 | 0.004578 | -0.045776 | -0.068665 | 0.17853 | 0.11902 | -0.10529 | -0.16937 | 123.1155 | 122.9965 | 0.022888 | 123.111 | 123.1705 | 0.17395 | -0.20142 | 122.6486 | 122.5845 | -0.43945 | 122.7585 | 122.6852 | 0.10071 | -0.49896 | 123.3948 | 123.1705 | 123.0698 | -0.37537 | 122.9324 | 122.8729 | 122.7081 | -0.78735
975.6875 | 123.3902 | -122.7768 | 0.59509 | 0.0037495 | 0.11125 | -0.0026689 | 0.019468 | -0.018207 | 0.017644 | 0.021048 | -0.20391 | 0.0096758 | 0.0075244 | 0.013378 | 0.0039788 | 0.034494 | 0.43945 | 0.42114 | 0.34332 | 0.4303 | 0.62256 | 0.36621 | 0.21515 | -0.009155 | -0.004578 | -0.086975 | 0.16022 | 0.10986 | -0.11444 | -0.17395 | 123.143 | 122.9919 | 0.027466 | 123.1979 | 123.2071 | 0.21515 | -0.15564 | 122.6624 | 122.6028 | -0.43488 | 122.7676 | 122.6898 | 0.086975 | -0.48523 | 123.3994 | 123.2162 | 123.1201 | -0.37994 | 122.937 | 122.8867 | 122.7722 | -0.76904
976.6875 | 123.3719 | -122.7768 | 0.6134 | 0.36996 | 0.12941 | 0.0048081 | 0.036558 | -0.01073 | 0.027258 | 0.040274 | -0.52434 | 0.019289 | 0.0011164 | 0.0059018 | 0.0061158 | 0.033426 | 0.24261 | 0.6958 | 0.40741 | 0.40741 | 0.66376 | 0.39825 | 0.23804 | 0 | -0.041199 | -0.07782 | 0.18768 | 0.13275 | -0.12817 | -0.17853 | 123.175 | 123.0148 | 0.050354 | 123.4726 | 123.1842 | 0.16937 | -0.37079 | 122.6486 | 122.5983 | -0.42572 | 122.7768 | 122.699 | 0.10071 | -0.48065 | 123.4406 | 123.0194 | 123.1842 | -0.37537 | 122.9645 | 122.9095 | 122.7356 | -0.79193
977.6875 | 123.5092 | -122.7402 | 0.58594 | 0.46151 | 0.074936 | 0.014421 | 0.017332 | -0.019275 | -0.0047856 | 0.031729 | 0.28437 | 0.01288 | -0.011702 | 0.0037648 | 0.0018428 | 0.030222 | 0.4715 | 0.5127 | 0.41657 | 0.4715 | 0.59509 | 0.39825 | 0.25635 | 0.09613 | 0.09613 | 0.041199 | 0.15106 | 0.086975 | -0.082397 | -0.1236 | 123.1384 | 122.9965 | 0.009156 | 123.2529 | 123.2117 | 0.21515 | -0.11444 | 122.6578 | 122.6166 | -0.43488 | 122.8363 | 122.7814 | 0.16479 | -0.49896 | 123.3353 | 123.2117 | 123.1567 | -0.32959 | 122.8912 | 122.8271 | 122.8363 | -0.70953
978.6875 | 123.4314 | -122.7356 | 0.6134 | 0.33944 | 0.11552 | 0.0026721 | 0.019468 | -0.011798 | 0.0026914 | 0.024253 | 0.17756 | 0.011812 | -0.0063606 | -0.013324 | 0.0061158 | 0.023813 | 0.42572 | 0.37537 | 0.30212 | 0.39825 | 0.63629 | 0.36163 | 0.21515 | 0.009155 | 0 | -0.032043 | 0.17853 | 0.11902 | -0.09613 | -0.16022 | 123.0972 | 122.9507 | 0.022889 | 123.111 | 123.1338 | 0.1831 | -0.18768 | 122.6395 | 122.5754 | -0.43488 | 122.7448 | 122.7036 | 0.12817 | -0.49438 | 123.3719 | 123.1613 | 123.0377 | -0.39825 | 122.9141 | 122.8546 | 122.7356 | -0.77362
979.6875 | 123.4085 | -122.7676 | 0.60425 | 0.29367 | 0.10271 | 0.0069441 | 0.033354 | -0.01073 | 0.0026914 | 0.031729 | 0.13178 | 0.018221 | -0.0020886 | 0.014447 | 0.0082518 | 0.020609 | 0.40741 | 0.37079 | 0.31128 | 0.41657 | 0.63171 | 0.35706 | 0.21515 | -0.004578 | -0.027466 | -0.041199 | 0.15564 | 0.10986 | -0.091553 | -0.17395 | 123.1247 | 122.9828 | 0.027466 | 123.1384 | 123.1842 | 0.20142 | -0.19684 | 122.6761 | 122.5937 | -0.44861 | 122.7631 | 122.7264 | 0.13275 | -0.49439 | 123.3994 | 123.175 | 123.0789 | -0.3891 | 122.9233 | 122.8775 | 122.7402 | -0.7782
980.6875 | 123.4085 | -122.7768 | 0.59967 | 0.11056 | 0.088821 | 0.0026721 | 0.022672 | -0.0043222 | -0.0037176 | 0.024253 | 0.19282 | 0.020357 | -0.0084976 | 0.0048338 | -0.0013612 | 0.037699 | 0.40283 | 0.36621 | 0.31586 | 0.42572 | 0.62256 | 0.35248 | 0.22888 | 0.004578 | -0.027466 | -0.050354 | 0.17853 | 0.1236 | -0.09613 | -0.16937 | 123.1293 | 123.0057 | 0.022889 | 123.143 | 123.2025 | 0.19684 | -0.19684 | 122.6807 | 122.6074 | -0.42114 | 122.7814 | 122.7264 | 0.11902 | -0.47607 | 123.3994 | 123.1796 | 123.0927 | -0.37079 | 122.9553 | 122.9004 | 122.7493 | -0.76904
981.6875 | 123.4909 | -122.7585 | 0.59509 | 0.46151 | 0.10698 | 0.0037401 | 0.034422 | -0.020343 | -0.00051261 | 0.021048 | 0.25385 | 0.011812 | -0.0063606 | 0.0069698 | 0.0007748 | 0.033426 | 0.4303 | 0.42114 | 0.35706 | 0.42114 | 0.6134 | 0.36163 | 0.2243 | 0.054932 | 0.064087 | 0.013733 | 0.17853 | 0.10529 | -0.082397 | -0.14191 | 123.1201 | 122.9828 | 0.01831 | 123.1796 | 123.1796 | 0.19684 | -0.16479 | 122.6761 | 122.6166 | -0.41656 | 122.8134 | 122.7722 | 0.15564 | -0.48981 | 123.3719 | 123.1888 | 123.1155 | -0.37079 | 122.937 | 122.8638 | 122.8226 | -0.737
982.6875 | 123.3902 | -122.7997 | 0.60883 | -0.057287 | 0.123 | 0.0037401 | 0.03549 | -0.020343 | 0.011236 | 0.018912 | -0.21917 | 0.0054038 | -0.0063606 | -0.0037112 | 0.0050478 | 0.021677 | 0.42572 | 0.40741 | 0.33875 | 0.40741 | 0.6134 | 0.35248 | 0.21057 | -0.004578 | -0.009155 | -0.082397 | 0.15564 | 0.10986 | -0.12817 | -0.1831 | 123.1522 | 123.0103 | 0.004577 | 123.2071 | 123.2071 | 0.19684 | -0.18311 | 122.6715 | 122.6166 | -0.45319 | 122.7951 | 122.7173 | 0.10071 | -0.49896 | 123.4131 | 123.2254 | 123.1384 | -0.39825 | 122.9553 | 122.9095 | 122.7905 | -0.79193
983.6875 | 123.349 | -122.7631 | 0.61798 | 0.034266 | 0.10591 | 0.0048081 | 0.0087873 | -0.012866 | 0.0058954 | 0.026389 | -0.24969 | 0.022493 | -0.01277 | 0.00056082 | 0.011456 | 0.015268 | 0.37079 | 0.35248 | 0.29297 | 0.3891 | 0.60425 | 0.35706 | 0.20142 | -0.059509 | -0.032043 | -0.11902 | 0.16937 | 0.12817 | -0.13275 | -0.18768 | 123.1201 | 122.9645 | -0.013733 | 123.1155 | 123.1522 | 0.18768 | -0.24719 | 122.6303 | 122.5754 | -0.44861 | 122.7036 | 122.644 | 0.068664 | -0.48981 | 123.3673 | 123.1339 | 123.056 | -0.41656 | 122.9324 | 122.8912 | 122.731 | -0.80566
984.6875 | 123.4222 | -122.7768 | 0.59509 | 0.30892 | 0.10484 | 0.0080121 | 0.017332 | -0.0064582 | -0.0015816 | 0.01998 | 0.22334 | 0.026766 | -0.0074286 | -0.0026432 | -0.0013612 | 0.027017 | 0.3891 | 0.37537 | 0.29297 | 0.40283 | 0.62256 | 0.36163 | 0.21515 | 0 | -0.013733 | -0.036621 | 0.16937 | 0.11444 | -0.10986 | -0.15564 | 123.1384 | 122.9919 | 0.027466 | 123.1522 | 123.1796 | 0.18768 | -0.20599 | 122.6669 | 122.6212 | -0.42572 | 122.7768 | 122.7402 | 0.11902 | -0.48065 | 123.3994 | 123.1659 | 123.0698 | -0.37994 | 122.9462 | 122.8912 | 122.7631 | -0.75073
985.6875 | 123.4909 | -122.7219 | 0.56305 | 0.40048 | 0.10805 | 0.0069441 | 0.019468 | -0.013935 | -0.012263 | 0.022116 | 0.26911 | 0.020357 | -0.011702 | -0.0037112 | 0.0007748 | 0.034494 | 0.41657 | 0.42572 | 0.37537 | 0.42572 | 0.59967 | 0.37537 | 0.2243 | 0.050354 | 0.082397 | 0.018311 | 0.14191 | 0.10529 | -0.091553 | -0.16022 | 123.0972 | 122.9462 | 0.036621 | 123.1476 | 123.1476 | 0.20142 | -0.14648 | 122.6303 | 122.5616 | -0.42114 | 122.7722 | 122.7402 | 0.17853 | -0.45776 | 123.3215 | 123.1384 | 123.0972 | -0.33875 | 122.8638 | 122.8271 | 122.8043 | -0.72327
986.6875 | 123.3673 | -122.7997 | 0.60425 | 0.080043 | 0.10057 | -0.00053286 | 0.029081 | -0.0043222 | 0.0048274 | 0.033866 | -0.005544 | 0.022493 | 4.7432e-05 | 0.0069698 | 0.012524 | 0.024881 | 0.34332 | 0.33417 | 0.27924 | 0.37537 | 0.62714 | 0.36163 | 0.19226 | -0.022888 | -0.041199 | -0.086975 | 0.19226 | 0.1236 | -0.11902 | -0.17853 | 123.1613 | 122.9919 | 0.022888 | 123.1338 | 123.175 | 0.1831 | -0.26093 | 122.6807 | 122.6212 | -0.41199 | 122.7768 | 122.7127 | 0.091553 | -0.48065 | 123.4268 | 123.143 | 123.0789 | -0.41199 | 122.9919 | 122.9233 | 122.7585 | -0.78278
987.6875 | 123.3536 | -122.7859 | 0.59967 | 0.049525 | 0.15077 | -0.00053286 | 0.042967 | -0.016071 | -0.0015816 | 0.026389 | 0.13178 | 0.011812 | 0.017137 | -0.00050718 | 0.010388 | 0.03129 | 0.36163 | 0.37079 | 0.29755 | 0.40283 | 0.58594 | 0.32959 | 0.20142 | -0.059509 | -0.041199 | -0.10986 | 0.16937 | 0.11902 | -0.10986 | -0.17395 | 123.1155 | 122.9874 | -0.013733 | 123.1567 | 123.1888 | 0.20142 | -0.23804 | 122.6761 | 122.612 | -0.4303 | 122.7264 | 122.6761 | 0.064087 | -0.48065 | 123.3719 | 123.1476 | 123.0835 | -0.39825 | 122.9553 | 122.905 | 122.7448 | -0.77362
988.6875 | 123.3902 | -122.7859 | 0.60425 | 0.27841 | 0.11552 | 0.0016041 | 0.032286 | -0.024616 | 0.0069634 | 0.024253 | -1.0889 | 0.019289 | -0.0031566 | 0.011242 | 0.0007748 | 0.039835 | 0.36621 | 0.34332 | 0.27924 | 0.39825 | 0.61798 | 0.35248 | 0.2243 | -0.027466 | -0.022888 | -0.07782 | 0.1831 | 0.13275 | -0.10986 | -0.16022 | 123.1384 | 123.0103 | 0.013733 | 123.1293 | 123.1842 | 0.17395 | -0.23804 | 122.6761 | 122.6257 | -0.42114 | 122.7585 | 122.7081 | 0.082397 | -0.4715 | 123.4039 | 123.1522 | 123.0652 | -0.37994 | 122.9691 | 122.9187 | 122.7631 | -0.76446
989.7031 | 123.4955 | -122.7493 | 0.59052 | 0.33944 | 0.090957 | 0.0048081 | 0.013059 | -0.022479 | -0.030421 | 0.017844 | 0.40644 | 0.0075398 | -0.018111 | 0.0037648 | -0.0024292 | 0.046244 | 0.44861 | 0.49896 | 0.4303 | 0.46692 | 0.5722 | 0.39368 | 0.26093 | 0.091553 | 0.091553 | 0.064087 | 0.14648 | 0.1236 | -0.068665 | -0.14191 | 123.143 | 123.0103 | -0.01831 | 123.2483 | 123.2162 | 0.20599 | -0.14191 | 122.6807 | 122.6074 | -0.44403 | 122.8409 | 122.8134 | 0.20599 | -0.46692 | 123.3215 | 123.1979 | 123.1796 | -0.32959 | 122.8958 | 122.8729 | 122.8409 | -0.73242
990.6875 | 123.4177 | -122.7997 | 0.59967 | -0.22513 | 0.10057 | 0.0048081 | 0.036558 | -0.01073 | 0.0080314 | 0.015708 | 0.14704 | 0.016085 | -0.0095656 | 0.021923 | 0.0029108 | 0.021677 | 0.39825 | 0.33417 | 0.27924 | 0.37994 | 0.64087 | 0.36163 | 0.21973 | -0.009155 | -0.036621 | -0.059509 | 0.17853 | 0.11902 | -0.10986 | -0.1831 | 123.1613 | 123.0194 | 0.041199 | 123.1338 | 123.1796 | 0.16022 | -0.20142 | 122.6898 | 122.6166 | -0.42114 | 122.7905 | 122.7402 | 0.1236 | -0.48065 | 123.4406 | 123.1979 | 123.0789 | -0.37994 | 122.9782 | 122.9187 | 122.7631 | -0.78277
991.6875 | 123.3627 | -122.8088 | 0.59052 | -0.01151 | 0.10271 | 0.013353 | 0.023741 | -0.021411 | 0.0069634 | 0.036002 | 0.54377 | 0.018221 | -0.0074286 | -0.0079842 | 0.0007748 | 0.029154 | 0.36163 | 0.35706 | 0.27466 | 0.37994 | 0.60883 | 0.33417 | 0.19226 | -0.045776 | -0.059509 | -0.10529 | 0.1831 | 0.10986 | -0.11902 | -0.19226 | 123.143 | 123.0011 | 0.018311 | 123.1659 | 123.1888 | 0.18768 | -0.22888 | 122.6898 | 122.6166 | -0.40741 | 122.7631 | 122.7036 | 0.086975 | -0.48065 | 123.4177 | 123.1705 | 123.0835 | -0.39825 | 122.9919 | 122.9187 | 122.7493 | -0.78278
992.6875 | 123.3994 | -122.7997 | 0.60883 | 0.24789 | 0.10377 | 0.0026721 | 0.032286 | -0.015003 | 0.0069634 | 0.024253 | -0.58538 | 0.0032668 | -0.0063606 | 0.0016288 | -0.0034972 | 0.03129 | 0.36163 | 0.36163 | 0.28839 | 0.3891 | 0.64087 | 0.33875 | 0.20599 | -0.018311 | -0.018311 | -0.073242 | 0.19226 | 0.14648 | -0.10986 | -0.18768 | 123.1384 | 123.0057 | 0.032043 | 123.1613 | 123.1888 | 0.1831 | -0.24719 | 122.6898 | 122.612 | -0.41656 | 122.7814 | 122.7264 | 0.11444 | -0.46234 | 123.4406 | 123.1613 | 123.0881 | -0.40283 | 122.9919 | 122.9462 | 122.7814 | -0.79651
993.6875 | 123.3994 | -122.7951 | 0.58594 | 0.431 | 0.1262 | 0.00053514 | 0.026945 | -0.016071 | -0.00051261 | 0.027457 | 0.14704 | 0.01288 | -0.015974 | 0.010174 | 0.0029108 | 0.044107 | 0.37537 | 0.37079 | 0.28839 | 0.37994 | 0.62714 | 0.33875 | 0.1831 | -0.013733 | -0.018311 | -0.059509 | 0.1831 | 0.09613 | -0.09613 | -0.17395 | 123.1339 | 122.9782 | 0.041199 | 123.1659 | 123.175 | 0.19684 | -0.21057 | 122.699 | 122.6212 | -0.40283 | 122.7814 | 122.7356 | 0.11444 | -0.48981 | 123.4222 | 123.1705 | 123.0835 | -0.40283 | 122.9782 | 122.8912 | 122.7768 | -0.75989
994.6875 | 123.3765 | -122.8043 | 0.59509 | 0.21737 | 0.12727 | 0.024034 | 0.026945 | -0.012866 | 0.010168 | 0.025321 | 0.13178 | 0.026766 | -0.0074286 | 0.0026968 | 0.0029108 | 0.022745 | 0.35706 | 0.35706 | 0.27466 | 0.39825 | 0.59509 | 0.32959 | 0.21057 | -0.059509 | -0.050354 | -0.091553 | 0.1831 | 0.13275 | -0.10529 | -0.19684 | 123.1338 | 123.0148 | 0 | 123.1613 | 123.2025 | 0.18768 | -0.23804 | 122.699 | 122.6074 | -0.41199 | 122.7448 | 122.7127 | 0.10529 | -0.46234 | 123.3994 | 123.1613 | 123.0789 | -0.38452 | 122.9874 | 122.937 | 122.7539 | -0.79193
995.6875 | 123.4131 | -122.8134 | 0.59052 | -0.026769 | 0.10164 | 0.0080121 | 0.024809 | -0.017139 | 0.010168 | 0.030661 | -0.2802 | 0.026766 | 4.7432e-05 | 0.015515 | 0.0050478 | 0.030222 | 0.43488 | 0.42572 | 0.35706 | 0.41657 | 0.5722 | 0.35248 | 0.20142 | 0.009155 | 0.004578 | -0.054932 | 0.16479 | 0.11902 | -0.10529 | -0.18768 | 123.1659 | 123.0148 | -0.01831 | 123.2391 | 123.23 | 0.21515 | -0.15564 | 122.7081 | 122.6257 | -0.42572 | 122.8226 | 122.7585 | 0.13275 | -0.4715 | 123.3856 | 123.2483 | 123.1705 | -0.3891 | 122.9782 | 122.9324 | 122.818 | -0.7782
996.6875 | 123.4177 | -122.7951 | 0.5722 | 0.26315 | 0.10164 | 0.0016041 | 0.026945 | -0.020343 | 0.0048274 | 0.016776 | -0.2802 | 0.021425 | 0.0021844 | -0.0090522 | 0.016797 | 0.032358 | 0.43488 | 0.43488 | 0.34332 | 0.40283 | 0.60883 | 0.36163 | 0.2243 | 0.018311 | 0.036621 | -0.045776 | 0.15564 | 0.1236 | -0.10529 | -0.17395 | 123.1567 | 123.0194 | 0.036621 | 123.23 | 123.1979 | 0.17853 | -0.13733 | 122.6898 | 122.6212 | -0.41656 | 122.8134 | 122.7493 | 0.12817 | -0.44861 | 123.4039 | 123.23 | 123.1384 | -0.3479 | 122.9507 | 122.9187 | 122.8317 | -0.74615
997.6875 | 123.381 | -122.7859 | 0.5722 | -0.042028 | 0.10805 | 0.00053514 | 0.028013 | -0.01073 | 0.011236 | 0.024253 | -0.15813 | 0.0096758 | -0.0010206 | -0.0015752 | 0.0071838 | 0.043039 | 0.39368 | 0.3891 | 0.31128 | 0.39368 | 0.59052 | 0.35248 | 0.18768 | -0.032043 | 0 | -0.07782 | 0.17395 | 0.12817 | -0.11444 | -0.17853 | 123.1384 | 122.9736 | 0.01831 | 123.175 | 123.1796 | 0.20599 | -0.17853 | 122.6715 | 122.6074 | -0.39825 | 122.7539 | 122.7081 | 0.10071 | -0.44403 | 123.3765 | 123.1796 | 123.0972 | -0.38452 | 122.9599 | 122.9141 | 122.7859 | -0.75073
998.6875 | 123.4039 | -122.7951 | 0.58136 | 0.019007 | 0.092026 | 0.011217 | 0.038694 | -0.0096622 | 0.0058954 | 0.031729 | -0.21917 | 0.021425 | -0.0052926 | -0.0026432 | -0.0034972 | 0.025949 | 0.40283 | 0.41657 | 0.32501 | 0.41199 | 0.59052 | 0.3479 | 0.18768 | -0.027466 | 0.004578 | -0.050354 | 0.14648 | 0.1236 | -0.10071 | -0.17853 | 123.143 | 122.9828 | 0.009155 | 123.2117 | 123.2071 | 0.2243 | -0.17853 | 122.6944 | 122.6166 | -0.43488 | 122.7676 | 122.7448 | 0.12817 | -0.45776 | 123.3856 | 123.1979 | 123.1201 | -0.39368 | 122.9416 | 122.9187 | 122.7997 | -0.75989
999.6875 | 123.3994 | -122.8043 | 0.59967 | 0.29367 | 0.11339 | 0.015489 | 0.0184 | -0.012866 | 0.0080314 | 0.007163 | 0.055491 | 0.016085 | 0.0011164 | 0.0080378 | -0.0013612 | 0.033426 | 0.33875 | 0.32044 | 0.25177 | 0.36163 | 0.61798 | 0.34332 | 0.1831 | -0.018311 | -0.19684 | -0.091553 | 0.1831 | 0.13275 | -0.09613 | -0.14648 | 123.1476 | 122.9874 | 0.018311 | 123.1247 | 123.1659 | 0.17853 | -0.26093 | 122.7081 | 122.6578 | -0.41657 | 122.7859 | 122.7127 | 0.054931 | -0.46692 | 123.4222 | 123.143 | 123.056 | -0.41657 | 122.9874 | 122.937 | 122.6074 | -0.74615
1000.6875 | 123.4222 | -122.7951 | 0.58136 | -0.11832 | 0.087753 | -0.0037369 | 0.023741 | -0.028888 | 0.011236 | 0.015708 | -0.29546 | 0.017153 | -0.013838 | -0.0069162 | 0.0061158 | 0.035562 | 0.48523 | 0.46234 | 0.37079 | 0.41657 | 0.6546 | 0.40741 | 0.27008 | 0.022888 | 0.032043 | -0.032043 | 0.17853 | 0.13275 | -0.10071 | -0.17853 | 123.2025 | 123.0652 | 0.073242 | 123.2574 | 123.2117 | 0.14648 | -0.096131 | 122.6944 | 122.6166 | -0.40283 | 122.818 | 122.7631 | 0.14648 | -0.44861 | 123.4497 | 123.2803 | 123.1659 | -0.31128 | 122.9736 | 122.9279 | 122.8271 | -0.75989
1001.6875 | 123.3673 | -122.818 | 0.58594 | 0.26315 | 0.10377 | -0.0037369 | 0.038694 | -0.013935 | 0.0048274 | 0.013571 | 0.31489 | 0.022493 | -0.0074286 | 0.0048338 | 0.0061158 | 0.043039 | 0.34332 | 0.33417 | 0.27008 | 0.38452 | 0.59052 | 0.32501 | 0.19226 | -0.064087 | -0.045776 | -0.10986 | 0.18768 | 0.13733 | -0.12817 | -0.17395 | 123.143 | 123.0103 | 0.004578 | 123.1522 | 123.2025 | 0.19226 | -0.24261 | 122.6898 | 122.644 | -0.39825 | 122.7539 | 122.7081 | 0.064087 | -0.44861 | 123.4085 | 123.1613 | 123.0881 | -0.39368 | 123.0057 | 122.9553 | 122.7722 | -0.75989
1002.6875 | 123.4543 | -122.7356 | 0.66834 | -0.10306 | 0.11446 | -0.0016009 | 0.021604 | -0.019275 | 0.0080314 | 0.024253 | -0.31072 | 0.015017 | -0.0031566 | 0.0048338 | 0.0029108 | 0.038767 | 0.41199 | 0.41199 | 0.3479 | 0.41199 | 0.60883 | 0.34332 | 0.20142 | 0.027466 | 0.073242 | 0.17395 | 0.17853 | 0.15564 | -0.068665 | -0.11444 | 123.0789 | 122.937 | -0.059509 | 123.1476 | 123.1476 | 0.21057 | -0.25635 | 122.6669 | 122.6212 | -0.48981 | 122.7631 | 122.9095 | 0.28839 | -0.5127 | 123.3444 | 123.1476 | 123.0835 | -0.46692 | 122.9141 | 122.8912 | 122.8088 | -0.78278
1003.6875 | 123.4406 | -122.8043 | 0.5722 | -0.22513 | 0.099502 | -0.0080089 | 0.028013 | -0.017139 | 0.0048274 | 0.024253 | -0.37176 | 0.016085 | -0.0063606 | 0.00056082 | -0.0045652 | 0.040903 | 0.39368 | 0.4303 | 0.33417 | 0.42114 | 0.59509 | 0.32501 | 0.19226 | 0 | 0.050354 | -0.018311 | 0.17395 | 0.12817 | -0.10071 | -0.16022 | 123.1293 | 122.9965 | 0.022888 | 123.2346 | 123.2254 | 0.22888 | -0.17853 | 122.7036 | 122.644 | -0.39825 | 122.8043 | 122.7859 | 0.14191 | -0.44403 | 123.3994 | 123.1979 | 123.1384 | -0.37994 | 122.9782 | 122.9324 | 122.8546 | -0.73242
1004.6875 | 123.3902 | -122.8134 | 0.56763 | 0.034266 | 0.12193 | -0.0037369 | 0.028013 | -0.01073 | 0.0037594 | 0.016776 | -0.15813 | 0.015017 | -0.0084976 | 0.0037648 | 0.0039788 | 0.034494 | 0.37994 | 0.39368 | 0.30212 | 0.38452 | 0.58594 | 0.32959 | 0.18768 | -0.041199 | -0.013733 | -0.07782 | 0.17395 | 0.11444 | -0.1236 | -0.1831 | 123.143 | 123.0011 | 0.01831 | 123.2071 | 123.1979 | 0.19684 | -0.18768 | 122.6898 | 122.6303 | -0.39368 | 122.7722 | 122.7356 | 0.10528 | -0.45319 | 123.3994 | 123.1934 | 123.1155 | -0.37994 | 122.9874 | 122.9279 | 122.7997 | -0.75073
1005.6875 | 123.3994 | -122.8271 | 0.5722 | -0.057287 | 0.09523 | 0.0048081 | 0.029081 | -0.013935 | 0.013372 | 0.028525 | -0.097097 | 0.027834 | 0.0096604 | 0.00056082 | 0.0007748 | 0.024881 | 0.39368 | 0.39825 | 0.31128 | 0.3891 | 0.60883 | 0.33417 | 0.1831 | -0.036621 | 0.009155 | -0.073242 | 0.17395 | 0.12817 | -0.1236 | -0.18768 | 123.1613 | 123.0103 | 0.036621 | 123.2254 | 123.2162 | 0.20599 | -0.17853 | 122.7036 | 122.6395 | -0.39825 | 122.7905 | 122.7539 | 0.11444 | -0.44403 | 123.436 | 123.2208 | 123.1384 | -0.3891 | 123.0011 | 122.9553 | 122.8363 | -0.75989
1006.6875 | 123.381 | -122.85 | 0.59052 | 0.064784 | 0.11018 | 0.010148 | 0.038694 | -0.017139 | 0.011236 | 0.017844 | -0.005544 | 0.020357 | -0.0084976 | -0.0047802 | 0.0018428 | 0.033426 | 0.33875 | 0.33875 | 0.2655 | 0.37079 | 0.58136 | 0.32044 | 0.17395 | -0.059509 | -0.050354 | -0.082397 | 0.16937 | 0.1236 | -0.1236 | -0.17395 | 123.1705 | 123.024 | -0.009155 | 123.1888 | 123.2208 | 0.19684 | -0.25177 | 122.7264 | 122.6761 | -0.42114 | 122.7905 | 122.7676 | 0.091553 | -0.46692 | 123.4314 | 123.1888 | 123.1155 | -0.41657 | 123.0194 | 122.9736 | 122.7997 | -0.76446
1007.6875 | 123.3627 | -122.6761 | 0.63171 | -0.087804 | 0.096298 | 0.0090801 | 0.026945 | -0.012866 | 0.010168 | 0.028525 | -0.31072 | 0.017153 | -0.015974 | -0.018665 | 0.0082518 | 0.03129 | 0.41199 | 0.42114 | 0.33417 | 0.41199 | 0.59967 | 0.33417 | 0.19684 | 0.013733 | 0.054932 | -0.018311 | 0.16479 | 0.11444 | -0.10071 | -0.17395 | 123.0103 | 122.8729 | -0.032044 | 123.0972 | 123.0881 | 0.21515 | -0.21973 | 122.5754 | 122.5021 | -0.46692 | 122.6898 | 122.6578 | 0.15564 | -0.51727 | 123.2758 | 123.0881 | 123.0103 | -0.43488 | 122.8409 | 122.7905 | 122.731 | -0.80566
1008.6875 | 123.436 | -122.7859 | 0.58594 | -0.31669 | 0.10591 | 0.0016041 | 0.034422 | -0.021411 | 0.0058954 | 0.017844 | -0.34124 | 0.020357 | 4.7432e-05 | 0.0091058 | -0.0024292 | 0.024881 | 0.3891 | 0.4303 | 0.32501 | 0.42572 | 0.59509 | 0.35248 | 0.17853 | 0.004578 | 0.059509 | -0.009155 | 0.17853 | 0.12817 | -0.10529 | -0.16937 | 123.1384 | 122.9645 | 0.009156 | 123.2162 | 123.2117 | 0.24719 | -0.19684 | 122.6807 | 122.6166 | -0.40741 | 122.7905 | 122.7768 | 0.16022 | -0.45776 | 123.381 | 123.175 | 123.111 | -0.40741 | 122.9645 | 122.9141 | 122.8455 | -0.75531
1009.6875 | 123.3627 | -122.8043 | 0.57678 | 0.095301 | 0.099502 | -0.00053286 | 0.022672 | -0.0064582 | 0.012304 | 0.023184 | 0.1623 | 0.016085 | -0.0052926 | -0.0047802 | 0.0029108 | 0.034494 | 0.32959 | 0.32959 | 0.24261 | 0.34332 | 0.59509 | 0.33417 | 0.17395 | -0.045776 | -0.054932 | -0.073242 | 0.17853 | 0.1236 | -0.1236 | -0.18768 | 123.1384 | 122.9782 | 0.018311 | 123.1338 | 123.1476 | 0.16937 | -0.24719 | 122.6807 | 122.6166 | -0.39825 | 122.7585 | 122.731 | 0.11444 | -0.45319 | 123.3994 | 123.1338 | 123.0469 | -0.40283 | 122.9828 | 122.9279 | 122.7493 | -0.76446
1010.6875 | 123.4039 | -122.8271 | 0.5722 | -0.057287 | 0.10591 | 0.02083 | 0.034422 | -0.017139 | 0.0080314 | 0.017844 | -0.14287 | 0.022493 | -0.0095656 | -0.00050718 | 0.0018428 | 0.039835 | 0.39368 | 0.40741 | 0.30212 | 0.39368 | 0.59509 | 0.31586 | 0.1831 | -0.036621 | -0.004578 | -0.068665 | 0.16479 | 0.1236 | -0.11902 | -0.1831 | 123.143 | 123.0103 | 0.022888 | 123.2346 | 123.2208 | 0.21057 | -0.17853 | 122.7081 | 122.644 | -0.40741 | 122.7905 | 122.7585 | 0.11444 | -0.44861 | 123.4222 | 123.2208 | 123.1293 | -0.3891 | 122.9919 | 122.9507 | 122.8226 | -0.75531
1011.6875 | 123.4268 | -122.7905 | 0.62714 | -0.22513 | 0.10377 | -0.0058729 | 0.032286 | -0.0085942 | 0.0016234 | 0.016776 | -0.32598 | 0.01288 | -0.013838 | 0.0059018 | -0.0099062 | 0.022745 | 0.39368 | 0.41657 | 0.33417 | 0.42572 | 0.58594 | 0.3479 | 0.16479 | 0.041199 | 0.09613 | -0.018311 | 0.23346 | 0.1831 | -0.045776 | -0.10986 | 123.1384 | 122.9553 | -0.041199 | 123.2071 | 123.2162 | 0.26092 | -0.23346 | 122.7448 | 122.6807 | -0.39368 | 122.8317 | 122.7722 | 0.091552 | -0.44403 | 123.3765 | 123.1842 | 123.1247 | -0.46234 | 123.024 | 122.9736 | 122.8867 | -0.737
1012.6875 | 123.4634 | -122.7402 | 0.63171 | -0.14884 | 0.089889 | 0.012285 | 0.033354 | -0.012866 | 0.00055539 | 0.015708 | -0.31072 | 0.018221 | -0.017042 | 0.0026968 | 0.0050478 | 0.03129 | 0.41199 | 0.42114 | 0.33417 | 0.40283 | 0.59509 | 0.33417 | 0.18768 | 0.013733 | 0.054932 | 0 | 0.16479 | 0.12817 | -0.091553 | -0.14191 | 123.0743 | 122.9279 | -0.036621 | 123.1613 | 123.143 | 0.21515 | -0.21973 | 122.6486 | 122.5983 | -0.46692 | 122.7539 | 122.7402 | 0.14191 | -0.50354 | 123.3353 | 123.1522 | 123.0743 | -0.44403 | 122.905 | 122.8683 | 122.7951 | -0.77362
1013.6875 | 123.4268 | -122.8409 | 0.5722 | -0.65238 | 0.1198 | 0.0016041 | 0.026945 | -0.0043222 | 0.013372 | 0.022116 | -0.24969 | 0.011812 | -0.01277 | -0.0079842 | -0.0056342 | 0.040903 | 0.41657 | 0.42572 | 0.32959 | 0.40741 | 0.6134 | 0.35706 | 0.21515 | -0.013733 | 0.022888 | -0.032043 | 0.16479 | 0.10986 | -0.11444 | -0.18768 | 123.1979 | 123.056 | 0.041198 | 123.2666 | 123.2483 | 0.19226 | -0.15564 | 122.7264 | 122.6532 | -0.40741 | 122.8271 | 122.8088 | 0.15564 | -0.46234 | 123.4543 | 123.2574 | 123.1705 | -0.35706 | 123.0057 | 122.9507 | 122.8638 | -0.75989
1014.6875 | 123.3765 | -122.8317 | 0.57678 | 0.019007 | 0.098434 | -0.0090779 | 0.025877 | -0.0021852 | 0.0037594 | 0.024253 | -0.005544 | 0.016085 | -0.0052926 | 0.0069698 | -0.0067022 | 0.020609 | 0.3479 | 0.37079 | 0.28839 | 0.36621 | 0.58594 | 0.3067 | 0.16937 | -0.036621 | -0.036621 | -0.082397 | 0.15106 | 0.10986 | -0.1236 | -0.21057 | 123.1384 | 123.0011 | 0.009155 | 123.2025 | 123.1979 | 0.19684 | -0.22888 | 122.7081 | 122.6212 | -0.42572 | 122.7951 | 122.7493 | 0.12817 | -0.46692 | 123.4177 | 123.1796 | 123.1201 | -0.40741 | 122.9828 | 122.9416 | 122.7951 | -0.78735
1015.6875 | 123.4451 | -122.8134 | 0.59052 | -0.31669 | 0.085617 | 0.014421 | 0.021604 | -0.01073 | 0.0016234 | 0.00289 | -0.69219 | 0.019289 | -0.0074286 | 0.0037648 | -0.0088382 | 0.024881 | 0.36621 | 0.3891 | 0.32501 | 0.41657 | 0.58136 | 0.33417 | 0.17853 | 0.004578 | 0.050354 | -0.013733 | 0.16937 | 0.10529 | -0.11902 | -0.16022 | 123.1476 | 122.9919 | -0.009155 | 123.2025 | 123.23 | 0.23804 | -0.2243 | 122.6944 | 122.6532 | -0.42114 | 122.818 | 122.7997 | 0.14648 | -0.48523 | 123.3948 | 123.1796 | 123.1384 | -0.41199 | 122.9828 | 122.9187 | 122.8638 | -0.75073
1016.6875 | 123.4085 | -122.8226 | 0.58594 | -0.33194 | 0.11446 | 0.0080121 | 0.020536 | 0.0020868 | -0.011195 | 0.013571 | -0.46331 | 0.016085 | -0.021315 | 0.010174 | -0.0045652 | 0.028086 | 0.33875 | 0.36621 | 0.27008 | 0.37537 | 0.59052 | 0.32044 | 0.16479 | -0.059509 | 0.018311 | -0.045776 | 0.18768 | 0.13275 | -0.12817 | -0.18768 | 123.143 | 122.9874 | 0.004578 | 123.1888 | 123.1979 | 0.21057 | -0.24719 | 122.6944 | 122.6349 | -0.39825 | 122.7631 | 122.7768 | 0.14191 | -0.45319 | 123.4131 | 123.1613 | 123.0927 | -0.42114 | 123.0103 | 122.9553 | 122.8409 | -0.77362
1017.6875 | 123.4451 | -122.8271 | 0.57678 | -0.33194 | 0.10591 | 0.0090801 | 0.026945 | -0.01073 | 0.0026914 | 0.021048 | -0.43279 | 0.017153 | -0.014906 | 0.01231 | 0.0050478 | 0.024881 | 0.36163 | 0.38452 | 0.27924 | 0.38452 | 0.58136 | 0.32044 | 0.15106 | -0.009155 | 0.022888 | -0.032043 | 0.16479 | 0.11902 | -0.11902 | -0.1831 | 123.1476 | 122.9782 | 0.004578 | 123.2117 | 123.2117 | 0.23346 | -0.21515 | 122.7081 | 122.644 | -0.41199 | 122.818 | 122.7951 | 0.15106 | -0.45776 | 123.4085 | 123.1888 | 123.1064 | -0.42572 | 122.9919 | 122.9462 | 122.85 | -0.75989
1018.6875 | 123.4131 | -122.8317 | 0.55847 | -0.1641 | 0.1198 | -0.0016009 | 0.049375 | -0.012866 | 0.010168 | 0.023184 | -0.20391 | 0.018221 | -0.0052926 | 0.0048338 | 0.0061158 | 0.029154 | 0.39368 | 0.42114 | 0.32501 | 0.39825 | 0.56305 | 0.32044 | 0.16937 | -0.009155 | 0.009155 | -0.041199 | 0.16937 | 0.11444 | -0.11444 | -0.16937 | 123.1522 | 123.0011 | 0.004577 | 123.2529 | 123.23 | 0.22888 | -0.16479 | 122.7173 | 122.6624 | -0.3891 | 122.8226 | 122.7905 | 0.12817 | -0.44403 | 123.3948 | 123.2254 | 123.1567 | -0.3891 | 123.0011 | 122.9462 | 122.8409 | -0.72784
1019.6875 | 123.3902 | -122.818 | 0.59967 | 0.30892 | 0.10377 | -0.0016009 | 0.026945 | -0.015003 | 0.00055539 | 0.022116 | 0.28437 | 0.021425 | 0.0053884 | -0.0037112 | -0.0034972 | 0.027017 | 0.3067 | 0.29755 | 0.25177 | 0.33875 | 0.59509 | 0.32959 | 0.16937 | 0.086975 | -0.23346 | 0.10986 | 0.19684 | 0.13275 | -0.10071 | -0.16022 | 123.1476 | 122.9874 | -0.004577 | 123.1155 | 123.1567 | 0.16937 | -0.29297 | 122.7173 | 122.6578 | -0.40283 | 122.905 | 122.9279 | 0.27008 | -0.46692 | 123.4131 | 123.1247 | 123.0698 | -0.4303 | 123.0148 | 122.9507 | 122.5845 | -0.75989
1020.6875 | 123.4314 | -122.7951 | 0.56763 | -0.31669 | 0.093094 | 0.016557 | 0.023741 | -0.0075262 | -0.0026496 | 0.014639 | -0.31072 | 0.017153 | -0.017042 | -0.0079842 | 0.0050478 | 0.027017 | 0.37994 | 0.41199 | 0.32959 | 0.41657 | 0.58594 | 0.31586 | 0.17395 | 0 | 0.036621 | -0.027466 | 0.16937 | 0.12817 | -0.086975 | -0.16937 | 123.111 | 122.9691 | 0.01831 | 123.2071 | 123.2117 | 0.24262 | -0.18768 | 122.7081 | 122.6257 | -0.39825 | 122.7951 | 122.7676 | 0.14191 | -0.43945 | 123.381 | 123.175 | 123.1247 | -0.39368 | 122.9645 | 122.9233 | 122.8317 | -0.737
1021.6875 | 123.4314 | -122.8134 | 0.56305 | -0.1641 | 0.12941 | -0.0016009 | 0.038694 | -0.0043222 | 0.0037594 | 0.029593 | -0.50908 | 0.013948 | -0.0010206 | -0.0015752 | -0.0034972 | 0.03663 | 0.46692 | 0.3891 | 0.33417 | 0.41657 | 0.63171 | 0.38452 | 0.25177 | 0.009155 | 0.036621 | -0.036621 | 0.17853 | 0.14648 | -0.091553 | -0.16022 | 123.1979 | 123.0652 | 0.068665 | 123.2025 | 123.23 | 0.1648 | -0.09613 | 122.7219 | 122.6532 | -0.38452 | 122.8226 | 122.7768 | 0.1236 | -0.41657 | 123.4451 | 123.2803 | 123.1476 | -0.31128 | 122.9919 | 122.9599 | 122.85 | -0.72327
1022.6875 | 123.3948 | -122.8317 | 0.56305 | -0.01151 | 0.10591 | 0.0026721 | 0.023741 | -0.0011172 | 0.0058954 | 0.030661 | -0.20391 | 0.0075398 | -0.0031566 | 0.0091058 | 0.0082518 | 0.037699 | 0.37079 | 0.37537 | 0.30212 | 0.37079 | 0.59509 | 0.33875 | 0.16479 | -0.022888 | -0.013733 | -0.068665 | 0.16937 | 0.11444 | -0.13275 | -0.16937 | 123.1705 | 122.9965 | 0.032044 | 123.2071 | 123.2025 | 0.20599 | -0.19226 | 122.699 | 122.6624 | -0.39368 | 122.8088 | 122.7631 | 0.10071 | -0.44861 | 123.4268 | 123.2025 | 123.1339 | -0.39825 | 123.0011 | 122.9462 | 122.818 | -0.73242
1023.6875 | 123.4177 | -122.818 | 0.58594 | -0.24039 | 0.084549 | 0.029375 | 0.042967 | -0.012866 | -0.00051261 | 0.008231 | -0.38701 | 0.021425 | -0.0063606 | -0.0015752 | -0.01311 | 0.021677 | 0.32959 | 0.35706 | 0.2655 | 0.37537 | 0.59052 | 0.32044 | 0.16479 | -0.050354 | -0.004578 | -0.064087 | 0.17853 | 0.11902 | -0.13275 | -0.16479 | 123.1384 | 122.9828 | 0.004578 | 123.175 | 123.1934 | 0.21057 | -0.25635 | 122.6852 | 122.6532 | -0.40741 | 122.7676 | 122.7539 | 0.10071 | -0.46692 | 123.4085 | 123.1476 | 123.0835 | -0.42114 | 122.9965 | 122.937 | 122.8134 | -0.75073
1024.6875 | 123.4222 | -122.85 | 0.55389 | -0.087804 | 0.11232 | 0.010148 | 0.024809 | -0.018207 | 0.0016234 | 0.021048 | -0.17339 | 0.010744 | -0.01277 | -0.0069162 | 0.011456 | 0.03129 | 0.38452 | 0.39825 | 0.30212 | 0.39368 | 0.58136 | 0.3067 | 0.16937 | -0.009155 | -0.004578 | -0.050354 | 0.17395 | 0.10986 | -0.10986 | -0.17395 | 123.1567 | 123.0194 | 0.027466 | 123.2483 | 123.2437 | 0.2243 | -0.16937 | 122.7402 | 122.6761 | -0.37994 | 122.8409 | 122.7997 | 0.1236 | -0.44403 | 123.4314 | 123.2346 | 123.1522 | -0.38452 | 123.024 | 122.9599 | 122.8455 | -0.72784
1025.6875 | 123.436 | -122.731 | 0.63171 | -0.65238 | 0.10591 | 0.0037401 | 0.025877 | -0.0075262 | 0.013372 | 0.033866 | -0.34124 | 0.010744 | 0.0021844 | -0.0015752 | 0.010388 | 0.034494 | 0.3891 | 0.40283 | 0.31128 | 0.39825 | 0.58594 | 0.33417 | 0.16479 | 0.009155 | 0.045776 | -0.004578 | 0.16479 | 0.10986 | -0.10529 | -0.16479 | 123.0652 | 122.8958 | -0.045777 | 123.1339 | 123.1293 | 0.23346 | -0.24262 | 122.6257 | 122.5662 | -0.46692 | 122.7402 | 122.7264 | 0.16022 | -0.52185 | 123.317 | 123.1201 | 123.0423 | -0.46692 | 122.8958 | 122.8409 | 122.7768 | -0.79651
1026.6875 | 123.4314 | -122.8226 | 0.54474 | -0.53031 | 0.11873 | -0.0037369 | 0.021604 | -0.0085942 | 0.010168 | 0.018912 | -0.24969 | 0.017153 | 0.015001 | -0.0026432 | -0.0002932 | 0.024881 | 0.39825 | 0.41199 | 0.31128 | 0.39368 | 0.60425 | 0.3479 | 0.20142 | -0.004578 | 0.032043 | -0.036621 | 0.16022 | 0.10529 | -0.1236 | -0.16937 | 123.1705 | 123.024 | 0.059509 | 123.2346 | 123.2162 | 0.19226 | -0.14648 | 122.699 | 122.6532 | -0.38452 | 122.818 | 122.7859 | 0.13275 | -0.43945 | 123.4268 | 123.2208 | 123.1338 | -0.34332 | 122.9828 | 122.9279 | 122.8546 | -0.71411
1027.6875 | 123.4268 | -122.8363 | 0.55389 | -0.10306 | 0.11552 | -0.0016009 | 0.034422 | -0.017139 | 0.0069634 | 0.016776 | -0.26494 | 0.021425 | 0.0043204 | 0.011242 | 0.0050478 | 0.029154 | 0.43488 | 0.42572 | 0.3479 | 0.42114 | 0.64545 | 0.37537 | 0.24261 | 0.004578 | 0.041199 | -0.022888 | 0.16479 | 0.11444 | -0.1236 | -0.16479 | 123.2117 | 123.0789 | 0.091553 | 123.262 | 123.2574 | 0.17853 | -0.11902 | 122.7127 | 122.6715 | -0.3891 | 122.8409 | 122.8134 | 0.14191 | -0.43945 | 123.4818 | 123.2712 | 123.1842 | -0.31128 | 123.0011 | 122.9507 | 122.8775 | -0.71869
1028.6875 | 123.4406 | -122.85 | 0.55389 | -0.30143 | 0.098434 | 0.0080121 | 0.023741 | -0.0032532 | 0.0016234 | 0.017844 | -0.50908 | 0.0021988 | -0.011702 | -0.00050718 | 0.0050478 | 0.033426 | 0.37537 | 0.39368 | 0.30212 | 0.39368 | 0.58136 | 0.31128 | 0.16022 | 0.009155 | 0.045776 | -0.027466 | 0.17395 | 0.11902 | -0.11902 | -0.16937 | 123.1613 | 123.0103 | 0.027466 | 123.2437 | 123.2437 | 0.23346 | -0.17853 | 122.731 | 122.6807 | -0.37994 | 122.8592 | 122.8226 | 0.14191 | -0.43488 | 123.4314 | 123.2254 | 123.1522 | -0.39368 | 123.024 | 122.9691 | 122.8958 | -0.72327
1029.6875 | 123.5184 | -122.7722 | 0.53558 | 0.44625 | 0.123 | -0.0026689 | 0.024809 | -0.029956 | -0.0079896 | 0.021048 | 0.25385 | 0.020357 | -0.0084976 | -0.0026432 | 0.0061158 | 0.032358 | 0.39825 | 0.42572 | 0.35706 | 0.43488 | 0.55389 | 0.3479 | 0.20599 | 0.059509 | 0.073242 | 0.054932 | 0.13275 | 0.091553 | -0.064087 | -0.15106 | 123.1201 | 122.9782 | 0.018311 | 123.1979 | 123.2071 | 0.22888 | -0.13733 | 122.7081 | 122.6212 | -0.40283 | 122.8317 | 122.8271 | 0.20599 | -0.44403 | 123.3261 | 123.1705 | 123.1293 | -0.32959 | 122.905 | 122.8638 | 122.8455 | -0.68665
1030.75 | 123.4497 | -122.8317 | 0.5722 | -0.39298 | 0.10591 | 0.0080121 | 0.029081 | -0.01073 | 0.0016234 | 0.01998 | -0.50908 | 0.020357 | -0.0052926 | 0.0059018 | -0.0024292 | 0.028086 | 0.33875 | 0.35706 | 0.2655 | 0.37079 | 0.58136 | 0.31586 | 0.16479 | -0.045776 | 0.004578 | -0.050354 | 0.18768 | 0.12817 | -0.14191 | -0.17853 | 123.1476 | 122.9965 | 0.009155 | 123.1888 | 123.2025 | 0.20599 | -0.23346 | 122.6898 | 122.6532 | -0.38452 | 122.7859 | 122.7814 | 0.12817 | -0.44403 | 123.4131 | 123.1705 | 123.0972 | -0.40741 | 123.0194 | 122.9599 | 122.8363 | -0.75073
1031.6875 | 123.4451 | -122.8363 | 0.54932 | -0.3472 | 0.11766 | 0.0080121 | 0.042967 | -0.011798 | 0.00055539 | 0.022116 | -0.46331 | 0.0086078 | -0.015974 | 0.0026968 | -0.0034972 | 0.035562 | 0.3479 | 0.37994 | 0.27924 | 0.37994 | 0.5722 | 0.32044 | 0.14191 | -0.009155 | 0.032043 | -0.036621 | 0.16937 | 0.10529 | -0.11444 | -0.1831 | 123.1567 | 122.9782 | 0.022889 | 123.2162 | 123.2162 | 0.23804 | -0.20142 | 122.7219 | 122.6532 | -0.37994 | 122.8271 | 122.7997 | 0.14648 | -0.44403 | 123.4085 | 123.1842 | 123.1155 | -0.40741 | 123.0057 | 122.9416 | 122.8683 | -0.73242
1032.6875 | 123.468 | -122.7676 | 0.62714 | -0.14884 | 0.11446 | 0.0037401 | 0.039762 | -0.028888 | 0.0080314 | 0.022116 | -0.40227 | 0.023562 | -0.0010206 | 0.0091058 | 0.0018428 | 0.03129 | 0.37537 | 0.41657 | 0.31586 | 0.3891 | 0.58136 | 0.31128 | 0.16022 | 0.018311 | 0.050354 | -0.018311 | 0.16022 | 0.13733 | -0.091553 | -0.12817 | 123.0789 | 122.9279 | -0.045776 | 123.1842 | 123.1567 | 0.22888 | -0.25177 | 122.6761 | 122.6395 | -0.46692 | 122.7859 | 122.7493 | 0.10986 | -0.48981 | 123.349 | 123.143 | 123.0835 | -0.46692 | 122.9279 | 122.905 | 122.818 | -0.75531
1033.6875 | 123.4314 | -122.8592 | 0.54016 | -0.20987 | 0.10591 | -0.0016009 | 0.023741 | -0.0096622 | 0.0091004 | 0.025321 | -0.17339 | 0.015017 | -0.0042246 | 0.0048338 | 0.0061158 | 0.019541 | 0.39368 | 0.40283 | 0.3067 | 0.3891 | 0.59052 | 0.32959 | 0.1831 | 0.004578 | 0.018311 | -0.041199 | 0.17395 | 0.13733 | -0.11444 | -0.1831 | 123.1888 | 123.0423 | 0.050354 | 123.262 | 123.2483 | 0.20599 | -0.14648 | 122.7448 | 122.6761 | -0.36621 | 122.8638 | 122.818 | 0.14191 | -0.40283 | 123.4497 | 123.2529 | 123.1659 | -0.35706 | 123.0331 | 122.9965 | 122.8775 | -0.72327
1034.6875 | 123.5229 | -122.8043 | 0.53558 | 0.30892 | 0.099502 | -0.0016009 | 0.030149 | -0.011798 | -0.0079896 | 0.018912 | 0.33015 | 0.017153 | -0.0084976 | -0.0069162 | -0.0056342 | 0.037699 | 0.40741 | 0.45319 | 0.37994 | 0.43488 | 0.54932 | 0.37079 | 0.20142 | 0.073242 | 0.10071 | 0.050354 | 0.14648 | 0.086975 | -0.082397 | -0.13275 | 123.175 | 123.0057 | 0.013733 | 123.2574 | 123.2391 | 0.23346 | -0.12817 | 122.7219 | 122.6715 | -0.3891 | 122.8775 | 122.8546 | 0.18311 | -0.44861 | 123.3536 | 123.2117 | 123.1842 | -0.33417 | 122.9507 | 122.8912 | 122.905 | -0.66833
1035.6875 | 123.4497 | -122.8317 | 0.55389 | -0.30143 | 0.094162 | 0.0080121 | 0.0184 | -0.013935 | 0.0091004 | 0.022116 | -0.18865 | 0.025698 | -0.0063606 | -0.00050718 | 0.0050478 | 0.020609 | 0.37994 | 0.38452 | 0.30212 | 0.39825 | 0.57678 | 0.31128 | 0.15106 | 0.018311 | 0.045776 | -0.027466 | 0.16479 | 0.1236 | -0.10529 | -0.17853 | 123.143 | 122.9828 | 0.022888 | 123.2162 | 123.23 | 0.24719 | -0.17395 | 122.7264 | 122.6532 | -0.3891 | 122.85 | 122.8043 | 0.15106 | -0.4303 | 123.4085 | 123.2117 | 123.1339 | -0.40283 | 122.9965 | 122.9553 | 122.8775 | -0.73242
1036.6875 | 123.436 | -122.8317 | 0.55389 | -0.3472 | 0.097366 | 0.015489 | 0.034422 | 0.0010188 | -0.0026496 | 0.012503 | -0.34124 | 0.013948 | -0.0095656 | -0.0047802 | 0.0082518 | 0.025949 | 0.3479 | 0.40283 | 0.28839 | 0.39368 | 0.58594 | 0.3067 | 0.16022 | -0.013733 | 0.059509 | -0.018311 | 0.16022 | 0.1236 | -0.1236 | -0.17395 | 123.1384 | 122.9919 | 0.032043 | 123.2346 | 123.2254 | 0.23346 | -0.20599 | 122.7081 | 122.6578 | -0.39368 | 122.818 | 122.8134 | 0.15564 | -0.4303 | 123.4177 | 123.1796 | 123.1201 | -0.39368 | 122.9919 | 122.9553 | 122.8912 | -0.72784
1037.6875 | 123.4314 | -122.8455 | 0.56305 | -0.37772 | 0.10271 | 0.0048081 | 0.0087873 | -0.018207 | -0.0026496 | 0.022116 | -0.26494 | 0.016085 | -0.0031566 | -0.0079842 | 0.0018428 | 0.029154 | 0.35248 | 0.39368 | 0.30212 | 0.39825 | 0.57678 | 0.29755 | 0.14191 | 0.018311 | 0.032043 | -0.032043 | 0.16022 | 0.12817 | -0.1236 | -0.17395 | 123.143 | 122.9874 | 0.013733 | 123.2391 | 123.2437 | 0.25635 | -0.21057 | 122.7219 | 122.6715 | -0.40283 | 122.8638 | 122.8134 | 0.14191 | -0.43488 | 123.4222 | 123.1979 | 123.1476 | -0.42114 | 123.0057 | 122.9736 | 122.8775 | -0.737
1038.6875 | 123.3994 | -122.8363 | 0.54932 | 0.034266 | 0.12086 | 0.0069441 | 0.033354 | -0.012866 | -0.0015816 | 0.026389 | -0.26494 | 0.0096758 | -0.010634 | -0.0058482 | 0.0050478 | 0.022745 | 0.35706 | 0.37537 | 0.29297 | 0.36621 | 0.55847 | 0.28839 | 0.16022 | -0.009155 | -0.004578 | -0.054932 | 0.16937 | 0.11902 | -0.12817 | -0.1831 | 123.1247 | 122.9965 | 0.009156 | 123.2117 | 123.2025 | 0.20599 | -0.19226 | 122.7081 | 122.6532 | -0.37994 | 122.8271 | 122.7814 | 0.12817 | -0.4303 | 123.3948 | 123.1934 | 123.1293 | -0.3891 | 123.0057 | 122.9553 | 122.8317 | -0.73242
1039.6875 | 123.5184 | -122.8134 | 0.54474 | 0.41574 | 0.11339 | 0.0080121 | 0.034422 | -0.031024 | -0.011195 | 0.016776 | -0.40227 | 0.0011308 | -0.0063606 | 0.00056082 | -0.0034972 | 0.032358 | 0.40283 | 0.46692 | 0.3891 | 0.44403 | 0.54474 | 0.36621 | 0.19226 | 0.082397 | 0.09613 | 0.064087 | 0.091553 | 0.073242 | -0.10529 | -0.16022 | 123.1796 | 123.0057 | 0 | 123.2803 | 123.2574 | 0.25177 | -0.14191 | 122.7081 | 122.6532 | -0.45319 | 122.8958 | 122.8775 | 0.2243 | -0.4715 | 123.3582 | 123.2162 | 123.2025 | -0.35248 | 122.905 | 122.8867 | 122.9095 | -0.70496
1040.6875 | 123.4451 | -122.8226 | 0.60425 | -0.1641 | 0.10591 | 0.0026721 | 0.024809 | -0.019275 | 0.0037594 | 0.022116 | -0.34124 | 0.0054038 | -0.0042246 | 0.0026968 | -0.0034972 | 0.017404 | 0.40741 | 0.39825 | 0.3067 | 0.39368 | 0.59052 | 0.32501 | 0.16022 | 0 | 0.10071 | -0.022888 | 0.22888 | 0.16022 | -0.064087 | -0.11902 | 123.1476 | 122.9828 | -0.013733 | 123.2208 | 123.2162 | 0.23346 | -0.19684 | 122.7585 | 122.7036 | -0.37537 | 122.8226 | 122.7997 | 0.096131 | -0.44403 | 123.4131 | 123.23 | 123.1293 | -0.44403 | 123.0515 | 122.9828 | 122.9233 | -0.72327
1041.6875 | 123.4222 | -122.8592 | 0.55389 | -0.13358 | 0.11873 | -0.0016009 | 0.021604 | -0.0043222 | 0.016576 | 0.030661 | -0.12761 | 0.017153 | -0.0063606 | -0.0079842 | 0.0029108 | 0.030222 | 0.37537 | 0.37537 | 0.30212 | 0.37537 | 0.56305 | 0.30212 | 0.16479 | -0.018311 | 0.004578 | -0.073242 | 0.16479 | 0.11902 | -0.11444 | -0.20599 | 123.1613 | 123.024 | 0.009155 | 123.2346 | 123.2346 | 0.21057 | -0.17853 | 122.7448 | 122.6532 | -0.3891 | 122.8409 | 122.7859 | 0.13275 | -0.43488 | 123.4222 | 123.2346 | 123.1613 | -0.3891 | 123.024 | 122.9782 | 122.8638 | -0.75989
1042.6875 | 123.3627 | -122.8363 | 0.56763 | 0.095301 | 0.11766 | 0.0016041 | 0.028013 | -0.012866 | 0.0058954 | 0.022116 | -0.11236 | 0.022493 | 4.7432e-05 | 0.01231 | 0.0071838 | 0.034494 | 0.32044 | 0.31128 | 0.26093 | 0.34332 | 0.56305 | 0.30212 | 0.16479 | -0.032043 | -0.07782 | -0.11902 | 0.17395 | 0.1236 | -0.13275 | -0.17395 | 123.1384 | 123.0011 | -0.004578 | 123.1476 | 123.1796 | 0.17853 | -0.24719 | 122.7036 | 122.6624 | -0.39368 | 122.8043 | 122.7173 | 0.054931 | -0.44403 | 123.3994 | 123.1567 | 123.0972 | -0.40283 | 123.0103 | 122.9599 | 122.7585 | -0.74158
1043.6875 | 123.4406 | -122.8546 | 0.54932 | -0.40824 | 0.12407 | 0.017625 | 0.022672 | -4.9167e-05 | -0.0047856 | 0.016776 | -0.50908 | 0.013948 | 4.7432e-05 | 0.0037648 | -0.0034972 | 0.025949 | 0.3479 | 0.36621 | 0.27924 | 0.37537 | 0.58594 | 0.29755 | 0.15106 | -0.009155 | 0.036621 | -0.032043 | 0.17395 | 0.1236 | -0.1236 | -0.19684 | 123.1522 | 123.0057 | 0.036621 | 123.2208 | 123.23 | 0.2243 | -0.20142 | 122.731 | 122.6578 | -0.37537 | 122.8455 | 122.8226 | 0.1648 | -0.42572 | 123.4406 | 123.2025 | 123.1338 | -0.39825 | 123.0286 | 122.9782 | 122.8912 | -0.74615
1044.6875 | 123.5321 | -122.8271 | 0.50812 | 0.53781 | 0.10057 | 0.00053514 | 0.019468 | 0.0042228 | -0.0090576 | 0.012503 | 0.34541 | 0.010744 | -0.0095656 | 0.00056082 | -0.0056342 | 0.032358 | 0.41199 | 0.46692 | 0.39368 | 0.43945 | 0.54932 | 0.35248 | 0.20142 | 0.086975 | 0.12817 | 0.050354 | 0.10529 | 0.032043 | -0.13733 | -0.16022 | 123.1796 | 123.0286 | 0.041198 | 123.2941 | 123.2666 | 0.23804 | -0.096131 | 122.6898 | 122.6669 | -0.40283 | 122.9141 | 122.8775 | 0.21057 | -0.47607 | 123.3765 | 123.2391 | 123.2208 | -0.3067 | 122.9324 | 122.8592 | 122.9553 | -0.66833
1045.6875 | 123.4314 | -122.8683 | 0.54932 | -0.057287 | 0.11125 | 0.0037401 | 0.013059 | -0.016071 | 0.019781 | 0.027457 | -0.15813 | 0.0032668 | -0.0020886 | 0.00056082 | 0.0018428 | 0.020609 | 0.40741 | 0.38452 | 0.29755 | 0.37537 | 0.56763 | 0.32044 | 0.15564 | 0 | 0.013733 | -0.054932 | 0.16479 | 0.1236 | -0.10986 | -0.17853 | 123.1888 | 123.024 | 0.018311 | 123.2529 | 123.2437 | 0.21973 | -0.14191 | 122.7585 | 122.6898 | -0.38452 | 122.8683 | 122.8134 | 0.1236 | -0.42572 | 123.436 | 123.2758 | 123.1659 | -0.39368 | 123.0331 | 122.9919 | 122.8821 | -0.72784
1046.7031 | 123.5321 | -122.7859 | 0.54474 | 0.0037495 | 0.069595 | -0.20988 | 0.011991 | -0.020343 | -0.045374 | 0.00289 | -0.036062 | 0.0064718 | -0.026655 | -0.0015752 | -0.0077702 | 0.045175 | 0.37537 | 0.45776 | 0.36163 | 0.43488 | 0.55389 | 0.35248 | 0.20142 | 0.054932 | 0.10529 | 0.082397 | 0.14648 | 0.10529 | -0.054932 | -0.1236 | 123.1384 | 122.9874 | 0.009155 | 123.2437 | 123.2208 | 0.23346 | -0.16937 | 122.731 | 122.6624 | -0.39825 | 122.8409 | 122.8683 | 0.20599 | -0.43945 | 123.3398 | 123.1613 | 123.1476 | -0.34332 | 122.9324 | 122.8912 | 122.8912 | -0.66834
1047.6875 | 123.4314 | -122.8546 | 0.55389 | -0.28617 | 0.12834 | 0.0048081 | 0.019468 | -0.019275 | 0.015508 | 0.014639 | -0.21917 | 0.013948 | -0.017042 | -0.014393 | 0.012524 | 0.027017 | 0.41199 | 0.39368 | 0.29755 | 0.3891 | 0.58136 | 0.3067 | 0.1831 | -0.022888 | 0.013733 | -0.041199 | 0.15106 | 0.10529 | -0.13275 | -0.1831 | 123.1613 | 123.0377 | 0.027466 | 123.2483 | 123.2437 | 0.20599 | -0.14191 | 122.7219 | 122.6715 | -0.40283 | 122.8317 | 122.8134 | 0.14191 | -0.44861 | 123.436 | 123.2666 | 123.1522 | -0.37079 | 123.0057 | 122.9599 | 122.8683 | -0.737
1048.6875 | 123.3902 | -122.85 | 0.55847 | 0.034266 | 0.11766 | 0.0058761 | 0.017332 | -0.018207 | 0.011236 | 0.026389 | -0.23443 | 0.0043348 | -0.0095656 | 0.0048338 | 0.0082518 | 0.025949 | 0.35248 | 0.34332 | 0.25635 | 0.34332 | 0.55389 | 0.3067 | 0.15106 | -0.041199 | -0.032043 | -0.091553 | 0.15106 | 0.10986 | -0.11444 | -0.19226 | 123.1567 | 123.0011 | -0.004578 | 123.1934 | 123.1934 | 0.19226 | -0.20599 | 122.7356 | 122.6578 | -0.40741 | 122.8088 | 122.7585 | 0.10071 | -0.44861 | 123.4039 | 123.2025 | 123.1064 | -0.40741 | 123.0011 | 122.9599 | 122.818 | -0.75073
1049.6875 | 123.5046 | -122.7951 | 0.53101 | 0.44625 | 0.11766 | 0.0016041 | 0.015196 | -0.015003 | -0.024012 | 0.014639 | 0.33015 | 0.0064718 | -0.010634 | -0.01012 | -0.0088382 | 0.037699 | 0.41657 | 0.46692 | 0.39825 | 0.42114 | 0.53101 | 0.3479 | 0.18768 | 0.10071 | 0.082397 | 0.059509 | 0.14648 | 0.09613 | -0.10071 | -0.14191 | 123.143 | 122.9828 | 0 | 123.262 | 123.2162 | 0.23346 | -0.11444 | 122.6944 | 122.6532 | -0.38452 | 122.8958 | 122.8546 | 0.20142 | -0.43488 | 123.3261 | 123.2117 | 123.1934 | -0.34332 | 122.9416 | 122.8912 | 122.8775 | -0.67291
1050.6875 | 123.5001 | -122.8455 | 0.58136 | 0.67514 | 0.10805 | 0.0069441 | 0.020536 | -0.020343 | 0.0058954 | 0.022116 | -0.05132 | 0.019289 | 0.0085924 | 0.0016288 | 0.0018428 | 0.025949 | 0.32959 | 0.27466 | 0.23346 | 0.32959 | 0.56763 | 0.32959 | 0.15106 | -0.032043 | -0.064087 | -0.09613 | 0.16937 | 0.1236 | -0.11444 | -0.17395 | 123.175 | 122.9965 | -0.013733 | 123.1201 | 123.175 | 0.17853 | -0.25177 | 122.731 | 122.6715 | -0.41199 | 122.8134 | 122.7493 | 0.07782 | -0.45776 | 123.4131 | 123.175 | 123.0789 | -0.4303 | 123.0148 | 122.9691 | 122.7814 | -0.75531
1051.7031 | 123.5046 | -122.8043 | 0.52185 | -0.48453 | 0.072799 | 0.010148 | 0.026945 | -0.016071 | -0.029353 | 0.032797 | -0.26494 | -0.0052782 | -0.014906 | 0.00056082 | -0.0067022 | 0.024881 | 0.21515 | 0.55389 | 0.3891 | 0.41657 | 0.52185 | 0.32501 | 0.16937 | 0.082397 | 0.14648 | 0.073242 | 0.13733 | 0.086975 | -0.086975 | -0.13275 | 123.1293 | 122.9736 | 0 | 123.3582 | 123.2208 | 0.24719 | -0.3067 | 122.7173 | 122.6715 | -0.38452 | 122.8867 | 122.8775 | 0.20599 | -0.43488 | 123.3261 | 123.0194 | 123.1934 | -0.35248 | 122.9416 | 122.8912 | 122.9507 | -0.6546
1052.6875 | 123.3902 | -122.8775 | 0.56305 | 0.12582 | 0.11766 | -0.0069409 | 0.024809 | -0.018207 | 0.010168 | 0.026389 | -0.11236 | 0.010744 | -0.0031566 | -0.01012 | 0.012524 | 0.025949 | 0.32044 | 0.30212 | 0.2243 | 0.35248 | 0.57678 | 0.28381 | 0.17853 | -0.045776 | -0.064087 | -0.10071 | 0.16937 | 0.12817 | -0.11902 | -0.18768 | 123.1613 | 123.056 | 0.013733 | 123.1796 | 123.23 | 0.17395 | -0.24261 | 122.7585 | 122.6898 | -0.39368 | 122.8317 | 122.7768 | 0.086975 | -0.43488 | 123.4543 | 123.1979 | 123.1018 | -0.38452 | 123.0469 | 123.0057 | 122.8134 | -0.75073
1053.6875 | 123.4222 | -122.85 | 0.56305 | 0.32418 | 0.10698 | 0.0058761 | 0.0184 | -0.026752 | -0.00051261 | 0.024253 | 0.11653 | 0.020357 | -0.0020886 | -0.0079842 | 0.0018428 | 0.028086 | 0.32959 | 0.31128 | 0.25177 | 0.3479 | 0.5722 | 0.30212 | 0.16937 | -0.036621 | -0.045776 | -0.059509 | 0.16937 | 0.13275 | -0.10529 | -0.18768 | 123.1522 | 123.0194 | 0.009156 | 123.1613 | 123.1979 | 0.17853 | -0.23346 | 122.7448 | 122.6624 | -0.39368 | 122.8134 | 122.7905 | 0.12817 | -0.4303 | 123.4222 | 123.1796 | 123.1018 | -0.39368 | 123.0194 | 122.9828 | 122.8043 | -0.75073
1054.6875 | 123.5138 | -122.8546 | 0.54932 | 0.15634 | 0.093094 | 0.0069441 | 0.025877 | -0.020343 | -0.032557 | -0.001382 | 0.086009 | 0.0032668 | -0.018111 | -0.0037112 | -0.015247 | 0.032358 | 0.32959 | 0.39825 | 0.33875 | 0.40741 | 0.55847 | 0.33417 | 0.16937 | 0.036621 | 0.064087 | 0.041199 | 0.13733 | 0.10529 | -0.086975 | -0.15106 | 123.1888 | 123.024 | 0.009156 | 123.2529 | 123.262 | 0.23804 | -0.21973 | 122.7676 | 122.7036 | -0.41199 | 122.8912 | 122.8958 | 0.19226 | -0.44403 | 123.4131 | 123.1842 | 123.1934 | -0.37994 | 122.9919 | 122.9599 | 122.9187 | -0.70038
1055.6875 | 123.4818 | -122.8271 | 0.53101 | 0.36996 | 0.10911 | 0.0069441 | 0.025877 | -0.020343 | 0.012304 | 0.023184 | 0.19282 | 0.0054038 | -0.0010206 | -0.0047802 | 0.0071838 | 0.027017 | 0.37994 | 0.34332 | 0.27008 | 0.37079 | 0.5722 | 0.32044 | 0.18768 | 0.041199 | 0 | -0.022888 | 0.16937 | 0.09613 | -0.10986 | -0.16022 | 123.1476 | 123.0148 | 0.041199 | 123.1705 | 123.1979 | 0.18311 | -0.15106 | 122.7173 | 122.6669 | -0.36163 | 122.8683 | 122.8043 | 0.13733 | -0.43488 | 123.3994 | 123.2071 | 123.0972 | -0.34332 | 122.9965 | 122.9233 | 122.8271 | -0.69122
1056.7031 | 123.4863 | -122.8134 | 0.52643 | 0.034266 | 0.074936 | 0.024034 | 0.010923 | -0.012866 | -0.037898 | 0.012503 | -0.020803 | 6.2833e-05 | -0.019179 | 0.0016288 | -0.0034972 | 0.032358 | 0.35706 | 0.40283 | 0.33417 | 0.39368 | 0.55389 | 0.32044 | 0.17395 | 0.041199 | 0.073242 | 0.036621 | 0.15106 | 0.09613 | -0.09613 | -0.14648 | 123.1339 | 122.9874 | 0.027466 | 123.2162 | 123.2071 | 0.21973 | -0.16937 | 122.7173 | 122.6669 | -0.37537 | 122.8546 | 122.85 | 0.18311 | -0.4303 | 123.3673 | 123.1705 | 123.1476 | -0.35248 | 122.9645 | 122.9095 | 122.8867 | -0.67291
1057.6875 | 123.3948 | -122.8638 | 0.58136 | 0.15634 | 0.11873 | 0.0048081 | 0.017332 | -0.012866 | 0.013372 | 0.017844 | -0.23443 | 0.0064718 | -0.0084976 | 0.0026968 | 0.011456 | 0.027017 | 0.37994 | 0.32959 | 0.2655 | 0.35248 | 0.5722 | 0.31586 | 0.16937 | -0.032043 | -0.027466 | -0.091553 | 0.18768 | 0.12817 | -0.11902 | -0.19226 | 123.1796 | 123.0331 | -0.009155 | 123.1934 | 123.2162 | 0.18311 | -0.20142 | 122.7448 | 122.6715 | -0.39368 | 122.8317 | 122.7722 | 0.10071 | -0.45319 | 123.436 | 123.2437 | 123.1293 | -0.41199 | 123.0515 | 122.9919 | 122.8363 | -0.77362
1058.6875 | 123.4039 | -122.8729 | 0.57678 | 0.080043 | 0.11446 | 0.015489 | 0.0087873 | -0.0096622 | 0.022985 | 0.024253 | -0.12761 | 0.019289 | 0.0032524 | 0.0091058 | 0.0050478 | 0.020609 | 0.36621 | 0.35248 | 0.27008 | 0.36621 | 0.56763 | 0.29297 | 0.14191 | -0.022888 | -0.041199 | -0.091553 | 0.16937 | 0.12817 | -0.11902 | -0.1831 | 123.1659 | 123.0148 | -0.009155 | 123.2254 | 123.2391 | 0.2243 | -0.21057 | 122.7539 | 122.6898 | -0.40741 | 122.85 | 122.7814 | 0.091552 | -0.44861 | 123.4406 | 123.2391 | 123.143 | -0.43488 | 123.0423 | 123.0011 | 122.8317 | -0.75989
1059.6875 | 123.5046 | -122.8226 | 0.53101 | 0.38522 | 0.099502 | 0.0026721 | 0.015196 | -0.015003 | 0.013372 | 0.022116 | 0.28437 | 0.017153 | -0.023451 | 0.0069698 | -0.0002932 | 0.034494 | 0.37537 | 0.37994 | 0.32044 | 0.3891 | 0.54932 | 0.33417 | 0.18768 | 0.073242 | 0.082397 | 0.036621 | 0.15106 | 0.09613 | -0.07782 | -0.13733 | 123.1567 | 123.0103 | 0.01831 | 123.2025 | 123.2117 | 0.20142 | -0.15564 | 122.7448 | 122.6852 | -0.37994 | 122.8958 | 122.8592 | 0.17395 | -0.43488 | 123.3719 | 123.1979 | 123.143 | -0.34332 | 122.9736 | 122.9187 | 122.905 | -0.66834
1060.6875 | 123.4222 | -122.8683 | 0.56305 | -0.01151 | 0.11018 | -0.0069409 | 0.022672 | -0.012866 | 0.01444 | 0.029593 | -0.23443 | 0.0075398 | -0.0010206 | 0.0016288 | 0.0093198 | 0.035562 | 0.37994 | 0.36163 | 0.27008 | 0.37994 | 0.56305 | 0.29755 | 0.15106 | 0.009155 | 0.004578 | -0.07782 | 0.1831 | 0.14648 | -0.11902 | -0.17853 | 123.1659 | 123.0194 | 0 | 123.23 | 123.2483 | 0.22888 | -0.18311 | 122.7493 | 122.6898 | -0.37994 | 122.8775 | 122.7905 | 0.10071 | -0.41657 | 123.4314 | 123.2483 | 123.1384 | -0.41199 | 123.0515 | 123.0148 | 122.8729 | -0.74158
1061.7031 | 123.5229 | -122.8043 | 0.52185 | 0.33944 | 0.089889 | 0.0069441 | 0.0087873 | -0.0085942 | -0.012263 | 0.017844 | 0.29963 | 0.0064718 | -0.015974 | -0.0069162 | 0.0007748 | 0.03663 | 0.40283 | 0.46234 | 0.37994 | 0.42114 | 0.52185 | 0.34332 | 0.19684 | 0.086975 | 0.10071 | 0.059509 | 0.15106 | 0.073242 | -0.086975 | -0.14648 | 123.1476 | 123.0011 | 0 | 123.2666 | 123.2254 | 0.2243 | -0.11902 | 122.7173 | 122.6578 | -0.37079 | 122.8912 | 122.8638 | 0.20599 | -0.44861 | 123.3261 | 123.2071 | 123.1842 | -0.32501 | 122.9553 | 122.8775 | 122.905 | -0.66833
1062.6875 | 123.4131 | -122.8592 | 0.55389 | 0.21737 | 0.10698 | -0.00053286 | 0.025877 | -0.011798 | 0.0080314 | 0.023184 | 0.1623 | 0.018221 | -0.0020886 | 0.0026968 | 0.0018428 | 0.023813 | 0.33875 | 0.30212 | 0.23346 | 0.35248 | 0.5722 | 0.3067 | 0.16937 | 0 | -0.036621 | -0.086975 | 0.17853 | 0.12817 | -0.10071 | -0.1831 | 123.1659 | 123.0286 | 0.018311 | 123.1613 | 123.2117 | 0.18311 | -0.21515 | 122.7585 | 122.6761 | -0.37537 | 122.8592 | 122.7722 | 0.09613 | -0.42572 | 123.4314 | 123.1979 | 123.0927 | -0.38452 | 123.0377 | 122.9874 | 122.8226 | -0.737
1063.6875 | 123.4085 | -122.8592 | 0.55847 | -0.072545 | 0.12941 | 0.0080121 | 0.023741 | -0.016071 | 0.011236 | 0.024253 | -0.24969 | 0.0075398 | -0.017042 | -0.0015752 | 0.0007748 | 0.020609 | 0.40741 | 0.36163 | 0.27466 | 0.37537 | 0.55847 | 0.32044 | 0.15106 | 0 | 0.013733 | -0.045776 | 0.17395 | 0.13275 | -0.09613 | -0.16937 | 123.1796 | 123.0103 | 0 | 123.2208 | 123.2346 | 0.2243 | -0.15106 | 122.7631 | 122.6898 | -0.38452 | 122.8592 | 122.8134 | 0.1236 | -0.42572 | 123.4177 | 123.2666 | 123.1338 | -0.40741 | 123.0331 | 122.9919 | 122.8729 | -0.72784
1064.6875 | 123.4131 | -122.8638 | 0.55389 | 0.12582 | 0.1262 | 0.0080121 | 0.031217 | -0.024616 | -0.0015816 | 0.024253 | 0.14704 | 0.023562 | -0.0074286 | -0.0026432 | -0.0002932 | 0.033426 | 0.33875 | 0.29297 | 0.23346 | 0.33417 | 0.57678 | 0.30212 | 0.15106 | -0.027466 | -0.045776 | -0.082397 | 0.17395 | 0.13733 | -0.10529 | -0.18768 | 123.1659 | 123.0148 | 0.022888 | 123.1567 | 123.1979 | 0.1831 | -0.21515 | 122.7585 | 122.6761 | -0.37994 | 122.8363 | 122.7814 | 0.10529 | -0.41656 | 123.4406 | 123.2025 | 123.0972 | -0.40283 | 123.0377 | 123.0011 | 122.818 | -0.74158
1065.6875 | 123.4085 | -122.8546 | 0.54474 | 0.11056 | 0.11232 | 0.0048081 | 0.030149 | -0.012866 | 0.011236 | 0.023184 | -0.081838 | 0.018221 | 0.0075244 | 0.0048338 | 0.0082518 | 0.028086 | 0.35706 | 0.33875 | 0.27466 | 0.36621 | 0.54932 | 0.3067 | 0.14648 | -0.036621 | -0.013733 | -0.07782 | 0.17395 | 0.13275 | -0.1236 | -0.1831 | 123.1613 | 123.0011 | 0.004577 | 123.1934 | 123.2208 | 0.21973 | -0.18768 | 122.731 | 122.6715 | -0.37079 | 122.818 | 122.7768 | 0.10528 | -0.41199 | 123.4039 | 123.2117 | 123.1293 | -0.39825 | 123.0286 | 122.9874 | 122.8409 | -0.72784
1066.7031 | 123.4955 | -122.8043 | 0.52185 | 0.3547 | 0.10271 | -0.0016009 | 0.03549 | -0.011798 | -0.022944 | 0.018912 | 0.28437 | 0.0064718 | -0.013838 | 0.0059018 | -0.0024292 | 0.025949 | 0.40741 | 0.44861 | 0.37537 | 0.42114 | 0.50812 | 0.3479 | 0.20142 | 0.073242 | 0.10071 | 0.059509 | 0.13733 | 0.086975 | -0.086975 | -0.14191 | 123.1522 | 123.0057 | -0.013733 | 123.2529 | 123.2254 | 0.21973 | -0.11444 | 122.7173 | 122.6624 | -0.38452 | 122.8775 | 122.8638 | 0.20142 | -0.43488 | 123.3124 | 123.2117 | 123.1796 | -0.32043 | 122.9416 | 122.8912 | 122.905 | -0.66376
1067.6875 | 123.5596 | -122.8455 | 0.52185 | 0.38522 | 0.11018 | 0.0080121 | 0.030149 | -0.012866 | 0.0069634 | 0.022116 | 0.29963 | 0.013948 | -0.011702 | -0.00050718 | -0.0013612 | 0.023813 | 0.37079 | 0.34332 | 0.58136 | 0.92926 | 0.55389 | 0.31128 | 0.16022 | 0.054932 | 0.050354 | 0.054932 | 0.15106 | 0.10071 | -0.09613 | -0.13275 | 123.1567 | 123.0057 | 0.032043 | 123.1888 | 123.7747 | 0.76904 | -0.15106 | 122.7493 | 122.7127 | -0.37079 | 122.9004 | 122.9004 | 0.18768 | -0.42114 | 123.3994 | 123.2162 | 123.4268 | -0.36163 | 122.9965 | 122.9462 | 122.8958 | -0.6546
1068.6875 | 123.4497 | -122.85 | 0.54016 | 0.034266 | 0.11018 | 0.0080121 | 0.022672 | -0.020343 | 0.013372 | 0.017844 | -0.18865 | 0.01288 | 0.0096604 | 0.0091058 | 0.0050478 | 0.022745 | 0.37994 | 0.39368 | 0.29297 | 0.50354 | 0.55847 | 0.27924 | 0.15564 | 0.054932 | 0.10071 | -0.045776 | 0.1831 | 0.13275 | -0.1236 | -0.19226 | 123.1293 | 123.0057 | 0.018311 | 123.2437 | 123.3536 | 0.3479 | -0.16022 | 122.7264 | 122.6578 | -0.35706 | 122.905 | 122.8043 | 0.14648 | -0.40741 | 123.4085 | 123.23 | 123.143 | -0.38452 | 123.0331 | 122.9828 | 122.9507 | -0.73242
1069.6875 | 123.3902 | -122.8638 | 0.54932 | 0.080043 | 0.11339 | -0.0037369 | 0.030149 | -0.019275 | 0.0037594 | 0.01998 | -0.17339 | 0.021425 | -0.0031566 | 0.0026968 | 0.013592 | 0.027017 | 0.34332 | 0.31586 | 0.25177 | 0.36163 | 0.58136 | 0.3067 | 0.14191 | -0.050354 | -0.054932 | -0.09613 | 0.1831 | 0.13275 | -0.13275 | -0.16937 | 123.1705 | 123.0057 | 0.032044 | 123.1796 | 123.2254 | 0.21973 | -0.20599 | 122.731 | 122.6944 | -0.36621 | 122.8134 | 122.7676 | 0.073243 | -0.41657 | 123.4451 | 123.2071 | 123.1155 | -0.40741 | 123.0469 | 122.9965 | 122.8088 | -0.71869
1070.6875 | 123.4406 | -122.8683 | 0.55847 | -0.042028 | 0.10271 | 0.0037401 | 0.034422 | -0.024616 | 0.0048274 | 0.025321 | -0.21917 | 0.016085 | -0.0063606 | -0.0015752 | 0.0007748 | 0.022745 | 0.40283 | 0.38452 | 0.29297 | 0.37994 | 0.54932 | 0.3067 | 0.14191 | 0 | 0.027466 | -0.045776 | 0.16479 | 0.13275 | -0.10986 | -0.17395 | 123.175 | 123.0103 | -0.009156 | 123.2529 | 123.2483 | 0.23804 | -0.15564 | 122.7585 | 122.6944 | -0.39368 | 122.8683 | 122.8226 | 0.12817 | -0.42572 | 123.4177 | 123.2712 | 123.1613 | -0.41656 | 123.0331 | 123.0011 | 122.8958 | -0.73242
1071.6875 | 123.4589 | -122.8317 | 0.55389 | -0.11832 | 0.1262 | 0.010148 | 0.031217 | -0.019275 | 0.0048274 | 0.017844 | -0.24969 | 0.018221 | 0.0085924 | -0.0037112 | 0.0061158 | 0.018473 | 0.3891 | 0.38452 | 0.28381 | 0.37994 | 0.5722 | 0.30212 | 0.15106 | 0.018311 | 0.027466 | -0.027466 | 0.16022 | 0.1236 | -0.10529 | -0.16022 | 123.1339 | 122.9828 | 0.018311 | 123.2162 | 123.2117 | 0.22888 | -0.1648 | 122.7264 | 122.6715 | -0.39368 | 122.85 | 122.8043 | 0.13275 | -0.4303 | 123.4039 | 123.2208 | 123.1155 | -0.40283 | 122.9919 | 122.9553 | 122.8592 | -0.71411
1072.6875 | 123.4222 | -122.8683 | 0.54474 | -0.026769 | 0.11446 | 0.011217 | 0.026945 | -0.021411 | -0.0047856 | 0.024253 | -0.066579 | 0.0064718 | -0.0084976 | 0.0048338 | -0.0045652 | 0.018473 | 0.35706 | 0.3479 | 0.27008 | 0.35706 | 0.58136 | 0.29297 | 0.16937 | -0.027466 | 0.009155 | -0.068665 | 0.17853 | 0.13733 | -0.11902 | -0.17853 | 123.1613 | 123.0377 | 0.036621 | 123.2162 | 123.2254 | 0.18768 | -0.18768 | 122.7493 | 122.6898 | -0.36621 | 122.8409 | 122.7997 | 0.10986 | -0.40741 | 123.4497 | 123.2254 | 123.1384 | -0.37537 | 123.0469 | 123.0057 | 122.8775 | -0.72327
1073.6875 | 123.4085 | -122.8821 | 0.55389 | -0.01151 | 0.10164 | 0.011217 | 0.036558 | -0.025684 | 0.016576 | 0.018912 | -0.081838 | 0.0096758 | -0.015974 | 0.020855 | 0.0071838 | 0.027017 | 0.36621 | 0.35706 | 0.27924 | 0.35248 | 0.5722 | 0.3067 | 0.14648 | -0.018311 | 0.027466 | -0.050354 | 0.16022 | 0.11444 | -0.10986 | -0.17853 | 123.1888 | 123.0286 | 0.018311 | 123.2391 | 123.2346 | 0.20599 | -0.18768 | 122.7722 | 122.7036 | -0.39368 | 122.8638 | 122.8317 | 0.12817 | -0.43945 | 123.4543 | 123.2483 | 123.1613 | -0.40741 | 123.0423 | 122.9965 | 122.9095 | -0.73242
1074.6875 | 123.4543 | -122.8592 | 0.54474 | -0.026769 | 0.11232 | 0.0026721 | 0.019468 | -0.032093 | 0.0037594 | 0.022116 | -0.21917 | 0.013948 | -0.0084976 | 0.0048338 | 0.010388 | 0.025949 | 0.35706 | 0.37079 | 0.28839 | 0.37079 | 0.54932 | 0.28381 | 0.15106 | -0.004578 | 0.018311 | -0.045776 | 0.17395 | 0.11902 | -0.10986 | -0.16937 | 123.143 | 123.0103 | 0.004577 | 123.23 | 123.23 | 0.21973 | -0.18768 | 122.7493 | 122.6898 | -0.37079 | 122.8546 | 122.8134 | 0.1236 | -0.42572 | 123.4085 | 123.2162 | 123.1476 | -0.39368 | 123.0331 | 122.9782 | 122.8775 | -0.71411
1075.6875 | 123.4314 | -122.8729 | 0.53558 | -0.042028 | 0.10377 | 0.0026721 | 0.029081 | -0.011798 | 0.0048274 | 0.012503 | -0.18865 | 0.018221 | -0.01277 | 0.0016288 | 0.0050478 | 0.030222 | 0.38452 | 0.39825 | 0.30212 | 0.38452 | 0.54474 | 0.30212 | 0.15564 | 0.009155 | 0.041199 | -0.032043 | 0.17853 | 0.13733 | -0.11444 | -0.16022 | 123.175 | 123.0286 | 0.009156 | 123.2712 | 123.2574 | 0.22888 | -0.15106 | 122.7585 | 122.7127 | -0.35706 | 122.8821 | 122.8409 | 0.12817 | -0.39825 | 123.4177 | 123.2574 | 123.175 | -0.37994 | 123.0515 | 123.0103 | 122.9141 | -0.6958
1076.6875 | 123.4589 | -122.8821 | 0.53558 | -0.20987 | 0.10271 | 0.0069441 | 0.028013 | -0.019275 | -0.0047856 | 0.016776 | -0.21917 | 0.022493 | -0.0063606 | 0.0037648 | 0.010388 | 0.024881 | 0.37079 | 0.3891 | 0.29297 | 0.38452 | 0.55847 | 0.31128 | 0.16022 | 0.022888 | 0.041199 | -0.027466 | 0.1831 | 0.11444 | -0.091553 | -0.17395 | 123.1934 | 123.0423 | 0.022889 | 123.2712 | 123.2666 | 0.2243 | -0.16479 | 122.7905 | 122.7081 | -0.35248 | 122.905 | 122.8546 | 0.14648 | -0.42114 | 123.4406 | 123.2529 | 123.175 | -0.37537 | 123.0652 | 122.9965 | 122.9233 | -0.70953
1077.6875 | 123.4451 | -122.8729 | 0.52185 | -0.13358 | 0.10057 | 0.0048081 | 0.020536 | -0.022479 | 0.0069634 | 0.026389 | -0.26494 | 0.011812 | -0.010634 | -0.0058482 | 0.0029108 | 0.034494 | 0.37537 | 0.39368 | 0.29297 | 0.3891 | 0.56305 | 0.29755 | 0.14191 | 0.018311 | 0.050354 | -0.022888 | 0.16479 | 0.13733 | -0.10986 | -0.15564 | 123.1705 | 123.0148 | 0.041198 | 123.2666 | 123.262 | 0.24719 | -0.14648 | 122.7631 | 122.7173 | -0.35706 | 122.8912 | 122.85 | 0.13275 | -0.38452 | 123.436 | 123.2483 | 123.1659 | -0.37994 | 123.0377 | 123.0103 | 122.9233 | -0.67749
1078.6875 | 123.4589 | -122.8867 | 0.54016 | -0.25565 | 0.098434 | 0.013353 | 0.031217 | -0.011798 | -0.0047856 | 0.014639 | -0.2802 | 0.021425 | -0.0020886 | 0.0037648 | -0.0013612 | 0.020609 | 0.36621 | 0.39368 | 0.29755 | 0.37537 | 0.55847 | 0.28381 | 0.14191 | 0.009155 | 0.045776 | -0.013733 | 0.17395 | 0.13733 | -0.09613 | -0.17853 | 123.1705 | 123.0286 | 0.018311 | 123.2803 | 123.262 | 0.23346 | -0.17395 | 122.7905 | 122.7081 | -0.36621 | 122.8958 | 122.8729 | 0.16479 | -0.40283 | 123.4451 | 123.2529 | 123.1842 | -0.39825 | 123.0606 | 123.024 | 122.9324 | -0.71869
1079.6875 | 123.4222 | -122.8638 | 0.54474 | -0.087804 | 0.1198 | 0.0037401 | 0.024809 | -0.029956 | 0.00055539 | 0.017844 | -0.15813 | 0.021425 | 0.011797 | 0.0069698 | 0.015729 | 0.023813 | 0.37537 | 0.37079 | 0.29755 | 0.35706 | 0.5722 | 0.32044 | 0.1236 | -0.013733 | 0.027466 | -0.036621 | 0.16937 | 0.11902 | -0.11902 | -0.17395 | 123.1842 | 122.9874 | 0.027466 | 123.2346 | 123.2208 | 0.23346 | -0.16937 | 122.7448 | 122.6898 | -0.37537 | 122.85 | 122.8271 | 0.13733 | -0.42572 | 123.436 | 123.2391 | 123.1613 | -0.42114 | 123.0331 | 122.9828 | 122.8912 | -0.71869
1080.6875 | 123.4451 | -122.8546 | 0.54016 | -0.1641 | 0.11446 | 0.0026721 | 0.031217 | -0.0085942 | 0.0069634 | 0.027457 | -0.21917 | 0.020357 | -0.0052926 | 0.0016288 | 0.0093198 | 0.025949 | 0.37994 | 0.37994 | 0.28381 | 0.37994 | 0.55847 | 0.3067 | 0.15106 | 0.009155 | 0.032043 | -0.032043 | 0.16479 | 0.10986 | -0.10071 | -0.17395 | 123.1613 | 123.0057 | 0.018311 | 123.2346 | 123.2346 | 0.22888 | -0.16022 | 122.7539 | 122.6807 | -0.37537 | 122.8638 | 122.8226 | 0.14191 | -0.4303 | 123.4131 | 123.2346 | 123.1384 | -0.3891 | 123.0194 | 122.9645 | 122.8867 | -0.71411
1081.6875 | 123.4177 | -122.8821 | 0.54474 | 0.034266 | 0.094162 | 0.013353 | 0.033354 | -0.021411 | 0.0048274 | 0.023184 | -0.11236 | 0.010744 | -0.0010206 | 0.0048338 | 0.0007748 | 0.023813 | 0.33875 | 0.35706 | 0.25177 | 0.36621 | 0.54932 | 0.30212 | 0.13733 | -0.018311 | -0.004578 | -0.064087 | 0.17395 | 0.12817 | -0.11902 | -0.17853 | 123.1842 | 123.0194 | 0.004577 | 123.2391 | 123.2483 | 0.22888 | -0.20599 | 122.7631 | 122.7036 | -0.37079 | 122.8638 | 122.818 | 0.11444 | -0.41656 | 123.4314 | 123.2208 | 123.1338 | -0.40741 | 123.056 | 123.0103 | 122.8775 | -0.72327
1082.6875 | 123.4039 | -122.8821 | 0.55389 | 0.049525 | 0.10271 | 0.0058761 | 0.025877 | -0.012866 | 0.0080314 | 0.01998 | -0.081838 | 0.019289 | 0.0085924 | 0.0048338 | 0.0071838 | 0.025949 | 0.31128 | 0.31128 | 0.24719 | 0.3479 | 0.56305 | 0.29755 | 0.15106 | -0.082397 | -0.054932 | -0.091553 | 0.17853 | 0.14191 | -0.10529 | -0.19226 | 123.1796 | 123.0331 | 0.009155 | 123.1934 | 123.23 | 0.19684 | -0.24262 | 122.7768 | 122.6898 | -0.37537 | 122.7997 | 122.7905 | 0.10071 | -0.41199 | 123.4451 | 123.1934 | 123.1293 | -0.40283 | 123.0606 | 123.024 | 122.8271 | -0.74616
1083.6875 | 123.4039 | -122.8683 | 0.54932 | 0.29367 | 0.12086 | 0.0037401 | 0.021604 | -0.026752 | 0.0058954 | 0.01998 | 0.17756 | 0.016085 | 0.018205 | 0.0080378 | -0.0002932 | 0.03129 | 0.28839 | 0.28381 | 0.2243 | 0.33417 | 0.54932 | 0.29297 | 0.14648 | -0.050354 | -0.054932 | -0.073242 | 0.1831 | 0.1236 | -0.12817 | -0.19226 | 123.1613 | 123.0148 | 0 | 123.1522 | 123.2025 | 0.18768 | -0.26093 | 122.7402 | 122.6761 | -0.36621 | 122.818 | 122.7951 | 0.11902 | -0.42572 | 123.4177 | 123.1567 | 123.0927 | -0.40283 | 123.0515 | 122.9919 | 122.8134 | -0.74158
1084.6875 | 123.436 | -122.8912 | 0.52185 | -0.33194 | 0.11873 | 0.017625 | 0.031217 | -0.018207 | -0.0037176 | 0.021048 | -0.46331 | 0.016085 | -0.017042 | -0.015461 | -0.0024292 | 0.018473 | 0.33875 | 0.33875 | 0.25177 | 0.35706 | 0.5722 | 0.28381 | 0.14648 | -0.032043 | 0.027466 | -0.041199 | 0.19684 | 0.13733 | -0.12817 | -0.1831 | 123.175 | 123.0377 | 0.050354 | 123.23 | 123.2483 | 0.21057 | -0.18311 | 122.7631 | 122.7081 | -0.32501 | 122.8592 | 122.85 | 0.14191 | -0.38452 | 123.4634 | 123.23 | 123.143 | -0.37537 | 123.0881 | 123.0286 | 122.9187 | -0.70496
1085.6875 | 123.4543 | -122.8546 | 0.53558 | -0.36246 | 0.1262 | 0.016557 | 0.023741 | -0.0032532 | 0.010168 | 0.014639 | -0.40227 | 0.0032668 | -0.0042246 | 0.010174 | -0.0056342 | 0.013132 | 0.33417 | 0.36621 | 0.27466 | 0.38452 | 0.5722 | 0.28839 | 0.13733 | 0 | 0.027466 | -0.022888 | 0.17395 | 0.13275 | -0.10071 | -0.17853 | 123.143 | 122.9919 | 0.036622 | 123.2208 | 123.2391 | 0.24719 | -0.20142 | 122.7539 | 122.6761 | -0.36163 | 122.8546 | 122.8317 | 0.15564 | -0.40283 | 123.4268 | 123.1888 | 123.1293 | -0.39825 | 123.0286 | 122.9874 | 122.8821 | -0.71411
1086.6875 | 123.4726 | -122.8729 | 0.53558 | -0.20987 | 0.11873 | 0.018693 | 0.022672 | -0.024616 | 0.012304 | 0.010367 | -0.38701 | 0.011812 | -0.0020886 | -0.0015752 | 0.0039788 | 0.025949 | 0.38452 | 0.37079 | 0.29297 | 0.37537 | 0.56763 | 0.29755 | 0.14191 | 0.009155 | 0.045776 | -0.022888 | 0.16479 | 0.12817 | -0.10986 | -0.17853 | 123.1705 | 123.0148 | 0.032044 | 123.2437 | 123.2483 | 0.23346 | -0.15106 | 122.7631 | 122.6944 | -0.37079 | 122.8821 | 122.85 | 0.15564 | -0.40741 | 123.4406 | 123.2574 | 123.1659 | -0.39368 | 123.0377 | 123.0011 | 122.9187 | -0.71411
1087.6875 | 123.4634 | -122.8912 | 0.53101 | -0.28617 | 0.10377 | 0.011217 | 0.039762 | -0.029956 | 0.010168 | 0.014639 | -0.38701 | 0.013948 | -0.010634 | -0.00050718 | 0.0018428 | 0.027017 | 0.36163 | 0.37537 | 0.27924 | 0.37079 | 0.55847 | 0.29297 | 0.12817 | 0.004578 | 0.050354 | -0.013733 | 0.16937 | 0.1236 | -0.1236 | -0.17853 | 123.1842 | 123.0194 | 0.027466 | 123.2666 | 123.262 | 0.24261 | -0.16937 | 122.7676 | 122.7127 | -0.36163 | 122.8958 | 122.8775 | 0.16479 | -0.40741 | 123.4497 | 123.2529 | 123.1705 | -0.40283 | 123.0606 | 123.0148 | 122.9416 | -0.70953
1088.6875 | 123.4589 | -122.8729 | 0.54016 | -0.31669 | 0.094162 | 0.0048081 | 0.025877 | -0.0064582 | -0.0037176 | 0.018912 | -0.23443 | 0.011812 | -0.0084976 | 0.0026968 | -0.0034972 | 0.030222 | 0.35248 | 0.37537 | 0.28839 | 0.3891 | 0.56305 | 0.28381 | 0.1236 | -0.009155 | 0.041199 | -0.018311 | 0.17395 | 0.13275 | -0.11444 | -0.17395 | 123.1567 | 122.9965 | 0.022888 | 123.2483 | 123.262 | 0.2655 | -0.18768 | 122.7585 | 122.699 | -0.36621 | 122.8638 | 122.8546 | 0.15564 | -0.40741 | 123.436 | 123.2254 | 123.1613 | -0.41657 | 123.0469 | 123.0057 | 122.9141 | -0.71411
1089.6875 | 123.4543 | -122.8638 | 0.54474 | -0.39298 | 0.089889 | 0.013353 | 0.036558 | -0.011798 | -0.0047856 | 0.021048 | -0.49383 | 0.020357 | -0.0052926 | -0.0069162 | 0.0007748 | 0.019541 | 0.33417 | 0.36621 | 0.26093 | 0.37537 | 0.57678 | 0.28381 | 0.15564 | -0.013733 | 0.045776 | -0.018311 | 0.1831 | 0.1236 | -0.12817 | -0.17395 | 123.1476 | 123.0194 | 0.032043 | 123.23 | 123.2391 | 0.21973 | -0.21057 | 122.7356 | 122.6898 | -0.36163 | 122.85 | 122.8455 | 0.15564 | -0.42114 | 123.4406 | 123.1979 | 123.1247 | -0.3891 | 123.0469 | 122.9874 | 122.9095 | -0.71869
1090.6875 | 123.4589 | -122.8821 | 0.54016 | -0.3472 | 0.09523 | 0.014421 | 0.022672 | -0.025684 | -0.0058536 | 0.024253 | -0.52434 | 0.0096758 | 0.0021844 | 0.0037648 | -0.0077702 | 0.025949 | 0.32044 | 0.32959 | 0.24261 | 0.37079 | 0.5722 | 0.28839 | 0.12817 | -0.027466 | 0.027466 | -0.041199 | 0.17395 | 0.11444 | -0.11444 | -0.17853 | 123.1705 | 123.0103 | 0.032044 | 123.2117 | 123.2529 | 0.24261 | -0.21973 | 122.7676 | 122.7036 | -0.36621 | 122.8546 | 122.8409 | 0.13733 | -0.42572 | 123.4543 | 123.2025 | 123.1247 | -0.41199 | 123.056 | 122.9965 | 122.9095 | -0.71869
1091.6875 | 123.4085 | -122.8958 | 0.54932 | -0.48453 | 0.094162 | 0.015489 | 0.029081 | -0.0032532 | -0.015467 | 0.014639 | -0.47857 | 0.02997 | 0.0011164 | -0.0015752 | -0.0056342 | 0.023813 | 0.30212 | 0.32501 | 0.22888 | 0.33417 | 0.57678 | 0.2655 | 0.1236 | -0.050354 | 0 | -0.059509 | 0.16937 | 0.13733 | -0.1236 | -0.19226 | 123.1613 | 123.0194 | 0.027466 | 123.2208 | 123.23 | 0.21057 | -0.24719 | 122.7722 | 122.7036 | -0.37994 | 122.8455 | 122.8363 | 0.13275 | -0.41199 | 123.4726 | 123.1979 | 123.1247 | -0.42572 | 123.0652 | 123.0331 | 122.8958 | -0.74158
1092.6875 | 123.4085 | -122.8592 | 0.54474 | -0.40824 | 0.10911 | 0.0048081 | 0.017332 | -0.026752 | -0.0037176 | 0.011435 | -0.46331 | 0.010744 | 0.0053884 | -0.0069162 | -0.0045652 | 0.029154 | 0.31128 | 0.32044 | 0.26093 | 0.32959 | 0.58594 | 0.2655 | 0.1236 | -0.068665 | 0.009155 | -0.054932 | 0.18768 | 0.13733 | -0.10529 | -0.18768 | 123.1247 | 122.9828 | 0.041198 | 123.1796 | 123.1888 | 0.20599 | -0.23346 | 122.7539 | 122.6715 | -0.35706 | 122.7905 | 122.8043 | 0.13275 | -0.40741 | 123.4451 | 123.1705 | 123.1201 | -0.42114 | 123.0469 | 122.9965 | 122.8683 | -0.73242
1093.6875 | 123.4543 | -122.8729 | 0.54016 | -0.36246 | 0.092026 | 0.0090801 | 0.013059 | -0.0075262 | 0.00055539 | 0.01998 | -0.49383 | 0.011812 | -0.0074286 | -0.0026432 | -0.0024292 | 0.030222 | 0.31128 | 0.34332 | 0.25635 | 0.36163 | 0.56763 | 0.30212 | 0.13733 | -0.009155 | 0.018311 | -0.032043 | 0.17395 | 0.12817 | -0.11444 | -0.17853 | 123.175 | 123.0103 | 0.027466 | 123.2162 | 123.2346 | 0.2243 | -0.22888 | 122.7585 | 122.6944 | -0.36621 | 122.8638 | 122.8409 | 0.14648 | -0.41199 | 123.4406 | 123.1842 | 123.1293 | -0.40283 | 123.0469 | 123.0011 | 122.8912 | -0.71869
1094.6875 | 123.436 | -122.8867 | 0.54474 | -0.39298 | 0.083481 | 0.025102 | 0.025877 | -0.02782 | -0.0047856 | 0.025321 | -0.46331 | 0.018221 | -0.0010206 | -0.012256 | -0.0034972 | 0.028086 | 0.3067 | 0.33417 | 0.25177 | 0.36163 | 0.5722 | 0.28381 | 0.13733 | -0.032043 | 0.018311 | -0.059509 | 0.17853 | 0.13275 | -0.10986 | -0.18768 | 123.1705 | 123.024 | 0.027466 | 123.2208 | 123.2483 | 0.2243 | -0.23804 | 122.7768 | 122.699 | -0.36621 | 122.8546 | 122.8271 | 0.12817 | -0.41199 | 123.4589 | 123.1934 | 123.1384 | -0.40741 | 123.0652 | 123.0194 | 122.905 | -0.73242
1095.6875 | 123.4451 | -122.9095 | 0.55847 | -0.37772 | 0.082412 | 0.014421 | 0.042967 | -0.017139 | -0.012263 | 0.015708 | -0.50908 | 0.016085 | -0.015974 | 0.00056082 | -0.0045652 | 0.019541 | 0.31586 | 0.32959 | 0.24719 | 0.34332 | 0.57678 | 0.29297 | 0.12817 | -0.054932 | 0.004578 | -0.064087 | 0.17853 | 0.13733 | -0.11444 | -0.18768 | 123.2025 | 123.0377 | 0.01831 | 123.2391 | 123.2529 | 0.21515 | -0.24261 | 122.7951 | 122.7219 | -0.37994 | 122.8546 | 122.8455 | 0.1236 | -0.42114 | 123.4863 | 123.2254 | 123.1567 | -0.4303 | 123.0881 | 123.0469 | 122.9141 | -0.74615
1096.6875 | 123.4222 | -122.9004 | 0.54016 | -0.36246 | 0.092026 | 0.019762 | 0.030149 | -0.0064582 | -0.0090576 | 0.007163 | -0.46331 | 0.0064718 | -0.023451 | 0.00056082 | -0.0056342 | 0.025949 | 0.29755 | 0.32044 | 0.24719 | 0.34332 | 0.57678 | 0.28839 | 0.13275 | -0.041199 | -0.018311 | -0.059509 | 0.17395 | 0.12817 | -0.11444 | -0.18768 | 123.1888 | 123.0331 | 0.036621 | 123.2208 | 123.2437 | 0.21057 | -0.24262 | 122.7859 | 122.7127 | -0.36621 | 122.8592 | 122.8409 | 0.12817 | -0.41199 | 123.4772 | 123.1979 | 123.1476 | -0.40741 | 123.0743 | 123.0286 | 122.8821 | -0.72784
1097.6875 | 123.4222 | -122.8821 | 0.55389 | -0.48453 | 0.09523 | 0.016557 | 0.020536 | -0.022479 | -0.0079896 | 0.015708 | -0.58538 | 6.2833e-05 | -0.018111 | 0.014447 | 0.0007748 | 0.03129 | 0.28839 | 0.32959 | 0.23804 | 0.33417 | 0.58136 | 0.2655 | 0.14191 | -0.045776 | 0 | -0.068665 | 0.19226 | 0.1236 | -0.1236 | -0.18768 | 123.1476 | 123.024 | 0.027466 | 123.2117 | 123.2162 | 0.19226 | -0.2655 | 122.7585 | 122.6944 | -0.36163 | 122.8363 | 122.8134 | 0.11902 | -0.4303 | 123.4634 | 123.1705 | 123.1201 | -0.41199 | 123.0743 | 123.0057 | 122.8821 | -0.74158
1098.6875 | 123.4314 | -122.8912 | 0.54474 | -0.4235 | 0.077072 | 0.025102 | 0.024809 | -0.015003 | -0.017603 | 0.005026 | -0.47857 | 0.010744 | -0.017042 | -0.0090522 | -0.0045652 | 0.027017 | 0.33417 | 0.40741 | 0.32044 | 0.39825 | 0.54474 | 0.31128 | 0.16022 | -0.022888 | 0.032043 | -0.036621 | 0.16479 | 0.11902 | -0.1236 | -0.17395 | 123.2025 | 123.0515 | 0 | 123.2986 | 123.2895 | 0.23804 | -0.21057 | 122.7676 | 122.7173 | -0.37994 | 122.8683 | 122.8546 | 0.13733 | -0.42572 | 123.436 | 123.2254 | 123.2117 | -0.38452 | 123.056 | 123.0103 | 122.9233 | -0.71869
1099.6875 | 123.4222 | -122.8912 | 0.55847 | -0.40824 | 0.081344 | 0.011217 | 0.029081 | -0.026752 | -0.011195 | 0.007163 | -0.58538 | 0.0011308 | -0.013838 | -0.013324 | -0.0067022 | 0.025949 | 0.29297 | 0.33875 | 0.24719 | 0.34332 | 0.5722 | 0.30212 | 0.12817 | -0.041199 | 0.009155 | -0.054932 | 0.18768 | 0.11902 | -0.13733 | -0.19226 | 123.1934 | 123.0194 | 0.013733 | 123.23 | 123.2346 | 0.21515 | -0.2655 | 122.7539 | 122.699 | -0.37079 | 122.85 | 122.8363 | 0.13733 | -0.43945 | 123.4634 | 123.1842 | 123.1384 | -0.4303 | 123.0789 | 123.0103 | 122.9004 | -0.75073
1100.6875 | 123.4131 | -122.8821 | 0.55847 | -0.48453 | 0.09523 | 0.024034 | 0.019468 | -0.019275 | 0.00055539 | 0.016776 | -0.64641 | -0.0063462 | -0.0031566 | 0.0091058 | -0.0013612 | 0.021677 | 0.30212 | 0.33417 | 0.23346 | 0.35248 | 0.58136 | 0.27924 | 0.13275 | -0.054932 | -0.027466 | -0.07782 | 0.1831 | 0.11902 | -0.1236 | -0.18768 | 123.1613 | 123.0148 | 0.022888 | 123.2162 | 123.2346 | 0.21973 | -0.25635 | 122.7585 | 122.6944 | -0.37537 | 122.8271 | 122.8043 | 0.10986 | -0.43945 | 123.4634 | 123.1842 | 123.1155 | -0.42572 | 123.0652 | 123.0011 | 122.8546 | -0.74615
1101.6875 | 123.4039 | -122.9095 | 0.55847 | -0.43876 | 0.097366 | 0.012285 | 0.021604 | -0.0096622 | -0.0090576 | 0.013571 | -0.6159 | 0.016085 | -0.01277 | 0.0080378 | -0.0034972 | 0.022745 | 0.29297 | 0.3479 | 0.25635 | 0.33875 | 0.58594 | 0.27466 | 0.11444 | -0.045776 | -0.013733 | -0.064087 | 0.18768 | 0.13275 | -0.11444 | -0.1831 | 123.1842 | 123.024 | 0.027465 | 123.2574 | 123.2483 | 0.2243 | -0.2655 | 122.7951 | 122.7264 | -0.37079 | 122.8638 | 122.8455 | 0.11902 | -0.42572 | 123.4955 | 123.2025 | 123.1659 | -0.44403 | 123.0972 | 123.0423 | 122.8958 | -0.74158
1102.6875 | 123.4177 | -122.8912 | 0.54932 | -0.46927 | 0.086685 | 0.014421 | 0.0055833 | -0.026752 | -0.0069216 | 0.009299 | -0.63115 | 0.013948 | -0.0095656 | 0.0059018 | -0.0024292 | 0.020609 | 0.29755 | 0.3479 | 0.24719 | 0.33417 | 0.5722 | 0.27924 | 0.13733 | -0.041199 | -0.004578 | -0.068665 | 0.19684 | 0.13733 | -0.12817 | -0.18768 | 123.1705 | 123.0286 | 0.022889 | 123.2391 | 123.2254 | 0.19684 | -0.25177 | 122.7631 | 122.7036 | -0.35248 | 122.85 | 122.8226 | 0.11902 | -0.41199 | 123.4634 | 123.1888 | 123.1384 | -0.41199 | 123.0881 | 123.0286 | 122.8867 | -0.737
1103.6875 | 123.4314 | -122.9141 | 0.55389 | -0.4235 | 0.085617 | 0.0048081 | 0.013059 | -0.011798 | 0.00055539 | 0.010367 | -0.6159 | 0.0064718 | -0.010634 | -0.0079842 | -0.0002932 | 0.022745 | 0.30212 | 0.37079 | 0.27008 | 0.32501 | 0.57678 | 0.27008 | 0.13275 | -0.036621 | 0.004578 | -0.054932 | 0.18768 | 0.13275 | -0.11902 | -0.21057 | 123.1842 | 123.0469 | 0.022888 | 123.2849 | 123.2391 | 0.19226 | -0.25177 | 122.7951 | 122.7036 | -0.36621 | 122.8775 | 122.8592 | 0.15564 | -0.42114 | 123.4909 | 123.2162 | 123.1842 | -0.42114 | 123.1018 | 123.0469 | 122.9187 | -0.76446
1104.6875 | 123.4131 | -122.8729 | 0.56305 | -0.57608 | 0.10591 | 0.013353 | 0.015196 | -0.015003 | -0.014399 | 0.016776 | -0.47857 | 0.011812 | -0.022383 | -0.012256 | -0.0002932 | 0.015268 | 0.31586 | 0.37537 | 0.27924 | 0.35706 | 0.54474 | 0.28839 | 0.13275 | -0.018311 | 0.013733 | -0.045776 | 0.17853 | 0.11902 | -0.1236 | -0.20142 | 123.1613 | 123.0057 | -0.01831 | 123.2483 | 123.23 | 0.2243 | -0.24719 | 122.7493 | 122.6715 | -0.38452 | 122.8546 | 122.8271 | 0.15564 | -0.44403 | 123.4177 | 123.1888 | 123.1522 | -0.4303 | 123.0515 | 122.9919 | 122.8867 | -0.76447
1105.6875 | 123.4314 | -122.8867 | 0.54932 | -0.51505 | 0.079208 | 0.019762 | 0.016264 | -0.028888 | -0.013331 | 0.009299 | -0.55486 | 0.0096758 | 0.0011164 | -0.0015752 | -0.0045652 | 0.015268 | 0.3479 | 0.42114 | 0.30212 | 0.39368 | 0.55847 | 0.29297 | 0.15564 | -0.022888 | 0.041199 | -0.022888 | 0.17853 | 0.12817 | -0.11902 | -0.1831 | 123.1796 | 123.0423 | 0.009156 | 123.3078 | 123.2803 | 0.23804 | -0.20142 | 122.7676 | 122.7036 | -0.37079 | 122.8638 | 122.8638 | 0.16022 | -0.42114 | 123.4451 | 123.2346 | 123.1888 | -0.39368 | 123.0652 | 123.0148 | 122.9279 | -0.73242
1106.6875 | 123.4497 | -122.8958 | 0.54474 | -0.45401 | 0.10377 | 0.013353 | 0.0184 | -0.017139 | -0.0026496 | 0.025321 | -0.52434 | 0.011812 | -0.025587 | -0.00050718 | -0.0067022 | 0.019541 | 0.37079 | 0.44861 | 0.33417 | 0.40741 | 0.54474 | 0.29755 | 0.15106 | 0 | 0.041199 | -0.009155 | 0.15106 | 0.10986 | -0.10986 | -0.17395 | 123.1934 | 123.0469 | 0 | 123.3444 | 123.3032 | 0.25635 | -0.17395 | 122.7859 | 122.7219 | -0.39368 | 122.8958 | 122.8867 | 0.16479 | -0.43488 | 123.4406 | 123.2666 | 123.23 | -0.39368 | 123.0469 | 123.0057 | 122.937 | -0.71869
1107.6875 | 123.4268 | -122.8683 | 0.55389 | -0.45401 | 0.080276 | 0.011217 | 0.023741 | -0.0075262 | -0.0079896 | 0.007163 | -0.57012 | 0.0021988 | -0.0052926 | -0.01012 | -0.0067022 | 0.019541 | 0.29755 | 0.36621 | 0.2655 | 0.35248 | 0.5722 | 0.28839 | 0.13733 | -0.022888 | 0.004578 | -0.045776 | 0.19226 | 0.11902 | -0.12817 | -0.18768 | 123.1567 | 123.0057 | 0.018311 | 123.2346 | 123.2208 | 0.21515 | -0.25635 | 122.7402 | 122.6807 | -0.36163 | 122.8455 | 122.8226 | 0.14191 | -0.43488 | 123.4406 | 123.1659 | 123.1338 | -0.41656 | 123.0606 | 122.9874 | 122.8729 | -0.74158
1108.6875 | 123.4268 | -122.8546 | 0.54474 | -0.48453 | 0.072799 | 0.0069441 | 0.03549 | -0.024616 | -0.0037176 | 0.017844 | -0.58538 | 0.0021988 | -0.014906 | -0.0090522 | -0.0045652 | 0.027017 | 0.32044 | 0.41199 | 0.28381 | 0.35706 | 0.55847 | 0.29755 | 0.14648 | -0.041199 | 0.022888 | -0.054932 | 0.19226 | 0.13275 | -0.10071 | -0.19226 | 123.1522 | 123.0011 | 0.013733 | 123.2666 | 123.2117 | 0.21057 | -0.2243 | 122.7539 | 122.6624 | -0.35248 | 122.8134 | 122.7997 | 0.13733 | -0.41199 | 123.4131 | 123.175 | 123.1384 | -0.39825 | 123.0469 | 122.9874 | 122.8775 | -0.737
1109.6875 | 123.4451 | -122.8775 | 0.55847 | -0.46927 | 0.058914 | 0.027238 | 0.019468 | -0.016071 | -0.012263 | 0.021048 | -0.60064 | -0.0020732 | -0.013838 | 0.0037648 | -0.0067022 | 0.022745 | 0.35248 | 0.4303 | 0.32044 | 0.40283 | 0.54474 | 0.3067 | 0.16022 | -0.022888 | 0.018311 | -0.022888 | 0.16479 | 0.12817 | -0.10986 | -0.1831 | 123.1842 | 123.0377 | -0.013733 | 123.3078 | 123.2803 | 0.24262 | -0.20599 | 122.7676 | 122.6944 | -0.39368 | 122.8546 | 122.8546 | 0.16022 | -0.4303 | 123.4222 | 123.23 | 123.1979 | -0.39825 | 123.0423 | 123.0057 | 122.8958 | -0.74158
1110.6875 | 123.4634 | -122.85 | 0.55389 | -0.43876 | 0.082412 | 0.0048081 | 0.029081 | -0.019275 | -0.015467 | 0.01998 | -0.58538 | -0.0020732 | -0.011702 | 0.010174 | -0.0056342 | 0.033426 | 0.37537 | 0.45776 | 0.33417 | 0.41199 | 0.54474 | 0.32501 | 0.16937 | 0.009155 | 0.054932 | 0 | 0.15564 | 0.10071 | -0.10529 | -0.15564 | 123.175 | 123.0194 | -0.009155 | 123.3078 | 123.262 | 0.24261 | -0.17853 | 122.7448 | 122.6944 | -0.39825 | 122.8592 | 122.85 | 0.15564 | -0.45319 | 123.3948 | 123.2254 | 123.1842 | -0.38452 | 123.0057 | 122.9507 | 122.905 | -0.70953
1111.6875 | 123.4955 | -122.85 | 0.54474 | -0.30143 | 0.086685 | 0.010148 | 0.0098553 | -0.02782 | -0.016535 | 0.012503 | -0.60064 | -0.0010052 | -0.013838 | -0.00050718 | -0.0077702 | 0.019541 | 0.37994 | 0.45776 | 0.35706 | 0.41199 | 0.54016 | 0.32044 | 0.15564 | 0.032043 | 0.07782 | 0.009155 | 0.15106 | 0.10071 | -0.09613 | -0.16022 | 123.1705 | 123.0057 | -0.004578 | 123.3078 | 123.262 | 0.25635 | -0.16479 | 122.7539 | 122.6898 | -0.39368 | 122.8821 | 122.8592 | 0.16937 | -0.44403 | 123.3902 | 123.23 | 123.2071 | -0.3891 | 123.0011 | 122.9507 | 122.9279 | -0.70496
1112.6875 | 123.5092 | -122.8592 | 0.54016 | -0.40824 | 0.082412 | 0.0080121 | 0.019468 | -0.011798 | -0.0090576 | 0.011435 | -0.47857 | 0.0032668 | -0.0042246 | -0.013324 | 0.0029108 | 0.015268 | 0.3891 | 0.48523 | 0.37079 | 0.41199 | 0.53558 | 0.32044 | 0.18768 | 0.050354 | 0.11444 | 0.018311 | 0.14191 | 0.10529 | -0.09613 | -0.17395 | 123.1796 | 123.0469 | -0.004578 | 123.3444 | 123.2712 | 0.2243 | -0.15106 | 122.7631 | 122.6852 | -0.39825 | 122.9095 | 122.8775 | 0.19226 | -0.43488 | 123.3948 | 123.2483 | 123.23 | -0.35248 | 123.0011 | 122.9645 | 122.9736 | -0.71411
1113.6875 | 123.5229 | -122.8592 | 0.51727 | -0.39298 | 0.089889 | 0.018693 | 0.029081 | -0.020343 | -0.012263 | 0.009299 | -0.5396 | -0.0042092 | -0.014906 | 0.0059018 | -0.0002932 | 0.010996 | 0.39368 | 0.48065 | 0.36621 | 0.43488 | 0.54016 | 0.33417 | 0.17395 | 0.059509 | 0.13275 | 0.050354 | 0.13275 | 0.086975 | -0.082397 | -0.14648 | 123.1934 | 123.0331 | 0.022888 | 123.3398 | 123.2941 | 0.26093 | -0.1236 | 122.7768 | 122.7127 | -0.38452 | 122.9187 | 122.9095 | 0.19684 | -0.4303 | 123.3994 | 123.2529 | 123.2254 | -0.34332 | 122.9919 | 122.9462 | 122.9919 | -0.66376
1114.6875 | 123.436 | -122.8775 | 0.55847 | -0.48453 | 0.074936 | 0.010148 | 0.025877 | -0.012866 | -0.0090576 | 0.009299 | -0.69219 | 0.0054038 | -0.018111 | -0.0037112 | -0.015247 | 0.028086 | 0.37537 | 0.45776 | 0.33417 | 0.41199 | 0.55847 | 0.30212 | 0.15564 | -0.004578 | 0.054932 | -0.004578 | 0.15106 | 0.10986 | -0.10071 | -0.16479 | 123.1796 | 123.0331 | 0 | 123.3353 | 123.2895 | 0.25635 | -0.18311 | 122.7768 | 122.7127 | -0.40741 | 122.8729 | 122.8729 | 0.16022 | -0.44861 | 123.436 | 123.2529 | 123.2117 | -0.40283 | 123.0286 | 122.9874 | 122.9324 | -0.72327
1115.6875 | 123.4863 | -122.8592 | 0.52643 | -0.43876 | 0.074936 | 0.019762 | 0.020536 | -0.026752 | -0.0037176 | 0.015708 | -0.63115 | 0.0096758 | -0.0074286 | -0.013324 | 0.0007748 | 0.015268 | 0.39368 | 0.48065 | 0.34332 | 0.42114 | 0.53558 | 0.29755 | 0.19226 | 0.045776 | 0.07782 | 0.004578 | 0.14648 | 0.09613 | -0.09613 | -0.17395 | 123.1567 | 123.0515 | 0.009155 | 123.3398 | 123.2803 | 0.22888 | -0.13275 | 122.7631 | 122.6852 | -0.37994 | 122.905 | 122.8638 | 0.17853 | -0.4303 | 123.3948 | 123.2529 | 123.2025 | -0.33417 | 123.0057 | 122.9553 | 122.937 | -0.70038
1116.6875 | 123.4863 | -122.8546 | 0.53558 | -0.37772 | 0.087753 | 0.012285 | 0.0066513 | -0.023548 | -0.0058536 | 0.024253 | -0.57012 | 0.0054038 | -0.0010206 | 0.0026968 | -0.0013612 | 0.024881 | 0.39368 | 0.48981 | 0.36163 | 0.42114 | 0.54016 | 0.3067 | 0.17395 | 0.050354 | 0.11444 | 0.022888 | 0.16022 | 0.091553 | -0.082397 | -0.16937 | 123.1613 | 123.0286 | 0.004578 | 123.3444 | 123.2758 | 0.24719 | -0.14191 | 122.7722 | 122.6852 | -0.37537 | 122.905 | 122.8775 | 0.19226 | -0.44403 | 123.3948 | 123.2483 | 123.2162 | -0.36163 | 123.0148 | 122.9462 | 122.9691 | -0.70496
1117.6875 | 123.5184 | -122.8638 | 0.53558 | -0.39298 | 0.065323 | 0.017625 | 0.023741 | -0.024616 | -0.0090576 | 0.022116 | -0.49383 | -0.0020732 | -0.01277 | -0.0058482 | 0.0071838 | 0.0088586 | 0.37537 | 0.49896 | 0.38452 | 0.4303 | 0.54474 | 0.33417 | 0.16022 | 0.059509 | 0.12817 | 0.027466 | 0.14191 | 0.07782 | -0.086975 | -0.14648 | 123.1979 | 123.024 | 0.009156 | 123.3627 | 123.2941 | 0.27008 | -0.16022 | 122.7768 | 122.7173 | -0.39368 | 122.9233 | 122.8912 | 0.17395 | -0.45776 | 123.4085 | 123.2391 | 123.2483 | -0.37537 | 123.0057 | 122.9416 | 122.9919 | -0.68207
1118.6875 | 123.5275 | -122.8455 | 0.52643 | -0.37772 | 0.053573 | 0.00053514 | 0.017332 | -0.025684 | -0.0058536 | 0.015708 | -0.52434 | 0.0064718 | -0.019179 | 0.0016288 | -0.0002932 | 0.025949 | 0.42114 | 0.49439 | 0.37994 | 0.42114 | 0.53558 | 0.34332 | 0.17395 | 0.082397 | 0.13275 | 0.045776 | 0.14191 | 0.068665 | -0.064087 | -0.15564 | 123.1888 | 123.0194 | 0.009155 | 123.3398 | 123.2666 | 0.24719 | -0.10529 | 122.7814 | 122.6898 | -0.38452 | 122.9279 | 122.8912 | 0.20142 | -0.45776 | 123.381 | 123.2666 | 123.2254 | -0.35248 | 122.9874 | 122.9141 | 122.9782 | -0.68207
1119.6875 | 123.5458 | -122.8363 | 0.54016 | -0.36246 | 0.068527 | 0.016557 | 0.023741 | -0.017139 | -0.0058536 | 0.025321 | -0.49383 | 6.2833e-05 | -0.02986 | -0.011188 | -0.0077702 | 0.023813 | 0.39368 | 0.50354 | 0.39825 | 0.4303 | 0.5127 | 0.31586 | 0.19226 | 0.07782 | 0.13275 | 0.064087 | 0.15106 | 0.082397 | -0.086975 | -0.15106 | 123.1522 | 123.0286 | -0.027466 | 123.3398 | 123.2666 | 0.23804 | -0.14648 | 122.7493 | 122.6852 | -0.3891 | 122.9141 | 122.9004 | 0.21515 | -0.45776 | 123.349 | 123.23 | 123.2346 | -0.3479 | 122.9874 | 122.9187 | 122.9691 | -0.69122
1120.6875 | 123.5504 | -122.8363 | 0.5127 | -0.30143 | 0.047165 | 0.017625 | 0.0066513 | -0.026752 | -0.010127 | 0.008231 | -0.52434 | -0.0031412 | -0.014906 | -0.0058482 | -0.016315 | 0.012064 | 0.3891 | 0.50354 | 0.38452 | 0.43488 | 0.53558 | 0.31586 | 0.1831 | 0.082397 | 0.14648 | 0.073242 | 0.13733 | 0.07782 | -0.091553 | -0.14648 | 123.1522 | 123.0194 | 0.022888 | 123.3398 | 123.2712 | 0.25177 | -0.1236 | 122.7448 | 122.6898 | -0.37537 | 122.9187 | 122.9095 | 0.21973 | -0.43488 | 123.3719 | 123.2254 | 123.2208 | -0.32959 | 122.9736 | 122.9141 | 122.9828 | -0.65918
1121.6875 | 123.5046 | -122.8455 | 0.53101 | -0.39298 | 0.086685 | 0.021898 | 0.032286 | -0.017139 | 0.0016234 | 0.014639 | -0.58538 | 0.0054038 | -0.021315 | -0.00050718 | 0.0082518 | 0.022745 | 0.40741 | 0.47607 | 0.36163 | 0.41657 | 0.54016 | 0.32501 | 0.17395 | 0.068665 | 0.11444 | 0.022888 | 0.16022 | 0.091553 | -0.09613 | -0.14648 | 123.1705 | 123.0194 | 0.009155 | 123.3215 | 123.262 | 0.24262 | -0.1236 | 122.7493 | 122.699 | -0.37079 | 122.9141 | 122.8683 | 0.16937 | -0.43945 | 123.3856 | 123.2529 | 123.2071 | -0.35706 | 123.0057 | 122.937 | 122.9599 | -0.67749
1122.6875 | 123.5275 | -122.85 | 0.52643 | -0.28617 | 0.070663 | 0.014421 | 0.019468 | -0.012866 | 0.00055539 | 0.017844 | -0.44805 | 0.0021988 | -0.014906 | 0.0037648 | -0.0056342 | 0.015268 | 0.40741 | 0.50812 | 0.37537 | 0.42114 | 0.53101 | 0.31586 | 0.16937 | 0.064087 | 0.12817 | 0.032043 | 0.16937 | 0.082397 | -0.082397 | -0.13275 | 123.1659 | 123.0194 | 0.004578 | 123.3582 | 123.2712 | 0.25177 | -0.11902 | 122.7676 | 122.7173 | -0.35706 | 122.9141 | 122.8821 | 0.16479 | -0.44403 | 123.381 | 123.2574 | 123.2254 | -0.35706 | 123.0194 | 122.9324 | 122.9782 | -0.65918
1123.6875 | 123.5458 | -122.818 | 0.52185 | -0.40824 | 0.080276 | 0.013353 | 0.016264 | -0.033161 | -0.0015816 | 0.018912 | -0.47857 | -0.0010052 | -0.019179 | -0.0058482 | 0.0093198 | 0.019541 | 0.41199 | 0.5127 | 0.37537 | 0.43488 | 0.52643 | 0.3067 | 0.15564 | 0.073242 | 0.13733 | 0.059509 | 0.13733 | 0.082397 | -0.09613 | -0.15564 | 123.1247 | 122.9736 | 0.004577 | 123.3307 | 123.2529 | 0.27924 | -0.10986 | 122.7219 | 122.6624 | -0.38452 | 122.8912 | 122.8775 | 0.21515 | -0.43945 | 123.3444 | 123.23 | 123.1934 | -0.36621 | 122.9553 | 122.9004 | 122.9553 | -0.67749
1124.6875 | 123.5321 | -122.8363 | 0.52643 | -0.33194 | 0.071731 | 0.0016041 | 0.0184 | -0.015003 | 0.00055539 | 0.01998 | -0.55486 | -0.0020732 | -0.021315 | -0.017597 | 0.0050478 | 0.019541 | 0.41199 | 0.52643 | 0.38452 | 0.42572 | 0.52185 | 0.31586 | 0.16937 | 0.086975 | 0.14648 | 0.059509 | 0.14648 | 0.082397 | -0.082397 | -0.14648 | 123.1522 | 123.0057 | -0.004577 | 123.3627 | 123.262 | 0.25635 | -0.11444 | 122.7539 | 122.6898 | -0.37994 | 122.9233 | 122.8958 | 0.20599 | -0.44403 | 123.3582 | 123.2483 | 123.2208 | -0.35706 | 122.9828 | 122.9187 | 122.9828 | -0.67291
1125.6875 | 123.5733 | -122.8271 | 0.53558 | -0.13358 | 0.042892 | 0.02617 | 0.016264 | -0.024616 | -0.015467 | 0.01998 | -0.2802 | 0.0043348 | -0.02986 | -0.0058482 | 0.0007748 | 0.034494 | 0.39825 | 0.50354 | 0.38452 | 0.41657 | 0.53558 | 0.32044 | 0.17853 | 0.11902 | 0.14648 | 0.10071 | 0.12817 | 0.086975 | -0.086975 | -0.14191 | 123.1476 | 123.0057 | 0 | 123.3307 | 123.2437 | 0.23804 | -0.13733 | 122.7402 | 122.6852 | -0.40741 | 122.9462 | 122.9279 | 0.24262 | -0.44861 | 123.3627 | 123.2254 | 123.2117 | -0.35706 | 122.9553 | 122.9141 | 122.9736 | -0.67749
1126.6875 | 123.5321 | -122.8317 | 0.53101 | -0.24039 | 0.07814 | 0.021898 | 0.020536 | -0.01073 | -0.0058536 | 0.006095 | -0.55486 | 0.0011308 | -0.01277 | -0.0026432 | 0.0061158 | 0.020609 | 0.40741 | 0.50812 | 0.38452 | 0.43488 | 0.53101 | 0.32044 | 0.16022 | 0.082397 | 0.16022 | 0.068665 | 0.15564 | 0.07782 | -0.091553 | -0.16937 | 123.1522 | 122.9919 | 0 | 123.3398 | 123.2666 | 0.27466 | -0.1236 | 122.7402 | 122.6624 | -0.37537 | 122.9141 | 122.9004 | 0.23804 | -0.45319 | 123.3627 | 123.2391 | 123.2162 | -0.37079 | 122.9874 | 122.9095 | 122.9919 | -0.70038
1127.6875 | 123.5092 | -122.8546 | 0.52643 | -0.3472 | 0.059982 | 0.016557 | 0.014128 | -0.018207 | -0.010127 | 0.010367 | -0.52434 | 0.0032668 | -0.0074286 | -0.0079842 | -0.0013612 | 0.023813 | 0.41199 | 0.49439 | 0.37079 | 0.4303 | 0.53101 | 0.3067 | 0.17395 | 0.064087 | 0.12817 | 0.041199 | 0.15106 | 0.082397 | -0.09613 | -0.15564 | 123.1613 | 123.0286 | 0.004578 | 123.349 | 123.2849 | 0.25635 | -0.11444 | 122.7585 | 122.699 | -0.37537 | 122.9187 | 122.8958 | 0.19684 | -0.44403 | 123.3856 | 123.2666 | 123.2254 | -0.35248 | 123.0057 | 122.937 | 122.9828 | -0.68207
1128.6875 | 123.5458 | -122.8271 | 0.54016 | -0.3472 | 0.079208 | 0.012285 | 0.015196 | -0.019275 | -0.0037176 | 0.018912 | -0.46331 | 0.0032668 | -0.02986 | 0.0037648 | -0.0013612 | 0.020609 | 0.42572 | 0.51727 | 0.38452 | 0.42572 | 0.53558 | 0.31128 | 0.1831 | 0.082397 | 0.13733 | 0.064087 | 0.15106 | 0.09613 | -0.10071 | -0.15564 | 123.1384 | 123.0103 | -0.004578 | 123.3444 | 123.2529 | 0.24261 | -0.11444 | 122.7264 | 122.6715 | -0.3891 | 122.9095 | 122.8912 | 0.21973 | -0.44403 | 123.3627 | 123.2529 | 123.2117 | -0.35706 | 122.9782 | 122.9233 | 122.9645 | -0.6958
1129.6875 | 123.5458 | -122.8409 | 0.51727 | -0.31669 | 0.065323 | 0.016557 | 0.0184 | -0.024616 | -0.014399 | 0.006095 | -0.46331 | 0.0096758 | -0.013838 | -0.0058482 | -0.0024292 | 0.023813 | 0.39825 | 0.51727 | 0.37537 | 0.42114 | 0.52643 | 0.31586 | 0.17395 | 0.091553 | 0.14648 | 0.054932 | 0.15106 | 0.091553 | -0.082397 | -0.13733 | 123.1567 | 123.0148 | 0.009155 | 123.3582 | 123.262 | 0.24719 | -0.11902 | 122.7585 | 122.7036 | -0.36621 | 122.9324 | 122.8958 | 0.19226 | -0.42572 | 123.3673 | 123.2391 | 123.2162 | -0.34332 | 122.9919 | 122.9324 | 122.9874 | -0.6546
1130.6875 | 123.5367 | -122.8043 | 0.51727 | -0.51505 | 0.080276 | 0.029375 | 0.023741 | -0.028888 | -0.0015816 | 0.025321 | -0.49383 | 0.0021988 | -0.013838 | 0.0016288 | 0.0071838 | 0.022745 | 0.41657 | 0.50354 | 0.39368 | 0.42572 | 0.54016 | 0.32959 | 0.16479 | 0.10529 | 0.16022 | 0.09613 | 0.13733 | 0.082397 | -0.086975 | -0.14648 | 123.1338 | 122.9691 | 0.022888 | 123.3078 | 123.23 | 0.26092 | -0.10071 | 122.7173 | 122.6578 | -0.37994 | 122.9095 | 122.9004 | 0.24261 | -0.43488 | 123.3444 | 123.2208 | 123.1979 | -0.35248 | 122.9416 | 122.8867 | 122.9645 | -0.66376
1131.6875 | 123.5413 | -122.8226 | 0.53101 | -0.22513 | 0.068527 | 0.014421 | 0.0184 | -0.0096622 | -0.0058536 | 0.018912 | -0.5396 | 0.01288 | -0.036268 | -0.0090522 | 0.0029108 | 0.0067226 | 0.4303 | 0.53101 | 0.39825 | 0.43488 | 0.53101 | 0.31586 | 0.1831 | 0.086975 | 0.16022 | 0.091553 | 0.13733 | 0.07782 | -0.10529 | -0.16022 | 123.1384 | 123.0057 | 0 | 123.3536 | 123.2574 | 0.25177 | -0.10071 | 122.7173 | 122.6624 | -0.39368 | 122.9095 | 122.9141 | 0.25177 | -0.45319 | 123.3536 | 123.2529 | 123.2208 | -0.3479 | 122.9599 | 122.9004 | 122.9828 | -0.69122
1132.6875 | 123.5458 | -122.8317 | 0.54016 | -0.1641 | 0.067459 | 0.012285 | 0.030149 | -0.024616 | -0.0090576 | 0.014639 | -0.21917 | 0.0054038 | -0.015974 | -0.0047802 | 0.0007748 | 0.024881 | 0.3891 | 0.47607 | 0.36163 | 0.40283 | 0.54932 | 0.32501 | 0.16479 | 0.10529 | 0.1236 | 0.091553 | 0.16022 | 0.073242 | -0.09613 | -0.13733 | 123.1567 | 122.9965 | 0.009155 | 123.3078 | 123.2346 | 0.23804 | -0.15106 | 122.7356 | 122.6944 | -0.37994 | 122.937 | 122.9233 | 0.22888 | -0.46692 | 123.381 | 123.2208 | 123.1934 | -0.37537 | 122.9919 | 122.905 | 122.9553 | -0.67749
1133.6875 | 123.5779 | -122.8271 | 0.54016 | -0.22513 | 0.071731 | 0.015489 | 0.029081 | -0.025684 | 0.0048274 | 0.014639 | -0.37176 | -0.0010052 | -0.020247 | 0.0037648 | -0.0013612 | 0.018473 | 0.43488 | 0.53101 | 0.40283 | 0.4303 | 0.53558 | 0.32044 | 0.17395 | 0.10529 | 0.15106 | 0.086975 | 0.15564 | 0.082397 | -0.068665 | -0.12817 | 123.1476 | 123.0011 | -0.004578 | 123.3582 | 123.2574 | 0.25635 | -0.10529 | 122.7585 | 122.699 | -0.38452 | 122.9324 | 122.9141 | 0.21515 | -0.45776 | 123.3627 | 123.262 | 123.23 | -0.36621 | 122.9828 | 122.9095 | 122.9782 | -0.66834
1134.6875 | 123.5413 | -122.8317 | 0.52643 | -0.39298 | 0.058914 | 0.0058761 | 0.019468 | -0.015003 | -0.0058536 | 0.015708 | -0.60064 | 0.0011308 | -0.017042 | 0.0059018 | 0.0018428 | 0.020609 | 0.41657 | 0.52185 | 0.39825 | 0.43488 | 0.54932 | 0.32501 | 0.18768 | 0.10071 | 0.15564 | 0.073242 | 0.14191 | 0.050354 | -0.07782 | -0.14191 | 123.1567 | 123.0194 | 0.022888 | 123.3536 | 123.2666 | 0.24719 | -0.10986 | 122.7539 | 122.6898 | -0.38452 | 122.9324 | 122.905 | 0.21515 | -0.47607 | 123.381 | 123.2483 | 123.23 | -0.33875 | 122.9736 | 122.8821 | 122.9874 | -0.66834
1135.6875 | 123.5596 | -122.8271 | 0.52185 | -0.25565 | 0.047165 | 0.013353 | 0.0023783 | -0.024616 | -0.0069216 | 0.024253 | -0.47857 | 0.010744 | -0.030928 | -0.0058482 | 0.0071838 | 0.013132 | 0.4303 | 0.51727 | 0.38452 | 0.4303 | 0.54932 | 0.32501 | 0.16479 | 0.10529 | 0.16022 | 0.086975 | 0.13733 | 0.091553 | -0.068665 | -0.14648 | 123.1522 | 122.9919 | 0.027465 | 123.3444 | 123.2574 | 0.2655 | -0.091553 | 122.7585 | 122.6807 | -0.38452 | 122.9324 | 122.9141 | 0.23346 | -0.4303 | 123.3765 | 123.2574 | 123.2117 | -0.35706 | 122.9645 | 122.9187 | 122.9874 | -0.66833
1136.6875 | 123.5458 | -122.8409 | 0.5127 | -0.28617 | 0.070663 | 0.018693 | 0.016264 | -0.015003 | -0.015467 | 0.026389 | -0.46331 | 0.0086078 | -0.025587 | -0.015461 | -0.0013612 | 0.019541 | 0.41199 | 0.52185 | 0.39368 | 0.4303 | 0.55389 | 0.32044 | 0.17395 | 0.09613 | 0.16022 | 0.09613 | 0.15106 | 0.073242 | -0.086975 | -0.15564 | 123.1613 | 123.0148 | 0.041199 | 123.3627 | 123.2712 | 0.25635 | -0.10071 | 122.7539 | 122.6852 | -0.36163 | 122.937 | 122.937 | 0.25177 | -0.43945 | 123.3948 | 123.2529 | 123.2346 | -0.33875 | 122.9919 | 122.9141 | 123.0011 | -0.66834
1137.7031 | 123.4726 | -122.8821 | 0.55847 | -0.31669 | 0.12193 | -0.0058729 | 0.045103 | -0.034229 | 0.033666 | 0.031729 | -0.49383 | 0.010744 | -0.0074286 | 0.0059018 | 0.0071838 | 0.0013826 | 0.41199 | 0.41657 | 0.27466 | 0.39825 | 0.57678 | 0.3067 | 0.14191 | 0.032043 | 0.059509 | -0.022888 | 0.16479 | 0.09613 | -0.10986 | -0.16937 | 123.1888 | 123.024 | 0.01831 | 123.2986 | 123.2803 | 0.25635 | -0.14648 | 122.7722 | 122.7127 | -0.39368 | 122.9141 | 122.8592 | 0.14649 | -0.46234 | 123.4589 | 123.2941 | 123.1567 | -0.41656 | 123.0469 | 122.9782 | 122.9416 | -0.72784
1138.6875 | 123.5687 | -122.8043 | 0.52643 | -0.19462 | 0.067459 | 0.011217 | 0.017332 | -0.013935 | -0.018671 | 0.01998 | -0.32598 | 0.010744 | -0.018111 | -0.0015752 | -0.0013612 | 0.025949 | 0.40741 | 0.52185 | 0.3891 | 0.43488 | 0.53101 | 0.32501 | 0.17395 | 0.10071 | 0.16022 | 0.09613 | 0.13275 | 0.073242 | -0.086975 | -0.14648 | 123.1293 | 122.9782 | 0.004578 | 123.3261 | 123.2391 | 0.26093 | -0.11902 | 122.7173 | 122.6578 | -0.39368 | 122.905 | 122.9004 | 0.24261 | -0.45319 | 123.3353 | 123.2117 | 123.1934 | -0.35248 | 122.937 | 122.8775 | 122.9645 | -0.67291
1139.6875 | 123.5825 | -122.8271 | 0.52185 | -0.20987 | 0.069595 | 0.019762 | 0.026945 | -0.029956 | -0.012263 | 0.018912 | -0.47857 | -0.0020732 | -0.031996 | -0.0037112 | -0.0088382 | 0.023813 | 0.41199 | 0.51727 | 0.39368 | 0.4303 | 0.55389 | 0.31128 | 0.17395 | 0.13275 | 0.15106 | 0.11444 | 0.13733 | 0.086975 | -0.073242 | -0.14191 | 123.1384 | 123.0011 | 0.032043 | 123.3444 | 123.2574 | 0.25635 | -0.10986 | 122.7539 | 122.6852 | -0.38452 | 122.9599 | 122.9416 | 0.25635 | -0.43488 | 123.381 | 123.2391 | 123.2208 | -0.3479 | 122.9645 | 122.9141 | 122.9782 | -0.66376
1140.6875 | 123.5641 | -122.8271 | 0.52643 | -0.22513 | 0.06105 | 0.0058761 | 0.025877 | -0.02782 | -0.013331 | 0.014639 | -0.43279 | 0.0043348 | -0.027724 | -0.017597 | -0.0088382 | 0.028086 | 0.41199 | 0.5127 | 0.36621 | 0.42572 | 0.55389 | 0.31586 | 0.18768 | 0.11902 | 0.15106 | 0.10529 | 0.13733 | 0.082397 | -0.09613 | -0.14648 | 123.143 | 123.0148 | 0.027466 | 123.3398 | 123.2529 | 0.23804 | -0.11444 | 122.731 | 122.6807 | -0.3891 | 122.9462 | 122.9324 | 0.25177 | -0.44403 | 123.381 | 123.2391 | 123.1934 | -0.33875 | 122.9645 | 122.9095 | 122.9782 | -0.67291
1141.6875 | 123.555 | -122.8363 | 0.55389 | -0.3472 | 0.065323 | 0.014421 | 0.023741 | -0.018207 | -0.0015816 | 0.016776 | -0.5396 | 0.0054038 | -0.028792 | -0.0037112 | -0.0045652 | 0.025949 | 0.42114 | 0.52185 | 0.37537 | 0.42572 | 0.54932 | 0.32501 | 0.15564 | 0.10986 | 0.16479 | 0.082397 | 0.14191 | 0.064087 | -0.082397 | -0.14648 | 123.1613 | 122.9919 | -0.004578 | 123.3582 | 123.262 | 0.27008 | -0.13275 | 122.7539 | 122.6898 | -0.41199 | 122.9462 | 122.9187 | 0.22888 | -0.48981 | 123.3856 | 123.2574 | 123.2117 | -0.39825 | 122.9782 | 122.9004 | 123.0011 | -0.70038
1142.7031 | 123.4177 | -122.8729 | 0.54932 | -0.042028 | 0.11339 | -0.0058729 | 0.037626 | -0.015003 | 0.024053 | 0.029593 | -0.32598 | 0.018221 | 0.0043204 | 0.0026968 | 0.010388 | 0.0013826 | 0.3891 | 0.3891 | 0.28839 | 0.37079 | 0.57678 | 0.30212 | 0.15564 | 0 | -0.004578 | -0.073242 | 0.17853 | 0.11444 | -0.10986 | -0.17395 | 123.175 | 123.0286 | 0.027466 | 123.262 | 123.2437 | 0.21515 | -0.16022 | 122.7631 | 122.699 | -0.37079 | 122.8729 | 122.7997 | 0.10071 | -0.43488 | 123.4497 | 123.262 | 123.1613 | -0.39368 | 123.0515 | 122.9874 | 122.8683 | -0.72327
1143.6875 | 123.5596 | -122.8226 | 0.49896 | -0.30143 | 0.064255 | 0.0037401 | 0.0184 | -0.016071 | -0.018671 | 0.011435 | -0.37176 | 0.0011308 | -0.01277 | -0.0079842 | -0.0045652 | 0.033426 | 0.42572 | 0.53101 | 0.39825 | 0.4303 | 0.54474 | 0.33417 | 0.17395 | 0.11444 | 0.16479 | 0.073242 | 0.15106 | 0.082397 | -0.091553 | -0.13733 | 123.1567 | 122.9965 | 0.045777 | 123.3536 | 123.2529 | 0.25635 | -0.073242 | 122.731 | 122.6852 | -0.3479 | 122.937 | 122.8958 | 0.21057 | -0.41657 | 123.3673 | 123.2483 | 123.2208 | -0.32501 | 122.9736 | 122.905 | 122.9874 | -0.63629
1144.6875 | 123.5596 | -122.8455 | 0.52643 | -0.11832 | 0.069595 | 0.015489 | 0.024809 | -0.011798 | -0.020808 | 0.012503 | -0.47857 | 0.0096758 | -0.022383 | 0.00056082 | 0.0061158 | 0.021677 | 0.41657 | 0.53558 | 0.41199 | 0.43945 | 0.53558 | 0.30212 | 0.21057 | 0.10071 | 0.15106 | 0.10529 | 0.13733 | 0.07782 | -0.07782 | -0.14648 | 123.1476 | 123.056 | 0.009155 | 123.381 | 123.2849 | 0.22888 | -0.10986 | 122.7676 | 122.699 | -0.3891 | 122.9462 | 122.9507 | 0.25177 | -0.44861 | 123.381 | 123.262 | 123.2574 | -0.31586 | 122.9828 | 122.9233 | 122.9965 | -0.67291
1145.6875 | 123.5733 | -122.8363 | 0.53558 | -0.17936 | 0.082412 | 0.010148 | 0.010923 | -0.021411 | -0.010127 | 0.014639 | -0.43279 | -0.0010052 | -0.020247 | -0.020801 | -0.0056342 | 0.023813 | 0.41657 | 0.51727 | 0.37994 | 0.42114 | 0.54932 | 0.33417 | 0.1831 | 0.11902 | 0.16479 | 0.10986 | 0.14191 | 0.073242 | -0.068665 | -0.15564 | 123.1705 | 123.0194 | 0.013733 | 123.3536 | 123.2574 | 0.23804 | -0.11902 | 122.7676 | 122.6807 | -0.39368 | 122.9553 | 122.9462 | 0.2655 | -0.46234 | 123.3856 | 123.2529 | 123.2162 | -0.35248 | 122.9782 | 122.9095 | 123.0011 | -0.69122
1146.6875 | 123.5825 | -122.818 | 0.53101 | -0.17936 | 0.05571 | 0.013353 | 0.032286 | -0.025684 | -0.0069216 | 0.016776 | -0.37176 | 0.0021988 | -0.019179 | -0.017597 | 0.0018428 | 0.016336 | 0.41199 | 0.51727 | 0.40283 | 0.43945 | 0.54474 | 0.33417 | 0.17395 | 0.13275 | 0.16479 | 0.10986 | 0.14648 | 0.073242 | -0.07782 | -0.14191 | 123.1522 | 122.9919 | 0.013733 | 123.3353 | 123.2574 | 0.2655 | -0.11902 | 122.7402 | 122.6761 | -0.38452 | 122.9507 | 122.9279 | 0.25177 | -0.45776 | 123.3627 | 123.23 | 123.2208 | -0.35706 | 122.9645 | 122.8912 | 122.9828 | -0.67291
1147.7031 | 123.4451 | -122.8638 | 0.54474 | -0.14884 | 0.11873 | 0.0037401 | 0.033354 | -0.029956 | 0.021917 | 0.025321 | -0.50908 | 0.0086078 | -0.0042246 | -0.00050718 | 0.0050478 | 0.0056546 | 0.42114 | 0.41657 | 0.31586 | 0.37079 | 0.56305 | 0.31128 | 0.16479 | 0.050354 | 0.032043 | -0.027466 | 0.16937 | 0.11444 | -0.11444 | -0.17853 | 123.175 | 123.0286 | 0.01831 | 123.2803 | 123.2346 | 0.20599 | -0.1236 | 122.7493 | 122.6852 | -0.37537 | 122.9141 | 122.8363 | 0.15106 | -0.4303 | 123.4268 | 123.2849 | 123.1796 | -0.37994 | 123.0331 | 122.9782 | 122.8958 | -0.72327
1148.6875 | 123.5641 | -122.8226 | 0.54474 | -0.33194 | 0.052505 | 0.0026721 | -0.0018937 | -0.012866 | -0.022944 | 0.012503 | -0.47857 | 0.0054038 | -0.030928 | -0.01012 | -0.0099062 | 0.025949 | 0.41657 | 0.5127 | 0.37994 | 0.42572 | 0.54474 | 0.31586 | 0.18768 | 0.086975 | 0.17395 | 0.09613 | 0.15106 | 0.07782 | -0.082397 | -0.14191 | 123.1384 | 123.0103 | 0 | 123.3353 | 123.2483 | 0.23804 | -0.12817 | 122.7402 | 122.6807 | -0.39368 | 122.9095 | 122.9187 | 0.23804 | -0.46692 | 123.3673 | 123.2391 | 123.2025 | -0.35706 | 122.9736 | 122.9004 | 122.9965 | -0.68665
1149.6875 | 123.5504 | -122.8134 | 0.54474 | -0.20987 | 0.066391 | 0.012285 | 0.014128 | -0.022479 | -0.014399 | 0.025321 | -0.49383 | 0.0032668 | -0.021315 | -0.01012 | -0.0024292 | 0.0142 | 0.42114 | 0.55389 | 0.41199 | 0.44403 | 0.53558 | 0.32501 | 0.18768 | 0.10071 | 0.15106 | 0.091553 | 0.13733 | 0.09613 | -0.082397 | -0.14191 | 123.1384 | 123.0011 | -0.009156 | 123.3673 | 123.2574 | 0.25635 | -0.1236 | 122.731 | 122.6715 | -0.40741 | 122.9141 | 122.905 | 0.23346 | -0.44861 | 123.349 | 123.2346 | 123.2254 | -0.35706 | 122.9507 | 122.9095 | 122.9645 | -0.68665
1150.6875 | 123.555 | -122.8546 | 0.54474 | -0.22513 | 0.067459 | 0.018693 | 0.017332 | -0.02782 | -0.015467 | 0.009299 | -0.41753 | -0.0042092 | -0.014906 | -0.016529 | -0.0024292 | 0.016336 | 0.4303 | 0.54016 | 0.39825 | 0.44861 | 0.55389 | 0.32959 | 0.1831 | 0.10986 | 0.14648 | 0.086975 | 0.14648 | 0.082397 | -0.068665 | -0.14648 | 123.1842 | 123.0377 | 0.009155 | 123.3948 | 123.3032 | 0.2655 | -0.11444 | 122.7859 | 122.7081 | -0.39825 | 122.9645 | 122.9416 | 0.23346 | -0.46234 | 123.4085 | 123.2849 | 123.2529 | -0.36163 | 123.0011 | 122.937 | 123.0011 | -0.69122
1151.6875 | 123.5733 | -122.818 | 0.53101 | -0.24039 | 0.066391 | 0.011217 | 0.010923 | -0.02782 | -0.015467 | 0.005026 | -0.40227 | -0.010618 | -0.015974 | -0.01012 | -0.0067022 | 0.018473 | 0.43488 | 0.53101 | 0.38452 | 0.4303 | 0.54474 | 0.32501 | 0.1831 | 0.12817 | 0.15564 | 0.082397 | 0.14191 | 0.068665 | -0.086975 | -0.15564 | 123.143 | 123.0011 | 0.013733 | 123.349 | 123.2483 | 0.24719 | -0.096131 | 122.731 | 122.6624 | -0.3891 | 122.9462 | 122.9004 | 0.23804 | -0.46234 | 123.3627 | 123.2529 | 123.2025 | -0.3479 | 122.9599 | 122.8867 | 122.9736 | -0.68665
1152.7031 | 123.4131 | -122.8317 | 0.56763 | -0.01151 | 0.13048 | -0.0058729 | 0.021604 | -0.02782 | 0.034734 | 0.026389 | -0.31072 | 0.017153 | -0.0074286 | -0.00050718 | 0.018933 | 0.012064 | 0.37994 | 0.36621 | 0.28381 | 0.36621 | 0.57678 | 0.3067 | 0.14648 | -0.009155 | -0.027466 | -0.091553 | 0.1831 | 0.12817 | -0.10986 | -0.17853 | 123.1384 | 122.9782 | 0.009155 | 123.1979 | 123.1979 | 0.21973 | -0.18768 | 122.7219 | 122.6532 | -0.38452 | 122.8226 | 122.7402 | 0.086975 | -0.43945 | 123.4085 | 123.2117 | 123.1155 | -0.42114 | 123.0148 | 122.9599 | 122.8043 | -0.74616
1153.6875 | 123.5733 | -122.8363 | 0.52185 | -0.24039 | 0.049301 | 0.010148 | 0.032286 | -0.021411 | -0.014399 | 0.011435 | -0.31072 | 0.0075398 | -0.015974 | 0.0069698 | -0.0067022 | 0.029154 | 0.40283 | 0.48523 | 0.37994 | 0.43488 | 0.54016 | 0.32044 | 0.1831 | 0.11902 | 0.16022 | 0.10071 | 0.15564 | 0.059509 | -0.086975 | -0.15106 | 123.1567 | 123.0194 | 0.01831 | 123.3215 | 123.2712 | 0.25177 | -0.11902 | 122.7493 | 122.6852 | -0.36621 | 122.9553 | 122.937 | 0.25177 | -0.46234 | 123.3765 | 123.2391 | 123.2162 | -0.33875 | 122.9919 | 122.8958 | 122.9965 | -0.67291
1154.6875 | 123.555 | -122.8271 | 0.53101 | -0.14884 | 0.067459 | 0.018693 | 0.019468 | -0.025684 | -0.020808 | 0.015708 | -0.20391 | 0.0011308 | -0.0084976 | 0.00056082 | -0.0024292 | 0.019541 | 0.39825 | 0.50812 | 0.37537 | 0.43488 | 0.54932 | 0.33417 | 0.19226 | 0.10529 | 0.14191 | 0.07782 | 0.13733 | 0.073242 | -0.07782 | -0.13275 | 123.1613 | 123.0194 | 0.01831 | 123.3353 | 123.262 | 0.24261 | -0.13275 | 122.7493 | 122.6944 | -0.39368 | 122.9324 | 122.905 | 0.21057 | -0.45776 | 123.3765 | 123.2254 | 123.2025 | -0.33874 | 122.9645 | 122.9004 | 122.9691 | -0.66376
1155.6875 | 123.5596 | -122.8317 | 0.5127 | -0.28617 | 0.067459 | 0.0090801 | 0.021604 | -0.024616 | -0.0079896 | 0.009299 | -0.44805 | -0.0031412 | -0.021315 | -0.0015752 | 0.0029108 | 0.022745 | 0.43945 | 0.53558 | 0.40741 | 0.42572 | 0.54016 | 0.33875 | 0.18768 | 0.11444 | 0.16022 | 0.091553 | 0.13733 | 0.086975 | -0.082397 | -0.13733 | 123.1705 | 123.0194 | 0.027466 | 123.3673 | 123.2574 | 0.23804 | -0.073242 | 122.7493 | 122.6944 | -0.37537 | 122.9462 | 122.9233 | 0.22888 | -0.42572 | 123.3719 | 123.2712 | 123.2391 | -0.32501 | 122.9691 | 122.9187 | 122.9919 | -0.65002
1156.6875 | 123.555 | -122.8134 | 0.53101 | -0.39298 | 0.069595 | 0.019762 | 0.025877 | -0.020343 | -0.0090576 | 0.011435 | -0.41753 | 6.2833e-05 | -0.01277 | 0.0026968 | -0.0013612 | 0.027017 | 0.43945 | 0.54474 | 0.42572 | 0.45776 | 0.55847 | 0.32501 | 0.18768 | 0.11902 | 0.15106 | 0.09613 | 0.16022 | 0.064087 | -0.073242 | -0.14191 | 123.1384 | 123.0011 | 0.027466 | 123.3582 | 123.2712 | 0.27008 | -0.091553 | 122.7402 | 122.6715 | -0.37079 | 122.9324 | 122.9095 | 0.23804 | -0.46692 | 123.3719 | 123.2529 | 123.2391 | -0.34332 | 122.9736 | 122.8775 | 122.9645 | -0.67291
1157.7031 | 123.4451 | -122.8638 | 0.57678 | -0.37772 | 0.083481 | 0.0048081 | 0.025877 | -0.012866 | 0.018713 | 0.017844 | -0.63115 | 0.016085 | -0.027724 | -0.012256 | 0.0061158 | 0.013132 | 0.35706 | 0.39825 | 0.25177 | 0.37079 | 0.58594 | 0.29755 | 0.15106 | 0 | 0.013733 | -0.050354 | 0.20142 | 0.11902 | -0.10986 | -0.18768 | 123.1613 | 123.0148 | 0.009155 | 123.262 | 123.2346 | 0.21973 | -0.21973 | 122.7539 | 122.6761 | -0.37537 | 122.8638 | 122.8134 | 0.13733 | -0.45776 | 123.4497 | 123.2208 | 123.1155 | -0.42572 | 123.0652 | 122.9828 | 122.8775 | -0.76446
1158.6875 | 123.5779 | -122.8317 | 0.52643 | -0.026769 | 0.076004 | 0.016557 | 0.016264 | -0.019275 | -0.013331 | 0.011435 | -0.38701 | -0.0074142 | -0.02986 | -0.0047802 | -0.0088382 | 0.019541 | 0.4303 | 0.54474 | 0.39368 | 0.44861 | 0.53558 | 0.35248 | 0.1831 | 0.091553 | 0.14648 | 0.09613 | 0.16022 | 0.082397 | -0.09613 | -0.14648 | 123.1842 | 123.0148 | 0.009155 | 123.3765 | 123.2803 | 0.2655 | -0.09613 | 122.7356 | 122.6852 | -0.36621 | 122.9233 | 122.9279 | 0.24261 | -0.44403 | 123.3673 | 123.262 | 123.2254 | -0.34332 | 122.9919 | 122.9141 | 122.9782 | -0.67291
1159.6875 | 123.5825 | -122.8043 | 0.52643 | -0.072545 | 0.047165 | 0.027238 | 0.022672 | -0.013935 | -0.01974 | 0.012503 | -0.3565 | 0.0021988 | -0.043745 | -0.0026432 | -0.014179 | 0.020609 | 0.40741 | 0.56763 | 0.40741 | 0.43945 | 0.53558 | 0.33417 | 0.20142 | 0.1236 | 0.16937 | 0.086975 | 0.14191 | 0.07782 | -0.091553 | -0.15106 | 123.1384 | 123.0057 | 0.009155 | 123.3719 | 123.2437 | 0.23804 | -0.11902 | 122.7127 | 122.6532 | -0.38452 | 122.9279 | 122.8912 | 0.23804 | -0.44861 | 123.3398 | 123.2117 | 123.2117 | -0.32501 | 122.9462 | 122.8821 | 122.9736 | -0.67749
1160.6875 | 123.5916 | -122.8271 | 0.53558 | -0.13358 | 0.071731 | 0.024034 | 0.020536 | -0.013935 | -0.011195 | 0.013571 | -0.46331 | 0.0096758 | -0.011702 | -0.01012 | -0.0013612 | 0.0077906 | 0.4303 | 0.53558 | 0.39825 | 0.4303 | 0.54932 | 0.33417 | 0.19226 | 0.11902 | 0.15564 | 0.09613 | 0.14648 | 0.068665 | -0.091553 | -0.14648 | 123.1613 | 123.0194 | 0.013733 | 123.3627 | 123.2574 | 0.23804 | -0.10529 | 122.7356 | 122.6807 | -0.3891 | 122.9462 | 122.9233 | 0.24261 | -0.46692 | 123.3765 | 123.2574 | 123.2254 | -0.34332 | 122.9736 | 122.8958 | 122.9828 | -0.68207
1161.6875 | 123.5641 | -122.818 | 0.54474 | -0.39298 | 0.071731 | 0.019762 | 0.0184 | -0.029956 | -0.0079896 | 0.014639 | -0.6159 | -0.0031412 | -0.0074286 | -0.0069162 | 0.0050478 | 0.019541 | 0.4303 | 0.52643 | 0.39368 | 0.44861 | 0.54932 | 0.33417 | 0.19226 | 0.10529 | 0.15106 | 0.082397 | 0.14191 | 0.064087 | -0.073242 | -0.16022 | 123.1522 | 123.0103 | 0.004577 | 123.3444 | 123.2666 | 0.25635 | -0.11444 | 122.7448 | 122.6578 | -0.40283 | 122.9233 | 122.9004 | 0.24261 | -0.48065 | 123.3673 | 123.2483 | 123.2117 | -0.35248 | 122.9599 | 122.8821 | 122.9691 | -0.70496
1162.6875 | 123.5458 | -122.8363 | 0.54016 | -0.25565 | 0.079208 | 0.021898 | 0.016264 | -0.025684 | -0.0090576 | 0.018912 | -0.49383 | -0.0042092 | -0.033064 | 0.0048338 | 0.0082518 | 0.021677 | 0.42114 | 0.54016 | 0.41199 | 0.44403 | 0.55389 | 0.32959 | 0.20599 | 0.10071 | 0.16479 | 0.068665 | 0.12817 | 0.082397 | -0.086975 | -0.16479 | 123.1659 | 123.0423 | 0.013733 | 123.3765 | 123.2803 | 0.23804 | -0.11902 | 122.7493 | 122.6715 | -0.41199 | 122.937 | 122.905 | 0.23346 | -0.45776 | 123.3902 | 123.2574 | 123.2483 | -0.33417 | 122.9645 | 122.9187 | 123.0011 | -0.70496
1163.6875 | 123.5596 | -122.8271 | 0.53558 | -0.30143 | 0.073868 | 0.019762 | 0.0184 | -0.022479 | -0.01974 | 0.009299 | -0.52434 | 0.0032668 | -0.036268 | -0.0037112 | -0.0056342 | 0.020609 | 0.43945 | 0.51727 | 0.39825 | 0.4303 | 0.55847 | 0.32501 | 0.17395 | 0.09613 | 0.16937 | 0.091553 | 0.14191 | 0.086975 | -0.086975 | -0.13275 | 123.1522 | 123.0011 | 0.022889 | 123.3444 | 123.2574 | 0.25635 | -0.09613 | 122.7402 | 122.6944 | -0.39368 | 122.9233 | 122.9187 | 0.2243 | -0.44861 | 123.3856 | 123.2666 | 123.2254 | -0.36163 | 122.9691 | 122.9141 | 122.9965 | -0.66833
1164.6875 | 123.555 | -122.8134 | 0.54016 | -0.4235 | 0.072799 | 0.0090801 | 0.016264 | -0.026752 | -0.0090576 | 0.010367 | -0.55486 | -0.0095502 | -0.027724 | 0.0091058 | 0.0007748 | 0.017404 | 0.44861 | 0.53101 | 0.39368 | 0.45319 | 0.54474 | 0.33417 | 0.19684 | 0.09613 | 0.15564 | 0.073242 | 0.15564 | 0.10071 | -0.07782 | -0.15564 | 123.1476 | 123.0103 | 0.004578 | 123.3444 | 123.2666 | 0.25635 | -0.091553 | 122.7356 | 122.6578 | -0.38452 | 122.9095 | 122.8867 | 0.22888 | -0.43945 | 123.3582 | 123.262 | 123.2071 | -0.34332 | 122.9691 | 122.9141 | 122.9691 | -0.6958
1165.6875 | 123.5596 | -122.8455 | 0.52643 | -0.33194 | 0.065323 | 0.019762 | 0.014128 | -0.025684 | -0.0079896 | 0.014639 | -0.47857 | -0.0052782 | -0.027724 | -0.0090522 | 0.0029108 | 0.0024506 | 0.45776 | 0.55389 | 0.42114 | 0.4715 | 0.54016 | 0.35706 | 0.19226 | 0.10529 | 0.15106 | 0.082397 | 0.13733 | 0.09613 | -0.07782 | -0.14648 | 123.2025 | 123.0377 | 0.013733 | 123.3994 | 123.317 | 0.27924 | -0.068664 | 122.7676 | 122.699 | -0.3891 | 122.9507 | 122.9279 | 0.22888 | -0.4303 | 123.3856 | 123.3032 | 123.2666 | -0.33417 | 122.9828 | 122.9416 | 122.9965 | -0.67291
1166.6875 | 123.5321 | -122.8363 | 0.54932 | -0.40824 | 0.094162 | 0.017625 | 0.015196 | -0.015003 | -0.0058536 | 0.016776 | -0.46331 | 0.0043348 | -0.020247 | -0.0079842 | 0.0039788 | 0.0088586 | 0.44403 | 0.50812 | 0.39825 | 0.43945 | 0.54474 | 0.33417 | 0.18768 | 0.073242 | 0.12817 | 0.059509 | 0.15106 | 0.086975 | -0.091553 | -0.16022 | 123.1705 | 123.024 | -0.004577 | 123.3444 | 123.2758 | 0.25177 | -0.10529 | 122.7448 | 122.6761 | -0.39825 | 122.9095 | 122.8958 | 0.21973 | -0.46234 | 123.381 | 123.2803 | 123.2346 | -0.36163 | 122.9874 | 122.9233 | 122.9645 | -0.70953
1167.6875 | 123.5779 | -122.8226 | 0.54016 | -0.11832 | 0.062118 | 0.015489 | 0.0184 | -0.029956 | -0.011195 | 0.014639 | -0.43279 | 0.0021988 | -0.026655 | -0.0058482 | -0.0077702 | 0.033426 | 0.44403 | 0.56763 | 0.39825 | 0.46234 | 0.54932 | 0.33417 | 0.21515 | 0.10529 | 0.14191 | 0.091553 | 0.14191 | 0.082397 | -0.068665 | -0.15564 | 123.1567 | 123.0377 | 0.009155 | 123.3902 | 123.2849 | 0.24719 | -0.09613 | 122.7539 | 122.6669 | -0.39825 | 122.9279 | 122.9141 | 0.24719 | -0.45776 | 123.3719 | 123.2666 | 123.2208 | -0.32501 | 122.9645 | 122.905 | 122.9645 | -0.6958
1168.6875 | 123.5413 | -122.8088 | 0.54474 | -0.39298 | 0.076004 | 0.012285 | 0.0098553 | -0.018207 | -0.014399 | 0.022116 | -0.46331 | 0.010744 | -0.020247 | -0.00050718 | 0.0050478 | 0.012064 | 0.44403 | 0.51727 | 0.40741 | 0.45776 | 0.53558 | 0.32959 | 0.1831 | 0.091553 | 0.15564 | 0.059509 | 0.14648 | 0.091553 | -0.082397 | -0.15106 | 123.1384 | 122.9919 | -0.009156 | 123.3261 | 123.2666 | 0.27466 | -0.10071 | 122.7264 | 122.6578 | -0.39825 | 122.9004 | 122.8683 | 0.21057 | -0.45319 | 123.3444 | 123.2529 | 123.2162 | -0.36163 | 122.9553 | 122.9004 | 122.9645 | -0.6958
1169.6875 | 123.5641 | -122.8271 | 0.55389 | -0.43876 | 0.076004 | 0.018693 | 0.029081 | -0.016071 | -0.0026496 | 0.018912 | -0.52434 | 0.0011308 | -0.020247 | -0.019733 | 0.0061158 | 0.017404 | 0.4303 | 0.54474 | 0.41199 | 0.46692 | 0.55847 | 0.33417 | 0.1831 | 0.10529 | 0.15564 | 0.082397 | 0.16937 | 0.091553 | -0.07782 | -0.16022 | 123.1613 | 123.0103 | 0.004578 | 123.3719 | 123.2941 | 0.28381 | -0.1236 | 122.7493 | 122.6669 | -0.38452 | 122.9324 | 122.9095 | 0.24261 | -0.46234 | 123.3856 | 123.2574 | 123.2391 | -0.37079 | 122.9965 | 122.9187 | 122.9828 | -0.71411
1170.6875 | 123.5504 | -122.8271 | 0.55847 | -0.31669 | 0.066391 | 0.0090801 | 0.0184 | -0.025684 | -0.0079896 | 0.014639 | -0.55486 | -0.0042092 | -0.014906 | -0.022937 | 0.0082518 | 0.018473 | 0.43488 | 0.54474 | 0.42114 | 0.45319 | 0.54932 | 0.34332 | 0.19684 | 0.086975 | 0.14648 | 0.073242 | 0.13733 | 0.086975 | -0.10071 | -0.14648 | 123.1705 | 123.024 | -0.009156 | 123.3719 | 123.2803 | 0.25635 | -0.1236 | 122.7264 | 122.6807 | -0.42114 | 122.9141 | 122.9004 | 0.21973 | -0.4715 | 123.3765 | 123.262 | 123.2483 | -0.36163 | 122.9645 | 122.9141 | 122.9736 | -0.70496
1171.6875 | 123.5596 | -122.8363 | 0.53558 | -0.25565 | 0.067459 | 0.015489 | 0.026945 | -0.015003 | -0.0037176 | 0.017844 | -0.5396 | 0.0086078 | -0.017042 | -0.0037112 | 0.0093198 | 0.018473 | 0.43945 | 0.53558 | 0.41199 | 0.45776 | 0.56305 | 0.33875 | 0.20142 | 0.09613 | 0.16479 | 0.086975 | 0.15564 | 0.091553 | -0.086975 | -0.13733 | 123.175 | 123.0377 | 0.027466 | 123.3719 | 123.2941 | 0.25635 | -0.09613 | 122.7493 | 122.699 | -0.37994 | 122.9324 | 122.9233 | 0.2243 | -0.44403 | 123.3994 | 123.2758 | 123.2483 | -0.33417 | 122.9919 | 122.9279 | 123.0011 | -0.67291
1172.6875 | 123.5825 | -122.8455 | 0.54016 | -0.22513 | 0.063186 | 0.0069441 | 0.015196 | -0.029956 | -0.0026496 | 0.013571 | -0.41753 | -0.0010052 | -0.017042 | -0.011188 | 0.0018428 | 0.017404 | 0.45776 | 0.58136 | 0.42114 | 0.45776 | 0.55847 | 0.33875 | 0.19684 | 0.11902 | 0.15564 | 0.086975 | 0.16022 | 0.068665 | -0.09613 | -0.14191 | 123.1842 | 123.0423 | 0.018311 | 123.4268 | 123.3032 | 0.26093 | -0.082397 | 122.7493 | 122.7036 | -0.37994 | 122.9645 | 122.9324 | 0.22888 | -0.4715 | 123.4039 | 123.3032 | 123.2666 | -0.34332 | 123.0057 | 122.9141 | 123.0011 | -0.68207
1173.6875 | 123.5733 | -122.8088 | 0.54932 | -0.042028 | 0.074936 | 0.021898 | 0.028013 | -0.032093 | -0.010127 | 0.024253 | -0.3565 | -0.0020732 | -0.024519 | -0.0079842 | -0.0045652 | 0.029154 | 0.41199 | 0.49439 | 0.3891 | 0.42114 | 0.5722 | 0.35248 | 0.19226 | 0.09613 | 0.10529 | 0.086975 | 0.17395 | 0.086975 | -0.082397 | -0.15564 | 123.1613 | 123.0011 | 0.022889 | 123.3032 | 123.23 | 0.22888 | -0.13733 | 122.7264 | 122.6532 | -0.37537 | 122.905 | 122.8958 | 0.24261 | -0.46234 | 123.381 | 123.2208 | 123.1979 | -0.35706 | 122.9828 | 122.8958 | 122.9141 | -0.70496
1174.6875 | 123.5779 | -122.8363 | 0.56305 | -0.1641 | 0.063186 | 0.017625 | 0.024809 | -0.028888 | -0.011195 | 0.005026 | -0.34124 | 0.0021988 | -0.025587 | -0.0037112 | -0.0056342 | 0.021677 | 0.45319 | 0.54016 | 0.40283 | 0.45319 | 0.55847 | 0.35706 | 0.20599 | 0.12817 | 0.16937 | 0.07782 | 0.14191 | 0.09613 | -0.073242 | -0.14191 | 123.1934 | 123.0423 | -0.004577 | 123.3765 | 123.2895 | 0.24719 | -0.10986 | 122.7631 | 122.6944 | -0.42114 | 122.9645 | 122.9141 | 0.21973 | -0.46692 | 123.3948 | 123.2895 | 123.2391 | -0.35706 | 122.9782 | 122.9324 | 123.0057 | -0.70496
1175.6875 | 123.5596 | -122.8363 | 0.54474 | -0.33194 | 0.048233 | 0.017625 | 0.015196 | -0.01073 | -0.0026496 | 0.013571 | -0.50908 | -0.0052782 | -0.027724 | -0.0015752 | -0.0002932 | 0.017404 | 0.45319 | 0.55389 | 0.41199 | 0.45319 | 0.56763 | 0.34332 | 0.18768 | 0.09613 | 0.14191 | 0.064087 | 0.13733 | 0.082397 | -0.07782 | -0.16479 | 123.1796 | 123.024 | 0.022888 | 123.3902 | 123.2895 | 0.2655 | -0.091553 | 122.7585 | 122.6715 | -0.40741 | 122.9324 | 122.9004 | 0.22888 | -0.46234 | 123.4039 | 123.2895 | 123.2483 | -0.35706 | 122.9736 | 122.9187 | 122.9782 | -0.70953
1176.6875 | 123.5458 | -122.8088 | 0.53558 | -0.28617 | 0.084549 | 0.0080121 | 0.019468 | -0.024616 | 0.00055539 | 0.015708 | -0.43279 | -0.0010052 | -0.022383 | -0.015461 | -0.0013612 | 0.010996 | 0.45319 | 0.54932 | 0.40741 | 0.45776 | 0.55389 | 0.35706 | 0.19226 | 0.11444 | 0.16937 | 0.091553 | 0.16022 | 0.07782 | -0.07782 | -0.15106 | 123.1659 | 123.0011 | 0.018311 | 123.3582 | 123.2666 | 0.2655 | -0.082397 | 122.731 | 122.6578 | -0.37537 | 122.9233 | 122.9004 | 0.24261 | -0.45776 | 123.3627 | 123.262 | 123.2162 | -0.34332 | 122.9691 | 122.8867 | 122.9782 | -0.68665
1177.6875 | 123.5825 | -122.8271 | 0.54474 | -0.37772 | 0.058914 | 0.0058761 | 0.022672 | -0.021411 | 0.0048274 | 0.016776 | -0.52434 | 0.0054038 | -0.034132 | -0.01012 | 0.0018428 | 0.0088586 | 0.4715 | 0.57678 | 0.4303 | 0.46234 | 0.55847 | 0.35248 | 0.21515 | 0.10071 | 0.15564 | 0.082397 | 0.14191 | 0.068665 | -0.059509 | -0.13733 | 123.1796 | 123.0423 | 0.013733 | 123.4039 | 123.2895 | 0.24719 | -0.073242 | 122.7676 | 122.6898 | -0.40283 | 122.9279 | 122.9095 | 0.21973 | -0.47607 | 123.3856 | 123.2986 | 123.2574 | -0.32959 | 122.9691 | 122.8958 | 122.9828 | -0.68207
1178.6875 | 123.5641 | -122.8226 | 0.54474 | -0.4235 | 0.070663 | 0.010148 | 0.019468 | -0.033161 | -0.0047856 | 0.014639 | -0.40227 | 0.0032668 | -0.039473 | 0.0048338 | 0.0050478 | 0.020609 | 0.48065 | 0.54474 | 0.42114 | 0.45776 | 0.5722 | 0.34332 | 0.21973 | 0.1236 | 0.15564 | 0.073242 | 0.13275 | 0.073242 | -0.07782 | -0.13733 | 123.1659 | 123.0423 | 0.027466 | 123.3673 | 123.2803 | 0.23804 | -0.064087 | 122.7448 | 122.6852 | -0.41199 | 122.9462 | 122.8958 | 0.21057 | -0.4715 | 123.3948 | 123.3032 | 123.2437 | -0.32501 | 122.9553 | 122.8958 | 122.9782 | -0.68207
1179.6875 | 123.5916 | -122.8043 | 0.54474 | -0.1641 | 0.083481 | 0.0090801 | 0.028013 | -0.019275 | -0.0069216 | 0.017844 | -0.43279 | 0.0064718 | -0.0052926 | 0.0048338 | -0.0013612 | 0.017404 | 0.43945 | 0.58136 | 0.41657 | 0.43945 | 0.55847 | 0.35248 | 0.20599 | 0.15106 | 0.16479 | 0.11444 | 0.15106 | 0.082397 | -0.082397 | -0.14191 | 123.1567 | 123.0103 | 0.013733 | 123.3856 | 123.2437 | 0.23346 | -0.10529 | 122.7219 | 122.6624 | -0.39368 | 122.9553 | 122.9187 | 0.25635 | -0.46234 | 123.3627 | 123.2437 | 123.2208 | -0.33874 | 122.9553 | 122.8867 | 122.9691 | -0.68665
1180.6875 | 123.5733 | -122.8043 | 0.55847 | -0.10306 | 0.068527 | 0.024034 | 0.016264 | -0.028888 | -0.013331 | 0.016776 | -0.64641 | 6.2833e-05 | -0.022383 | 0.00056082 | 0.0061158 | 0.024881 | 0.46692 | 0.52185 | 0.41199 | 0.46234 | 0.5722 | 0.34332 | 0.19226 | 0.12817 | 0.16479 | 0.09613 | 0.14191 | 0.07782 | -0.082397 | -0.13733 | 123.1476 | 122.9965 | 0.013733 | 123.3261 | 123.2666 | 0.27008 | -0.091553 | 122.7219 | 122.6669 | -0.41656 | 122.9324 | 122.9004 | 0.23346 | -0.48065 | 123.3765 | 123.2712 | 123.2162 | -0.36621 | 122.9462 | 122.8821 | 122.9691 | -0.6958
1181.6875 | 123.5779 | -122.818 | 0.54932 | -0.28617 | 0.050369 | 0.018693 | 0.021604 | -0.0043222 | -0.0037176 | 0.014639 | -0.32598 | 0.0064718 | -0.015974 | 0.0080378 | -0.0002932 | 0.019541 | 0.46234 | 0.54016 | 0.41657 | 0.45319 | 0.58136 | 0.35248 | 0.20599 | 0.12817 | 0.15106 | 0.09613 | 0.14648 | 0.086975 | -0.082397 | -0.16022 | 123.1705 | 123.024 | 0.032044 | 123.3582 | 123.2712 | 0.24719 | -0.086975 | 122.7356 | 122.6578 | -0.40283 | 122.9462 | 122.9141 | 0.25635 | -0.46234 | 123.3994 | 123.2803 | 123.2346 | -0.34332 | 122.9645 | 122.905 | 122.9691 | -0.70953
1182.6875 | 123.5779 | -122.8271 | 0.54932 | -0.30143 | 0.07814 | 0.021898 | 0.031217 | -0.017139 | -0.0058536 | 0.018912 | -0.57012 | -0.0020732 | -0.021315 | -0.0015752 | -0.0045652 | 0.017404 | 0.48523 | 0.56763 | 0.4303 | 0.47607 | 0.58136 | 0.35706 | 0.21057 | 0.11444 | 0.15106 | 0.086975 | 0.14191 | 0.082397 | -0.082397 | -0.14648 | 123.1842 | 123.0377 | 0.032044 | 123.3948 | 123.3032 | 0.2655 | -0.064087 | 122.7448 | 122.6807 | -0.40741 | 122.9416 | 122.9141 | 0.23346 | -0.46692 | 123.4085 | 123.3124 | 123.2574 | -0.33875 | 122.9691 | 122.9095 | 122.9782 | -0.6958
1183.6875 | 123.5687 | -122.8043 | 0.55389 | -0.1641 | 0.076004 | 0.018693 | 0.010923 | -0.015003 | 0.0069634 | 0.016776 | -0.37176 | -0.0031412 | -0.0352 | 0.0059018 | 0.0018428 | 0.018473 | 0.48523 | 0.56763 | 0.43488 | 0.48981 | 0.5722 | 0.3479 | 0.19684 | 0.11902 | 0.14191 | 0.091553 | 0.13275 | 0.091553 | -0.082397 | -0.14648 | 123.1522 | 123.0011 | 0.018311 | 123.3719 | 123.2941 | 0.29297 | -0.068665 | 122.7219 | 122.6578 | -0.42114 | 122.9233 | 122.8958 | 0.23804 | -0.46234 | 123.3765 | 123.2895 | 123.2391 | -0.35706 | 122.937 | 122.8958 | 122.9462 | -0.70038
1184.6875 | 123.587 | -122.7951 | 0.55389 | -0.087804 | 0.073868 | 0.019762 | 0.016264 | -0.036365 | -0.0069216 | 0.008231 | -0.40227 | -0.0031412 | -0.022383 | 0.00056082 | 0.011456 | 0.018473 | 0.4715 | 0.56763 | 0.43488 | 0.4715 | 0.56305 | 0.34332 | 0.21515 | 0.11444 | 0.15106 | 0.082397 | 0.13733 | 0.091553 | -0.09613 | -0.14191 | 123.1384 | 123.0103 | 0.009155 | 123.3627 | 123.2666 | 0.25635 | -0.082397 | 122.699 | 122.6532 | -0.41656 | 122.9095 | 122.8775 | 0.2243 | -0.46234 | 123.3582 | 123.2666 | 123.23 | -0.33874 | 122.9324 | 122.8867 | 122.9462 | -0.6958
1185.6875 | 123.587 | -122.7951 | 0.56763 | -0.13358 | 0.039688 | 0.014421 | 0.019468 | -0.024616 | 0.0037594 | 0.024253 | -0.44805 | -0.0074142 | -0.031996 | -0.021869 | -0.0013612 | 0.019541 | 0.47607 | 0.55389 | 0.41657 | 0.46692 | 0.58594 | 0.35706 | 0.22888 | 0.1236 | 0.16479 | 0.10071 | 0.14191 | 0.091553 | -0.09613 | -0.14648 | 123.1522 | 123.024 | 0.01831 | 123.349 | 123.262 | 0.23804 | -0.091553 | 122.699 | 122.6486 | -0.42572 | 122.9187 | 122.8958 | 0.24719 | -0.47607 | 123.381 | 123.2712 | 123.2117 | -0.33874 | 122.937 | 122.8867 | 122.9599 | -0.71411
1186.6875 | 123.5779 | -122.8134 | 0.55389 | -0.1641 | 0.058914 | 0.012285 | 0.024809 | -0.02782 | -0.0090576 | 0.022116 | -0.66167 | 0.010744 | -0.017042 | -0.0047802 | -0.0024292 | 0.022745 | 0.46234 | 0.53558 | 0.40741 | 0.46692 | 0.59967 | 0.35706 | 0.19226 | 0.13733 | 0.15564 | 0.10071 | 0.13733 | 0.091553 | -0.082397 | -0.16479 | 123.1705 | 123.0057 | 0.045776 | 123.349 | 123.2803 | 0.27466 | -0.091553 | 122.731 | 122.6486 | -0.41656 | 122.9507 | 122.9141 | 0.2655 | -0.46234 | 123.4131 | 123.2758 | 123.2208 | -0.36163 | 122.9507 | 122.905 | 122.9691 | -0.71869
1187.6875 | 123.5779 | -122.8134 | 0.5722 | -0.042028 | 0.050369 | 0.0048081 | 0.017332 | -0.024616 | -0.0047856 | 0.033866 | -0.34124 | 0.0086078 | -0.01277 | -0.011188 | 0.011456 | 0.018473 | 0.45319 | 0.53101 | 0.41657 | 0.45776 | 0.58594 | 0.35248 | 0.2243 | 0.09613 | 0.16937 | 0.091553 | 0.13275 | 0.07782 | -0.09613 | -0.16479 | 123.1659 | 123.0377 | 0.013732 | 123.3444 | 123.2712 | 0.23346 | -0.11902 | 122.7173 | 122.6486 | -0.43945 | 122.9095 | 122.905 | 0.25635 | -0.49438 | 123.3994 | 123.2666 | 123.23 | -0.3479 | 122.9462 | 122.8912 | 122.9828 | -0.737
1188.6875 | 123.5916 | -122.8043 | 0.56763 | -0.10306 | 0.074936 | 0.014421 | 0.036558 | -0.023548 | 0.0037594 | 0.023184 | -0.2802 | 6.2833e-05 | -0.019179 | -0.0015752 | 0.0061158 | 0.020609 | 0.44861 | 0.52643 | 0.40283 | 0.46234 | 0.58594 | 0.3479 | 0.21973 | 0.1236 | 0.1236 | 0.07782 | 0.13733 | 0.068665 | -0.091553 | -0.14191 | 123.1522 | 123.024 | 0.01831 | 123.3307 | 123.2666 | 0.24261 | -0.11902 | 122.7127 | 122.6624 | -0.4303 | 122.9279 | 122.8821 | 0.21973 | -0.49896 | 123.3902 | 123.2529 | 123.2071 | -0.3479 | 122.9416 | 122.8729 | 122.9279 | -0.70953
1189.6875 | 123.5596 | -122.8088 | 0.56763 | -0.24039 | 0.069595 | 0.013353 | 0.026945 | -0.026752 | 0.00055539 | 0.018912 | -0.46331 | 0.0075398 | -0.019179 | -0.0015752 | 0.0071838 | 0.017404 | 0.49439 | 0.58136 | 0.44403 | 0.47607 | 0.58594 | 0.35248 | 0.2243 | 0.11902 | 0.15564 | 0.082397 | 0.1236 | 0.07782 | -0.07782 | -0.16022 | 123.1613 | 123.0331 | 0.01831 | 123.3902 | 123.2849 | 0.25177 | -0.073242 | 122.731 | 122.6486 | -0.44403 | 122.9279 | 122.8912 | 0.24261 | -0.48981 | 123.3948 | 123.3032 | 123.2529 | -0.34332 | 122.9324 | 122.8867 | 122.9645 | -0.72784
1190.6875 | 123.5779 | -122.8043 | 0.5722 | -0.14884 | 0.086685 | 0.011217 | 0.017332 | -0.023548 | -0.010127 | 0.012503 | -0.43279 | 0.0011308 | -0.021315 | -0.011188 | -0.0024292 | 0.010996 | 0.48981 | 0.55847 | 0.44403 | 0.48065 | 0.59052 | 0.37994 | 0.22888 | 0.11444 | 0.16937 | 0.073242 | 0.15564 | 0.082397 | -0.073242 | -0.15106 | 123.1842 | 123.0331 | 0.01831 | 123.3627 | 123.2849 | 0.25177 | -0.082398 | 122.731 | 122.6532 | -0.41656 | 122.9187 | 122.8775 | 0.2243 | -0.48981 | 123.3948 | 123.2941 | 123.2483 | -0.34332 | 122.9599 | 122.8867 | 122.9736 | -0.72327
1191.6875 | 123.6008 | -122.7997 | 0.55847 | -0.25565 | 0.085617 | 0.016557 | 0.013059 | -0.02782 | 0.0058954 | 0.026389 | -0.44805 | -0.0010052 | -0.022383 | -0.0079842 | 0.0029108 | 0.015268 | 0.45776 | 0.59967 | 0.43945 | 0.4715 | 0.56763 | 0.37079 | 0.21973 | 0.11902 | 0.17395 | 0.11444 | 0.13275 | 0.07782 | -0.09613 | -0.14191 | 123.1705 | 123.0194 | 0.009155 | 123.3994 | 123.2712 | 0.25177 | -0.10071 | 122.7036 | 122.6578 | -0.42572 | 122.9187 | 122.9141 | 0.25635 | -0.48065 | 123.3673 | 123.2574 | 123.2391 | -0.33874 | 122.9324 | 122.8775 | 122.9736 | -0.70038
1192.6875 | 123.5504 | -122.8043 | 0.5722 | -0.33194 | 0.077072 | 0.014421 | 0.024809 | -0.022479 | -0.0058536 | 0.023184 | -0.55486 | 6.2833e-05 | -0.022383 | -0.0079842 | 0.0029108 | 0.013132 | 0.4715 | 0.57678 | 0.43945 | 0.47607 | 0.59052 | 0.37537 | 0.22888 | 0.10071 | 0.14191 | 0.073242 | 0.13275 | 0.07782 | -0.086975 | -0.14191 | 123.1796 | 123.0331 | 0.01831 | 123.381 | 123.2803 | 0.24719 | -0.10071 | 122.7173 | 122.6624 | -0.43945 | 122.905 | 122.8775 | 0.21515 | -0.49438 | 123.3948 | 123.2758 | 123.2437 | -0.34332 | 122.937 | 122.8821 | 122.9462 | -0.71411
1193.6875 | 123.6099 | -122.8088 | 0.57678 | -0.22513 | 0.07814 | 0.0048081 | 0.020536 | -0.025684 | -0.011195 | 0.025321 | -0.14287 | -0.0042092 | -0.015974 | 0.00056082 | -0.0067022 | 0.013132 | 0.45776 | 0.55847 | 0.42572 | 0.47607 | 0.58594 | 0.3479 | 0.21973 | 0.12817 | 0.14648 | 0.10529 | 0.14648 | 0.068665 | -0.09613 | -0.13733 | 123.1567 | 123.0286 | 0.009155 | 123.3673 | 123.2849 | 0.25635 | -0.11902 | 122.7127 | 122.6715 | -0.4303 | 122.937 | 122.9141 | 0.24262 | -0.50812 | 123.3948 | 123.2666 | 123.2346 | -0.35706 | 122.9553 | 122.8775 | 122.9553 | -0.71411
1194.6875 | 123.5596 | -122.7997 | 0.54474 | -0.13358 | 0.081344 | 0.012285 | -0.0061667 | -0.034229 | -0.0058536 | 0.01998 | -0.29546 | -0.0042092 | -0.027724 | 0.0016288 | 0.0071838 | 0.017404 | 0.45776 | 0.54016 | 0.41199 | 0.47607 | 0.60883 | 0.37994 | 0.2243 | 0.10071 | 0.15564 | 0.11444 | 0.16022 | 0.068665 | -0.082397 | -0.14191 | 123.1796 | 123.024 | 0.064087 | 123.3398 | 123.2758 | 0.25177 | -0.086975 | 122.7173 | 122.6578 | -0.38452 | 122.9004 | 122.9141 | 0.25635 | -0.47607 | 123.4085 | 123.2574 | 123.2117 | -0.32043 | 122.9599 | 122.8683 | 122.9553 | -0.68665
1195.6875 | 123.5916 | -122.8226 | 0.56763 | -0.026769 | 0.062118 | 0.011217 | 0.0087873 | -0.038501 | -0.0069216 | 0.015708 | -0.24969 | 0.0054038 | -0.020247 | -0.013324 | -0.0013612 | 0.019541 | 0.45776 | 0.54474 | 0.40741 | 0.45776 | 0.60425 | 0.37994 | 0.2243 | 0.1236 | 0.1236 | 0.068665 | 0.14191 | 0.068665 | -0.073242 | -0.15106 | 123.2025 | 123.0469 | 0.036621 | 123.3673 | 123.2803 | 0.23346 | -0.10986 | 122.7493 | 122.6715 | -0.42572 | 122.9462 | 122.8912 | 0.21973 | -0.49896 | 123.4268 | 123.2803 | 123.23 | -0.34332 | 122.9645 | 122.8912 | 122.9462 | -0.71869
1196.6875 | 123.5733 | -122.8088 | 0.56763 | -0.25565 | 0.080276 | 0.017625 | 0.023741 | -0.034229 | 0.0016234 | 0.008231 | -0.44805 | 0.0054038 | -0.025587 | -0.0037112 | -0.0067022 | 0.013132 | 0.49439 | 0.59052 | 0.44861 | 0.48065 | 0.59052 | 0.36621 | 0.21515 | 0.10986 | 0.15564 | 0.082397 | 0.14648 | 0.059509 | -0.091553 | -0.15564 | 123.175 | 123.024 | 0.022888 | 123.3994 | 123.2895 | 0.2655 | -0.073242 | 122.7173 | 122.6532 | -0.42114 | 122.9187 | 122.8912 | 0.23804 | -0.50812 | 123.3994 | 123.3032 | 123.2574 | -0.35248 | 122.9553 | 122.8683 | 122.9645 | -0.72327
1197.6875 | 123.5733 | -122.7859 | 0.58136 | -0.3472 | 0.067459 | 0.022966 | 0.034422 | -0.02782 | -0.0069216 | 0.01998 | -0.41753 | -0.013823 | -0.024519 | -0.0069162 | -0.0002932 | 0.0077906 | 0.50354 | 0.60425 | 0.4715 | 0.49439 | 0.57678 | 0.38452 | 0.21515 | 0.10986 | 0.15106 | 0.091553 | 0.14648 | 0.059509 | -0.086975 | -0.13733 | 123.1705 | 123.0011 | -0.004578 | 123.3902 | 123.2803 | 0.27924 | -0.07782 | 122.699 | 122.6486 | -0.43488 | 122.8958 | 122.8775 | 0.22888 | -0.52185 | 123.3627 | 123.2895 | 123.2574 | -0.36621 | 122.9324 | 122.8455 | 122.937 | -0.71869
1198.6875 | 123.5962 | -122.7997 | 0.57678 | -0.45401 | 0.081344 | 0.02617 | 0.024809 | -0.025684 | -0.0079896 | 0.018912 | -0.49383 | -0.0042092 | -0.027724 | -0.014393 | -0.0002932 | 0.0088586 | 0.49439 | 0.59052 | 0.46234 | 0.48523 | 0.59509 | 0.38452 | 0.23346 | 0.10071 | 0.15106 | 0.086975 | 0.13733 | 0.073242 | -0.068665 | -0.15106 | 123.1842 | 123.0331 | 0.018311 | 123.3902 | 123.2849 | 0.25177 | -0.082397 | 122.731 | 122.6486 | -0.43945 | 122.9004 | 122.8867 | 0.23804 | -0.50354 | 123.3948 | 123.2941 | 123.262 | -0.34332 | 122.937 | 122.8729 | 122.9507 | -0.72784
1199.6875 | 123.5733 | -122.7951 | 0.5722 | -0.057287 | 0.083481 | 0.010148 | 0.017332 | -0.015003 | -0.0058536 | 0.010367 | -0.44805 | -0.0010052 | -0.023451 | -0.017597 | 0.0018428 | 0.0142 | 0.48981 | 0.60425 | 0.44403 | 0.49439 | 0.5722 | 0.37537 | 0.2243 | 0.10529 | 0.15106 | 0.10071 | 0.12817 | 0.073242 | -0.09613 | -0.15106 | 123.1705 | 123.0194 | 0 | 123.3994 | 123.2895 | 0.27008 | -0.082398 | 122.699 | 122.644 | -0.44403 | 122.9004 | 122.8958 | 0.25177 | -0.49896 | 123.3673 | 123.2849 | 123.2391 | -0.3479 | 122.9233 | 122.8683 | 122.9462 | -0.72327
1200.6875 | 123.5779 | -122.8134 | 0.56763 | -0.19462 | 0.058914 | 0.011217 | 0.014128 | -0.026752 | 0.00055539 | 0.023184 | -0.29546 | 0.0054038 | -0.027724 | -0.0037112 | 0.0050478 | 0.015268 | 0.46234 | 0.62714 | 0.45776 | 0.49439 | 0.59509 | 0.37079 | 0.2243 | 0.14191 | 0.16022 | 0.091553 | 0.14648 | 0.086975 | -0.073242 | -0.15564 | 123.1842 | 123.0377 | 0.027466 | 123.4406 | 123.3078 | 0.27008 | -0.10529 | 122.7402 | 122.6578 | -0.42114 | 122.9553 | 122.905 | 0.24719 | -0.48065 | 123.4085 | 123.2758 | 123.2712 | -0.34332 | 122.9599 | 122.9004 | 122.9736 | -0.72327
1201.6875 | 123.5825 | -122.7722 | 0.5722 | -0.17936 | 0.077072 | 0.0080121 | 0.019468 | -0.029956 | -0.0079896 | 0.009299 | -0.31072 | 0.0021988 | -0.038405 | -0.0079842 | 0.0061158 | -0.00075443 | 0.49439 | 0.58136 | 0.45319 | 0.47607 | 0.59509 | 0.39368 | 0.23346 | 0.14191 | 0.15106 | 0.086975 | 0.12817 | 0.073242 | -0.082397 | -0.15106 | 123.1659 | 123.0057 | 0.022888 | 123.3536 | 123.2483 | 0.24261 | -0.07782 | 122.6898 | 122.6212 | -0.44403 | 122.9141 | 122.8592 | 0.23804 | -0.49896 | 123.3673 | 123.2666 | 123.2254 | -0.33875 | 122.9004 | 122.8455 | 122.9233 | -0.72327
1202.6875 | 123.5779 | -122.7859 | 0.56763 | -0.1641 | 0.085617 | 0.012285 | 0.015196 | -0.024616 | -0.017603 | 0.012503 | -0.05132 | 0.0064718 | -0.013838 | -0.011188 | -0.0034972 | 0.020609 | 0.47607 | 0.5722 | 0.43945 | 0.47607 | 0.59509 | 0.37994 | 0.22888 | 0.12817 | 0.15564 | 0.10986 | 0.14648 | 0.064087 | -0.064087 | -0.15106 | 123.1659 | 123.0148 | 0.027466 | 123.3582 | 123.262 | 0.24719 | -0.091553 | 122.7219 | 122.6349 | -0.42114 | 122.9141 | 122.8958 | 0.26093 | -0.50354 | 123.381 | 123.262 | 123.2254 | -0.33874 | 122.9324 | 122.85 | 122.9416 | -0.71869
1203.6875 | 123.5825 | -122.7722 | 0.5722 | -0.28617 | 0.082412 | 0.016557 | 0.023741 | -0.032093 | 0.0080314 | 0.021048 | -0.46331 | 0.010744 | -0.026655 | -0.0069162 | 0.011456 | 0.021677 | 0.47607 | 0.58136 | 0.44861 | 0.48065 | 0.58594 | 0.37994 | 0.21973 | 0.11444 | 0.16022 | 0.082397 | 0.14191 | 0.068665 | -0.091553 | -0.14648 | 123.1522 | 122.9919 | 0.013732 | 123.3536 | 123.2529 | 0.26093 | -0.096131 | 122.6807 | 122.6257 | -0.4303 | 122.8867 | 122.8546 | 0.22888 | -0.50354 | 123.3582 | 123.2483 | 123.2208 | -0.35248 | 122.9141 | 122.8409 | 122.9324 | -0.71869
1204.6875 | 123.5733 | -122.7905 | 0.59509 | -0.36246 | 0.080276 | 0.012285 | 0.017332 | -0.026752 | -0.0015816 | 0.021048 | -0.41753 | -0.010618 | -0.030928 | -0.011188 | 0.0039788 | 0.0088586 | 0.5127 | 0.60883 | 0.45776 | 0.48981 | 0.60425 | 0.37537 | 0.24261 | 0.10986 | 0.14191 | 0.09613 | 0.13733 | 0.059509 | -0.086975 | -0.16022 | 123.1659 | 123.0331 | 0.009155 | 123.3994 | 123.2803 | 0.24719 | -0.082398 | 122.7036 | 122.6303 | -0.45776 | 122.9004 | 122.8867 | 0.25635 | -0.53558 | 123.3948 | 123.3032 | 123.2483 | -0.35248 | 122.9279 | 122.85 | 122.9324 | -0.75531
1205.6875 | 123.5779 | -122.7951 | 0.59509 | -0.48453 | 0.065323 | 0.021898 | 0.019468 | -0.031024 | -0.010127 | 0.017844 | -0.50908 | -0.0031412 | -0.020247 | -0.0069162 | 0.0082518 | 0.015268 | 0.51727 | 0.60883 | 0.46692 | 0.5127 | 0.59967 | 0.37994 | 0.22888 | 0.10986 | 0.16022 | 0.086975 | 0.14191 | 0.07782 | -0.086975 | -0.16479 | 123.175 | 123.024 | 0.004577 | 123.4039 | 123.3078 | 0.28381 | -0.07782 | 122.7081 | 122.6303 | -0.45319 | 122.905 | 122.8821 | 0.25177 | -0.51727 | 123.3948 | 123.3124 | 123.262 | -0.36621 | 122.937 | 122.8729 | 122.9553 | -0.75989
1206.6875 | 123.5962 | -122.7722 | 0.58136 | -0.026769 | 0.071731 | 0.0037401 | 0.021604 | -0.029956 | -0.0069216 | 0.015708 | -0.34124 | -0.0074142 | -0.014906 | -0.0058482 | -0.0002932 | 0.024881 | 0.49439 | 0.60883 | 0.46692 | 0.51727 | 0.59509 | 0.39825 | 0.23804 | 0.10071 | 0.16022 | 0.09613 | 0.14648 | 0.073242 | -0.082397 | -0.14648 | 123.1705 | 123.0103 | 0.013733 | 123.381 | 123.2895 | 0.27924 | -0.086975 | 122.6898 | 122.6257 | -0.43488 | 122.8729 | 122.8683 | 0.24261 | -0.50812 | 123.3673 | 123.2666 | 123.2391 | -0.34332 | 122.9187 | 122.8455 | 122.9324 | -0.72784
1207.6875 | 123.5458 | -122.7905 | 0.60425 | -0.042028 | 0.037552 | 0.016557 | 0.020536 | -0.036365 | -0.010127 | 0.007163 | -0.21917 | -0.0084822 | -0.030928 | -0.0069162 | -0.0045652 | 0.015268 | 0.45319 | 0.53558 | 0.43488 | 0.48981 | 0.63629 | 0.37994 | 0.23346 | 0.10529 | 0.10986 | 0.054932 | 0.16022 | 0.082397 | -0.091553 | -0.14648 | 123.1705 | 123.024 | 0.032044 | 123.3261 | 123.2803 | 0.25635 | -0.15106 | 122.699 | 122.644 | -0.44403 | 122.8958 | 122.8455 | 0.20142 | -0.52185 | 123.4268 | 123.2437 | 123.2254 | -0.37079 | 122.9507 | 122.8729 | 122.9004 | -0.75073
1208.6875 | 123.6053 | -122.7951 | 0.59967 | -0.19462 | 0.073868 | 0.025102 | 0.022672 | -0.033161 | -0.016535 | 0.012503 | -0.41753 | 6.2833e-05 | -0.019179 | -0.015461 | 0.0039788 | 0.018473 | 0.49896 | 0.59967 | 0.45776 | 0.48065 | 0.6134 | 0.37994 | 0.23804 | 0.13733 | 0.16937 | 0.10986 | 0.15564 | 0.086975 | -0.082397 | -0.16022 | 123.175 | 123.0331 | 0.013733 | 123.3948 | 123.2758 | 0.24262 | -0.10071 | 122.7127 | 122.6349 | -0.44403 | 122.9324 | 122.905 | 0.27008 | -0.5127 | 123.4085 | 123.2941 | 123.2529 | -0.36163 | 122.9507 | 122.8821 | 122.9645 | -0.75989
1209.6875 | 123.5596 | -122.7814 | 0.59967 | -0.28617 | 0.066391 | 0.0080121 | 0.025877 | -0.016071 | -0.00051261 | 0.023184 | -0.5396 | -0.010618 | -0.025587 | -0.0058482 | -0.0034972 | 0.013132 | 0.50354 | 0.59967 | 0.45319 | 0.49896 | 0.61798 | 0.3891 | 0.23346 | 0.10071 | 0.15106 | 0.091553 | 0.15106 | 0.086975 | -0.082397 | -0.13733 | 123.1705 | 123.0148 | 0.018311 | 123.381 | 123.2803 | 0.2655 | -0.09613 | 122.699 | 122.644 | -0.44861 | 122.8821 | 122.8729 | 0.22888 | -0.5127 | 123.3994 | 123.2849 | 123.2346 | -0.36621 | 122.9324 | 122.8683 | 122.9324 | -0.737
1210.6875 | 123.5733 | -122.7676 | 0.60883 | -0.37772 | 0.079208 | 0.024034 | 0.024809 | -0.025684 | -0.0058536 | 0.013571 | -0.50908 | -0.0042092 | -0.02986 | -0.0015752 | -0.0045652 | 0.012064 | 0.48981 | 0.58136 | 0.45776 | 0.50812 | 0.60425 | 0.39368 | 0.23804 | 0.10529 | 0.14648 | 0.068665 | 0.14191 | 0.068665 | -0.10071 | -0.16022 | 123.1613 | 123.0057 | -0.004578 | 123.349 | 123.2758 | 0.27008 | -0.11902 | 122.6669 | 122.6074 | -0.46692 | 122.8729 | 122.8363 | 0.22888 | -0.54016 | 123.3719 | 123.2574 | 123.2254 | -0.37079 | 122.9095 | 122.8363 | 122.9141 | -0.76904
1211.6875 | 123.5779 | -122.7676 | 0.60883 | -0.24039 | 0.053573 | 0.0080121 | 0.024809 | -0.024616 | -0.0079896 | 0.007163 | -0.60064 | -0.0084822 | -0.031996 | -0.00050718 | 0.011456 | 0.020609 | 0.48981 | 0.6134 | 0.46234 | 0.50354 | 0.60883 | 0.39825 | 0.24261 | 0.11444 | 0.16479 | 0.07782 | 0.16022 | 0.086975 | -0.091553 | -0.14191 | 123.1659 | 123.0103 | 0 | 123.381 | 123.2712 | 0.26092 | -0.11902 | 122.6761 | 122.6257 | -0.44861 | 122.8821 | 122.8455 | 0.21973 | -0.52185 | 123.3765 | 123.2574 | 123.23 | -0.36621 | 122.9279 | 122.8546 | 122.9324 | -0.75073
1212.6875 | 123.5641 | -122.7768 | 0.59509 | -0.13358 | 0.070663 | 0.012285 | 0.010923 | -0.025684 | -0.0069216 | 0.026389 | -0.5396 | 0.0043348 | -0.028792 | -0.014393 | 0.0007748 | 0.018473 | 0.48065 | 0.60883 | 0.47607 | 0.5127 | 0.6134 | 0.38452 | 0.24719 | 0.10071 | 0.16479 | 0.082397 | 0.14648 | 0.073242 | -0.07782 | -0.14648 | 123.1613 | 123.024 | 0.01831 | 123.3856 | 123.2895 | 0.2655 | -0.11444 | 122.699 | 122.6303 | -0.44861 | 122.8775 | 122.8592 | 0.22888 | -0.52185 | 123.3902 | 123.2574 | 123.2529 | -0.3479 | 122.9233 | 122.85 | 122.9416 | -0.74158
1213.6875 | 123.5733 | -122.7859 | 0.59967 | -0.20987 | 0.031143 | -0.0080089 | 0.015196 | -0.024616 | -0.0090576 | 0.015708 | -0.46331 | -0.0063462 | -0.025587 | -0.0026432 | -0.0099062 | 0.023813 | 0.54474 | 0.62714 | 0.48065 | 0.54016 | 0.61798 | 0.40283 | 0.26093 | 0.10529 | 0.16022 | 0.086975 | 0.12817 | 0.086975 | -0.073242 | -0.15106 | 123.1888 | 123.0469 | 0.018311 | 123.4131 | 123.3261 | 0.27924 | -0.054931 | 122.7127 | 122.6349 | -0.4715 | 122.8912 | 122.8729 | 0.23804 | -0.5127 | 123.4039 | 123.3307 | 123.2666 | -0.33875 | 122.9141 | 122.8729 | 122.9462 | -0.75073
1214.75 | 123.5229 | -122.7768 | 0.6134 | 0.080043 | 0.058914 | 0.0090801 | 0.023741 | -0.021411 | 0.0037594 | 0.017844 | 0.009715 | 0.0054038 | -0.0095656 | 0.00056082 | 0.0007748 | 0.022745 | 0.44861 | 0.53101 | 0.42572 | 0.47607 | 0.63629 | 0.39368 | 0.26093 | 0.068665 | 0.050354 | 0.036621 | 0.14191 | 0.10071 | -0.10529 | -0.15564 | 123.1705 | 123.0377 | 0.022889 | 123.3078 | 123.2529 | 0.21515 | -0.1648 | 122.6715 | 122.6212 | -0.4715 | 122.8455 | 122.8134 | 0.19226 | -0.5127 | 123.4131 | 123.2254 | 123.2025 | -0.35248 | 122.9187 | 122.8775 | 122.8271 | -0.76904
1215.6875 | 123.587 | -122.7539 | 0.60883 | -0.13358 | 0.087753 | 0.011217 | 0.010923 | -0.037433 | -0.0079896 | 0.023184 | -0.38701 | -0.0042092 | -0.026655 | 0.00056082 | -0.0045652 | 0.017404 | 0.51727 | 0.62714 | 0.48065 | 0.53101 | 0.61798 | 0.40283 | 0.24261 | 0.09613 | 0.14648 | 0.091553 | 0.13733 | 0.064087 | -0.07782 | -0.15564 | 123.1567 | 122.9965 | 0.009155 | 123.381 | 123.2849 | 0.28839 | -0.091553 | 122.6761 | 122.5983 | -0.4715 | 122.85 | 122.8455 | 0.24719 | -0.54474 | 123.3719 | 123.2712 | 123.2346 | -0.36621 | 122.8912 | 122.818 | 122.9004 | -0.76447
1216.6875 | 123.5504 | -122.7768 | 0.61798 | -0.39298 | 0.11232 | 0.019762 | 0.022672 | -0.025684 | -0.0047856 | 0.010367 | -0.5396 | 0.0054038 | -0.017042 | 0.0037648 | 0.0039788 | 0.0142 | 0.50812 | 0.60425 | 0.4715 | 0.5127 | 0.63629 | 0.41657 | 0.2655 | 0.082397 | 0.13275 | 0.064087 | 0.16479 | 0.073242 | -0.09613 | -0.16022 | 123.1934 | 123.0423 | 0.018311 | 123.381 | 123.2895 | 0.24719 | -0.10986 | 122.6807 | 122.6166 | -0.45319 | 122.8592 | 122.8409 | 0.2243 | -0.54474 | 123.4131 | 123.2849 | 123.2483 | -0.35248 | 122.9416 | 122.85 | 122.9095 | -0.7782
1217.6875 | 123.5504 | -122.7859 | 0.60883 | -0.43876 | 0.054641 | 0.018693 | 0.013059 | -0.028888 | -0.010127 | 0.016776 | -0.49383 | 6.2833e-05 | -0.036268 | -0.011188 | 0.012524 | 0.019541 | 0.50812 | 0.60425 | 0.4715 | 0.52185 | 0.6134 | 0.40741 | 0.25635 | 0.086975 | 0.15106 | 0.059509 | 0.14191 | 0.07782 | -0.082397 | -0.17853 | 123.1934 | 123.0423 | 0.004577 | 123.3902 | 123.3078 | 0.2655 | -0.10071 | 122.7036 | 122.6074 | -0.46692 | 122.8729 | 122.8455 | 0.23804 | -0.53101 | 123.3994 | 123.2941 | 123.2574 | -0.35248 | 122.9279 | 122.8638 | 122.937 | -0.78735
1218.6875 | 123.555 | -122.7768 | 0.64087 | -0.37772 | 0.057846 | 0.012285 | 0.023741 | -0.029956 | -0.0015816 | 0.011435 | -0.63115 | 6.2833e-05 | -0.018111 | -0.0026432 | 0.0018428 | 0.013132 | 0.50812 | 0.60425 | 0.48065 | 0.5127 | 0.62714 | 0.41657 | 0.2655 | 0.10071 | 0.14191 | 0.064087 | 0.14648 | 0.059509 | -0.086975 | -0.13275 | 123.1934 | 123.0423 | -0.013733 | 123.381 | 123.2895 | 0.24719 | -0.13275 | 122.6898 | 122.644 | -0.49439 | 122.8775 | 122.8409 | 0.19684 | -0.58136 | 123.4039 | 123.2849 | 123.2574 | -0.37537 | 122.9233 | 122.8363 | 122.9187 | -0.77362
1219.6875 | 123.555 | -122.7814 | 0.60425 | -0.40824 | 0.052505 | 0.015489 | 0.026945 | -0.022479 | 0.00055539 | 0.01998 | -0.6159 | 0.0032668 | -0.025587 | -0.0058482 | 0.0029108 | 0.0077906 | 0.50354 | 0.59052 | 0.47607 | 0.50812 | 0.61798 | 0.40741 | 0.26093 | 0.09613 | 0.14648 | 0.073242 | 0.15106 | 0.059509 | -0.09613 | -0.15564 | 123.1888 | 123.0423 | 0.013733 | 123.3719 | 123.2895 | 0.24719 | -0.10071 | 122.6852 | 122.6257 | -0.45319 | 122.8775 | 122.8546 | 0.22888 | -0.54474 | 123.3994 | 123.2849 | 123.2574 | -0.34332 | 122.9324 | 122.8409 | 122.9279 | -0.75989
1220.6875 | 123.5641 | -122.7676 | 0.63171 | -0.3472 | 0.066391 | 0.011217 | 0.022672 | -0.022479 | -0.0079896 | 0.026389 | -0.50908 | 0.0011308 | -0.021315 | -0.016529 | 0.0039788 | 0.018473 | 0.5127 | 0.60883 | 0.4715 | 0.51727 | 0.62256 | 0.40741 | 0.27008 | 0.082397 | 0.15564 | 0.068665 | 0.13733 | 0.073242 | -0.086975 | -0.13275 | 123.175 | 123.0377 | -0.009155 | 123.3765 | 123.2849 | 0.24719 | -0.11902 | 122.6807 | 122.6349 | -0.49438 | 122.85 | 122.8363 | 0.20142 | -0.55847 | 123.3902 | 123.2803 | 123.2391 | -0.36163 | 122.905 | 122.8409 | 122.9233 | -0.76446
1221.6875 | 123.5596 | -122.7951 | 0.60425 | -0.37772 | 0.084549 | 0.0069441 | 0.0184 | -0.029956 | -0.0058536 | 0.024253 | -0.44805 | -0.0010052 | -0.0095656 | -0.012256 | 0.0018428 | 0.016336 | 0.49896 | 0.61798 | 0.48065 | 0.52643 | 0.63171 | 0.40741 | 0.26093 | 0.086975 | 0.16479 | 0.082397 | 0.14648 | 0.082397 | -0.091553 | -0.13275 | 123.2025 | 123.056 | 0.027466 | 123.4131 | 123.3215 | 0.2655 | -0.10529 | 122.7036 | 122.6624 | -0.45776 | 122.8821 | 122.8775 | 0.21515 | -0.52185 | 123.4268 | 123.2941 | 123.2758 | -0.34332 | 122.9416 | 122.8775 | 122.9599 | -0.737
1222.6875 | 123.5733 | -122.7814 | 0.61798 | -0.33194 | 0.050369 | 0.013353 | 0.020536 | -0.019275 | 0.0069634 | 0.014639 | -0.5396 | -0.0052782 | -0.023451 | -0.0069162 | 0.012524 | 0.0035186 | 0.5127 | 0.62714 | 0.48523 | 0.53558 | 0.64545 | 0.40741 | 0.25635 | 0.091553 | 0.16022 | 0.082397 | 0.14648 | 0.059509 | -0.10071 | -0.16479 | 123.1888 | 123.0377 | 0.027466 | 123.4085 | 123.317 | 0.27924 | -0.10529 | 122.6807 | 122.6166 | -0.4715 | 122.8729 | 122.8638 | 0.24719 | -0.55847 | 123.4268 | 123.2941 | 123.2666 | -0.36163 | 122.9279 | 122.8409 | 122.9416 | -0.78278
1223.6875 | 123.5046 | -122.7859 | 0.62714 | -0.40824 | 0.11232 | 0.013353 | 0.016264 | -0.026752 | -0.0058536 | 0.016776 | -0.66167 | 0.0021988 | -0.015974 | -0.012256 | 0.0061158 | 0.0088586 | 0.49896 | 0.59967 | 0.46692 | 0.5127 | 0.64545 | 0.3891 | 0.25635 | 0.064087 | 0.11902 | 0.027466 | 0.19226 | 0.082397 | -0.11444 | -0.16937 | 123.175 | 123.0423 | 0.018311 | 123.3856 | 123.2986 | 0.25635 | -0.12817 | 122.6715 | 122.6166 | -0.43488 | 122.85 | 122.8134 | 0.19684 | -0.54474 | 123.4314 | 123.2849 | 123.2529 | -0.37079 | 122.9782 | 122.8683 | 122.905 | -0.79651
1224.6875 | 123.5229 | -122.7997 | 0.64545 | -0.48453 | 0.097366 | 0.011217 | 0.0098553 | -0.033161 | 0.0026914 | 0.021048 | -0.60064 | 6.2833e-05 | -0.022383 | -0.014393 | 0.0050478 | 0.010996 | 0.49896 | 0.59052 | 0.44861 | 0.52643 | 0.62714 | 0.41199 | 0.24719 | 0.059509 | 0.11444 | 0.036621 | 0.16022 | 0.10071 | -0.10529 | -0.16937 | 123.2117 | 123.0469 | -0.018311 | 123.3902 | 123.3261 | 0.27924 | -0.14648 | 122.6944 | 122.6303 | -0.48523 | 122.8592 | 122.8363 | 0.20599 | -0.54474 | 123.4268 | 123.2986 | 123.2483 | -0.39826 | 122.9599 | 122.9004 | 122.9141 | -0.81482
1225.6875 | 123.5275 | -122.7859 | 0.63171 | -0.37772 | 0.088821 | 0.014421 | 0.0184 | -0.019275 | -0.010127 | 0.021048 | -0.63115 | 0.0064718 | -0.02986 | -0.0037112 | 0.0071838 | 0.015268 | 0.48981 | 0.58136 | 0.46692 | 0.54932 | 0.64087 | 0.41199 | 0.26093 | 0.050354 | 0.11902 | 0.036621 | 0.15564 | 0.09613 | -0.091553 | -0.16479 | 123.1979 | 123.0469 | 0.009155 | 123.3673 | 123.3353 | 0.28839 | -0.14191 | 122.6944 | 122.6212 | -0.47607 | 122.8363 | 122.8226 | 0.20142 | -0.53558 | 123.4268 | 123.2758 | 123.2529 | -0.37079 | 122.9416 | 122.8821 | 122.905 | -0.79651
1226.6875 | 123.5275 | -122.7814 | 0.62714 | -0.40824 | 0.064255 | 0.028306 | 0.014128 | -0.025684 | 0.00055539 | 0.013571 | -0.64641 | 0.0075398 | -0.022383 | -0.0037112 | 0.010388 | 0.0088586 | 0.49896 | 0.59052 | 0.46692 | 0.52185 | 0.62714 | 0.40741 | 0.25635 | 0.054932 | 0.11444 | 0.022888 | 0.14191 | 0.10529 | -0.11444 | -0.16022 | 123.1888 | 123.0377 | 0 | 123.3719 | 123.3032 | 0.2655 | -0.12817 | 122.6669 | 122.6212 | -0.48523 | 122.8363 | 122.8043 | 0.1831 | -0.52185 | 123.4085 | 123.2803 | 123.2483 | -0.37079 | 122.9233 | 122.8867 | 122.8958 | -0.78735
1227.6875 | 123.4543 | -122.8226 | 0.66834 | -0.51505 | 0.071731 | 0.010148 | 0.017332 | -0.023548 | 0.0026914 | 0.022116 | -0.31072 | 0.010744 | -0.030928 | 0.0037648 | -0.0002932 | 0.018473 | 0.44403 | 0.52185 | 0.37994 | 0.46692 | 0.65002 | 0.39825 | 0.22888 | 0 | 0 | -0.027466 | 0.19226 | 0.10986 | -0.1236 | -0.1831 | 123.2208 | 123.0515 | -0.018311 | 123.3444 | 123.2895 | 0.23804 | -0.2243 | 122.699 | 122.6395 | -0.47607 | 122.8226 | 122.7951 | 0.15564 | -0.55847 | 123.4726 | 123.2666 | 123.2025 | -0.43945 | 123.0148 | 122.9324 | 122.8226 | -0.85144
1228.6875 | 123.5458 | -122.7768 | 0.62714 | -0.37772 | 0.067459 | 0.025102 | 0.022672 | -0.028888 | -0.0090576 | 0.01998 | -0.50908 | -0.0031412 | -0.018111 | -0.014393 | 0.0018428 | 0.018473 | 0.49439 | 0.60425 | 0.48523 | 0.52643 | 0.65918 | 0.4303 | 0.2655 | 0.073242 | 0.14648 | 0.059509 | 0.15564 | 0.091553 | -0.091553 | -0.15106 | 123.2071 | 123.0423 | 0.032044 | 123.381 | 123.3032 | 0.26093 | -0.13275 | 122.6852 | 122.6257 | -0.4715 | 122.85 | 122.8363 | 0.21057 | -0.53558 | 123.436 | 123.2712 | 123.262 | -0.36163 | 122.9324 | 122.8683 | 122.9233 | -0.7782
1229.6875 | 123.5321 | -122.7814 | 0.63629 | -0.39298 | 0.063186 | 0.019762 | 0.033354 | -0.016071 | -0.0069216 | 0.024253 | -0.50908 | 0.0011308 | -0.02986 | -0.020801 | 0.0061158 | 0.013132 | 0.50354 | 0.59967 | 0.48065 | 0.52643 | 0.63629 | 0.42114 | 0.28381 | 0.064087 | 0.13733 | 0.036621 | 0.14191 | 0.091553 | -0.10529 | -0.16022 | 123.2025 | 123.0652 | 0 | 123.381 | 123.3078 | 0.24262 | -0.13275 | 122.6761 | 122.6212 | -0.49438 | 122.8455 | 122.818 | 0.19684 | -0.54474 | 123.4177 | 123.2849 | 123.262 | -0.35248 | 122.9233 | 122.8729 | 122.9187 | -0.79651
1230.6875 | 123.4772 | -122.7859 | 0.65918 | -0.4235 | 0.077072 | 0.012285 | 0.015196 | -0.033161 | -0.0015816 | 0.021048 | -0.67693 | -0.0020732 | -0.023451 | -0.019733 | -0.0024292 | 0.023813 | 0.47607 | 0.5722 | 0.4303 | 0.49896 | 0.66376 | 0.40283 | 0.23346 | 0.009155 | 0.064087 | -0.013733 | 0.17853 | 0.10529 | -0.1236 | -0.19226 | 123.1888 | 123.0194 | 0.004577 | 123.3582 | 123.2849 | 0.2655 | -0.18311 | 122.6624 | 122.5937 | -0.48065 | 122.7951 | 122.7722 | 0.17853 | -0.55389 | 123.4497 | 123.262 | 123.2162 | -0.42572 | 122.9645 | 122.8912 | 122.85 | -0.85144
1231.6875 | 123.468 | -122.7905 | 0.6546 | -0.43876 | 0.083481 | 0.012285 | 0.022672 | -0.021411 | -0.0069216 | 0.029593 | -0.64641 | -0.0052782 | -0.019179 | -0.0079842 | 0.0061158 | 0.012064 | 0.48981 | 0.59509 | 0.4303 | 0.52185 | 0.66376 | 0.41199 | 0.25635 | 0.022888 | 0.073242 | -0.013733 | 0.16937 | 0.10071 | -0.11902 | -0.16937 | 123.2025 | 123.0469 | 0.009155 | 123.3856 | 123.3124 | 0.2655 | -0.1648 | 122.6715 | 122.6212 | -0.48523 | 122.8134 | 122.7768 | 0.15564 | -0.55389 | 123.4543 | 123.2803 | 123.2208 | -0.39825 | 122.9599 | 122.8912 | 122.8638 | -0.82398
1232.6875 | 123.4955 | -122.7722 | 0.6546 | -0.4235 | 0.093094 | 0.0080121 | 0.023741 | -0.038501 | -0.0015816 | 0.024253 | -0.66167 | 0.0043348 | -0.018111 | -0.012256 | -0.0056342 | 0.0142 | 0.48523 | 0.58594 | 0.44861 | 0.53101 | 0.66834 | 0.40283 | 0.26093 | 0.027466 | 0.091553 | 0.009155 | 0.15564 | 0.091553 | -0.11444 | -0.15106 | 123.175 | 123.0331 | 0.013733 | 123.3582 | 123.3032 | 0.27008 | -0.16937 | 122.6578 | 122.6212 | -0.49896 | 122.7997 | 122.7814 | 0.16022 | -0.56305 | 123.4406 | 123.2574 | 123.2208 | -0.39368 | 122.9279 | 122.8638 | 122.8638 | -0.80566
1233.6875 | 123.5184 | -122.7768 | 0.65918 | -0.39298 | 0.083481 | 0.010148 | 0.0077193 | -0.022479 | -0.0047856 | 0.016776 | -0.55486 | 0.0032668 | -0.015974 | -0.012256 | -0.0067022 | 0.0035186 | 0.49896 | 0.60425 | 0.45776 | 0.53101 | 0.65002 | 0.42114 | 0.25635 | 0.041199 | 0.09613 | 0.036621 | 0.14648 | 0.10529 | -0.091553 | -0.16937 | 123.1979 | 123.0331 | -0.009156 | 123.381 | 123.3078 | 0.27466 | -0.16022 | 122.6852 | 122.6074 | -0.5127 | 122.818 | 122.8134 | 0.20599 | -0.55389 | 123.4268 | 123.2758 | 123.2346 | -0.40283 | 122.9233 | 122.8821 | 122.8729 | -0.82855
1234.6875 | 123.5275 | -122.7768 | 0.64545 | -0.31669 | 0.071731 | 0.016557 | 0.019468 | -0.011798 | -0.0037176 | 0.013571 | -0.64641 | 0.0054038 | -0.024519 | -0.0069162 | 0.0007748 | 0.0142 | 0.49896 | 0.60425 | 0.46692 | 0.54016 | 0.6546 | 0.43488 | 0.29297 | 0.036621 | 0.10529 | 0.041199 | 0.16022 | 0.07782 | -0.09613 | -0.17853 | 123.2117 | 123.0698 | 0.009155 | 123.381 | 123.317 | 0.24719 | -0.14648 | 122.6807 | 122.5983 | -0.48523 | 122.8134 | 122.818 | 0.21973 | -0.56763 | 123.4314 | 123.2758 | 123.2437 | -0.35248 | 122.937 | 122.8546 | 122.8821 | -0.82398
1235.6875 | 123.5321 | -122.7585 | 0.64545 | -0.39298 | 0.081344 | 0.016557 | 0.0077193 | -0.0096622 | -0.012263 | 0.024253 | -0.63115 | 0.0075398 | -0.022383 | 0.0026968 | 0.0061158 | 0.017404 | 0.51727 | 0.60425 | 0.48981 | 0.54474 | 0.65918 | 0.4303 | 0.29755 | 0.041199 | 0.11444 | 0.036621 | 0.13275 | 0.091553 | -0.091553 | -0.15564 | 123.1888 | 123.056 | 0.013733 | 123.3627 | 123.3032 | 0.24719 | -0.12817 | 122.6669 | 122.6028 | -0.5127 | 122.7997 | 122.7951 | 0.19226 | -0.55389 | 123.4177 | 123.2758 | 123.2483 | -0.3479 | 122.8912 | 122.85 | 122.8729 | -0.80109
1236.6875 | 123.5275 | -122.7768 | 0.65002 | -0.36246 | 0.097366 | 0.018693 | 0.025877 | -0.021411 | -0.0058536 | 0.025321 | -0.52434 | 0.015017 | -0.015974 | -0.0037112 | 0.011456 | 0.0088586 | 0.5127 | 0.60425 | 0.48523 | 0.54474 | 0.66834 | 0.42572 | 0.27466 | 0.050354 | 0.12817 | 0.036621 | 0.15564 | 0.10071 | -0.12817 | -0.16479 | 123.2025 | 123.0515 | 0.018311 | 123.381 | 123.3215 | 0.27008 | -0.13733 | 122.6486 | 122.612 | -0.49438 | 122.8271 | 122.8134 | 0.20142 | -0.54932 | 123.4451 | 123.2895 | 123.262 | -0.37537 | 122.9324 | 122.8775 | 122.905 | -0.81482
1237.6875 | 123.468 | -122.7768 | 0.67291 | -0.49979 | 0.11018 | 0.022966 | 0.017332 | -0.019275 | -0.0069216 | 0.012503 | -0.37176 | 0.0086078 | -0.027724 | -0.011188 | -0.0034972 | 0.010996 | 0.45776 | 0.54016 | 0.41199 | 0.47607 | 0.66376 | 0.41657 | 0.26093 | 0.004578 | 0.07782 | -0.064087 | 0.1831 | 0.11444 | -0.13275 | -0.19684 | 123.1934 | 123.0377 | -0.009156 | 123.317 | 123.2529 | 0.21515 | -0.21515 | 122.644 | 122.58 | -0.48981 | 122.7814 | 122.7127 | 0.13275 | -0.55847 | 123.4406 | 123.2346 | 123.1888 | -0.41199 | 122.9599 | 122.8912 | 122.8546 | -0.86975
1238.7031 | 123.4406 | -122.7722 | 0.68207 | -0.026769 | 0.096298 | 0.0037401 | 0.024809 | -0.016071 | 0.035802 | 0.026389 | -0.31072 | 0.0075398 | -0.0095656 | -0.0058482 | 0.015729 | 0.0142 | 0.48981 | 0.49896 | 0.3891 | 0.48523 | 0.69122 | 0.40283 | 0.24719 | 0 | -0.009155 | -0.073242 | 0.18768 | 0.11444 | -0.10986 | -0.19226 | 123.175 | 123.0194 | 0.009155 | 123.2712 | 123.2574 | 0.23804 | -0.19226 | 122.6624 | 122.58 | -0.49439 | 122.7722 | 122.699 | 0.11902 | -0.56763 | 123.4634 | 123.262 | 123.1613 | -0.43488 | 122.9599 | 122.8867 | 122.7631 | -0.87433
1239.6875 | 123.4634 | -122.7722 | 0.67749 | -0.43876 | 0.087753 | 0.011217 | 0.025877 | -0.020343 | -0.012263 | 0.022116 | -0.58538 | 0.0011308 | -0.027724 | -0.0015752 | -0.0099062 | 0.0142 | 0.47607 | 0.54932 | 0.42572 | 0.49439 | 0.68665 | 0.39825 | 0.25635 | 0 | 0.032043 | -0.009155 | 0.20599 | 0.11902 | -0.10529 | -0.19684 | 123.1705 | 123.0286 | 0.009156 | 123.3215 | 123.2666 | 0.23804 | -0.20142 | 122.6669 | 122.5754 | -0.4715 | 122.7722 | 122.7631 | 0.18768 | -0.55847 | 123.4589 | 123.2483 | 123.1979 | -0.42114 | 122.9782 | 122.8912 | 122.8043 | -0.87433
1240.6875 | 123.4543 | -122.7951 | 0.67749 | -0.54557 | 0.071731 | -0.0026689 | 0.011991 | -0.026752 | -0.0058536 | 0.015708 | -0.60064 | 6.2833e-05 | -0.022383 | -0.01012 | 0.0018428 | 0.018473 | 0.47607 | 0.54932 | 0.42114 | 0.50354 | 0.68207 | 0.41657 | 0.27466 | -0.013733 | 0.022888 | -0.013733 | 0.17853 | 0.10071 | -0.13275 | -0.16937 | 123.2117 | 123.0698 | 0.004578 | 123.3444 | 123.2986 | 0.22888 | -0.20142 | 122.6624 | 122.6257 | -0.49896 | 122.7814 | 122.7814 | 0.15564 | -0.57678 | 123.4772 | 123.2712 | 123.2162 | -0.40283 | 122.9736 | 122.8958 | 122.818 | -0.84686
1241.6875 | 123.4726 | -122.7859 | 0.68207 | -0.46927 | 0.067459 | 0.0048081 | 0.024809 | -0.021411 | -0.012263 | 0.012503 | -0.6159 | 0.01288 | -0.0084976 | 0.0091058 | -0.0034972 | 0.025949 | 0.4715 | 0.57678 | 0.43945 | 0.49896 | 0.70038 | 0.41199 | 0.27008 | 0.009155 | 0.027466 | -0.027466 | 0.18768 | 0.10529 | -0.12817 | -0.19684 | 123.1979 | 123.056 | 0.01831 | 123.3627 | 123.2849 | 0.22888 | -0.21057 | 122.6578 | 122.5891 | -0.49439 | 122.7951 | 122.7585 | 0.16937 | -0.57678 | 123.4863 | 123.2574 | 123.2254 | -0.41199 | 122.9736 | 122.8912 | 122.8134 | -0.87891
1242.6875 | 123.4589 | -122.8088 | 0.68207 | -0.46927 | 0.094162 | 0.0080121 | 0.025877 | -0.021411 | -0.0079896 | 0.025321 | -0.5396 | -0.0074142 | -0.017042 | -0.011188 | 0.0061158 | 0.016336 | 0.46692 | 0.55389 | 0.42114 | 0.48981 | 0.69122 | 0.4303 | 0.2655 | 0 | 0.018311 | -0.036621 | 0.1831 | 0.1236 | -0.13275 | -0.1831 | 123.2391 | 123.0743 | 0.009155 | 123.3627 | 123.2986 | 0.2243 | -0.21515 | 122.6761 | 122.6257 | -0.49896 | 122.8088 | 122.7722 | 0.14648 | -0.55847 | 123.5001 | 123.2758 | 123.23 | -0.41657 | 122.9919 | 122.9324 | 122.8271 | -0.86517
1243.7031 | 123.468 | -122.7585 | 0.67291 | 0.36996 | 0.097366 | 0.013353 | 0.024809 | -0.019275 | 0.013372 | 0.030661 | -0.05132 | 0.018221 | 0.0053884 | -0.01012 | 0.016797 | 0.0077906 | 0.46234 | 0.45776 | 0.36621 | 0.47607 | 0.72327 | 0.41199 | 0.26093 | 0.004578 | -0.027466 | -0.064087 | 0.19226 | 0.11902 | -0.11444 | -0.19226 | 123.1705 | 123.0194 | 0.050354 | 123.2162 | 123.2346 | 0.21515 | -0.21057 | 122.644 | 122.5662 | -0.48065 | 122.7631 | 122.6944 | 0.12817 | -0.55389 | 123.4818 | 123.2208 | 123.1247 | -0.41199 | 122.9507 | 122.8775 | 122.731 | -0.86517
1244.6875 | 123.4589 | -122.7997 | 0.67749 | -0.48453 | 0.10377 | 0.015489 | 0.033354 | -0.011798 | -0.0026496 | 0.010367 | -0.6159 | 0.010744 | -0.017042 | 0.0026968 | -0.0013612 | 0.010996 | 0.44861 | 0.49439 | 0.36621 | 0.4715 | 0.71411 | 0.40741 | 0.25177 | -0.018311 | -0.004578 | -0.064087 | 0.19684 | 0.12817 | -0.13733 | -0.18768 | 123.2071 | 123.0515 | 0.036621 | 123.2941 | 123.2712 | 0.21973 | -0.22888 | 122.6624 | 122.612 | -0.48065 | 122.7814 | 122.7356 | 0.1236 | -0.54932 | 123.5138 | 123.2483 | 123.1659 | -0.42572 | 122.9965 | 122.9279 | 122.7951 | -0.86517
1245.6875 | 123.436 | -122.7814 | 0.68665 | -0.4235 | 0.071731 | 0.014421 | 0.03549 | -0.019275 | -0.0058536 | 0.015708 | -0.67693 | 0.013948 | -0.019179 | 0.0091058 | -0.0045652 | 0.013132 | 0.42572 | 0.49439 | 0.36621 | 0.48065 | 0.71869 | 0.39825 | 0.25177 | -0.022888 | -0.004578 | -0.073242 | 0.19226 | 0.12817 | -0.13275 | -0.18768 | 123.1796 | 123.0331 | 0.032043 | 123.2758 | 123.262 | 0.22888 | -0.26093 | 122.6486 | 122.5937 | -0.49438 | 122.7585 | 122.7081 | 0.11444 | -0.55847 | 123.5001 | 123.2071 | 123.1476 | -0.43488 | 122.9736 | 122.9095 | 122.7768 | -0.87433
1246.6875 | 123.4589 | -122.7905 | 0.69122 | -0.53031 | 0.085617 | 0.017625 | 0.025877 | -0.034229 | -0.0047856 | 0.021048 | -0.6159 | 0.0054038 | -0.015974 | -0.01012 | 0.0018428 | 0.018473 | 0.44403 | 0.48981 | 0.37079 | 0.46234 | 0.70953 | 0.40283 | 0.23804 | -0.041199 | 0.009155 | -0.050354 | 0.1831 | 0.13733 | -0.15106 | -0.20142 | 123.1934 | 123.0286 | 0.018311 | 123.2803 | 123.2529 | 0.2243 | -0.24719 | 122.6395 | 122.5891 | -0.50812 | 122.7493 | 122.7402 | 0.15106 | -0.55389 | 123.5001 | 123.2346 | 123.1613 | -0.45319 | 122.9736 | 122.9279 | 122.7997 | -0.89264
1247.6875 | 123.4497 | -122.7905 | 0.68207 | -0.45401 | 0.092026 | 0.017625 | 0.036558 | -0.029956 | -0.0047856 | 0.021048 | -0.64641 | 0.0064718 | -0.0084976 | 0.0059018 | -0.0002932 | 0.017404 | 0.42114 | 0.49896 | 0.37994 | 0.46234 | 0.71411 | 0.39825 | 0.26093 | -0.036621 | -0.009155 | -0.059509 | 0.19226 | 0.11902 | -0.13733 | -0.19226 | 123.1888 | 123.0515 | 0.032043 | 123.2895 | 123.2529 | 0.20142 | -0.26093 | 122.6532 | 122.5983 | -0.48981 | 122.7539 | 122.731 | 0.13275 | -0.56305 | 123.5046 | 123.2117 | 123.1705 | -0.42114 | 122.9828 | 122.9095 | 122.7814 | -0.87433
1248.7031 | 123.5504 | -122.7493 | 0.66834 | 0.3547 | 0.084549 | 0.018693 | 0.020536 | -0.022479 | -0.00051261 | 0.023184 | 0.22334 | 0.010744 | 4.7432e-05 | 0.00056082 | -0.0034972 | 0.019541 | 0.48065 | 0.5127 | 0.39368 | 0.49896 | 0.6958 | 0.42572 | 0.27924 | 0.054932 | 0.036621 | 0.013733 | 0.16022 | 0.10071 | -0.09613 | -0.17395 | 123.175 | 123.0286 | 0.027466 | 123.262 | 123.2483 | 0.21973 | -0.18768 | 122.6532 | 122.5754 | -0.50812 | 122.8043 | 122.7631 | 0.18768 | -0.56763 | 123.4451 | 123.23 | 123.143 | -0.3891 | 122.9095 | 122.85 | 122.7859 | -0.84228
1249.6875 | 123.4406 | -122.8134 | 0.70496 | -0.46927 | 0.09523 | 0.012285 | 0.038694 | -0.022479 | -0.0079896 | 0.01998 | -0.63115 | 0.0032668 | -0.011702 | -0.0026432 | -0.0067022 | 0.013132 | 0.43945 | 0.48523 | 0.37079 | 0.47607 | 0.71869 | 0.41657 | 0.2655 | -0.050354 | 0.004578 | -0.041199 | 0.19226 | 0.14648 | -0.1236 | -0.21973 | 123.23 | 123.0789 | 0.013733 | 123.2986 | 123.2895 | 0.21057 | -0.2655 | 122.6898 | 122.5937 | -0.5127 | 122.7631 | 122.7722 | 0.17853 | -0.55847 | 123.5321 | 123.2529 | 123.1842 | -0.43945 | 123.0057 | 122.9599 | 122.818 | -0.92468
1250.6875 | 123.4818 | -122.7814 | 0.70038 | -0.43876 | 0.11766 | 0.0037401 | 0.022672 | -0.017139 | 0.010168 | 0.011435 | -0.55486 | 0.0086078 | -0.015974 | -0.017597 | -0.0002932 | 0.012064 | 0.44861 | 0.48981 | 0.37537 | 0.48523 | 0.71869 | 0.39825 | 0.27466 | -0.018311 | 0.032043 | -0.050354 | 0.19226 | 0.12817 | -0.13275 | -0.19226 | 123.1796 | 123.056 | 0.018311 | 123.2712 | 123.2666 | 0.21057 | -0.25177 | 122.6486 | 122.5891 | -0.50812 | 122.7631 | 122.731 | 0.14191 | -0.5722 | 123.5001 | 123.23 | 123.1567 | -0.42572 | 122.9736 | 122.9095 | 122.8134 | -0.89264
1251.6875 | 123.4909 | -122.7859 | 0.69122 | -0.39298 | 0.09523 | 0.0037401 | 0.022672 | -0.025684 | -0.0015816 | 0.018912 | -0.55486 | 0.0054038 | -0.0020886 | -0.00050718 | 0.0061158 | 0.016336 | 0.44403 | 0.48981 | 0.35706 | 0.48523 | 0.68207 | 0.39825 | 0.25177 | -0.041199 | 0.027466 | -0.054932 | 0.19684 | 0.11444 | -0.1236 | -0.19684 | 123.1842 | 123.0377 | -0.009155 | 123.2758 | 123.2712 | 0.23346 | -0.24719 | 122.6624 | 122.5891 | -0.49439 | 122.7448 | 122.731 | 0.14191 | -0.57678 | 123.468 | 123.23 | 123.143 | -0.43945 | 122.9828 | 122.9004 | 122.8134 | -0.88806
1252.6875 | 123.4589 | -122.7814 | 0.68665 | -0.4235 | 0.10805 | 0.013353 | 0.015196 | -0.029956 | 0.0080314 | 0.026389 | -0.5396 | 0.015017 | 4.7432e-05 | 0.0048338 | -0.0034972 | 0.0088586 | 0.44403 | 0.48523 | 0.38452 | 0.50812 | 0.72327 | 0.42114 | 0.25635 | -0.045776 | 0.018311 | -0.054932 | 0.1831 | 0.12817 | -0.14648 | -0.19684 | 123.2025 | 123.0377 | 0.036621 | 123.2666 | 123.2895 | 0.25177 | -0.24261 | 122.6349 | 122.5845 | -0.50354 | 122.7356 | 122.7264 | 0.14191 | -0.55847 | 123.5046 | 123.2254 | 123.1659 | -0.4303 | 122.9645 | 122.9095 | 122.7997 | -0.88348
1253.7031 | 123.5687 | -122.7081 | 0.6546 | 0.40048 | 0.088821 | 0.0080121 | 0.0045153 | -0.029956 | -0.016535 | 0.017844 | 0.28437 | 0.0086078 | -0.025587 | -0.0079842 | 0.0071838 | 0.015268 | 0.53558 | 0.60425 | 0.50354 | 0.56305 | 0.65918 | 0.45776 | 0.32501 | 0.073242 | 0.09613 | 0.059509 | 0.14191 | 0.082397 | -0.10529 | -0.14191 | 123.1659 | 123.0331 | 0.004578 | 123.3124 | 123.2712 | 0.23804 | -0.11902 | 122.6028 | 122.5662 | -0.5127 | 122.7814 | 122.7676 | 0.20142 | -0.57221 | 123.3673 | 123.2437 | 123.2117 | -0.32959 | 122.85 | 122.7905 | 122.8043 | -0.79651
1254.6875 | 123.468 | -122.7859 | 0.70038 | -0.37772 | 0.123 | 0.015489 | 0.020536 | -0.020343 | 0.0048274 | 0.018912 | -0.55486 | 0.011812 | -0.0063606 | -0.0069162 | -0.0002932 | 0.0077906 | 0.4715 | 0.47607 | 0.37537 | 0.48981 | 0.72327 | 0.40741 | 0.27008 | -0.041199 | 0.004578 | -0.045776 | 0.1831 | 0.14648 | -0.11902 | -0.19684 | 123.1934 | 123.056 | 0.022889 | 123.262 | 123.2758 | 0.21973 | -0.22888 | 122.6669 | 122.5891 | -0.51727 | 122.7448 | 122.7402 | 0.15106 | -0.55389 | 123.5092 | 123.2574 | 123.1613 | -0.4303 | 122.9691 | 122.9324 | 122.7905 | -0.89722
1255.6875 | 123.468 | -122.7814 | 0.70496 | -0.36246 | 0.10057 | 0.0016041 | 0.026945 | -0.016071 | 0.0037594 | 0.023184 | -0.67693 | 0.0086078 | -0.0063606 | -0.0015752 | 0.0029108 | 0.020609 | 0.46692 | 0.48981 | 0.39825 | 0.50812 | 0.71869 | 0.43488 | 0.27466 | -0.050354 | 0.009155 | -0.059509 | 0.18768 | 0.14648 | -0.13275 | -0.20142 | 123.2162 | 123.056 | 0.013733 | 123.2712 | 123.2895 | 0.23346 | -0.23804 | 122.6486 | 122.58 | -0.51727 | 122.731 | 122.7219 | 0.14191 | -0.55847 | 123.5001 | 123.2483 | 123.1796 | -0.4303 | 122.9691 | 122.9279 | 122.7905 | -0.90637
1256.6875 | 123.4909 | -122.7722 | 0.70953 | -0.40824 | 0.099502 | 0.024034 | 0.022672 | -0.029956 | -0.0047856 | 0.014639 | -0.5396 | 0.0043348 | 0.0011164 | 0.0026968 | 0.0061158 | 0.018473 | 0.4715 | 0.50812 | 0.3891 | 0.50812 | 0.73242 | 0.43488 | 0.28381 | -0.045776 | 0.004578 | -0.064087 | 0.17853 | 0.11444 | -0.13275 | -0.18768 | 123.2071 | 123.056 | 0.022888 | 123.2803 | 123.2803 | 0.2243 | -0.23804 | 122.6395 | 122.5845 | -0.53101 | 122.7264 | 122.7081 | 0.1236 | -0.59509 | 123.5046 | 123.2437 | 123.1613 | -0.42572 | 122.9507 | 122.8867 | 122.7768 | -0.89722
1257.6875 | 123.4863 | -122.7768 | 0.70496 | -0.39298 | 0.09523 | -0.00053286 | 0.033354 | -0.022479 | 0.0058954 | 0.017844 | -0.52434 | 0.013948 | -0.0031566 | 0.0016288 | 0.010388 | 0.019541 | 0.49896 | 0.52643 | 0.42114 | 0.55389 | 0.72327 | 0.42572 | 0.27924 | -0.004578 | 0.036621 | -0.018311 | 0.17395 | 0.13275 | -0.12817 | -0.21515 | 123.2025 | 123.056 | 0.018311 | 123.3032 | 123.3307 | 0.27466 | -0.20599 | 122.6486 | 122.5616 | -0.53101 | 122.7722 | 122.7585 | 0.19684 | -0.57221 | 123.5001 | 123.2758 | 123.1979 | -0.42572 | 122.9507 | 122.9095 | 122.8134 | -0.92011
1258.7031 | 123.4818 | -122.7676 | 0.70496 | 0.29367 | 0.1198 | -0.0016009 | 0.026945 | -0.01073 | -0.0015816 | 0.022116 | 0.19282 | 0.0086078 | -0.0010206 | 0.00056082 | 0.0061158 | 0.015268 | 0.48523 | 0.47607 | 0.3891 | 0.48523 | 0.71411 | 0.45319 | 0.28381 | 0.009155 | -0.022888 | -0.050354 | 0.16479 | 0.11444 | -0.11444 | -0.17853 | 123.2208 | 123.0515 | 0.009155 | 123.2437 | 123.2529 | 0.20142 | -0.21973 | 122.6532 | 122.5891 | -0.54016 | 122.7768 | 122.7173 | 0.12817 | -0.59052 | 123.4818 | 123.2529 | 123.1567 | -0.42114 | 122.9324 | 122.8821 | 122.7448 | -0.88348
1259.6875 | 123.5046 | -122.7264 | 0.71411 | -0.31669 | 0.089889 | 0.0090801 | 0.021604 | -0.029956 | 0.0016234 | 0.024253 | -0.57012 | 0.01288 | -0.0074286 | -0.0090522 | 0.0050478 | 0.012064 | 0.48981 | 0.48523 | 0.40741 | 0.52643 | 0.737 | 0.4303 | 0.27466 | -0.009155 | 0.041199 | -0.018311 | 0.17853 | 0.1236 | -0.12817 | -0.20142 | 123.1567 | 123.0011 | 0.022889 | 123.2117 | 123.2529 | 0.25177 | -0.2243 | 122.5983 | 122.525 | -0.53558 | 122.7173 | 122.7081 | 0.18311 | -0.59052 | 123.4634 | 123.2162 | 123.1338 | -0.43945 | 122.905 | 122.85 | 122.7676 | -0.91553
1260.6875 | 123.4955 | -122.7402 | 0.73242 | -0.37772 | 0.093094 | 0.0058761 | 0.023741 | -0.024616 | -0.0026496 | 0.031729 | -0.58538 | 0.016085 | 0.0011164 | -0.017597 | -0.0013612 | 0.0077906 | 0.48981 | 0.51727 | 0.42114 | 0.54016 | 0.74158 | 0.44861 | 0.27924 | -0.018311 | 0.041199 | -0.041199 | 0.17395 | 0.11902 | -0.11444 | -0.17853 | 123.1888 | 123.0194 | 0.009155 | 123.2574 | 123.2803 | 0.26093 | -0.24262 | 122.6257 | 122.5616 | -0.55847 | 122.7219 | 122.699 | 0.13733 | -0.6134 | 123.4818 | 123.23 | 123.1613 | -0.45319 | 122.9141 | 122.8592 | 122.7814 | -0.91095
1261.6875 | 123.4818 | -122.7539 | 0.71411 | -0.36246 | 0.10484 | -0.0080089 | 0.020536 | -0.024616 | 0.0069634 | 0.028525 | -0.57012 | -0.0084822 | -0.01277 | -0.00050718 | -0.0013612 | 0.0056546 | 0.47607 | 0.5127 | 0.41657 | 0.54474 | 0.73242 | 0.44403 | 0.29297 | -0.036621 | 0.032043 | -0.041199 | 0.17853 | 0.10529 | -0.13275 | -0.20142 | 123.1979 | 123.0469 | 0.018311 | 123.2666 | 123.2986 | 0.25177 | -0.23804 | 122.6212 | 122.5525 | -0.53558 | 122.7173 | 122.7127 | 0.16022 | -0.60883 | 123.4863 | 123.23 | 123.1705 | -0.42114 | 122.9324 | 122.8592 | 122.7859 | -0.91553
1262.6875 | 123.4772 | -122.7493 | 0.737 | -0.43876 | 0.090957 | 0.014421 | 0.021604 | -0.033161 | -0.0047856 | 0.016776 | -0.50908 | 0.0096758 | -0.011702 | -0.0047802 | 0.0050478 | 0.015268 | 0.4715 | 0.50354 | 0.40741 | 0.53558 | 0.73242 | 0.45319 | 0.29755 | -0.045776 | 0.022888 | -0.045776 | 0.18768 | 0.12817 | -0.15106 | -0.19684 | 123.2025 | 123.0469 | -0.004578 | 123.2529 | 123.2849 | 0.23804 | -0.2655 | 122.5983 | 122.5525 | -0.54932 | 122.7036 | 122.7036 | 0.15106 | -0.60883 | 123.4818 | 123.2208 | 123.1567 | -0.43945 | 122.937 | 122.8775 | 122.7722 | -0.93384
1263.6875 | 123.4818 | -122.7493 | 0.71411 | -0.40824 | 0.10377 | 0.015489 | 0.031217 | -0.029956 | 0.0048274 | 0.016776 | -0.5396 | 0.0075398 | -0.011702 | -0.0069162 | -0.0002932 | 0.015268 | 0.4715 | 0.50354 | 0.42572 | 0.53101 | 0.74158 | 0.44861 | 0.28839 | -0.036621 | 0.009155 | -0.059509 | 0.17853 | 0.12817 | -0.11902 | -0.20599 | 123.1979 | 123.0377 | 0.027466 | 123.2529 | 123.2803 | 0.24261 | -0.24261 | 122.6303 | 122.5433 | -0.53558 | 122.7127 | 122.6898 | 0.14649 | -0.58594 | 123.4909 | 123.2208 | 123.175 | -0.42572 | 122.9279 | 122.8775 | 122.7585 | -0.92011
1264.6875 | 123.4818 | -122.7448 | 0.70496 | -0.39298 | 0.11232 | 0.0037401 | 0.025877 | -0.024616 | 0.0069634 | 0.028525 | -0.31072 | 0.0075398 | -0.0063606 | -0.0090522 | 0.0061158 | 0.0056546 | 0.51727 | 0.55389 | 0.46234 | 0.54474 | 0.75531 | 0.45319 | 0.31128 | 0 | 0.041199 | -0.022888 | 0.16937 | 0.13275 | -0.12817 | -0.18768 | 123.1979 | 123.056 | 0.050354 | 123.2986 | 123.2895 | 0.23346 | -0.18768 | 122.6166 | 122.5571 | -0.53558 | 122.7448 | 122.7219 | 0.16479 | -0.57221 | 123.5001 | 123.262 | 123.2071 | -0.39368 | 122.9141 | 122.8775 | 122.7859 | -0.89264
1265.6875 | 123.4955 | -122.7539 | 0.72784 | -0.37772 | 0.094162 | 0.011217 | 0.028013 | -0.018207 | 0.0080314 | 0.029593 | -0.52434 | 0.018221 | -0.0074286 | -0.00050718 | 0.018933 | 0.0142 | 0.51727 | 0.53101 | 0.44403 | 0.56305 | 0.74616 | 0.45776 | 0.31128 | -0.004578 | 0.032043 | -0.018311 | 0.16937 | 0.13275 | -0.12817 | -0.1831 | 123.2117 | 123.0652 | 0.018311 | 123.2849 | 123.317 | 0.25177 | -0.21057 | 122.6257 | 122.5708 | -0.55847 | 122.7493 | 122.7356 | 0.16479 | -0.59509 | 123.5001 | 123.2712 | 123.1979 | -0.41657 | 122.9233 | 122.8867 | 122.7859 | -0.91095
1266.6875 | 123.4772 | -122.7402 | 0.73242 | -0.37772 | 0.10484 | 0.0016041 | 0.025877 | -0.019275 | 0.011236 | 0.021048 | -0.49383 | 0.0032668 | -0.021315 | 0.010174 | -0.0034972 | 0.010996 | 0.50812 | 0.54016 | 0.43945 | 0.55847 | 0.73242 | 0.46234 | 0.31586 | -0.004578 | 0.045776 | -0.022888 | 0.16937 | 0.11444 | -0.1236 | -0.19684 | 123.2025 | 123.056 | 0 | 123.2803 | 123.2986 | 0.24261 | -0.2243 | 122.6166 | 122.5433 | -0.56305 | 122.7356 | 122.7173 | 0.17395 | -0.61798 | 123.4726 | 123.2483 | 123.1796 | -0.41657 | 122.9095 | 122.8546 | 122.7859 | -0.92926
1267.6875 | 123.4909 | -122.7219 | 0.73242 | -0.40824 | 0.097366 | 0.0080121 | 0.014128 | -0.032093 | 0.0026914 | 0.028525 | -0.47857 | 0.013948 | -0.019179 | -0.0026432 | -0.0034972 | 0.0142 | 0.49439 | 0.52185 | 0.44403 | 0.54932 | 0.75531 | 0.44403 | 0.3067 | -0.004578 | 0.032043 | -0.022888 | 0.1831 | 0.12817 | -0.1236 | -0.1831 | 123.1659 | 123.0286 | 0.022888 | 123.2437 | 123.2712 | 0.24261 | -0.23804 | 122.5983 | 122.5388 | -0.54932 | 122.7173 | 122.699 | 0.16022 | -0.60425 | 123.4772 | 123.2162 | 123.1659 | -0.42572 | 122.905 | 122.85 | 122.7539 | -0.91553
1268.6875 | 123.5092 | -122.7356 | 0.73242 | -0.36246 | 0.10911 | 0.0016041 | 0.019468 | -0.025684 | -0.0015816 | 0.012503 | -0.52434 | -0.0010052 | -0.011702 | 0.0026968 | 0.0007748 | 0.024881 | 0.48523 | 0.54474 | 0.4303 | 0.54932 | 0.74616 | 0.45776 | 0.31586 | -0.018311 | 0.027466 | -0.027466 | 0.1831 | 0.11444 | -0.13733 | -0.19684 | 123.1934 | 123.0515 | 0.013733 | 123.2803 | 123.2849 | 0.23346 | -0.24719 | 122.5983 | 122.5388 | -0.54932 | 122.7173 | 122.7081 | 0.16937 | -0.61798 | 123.4818 | 123.2208 | 123.1659 | -0.41657 | 122.9187 | 122.85 | 122.7631 | -0.92926
1269.6875 | 123.4955 | -122.7448 | 0.72784 | -0.3472 | 0.10057 | 0.010148 | 0.024809 | -0.026752 | -0.0015816 | 0.012503 | -0.49383 | 0.0086078 | -0.010634 | 0.00056082 | -0.0067022 | 0.0067226 | 0.50354 | 0.53101 | 0.42572 | 0.55389 | 0.75989 | 0.45319 | 0.3067 | -0.041199 | 0.022888 | -0.027466 | 0.1831 | 0.12817 | -0.11902 | -0.18768 | 123.1979 | 123.0515 | 0.032044 | 123.2758 | 123.2986 | 0.24719 | -0.2243 | 122.6257 | 122.5571 | -0.54474 | 122.7036 | 122.7173 | 0.16022 | -0.59967 | 123.5046 | 123.2483 | 123.1705 | -0.42114 | 122.9279 | 122.8729 | 122.7676 | -0.91553
1270.6875 | 123.4726 | -122.7173 | 0.74158 | -0.40824 | 0.10698 | 0.0090801 | 0.032286 | -0.017139 | -0.0079896 | 0.015708 | -0.50908 | 0.0096758 | -0.011702 | -0.0047802 | 0.0071838 | 0.024881 | 0.48981 | 0.54016 | 0.44403 | 0.55389 | 0.75989 | 0.48065 | 0.32959 | -0.041199 | 0.013733 | -0.045776 | 0.16937 | 0.12817 | -0.13275 | -0.19684 | 123.1979 | 123.0469 | 0.018311 | 123.2574 | 123.2712 | 0.2243 | -0.25177 | 122.5845 | 122.5204 | -0.5722 | 122.6761 | 122.6715 | 0.15106 | -0.6134 | 123.4772 | 123.2071 | 123.1613 | -0.41199 | 122.8867 | 122.8455 | 122.731 | -0.93841

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.3552 | 23.9737 | 24.3942 | 24.6317
0.6448 | 23.9662 | 24.3941 | 24.6374
1.6448 | 23.9721 | 24.3973 | 24.6295
2.6448 | 23.9729 | 24.3927 | 24.635
3.6448 | 24.1022 | 24.3906 | 24.6303
4.6448 | 24.7833 | 24.3919 | 24.6278
5.6448 | 26.1546 | 24.3925 | 24.6301
6.6448 | 28.1778 | 24.3932 | 24.6336
7.6448 | 30.8019 | 24.3834 | 24.6355
8.6448 | 33.9506 | 24.3978 | 24.6338
9.6448 | 37.4559 | 24.3935 | 24.6342
10.6448 | 41.3566 | 24.3996 | 24.632
11.6448 | 45.5051 | 24.3999 | 24.6404
12.6448 | 49.9265 | 24.4083 | 24.6525
13.6448 | 54.54 | 24.4223 | 24.657
14.6448 | 59.4051 | 24.4385 | 24.6679
15.6448 | 64.3975 | 24.4408 | 24.6883
16.6448 | 69.5557 | 24.4609 | 24.7061
17.6448 | 74.7194 | 24.5027 | 24.7285
18.6448 | 80.1353 | 24.5152 | 24.7507
19.6448 | 85.7085 | 24.5584 | 24.7835
20.6448 | 91.2946 | 24.6025 | 24.8174
21.6448 | 96.9954 | 24.638 | 24.8513
22.6448 | 102.7824 | 24.6948 | 24.9005
23.6448 | 108.6513 | 24.745 | 24.9426
24.6448 | 114.6067 | 24.8125 | 24.9983
25.6448 | 120.5814 | 24.8875 | 25.062
26.6448 | 126.5435 | 24.9556 | 25.1235
27.6448 | 132.5232 | 25.0454 | 25.2021
28.6448 | 138.5167 | 25.1507 | 25.2706
29.6448 | 144.5912 | 25.2536 | 25.3494
30.6448 | 150.5904 | 25.374 | 25.445
31.6448 | 156.5123 | 25.4942 | 25.5394
32.6448 | 162.5216 | 25.6313 | 25.6456
33.6448 | 168.4306 | 25.7717 | 25.7601
34.6448 | 174.438 | 25.9393 | 25.8779
35.6448 | 180.353 | 26.1022 | 26.0082
36.6448 | 186.2369 | 26.2846 | 26.1378
37.6448 | 192.1898 | 26.4733 | 26.2798
38.6448 | 198.1268 | 26.6868 | 26.4382
39.6448 | 204.0041 | 26.9029 | 26.5987
40.6448 | 209.9291 | 27.1374 | 26.7729
41.6448 | 215.8452 | 27.3903 | 26.9652
42.6448 | 221.7588 | 27.6532 | 27.1527
43.6448 | 227.6618 | 27.9222 | 27.3555
44.6448 | 233.528 | 28.2128 | 27.5754
45.6448 | 239.2782 | 28.5038 | 27.8105
46.6448 | 245.0437 | 28.8279 | 28.0509
47.6448 | 250.8351 | 29.1635 | 28.3037
48.6448 | 256.5712 | 29.5072 | 28.5467
49.6448 | 262.3547 | 29.8679 | 28.8279
50.6448 | 268.0241 | 30.2619 | 29.1089
51.6448 | 273.6977 | 30.6648 | 29.4083
52.6448 | 279.3509 | 31.0798 | 29.7234
53.6448 | 284.8938 | 31.5067 | 30.0505
54.6448 | 290.4812 | 31.9523 | 30.3806
55.6448 | 296.0707 | 32.4272 | 30.7374
56.6448 | 301.7162 | 32.9047 | 31.1058
57.6448 | 307.2018 | 33.4182 | 31.4854
58.6448 | 312.6863 | 33.9268 | 31.8788
59.6448 | 318.1503 | 34.4497 | 32.2906
60.6448 | 323.5795 | 35.0052 | 32.7115
61.6448 | 328.9851 | 35.5611 | 33.1434
62.6448 | 334.3671 | 36.1296 | 33.6078
63.6448 | 339.6988 | 36.7336 | 34.0796
64.6448 | 345.062 | 37.337 | 34.5594
65.6448 | 350.4074 | 37.9836 | 35.0537
66.6448 | 355.5464 | 38.6398 | 35.574
67.6448 | 360.776 | 39.3108 | 36.1071
68.6448 | 365.9879 | 39.991 | 36.6557
69.6448 | 371.1207 | 40.698 | 37.2278
70.6448 | 376.2503 | 41.4239 | 37.8005
71.6448 | 381.2786 | 42.1609 | 38.3938
72.6448 | 386.3877 | 42.9461 | 39.007
73.6448 | 391.3197 | 43.729 | 39.6388
74.6448 | 396.2702 | 44.51 | 40.2802
75.6448 | 401.1556 | 45.3372 | 40.953
76.6448 | 406.1192 | 46.1944 | 41.6282
77.6448 | 410.9406 | 47.0731 | 42.33
78.6448 | 415.9238 | 47.974 | 43.0635
79.6448 | 420.7762 | 48.9364 | 43.8043
80.6448 | 425.5673 | 49.9217 | 44.5629
81.6448 | 430.3096 | 50.931 | 45.3424
82.6448 | 434.9878 | 51.9561 | 46.1389
83.6448 | 439.1419 | 53.035 | 46.9681
84.6448 | 442.9842 | 54.116 | 47.8116
85.6448 | 446.4422 | 55.2162 | 48.6783
86.6448 | 449.7264 | 56.334 | 49.562
87.6448 | 452.8756 | 57.4826 | 50.4687
88.6448 | 455.774 | 58.6466 | 51.3861
89.6448 | 458.4852 | 59.8147 | 52.3265
90.6448 | 461.0586 | 61.0044 | 53.2811
91.6448 | 463.6882 | 62.2254 | 54.2482
92.6448 | 466.238 | 63.4291 | 55.2205
93.6448 | 468.5512 | 64.6493 | 56.2131
94.6448 | 470.5998 | 65.8743 | 57.2222
95.6448 | 472.2463 | 67.1052 | 58.2308
96.6448 | 473.671 | 68.3281 | 59.2447
97.6448 | 474.8929 | 69.6055 | 60.2727
98.6448 | 475.8116 | 70.8622 | 61.306
99.6448 | 476.5257 | 72.1376 | 62.3631
100.6448 | 476.9642 | 73.3953 | 63.4046
101.6448 | 477.327 | 74.6712 | 64.4362
102.6448 | 477.4777 | 75.9433 | 65.4754
103.6448 | 477.4114 | 77.2198 | 66.5101
104.6448 | 477.1724 | 78.5032 | 67.5469
105.6448 | 477.0957 | 79.773 | 68.5736
106.6448 | 476.7448 | 81.0465 | 69.6001
107.6448 | 476.3789 | 82.3269 | 70.6305
108.6448 | 476.1761 | 83.5877 | 71.6513
109.6448 | 475.7989 | 84.8429 | 72.6617
110.6448 | 475.3974 | 86.083 | 73.6684
111.6448 | 474.9475 | 87.3295 | 74.6606
112.6448 | 474.5494 | 88.5643 | 75.647
113.6448 | 474.1055 | 89.809 | 76.6234
114.6448 | 473.7857 | 91.0381 | 77.6005
115.6448 | 473.5718 | 92.2638 | 78.5765
116.6448 | 473.4213 | 93.4742 | 79.5488
117.6448 | 473.2644 | 94.6768 | 80.5063
118.6448 | 473.0393 | 95.879 | 81.468
119.6448 | 472.8928 | 97.0651 | 82.403
120.6448 | 472.8896 | 98.2554 | 83.3435
121.6448 | 472.959 | 99.4554 | 84.2753
122.6448 | 472.9124 | 100.6421 | 85.2165
123.6448 | 472.8715 | 101.7874 | 86.1269
124.6448 | 472.9788 | 102.9509 | 87.0422
125.6448 | 472.9659 | 104.1209 | 87.9525
126.6448 | 473.0181 | 105.2692 | 88.8694
127.6448 | 473.1095 | 106.4168 | 89.7698
128.6448 | 473.2537 | 107.5648 | 90.6748
129.6448 | 473.2119 | 108.697 | 91.5657
130.6448 | 473.2713 | 109.8351 | 92.4615
131.6448 | 473.3732 | 110.9633 | 93.3602
132.6448 | 473.4162 | 112.088 | 94.2426
133.6448 | 473.3685 | 113.2102 | 95.124
134.6448 | 473.3162 | 114.307 | 96.0031
135.6448 | 473.4467 | 115.4104 | 96.8821
136.6448 | 473.5336 | 116.5095 | 97.7578
137.6448 | 473.7148 | 117.6062 | 98.6249
138.6448 | 473.9852 | 118.7023 | 99.499
139.6448 | 474.2414 | 119.7817 | 100.3707
140.6448 | 474.4028 | 120.8561 | 101.2251
141.6448 | 474.57 | 121.9258 | 102.0867
142.6448 | 474.8079 | 122.9864 | 102.9382
143.6448 | 475.0873 | 124.0375 | 103.7934
144.6448 | 475.3797 | 125.0845 | 104.6571
145.6448 | 475.635 | 126.143 | 105.5012
146.6448 | 475.9441 | 127.1988 | 106.3514
147.6448 | 476.1872 | 128.2439 | 107.1939
148.6448 | 476.496 | 129.291 | 108.0355
149.6448 | 476.7696 | 130.3152 | 108.8882
150.6448 | 476.9031 | 131.3396 | 109.7301
151.6448 | 477.0679 | 132.3696 | 110.5622
152.6448 | 477.2614 | 133.3912 | 111.4005
153.6448 | 477.3455 | 134.4039 | 112.2239
154.6448 | 477.4297 | 135.4078 | 113.0485
155.6448 | 477.5435 | 136.3982 | 113.8696
156.6448 | 477.57 | 137.3882 | 114.6897
157.6448 | 477.5538 | 138.3926 | 115.5027
158.6448 | 477.5323 | 139.3529 | 116.3142
159.6448 | 477.5811 | 140.3194 | 117.1167
160.6448 | 477.5641 | 141.2599 | 117.912
161.6448 | 477.5587 | 142.1957 | 118.7108
162.6448 | 477.4869 | 143.1133 | 119.4934
163.6448 | 477.3664 | 144.0222 | 120.2601
164.6448 | 477.2278 | 144.9302 | 121.0228
165.6448 | 477.2388 | 145.8237 | 121.7812
166.6448 | 477.3094 | 146.7066 | 122.5224
167.6448 | 477.3358 | 147.5942 | 123.2523
168.6448 | 477.3321 | 148.4412 | 123.9648
169.6448 | 477.1365 | 149.3022 | 124.6691
170.6448 | 477.1943 | 150.14 | 125.3634
171.6448 | 477.1569 | 150.9837 | 126.0414
172.6448 | 477.0689 | 151.8123 | 126.7045
173.6448 | 477.0324 | 152.6218 | 127.3483
174.6448 | 476.9543 | 153.4393 | 127.978
175.6448 | 476.9223 | 154.2529 | 128.5575
176.6448 | 476.8395 | 155.0634 | 129.1099
177.6448 | 476.8362 | 155.8566 | 129.6531
178.6448 | 476.8561 | 156.67 | 130.1956
179.6448 | 476.8937 | 157.4671 | 130.7623
180.6448 | 476.9592 | 158.2591 | 131.3276
181.6448 | 476.9706 | 159.0542 | 131.9049
182.6448 | 476.9238 | 159.8574 | 132.5012
183.6448 | 476.9613 | 160.6546 | 133.099
184.6448 | 476.9052 | 161.4331 | 133.6942
185.6448 | 476.9545 | 162.2224 | 134.2949
186.6448 | 476.945 | 162.9996 | 134.9031
187.6448 | 477.0068 | 163.7651 | 135.5134
188.6448 | 477.0853 | 164.5507 | 136.129
189.6448 | 477.2355 | 165.3245 | 136.735
190.6448 | 477.2817 | 166.0933 | 137.3557
191.6448 | 477.3587 | 166.8676 | 137.9803
192.6448 | 477.3627 | 167.6329 | 138.6147
193.6448 | 477.348 | 168.3853 | 139.2356
194.6448 | 477.3997 | 169.1637 | 139.8681
195.6448 | 477.453 | 169.9104 | 140.4958
196.6448 | 477.5384 | 170.6731 | 141.1355
197.6448 | 477.5798 | 171.4351 | 141.7721
198.6448 | 477.5647 | 172.1988 | 142.4231
199.6448 | 477.6263 | 172.965 | 143.0794
200.6448 | 477.4307 | 173.7193 | 143.7317
201.6448 | 477.3496 | 174.5007 | 144.4048
202.6448 | 477.3153 | 175.2773 | 145.0757
203.6448 | 477.3352 | 176.0418 | 145.7541
204.6448 | 477.2479 | 176.8089 | 146.4517
205.6448 | 477.0788 | 177.5794 | 147.1542
206.6448 | 476.947 | 178.34 | 147.8641
207.6448 | 476.8725 | 179.1227 | 148.5865
208.6448 | 476.8258 | 179.8779 | 149.3098
209.6448 | 476.8713 | 180.6558 | 150.052
210.6448 | 476.8441 | 181.4298 | 150.791
211.6448 | 476.7116 | 182.2013 | 151.5466
212.6448 | 476.7545 | 182.9672 | 152.3058
213.6448 | 476.7239 | 183.7446 | 153.0597
214.6448 | 476.7101 | 184.5088 | 153.838
215.6448 | 476.7763 | 185.267 | 154.6127
216.6448 | 476.727 | 186.0312 | 155.3879
217.6448 | 476.8266 | 186.813 | 156.1751
218.6448 | 476.9106 | 187.5732 | 156.9705
219.6448 | 476.8677 | 188.3259 | 157.7576
220.6448 | 476.8205 | 189.0824 | 158.5446
221.6448 | 476.8301 | 189.84 | 159.3321
222.6448 | 476.7833 | 190.5827 | 160.1242
223.6448 | 476.7406 | 191.3492 | 160.9236
224.6448 | 476.7669 | 192.095 | 161.7177
225.6448 | 476.7697 | 192.8307 | 162.5088
226.6448 | 476.7986 | 193.5868 | 163.3115
227.6448 | 476.8555 | 194.3238 | 164.1027
228.6448 | 476.8327 | 195.0543 | 164.9072
229.6448 | 476.7697 | 195.7875 | 165.7015
230.6448 | 476.7219 | 196.5277 | 166.4938
231.6448 | 476.7051 | 197.2774 | 167.3037
232.6448 | 476.6574 | 198.0365 | 168.0956
233.6448 | 476.5415 | 198.7531 | 168.8835
234.6448 | 476.6138 | 199.4549 | 169.6764
235.6448 | 476.6825 | 200.1322 | 170.4652
236.6448 | 476.7129 | 200.7747 | 171.251
237.6448 | 476.7203 | 201.3829 | 172.0309
238.6448 | 476.7586 | 201.9466 | 172.8245
239.6448 | 476.8237 | 202.4726 | 173.6019
240.6448 | 476.9843 | 202.9957 | 174.3823
241.6448 | 477.1146 | 203.4782 | 175.1663
242.6448 | 477.1855 | 203.9655 | 175.9445
243.6448 | 477.2372 | 204.4181 | 176.7267
244.6448 | 477.4073 | 204.8847 | 177.5071
245.6448 | 477.4886 | 205.3492 | 178.2809
246.6448 | 477.5221 | 205.8319 | 179.053
247.6448 | 477.4953 | 206.3254 | 179.8301
248.6448 | 477.413 | 206.7875 | 180.5995
249.6448 | 477.3748 | 207.297 | 181.3712
250.6448 | 477.3795 | 207.8558 | 182.1429
251.6448 | 477.2408 | 208.3245 | 182.9124
252.6448 | 477.2078 | 208.728 | 183.6648
253.6448 | 477.1825 | 209.0334 | 184.4251
254.6448 | 477.1875 | 209.2436 | 185.1831
255.6448 | 477.1082 | 209.4995 | 185.9418
256.6448 | 476.9531 | 209.8453 | 186.7028
257.6448 | 476.8071 | 210.1453 | 187.4569
258.6448 | 476.6902 | 210.3825 | 188.2176
259.6448 | 476.5817 | 210.5964 | 188.9778
260.6448 | 476.4874 | 210.7354 | 189.7437
261.6448 | 476.2853 | 210.8411 | 190.489
262.6448 | 476.1277 | 210.9619 | 191.2396
263.6448 | 476.0574 | 211.1505 | 191.988
264.6448 | 475.943 | 211.3012 | 192.7313
265.6448 | 475.8734 | 211.4162 | 193.4698
266.6448 | 475.8481 | 211.5778 | 194.2054
267.6448 | 475.7668 | 211.7952 | 194.9332
268.6448 | 475.7911 | 212.0254 | 195.6649
269.6448 | 475.8482 | 212.3114 | 196.3984
270.6448 | 475.7854 | 212.641 | 197.1279
271.6448 | 475.7054 | 213.0406 | 197.8525
272.6448 | 475.6423 | 213.4679 | 198.5836
273.6448 | 475.5174 | 213.955 | 199.3126
274.6448 | 475.5091 | 214.5372 | 200.0445
275.6448 | 475.485 | 215.1639 | 200.7701
276.6448 | 475.4842 | 215.8049 | 201.4972
277.6448 | 475.434 | 216.444 | 202.2019
278.6448 | 475.3578 | 217.1445 | 202.9101
279.6448 | 475.4022 | 217.8811 | 203.6143
280.6448 | 475.2697 | 219.0255 | 204.3114
281.6448 | 475.1713 | 221.6758 | 204.9967
282.6448 | 475.0797 | 223.296 | 205.6617
283.6448 | 474.9822 | 224.5212 | 206.3282
284.6448 | 474.9962 | 225.5357 | 206.97
285.6448 | 475.0386 | 226.3712 | 207.5949
286.6448 | 474.9975 | 227.1313 | 208.2049
287.6448 | 475.059 | 227.8055 | 208.7884
288.6448 | 475.0769 | 228.4201 | 209.3736
289.6448 | 475.1167 | 228.9882 | 209.9453
290.6448 | 475.1433 | 229.5491 | 210.5125
291.6448 | 475.0626 | 230.0918 | 211.079
292.6448 | 475.0635 | 230.615 | 211.6397
293.6448 | 475.181 | 231.1629 | 212.2088
294.6448 | 475.2969 | 231.7105 | 212.7839
295.6448 | 475.4199 | 232.268 | 213.3535
296.6448 | 475.5013 | 232.8306 | 213.9211
297.6448 | 475.5081 | 233.4113 | 214.4994
298.6448 | 475.5733 | 233.9879 | 215.0655
299.6448 | 475.5731 | 234.5974 | 215.6503
300.6448 | 475.648 | 235.2453 | 216.2097
301.6448 | 475.8246 | 235.8536 | 216.7646
302.6448 | 476.0403 | 236.4474 | 217.2998
303.6448 | 476.2543 | 237.0069 | 217.8014
304.6448 | 476.6827 | 237.5532 | 218.2815
305.6448 | 477.1556 | 238.0727 | 218.7636
306.6448 | 477.5108 | 238.6004 | 219.2236
307.6448 | 477.9093 | 239.1335 | 219.6647
308.6448 | 478.1227 | 239.76 | 220.1193
309.6448 | 478.3217 | 240.4732 | 220.529
310.6448 | 478.4374 | 241.2432 | 220.937
311.6448 | 478.4206 | 242.1422 | 221.3434
312.6448 | 478.2609 | 243.2305 | 221.7861
313.6448 | 478.3323 | 244.4195 | 222.254
314.6448 | 478.3456 | 245.6601 | 222.9234
315.6448 | 478.284 | 246.9537 | 223.6942
316.6448 | 478.1489 | 248.1136 | 224.8009
317.6448 | 477.9145 | 249.1502 | 226.5397
318.6448 | 477.6772 | 250.137 | 229.2527
319.6448 | 477.3146 | 251.1275 | 233.0042
320.6448 | 476.8943 | 251.6907 | 237.7131
321.6448 | 476.6189 | 252.4147 | 243.2228
322.6448 | 476.228 | 253.4216 | 249.2406
323.6448 | 475.7936 | 254.4177 | 255.4877
324.6448 | 475.357 | 255.4531 | 262.9278
325.6448 | 475.0658 | 256.3705 | 270.5884
326.6448 | 474.7455 | 257.5983 | 276.2242
327.6448 | 474.4717 | 258.8138 | 282.3425
328.6448 | 474.1992 | 260.0553 | 289.7073
329.6448 | 473.9548 | 261.0086 | 294.355
330.6448 | 473.6624 | 261.9966 | 301.4225
331.6448 | 473.3901 | 262.9496 | 306.1855
332.6448 | 473.1566 | 264.0692 | 310.4643
333.6448 | 472.8754 | 265.1696 | 315.049
334.6448 | 472.4972 | 266.1883 | 319.5938
335.6448 | 472.1756 | 267.2712 | 323.6924
336.6448 | 472.009 | 268.3255 | 326.514
337.6448 | 471.6882 | 269.3248 | 330.0089
338.6448 | 471.498 | 270.3187 | 332.3069
339.6448 | 471.3065 | 271.478 | 334.9511
340.6448 | 471.0168 | 272.6327 | 336.3583
341.6448 | 470.7099 | 274.0482 | 338.0077
342.6448 | 470.5063 | 275.3452 | 338.3155
343.6448 | 470.4081 | 275.9108 | 339.8703
344.6448 | 470.2981 | 276.7444 | 340.419
345.6448 | 470.1251 | 277.6416 | 341.2331
346.6448 | 470.0268 | 278.5776 | 342.7073
347.6448 | 469.9616 | 278.284 | 343.4148
348.6448 | 469.8476 | 280.4511 | 344.6412
349.6448 | 469.8771 | 279.9168 | 346.0936
350.6448 | 469.8473 | 282.9779 | 347.1255
351.6448 | 469.7669 | 283.8784 | 347.2029
352.6448 | 469.7472 | 284.4467 | 348.9713
353.6448 | 469.5985 | 286.0472 | 352.0857
354.6448 | 469.5722 | 288.4653 | 354.7013
355.6448 | 469.4684 | 289.2591 | 358.6498
356.6448 | 469.3786 | 291.6259 | 360.7708
357.6448 | 469.3288 | 293.5863 | 363.48
358.6448 | 469.2753 | 296.0216 | 365.7273
359.6448 | 469.3337 | 297.1065 | 368.2411
360.6448 | 469.2679 | 298.4682 | 370.6776
361.6448 | 469.2378 | 299.9048 | 373.526
362.6448 | 469.2736 | 301.5011 | 376.2291
363.6448 | 469.2689 | 303.0437 | 376.6858
364.6448 | 469.3383 | 304.8233 | 378.4983
365.6448 | 469.287 | 306.0897 | 381.1398
366.6448 | 469.325 | 307.7661 | 383.5204
367.6448 | 469.2994 | 309.435 | 386.85
368.6448 | 469.3936 | 310.9418 | 388.9651
369.6448 | 469.4102 | 312.9383 | 392.0321
370.6448 | 469.4696 | 315.3447 | 394.6667
371.6448 | 469.5684 | 316.6933 | 397.2539
372.6448 | 469.5986 | 318.5328 | 400.3422
373.6448 | 469.6786 | 320.8825 | 402.8909
374.6448 | 469.701 | 323.2586 | 405.1142
375.6448 | 469.7589 | 324.896 | 407.4382
376.6448 | 469.6981 | 327.7617 | 409.6391
377.6448 | 469.7612 | 330.3082 | 412.5634
378.6448 | 469.7745 | 332.3044 | 415.0491
379.6448 | 469.7871 | 334.8221 | 416.8893
380.6448 | 469.5526 | 337.2997 | 419.916
381.6448 | 469.5327 | 340.4826 | 422.6237
382.6448 | 469.4852 | 342.4774 | 424.4809
383.6448 | 469.4471 | 345.2339 | 428.1162
384.6448 | 469.4647 | 347.9949 | 430.3057
385.6448 | 469.5372 | 350.7817 | 432.5942
386.6448 | 469.4652 | 353.7207 | 431.9282
387.6448 | 469.4221 | 356.7084 | 433.3483
388.6448 | 469.366 | 359.9745 | 435.1572
389.6448 | 469.3764 | 363.4484 | 438.0236
390.6448 | 469.3252 | 366.5263 | 439.8437
391.6448 | 469.2443 | 368.9556 | 440.9687
392.6448 | 469.2111 | 370.9219 | 441.2926
393.6448 | 469.1995 | 373.4306 | 442.0387
394.6448 | 469.3134 | 375.9536 | 442.6318
395.6448 | 469.461 | 378.429 | 443.8556
396.6448 | 469.4314 | 380.2617 | 444.4922
397.6448 | 469.4948 | 382.0531 | 442.7647
398.6448 | 469.4532 | 384.3303 | 443.8413
399.6448 | 469.366 | 386.7494 | 443.2961
400.6448 | 469.3713 | 388.2942 | 443.9253
401.6448 | 469.3213 | 390.5564 | 443.9173
402.6448 | 469.3349 | 391.8307 | 445.2076
403.6448 | 469.3263 | 393.4964 | 445.5271
404.6448 | 469.3355 | 395.3492 | 446.4295
405.6448 | 469.3348 | 397.527 | 447.0214
406.6448 | 469.2728 | 398.496 | 447.6343
407.6448 | 469.2662 | 398.3197 | 447.7857
408.6448 | 469.1641 | 399.328 | 448.0533
409.6448 | 469.1792 | 399.2411 | 448.3051
410.6448 | 469.2443 | 398.8079 | 447.9933
411.6448 | 469.2372 | 397.4577 | 447.6023
412.6448 | 469.1835 | 396.8025 | 446.6079
413.6448 | 469.188 | 396.3953 | 446.2698
414.6448 | 469.1667 | 395.5497 | 444.8489
415.6448 | 469.1434 | 394.8245 | 443.5511
416.6448 | 469.1445 | 394.7476 | 441.8859
417.6448 | 469.2013 | 394.5712 | 440.341
418.6448 | 469.2811 | 393.9056 | 438.4189
419.6448 | 469.2787 | 394.9067 | 436.3842
420.6448 | 469.3815 | 394.1413 | 434.1105
421.6448 | 469.4024 | 393.5657 | 431.2501
422.6448 | 469.457 | 393.4345 | 428.754
423.6448 | 469.5371 | 393.2904 | 426.099
424.6448 | 469.6615 | 393.4843 | 423.7775
425.6448 | 469.7258 | 393.6621 | 421.4001
426.6448 | 469.6703 | 393.523 | 419.0876
427.6448 | 469.6143 | 393.9629 | 416.9854
428.6448 | 469.6771 | 394.4085 | 414.9551
429.6448 | 469.7033 | 394.5162 | 413.0248
430.6448 | 469.7001 | 394.604 | 411.2168
431.6448 | 469.6923 | 394.8303 | 409.4358
432.6448 | 469.6456 | 394.7392 | 407.737
433.6448 | 469.6658 | 395.3779 | 406.2734
434.6448 | 469.6954 | 395.2873 | 405.1879
435.6448 | 469.7375 | 395.2589 | 403.9882
436.6448 | 469.78 | 395.6424 | 403.055
437.6448 | 469.7528 | 395.8126 | 402.3001
438.6448 | 469.7541 | 395.9012 | 401.5485
439.6448 | 469.7312 | 395.7606 | 400.8962
440.6448 | 469.6844 | 395.9371 | 400.0494
441.6448 | 469.7112 | 396.3967 | 399.3786
442.6448 | 469.7473 | 396.7683 | 398.8428
443.6448 | 469.7706 | 397.0123 | 398.4208
444.6448 | 469.8341 | 397.2564 | 397.9018
445.6448 | 469.8196 | 397.6716 | 397.6105
446.6448 | 469.7534 | 397.7584 | 397.4517
447.6448 | 469.7893 | 398.0385 | 397.3939
448.6448 | 469.7649 | 398.2335 | 397.2435
449.6448 | 469.8224 | 398.5172 | 397.1233
450.6448 | 469.864 | 398.8953 | 397.1119
451.6448 | 469.8565 | 399.3529 | 395.726
452.6448 | 469.7718 | 399.6361 | 394.4279
453.6448 | 469.7837 | 399.9301 | 393.7909
454.6448 | 469.7703 | 400.3656 | 393.5964
455.6448 | 469.7693 | 400.8765 | 393.4512
456.6448 | 469.7028 | 401.1525 | 393.0977
457.6448 | 469.7178 | 401.4823 | 393.315
458.6448 | 469.7781 | 401.9211 | 393.3822
459.6448 | 469.8249 | 402.1815 | 393.1996
460.6448 | 469.8846 | 401.999 | 393.4072
461.6448 | 469.961 | 402.0682 | 393.8224
462.6448 | 470.0216 | 402.3354 | 394.2429
463.6448 | 470.0461 | 402.724 | 394.4983
464.6448 | 469.9915 | 403.294 | 395.1488
465.6448 | 469.9522 | 404.2137 | 395.6087
466.6448 | 470.0274 | 404.6307 | 396.0856
467.6448 | 470.0987 | 405.2441 | 396.8588
468.6448 | 470.0688 | 405.9752 | 397.4931
469.6448 | 470.0168 | 406.799 | 398.0704
470.6448 | 470.0227 | 407.8178 | 398.6883
471.6448 | 470.0921 | 408.4503 | 399.65
472.6448 | 470.0265 | 409.8297 | 400.0637
473.6448 | 469.9119 | 410.8359 | 400.5069
474.6448 | 469.929 | 411.8849 | 401.0058
475.6448 | 469.9011 | 412.9459 | 401.8078
476.6448 | 469.9044 | 414.1568 | 402.7691
477.6448 | 469.8645 | 415.1797 | 403.17
478.6448 | 469.8878 | 416.5157 | 404.2128
479.6448 | 469.7658 | 417.4622 | 404.6313
480.6448 | 469.8094 | 418.7811 | 405.3456
481.6448 | 469.8138 | 420.3539 | 405.9984
482.6448 | 469.8121 | 421.7897 | 406.7836
483.6448 | 469.8271 | 423.3024 | 407.5175
484.6448 | 469.81 | 424.6126 | 408.2146
485.6448 | 469.8748 | 425.851 | 408.9298
486.6448 | 469.9357 | 427.0759 | 409.5229
487.6448 | 469.9336 | 428.5366 | 410.2549
488.6448 | 469.9782 | 430.3002 | 410.8175
489.6448 | 470.0305 | 431.8433 | 411.6199
490.6448 | 470.0085 | 433.2147 | 412.5717
491.6448 | 469.9717 | 434.5737 | 413.2505
492.6448 | 469.9081 | 436.0721 | 413.8197
493.6448 | 469.8668 | 437.178 | 414.4997
494.6448 | 469.9011 | 438.2977 | 415.1535
495.6448 | 469.8769 | 439.6127 | 415.7142
496.6448 | 469.9896 | 440.936 | 416.3291
497.6448 | 469.9932 | 442.3292 | 416.8879
498.6448 | 469.9939 | 444.1341 | 417.5122
499.6448 | 469.8994 | 445.4345 | 418.1121
500.6448 | 469.8949 | 446.8838 | 418.8276
501.6448 | 469.9536 | 448.7658 | 419.3726
502.6448 | 469.9725 | 450.4791 | 419.9508
503.6448 | 469.9653 | 452.2989 | 420.188
504.6448 | 469.8884 | 453.6282 | 420.7289
505.6448 | 469.7741 | 455.4556 | 421.1658
506.6448 | 469.7078 | 456.7542 | 421.4687
507.6448 | 469.7163 | 458.0958 | 421.9386
508.6448 | 469.6791 | 459.3811 | 422.334
509.6448 | 469.7296 | 460.5143 | 422.7025
510.6448 | 469.6909 | 461.9253 | 423.0837
511.6448 | 469.7126 | 462.9589 | 423.5739
512.6448 | 469.7422 | 464.0375 | 424.0265
513.6448 | 469.8054 | 465.0887 | 424.4872
514.6448 | 469.8583 | 465.9951 | 424.9996
515.6448 | 469.8199 | 466.435 | 425.6429
516.6448 | 469.7842 | 467.1552 | 426.0115
517.6448 | 469.7367 | 468.0812 | 426.4736
518.6448 | 469.7623 | 468.7736 | 426.9617
519.6448 | 469.7933 | 469.3316 | 427.4662
520.6448 | 469.8271 | 469.8177 | 428.1121
521.6448 | 469.8454 | 470.8639 | 428.7857
522.6448 | 469.9004 | 471.2184 | 429.8207
523.6448 | 469.8639 | 471.7043 | 430.4137
524.6448 | 469.8686 | 472.148 | 431.0938
525.6448 | 469.8667 | 472.6318 | 431.6076
526.6448 | 469.9451 | 473.0722 | 432.0578
527.6448 | 469.9851 | 474.337 | 432.5989
528.6448 | 469.9704 | 475.0018 | 433.1484
529.6448 | 469.9664 | 475.639 | 433.6069
530.6448 | 469.9966 | 476.7312 | 434.1629
531.6448 | 469.9664 | 477.503 | 434.5369
532.6448 | 469.9568 | 478.1887 | 435.0865
533.6448 | 469.9726 | 478.7357 | 435.3941
534.6448 | 469.9983 | 479.3913 | 435.6726
535.6448 | 469.9767 | 480.0363 | 436.1277
536.6448 | 469.929 | 480.8794 | 436.6161
537.6448 | 469.9509 | 481.6608 | 437.0926
538.6448 | 469.9437 | 482.1688 | 437.3746
539.6448 | 469.9843 | 483.0583 | 437.741
540.6448 | 470.0548 | 483.7342 | 438.2274
541.6448 | 470.0482 | 484.7501 | 438.439
542.6448 | 469.9514 | 485.3374 | 438.8418
543.6448 | 469.8636 | 485.6548 | 439.1264
544.6448 | 469.8222 | 485.7647 | 439.5085
545.6448 | 469.7932 | 485.8091 | 439.7698
546.6448 | 469.7834 | 485.7026 | 440.1351
547.6448 | 469.7594 | 485.6782 | 440.1596
548.6448 | 469.6768 | 485.7172 | 440.4657
549.6448 | 469.567 | 485.5407 | 440.8041
550.6448 | 469.6113 | 485.6792 | 440.8916
551.6448 | 469.6439 | 485.1761 | 441.3745
552.6448 | 469.565 | 484.8589 | 441.7495
553.6448 | 469.5544 | 485.1477 | 442.0666
554.6448 | 469.6233 | 484.8267 | 442.3311
555.6448 | 469.6254 | 483.9801 | 442.7135
556.6448 | 469.6136 | 484.0238 | 442.9738
557.6448 | 469.6172 | 483.3625 | 443.4173
558.6448 | 469.5169 | 482.7825 | 443.8108
559.6448 | 469.4201 | 482.376 | 444.0558
560.6448 | 469.3816 | 481.7201 | 444.5659
561.6448 | 469.3788 | 481.0098 | 445.0026
562.6448 | 469.3671 | 480.5162 | 445.5083
563.6448 | 469.3828 | 480.9285 | 446.0577
564.6448 | 469.3622 | 480.7226 | 446.421
565.6448 | 469.368 | 480.4935 | 446.7353
566.6448 | 469.3165 | 480.5454 | 447.0577
567.6448 | 469.2926 | 480.524 | 447.5738
568.6448 | 469.3724 | 480.2901 | 447.9346
569.6448 | 469.4389 | 480.6799 | 448.2796
570.6448 | 469.4544 | 480.5422 | 448.1601
571.6448 | 469.472 | 479.5701 | 448.6425
572.6448 | 469.517 | 478.7781 | 449.3281
573.6448 | 469.5901 | 478.1081 | 449.6253
574.6448 | 469.6459 | 478.3902 | 449.8323
575.6448 | 469.7179 | 477.8265 | 449.846
576.6448 | 469.7218 | 478.1188 | 450.2039
577.6448 | 469.836 | 477.8511 | 450.4188
578.6448 | 469.8641 | 477.2933 | 450.4929
579.6448 | 469.9012 | 475.9092 | 451.231
580.6448 | 469.9672 | 475.3497 | 451.7155
581.6448 | 469.9746 | 474.6978 | 452.0964
582.6448 | 469.9501 | 474.2385 | 452.7025
583.6448 | 469.926 | 473.3758 | 452.9532
584.6448 | 470.0142 | 474.939 | 453.5195
585.6448 | 470.0379 | 473.901 | 453.971
586.6448 | 469.9981 | 472.7262 | 454.2984
587.6448 | 470.0115 | 471.3982 | 454.7086
588.6448 | 469.9712 | 469.6889 | 454.8725
589.6448 | 469.8781 | 470.6011 | 455.4102
590.6448 | 469.8537 | 471.8299 | 456.1995
591.6448 | 469.8588 | 470.1912 | 456.5255
592.6448 | 469.8198 | 468.0715 | 456.7636
593.6448 | 469.8085 | 467.8637 | 457.1687
594.6448 | 469.7502 | 470.4529 | 457.779
595.6448 | 469.7138 | 468.8926 | 458.1859
596.6448 | 469.6882 | 468.0784 | 458.5977
597.6448 | 469.6447 | 468.4094 | 458.8904
598.6448 | 469.6739 | 465.7222 | 459.1939
599.6448 | 469.5587 | 470.7901 | 460.1514
600.6448 | 469.5476 | 462.4599 | 459.9703
601.6448 | 469.5574 | 456.0021 | 459.9481
602.6448 | 469.5697 | 457.6704 | 460.8944
603.6448 | 469.5837 | 444.3967 | 460.1493
604.6448 | 469.5125 | 452.5241 | 461.4677
605.6448 | 469.4806 | 449.9849 | 461.9403
606.6448 | 469.5363 | 442.9015 | 462.3295
607.6448 | 469.6088 | 448.1012 | 462.984
608.6448 | 469.6576 | 450.8239 | 464.2515
609.6448 | 469.6666 | 451.9494 | 464.6608
610.6448 | 469.5948 | 451.3528 | 465.2457
611.6448 | 469.521 | 398.0807 | 462.5517
612.6448 | 469.4912 | 395.0876 | 462.5913
613.6448 | 469.4527 | 394.3246 | 463.2905
614.6448 | 469.359 | 394.1663 | 463.4563
615.6448 | 469.3164 | 391.2224 | 463.6288
616.6448 | 469.3473 | 390.5139 | 464.1342
617.6448 | 469.3494 | 387.613 | 465.0536
618.6448 | 469.4 | 383.6646 | 465.1285
619.6448 | 469.3636 | 384.6619 | 465.7029
620.6448 | 469.315 | 376.7574 | 465.1544
621.6448 | 469.306 | 372.5538 | 465.706
622.6448 | 469.2553 | 373.8814 | 466.1095
623.6448 | 469.2512 | 370.129 | 466.0098
624.6448 | 469.2394 | 368.5247 | 466.1343
625.6448 | 469.2634 | 366.695 | 465.7845
626.6448 | 469.261 | 364.7637 | 467.5593
627.6448 | 469.2078 | 362.7847 | 467.3452
628.6448 | 469.1479 | 364.0917 | 467.7722
629.6448 | 469.114 | 357.7061 | 468.5117
630.6448 | 469.1323 | 352.0587 | 467.8136
631.6448 | 469.0965 | 346.0138 | 467.8724
632.6448 | 469.0993 | 349.0575 | 468.7474
633.6448 | 469.0583 | 347.235 | 469.0646
634.6448 | 469.1199 | 351.1551 | 469.6551
635.6448 | 469.1382 | 350.5139 | 470.1528
636.6448 | 469.2043 | 349.7933 | 470.2234
637.6448 | 469.2148 | 348.3436 | 470.4813
638.6448 | 469.3236 | 341.0591 | 470.4395
639.6448 | 469.3837 | 340.8463 | 470.582
640.6448 | 469.4017 | 336.9056 | 470.6893
641.6448 | 469.4371 | 335.7327 | 470.7132
642.6448 | 469.3921 | 331.3428 | 470.9707
643.6448 | 469.4468 | 331.2429 | 471.1527
644.6448 | 469.49 | 326.4482 | 471.3542
645.6448 | 469.5172 | 323.1296 | 471.6708
646.6448 | 469.5204 | 320.1781 | 471.2178
647.6448 | 469.5626 | 323.5837 | 471.137
648.6448 | 469.6035 | 321.6754 | 470.7933
649.6448 | 469.6809 | 325.8257 | 471.5504
650.6448 | 469.65 | 324.8339 | 471.1354
651.6448 | 469.6066 | 324.4232 | 471.2253
652.6448 | 469.6692 | 328.5894 | 470.8009
653.6448 | 469.7493 | 327.2921 | 470.9122
654.6448 | 469.7416 | 329.8982 | 470.7109
655.6448 | 469.7562 | 330.4675 | 471.1543
656.6448 | 469.7234 | 334.9724 | 470.7798
657.6448 | 469.6975 | 339.6554 | 471.1373
658.6448 | 469.6683 | 339.2617 | 471.1295
659.6448 | 469.5935 | 338.704 | 471.0038
660.6448 | 469.5224 | 339.2283 | 469.5878
661.6448 | 469.4904 | 340.8518 | 469.659
662.6448 | 469.4467 | 340.8103 | 469.4324
663.6448 | 469.3229 | 342.2913 | 469.7172
664.6448 | 469.1914 | 329.7237 | 467.9241
665.6448 | 469.1531 | 326.1426 | 467.4334
666.6448 | 469.1408 | 329.9143 | 467.3389
667.6448 | 469.1543 | 320.1757 | 467.1637
668.6448 | 469.0472 | 318.4797 | 467.5561
669.6448 | 468.953 | 314.799 | 466.9986
670.6448 | 469.0586 | 320.2577 | 466.5164
671.6448 | 469.1425 | 320.5659 | 466.7593
672.6448 | 469.3085 | 324.1049 | 466.4517
673.6448 | 469.581 | 326.1482 | 466.5216
674.6448 | 469.6496 | 334.0293 | 466.6996
675.6448 | 469.753 | 340.7374 | 466.5087
676.6448 | 469.939 | 344.9679 | 466.0718
677.6448 | 470.2062 | 537.9788 | 485.0827
678.6448 | 470.3816 | 538.6956 | 485.4269
679.6448 | 470.6097 | 516.1301 | 483.2283
680.6448 | 470.7582 | 516.4391 | 483.2721
681.6448 | 470.9013 | 516.8824 | 483.4184
682.6448 | 471.0093 | 517.353 | 483.3535
683.6448 | 471.1063 | 517.3845 | 483.5754
684.6448 | 471.0948 | 517.2333 | 483.6443
685.6448 | 471.1936 | 517.5059 | 483.4459
686.6448 | 471.4489 | 518.1114 | 483.6324
687.6448 | 471.6512 | 518.1244 | 483.6745
688.6448 | 471.7273 | 518.1843 | 483.6123
689.6448 | 471.723 | 518.6178 | 483.6872
690.6448 | 471.7763 | 518.6225 | 483.6974
691.6448 | 471.9243 | 519.0673 | 483.5848
692.6448 | 471.9464 | 519.3739 | 483.3
693.6448 | 471.9466 | 519.4077 | 483.2676
694.6448 | 472.0228 | 519.7692 | 483.3537
695.6448 | 471.9258 | 520.087 | 483.1259
696.6448 | 471.7633 | 520.1017 | 483.2554
697.6448 | 471.6788 | 520.4912 | 483.3817
698.6448 | 471.7131 | 520.689 | 483.2023
699.6448 | 471.7641 | 521.1976 | 483.2847
700.6448 | 471.8223 | 521.5964 | 483.0965
701.6448 | 471.7252 | 521.5835 | 483.0787
702.6448 | 471.5703 | 522.0893 | 483.1168
703.6448 | 471.5382 | 522.1823 | 482.9879
704.6448 | 471.5004 | 522.3925 | 483.5052
705.6448 | 471.4592 | 522.8066 | 483.1544
706.6448 | 471.4036 | 523.271 | 483.2745
707.6448 | 471.272 | 523.4705 | 483.3041
708.6448 | 471.2043 | 524.2522 | 483.4529
709.6448 | 471.1329 | 524.5848 | 483.623
710.6448 | 471.0787 | 525.2338 | 483.7617
711.6448 | 471.003 | 525.4393 | 484.013
712.6448 | 471.0665 | 526.0397 | 484.1999
713.6448 | 471.1323 | 526.5741 | 484.2327
714.6448 | 471.1614 | 527.3854 | 484.5478
715.6448 | 471.1996 | 527.751 | 484.9862
716.6448 | 471.1519 | 528.22 | 485.1899
717.6448 | 471.0348 | 528.7606 | 485.5536
718.6448 | 470.9634 | 529.1277 | 485.906
719.6448 | 470.8951 | 529.873 | 486.2033
720.6448 | 470.8371 | 530.8698 | 486.5971
721.6448 | 470.8849 | 531.3139 | 486.7677
722.6448 | 470.8729 | 531.648 | 486.9377
723.6448 | 470.8259 | 532.3284 | 487.3139
724.6448 | 470.8004 | 532.9125 | 487.6908
725.6448 | 470.8046 | 533.664 | 487.9116
726.6448 | 470.7614 | 534.3572 | 488.3002
727.6448 | 470.7262 | 535.1843 | 488.4684
728.6448 | 470.6925 | 535.6437 | 488.7424
729.6448 | 470.5568 | 535.9369 | 489.1245
730.6448 | 470.4159 | 536.8096 | 489.0414
731.6448 | 470.3363 | 537.4262 | 489.2987
732.6448 | 470.2866 | 537.8273 | 489.6855
733.6448 | 470.2497 | 538.4594 | 489.8242
734.6448 | 470.2416 | 538.9916 | 490.1471
735.6448 | 470.1933 | 539.6407 | 490.3502
736.6448 | 470.3552 | 539.9984 | 490.5611
737.6448 | 470.3522 | 540.3326 | 490.8949
738.6448 | 470.3316 | 540.9525 | 491.3412
739.6448 | 470.2849 | 541.313 | 491.559
740.6448 | 470.2345 | 541.9492 | 492.022
741.6448 | 470.2795 | 542.3697 | 492.1473
742.6448 | 470.3666 | 542.695 | 492.5557
743.6448 | 470.3941 | 543.1964 | 492.9788
744.6448 | 470.3843 | 543.6622 | 493.2648
745.6448 | 470.3871 | 544.1997 | 493.4895
746.6448 | 470.387 | 544.6824 | 493.8711
747.6448 | 470.4418 | 545.114 | 494.224
748.6448 | 470.4795 | 545.871 | 494.4263
749.6448 | 470.4728 | 546.1904 | 494.7823
750.6448 | 470.5282 | 546.8044 | 495.2051
751.6448 | 470.6194 | 547.4736 | 495.5656
752.6448 | 470.6665 | 548.1183 | 495.8016
753.6448 | 470.6604 | 548.2495 | 496.1658
754.6448 | 470.6276 | 548.9881 | 496.5877
755.6448 | 470.5872 | 549.28 | 497.0232
756.6448 | 470.6553 | 549.6035 | 497.428
757.6448 | 470.6582 | 550.1439 | 497.6298
758.6448 | 470.722 | 550.4803 | 497.7724
759.6448 | 470.7713 | 550.6766 | 498.1678
760.6448 | 470.7482 | 551.1876 | 498.5561
761.6448 | 470.7509 | 551.6481 | 498.8591
762.6448 | 470.9334 | 552.2146 | 499.3307
763.6448 | 471.0287 | 552.6451 | 499.7161
764.6448 | 471.1734 | 553.2317 | 500.012
765.6448 | 471.2334 | 553.2571 | 500.2434
766.6448 | 471.2767 | 553.7781 | 500.7163
767.6448 | 471.3738 | 554.0515 | 501.1877
768.6448 | 471.4797 | 554.2263 | 501.5398
769.6448 | 471.5018 | 554.8205 | 502.0546
770.6448 | 471.4451 | 555.3478 | 502.5409
771.6448 | 471.3989 | 555.7031 | 503.0602
772.6448 | 471.4329 | 555.8941 | 503.5288
773.6448 | 471.5072 | 556.2947 | 503.9874
774.6448 | 471.4854 | 556.676 | 504.6048
775.6448 | 471.3666 | 557.2627 | 505.154
776.6448 | 471.2961 | 557.6465 | 505.7623
777.6448 | 471.3669 | 557.3958 | 506.1879
778.6448 | 471.3763 | 558.0084 | 506.8078
779.6448 | 471.3816 | 558.6548 | 507.287
780.6448 | 471.3749 | 559.0503 | 507.9592
781.6448 | 471.2926 | 559.4013 | 508.7802
782.6448 | 471.1719 | 559.9557 | 509.361
783.6448 | 471.1038 | 560.6429 | 509.8533
784.6448 | 471.0366 | 561.1568 | 510.0634
785.6448 | 470.9799 | 561.8139 | 510.462
786.6448 | 470.8815 | 562.4527 | 510.7934
787.6448 | 470.8547 | 563.1677 | 511.2446
788.6448 | 470.7952 | 563.2622 | 511.6874
789.6448 | 470.7252 | 563.8189 | 512.4442
790.6448 | 470.6499 | 564.1284 | 512.958
791.6448 | 470.5617 | 564.613 | 513.4544
792.6448 | 470.5013 | 564.832 | 514.0411
793.6448 | 470.4793 | 565.4139 | 514.8817
794.6448 | 470.422 | 565.8764 | 515.4468
795.6448 | 470.353 | 566.1188 | 516.1434
796.6448 | 470.3259 | 566.2684 | 516.3811
797.6448 | 470.2352 | 566.8111 | 516.8944
798.6448 | 470.1536 | 566.8485 | 517.6676
799.6448 | 470.065 | 566.8103 | 518.185
800.6448 | 469.9914 | 566.6859 | 518.735
801.6448 | 469.8346 | 566.6172 | 519.286
802.6448 | 469.7564 | 567.0944 | 519.9551
803.6448 | 469.6952 | 567.026 | 520.4927
804.6448 | 469.6308 | 567.4426 | 521.1309
805.6448 | 469.5916 | 567.9784 | 521.7472
806.6448 | 469.4833 | 567.7544 | 522.1932
807.6448 | 469.4591 | 567.6863 | 522.7121
808.6448 | 469.4372 | 568.1513 | 523.3143
809.6448 | 469.3581 | 568.4959 | 523.825
810.6448 | 469.335 | 568.3409 | 524.4504
811.6448 | 469.2813 | 568.7003 | 525.0277
812.6448 | 469.2102 | 568.4445 | 525.5573
813.6448 | 469.1946 | 568.353 | 525.9914
814.6448 | 469.177 | 568.2218 | 526.3704
815.6448 | 469.1089 | 568.7147 | 526.8715
816.6448 | 469.1367 | 568.7109 | 527.112
817.6448 | 469.1533 | 569.0384 | 527.4513
818.6448 | 469.2022 | 568.7797 | 527.7924
819.6448 | 469.2779 | 569.273 | 528.1565
820.6448 | 469.3095 | 569.3058 | 528.4836
821.6448 | 469.3188 | 569.42 | 528.689
822.6448 | 469.2285 | 569.0683 | 528.9576
823.6448 | 469.181 | 569.0192 | 529.1763
824.6448 | 469.1893 | 568.9456 | 529.3556
825.6448 | 469.1898 | 568.9157 | 529.4829
826.6448 | 469.1848 | 568.8684 | 529.4938
827.6448 | 469.218 | 568.7952 | 529.698
828.6448 | 469.21 | 568.9612 | 529.901
829.6448 | 469.2678 | 569.0171 | 529.9815
830.6448 | 469.3481 | 569.1103 | 530.202
831.6448 | 469.4356 | 569.1326 | 530.3063
832.6448 | 469.4717 | 569.5603 | 530.5131
833.6448 | 469.4612 | 569.6477 | 530.7248
834.6448 | 469.5179 | 569.6511 | 530.8972
835.6448 | 469.5925 | 569.5632 | 531.1246
836.6448 | 469.6149 | 569.4842 | 531.2774
837.6448 | 469.5608 | 569.3186 | 531.5405
838.6448 | 469.4335 | 569.5702 | 531.7571
839.6448 | 469.474 | 569.4071 | 531.941
840.6448 | 469.5109 | 569.9719 | 532.1783
841.6448 | 469.5483 | 570.0579 | 532.2015
842.6448 | 469.6132 | 570.0565 | 532.487
843.6448 | 469.6269 | 570.2933 | 532.6673
844.6448 | 469.6843 | 570.6522 | 532.6407
845.6448 | 469.7103 | 570.7047 | 533.0342
846.6448 | 469.6944 | 570.8077 | 533.2337
847.6448 | 469.6967 | 570.9412 | 533.2483
848.6448 | 469.6867 | 571.4011 | 533.4148
849.6448 | 469.7112 | 571.5701 | 533.6781
850.6448 | 469.754 | 571.7489 | 533.8435
851.6448 | 469.8138 | 571.9512 | 533.9455
852.6448 | 469.8554 | 572.299 | 534.2531
853.6448 | 469.8561 | 572.2676 | 534.5458
854.6448 | 469.9551 | 572.6358 | 534.7549
855.6448 | 469.931 | 573.0735 | 535.0618
856.6448 | 469.9375 | 573.3818 | 535.1924
857.6448 | 469.9595 | 573.4329 | 535.4156
858.6448 | 470.0749 | 573.532 | 535.7466
859.6448 | 470.1744 | 573.956 | 535.9225
860.6448 | 470.2168 | 574.3029 | 536.1957
861.6448 | 470.2113 | 574.3758 | 536.5037
862.6448 | 470.2046 | 574.4946 | 536.6228
863.6448 | 470.2023 | 574.7347 | 536.9073
864.6448 | 470.2107 | 574.8532 | 537.105
865.6448 | 470.2746 | 575.0288 | 537.3598
866.6448 | 470.253 | 575.2829 | 537.5569
867.6448 | 470.2069 | 575.2454 | 537.5725
868.6448 | 470.2469 | 575.505 | 537.6595
869.6448 | 470.262 | 575.682 | 537.5135
870.6448 | 470.2398 | 575.8614 | 537.8103
871.6448 | 470.2936 | 576.1707 | 537.9595
872.6448 | 470.2995 | 576.431 | 538.0207
873.6448 | 470.2402 | 576.675 | 538.0715
874.6448 | 470.2353 | 576.8252 | 538.1297
875.6448 | 470.2264 | 577.0712 | 538.3581
876.6448 | 470.2862 | 577.1841 | 538.6382
877.6448 | 470.2626 | 577.5036 | 538.7049
878.6448 | 470.2662 | 577.7442 | 538.8751
879.6448 | 470.2608 | 577.8653 | 538.8811
880.6448 | 470.2584 | 578.0739 | 539.1575
881.6448 | 470.2338 | 578.3277 | 539.4749
882.6448 | 470.1421 | 578.5165 | 539.5401
883.6448 | 470.0345 | 578.7876 | 539.7415
884.6448 | 470.0925 | 579.0893 | 539.9294
885.6448 | 470.14 | 579.4296 | 540.326
886.6448 | 470.147 | 579.7827 | 540.5207
887.6448 | 470.1677 | 579.9127 | 540.6324
888.6448 | 470.1601 | 580.1935 | 540.9045
889.6448 | 470.1305 | 580.3184 | 541.0805
890.6448 | 470.1426 | 580.809 | 541.3339
891.6448 | 470.1355 | 580.8553 | 541.4754
892.6448 | 470.041 | 581.1664 | 541.5006
893.6448 | 469.9789 | 581.4379 | 541.8096
894.6448 | 469.9677 | 581.3686 | 541.9591
895.6448 | 470.0448 | 581.5801 | 542.1901
896.6448 | 470.0573 | 581.8647 | 542.4996
897.6448 | 470.0606 | 582.2668 | 542.467
898.6448 | 470.051 | 582.6672 | 542.7013
899.6448 | 470.0182 | 582.8868 | 542.8838
900.6448 | 469.9682 | 583.252 | 543.1334
901.6448 | 469.9242 | 583.6146 | 543.3232
902.6448 | 469.9109 | 583.8078 | 543.2857
903.6448 | 469.8521 | 583.9473 | 543.4394
904.6448 | 469.8766 | 584.0635 | 543.4995
905.6448 | 469.8786 | 584.3717 | 543.7918
906.6448 | 469.8509 | 584.5909 | 543.8856
907.6448 | 469.8136 | 584.6184 | 543.9301
908.6448 | 469.7678 | 584.713 | 544.073
909.6448 | 469.8183 | 585.2374 | 544.2163
910.6448 | 469.8629 | 585.5491 | 544.5285
911.6448 | 469.8524 | 585.8829 | 544.704
912.6448 | 469.809 | 586.1024 | 544.774
913.6448 | 469.7951 | 586.5223 | 544.9665
914.6448 | 469.7968 | 586.8895 | 545.0985
915.6448 | 469.815 | 587.2727 | 545.4037
916.6448 | 469.8654 | 587.3651 | 545.5629
917.6448 | 469.9263 | 587.4853 | 545.7698
918.6448 | 469.9347 | 587.5511 | 545.9223
919.6448 | 469.9636 | 587.8517 | 546.0037
920.6448 | 469.9584 | 588.2672 | 546.3131
921.6448 | 469.987 | 588.258 | 546.489
922.6448 | 470.0668 | 588.23 | 546.6814
923.6448 | 470.1467 | 588.801 | 546.6486
924.6448 | 470.1832 | 589.0975 | 546.8225
925.6448 | 470.2317 | 589.545 | 547.1681
926.6448 | 470.2324 | 589.9533 | 547.3604
927.6448 | 470.3303 | 590.2837 | 547.3732
928.6448 | 470.3906 | 590.7935 | 547.5732
929.6448 | 470.4162 | 590.9636 | 547.7516
930.6448 | 470.46 | 591.1273 | 548.0439
931.6448 | 470.5615 | 591.2487 | 548.1748
932.6448 | 470.5494 | 591.2553 | 548.2602
933.6448 | 470.5503 | 591.3851 | 548.3963
934.6448 | 470.6139 | 591.6546 | 548.7727
935.6448 | 470.6194 | 592.0085 | 548.9263
936.6448 | 470.623 | 592.0831 | 549.0981
937.6448 | 470.6577 | 592.4859 | 549.2904
938.6448 | 470.7016 | 592.6774 | 549.4563
939.6448 | 470.704 | 592.8535 | 549.6605
940.6448 | 470.7378 | 593.2576 | 549.8977
941.6448 | 470.8135 | 593.3445 | 550.05
942.6448 | 470.8543 | 593.5537 | 550.3197
943.6448 | 470.9301 | 593.7512 | 550.5852
944.6448 | 470.9818 | 594.1374 | 550.7512
945.6448 | 470.9883 | 594.4594 | 550.8943
946.6448 | 471.0398 | 594.6073 | 551.1357
947.6448 | 471.0288 | 594.773 | 551.3269
948.6448 | 471.07 | 595.087 | 551.5491
949.6448 | 471.0343 | 595.333 | 551.6942
950.6448 | 471.0896 | 595.2193 | 551.8818
951.6448 | 471.1134 | 595.1563 | 552.0108
952.6448 | 471.1685 | 595.3487 | 552.1975
953.6448 | 471.2303 | 595.7331 | 552.3941
954.6448 | 471.2433 | 596.0258 | 552.569
955.6448 | 471.1827 | 596.098 | 552.7471
956.6448 | 471.1477 | 596.3446 | 552.9582
957.6448 | 471.0912 | 596.5679 | 553.1488
958.6448 | 471.1177 | 596.6921 | 553.4188
959.6448 | 471.164 | 596.8978 | 553.5733
960.6448 | 471.1041 | 597.0964 | 553.8076
961.6448 | 471.1141 | 597.2417 | 553.9578
962.6448 | 471.1207 | 597.2639 | 554.0229
963.6448 | 471.0613 | 597.2858 | 554.4333
964.6448 | 471.1086 | 597.2625 | 554.6653
965.6448 | 471.0536 | 597.5895 | 554.8055
966.6448 | 471.1192 | 597.6028 | 554.9924
967.6448 | 471.1213 | 597.7355 | 555.153
968.6448 | 471.0731 | 597.7932 | 555.3345
969.6448 | 471.1075 | 598.3464 | 555.4715
970.6448 | 471.1369 | 598.7609 | 555.7462
971.6448 | 471.1453 | 599.0376 | 555.9279
972.6448 | 471.1057 | 598.8062 | 556.0798
973.6448 | 471.1156 | 598.7177 | 556.286
974.6448 | 471.1554 | 598.9825 | 556.4283
975.6448 | 471.138 | 599.4232 | 556.7004
976.6448 | 471.1728 | 599.5422 | 556.8342
977.6448 | 471.1638 | 599.6394 | 557.0198
978.6448 | 471.1216 | 599.661 | 557.2733
979.6448 | 471.117 | 599.8746 | 557.4046
980.6448 | 471.0583 | 600.0575 | 557.6815
981.6448 | 471.0736 | 599.9264 | 557.8407
982.6448 | 471.083 | 600.2608 | 558.1305
983.6448 | 471.059 | 600.5851 | 558.3144
984.6448 | 471.0299 | 600.8028 | 558.5813
985.6448 | 471.0068 | 600.9663 | 558.8866
986.6448 | 471.0249 | 600.7501 | 559.079
987.6448 | 471.0951 | 600.9444 | 559.3485
988.6448 | 471.0545 | 601.003 | 559.3911
989.6448 | 471.0774 | 601.6073 | 559.8539
990.6448 | 471.1155 | 602.0925 | 560.1218
991.6448 | 471.1107 | 602.2416 | 560.2672
992.6448 | 471.1015 | 602.2153 | 560.4554
993.6448 | 471.1129 | 602.376 | 560.7128
994.6448 | 471.1597 | 602.4991 | 560.9133
995.6448 | 471.173 | 602.8897 | 561.1386
996.6448 | 471.1871 | 603.0976 | 561.2588
997.6448 | 471.2309 | 603.4657 | 561.4219
998.6448 | 471.2663 | 603.688 | 561.6367
999.6448 | 471.3153 | 603.9652 | 561.8248
1000.6448 | 471.3751 | 604.0854 | 562.0384
1001.6448 | 471.4231 | 604.1436 | 562.2171
1002.6448 | 471.3779 | 604.2226 | 562.4206
1003.6448 | 471.4046 | 604.2238 | 562.6991
1004.6448 | 471.3922 | 604.3905 | 562.9315
1005.6448 | 471.3755 | 604.4889 | 563.185
1006.6448 | 471.3985 | 604.4867 | 563.4478
1007.6448 | 471.3859 | 604.5576 | 563.6607
1008.6448 | 471.4325 | 604.7667 | 563.8323
1009.6448 | 471.4441 | 605.0269 | 564.1107
1010.6448 | 471.4383 | 605.4198 | 564.3912
1011.6448 | 471.4264 | 605.5972 | 564.5259
1012.6448 | 471.411 | 606.0899 | 564.7375
1013.6448 | 471.433 | 606.4954 | 564.9651
1014.6448 | 471.3641 | 606.6415 | 565.1303
1015.6448 | 471.3055 | 606.4122 | 565.4196
1016.6448 | 471.271 | 606.4848 | 565.5692
1017.6448 | 471.3143 | 606.5834 | 565.5959
1018.6448 | 471.3285 | 606.6544 | 565.7857
1019.6448 | 471.3574 | 606.7324 | 565.9956
1020.6448 | 471.3567 | 607.0926 | 566.5198
1021.6448 | 471.3651 | 607.2362 | 566.6558
1022.6448 | 471.3414 | 607.3211 | 566.9104
1023.6448 | 471.2779 | 607.4451 | 567.1029
1024.6448 | 471.2053 | 607.9199 | 567.3498
1025.6448 | 471.2014 | 608.0099 | 567.5427
1026.6448 | 471.2318 | 608.0632 | 567.697
1027.6448 | 471.2606 | 608.1911 | 567.9698
1028.6448 | 471.2972 | 608.3369 | 568.1537
1029.6448 | 471.3297 | 608.5965 | 568.3901
1030.6448 | 471.3789 | 608.7627 | 568.6653
1031.6448 | 471.3938 | 608.946 | 568.9809
1032.6448 | 471.2603 | 608.888 | 569.1381
1033.6448 | 471.1947 | 609.1203 | 569.3342
1034.6448 | 471.1301 | 609.1615 | 569.5835
1035.6448 | 471.1602 | 609.5729 | 569.8377
1036.6448 | 471.179 | 609.8735 | 570.1036
1037.6448 | 471.1716 | 610.2105 | 570.3535
1038.6448 | 471.0818 | 610.2269 | 570.5256
1039.6448 | 471.0326 | 610.4074 | 570.715
1040.6448 | 471.0502 | 610.6407 | 570.8893
1041.6448 | 471.0189 | 611.161 | 571.1241
1042.6448 | 471.048 | 611.5069 | 571.2818
1043.6448 | 471.1406 | 611.3785 | 571.2547
1044.6448 | 471.1512 | 611.3452 | 571.4235
1045.6448 | 471.097 | 611.4486 | 571.9154
1046.6448 | 471.0226 | 611.6632 | 572.1182
1047.6448 | 470.9847 | 611.9489 | 572.3743
1048.6448 | 470.9136 | 612.1747 | 572.5995
1049.6448 | 470.9104 | 612.3311 | 572.8633
1050.6448 | 470.9887 | 612.3921 | 573.0833
1051.6448 | 471.0496 | 612.4341 | 573.2324
1052.6448 | 470.9993 | 612.3412 | 573.434
1053.6448 | 470.9933 | 612.4191 | 573.7169
1054.6448 | 470.9659 | 612.4842 | 573.8073
1055.6448 | 470.8811 | 612.7301 | 573.9276
1056.6448 | 470.7767 | 612.7235 | 574.1621
1057.6448 | 470.5541 | 612.915 | 574.5219
1058.6448 | 470.3331 | 613.1084 | 574.7136
1059.6448 | 470.0029 | 613.0012 | 574.9118
1060.6448 | 469.6094 | 613.4291 | 575.1221
1061.6448 | 469.1461 | 613.0382 | 575.3078
1062.6448 | 468.6748 | 612.9267 | 575.4506
1063.6448 | 468.1424 | 612.8035 | 575.3837
1064.6448 | 467.6155 | 612.6966 | 575.4556
1065.6448 | 467.0132 | 613.3078 | 575.9886
1066.6448 | 466.3355 | 613.7918 | 576.0896
1067.6448 | 465.7857 | 613.5343 | 576.0595
1068.6448 | 465.2119 | 613.7476 | 576.2312
1069.6448 | 464.5741 | 613.8059 | 576.3013
1070.6448 | 463.8756 | 613.7298 | 576.7777
1071.6448 | 463.2035 | 613.9037 | 576.9024
1072.6448 | 462.5339 | 613.9042 | 576.851
1073.6448 | 461.9397 | 614.0469 | 577.0457
1074.6448 | 461.3531 | 613.8627 | 577.0652
1075.6448 | 460.7133 | 614.1496 | 577.541
1076.6448 | 460.0532 | 614.6329 | 577.715
1077.6448 | 459.3636 | 614.5363 | 577.6502
1078.6448 | 458.7284 | 614.5366 | 577.8404
1079.6448 | 458.1022 | 614.756 | 578.0868
1080.6448 | 457.4266 | 614.8064 | 578.3578
1081.6448 | 456.783 | 614.4025 | 578.4585
1082.6448 | 456.2317 | 613.8952 | 578.3574
1083.6448 | 455.6013 | 614.0865 | 578.5391
1084.6448 | 454.9313 | 614.2368 | 578.5602
1085.6448 | 454.2811 | 614.4234 | 579.0465
1086.6448 | 453.6015 | 614.1774 | 579.1291
1087.6448 | 453.0134 | 614.4919 | 579.2931
1088.6448 | 452.4102 | 614.1238 | 579.2022
1089.6448 | 451.7912 | 614.2103 | 579.3415
1090.6448 | 451.1726 | 614.3963 | 579.7013
1091.6448 | 450.4722 | 614.1931 | 579.7094
1092.6448 | 449.6999 | 613.8783 | 579.8215
1093.6448 | 449.0291 | 613.6065 | 579.8845
1094.6448 | 448.3945 | 613.6538 | 579.9818
1095.6448 | 447.7452 | 613.596 | 580.2702
1096.6448 | 447.0944 | 613.7789 | 580.4085
1097.6448 | 446.5135 | 613.6472 | 580.3153
1098.6448 | 445.8946 | 613.5496 | 580.3832
1099.6448 | 445.214 | 613.6052 | 580.4519
1100.6448 | 444.5319 | 613.7793 | 580.7749
1101.6448 | 443.824 | 613.5647 | 580.9297
1102.6448 | 443.1792 | 613.4909 | 581.1025
1103.6448 | 442.4871 | 613.3419 | 581.0596
1104.6448 | 441.7979 | 613.0744 | 581.1783
1105.6448 | 441.1926 | 613.3952 | 581.4492
1106.6448 | 440.5645 | 613.4986 | 581.6472
1107.6448 | 439.9144 | 613.5597 | 581.8236
1108.6448 | 439.2597 | 613.5211 | 581.9609
1109.6448 | 438.6199 | 613.3816 | 581.8231
1110.6448 | 438.0607 | 613.119 | 582.0954
1111.6448 | 437.3842 | 612.7855 | 582.2195
1112.6448 | 436.6402 | 612.588 | 582.3022
1113.6448 | 436.0222 | 612.0944 | 582.3161
1114.6448 | 435.4061 | 612.2883 | 582.4524
1115.6448 | 434.7831 | 612.1622 | 582.4029
1116.6448 | 434.1453 | 612.0486 | 582.4442
1117.6448 | 433.4463 | 611.8942 | 582.5106
1118.6448 | 432.7667 | 612.0113 | 582.5857
1119.6448 | 432.1212 | 611.8552 | 582.7042
1120.6448 | 431.4753 | 611.7716 | 582.7167
1121.6448 | 430.8514 | 611.3964 | 582.8589
1122.6448 | 430.1988 | 611.3885 | 582.9838
1123.6448 | 429.5725 | 611.1815 | 582.9757
1124.6448 | 428.9476 | 611.3343 | 583.0919
1125.6448 | 428.3811 | 611.1855 | 583.1653
1126.6448 | 427.7736 | 610.9436 | 583.2438
1127.6448 | 427.1119 | 610.553 | 583.2541
1128.6448 | 426.4802 | 610.4424 | 583.1803
1129.6448 | 425.912 | 609.7888 | 583.1019
1130.6448 | 425.3217 | 609.7833 | 583.2953
1131.6448 | 424.6938 | 609.4956 | 583.2768
1132.6448 | 424.1282 | 609.1231 | 583.3145
1133.6448 | 423.5192 | 608.8611 | 583.4484
1134.6448 | 422.9317 | 608.4779 | 583.4965
1135.6448 | 422.3609 | 608.5518 | 583.5526
1136.6448 | 421.7491 | 608.3544 | 583.5256
1137.6448 | 421.1228 | 608.1375 | 583.7124
1138.6448 | 420.5252 | 607.7183 | 583.6934
1139.6448 | 419.9038 | 607.5775 | 583.946
1140.6448 | 419.2418 | 607.6831 | 584.0879
1141.6448 | 418.6631 | 607.1566 | 584.0376
1142.6448 | 417.9469 | 606.42 | 583.865
1143.6448 | 417.2758 | 606.5153 | 584.2061
1144.6448 | 416.6524 | 606.4197 | 584.1626
1145.6448 | 416.0258 | 606.0625 | 584.1399
1146.6448 | 415.4096 | 605.4899 | 584.0758
1147.6448 | 414.7736 | 605.3037 | 584.1137
1148.6448 | 414.2216 | 605.1423 | 583.9582
1149.6448 | 413.6002 | 604.6545 | 583.8233
1150.6448 | 413.0234 | 604.5656 | 584.0724
1151.6448 | 412.4583 | 604.5495 | 584.0615
1152.6448 | 411.8134 | 604.1996 | 584.0459
1153.6448 | 411.2329 | 603.9239 | 583.8939
1154.6448 | 410.6341 | 603.6173 | 583.9415
1155.6448 | 409.9798 | 603.7433 | 584.3235
1156.6448 | 409.3521 | 603.7082 | 584.4408
1157.6448 | 408.7941 | 603.3694 | 584.1706
1158.6448 | 408.1789 | 603.2106 | 584.2083
1159.6448 | 407.576 | 603.1784 | 584.2839
1160.6448 | 407.0314 | 603.0904 | 584.6245
1161.6448 | 406.5092 | 602.8547 | 584.6271
1162.6448 | 405.9086 | 602.8366 | 584.7672
1163.6448 | 405.3465 | 602.4337 | 584.4753
1164.6448 | 404.86 | 601.8661 | 584.5455
1165.6448 | 404.3003 | 601.6478 | 584.8613
1166.6448 | 403.7403 | 601.5194 | 584.8167
1167.6448 | 403.1955 | 601.1195 | 584.6852
1168.6448 | 402.643 | 601.0325 | 584.745
1169.6448 | 402.1222 | 601.1453 | 584.7486
1170.6448 | 401.5259 | 600.9482 | 585.168
1171.6448 | 400.9584 | 600.7313 | 585.1281
1172.6448 | 400.3856 | 600.1523 | 584.9779
1173.6448 | 399.8545 | 600.0667 | 585.0927
1174.6448 | 399.3262 | 599.7565 | 585.1789
1175.6448 | 398.7711 | 599.8991 | 585.5265
1176.6448 | 398.2103 | 599.5249 | 585.7016
1177.6448 | 397.6807 | 599.094 | 585.432
1178.6448 | 397.1827 | 599.2839 | 585.4748
1179.6448 | 396.6459 | 599.0186 | 585.5451
1180.6448 | 396.1238 | 599.1546 | 585.983
1181.6448 | 395.535 | 598.7577 | 585.8317
1182.6448 | 394.943 | 598.3085 | 585.6122
1183.6448 | 394.3781 | 598.1999 | 585.6831
1184.6448 | 393.8458 | 597.9958 | 585.5148
1185.6448 | 393.289 | 598.3795 | 585.8365
1186.6448 | 392.7492 | 598.1864 | 585.6663
1187.6448 | 392.1388 | 598.3242 | 585.4406
1188.6448 | 391.5566 | 597.8459 | 585.5227
1189.6448 | 390.9414 | 597.74 | 585.4423
1190.6448 | 390.381 | 597.1683 | 585.532
1191.6448 | 389.8745 | 597.1826 | 585.4379
1192.6448 | 389.3363 | 596.8807 | 585.4561
1193.6448 | 388.7725 | 596.3773 | 585.4898
1194.6448 | 388.2684 | 596.0947 | 585.5841
1195.6448 | 387.6977 | 595.8094 | 585.611
1196.6448 | 387.1875 | 595.7606 | 585.7014
1197.6448 | 386.6415 | 595.2343 | 585.7447
1198.6448 | 386.0974 | 594.9353 | 585.629
1199.6448 | 385.5841 | 594.8372 | 585.5721
1200.6448 | 385.072 | 594.4852 | 585.6362
1201.6448 | 384.5436 | 594.5207 | 585.4877
1202.6448 | 383.9712 | 594.2967 | 585.4641
1203.6448 | 383.4647 | 593.8814 | 585.4202
1204.6448 | 382.9767 | 593.4908 | 585.3605
1205.6448 | 382.4654 | 593.1636 | 585.3944
1206.6448 | 381.8813 | 592.9095 | 585.3707
1207.6448 | 381.3132 | 592.3291 | 585.4535
1208.6448 | 380.8109 | 592.2902 | 585.3553
1209.6448 | 380.3676 | 592.1026 | 585.3296
1210.6448 | 379.8855 | 591.6907 | 585.3683
1211.6448 | 379.4037 | 591.5078 | 585.3611
1212.6448 | 378.9173 | 591.0299 | 585.4436
1213.6448 | 378.4016 | 590.5109 | 585.4573
1214.6448 | 377.9216 | 590.0338 | 585.4956
1215.6448 | 377.4322 | 589.8113 | 585.716
1216.6448 | 376.9415 | 589.6462 | 585.5917
1217.6448 | 376.4236 | 589.3835 | 585.703
1218.6448 | 375.8742 | 589.2541 | 585.6823
1219.6448 | 375.3819 | 588.7571 | 585.7616
1220.6448 | 374.8542 | 588.493 | 585.7988
1221.6448 | 374.3651 | 588.0188 | 585.8764
1222.6448 | 373.82 | 587.69 | 585.8649
1223.6448 | 373.2343 | 587.4245 | 586.004
1224.6448 | 372.7713 | 587.0435 | 586.0489
1225.6448 | 372.3025 | 586.7189 | 586.0084
1226.6448 | 371.7953 | 586.5364 | 586.0381
1227.6448 | 371.2569 | 585.9972 | 585.9742
1228.6448 | 370.7203 | 585.71 | 585.9813
1229.6448 | 370.25 | 585.5531 | 585.895
1230.6448 | 369.7511 | 584.9359 | 585.8452
1231.6448 | 369.2388 | 584.7097 | 585.7559
1232.6448 | 368.7117 | 584.234 | 585.6933
1233.6448 | 368.2012 | 584.1295 | 585.6546
1234.6448 | 367.7604 | 583.8129 | 585.5279
1235.6448 | 367.2874 | 583.382 | 585.4403
1236.6448 | 366.7905 | 583.0046 | 585.5094
1237.6448 | 366.3331 | 582.6127 | 585.4615
1238.6448 | 365.8285 | 582.3276 | 585.4559
1239.6448 | 365.3477 | 581.9839 | 585.4344
1240.6448 | 364.8618 | 581.6993 | 585.394
1241.6448 | 364.4308 | 581.4169 | 585.5033
1242.6448 | 363.968 | 581.082 | 585.5656
1243.6448 | 363.486 | 580.7122 | 585.4177
1244.6448 | 362.9747 | 580.3293 | 585.3322
1245.6448 | 362.4929 | 580.4353 | 585.2346
1246.6448 | 362.017 | 580.0222 | 585.184
1247.6448 | 361.5095 | 579.781 | 585.5225
1248.6448 | 360.9522 | 579.1843 | 585.3292
1249.6448 | 360.4448 | 578.7743 | 585.1471
1250.6448 | 359.9868 | 578.6302 | 585.0762
1251.6448 | 359.5158 | 578.3808 | 584.8916
1252.6448 | 359.0638 | 577.8532 | 584.8343
1253.6448 | 358.5964 | 577.5175 | 584.7679
1254.6448 | 358.1019 | 577.3762 | 584.6213
1255.6448 | 357.6008 | 577.0052 | 584.4389
1256.6448 | 357.1469 | 576.5482 | 584.3108
1257.6448 | 356.6824 | 576.4681 | 583.6527
1258.6448 | 356.1887 | 576.215 | 583.7359
1259.6448 | 355.684 | 576.0197 | 583.7976
1260.6448 | 355.2265 | 575.6516 | 583.5672
1261.6448 | 354.7977 | 575.2107 | 583.509
1262.6448 | 354.4073 | 574.4716 | 583.5589
1263.6448 | 353.9576 | 574.1327 | 583.5108
1264.6448 | 353.5263 | 573.7196 | 583.4735
1265.6448 | 353.0276 | 573.4145 | 583.4708
1266.6448 | 352.5414 | 573.0663 | 583.5066
1267.6448 | 352.0991 | 572.6016 | 583.4978
1268.6448 | 351.6731 | 572.1066 | 583.4992
1269.6448 | 351.2204 | 571.7833 | 583.502
1270.6448 | 350.7783 | 571.669 | 583.4518