## Test Conditions
DESIREE-FIRE Test Number 27 - Circuit Simulator Data Only
Test Date: | 2009-08-12
DCSim DAQ Start Time | 15:10
DCSim Time for Synchronization | 16:10
Heat Source Synchronization | 7:36 | minutes:seconds
Heat Source DAQ Start Time | 16:02
Fire Time | 16:10
Offset | 1:00 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3586 | seconds
Heat Source Offset | 0:08 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 500 | seconds
Heat Source Stop Time | 16:29
Test Duration | 0:19 | minutes:seconds
| 1151 | seconds
CT500 turns | 2 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 5 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
MOV 1 | SR/Aramid Braid, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
MOV 2 | SR/Aramid Braid, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | MOV-1_CT500 | MOV-1a_CT35_1_P | MOV-1a_CT35_2_N | MOV-1b_CT35_1_G | MOV-1b_CT35_2_R | MOV-1b_CT35_3_YO | MOV-1b_CT35_4_YC | MOV-2_CT500 | MOV-2a_CT35_1_P | MOV-2a_CT35_2_N | MOV-2b_CT35_1_G | MOV-2b_CT35_2_R | MOV-2b_CT35_3_YO | 2b_CT35_4_YC1 | MOV-1a_VT7_1_SP | MOV-1a_VTU_1_P | MOV-1a_VTU_2_N | MOV-1b_VT7_1_G | MOV-1b_VT7_2_R | MOV-1b_VT7_3_YO1 | MOV-1b_VT7_4_YC1 | MOV-2a_VT7_1_SP | MOV-2a_VTU_1_P | MOV-2a_VTU_2_N | MOV-2b_VT7_1_G | MOV-2b_VT7_2_R | 2b_VT7_3_YO1 | MOV-2b_VT7_4_YC1 | {MOV1} V(N) - V(Batt -) | {MOV1} V(P) - V(Batt +) | {MOV1} V(G) - V(Batt +) | {MOV1} V(R) - V(Batt -) | {MOV1} V(YC1) - V(Batt -) | {MOV1} V(YO1) - V(Batt -) | {MOV1} V(YC1) - V(N) | {MOV1} V(YO1) - V(N) | {MOV2} V(N) - V(Batt -) | {MOV2} V(P) - V(Batt +) | {MOV2} V(G) - V(Batt +) | {MOV2} V(R) - V(Batt -) | {MOV2} V(YC1) - V(Batt -) | {MOV2} V(YO1) - V(Batt -) | {MOV2} V(YC1) - V(N) | {MOV2} V(YO1) - V(N) | {MOV-1} V(R) - V(N) | {MOV-1} V(G) - V(N) | {MOV-2} V(R) - V(N) | {MOV-2} V(G) - V(N) | {MOV-1} V(P) - V(N) | {MOV-2} V(P) - V(N) | {MOV-1} V(P) - V(Batt -) | {MOV-2} V(P) - V(Batt -) | {MOV-1} V(N) - V(Batt +) | {MOV-2} V(N) - V(Batt +) | {MOV-1} V(G) - V(Batt -) | {MOV2} V(G) - V(Batt-) | {MOV1} V(SP) - V(Batt -) | {MOV2} V(SP) - V(Batt -)
-0.10938 | 123.2162 | -59.9808 | 63.1622 | 0.088501 | 0.00064726 | 0.061795 | 0.067791 | -0.0016279 | 0.00025633 | 0.00043363 | -0.045074 | 0.0022708 | 0.067257 | 0.07201 | -0.0034736 | 0.0035482 | 0.0030611 | -0.009155 | 63.0936 | -60.1685 | 62.9837 | -59.9442 | -60.2783 | 0.045776 | 0.018311 | 63.0478 | -60.0815 | 63.0295 | -60.0906 | -60.1868 | -59.967 | -0.18768 | -0.068664 | -0.17853 | 0.036621 | 60.0265 | -0.29755 | 60.2142 | -0.10986 | -0.10071 | -0.11444 | -0.13275 | -0.10986 | 0.013733 | -0.20599 | 0.11444 | -0.10529 | 0.2243 | 123.1522 | -0.009155 | 123.111 | 123.262 | 123.1293 | 123.0743 | 123.0286 | -123.3307 | -123.2437 | 122.9645 | 123.0103 | 59.9716 | 59.9991
0.85938 | 123.2208 | -60.0311 | 63.0707 | -0.01831 | 0.0032107 | 0.064572 | 0.065655 | -0.00055967 | -0.00059807 | 0.0017154 | -0.0084534 | 0.0018436 | 0.068325 | 0.06667 | -0.0028326 | 0.0039756 | 0.0030611 | 0.032043 | 63.0661 | -60.2097 | 63.0157 | -59.9167 | -60.2875 | 0.045776 | 0.073242 | 63.0386 | -60.0677 | 63.0615 | -60.054 | -60.173 | -59.967 | -0.17853 | -0.004578 | -0.054932 | 0.11444 | 60.0769 | -0.25635 | 60.2554 | -0.07782 | -0.036621 | -0.032044 | -0.009156 | -0.022888 | 0.064087 | -0.14191 | 0.10071 | -0.10529 | 0.29297 | 123.2254 | 0.013733 | 123.1293 | 123.2758 | 123.1064 | 123.0972 | 123.0698 | -123.2803 | -123.1384 | 123.0469 | 123.0927 | 60.0632 | 60.1044
1.9219 | 123.3261 | -60.0449 | 63.002 | -0.086975 | 0.0017155 | 0.064145 | 0.0648 | -0.00034607 | -0.0031617 | 0.00022003 | -0.023712 | 0.0018436 | 0.070248 | 0.061115 | -0.0028326 | 0.0041892 | 0.00028414 | -0.045776 | 62.9654 | -60.2051 | 63.0478 | -59.848 | -60.2646 | -0.013733 | -0.027466 | 62.9517 | -60.0952 | 63.1256 | -60.0311 | -60.1227 | -59.9075 | -0.16022 | -0.036621 | 0.045777 | 0.19684 | 60.0311 | -0.21973 | 60.1913 | -0.059509 | -0.050354 | -0.050354 | 0.1236 | 0.013733 | 0.13733 | -0.07782 | 0.18768 | -0.027466 | 0.35706 | 123.2529 | 0.064087 | 123.2208 | 123.1705 | 123.0469 | 123.0103 | 122.9965 | -123.2071 | -123.0972 | 123.0927 | 123.1705 | 59.9991 | 60.0174
2.8594 | 123.23 | -60.0357 | 63.0844 | -0.01831 | 0.0010745 | 0.062436 | 0.065868 | -0.0037641 | 0.00068353 | -0.00042077 | -0.05423 | 0.002698 | 0.069821 | 0.060261 | -0.0030462 | 0.0054708 | -0.0016385 | -0.018311 | 63.0707 | -60.2005 | 62.9791 | -59.9579 | -60.3104 | 0.032043 | 0.004578 | 63.0295 | -60.0952 | 63.0569 | -60.0906 | -60.1959 | -59.9762 | -0.16479 | -0.013733 | -0.10529 | 0.07782 | 60.0677 | -0.27466 | 60.2325 | -0.10986 | -0.059509 | -0.054932 | -0.027466 | -0.054931 | 0.05951 | -0.16022 | 0.11902 | -0.10071 | 0.24261 | 123.1796 | 0.004578 | 123.1522 | 123.2712 | 123.1247 | 123.1064 | 123.0652 | -123.2849 | -123.1796 | 123.0148 | 123.0927 | 60.0174 | 60.0403
3.9062 | 123.262 | -60.0357 | 63.0569 | -0.14038 | 0.0015019 | 0.063504 | 0.065228 | 0.00050853 | -0.0014527 | 0.001929 | -0.066437 | 0.0022708 | 0.067684 | 0.069233 | -0.0028326 | 0.0056846 | -0.0037747 | 0.018311 | 63.0524 | -60.2188 | 63.0341 | -59.8938 | -60.2737 | 0.045776 | 0.054932 | 63.0295 | -60.0769 | 63.1027 | -60.054 | -60.1685 | -59.935 | -0.18311 | -0.004578 | -0.022888 | 0.14191 | 60.0815 | -0.23804 | 60.2646 | -0.054932 | -0.041198 | -0.027466 | 0.045776 | -0.01831 | 0.10071 | -0.13275 | 0.14191 | -0.091553 | 0.32501 | 123.2529 | 0.022888 | 123.1796 | 123.2712 | 123.1064 | 123.0881 | 123.0652 | -123.2758 | -123.1338 | 123.0698 | 123.1384 | 60.054 | 60.0906
4.8594 | 123.2117 | -60.0082 | 63.0798 | -0.033569 | -0.00084814 | 0.061154 | 0.065228 | -0.00055967 | -0.0025207 | 6.432e-06 | -0.026764 | 0.003339 | 0.067898 | 0.062611 | -0.0030462 | 0.0061118 | -0.00035666 | -0.009155 | 63.0707 | -60.173 | 62.9883 | -59.9579 | -60.3012 | 0.032043 | 0.009155 | 63.0661 | -60.0815 | 63.0569 | -60.0861 | -60.1959 | -59.9716 | -0.16479 | -0.009155 | -0.091553 | 0.050354 | 60.0403 | -0.29297 | 60.2051 | -0.12817 | -0.073242 | -0.013733 | -0.022888 | -0.07782 | 0.036621 | -0.18768 | 0.10986 | -0.11444 | 0.21515 | 123.1613 | -0.004578 | 123.1384 | 123.2437 | 123.1476 | 123.0789 | 123.0743 | -123.2529 | -123.1613 | 122.9965 | 123.0652 | 59.9991 | 60.0174
5.8906 | 123.2254 | -60.0128 | 63.0524 | -0.033569 | 0.0019291 | 0.061795 | 0.066082 | -0.0016279 | -0.0038025 | -0.00084817 | -0.0054016 | 0.0018436 | 0.070889 | 0.073719 | -0.00091001 | 0.0050436 | -0.0039883 | 0.041199 | 63.0615 | -60.2005 | 63.0066 | -59.8663 | -60.2097 | 0.073242 | 0.068665 | 63.0203 | -60.0815 | 63.0661 | -60.0769 | -60.1639 | -59.967 | -0.18768 | 0.009155 | -0.045776 | 0.14648 | 60.0861 | -0.19684 | 60.2737 | -0.009156 | -0.068665 | -0.032043 | 0.013733 | -0.064087 | 0.045776 | -0.15106 | 0.11444 | -0.082397 | 0.33417 | 123.2071 | 0.004578 | 123.1476 | 123.262 | 123.1018 | 123.0743 | 123.0331 | -123.2529 | -123.1338 | 123.0194 | 123.0789 | 60.054 | 60.0815
6.875 | 123.2666 | -60.0266 | 63.0569 | -0.033569 | 0.00064726 | 0.063504 | 0.066509 | 8.1126e-05 | -0.0035889 | 0.00064723 | -0.063385 | 0.0012028 | 0.069607 | 0.064533 | -0.004328 | 0.0056846 | 0.0011385 | 0.013733 | 63.0569 | -60.2234 | 63.0112 | -59.903 | -60.2829 | 0.022888 | 0.041199 | 63.0112 | -60.0815 | 63.1027 | -60.0632 | -60.1685 | -59.9304 | -0.19684 | 0 | -0.045777 | 0.1236 | 60.0494 | -0.25635 | 60.2463 | -0.059509 | -0.054932 | -0.045777 | 0.045776 | -0.036621 | 0.09613 | -0.14191 | 0.15106 | -0.086975 | 0.32043 | 123.2346 | 0.018311 | 123.1842 | 123.2803 | 123.0927 | 123.0835 | 123.0377 | -123.2803 | -123.1384 | 123.0377 | 123.1293 | 60.0403 | 60.0677
7.8906 | 123.2071 | -60.0311 | 63.0844 | -0.041199 | 0.0019291 | 0.062222 | 0.066082 | 0.0015765 | -0.00081187 | -0.00020717 | -0.026764 | 0.0041934 | 0.07153 | 0.067524 | -0.0017646 | 0.0044028 | -0.00057046 | -0.018311 | 63.1027 | -60.1868 | 62.9791 | -59.9533 | -60.2921 | 0.036621 | 0.013733 | 63.0432 | -60.0723 | 63.0524 | -60.0815 | -60.1913 | -59.9762 | -0.15564 | 0.01831 | -0.10529 | 0.07782 | 60.0677 | -0.26093 | 60.2234 | -0.10529 | -0.041199 | -0.041199 | -0.032044 | -0.050354 | 0.054932 | -0.16022 | 0.096131 | -0.11902 | 0.23346 | 123.1659 | -0.009155 | 123.1247 | 123.2895 | 123.1155 | 123.1338 | 123.0743 | -123.2712 | -123.1567 | 123.0103 | 123.0835 | 60.0128 | 60.0449
8.8594 | 123.1979 | -60.0403 | 63.0844 | -0.033569 | 0.0034245 | 0.063717 | 0.064373 | 0.0032855 | -0.00081187 | 0.00064723 | -0.023712 | 0.0014164 | 0.068325 | 0.061329 | -0.0030462 | 0.0052572 | -0.00014306 | 0.068665 | 63.0661 | -60.1685 | 62.9974 | -59.9075 | -60.2646 | 0.059509 | 0.036621 | 63.0432 | -60.0906 | 63.0524 | -60.0906 | -60.1685 | -59.9762 | -0.12817 | -0.018311 | -0.086975 | 0.13275 | 60.0998 | -0.2243 | 60.228 | -0.09613 | -0.050354 | -0.041199 | -0.032044 | -0.050354 | 0.064087 | -0.12817 | 0.11444 | -0.07782 | 0.26092 | 123.1659 | 0 | 123.143 | 123.2346 | 123.1338 | 123.1064 | 123.0835 | -123.2529 | -123.175 | 123.0377 | 123.0927 | 60.1089 | 60.0769
9.8594 | 123.2941 | -60.0082 | 63.0524 | -0.02594 | 0.0025699 | 0.064358 | 0.066296 | -0.0014143 | -0.0025207 | -0.00084817 | 0.025116 | -0.0011472 | 0.067471 | 0.066242 | -0.0021918 | 0.00483 | -0.00057046 | 0.082397 | 63.0569 | -60.1639 | 63.0844 | -59.8297 | -60.1822 | 0.11444 | 0.14191 | 62.9791 | -60.0357 | 63.1393 | -59.9899 | -60.0815 | -59.8892 | -0.15564 | 0.004578 | 0.032044 | 0.17853 | 60.1227 | -0.17395 | 60.2783 | -0.018311 | -0.027466 | -0.073242 | 0.086975 | 0.018311 | 0.11902 | -0.073242 | 0.14648 | -0.045776 | 0.33417 | 123.2483 | 0.045777 | 123.175 | 123.2208 | 123.0148 | 123.0652 | 122.9874 | -123.2162 | -123.0881 | 123.0927 | 123.1476 | 60.0906 | 60.1501
10.9062 | 123.2437 | -60.0082 | 63.0569 | -0.079346 | 0.0012881 | 0.062649 | 0.065441 | 0.0013629 | -0.0010255 | -0.00042077 | -0.07254 | 0.0029116 | 0.070248 | 0.068165 | -0.0013372 | 0.006539 | -0.0020657 | -0.013733 | 63.0478 | -60.2234 | 62.9883 | -59.9304 | -60.3195 | -0.032043 | -0.032043 | 63.0203 | -60.0906 | 63.0524 | -60.1227 | -60.2234 | -59.9808 | -0.21515 | -0.009155 | -0.068665 | 0.07782 | 59.9762 | -0.31128 | 60.1913 | -0.09613 | -0.082397 | -0.036621 | -0.004578 | -0.11444 | 0.027466 | -0.21515 | 0.10986 | -0.13275 | 0.29297 | 123.2117 | -0.032044 | 123.143 | 123.2712 | 123.111 | 123.056 | 123.0286 | -123.2803 | -123.1476 | 122.9965 | 123.0606 | 59.9945 | 59.9762
11.875 | 123.3124 | -60.0128 | 62.9837 | -0.10986 | 0.0023563 | 0.064785 | 0.066937 | -0.0016279 | -0.00059807 | 0.001929 | -0.011505 | 0.00056179 | 0.070034 | 0.063679 | -0.0021918 | 0.0054708 | -0.00035666 | -0.032043 | 62.9974 | -60.2005 | 63.0432 | -59.8709 | -60.2554 | -0.022888 | -0.018311 | 62.9517 | -60.0769 | 63.1348 | -60.0266 | -60.1135 | -59.903 | -0.18768 | 0.013733 | 0.059509 | 0.14191 | 59.9899 | -0.24262 | 60.1776 | -0.054932 | -0.064087 | -0.032044 | 0.15106 | -0.013733 | 0.10986 | -0.10071 | 0.17395 | -0.036621 | 0.32959 | 123.2437 | 0.050354 | 123.2117 | 123.1979 | 123.0286 | 123.0103 | 122.9645 | -123.1842 | -123.0606 | 123.056 | 123.1476 | 59.9808 | 59.9945
12.8906 | 123.1979 | -60.0494 | 62.9974 | -0.11749 | 0.0019291 | 0.063504 | 0.066082 | 0.0058489 | 0.0011109 | -0.0034116 | -0.096954 | 0.0014164 | 0.070889 | 0.06432 | -0.0075324 | 0.0039756 | 0.0011385 | -0.050354 | 63.0341 | -60.2234 | 62.9745 | -59.967 | -60.3333 | -0.068665 | -0.064087 | 63.0066 | -60.0723 | 63.0203 | -60.1273 | -60.2417 | -59.9899 | -0.17395 | 0.036621 | -0.022889 | 0.082397 | 59.9808 | -0.28381 | 60.1547 | -0.10986 | -0.022889 | 0.009155 | 0.022888 | -0.07782 | 0.059509 | -0.19226 | 0.082398 | -0.16937 | 0.25635 | 123.1979 | -0.054931 | 123.0927 | 123.2574 | 123.0789 | 123.0835 | 123.056 | -123.2208 | -123.0698 | 123.024 | 123.0698 | 59.9991 | 59.9854
13.8594 | 123.2254 | -60.0403 | 63.0524 | -0.033569 | 0.00086086 | 0.062222 | 0.066296 | 8.1126e-05 | -0.00059807 | 0.00064723 | -0.017609 | 0.0037662 | 0.067898 | 0.063893 | -0.0032598 | 0.0029074 | -0.00078406 | -0.004578 | 63.0524 | -60.2005 | 62.97 | -59.9487 | -60.2829 | 0.036621 | 0.013733 | 63.0341 | -60.0677 | 63.0478 | -60.0906 | -60.1913 | -59.9808 | -0.16022 | 0 | -0.082397 | 0.091553 | 60.0769 | -0.24262 | 60.2371 | -0.082398 | -0.027466 | -0.01831 | -0.004577 | -0.050354 | 0.059509 | -0.15106 | 0.086975 | -0.1236 | 0.25177 | 123.1705 | -0.022888 | 123.1155 | 123.2529 | 123.1018 | 123.0927 | 123.0743 | -123.2529 | -123.1201 | 123.0103 | 123.0881 | 60.0357 | 60.054
14.8594 | 123.262 | -60.0357 | 63.0478 | -0.02594 | -0.00042094 | 0.063717 | 0.064159 | 0.0030719 | -0.0020935 | -0.0010618 | -0.057281 | -7.901e-05 | 0.070248 | 0.064961 | -0.004328 | 0.0041892 | -0.00035666 | 0.004578 | 63.0386 | -60.2142 | 63.0112 | -59.903 | -60.2783 | 0.027466 | 0.041199 | 63.0249 | -60.0861 | 63.089 | -60.0723 | -60.1547 | -59.9258 | -0.17853 | -0.009156 | -0.036622 | 0.13275 | 60.0632 | -0.24261 | 60.2417 | -0.064087 | -0.050354 | -0.022889 | 0.041198 | -0.036621 | 0.10986 | -0.11902 | 0.16022 | -0.068664 | 0.31128 | 123.2254 | 0.013733 | 123.175 | 123.2529 | 123.111 | 123.0743 | 123.0606 | -123.262 | -123.1339 | 123.0469 | 123.1247 | 60.0403 | 60.0769
15.8906 | 123.2574 | -60.0357 | 63.0615 | -0.041199 | 0.0029971 | 0.064145 | 0.066296 | 0.0017901 | -0.0023071 | -0.0044796 | 0.012909 | 0.00163 | 0.069607 | 0.06197 | -0.0030462 | 0.003762 | 0.00028414 | 0.054932 | 63.0661 | -60.1685 | 63.0753 | -59.8343 | -60.1822 | 0.11444 | 0.1236 | 62.9974 | -60.0449 | 63.121 | -60.0082 | -60.0906 | -59.9304 | -0.13275 | 0.004578 | 0.013733 | 0.20142 | 60.1501 | -0.14648 | 60.2829 | -0.013733 | -0.009155 | -0.064086 | 0.05951 | 0.027466 | 0.10529 | -0.054931 | 0.11444 | -0.045776 | 0.33417 | 123.2437 | 0.036621 | 123.1659 | 123.2346 | 123.0423 | 123.1018 | 123.0331 | -123.23 | -123.1064 | 123.111 | 123.1567 | 60.0906 | 60.1593
16.875 | 123.3627 | -59.9808 | 63.0569 | -0.048828 | 0.0010745 | 0.063931 | 0.064587 | -0.00098687 | 0.00046993 | -0.0034116 | 0.025116 | 0.00098899 | 0.068539 | 0.066029 | -0.0028326 | 0.0041892 | -0.0014249 | 0.036621 | 63.0066 | -60.1822 | 63.1027 | -59.7702 | -60.1547 | 0.13275 | 0.15106 | 62.9745 | -60.0586 | 63.1439 | -59.9533 | -60.0357 | -59.8663 | -0.20142 | -0.050354 | 0.045776 | 0.21057 | 60.1135 | -0.17395 | 60.3149 | 0.027466 | -0.07782 | -0.082398 | 0.086975 | 0.027466 | 0.11444 | -0.054932 | 0.19226 | 0.022888 | 0.41199 | 123.2849 | 0.10529 | 123.2025 | 123.1888 | 123.0331 | 122.9874 | 122.9553 | -123.2391 | -123.1155 | 123.0835 | 123.1247 | 60.0174 | 60.1318
17.9062 | 123.23 | -60.0586 | 63.0524 | -0.071716 | 0.0010745 | 0.063931 | 0.068646 | 0.0052081 | -0.0014527 | -0.0010618 | -0.078644 | 0.00163 | 0.068112 | 0.062611 | -0.0041144 | 0.003121 | -0.0022793 | -0.036621 | 63.0295 | -60.228 | 62.9745 | -59.9625 | -60.3378 | -0.068665 | -0.073242 | 63.0157 | -60.0861 | 63.0615 | -60.1089 | -60.2554 | -60.0037 | -0.16937 | -0.022888 | -0.07782 | 0.096131 | 59.9899 | -0.27924 | 60.1593 | -0.10986 | -0.027466 | -0.036621 | 0.009155 | -0.050354 | 0.054932 | -0.19684 | 0.082398 | -0.16937 | 0.2655 | 123.2025 | -0.022888 | 123.1476 | 123.2574 | 123.1018 | 123.0881 | 123.0743 | -123.2803 | -123.1384 | 123.0331 | 123.1201 | 60.022 | 59.9854
18.875 | 123.2117 | -60.0723 | 63.0295 | -0.064087 | 0.0010745 | 0.063931 | 0.065655 | -0.00077327 | 4.273e-05 | -0.0027708 | -0.051178 | -0.00050621 | 0.068325 | 0.067524 | -0.0015508 | 0.003762 | -0.0014249 | -0.09613 | 63.0295 | -60.2371 | 62.9105 | -60.0174 | -60.4019 | -0.10986 | -0.16479 | 63.0112 | -60.1273 | 63.0249 | -60.173 | -60.2554 | -59.9991 | -0.16479 | 0 | -0.11902 | 0.054932 | 59.9625 | -0.32959 | 60.1273 | -0.16479 | -0.054931 | -0.018311 | -0.004578 | -0.10071 | 0.073243 | -0.1831 | 0.12817 | -0.12817 | 0.21973 | 123.1476 | -0.045777 | 123.1522 | 123.2666 | 123.1384 | 123.1018 | 123.0835 | -123.2666 | -123.1567 | 122.9828 | 123.0972 | 59.9762 | 59.9075
19.8906 | 123.1934 | -60.054 | 63.0295 | -0.094604 | 6.46e-06 | 0.065854 | 0.066723 | 0.0041399 | -0.0016663 | 6.432e-06 | -0.066437 | 0.0018436 | 0.069821 | 0.068165 | -0.0039008 | 0.0056846 | 0.00049774 | -0.050354 | 63.0615 | -60.2417 | 62.9608 | -59.9625 | -60.3378 | -0.086975 | -0.13275 | 62.9883 | -60.0952 | 63.0295 | -60.1639 | -60.2188 | -59.9716 | -0.18768 | 0.032043 | -0.068665 | 0.091553 | 59.967 | -0.28381 | 60.1547 | -0.096131 | -0.041199 | -0.041199 | 0 | -0.10986 | 0.082397 | -0.1648 | 0.1236 | -0.1236 | 0.27924 | 123.2025 | -0.068664 | 123.1247 | 123.3032 | 123.0835 | 123.1155 | 123.0423 | -123.2712 | -123.1247 | 123.0148 | 123.0835 | 60.0037 | 59.9213
20.8594 | 123.2895 | -60.0494 | 63.0203 | -0.048828 | 0.0021427 | 0.063931 | 0.065014 | 0.00050853 | -0.0031617 | -0.0010618 | -0.05423 | 0.0024844 | 0.069607 | 0.062611 | -0.0032598 | 0.0046164 | -0.00014306 | 0.004578 | 63.0341 | -60.1913 | 63.0295 | -59.9121 | -60.2737 | 0.009155 | 0.013733 | 63.0203 | -60.054 | 63.1027 | -60.0632 | -60.1822 | -59.9442 | -0.14191 | 0.013733 | 0.009155 | 0.13733 | 60.0586 | -0.22431 | 60.2005 | -0.082398 | -0.004578 | 0 | 0.082397 | -0.013733 | 0.10529 | -0.13275 | 0.10986 | -0.12817 | 0.27924 | 123.2208 | -0.009155 | 123.1567 | 123.2254 | 123.0743 | 123.0835 | 123.0698 | -123.2117 | -123.0743 | 123.0789 | 123.1522 | 60.054 | 60.0632
21.9219 | 123.3078 | -60.0037 | 63.0386 | -0.079346 | 0.0015019 | 0.062222 | 0.063305 | 0.00029473 | -0.00017087 | -0.0019162 | 0.043427 | 0.00098899 | 0.068966 | 0.065388 | -0.006037 | 0.0044028 | -0.0012113 | 0.041199 | 63.0295 | -60.1593 | 63.0981 | -59.8297 | -60.1776 | 0.10986 | 0.1236 | 62.9974 | -60.0403 | 63.1119 | -59.9899 | -60.0769 | -59.8801 | -0.15564 | -0.009155 | 0.05951 | 0.17395 | 60.1135 | -0.17395 | 60.2692 | -0.01831 | -0.036621 | -0.041198 | 0.073242 | 0.013733 | 0.1236 | -0.073242 | 0.16022 | -0.036621 | 0.32959 | 123.2574 | 0.050354 | 123.1522 | 123.1888 | 123.0377 | 123.0331 | 123.0011 | -123.1979 | -123.0789 | 123.1018 | 123.1155 | 60.0449 | 60.1273
22.8594 | 123.2666 | -60.0266 | 63.0295 | -0.0030519 | 0.0010745 | 0.062222 | 0.066296 | -0.0029095 | -0.0038025 | 0.001929 | -0.051178 | 0.00077539 | 0.067898 | 0.065174 | -0.0036872 | 0.00483 | 0.0037021 | 0 | 63.0753 | -60.2097 | 62.9333 | -60.0815 | -60.1685 | 0.086975 | 0.086975 | 63.0341 | -60.0769 | 63.089 | -60.0494 | -60.1547 | -59.9396 | -0.18311 | 0.045776 | -0.09613 | -0.054932 | 60.1135 | -0.14191 | 60.2966 | 0.041199 | -0.050354 | 0.004578 | 0.059509 | -0.022888 | 0.086975 | -0.12817 | 0.13733 | -0.07782 | 0.12817 | 123.143 | 0.027466 | 123.1659 | 123.2849 | 123.111 | 123.1018 | 123.0606 | -123.2391 | -123.1064 | 122.9599 | 123.1155 | 60.0266 | 60.1135
23.9062 | 123.2483 | -60.0266 | 63.0569 | -0.094604 | 0.0012881 | 0.061367 | 0.064587 | 0.0045673 | -0.0027345 | 0.00043363 | -0.057281 | 0.0012028 | 0.068112 | 0.064961 | -0.0058234 | 0.003762 | 0.0032749 | -0.050354 | 63.0341 | -60.2188 | 62.9562 | -59.9625 | -60.3104 | -0.059509 | -0.068665 | 62.9974 | -60.0815 | 63.0112 | -60.0861 | -60.2371 | -59.9945 | -0.19226 | -0.022888 | -0.10071 | 0.064087 | 59.967 | -0.28381 | 60.1593 | -0.091553 | -0.054932 | -0.059509 | -0.045777 | -0.05951 | 0.032043 | -0.21057 | 0.086975 | -0.15564 | 0.25635 | 123.175 | -0.004578 | 123.0927 | 123.2529 | 123.0789 | 123.0606 | 123.024 | -123.2758 | -123.1384 | 122.9828 | 123.0377 | 59.9762 | 59.9579
24.8594 | 123.262 | -60.0311 | 63.0753 | -0.010681 | 0.00043366 | 0.062863 | 0.063946 | -0.0012005 | -0.00038447 | -0.002557 | -0.023712 | 0.003339 | 0.070248 | 0.062824 | -0.0032598 | 0.0033346 | -0.00057046 | 0 | 63.089 | -60.2142 | 62.9745 | -59.9625 | -60.2921 | 0.022888 | 0.022888 | 63.0341 | -60.0769 | 63.0936 | -60.2188 | -60.0815 | -59.8251 | -0.1831 | 0.013733 | -0.10071 | 0.068665 | 60.054 | -0.26093 | 60.2371 | -0.07782 | -0.045776 | -0.041198 | 0.018311 | -0.18768 | 0.20599 | -0.050354 | 0.25177 | -0.004578 | 0.25177 | 123.1888 | -0.14191 | 123.1705 | 123.3032 | 123.111 | 123.1201 | 123.0652 | -123.2895 | -123.1522 | 123.0057 | 123.1247 | 60.0311 | 60.054
25.8594 | 123.2208 | -60.0311 | 63.0753 | -0.086975 | 0.0010745 | 0.063931 | 0.065228 | 0.00072213 | -0.00059807 | 0.0010746 | 0.0098572 | -7.901e-05 | 0.068753 | 0.058552 | -0.0024054 | 0.003121 | 0.0019931 | 0.041199 | 63.0844 | -60.1639 | 62.9974 | -59.8709 | -60.1822 | 0.07782 | 0.086975 | 63.0112 | -60.0449 | 63.0569 | -60.0815 | -60.173 | -59.9396 | -0.13275 | 0.009156 | -0.077819 | 0.16022 | 60.1089 | -0.15106 | 60.2417 | -0.018311 | -0.013733 | -0.064087 | -0.01831 | -0.050354 | 0.091553 | -0.14191 | 0.10529 | -0.12817 | 0.29297 | 123.1613 | -0.036621 | 123.1018 | 123.2483 | 123.056 | 123.1155 | 123.0423 | -123.2391 | -123.1201 | 123.0286 | 123.0881 | 60.0723 | 60.1181
26.9219 | 123.3353 | -60.0128 | 63.0112 | -0.048828 | 0.0015019 | 0.064358 | 0.063519 | -0.0031231 | -0.00081187 | -0.0027708 | 0.052582 | -0.00029261 | 0.068325 | 0.06432 | -0.0049688 | 0.00483 | -0.0016385 | -0.036621 | 63.0203 | -60.2051 | 63.0112 | -59.9121 | -60.2646 | 0.013733 | -0.013733 | 62.9562 | -60.0769 | 63.1073 | -60.0128 | -60.1044 | -59.903 | -0.19226 | 0.009156 | 0 | 0.10071 | 60.0266 | -0.25177 | 60.2188 | -0.059509 | -0.064087 | -0.054931 | 0.096131 | 0 | 0.10986 | -0.091553 | 0.17395 | -0.027466 | 0.29297 | 123.2162 | 0.064087 | 123.1842 | 123.2254 | 123.0331 | 123.0331 | 122.9691 | -123.2162 | -123.0881 | 123.024 | 123.1201 | 59.9762 | 59.9991
27.8594 | 123.2117 | -60.022 | 63.0753 | 0.019837 | 0.0027835 | 0.063931 | 0.065441 | -0.0020551 | -0.0029481 | -0.002557 | -0.042023 | 0.003339 | 0.06918 | 0.064747 | -0.0032598 | 0.003762 | -0.00014306 | 0.009155 | 63.0615 | -60.1822 | 62.9745 | -59.967 | -60.3012 | 0.032043 | 0.022888 | 63.0524 | -60.0906 | 63.0341 | -60.0906 | -60.1868 | -59.967 | -0.16022 | -0.013733 | -0.10071 | 0.054932 | 60.054 | -0.27923 | 60.2142 | -0.11902 | -0.068664 | -0.022888 | -0.041198 | -0.068664 | 0.054932 | -0.16479 | 0.1236 | -0.096131 | 0.21515 | 123.1567 | 0 | 123.1247 | 123.2437 | 123.143 | 123.0835 | 123.0743 | -123.2574 | -123.1659 | 122.9965 | 123.056 | 60.0311 | 60.0449
28.9062 | 123.2849 | -60.0403 | 63.0157 | -0.086975 | 0.0021427 | 0.064145 | 0.065228 | 0.0020037 | -0.00081187 | -0.00020717 | 0.022064 | 0.002698 | 0.070675 | 0.061756 | -0.0019782 | 0.0024802 | -0.0024931 | -0.059509 | 62.9929 | -60.2051 | 63.1393 | -59.9258 | -60.4111 | -0.032043 | -0.054932 | 62.9517 | -60.1044 | 63.089 | -60.0677 | -60.1456 | -59.9213 | -0.16479 | -0.022888 | 0.1236 | 0.11444 | 60.0082 | -0.37079 | 60.173 | -0.20599 | -0.064087 | -0.064087 | 0.073242 | -0.027466 | 0.11902 | -0.10529 | 0.18311 | -0.041199 | 0.27924 | 123.3444 | 0.036621 | 123.1934 | 123.1979 | 123.056 | 123.0331 | 122.9919 | -123.2208 | -123.1201 | 123.1796 | 123.1293 | 59.9808 | 59.9854
29.8594 | 123.3582 | -59.9625 | 63.0432 | -0.041199 | 0.0021427 | 0.063931 | 0.064159 | -0.0014143 | -0.0023071 | -0.0021298 | 0.019012 | 0.00077539 | 0.069607 | 0.067738 | -0.004328 | 0.0056846 | 0.00092494 | 0.050354 | 63.0432 | -60.173 | 63.1256 | -59.7977 | -60.173 | 0.12817 | 0.15106 | 62.9791 | -60.0357 | 63.1622 | -59.9533 | -60.0357 | -59.8526 | -0.21057 | 0 | 0.082397 | 0.16479 | 60.0906 | -0.21057 | 60.3012 | 0 | -0.073243 | -0.064087 | 0.11902 | 0.009155 | 0.10986 | -0.073243 | 0.18311 | 0 | 0.37537 | 123.2986 | 0.082398 | 123.1979 | 123.2162 | 123.0148 | 123.0057 | 122.9416 | -123.2162 | -123.0789 | 123.0881 | 123.1247 | 60.0128 | 60.1135
30.8906 | 123.23 | -60.0082 | 63.0707 | -0.041199 | 0.0019291 | 0.061795 | 0.066509 | 0.0017901 | -0.00081187 | -0.001489 | -0.038971 | 0.002698 | 0.068325 | 0.068379 | -0.0049688 | 0.0041892 | -0.00035666 | -0.013733 | 63.0707 | -60.2051 | 62.97 | -59.9442 | -60.2875 | 0.045776 | 0.004578 | 63.0615 | -60.054 | 63.0524 | -60.0861 | -60.1868 | -59.9533 | -0.19684 | 0 | -0.10071 | 0.064087 | 60.054 | -0.27924 | 60.2509 | -0.082398 | -0.045776 | -0.009156 | -0.018311 | -0.07782 | 0.054932 | -0.17853 | 0.10071 | -0.13275 | 0.26093 | 123.175 | -0.032044 | 123.1064 | 123.2758 | 123.1155 | 123.0789 | 123.0698 | -123.2758 | -123.1247 | 122.9782 | 123.0606 | 59.9945 | 60.0128
31.8594 | 123.262 | -60.022 | 63.0569 | -0.010681 | 0.0010745 | 0.063504 | 0.066296 | 0.0017901 | 0.00025633 | -0.0029844 | -0.051178 | 0.0024844 | 0.070248 | 0.065815 | -0.004328 | 0.003762 | 0.0019931 | 0.009155 | 63.0753 | -60.1959 | 63.0707 | -59.9533 | -60.2554 | 0.082397 | 0.064087 | 63.0203 | -60.0586 | 63.1073 | -60.054 | -60.1547 | -59.9213 | -0.17395 | 0.01831 | 0.013733 | 0.068665 | 60.1044 | -0.23346 | 60.2783 | -0.059509 | -0.036621 | -0.036621 | 0.050354 | -0.032043 | 0.10071 | -0.13275 | 0.13733 | -0.09613 | 0.24262 | 123.2666 | 0.004578 | 123.1659 | 123.2712 | 123.0789 | 123.0972 | 123.0423 | -123.2529 | -123.1155 | 123.0927 | 123.1293 | 60.0311 | 60.0861
32.9062 | 123.175 | -60.054 | 63.0203 | -0.048828 | 0.0025699 | 0.062649 | 0.068218 | 8.1126e-05 | 0.0013245 | -0.0012754 | -0.069489 | 0.002698 | 0.068112 | 0.063893 | -0.0039008 | 0.00483 | 0.00092494 | -0.036621 | 63.0524 | -60.2417 | 62.9562 | -59.9716 | -60.3516 | -0.045776 | -0.064087 | 63.0157 | -60.0952 | 63.0432 | -60.141 | -60.2371 | -59.9945 | -0.18768 | 0.032043 | -0.064087 | 0.082397 | 60.0082 | -0.29755 | 60.1959 | -0.10986 | -0.041199 | -0.004578 | 0.022888 | -0.086975 | 0.059509 | -0.18311 | 0.10071 | -0.14191 | 0.27008 | 123.1979 | -0.045776 | 123.1384 | 123.2941 | 123.111 | 123.1064 | 123.0698 | -123.262 | -123.1155 | 123.0103 | 123.0972 | 60.0174 | 59.9899
33.8594 | 123.2117 | -60.0082 | 63.0478 | -0.086975 | 0.0025699 | 0.06329 | 0.066509 | 0.0020037 | -0.0033753 | 0.0015018 | -0.0084534 | 0.0022708 | 0.070034 | 0.058125 | -0.002619 | 0.0054708 | -0.0039883 | 0.050354 | 63.0798 | -60.1822 | 62.9974 | -59.9304 | -60.2554 | 0.073242 | 0.045776 | 63.0615 | -60.0906 | 63.0249 | -60.0769 | -60.173 | -59.9899 | -0.17395 | 0.032043 | -0.050354 | 0.07782 | 60.0815 | -0.24719 | 60.2554 | -0.073242 | -0.082397 | 0.013732 | -0.022889 | -0.068664 | 0.018311 | -0.16479 | 0.10071 | -0.082398 | 0.25177 | 123.1796 | 0.013733 | 123.1155 | 123.262 | 123.1522 | 123.0881 | 123.0698 | -123.23 | -123.1384 | 123.0057 | 123.0331 | 60.0586 | 60.054
34.8906 | 123.23 | -60.0311 | 63.0661 | -0.0030519 | 0.0029971 | 0.06094 | 0.066723 | -0.00077327 | -0.0040161 | -0.0012754 | -0.023712 | 0.002698 | 0.067044 | 0.065388 | -0.0034736 | 0.0046164 | 0.0026339 | -0.022888 | 63.0524 | -60.2097 | 62.97 | -59.9442 | -60.2875 | 0.041199 | 0.009155 | 63.0661 | -60.0632 | 63.0341 | -60.0769 | -60.1685 | -59.9579 | -0.17853 | -0.013733 | -0.09613 | 0.086975 | 60.0723 | -0.25635 | 60.2509 | -0.07782 | -0.032043 | 0 | -0.032043 | -0.045776 | 0.073242 | -0.13733 | 0.10528 | -0.10529 | 0.2655 | 123.1796 | -0.013733 | 123.0972 | 123.262 | 123.1293 | 123.0835 | 123.0972 | -123.2758 | -123.1293 | 123.0011 | 123.0652 | 60.0082 | 60.0403
35.8594 | 123.2117 | -60.0311 | 63.0478 | -0.048828 | -0.00020714 | 0.062222 | 0.065868 | 0.0013629 | -0.00038447 | 0.00086083 | -0.0054016 | 0.0014164 | 0.069821 | 0.066029 | -0.0030462 | 0.0056846 | -0.00035666 | 0.050354 | 63.0661 | -60.1776 | 62.9608 | -59.903 | -60.0723 | 0.091553 | 0.082397 | 63.0112 | -60.0494 | 63.0798 | -60.0723 | -60.1456 | -59.9213 | -0.14648 | 0.01831 | -0.086976 | 0.12817 | 60.1227 | -0.041199 | 60.2692 | 0.10529 | -0.01831 | -0.036622 | 0.032043 | -0.041199 | 0.10986 | -0.11444 | 0.12817 | -0.096131 | 0.27466 | 123.1384 | -0.022889 | 123.1293 | 123.2437 | 123.0606 | 123.0972 | 123.0423 | -123.2254 | -123.0972 | 122.9919 | 123.111 | 60.0815 | 60.1135
36.9062 | 123.2391 | -60.0266 | 63.0569 | -0.079346 | 0.0027835 | 0.064999 | 0.0648 | 0.0030719 | -0.0033753 | -0.0023434 | -0.057281 | 0.0018436 | 0.070248 | 0.067524 | -0.0019782 | 0.003762 | -0.0024931 | 0.036621 | 63.0661 | -60.2188 | 63.0112 | -59.9121 | -60.2829 | 0.022888 | 0.045776 | 63.0203 | -60.0769 | 63.1027 | -60.0449 | -60.173 | -59.935 | -0.19226 | 0.009155 | -0.045777 | 0.11444 | 60.0494 | -0.25635 | 60.2417 | -0.064087 | -0.050354 | -0.036621 | 0.045776 | -0.018311 | 0.091552 | -0.14648 | 0.14191 | -0.096131 | 0.3067 | 123.23 | 0.032043 | 123.1796 | 123.2849 | 123.0972 | 123.0927 | 123.0469 | -123.2758 | -123.1338 | 123.0377 | 123.1293 | 60.0632 | 60.0723
37.8594 | 123.3307 | -59.9854 | 63.0157 | -0.071716 | 0.0021427 | 0.064785 | 0.0648 | 0.0028583 | -0.00059807 | -0.0021298 | 0.015961 | 0.0024844 | 0.068539 | 0.069233 | -0.0032598 | 0.0041892 | -0.0031339 | 0.050354 | 63.0203 | -60.173 | 63.0798 | -59.8022 | -60.1822 | 0.11444 | 0.14191 | 63.0066 | -60.0357 | 63.1485 | -59.9487 | -60.0449 | -59.8709 | -0.18768 | 0.004578 | 0.064087 | 0.18311 | 60.0998 | -0.19684 | 60.2875 | -0.009155 | -0.050354 | -0.009155 | 0.13275 | 0.036622 | 0.11444 | -0.059509 | 0.16479 | -0.009155 | 0.37079 | 123.2529 | 0.086976 | 123.1842 | 123.1934 | 123.0423 | 123.0057 | 122.9919 | -123.1888 | -123.0515 | 123.0652 | 123.1339 | 60.0357 | 60.1273
38.9062 | 123.1979 | -60.0586 | 63.0249 | -0.071716 | 0.0025699 | 0.062436 | 0.065655 | 0.0028583 | 0.00068353 | -0.00020717 | -0.075592 | 0.0012028 | 0.068966 | 0.066242 | -0.0051824 | 0.0056846 | -0.0039883 | -0.07782 | 63.0249 | -60.2509 | 62.9242 | -60.0311 | -60.3699 | -0.11444 | -0.16937 | 63.0203 | -60.1318 | 62.9929 | -60.1776 | -60.2646 | -60.0037 | -0.19226 | 0 | -0.10071 | 0.027466 | 59.9442 | -0.31128 | 60.1364 | -0.11902 | -0.073242 | -0.004577 | -0.032043 | -0.11902 | 0.054932 | -0.20599 | 0.12817 | -0.13275 | 0.21973 | 123.175 | -0.045776 | 123.1247 | 123.2758 | 123.1522 | 123.0835 | 123.0789 | -123.2758 | -123.1567 | 122.9828 | 123.0515 | 59.9808 | 59.8892
39.8594 | 123.2117 | -60.0082 | 63.0661 | -0.041199 | 0.00022006 | 0.062008 | 0.063732 | 0.0022173 | -0.00017087 | -0.0029844 | -0.0023498 | 0.0014164 | 0.069607 | 0.060902 | -0.0034736 | 0.0035482 | -0.0016385 | 0.07782 | 63.0524 | -60.2051 | 63.0112 | -59.9258 | -60.2554 | 0.068665 | 0.041199 | 63.0157 | -60.0677 | 63.0661 | -60.0723 | -60.1685 | -59.9716 | -0.19684 | -0.013733 | -0.054932 | 0.082398 | 60.0769 | -0.24719 | 60.2737 | -0.050354 | -0.059509 | -0.050354 | 0 | -0.064087 | 0.036621 | -0.16022 | 0.09613 | -0.10071 | 0.27924 | 123.2162 | -0.004578 | 123.1338 | 123.2574 | 123.0835 | 123.0606 | 123.024 | -123.2712 | -123.1338 | 123.0194 | 123.0743 | 60.0861 | 60.0494
40.8906 | 123.262 | -59.9808 | 63.0844 | -0.056457 | 0.0023563 | 0.063717 | 0.066296 | -0.0029095 | -0.0020935 | -0.0023434 | 0.0037536 | -7.901e-05 | 0.07217 | 0.066242 | -0.0045416 | 0.0018394 | -0.0014249 | 0.054932 | 63.0569 | -60.1639 | 63.0661 | -59.8526 | -60.2142 | 0.10071 | 0 | 63.0112 | -60.0815 | 63.1165 | -60.0357 | -60.141 | -59.9258 | -0.18311 | -0.027466 | -0.018311 | 0.12817 | 60.0815 | -0.23346 | 60.2646 | -0.050354 | -0.10071 | -0.073243 | 0.032043 | -0.054932 | 0.054932 | -0.16022 | 0.15564 | -0.059509 | 0.31128 | 123.23 | 0.045776 | 123.1979 | 123.2208 | 123.0927 | 123.0377 | 122.9919 | -123.2483 | -123.1659 | 123.0469 | 123.0972 | 60.0357 | 59.9808
41.8594 | 123.2162 | -60.0494 | 63.0524 | -0.064087 | 0.0034245 | 0.066067 | 0.06715 | -0.0014143 | -0.00059807 | 0.00043363 | -0.090851 | 0.00163 | 0.070034 | 0.070728 | -0.0045416 | 0.0050436 | 0.0011385 | -0.10529 | 63.0341 | -60.2692 | 62.9059 | -60.0449 | -60.4065 | -0.10071 | -0.14648 | 62.9974 | -60.1044 | 63.0112 | -60.1776 | -60.2646 | -59.9945 | -0.21973 | -0.01831 | -0.14648 | 0.004577 | 59.9487 | -0.35706 | 60.1685 | -0.13733 | -0.054932 | -0.054931 | -0.041199 | -0.12817 | 0.054931 | -0.21515 | 0.10986 | -0.16022 | 0.2243 | 123.175 | -0.073242 | 123.1155 | 123.3032 | 123.1018 | 123.0835 | 123.0469 | -123.3215 | -123.1567 | 122.9553 | 123.0606 | 59.9442 | 59.903
42.9062 | 123.2712 | -60.0357 | 63.0203 | -0.086975 | 0.0023563 | 0.063717 | 0.06715 | 0.00029473 | 4.273e-05 | -0.0021298 | -0.069489 | 0.00098899 | 0.067684 | 0.066883 | -0.002619 | 0.0044028 | -0.00035666 | -0.009155 | 63.0569 | -60.2188 | 62.9974 | -59.9121 | -60.2783 | -0.009155 | 0.022888 | 63.002 | -60.0906 | 63.0707 | -60.0769 | -60.1776 | -59.9442 | -0.18311 | 0.036621 | -0.022888 | 0.1236 | 60.0266 | -0.24261 | 60.2097 | -0.059509 | -0.054931 | -0.018311 | 0.050354 | -0.041198 | 0.091553 | -0.14191 | 0.14648 | -0.086975 | 0.3067 | 123.2162 | 0.013733 | 123.1613 | 123.2758 | 123.0927 | 123.0927 | 123.0377 | -123.2391 | -123.111 | 123.0331 | 123.1064 | 60.0266 | 60.0586
43.8594 | 123.2162 | -60.0266 | 63.0936 | 0.035095 | 0.0023563 | 0.062008 | 0.0648 | 0.0028583 | -0.0023071 | 0.0015018 | 0.0068054 | 0.0029116 | 0.070034 | 0.066456 | -0.0045416 | 0.0044028 | -0.00099766 | 0.004578 | 63.0707 | -60.1868 | 62.9974 | -59.9213 | -60.2829 | 0.054932 | 0.022888 | 63.0386 | -60.0861 | 63.0524 | -60.0677 | -60.1685 | -59.9762 | -0.16022 | -0.022888 | -0.09613 | 0.10529 | 60.0815 | -0.25635 | 60.2417 | -0.09613 | -0.05951 | -0.054932 | -0.041199 | -0.041199 | 0.050354 | -0.14191 | 0.10986 | -0.082397 | 0.2655 | 123.1842 | 0.018311 | 123.1384 | 123.2574 | 123.1247 | 123.0972 | 123.0652 | -123.2803 | -123.1796 | 123.024 | 123.0789 | 60.0311 | 60.0494
44.8906 | 123.2574 | -60.0174 | 63.0798 | -0.056457 | 0.0034245 | 0.063504 | 0.065441 | 0.00050853 | 4.273e-05 | 6.432e-06 | 0.0068054 | 0.00163 | 0.071102 | 0.065388 | -0.0024054 | 0.0056846 | 0.00071134 | 0.045776 | 63.0478 | -60.1776 | 63.0478 | -59.8526 | -60.228 | 0.059509 | 0.17853 | 62.9974 | -60.0769 | 63.0707 | -60.0403 | -60.1456 | -59.935 | -0.16022 | -0.032043 | -0.032043 | 0.16479 | 60.0769 | -0.21057 | 60.2371 | -0.050354 | -0.059509 | -0.082397 | -0.009155 | -0.022888 | 0.082397 | -0.12817 | 0.14191 | -0.068665 | 0.32501 | 123.2254 | 0.036621 | 123.1476 | 123.2254 | 123.0743 | 123.0652 | 123.0148 | -123.2574 | -123.1567 | 123.0652 | 123.0881 | 60.0632 | 60.1959
45.8594 | 123.3124 | -60.0128 | 63.0432 | -0.048828 | 0.0019291 | 0.063076 | 0.064373 | -0.00034607 | -0.00038447 | -0.0023434 | 0.022064 | 0.0029116 | 0.070889 | 0.066883 | -0.0034736 | 0.003762 | -0.0016385 | 0.059509 | 63.0157 | -60.1913 | 63.089 | -59.8206 | -60.1685 | 0.12817 | 0.14191 | 62.9929 | -60.0449 | 63.1439 | -59.9716 | -60.0494 | -59.8663 | -0.17853 | -0.027466 | 0.045776 | 0.19226 | 60.141 | -0.15564 | 60.3195 | 0.022888 | -0.032044 | -0.050354 | 0.10071 | 0.041198 | 0.14648 | -0.036621 | 0.17853 | -0.004577 | 0.37079 | 123.2803 | 0.073242 | 123.1888 | 123.2071 | 123.0377 | 123.0286 | 123.0057 | -123.2346 | -123.0881 | 123.1018 | 123.1567 | 60.0723 | 60.1547
46.9062 | 123.2346 | -60.0357 | 63.0478 | -0.033569 | 0.0019291 | 0.064358 | 0.065868 | 0.0041399 | -0.00017087 | 0.0021426 | -0.078644 | 0.0041934 | 0.068753 | 0.071369 | -0.0056098 | 0.003762 | -0.0044157 | -0.041199 | 63.0295 | -60.2188 | 62.9837 | -59.9625 | -60.347 | -0.068665 | -0.073242 | 63.0157 | -60.0815 | 63.0386 | -60.1227 | -60.2463 | -59.9945 | -0.18311 | -0.018311 | -0.064087 | 0.073243 | 59.967 | -0.31128 | 60.1501 | -0.12817 | -0.045776 | -0.032044 | -0.009156 | -0.086975 | 0.041199 | -0.21057 | 0.086975 | -0.16479 | 0.25635 | 123.2025 | -0.041199 | 123.1201 | 123.2483 | 123.0972 | 123.0652 | 123.0515 | -123.2666 | -123.1293 | 123.0194 | 123.0743 | 59.9945 | 59.9625
47.8594 | 123.2574 | -60.0037 | 63.0524 | -0.033569 | 6.46e-06 | 0.064999 | 0.064373 | -0.00013247 | 0.00068353 | 0.00043363 | 0.015961 | -7.901e-05 | 0.069607 | 0.068165 | -0.0032598 | 0.0039756 | -0.00057046 | 0.068665 | 63.0661 | -60.1685 | 63.0707 | -59.8343 | -60.1776 | 0.10529 | 0.13275 | 63.002 | -60.054 | 63.1119 | -60.0037 | -60.0815 | -59.8984 | -0.16479 | 0.013733 | 0.018311 | 0.16937 | 60.1089 | -0.17395 | 60.2737 | -0.009155 | -0.050354 | -0.050354 | 0.059509 | 0 | 0.10529 | -0.07782 | 0.15564 | -0.027466 | 0.33417 | 123.2391 | 0.050354 | 123.1659 | 123.2346 | 123.056 | 123.0698 | 123.0057 | -123.2208 | -123.1064 | 123.0743 | 123.1155 | 60.0723 | 60.1364
48.9062 | 123.2071 | -60.0266 | 63.0707 | -0.056457 | 0.00022006 | 0.064785 | 0.066082 | 0.00072213 | -0.0035889 | -0.002557 | -0.042023 | 0.003339 | 0.067684 | 0.071583 | -0.0041144 | 0.0041892 | 0.0017795 | 0 | 63.0844 | -60.2005 | 62.9654 | -59.9533 | -60.2829 | 0.018311 | 0.004578 | 63.0386 | -60.0815 | 63.0524 | -60.0723 | -60.1913 | -59.9487 | -0.17395 | 0.013733 | -0.10529 | 0.073242 | 60.0449 | -0.25635 | 60.2188 | -0.082398 | -0.054932 | -0.032044 | -0.018311 | -0.045777 | 0.07782 | -0.16479 | 0.13275 | -0.10986 | 0.24719 | 123.1659 | 0.009155 | 123.1338 | 123.2849 | 123.1201 | 123.111 | 123.0652 | -123.2712 | -123.1522 | 122.9919 | 123.0789 | 60.0266 | 60.0311
49.8594 | 123.317 | -60.0082 | 63.0249 | -0.064087 | 0.0032107 | 0.064358 | 0.063732 | 0.0015765 | 0.00025633 | -0.0010618 | 0.043427 | -0.00071981 | 0.069607 | 0.060261 | -0.0049688 | 0.0069662 | -0.0031339 | -0.009155 | 63.002 | -60.2051 | 63.0386 | -59.8618 | -60.2142 | 0.059509 | 0.045776 | 62.9791 | -60.0586 | 63.121 | -59.967 | -60.0677 | -59.8801 | -0.19684 | -0.022888 | 0.013733 | 0.14648 | 60.0677 | -0.20599 | 60.2646 | -0.009155 | -0.050354 | -0.045776 | 0.096131 | 0.041199 | 0.12817 | -0.059509 | 0.17853 | -0.009155 | 0.34332 | 123.2437 | 0.091553 | 123.1796 | 123.2071 | 123.0377 | 123.0103 | 122.9874 | -123.23 | -123.0835 | 123.0469 | 123.1293 | 59.9991 | 60.054
50.9062 | 123.2666 | -60.0082 | 63.0798 | 0.019837 | 0.0010745 | 0.063717 | 0.064587 | 0.00029473 | -0.0020935 | -0.001489 | -0.060333 | 0.0039798 | 0.070034 | 0.070088 | -0.0056098 | 0.00483 | -0.0029203 | 0.018311 | 63.0707 | -60.2188 | 63.0112 | -59.9121 | -60.2646 | 0.027466 | 0.050354 | 63.0295 | -60.0906 | 63.0844 | -60.054 | -60.1685 | -59.9304 | -0.21057 | -0.009155 | -0.068665 | 0.096131 | 60.0357 | -0.25635 | 60.2463 | -0.045776 | -0.082397 | -0.050354 | 0.004578 | -0.045776 | 0.07782 | -0.16022 | 0.16022 | -0.07782 | 0.3067 | 123.23 | 0.036621 | 123.175 | 123.2895 | 123.1201 | 123.0789 | 123.0377 | -123.2986 | -123.1705 | 123.0194 | 123.0927 | 60.0266 | 60.0586
51.8594 | 123.2437 | -60.0311 | 63.0798 | -0.071716 | -0.00042094 | 0.06094 | 0.065655 | 0.0028583 | -0.0027345 | -0.0029844 | -0.048126 | 0.0024844 | 0.069821 | 0.06432 | -0.0013372 | 0.0046164 | -0.0014249 | -0.009155 | 63.1027 | -60.2097 | 62.9883 | -59.9487 | -60.2737 | 0.032043 | 0.009155 | 63.0341 | -60.0815 | 63.121 | -60.0998 | -60.1318 | -59.9075 | -0.17853 | 0.022888 | -0.091553 | 0.082398 | 60.0632 | -0.24262 | 60.2417 | -0.064087 | -0.050354 | -0.045776 | 0.041199 | -0.068664 | 0.1236 | -0.10071 | 0.17395 | -0.050354 | 0.26093 | 123.1979 | -0.01831 | 123.2025 | 123.3124 | 123.1155 | 123.1338 | 123.0652 | -123.2895 | -123.1613 | 123.0194 | 123.1522 | 60.022 | 60.0403
52.8906 | 123.2666 | -60.0082 | 63.0936 | 0.0045776 | 0.0032107 | 0.06329 | 0.066723 | 0.0026447 | -0.0010255 | -0.00020717 | -0.051178 | 0.0035526 | 0.068539 | 0.062397 | -0.0041144 | 0.0054708 | -0.00014306 | 0.022888 | 63.0798 | -60.2142 | 63.0203 | -59.9121 | -60.2646 | 0.041199 | 0.045776 | 63.0112 | -60.0677 | 63.0981 | -60.054 | -60.1685 | -59.935 | -0.20599 | -0.013733 | -0.073242 | 0.096131 | 60.0494 | -0.25635 | 60.2554 | -0.050354 | -0.059509 | -0.082398 | 0.004578 | -0.045776 | 0.073242 | -0.16022 | 0.13275 | -0.10071 | 0.30212 | 123.2346 | 0.013733 | 123.1659 | 123.2941 | 123.0789 | 123.0881 | 123.0194 | -123.3078 | -123.1613 | 123.0286 | 123.1064 | 60.0311 | 60.054
53.8594 | 123.2346 | -60.0082 | 63.0707 | -0.033569 | 0.0021427 | 0.062863 | 0.064373 | 0.00050853 | 4.273e-05 | -0.001489 | -0.026764 | 0.00098899 | 0.070461 | 0.066029 | -0.0024054 | 0.0054708 | 0.00071134 | 0.050354 | 63.0295 | -60.1593 | 62.915 | -59.9121 | -60.0357 | 0.11444 | 0.10986 | 63.0295 | -60.0586 | 63.0753 | -60.054 | -60.1547 | -59.9579 | -0.15106 | -0.041199 | -0.15564 | 0.096131 | 60.1227 | -0.027466 | 60.2737 | 0.1236 | -0.050354 | -0.041199 | 0.004577 | -0.045776 | 0.050354 | -0.14648 | 0.10071 | -0.09613 | 0.24719 | 123.0743 | 0.004578 | 123.1338 | 123.1888 | 123.0881 | 123.0377 | 123.0377 | -123.23 | -123.1293 | 122.9233 | 123.0835 | 60.0586 | 60.1181
54.8906 | 123.3444 | -59.9945 | 63.0112 | -0.056457 | 0.0019291 | 0.063504 | 0.065868 | 0.0020037 | -0.0010255 | -0.00084817 | 0.015961 | 0.00056179 | 0.068325 | 0.058552 | -0.0036872 | 0.0033346 | -0.0020657 | 0.041199 | 63.0295 | -60.1593 | 63.0798 | -59.7977 | -60.1776 | 0.10986 | 0.14648 | 62.9929 | -60.022 | 63.1531 | -59.9533 | -60.0403 | -59.8526 | -0.16479 | 0.018311 | 0.068665 | 0.19684 | 60.1044 | -0.18311 | 60.2692 | -0.01831 | -0.027466 | -0.01831 | 0.14191 | 0.041199 | 0.14191 | -0.045776 | 0.16937 | -0.01831 | 0.36163 | 123.2391 | 0.068665 | 123.175 | 123.1888 | 123.0148 | 123.024 | 122.9874 | -123.1705 | -123.0331 | 123.0743 | 123.1476 | 60.0357 | 60.141
55.8594 | 123.3307 | -59.9854 | 63.0432 | -0.048828 | 0.0019291 | 0.062649 | 0.064587 | 0.00072213 | 4.273e-05 | 0.0010746 | 0.015961 | 0.00056179 | 0.069393 | 0.064533 | -0.0030462 | 0.0039756 | 0.00049774 | 0.050354 | 63.0157 | -60.173 | 63.0981 | -59.7977 | -60.1685 | 0.13733 | 0.13733 | 62.9837 | -60.0311 | 63.1805 | -59.9579 | -60.0586 | -59.8389 | -0.18768 | -0.027466 | 0.054932 | 0.18768 | 60.1227 | -0.1831 | 60.3104 | 0.004578 | -0.045776 | -0.059509 | 0.13733 | 0.027466 | 0.14648 | -0.073242 | 0.19226 | -0.027466 | 0.37537 | 123.2712 | 0.073242 | 123.2117 | 123.1888 | 123.0148 | 123.0011 | 122.9691 | -123.2162 | -123.0743 | 123.0835 | 123.1659 | 60.0357 | 60.1227
56.9062 | 123.2346 | -60.0128 | 63.1027 | -0.064087 | 0.00043366 | 0.062436 | 0.064587 | 0.00029473 | -0.0014527 | -0.0044796 | -0.023712 | 0.0022708 | 0.070034 | 0.064533 | -0.004328 | 0.0035482 | -0.0012113 | -0.013733 | 63.0707 | -60.2097 | 62.9745 | -59.9396 | -60.2783 | 0.036621 | 0.036621 | 63.0524 | -60.0586 | 63.0478 | -60.0861 | -60.1822 | -59.967 | -0.19684 | -0.032043 | -0.12817 | 0.073242 | 60.0494 | -0.2655 | 60.2463 | -0.068664 | -0.045777 | -0.050354 | -0.054931 | -0.073243 | 0.045776 | -0.16937 | 0.091553 | -0.1236 | 0.27008 | 123.1842 | -0.027466 | 123.1064 | 123.2803 | 123.111 | 123.0835 | 123.0652 | -123.3124 | -123.1613 | 122.9874 | 123.0606 | 59.9991 | 60.0494
57.8594 | 123.3398 | -59.9991 | 63.0524 | -0.071716 | 0.00064726 | 0.062863 | 0.064373 | 0.00029473 | -0.00059807 | -0.00084817 | 0.028168 | -0.00071981 | 0.069607 | 0.061329 | -0.0047552 | 0.0052572 | -0.00014306 | -0.009155 | 63.0386 | -60.1913 | 63.0432 | -59.8526 | -60.2188 | 0.082397 | 0.059509 | 62.9883 | -60.0632 | 63.1393 | -59.9762 | -60.0769 | -59.8801 | -0.19226 | -0.013733 | -0.009155 | 0.14648 | 60.0815 | -0.21973 | 60.2737 | -0.027466 | -0.064087 | -0.064087 | 0.086975 | 0.022888 | 0.11902 | -0.07782 | 0.1831 | -0.013733 | 0.33874 | 123.2346 | 0.086975 | 123.2025 | 123.23 | 123.0515 | 123.0377 | 122.9874 | -123.2437 | -123.1155 | 123.0423 | 123.1384 | 59.9899 | 60.0586
58.9062 | 123.23 | -60.0174 | 63.0615 | -0.033569 | 0.0019291 | 0.063076 | 0.066082 | 0.0022173 | -0.0031617 | -0.00042077 | -0.087799 | 0.0022708 | 0.070248 | 0.069447 | -0.0062506 | 0.0039756 | -0.00078406 | 0.027466 | 63.0249 | -60.2188 | 63.0112 | -59.9213 | -60.2692 | 0.045776 | 0.050354 | 63.0432 | -60.0677 | 63.1027 | -60.054 | -60.1593 | -59.9167 | -0.20142 | -0.036621 | -0.050354 | 0.09613 | 60.0632 | -0.25177 | 60.2646 | -0.050354 | -0.050354 | -0.01831 | 0.041199 | -0.036621 | 0.10071 | -0.14191 | 0.15106 | -0.091553 | 0.29755 | 123.23 | 0.013733 | 123.1705 | 123.2437 | 123.111 | 123.0423 | 123.0606 | -123.2803 | -123.1293 | 123.0286 | 123.1201 | 60.0449 | 60.0677
59.8594 | 123.3627 | -59.9991 | 63.0203 | -0.048828 | 0.00086086 | 0.063931 | 0.063519 | 0.0030719 | 0.00025633 | -0.0027708 | 0.025116 | 0.00056179 | 0.068753 | 0.069233 | -0.004328 | 0.0033346 | 0.00028414 | 0.050354 | 63.0478 | -60.173 | 63.0936 | -59.8068 | -60.173 | 0.11902 | 0.15106 | 62.9974 | -60.054 | 63.1622 | -59.9579 | -60.0403 | -59.848 | -0.17395 | 0.027466 | 0.073242 | 0.19226 | 60.1181 | -0.17395 | 60.2921 | 0 | -0.054932 | -0.022888 | 0.14191 | 0.041198 | 0.15106 | -0.041199 | 0.20599 | 0.013733 | 0.36621 | 123.2666 | 0.09613 | 123.2162 | 123.2208 | 123.0515 | 123.0469 | 122.9965 | -123.1934 | -123.0743 | 123.0927 | 123.1613 | 60.0494 | 60.1501
60.8906 | 123.3124 | -59.9991 | 63.0157 | -0.094604 | 0.0023563 | 0.064145 | 0.0648 | 0.0011493 | -0.0012391 | -0.0010618 | 0.00070198 | 0.00077539 | 0.068966 | 0.064961 | -0.0041144 | 0.0033346 | -0.0024931 | -0.041199 | 63.0157 | -60.1959 | 63.0157 | -59.8938 | -60.2692 | -0.004578 | -0.032043 | 62.97 | -60.0815 | 63.0981 | -60.0266 | -60.1135 | -59.8801 | -0.19684 | 0 | 0 | 0.10529 | 59.9945 | -0.27008 | 60.1913 | -0.073242 | -0.082398 | -0.045776 | 0.082398 | -0.027466 | 0.11902 | -0.11444 | 0.20142 | -0.032043 | 0.30212 | 123.2117 | 0.054932 | 123.1796 | 123.2117 | 123.0515 | 123.0148 | 122.9691 | -123.2117 | -123.0972 | 123.0148 | 123.0972 | 59.9579 | 59.967
61.8594 | 123.2117 | -60.022 | 63.0844 | -0.056457 | 0.00043366 | 0.062222 | 0.065655 | -0.00055967 | -0.0018799 | -0.0027708 | -0.023712 | 0.0014164 | 0.06918 | 0.063038 | -0.0064642 | 0.0044028 | -0.0029203 | 0.041199 | 63.0524 | -60.2142 | 63.0341 | -59.848 | -60.2692 | 0.073242 | 0.054932 | 63.0386 | -60.0861 | 63.0478 | -60.0815 | -60.1639 | -59.9487 | -0.19226 | -0.032044 | -0.050354 | 0.17395 | 60.0952 | -0.24719 | 60.2875 | -0.054932 | -0.064087 | -0.045777 | -0.036621 | -0.059509 | 0.073243 | -0.14191 | 0.13733 | -0.077819 | 0.36621 | 123.2483 | 0.004578 | 123.1339 | 123.2666 | 123.1247 | 123.0743 | 123.0606 | -123.2986 | -123.1705 | 123.056 | 123.0698 | 60.0632 | 60.0769
62.8906 | 123.3261 | -60.0037 | 63.0661 | -0.02594 | 0.0017155 | 0.062863 | 0.063519 | 0.0011493 | -0.0046571 | -0.00020717 | -0.0023498 | -0.00050621 | 0.066616 | 0.069874 | -0.0034736 | 0.0050436 | -0.00057046 | 0.004578 | 63.0157 | -60.1913 | 63.0524 | -59.816 | -60.1547 | 0.10986 | 0.12817 | 62.9929 | -60.0266 | 63.1851 | -59.9075 | -60.0266 | -59.8251 | -0.18768 | -0.050354 | -0.013733 | 0.18768 | 60.1135 | -0.15106 | 60.3012 | 0.036621 | -0.022888 | -0.073242 | 0.11902 | 0.09613 | 0.17853 | -0.022888 | 0.20142 | 0 | 0.37537 | 123.2437 | 0.11902 | 123.2117 | 123.2071 | 123.0194 | 123.0194 | 122.9965 | -123.2574 | -123.0927 | 123.056 | 123.1888 | 60.0082 | 60.1318
63.8594 | 123.349 | -59.9762 | 63.0386 | -0.041199 | 0.00086086 | 0.061154 | 0.066082 | 0.0052081 | -0.0020935 | 6.432e-06 | 0.0037536 | 0.0024844 | 0.067471 | 0.066883 | -0.002619 | 0.0039756 | 0.0011385 | -0.027466 | 63.0203 | -60.1913 | 63.0524 | -59.8801 | -60.2234 | 0.059509 | 0.045776 | 62.9974 | -60.0677 | 63.1302 | -59.9854 | -60.0815 | -59.8755 | -0.21515 | -0.01831 | 0.013733 | 0.09613 | 60.0357 | -0.24719 | 60.2509 | -0.032044 | -0.091553 | -0.041198 | 0.091553 | -0.009156 | 0.10071 | -0.10529 | 0.19226 | -0.013733 | 0.31128 | 123.2437 | 0.082397 | 123.1979 | 123.2117 | 123.0652 | 122.9965 | 122.9736 | -123.23 | -123.1064 | 123.0286 | 123.1064 | 59.9487 | 60.022
64.8906 | 123.3215 | -60.0128 | 63.0615 | -0.094604 | 0.0021427 | 0.064785 | 0.065014 | -0.0037641 | -0.0016663 | -0.00042077 | -0.0084534 | 0.0018436 | 0.067471 | 0.067524 | -0.0028326 | 0.0046164 | -0.0063383 | 0.054932 | 63.0478 | -60.1776 | 63.1027 | -59.8297 | -60.1913 | 0.11444 | 0.13733 | 63.0341 | -60.0357 | 63.1119 | -59.9808 | -60.0677 | -59.8846 | -0.1648 | -0.013732 | 0.041199 | 0.1831 | 60.1273 | -0.17853 | 60.2921 | -0.013733 | -0.022889 | -0.027465 | 0.050354 | 0.032043 | 0.12817 | -0.054932 | 0.15106 | -0.032043 | 0.3479 | 123.2803 | 0.054932 | 123.1476 | 123.2254 | 123.0698 | 123.0606 | 123.0469 | -123.2391 | -123.0972 | 123.1155 | 123.1247 | 60.0677 | 60.1501
65.8594 | 123.3536 | -59.9991 | 63.0157 | -0.10223 | 0.0036381 | 0.060727 | 0.063519 | 8.1126e-05 | -0.00038447 | -0.0023434 | -0.014557 | 0.00034819 | 0.06918 | 0.061543 | -0.0032598 | 0.0050436 | -0.0033475 | 0.004578 | 63.0386 | -60.1868 | 63.0661 | -59.8206 | -60.2005 | 0.07782 | 0.10986 | 62.9929 | -60.0632 | 63.1622 | -59.9442 | -60.054 | -59.8434 | -0.18768 | 0.022888 | 0.050354 | 0.17853 | 60.0769 | -0.20142 | 60.2646 | -0.013732 | -0.064087 | -0.022888 | 0.14648 | 0.054931 | 0.15564 | -0.054932 | 0.21973 | 0.009155 | 0.36621 | 123.2529 | 0.11902 | 123.2254 | 123.2254 | 123.056 | 123.0377 | 122.9919 | -123.2025 | -123.0789 | 123.0652 | 123.1613 | 60.0037 | 60.1089
66.8906 | 123.349 | -59.9945 | 63.0295 | 0.0045776 | 0.0029971 | 0.062008 | 0.065014 | 0.0039263 | -0.0023071 | 0.00022003 | 0.019012 | 0.00056179 | 0.068112 | 0.060902 | -0.0053962 | 0.0033346 | 0.0024203 | 0.036621 | 63.0295 | -60.1822 | 63.0981 | -59.7931 | -60.1547 | 0.1236 | 0.16937 | 62.9974 | -60.0449 | 63.1577 | -59.9533 | -60.0494 | -59.8526 | -0.18768 | 0 | 0.068665 | 0.20142 | 60.1181 | -0.16022 | 60.3058 | 0.027466 | -0.050354 | -0.032043 | 0.12817 | 0.041199 | 0.14191 | -0.054931 | 0.19226 | -0.004577 | 0.3891 | 123.2803 | 0.091553 | 123.2025 | 123.2117 | 123.0423 | 123.024 | 122.9919 | -123.2117 | -123.0743 | 123.0927 | 123.1522 | 60.0311 | 60.1639
67.8594 | 123.381 | -59.9854 | 63.0295 | -0.02594 | 0.00043366 | 0.062436 | 0.065228 | 0.00072213 | -0.0016663 | -0.0010618 | -0.0084534 | 0.0018436 | 0.068966 | 0.067311 | -0.0041144 | 0.0050436 | -0.0044157 | 0.036621 | 63.0432 | -60.1639 | 63.1256 | -59.7794 | -60.1456 | 0.10071 | 0.14648 | 63.002 | -60.0449 | 63.1668 | -59.9487 | -60.0357 | -59.8526 | -0.17853 | 0.013733 | 0.09613 | 0.20599 | 60.0861 | -0.16022 | 60.2646 | 0.01831 | -0.059509 | -0.027466 | 0.13733 | 0.036622 | 0.13275 | -0.050354 | 0.19226 | 0.009155 | 0.38452 | 123.2895 | 0.096131 | 123.2117 | 123.2071 | 123.0469 | 123.0286 | 122.9874 | -123.1934 | -123.0743 | 123.111 | 123.1522 | 60.022 | 60.1318
68.9062 | 123.2483 | -60.0494 | 63.0066 | -0.086975 | 0.00086086 | 0.064572 | 0.067791 | 0.0015765 | 0.00089713 | 0.0012882 | -0.096954 | 0.002698 | 0.068325 | 0.071369 | -0.0053962 | 0.0050436 | 0.00092494 | -0.10529 | 63.0386 | -60.2417 | 62.9379 | -59.9899 | -60.3699 | -0.10986 | -0.13275 | 62.9883 | -60.1318 | 63.0478 | -60.1181 | -60.2234 | -59.9533 | -0.19226 | 0.032043 | -0.068665 | 0.059509 | 59.9396 | -0.32043 | 60.1318 | -0.12817 | -0.082398 | -0.018311 | 0.041199 | -0.068665 | 0.09613 | -0.17395 | 0.17853 | -0.091553 | 0.25177 | 123.1796 | 0.013733 | 123.1796 | 123.2803 | 123.1201 | 123.0881 | 123.0377 | -123.2483 | -123.1384 | 122.9874 | 123.0972 | 59.9442 | 59.9167
69.8594 | 123.2895 | -59.9991 | 63.0066 | -0.094604 | -0.00084814 | 0.061795 | 0.062664 | -0.0022687 | -0.0010255 | -0.0012754 | -0.011505 | 0.0024844 | 0.067898 | 0.066883 | -0.0047552 | 0.0052572 | -0.0020657 | -0.054932 | 63.0157 | -60.2188 | 63.0112 | -59.9396 | -60.2509 | -0.009155 | -0.036621 | 62.9837 | -60.0677 | 63.0981 | -60.0311 | -60.1318 | -59.9075 | -0.21973 | 0.009155 | 0.004577 | 0.059509 | 59.9899 | -0.25177 | 60.2097 | -0.032043 | -0.068665 | -0.022888 | 0.091553 | -0.032044 | 0.091552 | -0.13275 | 0.16022 | -0.064087 | 0.27924 | 123.23 | 0.036621 | 123.1659 | 123.2346 | 123.0515 | 123.0148 | 122.9828 | -123.2254 | -123.0743 | 123.0103 | 123.0972 | 59.9442 | 59.9625
70.9062 | 123.2071 | -60.0174 | 63.0936 | 0.0045776 | 0.0010745 | 0.06329 | 0.066082 | 0.00072213 | -0.0020935 | -0.0036252 | -0.084747 | 0.0014164 | 0.068966 | 0.065602 | -0.0024054 | 0.0041892 | 0.0017795 | 0 | 63.0753 | -60.2005 | 62.9837 | -59.9487 | -60.2829 | 0.018311 | 0.009155 | 63.0478 | -60.0723 | 62.9745 | -60.0449 | -60.0311 | -59.8709 | -0.1831 | -0.018311 | -0.10986 | 0.068665 | 60.0357 | -0.2655 | 60.2188 | -0.082398 | -0.054932 | -0.045776 | -0.11902 | -0.027466 | 0.14648 | -0.013733 | 0.20142 | 0.041199 | 0.25177 | 123.1842 | 0.027466 | 123.0469 | 123.2758 | 123.1201 | 123.0927 | 123.0652 | -123.2941 | -123.1659 | 123.0011 | 122.9919 | 60.0174 | 60.0266
71.8594 | 123.2254 | -60.0174 | 63.0753 | -0.010681 | 0.0010745 | 0.062436 | 0.065441 | 0.00029473 | -0.0042297 | -0.0036252 | -0.05423 | 0.0024844 | 0.069821 | 0.060688 | -0.0028326 | 0.0039756 | -0.0022793 | -0.009155 | 63.0707 | -60.2005 | 62.9608 | -59.9487 | -60.2875 | 0.022888 | 0.009155 | 63.0157 | -60.0723 | 63.0569 | -60.0861 | -60.2051 | -59.9487 | -0.1831 | -0.004577 | -0.11444 | 0.068665 | 60.0403 | -0.27008 | 60.2234 | -0.086976 | -0.054932 | -0.059509 | -0.01831 | -0.068665 | 0.068665 | -0.18768 | 0.1236 | -0.13275 | 0.25177 | 123.1613 | -0.013733 | 123.1293 | 123.2712 | 123.0881 | 123.0881 | 123.0331 | -123.2758 | -123.1476 | 122.9782 | 123.0743 | 60.0082 | 60.0266
72.8906 | 123.3215 | -59.9854 | 63.002 | -0.041199 | 0.00022006 | 0.063504 | 0.062023 | 0.00072213 | 0.00025633 | -0.00084817 | 0.012909 | 0.0018436 | 0.06683 | 0.065388 | -0.002619 | 0.00483 | -0.00099766 | 0.050354 | 63.0386 | -60.1913 | 63.1027 | -59.761 | -60.1593 | 0.12817 | 0.15564 | 63.0157 | -60.0632 | 63.1622 | -59.9487 | -60.0266 | -59.8434 | -0.20599 | 0.036621 | 0.10071 | 0.22431 | 60.1135 | -0.17395 | 60.3195 | 0.032043 | -0.077819 | 0.013733 | 0.16022 | 0.036622 | 0.14191 | -0.041198 | 0.21973 | 0.036621 | 0.4303 | 123.2941 | 0.11444 | 123.2254 | 123.23 | 123.0789 | 123.024 | 123.0011 | -123.1934 | -123.0652 | 123.0881 | 123.1476 | 60.0357 | 60.141
73.8594 | 123.2895 | -60.022 | 63.0432 | -0.071716 | 0.0027835 | 0.062649 | 0.064587 | -0.0020551 | -0.0018799 | -0.00042077 | -0.0023498 | 0.00013459 | 0.067257 | 0.065602 | -0.0032598 | 0.0022666 | 0.00092494 | 0.068665 | 63.0157 | -60.1456 | 63.0661 | -59.8206 | -60.173 | 0.1236 | 0.11444 | 63.0249 | -60.0449 | 63.1302 | -59.9991 | -60.0952 | -59.8801 | -0.1236 | -0.027466 | 0.022888 | 0.20142 | 60.1456 | -0.15106 | 60.2692 | -0.027466 | -0.022888 | -0.018311 | 0.086975 | 0.022889 | 0.14191 | -0.073242 | 0.16479 | -0.050354 | 0.32501 | 123.2117 | 0.045777 | 123.175 | 123.1613 | 123.0698 | 123.0377 | 123.0469 | -123.1888 | -123.0881 | 123.0881 | 123.1522 | 60.0906 | 60.1364
74.9062 | 123.23 | -60.0174 | 63.0981 | -0.02594 | 0.00022006 | 0.062222 | 0.066082 | 0.00050853 | -0.00038447 | -0.00020717 | -0.057281 | 0.00077539 | 0.068325 | 0.069447 | -0.006037 | 0.0073936 | -0.00035666 | -0.022888 | 63.0753 | -60.228 | 62.9745 | -59.9625 | -60.2966 | 0.022888 | -0.018311 | 63.0386 | -60.0723 | 63.0569 | -60.0815 | -60.1685 | -59.9487 | -0.21057 | -0.022889 | -0.1236 | 0.054932 | 60.0403 | -0.27924 | 60.2509 | -0.068665 | -0.054932 | -0.05951 | -0.041199 | -0.064087 | 0.068665 | -0.15106 | 0.1236 | -0.09613 | 0.2655 | 123.2025 | -0.009155 | 123.1293 | 123.3032 | 123.111 | 123.0927 | 123.056 | -123.3261 | -123.1705 | 122.9919 | 123.0743 | 59.9945 | 59.9991
75.8594 | 123.3353 | -59.9945 | 63.0157 | -0.02594 | 0.0019291 | 0.061367 | 0.065014 | -0.0018415 | -0.0027345 | -0.0023434 | 0.022064 | 0.0020572 | 0.069393 | 0.061329 | -0.0053962 | 0.0041892 | -0.00035666 | 0.045776 | 63.0157 | -60.1685 | 63.1073 | -59.7656 | -60.1501 | 0.1236 | 0.14191 | 63.0066 | -60.054 | 63.1668 | -59.9487 | -60.0449 | -59.8434 | -0.17395 | 0 | 0.091553 | 0.22888 | 60.1181 | -0.15564 | 60.2921 | 0.018311 | -0.059509 | -0.009155 | 0.15106 | 0.045777 | 0.15106 | -0.050354 | 0.21057 | 0.009155 | 0.40283 | 123.2758 | 0.10529 | 123.2208 | 123.1842 | 123.0606 | 123.0103 | 123.0011 | -123.1842 | -123.0698 | 123.1018 | 123.1613 | 60.0403 | 60.1364
76.9062 | 123.2483 | -59.9991 | 63.0386 | -0.0030519 | 0.0012881 | 0.063717 | 0.06715 | 0.0011493 | -0.0029481 | 0.00086083 | -0.10001 | 0.0022708 | 0.067684 | 0.070515 | -0.0032598 | 0.00483 | -0.0031339 | -0.004578 | 63.0569 | -60.2051 | 62.9974 | -59.935 | -60.2692 | -0.041199 | 0.10529 | 63.0432 | -60.0769 | 63.0981 | -60.0449 | -60.1547 | -59.9075 | -0.20599 | 0.018311 | -0.041198 | 0.064086 | 59.9579 | -0.27008 | 60.1639 | -0.064087 | -0.07782 | 0.004578 | 0.05951 | -0.045777 | 0.091552 | -0.15564 | 0.16937 | -0.07782 | 0.27008 | 123.2025 | 0.032043 | 123.175 | 123.262 | 123.1201 | 123.056 | 123.0423 | -123.2437 | -123.1155 | 122.9965 | 123.0972 | 59.9945 | 60.1044
77.8594 | 123.3078 | -60.0128 | 63.0341 | -0.10986 | 0.00043366 | 0.062863 | 0.065014 | 0.0020037 | -0.0038025 | 0.0010746 | -0.011505 | 0.0014164 | 0.070675 | 0.063252 | -0.0034736 | 0.0056846 | 0.0045565 | -0.050354 | 63.0249 | -60.1868 | 62.9974 | -59.9167 | -60.2783 | 0 | -0.045776 | 62.9929 | -60.0723 | 63.121 | -60.0494 | -60.1135 | -59.8892 | -0.17395 | -0.009156 | -0.036621 | 0.09613 | 60.0128 | -0.2655 | 60.1868 | -0.091552 | -0.05951 | -0.041199 | 0.086975 | -0.036621 | 0.1236 | -0.10071 | 0.18311 | -0.041198 | 0.27008 | 123.1842 | 0.022889 | 123.1934 | 123.2117 | 123.0652 | 123.0377 | 123.0057 | -123.2208 | -123.1064 | 123.0103 | 123.1338 | 59.9625 | 59.967
78.8906 | 123.2483 | -60.0037 | 63.0157 | -0.13275 | 0.00043366 | 0.064358 | 0.065441 | -0.00055967 | -0.00059807 | -0.003198 | 0.0068054 | 0.00163 | 0.069607 | 0.064533 | -0.0021918 | 0.0050436 | 0.0024203 | -0.059509 | 63.002 | -60.2051 | 62.9929 | -59.9075 | -60.2646 | -0.009155 | -0.064087 | 62.9837 | -60.0769 | 63.0936 | -60.0586 | -60.1135 | -59.9121 | -0.20142 | -0.013733 | -0.022888 | 0.09613 | 59.9945 | -0.26093 | 60.1959 | -0.059509 | -0.073242 | -0.032043 | 0.07782 | -0.054932 | 0.091553 | -0.10986 | 0.16479 | -0.036621 | 0.29755 | 123.1979 | 0.01831 | 123.1705 | 123.2071 | 123.0606 | 123.0057 | 122.9874 | -123.2208 | -123.0927 | 122.9965 | 123.0972 | 59.9442 | 59.9396
79.8594 | 123.3582 | -59.9991 | 63.0249 | -0.071716 | 0.0015019 | 0.062649 | 0.065441 | -0.00013247 | -0.00059807 | -0.002557 | -0.0054016 | 0.002698 | 0.068539 | 0.063465 | -0.0032598 | 0.0052572 | -0.00035666 | -0.004578 | 63.0203 | -60.1913 | 63.0615 | -59.8114 | -60.1822 | 0.082397 | 0.15106 | 62.9883 | -60.0494 | 63.1714 | -59.9396 | -60.0357 | -59.8251 | -0.19226 | -0.004577 | 0.036621 | 0.18768 | 60.0815 | -0.18311 | 60.2737 | 0.009155 | -0.050354 | -0.036621 | 0.14649 | 0.059509 | 0.17395 | -0.036622 | 0.2243 | 0.013732 | 0.37994 | 123.2529 | 0.10986 | 123.2208 | 123.2117 | 123.0377 | 123.0194 | 122.9874 | -123.2162 | -123.0743 | 123.0606 | 123.1705 | 59.9945 | 60.1501
80.8906 | 123.3078 | -60.0128 | 63.0157 | -0.056457 | 0.0015019 | 0.063076 | 0.063519 | 0.0013629 | 0.0015381 | 0.00043363 | -0.02066 | -0.00093361 | 0.07153 | 0.067311 | -0.0032598 | 0.0041892 | 0.0011385 | 0.050354 | 63.0341 | -60.1639 | 63.089 | -59.8206 | -60.1547 | 0.11444 | 0.15106 | 62.9929 | -60.0357 | 63.1531 | -59.9625 | -60.0586 | -59.8663 | -0.15106 | 0.018311 | 0.073242 | 0.19226 | 60.1273 | -0.14191 | 60.2783 | 0.009155 | -0.022889 | -0.022888 | 0.13733 | 0.050354 | 0.14648 | -0.045777 | 0.16937 | -0.022888 | 0.34332 | 123.2529 | 0.073243 | 123.1888 | 123.1979 | 123.0286 | 123.0469 | 123.0057 | -123.1796 | -123.0515 | 123.1018 | 123.1659 | 60.0632 | 60.1639
81.8594 | 123.2346 | -60.0311 | 63.0478 | -0.010681 | 0.00064726 | 0.062863 | 0.066509 | 0.0017901 | -0.00081187 | 6.432e-06 | -0.057281 | 0.0024844 | 0.068539 | 0.067524 | -0.0056098 | 0.0054708 | -0.00035666 | -0.004578 | 63.0844 | -60.2097 | 62.9745 | -59.9396 | -60.2921 | 0.022888 | -0.009155 | 63.0615 | -60.0723 | 63.0844 | -60.054 | -60.173 | -59.9167 | -0.17853 | 0.036621 | -0.073243 | 0.091553 | 60.054 | -0.26093 | 60.2325 | -0.082397 | -0.041199 | 0.013732 | 0.036621 | -0.022888 | 0.11444 | -0.14191 | 0.15564 | -0.10071 | 0.27008 | 123.1842 | 0.018311 | 123.1567 | 123.2941 | 123.1338 | 123.1155 | 123.0927 | -123.2574 | -123.1201 | 123.0057 | 123.1155 | 60.0266 | 60.022
82.8594 | 123.2895 | -59.9991 | 63.0386 | -0.064087 | 0.0023563 | 0.063717 | 0.066723 | 0.0032855 | -0.00059807 | 6.432e-06 | -0.032867 | 0.0022708 | 0.066189 | 0.06667 | -0.0030462 | 0.0018394 | -0.0022793 | 0.054932 | 63.0478 | -60.1776 | 63.0844 | -59.816 | -60.1639 | 0.13733 | 0.13733 | 63.0157 | -60.0494 | 63.1439 | -59.9945 | -60.054 | -59.8755 | -0.17853 | 0.009156 | 0.045777 | 0.18311 | 60.1364 | -0.16479 | 60.3149 | 0.013733 | -0.050354 | -0.022888 | 0.10529 | 0.004577 | 0.1236 | -0.054932 | 0.17395 | -0.004578 | 0.36163 | 123.262 | 0.054931 | 123.1934 | 123.2254 | 123.0652 | 123.0469 | 123.0148 | -123.2162 | -123.0881 | 123.0835 | 123.143 | 60.054 | 60.1364
83.8594 | 123.2208 | -59.9991 | 63.0615 | -0.02594 | 0.0010745 | 0.063931 | 0.063732 | -0.00034607 | -0.00059807 | -0.0019162 | -0.042023 | 0.00163 | 0.068112 | 0.061115 | -0.0036872 | 0.0050436 | -0.0012113 | 0.059509 | 63.0524 | -60.1685 | 63.0478 | -59.8755 | -60.2234 | -0.013733 | 0.15564 | 63.0203 | -60.0357 | 63.0753 | -60.0403 | -60.1273 | -59.9213 | -0.16937 | -0.009155 | -0.013732 | 0.1236 | 59.9854 | -0.2243 | 60.1547 | -0.054932 | -0.036622 | -0.041198 | 0.013733 | -0.041199 | 0.077819 | -0.12817 | 0.11444 | -0.091552 | 0.29297 | 123.2162 | -0.004577 | 123.111 | 123.2208 | 123.056 | 123.0515 | 123.0194 | -123.23 | -123.0972 | 123.0469 | 123.0743 | 60.0586 | 60.1547
84.8906 | 123.3032 | -60.0082 | 63.0157 | -0.079346 | 0.0021427 | 0.064358 | 0.065441 | -0.00013247 | 0.00025633 | -0.004266 | -0.0023498 | 0.0035526 | 0.067044 | 0.056629 | -0.0039008 | 0.003121 | -0.0033475 | -0.041199 | 63.0386 | -60.2051 | 63.0157 | -59.8892 | -60.2463 | 0.018311 | -0.004578 | 62.9929 | -60.0723 | 63.1531 | -60.0128 | -60.0861 | -59.8801 | -0.19684 | 0.022888 | 0 | 0.11902 | 60.0266 | -0.23804 | 60.2234 | -0.041199 | -0.064087 | -0.022888 | 0.13733 | -0.004577 | 0.12817 | -0.07782 | 0.19226 | -0.013733 | 0.31586 | 123.2208 | 0.05951 | 123.2254 | 123.2437 | 123.0652 | 123.0469 | 123.0011 | -123.2208 | -123.0881 | 123.024 | 123.1613 | 59.967 | 60.0037
85.8594 | 123.3353 | -60.0311 | 63.0432 | -0.041199 | 0.00086086 | 0.063504 | 0.065655 | 0.0022173 | 0.0021789 | -0.0019162 | -0.014557 | 0.0012028 | 0.069393 | 0.066029 | -0.0034736 | 0.0044028 | -0.00078406 | -0.036621 | 63.0203 | -60.2097 | 63.0295 | -59.8801 | -60.2234 | 0.032043 | 0.022888 | 62.9791 | -60.0769 | 63.1348 | -60.0082 | -60.0677 | -59.8618 | -0.17853 | -0.022888 | -0.013733 | 0.15106 | 60.0632 | -0.19226 | 60.2417 | -0.013733 | -0.045776 | -0.064087 | 0.091553 | 0.022888 | 0.16937 | -0.036621 | 0.21515 | 0.009155 | 0.32959 | 123.2391 | 0.068664 | 123.2117 | 123.23 | 123.056 | 123.0515 | 123.0103 | -123.2529 | -123.1201 | 123.0606 | 123.1659 | 59.9945 | 60.054
86.9062 | 123.1979 | -60.0037 | 63.0524 | -0.041199 | 0.00086086 | 0.062008 | 0.065014 | 0.0030719 | -0.0025207 | 0.00022003 | -0.057281 | 0.0018436 | 0.068325 | 0.068806 | -0.0051824 | 0.0054708 | -0.0012113 | -0.004578 | 63.0661 | -60.2051 | 62.9745 | -59.9579 | -60.2875 | 0.041199 | 0.027466 | 63.0386 | -60.0677 | 63.0432 | -60.0769 | -60.1776 | -59.9762 | -0.20142 | 0.013733 | -0.07782 | 0.045776 | 60.0449 | -0.28381 | 60.2463 | -0.082398 | -0.064087 | -0.013733 | -0.009155 | -0.073242 | 0.027466 | -0.17395 | 0.091553 | -0.10986 | 0.24719 | 123.1796 | -0.009155 | 123.111 | 123.2712 | 123.1064 | 123.0698 | 123.0423 | -123.2574 | -123.1201 | 122.9782 | 123.0469 | 59.9991 | 60.0311
87.8594 | 123.3444 | -60.0128 | 63.0295 | -0.079346 | 0.0029971 | 0.065426 | 0.064159 | -0.00077327 | -0.0010255 | -0.002557 | -0.0023498 | -0.00029261 | 0.071957 | 0.065174 | -0.002619 | 0.0024802 | -0.0029203 | 0.009155 | 63.0341 | -60.2051 | 63.0524 | -59.8343 | -60.2005 | 0.082397 | 0.10986 | 62.9883 | -60.0403 | 63.1714 | -59.9579 | -60.0494 | -59.8572 | -0.19226 | 0.004578 | 0.022888 | 0.17853 | 60.0952 | -0.18768 | 60.2875 | 0.004578 | -0.027466 | -0.041199 | 0.14191 | 0.054931 | 0.15564 | -0.036621 | 0.18311 | -0.009155 | 0.37079 | 123.2574 | 0.082397 | 123.2117 | 123.2391 | 123.0286 | 123.0469 | 123.0011 | -123.2346 | -123.0698 | 123.0652 | 123.1842 | 60.022 | 60.1227
88.9062 | 123.2346 | -60.022 | 63.0798 | -0.01831 | 0.00043366 | 0.063931 | 0.065228 | -0.00077327 | -0.0010255 | -0.001489 | -0.07254 | 0.00163 | 0.067471 | 0.070515 | -0.002619 | 0.0046164 | -0.0052701 | -0.022888 | 63.0981 | -60.2142 | 62.9745 | -59.9442 | -60.2875 | 0.018311 | 0 | 63.0661 | -60.0952 | 63.0615 | -60.0769 | -60.1593 | -59.9533 | -0.19226 | 0.018311 | -0.10529 | 0.07782 | 60.0403 | -0.2655 | 60.2325 | -0.073243 | -0.073242 | -0.013733 | -0.018311 | -0.054931 | 0.068665 | -0.13733 | 0.14191 | -0.064087 | 0.27008 | 123.1888 | 0.018311 | 123.1567 | 123.3124 | 123.1613 | 123.1201 | 123.0881 | -123.2941 | -123.175 | 122.9965 | 123.0835 | 59.9991 | 60.022
89.8594 | 123.3398 | -60.0128 | 63.0295 | -0.041199 | -0.00063454 | 0.06329 | 0.064587 | 0.0026447 | -0.0046571 | -0.00020717 | 0.0098572 | 0.00077539 | 0.068325 | 0.065388 | -0.0053962 | 0.0054708 | -0.0029203 | 0 | 63.0295 | -60.1822 | 63.0386 | -59.8618 | -60.2188 | 0.07782 | 0.068665 | 62.9837 | -60.0723 | 63.1485 | -59.9762 | -60.0815 | -59.8801 | -0.16937 | 0 | 0.009155 | 0.15106 | 60.0906 | -0.20599 | 60.26 | -0.036621 | -0.05951 | -0.045776 | 0.11902 | 0.036621 | 0.13275 | -0.068665 | 0.19226 | -0.009155 | 0.32043 | 123.2208 | 0.096131 | 123.2208 | 123.2117 | 123.056 | 123.0423 | 122.9965 | -123.2117 | -123.1018 | 123.0515 | 123.1613 | 60.0128 | 60.0815
90.9062 | 123.2117 | -60.0266 | 63.0661 | -0.064087 | 0.0027835 | 0.062649 | 0.064587 | -0.0016279 | -0.0052979 | 0.0025698 | -0.032867 | 0.0022708 | 0.070461 | 0.067524 | -0.006037 | 0.0046164 | 0.00092494 | -0.004578 | 63.0386 | -60.2142 | 62.9837 | -59.9258 | -60.2829 | 0.054932 | 0.018311 | 63.0661 | -60.0906 | 63.0478 | -60.0586 | -60.1501 | -59.9808 | -0.18768 | -0.027466 | -0.082397 | 0.10071 | 60.0815 | -0.25635 | 60.2692 | -0.068665 | -0.064087 | 0 | -0.01831 | -0.032044 | 0.045776 | -0.1236 | 0.10986 | -0.059509 | 0.28839 | 123.1979 | 0.032043 | 123.1384 | 123.2529 | 123.1567 | 123.0652 | 123.0927 | -123.2803 | -123.1567 | 123.0103 | 123.0743 | 60.022 | 60.0449
91.8594 | 123.2986 | -60.0082 | 63.002 | -0.094604 | 0.0010745 | 0.061795 | 0.066723 | -0.00034607 | 4.273e-05 | 0.0015018 | 0.0098572 | 0.002698 | 0.069607 | 0.065602 | -0.0030462 | 0.0052572 | -0.0014249 | -0.036621 | 63.0341 | -60.1959 | 63.0295 | -59.8755 | -60.2325 | 0.054932 | 0.036621 | 62.9745 | -60.0494 | 63.1577 | -60.0128 | -60.0815 | -59.8755 | -0.18768 | 0.032044 | 0.027466 | 0.13275 | 60.0632 | -0.2243 | 60.2509 | -0.036621 | -0.041198 | -0.027466 | 0.15564 | -0.004577 | 0.13275 | -0.073242 | 0.17395 | -0.032044 | 0.32044 | 123.2254 | 0.036621 | 123.2071 | 123.23 | 123.024 | 123.0423 | 122.9828 | -123.1979 | -123.0515 | 123.0377 | 123.1659 | 59.9716 | 60.0449
92.9062 | 123.3032 | -60.0082 | 62.9929 | -0.10223 | 0.0015019 | 0.064358 | 0.0648 | 0.0032855 | -0.0025207 | 0.00022003 | -0.042023 | 0.0018436 | 0.069393 | 0.061329 | -0.0047552 | 0.0046164 | -0.00035666 | -0.036621 | 62.9745 | -60.2097 | 63.0569 | -59.8801 | -60.2463 | -0.013733 | -0.013733 | 62.9654 | -60.0677 | 63.121 | -60.0357 | -60.1135 | -59.8709 | -0.20142 | -0.018311 | 0.064087 | 0.12817 | 59.9945 | -0.23804 | 60.1959 | -0.036621 | -0.059509 | -0.027466 | 0.12817 | -0.027466 | 0.13733 | -0.10529 | 0.19684 | -0.045776 | 0.32959 | 123.2666 | 0.032043 | 123.1888 | 123.1842 | 123.0331 | 122.9828 | 122.9736 | -123.2025 | -123.0606 | 123.0652 | 123.1293 | 59.9716 | 59.9945
93.875 | 123.2437 | -60.0037 | 63.0569 | -0.048828 | 0.0021427 | 0.063717 | 0.06715 | -0.00034607 | -0.00081187 | 0.0015018 | -0.10611 | 0.0020572 | 0.068539 | 0.070301 | -0.0032598 | 0.0063254 | 0.0022067 | 0.004578 | 63.0569 | -60.2325 | 63.002 | -59.8984 | -60.2737 | 0.018311 | 0.045776 | 63.0203 | -60.0723 | 63.0936 | -60.0586 | -60.1547 | -59.9121 | -0.22888 | 0 | -0.054932 | 0.10529 | 60.022 | -0.27008 | 60.2509 | -0.041199 | -0.068665 | -0.036621 | 0.036621 | -0.054932 | 0.091553 | -0.15106 | 0.16022 | -0.082397 | 0.33417 | 123.2346 | 0.013733 | 123.1659 | 123.2895 | 123.0927 | 123.0606 | 123.024 | -123.2895 | -123.1293 | 123.0057 | 123.0972 | 60.0082 | 60.0494
94.8906 | 123.3582 | -59.9854 | 63.0203 | -0.094604 | 0.0040653 | 0.063076 | 0.063305 | -0.0052595 | -0.0040161 | -0.0027708 | 0.0068054 | 0.0014164 | 0.070461 | 0.062611 | -0.0028326 | 0.0050436 | 7.0538e-05 | -0.009155 | 63.0386 | -60.1822 | 63.0524 | -59.8709 | -60.2325 | 0.059509 | 0.086975 | 63.0066 | -60.0632 | 63.1714 | -59.9625 | -60.0677 | -59.8618 | -0.19684 | 0.01831 | 0.032043 | 0.11444 | 60.0449 | -0.24719 | 60.2417 | -0.050354 | -0.077819 | -0.013733 | 0.15106 | 0.022889 | 0.1236 | -0.082397 | 0.20142 | -0.004578 | 0.31128 | 123.2346 | 0.10071 | 123.2346 | 123.2208 | 123.0698 | 123.024 | 122.9919 | -123.2025 | -123.0835 | 123.0377 | 123.1567 | 59.9762 | 60.0723
95.8594 | 123.3536 | -59.9991 | 63.0112 | -0.086975 | 0.0015019 | 0.062222 | 0.065655 | -0.0044049 | -0.0033753 | -0.002557 | 0.0037536 | -0.00071981 | 0.06918 | 0.064961 | -0.002619 | 0.003121 | 0.00092494 | -0.013733 | 63.0478 | -60.1822 | 63.0478 | -59.8663 | -60.1776 | 0.07782 | 0.10986 | 62.9837 | -60.0723 | 63.1531 | -59.967 | -60.0403 | -59.8389 | -0.18311 | 0.036622 | 0.036622 | 0.13275 | 60.0769 | -0.17853 | 60.26 | 0.004578 | -0.073243 | -0.027465 | 0.14191 | 0.032043 | 0.16022 | -0.041199 | 0.23346 | 0.032044 | 0.31586 | 123.23 | 0.10529 | 123.2254 | 123.23 | 123.056 | 123.0469 | 122.9828 | -123.1934 | -123.0835 | 123.0469 | 123.1522 | 59.9854 | 60.1089
96.8906 | 123.23 | -60.0082 | 63.0753 | -0.071716 | 0.0012881 | 0.064145 | 0.063946 | 0.0030719 | -0.0025207 | 6.432e-06 | -0.032867 | 0.002698 | 0.068539 | 0.06432 | -0.0053962 | 0.0052572 | 0.00071134 | 0.054932 | 63.0341 | -60.1776 | 63.0661 | -59.8801 | -60.2005 | 0.11444 | -0.032043 | 62.9929 | -60.0815 | 63.089 | -60.0494 | -60.1273 | -59.8984 | -0.16937 | -0.041198 | -0.009155 | 0.12817 | 60.1227 | -0.19226 | 60.2921 | -0.022888 | -0.073242 | -0.082397 | 0.013733 | -0.041198 | 0.10986 | -0.11902 | 0.18311 | -0.045776 | 0.29755 | 123.2437 | 0.032044 | 123.1705 | 123.2117 | 123.0743 | 123.0423 | 123.0011 | -123.2529 | -123.1567 | 123.0743 | 123.0972 | 60.0632 | 59.9762
97.875 | 123.1888 | -60.054 | 63.0615 | -0.056457 | 0.0012881 | 0.06564 | 0.065868 | 0.0049945 | -0.0027345 | 0.00043363 | -0.10611 | 0.003339 | 0.067044 | 0.068379 | -0.0034736 | 0.0069662 | -0.0024931 | -0.032043 | 63.0295 | -60.2188 | 62.9883 | -59.9533 | -60.3012 | -0.050354 | -0.045776 | 63.0295 | -60.0677 | 63.0569 | -60.0906 | -60.2142 | -59.9442 | -0.1648 | -0.032043 | -0.073242 | 0.10071 | 60.0037 | -0.24719 | 60.1685 | -0.082397 | -0.013733 | -0.032043 | -0.004577 | -0.036621 | 0.10986 | -0.16022 | 0.1236 | -0.14648 | 0.2655 | 123.2071 | -0.022888 | 123.1247 | 123.2483 | 123.0972 | 123.0835 | 123.0835 | -123.2803 | -123.1293 | 123.0423 | 123.111 | 60.022 | 60.0082
98.9062 | 123.1705 | -60.0494 | 63.0203 | -0.048828 | 0.0017155 | 0.064785 | 0.066082 | 0.0024311 | -0.0012391 | -0.00084817 | -0.10306 | 0.0031254 | 0.070675 | 0.070728 | -0.0017646 | 0.0044028 | -0.00057046 | -0.10529 | 63.0432 | -60.26 | 62.9059 | -60.0403 | -60.4111 | -0.10529 | -0.16937 | 63.0066 | -60.1273 | 63.0249 | -60.1318 | -60.2509 | -59.9808 | -0.21057 | 0.022888 | -0.11444 | 0.009155 | 59.9442 | -0.36163 | 60.1547 | -0.15106 | -0.07782 | -0.013733 | 0.004577 | -0.082398 | 0.068664 | -0.20142 | 0.14648 | -0.1236 | 0.21973 | 123.1659 | -0.004578 | 123.1522 | 123.3032 | 123.1338 | 123.0927 | 123.056 | -123.2803 | -123.1476 | 122.9553 | 123.0743 | 59.9442 | 59.8801
99.8594 | 123.349 | -59.9991 | 63.0432 | -0.048828 | 0.0015019 | 0.061795 | 0.065014 | 0.00072213 | -0.0040161 | -0.00063437 | 0.034271 | 0.0014164 | 0.068112 | 0.068806 | -0.0039008 | 0.0050436 | -0.00035666 | 0.004578 | 62.9974 | -60.1913 | 63.0844 | -59.7839 | -60.173 | 0.09613 | 0.16022 | 62.9791 | -60.054 | 63.1851 | -59.9213 | -60.0128 | -59.8343 | -0.19226 | -0.045776 | 0.041199 | 0.21515 | 60.0952 | -0.17395 | 60.2875 | 0.01831 | -0.054932 | -0.064087 | 0.14191 | 0.077819 | 0.16479 | -0.013733 | 0.21973 | 0.041199 | 0.40741 | 123.2758 | 0.13275 | 123.2391 | 123.1888 | 123.0331 | 122.9965 | 122.9782 | -123.2346 | -123.0972 | 123.0835 | 123.1842 | 60.0037 | 60.1593
100.8906 | 123.2208 | -59.9991 | 63.0386 | -0.17853 | 0.0034245 | 0.06094 | 0.066509 | 0.0032855 | 0.00068353 | -0.00063437 | -0.026764 | 0.0041934 | 0.067471 | 0.063465 | -0.0066778 | 0.0058982 | -0.0035611 | 0.064087 | 63.0249 | -60.1959 | 62.9837 | -59.8846 | -60.2463 | 0.059509 | 0.027466 | 63.0341 | -60.0769 | 63.0798 | -60.0677 | -60.1501 | -59.9579 | -0.19684 | -0.013733 | -0.054931 | 0.11444 | 60.0586 | -0.24719 | 60.2554 | -0.050354 | -0.07782 | -0.004577 | 0.041199 | -0.068665 | 0.041198 | -0.15106 | 0.11902 | -0.073242 | 0.31128 | 123.1796 | 0.009155 | 123.1567 | 123.2208 | 123.111 | 123.024 | 123.0331 | -123.2346 | -123.1155 | 122.9828 | 123.0789 | 60.0632 | 60.0266
101.8594 | 123.2346 | -59.9808 | 63.0386 | -0.094604 | 0.0027835 | 0.061795 | 0.064587 | 0.0017901 | -0.00059807 | 0.00043363 | 0.0037536 | 0.0014164 | 0.070034 | 0.062611 | -0.0039008 | 0.00483 | -0.0016385 | 0.041199 | 63.0386 | -60.1547 | 63.0615 | -59.8526 | -60.1868 | 0.11902 | 0.11902 | 63.0249 | -60.0632 | 63.1256 | -60.0128 | -60.1044 | -59.9213 | -0.17395 | 0 | 0.022888 | 0.12817 | 60.0998 | -0.20599 | 60.2737 | -0.032044 | -0.082397 | -0.013733 | 0.086975 | -0.032043 | 0.059509 | -0.1236 | 0.14191 | -0.041199 | 0.30212 | 123.2162 | 0.050354 | 123.1888 | 123.1934 | 123.0881 | 123.0194 | 123.0057 | -123.1934 | -123.1018 | 123.0423 | 123.1064 | 60.022 | 60.0998
102.875 | 123.2162 | -60.0632 | 63.0341 | -0.064087 | 0.0010745 | 0.062436 | 0.067364 | 0.0043537 | -0.0023071 | 0.00022003 | -0.075592 | 0.003339 | 0.071102 | 0.06902 | -0.0058234 | 0.0056846 | -0.00035666 | -0.086975 | 63.0341 | -60.26 | 62.915 | -59.9945 | -60.3882 | -0.12817 | -0.16022 | 62.9974 | -60.0906 | 63.0478 | -60.1227 | -60.2325 | -59.9625 | -0.19684 | 0 | -0.11902 | 0.068664 | 59.935 | -0.32501 | 60.1318 | -0.12817 | -0.027466 | -0.036621 | 0.013733 | -0.05951 | 0.10071 | -0.16937 | 0.12817 | -0.14191 | 0.2655 | 123.175 | -0.032044 | 123.1384 | 123.2941 | 123.0881 | 123.0972 | 123.0606 | -123.2941 | -123.1247 | 122.9782 | 123.111 | 59.9762 | 59.903
103.9062 | 123.2437 | -60.0174 | 63.0707 | -0.010681 | 0.0010745 | 0.063931 | 0.06715 | 0.0039263 | -0.0016663 | 6.432e-06 | -0.05423 | 0.003339 | 0.068112 | 0.070301 | -0.0041144 | 0.0033346 | 0.0028475 | -0.013733 | 63.0798 | -60.2005 | 62.9745 | -59.9625 | -60.3012 | 0.036621 | -0.004578 | 63.0524 | -60.0769 | 63.0615 | -60.0861 | -60.1822 | -59.9533 | -0.1831 | 0.009155 | -0.096131 | 0.054932 | 60.054 | -0.28381 | 60.2371 | -0.10071 | -0.059509 | -0.018311 | -0.009156 | -0.068665 | 0.064087 | -0.16479 | 0.1236 | -0.10529 | 0.23804 | 123.175 | -0.009156 | 123.1384 | 123.2803 | 123.1293 | 123.0972 | 123.0698 | -123.2712 | -123.1476 | 122.9919 | 123.0789 | 60.0037 | 60.0128
104.8594 | 123.2895 | -59.9991 | 63.0341 | -0.048828 | 0.0019291 | 0.063504 | 0.065228 | 0.0026447 | -0.0020935 | 6.432e-06 | 0.00070198 | 0.00098899 | 0.067898 | 0.059834 | -0.0051824 | 0.0063254 | -0.00099766 | 0.036621 | 63.0341 | -60.1868 | 63.0844 | -59.8114 | -60.1685 | 0.10986 | 0.13275 | 62.9974 | -60.0632 | 63.1439 | -59.9808 | -60.0723 | -59.8572 | -0.18768 | 0 | 0.050354 | 0.18768 | 60.1089 | -0.16937 | 60.2966 | 0.018311 | -0.064087 | -0.036621 | 0.10986 | 0.01831 | 0.14191 | -0.073243 | 0.20599 | -0.009156 | 0.37537 | 123.2712 | 0.082397 | 123.2071 | 123.2208 | 123.0606 | 123.0331 | 122.9965 | -123.2208 | -123.0972 | 123.0835 | 123.143 | 60.0357 | 60.1318
105.8906 | 123.2803 | -60.0128 | 63.0203 | -0.056457 | -0.00020714 | 0.064358 | 0.065014 | 0.0024311 | -0.0010255 | -0.0010618 | 0.0068054 | 0.0018436 | 0.070461 | 0.06432 | -0.0032598 | 0.0052572 | -0.00078406 | -0.059509 | 63.0157 | -60.1776 | 62.9974 | -59.9304 | -60.2692 | -0.004578 | -0.050354 | 62.9791 | -60.0723 | 63.0798 | -60.0449 | -60.1364 | -59.903 | -0.1648 | -0.004578 | -0.022888 | 0.082397 | 60.0082 | -0.25635 | 60.173 | -0.091553 | -0.05951 | -0.041199 | 0.059509 | -0.032044 | 0.10986 | -0.1236 | 0.16937 | -0.064087 | 0.24719 | 123.175 | 0.027466 | 123.1522 | 123.1934 | 123.0515 | 123.0286 | 122.9919 | -123.1979 | -123.0927 | 123.0103 | 123.0927 | 59.9533 | 59.9625
106.875 | 123.1979 | -60.0403 | 63.0203 | -0.01831 | 0.0012881 | 0.064999 | 0.06715 | 0.0032855 | 0.00089713 | -0.00020717 | -0.10916 | 0.0014164 | 0.069393 | 0.067738 | -0.0045416 | 0.0054708 | -0.00057046 | -0.032043 | 63.0295 | -60.2325 | 62.9608 | -59.9442 | -60.3241 | -0.050354 | -0.041199 | 63.0112 | -60.0998 | 63.0524 | -60.1044 | -60.2234 | -59.9533 | -0.19226 | 0.009155 | -0.05951 | 0.09613 | 59.9899 | -0.28381 | 60.1822 | -0.091553 | -0.059509 | -0.009156 | 0.032043 | -0.064087 | 0.086975 | -0.18311 | 0.14648 | -0.1236 | 0.28839 | 123.1934 | -0.004578 | 123.1522 | 123.262 | 123.111 | 123.0698 | 123.0515 | -123.2529 | -123.1201 | 123.0011 | 123.0927 | 60.0082 | 59.9991
107.8906 | 123.2025 | -60.0266 | 63.0753 | -0.048828 | -0.00063454 | 0.061581 | 0.066509 | -0.0016279 | 0.0013245 | -0.00084817 | -0.023712 | 0.0020572 | 0.070034 | 0.061115 | -0.0045416 | 0.0046164 | 0.0032749 | 0.004578 | 63.0753 | -60.1959 | 62.9654 | -59.9075 | -60.2737 | 0.045776 | -0.004578 | 63.0432 | -60.0952 | 63.0478 | -60.0677 | -60.1593 | -59.9533 | -0.16937 | 0 | -0.10986 | 0.11902 | 60.0723 | -0.24719 | 60.2417 | -0.07782 | -0.068665 | -0.032043 | -0.027465 | -0.041199 | 0.073242 | -0.13275 | 0.14191 | -0.064087 | 0.28839 | 123.1613 | 0.027466 | 123.143 | 123.2712 | 123.1384 | 123.1018 | 123.0698 | -123.2712 | -123.1705 | 122.9919 | 123.0743 | 60.0311 | 60.022
108.875 | 123.2437 | -60.0082 | 63.0203 | -0.079346 | -0.00084814 | 0.064572 | 0.065014 | 0.0017901 | -0.00081187 | 0.00043363 | -0.090851 | 0.0035526 | 0.068539 | 0.065388 | -0.0036872 | 0.0033346 | -0.0035611 | -0.022888 | 63.0478 | -60.2463 | 62.97 | -59.935 | -60.3058 | -0.036621 | -0.032043 | 63.0112 | -60.0906 | 63.0569 | -60.1089 | -60.2142 | -59.9487 | -0.23804 | 0.027466 | -0.050354 | 0.073242 | 59.9716 | -0.29755 | 60.2097 | -0.059509 | -0.082397 | -0.009156 | 0.036621 | -0.10071 | 0.05951 | -0.20599 | 0.14191 | -0.1236 | 0.31128 | 123.2162 | -0.018311 | 123.1476 | 123.2941 | 123.1018 | 123.056 | 123.0194 | -123.2666 | -123.111 | 122.9782 | 123.0652 | 59.9854 | 59.9762
109.8906 | 123.3582 | -59.9899 | 63.0249 | -0.10223 | 0.0010745 | 0.06329 | 0.063732 | -0.00055967 | -0.0010255 | -0.0027708 | 0.025116 | 0.0041934 | 0.06918 | 0.064747 | -0.0028326 | 0.0039756 | 0.00028414 | 0.013733 | 63.0341 | -60.1868 | 63.0661 | -59.8434 | -60.1868 | 0.09613 | 0.11902 | 62.97 | -60.0449 | 63.1714 | -59.935 | -60.0311 | -59.8389 | -0.19684 | 0.009156 | 0.041199 | 0.14648 | 60.0861 | -0.19684 | 60.2829 | 0 | -0.054932 | -0.054931 | 0.14649 | 0.054931 | 0.15106 | -0.041199 | 0.20599 | 0.013733 | 0.34332 | 123.2529 | 0.10986 | 123.2162 | 123.2208 | 123.0148 | 123.024 | 122.9599 | -123.2117 | -123.0698 | 123.056 | 123.1613 | 60.0037 | 60.1089
110.8594 | 123.2117 | -60.0266 | 63.1027 | -0.064087 | 0.0027835 | 0.062008 | 0.065655 | -0.00077327 | -0.0040161 | 0.0015018 | -0.051178 | 0.0024844 | 0.071102 | 0.063252 | -0.0030462 | 0.003762 | -0.0037747 | -0.013733 | 63.089 | -60.2097 | 62.9654 | -59.9396 | -60.2829 | 0.059509 | 0.004578 | 63.0478 | -60.0723 | 63.0615 | -60.0586 | -60.1685 | -59.9625 | -0.18311 | -0.013733 | -0.13733 | 0.086975 | 60.0861 | -0.25635 | 60.2692 | -0.073242 | -0.045777 | -0.054931 | -0.041199 | -0.032044 | 0.064087 | -0.14191 | 0.10986 | -0.09613 | 0.27008 | 123.175 | 0.013733 | 123.1338 | 123.2986 | 123.1201 | 123.1155 | 123.0743 | -123.3124 | -123.175 | 122.9919 | 123.0881 | 60.0128 | 60.0311
111.9062 | 123.2117 | -60.0494 | 63.0341 | -0.041199 | 0.0012881 | 0.063931 | 0.066509 | 0.0017901 | -0.00059807 | 0.00086083 | -0.090851 | 0.00163 | 0.068966 | 0.068165 | -0.0036872 | 0.0056846 | -0.0020657 | -0.059509 | 63.0386 | -60.2417 | 62.97 | -59.9808 | -60.3333 | -0.054932 | -0.073242 | 63.0203 | -60.0861 | 63.0341 | -60.1135 | -60.2325 | -59.967 | -0.19226 | 0.004577 | -0.064087 | 0.068664 | 59.9945 | -0.28381 | 60.1868 | -0.091553 | -0.036622 | -0.013733 | 0 | -0.064087 | 0.082397 | -0.18311 | 0.11902 | -0.14648 | 0.26093 | 123.2117 | -0.027465 | 123.1201 | 123.2803 | 123.1064 | 123.0881 | 123.0698 | -123.2758 | -123.1201 | 123.0194 | 123.0835 | 59.9899 | 59.9762
112.8594 | 123.1934 | -60.0266 | 63.0661 | -0.02594 | -0.00042094 | 0.062008 | 0.064159 | 0.00093573 | -0.0020935 | -0.0023434 | -0.026764 | 0.0035526 | 0.068966 | 0.067524 | -0.0028326 | 0.0061118 | -0.0020657 | 0 | 63.0798 | -60.1959 | 62.9562 | -59.935 | -60.2829 | 0.041199 | 0.004578 | 63.0295 | -60.0815 | 63.0341 | -60.0769 | -60.173 | -59.9487 | -0.16937 | 0.013733 | -0.10986 | 0.091552 | 60.0677 | -0.25635 | 60.2371 | -0.086975 | -0.054932 | -0.036621 | -0.032043 | -0.050354 | 0.07782 | -0.14648 | 0.13275 | -0.091553 | 0.26093 | 123.1522 | 0.004578 | 123.1155 | 123.2758 | 123.111 | 123.1064 | 123.056 | -123.262 | -123.1476 | 122.9828 | 123.0606 | 60.0266 | 60.0311
113.8906 | 123.2849 | -60.0311 | 62.9883 | -0.10223 | 0.0027835 | 0.062649 | 0.064159 | 0.0024311 | -0.00081187 | 0.0012882 | -0.023712 | 0.00034819 | 0.067257 | 0.063252 | -0.002619 | 0.0078208 | -0.00057046 | -0.068665 | 63.0112 | -60.1913 | 62.9929 | -59.8938 | -60.0677 | -0.022888 | -0.041199 | 62.9791 | -60.0998 | 63.1027 | -60.0494 | -60.1456 | -59.8984 | -0.16022 | 0.022888 | 0.004578 | 0.13733 | 60.0082 | -0.036621 | 60.1685 | 0.1236 | -0.068664 | -0.009155 | 0.11444 | -0.01831 | 0.13275 | -0.11444 | 0.20142 | -0.045777 | 0.29755 | 123.1842 | 0.050354 | 123.2025 | 123.2025 | 123.0789 | 123.0423 | 123.0103 | -123.1796 | -123.0881 | 123.024 | 123.1338 | 59.9625 | 59.9899
114.875 | 123.2117 | -60.0769 | 63.0203 | -0.12512 | 0.0025699 | 0.06329 | 0.066082 | -0.00077327 | 0.0015381 | 0.0023562 | -0.10306 | 0.0018436 | 0.071102 | 0.066242 | -0.0024054 | 0.0044028 | 0.00028414 | -0.10071 | 63.0386 | -60.2737 | 62.9242 | -60.022 | -60.379 | -0.10529 | -0.1831 | 63.0112 | -60.1273 | 63.0249 | -60.1685 | -60.26 | -59.9808 | -0.19684 | 0.01831 | -0.096131 | 0.054931 | 59.9716 | -0.30212 | 60.1685 | -0.10528 | -0.050354 | -0.009156 | 0.004577 | -0.091553 | 0.09613 | -0.18311 | 0.14648 | -0.13275 | 0.25177 | 123.1979 | -0.041199 | 123.1522 | 123.3124 | 123.1384 | 123.1155 | 123.0881 | -123.2941 | -123.1476 | 123.0011 | 123.1018 | 59.9762 | 59.8938
115.8906 | 123.3353 | -60.0128 | 63.0066 | -0.033569 | 0.0010745 | 0.063504 | 0.0648 | 0.0041399 | 0.0017517 | -0.0027708 | 0.025116 | 0.0018436 | 0.071102 | 0.061115 | -0.0041144 | 0.0022666 | 0.0011385 | 0.022888 | 63.0432 | -60.1456 | 63.0753 | -59.8068 | -60.1639 | 0.11444 | 0.13275 | 62.9791 | -60.0449 | 63.1668 | -59.9579 | -60.0403 | -59.8251 | -0.13275 | 0.036621 | 0.068664 | 0.20599 | 60.1273 | -0.15106 | 60.26 | -0.01831 | -0.032044 | -0.027466 | 0.16022 | 0.054931 | 0.18768 | -0.027466 | 0.21973 | 0.004578 | 0.33875 | 123.2208 | 0.086975 | 123.2117 | 123.1888 | 123.024 | 123.056 | 122.9919 | -123.1522 | -123.0515 | 123.0881 | 123.1796 | 60.0357 | 60.1456
116.8594 | 123.2208 | -60.0494 | 63.0844 | -0.0030519 | -0.00020714 | 0.062222 | 0.066509 | 0.0037127 | -0.0014527 | 0.0010746 | -0.069489 | 0.0020572 | 0.069607 | 0.065174 | -0.0032598 | 0.0033346 | -0.00057046 | -0.022888 | 63.089 | -60.2188 | 62.97 | -59.9625 | -60.2829 | 0.013733 | -0.004578 | 63.0661 | -60.0586 | 63.0478 | -60.0677 | -60.173 | -59.9442 | -0.16937 | 0.004577 | -0.11444 | 0.086975 | 60.0632 | -0.23346 | 60.2325 | -0.064087 | -0.009156 | -0.018311 | -0.036621 | -0.018311 | 0.10529 | -0.1236 | 0.11444 | -0.11444 | 0.25635 | 123.1888 | -0.009155 | 123.1064 | 123.3078 | 123.1247 | 123.1384 | 123.1155 | -123.3032 | -123.143 | 123.0194 | 123.0972 | 60.0266 | 60.0449
117.9062 | 123.2529 | -60.0174 | 63.0661 | -0.01831 | 0.00086086 | 0.063717 | 0.065441 | 0.00072213 | -0.0012391 | -0.0012754 | -0.035919 | 0.0035526 | 0.068325 | 0.068806 | -0.0051824 | 0.0063254 | -0.0027067 | 0 | 63.0844 | -60.2188 | 62.9837 | -59.9442 | -60.2829 | 0.032043 | -0.10986 | 63.0112 | -60.0952 | 63.1027 | -60.0357 | -60.1593 | -59.903 | -0.20142 | 0.018311 | -0.082397 | 0.073242 | 60.0494 | -0.2655 | 60.2509 | -0.064087 | -0.07782 | -0.054932 | 0.036621 | -0.018311 | 0.11444 | -0.14191 | 0.19226 | -0.064087 | 0.27466 | 123.2025 | 0.059509 | 123.1979 | 123.3032 | 123.1064 | 123.1018 | 123.0286 | -123.2849 | -123.1613 | 123.0011 | 123.1201 | 60.0174 | 59.9075
118.8594 | 123.2162 | -60.0311 | 63.0569 | -0.079346 | 0.0017155 | 0.062863 | 0.063091 | 8.1126e-05 | 0.00068353 | 0.0025698 | 0.00070198 | 0.0020572 | 0.068539 | 0.066029 | -0.0021918 | 0.0035482 | 0.00092494 | 0.036621 | 63.0432 | -60.1913 | 63.0157 | -59.9487 | -60.347 | 0.13275 | 0.068665 | 63.0432 | -60.0403 | 63.0707 | -60.0586 | -60.1364 | -59.9121 | -0.16022 | -0.013733 | -0.041199 | 0.082398 | 60.1639 | -0.31586 | 60.3241 | -0.15564 | -0.009155 | -0.013733 | 0.013733 | -0.027466 | 0.11902 | -0.10529 | 0.12817 | -0.096131 | 0.24262 | 123.2071 | -0.018311 | 123.111 | 123.2346 | 123.0835 | 123.0743 | 123.0743 | -123.2483 | -123.0972 | 123.0469 | 123.1018 | 60.0677 | 60.0998
119.8906 | 123.1934 | -60.0311 | 63.0798 | 0.0045776 | 0.00064726 | 0.062863 | 0.066296 | 0.0024311 | -0.0027345 | 0.001929 | -0.05423 | 0.0020572 | 0.068112 | 0.068165 | -0.0047552 | 0.0044028 | 0.0015659 | -0.018311 | 63.0798 | -60.1776 | 62.9654 | -59.9716 | -60.2783 | 0.018311 | -0.004578 | 63.0341 | -60.0769 | 63.0386 | -60.0769 | -60.1868 | -59.935 | -0.14648 | 0 | -0.11444 | 0.059509 | 60.0494 | -0.24719 | 60.1959 | -0.10071 | -0.045776 | -0.045776 | -0.041199 | -0.045776 | 0.09613 | -0.15564 | 0.14191 | -0.10986 | 0.20599 | 123.143 | 0 | 123.1155 | 123.2574 | 123.111 | 123.111 | 123.0652 | -123.2574 | -123.1567 | 122.9965 | 123.0698 | 60.0128 | 60.0266
120.875 | 123.1842 | -60.0632 | 63.0386 | -0.041199 | 0.00043366 | 0.063076 | 0.066937 | 0.00050853 | 4.273e-05 | -0.0036252 | -0.057281 | 0.0039798 | 0.067684 | 0.066883 | -0.0041144 | 0.0041892 | 0.0015659 | -0.064087 | 63.0478 | -60.2234 | 62.915 | -60.0174 | -60.3745 | -0.11902 | -0.17395 | 63.0203 | -60.1227 | 63.002 | -60.1685 | -60.2509 | -59.9899 | -0.16022 | 0.009156 | -0.1236 | 0.045776 | 59.9442 | -0.31128 | 60.1044 | -0.15106 | -0.05951 | -0.01831 | -0.036621 | -0.10529 | 0.073242 | -0.18768 | 0.13275 | -0.12817 | 0.20599 | 123.1384 | -0.045776 | 123.1247 | 123.2712 | 123.143 | 123.111 | 123.0835 | -123.262 | -123.1613 | 122.9782 | 123.0652 | 59.9991 | 59.8892
121.8906 | 123.2941 | -60.0174 | 63.0157 | -0.064087 | 0.0025699 | 0.063504 | 0.063091 | -0.0026959 | 4.273e-05 | -0.00020717 | 0.040375 | 0.0029116 | 0.068753 | 0.061543 | -0.0030462 | 0.0056846 | -0.0018521 | -0.059509 | 63.0066 | -60.2051 | 62.9791 | -59.9167 | -60.2646 | -0.013733 | -0.064087 | 63.002 | -60.0769 | 63.1073 | -60.0174 | -60.1227 | -59.8801 | -0.18768 | -0.009155 | -0.036621 | 0.10071 | 60.0037 | -0.24719 | 60.1913 | -0.059509 | -0.059509 | -0.013733 | 0.091553 | 0 | 0.13733 | -0.10529 | 0.19684 | -0.045777 | 0.28839 | 123.1842 | 0.059509 | 123.1842 | 123.2117 | 123.0789 | 123.024 | 123.0194 | -123.2208 | -123.0927 | 122.9965 | 123.1247 | 59.9579 | 59.9533
122.8594 | 123.2666 | -60.0311 | 63.0432 | 0.012207 | 0.0021427 | 0.062863 | 0.066082 | 0.0020037 | -0.00038447 | 0.0015018 | -0.05423 | 0.0022708 | 0.072384 | 0.070728 | -0.0058234 | 0.0039756 | -0.00035666 | -0.013733 | 63.0661 | -60.2097 | 62.9745 | -59.9579 | -60.2966 | 0.022888 | -0.009155 | 63.0524 | -60.0769 | 63.0798 | -60.0632 | -60.1593 | -59.9396 | -0.17853 | 0.022888 | -0.068665 | 0.073242 | 60.054 | -0.2655 | 60.2325 | -0.086975 | -0.045776 | 0.009155 | 0.036621 | -0.032043 | 0.091553 | -0.12817 | 0.13733 | -0.082398 | 0.25177 | 123.1842 | 0.013733 | 123.1567 | 123.2758 | 123.1293 | 123.0972 | 123.0835 | -123.2529 | -123.1201 | 123.0057 | 123.111 | 60.0174 | 60.022
123.8906 | 123.2391 | -60.0403 | 63.0524 | -0.01831 | 0.00064726 | 0.063931 | 0.068005 | -0.0020551 | -0.0018799 | -0.00084817 | -0.066437 | 0.0024844 | 0.068325 | 0.070942 | -0.0045416 | 0.00483 | -0.00014306 | -0.004578 | 63.0615 | -60.2325 | 62.9425 | -59.935 | -60.2051 | 0.045776 | 0.022888 | 63.0386 | -60.0815 | 63.0936 | -60.0586 | -60.1593 | -59.9121 | -0.19226 | 0.009155 | -0.10986 | 0.10529 | 60.0861 | -0.16479 | 60.2783 | 0.027466 | -0.041199 | -0.013733 | 0.041199 | -0.018311 | 0.12817 | -0.11902 | 0.16937 | -0.07782 | 0.29755 | 123.175 | 0.022888 | 123.175 | 123.2941 | 123.1201 | 123.1018 | 123.0789 | -123.2849 | -123.1338 | 122.9828 | 123.1338 | 60.0357 | 60.0632
124.8594 | 123.2391 | -60.0357 | 63.0432 | -0.033569 | -0.00020714 | 0.066281 | 0.065655 | 0.0039263 | -0.0012391 | 0.00022003 | -0.029816 | 0.00077539 | 0.068753 | 0.062824 | -0.0032598 | 0.0054708 | -0.0018521 | 0.036621 | 63.0844 | -60.1868 | 62.9974 | -59.8984 | -60.2692 | 0.032043 | 0.018311 | 63.0249 | -60.0586 | 63.0844 | -60.0449 | -60.1501 | -59.9213 | -0.15106 | 0.041199 | -0.045776 | 0.13733 | 60.0677 | -0.23346 | 60.2188 | -0.082397 | -0.022888 | -0.018311 | 0.041199 | -0.009155 | 0.11444 | -0.11444 | 0.13733 | -0.091552 | 0.28839 | 123.1842 | 0.013733 | 123.143 | 123.2712 | 123.0835 | 123.1201 | 123.0606 | -123.23 | -123.1018 | 123.0331 | 123.1201 | 60.0723 | 60.054
125.8906 | 123.1842 | -60.0403 | 63.0707 | -0.056457 | 0.00022006 | 0.063717 | 0.066509 | -0.0033369 | 0.00089713 | 0.00043363 | -0.0023498 | 0.004407 | 0.070034 | 0.061115 | -0.0045416 | 0.003762 | -0.00078406 | -0.041199 | 63.0707 | -60.2005 | 62.9654 | -59.935 | -60.2783 | 0.032043 | 0.004578 | 63.0432 | -60.0723 | 63.0432 | -60.0815 | -60.1868 | -59.9625 | -0.16022 | 0 | -0.10529 | 0.10529 | 60.0723 | -0.23804 | 60.2325 | -0.07782 | -0.032044 | -0.027466 | -0.027466 | -0.041199 | 0.07782 | -0.14648 | 0.10986 | -0.11444 | 0.2655 | 123.1659 | -0.009155 | 123.1155 | 123.2712 | 123.1155 | 123.111 | 123.0835 | -123.2712 | -123.143 | 123.0057 | 123.0835 | 59.9991 | 60.0449
126.875 | 123.3032 | -59.9991 | 62.9654 | -0.14801 | 0.0040653 | 0.063931 | 0.064159 | 0.00050853 | -0.00059807 | -0.00063437 | -0.051178 | -0.00071981 | 0.068753 | 0.069874 | -0.0047552 | 0.0058982 | 0.00028414 | -0.041199 | 63.0066 | -60.2188 | 63.0249 | -59.8801 | -60.2646 | -0.036621 | -0.041199 | 62.9425 | -60.0952 | 63.1256 | -60.0174 | -60.1089 | -59.8618 | -0.21973 | 0.041199 | 0.059509 | 0.11902 | 59.9625 | -0.2655 | 60.1822 | -0.045776 | -0.096131 | -0.022888 | 0.16022 | -0.018311 | 0.13733 | -0.10986 | 0.23346 | -0.013733 | 0.33875 | 123.2437 | 0.07782 | 123.2208 | 123.2254 | 123.0377 | 123.0057 | 122.9416 | -123.1842 | -123.0606 | 123.024 | 123.1247 | 59.9579 | 59.9579
127.8906 | 123.317 | -59.9808 | 63.0478 | -0.079346 | 0.0025699 | 0.064145 | 0.065228 | -0.0052595 | -0.0010255 | -0.00042077 | 0.012909 | -0.0013608 | 0.065548 | 0.060688 | -0.0049688 | 0.0046164 | -0.00099766 | 0.022888 | 63.0524 | -60.1547 | 63.0753 | -59.8022 | -60.1685 | 0.11902 | 0.10071 | 63.0112 | -60.0586 | 63.1439 | -59.9625 | -60.0403 | -59.8434 | -0.17395 | 0.004577 | 0.027465 | 0.17853 | 60.0998 | -0.18768 | 60.2737 | -0.013733 | -0.07782 | -0.036622 | 0.09613 | 0.018311 | 0.13733 | -0.059509 | 0.21515 | 0.018311 | 0.35248 | 123.23 | 0.096131 | 123.2025 | 123.2071 | 123.0698 | 123.0331 | 122.9919 | -123.2025 | -123.1064 | 123.056 | 123.1247 | 60.0037 | 60.0815
128.8594 | 123.2437 | -60.022 | 63.0295 | -0.033569 | 0.0021427 | 0.062649 | 0.067577 | 0.0034991 | 0.0011109 | 0.00086083 | -0.042023 | 0.003339 | 0.068966 | 0.067097 | -0.0047552 | 0.0041892 | -0.0014249 | -0.059509 | 63.0478 | -60.2234 | 63.0066 | -59.9075 | -60.26 | 0.036621 | 0.027466 | 63.0295 | -60.0632 | 63.0707 | -60.0632 | -60.1318 | -59.9213 | -0.20142 | 0.018311 | -0.022888 | 0.11444 | 60.0586 | -0.23804 | 60.26 | -0.036621 | -0.041198 | 0 | 0.041199 | -0.041198 | 0.10071 | -0.10986 | 0.14191 | -0.068665 | 0.31586 | 123.23 | 0 | 123.1338 | 123.2712 | 123.0927 | 123.0698 | 123.0515 | -123.2529 | -123.0927 | 123.0286 | 123.0927 | 59.9625 | 60.0494
129.9062 | 123.1979 | -60.0494 | 63.0203 | -0.02594 | 0.00064726 | 0.064145 | 0.068859 | 0.0030719 | -0.00081187 | -0.0012754 | -0.063385 | 0.0020572 | 0.070248 | 0.063252 | -0.0024054 | 0.0050436 | -0.0024931 | -0.11444 | 63.0615 | -60.2417 | 62.8784 | -60.0266 | -60.3745 | -0.10529 | -0.1831 | 63.0112 | -60.1227 | 63.0112 | -60.1685 | -60.2371 | -59.9762 | -0.19226 | 0.041198 | -0.14191 | 0.022888 | 59.9442 | -0.32501 | 60.1364 | -0.13275 | -0.073243 | -0.009156 | -0.009156 | -0.11902 | 0.073242 | -0.18768 | 0.14648 | -0.11444 | 0.21515 | 123.1201 | -0.045776 | 123.1338 | 123.3032 | 123.1338 | 123.111 | 123.0606 | -123.262 | -123.143 | 122.9279 | 123.0606 | 59.935 | 59.8663
130.8594 | 123.2574 | -60.0357 | 63.0386 | -0.033569 | 0.00022006 | 0.062863 | 0.066082 | -0.0012005 | -0.00038447 | -0.003198 | -0.02066 | 0.0022708 | 0.067471 | 0.071583 | -0.0036872 | 0.0061118 | -0.00099766 | -0.004578 | 63.0615 | -60.2142 | 63.0798 | -59.8755 | -60.3104 | 0.036621 | 0.027466 | 63.0295 | -60.054 | 63.0936 | -60.0403 | -60.1547 | -59.903 | -0.17853 | 0.022888 | 0.041199 | 0.16022 | 60.0723 | -0.27466 | 60.2509 | -0.096131 | -0.01831 | -0.009155 | 0.054932 | -0.004577 | 0.13275 | -0.11902 | 0.15106 | -0.10071 | 0.33875 | 123.2941 | 0.013733 | 123.1476 | 123.2758 | 123.0835 | 123.0972 | 123.0652 | -123.2529 | -123.0927 | 123.1155 | 123.1293 | 60.0311 | 60.0632
131.8906 | 123.2712 | -60.0037 | 63.0844 | -0.01831 | 0.00086086 | 0.063076 | 0.063946 | 0.0034991 | -0.0020935 | 0.0010746 | -0.023712 | 0.0022708 | 0.07153 | 0.066242 | -0.002619 | 0.0061118 | 7.0538e-05 | -0.027466 | 63.0707 | -60.2325 | 62.97 | -59.9487 | -60.2692 | 0.018311 | -0.027466 | 63.0432 | -60.054 | 63.0341 | -59.9396 | -60.1501 | -59.9533 | -0.22888 | -0.013733 | -0.11444 | 0.054932 | 60.022 | -0.2655 | 60.2509 | -0.036621 | -0.050354 | -0.041199 | -0.050354 | 0.064087 | 0.050354 | -0.14648 | 0.10071 | -0.09613 | 0.28381 | 123.2025 | 0.11444 | 123.0881 | 123.3032 | 123.0972 | 123.0743 | 123.0469 | -123.317 | -123.1384 | 122.9736 | 123.0377 | 59.9762 | 59.9762
132.875 | 123.317 | -59.9945 | 63.0066 | -0.056457 | 0.0027835 | 0.065426 | 0.065014 | 0.0045673 | 0.00025633 | -0.00084817 | -0.032867 | 0.0012028 | 0.068325 | 0.067097 | -0.0013372 | 0.0046164 | 0.0019931 | -0.16022 | 63.0203 | -60.2188 | 62.9929 | -59.9075 | -60.2875 | -0.064087 | -0.10529 | 62.9517 | -60.0906 | 63.1119 | -60.0311 | -60.1318 | -59.8801 | -0.2243 | 0.013733 | -0.013733 | 0.086975 | 59.9304 | -0.29297 | 60.1547 | -0.068665 | -0.09613 | -0.054932 | 0.10529 | -0.036621 | 0.11444 | -0.13733 | 0.21057 | -0.041199 | 0.31128 | 123.2117 | 0.059509 | 123.2025 | 123.2391 | 123.0423 | 123.0148 | 122.9462 | -123.2254 | -123.0972 | 122.9874 | 123.1064 | 59.8343 | 59.8892
133.9062 | 123.2071 | -60.0403 | 63.0844 | -0.048828 | 0.0012881 | 0.06564 | 0.065655 | 0.0043537 | -0.0016663 | -0.0017026 | -0.066437 | 0.0014164 | 0.069393 | 0.065174 | -0.0049688 | 0.0067526 | -0.00078406 | -0.045776 | 63.0524 | -60.2325 | 62.9654 | -59.9487 | -60.3195 | -0.059509 | -0.07782 | 63.0249 | -60.1181 | 63.0478 | -60.1135 | -60.2188 | -59.967 | -0.19226 | -0.032044 | -0.11902 | 0.091553 | 59.9808 | -0.27924 | 60.173 | -0.086975 | -0.07782 | -0.05951 | -0.036621 | -0.073242 | 0.073242 | -0.17853 | 0.15106 | -0.10071 | 0.28381 | 123.1979 | 0.004578 | 123.1659 | 123.2849 | 123.143 | 123.0927 | 123.0652 | -123.317 | -123.2025 | 123.0057 | 123.0881 | 59.9945 | 59.9625
134.8594 | 123.2254 | -60.0449 | 63.0386 | -0.041199 | 0.0010745 | 0.063931 | 0.066937 | 0.0032855 | 0.0032471 | 0.0010746 | -0.063385 | 0.0020572 | 0.070248 | 0.067097 | -0.0049688 | 0.0056846 | -0.00099766 | -0.10986 | 63.0386 | -60.2371 | 62.9059 | -60.0266 | -60.3836 | -0.13733 | -0.21515 | 63.0066 | -60.1273 | 63.0249 | -60.1501 | -60.2509 | -59.9808 | -0.19226 | 0 | -0.13275 | 0.018311 | 59.9075 | -0.33875 | 60.0998 | -0.14648 | -0.082397 | -0.032043 | -0.013733 | -0.10529 | 0.064087 | -0.20599 | 0.14648 | -0.1236 | 0.21057 | 123.143 | -0.022888 | 123.1522 | 123.2758 | 123.1338 | 123.0835 | 123.0515 | -123.2758 | -123.1659 | 122.9507 | 123.0698 | 59.935 | 59.8297
135.8906 | 123.2712 | -60.0266 | 63.0615 | 0.012207 | 0.0021427 | 0.062222 | 0.065441 | 0.0013629 | 0.00025633 | -0.0027708 | -0.0054016 | 0.0031254 | 0.068539 | 0.068806 | -0.004328 | 0.006539 | -0.0022793 | -0.032043 | 63.0569 | -60.1959 | 62.9791 | -60.022 | -60.434 | 0.050354 | -0.027466 | 63.0432 | -60.0632 | 63.0707 | -60.0403 | -60.1227 | -59.9121 | -0.16937 | -0.004577 | -0.082397 | 0.004577 | 60.0769 | -0.40741 | 60.2463 | -0.23804 | -0.036621 | -0.01831 | 0.009156 | -0.013733 | 0.11444 | -0.096131 | 0.15106 | -0.05951 | 0.17395 | 123.175 | 0.022888 | 123.1338 | 123.2529 | 123.1064 | 123.0835 | 123.0698 | -123.2574 | -123.1247 | 123.0057 | 123.0972 | 59.9945 | 59.9991
136.8594 | 123.2574 | -60.0174 | 63.0569 | -0.033569 | 0.0015019 | 0.062863 | 0.06715 | 0.0032855 | -0.0033753 | -0.0017026 | -0.035919 | 0.0014164 | 0.069393 | 0.062397 | -0.0041144 | 0.0069662 | 0.0022067 | -0.032043 | 63.1027 | -60.1913 | 63.0798 | -59.8984 | -60.2875 | 0.045776 | 0.004578 | 63.0524 | -60.0861 | 63.089 | -60.0357 | -60.1593 | -59.9121 | -0.17395 | 0.045776 | 0.022888 | 0.11902 | 60.0632 | -0.27008 | 60.2371 | -0.096131 | -0.068665 | -0.004578 | 0.032043 | -0.018311 | 0.10529 | -0.14191 | 0.17395 | -0.073242 | 0.29297 | 123.2712 | 0.050354 | 123.175 | 123.2941 | 123.1384 | 123.1201 | 123.0698 | -123.2483 | -123.143 | 123.0972 | 123.1064 | 59.9854 | 60.022
137.8906 | 123.3032 | -59.9991 | 63.0203 | -0.094604 | 0.0029971 | 0.063717 | 0.065655 | -0.00013247 | -0.0010255 | 6.432e-06 | 0.046478 | 0.0018436 | 0.068112 | 0.066242 | -0.0045416 | 0.00483 | 0.0041293 | -0.059509 | 63.0203 | -60.1822 | 62.9791 | -59.8801 | -60.2325 | 0.004578 | -0.068665 | 62.9883 | -60.0677 | 63.1073 | -60.0037 | -60.0815 | -59.8618 | -0.18311 | 0 | -0.041199 | 0.11902 | 60.0037 | -0.23346 | 60.1868 | -0.050354 | -0.068665 | -0.032044 | 0.086975 | -0.004578 | 0.13733 | -0.082398 | 0.20599 | -0.013733 | 0.30212 | 123.1613 | 0.064087 | 123.175 | 123.2025 | 123.056 | 123.0194 | 122.9874 | -123.2025 | -123.0881 | 122.9782 | 123.1064 | 59.9396 | 59.9304
138.875 | 123.23 | -60.0494 | 63.0295 | -0.064087 | 0.0012881 | 0.060513 | 0.066296 | 0.00050853 | -0.00038447 | -0.0017026 | -0.05423 | 0.0020572 | 0.069393 | 0.074574 | -0.0073188 | 0.0029074 | 7.0538e-05 | -0.13275 | 63.0295 | -60.2325 | 62.9196 | -60.0174 | -60.4019 | -0.13733 | -0.20599 | 62.9883 | -60.0998 | 63.0295 | -60.1318 | -60.2234 | -59.9396 | -0.18311 | 0 | -0.10986 | 0.032043 | 59.9121 | -0.35248 | 60.0952 | -0.16937 | -0.050354 | -0.041199 | 0 | -0.082398 | 0.10986 | -0.17395 | 0.16022 | -0.1236 | 0.21515 | 123.1522 | -0.032044 | 123.1293 | 123.262 | 123.0881 | 123.0789 | 123.0377 | -123.262 | -123.1293 | 122.9691 | 123.0789 | 59.9167 | 59.8434
139.8906 | 123.2574 | -60.0266 | 63.0341 | -0.056457 | 0.0021427 | 0.064358 | 0.065228 | 0.0034991 | -0.0031617 | -0.00084817 | -0.045074 | 0.0039798 | 0.068325 | 0.064961 | -0.0068914 | 0.0054708 | -0.0046293 | -0.018311 | 63.0707 | -60.1959 | 62.9929 | -59.903 | -60.2646 | 0.004578 | -0.013733 | 63.0341 | -60.0632 | 63.0936 | -60.0632 | -60.141 | -59.9075 | -0.16937 | 0.036621 | -0.041199 | 0.1236 | 60.0311 | -0.23804 | 60.2005 | -0.068664 | -0.036621 | 0 | 0.059509 | -0.036621 | 0.11902 | -0.11444 | 0.15564 | -0.07782 | 0.29297 | 123.1888 | 0 | 123.1567 | 123.2666 | 123.0972 | 123.0972 | 123.0606 | -123.23 | -123.0972 | 123.0194 | 123.1201 | 60.0082 | 60.0128
140.8594 | 123.2529 | -60.0266 | 63.0661 | -0.02594 | 0.0010745 | 0.063717 | 0.066296 | -0.0041913 | -0.0033753 | 0.0012882 | -0.032867 | 0.00056179 | 0.068966 | 0.060047 | -0.0039008 | 0.00483 | 0.0034885 | -0.045776 | 63.089 | -60.2005 | 62.9242 | -59.9533 | -60.1822 | 0.013733 | -0.041199 | 63.0341 | -60.0769 | 63.0569 | -60.0677 | -60.1685 | -59.9304 | -0.17395 | 0.022888 | -0.14191 | 0.073242 | 60.0403 | -0.15564 | 60.2142 | 0.01831 | -0.050354 | -0.032043 | -0.009155 | -0.041199 | 0.09613 | -0.14191 | 0.14648 | -0.091553 | 0.24719 | 123.1247 | 0.009155 | 123.1338 | 123.2895 | 123.111 | 123.1155 | 123.0606 | -123.2666 | -123.143 | 122.9507 | 123.0835 | 59.9808 | 59.9854
141.9062 | 123.1934 | -60.0311 | 63.0569 | -0.086975 | 0.0012881 | 0.063504 | 0.066937 | 0.0020037 | -0.0029481 | 0.0023562 | -0.060333 | 0.0037662 | 0.068325 | 0.069447 | -0.0051824 | 0.0054708 | 0.00028414 | -0.082397 | 63.0615 | -60.2234 | 62.9379 | -59.9396 | -60.3378 | -0.082397 | -0.15106 | 63.0249 | -60.0861 | 63.0295 | -60.1135 | -60.2142 | -59.9762 | -0.19226 | 0.004577 | -0.11902 | 0.091553 | 59.9487 | -0.3067 | 60.141 | -0.11444 | -0.054932 | -0.032044 | -0.027466 | -0.082397 | 0.054932 | -0.1831 | 0.10986 | -0.12817 | 0.28381 | 123.1613 | -0.027465 | 123.1155 | 123.2849 | 123.111 | 123.0927 | 123.056 | -123.2803 | -123.143 | 122.9691 | 123.0606 | 59.9487 | 59.8801
142.8594 | 123.2117 | -60.0174 | 63.0341 | -0.01831 | 0.0038517 | 0.063504 | 0.063091 | -0.0012005 | -0.0018799 | 0.0021426 | -0.035919 | 0.0020572 | 0.070889 | 0.060688 | -0.0041144 | 0.0056846 | 0.0026339 | -0.018311 | 63.0844 | -60.2051 | 62.9929 | -59.8984 | -60.2646 | -0.018311 | -0.041199 | 63.002 | -60.0403 | 63.0981 | -60.0449 | -60.1593 | -59.903 | -0.18768 | 0.050354 | -0.041199 | 0.11902 | 59.9991 | -0.24719 | 60.1868 | -0.059509 | -0.022888 | -0.032044 | 0.064087 | -0.027466 | 0.11444 | -0.14191 | 0.13733 | -0.11902 | 0.3067 | 123.1979 | -0.004578 | 123.1384 | 123.2895 | 123.0423 | 123.1018 | 123.0194 | -123.2391 | -123.0743 | 123.0103 | 123.1155 | 59.9991 | 59.9762
143.8906 | 123.3261 | -59.9945 | 63.0341 | -0.056457 | 0.0021427 | 0.063931 | 0.0648 | 0.0015765 | -0.0012391 | -0.0036252 | 0.070892 | -0.00050621 | 0.06918 | 0.05962 | -0.0053962 | 0.0024802 | 0.0030611 | 0.018311 | 63.0478 | -60.1593 | 63.1027 | -59.7748 | -60.228 | 0.10529 | 0.036621 | 63.0249 | -60.054 | 63.1393 | -59.9716 | -60.0449 | -59.8389 | -0.16479 | 0.013733 | 0.068664 | 0.21973 | 60.0998 | -0.23346 | 60.2646 | -0.068664 | -0.059509 | -0.009156 | 0.10528 | 0.022888 | 0.15564 | -0.050354 | 0.21515 | 0.009155 | 0.38452 | 123.262 | 0.082397 | 123.1934 | 123.2071 | 123.0789 | 123.0423 | 123.0194 | -123.1934 | -123.0881 | 123.0972 | 123.1338 | 60.0128 | 60.0311
144.8594 | 123.2346 | -60.022 | 63.0524 | -0.056457 | 0.0027835 | 0.064572 | 0.066082 | 0.0045673 | 0.00025633 | 0.00022003 | -0.069489 | 0.0035526 | 0.066616 | 0.063679 | -0.0068914 | 0.0050436 | -0.00035666 | -0.068665 | 63.0524 | -60.2188 | 62.9562 | -59.9487 | -60.3012 | -0.086975 | -0.14191 | 63.0112 | -60.0906 | 63.0386 | -60.1044 | -60.2005 | -59.9533 | -0.19684 | 0 | -0.09613 | 0.073243 | 59.935 | -0.27923 | 60.1318 | -0.082397 | -0.068664 | -0.041199 | -0.013733 | -0.082397 | 0.068665 | -0.17853 | 0.13733 | -0.10986 | 0.27008 | 123.175 | -0.013733 | 123.1293 | 123.2712 | 123.1018 | 123.0743 | 123.0331 | -123.2712 | -123.143 | 122.9782 | 123.0606 | 59.9533 | 59.8801
145.8906 | 123.2437 | -60.022 | 63.0386 | -0.033569 | 0.0017155 | 0.06564 | 0.064587 | -0.00055967 | -0.00017087 | -0.001489 | 0.040375 | 0.0022708 | 0.068325 | 0.05962 | -0.0019782 | 0.0067526 | -0.00035666 | 0.009155 | 63.0707 | -60.1547 | 63.0478 | -59.8389 | -60.1822 | 0.064087 | 0.013733 | 63.0203 | -60.0311 | 63.0981 | -60.0174 | -60.0861 | -59.8755 | -0.13275 | 0.032044 | 0.009156 | 0.18311 | 60.0861 | -0.16022 | 60.2188 | -0.027466 | -0.009155 | -0.01831 | 0.05951 | 0.004578 | 0.14649 | -0.064087 | 0.15564 | -0.054932 | 0.31586 | 123.2025 | 0.013733 | 123.1293 | 123.2254 | 123.0515 | 123.0927 | 123.0423 | -123.1934 | -123.0698 | 123.0698 | 123.1201 | 60.0311 | 60.0357
146.8594 | 123.2117 | -60.0174 | 63.0753 | -0.0030519 | 0.0027835 | 0.062008 | 0.065655 | -0.00077327 | -0.0020935 | -0.0027708 | -0.0054016 | 0.0035526 | 0.070675 | 0.067097 | -0.0030462 | 0.0056846 | 0.0034885 | 0.064087 | 63.089 | -60.2188 | 62.9745 | -59.8618 | -60.3607 | -0.032043 | -0.10986 | 63.0661 | -60.0586 | 63.0478 | -60.0769 | -60.1685 | -59.9213 | -0.20142 | 0.013733 | -0.10071 | 0.15564 | 59.9854 | -0.34332 | 60.1868 | -0.14191 | -0.041199 | -0.009155 | -0.027465 | -0.059509 | 0.09613 | -0.15106 | 0.13733 | -0.10986 | 0.35706 | 123.1934 | -0.01831 | 123.1064 | 123.3078 | 123.1247 | 123.1064 | 123.0835 | -123.2941 | -123.1338 | 122.9919 | 123.0652 | 60.0815 | 59.9075
147.9062 | 123.1934 | -60.0449 | 63.0524 | -0.064087 | 0.0025699 | 0.066494 | 0.066937 | 0.0013629 | 0.00089713 | -0.0036252 | -0.075592 | 0.0012028 | 0.069393 | 0.068806 | -0.002619 | 0.0056846 | -0.00057046 | -0.1236 | 63.0295 | -60.2371 | 62.915 | -60.0357 | -60.3836 | -0.16937 | -0.25635 | 63.0066 | -60.1135 | 63.0203 | -60.1456 | -60.2554 | -59.9716 | -0.19226 | -0.022888 | -0.13733 | 0.009155 | 59.8755 | -0.33875 | 60.0677 | -0.14648 | -0.068664 | -0.045776 | -0.032043 | -0.10071 | 0.073242 | -0.21057 | 0.14191 | -0.14191 | 0.20142 | 123.1522 | -0.032044 | 123.1338 | 123.2666 | 123.1201 | 123.0743 | 123.0515 | -123.2895 | -123.1659 | 122.9599 | 123.0652 | 59.9213 | 59.7885
148.8594 | 123.2346 | -60.0082 | 63.0341 | -0.048828 | 0.00043366 | 0.062863 | 0.068859 | 0.0028583 | -0.0035889 | -0.00020717 | -0.057281 | 0.003339 | 0.06918 | 0.063252 | -0.006037 | 0.0054708 | -0.0024931 | -0.050354 | 63.0478 | -60.2142 | 63.0798 | -59.9121 | -60.228 | -0.036621 | -0.091553 | 63.0386 | -60.054 | 63.0844 | -60.0586 | -60.1685 | -59.9167 | -0.20599 | 0.013733 | 0.045776 | 0.096131 | 59.9716 | -0.21973 | 60.1776 | -0.013733 | -0.045776 | 0.004577 | 0.050354 | -0.050354 | 0.091553 | -0.16022 | 0.13733 | -0.11444 | 0.30212 | 123.2941 | -0.004578 | 123.1384 | 123.262 | 123.0927 | 123.056 | 123.0469 | -123.2483 | -123.0881 | 123.0881 | 123.0927 | 59.9579 | 59.9167
149.8906 | 123.1842 | -60.0128 | 63.1073 | -0.0030519 | 0.0023563 | 0.06329 | 0.066723 | 0.0020037 | -0.0029481 | 0.00022003 | -0.0023498 | 0.0031254 | 0.068753 | 0.066242 | -0.0030462 | 0.0041892 | 0.0013521 | -0.07782 | 63.0936 | -60.1776 | 62.9654 | -59.9258 | -60.2737 | 0 | -0.068665 | 63.0569 | -60.0494 | 63.0386 | -60.0677 | -60.1868 | -59.9304 | -0.1648 | -0.013733 | -0.14191 | 0.086975 | 60.0128 | -0.26093 | 60.1776 | -0.096131 | -0.036621 | -0.050354 | -0.068665 | -0.054932 | 0.082397 | -0.17395 | 0.11902 | -0.13733 | 0.25177 | 123.143 | -0.018311 | 123.0881 | 123.2712 | 123.1064 | 123.1064 | 123.0698 | -123.2849 | -123.1567 | 122.9782 | 123.0515 | 59.935 | 59.9442
150.875 | 123.2574 | -60.0082 | 63.0066 | -0.064087 | 0.0019291 | 0.062863 | 0.066296 | -0.0026959 | 0.00068353 | -0.00063437 | -0.032867 | 0.0024844 | 0.070461 | 0.061756 | -0.0045416 | 0.00483 | -0.0016385 | -0.14191 | 63.0615 | -60.2371 | 62.9379 | -59.9487 | -60.3424 | -0.14648 | -0.23804 | 63.0249 | -60.0861 | 63.0798 | -60.0677 | -60.1685 | -59.9121 | -0.22888 | 0.054931 | -0.068665 | 0.05951 | 59.8618 | -0.33417 | 60.0906 | -0.10529 | -0.07782 | 0.01831 | 0.073242 | -0.059509 | 0.096131 | -0.16022 | 0.17395 | -0.082397 | 0.28839 | 123.175 | 0.018311 | 123.1659 | 123.2986 | 123.111 | 123.0698 | 123.0331 | -123.2437 | -123.0927 | 122.9462 | 123.0881 | 59.8663 | 59.7702
151.8906 | 123.3353 | -59.9625 | 63.0295 | -0.11749 | -0.00063454 | 0.06329 | 0.064373 | -0.0016279 | -0.0012391 | -0.0036252 | 0.043427 | -0.00050621 | 0.070034 | 0.062824 | -0.0039008 | 0.0044028 | 0.00071134 | -0.050354 | 63.0569 | -60.1364 | 63.0386 | -59.8068 | -60.1776 | 0.032043 | -0.004578 | 63.0203 | -60.0357 | 63.1714 | -59.9213 | -60.0082 | -59.8068 | -0.17395 | 0.027466 | 0.009155 | 0.15564 | 59.9945 | -0.21515 | 60.1685 | -0.041198 | -0.073243 | -0.009155 | 0.14191 | 0.041198 | 0.15564 | -0.045777 | 0.22888 | 0.027466 | 0.32959 | 123.175 | 0.11444 | 123.2071 | 123.1934 | 123.056 | 123.0194 | 122.9828 | -123.1659 | -123.0652 | 123.0011 | 123.1338 | 59.9121 | 59.9579
152.8594 | 123.2437 | -60.0128 | 63.0753 | -0.048828 | 0.0032107 | 0.062008 | 0.065868 | 0.00050853 | -0.00059807 | 0.00022003 | -0.05423 | 0.0022708 | 0.068753 | 0.068806 | -0.0056098 | 0.0052572 | -0.00035666 | -0.064087 | 63.0798 | -60.2051 | 63.0249 | -59.8984 | -60.2509 | -0.050354 | -0.082397 | 63.0386 | -60.0723 | 63.1027 | -60.0357 | -60.1547 | -59.8892 | -0.19226 | 0.004578 | -0.050354 | 0.11444 | 59.9625 | -0.23804 | 60.1547 | -0.045776 | -0.05951 | -0.036621 | 0.027466 | -0.022889 | 0.1236 | -0.14191 | 0.18311 | -0.082397 | 0.3067 | 123.23 | 0.036621 | 123.175 | 123.2849 | 123.111 | 123.0927 | 123.0515 | -123.2803 | -123.1476 | 123.0377 | 123.1155 | 59.9487 | 59.9304
153.8906 | 123.1979 | -60.0082 | 63.1027 | -0.033569 | -0.0010617 | 0.060299 | 0.064159 | 0.0017901 | -0.0018799 | 0.00022003 | -0.026764 | 0.002698 | 0.068325 | 0.060047 | -0.0045416 | 0.0061118 | -0.00057046 | -0.10529 | 63.1027 | -60.1639 | 62.9837 | -59.9213 | -60.2692 | -0.050354 | -0.15564 | 63.0753 | -60.054 | 63.0386 | -60.0632 | -60.1685 | -59.9167 | -0.15564 | 0 | -0.11902 | 0.086975 | 59.9579 | -0.26093 | 60.1135 | -0.10529 | -0.045776 | -0.027466 | -0.064087 | -0.054931 | 0.091553 | -0.16022 | 0.13733 | -0.11444 | 0.24261 | 123.1476 | -0.009155 | 123.0927 | 123.2666 | 123.1293 | 123.111 | 123.0835 | -123.2666 | -123.1567 | 122.9919 | 123.0469 | 59.903 | 59.8526
154.8594 | 123.2437 | -59.9991 | 63.1027 | -0.44556 | 0.0036381 | 0.060513 | 0.0648 | 0.0013629 | -0.0033753 | 0.00043363 | -0.038971 | 0.0031254 | 0.068753 | 0.062184 | -0.0034736 | 0.0029074 | 7.0538e-05 | 0.13275 | 63.0844 | -60.1685 | 62.9517 | -59.8892 | -60.2692 | -0.073242 | -0.17853 | 63.0661 | -60.0632 | 63.0707 | -60.0357 | -60.1364 | -59.903 | -0.16937 | -0.01831 | -0.15106 | 0.10986 | 59.9258 | -0.27008 | 60.0952 | -0.10071 | -0.064087 | -0.036621 | -0.032043 | -0.036622 | 0.09613 | -0.13733 | 0.16022 | -0.073243 | 0.27924 | 123.1201 | 0.027465 | 123.1338 | 123.2529 | 123.1293 | 123.0835 | 123.0652 | -123.2712 | -123.1659 | 122.9507 | 123.0698 | 60.1318 | 59.8206
155.8594 | 123.2437 | -60.022 | 63.121 | -0.094604 | 0.0025699 | 0.063931 | 0.065655 | 0.0022173 | 0.0026061 | -0.0019162 | 0.015961 | 0.0024844 | 0.071102 | 0.064533 | -0.0034736 | 0.0044028 | -0.00035666 | -0.054932 | 63.0569 | -60.1593 | 63.0432 | -59.8572 | -60.2234 | -0.018311 | -0.1236 | 63.0569 | -60.0082 | 63.0707 | -60.0403 | -60.1089 | -59.9167 | -0.13733 | -0.064087 | -0.07782 | 0.1648 | 60.0037 | -0.20142 | 60.141 | -0.064087 | 0.013733 | -0.064087 | -0.050354 | -0.01831 | 0.10529 | -0.086975 | 0.091553 | -0.10071 | 0.30212 | 123.2025 | -0.032043 | 123.0789 | 123.2162 | 123.0652 | 123.0789 | 123.0789 | -123.2803 | -123.1293 | 123.0652 | 123.0927 | 59.967 | 59.8984
156.9062 | 123.3398 | -59.9808 | 63.0203 | -0.086975 | 0.0019291 | 0.064145 | 0.065228 | 0.0026447 | 0.0011109 | 0.001929 | -0.014557 | 0.0020572 | 0.069821 | 0.073078 | -0.0062506 | 0.0069662 | 0.00071134 | -0.15106 | 63.0066 | -60.1868 | 63.0386 | -59.8526 | -60.2188 | -0.15106 | -0.25177 | 62.9929 | -60.0586 | 63.1485 | -59.9762 | -60.0861 | -59.8434 | -0.20599 | -0.013733 | 0.01831 | 0.12817 | 59.8297 | -0.23804 | 60.0357 | -0.032043 | -0.07782 | -0.027466 | 0.12817 | 0.004578 | 0.13733 | -0.10529 | 0.21515 | -0.027466 | 0.33417 | 123.2254 | 0.082398 | 123.2071 | 123.1934 | 123.0515 | 122.9874 | 122.9736 | -123.2071 | -123.0789 | 123.0194 | 123.1293 | 59.8297 | 59.729
157.8594 | 123.1979 | -59.9945 | 63.089 | 0.035095 | 0.0012881 | 0.063931 | 0.068432 | -0.0048321 | -0.0012391 | 0.00022003 | -0.05423 | 0.0022708 | 0.068966 | 0.065174 | -0.0047552 | 0.0050436 | 0.0011385 | -0.15564 | 63.1073 | -60.1547 | 62.9791 | -59.9167 | -60.2692 | -0.10986 | -0.2655 | 63.0661 | -60.054 | 63.0798 | -60.0494 | -60.1456 | -59.8984 | -0.16022 | 0.018311 | -0.10986 | 0.07782 | 59.8846 | -0.27466 | 60.0449 | -0.11444 | -0.059509 | -0.022888 | -0.009155 | -0.054931 | 0.096131 | -0.15106 | 0.15564 | -0.091553 | 0.23804 | 123.1338 | 0.004578 | 123.1338 | 123.262 | 123.1201 | 123.1018 | 123.0606 | -123.2437 | -123.143 | 122.9736 | 123.0743 | 59.8389 | 59.729
158.9062 | 123.2986 | -59.9854 | 63.0249 | -0.079346 | 0.0010745 | 0.064145 | 0.065655 | 0.0058489 | -0.00081187 | 0.00043363 | -0.014557 | 0.0012028 | 0.06918 | 0.067311 | -0.004328 | 0.0058982 | -0.0022793 | -0.27008 | 63.0478 | -60.1959 | 63.0112 | -59.9899 | -60.434 | -0.20142 | -0.4303 | 63.0112 | -60.0677 | 63.1119 | -60.0128 | -60.1273 | -59.8618 | -0.21057 | 0.022889 | -0.013733 | -0.004577 | 59.7839 | -0.44861 | 59.9945 | -0.23804 | -0.082397 | -0.013733 | 0.086975 | -0.027465 | 0.1236 | -0.14191 | 0.20599 | -0.059509 | 0.20599 | 123.2071 | 0.054932 | 123.1796 | 123.2437 | 123.0789 | 123.0331 | 122.9965 | -123.2208 | -123.0927 | 122.9965 | 123.0972 | 59.7153 | 59.5551
159.8594 | 123.3307 | -59.9442 | 63.0569 | -0.033569 | 6.46e-06 | 0.064145 | 0.063946 | 8.1126e-05 | -0.0014527 | -0.00042077 | 0.028168 | 0.0031254 | 0.068539 | 0.063465 | -0.0032598 | 0.0050436 | -0.0035611 | -0.12817 | 63.0478 | -60.1501 | 63.1027 | -59.7656 | -60.1318 | -0.059509 | -0.1831 | 63.0066 | -59.9991 | 63.1714 | -59.8984 | -60.022 | -59.7977 | -0.20599 | -0.009155 | 0.045776 | 0.17853 | 59.8846 | -0.18768 | 60.0906 | 0.01831 | -0.054931 | -0.050354 | 0.11444 | 0.045777 | 0.14648 | -0.07782 | 0.20142 | -0.022889 | 0.38452 | 123.2529 | 0.10071 | 123.1705 | 123.1979 | 123.0057 | 122.9919 | 122.9507 | -123.2071 | -123.056 | 123.0469 | 123.1155 | 59.816 | 59.761
160.8906 | 123.3353 | -59.9487 | 63.0615 | -0.056457 | 0.0010745 | 0.062649 | 0.06715 | 0.00072213 | -0.0023071 | -0.0023434 | 0.022064 | 0.00098899 | 0.067257 | 0.066029 | -0.0058234 | 0.0035482 | 0.00028414 | -0.20142 | 63.0753 | -60.1273 | 63.1027 | -59.7656 | -60.1501 | -0.10529 | -0.22888 | 63.0295 | -60.0037 | 63.1989 | -59.903 | -59.9945 | -59.7977 | -0.17853 | 0.013733 | 0.041199 | 0.1831 | 59.8434 | -0.20142 | 60.022 | -0.022888 | -0.054932 | -0.032043 | 0.13733 | 0.045776 | 0.15106 | -0.045777 | 0.20599 | 0.009155 | 0.36163 | 123.23 | 0.10071 | 123.2025 | 123.2025 | 123.0331 | 123.024 | 122.9782 | -123.1888 | -123.0652 | 123.0515 | 123.1476 | 59.7473 | 59.7198
161.8594 | 123.2071 | -59.9808 | 63.1119 | -0.086975 | -0.00084814 | 0.062222 | 0.066296 | -0.00055967 | -0.0027345 | -0.001489 | -0.035919 | 0.0035526 | 0.070461 | 0.066456 | -0.0036872 | 0.0046164 | -0.00035666 | -0.29297 | 63.1577 | -60.1639 | 63.002 | -59.8984 | -60.2463 | -0.2243 | -0.39825 | 63.0798 | -60.0494 | 63.089 | -60.022 | -60.141 | -59.9167 | -0.18311 | 0.045777 | -0.10986 | 0.082398 | 59.7565 | -0.2655 | 59.9396 | -0.082398 | -0.068664 | -0.032043 | -0.022888 | -0.041199 | 0.064087 | -0.16022 | 0.13275 | -0.091553 | 0.2655 | 123.1659 | 0.027465 | 123.1384 | 123.3215 | 123.1293 | 123.1384 | 123.0606 | -123.2758 | -123.1613 | 122.9828 | 123.0698 | 59.6878 | 59.5825
162.8906 | 123.2162 | -59.9762 | 63.1439 | -0.01831 | 0.00043366 | 0.063504 | 0.065014 | -0.00034607 | -0.0035889 | -0.00084817 | -0.032867 | 0.00163 | 0.068112 | 0.065602 | -0.0047552 | 0.0033346 | -0.0012113 | -0.32501 | 63.121 | -60.173 | 63.0112 | -59.9121 | -60.2463 | -0.2655 | -0.47607 | 63.1027 | -60.0357 | 63.089 | -60.0357 | -60.1318 | -59.8938 | -0.19684 | -0.022888 | -0.13275 | 0.064087 | 59.7107 | -0.27008 | 59.9075 | -0.073242 | -0.05951 | -0.041199 | -0.054932 | -0.05951 | 0.082397 | -0.15564 | 0.14191 | -0.09613 | 0.26093 | 123.1842 | 0 | 123.1247 | 123.2941 | 123.1384 | 123.0972 | 123.0789 | -123.317 | -123.1796 | 122.9874 | 123.0652 | 59.6512 | 59.5001
163.8594 | 123.1979 | -59.9716 | 63.1073 | -0.071716 | 0.00043366 | 0.063931 | 0.068218 | 0.0017901 | -0.0012391 | -0.0023434 | -0.045074 | 0.00077539 | 0.068966 | 0.062184 | -0.004328 | 0.0050436 | 7.0538e-05 | -0.37994 | 63.1393 | -60.1776 | 63.0203 | -59.9121 | -60.2371 | -0.31128 | -0.54016 | 63.1027 | -60.0266 | 63.0936 | -60.0128 | -60.1181 | -59.8892 | -0.20599 | 0.032043 | -0.086975 | 0.05951 | 59.6603 | -0.2655 | 59.8663 | -0.05951 | -0.054931 | -0.004578 | -0.013733 | -0.041198 | 0.082398 | -0.14648 | 0.13733 | -0.091553 | 0.2655 | 123.1979 | 0.013733 | 123.1201 | 123.317 | 123.1293 | 123.111 | 123.0743 | -123.2849 | -123.1338 | 122.9919 | 123.0652 | 59.5917 | 59.4315
164.8594 | 123.2117 | -60.0037 | 63.1073 | -0.064087 | 0.0032107 | 0.064572 | 0.065228 | 0.00050853 | -0.0023071 | -0.0012754 | -0.075592 | 0.0024844 | 0.067471 | 0.06902 | -0.0047552 | 0.0035482 | -0.00078406 | -0.4303 | 63.1027 | -60.1639 | 63.0432 | -59.8526 | -60.2188 | -0.40283 | -0.62714 | 63.0798 | -60.0494 | 63.1165 | -60.0311 | -60.1318 | -59.8846 | -0.16022 | -0.004578 | -0.064087 | 0.15106 | 59.6008 | -0.21515 | 59.761 | -0.054932 | -0.045776 | -0.027466 | 0.009155 | -0.027466 | 0.11902 | -0.12817 | 0.16479 | -0.082398 | 0.31128 | 123.2071 | 0.01831 | 123.1659 | 123.2666 | 123.1293 | 123.1064 | 123.0835 | -123.2712 | -123.1567 | 123.0469 | 123.1201 | 59.5734 | 59.3765
165.8906 | 123.2758 | -59.9396 | 63.0569 | -0.13275 | 0.0029971 | 0.062863 | 0.063091 | 0.00093573 | -0.00038447 | 0.00064723 | -0.0054016 | 0.0012028 | 0.06918 | 0.059193 | -0.004328 | 0.0052572 | -0.0014249 | -0.55847 | 63.0661 | -60.141 | 63.0341 | -59.8526 | -60.2371 | -0.50812 | -0.79193 | 63.0249 | -60.0266 | 63.1348 | -59.9808 | -60.0815 | -59.8526 | -0.20142 | 0.009155 | -0.022888 | 0.086975 | 59.4315 | -0.29755 | 59.6329 | -0.096131 | -0.086975 | -0.032044 | 0.07782 | -0.041199 | 0.086975 | -0.14191 | 0.17395 | -0.054932 | 0.28839 | 123.175 | 0.045776 | 123.1613 | 123.2071 | 123.0515 | 123.0057 | 122.9645 | -123.1979 | -123.0835 | 122.9736 | 123.0743 | 59.3811 | 59.1476
166.8594 | 123.2346 | -59.9625 | 63.1256 | -0.041199 | 0.0023563 | 0.06329 | 0.066509 | 0.00050853 | -0.0029481 | -0.00020717 | -0.060333 | 0.0024844 | 0.068539 | 0.06197 | -0.006037 | 0.0035482 | 0.0019931 | -0.56305 | 63.121 | -60.1547 | 63.0615 | -59.8526 | -60.2188 | -0.53101 | -0.78735 | 63.1073 | -60.0037 | 63.121 | -59.9854 | -60.0998 | -59.8572 | -0.19226 | -0.004577 | -0.064087 | 0.10986 | 59.4315 | -0.25635 | 59.6237 | -0.064087 | -0.041199 | -0.01831 | -0.004577 | -0.022889 | 0.10529 | -0.13733 | 0.14648 | -0.09613 | 0.30212 | 123.2162 | 0.01831 | 123.1247 | 123.2758 | 123.111 | 123.0835 | 123.0698 | -123.2803 | -123.1293 | 123.024 | 123.0835 | 59.3994 | 59.1751
167.8906 | 123.349 | -59.9121 | 63.1027 | -0.11749 | 0.0019291 | 0.062649 | 0.065868 | 8.1126e-05 | -0.0027345 | 0.00064723 | 0.019012 | 0.00077539 | 0.068753 | 0.065174 | -0.0047552 | 0.0041892 | -0.00057046 | -0.77362 | 63.0753 | -60.1456 | 63.0753 | -59.7336 | -60.1135 | -0.44861 | -0.78735 | 63.0707 | -59.9991 | 63.2172 | -59.8618 | -59.9167 | -59.7427 | -0.23346 | -0.027466 | -0.027466 | 0.17853 | 59.4635 | -0.20142 | 59.697 | 0.032044 | -0.086975 | -0.032043 | 0.11444 | 0.050354 | 0.16937 | -0.004578 | 0.25635 | 0.082397 | 0.41199 | 123.2208 | 0.13733 | 123.2162 | 123.2208 | 123.0698 | 122.9874 | 122.9828 | -123.2483 | -123.1018 | 122.9874 | 123.1293 | 59.1385 | 59.1248
168.8594 | 123.2483 | -59.935 | 63.1302 | -0.086975 | 0.0015019 | 0.062222 | 0.067364 | 0.0020037 | 0.00025633 | 0.0010746 | -0.032867 | 0.0020572 | 0.069821 | 0.071156 | -0.0056098 | 0.0067526 | -0.0044157 | -0.60883 | 63.1668 | -60.1501 | 63.0569 | -59.6924 | -60.7086 | -0.65002 | -1.1398 | 63.1165 | -60.0037 | 63.1668 | -59.9258 | -60.0723 | -59.848 | -0.21515 | 0.036621 | -0.073242 | 0.24262 | 59.285 | -0.77362 | 59.5001 | -0.55847 | -0.068664 | -0.013733 | 0.036621 | 0.009156 | 0.086976 | -0.13733 | 0.15564 | -0.068665 | 0.45776 | 123.2071 | 0.07782 | 123.1705 | 123.317 | 123.1201 | 123.1018 | 123.0515 | -123.2803 | -123.1338 | 122.9919 | 123.1018 | 59.3262 | 58.7952
169.8906 | 123.262 | -59.9121 | 63.1073 | -0.02594 | 0.0010745 | 0.062008 | 0.0648 | 0.00029473 | -0.0046571 | -0.0017026 | 0.012909 | 0.0024844 | 0.070461 | 0.065815 | -0.0032598 | 0.0054708 | -0.00078406 | -0.65918 | 63.1119 | -60.0906 | 63.1393 | -59.7153 | -60.0769 | -0.59509 | -1.03 | 63.0798 | -59.9808 | 63.2172 | -59.8938 | -59.9945 | -59.7748 | -0.17853 | 0.004577 | 0.032043 | 0.19684 | 59.317 | -0.16479 | 59.4955 | 0.013733 | -0.068665 | -0.027466 | 0.10986 | 0.01831 | 0.13733 | -0.082398 | 0.20599 | -0.013733 | 0.37537 | 123.23 | 0.086975 | 123.1979 | 123.2025 | 123.0606 | 123.024 | 122.9919 | -123.1979 | -123.0881 | 123.0515 | 123.1293 | 59.2529 | 58.8821
170.8594 | 123.2574 | -59.935 | 63.1439 | -0.10223 | 0.0017155 | 0.063504 | 0.066296 | 0.0022173 | -0.0012391 | 0.00086083 | -0.060333 | 0.002698 | 0.068966 | 0.064747 | -0.0051824 | 0.0050436 | -0.00057046 | -0.75531 | 63.1622 | -60.1273 | 63.089 | -59.8114 | -60.1822 | -0.75531 | -1.2543 | 63.1256 | -60.0082 | 63.176 | -59.9442 | -60.0769 | -59.816 | -0.19226 | 0.01831 | -0.054932 | 0.1236 | 59.1797 | -0.24719 | 59.3719 | -0.054932 | -0.073242 | -0.018311 | 0.032043 | -0.009155 | 0.11902 | -0.14191 | 0.19226 | -0.068664 | 0.31586 | 123.2162 | 0.064087 | 123.1842 | 123.2895 | 123.1338 | 123.0972 | 123.0606 | -123.2712 | -123.1522 | 123.024 | 123.111 | 59.1797 | 58.6807
171.8906 | 123.2254 | -59.9167 | 63.1577 | -0.033569 | -0.0010617 | 0.064145 | 0.065014 | 0.0015765 | -0.00081187 | 0.00064723 | -0.02066 | 0.0024844 | 0.069821 | 0.06667 | -0.0047552 | 0.0050436 | -0.0016385 | -0.94757 | 63.1714 | -60.1135 | 63.0341 | -59.848 | -60.1913 | -0.87891 | -1.4877 | 63.121 | -59.9945 | 63.1348 | -59.9716 | -60.0769 | -59.8434 | -0.19684 | 0.013733 | -0.1236 | 0.068665 | 59.0378 | -0.27466 | 59.2346 | -0.07782 | -0.07782 | -0.036621 | -0.022888 | -0.054932 | 0.073242 | -0.16022 | 0.15106 | -0.082397 | 0.2655 | 123.1476 | 0.022888 | 123.1293 | 123.2849 | 123.1155 | 123.0881 | 123.0377 | -123.2712 | -123.1522 | 122.9507 | 123.0515 | 58.9691 | 58.429
172.8594 | 123.2254 | -59.9304 | 63.1897 | -0.056457 | 0.00086086 | 0.065854 | 0.066082 | 0.0030719 | -0.00038447 | 0.0025698 | -0.048126 | 0.0014164 | 0.070675 | 0.068379 | -0.004328 | 0.0039756 | -0.0018521 | -1.0757 | 63.176 | -60.1227 | 63.0478 | -59.8297 | -60.2005 | -0.99335 | -1.6571 | 63.1622 | -59.9716 | 63.1439 | -59.9625 | -60.0769 | -59.8389 | -0.19226 | -0.013733 | -0.14191 | 0.10071 | 58.9371 | -0.27008 | 59.1293 | -0.077819 | -0.041199 | -0.027466 | -0.045776 | -0.032043 | 0.091553 | -0.14648 | 0.13275 | -0.10529 | 0.29297 | 123.1705 | 0.009156 | 123.1155 | 123.2986 | 123.1338 | 123.1064 | 123.0927 | -123.3124 | -123.1613 | 122.9782 | 123.0743 | 58.8547 | 58.2733
173.9062 | 123.2849 | -59.9121 | 63.1027 | -0.13275 | 0.0012881 | 0.06329 | 0.0648 | 0.00093573 | -0.00081187 | -0.0012754 | -0.014557 | 0.00098899 | 0.067898 | 0.060047 | -0.0034736 | 0.0061118 | 0.0026339 | -1.2039 | 63.1119 | -60.0952 | 63.1439 | -59.729 | -60.1318 | -1.1581 | -1.8311 | 63.0661 | -59.9854 | 63.2355 | -59.8846 | -59.9991 | -59.7565 | -0.18311 | 0.009155 | 0.041199 | 0.1831 | 58.754 | -0.21973 | 58.9371 | -0.036621 | -0.073243 | -0.036621 | 0.13275 | 0.027465 | 0.15564 | -0.086975 | 0.22888 | -0.013732 | 0.36621 | 123.2391 | 0.10071 | 123.2208 | 123.2071 | 123.0515 | 123.024 | 122.9782 | -123.1979 | -123.0881 | 123.056 | 123.1476 | 58.7082 | 58.0811
174.8594 | 123.2346 | -59.8938 | 63.1851 | -0.01831 | 0.0017155 | 0.063076 | 0.067791 | -0.0018415 | 0.0011109 | -0.0034116 | -0.032867 | 0.00077539 | 0.070034 | 0.062824 | -0.0034736 | 0.0067526 | -0.0046293 | -1.3321 | 63.1851 | -60.1044 | 63.0844 | -59.8114 | -60.1593 | -1.2451 | -2.0508 | 63.1622 | -59.9625 | 63.1714 | -59.9213 | -60.0403 | -59.8068 | -0.21057 | 0 | -0.10071 | 0.082398 | 58.6487 | -0.2655 | 58.8593 | -0.054932 | -0.068664 | -0.022889 | -0.013733 | -0.027466 | 0.086975 | -0.14648 | 0.15564 | -0.07782 | 0.29297 | 123.1888 | 0.041198 | 123.1338 | 123.2895 | 123.1247 | 123.0789 | 123.056 | -123.2895 | -123.1476 | 122.9782 | 123.0652 | 58.5617 | 57.843
175.8906 | 123.2758 | -59.8892 | 63.1439 | -0.094604 | 0.0010745 | 0.061581 | 0.064587 | 0.0017901 | -0.0020935 | 0.0010746 | 0.019012 | 0.00034819 | 0.069821 | 0.062184 | -0.006037 | 0.0052572 | -0.0012113 | -1.5518 | 63.1531 | -60.0449 | 63.1165 | -59.7244 | -60.1089 | -1.3916 | -2.2797 | 63.1302 | -59.9487 | 63.2401 | -59.8434 | -59.967 | -59.7427 | -0.15564 | 0.009155 | -0.027466 | 0.16479 | 58.4976 | -0.21973 | 58.6533 | -0.064087 | -0.059509 | -0.013733 | 0.09613 | 0.045776 | 0.14648 | -0.07782 | 0.20599 | -0.018311 | 0.32043 | 123.1613 | 0.10528 | 123.1888 | 123.1979 | 123.0789 | 123.0423 | 123.0194 | -123.1888 | -123.0927 | 123.0057 | 123.1293 | 58.3374 | 57.6096
176.875 | 123.1979 | -59.8892 | 63.1851 | -0.041199 | 0.0036381 | 0.063931 | 0.068005 | -0.00098687 | 0.00046993 | 0.00043363 | -0.023712 | 0.0024844 | 0.070248 | 0.070942 | -0.0056098 | 0.0046164 | -0.00099766 | -1.7349 | 63.1897 | -60.1273 | 63.1027 | -59.4543 | -60.26 | -1.6525 | -2.7191 | 63.1805 | -59.9442 | 63.1531 | -59.9579 | -60.1089 | -59.8343 | -0.23804 | 0.004577 | -0.082398 | 0.43487 | 58.2367 | -0.37079 | 58.4747 | -0.13275 | -0.054932 | -0.004578 | -0.032044 | -0.068665 | 0.054931 | -0.21973 | 0.10986 | -0.16479 | 0.67291 | 123.23 | -0.013733 | 123.0972 | 123.317 | 123.1247 | 123.0789 | 123.0698 | -123.3124 | -123.1293 | 122.9919 | 123.0423 | 58.1543 | 57.1701
177.8906 | 123.3444 | -59.8572 | 63.1805 | -0.033569 | 0.00064726 | 0.06329 | 0.063946 | 0.0028583 | -0.0016663 | -0.0010618 | 0.046478 | 0.00163 | 0.067684 | 0.059193 | -0.0051824 | 0.002053 | -0.0024931 | -1.8723 | 63.1989 | -60.0128 | 63.2355 | -59.6054 | -59.9762 | -1.6205 | -2.7008 | 63.121 | -59.903 | 63.2996 | -59.7748 | -59.9075 | -59.6649 | -0.15564 | 0.018311 | 0.054932 | 0.25177 | 58.2367 | -0.11902 | 58.3923 | 0.036621 | -0.045776 | -0.059509 | 0.11902 | 0.082398 | 0.19226 | -0.050354 | 0.23804 | -0.004578 | 0.40741 | 123.2483 | 0.12817 | 123.2025 | 123.2117 | 123.024 | 123.056 | 122.9782 | -123.1934 | -123.0835 | 123.0927 | 123.1567 | 57.9849 | 57.1564
178.875 | 123.2895 | -59.8755 | 63.1668 | -0.14801 | 0.0027835 | 0.062436 | 0.063946 | 0.0034991 | -0.0078613 | -0.0017026 | -0.05423 | 0.00163 | 0.06918 | 0.065388 | -0.0053962 | 0.0069662 | -0.0027067 | -2.1652 | 63.1531 | -60.0586 | 63.4415 | -59.8343 | -60.4019 | -1.8997 | -3.1265 | 63.1256 | -59.9396 | 63.2355 | -59.8526 | -59.9716 | -59.7427 | -0.18311 | -0.013733 | 0.27466 | 0.041198 | 57.9758 | -0.52643 | 58.1589 | -0.34332 | -0.064087 | -0.041199 | 0.068665 | 0.022888 | 0.13275 | -0.096131 | 0.19684 | -0.032044 | 0.2243 | 123.5001 | 0.086975 | 123.175 | 123.2117 | 123.0652 | 123.0286 | 123.0011 | -123.2254 | -123.1064 | 123.317 | 123.111 | 57.7103 | 56.749
179.8594 | 123.3444 | -59.8251 | 63.1943 | -0.071716 | 0.0021427 | 0.062863 | 0.063305 | 0.0024311 | 0.00025633 | -0.0029844 | 0.012909 | 0.00077539 | 0.067471 | 0.065388 | -0.0053962 | 0.0018394 | 0.0028475 | -2.3346 | 63.1989 | -60.022 | 63.2355 | -59.5871 | -59.9899 | -2.0004 | -3.2089 | 63.1577 | -59.8663 | 63.3362 | -59.7427 | -59.8526 | -59.6741 | -0.19684 | 0.004578 | 0.041199 | 0.23804 | 57.8247 | -0.16479 | 58.0215 | 0.032044 | -0.041199 | -0.036621 | 0.14191 | 0.082397 | 0.15106 | -0.027466 | 0.19226 | 0.013733 | 0.43488 | 123.2574 | 0.1236 | 123.2025 | 123.2208 | 123.024 | 123.024 | 122.9828 | -123.2162 | -123.0606 | 123.0606 | 123.1613 | 57.4905 | 56.6162
180.8906 | 123.3261 | -59.8114 | 63.2217 | -0.079346 | 0.0019291 | 0.064999 | 0.066082 | 0.00072213 | -0.0010255 | 0.00043363 | 0.019012 | -0.00029261 | 0.068325 | 0.058552 | -0.0058234 | 0.00483 | -0.0035611 | -2.5269 | 63.2217 | -59.9762 | 63.2538 | -59.5688 | -59.9533 | -2.2247 | -3.5706 | 63.176 | -59.8297 | 63.3408 | -59.7198 | -59.848 | -59.6329 | -0.1648 | 0 | 0.032043 | 0.24261 | 57.5867 | -0.14191 | 57.7515 | 0.022888 | -0.018311 | -0.045777 | 0.11902 | 0.091552 | 0.17853 | -0.036621 | 0.19684 | -0.01831 | 0.40741 | 123.23 | 0.10986 | 123.1705 | 123.1979 | 123.0057 | 123.0331 | 122.9874 | -123.1979 | -123.0515 | 123.0652 | 123.1522 | 57.2845 | 56.2408
181.8594 | 123.3398 | -59.7702 | 63.2492 | -0.02594 | 0.00064726 | 0.063504 | 0.063519 | -0.0031231 | -0.0014527 | -0.0019162 | -0.0023498 | -0.00029261 | 0.068753 | 0.063465 | -0.0056098 | 0.0069662 | -0.0012113 | -2.7649 | 63.2355 | -59.9854 | 63.2904 | -59.5551 | -59.9487 | -2.3758 | -3.8406 | 63.1989 | -59.8526 | 63.3545 | -59.7198 | -59.8206 | -59.6283 | -0.21515 | -0.013733 | 0.041198 | 0.21515 | 57.3944 | -0.17853 | 57.6096 | 0.036622 | -0.082397 | -0.050354 | 0.10529 | 0.050354 | 0.14191 | -0.050354 | 0.2243 | 0.032043 | 0.4303 | 123.2758 | 0.13275 | 123.2071 | 123.2208 | 123.0515 | 123.0057 | 122.9691 | -123.2346 | -123.1018 | 123.0606 | 123.1247 | 57.0053 | 55.9296
182.9062 | 123.2437 | -59.8343 | 63.2767 | -0.11749 | 0.0021427 | 0.064145 | 0.068218 | 0.0020037 | 0.00025633 | -0.0019162 | -0.11832 | 0.0037662 | 0.071102 | 0.065602 | -0.004328 | 0.0058982 | 0.0013521 | -3.1403 | 63.2584 | -60.0037 | 63.176 | -59.6649 | -60.0861 | -2.8061 | -4.3808 | 63.2309 | -59.848 | 63.2492 | -59.8206 | -59.9945 | -59.729 | -0.16937 | -0.01831 | -0.10071 | 0.16937 | 57.0282 | -0.25177 | 57.1976 | -0.082398 | -0.013732 | -0.045776 | -0.027465 | 0.013733 | 0.10529 | -0.16022 | 0.11902 | -0.14648 | 0.33874 | 123.1796 | 0.027465 | 123.0972 | 123.262 | 123.0789 | 123.0927 | 123.0652 | -123.2803 | -123.1247 | 123.0103 | 123.0835 | 56.694 | 55.4535
183.875 | 123.317 | -59.761 | 63.2034 | -0.033569 | 0.0017155 | 0.063931 | 0.067577 | 0.0034991 | -0.0018799 | 0.0027834 | -0.069489 | 0.002698 | 0.069393 | 0.071797 | -0.0036872 | 0.0058982 | -0.00035666 | -3.4287 | 63.2263 | -59.9762 | 63.2629 | -59.6054 | -60.0174 | -2.98 | -4.6188 | 63.1943 | -59.8389 | 63.3774 | -59.7244 | -59.8938 | -59.6283 | -0.21515 | 0.022888 | 0.059509 | 0.15564 | 56.781 | -0.25635 | 56.9962 | -0.041199 | -0.07782 | -0.009155 | 0.17395 | 0.036621 | 0.13275 | -0.13275 | 0.21057 | -0.054932 | 0.37079 | 123.2391 | 0.11444 | 123.2162 | 123.2025 | 123.0331 | 122.9874 | 122.9553 | -123.1796 | -123.0423 | 123.024 | 123.1384 | 56.3324 | 55.1422
184.875 | 123.2346 | -59.7702 | 63.2812 | -0.041199 | 0.0029971 | 0.064785 | 0.068218 | -0.00013247 | -0.0023071 | -0.001489 | -0.093903 | 0.0031254 | 0.070675 | 0.060688 | -0.0039008 | 0.0058982 | -0.0016385 | -3.6575 | 63.2858 | -59.967 | 63.2538 | -59.6146 | -60.0311 | -3.1677 | -4.9393 | 63.2584 | -59.8206 | 63.3408 | -59.7565 | -59.8984 | -59.6741 | -0.19684 | 0.004578 | -0.027466 | 0.15564 | 56.6025 | -0.26093 | 56.7993 | -0.064087 | -0.050354 | -0.022888 | 0.059509 | 0.013733 | 0.096131 | -0.12817 | 0.14648 | -0.077819 | 0.35248 | 123.2208 | 0.064087 | 123.1613 | 123.2529 | 123.0789 | 123.056 | 123.0286 | -123.2483 | -123.1018 | 123.024 | 123.111 | 56.1127 | 54.8309
185.8906 | 123.2346 | -59.7702 | 63.3041 | -0.064087 | 0.0021427 | 0.063931 | 0.066509 | 0.00029473 | -0.0025207 | 0.00022003 | -0.13358 | 0.00163 | 0.071102 | 0.065815 | -0.0041144 | 0.0061118 | -0.00099766 | -3.9093 | 63.3499 | -59.9442 | 63.1851 | -59.8938 | -59.9991 | -3.1311 | -5.1544 | 63.3133 | -59.8114 | 63.3636 | -59.7244 | -59.8846 | -59.6329 | -0.17395 | 0.045777 | -0.11902 | -0.1236 | 56.6391 | -0.22888 | 56.813 | -0.054931 | -0.041198 | 0.009155 | 0.059509 | 0.045777 | 0.13733 | -0.11444 | 0.17853 | -0.073243 | 0.050354 | 123.1293 | 0.086975 | 123.175 | 123.2941 | 123.1247 | 123.1201 | 123.0835 | -123.2483 | -123.1155 | 122.9553 | 123.1338 | 55.8609 | 54.6158
186.8594 | 123.2208 | -59.761 | 63.3408 | -0.048828 | 0.0017155 | 0.062863 | 0.066082 | 0.00093573 | -0.0012391 | -0.002557 | -0.02066 | 0.003339 | 0.069821 | 0.066242 | -0.0041144 | 0.0054708 | 0.00049774 | -4.1611 | 63.3865 | -59.9442 | 63.2309 | -59.6054 | -60.0037 | -3.5431 | -5.5573 | 63.3179 | -59.8068 | 63.3408 | -59.7336 | -59.8892 | -59.642 | -0.18311 | 0.045777 | -0.10986 | 0.15564 | 56.218 | -0.24262 | 56.4011 | -0.059509 | -0.045777 | -0.022888 | 0 | 0.027465 | 0.11902 | -0.12817 | 0.16479 | -0.082397 | 0.33875 | 123.175 | 0.073242 | 123.1476 | 123.3307 | 123.1247 | 123.1476 | 123.0789 | -123.2849 | -123.1476 | 122.9919 | 123.1018 | 55.6 | 54.2038
187.9062 | 123.2254 | -59.7382 | 63.382 | -0.02594 | -0.0010617 | 0.061795 | 0.066296 | -0.00034607 | -0.0010255 | -0.0040524 | -0.05423 | 0.0022708 | 0.067684 | 0.06902 | -0.0047552 | 0.0063254 | 0.0011385 | -4.422 | 63.3865 | -59.9075 | 63.2492 | -59.5779 | -59.9762 | -3.7628 | -5.864 | 63.3316 | -59.8114 | 63.3591 | -59.6924 | -59.8572 | -59.6008 | -0.16937 | 0.004578 | -0.13275 | 0.16022 | 55.9753 | -0.23804 | 56.1447 | -0.068664 | -0.073242 | -0.050354 | -0.022888 | 0.045776 | 0.13733 | -0.11902 | 0.21057 | -0.045777 | 0.32959 | 123.1567 | 0.11902 | 123.1705 | 123.2941 | 123.143 | 123.1247 | 123.0698 | -123.2895 | -123.1934 | 122.9874 | 123.0972 | 55.3162 | 53.8742
188.875 | 123.3398 | -59.7015 | 63.3133 | -0.071716 | 0.0019291 | 0.064785 | 0.065228 | 0.0013629 | -0.0020935 | -0.0010618 | -0.014557 | 0.0018436 | 0.067898 | 0.065602 | -0.0051824 | 0.0058982 | -0.0016385 | -4.5914 | 63.3133 | -59.9121 | 63.3408 | -59.5001 | -59.9121 | -3.9368 | -6.0562 | 63.2767 | -59.7656 | 63.4552 | -59.6329 | -59.7839 | -59.5276 | -0.21057 | 0 | 0.027466 | 0.20142 | 55.7648 | -0.21057 | 55.9753 | 0 | -0.064087 | -0.036621 | 0.14191 | 0.068664 | 0.17395 | -0.082398 | 0.23804 | -0.018311 | 0.41199 | 123.2529 | 0.13275 | 123.2208 | 123.2254 | 123.0423 | 123.0148 | 122.9782 | -123.2254 | -123.0789 | 123.0423 | 123.1567 | 55.1102 | 53.6453
189.8906 | 123.3353 | -59.642 | 63.3591 | -0.071716 | 0.0034245 | 0.06329 | 0.066509 | -0.0014143 | 4.273e-05 | -0.0012754 | 0.037323 | 0.00077539 | 0.066616 | 0.065602 | -0.0041144 | 0.0039756 | -0.00057046 | -4.7653 | 63.3636 | -59.8434 | 63.3682 | -59.4543 | -59.8618 | -4.0054 | -6.1295 | 63.3362 | -59.6924 | 63.4735 | -59.5825 | -59.7153 | -59.4635 | -0.20142 | 0.004577 | 0.009155 | 0.18768 | 55.6366 | -0.21973 | 55.838 | -0.01831 | -0.050354 | -0.022888 | 0.11444 | 0.059509 | 0.17853 | -0.073242 | 0.22888 | -0.022888 | 0.3891 | 123.2117 | 0.10986 | 123.1659 | 123.2071 | 123.0286 | 123.0057 | 122.9782 | -123.2025 | -123.0515 | 123.0103 | 123.1155 | 54.8767 | 53.5126
190.8594 | 123.2162 | -59.6237 | 63.4689 | -0.041199 | 0.0017155 | 0.061581 | 0.066723 | 0.0041399 | -0.00017087 | 0.00022003 | -0.05423 | 0.004407 | 0.070675 | 0.064533 | -0.0045416 | 0.0046164 | -0.00099766 | -4.9393 | 63.4598 | -59.8251 | 63.3408 | -59.5139 | -59.9121 | -4.1794 | -6.3354 | 63.3957 | -59.6878 | 63.4277 | -59.6237 | -59.7794 | -59.5459 | -0.20142 | -0.009155 | -0.12817 | 0.10986 | 55.4443 | -0.28839 | 55.6458 | -0.086975 | -0.064087 | -0.073242 | -0.041199 | 0 | 0.07782 | -0.15564 | 0.14191 | -0.091553 | 0.31128 | 123.1659 | 0.064087 | 123.1155 | 123.2849 | 123.0835 | 123.0835 | 123.0194 | -123.2941 | -123.1567 | 122.9645 | 123.0515 | 54.6844 | 53.2883
191.9062 | 123.2574 | -59.61 | 63.4552 | -0.0030519 | 0.0029971 | 0.064358 | 0.065868 | -0.00034607 | -0.0012391 | 0.00086083 | -0.060333 | 0.0031254 | 0.070675 | 0.063679 | -0.002619 | 0.0076072 | -0.0035611 | -5.0262 | 63.4781 | -59.816 | 63.4048 | -59.4269 | -59.848 | -4.2847 | -6.3812 | 63.4232 | -59.6558 | 63.501 | -59.5688 | -59.7382 | -59.4955 | -0.20599 | 0.022888 | -0.050354 | 0.18311 | 55.3253 | -0.23804 | 55.5313 | -0.032043 | -0.045777 | -0.032043 | 0.045777 | 0.041198 | 0.11444 | -0.12817 | 0.16022 | -0.082397 | 0.3891 | 123.2208 | 0.086975 | 123.1567 | 123.2941 | 123.0789 | 123.0881 | 123.0331 | -123.2712 | -123.111 | 123.0148 | 123.111 | 54.5837 | 53.2288
192.8594 | 123.2574 | -59.5688 | 63.4827 | -0.079346 | 0.0019291 | 0.066067 | 0.066937 | 0.0049945 | 0.0013245 | 0.00086083 | -0.063385 | 0.002698 | 0.067898 | 0.066883 | 0.0044306 | 0.0056846 | -0.0035611 | -5.159 | 63.4872 | -59.8022 | 63.3682 | -59.4498 | -59.8801 | -4.4266 | -6.5781 | 63.4552 | -59.6741 | 63.4048 | -59.3033 | -59.848 | -59.6283 | -0.23346 | 0.004578 | -0.11444 | 0.11902 | 55.1422 | -0.31128 | 55.3757 | -0.07782 | -0.10529 | -0.027466 | -0.07782 | 0.2655 | -0.059509 | -0.27923 | 0.045776 | -0.17395 | 0.35248 | 123.1705 | 0.37079 | 123.0789 | 123.2895 | 123.1293 | 123.056 | 123.024 | -123.2849 | -123.1567 | 122.937 | 122.9736 | 54.4098 | 52.9907
193.9062 | 123.3078 | -59.5596 | 63.4277 | -0.10223 | 0.0019291 | 0.06564 | 0.065228 | 0.0026447 | -0.00059807 | 0.0015018 | -0.0023498 | 0.00098899 | 0.065762 | 0.061329 | -0.0036872 | 0.0052572 | 7.0538e-05 | -5.1956 | 63.4552 | -59.7519 | 63.4827 | -59.2896 | -59.7565 | -4.3991 | -6.5323 | 63.4186 | -59.6008 | 63.5742 | -59.4727 | -59.6558 | -59.3811 | -0.19226 | 0.027466 | 0.054932 | 0.27008 | 55.1605 | -0.19684 | 55.3528 | -0.004578 | -0.041199 | -0.009155 | 0.14648 | 0.086975 | 0.17853 | -0.096131 | 0.21973 | -0.054932 | 0.46234 | 123.2346 | 0.12817 | 123.175 | 123.2071 | 123.0194 | 123.0148 | 122.9782 | -123.1796 | -123.0286 | 123.0423 | 123.1338 | 54.364 | 53.0273
194.8594 | 123.2208 | -59.5139 | 63.5559 | -0.18616 | 0.0023563 | 0.062436 | 0.064373 | -0.0012005 | -0.0014527 | -0.00063437 | -0.0023498 | 0.0014164 | 0.068539 | 0.06667 | -0.0021918 | 0.003762 | -0.00078406 | -5.1819 | 63.6017 | -59.697 | 63.4506 | -59.3262 | -59.7931 | -4.4083 | -6.5964 | 63.5422 | -59.5871 | 63.533 | -59.5093 | -59.6741 | -59.4498 | -0.1831 | 0.045777 | -0.10529 | 0.18768 | 55.1056 | -0.27924 | 55.2887 | -0.096131 | -0.073242 | -0.013733 | -0.022888 | 0.004578 | 0.064087 | -0.16022 | 0.13733 | -0.086975 | 0.37079 | 123.1476 | 0.07782 | 123.1201 | 123.2986 | 123.1293 | 123.1155 | 123.056 | -123.2529 | -123.143 | 122.9645 | 123.0469 | 54.332 | 52.9175
195.8906 | 123.349 | -59.5093 | 63.4918 | -0.11749 | 0.00086086 | 0.065426 | 0.066082 | 0.00072213 | 4.273e-05 | 0.0010746 | -0.011505 | 0.0018436 | 0.067471 | 0.06966 | -0.0053962 | 0.0071798 | -0.0022793 | -5.3009 | 63.5147 | -59.7015 | 63.5147 | -59.2712 | -59.7336 | -4.5044 | -6.514 | 63.4872 | -59.5688 | 63.6612 | -59.436 | -59.5779 | -59.3445 | -0.19226 | 0.022888 | 0.022888 | 0.23804 | 55.0049 | -0.22431 | 55.1971 | -0.032044 | -0.05951 | -0.004577 | 0.16937 | 0.073242 | 0.16479 | -0.068665 | 0.22431 | -0.009155 | 0.4303 | 123.2162 | 0.13275 | 123.23 | 123.2162 | 123.056 | 123.024 | 122.9965 | -123.1934 | -123.0606 | 123.024 | 123.1705 | 54.2084 | 52.9953
196.875 | 123.2254 | -59.4955 | 63.5605 | -0.02594 | 0.0019291 | 0.064572 | 0.066723 | 8.1126e-05 | -0.00081187 | -0.0021298 | -0.084747 | 0.0046206 | 0.069821 | 0.068806 | -0.0051824 | 0.0052572 | -0.0014249 | -5.2826 | 63.6063 | -59.6832 | 63.5376 | -59.2941 | -59.7198 | -4.4998 | -6.4545 | 63.5422 | -59.5367 | 63.6383 | -59.4406 | -59.6191 | -59.3719 | -0.18768 | 0.045776 | -0.022888 | 0.20142 | 54.9957 | -0.22431 | 55.1834 | -0.036621 | -0.041199 | -0.018311 | 0.07782 | 0.054931 | 0.1236 | -0.1236 | 0.16479 | -0.082398 | 0.3891 | 123.2208 | 0.09613 | 123.175 | 123.2895 | 123.0789 | 123.1018 | 123.0377 | -123.2437 | -123.0972 | 123.0331 | 123.1338 | 54.213 | 53.0411
197.8906 | 123.2712 | -59.4452 | 63.5376 | -0.11749 | 0.0032107 | 0.063717 | 0.065228 | 0.00029473 | -0.0012391 | 0.00043363 | -0.014557 | 0.003339 | 0.068966 | 0.067311 | -0.0053962 | 0.0067526 | -0.0033475 | -5.3009 | 63.5559 | -59.642 | 63.588 | -59.2072 | -59.6832 | -4.4861 | -6.3446 | 63.5147 | -59.5001 | 63.6795 | -59.3719 | -59.5367 | -59.2987 | -0.19684 | 0.01831 | 0.050354 | 0.23804 | 54.9591 | -0.23804 | 55.1559 | -0.041199 | -0.054932 | -0.022889 | 0.14191 | 0.073242 | 0.14648 | -0.091553 | 0.20142 | -0.036621 | 0.43488 | 123.23 | 0.12817 | 123.1796 | 123.1979 | 123.0148 | 123.0011 | 122.9599 | -123.1796 | -123.0377 | 123.0331 | 123.1247 | 54.1443 | 53.1006
198.875 | 123.1979 | -59.4589 | 63.6383 | -0.10986 | 0.0021427 | 0.062436 | 0.064373 | 0.0045673 | -0.00059807 | 0.00064723 | -0.084747 | 0.0024844 | 0.065975 | 0.06902 | -0.0062506 | 0.0056846 | 7.0538e-05 | -5.2826 | 63.652 | -59.6466 | 63.4827 | -59.729 | -60.0128 | -4.3213 | -6.2805 | 63.6475 | -59.4955 | 63.6017 | -59.4498 | -59.642 | -59.3719 | -0.18768 | 0.013733 | -0.15564 | -0.27008 | 55.1376 | -0.55389 | 55.3253 | -0.36621 | -0.036621 | 0.009155 | -0.036621 | 0.009155 | 0.086975 | -0.18311 | 0.1236 | -0.14648 | -0.082398 | 123.1293 | 0.045776 | 123.0972 | 123.2986 | 123.143 | 123.111 | 123.1064 | -123.2849 | -123.1338 | 122.9416 | 123.0606 | 54.1763 | 53.1784
199.8906 | 123.2712 | -59.3903 | 63.6612 | -0.041199 | 0.0034245 | 0.063717 | 0.066296 | 0.0020037 | -0.0023071 | -0.001489 | 0.0037536 | 0.0014164 | 0.066616 | 0.064961 | -0.0051824 | 0.0052572 | 0.00071134 | -5.072 | 63.6383 | -59.5688 | 63.6703 | -59.1064 | -59.5505 | -4.2343 | -5.983 | 63.6063 | -59.4315 | 63.7482 | -59.3033 | -59.4543 | -59.23 | -0.17853 | -0.022888 | 0.009155 | 0.28381 | 55.1559 | -0.16022 | 55.3345 | 0.018311 | -0.041199 | -0.054932 | 0.086975 | 0.086975 | 0.16022 | -0.064087 | 0.20142 | -0.022888 | 0.46234 | 123.2391 | 0.12817 | 123.1796 | 123.2071 | 123.0377 | 123.0286 | 122.9965 | -123.23 | -123.0927 | 123.0606 | 123.1384 | 54.3182 | 53.4073
200.8594 | 123.175 | -59.3811 | 63.6887 | -0.048828 | 0.0036381 | 0.065854 | 0.066509 | 0.0037127 | -0.0035889 | -0.00042077 | -0.078644 | 0.00098899 | 0.068539 | 0.067311 | -0.0064642 | 0.0054708 | -0.00014306 | -5.0674 | 63.6658 | -59.61 | 63.5925 | -59.23 | -59.6878 | -4.3259 | -6.0333 | 63.6658 | -59.4315 | 63.6749 | -59.3903 | -59.5734 | -59.3216 | -0.22888 | -0.022889 | -0.096131 | 0.15106 | 55.0552 | -0.3067 | 55.2841 | -0.07782 | -0.050354 | -0.022889 | -0.013733 | -0.009155 | 0.05951 | -0.19226 | 0.10986 | -0.14191 | 0.37994 | 123.2025 | 0.041199 | 123.1064 | 123.2758 | 123.0972 | 123.0469 | 123.0469 | -123.2986 | -123.1201 | 122.9736 | 123.056 | 54.3137 | 53.3478
201.9062 | 123.2666 | -59.3674 | 63.6932 | -0.056457 | 0.0012881 | 0.062436 | 0.06715 | -0.0014143 | -0.0014527 | 0.00064723 | -0.057281 | 0.0029116 | 0.069607 | 0.063679 | -0.0051824 | 0.0056846 | 0.0026339 | -4.8889 | 63.7161 | -59.5642 | 63.6337 | -59.1522 | -59.61 | -4.1519 | -5.7861 | 63.6749 | -59.4269 | 63.7344 | -59.3216 | -59.5047 | -59.2438 | -0.19684 | 0.022888 | -0.059509 | 0.21515 | 55.2155 | -0.24261 | 55.4123 | -0.045776 | -0.059509 | -0.01831 | 0.041199 | 0.045777 | 0.1236 | -0.13733 | 0.18311 | -0.07782 | 0.41199 | 123.1979 | 0.10529 | 123.1613 | 123.2803 | 123.1018 | 123.0835 | 123.0423 | -123.2574 | -123.1201 | 123.0011 | 123.1018 | 54.4785 | 53.5812
202.8594 | 123.1934 | -59.3674 | 63.7207 | -0.01831 | -0.00020714 | 0.062436 | 0.063946 | 0.0015765 | -0.00038447 | 0.00022003 | 0.040375 | -0.00029261 | 0.069607 | 0.062397 | -0.0036872 | 0.0058982 | 0.00071134 | -4.7745 | 63.7207 | -59.5184 | 63.6612 | -59.1293 | -59.5596 | -3.9459 | -5.8273 | 63.6978 | -59.4131 | 63.707 | -59.3216 | -59.5047 | -59.2758 | -0.15106 | 0 | -0.059509 | 0.23804 | 55.4214 | -0.19226 | 55.5725 | -0.041198 | -0.045776 | -0.022888 | -0.013733 | 0.045777 | 0.091553 | -0.13733 | 0.13733 | -0.091553 | 0.3891 | 123.1796 | 0.091553 | 123.1201 | 123.2391 | 123.111 | 123.0881 | 123.0652 | -123.2391 | -123.1338 | 123.0286 | 123.0743 | 54.5929 | 53.54
203.8906 | 123.1842 | -59.3536 | 63.7482 | -0.11749 | 0.00064726 | 0.060513 | 0.065655 | 8.1126e-05 | -0.0014527 | -0.00042077 | -0.014557 | 0.0024844 | 0.068753 | 0.069447 | -0.0056098 | 0.0024802 | 0.00049774 | -4.6692 | 63.7619 | -59.523 | 63.6246 | -59.1614 | -59.6329 | -3.9825 | -5.5115 | 63.6978 | -59.4086 | 63.707 | -59.3033 | -59.4727 | -59.2667 | -0.16937 | 0.013733 | -0.1236 | 0.19226 | 55.3711 | -0.27924 | 55.5405 | -0.10986 | -0.054931 | -0.050354 | -0.041199 | 0.050354 | 0.086975 | -0.11902 | 0.14191 | -0.064087 | 0.36163 | 123.1476 | 0.10529 | 123.1155 | 123.2849 | 123.1064 | 123.1155 | 123.0515 | -123.2712 | -123.1567 | 122.9782 | 123.0606 | 54.6844 | 53.8422
204.8594 | 123.2712 | -59.3536 | 63.7482 | -0.01831 | 6.46e-06 | 0.062436 | 0.068218 | 0.0045673 | -0.00059807 | 0.0010746 | -0.035919 | 0.003339 | 0.06918 | 0.065388 | -0.0049688 | 0.006539 | 0.0015659 | -4.5731 | 63.7619 | -59.5413 | 63.6475 | -59.1522 | -59.5734 | -3.8681 | -5.3421 | 63.7115 | -59.3948 | 63.6795 | -59.2026 | -59.4681 | -59.2529 | -0.18768 | 0.013733 | -0.10071 | 0.20142 | 55.4855 | -0.21973 | 55.6732 | -0.032043 | -0.041198 | -0.036621 | -0.068665 | 0.15106 | 0.10071 | -0.11444 | 0.14191 | -0.073243 | 0.3891 | 123.1888 | 0.19226 | 123.0743 | 123.3032 | 123.1064 | 123.1155 | 123.0652 | -123.2895 | -123.143 | 123.0011 | 123.0331 | 54.7806 | 54.0115
205.8906 | 123.2941 | -59.3353 | 63.7115 | -0.094604 | 0.00022006 | 0.06564 | 0.063519 | -0.00055967 | -0.00081187 | -0.0017026 | 0.028168 | 0.0024844 | 0.068112 | 0.065815 | -0.0051824 | 0.0026938 | -0.0056973 | -4.3991 | 63.7161 | -59.5093 | 63.7299 | -59.0744 | -59.5047 | -3.685 | -5.2872 | 63.6658 | -59.3445 | 63.8672 | -59.3719 | -59.2987 | -59.0698 | -0.17395 | 0.004577 | 0.01831 | 0.26093 | 55.6503 | -0.16937 | 55.8243 | 0.004577 | -0.009155 | -0.045777 | 0.15564 | -0.036621 | 0.2655 | 0.036621 | 0.27466 | 0.045776 | 0.43487 | 123.2391 | -0.027466 | 123.2117 | 123.2254 | 123.0103 | 123.0515 | 123.0011 | -123.2208 | -123.056 | 123.0652 | 123.2025 | 54.9362 | 54.0482
206.8594 | 123.2162 | -59.3308 | 63.739 | -0.079346 | 0.0015019 | 0.063504 | 0.065441 | 0.00050853 | -0.0038025 | -0.0044796 | -0.017609 | 0.0020572 | 0.069821 | 0.064533 | -0.0034736 | 0.0063254 | 0.0030611 | -4.2892 | 63.739 | -59.5322 | 63.62 | -59.1934 | -59.5963 | -3.6301 | -5.0262 | 63.7436 | -59.4177 | 63.7207 | -59.3216 | -59.523 | -59.2621 | -0.20142 | 0 | -0.11902 | 0.13733 | 55.7007 | -0.2655 | 55.9021 | -0.064086 | -0.086975 | 0.004577 | -0.018311 | 0.009156 | 0.068665 | -0.19226 | 0.15564 | -0.10529 | 0.33875 | 123.1522 | 0.096131 | 123.1384 | 123.2712 | 123.1613 | 123.0698 | 123.0743 | -123.2712 | -123.1567 | 122.9507 | 123.0515 | 55.0415 | 54.3045
207.8906 | 123.2666 | -59.3445 | 63.6932 | 0.035095 | 0.0029971 | 0.063076 | 0.065228 | 0.0026447 | -0.0010255 | -0.0017026 | 0.012909 | 0.0020572 | 0.071102 | 0.062824 | -0.0049688 | 0.0026938 | -0.0022793 | -4.3396 | 63.6566 | -59.5322 | 63.6246 | -59.166 | -59.61 | -3.5568 | -4.8706 | 63.6337 | -59.4086 | 63.7344 | -59.2941 | -59.4498 | -59.2255 | -0.18768 | -0.036621 | -0.068664 | 0.17853 | 55.7877 | -0.2655 | 55.9753 | -0.077819 | -0.064087 | -0.059509 | 0.041199 | 0.050354 | 0.11902 | -0.10529 | 0.1831 | -0.041199 | 0.36621 | 123.1567 | 0.11444 | 123.143 | 123.1888 | 123.0423 | 123.0011 | 122.9782 | -123.2254 | -123.1018 | 122.9691 | 123.0789 | 55.0049 | 54.4739
208.875 | 123.2666 | -59.4131 | 63.6246 | -0.041199 | 0.0023563 | 0.062863 | 0.068432 | 0.0034991 | -0.0023071 | -0.0019162 | -0.096954 | 0.0041934 | 0.069821 | 0.072651 | -0.0030462 | 0.0061118 | -0.0014249 | -4.0558 | 63.6978 | -59.5917 | 63.5834 | -59.2255 | -59.6786 | -3.4744 | -4.715 | 63.6932 | -59.4269 | 63.6841 | -59.3857 | -59.5825 | -59.3079 | -0.17853 | 0.073242 | -0.041199 | 0.18768 | 55.9387 | -0.2655 | 56.1172 | -0.086975 | -0.013733 | 0.068664 | 0.059509 | 0.027466 | 0.10529 | -0.16937 | 0.11902 | -0.15564 | 0.36621 | 123.175 | 0.041199 | 123.111 | 123.2895 | 123.1201 | 123.111 | 123.1064 | -123.2162 | -123.0515 | 122.9965 | 123.0972 | 55.3574 | 54.6982
209.8906 | 123.1979 | -59.3811 | 63.7115 | 0.012207 | 0.0010745 | 0.06329 | 0.066937 | 0.00050853 | -0.00038447 | -0.0012754 | -0.023712 | 0.002698 | 0.068966 | 0.065815 | -0.002619 | 0.0067526 | -0.0035611 | -3.8956 | 63.739 | -59.5596 | 63.5971 | -59.198 | -59.6191 | -3.2593 | -4.4678 | 63.6795 | -59.436 | 63.6795 | -59.3628 | -59.5139 | -59.2804 | -0.17853 | 0.027466 | -0.11444 | 0.18311 | 56.1218 | -0.23804 | 56.3004 | -0.05951 | -0.054931 | -0.032044 | -0.032044 | 0.018311 | 0.10071 | -0.13275 | 0.15564 | -0.07782 | 0.36163 | 123.1567 | 0.073242 | 123.1155 | 123.2986 | 123.1155 | 123.1201 | 123.0606 | -123.2712 | -123.1476 | 122.9782 | 123.0606 | 55.4855 | 54.9133
210.8594 | 123.2483 | -59.3765 | 63.7207 | -0.048828 | 0.0015019 | 0.062863 | 0.066937 | 0.0013629 | -0.0012391 | 0.00086083 | -0.035919 | 0.0029116 | 0.068325 | 0.063679 | -0.0058234 | 0.0067526 | -0.0046293 | -3.7308 | 63.7115 | -59.5688 | 63.5834 | -59.2575 | -59.6466 | -3.1174 | -4.2938 | 63.6749 | -59.4406 | 63.6978 | -59.3536 | -59.5276 | -59.2758 | -0.19226 | -0.009155 | -0.13733 | 0.11902 | 56.2592 | -0.27008 | 56.4514 | -0.077819 | -0.064087 | -0.045776 | -0.022888 | 0.022888 | 0.10071 | -0.15106 | 0.16479 | -0.086975 | 0.31128 | 123.1522 | 0.086975 | 123.1384 | 123.2803 | 123.1155 | 123.0881 | 123.0515 | -123.2895 | -123.1613 | 122.9599 | 123.0743 | 55.6458 | 55.0827
211.8906 | 123.3261 | -59.3536 | 63.6566 | -0.086975 | 0.0019291 | 0.062222 | 0.064373 | -0.0029095 | -0.00081187 | -0.0017026 | 0.043427 | 0.00077539 | 0.06918 | 0.063465 | -0.0045416 | 0.003762 | -0.00014306 | -3.5156 | 63.6337 | -59.5413 | 63.6703 | -59.0881 | -59.5505 | -2.8702 | -3.9413 | 63.6337 | -59.4223 | 63.7756 | -59.2529 | -59.4177 | -59.2026 | -0.18768 | -0.022888 | 0.013733 | 0.2655 | 56.4835 | -0.19684 | 56.6711 | -0.009155 | -0.068664 | -0.022888 | 0.11902 | 0.10071 | 0.15106 | -0.064087 | 0.21973 | 0.004577 | 0.45319 | 123.2117 | 0.16937 | 123.1979 | 123.175 | 123.056 | 122.9874 | 122.9874 | -123.1979 | -123.0789 | 123.024 | 123.1293 | 55.838 | 55.4123
212.8594 | 123.2483 | -59.4131 | 63.6612 | -0.10223 | 0.0040653 | 0.066281 | 0.067577 | 0.0028583 | -0.0012391 | -0.001489 | -0.048126 | 0.0039798 | 0.065762 | 0.06197 | -0.0058234 | 0.0052572 | 0.00092494 | -3.392 | 63.6932 | -59.5963 | 63.5971 | -59.2255 | -59.6649 | -2.8198 | -4.1199 | 63.6017 | -59.491 | 63.6841 | -59.3719 | -59.4955 | -59.2667 | -0.1831 | 0.032043 | -0.064087 | 0.18768 | 56.5933 | -0.25177 | 56.7764 | -0.068665 | -0.07782 | -0.059509 | 0.022888 | 0.041199 | 0.14648 | -0.082397 | 0.2243 | -0.004577 | 0.37079 | 123.1934 | 0.11902 | 123.175 | 123.2895 | 123.0927 | 123.1064 | 123.0148 | -123.2574 | -123.1522 | 123.0103 | 123.0972 | 56.0211 | 55.2933
213.8594 | 123.2254 | -59.4452 | 63.6429 | 0.027466 | 0.0019291 | 0.063504 | 0.066937 | 0.00093573 | -0.00081187 | -0.0046934 | -0.035919 | 0.004407 | 0.071743 | 0.058552 | -0.0051824 | 0.0046164 | 0.0011385 | -3.273 | 63.707 | -59.6008 | 63.5422 | -59.2896 | -59.6878 | -2.7191 | -3.6346 | 63.6475 | -59.4681 | 63.6246 | -59.4086 | -59.5825 | -59.3491 | -0.15564 | 0.064087 | -0.10071 | 0.15564 | 56.7261 | -0.24262 | 56.8817 | -0.086975 | -0.022889 | 0.004578 | -0.01831 | 0.036621 | 0.09613 | -0.13733 | 0.11902 | -0.11444 | 0.31128 | 123.143 | 0.05951 | 123.0927 | 123.3078 | 123.1155 | 123.1522 | 123.0927 | -123.2437 | -123.111 | 122.9874 | 123.0698 | 56.1722 | 55.8105
214.9062 | 123.2391 | -59.4727 | 63.6337 | -0.056457 | 6.46e-06 | 0.063504 | 0.065868 | 0.0013629 | 0.00089713 | -0.001489 | -0.078644 | 0.0012028 | 0.070889 | 0.064747 | -0.0030462 | 0.0050436 | -0.00099766 | -3.0853 | 63.6612 | -59.6558 | 63.5239 | -59.285 | -59.697 | -2.5452 | -3.4149 | 63.6154 | -59.4864 | 63.6337 | -59.3994 | -59.5596 | -59.3399 | -0.18311 | 0.027466 | -0.10986 | 0.18768 | 56.9275 | -0.2243 | 57.1106 | -0.041198 | -0.013733 | -0.018311 | 0 | 0.073242 | 0.13275 | -0.086975 | 0.14648 | -0.073242 | 0.37079 | 123.1796 | 0.086975 | 123.1201 | 123.317 | 123.1018 | 123.1338 | 123.0881 | -123.2895 | -123.1201 | 122.9965 | 123.1064 | 56.3873 | 56.0577
215.8594 | 123.3032 | -59.4498 | 63.5696 | -0.10986 | 0.00064726 | 0.063717 | 0.066937 | 0.0020037 | 0.00089713 | -0.003198 | 0.037323 | 0.0029116 | 0.067684 | 0.067311 | -0.0066778 | 0.0061118 | -0.0031339 | -2.9022 | 63.5925 | -59.6329 | 63.5559 | -59.2346 | -59.6649 | -2.3209 | -3.1494 | 63.533 | -59.5184 | 63.6841 | -59.3628 | -59.5047 | -59.285 | -0.18311 | 0.022888 | -0.013733 | 0.21515 | 57.1289 | -0.21515 | 57.312 | -0.032043 | -0.068665 | -0.036621 | 0.11444 | 0.086975 | 0.16479 | -0.054932 | 0.23346 | 0.013733 | 0.39825 | 123.1888 | 0.15564 | 123.2025 | 123.2254 | 123.0515 | 123.0423 | 122.9828 | -123.2025 | -123.0881 | 123.0057 | 123.1338 | 56.5475 | 56.3004
216.9062 | 123.2346 | -59.5001 | 63.5971 | -0.01831 | 0.0032107 | 0.062649 | 0.067577 | 0.0034991 | -0.00059807 | -0.0038388 | -0.093903 | 0.003339 | 0.068966 | 0.064533 | -0.0034736 | 0.0050436 | -0.0022793 | -2.6459 | 63.588 | -59.6878 | 63.5468 | -59.5917 | -59.729 | -1.9913 | -2.8564 | 63.5651 | -59.5367 | 63.6337 | -59.4543 | -59.61 | -59.3582 | -0.18768 | -0.009155 | -0.050354 | -0.091553 | 57.5088 | -0.22888 | 57.6965 | -0.041199 | -0.036621 | -0.032044 | 0.036621 | 0.045776 | 0.14191 | -0.10986 | 0.17853 | -0.073242 | 0.09613 | 123.2346 | 0.082397 | 123.1705 | 123.2758 | 123.1018 | 123.0881 | 123.0652 | -123.2849 | -123.1338 | 123.0469 | 123.1338 | 56.8542 | 56.6437
217.8594 | 123.2758 | -59.4681 | 63.5742 | -0.033569 | 0.0025699 | 0.062222 | 0.063946 | 0.0034991 | 0.00068353 | -0.00084817 | 0.0068054 | 0.0022708 | 0.070889 | 0.063893 | -0.006037 | 0.0061118 | -0.00078406 | -2.4124 | 63.588 | -59.6283 | 63.5742 | -59.2255 | -59.6695 | -1.8768 | -2.6596 | 63.533 | -59.5505 | 63.6292 | -59.4269 | -59.5642 | -59.3445 | -0.16022 | 0.013733 | 0 | 0.24262 | 57.5912 | -0.20142 | 57.7515 | -0.041199 | -0.082397 | -0.041199 | 0.054931 | 0.041199 | 0.1236 | -0.09613 | 0.20599 | -0.013733 | 0.40283 | 123.2025 | 0.1236 | 123.1796 | 123.2162 | 123.0835 | 123.056 | 123.0011 | -123.2025 | -123.1247 | 123.0423 | 123.0972 | 57.0557 | 56.8085
218.8594 | 123.1796 | -59.5367 | 63.5605 | -0.056457 | 0.0034245 | 0.064358 | 0.065868 | 0.0017901 | 0.00025633 | -0.00042077 | -0.057281 | 0.002698 | 0.068112 | 0.064961 | -0.0056098 | 0.0058982 | -0.0042021 | -2.33 | 63.5651 | -59.7153 | 63.4964 | -59.7702 | -60.3104 | -1.7303 | -2.7191 | 63.5239 | -59.5917 | 63.4827 | -59.5551 | -59.7244 | -59.4635 | -0.17853 | 0.004577 | -0.064087 | -0.23346 | 57.8064 | -0.77362 | 57.9849 | -0.59509 | -0.054932 | -0.036621 | -0.07782 | -0.018311 | 0.073242 | -0.18768 | 0.12817 | -0.13275 | -0.054932 | 123.2117 | 0.036621 | 123.0743 | 123.2803 | 123.1155 | 123.1018 | 123.0606 | -123.2758 | -123.1522 | 123.0331 | 123.0194 | 57.2067 | 56.8176
219.8906 | 123.3032 | -59.523 | 63.4918 | -0.12512 | 0.0015019 | 0.065854 | 0.065228 | 0.0017901 | 0.0030335 | -0.00020717 | -0.014557 | 0.00077539 | 0.070248 | 0.065602 | -0.0036872 | 0.0052572 | 0.00071134 | -2.124 | 63.4781 | -59.7473 | 63.4918 | -59.3079 | -59.7794 | -1.5793 | -2.33 | 63.4644 | -59.61 | 63.5788 | -59.5047 | -59.6329 | -59.404 | -0.2243 | -0.013733 | 0 | 0.21515 | 57.9437 | -0.25635 | 58.168 | -0.032044 | -0.086975 | -0.027466 | 0.086975 | 0.01831 | 0.11902 | -0.10986 | 0.20599 | -0.022889 | 0.43945 | 123.2391 | 0.10529 | 123.1888 | 123.2254 | 123.0743 | 123.0011 | 122.9874 | -123.2391 | -123.1018 | 123.0148 | 123.1018 | 57.399 | 57.193
220.8594 | 123.1842 | -59.5779 | 63.4964 | -0.079346 | 0.0023563 | 0.064785 | 0.068005 | 0.0028583 | 0.0011109 | -0.0010618 | -0.084747 | 0.0035526 | 0.070034 | 0.066883 | -0.0036872 | 0.0063254 | -0.0022793 | -1.973 | 63.5056 | -59.7656 | 63.3774 | -59.4681 | -59.9075 | -1.4923 | -2.2659 | 63.4918 | -59.6466 | 63.4964 | -59.6008 | -59.7656 | -59.4681 | -0.18768 | 0.009155 | -0.11902 | 0.10986 | 58.0856 | -0.32959 | 58.2733 | -0.14191 | -0.068664 | -0.004578 | 0 | -0.022888 | 0.10986 | -0.18768 | 0.17853 | -0.11902 | 0.29755 | 123.143 | 0.045776 | 123.143 | 123.2712 | 123.1384 | 123.0835 | 123.0698 | -123.262 | -123.143 | 122.9553 | 123.0743 | 57.605 | 57.312
221.8906 | 123.2208 | -59.5322 | 63.5056 | -0.02594 | 6.46e-06 | 0.062649 | 0.065655 | -0.00013247 | -0.0038025 | -0.0046934 | -0.0023498 | 0.00098899 | 0.068539 | 0.06667 | -0.0062506 | 0.0056846 | -0.0024931 | -1.6937 | 63.5239 | -59.729 | 63.4781 | -59.3445 | -59.7565 | -1.149 | -1.8723 | 63.4827 | -59.6283 | 63.5376 | -59.523 | -59.6695 | -59.4406 | -0.19684 | 0.018311 | -0.027466 | 0.18768 | 58.3832 | -0.2243 | 58.58 | -0.027466 | -0.09613 | -0.022888 | 0.032044 | 0.009156 | 0.091553 | -0.13733 | 0.18768 | -0.041199 | 0.38452 | 123.2071 | 0.10529 | 123.1659 | 123.2529 | 123.111 | 123.056 | 123.0148 | -123.2346 | -123.1338 | 123.0103 | 123.0698 | 57.8384 | 57.6599
222.8594 | 123.2071 | -59.5963 | 63.4827 | -0.086975 | 0.0023563 | 0.062008 | 0.065441 | 0.0030719 | -0.00038447 | -0.0021298 | -0.017609 | 0.0020572 | 0.070034 | 0.065602 | -0.0068914 | 0.00483 | 0.0019931 | -1.5106 | 63.5056 | -59.7427 | 63.4415 | -59.3765 | -59.7885 | -1.0117 | -1.7532 | 63.4689 | -59.6146 | 63.4369 | -59.3079 | -59.8892 | -59.697 | -0.14648 | 0.022888 | -0.041199 | 0.21973 | 58.5846 | -0.19226 | 58.7311 | -0.045776 | -0.018311 | -0.013733 | -0.045776 | 0.28839 | -0.10071 | -0.29297 | -0.082397 | -0.27466 | 0.36621 | 123.1842 | 0.3067 | 123.0515 | 123.2483 | 123.0835 | 123.1018 | 123.0652 | -123.2254 | -123.0972 | 123.0377 | 123.0331 | 58.0856 | 57.843
223.8906 | 123.2117 | -59.5963 | 63.4964 | -0.041199 | 0.0015019 | 0.06329 | 0.068218 | 0.0056353 | 0.0019653 | 6.432e-06 | -0.051178 | 0.0014164 | 0.067471 | 0.069447 | -0.0041144 | 0.0069662 | -0.00099766 | -1.3824 | 63.4552 | -59.816 | 63.4094 | -59.4177 | -59.8434 | -0.91095 | -1.6067 | 63.4323 | -59.6741 | 63.4872 | -59.61 | -59.7473 | -59.4955 | -0.21973 | -0.041199 | -0.086975 | 0.17853 | 58.6853 | -0.24719 | 58.905 | -0.027466 | -0.07782 | -0.064087 | -0.009155 | -0.013733 | 0.10071 | -0.15106 | 0.17853 | -0.073242 | 0.39825 | 123.2254 | 0.064087 | 123.1613 | 123.2712 | 123.1064 | 123.0515 | 123.0286 | -123.3124 | -123.1705 | 123.0057 | 123.0835 | 58.2138 | 57.9895
224.8594 | 123.2574 | -59.6191 | 63.446 | -0.071716 | 0.0021427 | 0.064572 | 0.066723 | 0.00072213 | 0.0013245 | -0.0012754 | -0.069489 | 0.0024844 | 0.071316 | 0.068165 | -0.0039008 | 0.0046164 | -0.0029203 | -1.2405 | 63.4644 | -59.816 | 63.3957 | -59.4223 | -59.8572 | -0.74158 | -1.4603 | 63.4323 | -59.6786 | 63.4918 | -59.6054 | -59.7382 | -59.4864 | -0.19684 | 0.01831 | -0.050354 | 0.19684 | 58.8776 | -0.23804 | 59.0744 | -0.041199 | -0.059509 | -0.013733 | 0.045776 | 0.013733 | 0.13275 | -0.11902 | 0.19226 | -0.059509 | 0.39368 | 123.2117 | 0.073242 | 123.1705 | 123.2803 | 123.111 | 123.0835 | 123.0515 | -123.262 | -123.1247 | 123.0148 | 123.111 | 58.3786 | 58.1589
225.8906 | 123.3307 | -59.61 | 63.4003 | 0.0045776 | 0.00022006 | 0.063717 | 0.063091 | -0.00098687 | -0.0027345 | -0.0010618 | 0.046478 | 0.0012028 | 0.070034 | 0.06667 | -0.0056098 | 0.0076072 | 0.0011385 | -1.1124 | 63.4369 | -59.7931 | 63.4323 | -59.3674 | -59.8022 | -0.54932 | -0.70038 | 63.4644 | -59.6237 | 63.4644 | -59.4681 | -59.642 | -59.4543 | -0.18311 | 0.036621 | 0.032043 | 0.24261 | 59.0607 | -0.19226 | 59.2438 | -0.009155 | -0.013733 | 0.064086 | 0.064086 | 0.14191 | 0.15564 | -0.032044 | 0.16937 | -0.018311 | 0.42572 | 123.2254 | 0.15564 | 123.0881 | 123.23 | 123.0881 | 123.0469 | 123.0743 | -123.1934 | -123.024 | 123.0423 | 123.0743 | 58.4976 | 58.9096
226.8594 | 123.2437 | -59.6878 | 63.4094 | -0.02594 | 0.00086086 | 0.063504 | 0.065655 | 0.00072213 | -0.00059807 | -0.00084817 | -0.05423 | 0.003339 | 0.070034 | 0.062611 | -0.0053962 | 0.006539 | 0.0051975 | -1.0849 | 63.4094 | -59.8846 | 63.2629 | -59.5734 | -59.9762 | -0.63629 | -1.3458 | 63.3728 | -59.729 | 63.3957 | -59.7107 | -59.8343 | -59.5688 | -0.19684 | 0 | -0.14648 | 0.11444 | 59.0515 | -0.28839 | 59.2484 | -0.091552 | -0.041199 | -0.036621 | -0.013733 | -0.022888 | 0.11902 | -0.14649 | 0.16022 | -0.10529 | 0.31128 | 123.1476 | 0.018311 | 123.1247 | 123.2941 | 123.1018 | 123.0972 | 123.0606 | -123.2941 | -123.1384 | 122.9507 | 123.0835 | 58.6029 | 58.342
227.8906 | 123.3124 | -59.6329 | 63.3408 | -0.086975 | 0.0012881 | 0.062436 | 0.063946 | 0.0015765 | -0.00081187 | -0.0010618 | 0.00070198 | 0.0029116 | 0.067898 | 0.05962 | -0.0056098 | 0.0039756 | -0.00057046 | -0.90637 | 63.3911 | -59.8434 | 63.3636 | -59.4864 | -59.8846 | -0.39368 | -1.0712 | 63.3362 | -59.6924 | 63.4644 | -59.5871 | -59.7198 | -59.491 | -0.21057 | 0.050354 | 0.022888 | 0.14648 | 59.2392 | -0.25177 | 59.4498 | -0.041199 | -0.059509 | -0.004577 | 0.1236 | 0.045777 | 0.14191 | -0.086975 | 0.20142 | -0.027466 | 0.35706 | 123.2071 | 0.10529 | 123.1567 | 123.2346 | 123.0286 | 123.024 | 122.9691 | -123.1842 | -123.0331 | 122.9965 | 123.0972 | 58.7265 | 58.5617
228.8594 | 123.2162 | -59.7244 | 63.3591 | -0.056457 | 0.0021427 | 0.064358 | 0.068218 | 0.0030719 | -0.00059807 | -0.001489 | -0.090851 | 0.0018436 | 0.069393 | 0.07201 | -0.0045416 | 0.0071798 | 0.0017795 | -0.87891 | 63.4003 | -59.8938 | 63.2263 | -59.6466 | -60.0449 | -0.46234 | -1.1261 | 63.3362 | -59.7977 | 63.3453 | -59.7702 | -59.903 | -59.6329 | -0.16937 | 0.041199 | -0.13275 | 0.07782 | 59.2621 | -0.32043 | 59.4315 | -0.15106 | -0.073242 | -0.022888 | -0.013733 | -0.045777 | 0.091552 | -0.17853 | 0.16479 | -0.10529 | 0.24719 | 123.1201 | 0.027465 | 123.143 | 123.2941 | 123.1338 | 123.1247 | 123.0606 | -123.2529 | -123.1567 | 122.9507 | 123.0698 | 58.8455 | 58.5983
229.8906 | 123.2162 | -59.7061 | 63.3774 | -0.071716 | 0.0021427 | 0.062008 | 0.065655 | -0.0016279 | -0.00017087 | -0.0021298 | -0.029816 | 0.0022708 | 0.071316 | 0.067738 | -0.0032598 | 0.00483 | -0.00099766 | -0.71411 | 63.4186 | -59.8938 | 63.2584 | -59.5871 | -59.9625 | -0.22888 | -0.89722 | 63.3545 | -59.7748 | 63.3682 | -59.7107 | -59.8663 | -59.5963 | -0.18768 | 0.041199 | -0.11902 | 0.11902 | 59.4772 | -0.25635 | 59.6649 | -0.068664 | -0.068664 | -0.022888 | -0.009155 | -0.004577 | 0.10986 | -0.16022 | 0.17853 | -0.091553 | 0.3067 | 123.1522 | 0.064087 | 123.143 | 123.3124 | 123.1293 | 123.1247 | 123.0606 | -123.2712 | -123.1522 | 122.9645 | 123.0743 | 58.992 | 58.8089
230.8594 | 123.3078 | -59.729 | 63.327 | -0.079346 | 0.0032107 | 0.063717 | 0.066509 | 0.0022173 | 0.00025633 | -0.001489 | -0.048126 | 0.0031254 | 0.067471 | 0.06902 | -0.0051824 | 0.0052572 | -0.00099766 | -0.60425 | 63.3957 | -59.9121 | 63.2812 | -59.5734 | -59.9396 | -0.13733 | -0.76904 | 63.3362 | -59.7702 | 63.446 | -59.903 | -60.0174 | -59.5917 | -0.1831 | 0.068665 | -0.045776 | 0.15564 | 59.5917 | -0.21057 | 59.7748 | -0.027466 | -0.041199 | 0.009156 | 0.11902 | -0.17395 | 0.13733 | -0.28839 | 0.17853 | -0.24719 | 0.33875 | 123.1934 | -0.13275 | 123.2162 | 123.3078 | 123.1064 | 123.1247 | 123.0652 | -123.2391 | -123.0972 | 123.0103 | 123.175 | 59.1248 | 58.96
231.9062 | 123.3261 | -59.7336 | 63.3041 | -0.14801 | 0.0036381 | 0.065213 | 0.067577 | 0.0013629 | 4.273e-05 | -0.00063437 | -0.045074 | 0.0029116 | 0.070675 | 0.067311 | -0.0039008 | 0.00483 | 7.0538e-05 | -0.59967 | 63.3179 | -59.9442 | 63.2401 | -59.5917 | -60.0128 | -0.16479 | -0.76904 | 63.2538 | -59.816 | 63.3591 | -59.4589 | -59.7473 | -59.6283 | -0.21057 | 0.013733 | -0.064087 | 0.14191 | 59.5688 | -0.27923 | 59.7794 | -0.068664 | -0.082397 | -0.050354 | 0.054932 | 0.27466 | 0.10529 | -0.013732 | 0.18768 | 0.068665 | 0.35248 | 123.1842 | 0.35706 | 123.175 | 123.262 | 123.0698 | 123.0515 | 122.9874 | -123.2483 | -123.1201 | 122.9736 | 123.0927 | 59.1339 | 58.9645
232.8594 | 123.1979 | -59.7565 | 63.3224 | -0.01831 | 0.0047061 | 0.064785 | 0.065228 | -0.00034607 | -0.00038447 | 0.00086083 | -0.048126 | 0.0020572 | 0.068753 | 0.063679 | -0.0041144 | 0.0052572 | 0.0060519 | -0.46234 | 63.3408 | -59.9487 | 63.2492 | -59.6054 | -59.9762 | -0.032043 | -0.64087 | 63.3041 | -59.8022 | 63.3865 | -59.9625 | -59.7931 | -59.4635 | -0.19226 | 0.01831 | -0.073242 | 0.15106 | 59.7244 | -0.21973 | 59.9167 | -0.027466 | -0.045776 | -0.018311 | 0.064087 | -0.20599 | 0.29297 | -0.036621 | 0.33874 | 0.009155 | 0.34332 | 123.1979 | -0.16022 | 123.1888 | 123.2895 | 123.1064 | 123.0972 | 123.0606 | -123.2712 | -123.1247 | 123.0057 | 123.143 | 59.2941 | 59.1156
233.9062 | 123.3032 | -59.7702 | 63.2309 | -0.071716 | 0.0015019 | 0.065213 | 0.063732 | 0.00029473 | -0.0014527 | -0.001489 | -0.0054016 | 0.00077539 | 0.067471 | 0.06197 | -0.0058234 | 0.0041892 | -0.00099766 | -0.43945 | 63.2355 | -59.9625 | 63.2721 | -59.5734 | -60.0037 | -0.022888 | -0.59967 | 63.2263 | -59.8206 | 63.3865 | -59.7244 | -59.8526 | -59.5963 | -0.19226 | 0.004578 | 0.041199 | 0.19684 | 59.7473 | -0.23346 | 59.9396 | -0.041199 | -0.050354 | -0.004578 | 0.15564 | 0.045777 | 0.17395 | -0.082397 | 0.22431 | -0.032043 | 0.3891 | 123.2346 | 0.096131 | 123.2071 | 123.1979 | 123.0469 | 123.0057 | 122.9965 | -123.1934 | -123.0515 | 123.0423 | 123.1567 | 59.3308 | 59.1705
234.8594 | 123.2391 | -59.7702 | 63.3041 | -0.02594 | 0.0027835 | 0.062008 | 0.066937 | 0.00093573 | -0.0029481 | 0.00064723 | -0.02066 | 0.0035526 | 0.070461 | 0.062184 | -0.0028326 | 0.0063254 | 7.0538e-05 | -0.36621 | 63.3133 | -59.9762 | 63.1851 | -59.6832 | -60.0494 | 0.041199 | -0.57678 | 63.2721 | -59.8434 | 63.2858 | -59.7885 | -59.9442 | -59.6695 | -0.20599 | 0.009155 | -0.11902 | 0.086975 | 59.8114 | -0.27923 | 60.0174 | -0.073242 | -0.073242 | -0.032043 | -0.01831 | -0.01831 | 0.10071 | -0.17395 | 0.17395 | -0.10071 | 0.29297 | 123.1613 | 0.054932 | 123.1293 | 123.2895 | 123.1155 | 123.0835 | 123.0423 | -123.2803 | -123.1476 | 122.9553 | 123.056 | 59.404 | 59.1934
235.8906 | 123.3078 | -59.7794 | 63.2492 | -0.033569 | 0.00086086 | 0.064785 | 0.063519 | -0.00013247 | -0.00038447 | -0.001489 | 0.043427 | 0.0012028 | 0.068539 | 0.064106 | -0.0058234 | 0.0035482 | 0.0015659 | -0.34332 | 63.2629 | -59.9716 | 63.2355 | -59.6146 | -59.9945 | 0.11444 | -0.48065 | 63.1989 | -59.8297 | 63.3591 | -59.7198 | -59.848 | -59.6329 | -0.19226 | 0.013732 | -0.013733 | 0.1648 | 59.8938 | -0.21515 | 60.0861 | -0.022888 | -0.050354 | -0.050354 | 0.10986 | 0.059509 | 0.14648 | -0.068664 | 0.19684 | -0.01831 | 0.35706 | 123.2071 | 0.10986 | 123.1888 | 123.2346 | 123.0286 | 123.0423 | 122.9782 | -123.2208 | -123.0789 | 123.0148 | 123.1384 | 59.436 | 59.2987
236.8594 | 123.2346 | -59.816 | 63.2721 | -0.048828 | 0.0012881 | 0.062436 | 0.066082 | 0.00050853 | 0.00089713 | -0.0040524 | -0.042023 | 0.002698 | 0.067257 | 0.070088 | -0.0039008 | 0.0044028 | -0.0014249 | -0.31586 | 63.327 | -60.0037 | 63.1622 | -59.697 | -60.0632 | 0.086975 | -0.4715 | 63.2629 | -59.8434 | 63.2675 | -59.8068 | -59.935 | -59.6924 | -0.18768 | 0.054931 | -0.10986 | 0.11902 | 59.903 | -0.24719 | 60.0906 | -0.059509 | -0.027466 | -0.009156 | -0.004578 | 0.009155 | 0.1236 | -0.11902 | 0.15106 | -0.091553 | 0.3067 | 123.1659 | 0.036621 | 123.111 | 123.3307 | 123.1064 | 123.143 | 123.0789 | -123.2758 | -123.1155 | 122.9782 | 123.0835 | 59.5001 | 59.3445
237.8906 | 123.3078 | -59.7839 | 63.2126 | -0.064087 | 0.0017155 | 0.064572 | 0.063519 | -0.00077327 | 0.0017517 | -0.00042077 | 0.03122 | 0.0018436 | 0.069393 | 0.063465 | -0.0045416 | 0.0039756 | -0.0033475 | -0.27466 | 63.2309 | -59.9899 | 63.208 | -59.6146 | -60.0311 | 0.16022 | -0.40741 | 63.176 | -59.8618 | 63.3087 | -59.7382 | -59.8663 | -59.6375 | -0.20599 | 0.018311 | -0.004577 | 0.16937 | 59.9442 | -0.24719 | 60.1501 | -0.041199 | -0.077819 | -0.036621 | 0.096131 | 0.045777 | 0.14648 | -0.082397 | 0.2243 | -0.004578 | 0.37537 | 123.1979 | 0.1236 | 123.1705 | 123.2208 | 123.0377 | 123.0148 | 122.9599 | -123.2025 | -123.0743 | 122.9919 | 123.0927 | 59.5093 | 59.3765
238.8594 | 123.2437 | -59.816 | 63.2309 | -0.094604 | 0.0015019 | 0.063931 | 0.065228 | 0.0022173 | -0.0020935 | -0.0012754 | -0.060333 | 0.002698 | 0.070034 | 0.062184 | -0.0062506 | 0.003121 | -0.00014306 | -0.21973 | 63.2721 | -60.0174 | 63.1851 | -59.6695 | -60.0769 | 0.13733 | -0.36621 | 63.2492 | -59.8892 | 63.2812 | -59.8526 | -59.8892 | -59.6466 | -0.20142 | 0.041199 | -0.045776 | 0.14648 | 59.9533 | -0.26093 | 60.1547 | -0.059509 | -0.073242 | 0.018311 | 0.050354 | -0.036621 | 0.16937 | -0.073242 | 0.24262 | 0 | 0.3479 | 123.2025 | 0.036621 | 123.1705 | 123.2895 | 123.1384 | 123.0881 | 123.0652 | -123.2483 | -123.1201 | 123.0011 | 123.0972 | 59.5963 | 59.4498
239.9062 | 123.1979 | -59.8526 | 63.2263 | -0.056457 | 0.00086086 | 0.063504 | 0.068218 | 0.00029473 | -0.0014527 | 6.432e-06 | -0.087799 | 0.004407 | 0.068325 | 0.063679 | -0.0036872 | 0.0071798 | 0.0086153 | -0.26093 | 63.2309 | -60.0403 | 63.1165 | -59.7656 | -60.173 | 0.050354 | -0.50354 | 63.208 | -59.8892 | 63.2263 | -60.3745 | -59.8755 | -59.4589 | -0.18768 | 0.004578 | -0.10986 | 0.086975 | 59.903 | -0.32043 | 60.0906 | -0.13275 | -0.036621 | -0.01831 | 0 | -0.52185 | 0.39368 | -0.022888 | 0.4303 | 0.013733 | 0.27466 | 123.1567 | -0.48523 | 123.1155 | 123.2712 | 123.0972 | 123.0835 | 123.0606 | -123.2666 | -123.1155 | 122.9691 | 123.0789 | 59.5917 | 59.3491
240.8594 | 123.2483 | -59.8434 | 63.2263 | -0.033569 | 0.0038517 | 0.064572 | 0.065441 | -0.0014143 | -0.00017087 | 0.0025698 | -0.048126 | 0.0020572 | 0.068112 | 0.067311 | -0.006037 | 0.003762 | -0.0022793 | -0.18768 | 63.2584 | -60.0586 | 63.1622 | -59.6832 | -60.0952 | 0.16479 | -0.31586 | 63.1989 | -59.8801 | 63.295 | -59.9304 | -59.9167 | -59.6329 | -0.21515 | 0.032044 | -0.064087 | 0.16022 | 60.0082 | -0.25177 | 60.2234 | -0.036621 | -0.036621 | -0.027465 | 0.068665 | -0.086975 | 0.21057 | -0.073242 | 0.24719 | -0.036621 | 0.37537 | 123.2208 | -0.050354 | 123.175 | 123.317 | 123.0789 | 123.1018 | 123.0423 | -123.2849 | -123.1064 | 123.0057 | 123.1384 | 59.6558 | 59.5276
241.8906 | 123.2346 | -59.8663 | 63.2309 | -0.064087 | 0.0029971 | 0.062222 | 0.066509 | 0.0017901 | 0.00089713 | -0.0040524 | -0.045074 | 0.0039798 | 0.070675 | 0.064106 | -0.0045416 | 0.0056846 | -0.0029203 | -0.18768 | 63.2492 | -60.0311 | 63.1348 | -59.7153 | -60.0815 | 0.18768 | -0.31586 | 63.2309 | -59.9121 | 63.2584 | -59.8297 | -59.9625 | -59.7198 | -0.1648 | 0.018311 | -0.09613 | 0.15106 | 60.054 | -0.21515 | 60.2188 | -0.050354 | -0.045776 | 0 | 0.027466 | 0.036621 | 0.14648 | -0.09613 | 0.19226 | -0.050354 | 0.31586 | 123.1659 | 0.082397 | 123.1705 | 123.2803 | 123.143 | 123.1155 | 123.0972 | -123.262 | -123.143 | 123.0011 | 123.1247 | 59.6786 | 59.5505
242.8594 | 123.262 | -59.848 | 63.208 | -0.0030519 | -0.00020714 | 0.062436 | 0.0648 | 0.0028583 | -0.0010255 | -0.00020717 | -0.05423 | 0.0014164 | 0.070248 | 0.063038 | -0.004328 | 0.0061118 | -0.00014306 | -0.16022 | 63.2401 | -60.0494 | 63.1393 | -59.7153 | -60.0769 | 0.19226 | -0.22888 | 63.1714 | -59.9304 | 63.2812 | -59.7977 | -59.9899 | -59.7336 | -0.20142 | 0.032043 | -0.068665 | 0.13275 | 60.0403 | -0.22888 | 60.2417 | -0.027466 | -0.082398 | -0.036621 | 0.073242 | 0.050354 | 0.11444 | -0.14191 | 0.19684 | -0.059509 | 0.33417 | 123.1888 | 0.13275 | 123.2117 | 123.2895 | 123.1018 | 123.0881 | 123.0194 | -123.2574 | -123.1384 | 122.9874 | 123.1293 | 59.6878 | 59.6191
243.8906 | 123.2437 | -59.8618 | 63.208 | -0.048828 | 0.0042789 | 0.062436 | 0.0648 | 0.0034991 | 0.00025633 | -0.0023434 | -0.069489 | 0.0020572 | 0.06918 | 0.062397 | -0.0056098 | 0.0063254 | -0.0048429 | -0.13275 | 63.2355 | -60.0174 | 63.1256 | -59.7153 | -60.0998 | 0.16022 | -0.28381 | 63.1531 | -59.9121 | 63.2492 | -59.8434 | -59.9899 | -59.7244 | -0.15564 | 0.027466 | -0.082398 | 0.14648 | 60.022 | -0.23804 | 60.1776 | -0.082397 | -0.050354 | -0.054932 | 0.041199 | 0.01831 | 0.13733 | -0.12817 | 0.18768 | -0.07782 | 0.30212 | 123.143 | 0.068664 | 123.1613 | 123.2529 | 123.0652 | 123.0972 | 123.0148 | -123.2254 | -123.1201 | 122.9874 | 123.111 | 59.729 | 59.5779
244.8594 | 123.2346 | -59.8663 | 63.1943 | -0.064087 | 0.0027835 | 0.063717 | 0.065655 | 0.00050853 | -0.0018799 | -0.00084817 | -0.038971 | 0.0018436 | 0.070461 | 0.064961 | -0.0045416 | 0.00483 | 0.0071201 | -0.16022 | 63.2172 | -60.0586 | 63.1348 | -59.7244 | -60.1089 | 0.16022 | -0.30212 | 63.1485 | -59.9442 | 63.2263 | -59.8801 | -60.0037 | -59.7656 | -0.19226 | 0.022888 | -0.059509 | 0.14191 | 60.0266 | -0.24262 | 60.2188 | -0.050354 | -0.07782 | -0.045776 | 0.032043 | -0.013733 | 0.10071 | -0.13733 | 0.17853 | -0.059509 | 0.33417 | 123.1934 | 0.064087 | 123.1705 | 123.2758 | 123.0927 | 123.0835 | 123.0148 | -123.2529 | -123.1384 | 123.0011 | 123.0927 | 59.7061 | 59.5642
245.8906 | 123.2208 | -59.8526 | 63.2172 | -0.071716 | 0.0036381 | 0.064145 | 0.065868 | -0.0018415 | -0.00059807 | -0.0023434 | 0.025116 | 0.0014164 | 0.070248 | 0.064106 | -0.002619 | 0.0050436 | -0.00099766 | -0.11444 | 63.1943 | -60.0403 | 63.1485 | -59.6878 | -60.0632 | 0.2243 | -0.25177 | 63.1805 | -59.9396 | 63.1989 | -59.8572 | -59.9716 | -59.7702 | -0.18768 | -0.022888 | -0.068664 | 0.1648 | 60.0769 | -0.21057 | 60.2646 | -0.022888 | -0.086975 | -0.036621 | -0.01831 | -0.004578 | 0.082397 | -0.11902 | 0.16937 | -0.032044 | 0.35248 | 123.1888 | 0.082397 | 123.1384 | 123.2346 | 123.1201 | 123.0469 | 123.0331 | -123.2574 | -123.1567 | 123.0011 | 123.0515 | 59.7382 | 59.6008
246.8594 | 123.1979 | -59.8846 | 63.1805 | -0.056457 | 0.0023563 | 0.063504 | 0.067577 | 0.0015765 | 0.00046993 | -0.0012754 | -0.069489 | 0.0037662 | 0.068112 | 0.066883 | -0.0047552 | 0.0067526 | -0.00078406 | -0.17395 | 63.1989 | -60.1089 | 63.0707 | -59.7702 | -60.1868 | 0.07782 | -0.37079 | 63.1485 | -59.9579 | 63.1668 | -59.935 | -60.0769 | -59.8022 | -0.2243 | 0.018311 | -0.10986 | 0.11444 | 59.9625 | -0.30212 | 60.1868 | -0.07782 | -0.073242 | -0.032043 | -0.013733 | -0.050354 | 0.082398 | -0.19226 | 0.15564 | -0.11902 | 0.33874 | 123.1796 | 0.022888 | 123.1247 | 123.3078 | 123.1064 | 123.0835 | 123.0331 | -123.2895 | -123.1384 | 122.9553 | 123.0515 | 59.7107 | 59.5139
247.8906 | 123.2895 | -59.8572 | 63.1943 | -0.048828 | 0.0027835 | 0.064145 | 0.065014 | -0.00055967 | 0.0017517 | -0.0027708 | 0.040375 | -0.00050621 | 0.068112 | 0.061543 | -0.0051824 | 0.0046164 | -0.0018521 | -0.10529 | 63.1668 | -60.0449 | 63.1989 | -59.6512 | -60.0174 | 0.25177 | -0.1831 | 63.121 | -59.9396 | 63.2675 | -59.8022 | -59.9075 | -59.7015 | -0.18768 | -0.027466 | 0.004578 | 0.20599 | 60.1089 | -0.16022 | 60.2966 | 0.027466 | -0.082397 | -0.073242 | 0.073242 | 0.054932 | 0.15564 | -0.050354 | 0.23804 | 0.032043 | 0.39368 | 123.2437 | 0.13733 | 123.2071 | 123.2117 | 123.0606 | 123.024 | 122.9782 | -123.2391 | -123.1338 | 123.056 | 123.1247 | 59.7519 | 59.6741
248.8594 | 123.349 | -59.8526 | 63.1393 | -0.071716 | 0.0012881 | 0.062863 | 0.066937 | 0.0022173 | -0.00059807 | -0.0017026 | -0.038971 | 0.00163 | 0.069393 | 0.073719 | -0.0034736 | 0.0046164 | 0.0013521 | -0.21973 | 63.1531 | -60.1273 | 63.1165 | -59.7382 | -60.1318 | 0.10071 | -0.33875 | 63.1302 | -59.9533 | 63.327 | -59.7656 | -59.9854 | -59.7198 | -0.27466 | 0.013733 | -0.022888 | 0.11444 | 59.9533 | -0.27924 | 60.228 | -0.004578 | -0.10071 | -0.009155 | 0.18768 | 0.086975 | 0.13275 | -0.13275 | 0.23346 | -0.032044 | 0.3891 | 123.2437 | 0.18768 | 123.2803 | 123.2803 | 123.0835 | 123.0057 | 122.9828 | -123.2666 | -123.0927 | 122.9691 | 123.1796 | 59.6329 | 59.5139
249.8906 | 123.2071 | -59.9167 | 63.176 | -0.079346 | 0.0081241 | 0.064358 | 0.068432 | 8.1126e-05 | -0.0031617 | 0.0015018 | -0.081696 | 0.0020572 | 0.070034 | 0.065815 | -0.0047552 | 0.0063254 | -0.00014306 | -0.5127 | 63.1348 | -60.1273 | 62.9837 | -59.8389 | -60.2417 | 0.022888 | -0.43488 | 63.176 | -59.9854 | 63.1393 | -59.9945 | -60.1089 | -59.8297 | -0.21057 | -0.041198 | -0.19226 | 0.07782 | 59.9396 | -0.32501 | 60.1501 | -0.11444 | -0.068665 | 0 | -0.036621 | -0.07782 | 0.086975 | -0.19226 | 0.15564 | -0.1236 | 0.28839 | 123.111 | -0.009155 | 123.1247 | 123.262 | 123.1613 | 123.0515 | 123.0927 | -123.3032 | -123.1613 | 122.9004 | 123.056 | 59.404 | 59.4818
250.8594 | 123.2346 | -59.8938 | 63.1805 | -0.02594 | 0.0015019 | 0.064572 | 0.06715 | 0.0032855 | 0.00046993 | -0.0012754 | -0.075592 | 0.003339 | 0.071316 | 0.064961 | -0.007105 | 0.0054708 | 0.0022067 | -0.16022 | 63.2034 | -60.0952 | 63.0753 | -59.7702 | -60.1639 | 0.086975 | -0.32959 | 63.1439 | -59.9487 | 63.176 | -59.9213 | -60.0494 | -59.7977 | -0.20142 | 0.022888 | -0.10529 | 0.1236 | 59.9808 | -0.27008 | 60.1822 | -0.068664 | -0.054931 | -0.036621 | -0.004578 | -0.027466 | 0.096131 | -0.15564 | 0.15106 | -0.10071 | 0.32501 | 123.1705 | 0.027465 | 123.1247 | 123.2986 | 123.0927 | 123.0972 | 123.0377 | -123.2758 | -123.1293 | 122.9691 | 123.0698 | 59.7336 | 59.5642
251.8906 | 123.2025 | -59.9167 | 63.176 | -0.056457 | 0.0012881 | 0.062222 | 0.06715 | 0.0030719 | -0.0025207 | -0.0038388 | -0.084747 | 0.0029116 | 0.070248 | 0.065388 | -0.0062506 | 0.0067526 | -0.0031339 | -0.15564 | 63.1851 | -60.0723 | 63.089 | -59.7519 | -60.173 | 0.10986 | -0.31586 | 63.1393 | -59.9533 | 63.176 | -59.9258 | -60.0632 | -59.8114 | -0.15564 | 0.009156 | -0.086975 | 0.1648 | 60.0266 | -0.25635 | 60.1822 | -0.10071 | -0.036621 | -0.036621 | 0 | -0.009155 | 0.10529 | -0.14648 | 0.14191 | -0.10986 | 0.32044 | 123.1613 | 0.027466 | 123.1293 | 123.2574 | 123.0927 | 123.1018 | 123.056 | -123.2483 | -123.1293 | 123.0057 | 123.0927 | 59.761 | 59.6008
252.8594 | 123.2071 | -59.9213 | 63.1348 | -0.14801 | 0.0023563 | 0.065213 | 0.063305 | 0.0034991 | -0.0018799 | -0.0021298 | -0.057281 | 0.00098899 | 0.07217 | 0.062184 | -0.004328 | 0.0056846 | -0.00057046 | -0.23346 | 63.1668 | -60.1318 | 63.0249 | -59.8572 | -60.2234 | 0.013733 | -0.44403 | 63.1302 | -59.9762 | 63.1622 | -59.9808 | -60.1089 | -59.8068 | -0.21057 | 0.032043 | -0.10986 | 0.064087 | 59.935 | -0.30212 | 60.1456 | -0.091553 | -0.054931 | -0.004578 | 0.027465 | -0.059509 | 0.11444 | -0.18768 | 0.16937 | -0.13275 | 0.27466 | 123.1567 | -0.004578 | 123.1384 | 123.2986 | 123.1064 | 123.0881 | 123.0515 | -123.2666 | -123.111 | 122.9462 | 123.0835 | 59.6878 | 59.4772
253.8906 | 123.1613 | -59.9167 | 63.1805 | -0.064087 | 0.0044925 | 0.064358 | 0.066082 | -0.0012005 | -0.0016663 | 0.0012882 | -0.045074 | 0.00034819 | 0.070889 | 0.073506 | -0.0064642 | 0.0054708 | 0.00071134 | -0.18768 | 63.1943 | -60.0952 | 63.0249 | -59.8709 | -60.228 | 0.032043 | -0.90637 | 63.0707 | -60.0174 | 63.1302 | -59.9854 | -60.0998 | -59.8206 | -0.17853 | 0.013733 | -0.15564 | 0.045776 | 59.9487 | -0.31128 | 60.1273 | -0.13275 | -0.10071 | -0.10986 | -0.050354 | -0.068665 | 0.09613 | -0.1831 | 0.19684 | -0.082397 | 0.2243 | 123.1201 | 0.032043 | 123.1476 | 123.2895 | 123.0881 | 123.111 | 122.9874 | -123.2758 | -123.1979 | 122.9416 | 123.0469 | 59.729 | 59.0103
254.8594 | 123.1705 | -59.9396 | 63.1668 | -0.079346 | -0.0034115 | 0.067563 | 0.066723 | -0.00034607 | -0.00081187 | -0.00084817 | -0.07254 | 0.0029116 | 0.070675 | 0.065602 | -0.0053962 | 0.0061118 | -0.0027067 | -0.59052 | 63.0981 | -60.173 | 62.9974 | -59.8984 | -60.2005 | 0.027466 | -0.41199 | 63.1577 | -59.9899 | 63.1531 | -59.9854 | -60.0952 | -59.8343 | -0.23346 | -0.068664 | -0.16937 | 0.041199 | 59.967 | -0.26093 | 60.2005 | -0.027465 | -0.050354 | -0.009155 | -0.013733 | -0.045777 | 0.10528 | -0.15564 | 0.15564 | -0.10529 | 0.27466 | 123.1705 | 0.004577 | 123.143 | 123.2712 | 123.1476 | 123.0377 | 123.0972 | -123.3398 | -123.1567 | 122.937 | 123.0927 | 59.3491 | 59.5276
255.8906 | 123.262 | -59.8938 | 63.1256 | -0.071716 | 0.0015019 | 0.062222 | 0.063732 | 0.0022173 | -0.0016663 | -0.001489 | 0.03122 | 0.0020572 | 0.068753 | 0.061756 | -0.0053962 | 0.00483 | 0.0013521 | -0.1831 | 63.121 | -60.0632 | 63.1165 | -59.7015 | -60.1501 | 0.11444 | -0.32044 | 63.0936 | -59.9716 | 63.2126 | -59.8801 | -59.9899 | -59.7565 | -0.16937 | -0.004577 | -0.009155 | 0.19226 | 60.0082 | -0.25635 | 60.1776 | -0.086975 | -0.07782 | -0.032043 | 0.086975 | 0.013733 | 0.13733 | -0.09613 | 0.21515 | -0.01831 | 0.36163 | 123.1796 | 0.091553 | 123.1842 | 123.1842 | 123.0652 | 123.0148 | 122.9874 | -123.1888 | -123.0972 | 123.0103 | 123.1064 | 59.7107 | 59.5734
256.8594 | 123.1842 | -59.935 | 63.176 | 0.019837 | -0.00020714 | 0.065854 | 0.06715 | -0.0029095 | -0.00038447 | -0.0017026 | -0.063385 | 0.0031254 | 0.068753 | 0.066883 | -0.0051824 | 0.0052572 | 0.0015659 | -0.19684 | 63.1897 | -60.0998 | 63.0341 | -59.8938 | -60.228 | 0.018311 | -0.42114 | 63.1393 | -59.9762 | 63.1439 | -60.0037 | -60.0998 | -59.8434 | -0.16479 | 0.013733 | -0.14191 | 0.041199 | 59.9533 | -0.29297 | 60.1181 | -0.12817 | -0.041198 | -0.036621 | -0.032043 | -0.068664 | 0.091553 | -0.16479 | 0.13275 | -0.1236 | 0.20599 | 123.1338 | -0.027466 | 123.1201 | 123.2895 | 123.1155 | 123.1247 | 123.0743 | -123.2758 | -123.1522 | 122.9691 | 123.0789 | 59.7382 | 59.5139
257.8906 | 123.2483 | -59.8938 | 63.1531 | 0.0045776 | 0.0034245 | 0.062222 | 0.067577 | 0.00029473 | -0.0018799 | -0.0051206 | -0.029816 | 0.0054752 | 0.069821 | 0.061329 | -0.0049688 | 0.0058982 | -0.00078406 | -0.11444 | 63.2172 | -60.0677 | 63.1073 | -59.7519 | -60.1227 | 0.15106 | -0.48523 | 63.1577 | -59.9579 | 63.2126 | -59.8755 | -60.0174 | -59.7702 | -0.17395 | 0.064087 | -0.045776 | 0.14191 | 60.0449 | -0.22888 | 60.2188 | -0.054932 | -0.064087 | 0.004578 | 0.059509 | 0.018311 | 0.1236 | -0.1236 | 0.18768 | -0.059509 | 0.31586 | 123.175 | 0.082398 | 123.1705 | 123.2849 | 123.1155 | 123.111 | 123.0515 | -123.2208 | -123.111 | 123.0011 | 123.1064 | 59.7794 | 59.4086
258.8594 | 123.2574 | -59.9075 | 63.1531 | -0.033569 | 0.0019291 | 0.06329 | 0.066296 | 0.0013629 | -0.00081187 | 0.00022003 | -0.051178 | 0.00098899 | 0.070461 | 0.069233 | -0.006037 | 0.00483 | 0.0022067 | -0.2243 | 63.1668 | -60.0952 | 63.0157 | -59.8343 | -60.2234 | 0 | -0.40741 | 63.1027 | -59.9716 | 63.176 | -59.9533 | -60.0906 | -59.8022 | -0.18768 | 0.013733 | -0.13733 | 0.073242 | 59.9075 | -0.31586 | 60.0952 | -0.12817 | -0.064087 | -0.050354 | 0.022888 | -0.045776 | 0.10529 | -0.1831 | 0.16937 | -0.11902 | 0.26093 | 123.111 | 0.018311 | 123.1476 | 123.262 | 123.0743 | 123.0743 | 123.0103 | -123.2483 | -123.1247 | 122.9233 | 123.0835 | 59.6832 | 59.5001
259.8906 | 123.1979 | -59.9258 | 63.1622 | -0.048828 | 0.0015019 | 0.065213 | 0.069714 | -0.00077327 | -0.0016663 | -0.0027708 | -0.078644 | 0.0024844 | 0.06918 | 0.062824 | -0.0045416 | 0.0061118 | -0.0016385 | -0.21515 | 63.208 | -60.1089 | 63.208 | -60.0403 | -60.1639 | 0.091553 | -0.38452 | 63.1714 | -59.967 | 63.1531 | -59.9854 | -60.1318 | -59.8343 | -0.18311 | 0.045777 | 0.045777 | -0.11444 | 60.0174 | -0.23804 | 60.2005 | -0.054931 | -0.041199 | 0.009156 | -0.009155 | -0.05951 | 0.091552 | -0.20599 | 0.13275 | -0.16479 | 0.068665 | 123.317 | -0.018311 | 123.1201 | 123.317 | 123.1384 | 123.1338 | 123.0972 | -123.2712 | -123.1293 | 123.1338 | 123.0789 | 59.7107 | 59.5413
260.8594 | 123.3124 | -59.8755 | 63.1073 | -0.11749 | 0.0021427 | 0.061581 | 0.065655 | -0.0031231 | 0.00089713 | -0.0012754 | -0.035919 | 0.002698 | 0.069821 | 0.06432 | -0.0049688 | 0.009957 | -0.00057046 | -0.19226 | 63.1393 | -60.1181 | 63.1119 | -59.7473 | -60.1135 | 0.064087 | -0.30212 | 63.0844 | -59.9625 | 63.1989 | -59.6558 | -59.9258 | -59.7382 | -0.24262 | 0.032043 | 0.004577 | 0.12817 | 59.9396 | -0.23804 | 60.1822 | 0.004578 | -0.086975 | -0.022888 | 0.091553 | 0.21973 | 0.13733 | -0.050354 | 0.2243 | 0.036621 | 0.37079 | 123.23 | 0.3067 | 123.1613 | 123.2574 | 123.0469 | 123.0148 | 122.9599 | -123.2254 | -123.0698 | 122.9874 | 123.0743 | 59.6832 | 59.5734
261.9062 | 123.2803 | -59.8846 | 63.1531 | -0.094604 | 0.0015019 | 0.063076 | 0.064159 | -0.00077327 | -0.0023071 | 6.432e-06 | 0.015961 | 0.0012028 | 0.068753 | 0.059406 | -0.0045416 | 0.0067526 | 0.00071134 | -0.18768 | 63.1668 | -60.0677 | 63.1073 | -59.761 | -60.1181 | 0.068665 | -0.34332 | 63.1165 | -59.9487 | 63.2034 | -59.8892 | -59.9762 | -59.7519 | -0.1831 | 0.013733 | -0.045776 | 0.1236 | 59.9533 | -0.23346 | 60.1364 | -0.050354 | -0.064086 | -0.036621 | 0.050354 | -0.004577 | 0.13275 | -0.091552 | 0.19684 | -0.027466 | 0.3067 | 123.175 | 0.059509 | 123.1522 | 123.2346 | 123.0652 | 123.0515 | 123.0011 | -123.2208 | -123.1018 | 122.9919 | 123.0881 | 59.697 | 59.5413
262.8594 | 123.1934 | -59.9213 | 63.1622 | -0.086975 | 0.0021427 | 0.062436 | 0.067791 | 0.0020037 | 0.00046993 | -0.0010618 | -0.069489 | 0.0022708 | 0.068753 | 0.067738 | -0.0062506 | 0.0069662 | -0.0022793 | -0.14648 | 63.2034 | -60.0952 | 63.0295 | -59.8801 | -60.2325 | -0.004578 | -0.42114 | 63.1577 | -59.9716 | 63.1485 | -59.9991 | -60.1135 | -59.816 | -0.17395 | 0.041199 | -0.13275 | 0.041199 | 59.9167 | -0.31128 | 60.0906 | -0.13733 | -0.050354 | -0.004577 | -0.013732 | -0.077819 | 0.10529 | -0.19226 | 0.15564 | -0.14191 | 0.21515 | 123.1247 | -0.027465 | 123.1201 | 123.2986 | 123.1293 | 123.1247 | 123.0789 | -123.2574 | -123.1338 | 122.9507 | 123.0698 | 59.7748 | 59.5001
263.8906 | 123.2025 | -59.9258 | 63.1577 | -0.0030519 | 0.0023563 | 0.062222 | 0.066723 | 0.0030719 | -0.0033753 | 0.0021426 | -0.051178 | 0.0041934 | 0.070889 | 0.071797 | -0.0058234 | 0.0046164 | -0.0027067 | -0.21057 | 63.2034 | -60.1044 | 63.0157 | -59.8526 | -60.2371 | -0.018311 | -0.4303 | 63.121 | -59.9716 | 63.1622 | -59.9762 | -60.0861 | -59.8114 | -0.17853 | 0.045776 | -0.14191 | 0.073242 | 59.9075 | -0.31128 | 60.0861 | -0.13275 | -0.045777 | -0.036621 | 0.004577 | -0.050354 | 0.11444 | -0.16022 | 0.16022 | -0.11444 | 0.25177 | 123.1201 | -0.004577 | 123.1338 | 123.3078 | 123.0927 | 123.1293 | 123.0469 | -123.262 | -123.1293 | 122.9416 | 123.0881 | 59.7153 | 59.4955
264.875 | 123.2666 | -59.8526 | 63.1989 | -0.064087 | 0.0012881 | 0.065213 | 0.062878 | 0.00093573 | 0.00068353 | -0.00020717 | 0.012909 | 0.00098899 | 0.068325 | 0.056202 | -0.0041144 | 0.0035482 | -0.0014249 | -0.07782 | 63.1714 | -60.0174 | 63.1943 | -59.6649 | -60.0266 | 0.19684 | -0.15106 | 63.1485 | -59.903 | 63.2538 | -59.8206 | -59.9075 | -59.697 | -0.16479 | -0.027466 | -0.004578 | 0.18768 | 60.0494 | -0.17395 | 60.2142 | -0.009155 | -0.050354 | -0.050354 | 0.054931 | 0.032043 | 0.15564 | -0.054932 | 0.20599 | -0.004578 | 0.35248 | 123.2117 | 0.082397 | 123.1567 | 123.1888 | 123.0515 | 123.024 | 123.0011 | -123.2162 | -123.1018 | 123.0469 | 123.1064 | 59.7748 | 59.7015
265.8906 | 123.3307 | -59.8801 | 63.1531 | -0.079346 | 0.0015019 | 0.062436 | 0.067791 | 0.0024311 | -0.00059807 | 0.00086083 | -0.035919 | 0.004407 | 0.067044 | 0.062397 | -0.0058234 | 0.0063254 | 0.00049774 | -0.21515 | 63.1439 | -60.1044 | 63.0844 | -59.7794 | -60.1685 | 0.009155 | -0.3479 | 63.1119 | -59.9487 | 63.2492 | -59.8938 | -60.0174 | -59.7198 | -0.2243 | -0.009155 | -0.068664 | 0.10071 | 59.8892 | -0.28839 | 60.1135 | -0.064087 | -0.068664 | -0.041199 | 0.096131 | -0.013733 | 0.16022 | -0.13733 | 0.22888 | -0.068665 | 0.32501 | 123.1888 | 0.054931 | 123.1979 | 123.2483 | 123.0606 | 123.024 | 122.9919 | -123.2574 | -123.1018 | 122.9645 | 123.1293 | 59.6649 | 59.5322
266.8594 | 123.3124 | -59.8892 | 63.1256 | -0.13275 | 0.0029971 | 0.065426 | 0.066082 | -0.0014143 | -0.0012391 | 6.432e-06 | -0.035919 | 0.0037662 | 0.067898 | 0.064533 | -0.0066778 | 0.001412 | -0.0018521 | -0.16479 | 63.121 | -60.0677 | 63.1439 | -59.7107 | -60.0998 | 0.064087 | -0.29297 | 63.1073 | -59.9533 | 63.2721 | -59.8526 | -59.9579 | -59.7061 | -0.17853 | -0.004577 | 0.018311 | 0.17853 | 59.9533 | -0.21057 | 60.1318 | -0.032043 | -0.064087 | -0.01831 | 0.14648 | 0.036621 | 0.1831 | -0.068665 | 0.24719 | -0.004578 | 0.35706 | 123.2117 | 0.10071 | 123.2254 | 123.1888 | 123.0606 | 123.0103 | 122.9965 | -123.1934 | -123.0789 | 123.0331 | 123.1613 | 59.7244 | 59.5963
267.8906 | 123.2254 | -59.8846 | 63.1897 | -0.041199 | -0.00042094 | 0.065213 | 0.067577 | -0.00013247 | 0.0013245 | -0.00063437 | -0.048126 | -7.901e-05 | 0.06918 | 0.06966 | -0.0039008 | 0.0050436 | -0.0012113 | -0.13275 | 63.1989 | -60.0586 | 63.121 | -59.7565 | -60.1364 | 0.07782 | -0.27466 | 63.1577 | -59.9487 | 63.2034 | -59.9121 | -60.0494 | -59.7748 | -0.17395 | 0.009156 | -0.068664 | 0.12817 | 59.9625 | -0.25177 | 60.1364 | -0.07782 | -0.064086 | -0.032043 | 0.013733 | -0.027465 | 0.10986 | -0.16479 | 0.17395 | -0.10071 | 0.30212 | 123.1796 | 0.036621 | 123.1522 | 123.2574 | 123.1064 | 123.0835 | 123.0423 | -123.2483 | -123.1384 | 123.0057 | 123.0881 | 59.7519 | 59.61
268.8594 | 123.2849 | -59.8618 | 63.1485 | -0.079346 | -0.00063454 | 0.064145 | 0.06715 | -0.00055967 | -0.00017087 | -0.00020717 | -0.035919 | 0.0014164 | 0.069393 | 0.068592 | -0.0066778 | 0.0018394 | -0.00078406 | -0.20142 | 63.1714 | -60.1044 | 63.1348 | -59.7153 | -60.1227 | 0.059509 | -0.31586 | 63.1302 | -59.967 | 63.382 | -59.9442 | -59.9533 | -59.7015 | -0.24262 | 0.022888 | -0.013733 | 0.14648 | 59.9213 | -0.26093 | 60.1639 | -0.018311 | -0.10529 | -0.018311 | 0.23346 | -0.082398 | 0.16022 | -0.091553 | 0.2655 | 0.013733 | 0.3891 | 123.2391 | 0.022888 | 123.349 | 123.2758 | 123.0972 | 123.0331 | 122.9919 | -123.2529 | -123.1155 | 122.9965 | 123.2437 | 59.6603 | 59.5459
269.9062 | 123.1842 | -59.8846 | 63.2126 | -0.01831 | -0.00063454 | 0.062222 | 0.066723 | -0.00077327 | -0.0033753 | -0.002557 | -0.029816 | 0.0024844 | 0.068539 | 0.064533 | -0.0056098 | 0.0071798 | 0.00028414 | -0.13275 | 63.2401 | -60.0449 | 63.0844 | -59.7794 | -60.1547 | 0.10071 | -0.27924 | 63.1897 | -59.9167 | 63.1897 | -59.903 | -60.0174 | -59.7748 | -0.16022 | 0.027466 | -0.12817 | 0.10529 | 59.9854 | -0.27008 | 60.1456 | -0.10986 | -0.032043 | -0.022888 | -0.022888 | -0.01831 | 0.10986 | -0.13275 | 0.14191 | -0.10071 | 0.2655 | 123.1293 | 0.013733 | 123.1064 | 123.2849 | 123.1064 | 123.1247 | 123.0743 | -123.2574 | -123.1293 | 122.9691 | 123.0743 | 59.7519 | 59.6054
270.8594 | 123.2346 | -59.9075 | 63.1668 | -0.079346 | 0.0025699 | 0.062863 | 0.066296 | 0.0017901 | -0.00081187 | -0.00084817 | -0.042023 | 0.0014164 | 0.069821 | 0.067097 | -0.0064642 | 0.0046164 | -0.0018521 | -0.21515 | 63.1897 | -60.1089 | 63.0432 | -59.8343 | -60.2188 | -0.036621 | -0.41199 | 63.1256 | -59.9442 | 63.1805 | -59.9167 | -60.0769 | -59.7839 | -0.20142 | 0.022888 | -0.1236 | 0.073242 | 59.8709 | -0.31128 | 60.0723 | -0.10986 | -0.036621 | -0.041199 | 0.013733 | -0.009155 | 0.1236 | -0.16937 | 0.16022 | -0.13275 | 0.27466 | 123.1522 | 0.027466 | 123.1247 | 123.2986 | 123.0698 | 123.0972 | 123.0331 | -123.2758 | -123.111 | 122.9507 | 123.0881 | 59.6924 | 59.4955
271.9062 | 123.3124 | -59.8389 | 63.176 | -0.041199 | 0.0015019 | 0.063076 | 0.064159 | 0.00050853 | 0.0026061 | -0.0019162 | 0.04953 | 0.0029116 | 0.067257 | 0.060475 | -0.0051824 | 0.003762 | -0.0029203 | -0.09613 | 63.2126 | -60.0266 | 63.1851 | -59.6283 | -60.0174 | 0.17853 | -0.13275 | 63.1302 | -59.903 | 63.2996 | -59.7656 | -59.8846 | -59.6695 | -0.18768 | 0.036621 | 0.009156 | 0.21057 | 60.0174 | -0.17853 | 60.2051 | 0.009155 | -0.064087 | -0.045776 | 0.1236 | 0.073242 | 0.16937 | -0.045777 | 0.23346 | 0.01831 | 0.39825 | 123.2117 | 0.13733 | 123.2025 | 123.2391 | 123.0331 | 123.0515 | 122.9691 | -123.2025 | -123.0789 | 123.024 | 123.1384 | 59.7427 | 59.7061
272.8594 | 123.3078 | -59.8801 | 63.1348 | -0.14038 | 0.0036381 | 0.060513 | 0.065014 | 0.0011493 | 0.0015381 | 0.001929 | -0.035919 | 0.0022708 | 0.071316 | 0.06966 | -0.0041144 | 0.0056846 | -0.0039883 | -0.11902 | 63.1668 | -60.0586 | 63.1485 | -59.6924 | -60.0906 | 0.050354 | -0.29755 | 63.0936 | -59.9213 | 63.2904 | -59.8297 | -59.9762 | -59.6741 | -0.17853 | 0.032043 | 0.013733 | 0.18768 | 59.9304 | -0.21057 | 60.1089 | -0.032043 | -0.041199 | -0.041199 | 0.15564 | 0.050354 | 0.20599 | -0.09613 | 0.24719 | -0.054931 | 0.36621 | 123.2071 | 0.091553 | 123.2117 | 123.2254 | 123.0148 | 123.0469 | 122.9736 | -123.1934 | -123.056 | 123.0286 | 123.1705 | 59.761 | 59.5825
273.8906 | 123.1796 | -59.8892 | 63.2172 | -0.086975 | 0.0032107 | 0.064999 | 0.066723 | 0.0013629 | 0.00089713 | 0.0021426 | -0.063385 | 0.00034819 | 0.069821 | 0.062611 | -0.0066778 | 0.0078208 | -0.0029203 | -0.16479 | 63.208 | -60.1044 | 63.0661 | -59.8297 | -60.2234 | -0.036621 | -0.41657 | 63.1577 | -59.9808 | 63.0661 | -59.8206 | -60.0906 | -59.8618 | -0.21515 | -0.009155 | -0.15106 | 0.059509 | 59.8526 | -0.33417 | 60.0677 | -0.11902 | -0.091553 | -0.059509 | -0.15106 | 0.068664 | 0.027466 | -0.20142 | 0.11902 | -0.10986 | 0.27466 | 123.1705 | 0.16022 | 123.0469 | 123.3124 | 123.1384 | 123.0972 | 123.0469 | -123.3215 | -123.1979 | 122.9553 | 122.9553 | 59.7244 | 59.4727
274.875 | 123.317 | -59.8206 | 63.176 | -0.041199 | 0.00022006 | 0.062863 | 0.06245 | 0.00072213 | -0.0012391 | -0.0053342 | 0.034271 | 0.0024844 | 0.069393 | 0.064106 | -0.0030462 | 0.003121 | -0.00078406 | -0.054932 | 63.176 | -60.0311 | 63.2034 | -59.6283 | -60.022 | 0.18768 | -0.14648 | 63.1393 | -59.9075 | 63.3087 | -59.7839 | -59.8846 | -59.6603 | -0.21057 | 0 | 0.027466 | 0.19226 | 60.0082 | -0.20142 | 60.2188 | 0.009155 | -0.086975 | -0.036621 | 0.13275 | 0.036621 | 0.16022 | -0.064087 | 0.24719 | 0.022888 | 0.40283 | 123.2346 | 0.1236 | 123.2162 | 123.2071 | 123.0469 | 122.9965 | 122.9599 | -123.2071 | -123.0835 | 123.024 | 123.1293 | 59.7656 | 59.6741
275.8906 | 123.2391 | -59.8618 | 63.2034 | -0.086975 | 0.0010745 | 0.06329 | 0.067577 | 0.0037127 | -0.0027345 | -0.0010618 | -0.075592 | 0.0024844 | 0.069821 | 0.06432 | -0.006037 | 0.0069662 | 0.00028414 | -0.064087 | 63.1943 | -60.054 | 63.1714 | -59.6924 | -60.1089 | 0.10071 | -0.21973 | 63.1851 | -59.9304 | 63.2401 | -59.8572 | -60.0082 | -59.7427 | -0.19226 | -0.009155 | -0.032043 | 0.16937 | 59.9625 | -0.24719 | 60.1547 | -0.054932 | -0.068665 | -0.01831 | 0.036621 | 0.004577 | 0.11902 | -0.14648 | 0.18768 | -0.07782 | 0.36163 | 123.2254 | 0.073242 | 123.1705 | 123.2483 | 123.1155 | 123.056 | 123.0469 | -123.2574 | -123.1338 | 123.0331 | 123.1018 | 59.7977 | 59.642
276.8594 | 123.2849 | -59.848 | 63.1485 | -0.13275 | 0.00043366 | 0.06329 | 0.0648 | -0.00055967 | -0.0038025 | -0.001489 | -0.051178 | 0.0024844 | 0.073239 | 0.064106 | -0.0047552 | 0.0056846 | 0.0026339 | -0.19226 | 63.1714 | -60.0815 | 63.1393 | -59.761 | -60.1181 | 0.059509 | -0.53558 | 63.0661 | -59.9533 | 63.3041 | -59.8663 | -59.9945 | -59.697 | -0.23346 | 0.022888 | -0.009156 | 0.086975 | 59.9075 | -0.27008 | 60.141 | -0.036621 | -0.10529 | -0.082398 | 0.15564 | -0.018311 | 0.15106 | -0.14648 | 0.25635 | -0.041199 | 0.32044 | 123.2208 | 0.086975 | 123.2574 | 123.2529 | 123.0194 | 123.0194 | 122.9141 | -123.23 | -123.1018 | 122.9874 | 123.1522 | 59.6558 | 59.3124
277.8906 | 123.1888 | -59.8892 | 63.1622 | -0.056457 | 0.0027835 | 0.064999 | 0.067364 | 0.0024311 | 0.0013245 | -0.001489 | -0.066437 | 0.0022708 | 0.070034 | 0.075855 | -0.0053962 | 0.0080344 | -0.0024931 | -0.21057 | 63.1897 | -60.1089 | 63.0386 | -59.8297 | -60.2188 | -0.032043 | -0.43488 | 63.1577 | -59.9533 | 63.176 | -59.9487 | -60.0632 | -59.7794 | -0.21973 | 0.027466 | -0.1236 | 0.059509 | 59.8572 | -0.32959 | 60.0769 | -0.10986 | -0.064087 | -0.004577 | 0.013733 | -0.059509 | 0.10986 | -0.17395 | 0.17395 | -0.10986 | 0.27924 | 123.1476 | 0.004578 | 123.1293 | 123.2986 | 123.111 | 123.0789 | 123.0469 | -123.2712 | -123.1155 | 122.9279 | 123.0652 | 59.6786 | 59.4543
278.8594 | 123.2803 | -59.8618 | 63.1256 | -0.10223 | 0.0019291 | 0.063931 | 0.0648 | -0.00034607 | 0.00089713 | -0.0038388 | -0.017609 | 0.0018436 | 0.067684 | 0.065815 | -0.0041144 | 0.0039756 | -0.0014249 | -0.15106 | 63.176 | -60.0449 | 63.1668 | -59.6924 | -60.0861 | 0.064087 | -0.29755 | 63.1165 | -59.9258 | 63.2675 | -59.8663 | -59.9533 | -59.7061 | -0.18311 | 0.050354 | 0.041199 | 0.16937 | 59.9258 | -0.22431 | 60.1089 | -0.041199 | -0.064087 | -0.009155 | 0.14191 | -0.004578 | 0.15564 | -0.091553 | 0.21973 | -0.027466 | 0.35248 | 123.2117 | 0.059509 | 123.1934 | 123.2208 | 123.0423 | 123.0377 | 122.9782 | -123.1705 | -123.0515 | 123.0286 | 123.1293 | 59.7107 | 59.5642
279.9062 | 123.3261 | -59.816 | 63.1668 | -0.048828 | 0.0010745 | 0.062649 | 0.066296 | -0.0020551 | -0.00038447 | -0.00020717 | 0.015961 | -0.00050621 | 0.067044 | 0.06432 | -0.0062506 | 0.0044028 | -0.0031339 | -0.1236 | 63.1943 | -60.0128 | 63.1989 | -59.6512 | -60.0494 | 0.14191 | -0.16937 | 63.1348 | -59.9075 | 63.295 | -59.7702 | -59.8663 | -59.6512 | -0.19684 | 0.027466 | 0.032044 | 0.16479 | 59.9579 | -0.23346 | 60.1547 | -0.036621 | -0.091553 | -0.032043 | 0.12817 | 0.045776 | 0.16479 | -0.050354 | 0.25635 | 0.041199 | 0.36163 | 123.2117 | 0.13733 | 123.2025 | 123.2071 | 123.0423 | 123.0103 | 122.9507 | -123.1796 | -123.0743 | 123.0148 | 123.111 | 59.6924 | 59.6466
280.8594 | 123.3215 | -59.8618 | 63.1393 | -0.086975 | 6.46e-06 | 0.064785 | 0.0695 | 8.1126e-05 | -0.0025207 | -0.00020717 | -0.066437 | 0.0020572 | 0.067898 | 0.061329 | -0.009455 | 0.0056846 | -0.00057046 | -0.15564 | 63.1348 | -60.0632 | 63.2629 | -59.761 | -60.054 | 0.064087 | -0.27008 | 63.121 | -59.9121 | 63.2767 | -59.8434 | -59.9625 | -59.6786 | -0.20142 | -0.004577 | 0.1236 | 0.10071 | 59.9258 | -0.19226 | 60.1273 | 0.009155 | -0.050354 | -0.01831 | 0.13733 | 0.01831 | 0.18311 | -0.10071 | 0.23346 | -0.050354 | 0.30212 | 123.3261 | 0.068664 | 123.1888 | 123.1979 | 123.0331 | 122.9965 | 122.9828 | -123.2025 | -123.0515 | 123.1247 | 123.1384 | 59.7061 | 59.5917
281.8906 | 123.2529 | -59.8618 | 63.1805 | -0.071716 | 0.0027835 | 0.063931 | 0.064587 | 8.1126e-05 | -0.0023071 | -0.003198 | 0.0037536 | 0.00098899 | 0.068325 | 0.060902 | -0.0030462 | 0.0039756 | -0.0014249 | -0.19684 | 63.1622 | -60.0494 | 63.1165 | -59.7519 | -60.1135 | 0.050354 | -0.33417 | 63.1439 | -59.935 | 63.2355 | -59.8709 | -59.9762 | -59.7336 | -0.18768 | -0.018311 | -0.064087 | 0.10986 | 59.9121 | -0.25177 | 60.0998 | -0.064087 | -0.073243 | -0.036621 | 0.054932 | -0.009156 | 0.12817 | -0.11444 | 0.20142 | -0.041198 | 0.29755 | 123.1659 | 0.064087 | 123.1705 | 123.2117 | 123.0789 | 123.024 | 123.0057 | -123.23 | -123.1155 | 122.9782 | 123.0972 | 59.6649 | 59.5276
282.8594 | 123.317 | -59.8434 | 63.1393 | -0.071716 | 0.0010745 | 0.063504 | 0.064373 | 0.0030719 | -0.00081187 | 0.00043363 | -0.093903 | 0.0037662 | 0.06918 | 0.06966 | -0.0041144 | 0.0058982 | -0.0044157 | -0.15564 | 63.176 | -60.0677 | 63.1302 | -59.7565 | -60.0815 | 0.022888 | -0.52643 | 63.0753 | -59.935 | 63.3041 | -59.848 | -59.9258 | -59.6512 | -0.2243 | 0.036621 | -0.009155 | 0.086975 | 59.8663 | -0.23804 | 60.0906 | -0.013733 | -0.091553 | -0.064087 | 0.1648 | -0.004577 | 0.19226 | -0.082397 | 0.28381 | 0.009156 | 0.31128 | 123.1979 | 0.086976 | 123.2391 | 123.2437 | 123.0103 | 123.0194 | 122.9187 | -123.2071 | -123.0743 | 122.9736 | 123.1476 | 59.6878 | 59.317
283.9062 | 123.2986 | -59.848 | 63.1577 | -0.071716 | 0.0023563 | 0.061367 | 0.065228 | 0.00072213 | -0.0033753 | 0.001929 | -0.029816 | 0.00056179 | 0.070461 | 0.058979 | -0.0056098 | 0.0054708 | -0.0012113 | -0.19226 | 63.1851 | -60.0723 | 63.1348 | -59.7244 | -60.1227 | 0.018311 | -0.35248 | 63.121 | -59.9304 | 63.2172 | -59.642 | -60.0403 | -59.8755 | -0.22431 | 0.027466 | -0.022888 | 0.1236 | 59.8663 | -0.27466 | 60.0906 | -0.050354 | -0.082398 | -0.036621 | 0.059509 | 0.20599 | -0.027466 | -0.19226 | 0.054932 | -0.10986 | 0.3479 | 123.2071 | 0.28839 | 123.1476 | 123.2574 | 123.0515 | 123.0331 | 122.9691 | -123.23 | -123.0881 | 122.9828 | 123.0652 | 59.6558 | 59.4955
284.875 | 123.3078 | -59.8526 | 63.1622 | -0.071716 | 0.0010745 | 0.062008 | 0.065228 | -0.00098687 | -0.0029481 | -0.002557 | 0.012909 | 0.00077539 | 0.06683 | 0.063679 | -0.0047552 | 0.0035482 | 7.0538e-05 | -0.14648 | 63.1622 | -60.0494 | 63.1805 | -59.6832 | -60.0311 | 0.1236 | -0.20599 | 63.1622 | -59.9075 | 63.2812 | -59.8022 | -59.8984 | -59.6695 | -0.19684 | 0 | 0.018311 | 0.16937 | 59.9762 | -0.17853 | 60.173 | 0.01831 | -0.054932 | 0 | 0.11902 | 0.050354 | 0.18311 | -0.045776 | 0.23804 | 0.009156 | 0.36621 | 123.23 | 0.10529 | 123.1888 | 123.2117 | 123.0698 | 123.0148 | 123.0148 | -123.2117 | -123.0698 | 123.0331 | 123.1338 | 59.7061 | 59.6466
285.8906 | 123.1842 | -59.9075 | 63.1805 | -0.10986 | 0.00064726 | 0.065213 | 0.068005 | 0.0011493 | 0.00046993 | 0.00022003 | -0.10611 | 0.0022708 | 0.07153 | 0.071369 | -0.0045416 | 0.0058982 | -0.00035666 | -0.20599 | 63.1943 | -60.0906 | 63.0524 | -59.848 | -60.1959 | -0.064087 | -0.42572 | 63.176 | -59.9487 | 63.1851 | -59.9579 | -60.0769 | -59.7931 | -0.1831 | 0.013733 | -0.12817 | 0.05951 | 59.8434 | -0.28839 | 60.0266 | -0.10529 | -0.041198 | -0.004578 | 0.004578 | -0.050354 | 0.11444 | -0.16937 | 0.15564 | -0.12817 | 0.24262 | 123.143 | -0.009156 | 123.1338 | 123.2849 | 123.1247 | 123.1018 | 123.0835 | -123.2712 | -123.1293 | 122.9599 | 123.0927 | 59.7015 | 59.4818
286.8594 | 123.2758 | -59.8618 | 63.1531 | -0.064087 | 0.0021427 | 0.062436 | 0.065655 | 0.0024311 | 0.00025633 | -0.0010618 | 0.019012 | 0.00077539 | 0.06918 | 0.069233 | -0.0049688 | 0.0039756 | -0.0024931 | -0.16937 | 63.1714 | -60.0449 | 63.1348 | -59.7565 | -60.1181 | 0.045776 | -0.33875 | 63.1485 | -59.9304 | 63.2538 | -59.848 | -59.9762 | -59.7107 | -0.18311 | 0.018311 | -0.01831 | 0.10529 | 59.9075 | -0.25635 | 60.0906 | -0.073242 | -0.068665 | -0.004577 | 0.10071 | 0.013733 | 0.15106 | -0.11444 | 0.21973 | -0.045776 | 0.28839 | 123.1796 | 0.082398 | 123.1842 | 123.2162 | 123.0789 | 123.0331 | 123.0103 | -123.1979 | -123.0835 | 122.9965 | 123.1155 | 59.6924 | 59.523
287.8906 | 123.3353 | -59.8618 | 63.1393 | -0.15564 | -0.00063454 | 0.062649 | 0.066082 | 0.0011493 | -0.0010255 | -0.0057614 | 0.022064 | 0.0035526 | 0.065548 | 0.06966 | -0.0045416 | 0.0063254 | -0.0020657 | -0.16022 | 63.1622 | -60.0632 | 63.1531 | -59.6558 | -60.4706 | -0.10529 | -0.36163 | 63.1073 | -59.8984 | 63.2904 | -59.8572 | -59.9213 | -59.6832 | -0.20142 | 0.022888 | 0.013733 | 0.20599 | 59.7565 | -0.60883 | 59.9579 | -0.40741 | -0.036621 | -0.032043 | 0.15106 | 0.004577 | 0.17853 | -0.05951 | 0.21515 | -0.022889 | 0.40741 | 123.2162 | 0.041198 | 123.1888 | 123.2254 | 123.0057 | 123.024 | 122.9691 | -123.2025 | -123.0377 | 123.0148 | 123.1522 | 59.7015 | 59.5001
288.8594 | 123.3398 | -59.848 | 63.1348 | -0.048828 | 0.0036381 | 0.06329 | 0.065655 | 0.0026447 | -0.0016663 | 0.0029972 | -0.051178 | 0.0029116 | 0.068539 | 0.068379 | -0.0053962 | 0.00483 | -0.0035611 | -0.17853 | 63.1485 | -60.0815 | 63.1668 | -59.6512 | -60.1364 | 0.018311 | -0.31128 | 63.1165 | -59.9304 | 63.2721 | -59.8251 | -59.9396 | -59.6695 | -0.23346 | 0.013733 | 0.032043 | 0.19684 | 59.8663 | -0.28839 | 60.0998 | -0.054932 | -0.082398 | -0.018311 | 0.13733 | 0.022888 | 0.17853 | -0.091553 | 0.26093 | -0.009155 | 0.4303 | 123.2483 | 0.10529 | 123.2025 | 123.23 | 123.0469 | 122.9965 | 122.9645 | -123.2162 | -123.0652 | 123.0148 | 123.1201 | 59.6695 | 59.5367
289.8906 | 123.2437 | -59.8572 | 63.1897 | -0.27771 | 0.0029971 | 0.062649 | 0.068432 | 0.0041399 | -0.00038447 | -0.0019162 | -0.093903 | 0.0018436 | 0.068325 | 0.067311 | -0.0034736 | 0.006539 | -0.0029203 | 0.041199 | 63.1989 | -60.1044 | 63.1531 | -59.7244 | -60.1318 | 0.068665 | -0.2243 | 63.176 | -59.9213 | 63.2492 | -59.848 | -59.9854 | -59.7107 | -0.24719 | 0.009156 | -0.036621 | 0.13275 | 59.9258 | -0.27466 | 60.173 | -0.027466 | -0.064087 | -0.013733 | 0.05951 | 0.009156 | 0.14648 | -0.12817 | 0.21057 | -0.064087 | 0.37994 | 123.2574 | 0.073243 | 123.1705 | 123.3032 | 123.0972 | 123.056 | 123.0331 | -123.2941 | -123.111 | 123.0103 | 123.1064 | 59.8984 | 59.6329
290.8594 | 123.262 | -59.8846 | 63.1485 | -0.079346 | 0.00064726 | 0.064145 | 0.068218 | 0.0015765 | 0.00068353 | 0.0015018 | -0.087799 | 0.0024844 | 0.071102 | 0.06966 | -0.0041144 | 0.0069662 | -0.0044157 | -0.2243 | 63.2034 | -60.1089 | 63.0661 | -59.7977 | -60.1913 | -0.059509 | -0.40741 | 63.1531 | -59.967 | 63.2217 | -59.8892 | -60.0174 | -59.7565 | -0.2243 | 0.054931 | -0.082398 | 0.086976 | 59.8251 | -0.3067 | 60.0494 | -0.082397 | -0.082397 | 0.004577 | 0.073242 | -0.004577 | 0.12817 | -0.13275 | 0.21057 | -0.050354 | 0.31128 | 123.175 | 0.07782 | 123.1888 | 123.3124 | 123.1201 | 123.0881 | 123.0377 | -123.2574 | -123.1155 | 122.9507 | 123.1064 | 59.6603 | 59.4772
291.8906 | 123.1888 | -59.9121 | 63.1714 | -0.62866 | 0.0038517 | 0.061154 | 0.066296 | 0.00050853 | -0.00059807 | -0.00042077 | -0.090851 | 0.00077539 | 0.069393 | 0.06667 | -0.0056098 | 0.0078208 | -0.00057046 | -0.032043 | 63.1851 | -60.1044 | 63.0295 | -59.7977 | -60.2554 | -0.068665 | -0.44861 | 63.1805 | -59.9579 | 63.1805 | -59.9808 | -60.0906 | -59.8114 | -0.19226 | 0.013733 | -0.14191 | 0.11444 | 59.8434 | -0.34332 | 60.0357 | -0.15106 | -0.045777 | 0.009155 | 0.009155 | -0.068665 | 0.10071 | -0.17853 | 0.14649 | -0.13275 | 0.3067 | 123.1338 | -0.022888 | 123.1384 | 123.2895 | 123.1384 | 123.0972 | 123.0927 | -123.2758 | -123.1293 | 122.9416 | 123.0927 | 59.8801 | 59.4635
292.8594 | 123.3078 | -59.8846 | 63.1393 | -0.048828 | 0.0021427 | 0.063931 | 0.065014 | -0.0016279 | -0.0012391 | 0.0021426 | -0.035919 | 0.003339 | 0.067044 | 0.06432 | -0.0058234 | 0.0044028 | -0.0042021 | -0.16937 | 63.1348 | -60.0357 | 63.1531 | -59.6878 | -60.0952 | 0.018311 | -0.29297 | 63.1027 | -59.935 | 63.2812 | -59.8206 | -59.9487 | -59.6741 | -0.15106 | -0.004577 | 0.013733 | 0.19684 | 59.903 | -0.21057 | 60.054 | -0.059509 | -0.050354 | -0.036621 | 0.14191 | 0.064087 | 0.21057 | -0.064086 | 0.26093 | -0.013732 | 0.3479 | 123.1888 | 0.11444 | 123.2162 | 123.1705 | 123.0377 | 123.0194 | 122.9874 | -123.175 | -123.0743 | 123.0377 | 123.1659 | 59.7153 | 59.5917
293.8906 | 123.317 | -59.8434 | 63.1302 | -0.20142 | 0.0032107 | 0.061795 | 0.065868 | 0.0013629 | 0.00025633 | 0.00064723 | -0.060333 | 0.00013459 | 0.068753 | 0.06432 | -0.0053962 | 0.0052572 | 0.0022067 | -0.091553 | 63.1393 | -60.0769 | 63.1577 | -59.6741 | -60.0861 | 0.013733 | -0.32044 | 63.1165 | -59.9396 | 63.295 | -59.8389 | -59.9579 | -59.6832 | -0.23346 | 0.009155 | 0.027466 | 0.16937 | 59.8572 | -0.24262 | 60.0906 | -0.009156 | -0.09613 | -0.013733 | 0.1648 | 0.004578 | 0.16022 | -0.11444 | 0.25635 | -0.018311 | 0.40283 | 123.2346 | 0.10071 | 123.2346 | 123.2162 | 123.056 | 122.9828 | 122.9599 | -123.2071 | -123.0698 | 123.0011 | 123.1384 | 59.7519 | 59.523
294.8594 | 123.3078 | -59.8709 | 63.1393 | -0.10223 | 0.0010745 | 0.064999 | 0.065228 | -0.0014143 | -0.0012391 | -0.0027708 | -0.038971 | 0.00163 | 0.070248 | 0.06966 | -0.006037 | 0.0054708 | -0.0022793 | -0.15106 | 63.1668 | -60.0449 | 63.1439 | -59.697 | -60.1089 | 0.027466 | -0.3067 | 63.0981 | -59.903 | 63.2904 | -59.8251 | -59.9396 | -59.6924 | -0.17395 | 0.027466 | 0.004578 | 0.17395 | 59.8984 | -0.23804 | 60.0723 | -0.064087 | -0.032043 | -0.041198 | 0.15106 | 0.045777 | 0.17853 | -0.068664 | 0.21057 | -0.036621 | 0.3479 | 123.1888 | 0.07782 | 123.1934 | 123.2117 | 123.0011 | 123.0377 | 122.9691 | -123.1842 | -123.0423 | 123.0148 | 123.1613 | 59.7198 | 59.5642
295.8906 | 123.2071 | -59.8846 | 63.1622 | -0.056457 | 0.0025699 | 0.064785 | 0.065441 | 0.0049945 | -0.0010255 | 0.0017154 | -0.096954 | 0.0031254 | 0.070248 | 0.070088 | -0.0058234 | 0.0076072 | -0.0012113 | -0.20142 | 63.1622 | -60.1089 | 63.0524 | -59.8206 | -60.2188 | -0.068665 | -0.43945 | 63.1622 | -59.9533 | 63.1805 | -59.967 | -60.0723 | -59.7931 | -0.2243 | 0 | -0.10986 | 0.064087 | 59.816 | -0.33417 | 60.0403 | -0.10986 | -0.068664 | 0 | 0.018311 | -0.082397 | 0.091553 | -0.18768 | 0.16022 | -0.11902 | 0.28839 | 123.1613 | -0.013733 | 123.1338 | 123.2712 | 123.1155 | 123.0469 | 123.0469 | -123.2712 | -123.1155 | 122.937 | 123.0652 | 59.6832 | 59.4452
296.8594 | 123.3032 | -59.8709 | 63.1485 | -0.094604 | 0.0012881 | 0.063076 | 0.0648 | 0.0024311 | -0.0033753 | -0.0040524 | 0.019012 | 0.0020572 | 0.070034 | 0.067951 | -0.0041144 | 0.003762 | -0.0022793 | -0.19226 | 63.1668 | -60.0586 | 63.1256 | -59.7336 | -60.1456 | 0.018311 | -0.35248 | 63.1119 | -59.9487 | 63.327 | -59.729 | -60.1227 | -59.7519 | -0.18768 | 0.01831 | -0.022889 | 0.13733 | 59.8892 | -0.27466 | 60.0769 | -0.086975 | -0.077819 | -0.036622 | 0.17853 | 0.14191 | 0.11902 | -0.25177 | 0.19684 | -0.17395 | 0.32501 | 123.1842 | 0.21973 | 123.2758 | 123.2254 | 123.0606 | 123.0377 | 122.9828 | -123.2071 | -123.0972 | 122.9965 | 123.1979 | 59.6786 | 59.5184
297.8906 | 123.1705 | -59.8755 | 63.1897 | -0.056457 | -0.00063454 | 0.063717 | 0.06715 | -0.00013247 | -0.0031617 | -0.0017026 | -0.11221 | 0.005048 | 0.067471 | 0.06902 | -0.0075324 | 0.0039756 | 0.0019931 | -0.1831 | 63.1805 | -60.0952 | 63.0707 | -59.8251 | -60.2005 | -0.064087 | -0.43945 | 63.1622 | -59.9579 | 63.1439 | -59.9762 | -59.9625 | -59.7931 | -0.21973 | -0.009155 | -0.11902 | 0.050354 | 59.8114 | -0.32501 | 60.0311 | -0.10528 | -0.082398 | -0.027466 | -0.045776 | -0.10071 | 0.082397 | -0.086975 | 0.1648 | -0.004577 | 0.27008 | 123.1659 | -0.01831 | 123.1018 | 123.2758 | 123.1201 | 123.056 | 123.0377 | -123.2849 | -123.1476 | 122.9462 | 123.0194 | 59.6924 | 59.436
298.8594 | 123.2986 | -59.8709 | 63.1027 | -0.14801 | 0.0015019 | 0.065426 | 0.065868 | -0.00013247 | 0.00089713 | -0.00084817 | -0.026764 | 0.0014164 | 0.068325 | 0.062397 | -0.0058234 | 0.0052572 | -0.0074063 | -0.15564 | 63.1577 | -60.1044 | 63.1393 | -59.6649 | -60.1135 | 0 | -0.33417 | 63.1119 | -59.9442 | 63.2858 | -59.8343 | -59.9213 | -59.6558 | -0.23346 | 0.054932 | 0.036621 | 0.20599 | 59.8709 | -0.24261 | 60.1044 | -0.009155 | -0.073242 | 0.009155 | 0.18311 | 0.036621 | 0.21515 | -0.050354 | 0.28839 | 0.022888 | 0.43945 | 123.2437 | 0.10986 | 123.23 | 123.262 | 123.056 | 123.0286 | 122.9828 | -123.2071 | -123.0469 | 123.0103 | 123.1567 | 59.7153 | 59.5367
299.8906 | 123.262 | -59.8801 | 63.1531 | -0.056457 | 0.0019291 | 0.063717 | 0.064159 | -0.00098687 | -0.0023071 | -0.00063437 | -0.090851 | 0.0018436 | 0.068753 | 0.068806 | -0.004328 | 0.0039756 | -0.0020657 | -0.23346 | 63.1805 | -60.1135 | 63.0569 | -59.8297 | -60.1959 | -0.068665 | -0.4303 | 63.1393 | -59.9716 | 63.1989 | -59.9258 | -60.0494 | -59.7839 | -0.23346 | 0.027466 | -0.09613 | 0.050354 | 59.8114 | -0.31586 | 60.0449 | -0.082398 | -0.091553 | -0.013733 | 0.045777 | -0.045776 | 0.09613 | -0.16937 | 0.18768 | -0.077819 | 0.28381 | 123.1705 | 0.045777 | 123.1705 | 123.2941 | 123.111 | 123.0606 | 123.0194 | -123.2666 | -123.1247 | 122.937 | 123.0789 | 59.6466 | 59.4498
300.8594 | 123.317 | -59.8663 | 63.1485 | -0.10223 | 0.0032107 | 0.061795 | 0.065655 | -0.00077327 | -0.00017087 | -0.0023434 | -0.029816 | 0.0024844 | 0.067471 | 0.064106 | -0.0034736 | 0.0073936 | 0.00028414 | -0.16022 | 63.1485 | -60.0723 | 63.1485 | -59.6878 | -60.0998 | 0.022888 | -0.32044 | 63.121 | -59.9258 | 63.2904 | -59.8206 | -59.9487 | -59.6878 | -0.20599 | 0 | 0 | 0.17853 | 59.8892 | -0.23346 | 60.0952 | -0.027465 | -0.059509 | -0.027466 | 0.14191 | 0.045776 | 0.17853 | -0.082397 | 0.23804 | -0.022888 | 0.38452 | 123.2208 | 0.10529 | 123.2162 | 123.2208 | 123.0469 | 123.0148 | 122.9874 | -123.2208 | -123.0743 | 123.0148 | 123.1567 | 59.7061 | 59.5459
301.8906 | 123.3078 | -59.8297 | 63.1577 | -0.01831 | 0.0017155 | 0.061154 | 0.065228 | -0.00098687 | 0.0017517 | -0.0021298 | 0.019012 | 0.0035526 | 0.069607 | 0.060902 | -0.0053962 | 0.0035482 | -0.0024931 | -0.15106 | 63.1897 | -60.0403 | 63.1302 | -59.7244 | -60.0906 | 0.068665 | -0.29297 | 63.1256 | -59.9213 | 63.2721 | -59.8251 | -59.9167 | -59.6832 | -0.21057 | 0.032043 | -0.027466 | 0.10529 | 59.8984 | -0.26093 | 60.1089 | -0.050354 | -0.091553 | -0.032044 | 0.11444 | 0.004578 | 0.14648 | -0.086975 | 0.23804 | 0.004578 | 0.31586 | 123.1705 | 0.096131 | 123.1934 | 123.23 | 123.0469 | 123.0194 | 122.9553 | -123.1979 | -123.0789 | 122.9599 | 123.1018 | 59.6786 | 59.5367
302.8594 | 123.317 | -59.8526 | 63.121 | -0.086975 | 0.0038517 | 0.063931 | 0.0648 | 0.0034991 | 0.0013245 | 0.0025698 | -0.038971 | 0.0022708 | 0.067684 | 0.070301 | -0.0068914 | 0.0052572 | -0.0018521 | -0.13733 | 63.1393 | -60.0952 | 63.1668 | -59.697 | -60.1135 | 0.013733 | -0.31128 | 63.1165 | -59.9487 | 63.2767 | -59.8434 | -59.9533 | -59.697 | -0.24262 | 0.01831 | 0.045776 | 0.15564 | 59.8663 | -0.26093 | 60.1089 | -0.01831 | -0.09613 | -0.004578 | 0.15564 | 0.009155 | 0.15564 | -0.10071 | 0.25177 | -0.004578 | 0.39826 | 123.262 | 0.10528 | 123.2254 | 123.2346 | 123.0652 | 122.9919 | 122.9691 | -123.2162 | -123.0698 | 123.0194 | 123.1293 | 59.7153 | 59.5413
303.9062 | 123.2895 | -59.8755 | 63.1119 | -0.10986 | 0.0019291 | 0.063931 | 0.065228 | 0.00029473 | 0.00046993 | -0.002557 | -0.023712 | 0.002698 | 0.071102 | 0.062397 | -0.0056098 | 0.0050436 | 0.0039157 | -0.1831 | 63.1622 | -60.0769 | 63.121 | -59.7153 | -60.1364 | 0.009155 | -0.36621 | 63.1256 | -59.9442 | 63.2446 | -59.8801 | -59.9762 | -59.7336 | -0.20142 | 0.050354 | 0.009156 | 0.16022 | 59.8846 | -0.26093 | 60.0861 | -0.05951 | -0.068665 | 0.013733 | 0.13275 | -0.004578 | 0.14191 | -0.10071 | 0.21057 | -0.032043 | 0.36163 | 123.1979 | 0.064087 | 123.1888 | 123.2391 | 123.0698 | 123.0377 | 123.0011 | -123.1888 | -123.056 | 122.9965 | 123.1201 | 59.6924 | 59.5093
304.8594 | 123.317 | -59.8343 | 63.1393 | -0.094604 | -0.00063454 | 0.067776 | 0.0648 | 0.0011493 | 0.00025633 | 0.00022003 | -0.051178 | 0.00077539 | 0.06918 | 0.068165 | -0.007105 | 0.0058982 | 0.00049774 | -0.35248 | 63.121 | -60.1135 | 63.1714 | -59.7244 | -60.1273 | 0.009155 | -0.31586 | 63.1302 | -59.9304 | 63.295 | -59.8343 | -59.9167 | -59.7061 | -0.27923 | -0.01831 | 0.032044 | 0.10986 | 59.8434 | -0.29297 | 60.1227 | -0.013733 | -0.09613 | -0.009155 | 0.15564 | 0 | 0.12817 | -0.082397 | 0.2243 | 0.013733 | 0.3891 | 123.2849 | 0.09613 | 123.2254 | 123.2346 | 123.0606 | 122.9553 | 122.9645 | -123.2529 | -123.0698 | 123.0057 | 123.1293 | 59.4818 | 59.5184
305.8906 | 123.2574 | -59.8709 | 63.1943 | -0.041199 | 0.0010745 | 0.06329 | 0.066937 | 0.00093573 | -0.00059807 | -0.0021298 | -0.057281 | 0.0035526 | 0.06918 | 0.060902 | -0.0053962 | 0.0067526 | -0.0044157 | -0.13733 | 63.2584 | -60.0723 | 63.1073 | -59.7565 | -60.1181 | 0.068665 | -0.27466 | 63.1989 | -59.9213 | 63.2263 | -59.8663 | -59.9945 | -59.7427 | -0.20142 | 0.064087 | -0.086975 | 0.11444 | 59.9396 | -0.24719 | 60.141 | -0.045776 | -0.050354 | 0.004578 | 0.032043 | 0.004578 | 0.12817 | -0.1236 | 0.17853 | -0.073242 | 0.31586 | 123.1796 | 0.054932 | 123.1476 | 123.3307 | 123.1201 | 123.1293 | 123.0698 | -123.2666 | -123.1155 | 122.9782 | 123.0972 | 59.7336 | 59.5963
306.8594 | 123.2895 | -59.8892 | 63.1531 | -0.079346 | 0.0019291 | 0.063504 | 0.067577 | 0.00072213 | -0.0012391 | -0.002557 | -0.0054016 | 0.00163 | 0.068753 | 0.066456 | -0.0051824 | 0.0069662 | -0.0033475 | -0.19684 | 63.1622 | -60.0494 | 63.1531 | -59.9487 | -60.022 | 0.009155 | -0.37537 | 63.1302 | -59.9487 | 63.2355 | -59.8755 | -59.9945 | -59.729 | -0.16022 | 0.009155 | 0 | -0.059509 | 59.8984 | -0.13275 | 60.0586 | 0.027465 | -0.059509 | -0.022888 | 0.082398 | 0.013733 | 0.16022 | -0.10529 | 0.21973 | -0.045777 | 0.10071 | 123.2025 | 0.073242 | 123.1842 | 123.2117 | 123.0789 | 123.0515 | 123.0194 | -123.2025 | -123.1018 | 123.0423 | 123.1247 | 59.6924 | 59.5139
307.8906 | 123.2025 | -59.9167 | 63.208 | -0.02594 | 0.0023563 | 0.064358 | 0.06715 | 0.0020037 | 0.00046993 | -0.0023434 | -0.081696 | 0.0039798 | 0.069393 | 0.066883 | -0.0041144 | 0.0073936 | -0.0022793 | -0.1831 | 63.1897 | -60.1227 | 63.0707 | -59.7885 | -60.1776 | -0.027466 | -0.36621 | 63.1851 | -59.9442 | 63.1943 | -59.9396 | -60.0586 | -59.8022 | -0.20599 | -0.018311 | -0.13733 | 0.12817 | 59.8892 | -0.26093 | 60.0952 | -0.054931 | -0.027466 | -0.022888 | -0.013733 | -0.022888 | 0.11444 | -0.14191 | 0.14191 | -0.11444 | 0.33417 | 123.1934 | 0.004578 | 123.1384 | 123.3124 | 123.1293 | 123.1064 | 123.1018 | -123.3307 | -123.1522 | 122.9874 | 123.111 | 59.7336 | 59.5505
308.8594 | 123.3307 | -59.8755 | 63.1393 | -0.10223 | -0.00020714 | 0.064785 | 0.066082 | 0.0017901 | -0.0014527 | -0.003198 | -0.026764 | 0.0022708 | 0.068325 | 0.06667 | -0.0049688 | 0.0056846 | -0.0014249 | -0.17853 | 63.1393 | -60.0769 | 63.1668 | -59.7015 | -60.1135 | -0.004578 | -0.31128 | 63.1119 | -59.9487 | 63.2812 | -59.8297 | -59.9442 | -59.6878 | -0.20142 | 0 | 0.027466 | 0.17395 | 59.8709 | -0.23804 | 60.0723 | -0.036621 | -0.073242 | -0.027466 | 0.14191 | 0.045776 | 0.18768 | -0.068665 | 0.26093 | 0.004577 | 0.37537 | 123.2437 | 0.11902 | 123.23 | 123.2162 | 123.0606 | 123.0148 | 122.9874 | -123.2162 | -123.0881 | 123.0423 | 123.1567 | 59.697 | 59.5642
309.8906 | 123.3078 | -59.8663 | 63.1165 | -0.071716 | 0.0032107 | 0.066067 | 0.065868 | -0.00098687 | -0.0012391 | -0.00020717 | 0.04953 | 0.0031254 | 0.069821 | 0.063465 | -0.0049688 | 0.0058982 | -0.0022793 | -0.19226 | 63.1531 | -60.0861 | 63.1485 | -59.6878 | -60.466 | -0.013733 | -0.38452 | 63.1256 | -59.9258 | 63.2675 | -59.8663 | -59.9258 | -59.6878 | -0.21973 | 0.036621 | 0.032044 | 0.17853 | 59.8526 | -0.59967 | 60.0723 | -0.37994 | -0.059509 | 0.009155 | 0.15106 | 0 | 0.17853 | -0.059509 | 0.23804 | 0 | 0.39826 | 123.2346 | 0.059509 | 123.1934 | 123.2391 | 123.0515 | 123.0194 | 122.9919 | -123.2025 | -123.0423 | 123.0148 | 123.1338 | 59.6741 | 59.4818
310.8594 | 123.2895 | -59.8984 | 63.1348 | -0.086975 | 0.0036381 | 0.06329 | 0.066509 | -0.00013247 | -0.00081187 | -0.00020717 | -0.060333 | 0.0018436 | 0.070675 | 0.060475 | -0.0047552 | 0.0044028 | 0.00092494 | -0.23346 | 63.1897 | -60.1135 | 63.0753 | -59.7885 | -60.1959 | -0.054932 | -0.41657 | 63.1302 | -59.9579 | 63.2401 | -59.903 | -59.9854 | -59.7198 | -0.21515 | 0.054931 | -0.05951 | 0.10986 | 59.8434 | -0.29755 | 60.0586 | -0.082398 | -0.05951 | -0.004578 | 0.10529 | -0.004578 | 0.17853 | -0.086976 | 0.23804 | -0.027466 | 0.32501 | 123.1888 | 0.054932 | 123.1979 | 123.3032 | 123.0881 | 123.0881 | 123.0286 | -123.2483 | -123.0927 | 122.9736 | 123.1384 | 59.6649 | 59.4818
311.9062 | 123.2849 | -59.8755 | 63.1668 | -0.10986 | 0.0015019 | 0.063076 | 0.063091 | 0.00093573 | -0.00038447 | -0.0036252 | 0.025116 | 0.0020572 | 0.070248 | 0.063038 | -0.004328 | 0.0046164 | 0.0024203 | -0.19684 | 63.1622 | -60.0403 | 63.1165 | -59.7473 | -60.1318 | 0.032043 | -0.33417 | 63.1439 | -59.9442 | 63.2309 | -59.848 | -59.9396 | -59.7198 | -0.1648 | -0.004578 | -0.050354 | 0.12817 | 59.9075 | -0.25635 | 60.0723 | -0.091553 | -0.068665 | -0.022888 | 0.064087 | 0.027466 | 0.15564 | -0.064087 | 0.2243 | 0.004578 | 0.29297 | 123.1567 | 0.096131 | 123.175 | 123.2025 | 123.0881 | 123.0377 | 123.0194 | -123.2071 | -123.111 | 122.9919 | 123.1064 | 59.6786 | 59.5413
312.8594 | 123.3215 | -59.8389 | 63.1348 | -0.11749 | 0.0034245 | 0.065213 | 0.064159 | 0.0030719 | -0.0016663 | -0.001489 | -0.042023 | 0.002698 | 0.070248 | 0.067738 | -0.0056098 | 0.0063254 | -0.0029203 | -0.16479 | 63.1393 | -60.0861 | 63.1531 | -59.6878 | -60.0861 | 0.018311 | -0.32044 | 63.1256 | -59.9487 | 63.2629 | -59.8434 | -59.9442 | -59.7061 | -0.24719 | 0.004577 | 0.01831 | 0.15106 | 59.8572 | -0.24719 | 60.1044 | 0 | -0.10986 | -0.009156 | 0.12817 | -0.004578 | 0.13275 | -0.10529 | 0.24261 | 0.004577 | 0.39826 | 123.2391 | 0.10528 | 123.2117 | 123.2254 | 123.0743 | 122.9782 | 122.9645 | -123.2208 | -123.0835 | 122.9919 | 123.1018 | 59.6741 | 59.5184
313.8906 | 123.2346 | -59.8663 | 63.1805 | -0.056457 | 0.00022006 | 0.063717 | 0.068005 | 0.00093573 | -0.0016663 | 0.001929 | 0.012909 | 0.005048 | 0.069607 | 0.06966 | -0.0049688 | 0.0046164 | 0.00028414 | -0.1236 | 63.2355 | -60.0723 | 63.121 | -59.6695 | -60.4111 | -0.022888 | -0.30212 | 63.1897 | -59.9258 | 63.2446 | -59.8572 | -60.0128 | -59.7336 | -0.20599 | 0.054932 | -0.059509 | 0.19684 | 59.8434 | -0.54474 | 60.0494 | -0.33874 | -0.059509 | 0.009155 | 0.064087 | 0.009155 | 0.13275 | -0.14648 | 0.19226 | -0.086975 | 0.40283 | 123.1934 | 0.068664 | 123.1705 | 123.3078 | 123.1155 | 123.1018 | 123.056 | -123.2529 | -123.1064 | 122.9874 | 123.111 | 59.7427 | 59.5642
314.8594 | 123.3124 | -59.8572 | 63.1393 | -0.086975 | 0.00064726 | 0.06564 | 0.06715 | 0.00050853 | 0.00068353 | -0.00020717 | -0.023712 | 0.00013459 | 0.068539 | 0.058338 | -0.0056098 | 0.0046164 | -0.0037747 | -0.18768 | 63.1256 | -60.0449 | 63.1485 | -59.7015 | -60.0998 | 0 | -0.31586 | 63.089 | -59.9579 | 63.2629 | -59.848 | -59.9716 | -59.6924 | -0.18768 | -0.013733 | 0.009156 | 0.15564 | 59.8572 | -0.24261 | 60.0449 | -0.054931 | -0.10071 | -0.050354 | 0.1236 | 0.009156 | 0.16479 | -0.11444 | 0.2655 | -0.013733 | 0.34332 | 123.1934 | 0.10986 | 123.2208 | 123.1705 | 123.0469 | 122.9828 | 122.9462 | -123.1842 | -123.0972 | 123.0057 | 123.1201 | 59.6695 | 59.5413
315.8906 | 123.2162 | -59.9075 | 63.1577 | -0.086975 | 0.00064726 | 0.063076 | 0.065655 | 0.00050853 | -0.00059807 | 0.0010746 | -0.087799 | 0.0035526 | 0.069393 | 0.058979 | -0.0053962 | 0.0058982 | -0.0020657 | -0.25177 | 63.1851 | -60.0861 | 63.0432 | -59.8434 | -60.228 | -0.09613 | -0.45319 | 63.1622 | -59.9945 | 63.1714 | -59.9579 | -60.0998 | -59.7885 | -0.17853 | 0.027466 | -0.11444 | 0.064087 | 59.8114 | -0.32043 | 59.9899 | -0.14191 | -0.086975 | 0.004577 | 0.013733 | -0.050354 | 0.11902 | -0.19226 | 0.20599 | -0.10529 | 0.24262 | 123.1293 | 0.036621 | 123.1659 | 123.2712 | 123.1567 | 123.0927 | 123.0698 | -123.2437 | -123.1522 | 122.9507 | 123.0789 | 59.6558 | 59.4543
316.8594 | 123.262 | -59.8709 | 63.1622 | -0.12512 | 0.0017155 | 0.062436 | 0.06715 | 0.00050853 | 0.00068353 | -0.002557 | 0.012909 | 0.00098899 | 0.068539 | 0.060475 | -0.0051824 | 0.0041892 | 0.0022067 | -0.21973 | 63.1897 | -60.0723 | 63.0981 | -59.7382 | -60.1227 | 0.013733 | -0.3479 | 63.1348 | -59.9396 | 63.2309 | -59.8526 | -59.9533 | -59.7198 | -0.20142 | 0.027466 | -0.064086 | 0.13275 | 59.8846 | -0.25177 | 60.0861 | -0.050354 | -0.068664 | -0.027465 | 0.068665 | 0.018311 | 0.15106 | -0.082397 | 0.21973 | -0.013733 | 0.33417 | 123.1705 | 0.086975 | 123.1705 | 123.262 | 123.0743 | 123.0606 | 123.0057 | -123.2346 | -123.1018 | 122.9691 | 123.1018 | 59.6512 | 59.523
317.8906 | 123.2208 | -59.8938 | 63.1851 | -0.048828 | -0.00020714 | 0.062863 | 0.069073 | 0.00093573 | -0.0033753 | -0.00020717 | -0.087799 | 0.0014164 | 0.06918 | 0.067311 | -0.0041144 | 0.0073936 | -0.0012113 | -0.16022 | 63.176 | -60.0677 | 63.1348 | -59.729 | -60.1181 | 0.018311 | -0.25177 | 63.1805 | -59.9396 | 63.2309 | -59.8755 | -60.0037 | -59.7382 | -0.17395 | -0.009156 | -0.050354 | 0.16479 | 59.9121 | -0.2243 | 60.0861 | -0.050354 | -0.045776 | -0.004578 | 0.045776 | 0.018311 | 0.15564 | -0.10986 | 0.20142 | -0.064087 | 0.33874 | 123.2025 | 0.064087 | 123.1705 | 123.2437 | 123.1201 | 123.0698 | 123.0743 | -123.2529 | -123.1247 | 123.0286 | 123.1247 | 59.7336 | 59.642
318.8594 | 123.2895 | -59.8755 | 63.1302 | -0.086975 | 0.0021427 | 0.063504 | 0.067364 | 0.0024311 | -0.00017087 | -0.0023434 | -0.057281 | 0.00077539 | 0.070034 | 0.071797 | -0.0058234 | 0.0046164 | -0.0044157 | -0.25177 | 63.1897 | -60.0998 | 63.1027 | -59.7702 | -60.1822 | -0.068665 | -0.37537 | 63.1119 | -59.9625 | 63.2263 | -59.8984 | -59.9808 | -59.697 | -0.2243 | 0.059509 | -0.027466 | 0.10528 | 59.8068 | -0.3067 | 60.0311 | -0.082398 | -0.086975 | -0.018311 | 0.09613 | -0.022888 | 0.17853 | -0.10529 | 0.2655 | -0.018311 | 0.32959 | 123.2025 | 0.064087 | 123.1888 | 123.2895 | 123.0743 | 123.0652 | 122.9874 | -123.23 | -123.0927 | 122.9782 | 123.1018 | 59.6237 | 59.5001
319.8906 | 123.2483 | -59.8892 | 63.176 | -0.056457 | 0.0021427 | 0.064572 | 0.065441 | 0.0017901 | -0.0014527 | -0.00020717 | -0.066437 | 0.002698 | 0.068539 | 0.063679 | -0.0047552 | 0.0076072 | -0.0016385 | -0.16022 | 63.2126 | -60.0723 | 63.1119 | -59.729 | -60.1089 | 0.036621 | -0.2655 | 63.1531 | -59.9258 | 63.2401 | -59.8801 | -60.022 | -59.7382 | -0.18311 | 0.036621 | -0.064087 | 0.16022 | 59.9258 | -0.21973 | 60.1089 | -0.036621 | -0.036621 | -0.022888 | 0.064087 | 0.009155 | 0.15106 | -0.13275 | 0.18768 | -0.096131 | 0.34332 | 123.1842 | 0.045776 | 123.1659 | 123.2849 | 123.0789 | 123.1018 | 123.0423 | -123.2483 | -123.1018 | 123.0011 | 123.1293 | 59.729 | 59.6237
320.8594 | 123.2941 | -59.8984 | 63.1073 | -0.12512 | 0.0034245 | 0.062436 | 0.063732 | 0.0013629 | -0.0010255 | -0.0012754 | -0.011505 | 0.0020572 | 0.071743 | 0.062824 | -0.0036872 | 0.0061118 | 0.0019931 | -0.20599 | 63.1256 | -60.0586 | 63.1439 | -59.6832 | -60.0998 | 0 | -0.32044 | 63.1073 | -59.9533 | 63.2492 | -59.8343 | -59.967 | -59.7198 | -0.16022 | 0.01831 | 0.036621 | 0.21515 | 59.8984 | -0.20142 | 60.0586 | -0.041198 | -0.054932 | 0 | 0.14191 | 0.064086 | 0.17853 | -0.068665 | 0.23346 | -0.013733 | 0.37537 | 123.2025 | 0.11902 | 123.2025 | 123.1842 | 123.0606 | 123.024 | 123.0057 | -123.1659 | -123.0606 | 123.0423 | 123.1476 | 59.6924 | 59.5779
321.8906 | 123.3261 | -59.8663 | 63.1348 | -0.13275 | 0.0025699 | 0.06564 | 0.066296 | 0.00072213 | -0.0027345 | -0.00084817 | 0.034271 | 0.0018436 | 0.06918 | 0.063465 | -0.0053962 | 0.0054708 | -0.0056973 | -0.21057 | 63.1393 | -60.0815 | 63.1256 | -59.7336 | -60.3973 | -0.23346 | -0.33417 | 63.1119 | -59.9167 | 63.2812 | -59.8618 | -59.935 | -59.6649 | -0.21515 | 0.004577 | -0.009156 | 0.13275 | 59.6329 | -0.53101 | 59.848 | -0.31586 | -0.050354 | -0.022889 | 0.14648 | 0.004578 | 0.20142 | -0.068665 | 0.25177 | -0.018311 | 0.3479 | 123.2071 | 0.054932 | 123.1979 | 123.2208 | 123.0286 | 123.0057 | 122.9782 | -123.2162 | -123.0515 | 122.9919 | 123.1476 | 59.6558 | 59.5322
322.8594 | 123.2758 | -59.8755 | 63.1393 | -0.12512 | 0.0049197 | 0.064572 | 0.065441 | -0.00077327 | 0.0021789 | -0.0023434 | -0.032867 | 0.00163 | 0.069821 | 0.065815 | -0.0045416 | 0.0050436 | -0.00078406 | -0.21057 | 63.1302 | -60.0769 | 63.1439 | -59.6832 | -60.0998 | 0.004578 | -0.31586 | 63.121 | -59.9213 | 63.2675 | -59.8434 | -59.9579 | -59.7015 | -0.20142 | -0.009155 | 0.004578 | 0.19226 | 59.8801 | -0.2243 | 60.0815 | -0.022888 | -0.045777 | -0.01831 | 0.12817 | 0.032043 | 0.17395 | -0.082398 | 0.21973 | -0.036621 | 0.39368 | 123.2208 | 0.07782 | 123.1888 | 123.2071 | 123.0423 | 123.0057 | 122.9965 | -123.2162 | -123.0606 | 123.0194 | 123.143 | 59.6649 | 59.5596
323.8906 | 123.2529 | -59.8709 | 63.1622 | -0.10223 | 0.0015019 | 0.062222 | 0.066723 | -0.0024823 | 0.00046993 | 0.0010746 | -0.069489 | 0.0035526 | 0.067898 | 0.075428 | -0.0079596 | 0.0052572 | -0.00057046 | -0.11444 | 63.1897 | -60.0586 | 63.1256 | -59.7382 | -60.1044 | 0.036621 | -0.26093 | 63.1531 | -59.935 | 63.2309 | -59.8709 | -60.0037 | -59.7382 | -0.18768 | 0.027466 | -0.036621 | 0.13275 | 59.9075 | -0.23346 | 60.0952 | -0.045776 | -0.064087 | -0.009155 | 0.068665 | 0 | 0.13275 | -0.13275 | 0.19684 | -0.068664 | 0.32043 | 123.1842 | 0.064087 | 123.1659 | 123.2483 | 123.0881 | 123.0606 | 123.024 | -123.2208 | -123.0972 | 122.9965 | 123.1018 | 59.7565 | 59.61
324.8594 | 123.3124 | -59.8938 | 63.1073 | -0.10223 | 0.0040653 | 0.06564 | 0.067577 | -0.0022687 | -0.00059807 | -0.00063437 | -0.02066 | 0.0029116 | 0.068539 | 0.071583 | -0.0053962 | 0.0061118 | -0.0014249 | -0.21057 | 63.1439 | -60.0952 | 63.1073 | -59.6741 | -60.0952 | -0.045776 | -0.32044 | 63.1027 | -59.9487 | 63.2767 | -59.8389 | -59.9533 | -59.6786 | -0.20142 | 0.036621 | 0 | 0.21973 | 59.848 | -0.20142 | 60.0494 | 0 | -0.054931 | -0.004578 | 0.16937 | 0.054932 | 0.21515 | -0.059509 | 0.27008 | -0.004578 | 0.42114 | 123.2025 | 0.10986 | 123.2254 | 123.2391 | 123.0515 | 123.0377 | 122.9965 | -123.2025 | -123.056 | 123.0011 | 123.1705 | 59.6832 | 59.5734
325.9062 | 123.2849 | -59.8892 | 63.1577 | -0.056457 | 0.00086086 | 0.064572 | 0.065228 | 0.00093573 | 4.273e-05 | -0.00063437 | 0.043427 | 0.0029116 | 0.069607 | 0.070942 | -0.0049688 | 0.00483 | -0.00035666 | -0.21973 | 63.176 | -60.0769 | 63.1027 | -59.761 | -60.1227 | 0.004578 | -0.32959 | 63.1348 | -59.967 | 63.2401 | -59.8434 | -59.9579 | -59.7015 | -0.18768 | 0.01831 | -0.054932 | 0.12817 | 59.8938 | -0.23346 | 60.0815 | -0.045777 | -0.07782 | -0.022888 | 0.082397 | 0.045776 | 0.18768 | -0.068665 | 0.2655 | 0.009155 | 0.31586 | 123.1796 | 0.1236 | 123.2071 | 123.2529 | 123.1018 | 123.0652 | 123.024 | -123.2346 | -123.1247 | 122.9919 | 123.1293 | 59.6695 | 59.5596
326.8594 | 123.2712 | -59.8709 | 63.1348 | -0.10223 | 0.0025699 | 0.066494 | 0.0648 | 8.1126e-05 | -0.0020935 | -0.0010618 | -0.017609 | 0.0014164 | 0.07153 | 0.065388 | -0.0049688 | 0.0067526 | -0.0039883 | -0.2243 | 63.1439 | -60.0769 | 63.1256 | -59.7382 | -60.1273 | -0.013733 | -0.3479 | 63.1073 | -59.9625 | 63.2355 | -59.8801 | -59.9945 | -59.7519 | -0.20599 | 0.009155 | -0.009156 | 0.13275 | 59.8572 | -0.25635 | 60.0632 | -0.050354 | -0.091552 | -0.027466 | 0.10071 | -0.009155 | 0.11902 | -0.1236 | 0.21057 | -0.032044 | 0.33874 | 123.2025 | 0.082397 | 123.1979 | 123.2208 | 123.0698 | 123.0148 | 122.9782 | -123.2117 | -123.0972 | 122.9965 | 123.1064 | 59.6466 | 59.523
327.8906 | 123.2483 | -59.8709 | 63.1393 | -0.12512 | 0.0032107 | 0.064785 | 0.066509 | 0.0017901 | -0.0029481 | -0.00042077 | -0.063385 | 0.0022708 | 0.068112 | 0.064747 | -0.0079596 | 0.00483 | -0.0012113 | -0.25177 | 63.1577 | -60.0906 | 63.1027 | -59.7565 | -60.1501 | -0.041199 | -0.36163 | 63.0936 | -59.9625 | 63.1027 | -59.7244 | -59.7519 | -59.5688 | -0.21973 | 0.018311 | -0.036621 | 0.11444 | 59.8297 | -0.27923 | 60.0494 | -0.059509 | -0.091552 | -0.045776 | -0.036621 | 0.14648 | 0.30212 | 0.11902 | 0.39368 | 0.21057 | 0.33417 | 123.1934 | 0.23804 | 123.0652 | 123.2483 | 123.056 | 123.0286 | 122.9645 | -123.23 | -123.1018 | 122.9736 | 122.9736 | 59.6191 | 59.5093
328.8594 | 123.2666 | -59.8846 | 63.1485 | -0.11749 | 0.0012881 | 0.064358 | 0.066296 | -0.00034607 | 0.0013245 | -0.00084817 | 0.0037536 | 0.0018436 | 0.068753 | 0.060047 | -0.0045416 | 0.0050436 | -0.0037747 | -0.25635 | 63.1851 | -60.0723 | 63.1485 | -59.7107 | -60.2051 | -0.041199 | -0.38452 | 63.1256 | -59.9579 | 63.2309 | -59.8938 | -59.9808 | -59.7153 | -0.18768 | 0.036621 | 0 | 0.17395 | 59.8434 | -0.32043 | 60.0311 | -0.13275 | -0.073242 | -0.022889 | 0.082397 | -0.009155 | 0.16937 | -0.09613 | 0.24262 | -0.022888 | 0.36163 | 123.2208 | 0.064087 | 123.1888 | 123.2574 | 123.0835 | 123.0698 | 123.0103 | -123.2208 | -123.1064 | 123.0331 | 123.1155 | 59.6283 | 59.5001
329.8906 | 123.1888 | -59.903 | 63.1668 | 0.15717 | 0.0023563 | 0.063504 | 0.065655 | -0.00055967 | -0.0020935 | 0.00022003 | -0.090851 | 0.00098899 | 0.068753 | 0.067738 | -0.0081732 | 0.0046164 | -0.0014249 | -0.37994 | 63.1897 | -60.0952 | 63.002 | -59.8984 | -60.2051 | -0.091553 | -0.46234 | 63.1485 | -59.9762 | 63.1668 | -59.9854 | -60.1135 | -59.8251 | -0.19226 | 0.022888 | -0.16479 | 0.004578 | 59.8114 | -0.30212 | 60.0037 | -0.10986 | -0.073242 | -0.01831 | 0 | -0.082398 | 0.07782 | -0.21057 | 0.15106 | -0.13733 | 0.19684 | 123.0972 | -0.009156 | 123.143 | 123.2849 | 123.1247 | 123.0927 | 123.0515 | -123.262 | -123.143 | 122.905 | 123.0698 | 59.523 | 59.4406
330.8594 | 123.2803 | -59.8984 | 63.1393 | -0.079346 | 0.0015019 | 0.064572 | 0.065228 | -0.0031231 | -0.0027345 | -0.0023434 | -0.035919 | 0.00098899 | 0.068753 | 0.069233 | -0.004328 | 0.0058982 | 0.0017795 | -0.23346 | 63.1485 | -60.0952 | 63.121 | -59.7153 | -60.1456 | -0.013733 | -0.35248 | 63.1119 | -59.9304 | 63.2126 | -59.8938 | -59.9945 | -59.729 | -0.19684 | 0.009156 | -0.01831 | 0.1831 | 59.8846 | -0.24719 | 60.0815 | -0.050354 | -0.032044 | -0.027466 | 0.073242 | 0.004577 | 0.16937 | -0.096131 | 0.20142 | -0.064087 | 0.37994 | 123.2162 | 0.036621 | 123.143 | 123.2437 | 123.0423 | 123.0469 | 123.0103 | -123.2346 | -123.0698 | 123.0194 | 123.111 | 59.6649 | 59.5459
331.8906 | 123.2666 | -59.8801 | 63.1302 | -0.11749 | 0.00064726 | 0.062222 | 0.063732 | -0.0016279 | 4.273e-05 | -0.0023434 | -0.0054016 | 0.0022708 | 0.068966 | 0.068165 | -0.0045416 | 0.0056846 | 0.00028414 | -0.25177 | 63.176 | -60.0632 | 63.0981 | -59.7702 | -60.1364 | -0.027466 | -0.44403 | 63.1302 | -59.935 | 63.1805 | -59.903 | -60.0174 | -59.7336 | -0.1831 | 0.045776 | -0.032043 | 0.10986 | 59.8526 | -0.25635 | 60.0357 | -0.073243 | -0.054932 | 0 | 0.050354 | -0.022888 | 0.14648 | -0.13733 | 0.20142 | -0.082397 | 0.29297 | 123.1613 | 0.032044 | 123.1155 | 123.2391 | 123.0652 | 123.056 | 123.0103 | -123.1934 | -123.0652 | 122.9782 | 123.0606 | 59.6283 | 59.436
332.8594 | 123.2758 | -59.8938 | 63.1439 | -0.056457 | 0.0010745 | 0.064785 | 0.066723 | 0.0013629 | -0.0010255 | -0.0027708 | -0.038971 | -0.00050621 | 0.065762 | 0.067097 | -0.006037 | 0.0061118 | -0.0029203 | -0.20599 | 63.1348 | -60.0815 | 63.121 | -59.7244 | -60.1273 | -0.027466 | -0.33875 | 63.1165 | -59.9442 | 63.2172 | -59.8984 | -59.9991 | -59.7382 | -0.18768 | -0.009155 | -0.022888 | 0.16937 | 59.8663 | -0.23346 | 60.054 | -0.045776 | -0.050354 | -0.027466 | 0.073242 | -0.004577 | 0.15564 | -0.10529 | 0.20599 | -0.054931 | 0.35706 | 123.2025 | 0.045777 | 123.1613 | 123.2162 | 123.0606 | 123.0286 | 123.0103 | -123.2254 | -123.0881 | 123.0148 | 123.111 | 59.6878 | 59.5551
333.8906 | 123.262 | -59.8755 | 63.1393 | -0.056457 | 0.0021427 | 0.063717 | 0.065441 | 0.0020037 | -0.0014527 | -0.0012754 | -0.045074 | 0.00163 | 0.067471 | 0.065388 | -0.0062506 | 0.0069662 | -0.0048429 | -0.21973 | 63.1485 | -60.0723 | 63.1393 | -59.7107 | -60.1273 | -0.022888 | -0.32501 | 63.0936 | -59.9716 | 63.2492 | -59.8663 | -59.9854 | -59.7382 | -0.19684 | 0.009156 | 0 | 0.16479 | 59.8526 | -0.25177 | 60.0494 | -0.054931 | -0.096131 | -0.045776 | 0.10986 | 0.009155 | 0.13733 | -0.10986 | 0.23346 | -0.013733 | 0.36163 | 123.2117 | 0.10529 | 123.2208 | 123.2208 | 123.0652 | 123.024 | 122.9691 | -123.2117 | -123.111 | 123.0148 | 123.1247 | 59.6558 | 59.5505
334.8594 | 123.3124 | -59.8709 | 63.1531 | -0.056457 | 0.00086086 | 0.062863 | 0.066296 | -0.0020551 | -0.0025207 | -0.002557 | 0.03122 | 0.0012028 | 0.068325 | 0.064961 | -0.006037 | 0.006539 | -0.00099766 | -0.22888 | 63.1805 | -60.0723 | 63.1348 | -59.7473 | -60.1135 | 0.032043 | -0.30212 | 63.1439 | -59.9304 | 63.2401 | -59.8343 | -59.9396 | -59.6924 | -0.20142 | 0.027466 | -0.01831 | 0.1236 | 59.903 | -0.24261 | 60.1044 | -0.041198 | -0.059509 | -0.009155 | 0.086975 | 0.036621 | 0.17853 | -0.068664 | 0.23804 | -0.009155 | 0.32501 | 123.2071 | 0.09613 | 123.1705 | 123.2529 | 123.0743 | 123.0515 | 123.0148 | -123.2254 | -123.0835 | 123.0057 | 123.111 | 59.642 | 59.5688
335.8906 | 123.1979 | -59.9121 | 63.1668 | -0.041199 | 0.0025699 | 0.064572 | 0.067791 | 0.0034991 | -0.0031617 | -0.0012754 | -0.096954 | 0.0037662 | 0.068325 | 0.068379 | -0.0081732 | 0.006539 | -0.0033475 | -0.26093 | 63.1897 | -60.1044 | 63.0524 | -59.848 | -60.2371 | -0.11902 | -0.45776 | 63.1485 | -59.9899 | 63.1531 | -59.9899 | -60.0998 | -59.8114 | -0.19226 | 0.022888 | -0.11444 | 0.064087 | 59.7931 | -0.32501 | 59.9854 | -0.13275 | -0.07782 | -0.01831 | -0.013733 | -0.07782 | 0.10071 | -0.18768 | 0.17853 | -0.10986 | 0.25635 | 123.1567 | 0 | 123.143 | 123.2941 | 123.1384 | 123.1018 | 123.0606 | -123.2712 | -123.1567 | 122.9645 | 123.0652 | 59.6512 | 59.4543
336.8594 | 123.3032 | -59.8572 | 63.1439 | -0.086975 | 0.00064726 | 0.064572 | 0.066296 | -0.0022687 | -0.00038447 | -0.002557 | -0.0023498 | 0.0012028 | 0.070675 | 0.061115 | -0.0030462 | 0.0069662 | -0.0022793 | -0.21057 | 63.1668 | -60.0677 | 63.1439 | -59.7244 | -60.0723 | 0.036621 | -0.29297 | 63.1256 | -59.9213 | 63.2675 | -59.8389 | -59.9258 | -59.7015 | -0.21057 | 0.022888 | 0 | 0.13275 | 59.8938 | -0.21515 | 60.1044 | -0.004578 | -0.064087 | -0.018311 | 0.1236 | 0.018311 | 0.15564 | -0.068664 | 0.21973 | -0.004577 | 0.34332 | 123.2117 | 0.082398 | 123.1888 | 123.2346 | 123.0469 | 123.024 | 122.9828 | -123.2117 | -123.0652 | 123.0011 | 123.1247 | 59.6466 | 59.5642
337.8594 | 123.2941 | -59.8618 | 63.1348 | -0.079346 | 0.0027835 | 0.062222 | 0.065441 | -0.0012005 | -0.0014527 | 0.0021426 | -0.029816 | 0.0029116 | 0.068753 | 0.061329 | -0.0049688 | 0.0050436 | 0.0017795 | -0.21973 | 63.1348 | -60.0769 | 63.1531 | -59.697 | -60.1089 | -0.013733 | -0.32044 | 63.0981 | -59.9487 | 63.2446 | -59.8755 | -59.9808 | -59.7244 | -0.21515 | 0 | 0.01831 | 0.1648 | 59.848 | -0.24719 | 60.0632 | -0.032044 | -0.086975 | -0.036621 | 0.10986 | -0.013733 | 0.13733 | -0.11902 | 0.2243 | -0.032044 | 0.37994 | 123.23 | 0.073242 | 123.1934 | 123.2117 | 123.0469 | 122.9965 | 122.9599 | -123.2117 | -123.0835 | 123.0148 | 123.1064 | 59.642 | 59.5413
338.8594 | 123.2849 | -59.8709 | 63.1531 | -0.079346 | 0.0023563 | 0.061154 | 0.065014 | 0.0022173 | -0.00038447 | -0.001489 | 0.080048 | 0.0020572 | 0.070034 | 0.067097 | -0.0030462 | 0.006539 | -0.00014306 | -0.25177 | 63.1393 | -60.0677 | 63.0936 | -59.7519 | -60.1456 | -0.032043 | -0.37994 | 63.1256 | -59.9258 | 63.2263 | -59.9075 | -59.967 | -59.7061 | -0.19684 | -0.013733 | -0.059509 | 0.11902 | 59.8389 | -0.27466 | 60.0357 | -0.07782 | -0.054931 | -0.027466 | 0.073242 | -0.036621 | 0.16479 | -0.09613 | 0.21973 | -0.041199 | 0.31586 | 123.1613 | 0.01831 | 123.1522 | 123.2071 | 123.0515 | 123.0103 | 122.9965 | -123.2208 | -123.0789 | 122.9645 | 123.0972 | 59.6191 | 59.491
339.8594 | 123.2986 | -59.8892 | 63.1302 | -0.10223 | 0.0019291 | 0.063504 | 0.065014 | 8.1126e-05 | -0.0025207 | -0.003198 | -0.05423 | 0.00163 | 0.070461 | 0.066242 | -0.0056098 | 0.0056846 | -0.00099766 | -0.2243 | 63.1393 | -60.0586 | 63.1531 | -59.7244 | -60.1135 | -0.027466 | -0.34332 | 63.0981 | -59.9442 | 63.2446 | -59.8801 | -59.9899 | -59.7244 | -0.16937 | 0.009155 | 0.022888 | 0.16479 | 59.8618 | -0.2243 | 60.0311 | -0.054931 | -0.054932 | -0.032043 | 0.11444 | 0.009155 | 0.16479 | -0.10071 | 0.21973 | -0.045776 | 0.33417 | 123.2117 | 0.064087 | 123.1888 | 123.1979 | 123.0423 | 123.0286 | 122.9874 | -123.1888 | -123.0743 | 123.0423 | 123.1338 | 59.6649 | 59.5459
340.8906 | 123.2712 | -59.8846 | 63.1348 | -0.15564 | 0.00086086 | 0.064358 | 0.066082 | 0.00072213 | 0.0011109 | -0.00042077 | -0.026764 | 0.0029116 | 0.069821 | 0.059193 | -0.0056098 | 0.0056846 | -0.0029203 | -0.24261 | 63.176 | -60.054 | 63.0981 | -59.7473 | -60.1364 | -0.045776 | -0.37537 | 63.121 | -59.9304 | 63.2812 | -59.9533 | -60.0403 | -59.7473 | -0.16937 | 0.041198 | -0.036621 | 0.13733 | 59.8389 | -0.25177 | 60.0082 | -0.082398 | -0.045776 | -0.013733 | 0.14648 | -0.068664 | 0.13733 | -0.15564 | 0.18311 | -0.10986 | 0.3067 | 123.1522 | -0.022888 | 123.2117 | 123.23 | 123.0515 | 123.0606 | 123.0057 | -123.1888 | -123.0652 | 122.9828 | 123.1659 | 59.642 | 59.5093
341.8594 | 123.2483 | -59.8846 | 63.1577 | -0.048828 | 0.0012881 | 0.06329 | 0.065441 | 0.0052081 | -0.0029481 | 0.00086083 | -0.035919 | 0.0024844 | 0.070034 | 0.06197 | -0.007105 | 0.0071798 | -0.00078406 | -0.25635 | 63.1577 | -60.0769 | 63.176 | -59.7794 | -60.2188 | -0.036621 | -0.38452 | 63.1439 | -59.9396 | 63.2172 | -59.8846 | -59.9991 | -59.729 | -0.19226 | 0 | 0.01831 | 0.10529 | 59.848 | -0.33417 | 60.0403 | -0.14191 | -0.054931 | -0.013733 | 0.059509 | 0 | 0.15564 | -0.11444 | 0.21057 | -0.059509 | 0.29755 | 123.2529 | 0.054931 | 123.1567 | 123.2346 | 123.0835 | 123.0423 | 123.0286 | -123.2346 | -123.0972 | 123.0606 | 123.1018 | 59.6283 | 59.5001
342.8906 | 123.1934 | -59.8709 | 63.1989 | -0.033569 | 0.0019291 | 0.063076 | 0.065655 | 0.0043537 | -0.00059807 | -0.002557 | -0.014557 | 0.002698 | 0.069393 | 0.065815 | -0.007105 | 0.0069662 | -0.0065519 | -0.1831 | 63.2309 | -60.0723 | 63.1622 | -59.491 | -60.3241 | -0.1236 | -0.33417 | 63.1714 | -59.9579 | 63.1943 | -59.9213 | -60.022 | -59.7519 | -0.20142 | 0.032043 | -0.036622 | 0.37994 | 59.7473 | -0.45319 | 59.9487 | -0.25177 | -0.086975 | -0.027466 | -0.004578 | -0.050354 | 0.11902 | -0.15106 | 0.20599 | -0.064087 | 0.58136 | 123.2346 | 0.036621 | 123.1522 | 123.3032 | 123.1293 | 123.1018 | 123.0423 | -123.2712 | -123.1567 | 123.0331 | 123.0652 | 59.6878 | 59.5367
343.8594 | 123.2712 | -59.8755 | 63.1668 | -0.041199 | 0.0042789 | 0.06094 | 0.066509 | 0.0041399 | 0.00089713 | 0.00064723 | -0.017609 | 0.0014164 | 0.069821 | 0.060475 | -0.0030462 | 0.0033346 | 0.00092494 | -0.073242 | 63.1851 | -60.0677 | 63.1073 | -59.7748 | -60.1456 | -0.036621 | -0.3891 | 63.1485 | -59.9579 | 63.208 | -59.8892 | -59.9808 | -59.7427 | -0.19226 | 0.018311 | -0.059509 | 0.10071 | 59.8389 | -0.27008 | 60.0311 | -0.07782 | -0.082398 | -0.01831 | 0.041199 | -0.013733 | 0.13275 | -0.10529 | 0.21515 | -0.022888 | 0.29297 | 123.175 | 0.068665 | 123.1659 | 123.2529 | 123.1064 | 123.0606 | 123.024 | -123.2346 | -123.1247 | 122.9828 | 123.0835 | 59.8022 | 59.4864
344.8906 | 123.2758 | -59.8892 | 63.1393 | -0.071716 | 0.0015019 | 0.062436 | 0.065441 | -0.00098687 | -0.00059807 | 0.00022003 | -0.017609 | 0.00163 | 0.068753 | 0.064106 | -0.004328 | 0.0054708 | 0.0028475 | -0.2243 | 63.1897 | -60.0769 | 63.0981 | -59.7427 | -60.1318 | -0.004578 | -0.3479 | 63.1302 | -59.9442 | 63.2355 | -59.8663 | -59.9579 | -59.7153 | -0.18768 | 0.050354 | -0.041198 | 0.14648 | 59.8846 | -0.24262 | 60.0723 | -0.054932 | -0.054932 | -0.009155 | 0.096131 | 0.022888 | 0.17395 | -0.068665 | 0.22888 | -0.013733 | 0.33417 | 123.175 | 0.07782 | 123.1796 | 123.2666 | 123.0743 | 123.0789 | 123.0194 | -123.2162 | -123.0835 | 122.9874 | 123.1247 | 59.6649 | 59.5413
345.8594 | 123.2758 | -59.8984 | 63.1577 | -0.13275 | 0.0012881 | 0.064999 | 0.066082 | 0.0022173 | -0.00081187 | -0.0019162 | -0.038971 | 0.00098899 | 0.068753 | 0.061756 | -0.0045416 | 0.0069662 | -0.0033475 | -0.23804 | 63.1485 | -60.0998 | 63.1256 | -59.7244 | -60.1501 | -0.032043 | -0.37994 | 63.1302 | -59.9487 | 63.2355 | -59.9075 | -59.9854 | -59.7565 | -0.20142 | -0.009155 | -0.032044 | 0.17395 | 59.8663 | -0.25177 | 60.0677 | -0.050354 | -0.050354 | -0.027466 | 0.07782 | -0.009156 | 0.14191 | -0.086976 | 0.19226 | -0.036622 | 0.37537 | 123.2254 | 0.041198 | 123.1842 | 123.2483 | 123.0789 | 123.0469 | 123.0286 | -123.2574 | -123.1064 | 123.024 | 123.1338 | 59.6603 | 59.5184
346.9062 | 123.2758 | -59.8663 | 63.2401 | -0.033569 | 0.0025699 | 0.063717 | 0.066082 | -0.00013247 | -0.0042297 | -0.00084817 | -0.05423 | 0.00077539 | 0.067898 | 0.063038 | -0.0034736 | 0.0078208 | -0.0014249 | -0.16022 | 63.1897 | -60.0494 | 63.1302 | -59.7153 | -60.0952 | 0.07782 | -0.2655 | 63.1668 | -59.9487 | 63.1943 | -59.848 | -60.0266 | -59.8709 | -0.18311 | -0.050354 | -0.10986 | 0.15106 | 59.9442 | -0.22888 | 60.1273 | -0.045777 | -0.082397 | -0.073242 | -0.045776 | 0.018311 | -0.004578 | -0.16022 | 0.077819 | -0.07782 | 0.33417 | 123.1796 | 0.10071 | 123.143 | 123.2391 | 123.1155 | 123.056 | 123.0331 | -123.2895 | -123.1888 | 122.9965 | 123.0606 | 59.7061 | 59.6008
347.8594 | 123.2941 | -59.8526 | 63.1622 | -0.056457 | 0.0015019 | 0.062436 | 0.066296 | 0.0015765 | -0.0020935 | 0.0010746 | -0.026764 | 0.00098899 | 0.068539 | 0.066883 | -0.0039008 | 0.00483 | 0.0017795 | -0.21515 | 63.1622 | -60.0677 | 63.1302 | -59.7336 | -60.1227 | 0.009155 | -0.32959 | 63.1165 | -59.9304 | 63.2584 | -59.848 | -59.935 | -59.7015 | -0.21515 | 0 | -0.032043 | 0.11902 | 59.8618 | -0.27008 | 60.0769 | -0.054932 | -0.07782 | -0.045776 | 0.096131 | 0.004578 | 0.15106 | -0.082398 | 0.22888 | -0.004578 | 0.33417 | 123.1979 | 0.082398 | 123.1888 | 123.23 | 123.0469 | 123.0148 | 122.9691 | -123.23 | -123.0927 | 122.9828 | 123.111 | 59.6375 | 59.523
348.8906 | 123.2849 | -59.8755 | 63.1256 | -0.10986 | 0.0019291 | 0.063717 | 0.065441 | -0.00098687 | -0.0038025 | -0.001489 | -0.069489 | 0.00056179 | 0.06683 | 0.072437 | -0.0045416 | 0.0054708 | -0.0046293 | -0.22888 | 63.1302 | -60.1089 | 63.1439 | -59.7107 | -60.1227 | -0.009155 | -0.33875 | 63.1165 | -59.9487 | 63.2492 | -59.8801 | -59.9716 | -59.729 | -0.23346 | 0.004578 | 0.018311 | 0.16479 | 59.8663 | -0.24719 | 60.0998 | -0.013733 | -0.073242 | -0.009155 | 0.1236 | -0.004578 | 0.14648 | -0.096131 | 0.21973 | -0.022889 | 0.39825 | 123.2529 | 0.068664 | 123.1979 | 123.2391 | 123.0652 | 123.0057 | 122.9919 | -123.2346 | -123.0743 | 123.0194 | 123.1247 | 59.6466 | 59.5367
349.8594 | 123.3124 | -59.8526 | 63.1439 | -0.10223 | 0.00043366 | 0.064785 | 0.065655 | 8.1126e-05 | -0.0020935 | 0.0021426 | 0.00070198 | 0.00013459 | 0.069607 | 0.067524 | -0.0039008 | 0.0058982 | 0.0019931 | -0.19226 | 63.1897 | -60.0723 | 63.1577 | -59.6832 | -60.0586 | 0.054932 | -0.23804 | 63.1256 | -59.9213 | 63.2767 | -59.7885 | -59.9075 | -59.6603 | -0.21973 | 0.045776 | 0.013733 | 0.16937 | 59.9075 | -0.20599 | 60.1273 | 0.013733 | -0.068665 | -0.018311 | 0.13275 | 0.064087 | 0.19226 | -0.054932 | 0.26093 | 0.013733 | 0.3891 | 123.23 | 0.13275 | 123.1979 | 123.262 | 123.0469 | 123.0423 | 122.9782 | -123.2162 | -123.0652 | 123.0103 | 123.1293 | 59.6603 | 59.6146
350.9062 | 123.2574 | -59.8801 | 63.121 | -0.10223 | 0.00022006 | 0.062008 | 0.065655 | 0.0045673 | -0.0023071 | -0.00042077 | -0.066437 | 0.0022708 | 0.068753 | 0.060475 | -0.006037 | 0.0056846 | -0.00078406 | -0.24719 | 63.1393 | -60.0723 | 63.2629 | -59.848 | -60.1776 | 0.009155 | -0.39825 | 63.1073 | -59.9304 | 63.2401 | -59.8846 | -60.0128 | -59.7519 | -0.19226 | 0.01831 | 0.14191 | 0.032044 | 59.8892 | -0.29755 | 60.0815 | -0.10529 | -0.050354 | -0.013733 | 0.11902 | -0.004578 | 0.12817 | -0.13275 | 0.17853 | -0.082397 | 0.22431 | 123.3353 | 0.045776 | 123.1705 | 123.2117 | 123.0377 | 123.0194 | 122.9874 | -123.1934 | -123.0515 | 123.143 | 123.1201 | 59.6329 | 59.4818
351.8594 | 123.317 | -59.848 | 63.1622 | -0.048828 | 0.0017155 | 0.062649 | 0.064587 | -0.00055967 | -0.0016663 | -0.0010618 | -0.029816 | 0.0024844 | 0.070248 | 0.06902 | -0.0053962 | 0.0054708 | -0.0022793 | -0.18768 | 63.1622 | -60.0586 | 63.1668 | -59.7107 | -60.0723 | 0.050354 | -0.28839 | 63.1531 | -59.9213 | 63.2767 | -59.8251 | -59.8892 | -59.6649 | -0.21057 | 0 | 0.004578 | 0.13733 | 59.8984 | -0.22431 | 60.1089 | -0.013733 | -0.073243 | -0.009155 | 0.11444 | 0.022888 | 0.1831 | -0.041199 | 0.25635 | 0.032044 | 0.3479 | 123.2254 | 0.096131 | 123.1979 | 123.2208 | 123.0743 | 123.0103 | 123.0011 | -123.2208 | -123.0835 | 123.0148 | 123.1247 | 59.6603 | 59.5596
352.8906 | 123.2849 | -59.8755 | 63.1256 | -0.086975 | 0.0015019 | 0.062649 | 0.064373 | -0.00055967 | -0.0010255 | 6.432e-06 | -0.038971 | 0.0014164 | 0.068753 | 0.073292 | -0.006037 | 0.0054708 | -0.00035666 | -0.23346 | 63.1302 | -60.0952 | 63.1165 | -59.7473 | -60.1501 | -0.050354 | -0.41199 | 63.1302 | -59.9442 | 63.2217 | -59.8846 | -59.9762 | -59.7519 | -0.21973 | 0.004578 | -0.009155 | 0.12817 | 59.8251 | -0.27466 | 60.0449 | -0.054931 | -0.068665 | 0.004578 | 0.096131 | -0.009156 | 0.1236 | -0.10071 | 0.19226 | -0.032043 | 0.3479 | 123.2117 | 0.059509 | 123.1659 | 123.2254 | 123.0743 | 123.0057 | 123.0057 | -123.2208 | -123.0698 | 122.9919 | 123.0972 | 59.642 | 59.4635
353.8594 | 123.3032 | -59.8618 | 63.1439 | -0.048828 | 0.0027835 | 0.063931 | 0.065868 | 0.0024311 | -0.00081187 | -0.001489 | -0.026764 | 0.0024844 | 0.067898 | 0.067738 | -0.0028326 | 0.00483 | -0.0029203 | -0.21057 | 63.1668 | -60.0861 | 63.1439 | -59.7198 | -60.0861 | 0.027466 | -0.3067 | 63.1256 | -59.9442 | 63.2629 | -59.8572 | -59.9213 | -59.7015 | -0.22431 | 0.022888 | 0 | 0.14191 | 59.8892 | -0.22431 | 60.1135 | 0 | -0.082398 | -0.018311 | 0.11902 | 0.004577 | 0.16022 | -0.05951 | 0.24262 | 0.022888 | 0.36621 | 123.23 | 0.086975 | 123.2071 | 123.2529 | 123.0698 | 123.0286 | 122.9874 | -123.23 | -123.0881 | 123.0057 | 123.1247 | 59.6512 | 59.5551
354.8906 | 123.262 | -59.8572 | 63.1531 | -0.094604 | 0.0010745 | 0.063076 | 0.0648 | -0.0020551 | -0.0012391 | -0.0019162 | -0.042023 | 0.0012028 | 0.070675 | 0.065174 | -0.006037 | 0.0033346 | -0.00035666 | -0.24719 | 63.1073 | -60.0952 | 63.1119 | -59.8068 | -60.1593 | -0.022888 | -0.39825 | 63.1027 | -59.9442 | 63.2263 | -59.8892 | -59.9899 | -59.7382 | -0.23804 | -0.045776 | -0.041199 | 0.050354 | 59.8343 | -0.30212 | 60.0723 | -0.064087 | -0.086975 | -0.050354 | 0.073242 | -0.032043 | 0.11902 | -0.13275 | 0.20599 | -0.045776 | 0.28839 | 123.2071 | 0.054932 | 123.1705 | 123.2025 | 123.0469 | 122.9645 | 122.9599 | -123.2483 | -123.0972 | 122.9691 | 123.0835 | 59.61 | 59.4589
355.875 | 123.23 | -59.9121 | 63.1531 | -0.094604 | 0.00064726 | 0.063717 | 0.067791 | 0.0017901 | -0.0014527 | 0.00043363 | -0.10611 | 0.0035526 | 0.068753 | 0.062397 | -0.0053962 | 0.0080344 | -0.0024931 | -0.19684 | 63.176 | -60.1318 | 63.1027 | -59.7473 | -60.1456 | -0.009155 | -0.3479 | 63.1577 | -59.9762 | 63.208 | -59.9213 | -60.0266 | -59.7702 | -0.21973 | 0.022888 | -0.050354 | 0.16479 | 59.903 | -0.23346 | 60.1227 | -0.013733 | -0.064087 | 0.004578 | 0.054932 | -0.009156 | 0.14191 | -0.11444 | 0.20599 | -0.050354 | 0.38452 | 123.2346 | 0.054931 | 123.1842 | 123.3078 | 123.1338 | 123.0881 | 123.0698 | -123.2849 | -123.1293 | 123.0148 | 123.1201 | 59.7153 | 59.5642
356.8906 | 123.317 | -59.8618 | 63.1531 | -0.079346 | -0.0010617 | 0.064785 | 0.067577 | -0.0073957 | 0.0017517 | -0.0021298 | -0.057281 | 0.0020572 | 0.069607 | 0.061329 | -0.0058234 | 0.0069662 | -0.00099766 | -0.17395 | 63.1668 | -60.0586 | 63.0066 | -59.9396 | -59.8709 | 0.07782 | -0.20142 | 63.1027 | -59.9075 | 63.2812 | -59.7885 | -59.8709 | -59.6603 | -0.19684 | 0.013733 | -0.14648 | -0.07782 | 59.9396 | -0.009156 | 60.1364 | 0.18768 | -0.045777 | -0.050354 | 0.12817 | 0.073242 | 0.20142 | -0.009156 | 0.24719 | 0.036621 | 0.11902 | 123.0652 | 0.11902 | 123.1888 | 123.2254 | 123.0103 | 123.0286 | 122.9645 | -123.2117 | -123.0606 | 122.8683 | 123.143 | 59.6878 | 59.6603
357.8594 | 123.2666 | -59.903 | 63.1622 | -0.079346 | 0.0017155 | 0.061581 | 0.063732 | 0.0020037 | -0.00081187 | -0.00020717 | -0.032867 | 0.0020572 | 0.068112 | 0.061543 | -0.0058234 | 0.003762 | -0.00078406 | -0.23804 | 63.1485 | -60.0861 | 63.1119 | -59.7519 | -60.1273 | -0.013733 | -0.36163 | 63.0981 | -59.9396 | 63.2446 | -59.8709 | -59.9579 | -59.7153 | -0.18311 | -0.013732 | -0.050354 | 0.15106 | 59.8892 | -0.2243 | 60.0723 | -0.041198 | -0.036621 | -0.064086 | 0.082398 | 0.032043 | 0.18768 | -0.054932 | 0.2243 | -0.018311 | 0.33417 | 123.1979 | 0.068664 | 123.1842 | 123.2346 | 123.0377 | 123.0515 | 123.0011 | -123.2483 | -123.1018 | 123.0148 | 123.1476 | 59.6649 | 59.5413
358.8906 | 123.3078 | -59.8663 | 63.1622 | -0.056457 | 0.0023563 | 0.063076 | 0.065868 | -0.00034607 | -0.0014527 | -0.0034116 | -0.029816 | 0.003339 | 0.070248 | 0.064747 | -0.0049688 | 0.0046164 | -0.0033475 | -0.16022 | 63.1805 | -60.0449 | 63.1897 | -59.6512 | -60.0357 | 0.07782 | -0.20142 | 63.1302 | -59.9304 | 63.2904 | -59.7839 | -59.9075 | -59.6695 | -0.17853 | 0.018311 | 0.027466 | 0.21515 | 59.9442 | -0.16937 | 60.1227 | 0.009155 | -0.064087 | -0.032043 | 0.12817 | 0.082397 | 0.19684 | -0.041199 | 0.26093 | 0.022888 | 0.39368 | 123.2346 | 0.14648 | 123.2208 | 123.2254 | 123.0606 | 123.0469 | 122.9965 | -123.2071 | -123.0927 | 123.056 | 123.1567 | 59.7061 | 59.6649
359.8594 | 123.2529 | -59.8984 | 63.1485 | -0.064087 | 0.0021427 | 0.062863 | 0.06715 | 0.0020037 | -0.0025207 | -0.0027708 | -0.051178 | 0.00034819 | 0.071102 | 0.06902 | -0.0068914 | 0.0063254 | -0.0020657 | -0.2655 | 63.1577 | -60.0769 | 63.1027 | -59.7702 | -60.1456 | -0.068665 | -0.51727 | 63.1073 | -59.9579 | 63.1943 | -59.9213 | -60.022 | -59.7473 | -0.17853 | 0.009155 | -0.045777 | 0.12817 | 59.8297 | -0.24719 | 60.0082 | -0.068665 | -0.05951 | -0.041199 | 0.045776 | -0.022889 | 0.15106 | -0.1236 | 0.21057 | -0.064087 | 0.3067 | 123.1796 | 0.036621 | 123.1522 | 123.2346 | 123.0652 | 123.056 | 123.0057 | -123.2254 | -123.1064 | 123.0011 | 123.0927 | 59.6329 | 59.3811
360.9062 | 123.2025 | -59.9075 | 63.176 | -0.071716 | 0.0021427 | 0.064785 | 0.068859 | 0.0034991 | 0.0011109 | -0.0029844 | -0.10611 | 0.0041934 | 0.06683 | 0.066029 | -0.004328 | 0.0063254 | 0.0022067 | -0.20142 | 63.1805 | -60.0998 | 63.1119 | -59.7519 | -60.141 | -0.018311 | -0.35248 | 63.1622 | -59.9533 | 63.2034 | -59.9167 | -60.0403 | -59.7839 | -0.19226 | 0.004578 | -0.064087 | 0.15564 | 59.8892 | -0.23346 | 60.0815 | -0.041199 | -0.045776 | -0.013733 | 0.027466 | -0.009155 | 0.1236 | -0.13275 | 0.16937 | -0.086975 | 0.3479 | 123.2117 | 0.036621 | 123.1567 | 123.2803 | 123.1155 | 123.0881 | 123.0698 | -123.2758 | -123.1293 | 123.0194 | 123.111 | 59.7061 | 59.5551
361.8594 | 123.3078 | -59.848 | 63.1577 | -0.071716 | 0.0023563 | 0.063504 | 0.0648 | 0.00093573 | -0.0010255 | 0.00022003 | 0.0098572 | 0.0022708 | 0.068112 | 0.066029 | -0.0034736 | 0.0050436 | 0.0051975 | -0.16479 | 63.1622 | -60.0677 | 63.1989 | -59.6558 | -60.0357 | 0.09613 | -0.2243 | 63.1348 | -59.8938 | 63.2812 | -59.7931 | -59.8984 | -59.6649 | -0.21973 | 0.004577 | 0.041199 | 0.19226 | 59.9442 | -0.18768 | 60.1639 | 0.032043 | -0.045777 | -0.022888 | 0.1236 | 0.054931 | 0.1831 | -0.050354 | 0.22888 | -0.004577 | 0.41199 | 123.2666 | 0.10071 | 123.175 | 123.23 | 123.0286 | 123.0103 | 122.9828 | -123.2254 | -123.0515 | 123.0469 | 123.1293 | 59.6832 | 59.6237
362.8906 | 123.2666 | -59.9075 | 63.121 | -0.079346 | 0.0017155 | 0.064358 | 0.066082 | -0.0052595 | -0.0020935 | -0.00020717 | -0.057281 | 0.00098899 | 0.070675 | 0.063252 | -0.0036872 | 0.00483 | 0.0013521 | -0.24261 | 63.1531 | -60.0906 | 63.1165 | -59.7107 | -60.141 | -0.036621 | -0.39368 | 63.1165 | -59.935 | 63.2401 | -59.8984 | -59.9808 | -59.7382 | -0.1831 | 0.032043 | -0.004578 | 0.19684 | 59.8709 | -0.23346 | 60.054 | -0.050354 | -0.027466 | -0.004578 | 0.11902 | 0.009156 | 0.16937 | -0.073242 | 0.19684 | -0.045776 | 0.37994 | 123.2071 | 0.036622 | 123.175 | 123.2437 | 123.0515 | 123.0606 | 123.024 | -123.2117 | -123.056 | 123.024 | 123.1476 | 59.6649 | 59.5139
363.8594 | 123.5413 | -59.8297 | 63.1989 | -0.056457 | -0.00020714 | 0.06329 | 0.065868 | -0.0046185 | -0.0031617 | -0.0027708 | -0.014557 | 0.0018436 | 0.067898 | 0.062611 | -0.0041144 | 0.0067526 | -0.0029203 | -0.20142 | 63.1714 | -60.054 | 63.1577 | -59.697 | -60.0586 | 0.059509 | -0.27466 | 63.1348 | -59.8984 | 63.2767 | -59.7885 | -59.8984 | -59.9213 | -0.2243 | -0.027466 | -0.041199 | 0.13275 | 59.8892 | -0.22888 | 60.1135 | -0.004578 | -0.068664 | -0.064087 | 0.077819 | 0.041199 | -0.091553 | -0.068664 | -0.022889 | 0 | 0.35706 | 123.2117 | 0.10986 | 123.175 | 123.2254 | 123.0331 | 123.0011 | 122.9645 | -123.2529 | -123.0972 | 122.9874 | 123.1064 | 59.6283 | 59.5551
364.9062 | 123.3032 | -59.8755 | 63.1622 | -0.056457 | 0.0017155 | 0.06329 | 0.068859 | 0.0026447 | 0.0015381 | -0.0019162 | -0.07254 | 0.0024844 | 0.067898 | 0.071156 | -0.0066778 | 0.0063254 | 0.0011385 | -0.21057 | 63.2172 | -60.0998 | 63.1027 | -59.7839 | -60.1273 | -0.004578 | -0.33417 | 63.1851 | -59.9579 | 63.2309 | -59.8892 | -60.0128 | -59.7565 | -0.2243 | 0.054932 | -0.059509 | 0.091552 | 59.8709 | -0.25177 | 60.0952 | -0.027466 | -0.082398 | 0.022889 | 0.068665 | -0.013733 | 0.11902 | -0.13733 | 0.20142 | -0.054931 | 0.31586 | 123.2025 | 0.068665 | 123.1888 | 123.317 | 123.143 | 123.0927 | 123.0606 | -123.262 | -123.1201 | 122.9782 | 123.1064 | 59.6649 | 59.5413
365.875 | 123.23 | -59.8801 | 63.1897 | -0.048828 | 0.0025699 | 0.063504 | 0.068646 | 0.0011493 | -0.0033753 | -0.0017026 | -0.10916 | 0.0039798 | 0.070675 | 0.075642 | -0.0017646 | 0.0069662 | -0.00057046 | -0.21515 | 63.208 | -60.0906 | 63.0844 | -59.7565 | -60.1318 | 0 | -0.35706 | 63.176 | -59.9579 | 63.2355 | -59.8892 | -60.0128 | -59.7473 | -0.21057 | 0.018311 | -0.10529 | 0.1236 | 59.8801 | -0.25177 | 60.0906 | -0.041199 | -0.07782 | -0.013733 | 0.045777 | -0.009155 | 0.13275 | -0.13275 | 0.21057 | -0.054931 | 0.33417 | 123.175 | 0.068665 | 123.1934 | 123.2986 | 123.1338 | 123.0881 | 123.056 | -123.2803 | -123.1476 | 122.9645 | 123.1155 | 59.6649 | 59.523
366.8906 | 123.2666 | -59.8572 | 63.1485 | -0.071716 | 0.0034245 | 0.062863 | 0.065014 | 0.00050853 | -0.0023071 | -0.002557 | -0.0023498 | 0.0031254 | 0.066189 | 0.057057 | -0.0062506 | 0.0054708 | -0.00014306 | -0.16937 | 63.1668 | -60.054 | 63.1622 | -59.6832 | -60.054 | 0.073242 | -0.27008 | 63.1531 | -59.9075 | 63.2492 | -59.8297 | -59.9533 | -59.7061 | -0.19684 | 0.01831 | 0.013732 | 0.17395 | 59.9304 | -0.19684 | 60.1273 | 0 | -0.050354 | 0.004577 | 0.10071 | 0.027466 | 0.15106 | -0.09613 | 0.20142 | -0.045776 | 0.37079 | 123.2162 | 0.07782 | 123.1567 | 123.2208 | 123.0606 | 123.024 | 123.0103 | -123.2025 | -123.056 | 123.0194 | 123.1064 | 59.6878 | 59.5871
367.8594 | 123.2941 | -59.8709 | 63.1439 | -0.079346 | 0.00022006 | 0.06329 | 0.066082 | 0.0028583 | -0.0018799 | -0.0027708 | 0.0068054 | 0.0014164 | 0.068112 | 0.054493 | -0.0051824 | 0.0069662 | -0.0029203 | -0.24719 | 63.1485 | -60.0723 | 63.1027 | -59.729 | -60.0998 | 0.018311 | -0.35706 | 63.1119 | -59.9442 | 63.2492 | -59.8206 | -59.935 | -59.6878 | -0.20142 | 0.004578 | -0.041199 | 0.14191 | 59.8892 | -0.22888 | 60.0906 | -0.027465 | -0.073242 | -0.032044 | 0.10529 | 0.050354 | 0.18311 | -0.064087 | 0.25635 | 0.009155 | 0.34332 | 123.175 | 0.1236 | 123.1934 | 123.2208 | 123.056 | 123.0194 | 122.9828 | -123.2162 | -123.0881 | 122.9736 | 123.1201 | 59.6237 | 59.5139
368.8594 | 123.3353 | -59.8434 | 63.1622 | -0.041199 | 0.0019291 | 0.062008 | 0.065441 | -0.0014143 | -0.00059807 | -0.00063437 | -0.0084534 | 0.0024844 | 0.068325 | 0.066242 | -0.0058234 | 0.0056846 | -0.0016385 | -0.17853 | 63.1714 | -60.0494 | 63.1668 | -59.642 | -60.0174 | 0.07782 | -0.24261 | 63.1302 | -59.9396 | 63.2812 | -59.8022 | -59.8846 | -59.6832 | -0.20599 | 0.009156 | 0.004578 | 0.20142 | 59.9213 | -0.17395 | 60.1273 | 0.032043 | -0.09613 | -0.032043 | 0.11902 | 0.041199 | 0.16022 | -0.041199 | 0.25635 | 0.054931 | 0.40741 | 123.2162 | 0.13733 | 123.2208 | 123.2208 | 123.0698 | 123.0148 | 122.9736 | -123.2117 | -123.1018 | 123.0103 | 123.1247 | 59.6649 | 59.6008
369.8906 | 123.317 | -59.8618 | 63.1302 | -0.086975 | 0.0017155 | 0.062436 | 0.059246 | -0.00077327 | 0.0013245 | 0.001929 | 0.025116 | 0.00098899 | 0.067898 | 0.072224 | -0.0056098 | 0.0052572 | -0.00057046 | -0.20599 | 63.1577 | -60.0449 | 62.9379 | -59.5917 | -60.0357 | -0.027466 | -0.28839 | 63.1119 | -59.9167 | 63.2767 | -59.8068 | -59.8892 | -59.6695 | -0.18311 | 0.027466 | -0.19226 | 0.27008 | 59.8343 | -0.17395 | 60.0174 | 0.009155 | -0.054932 | -0.018311 | 0.14648 | 0.054931 | 0.19226 | -0.027466 | 0.24719 | 0.027466 | 0.45319 | 122.9828 | 0.10986 | 123.1934 | 123.2025 | 123.0286 | 123.0194 | 122.9736 | -123.175 | -123.0469 | 122.7997 | 123.1384 | 59.6558 | 59.5734
370.8594 | 123.3261 | -59.8846 | 63.1577 | 0.0045776 | 0.0034245 | 0.065426 | 0.065441 | 0.00050853 | -0.0040161 | -0.0046934 | 0.0068054 | 0.00056179 | 0.068112 | 0.064747 | -0.0062506 | 0.0063254 | -0.0018521 | -0.46234 | 63.1622 | -60.0723 | 63.1393 | -59.6695 | -59.967 | 0.059509 | -0.24261 | 63.1165 | -59.9258 | 63.2721 | -59.7839 | -59.8938 | -59.6649 | -0.18768 | 0.004577 | -0.018311 | 0.21515 | 59.9442 | -0.082397 | 60.1318 | 0.10529 | -0.041198 | -0.041199 | 0.11444 | 0.10071 | 0.21973 | -0.009155 | 0.26093 | 0.032043 | 0.40283 | 123.2117 | 0.14191 | 123.1979 | 123.2346 | 123.0423 | 123.0469 | 123.0011 | -123.23 | -123.0835 | 123.024 | 123.1567 | 59.4223 | 59.642
371.8906 | 123.3215 | -59.9075 | 63.1302 | -0.048828 | 0.00086086 | 0.062649 | 0.066723 | 0.0011493 | -0.0023071 | -0.0023434 | -0.023712 | 0.0018436 | 0.068325 | 0.062824 | -0.0056098 | 0.0054708 | -0.0014249 | -0.28839 | 63.1302 | -60.0861 | 63.1073 | -59.7656 | -60.1593 | -0.064087 | -0.44403 | 63.121 | -59.9396 | 63.327 | -59.7748 | -60.173 | -59.7839 | -0.17853 | 0 | -0.022888 | 0.14191 | 59.8434 | -0.25177 | 60.022 | -0.073242 | -0.032043 | -0.009155 | 0.19684 | 0.13275 | 0.1236 | -0.2655 | 0.15564 | -0.23346 | 0.32044 | 123.1934 | 0.16479 | 123.2666 | 123.2162 | 123.0606 | 123.0377 | 123.0286 | -123.2162 | -123.0698 | 123.0148 | 123.2346 | 59.6191 | 59.4635
372.8594 | 123.3124 | -59.8709 | 63.1485 | -0.086975 | 0.0010745 | 0.062649 | 0.068859 | -0.0016279 | -0.00081187 | 0.00043363 | -0.011505 | 0.0018436 | 0.068112 | 0.064747 | -0.0051824 | 0.0056846 | 0.00049774 | -0.24261 | 63.1805 | -60.0952 | 63.1348 | -59.7198 | -60.0861 | 0.009155 | -0.3479 | 63.121 | -59.9258 | 63.2538 | -59.8343 | -59.9258 | -59.6786 | -0.2243 | 0.032043 | -0.013733 | 0.15106 | 59.8801 | -0.21515 | 60.1044 | 0.009155 | -0.054931 | -0.027466 | 0.10529 | 0.036621 | 0.19226 | -0.054931 | 0.24719 | 0 | 0.37537 | 123.23 | 0.091552 | 123.1796 | 123.2758 | 123.0469 | 123.0515 | 122.9919 | -123.2437 | -123.0743 | 123.0057 | 123.1247 | 59.6283 | 59.523
373.8906 | 123.2574 | -59.8938 | 63.1302 | -0.10223 | 0.0021427 | 0.064145 | 0.067364 | 0.0028583 | -0.00081187 | 0.00022003 | -0.038971 | 0.0020572 | 0.069607 | 0.065388 | -0.0073188 | 0.0063254 | -0.00014306 | -0.26093 | 63.121 | -60.1044 | 63.1027 | -59.7427 | -60.1501 | -0.082397 | -0.43488 | 63.0981 | -59.967 | 63.2172 | -59.9121 | -59.9945 | -59.7427 | -0.21057 | -0.009155 | -0.027466 | 0.15106 | 59.8114 | -0.25635 | 60.022 | -0.045776 | -0.073242 | -0.032043 | 0.086975 | -0.01831 | 0.15106 | -0.10071 | 0.2243 | -0.027466 | 0.36163 | 123.2071 | 0.054932 | 123.1842 | 123.2254 | 123.0652 | 123.0148 | 122.9919 | -123.2346 | -123.0972 | 122.9965 | 123.111 | 59.6329 | 59.4589
374.8594 | 123.3124 | -59.8297 | 63.1577 | -0.094604 | 0.0023563 | 0.062649 | 0.067791 | 0.0015765 | -0.0038025 | -0.0010618 | -0.014557 | 0.0022708 | 0.069607 | 0.063038 | -0.0073188 | 0.0039756 | 0.0013521 | -0.17853 | 63.1577 | -60.054 | 63.1897 | -59.6649 | -60.0449 | 0.082397 | -0.25177 | 63.1027 | -59.9442 | 63.2675 | -59.7931 | -59.8938 | -59.6741 | -0.2243 | 0 | 0.032043 | 0.16479 | 59.9121 | -0.21515 | 60.1364 | 0.009155 | -0.11444 | -0.054932 | 0.10986 | 0.036621 | 0.15564 | -0.064087 | 0.27008 | 0.050354 | 0.3891 | 123.2437 | 0.15106 | 123.2117 | 123.2117 | 123.0469 | 122.9874 | 122.9324 | -123.2117 | -123.1018 | 123.0194 | 123.0972 | 59.6512 | 59.5779
375.8906 | 123.3398 | -59.903 | 63.0936 | -0.12512 | 0.0040653 | 0.062863 | 0.067364 | 0.0039263 | -0.0012391 | 0.00064723 | -0.10306 | 0.00034819 | 0.068753 | 0.06902 | -0.0073188 | 0.0073936 | -0.0035611 | -0.28839 | 63.1073 | -60.1227 | 63.0112 | -59.9716 | -59.8206 | 0.041199 | -0.40741 | 63.121 | -59.9304 | 63.2629 | -59.848 | -59.9899 | -59.729 | -0.21973 | 0.013733 | -0.082398 | -0.068665 | 59.9442 | 0.082397 | 60.1639 | 0.30212 | -0.027466 | 0.027466 | 0.16937 | 0.054932 | 0.17395 | -0.086975 | 0.20142 | -0.059509 | 0.15106 | 123.1338 | 0.082398 | 123.1934 | 123.23 | 123.0515 | 123.0103 | 123.024 | -123.2162 | -123.024 | 122.9141 | 123.1659 | 59.6146 | 59.4955
376.8594 | 123.3032 | -59.8389 | 63.1714 | -0.086975 | 0.0017155 | 0.064145 | 0.065228 | -0.00013247 | -0.00081187 | -0.002557 | 0.0037536 | 0.0014164 | 0.070248 | 0.068165 | -0.0056098 | 0.0052572 | -0.0022793 | -0.20142 | 63.176 | -60.0769 | 63.1805 | -59.6558 | -60.0403 | 0.07782 | -0.27924 | 63.1348 | -59.9442 | 63.2858 | -59.7931 | -59.903 | -59.6741 | -0.23804 | 0.004577 | 0.009155 | 0.1831 | 59.9167 | -0.20142 | 60.1547 | 0.036621 | -0.10529 | -0.036621 | 0.11444 | 0.045776 | 0.16479 | -0.064087 | 0.27008 | 0.041199 | 0.42114 | 123.2574 | 0.15106 | 123.23 | 123.2529 | 123.0789 | 123.0148 | 122.9736 | -123.2483 | -123.1155 | 123.0194 | 123.1247 | 59.6375 | 59.5596
377.8906 | 123.2483 | -59.8618 | 63.1393 | -0.048828 | 0.0034245 | 0.062649 | 0.065441 | -0.0018415 | -0.00038447 | -0.0017026 | -0.038971 | 0.0018436 | 0.070034 | 0.065388 | -0.0049688 | 0.0056846 | -0.0042021 | -0.31128 | 63.1165 | -60.0861 | 63.0753 | -59.8251 | -60.1593 | -0.059509 | -0.46692 | 63.121 | -59.9625 | 63.2034 | -59.9121 | -60.0128 | -59.7519 | -0.22431 | -0.022888 | -0.064087 | 0.036621 | 59.8022 | -0.29755 | 60.0266 | -0.073242 | -0.10071 | -0.01831 | 0.064087 | -0.050354 | 0.10986 | -0.15106 | 0.21057 | -0.050354 | 0.26093 | 123.1613 | 0.050354 | 123.1659 | 123.2025 | 123.0835 | 122.9782 | 122.9828 | -123.2254 | -123.1018 | 122.937 | 123.0652 | 59.5505 | 59.3948
378.8594 | 123.3307 | -59.8663 | 63.1485 | -0.10223 | 0.0025699 | 0.06094 | 0.065655 | -0.0014143 | -0.00059807 | -0.00042077 | -0.0023498 | 0.00098899 | 0.068753 | 0.065174 | -0.0064642 | 0.0056846 | 0.0019931 | -0.20142 | 63.1668 | -60.0403 | 63.1805 | -59.6695 | -60.0403 | 0.07782 | -0.27924 | 63.1485 | -59.9396 | 63.2904 | -59.7794 | -59.8892 | -59.6786 | -0.17395 | 0.01831 | 0.032043 | 0.19684 | 59.9442 | -0.17395 | 60.1181 | 0 | -0.073242 | 0 | 0.14191 | 0.086975 | 0.18768 | -0.022888 | 0.26093 | 0.050354 | 0.37079 | 123.2208 | 0.16022 | 123.23 | 123.2071 | 123.0881 | 123.0331 | 123.0148 | -123.1888 | -123.0881 | 123.0469 | 123.1567 | 59.6649 | 59.5871
379.8906 | 123.3032 | -59.848 | 63.1393 | -0.064087 | 0.0017155 | 0.063076 | 0.066296 | 0.00029473 | -0.0031617 | -0.0019162 | -0.0054016 | 0.0020572 | 0.068539 | 0.058338 | -0.0058234 | 0.0052572 | 0.0013521 | -0.23804 | 63.1668 | -60.0861 | 63.1302 | -59.7061 | -60.0906 | 0.018311 | -0.33875 | 63.121 | -59.9442 | 63.2812 | -59.816 | -59.9213 | -59.6878 | -0.23804 | 0.027466 | -0.009155 | 0.14191 | 59.8663 | -0.24262 | 60.1044 | -0.004577 | -0.096131 | -0.01831 | 0.14191 | 0.032043 | 0.16022 | -0.073243 | 0.25635 | 0.022888 | 0.37994 | 123.2162 | 0.12817 | 123.2254 | 123.2529 | 123.0652 | 123.0148 | 122.9691 | -123.2254 | -123.0835 | 122.9782 | 123.1293 | 59.61 | 59.5093
380.8594 | 123.3032 | -59.8389 | 63.1485 | -0.079346 | 0.0010745 | 0.062436 | 0.066082 | -0.00013247 | -0.0027345 | -0.0027708 | -0.029816 | 0.0014164 | 0.067684 | 0.062184 | -0.004328 | 0.0061118 | -0.0018521 | -0.19684 | 63.1668 | -60.0632 | 63.1851 | -59.6603 | -60.0311 | 0.064087 | -0.28839 | 63.1119 | -59.9533 | 63.295 | -59.7931 | -59.903 | -59.6741 | -0.2243 | 0.01831 | 0.036621 | 0.17853 | 59.903 | -0.19226 | 60.1273 | 0.032043 | -0.11444 | -0.036622 | 0.14648 | 0.045776 | 0.16479 | -0.064087 | 0.27924 | 0.050354 | 0.40283 | 123.2483 | 0.16022 | 123.2483 | 123.23 | 123.0652 | 123.0057 | 122.9507 | -123.2117 | -123.1018 | 123.024 | 123.1338 | 59.642 | 59.5505
381.8594 | 123.3124 | -59.8526 | 63.1577 | -0.033569 | 0.0012881 | 0.063076 | 0.066723 | -0.00098687 | -0.00081187 | -0.002557 | -0.029816 | 0.00163 | 0.069607 | 0.065174 | -0.0062506 | 0.003762 | 0.0011385 | -0.20599 | 63.1805 | -60.0677 | 63.1805 | -59.6603 | -60.0449 | 0.068665 | -0.27924 | 63.1348 | -59.9304 | 63.2767 | -59.7977 | -59.8984 | -59.6649 | -0.21515 | 0.022888 | 0.022888 | 0.19226 | 59.9213 | -0.19226 | 60.1364 | 0.022888 | -0.07782 | -0.022888 | 0.11902 | 0.054932 | 0.18768 | -0.045776 | 0.2655 | 0.032044 | 0.40741 | 123.2483 | 0.13275 | 123.2071 | 123.2483 | 123.0652 | 123.0331 | 122.9874 | -123.2254 | -123.0881 | 123.0331 | 123.1293 | 59.6466 | 59.5734
382.8906 | 123.2895 | -59.8801 | 63.1622 | -0.010681 | 0.0015019 | 0.062436 | 0.06715 | -0.00034607 | -0.0025207 | 6.432e-06 | -0.029816 | 0.00013459 | 0.068753 | 0.06966 | -0.0045416 | 0.0044028 | -0.00035666 | -0.19684 | 63.1851 | -60.0586 | 63.1851 | -59.6695 | -60.0449 | 0.073242 | -0.29755 | 63.1348 | -59.9258 | 63.2538 | -59.8206 | -59.9533 | -59.6924 | -0.17853 | 0.022889 | 0.022889 | 0.21057 | 59.9533 | -0.16479 | 60.1318 | 0.013733 | -0.045776 | -0.027465 | 0.091553 | 0.059509 | 0.18768 | -0.073242 | 0.23346 | -0.027466 | 0.3891 | 123.2437 | 0.10529 | 123.1796 | 123.2437 | 123.0606 | 123.0652 | 123.0148 | -123.2208 | -123.0881 | 123.0652 | 123.1338 | 59.6832 | 59.5825
383.8594 | 123.2986 | -59.8938 | 63.1256 | -0.071716 | 0.0023563 | 0.062649 | 0.065655 | -0.00013247 | -0.0025207 | -0.0038388 | -0.02066 | 0.0024844 | 0.069821 | 0.065815 | -0.0041144 | 0.0044028 | 0.0030611 | -0.23804 | 63.1348 | -60.0723 | 63.1622 | -59.6695 | -60.054 | 0.041199 | -0.51727 | 63.1439 | -59.8984 | 63.2538 | -59.8709 | -59.8434 | -59.6283 | -0.17853 | 0.009156 | 0.036621 | 0.2243 | 59.935 | -0.16022 | 60.1135 | 0.018311 | -0.004577 | 0.018311 | 0.12817 | 0.022888 | 0.2655 | 0.050354 | 0.27008 | 0.054931 | 0.40283 | 123.2346 | 0.027465 | 123.1522 | 123.2071 | 123.0423 | 123.0286 | 123.0377 | -123.1979 | -123.024 | 123.056 | 123.1476 | 59.6558 | 59.3765
384.8906 | 123.2483 | -59.8755 | 63.1668 | -0.056457 | 0.0023563 | 0.062008 | 0.066082 | 0.0026447 | -0.0031617 | -0.0029844 | -0.12137 | 0.0020572 | 0.068539 | 0.064106 | -0.004328 | 0.0095298 | -0.00057046 | -0.24261 | 63.2309 | -60.1044 | 63.0981 | -59.7748 | -60.1227 | -0.013733 | -0.3891 | 63.1439 | -59.9396 | 63.0478 | -59.6924 | -60.0311 | -59.816 | -0.22888 | 0.064087 | -0.068664 | 0.10071 | 59.8618 | -0.24719 | 60.0906 | -0.018311 | -0.064087 | -0.022888 | -0.11902 | 0.1831 | 0.059509 | -0.15564 | 0.1236 | -0.091553 | 0.32959 | 123.2025 | 0.24719 | 122.9874 | 123.3353 | 123.0835 | 123.1064 | 123.0194 | -123.2712 | -123.1064 | 122.9736 | 122.9233 | 59.6329 | 59.4864
385.8594 | 123.3078 | -59.8526 | 63.1393 | -0.064087 | 0.0029971 | 0.061367 | 0.066723 | 0.0011493 | -0.0014527 | 6.432e-06 | 0.21127 | 0.00034819 | 0.072384 | 0.064106 | -0.0068914 | 0.0052572 | -0.00078406 | -0.23804 | 63.1577 | -60.0815 | 63.1622 | -59.6741 | -60.0449 | 0.091553 | -0.64545 | 63.1348 | -59.9258 | 63.2812 | -59.8297 | -59.8526 | -59.6786 | -0.22888 | 0.018311 | 0.022888 | 0.17853 | 59.9442 | -0.19226 | 60.173 | 0.036621 | -0.073242 | -0.004577 | 0.14191 | 0.022888 | 0.17395 | 0 | 0.24719 | 0.073242 | 0.40741 | 123.2437 | 0.09613 | 123.2071 | 123.2391 | 123.0606 | 123.0103 | 122.9874 | -123.2208 | -123.0652 | 123.0148 | 123.1338 | 59.6146 | 59.2072
386.8594 | 123.3032 | -59.8663 | 63.1668 | -0.056457 | 0.0010745 | 0.06094 | 0.066296 | -0.0018415 | 0.00046993 | -0.0019162 | -0.0054016 | 0.0022708 | 0.070889 | 0.060475 | -0.0049688 | 0.0069662 | 0.0015659 | -0.21515 | 63.1485 | -60.0906 | 63.176 | -59.6558 | -60.0357 | 0.068665 | -0.29755 | 63.1165 | -59.9442 | 63.2767 | -59.8068 | -59.9121 | -59.6832 | -0.2243 | -0.01831 | 0.009155 | 0.21057 | 59.935 | -0.16937 | 60.1593 | 0.054931 | -0.07782 | -0.050354 | 0.10986 | 0.059509 | 0.1831 | -0.045776 | 0.26093 | 0.032044 | 0.43487 | 123.2666 | 0.13733 | 123.2208 | 123.2391 | 123.0606 | 123.0148 | 122.9828 | -123.2574 | -123.111 | 123.0423 | 123.143 | 59.6512 | 59.5688
387.8906 | 123.2941 | -59.8892 | 63.1714 | -0.064087 | -0.00063454 | 0.064572 | 0.066082 | 0.0054217 | -0.0035889 | -0.0023434 | -0.048126 | 0.0039798 | 0.068966 | 0.068592 | -0.0047552 | 0.0054708 | 0.0019931 | -0.19684 | 63.1668 | -60.0449 | 63.1622 | -59.6832 | -60.054 | 0.054932 | -0.32959 | 63.1439 | -59.9396 | 63.2355 | -59.8389 | -59.9579 | -59.7244 | -0.15564 | -0.004578 | -0.009156 | 0.20599 | 59.9442 | -0.16479 | 60.0998 | -0.009155 | -0.050354 | -0.027466 | 0.064087 | 0.050354 | 0.16479 | -0.068665 | 0.21515 | -0.018311 | 0.36163 | 123.2071 | 0.10071 | 123.175 | 123.2117 | 123.0835 | 123.056 | 123.0331 | -123.2162 | -123.111 | 123.0515 | 123.1247 | 59.6924 | 59.5596
388.8594 | 123.1979 | -59.9121 | 63.1805 | 0.019837 | -0.0012753 | 0.065213 | 0.068646 | 0.00093573 | -0.0038025 | -0.0027708 | -0.038971 | 0.0018436 | 0.068753 | 0.061115 | -0.0028326 | 0.0058982 | -0.00099766 | -0.34332 | 63.2401 | -60.0998 | 63.0615 | -59.8114 | -60.1822 | -0.018311 | -0.42114 | 63.176 | -59.9625 | 63.1668 | -59.9442 | -60.0449 | -59.7794 | -0.18768 | 0.059509 | -0.11902 | 0.10071 | 59.8938 | -0.27008 | 60.0815 | -0.082398 | -0.050354 | -0.004578 | -0.013733 | -0.032044 | 0.13275 | -0.13275 | 0.1831 | -0.082398 | 0.28839 | 123.1613 | 0.01831 | 123.1293 | 123.3398 | 123.1384 | 123.1522 | 123.0881 | -123.2803 | -123.143 | 122.9736 | 123.0789 | 59.5688 | 59.491
389.8906 | 123.2758 | -59.9167 | 63.1439 | -0.071716 | 0.0019291 | 0.062436 | 0.065655 | 0.0043537 | -0.0025207 | 0.00022003 | -0.023712 | 0.0020572 | 0.068325 | 0.070301 | -0.0053962 | 0.0061118 | 0.0015659 | -0.32044 | 63.1622 | -60.0952 | 63.0753 | -59.7839 | -60.1364 | -0.059509 | -0.50354 | 63.1256 | -60.0037 | 63.2034 | -59.8984 | -60.0037 | -59.7565 | -0.17853 | 0.01831 | -0.068665 | 0.13275 | 59.8572 | -0.21973 | 60.0357 | -0.041199 | -0.086975 | -0.018311 | 0.059509 | 0.018311 | 0.16022 | -0.086975 | 0.24719 | 0 | 0.31128 | 123.1705 | 0.10529 | 123.2071 | 123.2574 | 123.1293 | 123.0789 | 123.0423 | -123.2391 | -123.1476 | 122.9919 | 123.1201 | 59.5963 | 59.4131
390.8594 | 123.175 | -59.9075 | 63.1851 | 0.042725 | 0.0044925 | 0.061795 | 0.065014 | 0.0024311 | -0.0044433 | -0.00020717 | -0.048126 | 0.0020572 | 0.068112 | 0.061756 | -0.0036872 | 0.0046164 | -0.0035611 | -0.3067 | 63.1989 | -60.1181 | 63.0569 | -59.8022 | -60.1501 | 0 | -0.44861 | 63.176 | -59.9716 | 63.1531 | -59.9487 | -60.054 | -59.8022 | -0.21057 | 0.013733 | -0.12817 | 0.10529 | 59.9075 | -0.24261 | 60.1181 | -0.032043 | -0.064087 | -0.009156 | -0.032044 | -0.041198 | 0.10529 | -0.14648 | 0.16937 | -0.082397 | 0.31586 | 123.175 | 0.022889 | 123.1247 | 123.317 | 123.1476 | 123.1064 | 123.0835 | -123.3032 | -123.1567 | 122.9645 | 123.0606 | 59.6008 | 59.4589
391.9062 | 123.2254 | -59.8846 | 63.1714 | -0.079346 | 0.0010745 | 0.064358 | 0.068005 | 0.0020037 | -0.0016663 | 0.0015018 | -0.12442 | 0.002698 | 0.06683 | 0.067738 | -0.0019782 | 0.0050436 | -0.0012113 | -0.32501 | 63.1622 | -60.1273 | 63.0432 | -59.8572 | -60.2417 | -0.1236 | -0.57678 | 63.1668 | -59.9854 | 63.1439 | -59.6924 | -60.2051 | -59.9258 | -0.24261 | -0.009156 | -0.12817 | 0.027466 | 59.761 | -0.35705 | 60.0037 | -0.11444 | -0.10071 | -0.004578 | -0.027466 | 0.19226 | -0.041198 | -0.32043 | 0.05951 | -0.21973 | 0.27008 | 123.1705 | 0.29297 | 123.1293 | 123.2895 | 123.1522 | 123.0469 | 123.0515 | -123.2986 | -123.1567 | 122.9279 | 123.0286 | 59.5596 | 59.3079
392.8594 | 123.2254 | -59.903 | 63.1943 | -0.056457 | 0.0051333 | 0.064145 | 0.066296 | -0.00013247 | 4.273e-05 | -0.00084817 | -0.048126 | 0.0039798 | 0.070034 | 0.067738 | -0.0045416 | 0.0078208 | -0.0029203 | -0.26093 | 63.1989 | -60.0906 | 63.0478 | -59.8206 | -60.1501 | -0.027466 | -0.45776 | 63.1897 | -59.9808 | 63.1851 | -59.8938 | -60.0082 | -59.7794 | -0.18768 | 0.004578 | -0.14648 | 0.082397 | 59.8755 | -0.24719 | 60.0632 | -0.059509 | -0.07782 | -0.004578 | -0.009155 | 0.009155 | 0.1236 | -0.10529 | 0.20142 | -0.027466 | 0.27008 | 123.1384 | 0.086975 | 123.1659 | 123.2895 | 123.1705 | 123.1018 | 123.0927 | -123.2849 | -123.175 | 122.9507 | 123.0881 | 59.642 | 59.4452
393.8594 | 123.3032 | -59.8801 | 63.1439 | -0.048828 | 6.46e-06 | 0.065426 | 0.066296 | -0.00098687 | -0.0012391 | -0.00042077 | 0.0098572 | 0.00013459 | 0.06918 | 0.062611 | -0.0049688 | 0.0080344 | -0.00014306 | -0.23346 | 63.1485 | -60.0906 | 63.1851 | -59.6603 | -60.0449 | 0.050354 | -0.32501 | 63.1393 | -59.9487 | 63.2812 | -59.8022 | -59.8938 | -59.6786 | -0.21057 | 0.004578 | 0.041199 | 0.21973 | 59.9304 | -0.16479 | 60.141 | 0.045776 | -0.068664 | -0.004578 | 0.13733 | 0.07782 | 0.20142 | -0.013733 | 0.27008 | 0.054931 | 0.4303 | 123.2758 | 0.14648 | 123.23 | 123.2391 | 123.0881 | 123.0286 | 123.0194 | -123.2346 | -123.0927 | 123.0652 | 123.1613 | 59.6466 | 59.5551
394.8594 | 123.2117 | -59.8801 | 63.1943 | -0.041199 | 0.00086086 | 0.063717 | 0.065441 | 0.0022173 | -0.0014527 | -0.0010618 | -0.035919 | 0.0039798 | 0.069821 | 0.066029 | -0.0045416 | 0.0044028 | 0.00028414 | -0.27008 | 63.2217 | -60.1044 | 63.0524 | -59.8068 | -60.1593 | -0.041199 | -0.45319 | 63.1622 | -59.967 | 63.1531 | -59.9304 | -60.0494 | -59.7839 | -0.2243 | 0.027466 | -0.14191 | 0.073242 | 59.8389 | -0.27924 | 60.0632 | -0.054932 | -0.086975 | -0.032044 | -0.041199 | -0.050354 | 0.09613 | -0.16937 | 0.18311 | -0.082397 | 0.29755 | 123.1567 | 0.036621 | 123.1201 | 123.3261 | 123.1293 | 123.1018 | 123.0423 | -123.2986 | -123.1613 | 122.9324 | 123.0331 | 59.61 | 59.4269
395.8594 | 123.2346 | -59.903 | 63.176 | -0.086975 | 0.0021427 | 0.063717 | 0.067364 | 0.0022173 | -0.0031617 | -0.0046934 | -0.063385 | 0.0020572 | 0.072384 | 0.060902 | -0.0039008 | 0.0050436 | 0.00071134 | -0.25177 | 63.2126 | -60.1089 | 63.0753 | -59.7839 | -60.1227 | -0.004578 | -0.38452 | 63.2263 | -59.9213 | 63.1668 | -59.935 | -60.0494 | -59.8114 | -0.20599 | 0.036621 | -0.10071 | 0.11902 | 59.8984 | -0.21973 | 60.1044 | -0.013733 | -0.018311 | 0.050354 | -0.009155 | -0.032044 | 0.091553 | -0.14648 | 0.10986 | -0.12817 | 0.32501 | 123.1842 | -0.013733 | 123.0881 | 123.3215 | 123.1476 | 123.1155 | 123.1293 | -123.2849 | -123.0972 | 122.9782 | 123.0698 | 59.6512 | 59.5184
396.9062 | 123.1888 | -59.9121 | 63.1531 | -0.064087 | 6.46e-06 | 0.062863 | 0.066723 | 0.0026447 | -0.0010255 | -0.0012754 | -0.093903 | 0.0031254 | 0.06918 | 0.069233 | -0.0068914 | 0.0071798 | -0.0027067 | -0.30212 | 63.1577 | -60.1135 | 63.0569 | -59.8206 | -60.1913 | -0.10529 | -0.52185 | 63.1393 | -59.9762 | 63.1622 | -59.9716 | -60.0677 | -59.7977 | -0.20142 | 0.004578 | -0.09613 | 0.091552 | 59.8068 | -0.27924 | 60.0082 | -0.07782 | -0.064087 | -0.013733 | 0.009155 | -0.05951 | 0.11444 | -0.15564 | 0.17853 | -0.091553 | 0.29297 | 123.1705 | 0.004577 | 123.1384 | 123.2712 | 123.1155 | 123.0698 | 123.0515 | -123.2666 | -123.1293 | 122.9691 | 123.0743 | 59.61 | 59.3903
397.8594 | 123.2254 | -59.8846 | 63.208 | -0.056457 | 0.0017155 | 0.061795 | 0.067791 | -0.0018415 | -0.0023071 | 0.0023562 | -0.14578 | 0.0020572 | 0.068325 | 0.061329 | -0.0032598 | 0.0056846 | 0.00028414 | -0.24719 | 63.2126 | -60.0632 | 63.0295 | -59.7473 | -59.9487 | 0.20599 | -0.46692 | 63.176 | -59.9579 | 63.1485 | -59.9075 | -60.0632 | -59.8022 | -0.17853 | 0.004577 | -0.17853 | 0.13733 | 60.0906 | -0.064086 | 60.2692 | 0.11444 | -0.073242 | -0.032044 | -0.059509 | -0.022888 | 0.082398 | -0.17853 | 0.15564 | -0.10528 | 0.31586 | 123.0927 | 0.050354 | 123.1064 | 123.2758 | 123.1338 | 123.0972 | 123.0606 | -123.2712 | -123.1659 | 122.9141 | 123.0331 | 59.6375 | 59.4177
398.8906 | 123.317 | -59.8618 | 63.1302 | -0.094604 | 0.0025699 | 0.061367 | 0.065655 | 0.0024311 | 0.00089713 | -0.0040524 | 0.028168 | 0.00034819 | 0.068539 | 0.061543 | -0.0041144 | 0.0056846 | 0.0028475 | -0.27924 | 63.1668 | -60.0815 | 63.1302 | -59.7061 | -60.0906 | 0 | -0.41657 | 63.0936 | -59.9716 | 63.2538 | -59.8343 | -59.8938 | -59.6603 | -0.21973 | 0.036621 | 0 | 0.15564 | 59.8618 | -0.22888 | 60.0815 | -0.009155 | -0.10986 | -0.036621 | 0.1236 | 0.027465 | 0.20142 | -0.032044 | 0.31128 | 0.07782 | 0.37537 | 123.2117 | 0.13733 | 123.2254 | 123.2483 | 123.0652 | 123.0286 | 122.9553 | -123.2117 | -123.1018 | 122.9919 | 123.1155 | 59.5825 | 59.4452
399.8594 | 123.1888 | -59.8984 | 63.1943 | -0.056457 | -0.00020714 | 0.062222 | 0.067791 | 0.00050853 | 0.00068353 | -0.00020717 | -0.026764 | 0.0031254 | 0.070034 | 0.071583 | -0.0045416 | 0.0058982 | -0.0024931 | -0.29297 | 63.2172 | -60.1135 | 63.0569 | -59.8068 | -60.1776 | -0.045776 | -0.46234 | 63.1714 | -59.9579 | 63.1485 | -59.9304 | -60.0311 | -59.7794 | -0.21515 | 0.022888 | -0.13733 | 0.091552 | 59.8526 | -0.27924 | 60.0677 | -0.064087 | -0.05951 | -0.022888 | -0.045776 | -0.032044 | 0.11902 | -0.13275 | 0.17853 | -0.073242 | 0.3067 | 123.1705 | 0.027466 | 123.1064 | 123.3307 | 123.1293 | 123.1155 | 123.0698 | -123.3078 | -123.1522 | 122.9553 | 123.0469 | 59.6054 | 59.436
400.8906 | 123.2071 | -59.9121 | 63.1805 | -0.056457 | 0.0015019 | 0.06329 | 0.068218 | -0.00013247 | -0.0020935 | -0.0019162 | -0.026764 | 0.0012028 | 0.070889 | 0.069874 | -0.0053962 | 0.0052572 | 0.0019931 | -0.30212 | 63.2355 | -60.1227 | 63.0478 | -59.8114 | -60.1685 | -0.045776 | -0.4715 | 63.1668 | -59.9579 | 63.1622 | -59.9442 | -60.0311 | -59.7748 | -0.21057 | 0.054932 | -0.13275 | 0.10071 | 59.8663 | -0.25635 | 60.0769 | -0.045776 | -0.045777 | -0.013733 | -0.018311 | -0.032044 | 0.13733 | -0.11902 | 0.18311 | -0.073242 | 0.31128 | 123.1705 | 0.013733 | 123.1201 | 123.3582 | 123.1247 | 123.1476 | 123.0789 | -123.3032 | -123.1384 | 122.9599 | 123.0743 | 59.61 | 59.4406
401.8594 | 123.2483 | -59.8938 | 63.1897 | -0.071716 | 0.0015019 | 0.061795 | 0.068218 | 0.00050853 | -0.0023071 | 0.0015018 | -0.048126 | 0.0018436 | 0.070034 | 0.06667 | -0.0045416 | 0.006539 | -0.00035666 | -0.27924 | 63.2217 | -60.0861 | 63.0753 | -59.7885 | -60.1639 | -0.054932 | -0.46234 | 63.1897 | -59.935 | 63.1989 | -59.8984 | -60.0128 | -59.761 | -0.19226 | 0.032044 | -0.11444 | 0.10529 | 59.8389 | -0.27008 | 60.0311 | -0.077819 | -0.041199 | 0 | 0.009156 | -0.004577 | 0.13275 | -0.11902 | 0.17395 | -0.077819 | 0.29755 | 123.1613 | 0.036622 | 123.1339 | 123.3078 | 123.1247 | 123.1155 | 123.0835 | -123.2758 | -123.1247 | 122.9691 | 123.0927 | 59.6146 | 59.4315
402.8906 | 123.2117 | -59.9075 | 63.1851 | -0.041199 | 0.0012881 | 0.061367 | 0.066082 | 0.0017901 | -0.00017087 | -0.0017026 | -0.045074 | 0.002698 | 0.069821 | 0.063679 | -0.0058234 | 0.0071798 | -0.00099766 | -0.28381 | 63.208 | -60.0815 | 63.0432 | -59.8114 | -60.1501 | -0.027466 | -0.48065 | 63.176 | -59.9625 | 63.1805 | -59.903 | -60.022 | -59.7748 | -0.17395 | 0.022888 | -0.14191 | 0.096131 | 59.8801 | -0.24261 | 60.054 | -0.068664 | -0.054931 | -0.009156 | -0.004578 | 0.004578 | 0.13275 | -0.11444 | 0.18768 | -0.05951 | 0.27008 | 123.1247 | 0.059509 | 123.143 | 123.2895 | 123.1384 | 123.1155 | 123.0835 | -123.2666 | -123.1476 | 122.9507 | 123.0881 | 59.6237 | 59.4269
403.8594 | 123.1659 | -59.8846 | 63.1851 | -0.010681 | 0.0010745 | 0.064358 | 0.067577 | -0.0024823 | -0.0029481 | -0.002557 | -0.011505 | 0.0022708 | 0.068539 | 0.062397 | -0.0039008 | 0.0041892 | 0.0019931 | -0.29297 | 63.2172 | -60.0906 | 63.0569 | -59.8022 | -60.1639 | -0.036621 | -0.47607 | 63.1897 | -59.967 | 63.1577 | -59.9304 | -60.0494 | -59.7885 | -0.20599 | 0.032043 | -0.12817 | 0.082398 | 59.848 | -0.27923 | 60.054 | -0.073242 | -0.082397 | 0.004577 | -0.027466 | -0.045776 | 0.096131 | -0.16479 | 0.17853 | -0.082397 | 0.28839 | 123.1476 | 0.036621 | 123.1247 | 123.3078 | 123.1567 | 123.1018 | 123.0743 | -123.2758 | -123.1522 | 122.9416 | 123.0423 | 59.5917 | 59.4086
404.9062 | 123.1659 | -59.9442 | 63.1348 | -0.048828 | 0.0023563 | 0.063717 | 0.070141 | 0.0030719 | -0.0027345 | -0.0027708 | -0.078644 | 0.004407 | 0.071316 | 0.067311 | -0.0041144 | 0.0046164 | -0.0024931 | -0.37537 | 63.1897 | -60.1501 | 63.3179 | -59.7519 | -60.3699 | -0.10986 | -0.6134 | 63.1577 | -59.9945 | 63.1027 | -59.9991 | -60.1227 | -59.8297 | -0.20599 | 0.054931 | 0.1831 | 0.19226 | 59.8343 | -0.42572 | 60.0403 | -0.21973 | -0.050354 | 0.022888 | -0.032044 | -0.054931 | 0.11444 | -0.17853 | 0.16479 | -0.12817 | 0.39825 | 123.468 | -0.004577 | 123.0972 | 123.3398 | 123.1522 | 123.1338 | 123.1018 | -123.2849 | -123.1293 | 123.262 | 123.0469 | 59.5688 | 59.3308
405.8594 | 123.2254 | -59.903 | 63.1943 | -0.02594 | 0.0012881 | 0.062008 | 0.066082 | -0.0012005 | -0.0025207 | -0.0027708 | -0.0084534 | 0.0022708 | 0.072598 | 0.070301 | -0.004328 | 0.0069662 | 0.00092494 | -0.28839 | 63.2355 | -60.1135 | 63.0478 | -59.8114 | -60.1501 | -0.050354 | -0.47607 | 63.1714 | -59.9716 | 63.1531 | -59.9487 | -60.0311 | -59.7885 | -0.21057 | 0.041199 | -0.14648 | 0.091553 | 59.8526 | -0.24719 | 60.0632 | -0.036621 | -0.068665 | -0.022888 | -0.041199 | -0.045776 | 0.11444 | -0.12817 | 0.18311 | -0.059509 | 0.30212 | 123.1613 | 0.022889 | 123.1247 | 123.349 | 123.143 | 123.1384 | 123.0743 | -123.3078 | -123.1659 | 122.9507 | 123.056 | 59.6146 | 59.4269
406.8906 | 123.1888 | -59.8984 | 63.1668 | -0.071716 | 0.0019291 | 0.065213 | 0.068005 | 0.0013629 | 0.0023925 | -0.0010618 | -0.07254 | 0.0024844 | 0.068325 | 0.062824 | -0.0051824 | 0.0078208 | 0.0019931 | -0.27008 | 63.1897 | -60.1318 | 63.0753 | -59.7519 | -60.1501 | -0.059509 | -0.46692 | 63.1439 | -59.9579 | 63.1897 | -59.8984 | -60.0403 | -59.7656 | -0.23346 | 0.022888 | -0.091553 | 0.14648 | 59.8389 | -0.25177 | 60.0723 | -0.01831 | -0.05951 | -0.022888 | 0.022888 | 0 | 0.13275 | -0.14191 | 0.19226 | -0.082397 | 0.37994 | 123.2071 | 0.05951 | 123.1476 | 123.3215 | 123.1018 | 123.0881 | 123.0423 | -123.2986 | -123.1247 | 122.9736 | 123.0881 | 59.6283 | 59.4315
407.8594 | 123.2025 | -59.9121 | 63.1897 | -0.056457 | 0.0015019 | 0.062222 | 0.0648 | -0.0076093 | -0.0023071 | -0.002557 | -0.032867 | 0.00163 | 0.068753 | 0.065174 | -0.0056098 | 0.0069662 | -0.00099766 | -0.27008 | 63.2172 | -60.0861 | 62.9929 | -60.0357 | -60.1959 | -0.004578 | -0.44861 | 63.1622 | -59.9304 | 63.1393 | -59.8984 | -59.9854 | -59.7702 | -0.17395 | 0.027466 | -0.19684 | -0.1236 | 59.9075 | -0.28381 | 60.0815 | -0.10986 | -0.018311 | -0.027466 | -0.050354 | 0.013733 | 0.14191 | -0.073243 | 0.16022 | -0.054932 | 0.050354 | 123.0789 | 0.032044 | 123.0698 | 123.3032 | 123.0927 | 123.1293 | 123.0743 | -123.2758 | -123.1201 | 122.905 | 123.0515 | 59.642 | 59.4635
408.8906 | 123.2208 | -59.8755 | 63.2034 | -0.094604 | 0.0017155 | 0.062863 | 0.066723 | 0.0013629 | -0.0027345 | -0.0012754 | -0.017609 | 0.0031254 | 0.065975 | 0.067738 | -0.0049688 | 0.0054708 | 0.0013521 | -0.27466 | 63.2309 | -60.0952 | 63.0478 | -59.8022 | -60.1547 | -0.041199 | -0.48523 | 63.1805 | -59.9487 | 63.1897 | -59.8801 | -60.022 | -59.7519 | -0.21973 | 0.027466 | -0.15564 | 0.073242 | 59.8343 | -0.27924 | 60.054 | -0.059509 | -0.073242 | -0.022888 | -0.013733 | -0.004578 | 0.1236 | -0.14649 | 0.19684 | -0.073243 | 0.29297 | 123.143 | 0.068664 | 123.1384 | 123.3261 | 123.1293 | 123.1064 | 123.056 | -123.2986 | -123.1522 | 122.9233 | 123.0652 | 59.6008 | 59.3903
409.8594 | 123.2437 | -59.8892 | 63.2034 | -0.041199 | 0.00022006 | 0.062222 | 0.065441 | 0.00093573 | -0.0033753 | 0.00022003 | -0.026764 | 0.0020572 | 0.067898 | 0.061329 | -0.006037 | 0.0050436 | 0.00028414 | -0.28381 | 63.2126 | -60.0815 | 63.0661 | -59.7839 | -60.1273 | -0.022888 | -0.46234 | 63.176 | -59.9625 | 63.2034 | -59.8846 | -59.9991 | -59.7519 | -0.19226 | 0.009155 | -0.13733 | 0.10529 | 59.8663 | -0.23804 | 60.0586 | -0.045776 | -0.073242 | -0.027466 | 0 | 0.004577 | 0.13733 | -0.10986 | 0.21057 | -0.036621 | 0.29755 | 123.1476 | 0.077819 | 123.1659 | 123.2941 | 123.1384 | 123.1018 | 123.0652 | -123.2849 | -123.1659 | 122.9553 | 123.0927 | 59.6054 | 59.4269
410.8906 | 123.2254 | -59.8755 | 63.1439 | -0.11749 | 0.0025699 | 0.062008 | 0.065014 | 0.0022173 | -0.00081187 | -0.0019162 | -0.063385 | 0.0018436 | 0.069607 | 0.063679 | -0.0028326 | 0.0050436 | 0.0034885 | -0.28839 | 63.1805 | -60.0952 | 63.1027 | -59.7473 | -60.141 | -0.054932 | -0.46692 | 63.1485 | -59.9533 | 63.1851 | -59.9121 | -60.0403 | -59.7565 | -0.21973 | 0.036621 | -0.041199 | 0.12817 | 59.8206 | -0.2655 | 60.0403 | -0.045776 | -0.07782 | 0.004578 | 0.041199 | -0.036621 | 0.11902 | -0.1648 | 0.19684 | -0.086975 | 0.3479 | 123.1979 | 0.041199 | 123.1384 | 123.2758 | 123.1018 | 123.056 | 123.024 | -123.2391 | -123.0972 | 122.9782 | 123.0606 | 59.5871 | 59.4086
411.8594 | 123.1979 | -59.8892 | 63.1851 | -0.079346 | -0.0014889 | 0.063076 | 0.06715 | -0.00077327 | -0.00038447 | 0.001929 | -0.060333 | 0.0035526 | 0.06918 | 0.060475 | -0.0036872 | 0.0069662 | 0.0015659 | -0.27924 | 63.208 | -60.1044 | 63.0798 | -59.761 | -60.1547 | -0.09613 | -0.5127 | 63.1531 | -59.9579 | 63.1714 | -59.9442 | -60.054 | -59.7748 | -0.21515 | 0.022888 | -0.10529 | 0.12817 | 59.7931 | -0.2655 | 60.0082 | -0.050354 | -0.068665 | -0.032044 | -0.013733 | -0.054932 | 0.11444 | -0.16479 | 0.18311 | -0.09613 | 0.34332 | 123.1842 | 0.013733 | 123.1293 | 123.3124 | 123.111 | 123.0972 | 123.0423 | -123.2895 | -123.143 | 122.9691 | 123.0606 | 59.61 | 59.3765
412.8906 | 123.1979 | -59.8938 | 63.1393 | -0.079346 | 0.0017155 | 0.063504 | 0.068859 | 0.00093573 | 4.273e-05 | 0.00043363 | -0.07254 | 0.0024844 | 0.070461 | 0.068379 | -0.0051824 | 0.0067526 | -0.0020657 | -0.33417 | 63.1897 | -60.1044 | 63.0341 | -59.8068 | -60.1822 | -0.1236 | -0.58136 | 63.1668 | -59.9487 | 63.1393 | -59.9716 | -60.0861 | -59.7931 | -0.21057 | 0.050354 | -0.10528 | 0.086975 | 59.7702 | -0.28839 | 59.9808 | -0.07782 | -0.054931 | 0.027466 | 0 | -0.07782 | 0.10071 | -0.19226 | 0.15564 | -0.13733 | 0.29755 | 123.1384 | -0.022889 | 123.0881 | 123.2941 | 123.1155 | 123.0835 | 123.0606 | -123.2437 | -123.0881 | 122.9279 | 123.0331 | 59.5596 | 59.3124
413.8594 | 123.1979 | -59.8846 | 63.1989 | -0.01831 | 0.0032107 | 0.063717 | 0.066937 | -0.00077327 | 0.00089713 | -0.0023434 | -0.023712 | 0.0039798 | 0.068539 | 0.061329 | -0.0041144 | 0.0050436 | 0.0019931 | -0.30212 | 63.2355 | -60.0952 | 63.0432 | -59.8022 | -60.1639 | -0.045776 | -0.50354 | 63.1668 | -59.935 | 63.1668 | -59.9121 | -60.0357 | -59.7656 | -0.21057 | 0.036621 | -0.15564 | 0.082398 | 59.8389 | -0.27923 | 60.0494 | -0.068664 | -0.050354 | -0.032044 | -0.032044 | -0.027465 | 0.11902 | -0.15106 | 0.16937 | -0.10071 | 0.29297 | 123.1384 | 0.022889 | 123.1018 | 123.3307 | 123.1018 | 123.1201 | 123.0515 | -123.2941 | -123.1339 | 122.9279 | 123.0515 | 59.5825 | 59.3811
414.9062 | 123.2529 | -59.935 | 63.1119 | -0.079346 | 0.0025699 | 0.063717 | 0.066723 | -0.00077327 | -0.0023071 | -0.0038388 | -0.0023498 | 0.0031254 | 0.069607 | 0.061543 | -0.0053962 | 0.0041892 | -0.00014306 | -0.36163 | 63.1805 | -60.1089 | 63.0661 | -59.7885 | -60.1776 | -0.13733 | -0.57678 | 63.1302 | -59.9487 | 63.2309 | -59.8984 | -60.0082 | -59.9304 | -0.17395 | 0.068665 | -0.045776 | 0.14648 | 59.7977 | -0.24261 | 59.9716 | -0.068664 | -0.013732 | 0.018311 | 0.11902 | 0.036622 | 0.004578 | -0.073242 | 0.01831 | -0.05951 | 0.32043 | 123.175 | 0.050354 | 123.1796 | 123.2895 | 123.0789 | 123.1155 | 123.0652 | -123.2208 | -123.0606 | 123.0011 | 123.1659 | 59.5734 | 59.3582
415.8594 | 123.2437 | -59.848 | 63.176 | -0.02594 | 0.0027835 | 0.063931 | 0.066082 | 0.0030719 | 0.00068353 | 0.0010746 | -0.042023 | 0.0020572 | 0.070675 | 0.069874 | -0.0075324 | 0.0069662 | -0.0020657 | -0.28839 | 63.208 | -60.0906 | 63.089 | -59.7473 | -60.1364 | -0.036621 | -0.46692 | 63.1393 | -59.9487 | 63.2172 | -59.8938 | -59.9991 | -59.7382 | -0.24262 | 0.032044 | -0.086975 | 0.10071 | 59.8114 | -0.28839 | 60.054 | -0.045777 | -0.10071 | -0.036621 | 0.041199 | -0.045777 | 0.10986 | -0.15106 | 0.21057 | -0.050354 | 0.34332 | 123.1796 | 0.054931 | 123.1659 | 123.2986 | 123.0881 | 123.056 | 122.9874 | -123.2666 | -123.1247 | 122.937 | 123.0652 | 59.5596 | 59.3811
416.8594 | 123.2391 | -59.9304 | 63.1256 | -0.086975 | 0.0032107 | 0.064572 | 0.065655 | 0.0032855 | 0.0021789 | -0.003198 | -0.038971 | 0.003339 | 0.07153 | 0.069233 | -0.004328 | 0.0076072 | 0.0019931 | -0.37079 | 63.208 | -60.1364 | 63.0157 | -59.8251 | -60.2234 | -0.17395 | -0.64545 | 63.121 | -59.9716 | 63.1714 | -59.9487 | -60.0494 | -59.7656 | -0.20599 | 0.082398 | -0.10986 | 0.10529 | 59.7565 | -0.29297 | 59.9625 | -0.086975 | -0.041199 | -0.004577 | 0.045777 | -0.01831 | 0.16479 | -0.11902 | 0.20599 | -0.077819 | 0.31128 | 123.1522 | 0.022889 | 123.143 | 123.3444 | 123.0927 | 123.1384 | 123.0515 | -123.262 | -123.0972 | 122.9462 | 123.1018 | 59.5596 | 59.285
417.8906 | 123.2254 | -59.8572 | 63.1805 | -0.079346 | 0.0017155 | 0.063504 | 0.066296 | 0.0028583 | -0.0027345 | -0.00042077 | -0.0084534 | 0.0020572 | 0.070889 | 0.061756 | -0.0079596 | 0.0056846 | 0.00071134 | -0.25635 | 63.208 | -60.0769 | 63.1073 | -59.7336 | -60.0952 | -0.20599 | -0.4715 | 63.1851 | -59.9487 | 63.2309 | -59.8755 | -60.0082 | -59.7198 | -0.21973 | 0.027466 | -0.073242 | 0.1236 | 59.6512 | -0.23804 | 59.8709 | -0.018311 | -0.091552 | 0.004578 | 0.050354 | -0.01831 | 0.13733 | -0.15106 | 0.22888 | -0.05951 | 0.34332 | 123.1842 | 0.073242 | 123.1796 | 123.2849 | 123.1338 | 123.0652 | 123.0423 | -123.2574 | -123.1293 | 122.9645 | 123.0881 | 59.6008 | 59.3857
418.8594 | 123.1705 | -59.903 | 63.1897 | -0.094604 | 0.0025699 | 0.063717 | 0.068005 | 0.0026447 | -0.0020935 | -0.00084817 | -0.05423 | 0.0029116 | 0.070889 | 0.063679 | -0.0062506 | 0.0052572 | 0.00028414 | -0.32959 | 63.2126 | -60.1089 | 63.0524 | -59.8114 | -60.173 | -0.13275 | -0.58594 | 63.1439 | -59.9487 | 63.1622 | -59.9625 | -60.0906 | -59.7931 | -0.20599 | 0.022888 | -0.13733 | 0.091553 | 59.7702 | -0.27008 | 59.9762 | -0.064087 | -0.045776 | -0.045776 | -0.027466 | -0.059509 | 0.10986 | -0.18768 | 0.15564 | -0.14191 | 0.29755 | 123.1613 | -0.013733 | 123.111 | 123.3215 | 123.0927 | 123.1155 | 123.0469 | -123.2986 | -123.1384 | 122.9553 | 123.0652 | 59.5734 | 59.317
419.8906 | 123.2254 | -59.8755 | 63.2126 | -0.071716 | 6.46e-06 | 0.062649 | 0.066723 | 0.00029473 | -0.00081187 | -0.0036252 | -0.023712 | 0.004407 | 0.069821 | 0.063679 | -0.007746 | 0.0067526 | -0.0027067 | -0.2655 | 63.2401 | -60.0723 | 63.1119 | -59.7519 | -60.1089 | -0.032043 | -0.48065 | 63.1805 | -59.9533 | 63.1622 | -59.8022 | -59.9487 | -59.729 | -0.19684 | 0.027466 | -0.10071 | 0.1236 | 59.8434 | -0.23346 | 60.0403 | -0.036621 | -0.07782 | -0.032043 | -0.050354 | 0.073242 | 0.14648 | -0.073242 | 0.2243 | 0.004578 | 0.32044 | 123.1842 | 0.15106 | 123.1155 | 123.3124 | 123.1338 | 123.1155 | 123.056 | -123.2849 | -123.1659 | 122.9874 | 123.0377 | 59.61 | 59.3948
420.8594 | 123.2391 | -59.903 | 63.1622 | -0.064087 | 0.0029971 | 0.062222 | 0.066509 | 0.0017901 | -0.0016663 | -0.004907 | -0.042023 | 0.0039798 | 0.072384 | 0.067311 | -0.0056098 | 0.0067526 | -0.0035611 | -0.2655 | 63.2309 | -60.0861 | 63.1073 | -59.729 | -60.1181 | -0.064087 | -0.49439 | 63.176 | -59.9167 | 63.2217 | -59.903 | -60.0174 | -59.7382 | -0.18311 | 0.068665 | -0.054931 | 0.17395 | 59.8389 | -0.21515 | 60.022 | -0.032043 | -0.013733 | 0.013733 | 0.05951 | 0 | 0.16479 | -0.11444 | 0.17853 | -0.10071 | 0.35706 | 123.1934 | 0.013733 | 123.1384 | 123.317 | 123.0927 | 123.1338 | 123.0789 | -123.2483 | -123.0789 | 123.0103 | 123.1247 | 59.6375 | 59.4086
421.8594 | 123.2254 | -59.8755 | 63.2217 | -0.071716 | 0.0017155 | 0.062008 | 0.068218 | 0.0028583 | -0.0025207 | -0.0010618 | 0.00070198 | 0.0018436 | 0.070248 | 0.066883 | -0.0034736 | 0.0056846 | -0.0022793 | -0.29297 | 63.2355 | -60.0632 | 63.0661 | -59.7839 | -60.1273 | -0.054932 | -0.53558 | 63.1989 | -59.935 | 63.1989 | -59.9075 | -59.9945 | -59.7336 | -0.18768 | 0.013733 | -0.15564 | 0.091552 | 59.8206 | -0.25177 | 60.0082 | -0.064087 | -0.05951 | -0.022888 | -0.022888 | -0.032044 | 0.14191 | -0.11902 | 0.20142 | -0.059509 | 0.27923 | 123.1293 | 0.027466 | 123.1339 | 123.2986 | 123.1339 | 123.111 | 123.0743 | -123.2849 | -123.1567 | 122.9416 | 123.0743 | 59.5825 | 59.3399
422.8906 | 123.2391 | -59.8526 | 63.2172 | 0.0045776 | 0.0017155 | 0.062863 | 0.067577 | 0.0034991 | -0.0012391 | -0.0010618 | -0.029816 | 0.0024844 | 0.068966 | 0.068806 | -0.0047552 | 0.0067526 | -0.0027067 | -0.25635 | 63.2217 | -60.0906 | 63.0981 | -59.7198 | -60.0998 | -0.045776 | -0.47607 | 63.1668 | -59.9258 | 63.2355 | -59.8846 | -59.9945 | -59.7336 | -0.23804 | 0.004578 | -0.11902 | 0.13275 | 59.8068 | -0.24719 | 60.0449 | -0.009155 | -0.073242 | -0.050354 | 0.018311 | -0.032044 | 0.11902 | -0.14191 | 0.19226 | -0.068665 | 0.37079 | 123.1888 | 0.041198 | 123.1613 | 123.3124 | 123.0927 | 123.0743 | 123.0194 | -123.3078 | -123.143 | 122.9507 | 123.0881 | 59.5963 | 59.3765
423.8594 | 123.2162 | -59.8343 | 63.1989 | -0.064087 | 0.0040653 | 0.06329 | 0.068432 | -0.0016279 | -0.0035889 | -0.0029844 | -0.042023 | 0.002698 | 0.070034 | 0.06197 | -0.0058234 | 0.0056846 | 0.0032749 | -0.27008 | 63.2217 | -60.0632 | 63.1073 | -59.7244 | -60.0952 | -0.054932 | -0.49439 | 63.1851 | -59.9213 | 63.2217 | -59.8709 | -59.9808 | -59.7244 | -0.22888 | 0.022888 | -0.091553 | 0.10986 | 59.7794 | -0.26093 | 60.0082 | -0.032044 | -0.086975 | -0.013733 | 0.022888 | -0.036621 | 0.10986 | -0.14648 | 0.19684 | -0.059509 | 0.33874 | 123.1705 | 0.050354 | 123.143 | 123.2849 | 123.1064 | 123.056 | 123.0194 | -123.262 | -123.1201 | 122.9416 | 123.056 | 59.5642 | 59.3399
424.8906 | 123.1796 | -59.9075 | 63.1577 | 0.035095 | 0.0015019 | 0.063717 | 0.065228 | 0.00072213 | 0.0013245 | -0.0023434 | -0.057281 | 0.004407 | 0.069393 | 0.064106 | -0.0073188 | 0.0039756 | -0.0012113 | -0.39368 | 63.2263 | -60.0815 | 62.9929 | -59.8663 | -60.2005 | -0.16937 | -0.66834 | 63.1668 | -59.9258 | 63.1439 | -59.9533 | -60.0861 | -59.7794 | -0.17395 | 0.068664 | -0.16479 | 0.041199 | 59.7382 | -0.29297 | 59.9121 | -0.11902 | -0.01831 | 0.009155 | -0.013733 | -0.045776 | 0.12817 | -0.17853 | 0.14648 | -0.16022 | 0.21515 | 123.0743 | -0.027466 | 123.0698 | 123.3078 | 123.0927 | 123.1338 | 123.0743 | -123.2391 | -123.0835 | 122.9004 | 123.0515 | 59.5139 | 59.2392
425.8594 | 123.2437 | -59.8755 | 63.1989 | -0.064087 | 0.0021427 | 0.062863 | 0.067577 | 0.00072213 | -0.0016663 | -0.00084817 | -0.026764 | 0.0029116 | 0.069821 | 0.062824 | -0.007105 | 0.0052572 | 0.00071134 | -0.25177 | 63.2584 | -60.0677 | 63.1165 | -59.7153 | -60.0952 | -0.059509 | -0.48065 | 63.1851 | -59.9258 | 63.2263 | -59.8663 | -59.9762 | -59.7153 | -0.19226 | 0.059509 | -0.082398 | 0.16022 | 59.816 | -0.21973 | 60.0082 | -0.027466 | -0.050354 | -0.013733 | 0.027465 | 0.009155 | 0.16022 | -0.10071 | 0.21057 | -0.050354 | 0.35248 | 123.1842 | 0.059509 | 123.1522 | 123.3261 | 123.111 | 123.1338 | 123.0606 | -123.2666 | -123.1247 | 122.9919 | 123.1018 | 59.6237 | 59.3948
426.9062 | 123.3307 | -59.8389 | 63.121 | -0.041199 | 0.0025699 | 0.065213 | 0.066937 | -0.00013247 | 0.0013245 | -0.0019162 | -0.0084534 | -0.00050621 | 0.069393 | 0.061543 | -0.0053962 | 0.0050436 | -0.00057046 | -0.32501 | 63.1851 | -60.0494 | 63.121 | -59.697 | -60.0723 | -0.09613 | -0.54474 | 63.1348 | -59.9213 | 63.2721 | -59.816 | -59.9442 | -59.6512 | -0.21057 | 0.064087 | 0 | 0.14191 | 59.7427 | -0.23346 | 59.9533 | -0.022889 | -0.082398 | 0.013733 | 0.15106 | 0.022888 | 0.18768 | -0.10529 | 0.27008 | -0.022888 | 0.35248 | 123.1705 | 0.10529 | 123.1934 | 123.2346 | 123.056 | 123.024 | 122.9736 | -123.1705 | -123.0423 | 122.9599 | 123.111 | 59.5139 | 59.2941
427.8594 | 123.2117 | -59.8618 | 63.2263 | -0.12512 | -0.00042094 | 0.064145 | 0.06715 | 0.0015765 | -0.0016663 | -0.0034116 | -0.011505 | 0.0035526 | 0.068966 | 0.066456 | -0.0062506 | 0.0091024 | -0.00078406 | -0.30212 | 63.2584 | -60.0494 | 63.0936 | -59.761 | -60.1089 | -0.050354 | -0.52643 | 63.2126 | -59.9121 | 63.2126 | -59.8663 | -59.9854 | -59.7107 | -0.18768 | 0.032044 | -0.13275 | 0.10071 | 59.8114 | -0.24719 | 59.9991 | -0.05951 | -0.050354 | -0.013733 | -0.013733 | -0.004578 | 0.15106 | -0.1236 | 0.20142 | -0.073243 | 0.28839 | 123.143 | 0.045776 | 123.1247 | 123.3078 | 123.1247 | 123.1201 | 123.0743 | -123.2758 | -123.1384 | 122.9553 | 123.0743 | 59.5596 | 59.3353
428.8906 | 123.2254 | -59.8526 | 63.2034 | -0.086975 | 0.0036381 | 0.065213 | 0.066723 | 8.1126e-05 | -0.0012391 | 0.00022003 | -0.048126 | 0.0031254 | 0.069821 | 0.065174 | -0.0062506 | 0.0076072 | 0.00028414 | -0.27924 | 63.2538 | -60.054 | 63.1119 | -59.7061 | -60.1089 | -0.054932 | -0.47607 | 63.1989 | -59.935 | 63.2309 | -59.8618 | -59.9762 | -59.7153 | -0.20142 | 0.050354 | -0.091553 | 0.14648 | 59.7977 | -0.25635 | 59.9991 | -0.054932 | -0.082398 | -0.004577 | 0.027466 | -0.009155 | 0.13733 | -0.1236 | 0.21973 | -0.041198 | 0.3479 | 123.1659 | 0.073243 | 123.1659 | 123.3078 | 123.1339 | 123.1064 | 123.0515 | -123.2574 | -123.1384 | 122.9645 | 123.0835 | 59.5734 | 59.3765
429.8594 | 123.2391 | -59.8663 | 63.1989 | -0.086975 | 0.0012881 | 0.063931 | 0.066082 | -0.00055967 | -0.0014527 | -0.00084817 | -0.042023 | 0.0020572 | 0.070461 | 0.067311 | -0.0066778 | 0.0044028 | 0.00028414 | -0.28839 | 63.2172 | -60.0494 | 63.1302 | -59.7015 | -60.0815 | -0.050354 | -0.49439 | 63.208 | -59.935 | 63.2446 | -59.8618 | -59.9808 | -59.7061 | -0.18311 | 0.01831 | -0.068665 | 0.16479 | 59.816 | -0.21515 | 59.9991 | -0.032044 | -0.068665 | 0.009155 | 0.045776 | 0.004578 | 0.16022 | -0.11444 | 0.22888 | -0.045776 | 0.3479 | 123.1796 | 0.073243 | 123.1796 | 123.2666 | 123.143 | 123.0835 | 123.0743 | -123.2483 | -123.1339 | 122.9965 | 123.111 | 59.5779 | 59.3719
430.8906 | 123.2025 | -59.8618 | 63.1943 | -0.10223 | 0.0029971 | 0.06329 | 0.067364 | 0.0037127 | -0.00081187 | -0.0017026 | -0.045074 | 0.0029116 | 0.068325 | 0.062397 | -0.0049688 | 0.006539 | -0.0029203 | -0.28381 | 63.2309 | -60.0723 | 63.121 | -59.729 | -60.1044 | -0.073242 | -0.52643 | 63.1668 | -59.9121 | 63.2309 | -59.8755 | -59.9991 | -59.7198 | -0.21057 | 0.036621 | -0.073242 | 0.13275 | 59.7885 | -0.24262 | 59.9991 | -0.032043 | -0.050354 | -0.027466 | 0.036621 | -0.013733 | 0.14191 | -0.13733 | 0.19226 | -0.086975 | 0.34332 | 123.1934 | 0.036621 | 123.143 | 123.3032 | 123.0789 | 123.0927 | 123.0286 | -123.2666 | -123.1064 | 122.9828 | 123.0927 | 59.5779 | 59.3353
431.8594 | 123.2254 | -59.8389 | 63.208 | -0.048828 | 0.0015019 | 0.064999 | 0.064587 | 0.00029473 | -0.0018799 | -0.00020717 | -0.069489 | 0.002698 | 0.070461 | 0.069233 | -0.006037 | 0.0073936 | 0.0022067 | -0.41657 | 63.2217 | -60.0769 | 63.1119 | -59.7015 | -60.0723 | -0.064087 | -0.48981 | 63.1805 | -59.9167 | 63.2584 | -59.8343 | -59.967 | -59.7015 | -0.23804 | 0.013733 | -0.096131 | 0.13733 | 59.7748 | -0.23346 | 60.0128 | 0.004577 | -0.07782 | -0.027466 | 0.050354 | 0.004577 | 0.13733 | -0.12817 | 0.21515 | -0.050354 | 0.37537 | 123.1888 | 0.082397 | 123.175 | 123.2986 | 123.0972 | 123.0606 | 123.0194 | -123.2849 | -123.1247 | 122.9507 | 123.0972 | 59.4223 | 59.3491
432.9062 | 123.2712 | -59.8709 | 63.1714 | -0.064087 | 0.0010745 | 0.06329 | 0.066296 | 0.0015765 | -0.0012391 | -0.0010618 | -0.035919 | 0.0029116 | 0.068325 | 0.067951 | -0.0062506 | 0.0073936 | 0.0034885 | -0.3891 | 63.208 | -60.0769 | 63.0707 | -59.7794 | -60.173 | -0.1831 | -0.64545 | 63.1577 | -59.9304 | 63.2172 | -59.8938 | -59.9945 | -59.7244 | -0.20599 | 0.036621 | -0.10071 | 0.091553 | 59.6878 | -0.30212 | 59.8938 | -0.096131 | -0.059509 | -0.013733 | 0.045776 | -0.022888 | 0.14648 | -0.1236 | 0.20599 | -0.064087 | 0.29755 | 123.1476 | 0.036621 | 123.1476 | 123.2849 | 123.0881 | 123.0789 | 123.0286 | -123.2483 | -123.1018 | 122.9416 | 123.0881 | 59.4818 | 59.2255
433.8594 | 123.2391 | -59.8434 | 63.2172 | -0.041199 | 0.0023563 | 0.063504 | 0.067791 | 0.0028583 | -0.0018799 | -0.00084817 | -0.026764 | 0.002698 | 0.068325 | 0.068165 | -0.0066778 | 0.0069662 | 0.0028475 | -0.29297 | 63.2767 | -60.0266 | 63.1256 | -59.7107 | -60.0769 | -0.068665 | -0.48981 | 63.2355 | -59.8892 | 63.2034 | -59.7427 | -59.9213 | -59.697 | -0.1831 | 0.059509 | -0.091553 | 0.13275 | 59.7748 | -0.23346 | 59.9579 | -0.050354 | -0.045776 | 0.018311 | -0.013733 | 0.10071 | 0.14649 | -0.07782 | 0.19226 | -0.032044 | 0.31586 | 123.1522 | 0.14648 | 123.0927 | 123.3032 | 123.1247 | 123.1201 | 123.0789 | -123.2437 | -123.1064 | 122.9691 | 123.0469 | 59.5505 | 59.3536
434.8906 | 123.1934 | -59.8343 | 63.2172 | -0.071716 | 0.0015019 | 0.062436 | 0.066082 | 0.0015765 | 4.273e-05 | 0.0015018 | -0.051178 | 0.004407 | 0.070248 | 0.07201 | -0.004328 | 0.0054708 | -0.0022793 | -0.34332 | 63.2446 | -60.0449 | 63.089 | -59.7702 | -60.141 | -0.15106 | -0.60425 | 63.2309 | -59.9121 | 63.176 | -59.9121 | -60.022 | -59.7244 | -0.21057 | 0.027466 | -0.12817 | 0.064087 | 59.6832 | -0.3067 | 59.8938 | -0.09613 | -0.077819 | 0.013733 | -0.041199 | -0.077819 | 0.10986 | -0.18768 | 0.18768 | -0.10986 | 0.27466 | 123.1338 | 0 | 123.0881 | 123.2895 | 123.143 | 123.0789 | 123.0652 | -123.262 | -123.1293 | 122.9233 | 123.0103 | 59.491 | 59.23
435.8594 | 123.2162 | -59.8343 | 63.2401 | -0.094604 | -0.0010617 | 0.063076 | 0.066937 | -0.0022687 | -0.0027345 | -0.0012754 | 0.028168 | 0.0029116 | 0.069607 | 0.060688 | -0.0056098 | 0.0041892 | 0.0019931 | -0.3067 | 63.295 | -60.0403 | 63.0844 | -59.7473 | -60.0998 | -0.064087 | -0.54932 | 63.2263 | -59.8984 | 63.2034 | -59.8709 | -59.9762 | -59.7427 | -0.20599 | 0.054932 | -0.15564 | 0.086976 | 59.7702 | -0.2655 | 59.9762 | -0.059509 | -0.064086 | -0.013733 | -0.036621 | -0.036621 | 0.091553 | -0.14191 | 0.15564 | -0.07782 | 0.29297 | 123.1247 | 0.027465 | 123.1018 | 123.3353 | 123.1247 | 123.1293 | 123.0606 | -123.2803 | -123.1384 | 122.9187 | 123.0377 | 59.5276 | 59.285
436.8906 | 123.2025 | -59.848 | 63.2172 | -0.10223 | 0.0010745 | 0.06329 | 0.066723 | 0.00093573 | -0.0012391 | 0.00022003 | -0.042023 | 0.0020572 | 0.067044 | 0.063038 | -0.0051824 | 0.0056846 | 0.0011385 | -0.31128 | 63.2263 | -60.0449 | 63.1027 | -59.7427 | -60.1181 | -0.091553 | -0.56305 | 63.2126 | -59.9213 | 63.2126 | -59.8938 | -60.022 | -59.7198 | -0.19684 | 0.009155 | -0.11444 | 0.10529 | 59.7565 | -0.27008 | 59.9533 | -0.073242 | -0.073243 | -0.004578 | -0.004578 | -0.045777 | 0.12817 | -0.17395 | 0.20142 | -0.10071 | 0.30212 | 123.1476 | 0.027466 | 123.1338 | 123.2712 | 123.1338 | 123.0743 | 123.0606 | -123.262 | -123.1384 | 122.9507 | 123.0606 | 59.5367 | 59.285
437.8594 | 123.2208 | -59.8389 | 63.2309 | -0.033569 | 0.0015019 | 0.062222 | 0.06715 | 0.0022173 | 4.273e-05 | -0.0019162 | -0.017609 | 0.002698 | 0.067257 | 0.064533 | -0.0047552 | 0.003762 | -0.00014306 | -0.28381 | 63.2629 | -60.0494 | 63.1348 | -59.729 | -60.0677 | -0.045776 | -0.50354 | 63.2446 | -59.8892 | 63.3179 | -59.9625 | -59.8892 | -59.5963 | -0.21057 | 0.032043 | -0.09613 | 0.10986 | 59.7931 | -0.22888 | 60.0037 | -0.018311 | -0.050354 | 0.013733 | 0.086975 | -0.1236 | 0.24262 | -0.050354 | 0.29297 | 0 | 0.32043 | 123.1842 | -0.073242 | 123.2071 | 123.3124 | 123.1338 | 123.1018 | 123.0835 | -123.2803 | -123.1201 | 122.9736 | 123.1567 | 59.5551 | 59.3353
438.8906 | 123.1842 | -59.8663 | 63.2446 | -0.086975 | 0.0019291 | 0.063504 | 0.067791 | 0.00050853 | 0.00046993 | 0.001929 | -0.029816 | 0.00163 | 0.06918 | 0.066883 | -0.0068914 | 0.0067526 | 0.0030611 | -0.33875 | 63.2446 | -60.054 | 63.1073 | -59.7565 | -60.1456 | -0.14191 | -0.59509 | 63.2126 | -59.9213 | 63.2217 | -59.8892 | -60.022 | -59.7336 | -0.18768 | 0 | -0.13733 | 0.10986 | 59.7244 | -0.27924 | 59.9121 | -0.091553 | -0.054932 | -0.032044 | -0.022888 | -0.022888 | 0.13275 | -0.15564 | 0.18768 | -0.10071 | 0.29755 | 123.1613 | 0.032044 | 123.143 | 123.2986 | 123.1338 | 123.111 | 123.0789 | -123.2986 | -123.1659 | 122.9736 | 123.0881 | 59.5276 | 59.2712
439.8594 | 123.2437 | -59.8251 | 63.2538 | -0.01831 | 0.0027835 | 0.06329 | 0.067577 | 0.0022173 | 0.00025633 | -0.00063437 | 0.0068054 | 0.00163 | 0.068753 | 0.064106 | -0.0051824 | 0.0063254 | -0.0012113 | -0.29297 | 63.2812 | -60.0357 | 63.1027 | -59.7473 | -60.0906 | -0.064087 | -0.54932 | 63.2584 | -59.8846 | 63.2401 | -59.8297 | -59.9625 | -59.6924 | -0.21057 | 0.027466 | -0.15106 | 0.07782 | 59.761 | -0.2655 | 59.9716 | -0.054931 | -0.05951 | 0.004578 | -0.013733 | -0.004578 | 0.13275 | -0.13733 | 0.19226 | -0.077819 | 0.28839 | 123.1384 | 0.054932 | 123.1247 | 123.317 | 123.143 | 123.1064 | 123.0835 | -123.2895 | -123.1384 | 122.9279 | 123.0652 | 59.5322 | 59.2758
440.8906 | 123.23 | -59.7977 | 63.2263 | 0.0045776 | 0.0019291 | 0.066067 | 0.068218 | 0.0013629 | -0.0012391 | -0.001489 | -0.017609 | 0.0020572 | 0.070248 | 0.063465 | -0.0058234 | 0.0041892 | -0.00078406 | -0.26093 | 63.2675 | -60.0082 | 63.1439 | -59.6924 | -60.0586 | -0.068665 | -0.50354 | 63.2355 | -59.8892 | 63.2538 | -59.8251 | -59.9442 | -59.6878 | -0.21057 | 0.041199 | -0.082397 | 0.10529 | 59.729 | -0.26093 | 59.9396 | -0.050354 | -0.091553 | 0.009156 | 0.027466 | -0.027466 | 0.10986 | -0.14648 | 0.20142 | -0.054932 | 0.31586 | 123.1522 | 0.064087 | 123.143 | 123.2758 | 123.1247 | 123.0652 | 123.0331 | -123.2346 | -123.1155 | 122.9416 | 123.0515 | 59.5367 | 59.2941
441.8594 | 123.2712 | -59.8663 | 63.2446 | -0.02594 | 0.0012881 | 0.063717 | 0.068859 | -0.0016279 | -0.0014527 | -0.0019162 | -0.011505 | 0.0031254 | 0.071316 | 0.063038 | -0.0053962 | 0.0052572 | -0.0022793 | -0.29297 | 63.2629 | -60.0266 | 63.1256 | -59.7107 | -60.0494 | -0.041199 | -0.49439 | 63.2401 | -59.8892 | 63.2538 | -59.8343 | -60.1501 | -59.8618 | -0.16022 | 0.01831 | -0.11902 | 0.15564 | 59.8251 | -0.18311 | 59.9854 | -0.022888 | -0.022888 | -0.004578 | 0.009155 | 0.032043 | 0.004578 | -0.28381 | 0.027466 | -0.26093 | 0.31586 | 123.1522 | 0.054931 | 123.143 | 123.2895 | 123.1293 | 123.1293 | 123.1064 | -123.2712 | -123.1338 | 122.9919 | 123.1201 | 59.5734 | 59.3719
442.9062 | 123.2666 | -59.816 | 63.2034 | -0.10986 | 0.00043366 | 0.063931 | 0.066723 | -0.00034607 | -0.0012391 | -0.00084817 | -0.017609 | 0.0022708 | 0.068753 | 0.066242 | -0.0045416 | 0.0056846 | -0.00078406 | -0.3891 | 63.2217 | -60.0494 | 63.0707 | -59.761 | -60.1318 | -0.17853 | -0.65002 | 63.2034 | -59.9213 | 63.2629 | -59.8526 | -59.9579 | -59.6695 | -0.23346 | 0.018311 | -0.13275 | 0.054932 | 59.6375 | -0.31586 | 59.8709 | -0.082398 | -0.10529 | 0 | 0.059509 | -0.036621 | 0.14648 | -0.14191 | 0.25177 | -0.036621 | 0.28839 | 123.1201 | 0.068665 | 123.1842 | 123.2712 | 123.1247 | 123.0377 | 123.0194 | -123.2529 | -123.1247 | 122.8867 | 123.0789 | 59.4269 | 59.166
443.8594 | 123.2208 | -59.7977 | 63.2492 | -0.056457 | 0.0032107 | 0.062436 | 0.065655 | 0.0022173 | -0.0010255 | -0.0034116 | -0.017609 | 0.0022708 | 0.06918 | 0.06197 | -0.0053962 | 0.0058982 | 0.00049774 | -0.30212 | 63.2858 | -60.0266 | 63.1073 | -59.729 | -60.0861 | -0.07782 | -0.54932 | 63.2401 | -59.8801 | 63.2355 | -59.8251 | -59.9442 | -59.6741 | -0.22888 | 0.036621 | -0.14191 | 0.068664 | 59.7198 | -0.28839 | 59.9487 | -0.05951 | -0.082398 | -0.009156 | -0.013733 | -0.027466 | 0.1236 | -0.14648 | 0.20599 | -0.064087 | 0.29755 | 123.1338 | 0.054932 | 123.1155 | 123.3124 | 123.1201 | 123.0835 | 123.0377 | -123.2758 | -123.1293 | 122.905 | 123.0331 | 59.4955 | 59.2484
444.8594 | 123.2391 | -59.8297 | 63.2309 | -0.086975 | -0.00020714 | 0.062008 | 0.066509 | 0.0011493 | 0.0032471 | 6.432e-06 | -0.051178 | 0.004407 | 0.071102 | 0.070088 | -0.0049688 | 0.0046164 | 7.0538e-05 | -0.28381 | 63.2767 | -60.0266 | 63.1531 | -59.6786 | -60.0723 | -0.068665 | -0.49439 | 63.2309 | -59.8755 | 63.2675 | -59.8251 | -59.9304 | -59.6603 | -0.19684 | 0.045776 | -0.07782 | 0.15106 | 59.761 | -0.24262 | 59.9579 | -0.045777 | -0.045776 | 0 | 0.036621 | 0.004578 | 0.16937 | -0.10071 | 0.21515 | -0.054932 | 0.3479 | 123.1796 | 0.050354 | 123.143 | 123.3032 | 123.1064 | 123.1064 | 123.0606 | -123.2574 | -123.1064 | 122.9828 | 123.0972 | 59.5459 | 59.3353
445.8906 | 123.1934 | -59.8297 | 63.2629 | -0.056457 | 0.0023563 | 0.06329 | 0.066082 | 0.0015765 | -0.0010255 | -0.0023434 | 0.015961 | 0.002698 | 0.070889 | 0.059193 | -0.0053962 | 0.0050436 | 0.0037021 | -0.31128 | 63.3179 | -60.022 | 63.1027 | -59.7244 | -60.0861 | -0.064087 | -0.56305 | 63.2629 | -59.8618 | 63.2126 | -59.8572 | -59.9579 | -59.7061 | -0.19226 | 0.054932 | -0.16022 | 0.10529 | 59.7656 | -0.25635 | 59.9579 | -0.064087 | -0.032043 | 0 | -0.050354 | -0.027466 | 0.1236 | -0.12817 | 0.15564 | -0.096131 | 0.29755 | 123.1247 | 0.004577 | 123.0743 | 123.3398 | 123.1247 | 123.1476 | 123.0927 | -123.2849 | -123.1247 | 122.9324 | 123.0423 | 59.5184 | 59.2667
446.875 | 123.3124 | -59.7977 | 63.1989 | -0.079346 | 0.0027835 | 0.061154 | 0.066509 | 0.0034991 | 0.00025633 | -0.0038388 | 0.040375 | 0.00034819 | 0.070248 | 0.05727 | -0.0034736 | 0.0046164 | -0.00014306 | -0.33417 | 63.2492 | -60.0037 | 63.1668 | -59.6603 | -60.0311 | -0.064087 | -0.53101 | 63.1943 | -59.8618 | 63.2858 | -59.7702 | -59.8526 | -59.6008 | -0.20599 | 0.050354 | -0.032044 | 0.13733 | 59.7336 | -0.23346 | 59.9396 | -0.027466 | -0.064087 | -0.004578 | 0.086975 | 0.027465 | 0.19684 | -0.054932 | 0.26093 | 0.009155 | 0.34332 | 123.1705 | 0.091552 | 123.1476 | 123.2529 | 123.056 | 123.0469 | 122.9919 | -123.2025 | -123.0606 | 122.9645 | 123.0835 | 59.4635 | 59.2667
447.8906 | 123.2117 | -59.8114 | 63.3041 | -0.0030519 | 0.0036381 | 0.061795 | 0.069073 | 8.1126e-05 | -0.0012391 | -0.0044796 | -0.026764 | 0.0020572 | 0.071316 | 0.05962 | -0.0049688 | 0.003121 | 0.00049774 | -0.32959 | 63.3179 | -60.0082 | 63.1393 | -59.7198 | -60.0815 | -0.073242 | -0.56305 | 63.2584 | -59.8709 | 63.2263 | -59.8389 | -59.9579 | -59.697 | -0.19684 | 0.013733 | -0.1648 | 0.091552 | 59.7382 | -0.27008 | 59.935 | -0.073242 | -0.05951 | -0.045776 | -0.07782 | -0.027466 | 0.11444 | -0.14649 | 0.17395 | -0.086975 | 0.28839 | 123.1476 | 0.032044 | 123.0972 | 123.3261 | 123.1293 | 123.1293 | 123.0698 | -123.3124 | -123.175 | 122.9507 | 123.0377 | 59.4818 | 59.2484
448.8594 | 123.2208 | -59.8022 | 63.2812 | -0.02594 | -0.00020714 | 0.062863 | 0.068218 | 0.0020037 | 0.00025633 | -0.0029844 | -0.014557 | 0.0024844 | 0.069393 | 0.069233 | -0.0056098 | 0.0046164 | -0.00078406 | -0.33417 | 63.3133 | -60.0128 | 63.1165 | -59.7244 | -60.0815 | -0.054932 | -0.54474 | 63.2812 | -59.8755 | 63.2309 | -59.8389 | -59.9579 | -59.6832 | -0.21057 | 0.032043 | -0.16479 | 0.07782 | 59.7473 | -0.27924 | 59.9579 | -0.068665 | -0.073242 | 0 | -0.050354 | -0.036621 | 0.11902 | -0.15564 | 0.19226 | -0.082398 | 0.28839 | 123.1293 | 0.036621 | 123.1064 | 123.3261 | 123.1567 | 123.1155 | 123.0835 | -123.2941 | -123.1567 | 122.9187 | 123.0331 | 59.4681 | 59.2575
449.8906 | 123.317 | -59.7748 | 63.2584 | -0.056457 | 0.0025699 | 0.061581 | 0.066082 | -0.00055967 | -0.00017087 | -0.003198 | 0.019012 | 0.0029116 | 0.068539 | 0.060688 | -0.0056098 | 0.0035482 | -0.00035666 | -0.26093 | 63.2721 | -59.9808 | 63.2492 | -59.5688 | -59.9625 | 0.027466 | -0.41657 | 63.208 | -59.8434 | 63.3499 | -59.7107 | -59.8251 | -59.5871 | -0.20599 | 0.013733 | -0.009155 | 0.20599 | 59.8022 | -0.18768 | 60.0082 | 0.018311 | -0.068665 | -0.050354 | 0.091553 | 0.064087 | 0.18768 | -0.050354 | 0.25635 | 0.018311 | 0.41199 | 123.23 | 0.13275 | 123.1934 | 123.2529 | 123.0515 | 123.0469 | 122.9828 | -123.2391 | -123.1018 | 123.024 | 123.1247 | 59.5139 | 59.3582
450.8594 | 123.2391 | -59.8251 | 63.2675 | -0.033569 | 0.00064726 | 0.061581 | 0.068646 | 0.0013629 | -0.0020935 | 0.00064723 | -0.048126 | 0.002698 | 0.068753 | 0.053211 | -0.0051824 | 0.0063254 | -0.0029203 | -0.2655 | 63.295 | -60.022 | 63.1668 | -59.6878 | -60.0311 | -0.07782 | -0.48981 | 63.2584 | -59.848 | 63.295 | -59.8068 | -59.9396 | -59.6649 | -0.19684 | 0.027466 | -0.10071 | 0.13733 | 59.7473 | -0.20599 | 59.9442 | -0.009155 | -0.022888 | -0.009155 | 0.027466 | 0.01831 | 0.16022 | -0.11444 | 0.1831 | -0.091553 | 0.33417 | 123.1888 | 0.041198 | 123.143 | 123.317 | 123.1064 | 123.1201 | 123.0835 | -123.2895 | -123.1155 | 122.9919 | 123.1201 | 59.5596 | 59.3353
451.9062 | 123.1567 | -59.816 | 63.2584 | -0.071716 | 0.0010745 | 0.065426 | 0.067577 | 0.0045673 | -0.0020935 | -0.0012754 | 0.15634 | 0.0020572 | 0.070034 | 0.065388 | -0.0073188 | 0.0063254 | 7.0538e-05 | -0.35706 | 63.2767 | -60.0174 | 63.1027 | -59.7702 | -60.6537 | -0.49439 | -0.86517 | 63.2721 | -59.8892 | 63.2172 | -59.9304 | -60.022 | -59.7015 | -0.20142 | 0.01831 | -0.15564 | 0.045776 | 59.3216 | -0.83771 | 59.523 | -0.63629 | -0.073242 | 0.013733 | -0.041199 | -0.11444 | 0.11444 | -0.20599 | 0.18768 | -0.13275 | 0.24719 | 123.1201 | -0.041199 | 123.1064 | 123.2941 | 123.1613 | 123.0927 | 123.0881 | -123.2758 | -123.1476 | 122.9187 | 123.0331 | 59.4589 | 58.9508
452.8594 | 123.2071 | -59.8022 | 63.2675 | -0.056457 | 0.0027835 | 0.062436 | 0.067791 | 0.0013629 | -0.0010255 | -0.004266 | -0.026764 | 0.0024844 | 0.068325 | 0.06197 | -0.0039008 | 0.0044028 | -0.00078406 | -0.31128 | 63.3133 | -59.9899 | 63.1256 | -59.7198 | -60.0632 | -0.082397 | -0.56305 | 63.2675 | -59.8618 | 63.2538 | -59.8251 | -59.9396 | -59.6786 | -0.18768 | 0.045776 | -0.14191 | 0.082397 | 59.7198 | -0.26093 | 59.9075 | -0.073242 | -0.059509 | 0 | -0.013733 | -0.022888 | 0.1236 | -0.13733 | 0.18311 | -0.07782 | 0.27008 | 123.1155 | 0.036621 | 123.1155 | 123.3032 | 123.1293 | 123.1155 | 123.0698 | -123.2574 | -123.1293 | 122.9279 | 123.056 | 59.491 | 59.2392
453.8906 | 123.2025 | -59.8389 | 63.2858 | -0.02594 | 0.00064726 | 0.065426 | 0.066296 | 0.0017901 | -0.00081187 | -0.002557 | 0.028168 | 0.0035526 | 0.069393 | 0.065388 | -0.0039008 | 0.0018394 | 0.00049774 | -0.27466 | 63.295 | -59.9899 | 63.1714 | -59.6558 | -60.0311 | -0.064087 | -0.49439 | 63.2721 | -59.8114 | 63.2904 | -59.8663 | -59.8846 | -59.6237 | -0.15106 | 0.009155 | -0.11444 | 0.1831 | 59.7748 | -0.19226 | 59.9258 | -0.041199 | 0.027466 | -0.013733 | 0.004577 | -0.027466 | 0.21515 | -0.045777 | 0.18768 | -0.073243 | 0.33417 | 123.1613 | -0.054932 | 123.1018 | 123.2849 | 123.0835 | 123.1338 | 123.111 | -123.2758 | -123.0972 | 123.0103 | 123.1293 | 59.5642 | 59.3445
454.8594 | 123.1888 | -59.7977 | 63.295 | -0.048828 | 0.0015019 | 0.062436 | 0.067791 | -0.0059003 | -0.00081187 | -0.0034116 | -0.0084534 | 0.0035526 | 0.068753 | 0.066242 | -0.0049688 | 0.0044028 | 7.0538e-05 | -0.31586 | 63.327 | -59.9808 | 63.1439 | -59.6878 | -60.0677 | -0.07782 | -0.55847 | 63.2812 | -59.8572 | 63.2446 | -59.8297 | -59.9442 | -59.6924 | -0.18311 | 0.032043 | -0.15106 | 0.10986 | 59.7198 | -0.27008 | 59.903 | -0.086975 | -0.05951 | -0.013733 | -0.050354 | -0.032044 | 0.10529 | -0.14648 | 0.16479 | -0.086975 | 0.29297 | 123.1247 | 0.027466 | 123.1018 | 123.3078 | 123.1384 | 123.1247 | 123.0789 | -123.2758 | -123.1522 | 122.9416 | 123.0423 | 59.4818 | 59.2392
455.9062 | 123.317 | -59.8572 | 63.295 | -0.071716 | 0.0021427 | 0.061795 | 0.067577 | 0.0039263 | 0.00089713 | -0.0019162 | -0.081696 | 0.0029116 | 0.070034 | 0.064961 | -0.006037 | 0.0056846 | -0.0014249 | -0.34332 | 63.2812 | -60.022 | 63.1302 | -59.7244 | -60.1089 | -0.18768 | -0.66376 | 63.2721 | -59.8801 | 63.2126 | -59.8206 | -60.5759 | -60.0815 | -0.1648 | -0.013733 | -0.1648 | 0.13275 | 59.6695 | -0.25177 | 59.8343 | -0.086975 | -0.022888 | -0.022888 | -0.082398 | 0.036621 | -0.2243 | -0.71869 | -0.20142 | -0.6958 | 0.29755 | 123.1522 | 0.059509 | 123.0927 | 123.3032 | 123.1522 | 123.1384 | 123.1293 | -123.317 | -123.175 | 122.9874 | 123.0698 | 59.5139 | 59.1934
456.875 | 123.2162 | -59.8206 | 63.2538 | -0.12512 | 0.0034245 | 0.064785 | 0.066296 | -0.00077327 | -0.0012391 | -0.0010618 | -0.051178 | 0.0039798 | 0.069607 | 0.065388 | -0.0051824 | 0.0054708 | -0.0027067 | -0.39368 | 63.295 | -60.0357 | 63.1119 | -59.7427 | -60.1456 | -0.21973 | -0.68665 | 63.2446 | -59.8938 | 63.2584 | -59.8389 | -59.9762 | -59.6741 | -0.21515 | 0.041199 | -0.14191 | 0.07782 | 59.6008 | -0.32501 | 59.816 | -0.10986 | -0.073242 | -0.009155 | 0.004578 | -0.01831 | 0.14648 | -0.15564 | 0.21973 | -0.082397 | 0.29297 | 123.1476 | 0.054932 | 123.1522 | 123.3307 | 123.1384 | 123.1155 | 123.0652 | -123.2895 | -123.1476 | 122.9324 | 123.0789 | 59.4269 | 59.1339
457.8906 | 123.317 | -59.7519 | 63.2492 | 0.035095 | -0.00042094 | 0.064999 | 0.064587 | 0.0028583 | -0.0025207 | -0.0021298 | 0.058685 | 0.00163 | 0.068539 | 0.060688 | -0.006037 | 0.0056846 | -0.00014306 | -0.32044 | 63.2812 | -59.9258 | 63.295 | -59.5917 | -59.903 | 0.018311 | -0.4303 | 63.2401 | -59.8389 | 63.3636 | -59.6878 | -59.8114 | -59.5596 | -0.17395 | 0.032043 | 0.045776 | 0.16022 | 59.7702 | -0.15106 | 59.9442 | 0.022888 | -0.086975 | -0.009156 | 0.11444 | 0.064087 | 0.19226 | -0.059509 | 0.27924 | 0.027466 | 0.33417 | 123.2208 | 0.15106 | 123.2025 | 123.2071 | 123.0789 | 123.0331 | 122.9919 | -123.175 | -123.0881 | 123.0469 | 123.1155 | 59.4315 | 59.3216
458.8594 | 123.2346 | -59.7977 | 63.3041 | -0.02594 | -0.00042094 | 0.062436 | 0.067577 | 8.1126e-05 | -0.0033753 | -0.0036252 | -0.051178 | 0.002698 | 0.069607 | 0.066029 | -0.0064642 | 0.0061118 | 0.0032749 | -0.3067 | 63.3224 | -59.9716 | 63.1531 | -59.697 | -60.0494 | -0.091553 | -0.55389 | 63.2904 | -59.8389 | 63.2721 | -59.7977 | -59.9213 | -59.642 | -0.17395 | 0.018311 | -0.15106 | 0.10071 | 59.7061 | -0.25177 | 59.8801 | -0.077819 | -0.041199 | -0.013733 | -0.032043 | 0 | 0.15564 | -0.1236 | 0.19684 | -0.082398 | 0.27466 | 123.1247 | 0.041199 | 123.111 | 123.2941 | 123.1293 | 123.1201 | 123.0881 | -123.2758 | -123.143 | 122.9507 | 123.0698 | 59.491 | 59.2438
459.8906 | 123.1659 | -59.7931 | 63.2904 | -0.01831 | 0.0017155 | 0.062008 | 0.066296 | 8.1126e-05 | -0.0038025 | -0.0019162 | -0.060333 | 0.0037662 | 0.070248 | 0.064106 | -0.0056098 | 0.003762 | -0.0037747 | -0.27924 | 63.3224 | -59.9716 | 63.121 | -59.5322 | -59.697 | -0.16937 | -0.49896 | 63.2675 | -59.848 | 63.2675 | -59.8022 | -59.9487 | -59.6786 | -0.17853 | 0.032044 | -0.16937 | 0.26093 | 59.6237 | 0.096131 | 59.8022 | 0.27466 | -0.054931 | -0.022888 | -0.022888 | -0.009155 | 0.11444 | -0.15564 | 0.16937 | -0.10071 | 0.43945 | 123.0927 | 0.045776 | 123.1155 | 123.2941 | 123.1155 | 123.1155 | 123.0606 | -123.262 | -123.1384 | 122.9141 | 123.0606 | 59.5139 | 59.2941
460.8594 | 123.2117 | -59.7931 | 63.3133 | -0.071716 | 0.0029971 | 0.063076 | 0.066296 | -0.0018415 | -0.0014527 | -0.0055478 | -0.02066 | 0.0039798 | 0.070248 | 0.064533 | -0.0062506 | 0.0035482 | -0.0014249 | -0.3067 | 63.3179 | -59.9762 | 63.327 | -59.8618 | -60.2966 | -0.050354 | -0.53558 | 63.295 | -59.8572 | 63.2721 | -59.8206 | -59.8801 | -59.6466 | -0.18311 | 0.004578 | 0.013733 | -0.068664 | 59.7427 | -0.50354 | 59.9258 | -0.32043 | -0.064087 | -0.01831 | -0.041198 | -0.027466 | 0.14648 | -0.086975 | 0.21057 | -0.022888 | 0.11444 | 123.3032 | 0.036621 | 123.1293 | 123.2941 | 123.1522 | 123.111 | 123.0881 | -123.2895 | -123.1705 | 123.1201 | 123.0652 | 59.4864 | 59.2575
461.9062 | 123.3078 | -59.7473 | 63.2812 | -0.086975 | 0.0019291 | 0.063931 | 0.066509 | -0.00055967 | -0.0027345 | -0.0027708 | 0.022064 | 0.00077539 | 0.068966 | 0.061115 | -0.0075324 | 0.0054708 | -0.0024931 | -0.33875 | 63.295 | -59.9716 | 63.1897 | -59.6466 | -60.0128 | -0.10071 | -0.55389 | 63.2263 | -59.8206 | 63.3316 | -59.7382 | -59.8343 | -59.5963 | -0.2243 | 0.013733 | -0.091553 | 0.10071 | 59.6466 | -0.2655 | 59.8709 | -0.041198 | -0.073243 | -0.054932 | 0.050354 | 0.009155 | 0.15106 | -0.086976 | 0.22431 | -0.013733 | 0.32501 | 123.1613 | 0.082398 | 123.1522 | 123.2666 | 123.0469 | 123.0423 | 122.9736 | -123.2529 | -123.1018 | 122.937 | 123.0789 | 59.4086 | 59.1934
462.8594 | 123.2849 | -59.761 | 63.2767 | -0.01831 | 0.0027835 | 0.064785 | 0.067364 | 0.0011493 | -0.0010255 | -0.001489 | 0.012909 | 0.0018436 | 0.068539 | 0.057911 | -0.0047552 | 0.00483 | 0.0032749 | -0.25177 | 63.2675 | -59.9396 | 63.2812 | -59.5459 | -59.9442 | 0.004578 | -0.42572 | 63.2446 | -59.8114 | 63.3682 | -59.697 | -59.7931 | -59.5734 | -0.17853 | -0.009155 | 0.004578 | 0.21515 | 59.7656 | -0.18311 | 59.9442 | -0.004578 | -0.050354 | -0.032043 | 0.091553 | 0.064087 | 0.18768 | -0.032044 | 0.23804 | 0.01831 | 0.39368 | 123.2208 | 0.11444 | 123.1796 | 123.2071 | 123.056 | 123.0286 | 123.0057 | -123.2162 | -123.0881 | 123.0423 | 123.1293 | 59.5093 | 59.3353
463.8906 | 123.1979 | -59.7748 | 63.3133 | -0.071716 | 0.00086086 | 0.063931 | 0.067364 | 0.0039263 | -0.0016663 | -0.0010618 | -0.014557 | 0.0024844 | 0.067257 | 0.068165 | -0.006037 | 0.00483 | -0.0012113 | -0.27466 | 63.3087 | -59.9716 | 63.1119 | -59.3353 | -60.054 | -0.23346 | -0.52185 | 63.2767 | -59.8389 | 63.3041 | -59.7885 | -59.9213 | -59.6466 | -0.19684 | -0.004577 | -0.20142 | 0.43945 | 59.5413 | -0.27924 | 59.7382 | -0.082397 | -0.064087 | -0.036621 | -0.009155 | -0.013733 | 0.12817 | -0.14648 | 0.19226 | -0.082398 | 0.63629 | 123.0835 | 0.050354 | 123.143 | 123.2803 | 123.1155 | 123.0835 | 123.0515 | -123.2849 | -123.1522 | 122.8867 | 123.0789 | 59.5001 | 59.2529
464.8594 | 123.2117 | -59.7794 | 63.3224 | -0.079346 | 0.0040653 | 0.063717 | 0.0695 | -0.0041913 | -0.00017087 | -0.0017026 | -0.017609 | 0.0018436 | 0.068325 | 0.064747 | -0.0058234 | 0.0033346 | -0.0029203 | -0.30212 | 63.3408 | -59.9579 | 63.0295 | -59.697 | -59.9991 | -0.10986 | -0.52185 | 63.2904 | -59.8434 | 63.2904 | -59.7839 | -59.8801 | -59.642 | -0.17853 | 0.01831 | -0.29297 | 0.082398 | 59.6695 | -0.21973 | 59.848 | -0.041198 | -0.064087 | -0.032044 | -0.032044 | -0.004578 | 0.13733 | -0.10071 | 0.20142 | -0.036621 | 0.26093 | 122.9874 | 0.059509 | 123.1338 | 123.2986 | 123.1338 | 123.1201 | 123.0698 | -123.2803 | -123.1659 | 122.8088 | 123.0698 | 59.4772 | 59.2575
465.8906 | 123.2529 | -59.7794 | 63.2721 | -0.13275 | 0.0021427 | 0.062008 | 0.06181 | 0.0013629 | -0.0023071 | -0.0021298 | 0.0037536 | 0.0012028 | 0.070461 | 0.065174 | -0.0058234 | 0.0054708 | -0.00057046 | -0.3479 | 63.2675 | -59.9762 | 63.121 | -59.5459 | -60.0815 | -0.17853 | -0.65002 | 63.2446 | -59.8526 | 63.3224 | -59.761 | -59.8709 | -59.6146 | -0.19684 | -0.004578 | -0.15106 | 0.23346 | 59.6008 | -0.30212 | 59.7977 | -0.10529 | -0.073242 | -0.027466 | 0.050354 | 0.018311 | 0.1648 | -0.091553 | 0.23804 | -0.018311 | 0.4303 | 123.0972 | 0.091553 | 123.175 | 123.2437 | 123.0972 | 123.0469 | 123.024 | -123.2483 | -123.1247 | 122.9004 | 123.1018 | 59.4315 | 59.1293
466.8594 | 123.2117 | -59.7519 | 63.3133 | -0.041199 | 0.0025699 | 0.063717 | 0.069286 | 0.0041399 | -0.0012391 | 0.00086083 | 0.040375 | 0.0024844 | 0.068539 | 0.069233 | -0.0064642 | 0.0063254 | -0.0018521 | -0.28381 | 63.3545 | -59.9762 | 63.2172 | -59.6283 | -60.1776 | -0.1831 | -0.63629 | 63.3041 | -59.8389 | 63.3362 | -59.761 | -59.9121 | -59.61 | -0.2243 | 0.041199 | -0.09613 | 0.1236 | 59.5688 | -0.42572 | 59.7931 | -0.20142 | -0.086975 | -0.009155 | 0.022889 | -0.009155 | 0.14191 | -0.16022 | 0.22888 | -0.073242 | 0.3479 | 123.1934 | 0.07782 | 123.175 | 123.3307 | 123.143 | 123.1064 | 123.056 | -123.2895 | -123.1522 | 122.9691 | 123.0881 | 59.4681 | 59.1156
467.8906 | 123.3261 | -59.7336 | 63.2767 | -0.048828 | 0.0017155 | 0.064572 | 0.067364 | 0.00050853 | -0.0025207 | -0.0029844 | 0.0098572 | 0.0014164 | 0.070461 | 0.065388 | -0.0047552 | 0.0063254 | -0.00035666 | -0.2655 | 63.327 | -59.935 | 63.2812 | -59.523 | -59.9075 | 0.013733 | -0.41199 | 63.2721 | -59.8022 | 63.4003 | -59.6512 | -59.7748 | -59.5276 | -0.20142 | 0.050354 | 0.004578 | 0.21057 | 59.7473 | -0.17395 | 59.9487 | 0.027466 | -0.068664 | -0.004577 | 0.1236 | 0.082398 | 0.20599 | -0.041198 | 0.27466 | 0.027466 | 0.41199 | 123.2162 | 0.15106 | 123.2025 | 123.262 | 123.0743 | 123.0606 | 123.0057 | -123.2117 | -123.0789 | 123.0148 | 123.1339 | 59.4681 | 59.3216
468.8594 | 123.2254 | -59.7473 | 63.3087 | -0.01831 | 0.0010745 | 0.063076 | 0.065868 | 0.00072213 | -0.00059807 | -0.0012754 | 0.0098572 | 0.0012028 | 0.068112 | 0.071156 | -0.0058234 | 0.0054708 | 0.0015659 | -0.24719 | 63.3362 | -59.9304 | 63.2721 | -59.5596 | -59.9487 | -0.004578 | -0.46692 | 63.2767 | -59.7977 | 63.3133 | -59.7336 | -59.8526 | -59.6146 | -0.18311 | 0.027466 | -0.036621 | 0.18768 | 59.7427 | -0.20142 | 59.9258 | -0.01831 | -0.050354 | -0.032044 | 0.004577 | 0.013732 | 0.13275 | -0.10529 | 0.18311 | -0.054932 | 0.37079 | 123.2025 | 0.064086 | 123.111 | 123.2666 | 123.0743 | 123.0835 | 123.024 | -123.2391 | -123.1064 | 123.0194 | 123.0606 | 59.5001 | 59.2804
469.8906 | 123.2803 | -59.7336 | 63.3179 | -0.079346 | 0.00022006 | 0.062008 | 0.066937 | 0.0024311 | -0.0046571 | -0.0019162 | -0.017609 | 0.00163 | 0.069821 | 0.06197 | -0.0049688 | 0.0046164 | -0.0029203 | -0.23804 | 63.2904 | -59.9167 | 63.2904 | -59.5367 | -59.9121 | 0 | -0.43488 | 63.2767 | -59.7885 | 63.3682 | -59.6924 | -59.8114 | -59.5551 | -0.18311 | -0.027466 | -0.027466 | 0.19684 | 59.7336 | -0.17853 | 59.9167 | 0.004578 | -0.054931 | -0.041199 | 0.050354 | 0.041199 | 0.17853 | -0.077819 | 0.23346 | -0.022888 | 0.37994 | 123.2071 | 0.09613 | 123.1567 | 123.2071 | 123.0652 | 123.024 | 123.0103 | -123.2346 | -123.1064 | 123.024 | 123.1018 | 59.4955 | 59.2987
470.8594 | 123.2574 | -59.7336 | 63.3316 | -0.033569 | 0.0012881 | 0.062008 | 0.066937 | 0.00050853 | -0.0023071 | -0.0023434 | -0.026764 | 0.0014164 | 0.068539 | 0.061543 | -0.0066778 | 0.0050436 | 0.00028414 | -0.26093 | 63.3224 | -59.9213 | 63.2858 | -59.5505 | -59.9075 | 0.004578 | -0.43945 | 63.2904 | -59.7794 | 63.3682 | -59.7107 | -59.816 | -59.5825 | -0.18768 | -0.009155 | -0.045776 | 0.18311 | 59.7382 | -0.17395 | 59.9258 | 0.013733 | -0.045776 | -0.041199 | 0.036621 | 0.022889 | 0.15106 | -0.082397 | 0.19684 | -0.036621 | 0.37079 | 123.2071 | 0.068665 | 123.1476 | 123.2437 | 123.0698 | 123.056 | 123.024 | -123.2529 | -123.111 | 123.0194 | 123.1018 | 59.4727 | 59.2941
471.9062 | 123.2071 | -59.7427 | 63.3087 | -0.02594 | 0.0023563 | 0.063717 | 0.068218 | -0.00098687 | -0.0038025 | -0.0019162 | -0.096954 | 0.0022708 | 0.069393 | 0.064961 | -0.0058234 | 0.0067526 | 0.0013521 | -0.28839 | 63.3499 | -59.9487 | 63.2355 | -59.6237 | -59.9945 | -0.059509 | -0.50354 | 63.3133 | -59.816 | 63.3545 | -59.6924 | -59.848 | -59.5963 | -0.20599 | 0.041199 | -0.073242 | 0.11902 | 59.6832 | -0.25177 | 59.8892 | -0.045777 | -0.073242 | 0.004577 | 0.045776 | 0.050354 | 0.14648 | -0.10529 | 0.21973 | -0.032043 | 0.32501 | 123.1842 | 0.1236 | 123.1705 | 123.2986 | 123.1293 | 123.0927 | 123.056 | -123.2574 | -123.1247 | 122.9782 | 123.0972 | 59.4543 | 59.2392
472.8594 | 123.2117 | -59.7565 | 63.3179 | -0.079346 | 0.0017155 | 0.06329 | 0.065014 | -0.00055967 | -0.0014527 | -0.0019162 | -0.014557 | 0.0018436 | 0.070889 | 0.068165 | -0.0047552 | 0.0039756 | 0.0022067 | -0.26093 | 63.3362 | -59.9304 | 63.2355 | -59.6054 | -59.9716 | -0.032043 | -0.53101 | 63.327 | -59.7702 | 63.3453 | -59.7839 | -59.8572 | -59.5917 | -0.17395 | 0.018311 | -0.082397 | 0.15106 | 59.7244 | -0.21515 | 59.8984 | -0.041199 | -0.013733 | 0.009155 | 0.027466 | -0.027466 | 0.16479 | -0.10071 | 0.17853 | -0.086975 | 0.32501 | 123.1659 | -0.013733 | 123.1155 | 123.2666 | 123.0972 | 123.0927 | 123.0835 | -123.2483 | -123.0881 | 122.9919 | 123.1018 | 59.4955 | 59.2255
473.8906 | 123.1979 | -59.7244 | 63.3224 | 0.019837 | 6.46e-06 | 0.063931 | 0.066296 | 0.0026447 | 0.0013245 | 0.0010746 | -0.051178 | 0.0024844 | 0.068539 | 0.066242 | -0.006037 | 0.00483 | -0.00014306 | -0.38452 | 63.4048 | -59.9396 | 63.2126 | -59.6649 | -60.0266 | -0.073242 | -0.54474 | 63.3316 | -59.8114 | 63.3133 | -59.761 | -59.8984 | -59.6375 | -0.21515 | 0.082397 | -0.10986 | 0.059509 | 59.6512 | -0.30212 | 59.8663 | -0.086975 | -0.086975 | 0.009155 | -0.009156 | -0.036621 | 0.086975 | -0.17395 | 0.17395 | -0.086975 | 0.27466 | 123.1522 | 0.050354 | 123.1247 | 123.3444 | 123.143 | 123.1293 | 123.056 | -123.262 | -123.1338 | 122.937 | 123.0377 | 59.3399 | 59.1797
474.8594 | 123.2895 | -59.7061 | 63.4094 | 0.0045776 | 0.0027835 | 0.063717 | 0.067791 | 0.0060627 | -0.0029481 | -0.00084817 | -0.0023498 | 0.00163 | 0.068325 | 0.067311 | -0.0049688 | 0.006539 | 0.0026339 | -0.25635 | 63.3133 | -59.9258 | 63.2629 | -59.5779 | -59.9304 | -0.022888 | -0.49439 | 63.2996 | -59.8068 | 63.3408 | -59.7427 | -59.8389 | -59.5001 | -0.21973 | -0.096131 | -0.14648 | 0.12817 | 59.6832 | -0.2243 | 59.903 | -0.004578 | -0.10071 | -0.10986 | -0.068665 | -0.036621 | 0.20599 | -0.13275 | 0.3067 | -0.032043 | 0.3479 | 123.1888 | 0.064087 | 123.1476 | 123.2391 | 123.1064 | 123.0194 | 123.0057 | -123.3353 | -123.2162 | 122.9691 | 123.0469 | 59.4498 | 59.2117
475.8906 | 123.2849 | -59.697 | 63.3087 | -0.056457 | -0.00063454 | 0.063504 | 0.065014 | -0.0016279 | -0.0023071 | -0.002557 | -0.011505 | 0.0029116 | 0.067898 | 0.060902 | -0.0062506 | 0.0039756 | -0.0020657 | -0.33417 | 63.3224 | -59.9396 | 63.2401 | -59.5871 | -59.9487 | -0.082397 | -0.54016 | 63.2996 | -59.8068 | 63.3957 | -59.6741 | -59.7748 | -59.5367 | -0.24262 | 0.013733 | -0.068665 | 0.10986 | 59.6146 | -0.25177 | 59.8572 | -0.009155 | -0.10986 | -0.009155 | 0.086975 | 0.022888 | 0.16022 | -0.07782 | 0.27008 | 0.032044 | 0.35248 | 123.1796 | 0.13275 | 123.2025 | 123.262 | 123.1064 | 123.0194 | 122.9965 | -123.2483 | -123.1155 | 122.937 | 123.0927 | 59.3628 | 59.1568
476.8594 | 123.1888 | -59.7244 | 63.3545 | 0.10376 | 0.00086086 | 0.061154 | 0.066937 | 0.00072213 | -0.0020935 | 0.00022003 | -0.048126 | 0.00098899 | 0.068112 | 0.058979 | -0.0053962 | 0.0058982 | -0.0029203 | -0.35706 | 63.4003 | -59.9396 | 63.2126 | -59.642 | -60.022 | -0.059509 | -0.56763 | 63.3362 | -59.8022 | 63.3316 | -59.7656 | -59.8801 | -59.6054 | -0.21515 | 0.045777 | -0.14191 | 0.082397 | 59.6649 | -0.29755 | 59.8801 | -0.082398 | -0.07782 | -0.01831 | -0.022888 | -0.041199 | 0.11902 | -0.15564 | 0.19684 | -0.07782 | 0.29755 | 123.1522 | 0.036621 | 123.1338 | 123.3398 | 123.1384 | 123.1247 | 123.0606 | -123.2941 | -123.1567 | 122.937 | 123.056 | 59.3674 | 59.1568
477.8906 | 123.3261 | -59.697 | 63.2904 | -0.094604 | 0.0010745 | 0.063076 | 0.066296 | -0.0033369 | -0.00059807 | -0.004266 | -0.0023498 | 0.0012028 | 0.067257 | 0.068165 | -0.0062506 | 0.006539 | -0.0016385 | -0.32501 | 63.3041 | -59.9487 | 63.2492 | -59.5917 | -59.9716 | -0.091553 | -0.55847 | 63.295 | -59.7885 | 63.3911 | -59.6786 | -59.7977 | -59.5505 | -0.25177 | 0.013733 | -0.041198 | 0.10528 | 59.6054 | -0.27466 | 59.8572 | -0.022889 | -0.091553 | 0.004578 | 0.10071 | 0.01831 | 0.14648 | -0.10071 | 0.23804 | -0.009155 | 0.35705 | 123.1979 | 0.10986 | 123.1796 | 123.2529 | 123.0835 | 123.0011 | 122.9919 | -123.2391 | -123.0789 | 122.9462 | 123.0881 | 59.3719 | 59.1385
478.8594 | 123.1979 | -59.7382 | 63.3774 | -0.01831 | 0.0017155 | 0.064145 | 0.061169 | -0.0014143 | -0.0027345 | -0.0044796 | -0.035919 | 0.00163 | 0.069607 | 0.060688 | -0.0079596 | 0.0046164 | 0.0019931 | -0.30212 | 63.3957 | -59.9396 | 63.0707 | -59.6466 | -59.9533 | -0.10986 | -0.54474 | 63.3362 | -59.8297 | 63.3133 | -59.7473 | -59.848 | -59.6329 | -0.20142 | 0.018311 | -0.3067 | 0.091553 | 59.6283 | -0.21515 | 59.8297 | -0.013733 | -0.091553 | -0.041198 | -0.064087 | -0.009155 | 0.10529 | -0.10986 | 0.19684 | -0.01831 | 0.29297 | 123.0103 | 0.082398 | 123.143 | 123.3353 | 123.1659 | 123.1338 | 123.0743 | -123.317 | -123.2071 | 122.8088 | 123.0515 | 59.436 | 59.1934
479.8906 | 123.2666 | -59.729 | 63.3087 | -0.094604 | 0.0053471 | 0.06094 | 0.065868 | 0.00093573 | 0.00046993 | -0.0044796 | -0.0084534 | 0.00098899 | 0.067471 | 0.060261 | -0.0058234 | 0.0058982 | -0.0022793 | -0.21973 | 63.3499 | -59.9304 | 63.2584 | -59.5963 | -60.0174 | -0.1236 | -0.61798 | 63.2721 | -59.8206 | 63.3499 | -59.7427 | -59.8389 | -59.5642 | -0.20142 | 0.041199 | -0.050354 | 0.13275 | 59.6054 | -0.28839 | 59.8068 | -0.086975 | -0.091553 | -0.036621 | 0.041199 | -0.013733 | 0.1648 | -0.10986 | 0.25635 | -0.01831 | 0.33417 | 123.1888 | 0.07782 | 123.1705 | 123.2803 | 123.0927 | 123.0789 | 123.0011 | -123.2391 | -123.1293 | 122.9874 | 123.0789 | 59.5093 | 59.111
480.8594 | 123.2071 | -59.7336 | 63.3545 | -0.064087 | 0.0010745 | 0.062649 | 0.0648 | 0.0024311 | -0.0020935 | -0.002557 | -0.13663 | 0.0039798 | 0.067257 | 0.06902 | -0.0066778 | 0.0044028 | -0.0014249 | -0.28839 | 63.3591 | -59.8938 | 63.2355 | -59.6237 | -59.6649 | 0.13275 | -0.50812 | 63.3408 | -59.816 | 63.3362 | -59.7336 | -59.8984 | -59.6237 | -0.16022 | 0.004578 | -0.11902 | 0.10986 | 59.8663 | 0.068665 | 60.0266 | 0.22888 | -0.082397 | -0.013733 | -0.01831 | 0 | 0.10986 | -0.16479 | 0.19226 | -0.082397 | 0.27008 | 123.1293 | 0.082397 | 123.1522 | 123.2529 | 123.1567 | 123.0927 | 123.0743 | -123.2483 | -123.1705 | 122.9691 | 123.0698 | 59.4452 | 59.2255
481.8906 | 123.1613 | -59.7336 | 63.3636 | -0.041199 | 0.0021427 | 0.063931 | 0.068218 | 0.0015765 | -0.0040161 | -0.0034116 | -0.051178 | 0.0020572 | 0.068112 | 0.064106 | -0.0073188 | 0.0052572 | -0.0046293 | -0.33417 | 63.3636 | -59.9487 | 63.2217 | -59.6146 | -59.9579 | -0.073242 | -0.57678 | 63.3682 | -59.7977 | 63.3408 | -59.761 | -59.8663 | -59.6008 | -0.21515 | 0 | -0.14191 | 0.11902 | 59.6603 | -0.2243 | 59.8755 | -0.009156 | -0.064086 | 0.004578 | -0.022888 | -0.027465 | 0.13275 | -0.13275 | 0.19684 | -0.068665 | 0.33417 | 123.1705 | 0.036621 | 123.1384 | 123.3124 | 123.1659 | 123.0972 | 123.1018 | -123.3124 | -123.1613 | 122.9553 | 123.0743 | 59.3994 | 59.1568
482.8594 | 123.2574 | -59.6832 | 63.3408 | -0.064087 | 0.0010745 | 0.063504 | 0.067791 | -0.0012005 | -0.0020935 | 0.0010746 | -0.011505 | 0.0037662 | 0.068966 | 0.06432 | -0.0049688 | 0.0063254 | -0.0033475 | -0.23346 | 63.3591 | -59.8801 | 63.3316 | -59.5047 | -59.8801 | 0.004578 | -0.44403 | 63.327 | -59.7565 | 63.414 | -59.6603 | -59.7565 | -59.5093 | -0.19684 | 0.018311 | -0.009155 | 0.17853 | 59.6878 | -0.19684 | 59.8846 | 0 | -0.073242 | -0.013733 | 0.073242 | 0.022889 | 0.17395 | -0.073242 | 0.24719 | 0 | 0.37537 | 123.2117 | 0.096131 | 123.1705 | 123.2391 | 123.0835 | 123.0423 | 123.0103 | -123.2208 | -123.0972 | 123.0148 | 123.0972 | 59.4498 | 59.2392
483.8906 | 123.2895 | -59.697 | 63.295 | -0.02594 | 0.00086086 | 0.061581 | 0.065868 | 0.0039263 | -0.0016663 | -0.0023434 | 0.019012 | 0.0012028 | 0.068753 | 0.064106 | -0.006037 | 0.0039756 | -0.00057046 | -0.32044 | 63.3453 | -59.9075 | 63.2858 | -59.5459 | -59.9075 | -0.045776 | -0.49896 | 63.2996 | -59.7748 | 63.4232 | -59.6512 | -59.7473 | -59.5184 | -0.21057 | 0.050354 | -0.009155 | 0.15106 | 59.6512 | -0.21057 | 59.8618 | 0 | -0.07782 | 0.004578 | 0.12817 | 0.045776 | 0.17853 | -0.050354 | 0.25635 | 0.027466 | 0.36163 | 123.1934 | 0.1236 | 123.1979 | 123.2529 | 123.0743 | 123.0423 | 122.9965 | -123.2025 | -123.0698 | 122.9828 | 123.1201 | 59.3765 | 59.198
484.8594 | 123.2437 | -59.7198 | 63.3636 | -0.01831 | 0.00064726 | 0.063076 | 0.068218 | -0.0020551 | -0.0023071 | -0.00042077 | -0.078644 | 0.0029116 | 0.069607 | 0.067097 | -0.0047552 | 0.0056846 | 7.0538e-05 | -0.30212 | 63.3957 | -59.9258 | 63.2034 | -59.6329 | -59.9808 | -0.091553 | -0.5722 | 63.3636 | -59.7839 | 63.3545 | -59.7244 | -59.8618 | -59.5825 | -0.20599 | 0.032044 | -0.16022 | 0.086975 | 59.6283 | -0.26092 | 59.8343 | -0.054932 | -0.064087 | 0 | -0.009155 | -0.004577 | 0.13733 | -0.14191 | 0.20142 | -0.077819 | 0.29297 | 123.1293 | 0.05951 | 123.1384 | 123.3215 | 123.1476 | 123.1155 | 123.0835 | -123.2895 | -123.1476 | 122.9233 | 123.0743 | 59.4177 | 59.1476
485.8906 | 123.1842 | -59.7198 | 63.3636 | -0.01831 | 0.00086086 | 0.057736 | 0.067791 | -0.0016279 | -0.0012391 | -0.0019162 | -0.017609 | 0.0022708 | 0.068325 | 0.069874 | -0.0047552 | 0.0076072 | 0.00028414 | -0.064087 | 63.4598 | -59.8618 | 63.1943 | -59.5779 | -59.9579 | -0.086975 | -0.57678 | 63.382 | -59.7656 | 63.3499 | -59.7244 | -59.8663 | -59.6008 | -0.14191 | 0.096131 | -0.16937 | 0.14191 | 59.6329 | -0.23804 | 59.7748 | -0.096131 | -0.045776 | 0.018311 | -0.013732 | -0.004577 | 0.11902 | -0.14648 | 0.16479 | -0.10071 | 0.28381 | 123.056 | 0.041199 | 123.1155 | 123.3215 | 123.1476 | 123.1796 | 123.1018 | -123.2254 | -123.1293 | 122.9141 | 123.0698 | 59.6558 | 59.1431
486.8594 | 123.2071 | -59.6924 | 63.3591 | -0.041199 | 0.0010745 | 0.062222 | 0.069714 | 0.0024311 | -0.00038447 | 0.0010746 | -0.069489 | 0.0031254 | 0.067684 | 0.067738 | -0.0064642 | 0.0054708 | -0.00099766 | -0.30212 | 63.4048 | -59.9258 | 63.2538 | -59.5871 | -59.9304 | -0.07782 | -0.52643 | 63.3682 | -59.7931 | 63.3499 | -59.697 | -59.7382 | -59.4955 | -0.23346 | 0.045776 | -0.10529 | 0.10529 | 59.6146 | -0.23804 | 59.848 | -0.004578 | -0.10071 | 0.009155 | -0.009155 | -0.004577 | 0.19684 | -0.045776 | 0.29755 | 0.054932 | 0.33875 | 123.1796 | 0.096131 | 123.143 | 123.3307 | 123.1613 | 123.0972 | 123.0606 | -123.2849 | -123.1522 | 122.9462 | 123.0423 | 59.3903 | 59.166
487.8906 | 123.175 | -59.7244 | 63.3682 | -0.094604 | 0.0027835 | 0.062222 | 0.068218 | 8.1126e-05 | -0.0033753 | -0.00042077 | -0.023712 | 0.0029116 | 0.071316 | 0.063252 | -0.0056098 | 0.0067526 | 0.00092494 | -0.27924 | 63.3774 | -59.9167 | 63.3728 | -59.7702 | -60.1959 | -0.059509 | -0.54932 | 63.3682 | -59.8114 | 63.3408 | -59.7382 | -59.8068 | -59.5688 | -0.19226 | 0.009155 | 0.004578 | -0.045777 | 59.6649 | -0.4715 | 59.8572 | -0.27924 | -0.086975 | 0 | -0.027466 | -0.013733 | 0.15564 | -0.082398 | 0.24261 | 0.004577 | 0.14648 | 123.2895 | 0.073242 | 123.1522 | 123.2941 | 123.1796 | 123.1018 | 123.0927 | -123.2849 | -123.1796 | 123.0972 | 123.0652 | 59.4452 | 59.1751
488.8594 | 123.1659 | -59.697 | 63.382 | -0.02594 | 0.00086086 | 0.066281 | 0.06715 | -0.0016279 | -0.0010255 | -0.0010618 | -0.048126 | 0.0035526 | 0.06918 | 0.068379 | -0.0058234 | 0.0063254 | -0.0020657 | -0.46234 | 63.4277 | -59.8984 | 63.2492 | -59.6237 | -59.9762 | -0.073242 | -0.54932 | 63.3728 | -59.7748 | 63.3453 | -59.7198 | -59.848 | -59.5734 | -0.20142 | 0.045776 | -0.13275 | 0.073242 | 59.6237 | -0.27924 | 59.8251 | -0.07782 | -0.07782 | -0.009155 | -0.036621 | -0.022889 | 0.1236 | -0.15106 | 0.20142 | -0.073242 | 0.27466 | 123.1476 | 0.054931 | 123.1201 | 123.3261 | 123.1476 | 123.1247 | 123.0698 | -123.2803 | -123.1567 | 122.9462 | 123.0423 | 59.2346 | 59.1476
489.8906 | 123.2025 | -59.6832 | 63.3728 | -0.056457 | 0.0027835 | 0.063076 | 0.066082 | -0.0016279 | -0.0023071 | 0.0010746 | 0.080048 | 0.0052616 | 0.070889 | 0.063038 | -0.0075324 | 0.0035482 | -0.0018521 | -0.27924 | 63.3957 | -59.8984 | 63.2584 | -59.5551 | -59.9533 | -0.086975 | -0.737 | 63.3865 | -59.7473 | 63.3499 | -59.7427 | -59.848 | -59.5963 | -0.21515 | 0.022888 | -0.11444 | 0.12817 | 59.5963 | -0.27008 | 59.8114 | -0.054932 | -0.064086 | 0.013733 | -0.022888 | -0.059509 | 0.086976 | -0.16479 | 0.15106 | -0.10071 | 0.34332 | 123.1567 | 0.004577 | 123.0972 | 123.2941 | 123.1338 | 123.0789 | 123.0698 | -123.2712 | -123.1201 | 122.9416 | 123.0331 | 59.404 | 58.9462
490.8594 | 123.1888 | -59.7107 | 63.3865 | -0.079346 | 0.0010745 | 0.063504 | 0.066509 | 0.00093573 | 0.00025633 | -0.0044796 | -0.035919 | 0.0018436 | 0.069821 | 0.065388 | -0.0073188 | 0.0029074 | 0.0030611 | -0.31586 | 63.4048 | -59.9075 | 63.1851 | -59.5093 | -60.022 | -0.082397 | -0.5722 | 63.3499 | -59.7565 | 63.3499 | -59.7061 | -59.8251 | -59.5963 | -0.19684 | 0.01831 | -0.20142 | 0.20142 | 59.6283 | -0.31128 | 59.8251 | -0.11444 | -0.045777 | -0.036621 | -0.036621 | 0.004577 | 0.11444 | -0.11444 | 0.16022 | -0.068664 | 0.39826 | 123.0927 | 0.050354 | 123.1064 | 123.3124 | 123.1064 | 123.1155 | 123.0606 | -123.2941 | -123.143 | 122.8958 | 123.0606 | 59.3948 | 59.1385
491.8906 | 123.175 | -59.7107 | 63.3728 | -0.02594 | 0.0023563 | 0.062008 | 0.06715 | 0.00029473 | 0.0015381 | -0.005975 | -0.035919 | 0.0020572 | 0.069393 | 0.060688 | -0.006037 | 0.006539 | -0.00078406 | -0.27008 | 63.382 | -59.8938 | 63.2858 | -59.5184 | -59.8984 | -0.045776 | -0.50812 | 63.3591 | -59.761 | 63.2584 | -59.7336 | -59.8068 | -59.5596 | -0.18311 | 0.009155 | -0.086975 | 0.19226 | 59.6649 | -0.18768 | 59.848 | -0.004577 | -0.050354 | -0.013733 | -0.11444 | -0.022889 | 0.15106 | -0.096131 | 0.20142 | -0.045777 | 0.37537 | 123.1796 | 0.027465 | 123.0194 | 123.2758 | 123.1201 | 123.0927 | 123.0698 | -123.2666 | -123.1338 | 122.9965 | 122.9691 | 59.4406 | 59.2026
492.8594 | 123.2391 | -59.6924 | 63.3591 | -0.056457 | 0.0027835 | 0.063504 | 0.069714 | 0.00093573 | -0.0014527 | -0.0034116 | -0.05423 | 0.003339 | 0.071957 | 0.067097 | -0.0049688 | 0.0078208 | -0.0024931 | -0.29755 | 63.414 | -59.8938 | 63.2446 | -59.5963 | -59.9716 | -0.082397 | -0.54474 | 63.3865 | -59.761 | 63.3957 | -59.6832 | -59.8114 | -59.5322 | -0.20142 | 0.054931 | -0.11444 | 0.096131 | 59.61 | -0.27924 | 59.8114 | -0.07782 | -0.068664 | 0.027466 | 0.036621 | 0.009155 | 0.16022 | -0.11902 | 0.22888 | -0.050354 | 0.29755 | 123.1384 | 0.077819 | 123.1567 | 123.3078 | 123.1476 | 123.1064 | 123.0789 | -123.2529 | -123.1201 | 122.937 | 123.0881 | 59.3948 | 59.1476
493.8906 | 123.2208 | -59.697 | 63.382 | -0.01831 | 0.0017155 | 0.060299 | 0.069714 | -0.0012005 | -0.0038025 | -0.00063437 | -0.042023 | 0.0024844 | 0.069393 | 0.065815 | -0.004328 | 0.0046164 | 0.0022067 | -0.32501 | 63.4644 | -59.8663 | 63.2309 | -59.5779 | -59.9579 | -0.091553 | -0.55847 | 63.4094 | -59.7382 | 63.3728 | -59.7015 | -59.8206 | -59.5505 | -0.16937 | 0.082397 | -0.15106 | 0.11902 | 59.6054 | -0.26093 | 59.7748 | -0.091553 | -0.041199 | 0.027466 | -0.009155 | -0.004578 | 0.14648 | -0.1236 | 0.18768 | -0.082398 | 0.28839 | 123.0972 | 0.036621 | 123.111 | 123.3307 | 123.1476 | 123.1613 | 123.1064 | -123.2483 | -123.1201 | 122.9279 | 123.0698 | 59.3719 | 59.1385
494.8594 | 123.2208 | -59.7153 | 63.3774 | -0.094604 | 0.0015019 | 0.061795 | 0.068646 | -0.0018415 | 0.00046993 | -0.004266 | -0.05423 | 0.0012028 | 0.067684 | 0.06667 | -0.007746 | 0.00483 | -0.00099766 | -0.31586 | 63.414 | -59.9075 | 63.2492 | -59.6054 | -59.9442 | -0.09613 | -0.56305 | 63.4003 | -59.7565 | 63.3774 | -59.6832 | -59.816 | -59.5413 | -0.19226 | 0.036621 | -0.12817 | 0.10986 | 59.6191 | -0.22888 | 59.8114 | -0.036621 | -0.041199 | 0.022889 | 0 | 0.032043 | 0.17395 | -0.10071 | 0.21515 | -0.059509 | 0.30212 | 123.1567 | 0.073242 | 123.1338 | 123.3215 | 123.1567 | 123.1293 | 123.1155 | -123.2849 | -123.1338 | 122.9645 | 123.0927 | 59.3994 | 59.1522
495.8906 | 123.3307 | -59.6603 | 63.3682 | -0.12512 | 0.0017155 | 0.061581 | 0.068218 | 0.0026447 | -0.0010255 | -0.0038388 | -0.0054016 | 0.0024844 | 0.067257 | 0.060475 | -0.0053962 | 0.0061118 | -0.0042021 | -0.27924 | 63.3636 | -59.8572 | 63.4186 | -59.5688 | -59.8846 | 0.018311 | -0.39368 | 63.3179 | -59.7198 | 63.4781 | -59.5596 | -59.6786 | -59.4589 | -0.19684 | -0.004578 | 0.050354 | 0.091552 | 59.6786 | -0.22431 | 59.8755 | -0.027466 | -0.05951 | -0.050354 | 0.10986 | 0.10071 | 0.20142 | -0.018311 | 0.26093 | 0.041199 | 0.28839 | 123.2758 | 0.16022 | 123.1979 | 123.2208 | 123.0377 | 123.024 | 122.9782 | -123.2254 | -123.0881 | 123.0789 | 123.1384 | 59.3811 | 59.2667
496.8594 | 123.2162 | -59.6375 | 63.3911 | 0.019837 | 0.0017155 | 0.061581 | 0.066509 | 0.0026447 | -0.0020935 | 0.00086083 | -0.069489 | 0.0022708 | 0.068753 | 0.068592 | -0.007105 | 0.0058982 | 0.00071134 | -0.29755 | 63.4277 | -59.8801 | 63.2904 | -59.5505 | -59.9304 | -0.07782 | -0.70496 | 63.3545 | -59.7931 | 63.4415 | -59.6832 | -59.7702 | -59.5184 | -0.24262 | 0.036621 | -0.10071 | 0.086975 | 59.5596 | -0.29297 | 59.8022 | -0.050354 | -0.15564 | -0.036621 | 0.050354 | -0.045777 | 0.11902 | -0.13275 | 0.27466 | 0.022888 | 0.32959 | 123.1705 | 0.10986 | 123.2346 | 123.3078 | 123.1476 | 123.0652 | 122.9919 | -123.2712 | -123.1842 | 122.9279 | 123.0789 | 59.3399 | 58.9325
497.8906 | 123.2254 | -59.6878 | 63.3224 | -0.10223 | 0.0025699 | 0.062863 | 0.065441 | 0.0028583 | 0.00046993 | -0.0012754 | 0.022064 | 0.00098899 | 0.068539 | 0.064747 | -0.0090278 | 0.006539 | 0.0043429 | -0.34332 | 63.3362 | -59.903 | 63.2812 | -59.5276 | -59.9396 | -0.14648 | -0.61798 | 63.2996 | -59.7382 | 63.3865 | -59.7427 | -59.6558 | -59.491 | -0.21515 | 0.013733 | -0.041199 | 0.16022 | 59.5413 | -0.25177 | 59.7565 | -0.036621 | -0.050354 | -0.022888 | 0.064087 | -0.054932 | 0.19684 | 0.032043 | 0.24719 | 0.082397 | 0.37537 | 123.1842 | -0.004578 | 123.1247 | 123.2391 | 123.0377 | 123.024 | 122.9874 | -123.2254 | -123.0606 | 122.9691 | 123.0743 | 59.3445 | 59.0698
498.8594 | 123.23 | -59.7015 | 63.4186 | -0.01831 | 0.0012881 | 0.061367 | 0.0695 | 0.00029473 | -0.0035889 | 0.0025698 | -0.066437 | 0.0014164 | 0.068539 | 0.063679 | -0.0079596 | 0.0058982 | 0.00071134 | -0.31586 | 63.4323 | -59.8892 | 63.2629 | -59.5779 | -59.9396 | -0.086975 | -0.5722 | 63.4003 | -59.7336 | 63.3636 | -59.697 | -59.8114 | -59.5551 | -0.18768 | 0.013733 | -0.15564 | 0.1236 | 59.6146 | -0.23804 | 59.8022 | -0.050354 | -0.032044 | -0.01831 | -0.054932 | 0.004578 | 0.14648 | -0.10986 | 0.17853 | -0.077819 | 0.31128 | 123.1522 | 0.036622 | 123.0972 | 123.3215 | 123.1339 | 123.1338 | 123.1018 | -123.3078 | -123.1522 | 122.9645 | 123.0652 | 59.3857 | 59.1293
499.8906 | 123.2117 | -59.6649 | 63.4003 | -0.033569 | 0.0025699 | 0.062008 | 0.06715 | 0.0028583 | -0.0031617 | -0.001489 | 0.0068054 | 0.003339 | 0.070889 | 0.068806 | -0.0056098 | 0.0050436 | 0.00071134 | -0.27008 | 63.3911 | -59.8572 | 63.2858 | -59.5322 | -59.903 | -0.054932 | -0.32959 | 63.4323 | -59.6924 | 63.3591 | -59.6741 | -59.7519 | -59.5596 | -0.19226 | -0.009156 | -0.11444 | 0.13275 | 59.61 | -0.23804 | 59.8022 | -0.045776 | -0.027466 | 0.032043 | -0.041199 | -0.009155 | 0.10529 | -0.086975 | 0.13275 | -0.059509 | 0.32501 | 123.143 | 0.018311 | 123.0515 | 123.2483 | 123.1247 | 123.056 | 123.0972 | -123.2574 | -123.0927 | 122.9507 | 123.024 | 59.3948 | 59.3353
500.8594 | 123.2254 | -59.697 | 63.4277 | -0.010681 | 0.0027835 | 0.063504 | 0.070141 | -0.0024823 | -0.00017087 | -0.0040524 | -0.045074 | 0.0031254 | 0.069821 | 0.065602 | -0.0053962 | 0.0071798 | 0.00049774 | -0.31586 | 63.4506 | -59.8892 | 63.2675 | -59.5825 | -59.935 | -0.082397 | -0.56305 | 63.4277 | -59.7382 | 63.382 | -59.6786 | -59.8114 | -59.5505 | -0.19226 | 0.022889 | -0.16022 | 0.11444 | 59.6146 | -0.23804 | 59.8068 | -0.045777 | -0.041199 | 0 | -0.045776 | 0.01831 | 0.14648 | -0.11444 | 0.18768 | -0.073242 | 0.3067 | 123.1567 | 0.059509 | 123.1201 | 123.3398 | 123.1659 | 123.1476 | 123.1247 | -123.317 | -123.1659 | 122.9645 | 123.0789 | 59.3811 | 59.1339
501.9062 | 123.2941 | -59.6558 | 63.327 | -0.033569 | 0.0010745 | 0.07034 | 0.066937 | -0.00013247 | -0.00081187 | -0.002557 | -0.029816 | 0.0012028 | 0.070889 | 0.068592 | -0.0079596 | 0.0056846 | -0.0027067 | -0.52185 | 63.3224 | -59.9304 | 63.3408 | -59.5184 | -59.9442 | -0.1236 | -0.55847 | 63.3087 | -59.7427 | 63.4598 | -59.6283 | -59.729 | -59.4452 | -0.27466 | -0.004577 | 0.013733 | 0.13733 | 59.5322 | -0.28839 | 59.8068 | -0.013733 | -0.086975 | -0.01831 | 0.13275 | 0.027466 | 0.21057 | -0.073242 | 0.29755 | 0.013733 | 0.41199 | 123.2712 | 0.11444 | 123.2025 | 123.2529 | 123.0515 | 122.9782 | 122.9645 | -123.2574 | -123.0698 | 122.9965 | 123.1155 | 59.1339 | 59.0973
502.8594 | 123.2071 | -59.6741 | 63.3911 | -0.02594 | 0.0012881 | 0.062863 | 0.065228 | 0.0028583 | -0.0016663 | -0.0021298 | -0.029816 | 0.0035526 | 0.070248 | 0.061756 | -0.0045416 | 0.0046164 | -0.0035611 | -0.3067 | 63.4598 | -59.8663 | 63.2675 | -59.5596 | -59.9258 | -0.07782 | -0.56763 | 63.4094 | -59.7244 | 63.3774 | -59.6924 | -59.8068 | -59.5413 | -0.19226 | 0.068665 | -0.1236 | 0.11444 | 59.5963 | -0.25177 | 59.7885 | -0.059509 | -0.050354 | 0.018311 | -0.013733 | -0.018311 | 0.13275 | -0.13275 | 0.1831 | -0.082398 | 0.3067 | 123.1338 | 0.032043 | 123.1018 | 123.3261 | 123.1338 | 123.1338 | 123.0835 | -123.2574 | -123.1155 | 122.9416 | 123.0515 | 59.3674 | 59.1064
503.8906 | 123.2986 | -59.6329 | 63.382 | -0.10223 | 0.0017155 | 0.062649 | 0.067577 | 0.0028583 | 4.273e-05 | -0.003198 | 0.025116 | 0.00077539 | 0.070248 | 0.060261 | -0.004328 | 0.0039756 | 0.0019931 | -0.32501 | 63.414 | -59.8663 | 63.3316 | -59.4818 | -59.8572 | -0.050354 | -0.5127 | 63.3591 | -59.7336 | 63.4598 | -59.61 | -59.6878 | -59.4452 | -0.23346 | 0.032043 | -0.050354 | 0.15106 | 59.5825 | -0.2243 | 59.816 | 0.009155 | -0.10071 | -0.022888 | 0.07782 | 0.022889 | 0.18768 | -0.054931 | 0.28839 | 0.045777 | 0.38452 | 123.1979 | 0.1236 | 123.1934 | 123.2803 | 123.0927 | 123.0469 | 122.9919 | -123.2483 | -123.1155 | 122.9645 | 123.0927 | 59.3079 | 59.1202
504.8594 | 123.1934 | -59.6603 | 63.4415 | -0.02594 | 0.0029971 | 0.063076 | 0.069073 | 0.0013629 | -0.0031617 | -0.0040524 | -0.029816 | 0.0031254 | 0.067898 | 0.062184 | -0.0068914 | 0.0058982 | 0.0022067 | -0.28839 | 63.4369 | -59.8755 | 63.2675 | -59.5596 | -59.8984 | -0.059509 | -0.55847 | 63.4323 | -59.729 | 63.3865 | -59.6741 | -59.816 | -59.5322 | -0.21515 | -0.004577 | -0.17395 | 0.10071 | 59.6008 | -0.23804 | 59.816 | -0.022888 | -0.068665 | -0.009155 | -0.054931 | -0.013733 | 0.12817 | -0.15564 | 0.19684 | -0.086975 | 0.31586 | 123.143 | 0.054932 | 123.1155 | 123.3124 | 123.1613 | 123.0972 | 123.0927 | -123.317 | -123.1705 | 122.9279 | 123.0469 | 59.3719 | 59.1019
505.8906 | 123.175 | -59.6741 | 63.4232 | -0.0030519 | 0.0032107 | 0.061795 | 0.068005 | -0.00013247 | -0.0023071 | -0.004266 | -0.026764 | 0.002698 | 0.068539 | 0.064533 | -0.006037 | 0.0063254 | -0.0016385 | -0.3067 | 63.4827 | -59.8801 | 63.2812 | -59.5596 | -59.9304 | -0.073242 | -0.55847 | 63.4186 | -59.729 | 63.3911 | -59.6649 | -59.816 | -59.5413 | -0.20599 | 0.059509 | -0.14191 | 0.11444 | 59.6008 | -0.25635 | 59.8068 | -0.050354 | -0.054932 | -0.004578 | -0.032044 | 0.009155 | 0.13275 | -0.14191 | 0.18768 | -0.086975 | 0.32043 | 123.1613 | 0.064087 | 123.1201 | 123.3627 | 123.1476 | 123.1567 | 123.0927 | -123.3032 | -123.1522 | 122.9553 | 123.0652 | 59.3674 | 59.1156
506.8594 | 123.2529 | -59.6603 | 63.3957 | -0.10986 | 0.0021427 | 0.064999 | 0.066082 | 8.1126e-05 | -0.0027345 | -0.0029844 | -0.081696 | 0.0022708 | 0.068753 | 0.064961 | -0.0081732 | 0.0071798 | 0.0011385 | -0.18768 | 63.446 | -59.8434 | 63.3224 | -59.523 | -59.8892 | -0.091553 | -0.50812 | 63.3865 | -59.7153 | 63.4506 | -59.6466 | -59.7748 | -59.5001 | -0.18311 | 0.050354 | -0.073242 | 0.13733 | 59.5688 | -0.22888 | 59.7519 | -0.045776 | -0.054932 | -0.009155 | 0.054932 | 0.013733 | 0.16022 | -0.11444 | 0.21515 | -0.059509 | 0.32044 | 123.1659 | 0.068665 | 123.1659 | 123.2895 | 123.1018 | 123.1064 | 123.0469 | -123.2391 | -123.111 | 122.9828 | 123.111 | 59.4727 | 59.1522
507.8594 | 123.23 | -59.6329 | 63.4003 | -0.0030519 | 0.00043366 | 0.065426 | 0.065868 | -0.0031231 | -0.0029481 | -0.00063437 | 0.0098572 | 0.00056179 | 0.068112 | 0.060688 | -0.0047552 | 0.0054708 | 0.0024203 | -0.23346 | 63.4186 | -59.8068 | 63.3728 | -59.4315 | -59.8251 | -0.022888 | -0.44403 | 63.3911 | -59.7198 | 63.4598 | -59.5963 | -59.7244 | -59.4543 | -0.17395 | 0.01831 | -0.027466 | 0.20142 | 59.61 | -0.19226 | 59.7839 | -0.01831 | -0.086975 | -0.009156 | 0.059509 | 0.036622 | 0.17853 | -0.091552 | 0.2655 | -0.004577 | 0.37537 | 123.1796 | 0.1236 | 123.1796 | 123.2254 | 123.111 | 123.0515 | 123.024 | -123.2071 | -123.1201 | 123.0057 | 123.0927 | 59.3994 | 59.1888
508.8906 | 123.3032 | -59.6237 | 63.3957 | -0.11749 | 0.0021427 | 0.06329 | 0.06715 | -0.0033369 | -0.00059807 | -0.0027708 | 0.028168 | 0.0012028 | 0.068753 | 0.063252 | -0.0062506 | 0.003762 | -0.0022793 | -0.30212 | 63.4186 | -59.8434 | 63.3682 | -59.4543 | -59.8434 | -0.036621 | -0.5127 | 63.3636 | -59.7107 | 63.4964 | -59.5505 | -59.6741 | -59.4269 | -0.21973 | 0.022888 | -0.027466 | 0.16937 | 59.5871 | -0.21973 | 59.8068 | 0 | -0.086975 | -0.032044 | 0.10071 | 0.073242 | 0.19684 | -0.050354 | 0.28381 | 0.036621 | 0.3891 | 123.2117 | 0.16022 | 123.2071 | 123.262 | 123.0743 | 123.0423 | 122.9874 | -123.2391 | -123.1064 | 122.9919 | 123.1201 | 59.3216 | 59.111
509.8594 | 123.2208 | -59.6558 | 63.4277 | -0.079346 | 0.0019291 | 0.062222 | 0.066509 | -0.0039777 | -0.0010255 | -0.00084817 | -0.0084534 | 0.0022708 | 0.067471 | 0.068165 | -0.0068914 | 0.0041892 | 0.0030611 | -0.27008 | 63.446 | -59.8343 | 63.3362 | -59.4818 | -59.8663 | -0.050354 | -0.51727 | 63.4277 | -59.697 | 63.4323 | -59.6786 | -59.7519 | -59.4864 | -0.17853 | 0.018311 | -0.091552 | 0.17395 | 59.6054 | -0.21057 | 59.7839 | -0.032043 | -0.041198 | 0 | 0.004578 | -0.022888 | 0.16937 | -0.09613 | 0.21057 | -0.054932 | 0.35248 | 123.1705 | 0.01831 | 123.1293 | 123.2803 | 123.1247 | 123.1018 | 123.0835 | -123.262 | -123.1247 | 122.9919 | 123.0881 | 59.3857 | 59.1385
510.8906 | 123.2437 | -59.6191 | 63.4232 | -0.041199 | 0.0027835 | 0.06094 | 0.065441 | 0.0017901 | 0.00025633 | -0.004266 | -0.014557 | 0.0012028 | 0.067257 | 0.061115 | -0.0073188 | 0.0058982 | -0.0027067 | -0.24719 | 63.446 | -59.8114 | 63.3682 | -59.4452 | -59.816 | -0.009155 | -0.4715 | 63.4094 | -59.7107 | 63.4506 | -59.6054 | -59.729 | -59.4818 | -0.19226 | 0.022888 | -0.054932 | 0.17395 | 59.61 | -0.19684 | 59.8022 | -0.004578 | -0.091552 | -0.013733 | 0.027466 | 0.013733 | 0.13733 | -0.10986 | 0.22888 | -0.018311 | 0.36621 | 123.1796 | 0.10529 | 123.1613 | 123.2574 | 123.1201 | 123.0652 | 123.0286 | -123.2346 | -123.1338 | 122.9874 | 123.0698 | 59.3719 | 59.1476
511.8594 | 123.2162 | -59.6375 | 63.4781 | -0.01831 | 0.0017155 | 0.062863 | 0.069073 | 0.00050853 | -0.0031617 | -0.0010618 | -0.057281 | 0.00163 | 0.067044 | 0.067738 | -0.0053962 | 0.0058982 | 0.00071134 | -0.31128 | 63.4735 | -59.8389 | 63.3087 | -59.5596 | -59.903 | -0.086975 | -0.56305 | 63.4232 | -59.7153 | 63.414 | -59.6512 | -59.7839 | -59.5001 | -0.20142 | -0.004577 | -0.16937 | 0.07782 | 59.5505 | -0.2655 | 59.7519 | -0.064087 | -0.07782 | -0.054931 | -0.064087 | -0.013733 | 0.13733 | -0.14648 | 0.21515 | -0.068665 | 0.27924 | 123.1476 | 0.064087 | 123.1293 | 123.3124 | 123.1384 | 123.111 | 123.0606 | -123.317 | -123.1934 | 122.9462 | 123.0515 | 59.3262 | 59.0744
512.8906 | 123.2117 | -59.642 | 63.4735 | -0.048828 | 0.0017155 | 0.062649 | 0.06715 | 0.00029473 | -0.0016663 | -0.0010618 | -0.029816 | 0.0018436 | 0.068753 | 0.06667 | -0.0058234 | 0.0058982 | 0.0011385 | -0.27924 | 63.4552 | -59.8251 | 63.2675 | -59.2575 | -59.7656 | -0.23804 | -0.54474 | 63.4277 | -59.7336 | 63.4232 | -59.6603 | -59.7885 | -59.5047 | -0.1831 | -0.018311 | -0.20599 | 0.38452 | 59.404 | -0.1236 | 59.5871 | 0.059509 | -0.091553 | -0.045777 | -0.050354 | -0.01831 | 0.13733 | -0.14648 | 0.22888 | -0.054931 | 0.56763 | 123.0927 | 0.073243 | 123.1567 | 123.2803 | 123.1613 | 123.0972 | 123.0698 | -123.2986 | -123.2071 | 122.9095 | 123.0652 | 59.3628 | 59.0973
513.8594 | 123.2849 | -59.61 | 63.4415 | -0.10223 | 0.0015019 | 0.062008 | 0.066723 | 0.00029473 | 0.0013245 | -0.0044796 | 0.0098572 | 0.00034819 | 0.067684 | 0.061543 | -0.0053962 | 0.0050436 | 0.0019931 | -0.22888 | 63.4644 | -59.8068 | 63.3911 | -59.4131 | -59.8068 | -0.009155 | -0.46234 | 63.3865 | -59.6603 | 63.4781 | -59.5963 | -59.7153 | -59.4543 | -0.19684 | 0.022888 | -0.050354 | 0.19684 | 59.6008 | -0.19684 | 59.7977 | 0 | -0.050354 | -0.054931 | 0.036621 | 0.013733 | 0.15564 | -0.10529 | 0.20599 | -0.054932 | 0.39368 | 123.1979 | 0.064087 | 123.1384 | 123.2712 | 123.0469 | 123.0743 | 122.9965 | -123.2483 | -123.1018 | 123.0011 | 123.0881 | 59.3811 | 59.1476
514.8906 | 123.2941 | -59.61 | 63.4232 | -0.01831 | 0.0027835 | 0.063076 | 0.066082 | 0.0028583 | -0.0023071 | -0.0012754 | 0.015961 | 0.00056179 | 0.068112 | 0.063038 | -0.0045416 | 0.006539 | 0.0019931 | -0.24261 | 63.4323 | -59.8251 | 63.4232 | -59.3903 | -59.7839 | 0 | -0.43945 | 63.4186 | -59.6649 | 63.5101 | -59.5505 | -59.6558 | -59.4177 | -0.21515 | 0.009155 | 0 | 0.21973 | 59.61 | -0.17395 | 59.8251 | 0.041198 | -0.054932 | -0.004578 | 0.086975 | 0.059509 | 0.19226 | -0.045777 | 0.24719 | 0.009155 | 0.43487 | 123.2483 | 0.11444 | 123.175 | 123.2574 | 123.0835 | 123.0423 | 123.0286 | -123.2483 | -123.0881 | 123.0331 | 123.1201 | 59.3674 | 59.1705
515.8594 | 123.2666 | -59.61 | 63.4277 | -0.010681 | 0.0027835 | 0.064999 | 0.066937 | -0.00013247 | -0.00038447 | -0.001489 | -0.0054016 | 0.00056179 | 0.068966 | 0.06432 | -0.0066778 | 0.0063254 | -0.00099766 | -0.23804 | 63.4369 | -59.7977 | 63.414 | -59.404 | -59.7839 | -0.004578 | -0.43488 | 63.4323 | -59.6558 | 63.5147 | -59.5551 | -59.6695 | -59.4223 | -0.18768 | 0.009156 | -0.013733 | 0.20599 | 59.6054 | -0.17395 | 59.7931 | 0.013732 | -0.045777 | 0.004578 | 0.086975 | 0.054931 | 0.18768 | -0.05951 | 0.23346 | -0.013733 | 0.39368 | 123.2117 | 0.10071 | 123.1705 | 123.2346 | 123.0881 | 123.0469 | 123.0423 | -123.2254 | -123.0835 | 123.024 | 123.1247 | 59.3719 | 59.1751
516.8906 | 123.3353 | -59.6054 | 63.4186 | -0.071716 | 0.00064726 | 0.061581 | 0.067791 | 0.0028583 | 0.0013245 | -0.00042077 | 0.00070198 | 0.00098899 | 0.067684 | 0.065174 | -0.0051824 | 0.0044028 | -0.0037747 | -0.25177 | 63.4232 | -59.7885 | 63.4827 | -59.317 | -60.0174 | -0.036621 | -0.44403 | 63.382 | -59.6695 | 63.5468 | -59.5001 | -59.6283 | -59.3903 | -0.18311 | 0.004578 | 0.064087 | 0.28839 | 59.5688 | -0.41199 | 59.7519 | -0.22888 | -0.064087 | -0.036621 | 0.12817 | 0.10529 | 0.21515 | -0.022888 | 0.27924 | 0.041199 | 0.4715 | 123.2712 | 0.16937 | 123.2162 | 123.2117 | 123.0515 | 123.0286 | 122.9874 | -123.2071 | -123.0881 | 123.0881 | 123.1522 | 59.3536 | 59.1614
517.8594 | 123.3124 | -59.6008 | 63.4186 | 0.1648 | 0.0034245 | 0.065426 | 0.068005 | -0.0018415 | -0.0016663 | 0.0017154 | 0.0068054 | 0.0037662 | 0.066403 | 0.068165 | -0.0062506 | 0.0054708 | 7.0538e-05 | -0.52643 | 63.4369 | -59.8206 | 63.3957 | -59.3719 | -59.729 | 0 | -0.41657 | 63.4048 | -59.6466 | 63.5376 | -59.5184 | -59.6237 | -59.3765 | -0.21973 | 0.018311 | -0.022888 | 0.22888 | 59.6008 | -0.12817 | 59.8206 | 0.091553 | -0.045776 | -0.013733 | 0.11902 | 0.082397 | 0.2243 | -0.022888 | 0.27008 | 0.022888 | 0.44861 | 123.2162 | 0.12817 | 123.1842 | 123.2574 | 123.0515 | 123.0377 | 123.0057 | -123.2391 | -123.0652 | 122.9965 | 123.1384 | 59.0744 | 59.1843
518.8906 | 123.3398 | -59.6146 | 63.414 | -0.079346 | 0.0012881 | 0.06329 | 0.066509 | -0.0018415 | -0.0016663 | -0.0012754 | 0.13193 | 0.0041934 | 0.066616 | 0.06432 | -0.0049688 | 0.0035482 | -0.0033475 | -0.27466 | 63.4277 | -59.7885 | 63.4094 | -59.3948 | -59.7839 | -0.032043 | -0.27466 | 63.446 | -59.6466 | 63.5696 | -59.5505 | -59.642 | -59.3765 | -0.17395 | 0.013733 | -0.004577 | 0.21973 | 59.5825 | -0.16937 | 59.7565 | 0.004577 | -0.032043 | 0.032044 | 0.15564 | 0.064087 | 0.23804 | -0.027466 | 0.27008 | 0.004577 | 0.39368 | 123.1979 | 0.09613 | 123.2162 | 123.2162 | 123.0927 | 123.0423 | 123.0606 | -123.2025 | -123.0606 | 123.024 | 123.1842 | 59.3399 | 59.3399
519.8594 | 123.2529 | -59.5688 | 63.4689 | -0.041199 | 0.00064726 | 0.063931 | 0.066937 | 0.00029473 | -0.0018799 | 0.00043363 | -0.011505 | 0.00056179 | 0.069821 | 0.068379 | -0.0049688 | 0.00483 | -0.0024931 | -0.22888 | 63.4689 | -59.8068 | 63.414 | -59.3994 | -59.7931 | 0 | -0.44403 | 63.4277 | -59.6512 | 63.4872 | -59.5734 | -59.6924 | -59.4177 | -0.23804 | 0 | -0.054932 | 0.16937 | 59.5688 | -0.2243 | 59.8068 | 0.013733 | -0.082397 | -0.041199 | 0.018311 | -0.004577 | 0.15106 | -0.1236 | 0.23346 | -0.041199 | 0.40741 | 123.2208 | 0.07782 | 123.1384 | 123.2758 | 123.0789 | 123.0377 | 122.9965 | -123.2758 | -123.1201 | 122.9828 | 123.056 | 59.3399 | 59.1248
520.8906 | 123.3078 | -59.5963 | 63.4277 | 0.050354 | 0.0029971 | 0.06329 | 0.067577 | 8.1126e-05 | -0.0035889 | 0.0015018 | 0.0068054 | 0.00034819 | 0.069607 | 0.070942 | -0.0058234 | 0.00483 | -0.0018521 | -0.36163 | 63.414 | -59.7748 | 63.4369 | -59.3628 | -59.7473 | 0.018311 | -0.41657 | 63.4094 | -59.6649 | 63.5559 | -59.4955 | -59.6191 | -59.3857 | -0.17853 | -0.013733 | 0.009156 | 0.23346 | 59.6146 | -0.15106 | 59.7931 | 0.027466 | -0.068665 | -0.01831 | 0.12817 | 0.10071 | 0.21057 | -0.022889 | 0.27924 | 0.045776 | 0.41199 | 123.2117 | 0.16937 | 123.2208 | 123.1888 | 123.0743 | 123.0103 | 123.0057 | -123.2025 | -123.0927 | 123.0331 | 123.1522 | 59.2346 | 59.1797
521.8594 | 123.2666 | -59.6008 | 63.4506 | -0.041199 | 0.00086086 | 0.063504 | 0.066723 | 0.0026447 | -0.0014527 | -0.0021298 | -0.014557 | 0.002698 | 0.069393 | 0.062611 | -0.0068914 | 0.0073936 | -0.0059109 | -0.23804 | 63.4277 | -59.8068 | 63.4552 | -59.3811 | -59.7656 | 0 | -0.4303 | 63.4323 | -59.6329 | 63.5239 | -59.5276 | -59.6466 | -59.3948 | -0.20599 | -0.022889 | 0.004577 | 0.21973 | 59.6008 | -0.16479 | 59.8068 | 0.041199 | -0.032044 | -0.018311 | 0.073242 | 0.073242 | 0.20599 | -0.045776 | 0.23804 | -0.013732 | 0.42572 | 123.262 | 0.10529 | 123.1567 | 123.2346 | 123.0652 | 123.0286 | 123.0331 | -123.2574 | -123.0835 | 123.056 | 123.1247 | 59.3628 | 59.1705
522.9062 | 123.3078 | -59.5825 | 63.3728 | -0.086975 | 0.0032107 | 0.064572 | 0.067791 | -0.00034607 | -0.0010255 | 0.0010746 | -0.087799 | -7.901e-05 | 0.067898 | 0.06667 | -0.0068914 | 0.006539 | -0.0020657 | -0.3479 | 63.4003 | -59.8526 | 63.3728 | -59.4864 | -59.8892 | -0.33875 | -0.39368 | 63.3865 | -59.6786 | 63.533 | -59.5551 | -59.6924 | -59.3857 | -0.27008 | 0.027466 | 0 | 0.096131 | 59.2438 | -0.3067 | 59.5139 | -0.036621 | -0.09613 | 0.013733 | 0.16022 | 0.027466 | 0.19684 | -0.10986 | 0.29297 | -0.013733 | 0.36621 | 123.2254 | 0.1236 | 123.2117 | 123.2529 | 123.0652 | 122.9828 | 122.9691 | -123.2254 | -123.0515 | 122.9553 | 123.1155 | 59.2346 | 59.1888
523.8594 | 123.3582 | -59.5734 | 63.4186 | -0.048828 | 0.0023563 | 0.062008 | 0.066296 | -0.0046185 | -0.0035889 | 0.0025698 | -0.0084534 | 0.0022708 | 0.065548 | 0.067311 | -0.0062506 | 0.0061118 | 0.0011385 | -0.28381 | 63.4598 | -59.7839 | 63.1622 | -59.5779 | -59.5779 | -0.045776 | -0.41199 | 63.4186 | -59.642 | 63.5971 | -59.4727 | -59.5871 | -59.3491 | -0.21057 | 0.041199 | -0.25635 | -0.004578 | 59.5276 | -0.004578 | 59.7382 | 0.20599 | -0.068665 | 0 | 0.17853 | 0.10071 | 0.2243 | -0.013733 | 0.29297 | 0.054932 | 0.20599 | 122.9462 | 0.16937 | 123.2391 | 123.2437 | 123.0606 | 123.0331 | 122.9919 | -123.2025 | -123.0606 | 122.7356 | 123.1705 | 59.2896 | 59.1614
524.8906 | 123.2483 | -59.5596 | 63.4735 | -0.041199 | 0.0036381 | 0.063717 | 0.065228 | -0.00055967 | -0.0016663 | -0.0019162 | -0.014557 | 0.0018436 | 0.067257 | 0.060475 | -0.006037 | 0.0063254 | -0.0012113 | -0.24261 | 63.4689 | -59.7839 | 63.4415 | -59.3628 | -59.7565 | 0.009155 | -0.4303 | 63.4415 | -59.642 | 63.5513 | -59.5184 | -59.6375 | -59.3719 | -0.2243 | -0.004578 | -0.032044 | 0.19684 | 59.5688 | -0.19684 | 59.7931 | 0.027466 | -0.082398 | -0.032044 | 0.07782 | 0.041198 | 0.18768 | -0.07782 | 0.27008 | 0.004578 | 0.42114 | 123.2254 | 0.1236 | 123.1934 | 123.2529 | 123.0835 | 123.0286 | 123.0011 | -123.2574 | -123.1155 | 123.0011 | 123.111 | 59.317 | 59.1293
525.8594 | 123.2666 | -59.5871 | 63.4552 | -0.048828 | 0.0015019 | 0.062222 | 0.066937 | 0.00093573 | -0.0012391 | -0.0010618 | -0.02066 | 0.0029116 | 0.06683 | 0.064106 | -0.0064642 | 0.0061118 | -0.0022793 | -0.23346 | 63.4598 | -59.7656 | 63.4369 | -59.3582 | -59.7794 | 0 | -0.42572 | 63.4552 | -59.6466 | 63.5239 | -59.5001 | -59.642 | -59.404 | -0.17853 | 0.004578 | -0.01831 | 0.22888 | 59.5871 | -0.19226 | 59.7656 | -0.013733 | -0.059509 | 0 | 0.068665 | 0.086975 | 0.1831 | -0.054932 | 0.24261 | 0.004577 | 0.40741 | 123.2025 | 0.14648 | 123.1705 | 123.2254 | 123.1018 | 123.0469 | 123.0423 | -123.2208 | -123.1018 | 123.024 | 123.111 | 59.3536 | 59.1614
526.9062 | 123.2025 | -59.642 | 63.4644 | -0.056457 | 0.0010745 | 0.062008 | 0.068432 | 0.0043537 | -0.0018799 | -0.0010618 | -0.11526 | 0.0018436 | 0.065975 | 0.070301 | -0.0056098 | 0.0063254 | -0.00014306 | -0.35248 | 63.4781 | -59.8526 | 63.2858 | -59.5688 | -59.9533 | -0.19684 | -0.68207 | 63.4506 | -59.697 | 63.4415 | -59.6924 | -59.8206 | -59.5139 | -0.21057 | 0.013733 | -0.17853 | 0.073242 | 59.4452 | -0.31128 | 59.6558 | -0.10071 | -0.054931 | -0.013732 | -0.022888 | -0.050354 | 0.12817 | -0.17853 | 0.1831 | -0.1236 | 0.28381 | 123.1384 | 0.004577 | 123.1384 | 123.3307 | 123.1476 | 123.1201 | 123.0927 | -123.317 | -123.1613 | 122.9279 | 123.0835 | 59.2896 | 58.96
527.875 | 123.1979 | -59.6329 | 63.4323 | -0.10986 | 0.00064726 | 0.06329 | 0.069714 | 0.0039263 | -0.0023071 | -0.00084817 | -0.096954 | 0.0024844 | 0.068966 | 0.065388 | -0.0047552 | 0.0067526 | -0.00057046 | -0.37079 | 63.4872 | -59.8389 | 63.2812 | -59.5596 | -59.9487 | -0.23804 | -0.69122 | 63.4415 | -59.7015 | 63.4415 | -59.6786 | -59.8251 | -59.4955 | -0.20599 | 0.054932 | -0.15106 | 0.073243 | 59.3948 | -0.31586 | 59.6008 | -0.10986 | -0.068664 | 0.009155 | 0.009155 | -0.045776 | 0.13733 | -0.19226 | 0.20599 | -0.1236 | 0.27924 | 123.1201 | 0.022888 | 123.143 | 123.3261 | 123.143 | 123.1201 | 123.0743 | -123.2712 | -123.1338 | 122.9141 | 123.0743 | 59.2621 | 58.9417
528.9062 | 123.1888 | -59.6146 | 63.4506 | -0.14038 | -0.0010617 | 0.064145 | 0.068005 | 0.0013629 | -0.00059807 | -0.00063437 | -0.10916 | 0.00163 | 0.068112 | 0.065602 | -0.0045416 | 0.0069662 | -0.0027067 | -0.17853 | 63.5056 | -59.8389 | 63.3316 | -59.5734 | -59.9716 | -0.19684 | -0.68207 | 63.446 | -59.7153 | 63.4277 | -59.6741 | -59.8114 | -59.4955 | -0.2243 | 0.054931 | -0.11902 | 0.041199 | 59.4177 | -0.35706 | 59.642 | -0.13275 | -0.10071 | -0.004578 | -0.022889 | -0.059509 | 0.11902 | -0.19684 | 0.21973 | -0.09613 | 0.2655 | 123.1705 | 0.041199 | 123.143 | 123.3444 | 123.1613 | 123.1201 | 123.0606 | -123.2895 | -123.1659 | 122.9462 | 123.0423 | 59.436 | 58.9325
529.8594 | 123.2986 | -59.5871 | 63.4415 | -0.071716 | 0.0012881 | 0.06094 | 0.065868 | 0.00072213 | -0.00059807 | -0.0034116 | 0.025116 | 0.0014164 | 0.066616 | 0.063679 | -0.0051824 | 0.0046164 | 0.00028414 | -0.2655 | 63.4872 | -59.7519 | 63.4506 | -59.3353 | -59.7336 | -0.009155 | -0.41199 | 63.4277 | -59.6237 | 63.5788 | -59.4772 | -59.6008 | -59.3628 | -0.16479 | 0.045777 | 0.009156 | 0.25177 | 59.5779 | -0.14648 | 59.7427 | 0.01831 | -0.036621 | -0.013733 | 0.13733 | 0.10986 | 0.2243 | -0.013733 | 0.26092 | 0.022888 | 0.41656 | 123.2025 | 0.14648 | 123.2025 | 123.2391 | 123.0515 | 123.0743 | 123.0148 | -123.1934 | -123.0652 | 123.0377 | 123.1659 | 59.3216 | 59.1751
530.9062 | 123.2071 | -59.5917 | 63.4735 | 0.012207 | 0.00022006 | 0.063504 | 0.070568 | 8.1126e-05 | 0.00025633 | -0.0019162 | -0.078644 | 0.002698 | 0.068753 | 0.068379 | -0.0064642 | 0.0069662 | -0.00099766 | -0.28381 | 63.4918 | -59.8114 | 63.3636 | -59.4452 | -59.8297 | -0.09613 | -0.50354 | 63.4415 | -59.6512 | 63.5056 | -59.5688 | -59.7336 | -59.4406 | -0.21973 | 0.01831 | -0.10986 | 0.14649 | 59.4955 | -0.23804 | 59.7153 | -0.018311 | -0.059509 | -0.032044 | 0.032043 | 0.022888 | 0.15106 | -0.14191 | 0.21057 | -0.082398 | 0.36621 | 123.175 | 0.082397 | 123.1567 | 123.3032 | 123.0927 | 123.0835 | 123.0331 | -123.2849 | -123.1247 | 122.9553 | 123.0972 | 59.3079 | 59.0881
531.8594 | 123.1796 | -59.5825 | 63.4918 | -0.086975 | 6.46e-06 | 0.061581 | 0.064373 | 0.00093573 | 0.00046993 | -0.0046934 | 0.034271 | 0.0056888 | 0.067898 | 0.063252 | -0.0049688 | 0.0058982 | 0.0037021 | -0.28839 | 63.5284 | -59.7702 | 63.3865 | -59.4406 | -59.7794 | 0.10986 | -0.70953 | 63.4644 | -59.6741 | 63.4598 | -59.5917 | -59.7382 | -59.4772 | -0.18768 | 0.036621 | -0.10529 | 0.14191 | 59.6924 | -0.19684 | 59.8801 | -0.009155 | -0.091552 | -0.027466 | -0.032043 | -0.009155 | 0.10529 | -0.15564 | 0.19684 | -0.064087 | 0.32959 | 123.1567 | 0.082397 | 123.1338 | 123.2986 | 123.1384 | 123.111 | 123.0469 | -123.262 | -123.1659 | 122.9691 | 123.0423 | 59.2941 | 58.873
532.9062 | 123.1979 | -59.6054 | 63.4598 | -0.071716 | 0.0015019 | 0.063931 | 0.068005 | 0.00029473 | -0.0016663 | -0.00084817 | -0.093903 | 0.0031254 | 0.068112 | 0.065388 | -0.0058234 | 0.0073936 | 0.00049774 | -0.32501 | 63.5101 | -59.8068 | 63.3591 | -59.4681 | -59.8801 | -0.15106 | -0.57678 | 63.4552 | -59.6786 | 63.4781 | -59.6191 | -59.7473 | -59.4681 | -0.20142 | 0.050354 | -0.10071 | 0.13733 | 59.4543 | -0.27466 | 59.6558 | -0.073242 | -0.073242 | -0.004578 | 0.01831 | -0.013733 | 0.13733 | -0.14191 | 0.21057 | -0.068664 | 0.33874 | 123.1659 | 0.059509 | 123.1567 | 123.317 | 123.1338 | 123.1155 | 123.0606 | -123.2666 | -123.1384 | 122.9645 | 123.0835 | 59.2804 | 59.0286
533.8594 | 123.2758 | -59.5551 | 63.4781 | -0.041199 | 0.0029971 | 0.062222 | 0.066296 | 0.00093573 | -0.00038447 | -0.00020717 | 0.028168 | 0.0029116 | 0.068112 | 0.068592 | -0.0062506 | 0.0061118 | 0.0026339 | -0.24719 | 63.5147 | -59.7473 | 63.4644 | -59.3445 | -59.729 | 0.009155 | -0.4303 | 63.4323 | -59.642 | 63.5559 | -59.4818 | -59.6191 | -59.3719 | -0.19226 | 0.036621 | -0.013733 | 0.21057 | 59.5642 | -0.17395 | 59.7565 | 0.01831 | -0.086975 | -0.045776 | 0.07782 | 0.073242 | 0.18311 | -0.064087 | 0.27008 | 0.022888 | 0.40283 | 123.2117 | 0.16022 | 123.1979 | 123.262 | 123.0743 | 123.0698 | 122.9874 | -123.2254 | -123.1201 | 123.0194 | 123.111 | 59.3079 | 59.1248
534.8906 | 123.1979 | -59.5963 | 63.4735 | -0.10223 | 0.0023563 | 0.064572 | 0.067577 | 0.0024311 | -0.0029481 | 0.0012882 | -0.084747 | 0.0020572 | 0.068325 | 0.063679 | -0.0073188 | 0.0067526 | -0.0014249 | -0.30212 | 63.533 | -59.8114 | 63.3865 | -59.4315 | -59.8343 | -0.11902 | -0.54932 | 63.4918 | -59.6603 | 63.4964 | -59.5825 | -59.7336 | -59.4406 | -0.21515 | 0.059509 | -0.086975 | 0.16479 | 59.4772 | -0.23804 | 59.6924 | -0.022889 | -0.064087 | 0.01831 | 0.022888 | 0.013732 | 0.15564 | -0.13733 | 0.21973 | -0.073243 | 0.37994 | 123.1979 | 0.077819 | 123.1567 | 123.3444 | 123.1522 | 123.1293 | 123.0881 | -123.2849 | -123.1338 | 122.9828 | 123.0927 | 59.2941 | 59.0469
535.8594 | 123.2803 | -59.5459 | 63.4918 | -0.071716 | 0.0023563 | 0.064145 | 0.06715 | 0.00072213 | -0.0029481 | 0.00064723 | 0.00070198 | 0.0018436 | 0.066616 | 0.061543 | -0.0053962 | 0.0056846 | -0.0012113 | -0.24261 | 63.501 | -59.7244 | 63.4598 | -59.3353 | -59.7244 | -0.004578 | -0.4303 | 63.4506 | -59.6191 | 63.5559 | -59.4681 | -59.6008 | -59.3582 | -0.17853 | 0.009156 | -0.032043 | 0.21057 | 59.5413 | -0.17853 | 59.7198 | 0 | -0.073243 | -0.041198 | 0.064087 | 0.077819 | 0.18768 | -0.054932 | 0.26093 | 0.018311 | 0.3891 | 123.1842 | 0.15106 | 123.175 | 123.2254 | 123.0698 | 123.0469 | 122.9965 | -123.2162 | -123.111 | 123.0057 | 123.1018 | 59.3033 | 59.1156
536.8906 | 123.143 | -59.5825 | 63.4964 | -0.02594 | 0.00064726 | 0.061367 | 0.065868 | -0.0012005 | -0.0014527 | -0.00063437 | -0.032867 | 0.002698 | 0.06918 | 0.068592 | -0.0051824 | 0.0067526 | -0.00014306 | -0.30212 | 63.5284 | -59.8022 | 63.3591 | -59.4681 | -59.8297 | -0.091553 | -0.58594 | 63.5193 | -59.6375 | 63.4781 | -59.5917 | -59.7244 | -59.4498 | -0.21973 | 0.032043 | -0.13733 | 0.11444 | 59.491 | -0.24719 | 59.7107 | -0.027466 | -0.054931 | 0.022888 | -0.018311 | -0.009155 | 0.13275 | -0.14191 | 0.18768 | -0.086975 | 0.33417 | 123.1613 | 0.045776 | 123.1155 | 123.3307 | 123.1567 | 123.111 | 123.1018 | -123.2986 | -123.1338 | 122.9416 | 123.0606 | 59.2804 | 58.9966
537.875 | 123.1796 | -59.5917 | 63.4781 | -0.056457 | 0.0025699 | 0.061367 | 0.068005 | -0.0020551 | 0.0013245 | -0.0019162 | -0.07254 | 0.0046206 | 0.068539 | 0.07201 | -0.0064642 | 0.0046164 | 7.0538e-05 | -0.35706 | 63.5101 | -59.848 | 63.1897 | -59.4818 | -59.7427 | -0.19684 | -0.6958 | 63.4598 | -59.6832 | 63.4552 | -59.6558 | -59.8068 | -59.4818 | -0.25635 | 0.032044 | -0.28839 | 0.10986 | 59.3948 | -0.15106 | 59.6512 | 0.10529 | -0.091553 | -0.01831 | -0.022888 | -0.064087 | 0.10986 | -0.21515 | 0.20142 | -0.1236 | 0.36621 | 123.0377 | 0.027466 | 123.1384 | 123.3582 | 123.143 | 123.1018 | 123.0515 | -123.3261 | -123.1613 | 122.7814 | 123.0469 | 59.2346 | 58.8959
538.8906 | 123.2986 | -59.5642 | 63.4964 | -0.064087 | 0.0032107 | 0.060513 | 0.066082 | -0.0024823 | -0.0010255 | -0.00042077 | 0.037323 | 0.00098899 | 0.06683 | 0.065174 | -0.0051824 | 0.0073936 | -0.00099766 | -0.25635 | 63.4872 | -59.7427 | 63.4735 | -59.3216 | -59.7198 | 0.013733 | -0.42114 | 63.4552 | -59.61 | 63.5742 | -59.4543 | -59.5734 | -59.3399 | -0.17853 | -0.009155 | -0.022888 | 0.24262 | 59.5779 | -0.15564 | 59.7565 | 0.022888 | -0.045776 | -0.041199 | 0.07782 | 0.10986 | 0.2243 | -0.009155 | 0.27008 | 0.036621 | 0.42114 | 123.2162 | 0.15564 | 123.1842 | 123.23 | 123.0652 | 123.0515 | 123.0194 | -123.2391 | -123.1064 | 123.0377 | 123.1384 | 59.3079 | 59.1431
539.8594 | 123.2025 | -59.5505 | 63.5101 | -0.033569 | 0.0032107 | 0.063717 | 0.065228 | -0.00034607 | -0.0027345 | -0.001489 | 0.0098572 | 0.0014164 | 0.06918 | 0.061756 | -0.0062506 | 0.003121 | 0.0039157 | -0.25177 | 63.5239 | -59.7382 | 63.4094 | -59.3811 | -59.7702 | -0.054932 | -0.48981 | 63.4872 | -59.6237 | 63.4277 | -59.6466 | -59.6558 | -59.404 | -0.18768 | 0.013733 | -0.10071 | 0.16937 | 59.4955 | -0.21973 | 59.6832 | -0.032044 | -0.073242 | -0.022888 | -0.082398 | -0.09613 | 0.14648 | -0.10529 | 0.21973 | -0.032044 | 0.35706 | 123.1476 | -0.022888 | 123.0515 | 123.262 | 123.111 | 123.0743 | 123.0377 | -123.2483 | -123.1338 | 122.9599 | 122.9782 | 59.2987 | 59.0607
540.9062 | 123.1979 | -59.5734 | 63.4964 | -0.079346 | 0.0029971 | 0.06329 | 0.068432 | 0.00029473 | -0.00059807 | -0.00084817 | -0.069489 | 0.0031254 | 0.067471 | 0.065174 | -0.0053962 | 0.0054708 | 0.00071134 | -0.30212 | 63.5193 | -59.7794 | 63.382 | -59.4498 | -59.8434 | -0.15106 | -0.5722 | 63.4781 | -59.6466 | 63.4872 | -59.5917 | -59.7473 | -59.436 | -0.20599 | 0.022888 | -0.11444 | 0.1236 | 59.4223 | -0.27008 | 59.6283 | -0.064087 | -0.073242 | -0.018311 | -0.009155 | -0.018311 | 0.13733 | -0.17395 | 0.21057 | -0.10071 | 0.32959 | 123.1613 | 0.054931 | 123.1338 | 123.2986 | 123.1247 | 123.0927 | 123.0515 | -123.2758 | -123.143 | 122.9553 | 123.0606 | 59.2712 | 59.0012
541.8594 | 123.1888 | -59.5642 | 63.5056 | -0.048828 | 0.0036381 | 0.062649 | 0.066082 | 0.00093573 | -0.0010255 | 0.00022003 | -0.014557 | 0.00034819 | 0.067471 | 0.065388 | -0.0032598 | 0.0063254 | 0.00092494 | -0.25635 | 63.5376 | -59.729 | 63.4048 | -59.404 | -59.7839 | -0.050354 | -0.5722 | 63.5284 | -59.5779 | 63.4964 | -59.5871 | -59.642 | -59.3994 | -0.1648 | 0.032044 | -0.10071 | 0.16022 | 59.5139 | -0.21973 | 59.6787 | -0.054932 | -0.013733 | 0.022888 | -0.009155 | -0.022888 | 0.16479 | -0.07782 | 0.17853 | -0.064087 | 0.32501 | 123.1338 | -0.009155 | 123.0743 | 123.2666 | 123.1064 | 123.1018 | 123.0927 | -123.2346 | -123.0835 | 122.9691 | 123.0606 | 59.3079 | 58.992
542.9062 | 123.3032 | -59.5505 | 63.4369 | -0.14038 | 0.0027835 | 0.063931 | 0.065655 | -0.00077327 | 0.0023925 | -0.00084817 | -0.017609 | 0.0024844 | 0.068753 | 0.063465 | -0.0068914 | 0.0058982 | 7.0538e-05 | -0.3067 | 63.4735 | -59.7702 | 63.446 | -59.3536 | -59.7794 | -0.11902 | -0.55389 | 63.4186 | -59.6283 | 63.5742 | -59.5047 | -59.6329 | -59.3491 | -0.21973 | 0.036621 | 0.009155 | 0.19684 | 59.4315 | -0.22888 | 59.6512 | -0.009155 | -0.07782 | -0.018311 | 0.13733 | 0.045776 | 0.20142 | -0.082398 | 0.27924 | -0.004578 | 0.41657 | 123.2162 | 0.1236 | 123.2025 | 123.2437 | 123.0469 | 123.024 | 122.9691 | -123.2071 | -123.0652 | 122.9965 | 123.1247 | 59.2438 | 58.9966
543.8594 | 123.1934 | -59.5551 | 63.5239 | -0.033569 | 0.0023563 | 0.062649 | 0.067364 | 0.00093573 | -0.00059807 | -0.0023434 | -0.093903 | 0.00013459 | 0.070248 | 0.069233 | -0.0062506 | 0.0063254 | -0.00035666 | -0.26093 | 63.5239 | -59.7382 | 63.4048 | -59.3994 | -59.8068 | -0.054932 | -0.45776 | 63.5696 | -59.6146 | 63.4872 | -59.5734 | -59.7107 | -59.4681 | -0.18311 | 0 | -0.11902 | 0.15564 | 59.5001 | -0.25177 | 59.6832 | -0.068665 | -0.059509 | 0.045776 | -0.036621 | -0.01831 | 0.086975 | -0.15564 | 0.14648 | -0.09613 | 0.33875 | 123.143 | 0.041199 | 123.1018 | 123.262 | 123.1842 | 123.0789 | 123.1247 | -123.262 | -123.1384 | 122.9599 | 123.0423 | 59.2941 | 59.0973
544.8906 | 123.2391 | -59.5505 | 63.5056 | -0.041199 | 0.0025699 | 0.064358 | 0.069927 | 0.00072213 | -0.0010255 | -0.0040524 | -0.069489 | 0.002698 | 0.068753 | 0.06197 | -0.0064642 | 0.0088888 | -0.0037747 | -0.27466 | 63.5651 | -59.7656 | 63.4232 | -59.4086 | -59.7748 | -0.073242 | -0.40741 | 63.4872 | -59.6008 | 63.5605 | -59.491 | -59.6603 | -59.3765 | -0.21515 | 0.059509 | -0.082397 | 0.14191 | 59.4772 | -0.2243 | 59.6924 | -0.009155 | -0.050354 | -0.01831 | 0.054932 | 0.059509 | 0.17395 | -0.10986 | 0.2243 | -0.059509 | 0.35706 | 123.1888 | 0.10986 | 123.1613 | 123.3307 | 123.0881 | 123.1155 | 123.0377 | -123.2712 | -123.1064 | 122.9736 | 123.111 | 59.2758 | 59.1431
545.8594 | 123.1842 | -59.5459 | 63.5422 | -0.079346 | 0.00064726 | 0.061795 | 0.06715 | -0.0018415 | -0.0010255 | 0.00043363 | -0.084747 | 0.00163 | 0.067684 | 0.061756 | -0.0036872 | 0.0054708 | 0.00028414 | -0.26093 | 63.5513 | -59.7519 | 63.4003 | -59.436 | -59.6512 | 0.19684 | -0.59509 | 63.5147 | -59.6329 | 63.4827 | -59.5413 | -59.7015 | -59.4452 | -0.20599 | 0.009156 | -0.14191 | 0.10986 | 59.7427 | -0.10529 | 59.9487 | 0.10071 | -0.086976 | -0.027466 | -0.059509 | 0.004577 | 0.10071 | -0.15564 | 0.18768 | -0.068664 | 0.31586 | 123.1522 | 0.091553 | 123.1155 | 123.3032 | 123.1476 | 123.0972 | 123.0606 | -123.2941 | -123.175 | 122.9462 | 123.0286 | 59.285 | 58.9508
546.8906 | 123.23 | -59.5413 | 63.5376 | -0.071716 | 0.0017155 | 0.064145 | 0.068218 | 0.0047809 | -0.00038447 | -0.0010618 | -0.060333 | 0.0031254 | 0.067898 | 0.070301 | -0.0045416 | 0.0058982 | -0.0012113 | -0.28381 | 63.5284 | -59.7885 | 63.4232 | -59.3994 | -59.7885 | -0.086975 | -0.52643 | 63.501 | -59.6237 | 63.5239 | -59.5276 | -59.6786 | -59.404 | -0.24719 | -0.009156 | -0.11444 | 0.14191 | 59.4543 | -0.24719 | 59.7015 | 0 | -0.082397 | -0.036621 | -0.013733 | 0.013733 | 0.13733 | -0.13733 | 0.21973 | -0.054932 | 0.3891 | 123.2117 | 0.09613 | 123.1476 | 123.317 | 123.1247 | 123.0698 | 123.0423 | -123.3261 | -123.1613 | 122.9645 | 123.0652 | 59.2575 | 59.0149
547.8594 | 123.1796 | -59.5367 | 63.533 | -0.086975 | 0.0019291 | 0.062436 | 0.067577 | 0.0017901 | -0.0018799 | -0.0010618 | -0.032867 | 0.003339 | 0.069607 | 0.058766 | -0.0049688 | 0.0058982 | -0.0024931 | -0.31586 | 63.5651 | -59.7519 | 63.382 | -59.4498 | -59.8114 | -0.086975 | -0.54932 | 63.5422 | -59.6191 | 63.5147 | -59.5505 | -59.6878 | -59.4223 | -0.21515 | 0.032043 | -0.15106 | 0.086975 | 59.4498 | -0.27466 | 59.6649 | -0.059509 | -0.082398 | 0.009155 | -0.018311 | -0.013733 | 0.11444 | -0.15106 | 0.19684 | -0.068664 | 0.30212 | 123.1338 | 0.068665 | 123.1338 | 123.317 | 123.1613 | 123.1018 | 123.0789 | -123.2849 | -123.1522 | 122.9187 | 123.0515 | 59.2209 | 58.9874
548.8906 | 123.2254 | -59.5413 | 63.5422 | -0.041199 | 0.0015019 | 0.065213 | 0.068646 | 0.00093573 | -0.0042297 | -0.0010618 | -0.02066 | 0.0018436 | 0.067471 | 0.066242 | -0.0053962 | 0.006539 | -0.00078406 | -0.29297 | 63.5696 | -59.761 | 63.3957 | -59.4498 | -59.8114 | -0.10071 | -0.58136 | 63.5422 | -59.6191 | 63.5239 | -59.5551 | -59.6695 | -59.404 | -0.21973 | 0.027466 | -0.14648 | 0.091553 | 59.4406 | -0.27008 | 59.6603 | -0.050354 | -0.07782 | 0 | -0.01831 | -0.013733 | 0.13733 | -0.12817 | 0.21515 | -0.050354 | 0.31128 | 123.1567 | 0.064087 | 123.143 | 123.3307 | 123.1613 | 123.111 | 123.0835 | -123.3032 | -123.1613 | 122.937 | 123.0652 | 59.2484 | 58.96
549.8594 | 123.2071 | -59.5322 | 63.5422 | -0.010681 | 0.00086086 | 0.062008 | 0.066509 | -0.0048321 | -0.0044433 | -0.00084817 | -0.023712 | 0.0022708 | 0.070248 | 0.062184 | -0.0049688 | 0.0067526 | 0.00071134 | -0.31586 | 63.5651 | -59.7519 | 63.3682 | -59.4498 | -59.816 | -0.086975 | -0.54474 | 63.5468 | -59.61 | 63.5101 | -59.5596 | -59.6878 | -59.4131 | -0.21973 | 0.022888 | -0.17395 | 0.082398 | 59.4452 | -0.28381 | 59.6649 | -0.064087 | -0.077819 | 0.004578 | -0.032043 | -0.027465 | 0.11902 | -0.15564 | 0.19684 | -0.07782 | 0.30212 | 123.1201 | 0.050354 | 123.1201 | 123.317 | 123.1567 | 123.0972 | 123.0789 | -123.2941 | -123.1522 | 122.9004 | 123.0423 | 59.2163 | 58.9874
550.8906 | 123.23 | -59.523 | 63.5101 | -0.10986 | 0.0025699 | 0.061154 | 0.068859 | 0.0043537 | -0.0042297 | -0.0021298 | -0.042023 | 0.0048344 | 0.067471 | 0.06667 | -0.0064642 | 0.0063254 | -0.0016385 | -0.28381 | 63.5239 | -59.7565 | 63.4186 | -59.3811 | -59.7748 | -0.082397 | -0.51727 | 63.5147 | -59.6191 | 63.5422 | -59.5184 | -59.6741 | -59.3903 | -0.23346 | 0.013733 | -0.091553 | 0.14191 | 59.4406 | -0.25177 | 59.6741 | -0.01831 | -0.096131 | 0.004577 | 0.032043 | 0.004577 | 0.13275 | -0.15106 | 0.22888 | -0.054931 | 0.37537 | 123.175 | 0.10071 | 123.1613 | 123.2803 | 123.1338 | 123.0469 | 123.0377 | -123.2666 | -123.1293 | 122.9416 | 123.0652 | 59.2392 | 59.0057
551.8594 | 123.2117 | -59.5551 | 63.5376 | -0.01831 | 0.0021427 | 0.06329 | 0.068005 | 0.00050853 | -0.00017087 | -0.00042077 | -0.038971 | 0.0035526 | 0.06918 | 0.064533 | -0.0062506 | 0.0050436 | -0.00057046 | -0.28839 | 63.588 | -59.7427 | 63.3865 | -59.4315 | -59.7885 | -0.082397 | -0.56763 | 63.5376 | -59.5963 | 63.5422 | -59.5184 | -59.6512 | -59.3857 | -0.18768 | 0.050354 | -0.15106 | 0.1236 | 59.4727 | -0.23346 | 59.6603 | -0.045776 | -0.041198 | 0 | 0.004577 | 0.036621 | 0.16937 | -0.09613 | 0.21057 | -0.054932 | 0.31128 | 123.1293 | 0.077819 | 123.1384 | 123.3307 | 123.1338 | 123.143 | 123.0927 | -123.2803 | -123.1338 | 122.9416 | 123.0972 | 59.2667 | 58.9874
552.8906 | 123.2254 | -59.5322 | 63.5422 | -0.10986 | 0.0038517 | 0.061581 | 0.068005 | 0.0020037 | -0.00081187 | -0.0012754 | 0.022064 | 0.0048344 | 0.06683 | 0.062824 | -0.0034736 | 0.0058982 | -0.0022793 | -0.24719 | 63.5422 | -59.7336 | 63.4506 | -59.3308 | -59.7244 | -0.009155 | -0.4715 | 63.5147 | -59.6008 | 63.5468 | -59.5047 | -59.6375 | -59.3765 | -0.20142 | 0 | -0.091552 | 0.20142 | 59.523 | -0.19226 | 59.7244 | 0.009156 | -0.068664 | -0.027466 | 0.004578 | 0.027466 | 0.15564 | -0.10529 | 0.2243 | -0.036621 | 0.40283 | 123.1842 | 0.09613 | 123.1476 | 123.2758 | 123.1155 | 123.0743 | 123.0469 | -123.2758 | -123.143 | 122.9828 | 123.0789 | 59.285 | 59.0607
553.8594 | 123.2391 | -59.5459 | 63.5559 | -0.048828 | 0.00064726 | 0.064145 | 0.068218 | 0.0015765 | -0.00059807 | -0.0010618 | -0.042023 | 0.0048344 | 0.068753 | 0.063038 | -0.0049688 | 0.006539 | -0.00014306 | -0.29297 | 63.5742 | -59.7427 | 63.3728 | -59.4269 | -59.8022 | -0.09613 | -0.55847 | 63.5559 | -59.6054 | 63.5284 | -59.5276 | -59.6603 | -59.3948 | -0.19684 | 0.018311 | -0.18311 | 0.11902 | 59.4498 | -0.25635 | 59.6466 | -0.059509 | -0.05951 | 0 | -0.027466 | 0.01831 | 0.15106 | -0.11444 | 0.21057 | -0.054931 | 0.31586 | 123.1155 | 0.07782 | 123.1338 | 123.317 | 123.1613 | 123.1201 | 123.1018 | -123.2986 | -123.1613 | 122.9187 | 123.0743 | 59.2529 | 58.9874
554.8906 | 123.1705 | -59.5459 | 63.5101 | -0.064087 | 0.0027835 | 0.062436 | 0.066723 | -0.00013247 | -0.0012391 | -0.0010618 | -0.035919 | 0.0029116 | 0.068325 | 0.066242 | -0.006037 | 0.0076072 | 0.0015659 | -0.29297 | 63.5605 | -59.7382 | 63.414 | -59.3948 | -59.7656 | -0.068665 | -0.52643 | 63.5513 | -59.5825 | 63.5605 | -59.4955 | -59.6329 | -59.3124 | -0.19226 | 0.050354 | -0.096131 | 0.15106 | 59.4772 | -0.21973 | 59.6695 | -0.027466 | -0.036622 | 0.041199 | 0.050354 | 0.050354 | 0.23346 | -0.086976 | 0.27008 | -0.050354 | 0.34332 | 123.1522 | 0.086976 | 123.143 | 123.2986 | 123.1339 | 123.1064 | 123.0972 | -123.2483 | -123.0927 | 122.9599 | 123.1064 | 59.2529 | 59.0195
555.8594 | 123.1934 | -59.5551 | 63.5468 | -0.02594 | 0.00086086 | 0.062008 | 0.069073 | -0.0016279 | -0.0025207 | 0.00043363 | -0.017609 | 0.003339 | 0.068753 | 0.063252 | -0.0073188 | 0.0067526 | -0.0033475 | -0.29297 | 63.588 | -59.729 | 63.3911 | -59.4269 | -59.7931 | -0.086975 | -0.56763 | 63.5422 | -59.5963 | 63.5193 | -59.5367 | -59.6649 | -59.3765 | -0.17395 | 0.041199 | -0.15564 | 0.12817 | 59.4681 | -0.23804 | 59.642 | -0.064087 | -0.041198 | -0.004578 | -0.027466 | 0.018311 | 0.17853 | -0.10986 | 0.21973 | -0.068665 | 0.30212 | 123.1201 | 0.059509 | 123.1155 | 123.317 | 123.1384 | 123.143 | 123.0972 | -123.2758 | -123.143 | 122.9462 | 123.0743 | 59.2621 | 58.9874
556.9062 | 123.3124 | -59.5139 | 63.4964 | -0.033569 | 0.00043366 | 0.063504 | 0.068218 | -0.0022687 | -0.00059807 | -0.0019162 | 0.067841 | 0.0018436 | 0.06918 | 0.054066 | -0.0049688 | 0.0041892 | -0.0018521 | -0.29755 | 63.5376 | -59.7336 | 63.4598 | -59.3262 | -59.7061 | -0.041199 | -0.48981 | 63.4872 | -59.5963 | 63.6063 | -59.4406 | -59.5551 | -59.3079 | -0.21973 | 0.041199 | -0.036621 | 0.18768 | 59.4727 | -0.19226 | 59.6924 | 0.027466 | -0.082397 | -0.009155 | 0.10986 | 0.073242 | 0.20599 | -0.041199 | 0.28839 | 0.041198 | 0.40741 | 123.1934 | 0.15564 | 123.2025 | 123.2712 | 123.0835 | 123.0515 | 123.0011 | -123.23 | -123.0927 | 122.9736 | 123.1201 | 59.2163 | 59.024
557.8594 | 123.2208 | -59.5367 | 63.5925 | -0.02594 | -0.00063454 | 0.063717 | 0.069073 | 0.0047809 | -0.0027345 | -0.0029844 | -0.02066 | 0.0031254 | 0.069607 | 0.065388 | -0.0079596 | 0.0061118 | -0.0037747 | -0.3067 | 63.6017 | -59.7473 | 63.4048 | -59.4315 | -59.7748 | -0.086975 | -0.54932 | 63.5422 | -59.6008 | 63.5101 | -59.5322 | -59.6649 | -59.3811 | -0.21057 | 0.009156 | -0.18768 | 0.10529 | 59.4498 | -0.23804 | 59.6603 | -0.027466 | -0.064087 | -0.050354 | -0.082397 | 0.004577 | 0.15564 | -0.12817 | 0.21973 | -0.064087 | 0.31586 | 123.1522 | 0.068664 | 123.111 | 123.349 | 123.143 | 123.1384 | 123.0789 | -123.3398 | -123.1934 | 122.9416 | 123.0469 | 59.23 | 58.9874
558.8906 | 123.2483 | -59.523 | 63.5422 | 0.012207 | 0.0019291 | 0.062863 | 0.06715 | 0.0011493 | 0.0017517 | -0.0034116 | -0.057281 | 0.004407 | 0.069821 | 0.067738 | -0.006037 | 0.0078208 | -0.0052701 | -0.30212 | 63.588 | -59.7336 | 63.4094 | -59.4131 | -59.7794 | -0.082397 | -0.55847 | 63.5376 | -59.5917 | 63.5513 | -59.491 | -59.6512 | -59.3765 | -0.21057 | 0.045777 | -0.13275 | 0.10986 | 59.4406 | -0.25635 | 59.6512 | -0.045776 | -0.068665 | -0.004577 | 0.009156 | 0.032043 | 0.14648 | -0.12817 | 0.21515 | -0.059509 | 0.32043 | 123.143 | 0.10071 | 123.143 | 123.3215 | 123.1293 | 123.111 | 123.0606 | -123.2758 | -123.1338 | 122.9324 | 123.0743 | 59.2209 | 58.9645
559.8594 | 123.2483 | -59.5184 | 63.5422 | -0.071716 | 0.0012881 | 0.062222 | 0.067577 | 0.0062763 | -0.0016663 | -0.0010618 | -0.042023 | 0.0020572 | 0.069607 | 0.066029 | -0.0039008 | 0.0054708 | -0.0044157 | -0.28839 | 63.5925 | -59.7198 | 63.4048 | -59.404 | -59.761 | -0.10529 | -0.54016 | 63.5468 | -59.6008 | 63.5696 | -59.491 | -59.6191 | -59.3582 | -0.20142 | 0.050354 | -0.13733 | 0.11444 | 59.4131 | -0.24261 | 59.6146 | -0.041198 | -0.082397 | 0.004578 | 0.027466 | 0.027466 | 0.16022 | -0.10071 | 0.24262 | -0.018311 | 0.31586 | 123.1247 | 0.10986 | 123.1705 | 123.3124 | 123.1476 | 123.111 | 123.0652 | -123.262 | -123.143 | 122.9233 | 123.0881 | 59.23 | 58.9783
560.8906 | 123.2162 | -59.5093 | 63.5513 | -0.02594 | 0.0015019 | 0.062008 | 0.067791 | -0.0020551 | -0.0035889 | 0.00022003 | -0.038971 | 0.003339 | 0.068539 | 0.065602 | -0.0053962 | 0.0050436 | 7.0538e-05 | -0.30212 | 63.6063 | -59.7336 | 63.4094 | -59.4086 | -59.7794 | -0.10071 | -0.55389 | 63.5605 | -59.5917 | 63.5468 | -59.5047 | -59.6466 | -59.3765 | -0.22431 | 0.054931 | -0.14191 | 0.10071 | 59.4086 | -0.27008 | 59.6329 | -0.045776 | -0.082398 | 0.009155 | -0.004578 | 0.004577 | 0.13275 | -0.13733 | 0.21515 | -0.054931 | 0.32501 | 123.143 | 0.086975 | 123.1384 | 123.3398 | 123.1522 | 123.1155 | 123.0698 | -123.2849 | -123.143 | 122.9187 | 123.056 | 59.2072 | 58.9554
561.875 | 123.3078 | -59.5001 | 63.4918 | -0.12512 | 0.0021427 | 0.063504 | 0.06715 | 0.0047809 | 4.273e-05 | -0.0017026 | -0.02066 | 0.00077539 | 0.068539 | 0.069874 | -0.0073188 | 0.0073936 | -0.0029203 | -0.29297 | 63.4964 | -59.7244 | 63.4735 | -59.3262 | -59.761 | -0.1236 | -0.55389 | 63.4506 | -59.5871 | 63.6154 | -59.4635 | -59.5917 | -59.3124 | -0.2243 | 0.004578 | -0.01831 | 0.17395 | 59.3765 | -0.26093 | 59.6008 | -0.036621 | -0.086975 | -0.041198 | 0.1236 | 0.036621 | 0.18768 | -0.091553 | 0.27466 | -0.004578 | 0.39825 | 123.1979 | 0.1236 | 123.2025 | 123.2208 | 123.0377 | 122.9965 | 122.9507 | -123.2162 | -123.0789 | 122.9736 | 123.1155 | 59.2072 | 58.9462
562.9062 | 123.1888 | -59.5413 | 63.5284 | -0.086975 | 0.0034245 | 0.062863 | 0.067364 | 0.0030719 | -0.00059807 | -0.00084817 | -0.048126 | 0.0022708 | 0.070461 | 0.063679 | -0.0066778 | 0.0054708 | -0.0018521 | -0.37079 | 63.5559 | -59.7656 | 63.3545 | -59.4543 | -59.8846 | -0.2243 | -0.6958 | 63.5284 | -59.642 | 63.5239 | -59.5871 | -59.729 | -59.4269 | -0.2243 | 0.027466 | -0.17395 | 0.086975 | 59.317 | -0.34332 | 59.5413 | -0.11902 | -0.10071 | 0 | -0.004577 | -0.045776 | 0.11444 | -0.18768 | 0.21515 | -0.086975 | 0.31128 | 123.1201 | 0.054932 | 123.1659 | 123.3215 | 123.1705 | 123.0972 | 123.0698 | -123.2941 | -123.1705 | 122.8958 | 123.0652 | 59.1705 | 58.8455
563.8594 | 123.2117 | -59.5047 | 63.5696 | -0.0030519 | 0.0010745 | 0.062436 | 0.067791 | 0.00072213 | -0.00059807 | 0.00022003 | -0.026764 | 0.003339 | 0.06918 | 0.062184 | -0.007746 | 0.0041892 | -0.0033475 | -0.3067 | 63.6108 | -59.7198 | 63.3957 | -59.4177 | -59.7656 | -0.09613 | -0.56305 | 63.5468 | -59.5779 | 63.5468 | -59.5139 | -59.6603 | -59.3719 | -0.21515 | 0.041199 | -0.17395 | 0.086975 | 59.4086 | -0.26093 | 59.6237 | -0.045776 | -0.073242 | -0.022888 | -0.022888 | -0.009155 | 0.13275 | -0.15564 | 0.20599 | -0.082397 | 0.30212 | 123.1155 | 0.064087 | 123.1247 | 123.3307 | 123.1247 | 123.1155 | 123.0515 | -123.2895 | -123.1476 | 122.9004 | 123.0515 | 59.198 | 58.9417
564.8906 | 123.1934 | -59.5276 | 63.5925 | -0.041199 | 0.00086086 | 0.062222 | 0.070568 | -0.0020551 | 0.00025633 | 6.432e-06 | -0.0084534 | 0.0020572 | 0.070461 | 0.063893 | -0.0049688 | 0.0046164 | -0.0016385 | -0.29755 | 63.5742 | -59.6786 | 63.3224 | -59.3262 | -59.8251 | -0.10071 | -0.54016 | 63.5513 | -59.5551 | 63.5468 | -59.491 | -59.6283 | -59.3903 | -0.15106 | -0.01831 | -0.27008 | 0.20142 | 59.4269 | -0.29755 | 59.5779 | -0.14648 | -0.027466 | -0.041198 | -0.045776 | 0.036621 | 0.13733 | -0.10071 | 0.16479 | -0.073242 | 0.35248 | 123.0011 | 0.064087 | 123.1018 | 123.2529 | 123.1064 | 123.1018 | 123.0789 | -123.2712 | -123.1476 | 122.85 | 123.0743 | 59.23 | 58.9874
565.8594 | 123.1613 | -59.523 | 63.5925 | -0.094604 | 0.0027835 | 0.060299 | 0.069714 | -0.00034607 | -0.0027345 | -0.0021298 | -0.0084534 | 0.00098899 | 0.068966 | 0.062184 | -0.0058234 | 0.0044028 | 0.00049774 | -0.36163 | 63.5925 | -59.7382 | 63.4186 | -59.3765 | -59.7794 | -0.09613 | -0.52643 | 63.5696 | -59.5825 | 63.5193 | -59.5093 | -59.6466 | -59.3719 | -0.21515 | 0 | -0.17395 | 0.14648 | 59.4269 | -0.25635 | 59.642 | -0.041199 | -0.05951 | -0.022888 | -0.073242 | 0.013733 | 0.15106 | -0.1236 | 0.21057 | -0.064086 | 0.36163 | 123.1567 | 0.073243 | 123.1018 | 123.3307 | 123.1522 | 123.1155 | 123.0927 | -123.3307 | -123.175 | 122.9416 | 123.0423 | 59.1614 | 58.9966
566.8906 | 123.23 | -59.5139 | 63.5651 | -0.01831 | 0.0040653 | 0.063717 | 0.066723 | 0.0026447 | -0.00081187 | -0.0019162 | -0.060333 | 0.0014164 | 0.068112 | 0.070515 | -0.0083868 | 0.0067526 | 0.0026339 | -0.27466 | 63.5971 | -59.7336 | 63.4506 | -59.3445 | -59.7519 | -0.10529 | -0.53101 | 63.5376 | -59.5871 | 63.5834 | -59.5093 | -59.642 | -59.3582 | -0.21973 | 0.032044 | -0.11444 | 0.16937 | 59.4086 | -0.23804 | 59.6283 | -0.01831 | -0.073242 | -0.027465 | 0.018311 | 0.004578 | 0.15564 | -0.12817 | 0.22888 | -0.054932 | 0.3891 | 123.1842 | 0.07782 | 123.1705 | 123.3307 | 123.1247 | 123.111 | 123.0515 | -123.2986 | -123.1522 | 122.9645 | 123.0972 | 59.2392 | 58.9828
567.8594 | 123.2483 | -59.4955 | 63.5834 | -0.064087 | 0.0023563 | 0.06329 | 0.066723 | -0.00034607 | -0.0025207 | -0.002557 | -0.038971 | 0.0041934 | 0.072384 | 0.062611 | -0.0047552 | 0.0050436 | -0.0029203 | -0.29755 | 63.6108 | -59.7107 | 63.4277 | -59.3903 | -59.7702 | -0.09613 | -0.55389 | 63.5742 | -59.5779 | 63.5651 | -59.4589 | -59.6329 | -59.3582 | -0.21515 | 0.027466 | -0.15564 | 0.10529 | 59.3994 | -0.27466 | 59.6146 | -0.05951 | -0.082398 | -0.009155 | -0.018311 | 0.036621 | 0.13733 | -0.13733 | 0.21973 | -0.054932 | 0.32043 | 123.1384 | 0.11902 | 123.143 | 123.3215 | 123.1522 | 123.1064 | 123.0698 | -123.2941 | -123.1613 | 122.9233 | 123.0606 | 59.198 | 58.9417
568.8906 | 123.2025 | -59.5001 | 63.5834 | -0.01831 | 0.0017155 | 0.063504 | 0.067577 | -0.00077327 | -0.0014527 | 6.432e-06 | -0.032867 | 0.0041934 | 0.065975 | 0.058338 | -0.0041144 | 0.0044028 | -0.00014306 | -0.29297 | 63.6108 | -59.7198 | 63.414 | -59.3948 | -59.7565 | -0.09613 | -0.55389 | 63.5834 | -59.5825 | 63.5559 | -59.5001 | -59.6466 | -59.3765 | -0.21973 | 0.027466 | -0.16937 | 0.10529 | 59.404 | -0.25635 | 59.6237 | -0.036621 | -0.082398 | 0 | -0.027466 | 0 | 0.1236 | -0.14648 | 0.20599 | -0.064086 | 0.32501 | 123.1338 | 0.082398 | 123.1384 | 123.3307 | 123.1659 | 123.111 | 123.0835 | -123.3032 | -123.1659 | 122.9141 | 123.056 | 59.2072 | 58.9462
569.8594 | 123.1934 | -59.4818 | 63.5925 | -0.041199 | 0.00086086 | 0.063717 | 0.068218 | 0.0017901 | -0.00017087 | 0.00086083 | -0.02066 | 0.0037662 | 0.069607 | 0.065174 | -0.0053962 | 0.003762 | 0.00049774 | -0.29755 | 63.6108 | -59.7153 | 63.4232 | -59.3948 | -59.7702 | -0.09613 | -0.55847 | 63.5834 | -59.5688 | 63.5559 | -59.4864 | -59.642 | -59.3719 | -0.23346 | 0.018311 | -0.16937 | 0.086976 | 59.3857 | -0.28839 | 59.6191 | -0.054932 | -0.086975 | -0.009155 | -0.036621 | -0.004577 | 0.10986 | -0.16022 | 0.19684 | -0.073242 | 0.32044 | 123.1384 | 0.082398 | 123.1247 | 123.3261 | 123.1522 | 123.0927 | 123.0652 | -123.3078 | -123.1613 | 122.905 | 123.0377 | 59.1843 | 58.9233
570.8594 | 123.2529 | -59.5093 | 63.5788 | -0.10986 | 0.0021427 | 0.062436 | 0.067791 | 0.0015765 | -0.00059807 | -0.0051206 | -0.060333 | 0.002698 | 0.069393 | 0.069233 | -0.0058234 | 0.0076072 | -0.00014306 | -0.27008 | 63.6063 | -59.6786 | 63.4644 | -59.3308 | -59.7565 | -0.091553 | -0.5127 | 63.5605 | -59.5367 | 63.5925 | -59.4864 | -59.6283 | -59.3628 | -0.16937 | 0.027466 | -0.11444 | 0.17853 | 59.4177 | -0.24719 | 59.5871 | -0.07782 | -0.027466 | -0.01831 | 0.013733 | 0.022888 | 0.14648 | -0.11902 | 0.17395 | -0.091553 | 0.3479 | 123.143 | 0.050354 | 123.1293 | 123.2849 | 123.0972 | 123.1155 | 123.0698 | -123.2574 | -123.1155 | 122.9736 | 123.1018 | 59.2392 | 58.9966
571.8906 | 123.3078 | -59.4635 | 63.5284 | -0.086975 | 0.0036381 | 0.064358 | 0.066937 | 0.00050853 | -0.0025207 | -0.00084817 | 0.052582 | -7.901e-05 | 0.069393 | 0.060688 | -0.0024054 | -0.000297 | -0.0014249 | -0.27924 | 63.5559 | -59.6878 | 63.4964 | -59.2804 | -59.6786 | -0.027466 | -0.45319 | 63.5422 | -59.5551 | 63.9999 | -59.8114 | -59.5779 | -59.1568 | -0.2243 | 0.027466 | -0.032043 | 0.1831 | 59.436 | -0.21515 | 59.6603 | 0.009155 | -0.091553 | 0.013733 | 0.4715 | -0.3479 | 0.3067 | -0.11444 | 0.39825 | -0.022888 | 0.40741 | 123.1842 | -0.25635 | 123.555 | 123.2437 | 123.0972 | 123.0194 | 123.0057 | -123.2162 | -123.0835 | 122.9599 | 123.4634 | 59.1843 | 59.0103
572.8594 | 123.2208 | -59.4864 | 63.5834 | -0.064087 | 0.00043366 | 0.062222 | 0.067364 | 0.0017901 | -0.0042297 | -0.0027708 | -0.038971 | 0.0020572 | 0.068539 | 0.068592 | -0.0083868 | 0.006539 | -0.0052701 | -0.30212 | 63.62 | -59.7107 | 63.4323 | -59.3903 | -59.7427 | -0.086975 | -0.54016 | 63.5925 | -59.5505 | 63.5834 | -59.4727 | -59.6329 | -59.3445 | -0.2243 | 0.036621 | -0.15106 | 0.09613 | 59.3994 | -0.25635 | 59.6237 | -0.032044 | -0.064087 | 0.009155 | 0 | 0.013733 | 0.14191 | -0.14648 | 0.20599 | -0.082398 | 0.32043 | 123.143 | 0.07782 | 123.1338 | 123.3307 | 123.143 | 123.1064 | 123.0789 | -123.2941 | -123.1338 | 122.9187 | 123.0698 | 59.1843 | 58.9462
573.8906 | 123.2346 | -59.4727 | 63.588 | -0.094604 | 0.0010745 | 0.062863 | 0.065014 | 0.0013629 | -0.0027345 | -0.001489 | 0.040375 | 0.0037662 | 0.066403 | 0.064961 | -0.0053962 | 0.0058982 | 0.0019931 | -0.23804 | 63.5651 | -59.6512 | 63.5147 | -59.2758 | -59.6603 | -0.013733 | -0.45776 | 63.5376 | -59.5505 | 63.6108 | -59.4452 | -59.5642 | -59.3216 | -0.17853 | -0.022889 | -0.073243 | 0.19684 | 59.4589 | -0.18768 | 59.6375 | -0.009155 | -0.07782 | -0.050354 | 0.022888 | 0.027466 | 0.15106 | -0.091553 | 0.22888 | -0.013733 | 0.37537 | 123.1659 | 0.10529 | 123.1613 | 123.2162 | 123.0881 | 123.0377 | 123.0103 | -123.2391 | -123.1384 | 122.9874 | 123.0835 | 59.2346 | 59.0149
574.8594 | 123.2529 | -59.4864 | 63.5925 | -0.01831 | 0.0019291 | 0.062222 | 0.067577 | 0.0020037 | -0.0031617 | -0.00063437 | -0.038971 | 0.0041934 | 0.068112 | 0.073292 | -0.0079596 | 0.0039756 | -0.0029203 | -0.27008 | 63.6108 | -59.7061 | 63.4644 | -59.3353 | -59.729 | -0.091553 | -0.48523 | 63.5788 | -59.5551 | 63.6017 | -59.4589 | -59.6146 | -59.3124 | -0.21973 | 0.018311 | -0.12817 | 0.15106 | 59.3948 | -0.24262 | 59.6146 | -0.022888 | -0.068665 | -0.013733 | 0.009156 | 0.027466 | 0.17395 | -0.12817 | 0.24262 | -0.059509 | 0.37079 | 123.1705 | 0.096131 | 123.1567 | 123.317 | 123.1338 | 123.0972 | 123.0652 | -123.2986 | -123.1476 | 122.9507 | 123.0881 | 59.2163 | 59.0012
575.8906 | 123.317 | -59.4452 | 63.5559 | -0.15564 | 0.00086086 | 0.064572 | 0.066723 | 0.00029473 | -0.0029481 | -0.0021298 | 0.04953 | 0.0037662 | 0.068112 | 0.062611 | -0.0053962 | 0.0071798 | 0.00092494 | -0.21973 | 63.5788 | -59.6786 | 63.5788 | -59.1934 | -59.6283 | -0.013733 | -0.40741 | 63.533 | -59.5139 | 63.6703 | -59.3582 | -59.4864 | -59.2392 | -0.23346 | 0.022888 | 0.022888 | 0.25177 | 59.4315 | -0.18311 | 59.6649 | 0.050354 | -0.068665 | -0.022888 | 0.11444 | 0.086975 | 0.20599 | -0.041199 | 0.27466 | 0.027466 | 0.48523 | 123.2574 | 0.15564 | 123.1842 | 123.2574 | 123.0469 | 123.024 | 122.9782 | -123.2346 | -123.0698 | 123.024 | 123.1155 | 59.2255 | 59.0378
576.8594 | 123.2208 | -59.5093 | 63.5696 | -0.094604 | 0.0017155 | 0.06329 | 0.066937 | 0.0043537 | -0.0042297 | -0.00042077 | -0.10001 | 0.00077539 | 0.067471 | 0.072651 | -0.0062506 | 0.0076072 | 0.0011385 | -0.25177 | 63.6292 | -59.7061 | 63.5468 | -59.5367 | -59.7839 | 0.054932 | -0.43488 | 63.6017 | -59.5459 | 63.6154 | -59.4406 | -59.6146 | -59.2987 | -0.19684 | 0.059509 | -0.022888 | -0.027466 | 59.5642 | -0.27466 | 59.761 | -0.07782 | -0.036621 | 0.032044 | 0.045776 | 0.068664 | 0.21057 | -0.10529 | 0.24719 | -0.068665 | 0.16937 | 123.2529 | 0.10529 | 123.1613 | 123.3353 | 123.1476 | 123.1384 | 123.111 | -123.2758 | -123.1155 | 123.056 | 123.1247 | 59.2575 | 59.0744
577.8906 | 123.3307 | -59.4543 | 63.5696 | -0.064087 | 0.0019291 | 0.062222 | 0.065655 | -0.0026959 | -0.0031617 | -0.0017026 | 0.015961 | 0.0022708 | 0.067684 | 0.060475 | -0.0056098 | 0.00483 | 0.00071134 | -0.25635 | 63.5742 | -59.6466 | 63.5605 | -59.2117 | -59.6237 | -0.018311 | -0.3891 | 63.5468 | -59.5184 | 63.6749 | -59.3628 | -59.5001 | -59.2346 | -0.19226 | 0.004578 | -0.009155 | 0.24262 | 59.436 | -0.16937 | 59.6283 | 0.022888 | -0.064087 | -0.022888 | 0.10529 | 0.091553 | 0.21973 | -0.045776 | 0.28381 | 0.018311 | 0.43487 | 123.2071 | 0.15564 | 123.1934 | 123.2208 | 123.0652 | 123.0286 | 123.0011 | -123.2162 | -123.0881 | 123.0148 | 123.1293 | 59.198 | 59.0652
578.8594 | 123.1979 | -59.491 | 63.6337 | -0.01831 | 0.00064726 | 0.062222 | 0.067791 | -0.0024823 | -0.0050843 | -0.002557 | -0.035919 | 0.0031254 | 0.072598 | 0.065388 | -0.0056098 | 0.0039756 | 7.0538e-05 | -0.29297 | 63.6246 | -59.7061 | 63.4415 | -59.3628 | -59.7336 | -0.10071 | -0.54474 | 63.5971 | -59.5367 | 63.5696 | -59.4864 | -59.6375 | -59.3445 | -0.21515 | -0.009155 | -0.19226 | 0.12817 | 59.3903 | -0.24262 | 59.6054 | -0.027466 | -0.045776 | -0.036621 | -0.064087 | 0.004578 | 0.14648 | -0.14648 | 0.19226 | -0.10071 | 0.34332 | 123.1476 | 0.050354 | 123.1064 | 123.3307 | 123.1338 | 123.1155 | 123.0881 | -123.3398 | -123.1705 | 122.9324 | 123.0606 | 59.198 | 58.9462
579.8906 | 123.2208 | -59.4864 | 63.6063 | -0.048828 | 0.00022006 | 0.063504 | 0.068005 | 0.00050853 | -0.00038447 | -0.00042077 | -0.035919 | 0.003339 | 0.068539 | 0.066029 | -0.006037 | 0.0061118 | -0.0024931 | -0.29755 | 63.62 | -59.6832 | 63.4323 | -59.3719 | -59.761 | -0.086975 | -0.54474 | 63.6154 | -59.5551 | 63.5788 | -59.4772 | -59.6191 | -59.3445 | -0.19684 | 0.013733 | -0.17395 | 0.11444 | 59.3994 | -0.27466 | 59.5963 | -0.077819 | -0.068665 | 0.009155 | -0.027466 | 0.009155 | 0.14191 | -0.13275 | 0.21057 | -0.064087 | 0.31128 | 123.1155 | 0.07782 | 123.1338 | 123.3032 | 123.1705 | 123.1064 | 123.1018 | -123.2895 | -123.1613 | 122.9187 | 123.0652 | 59.1888 | 58.9417
580.8594 | 123.1979 | -59.5001 | 63.6246 | -0.041199 | 0.0021427 | 0.063076 | 0.066509 | 0.0024311 | -0.0031617 | -0.00042077 | -0.023712 | 0.0048344 | 0.068753 | 0.065602 | -0.0075324 | 0.0016256 | -0.00014306 | -0.28839 | 63.6566 | -59.6786 | 63.4415 | -59.3811 | -59.7382 | -0.09613 | -0.54474 | 63.5834 | -59.5413 | 63.5788 | -59.4864 | -59.6146 | -59.3353 | -0.17853 | 0.032043 | -0.18311 | 0.11902 | 59.404 | -0.23804 | 59.5825 | -0.059509 | -0.041199 | -0.041199 | -0.045777 | 0.013733 | 0.16479 | -0.11444 | 0.20599 | -0.073242 | 0.29755 | 123.1201 | 0.054932 | 123.1201 | 123.3353 | 123.1247 | 123.1567 | 123.0835 | -123.3032 | -123.1659 | 122.9416 | 123.0789 | 59.2117 | 58.9554
581.8906 | 123.3124 | -59.4406 | 63.5788 | -0.056457 | 0.00022006 | 0.060299 | 0.066509 | -0.00077327 | 0.00046993 | -0.001489 | 0.025116 | 0.002698 | 0.070461 | 0.063893 | -0.0039008 | 0.003762 | -0.0039883 | -0.29297 | 63.6108 | -59.6695 | 63.5284 | -59.2575 | -59.6649 | -0.027466 | -0.46234 | 63.5284 | -59.5367 | 63.6749 | -59.3719 | -59.4955 | -59.23 | -0.22888 | 0.032044 | -0.050354 | 0.18311 | 59.4131 | -0.2243 | 59.642 | 0.004578 | -0.09613 | -0.050354 | 0.096131 | 0.068665 | 0.21057 | -0.054931 | 0.3067 | 0.041199 | 0.41199 | 123.1979 | 0.16479 | 123.2117 | 123.2803 | 123.0652 | 123.0515 | 122.9691 | -123.2483 | -123.1155 | 122.9691 | 123.1155 | 59.1476 | 58.9783
582.8594 | 123.2254 | -59.4589 | 63.6246 | 0.0045776 | 0.0019291 | 0.062436 | 0.066937 | 0.0032855 | -0.0031617 | -0.0027708 | -0.042023 | 0.0035526 | 0.067684 | 0.068379 | -0.0064642 | 0.0076072 | -0.0012113 | -0.27466 | 63.652 | -59.6741 | 63.4598 | -59.3628 | -59.7382 | -0.10986 | -0.54016 | 63.6063 | -59.523 | 63.5925 | -59.4452 | -59.6237 | -59.3308 | -0.21515 | 0.027466 | -0.16479 | 0.09613 | 59.3491 | -0.27924 | 59.5642 | -0.064087 | -0.064087 | -0.018311 | -0.032044 | 0.013733 | 0.12817 | -0.16479 | 0.19226 | -0.10071 | 0.31128 | 123.1338 | 0.07782 | 123.1155 | 123.3261 | 123.1293 | 123.111 | 123.0652 | -123.2986 | -123.1476 | 122.9187 | 123.0515 | 59.1843 | 58.9188
583.8906 | 123.1842 | -59.4589 | 63.62 | -0.033569 | 0.00064726 | 0.062008 | 0.067364 | 0.0039263 | -0.00038447 | -0.0017026 | -0.029816 | 0.0037662 | 0.069393 | 0.063893 | -0.0066778 | 0.0050436 | -0.00014306 | -0.3067 | 63.6612 | -59.6558 | 63.4277 | -59.3628 | -59.7336 | -0.091553 | -0.54932 | 63.6337 | -59.5367 | 63.5788 | -59.4955 | -59.6237 | -59.3308 | -0.19684 | 0.041199 | -0.19226 | 0.09613 | 59.3674 | -0.27466 | 59.5642 | -0.07782 | -0.07782 | 0.013733 | -0.041199 | -0.036621 | 0.12817 | -0.16479 | 0.20599 | -0.086975 | 0.29297 | 123.0835 | 0.041199 | 123.1155 | 123.317 | 123.1705 | 123.1201 | 123.0927 | -123.2758 | -123.1567 | 122.8867 | 123.0377 | 59.1522 | 58.9096
584.8594 | 123.1934 | -59.4727 | 63.6246 | -0.0030519 | 0.0015019 | 0.060727 | 0.067577 | 0.0015765 | -0.0010255 | -0.0044796 | -0.032867 | 0.0041934 | 0.069607 | 0.060047 | -0.0066778 | 0.0054708 | -0.0027067 | -0.30212 | 63.6749 | -59.6603 | 63.4415 | -59.3628 | -59.7336 | -0.086975 | -0.53101 | 63.6154 | -59.5505 | 63.5742 | -59.4864 | -59.61 | -59.3262 | -0.18768 | 0.050354 | -0.18311 | 0.10986 | 59.3857 | -0.26093 | 59.5734 | -0.073243 | -0.07782 | -0.009156 | -0.050354 | -0.013733 | 0.14648 | -0.13733 | 0.2243 | -0.059509 | 0.29755 | 123.1018 | 0.064087 | 123.1247 | 123.3353 | 123.1659 | 123.1476 | 123.0881 | -123.2849 | -123.175 | 122.9141 | 123.0469 | 59.1705 | 58.9417
585.8906 | 123.1979 | -59.491 | 63.6429 | -0.02594 | 0.0023563 | 0.063931 | 0.068646 | 0.0022173 | -0.0057251 | -0.0021298 | -0.02066 | 0.0054752 | 0.067898 | 0.068806 | -0.006037 | 0.0058982 | 0.0030611 | -0.31128 | 63.6246 | -59.6603 | 63.4827 | -59.3811 | -59.7153 | -0.064087 | -0.52185 | 63.6017 | -59.5367 | 63.5834 | -59.4772 | -59.6146 | -59.3536 | -0.16937 | -0.01831 | -0.16022 | 0.10986 | 59.4269 | -0.2243 | 59.5963 | -0.054932 | -0.045776 | -0.041198 | -0.059509 | 0.013733 | 0.13733 | -0.1236 | 0.18311 | -0.07782 | 0.27923 | 123.143 | 0.059509 | 123.1201 | 123.2849 | 123.1384 | 123.1155 | 123.0927 | -123.3032 | -123.1796 | 122.9736 | 123.0743 | 59.1797 | 58.9691
586.8594 | 123.1842 | -59.4635 | 63.6292 | -0.02594 | -0.00020714 | 0.061367 | 0.065655 | 8.1126e-05 | -0.0014527 | 6.432e-06 | -0.023712 | 0.0035526 | 0.06683 | 0.061756 | -0.0045416 | 0.0035482 | -0.00057046 | -0.29755 | 63.6337 | -59.6786 | 63.5101 | -59.3628 | -59.7656 | -0.064087 | -0.53558 | 63.6108 | -59.5367 | 63.5925 | -59.4635 | -59.5871 | -59.3536 | -0.21515 | 0.004578 | -0.11902 | 0.10071 | 59.3994 | -0.30212 | 59.6146 | -0.086975 | -0.073242 | -0.01831 | -0.036621 | 0 | 0.10986 | -0.1236 | 0.18311 | -0.050354 | 0.31586 | 123.1888 | 0.073242 | 123.1293 | 123.3124 | 123.1476 | 123.0972 | 123.0743 | -123.3078 | -123.1659 | 122.9736 | 123.056 | 59.166 | 58.9279
587.8906 | 123.2895 | -59.4452 | 63.5925 | -0.064087 | 0.0015019 | 0.064145 | 0.066937 | 0.0013629 | -0.0023071 | -0.0017026 | 0.015961 | 0.002698 | 0.067898 | 0.058338 | -0.0049688 | 0.0061118 | -0.0012113 | -0.34332 | 63.5742 | -59.6649 | 63.4872 | -59.3033 | -59.7061 | -0.11902 | -0.55389 | 63.5651 | -59.5413 | 63.6292 | -59.4131 | -59.5596 | -59.2667 | -0.21973 | -0.01831 | -0.10529 | 0.14191 | 59.3262 | -0.26093 | 59.5459 | -0.041199 | -0.096131 | -0.027466 | 0.036621 | 0.032043 | 0.17853 | -0.11444 | 0.27466 | -0.01831 | 0.36163 | 123.1522 | 0.12817 | 123.1705 | 123.2391 | 123.1064 | 123.0194 | 123.0103 | -123.2574 | -123.1338 | 122.9324 | 123.0743 | 59.1019 | 58.8913
588.8594 | 123.2208 | -59.491 | 63.6246 | -0.079346 | 0.0015019 | 0.062649 | 0.067791 | -0.00013247 | -0.00081187 | -0.00084817 | -0.05423 | 0.00163 | 0.06683 | 0.068806 | -0.0058234 | 0.0033346 | -0.0037747 | -0.3067 | 63.6383 | -59.6832 | 63.4644 | -59.3399 | -59.6924 | -0.073242 | -0.54016 | 63.5971 | -59.5413 | 63.5834 | -59.4589 | -59.6146 | -59.3399 | -0.19226 | 0.013733 | -0.16022 | 0.15106 | 59.4177 | -0.20142 | 59.61 | -0.009155 | -0.050354 | -0.027466 | -0.041199 | 0.032044 | 0.15106 | -0.1236 | 0.20142 | -0.073242 | 0.34332 | 123.1476 | 0.082398 | 123.1247 | 123.3215 | 123.1384 | 123.1293 | 123.0881 | -123.3078 | -123.1659 | 122.9553 | 123.0743 | 59.1843 | 58.9508
589.8594 | 123.3215 | -59.4223 | 63.588 | -0.056457 | 0.00064726 | 0.063504 | 0.066509 | 0.0015765 | -0.0012391 | -0.0010618 | 0.025116 | 0.0024844 | 0.065762 | 0.066883 | -0.0066778 | 0.0050436 | -0.0024931 | -0.24261 | 63.5925 | -59.61 | 63.5788 | -59.1888 | -59.6054 | 0.004578 | -0.40283 | 63.5788 | -59.4818 | 63.7024 | -59.3308 | -59.4681 | -59.2346 | -0.18768 | 0.004577 | -0.009156 | 0.23346 | 59.4269 | -0.18311 | 59.6146 | 0.004577 | -0.05951 | -0.009156 | 0.11444 | 0.091552 | 0.18768 | -0.045777 | 0.24719 | 0.013733 | 0.42114 | 123.1888 | 0.15106 | 123.1842 | 123.2025 | 123.0606 | 123.0148 | 123.0011 | -123.1979 | -123.0698 | 123.0011 | 123.1247 | 59.1797 | 59.0195
590.8906 | 123.3124 | -59.4086 | 63.5788 | -0.10986 | 0.0010745 | 0.062222 | 0.067577 | 0.0013629 | -0.0010255 | -0.00042077 | 0.012909 | 0.00077539 | 0.070461 | 0.070301 | -0.0075324 | 0.0067526 | -0.0029203 | -0.28839 | 63.5696 | -59.6558 | 63.533 | -59.2575 | -59.642 | -0.054932 | -0.48981 | 63.5651 | -59.5413 | 63.6703 | -59.3811 | -59.5093 | -59.23 | -0.24719 | -0.009155 | -0.045776 | 0.15106 | 59.3536 | -0.23346 | 59.6008 | 0.013733 | -0.13275 | -0.013733 | 0.091553 | 0.027465 | 0.17853 | -0.10071 | 0.31128 | 0.032044 | 0.39826 | 123.1888 | 0.16022 | 123.2117 | 123.2254 | 123.1064 | 122.9782 | 122.9736 | -123.2346 | -123.1201 | 122.9416 | 123.0789 | 59.1202 | 58.9188
591.8594 | 123.3124 | -59.4131 | 63.5925 | 0.20294 | -0.0019161 | 0.063717 | 0.06715 | -0.00077327 | -0.00059807 | -0.0017026 | -0.011505 | 0.0041934 | 0.070248 | 0.060688 | -0.0068914 | 0.0061118 | -0.0016385 | -0.004578 | 63.6429 | -59.6191 | 63.5971 | -59.23 | -59.6054 | 0.009155 | -0.38452 | 63.5605 | -59.4818 | 63.7115 | -59.3216 | -59.4727 | -59.2117 | -0.20599 | 0.050354 | 0.004578 | 0.18311 | 59.4223 | -0.19226 | 59.6283 | 0.013733 | -0.068665 | -0.032043 | 0.11902 | 0.091553 | 0.20142 | -0.059509 | 0.27008 | 0.009156 | 0.3891 | 123.2162 | 0.16022 | 123.1934 | 123.262 | 123.0423 | 123.056 | 122.9736 | -123.2117 | -123.0743 | 123.0103 | 123.1247 | 59.4086 | 59.0286
592.8906 | 123.3215 | -59.4086 | 63.5834 | -0.12512 | 0.0021427 | 0.06094 | 0.066937 | -0.00077327 | -0.0031617 | -0.0021298 | 0.015961 | 0.003339 | 0.068112 | 0.064106 | -0.0058234 | 0.0041892 | 0.0011385 | -0.2243 | 63.5834 | -59.6283 | 63.6063 | -59.166 | -59.5871 | 0.004578 | -0.3891 | 63.5696 | -59.5001 | 63.6932 | -59.3216 | -59.4498 | -59.2117 | -0.21973 | 0 | 0.022888 | 0.24261 | 59.4131 | -0.17853 | 59.6329 | 0.041199 | -0.091553 | -0.013733 | 0.10986 | 0.086975 | 0.19684 | -0.041199 | 0.28839 | 0.050354 | 0.46234 | 123.2346 | 0.17853 | 123.1934 | 123.2117 | 123.0698 | 122.9919 | 122.9782 | -123.2117 | -123.0835 | 123.0148 | 123.1018 | 59.1843 | 59.0195
593.8594 | 123.2712 | -59.436 | 63.5376 | -0.094604 | 0.0012881 | 0.062863 | 0.067364 | 0.0015765 | -0.0010255 | -0.0036252 | 0.0098572 | 0.0018436 | 0.068325 | 0.060261 | -0.010523 | 0.0052572 | -0.00099766 | -0.27008 | 63.6246 | -59.6558 | 63.5651 | -59.23 | -59.6375 | -0.027466 | -0.43488 | 63.5605 | -59.4818 | 63.5284 | -59.4864 | -59.3674 | -59.1797 | -0.21973 | 0.086975 | 0.027465 | 0.20599 | 59.4086 | -0.20142 | 59.6283 | 0.018311 | -0.045777 | 0.022888 | -0.009156 | -0.050354 | 0.25635 | 0.068664 | 0.30212 | 0.11444 | 0.42572 | 123.2208 | -0.004577 | 123.0103 | 123.2803 | 123.0423 | 123.0606 | 122.9965 | -123.1934 | -123.0194 | 123.0011 | 122.9645 | 59.166 | 59.0012
594.8594 | 123.2437 | -59.4543 | 63.6154 | -0.01831 | 0.0017155 | 0.062222 | 0.068432 | -0.00098687 | -0.0012391 | -0.00042077 | -0.035919 | 0.0039798 | 0.068753 | 0.061543 | -0.0073188 | 0.0069662 | 0.0032749 | -0.25635 | 63.6246 | -59.6649 | 63.5468 | -59.2712 | -59.6512 | -0.054932 | -0.4715 | 63.62 | -59.4955 | 63.7619 | -59.5596 | -59.8206 | -59.4452 | -0.21057 | 0.009156 | -0.068664 | 0.18311 | 59.3994 | -0.19684 | 59.61 | 0.013733 | -0.041198 | 0.004578 | 0.14648 | -0.10529 | 0.009156 | -0.36621 | 0.050354 | -0.32501 | 0.39368 | 123.2117 | -0.064087 | 123.2574 | 123.2895 | 123.1155 | 123.0789 | 123.0743 | -123.2803 | -123.111 | 123.0011 | 123.2162 | 59.198 | 58.9828
595.8594 | 123.3536 | -59.4223 | 63.6017 | -0.056457 | 0.0019291 | 0.063076 | 0.060314 | 0.0049945 | -0.0016663 | -0.002557 | 0.03122 | 0.00163 | 0.06918 | 0.063252 | -0.009455 | 0.0035482 | -0.0035611 | -0.25635 | 63.6154 | -59.6237 | 63.3362 | -59.0973 | -59.6237 | -0.11902 | -0.43488 | 63.5742 | -59.5139 | 63.7436 | -59.3033 | -59.436 | -59.1888 | -0.20142 | 0.013732 | -0.2655 | 0.32501 | 59.3033 | -0.20142 | 59.5047 | 0 | -0.091553 | -0.027466 | 0.14191 | 0.11902 | 0.23346 | -0.013733 | 0.32501 | 0.07782 | 0.52643 | 122.9599 | 0.21057 | 123.2574 | 123.2391 | 123.0881 | 123.0377 | 122.9965 | -123.2254 | -123.1155 | 122.7585 | 123.1659 | 59.166 | 58.9874
596.9062 | 123.23 | -59.4681 | 63.6017 | -0.064087 | 0.0015019 | 0.061795 | 0.068005 | -0.00098687 | -0.0023071 | -0.00084817 | -0.13968 | 0.0014164 | 0.06683 | 0.066456 | -0.0079596 | 0.008248 | 0.0032749 | -0.26093 | 63.6429 | -59.6558 | 63.5284 | -59.3628 | -59.8801 | 0 | -0.46234 | 63.6383 | -59.4955 | 63.6475 | -59.404 | -59.5917 | -59.2667 | -0.18768 | 0.041198 | -0.073243 | 0.10529 | 59.4681 | -0.41199 | 59.6558 | -0.2243 | -0.027465 | 0.036621 | 0.045776 | 0.064087 | 0.20142 | -0.1236 | 0.22888 | -0.096131 | 0.29297 | 123.1842 | 0.091552 | 123.143 | 123.2986 | 123.1338 | 123.111 | 123.1064 | -123.2574 | -123.0972 | 122.9965 | 123.1155 | 59.2072 | 59.0057
597.8594 | 123.3215 | -59.4452 | 63.533 | -0.086975 | 6.46e-06 | 0.063717 | 0.066082 | -0.00077327 | -0.0020935 | -0.003198 | 0.0068054 | 0.0018436 | 0.067898 | 0.065388 | -0.012873 | 0.0035482 | -0.0027067 | -0.28381 | 63.6337 | -59.6191 | 63.5742 | -59.2117 | -59.6283 | -0.027466 | -0.42572 | 63.588 | -59.4864 | 63.9954 | -59.7519 | -59.4543 | -59.0927 | -0.17395 | 0.10071 | 0.041199 | 0.23346 | 59.4177 | -0.18311 | 59.5917 | -0.009155 | -0.041199 | 0.054932 | 0.46234 | -0.3067 | 0.35248 | -0.009156 | 0.39368 | 0.032043 | 0.40741 | 123.1934 | -0.2655 | 123.4818 | 123.2529 | 123.0743 | 123.0789 | 123.0331 | -123.1522 | -123.0194 | 123.0194 | 123.4406 | 59.1614 | 59.0195
598.9062 | 123.262 | -59.4315 | 63.5971 | -0.11749 | 0.0015019 | 0.064358 | 0.066509 | -0.0018415 | -0.0018799 | -0.0027708 | 0.0068054 | 0.0014164 | 0.067898 | 0.062397 | -0.0075324 | 0.0039756 | 0.0011385 | -0.37537 | 63.5925 | -59.6466 | 63.4598 | -59.2896 | -59.7015 | -0.16022 | -0.59967 | 63.5559 | -59.523 | 63.6566 | -59.404 | -59.5413 | -59.2667 | -0.21515 | -0.004578 | -0.13733 | 0.14191 | 59.2712 | -0.27008 | 59.4864 | -0.054932 | -0.091552 | -0.041199 | 0.059509 | 0.027466 | 0.16479 | -0.10986 | 0.25635 | -0.018311 | 0.35705 | 123.1064 | 0.11902 | 123.1796 | 123.2391 | 123.0789 | 123.024 | 122.9874 | -123.2437 | -123.1201 | 122.8912 | 123.0881 | 59.0561 | 58.8318
599.8594 | 123.2895 | -59.4498 | 63.588 | -0.071716 | 0.00022006 | 0.062436 | 0.067577 | -0.00034607 | -0.0023071 | -0.0017026 | -0.029816 | 0.00056179 | 0.068539 | 0.060261 | -0.0056098 | 0.0058982 | 0.0011385 | -0.32501 | 63.62 | -59.6466 | 63.5147 | -59.285 | -59.6924 | -0.10529 | -0.55847 | 63.5834 | -59.5184 | 63.6703 | -59.3903 | -59.5322 | -59.2575 | -0.19684 | 0.032043 | -0.073243 | 0.16479 | 59.3445 | -0.24262 | 59.5413 | -0.045777 | -0.068665 | -0.004578 | 0.082397 | 0.059509 | 0.19226 | -0.082398 | 0.26093 | -0.013733 | 0.36163 | 123.1613 | 0.12817 | 123.1888 | 123.2666 | 123.1018 | 123.0698 | 123.0331 | -123.2346 | -123.1064 | 122.9645 | 123.1201 | 59.1248 | 58.8913
600.8594 | 123.2391 | -59.4406 | 63.6383 | -0.041199 | 0.0034245 | 0.062863 | 0.066509 | -0.0016279 | -0.0020935 | -0.003198 | -0.038971 | 0.0022708 | 0.067044 | 0.065815 | -0.0049688 | 0.0067526 | -0.0018521 | -0.24261 | 63.62 | -59.642 | 63.5696 | -59.2163 | -59.6329 | -0.013733 | -0.42572 | 63.6292 | -59.491 | 63.6749 | -59.3857 | -59.5001 | -59.2529 | -0.20142 | -0.018311 | -0.068665 | 0.2243 | 59.4269 | -0.19226 | 59.6283 | 0.009155 | -0.050354 | -0.009156 | 0.036621 | 0.054932 | 0.18768 | -0.059509 | 0.23804 | -0.009155 | 0.42572 | 123.2117 | 0.10529 | 123.1659 | 123.262 | 123.1201 | 123.0606 | 123.0698 | -123.2803 | -123.1293 | 123.0103 | 123.1155 | 59.198 | 59.0149
601.8594 | 123.1979 | -59.4269 | 63.6337 | -0.056457 | -0.0017025 | 0.061154 | 0.070141 | 0.0022173 | -0.0010255 | -0.0012754 | -0.060333 | 0.00163 | 0.067257 | 0.06667 | -0.0064642 | 0.00483 | -0.0039883 | -0.30212 | 63.707 | -59.6512 | 63.4735 | -59.3353 | -59.7198 | -0.091553 | -0.53101 | 63.6566 | -59.4864 | 63.6017 | -59.4315 | -59.5917 | -59.3079 | -0.2243 | 0.073242 | -0.16022 | 0.091553 | 59.3353 | -0.29297 | 59.5596 | -0.068665 | -0.059509 | 0.022888 | -0.032043 | -0.004578 | 0.11902 | -0.1648 | 0.17853 | -0.10529 | 0.31586 | 123.1247 | 0.054931 | 123.0881 | 123.3582 | 123.143 | 123.1338 | 123.0835 | -123.2849 | -123.1201 | 122.9004 | 123.0286 | 59.1248 | 58.8959
602.8906 | 123.2208 | -59.4223 | 63.6703 | -0.12512 | 0.0040653 | 0.063076 | 0.066723 | -0.0024823 | -0.0031617 | -0.0019162 | -0.032867 | 0.0024844 | 0.068966 | 0.070515 | -0.007746 | 0.0058982 | -0.00035666 | -0.22888 | 63.6566 | -59.6237 | 63.5742 | -59.23 | -59.6283 | -0.022888 | -0.46234 | 63.6337 | -59.5047 | 63.652 | -59.3857 | -59.5184 | -59.2758 | -0.20142 | -0.013733 | -0.09613 | 0.19226 | 59.3994 | -0.20599 | 59.6008 | -0.004578 | -0.082398 | -0.036621 | -0.01831 | 0.036621 | 0.14648 | -0.096131 | 0.22888 | -0.013733 | 0.39368 | 123.1979 | 0.11902 | 123.1567 | 123.2803 | 123.1384 | 123.0789 | 123.056 | -123.2941 | -123.175 | 122.9965 | 123.0743 | 59.1934 | 58.96
603.8594 | 123.1842 | -59.4635 | 63.6658 | -0.0030519 | -0.0010617 | 0.060513 | 0.068218 | -0.0020551 | 0.00046993 | -0.0017026 | -0.07254 | 0.0037662 | 0.065975 | 0.067524 | -0.007746 | 0.0071798 | -0.0022793 | -0.30212 | 63.707 | -59.6603 | 63.4827 | -59.3124 | -59.7061 | -0.10071 | -0.55847 | 63.6612 | -59.523 | 63.6292 | -59.4543 | -59.5825 | -59.2667 | -0.19684 | 0.041199 | -0.1831 | 0.15106 | 59.3628 | -0.24262 | 59.5596 | -0.045777 | -0.059509 | -0.004577 | -0.036621 | 0.009155 | 0.19684 | -0.11902 | 0.25635 | -0.05951 | 0.3479 | 123.143 | 0.068664 | 123.1522 | 123.3673 | 123.1842 | 123.1705 | 123.1247 | -123.3261 | -123.1888 | 122.9462 | 123.0927 | 59.1614 | 58.905
604.9062 | 123.1705 | -59.4498 | 63.6612 | -0.048828 | 0.0021427 | 0.063076 | 0.068432 | 0.0020037 | -0.00081187 | -0.00020717 | -0.078644 | 0.0029116 | 0.070461 | 0.067097 | -0.0036872 | 0.0067526 | -0.00035666 | -0.3067 | 63.6749 | -59.6603 | 63.4964 | -59.3216 | -59.7015 | -0.086975 | -0.52643 | 63.6566 | -59.4955 | 63.6246 | -59.4315 | -59.5688 | -59.285 | -0.21057 | 0.013733 | -0.1648 | 0.12817 | 59.3628 | -0.25177 | 59.5734 | -0.041199 | -0.045776 | -0.004578 | -0.036621 | 0.01831 | 0.16479 | -0.11902 | 0.21057 | -0.073243 | 0.33875 | 123.1567 | 0.064086 | 123.1201 | 123.3353 | 123.1522 | 123.1247 | 123.1064 | -123.3215 | -123.1567 | 122.9462 | 123.0743 | 59.1431 | 58.9233
605.8594 | 123.3124 | -59.4131 | 63.6108 | -0.094604 | 0.00086086 | 0.061795 | 0.065228 | 0.00093573 | -0.0014527 | -0.00042077 | -0.011505 | 0.00098899 | 0.066403 | 0.064961 | -0.004328 | 0.0063254 | -0.00057046 | -0.29755 | 63.6292 | -59.6283 | 63.5376 | -59.2392 | -59.6466 | -0.073242 | -0.50812 | 63.5971 | -59.4818 | 63.707 | -59.3491 | -59.491 | -59.2163 | -0.21515 | 0.01831 | -0.073242 | 0.17395 | 59.3399 | -0.23346 | 59.5551 | -0.01831 | -0.068665 | -0.013733 | 0.09613 | 0.064087 | 0.19684 | -0.07782 | 0.2655 | -0.009155 | 0.3891 | 123.1659 | 0.13275 | 123.1888 | 123.2574 | 123.0789 | 123.0423 | 123.0103 | -123.2391 | -123.0927 | 122.9507 | 123.1201 | 59.1156 | 58.905
606.8906 | 123.2803 | -59.4223 | 63.6063 | -0.13275 | 0.0027835 | 0.063717 | 0.066509 | 0.0034991 | -0.00059807 | -0.0029844 | 0.019012 | 0.0024844 | 0.06683 | 0.061115 | -0.0039008 | 0.0050436 | 0.00071134 | -0.33875 | 63.6063 | -59.6283 | 63.5239 | -59.2667 | -59.6878 | -0.10071 | -0.55389 | 63.5834 | -59.523 | 63.6749 | -59.3628 | -59.5047 | -59.2346 | -0.20599 | 0 | -0.082397 | 0.15564 | 59.3216 | -0.2655 | 59.5276 | -0.059509 | -0.10071 | -0.022888 | 0.068665 | 0.059509 | 0.18768 | -0.082398 | 0.28839 | 0.01831 | 0.36163 | 123.1522 | 0.16022 | 123.1979 | 123.2346 | 123.1064 | 123.0286 | 123.0057 | -123.2346 | -123.1293 | 122.9462 | 123.0972 | 59.0836 | 58.8684
607.8594 | 123.2529 | -59.4223 | 63.6063 | -0.064087 | 0.0023563 | 0.06564 | 0.067364 | 0.0047809 | 0.0017517 | -0.0023434 | -0.0054016 | 0.00163 | 0.067044 | 0.061115 | -0.0058234 | 0.0058982 | -0.0012113 | -0.32044 | 63.62 | -59.6466 | 63.5376 | -59.2804 | -59.6695 | -0.10986 | -0.53558 | 63.588 | -59.4864 | 63.6887 | -59.3719 | -59.4955 | -59.2209 | -0.2243 | 0.013733 | -0.068664 | 0.14191 | 59.3124 | -0.24719 | 59.5367 | -0.022889 | -0.064087 | -0.01831 | 0.082398 | 0.050354 | 0.20142 | -0.073242 | 0.2655 | -0.009155 | 0.36621 | 123.1842 | 0.11444 | 123.175 | 123.2666 | 123.0743 | 123.0423 | 123.0103 | -123.2529 | -123.0927 | 122.9599 | 123.111 | 59.1019 | 58.8867
608.9062 | 123.2346 | -59.4452 | 63.588 | -0.064087 | 0.00086086 | 0.062436 | 0.069286 | 0.00072213 | -0.0025207 | 6.432e-06 | -0.10916 | 0.0035526 | 0.067471 | 0.06432 | -0.0064642 | 0.00483 | -0.00057046 | -0.37537 | 63.6292 | -59.6832 | 63.4598 | -59.3674 | -59.7794 | -0.21057 | -0.63629 | 63.6017 | -59.5047 | 63.6292 | -59.4543 | -59.6054 | -59.3033 | -0.23804 | 0.041198 | -0.12817 | 0.077819 | 59.2346 | -0.33417 | 59.4727 | -0.09613 | -0.05951 | 0.013733 | 0.041198 | -0.009156 | 0.14191 | -0.16022 | 0.20142 | -0.10071 | 0.31586 | 123.143 | 0.050354 | 123.1338 | 123.3124 | 123.1064 | 123.0743 | 123.0469 | -123.2712 | -123.0927 | 122.905 | 123.0743 | 59.0698 | 58.8089
609.8594 | 123.3124 | -59.4177 | 63.5834 | -0.064087 | 0.0021427 | 0.062863 | 0.067577 | -0.00055967 | -0.00017087 | -0.0012754 | 0.0098572 | 0.0020572 | 0.067044 | 0.063893 | -0.006037 | 0.0069662 | -0.00078406 | -0.29755 | 63.6475 | -59.6237 | 63.5605 | -59.23 | -59.6191 | -0.041199 | -0.48981 | 63.5651 | -59.4681 | 63.7299 | -59.3353 | -59.4727 | -59.1888 | -0.20599 | 0.064087 | -0.022888 | 0.18768 | 59.3765 | -0.20142 | 59.5825 | 0.004577 | -0.050354 | -0.018311 | 0.14648 | 0.082398 | 0.22888 | -0.054931 | 0.27924 | -0.004577 | 0.39368 | 123.1842 | 0.13275 | 123.1979 | 123.2712 | 123.0331 | 123.0652 | 122.9828 | -123.2071 | -123.0515 | 122.9782 | 123.1476 | 59.1202 | 58.9279
610.8906 | 123.2895 | -59.4086 | 63.6246 | -0.064087 | 0.0023563 | 0.062008 | 0.065868 | -0.0018415 | -0.0027345 | -0.00084817 | -0.0084534 | 0.00056179 | 0.067684 | 0.066456 | -0.0058234 | 0.0044028 | 0.0017795 | -0.23346 | 63.6475 | -59.6008 | 63.6108 | -59.1614 | -59.5825 | 0.004578 | -0.39368 | 63.6337 | -59.4727 | 63.7115 | -59.317 | -59.4635 | -59.2026 | -0.19226 | 0.022888 | -0.013733 | 0.24719 | 59.4131 | -0.17395 | 59.6054 | 0.01831 | -0.064087 | 0.009155 | 0.086975 | 0.091552 | 0.20599 | -0.054932 | 0.27008 | 0.009155 | 0.43945 | 123.2117 | 0.15564 | 123.1842 | 123.2483 | 123.1064 | 123.056 | 123.0423 | -123.2254 | -123.0972 | 123.0194 | 123.1201 | 59.1751 | 59.0149
611.8594 | 123.2849 | -59.3994 | 63.6154 | -0.079346 | 0.00086086 | 0.063931 | 0.067577 | 0.00093573 | -0.00059807 | -0.0019162 | -0.0084534 | 0.0031254 | 0.068966 | 0.066456 | -0.0068914 | 0.0052572 | -0.00057046 | -0.31586 | 63.6566 | -59.6008 | 63.5605 | -59.2392 | -59.6329 | -0.07782 | -0.49896 | 63.6154 | -59.4818 | 63.7299 | -59.317 | -59.4589 | -59.2026 | -0.20142 | 0.041199 | -0.054931 | 0.16022 | 59.3216 | -0.23346 | 59.523 | -0.032044 | -0.082398 | 0 | 0.11444 | 0.082397 | 0.19684 | -0.059509 | 0.27924 | 0.022889 | 0.36163 | 123.1613 | 0.16479 | 123.2117 | 123.2574 | 123.0972 | 123.056 | 123.0148 | -123.2162 | -123.0972 | 122.9599 | 123.1293 | 59.0836 | 58.9005
612.8906 | 123.2529 | -59.4177 | 63.6017 | -0.071716 | 0.0027835 | 0.064358 | 0.06715 | 0.0022173 | -0.0025207 | 0.00043363 | -0.0084534 | 0.00098899 | 0.065975 | 0.066029 | -0.007105 | 0.0063254 | -0.0020657 | -0.31128 | 63.652 | -59.6237 | 63.5422 | -59.2758 | -59.6649 | -0.09613 | -0.54016 | 63.5971 | -59.4955 | 63.6887 | -59.3536 | -59.5093 | -59.2255 | -0.20599 | 0.050354 | -0.05951 | 0.14191 | 59.3216 | -0.24719 | 59.5276 | -0.041199 | -0.077819 | -0.004578 | 0.086975 | 0.064087 | 0.19226 | -0.091552 | 0.27008 | -0.013733 | 0.3479 | 123.1659 | 0.14191 | 123.1842 | 123.2758 | 123.0927 | 123.0698 | 123.0148 | -123.2254 | -123.0972 | 122.9599 | 123.1064 | 59.1064 | 58.8776
613.8594 | 123.175 | -59.4223 | 63.6658 | 0.042725 | 0.00064726 | 0.06329 | 0.068646 | -0.0012005 | -0.0016663 | -0.00042077 | -0.066437 | 0.00163 | 0.070461 | 0.067311 | -0.0075324 | 0.0061118 | -0.00014306 | -0.30212 | 63.707 | -59.6466 | 63.501 | -59.2987 | -59.6832 | -0.091553 | -0.54474 | 63.6612 | -59.4635 | 63.6429 | -59.4177 | -59.5688 | -59.285 | -0.2243 | 0.041199 | -0.16479 | 0.1236 | 59.3307 | -0.26093 | 59.5551 | -0.036622 | -0.041199 | -0.004577 | -0.022888 | 0.004577 | 0.13733 | -0.14648 | 0.17853 | -0.10529 | 0.3479 | 123.1476 | 0.045776 | 123.1064 | 123.3536 | 123.1247 | 123.1293 | 123.0835 | -123.3124 | -123.1293 | 122.9233 | 123.0652 | 59.1202 | 58.8776
614.8906 | 123.2941 | -59.404 | 63.6108 | -0.086975 | 0.0017155 | 0.062222 | 0.067364 | 0.0026447 | -0.0035889 | -0.0029844 | -0.078644 | 0.0031254 | 0.06683 | 0.066242 | -0.0064642 | 0.0078208 | -0.00035666 | -0.33875 | 63.6383 | -59.6375 | 63.5513 | -59.2484 | -59.6878 | 0.045776 | -0.54474 | 63.5925 | -59.4772 | 63.6841 | -59.3582 | -59.5047 | -59.23 | -0.23346 | 0.027466 | -0.059509 | 0.15564 | 59.4498 | -0.28381 | 59.6832 | -0.050354 | -0.073242 | -0.018311 | 0.073242 | 0.045777 | 0.17395 | -0.10071 | 0.24719 | -0.027466 | 0.3891 | 123.1888 | 0.11902 | 123.1613 | 123.2758 | 123.0698 | 123.0423 | 122.9965 | -123.2483 | -123.0881 | 122.9553 | 123.0881 | 59.0652 | 58.8593
615.8594 | 123.2803 | -59.4315 | 63.6246 | -0.056457 | 0.0023563 | 0.062008 | 0.066509 | 0.0037127 | -0.00038447 | 0.00022003 | 0.0098572 | 0.0018436 | 0.066189 | 0.066242 | -0.007105 | 0.006539 | 0.00049774 | -0.28839 | 63.6383 | -59.61 | 63.5788 | -59.2255 | -59.6054 | -0.054932 | -0.46692 | 63.6154 | -59.4589 | 63.7253 | -59.3079 | -59.4498 | -59.1888 | -0.17853 | 0.013733 | -0.045777 | 0.20599 | 59.3765 | -0.17395 | 59.5551 | 0.004577 | -0.027465 | -0.009156 | 0.10071 | 0.1236 | 0.24262 | -0.01831 | 0.27008 | 0.009155 | 0.38452 | 123.1888 | 0.15106 | 123.1842 | 123.2483 | 123.0743 | 123.0698 | 123.0469 | -123.2346 | -123.0835 | 123.0103 | 123.1567 | 59.1431 | 58.9645
616.9062 | 123.1888 | -59.4498 | 63.6429 | -0.048828 | 0.0017155 | 0.063076 | 0.069286 | 0.00050853 | -0.0010255 | -0.0021298 | -0.10306 | 0.0048344 | 0.06683 | 0.068165 | -0.007105 | 0.0076072 | 7.0538e-05 | -0.33417 | 63.6337 | -59.6603 | 63.5101 | -59.3079 | -59.7244 | -0.16937 | -0.60425 | 63.6337 | -59.5184 | 63.6429 | -59.4452 | -59.61 | -59.2896 | -0.21057 | -0.009155 | -0.13275 | 0.14191 | 59.2804 | -0.27466 | 59.491 | -0.064087 | -0.068665 | -0.009155 | 0 | 0.004578 | 0.16022 | -0.16022 | 0.22888 | -0.091552 | 0.35248 | 123.1705 | 0.073243 | 123.1613 | 123.2941 | 123.1522 | 123.0835 | 123.0835 | -123.3032 | -123.1613 | 122.9599 | 123.0927 | 59.1156 | 58.8455
617.8594 | 123.2849 | -59.3719 | 63.6063 | -0.094604 | 0.0010745 | 0.062649 | 0.068646 | -0.0020551 | 0.00025633 | -0.001489 | 0.0037536 | 0.00056179 | 0.067471 | 0.064106 | -0.0047552 | 0.0039756 | -0.00057046 | -0.3067 | 63.6658 | -59.6191 | 63.5696 | -59.23 | -59.6283 | -0.059509 | -0.49439 | 63.62 | -59.4727 | 63.7299 | -59.317 | -59.4543 | -59.1934 | -0.24719 | 0.059509 | -0.036621 | 0.14191 | 59.3124 | -0.25635 | 59.5596 | -0.009155 | -0.10071 | 0.013733 | 0.1236 | 0.054931 | 0.17853 | -0.082398 | 0.27924 | 0.01831 | 0.3891 | 123.1888 | 0.15564 | 123.2025 | 123.2849 | 123.0927 | 123.0377 | 122.9919 | -123.2254 | -123.0789 | 122.9416 | 123.1018 | 59.0652 | 58.8776
618.875 | 123.23 | -59.4269 | 63.6429 | -0.048828 | 0.0017155 | 0.062649 | 0.0695 | 0.0075579 | -0.0052979 | 0.00043363 | -0.10916 | 0.0046206 | 0.067898 | 0.067311 | -0.0062506 | 0.0084616 | 0.0011385 | -0.25635 | 63.6749 | -59.61 | 63.7299 | -59.2621 | -59.7473 | -0.032043 | -0.4303 | 63.6749 | -59.4818 | 63.7024 | -59.3582 | -59.5184 | -59.2621 | -0.18311 | 0.032044 | 0.086975 | 0.16479 | 59.3948 | -0.32043 | 59.5779 | -0.13733 | -0.054932 | 0.032044 | 0.05951 | 0.068665 | 0.16479 | -0.091553 | 0.21973 | -0.036621 | 0.3479 | 123.3398 | 0.1236 | 123.1842 | 123.2849 | 123.1567 | 123.1018 | 123.1018 | -123.2529 | -123.1247 | 123.1567 | 123.1293 | 59.1705 | 58.9966
619.8906 | 123.3124 | -59.3582 | 63.6246 | -0.048828 | 0.0032107 | 0.063504 | 0.066937 | 0.0024311 | -0.0020935 | 6.432e-06 | 0.012909 | 0.0039798 | 0.07153 | 0.066242 | -0.006037 | 0.0044028 | 0.00028414 | -0.26093 | 63.6566 | -59.6146 | 63.9587 | -59.0652 | -60.0128 | -0.013733 | -0.44403 | 63.5971 | -59.4772 | 63.7665 | -59.2438 | -59.3948 | -59.1385 | -0.25635 | 0.032043 | 0.33417 | 0.29297 | 59.3445 | -0.6546 | 59.6008 | -0.39825 | -0.11902 | -0.027466 | 0.14191 | 0.11444 | 0.21973 | -0.036621 | 0.33875 | 0.082398 | 0.54932 | 123.5733 | 0.23346 | 123.2437 | 123.2712 | 123.0743 | 123.0148 | 122.9553 | -123.2391 | -123.1018 | 123.317 | 123.1247 | 59.0973 | 58.9142
620.8594 | 123.3124 | -59.3765 | 63.6337 | -0.01831 | -0.00042094 | 0.06094 | 0.06245 | 0.00050853 | 0.0017517 | -0.004266 | 0.015961 | 0.0024844 | 0.065762 | 0.062824 | -0.006037 | 0.00483 | 0.0015659 | -0.26093 | 63.6612 | -59.5963 | 63.5742 | -58.992 | -59.7427 | -0.068665 | -0.42572 | 63.6017 | -59.4543 | 63.7665 | -59.2529 | -59.3811 | -59.1568 | -0.21973 | 0.027466 | -0.059509 | 0.38452 | 59.3079 | -0.36621 | 59.5276 | -0.14648 | -0.07782 | -0.032043 | 0.13275 | 0.1236 | 0.21973 | -0.004578 | 0.29755 | 0.073242 | 0.60425 | 123.1705 | 0.20142 | 123.2208 | 123.2574 | 123.056 | 123.0377 | 122.9782 | -123.23 | -123.0881 | 122.9507 | 123.143 | 59.1156 | 58.9508
621.9062 | 123.2117 | -59.4315 | 63.652 | -0.041199 | 0.0034245 | 0.062649 | 0.069286 | 0.0043537 | -0.0023071 | -0.00020717 | -0.078644 | 0.002698 | 0.068539 | 0.073719 | -0.0092414 | 0.0058982 | -0.0018521 | -0.26093 | 63.6841 | -59.6283 | 63.5742 | -59.166 | -59.8984 | -0.059509 | -0.49439 | 63.6703 | -59.491 | 63.6749 | -59.3491 | -59.5459 | -59.23 | -0.19684 | 0.032043 | -0.07782 | 0.2655 | 59.3719 | -0.46692 | 59.5688 | -0.27008 | -0.059509 | 0.01831 | 0.022888 | 0.082398 | 0.20142 | -0.11444 | 0.26093 | -0.054931 | 0.46234 | 123.2025 | 0.14191 | 123.1659 | 123.3124 | 123.1613 | 123.1155 | 123.1018 | -123.2803 | -123.143 | 123.0057 | 123.1064 | 59.1705 | 58.9371
622.8594 | 123.3078 | -59.3857 | 63.6566 | -0.071716 | 0.0012881 | 0.061367 | 0.067577 | 0.0026447 | -0.0010255 | -0.00084817 | 0.012909 | -0.00029261 | 0.068966 | 0.069233 | -0.0058234 | 0.006539 | -0.0031339 | -0.23346 | 63.6658 | -59.5917 | 63.652 | -59.1156 | -59.5413 | -0.009155 | -0.37994 | 63.6246 | -59.4315 | 63.7711 | -59.2438 | -59.3811 | -59.1476 | -0.20599 | 0.009155 | -0.004577 | 0.27008 | 59.3765 | -0.15564 | 59.5825 | 0.050354 | -0.045777 | -0.032043 | 0.11444 | 0.14191 | 0.23804 | 0.004577 | 0.28381 | 0.050354 | 0.47607 | 123.2437 | 0.18768 | 123.2025 | 123.2574 | 123.056 | 123.0515 | 123.0103 | -123.2483 | -123.0881 | 123.0377 | 123.1567 | 59.1522 | 59.0057
623.875 | 123.2529 | -59.3536 | 63.6566 | -0.079346 | 0.0015019 | 0.06329 | 0.065868 | -0.0024823 | -0.00059807 | -0.002557 | -0.0054016 | 0.0029116 | 0.067898 | 0.061543 | -0.0064642 | 0.0054708 | 0.0017795 | -0.23346 | 63.652 | -59.5825 | 63.6566 | -59.1522 | -59.5551 | 0.009155 | -0.39368 | 63.6566 | -59.4269 | 63.7436 | -59.2896 | -59.436 | -59.1888 | -0.22888 | -0.004577 | 0 | 0.20142 | 59.3628 | -0.20142 | 59.5917 | 0.027466 | -0.073242 | 0 | 0.086975 | 0.064087 | 0.16479 | -0.082397 | 0.23804 | -0.009155 | 0.4303 | 123.2391 | 0.13733 | 123.1705 | 123.2346 | 123.0835 | 123.0057 | 123.0103 | -123.2391 | -123.0835 | 123.0103 | 123.0972 | 59.1202 | 58.96
624.8906 | 123.1934 | -59.3903 | 63.6887 | -0.094604 | 0.00086086 | 0.059659 | 0.066723 | 0.00072213 | -0.0012391 | -0.0012754 | -0.051178 | 0.00163 | 0.069393 | 0.063893 | -0.0066778 | 0.0061118 | 0.00092494 | -0.26093 | 63.7161 | -59.61 | 63.533 | -59.2575 | -59.6375 | -0.073242 | -0.52185 | 63.6703 | -59.4772 | 63.6612 | -59.3811 | -59.5459 | -59.2896 | -0.21973 | 0.027465 | -0.15564 | 0.13275 | 59.317 | -0.24719 | 59.5367 | -0.027466 | -0.086975 | -0.018311 | -0.027466 | 0.009155 | 0.10071 | -0.15564 | 0.18768 | -0.068664 | 0.35248 | 123.143 | 0.09613 | 123.1384 | 123.3261 | 123.1476 | 123.1064 | 123.0606 | -123.2986 | -123.1659 | 122.9233 | 123.0515 | 59.1293 | 58.8684
625.8594 | 123.2574 | -59.404 | 63.6292 | -0.041199 | 0.00043366 | 0.06329 | 0.068218 | 0.0015765 | -0.00017087 | -0.0038388 | -0.0023498 | 0.0029116 | 0.068539 | 0.06197 | -0.0051824 | 0.006539 | -0.0044157 | -0.36163 | 63.652 | -59.61 | 63.5468 | -59.2529 | -59.6512 | -0.11902 | -0.55389 | 63.6108 | -59.4543 | 63.6795 | -59.3445 | -59.4955 | -59.2117 | -0.20599 | 0.022889 | -0.082397 | 0.15106 | 59.285 | -0.24719 | 59.491 | -0.041199 | -0.050354 | -0.01831 | 0.050354 | 0.05951 | 0.19226 | -0.091552 | 0.24262 | -0.041198 | 0.35706 | 123.1567 | 0.10986 | 123.1338 | 123.262 | 123.0652 | 123.056 | 123.0148 | -123.2391 | -123.0835 | 122.9507 | 123.0835 | 59.0424 | 58.8501
626.9062 | 123.2254 | -59.3857 | 63.6658 | -0.048828 | 0.0012881 | 0.063931 | 0.068859 | -0.00098687 | -0.0012391 | -0.0010618 | -0.075592 | 0.0039798 | 0.070248 | 0.068592 | -0.0062506 | 0.0061118 | -0.00057046 | -0.28381 | 63.707 | -59.61 | 63.5605 | -59.2484 | -59.6329 | -0.07782 | -0.49439 | 63.6978 | -59.4635 | 63.7024 | -59.3353 | -59.5093 | -59.23 | -0.2243 | 0.041199 | -0.10529 | 0.13733 | 59.3079 | -0.24719 | 59.5322 | -0.022889 | -0.07782 | 0.032044 | 0.036622 | 0.050354 | 0.15564 | -0.1236 | 0.23346 | -0.045776 | 0.36163 | 123.1705 | 0.12817 | 123.1659 | 123.317 | 123.1613 | 123.0927 | 123.0835 | -123.2758 | -123.1293 | 122.9462 | 123.0881 | 59.1019 | 58.8913
627.8594 | 123.2758 | -59.4086 | 63.62 | -0.086975 | 0.0015019 | 0.064145 | 0.068218 | -0.00013247 | 0.00046993 | 6.432e-06 | -0.017609 | 0.0024844 | 0.069821 | 0.061329 | -0.007105 | 0.0073936 | -0.0016385 | -0.34332 | 63.6246 | -59.6237 | 63.5605 | -59.2392 | -59.6466 | -0.13275 | -0.47607 | 63.6429 | -59.4681 | 63.6566 | -59.3262 | -59.5322 | -59.2392 | -0.21515 | 0.004578 | -0.059509 | 0.16937 | 59.2758 | -0.23804 | 59.491 | -0.022888 | -0.05951 | 0.022888 | 0.036621 | 0.082397 | 0.16937 | -0.1236 | 0.22888 | -0.064087 | 0.38452 | 123.1842 | 0.14191 | 123.1247 | 123.2483 | 123.111 | 123.0331 | 123.0515 | -123.2437 | -123.0881 | 122.9691 | 123.0652 | 59.0652 | 58.9325
628.8906 | 123.2254 | -59.404 | 63.6932 | -0.02594 | 0.0021427 | 0.061367 | 0.068005 | -0.00034607 | -0.0010255 | 0.00022003 | -0.051178 | 0.002698 | 0.066616 | 0.070728 | -0.0062506 | 0.0076072 | -0.00035666 | -0.30212 | 63.7207 | -59.6191 | 63.5284 | -59.2896 | -59.6512 | -0.091553 | -0.53558 | 63.6841 | -59.4543 | 63.6612 | -59.3811 | -59.5322 | -59.2392 | -0.21515 | 0.027466 | -0.1648 | 0.11444 | 59.3124 | -0.24719 | 59.5276 | -0.032043 | -0.050354 | -0.009155 | -0.032043 | 0.022888 | 0.1648 | -0.12817 | 0.21515 | -0.07782 | 0.32959 | 123.1476 | 0.073242 | 123.1155 | 123.3398 | 123.1384 | 123.1247 | 123.0881 | -123.3124 | -123.1476 | 122.9324 | 123.0652 | 59.1019 | 58.8684
629.8594 | 123.2986 | -59.3903 | 63.6383 | -0.041199 | 0.00022006 | 0.061795 | 0.066937 | 0.0015765 | -0.0012391 | -0.0044796 | 0.012909 | 0.0024844 | 0.06918 | 0.061329 | -0.006037 | 0.00483 | 0.0011385 | -0.20599 | 63.707 | -59.5825 | 63.5696 | -59.2392 | -59.6786 | -0.12817 | -0.55847 | 63.6246 | -59.4727 | 63.6887 | -59.3536 | -59.5047 | -59.2163 | -0.19226 | 0.068664 | -0.068665 | 0.15106 | 59.2621 | -0.28839 | 59.4543 | -0.09613 | -0.082397 | -0.013733 | 0.050354 | 0.036621 | 0.17395 | -0.11444 | 0.25635 | -0.032044 | 0.34332 | 123.1522 | 0.11902 | 123.1613 | 123.2895 | 123.0972 | 123.0972 | 123.0148 | -123.2208 | -123.111 | 122.9599 | 123.0789 | 59.1843 | 58.8318
630.9062 | 123.1979 | -59.3857 | 63.7024 | -0.02594 | -0.00020714 | 0.062008 | 0.068432 | 0.00072213 | -0.0027345 | -0.00063437 | -0.063385 | 0.004407 | 0.068325 | 0.065815 | -0.006037 | 0.0073936 | -0.0035611 | -0.28381 | 63.7207 | -59.5963 | 63.5376 | -59.2804 | -59.6375 | -0.091553 | -0.53101 | 63.6932 | -59.4589 | 63.6749 | -59.3765 | -59.5413 | -59.2575 | -0.21057 | 0.01831 | -0.16479 | 0.10528 | 59.2941 | -0.25177 | 59.5047 | -0.041199 | -0.073242 | -0.009156 | -0.027466 | 0.009155 | 0.12817 | -0.15564 | 0.20142 | -0.082398 | 0.31586 | 123.1338 | 0.082397 | 123.1338 | 123.317 | 123.1522 | 123.1064 | 123.0789 | -123.2986 | -123.1613 | 122.9233 | 123.0606 | 59.1019 | 58.8547
631.8594 | 123.2941 | -59.3811 | 63.6337 | -0.048828 | -0.00020714 | 0.062649 | 0.067364 | 0.0013629 | -0.0027345 | -0.001489 | 0.03122 | 0.0024844 | 0.067898 | 0.066456 | -0.0047552 | 0.0054708 | -0.00035666 | -0.3067 | 63.6612 | -59.6054 | 63.5925 | -59.198 | -59.5871 | -0.054932 | -0.48981 | 63.6383 | -59.4498 | 63.7573 | -59.285 | -59.4086 | -59.1385 | -0.2243 | 0.027466 | -0.041199 | 0.18311 | 59.3262 | -0.20599 | 59.5505 | 0.018311 | -0.068664 | 0.004578 | 0.1236 | 0.096131 | 0.24262 | -0.027465 | 0.31128 | 0.041199 | 0.40741 | 123.1979 | 0.16479 | 123.2071 | 123.2666 | 123.0881 | 123.0423 | 123.0194 | -123.2391 | -123.0835 | 122.9736 | 123.1384 | 59.0744 | 58.8913
632.8906 | 123.2758 | -59.3994 | 63.6292 | -0.10986 | 0.0036381 | 0.06329 | 0.066509 | 0.0026447 | -0.00017087 | -0.001489 | -0.060333 | 0.0014164 | 0.066403 | 0.064106 | -0.0083868 | 0.0067526 | -0.0033475 | -0.29297 | 63.6475 | -59.5825 | 63.6154 | -59.1843 | -59.6008 | -0.10986 | -0.49439 | 63.6108 | -59.4543 | 63.7482 | -59.2941 | -59.4635 | -59.1797 | -0.18311 | 0.018311 | -0.013733 | 0.21515 | 59.2896 | -0.20142 | 59.4727 | -0.01831 | -0.054932 | -0.01831 | 0.11902 | 0.10529 | 0.21973 | -0.064087 | 0.27466 | -0.009155 | 0.39825 | 123.1979 | 0.16022 | 123.2025 | 123.23 | 123.0652 | 123.0469 | 123.0103 | -123.2117 | -123.0835 | 123.0148 | 123.1476 | 59.1064 | 58.905
633.8594 | 123.317 | -59.3857 | 63.6108 | -0.11749 | 0.0029971 | 0.062649 | 0.068005 | 0.00093573 | -0.00081187 | -0.00063437 | -0.029816 | -0.00029261 | 0.067257 | 0.066242 | -0.0068914 | 0.008248 | -0.0024931 | -0.29297 | 63.652 | -59.6237 | 63.6063 | -59.1568 | -59.6375 | -0.12817 | -0.50812 | 63.62 | -59.4727 | 63.7573 | -59.2987 | -59.4498 | -59.1568 | -0.23804 | 0.041199 | -0.004578 | 0.22888 | 59.2575 | -0.25177 | 59.4955 | -0.013733 | -0.086975 | 0.009155 | 0.14648 | 0.086975 | 0.22888 | -0.064087 | 0.31586 | 0.022888 | 0.46692 | 123.23 | 0.17395 | 123.23 | 123.2758 | 123.0927 | 123.0377 | 123.0057 | -123.2346 | -123.0835 | 122.9919 | 123.143 | 59.0927 | 58.8776
634.8906 | 123.3032 | -59.3536 | 63.6063 | -0.094604 | 0.0023563 | 0.06329 | 0.066723 | 0.0013629 | -0.0027345 | -0.00063437 | -0.017609 | 0.002698 | 0.066616 | 0.058552 | -0.0075324 | 0.0046164 | -0.0012113 | -0.30212 | 63.6337 | -59.5688 | 63.6154 | -59.1797 | -59.6008 | -0.10071 | -0.50812 | 63.6154 | -59.4543 | 63.7527 | -59.2941 | -59.4589 | -59.1568 | -0.21515 | 0.027466 | 0.009155 | 0.17395 | 59.2529 | -0.24719 | 59.4681 | -0.032043 | -0.10071 | 0.009155 | 0.14648 | 0.05951 | 0.19684 | -0.10529 | 0.29755 | -0.004577 | 0.3891 | 123.1842 | 0.16022 | 123.2071 | 123.2025 | 123.0698 | 122.9874 | 122.9691 | -123.175 | -123.0606 | 122.9691 | 123.1064 | 59.0515 | 58.8455
635.8594 | 123.23 | -59.3948 | 63.6703 | -0.094604 | 0.0015019 | 0.062222 | 0.068859 | 0.0011493 | -0.00038447 | -0.0021298 | -0.023712 | 0.0029116 | 0.068539 | 0.05962 | -0.006037 | 0.0033346 | -0.00099766 | -0.32501 | 63.6658 | -59.61 | 63.5788 | -59.2072 | -59.6237 | -0.10986 | -0.56305 | 63.6292 | -59.4635 | 63.7573 | -59.3994 | -59.491 | -59.2072 | -0.21515 | -0.004578 | -0.091553 | 0.18768 | 59.285 | -0.22888 | 59.5001 | -0.013733 | -0.068665 | -0.041199 | 0.086975 | -0.004578 | 0.18768 | -0.096131 | 0.25635 | -0.027466 | 0.40283 | 123.1888 | 0.064087 | 123.2208 | 123.2758 | 123.0927 | 123.0606 | 123.024 | -123.2803 | -123.1338 | 122.9736 | 123.1522 | 59.0698 | 58.8318
636.9062 | 123.2529 | -59.3811 | 63.6658 | -0.086975 | 0.0021427 | 0.061154 | 0.067577 | 0.0039263 | 0.00025633 | -0.00020717 | -0.084747 | 0.0029116 | 0.065335 | 0.070728 | -0.0081732 | 0.0052572 | -0.0024931 | -0.27466 | 63.7024 | -59.6146 | 63.5925 | -59.1934 | -59.6283 | -0.091553 | -0.48981 | 63.6887 | -59.436 | 63.7253 | -59.3445 | -59.5047 | -59.2026 | -0.23346 | 0.036622 | -0.073242 | 0.18768 | 59.2896 | -0.24719 | 59.523 | -0.013733 | -0.054931 | 0.022889 | 0.05951 | 0.036622 | 0.17853 | -0.1236 | 0.23346 | -0.068665 | 0.42114 | 123.2071 | 0.091553 | 123.1613 | 123.317 | 123.1247 | 123.0835 | 123.0698 | -123.2803 | -123.1018 | 122.9736 | 123.1064 | 59.1064 | 58.8913
637.8594 | 123.2574 | -59.3948 | 63.6246 | -0.086975 | -0.00020714 | 0.063076 | 0.067577 | 0.0045673 | -0.0025207 | -0.00042077 | -0.057281 | 0.0029116 | 0.067898 | 0.067311 | -0.0047552 | 0.006539 | 0.0013521 | -0.29755 | 63.6566 | -59.5825 | 63.5971 | -59.1705 | -59.6191 | -0.09613 | -0.52643 | 63.6246 | -59.4589 | 63.739 | -59.3262 | -59.4864 | -59.1888 | -0.18768 | 0.032043 | -0.027466 | 0.2243 | 59.2987 | -0.22431 | 59.4864 | -0.036621 | -0.064087 | 0 | 0.11444 | 0.068664 | 0.20599 | -0.091553 | 0.27008 | -0.027466 | 0.41199 | 123.1796 | 0.13275 | 123.1979 | 123.2391 | 123.0835 | 123.0515 | 123.0194 | -123.2071 | -123.0835 | 122.9919 | 123.1338 | 59.0973 | 58.8684
638.8906 | 123.2529 | -59.3948 | 63.6063 | -0.079346 | 0.0032107 | 0.064358 | 0.066937 | -0.00077327 | -0.0020935 | -0.00084817 | 0.00070198 | 0.00056179 | 0.066189 | 0.063893 | -0.0064642 | 0.0046164 | 0.0032749 | -0.32501 | 63.6978 | -59.5642 | 63.5696 | -59.2072 | -59.6375 | -0.10071 | -0.56305 | 63.652 | -59.4315 | 63.7482 | -59.3216 | -59.4772 | -59.1843 | -0.16937 | 0.091553 | -0.036621 | 0.18768 | 59.2941 | -0.24262 | 59.4635 | -0.073242 | -0.036622 | 0.045777 | 0.14191 | 0.073242 | 0.21057 | -0.082398 | 0.24719 | -0.045776 | 0.35706 | 123.1338 | 0.10986 | 123.1796 | 123.262 | 123.0835 | 123.0927 | 123.0469 | -123.1705 | -123.0377 | 122.9645 | 123.143 | 59.0698 | 58.8318
639.8594 | 123.2895 | -59.3674 | 63.62 | -0.16327 | 0.0015019 | 0.06329 | 0.066509 | 0.00093573 | -0.0014527 | 6.432e-06 | -0.035919 | 0.00098899 | 0.067044 | 0.063679 | -0.007105 | 0.0069662 | 0.00071134 | -0.30212 | 63.6383 | -59.5505 | 63.62 | -59.1522 | -59.6008 | -0.10986 | -0.48981 | 63.6246 | -59.4543 | 63.7527 | -59.3033 | -59.4589 | -59.166 | -0.18311 | 0.018311 | 0 | 0.21515 | 59.2575 | -0.23346 | 59.4406 | -0.050354 | -0.086975 | 0.004578 | 0.13275 | 0.064087 | 0.20142 | -0.091552 | 0.28839 | -0.004577 | 0.39825 | 123.1705 | 0.15106 | 123.2071 | 123.1888 | 123.0789 | 123.0057 | 122.9919 | -123.1705 | -123.0743 | 122.9874 | 123.1201 | 59.0652 | 58.8776
640.8906 | 123.2941 | -59.3628 | 63.6612 | -0.01831 | 0.00086086 | 0.06329 | 0.068005 | -0.00034607 | -0.00059807 | -0.0021298 | 0.0037536 | -0.00050621 | 0.066616 | 0.057484 | -0.007746 | 0.0063254 | -0.00057046 | -0.30212 | 63.707 | -59.5688 | 63.5971 | -59.198 | -59.6008 | -0.086975 | -0.52185 | 63.6703 | -59.4269 | 63.7482 | -59.2758 | -59.404 | -59.1614 | -0.20599 | 0.045776 | -0.064087 | 0.1648 | 59.2758 | -0.23804 | 59.4818 | -0.032043 | -0.064087 | 0.009155 | 0.086975 | 0.086975 | 0.20142 | -0.041199 | 0.2655 | 0.022888 | 0.37079 | 123.1659 | 0.15106 | 123.175 | 123.2758 | 123.0972 | 123.0698 | 123.0331 | -123.23 | -123.0881 | 122.9599 | 123.111 | 59.0607 | 58.8409
641.8594 | 123.2666 | -59.3491 | 63.6429 | -0.071716 | 6.46e-06 | 0.062436 | 0.066509 | 0.00072213 | -0.0023071 | -0.0027708 | -0.011505 | 0.0029116 | 0.067471 | 0.054066 | -0.009455 | 0.0086752 | -0.0016385 | -0.28381 | 63.7344 | -59.5825 | 63.6475 | -59.1431 | -59.5505 | -0.027466 | -0.40283 | 63.6429 | -59.4131 | 63.5788 | -59.2117 | -59.3399 | -59.1431 | -0.23346 | 0.091553 | 0.004578 | 0.20599 | 59.3216 | -0.20142 | 59.5551 | 0.032044 | -0.064087 | 0 | -0.064087 | 0.13733 | 0.20599 | 0.009155 | 0.27008 | 0.073242 | 0.43945 | 123.23 | 0.20142 | 122.9919 | 123.317 | 123.056 | 123.0835 | 122.9919 | -123.2254 | -123.056 | 122.9965 | 122.9279 | 59.0652 | 58.9462
642.8906 | 123.2941 | -59.3536 | 63.6475 | -0.056457 | 0.0017155 | 0.061367 | 0.066937 | -0.0018415 | -0.0029481 | 0.00022003 | 0.00070198 | 0.0018436 | 0.068112 | 0.070301 | -0.0066778 | 0.0050436 | 0.0019931 | -0.28839 | 63.7024 | -59.5642 | 63.6292 | -59.166 | -59.5642 | -0.041199 | -0.44861 | 63.6566 | -59.4086 | 63.7939 | -59.2621 | -59.404 | -59.1248 | -0.21057 | 0.054932 | -0.018311 | 0.18768 | 59.3124 | -0.21057 | 59.523 | 0 | -0.054931 | 0.009155 | 0.14648 | 0.091553 | 0.22888 | -0.050354 | 0.28381 | 0.004577 | 0.39825 | 123.1934 | 0.14648 | 123.2025 | 123.2666 | 123.0652 | 123.056 | 123.0103 | -123.2117 | -123.056 | 122.9828 | 123.1476 | 59.0652 | 58.905
643.8594 | 123.2666 | -59.3628 | 63.6475 | -0.094604 | 0.0015019 | 0.06329 | 0.066723 | 0.0017901 | -0.00059807 | -0.0017026 | -0.063385 | 0.0031254 | 0.068112 | 0.062824 | -0.0081732 | 0.0063254 | -0.00014306 | -0.29755 | 63.6841 | -59.5596 | 63.6337 | -59.1431 | -59.5871 | -0.10986 | -0.50812 | 63.6429 | -59.4315 | 63.7527 | -59.2987 | -59.4498 | -59.166 | -0.19684 | 0.036621 | -0.013733 | 0.21973 | 59.2529 | -0.2243 | 59.4498 | -0.027466 | -0.068665 | -0.004578 | 0.10529 | 0.064087 | 0.19684 | -0.086975 | 0.2655 | -0.01831 | 0.41657 | 123.1934 | 0.13275 | 123.1842 | 123.2437 | 123.0743 | 123.0469 | 123.0057 | -123.2071 | -123.0789 | 122.9965 | 123.1155 | 59.0652 | 58.8547
644.8906 | 123.2895 | -59.3353 | 63.6841 | -0.056457 | 0.00064726 | 0.063504 | 0.06715 | -0.0026959 | -0.00081187 | -0.003198 | 0.00070198 | 0.0035526 | 0.067684 | 0.059834 | -0.0068914 | 0.0039756 | 7.0538e-05 | -0.3067 | 63.7024 | -59.5779 | 63.6292 | -59.1751 | -59.5779 | -0.064087 | -0.47607 | 63.6841 | -59.4177 | 63.7756 | -59.2621 | -59.4086 | -59.1522 | -0.24262 | 0.018311 | -0.054932 | 0.16022 | 59.2712 | -0.24262 | 59.5139 | 0 | -0.082398 | 0 | 0.091553 | 0.073242 | 0.1831 | -0.073242 | 0.2655 | 0.009156 | 0.40283 | 123.2071 | 0.15564 | 123.1934 | 123.2803 | 123.1018 | 123.0377 | 123.0194 | -123.262 | -123.1018 | 122.9645 | 123.111 | 59.0286 | 58.8593
645.8594 | 123.2758 | -59.3674 | 63.6246 | -0.12512 | 0.0032107 | 0.06329 | 0.068218 | 0.0013629 | -0.00038447 | 0.00043363 | -0.048126 | 0.0018436 | 0.068539 | 0.064106 | -0.0066778 | 0.0058982 | 0.00092494 | -0.28839 | 63.6612 | -59.5779 | 63.6337 | -59.1476 | -59.5734 | -0.10529 | -0.49896 | 63.6703 | -59.4269 | 63.7848 | -59.2987 | -59.4452 | -59.1476 | -0.21057 | 0.036621 | 0.009155 | 0.21973 | 59.2621 | -0.20599 | 59.4727 | 0.004578 | -0.059509 | 0.045776 | 0.16022 | 0.068665 | 0.21973 | -0.077819 | 0.27924 | -0.01831 | 0.4303 | 123.2117 | 0.12817 | 123.2117 | 123.2391 | 123.0972 | 123.0286 | 123.0377 | -123.2025 | -123.0515 | 123.0011 | 123.1522 | 59.079 | 58.8684
646.9062 | 123.3078 | -59.3033 | 63.6292 | -0.094604 | 0.0040653 | 0.062863 | 0.066509 | 0.0013629 | -0.0018799 | -0.0019162 | -0.02066 | 0.0018436 | 0.067257 | 0.059406 | -0.0056098 | 0.00483 | -0.0014249 | -0.26093 | 63.7161 | -59.5459 | 63.6612 | -59.1248 | -59.5367 | -0.022888 | -0.4303 | 63.6703 | -59.3994 | 63.8168 | -59.3628 | -58.8181 | -58.7311 | -0.24261 | 0.086975 | 0.032044 | 0.17853 | 59.2804 | -0.23346 | 59.523 | 0.009155 | -0.09613 | 0.041199 | 0.18768 | -0.059509 | 0.5722 | 0.48523 | 0.66833 | 0.58136 | 0.42114 | 123.2071 | 0.036621 | 123.2162 | 123.262 | 123.0698 | 123.0194 | 122.9736 | -123.175 | -123.0286 | 122.9645 | 123.1201 | 59.0424 | 58.873
647.8594 | 123.3124 | -59.3353 | 63.6429 | -0.056457 | 0.0027835 | 0.064999 | 0.068218 | 0.00029473 | -0.0014527 | -0.0046934 | -0.084747 | 0.0039798 | 0.065335 | 0.067951 | -0.0066778 | 0.006539 | -0.0031339 | -0.43945 | 63.6154 | -59.5871 | 63.6292 | -59.1797 | -59.5596 | -0.10986 | -0.48981 | 63.6566 | -59.4269 | 63.7848 | -59.2667 | -59.4223 | -59.1202 | -0.25177 | -0.027466 | -0.013733 | 0.15564 | 59.2255 | -0.2243 | 59.4772 | 0.027466 | -0.091553 | 0.013733 | 0.14191 | 0.068664 | 0.21515 | -0.086975 | 0.3067 | 0.004578 | 0.40741 | 123.2162 | 0.16022 | 123.2117 | 123.2025 | 123.0835 | 122.9507 | 122.9919 | -123.23 | -123.0698 | 122.9645 | 123.1201 | 58.8959 | 58.8455
648.8906 | 123.2941 | -59.3445 | 63.6658 | -0.086975 | 0.0017155 | 0.063504 | 0.064587 | 0.0011493 | 0.0023925 | -0.0027708 | -0.0054016 | 0.0014164 | 0.068325 | 0.060688 | -0.0066778 | 0.0061118 | 0.0019931 | -0.28839 | 63.7024 | -59.5459 | 63.6292 | -59.1476 | -59.5505 | -0.045776 | -0.4715 | 63.6841 | -59.4131 | 63.8031 | -59.2209 | -59.3948 | -59.1156 | -0.20142 | 0.036622 | -0.036621 | 0.19684 | 59.2987 | -0.20599 | 59.5001 | -0.004578 | -0.068665 | 0.018311 | 0.13733 | 0.1236 | 0.22888 | -0.050354 | 0.29755 | 0.018311 | 0.39825 | 123.175 | 0.19226 | 123.2162 | 123.2483 | 123.0972 | 123.0469 | 123.0286 | -123.2117 | -123.0789 | 122.9736 | 123.1476 | 59.0561 | 58.873
649.8594 | 123.2483 | -59.3216 | 63.6658 | -0.10986 | 0.0036381 | 0.063717 | 0.066937 | 0.00050853 | -0.0014527 | -0.0021298 | -0.045074 | 0.002698 | 0.067898 | 0.06197 | -0.0064642 | 0.0058982 | -0.0016385 | -0.29755 | 63.6795 | -59.5596 | 63.652 | -59.1431 | -59.5825 | -0.11444 | -0.48981 | 63.6612 | -59.4315 | 63.7802 | -59.285 | -59.436 | -59.1614 | -0.23804 | 0.013733 | -0.013732 | 0.17853 | 59.2072 | -0.26093 | 59.4452 | -0.022889 | -0.10986 | -0.004577 | 0.11444 | 0.036621 | 0.16022 | -0.11444 | 0.27008 | -0.004577 | 0.41657 | 123.2117 | 0.14648 | 123.2117 | 123.2391 | 123.0927 | 123.0011 | 122.9828 | -123.2254 | -123.0972 | 122.9736 | 123.1018 | 59.024 | 58.8318
650.8906 | 123.262 | -59.3308 | 63.6429 | -0.10986 | 0.0036381 | 0.063076 | 0.067364 | 0.00072213 | -0.0010255 | -0.00063437 | -0.060333 | -7.901e-05 | 0.065762 | 0.065388 | -0.006037 | 0.0054708 | -0.0048429 | -0.3067 | 63.6566 | -59.5551 | 63.6475 | -59.1248 | -59.5917 | -0.10529 | -0.48981 | 63.652 | -59.4315 | 63.7985 | -59.2621 | -59.4315 | -59.1293 | -0.2243 | 0.013733 | 0.004578 | 0.20599 | 59.2255 | -0.26093 | 59.4498 | -0.036621 | -0.10071 | 0.009156 | 0.15564 | 0.068665 | 0.20142 | -0.10071 | 0.30212 | 0 | 0.4303 | 123.2025 | 0.16937 | 123.23 | 123.2117 | 123.0835 | 122.9874 | 122.9828 | -123.1979 | -123.0743 | 122.9782 | 123.1293 | 59.024 | 58.8409
651.8594 | 123.2803 | -59.3308 | 63.6932 | -0.12512 | 0.0010745 | 0.063717 | 0.06715 | -0.0012005 | -0.0027345 | -0.002557 | -0.029816 | 0.00163 | 0.067044 | 0.067097 | -0.0066778 | 0.00483 | -0.0035611 | -0.32501 | 63.6795 | -59.5642 | 63.5971 | -59.1797 | -59.61 | -0.14191 | -0.55389 | 63.652 | -59.4269 | 63.826 | -59.3445 | -59.5184 | -59.1888 | -0.23346 | -0.013733 | -0.09613 | 0.15106 | 59.1888 | -0.27923 | 59.4223 | -0.045776 | -0.09613 | -0.041198 | 0.13275 | -0.013732 | 0.14191 | -0.18768 | 0.23804 | -0.091553 | 0.38452 | 123.1613 | 0.082398 | 123.2529 | 123.2437 | 123.0789 | 123.0103 | 122.9828 | -123.2574 | -123.1201 | 122.9279 | 123.1567 | 59.0057 | 58.7769
652.8906 | 123.2574 | -59.3445 | 63.6749 | -0.071716 | 0.0019291 | 0.063931 | 0.065868 | -0.0022687 | -0.0027345 | -0.00084817 | -0.02066 | 0.00098899 | 0.067471 | 0.062397 | -0.0047552 | 0.006539 | 0.00049774 | -0.3067 | 63.7253 | -59.5505 | 63.6292 | -59.1522 | -59.5917 | -0.073242 | -0.51727 | 63.6703 | -59.4315 | 63.7756 | -59.2575 | -59.3994 | -59.1293 | -0.20599 | 0.050354 | -0.045777 | 0.19226 | 59.2712 | -0.24719 | 59.4772 | -0.041199 | -0.086976 | -0.004578 | 0.10071 | 0.086975 | 0.21515 | -0.054932 | 0.30212 | 0.032044 | 0.39825 | 123.1796 | 0.17395 | 123.2071 | 123.2758 | 123.1018 | 123.0698 | 123.0148 | -123.2254 | -123.1064 | 122.9736 | 123.1201 | 59.0378 | 58.8272
653.8594 | 123.317 | -59.3308 | 63.6749 | -0.071716 | 0.0017155 | 0.064145 | 0.065868 | 0.0015765 | -0.00081187 | -0.0021298 | -0.060333 | 0.0020572 | 0.067684 | 0.066242 | -0.0073188 | 0.006539 | 0.0013521 | -0.28839 | 63.6887 | -59.5734 | 63.6292 | -59.1248 | -59.5825 | -0.10529 | -0.49896 | 63.6612 | -59.4223 | 63.8077 | -59.2484 | -59.4086 | -59.1293 | -0.24261 | 0.013733 | -0.045777 | 0.20599 | 59.2255 | -0.25177 | 59.4681 | -0.009156 | -0.091552 | -0.013733 | 0.13275 | 0.082398 | 0.20142 | -0.077819 | 0.29297 | 0.013733 | 0.44861 | 123.2025 | 0.17395 | 123.23 | 123.262 | 123.0835 | 123.0194 | 122.9919 | -123.2483 | -123.0972 | 122.9599 | 123.1384 | 59.0424 | 58.8318
654.8594 | 123.2712 | -59.3399 | 63.6932 | -0.10986 | 0.0023563 | 0.061795 | 0.062664 | 8.1126e-05 | -0.0020935 | 0.00086083 | -0.0054016 | 0.0020572 | 0.068112 | 0.062397 | -0.0073188 | 0.006539 | -0.0024931 | -0.33417 | 63.7161 | -59.5779 | 63.4506 | -59.1248 | -59.5459 | -0.17395 | -0.59052 | 63.6795 | -59.4223 | 63.7711 | -59.2667 | -59.4406 | -59.1431 | -0.23804 | 0.022888 | -0.24261 | 0.21515 | 59.166 | -0.20599 | 59.404 | 0.032044 | -0.082397 | -0.013733 | 0.07782 | 0.073242 | 0.19684 | -0.10071 | 0.27924 | -0.018311 | 0.45319 | 123.0286 | 0.15564 | 123.1934 | 123.2941 | 123.1018 | 123.056 | 123.0194 | -123.2712 | -123.1155 | 122.7905 | 123.111 | 59.0057 | 58.7494
655.8594 | 123.2849 | -59.3216 | 63.6612 | -0.12512 | 0.0025699 | 0.06329 | 0.066723 | 0.0024311 | -0.0023071 | -0.0010618 | -0.093903 | 0.003339 | 0.067898 | 0.066242 | -0.0049688 | 0.0056846 | -0.0012113 | -0.27924 | 63.6703 | -59.5184 | 63.6749 | -59.1248 | -59.5642 | -0.1236 | -0.49439 | 63.6795 | -59.4177 | 63.8123 | -59.2529 | -59.404 | -59.1248 | -0.19684 | 0.009155 | 0.013733 | 0.19684 | 59.198 | -0.24262 | 59.3948 | -0.045776 | -0.096131 | 0.01831 | 0.15106 | 0.068664 | 0.19684 | -0.082398 | 0.29297 | 0.013733 | 0.39368 | 123.1934 | 0.16479 | 123.23 | 123.1888 | 123.0972 | 122.9919 | 123.0011 | -123.1796 | -123.0789 | 122.9965 | 123.1338 | 59.0424 | 58.8272
656.8906 | 123.2895 | -59.3124 | 63.6887 | -0.10986 | 0.0019291 | 0.063504 | 0.067364 | 0.0020037 | -0.0044433 | 0.00022003 | -0.029816 | 0.0012028 | 0.067471 | 0.065815 | -0.0075324 | 0.0046164 | -0.0022793 | -0.3067 | 63.7573 | -59.5413 | 63.6383 | -59.166 | -59.5734 | -0.082397 | -0.48981 | 63.707 | -59.3903 | 63.8031 | -59.2484 | -59.3903 | -59.1202 | -0.22888 | 0.068664 | -0.050354 | 0.14648 | 59.23 | -0.26093 | 59.4589 | -0.032043 | -0.07782 | 0.01831 | 0.11444 | 0.064087 | 0.19226 | -0.07782 | 0.27008 | 0 | 0.37537 | 123.1796 | 0.14191 | 123.1934 | 123.2986 | 123.0972 | 123.0698 | 123.0194 | -123.23 | -123.0789 | 122.9507 | 123.1155 | 59.0057 | 58.8226
657.8594 | 123.2986 | -59.3216 | 63.652 | -0.071716 | 0.00043366 | 0.062649 | 0.066296 | 0.0024311 | -0.0010255 | -0.00084817 | -0.078644 | 0.0035526 | 0.067044 | 0.064747 | -0.0066778 | 0.0061118 | -0.0039883 | -0.29755 | 63.6841 | -59.5322 | 63.6887 | -59.1156 | -59.5551 | -0.10529 | -0.49896 | 63.7024 | -59.3994 | 63.8214 | -59.2346 | -59.3948 | -59.111 | -0.21057 | 0.032043 | 0.036621 | 0.20599 | 59.2163 | -0.23346 | 59.4269 | -0.022888 | -0.07782 | 0.050354 | 0.16937 | 0.086975 | 0.21057 | -0.073242 | 0.28839 | 0.004578 | 0.41656 | 123.2208 | 0.16479 | 123.2208 | 123.2162 | 123.1018 | 123.0057 | 123.024 | -123.1842 | -123.0515 | 123.0103 | 123.143 | 59.024 | 58.8226
658.8906 | 123.2803 | -59.2987 | 63.6978 | -0.064087 | 0.0019291 | 0.064572 | 0.067364 | 0.00093573 | -0.0010255 | -0.00020717 | -0.029816 | 0.0035526 | 0.068753 | 0.065815 | -0.0053962 | 0.0069662 | -0.0012113 | -0.32959 | 63.7253 | -59.5367 | 63.6246 | -59.1522 | -59.5825 | -0.10529 | -0.53101 | 63.707 | -59.3903 | 63.7894 | -59.2484 | -59.404 | -59.1431 | -0.23804 | 0.027466 | -0.073242 | 0.14648 | 59.1934 | -0.28381 | 59.4315 | -0.045777 | -0.091553 | 0.009155 | 0.091553 | 0.050354 | 0.15564 | -0.10529 | 0.24719 | -0.013733 | 0.38452 | 123.1613 | 0.14191 | 123.1796 | 123.262 | 123.0972 | 123.024 | 123.0057 | -123.2346 | -123.0881 | 122.9233 | 123.0881 | 58.9691 | 58.7677
659.8594 | 123.2941 | -59.3033 | 63.6887 | -0.079346 | 0.0017155 | 0.062436 | 0.067791 | -0.0024823 | 0.00025633 | -0.00063437 | -0.078644 | 0.00098899 | 0.066189 | 0.06432 | -0.0073188 | 0.0076072 | -0.0029203 | -0.30212 | 63.6932 | -59.5367 | 63.6749 | -59.1019 | -59.5642 | -0.10529 | -0.49439 | 63.6658 | -59.3994 | 63.826 | -59.2255 | -59.3903 | -59.1019 | -0.23346 | 0.004577 | -0.013733 | 0.20142 | 59.198 | -0.26093 | 59.4315 | -0.027466 | -0.09613 | -0.022889 | 0.13733 | 0.07782 | 0.20142 | -0.086975 | 0.29755 | 0.009155 | 0.43487 | 123.2117 | 0.17395 | 123.2254 | 123.23 | 123.0652 | 122.9965 | 122.9691 | -123.2254 | -123.0881 | 122.9782 | 123.1293 | 59.0012 | 58.8089
660.9062 | 123.3215 | -59.3079 | 63.7253 | -0.079346 | 0.0015019 | 0.064572 | 0.06715 | -0.0014143 | -0.0012391 | -0.001489 | -0.032867 | 0.0014164 | 0.070889 | 0.057911 | -0.0064642 | 0.006539 | -0.0014249 | -0.31128 | 63.739 | -59.5413 | 63.6475 | -59.1385 | -59.5459 | -0.073242 | -0.48523 | 63.7207 | -59.3857 | 63.8031 | -59.2163 | -59.3719 | -59.1064 | -0.23346 | 0.013733 | -0.07782 | 0.16937 | 59.2346 | -0.23804 | 59.4681 | -0.004577 | -0.07782 | -0.004578 | 0.07782 | 0.091552 | 0.20142 | -0.064087 | 0.27924 | 0.013733 | 0.40283 | 123.1888 | 0.16937 | 123.1888 | 123.2803 | 123.1064 | 123.0469 | 123.0286 | -123.2666 | -123.111 | 122.9553 | 123.111 | 58.9966 | 58.8226
661.8594 | 123.3078 | -59.3124 | 63.6795 | -0.13275 | 0.0036381 | 0.062863 | 0.068005 | 0.0017901 | -0.0012391 | -0.003198 | -0.087799 | 0.0020572 | 0.068966 | 0.066883 | -0.006037 | 0.0063254 | -0.0022793 | -0.31586 | 63.6932 | -59.5413 | 63.6841 | -59.1064 | -59.5413 | -0.10986 | -0.47607 | 63.6612 | -59.4131 | 63.8214 | -59.2392 | -59.3491 | -59.0881 | -0.22888 | 0.013733 | 0.004578 | 0.20599 | 59.2026 | -0.22888 | 59.4315 | 0 | -0.10071 | -0.01831 | 0.14191 | 0.073242 | 0.2243 | -0.036621 | 0.32501 | 0.064087 | 0.43488 | 123.2254 | 0.17395 | 123.2346 | 123.2346 | 123.0743 | 123.0057 | 122.9736 | -123.2208 | -123.0927 | 122.9965 | 123.1338 | 58.9966 | 58.8364
662.9062 | 123.317 | -59.2896 | 63.7207 | -0.02594 | 0.0029971 | 0.062649 | 0.066082 | -0.00013247 | -0.00017087 | -0.0010618 | -0.023712 | 0.003339 | 0.068753 | 0.064747 | -0.0058234 | 0.0067526 | -0.00078406 | -0.27466 | 63.7619 | -59.5001 | 63.6932 | -59.0881 | -59.5093 | -0.022888 | -0.43488 | 63.7161 | -59.3674 | 63.858 | -59.1934 | -59.3399 | -59.0652 | -0.21057 | 0.041199 | -0.027466 | 0.20142 | 59.2667 | -0.21973 | 59.4772 | -0.009155 | -0.07782 | -0.004578 | 0.13733 | 0.096131 | 0.2243 | -0.050354 | 0.30212 | 0.027466 | 0.41199 | 123.1934 | 0.17395 | 123.2254 | 123.262 | 123.0835 | 123.0515 | 123.0057 | -123.2208 | -123.0881 | 122.9828 | 123.1476 | 59.0149 | 58.8547
663.8594 | 123.317 | -59.2941 | 63.6978 | -0.094604 | 0.0023563 | 0.065213 | 0.066937 | -0.00055967 | -0.0029481 | 0.001929 | -0.057281 | -0.00029261 | 0.067898 | 0.06902 | -0.006037 | 0.0044028 | -0.0027067 | -0.29755 | 63.707 | -59.5413 | 63.6703 | -59.0881 | -59.5551 | -0.10071 | -0.48065 | 63.6978 | -59.3719 | 63.8351 | -59.2255 | -59.3857 | -59.079 | -0.24719 | 0.009155 | -0.027466 | 0.20599 | 59.1934 | -0.26093 | 59.4406 | -0.013733 | -0.07782 | 0 | 0.13733 | 0.068664 | 0.21515 | -0.091553 | 0.29297 | -0.013733 | 0.45319 | 123.2117 | 0.14648 | 123.2071 | 123.2483 | 123.0698 | 123.0011 | 122.9919 | -123.2391 | -123.0698 | 122.9645 | 123.1293 | 58.9966 | 58.8135
664.8906 | 123.3353 | -59.2758 | 63.739 | -0.048828 | -0.0019161 | 0.062436 | 0.066082 | 0.00029473 | -0.0018799 | -0.00063437 | -0.023712 | 0.0014164 | 0.067044 | 0.064747 | -0.0049688 | 0.0061118 | -0.0012113 | -0.28381 | 63.7482 | -59.5001 | 63.7436 | -59.0103 | -59.404 | 0.013733 | -0.35248 | 63.7436 | -59.3445 | 63.858 | -59.1339 | -59.3079 | -59.0515 | -0.2243 | 0.009155 | 0.004577 | 0.2655 | 59.2896 | -0.12817 | 59.5139 | 0.09613 | -0.068664 | 0.004577 | 0.11902 | 0.14191 | 0.2243 | -0.032043 | 0.29297 | 0.036621 | 0.48981 | 123.2437 | 0.21057 | 123.2025 | 123.2483 | 123.0881 | 123.024 | 123.0194 | -123.2391 | -123.0835 | 123.0194 | 123.1338 | 58.992 | 58.9233
665.8594 | 123.2895 | -59.3124 | 63.6932 | -0.10986 | 0.0019291 | 0.063504 | 0.069286 | 0.0054217 | 0.00089713 | -0.0012754 | -0.084747 | 0.0020572 | 0.068325 | 0.069447 | -0.0058234 | 0.0061118 | -0.00057046 | -0.28381 | 63.7207 | -59.5184 | 63.6795 | -59.0927 | -59.5596 | -0.10529 | -0.50354 | 63.6795 | -59.3903 | 63.8443 | -59.2072 | -59.3765 | -59.0652 | -0.20599 | 0.027466 | -0.013733 | 0.21973 | 59.2072 | -0.24719 | 59.4131 | -0.041198 | -0.07782 | -0.013733 | 0.15106 | 0.10529 | 0.24719 | -0.064087 | 0.32501 | 0.013733 | 0.42572 | 123.1979 | 0.18311 | 123.2346 | 123.2391 | 123.0698 | 123.0331 | 122.9919 | -123.2117 | -123.0835 | 122.9919 | 123.1567 | 59.0286 | 58.8089
666.9062 | 123.2071 | -59.285 | 63.7894 | -0.02594 | 0.0025699 | 0.06094 | 0.069927 | -0.0020551 | -0.0023071 | -0.00020717 | -0.057281 | 0.0024844 | 0.067684 | 0.067951 | -0.007105 | 0.0063254 | -0.00014306 | -0.31128 | 63.8306 | -59.523 | 63.6337 | -59.1614 | -59.5642 | -0.064087 | -0.49896 | 63.8077 | -59.3857 | 63.7619 | -59.2712 | -59.4223 | -59.1339 | -0.23804 | 0.041198 | -0.15564 | 0.1236 | 59.2209 | -0.27924 | 59.4589 | -0.041199 | -0.10071 | 0.01831 | -0.027466 | 0.013733 | 0.15106 | -0.13733 | 0.25177 | -0.036621 | 0.36163 | 123.1567 | 0.11444 | 123.1476 | 123.3536 | 123.1934 | 123.1155 | 123.0927 | -123.3124 | -123.175 | 122.9187 | 123.0469 | 58.9737 | 58.786
667.8594 | 123.2254 | -59.317 | 63.7207 | -0.13275 | 0.0012881 | 0.061795 | 0.069286 | 0.0039263 | -0.0035889 | 0.00043363 | -0.084747 | 0.0035526 | 0.067044 | 0.071583 | -0.0058234 | 0.0084616 | -0.00035666 | -0.35706 | 63.7665 | -59.5413 | 63.5971 | -59.2072 | -59.6329 | -0.20142 | -0.59967 | 63.7573 | -59.4223 | 63.7619 | -59.2987 | -59.4772 | -59.1476 | -0.2243 | 0.045776 | -0.1236 | 0.10986 | 59.1156 | -0.31586 | 59.3399 | -0.091553 | -0.10529 | 0.036621 | 0.041199 | 0.018311 | 0.16937 | -0.16022 | 0.27466 | -0.054932 | 0.33417 | 123.1384 | 0.1236 | 123.1842 | 123.3078 | 123.1796 | 123.0835 | 123.0743 | -123.262 | -123.143 | 122.9141 | 123.0789 | 58.96 | 58.7173
668.8906 | 123.2712 | -59.2941 | 63.7299 | -0.10223 | 0.0017155 | 0.064145 | 0.067791 | 0.0011493 | -0.0027345 | -0.001489 | -0.087799 | 0.0031254 | 0.069607 | 0.067311 | -0.0062506 | 0.0076072 | 0.00071134 | -0.35248 | 63.7711 | -59.5276 | 63.6154 | -59.198 | -59.6054 | -0.18768 | -0.55847 | 63.7711 | -59.3994 | 63.8031 | -59.2392 | -59.4223 | -59.111 | -0.23346 | 0.041199 | -0.11444 | 0.09613 | 59.1064 | -0.31128 | 59.3399 | -0.07782 | -0.10529 | 0.041199 | 0.073243 | 0.054931 | 0.1831 | -0.12817 | 0.28839 | -0.022888 | 0.32959 | 123.143 | 0.16022 | 123.2025 | 123.2986 | 123.1705 | 123.0652 | 123.0652 | -123.2574 | -123.1293 | 122.9095 | 123.0972 | 58.9417 | 58.7357
669.8594 | 123.2803 | -59.2941 | 63.7115 | -0.2243 | 0.0049197 | 0.063504 | 0.066937 | 0.00072213 | -0.0023071 | 0.00022003 | -0.032867 | 0.0035526 | 0.068112 | 0.069233 | -0.0066778 | 0.0046164 | -0.0033475 | -0.27924 | 63.7619 | -59.5093 | 63.7115 | -59.0607 | -59.5276 | -0.11902 | -0.48065 | 63.7161 | -59.3628 | 63.8626 | -59.1934 | -59.3628 | -59.0607 | -0.21515 | 0.050354 | 0 | 0.23346 | 59.1751 | -0.23346 | 59.3903 | -0.018311 | -0.068665 | 0.004577 | 0.15106 | 0.10071 | 0.23346 | -0.068665 | 0.30212 | 0 | 0.44861 | 123.2208 | 0.16937 | 123.2254 | 123.2712 | 123.0789 | 123.056 | 123.0103 | -123.2208 | -123.0743 | 123.0057 | 123.1567 | 59.0149 | 58.8135
670.8906 | 123.2986 | -59.2941 | 63.7161 | -0.048828 | -0.00042094 | 0.06564 | 0.068859 | 0.0022173 | -0.0016663 | -0.0029844 | -0.084747 | 0.0035526 | 0.067898 | 0.068165 | -0.0066778 | 0.0069662 | -0.0027067 | -0.33875 | 63.7665 | -59.5322 | 63.6383 | -59.1385 | -59.5596 | -0.12817 | -0.54016 | 63.7024 | -59.4086 | 63.8397 | -59.1568 | -59.4269 | -59.0973 | -0.23804 | 0.050354 | -0.077819 | 0.15564 | 59.166 | -0.2655 | 59.404 | -0.027465 | -0.11444 | -0.013732 | 0.1236 | 0.13733 | 0.19684 | -0.13275 | 0.31128 | -0.018311 | 0.39368 | 123.1705 | 0.25177 | 123.2483 | 123.2986 | 123.111 | 123.0606 | 122.9965 | -123.2483 | -123.1247 | 122.9324 | 123.1338 | 58.9554 | 58.754
671.8594 | 123.317 | -59.2621 | 63.7115 | -0.11749 | 0.0027835 | 0.063504 | 0.06715 | 0.0013629 | 0.0017517 | 0.00043363 | -0.042023 | 0.0018436 | 0.068753 | 0.067951 | -0.0064642 | 0.006539 | 0.00049774 | -0.3067 | 63.7344 | -59.5093 | 63.707 | -59.0561 | -59.5184 | -0.10529 | -0.48523 | 63.7299 | -59.3582 | 63.8718 | -59.1705 | -59.3353 | -59.0469 | -0.24719 | 0.022888 | -0.004578 | 0.20599 | 59.1568 | -0.25635 | 59.404 | -0.009156 | -0.09613 | 0.01831 | 0.16022 | 0.091553 | 0.21515 | -0.073242 | 0.31128 | 0.022888 | 0.45319 | 123.2162 | 0.18768 | 123.23 | 123.2437 | 123.0881 | 122.9965 | 122.9919 | -123.2208 | -123.0698 | 122.9691 | 123.1338 | 58.9554 | 58.7769
672.8906 | 123.1476 | -59.3033 | 63.7344 | -0.094604 | 0.0025699 | 0.061581 | 0.067364 | 0.00050853 | -0.0025207 | -0.00084817 | -0.16104 | 0.0022708 | 0.067471 | 0.067097 | -0.0066778 | 0.006539 | -0.00014306 | -0.33417 | 63.8214 | -59.5139 | 63.5559 | -59.6832 | -59.6008 | 0.068665 | -0.46692 | 63.8123 | -59.3674 | 63.7482 | -59.2987 | -59.5093 | -59.1843 | -0.21057 | 0.086975 | -0.17853 | -0.37994 | 59.3719 | -0.29755 | 59.5825 | -0.086975 | -0.064087 | 0.07782 | 0.013733 | 0.004578 | 0.11902 | -0.20599 | 0.18311 | -0.14191 | -0.16937 | 123.0698 | 0.068665 | 123.1155 | 123.3353 | 123.1796 | 123.1247 | 123.1155 | -123.2483 | -123.1018 | 122.8592 | 123.0515 | 58.9691 | 58.8364
673.8594 | 123.262 | -59.2804 | 63.739 | -0.13275 | 0.00086086 | 0.064572 | 0.068218 | -0.00098687 | 0.0011109 | -0.0017026 | -0.087799 | 0.0037662 | 0.068753 | 0.071797 | -0.004328 | 0.0073936 | -0.00099766 | -0.36621 | 63.7756 | -59.5047 | 63.6108 | -59.1614 | -59.5963 | -0.1831 | -0.5722 | 63.7482 | -59.3811 | 63.826 | -59.2392 | -59.4086 | -59.0927 | -0.2243 | 0.036621 | -0.12817 | 0.11902 | 59.0973 | -0.31586 | 59.3216 | -0.091552 | -0.10071 | 0.009155 | 0.086975 | 0.041199 | 0.18768 | -0.12817 | 0.28839 | -0.027465 | 0.34332 | 123.1155 | 0.14191 | 123.2071 | 123.2803 | 123.1293 | 123.056 | 123.0286 | -123.2437 | -123.1201 | 122.8912 | 123.1064 | 58.9142 | 58.7082
674.8906 | 123.0423 | -59.3308 | 63.7802 | -0.02594 | 0.0040653 | 0.064572 | 0.069073 | -0.0014143 | 0.00068353 | -0.0027708 | -0.10611 | 0.0031254 | 0.070461 | 0.065388 | -0.0056098 | 0.0071798 | 0.0011385 | -0.3067 | 63.8123 | -59.5001 | 63.6566 | -59.1568 | -59.5734 | -0.16022 | -0.55847 | 63.7848 | -59.3491 | 63.7665 | -59.285 | -59.7702 | -59.5413 | -0.16937 | 0.032044 | -0.1236 | 0.17395 | 59.1705 | -0.24261 | 59.3399 | -0.073242 | -0.01831 | 0.004578 | -0.013733 | 0.045777 | -0.21057 | -0.43945 | -0.19226 | -0.42114 | 0.34332 | 123.1567 | 0.064087 | 123.1155 | 123.3124 | 123.1338 | 123.143 | 123.1155 | -123.2803 | -123.1293 | 122.9874 | 123.0972 | 59.024 | 58.7723
675.8594 | 123.1979 | -59.2804 | 63.7527 | -0.10223 | 0.00064726 | 0.062649 | 0.066723 | 0.0022173 | 0.00068353 | -0.004266 | -0.081696 | 0.0029116 | 0.069607 | 0.063679 | -0.006037 | 0.0071798 | 0.00049774 | -0.36163 | 63.8443 | -59.5139 | 63.62 | -59.1751 | -59.6054 | -0.1831 | -0.59509 | 63.7802 | -59.3582 | 63.7848 | -59.2575 | -59.436 | -59.1293 | -0.23346 | 0.091552 | -0.13275 | 0.10529 | 59.0973 | -0.32501 | 59.3308 | -0.091553 | -0.077819 | 0.027465 | 0.032043 | 0.022889 | 0.15106 | -0.15564 | 0.22888 | -0.07782 | 0.33875 | 123.1338 | 0.10071 | 123.143 | 123.3582 | 123.1384 | 123.1247 | 123.0606 | -123.2666 | -123.111 | 122.9004 | 123.0652 | 58.9188 | 58.6853
676.9062 | 123.2666 | -59.198 | 63.7848 | -0.10986 | 0.00086086 | 0.062008 | 0.066082 | -0.0044049 | -0.0016663 | -0.0012754 | 0.022064 | 0.0018436 | 0.068112 | 0.062824 | -0.0032598 | 0.0054708 | 0.0039157 | -0.3067 | 63.8351 | -59.4452 | 63.6978 | -59.0607 | -59.4727 | -0.054932 | -0.46692 | 63.7665 | -59.3124 | 63.8672 | -59.1339 | -59.2987 | -59.0332 | -0.24719 | 0.050354 | -0.086975 | 0.13733 | 59.1431 | -0.27466 | 59.3903 | -0.027466 | -0.11444 | -0.018311 | 0.082397 | 0.064087 | 0.16479 | -0.10071 | 0.27924 | 0.013733 | 0.38452 | 123.143 | 0.17853 | 123.1796 | 123.2803 | 123.0789 | 123.0331 | 122.9645 | -123.23 | -123.0972 | 122.8958 | 123.0652 | 58.8913 | 58.7311
677.8594 | 123.2117 | -59.2804 | 63.7436 | -0.071716 | 0.0032107 | 0.063076 | 0.068005 | 0.0026447 | -0.0012391 | -0.00063437 | -0.066437 | 0.0022708 | 0.070034 | 0.066029 | -0.0073188 | 0.0071798 | -0.0020657 | -0.36163 | 63.8168 | -59.4772 | 63.6658 | -59.1202 | -59.5688 | -0.16937 | -0.54474 | 63.7985 | -59.3536 | 63.858 | -59.1888 | -59.3445 | -59.0515 | -0.19684 | 0.073242 | -0.07782 | 0.16022 | 59.111 | -0.28839 | 59.3079 | -0.091553 | -0.073242 | 0.054932 | 0.11444 | 0.091553 | 0.22888 | -0.064086 | 0.30212 | 0.009156 | 0.35706 | 123.143 | 0.16479 | 123.2117 | 123.2941 | 123.1522 | 123.0972 | 123.0789 | -123.2208 | -123.0972 | 122.9462 | 123.1384 | 58.9188 | 58.7357
678.8906 | 123.1979 | -59.285 | 63.8168 | -0.12512 | 0.0023563 | 0.062436 | 0.068859 | 0.0060627 | -0.0027345 | -0.001489 | -0.093903 | 0.0022708 | 0.068966 | 0.067524 | -0.0066778 | 0.008248 | -0.0014249 | -0.35248 | 63.8535 | -59.4818 | 63.6246 | -59.1843 | -59.5825 | -0.17853 | -0.60425 | 63.8077 | -59.3353 | 63.7848 | -59.2804 | -59.4543 | -59.1293 | -0.19684 | 0.036622 | -0.19226 | 0.10071 | 59.1064 | -0.29755 | 59.3033 | -0.10071 | -0.050354 | -0.009155 | -0.032043 | 0.004577 | 0.15564 | -0.16937 | 0.20599 | -0.11902 | 0.29755 | 123.1064 | 0.054931 | 123.1201 | 123.3353 | 123.143 | 123.1384 | 123.0927 | -123.2986 | -123.1522 | 122.9095 | 123.0698 | 58.9325 | 58.6807
679.8594 | 123.2437 | -59.2484 | 63.7894 | -0.11749 | 0.0023563 | 0.063076 | 0.067364 | 0.00050853 | -0.0025207 | -0.001489 | -0.069489 | 0.0031254 | 0.064907 | 0.069233 | -0.0064642 | 0.0071798 | -0.0035611 | -0.36163 | 63.826 | -59.4681 | 63.6337 | -59.1248 | -59.5551 | -0.19684 | -0.58136 | 63.8031 | -59.3582 | 63.8306 | -59.198 | -59.3674 | -59.0973 | -0.21973 | 0.036621 | -0.15564 | 0.1236 | 59.0515 | -0.3067 | 59.2712 | -0.086975 | -0.10986 | 0.013733 | 0.041198 | 0.050354 | 0.15106 | -0.11902 | 0.26093 | -0.009156 | 0.34332 | 123.1018 | 0.16022 | 123.1888 | 123.2941 | 123.1613 | 123.0743 | 123.0515 | -123.2574 | -123.1476 | 122.8821 | 123.0789 | 58.8867 | 58.667
680.8906 | 123.2208 | -59.2621 | 63.7848 | -0.079346 | 0.0010745 | 0.063504 | 0.069714 | 0.0022173 | -0.0012391 | -0.0034116 | -0.048126 | 0.004407 | 0.067898 | 0.064533 | -0.0049688 | 0.0073936 | -0.0039883 | -0.3479 | 63.8443 | -59.4955 | 63.6383 | -59.1431 | -59.5734 | -0.19684 | -0.60425 | 63.8443 | -59.3353 | 63.8123 | -59.2484 | -59.4131 | -59.0927 | -0.23346 | 0.059509 | -0.14648 | 0.11902 | 59.0652 | -0.31128 | 59.2987 | -0.07782 | -0.073242 | 0.059509 | 0.027466 | 0.013733 | 0.16937 | -0.15106 | 0.24262 | -0.07782 | 0.35248 | 123.1338 | 0.086975 | 123.1476 | 123.3398 | 123.1796 | 123.1064 | 123.1064 | -123.2803 | -123.1201 | 122.9004 | 123.0743 | 58.9142 | 58.6578
681.875 | 123.3078 | -59.1797 | 63.8214 | -0.086975 | 0.00022006 | 0.06094 | 0.066723 | -0.0014143 | -0.0014527 | -0.0034116 | 0.034271 | 0.0037662 | 0.067684 | 0.065815 | -0.0083868 | 0.003762 | 0.0022067 | -0.32501 | 63.8855 | -59.3628 | 63.7253 | -59.0515 | -59.3079 | 0.013733 | -0.32044 | 63.8123 | -59.2529 | 63.9816 | -59.0424 | -59.2117 | -58.96 | -0.18311 | 0.064087 | -0.09613 | 0.12817 | 59.1934 | -0.12817 | 59.3765 | 0.054932 | -0.073243 | -0.009155 | 0.16022 | 0.13733 | 0.21973 | -0.032044 | 0.29297 | 0.041199 | 0.31128 | 123.0881 | 0.21057 | 123.2346 | 123.2483 | 123.0652 | 123.0652 | 122.9919 | -123.1842 | -123.0743 | 122.905 | 123.1613 | 58.8547 | 58.8593
682.8906 | 123.2071 | -59.2529 | 63.826 | -0.064087 | 0.0027835 | 0.061795 | 0.068432 | 0.0017901 | -0.0018799 | -0.001489 | -0.07254 | 0.0031254 | 0.067684 | 0.069447 | -0.0056098 | 0.0058982 | -0.0039883 | -0.3479 | 63.8809 | -59.4681 | 63.652 | -59.1385 | -59.5779 | -0.18768 | -0.59967 | 63.8489 | -59.3124 | 63.8031 | -59.2484 | -59.4269 | -59.1019 | -0.21515 | 0.054931 | -0.17395 | 0.11444 | 59.0652 | -0.32501 | 59.2804 | -0.10986 | -0.059509 | 0.022888 | -0.022888 | 0.004578 | 0.15106 | -0.17395 | 0.21057 | -0.11444 | 0.32959 | 123.1201 | 0.064087 | 123.1155 | 123.349 | 123.1613 | 123.1338 | 123.1018 | -123.2941 | -123.1384 | 122.905 | 123.056 | 58.905 | 58.6533
683.8594 | 123.2712 | -59.2163 | 63.8214 | -0.086975 | 0.0023563 | 0.061154 | 0.06715 | 0.0013629 | -0.0010255 | -0.00084817 | -0.035919 | 0.0014164 | 0.067471 | 0.071156 | -0.007105 | 0.006539 | -0.0012113 | -0.35706 | 63.8626 | -59.4681 | 63.707 | -59.0927 | -59.5001 | -0.16937 | -0.54016 | 63.8214 | -59.317 | 63.8855 | -59.1476 | -59.3353 | -59.0149 | -0.25177 | 0.041199 | -0.11444 | 0.1236 | 59.0469 | -0.28381 | 59.2987 | -0.032043 | -0.10071 | 0 | 0.064087 | 0.068665 | 0.20142 | -0.11902 | 0.30212 | -0.01831 | 0.37537 | 123.175 | 0.16937 | 123.2025 | 123.3307 | 123.1384 | 123.0789 | 123.0377 | -123.2895 | -123.1384 | 122.9233 | 123.1018 | 58.8593 | 58.6761
684.8906 | 123.2895 | -59.1843 | 63.7848 | -0.10223 | 0.0036381 | 0.06329 | 0.068005 | 0.0041399 | -0.0010255 | 0.0015018 | -0.038971 | 0.0059024 | 0.066403 | 0.068165 | -0.007746 | 0.0052572 | -0.0042021 | -0.32959 | 63.8718 | -59.4452 | 63.7573 | -59.0286 | -59.4543 | -0.14648 | -0.70496 | 63.7756 | -59.3033 | 63.9404 | -59.1248 | -59.2712 | -58.9325 | -0.26092 | 0.086975 | -0.027466 | 0.15564 | 59.0378 | -0.27008 | 59.2987 | -0.009156 | -0.11902 | -0.009155 | 0.15564 | 0.059509 | 0.25177 | -0.086975 | 0.37079 | 0.032044 | 0.41656 | 123.2025 | 0.17853 | 123.2437 | 123.317 | 123.0789 | 123.056 | 122.9599 | -123.23 | -123.0881 | 122.9416 | 123.1247 | 58.8547 | 58.4793
685.8594 | 123.2254 | -59.2117 | 63.8214 | -0.12512 | 0.00086086 | 0.064358 | 0.06715 | -0.0022687 | -0.0018799 | -0.001489 | -0.063385 | 0.003339 | 0.067257 | 0.073506 | -0.0062506 | 0.0080344 | -0.0018521 | -0.36163 | 63.8992 | -59.4223 | 63.6841 | -59.0744 | -59.5322 | -0.16937 | -0.56305 | 63.8535 | -59.285 | 63.8763 | -59.1705 | -59.3674 | -59.024 | -0.21057 | 0.07782 | -0.13733 | 0.13733 | 59.0424 | -0.32043 | 59.2529 | -0.10986 | -0.073242 | 0.032044 | 0.054932 | 0.041199 | 0.18768 | -0.15564 | 0.26093 | -0.082398 | 0.3479 | 123.1064 | 0.11444 | 123.1613 | 123.3215 | 123.1384 | 123.111 | 123.0652 | -123.2437 | -123.1064 | 122.8958 | 123.0881 | 58.8501 | 58.6487
686.9062 | 123.2437 | -59.1705 | 63.8443 | -0.10223 | 0.0027835 | 0.06094 | 0.067791 | -0.0029095 | 0.00089713 | -0.0055478 | 0.034271 | 0.0018436 | 0.067044 | 0.064533 | -0.0064642 | 0.0044028 | -0.0035611 | -0.31128 | 63.8855 | -59.3719 | 63.7573 | -59.0057 | -59.4177 | -0.091553 | -0.5127 | 63.858 | -59.2529 | 63.8992 | -59.0973 | -59.2667 | -58.9783 | -0.20142 | 0.041199 | -0.086975 | 0.16479 | 59.079 | -0.24719 | 59.2804 | -0.045777 | -0.082398 | 0.013733 | 0.054932 | 0.073242 | 0.19226 | -0.096131 | 0.27466 | -0.013733 | 0.36621 | 123.1293 | 0.15564 | 123.1522 | 123.2574 | 123.111 | 123.056 | 123.0286 | -123.2162 | -123.0972 | 122.9279 | 123.0698 | 58.8593 | 58.6578
687.8594 | 123.1979 | -59.198 | 63.858 | -0.13275 | -0.00084814 | 0.064358 | 0.069073 | 0.0032855 | -0.0014527 | -0.0010618 | -0.078644 | 0.0031254 | 0.068325 | 0.067738 | -0.009455 | 0.0054708 | -0.00099766 | -0.33875 | 63.9175 | -59.4223 | 63.7024 | -59.0836 | -59.5184 | -0.17853 | -0.58136 | 63.9038 | -59.2896 | 63.8809 | -59.1843 | -59.3674 | -59.0561 | -0.2243 | 0.05951 | -0.15564 | 0.11444 | 59.0195 | -0.32044 | 59.2438 | -0.096131 | -0.091553 | 0.045777 | 0.022888 | 0.013733 | 0.14191 | -0.16937 | 0.23346 | -0.07782 | 0.33875 | 123.1247 | 0.10529 | 123.1705 | 123.3398 | 123.1934 | 123.1155 | 123.1018 | -123.2803 | -123.1476 | 122.9004 | 123.0789 | 58.8593 | 58.6166
688.9062 | 123.2437 | -59.1614 | 63.8351 | -0.14038 | 0.0012881 | 0.062863 | 0.068005 | -0.0012005 | 0.00046993 | -0.0040524 | 0.028168 | 0.00098899 | 0.066403 | 0.064533 | -0.0066778 | 0.0058982 | -0.0027067 | -0.31128 | 63.8809 | -59.3811 | 63.9267 | -58.8181 | -59.6832 | -0.13275 | -0.57678 | 63.8351 | -59.2117 | 63.9313 | -59.0698 | -59.2529 | -59.0057 | -0.21973 | 0.045776 | 0.091553 | 0.34332 | 59.0286 | -0.52185 | 59.2484 | -0.30212 | -0.050354 | 0 | 0.09613 | 0.091553 | 0.15564 | -0.091553 | 0.20599 | -0.041199 | 0.56305 | 123.3078 | 0.14191 | 123.143 | 123.262 | 123.0469 | 123.0423 | 122.9965 | -123.2162 | -123.0469 | 123.0881 | 123.0927 | 58.8501 | 58.5846
689.8594 | 123.1934 | -59.198 | 63.9038 | -0.041199 | 0.00064726 | 0.064785 | 0.069714 | 0.0026447 | -0.0018799 | -0.001489 | -0.084747 | 0.0035526 | 0.066189 | 0.069233 | -0.006037 | 0.006539 | -0.0012113 | -0.35706 | 63.9267 | -59.4177 | 63.7253 | -59.0927 | -59.5001 | -0.17395 | -0.59052 | 63.9038 | -59.2346 | 63.8809 | -59.166 | -59.3582 | -59.0378 | -0.21973 | 0.022888 | -0.17853 | 0.10529 | 59.024 | -0.30212 | 59.2438 | -0.082397 | -0.036621 | 0 | -0.022889 | 0.032043 | 0.16022 | -0.16022 | 0.19684 | -0.1236 | 0.32501 | 123.143 | 0.068664 | 123.1155 | 123.3444 | 123.1384 | 123.1247 | 123.1018 | -123.3215 | -123.1384 | 122.9233 | 123.0789 | 58.8409 | 58.6075
690.9062 | 123.2803 | -59.1293 | 63.8763 | -0.10223 | -0.00042094 | 0.062222 | 0.066937 | 0.0017901 | 0.00046993 | -0.0021298 | 0.040375 | 0.003339 | 0.06918 | 0.060688 | -0.0064642 | 0.0041892 | -0.0039883 | -0.30212 | 63.9313 | -59.3262 | 63.8214 | -58.9417 | -59.3811 | -0.045776 | -0.45319 | 63.8855 | -59.2209 | 63.9862 | -59.0103 | -59.1888 | -58.905 | -0.19684 | 0.054931 | -0.054932 | 0.18768 | 59.0836 | -0.25177 | 59.2804 | -0.054932 | -0.091553 | 0.009155 | 0.10986 | 0.11902 | 0.2243 | -0.05951 | 0.31586 | 0.032043 | 0.38452 | 123.1476 | 0.21057 | 123.2071 | 123.2574 | 123.1064 | 123.0606 | 123.0148 | -123.2025 | -123.0972 | 122.9507 | 123.1155 | 58.8272 | 58.6761
691.8594 | 123.2712 | -59.1431 | 63.9038 | -0.071716 | 0.00064726 | 0.06329 | 0.068859 | -0.0020551 | -0.0023071 | -0.00063437 | -0.069489 | 0.0024844 | 0.067471 | 0.073506 | -0.007746 | 0.0052572 | -0.00014306 | -0.34332 | 63.9221 | -59.3811 | 63.7848 | -59.0149 | -59.4589 | -0.16937 | -0.53101 | 63.9221 | -59.2346 | 63.9496 | -59.0607 | -59.2758 | -58.96 | -0.23804 | 0.01831 | -0.11902 | 0.12817 | 58.9737 | -0.31586 | 59.2117 | -0.077819 | -0.091553 | 0.01831 | 0.045776 | 0.082397 | 0.1831 | -0.13275 | 0.27466 | -0.041199 | 0.36621 | 123.1659 | 0.17395 | 123.1842 | 123.3032 | 123.1567 | 123.0652 | 123.0652 | -123.2849 | -123.1384 | 122.9279 | 123.0927 | 58.7997 | 58.6121
692.8906 | 123.2346 | -59.1568 | 63.9175 | -0.064087 | 0.0027835 | 0.063717 | 0.067577 | -0.0018415 | -0.0014527 | -0.004907 | -0.075592 | 0.0048344 | 0.069607 | 0.066242 | -0.0049688 | 0.0071798 | -0.00099766 | -0.33875 | 63.9679 | -59.3765 | 63.7619 | -59.0286 | -59.4635 | -0.16937 | -0.56305 | 63.9267 | -59.2255 | 63.9313 | -59.1202 | -59.3079 | -58.9874 | -0.21973 | 0.050354 | -0.15564 | 0.12817 | 58.9874 | -0.3067 | 59.2072 | -0.086975 | -0.068665 | 0.009155 | 0.013732 | 0.036621 | 0.16937 | -0.15106 | 0.23804 | -0.082397 | 0.3479 | 123.1384 | 0.10529 | 123.1567 | 123.3444 | 123.1522 | 123.1247 | 123.0835 | -123.2941 | -123.143 | 122.9187 | 123.0881 | 58.8181 | 58.5938
693.8594 | 123.2025 | -59.1202 | 63.9542 | 0.11902 | 6.46e-06 | 0.062649 | 0.06715 | 0.00029473 | -0.0023071 | 6.432e-06 | -0.07254 | 0.0031254 | 0.068112 | 0.064106 | -0.0051824 | 0.0071798 | -0.0074063 | -0.37537 | 63.9908 | -59.3536 | 63.7711 | -59.0744 | -59.4635 | -0.17853 | -0.56763 | 63.9542 | -59.198 | 63.9313 | -59.1156 | -59.3308 | -58.9874 | -0.23346 | 0.036621 | -0.18311 | 0.045776 | 58.9417 | -0.34332 | 59.1751 | -0.10986 | -0.07782 | 0 | -0.022889 | 0.004577 | 0.13275 | -0.21057 | 0.21057 | -0.13275 | 0.27924 | 123.1247 | 0.082397 | 123.1293 | 123.3444 | 123.1522 | 123.111 | 123.0743 | -123.3078 | -123.1522 | 122.8912 | 123.0515 | 58.7448 | 58.5526
694.9062 | 123.3078 | -59.0424 | 63.9404 | -0.39978 | 0.0021427 | 0.061154 | 0.066509 | 0.00029473 | -0.0018799 | -0.0036252 | 0.04953 | 0.0037662 | 0.06918 | 0.060475 | -0.006037 | 0.0052572 | 0.00028414 | -0.10529 | 63.9633 | -59.285 | 63.9633 | -58.7769 | -59.2621 | 0.027466 | -0.30212 | 63.9313 | -59.1339 | 64.0686 | -58.9005 | -59.0927 | -58.8181 | -0.24262 | 0.022888 | 0.022888 | 0.2655 | 59.0698 | -0.21973 | 59.3124 | 0.022888 | -0.091553 | -0.009156 | 0.12817 | 0.14191 | 0.2243 | -0.050354 | 0.31586 | 0.041199 | 0.50812 | 123.2483 | 0.23346 | 123.2025 | 123.2483 | 123.0652 | 123.0057 | 122.9736 | -123.2254 | -123.0743 | 123.0057 | 123.111 | 58.9371 | 58.7402
695.8594 | 123.2254 | -59.111 | 63.9771 | -0.079346 | 0.0025699 | 0.063076 | 0.067577 | 0.0017901 | -0.0020935 | -0.00042077 | -0.087799 | 0.0041934 | 0.068112 | 0.060261 | -0.0079596 | 0.0073936 | -0.00035666 | -0.2655 | 63.9954 | -59.3033 | 63.8626 | -58.9188 | -59.3536 | -0.10529 | -0.44861 | 63.9816 | -59.1476 | 63.9816 | -59.0286 | -59.2529 | -58.9371 | -0.19226 | 0.01831 | -0.11444 | 0.19226 | 59.0057 | -0.24261 | 59.198 | -0.050354 | -0.036621 | 0.004577 | 0.004577 | 0.082398 | 0.17395 | -0.14191 | 0.21057 | -0.10529 | 0.38452 | 123.1659 | 0.11902 | 123.1293 | 123.2986 | 123.1293 | 123.1064 | 123.0927 | -123.2803 | -123.1247 | 122.9736 | 123.0927 | 58.8455 | 58.6624
696.8906 | 123.2025 | -59.0881 | 63.9816 | -0.094604 | 0.0025699 | 0.061154 | 0.068005 | 0.0034991 | 0.0011109 | -0.0019162 | -0.066437 | 0.0029116 | 0.070461 | 0.067524 | -0.006037 | 0.0067526 | -0.00078406 | -0.32959 | 64.0091 | -59.3353 | 63.7985 | -58.9828 | -59.4086 | -0.19226 | -0.56305 | 63.9862 | -59.1751 | 63.9542 | -59.0515 | -59.2667 | -58.9371 | -0.24719 | 0.027466 | -0.1831 | 0.10529 | 58.8959 | -0.32043 | 59.1431 | -0.073242 | -0.086975 | 0.004578 | -0.027465 | 0.036621 | 0.15106 | -0.17853 | 0.23804 | -0.091553 | 0.35248 | 123.1338 | 0.1236 | 123.1293 | 123.3444 | 123.1613 | 123.0972 | 123.0743 | -123.317 | -123.1567 | 122.8867 | 123.0423 | 58.7585 | 58.5251
697.8594 | 123.1796 | -59.079 | 64.0045 | -0.0030519 | 0.0034245 | 0.063504 | 0.069927 | 0.0022173 | -0.0016663 | -0.0023434 | -0.081696 | 0.0031254 | 0.067684 | 0.063465 | -0.0083868 | 0.0061118 | -0.00057046 | -0.32044 | 64.0366 | -59.2896 | 63.8123 | -58.992 | -59.404 | -0.18768 | -0.58594 | 64.0366 | -59.1705 | 63.9404 | -59.0881 | -59.285 | -58.9554 | -0.21057 | 0.032043 | -0.19226 | 0.086975 | 58.8913 | -0.32501 | 59.1019 | -0.11444 | -0.091553 | 0.032043 | -0.064087 | -0.009156 | 0.1236 | -0.20599 | 0.21515 | -0.11444 | 0.29755 | 123.1018 | 0.082397 | 123.111 | 123.3261 | 123.2071 | 123.1155 | 123.1155 | -123.2941 | -123.175 | 122.8912 | 123.0194 | 58.7585 | 58.493
698.8906 | 123.1979 | -59.0195 | 64.0686 | -0.02594 | 0.0010745 | 0.063076 | 0.067791 | 0.0017901 | -0.0042297 | -0.0019162 | -0.038971 | 0.0041934 | 0.067684 | 0.070515 | -0.0051824 | 0.011666 | -0.0056973 | -0.25177 | 64.0915 | -59.2621 | 63.8947 | -58.8913 | -59.285 | -0.054932 | -0.42114 | 64.0549 | -59.0973 | 63.9404 | -58.8913 | -59.0424 | -58.8181 | -0.24262 | 0.022888 | -0.17395 | 0.12817 | 58.9645 | -0.2655 | 59.2072 | -0.022888 | -0.07782 | -0.013733 | -0.12817 | 0.12817 | 0.20142 | -0.022888 | 0.27924 | 0.054932 | 0.37079 | 123.1567 | 0.20599 | 123.0377 | 123.3536 | 123.1522 | 123.111 | 123.0743 | -123.3307 | -123.1659 | 122.9141 | 122.9599 | 58.7677 | 58.5983
699.875 | 123.262 | -59.0149 | 64.0182 | -0.086975 | 0.0012881 | 0.062863 | 0.066509 | 0.0013629 | -0.0031617 | -0.0021298 | 0.046478 | 0.0031254 | 0.068539 | 0.059834 | -0.0047552 | 0.0052572 | 0.0013521 | -0.2655 | 64.0503 | -59.198 | 63.9404 | -58.8318 | -59.2667 | -0.059509 | -0.43945 | 64.0228 | -59.0881 | 64.0915 | -58.8959 | -59.079 | -58.8135 | -0.1831 | 0.032043 | -0.07782 | 0.18311 | 58.9554 | -0.25177 | 59.1385 | -0.068665 | -0.073242 | 0.004577 | 0.073242 | 0.11902 | 0.20142 | -0.064086 | 0.27466 | 0.009156 | 0.36621 | 123.1384 | 0.19226 | 123.1796 | 123.2483 | 123.111 | 123.0652 | 123.0377 | -123.2162 | -123.1064 | 122.9553 | 123.1064 | 58.7494 | 58.5754
700.9375 | 123.2254 | -59.0424 | 64.0091 | -0.10223 | 0.0023563 | 0.063931 | 0.069286 | 8.1126e-05 | -0.0023071 | -0.002557 | -0.057281 | 0.00163 | 0.068325 | 0.066883 | -0.007105 | 0.0041892 | 0.00049774 | -0.32501 | 64.0411 | -59.2667 | 63.8901 | -58.9005 | -59.3399 | -0.16479 | -0.53101 | 64.0274 | -59.111 | 64.0778 | -58.9371 | -59.1705 | -58.8501 | -0.22431 | 0.032044 | -0.11902 | 0.14191 | 58.8776 | -0.29755 | 59.1019 | -0.073242 | -0.068665 | 0.018311 | 0.068665 | 0.10529 | 0.19226 | -0.12817 | 0.26093 | -0.059509 | 0.36621 | 123.1567 | 0.17395 | 123.1888 | 123.3078 | 123.1384 | 123.0835 | 123.0698 | -123.2758 | -123.1201 | 122.9324 | 123.1201 | 58.7173 | 58.5114
701.875 | 123.3124 | -58.9874 | 64.0182 | -0.094604 | 0.0025699 | 0.061581 | 0.065868 | 0.0022173 | 4.273e-05 | -0.0010618 | -0.038971 | 0.00098899 | 0.067471 | 0.064533 | -0.006037 | 0.0058982 | -0.0042021 | -0.24261 | 64.0549 | -59.2117 | 64.0045 | -58.7448 | -59.2117 | -0.064087 | -0.39825 | 64.032 | -59.0515 | 64.1556 | -58.8409 | -59.0515 | -58.7402 | -0.2243 | 0.036621 | -0.013733 | 0.24261 | 58.9233 | -0.2243 | 59.1476 | 0 | -0.064087 | 0.013732 | 0.13733 | 0.14648 | 0.24719 | -0.064087 | 0.31128 | 0 | 0.46692 | 123.2162 | 0.21057 | 123.2071 | 123.2666 | 123.0835 | 123.0423 | 123.0194 | -123.23 | -123.0698 | 122.9919 | 123.143 | 58.7448 | 58.5892
702.8906 | 123.23 | -58.9737 | 64.0915 | 0.0045776 | 0.0049197 | 0.062649 | 0.065228 | 0.00093573 | -0.0035889 | -0.001489 | -0.066437 | 0.0024844 | 0.070034 | 0.073078 | -0.0075324 | 0.006539 | -0.0014249 | -0.41199 | 64.1235 | -59.2163 | 63.9908 | -58.754 | -59.2209 | -0.054932 | -0.37537 | 64.1144 | -59.0378 | 64.1418 | -58.8638 | -59.079 | -58.7906 | -0.24262 | 0.032043 | -0.10071 | 0.21973 | 58.9188 | -0.24719 | 59.1614 | -0.004577 | -0.064087 | 0.022888 | 0.050354 | 0.10986 | 0.18311 | -0.10528 | 0.24719 | -0.041198 | 0.46234 | 123.2071 | 0.17395 | 123.1796 | 123.3398 | 123.1522 | 123.0972 | 123.0881 | -123.3078 | -123.1293 | 122.9645 | 123.1155 | 58.5617 | 58.5983
703.8594 | 123.2071 | -58.9508 | 64.1235 | -0.041199 | 0.0025699 | 0.062649 | 0.06715 | 0.0015765 | -0.00017087 | 0.00022003 | -0.075592 | 0.0029116 | 0.06683 | 0.06966 | -0.006037 | 0.0073936 | -0.0033475 | -0.23346 | 64.119 | -59.1614 | 63.9908 | -58.7906 | -59.23 | -0.10529 | -0.43945 | 64.1327 | -59.0286 | 64.119 | -58.8821 | -59.1156 | -58.8089 | -0.21057 | -0.004577 | -0.13275 | 0.16022 | 58.8455 | -0.27924 | 59.0561 | -0.068665 | -0.077819 | 0.009155 | -0.004577 | 0.068665 | 0.14191 | -0.16479 | 0.21973 | -0.086976 | 0.37079 | 123.1522 | 0.14648 | 123.1476 | 123.2803 | 123.1613 | 123.0698 | 123.0835 | -123.2849 | -123.1522 | 122.9416 | 123.0698 | 58.7173 | 58.5114
704.9062 | 123.2758 | -58.9188 | 64.1144 | -0.086975 | 0.0015019 | 0.062436 | 0.06715 | 0.0015765 | -0.0010255 | -0.004266 | 0.00070198 | 0.0031254 | 0.069393 | 0.060475 | -0.0073188 | 0.0063254 | 0.00092494 | -0.25177 | 64.1373 | -59.1202 | 64.0182 | -58.7265 | -59.1888 | -0.059509 | -0.42114 | 64.0823 | -58.9966 | 64.1556 | -58.7997 | -59.0149 | -58.7448 | -0.20142 | 0.022888 | -0.09613 | 0.19226 | 58.8593 | -0.27008 | 59.0607 | -0.068665 | -0.07782 | -0.032044 | 0.041199 | 0.11902 | 0.17395 | -0.096131 | 0.25177 | -0.018311 | 0.39368 | 123.1384 | 0.19684 | 123.1522 | 123.2574 | 123.0789 | 123.056 | 123.0011 | -123.2346 | -123.111 | 122.937 | 123.0743 | 58.667 | 58.4976
705.8594 | 123.175 | -58.9096 | 64.1556 | -0.094604 | 0.0015019 | 0.062649 | 0.06715 | 0.0026447 | -0.0012391 | -0.00020717 | -0.069489 | 0.0046206 | 0.067044 | 0.064747 | -0.0081732 | 0.0069662 | -0.0012113 | -0.2655 | 64.1693 | -59.1202 | 64.0045 | -58.786 | -59.2209 | -0.13275 | -0.49896 | 64.1647 | -58.9828 | 64.1235 | -58.873 | -59.0927 | -58.7723 | -0.21057 | 0.013733 | -0.15106 | 0.1236 | 58.7769 | -0.31128 | 58.9874 | -0.10071 | -0.073242 | 0.009155 | -0.032044 | 0.036621 | 0.13733 | -0.1831 | 0.21057 | -0.10986 | 0.33417 | 123.1247 | 0.10986 | 123.1064 | 123.2895 | 123.1476 | 123.0789 | 123.0743 | -123.2758 | -123.1384 | 122.9141 | 123.0331 | 58.6441 | 58.4106
707.2656 | 123.2391 | -58.8684 | 64.2288 | -0.064087 | 0.0010745 | 0.064145 | 0.066723 | -0.00077327 | -0.00081187 | 0.0010746 | 0.019012 | 0.00098899 | 0.067684 | 0.05962 | -0.006037 | 0.0069662 | 0.00049774 | -0.17395 | 64.2334 | -59.0378 | 64.1418 | -58.6075 | -59.0652 | 0.036621 | -0.32044 | 64.1968 | -58.9096 | 64.2288 | -58.7265 | -58.9508 | -58.6807 | -0.16937 | 0.004577 | -0.086975 | 0.26093 | 58.905 | -0.19684 | 59.0744 | -0.027466 | -0.041199 | -0.032044 | 0 | 0.14191 | 0.18768 | -0.082398 | 0.22888 | -0.041199 | 0.4303 | 123.1796 | 0.18311 | 123.1384 | 123.2712 | 123.1064 | 123.1018 | 123.0652 | -123.2666 | -123.1384 | 123.0103 | 123.0972 | 58.6945 | 58.548
707.8594 | 123.1979 | -58.8638 | 64.2197 | -0.086975 | 0.0017155 | 0.062649 | 0.067791 | 0.0032855 | 0.00068353 | -0.0012754 | -0.084747 | 0.0031254 | 0.067898 | 0.068379 | -0.007105 | 0.006539 | 0.0019931 | -0.24261 | 64.2242 | -59.0652 | 64.0686 | -58.7082 | -59.1476 | -0.10986 | -0.44861 | 64.2197 | -58.9508 | 64.1876 | -58.8089 | -59.0332 | -58.7219 | -0.20142 | 0.004577 | -0.15106 | 0.15564 | 58.754 | -0.28381 | 58.9554 | -0.082397 | -0.086975 | 0 | -0.032044 | 0.054932 | 0.14191 | -0.16937 | 0.22888 | -0.082397 | 0.35706 | 123.1339 | 0.14191 | 123.1384 | 123.2895 | 123.1705 | 123.0881 | 123.0835 | -123.2849 | -123.1705 | 122.9324 | 123.0515 | 58.6212 | 58.4152
708.875 | 123.2895 | -58.8409 | 64.1693 | -0.064087 | 0.0017155 | 0.063076 | 0.067577 | 0.0017901 | -0.0014527 | -0.001489 | -0.011505 | 0.00163 | 0.067257 | 0.069233 | -0.0068914 | 0.0058982 | -0.0042021 | -0.21973 | 64.1876 | -59.0515 | 64.1602 | -58.5938 | -59.0515 | -0.054932 | -0.36621 | 64.1968 | -58.9096 | 64.3158 | -58.6716 | -58.8913 | -58.5983 | -0.21057 | 0.01831 | -0.009156 | 0.24719 | 58.786 | -0.21057 | 58.9966 | 0 | -0.068665 | 0.027465 | 0.14648 | 0.16937 | 0.24261 | -0.050354 | 0.31128 | 0.018311 | 0.45776 | 123.2117 | 0.23804 | 123.2254 | 123.2391 | 123.1064 | 123.0286 | 123.0377 | -123.2208 | -123.0789 | 123.0011 | 123.1567 | 58.6212 | 58.4747
709.8594 | 123.1613 | -58.8089 | 64.2609 | -0.048828 | 0.0010745 | 0.06329 | 0.069714 | 0.0026447 | 0.00068353 | -0.0019162 | -0.069489 | 0.0037662 | 0.068539 | 0.067097 | -0.0090278 | 0.0073936 | 0.0024203 | -0.22888 | 64.27 | -59.024 | 64.2242 | -58.429 | -59.1797 | -0.073242 | -0.42114 | 64.2792 | -58.8593 | 64.2654 | -58.7311 | -58.9691 | -58.667 | -0.21515 | 0.009156 | -0.036621 | 0.37994 | 58.7357 | -0.37079 | 58.9508 | -0.15564 | -0.050354 | 0.018311 | 0.004578 | 0.07782 | 0.14191 | -0.16022 | 0.19226 | -0.10986 | 0.59509 | 123.2483 | 0.12817 | 123.1247 | 123.2941 | 123.1384 | 123.0789 | 123.0881 | -123.2849 | -123.1201 | 123.0331 | 123.0743 | 58.58 | 58.3878
710.9062 | 123.2895 | -58.7677 | 64.2288 | -0.10986 | 0.0019291 | 0.063076 | 0.065868 | 0.0013629 | -0.0014527 | -0.00042077 | -0.066437 | 0.0024844 | 0.067471 | 0.066883 | -0.0053962 | 0.0058982 | -0.00099766 | -0.22888 | 64.2654 | -58.9874 | 64.1876 | -58.5388 | -59.0286 | 0.21057 | -0.50812 | 64.2197 | -58.8547 | 64.3066 | -58.6075 | -58.8501 | -58.5709 | -0.21973 | 0.036621 | -0.041199 | 0.22888 | 58.9783 | -0.26093 | 59.198 | -0.041198 | -0.086975 | -0.009155 | 0.07782 | 0.16022 | 0.19684 | -0.082398 | 0.28381 | 0.004577 | 0.44861 | 123.175 | 0.24719 | 123.1613 | 123.2529 | 123.0743 | 123.0331 | 122.9874 | -123.2162 | -123.0835 | 122.9553 | 123.0743 | 58.5388 | 58.2596
711.8594 | 123.175 | -58.7906 | 64.3387 | -0.086975 | 0.0032107 | 0.064785 | 0.068432 | 0.0028583 | -0.0014527 | -0.00063437 | -0.090851 | 0.0024844 | 0.067898 | 0.072865 | -0.0056098 | 0.0058982 | -0.00014306 | -0.23804 | 64.3387 | -58.992 | 64.151 | -58.6349 | -59.079 | -0.10986 | -0.50354 | 64.3158 | -58.8684 | 64.2746 | -58.7173 | -58.9554 | -58.6304 | -0.20142 | 0 | -0.18768 | 0.15564 | 58.6807 | -0.28839 | 58.8821 | -0.086975 | -0.07782 | -0.022888 | -0.064087 | 0.073242 | 0.16022 | -0.16479 | 0.23804 | -0.086975 | 0.35706 | 123.143 | 0.15106 | 123.143 | 123.3307 | 123.1842 | 123.1293 | 123.1064 | -123.3307 | -123.2071 | 122.9416 | 123.0652 | 58.5526 | 58.287
712.8906 | 123.2529 | -58.7082 | 64.2975 | -0.079346 | 0.00043366 | 0.062436 | 0.061596 | 0.0043537 | 0.00068353 | -0.0029844 | 0.037323 | 0.0031254 | 0.068966 | 0.065388 | -0.0053962 | 0.00483 | 0.0015659 | -0.2243 | 64.325 | -58.9417 | 64.0823 | -58.2962 | -59.0378 | -0.14648 | -0.43945 | 64.27 | -58.8135 | 64.3845 | -58.5846 | -58.8089 | -58.5297 | -0.23346 | 0.027466 | -0.21515 | 0.41199 | 58.5617 | -0.32959 | 58.7952 | -0.096131 | -0.10529 | -0.027465 | 0.086975 | 0.1236 | 0.17853 | -0.10071 | 0.28381 | 0.004578 | 0.64545 | 123.024 | 0.22888 | 123.1979 | 123.2666 | 123.0835 | 123.0331 | 122.9782 | -123.2391 | -123.111 | 122.7905 | 123.0927 | 58.4839 | 58.2687
713.8594 | 123.175 | -58.7265 | 64.3753 | -0.048828 | 0.00064726 | 0.06329 | 0.070355 | -0.00055967 | -0.0027345 | -0.0017026 | -0.075592 | 0.0037662 | 0.070461 | 0.067097 | -0.0075324 | 0.0058982 | 0.00028414 | -0.28839 | 64.3845 | -58.9417 | 64.1602 | -58.5983 | -59.0469 | -0.1236 | -0.49439 | 64.3845 | -58.8043 | 64.3341 | -58.6441 | -58.905 | -58.5617 | -0.21515 | 0.009155 | -0.21515 | 0.12817 | 58.6029 | -0.32044 | 58.8181 | -0.10529 | -0.07782 | 0.009155 | -0.041199 | 0.082397 | 0.16479 | -0.17853 | 0.24261 | -0.10071 | 0.34332 | 123.1018 | 0.16022 | 123.1384 | 123.3261 | 123.1888 | 123.111 | 123.111 | -123.317 | -123.1796 | 122.8867 | 123.0606 | 58.4381 | 58.2321
714.8906 | 123.1659 | -58.6716 | 64.3845 | -0.079346 | 0.0025699 | 0.064145 | 0.069073 | 0.0043537 | 4.273e-05 | -0.00063437 | -0.07254 | 0.0022708 | 0.067471 | 0.068165 | -0.0062506 | 0.0076072 | -0.0014249 | -0.25177 | 64.4211 | -58.9279 | 64.2197 | -58.58 | -59.0057 | -0.12817 | -0.5127 | 64.389 | -58.7631 | 64.3478 | -58.6212 | -58.873 | -58.5388 | -0.25635 | 0.036622 | -0.16479 | 0.091553 | 58.5434 | -0.33417 | 58.7997 | -0.07782 | -0.091553 | 0.004578 | -0.036621 | 0.050354 | 0.13275 | -0.20142 | 0.22431 | -0.10986 | 0.3479 | 123.1476 | 0.14191 | 123.111 | 123.349 | 123.1522 | 123.0927 | 123.0606 | -123.3124 | -123.1476 | 122.8912 | 123.0194 | 58.4198 | 58.1589
715.8594 | 123.1796 | -58.667 | 64.4302 | -0.064087 | 0.0040653 | 0.06329 | 0.066723 | 0.0020037 | 0.00046993 | -0.0019162 | -0.19461 | 0.0018436 | 0.067044 | 0.06966 | -0.0062506 | 0.0086752 | -0.0014249 | -0.21973 | 64.4806 | -58.8821 | 64.2883 | -58.4747 | -58.9233 | -0.14191 | -0.10071 | 64.4485 | -58.6807 | 64.4165 | -58.5068 | -58.8547 | -58.5068 | -0.21515 | 0.050354 | -0.14191 | 0.19226 | 58.5251 | -0.25635 | 58.7402 | -0.041199 | -0.013733 | 0.01831 | -0.013733 | 0.16022 | 0.16022 | -0.18768 | 0.17395 | -0.17395 | 0.40741 | 123.1705 | 0.17395 | 123.0972 | 123.3627 | 123.1293 | 123.1476 | 123.1155 | -123.3124 | -123.111 | 122.9553 | 123.0835 | 58.4473 | 58.5663
716.8906 | 123.1934 | -58.6304 | 64.4211 | -0.10223 | 0.0017155 | 0.064785 | 0.069286 | 0.00093573 | -0.0014527 | -0.00020717 | -0.060333 | 0.0031254 | 0.067471 | 0.067097 | -0.0049688 | 0.0076072 | -0.0033475 | -0.17853 | 64.4943 | -58.8409 | 64.3158 | -58.4244 | -58.8776 | -0.059509 | -0.38452 | 64.4714 | -58.7036 | 64.4669 | -58.5068 | -58.7585 | -58.4518 | -0.21057 | 0.073242 | -0.10529 | 0.20599 | 58.5709 | -0.24719 | 58.7814 | -0.036621 | -0.073242 | 0.050354 | 0.045776 | 0.1236 | 0.17853 | -0.12817 | 0.25177 | -0.054932 | 0.41656 | 123.1567 | 0.19684 | 123.1705 | 123.3353 | 123.175 | 123.1247 | 123.1018 | -123.262 | -123.1247 | 122.9462 | 123.0972 | 58.4518 | 58.2458
717.8594 | 123.143 | -58.5663 | 64.5172 | -0.071716 | 0.0021427 | 0.063717 | 0.067791 | 0.0034991 | -0.00081187 | -0.001489 | -0.048126 | 0.0024844 | 0.069607 | 0.069447 | -0.0068914 | 0.0078208 | 0.0034885 | -0.20599 | 64.5172 | -58.7997 | 64.3433 | -58.3969 | -58.8593 | -0.059509 | -0.39825 | 64.4852 | -58.6533 | 64.3387 | -58.786 | -58.4198 | -58.1772 | -0.23346 | 0 | -0.17395 | 0.16937 | 58.5068 | -0.29297 | 58.7402 | -0.059509 | -0.086975 | -0.032044 | -0.17853 | -0.21973 | 0.3891 | 0.14648 | 0.47607 | 0.23346 | 0.40283 | 123.143 | -0.13275 | 122.9919 | 123.317 | 123.1384 | 123.0835 | 123.0515 | -123.317 | -123.1705 | 122.9095 | 122.905 | 58.3603 | 58.168
718.9062 | 123.3124 | -58.5251 | 64.4531 | -0.13275 | 0.0012881 | 0.062649 | 0.065228 | -0.0012005 | -0.0018799 | -0.002557 | 0.00070198 | 0.002698 | 0.068112 | 0.066883 | -0.0056098 | 0.0052572 | 7.0538e-05 | -0.17395 | 64.4943 | -58.7219 | 64.4348 | -58.2779 | -58.7631 | -0.018311 | -0.32501 | 64.4806 | -58.6075 | 64.6042 | -58.3374 | -58.6075 | -58.3054 | -0.19684 | 0.041199 | -0.018311 | 0.24719 | 58.5068 | -0.23804 | 58.7036 | -0.041199 | -0.082398 | 0.027466 | 0.15106 | 0.18768 | 0.21973 | -0.082398 | 0.30212 | 0 | 0.44403 | 123.1567 | 0.27008 | 123.2117 | 123.2162 | 123.0881 | 123.0194 | 123.0057 | -123.175 | -123.0606 | 122.9599 | 123.1293 | 58.3511 | 58.2001
719.8594 | 123.1705 | -58.5388 | 64.5676 | -0.071716 | 0.0021427 | 0.063076 | 0.070355 | -0.0035505 | -0.0020935 | 0.0010746 | -0.048126 | 0.0024844 | 0.068325 | 0.067311 | -0.0068914 | 0.0056846 | -0.0024931 | -0.20599 | 64.595 | -58.754 | 64.3066 | -58.287 | -58.7128 | -0.082397 | -0.44403 | 64.5813 | -58.5709 | 64.5401 | -58.4244 | -58.699 | -58.3786 | -0.21515 | 0.027466 | -0.26093 | 0.25177 | 58.4564 | -0.17395 | 58.6716 | 0.041198 | -0.032044 | 0.013733 | -0.027466 | 0.11444 | 0.16022 | -0.16022 | 0.19226 | -0.12817 | 0.46692 | 123.0606 | 0.14648 | 123.111 | 123.349 | 123.1522 | 123.1338 | 123.1201 | -123.3215 | -123.1384 | 122.8455 | 123.0789 | 58.3328 | 58.0948
720.8906 | 123.2758 | -58.4702 | 64.5493 | -0.056457 | 0.0017155 | 0.065426 | 0.066723 | 0.0032855 | 0.0017517 | 6.432e-06 | -0.035919 | 0.005048 | 0.070034 | 0.067311 | -0.0041144 | 0.0067526 | 0.0022067 | -0.23804 | 64.6133 | -58.7311 | 64.4165 | -58.3145 | -58.786 | -0.086975 | -0.42572 | 64.5447 | -58.5754 | 64.595 | -58.3282 | -58.6166 | -58.2962 | -0.26093 | 0.064087 | -0.13275 | 0.15564 | 58.3832 | -0.31586 | 58.6441 | -0.054932 | -0.10529 | -0.004577 | 0.045777 | 0.14191 | 0.17395 | -0.14648 | 0.27923 | -0.041199 | 0.41656 | 123.1476 | 0.24719 | 123.1705 | 123.3444 | 123.1201 | 123.0835 | 123.0148 | -123.2803 | -123.1247 | 122.8867 | 123.0652 | 58.2321 | 58.0444
721.8594 | 123.2162 | -58.4702 | 64.6133 | -0.071716 | 0.0015019 | 0.06329 | 0.067791 | 0.0026447 | -0.0012391 | -0.00063437 | -0.045074 | 0.00098899 | 0.06918 | 0.06432 | -0.013087 | 0.011239 | 0.0011385 | -0.18768 | 64.6408 | -58.6533 | 64.476 | -58.2733 | -58.7402 | -0.059509 | -0.37994 | 64.6179 | -58.5342 | 64.4394 | -58.0078 | -58.6624 | -58.3969 | -0.1831 | 0.027466 | -0.13733 | 0.19684 | 58.4106 | -0.27008 | 58.5938 | -0.086975 | -0.064087 | 0.004578 | -0.17395 | 0.46234 | 0.073242 | -0.19226 | 0.13733 | -0.12817 | 0.37994 | 123.1293 | 0.52643 | 122.9736 | 123.2941 | 123.1522 | 123.111 | 123.0881 | -123.2666 | -123.1476 | 122.9462 | 122.9095 | 58.2825 | 58.0902
722.8594 | 123.2071 | -58.461 | 64.6591 | -0.064087 | 0.0010745 | 0.063504 | 0.06715 | 0.0015765 | -0.0055115 | -0.00063437 | -0.045074 | 0.004407 | 0.069821 | 0.063465 | -0.0081732 | 0.0061118 | 0.0015659 | -0.21973 | 64.6912 | -58.6533 | 64.4485 | -58.2916 | -58.7585 | -0.086975 | -0.44861 | 64.6408 | -58.5022 | 64.6088 | -58.3282 | -58.6121 | -58.287 | -0.19226 | 0.032043 | -0.21057 | 0.16937 | 58.374 | -0.29755 | 58.5663 | -0.10529 | -0.041198 | -0.018311 | -0.050354 | 0.13275 | 0.17395 | -0.15106 | 0.21515 | -0.10986 | 0.36163 | 123.1018 | 0.17395 | 123.111 | 123.3444 | 123.143 | 123.1522 | 123.1018 | -123.3124 | -123.1613 | 122.9095 | 123.0698 | 58.2413 | 58.0124
723.8594 | 123.2162 | -58.4244 | 64.682 | -0.041199 | 0.0023563 | 0.063076 | 0.067577 | 0.00093573 | -0.00017087 | -0.0021298 | -0.060333 | 0.0022708 | 0.067044 | 0.064106 | -0.0047552 | 0.0071798 | -0.0016385 | -0.15564 | 64.7141 | -58.5709 | 64.5721 | -58.1589 | -58.6395 | -0.018311 | -0.32959 | 64.7186 | -58.4564 | 64.6957 | -58.2367 | -58.5388 | -58.2138 | -0.14648 | 0.032043 | -0.10986 | 0.2655 | 58.4061 | -0.21515 | 58.5526 | -0.068664 | -0.032044 | 0.036621 | 0.013733 | 0.18768 | 0.21057 | -0.11444 | 0.24262 | -0.082397 | 0.41199 | 123.143 | 0.21973 | 123.1522 | 123.2849 | 123.175 | 123.1384 | 123.143 | -123.2529 | -123.1384 | 122.9965 | 123.1201 | 58.2687 | 58.0948
724.8594 | 123.1842 | -58.3603 | 64.7186 | -0.10223 | -0.00042094 | 0.064358 | 0.068005 | 0.0017901 | -0.0016663 | -0.001489 | -0.045074 | 0.0037662 | 0.069821 | 0.06902 | -0.0064642 | 0.0067526 | 0.0013521 | -0.21057 | 64.7598 | -58.5663 | 64.5126 | -58.2413 | -58.6899 | -0.10071 | -0.44403 | 64.7186 | -58.4152 | 64.682 | -58.2504 | -58.5526 | -58.2001 | -0.20599 | 0.041199 | -0.20599 | 0.11902 | 58.2596 | -0.32959 | 58.4656 | -0.1236 | -0.054931 | 0 | -0.036621 | 0.10986 | 0.16022 | -0.19226 | 0.21515 | -0.13733 | 0.32501 | 123.0789 | 0.16479 | 123.0972 | 123.3261 | 123.1338 | 123.1201 | 123.0789 | -123.2849 | -123.1338 | 122.8729 | 123.0423 | 58.1497 | 57.9163
725.8906 | 123.1979 | -58.2962 | 64.7919 | -0.071716 | 0.0012881 | 0.061581 | 0.065868 | 0.0032855 | -0.0027345 | -0.004266 | -0.017609 | 0.0020572 | 0.068325 | 0.064961 | -0.0056098 | 0.00483 | 0.0041293 | -0.16937 | 64.8331 | -58.5114 | 64.595 | -58.1223 | -58.5846 | 0.022888 | -0.32044 | 64.7873 | -58.3603 | 64.7278 | -58.1543 | -58.4244 | -58.1497 | -0.21515 | 0.041199 | -0.19684 | 0.17395 | 58.3191 | -0.28839 | 58.5342 | -0.073242 | -0.064087 | -0.004578 | -0.064087 | 0.14191 | 0.14649 | -0.12817 | 0.21057 | -0.064086 | 0.3891 | 123.1064 | 0.20599 | 123.0881 | 123.3444 | 123.1476 | 123.1293 | 123.0835 | -123.3032 | -123.1522 | 122.8912 | 123.024 | 58.1268 | 57.9758
726.8594 | 123.2117 | -58.3099 | 64.7781 | -0.094604 | 0.0023563 | 0.06329 | 0.069286 | 0.0032855 | -0.0029481 | -0.0036252 | -0.066437 | 0.0056888 | 0.06918 | 0.065388 | -0.0086004 | 0.006539 | 0.00092494 | -0.20599 | 64.8056 | -58.5251 | 64.5813 | -58.1314 | -58.6121 | -0.068665 | -0.44403 | 64.7964 | -58.3603 | 64.7507 | -58.1772 | -58.4747 | -58.136 | -0.21515 | 0.027466 | -0.19684 | 0.17853 | 58.2413 | -0.30212 | 58.4564 | -0.086976 | -0.050354 | 0.018311 | -0.027466 | 0.13275 | 0.17395 | -0.16479 | 0.2243 | -0.11444 | 0.39368 | 123.1064 | 0.18311 | 123.111 | 123.3307 | 123.1567 | 123.1155 | 123.1064 | -123.3032 | -123.1384 | 122.8912 | 123.0606 | 58.1039 | 57.8659
727.8906 | 123.23 | -58.2275 | 64.8193 | -0.064087 | 0.00086086 | 0.064358 | 0.068005 | 0.0015765 | -0.0018799 | -0.00063437 | -0.042023 | 0.0052616 | 0.068112 | 0.06902 | -0.0053962 | 0.0044028 | 0.0064791 | -0.11444 | 64.8972 | -58.4518 | 64.7186 | -57.9941 | -58.4656 | 0.013733 | -0.2655 | 64.8331 | -58.3008 | 64.8376 | -58.0673 | -58.3557 | -58.0536 | -0.2243 | 0.07782 | -0.10071 | 0.23346 | 58.2413 | -0.23804 | 58.4656 | -0.013733 | -0.073242 | 0.013733 | 0.01831 | 0.16022 | 0.17395 | -0.12817 | 0.24719 | -0.054932 | 0.45776 | 123.1705 | 0.23346 | 123.1384 | 123.349 | 123.1338 | 123.1247 | 123.0606 | -123.2712 | -123.1201 | 122.9462 | 123.0652 | 58.1131 | 57.962
728.8594 | 123.2208 | -58.2321 | 64.8468 | -0.071716 | 0.0027835 | 0.06329 | 0.067364 | 8.1126e-05 | -0.0014527 | -0.0040524 | -0.035919 | 0.003339 | 0.071316 | 0.066029 | -0.0045416 | 0.0056846 | -0.0031339 | -0.18768 | 64.8972 | -58.4427 | 64.6683 | -58.0582 | -58.5342 | -0.064087 | -0.40741 | 64.8331 | -58.3054 | 64.8514 | -58.0948 | -58.3786 | -58.0627 | -0.21057 | 0.050354 | -0.17853 | 0.17395 | 58.168 | -0.30212 | 58.3786 | -0.091553 | -0.073242 | -0.013733 | 0.004577 | 0.13733 | 0.16937 | -0.14648 | 0.24262 | -0.073242 | 0.38452 | 123.111 | 0.21057 | 123.1567 | 123.3398 | 123.1384 | 123.1293 | 123.0652 | -123.2895 | -123.1522 | 122.9004 | 123.0835 | 58.0444 | 57.8247
729.8906 | 123.2071 | -58.1589 | 64.9338 | 0.012207 | 0.0025699 | 0.061581 | 0.067364 | -0.0018415 | -0.0010255 | -0.0046934 | 0.012909 | 0.0037662 | 0.069821 | 0.062184 | -0.004328 | 0.0029074 | 0.00092494 | -0.11902 | 64.9841 | -58.3466 | 64.7507 | -57.9254 | -58.4106 | 0.050354 | -0.27466 | 64.9246 | -58.2001 | 64.8926 | -57.9849 | -58.2779 | -58.0124 | -0.18768 | 0.050354 | -0.18311 | 0.23346 | 58.2092 | -0.25177 | 58.3969 | -0.064087 | -0.041198 | -0.009155 | -0.041199 | 0.17395 | 0.14648 | -0.11902 | 0.18768 | -0.07782 | 0.42114 | 123.0972 | 0.21515 | 123.0927 | 123.3307 | 123.1247 | 123.143 | 123.0835 | -123.2803 | -123.1339 | 122.9095 | 123.0515 | 58.0399 | 57.8842
730.8594 | 123.175 | -58.136 | 64.9429 | -0.13275 | 0.00064726 | 0.062649 | 0.06715 | 0.0013629 | 0.00025633 | -0.00020717 | -0.078644 | 0.003339 | 0.067471 | 0.068806 | -0.0079596 | 0.00483 | -0.00078406 | -0.13275 | 64.9338 | -58.4106 | 64.8285 | -57.8476 | -58.4793 | -0.027466 | -0.36621 | 64.9429 | -58.223 | 64.9017 | -58.0032 | -58.3237 | -58.0032 | -0.27466 | -0.009155 | -0.11444 | 0.28839 | 58.1085 | -0.34332 | 58.3832 | -0.068664 | -0.086975 | 0 | -0.041199 | 0.13275 | 0.13275 | -0.18768 | 0.21973 | -0.10071 | 0.56305 | 123.2391 | 0.21973 | 123.1247 | 123.3444 | 123.1659 | 123.0698 | 123.0789 | -123.3536 | -123.1659 | 122.9645 | 123.0377 | 58.0032 | 57.7698
731.8906 | 123.23 | -58.0856 | 65.0116 | -0.15564 | 0.0032107 | 0.066067 | 0.0695 | -0.00077327 | -0.0014527 | -0.0019162 | -0.017609 | 0.0041934 | 0.069607 | 0.065174 | -0.0066778 | 0.006539 | -0.0016385 | -0.23804 | 65.0345 | -58.3145 | 64.8514 | -57.8522 | -58.3145 | 0.07782 | -0.23346 | 64.9979 | -58.1497 | 64.9979 | -57.8705 | -58.1909 | -57.9025 | -0.22888 | 0.022888 | -0.16022 | 0.23346 | 58.1635 | -0.22888 | 58.3923 | 0 | -0.064087 | -0.013733 | -0.013733 | 0.21515 | 0.1831 | -0.10529 | 0.24719 | -0.041199 | 0.46234 | 123.1659 | 0.27924 | 123.1476 | 123.349 | 123.1476 | 123.1201 | 123.0835 | -123.3261 | -123.1613 | 122.937 | 123.0835 | 57.8476 | 57.8522
732.8594 | 123.1888 | -58.0811 | 65.0162 | -0.041199 | 0.0010745 | 0.063931 | 0.069714 | 0.0034991 | -0.0018799 | -0.0021298 | -0.087799 | 0.0046206 | 0.069607 | 0.06667 | -0.0058234 | 0.0050436 | -0.0048429 | -0.16022 | 65.007 | -58.3191 | 64.8422 | -57.9025 | -58.3694 | -0.041199 | -0.39825 | 65.0208 | -58.1451 | 64.9475 | -57.9575 | -58.2779 | -57.9437 | -0.23804 | -0.009155 | -0.17395 | 0.17853 | 58.0399 | -0.28839 | 58.2779 | -0.050354 | -0.064087 | 0.004578 | -0.068664 | 0.1236 | 0.13733 | -0.19684 | 0.20142 | -0.13275 | 0.41656 | 123.1613 | 0.18768 | 123.0927 | 123.3261 | 123.1659 | 123.0881 | 123.1018 | -123.3353 | -123.1613 | 122.9233 | 123.0286 | 57.9208 | 57.6828
733.8906 | 123.1979 | -57.9849 | 65.0803 | -0.12512 | 0.0021427 | 0.062008 | 0.068432 | -0.00013247 | -0.0035889 | -0.0061886 | 0.0037536 | 0.0046206 | 0.070889 | 0.059193 | -0.006037 | 0.0058982 | -0.0018521 | -0.050354 | 65.1306 | -58.2184 | 64.92 | -57.7744 | -58.2413 | 0.073242 | -0.24719 | 65.0757 | -58.0856 | 65.0391 | -57.843 | -58.1177 | -57.8522 | -0.23346 | 0.050354 | -0.16022 | 0.21057 | 58.0582 | -0.25635 | 58.2916 | -0.022888 | -0.10071 | -0.004577 | -0.041199 | 0.14191 | 0.13275 | -0.13275 | 0.23346 | -0.032044 | 0.44403 | 123.1384 | 0.24261 | 123.1247 | 123.349 | 123.1613 | 123.1155 | 123.0606 | -123.2986 | -123.1659 | 122.905 | 123.024 | 57.9346 | 57.7377
734.8594 | 123.1888 | -57.9895 | 65.1123 | -0.064087 | 0.0017155 | 0.064785 | 0.068646 | 0.0032855 | -0.0012391 | -0.0087522 | -0.13358 | 0.0037662 | 0.06918 | 0.063252 | -0.0056098 | 0.0076072 | -0.0018521 | -0.12817 | 65.1352 | -58.1909 | 64.6408 | -58.1177 | -57.8888 | 0.13275 | -0.1831 | 65.1215 | -58.0399 | 65.0757 | -57.8293 | -58.1543 | -57.8522 | -0.20142 | 0.022888 | -0.4715 | -0.12817 | 58.1223 | 0.10071 | 58.3237 | 0.30212 | -0.050354 | 0.009155 | -0.036621 | 0.16022 | 0.13733 | -0.16479 | 0.18768 | -0.11444 | 0.073242 | 122.8317 | 0.21057 | 123.1155 | 123.3261 | 123.1613 | 123.1247 | 123.111 | -123.3032 | -123.1522 | 122.6303 | 123.0652 | 57.8613 | 57.8064
735.8906 | 123.1934 | -57.9391 | 65.1764 | 0.042725 | 0.0010745 | 0.062008 | 0.066296 | -0.0016279 | -0.0023071 | -0.002557 | -0.0084534 | 0.0014164 | 0.069393 | 0.060475 | -0.008814 | 0.0050436 | -0.0027067 | -0.11444 | 65.1993 | -58.136 | 64.9933 | -57.7194 | -58.1909 | 0.064087 | -0.26093 | 65.1535 | -57.9758 | 65.126 | -57.724 | -58.049 | -57.7652 | -0.19684 | 0.022888 | -0.18311 | 0.21973 | 58.0032 | -0.25177 | 58.2001 | -0.054932 | -0.036621 | -0.022889 | -0.050354 | 0.21515 | 0.17395 | -0.10986 | 0.21057 | -0.073242 | 0.41657 | 123.1293 | 0.25177 | 123.1018 | 123.3353 | 123.1293 | 123.1384 | 123.0927 | -123.3124 | -123.1522 | 122.9324 | 123.0652 | 57.8247 | 57.6782
736.8594 | 123.2437 | -57.8888 | 65.1993 | -0.041199 | 0.0027835 | 0.063504 | 0.066937 | 0.0039263 | -0.0048707 | -0.0021298 | -0.035919 | 0.0031254 | 0.06918 | 0.061543 | -0.0068914 | 0.0086752 | -0.0018521 | -0.07782 | 65.2084 | -58.1085 | 65.062 | -57.6233 | -58.136 | 0.068665 | -0.19226 | 65.1901 | -57.9575 | 65.2039 | -57.6691 | -58.0032 | -57.7103 | -0.21973 | 0.009155 | -0.13733 | 0.2655 | 57.9575 | -0.24719 | 58.1772 | -0.027465 | -0.068664 | -0.009155 | 0.004577 | 0.21973 | 0.17853 | -0.11444 | 0.24719 | -0.045777 | 0.48523 | 123.1705 | 0.28839 | 123.1613 | 123.317 | 123.1476 | 123.0972 | 123.0789 | -123.3078 | -123.1567 | 122.9507 | 123.0927 | 57.811 | 57.6965
737.8906 | 123.3536 | -57.843 | 65.2634 | -0.0030519 | 0.0015019 | 0.063504 | 0.067364 | 0.00072213 | -0.0027345 | -0.00084817 | 0.0098572 | 0.0018436 | 0.06918 | 0.060475 | -0.0047552 | 0.0061118 | 0.0024203 | -0.091553 | 65.3091 | -58.0627 | 65.0574 | -57.6324 | -58.0902 | 0.068665 | -0.24261 | 65.2725 | -57.9346 | 65.2771 | -57.8201 | -58.2367 | -57.8705 | -0.21973 | 0.045776 | -0.20599 | 0.21057 | 57.9117 | -0.24719 | 58.1314 | -0.027466 | -0.091552 | 0.009155 | 0.013733 | 0.022889 | -0.027465 | -0.39368 | 0.064087 | -0.30212 | 0.4303 | 123.1201 | 0.11444 | 123.2117 | 123.3719 | 123.2071 | 123.1522 | 123.1155 | -123.3261 | -123.1979 | 122.9004 | 123.1201 | 57.7515 | 57.6004
738.8594 | 123.1934 | -57.8156 | 65.2588 | -0.079346 | 0.0023563 | 0.065426 | 0.068432 | 0.0043537 | -0.0023071 | -0.0012754 | -0.13052 | 0.0029116 | 0.06683 | 0.066242 | -0.0066778 | 0.0069662 | -0.0027067 | -0.13275 | 65.2863 | -58.049 | 65.0848 | -57.6141 | -58.0994 | 0.009155 | -0.009155 | 65.2634 | -57.8842 | 65.2084 | -57.5958 | -58.0124 | -57.6828 | -0.23346 | 0.027466 | -0.17395 | 0.20142 | 57.8247 | -0.28381 | 58.0582 | -0.050354 | -0.068664 | 0.004578 | -0.050354 | 0.21973 | 0.13275 | -0.19684 | 0.20142 | -0.12817 | 0.43487 | 123.1338 | 0.28839 | 123.0927 | 123.3353 | 123.1476 | 123.1018 | 123.0789 | -123.3078 | -123.143 | 122.9004 | 123.024 | 57.6828 | 57.8064
739.8906 | 123.1934 | -57.7835 | 65.3366 | -0.064087 | 0.0019291 | 0.063076 | 0.068646 | -0.00055967 | -0.0035889 | -0.001489 | -0.0054016 | 0.0024844 | 0.06918 | 0.056629 | -0.0062506 | 0.0044028 | 0.0049837 | -0.09613 | 65.3778 | -57.9712 | 65.1398 | -57.5363 | -58.0124 | 0.09613 | -0.22888 | 65.332 | -57.8156 | 65.2725 | -57.5592 | -57.8934 | -57.6187 | -0.18768 | 0.041199 | -0.19684 | 0.24719 | 57.8796 | -0.22888 | 58.0673 | -0.041199 | -0.032044 | -0.004578 | -0.064087 | 0.2243 | 0.16479 | -0.10986 | 0.19684 | -0.07782 | 0.43487 | 123.111 | 0.25635 | 123.0881 | 123.349 | 123.1476 | 123.1613 | 123.1155 | -123.3078 | -123.1522 | 122.9233 | 123.056 | 57.6874 | 57.5546
740.8594 | 123.2162 | -57.7377 | 65.3549 | -0.056457 | 0.0027835 | 0.063076 | 0.068432 | 0.0037127 | -0.0042297 | 0.003638 | -0.032867 | 0.0039798 | 0.06918 | 0.065174 | -0.0075324 | 0.0056846 | -0.00014306 | -0.09613 | 65.3732 | -57.9803 | 65.2039 | -57.5043 | -58.0124 | 0.036621 | -0.23804 | 65.3275 | -57.8201 | 65.332 | -57.5363 | -57.8934 | -57.5729 | -0.24262 | 0.018311 | -0.15106 | 0.23346 | 57.7744 | -0.27466 | 58.017 | -0.032043 | -0.082397 | -0.027465 | -0.022888 | 0.20142 | 0.16479 | -0.15564 | 0.24719 | -0.073243 | 0.47608 | 123.1842 | 0.28381 | 123.1522 | 123.3536 | 123.1476 | 123.111 | 123.0652 | -123.3353 | -123.175 | 122.9416 | 123.0698 | 57.6416 | 57.4997
741.8906 | 123.2437 | -57.6691 | 65.3915 | -0.056457 | 0.0015019 | 0.062863 | 0.066937 | 0.0028583 | -0.0033753 | 6.432e-06 | -0.026764 | 0.003339 | 0.068539 | 0.062184 | -0.0083868 | 0.0073936 | -0.00014306 | -0.041199 | 65.4144 | -57.9025 | 65.2634 | -57.4081 | -57.93 | 0.10071 | -0.15106 | 65.3824 | -57.7332 | 65.4053 | -57.4631 | -57.7744 | -57.4951 | -0.23346 | 0.022888 | -0.12817 | 0.26093 | 57.7698 | -0.26093 | 58.0032 | -0.027466 | -0.064087 | -0.009156 | 0.013732 | 0.20599 | 0.17395 | -0.10529 | 0.23804 | -0.041199 | 0.49439 | 123.1659 | 0.27008 | 123.1384 | 123.317 | 123.1155 | 123.0835 | 123.0515 | -123.2941 | -123.1247 | 122.9324 | 123.0743 | 57.6279 | 57.518
742.8594 | 123.2391 | -57.6645 | 65.4373 | -0.10223 | 0.0021427 | 0.062008 | 0.068859 | 0.00072213 | -0.0027345 | -0.0017026 | -0.051178 | 0.0022708 | 0.069821 | 0.061756 | -0.0051824 | 0.003762 | -0.00035666 | -0.054932 | 65.4648 | -57.8613 | 65.2863 | -57.3898 | -57.9117 | 0.091553 | -0.19226 | 65.4373 | -57.7332 | 65.4327 | -57.4402 | -57.7972 | -57.4722 | -0.19684 | 0.027466 | -0.15106 | 0.27466 | 57.756 | -0.24719 | 57.9529 | -0.050354 | -0.068664 | 0 | -0.004578 | 0.2243 | 0.19226 | -0.13275 | 0.26093 | -0.064087 | 0.4715 | 123.1476 | 0.29297 | 123.1659 | 123.3261 | 123.1705 | 123.1293 | 123.1018 | -123.2986 | -123.1705 | 122.9507 | 123.0972 | 57.6096 | 57.4722
743.8906 | 123.2208 | -57.6141 | 65.4831 | 0.019837 | 0.00086086 | 0.062863 | 0.068859 | -0.00034607 | -0.00017087 | -0.0017026 | -0.017609 | 0.0035526 | 0.068112 | 0.071156 | -0.006037 | 0.0063254 | -0.0014249 | -0.068665 | 65.5289 | -57.811 | 65.3 | -57.3715 | -57.8476 | 0.10071 | -0.21515 | 65.4648 | -57.6874 | 65.4602 | -57.3761 | -57.7148 | -57.4173 | -0.19684 | 0.045777 | -0.1831 | 0.24262 | 57.7148 | -0.23346 | 57.9117 | -0.036621 | -0.073242 | -0.01831 | -0.022888 | 0.23804 | 0.19684 | -0.10071 | 0.27008 | -0.027466 | 0.43945 | 123.111 | 0.31128 | 123.1476 | 123.3398 | 123.1522 | 123.143 | 123.0789 | -123.2941 | -123.1705 | 122.9141 | 123.0743 | 57.5455 | 57.399
744.8594 | 123.2208 | -57.5546 | 65.506 | -0.056457 | 0.0012881 | 0.063717 | 0.067364 | 8.1126e-05 | -0.0010255 | -0.0012754 | -0.042023 | 0.0063296 | 0.067898 | 0.065602 | -0.0062506 | 0.0058982 | 0.0030611 | -0.036621 | 65.5197 | -57.7927 | 65.3778 | -57.2754 | -57.811 | 0.10529 | -0.17395 | 65.5014 | -57.6462 | 65.5106 | -57.3212 | -57.6874 | -57.3853 | -0.23804 | 0.013733 | -0.12817 | 0.27923 | 57.6599 | -0.25635 | 57.898 | -0.01831 | -0.091553 | -0.004577 | 0.004578 | 0.23346 | 0.16937 | -0.13275 | 0.26092 | -0.041199 | 0.51727 | 123.1705 | 0.32501 | 123.1567 | 123.3124 | 123.1476 | 123.0743 | 123.056 | -123.2986 | -123.1522 | 122.9324 | 123.0652 | 57.518 | 57.3807
745.8906 | 123.1979 | -57.518 | 65.5792 | -0.041199 | 0.0036381 | 0.060086 | 0.0695 | 0.0024311 | -0.0050843 | -0.0029844 | 0.012909 | 0.003339 | 0.068753 | 0.064106 | -0.0047552 | 0.0044028 | 0.0028475 | -0.068665 | 65.6158 | -57.7469 | 65.387 | -57.28 | -57.7744 | 0.11902 | -0.1831 | 65.5472 | -57.5684 | 65.5243 | -57.3074 | -57.6508 | -57.3715 | -0.22888 | 0.036621 | -0.19226 | 0.23804 | 57.637 | -0.25635 | 57.8659 | -0.027466 | -0.050354 | -0.032044 | -0.054932 | 0.21057 | 0.14648 | -0.13275 | 0.19684 | -0.082398 | 0.46692 | 123.1338 | 0.26093 | 123.0927 | 123.3627 | 123.1155 | 123.1338 | 123.0652 | -123.3261 | -123.1476 | 122.905 | 123.0423 | 57.4493 | 57.3349
746.8594 | 123.2117 | -57.4951 | 65.6158 | -0.13275 | 0.0021427 | 0.063504 | 0.068432 | 0.0020037 | 4.273e-05 | -0.0017026 | -0.035919 | 0.0035526 | 0.071743 | 0.062397 | -0.0090278 | 0.0073936 | -0.0022793 | -0.064087 | 65.6113 | -57.6965 | 65.4465 | -57.2205 | -57.7698 | 0.086975 | -0.20142 | 65.5792 | -57.55 | 65.5518 | -57.2845 | -57.6462 | -57.3349 | -0.20142 | -0.004578 | -0.16937 | 0.27466 | 57.5821 | -0.27466 | 57.7835 | -0.073242 | -0.054932 | -0.036621 | -0.064087 | 0.21057 | 0.16022 | -0.15106 | 0.21515 | -0.09613 | 0.47607 | 123.143 | 0.2655 | 123.1018 | 123.3078 | 123.1293 | 123.1064 | 123.0743 | -123.3124 | -123.1659 | 122.9416 | 123.0469 | 57.431 | 57.2937
747.9062 | 123.1934 | -57.4631 | 65.6067 | -0.048828 | 0.0017155 | 0.063717 | 0.068218 | 0.0041399 | -0.0020935 | -0.0019162 | -0.045074 | 0.0031254 | 0.070248 | 0.060688 | -0.0056098 | 0.006539 | -0.00057046 | -0.10986 | 65.6479 | -57.6691 | 65.419 | -57.2433 | -57.7789 | 0.032043 | -0.27008 | 65.5975 | -57.55 | 65.6067 | -57.2617 | -57.6187 | -57.2891 | -0.20599 | 0.041199 | -0.18768 | 0.21973 | 57.4951 | -0.31586 | 57.7011 | -0.10986 | -0.086975 | -0.009155 | 0 | 0.20142 | 0.17395 | -0.15564 | 0.26093 | -0.068664 | 0.42572 | 123.0881 | 0.28839 | 123.1567 | 123.317 | 123.1476 | 123.111 | 123.0606 | -123.2758 | -123.1567 | 122.8821 | 123.0698 | 57.3532 | 57.193
748.8594 | 123.2025 | -57.4127 | 65.6891 | -0.048828 | 0.0017155 | 0.061795 | 0.068859 | 0.0028583 | -0.0016663 | -0.00042077 | -0.060333 | 0.0014164 | 0.068966 | 0.062611 | -0.0066778 | 0.0058982 | -0.0020657 | -0.018311 | 65.6891 | -57.6141 | 65.5563 | -57.1014 | -57.6508 | 0.10986 | -0.14648 | 65.6616 | -57.4997 | 65.6662 | -57.1609 | -57.5592 | -57.2388 | -0.20142 | 0 | -0.13275 | 0.31128 | 57.5226 | -0.23804 | 57.724 | -0.036621 | -0.086975 | -0.027466 | -0.022888 | 0.25177 | 0.17395 | -0.14648 | 0.26093 | -0.059509 | 0.5127 | 123.1705 | 0.33875 | 123.1659 | 123.3032 | 123.1613 | 123.1018 | 123.0743 | -123.3032 | -123.1888 | 122.9691 | 123.0789 | 57.3944 | 57.2662
749.8906 | 123.23 | -57.3486 | 65.7028 | -0.064087 | 0.0015019 | 0.062649 | 0.0648 | -0.00034607 | -0.0029481 | -0.0034116 | 0.12888 | 0.0024844 | 0.070675 | 0.06902 | -0.0041144 | 0.0054708 | -0.00057046 | 0 | 65.744 | -57.5455 | 65.6158 | -57.0099 | -57.55 | 0.26093 | -0.24719 | 65.744 | -57.399 | 65.712 | -57.1152 | -57.4585 | -57.1976 | -0.19684 | 0.041199 | -0.086975 | 0.33875 | 57.6096 | -0.20142 | 57.8064 | -0.004578 | -0.050354 | 0.041199 | 0.009155 | 0.23346 | 0.15106 | -0.10986 | 0.20142 | -0.059509 | 0.53558 | 123.1613 | 0.28381 | 123.111 | 123.2895 | 123.143 | 123.0927 | 123.0927 | -123.2483 | -123.1018 | 122.9645 | 123.0606 | 57.3486 | 57.1014
750.8594 | 123.2346 | -57.2983 | 65.7532 | -0.11749 | 0.00064726 | 0.068844 | 0.069286 | 0.0054217 | -0.0016663 | -0.00020717 | -0.042023 | 0.0035526 | 0.068966 | 0.068165 | -0.0079596 | 0.0067526 | -0.00099766 | -0.09613 | 65.7806 | -57.5409 | 65.7349 | -57.0465 | -57.5043 | 0.1831 | -0.07782 | 65.7486 | -57.3807 | 65.7761 | -57.0374 | -57.4448 | -57.1198 | -0.24262 | 0.027466 | -0.018311 | 0.25177 | 57.4814 | -0.20599 | 57.724 | 0.036622 | -0.082397 | -0.004578 | 0.022888 | 0.26093 | 0.17853 | -0.14648 | 0.26093 | -0.064087 | 0.49439 | 123.2758 | 0.34332 | 123.1567 | 123.3215 | 123.1293 | 123.0789 | 123.0469 | -123.2941 | -123.1338 | 123.0331 | 123.0743 | 57.2021 | 57.2205
751.8906 | 123.1384 | -57.2479 | 65.831 | -0.033569 | 0.0051333 | 0.060513 | 0.067577 | 0.0020037 | -0.0018799 | -0.0012754 | -0.038971 | 0.0031254 | 0.067257 | 0.063465 | -0.0073188 | 0.0091024 | 0.00028414 | -0.036621 | 65.8447 | -57.486 | 65.6616 | -57.0053 | -57.5043 | 0.15106 | -0.14648 | 65.8127 | -57.3257 | 65.6433 | -56.9138 | -57.193 | -57.0694 | -0.23804 | 0.013733 | -0.16937 | 0.24262 | 57.399 | -0.25635 | 57.637 | -0.01831 | -0.07782 | -0.018311 | -0.18768 | 0.33417 | 0.17853 | 0.054932 | 0.25635 | 0.13275 | 0.48065 | 123.1476 | 0.41199 | 122.9691 | 123.3307 | 123.1384 | 123.0927 | 123.0606 | -123.317 | -123.1567 | 122.9095 | 122.8912 | 57.2113 | 57.1014
752.8594 | 123.2162 | -57.2433 | 65.8447 | -0.071716 | 0.00086086 | 0.062863 | 0.067577 | 0.0020037 | -0.0014527 | 0.00064723 | -0.05423 | 0.0039798 | 0.068325 | 0.065388 | -0.0086004 | 0.0061118 | -0.0016385 | -0.013733 | 65.863 | -57.4631 | 65.6982 | -56.9229 | -57.4905 | 0.1236 | -0.12817 | 65.8218 | -57.3029 | 65.8264 | -56.9916 | -57.3944 | -57.0648 | -0.21973 | 0.01831 | -0.14649 | 0.32043 | 57.3669 | -0.24719 | 57.5867 | -0.027466 | -0.059509 | -0.022889 | -0.018311 | 0.25177 | 0.17853 | -0.15106 | 0.23804 | -0.091553 | 0.54016 | 123.1613 | 0.31128 | 123.1293 | 123.3261 | 123.1247 | 123.1064 | 123.0652 | -123.3078 | -123.1476 | 122.9416 | 123.0698 | 57.2296 | 57.1152
753.8906 | 123.2208 | -57.1793 | 65.8722 | -0.033569 | 0.0017155 | 0.062222 | 0.06715 | -0.00098687 | -0.0020935 | -0.0010618 | -0.051178 | 0.0035526 | 0.067898 | 0.073719 | -0.006037 | 0.0084616 | -0.0020657 | -0.004578 | 65.9134 | -57.4127 | 65.7578 | -56.8634 | -57.4448 | 0.15564 | -0.091553 | 65.8676 | -57.2754 | 65.9134 | -56.9138 | -57.3074 | -57.0053 | -0.23346 | 0.041199 | -0.11444 | 0.31586 | 57.3349 | -0.2655 | 57.5684 | -0.032043 | -0.096131 | -0.004577 | 0.041199 | 0.2655 | 0.17395 | -0.12817 | 0.27008 | -0.032043 | 0.54932 | 123.1705 | 0.36163 | 123.1888 | 123.3261 | 123.143 | 123.0927 | 123.0469 | -123.2849 | -123.1476 | 122.937 | 123.0927 | 57.1747 | 57.0877
754.8594 | 123.2208 | -57.1426 | 65.9271 | -0.048828 | 0.0027835 | 0.062436 | 0.068432 | 0.00029473 | -0.0029481 | -0.0038388 | -0.026764 | 0.0029116 | 0.066403 | 0.055348 | -0.0058234 | 0.0063254 | -0.0031339 | 0.013733 | 65.9821 | -57.3578 | 65.799 | -56.8222 | -57.3853 | 0.16479 | -0.086975 | 65.9409 | -57.2159 | 65.9271 | -56.8771 | -57.2662 | -56.9733 | -0.21515 | 0.054932 | -0.12817 | 0.32043 | 57.3074 | -0.24262 | 57.5226 | -0.027466 | -0.073242 | 0.013733 | 0 | 0.2655 | 0.16937 | -0.1236 | 0.24261 | -0.050354 | 0.53558 | 123.1567 | 0.33875 | 123.143 | 123.3398 | 123.1567 | 123.1247 | 123.0835 | -123.2849 | -123.143 | 122.9416 | 123.0698 | 57.1564 | 57.0557
755.8906 | 123.3536 | -57.0923 | 65.9363 | -0.02594 | -0.0027707 | 0.056668 | 0.06715 | -0.0016279 | 4.273e-05 | -0.0036252 | 0.052582 | 0.0018436 | 0.069607 | 0.054493 | -0.0068914 | 0.0078208 | 0.00092494 | 0.27466 | 66.0049 | -57.2571 | 65.9271 | -56.7261 | -57.2937 | 0.25635 | 0.032043 | 65.9454 | -57.1426 | 66.0599 | -56.7078 | -57.0786 | -56.8039 | -0.1648 | 0.068665 | -0.009155 | 0.36621 | 57.3486 | -0.20142 | 57.5134 | -0.036621 | -0.050354 | 0.009156 | 0.1236 | 0.38452 | 0.28839 | 0.013733 | 0.33875 | 0.064087 | 0.53101 | 123.1842 | 0.43488 | 123.2025 | 123.262 | 123.0881 | 123.0972 | 123.0377 | -123.1934 | -123.0789 | 123.0194 | 123.1522 | 57.3669 | 57.1243
756.8594 | 123.2071 | -57.0877 | 66.0278 | -0.10223 | 0.0027835 | 0.062008 | 0.068646 | 0.0047809 | -0.0016663 | -0.0023434 | -0.051178 | 0.0046206 | 0.068539 | 0.067951 | -0.009455 | 0.006539 | -0.00035666 | 0 | 66.0141 | -57.2754 | 65.8813 | -56.7627 | -57.3303 | 0.13275 | -0.10529 | 66.0049 | -57.1472 | 65.9912 | -56.7993 | -57.2021 | -56.9183 | -0.18768 | -0.013733 | -0.14648 | 0.32501 | 57.2205 | -0.24261 | 57.4081 | -0.054931 | -0.059509 | -0.022888 | -0.036621 | 0.28839 | 0.16937 | -0.11444 | 0.22888 | -0.054931 | 0.5127 | 123.1567 | 0.3479 | 123.1384 | 123.2895 | 123.1522 | 123.1018 | 123.0927 | -123.3032 | -123.175 | 122.9691 | 123.0789 | 57.0877 | 56.9824
757.8906 | 123.2071 | -57.0236 | 66.0782 | -0.01831 | -0.0010617 | 0.063076 | 0.066509 | -0.0014143 | -0.0010255 | -0.0036252 | -0.0084534 | 0.0035526 | 0.069607 | 0.069447 | -0.0066778 | 0.0052572 | -0.0014249 | -0.022888 | 66.1148 | -57.2205 | 65.8951 | -56.7215 | -57.2617 | 0.15564 | -0.11902 | 66.0965 | -57.074 | 66.0324 | -56.7535 | -57.1381 | -56.8588 | -0.19684 | 0.036621 | -0.1831 | 0.30212 | 57.1793 | -0.23804 | 57.3761 | -0.041199 | -0.050354 | 0.018311 | -0.045776 | 0.27008 | 0.16479 | -0.11444 | 0.21515 | -0.064087 | 0.49896 | 123.1155 | 0.32043 | 123.1064 | 123.3353 | 123.1705 | 123.1384 | 123.1201 | -123.2986 | -123.1522 | 122.9187 | 123.056 | 57.0007 | 56.9046
758.8594 | 123.2162 | -56.9824 | 66.1194 | -0.086975 | 0.0044925 | 0.065854 | 0.068218 | 0.00029473 | -0.0012391 | -0.001489 | -0.084747 | 0.00163 | 0.069393 | 0.077778 | -0.0090278 | 0.0054708 | -0.0035611 | -0.022888 | 66.1331 | -57.2296 | 65.9409 | -56.6849 | -57.2891 | 0.10986 | -0.14191 | 66.0873 | -57.0648 | 66.2704 | -56.8451 | -57.1655 | -56.7581 | -0.24719 | 0.013733 | -0.17853 | 0.29755 | 57.0923 | -0.3067 | 57.3395 | -0.05951 | -0.082397 | -0.032044 | 0.15106 | 0.13733 | 0.2243 | -0.1831 | 0.3067 | -0.10071 | 0.54474 | 123.1705 | 0.21973 | 123.3353 | 123.3627 | 123.1522 | 123.1155 | 123.0698 | -123.349 | -123.1842 | 122.9233 | 123.2529 | 56.9595 | 56.8405
759.8906 | 123.2162 | -56.9138 | 66.1423 | -0.071716 | 0.0032107 | 0.063076 | 0.067577 | 0.0022173 | 0.0011109 | 0.00064723 | -0.051178 | 0.0014164 | 0.070034 | 0.070301 | -0.0068914 | 0.0054708 | -0.0014249 | 0.032043 | 66.1652 | -57.1426 | 66.0187 | -56.575 | -57.1701 | 0.18768 | -0.045776 | 66.1469 | -57.0053 | 66.1423 | -56.6254 | -57.0282 | -56.7444 | -0.22888 | 0.022888 | -0.1236 | 0.33874 | 57.1014 | -0.25635 | 57.3303 | -0.027466 | -0.091553 | 0.004578 | 0 | 0.28839 | 0.16937 | -0.11444 | 0.26093 | -0.022888 | 0.56763 | 123.1613 | 0.37994 | 123.1476 | 123.3078 | 123.1522 | 123.0789 | 123.0606 | -123.2849 | -123.1476 | 122.9324 | 123.056 | 56.9458 | 56.868
760.8594 | 123.2025 | -56.9138 | 66.1789 | -0.079346 | 0.0010745 | 0.063717 | 0.068859 | 0.0039263 | -0.0035889 | -0.0010618 | -0.063385 | 0.0012028 | 0.068966 | 0.066456 | -0.004328 | 0.0069662 | 0.0013521 | -0.009155 | 66.2109 | -57.1106 | 66.0187 | -56.5887 | -57.1747 | 0.12817 | -0.10986 | 66.1926 | -56.9824 | 66.156 | -56.6345 | -57.0419 | -56.7352 | -0.19684 | 0.032043 | -0.16022 | 0.32501 | 57.0419 | -0.26093 | 57.2388 | -0.064087 | -0.068665 | 0.013733 | -0.022888 | 0.27924 | 0.17853 | -0.12817 | 0.24719 | -0.059509 | 0.52185 | 123.1293 | 0.3479 | 123.1384 | 123.3215 | 123.175 | 123.1247 | 123.1064 | -123.2895 | -123.1613 | 122.9324 | 123.0698 | 56.9046 | 56.8039
761.8906 | 123.2025 | -56.8222 | 66.2842 | -0.041199 | 0.00043366 | 0.063076 | 0.069073 | -0.0018415 | -0.0048707 | -0.0021298 | 0.0037536 | 0.003339 | 0.067684 | 0.07201 | -0.0049688 | 0.0056846 | -0.00035666 | -0.009155 | 66.3025 | -57.0419 | 66.0507 | -56.5384 | -57.0923 | 0.18768 | -0.10986 | 66.2476 | -56.8954 | 66.2018 | -56.5704 | -56.9641 | -56.6711 | -0.21973 | 0.01831 | -0.23346 | 0.28381 | 57.0099 | -0.27008 | 57.2296 | -0.050354 | -0.073242 | -0.036621 | -0.082398 | 0.25177 | 0.15106 | -0.14191 | 0.2243 | -0.068664 | 0.50354 | 123.0927 | 0.32501 | 123.0972 | 123.3444 | 123.143 | 123.1247 | 123.0698 | -123.3261 | -123.1796 | 122.8729 | 123.024 | 56.813 | 56.7123
762.8594 | 123.2483 | -56.813 | 66.2888 | -0.071716 | 0.0040653 | 0.06329 | 0.0695 | 0.00093573 | 0.00025633 | 6.432e-06 | -0.042023 | 0.0024844 | 0.067471 | 0.068592 | -0.0053962 | 0.0061118 | 0.0015659 | 0.041199 | 66.3025 | -57.0374 | 66.1423 | -56.4239 | -57.0557 | 0.20599 | -0.027466 | 66.2888 | -56.8588 | 66.2888 | -56.4789 | -56.9092 | -56.6071 | -0.22431 | 0.013733 | -0.14648 | 0.3891 | 57.019 | -0.24262 | 57.2433 | -0.01831 | -0.045777 | 0 | 0 | 0.33417 | 0.20599 | -0.096131 | 0.25177 | -0.050354 | 0.6134 | 123.1796 | 0.37994 | 123.1476 | 123.3398 | 123.1476 | 123.1155 | 123.1018 | -123.3261 | -123.1476 | 122.9553 | 123.1018 | 56.8542 | 56.7856
763.8906 | 123.2117 | -56.7581 | 66.33 | -0.048828 | 0.0015019 | 0.063076 | 0.069073 | 0.0024311 | -0.0040161 | -0.0017026 | -0.032867 | 0.0037662 | 0.069393 | 0.064106 | -0.0066778 | 0.0067526 | -0.00057046 | 0.013733 | 66.3528 | -56.9641 | 66.2796 | -56.4239 | -56.955 | 0.24261 | 0 | 66.3391 | -56.7993 | 66.3437 | -56.4011 | -56.8542 | -56.5521 | -0.20599 | 0.022888 | -0.050354 | 0.33417 | 57.0007 | -0.19684 | 57.2067 | 0.009155 | -0.041198 | 0.009155 | 0.013733 | 0.35706 | 0.20599 | -0.09613 | 0.24719 | -0.054932 | 0.54016 | 123.2437 | 0.39825 | 123.143 | 123.317 | 123.1384 | 123.111 | 123.0972 | -123.2941 | -123.1293 | 123.0377 | 123.1018 | 56.7719 | 56.7581
764.8594 | 123.2162 | -56.694 | 66.3757 | 0.11902 | 0.00064726 | 0.064145 | 0.066937 | 0.0017901 | 0.00025633 | -0.0012754 | -0.032867 | 0.0029116 | 0.069393 | 0.06667 | -0.0068914 | 0.0061118 | 0.0015659 | -0.064087 | 66.3986 | -56.9138 | 66.2292 | -56.3507 | -56.9275 | 0.21057 | -0.009155 | 66.3712 | -56.7764 | 66.3803 | -56.3736 | -56.8085 | -56.5063 | -0.21973 | 0.022889 | -0.14648 | 0.34332 | 56.9046 | -0.23346 | 57.1243 | -0.013733 | -0.082397 | -0.004577 | 0.004578 | 0.32044 | 0.18768 | -0.11444 | 0.27008 | -0.032044 | 0.56305 | 123.143 | 0.40283 | 123.1567 | 123.3124 | 123.1476 | 123.0927 | 123.0652 | -123.2895 | -123.1522 | 122.9233 | 123.0743 | 56.6299 | 56.6849
765.9062 | 123.3032 | -56.6391 | 66.3254 | -0.3006 | 0.00064726 | 0.059659 | 0.06715 | 0.0024311 | -0.00017087 | -0.0019162 | 0.00070198 | -0.0013608 | 0.06918 | 0.066029 | -0.007105 | 0.006539 | 0.00071134 | 0.086975 | 66.394 | -56.8863 | 66.2933 | -56.25 | -56.8817 | 0.19684 | -0.050354 | 66.3437 | -56.7535 | 66.4581 | -56.3095 | -56.7398 | -56.4194 | -0.24719 | 0.068665 | -0.032043 | 0.3891 | 56.8359 | -0.24262 | 57.0831 | 0.004578 | -0.11444 | 0.018311 | 0.13275 | 0.32959 | 0.21973 | -0.10071 | 0.33417 | 0.013733 | 0.63629 | 123.1796 | 0.44403 | 123.2117 | 123.2803 | 123.0972 | 123.0331 | 122.9828 | -123.2117 | -123.0789 | 122.9324 | 123.0972 | 56.7261 | 56.5887
766.8594 | 123.2391 | -56.6254 | 66.4352 | -0.033569 | 0.0034245 | 0.064145 | 0.068646 | -0.00077327 | -0.0010255 | -0.0019162 | -0.035919 | 0.00077539 | 0.070675 | 0.065388 | -0.0083868 | 0.0056846 | 0.0034885 | 0.050354 | 66.5131 | -56.8268 | 66.33 | -56.2363 | -56.8497 | 0.20599 | -0.027466 | 66.449 | -56.6666 | 66.4856 | -56.2775 | -56.7307 | -56.4331 | -0.20142 | 0.07782 | -0.10529 | 0.3891 | 56.8314 | -0.2243 | 57.0328 | -0.022888 | -0.041199 | 0.013733 | 0.050354 | 0.3479 | 0.19226 | -0.10529 | 0.23346 | -0.064087 | 0.59052 | 123.1567 | 0.3891 | 123.1522 | 123.3398 | 123.1155 | 123.1384 | 123.0743 | -123.262 | -123.1018 | 122.9553 | 123.111 | 56.6757 | 56.5979
767.8906 | 123.1842 | -56.575 | 66.5268 | -0.11749 | 0.0027835 | 0.063504 | 0.068218 | 0.00029473 | -0.0010255 | -0.003198 | 0.0098572 | 0.0041934 | 0.067898 | 0.060047 | -0.0081732 | 0.0052572 | -0.00035666 | 0.013733 | 66.5817 | -56.7352 | 66.3574 | -56.218 | -56.8359 | 0.24261 | -0.041199 | 66.5222 | -56.6299 | 66.4673 | -56.2592 | -56.7032 | -56.4056 | -0.16022 | 0.054932 | -0.16937 | 0.35706 | 56.8176 | -0.26093 | 56.9778 | -0.10071 | -0.054932 | -0.004577 | -0.059509 | 0.31586 | 0.16937 | -0.12817 | 0.2243 | -0.073242 | 0.51727 | 123.0927 | 0.37079 | 123.0972 | 123.317 | 123.1522 | 123.1567 | 123.0972 | -123.262 | -123.1567 | 122.9324 | 123.0423 | 56.5887 | 56.5338
768.8594 | 123.23 | -56.5338 | 66.5359 | -0.02594 | 0.00064726 | 0.063931 | 0.066723 | 0.0030719 | -0.0038025 | -0.0027708 | -0.051178 | 0.0037662 | 0.069607 | 0.06667 | -0.0079596 | 0.0071798 | 0.00049774 | 0.041199 | 66.5726 | -56.7444 | 66.4169 | -56.1676 | -56.7902 | 0.1831 | -0.041199 | 66.5314 | -56.5887 | 66.5359 | -56.1996 | -56.6711 | -56.3553 | -0.21057 | 0.036621 | -0.11902 | 0.36621 | 56.7169 | -0.25635 | 56.9275 | -0.045776 | -0.054932 | -0.004578 | 0 | 0.33417 | 0.17853 | -0.13733 | 0.23346 | -0.082398 | 0.57678 | 123.1613 | 0.3891 | 123.1247 | 123.317 | 123.1201 | 123.1064 | 123.0652 | -123.2803 | -123.1247 | 122.9507 | 123.0698 | 56.575 | 56.4926
769.8906 | 123.3261 | -56.4468 | 66.5634 | -0.11749 | 0.00064726 | 0.061581 | 0.067364 | 0.00072213 | -0.0023071 | -0.002557 | 0.073944 | 0.0024844 | 0.068325 | 0.061756 | -0.007105 | 0.00483 | 0.00071134 | 0.064087 | 66.5909 | -56.6437 | 66.5359 | -55.9799 | -56.6071 | 0.34332 | 0.091553 | 66.5543 | -56.5247 | 66.6641 | -56.0257 | -56.456 | -56.1996 | -0.19684 | 0.027465 | -0.027466 | 0.46692 | 56.7902 | -0.16022 | 56.987 | 0.036621 | -0.07782 | -0.009156 | 0.10071 | 0.42114 | 0.24719 | -0.009156 | 0.32501 | 0.068664 | 0.66376 | 123.1796 | 0.49896 | 123.1888 | 123.2346 | 123.0789 | 123.0377 | 123.0011 | -123.2071 | -123.0881 | 122.9828 | 123.111 | 56.5109 | 56.5384
770.875 | 123.3032 | -56.4011 | 66.5588 | -0.12512 | 0.0032107 | 0.063717 | 0.06715 | 0.0013629 | -0.00038447 | 0.0015018 | -0.0023498 | -7.901e-05 | 0.069607 | 0.063465 | -0.0086004 | 0.0058982 | -0.0022793 | 0.054932 | 66.6 | -56.6437 | 66.5359 | -56.0074 | -56.6574 | 0.2655 | 0.036621 | 66.5497 | -56.5018 | 66.6916 | -56.0623 | -56.5063 | -56.1996 | -0.24261 | 0.041199 | -0.022888 | 0.39368 | 56.6666 | -0.25635 | 56.9092 | -0.013733 | -0.10071 | -0.009155 | 0.13275 | 0.33875 | 0.20142 | -0.10529 | 0.30212 | -0.004578 | 0.63629 | 123.1796 | 0.43945 | 123.1934 | 123.2437 | 123.0515 | 123.0011 | 122.9507 | -123.2025 | -123.0606 | 122.937 | 123.0927 | 56.456 | 56.4377
771.8906 | 123.2025 | -56.4011 | 66.7191 | -0.033569 | 0.0015019 | 0.062222 | 0.068005 | -0.0016279 | -0.0020935 | -0.003198 | -0.011505 | 0.002698 | 0.069821 | 0.067097 | -0.0068914 | 0.0056846 | 0.0013521 | 0.064087 | 66.7282 | -56.5887 | 66.5405 | -56.012 | -56.6162 | 0.23804 | -0.045776 | 66.7191 | -56.4514 | 66.6321 | -56.0669 | -56.4926 | -56.2134 | -0.18768 | 0.009155 | -0.17853 | 0.3891 | 56.6391 | -0.21515 | 56.8268 | -0.027466 | -0.050354 | 0 | -0.086975 | 0.33417 | 0.18768 | -0.091553 | 0.23804 | -0.041199 | 0.57678 | 123.1293 | 0.38452 | 123.0835 | 123.317 | 123.1705 | 123.1293 | 123.1201 | -123.3078 | -123.1705 | 122.9416 | 123.0331 | 56.4651 | 56.3553
772.8594 | 123.2437 | -56.3187 | 66.7557 | -0.02594 | 0.0017155 | 0.062222 | 0.069286 | 0.0020037 | -0.0031617 | -0.0019162 | 0.092255 | 0.0035526 | 0.066616 | 0.070301 | -0.0079596 | 0.0056846 | -0.0039883 | 0.045776 | 66.7603 | -56.5567 | 66.5909 | -55.9845 | -56.5704 | 0.23346 | -0.19684 | 66.7511 | -56.4148 | 66.7145 | -55.9387 | -56.4285 | -56.1813 | -0.23804 | 0.004578 | -0.16479 | 0.33417 | 56.5521 | -0.25177 | 56.7902 | -0.013733 | -0.09613 | -0.004577 | -0.041198 | 0.37994 | 0.13733 | -0.10986 | 0.23346 | -0.013733 | 0.57221 | 123.1476 | 0.47607 | 123.1293 | 123.317 | 123.1659 | 123.0789 | 123.0698 | -123.3124 | -123.1705 | 122.9095 | 123.0331 | 56.3644 | 56.1218
773.8906 | 123.2437 | -56.2912 | 66.7786 | -0.02594 | 0.0021427 | 0.064145 | 0.069073 | 0.0043537 | -0.0038025 | 0.00086083 | -0.081696 | 0.0037662 | 0.069393 | 0.06667 | -0.0090278 | 0.0069662 | 0.00049774 | 0.059509 | 66.7786 | -56.5201 | 66.655 | -55.8884 | -56.5247 | 0.23346 | -0.004578 | 66.7923 | -56.3736 | 66.7923 | -55.9387 | -56.4102 | -56.1035 | -0.22888 | 0 | -0.1236 | 0.40283 | 56.5247 | -0.23346 | 56.7535 | -0.004577 | -0.082397 | 0.013733 | 0.013733 | 0.35248 | 0.18768 | -0.11902 | 0.27008 | -0.036621 | 0.63171 | 123.175 | 0.43487 | 123.1659 | 123.2986 | 123.1659 | 123.0698 | 123.0835 | -123.2986 | -123.1522 | 122.9462 | 123.0835 | 56.3507 | 56.2866
774.8594 | 123.23 | -56.2317 | 66.8106 | -0.11749 | 0.0010745 | 0.063717 | 0.069714 | 0.0032855 | -0.0048707 | -0.00020717 | -0.075592 | 0.0031254 | 0.069821 | 0.063038 | -0.0066778 | 0.0052572 | -0.0014249 | 0.09613 | 66.8747 | -56.4514 | 66.7007 | -55.8243 | -56.4651 | 0.27008 | 0.018311 | 66.8335 | -56.3049 | 66.8335 | -55.8746 | -56.3416 | -56.0486 | -0.21973 | 0.064087 | -0.10986 | 0.40741 | 56.5018 | -0.23346 | 56.7215 | -0.013733 | -0.073243 | 0.022888 | 0.022888 | 0.35706 | 0.18311 | -0.10986 | 0.25635 | -0.036621 | 0.62714 | 123.1522 | 0.4303 | 123.1384 | 123.3261 | 123.1384 | 123.1064 | 123.0652 | -123.262 | -123.1155 | 122.9324 | 123.0652 | 56.3278 | 56.25
775.9062 | 123.1979 | -56.2271 | 66.8747 | -0.079346 | 0.0029971 | 0.062649 | 0.068646 | 0.0079853 | 0.0011109 | -0.0070432 | -0.035919 | 0.003339 | 0.068966 | 0.066883 | -0.009455 | 0.0084616 | 0.00071134 | 0 | 66.893 | -56.4514 | 66.9205 | -55.6458 | -56.7032 | 0.2243 | -0.10529 | 66.9067 | -56.2912 | 66.8243 | -55.9021 | -56.3919 | -56.0761 | -0.2243 | 0.01831 | 0.045776 | 0.58136 | 56.4514 | -0.47607 | 56.6757 | -0.25177 | -0.064087 | 0.032043 | -0.050354 | 0.32501 | 0.15106 | -0.1648 | 0.21515 | -0.10071 | 0.80566 | 123.3719 | 0.3891 | 123.1155 | 123.3444 | 123.1979 | 123.1201 | 123.1338 | -123.3261 | -123.1659 | 123.1476 | 123.0515 | 56.2271 | 56.1218
776.8594 | 123.2437 | -56.1218 | 66.9159 | -0.01831 | 0.00064726 | 0.064358 | 0.070141 | 0.0013629 | -0.00081187 | -0.001489 | -0.042023 | 0.005048 | 0.068325 | 0.064747 | -0.0068914 | 0.0071798 | 0.0013521 | 0.059509 | 66.9754 | -56.3507 | 66.7969 | -55.6915 | -56.6208 | 0.37994 | -0.018311 | 66.9388 | -56.1905 | 66.925 | -55.7602 | -56.2546 | -55.9662 | -0.22888 | 0.059509 | -0.11902 | 0.4303 | 56.5018 | -0.49896 | 56.7307 | -0.27008 | -0.068665 | 0.022888 | 0.009155 | 0.36163 | 0.15564 | -0.13275 | 0.2243 | -0.064087 | 0.65918 | 123.1476 | 0.4303 | 123.1155 | 123.3261 | 123.1293 | 123.0972 | 123.0606 | -123.2666 | -123.1064 | 122.9187 | 123.0469 | 56.1813 | 56.1035
777.8906 | 123.2712 | -56.0761 | 66.9708 | -0.10223 | 0.0029971 | 0.062649 | 0.067577 | -0.0020551 | -0.0029481 | -0.0051206 | 0.025116 | 0.0012028 | 0.064694 | 0.067311 | -0.0075324 | 0.0069662 | -0.0016385 | 0.11444 | 66.98 | -56.2775 | 66.9159 | -55.6091 | -56.2408 | 0.34332 | 0.086975 | 66.9662 | -56.1401 | 67.0258 | -55.6686 | -56.131 | -55.8517 | -0.20142 | 0.009155 | -0.054931 | 0.46692 | 56.4194 | -0.16479 | 56.6208 | 0.036621 | -0.064087 | -0.004577 | 0.054932 | 0.40741 | 0.2243 | -0.054931 | 0.28839 | 0.009156 | 0.66833 | 123.1934 | 0.4715 | 123.1659 | 123.2574 | 123.1064 | 123.056 | 123.0423 | -123.2483 | -123.111 | 122.9919 | 123.1018 | 56.1905 | 56.163
778.8594 | 123.1842 | -56.0394 | 67.0212 | -0.064087 | 0.0021427 | 0.062222 | 0.067364 | 0.0024311 | -0.0023071 | -0.00020717 | -0.069489 | 0.00098899 | 0.068966 | 0.066242 | -0.0079596 | 0.0069662 | 0.00049774 | 0.064087 | 67.067 | -56.2637 | 66.893 | -55.6229 | -56.2912 | 0.26093 | 0.022888 | 67.0303 | -56.1035 | 67.0303 | -55.6824 | -56.1813 | -55.8746 | -0.2243 | 0.045777 | -0.12817 | 0.41656 | 56.3004 | -0.25177 | 56.5247 | -0.027466 | -0.064087 | 0.009155 | 0.009155 | 0.35706 | 0.16479 | -0.14191 | 0.22888 | -0.077819 | 0.64087 | 123.1567 | 0.42114 | 123.1338 | 123.3307 | 123.1338 | 123.1064 | 123.0698 | -123.2849 | -123.1247 | 122.9324 | 123.0698 | 56.1035 | 56.0623
779.8906 | 123.2346 | -56.012 | 67.0853 | -0.079346 | 0.00086086 | 0.064145 | 0.066296 | -0.00034607 | 0.00046993 | -0.0021298 | -0.05423 | 0.002698 | 0.068539 | 0.064533 | -0.0086004 | 0.0076072 | 0.0015659 | 0.064087 | 67.1082 | -56.218 | 66.9662 | -55.5496 | -56.2271 | 0.27466 | 0.022888 | 67.0898 | -56.0577 | 67.0898 | -55.6091 | -56.0989 | -55.7922 | -0.20599 | 0.022888 | -0.11902 | 0.46234 | 56.2866 | -0.21515 | 56.4926 | -0.009155 | -0.045776 | 0.004578 | 0.004578 | 0.40283 | 0.21973 | -0.086975 | 0.2655 | -0.041199 | 0.66833 | 123.1842 | 0.44861 | 123.1476 | 123.3261 | 123.1476 | 123.1201 | 123.1018 | -123.3032 | -123.143 | 122.9782 | 123.1018 | 56.0761 | 56.0349
780.8594 | 123.2895 | -55.9387 | 67.1356 | -0.086975 | 0.0021427 | 0.063504 | 0.066082 | -0.0024823 | -0.0016663 | 0.0012882 | 0.040375 | 0.002698 | 0.068112 | 0.059834 | -0.007105 | 0.0054708 | -0.0012113 | 0.045776 | 67.1173 | -56.1493 | 66.9983 | -55.481 | -56.1722 | 0.30212 | 0.013733 | 67.099 | -55.9891 | 67.1677 | -55.513 | -55.9891 | -55.7098 | -0.21057 | -0.01831 | -0.13733 | 0.45776 | 56.2408 | -0.23346 | 56.4514 | -0.022888 | -0.050354 | -0.036621 | 0.032044 | 0.42572 | 0.22888 | -0.050354 | 0.27924 | 0 | 0.66834 | 123.1476 | 0.47608 | 123.1567 | 123.2666 | 123.0881 | 123.056 | 123.0377 | -123.2849 | -123.1247 | 122.937 | 123.1064 | 55.9845 | 55.9525
781.8906 | 123.2803 | -55.8701 | 67.1814 | -0.071716 | 0.0025699 | 0.062222 | 0.065868 | -0.00098687 | -0.0010255 | -0.0046934 | 0.03122 | 0.0022708 | 0.06683 | 0.070301 | -0.0090278 | 0.006539 | 0.0011385 | 0.10071 | 67.2134 | -56.0577 | 67.1402 | -55.3482 | -56.0211 | 0.37079 | 0.11902 | 67.1722 | -55.925 | 67.2592 | -55.3848 | -55.8746 | -55.6091 | -0.18768 | 0.032044 | -0.041198 | 0.52185 | 56.2408 | -0.15106 | 56.4285 | 0.036621 | -0.054932 | -0.009155 | 0.07782 | 0.48523 | 0.26093 | -0.004578 | 0.31586 | 0.050354 | 0.70953 | 123.1979 | 0.54016 | 123.1842 | 123.2712 | 123.0972 | 123.0835 | 123.0423 | -123.2391 | -123.1064 | 123.0103 | 123.1293 | 55.9708 | 55.9891
782.8594 | 123.2529 | -55.8151 | 67.2729 | 0.019837 | 0.0012881 | 0.062863 | 0.066937 | 0.0022173 | -0.0035889 | -0.00020717 | -0.057281 | 0.0059024 | 0.067898 | 0.06667 | -0.0056098 | 0.0071798 | -0.0020657 | 0.073242 | 67.2867 | -56.044 | 67.1082 | -55.4031 | -56.0532 | 0.27466 | -0.009155 | 67.2226 | -55.8746 | 67.3462 | -55.4489 | -55.9113 | -55.6 | -0.22888 | 0.013733 | -0.16479 | 0.41199 | 56.0898 | -0.23804 | 56.3187 | -0.009156 | -0.059509 | -0.050354 | 0.073242 | 0.36621 | 0.21515 | -0.09613 | 0.27466 | -0.036621 | 0.64087 | 123.1522 | 0.42572 | 123.2208 | 123.3307 | 123.0972 | 123.1018 | 123.0377 | -123.317 | -123.1476 | 122.9233 | 123.1613 | 55.8884 | 55.806
783.8906 | 123.2025 | -55.806 | 67.2913 | -0.056457 | -0.00042094 | 0.06094 | 0.067791 | -0.00055967 | -0.0025207 | -0.0019162 | -0.038971 | 0.00098899 | 0.068539 | 0.062824 | -0.006037 | 0.0058982 | 0.00092494 | 0.054932 | 67.3462 | -55.9891 | 67.131 | -55.3619 | -56.0349 | 0.2655 | -0.036621 | 67.3004 | -55.8334 | 67.2867 | -55.3802 | -55.8746 | -55.6046 | -0.18311 | 0.054931 | -0.16022 | 0.44403 | 56.0715 | -0.22888 | 56.2546 | -0.045776 | -0.027466 | 0.009155 | -0.004578 | 0.42572 | 0.20142 | -0.068665 | 0.22888 | -0.041199 | 0.62714 | 123.1201 | 0.45319 | 123.1201 | 123.3353 | 123.1338 | 123.1522 | 123.1064 | -123.2803 | -123.1247 | 122.937 | 123.0927 | 55.8609 | 55.7693
784.8594 | 123.2162 | -55.7007 | 67.3462 | -0.048828 | 0.0010745 | 0.060727 | 0.06715 | 0.0024311 | -0.0020935 | -0.00063437 | -0.05423 | 0.0022708 | 0.069393 | 0.065174 | -0.0062506 | 0.0041892 | 0.0013521 | 0.064087 | 67.3874 | -55.957 | 67.1814 | -55.3116 | -55.9799 | 0.27466 | -0.022888 | 67.3691 | -55.8014 | 67.3416 | -55.3391 | -55.8151 | -55.5405 | -0.25635 | 0.041199 | -0.16479 | 0.3891 | 55.9753 | -0.27923 | 56.2317 | -0.022888 | -0.10071 | 0.022889 | -0.004577 | 0.36163 | 0.16022 | -0.11444 | 0.26093 | -0.013733 | 0.64545 | 123.1384 | 0.46234 | 123.143 | 123.3444 | 123.1705 | 123.0881 | 123.0698 | -123.3032 | -123.1476 | 122.8821 | 123.0423 | 55.7648 | 55.6778
785.8906 | 123.2025 | -55.6961 | 67.4103 | -0.01831 | 0.0027835 | 0.06329 | 0.067791 | 0.00029473 | -0.0040161 | -0.0038388 | -0.038971 | 0.0029116 | 0.069821 | 0.065602 | -0.0073188 | 0.0039756 | -0.0012113 | 0.050354 | 67.4561 | -55.8838 | 67.2409 | -55.2658 | -55.925 | 0.27924 | -0.032043 | 67.4332 | -55.7465 | 67.3874 | -55.2704 | -55.8014 | -55.5084 | -0.18768 | 0.045777 | -0.16937 | 0.4303 | 55.9753 | -0.22888 | 56.163 | -0.041199 | -0.050354 | 0.022889 | -0.022888 | 0.42572 | 0.18768 | -0.10529 | 0.23804 | -0.054932 | 0.61798 | 123.1247 | 0.47607 | 123.1338 | 123.3398 | 123.1796 | 123.1522 | 123.1293 | -123.2941 | -123.1567 | 122.937 | 123.0835 | 55.7465 | 55.6641
786.8594 | 123.2254 | -55.6183 | 67.4789 | -0.010681 | -0.00063454 | 0.062222 | 0.066509 | 0.0017901 | -0.00081187 | -0.004266 | -0.048126 | 0.0022708 | 0.067684 | 0.068592 | -0.0064642 | 0.006539 | -0.00035666 | 0.054932 | 67.5018 | -55.8334 | 67.2729 | -55.2063 | -55.8929 | 0.27466 | -0.018311 | 67.4606 | -55.6961 | 67.4332 | -55.2155 | -55.7373 | -55.4443 | -0.21515 | 0.022888 | -0.20599 | 0.41199 | 55.8929 | -0.27466 | 56.1081 | -0.059509 | -0.07782 | -0.018311 | -0.045776 | 0.40283 | 0.17395 | -0.11902 | 0.25177 | -0.041199 | 0.62714 | 123.1064 | 0.48065 | 123.1293 | 123.3353 | 123.1567 | 123.1201 | 123.0789 | -123.3124 | -123.175 | 122.8912 | 123.0515 | 55.6732 | 55.6
787.8906 | 123.4177 | -55.5588 | 67.5476 | -0.01831 | 0.0010745 | 0.063931 | 0.068646 | 0.0011493 | 0.00025633 | -0.003198 | -0.045074 | 0.0054752 | 0.071102 | 0.064533 | -0.006037 | 0.0076072 | -0.0016385 | 0.059509 | 67.5659 | -55.8105 | 67.3508 | -55.1239 | -55.806 | 0.28381 | -0.018311 | 67.5385 | -55.6366 | 67.5018 | -55.069 | -55.8014 | -55.394 | -0.25177 | 0.018311 | -0.19684 | 0.43488 | 55.8426 | -0.24719 | 56.0944 | 0.004578 | -0.07782 | -0.009155 | -0.045776 | 0.48981 | 0.16479 | -0.24262 | 0.24262 | -0.16479 | 0.68665 | 123.1613 | 0.56763 | 123.1384 | 123.3765 | 123.175 | 123.1247 | 123.0972 | -123.3582 | -123.1842 | 122.9095 | 123.0606 | 55.6183 | 55.5405
788.8594 | 123.1934 | -55.5405 | 67.5247 | -0.079346 | 0.0025699 | 0.062436 | 0.067577 | 0.0022173 | 4.273e-05 | 0.0015018 | -0.051178 | 0.0018436 | 0.070889 | 0.064747 | -0.0096686 | 0.0073936 | -0.0014249 | 0.09613 | 67.598 | -55.7373 | 67.4194 | -55.0461 | -55.7739 | 0.27008 | 0.032043 | 67.5385 | -55.5862 | 67.5522 | -55.1193 | -55.6595 | -55.3482 | -0.19684 | 0.073242 | -0.10529 | 0.49438 | 55.8105 | -0.23346 | 56.0074 | -0.036621 | -0.045777 | 0.013733 | 0.027466 | 0.42114 | 0.19226 | -0.11902 | 0.23804 | -0.073242 | 0.69122 | 123.1567 | 0.46692 | 123.1384 | 123.3353 | 123.1247 | 123.1384 | 123.0789 | -123.262 | -123.111 | 122.9599 | 123.0927 | 55.6366 | 55.5725
789.9062 | 123.175 | -55.4855 | 67.6163 | -0.064087 | 0.0032107 | 0.063931 | 0.070568 | 0.00093573 | -0.0038025 | -0.00020717 | -0.035919 | 0.00098899 | 0.068966 | 0.060047 | -0.0056098 | 0.0073936 | -0.0018521 | 0.045776 | 67.6163 | -55.6915 | 67.4561 | -55.0232 | -55.7419 | 0.26093 | -0.027466 | 67.6025 | -55.5588 | 67.5797 | -55.0873 | -55.6091 | -55.307 | -0.20599 | 0 | -0.16022 | 0.46234 | 55.7465 | -0.25635 | 55.9525 | -0.050354 | -0.073242 | -0.013733 | -0.036621 | 0.39825 | 0.17853 | -0.1236 | 0.25177 | -0.050354 | 0.66833 | 123.1476 | 0.4715 | 123.1384 | 123.3078 | 123.1613 | 123.1018 | 123.0881 | -123.3078 | -123.175 | 122.9416 | 123.0652 | 55.5313 | 55.4581
790.8594 | 123.2391 | -55.4123 | 67.6758 | 0.0045776 | 0.0038517 | 0.061154 | 0.066723 | 0.0015765 | -0.0016663 | 0.0023562 | 0.0037536 | 0.0037662 | 0.068539 | 0.064747 | -0.0079596 | 0.0073936 | 0.0013521 | 0.054932 | 67.717 | -55.6046 | 67.4927 | -54.9728 | -55.6778 | 0.28839 | -0.022888 | 67.6666 | -55.4855 | 67.662 | -54.9774 | -55.5176 | -55.2292 | -0.19226 | 0.041199 | -0.1831 | 0.43945 | 55.7007 | -0.2655 | 55.8929 | -0.073242 | -0.073243 | -0.009155 | -0.013733 | 0.43487 | 0.1831 | -0.10529 | 0.25635 | -0.032043 | 0.63171 | 123.0972 | 0.50812 | 123.1476 | 123.3215 | 123.1522 | 123.1293 | 123.0789 | -123.2803 | -123.1613 | 122.905 | 123.0743 | 55.4672 | 55.3894
791.8906 | 123.2986 | -55.3619 | 67.6941 | -0.071716 | 0.0038517 | 0.062649 | 0.066937 | 0.0028583 | -0.00017087 | -0.0027708 | 0.043427 | 0.0037662 | 0.067471 | 0.066029 | -0.0058234 | 0.008248 | -0.0012113 | 0.11444 | 67.7261 | -55.5496 | 67.6666 | -54.7485 | -55.4993 | 0.40283 | 0.13275 | 67.6758 | -55.4031 | 67.7902 | -54.8264 | -55.3528 | -55.0919 | -0.18768 | 0.032043 | -0.027466 | 0.6134 | 55.7648 | -0.13733 | 55.9525 | 0.050354 | -0.041199 | -0.018311 | 0.09613 | 0.53558 | 0.27008 | 0.009155 | 0.31128 | 0.050354 | 0.80109 | 123.2162 | 0.57678 | 123.1934 | 123.2758 | 123.0789 | 123.0881 | 123.0377 | -123.2437 | -123.0972 | 123.0286 | 123.1522 | 55.4764 | 55.4947
792.8594 | 123.2254 | -55.3299 | 67.7811 | -0.01831 | 0.0015019 | 0.062008 | 0.069714 | 0.0011493 | -0.0016663 | -0.002557 | -0.014557 | 0.0048344 | 0.070461 | 0.065602 | -0.0079596 | 0.008248 | -0.00035666 | 0.059509 | 67.836 | -55.5176 | 67.5842 | -54.863 | -55.5679 | 0.29755 | -0.004578 | 67.7902 | -55.3757 | 67.7353 | -54.9088 | -55.4398 | -55.1468 | -0.18768 | 0.054932 | -0.19684 | 0.46692 | 55.6274 | -0.23804 | 55.8151 | -0.050354 | -0.045776 | 0.009155 | -0.045776 | 0.42114 | 0.1831 | -0.10986 | 0.22888 | -0.064087 | 0.6546 | 123.1018 | 0.46692 | 123.111 | 123.3536 | 123.1659 | 123.1659 | 123.1201 | -123.2986 | -123.1567 | 122.9141 | 123.0652 | 55.3894 | 55.3253
793.8906 | 123.2941 | -55.2292 | 67.804 | -0.071716 | 0.0010745 | 0.062436 | 0.068859 | 0.0024311 | -0.00017087 | -0.0023434 | 0.043427 | 0.0029116 | 0.069607 | 0.063465 | -0.0079596 | 0.0050436 | -0.00014306 | 0.13733 | 67.8223 | -55.4443 | 67.7536 | -54.657 | -55.4123 | 0.40741 | 0.11902 | 67.7902 | -55.3116 | 67.8818 | -54.7348 | -55.275 | -55.0003 | -0.21515 | 0.018311 | -0.050354 | 0.57221 | 55.6366 | -0.1831 | 55.8517 | 0.032044 | -0.082397 | -0.013733 | 0.07782 | 0.49439 | 0.22888 | -0.045776 | 0.31128 | 0.036621 | 0.78735 | 123.1979 | 0.57678 | 123.1934 | 123.2666 | 123.1018 | 123.0515 | 123.0194 | -123.2483 | -123.1155 | 122.9828 | 123.111 | 55.3665 | 55.3482
794.8594 | 123.2254 | -55.2063 | 67.9001 | -0.0030519 | 0.00064726 | 0.062008 | 0.070355 | 0.0028583 | -0.0010255 | 0.00022003 | -0.051178 | 0.0054752 | 0.070248 | 0.063679 | -0.0073188 | 0.0050436 | 0.0037021 | 0.068665 | 67.9321 | -55.3986 | 67.6895 | -54.7394 | -55.4672 | 0.32044 | -0.013733 | 67.9001 | -55.2979 | 67.8543 | -54.7714 | -55.3207 | -55.0369 | -0.19226 | 0.032044 | -0.21057 | 0.46692 | 55.5267 | -0.26093 | 55.719 | -0.068664 | -0.091553 | 0 | -0.045776 | 0.43488 | 0.16937 | -0.11444 | 0.26093 | -0.022888 | 0.65918 | 123.0881 | 0.52643 | 123.1522 | 123.3307 | 123.1979 | 123.1384 | 123.1064 | -123.2986 | -123.1979 | 122.8958 | 123.0606 | 55.275 | 55.1926
795.8906 | 123.3307 | -55.1193 | 67.8909 | -0.048828 | 0.00043366 | 0.064145 | 0.068432 | 0.0064899 | -0.010638 | -0.001489 | -0.029816 | 0.0014164 | 0.067471 | 0.058979 | -0.006037 | 0.0058982 | 0.00028414 | 0.11444 | 67.9001 | -55.3436 | 68.0008 | -54.9225 | -55.3665 | 0.48065 | 0.1831 | 67.8818 | -55.2063 | 68.0099 | -54.5975 | -55.1559 | -54.8813 | -0.2243 | 0.009155 | 0.10986 | 0.19684 | 55.6 | -0.24719 | 55.8243 | -0.022888 | -0.086975 | -0.009155 | 0.11902 | 0.52185 | 0.23804 | -0.036621 | 0.32501 | 0.050354 | 0.42114 | 123.3444 | 0.60883 | 123.2162 | 123.2437 | 123.0881 | 123.0194 | 123.0011 | -123.2346 | -123.0972 | 123.1201 | 123.1293 | 55.2338 | 55.3024
796.8594 | 123.2162 | -55.1102 | 67.9871 | -0.048828 | 0.0032107 | 0.062863 | 0.068218 | -0.0026959 | -0.0020935 | -0.0036252 | -0.051178 | 0.0031254 | 0.069607 | 0.065388 | -0.007105 | 0.0052572 | 0.0041293 | 0.059509 | 68.0099 | -55.3345 | 67.804 | -54.6204 | -55.3665 | 0.31128 | -0.009155 | 67.9871 | -55.1697 | 67.9276 | -54.6799 | -55.2383 | -54.95 | -0.22431 | 0.022888 | -0.18311 | 0.48981 | 55.4214 | -0.25635 | 55.6458 | -0.032043 | -0.05951 | 0 | -0.05951 | 0.4303 | 0.16022 | -0.12817 | 0.21973 | -0.068664 | 0.71411 | 123.1384 | 0.48981 | 123.0972 | 123.3444 | 123.1567 | 123.1201 | 123.0972 | -123.3215 | -123.1567 | 122.9141 | 123.0377 | 55.1697 | 55.101
797.8906 | 123.2437 | -55.0552 | 67.9779 | -0.086975 | 0.00022006 | 0.064145 | 0.067577 | 0.0043537 | 0.0019653 | -0.0012754 | 0.0068054 | 0.0012028 | 0.067471 | 0.075215 | -0.0049688 | 0.0071798 | 0.0017795 | 0.091553 | 67.9962 | -55.2521 | 67.9916 | -54.5609 | -55.4306 | 0.32044 | 0.022888 | 67.9733 | -55.1285 | 68.0237 | -54.5929 | -55.1605 | -54.8584 | -0.19684 | 0.018311 | 0.013733 | 0.49439 | 55.3757 | -0.37537 | 55.5725 | -0.17853 | -0.073242 | -0.004577 | 0.045777 | 0.46234 | 0.19684 | -0.10529 | 0.27008 | -0.032043 | 0.69122 | 123.2437 | 0.53558 | 123.1522 | 123.2483 | 123.1018 | 123.0515 | 123.0286 | -123.23 | -123.1064 | 123.0469 | 123.0789 | 55.1468 | 55.0781
798.8594 | 123.2483 | -55.0049 | 68.0557 | -0.010681 | 0.0034245 | 0.064572 | 0.068859 | 0.00050853 | -0.0031617 | -0.0029844 | -0.081696 | 0.003339 | 0.068753 | 0.068379 | -0.0090278 | 0.0056846 | 0.0017795 | 0.082397 | 68.0786 | -55.2521 | 67.9367 | -54.5151 | -55.2292 | 0.33417 | -0.045776 | 68.0557 | -55.069 | 68.1564 | -54.5792 | -55.0919 | -54.776 | -0.24719 | 0.022888 | -0.11902 | 0.48981 | 55.3391 | -0.2243 | 55.5862 | 0.022888 | -0.064087 | 0 | 0.10071 | 0.42572 | 0.22888 | -0.086975 | 0.29297 | -0.022888 | 0.737 | 123.1888 | 0.48981 | 123.2254 | 123.3307 | 123.1247 | 123.0835 | 123.0606 | -123.3078 | -123.1247 | 122.9416 | 123.1613 | 55.0873 | 54.9591
799.8906 | 123.1888 | -54.9774 | 68.1061 | -0.010681 | 0.0023563 | 0.061581 | 0.067791 | -0.00077327 | -0.00017087 | 6.432e-06 | -0.029816 | 0.0046206 | 0.069607 | 0.070942 | -0.0066778 | 0.0052572 | 0.0022067 | 0.064087 | 68.1473 | -55.1971 | 67.9504 | -54.4693 | -55.2246 | 0.32959 | -0.009155 | 68.1107 | -55.0369 | 68.0695 | -54.5242 | -55.0919 | -54.8172 | -0.21973 | 0.041199 | -0.15564 | 0.50812 | 55.307 | -0.24719 | 55.5267 | -0.027465 | -0.059509 | 0.004578 | -0.036621 | 0.45319 | 0.16022 | -0.11444 | 0.21973 | -0.054932 | 0.72785 | 123.1476 | 0.5127 | 123.1064 | 123.3444 | 123.1476 | 123.1247 | 123.0881 | -123.3032 | -123.143 | 122.9279 | 123.0469 | 55.0415 | 54.9683
800.8594 | 123.1842 | -54.9225 | 68.1747 | -0.033569 | 0.0019291 | 0.06329 | 0.066509 | 0.0017901 | -0.0029481 | -0.0019162 | -0.011505 | 0.0037662 | 0.066616 | 0.062611 | -0.0056098 | 0.006539 | 0.00049774 | 0.082397 | 68.2068 | -55.1285 | 67.9779 | -54.4189 | -55.1788 | 0.33417 | -0.018311 | 68.1656 | -54.9728 | 68.1152 | -54.4785 | -55.0507 | -54.7623 | -0.20599 | 0.032043 | -0.19684 | 0.50354 | 55.2567 | -0.25635 | 55.4626 | -0.050354 | -0.050354 | -0.009156 | -0.05951 | 0.44403 | 0.16022 | -0.12817 | 0.21057 | -0.07782 | 0.70953 | 123.1064 | 0.49438 | 123.0881 | 123.3353 | 123.1384 | 123.1293 | 123.0881 | -123.3032 | -123.1476 | 122.9004 | 123.0377 | 55.0049 | 54.9042
801.8906 | 123.349 | -54.8401 | 68.1427 | -0.048828 | 0.00086086 | 0.061581 | 0.066723 | 0.0017901 | -0.0087159 | -0.0046934 | -0.069489 | 0.0018436 | 0.068112 | 0.062824 | -0.0068914 | 0.0063254 | -0.0014249 | 0.1236 | 68.2022 | -55.0827 | 68.3212 | -54.6021 | -55.1056 | 0.50354 | 0.19226 | 68.1747 | -54.9408 | 68.28 | -54.3091 | -54.8721 | -54.6112 | -0.24262 | 0.059509 | 0.17853 | 0.23804 | 55.3436 | -0.2655 | 55.5862 | -0.022888 | -0.10071 | 0.032044 | 0.13733 | 0.53101 | 0.22888 | -0.032043 | 0.32959 | 0.068665 | 0.48065 | 123.4039 | 0.63171 | 123.2208 | 123.2849 | 123.1155 | 123.0423 | 123.0148 | -123.2254 | -123.0835 | 123.1613 | 123.1201 | 54.9637 | 55.0323
802.8594 | 123.1934 | -54.8355 | 68.2434 | 0.22583 | 0.0019291 | 0.064999 | 0.0695 | 0.0032855 | -0.0029481 | -0.0021298 | -0.042023 | 0.004407 | 0.068112 | 0.065815 | -0.0056098 | 0.0052572 | 0.0019931 | 0.054932 | 68.3121 | -55.0415 | 68.0923 | -54.3228 | -55.1147 | 0.36163 | 0.022888 | 68.2663 | -54.9133 | 68.1885 | -54.3869 | -54.9591 | -54.689 | -0.20599 | 0.068665 | -0.15106 | 0.5127 | 55.1971 | -0.27924 | 55.4031 | -0.073242 | -0.07782 | 0.022888 | -0.054931 | 0.44861 | 0.14648 | -0.1236 | 0.2243 | -0.045776 | 0.71869 | 123.1339 | 0.52643 | 123.1018 | 123.3536 | 123.1796 | 123.1476 | 123.1018 | -123.2849 | -123.1567 | 122.9279 | 123.024 | 54.8904 | 54.8584
803.8906 | 123.1888 | -54.808 | 68.2846 | -0.033569 | 0.0010745 | 0.063717 | 0.068859 | -0.0022687 | -0.0035889 | 6.432e-06 | -0.02066 | 0.0031254 | 0.070034 | 0.062611 | -0.0053962 | 0.0063254 | -0.00099766 | 0.07782 | 68.3166 | -55.0049 | 68.1244 | -54.277 | -55.0598 | 0.35248 | 0.009155 | 68.2892 | -54.863 | 68.2434 | -54.3549 | -54.9179 | -54.6478 | -0.19684 | 0.032043 | -0.16022 | 0.53101 | 55.1605 | -0.25177 | 55.3574 | -0.054931 | -0.054932 | 0.004578 | -0.041199 | 0.45319 | 0.16022 | -0.10986 | 0.21515 | -0.054932 | 0.72784 | 123.1293 | 0.50812 | 123.1064 | 123.3215 | 123.1522 | 123.1247 | 123.0972 | -123.2895 | -123.1476 | 122.9324 | 123.0515 | 54.8859 | 54.8172
804.8594 | 123.1842 | -54.7668 | 68.3212 | -0.086975 | 0.0017155 | 0.064572 | 0.068005 | 0.0022173 | 4.273e-05 | -0.0017026 | -0.017609 | 0.0035526 | 0.068753 | 0.061115 | -0.0045416 | 0.0058982 | -0.0022793 | 0.15564 | 68.3441 | -54.9545 | 68.2205 | -54.1489 | -54.9454 | 0.39825 | 0.068665 | 68.3166 | -54.8035 | 68.2114 | -54.2313 | -54.8172 | -54.57 | -0.18768 | 0.022888 | -0.10071 | 0.61798 | 55.1651 | -0.17853 | 55.3528 | 0.009155 | -0.036621 | -0.004578 | -0.10986 | 0.53558 | 0.19684 | -0.050354 | 0.23346 | -0.013733 | 0.80566 | 123.175 | 0.5722 | 123.0148 | 123.2986 | 123.1201 | 123.111 | 123.0835 | -123.2758 | -123.1247 | 122.9874 | 122.9782 | 54.9225 | 54.8355
805.8906 | 123.2254 | -54.7302 | 68.2663 | -0.086975 | 0.0044925 | 0.063076 | 0.070141 | 0.0022173 | -0.0010255 | -0.0019162 | -0.02066 | 0.00013459 | 0.070034 | 0.063038 | -0.0075324 | 0.0080344 | -0.00014306 | 0.086975 | 68.3029 | -54.9454 | 68.2526 | -54.1122 | -54.9637 | 0.38452 | 0.073242 | 68.3029 | -54.776 | 68.3304 | -53.9612 | -54.7073 | -54.6158 | -0.21515 | 0.036621 | -0.013733 | 0.61798 | 55.1147 | -0.23346 | 55.3299 | -0.01831 | -0.045776 | 0.036621 | 0.064087 | 0.76904 | 0.11444 | 0.022889 | 0.16022 | 0.068665 | 0.83313 | 123.1979 | 0.81482 | 123.1064 | 123.2483 | 123.0789 | 123.0331 | 123.0331 | -123.2117 | -123.0423 | 122.9828 | 123.0606 | 54.8172 | 54.8035
806.8594 | 123.262 | -54.6616 | 68.3945 | -0.079346 | 0.0021427 | 0.065213 | 0.06715 | 8.1126e-05 | -0.0012391 | -0.002557 | -0.042023 | 0.0039798 | 0.068112 | 0.068165 | -0.0056098 | 0.0058982 | -0.0039883 | 0.16022 | 68.3899 | -54.8721 | 68.3395 | -54.0253 | -54.8264 | 0.43945 | 0.13733 | 68.4036 | -54.7531 | 68.4448 | -54.1306 | -54.7028 | -54.4373 | -0.21057 | -0.004577 | -0.054931 | 0.63629 | 55.101 | -0.16479 | 55.3116 | 0.045776 | -0.091553 | 0.009155 | 0.050354 | 0.53101 | 0.2243 | -0.041199 | 0.31586 | 0.050354 | 0.84686 | 123.2117 | 0.62256 | 123.1979 | 123.262 | 123.1567 | 123.0515 | 123.0652 | -123.2666 | -123.1476 | 123.0011 | 123.1064 | 54.8218 | 54.7989
807.8906 | 123.2437 | -54.657 | 68.3899 | -0.094604 | 0.0019291 | 0.06329 | 0.06715 | 0.0013629 | -0.0035889 | 6.432e-06 | -0.11526 | 0.00163 | 0.068112 | 0.064961 | -0.0062506 | 0.0063254 | -0.0014249 | 0.086975 | 68.399 | -54.8447 | 68.2938 | -54.2038 | -54.5792 | 0.32959 | 0.15106 | 68.3853 | -54.7485 | 68.4448 | -54.1626 | -54.7394 | -54.4418 | -0.18768 | 0.009155 | -0.096131 | 0.45319 | 54.9866 | 0.077819 | 55.1743 | 0.2655 | -0.091553 | -0.004578 | 0.054931 | 0.49438 | 0.21515 | -0.082398 | 0.3067 | 0.009155 | 0.64087 | 123.1384 | 0.58594 | 123.1934 | 123.2437 | 123.1338 | 123.056 | 123.0423 | -123.2346 | -123.1384 | 122.9507 | 123.1018 | 54.744 | 54.808
808.875 | 123.1979 | -54.6295 | 68.4448 | -0.041199 | 0.0019291 | 0.062863 | 0.069286 | 0.00050853 | -0.0038025 | -0.0040524 | -0.078644 | 0.0037662 | 0.068753 | 0.06667 | -0.009455 | 0.0063254 | -0.0042021 | 0.10529 | 68.4586 | -54.8584 | 68.3304 | -54.0482 | -54.8813 | 0.32501 | 0.032043 | 68.486 | -54.6844 | 68.4631 | -54.1534 | -54.7714 | -54.451 | -0.22888 | 0.013733 | -0.11444 | 0.58136 | 54.9545 | -0.25177 | 55.1834 | -0.022889 | -0.054931 | 0.041199 | 0.018311 | 0.47608 | 0.17853 | -0.14191 | 0.23346 | -0.086975 | 0.81024 | 123.1888 | 0.53101 | 123.1476 | 123.317 | 123.1705 | 123.0881 | 123.1155 | -123.3032 | -123.1293 | 122.9599 | 123.0927 | 54.7348 | 54.6616
809.8906 | 123.3124 | -54.5288 | 68.454 | -0.11749 | 0.0023563 | 0.062222 | 0.06715 | -0.0022687 | -0.0010255 | -0.0012754 | -0.0023498 | 0.0020572 | 0.068966 | 0.066883 | -0.0058234 | 0.0052572 | -0.00014306 | 0.17853 | 68.5181 | -54.7714 | 68.4494 | -53.8834 | -54.6982 | 0.47607 | 0.16022 | 68.4723 | -54.6341 | 68.5822 | -53.9749 | -54.5746 | -54.2908 | -0.24261 | 0.064087 | -0.004577 | 0.64545 | 55.0049 | -0.16937 | 55.2475 | 0.073242 | -0.10528 | 0.018311 | 0.12817 | 0.55389 | 0.23804 | -0.045776 | 0.34332 | 0.059509 | 0.88806 | 123.2208 | 0.65918 | 123.2162 | 123.2895 | 123.1064 | 123.0469 | 123.0011 | -123.2254 | -123.0881 | 122.9782 | 123.111 | 54.7073 | 54.689
810.8594 | 123.2803 | -54.5013 | 68.5181 | -0.071716 | 0.00022006 | 0.06094 | 0.06715 | 0.0013629 | -0.00038447 | -0.0010618 | -0.0023498 | 0.0052616 | 0.064694 | 0.067738 | -0.007105 | 0.0058982 | -0.0033475 | 0.15564 | 68.5501 | -54.7394 | 68.4906 | -53.8605 | -54.6844 | 0.44403 | 0.12817 | 68.486 | -54.5883 | 68.605 | -53.9749 | -54.5471 | -54.3045 | -0.23804 | 0.032044 | -0.027465 | 0.64087 | 54.9454 | -0.18311 | 55.1834 | 0.054932 | -0.086975 | -0.032043 | 0.086976 | 0.52643 | 0.19684 | -0.045776 | 0.28381 | 0.041199 | 0.87891 | 123.23 | 0.6134 | 123.1934 | 123.2895 | 123.0743 | 123.0515 | 122.9874 | -123.2574 | -123.1064 | 122.9919 | 123.1064 | 54.657 | 54.6295
811.8906 | 123.2941 | -54.5059 | 68.5043 | -0.086975 | 0.0010745 | 0.062649 | 0.069714 | -0.0014143 | 0.00025633 | -0.0036252 | 0.0068054 | 0.00013459 | 0.067684 | 0.05962 | -0.0081732 | 0.0054708 | -0.00057046 | 0.10529 | 68.5684 | -54.7302 | 68.4494 | -53.92 | -54.7211 | 0.42114 | 0.059509 | 68.5043 | -54.5563 | 68.6279 | -53.9658 | -54.5425 | -54.2633 | -0.2243 | 0.064087 | -0.054931 | 0.58594 | 54.9271 | -0.21515 | 55.1514 | 0.009156 | -0.050354 | 0 | 0.1236 | 0.54016 | 0.24261 | -0.036622 | 0.29297 | 0.013732 | 0.81024 | 123.1796 | 0.59052 | 123.1842 | 123.2986 | 123.0606 | 123.0743 | 123.0103 | -123.2346 | -123.0606 | 122.9553 | 123.1339 | 54.6112 | 54.5654
812.8594 | 123.317 | -54.4281 | 68.5684 | -0.048828 | 0.0023563 | 0.061581 | 0.068005 | -0.0033369 | -0.0025207 | -0.00042077 | -0.0084534 | 0.0022708 | 0.067044 | 0.06432 | -0.0064642 | 0.006539 | 0.00049774 | 0.14648 | 68.6234 | -54.6524 | 68.5547 | -53.7781 | -54.6158 | 0.47607 | 0.16022 | 68.5684 | -54.5425 | 68.6783 | -53.8696 | -54.4739 | -54.2084 | -0.2243 | 0.054932 | -0.013733 | 0.65002 | 54.9042 | -0.18768 | 55.1285 | 0.036621 | -0.11444 | 0 | 0.10986 | 0.55847 | 0.21973 | -0.045776 | 0.33417 | 0.068665 | 0.87433 | 123.2071 | 0.67291 | 123.2208 | 123.2758 | 123.111 | 123.0515 | 122.9965 | -123.2208 | -123.111 | 122.9828 | 123.1064 | 54.5746 | 54.5883
813.8906 | 123.2025 | -54.4647 | 68.6417 | -0.01831 | 0.0036381 | 0.063717 | 0.068859 | 0.00093573 | -0.0040161 | 0.00086083 | -0.048126 | 0.0012028 | 0.068539 | 0.065602 | -0.0096686 | 0.0078208 | -0.00035666 | 0.16022 | 68.6737 | -54.6478 | 68.5272 | -53.8284 | -54.6433 | 0.42572 | 0.34332 | 68.692 | -54.4647 | 68.5959 | -53.9337 | -54.5242 | -54.2953 | -0.1831 | 0.032043 | -0.11444 | 0.63629 | 54.8904 | -0.17853 | 55.0735 | 0.004577 | 0 | 0.050354 | -0.045777 | 0.53101 | 0.16937 | -0.059509 | 0.16937 | -0.059509 | 0.8194 | 123.175 | 0.53101 | 123.0606 | 123.3215 | 123.1567 | 123.1384 | 123.1567 | -123.2895 | -123.1064 | 122.9919 | 123.0606 | 54.6249 | 54.808
814.8594 | 123.2758 | -54.4235 | 68.6554 | -0.056457 | 0.00022006 | 0.061795 | 0.067791 | -0.0033369 | -0.0012391 | -0.0040524 | -0.032867 | 0.0041934 | 0.070034 | 0.070728 | -0.0073188 | 0.006539 | -0.00035666 | 0.16022 | 68.6554 | -54.5929 | 68.6005 | -53.7415 | -54.5609 | 0.46234 | 0.10986 | 68.6462 | -54.483 | 68.7241 | -53.8376 | -54.4327 | -54.1763 | -0.16937 | 0 | -0.054932 | 0.68207 | 54.8859 | -0.13733 | 55.0552 | 0.032044 | -0.059509 | -0.009156 | 0.068664 | 0.58594 | 0.24719 | -0.009155 | 0.3067 | 0.050354 | 0.85144 | 123.1934 | 0.64545 | 123.2071 | 123.2483 | 123.1293 | 123.0789 | 123.0698 | -123.2483 | -123.1384 | 123.024 | 123.1476 | 54.5837 | 54.5334
815.8906 | 123.2941 | -54.4144 | 68.6554 | -0.10986 | 0.0010745 | 0.062863 | 0.068646 | -0.0024823 | 0.00046993 | -0.010248 | -0.093903 | 0.003339 | 0.068539 | 0.063893 | -0.0073188 | 0.0071798 | -0.0012113 | 0.10529 | 68.6508 | -54.6158 | 68.7241 | -53.8422 | -54.8767 | 0.42114 | -0.027466 | 68.6279 | -54.4693 | 68.6829 | -53.8559 | -54.4601 | -54.1992 | -0.20142 | -0.004578 | 0.068664 | 0.57221 | 54.8355 | -0.46234 | 55.0369 | -0.26093 | -0.054931 | -0.027466 | 0.027465 | 0.55847 | 0.21515 | -0.045776 | 0.27008 | 0.009155 | 0.77362 | 123.3398 | 0.6134 | 123.1522 | 123.2666 | 123.0972 | 123.0652 | 123.0423 | -123.2712 | -123.1247 | 123.1384 | 123.0972 | 54.5197 | 54.3869
816.8594 | 123.2941 | -54.3228 | 68.7057 | -0.079346 | 0.00064726 | 0.063717 | 0.068005 | 0.00093573 | 0.00025633 | -0.0019162 | -0.029816 | 0.0012028 | 0.067471 | 0.065174 | -0.0086004 | 0.0054708 | -0.0012113 | 0.16937 | 68.7286 | -54.5563 | 68.6554 | -53.6728 | -54.4968 | 0.48065 | 0.12817 | 68.6783 | -54.4006 | 68.7881 | -53.7643 | -54.3732 | -54.1031 | -0.23346 | 0.022888 | -0.050354 | 0.65002 | 54.8035 | -0.17395 | 55.0369 | 0.059509 | -0.07782 | -0.027466 | 0.082397 | 0.55847 | 0.21973 | -0.050354 | 0.29755 | 0.027466 | 0.88348 | 123.2117 | 0.63629 | 123.1888 | 123.2849 | 123.0789 | 123.0515 | 123.0011 | -123.262 | -123.1064 | 122.9782 | 123.111 | 54.4922 | 54.451
817.8906 | 123.3307 | -54.3365 | 68.66 | -0.14038 | 0.0019291 | 0.064999 | 0.068218 | 0.0028583 | -0.0029481 | -0.0021298 | -0.07254 | 0.0041934 | 0.067684 | 0.073292 | -0.0073188 | 0.0091024 | 7.0538e-05 | 0.1236 | 68.7012 | -54.5471 | 68.6508 | -53.6957 | -54.5654 | 0.40283 | 0.068665 | 68.6646 | -54.4327 | 68.8019 | -53.7827 | -54.3823 | -54.0894 | -0.21057 | 0.041199 | -0.009155 | 0.64087 | 54.7394 | -0.22888 | 54.95 | -0.018311 | -0.09613 | 0.004578 | 0.14191 | 0.55389 | 0.24719 | -0.045776 | 0.34332 | 0.050354 | 0.85144 | 123.1979 | 0.65002 | 123.2346 | 123.2483 | 123.0972 | 123.0377 | 123.0011 | -123.2071 | -123.0927 | 122.9874 | 123.1384 | 54.4601 | 54.4052
818.8594 | 123.1934 | -54.3091 | 68.7698 | -0.071716 | 0.00043366 | 0.06094 | 0.068646 | 0.0011493 | -0.0031617 | -0.0021298 | -0.069489 | 0.0039798 | 0.070675 | 0.063679 | -0.0045416 | 0.006539 | -0.0031339 | 0.086975 | 68.8202 | -54.5334 | 68.5822 | -53.7598 | -54.5563 | 0.36163 | -0.045776 | 68.7927 | -54.3777 | 68.7515 | -53.8239 | -54.4418 | -54.1306 | -0.2243 | 0.050354 | -0.18768 | 0.54932 | 54.6707 | -0.24719 | 54.895 | -0.022888 | -0.068665 | 0.022889 | -0.01831 | 0.48523 | 0.17853 | -0.13275 | 0.24719 | -0.064086 | 0.77362 | 123.1155 | 0.55389 | 123.1293 | 123.3536 | 123.1705 | 123.1293 | 123.1018 | -123.3032 | -123.1476 | 122.8912 | 123.0606 | 54.3961 | 54.2633
819.9062 | 123.1705 | -54.2953 | 68.8202 | -0.056457 | 0.0025699 | 0.06094 | 0.060528 | 0.00072213 | -0.00081187 | -0.00063437 | -0.038971 | 0.004407 | 0.070461 | 0.061756 | -0.006037 | 0.0058982 | 0.00028414 | 0.12817 | 68.8156 | -54.4968 | 68.5638 | -53.7735 | -54.4785 | 0.42572 | 0.022888 | 68.7973 | -54.3686 | 68.7607 | -53.7735 | -54.3869 | -54.1397 | -0.20142 | -0.004577 | -0.25635 | 0.52185 | 54.7211 | -0.18311 | 54.9225 | 0.01831 | -0.073242 | -0.022888 | -0.059509 | 0.52185 | 0.15564 | -0.091553 | 0.22888 | -0.018311 | 0.72327 | 123.0606 | 0.59509 | 123.1293 | 123.3124 | 123.1659 | 123.111 | 123.0927 | -123.317 | -123.1888 | 122.8592 | 123.056 | 54.4235 | 54.3182
820.8594 | 123.2986 | -54.2358 | 68.7744 | -0.056457 | 0.0021427 | 0.062436 | 0.06715 | -0.0014143 | -0.0012391 | -0.0012754 | 0.0037536 | 0.0029116 | 0.068753 | 0.061543 | -0.0086004 | 0.0056846 | 0.00092494 | 0.15106 | 68.7881 | -54.451 | 68.7744 | -53.5446 | -54.4006 | 0.48065 | 0.1236 | 68.7744 | -54.332 | 68.9026 | -53.6453 | -54.2587 | -54.0161 | -0.21515 | 0.013733 | 0 | 0.69122 | 54.7165 | -0.16479 | 54.9316 | 0.050354 | -0.09613 | 0 | 0.12817 | 0.59052 | 0.21973 | -0.022888 | 0.31586 | 0.073242 | 0.90637 | 123.2254 | 0.68664 | 123.2346 | 123.2391 | 123.1064 | 123.024 | 123.0103 | -123.2254 | -123.1064 | 123.0103 | 123.1384 | 54.3869 | 54.3594
821.8906 | 123.3124 | -54.2496 | 68.7836 | -0.11749 | 0.0023563 | 0.061795 | 0.070568 | 0.0013629 | 4.273e-05 | -0.002557 | -0.063385 | 0.0037662 | 0.067471 | 0.064961 | -0.0079596 | 0.0063254 | 0.00071134 | 0.13275 | 68.7973 | -54.451 | 68.7653 | -53.5904 | -54.4464 | 0.41199 | 0.073242 | 68.7973 | -54.2999 | 68.9026 | -53.6774 | -54.2862 | -53.9795 | -0.20142 | 0.013733 | -0.01831 | 0.65918 | 54.6616 | -0.19684 | 54.863 | 0.004578 | -0.050354 | 0.013733 | 0.11902 | 0.5722 | 0.27008 | -0.036621 | 0.32043 | 0.013733 | 0.8606 | 123.2162 | 0.62256 | 123.2025 | 123.2483 | 123.0972 | 123.0469 | 123.0469 | -123.2346 | -123.0835 | 123.0148 | 123.1522 | 54.3823 | 54.3228
822.8594 | 123.2712 | -54.2084 | 68.866 | -0.01831 | 0.0015019 | 0.064999 | 0.06715 | 0.0015765 | -0.00017087 | -0.0034116 | -0.0023498 | 0.0022708 | 0.068325 | 0.060047 | -0.0081732 | 0.0061118 | -0.0031339 | 0.16479 | 68.8614 | -54.4098 | 68.7973 | -53.5263 | -54.3594 | 0.48065 | 0.086975 | 68.8385 | -54.2633 | 68.9301 | -53.627 | -54.2221 | -53.9612 | -0.20142 | -0.004578 | -0.068665 | 0.68207 | 54.689 | -0.15106 | 54.8904 | 0.050354 | -0.054932 | -0.027466 | 0.064087 | 0.58136 | 0.24719 | -0.013733 | 0.30212 | 0.041199 | 0.88348 | 123.2071 | 0.63629 | 123.1934 | 123.2712 | 123.1018 | 123.0698 | 123.0469 | -123.2758 | -123.1293 | 123.0057 | 123.1384 | 54.3732 | 54.2953
823.9062 | 123.1979 | -54.2175 | 68.8751 | -0.071716 | 0.0036381 | 0.063931 | 0.070568 | -0.00077327 | 0.00046993 | 0.00086083 | -0.11221 | 0.004407 | 0.067684 | 0.065602 | -0.0064642 | 0.0086752 | -0.00078406 | 0.11444 | 68.9072 | -54.4464 | 68.7286 | -53.595 | -54.4647 | 0.37537 | -0.018311 | 68.8843 | -54.277 | 68.8614 | -53.7048 | -54.332 | -54.0298 | -0.22888 | 0.032044 | -0.14648 | 0.62256 | 54.5929 | -0.24719 | 54.8218 | -0.018311 | -0.05951 | 0.009155 | -0.013733 | 0.5127 | 0.18768 | -0.11444 | 0.24719 | -0.054931 | 0.85144 | 123.175 | 0.57221 | 123.1384 | 123.3536 | 123.1613 | 123.1247 | 123.1018 | -123.3215 | -123.1522 | 122.9462 | 123.0789 | 54.332 | 54.1992
824.8594 | 123.3032 | -54.1443 | 68.8934 | -0.064087 | 0.0036381 | 0.062649 | 0.066937 | 0.00072213 | -0.0016663 | -0.0040524 | -0.017609 | 0.0048344 | 0.068966 | 0.061329 | -0.007105 | 0.0061118 | 0.00071134 | 0.14648 | 68.9255 | -54.3686 | 68.8339 | -53.4531 | -54.3137 | 0.48981 | 0.09613 | 68.8843 | -54.2633 | 68.9758 | -53.5446 | -54.1855 | -53.9154 | -0.2243 | 0.032043 | -0.05951 | 0.69122 | 54.6341 | -0.16937 | 54.8584 | 0.054931 | -0.11902 | -0.009156 | 0.082397 | 0.59967 | 0.22888 | -0.041199 | 0.3479 | 0.07782 | 0.91553 | 123.2025 | 0.71869 | 123.2391 | 123.2941 | 123.1476 | 123.0698 | 123.0286 | -123.262 | -123.1567 | 122.9782 | 123.1201 | 54.2908 | 54.2404
825.8906 | 123.2895 | -54.1168 | 68.8889 | -0.071716 | 0.00064726 | 0.06329 | 0.068432 | 0.00072213 | -0.0018799 | -0.0034116 | -0.0023498 | 0.0039798 | 0.067257 | 0.062397 | -0.0075324 | 0.0061118 | -0.0020657 | 0.10529 | 68.9346 | -54.3594 | 68.8065 | -53.4943 | -54.3365 | 0.46692 | 0.045776 | 68.8934 | -54.2175 | 68.9621 | -53.54 | -54.1718 | -53.8925 | -0.24262 | 0.045776 | -0.082397 | 0.62256 | 54.5837 | -0.21973 | 54.8264 | 0.022888 | -0.10071 | 0.004578 | 0.073242 | 0.57678 | 0.2243 | -0.054932 | 0.32501 | 0.045776 | 0.86517 | 123.1659 | 0.67749 | 123.1796 | 123.2941 | 123.111 | 123.0515 | 123.0103 | -123.2483 | -123.1064 | 122.9233 | 123.0789 | 54.2221 | 54.1626
826.8594 | 123.2986 | -54.0939 | 68.9209 | -0.094604 | 0.0025699 | 0.062222 | 0.067791 | 0.0015765 | 0.00089713 | -0.0021298 | -0.02066 | 0.00163 | 0.069821 | 0.062824 | -0.0083868 | 0.006539 | 0.00049774 | 0.15564 | 68.9438 | -54.3091 | 68.898 | -53.4119 | -54.2587 | 0.50812 | 0.09613 | 68.9163 | -54.1718 | 69.0308 | -53.5034 | -54.1031 | -53.8467 | -0.21515 | 0.022889 | -0.022888 | 0.68207 | 54.6021 | -0.16479 | 54.8172 | 0.050354 | -0.07782 | -0.004577 | 0.10986 | 0.59051 | 0.24719 | -0.009155 | 0.32501 | 0.068665 | 0.89722 | 123.2071 | 0.66833 | 123.2025 | 123.2529 | 123.0881 | 123.0377 | 123.0103 | -123.23 | -123.0927 | 122.9919 | 123.1247 | 54.2496 | 54.1901
827.9062 | 123.2025 | -54.1214 | 68.9804 | -0.041199 | 0.0021427 | 0.065213 | 0.070782 | -0.00034607 | -0.0012391 | 6.432e-06 | -0.066437 | 0.0014164 | 0.067471 | 0.06197 | -0.0079596 | 0.0076072 | -0.0020657 | 0.091553 | 68.985 | -54.3091 | 68.8019 | -53.5309 | -54.364 | 0.40283 | -0.068665 | 68.9896 | -54.1901 | 68.9392 | -53.6087 | -54.2313 | -53.9429 | -0.18768 | 0.004577 | -0.17853 | 0.59051 | 54.5242 | -0.24262 | 54.7119 | -0.054932 | -0.068664 | 0.009155 | -0.041199 | 0.51269 | 0.17853 | -0.10986 | 0.24719 | -0.041199 | 0.7782 | 123.111 | 0.58136 | 123.1293 | 123.2941 | 123.1796 | 123.1064 | 123.111 | -123.2895 | -123.1705 | 122.9233 | 123.0606 | 54.213 | 54.0527
828.875 | 123.2208 | -54.0756 | 68.9804 | -0.14801 | 0.00022006 | 0.06329 | 0.068646 | 0.0017901 | -0.0020935 | -0.00084817 | -0.093903 | 0.0031254 | 0.069821 | 0.06667 | -0.0068914 | 0.0073936 | -0.00099766 | 0.17395 | 69.0582 | -54.2908 | 68.866 | -53.4439 | -54.3228 | 0.42114 | 0 | 68.9941 | -54.1718 | 69.0262 | -53.54 | -54.1901 | -53.8879 | -0.21515 | 0.07782 | -0.11444 | 0.63171 | 54.4968 | -0.24719 | 54.7119 | -0.032044 | -0.09613 | 0.013733 | 0.045776 | 0.53558 | 0.18768 | -0.11444 | 0.28381 | -0.01831 | 0.84686 | 123.1567 | 0.63171 | 123.1979 | 123.349 | 123.1659 | 123.1339 | 123.0698 | -123.2712 | -123.1522 | 122.9416 | 123.1018 | 54.2496 | 54.0756
829.8906 | 123.2895 | -54.0573 | 68.9621 | -0.086975 | 0.0032107 | 0.063931 | 0.06715 | 0.0017901 | -0.0010255 | -0.0038388 | -0.042023 | -0.00050621 | 0.069607 | 0.067951 | -0.0062506 | 0.0071798 | 0.00092494 | 0.13733 | 68.9713 | -54.2816 | 68.9117 | -53.421 | -54.2725 | 0.43945 | 0.027466 | 68.9392 | -54.1672 | 69.072 | -53.476 | -54.1031 | -53.8239 | -0.2243 | 0.009155 | -0.050354 | 0.63629 | 54.4968 | -0.21515 | 54.7211 | 0.009155 | -0.10986 | -0.022888 | 0.10986 | 0.58136 | 0.23346 | -0.045776 | 0.34332 | 0.064087 | 0.86059 | 123.1934 | 0.69122 | 123.2391 | 123.2529 | 123.1064 | 123.0286 | 122.9965 | -123.2437 | -123.1293 | 122.9691 | 123.1293 | 54.1946 | 54.0848
830.8594 | 123.2895 | -54.0115 | 69.017 | -0.071716 | 0.0032107 | 0.064145 | 0.068432 | -0.00034607 | 4.273e-05 | -0.0010618 | 0.0068054 | 0.0020572 | 0.069821 | 0.06197 | -0.0064642 | 0.0069662 | 0.0032749 | 0.13733 | 69.0582 | -54.2267 | 68.9667 | -53.3295 | -54.1809 | 0.50354 | 0.068665 | 69.0033 | -54.1168 | 69.0903 | -53.421 | -54.0527 | -53.801 | -0.21515 | 0.041199 | -0.050354 | 0.68207 | 54.5151 | -0.16937 | 54.7302 | 0.045777 | -0.10529 | -0.013733 | 0.073242 | 0.59051 | 0.21057 | -0.041198 | 0.31586 | 0.064087 | 0.89722 | 123.1934 | 0.6958 | 123.2071 | 123.2849 | 123.1201 | 123.0698 | 123.0148 | -123.2437 | -123.1338 | 122.9782 | 123.1018 | 54.1489 | 54.0802
831.8906 | 123.3078 | -54.007 | 68.9941 | -0.10986 | 0.0023563 | 0.063504 | 0.069286 | 0.0020037 | -0.00081187 | 0.00022003 | -0.023712 | 0.0012028 | 0.068112 | 0.066029 | -0.007746 | 0.0073936 | -0.0014249 | 0.13733 | 69.0125 | -54.2358 | 68.9529 | -53.3432 | -54.245 | 0.46692 | 0.036621 | 68.985 | -54.1077 | 69.104 | -53.4439 | -54.0802 | -53.7918 | -0.22888 | 0.01831 | -0.041199 | 0.66376 | 54.4739 | -0.23804 | 54.7028 | -0.009155 | -0.10071 | -0.009156 | 0.10986 | 0.56305 | 0.21515 | -0.073242 | 0.31586 | 0.027466 | 0.89264 | 123.1888 | 0.66376 | 123.2117 | 123.2483 | 123.0927 | 123.0194 | 122.9919 | -123.23 | -123.1018 | 122.9599 | 123.111 | 54.1443 | 54.0436
832.8594 | 123.2849 | -53.9658 | 69.0262 | -0.094604 | 0.0017155 | 0.063931 | 0.067577 | -0.0050457 | -0.0012391 | 6.432e-06 | 0.00070198 | 0.0031254 | 0.068966 | 0.067524 | -0.0045416 | 0.006539 | -0.0035611 | 0.16937 | 69.0811 | -54.1992 | 69.0125 | -53.2791 | -54.1397 | 0.51727 | 0.068665 | 69.0491 | -54.0619 | 69.1452 | -53.3569 | -53.9886 | -53.7506 | -0.23346 | 0.054932 | -0.013733 | 0.68664 | 54.483 | -0.17395 | 54.7165 | 0.05951 | -0.096131 | 0.022888 | 0.11902 | 0.60882 | 0.21515 | -0.022888 | 0.31128 | 0.073243 | 0.9201 | 123.2117 | 0.70496 | 123.2071 | 123.2803 | 123.111 | 123.0469 | 123.0148 | -123.2254 | -123.0881 | 122.9782 | 123.111 | 54.1351 | 54.0344
833.8906 | 123.3215 | -53.9658 | 69.0308 | -0.056457 | 0.0017155 | 0.063717 | 0.070568 | -0.00013247 | -0.0027345 | -0.003198 | 0.0068054 | 0.00034819 | 0.067044 | 0.063038 | -0.0083868 | 0.006539 | -0.0014249 | 0.12817 | 69.0903 | -54.1809 | 69.0262 | -53.2333 | -54.1168 | 0.52185 | 0.07782 | 69.0491 | -54.0253 | 69.1818 | -53.3386 | -53.9658 | -53.7186 | -0.21515 | 0.059509 | -0.004578 | 0.73242 | 54.4876 | -0.15106 | 54.7028 | 0.064087 | -0.05951 | 0.01831 | 0.15106 | 0.62714 | 0.24719 | 0 | 0.3067 | 0.05951 | 0.94757 | 123.2071 | 0.68665 | 123.2071 | 123.2712 | 123.0743 | 123.056 | 123.0148 | -123.2117 | -123.056 | 122.9919 | 123.1476 | 54.0939 | 54.0436
834.8594 | 123.3124 | -53.9154 | 69.0811 | -0.079346 | 0.0029971 | 0.064145 | 0.068005 | 0.00093573 | -0.0012391 | -0.0044796 | 0.015961 | 0.0012028 | 0.06918 | 0.065174 | -0.007746 | 0.0050436 | 0.0024203 | 0.16479 | 69.0765 | -54.1351 | 69.0537 | -53.2013 | -54.1077 | 0.52643 | 0.068665 | 69.0674 | -54.0024 | 69.1956 | -53.3386 | -53.952 | -53.7003 | -0.21973 | -0.004578 | -0.027466 | 0.71411 | 54.4418 | -0.19226 | 54.6616 | 0.027466 | -0.086975 | -0.013733 | 0.11444 | 0.57678 | 0.21515 | -0.036621 | 0.30212 | 0.050354 | 0.93384 | 123.1888 | 0.66376 | 123.1979 | 123.2117 | 123.0698 | 122.9919 | 122.9828 | -123.2162 | -123.0835 | 122.9691 | 123.111 | 54.0802 | 53.9841
835.8906 | 123.2849 | -53.9474 | 69.0811 | -0.071716 | 0.0017155 | 0.065213 | 0.067577 | 0.00050853 | -0.0029481 | -0.0019162 | 0.028168 | 0.0022708 | 0.067471 | 0.063679 | -0.0096686 | 0.0071798 | 0.0013521 | 0.1236 | 69.1223 | -54.1672 | 69.017 | -53.2974 | -54.1443 | 0.49896 | 0.013733 | 69.0903 | -54.0115 | 69.1864 | -53.334 | -53.9703 | -53.6911 | -0.21973 | 0.041198 | -0.064087 | 0.65002 | 54.4464 | -0.19684 | 54.6661 | 0.022888 | -0.064087 | 0.009155 | 0.10529 | 0.6134 | 0.25635 | -0.022888 | 0.32043 | 0.041199 | 0.86975 | 123.1842 | 0.67749 | 123.1979 | 123.2895 | 123.1018 | 123.0698 | 123.0377 | -123.2483 | -123.0927 | 122.9645 | 123.1338 | 54.071 | 53.9612
836.8594 | 123.2071 | -53.9337 | 69.1544 | -0.033569 | 0.00086086 | 0.062008 | 0.068005 | -0.00077327 | -0.0025207 | -0.0017026 | -0.032867 | -0.0026426 | 0.070675 | 0.062611 | -0.0051824 | 0.0046164 | -0.0024931 | 0.15564 | 69.1544 | -54.1351 | 69.0491 | -53.2654 | -54.126 | 0.48981 | -0.032043 | 69.1315 | -54.0207 | 69.1681 | -53.54 | -54.0939 | -53.7415 | -0.20142 | 0 | -0.10529 | 0.66833 | 54.4235 | -0.19226 | 54.6249 | 0.009155 | -0.086975 | -0.022888 | 0.013733 | 0.39368 | 0.19226 | -0.16022 | 0.27924 | -0.073242 | 0.86975 | 123.1842 | 0.48065 | 123.1888 | 123.2895 | 123.1522 | 123.0881 | 123.0652 | -123.2895 | -123.175 | 122.9828 | 123.1018 | 54.0894 | 53.9017
837.8906 | 123.2941 | -53.9154 | 69.0994 | -0.094604 | 0.0040653 | 0.062863 | 0.068859 | 0.0024311 | -0.0020935 | -0.0010618 | -0.075592 | 0.0048344 | 0.067684 | 0.075215 | -0.0073188 | 0.0046164 | -0.0020657 | 0.13275 | 69.1315 | -54.158 | 69.0537 | -53.2425 | -54.158 | 0.47607 | 0 | 69.0994 | -53.9932 | 69.223 | -53.3386 | -53.9749 | -53.6911 | -0.24262 | 0.032044 | -0.045776 | 0.67291 | 54.3915 | -0.24262 | 54.6341 | 0 | -0.07782 | 0 | 0.1236 | 0.57678 | 0.2243 | -0.05951 | 0.30212 | 0.01831 | 0.91553 | 123.2117 | 0.6546 | 123.2162 | 123.2895 | 123.0927 | 123.0469 | 123.0148 | -123.2574 | -123.0927 | 122.9691 | 123.1384 | 54.0482 | 53.9154
838.8594 | 123.1842 | -53.9246 | 69.1498 | -0.041199 | -0.0025571 | 0.060727 | 0.067577 | 0.0039263 | -0.0010255 | -0.002557 | -0.023712 | 0.0012028 | 0.071102 | 0.067097 | -0.0058234 | 0.0073936 | -0.00057046 | 0.28839 | 69.2642 | -54.0894 | 69.0033 | -53.2791 | -54.1626 | 0.43488 | -0.10529 | 69.2001 | -53.9932 | 69.136 | -53.3936 | -54.0253 | -53.7643 | -0.16479 | 0.11444 | -0.14648 | 0.64545 | 54.3594 | -0.23804 | 54.5242 | -0.073243 | -0.068664 | 0.050354 | -0.013733 | 0.53101 | 0.16022 | -0.10071 | 0.22888 | -0.032044 | 0.81024 | 123.0927 | 0.59967 | 123.1293 | 123.3536 | 123.1934 | 123.1888 | 123.1247 | -123.2391 | -123.143 | 122.9279 | 123.0606 | 54.213 | 53.8193
839.8906 | 123.317 | -53.8605 | 69.1406 | -0.048828 | 0.00086086 | 0.062008 | 0.067577 | 0.0026447 | 0.00089713 | 0.00086083 | -0.011505 | 0.0018436 | 0.068753 | 0.06432 | -0.007105 | 0.0046164 | 0.0011385 | 0.10986 | 69.1589 | -54.0985 | 69.1086 | -53.1509 | -54.0024 | 0.54016 | 0.068665 | 69.1452 | -53.952 | 69.2505 | -53.2471 | -53.8742 | -53.6407 | -0.23804 | 0.018311 | -0.032043 | 0.70953 | 54.4006 | -0.14191 | 54.6387 | 0.096131 | -0.091552 | 0.004578 | 0.10986 | 0.6134 | 0.21973 | -0.013733 | 0.31128 | 0.077819 | 0.94757 | 123.2071 | 0.70496 | 123.2025 | 123.2574 | 123.0972 | 123.0194 | 123.0057 | -123.2391 | -123.0927 | 122.9691 | 123.111 | 53.9703 | 53.9291
840.8594 | 123.3124 | -53.8742 | 69.1772 | -0.079346 | 6.46e-06 | 0.063076 | 0.068646 | -0.00098687 | -0.0042297 | 0.00022003 | -0.0023498 | 0.0035526 | 0.066616 | 0.062824 | -0.0079596 | 0.0061118 | -0.0014249 | 0.16479 | 69.1727 | -54.0665 | 69.1406 | -53.1143 | -53.9886 | 0.52643 | 0.041199 | 69.1544 | -53.9474 | 69.278 | -53.2242 | -53.8605 | -53.6087 | -0.19226 | -0.004578 | -0.036621 | 0.75989 | 54.4006 | -0.11444 | 54.5929 | 0.07782 | -0.073242 | -0.022888 | 0.10071 | 0.65002 | 0.2655 | 0.013733 | 0.33874 | 0.086975 | 0.95215 | 123.2071 | 0.72327 | 123.2254 | 123.2391 | 123.1018 | 123.0469 | 123.0286 | -123.2437 | -123.1247 | 123.0148 | 123.1522 | 54.039 | 53.9154
841.9062 | 123.2162 | -53.8742 | 69.1864 | -0.094604 | 0.0019291 | 0.063504 | 0.069286 | 0.0015765 | -0.0014527 | -0.00042077 | -0.12747 | 0.0020572 | 0.06918 | 0.073506 | -0.0066778 | 0.0071798 | -0.0022793 | 0.11902 | 69.223 | -54.1168 | 69.0628 | -53.2379 | -54.1214 | 0.42572 | -0.07782 | 69.2276 | -53.9658 | 69.1956 | -53.3432 | -54.0161 | -53.7048 | -0.24261 | 0.036621 | -0.1236 | 0.63629 | 54.2999 | -0.24719 | 54.5425 | -0.004578 | -0.091552 | 0.041199 | 0.009156 | 0.53101 | 0.16937 | -0.14191 | 0.26093 | -0.050354 | 0.87891 | 123.1796 | 0.62256 | 123.1613 | 123.3398 | 123.1934 | 123.0972 | 123.1018 | -123.3032 | -123.1522 | 122.937 | 123.0698 | 53.9932 | 53.7964
842.8594 | 123.2941 | -53.8193 | 69.1864 | -0.094604 | 0.0034245 | 0.064145 | 0.066723 | -0.0056867 | -0.0025207 | -0.0010618 | -0.02066 | 0.00056179 | 0.068539 | 0.062824 | -0.007105 | 0.0063254 | 0.0013521 | 0.15106 | 69.223 | -54.0115 | 69.1818 | -53.1052 | -54.0024 | 0.53101 | 0.041199 | 69.2001 | -53.8971 | 69.2917 | -53.2104 | -53.8376 | -53.5904 | -0.19226 | 0.036621 | -0.004577 | 0.71411 | 54.3503 | -0.18311 | 54.5425 | 0.009156 | -0.07782 | 0.013733 | 0.10529 | 0.60883 | 0.22888 | -0.01831 | 0.3067 | 0.05951 | 0.90637 | 123.1934 | 0.68665 | 123.1888 | 123.2346 | 123.0972 | 123.0423 | 123.0194 | -123.1979 | -123.0835 | 123.0011 | 123.111 | 53.9703 | 53.8605
843.9062 | 123.2117 | -53.8376 | 69.2184 | -0.01831 | 0.0017155 | 0.062863 | 0.070355 | 0.00093573 | -0.0018799 | -0.00042077 | -0.090851 | 0.0037662 | 0.068539 | 0.067311 | -0.0056098 | 0.0058982 | -0.00014306 | 0.091553 | 69.2688 | -54.0894 | 69.0811 | -53.2516 | -54.0848 | 0.41657 | -0.14191 | 69.2688 | -53.9291 | 69.2276 | -53.2883 | -53.9429 | -53.6728 | -0.25177 | 0.050354 | -0.13733 | 0.58594 | 54.2541 | -0.24719 | 54.5059 | 0.004577 | -0.091553 | 0.050354 | 0.009155 | 0.54932 | 0.16479 | -0.10529 | 0.25635 | -0.013733 | 0.83771 | 123.1705 | 0.64087 | 123.1567 | 123.3582 | 123.1979 | 123.1064 | 123.1064 | -123.3078 | -123.1476 | 122.9187 | 123.0652 | 53.9291 | 53.6957
844.8594 | 123.2712 | -53.8239 | 69.2184 | -0.079346 | 0.0017155 | 0.064785 | 0.066509 | 8.1126e-05 | 0.00089713 | -0.002557 | 0.0098572 | 0.00163 | 0.070034 | 0.059193 | -0.0049688 | 0.0058982 | -0.0022793 | 0.15106 | 69.2551 | -53.9932 | 69.1635 | -53.1006 | -53.9749 | 0.52185 | -0.013733 | 69.2184 | -53.8834 | 69.2825 | -53.2196 | -53.8605 | -53.6087 | -0.16937 | 0.036621 | -0.054932 | 0.72327 | 54.3457 | -0.15106 | 54.5151 | 0.01831 | -0.059509 | 0 | 0.064087 | 0.60425 | 0.21515 | -0.036621 | 0.27466 | 0.022888 | 0.89264 | 123.1567 | 0.66376 | 123.1659 | 123.2483 | 123.1018 | 123.0789 | 123.0423 | -123.2117 | -123.1018 | 122.9874 | 123.1064 | 53.9749 | 53.8101
845.8906 | 123.262 | -53.7918 | 69.2093 | -0.079346 | 0.0015019 | 0.062222 | 0.06715 | 0.0022173 | -0.0046571 | -0.0023434 | -0.0023498 | 0.002698 | 0.068325 | 0.067311 | -0.0096686 | 0.006539 | 0.00049774 | 0.082397 | 69.2459 | -54.0344 | 69.1132 | -53.1738 | -54.0482 | 0.45776 | -0.07782 | 69.2276 | -53.8834 | 69.2825 | -53.2425 | -53.8696 | -53.5858 | -0.24262 | 0.036621 | -0.096131 | 0.61798 | 54.2496 | -0.25635 | 54.4922 | -0.013733 | -0.091553 | 0.01831 | 0.073242 | 0.54932 | 0.20599 | -0.07782 | 0.29755 | 0.013733 | 0.8606 | 123.1476 | 0.64087 | 123.1659 | 123.2803 | 123.111 | 123.0377 | 123.0194 | -123.2437 | -123.0927 | 122.905 | 123.0743 | 53.8742 | 53.714
846.875 | 123.1613 | -53.8193 | 69.2322 | -0.10223 | -0.00020714 | 0.064358 | 0.069286 | 0.0047809 | -0.00038447 | 0.00064723 | -0.10001 | 0.0024844 | 0.06918 | 0.068592 | -0.008814 | 0.0063254 | 0.0028475 | 0.07782 | 69.278 | -54.0436 | 69.0994 | -53.2104 | -54.0802 | 0.3891 | -0.15106 | 69.2596 | -53.9062 | 69.2368 | -53.2974 | -53.9749 | -53.6591 | -0.2243 | 0.045776 | -0.13275 | 0.60883 | 54.2084 | -0.26093 | 54.4327 | -0.036621 | -0.086975 | 0.027466 | 0.004577 | 0.52185 | 0.16022 | -0.15564 | 0.24719 | -0.068665 | 0.83313 | 123.143 | 0.60883 | 123.143 | 123.3215 | 123.1659 | 123.0972 | 123.0789 | -123.2758 | -123.1384 | 122.9187 | 123.056 | 53.8971 | 53.6682
847.8906 | 123.3078 | -53.8101 | 69.2184 | -0.11749 | 0.0012881 | 0.063717 | 0.068646 | 0.0020037 | -0.0014527 | -0.00063437 | -0.011505 | -0.00071981 | 0.068966 | 0.05962 | -0.006037 | 0.0086752 | 0.0037021 | 0.11444 | 69.2596 | -54.0344 | 69.191 | -53.096 | -53.9932 | 0.48065 | -0.027466 | 69.2413 | -53.8788 | 69.3558 | -53.1921 | -53.8422 | -53.5629 | -0.2243 | 0.041199 | -0.027466 | 0.71411 | 54.2908 | -0.18311 | 54.5151 | 0.041199 | -0.068664 | 0.022888 | 0.13733 | 0.61798 | 0.24719 | -0.032043 | 0.31586 | 0.036621 | 0.93842 | 123.2254 | 0.68665 | 123.2346 | 123.2941 | 123.1201 | 123.0698 | 123.0515 | -123.2529 | -123.0972 | 123.0011 | 123.1659 | 53.9246 | 53.7827
848.8594 | 123.2483 | -53.7827 | 69.2917 | -0.094604 | 0.0040653 | 0.064145 | 0.068005 | -0.0037641 | -0.0012391 | -0.0023434 | -0.032867 | 0.00098899 | 0.065121 | 0.064533 | -0.0075324 | 0.0063254 | 0.00092494 | 0.15106 | 69.3054 | -53.9612 | 69.1864 | -53.0731 | -53.952 | 0.50812 | -0.059509 | 69.2825 | -53.8513 | 69.4611 | -53.1738 | -54.1306 | -53.7643 | -0.17853 | 0.013733 | -0.10529 | 0.70953 | 54.2908 | -0.16937 | 54.4693 | 0.009156 | -0.068664 | -0.009155 | 0.16937 | 0.60883 | 0.018311 | -0.3479 | 0.086975 | -0.27924 | 0.88806 | 123.1476 | 0.67749 | 123.3124 | 123.2666 | 123.1338 | 123.0881 | 123.0652 | -123.2529 | -123.143 | 122.9691 | 123.2437 | 53.9337 | 53.7231
849.8906 | 123.3261 | -53.7506 | 69.2642 | -0.041199 | 0.0017155 | 0.062649 | 0.068432 | -0.0012005 | 4.273e-05 | -0.00063437 | -0.0054016 | 0.0018436 | 0.068539 | 0.058766 | -0.007105 | 0.0061118 | 7.0538e-05 | 0.15106 | 69.31 | -53.952 | 69.2459 | -53.0228 | -53.9062 | 0.53101 | 0.013733 | 69.2734 | -53.833 | 69.3787 | -53.1097 | -53.7506 | -53.5217 | -0.20142 | 0.045777 | -0.01831 | 0.72784 | 54.2816 | -0.15564 | 54.483 | 0.045776 | -0.082398 | 0.009155 | 0.11444 | 0.64087 | 0.22888 | 0 | 0.31128 | 0.082398 | 0.92926 | 123.1979 | 0.72327 | 123.2117 | 123.262 | 123.1064 | 123.0606 | 123.024 | -123.2162 | -123.0972 | 122.9965 | 123.1293 | 53.9017 | 53.7643
850.8594 | 123.3032 | -53.746 | 69.2963 | -0.056457 | -0.00063454 | 0.062436 | 0.068432 | -0.00055967 | 0.0011109 | -0.0021298 | 0.0037536 | 0.0024844 | 0.070248 | 0.06432 | -0.0053962 | 0.0061118 | 0.00071134 | 0.14648 | 69.3054 | -53.952 | 69.2551 | -53.0045 | -53.8834 | 0.54474 | 0.009155 | 69.2825 | -53.8193 | 69.397 | -53.1052 | -53.7506 | -53.4988 | -0.20599 | 0.009155 | -0.041199 | 0.74158 | 54.2908 | -0.13733 | 54.4968 | 0.068664 | -0.073242 | -0.013733 | 0.10071 | 0.64087 | 0.24719 | -0.004577 | 0.32043 | 0.068665 | 0.94757 | 123.2071 | 0.71411 | 123.2162 | 123.2574 | 123.1018 | 123.0515 | 123.0286 | -123.2483 | -123.1155 | 123.0011 | 123.143 | 53.8925 | 53.7552
851.875 | 123.2437 | -53.7643 | 69.3329 | -0.071716 | 0.0015019 | 0.060727 | 0.069073 | 0.0026447 | -0.0023071 | -0.0010618 | -0.10306 | 0.0037662 | 0.06918 | 0.067951 | -0.0073188 | 0.0091024 | -0.0039883 | 0.068665 | 69.3237 | -54.0024 | 69.1406 | -53.1647 | -54.0436 | 0.3891 | -0.18768 | 69.3329 | -53.8376 | 69.3649 | -53.1372 | -54.0161 | -53.5812 | -0.23804 | -0.009156 | -0.19226 | 0.59967 | 54.1534 | -0.27924 | 54.3915 | -0.041199 | -0.073242 | 0 | 0.032043 | 0.62714 | 0.1831 | -0.25177 | 0.25635 | -0.17853 | 0.83771 | 123.143 | 0.70038 | 123.2025 | 123.3261 | 123.1705 | 123.0881 | 123.0972 | -123.3353 | -123.1705 | 122.905 | 123.1293 | 53.833 | 53.5767
852.8594 | 123.2941 | -53.7094 | 69.3146 | -0.056457 | 0.0021427 | 0.063076 | 0.066082 | -0.0020551 | -0.0012391 | -0.0034116 | 0.0068054 | 0.0031254 | 0.067684 | 0.060688 | -0.006037 | 0.003121 | 0.0013521 | 0.15564 | 69.3375 | -53.9154 | 69.2871 | -52.9724 | -53.8788 | 0.54932 | 0 | 69.342 | -53.801 | 69.4244 | -53.0777 | -53.714 | -53.4622 | -0.20599 | 0.022888 | -0.027466 | 0.737 | 54.2587 | -0.16937 | 54.4647 | 0.036621 | -0.091552 | 0.027466 | 0.10986 | 0.63171 | 0.24719 | -0.004577 | 0.33875 | 0.086975 | 0.94299 | 123.2025 | 0.72327 | 123.2254 | 123.2529 | 123.143 | 123.0469 | 123.0515 | -123.23 | -123.1155 | 122.9965 | 123.1338 | 53.8651 | 53.7094
853.8594 | 123.1934 | -53.7552 | 69.3604 | -0.056457 | 0.0034245 | 0.061581 | 0.068218 | 0.0015765 | -0.0016663 | -0.0034116 | 0.012909 | -0.00029261 | 0.069393 | 0.061329 | -0.0079596 | 0.0052572 | -0.0039883 | 0.13275 | 69.3649 | -53.9291 | 69.278 | -52.803 | -54.0573 | 0.33875 | -0.1236 | 69.3741 | -53.8376 | 69.3283 | -53.2013 | -53.8467 | -53.5675 | -0.17395 | 0.004577 | -0.082398 | 0.95215 | 54.0939 | -0.30212 | 54.2679 | -0.12817 | -0.082397 | 0.013732 | -0.032044 | 0.55389 | 0.18768 | -0.091553 | 0.27008 | -0.009156 | 1.1261 | 123.2071 | 0.63629 | 123.1659 | 123.2941 | 123.2117 | 123.1201 | 123.1293 | -123.2895 | -123.1979 | 123.0331 | 123.0835 | 53.8879 | 53.6316
854.8594 | 123.3215 | -53.6865 | 69.342 | -0.064087 | 0.0015019 | 0.063717 | 0.069927 | 0.0011493 | 0.00068353 | 0.00086083 | 0.00070198 | 0.00163 | 0.067684 | 0.060047 | -0.006037 | 0.0056846 | -0.0027067 | 0.15564 | 69.3832 | -53.9108 | 69.31 | -52.9449 | -53.8284 | 0.54932 | 0 | 69.3054 | -53.7918 | 69.4382 | -53.0594 | -53.6911 | -53.4531 | -0.22431 | 0.041199 | -0.032043 | 0.74158 | 54.2358 | -0.14191 | 54.4601 | 0.082398 | -0.10529 | -0.036621 | 0.09613 | 0.62714 | 0.23346 | -0.004578 | 0.33875 | 0.10071 | 0.96588 | 123.2208 | 0.73242 | 123.23 | 123.2941 | 123.0972 | 123.0698 | 122.9919 | -123.2529 | -123.1338 | 122.9965 | 123.1247 | 53.8422 | 53.6865
855.8594 | 123.2849 | -53.6865 | 69.3466 | -0.064087 | 0.0027835 | 0.062649 | 0.068432 | 0.0020037 | 0.00025633 | -0.0027708 | 0.0098572 | 0.0022708 | 0.070034 | 0.060047 | -0.0066778 | 0.0058982 | 0.0030611 | 0.12817 | 69.3558 | -53.8971 | 69.2596 | -53.009 | -53.8925 | 0.51727 | -0.050354 | 69.31 | -53.7552 | 69.5389 | -53.2333 | -53.714 | -53.3936 | -0.21057 | 0.009155 | -0.086975 | 0.67749 | 54.2038 | -0.20599 | 54.4144 | 0.004578 | -0.068665 | -0.036621 | 0.19226 | 0.45319 | 0.29297 | -0.027466 | 0.36163 | 0.041199 | 0.88806 | 123.1567 | 0.52185 | 123.2941 | 123.2529 | 123.0652 | 123.0423 | 122.9965 | -123.2437 | -123.1018 | 122.9462 | 123.2254 | 53.8147 | 53.6362
856.875 | 123.1476 | -53.7506 | 69.3237 | 0.042725 | 0.0010745 | 0.063717 | 0.070355 | 0.0058489 | -0.0016663 | -0.0038388 | -0.10916 | 0.0037662 | 0.067471 | 0.073078 | -0.0083868 | 0.0084616 | 0.0011385 | 0.2655 | 69.3878 | -53.9612 | 69.1818 | -53.1647 | -53.9795 | 0.37537 | -0.24719 | 69.3787 | -53.833 | 69.3146 | -53.2562 | -53.9154 | -53.6133 | -0.21057 | 0.064087 | -0.14191 | 0.58594 | 54.126 | -0.22888 | 54.3365 | -0.01831 | -0.082398 | 0.054932 | -0.009155 | 0.49438 | 0.13733 | -0.16479 | 0.21973 | -0.082397 | 0.79651 | 123.143 | 0.57678 | 123.1476 | 123.349 | 123.2117 | 123.1384 | 123.1293 | -123.2849 | -123.1567 | 122.9324 | 123.0652 | 54.0161 | 53.5034
857.8906 | 123.2666 | -53.7048 | 69.3466 | -0.071716 | 0.0032107 | 0.062436 | 0.066937 | 0.0052081 | -0.0010255 | -0.004907 | -0.0084534 | 0.00056179 | 0.068112 | 0.065174 | -0.0064642 | 0.0056846 | -0.0022793 | 0.07782 | 69.3558 | -53.9383 | 69.223 | -53.0685 | -53.9154 | 0.46692 | -0.15106 | 69.342 | -53.8055 | 69.3878 | -53.1464 | -53.7735 | -53.4805 | -0.23346 | 0.009155 | -0.1236 | 0.63629 | 54.1718 | -0.21057 | 54.4052 | 0.022888 | -0.10071 | -0.004578 | 0.041198 | 0.55847 | 0.2243 | -0.068665 | 0.32501 | 0.032043 | 0.86975 | 123.1613 | 0.65918 | 123.1934 | 123.2941 | 123.1476 | 123.0606 | 123.0469 | -123.2849 | -123.1522 | 122.9279 | 123.0927 | 53.7827 | 53.5538
858.8594 | 123.2208 | -53.7048 | 69.3924 | -0.064087 | 0.0019291 | 0.063504 | 0.069073 | 0.00093573 | -0.0040161 | -0.0019162 | -0.023712 | 0.00098899 | 0.06918 | 0.06966 | -0.0056098 | 0.0054708 | -0.00057046 | 0.13275 | 69.4199 | -53.8834 | 69.278 | -52.9907 | -53.8696 | 0.49896 | -0.09613 | 69.3695 | -53.7506 | 69.2917 | -53.064 | -53.7643 | -53.4897 | -0.17853 | 0.027466 | -0.11444 | 0.71411 | 54.2038 | -0.1648 | 54.3823 | 0.013733 | -0.045776 | -0.022888 | -0.10071 | 0.64087 | 0.21515 | -0.059509 | 0.26093 | -0.013733 | 0.89264 | 123.1613 | 0.68664 | 123.0423 | 123.3032 | 123.1201 | 123.1247 | 123.0743 | -123.2758 | -123.143 | 122.9828 | 122.9965 | 53.8376 | 53.6087
859.8906 | 123.2849 | -53.6774 | 69.342 | -0.15564 | 0.0025699 | 0.065426 | 0.067577 | 0.0047809 | -0.0010255 | -0.002557 | -0.032867 | 0.0037662 | 0.068112 | 0.067524 | -0.0073188 | 0.0067526 | 0.0013521 | 0.11444 | 69.3741 | -53.9017 | 69.3008 | -52.9816 | -53.9017 | 0.48523 | -0.07782 | 69.3466 | -53.7643 | 69.4519 | -53.1006 | -53.7415 | -53.4622 | -0.2243 | 0.032043 | -0.041199 | 0.6958 | 54.1626 | -0.2243 | 54.3869 | 0 | -0.086975 | 0.004578 | 0.10986 | 0.57678 | 0.21515 | -0.064087 | 0.30212 | 0.022888 | 0.9201 | 123.2025 | 0.66376 | 123.2162 | 123.2758 | 123.111 | 123.0515 | 123.024 | -123.2437 | -123.1064 | 122.9782 | 123.1293 | 53.7918 | 53.5995
860.8594 | 123.2895 | -53.6362 | 69.3787 | -0.064087 | 0.00086086 | 0.06329 | 0.0695 | 0.0022173 | -0.0023071 | -0.0010618 | -0.014557 | 0.003339 | 0.068112 | 0.067311 | -0.0090278 | 0.006539 | -0.00014306 | 0.1236 | 69.3878 | -53.8742 | 69.3375 | -52.9312 | -53.8193 | 0.54016 | -0.045776 | 69.3695 | -53.7003 | 69.4748 | -53.0273 | -53.6728 | -53.4027 | -0.23804 | 0.009155 | -0.041199 | 0.70496 | 54.1763 | -0.18311 | 54.4144 | 0.054932 | -0.064087 | -0.009155 | 0.09613 | 0.60883 | 0.23346 | -0.036622 | 0.29755 | 0.027465 | 0.94299 | 123.2117 | 0.67291 | 123.175 | 123.262 | 123.0698 | 123.024 | 123.0057 | -123.2529 | -123.0789 | 122.9736 | 123.111 | 53.7598 | 53.5904
861.8594 | 123.2208 | -53.7186 | 69.3695 | -0.079346 | 0.0017155 | 0.063504 | 0.070141 | -0.00055967 | -0.0014527 | -0.00084817 | -0.087799 | 0.003339 | 0.071316 | 0.067311 | -0.0066778 | 0.0080344 | 0.00071134 | 0.032043 | 69.4153 | -53.8925 | 69.1956 | -53.1143 | -53.9932 | 0.37994 | -0.22888 | 69.3832 | -53.7918 | 69.3787 | -53.183 | -53.833 | -53.5126 | -0.17395 | 0.045776 | -0.17395 | 0.60425 | 54.0985 | -0.27466 | 54.2725 | -0.10071 | -0.073242 | 0.013733 | 0.009155 | 0.53558 | 0.20599 | -0.11444 | 0.27924 | -0.041199 | 0.7782 | 123.0881 | 0.60883 | 123.1705 | 123.3078 | 123.175 | 123.1338 | 123.1018 | -123.262 | -123.1613 | 122.9141 | 123.0972 | 53.7506 | 53.4897
862.8906 | 123.2849 | -53.6728 | 69.3649 | -0.079346 | -0.0010617 | 0.063717 | 0.067791 | 0.00050853 | -0.0010255 | -0.0019162 | -0.0054016 | 0.00013459 | 0.069607 | 0.064961 | -0.0058234 | 0.0054708 | -0.00099766 | 0.059509 | 69.4061 | -53.8925 | 69.2688 | -53.0182 | -53.8971 | 0.46692 | -0.16022 | 69.3741 | -53.7598 | 69.429 | -53.096 | -53.7506 | -53.4576 | -0.21973 | 0.041199 | -0.09613 | 0.6546 | 54.1397 | -0.2243 | 54.3594 | -0.004578 | -0.086975 | 0.009155 | 0.064087 | 0.57678 | 0.21515 | -0.077819 | 0.30212 | 0.009156 | 0.87433 | 123.1613 | 0.66376 | 123.1888 | 123.2986 | 123.1338 | 123.0789 | 123.0469 | -123.2574 | -123.1247 | 122.9416 | 123.1018 | 53.7323 | 53.5126
863.8594 | 123.3307 | -53.627 | 69.3741 | -0.0030519 | 0.0044925 | 0.06329 | 0.067364 | -0.0022687 | -0.0031617 | -0.001489 | -0.011505 | 0.00056179 | 0.066616 | 0.06197 | -0.0079596 | 0.0050436 | -0.00078406 | 0.027466 | 69.397 | -53.8651 | 69.3512 | -52.8992 | -53.8147 | 0.55847 | -0.013733 | 69.3787 | -53.7094 | 69.5023 | -52.9816 | -53.6224 | -53.3844 | -0.23804 | 0.022889 | -0.022888 | 0.72784 | 54.1855 | -0.18768 | 54.4235 | 0.050354 | -0.082398 | 0.004578 | 0.12817 | 0.64545 | 0.24262 | 0.004577 | 0.32501 | 0.086975 | 0.96588 | 123.2162 | 0.72785 | 123.2117 | 123.262 | 123.0881 | 123.024 | 123.0057 | -123.2391 | -123.0835 | 122.9782 | 123.1293 | 53.6545 | 53.6133
864.9062 | 123.143 | -53.6636 | 69.4336 | -0.079346 | 0.0027835 | 0.062649 | 0.071423 | 0.0017901 | -0.0014527 | 0.0010746 | -0.10611 | 0.005048 | 0.071102 | 0.066883 | -0.0083868 | 0.0071798 | -0.0016385 | 0.054932 | 69.4611 | -53.8879 | 69.2505 | -53.0502 | -53.8879 | 0.44403 | -0.20142 | 69.4427 | -53.7231 | 69.4519 | -53.0823 | -53.7552 | -53.4439 | -0.2243 | 0.027466 | -0.18311 | 0.6134 | 54.1077 | -0.2243 | 54.332 | 0 | -0.05951 | 0.009155 | 0.01831 | 0.58136 | 0.21973 | -0.091553 | 0.27924 | -0.032043 | 0.83771 | 123.1384 | 0.64087 | 123.175 | 123.349 | 123.1659 | 123.1247 | 123.1064 | -123.3215 | -123.1567 | 122.9141 | 123.1155 | 53.7186 | 53.4622
865.8594 | 123.3353 | -53.6133 | 69.3832 | -0.27008 | -0.0010617 | 0.062649 | 0.068859 | -0.0014143 | 0.0015381 | -0.0019162 | 0.0098572 | 0.0022708 | 0.069821 | 0.061756 | -0.0092414 | 0.006539 | -0.0024931 | 0.11902 | 69.429 | -53.8513 | 69.3237 | -52.9083 | -53.7689 | 0.53101 | -0.036621 | 69.3787 | -53.6774 | 69.5251 | -52.977 | -53.6179 | -53.3844 | -0.23804 | 0.045776 | -0.05951 | 0.70496 | 54.1443 | -0.15564 | 54.3823 | 0.082397 | -0.064087 | -0.004578 | 0.14191 | 0.63629 | 0.22888 | -0.004578 | 0.29297 | 0.059509 | 0.94299 | 123.175 | 0.70038 | 123.2025 | 123.2803 | 123.056 | 123.0423 | 122.9919 | -123.2346 | -123.0606 | 122.937 | 123.1384 | 53.7323 | 53.5767
866.8906 | 123.2529 | -53.6499 | 69.3832 | -0.071716 | 0.0015019 | 0.062222 | 0.065868 | 0.0020037 | -0.0033753 | -0.0010618 | -0.017609 | 0.00077539 | 0.069607 | 0.060688 | -0.0081732 | 0.0058982 | 0.00049774 | 0.041199 | 69.429 | -53.8651 | 69.2871 | -52.9999 | -53.8788 | 0.46692 | -0.18768 | 69.3878 | -53.7369 | 69.4427 | -53.0685 | -53.7277 | -53.4531 | -0.21515 | 0.045776 | -0.096131 | 0.65002 | 54.1168 | -0.22888 | 54.332 | -0.013733 | -0.086975 | 0.004577 | 0.059509 | 0.58136 | 0.19684 | -0.07782 | 0.28381 | 0.009155 | 0.86517 | 123.1522 | 0.66833 | 123.1796 | 123.2941 | 123.1247 | 123.0789 | 123.0377 | -123.2483 | -123.1201 | 122.937 | 123.0927 | 53.6911 | 53.4622
867.8594 | 123.3261 | -53.6133 | 69.4016 | -0.041199 | 0.0034245 | 0.064572 | 0.067791 | 0.0015765 | -0.0014527 | -0.0038388 | -0.0023498 | 0.0029116 | 0.070248 | 0.056416 | -0.0075324 | 0.0076072 | 0.00028414 | 0.041199 | 69.3924 | -53.9108 | 69.342 | -52.8854 | -53.7872 | 0.56763 | -0.054932 | 69.3878 | -53.6957 | 69.5435 | -52.977 | -53.627 | -53.3661 | -0.29755 | -0.009155 | -0.059509 | 0.72784 | 54.1809 | -0.17395 | 54.4785 | 0.1236 | -0.082398 | -0.013733 | 0.14191 | 0.63629 | 0.24719 | -0.013733 | 0.32959 | 0.068665 | 1.0254 | 123.2529 | 0.71869 | 123.2391 | 123.3032 | 123.0835 | 123.0057 | 123.0011 | -123.3124 | -123.0972 | 122.9553 | 123.1567 | 53.6545 | 53.5583
868.9062 | 123.2208 | -53.6453 | 69.4336 | -0.033569 | 0.0019291 | 0.061581 | 0.069286 | 0.0043537 | -0.0010255 | -0.00020717 | -0.096954 | 0.0035526 | 0.068112 | 0.068592 | -0.0066778 | 0.0067526 | -0.0039883 | 0.082397 | 69.4611 | -53.8513 | 69.2963 | -52.9861 | -53.8559 | 0.45319 | -0.17853 | 69.4336 | -53.7369 | 69.4656 | -53.0731 | -53.7369 | -53.4531 | -0.20599 | 0.027466 | -0.13733 | 0.65918 | 54.0985 | -0.21057 | 54.3045 | -0.004578 | -0.091552 | 0 | 0.032043 | 0.5722 | 0.19226 | -0.091552 | 0.28381 | 0 | 0.86517 | 123.1476 | 0.66376 | 123.2025 | 123.3124 | 123.1705 | 123.1064 | 123.0789 | -123.2849 | -123.1705 | 122.9416 | 123.111 | 53.7277 | 53.4668
869.8594 | 123.2849 | -53.6179 | 69.4061 | -0.10986 | 0.0036381 | 0.063504 | 0.067364 | -0.00034607 | 0.0013245 | -0.0019162 | -0.0054016 | 0.0024844 | 0.067044 | 0.066242 | -0.0073188 | 0.0058982 | -0.0039883 | 0.10986 | 69.4244 | -53.833 | 69.3787 | -52.8854 | -53.7735 | 0.52185 | -0.091553 | 69.429 | -53.6728 | 69.5068 | -52.9953 | -53.6362 | -53.3707 | -0.21515 | 0.01831 | -0.027466 | 0.73242 | 54.1397 | -0.15564 | 54.3549 | 0.059509 | -0.054932 | 0.022888 | 0.10071 | 0.62256 | 0.24719 | -0.01831 | 0.30212 | 0.036622 | 0.94757 | 123.2117 | 0.67749 | 123.1796 | 123.2574 | 123.1018 | 123.0423 | 123.0469 | -123.2391 | -123.0789 | 122.9965 | 123.1247 | 53.7277 | 53.5263
870.9062 | 123.1567 | -53.6774 | 69.4656 | -0.048828 | 0.0029971 | 0.06329 | 0.070355 | 0.0054217 | -0.0038025 | -0.002557 | -0.11832 | 0.0048344 | 0.070034 | 0.062184 | -0.0090278 | 0.0035482 | 0.0015659 | 0.032043 | 69.4473 | -53.8696 | 69.2551 | -53.0502 | -53.9429 | 0.36621 | -0.26093 | 69.4427 | -53.7689 | 69.3649 | -53.096 | -53.7277 | -53.4988 | -0.19226 | -0.01831 | -0.21057 | 0.62714 | 54.0436 | -0.2655 | 54.2358 | -0.073242 | -0.091553 | -0.022888 | -0.10071 | 0.58136 | 0.17853 | -0.050354 | 0.27008 | 0.041199 | 0.8194 | 123.1247 | 0.67291 | 123.1338 | 123.317 | 123.2117 | 123.1247 | 123.1201 | -123.3353 | -123.2346 | 122.9324 | 123.0423 | 53.7094 | 53.4164
871.8594 | 123.2712 | -53.6041 | 69.4107 | -0.041199 | 0.0029971 | 0.062436 | 0.066723 | 0.00050853 | -0.0018799 | -0.004266 | 0.0068054 | 0.0035526 | 0.070675 | 0.065815 | -0.0073188 | 0.0063254 | 0.0024203 | 0.11444 | 69.4382 | -53.8193 | 69.3695 | -52.8671 | -53.7689 | 0.52643 | -0.082397 | 69.4107 | -53.7003 | 69.5023 | -52.9816 | -53.6316 | -53.3661 | -0.21515 | 0.027465 | -0.041199 | 0.737 | 54.1306 | -0.16479 | 54.3457 | 0.050354 | -0.09613 | 0 | 0.091552 | 0.62256 | 0.23804 | -0.027466 | 0.33417 | 0.068664 | 0.95215 | 123.1888 | 0.71869 | 123.2025 | 123.2574 | 123.111 | 123.0423 | 123.0148 | -123.23 | -123.111 | 122.9736 | 123.1064 | 53.7186 | 53.5217
872.8906 | 123.3032 | -53.6087 | 69.3878 | -0.033569 | 0.0019291 | 0.063931 | 0.068005 | 0.0043537 | 0.0011109 | -0.0044796 | -0.18546 | 0.0031254 | 0.069393 | 0.064106 | -0.0079596 | 0.0054708 | -0.00099766 | 0.086975 | 69.4382 | -53.8193 | 69.3558 | -53.1235 | -53.1921 | 0.69122 | -0.009155 | 69.3924 | -53.7231 | 69.516 | -52.9953 | -53.5995 | -53.3752 | -0.21057 | 0.050354 | -0.032043 | 0.48523 | 54.2999 | 0.41657 | 54.5105 | 0.62714 | -0.11444 | 0.004578 | 0.12817 | 0.6134 | 0.23346 | 0.009156 | 0.3479 | 0.1236 | 0.6958 | 123.175 | 0.72785 | 123.2391 | 123.2574 | 123.1155 | 123.0469 | 123.0011 | -123.2071 | -123.111 | 122.9645 | 123.1247 | 53.6957 | 53.5995
873.8594 | 123.2483 | -53.627 | 69.4748 | -0.056457 | 0.0023563 | 0.062863 | 0.066296 | 0.00050853 | -0.00081187 | -0.0021298 | -0.032867 | 0.0035526 | 0.067471 | 0.068165 | -0.0079596 | 0.0046164 | -0.0039883 | 0.086975 | 69.4382 | -53.8376 | 69.3558 | -52.9083 | -53.7781 | 0.49439 | -0.15564 | 69.4473 | -53.6774 | 69.4839 | -53.0365 | -53.6819 | -53.4119 | -0.21057 | -0.036621 | -0.11902 | 0.71869 | 54.1214 | -0.15106 | 54.332 | 0.059509 | -0.050354 | -0.027465 | 0.009156 | 0.59052 | 0.21515 | -0.054932 | 0.2655 | -0.004578 | 0.92926 | 123.1934 | 0.64087 | 123.1613 | 123.2758 | 123.1247 | 123.0652 | 123.0743 | -123.3124 | -123.1522 | 122.9828 | 123.111 | 53.714 | 53.4714
874.8906 | 123.2941 | -53.5995 | 69.4061 | -0.071716 | 0.00086086 | 0.063717 | 0.06715 | 8.1126e-05 | -0.0023071 | -0.0034116 | 0.0098572 | 0.002698 | 0.067257 | 0.06902 | -0.0092414 | 0.0046164 | 0.00049774 | 0.09613 | 69.4519 | -53.8239 | 69.3787 | -52.8534 | -53.7552 | 0.53101 | -0.10529 | 69.4061 | -53.7094 | 69.5114 | -52.9724 | -53.6179 | -53.3661 | -0.22431 | 0.045776 | -0.027466 | 0.74615 | 54.1306 | -0.15564 | 54.3549 | 0.068665 | -0.10986 | 0 | 0.10529 | 0.62714 | 0.23346 | -0.018311 | 0.34332 | 0.091553 | 0.97046 | 123.2025 | 0.737 | 123.2208 | 123.2758 | 123.1155 | 123.0515 | 123.0057 | -123.23 | -123.1155 | 122.9782 | 123.111 | 53.6957 | 53.4943
875.8594 | 123.2574 | -53.6041 | 69.4199 | -0.079346 | 0.0017155 | 0.063931 | 0.06715 | -0.00055967 | -0.0016663 | -0.001489 | -0.0084534 | 0.0029116 | 0.067257 | 0.068592 | -0.0083868 | 0.003762 | -0.00035666 | 0.09613 | 69.4473 | -53.8055 | 69.3741 | -52.9083 | -53.7918 | 0.5127 | -0.13275 | 69.4153 | -53.714 | 69.4839 | -53.0228 | -53.6682 | -53.389 | -0.20142 | 0.027466 | -0.045777 | 0.6958 | 54.1168 | -0.18768 | 54.3182 | 0.013733 | -0.10986 | -0.004578 | 0.064087 | 0.58136 | 0.21515 | -0.064087 | 0.32501 | 0.045776 | 0.89722 | 123.1796 | 0.69122 | 123.1979 | 123.2529 | 123.1293 | 123.0515 | 123.0194 | -123.2254 | -123.1338 | 122.9782 | 123.0881 | 53.7003 | 53.4714
876.8906 | 123.2208 | -53.6407 | 69.4427 | -0.041199 | 0.0015019 | 0.062649 | 0.067364 | 0.0024311 | -0.00038447 | -0.0034116 | -0.026764 | 0.0029116 | 0.068112 | 0.066029 | -0.0056098 | 0.0052572 | -0.0012113 | 0.073242 | 69.4748 | -53.8422 | 69.3375 | -52.9449 | -53.8055 | 0.48523 | -0.16479 | 69.4611 | -53.6499 | 69.4519 | -53.1189 | -53.6865 | -53.4393 | -0.20142 | 0.032043 | -0.10529 | 0.6958 | 54.126 | -0.1648 | 54.3274 | 0.036621 | -0.009155 | 0.018311 | 0.009155 | 0.52185 | 0.20142 | -0.045776 | 0.21057 | -0.036621 | 0.89722 | 123.1796 | 0.53101 | 123.1018 | 123.317 | 123.111 | 123.1155 | 123.1018 | -123.2849 | -123.0927 | 122.9782 | 123.0927 | 53.714 | 53.476
877.8594 | 123.1888 | -53.6316 | 69.4336 | -0.033569 | 0.0038517 | 0.061795 | 0.068432 | -0.0035505 | 0.00046993 | -0.005975 | -0.048126 | 0.0035526 | 0.071102 | 0.063679 | -0.0068914 | 0.0063254 | -0.0035611 | 0.064087 | 69.4565 | -53.8376 | 69.3375 | -53.1509 | -53.9841 | 0.53558 | -0.20599 | 69.4473 | -53.7003 | 69.4061 | -53.0777 | -53.7277 | -53.476 | -0.20599 | 0.022888 | -0.096131 | 0.48065 | 54.1672 | -0.35248 | 54.3732 | -0.14649 | -0.068664 | 0.013733 | -0.027466 | 0.55389 | 0.15564 | -0.09613 | 0.2243 | -0.027466 | 0.68664 | 123.175 | 0.62256 | 123.1064 | 123.2941 | 123.1476 | 123.0881 | 123.0789 | -123.2712 | -123.1338 | 122.9691 | 123.0377 | 53.6957 | 53.4256
878.8906 | 123.2941 | -53.6133 | 69.4153 | -0.048828 | -0.00084814 | 0.062863 | 0.067364 | 0.0011493 | 0.0015381 | -0.0034116 | 0.00070198 | 0.0031254 | 0.068539 | 0.065815 | -0.0075324 | 0.0054708 | 0.00071134 | 0.045776 | 69.4611 | -53.8193 | 69.3283 | -52.9541 | -53.8284 | 0.49896 | -0.17853 | 69.4244 | -53.7094 | 69.5114 | -53.0319 | -53.6591 | -53.3844 | -0.20599 | 0.045777 | -0.086975 | 0.65918 | 54.1122 | -0.21515 | 54.3182 | -0.009155 | -0.096131 | 0.009155 | 0.096131 | 0.58136 | 0.22888 | -0.045777 | 0.32501 | 0.050354 | 0.86517 | 123.1476 | 0.67749 | 123.2208 | 123.2803 | 123.1338 | 123.0743 | 123.0377 | -123.2346 | -123.1247 | 122.9416 | 123.1247 | 53.6591 | 53.4348
879.8594 | 123.317 | -53.6179 | 69.4061 | -0.056457 | 0.0017155 | 0.062222 | 0.068218 | -0.0024823 | 0.00046993 | -0.0038388 | -0.023712 | 0.002698 | 0.068112 | 0.060688 | -0.0075324 | 0.0073936 | 0.00049774 | 0.073242 | 69.4473 | -53.8239 | 69.3787 | -52.89 | -53.7781 | 0.50812 | -0.13275 | 69.397 | -53.7048 | 69.516 | -52.9999 | -53.6362 | -53.3844 | -0.20599 | 0.041199 | -0.027466 | 0.72784 | 54.126 | -0.16022 | 54.332 | 0.045777 | -0.086975 | -0.009155 | 0.10986 | 0.61798 | 0.23346 | -0.01831 | 0.32043 | 0.068665 | 0.93384 | 123.2025 | 0.70496 | 123.2208 | 123.2712 | 123.1018 | 123.0652 | 123.0148 | -123.23 | -123.111 | 122.9965 | 123.1338 | 53.6911 | 53.4851
880.9062 | 123.317 | -53.6087 | 69.4565 | 0.019837 | 0.00043366 | 0.063717 | 0.071636 | 0.0011493 | -0.0031617 | -0.00020717 | -0.075592 | 0.004407 | 0.071102 | 0.069447 | -0.0086004 | 0.0054708 | -0.0024931 | 0.013733 | 69.4885 | -53.8879 | 69.2688 | -53.0228 | -53.8788 | 0.41657 | -0.29755 | 69.4794 | -53.746 | 69.5343 | -53.2608 | -53.5355 | -53.2562 | -0.27923 | 0.032043 | -0.18768 | 0.58594 | 54.0253 | -0.27008 | 54.3045 | 0.009155 | -0.13733 | 0.022888 | 0.07782 | 0.3479 | 0.35248 | 0.073243 | 0.48981 | 0.21057 | 0.86517 | 123.1567 | 0.48523 | 123.2803 | 123.3765 | 123.2254 | 123.0972 | 123.0881 | -123.3444 | -123.2025 | 122.8775 | 123.143 | 53.6224 | 53.3112
881.8594 | 123.2986 | -53.6179 | 69.4061 | -0.079346 | 0.0032107 | 0.061795 | 0.06715 | 0.00093573 | -0.0016663 | -0.003198 | 0.0037536 | 0.0031254 | 0.067898 | 0.066242 | -0.008814 | 0.0071798 | 0.00028414 | 0.068665 | 69.4519 | -53.8376 | 69.3741 | -52.8854 | -53.7598 | 0.51727 | -0.13733 | 69.3924 | -53.6911 | 69.5068 | -52.9816 | -53.6407 | -53.3707 | -0.21973 | 0.045776 | -0.032044 | 0.73242 | 54.1351 | -0.14191 | 54.3549 | 0.077819 | -0.073242 | -0.013733 | 0.10071 | 0.63629 | 0.24719 | -0.022888 | 0.32043 | 0.050354 | 0.95215 | 123.2117 | 0.70953 | 123.1979 | 123.2895 | 123.0835 | 123.0698 | 123.0103 | -123.2437 | -123.0972 | 122.9919 | 123.1247 | 53.6865 | 53.4805
882.9062 | 123.2162 | -53.6453 | 69.4107 | -0.086975 | 0.0021427 | 0.063076 | 0.068218 | 0.0022173 | -0.0023071 | -0.0017026 | -0.10916 | 0.0037662 | 0.070248 | 0.070728 | -0.0079596 | 0.006539 | -0.00014306 | 0.013733 | 69.4565 | -53.8788 | 69.2917 | -52.9816 | -53.8788 | 0.41199 | -0.24719 | 69.4382 | -53.7277 | 69.429 | -53.1097 | -53.7643 | -53.476 | -0.23346 | 0.045776 | -0.11902 | 0.66376 | 54.0573 | -0.23346 | 54.2908 | 0 | -0.082397 | 0.027465 | 0.01831 | 0.53558 | 0.16937 | -0.11902 | 0.25177 | -0.036621 | 0.89722 | 123.1705 | 0.61798 | 123.1567 | 123.3353 | 123.1659 | 123.1018 | 123.0835 | -123.2895 | -123.1384 | 122.937 | 123.0743 | 53.6591 | 53.3981
883.8594 | 123.2162 | -53.6819 | 69.4427 | -0.01831 | 0.00086086 | 0.061581 | 0.069714 | 0.0026447 | -0.0031617 | -0.001489 | -0.07254 | 0.0046206 | 0.069821 | 0.070088 | -0.0066778 | 0.0078208 | -0.0012113 | -0.018311 | 69.4702 | -53.8559 | 69.2413 | -53.0457 | -53.8834 | 0.41199 | -0.32501 | 69.4519 | -53.7231 | 69.4199 | -53.096 | -53.7552 | -53.4576 | -0.17395 | 0.027466 | -0.20142 | 0.63629 | 54.0939 | -0.20142 | 54.2679 | -0.027466 | -0.041199 | 0.009155 | -0.022888 | 0.58594 | 0.2243 | -0.073242 | 0.2655 | -0.032043 | 0.81024 | 123.0972 | 0.62714 | 123.143 | 123.3261 | 123.175 | 123.1522 | 123.1338 | -123.2986 | -123.1659 | 122.9233 | 123.1018 | 53.6636 | 53.3569
884.8906 | 123.1979 | -53.6636 | 69.397 | -0.079346 | 0.0034245 | 0.062863 | 0.070141 | -0.00034607 | 4.273e-05 | 0.00064723 | -0.07254 | 0.0037662 | 0.071743 | 0.06667 | -0.0062506 | 0.0080344 | 0.0017795 | -0.018311 | 69.4611 | -53.8879 | 69.2688 | -53.009 | -53.8834 | 0.40283 | -0.28839 | 69.4336 | -53.7323 | 69.429 | -53.1326 | -53.7964 | -53.4668 | -0.2243 | 0.064087 | -0.12817 | 0.6546 | 54.0665 | -0.21973 | 54.2908 | 0.004577 | -0.068665 | 0.036621 | 0.032043 | 0.53101 | 0.19684 | -0.13275 | 0.2655 | -0.064087 | 0.87891 | 123.1567 | 0.59967 | 123.1613 | 123.349 | 123.1659 | 123.1247 | 123.0972 | -123.2849 | -123.1293 | 122.9324 | 123.0927 | 53.6453 | 53.3752
885.8594 | 123.2758 | -53.6453 | 69.4016 | -0.048828 | 0.00086086 | 0.063717 | 0.068432 | -0.0033369 | -0.00059807 | -0.001489 | 0.025116 | 0.0022708 | 0.066189 | 0.068379 | -0.0081732 | 0.0046164 | 0.0015659 | 0.032043 | 69.4656 | -53.8422 | 69.3558 | -52.9175 | -53.7827 | 0.50812 | -0.19684 | 69.4107 | -53.7277 | 69.4931 | -53.0136 | -53.6453 | -53.3936 | -0.19684 | 0.064087 | -0.045776 | 0.72785 | 54.1534 | -0.13733 | 54.3503 | 0.059509 | -0.082397 | 0.009156 | 0.091553 | 0.63171 | 0.25177 | 0 | 0.33417 | 0.082397 | 0.92468 | 123.1979 | 0.71411 | 123.2208 | 123.3078 | 123.1384 | 123.111 | 123.056 | -123.2437 | -123.1293 | 123.0011 | 123.1384 | 53.6774 | 53.4485
886.8906 | 123.3032 | -53.6316 | 69.4016 | -0.10986 | 0.00064726 | 0.061581 | 0.067577 | 0.0015765 | -0.0012391 | -0.0010618 | 0.0037536 | 0.00098899 | 0.070034 | 0.061115 | -0.0079596 | 0.0039756 | -0.00057046 | 0.032043 | 69.3924 | -53.8559 | 69.3558 | -52.9037 | -53.7781 | 0.51727 | -0.1831 | 69.397 | -53.7094 | 69.4885 | -53.0045 | -53.6407 | -53.3615 | -0.2243 | -0.009155 | -0.045776 | 0.72784 | 54.1489 | -0.14648 | 54.3732 | 0.07782 | -0.07782 | -0.004577 | 0.086975 | 0.62714 | 0.27008 | -0.009155 | 0.3479 | 0.068665 | 0.95215 | 123.2117 | 0.70496 | 123.1979 | 123.2483 | 123.1064 | 123.024 | 123.0286 | -123.2574 | -123.111 | 122.9874 | 123.1201 | 53.6636 | 53.4485
887.8594 | 123.3444 | -53.6362 | 69.3741 | -0.10223 | -0.0036251 | 0.064358 | 0.067577 | 0.0030719 | -0.00038447 | -0.004907 | -0.0054016 | 0.002698 | 0.070889 | 0.062397 | -0.0064642 | 0.0061118 | 0.0024203 | 0.31586 | 69.4748 | -53.8239 | 69.3878 | -52.9587 | -53.8193 | 0.53101 | -0.17853 | 69.3649 | -53.7094 | 69.5114 | -53.0045 | -53.6087 | -53.3752 | -0.18768 | 0.10071 | 0.013733 | 0.67749 | 54.1672 | -0.18311 | 54.3549 | 0.004578 | -0.073243 | -0.009155 | 0.13733 | 0.63171 | 0.26093 | 0.027465 | 0.33417 | 0.10071 | 0.86517 | 123.2117 | 0.70496 | 123.2208 | 123.2986 | 123.0743 | 123.111 | 123.0011 | -123.1979 | -123.0835 | 123.024 | 123.1476 | 53.952 | 53.4576
888.8906 | 123.2162 | -53.6636 | 69.4199 | -0.056457 | 0.0015019 | 0.062222 | 0.0695 | -0.00034607 | -0.0025207 | 6.432e-06 | -0.066437 | 0.004407 | 0.069821 | 0.066242 | -0.0086004 | 0.0044028 | 0.0017795 | -0.050354 | 69.4519 | -53.8925 | 69.2276 | -53.0685 | -53.92 | 0.39825 | -0.36163 | 69.4565 | -53.7643 | 69.4199 | -53.1372 | -53.7781 | -53.4805 | -0.22888 | 0.032043 | -0.19226 | 0.59509 | 54.0619 | -0.25635 | 54.2908 | -0.027466 | -0.10071 | 0.036621 | 0 | 0.52643 | 0.1831 | -0.11444 | 0.28381 | -0.013733 | 0.82397 | 123.1201 | 0.62714 | 123.1842 | 123.3444 | 123.2208 | 123.1155 | 123.1201 | -123.3124 | -123.1842 | 122.8912 | 123.0835 | 53.6133 | 53.302
889.8594 | 123.2712 | -53.6636 | 69.3832 | -0.071716 | 6.46e-06 | 0.063717 | 0.068432 | -0.00055967 | -0.0025207 | -0.00042077 | 0.012909 | 0.0039798 | 0.064266 | 0.059834 | -0.0081732 | 0.0061118 | 0.0019931 | 0.009155 | 69.4061 | -53.8559 | 69.3329 | -52.9404 | -53.8193 | 0.48981 | -0.25177 | 69.4016 | -53.7277 | 69.4656 | -53.0777 | -53.7003 | -53.4485 | -0.19226 | 0.022888 | -0.050354 | 0.72327 | 54.1534 | -0.15564 | 54.3457 | 0.036621 | -0.064087 | 0.01831 | 0.082397 | 0.58594 | 0.21515 | -0.036621 | 0.27924 | 0.027466 | 0.91553 | 123.1888 | 0.65002 | 123.1934 | 123.262 | 123.1293 | 123.0698 | 123.0652 | -123.2391 | -123.111 | 122.9965 | 123.1293 | 53.6728 | 53.4119
890.9062 | 123.2529 | -53.6682 | 69.397 | -0.079346 | 0.0047061 | 0.063931 | 0.068005 | 0.0022173 | -0.0035889 | -0.00084817 | -0.084747 | 0.0041934 | 0.067898 | 0.067738 | -0.0066778 | 0.0052572 | 0.0013521 | -0.018311 | 69.4199 | -53.8971 | 69.2596 | -53.0182 | -53.8925 | 0.41199 | -0.31128 | 69.4016 | -53.7552 | 69.4153 | -53.1189 | -53.7872 | -53.4714 | -0.22888 | 0.022888 | -0.13733 | 0.65002 | 54.0802 | -0.2243 | 54.3091 | 0.004578 | -0.086975 | 0.004577 | 0.01831 | 0.54932 | 0.19684 | -0.11902 | 0.28381 | -0.032043 | 0.87891 | 123.1567 | 0.63629 | 123.1705 | 123.317 | 123.1567 | 123.0881 | 123.0698 | -123.2941 | -123.1522 | 122.9279 | 123.0835 | 53.6499 | 53.3569
891.8594 | 123.2849 | -53.6636 | 69.3878 | -0.071716 | 0.0019291 | 0.062436 | 0.067791 | -0.0018415 | -0.0010255 | -0.0019162 | -0.0084534 | 0.0041934 | 0.067044 | 0.066029 | -0.0073188 | 0.0061118 | 0.0013521 | -0.004578 | 69.429 | -53.8788 | 69.3192 | -52.9312 | -53.801 | 0.49439 | -0.24719 | 69.3558 | -53.7369 | 69.4519 | -53.0457 | -53.6728 | -53.4164 | -0.21515 | 0.041199 | -0.068664 | 0.73242 | 54.158 | -0.13733 | 54.3732 | 0.07782 | -0.073242 | -0.032043 | 0.064087 | 0.61798 | 0.24719 | -0.009156 | 0.32043 | 0.064086 | 0.94757 | 123.1979 | 0.69122 | 123.1888 | 123.3078 | 123.0927 | 123.0927 | 123.0194 | -123.2666 | -123.1247 | 122.9828 | 123.1155 | 53.6591 | 53.4164
892.8906 | 123.1888 | -53.6774 | 69.4061 | -0.27771 | 0.0036381 | 0.061367 | 0.068218 | 0.0028583 | -0.00081187 | -0.0010618 | -0.035919 | 0.0039798 | 0.070889 | 0.066883 | -0.0047552 | 0.0056846 | 0.0028475 | -0.054932 | 69.4656 | -53.8742 | 69.223 | -53.0502 | -53.9246 | 0.40283 | -0.41199 | 69.397 | -53.7643 | 69.3512 | -53.1555 | -53.8055 | -53.5309 | -0.19684 | 0.059509 | -0.18311 | 0.62714 | 54.0802 | -0.24719 | 54.277 | -0.050354 | -0.086975 | -0.009155 | -0.054932 | 0.52185 | 0.14648 | -0.12817 | 0.23346 | -0.041199 | 0.82397 | 123.0972 | 0.60882 | 123.1155 | 123.3398 | 123.1613 | 123.143 | 123.0743 | -123.2803 | -123.1705 | 122.9004 | 123.0286 | 53.6224 | 53.2654
893.8594 | 123.3124 | -53.6316 | 69.4382 | -0.056457 | 0.0025699 | 0.061795 | 0.068859 | -0.00055967 | -0.0010255 | -0.0021298 | -0.02066 | 0.0037662 | 0.068966 | 0.064106 | -0.008814 | 0.0071798 | 0.0034885 | -0.032043 | 69.4061 | -53.8651 | 69.2963 | -52.9861 | -53.8559 | 0.46692 | -0.32044 | 69.3741 | -53.7918 | 69.3924 | -53.1235 | -53.7415 | -53.5126 | -0.23346 | -0.032043 | -0.14191 | 0.64545 | 54.0985 | -0.2243 | 54.332 | 0.009155 | -0.16022 | -0.064087 | -0.045776 | 0.50812 | 0.11902 | -0.10986 | 0.27924 | 0.050354 | 0.87891 | 123.1613 | 0.66833 | 123.1842 | 123.2712 | 123.1659 | 123.0377 | 123.0057 | -123.3032 | -123.23 | 122.9279 | 123.024 | 53.5995 | 53.3112
894.8906 | 123.2803 | -53.6911 | 69.3741 | -0.01831 | 0.0012881 | 0.065213 | 0.069714 | 0.00072213 | -0.00081187 | -0.0017026 | 0.022064 | 0.0020572 | 0.068539 | 0.066242 | -0.0056098 | 0.0078208 | -0.00035666 | -0.041199 | 69.3832 | -53.8925 | 69.3192 | -52.9633 | -53.8376 | 0.48523 | -0.29755 | 69.3558 | -53.7643 | 69.4427 | -53.1006 | -53.714 | -53.4439 | -0.20142 | 0.009156 | -0.054931 | 0.72784 | 54.1763 | -0.14648 | 54.3777 | 0.054932 | -0.073242 | -0.01831 | 0.068665 | 0.59052 | 0.24719 | -0.022888 | 0.32043 | 0.050354 | 0.92926 | 123.2117 | 0.66376 | 123.2071 | 123.2758 | 123.1201 | 123.0743 | 123.0469 | -123.2666 | -123.1384 | 123.0103 | 123.1339 | 53.6499 | 53.3936
895.8594 | 123.3124 | -53.6774 | 69.3375 | -0.10986 | 0.0023563 | 0.064785 | 0.068432 | 0.00072213 | -0.00017087 | -0.0040524 | -0.0054016 | 0.0024844 | 0.06918 | 0.060688 | -0.0083868 | 0.0056846 | -0.00014306 | -0.036621 | 69.342 | -53.9154 | 69.3375 | -52.9633 | -53.8467 | 0.50354 | -0.28381 | 69.3375 | -53.7643 | 69.4519 | -53.0685 | -53.6911 | -53.4531 | -0.23804 | 0.004578 | 0 | 0.71411 | 54.1809 | -0.16937 | 54.4189 | 0.068664 | -0.086975 | 0 | 0.11444 | 0.60883 | 0.2243 | -0.013733 | 0.31128 | 0.073242 | 0.95215 | 123.2529 | 0.6958 | 123.2162 | 123.2574 | 123.1018 | 123.0194 | 123.0148 | -123.2529 | -123.1018 | 123.0148 | 123.1293 | 53.6407 | 53.3936
896.9062 | 123.2162 | -53.7369 | 69.3466 | -0.071716 | 0.0027835 | 0.062436 | 0.068859 | 0.0013629 | -0.0029481 | 0.00022003 | -0.10611 | 0.0052616 | 0.069821 | 0.066883 | -0.009455 | 0.0084616 | -0.0018521 | -0.10529 | 69.3512 | -53.9749 | 69.1956 | -53.1052 | -53.9749 | 0.37079 | -0.43488 | 69.3604 | -53.801 | 69.342 | -53.2196 | -53.8651 | -53.5583 | -0.23804 | 0.004577 | -0.15106 | 0.63171 | 54.1077 | -0.23804 | 54.3457 | 0 | -0.064087 | 0.013733 | -0.004578 | 0.51727 | 0.17853 | -0.12817 | 0.24261 | -0.064087 | 0.86975 | 123.1705 | 0.58136 | 123.143 | 123.3261 | 123.1613 | 123.0881 | 123.0972 | -123.3215 | -123.1476 | 122.9324 | 123.0789 | 53.6316 | 53.302
897.8594 | 123.2803 | -53.6728 | 69.3375 | -0.056457 | 0.0015019 | 0.063076 | 0.068432 | 0.0060627 | -0.00059807 | -0.0027708 | -0.0023498 | 0.00163 | 0.068753 | 0.06432 | -0.007105 | 0.0076072 | 0.0011385 | -0.082397 | 69.3741 | -53.9062 | 69.278 | -52.9816 | -53.8651 | 0.48065 | -0.31586 | 69.342 | -53.7689 | 69.429 | -53.1097 | -53.7231 | -53.476 | -0.23346 | 0.036621 | -0.059509 | 0.69122 | 54.1534 | -0.19226 | 54.3869 | 0.041199 | -0.09613 | 0.004578 | 0.091553 | 0.56305 | 0.19684 | -0.050354 | 0.29297 | 0.045776 | 0.92468 | 123.1842 | 0.65918 | 123.1979 | 123.2803 | 123.111 | 123.0469 | 123.0148 | -123.2437 | -123.1064 | 122.9507 | 123.1018 | 53.5904 | 53.3569
898.8906 | 123.1888 | -53.746 | 69.3512 | -0.033569 | 0.0019291 | 0.061795 | 0.069073 | -0.0046185 | -0.0027345 | -0.00020717 | -0.035919 | 0.0039798 | 0.068539 | 0.067738 | -0.0066778 | 0.003762 | 0.0017795 | -0.16022 | 69.4016 | -53.9383 | 69.1635 | -53.1509 | -53.9932 | 0.36621 | -0.5127 | 69.3878 | -53.8239 | 69.3146 | -53.2288 | -53.8605 | -53.5675 | -0.19226 | 0.050354 | -0.18768 | 0.59509 | 54.1122 | -0.24719 | 54.3045 | -0.054932 | -0.07782 | 0.036621 | -0.036621 | 0.51727 | 0.17853 | -0.11444 | 0.25635 | -0.036621 | 0.78735 | 123.1018 | 0.59509 | 123.1384 | 123.3398 | 123.2117 | 123.1476 | 123.1338 | -123.2895 | -123.175 | 122.9095 | 123.0606 | 53.5858 | 53.2333
899.8594 | 123.2941 | -53.7231 | 69.3054 | -0.048828 | 0.0012881 | 0.062222 | 0.067791 | 0.0026447 | 0.00025633 | -0.0029844 | 0.0068054 | 0.00098899 | 0.068325 | 0.068379 | -0.0068914 | 0.0054708 | 0.0011385 | -0.086975 | 69.3146 | -53.92 | 69.2825 | -52.9999 | -53.8651 | 0.4715 | -0.33417 | 69.31 | -53.8101 | 69.397 | -53.1097 | -53.7323 | -53.4851 | -0.19684 | 0.009155 | -0.022888 | 0.72327 | 54.1946 | -0.14191 | 54.3915 | 0.054932 | -0.086975 | 0.004578 | 0.091553 | 0.6134 | 0.23804 | -0.009155 | 0.32501 | 0.07782 | 0.9201 | 123.2025 | 0.70038 | 123.2071 | 123.2346 | 123.1201 | 123.0377 | 123.0331 | -123.2254 | -123.1155 | 123.0057 | 123.1201 | 53.6362 | 53.389
900.8906 | 123.2117 | -53.746 | 69.3512 | -0.079346 | 0.0021427 | 0.063717 | 0.068432 | 0.0039263 | -0.0059387 | -0.0017026 | -0.014557 | 0.0018436 | 0.067898 | 0.065602 | -0.0079596 | 0.0067526 | -0.00078406 | -0.1236 | 69.3375 | -53.952 | 69.2047 | -53.0731 | -53.9474 | 0.41657 | -0.30212 | 69.397 | -53.7781 | 69.3054 | -53.2013 | -53.8696 | -53.6133 | -0.20599 | -0.013733 | -0.14648 | 0.67291 | 54.1626 | -0.20142 | 54.3686 | 0.004577 | -0.032043 | 0.045777 | -0.045776 | 0.54474 | 0.13275 | -0.1236 | 0.16479 | -0.091553 | 0.87891 | 123.1567 | 0.57678 | 123.0835 | 123.2895 | 123.175 | 123.0835 | 123.143 | -123.3032 | -123.1293 | 122.9507 | 123.0515 | 53.6224 | 53.4439
901.8594 | 123.3353 | -53.7277 | 69.2963 | -0.048828 | 0.0015019 | 0.06094 | 0.068646 | -0.00034607 | -0.0010255 | -0.0019162 | 0.0037536 | 0.0022708 | 0.069821 | 0.059834 | -0.0081732 | 0.0046164 | -0.0044157 | -0.11902 | 69.3146 | -53.9703 | 69.2551 | -52.9861 | -53.8651 | 0.46692 | -0.37079 | 69.3054 | -53.8147 | 69.4016 | -53.1326 | -53.7552 | -53.4988 | -0.24262 | 0.01831 | -0.041199 | 0.74158 | 54.1946 | -0.13733 | 54.4373 | 0.10529 | -0.086975 | 0.009155 | 0.10528 | 0.59509 | 0.22888 | -0.027466 | 0.31586 | 0.059509 | 0.98419 | 123.2254 | 0.68207 | 123.2162 | 123.2849 | 123.1201 | 123.0423 | 123.0331 | -123.2666 | -123.111 | 122.9828 | 123.1293 | 53.6087 | 53.3569
902.9062 | 123.2346 | -53.7827 | 69.2688 | -0.10986 | 0.0032107 | 0.062863 | 0.070141 | 0.0026447 | 0.00068353 | -0.004266 | -0.10001 | 0.0014164 | 0.068753 | 0.063893 | -0.0066778 | 0.006539 | 0.00028414 | -0.23804 | 69.3054 | -54.0436 | 69.0994 | -53.2288 | -54.1031 | 0.31128 | -0.5722 | 69.278 | -53.8742 | 69.2825 | -53.2791 | -53.9154 | -53.6179 | -0.26093 | 0.036621 | -0.16937 | 0.55389 | 54.0939 | -0.32043 | 54.3549 | -0.059509 | -0.091553 | 0.009155 | 0.013733 | 0.50354 | 0.16479 | -0.13275 | 0.25635 | -0.041198 | 0.81482 | 123.143 | 0.59509 | 123.1567 | 123.349 | 123.1522 | 123.0881 | 123.0606 | -123.3124 | -123.143 | 122.8821 | 123.0652 | 53.5446 | 53.2104
903.8594 | 123.3078 | -53.7689 | 69.2825 | -0.094604 | 0.0038517 | 0.062008 | 0.068005 | -0.0020551 | -0.0023071 | -0.0012754 | 0.0068054 | 0.0020572 | 0.06683 | 0.064747 | -0.007105 | 0.0069662 | -0.0014249 | -0.12817 | 69.2917 | -53.9749 | 69.223 | -53.0594 | -53.9108 | 0.44861 | -0.42114 | 69.2642 | -53.8193 | 69.3558 | -53.1647 | -53.7689 | -53.5309 | -0.20599 | 0.009155 | -0.05951 | 0.70953 | 54.2175 | -0.14191 | 54.4235 | 0.064087 | -0.050354 | -0.018311 | 0.073242 | 0.60425 | 0.23804 | 0 | 0.28839 | 0.050354 | 0.91553 | 123.1979 | 0.6546 | 123.175 | 123.2666 | 123.0835 | 123.0606 | 123.0331 | -123.2574 | -123.1018 | 122.9919 | 123.1247 | 53.6407 | 53.3478
904.8906 | 123.2208 | -53.8101 | 69.2459 | -0.056457 | 0.0012881 | 0.064999 | 0.070782 | 0.0047809 | -0.0027345 | -0.0023434 | -0.087799 | 0.0039798 | 0.067257 | 0.074787 | -0.0066778 | 0.0076072 | -0.0022793 | -0.16937 | 69.2917 | -54.0482 | 69.1452 | -53.1555 | -54.0115 | 0.36621 | -0.52643 | 69.2596 | -53.8696 | 69.2825 | -53.2791 | -53.8925 | -53.6087 | -0.23804 | 0.045776 | -0.10071 | 0.6546 | 54.1763 | -0.20142 | 54.4144 | 0.036621 | -0.059509 | 0.013733 | 0.036621 | 0.53101 | 0.20142 | -0.082397 | 0.26093 | -0.022888 | 0.89264 | 123.1934 | 0.59052 | 123.1522 | 123.3398 | 123.1293 | 123.1018 | 123.0698 | -123.2941 | -123.1155 | 122.9553 | 123.0927 | 53.6407 | 53.2837
905.8594 | 123.2941 | -53.7918 | 69.2368 | -0.041199 | 0.0036381 | 0.063717 | 0.068859 | -0.0031231 | -0.0023071 | -0.004266 | 0.022064 | 0.003339 | 0.067257 | 0.066029 | -0.0066778 | 0.0063254 | 0.00049774 | -0.16022 | 69.2871 | -54.0161 | 69.1818 | -53.0594 | -53.9246 | 0.45776 | -0.44861 | 69.2368 | -53.8696 | 69.3466 | -53.1967 | -53.801 | -53.5355 | -0.2243 | 0.050354 | -0.054931 | 0.73242 | 54.2496 | -0.13275 | 54.4739 | 0.091552 | -0.07782 | 0 | 0.10986 | 0.59509 | 0.25635 | -0.009155 | 0.33417 | 0.068665 | 0.95673 | 123.1979 | 0.67291 | 123.2162 | 123.3032 | 123.1064 | 123.0789 | 123.0286 | -123.2529 | -123.1064 | 122.9736 | 123.1384 | 53.6316 | 53.3432
906.8906 | 123.2849 | -53.7918 | 69.2276 | -0.01831 | 0.0042789 | 0.063076 | 0.067577 | -0.00055967 | -0.0012391 | -0.00084817 | 0.00070198 | 0.002698 | 0.067898 | 0.067738 | -0.0075324 | 0.0056846 | -0.00078406 | -0.19226 | 69.2505 | -54.0207 | 69.1818 | -53.0823 | -53.9612 | 0.44861 | -0.50812 | 69.2322 | -53.8925 | 69.3192 | -53.215 | -53.8193 | -53.5675 | -0.22888 | 0.022888 | -0.045776 | 0.70953 | 54.2404 | -0.16937 | 54.4693 | 0.059509 | -0.10071 | 0.004578 | 0.091553 | 0.57678 | 0.2243 | -0.027466 | 0.32501 | 0.073242 | 0.93842 | 123.2025 | 0.67749 | 123.2117 | 123.2712 | 123.1247 | 123.0423 | 123.024 | -123.2483 | -123.1201 | 122.9736 | 123.111 | 53.5995 | 53.2837
907.8594 | 123.3032 | -53.8147 | 69.2184 | -0.041199 | 0.0029971 | 0.06094 | 0.066723 | -0.00098687 | -0.00038447 | -0.001489 | -0.0084534 | 0.002698 | 0.070034 | 0.068592 | -0.0081732 | 0.0041892 | -0.0027067 | -0.21973 | 69.2413 | -54.0436 | 69.1772 | -53.0731 | -53.952 | 0.45319 | -0.5127 | 69.2001 | -53.8879 | 69.3146 | -53.215 | -53.8239 | -53.5675 | -0.22888 | 0.022888 | -0.041199 | 0.74158 | 54.2679 | -0.13733 | 54.4968 | 0.091553 | -0.073242 | -0.018311 | 0.09613 | 0.59967 | 0.24719 | -0.009156 | 0.32043 | 0.064086 | 0.97046 | 123.2208 | 0.67291 | 123.2025 | 123.2849 | 123.0881 | 123.056 | 123.0148 | -123.262 | -123.1064 | 122.9919 | 123.1293 | 53.595 | 53.302
908.9062 | 123.23 | -53.8467 | 69.2368 | -0.071716 | -0.00020714 | 0.062436 | 0.070995 | 0.0011493 | -0.0016663 | -0.0036252 | -0.090851 | 0.0035526 | 0.067471 | 0.068806 | -0.0039008 | 0.0078208 | 0.00092494 | -0.28381 | 69.2596 | -54.0985 | 69.0674 | -53.2608 | -54.0894 | 0.31128 | -0.6958 | 69.2459 | -53.9474 | 69.2322 | -53.3203 | -53.8788 | -53.6179 | -0.25177 | 0.022889 | -0.16937 | 0.58594 | 54.158 | -0.24261 | 54.4098 | 0.009156 | -0.10071 | 0.009156 | -0.004577 | 0.52643 | 0.22888 | -0.032043 | 0.32959 | 0.068665 | 0.83771 | 123.1659 | 0.62714 | 123.1796 | 123.3582 | 123.1934 | 123.1064 | 123.0927 | -123.3353 | -123.1842 | 122.9141 | 123.0789 | 53.5629 | 53.1509
909.8594 | 123.3444 | -53.833 | 69.1681 | -0.056457 | 0.0015019 | 0.061154 | 0.069073 | 0.0013629 | -0.0020935 | -0.0010618 | 0.0037536 | 0.0029116 | 0.067044 | 0.064747 | -0.007105 | 0.0071798 | -0.0027067 | -0.30212 | 69.1956 | -54.0756 | 69.1269 | -53.1143 | -54.0024 | 0.43945 | -0.56763 | 69.1772 | -53.92 | 69.3008 | -53.2425 | -53.8376 | -53.595 | -0.24262 | 0.027466 | -0.041199 | 0.71869 | 54.2725 | -0.16937 | 54.5151 | 0.073243 | -0.086975 | 0.009155 | 0.13275 | 0.59051 | 0.23804 | -0.004577 | 0.32501 | 0.082398 | 0.9613 | 123.2025 | 0.67749 | 123.2208 | 123.2712 | 123.0972 | 123.0286 | 123.0103 | -123.2437 | -123.0881 | 122.9599 | 123.1338 | 53.5309 | 53.2654
910.9062 | 123.2254 | -53.8971 | 69.1681 | -0.071716 | 0.0012881 | 0.064572 | 0.069073 | 0.0030719 | -0.0012391 | -0.0036252 | -0.081696 | 0.0024844 | 0.067471 | 0.067524 | -0.0079596 | 0.0086752 | -0.0016385 | -0.28839 | 69.223 | -54.1351 | 69.0308 | -53.2791 | -54.1306 | 0.29297 | -0.76446 | 69.191 | -53.9566 | 69.1681 | -53.3981 | -54.0253 | -53.7323 | -0.23804 | 0.054931 | -0.13733 | 0.61798 | 54.1901 | -0.23346 | 54.4281 | 0.004578 | -0.059509 | 0.022888 | 0 | 0.49896 | 0.16479 | -0.12817 | 0.2243 | -0.068665 | 0.85602 | 123.1659 | 0.55847 | 123.1247 | 123.3582 | 123.1476 | 123.1201 | 123.0881 | -123.3032 | -123.1247 | 122.9279 | 123.0652 | 53.6087 | 53.1326
911.8594 | 123.3124 | -53.8834 | 69.1315 | -0.11749 | 0.0012881 | 0.065426 | 0.069073 | -0.0018415 | -0.0010255 | 6.432e-06 | 0.00070198 | 0.0020572 | 0.066403 | 0.063465 | -0.007105 | 0.0054708 | 0.0028475 | -0.27466 | 69.1635 | -54.0939 | 69.104 | -53.1738 | -54.0253 | 0.40283 | -0.68207 | 69.1498 | -53.9658 | 69.2459 | -53.2791 | -53.9062 | -53.6407 | -0.21057 | 0.032043 | -0.027466 | 0.70953 | 54.2862 | -0.14191 | 54.4968 | 0.068664 | -0.082397 | 0.01831 | 0.11444 | 0.60425 | 0.24262 | -0.022888 | 0.32501 | 0.059509 | 0.9201 | 123.1979 | 0.68664 | 123.2117 | 123.2574 | 123.1155 | 123.0469 | 123.0331 | -123.2254 | -123.0972 | 122.9874 | 123.1293 | 53.6087 | 53.2013
912.8906 | 123.2162 | -53.9383 | 69.1498 | -0.11749 | 0.0027835 | 0.062222 | 0.068859 | 0.0028583 | -0.0029481 | -0.0040524 | -0.075592 | 0.0039798 | 0.06683 | 0.064106 | -0.0086004 | 0.0063254 | 7.0538e-05 | -0.32501 | 69.1864 | -54.1763 | 69.017 | -53.302 | -54.1489 | 0.3067 | -0.82398 | 69.1544 | -54.0298 | 69.1589 | -53.421 | -54.0436 | -53.7506 | -0.23804 | 0.036621 | -0.13275 | 0.63629 | 54.245 | -0.21057 | 54.483 | 0.027466 | -0.091553 | 0.004578 | 0.009156 | 0.51727 | 0.18768 | -0.10529 | 0.27924 | -0.013733 | 0.87433 | 123.1934 | 0.60882 | 123.1888 | 123.3627 | 123.1842 | 123.1247 | 123.0927 | -123.3261 | -123.1796 | 122.9553 | 123.0972 | 53.6133 | 53.1143
913.8594 | 123.1842 | -53.952 | 69.1406 | -0.02594 | 0.0010745 | 0.06094 | 0.068432 | -0.0024823 | -0.00059807 | -0.002557 | -0.017609 | 0.0029116 | 0.068112 | 0.066456 | -0.0062506 | 0.006539 | 0.0032749 | -0.38452 | 69.191 | -54.1672 | 68.9438 | -53.3661 | -54.1763 | 0.28381 | -0.91553 | 69.1544 | -54.0298 | 69.0948 | -53.4622 | -54.0527 | -53.7781 | -0.21515 | 0.050354 | -0.19684 | 0.58594 | 54.2358 | -0.22431 | 54.451 | -0.009156 | -0.07782 | 0.013733 | -0.045776 | 0.48981 | 0.17395 | -0.10071 | 0.25177 | -0.022888 | 0.80109 | 123.111 | 0.56763 | 123.1247 | 123.3582 | 123.1842 | 123.143 | 123.1064 | -123.3078 | -123.1705 | 122.8958 | 123.0469 | 53.5675 | 53.0365
914.8906 | 123.2529 | -53.9658 | 69.0994 | -0.048828 | 0.0036381 | 0.061795 | 0.068646 | -0.00098687 | -0.00017087 | -0.0034116 | -0.0084534 | 0.0029116 | 0.065762 | 0.063252 | -0.0086004 | 0.0086752 | 0.0030611 | -0.32959 | 69.1132 | -54.1718 | 69.0353 | -53.2425 | -54.0985 | 0.35706 | -0.84686 | 69.0903 | -54.0344 | 69.1406 | -53.3752 | -53.9978 | -53.7277 | -0.20599 | 0.013733 | -0.064087 | 0.72327 | 54.3228 | -0.13275 | 54.5288 | 0.073242 | -0.068665 | -0.009155 | 0.041199 | 0.59051 | 0.23804 | -0.032044 | 0.3067 | 0.036621 | 0.92926 | 123.2071 | 0.65918 | 123.175 | 123.2849 | 123.1247 | 123.0789 | 123.056 | -123.2712 | -123.1338 | 123.0011 | 123.1064 | 53.6362 | 53.1189
915.8594 | 123.3261 | -53.9703 | 69.0674 | -0.048828 | 0.0023563 | 0.063076 | 0.067577 | -0.0016279 | -0.0029481 | -0.0038388 | 0.028168 | 0.0024844 | 0.068325 | 0.065174 | -0.0079596 | 0.0052572 | -0.00035666 | -0.33875 | 69.1223 | -54.1626 | 69.0216 | -53.2608 | -54.0848 | 0.35248 | -0.85602 | 69.0582 | -54.0573 | 69.1772 | -53.3661 | -53.9703 | -53.7277 | -0.19226 | 0.054931 | -0.045777 | 0.70953 | 54.3228 | -0.11444 | 54.5151 | 0.07782 | -0.086975 | -0.009155 | 0.10986 | 0.60425 | 0.24262 | 0 | 0.32959 | 0.086975 | 0.90179 | 123.1842 | 0.69122 | 123.2346 | 123.2849 | 123.1155 | 123.0927 | 123.0286 | -123.23 | -123.1247 | 122.9919 | 123.1476 | 53.6316 | 53.1143
916.9062 | 123.2208 | -54.0207 | 69.0582 | -0.041199 | 0.0027835 | 0.065213 | 0.068005 | 0.0017901 | 0.00046993 | -0.0021298 | -0.10306 | 0.002698 | 0.067684 | 0.065174 | -0.0075324 | 0.0076072 | -0.0018521 | -0.42114 | 69.0628 | -54.2542 | 68.9346 | -53.3844 | -54.2404 | 0.24261 | -0.99792 | 69.0674 | -54.0848 | 69.072 | -53.508 | -54.1351 | -53.8239 | -0.23346 | 0.004577 | -0.1236 | 0.63629 | 54.2633 | -0.21973 | 54.4968 | 0.013733 | -0.064087 | 0.009155 | 0.013732 | 0.5127 | 0.19684 | -0.11444 | 0.26093 | -0.050354 | 0.86975 | 123.1888 | 0.57678 | 123.1567 | 123.317 | 123.1522 | 123.0835 | 123.0881 | -123.3124 | -123.143 | 122.9553 | 123.0927 | 53.5995 | 53.0228
917.8594 | 123.2483 | -54.0207 | 69.0582 | -0.10986 | 0.0012881 | 0.064358 | 0.07185 | -0.00034607 | 0.0015381 | -0.0029844 | 0.015961 | 0.0035526 | 0.067471 | 0.068592 | -0.0073188 | 0.0063254 | -0.00099766 | -0.39825 | 69.0537 | -54.213 | 68.9667 | -53.3478 | -54.1855 | 0.31128 | -0.97961 | 69.0399 | -54.071 | 69.0811 | -53.4714 | -54.071 | -53.7918 | -0.19226 | -0.004578 | -0.091553 | 0.67291 | 54.332 | -0.16479 | 54.5242 | 0.027466 | -0.050354 | -0.018311 | 0.022888 | 0.54932 | 0.22888 | -0.050354 | 0.27924 | 0 | 0.86517 | 123.1796 | 0.59967 | 123.1522 | 123.2666 | 123.111 | 123.0743 | 123.0606 | -123.2712 | -123.1293 | 122.9874 | 123.1018 | 53.6224 | 53.0411
918.9062 | 122.9507 | -54.1031 | 68.9758 | -0.048828 | 0.0015019 | 0.064785 | 0.071209 | 0.00072213 | -0.00017087 | -0.0038388 | -0.10306 | 0.005048 | 0.068753 | 0.064747 | -0.0062506 | 0.0076072 | -0.00057046 | -0.48981 | 69.0445 | -54.3228 | 68.8477 | -53.4897 | -54.3457 | 0.16479 | -1.1307 | 69.0353 | -54.1489 | 68.9941 | -53.6041 | -54.2084 | -53.7872 | -0.21973 | 0.068665 | -0.12817 | 0.6134 | 54.2679 | -0.24262 | 54.4876 | -0.022888 | -0.045777 | 0.059509 | 0.018311 | 0.49896 | 0.31586 | -0.10529 | 0.36163 | -0.059509 | 0.83313 | 123.1705 | 0.54474 | 123.143 | 123.3673 | 123.1842 | 123.1476 | 123.1384 | -123.2986 | -123.1247 | 122.9507 | 123.0972 | 53.6133 | 52.9724
919.8594 | 123.2529 | -54.0436 | 69.017 | -0.01831 | 6.46e-06 | 0.063717 | 0.068005 | -0.0016279 | -0.00059807 | -0.0021298 | 0.028168 | 0.003339 | 0.069607 | 0.067738 | -0.0056098 | 0.0054708 | -0.00057046 | -0.43945 | 69.0445 | -54.2587 | 68.9209 | -53.3707 | -54.213 | 0.27924 | -1.0574 | 69.017 | -54.1214 | 69.0491 | -53.5126 | -54.1077 | -53.8376 | -0.21515 | 0.027466 | -0.096131 | 0.67291 | 54.3228 | -0.16937 | 54.538 | 0.045776 | -0.07782 | 0 | 0.032043 | 0.53101 | 0.20599 | -0.064087 | 0.28381 | 0.013733 | 0.88806 | 123.1796 | 0.60883 | 123.1705 | 123.3032 | 123.1384 | 123.0881 | 123.0606 | -123.2758 | -123.1384 | 122.9645 | 123.0927 | 53.6041 | 52.9861
920.9062 | 123.2346 | -54.1168 | 68.9575 | -0.064087 | 0.00064726 | 0.06329 | 0.069714 | 0.0013629 | -0.00081187 | -0.00020717 | -0.057281 | 0.0039798 | 0.067044 | 0.070515 | -0.0066778 | 0.0076072 | -0.0031339 | -0.49896 | 68.9804 | -54.3457 | 68.8385 | -53.4668 | -54.3274 | 0.17853 | -1.1398 | 68.9804 | -54.1763 | 68.9987 | -53.6041 | -54.1946 | -53.9154 | -0.22888 | 0.022888 | -0.11902 | 0.65002 | 54.2953 | -0.21057 | 54.5242 | 0.01831 | -0.05951 | 0.022888 | 0.041198 | 0.5127 | 0.20142 | -0.07782 | 0.26093 | -0.01831 | 0.87891 | 123.1842 | 0.5722 | 123.175 | 123.3261 | 123.1567 | 123.0972 | 123.0972 | -123.3032 | -123.1339 | 122.9553 | 123.1155 | 53.6179 | 52.977
921.8594 | 123.2758 | -54.1031 | 68.9575 | -0.056457 | 0.0038517 | 0.060299 | 0.068218 | -0.00034607 | -0.00059807 | -0.0010618 | 0.015961 | 0.0012028 | 0.070248 | 0.067097 | -0.0068914 | 0.0044028 | -0.0016385 | -0.48523 | 68.985 | -54.2999 | 68.8614 | -53.4302 | -54.2587 | 0.25177 | -1.1444 | 68.9621 | -54.1718 | 68.9941 | -53.5675 | -54.1443 | -53.8834 | -0.19684 | 0.027465 | -0.096131 | 0.67291 | 54.3549 | -0.15564 | 54.5517 | 0.041199 | -0.068665 | 0.004577 | 0.036621 | 0.53558 | 0.21973 | -0.041199 | 0.28839 | 0.027466 | 0.86975 | 123.1613 | 0.60425 | 123.1659 | 123.2849 | 123.1338 | 123.0881 | 123.0652 | -123.2574 | -123.1293 | 122.9645 | 123.0972 | 53.6179 | 52.9587
922.9062 | 123.2758 | -54.126 | 68.8934 | -0.041199 | 0.0015019 | 0.061367 | 0.068646 | 0.0037127 | -0.00081187 | -0.0038388 | 0.00070198 | 0.0012028 | 0.067257 | 0.058766 | -0.007746 | 0.0084616 | -0.0018521 | -0.59052 | 68.9346 | -54.3549 | 68.779 | -53.54 | -54.3777 | 0.16479 | -1.2726 | 68.8934 | -54.2084 | 68.9346 | -53.6499 | -54.2221 | -53.9291 | -0.22888 | 0.041198 | -0.11444 | 0.58594 | 54.2908 | -0.25177 | 54.5197 | -0.022889 | -0.082397 | 0 | 0.041198 | 0.47608 | 0.19684 | -0.09613 | 0.27924 | -0.013733 | 0.81482 | 123.1338 | 0.55847 | 123.143 | 123.2895 | 123.1018 | 123.0606 | 123.0194 | -123.2483 | -123.1018 | 122.905 | 123.0606 | 53.5355 | 52.8534
923.8594 | 123.1934 | -54.1809 | 68.898 | -0.048828 | 0.0015019 | 0.061581 | 0.069286 | -0.0014143 | -0.0029481 | -0.0023434 | -0.032867 | 0.0024844 | 0.067257 | 0.062397 | -0.0096686 | 0.006539 | 0.0030611 | -0.61798 | 68.9758 | -54.3961 | 68.7241 | -53.6041 | -54.4281 | 0.12817 | -1.355 | 68.9255 | -54.245 | 68.8751 | -53.7094 | -54.2862 | -54.0024 | -0.21515 | 0.07782 | -0.17395 | 0.57678 | 54.3091 | -0.24719 | 54.5242 | -0.032044 | -0.064087 | 0.027466 | -0.022888 | 0.4715 | 0.17853 | -0.10529 | 0.24262 | -0.041199 | 0.79193 | 123.1201 | 0.53558 | 123.1201 | 123.3719 | 123.1705 | 123.1567 | 123.1064 | -123.2941 | -123.143 | 122.905 | 123.056 | 53.5629 | 52.8259
924.9062 | 123.1842 | -54.2175 | 68.8797 | -0.048828 | 0.0027835 | 0.06329 | 0.070568 | -0.00098687 | -0.00059807 | -0.002557 | -0.090851 | 0.0029116 | 0.068753 | 0.065602 | -0.0079596 | 0.0073936 | 0.00092494 | -0.60883 | 68.9209 | -54.4556 | 68.6966 | -53.6362 | -54.4693 | 0.086975 | -1.3962 | 68.9117 | -54.2953 | 68.8477 | -53.7643 | -54.3549 | -54.0436 | -0.23804 | 0.041198 | -0.18311 | 0.58136 | 54.3045 | -0.25177 | 54.5425 | -0.013733 | -0.07782 | 0.032043 | -0.032044 | 0.45319 | 0.17395 | -0.13733 | 0.25177 | -0.059509 | 0.8194 | 123.1522 | 0.53101 | 123.143 | 123.3765 | 123.2071 | 123.1384 | 123.1293 | -123.3353 | -123.175 | 122.9141 | 123.0652 | 53.6087 | 52.8213
925.8594 | 123.1888 | -54.2496 | 68.866 | -0.02594 | 0.0027835 | 0.061154 | 0.065441 | -0.00055967 | 4.273e-05 | -0.0010618 | 0.0068054 | 0.0031254 | 0.06918 | 0.061756 | -0.0056098 | 0.0056846 | 0.00071134 | -0.59967 | 68.898 | -54.4144 | 68.5822 | -53.5904 | -54.4601 | 0.10529 | -1.3916 | 68.8751 | -54.3228 | 68.8431 | -53.7506 | -54.3365 | -54.0665 | -0.1648 | 0.032043 | -0.28381 | 0.65918 | 54.3549 | -0.21057 | 54.5197 | -0.045776 | -0.073242 | 0.009155 | -0.022888 | 0.49896 | 0.18311 | -0.086975 | 0.25635 | -0.013733 | 0.82398 | 122.9965 | 0.5722 | 123.1659 | 123.3124 | 123.1979 | 123.1476 | 123.1247 | -123.2803 | -123.1888 | 122.8317 | 123.0927 | 53.6499 | 52.858
926.9062 | 123.2849 | -54.2221 | 68.7973 | -0.048828 | 0.0010745 | 0.062649 | 0.067364 | 0.00029473 | -0.0016663 | -0.0019162 | 0.028168 | 0.003339 | 0.063198 | 0.064961 | -0.006037 | 0.0052572 | -0.0039883 | -0.6134 | 68.8293 | -54.4464 | 68.7149 | -53.5858 | -54.4189 | 0.17395 | -0.97961 | 68.8431 | -54.2908 | 68.9392 | -53.714 | -54.2953 | -53.9841 | -0.2243 | 0.032044 | -0.082397 | 0.63629 | 54.3961 | -0.19684 | 54.6204 | 0.027466 | -0.068664 | 0.045777 | 0.14191 | 0.50812 | 0.23804 | -0.073242 | 0.3067 | -0.004578 | 0.8606 | 123.1613 | 0.57678 | 123.23 | 123.2758 | 123.1338 | 123.0515 | 123.0652 | -123.2437 | -123.0881 | 122.937 | 123.1613 | 53.6087 | 53.2425
927.8594 | 123.2574 | -54.2953 | 68.7424 | -0.048828 | 0.00022006 | 0.064145 | 0.069927 | 0.0032855 | -0.0029481 | -0.0010618 | -0.093903 | 0.004407 | 0.069607 | 0.063893 | -0.007746 | 0.0097434 | -0.00035666 | -0.72784 | 68.7973 | -54.5425 | 68.5822 | -53.7506 | -54.5929 | 0.004578 | -1.5884 | 68.7561 | -54.3961 | 68.7881 | -53.8284 | -54.4235 | -54.1122 | -0.24719 | 0.054931 | -0.16022 | 0.54474 | 54.2999 | -0.29755 | 54.5471 | -0.050354 | -0.10071 | 0.013733 | 0.045776 | 0.46692 | 0.18311 | -0.12817 | 0.28381 | -0.027466 | 0.79193 | 123.1247 | 0.56763 | 123.1842 | 123.3398 | 123.1522 | 123.0927 | 123.0515 | -123.2849 | -123.1384 | 122.8775 | 123.0835 | 53.5675 | 52.7069
928.8906 | 123.1979 | -54.332 | 68.7607 | -0.041199 | 0.0021427 | 0.063076 | 0.068859 | -0.00013247 | -0.0025207 | 0.00086083 | -0.05423 | 0.0029116 | 0.067471 | 0.067097 | -0.0075324 | 0.0058982 | -0.0044157 | -0.72784 | 68.7698 | -54.5563 | 68.573 | -53.7552 | -54.5746 | 0.027466 | -1.6891 | 68.7881 | -54.3915 | 68.7378 | -53.8422 | -54.4418 | -54.1397 | -0.2243 | 0.009155 | -0.18768 | 0.57678 | 54.3594 | -0.24262 | 54.5837 | -0.018311 | -0.059509 | 0.027466 | -0.022888 | 0.48981 | 0.19226 | -0.10986 | 0.25177 | -0.050354 | 0.80109 | 123.1293 | 0.54932 | 123.1293 | 123.3261 | 123.1796 | 123.1018 | 123.1201 | -123.317 | -123.1522 | 122.905 | 123.0698 | 53.6041 | 52.6428
929.8594 | 123.1842 | -54.364 | 68.7241 | -0.048828 | 0.00086086 | 0.063504 | 0.068646 | -0.00098687 | 0.00089713 | -0.00020717 | -0.048126 | 0.005048 | 0.070034 | 0.06667 | -0.0068914 | 0.0067526 | -0.0016385 | -0.68207 | 68.7515 | -54.5563 | 68.5867 | -53.7231 | -54.5471 | 0.050354 | -1.6479 | 68.7881 | -54.3915 | 68.6966 | -53.8696 | -54.4785 | -54.1992 | -0.19226 | 0.027466 | -0.13733 | 0.64087 | 54.4144 | -0.18311 | 54.6066 | 0.009155 | -0.027465 | 0.064087 | -0.027466 | 0.49438 | 0.16479 | -0.11444 | 0.19226 | -0.086976 | 0.83313 | 123.143 | 0.52185 | 123.0881 | 123.3078 | 123.1796 | 123.1155 | 123.1522 | -123.2803 | -123.1155 | 122.9507 | 123.0606 | 53.6819 | 52.7161
930.8906 | 123.1888 | -54.3823 | 68.6966 | -0.010681 | 0.00086086 | 0.061795 | 0.067791 | -0.00077327 | -0.0029481 | -0.0034116 | -0.060333 | 0.0018436 | 0.071102 | 0.080128 | -0.0086004 | 0.0058982 | 0.0017795 | -0.75989 | 68.7744 | -54.6249 | 68.5272 | -53.8055 | -54.6158 | -0.004578 | -1.8311 | 68.6874 | -54.4647 | 68.7973 | -54.0115 | -54.4144 | -54.1168 | -0.24262 | 0.07782 | -0.16937 | 0.57678 | 54.3777 | -0.23346 | 54.6204 | 0.009155 | -0.082398 | -0.009155 | 0.10071 | 0.37079 | 0.2655 | -0.032044 | 0.3479 | 0.050354 | 0.8194 | 123.1522 | 0.45319 | 123.262 | 123.3994 | 123.1522 | 123.1567 | 123.0698 | -123.3215 | -123.1613 | 122.9095 | 123.1796 | 53.6224 | 52.5513
931.8594 | 123.1705 | -54.4189 | 68.6783 | -0.0030519 | 0.0012881 | 0.062863 | 0.068432 | 0.0011493 | -0.0016663 | -0.00042077 | -0.017609 | 0.0012028 | 0.070248 | 0.061756 | -0.007105 | 0.008248 | -0.0016385 | -0.79651 | 68.7057 | -54.6661 | 68.4769 | -53.8559 | -54.6661 | -0.032043 | -1.9547 | 68.6737 | -54.483 | 68.6188 | -53.9658 | -54.538 | -54.2679 | -0.24719 | 0.027466 | -0.20142 | 0.56305 | 54.3869 | -0.24719 | 54.6341 | 0 | -0.064087 | -0.004578 | -0.05951 | 0.45319 | 0.15106 | -0.11902 | 0.21515 | -0.054932 | 0.81024 | 123.143 | 0.51727 | 123.1018 | 123.3719 | 123.1567 | 123.1247 | 123.0927 | -123.3444 | -123.1613 | 122.8958 | 123.0377 | 53.6224 | 52.4643
932.9062 | 123.2025 | -54.4922 | 68.605 | -0.041199 | 0.00064726 | 0.063717 | 0.069714 | 0.00093573 | -0.00059807 | -0.001489 | -0.12137 | 0.0018436 | 0.069607 | 0.062611 | -0.0066778 | 0.0093162 | -0.00035666 | -0.82855 | 68.6142 | -54.7119 | 68.4265 | -53.9383 | -54.7623 | -0.13275 | -2.1698 | 68.5776 | -54.5975 | 68.5684 | -54.0115 | -54.6616 | -54.3365 | -0.21973 | 0.009155 | -0.17853 | 0.55389 | 54.3594 | -0.27008 | 54.5792 | -0.050354 | -0.10529 | -0.027466 | -0.036622 | 0.48065 | 0.15564 | -0.16937 | 0.26093 | -0.064087 | 0.77362 | 123.1384 | 0.58594 | 123.1659 | 123.3261 | 123.175 | 123.1064 | 123.0698 | -123.317 | -123.2025 | 122.9187 | 123.0606 | 53.6636 | 52.3224
933.8594 | 123.2391 | -54.5197 | 68.5867 | -0.056457 | 0.0042789 | 0.061367 | 0.070355 | -0.00077327 | -0.0018799 | 0.00022003 | -0.029816 | 0.0031254 | 0.070461 | 0.065174 | -0.0092414 | 0.0061118 | 0.00049774 | -0.88348 | 68.6096 | -54.7394 | 68.3899 | -53.9566 | -54.7531 | -0.09613 | -2.2018 | 68.5776 | -54.5929 | 68.5455 | -54.0482 | -54.6204 | -54.332 | -0.21973 | 0.022888 | -0.19684 | 0.56305 | 54.4235 | -0.23346 | 54.6432 | -0.013733 | -0.073243 | -0.009155 | -0.041199 | 0.4715 | 0.18768 | -0.10071 | 0.26093 | -0.027465 | 0.78278 | 123.1293 | 0.54474 | 123.1384 | 123.349 | 123.1705 | 123.1293 | 123.0972 | -123.3261 | -123.1796 | 122.9095 | 123.0652 | 53.6362 | 52.3178
934.8906 | 123.1888 | -54.57 | 68.5364 | -0.064087 | 0.0021427 | 0.062008 | 0.068432 | 0.0034991 | -0.0023071 | -0.003198 | -0.017609 | 0.0022708 | 0.068966 | 0.060902 | -0.0066778 | 0.0071798 | -0.0022793 | -0.89722 | 68.5959 | -54.7806 | 68.3258 | -53.9932 | -54.8126 | -0.1236 | -2.3392 | 68.5455 | -54.6341 | 68.486 | -54.0894 | -54.6799 | -54.3823 | -0.21057 | 0.059509 | -0.21057 | 0.57678 | 54.4464 | -0.24262 | 54.657 | -0.032043 | -0.064087 | 0.009155 | -0.050354 | 0.48065 | 0.18768 | -0.10986 | 0.25177 | -0.045777 | 0.78735 | 123.1064 | 0.54474 | 123.1201 | 123.3765 | 123.1796 | 123.1659 | 123.1155 | -123.317 | -123.1705 | 122.8958 | 123.056 | 53.6728 | 52.2308
935.8594 | 123.1888 | -54.6021 | 68.5043 | -0.056457 | 0.0012881 | 0.059659 | 0.068005 | -0.00098687 | -0.0029481 | -0.0040524 | -0.0084534 | 0.0029116 | 0.070034 | 0.066456 | -0.0056098 | 0.0050436 | 0.0039157 | -0.9201 | 68.5318 | -54.808 | 68.28 | -54.0207 | -54.8355 | -0.13733 | -2.4124 | 68.5043 | -54.689 | 68.4265 | -54.1351 | -54.7165 | -54.4418 | -0.20599 | 0.027466 | -0.2243 | 0.58136 | 54.4647 | -0.23346 | 54.6707 | -0.027466 | -0.086975 | 0 | -0.077819 | 0.46692 | 0.16022 | -0.11444 | 0.24719 | -0.027466 | 0.78735 | 123.0881 | 0.55389 | 123.1155 | 123.3398 | 123.1934 | 123.1339 | 123.1064 | -123.3124 | -123.1934 | 122.8821 | 123.0286 | 53.6819 | 52.1896
936.9219 | 123.3032 | -54.6524 | 68.367 | -0.056457 | 0.0042789 | 0.062008 | 0.068005 | 0.0011493 | -0.00081187 | -0.001489 | -0.014557 | 0.0020572 | 0.06918 | 0.069233 | -0.0068914 | 0.0063254 | -0.0027067 | -0.93384 | 68.399 | -54.9088 | 68.2846 | -53.9886 | -54.895 | -0.1831 | -2.4445 | 68.3578 | -54.744 | 68.486 | -54.1351 | -54.7028 | -54.3869 | -0.25635 | 0.032044 | -0.082397 | 0.66376 | 54.4693 | -0.24262 | 54.7256 | 0.013732 | -0.091553 | -0.009155 | 0.11902 | 0.51727 | 0.2655 | -0.050354 | 0.35706 | 0.041199 | 0.9201 | 123.1934 | 0.60883 | 123.23 | 123.3078 | 123.1018 | 123.0515 | 123.0103 | -123.2758 | -123.111 | 122.937 | 123.1384 | 53.7186 | 52.2079
937.8594 | 123.1934 | -54.7165 | 68.3853 | -0.10986 | 0.0042789 | 0.063931 | 0.0695 | 0.00029473 | -0.0010255 | -0.0021298 | -0.029816 | 0.003339 | 0.070461 | 0.063465 | -0.0083868 | 0.008248 | -0.00035666 | -1.03 | 68.4036 | -54.9408 | 68.1976 | -54.1489 | -55.0049 | -0.62256 | -2.6093 | 68.4265 | -54.776 | 68.3304 | -54.2725 | -54.8676 | -54.5609 | -0.2243 | 0.01831 | -0.18768 | 0.56763 | 54.0939 | -0.28839 | 54.3182 | -0.064087 | -0.059509 | 0.041199 | -0.054932 | 0.44403 | 0.15564 | -0.15106 | 0.21515 | -0.091553 | 0.79193 | 123.1384 | 0.50354 | 123.1064 | 123.3444 | 123.2025 | 123.1201 | 123.143 | -123.3261 | -123.1613 | 122.9141 | 123.0469 | 53.6865 | 52.1072
938.9062 | 123.1934 | -54.7531 | 68.2892 | -0.079346 | 0.0027835 | 0.064572 | 0.071209 | 8.1126e-05 | -0.0014527 | -0.0012754 | -0.060333 | 0.0039798 | 0.068966 | 0.059834 | -0.007105 | 0.0063254 | -0.0039883 | -1.0941 | 68.3533 | -55.0095 | 68.0832 | -54.2358 | -55.0598 | -0.31586 | -2.7283 | 68.3029 | -54.8676 | 68.2983 | -54.332 | -54.9179 | -54.5975 | -0.25635 | 0.064086 | -0.20599 | 0.51727 | 54.4373 | -0.3067 | 54.6936 | -0.050354 | -0.11444 | 0.013732 | 0.009155 | 0.42114 | 0.15564 | -0.16479 | 0.27008 | -0.050354 | 0.77362 | 123.0927 | 0.53558 | 123.1659 | 123.3627 | 123.1705 | 123.1064 | 123.056 | -123.2986 | -123.1567 | 122.8363 | 123.0515 | 53.6591 | 52.0248
939.8594 | 123.2117 | -54.7806 | 68.2892 | -0.033569 | 0.0027835 | 0.063504 | 0.069927 | -0.0039777 | -0.0029481 | -0.0019162 | -0.05423 | 0.0035526 | 0.066616 | 0.066029 | -0.0079596 | 0.0058982 | -0.0012113 | -1.1215 | 68.367 | -55.0232 | 68.0969 | -54.2404 | -55.0278 | -0.29755 | -2.7649 | 68.3121 | -54.8813 | 68.2663 | -54.332 | -54.895 | -54.6158 | -0.24261 | 0.077819 | -0.19226 | 0.54016 | 54.483 | -0.24719 | 54.7256 | -0.004578 | -0.10071 | 0.022888 | -0.022889 | 0.44861 | 0.1648 | -0.11444 | 0.2655 | -0.013733 | 0.78278 | 123.1201 | 0.54932 | 123.1476 | 123.3902 | 123.1934 | 123.1476 | 123.0927 | -123.3124 | -123.1705 | 122.8775 | 123.0469 | 53.6591 | 52.0157
940.8906 | 123.2254 | -54.8584 | 68.2114 | -0.033569 | 0.00064726 | 0.063504 | 0.0695 | 0.0047809 | -0.00059807 | -0.0012754 | -0.13052 | 0.0018436 | 0.069393 | 0.066029 | -0.007746 | 0.0067526 | 0.00071134 | -1.1581 | 68.2892 | -55.0873 | 68.2343 | -54.5013 | -54.9866 | -0.082397 | -2.655 | 68.2617 | -54.9088 | 68.2571 | -54.3732 | -54.9271 | -54.6387 | -0.22888 | 0.07782 | 0.022888 | 0.35706 | 54.776 | -0.12817 | 55.0049 | 0.10071 | -0.050354 | 0.050354 | 0.045776 | 0.48523 | 0.21973 | -0.068665 | 0.27008 | -0.018311 | 0.58594 | 123.3215 | 0.53558 | 123.1659 | 123.3765 | 123.1705 | 123.1476 | 123.1201 | -123.2986 | -123.1201 | 123.0927 | 123.1155 | 53.7003 | 52.2034
941.8594 | 123.2117 | -54.8904 | 68.2022 | -0.064087 | 0.0010745 | 0.061581 | 0.068859 | 0.0034991 | -0.00038447 | -0.0029844 | -0.032867 | 0.0031254 | 0.070248 | 0.06667 | -0.0073188 | 0.008248 | -0.0012113 | -1.2314 | 68.2663 | -55.1239 | 68.0054 | -54.3594 | -55.1468 | -0.42114 | -2.948 | 68.2114 | -54.9866 | 68.1793 | -54.4235 | -54.9866 | -54.7256 | -0.23346 | 0.064087 | -0.19684 | 0.53101 | 54.4693 | -0.25635 | 54.7028 | -0.022889 | -0.09613 | 0.009156 | -0.022888 | 0.46692 | 0.16479 | -0.09613 | 0.26093 | 0 | 0.76446 | 123.1293 | 0.56305 | 123.1659 | 123.3902 | 123.1979 | 123.1567 | 123.1018 | -123.3261 | -123.1888 | 122.8958 | 123.0698 | 53.6591 | 51.9424
942.9062 | 123.1705 | -54.982 | 68.1061 | -0.041199 | 0.0036381 | 0.062222 | 0.0695 | 0.0026447 | -0.0010255 | -0.002557 | -0.28311 | 0.00163 | 0.067684 | 0.062397 | -0.006037 | 0.008248 | -0.0044157 | -1.3367 | 68.1244 | -55.2109 | 67.9184 | -54.4281 | -55.2383 | -0.54474 | -2.742 | 68.129 | -55.0323 | 68.1198 | -54.57 | -55.1102 | -54.7806 | -0.22888 | 0.018311 | -0.18768 | 0.55389 | 54.4373 | -0.25635 | 54.6661 | -0.027466 | -0.050354 | 0.022888 | 0.013733 | 0.41199 | 0.20142 | -0.12817 | 0.25177 | -0.077819 | 0.78278 | 123.1293 | 0.46234 | 123.1522 | 123.3353 | 123.1613 | 123.1064 | 123.111 | -123.317 | -123.1384 | 122.9004 | 123.1018 | 53.6453 | 52.24
943.8594 | 123.1842 | -55.014 | 68.0786 | -0.033569 | 0.0023563 | 0.06329 | 0.069286 | -0.00013247 | -0.0023071 | -0.00020717 | -0.032867 | 0.0046206 | 0.06918 | 0.061329 | -0.007746 | 0.003762 | 0.00049774 | -1.4236 | 68.129 | -55.22 | 67.8726 | -54.4647 | -55.2292 | -0.54474 | -3.1174 | 68.0923 | -55.0827 | 68.0328 | -54.5563 | -55.1285 | -54.8172 | -0.20599 | 0.050354 | -0.20599 | 0.54932 | 54.4693 | -0.21515 | 54.6753 | -0.009155 | -0.068665 | 0.013733 | -0.045776 | 0.45776 | 0.19684 | -0.11444 | 0.2655 | -0.045776 | 0.75531 | 123.0927 | 0.52643 | 123.1155 | 123.349 | 123.175 | 123.143 | 123.1064 | -123.2986 | -123.1613 | 122.8867 | 123.0469 | 53.5904 | 51.8967
944.9062 | 123.317 | -55.0873 | 67.9504 | -0.10223 | 0.0029971 | 0.062222 | 0.0695 | 0.00050853 | 0.00025633 | -0.001489 | 0.0068054 | 0.0039798 | 0.068966 | 0.061756 | -0.0066778 | 0.006539 | 0.0015659 | -1.474 | 67.9916 | -55.307 | 67.8772 | -54.4601 | -55.2612 | -0.56763 | -3.0991 | 67.9504 | -55.1559 | 68.0557 | -54.5746 | -55.1147 | -54.7897 | -0.21973 | 0.041199 | -0.073242 | 0.62714 | 54.5197 | -0.17395 | 54.7394 | 0.045777 | -0.068665 | 0 | 0.10529 | 0.5127 | 0.29755 | -0.027466 | 0.36621 | 0.041199 | 0.84686 | 123.1842 | 0.58136 | 123.2117 | 123.2986 | 123.1064 | 123.0789 | 123.0377 | -123.2574 | -123.1064 | 122.9645 | 123.143 | 53.6133 | 51.9882
945.8594 | 123.2117 | -55.1285 | 67.9779 | -0.056457 | 0.00043366 | 0.063076 | 0.068646 | -0.00077327 | -0.0018799 | -0.00042077 | -0.026764 | 0.0022708 | 0.068112 | 0.067524 | -0.0075324 | 0.0063254 | 0.0017795 | -1.5976 | 68.0374 | -55.3207 | 67.7673 | -54.5792 | -55.3619 | -0.66834 | -3.2639 | 67.9871 | -55.2017 | 67.9047 | -54.6844 | -55.2383 | -54.9454 | -0.19226 | 0.05951 | -0.21057 | 0.54932 | 54.4601 | -0.23346 | 54.6524 | -0.041198 | -0.073242 | 0.009156 | -0.073242 | 0.44403 | 0.1831 | -0.10986 | 0.25635 | -0.036621 | 0.74158 | 123.0881 | 0.51727 | 123.1064 | 123.3582 | 123.1888 | 123.1659 | 123.1155 | -123.2986 | -123.1796 | 122.8958 | 123.0331 | 53.5309 | 51.8646
946.9219 | 123.2574 | -55.1834 | 67.8726 | -0.041199 | 0.00086086 | 0.063931 | 0.068432 | -0.00034607 | -0.0027345 | -0.0010618 | 0.037323 | 0.0024844 | 0.069607 | 0.055134 | -0.008814 | 0.0061118 | 0.0019931 | -1.5747 | 67.9276 | -55.3619 | 67.8177 | -54.5288 | -55.3162 | -0.61798 | -3.2272 | 67.8864 | -55.2246 | 67.9321 | -54.6616 | -55.2017 | -54.9408 | -0.17853 | 0.054931 | -0.054932 | 0.6546 | 54.5654 | -0.13275 | 54.744 | 0.045776 | -0.041198 | 0.013733 | 0.059509 | 0.52185 | 0.24262 | -0.01831 | 0.28381 | 0.022888 | 0.83313 | 123.1796 | 0.56305 | 123.1567 | 123.2895 | 123.111 | 123.111 | 123.0698 | -123.2346 | -123.0972 | 123.0011 | 123.1155 | 53.6087 | 51.9562
947.8594 | 123.1842 | -55.2429 | 67.8543 | -0.079346 | 0.0027835 | 0.062863 | 0.069714 | 0.00093573 | -0.00081187 | -0.0046934 | -0.014557 | 0.0052616 | 0.068966 | 0.061329 | -0.0079596 | 0.006539 | 0.00049774 | -1.6846 | 67.8955 | -55.4352 | 67.6804 | -54.6936 | -55.4718 | -0.737 | -3.4149 | 67.8589 | -55.307 | 67.804 | -54.7897 | -55.3528 | -55.0598 | -0.19226 | 0.041199 | -0.17395 | 0.54932 | 54.5059 | -0.22888 | 54.6982 | -0.036621 | -0.064087 | 0.004578 | -0.050354 | 0.45319 | 0.18311 | -0.10986 | 0.24719 | -0.045776 | 0.74158 | 123.1155 | 0.51727 | 123.111 | 123.3307 | 123.1659 | 123.1384 | 123.1018 | -123.2895 | -123.1613 | 122.9233 | 123.0469 | 53.5583 | 51.828
948.9062 | 123.1796 | -55.3116 | 67.7673 | -0.086975 | 0.0012881 | 0.06329 | 0.070141 | 0.0030719 | -0.0025207 | -0.00020717 | -0.096954 | 0.0037662 | 0.069393 | 0.069447 | -0.007105 | 0.006539 | -0.0012113 | -1.767 | 67.8131 | -55.5634 | 67.543 | -54.8401 | -55.6458 | -0.85602 | -3.5522 | 67.7994 | -55.394 | 67.7261 | -54.9179 | -55.4901 | -55.1514 | -0.25177 | 0.045776 | -0.2243 | 0.4715 | 54.4556 | -0.33417 | 54.7073 | -0.082398 | -0.082398 | 0.032043 | -0.041199 | 0.39368 | 0.16022 | -0.17853 | 0.24262 | -0.09613 | 0.72327 | 123.1064 | 0.47607 | 123.1201 | 123.3765 | 123.1934 | 123.1247 | 123.111 | -123.3307 | -123.1613 | 122.8546 | 123.0377 | 53.5446 | 51.7593
949.8594 | 123.2025 | -55.3482 | 67.7399 | -0.02594 | 0.0036381 | 0.063717 | 0.068859 | -0.0016279 | -0.0023071 | -0.001489 | -0.0023498 | 0.0024844 | 0.06683 | 0.058766 | -0.0051824 | 0.0050436 | -0.00014306 | -1.7899 | 67.7902 | -55.5862 | 67.5613 | -54.8172 | -55.5725 | -0.81482 | -3.511 | 67.7856 | -55.426 | 67.6987 | -54.9042 | -55.4398 | -55.1697 | -0.23804 | 0.050354 | -0.17853 | 0.53101 | 54.5334 | -0.2243 | 54.7714 | 0.013733 | -0.077819 | 0.045777 | -0.041199 | 0.44403 | 0.17853 | -0.091552 | 0.25635 | -0.013733 | 0.76904 | 123.1476 | 0.52185 | 123.1247 | 123.3765 | 123.2117 | 123.1384 | 123.1339 | -123.3261 | -123.1659 | 122.9095 | 123.0469 | 53.5583 | 51.8372
950.9062 | 123.3032 | -55.3848 | 67.6163 | -0.048828 | 0.0019291 | 0.065213 | 0.0695 | 0.0024311 | 0.00068353 | -0.0029844 | -0.038971 | 0.0018436 | 0.068325 | 0.070942 | -0.0068914 | 0.0071798 | -0.00014306 | -1.7944 | 67.6483 | -55.6366 | 67.543 | -54.808 | -55.6274 | -0.84228 | -3.5156 | 67.5934 | -55.4993 | 67.7353 | -54.9133 | -55.4672 | -55.1422 | -0.25177 | 0.032043 | -0.073242 | 0.57678 | 54.5425 | -0.24261 | 54.7943 | 0.009156 | -0.11444 | -0.022888 | 0.11902 | 0.4715 | 0.24262 | -0.082397 | 0.35706 | 0.032044 | 0.82855 | 123.1796 | 0.58594 | 123.2346 | 123.2849 | 123.0927 | 123.0331 | 122.9782 | -123.2529 | -123.1155 | 122.9279 | 123.1201 | 53.5904 | 51.8692
951.8594 | 123.2117 | -55.4718 | 67.6163 | -0.033569 | 0.0015019 | 0.062436 | 0.070141 | 0.00072213 | -0.0010255 | -0.00084817 | -0.011505 | 0.00163 | 0.069607 | 0.064747 | -0.0086004 | 0.0054708 | -0.0027067 | -1.8768 | 67.6758 | -55.687 | 67.4286 | -54.9179 | -55.7007 | -0.93384 | -3.6667 | 67.6483 | -55.5176 | 67.5797 | -55.0232 | -55.5862 | -55.2887 | -0.21515 | 0.059509 | -0.18768 | 0.55389 | 54.538 | -0.22888 | 54.7531 | -0.013733 | -0.045776 | 0.032043 | -0.036621 | 0.44861 | 0.18311 | -0.11444 | 0.22888 | -0.068665 | 0.76904 | 123.1155 | 0.49439 | 123.0972 | 123.3627 | 123.1659 | 123.1476 | 123.1201 | -123.3032 | -123.1338 | 122.9004 | 123.0515 | 53.595 | 51.8051
952.9062 | 123.2986 | -55.5267 | 67.4973 | -0.10223 | 0.00022006 | 0.063717 | 0.068005 | 0.0024311 | -0.0012391 | -0.0021298 | -0.069489 | 0.0031254 | 0.067044 | 0.067951 | -0.008814 | 0.0088888 | -0.00035666 | -2.0416 | 67.4973 | -55.8014 | 67.4194 | -54.9133 | -55.7785 | -0.99792 | -3.685 | 67.4881 | -55.6137 | 67.6025 | -55.0323 | -55.5679 | -55.2612 | -0.27466 | 0 | -0.077819 | 0.6134 | 54.5288 | -0.25177 | 54.8035 | 0.022889 | -0.086975 | -0.009155 | 0.10529 | 0.49438 | 0.2655 | -0.041199 | 0.35248 | 0.045776 | 0.88806 | 123.2208 | 0.58136 | 123.2162 | 123.2986 | 123.1018 | 123.024 | 123.0148 | -123.2986 | -123.111 | 122.9462 | 123.1293 | 53.4851 | 51.8417
953.8594 | 123.2346 | -55.6137 | 67.4835 | -0.02594 | 0.0029971 | 0.062863 | 0.068432 | 0.0039263 | -0.0018799 | -0.00084817 | -0.0054016 | 0.0037662 | 0.068539 | 0.06902 | -0.0090278 | 0.0093162 | -0.00099766 | -1.9501 | 67.5339 | -55.806 | 67.3553 | -55.0232 | -55.7922 | -1.2222 | -3.8681 | 67.511 | -55.6366 | 67.4973 | -55.101 | -55.6961 | -55.3848 | -0.19226 | 0.050354 | -0.12817 | 0.59052 | 54.3915 | -0.17853 | 54.5837 | 0.013733 | -0.022889 | 0.027465 | 0.013732 | 0.5127 | 0.22888 | -0.082398 | 0.25177 | -0.059509 | 0.78278 | 123.1613 | 0.53558 | 123.1338 | 123.3398 | 123.1476 | 123.1476 | 123.1247 | -123.2895 | -123.1201 | 122.9691 | 123.111 | 53.6636 | 51.7456
954.9062 | 123.1842 | -55.6824 | 67.424 | -0.10986 | 0.0021427 | 0.062649 | 0.070782 | 0.00072213 | -0.0033753 | -0.00042077 | -0.090851 | 0.0041934 | 0.067471 | 0.070301 | -0.0075324 | 0.0080344 | 0.0011385 | -2.0737 | 67.4606 | -55.8975 | 67.2043 | -55.2017 | -55.9891 | -1.2497 | -3.9642 | 67.424 | -55.7693 | 67.3691 | -55.2795 | -55.838 | -55.5038 | -0.21515 | 0.036621 | -0.21973 | 0.48065 | 54.4327 | -0.3067 | 54.6478 | -0.091553 | -0.086975 | 0 | -0.054931 | 0.40283 | 0.17853 | -0.15564 | 0.2655 | -0.068665 | 0.6958 | 123.1018 | 0.48981 | 123.1384 | 123.3582 | 123.1934 | 123.143 | 123.1064 | -123.3215 | -123.1934 | 122.8867 | 123.0515 | 53.6087 | 51.7181
955.8594 | 123.1979 | -55.7144 | 67.3874 | 0.065613 | 0.0023563 | 0.06094 | 0.067791 | 0.0020037 | -0.00038447 | -0.0019162 | -0.0054016 | 0.0039798 | 0.068325 | 0.067311 | -0.0066778 | 0.0067526 | -0.0016385 | -2.1881 | 67.4423 | -55.9158 | 67.1951 | -55.1743 | -55.9158 | -1.1169 | -3.9413 | 67.4149 | -55.7648 | 67.337 | -55.2704 | -55.806 | -55.5359 | -0.20142 | 0.054932 | -0.19226 | 0.54016 | 54.5975 | -0.20142 | 54.7989 | 0 | -0.050354 | 0.027466 | -0.050354 | 0.44403 | 0.17853 | -0.091552 | 0.22888 | -0.041198 | 0.74158 | 123.111 | 0.49439 | 123.1018 | 123.3582 | 123.1796 | 123.1567 | 123.1293 | -123.3032 | -123.1522 | 122.9095 | 123.0515 | 53.5263 | 51.7731
956.9219 | 123.2437 | -55.7693 | 67.2684 | -0.10223 | 0.0027835 | 0.061154 | 0.067791 | 0.00050853 | 0.00025633 | -0.003198 | 0.034271 | 0.0014164 | 0.068966 | 0.064747 | -0.008814 | 0.0050436 | -0.00078406 | -2.1469 | 67.305 | -55.9662 | 67.1585 | -55.1926 | -55.9799 | -1.2085 | -3.9825 | 67.2684 | -55.838 | 67.3141 | -55.307 | -55.8517 | -55.545 | -0.19684 | 0.036621 | -0.10986 | 0.57678 | 54.5609 | -0.21057 | 54.7577 | -0.013732 | -0.068665 | 0 | 0.045776 | 0.46234 | 0.2243 | -0.082398 | 0.29297 | -0.013733 | 0.77362 | 123.1247 | 0.53101 | 123.1522 | 123.2712 | 123.1064 | 123.0743 | 123.0377 | -123.2346 | -123.1064 | 122.9279 | 123.0835 | 53.6224 | 51.7868
957.8594 | 123.1842 | -55.8289 | 67.2867 | -0.02594 | 0.0019291 | 0.061581 | 0.069714 | 0.0026447 | -0.0033753 | 6.432e-06 | -0.014557 | 0.0037662 | 0.068325 | 0.067738 | -0.006037 | 0.0069662 | -0.0016385 | -2.1469 | 67.2867 | -56.0165 | 67.131 | -55.2338 | -55.9708 | -0.97504 | -4.0878 | 67.2684 | -55.8884 | 67.2272 | -55.3665 | -55.925 | -55.6183 | -0.18768 | 0 | -0.15564 | 0.59509 | 54.8538 | -0.14191 | 55.0415 | 0.045777 | -0.05951 | -0.01831 | -0.059509 | 0.46234 | 0.21057 | -0.096131 | 0.27008 | -0.036621 | 0.78278 | 123.1476 | 0.52185 | 123.1155 | 123.3032 | 123.1567 | 123.1155 | 123.0972 | -123.3032 | -123.175 | 122.9599 | 123.056 | 53.6819 | 51.741
958.9062 | 123.2941 | -55.8884 | 67.1265 | -0.15564 | -0.00020714 | 0.064999 | 0.070568 | 8.1126e-05 | 0.00046993 | -0.0023434 | -0.042023 | 0.0022708 | 0.06683 | 0.06667 | -0.0079596 | 0.0058982 | -0.0012113 | -2.2797 | 67.1997 | -56.1218 | 67.0166 | -55.2063 | -55.9525 | -1.3321 | -4.0695 | 67.1631 | -55.9616 | 67.2592 | -55.4123 | -55.9616 | -55.6412 | -0.23346 | 0.073242 | -0.10986 | 0.68207 | 54.5563 | -0.064087 | 54.7897 | 0.16937 | -0.073242 | 0.036621 | 0.13275 | 0.47608 | 0.24719 | -0.073242 | 0.32044 | 0 | 0.91553 | 123.1384 | 0.54932 | 123.2208 | 123.3215 | 123.1247 | 123.0881 | 123.0515 | -123.2483 | -123.0881 | 122.905 | 123.1476 | 53.6087 | 51.8188
959.8594 | 123.175 | -55.9616 | 67.1585 | -0.064087 | 0.0019291 | 0.063717 | 0.068218 | -0.00077327 | -0.0048707 | -0.0034116 | -0.048126 | 0.0022708 | 0.067684 | 0.065388 | -0.0064642 | 0.0063254 | -0.00078406 | -2.3163 | 67.1906 | -56.1584 | 66.9754 | -55.4169 | -56.163 | -1.3138 | -4.1428 | 67.1722 | -56.044 | 67.1082 | -55.5176 | -56.0486 | -55.7648 | -0.19684 | 0.032044 | -0.1831 | 0.54474 | 54.6478 | -0.20142 | 54.8447 | -0.004578 | -0.082397 | 0.013733 | -0.050354 | 0.44403 | 0.19684 | -0.086975 | 0.27923 | -0.004578 | 0.74158 | 123.1338 | 0.52643 | 123.1522 | 123.349 | 123.2162 | 123.1522 | 123.1338 | -123.317 | -123.2025 | 122.937 | 123.0698 | 53.6453 | 51.8188
960.9062 | 123.1979 | -56.044 | 67.0303 | -0.094604 | 0.0012881 | 0.062222 | 0.0695 | 8.1126e-05 | -0.0035889 | -0.0036252 | -0.096954 | 0.0029116 | 0.069393 | 0.068165 | -0.0066778 | 0.0058982 | -0.0016385 | -2.4033 | 67.0853 | -56.2775 | 66.861 | -55.5359 | -56.3232 | -1.4282 | -4.2389 | 67.0578 | -56.1035 | 67.0395 | -55.6274 | -56.163 | -55.8563 | -0.23346 | 0.054932 | -0.16937 | 0.50812 | 54.6158 | -0.27924 | 54.8492 | -0.045776 | -0.05951 | 0.027466 | 0.009156 | 0.41657 | 0.18768 | -0.11902 | 0.24719 | -0.059509 | 0.74158 | 123.1384 | 0.47608 | 123.143 | 123.3627 | 123.1613 | 123.1293 | 123.1018 | -123.3078 | -123.1338 | 122.905 | 123.0835 | 53.6407 | 51.8051
961.8594 | 123.23 | -56.0394 | 67.0166 | -0.048828 | 0.0023563 | 0.061581 | 0.070782 | -0.00034607 | 4.273e-05 | -0.0019162 | -0.048126 | 0.0018436 | 0.06918 | 0.066456 | -0.0066778 | 0.0056846 | 0.0011385 | -2.4307 | 67.0944 | -56.282 | 66.8518 | -55.5313 | -56.2683 | -1.387 | -4.2114 | 67.0624 | -56.1218 | 67.0395 | -55.5862 | -56.1401 | -55.8334 | -0.24261 | 0.077819 | -0.1648 | 0.50812 | 54.6524 | -0.22888 | 54.895 | 0.013732 | -0.082397 | 0.045776 | 0.022888 | 0.45319 | 0.20599 | -0.10071 | 0.28839 | -0.018311 | 0.75073 | 123.1338 | 0.53558 | 123.1613 | 123.3765 | 123.1842 | 123.1338 | 123.1018 | -123.2986 | -123.1384 | 122.8912 | 123.0789 | 53.6087 | 51.828
962.9062 | 123.1979 | -56.1172 | 66.9113 | -0.11749 | 0.0029971 | 0.063931 | 0.067577 | -0.00013247 | 0.00068353 | -0.0023434 | -0.011505 | 0.003339 | 0.070034 | 0.067951 | -0.007746 | 0.0061118 | -0.0014249 | -2.4353 | 66.9708 | -56.3187 | 66.8381 | -55.481 | -56.3232 | -1.3596 | -4.1519 | 66.925 | -56.1813 | 66.8472 | -55.4535 | -56.1172 | -55.9067 | -0.20142 | 0.059509 | -0.073242 | 0.63629 | 54.7577 | -0.20599 | 54.9591 | -0.004577 | -0.064086 | 0.013733 | -0.064087 | 0.66376 | 0.21057 | 0 | 0.27466 | 0.064086 | 0.83771 | 123.1567 | 0.72784 | 123.0286 | 123.2895 | 123.1064 | 123.0881 | 123.0423 | -123.23 | -123.0927 | 122.9553 | 122.9645 | 53.6819 | 51.9653
963.8594 | 123.2025 | -56.163 | 66.9525 | -0.01831 | -0.00084814 | 0.061367 | 0.068859 | -0.00013247 | -0.0029481 | -0.0029844 | -0.048126 | 0.0048344 | 0.069821 | 0.061115 | -0.007105 | 0.006539 | -0.0042021 | -2.4857 | 66.9617 | -56.3736 | 66.7419 | -55.6412 | -56.3919 | -1.3962 | -4.2801 | 66.9571 | -56.2225 | 66.893 | -55.719 | -56.2683 | -55.9616 | -0.21057 | 0.009155 | -0.21057 | 0.52185 | 54.7668 | -0.22888 | 54.9774 | -0.018311 | -0.059509 | 0.004577 | -0.05951 | 0.44403 | 0.20142 | -0.10529 | 0.26093 | -0.045777 | 0.73242 | 123.1155 | 0.50354 | 123.1155 | 123.3353 | 123.1796 | 123.1247 | 123.1201 | -123.3261 | -123.175 | 122.905 | 123.056 | 53.6774 | 51.8829
964.9062 | 123.1888 | -56.218 | 66.8701 | -0.048828 | 0.0017155 | 0.063504 | 0.071209 | 0.0017901 | -0.0020935 | -0.0010618 | -0.066437 | 0.004407 | 0.067044 | 0.064106 | -0.0062506 | 0.0084616 | 0.0024203 | -2.5543 | 66.8976 | -56.4468 | 66.6458 | -55.7831 | -56.5567 | -1.4603 | -4.3396 | 66.8655 | -56.3004 | 66.8198 | -55.8517 | -56.3782 | -56.0532 | -0.22888 | 0.027466 | -0.2243 | 0.43488 | 54.7577 | -0.33875 | 54.9866 | -0.10986 | -0.082397 | -0.004577 | -0.050354 | 0.36621 | 0.16479 | -0.16022 | 0.24719 | -0.07782 | 0.66376 | 123.0927 | 0.44861 | 123.1201 | 123.3444 | 123.1659 | 123.1155 | 123.0835 | -123.317 | -123.1705 | 122.8638 | 123.0377 | 53.6636 | 51.8784
965.8594 | 123.2071 | -56.2546 | 66.8381 | 0.0045776 | 0.00064726 | 0.063717 | 0.069073 | 0.0024311 | -0.0012391 | -0.0021298 | -0.042023 | 0.0029116 | 0.070248 | 0.062824 | -0.0066778 | 0.0063254 | -0.0020657 | -2.5543 | 66.8793 | -56.4743 | 66.6458 | -55.7236 | -56.4835 | -1.3962 | -4.2892 | 66.8472 | -56.3232 | 66.7969 | -55.8334 | -56.369 | -56.0761 | -0.21973 | 0.041198 | -0.19226 | 0.53101 | 54.8584 | -0.22888 | 55.0781 | -0.009155 | -0.068664 | 0.009155 | -0.041199 | 0.42114 | 0.17853 | -0.11444 | 0.24719 | -0.045777 | 0.75073 | 123.1201 | 0.48981 | 123.1201 | 123.3536 | 123.1705 | 123.1338 | 123.1018 | -123.3124 | -123.1613 | 122.9004 | 123.0515 | 53.7003 | 51.9653
966.9219 | 123.2895 | -56.2363 | 66.7603 | -0.041199 | 0.0023563 | 0.064145 | 0.068646 | 0.0013629 | -0.00059807 | -0.0057614 | 0.025116 | 0.0018436 | 0.069821 | 0.057057 | -0.0064642 | 0.0056846 | -0.00014306 | -2.5314 | 66.7969 | -56.4972 | 66.7099 | -55.6503 | -56.4148 | -1.2909 | -4.1245 | 66.774 | -56.3553 | 66.8335 | -55.751 | -56.282 | -56.0211 | -0.26093 | 0.036621 | -0.050354 | 0.58594 | 54.9454 | -0.17853 | 55.2063 | 0.082397 | -0.11902 | 0.013733 | 0.073242 | 0.48523 | 0.21515 | -0.045776 | 0.33417 | 0.073243 | 0.84686 | 123.2071 | 0.60425 | 123.1888 | 123.2941 | 123.1293 | 123.0331 | 123.0103 | -123.2574 | -123.1155 | 122.9462 | 123.0698 | 53.7048 | 52.1118
967.8594 | 123.2117 | -56.3599 | 66.7465 | -0.086975 | 0.0036381 | 0.062222 | 0.069073 | 0.0022173 | -0.00081187 | -0.0038388 | -0.05423 | 0.0020572 | 0.067684 | 0.064533 | -0.0073188 | 0.0073936 | -0.0012113 | -2.6367 | 66.7969 | -56.5567 | 66.5451 | -55.838 | -56.575 | -1.3962 | -4.2984 | 66.7557 | -56.4377 | 66.7007 | -55.9341 | -56.456 | -56.1584 | -0.19684 | 0.050354 | -0.20142 | 0.52185 | 54.9637 | -0.21515 | 55.1605 | -0.01831 | -0.07782 | 0.009155 | -0.045776 | 0.42572 | 0.20142 | -0.096131 | 0.27924 | -0.018311 | 0.71869 | 123.1018 | 0.50354 | 123.1384 | 123.3536 | 123.1934 | 123.1567 | 123.1155 | -123.3032 | -123.1842 | 122.905 | 123.0606 | 53.7231 | 52.0615
968.9062 | 123.2712 | -56.3965 | 66.6412 | 0.11902 | 0.0012881 | 0.06329 | 0.0695 | 0.00050853 | -0.00038447 | 0.00064723 | -0.051178 | 0.0031254 | 0.068112 | 0.061756 | -0.0090278 | 0.0076072 | -0.0014249 | -2.6596 | 66.6641 | -56.6116 | 66.5543 | -55.8426 | -56.5887 | -1.3504 | -4.2297 | 66.6183 | -56.4606 | 66.7374 | -55.9204 | -56.4468 | -56.1356 | -0.21515 | 0.022889 | -0.086975 | 0.55389 | 55.0461 | -0.19226 | 55.2612 | 0.022888 | -0.064087 | -0.022888 | 0.096131 | 0.47607 | 0.26093 | -0.050354 | 0.32501 | 0.013733 | 0.76904 | 123.1659 | 0.54016 | 123.1979 | 123.2758 | 123.0789 | 123.0606 | 123.0148 | -123.2529 | -123.1018 | 122.9507 | 123.1338 | 53.7369 | 52.1667
969.8594 | 123.1888 | -56.4239 | 66.6595 | -0.079346 | 0.0010745 | 0.064145 | 0.070568 | 0.0024311 | -0.0040161 | -0.002557 | -0.035919 | 0.0039798 | 0.070034 | 0.059834 | -0.0068914 | 0.0052572 | -0.0012113 | -2.6962 | 66.7236 | -56.6711 | 66.4398 | -55.9204 | -56.662 | -1.3641 | -4.2801 | 66.6824 | -56.5201 | 66.6092 | -56.0349 | -56.5475 | -56.2454 | -0.24719 | 0.064087 | -0.21973 | 0.50354 | 55.0598 | -0.23804 | 55.307 | 0.009156 | -0.096131 | 0.022888 | -0.050354 | 0.3891 | 0.17853 | -0.1236 | 0.27466 | -0.027465 | 0.75073 | 123.111 | 0.48523 | 123.1293 | 123.3948 | 123.2025 | 123.1476 | 123.1064 | -123.3307 | -123.1796 | 122.8638 | 123.0331 | 53.7277 | 52.1439
970.8906 | 123.1842 | -56.4835 | 66.6183 | 0.012207 | 0.0019291 | 0.059445 | 0.069073 | 0.0030719 | -0.0033753 | -0.0038388 | -0.032867 | 0.005048 | 0.068539 | 0.066883 | -0.0068914 | 0.006539 | -0.00035666 | -2.7145 | 66.6321 | -56.7123 | 66.4124 | -55.9708 | -56.7215 | -1.3458 | -4.3076 | 66.6275 | -56.5704 | 66.568 | -56.0761 | -56.5933 | -56.3049 | -0.22888 | 0.013733 | -0.20599 | 0.5127 | 55.1376 | -0.23804 | 55.3665 | -0.009156 | -0.086976 | 0.009155 | -0.050354 | 0.40741 | 0.17853 | -0.10986 | 0.2655 | -0.022888 | 0.74158 | 123.1247 | 0.49439 | 123.1384 | 123.3444 | 123.1979 | 123.1155 | 123.111 | -123.3307 | -123.1888 | 122.8958 | 123.0515 | 53.7689 | 52.1759
971.8594 | 123.2437 | -56.5201 | 66.5543 | 0.0045776 | 0.0021427 | 0.063931 | 0.071423 | -0.0014143 | -0.0018799 | -0.005975 | -0.066437 | 0.005048 | 0.067044 | 0.067311 | -0.0058234 | 0.0071798 | -0.0020657 | -2.6917 | 66.5955 | -56.7398 | 66.4169 | -55.957 | -56.749 | -1.3412 | -4.2252 | 66.5909 | -56.6162 | 66.5634 | -56.0944 | -56.6025 | -56.3049 | -0.21973 | 0.041199 | -0.13733 | 0.56305 | 55.1788 | -0.22888 | 55.3986 | -0.009155 | -0.09613 | 0.036621 | 0.009156 | 0.42572 | 0.21515 | -0.082397 | 0.31128 | 0.013733 | 0.78278 | 123.1567 | 0.52185 | 123.1796 | 123.3353 | 123.2071 | 123.1155 | 123.111 | -123.2941 | -123.1705 | 122.937 | 123.0835 | 53.8284 | 52.2949
972.9062 | 123.175 | -56.5704 | 66.4948 | -0.071716 | 0.0019291 | 0.06329 | 0.069286 | 0.0045673 | -0.0023071 | -0.00020717 | -0.084747 | 0.0035526 | 0.070675 | 0.063679 | -0.0058234 | 0.0054708 | 0.0017795 | -2.7969 | 66.5359 | -56.8176 | 66.2796 | -56.1172 | -56.9 | -1.3916 | -4.3808 | 66.5131 | -56.6986 | 66.4444 | -56.2134 | -56.7398 | -56.4148 | -0.24719 | 0.041199 | -0.21515 | 0.45319 | 55.1788 | -0.32959 | 55.426 | -0.082397 | -0.12817 | 0.018311 | -0.050354 | 0.35706 | 0.15564 | -0.16937 | 0.28381 | -0.041199 | 0.70038 | 123.0972 | 0.48523 | 123.143 | 123.3536 | 123.2117 | 123.1064 | 123.0835 | -123.3124 | -123.1934 | 122.85 | 123.0148 | 53.7735 | 52.1896
973.8594 | 123.1979 | -56.6116 | 66.4902 | -0.01831 | 0.0023563 | 0.060513 | 0.0695 | 0.0017901 | -0.0025207 | 6.432e-06 | -0.023712 | 0.0039798 | 0.069393 | 0.06667 | -0.0066778 | 0.0067526 | -0.00099766 | -2.7969 | 66.5359 | -56.8268 | 66.2704 | -56.0898 | -56.8405 | -1.2817 | -4.335 | 66.4993 | -56.6757 | 66.449 | -56.1905 | -56.7169 | -56.4239 | -0.21515 | 0.045777 | -0.21973 | 0.52185 | 55.3299 | -0.22888 | 55.545 | -0.013733 | -0.064087 | 0.009156 | -0.041198 | 0.42114 | 0.18768 | -0.10529 | 0.25177 | -0.041199 | 0.737 | 123.0972 | 0.48523 | 123.1247 | 123.3627 | 123.175 | 123.1476 | 123.111 | -123.317 | -123.1659 | 122.8821 | 123.0606 | 53.8147 | 52.2766
974.8906 | 123.1659 | -56.6666 | 66.4215 | -0.071716 | 0.0036381 | 0.063931 | 0.069286 | 0.0028583 | -0.0033753 | 0.00086083 | 0.10141 | 0.0037662 | 0.068539 | 0.067311 | -0.008814 | 0.0076072 | -0.00078406 | -2.8198 | 66.4536 | -56.8909 | 66.2338 | -56.1035 | -57.4448 | -1.5701 | -4.5181 | 66.449 | -56.7261 | 66.3757 | -56.2729 | -56.8314 | -56.488 | -0.2243 | 0.032043 | -0.18768 | 0.56305 | 55.0964 | -0.7782 | 55.3207 | -0.55389 | -0.059509 | 0.027466 | -0.045777 | 0.39368 | 0.17853 | -0.16479 | 0.23804 | -0.10529 | 0.78735 | 123.1247 | 0.45319 | 123.1018 | 123.3444 | 123.175 | 123.1201 | 123.1155 | -123.3124 | -123.1476 | 122.9004 | 123.0423 | 53.8467 | 52.1484
975.8594 | 123.1842 | -56.694 | 66.3986 | -0.056457 | 0.0017155 | 0.059872 | 0.068432 | -0.0024823 | -0.0038025 | -0.002557 | -0.02066 | 0.0022708 | 0.070034 | 0.063038 | -0.0051824 | 0.0052572 | -0.00014306 | -2.8427 | 66.4581 | -56.8954 | 66.2018 | -56.1584 | -56.9 | -1.2726 | -4.3488 | 66.4261 | -56.7673 | 66.3666 | -56.2912 | -56.7856 | -56.4972 | -0.20142 | 0.059509 | -0.19684 | 0.53558 | 55.4214 | -0.20599 | 55.6229 | -0.004577 | -0.073242 | 0.027465 | -0.032044 | 0.40283 | 0.19684 | -0.091552 | 0.27008 | -0.01831 | 0.737 | 123.0972 | 0.47607 | 123.1339 | 123.3536 | 123.1934 | 123.1522 | 123.1201 | -123.2941 | -123.1659 | 122.8958 | 123.0606 | 53.8513 | 52.3453
976.9219 | 123.3078 | -56.6666 | 66.3254 | -0.064087 | 0.0017155 | 0.061581 | 0.06715 | -0.0076093 | -0.0044433 | -0.002557 | 0.025116 | 0.0024844 | 0.067471 | 0.058338 | -0.0073188 | 0.0063254 | -0.0018521 | -2.8381 | 66.3757 | -56.9412 | 66.1331 | -56.3232 | -56.7032 | -1.2726 | -4.3076 | 66.3025 | -56.7764 | 66.4215 | -56.1768 | -56.6986 | -56.4148 | -0.27466 | 0.050354 | -0.19226 | 0.34332 | 55.394 | -0.036621 | 55.6686 | 0.23804 | -0.10986 | -0.022888 | 0.096131 | 0.48981 | 0.25177 | -0.032043 | 0.36163 | 0.07782 | 0.61798 | 123.0743 | 0.59967 | 123.1979 | 123.317 | 123.0789 | 123.0423 | 122.9691 | -123.2666 | -123.1018 | 122.7997 | 123.0881 | 53.8284 | 52.359
977.8594 | 123.175 | -56.7764 | 66.362 | -0.010681 | 6.46e-06 | 0.060299 | 0.0695 | -0.0014143 | -0.0025207 | -0.0023434 | -0.023712 | 0.002698 | 0.06918 | 0.064961 | -0.0075324 | 0.0050436 | -0.0022793 | -2.9068 | 66.3895 | -56.9824 | 66.1423 | -56.2317 | -56.9595 | -1.2039 | -4.3579 | 66.3483 | -56.8314 | 66.2933 | -56.3553 | -56.8542 | -56.5567 | -0.20599 | 0.027465 | -0.21973 | 0.54474 | 55.5725 | -0.18311 | 55.7785 | 0.022888 | -0.054932 | -0.013733 | -0.068665 | 0.42114 | 0.21973 | -0.07782 | 0.27466 | -0.022888 | 0.75073 | 123.1247 | 0.47607 | 123.1247 | 123.3719 | 123.1796 | 123.1659 | 123.1247 | -123.3444 | -123.1934 | 122.9187 | 123.0698 | 53.8696 | 52.4185
978.9062 | 123.2941 | -56.7764 | 66.2521 | -0.064087 | 0.0010745 | 0.061154 | 0.069073 | 8.1126e-05 | -0.00081187 | -0.0017026 | 0.019012 | 0.002698 | 0.067471 | 0.057057 | -0.008814 | 0.0054708 | -0.0029203 | -2.9068 | 66.3116 | -56.9778 | 66.1606 | -56.2317 | -56.9962 | -1.1765 | -4.3396 | 66.2704 | -56.8542 | 66.3254 | -56.3416 | -56.8451 | -56.5475 | -0.20142 | 0.05951 | -0.091553 | 0.54474 | 55.6 | -0.21973 | 55.8014 | -0.018311 | -0.07782 | 0.018311 | 0.073242 | 0.43488 | 0.22888 | -0.068665 | 0.3067 | 0.009155 | 0.74615 | 123.1384 | 0.5127 | 123.1796 | 123.2895 | 123.1247 | 123.0881 | 123.0469 | -123.23 | -123.1064 | 122.937 | 123.1018 | 53.8696 | 52.4368
979.8594 | 123.1796 | -56.7856 | 66.2979 | -0.02594 | 0.00086086 | 0.062222 | 0.069286 | -0.0024823 | -0.0012391 | -0.0038388 | -0.063385 | 0.002698 | 0.070248 | 0.070515 | -0.0086004 | 0.0063254 | -0.00078406 | -2.9343 | 66.3391 | -57.0465 | 66.0873 | -56.3095 | -57.0511 | -1.1719 | -4.4128 | 66.2933 | -56.8863 | 66.2338 | -56.4056 | -56.9275 | -56.6116 | -0.26093 | 0.041198 | -0.21057 | 0.47607 | 55.6137 | -0.2655 | 55.8746 | -0.004577 | -0.10071 | -0.004578 | -0.064087 | 0.37994 | 0.17395 | -0.14191 | 0.27466 | -0.041198 | 0.737 | 123.1338 | 0.48065 | 123.1201 | 123.3856 | 123.1796 | 123.1247 | 123.0789 | -123.3444 | -123.1842 | 122.8729 | 123.0194 | 53.8513 | 52.3727
980.9062 | 123.1979 | -56.8542 | 66.2155 | -0.079346 | 0.0017155 | 0.063717 | 0.070141 | 0.0015765 | -0.00081187 | -0.0023434 | -0.075592 | 0.0041934 | 0.06918 | 0.06667 | -0.007746 | 0.0063254 | -0.0031339 | -2.9709 | 66.2613 | -57.1152 | 66.0004 | -56.3873 | -57.1609 | -1.2268 | -4.541 | 66.2201 | -56.9504 | 66.2064 | -56.488 | -56.9962 | -56.6757 | -0.26093 | 0.045777 | -0.21515 | 0.46692 | 55.6274 | -0.3067 | 55.8884 | -0.045777 | -0.09613 | 0.004578 | -0.009155 | 0.36621 | 0.17853 | -0.14191 | 0.27466 | -0.045777 | 0.72784 | 123.1155 | 0.46234 | 123.1567 | 123.3765 | 123.1705 | 123.1155 | 123.0743 | -123.3307 | -123.1659 | 122.8546 | 123.0606 | 53.8834 | 52.3132
981.875 | 123.317 | -56.8497 | 66.1743 | 0.035095 | 0.0032107 | 0.065213 | 0.068859 | 0.00072213 | -0.0025207 | -0.0038388 | 0.019012 | 0.00163 | 0.068753 | 0.063893 | -0.0081732 | 0.0044028 | -0.0022793 | -2.98 | 66.2018 | -57.0602 | 66.1377 | -56.2134 | -57.0099 | -0.99335 | -4.2984 | 66.188 | -56.9229 | 66.3162 | -56.3049 | -56.8268 | -56.5659 | -0.21057 | 0.027466 | -0.036621 | 0.63629 | 55.8563 | -0.16022 | 56.0669 | 0.050354 | -0.073243 | 0.013733 | 0.14191 | 0.54474 | 0.28381 | 0.022888 | 0.35706 | 0.096131 | 0.84686 | 123.1979 | 0.61798 | 123.2391 | 123.262 | 123.111 | 123.0515 | 123.0377 | -123.2346 | -123.0972 | 122.9874 | 123.1659 | 53.8696 | 52.5513
982.9062 | 123.1934 | -56.9046 | 66.1469 | -0.056457 | 0.0034245 | 0.063076 | 0.069073 | 0.0028583 | 0.00089713 | 0.0025698 | -0.081696 | 0.0037662 | 0.067898 | 0.062611 | -0.007746 | 0.0078208 | -0.0031339 | -3.0304 | 66.1926 | -57.1472 | 65.9454 | -56.4651 | -57.2113 | -1.2085 | -4.5502 | 66.156 | -57.0053 | 66.1377 | -56.5796 | -57.0602 | -56.7352 | -0.24262 | 0.045776 | -0.20142 | 0.43945 | 55.6961 | -0.3067 | 55.9387 | -0.064087 | -0.10071 | 0.009155 | -0.009156 | 0.32501 | 0.16937 | -0.15564 | 0.27008 | -0.054932 | 0.68207 | 123.0927 | 0.42572 | 123.143 | 123.3398 | 123.1613 | 123.0972 | 123.0606 | -123.2941 | -123.1522 | 122.85 | 123.0423 | 53.8742 | 52.3544
983.8594 | 123.2254 | -56.9183 | 66.1652 | -0.033569 | 0.0019291 | 0.062863 | 0.072491 | -0.0012005 | 0.0011109 | 0.00086083 | -0.075592 | 0.0022708 | 0.068325 | 0.06667 | -0.0081732 | 0.0069662 | 0.0019931 | -3.0396 | 66.188 | -57.1335 | 66.0416 | -56.3507 | -57.1426 | -1.0849 | -4.4037 | 66.1652 | -56.9916 | 66.1652 | -56.488 | -57.0053 | -56.6986 | -0.21515 | 0.022888 | -0.1236 | 0.56763 | 55.8334 | -0.2243 | 56.0486 | -0.009155 | -0.073242 | 0 | 0 | 0.4303 | 0.21973 | -0.086975 | 0.29297 | -0.013733 | 0.78278 | 123.175 | 0.50354 | 123.1567 | 123.3215 | 123.1567 | 123.1064 | 123.0835 | -123.2986 | -123.1567 | 122.9599 | 123.0835 | 53.8788 | 52.5146
984.9062 | 123.2208 | -56.9733 | 66.1148 | -0.033569 | 0.0032107 | 0.06329 | 0.069286 | 0.0011493 | 0.00025633 | -0.003198 | -0.066437 | 0.002698 | 0.070675 | 0.062184 | -0.0066778 | 0.0067526 | -0.0048429 | -2.9892 | 66.1606 | -57.1793 | 65.9729 | -56.3965 | -57.1609 | -1.0757 | -4.4403 | 66.1377 | -57.0328 | 66.1377 | -56.5201 | -57.0236 | -56.7352 | -0.20599 | 0.045776 | -0.14191 | 0.57678 | 55.8975 | -0.18768 | 56.1035 | 0.01831 | -0.059509 | 0.022888 | 0.022888 | 0.45319 | 0.23804 | -0.050354 | 0.29755 | 0.009155 | 0.78278 | 123.1522 | 0.5127 | 123.1705 | 123.3398 | 123.1705 | 123.1338 | 123.111 | -123.2941 | -123.1476 | 122.9462 | 123.111 | 53.9841 | 52.533
985.8594 | 123.2254 | -56.9733 | 66.1011 | -0.041199 | 0.0015019 | 0.061154 | 0.068218 | -0.0031231 | -0.0038025 | -0.0034116 | -0.045074 | 0.0041934 | 0.067684 | 0.063893 | -0.0064642 | 0.0054708 | -0.00099766 | -3.0258 | 66.1606 | -57.2067 | 65.8997 | -56.4835 | -57.2067 | -1.062 | -4.509 | 66.1194 | -57.0648 | 66.0828 | -56.5704 | -57.0786 | -56.7902 | -0.23346 | 0.059509 | -0.20142 | 0.48981 | 55.9113 | -0.23346 | 56.1447 | 0 | -0.091552 | 0.018311 | -0.01831 | 0.40283 | 0.18311 | -0.10529 | 0.27466 | -0.013733 | 0.72327 | 123.1064 | 0.49438 | 123.1476 | 123.3673 | 123.1842 | 123.1338 | 123.0927 | -123.3078 | -123.1659 | 122.8729 | 123.056 | 53.9474 | 52.4643
986.9219 | 123.262 | -56.9687 | 66.0553 | -0.086975 | 0.0051333 | 0.064145 | 0.067364 | 0.0028583 | -0.0027345 | -0.0019162 | 0.03122 | 0.0031254 | 0.068966 | 0.068165 | -0.007105 | 0.0061118 | -0.00014306 | -2.9343 | 66.0965 | -57.193 | 66.0049 | -56.3736 | -57.1289 | -0.93384 | -4.3396 | 66.0599 | -57.0648 | 66.1331 | -56.5109 | -57.0236 | -56.7352 | -0.2243 | 0.041199 | -0.050354 | 0.59509 | 56.0349 | -0.16022 | 56.2592 | 0.064087 | -0.09613 | 0.004577 | 0.07782 | 0.45776 | 0.23346 | -0.054932 | 0.32959 | 0.041198 | 0.8194 | 123.1979 | 0.55389 | 123.1979 | 123.2895 | 123.1247 | 123.0652 | 123.0286 | -123.2483 | -123.1201 | 122.9736 | 123.1018 | 54.0344 | 52.6291
987.8594 | 123.2162 | -57.0648 | 66.037 | -0.056457 | 0.0015019 | 0.061154 | 0.070568 | 0.0041399 | -0.0025207 | -0.00084817 | -0.069489 | 0.0035526 | 0.069821 | 0.064961 | -0.008814 | 0.0063254 | -0.0020657 | -2.98 | 66.1011 | -57.2479 | 65.9042 | -56.488 | -57.2388 | -0.98419 | -4.4083 | 66.0828 | -57.1335 | 66.069 | -56.6162 | -57.1106 | -56.8085 | -0.18311 | 0.064087 | -0.13275 | 0.57678 | 56.0806 | -0.17395 | 56.2637 | 0.009155 | -0.068665 | 0.045777 | 0.032044 | 0.44861 | 0.25635 | -0.045777 | 0.32501 | 0.022888 | 0.75989 | 123.1522 | 0.51727 | 123.2025 | 123.349 | 123.2162 | 123.1659 | 123.1476 | -123.2849 | -123.1705 | 122.9691 | 123.1338 | 54.0848 | 52.6566
988.9062 | 123.2208 | -57.0602 | 65.9775 | -0.13275 | 0.0021427 | 0.063504 | 0.068432 | -0.00034607 | -0.0012391 | -0.0023434 | -0.057281 | 0.0046206 | 0.070248 | 0.068165 | -0.0079596 | 0.0073936 | 0.0019931 | -3.0808 | 66.0324 | -57.3212 | 65.7898 | -56.5887 | -57.3669 | -1.0254 | -4.5273 | 66.0004 | -57.1564 | 65.9821 | -56.7032 | -57.2205 | -56.8817 | -0.26093 | 0.054932 | -0.18768 | 0.4715 | 56.0349 | -0.3067 | 56.2958 | -0.045776 | -0.09613 | 0.022888 | 0.004578 | 0.35706 | 0.17853 | -0.16022 | 0.27466 | -0.064087 | 0.73242 | 123.111 | 0.45319 | 123.1384 | 123.3536 | 123.1567 | 123.0927 | 123.0606 | -123.2986 | -123.1338 | 122.85 | 123.0423 | 53.9795 | 52.533
989.8594 | 123.2162 | -57.0877 | 66.0095 | -0.071716 | 0.0032107 | 0.061581 | 0.068218 | -0.0018415 | 0.0011109 | -0.0010618 | -0.02066 | 0.0041934 | 0.068753 | 0.067738 | -0.008814 | 0.0063254 | -0.0046293 | -3.0304 | 66.069 | -57.28 | 65.8127 | -56.5842 | -57.3074 | -0.91553 | -4.4952 | 66.0507 | -57.1564 | 65.9683 | -56.6849 | -57.1838 | -56.8771 | -0.19226 | 0.05951 | -0.19684 | 0.50354 | 56.1722 | -0.21973 | 56.3644 | -0.027466 | -0.068664 | 0.041199 | -0.041198 | 0.40283 | 0.21057 | -0.09613 | 0.27924 | -0.027466 | 0.6958 | 123.0927 | 0.4715 | 123.1247 | 123.349 | 123.2071 | 123.1567 | 123.1384 | -123.2895 | -123.1659 | 122.9004 | 123.056 | 54.0573 | 52.5925
990.9062 | 123.2117 | -57.1198 | 65.9317 | -0.010681 | 0.0012881 | 0.064358 | 0.0695 | 0.0062763 | 4.273e-05 | -0.0010618 | -0.060333 | 0.0039798 | 0.067898 | 0.062397 | -0.0058234 | 0.0056846 | 0.0049837 | -3.0716 | 65.9821 | -57.3669 | 65.7532 | -56.6574 | -57.4219 | -0.96588 | -4.5547 | 65.95 | -57.2067 | 65.9454 | -56.7673 | -57.2754 | -56.9183 | -0.24719 | 0.050354 | -0.17853 | 0.46234 | 56.1539 | -0.30212 | 56.4011 | -0.054932 | -0.086975 | 0.01831 | 0.013733 | 0.35248 | 0.20142 | -0.15564 | 0.28839 | -0.068665 | 0.70953 | 123.1201 | 0.43945 | 123.1522 | 123.349 | 123.1567 | 123.1018 | 123.0698 | -123.2986 | -123.1384 | 122.8729 | 123.0652 | 54.0482 | 52.565
991.875 | 123.2071 | -57.1518 | 65.9821 | -0.048828 | 0.0023563 | 0.060727 | 0.068859 | 0.0013629 | -0.0031617 | -0.00020717 | -0.014557 | 0.0024844 | 0.070034 | 0.060261 | -0.0068914 | 0.0067526 | -0.0012113 | -3.0487 | 66.0187 | -57.3349 | 65.7715 | -56.6345 | -57.3532 | -0.87891 | -4.5044 | 65.9866 | -57.2021 | 65.9363 | -56.7215 | -57.2205 | -56.9275 | -0.18311 | 0.036621 | -0.21057 | 0.51727 | 56.2729 | -0.20142 | 56.456 | -0.01831 | -0.050354 | 0.004577 | -0.045777 | 0.4303 | 0.2243 | -0.068665 | 0.27466 | -0.018311 | 0.70038 | 123.1064 | 0.48065 | 123.1384 | 123.3536 | 123.1888 | 123.1705 | 123.1384 | -123.317 | -123.1842 | 122.9233 | 123.0881 | 54.1031 | 52.6474
992.9062 | 123.2437 | -57.1701 | 65.8997 | -0.12512 | -0.00020714 | 0.064785 | 0.067577 | 0.0026447 | -0.00081187 | -0.0053342 | 0.0098572 | 0.003339 | 0.073025 | 0.061115 | -0.0079596 | 0.0050436 | 0.0015659 | -3.0441 | 65.918 | -57.3441 | 65.7898 | -56.5887 | -57.3669 | -0.84686 | -4.1748 | 65.8859 | -57.225 | 65.9866 | -56.781 | -57.2296 | -56.9183 | -0.17395 | 0.018311 | -0.10986 | 0.58136 | 56.3232 | -0.19684 | 56.4972 | -0.022888 | -0.054932 | -0.013733 | 0.086975 | 0.3891 | 0.25177 | -0.059509 | 0.3067 | -0.004577 | 0.75531 | 123.1338 | 0.44403 | 123.2117 | 123.262 | 123.111 | 123.0881 | 123.056 | -123.2437 | -123.1247 | 122.9599 | 123.1567 | 54.126 | 52.9953
993.8594 | 123.2208 | -57.1747 | 65.8859 | 0.0045776 | 0.0027835 | 0.063504 | 0.069286 | 8.1126e-05 | -0.00017087 | -0.0017026 | -0.051178 | 0.005048 | 0.068966 | 0.063679 | -0.0090278 | 0.0061118 | 0.00071134 | -3.067 | 65.9775 | -57.3853 | 65.7257 | -56.6711 | -57.3944 | -0.82855 | -4.5044 | 65.9546 | -57.2433 | 65.918 | -56.7444 | -57.2296 | -56.9504 | -0.21057 | 0.091553 | -0.16022 | 0.50354 | 56.3461 | -0.21973 | 56.5567 | -0.009155 | -0.068664 | 0.068665 | 0.032044 | 0.4303 | 0.22431 | -0.054931 | 0.29297 | 0.013733 | 0.71411 | 123.111 | 0.49896 | 123.1613 | 123.3627 | 123.1979 | 123.1522 | 123.1293 | -123.2712 | -123.1293 | 122.9004 | 123.0927 | 54.1077 | 52.6703
994.9062 | 123.2986 | -57.1976 | 65.8218 | -0.071716 | 0.0023563 | 0.062649 | 0.068432 | 0.00093573 | -0.00081187 | -0.004907 | 0.0068054 | 0.00098899 | 0.068325 | 0.05193 | -0.0092414 | 0.0044028 | -0.0029203 | -3.0853 | 65.8768 | -57.3944 | 65.7623 | -56.6071 | -57.4036 | -0.78735 | -4.4586 | 65.8539 | -57.2433 | 65.8081 | -56.6391 | -57.3669 | -57.0328 | -0.19684 | 0.054932 | -0.059509 | 0.59052 | 56.4102 | -0.20599 | 56.6071 | -0.009155 | -0.045776 | 0.032044 | -0.013733 | 0.55847 | 0.1648 | -0.16937 | 0.21057 | -0.1236 | 0.78735 | 123.1567 | 0.60425 | 123.0515 | 123.2712 | 123.0972 | 123.0743 | 123.0515 | -123.2162 | -123.0652 | 122.9599 | 123.0057 | 54.1122 | 52.739
995.8594 | 123.2071 | -57.2021 | 65.863 | -0.02594 | 0.0010745 | 0.060086 | 0.067791 | 0.00093573 | 0.00068353 | -0.0010618 | -0.10306 | 0.0024844 | 0.069821 | 0.063465 | -0.0092414 | 0.008248 | 0.00049774 | -3.1036 | 65.9042 | -57.4265 | 65.7394 | -56.6711 | -57.4081 | -0.78735 | -4.4769 | 65.8859 | -57.28 | 65.8813 | -56.8222 | -57.312 | -56.987 | -0.22431 | 0.041199 | -0.1236 | 0.53101 | 56.4148 | -0.20599 | 56.6391 | 0.018311 | -0.07782 | 0.022888 | 0.018311 | 0.37994 | 0.21515 | -0.10986 | 0.29297 | -0.032044 | 0.75531 | 123.1659 | 0.45776 | 123.1613 | 123.3307 | 123.1659 | 123.1064 | 123.0881 | -123.2895 | -123.143 | 122.9416 | 123.0835 | 54.0985 | 52.7252
996.9219 | 123.2941 | -57.2205 | 65.799 | -0.10986 | 0.00086086 | 0.063076 | 0.0695 | 0.0015765 | -0.0016663 | -0.0019162 | 0.052582 | 0.0048344 | 0.073025 | 0.061756 | -0.0092414 | 0.0050436 | 0.00071134 | -3.2227 | 65.8173 | -57.4081 | 65.7257 | -56.6711 | -57.4356 | -0.75073 | -4.6097 | 65.8127 | -57.3074 | 65.8493 | -56.8222 | -57.2662 | -56.9641 | -0.18768 | 0.018311 | -0.073242 | 0.54932 | 56.4697 | -0.21515 | 56.6574 | -0.027466 | -0.086975 | 0.013733 | 0.050354 | 0.39825 | 0.25635 | -0.045776 | 0.34332 | 0.041199 | 0.737 | 123.1338 | 0.48523 | 123.1567 | 123.2254 | 123.1201 | 123.0377 | 123.0331 | -123.2071 | -123.1064 | 122.9462 | 123.0698 | 53.9978 | 52.6108
997.8594 | 123.1979 | -57.2525 | 65.8585 | -0.041199 | 0.0015019 | 0.063504 | 0.070355 | 8.1126e-05 | -0.0012391 | 0.0012882 | -0.066437 | 0.004407 | 0.068325 | 0.061756 | -0.0083868 | 0.0071798 | -0.00078406 | -3.2227 | 65.8951 | -57.4677 | 65.6662 | -56.7444 | -57.4677 | -0.76446 | -4.541 | 65.8722 | -57.3212 | 65.8401 | -56.8405 | -57.3349 | -57.0236 | -0.21515 | 0.036622 | -0.19226 | 0.50812 | 56.488 | -0.21515 | 56.7032 | 0 | -0.068665 | 0.013733 | -0.01831 | 0.41199 | 0.22888 | -0.082398 | 0.29755 | -0.013733 | 0.72327 | 123.1338 | 0.48065 | 123.1613 | 123.3627 | 123.1934 | 123.1476 | 123.1247 | -123.3261 | -123.1796 | 122.9187 | 123.0927 | 54.0298 | 52.7115
998.9062 | 123.2162 | -57.2845 | 65.8539 | -0.02594 | 0.00043366 | 0.061154 | 0.069714 | 0.0028583 | -0.0012391 | -0.0010618 | -0.042023 | 0.003339 | 0.06448 | 0.065815 | -0.0062506 | 0.0061118 | 0.0022067 | -3.2501 | 65.8951 | -57.4677 | 65.6387 | -56.7764 | -57.4951 | -0.74616 | -4.5776 | 65.8539 | -57.3441 | 65.8035 | -56.8588 | -57.3669 | -57.0694 | -0.1831 | 0.041199 | -0.21515 | 0.50812 | 56.5384 | -0.21057 | 56.7215 | -0.027466 | -0.059509 | 0 | -0.050354 | 0.42572 | 0.21515 | -0.082397 | 0.27466 | -0.022888 | 0.69122 | 123.1064 | 0.48523 | 123.1476 | 123.3627 | 123.1979 | 123.1796 | 123.1384 | -123.3215 | -123.1979 | 122.9233 | 123.0881 | 54.0344 | 52.7069
999.8594 | 123.2483 | -57.28 | 65.8127 | -0.048828 | 0.0017155 | 0.061581 | 0.069927 | 0.0056353 | -0.0023071 | -0.00042077 | -0.069489 | 0.0041934 | 0.06918 | 0.06667 | -0.0075324 | 0.0069662 | 0.00049774 | -3.2227 | 65.8539 | -57.4997 | 65.6616 | -56.7352 | -57.4905 | -0.70953 | -4.4998 | 65.8173 | -57.3257 | 65.8218 | -56.868 | -57.3624 | -57.0374 | -0.21973 | 0.041199 | -0.15106 | 0.54474 | 56.5704 | -0.21057 | 56.7902 | 0.009155 | -0.045777 | 0.004578 | 0.009155 | 0.41199 | 0.24261 | -0.082398 | 0.28839 | -0.036621 | 0.76447 | 123.1613 | 0.45776 | 123.1476 | 123.3536 | 123.143 | 123.1338 | 123.0972 | -123.3124 | -123.1384 | 122.9416 | 123.1018 | 54.0573 | 52.7802
1000.9062 | 123.1613 | -57.3166 | 65.7578 | -0.10986 | 0.0034245 | 0.063931 | 0.069073 | 0.00072213 | -0.0016663 | -0.0019162 | -0.066437 | 0.0035526 | 0.069393 | 0.070728 | -0.0083868 | 0.0058982 | -0.0014249 | -3.3096 | 65.8173 | -57.5729 | 65.538 | -56.8863 | -57.637 | -0.80109 | -4.7058 | 65.7578 | -57.4173 | 65.7211 | -56.9733 | -57.4722 | -57.1381 | -0.25635 | 0.05951 | -0.21973 | 0.4303 | 56.5155 | -0.32043 | 56.7719 | -0.064087 | -0.10071 | 0 | -0.036621 | 0.34332 | 0.17853 | -0.15564 | 0.27923 | -0.054932 | 0.68665 | 123.111 | 0.44403 | 123.1384 | 123.3902 | 123.175 | 123.1338 | 123.0743 | -123.3307 | -123.175 | 122.8546 | 123.0377 | 54.007 | 52.6108
1001.8594 | 123.1293 | -57.3166 | 65.7623 | -0.11749 | 0.0023563 | 0.064785 | 0.068432 | 0.0017901 | 0.00046993 | -0.0053342 | -0.07254 | 0.0041934 | 0.067044 | 0.071797 | -0.0092414 | 0.0041892 | 0.00071134 | -3.3096 | 65.8035 | -57.5638 | 65.5701 | -56.868 | -57.605 | -0.737 | -4.6738 | 65.7623 | -57.4127 | 65.863 | -57.1014 | -57.3257 | -57.0602 | -0.24719 | 0.041199 | -0.19226 | 0.44861 | 56.5796 | -0.28839 | 56.8268 | -0.041198 | -0.096131 | 0 | 0.10071 | 0.21515 | 0.25635 | -0.009156 | 0.35248 | 0.086975 | 0.6958 | 123.1339 | 0.31128 | 123.2758 | 123.3673 | 123.175 | 123.1201 | 123.0789 | -123.3261 | -123.175 | 122.8867 | 123.1796 | 54.007 | 52.6428
1002.9062 | 123.1888 | -57.3624 | 65.7166 | -0.079346 | 0.0019291 | 0.064572 | 0.070355 | 0.0013629 | 0.0017517 | -0.0040524 | -0.057281 | 0.005048 | 0.072384 | 0.06902 | -0.0073188 | 0.0080344 | -0.0024931 | -3.3508 | 65.7761 | -57.6004 | 65.5014 | -56.9092 | -57.6599 | -0.75989 | -4.7287 | 65.7303 | -57.431 | 65.6799 | -57.0053 | -57.5134 | -57.1701 | -0.23804 | 0.059509 | -0.21515 | 0.45319 | 56.6025 | -0.29755 | 56.8405 | -0.059509 | -0.068664 | 0.013733 | -0.036621 | 0.35706 | 0.19226 | -0.15106 | 0.26093 | -0.082398 | 0.69122 | 123.1018 | 0.42572 | 123.111 | 123.3765 | 123.1613 | 123.1384 | 123.0927 | -123.317 | -123.1476 | 122.8638 | 123.0423 | 54.0115 | 52.6337
1003.875 | 123.2712 | -57.3395 | 65.6891 | -0.048828 | 0.0015019 | 0.062436 | 0.06715 | -0.0024823 | -0.0014527 | -0.003198 | 0.052582 | 0.0014164 | 0.068325 | 0.057697 | -0.0053962 | 0.0050436 | -0.0027067 | -3.3234 | 65.744 | -57.5592 | 65.5792 | -56.813 | -57.5409 | -0.60425 | -4.6234 | 65.6891 | -57.4265 | 65.7669 | -56.9092 | -57.3669 | -57.0786 | -0.21973 | 0.054932 | -0.10986 | 0.52643 | 56.7352 | -0.20142 | 56.955 | 0.01831 | -0.086975 | 0 | 0.07782 | 0.4303 | 0.26093 | -0.027465 | 0.3479 | 0.05951 | 0.74616 | 123.1384 | 0.51727 | 123.1934 | 123.3032 | 123.1155 | 123.0835 | 123.0286 | -123.2483 | -123.1155 | 122.9187 | 123.1064 | 54.0161 | 52.7161
1004.9062 | 123.2117 | -57.4036 | 65.7028 | -0.10223 | 0.0021427 | 0.064785 | 0.070995 | -0.00098687 | 0.00089713 | -0.0023434 | -0.069489 | 0.0046206 | 0.07217 | 0.068379 | -0.01095 | 0.0078208 | -0.0029203 | -3.3737 | 65.7394 | -57.6187 | 65.506 | -56.9229 | -57.6553 | -0.72327 | -5.1544 | 65.6433 | -57.5089 | 65.6158 | -56.9733 | -57.55 | -57.225 | -0.21515 | 0.036621 | -0.19684 | 0.48065 | 56.6803 | -0.25177 | 56.8954 | -0.036621 | -0.10529 | -0.059509 | -0.086975 | 0.4303 | 0.17853 | -0.14648 | 0.28381 | -0.041199 | 0.6958 | 123.1247 | 0.53558 | 123.1247 | 123.3582 | 123.1522 | 123.143 | 123.0469 | -123.3215 | -123.2117 | 122.9095 | 123.0194 | 54.0298 | 52.2491
1005.8594 | 123.1842 | -57.4127 | 65.6891 | -0.0030519 | 0.00086086 | 0.063076 | 0.069714 | 0.0011493 | 0.00089713 | -0.0034116 | -0.035919 | 0.0031254 | 0.068753 | 0.067311 | -0.0096686 | 0.0073936 | 0.00049774 | -3.3966 | 65.7394 | -57.6096 | 65.4922 | -56.9321 | -57.6233 | -0.63171 | -4.7516 | 65.712 | -57.4905 | 65.6616 | -57.0145 | -57.5043 | -57.193 | -0.19684 | 0.050354 | -0.19684 | 0.48065 | 56.781 | -0.21057 | 56.9778 | -0.013733 | -0.07782 | 0.022888 | -0.027466 | 0.39825 | 0.21973 | -0.091552 | 0.29755 | -0.013732 | 0.67749 | 123.1018 | 0.47608 | 123.1522 | 123.349 | 123.2025 | 123.1522 | 123.1247 | -123.2986 | -123.1796 | 122.905 | 123.0743 | 54.0161 | 52.6611
1006.9219 | 123.3078 | -57.3807 | 65.6342 | -0.071716 | 0.0021427 | 0.061367 | 0.066937 | 8.1126e-05 | -0.00081187 | -0.003198 | 0.034271 | 0.002698 | 0.066189 | 0.060475 | -0.0083868 | 0.003121 | -0.0016385 | -3.3691 | 65.6616 | -57.6004 | 65.6021 | -56.7856 | -57.5409 | -0.53101 | -4.6143 | 65.6342 | -57.4539 | 65.7349 | -56.9092 | -57.399 | -57.1152 | -0.21973 | 0.027466 | -0.032043 | 0.59509 | 56.8497 | -0.16022 | 57.0694 | 0.059509 | -0.073242 | 0 | 0.10071 | 0.4715 | 0.2655 | -0.018311 | 0.33875 | 0.054931 | 0.81482 | 123.2025 | 0.54474 | 123.1888 | 123.262 | 123.0881 | 123.0423 | 123.0148 | -123.2346 | -123.0881 | 122.9828 | 123.1155 | 54.0115 | 52.7664
1007.8594 | 123.3902 | -57.4493 | 65.6982 | -0.056457 | 0.0023563 | 0.064145 | 0.069714 | 0.0015765 | -0.0014527 | 0.00086083 | -0.02066 | 0.0041934 | 0.068325 | 0.067951 | -0.0081732 | 0.0071798 | -0.0027067 | -3.4378 | 65.6799 | -57.6736 | 65.4556 | -56.9595 | -57.6553 | -0.61798 | -4.8935 | 65.657 | -57.5089 | 65.6342 | -57.0465 | -57.7377 | -57.2067 | -0.2243 | -0.01831 | -0.24261 | 0.48981 | 56.8314 | -0.20599 | 57.0557 | 0.018311 | -0.059509 | -0.041199 | -0.064087 | 0.40283 | 0.24261 | -0.28839 | 0.30212 | -0.22888 | 0.71411 | 123.1293 | 0.46234 | 123.143 | 123.3536 | 123.1659 | 123.1293 | 123.1064 | -123.3719 | -123.2071 | 122.905 | 123.0835 | 54.0115 | 52.5558
1008.9062 | 123.3124 | -57.4127 | 65.5975 | -0.056457 | 0.0021427 | 0.062008 | 0.068859 | 0.0017901 | -0.0012391 | -0.0027708 | 0.037323 | 0.0041934 | 0.068325 | 0.062824 | -0.007746 | 0.0052572 | 7.0538e-05 | -3.3737 | 65.6204 | -57.6324 | 65.5655 | -56.8176 | -57.5729 | -0.48523 | -4.747 | 65.5838 | -57.4814 | 65.6937 | -56.9687 | -57.431 | -57.1472 | -0.21973 | 0.022888 | -0.032043 | 0.59509 | 56.9275 | -0.16022 | 57.1472 | 0.059509 | -0.068664 | -0.013733 | 0.096131 | 0.44403 | 0.2655 | -0.01831 | 0.33417 | 0.050354 | 0.81482 | 123.1979 | 0.5127 | 123.175 | 123.2529 | 123.0652 | 123.0331 | 122.9965 | -123.23 | -123.0789 | 122.9782 | 123.1064 | 54.039 | 52.6657
1009.8594 | 123.2483 | -57.4677 | 65.6158 | -0.071716 | 0.0019291 | 0.060299 | 0.070782 | -0.0012005 | -0.0014527 | -0.0019162 | -0.057281 | 0.004407 | 0.070248 | 0.067738 | -0.0066778 | 0.0069662 | -0.00014306 | -3.4424 | 65.6708 | -57.6965 | 65.4236 | -57.0099 | -57.7057 | -0.59509 | -4.9301 | 65.6342 | -57.5546 | 65.5884 | -57.0969 | -57.5684 | -57.2571 | -0.22888 | 0.054931 | -0.19226 | 0.45776 | 56.8726 | -0.23804 | 57.1014 | -0.009155 | -0.086975 | 0.01831 | -0.027466 | 0.37079 | 0.21057 | -0.10071 | 0.29755 | -0.013733 | 0.68665 | 123.1201 | 0.45776 | 123.143 | 123.3673 | 123.1888 | 123.1384 | 123.1018 | -123.3124 | -123.1705 | 122.8912 | 123.056 | 54.0253 | 52.5375
1010.8906 | 123.23 | -57.4905 | 65.5975 | -0.02594 | 0.0027835 | 0.061581 | 0.070355 | 0.0011493 | 0.00068353 | -0.0044796 | -0.051178 | 0.0029116 | 0.065975 | 0.070942 | -0.008814 | 0.0067526 | -0.0018521 | -3.4103 | 65.5975 | -57.7377 | 65.4373 | -56.9687 | -57.7103 | -0.5722 | -4.866 | 65.6067 | -57.5592 | 65.6067 | -57.0786 | -57.5821 | -57.2662 | -0.24719 | 0 | -0.16022 | 0.52185 | 56.9183 | -0.21973 | 57.1655 | 0.027466 | -0.068664 | 0.009155 | 0.009155 | 0.41199 | 0.22431 | -0.091552 | 0.29297 | -0.022888 | 0.76904 | 123.175 | 0.48065 | 123.1659 | 123.3353 | 123.1659 | 123.0881 | 123.0972 | -123.3353 | -123.1567 | 122.9279 | 123.0972 | 54.0802 | 52.6245
1011.875 | 123.2986 | -57.5272 | 65.4877 | -0.094604 | 0.0027835 | 0.063076 | 0.069286 | 0.0015765 | 4.273e-05 | 0.0015018 | -0.032867 | 0.00163 | 0.066616 | 0.065815 | -0.0062506 | 0.0067526 | 0.00071134 | -3.4515 | 65.5472 | -57.7515 | 65.4236 | -56.9824 | -57.6874 | -0.56305 | -4.9118 | 65.5106 | -57.6096 | 65.6296 | -57.0877 | -57.5638 | -57.2205 | -0.2243 | 0.059509 | -0.064087 | 0.54474 | 56.9641 | -0.16022 | 57.1884 | 0.064087 | -0.082397 | 0.022888 | 0.14191 | 0.43945 | 0.3067 | -0.036621 | 0.3891 | 0.045776 | 0.76904 | 123.175 | 0.52185 | 123.2391 | 123.2986 | 123.1201 | 123.0743 | 123.0377 | -123.2391 | -123.0972 | 122.9507 | 123.1567 | 54.0756 | 52.6154
1012.9062 | 123.2117 | -57.55 | 65.5106 | -0.10223 | 0.0010745 | 0.063076 | 0.070141 | 0.0049945 | 0.00068353 | -0.0021298 | -0.042023 | 0.0065432 | 0.06918 | 0.063465 | -0.0068914 | 0.0069662 | 0.00071134 | -3.4836 | 65.5563 | -57.7744 | 65.3229 | -57.1152 | -57.8384 | -0.62714 | -5.0308 | 65.5655 | -57.6324 | 65.5014 | -57.225 | -57.6874 | -57.3441 | -0.2243 | 0.045776 | -0.18768 | 0.43488 | 56.9229 | -0.28839 | 57.1472 | -0.064087 | -0.082397 | 0.054932 | -0.009155 | 0.32501 | 0.20599 | -0.13733 | 0.28839 | -0.054932 | 0.65918 | 123.0972 | 0.40741 | 123.1338 | 123.3307 | 123.1979 | 123.1064 | 123.1155 | -123.2849 | -123.143 | 122.8729 | 123.0515 | 54.0665 | 52.5192
1013.8594 | 123.262 | -57.5272 | 65.4831 | -0.056457 | -0.00084814 | 0.06329 | 0.067791 | 0.0028583 | -0.0044433 | -0.0010618 | 0.037323 | 0.00163 | 0.068325 | 0.064106 | -0.007746 | 0.00483 | -0.0014249 | -3.4424 | 65.5289 | -57.7377 | 65.3824 | -57.0419 | -57.7698 | -0.52643 | -4.9713 | 65.4922 | -57.6279 | 65.5334 | -57.1381 | -57.6096 | -57.3029 | -0.21057 | 0.045777 | -0.10071 | 0.48523 | 57.0007 | -0.24261 | 57.2113 | -0.032043 | -0.10071 | 0.009156 | 0.050354 | 0.3891 | 0.22431 | -0.082397 | 0.32501 | 0.018311 | 0.6958 | 123.1201 | 0.48981 | 123.1613 | 123.2666 | 123.1201 | 123.056 | 123.0194 | -123.2208 | -123.111 | 122.9095 | 123.0606 | 54.0848 | 52.5558
1014.9062 | 123.2346 | -57.5638 | 65.4785 | -0.14038 | 0.0019291 | 0.063076 | 0.071209 | 0.00093573 | -0.0038025 | -0.0036252 | -0.0023498 | 0.003339 | 0.071957 | 0.060688 | -0.007105 | 0.0058982 | -0.0022793 | -3.4332 | 65.5106 | -57.7744 | 65.3687 | -57.074 | -57.7972 | -0.51727 | -4.985 | 65.4922 | -57.6416 | 65.538 | -57.1701 | -57.6279 | -57.3212 | -0.21057 | 0.032043 | -0.10986 | 0.48981 | 57.0465 | -0.23346 | 57.2571 | -0.022888 | -0.07782 | 0.013733 | 0.059509 | 0.39368 | 0.24262 | -0.064087 | 0.32043 | 0.013733 | 0.70038 | 123.143 | 0.4715 | 123.1796 | 123.2849 | 123.1339 | 123.0743 | 123.056 | -123.2529 | -123.1201 | 122.9324 | 123.1018 | 54.1306 | 52.5787
1015.8594 | 123.3353 | -57.5684 | 65.4968 | -0.056457 | 0.0025699 | 0.063504 | 0.070568 | -0.0012005 | -0.0038025 | -0.001489 | -0.066437 | 0.0035526 | 0.067044 | 0.067311 | -0.0090278 | 0.00483 | -0.0031339 | -3.3966 | 65.5472 | -57.8064 | 65.3366 | -57.1152 | -57.7835 | -0.52643 | -5.0171 | 65.5472 | -57.6736 | 65.5609 | -57.4127 | -57.5867 | -57.1747 | -0.23804 | 0.050354 | -0.16022 | 0.45319 | 57.0419 | -0.21515 | 57.28 | 0.022888 | -0.10529 | 0.050354 | 0.064087 | 0.15564 | 0.39368 | -0.018311 | 0.49896 | 0.086975 | 0.69122 | 123.143 | 0.26093 | 123.2346 | 123.3536 | 123.2208 | 123.1155 | 123.1155 | -123.3032 | -123.1705 | 122.905 | 123.1293 | 54.1718 | 52.5513
1016.9219 | 123.3353 | -57.5455 | 65.4556 | -0.10986 | 0.0064151 | 0.061581 | 0.068432 | -0.0031231 | -0.0020935 | -0.003198 | 0.015961 | 0.0037662 | 0.068325 | 0.060261 | -0.008814 | 0.0056846 | -0.0016385 | -3.4287 | 65.4602 | -57.8339 | 65.4144 | -56.987 | -57.7377 | -0.42572 | -4.8706 | 65.4465 | -57.6279 | 65.5838 | -57.1014 | -57.5409 | -57.28 | -0.28839 | 0.004578 | -0.041198 | 0.55847 | 57.1198 | -0.19226 | 57.4081 | 0.09613 | -0.082398 | -0.009155 | 0.12817 | 0.44403 | 0.2655 | 0.004577 | 0.3479 | 0.086975 | 0.84686 | 123.2483 | 0.52643 | 123.2117 | 123.2941 | 123.0743 | 123.0057 | 122.9919 | -123.2895 | -123.0835 | 122.9599 | 123.1293 | 54.1168 | 52.6749
1017.8594 | 123.2346 | -57.6096 | 65.451 | -0.02594 | 0.00086086 | 0.06094 | 0.069714 | 0.0030719 | -0.00081187 | -0.0017026 | -0.057281 | 0.0046206 | 0.068325 | 0.070728 | -0.0081732 | 0.0050436 | -0.00057046 | -3.392 | 65.5243 | -57.8476 | 65.3 | -57.1564 | -57.8476 | -0.51727 | -5.0766 | 65.5197 | -57.6874 | 65.4694 | -57.2296 | -57.7057 | -57.399 | -0.23804 | 0.073242 | -0.15106 | 0.45319 | 57.0923 | -0.23804 | 57.3303 | 0 | -0.07782 | 0.068664 | 0.01831 | 0.37994 | 0.21057 | -0.09613 | 0.28839 | -0.01831 | 0.69122 | 123.1476 | 0.45776 | 123.1567 | 123.3719 | 123.2071 | 123.1338 | 123.1293 | -123.2986 | -123.1384 | 122.9095 | 123.0789 | 54.2175 | 52.533
1018.9062 | 123.2483 | -57.6233 | 65.3961 | -0.079346 | 0.0012881 | 0.062649 | 0.070141 | -0.0018415 | -0.0035889 | -0.0034116 | -0.078644 | 0.0031254 | 0.068325 | 0.070301 | -0.0073188 | 0.0071798 | 0.00049774 | -3.4195 | 65.4373 | -57.8934 | 65.2542 | -57.1976 | -57.9437 | -0.55389 | -5.1498 | 65.4327 | -57.7332 | 65.4648 | -57.3074 | -57.756 | -57.4173 | -0.27008 | 0.041199 | -0.14191 | 0.42572 | 57.0694 | -0.32043 | 57.3395 | -0.050354 | -0.10986 | 0.036621 | 0.068665 | 0.31586 | 0.20599 | -0.13275 | 0.31586 | -0.022888 | 0.6958 | 123.1476 | 0.42572 | 123.1979 | 123.3307 | 123.1659 | 123.0606 | 123.056 | -123.2895 | -123.1293 | 122.8775 | 123.0881 | 54.2038 | 52.4734
1019.8594 | 123.2208 | -57.6508 | 65.4373 | -0.048828 | 6.46e-06 | 0.063504 | 0.0695 | -0.00013247 | -0.0033753 | -0.0021298 | -0.045074 | 0.00163 | 0.069821 | 0.068379 | -0.0079596 | 0.0054708 | -0.00014306 | -3.3829 | 65.4922 | -57.8751 | 65.2405 | -57.1976 | -57.8888 | -0.50354 | -5.1636 | 65.4831 | -57.724 | 65.4327 | -57.2662 | -57.7423 | -57.4493 | -0.2243 | 0.054932 | -0.19684 | 0.45319 | 57.1472 | -0.23804 | 57.3715 | -0.013733 | -0.073242 | 0.045776 | -0.004578 | 0.38452 | 0.20142 | -0.091553 | 0.27466 | -0.018311 | 0.67749 | 123.1155 | 0.45776 | 123.1567 | 123.3673 | 123.2071 | 123.143 | 123.1338 | -123.3124 | -123.1613 | 122.8912 | 123.0835 | 54.2679 | 52.4872
1020.8906 | 123.2574 | -57.6553 | 65.3824 | -0.071716 | 0.0029971 | 0.062222 | 0.071636 | 0.0037127 | -0.0016663 | -0.002557 | -0.07254 | 0.0039798 | 0.069821 | 0.067311 | -0.0073188 | 0.0067526 | -0.0016385 | -3.3142 | 65.4694 | -57.8888 | 65.2771 | -57.1564 | -57.8842 | -0.47607 | -5.1086 | 65.419 | -57.7286 | 65.4282 | -57.28 | -57.7377 | -57.4585 | -0.23346 | 0.086975 | -0.10528 | 0.49896 | 57.1793 | -0.22888 | 57.4127 | 0.004578 | -0.073243 | 0.036621 | 0.045777 | 0.37537 | 0.19684 | -0.082398 | 0.27008 | -0.009155 | 0.73242 | 123.1659 | 0.44861 | 123.1567 | 123.3582 | 123.1476 | 123.1247 | 123.0743 | -123.2712 | -123.111 | 122.9324 | 123.0835 | 54.3411 | 52.5467
1021.875 | 123.2391 | -57.7103 | 65.3549 | -0.10986 | 0.00086086 | 0.06329 | 0.070995 | -0.00098687 | -0.0012391 | -0.002557 | -0.084747 | 0.0031254 | 0.069393 | 0.063038 | -0.0090278 | 0.0073936 | 0.0034885 | -3.4058 | 65.3732 | -57.9163 | 65.1901 | -57.2525 | -57.9803 | -0.56305 | -5.2551 | 65.3687 | -57.811 | 65.3961 | -57.3257 | -57.7972 | -57.4677 | -0.20599 | 0.018311 | -0.16479 | 0.45776 | 57.1472 | -0.27008 | 57.3532 | -0.064087 | -0.10071 | 0.013733 | 0.041199 | 0.38452 | 0.24262 | -0.086975 | 0.34332 | 0.013733 | 0.66376 | 123.1064 | 0.48523 | 123.2071 | 123.2895 | 123.1796 | 123.0835 | 123.0789 | -123.2712 | -123.1659 | 122.9004 | 123.1064 | 54.3045 | 52.4551
1022.9062 | 123.317 | -57.7057 | 65.3275 | -0.048828 | 0.0038517 | 0.063931 | 0.068005 | 0.0043537 | -0.0023071 | -0.0027708 | -0.066437 | 0.0037662 | 0.067684 | 0.061543 | -0.0090278 | 0.0058982 | -0.0035611 | -3.392 | 65.3732 | -57.9575 | 65.2084 | -57.2342 | -57.9758 | -0.70953 | -5.072 | 65.3458 | -57.8064 | 65.4419 | -57.3029 | -57.756 | -57.431 | -0.25177 | 0.045776 | -0.11902 | 0.4715 | 56.9962 | -0.27008 | 57.2479 | -0.018311 | -0.10071 | 0.01831 | 0.11444 | 0.40283 | 0.27466 | -0.050354 | 0.37537 | 0.050354 | 0.72327 | 123.1659 | 0.50354 | 123.2483 | 123.3307 | 123.1522 | 123.0789 | 123.0515 | -123.2849 | -123.1338 | 122.9141 | 123.1476 | 54.3137 | 52.6337
1023.8594 | 123.1888 | -57.7469 | 65.332 | -0.079346 | 0.0023563 | 0.062436 | 0.068646 | 0.0024311 | -0.0012391 | 0.0017154 | 0.052582 | 0.0056888 | 0.065975 | 0.065602 | -0.0096686 | 0.0086752 | -0.0033475 | -3.3783 | 65.4007 | -57.9758 | 65.1489 | -57.1152 | -58.6304 | -0.77362 | -5.4428 | 65.3778 | -57.7972 | 65.3 | -57.4173 | -57.9025 | -57.5546 | -0.22888 | 0.068665 | -0.1831 | 0.63171 | 56.9733 | -0.88348 | 57.2021 | -0.6546 | -0.050354 | 0.045777 | -0.032043 | 0.32959 | 0.19226 | -0.15564 | 0.24262 | -0.10529 | 0.8606 | 123.1247 | 0.37994 | 123.0972 | 123.3765 | 123.175 | 123.1476 | 123.1247 | -123.3078 | -123.1293 | 122.8958 | 123.0469 | 54.3686 | 52.3041
1024.8906 | 123.2346 | -57.7332 | 65.332 | -0.0030519 | 0.0044925 | 0.064358 | 0.067791 | -0.00013247 | -0.0020935 | -0.0046934 | -0.078644 | 0.0022708 | 0.067471 | 0.063893 | -0.0066778 | 0.0073936 | -0.0012113 | -3.0808 | 65.4007 | -57.9391 | 65.2496 | -57.2296 | -57.9346 | -0.4715 | -5.2643 | 65.3641 | -57.8156 | 65.3503 | -57.3532 | -57.8201 | -57.5226 | -0.20599 | 0.068665 | -0.082397 | 0.50354 | 57.2617 | -0.20142 | 57.4677 | 0.004578 | -0.082398 | 0.032044 | 0.018311 | 0.37994 | 0.21057 | -0.086975 | 0.29297 | -0.004577 | 0.70953 | 123.1888 | 0.46234 | 123.1659 | 123.3398 | 123.1796 | 123.1338 | 123.0972 | -123.2712 | -123.1476 | 122.9828 | 123.0835 | 54.6524 | 52.4689
1025.8594 | 123.23 | -57.7606 | 65.3046 | -0.079346 | 0.0036381 | 0.062863 | 0.071423 | 0.0022173 | -0.0033753 | 0.0015018 | -0.057281 | 0.0029116 | 0.070034 | 0.070088 | -0.008814 | 0.0061118 | -0.00014306 | -3.3417 | 65.3412 | -57.9849 | 65.1764 | -57.2662 | -57.9849 | -0.49896 | -5.3101 | 65.3366 | -57.8522 | 65.332 | -57.4173 | -57.8705 | -57.5455 | -0.2243 | 0.036622 | -0.12817 | 0.49439 | 57.2617 | -0.2243 | 57.486 | 0 | -0.091553 | 0.032044 | 0.027466 | 0.34332 | 0.21515 | -0.10986 | 0.3067 | -0.01831 | 0.71869 | 123.1613 | 0.43488 | 123.1842 | 123.3261 | 123.1888 | 123.1018 | 123.0972 | -123.2895 | -123.1567 | 122.937 | 123.0927 | 54.4189 | 52.4506
1026.9062 | 123.1934 | -57.7835 | 65.3229 | -0.048828 | 0.0029971 | 0.062222 | 0.068646 | 0.00029473 | -0.0018799 | -0.00063437 | -0.026764 | 0.0048344 | 0.06683 | 0.06197 | -0.0064642 | 0.0056846 | -0.0042021 | -3.3646 | 65.3961 | -57.9712 | 65.1169 | -57.3166 | -57.9987 | -0.49896 | -5.397 | 65.3275 | -57.8751 | 65.2817 | -57.4265 | -57.8842 | -57.5638 | -0.18768 | 0.073242 | -0.20599 | 0.46692 | 57.2845 | -0.21515 | 57.4722 | -0.027466 | -0.091553 | 0.004578 | -0.041199 | 0.35705 | 0.21973 | -0.10071 | 0.31128 | -0.009155 | 0.6546 | 123.0881 | 0.44861 | 123.1567 | 123.3673 | 123.2025 | 123.1796 | 123.111 | -123.2941 | -123.1979 | 122.9004 | 123.0652 | 54.4189 | 52.3865
1027.8594 | 123.2208 | -57.7698 | 65.3137 | -0.10223 | 0.0042789 | 0.062649 | 0.067364 | 0.0034991 | -0.0012391 | -0.003198 | -0.026764 | 0.005048 | 0.06918 | 0.062184 | -0.008814 | 0.0063254 | 0.0019931 | -3.2089 | 65.387 | -57.9895 | 65.1718 | -57.3029 | -57.9987 | -0.48523 | -5.3696 | 65.3 | -57.8613 | 65.3046 | -57.4173 | -57.8476 | -57.5272 | -0.21973 | 0.073242 | -0.14191 | 0.46692 | 57.2845 | -0.22888 | 57.5043 | -0.009155 | -0.091553 | -0.013733 | -0.009156 | 0.35248 | 0.24261 | -0.07782 | 0.33417 | 0.013733 | 0.68665 | 123.1613 | 0.44403 | 123.1659 | 123.3765 | 123.1613 | 123.1567 | 123.0698 | -123.3032 | -123.175 | 122.9416 | 123.0743 | 54.5609 | 52.4002
1028.9062 | 123.2529 | -57.8018 | 65.2222 | -0.10986 | 0.00064726 | 0.063076 | 0.069286 | 0.0037127 | -0.0025207 | -0.0040524 | -0.038971 | 0.006116 | 0.069607 | 0.068806 | -0.0066778 | 0.008248 | 0.0013521 | -3.4287 | 65.3 | -58.0536 | 65.062 | -57.3669 | -58.0994 | -0.58136 | -5.5115 | 65.2634 | -57.9117 | 65.2634 | -57.4585 | -57.9254 | -57.5821 | -0.25177 | 0.07782 | -0.16022 | 0.43488 | 57.2205 | -0.29755 | 57.4722 | -0.045776 | -0.10986 | 0.041199 | 0.041199 | 0.34332 | 0.21973 | -0.1236 | 0.32959 | -0.013733 | 0.68665 | 123.1155 | 0.45319 | 123.175 | 123.3536 | 123.175 | 123.1018 | 123.0652 | -123.2758 | -123.1338 | 122.8638 | 123.0652 | 54.3732 | 52.2903
1029.8594 | 123.2254 | -57.8293 | 65.2588 | -0.079346 | 0.0032107 | 0.066708 | 0.070995 | 0.0049945 | 0.00089713 | -0.0021298 | -0.038971 | 0.0041934 | 0.070034 | 0.06197 | -0.0083868 | 0.0063254 | 0.00028414 | -3.566 | 65.2679 | -58.0444 | 65.062 | -57.28 | -57.9987 | -0.50354 | -5.4565 | 65.2817 | -57.8796 | 65.2634 | -57.4448 | -57.9117 | -57.5821 | -0.21515 | 0.009155 | -0.19684 | 0.54932 | 57.3257 | -0.16937 | 57.5409 | 0.045777 | -0.050354 | 0.022888 | 0.004578 | 0.38452 | 0.24719 | -0.082397 | 0.29755 | -0.032043 | 0.76447 | 123.1064 | 0.43488 | 123.143 | 123.3124 | 123.1613 | 123.0972 | 123.111 | -123.3032 | -123.1384 | 122.8912 | 123.0927 | 54.2633 | 52.3727
1030.9062 | 123.2895 | -57.8156 | 65.1855 | -0.11749 | 0.00064726 | 0.06329 | 0.069714 | 0.0052081 | -0.0033753 | -0.0029844 | -0.0023498 | 0.0029116 | 0.067044 | 0.064747 | -0.0073188 | 0.0063254 | -0.0020657 | -3.3691 | 65.1855 | -58.0536 | 65.1215 | -57.2937 | -58.0261 | -0.51727 | -5.5023 | 65.1672 | -57.9254 | 65.3 | -57.4265 | -57.8842 | -57.55 | -0.23804 | 0 | -0.064087 | 0.52185 | 57.2983 | -0.21057 | 57.5363 | 0.027466 | -0.10986 | -0.018311 | 0.11444 | 0.3891 | 0.2655 | -0.068664 | 0.37537 | 0.041199 | 0.75989 | 123.175 | 0.49896 | 123.2254 | 123.2391 | 123.0927 | 123.0011 | 122.9828 | -123.2391 | -123.111 | 122.937 | 123.1155 | 54.4464 | 52.3132
1031.8594 | 123.2071 | -57.8751 | 65.1855 | -0.041199 | 0.0034245 | 0.063076 | 0.068432 | 0.0041399 | -0.0014527 | -0.0038388 | -0.057281 | 0.0031254 | 0.068325 | 0.063679 | -0.0073188 | 0.006539 | 0.00028414 | -3.4607 | 65.2496 | -58.1223 | 64.9933 | -57.4677 | -58.1772 | -0.62714 | -5.7312 | 65.2176 | -57.9712 | 65.1855 | -57.5867 | -58.0353 | -57.6874 | -0.24719 | 0.064087 | -0.19226 | 0.40741 | 57.2479 | -0.30212 | 57.4951 | -0.054932 | -0.09613 | 0.032043 | 0 | 0.28839 | 0.18768 | -0.16022 | 0.28381 | -0.064087 | 0.6546 | 123.1155 | 0.38452 | 123.1567 | 123.3719 | 123.1888 | 123.1247 | 123.0927 | -123.3078 | -123.1567 | 122.8683 | 123.0606 | 54.4144 | 52.1439
1032.8906 | 123.1979 | -57.8934 | 65.2267 | 0.019837 | 0.0021427 | 0.063076 | 0.070782 | -0.0022687 | -0.0033753 | -0.0023434 | -0.026764 | 0.005048 | 0.06918 | 0.063252 | -0.0053962 | 0.0067526 | -0.0012113 | -3.4332 | 65.2725 | -58.1039 | 65.0116 | -57.4356 | -58.1085 | -0.5722 | -5.7816 | 65.2359 | -57.9346 | 65.1718 | -57.5455 | -57.9941 | -57.6736 | -0.21057 | 0.045776 | -0.21515 | 0.45776 | 57.3212 | -0.21515 | 57.5317 | -0.004578 | -0.041198 | 0.009155 | -0.054932 | 0.3479 | 0.21973 | -0.10071 | 0.26093 | -0.05951 | 0.66833 | 123.1155 | 0.3891 | 123.1064 | 123.3765 | 123.1705 | 123.1659 | 123.1293 | -123.3307 | -123.1613 | 122.905 | 123.0652 | 54.4601 | 52.1118
1033.8594 | 123.2391 | -57.8934 | 65.1947 | -0.064087 | 0.00043366 | 0.063076 | 0.070141 | -0.0020551 | -0.00059807 | -0.00084817 | -0.069489 | 0.0041934 | 0.070248 | 0.068165 | -0.0086004 | 0.0054708 | -0.00099766 | -3.4103 | 65.2496 | -58.1085 | 64.9796 | -57.7103 | -57.8842 | -0.4303 | -5.6946 | 65.1901 | -57.9758 | 65.1993 | -57.5272 | -57.9803 | -57.6599 | -0.21515 | 0.054932 | -0.21515 | 0.18311 | 57.4631 | 0.009156 | 57.6782 | 0.22431 | -0.082397 | -0.004577 | 0.004578 | 0.36621 | 0.23346 | -0.086975 | 0.31586 | -0.004578 | 0.39826 | 123.0881 | 0.44861 | 123.175 | 123.3582 | 123.1659 | 123.143 | 123.0835 | -123.3032 | -123.1705 | 122.8729 | 123.0927 | 54.483 | 52.1988
1034.8906 | 123.1979 | -57.9071 | 65.1352 | 0.0045776 | 0.0034245 | 0.063076 | 0.070568 | 0.0013629 | -0.00059807 | 0.00086083 | -0.066437 | 0.0035526 | 0.067471 | 0.06902 | -0.007746 | 0.00483 | -0.0012113 | -3.4287 | 65.1993 | -58.1451 | 65.0162 | -57.4127 | -58.1497 | -0.60425 | -5.8548 | 65.1855 | -57.9987 | 65.1535 | -57.5958 | -58.0353 | -57.7148 | -0.23804 | 0.064087 | -0.11902 | 0.49438 | 57.3029 | -0.24262 | 57.5409 | -0.004577 | -0.091553 | 0.050354 | 0.01831 | 0.31128 | 0.19226 | -0.12817 | 0.28381 | -0.036621 | 0.73242 | 123.1613 | 0.40283 | 123.1522 | 123.3444 | 123.1842 | 123.1064 | 123.0927 | -123.2803 | -123.1338 | 122.9233 | 123.0606 | 54.4785 | 52.0523
1035.8594 | 123.2346 | -57.9483 | 65.1077 | -0.02594 | 0.0029971 | 0.064572 | 0.070355 | 0.0032855 | 0.00068353 | -0.00020717 | -0.060333 | 0.002698 | 0.068112 | 0.063465 | -0.0073188 | 0.0067526 | 0.0024203 | -3.4332 | 65.181 | -58.1543 | 64.9979 | -57.4402 | -58.1406 | -0.60425 | -5.9006 | 65.1535 | -58.0078 | 65.1581 | -57.5912 | -58.0261 | -57.7057 | -0.20599 | 0.073242 | -0.10986 | 0.50812 | 57.3441 | -0.19226 | 57.55 | 0.013733 | -0.059509 | 0.045776 | 0.050354 | 0.35706 | 0.24262 | -0.07782 | 0.30212 | -0.018311 | 0.71411 | 123.1522 | 0.41656 | 123.1659 | 123.3353 | 123.1613 | 123.1293 | 123.1018 | -123.262 | -123.1155 | 122.9462 | 123.1064 | 54.5151 | 52.0477
1036.9062 | 123.3215 | -57.9529 | 65.062 | -0.14038 | 0.0025699 | 0.064358 | 0.068005 | -0.00034607 | -0.0016663 | -0.0021298 | 0.012909 | 0.0035526 | 0.068112 | 0.068379 | -0.0079596 | 0.0097434 | 0.00049774 | -3.4561 | 65.0894 | -58.168 | 65.0024 | -57.4219 | -58.1497 | -0.61798 | -5.9463 | 65.0803 | -58.0307 | 65.181 | -57.5592 | -57.9758 | -57.6691 | -0.21515 | 0.027466 | -0.05951 | 0.53101 | 57.3349 | -0.19684 | 57.55 | 0.018311 | -0.07782 | 0.01831 | 0.11902 | 0.39368 | 0.28381 | -0.022888 | 0.36163 | 0.054932 | 0.74616 | 123.1705 | 0.4715 | 123.2117 | 123.2574 | 123.111 | 123.0423 | 123.0331 | -123.23 | -123.0927 | 122.9553 | 123.1338 | 54.4968 | 52.0065
1037.8594 | 123.2483 | -57.9483 | 65.1077 | -0.064087 | 0.0040653 | 0.063717 | 0.0695 | 0.0026447 | -0.0044433 | -0.003198 | -0.084747 | 0.0041934 | 0.068325 | 0.065388 | -0.0083868 | 0.0054708 | 0.0015659 | -3.4653 | 65.1398 | -58.2047 | 64.9567 | -57.486 | -58.1726 | -0.63629 | -6.0104 | 65.1306 | -58.0261 | 65.1352 | -57.6279 | -58.0444 | -57.7332 | -0.25635 | 0.032044 | -0.15106 | 0.46234 | 57.312 | -0.2243 | 57.5684 | 0.032044 | -0.07782 | 0.022888 | 0.027466 | 0.32043 | 0.21515 | -0.096131 | 0.29297 | -0.018311 | 0.71869 | 123.1613 | 0.39825 | 123.1613 | 123.3444 | 123.1567 | 123.0881 | 123.0789 | -123.3124 | -123.1338 | 122.905 | 123.0835 | 54.483 | 51.9379
1038.8906 | 123.2117 | -57.9987 | 65.0848 | -0.11749 | 0.0027835 | 0.062436 | 0.069714 | 0.00093573 | 0.0019653 | 0.0021426 | -0.038971 | 0.004407 | 0.069821 | 0.070728 | -0.007105 | 0.0054708 | 0.0013521 | -3.4744 | 65.1306 | -58.2092 | 64.9384 | -57.5089 | -58.2275 | -0.68207 | -6.102 | 65.0986 | -58.0536 | 65.0848 | -57.6553 | -58.1039 | -57.7652 | -0.21057 | 0.045776 | -0.14648 | 0.48981 | 57.3166 | -0.22888 | 57.5272 | -0.01831 | -0.054932 | 0.013733 | 0 | 0.34332 | 0.23346 | -0.10529 | 0.28839 | -0.050354 | 0.70038 | 123.1476 | 0.39825 | 123.1384 | 123.3398 | 123.1522 | 123.1293 | 123.0972 | -123.2941 | -123.1384 | 122.937 | 123.0835 | 54.5242 | 51.8967
1039.8594 | 123.2254 | -58.0032 | 65.0574 | -0.033569 | 0.0023563 | 0.06329 | 0.070995 | 0.0043537 | -0.0016663 | -0.0012754 | -0.035919 | 0.0024844 | 0.069821 | 0.060688 | -0.008814 | 0.0050436 | 7.0538e-05 | -3.4973 | 65.1352 | -58.223 | 64.9338 | -57.5089 | -58.2092 | -0.64087 | -6.134 | 65.0848 | -58.0719 | 65.094 | -57.6508 | -58.0719 | -57.7652 | -0.21973 | 0.07782 | -0.1236 | 0.49438 | 57.3624 | -0.20599 | 57.5821 | 0.013732 | -0.068664 | 0.027466 | 0.036621 | 0.35248 | 0.23804 | -0.068664 | 0.3067 | 0 | 0.71411 | 123.1567 | 0.42114 | 123.1659 | 123.3582 | 123.1567 | 123.1384 | 123.0881 | -123.2803 | -123.1293 | 122.937 | 123.0972 | 54.5059 | 51.8692
1040.8906 | 123.1567 | -58.0444 | 65.0665 | -0.13275 | 0.0029971 | 0.064145 | 0.070995 | 0.0017901 | -0.0020935 | -0.00042077 | -0.07254 | 0.0041934 | 0.069821 | 0.068379 | -0.0068914 | 0.0084616 | 0.0011385 | -3.6072 | 65.1031 | -58.2687 | 64.7964 | -57.6462 | -58.3328 | -0.75073 | -6.3492 | 65.0528 | -58.1223 | 65.007 | -57.7652 | -58.1818 | -57.843 | -0.2243 | 0.036621 | -0.27008 | 0.39826 | 57.2937 | -0.28839 | 57.518 | -0.064087 | -0.077819 | -0.013733 | -0.059509 | 0.27924 | 0.20142 | -0.13733 | 0.27923 | -0.05951 | 0.62256 | 123.0652 | 0.35706 | 123.1293 | 123.3719 | 123.175 | 123.1476 | 123.0972 | -123.3353 | -123.1888 | 122.8409 | 123.0515 | 54.4373 | 51.6953
1041.875 | 123.2849 | -58.0582 | 64.9933 | -0.10986 | 0.0044925 | 0.063076 | 0.070141 | -0.00077327 | -0.0012391 | -0.0034116 | 0.025116 | 0.0014164 | 0.068112 | 0.063679 | -0.0028326 | 0.0086752 | -0.0033475 | -3.5568 | 65.0436 | -58.2367 | 64.9063 | -57.5272 | -58.2458 | -0.66834 | -6.2759 | 65.0024 | -58.0902 | 65.0528 | -57.7515 | -58.1497 | -57.7972 | -0.17853 | 0.050354 | -0.086975 | 0.53101 | 57.3898 | -0.18768 | 57.5684 | -0.009156 | -0.032043 | 0.009155 | 0.059509 | 0.3067 | 0.26093 | -0.091552 | 0.29297 | -0.059509 | 0.70953 | 123.143 | 0.33874 | 123.143 | 123.2803 | 123.0927 | 123.1018 | 123.0606 | -123.23 | -123.0835 | 122.9645 | 123.111 | 54.5013 | 51.7822
1042.9062 | 123.3719 | -58.0261 | 64.9796 | -0.071716 | -0.00020714 | 0.063931 | 0.067791 | 8.1126e-05 | -0.0018799 | -0.0044796 | 0.052582 | 0.0020572 | 0.068753 | 0.059193 | -0.008814 | 0.0058982 | 0.0073337 | -3.5477 | 65.0253 | -58.2504 | 64.92 | -57.5317 | -58.2047 | -0.63171 | -6.3126 | 65.0208 | -58.1039 | 65.3732 | -57.4219 | -58.3694 | -57.9712 | -0.2243 | 0.045777 | -0.059509 | 0.49439 | 57.3944 | -0.17853 | 57.6187 | 0.045776 | -0.07782 | 0.041199 | 0.39368 | 0.60425 | 0.054932 | -0.34332 | 0.13275 | -0.2655 | 0.71869 | 123.1705 | 0.68207 | 123.4772 | 123.2758 | 123.1247 | 123.0515 | 123.0469 | -123.23 | -123.0835 | 122.9462 | 123.3994 | 54.4785 | 51.7136
1043.8594 | 123.1934 | -58.1039 | 64.9841 | -0.064087 | 0.0023563 | 0.06329 | 0.069714 | 0.0026447 | -0.0014527 | -0.0010618 | -0.078644 | 0.0035526 | 0.067471 | 0.065602 | -0.008814 | 0.0078208 | 0.00071134 | -3.6301 | 65.0253 | -58.3237 | 64.7827 | -57.6874 | -58.3923 | -0.80109 | -6.5231 | 65.0253 | -58.1589 | 64.9567 | -57.8293 | -58.2458 | -57.9025 | -0.21973 | 0.041199 | -0.20142 | 0.41656 | 57.3029 | -0.28839 | 57.5226 | -0.068665 | -0.054932 | 0.041199 | -0.027466 | 0.27466 | 0.20142 | -0.14191 | 0.25635 | -0.086975 | 0.63629 | 123.1064 | 0.32959 | 123.1155 | 123.349 | 123.1842 | 123.1293 | 123.1293 | -123.3078 | -123.143 | 122.8867 | 123.0606 | 54.4739 | 51.5808
1044.8906 | 123.23 | -58.0856 | 64.9979 | -0.02594 | -0.00042094 | 0.06329 | 0.069286 | -0.0022687 | -0.0010255 | -0.003198 | -0.063385 | 0.0039798 | 0.065548 | 0.066242 | -0.0081732 | 0.0069662 | -0.0020657 | -3.5889 | 65.0482 | -58.3237 | 64.856 | -57.6279 | -58.3237 | -0.75989 | -6.5094 | 64.9979 | -58.1909 | 64.9796 | -57.7927 | -58.2001 | -57.8842 | -0.23804 | 0.050354 | -0.14191 | 0.45776 | 57.3257 | -0.23804 | 57.5638 | 0 | -0.10529 | 0 | -0.018311 | 0.29297 | 0.20142 | -0.11444 | 0.3067 | -0.009155 | 0.6958 | 123.1796 | 0.39825 | 123.1705 | 123.3719 | 123.1888 | 123.1338 | 123.0835 | -123.3215 | -123.1888 | 122.9416 | 123.0652 | 54.4968 | 51.5762
1045.8594 | 123.2254 | -58.1223 | 64.9796 | -0.094604 | 0.00043366 | 0.063076 | 0.068432 | 0.0043537 | -0.0025207 | -0.002557 | -0.051178 | 0.0020572 | 0.06683 | 0.064747 | -0.0049688 | 0.006539 | 0.00049774 | -3.6118 | 65.0208 | -58.3145 | 64.8331 | -57.6096 | -58.3099 | -0.737 | -6.5506 | 65.007 | -58.1451 | 65.007 | -57.7606 | -58.1772 | -57.8567 | -0.19226 | 0.041199 | -0.14648 | 0.5127 | 57.3853 | -0.18768 | 57.5775 | 0.004577 | -0.022889 | 0.027466 | 0.027466 | 0.36163 | 0.2655 | -0.054932 | 0.28839 | -0.032043 | 0.70496 | 123.1476 | 0.38452 | 123.1522 | 123.3353 | 123.1522 | 123.143 | 123.1293 | -123.2941 | -123.1247 | 122.9553 | 123.1293 | 54.5105 | 51.5717
1046.9062 | 123.3078 | -58.1085 | 64.8972 | -0.14038 | 0.0034245 | 0.064572 | 0.066937 | -0.00098687 | -0.00017087 | -0.003198 | -0.0023498 | 0.0031254 | 0.068112 | 0.064961 | -0.0081732 | 0.0061118 | 0.0013521 | -3.6438 | 64.9246 | -58.2687 | 64.8376 | -57.6004 | -58.3282 | -0.75531 | -6.6101 | 64.92 | -58.1863 | 65.0024 | -57.7835 | -58.168 | -57.8476 | -0.16022 | 0.027466 | -0.05951 | 0.50812 | 57.3532 | -0.21973 | 57.5134 | -0.059509 | -0.077819 | 0.022888 | 0.10529 | 0.32501 | 0.26093 | -0.059509 | 0.33875 | 0.01831 | 0.66833 | 123.1064 | 0.40283 | 123.1888 | 123.1934 | 123.1064 | 123.0331 | 123.0286 | -123.1659 | -123.0835 | 122.9462 | 123.111 | 54.4647 | 51.4984
1047.8594 | 123.1796 | -58.1726 | 64.9063 | -0.071716 | 0.0019291 | 0.062436 | 0.068005 | 0.0079853 | -0.0020935 | -0.0021298 | -0.02066 | 0.0046206 | 0.068325 | 0.070942 | -0.007746 | 0.0078208 | 0.0015659 | -3.7079 | 64.9979 | -58.3649 | 64.6774 | -57.3898 | -58.5342 | -0.84228 | -6.8161 | 64.9979 | -58.2367 | 64.8926 | -57.8888 | -58.3191 | -57.9666 | -0.19226 | 0.091553 | -0.22888 | 0.78278 | 57.3303 | -0.36163 | 57.5226 | -0.16937 | -0.064087 | 0.091553 | -0.013733 | 0.28381 | 0.20599 | -0.14648 | 0.27008 | -0.082398 | 0.97504 | 123.0423 | 0.3479 | 123.1293 | 123.3627 | 123.2346 | 123.1705 | 123.1705 | -123.2712 | -123.143 | 122.85 | 123.0652 | 54.4647 | 51.3565
1048.9062 | 123.2986 | -58.0994 | 64.8972 | -0.10223 | 0.00064726 | 0.061154 | 0.0695 | -0.00055967 | 0.00068353 | -0.0036252 | 0.043427 | 0.0037662 | 0.069393 | 0.061329 | -0.0058234 | 0.00483 | 0.0013521 | -3.6942 | 64.9521 | -58.3374 | 64.8193 | -57.6279 | -58.3054 | -0.75073 | -6.7108 | 64.9063 | -58.2001 | 64.975 | -57.7515 | -58.1497 | -57.8613 | -0.23804 | 0.054931 | -0.07782 | 0.4715 | 57.3486 | -0.20599 | 57.5867 | 0.032043 | -0.10071 | 0.009155 | 0.07782 | 0.3479 | 0.23804 | -0.050354 | 0.33875 | 0.050354 | 0.70953 | 123.1567 | 0.44861 | 123.175 | 123.2895 | 123.1064 | 123.0515 | 123.0057 | -123.2346 | -123.0972 | 122.9187 | 123.0743 | 54.4052 | 51.3885
1049.8594 | 123.2071 | -58.2001 | 64.8834 | -0.079346 | 0.0027835 | 0.060513 | 0.069073 | 0.0026447 | 0.00025633 | -0.00084817 | -0.069489 | 0.0035526 | 0.067898 | 0.066456 | -0.0098822 | 0.0061118 | -0.0014249 | -3.8086 | 64.9429 | -58.429 | 64.7003 | -57.7606 | -58.4793 | -0.91095 | -6.9168 | 64.888 | -58.2504 | 64.9063 | -57.8842 | -58.287 | -57.9529 | -0.22888 | 0.059509 | -0.18311 | 0.43945 | 57.2891 | -0.27924 | 57.518 | -0.050354 | -0.050354 | 0.004577 | 0.022888 | 0.31586 | 0.24719 | -0.086975 | 0.29755 | -0.036621 | 0.66833 | 123.1293 | 0.36621 | 123.1567 | 123.3719 | 123.1384 | 123.143 | 123.0881 | -123.3124 | -123.1338 | 122.9004 | 123.1064 | 54.3915 | 51.2833
1050.8906 | 123.1567 | -58.2047 | 64.8972 | -0.086975 | 0.0023563 | 0.06329 | 0.070995 | 0.0017901 | -0.0018799 | -0.0019162 | -0.093903 | 0.0031254 | 0.067898 | 0.068806 | -0.0075324 | 0.0069662 | 0.0022067 | -3.8223 | 64.9521 | -58.4152 | 64.6683 | -57.8201 | -58.5205 | -0.96588 | -7.0724 | 64.8926 | -58.2687 | 64.8468 | -57.9437 | -58.3511 | -58.0124 | -0.21057 | 0.054931 | -0.22888 | 0.38452 | 57.2388 | -0.31586 | 57.4493 | -0.10529 | -0.064087 | -0.004578 | -0.050354 | 0.26093 | 0.19226 | -0.14648 | 0.25635 | -0.082397 | 0.59509 | 123.0835 | 0.32501 | 123.1155 | 123.3673 | 123.1613 | 123.1567 | 123.0972 | -123.3124 | -123.1659 | 122.8729 | 123.0515 | 54.3823 | 51.1322
1051.8594 | 123.3261 | -58.1863 | 64.8056 | -0.10986 | 0.0032107 | 0.066922 | 0.069286 | -0.0035505 | -0.0020935 | 0.00086083 | -0.02066 | 0.002698 | 0.068325 | 0.070515 | -0.0083868 | 0.0076072 | -0.0020657 | -3.8727 | 64.8788 | -58.4106 | 64.769 | -57.6965 | -58.3878 | -0.88806 | -6.9397 | 64.8468 | -58.2916 | 64.9475 | -57.8201 | -58.2184 | -57.8934 | -0.22431 | 0.073242 | -0.036621 | 0.48981 | 57.2983 | -0.20142 | 57.5226 | 0.022889 | -0.10529 | 0.041199 | 0.14191 | 0.36621 | 0.29297 | -0.032044 | 0.39825 | 0.073242 | 0.71411 | 123.1796 | 0.4715 | 123.2391 | 123.2895 | 123.1384 | 123.0652 | 123.0331 | -123.2162 | -123.0972 | 122.9553 | 123.1338 | 54.3137 | 51.2466
1052.9062 | 123.2941 | -58.2275 | 64.7873 | -0.10223 | 0.0010745 | 0.063717 | 0.069073 | 0.0024311 | -0.0031617 | -0.0017026 | -0.017609 | 0.00034819 | 0.065762 | 0.067738 | -0.0075324 | 0.0050436 | 0.0026339 | -3.9093 | 64.8697 | -58.3969 | 64.7736 | -57.692 | -58.3923 | -0.90637 | -7.0038 | 64.8239 | -58.2825 | 64.9429 | -57.8522 | -58.2458 | -57.9208 | -0.16937 | 0.082398 | -0.013732 | 0.53558 | 57.3212 | -0.16479 | 57.4905 | 0.004578 | -0.054932 | 0.036622 | 0.15564 | 0.37537 | 0.3067 | -0.018311 | 0.36163 | 0.036621 | 0.70496 | 123.1705 | 0.4303 | 123.2254 | 123.2666 | 123.1064 | 123.0972 | 123.0515 | -123.1842 | -123.0698 | 123.0011 | 123.1705 | 54.3182 | 51.2238
1053.8594 | 123.1888 | -58.2367 | 64.8239 | -0.02594 | -0.00042094 | 0.063076 | 0.071209 | 0.0071307 | -0.0029481 | -0.00084817 | -0.075592 | 0.0035526 | 0.067684 | 0.071369 | -0.0075324 | 0.0073936 | -0.00057046 | -4.0466 | 64.8834 | -58.4793 | 64.6362 | -57.8339 | -58.5526 | -1.0391 | -7.196 | 64.8743 | -58.3282 | 64.8376 | -57.9895 | -58.3603 | -58.0215 | -0.24262 | 0.059509 | -0.18768 | 0.40283 | 57.1976 | -0.31586 | 57.4402 | -0.073242 | -0.091553 | 0.050354 | 0.013732 | 0.24719 | 0.21515 | -0.1236 | 0.3067 | -0.032044 | 0.64545 | 123.1155 | 0.33874 | 123.1659 | 123.3627 | 123.2025 | 123.1201 | 123.111 | -123.3032 | -123.1522 | 122.8729 | 123.0743 | 54.1901 | 51.0406
1054.9062 | 123.3032 | -58.1726 | 64.8102 | -0.056457 | 0.0019291 | 0.061581 | 0.068646 | 0.0015765 | -0.00059807 | -0.0027708 | 0.015961 | 0.003339 | 0.06683 | 0.058125 | -0.0090278 | 0.00483 | 7.0538e-05 | -3.9917 | 64.8743 | -58.429 | 64.7964 | -57.637 | -58.342 | -0.89264 | -7.0404 | 64.8239 | -58.2962 | 64.9429 | -57.8156 | -58.2001 | -57.93 | -0.25635 | 0.064087 | -0.013733 | 0.53558 | 57.28 | -0.16937 | 57.5363 | 0.086975 | -0.1236 | 0.013733 | 0.13275 | 0.35706 | 0.24261 | -0.027466 | 0.36621 | 0.096131 | 0.79193 | 123.2254 | 0.48065 | 123.2391 | 123.3032 | 123.1201 | 123.0469 | 122.9965 | -123.2391 | -123.1064 | 122.9691 | 123.1155 | 54.1809 | 51.1322
1055.8594 | 123.1705 | -58.2687 | 64.8102 | -0.12512 | 0.0038517 | 0.062008 | 0.072064 | 0.0034991 | -0.0018799 | -0.0027708 | -0.096954 | 0.0020572 | 0.068112 | 0.070515 | -0.007746 | 0.0073936 | -0.0022793 | -4.097 | 64.8788 | -58.4702 | 64.5996 | -57.9117 | -58.5617 | -1.0986 | -7.3837 | 64.8376 | -58.3603 | 64.7827 | -58.017 | -58.429 | -58.0856 | -0.20142 | 0.068664 | -0.21057 | 0.35706 | 57.1701 | -0.29297 | 57.3715 | -0.091553 | -0.091553 | 0.027465 | -0.027466 | 0.25177 | 0.18311 | -0.16022 | 0.27466 | -0.068664 | 0.55847 | 123.0698 | 0.34332 | 123.143 | 123.349 | 123.1979 | 123.1476 | 123.1064 | -123.2803 | -123.1705 | 122.8683 | 123.0515 | 54.1718 | 50.885
1056.9062 | 123.3261 | -58.2321 | 64.7827 | -0.094604 | 0.0021427 | 0.063076 | 0.066082 | 0.0013629 | -0.00038447 | 6.432e-06 | 0.019012 | 0.0024844 | 0.065335 | 0.067311 | -0.007746 | 0.003762 | 0.0032749 | -4.1382 | 64.8422 | -58.4427 | 64.769 | -57.6691 | -58.3557 | -0.93842 | -7.2327 | 64.8056 | -58.287 | 64.9017 | -57.843 | -58.2413 | -57.9437 | -0.21057 | 0.059509 | -0.013733 | 0.56305 | 57.2937 | -0.1236 | 57.5043 | 0.086975 | -0.054931 | 0.022888 | 0.11902 | 0.3891 | 0.28839 | -0.009155 | 0.34332 | 0.045776 | 0.77362 | 123.2117 | 0.44403 | 123.1888 | 123.2849 | 123.0927 | 123.0743 | 123.0377 | -123.2254 | -123.0698 | 123.0011 | 123.1338 | 54.0939 | 50.9995
1057.8594 | 123.3261 | -58.2733 | 64.7552 | -0.10986 | 0.0029971 | 0.062649 | 0.068432 | 0.0032855 | -0.0033753 | -0.00084817 | -0.066437 | 0.0029116 | 0.067471 | 0.074146 | -0.0073188 | 0.0063254 | -0.00057046 | -4.2892 | 64.8056 | -58.5434 | 64.6088 | -57.8659 | -58.548 | -1.1398 | -7.4936 | 64.7827 | -58.374 | 64.8468 | -58.1863 | -58.4381 | -58.0399 | -0.27008 | 0.050354 | -0.14648 | 0.40741 | 57.1335 | -0.27466 | 57.4036 | -0.004578 | -0.10071 | 0.027466 | 0.091553 | 0.086975 | 0.23346 | -0.1648 | 0.33417 | -0.064087 | 0.67749 | 123.1522 | 0.18768 | 123.2208 | 123.349 | 123.1567 | 123.0789 | 123.056 | -123.2986 | -123.1293 | 122.8821 | 123.1201 | 53.9841 | 50.7797
1058.9062 | 123.2803 | -58.2825 | 64.7598 | -0.11749 | 0.0017155 | 0.062008 | 0.069927 | -0.00098687 | -0.0020935 | -0.0038388 | 0.012909 | 0.00163 | 0.069821 | 0.059406 | -0.009455 | 0.0067526 | -0.0012113 | -4.2572 | 64.7873 | -58.4885 | 64.7095 | -57.7194 | -58.4015 | -1.0025 | -7.7087 | 64.7736 | -58.3374 | 64.8697 | -57.8796 | -58.2687 | -57.9941 | -0.20599 | 0.027465 | -0.050354 | 0.56305 | 57.28 | -0.11902 | 57.486 | 0.086975 | -0.054931 | 0.013733 | 0.10986 | 0.40283 | 0.28839 | 0.013733 | 0.34332 | 0.068664 | 0.76904 | 123.1979 | 0.45776 | 123.2071 | 123.2758 | 123.111 | 123.0698 | 123.056 | -123.2483 | -123.0972 | 122.9919 | 123.1522 | 54.0253 | 50.5737
1059.8594 | 123.1842 | -58.3466 | 64.7644 | -0.079346 | 0.0012881 | 0.06329 | 0.072277 | 0.0052081 | -0.0031617 | 0.0017154 | -0.12747 | 0.003339 | 0.065975 | 0.069874 | -0.009455 | 0.0093162 | -0.0029203 | -4.2847 | 64.7873 | -58.6029 | 64.682 | -57.9117 | -58.6487 | -1.1581 | -8.0612 | 64.7781 | -58.4152 | 64.7186 | -58.1177 | -58.5114 | -58.1497 | -0.25635 | 0.022888 | -0.082397 | 0.43488 | 57.1884 | -0.30212 | 57.4448 | -0.045777 | -0.068664 | 0.013733 | -0.045776 | 0.22888 | 0.19684 | -0.16479 | 0.2655 | -0.096131 | 0.69122 | 123.2849 | 0.29755 | 123.1338 | 123.3902 | 123.1934 | 123.1338 | 123.1247 | -123.3673 | -123.1796 | 123.0286 | 123.0652 | 54.0619 | 50.2853
1060.8906 | 123.1796 | -58.374 | 64.7415 | -0.094604 | 0.0021427 | 0.063504 | 0.072277 | 0.00093573 | -0.0029481 | 0.00086083 | -0.087799 | 0.003339 | 0.068753 | 0.069233 | -0.0079596 | 0.0069662 | -0.00057046 | -4.4449 | 64.7964 | -58.58 | 64.5035 | -57.9895 | -58.6716 | -1.2817 | -8.1482 | 64.7552 | -58.4198 | 64.7049 | -58.1085 | -58.5159 | -58.1543 | -0.20599 | 0.054932 | -0.23804 | 0.38452 | 57.0923 | -0.29755 | 57.2983 | -0.091553 | -0.045777 | 0.013733 | -0.036621 | 0.2655 | 0.21973 | -0.14191 | 0.2655 | -0.09613 | 0.59051 | 123.0835 | 0.31128 | 123.1247 | 123.3765 | 123.175 | 123.1705 | 123.1293 | -123.3215 | -123.1613 | 122.8775 | 123.0789 | 53.9291 | 50.2258
1061.875 | 123.3902 | -58.3008 | 64.6912 | -0.14038 | 0.0027835 | 0.063717 | 0.06715 | 8.1126e-05 | -0.00017087 | -0.0027708 | -0.0084534 | 0.0022708 | 0.06683 | 0.063679 | -0.0058234 | 0.0041892 | 0.00092494 | -4.4174 | 64.7324 | -58.5526 | 64.6133 | -57.8247 | -58.5434 | -1.1719 | -8.0521 | 64.7049 | -58.4198 | 64.7964 | -58.0353 | -58.3969 | -58.1818 | -0.25177 | 0.041199 | -0.07782 | 0.47607 | 57.1289 | -0.24262 | 57.3807 | 0.009155 | -0.11902 | 0.013733 | 0.10529 | 0.2655 | 0.11902 | -0.096131 | 0.23804 | 0.022888 | 0.72784 | 123.1659 | 0.38452 | 123.2162 | 123.2849 | 123.1247 | 123.0331 | 123.0057 | -123.2437 | -123.111 | 122.9141 | 123.0972 | 53.8834 | 50.2487
1062.9062 | 123.262 | -58.342 | 64.6912 | -0.10223 | 0.0032107 | 0.064785 | 0.0695 | -0.0026959 | 0.0019653 | 0.0034244 | 0.037323 | 0.00163 | 0.068966 | 0.062397 | -0.0068914 | 0.0071798 | -0.0012113 | -4.4815 | 64.7049 | -58.5571 | 64.3524 | -57.843 | -58.5114 | -1.3184 | -8.2077 | 64.7232 | -58.4061 | 64.7552 | -58.0215 | -58.429 | -58.0902 | -0.21515 | 0.013733 | -0.33875 | 0.49896 | 57.0236 | -0.16937 | 57.2388 | 0.045776 | -0.064087 | 0.032044 | 0.064087 | 0.32043 | 0.25177 | -0.086975 | 0.31586 | -0.022888 | 0.71411 | 122.9095 | 0.38452 | 123.1613 | 123.262 | 123.1293 | 123.0469 | 123.0652 | -123.2483 | -123.0972 | 122.6944 | 123.0972 | 53.8605 | 50.1343
1063.8594 | 123.2025 | -58.3923 | 64.7049 | -0.064087 | 0.0023563 | 0.062649 | 0.071423 | 0.0013629 | -0.0033753 | -0.0029844 | -0.078644 | 0.0037662 | 0.070461 | 0.067951 | -0.007105 | 0.0069662 | -0.0029203 | -4.5502 | 64.7552 | -58.6121 | 64.5081 | -57.9895 | -58.6945 | -1.3412 | -8.2901 | 64.7369 | -58.4335 | 64.6957 | -58.1314 | -58.5205 | -58.1726 | -0.21973 | 0.050354 | -0.19684 | 0.40283 | 57.0511 | -0.30212 | 57.2708 | -0.082397 | -0.041199 | 0.032043 | -0.009155 | 0.26093 | 0.21973 | -0.12817 | 0.26093 | -0.086975 | 0.62256 | 123.1201 | 0.30212 | 123.1293 | 123.3673 | 123.1705 | 123.1476 | 123.1293 | -123.317 | -123.1384 | 122.9004 | 123.0881 | 53.8422 | 50.1022
1064.8594 | 123.2803 | -58.3145 | 64.6591 | -0.14801 | 0.0051333 | 0.062863 | 0.069714 | 0.00072213 | -0.0044433 | -0.0010618 | -0.042023 | 0.0029116 | 0.06448 | 0.06902 | -0.0083868 | 0.006539 | -0.00035666 | -4.4998 | 64.7141 | -58.58 | 64.6133 | -57.8522 | -58.5571 | -1.2589 | -8.1665 | 64.6729 | -58.4381 | 64.7827 | -58.017 | -58.3878 | -58.0765 | -0.2655 | 0.054931 | -0.045777 | 0.46234 | 57.0557 | -0.24262 | 57.3212 | 0.022888 | -0.1236 | 0.013733 | 0.1236 | 0.29755 | 0.23804 | -0.073242 | 0.36163 | 0.050354 | 0.72784 | 123.1934 | 0.42114 | 123.2208 | 123.2941 | 123.111 | 123.0286 | 122.9874 | -123.2391 | -123.0972 | 122.9279 | 123.0972 | 53.8147 | 50.148
1065.8906 | 123.2025 | -58.3649 | 64.7186 | 0.0045776 | 0.0015019 | 0.062222 | 0.069714 | 8.1126e-05 | -0.0016663 | 0.00022003 | -0.057281 | 0.0041934 | 0.06683 | 0.06432 | -0.0096686 | 0.0076072 | -0.0035611 | -4.5502 | 64.7781 | -58.5846 | 64.5401 | -57.9575 | -58.5709 | -1.3 | -8.2901 | 64.7369 | -58.4381 | 64.7415 | -58.0856 | -58.461 | -58.1497 | -0.21973 | 0.059509 | -0.17853 | 0.40741 | 57.0648 | -0.20599 | 57.2845 | 0.013733 | -0.073242 | 0.01831 | 0.022888 | 0.27924 | 0.21515 | -0.096131 | 0.28839 | -0.022889 | 0.62714 | 123.1247 | 0.35248 | 123.1796 | 123.3627 | 123.175 | 123.143 | 123.1018 | -123.3032 | -123.1567 | 122.905 | 123.1064 | 53.8147 | 50.0748
1066.875 | 123.4406 | -58.3054 | 64.6866 | -0.10986 | 0.0015019 | 0.059872 | 0.068432 | 0.00072213 | 0.00025633 | -0.0019162 | -0.0084534 | 0.0029116 | 0.069607 | 0.066242 | -0.0066778 | 0.0050436 | 0.0019931 | -4.541 | 64.7003 | -58.5709 | 64.6088 | -57.8751 | -58.5434 | -1.2589 | -8.2443 | 64.7049 | -58.4427 | 64.7919 | -58.0215 | -58.1589 | -57.8522 | -0.2655 | 0.013733 | -0.077819 | 0.4303 | 57.0465 | -0.23804 | 57.312 | 0.027466 | -0.13733 | 0.018311 | 0.10529 | 0.28381 | 0.45319 | 0.14648 | 0.59051 | 0.28381 | 0.6958 | 123.1796 | 0.42114 | 123.2346 | 123.2712 | 123.1476 | 123.0057 | 123.0103 | -123.2574 | -123.1293 | 122.9141 | 123.0972 | 53.7643 | 50.061
1067.8906 | 122.9553 | -58.4198 | 64.6637 | -0.048828 | 0.0017155 | 0.063504 | 0.069927 | 0.0045673 | -0.00038447 | 0.00022003 | -0.07254 | 0.0046206 | 0.068753 | 0.068806 | -0.0090278 | 0.006539 | -0.0033475 | -4.6005 | 64.7278 | -58.6395 | 64.5126 | -57.9712 | -58.6533 | -1.3962 | -8.4091 | 64.7003 | -58.4656 | 64.6637 | -58.1543 | -58.5342 | -58.0765 | -0.21973 | 0.064087 | -0.15106 | 0.44861 | 57.0236 | -0.23346 | 57.2433 | -0.013733 | -0.045776 | 0.036621 | 0 | 0.2655 | 0.34332 | -0.11444 | 0.3891 | -0.068665 | 0.66833 | 123.1522 | 0.31128 | 123.1293 | 123.3673 | 123.1659 | 123.1476 | 123.1201 | -123.3032 | -123.1293 | 122.9324 | 123.0835 | 53.8193 | 50.0107
1068.8594 | 123.2758 | -58.374 | 64.6179 | -0.15564 | 0.0025699 | 0.063504 | 0.068432 | 0.0047809 | 0.0019653 | -0.00084817 | -0.011505 | 0.00163 | 0.067257 | 0.065602 | -0.0066778 | 0.0044028 | -0.00057046 | -4.5959 | 64.6408 | -58.6121 | 64.5721 | -57.8888 | -58.5938 | -1.3412 | -8.3496 | 64.6545 | -58.4702 | 64.7278 | -58.0765 | -58.4427 | -58.1314 | -0.23804 | 0.022888 | -0.045776 | 0.48523 | 57.0328 | -0.21973 | 57.2708 | 0.018311 | -0.096131 | 0.036621 | 0.10986 | 0.29755 | 0.24261 | -0.068665 | 0.33875 | 0.027466 | 0.72327 | 123.1842 | 0.39368 | 123.1979 | 123.2529 | 123.1247 | 123.0148 | 123.0286 | -123.23 | -123.0881 | 122.9462 | 123.1018 | 53.7781 | 50.0244
1069.8906 | 123.2346 | -58.3923 | 64.6637 | -0.10223 | 0.0034245 | 0.063076 | 0.069286 | -0.0067547 | -0.0012391 | -0.0010618 | -0.057281 | 0.004407 | 0.067898 | 0.067524 | -0.0064642 | 0.0073936 | 0.0015659 | -4.6143 | 64.7415 | -58.6441 | 64.4348 | -57.8842 | -58.5526 | -1.3962 | -8.4 | 64.6866 | -58.4747 | 64.7095 | -58.1039 | -58.4839 | -58.1635 | -0.25177 | 0.07782 | -0.22888 | 0.50812 | 56.9962 | -0.16022 | 57.2479 | 0.091553 | -0.082397 | 0.022888 | 0.045777 | 0.28839 | 0.22888 | -0.091553 | 0.31128 | -0.009156 | 0.75989 | 123.0789 | 0.37079 | 123.1842 | 123.3856 | 123.1613 | 123.1338 | 123.0789 | -123.3078 | -123.1384 | 122.8271 | 123.1018 | 53.7781 | 49.9924
1070.8594 | 123.2574 | -58.3969 | 64.6225 | -0.079346 | 0.0015019 | 0.061367 | 0.0695 | -0.0016279 | 0.0023925 | 0.0076968 | 0.067841 | 0.002698 | 0.065762 | 0.063893 | -0.0064642 | 0.0056846 | 0.00049774 | -4.6829 | 64.6774 | -58.6029 | 64.27 | -57.9208 | -58.6029 | -1.5198 | -8.5281 | 64.6133 | -58.4747 | 64.6774 | -58.1177 | -58.4518 | -58.1589 | -0.20599 | 0.054931 | -0.35248 | 0.47608 | 56.8771 | -0.20599 | 57.0831 | 0 | -0.077819 | -0.009156 | 0.054931 | 0.27924 | 0.23804 | -0.054931 | 0.31586 | 0.022888 | 0.68207 | 122.8729 | 0.35705 | 123.1522 | 123.2803 | 123.0881 | 123.0743 | 123.0103 | -123.2254 | -123.0972 | 122.6669 | 123.0743 | 53.714 | 49.8688
1071.9062 | 123.2849 | -58.3923 | 64.6271 | -0.14038 | 0.0027835 | 0.062436 | 0.066937 | -0.0056867 | -0.0010255 | -0.0029844 | -0.0023498 | 0.003339 | 0.066189 | 0.057697 | -0.0073188 | 0.006539 | 7.0538e-05 | -4.715 | 64.6545 | -58.6121 | 64.5172 | -57.962 | -58.6349 | -1.4328 | -8.5144 | 64.6454 | -58.4976 | 64.6912 | -58.1177 | -58.4885 | -58.1589 | -0.21973 | 0.027466 | -0.10986 | 0.4303 | 56.9595 | -0.24262 | 57.1793 | -0.022888 | -0.10529 | 0.018311 | 0.064087 | 0.27466 | 0.23346 | -0.09613 | 0.33874 | 0.009156 | 0.65002 | 123.1293 | 0.37994 | 123.1888 | 123.2666 | 123.143 | 123.0469 | 123.0377 | -123.2391 | -123.1247 | 122.9095 | 123.0835 | 53.6774 | 49.8779
1072.8594 | 123.2895 | -58.4198 | 64.5996 | -0.086975 | 0.0029971 | 0.064358 | 0.070782 | 0.0017901 | -0.0029481 | -0.00063437 | -0.045074 | 0.0012028 | 0.066189 | 0.069447 | -0.0090278 | 0.0067526 | -0.0022793 | -4.7058 | 64.6362 | -58.6349 | 64.5493 | -57.9163 | -58.6258 | -1.4465 | -8.4732 | 64.6133 | -58.5068 | 64.7141 | -58.1039 | -58.4564 | -58.136 | -0.21515 | 0.036621 | -0.050354 | 0.50354 | 56.9733 | -0.20599 | 57.1884 | 0.009156 | -0.086975 | 0.013733 | 0.11444 | 0.31586 | 0.28381 | -0.036621 | 0.37079 | 0.050354 | 0.71869 | 123.1842 | 0.40283 | 123.2208 | 123.2712 | 123.1201 | 123.056 | 123.0331 | -123.2346 | -123.1064 | 122.9691 | 123.1338 | 53.714 | 49.9466
1073.8906 | 123.1934 | -58.429 | 64.6408 | -0.056457 | 0.0021427 | 0.064785 | 0.070355 | 0.0052081 | -0.00081187 | -0.001489 | -0.12137 | 0.0048344 | 0.068539 | 0.065174 | -0.007746 | 0.0052572 | -0.0044157 | -4.7424 | 64.6591 | -58.667 | 64.5172 | -58.0032 | -58.6945 | -1.5198 | -8.5693 | 64.6454 | -58.5114 | 64.65 | -58.1863 | -58.5526 | -58.2092 | -0.23804 | 0.018311 | -0.1236 | 0.42572 | 56.9092 | -0.2655 | 57.1472 | -0.027466 | -0.082398 | 0.004578 | 0.009155 | 0.24262 | 0.21973 | -0.1236 | 0.30212 | -0.041198 | 0.66376 | 123.1842 | 0.32501 | 123.1613 | 123.3261 | 123.1567 | 123.0881 | 123.0743 | -123.3078 | -123.1522 | 122.9462 | 123.0789 | 53.6865 | 49.8596
1074.875 | 123.2529 | -58.4381 | 64.6088 | -0.12512 | 0.0025699 | 0.062649 | 0.069073 | -0.0016279 | -0.00081187 | -0.0029844 | 0.0037536 | 0.00163 | 0.066403 | 0.065815 | -0.0079596 | 0.0063254 | -0.0014249 | -4.8019 | 64.6408 | -58.6441 | 64.5035 | -57.9849 | -58.6578 | -1.4923 | -8.5968 | 64.6362 | -58.5068 | 64.6683 | -58.1451 | -58.4793 | -58.1772 | -0.20599 | 0.032043 | -0.10529 | 0.45319 | 56.9458 | -0.21973 | 57.1518 | -0.013733 | -0.068665 | 0.027465 | 0.059509 | 0.29297 | 0.26093 | -0.041199 | 0.32959 | 0.027466 | 0.65918 | 123.1476 | 0.36163 | 123.175 | 123.2849 | 123.143 | 123.0789 | 123.0743 | -123.2529 | -123.1155 | 122.9416 | 123.1064 | 53.6362 | 49.8413
1075.8906 | 123.3078 | -58.4244 | 64.5905 | -0.094604 | 0.0025699 | 0.064785 | 0.068859 | 0.0013629 | -0.00038447 | -0.001489 | -0.032867 | 0.0039798 | 0.067684 | 0.067097 | -0.0086004 | 0.0061118 | 0.00092494 | -4.7928 | 64.5996 | -58.6487 | 64.5309 | -57.962 | -58.6395 | -1.5381 | -8.5785 | 64.5996 | -58.5205 | 64.7186 | -58.1223 | -58.4702 | -58.1497 | -0.22431 | 0.009155 | -0.059509 | 0.46234 | 56.8863 | -0.21515 | 57.1106 | 0.009156 | -0.096131 | 0.009155 | 0.12817 | 0.30212 | 0.27466 | -0.045777 | 0.37079 | 0.050354 | 0.68665 | 123.1796 | 0.39825 | 123.2391 | 123.2483 | 123.1201 | 123.024 | 123.024 | -123.2391 | -123.111 | 122.9553 | 123.143 | 53.6316 | 49.8459
1076.875 | 123.2712 | -58.4152 | 64.6408 | -0.086975 | 0.0036381 | 0.06329 | 0.0695 | -0.00013247 | -0.0027345 | -0.0029844 | -0.023712 | 0.0012028 | 0.065975 | 0.062824 | -0.008814 | 0.00483 | 0.0011385 | -4.7653 | 64.6545 | -58.6212 | 64.5676 | -57.9071 | -58.5617 | -1.4648 | -8.5464 | 64.6271 | -58.493 | 64.7049 | -58.0856 | -58.4427 | -58.136 | -0.20599 | 0.013733 | -0.073242 | 0.50812 | 56.9504 | -0.14648 | 57.1564 | 0.059509 | -0.07782 | -0.013733 | 0.064087 | 0.32959 | 0.27924 | -0.027466 | 0.35706 | 0.050354 | 0.71411 | 123.1888 | 0.40741 | 123.1979 | 123.2758 | 123.1201 | 123.0698 | 123.0423 | -123.262 | -123.1339 | 122.9828 | 123.1201 | 53.6499 | 49.8688
1077.8906 | 123.2071 | -58.4473 | 64.6545 | 0.065613 | 0.0047061 | 0.063717 | 0.070995 | -0.00013247 | -0.0031617 | -0.002557 | -0.10611 | 0.00098899 | 0.067684 | 0.065602 | -0.007105 | 0.0073936 | 0.00049774 | -4.8523 | 64.6912 | -58.6624 | 64.4897 | -57.9941 | -58.6716 | -1.593 | -8.6426 | 64.6637 | -58.4976 | 64.6591 | -58.168 | -58.5251 | -58.2321 | -0.21515 | 0.036621 | -0.16479 | 0.45319 | 56.8542 | -0.2243 | 57.0694 | -0.009155 | -0.050354 | 0.009155 | 0.004578 | 0.27924 | 0.21515 | -0.077819 | 0.2655 | -0.027465 | 0.66834 | 123.1522 | 0.32959 | 123.1567 | 123.3536 | 123.1613 | 123.1384 | 123.111 | -123.317 | -123.1522 | 122.937 | 123.1064 | 53.595 | 49.8047
1078.8594 | 123.2574 | -58.4198 | 64.5767 | -0.13275 | 0.0017155 | 0.062436 | 0.06715 | -0.0016279 | 0.00068353 | -0.0027708 | -0.023712 | 0.002698 | 0.066403 | 0.062611 | -0.006037 | 0.0061118 | -0.0039883 | -4.8889 | 64.6042 | -58.667 | 64.5081 | -57.962 | -58.6578 | -1.593 | -8.6563 | 64.5996 | -58.5159 | 64.6774 | -58.1589 | -58.5022 | -58.1955 | -0.24719 | 0.027466 | -0.068664 | 0.45776 | 56.8268 | -0.23804 | 57.074 | 0.009155 | -0.09613 | 0.022888 | 0.10071 | 0.26093 | 0.2243 | -0.082397 | 0.32043 | 0.013733 | 0.70496 | 123.175 | 0.35705 | 123.1934 | 123.2712 | 123.1155 | 123.024 | 123.0194 | -123.2437 | -123.0927 | 122.9279 | 123.0972 | 53.5309 | 49.7635
1079.9062 | 123.2666 | -58.4839 | 64.5996 | -0.11749 | 0.0034245 | 0.062863 | 0.066296 | 0.0015765 | -0.0029481 | 0.0010746 | 0.0037536 | 0.003339 | 0.067257 | 0.060688 | -0.0075324 | 0.00483 | -0.0050565 | -4.9438 | 64.6454 | -58.6807 | 64.476 | -58.049 | -58.667 | -1.6342 | -8.7662 | 64.595 | -58.5342 | 64.6362 | -58.1772 | -58.5251 | -58.2001 | -0.19684 | 0.045777 | -0.1236 | 0.43488 | 56.8497 | -0.1831 | 57.0465 | 0.013733 | -0.050354 | -0.004577 | 0.036621 | 0.3067 | 0.28381 | -0.041198 | 0.33417 | 0.009156 | 0.63171 | 123.1567 | 0.35706 | 123.1705 | 123.3261 | 123.1293 | 123.1293 | 123.0789 | -123.2803 | -123.1338 | 122.9599 | 123.1201 | 53.54 | 49.7177
1080.8594 | 123.3032 | -58.4473 | 64.563 | -0.14038 | 0.0032107 | 0.06329 | 0.068859 | 0.0041399 | 4.273e-05 | -0.002557 | -0.051178 | 0.0024844 | 0.067898 | 0.064747 | -0.0096686 | 0.0044028 | -0.0012113 | -4.9393 | 64.6042 | -58.6899 | 64.5264 | -57.9941 | -58.6716 | -1.6479 | -8.7433 | 64.563 | -58.5526 | 64.6957 | -58.1451 | -58.5022 | -58.1635 | -0.24261 | 0.041199 | -0.036621 | 0.45319 | 56.7993 | -0.2243 | 57.0419 | 0.01831 | -0.10529 | 0 | 0.13275 | 0.30212 | 0.28381 | -0.054931 | 0.3891 | 0.050354 | 0.6958 | 123.2162 | 0.40741 | 123.2483 | 123.2941 | 123.1155 | 123.0515 | 123.0103 | -123.2529 | -123.1155 | 122.9736 | 123.143 | 53.508 | 49.704
1081.8906 | 123.2803 | -58.4747 | 64.5401 | -0.12512 | 0.0062015 | 0.061367 | 0.068859 | 0.00072213 | -0.0016663 | 0.00043363 | -0.084747 | 0.0046206 | 0.06683 | 0.064106 | -0.0096686 | 0.0058982 | -0.00078406 | -5.072 | 64.5676 | -58.6853 | 64.4943 | -58.0399 | -58.6945 | -1.6754 | -8.7708 | 64.563 | -58.5526 | 64.6729 | -58.168 | -58.5114 | -58.1909 | -0.21057 | 0.027466 | -0.045776 | 0.43487 | 56.7993 | -0.21973 | 57.0099 | -0.009155 | -0.07782 | 0.022888 | 0.13275 | 0.3067 | 0.28381 | -0.036622 | 0.36163 | 0.041198 | 0.64545 | 123.1796 | 0.38452 | 123.2254 | 123.2529 | 123.1155 | 123.0423 | 123.0377 | -123.2254 | -123.0927 | 122.9691 | 123.1476 | 53.4027 | 49.704
1082.875 | 123.3215 | -58.4564 | 64.5767 | -0.10223 | 0.0023563 | 0.062222 | 0.067577 | 0.0013629 | -0.00038447 | -0.003198 | 0.0037536 | 0.003339 | 0.066189 | 0.060261 | -0.0096686 | 0.0067526 | -0.0042021 | -5.0354 | 64.6179 | -58.6807 | 64.4806 | -58.0444 | -58.6533 | -1.6708 | -8.8257 | 64.5996 | -58.5297 | 64.65 | -58.1497 | -58.4976 | -58.1863 | -0.2243 | 0.041199 | -0.09613 | 0.41199 | 56.7856 | -0.19684 | 57.0099 | 0.027466 | -0.073242 | 0.022888 | 0.073242 | 0.3067 | 0.27008 | -0.041199 | 0.34332 | 0.032043 | 0.63629 | 123.1613 | 0.37994 | 123.1796 | 123.2986 | 123.1293 | 123.0743 | 123.056 | -123.2574 | -123.1064 | 122.937 | 123.1064 | 53.421 | 49.6307
1083.8906 | 123.2437 | -58.4564 | 64.5721 | -0.071716 | 0.00086086 | 0.062436 | 0.067364 | 0.0011493 | -0.00038447 | 0.00086083 | -0.017609 | 0.0024844 | 0.065762 | 0.066242 | -0.0090278 | 0.0067526 | -0.0033475 | -5.0629 | 64.6042 | -58.7082 | 64.444 | -58.0536 | -58.6899 | -1.7349 | -8.876 | 64.595 | -58.5388 | 64.6225 | -58.1955 | -58.5526 | -58.2321 | -0.25177 | 0.032043 | -0.12817 | 0.40283 | 56.7215 | -0.23346 | 56.9733 | 0.018311 | -0.082397 | 0.022888 | 0.050354 | 0.26093 | 0.2243 | -0.09613 | 0.3067 | -0.013733 | 0.6546 | 123.1522 | 0.34332 | 123.1613 | 123.3124 | 123.1338 | 123.0606 | 123.0515 | -123.2803 | -123.111 | 122.9004 | 123.0789 | 53.3936 | 49.5804
1084.875 | 123.2208 | -58.4976 | 64.6042 | -0.041199 | 0.00022006 | 0.062436 | 0.070568 | -0.0012005 | -0.0040161 | 0.00064723 | -0.081696 | 0.003339 | 0.067898 | 0.071369 | -0.0083868 | 0.0069662 | 0.0011385 | -5.0903 | 64.6545 | -58.7219 | 64.4257 | -58.0948 | -58.7082 | -1.767 | -8.931 | 64.65 | -58.5571 | 64.5859 | -58.2321 | -58.5892 | -58.287 | -0.2243 | 0.050354 | -0.17853 | 0.40283 | 56.7307 | -0.21057 | 56.955 | 0.013733 | -0.059509 | 0.045776 | -0.018311 | 0.2655 | 0.21057 | -0.091552 | 0.27008 | -0.032043 | 0.62714 | 123.1476 | 0.32501 | 123.143 | 123.3765 | 123.2071 | 123.1522 | 123.1476 | -123.3261 | -123.1613 | 122.9233 | 123.0835 | 53.4073 | 49.5667
1085.8906 | 123.2666 | -58.5342 | 64.5309 | -0.086975 | 0.0021427 | 0.062649 | 0.070355 | 0.0026447 | -0.0046571 | -0.0034116 | -0.084747 | 0.0037662 | 0.067898 | 0.068592 | -0.0083868 | 0.0067526 | 0.00028414 | -5.1453 | 64.6042 | -58.7585 | 64.3982 | -58.1223 | -58.7677 | -1.8402 | -8.9676 | 64.5676 | -58.6029 | 64.5996 | -58.1314 | -58.8593 | -58.3237 | -0.2243 | 0.073242 | -0.13275 | 0.41199 | 56.694 | -0.23346 | 56.9183 | -0.009155 | -0.068664 | 0.036621 | 0.068664 | 0.40283 | 0.21057 | -0.32501 | 0.27924 | -0.25635 | 0.63629 | 123.1567 | 0.4715 | 123.2025 | 123.3627 | 123.1705 | 123.1384 | 123.1018 | -123.2895 | -123.1338 | 122.9324 | 123.1338 | 53.389 | 49.5667
1086.875 | 123.1705 | -58.4976 | 64.5859 | 0.057984 | -0.00042094 | 0.062863 | 0.069927 | 0.0034991 | -0.0012391 | 6.432e-06 | -0.032867 | 0.0054752 | 0.067898 | 0.062397 | -0.007746 | 0.0050436 | 0.00049774 | -5.2597 | 64.65 | -58.7265 | 64.4119 | -58.0811 | -58.7128 | -1.7761 | -8.9813 | 64.6271 | -58.5434 | 64.5721 | -58.2367 | -58.5892 | -58.2962 | -0.22888 | 0.064087 | -0.17395 | 0.41656 | 56.7215 | -0.21515 | 56.9504 | 0.013732 | -0.045776 | 0.041199 | -0.013732 | 0.26093 | 0.20142 | -0.091552 | 0.24719 | -0.045776 | 0.64545 | 123.1384 | 0.3067 | 123.1155 | 123.3765 | 123.1705 | 123.1476 | 123.1247 | -123.3124 | -123.1293 | 122.9095 | 123.0698 | 53.2379 | 49.5163
1087.9062 | 123.2895 | -58.5251 | 64.5218 | -0.10223 | 0.0038517 | 0.062436 | 0.068218 | 0.0024311 | -0.0014527 | 0.0015018 | -0.038971 | 0.0018436 | 0.065975 | 0.065602 | -0.0075324 | 0.0067526 | -0.00099766 | -5.1453 | 64.5401 | -58.7082 | 64.4806 | -58.0032 | -58.6899 | -1.8082 | -8.9355 | 64.5401 | -58.5617 | 64.6545 | -58.1909 | -58.548 | -58.2184 | -0.18311 | 0.01831 | -0.041199 | 0.52185 | 56.7169 | -0.1648 | 56.9 | 0.018311 | -0.036622 | 0.01831 | 0.13275 | 0.33417 | 0.3067 | -0.022889 | 0.34332 | 0.013733 | 0.70496 | 123.1888 | 0.37079 | 123.2162 | 123.2483 | 123.1018 | 123.0652 | 123.0652 | -123.23 | -123.0835 | 123.0057 | 123.1796 | 53.3798 | 49.5895
1088.875 | 123.2574 | -58.4702 | 64.5264 | -0.071716 | 0.0029971 | 0.062436 | 0.069927 | 0.0022173 | -0.0027345 | -0.002557 | -0.02066 | 0.0020572 | 0.068325 | 0.067951 | -0.007746 | 0.0069662 | -0.0037747 | -5.2505 | 64.5767 | -58.7357 | 64.444 | -58.0765 | -58.7265 | -1.8539 | -9.0408 | 64.5584 | -58.5846 | 64.5813 | -58.2413 | -58.5571 | -58.2413 | -0.2655 | 0.050354 | -0.082397 | 0.39368 | 56.6162 | -0.25635 | 56.8817 | 0.009156 | -0.11444 | 0.032044 | 0.054932 | 0.22888 | 0.22888 | -0.086975 | 0.34332 | 0.027466 | 0.65918 | 123.1796 | 0.34332 | 123.1659 | 123.3124 | 123.143 | 123.0469 | 123.0286 | -123.262 | -123.111 | 122.9141 | 123.0515 | 53.2196 | 49.4293
1089.9062 | 123.2071 | -58.4793 | 64.6225 | -0.041199 | 0.0015019 | 0.060513 | 0.069073 | -0.00098687 | -0.0018799 | -0.0012754 | -0.011505 | 0.0022708 | 0.066403 | 0.065602 | -0.0079596 | 0.0063254 | -0.0044157 | -5.1498 | 64.5676 | -58.7173 | 64.5126 | -58.0307 | -58.6395 | -1.7807 | -8.963 | 64.5859 | -58.5571 | 64.6042 | -58.1955 | -58.548 | -58.2413 | -0.23804 | -0.054932 | -0.10986 | 0.44861 | 56.6986 | -0.16022 | 56.9366 | 0.07782 | -0.07782 | -0.036622 | -0.018311 | 0.28381 | 0.23804 | -0.068665 | 0.31586 | 0.009155 | 0.68664 | 123.23 | 0.36163 | 123.1613 | 123.2849 | 123.143 | 123.0469 | 123.0652 | -123.3398 | -123.1796 | 122.9919 | 123.0835 | 53.3295 | 49.5163
1090.875 | 123.2895 | -58.5022 | 64.5401 | -0.079346 | 0.00086086 | 0.062008 | 0.069927 | 0.0037127 | -0.0012391 | -0.0021298 | -0.0084534 | 0.002698 | 0.067471 | 0.063465 | -0.007746 | 0.0052572 | -0.0012113 | -5.2643 | 64.5721 | -58.7311 | 64.4073 | -58.0856 | -58.7448 | -1.8677 | -9.0683 | 64.5447 | -58.5938 | 64.6042 | -58.223 | -58.5617 | -58.2687 | -0.22888 | 0.032044 | -0.13275 | 0.41657 | 56.6345 | -0.24262 | 56.8634 | -0.013733 | -0.091553 | 0.004578 | 0.064087 | 0.27924 | 0.23346 | -0.05951 | 0.32501 | 0.032043 | 0.64545 | 123.1384 | 0.37079 | 123.1979 | 123.3032 | 123.1384 | 123.0743 | 123.0469 | -123.2712 | -123.1338 | 122.9095 | 123.1064 | 53.2379 | 49.4339
1091.9062 | 123.2712 | -58.5068 | 64.5538 | -0.079346 | 0.0025699 | 0.063717 | 0.068859 | 0.00072213 | -0.0023071 | -0.0027708 | -0.0084534 | 0.00098899 | 0.069607 | 0.06667 | -0.0081732 | 0.006539 | -0.0014249 | -5.2689 | 64.5813 | -58.7219 | 64.4394 | -58.0856 | -58.7219 | -1.8906 | -9.0958 | 64.5355 | -58.5754 | 64.6088 | -58.2001 | -58.5434 | -58.2458 | -0.21515 | 0.027466 | -0.11444 | 0.42114 | 56.6162 | -0.21515 | 56.8314 | 0 | -0.068664 | -0.018311 | 0.054932 | 0.3067 | 0.26093 | -0.036621 | 0.32959 | 0.032043 | 0.63629 | 123.1613 | 0.37537 | 123.1842 | 123.3032 | 123.111 | 123.0881 | 123.0423 | -123.2758 | -123.1293 | 122.9462 | 123.1155 | 53.2379 | 49.411
1092.8594 | 123.2758 | -58.5159 | 64.5126 | -0.10223 | 0.00022006 | 0.063504 | 0.068859 | 0.0013629 | -0.0020935 | -0.0046934 | -0.032867 | 0.0029116 | 0.065548 | 0.060261 | -0.0079596 | 0.0078208 | -0.00014306 | -5.2872 | 64.5447 | -58.7265 | 64.4531 | -58.0353 | -58.7219 | -1.918 | -9.0866 | 64.5081 | -58.58 | 64.6179 | -58.2275 | -58.5709 | -58.2504 | -0.21057 | 0.032044 | -0.059509 | 0.48065 | 56.5979 | -0.20599 | 56.8085 | 0.004577 | -0.064087 | -0.004577 | 0.10529 | 0.28839 | 0.2655 | -0.054932 | 0.32959 | 0.009155 | 0.69122 | 123.1796 | 0.35248 | 123.1979 | 123.2712 | 123.0881 | 123.0606 | 123.024 | -123.2391 | -123.0927 | 122.9691 | 123.1338 | 53.2288 | 49.4293
1093.8906 | 123.1934 | -58.548 | 64.5309 | -0.15564 | 0.0036381 | 0.063717 | 0.072277 | 0.00072213 | -0.0016663 | -0.00063437 | -0.10916 | 0.0069706 | 0.065762 | 0.067524 | -0.006037 | 0.0067526 | -0.00057046 | -5.3879 | 64.5905 | -58.786 | 64.325 | -58.2138 | -58.8593 | -2.0462 | -9.2789 | 64.5584 | -58.6304 | 64.5218 | -58.3694 | -58.7082 | -58.3649 | -0.23804 | 0.059509 | -0.20599 | 0.33417 | 56.5018 | -0.31128 | 56.7398 | -0.073242 | -0.082397 | 0.027466 | -0.009155 | 0.17853 | 0.18311 | -0.16022 | 0.2655 | -0.07782 | 0.57221 | 123.111 | 0.26092 | 123.1522 | 123.3765 | 123.1888 | 123.1384 | 123.1064 | -123.317 | -123.1613 | 122.8729 | 123.0698 | 53.1601 | 49.2691
1094.875 | 123.2941 | -58.5159 | 64.5126 | -0.071716 | 0.00086086 | 0.062863 | 0.067791 | 0.00072213 | -0.0042297 | -0.0034116 | 0.0037536 | 0.0031254 | 0.068325 | 0.065815 | -0.0064642 | 0.0054708 | -0.0014249 | -5.3696 | 64.5401 | -58.7631 | 64.4119 | -58.0902 | -58.7311 | -1.9318 | -9.1782 | 64.5401 | -58.6121 | 64.595 | -58.2321 | -58.5388 | -58.2504 | -0.24719 | 0.027466 | -0.10071 | 0.42572 | 56.5842 | -0.21515 | 56.8314 | 0.032044 | -0.096131 | 0.027466 | 0.082398 | 0.28381 | 0.2655 | -0.022888 | 0.36163 | 0.073243 | 0.67291 | 123.175 | 0.37994 | 123.2071 | 123.3032 | 123.1522 | 123.056 | 123.056 | -123.2758 | -123.1247 | 122.9279 | 123.111 | 53.1464 | 49.3378
1095.8906 | 123.2895 | -58.5159 | 64.4852 | -0.056457 | 0.0029971 | 0.062222 | 0.072918 | 0.0024311 | -0.00038447 | 0.0057742 | -0.11832 | 0.0039798 | 0.067898 | 0.065174 | -0.0073188 | 0.0073936 | -0.0044157 | -5.4382 | 64.563 | -58.8135 | 64.2517 | -58.2092 | -58.5068 | -1.9318 | -9.169 | 64.5081 | -58.6121 | 64.5905 | -58.2321 | -58.5938 | -58.2687 | -0.29755 | 0.07782 | -0.23346 | 0.3067 | 56.5842 | 0.009155 | 56.8817 | 0.3067 | -0.096131 | 0.022889 | 0.10529 | 0.28381 | 0.24719 | -0.07782 | 0.34332 | 0.018311 | 0.60425 | 123.0652 | 0.37994 | 123.2025 | 123.3765 | 123.1201 | 123.0789 | 123.024 | -123.2986 | -123.0972 | 122.7676 | 123.1064 | 53.0777 | 49.3469
1096.8594 | 123.4772 | -58.5342 | 64.476 | -0.10223 | 0.0047061 | 0.059872 | 0.070141 | -0.00077327 | 0.00046993 | 0.0015018 | -0.078644 | 0.003339 | 0.065548 | 0.061329 | -0.0081732 | 0.006539 | 0.0015659 | -5.4153 | 64.5218 | -58.754 | 64.4165 | -58.0811 | -58.7494 | -2.0142 | -9.2056 | 64.5218 | -58.6212 | 64.5767 | -58.2687 | -58.6075 | -58.1726 | -0.21973 | 0.045777 | -0.059509 | 0.45319 | 56.5201 | -0.21515 | 56.7398 | 0.004577 | -0.086975 | 0.045777 | 0.10071 | 0.2655 | 0.36163 | -0.073242 | 0.44861 | 0.013733 | 0.67291 | 123.1705 | 0.35248 | 123.1979 | 123.2758 | 123.143 | 123.056 | 123.056 | -123.23 | -123.0972 | 122.9507 | 123.111 | 53.1189 | 49.3286
1097.8906 | 123.2529 | -58.5434 | 64.5081 | -0.086975 | 0.0034245 | 0.063931 | 0.0695 | -0.0016279 | -0.0025207 | -0.0010618 | -0.10611 | 0.0048344 | 0.070675 | 0.07201 | -0.008814 | 0.0071798 | -0.00057046 | -5.4337 | 64.5584 | -58.7769 | 64.4073 | -58.1268 | -58.754 | -2.0691 | -9.2468 | 64.5493 | -58.6487 | 64.5401 | -58.3008 | -58.6624 | -58.3237 | -0.23346 | 0.050354 | -0.10071 | 0.41656 | 56.4743 | -0.21057 | 56.7078 | 0.022888 | -0.10529 | 0.041198 | 0.032043 | 0.24262 | 0.21973 | -0.11902 | 0.32501 | -0.013733 | 0.65002 | 123.1842 | 0.3479 | 123.1888 | 123.3353 | 123.1979 | 123.1018 | 123.0927 | -123.2849 | -123.1567 | 122.9507 | 123.0835 | 53.1097 | 49.2966
1098.875 | 123.2758 | -58.5022 | 64.476 | -0.10223 | 0.0040653 | 0.063717 | 0.066937 | -0.00034607 | -0.0031617 | -0.0034116 | -0.0023498 | 0.0014164 | 0.065975 | 0.067097 | -0.007105 | 0.0050436 | 0.0017795 | -5.4382 | 64.5584 | -58.7585 | 64.4302 | -58.0719 | -58.6945 | -1.9867 | -9.2194 | 64.5126 | -58.6075 | 64.6133 | -57.692 | -58.5022 | -58.5114 | -0.25635 | 0.082398 | -0.045776 | 0.4303 | 56.5155 | -0.19226 | 56.7719 | 0.064087 | -0.10529 | 0.036621 | 0.13733 | 0.81024 | -0.009156 | 0 | 0.09613 | 0.10529 | 0.68665 | 123.1888 | 0.91553 | 123.2208 | 123.317 | 123.1201 | 123.0606 | 123.0148 | -123.2346 | -123.0835 | 122.9324 | 123.1155 | 53.064 | 49.2828
1099.9062 | 123.2483 | -58.5068 | 64.5447 | -0.12512 | 0.0023563 | 0.061795 | 0.068218 | 0.00072213 | 4.273e-05 | -0.0012754 | -0.035919 | 0.0022708 | 0.066616 | 0.066883 | -0.007746 | 0.0069662 | -0.00078406 | -5.4474 | 64.5584 | -58.7402 | 64.4577 | -58.0582 | -58.699 | -2.0233 | -9.2194 | 64.5309 | -58.6029 | 64.5676 | -58.255 | -58.5892 | -58.2825 | -0.23346 | 0.013733 | -0.086975 | 0.44861 | 56.4835 | -0.19226 | 56.7169 | 0.041198 | -0.09613 | -0.013733 | 0.022888 | 0.25177 | 0.2243 | -0.082397 | 0.32043 | 0.013733 | 0.68207 | 123.1979 | 0.3479 | 123.1705 | 123.2986 | 123.1338 | 123.0652 | 123.0377 | -123.2849 | -123.1476 | 122.9645 | 123.0743 | 53.0594 | 49.2874
1100.8594 | 123.2803 | -58.5709 | 64.4943 | -0.10986 | 0.0025699 | 0.056241 | 0.070141 | -0.0029095 | -0.0016663 | -0.00063437 | -0.017609 | 0.00077539 | 0.068539 | 0.061329 | -0.009455 | 0.0054708 | 7.0538e-05 | -5.397 | 64.5538 | -58.7585 | 64.3662 | -58.0994 | -58.8501 | -2.1332 | -9.3521 | 64.5035 | -58.6395 | 64.5401 | -58.2916 | -58.6166 | -58.2962 | -0.18768 | 0.059509 | -0.12817 | 0.4715 | 56.4377 | -0.27924 | 56.6254 | -0.091553 | -0.068664 | 0.009155 | 0.045776 | 0.27924 | 0.27466 | -0.045776 | 0.34332 | 0.022888 | 0.65918 | 123.1247 | 0.3479 | 123.1796 | 123.3124 | 123.143 | 123.1247 | 123.0743 | -123.2529 | -123.1338 | 122.937 | 123.111 | 53.1738 | 49.2188
1101.9062 | 123.2986 | -58.5571 | 64.5035 | -0.064087 | 0.0036381 | 0.063504 | 0.068646 | 0.0047809 | -0.0023071 | -0.0023434 | -0.0084534 | 0.0020572 | 0.068112 | 0.059193 | -0.010096 | 0.0058982 | 0.00028414 | -5.5481 | 64.5493 | -58.786 | 64.3982 | -58.1223 | -58.754 | -2.0874 | -9.3155 | 64.5035 | -58.6121 | 64.5813 | -58.255 | -58.5526 | -58.2733 | -0.22888 | 0.045776 | -0.10529 | 0.43488 | 56.4697 | -0.19684 | 56.6986 | 0.032044 | -0.054932 | 0 | 0.07782 | 0.30212 | 0.28381 | 0.004578 | 0.33875 | 0.05951 | 0.66376 | 123.1842 | 0.35706 | 123.1934 | 123.3353 | 123.1155 | 123.1064 | 123.0606 | -123.2895 | -123.1155 | 122.9553 | 123.1384 | 53.009 | 49.2416
1102.8594 | 123.2712 | -58.5251 | 64.4623 | -0.14038 | 0.0023563 | 0.061367 | 0.069073 | 0.00029473 | 0.00046993 | -0.0034116 | -0.066437 | 0.0024844 | 0.067044 | 0.062397 | -0.0079596 | 0.0076072 | 0.00071134 | -5.5618 | 64.4943 | -58.8135 | 64.3936 | -58.0948 | -58.7677 | -2.1469 | -9.3384 | 64.4577 | -58.6578 | 64.5721 | -58.2916 | -58.6304 | -58.2916 | -0.28839 | 0.032044 | -0.068664 | 0.4303 | 56.3782 | -0.24262 | 56.6666 | 0.045777 | -0.13275 | -0.004577 | 0.10986 | 0.23346 | 0.23346 | -0.10529 | 0.36621 | 0.027466 | 0.71869 | 123.2071 | 0.36621 | 123.23 | 123.3078 | 123.1155 | 123.0194 | 122.9828 | -123.2758 | -123.1201 | 122.9187 | 123.0972 | 52.9633 | 49.1867
1103.9062 | 123.2895 | -58.5205 | 64.5035 | -0.079346 | 0.00086086 | 0.061581 | 0.070141 | 8.1126e-05 | -0.0020935 | -0.0019162 | 0.00070198 | 0.0039798 | 0.06918 | 0.067951 | -0.008814 | 0.006539 | -0.0027067 | -5.6076 | 64.5172 | -58.7952 | 64.4028 | -58.1314 | -58.7677 | -2.124 | -9.375 | 64.4852 | -58.6166 | 64.5813 | -58.2687 | -58.5846 | -58.2962 | -0.27466 | 0.013733 | -0.10071 | 0.3891 | 56.3965 | -0.24719 | 56.6711 | 0.027466 | -0.09613 | -0.018311 | 0.07782 | 0.25177 | 0.2243 | -0.064087 | 0.32043 | 0.032043 | 0.66376 | 123.1979 | 0.3479 | 123.1979 | 123.3124 | 123.1018 | 123.0377 | 123.0057 | -123.2986 | -123.1201 | 122.9233 | 123.1018 | 52.9129 | 49.1455
1104.875 | 123.1567 | -58.5938 | 64.5126 | -0.01831 | 0.0038517 | 0.064145 | 0.073986 | 0.0017901 | -0.0046571 | -0.003198 | -0.24649 | 0.00163 | 0.066616 | 0.067951 | -0.008814 | 0.0054708 | -0.0016385 | -5.6442 | 64.5447 | -58.8318 | 64.3341 | -58.2321 | -58.8684 | -2.4261 | -9.2606 | 64.5355 | -58.6624 | 64.5126 | -58.4427 | -58.7219 | -58.3878 | -0.23804 | 0.032044 | -0.17853 | 0.36163 | 56.1676 | -0.27466 | 56.4056 | -0.036621 | -0.068665 | 0.022888 | 0 | 0.15106 | 0.20599 | -0.12817 | 0.27466 | -0.059509 | 0.59967 | 123.1659 | 0.21973 | 123.175 | 123.3765 | 123.1979 | 123.1384 | 123.1293 | -123.3444 | -123.175 | 122.9279 | 123.1064 | 52.9495 | 49.3332
1105.8906 | 123.3215 | -58.5617 | 64.4394 | 0.012207 | 0.0017155 | 0.064572 | 0.069714 | 0.0020037 | -0.0010255 | -0.00042077 | -0.090851 | 0.0022708 | 0.064907 | 0.067951 | -0.009455 | 0.0076072 | -0.0014249 | -5.69 | 64.4852 | -58.8318 | 64.3799 | -58.1589 | -58.7677 | -2.2293 | -9.4482 | 64.4623 | -58.6258 | 64.5721 | -58.2916 | -58.6258 | -58.2916 | -0.27008 | 0.045776 | -0.059509 | 0.40283 | 56.3324 | -0.20599 | 56.6025 | 0.064087 | -0.064086 | 0.022888 | 0.13275 | 0.27008 | 0.27008 | -0.064086 | 0.33417 | 0 | 0.67291 | 123.2117 | 0.33417 | 123.1979 | 123.317 | 123.0881 | 123.0469 | 123.024 | -123.2712 | -123.0652 | 122.9416 | 123.1339 | 52.8717 | 49.1135
1106.875 | 123.2025 | -58.5846 | 64.5218 | 0.15717 | 0.00086086 | 0.063504 | 0.069714 | -0.0022687 | -0.0033753 | -0.0036252 | -0.07254 | 0.0035526 | 0.065548 | 0.063038 | -0.0079596 | 0.0054708 | -0.00035666 | -5.8365 | 64.5538 | -58.7997 | 64.3341 | -58.2138 | -58.8089 | -2.2293 | -9.5032 | 64.5538 | -58.6578 | 64.4806 | -58.3557 | -58.6807 | -58.374 | -0.21515 | 0.032043 | -0.18768 | 0.37079 | 56.3553 | -0.2243 | 56.5704 | -0.009155 | -0.073242 | 0.032043 | -0.041199 | 0.22888 | 0.21057 | -0.09613 | 0.28381 | -0.022888 | 0.58594 | 123.1338 | 0.30212 | 123.1384 | 123.3536 | 123.2117 | 123.1384 | 123.1384 | -123.3215 | -123.1796 | 122.9187 | 123.0652 | 52.7481 | 49.0814
1107.8594 | 123.2437 | -58.5846 | 64.4394 | -0.14801 | 0.00064726 | 0.064999 | 0.066937 | 0.00072213 | -0.00081187 | -0.00084817 | -0.0084534 | 0.0039798 | 0.068966 | 0.065815 | -0.0056098 | 0.0050436 | -0.0022793 | -5.7312 | 64.5081 | -58.7952 | 64.3707 | -58.1543 | -58.8181 | -2.2705 | -9.2194 | 64.4943 | -58.6487 | 64.563 | -58.3786 | -58.6899 | -58.3328 | -0.21057 | 0.068665 | -0.068664 | 0.4303 | 56.3141 | -0.23346 | 56.5247 | -0.022888 | -0.064087 | 0.054932 | 0.1236 | 0.20599 | 0.25177 | -0.10529 | 0.31586 | -0.041198 | 0.64087 | 123.1659 | 0.27008 | 123.2117 | 123.3032 | 123.143 | 123.0927 | 123.0789 | -123.2346 | -123.0881 | 122.9553 | 123.1476 | 52.8534 | 49.3652
1108.8594 | 123.2986 | -58.5983 | 64.4257 | -0.10986 | 0.0049197 | 0.062436 | 0.069286 | -0.00013247 | -0.0031617 | -0.0027708 | -0.038971 | 0.0022708 | 0.06918 | 0.061329 | -0.0068914 | 0.0061118 | -0.0016385 | -5.7312 | 64.4577 | -58.8089 | 64.3707 | -58.1314 | -58.7997 | -2.298 | -9.5169 | 64.4485 | -58.6761 | 64.563 | -58.3145 | -58.6212 | -58.3191 | -0.21057 | 0.032044 | -0.054931 | 0.46692 | 56.3004 | -0.20142 | 56.5109 | 0.009155 | -0.077819 | 0.022888 | 0.13733 | 0.28381 | 0.27924 | -0.022888 | 0.35706 | 0.054931 | 0.67749 | 123.1796 | 0.36163 | 123.2391 | 123.2666 | 123.1247 | 123.056 | 123.0469 | -123.2346 | -123.1018 | 122.9691 | 123.1613 | 52.8671 | 49.0814
1109.9062 | 123.175 | -58.5526 | 64.4394 | -0.079346 | 0.0019291 | 0.061154 | 0.069073 | -0.00013247 | -0.0014527 | -0.00042077 | -0.011505 | 0.0020572 | 0.067684 | 0.063038 | -0.007105 | 0.0052572 | -0.0024931 | -5.7587 | 64.5172 | -58.8181 | 64.389 | -58.136 | -58.7585 | -2.2476 | -9.5215 | 64.4531 | -58.6533 | 64.3387 | -57.8613 | -58.3328 | -58.223 | -0.2655 | 0.07782 | -0.050354 | 0.41656 | 56.3049 | -0.20599 | 56.5704 | 0.059509 | -0.10071 | 0.013733 | -0.10071 | 0.69122 | 0.32959 | 0.21973 | 0.4303 | 0.32043 | 0.68207 | 123.2071 | 0.79193 | 122.9919 | 123.3353 | 123.1064 | 123.0698 | 123.0057 | -123.2574 | -123.0927 | 122.9416 | 122.8912 | 52.7939 | 49.0311
1110.8594 | 123.2712 | -58.5892 | 64.444 | -0.048828 | 0.0023563 | 0.062436 | 0.06715 | 0.0013629 | -0.0020935 | -0.0046934 | -0.0084534 | 0.0035526 | 0.068112 | 0.058766 | -0.0066778 | 0.0054708 | -0.0035611 | -5.8319 | 64.476 | -58.7906 | 64.3387 | -58.1818 | -58.8089 | -2.3392 | -9.6405 | 64.4623 | -58.6761 | 64.5218 | -58.3557 | -58.6624 | -58.342 | -0.20142 | 0.032043 | -0.10529 | 0.40741 | 56.25 | -0.21973 | 56.4514 | -0.018311 | -0.086975 | 0.01831 | 0.07782 | 0.23346 | 0.24719 | -0.073243 | 0.33417 | 0.013732 | 0.60883 | 123.1293 | 0.32043 | 123.1979 | 123.2666 | 123.1384 | 123.0652 | 123.0515 | -123.2346 | -123.1201 | 122.9279 | 123.111 | 52.7573 | 48.9487
1111.8906 | 123.317 | -58.5983 | 64.4073 | -0.11749 | 0.00086086 | 0.062863 | 0.071423 | 0.00072213 | -0.0027345 | 0.001929 | -0.084747 | 0.0035526 | 0.068539 | 0.06432 | -0.0073188 | 0.0084616 | -0.0031339 | -5.8228 | 64.4485 | -58.8226 | 64.389 | -58.1543 | -58.8135 | -2.3483 | -9.5947 | 64.4302 | -58.6716 | 64.5538 | -58.3282 | -58.6533 | -58.3191 | -0.2243 | 0.041198 | -0.018311 | 0.44403 | 56.25 | -0.21515 | 56.4743 | 0.009155 | -0.073242 | 0.022888 | 0.14648 | 0.27008 | 0.27924 | -0.054931 | 0.35248 | 0.018311 | 0.66833 | 123.2117 | 0.34332 | 123.2254 | 123.2712 | 123.1018 | 123.0469 | 123.0286 | -123.23 | -123.0789 | 122.9874 | 123.1522 | 52.7756 | 49.0036
1112.8594 | 123.3398 | -58.5571 | 64.4623 | -0.086975 | 0.0029971 | 0.060299 | 0.069286 | -0.0035505 | -0.0029481 | -0.003198 | -0.02066 | 0.0039798 | 0.067257 | 0.059834 | -0.0086004 | 0.0052572 | -0.0044157 | -5.7953 | 64.4989 | -58.7997 | 64.4211 | -58.0994 | -58.7265 | -2.2934 | -9.5352 | 64.4623 | -58.6487 | 64.563 | -58.2642 | -58.5938 | -58.287 | -0.24261 | 0.036621 | -0.041198 | 0.45776 | 56.2637 | -0.16937 | 56.5063 | 0.073243 | -0.091553 | 0 | 0.10071 | 0.29297 | 0.27008 | -0.036621 | 0.36163 | 0.054932 | 0.70038 | 123.2208 | 0.38452 | 123.2117 | 123.2986 | 123.111 | 123.056 | 123.0194 | -123.262 | -123.111 | 122.9782 | 123.1201 | 52.7618 | 49.0219
1113.8906 | 123.1796 | -58.6533 | 64.4485 | -0.086975 | 0.0015019 | 0.06329 | 0.070355 | 0.0045673 | 0.00089713 | 0.0017154 | -0.12442 | 0.0041934 | 0.069821 | 0.067311 | -0.0081732 | 0.0078208 | -0.0016385 | -5.9189 | 64.4943 | -58.8867 | 64.2654 | -58.3282 | -58.9462 | -2.5177 | -9.8145 | 64.4806 | -58.7082 | 64.4394 | -58.4702 | -58.7906 | -58.4381 | -0.23346 | 0.045777 | -0.18311 | 0.32501 | 56.1356 | -0.29297 | 56.369 | -0.059509 | -0.054932 | 0.032044 | -0.009155 | 0.1831 | 0.21515 | -0.13733 | 0.27008 | -0.082397 | 0.55847 | 123.1522 | 0.23804 | 123.1476 | 123.381 | 123.1888 | 123.1476 | 123.1338 | -123.3353 | -123.1567 | 122.9187 | 123.0927 | 52.7344 | 48.8388
1114.8594 | 123.2758 | -58.5938 | 64.4302 | -0.10223 | 0.0036381 | 0.065213 | 0.068859 | 8.1126e-05 | -0.0014527 | -0.0017026 | 0.0037536 | 0.0020572 | 0.068325 | 0.061115 | -0.0081732 | 0.0063254 | -0.0018521 | -5.9143 | 64.4531 | -58.8272 | 64.325 | -58.2138 | -58.8364 | -2.3987 | -9.7275 | 64.4577 | -58.699 | 64.5035 | -58.3374 | -58.6624 | -58.3466 | -0.23346 | 0.022888 | -0.10529 | 0.37994 | 56.1951 | -0.24262 | 56.4285 | -0.009156 | -0.10529 | 0.027466 | 0.073242 | 0.25635 | 0.24719 | -0.068665 | 0.35248 | 0.036621 | 0.6134 | 123.1522 | 0.36163 | 123.2025 | 123.2803 | 123.1567 | 123.0469 | 123.0515 | -123.2574 | -123.1293 | 122.9187 | 123.0972 | 52.6794 | 48.8663
1115.9062 | 123.317 | -58.5983 | 64.4302 | -0.086975 | 0.0010745 | 0.061795 | 0.068646 | 0.00050853 | -0.0012391 | -0.0027708 | -0.026764 | 0.0031254 | 0.064907 | 0.067097 | -0.007746 | 0.0063254 | -0.0035611 | -5.8594 | 64.4943 | -58.8089 | 64.4211 | -58.1085 | -58.7357 | -2.3438 | -9.6039 | 64.4394 | -58.6533 | 64.5538 | -58.2733 | -58.5938 | -58.3145 | -0.21057 | 0.064087 | -0.009155 | 0.48981 | 56.2546 | -0.13733 | 56.4651 | 0.073242 | -0.054931 | 0.009155 | 0.1236 | 0.32501 | 0.28381 | 0.004578 | 0.33874 | 0.059509 | 0.70038 | 123.23 | 0.37994 | 123.2071 | 123.3032 | 123.0927 | 123.0927 | 123.0377 | -123.2391 | -123.0835 | 123.0194 | 123.1522 | 52.739 | 48.9944
1116.8594 | 123.2574 | -58.6166 | 64.4485 | -0.071716 | 0.0032107 | 0.063931 | 0.068432 | 0.0034991 | -0.0031617 | 6.432e-06 | -0.032867 | 0.003339 | 0.065335 | 0.065602 | -0.0066778 | 0.0080344 | -0.0016385 | -6.0013 | 64.4165 | -58.8638 | 64.3066 | -58.223 | -58.8593 | -2.4902 | -9.7824 | 64.4257 | -58.7036 | 64.4714 | -58.374 | -58.6807 | -58.3878 | -0.24719 | -0.032043 | -0.14191 | 0.39368 | 56.1264 | -0.24262 | 56.3736 | 0.004578 | -0.086975 | -0.022888 | 0.022889 | 0.24262 | 0.22888 | -0.064087 | 0.31586 | 0.022888 | 0.64087 | 123.1705 | 0.32959 | 123.175 | 123.2803 | 123.1293 | 123.0331 | 123.0423 | -123.3124 | -123.1522 | 122.9233 | 123.0881 | 52.6154 | 48.8342
1117.8906 | 123.2849 | -58.6121 | 64.4257 | -0.071716 | 0.00086086 | 0.063717 | 0.070355 | -0.00034607 | -0.0035889 | -0.0019162 | -0.096954 | 0.002698 | 0.067257 | 0.063465 | -0.0079596 | 0.0093162 | -0.0024931 | -6.0104 | 64.4623 | -58.8913 | 64.2883 | -58.2733 | -58.905 | -2.5314 | -9.938 | 64.4302 | -58.754 | 64.4897 | -58.3603 | -58.7357 | -58.374 | -0.27923 | 0.036621 | -0.13733 | 0.33875 | 56.0806 | -0.29297 | 56.3599 | -0.013733 | -0.14191 | 0.004578 | 0.064087 | 0.25177 | 0.23804 | -0.1236 | 0.37994 | 0.01831 | 0.61798 | 123.1796 | 0.39368 | 123.2437 | 123.3536 | 123.1842 | 123.0743 | 123.0423 | -123.317 | -123.1796 | 122.9004 | 123.1018 | 52.6016 | 48.674
1118.8594 | 123.2986 | -58.6212 | 64.4119 | -0.071716 | 0.0027835 | 0.061795 | 0.068646 | 8.1126e-05 | -0.0031617 | 6.432e-06 | -0.0084534 | 0.0024844 | 0.066189 | 0.064106 | -0.0066778 | 0.0061118 | -0.0029203 | -6.0333 | 64.4531 | -58.8455 | 64.3021 | -58.2138 | -58.8547 | -2.4994 | -9.8236 | 64.4211 | -58.7128 | 64.4989 | -58.374 | -58.6853 | -58.3557 | -0.2243 | 0.041199 | -0.10986 | 0.40741 | 56.1218 | -0.23346 | 56.3461 | -0.009155 | -0.091553 | 0.009156 | 0.086975 | 0.24719 | 0.2655 | -0.064087 | 0.35706 | 0.027466 | 0.63171 | 123.1476 | 0.33875 | 123.2117 | 123.2986 | 123.1339 | 123.0743 | 123.0423 | -123.2574 | -123.1247 | 122.9233 | 123.1201 | 52.5879 | 48.7976
1119.8906 | 123.23 | -58.6441 | 64.4394 | -0.064087 | 0.0015019 | 0.063931 | 0.071423 | -0.0014143 | -0.00081187 | 6.432e-06 | -0.10611 | 0.006757 | 0.066616 | 0.068806 | -0.0083868 | 0.0071798 | -0.0031339 | -6.0059 | 64.4806 | -58.8776 | 64.2975 | -58.2275 | -58.8593 | -2.5314 | -9.8145 | 64.4669 | -58.7128 | 64.4669 | -58.4015 | -58.7494 | -58.4106 | -0.23346 | 0.041199 | -0.14191 | 0.41656 | 56.1127 | -0.21515 | 56.3461 | 0.01831 | -0.068665 | 0.027466 | 0.027466 | 0.24262 | 0.23346 | -0.10529 | 0.30212 | -0.036621 | 0.65002 | 123.175 | 0.31128 | 123.1796 | 123.3582 | 123.1796 | 123.1247 | 123.111 | -123.317 | -123.1522 | 122.9416 | 123.111 | 52.6382 | 48.8297
1120.8594 | 123.3078 | -58.6395 | 64.4119 | -0.086975 | 0.0036381 | 0.062863 | 0.069927 | -0.00055967 | -0.00038447 | -0.0055478 | 0.0037536 | 0.0041934 | 0.068112 | 0.064747 | -0.0081732 | 0.0054708 | 0.00071134 | -6.0699 | 64.4577 | -58.8547 | 64.2975 | -58.2367 | -58.8638 | -2.536 | -9.8511 | 64.4211 | -58.7036 | 64.4852 | -58.3694 | -58.6807 | -58.3786 | -0.21515 | 0.045777 | -0.11444 | 0.40283 | 56.1035 | -0.22431 | 56.3187 | -0.009156 | -0.064087 | 0.009156 | 0.073242 | 0.27008 | 0.26092 | -0.041199 | 0.32501 | 0.022888 | 0.61798 | 123.1522 | 0.33417 | 123.1888 | 123.3124 | 123.1247 | 123.0972 | 123.0606 | -123.2666 | -123.1155 | 122.937 | 123.1247 | 52.5696 | 48.7885
1121.8906 | 123.2803 | -58.6578 | 64.3982 | -0.079346 | 0.0021427 | 0.06329 | 0.070355 | 0.00093573 | -0.0014527 | -0.0034116 | -0.026764 | 0.0012028 | 0.070034 | 0.060902 | -0.008814 | 0.0063254 | -0.0018521 | -6.102 | 64.4257 | -58.8638 | 64.2654 | -58.3878 | -58.5022 | -2.5635 | -9.874 | 64.3753 | -58.7036 | 64.4577 | -58.3923 | -58.7036 | -58.4015 | -0.20599 | 0.027466 | -0.13275 | 0.27008 | 56.0944 | 0.15564 | 56.3004 | 0.36163 | -0.045776 | -0.022888 | 0.05951 | 0.2655 | 0.25635 | -0.045776 | 0.30212 | 0 | 0.47607 | 123.1293 | 0.31128 | 123.1613 | 123.2895 | 123.0789 | 123.0835 | 123.0331 | -123.262 | -123.1018 | 122.9233 | 123.1155 | 52.5558 | 48.7839
1122.8594 | 123.2941 | -58.6166 | 64.4073 | -0.086975 | 0.0032107 | 0.061367 | 0.068218 | -0.0022687 | -0.0023071 | -0.0038388 | -0.023712 | 0.004407 | 0.067257 | 0.065815 | -0.0092414 | 0.0080344 | -0.0044157 | -6.1157 | 64.444 | -58.8501 | 64.3066 | -58.255 | -58.8684 | -2.5726 | -9.8969 | 64.4165 | -58.7357 | 64.4577 | -58.3969 | -58.6853 | -58.3969 | -0.23346 | 0.036621 | -0.10071 | 0.36163 | 56.044 | -0.25177 | 56.2775 | -0.01831 | -0.11902 | 0.009155 | 0.050354 | 0.21973 | 0.21973 | -0.068665 | 0.33875 | 0.050354 | 0.59509 | 123.1567 | 0.33875 | 123.1934 | 123.2941 | 123.1522 | 123.0606 | 123.0331 | -123.2574 | -123.143 | 122.9233 | 123.0743 | 52.5009 | 48.7198
1123.8906 | 123.3032 | -58.6578 | 64.3982 | -0.071716 | 0.0023563 | 0.062222 | 0.069286 | -0.00077327 | -0.00038447 | -0.001489 | -0.029816 | 0.00163 | 0.065975 | 0.055988 | -0.008814 | 0.0076072 | -0.0016385 | -6.1386 | 64.4257 | -58.8593 | 64.2838 | -58.2504 | -58.8867 | -2.6093 | -9.9609 | 64.3936 | -58.6945 | 64.4577 | -58.4061 | -58.7128 | -58.4015 | -0.20142 | 0.027466 | -0.11444 | 0.40741 | 56.0486 | -0.22888 | 56.25 | -0.027466 | -0.036621 | -0.004577 | 0.05951 | 0.25177 | 0.25635 | -0.054932 | 0.29297 | -0.018311 | 0.60883 | 123.143 | 0.28839 | 123.1522 | 123.2849 | 123.0881 | 123.0835 | 123.0515 | -123.2574 | -123.0927 | 122.9416 | 123.1155 | 52.5192 | 48.6969
1124.875 | 123.2758 | -58.6441 | 64.4485 | -0.041199 | 0.0017155 | 0.062008 | 0.069286 | -0.0037641 | -0.00059807 | -0.0017026 | -0.045074 | 0.0035526 | 0.06683 | 0.064747 | -0.007746 | 0.0091024 | -0.0037747 | -6.0837 | 64.476 | -58.8776 | 64.3158 | -58.2001 | -58.8226 | -2.5772 | -9.874 | 64.4669 | -58.7128 | 64.5355 | -58.4793 | -58.9737 | -58.5388 | -0.23346 | 0.027466 | -0.13275 | 0.44403 | 56.0669 | -0.17853 | 56.3004 | 0.054931 | -0.068665 | 0.018311 | 0.086975 | 0.16479 | 0.10529 | -0.32959 | 0.17395 | -0.26093 | 0.67749 | 123.1934 | 0.23346 | 123.2483 | 123.3536 | 123.1796 | 123.1201 | 123.111 | -123.3261 | -123.1613 | 122.9599 | 123.1796 | 52.5604 | 48.7701
1125.8906 | 123.2712 | -58.6533 | 64.3616 | -0.14038 | 0.0012881 | 0.062008 | 0.0695 | 0.00050853 | -0.0018799 | -0.0029844 | -0.07254 | 0.00163 | 0.067471 | 0.063893 | -0.0068914 | 0.0058982 | -0.0031339 | -6.1661 | 64.4073 | -58.8638 | 64.3021 | -58.2138 | -58.8638 | -2.6596 | -9.9152 | 64.3845 | -58.7082 | 64.4897 | -58.4106 | -58.6899 | -58.3832 | -0.21057 | 0.045777 | -0.059509 | 0.43945 | 55.9937 | -0.21057 | 56.2042 | 0 | -0.054932 | 0.022888 | 0.12817 | 0.24261 | 0.27008 | -0.036621 | 0.32501 | 0.018311 | 0.65002 | 123.1659 | 0.29755 | 123.1979 | 123.2712 | 123.0927 | 123.0606 | 123.0377 | -123.2254 | -123.0698 | 122.9553 | 123.143 | 52.4872 | 48.7381
1126.8594 | 123.2849 | -58.667 | 64.3845 | -0.10986 | 0.00022006 | 0.063717 | 0.071209 | -0.0018415 | -0.0012391 | -0.001489 | -0.0023498 | 0.0031254 | 0.068325 | 0.067738 | -0.009455 | 0.00483 | -0.00078406 | -6.2073 | 64.4302 | -58.8867 | 64.2883 | -58.2687 | -58.8776 | -2.6825 | -9.9976 | 64.4165 | -58.7494 | 64.4577 | -58.4106 | -58.7173 | -58.4106 | -0.21973 | 0.045777 | -0.09613 | 0.39825 | 55.9845 | -0.21057 | 56.2042 | 0.009156 | -0.082398 | 0.032044 | 0.073243 | 0.25635 | 0.25635 | -0.050354 | 0.33874 | 0.032044 | 0.61798 | 123.175 | 0.33874 | 123.2071 | 123.317 | 123.1659 | 123.0972 | 123.0835 | -123.2712 | -123.1338 | 122.9553 | 123.1247 | 52.4597 | 48.6694
1127.9062 | 123.3124 | -58.6304 | 64.389 | -0.079346 | 0.00086086 | 0.064358 | 0.069714 | -0.0012005 | -0.00017087 | -0.0023434 | -0.023712 | 0.004407 | 0.066616 | 0.063679 | -0.0090278 | 0.0052572 | 0.00028414 | -6.1478 | 64.4302 | -58.8593 | 64.3799 | -58.136 | -58.7814 | -2.5909 | -9.8602 | 64.4211 | -58.699 | 64.5081 | -58.3145 | -58.6395 | -58.3603 | -0.22888 | 0.041199 | -0.009155 | 0.49438 | 56.0394 | -0.15106 | 56.2683 | 0.07782 | -0.068665 | 0.032044 | 0.11902 | 0.31586 | 0.27008 | -0.009155 | 0.33875 | 0.05951 | 0.72327 | 123.2391 | 0.38452 | 123.2071 | 123.2895 | 123.1201 | 123.0606 | 123.0515 | -123.2483 | -123.0881 | 123.0103 | 123.1384 | 52.4826 | 48.7701
1128.8594 | 123.2574 | -58.6533 | 64.3707 | -0.10223 | 0.0042789 | 0.062008 | 0.070995 | 0.00072213 | 0.00046993 | -0.00020717 | -0.038971 | 0.00056179 | 0.067898 | 0.062824 | -0.0075324 | 0.0063254 | -0.0018521 | -6.2531 | 64.4119 | -58.8821 | 64.2746 | -58.2733 | -58.9005 | -2.7328 | -10.0204 | 64.4028 | -58.7585 | 64.4485 | -58.4381 | -58.7265 | -58.4061 | -0.22888 | 0.041198 | -0.096131 | 0.37994 | 55.9204 | -0.24719 | 56.1493 | -0.018311 | -0.10529 | 0.032043 | 0.077819 | 0.21515 | 0.24719 | -0.073242 | 0.35248 | 0.032044 | 0.60883 | 123.1567 | 0.32043 | 123.2071 | 123.2941 | 123.1613 | 123.0652 | 123.056 | -123.2529 | -123.1293 | 122.9279 | 123.1018 | 52.4002 | 48.6328
1129.8906 | 123.2529 | -58.6533 | 64.3478 | -0.13275 | 0.0023563 | 0.062222 | 0.070568 | -0.00077327 | -0.00059807 | -0.001489 | -0.07254 | 0.002698 | 0.066189 | 0.065174 | -0.0096686 | 0.0063254 | 0.00049774 | -6.2439 | 64.3845 | -58.873 | 64.2975 | -58.2184 | -58.8821 | -2.7283 | -9.9792 | 64.3753 | -58.7402 | 64.4714 | -58.4381 | -58.7357 | -58.4198 | -0.21973 | 0.036621 | -0.050354 | 0.43487 | 55.925 | -0.22888 | 56.1447 | -0.009155 | -0.086975 | 0.027466 | 0.1236 | 0.21515 | 0.23346 | -0.082398 | 0.32043 | 0.004577 | 0.6546 | 123.1705 | 0.30212 | 123.2117 | 123.2574 | 123.1155 | 123.0377 | 123.0286 | -123.2208 | -123.0881 | 122.9507 | 123.1247 | 52.4094 | 48.674
1130.875 | 123.2986 | -58.6349 | 64.4073 | -0.079346 | 0.0015019 | 0.062649 | 0.068005 | -0.0020551 | -0.0027345 | -0.0017026 | -0.048126 | 0.0039798 | 0.068112 | 0.060688 | -0.0083868 | 0.0056846 | 7.0538e-05 | -6.1981 | 64.444 | -58.8547 | 64.357 | -58.2001 | -58.7952 | -2.6688 | -9.9426 | 64.4028 | -58.6945 | 64.4714 | -58.3786 | -58.6853 | -58.3832 | -0.21973 | 0.036621 | -0.050354 | 0.43488 | 55.9662 | -0.16022 | 56.1859 | 0.059509 | -0.059509 | -0.004578 | 0.064087 | 0.25635 | 0.25177 | -0.050354 | 0.31128 | 0.009155 | 0.6546 | 123.2117 | 0.31586 | 123.1659 | 123.2986 | 123.0972 | 123.0789 | 123.0377 | -123.262 | -123.1018 | 122.9919 | 123.1064 | 52.4368 | 48.6923
1131.8906 | 123.2986 | -58.6578 | 64.357 | -0.071716 | 0.0023563 | 0.06329 | 0.071636 | 0.0030719 | -0.00059807 | -0.0017026 | -0.081696 | 0.0037662 | 0.065975 | 0.06667 | -0.0083868 | 0.0061118 | -0.0031339 | -6.2668 | 64.3799 | -58.9188 | 64.2883 | -58.2642 | -58.8821 | -2.7649 | -10.0342 | 64.3616 | -58.7723 | 64.4897 | -58.4198 | -58.7082 | -58.3923 | -0.26093 | 0.022888 | -0.068665 | 0.39368 | 55.8929 | -0.2243 | 56.1539 | 0.036621 | -0.11444 | 0.004577 | 0.13275 | 0.23804 | 0.2655 | -0.050354 | 0.37994 | 0.064087 | 0.6546 | 123.2071 | 0.35248 | 123.262 | 123.2986 | 123.1338 | 123.0377 | 123.0194 | -123.2758 | -123.1293 | 122.9462 | 123.1476 | 52.3911 | 48.6237
1132.8594 | 123.381 | -58.6395 | 64.3524 | -0.071716 | -0.0014889 | 0.062863 | 0.068218 | -0.00055967 | -0.00017087 | -0.0055478 | -0.026764 | 0.0018436 | 0.068325 | 0.065388 | -0.0075324 | 0.0039756 | -0.00057046 | -6.2759 | 64.4257 | -58.9005 | 64.2883 | -58.223 | -58.8409 | -2.7374 | -10.0296 | 64.3753 | -58.7311 | 64.6088 | -57.9849 | -58.9233 | -58.6945 | -0.26093 | 0.073242 | -0.064087 | 0.41656 | 55.9021 | -0.20142 | 56.163 | 0.05951 | -0.091553 | 0.022888 | 0.25635 | 0.6546 | -0.054932 | -0.28381 | 0.036621 | -0.19226 | 0.67749 | 123.1888 | 0.74616 | 123.3398 | 123.3261 | 123.1064 | 123.0652 | 123.0148 | -123.2529 | -123.0835 | 122.9279 | 123.2483 | 52.3636 | 48.6099
1133.9062 | 123.3124 | -58.6624 | 64.3936 | -0.071716 | 0.0012881 | 0.063717 | 0.068432 | -0.00055967 | -0.00017087 | -0.0040524 | -0.0054016 | 0.00077539 | 0.067044 | 0.065815 | -0.0096686 | 0.0073936 | -0.0016385 | -6.2485 | 64.4165 | -58.8684 | 64.3387 | -58.1635 | -58.7997 | -2.6825 | -9.9609 | 64.3936 | -58.7357 | 64.4943 | -58.3466 | -58.6487 | -58.3786 | -0.20599 | 0.022888 | -0.054932 | 0.49896 | 55.9799 | -0.13733 | 56.1859 | 0.068664 | -0.073242 | 0 | 0.10071 | 0.31586 | 0.28381 | 0.013733 | 0.35706 | 0.086975 | 0.70496 | 123.2071 | 0.3891 | 123.23 | 123.2849 | 123.1293 | 123.0789 | 123.056 | -123.262 | -123.1293 | 123.0011 | 123.1567 | 52.4139 | 48.7015
1134.8594 | 123.3444 | -58.6533 | 64.357 | 0.63782 | 0.0012881 | 0.064145 | 0.069714 | -0.0022687 | -0.0020935 | -0.004266 | 0.0068054 | 0.0041934 | 0.066403 | 0.063893 | -0.007105 | 0.0056846 | -0.0059109 | -6.4911 | 64.4119 | -58.8776 | 64.2563 | -58.2001 | -58.8135 | -2.7557 | -9.9838 | 64.3662 | -58.7173 | 64.5172 | -58.3328 | -58.6533 | -58.3603 | -0.2243 | 0.054931 | -0.10071 | 0.45319 | 55.8975 | -0.16022 | 56.1218 | 0.064086 | -0.064087 | 0.009155 | 0.16022 | 0.32043 | 0.29297 | 0 | 0.35706 | 0.064087 | 0.67749 | 123.1338 | 0.38452 | 123.2346 | 123.2895 | 123.0835 | 123.0652 | 123.0194 | -123.2346 | -123.0743 | 122.9095 | 123.1705 | 52.1622 | 48.6694
1135.8906 | 123.3124 | -58.6624 | 64.3616 | -0.094604 | 0.0019291 | 0.063076 | 0.070568 | 0.0034991 | -0.0014527 | -0.0019162 | -0.078644 | 0.003339 | 0.066403 | 0.068806 | -0.0086004 | 0.0093162 | -0.0046293 | -6.3217 | 64.3478 | -58.9188 | 64.2975 | -58.2458 | -58.8913 | -2.8473 | -10.0708 | 64.3753 | -58.7448 | 64.4623 | -58.4106 | -58.7173 | -58.3878 | -0.25635 | -0.013733 | -0.064087 | 0.41657 | 55.8151 | -0.22888 | 56.0715 | 0.027466 | -0.082397 | 0.013733 | 0.10071 | 0.25177 | 0.27466 | -0.054931 | 0.35706 | 0.027466 | 0.67291 | 123.2162 | 0.33417 | 123.2071 | 123.2666 | 123.1201 | 123.0103 | 123.0377 | -123.2803 | -123.1064 | 122.9599 | 123.1247 | 52.3407 | 48.5916
1136.875 | 123.2803 | -58.667 | 64.3753 | -0.10986 | 0.00022006 | 0.063076 | 0.069286 | 0.0032855 | -0.0014527 | -0.0038388 | -0.05423 | 0.0020572 | 0.065121 | 0.058552 | -0.006037 | 0.0050436 | -0.00078406 | -6.2851 | 64.4257 | -58.8684 | 64.3387 | -58.2047 | -58.8226 | -2.7695 | -10.0525 | 64.4028 | -58.7448 | 64.4577 | -58.4015 | -58.7036 | -58.4015 | -0.20142 | 0.050354 | -0.036621 | 0.46234 | 55.8975 | -0.15564 | 56.0989 | 0.045776 | -0.07782 | 0.027466 | 0.082398 | 0.2655 | 0.2655 | -0.036621 | 0.34332 | 0.041199 | 0.66376 | 123.2071 | 0.34332 | 123.2025 | 123.2941 | 123.1476 | 123.0927 | 123.0698 | -123.2437 | -123.1201 | 123.0057 | 123.1247 | 52.3819 | 48.6145
1137.8906 | 123.2666 | -58.6945 | 64.325 | -0.10986 | 0.00022006 | 0.063076 | 0.069073 | 0.00029473 | -0.00081187 | -0.0027708 | -0.075592 | 0.0024844 | 0.068966 | 0.065602 | -0.0083868 | 0.0084616 | -0.0031339 | -6.3629 | 64.3662 | -58.9096 | 64.2929 | -58.2596 | -58.905 | -2.8656 | -10.1395 | 64.3341 | -58.754 | 64.4394 | -58.4564 | -58.7448 | -58.4335 | -0.21515 | 0.041199 | -0.032043 | 0.43487 | 55.8289 | -0.21057 | 56.044 | 0.004578 | -0.059509 | 0.009155 | 0.11444 | 0.23804 | 0.26093 | -0.050354 | 0.32043 | 0.009155 | 0.65002 | 123.2025 | 0.29755 | 123.1934 | 123.2758 | 123.0881 | 123.0606 | 123.0286 | -123.2346 | -123.0789 | 122.9874 | 123.1338 | 52.3315 | 48.555
1138.875 | 123.2803 | -58.6487 | 64.3845 | -0.10986 | 0.0029971 | 0.06094 | 0.070568 | -0.0039777 | -0.0014527 | -0.0021298 | -0.029816 | 0.0029116 | 0.067898 | 0.063038 | -0.007105 | 0.0039756 | -0.0039883 | -6.3126 | 64.4394 | -58.9096 | 64.3295 | -58.2047 | -58.8181 | -2.7969 | -10.0616 | 64.3982 | -58.7585 | 64.4806 | -58.3832 | -58.6853 | -58.3878 | -0.26093 | 0.054932 | -0.054931 | 0.44403 | 55.8517 | -0.16937 | 56.1127 | 0.091553 | -0.10986 | 0.013733 | 0.096131 | 0.2655 | 0.26093 | -0.036621 | 0.37079 | 0.073242 | 0.70496 | 123.2391 | 0.37537 | 123.2391 | 123.349 | 123.1567 | 123.0881 | 123.0469 | -123.2941 | -123.143 | 122.9782 | 123.1293 | 52.3361 | 48.587
1139.8906 | 123.3078 | -58.6899 | 64.3433 | -0.048828 | 0.0023563 | 0.063504 | 0.070995 | 0.0020037 | -0.0023071 | -0.0012754 | -0.063385 | 0.0039798 | 0.068966 | 0.071156 | -0.0079596 | 0.0084616 | 0.0015659 | -6.3858 | 64.3616 | -58.9142 | 64.2883 | -58.2779 | -58.9096 | -2.9114 | -10.144 | 64.3341 | -58.7814 | 64.4485 | -58.4244 | -58.754 | -58.4198 | -0.22431 | 0.01831 | -0.054932 | 0.41199 | 55.7785 | -0.21973 | 56.0028 | 0.004578 | -0.091553 | -0.009156 | 0.10529 | 0.2655 | 0.27008 | -0.064087 | 0.36163 | 0.027466 | 0.63629 | 123.2025 | 0.35706 | 123.23 | 123.2758 | 123.1155 | 123.0515 | 123.024 | -123.2574 | -123.1247 | 122.9782 | 123.1384 | 52.3041 | 48.5458
1140.8594 | 123.3215 | -58.667 | 64.3478 | -0.12512 | 0.00064726 | 0.061367 | 0.072277 | -0.0031231 | -0.0012391 | -0.0044796 | 0.028168 | 0.0054752 | 0.067471 | 0.063038 | -0.007105 | 0.0056846 | -0.00035666 | -6.3812 | 64.4028 | -58.8959 | 64.0274 | -58.2825 | -58.8409 | -2.9617 | -10.1761 | 64.3478 | -58.7357 | 64.4577 | -58.374 | -58.6624 | -58.3694 | -0.22888 | 0.054932 | -0.32043 | 0.38452 | 55.7053 | -0.17395 | 55.9341 | 0.054932 | -0.068665 | 0 | 0.10986 | 0.29297 | 0.29755 | 0.004577 | 0.36621 | 0.073242 | 0.6134 | 122.9233 | 0.36163 | 123.1934 | 123.2986 | 123.0835 | 123.0698 | 123.0148 | -123.2437 | -123.0835 | 122.6944 | 123.1247 | 52.2858 | 48.4909
1141.9062 | 123.2758 | -58.6853 | 64.3387 | -0.10223 | 0.0015019 | 0.061581 | 0.068646 | 0.0058489 | -0.0014527 | 0.00022003 | 0.00070198 | 0.002698 | 0.068325 | 0.061115 | -0.0073188 | 0.0041892 | -0.0029203 | -6.4545 | 64.3662 | -58.9325 | 64.2517 | -58.3008 | -58.9371 | -2.9388 | -10.231 | 64.3524 | -58.7723 | 64.4211 | -58.4839 | -58.7448 | -58.4427 | -0.24719 | 0.027466 | -0.086975 | 0.38452 | 55.7465 | -0.25177 | 55.9937 | -0.004578 | -0.086975 | 0.013733 | 0.082398 | 0.20142 | 0.24262 | -0.059509 | 0.32959 | 0.027466 | 0.63171 | 123.1842 | 0.28839 | 123.1934 | 123.2986 | 123.1247 | 123.0515 | 123.0377 | -123.2712 | -123.111 | 122.937 | 123.1064 | 52.2308 | 48.4543
1142.875 | 123.1934 | -58.7128 | 64.3845 | -0.048828 | 0.0012881 | 0.06329 | 0.069286 | 0.0032855 | -0.0012391 | -0.00042077 | -0.13663 | 0.0039798 | 0.068112 | 0.067951 | -0.0073188 | 0.0058982 | 7.0538e-05 | -6.4041 | 64.4394 | -58.9142 | 64.238 | -58.3191 | -58.6349 | -2.8564 | -10.1715 | 64.4257 | -58.7585 | 64.3662 | -58.4793 | -58.8089 | -58.5068 | -0.20142 | 0.054932 | -0.14648 | 0.39368 | 55.8563 | 0.07782 | 56.0577 | 0.27924 | -0.045776 | 0.041199 | -0.01831 | 0.23346 | 0.20599 | -0.09613 | 0.25177 | -0.050354 | 0.59509 | 123.1522 | 0.27924 | 123.1247 | 123.3536 | 123.1842 | 123.1522 | 123.1384 | -123.2986 | -123.143 | 122.9507 | 123.0789 | 52.3087 | 48.5413
1143.8906 | 123.2574 | -58.7357 | 64.3433 | -0.11749 | 0.0029971 | 0.061154 | 0.065868 | 8.1126e-05 | -0.0012391 | -0.0019162 | -0.038971 | 0.0052616 | 0.066403 | 0.060688 | -0.0083868 | 0.0071798 | -0.0042021 | -6.4774 | 64.4028 | -58.9371 | 64.2242 | -58.3282 | -58.9371 | -2.98 | -10.2676 | 64.3524 | -58.7814 | 64.3936 | -58.4793 | -58.7769 | -58.461 | -0.20142 | 0.059509 | -0.11902 | 0.40741 | 55.7556 | -0.20142 | 55.957 | 0 | -0.045776 | 0.009155 | 0.050354 | 0.25635 | 0.27466 | -0.041198 | 0.32043 | 0.004578 | 0.60883 | 123.1613 | 0.30212 | 123.175 | 123.3398 | 123.1338 | 123.1384 | 123.0881 | -123.2803 | -123.1247 | 122.9599 | 123.1293 | 52.2583 | 48.468
1144.8594 | 123.5504 | -58.6578 | 64.4073 | -0.071716 | 0.0012881 | 0.062863 | 0.06715 | -0.00077327 | -0.0016663 | -0.0012754 | -0.017609 | 0.0046206 | 0.067684 | 0.064533 | -0.0064642 | 0.0067526 | -0.0031339 | -6.4728 | 64.3799 | -58.9417 | 64.2609 | -58.2962 | -58.8959 | -2.9617 | -10.231 | 64.3387 | -58.7906 | 64.4257 | -58.4335 | -58.7036 | -58.4976 | -0.28381 | -0.027466 | -0.14648 | 0.36163 | 55.6961 | -0.23804 | 55.9799 | 0.045776 | -0.13275 | -0.068665 | 0.01831 | 0.2243 | 0.16022 | -0.045776 | 0.29297 | 0.086975 | 0.64545 | 123.2025 | 0.35706 | 123.2162 | 123.3215 | 123.1293 | 123.0377 | 122.9965 | -123.349 | -123.1979 | 122.9187 | 123.0835 | 52.1851 | 48.4268
1145.8906 | 123.262 | -58.7173 | 64.3112 | -0.071716 | 0.0027835 | 0.063931 | 0.068432 | 0.0013629 | -0.00059807 | -0.0029844 | -0.023712 | 0.0024844 | 0.068325 | 0.063893 | -0.0092414 | 0.0050436 | -0.0024931 | -6.5369 | 64.3662 | -58.9508 | 64.2242 | -58.342 | -58.9417 | -3.0579 | -10.3226 | 64.3433 | -58.7906 | 64.3799 | -58.4839 | -58.7814 | -58.4656 | -0.23346 | 0.054932 | -0.086975 | 0.37537 | 55.6595 | -0.2243 | 55.8929 | 0.009156 | -0.073242 | 0.032044 | 0.068665 | 0.23346 | 0.25177 | -0.064087 | 0.32501 | 0.009155 | 0.60883 | 123.175 | 0.3067 | 123.1705 | 123.317 | 123.1338 | 123.0835 | 123.0606 | -123.262 | -123.1018 | 122.9416 | 123.0972 | 52.1805 | 48.3948
1146.875 | 123.143 | -58.6899 | 64.3707 | -0.064087 | 0.0012881 | 0.062863 | 0.071209 | 0.0011493 | -0.00059807 | -0.0012754 | -0.057281 | 0.0039798 | 0.065975 | 0.065815 | -0.007746 | 0.0067526 | -0.00078406 | -6.4728 | 64.389 | -58.9279 | 64.2746 | -58.2916 | -58.873 | -2.9846 | -10.2676 | 64.3936 | -58.7723 | 64.3982 | -58.5617 | -58.429 | -58.3557 | -0.23804 | 0.01831 | -0.096131 | 0.39825 | 55.7053 | -0.18311 | 55.9433 | 0.054931 | -0.082398 | 0.022888 | 0.027465 | 0.12817 | 0.33417 | 0.26093 | 0.41656 | 0.34332 | 0.63629 | 123.2025 | 0.21057 | 123.1705 | 123.317 | 123.1659 | 123.0789 | 123.0835 | -123.2986 | -123.143 | 122.9645 | 123.0881 | 52.2171 | 48.4222
1147.9062 | 123.2483 | -58.6899 | 64.3524 | -0.02594 | 0.0012881 | 0.061581 | 0.070568 | -0.0012005 | -0.00038447 | -0.0019162 | -0.042023 | 0.0041934 | 0.068966 | 0.066242 | -0.0098822 | 0.0056846 | 0.00092494 | -6.4819 | 64.3616 | -58.9005 | 64.2883 | -58.2687 | -58.8593 | -2.9846 | -10.2539 | 64.3707 | -58.7585 | 64.4211 | -58.4564 | -58.7448 | -58.4427 | -0.21057 | 0.009155 | -0.064087 | 0.42114 | 55.7053 | -0.16937 | 55.9158 | 0.041199 | -0.068665 | 0.018311 | 0.068665 | 0.23346 | 0.24719 | -0.054932 | 0.31586 | 0.013733 | 0.63171 | 123.1888 | 0.30212 | 123.1796 | 123.262 | 123.1293 | 123.0515 | 123.0606 | -123.2529 | -123.111 | 122.9782 | 123.111 | 52.2079 | 48.436
1148.8594 | 123.2071 | -58.7128 | 64.3845 | -0.079346 | 0.0017155 | 0.06094 | 0.069714 | 0.0024311 | -0.0033753 | -0.004266 | -0.057281 | 0.004407 | 0.068325 | 0.061756 | -0.007746 | 0.006539 | -0.0018521 | -6.5277 | 64.4119 | -58.9508 | 64.1968 | -58.3557 | -58.9096 | -3.0533 | -10.3638 | 64.3799 | -58.7997 | 64.3433 | -58.5342 | -58.8455 | -58.5251 | -0.23804 | 0.027466 | -0.18768 | 0.35706 | 55.6595 | -0.19684 | 55.8975 | 0.041199 | -0.086975 | -0.004577 | -0.041198 | 0.17853 | 0.18768 | -0.13275 | 0.27466 | -0.045776 | 0.59509 | 123.1476 | 0.2655 | 123.143 | 123.3627 | 123.1796 | 123.1247 | 123.0927 | -123.3353 | -123.1842 | 122.9095 | 123.056 | 52.1851 | 48.349
1149.9062 | 123.3032 | -58.7036 | 64.325 | -0.0030519 | 0.0032107 | 0.062008 | 0.067364 | -0.0012005 | -0.00081187 | -0.0010618 | -0.023712 | 0.0046206 | 0.06683 | 0.062397 | -0.0066778 | 0.0058982 | -0.0012113 | -6.514 | 64.3662 | -58.9188 | 64.2975 | -58.2504 | -58.8455 | -3.0029 | -10.2402 | 64.357 | -58.7585 | 64.4577 | -58.429 | -58.7036 | -58.4198 | -0.21515 | 0.041199 | -0.027466 | 0.45319 | 55.7007 | -0.14191 | 55.9158 | 0.073242 | -0.054932 | 0.032044 | 0.13275 | 0.27466 | 0.28381 | 0 | 0.33874 | 0.054932 | 0.66833 | 123.2162 | 0.32959 | 123.2162 | 123.2849 | 123.1155 | 123.0698 | 123.0606 | -123.2437 | -123.0835 | 123.0011 | 123.1613 | 52.1896 | 48.4634
1150.875 | 123.1979 | -58.754 | 64.3707 | -0.10986 | 0.0029971 | 0.059872 | 0.069714 | -0.0035505 | -0.0020935 | -0.0019162 | -0.048126 | 0.0048344 | 0.068325 | 0.069233 | -0.0075324 | 0.0056846 | 0.00028414 | -6.5369 | 64.389 | -58.9508 | 64.2471 | -58.3191 | -58.9188 | -3.0853 | -10.3455 | 64.3799 | -58.7814 | 64.3524 | -58.5297 | -58.8226 | -58.5251 | -0.19684 | 0.01831 | -0.1236 | 0.43488 | 55.6686 | -0.16479 | 55.8655 | 0.032044 | -0.027466 | 0.009155 | -0.018311 | 0.2243 | 0.22888 | -0.068665 | 0.25635 | -0.041199 | 0.63171 | 123.1979 | 0.25177 | 123.1338 | 123.3398 | 123.1613 | 123.143 | 123.1339 | -123.3215 | -123.1522 | 123.0011 | 123.1064 | 52.2171 | 48.4085
1151.8906 | 123.3032 | -58.7311 | 64.3021 | -0.056457 | 0.0021427 | 0.06094 | 0.070782 | -0.00034607 | -0.0010255 | -0.0023434 | -0.023712 | 0.002698 | 0.06918 | 0.065815 | -0.0062506 | 0.0056846 | -0.00057046 | -6.5918 | 64.3295 | -58.9645 | 64.2288 | -58.3145 | -58.9188 | -3.0762 | -10.3363 | 64.325 | -58.8043 | 64.4119 | -58.4747 | -58.7448 | -58.4564 | -0.23346 | 0.027466 | -0.073242 | 0.41656 | 55.6549 | -0.18768 | 55.8884 | 0.045777 | -0.073242 | 0.022888 | 0.10986 | 0.25635 | 0.27466 | -0.013733 | 0.3479 | 0.059509 | 0.65002 | 123.1934 | 0.32959 | 123.2162 | 123.2941 | 123.1293 | 123.0606 | 123.056 | -123.2666 | -123.1064 | 122.9599 | 123.143 | 52.1393 | 48.3948

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.9958 | 22.4739 | 22.3914 | 22.5442
0.0042 | 22.4733 | 22.3922 | 22.5443
1.0042 | 22.4674 | 22.3831 | 22.5414
2.0042 | 22.4626 | 22.3918 | 22.541
3.0042 | 22.5534 | 22.393 | 22.543
4.0042 | 23.1653 | 22.3766 | 22.5415
5.0042 | 24.5705 | 22.39 | 22.5437
6.0042 | 26.7121 | 22.3937 | 22.542
7.0042 | 29.498 | 22.3859 | 22.5517
8.0042 | 32.8106 | 22.393 | 22.5569
9.0042 | 36.5437 | 22.4185 | 22.5704
10.0042 | 40.6426 | 22.4283 | 22.5904
11.0042 | 44.991 | 22.4414 | 22.6134
12.0042 | 49.5806 | 22.4795 | 22.6463
13.0042 | 54.3174 | 22.5084 | 22.6794
14.0042 | 59.2917 | 22.5456 | 22.7242
15.0042 | 64.3789 | 22.5967 | 22.776
16.0042 | 69.6119 | 22.6454 | 22.8319
17.0042 | 75.0018 | 22.7165 | 22.9075
18.0042 | 80.4865 | 22.7857 | 22.9873
19.0042 | 85.9954 | 22.8664 | 23.0828
20.0042 | 91.5999 | 22.9586 | 23.1796
21.0042 | 97.2947 | 23.0473 | 23.2954
22.0042 | 103.0177 | 23.1682 | 23.4256
23.0042 | 108.8267 | 23.2883 | 23.5632
24.0042 | 114.7312 | 23.4205 | 23.729
25.0042 | 120.7181 | 23.5617 | 23.8803
26.0042 | 126.7527 | 23.7394 | 24.0608
27.0042 | 132.7607 | 23.904 | 24.2506
28.0042 | 138.8016 | 24.089 | 24.4505
29.0042 | 144.8557 | 24.2764 | 24.6705
30.0042 | 150.8223 | 24.494 | 24.9039
31.0042 | 156.845 | 24.7135 | 25.1509
32.0042 | 162.8367 | 24.9594 | 25.4201
33.0042 | 168.7672 | 25.2061 | 25.6984
34.0042 | 174.6306 | 25.466 | 25.9995
35.2073 | 181.7626 | 25.8153 | 26.3762
36.1292 | 187.1907 | 26.0853 | 26.6813
37.0042 | 192.3994 | 26.3509 | 26.9958
38.0042 | 198.3763 | 26.6961 | 27.3675
39.1292 | 204.8634 | 27.0743 | 27.8025
40.0667 | 210.4347 | 27.4104 | 28.1862
41.0198 | 216.0461 | 27.774 | 28.564
42.0979 | 222.5197 | 28.206 | 29.0413
43.0667 | 228.1456 | 28.5855 | 29.4902
44.0042 | 233.6463 | 28.9814 | 29.9425
45.1135 | 240.0923 | 29.4713 | 30.5048
46.0042 | 245.1995 | 29.8826 | 30.9704
47.1135 | 251.4558 | 30.3894 | 31.5652
48.0198 | 256.4892 | 30.8404 | 32.0601
49.0198 | 262.1264 | 31.3527 | 32.6495
50.0042 | 267.7658 | 31.8762 | 33.242
51.1448 | 274.2195 | 32.4889 | 33.9674
52.0042 | 279.0744 | 32.9814 | 34.534
53.0198 | 284.6314 | 33.5865 | 35.2054
54.0042 | 290.0937 | 34.1867 | 35.8856
55.0042 | 295.5071 | 34.8077 | 36.5926
56.0042 | 300.9012 | 35.4607 | 37.3323
57.0042 | 306.2049 | 36.1198 | 38.0759
58.0354 | 311.9554 | 36.8174 | 38.8804
59.0042 | 317.2101 | 37.4985 | 39.657
60.0823 | 322.7476 | 38.2447 | 40.4943
61.0667 | 328.4649 | 39.0466 | 41.388
62.0042 | 333.4641 | 39.7875 | 42.2268
63.0042 | 338.6375 | 40.5987 | 43.1449
64.0042 | 343.9352 | 41.4188 | 44.0834
65.0042 | 349.2701 | 42.2731 | 45.0417
66.0042 | 354.4574 | 43.1484 | 46.0401
67.0042 | 359.6028 | 44.0368 | 47.0561
68.0042 | 364.7704 | 44.9496 | 48.0997
69.0042 | 369.9752 | 45.8968 | 49.163
70.0042 | 375.0174 | 46.8609 | 50.2556
71.051 | 380.283 | 47.8955 | 51.4368
72.0042 | 384.9384 | 48.8615 | 52.5397
73.0042 | 389.9138 | 49.904 | 53.7226
74.0042 | 394.8962 | 50.9622 | 54.919
75.0042 | 399.9038 | 52.0489 | 56.1367
76.0042 | 404.8813 | 53.1844 | 57.3838
77.0198 | 409.6878 | 54.3345 | 58.6652
78.0042 | 414.3767 | 55.4875 | 59.9561
79.0042 | 419.185 | 56.6844 | 61.2846
80.0042 | 423.9118 | 57.8942 | 62.6513
81.0198 | 428.6943 | 59.1646 | 64.0308
82.0042 | 433.4346 | 60.4478 | 65.4117
83.0042 | 438.2819 | 61.7621 | 66.8199
84.0042 | 442.9589 | 63.1051 | 68.2518
85.0042 | 447.4554 | 64.4821 | 69.6988
86.0198 | 451.9729 | 65.9214 | 71.2007
87.0042 | 456.5302 | 67.3588 | 72.7025
88.0042 | 461.2122 | 68.8723 | 74.2592
89.0198 | 465.7795 | 70.418 | 75.8753
90.0042 | 470.1902 | 72.0022 | 77.5202
91.0042 | 474.5564 | 73.6294 | 79.2419
92.0042 | 478.9429 | 75.2894 | 81.023
93.0042 | 483.1141 | 76.9813 | 82.8449
94.0042 | 487.3334 | 78.7163 | 84.7239
95.0042 | 491.5507 | 80.4968 | 86.6349
96.0042 | 495.7268 | 82.3368 | 88.5977
97.0042 | 500.0174 | 84.2341 | 90.6048
98.0042 | 504.2197 | 86.1597 | 92.6501
99.0042 | 508.33 | 88.1221 | 94.7434
100.0042 | 512.4249 | 90.1659 | 96.8886
101.0042 | 516.5074 | 92.2341 | 99.0931
102.0042 | 520.5009 | 94.3519 | 101.3716
103.0042 | 524.5011 | 96.5408 | 103.6923
104.0042 | 528.3558 | 98.7739 | 106.0877
105.0042 | 532.1152 | 101.0734 | 108.512
106.0042 | 535.931 | 103.3737 | 111
107.0042 | 539.587 | 105.7287 | 113.5049
108.0042 | 543.2464 | 108.1288 | 116.0723
109.0042 | 547.0843 | 110.594 | 118.6839
110.0042 | 550.5869 | 113.0564 | 121.3226
111.0042 | 553.9457 | 115.563 | 123.9877
112.0042 | 557.3487 | 118.1048 | 126.7157
113.0042 | 560.6077 | 120.7018 | 129.4964
114.0042 | 564.0992 | 123.307 | 132.2947
115.0042 | 567.7639 | 125.9589 | 135.1337
116.0042 | 571.1879 | 128.6437 | 138.0129
117.0042 | 574.3908 | 131.3326 | 140.9149
118.0042 | 577.4596 | 134.0308 | 143.8461
119.0042 | 580.6498 | 136.7777 | 146.8104
120.0042 | 583.7908 | 139.5462 | 149.8279
121.0042 | 586.6878 | 142.3421 | 152.8625
122.0042 | 589.5715 | 145.1525 | 155.9445
123.0042 | 592.5515 | 147.9902 | 159.059
124.0042 | 595.491 | 150.8794 | 162.1844
125.0042 | 598.4558 | 153.7925 | 165.3686
126.0042 | 601.3124 | 156.7506 | 168.5861
127.0042 | 604.1708 | 159.7514 | 171.8225
128.0042 | 607.1257 | 162.7543 | 175.0806
129.0042 | 609.9971 | 165.8084 | 178.3903
130.0042 | 613.0738 | 168.9046 | 181.7454
131.0042 | 616.1243 | 172.0367 | 185.111
132.0042 | 618.9735 | 175.1937 | 188.4925
133.0042 | 621.9622 | 178.391 | 191.8488
134.0042 | 624.9582 | 181.5885 | 195.204
135.0042 | 627.7041 | 184.8106 | 198.5643
136.0042 | 630.4766 | 188.0873 | 201.9554
137.0042 | 633.3173 | 191.3733 | 205.4418
138.0042 | 636.2949 | 194.6866 | 209.0055
139.0042 | 639.1835 | 198.0491 | 212.6831
140.0042 | 642.1383 | 201.468 | 216.4801
141.0042 | 645.015 | 205.0021 | 220.4215
142.0042 | 647.5275 | 208.5462 | 224.4436
143.0042 | 649.921 | 212.138 | 228.6153
144.0042 | 652.0867 | 215.7372 | 232.9495
145.0042 | 654.0489 | 219.3893 | 237.4194
146.0042 | 655.9716 | 223.215 | 242.2194
147.0042 | 657.9243 | 227.1327 | 247.0706
148.0042 | 659.7265 | 231.0285 | 251.644
149.0042 | 661.522 | 235.1769 | 255.7106
150.0042 | 663.4565 | 240.9139 | 261.3783
151.0042 | 665.4866 | 249.0959 | 269.7028
152.0042 | 667.6835 | 257.9134 | 278.1846
153.0042 | 669.9045 | 266.6063 | 286.3991
154.0042 | 671.9506 | 274.8511 | 294.2118
155.0042 | 674.1357 | 282.7293 | 301.833
156.0042 | 676.3044 | 290.7756 | 310.0637
157.0042 | 678.3656 | 298.6748 | 319.3746
158.0042 | 680.3644 | 306.696 | 330.0185
159.0042 | 682.1075 | 314.5077 | 339.4019
160.0042 | 683.5727 | 323.1016 | 349.8802
161.0042 | 685.0124 | 330.5781 | 359.1265
162.0042 | 686.0386 | 338.6077 | 367.609
163.0042 | 686.8224 | 345.6643 | 376.0721
164.0042 | 687.5226 | 353.0716 | 385.6362
165.0042 | 688.0967 | 360.7914 | 395.5923
166.0042 | 688.519 | 368.2076 | 405.0633
167.0042 | 689.0197 | 376.8975 | 413.6995
168.0042 | 689.6012 | 384.355 | 422.6067
169.0042 | 689.8943 | 392.096 | 431.541
170.0042 | 690.1358 | 401.5173 | 440.319
171.0042 | 690.469 | 409.3807 | 447.8394
172.0042 | 690.8593 | 416.4898 | 454.3205
173.0042 | 690.9906 | 423.8618 | 460.8316
174.0042 | 691.2481 | 431.3821 | 468.738
175.0042 | 691.5694 | 438.9671 | 475.2037
176.0042 | 691.9192 | 445.8538 | 480.9563
177.0042 | 692.333 | 452.6358 | 484.9522
178.0042 | 692.7397 | 459.5918 | 488.5224
179.0042 | 693.1486 | 467.1402 | 491.8286
180.0042 | 693.5022 | 472.6854 | 495.6287
181.0042 | 694.1605 | 477.6136 | 498.4749
182.0042 | 694.6322 | 483.4939 | 501.6866
183.0042 | 695.0679 | 487.8821 | 503.025
184.0042 | 695.3622 | 493.4616 | 505.7694
185.0042 | 695.6098 | 498.1556 | 507.8863
186.0042 | 695.8366 | 502.6179 | 510.5972
187.0042 | 696.0972 | 507.2842 | 513.5346
188.0042 | 696.2355 | 511.0177 | 516.0824
189.0042 | 696.4728 | 515.5499 | 518.7063
190.0042 | 696.6843 | 519.5622 | 521.3177
191.0042 | 696.8098 | 523.4567 | 524.2831
192.0042 | 697.0734 | 526.8482 | 527.019
193.0042 | 697.2637 | 530.5993 | 529.6288
194.0042 | 697.4775 | 533.8066 | 532.3668
195.0042 | 697.5019 | 536.9896 | 535.0149
196.0042 | 697.4296 | 539.2876 | 537.2367
197.0042 | 697.6915 | 542.6509 | 539.1933
198.0042 | 698.0655 | 546.0415 | 541.2282
199.0042 | 698.3574 | 548.2582 | 543.3862
200.0042 | 698.3623 | 550.9283 | 545.6657
201.0042 | 698.4419 | 554.0096 | 546.9535
202.0042 | 698.6738 | 557.5662 | 548.9684
203.0042 | 698.8436 | 560.1425 | 551.4735
204.0042 | 698.8791 | 562.7799 | 553.8336
205.0042 | 699.0891 | 565.4919 | 556.0881
206.0042 | 699.3888 | 568.7861 | 558.5817
207.0042 | 699.7188 | 572.2551 | 561.3423
208.0042 | 700.0708 | 574.8804 | 563.9326
209.0042 | 700.1511 | 577.4515 | 566.5758
210.0042 | 700.0611 | 580.0205 | 569.2284
211.0042 | 699.7844 | 582.9906 | 571.6129
212.0042 | 699.8678 | 586.251 | 574.2366
213.0042 | 699.9117 | 590.0314 | 576.9901
214.0042 | 700.1314 | 593.8794 | 579.3111
215.0042 | 700.1047 | 596.9032 | 581.5953
216.0042 | 700.1909 | 599.3466 | 583.6414
217.0042 | 700.3904 | 601.6471 | 585.7151
218.0042 | 700.5316 | 604.1279 | 587.7781
219.0042 | 700.5879 | 606.3545 | 589.8422
220.0042 | 700.5808 | 608.5128 | 591.8311
221.0042 | 700.5154 | 610.4877 | 593.8956
222.0042 | 700.3912 | 612.6517 | 595.6742
223.0042 | 700.2556 | 614.9508 | 597.4069
224.0042 | 700.2723 | 617.0688 | 599.0771
225.0042 | 700.1551 | 618.8661 | 601.0549
226.0042 | 700.2208 | 620.7681 | 602.956
227.0042 | 700.1974 | 622.3832 | 604.8454
228.0042 | 700.2146 | 624.0513 | 606.6852
229.0042 | 700.1748 | 625.966 | 608.5022
230.0042 | 700.1134 | 628.1499 | 609.934
231.0042 | 700.0042 | 630.0339 | 611.6225
232.0042 | 700.0315 | 632.0063 | 613.2027
233.0042 | 700.0711 | 634.0802 | 614.5312
234.0042 | 700.0665 | 636.1633 | 615.9462
235.0042 | 699.9683 | 638.1971 | 617.043
236.0042 | 699.9263 | 640.1688 | 618.2654
237.0042 | 699.9503 | 641.8408 | 619.6011
238.0042 | 700.0915 | 643.4981 | 620.9238
239.0042 | 700.0181 | 645.1511 | 621.9623
240.0042 | 699.8326 | 646.8411 | 622.9509
241.0042 | 699.7994 | 648.6248 | 624.0852
242.0042 | 699.7605 | 650.4442 | 625.2873
243.0042 | 699.6722 | 651.9106 | 626.6505
244.0042 | 699.6779 | 653.3074 | 627.8669
245.0042 | 699.6216 | 654.8802 | 628.9001
246.0042 | 699.6453 | 656.7131 | 630.0495
247.0042 | 699.6232 | 658.3436 | 630.858
248.0042 | 699.6427 | 659.7856 | 631.6789
249.0042 | 699.6735 | 661.2506 | 632.8577
250.0042 | 699.5744 | 662.7309 | 633.8477
251.0042 | 699.5895 | 664.2553 | 634.9895
252.0042 | 699.6204 | 665.716 | 636.2549
253.0042 | 699.6483 | 666.8403 | 637.2024
254.0042 | 699.5764 | 667.7339 | 638.0676
255.0042 | 699.6231 | 669.0005 | 638.7126
256.0042 | 699.5279 | 670.339 | 639.7243
257.0042 | 699.5747 | 671.621 | 640.5334
258.0042 | 699.6702 | 672.8231 | 641.2343
259.0042 | 699.7118 | 673.7318 | 641.9779
260.0042 | 699.5414 | 674.7073 | 642.6332
261.0042 | 699.2988 | 675.6485 | 643.595
262.0042 | 699.1914 | 676.7265 | 644.1773
263.0042 | 699.0344 | 678.2155 | 644.9228
264.0042 | 698.9265 | 679.6914 | 645.7571
265.0042 | 698.8623 | 681.3627 | 646.2292
266.0042 | 698.6682 | 682.9639 | 647.5107
267.0042 | 698.574 | 684.7136 | 648.3437
268.0042 | 698.4197 | 686.3625 | 649.2518
269.0042 | 698.4954 | 687.9894 | 650.0825
270.0042 | 698.4984 | 689.3602 | 650.3658
271.0042 | 698.3682 | 690.7067 | 651.6509
272.0042 | 698.2909 | 691.9628 | 652.7
273.0042 | 698.2402 | 693.1666 | 653.3459
274.0042 | 698.2774 | 694.3599 | 654.1941
275.0042 | 698.2604 | 695.2721 | 654.7555
276.0042 | 698.3488 | 696.1584 | 656.1847
277.0042 | 698.2345 | 697.0528 | 657.5816
278.0042 | 698.3257 | 698.0037 | 658.9497
279.0042 | 698.6254 | 698.9197 | 660.0824
280.0042 | 698.8005 | 699.8461 | 660.9529
281.0042 | 698.9076 | 700.7832 | 662.4926
282.0042 | 699.0431 | 701.8344 | 663.6407
283.0042 | 699.0965 | 702.7913 | 664.075
284.0042 | 699.0708 | 703.7314 | 664.5141
285.0042 | 699.036 | 704.5565 | 665.7768
286.0042 | 699.0558 | 705.293 | 666.43
287.0042 | 698.953 | 706.0622 | 667.6845
288.0042 | 698.9598 | 706.8508 | 668.6256
289.0667 | 699.0519 | 707.6758 | 668.8379
290.0823 | 699.055 | 708.4226 | 669.3646
291.0198 | 699.2501 | 709.172 | 670.8588
292.0042 | 699.3471 | 709.7611 | 671.1813
293.0042 | 699.2966 | 710.3745 | 671.5103
294.0042 | 699.3123 | 711.0075 | 672.6516
295.0042 | 699.3014 | 711.6024 | 673.2198
296.0042 | 699.3244 | 712.2013 | 674.3666
297.0042 | 699.4289 | 712.7944 | 675.0905
298.0042 | 699.4075 | 713.3938 | 676.3447
299.0042 | 699.3958 | 713.867 | 676.5944
300.0042 | 699.4838 | 714.2539 | 675.4629
301.0979 | 699.5876 | 715.0885 | 673.2953
302.0979 | 699.546 | 716.6639 | 674.7888
303.0354 | 699.5655 | 718.1539 | 677.6223
304.0042 | 699.5735 | 719.2599 | 678.1955
305.0042 | 699.5518 | 720.046 | 677.91
306.0042 | 699.6276 | 720.8697 | 678.3991
307.0042 | 699.6588 | 721.5797 | 679.0098
308.0042 | 699.5903 | 722.2288 | 680.3712
309.0042 | 699.5646 | 722.8522 | 681.3431
310.0042 | 699.5128 | 723.4462 | 681.699
311.0042 | 699.5781 | 724.1328 | 683.165
312.0042 | 699.5792 | 724.5667 | 683.6538
313.0042 | 699.4951 | 724.9597 | 684.4912
314.0042 | 699.5623 | 725.2862 | 684.8129
315.0198 | 699.5921 | 725.5159 | 685.1911
316.0823 | 699.6878 | 725.7709 | 686.139
317.0354 | 699.751 | 726.0499 | 687.0494
318.051 | 699.8036 | 726.3053 | 686.9719
319.051 | 699.8224 | 726.5564 | 687.7343
320.0042 | 699.7602 | 726.7244 | 687.655
321.0042 | 699.7224 | 726.8521 | 687.9723
322.0042 | 699.7378 | 727.0588 | 688.3646
323.0042 | 699.7189 | 727.2136 | 689.168
324.0042 | 699.7155 | 727.4064 | 690.1785
325.0042 | 699.6804 | 727.4558 | 690.3584
326.0042 | 699.7199 | 727.6349 | 691.6428
327.0042 | 699.6974 | 727.7781 | 692.0197
328.0042 | 699.6309 | 727.871 | 691.8356
329.0042 | 699.4791 | 728.1309 | 692.9797
330.0042 | 699.4786 | 728.3825 | 693.1524
331.0042 | 699.4601 | 728.8719 | 694.5593
332.0042 | 699.3639 | 729.0864 | 694.3306
333.0042 | 699.3711 | 729.3124 | 694.3165
334.0042 | 699.4748 | 729.6277 | 694.9461
335.0042 | 699.4907 | 729.775 | 694.8054
336.0042 | 699.4803 | 729.8761 | 694.7559
337.0042 | 699.4483 | 729.9486 | 694.944
338.0042 | 699.345 | 730.1583 | 695.7993
339.0042 | 699.3822 | 730.283 | 696.3167
340.0042 | 699.4278 | 730.2876 | 696.4653
341.0042 | 699.3443 | 730.3872 | 697.3676
342.0042 | 699.3795 | 730.718 | 699.5785
343.0042 | 699.399 | 730.7456 | 699.7894
344.0042 | 699.4729 | 730.782 | 700.2935
345.0042 | 699.4233 | 730.8964 | 701.2513
346.0042 | 699.4612 | 731.1656 | 703.132
347.0042 | 699.4526 | 731.154 | 703.3844
348.0042 | 699.3941 | 731.0291 | 702.933
349.0042 | 699.4087 | 730.7374 | 701.6661
350.0042 | 699.3711 | 730.5358 | 700.5698
351.0042 | 699.2599 | 730.9219 | 702.1047
352.0042 | 699.2617 | 731.3392 | 703.7662
353.0042 | 699.1425 | 732.0739 | 706.7294
354.0042 | 699.0825 | 732.3691 | 707.4553
355.0042 | 699.0005 | 732.3709 | 706.9247
356.0042 | 698.8525 | 732.6033 | 707.8171
357.0042 | 698.8043 | 732.8406 | 708.7719
358.0042 | 698.7563 | 733.0454 | 709.6508
359.0042 | 698.7515 | 732.9036 | 709.0358
360.0042 | 698.7227 | 733.1218 | 709.9171
361.0042 | 698.6753 | 733.4486 | 711.1151
362.0042 | 698.7114 | 733.4655 | 711.0456
363.0042 | 698.6679 | 733.7247 | 711.7404
364.0042 | 698.6179 | 733.7984 | 711.5403
365.0042 | 698.5039 | 734.2818 | 713.0777
366.0042 | 698.4976 | 734.9661 | 715.7184
367.0042 | 698.5336 | 735.1972 | 716.3532
368.0042 | 698.5 | 735.5299 | 717.1321
369.0042 | 698.5314 | 735.8748 | 718.0823
370.0042 | 698.5615 | 735.8395 | 717.8291
371.0042 | 698.5766 | 736.2796 | 718.9403
372.0042 | 698.6121 | 736.6043 | 719.5197
373.0042 | 698.4898 | 736.9608 | 720.4718
374.0042 | 698.4845 | 737.5111 | 721.9345
375.0042 | 698.4752 | 737.3902 | 721.111
376.0042 | 698.583 | 737.8575 | 722.0785
377.0042 | 698.5822 | 738.3954 | 723.5273
378.0042 | 698.4468 | 739.01 | 724.8622
379.0042 | 698.5995 | 739.5202 | 725.8693
380.0042 | 698.6921 | 739.5757 | 725.4856
381.0042 | 698.7808 | 739.9979 | 726.38
382.0042 | 698.7452 | 740.5592 | 727.4465
383.0042 | 698.8603 | 741.1808 | 728.4311
384.0042 | 698.9693 | 742.0209 | 730.3441
385.0042 | 699.0783 | 742.5708 | 731.1452
386.0042 | 699.1351 | 742.8378 | 731.294
387.0042 | 699.1407 | 743.3412 | 732.0585
388.0042 | 699.2517 | 744.1428 | 733.6353
389.0042 | 699.314 | 744.4654 | 734.0178
390.0042 | 699.3125 | 745.1046 | 735.4022
391.0042 | 699.3689 | 745.967 | 737.565
392.0042 | 699.4507 | 746.381 | 738.2691
393.0042 | 699.495 | 746.6278 | 738.2593
394.0042 | 699.5105 | 747.2171 | 739.0306
395.0042 | 699.5096 | 747.8147 | 739.9138
396.0042 | 699.3034 | 748.3583 | 740.3873
397.0042 | 699.2882 | 749.1262 | 741.7181
398.0042 | 699.2948 | 749.3775 | 741.7132
399.0042 | 699.2428 | 750.0674 | 742.4339
400.0042 | 699.2607 | 750.4568 | 742.7353
401.0042 | 699.3234 | 751.2295 | 744.0002
402.0042 | 699.3004 | 751.1902 | 743.441
403.0042 | 699.3389 | 751.6323 | 744.0986
404.0042 | 699.4429 | 751.71 | 743.8363
405.0042 | 699.558 | 751.7799 | 743.6326
406.0042 | 699.5532 | 752.1551 | 744.1781
407.0042 | 699.6708 | 752.8463 | 745.3857
408.0042 | 699.7078 | 753.4891 | 746.4867
409.0042 | 699.627 | 753.8008 | 746.8554
410.0042 | 699.5849 | 753.9843 | 747.2873
411.0042 | 699.5857 | 754.3241 | 747.8228
412.0042 | 699.6505 | 754.9344 | 748.8807
413.0042 | 699.5992 | 754.8433 | 748.7117
414.0042 | 699.5663 | 755.1726 | 749.1265
415.0042 | 699.5212 | 754.5993 | 747.8711
416.0042 | 699.5138 | 755.0869 | 748.7463
417.0042 | 699.4771 | 755.5189 | 749.3819
418.0042 | 699.4873 | 755.6216 | 749.3673
419.0042 | 699.4162 | 755.9888 | 749.8765
420.0042 | 699.3759 | 756.0987 | 749.8358
421.0042 | 699.289 | 756.6112 | 750.5782
422.0042 | 699.1737 | 757.1661 | 751.1055
423.0042 | 699.1467 | 757.4861 | 751.2748
424.0042 | 699.0668 | 757.9542 | 751.386
425.0042 | 699.0467 | 758.3944 | 751.8403
426.0042 | 699.0764 | 758.6772 | 752.2519
427.0042 | 699.0373 | 758.66 | 751.9957
428.0042 | 699.0808 | 758.7242 | 751.9137
429.0042 | 699.1146 | 759.0298 | 751.9713
430.0042 | 699.1098 | 759.4282 | 752.3604
431.0042 | 699.0699 | 759.496 | 752.3894
432.0042 | 698.9776 | 759.7058 | 752.6744
433.0042 | 698.9945 | 760.213 | 753.2824
434.0042 | 698.9975 | 760.655 | 754.0405
435.0042 | 699.0304 | 760.9443 | 754.6554
436.0042 | 698.9613 | 761.1488 | 755.2825
437.0042 | 698.9441 | 761.0365 | 755.2837
438.0042 | 698.9406 | 761.1154 | 755.4667
439.0042 | 698.8768 | 760.8131 | 754.865
440.0042 | 698.8794 | 760.6855 | 754.455
441.0042 | 698.957 | 761.1122 | 754.8949
442.0042 | 699.0376 | 761.6575 | 755.5863
443.0042 | 699.0526 | 762.0213 | 756.0822
444.0042 | 699.0372 | 762.138 | 756.0655
445.0042 | 699.104 | 762.5589 | 756.5776
446.0042 | 699.0849 | 762.5225 | 756.2273
447.0042 | 699.0953 | 762.6418 | 755.9617
448.0042 | 699.2018 | 762.7682 | 755.9278
449.0042 | 699.2889 | 763.4374 | 756.6681
450.0042 | 699.3178 | 763.3871 | 756.4577
451.0042 | 699.2862 | 763.4065 | 756.2317
452.0042 | 699.3871 | 763.4849 | 756.0355
453.0042 | 699.4018 | 763.2664 | 755.6131
454.0042 | 699.4487 | 763.5363 | 755.8789
455.0042 | 699.5129 | 763.3129 | 755.4746
456.0042 | 699.5023 | 763.469 | 755.5512
457.0042 | 699.3828 | 764.294 | 756.5667
458.0354 | 699.3793 | 763.5911 | 755.6572
459.0042 | 699.3296 | 764.6045 | 757.0353
460.0042 | 699.1992 | 764.4369 | 756.5077
461.0042 | 699.1087 | 764.8602 | 756.8603
462.0042 | 699.0629 | 765.3584 | 757.5266
463.0042 | 699.0359 | 765.5543 | 757.6512
464.0042 | 699.0335 | 765.0409 | 756.7376
465.0042 | 698.9954 | 764.8111 | 756.4585
466.0042 | 698.9957 | 764.6249 | 756.5357
467.0042 | 698.9723 | 764.7627 | 756.8713
468.0042 | 698.922 | 765.3048 | 757.6234
469.0042 | 698.884 | 764.9749 | 757.2328
470.0042 | 698.9576 | 764.5114 | 756.5202
471.0042 | 698.9728 | 764.9872 | 756.9788
472.0042 | 699.033 | 766.1477 | 758.5074
473.0042 | 699.0955 | 766.5669 | 759.0426
474.0042 | 699.1108 | 766.6902 | 759.3371
475.0042 | 699.1605 | 766.5594 | 758.9968
476.0042 | 699.2414 | 767.3816 | 759.9015
477.0042 | 699.3766 | 767.4612 | 759.7097
478.0042 | 699.5141 | 767.6149 | 759.796
479.0042 | 699.6103 | 767.4119 | 759.5468
480.0042 | 699.7098 | 767.771 | 759.9618
481.0042 | 699.8414 | 768.6617 | 761.2254
482.0042 | 699.7843 | 768.6067 | 761.0685
483.0042 | 699.653 | 768.7305 | 761.0448
484.0042 | 699.7101 | 769.098 | 761.5884
485.0042 | 699.7398 | 769.2207 | 761.9123
486.0042 | 699.8223 | 769.7478 | 762.4501
487.0042 | 699.8279 | 769.5775 | 761.9917
488.0042 | 699.7448 | 769.5249 | 761.9922
489.0042 | 699.7484 | 769.435 | 761.9385
490.0042 | 699.8237 | 767.7569 | 759.5647
491.0042 | 699.8471 | 768.2524 | 760.4717
492.0042 | 699.9741 | 768.5012 | 761.4737
493.0042 | 700.0242 | 768.5931 | 761.9093
494.0042 | 699.994 | 768.1989 | 761.3557
495.0042 | 699.9581 | 768.0247 | 761.497
496.0042 | 699.9577 | 769.3599 | 763.8479
497.0042 | 700.0497 | 769.3287 | 764.2856
498.0042 | 700.1617 | 769.6055 | 764.7725
499.0042 | 700.3214 | 770.036 | 765.2483
500.0042 | 700.5492 | 769.7574 | 765.0642
501.0042 | 700.6675 | 769.9342 | 765.2632
502.0042 | 700.5118 | 770.8874 | 766.5889
503.0042 | 700.1294 | 771.5258 | 767.2905
504.0042 | 700.0477 | 772.0874 | 767.8635
505.0042 | 700.0289 | 772.3128 | 768.1379
506.0042 | 700.0992 | 772.4311 | 768.114
507.0042 | 700.1246 | 772.9003 | 768.6528
508.0042 | 700.1935 | 772.9293 | 768.5406
509.0042 | 700.3663 | 773.0018 | 769.0026
510.0042 | 700.3886 | 772.7501 | 768.581
511.0042 | 700.3411 | 773.1803 | 769.3182
512.0042 | 700.3185 | 773.2472 | 769.5682
513.0042 | 700.2967 | 773.4171 | 769.6649
514.0042 | 700.2279 | 773.6395 | 769.7031
515.0042 | 700.2258 | 773.7046 | 769.3202
516.0042 | 700.2273 | 774.3898 | 769.7846
517.0042 | 700.2672 | 774.4051 | 769.6022
518.0042 | 700.2549 | 774.6186 | 769.5936
519.0042 | 700.1874 | 774.853 | 769.6697
520.0042 | 700.1763 | 775.0229 | 769.6861
521.0042 | 700.1748 | 775.1516 | 769.7461
522.0042 | 700.2236 | 774.9097 | 769.4684
523.0042 | 700.2506 | 775.1545 | 769.8916
524.0042 | 700.3587 | 775.2348 | 769.7369
525.0042 | 700.4525 | 775.2972 | 769.7708
526.0354 | 700.4197 | 774.704 | 769.2458
527.0042 | 700.4116 | 775.3269 | 769.9769
528.0042 | 700.5375 | 775.5604 | 770.1697
529.0042 | 700.5552 | 775.5511 | 769.9528
530.0042 | 700.6455 | 775.2809 | 769.4478
531.0042 | 700.7221 | 775.6075 | 769.8376
532.0042 | 700.6827 | 776.0424 | 770.4468
533.0042 | 700.6203 | 776.0419 | 770.1472
534.0042 | 700.5215 | 776.2563 | 770.1101
535.0042 | 700.4442 | 776.3419 | 770.0175
536.0042 | 700.5448 | 776.6557 | 770.4168
537.0042 | 700.6166 | 776.8827 | 770.731
538.0042 | 700.6409 | 776.9167 | 770.7684
539.0042 | 700.7161 | 776.8612 | 770.7828
540.0042 | 700.7362 | 776.9137 | 770.6082
541.0042 | 700.7817 | 777.4648 | 771.2527
542.0042 | 700.8274 | 777.65 | 771.3944
543.0042 | 701.0008 | 777.9282 | 771.8322
544.0042 | 701.0003 | 777.9955 | 771.5593
545.0042 | 701.0128 | 777.7545 | 771.078
546.0042 | 700.963 | 778.0152 | 771.5189
547.0042 | 701.0349 | 777.8813 | 771.3106
548.0042 | 700.9843 | 777.8421 | 771.3289
549.0042 | 700.8901 | 777.8765 | 771.0997
550.0042 | 700.8212 | 777.7432 | 771.0127
551.0042 | 700.7744 | 778.0141 | 771.8309
552.0042 | 700.6844 | 778.2632 | 772.4769
553.0042 | 700.679 | 778.0479 | 772.3558
554.0042 | 700.6876 | 778.0204 | 772.6283
555.0042 | 700.6602 | 777.7703 | 772.3628
556.0042 | 700.6372 | 777.7635 | 772.2621
557.0042 | 700.5699 | 777.6616 | 771.8677
558.0042 | 700.4683 | 777.4537 | 771.1978
559.0042 | 700.4123 | 777.9867 | 771.8627
560.0042 | 700.4032 | 777.7713 | 771.2626
561.0198 | 700.4124 | 777.7992 | 770.7383
562.0042 | 700.3842 | 777.7687 | 770.4933
563.0042 | 700.4448 | 777.8025 | 770.4048
564.0042 | 700.536 | 777.7311 | 770.4137
565.0042 | 700.5883 | 777.9846 | 770.8518
566.0042 | 700.6008 | 778.3331 | 771.3017
567.0042 | 700.6023 | 779.612 | 773.2353
568.0042 | 700.5601 | 779.6738 | 773.2462
569.0042 | 700.5629 | 779.768 | 773.1753
570.0042 | 700.6658 | 780.2725 | 774.4639
571.0042 | 700.7287 | 781.0753 | 776.3621
572.0042 | 700.6132 | 781.1716 | 776.6896
573.0042 | 700.5998 | 781.2532 | 776.9007
574.0042 | 700.5978 | 780.8578 | 776.1988
575.0042 | 700.5576 | 780.6259 | 776.0106
576.0042 | 700.5384 | 780.8502 | 776.1648
577.0042 | 700.5934 | 781.2592 | 776.4282
578.0042 | 700.6364 | 781.2093 | 776.1675
579.0042 | 700.6582 | 782.0105 | 777.2814
580.0042 | 700.5933 | 782.2688 | 777.751
581.0042 | 700.5408 | 782.1219 | 777.3493
582.0042 | 700.6284 | 782.2323 | 777.1869
583.0042 | 700.8544 | 782.4581 | 777.5023
584.0042 | 700.8946 | 782.088 | 777.0926
585.0042 | 700.894 | 781.4618 | 776.0925
586.0042 | 700.8082 | 781.4261 | 776.0061
587.0042 | 700.7059 | 781.0142 | 775.1973
588.0042 | 700.6311 | 780.9551 | 774.7269
589.0042 | 700.5427 | 781.3363 | 774.5383
590.0042 | 700.4665 | 781.2587 | 773.9192
591.0198 | 700.3569 | 781.4612 | 773.9899
592.0042 | 700.344 | 781.2914 | 773.5539
593.0042 | 700.4109 | 781.4913 | 773.7618
594.0042 | 700.2972 | 782.3384 | 775.2158
595.0042 | 700.3541 | 782.4519 | 775.6217
596.0042 | 700.4152 | 782.5291 | 775.2935
597.0042 | 700.4339 | 782.4149 | 774.8031
598.0042 | 700.4484 | 782.2267 | 774.4407
599.0042 | 700.4445 | 781.7962 | 773.6944
600.0042 | 700.4593 | 781.6242 | 773.2748
601.0042 | 700.5346 | 781.9379 | 773.7216
602.0042 | 700.5541 | 781.7345 | 772.9976
603.0042 | 700.4634 | 781.7993 | 772.8786
604.0042 | 700.3214 | 781.8029 | 772.7652
605.0042 | 700.3252 | 781.6848 | 772.2888
606.0042 | 700.4031 | 781.6863 | 772.5663
607.0042 | 700.4156 | 781.851 | 772.8602
608.0042 | 700.4378 | 782.0969 | 773.3954
609.0042 | 700.5532 | 781.9511 | 773.1685
610.0042 | 700.63 | 781.5575 | 772.2896
611.0042 | 700.7089 | 781.599 | 772.4764
612.0042 | 700.8004 | 781.5054 | 772.7866
613.0042 | 700.7881 | 780.8062 | 771.8529
614.0042 | 700.7323 | 780.3234 | 770.7536
615.0042 | 700.8043 | 779.7645 | 769.6715
616.0042 | 700.7931 | 779.9293 | 769.9009
617.0042 | 700.7212 | 779.6223 | 769.5024
618.0042 | 700.6029 | 779.4553 | 769.0092
619.0042 | 700.5253 | 779.4133 | 768.8668
620.0042 | 700.6006 | 779.3717 | 768.9572
621.0042 | 700.6732 | 779.5894 | 769.5708
622.0042 | 700.5466 | 779.5477 | 769.3566
623.0042 | 700.4523 | 779.7954 | 769.9391
624.0042 | 700.3169 | 780.0945 | 770.7029
625.0042 | 700.2172 | 779.4225 | 769.4505
626.0042 | 700.0591 | 779.1663 | 768.8466
627.0042 | 700.0366 | 779.6407 | 769.5051
628.0042 | 700.041 | 779.7699 | 769.3314
629.0042 | 700.038 | 779.7388 | 768.9069
630.0042 | 699.9206 | 779.4487 | 768.2475
631.0042 | 699.7611 | 779.5613 | 768.2743
632.0042 | 699.5897 | 779.5169 | 768.5454
633.0042 | 699.5248 | 779.7164 | 769.0252
634.0042 | 699.554 | 779.8433 | 769.5098
635.0042 | 699.4172 | 779.3282 | 768.6564
636.0042 | 699.1824 | 779.4993 | 768.7866
637.0042 | 699.1233 | 779.1033 | 768.093
638.0042 | 699.0718 | 778.8405 | 767.3076
639.0042 | 699.116 | 778.8245 | 767.2886
640.0042 | 699.1468 | 778.662 | 766.4788
641.0042 | 699.1869 | 779.0093 | 766.5666
642.0042 | 699.0392 | 778.8111 | 766.0423
643.0042 | 698.9109 | 779.0718 | 766.3118
644.0042 | 698.7421 | 779.0155 | 765.8374
645.0042 | 698.7425 | 779.0039 | 765.2067
646.0042 | 698.8166 | 779.5017 | 765.6596
647.0042 | 698.7023 | 779.4223 | 765.1127
648.0042 | 698.5733 | 779.4481 | 765.0996
649.0042 | 698.4387 | 779.1746 | 764.385
650.0042 | 698.4251 | 779.2828 | 763.9543
651.0042 | 698.4148 | 779.7098 | 764.309
652.0042 | 698.3966 | 780.0548 | 764.488
653.0042 | 698.3585 | 780.2985 | 764.9428
654.0042 | 698.4632 | 780.2364 | 764.5621
655.0042 | 698.5743 | 779.9976 | 763.9495
656.0042 | 698.4705 | 780.2013 | 763.9869
657.0042 | 698.442 | 780.1349 | 763.7599
658.0042 | 698.3124 | 779.8537 | 762.893
659.0042 | 698.3323 | 780.0537 | 762.9004
660.0042 | 698.2046 | 779.9692 | 762.073
661.0042 | 698.0819 | 780.9011 | 763.6766
662.0042 | 698.062 | 781.0122 | 763.8242
663.0042 | 698.0408 | 781.0975 | 763.5842
664.0042 | 697.8293 | 781.111 | 763.4806
665.0042 | 697.6826 | 780.8647 | 762.9825
666.0042 | 697.6952 | 781.2206 | 763.3207
667.0042 | 697.748 | 781.2602 | 763.2535
668.0042 | 697.7722 | 781.5748 | 763.6467
669.0042 | 697.9918 | 781.7265 | 763.4679
670.0042 | 698.0867 | 781.3761 | 762.7889
671.0042 | 698.0988 | 781.6372 | 763.4891
672.0042 | 698.3962 | 781.543 | 762.872
673.0042 | 698.5767 | 781.9751 | 763.5037
674.0042 | 698.5624 | 782.3348 | 763.9009
675.0042 | 698.4987 | 781.8482 | 762.9408
676.0042 | 698.4297 | 782.1024 | 763.1342
677.0042 | 698.4878 | 782.244 | 763.1958
678.0042 | 698.6778 | 782.1726 | 763.0135
679.0042 | 698.9056 | 782.2099 | 762.8145
680.0042 | 698.9909 | 781.8317 | 761.949
681.0042 | 698.9915 | 782.0045 | 762.4656
682.0042 | 698.9673 | 782.0836 | 762.0773
683.0042 | 698.876 | 781.9238 | 761.0426
684.0042 | 698.8811 | 781.9707 | 760.9869
685.0042 | 698.941 | 781.6889 | 759.9381
686.0042 | 698.9764 | 781.9499 | 760.1824
687.0042 | 699.0507 | 781.7958 | 759.6427
688.0042 | 699.2258 | 781.9718 | 759.4228
689.0042 | 699.3012 | 782.2499 | 759.6264
690.0042 | 699.1743 | 782.0944 | 758.695
691.0042 | 699.1558 | 782.5363 | 758.8764
692.0042 | 699.2581 | 782.5217 | 758.739
693.0042 | 699.2705 | 782.581 | 758.534
694.0042 | 699.2081 | 782.9256 | 758.9773
695.0042 | 699.0613 | 782.652 | 758.0516
696.0042 | 698.8243 | 783.0113 | 758.4375
697.0042 | 698.8676 | 782.9465 | 757.8592
698.0042 | 698.9509 | 782.8252 | 757.3168
699.0042 | 699.1566 | 782.917 | 757.0371
700.0042 | 700.2252 | 782.7582 | 756.3176
701.0042 | 701.8795 | 782.9815 | 756.1653
702.0042 | 703.9459 | 783.0881 | 756.1073
703.0042 | 706.1319 | 782.8294 | 755.0756
704.0042 | 708.353 | 783.2118 | 755.3173
705.0042 | 710.915 | 783.5272 | 755.5047
706.0042 | 713.3935 | 784.1337 | 756.1812
707.0042 | 715.7862 | 784.5619 | 756.3443
708.0042 | 718.0621 | 785.1438 | 756.8618
709.0042 | 720.3752 | 785.4487 | 756.7531
710.0042 | 722.6361 | 785.9182 | 756.6086
711.0042 | 724.709 | 786.7655 | 757.5843
712.0042 | 726.5215 | 787.5691 | 758.5036
713.0042 | 728.1351 | 787.8881 | 758.1427
714.0042 | 729.503 | 788.2265 | 758.0766
715.0042 | 730.6931 | 788.7477 | 758.7142
716.0042 | 731.7799 | 789.2627 | 759.1586
717.0042 | 732.5755 | 789.1834 | 758.4304
718.0042 | 733.4222 | 789.3995 | 758.2879
719.0042 | 734.084 | 789.3322 | 757.3172
720.0042 | 734.6357 | 789.1837 | 756.2545
721.0042 | 734.9909 | 789.5219 | 756.683
722.0042 | 735.4355 | 789.5952 | 756.4897
723.0042 | 735.8714 | 789.5766 | 755.8834
724.0042 | 736.3138 | 789.8757 | 756.2632
725.0042 | 736.6926 | 789.5238 | 755.1096
726.0042 | 737.0964 | 789.7988 | 755.453
727.0042 | 737.3684 | 789.7419 | 755.0401
728.0042 | 737.6536 | 789.5298 | 754.5134
729.0042 | 737.8217 | 789.4623 | 754.3739
730.0042 | 738.0581 | 789.2414 | 753.8741
731.0042 | 738.3873 | 789.3898 | 754.3786
732.0042 | 738.7884 | 789.1885 | 753.9497
733.0042 | 739.2222 | 788.9956 | 753.5549
734.0042 | 739.5463 | 788.625 | 752.6214
735.0042 | 739.9778 | 788.1394 | 751.4592
736.0042 | 740.3005 | 788.3224 | 752.1197
737.0042 | 740.7659 | 788.1888 | 751.7137
738.0042 | 741.2755 | 788.0285 | 751.3298
739.0042 | 741.6701 | 787.7739 | 750.81
740.0042 | 742.0793 | 787.3092 | 749.83
741.0042 | 742.5182 | 787.1389 | 749.752
742.0042 | 742.8358 | 786.7358 | 748.9463
743.0042 | 743.012 | 786.417 | 748.421
744.0042 | 743.0552 | 786.0074 | 747.6222
745.0042 | 743.2939 | 785.2303 | 745.8169
746.0042 | 743.7112 | 784.9784 | 745.6325
747.0042 | 743.9775 | 784.6683 | 745.2699
748.0042 | 744.1777 | 784.3611 | 745.0202
749.0042 | 744.4345 | 783.8207 | 744.2391
750.0042 | 744.6813 | 783.1131 | 742.863
751.0042 | 744.7604 | 782.6786 | 742.3333
752.0042 | 745.0687 | 782.203 | 741.7111
753.0042 | 745.2969 | 781.8542 | 741.4479
754.0042 | 745.5887 | 781.454 | 741.1281
755.0042 | 745.5956 | 780.829 | 740.2051
756.0042 | 745.8477 | 780.6891 | 740.8176
757.0042 | 746.0826 | 780.2136 | 740.6306
758.0042 | 746.2428 | 779.6564 | 740.1119
759.0042 | 746.3668 | 779.3092 | 740.311
760.0042 | 746.3059 | 778.4302 | 738.986
761.0042 | 746.4678 | 777.91 | 738.8633
762.0042 | 746.5953 | 777.2849 | 738.4237
763.0042 | 746.5535 | 776.3942 | 737.3282
764.0042 | 746.5365 | 775.7321 | 736.8544
765.0042 | 746.7173 | 775.0798 | 736.4736
766.0042 | 746.7869 | 774.7309 | 737.0316
767.0042 | 746.6877 | 774.1677 | 736.942
768.0042 | 746.6047 | 773.3714 | 736.1148
769.0042 | 746.5656 | 772.5693 | 735.2692
770.0042 | 746.7171 | 771.5437 | 733.7823
771.0042 | 746.915 | 771.3047 | 734.754
772.0042 | 747.1596 | 770.6657 | 734.4892
773.0042 | 747.0685 | 769.8641 | 733.7808
774.0042 | 747.0093 | 769.1156 | 733.0454
775.0042 | 747.1023 | 768.3793 | 732.3605
776.0042 | 747.1914 | 767.7739 | 731.9869
777.0042 | 747.3224 | 767.0585 | 731.3121
778.0042 | 747.5438 | 766.4895 | 731.0086
779.0042 | 747.5434 | 765.7927 | 730.3076
780.0042 | 747.6349 | 765.0357 | 729.5415
781.0042 | 747.6785 | 764.488 | 729.2728
782.0042 | 747.7461 | 763.9337 | 729.0498
783.0042 | 747.9377 | 763.3453 | 728.6972
784.0042 | 748.1383 | 762.5542 | 727.6932
785.0042 | 748.1744 | 761.8442 | 726.8904
786.0042 | 748.3406 | 761.0482 | 725.8327
787.0042 | 748.4856 | 760.3859 | 725.141
788.0042 | 748.3354 | 759.934 | 725.1016
789.0042 | 748.2837 | 759.5271 | 725.1726
790.0042 | 748.3013 | 758.8343 | 724.445
791.0042 | 748.2555 | 758.4327 | 724.4512
792.0042 | 748.1601 | 757.7708 | 723.5856
793.0042 | 748.2112 | 757.2126 | 723.0271
794.0042 | 748.2045 | 756.8694 | 723.0043
795.0042 | 748.2568 | 756.3985 | 722.5172
796.0042 | 748.418 | 756.0703 | 722.4221
797.0042 | 748.6164 | 755.5373 | 721.7632
798.0042 | 748.746 | 755.2625 | 722.0572
799.0042 | 748.8539 | 754.9301 | 722.0743
800.0042 | 748.8063 | 754.3712 | 721.2563
801.0042 | 748.6704 | 754.1663 | 721.5697
802.0042 | 748.4932 | 753.7638 | 721.2011
803.0042 | 748.3539 | 753.4063 | 720.9618
804.0042 | 748.5067 | 753.0993 | 720.8566
805.0042 | 748.4615 | 752.4235 | 719.5094
806.0042 | 748.4194 | 752.1871 | 719.4745
807.0042 | 748.3583 | 751.8509 | 719.1307
808.0042 | 748.4067 | 751.3931 | 718.2898
809.0042 | 748.4638 | 751.2749 | 718.5063
810.0042 | 748.5719 | 750.8071 | 717.559
811.0042 | 748.65 | 750.6883 | 717.7557
812.0042 | 748.6302 | 750.4536 | 717.4464
813.0042 | 748.7673 | 750.2157 | 717.0245
814.0042 | 748.6615 | 749.8815 | 716.3638
815.0042 | 748.6678 | 749.4005 | 715.2634
816.0042 | 748.6755 | 749.3538 | 715.6842
817.0042 | 748.6432 | 749.0971 | 715.3777
818.0042 | 748.6074 | 748.8703 | 715.1936
819.0042 | 748.504 | 748.6034 | 714.839
820.0042 | 748.6434 | 748.2267 | 713.9963
821.0042 | 748.5316 | 748.2311 | 714.3977
822.0042 | 748.3699 | 747.8626 | 713.6108
823.0042 | 748.4896 | 747.7626 | 713.712
824.0042 | 748.4966 | 747.5335 | 713.3247
825.0042 | 748.597 | 747.2972 | 712.9891
826.0042 | 748.5179 | 747.3088 | 713.3505
827.0042 | 748.4495 | 747.1089 | 712.9906
828.0042 | 748.4299 | 746.9172 | 712.6778
829.0042 | 748.4331 | 746.7115 | 712.2341
830.0042 | 748.4223 | 746.4877 | 711.7446
831.0042 | 748.726 | 746.4854 | 711.9393
832.0042 | 748.9368 | 746.5058 | 712.1767
833.0042 | 749.1605 | 746.4045 | 712.0656
834.0042 | 749.3202 | 746.3308 | 711.9929
835.0042 | 749.3476 | 746.1218 | 711.4064
836.0042 | 749.4256 | 746.1855 | 711.6817
837.0042 | 749.4942 | 746.1293 | 711.5825
838.0042 | 749.5045 | 746.0688 | 711.5917
839.0042 | 749.342 | 746.0481 | 711.6898
840.0042 | 749.3166 | 745.822 | 711.1885
841.0042 | 749.3172 | 745.858 | 711.452
842.0042 | 749.2595 | 745.7483 | 711.2121
843.0042 | 749.0126 | 745.6444 | 711.0258
844.0042 | 748.9728 | 745.6619 | 711.2436
845.0042 | 748.8452 | 745.5106 | 710.9799
846.0042 | 748.8028 | 745.4687 | 711.1094
847.0042 | 748.8957 | 745.3072 | 710.8092
848.0042 | 748.9445 | 745.2243 | 710.7954
849.0042 | 749.0082 | 745.3754 | 711.49
850.0042 | 748.9354 | 745.1579 | 710.9793
851.0042 | 748.9607 | 745.1715 | 711.2889
852.0042 | 748.9427 | 745.1187 | 711.3333
853.0042 | 748.8643 | 744.9015 | 710.7698
854.0042 | 748.8239 | 744.6781 | 710.2321
855.0042 | 748.8583 | 744.5755 | 710.0259
856.0042 | 748.7949 | 744.5834 | 710.249
857.0042 | 748.8162 | 744.505 | 710.177
858.0042 | 748.8481 | 744.5764 | 710.448
859.0042 | 748.9188 | 744.5296 | 710.3553
860.0042 | 749.0777 | 744.4134 | 710.056
861.0042 | 749.1836 | 744.466 | 710.2956
862.0042 | 749.0939 | 744.4815 | 710.5228
863.0042 | 749.1591 | 744.2967 | 709.975
864.0042 | 749.0678 | 744.2073 | 709.7801
865.0042 | 749.0414 | 743.9696 | 709.0517
866.0042 | 748.9681 | 744.002 | 709.3762
867.0042 | 748.8757 | 744.0813 | 709.6968
868.0042 | 748.8091 | 743.9633 | 709.474
869.0042 | 748.6948 | 743.8966 | 709.3128
870.0042 | 748.6104 | 743.6734 | 708.6397
871.0042 | 748.5301 | 743.6593 | 708.7879
872.0042 | 748.6567 | 743.5698 | 708.5681
873.0042 | 748.7951 | 743.4965 | 708.4896
874.0042 | 748.7518 | 743.3636 | 708.1447
875.0042 | 748.6483 | 743.2345 | 707.939
876.0042 | 748.5964 | 743.2555 | 708.2962
877.0042 | 748.4755 | 742.965 | 707.5504
878.0042 | 748.3901 | 743.1452 | 708.4184
879.0042 | 748.4092 | 743.0008 | 708.112
880.0042 | 748.5712 | 742.9162 | 708.0818
881.0042 | 748.6782 | 743.0771 | 708.816
882.0042 | 748.9567 | 743.056 | 708.8968
883.0042 | 749.038 | 743.1895 | 709.4538
884.0042 | 749.1604 | 743.3471 | 710.1454
885.0042 | 749.361 | 743.2233 | 709.8616
886.0042 | 749.4535 | 743.2408 | 710.0017
887.0042 | 749.5077 | 743.2098 | 710.0438
888.0042 | 749.4316 | 743.0958 | 709.7427
889.0042 | 749.4968 | 743.1704 | 710.1501
890.0042 | 749.3633 | 743.0435 | 709.8196
891.0042 | 749.2446 | 743.0597 | 710.0126
892.0042 | 749.1938 | 743.2945 | 711.1133
893.0042 | 749.332 | 743.1468 | 710.7365
894.0042 | 749.3882 | 743.157 | 711.0322
895.0042 | 749.2891 | 742.8769 | 710.2575
896.0042 | 749.0809 | 742.873 | 710.4878
897.0042 | 749.1602 | 742.7844 | 710.4274
898.0042 | 749.1076 | 742.7069 | 710.4564
899.0042 | 749.1018 | 742.4553 | 709.8609
900.0042 | 749.0893 | 742.3177 | 709.5784
901.0042 | 749.0003 | 742.4152 | 710.008
902.0042 | 748.7744 | 742.4455 | 710.1353
903.0042 | 748.7756 | 742.3243 | 709.7992
904.0042 | 748.7584 | 742.26 | 709.679
905.0042 | 748.5586 | 742.0997 | 709.2177
906.0042 | 748.5785 | 742.1619 | 709.462
907.0042 | 748.5726 | 741.9853 | 708.8648
908.0042 | 748.6789 | 741.8494 | 708.4314
909.0042 | 748.5893 | 741.718 | 708.1074
910.0042 | 748.633 | 741.5236 | 707.5593
911.0042 | 748.6302 | 741.6108 | 708.0137
912.0042 | 748.7282 | 741.7283 | 708.5808
913.0042 | 748.4937 | 741.6378 | 708.3513
914.0042 | 748.3955 | 741.5033 | 708.1232
915.0042 | 748.5226 | 741.4921 | 708.3801
916.0042 | 748.6875 | 741.5938 | 708.8964
917.0042 | 748.7918 | 741.3789 | 708.2024
918.0042 | 748.8322 | 741.2816 | 707.9069
919.0042 | 748.862 | 741.3071 | 708.0461
920.0042 | 748.8574 | 741.2933 | 708.026
921.0042 | 748.9135 | 741.2466 | 707.8286
922.0042 | 748.9277 | 741.379 | 708.4843
923.0042 | 748.9716 | 741.3246 | 708.2624
924.0042 | 749.0562 | 741.5248 | 709.0696
925.0042 | 749.1231 | 741.3336 | 708.3621
926.0042 | 748.9605 | 741.3043 | 708.3845
927.0042 | 748.7113 | 741.2014 | 708.1492
928.0042 | 748.7228 | 741.1825 | 708.2127
929.0042 | 748.6999 | 741.0496 | 707.8772
930.0042 | 748.6232 | 740.8538 | 707.3078
931.0042 | 748.466 | 740.766 | 707.2104
932.0042 | 748.4156 | 740.6939 | 707.1087
933.0042 | 748.3022 | 740.7584 | 707.5021
934.0042 | 748.1853 | 740.658 | 707.2707
935.0042 | 748.1507 | 740.4595 | 706.6856
936.0042 | 748.1093 | 740.4012 | 706.7306
937.0042 | 747.9579 | 740.3702 | 706.7614
938.0042 | 747.8538 | 740.2281 | 706.4832
939.0042 | 747.9861 | 740.0118 | 706.0479
940.0042 | 747.9939 | 739.7319 | 705.3116
941.0042 | 747.9784 | 739.6966 | 705.4955
942.0042 | 748.0417 | 739.6378 | 705.4594
943.0042 | 748.0305 | 739.6313 | 705.6743
944.0042 | 748.045 | 739.6087 | 705.8024
945.0042 | 748.1394 | 739.4116 | 705.2539
946.0042 | 748.0857 | 739.4808 | 705.8072
947.0042 | 748.0542 | 739.4907 | 706.095
948.0042 | 748.1954 | 739.4539 | 706.0799
949.0042 | 748.251 | 739.3993 | 706.0438
950.0042 | 748.2814 | 739.2991 | 705.7615
951.0042 | 748.442 | 739.238 | 705.7005
952.0042 | 748.4221 | 739.1511 | 705.5935
953.0042 | 748.4371 | 739.1591 | 705.6208
954.0042 | 748.4632 | 739.2075 | 705.9584
955.0042 | 748.4 | 739.0937 | 705.474
956.0042 | 748.3479 | 739.0731 | 705.5129
957.0042 | 748.2952 | 739.0982 | 705.6634
958.0042 | 748.3091 | 739.1644 | 705.8675
959.0042 | 748.4386 | 739.2507 | 706.1961
960.0042 | 748.5547 | 739.0663 | 705.3768
961.0042 | 748.6287 | 739.034 | 705.3726
962.0042 | 748.6817 | 738.9714 | 705.1984
963.0042 | 748.6886 | 738.9339 | 705.2702
964.0042 | 748.7721 | 738.7937 | 704.9344
965.0042 | 748.7592 | 738.644 | 704.4835
966.0042 | 748.7382 | 738.6429 | 704.5697
967.0042 | 748.8064 | 738.5007 | 704.136
968.0042 | 748.7843 | 738.4391 | 703.9717
969.0042 | 748.968 | 738.3813 | 703.8983
970.0042 | 749.1361 | 738.3023 | 703.7549
971.0042 | 749.0434 | 738.2857 | 704.0222
972.0042 | 748.9759 | 738.1379 | 703.6894
973.0042 | 749.022 | 738.1229 | 703.7821
974.0042 | 749.0314 | 738.0337 | 703.5745
975.0042 | 749.0634 | 737.9494 | 703.2748
976.0042 | 749.0406 | 737.9424 | 703.3882
977.0042 | 748.9761 | 737.9633 | 703.5953
978.0042 | 749.0186 | 737.8821 | 703.4479
979.0042 | 749.0639 | 737.7558 | 703.06
980.0042 | 749.1179 | 737.819 | 703.5097
981.0042 | 749.0747 | 737.8489 | 703.6962
982.0042 | 749.0198 | 737.8456 | 704.0057
983.0042 | 749.0138 | 737.7596 | 703.8398
984.0042 | 749.0164 | 737.7396 | 703.8746
985.0042 | 749.0362 | 737.6724 | 703.8063
986.0042 | 749.1146 | 737.5323 | 703.4058
987.0042 | 749.1746 | 737.5025 | 703.4087
988.0042 | 749.1932 | 737.3322 | 702.8802
989.0042 | 749.2103 | 737.2852 | 702.9425
990.0042 | 749.2586 | 737.1902 | 702.8167
991.0042 | 749.3177 | 737.1413 | 702.8381
992.0042 | 749.3978 | 737.0656 | 702.7848
993.0042 | 749.3906 | 736.9761 | 702.6287
994.0042 | 749.3029 | 736.8999 | 702.4703
995.0042 | 749.2615 | 736.7263 | 701.9243
996.0042 | 749.1953 | 736.6766 | 701.8864
997.0042 | 749.2255 | 736.6275 | 701.8483
998.0042 | 749.3642 | 736.6164 | 701.8778
999.0042 | 749.4369 | 736.5607 | 701.7393
1000.0042 | 749.2892 | 736.5185 | 701.5951
1001.0042 | 749.1346 | 736.4629 | 701.5704
1002.0042 | 749.0246 | 736.4323 | 701.6319
1003.0042 | 748.9091 | 736.4016 | 701.6613
1004.0042 | 748.8402 | 736.2621 | 701.1497
1005.0042 | 748.8357 | 736.2015 | 701.0512
1006.0042 | 748.6876 | 736.0987 | 700.8312
1007.0042 | 748.6375 | 735.9792 | 700.6148
1008.0042 | 748.7175 | 735.8757 | 700.3658
1009.0042 | 748.6369 | 735.8298 | 700.4225
1010.0042 | 748.7248 | 735.7608 | 700.2472
1011.0042 | 748.8267 | 735.6936 | 700.2219
1012.0042 | 748.8973 | 735.5689 | 699.9478
1013.0042 | 748.9151 | 735.3478 | 699.325
1014.0042 | 748.9704 | 735.2757 | 699.2431
1015.0042 | 748.8645 | 735.3192 | 699.8495
1016.0042 | 748.8381 | 735.2429 | 699.6731
1017.0042 | 748.8709 | 735.1761 | 699.6152
1018.0042 | 748.7902 | 735.0434 | 699.2507
1019.0042 | 748.7826 | 735.0521 | 699.4379
1020.0042 | 748.8506 | 734.8595 | 698.8026
1021.0042 | 748.8752 | 734.8105 | 698.8057
1022.0042 | 748.7709 | 734.7595 | 698.9555
1023.0042 | 748.7898 | 734.6516 | 698.7077
1024.0042 | 748.8559 | 734.523 | 698.4038
1025.0042 | 748.863 | 734.3301 | 697.7476
1026.0042 | 748.8587 | 734.2902 | 697.9138
1027.0042 | 748.7504 | 734.2769 | 697.9911
1028.0042 | 748.7302 | 734.2408 | 697.9523
1029.0042 | 748.8715 | 734.2352 | 698.0388
1030.0042 | 748.883 | 734.1862 | 697.9446
1031.0042 | 748.9968 | 734.166 | 697.8836
1032.0042 | 749.1761 | 734.1545 | 697.9523
1033.0042 | 749.2285 | 734.1324 | 697.9667
1034.0042 | 749.2791 | 734.1571 | 698.0712
1035.0042 | 749.1055 | 734.1519 | 698.0069
1036.0042 | 748.9877 | 734.092 | 697.7329
1037.0042 | 749.0818 | 734.025 | 697.7425
1038.0042 | 749.0844 | 734.0348 | 698.1265
1039.0042 | 749.2084 | 733.9966 | 698.1678
1040.0042 | 749.3575 | 733.9327 | 698.0587
1041.0042 | 749.2101 | 733.964 | 698.2795
1042.0042 | 749.1891 | 733.9354 | 698.3681
1043.0042 | 749.1171 | 733.9206 | 698.4373
1044.0042 | 749.1231 | 733.961 | 698.7758
1045.0042 | 748.9726 | 733.9269 | 698.7511
1046.0042 | 748.7432 | 733.8993 | 698.7474
1047.0042 | 748.7528 | 733.7756 | 698.3973
1048.0042 | 748.6955 | 733.7449 | 698.2988
1049.0042 | 748.5909 | 733.7873 | 698.7364
1050.0042 | 748.6048 | 733.7797 | 698.7345
1051.0042 | 748.644 | 733.7945 | 698.9409
1052.0042 | 748.8232 | 733.7553 | 698.9295
1053.0042 | 748.7754 | 733.6945 | 698.8637
1054.0042 | 748.6934 | 733.645 | 698.8623
1055.0042 | 748.6342 | 733.6274 | 699.0477
1056.0042 | 748.6682 | 733.6566 | 699.4771
1057.0042 | 748.6686 | 733.6238 | 699.6834
1058.0042 | 748.6009 | 733.5304 | 699.5286
1059.0042 | 748.7102 | 733.4537 | 699.5255
1060.0042 | 748.7295 | 733.3986 | 699.5444
1061.0042 | 748.6659 | 733.4197 | 699.9548
1062.0042 | 748.8413 | 733.3902 | 700.1549
1063.0042 | 748.8858 | 733.3083 | 700.0974
1064.0042 | 748.7885 | 733.2551 | 700.0209
1065.0042 | 748.7611 | 733.2218 | 700.0682
1066.0042 | 748.887 | 733.2173 | 700.1771
1067.0042 | 748.8068 | 733.2136 | 700.2744
1068.0042 | 748.7741 | 733.1876 | 700.2535
1069.0042 | 748.8531 | 733.1605 | 700.4949
1070.0042 | 749.0214 | 733.0687 | 700.2269
1071.0042 | 748.9157 | 733.1016 | 700.6129
1072.0042 | 748.8078 | 733.0672 | 700.7274
1073.0042 | 748.7748 | 733.0718 | 701.0733
1074.0042 | 748.6809 | 733.1309 | 701.6069
1075.0042 | 748.6061 | 733.1285 | 701.7484
1076.0042 | 748.7543 | 733.1239 | 701.7806
1077.0042 | 748.7834 | 733.1255 | 701.9875
1078.0042 | 748.8272 | 733.1379 | 702.1822
1079.0042 | 748.6355 | 733.1514 | 702.3867
1080.0042 | 748.5386 | 733.1305 | 702.4687
1081.0042 | 748.5102 | 732.917 | 701.3206
1082.0042 | 748.6424 | 733.0592 | 702.2654
1083.0042 | 748.8224 | 733.1142 | 702.7811
1084.0042 | 748.9052 | 733.1287 | 702.9005
1085.0042 | 749.1206 | 733.1732 | 703.2827
1086.0042 | 749.1068 | 733.198 | 703.6539
1087.0042 | 749.1464 | 733.1799 | 703.9047
1088.0042 | 749.2667 | 733.1426 | 703.8325
1089.0042 | 749.2037 | 733.0977 | 703.9536
1090.0042 | 749.1587 | 733.0909 | 703.9571
1091.0042 | 749.0583 | 733.0151 | 703.632
1092.0042 | 749.0707 | 733.0461 | 703.8371
1093.0042 | 749.0934 | 733.0742 | 704.1361
1094.0042 | 749.1984 | 733.0648 | 704.2121
1095.0042 | 749.2916 | 733.0148 | 704.1499
1096.0042 | 749.3842 | 732.9718 | 704.1512
1097.0042 | 749.3026 | 732.9377 | 704.1483
1098.0042 | 749.252 | 732.9193 | 704.2993
1099.0042 | 749.2076 | 732.8961 | 704.3661
1100.0042 | 749.0783 | 732.9033 | 704.6331
1101.0042 | 749.0906 | 732.8843 | 704.7685
1102.0042 | 749.0119 | 732.8614 | 704.8671
1103.0042 | 748.9218 | 732.8428 | 704.9327
1104.0042 | 748.9188 | 732.8515 | 705.1106
1105.0042 | 748.9672 | 732.8331 | 705.4287
1106.0042 | 748.9206 | 732.7846 | 705.6061
1107.0042 | 748.8137 | 732.72 | 705.7507
1108.0042 | 748.7774 | 732.6668 | 705.7558
1109.0042 | 748.6775 | 732.6224 | 706.0071
1110.0042 | 748.7105 | 732.6002 | 706.1271
1111.0042 | 748.7064 | 732.5857 | 706.2424
1112.0042 | 748.6158 | 732.5197 | 706.2021
1113.0042 | 748.6802 | 732.5198 | 706.3448
1114.0042 | 748.4729 | 732.542 | 706.795
1115.0042 | 748.4643 | 732.5005 | 706.8203
1116.0042 | 748.555 | 732.4152 | 706.6485
1117.0042 | 748.5798 | 732.4549 | 707.2573
1118.0042 | 748.5612 | 732.3992 | 707.3432
1119.0042 | 748.5693 | 732.32 | 707.3001
1120.0042 | 748.7084 | 732.2838 | 707.3338
1121.0042 | 748.689 | 732.247 | 707.5406
1122.0042 | 748.669 | 732.2132 | 707.5125
1123.0042 | 748.6269 | 732.2368 | 707.7211
1124.0042 | 748.6227 | 732.2498 | 707.9357
1125.0042 | 748.8589 | 732.229 | 708.0761
1126.0042 | 748.9533 | 732.2131 | 708.1355
1127.0042 | 748.9698 | 732.1881 | 708.26
1128.0042 | 748.8345 | 732.176 | 708.3645
1129.0042 | 748.7659 | 732.1653 | 708.713
1130.0042 | 748.8084 | 732.0957 | 708.9779
1131.0042 | 748.7654 | 732.0952 | 709.6124
1132.0042 | 748.666 | 732.0294 | 709.7141
1133.0042 | 748.6341 | 731.9469 | 709.648
1134.0042 | 748.6615 | 731.8678 | 709.4691
1135.0042 | 748.7444 | 731.7879 | 709.5345
1136.0042 | 748.7045 | 731.7389 | 709.4953
1137.0042 | 748.6987 | 731.6963 | 709.4401
1138.0042 | 748.8243 | 731.6576 | 709.1382
1139.0042 | 748.901 | 731.6094 | 708.8391
1140.0042 | 749.0971 | 731.5629 | 708.7487
1141.0042 | 749.0473 | 731.4592 | 708.3716
1142.0042 | 749.0985 | 731.406 | 708.4447
1143.0042 | 749.1327 | 731.4034 | 708.5877
1144.0042 | 749.0943 | 731.3534 | 708.4003
1145.0042 | 749.1201 | 731.3186 | 708.1257
1146.0042 | 749.0967 | 731.3077 | 708.2353
1147.0042 | 749.1032 | 731.1992 | 707.646
1148.0042 | 749.1325 | 731.0768 | 706.83
1149.0042 | 749.0845 | 731.0163 | 706.438
1150.0042 | 749.0465 | 730.8765 | 705.6985
1151.0042 | 749.0235 | 730.814 | 705.7016