## Test Conditions
DESIREE-FIRE Test Number 26 - Circuit Simulator Data Only
Test Date: | 2009-07-23
DCSim DAQ Start Time | 10:47
DCSim Time for Synchronization | 11:18
Heat Source Synchronization | 0:01 | hour:minutes:seconds
Heat Source DAQ Start Time | 11:17
Fire Time | 11:28
Offset | 0:41 | hour:minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 2444 | seconds
Heat Source Offset | 0:11 | hour:minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 665 | seconds
Heat Source Stop Time | 11:54
Test Duration | 0:26 | hour:minutes:seconds
| 1566 | seconds
CT500 turns | 1 | 1 or 2 | This is the number of times the lead conductor within the DCSim Panels were wrapped around the Hall Effect Device of the current transducer.
CT35 turns | 1 | 1 or 5
Pre-Test Baseline: | Gathered | Gathered or Not Gathered
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit Number | Cable Type |  | Cable TC Channel | Air TC Channel
SOV 1 | Silicon Rubber, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
SOV 2 | Silicon Rubber, 7c, 12AWG |  | Channel 3 and Channel 4 represent the side and top of the thermocouple cable, respectively. | TC11 in the Temperature Data File
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds. Two different current transducers were for each circuit. One current transducer (Ohio Semitronics, model number CTL-51/35) was used to detect lower (0 - 35A) amperage transient behavior through a paired and calibrated signal conditioner (CTA201RX5). The other transducer (Ohio Semitronics, model number CTL-601/500) was set to detect transient current increases from 0 - 500A. These were also paired and calibrated with a signal conditioner (CTA2-1X5).
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | SOV-1_CT500 | SOV-1_CT35_1_P | SOV-1_CT35_2_S1 | SOV-1_CT35_3_G | SOV-1_CT35_4_S2 | SOV-1_CT35_5_N | SOV-2_CT500 | SOV-2_CT35_1_P | SOV-2_CT35_2_S1 | SOV-2_CT35_3_G | SOV-2_CT35_4_S2 | SOV-2_CT35_5_N | SOV-1_VT7_1_R | SOV-1_VT7_2_SP | SOV-1_VT7_3_S | SOV-1_VTU_1_P | SOV-1_VTU_2_S1 | SOV-1_VTU_3_G | SOV-1_VTU_4_N | SOV-2_VT7_1_R | SOV-2_VT7_2_SP | SOV-2_VT7_3_S | SOV-2_VTU_1_P | SOV-2_VTU_2_S1 | SOV-2_VTU_3_G | SOV-2_VTU_4_N | {SOV1} V(N) - V(Batt -) | {SOV1} V(P) - V(Batt +) | {SOV1} V(R) - V(Batt -) | {SOV1} V(S) - V(Batt -) | {SOV1} V(S) - V(N) | {SOV1} V(S1) - V(Batt +) | {SOV1} V(G) - V(Batt +) | {SOV2} V(N) - V(Batt -) | {SOV2} V(P) - V(Batt +) | {SOV2} V(R) - V(Batt -) | {SOV2} V(S) - V(Batt -) | {SOV2} V(S) - V(N) | {SOV2} V(S1) - V(Batt +) | {SOV2} V(G) - V(Batt +) | {SOV1} V(P) - V(Batt -) | {SOV1} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV1} V(SP) - V(Batt -) | {SOV1} V(N) - V(Batt +) | {SOV2} V(P) - V(Batt -) | {SOV2} V(S1) - V(Batt -) | {SOV1} V(G) - V(Batt -) | {SOV2} V(SP) - V(Batt -) | {SOV2} V(N) - V(Batt +)
-0.73438 | 123.1476 | -66.6962 | 56.3004 | 0.057412 | 0.0043572 | -0.0010997 | 0.058508 | 7.3304e-05 | 0.054873 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.066382 | -0.0034461 | 0.067869 | -66.6969 | 0.033457 | -66.6544 | 56.2289 | 56.0327 | 56.2436 | -66.8192 | -66.697 | 0.03241 | -66.7544 | 56.1344 | 56.2893 | 56.2559 | -66.9828 | -0.12303 | -0.071407 | -0.00074 | 0.041728 | 0.16476 | -0.26769 | -0.056771 | -0.28666 | -0.16591 | -0.000852 | -0.058251 | 0.22841 | -0.011044 | -0.044471 | 122.9251 | 122.7288 | 122.9398 | 66.7296 | -123.1196 | 122.8306 | 122.9855 | 122.952 | 66.7286 | -123.2832
0.26562 | 123.1567 | -66.6916 | 56.2592 | 0.04215 | 0.0043572 | -0.0010997 | 0.058508 | -0.0009947 | 0.05701 | 0.058145 | 0.00062833 | -0.0010156 | 0.065314 | -0.0034461 | 0.066801 | -66.7106 | 0.038035 | -66.659 | 56.2335 | 56.0372 | 56.2344 | -66.8192 | -66.697 | 0.023253 | -66.7544 | 56.1344 | 56.2847 | 56.2238 | -66.9828 | -0.12761 | -0.02563 | -0.019053 | 0.032572 | 0.16018 | -0.22192 | -0.02473 | -0.29124 | -0.12471 | -0.00543 | -0.062829 | 0.22841 | 0.025576 | -0.035323 | 122.9251 | 122.7288 | 122.926 | 66.7296 | -123.0784 | 122.826 | 122.9763 | 122.9154 | 66.7148 | -123.242
1.2656 | 123.1338 | -66.7007 | 56.2775 | 0.072674 | 0.0054252 | 0.0031733 | 0.057439 | -0.0009947 | 0.055941 | 0.058145 | 0.00062833 | 0.0011204 | 0.066382 | -0.0023781 | 0.066801 | -66.6969 | 0.033457 | -66.659 | 56.2289 | 56.0235 | 56.2436 | -66.8238 | -66.7016 | 0.027831 | -66.759 | 56.1344 | 56.2802 | 56.1964 | -66.9828 | -0.12303 | -0.048519 | 0.003838 | 0.041728 | 0.16476 | -0.25396 | -0.033883 | -0.28208 | -0.14302 | -0.000853 | -0.058251 | 0.22383 | 0.002687 | -0.081105 | 122.9297 | 122.7242 | 122.9443 | 66.7342 | -123.1012 | 122.8352 | 122.9809 | 122.8971 | 66.7286 | -123.2603
2.2656 | 123.1796 | -66.7099 | 56.2683 | 0.04215 | 0.0043572 | 0.0010373 | 0.058508 | 0.0011413 | 0.055941 | 0.058145 | -0.00043967 | 0.0011204 | 0.066382 | -0.0045141 | 0.065733 | -66.6923 | 0.033457 | -66.659 | 56.2289 | 56.0281 | 56.239 | -66.8238 | -66.7108 | 0.027831 | -66.7498 | 56.1299 | 56.2893 | 56.1414 | -66.9874 | -0.11388 | -0.039364 | 0.017572 | 0.050883 | 0.16476 | -0.24023 | -0.029307 | -0.27751 | -0.13844 | -0.000855 | -0.039939 | 0.23757 | 0.020999 | -0.12689 | 122.9388 | 122.738 | 122.9489 | 66.7434 | -123.0921 | 122.8398 | 122.9992 | 122.8513 | 66.7377 | -123.2557
3.2656 | 123.1567 | -66.6595 | 56.2912 | 0.04215 | 0.0022202 | -3.1667e-05 | 0.057439 | 0.0011413 | 0.05701 | 0.058145 | 0.00062833 | -0.0020846 | 0.065314 | -0.0045141 | 0.064664 | -66.6923 | 0.033457 | -66.6636 | 56.2244 | 56.0372 | 56.2436 | -66.8238 | -66.7016 | 0.027831 | -66.7453 | 56.1344 | 56.2802 | 56.0727 | -66.9874 | -0.16423 | -0.066831 | -0.032782 | -0.00405 | 0.16018 | -0.25396 | -0.047616 | -0.32786 | -0.15675 | -0.042052 | -0.085714 | 0.24215 | -0.011046 | -0.21846 | 122.8839 | 122.6968 | 122.9031 | 66.693 | -123.115 | 122.794 | 122.9397 | 122.7323 | 66.6874 | -123.2786
4.2656 | 123.1842 | -66.687 | 56.2958 | 0.057412 | 0.0032892 | -3.1667e-05 | 0.057439 | 0.0011413 | 0.058078 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.066382 | -0.0034461 | 0.066801 | -66.6969 | 0.033457 | -66.6544 | 56.2244 | 56.0372 | 56.2344 | -66.8238 | -66.7062 | 0.03241 | -66.7498 | 56.1436 | 56.2893 | 56.1735 | -66.9828 | -0.13677 | -0.071408 | -0.009895 | 0.032573 | 0.16934 | -0.25854 | -0.061351 | -0.29582 | -0.15217 | -0.019164 | -0.062827 | 0.23299 | -0.006466 | -0.12231 | 122.9114 | 122.7242 | 122.9214 | 66.7205 | -123.1196 | 122.8306 | 122.9763 | 122.8605 | 66.7194 | -123.2786
5.2656 | 123.1155 | -66.6779 | 56.2912 | 0.04215 | 0.0043572 | -0.0010997 | 0.059576 | 0.0011413 | 0.05701 | 0.073406 | -0.00043967 | -0.0010156 | 0.066382 | -0.0045141 | 0.064664 | -66.6969 | 0.038035 | -66.659 | 56.2335 | 56.0418 | 56.2436 | -66.8192 | -66.6924 | 0.027831 | -66.7453 | 56.1344 | 56.2802 | 56.1506 | -66.992 | -0.14134 | -0.057674 | -0.019051 | 0.018839 | 0.16018 | -0.24938 | -0.047616 | -0.31413 | -0.15675 | -0.014584 | -0.067404 | 0.24673 | -0.011046 | -0.14062 | 122.9114 | 122.7197 | 122.9214 | 66.7159 | -123.1104 | 122.8123 | 122.958 | 122.8284 | 66.7057 | -123.2832
6.2656 | 123.1155 | -66.687 | 56.2683 | 0.072674 | 0.0032892 | 0.0010373 | 0.058508 | 7.3304e-05 | 0.05701 | 0.058145 | 0.0016963 | -0.0010156 | 0.064245 | -0.0034461 | 0.064664 | -66.7015 | 0.028878 | -66.659 | 56.2289 | 56.0372 | 56.2436 | -66.8146 | -66.697 | 0.03241 | -66.7544 | 56.1344 | 56.2802 | 56.1368 | -66.9874 | -0.12761 | -0.039364 | -0.014473 | 0.027995 | 0.1556 | -0.23107 | -0.024728 | -0.3004 | -0.13387 | -0.010007 | -0.067406 | 0.23299 | 0.011842 | -0.13147 | 122.916 | 122.7242 | 122.9306 | 66.7159 | -123.0829 | 122.8215 | 122.9672 | 122.8239 | 66.7194 | -123.2557
7.2656 | 123.1613 | -66.6962 | 56.282 | 0.072674 | 0.0054252 | 0.0021053 | 0.055302 | 7.3304e-05 | 0.054873 | 0.088667 | 0.00062833 | -0.0020846 | 0.065314 | -0.0045141 | 0.066801 | -66.7015 | 0.033457 | -66.6636 | 56.2244 | 56.0418 | 56.2436 | -66.8192 | -66.697 | 0.03241 | -66.759 | 56.139 | 56.2802 | 56.2055 | -66.9828 | -0.12303 | -0.057675 | -0.005318 | 0.032571 | 0.1556 | -0.24023 | -0.03846 | -0.28666 | -0.14302 | -0.000852 | -0.062829 | 0.22383 | -0.00189 | -0.076525 | 122.9205 | 122.738 | 122.9398 | 66.7296 | -123.1012 | 122.8352 | 122.9763 | 122.9017 | 66.7286 | -123.2649
8.2656 | 123.1293 | -66.6779 | 56.3095 | 0.072674 | 0.0032892 | -3.1667e-05 | 0.058508 | -0.0020637 | 0.058078 | 0.10393 | -0.0015087 | 5.2373e-05 | 0.065314 | -0.0034461 | 0.065733 | -66.6969 | 0.033457 | -66.659 | 56.2198 | 56.0327 | 56.239 | -66.8192 | -66.7016 | 0.027831 | -66.7498 | 56.139 | 56.2802 | 56.2193 | -66.992 | -0.14134 | -0.089719 | -0.019051 | 0.018839 | 0.16018 | -0.27685 | -0.070505 | -0.31413 | -0.17048 | -0.023742 | -0.071983 | 0.24215 | -0.029356 | -0.090255 | 122.8976 | 122.7105 | 122.9169 | 66.7113 | -123.1287 | 122.8169 | 122.958 | 122.8971 | 66.7057 | -123.3015
9.2656 | 123.1064 | -66.6824 | 56.2866 | 0.04215 | 0.0022202 | -3.1667e-05 | 0.057439 | 0.0011413 | 0.055941 | 0.042884 | 0.00062833 | -0.0020846 | 0.063177 | -0.0034461 | 0.064664 | -66.7015 | 0.028878 | -66.659 | 56.2289 | 56.0327 | 56.2436 | -66.8192 | -66.7062 | 0.027831 | -66.7453 | 56.139 | 56.2847 | 56.2193 | -66.9782 | -0.13676 | -0.057674 | -0.019051 | 0.023417 | 0.16018 | -0.25396 | -0.043038 | -0.29582 | -0.1476 | -0.023742 | -0.062826 | 0.23299 | -0.00189 | -0.067367 | 122.9114 | 122.7151 | 122.926 | 66.7113 | -123.1058 | 122.8215 | 122.9672 | 122.9017 | 66.7103 | -123.2649
10.2656 | 123.1293 | -66.6962 | 56.2912 | 0.057412 | 0.0032892 | 0.0010373 | 0.058508 | 0.0022103 | 0.055941 | 0.073406 | -0.00043967 | 0.0011204 | 0.066382 | -0.0045141 | 0.065733 | -66.6969 | 0.038035 | -66.659 | 56.2198 | 56.0418 | 56.2436 | -66.8238 | -66.7016 | 0.023253 | -66.7544 | 56.1436 | 56.2847 | 56.1872 | -66.992 | -0.12761 | -0.071409 | -0.00074 | 0.03715 | 0.16476 | -0.24938 | -0.047616 | -0.29582 | -0.1476 | -0.005431 | -0.058251 | 0.23757 | -0.006468 | -0.10399 | 122.916 | 122.738 | 122.9398 | 66.7342 | -123.115 | 122.8398 | 122.9809 | 122.8834 | 66.7194 | -123.2832
11.2656 | 123.1293 | -66.6824 | 56.3004 | 0.04215 | 0.0032892 | -3.1667e-05 | 0.057439 | 7.3304e-05 | 0.055941 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.065314 | -0.0045141 | 0.065733 | -66.6969 | 0.038035 | -66.6544 | 56.2198 | 56.0327 | 56.2436 | -66.8192 | -66.7016 | 0.027831 | -66.7453 | 56.1436 | 56.2802 | 56.1735 | -66.9828 | -0.13676 | -0.080564 | -0.014473 | 0.027995 | 0.16476 | -0.26769 | -0.056771 | -0.30039 | -0.15675 | -0.019164 | -0.062826 | 0.23757 | -0.020201 | -0.12689 | 122.9022 | 122.7151 | 122.926 | 66.7205 | -123.1196 | 122.826 | 122.9626 | 122.8559 | 66.7103 | -123.2832
12.2656 | 123.1476 | -66.6962 | 56.3141 | 0.087936 | 0.0043572 | -3.1667e-05 | 0.056371 | 0.0022103 | 0.05701 | 0.088667 | -0.00043967 | -0.0010156 | 0.065314 | -0.0034461 | 0.065733 | -66.6969 | 0.033457 | -66.659 | 56.2244 | 56.0327 | 56.239 | -66.8238 | -66.7016 | 0.027831 | -66.7498 | 56.1482 | 56.2802 | 56.2238 | -66.9874 | -0.12761 | -0.089719 | -0.00074 | 0.03715 | 0.16476 | -0.28143 | -0.075083 | -0.29124 | -0.16591 | -0.005431 | -0.053672 | 0.23757 | -0.033934 | -0.090255 | 122.9205 | 122.7288 | 122.9352 | 66.7296 | -123.1379 | 122.8443 | 122.9763 | 122.92 | 66.724 | -123.3015
13.2656 | 123.1247 | -66.6733 | 56.2866 | 0.072674 | 0.0032892 | -3.1667e-05 | 0.059576 | 0.0011413 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.064245 | -0.0045141 | 0.065733 | -66.7015 | 0.038035 | -66.6544 | 56.2244 | 56.0281 | 56.239 | -66.8238 | -66.7016 | 0.023253 | -66.7498 | 56.139 | 56.2847 | 56.1826 | -66.9828 | -0.1505 | -0.062253 | -0.028206 | 0.01884 | 0.16934 | -0.25854 | -0.047617 | -0.30955 | -0.1476 | -0.028319 | -0.07656 | 0.23299 | -0.00189 | -0.104 | 122.8976 | 122.7014 | 122.9123 | 66.7113 | -123.1104 | 122.8123 | 122.958 | 122.8559 | 66.6965 | -123.2694
14.2656 | 123.1293 | -66.6824 | 56.2912 | 0.057412 | 0.0032892 | -0.0010997 | 0.057439 | 7.3304e-05 | 0.053805 | 0.073406 | 0.0016963 | 5.2373e-05 | 0.065314 | -0.0034461 | 0.066801 | -66.6923 | 0.033457 | -66.6636 | 56.2335 | 56.0418 | 56.2436 | -66.8238 | -66.7016 | 0.023253 | -66.7498 | 56.1436 | 56.2939 | 56.2284 | -66.992 | -0.14134 | -0.057674 | -0.009894 | 0.018838 | 0.16018 | -0.24938 | -0.047616 | -0.30955 | -0.1476 | -0.019164 | -0.067405 | 0.24215 | 0.00269 | -0.062788 | 122.916 | 122.7242 | 122.926 | 66.7159 | -123.115 | 122.826 | 122.9763 | 122.9108 | 66.7057 | -123.2832
15.2656 | 123.1384 | -66.7099 | 56.2546 | 0.057412 | 0.0032892 | -0.0010997 | 0.058508 | 7.3304e-05 | 0.05701 | 0.042884 | 0.00062833 | 5.2373e-05 | 0.06745 | -0.0023781 | 0.065733 | -66.7015 | 0.033457 | -66.6544 | 56.2244 | 56.0281 | 56.2436 | -66.8192 | -66.7062 | 0.023253 | -66.7498 | 56.1436 | 56.2847 | 56.233 | -66.9966 | -0.1093 | -0.03021 | 0.008415 | 0.055461 | 0.16476 | -0.2265 | -0.010995 | -0.28666 | -0.11098 | 0.003724 | -0.039939 | 0.24673 | 0.030153 | -0.021588 | 122.9343 | 122.738 | 122.9535 | 66.7434 | -123.0738 | 122.8535 | 122.9946 | 122.9429 | 66.7332 | -123.2511
16.2656 | 123.2071 | -66.6687 | 56.25 | 0.087936 | 0.0032892 | -3.1667e-05 | 0.057439 | 0.0011413 | 0.059146 | 0.088667 | 0.00062833 | -0.0010156 | 0.066382 | -0.0034461 | 0.065733 | -66.6969 | 0.028878 | -66.6636 | 56.2289 | 56.0327 | 56.2436 | -66.8192 | -66.7016 | 0.027831 | -66.7453 | 56.1436 | 56.2893 | 56.0224 | -66.9828 | -0.1505 | -0.021053 | -0.028206 | 0.005105 | 0.1556 | -0.21734 | -0.006417 | -0.31413 | -0.1064 | -0.032897 | -0.076559 | 0.23757 | 0.03931 | -0.22763 | 122.8976 | 122.7014 | 122.9123 | 66.6976 | -123.0692 | 122.8123 | 122.958 | 122.6911 | 66.6965 | -123.2328
17.2656 | 123.1384 | -66.6962 | 56.2912 | 0.026888 | 0.0022202 | 0.0010373 | 0.057439 | -0.0020637 | 0.05701 | 0.088667 | -0.00043967 | 5.2373e-05 | 0.06745 | -0.0055831 | 0.064664 | -66.7015 | 0.028878 | -66.6544 | 56.2289 | 56.0327 | 56.2436 | -66.8238 | -66.697 | 0.03241 | -66.7544 | 56.139 | 56.2847 | 56.1048 | -66.9828 | -0.12761 | -0.062252 | -0.005318 | 0.041728 | 0.16934 | -0.25854 | -0.047616 | -0.28666 | -0.15217 | -0.000852 | -0.058251 | 0.22841 | -0.006468 | -0.18641 | 122.9251 | 122.7288 | 122.9398 | 66.725 | -123.115 | 122.8352 | 122.9809 | 122.801 | 66.7286 | -123.274
18.2656 | 123.1384 | -66.6641 | 56.282 | 0.057412 | 0.0022202 | 0.0010373 | 0.057439 | 7.3304e-05 | 0.055941 | 0.058145 | 0.00062833 | -0.0010156 | 0.064245 | -0.0034461 | 0.065733 | -66.7015 | 0.028878 | -66.659 | 56.2289 | 56.0327 | 56.2436 | -66.8238 | -66.697 | 0.036989 | -66.7498 | 56.1344 | 56.2939 | 56.1185 | -66.992 | -0.15965 | -0.053096 | -0.037361 | 0.005107 | 0.16476 | -0.24938 | -0.03846 | -0.32786 | -0.1476 | -0.032895 | -0.085715 | 0.24215 | 0.011846 | -0.16352 | 122.8931 | 122.6968 | 122.9077 | 66.693 | -123.1058 | 122.7986 | 122.958 | 122.7826 | 66.7011 | -123.274
19.2656 | 123.1613 | -66.6687 | 56.3004 | 0.057412 | 0.0022202 | -0.0010997 | 0.055302 | 0.0011413 | 0.05701 | 0.058145 | 0.00062833 | 0.0011204 | 0.06745 | -0.0023781 | 0.065733 | -66.6969 | 0.038035 | -66.6544 | 56.2198 | 56.0281 | 56.239 | -66.8238 | -66.7016 | 0.023253 | -66.7498 | 56.139 | 56.2847 | 56.1185 | -66.9874 | -0.15508 | -0.080564 | -0.028206 | 0.014262 | 0.16934 | -0.27227 | -0.06135 | -0.31871 | -0.16133 | -0.032897 | -0.081138 | 0.23757 | -0.015623 | -0.18183 | 122.8885 | 122.6968 | 122.9077 | 66.7067 | -123.1241 | 122.8077 | 122.9534 | 122.7872 | 66.692 | -123.2878
20.2656 | 123.1155 | -66.7236 | 56.2775 | 0.04215 | 0.0011522 | -3.1667e-05 | 0.057439 | -0.0009947 | 0.054873 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.065314 | -0.0013091 | 0.066801 | -66.7015 | 0.042614 | -66.659 | 56.2289 | 56.0372 | 56.2436 | -66.8192 | -66.697 | 0.036989 | -66.7453 | 56.139 | 56.2893 | 56.178 | -66.9874 | -0.095565 | -0.048519 | 0.022148 | 0.064616 | 0.16018 | -0.24023 | -0.033883 | -0.26377 | -0.13844 | 0.026614 | -0.021627 | 0.24215 | 0.011844 | -0.09942 | 122.9526 | 122.7609 | 122.9672 | 66.7662 | -123.0967 | 122.8627 | 123.0129 | 122.9017 | 66.7606 | -123.2649
21.2656 | 123.1201 | -66.687 | 56.3095 | 0.057412 | 0.0022202 | 0.0021053 | 0.056371 | 0.0011413 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.066382 | -0.0013091 | 0.064664 | -66.7061 | 0.038035 | -66.659 | 56.2198 | 56.0418 | 56.2482 | -66.8146 | -66.6924 | 0.036989 | -66.7544 | 56.1436 | 56.2847 | 56.0773 | -66.9874 | -0.12761 | -0.089719 | -0.019052 | 0.027995 | 0.1556 | -0.26769 | -0.061348 | -0.3004 | -0.16591 | -0.005428 | -0.067406 | 0.23299 | -0.024778 | -0.23219 | 122.9068 | 122.7288 | 122.9352 | 66.725 | -123.1241 | 122.8306 | 122.9717 | 122.7643 | 66.724 | -123.2969
22.2656 | 123.2254 | -66.6367 | 56.2592 | 0.04215 | 0.0043572 | -3.1667e-05 | 0.056371 | 7.3304e-05 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.066382 | -0.0034461 | 0.066801 | -66.7061 | 0.033457 | -66.6636 | 56.2244 | 56.0281 | 56.2436 | -66.8192 | -66.7062 | 0.027831 | -66.7544 | 56.1344 | 56.2893 | 56.0865 | -66.9874 | -0.18254 | -0.034787 | -0.069406 | -0.026938 | 0.1556 | -0.23107 | -0.015572 | -0.35075 | -0.12471 | -0.069518 | -0.11776 | 0.23299 | 0.030155 | -0.17268 | 122.861 | 122.6647 | 122.8802 | 66.6701 | -123.0784 | 122.7711 | 122.926 | 122.7231 | 66.6645 | -123.2466
23.2656 | 123.143 | -66.6962 | 56.3187 | 0.04215 | 0.0032892 | 0.0010373 | 0.056371 | 7.3304e-05 | 0.055941 | 0.073406 | 0.00062833 | -0.0020846 | 0.065314 | -0.0034461 | 0.065733 | -66.7061 | 0.038035 | -66.6636 | 56.2289 | 56.0372 | 56.2436 | -66.8238 | -66.7016 | 0.027831 | -66.7498 | 56.1436 | 56.2847 | 56.1735 | -66.9874 | -0.12761 | -0.089718 | -0.009897 | 0.032571 | 0.16018 | -0.28143 | -0.075082 | -0.29124 | -0.17506 | -0.005431 | -0.053672 | 0.23757 | -0.033934 | -0.1452 | 122.9251 | 122.7334 | 122.9398 | 66.7342 | -123.1424 | 122.8398 | 122.9809 | 122.8696 | 66.724 | -123.3061
24.2656 | 123.1338 | -66.655 | 56.2729 | 0.072674 | 0.0022202 | 0.0010373 | 0.057439 | 7.3304e-05 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.065314 | -0.0023781 | 0.067869 | -66.7015 | 0.038035 | -66.6636 | 56.2152 | 56.0372 | 56.239 | -66.8192 | -66.697 | 0.03241 | -66.7544 | 56.139 | 56.2847 | 56.1689 | -66.992 | -0.16423 | -0.057676 | -0.046517 | -0.008628 | 0.1556 | -0.23565 | -0.033884 | -0.33702 | -0.13386 | -0.042051 | -0.09945 | 0.23757 | 0.011843 | -0.104 | 122.8702 | 122.6922 | 122.894 | 66.693 | -123.0921 | 122.794 | 122.9397 | 122.8239 | 66.6874 | -123.2649
25.2656 | 123.1155 | -66.6916 | 56.2912 | 0.057412 | 0.0032892 | -0.0010997 | 0.058508 | 0.0022103 | 0.055941 | 0.042884 | -0.00043967 | -0.0010156 | 0.066382 | -0.0023781 | 0.065733 | -66.7015 | 0.033457 | -66.6682 | 56.2198 | 56.0281 | 56.2436 | -66.8192 | -66.7016 | 0.03241 | -66.7544 | 56.1436 | 56.2939 | 56.1597 | -66.9828 | -0.12761 | -0.071409 | -0.009896 | 0.023415 | 0.15102 | -0.26312 | -0.047616 | -0.29124 | -0.1476 | -0.010009 | -0.062829 | 0.22841 | 0.00269 | -0.13147 | 122.9114 | 122.7197 | 122.9352 | 66.725 | -123.1104 | 122.8352 | 122.9855 | 122.8513 | 66.724 | -123.274
26.2656 | 123.2208 | -66.6367 | 56.2958 | 0.04215 | 0.0043572 | 0.0021053 | 0.055302 | 0.0022103 | 0.05701 | 0.073406 | 0.00062833 | 0.0021894 | 0.065314 | -0.0013091 | 0.065733 | -66.6969 | 0.028878 | -66.6544 | 56.2244 | 56.0327 | 56.239 | -66.8238 | -66.7062 | 0.027831 | -66.7636 | 56.139 | 56.2893 | 56.0498 | -66.992 | -0.18712 | -0.071408 | -0.060249 | -0.017781 | 0.16934 | -0.26312 | -0.056772 | -0.35533 | -0.15675 | -0.069518 | -0.12692 | 0.22841 | -0.006466 | -0.24593 | 122.861 | 122.6693 | 122.8757 | 66.6655 | -123.1196 | 122.7757 | 122.926 | 122.6865 | 66.6645 | -123.2878
27.2656 | 123.1293 | -66.6687 | 56.2592 | 0.072674 | 0.0032892 | 0.0010373 | 0.058508 | 0.0011413 | 0.055941 | 0.058145 | -0.00043967 | 0.0011204 | 0.065314 | -0.00024112 | 0.065733 | -66.7015 | 0.042614 | -66.6636 | 56.2106 | 56.0372 | 56.2436 | -66.8192 | -66.7016 | 0.027831 | -66.7544 | 56.1436 | 56.2802 | 56.0911 | -66.9874 | -0.1505 | -0.048522 | -0.032784 | 0.005105 | 0.1556 | -0.22192 | -0.015572 | -0.31871 | -0.11555 | -0.032897 | -0.085717 | 0.23299 | 0.020998 | -0.1681 | 122.8793 | 122.7059 | 122.9123 | 66.7113 | -123.0784 | 122.8123 | 122.9489 | 122.7598 | 66.6965 | -123.2466
28.2656 | 123.2208 | -66.6458 | 56.2729 | 0.087936 | 0.0022202 | -3.1667e-05 | 0.056371 | 7.3304e-05 | 0.058078 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.064245 | -0.0013091 | 0.066801 | -66.6969 | 0.0243 | -66.659 | 56.2244 | 56.0281 | 56.2482 | -66.8192 | -66.697 | 0.023253 | -66.7498 | 56.1482 | 56.2802 | 56.1323 | -66.9828 | -0.17338 | -0.04852 | -0.051094 | -0.013204 | 0.16018 | -0.24481 | -0.024727 | -0.33701 | -0.12471 | -0.051206 | -0.10403 | 0.23299 | 0.007265 | -0.14063 | 122.8702 | 122.6739 | 122.894 | 66.6701 | -123.0921 | 122.794 | 122.926 | 122.7781 | 66.6691 | -123.2557
29.2656 | 123.1888 | -66.6229 | 56.2683 | 0.04215 | 0.0022202 | 0.0010373 | 0.056371 | 7.3304e-05 | 0.059146 | 0.058145 | -0.00043967 | -0.0010156 | 0.065314 | -0.0023781 | 0.066801 | -66.6969 | 0.028878 | -66.659 | 56.2244 | 56.0327 | 56.2436 | -66.8238 | -66.7016 | 0.027831 | -66.7544 | 56.139 | 56.2939 | 56.2101 | -66.9828 | -0.20085 | -0.043943 | -0.073982 | -0.036092 | 0.16476 | -0.23565 | -0.024728 | -0.3599 | -0.12929 | -0.078673 | -0.13149 | 0.22841 | 0.025578 | -0.058214 | 122.8473 | 122.6556 | 122.8665 | 66.6518 | -123.0921 | 122.7619 | 122.9168 | 122.833 | 66.6508 | -123.2511
30.2656 | 123.1201 | -66.7053 | 56.2683 | 0.04215 | 0.0022202 | 0.0010373 | 0.057439 | 0.0011413 | 0.05701 | 0.058145 | 0.00062833 | -0.0010156 | 0.065314 | -0.0013091 | 0.065733 | -66.6923 | 0.033457 | -66.659 | 56.2289 | 56.0327 | 56.2436 | -66.8192 | -66.7016 | 0.027831 | -66.7498 | 56.1344 | 56.2893 | 56.1643 | -66.9828 | -0.11388 | -0.039364 | 0.012994 | 0.046305 | 0.16018 | -0.23565 | -0.024728 | -0.27751 | -0.13387 | 0.003724 | -0.044517 | 0.23299 | 0.020999 | -0.104 | 122.9343 | 122.738 | 122.9489 | 66.7388 | -123.0875 | 122.8398 | 122.9946 | 122.8696 | 66.7332 | -123.2511
31.2656 | 123.1842 | -66.6595 | 56.3004 | 0.04215 | 0.0011522 | -0.0010997 | 0.055302 | 0.0011413 | 0.054873 | 0.058145 | 0.0016963 | 5.2373e-05 | 0.065314 | -0.0013091 | 0.064664 | -66.7061 | 0.033457 | -66.6636 | 56.2198 | 56.0372 | 56.239 | -66.8238 | -66.697 | 0.027831 | -66.7498 | 56.139 | 56.2847 | 56.1826 | -66.9874 | -0.16423 | -0.080564 | -0.046518 | -0.00405 | 0.16018 | -0.26312 | -0.06135 | -0.32786 | -0.16133 | -0.037473 | -0.090293 | 0.23757 | -0.015623 | -0.11773 | 122.8793 | 122.6968 | 122.8986 | 66.693 | -123.1241 | 122.7986 | 122.9443 | 122.8422 | 66.6874 | -123.2878
32.2656 | 123.2254 | -66.6641 | 56.2546 | 0.057412 | 0.0011522 | 0.0031733 | 0.057439 | 7.3304e-05 | 0.054873 | 0.042884 | -0.00043967 | -0.0010156 | 0.064245 | -0.0023781 | 0.065733 | -66.6969 | 0.033457 | -66.6544 | 56.2244 | 56.0372 | 56.239 | -66.8146 | -66.6924 | 0.023253 | -66.759 | 56.139 | 56.2847 | 56.1597 | -66.9828 | -0.15049 | -0.03021 | -0.032783 | 0.009685 | 0.16018 | -0.21734 | -0.015574 | -0.3187 | -0.11555 | -0.028316 | -0.094872 | 0.22383 | 0.030153 | -0.094846 | 122.8885 | 122.7014 | 122.9031 | 66.6976 | -123.0692 | 122.8031 | 122.9489 | 122.8239 | 66.6874 | -123.2374
33.2656 | 123.2025 | -66.6595 | 56.2729 | 0.072674 | 8.4235e-05 | -3.1667e-05 | 0.056371 | 0.0022103 | 0.055941 | 0.073406 | 0.00062833 | 0.0011204 | 0.065314 | -0.00024112 | 0.065733 | -66.6969 | 0.033457 | -66.659 | 56.2152 | 56.0418 | 56.2482 | -66.8284 | -66.7016 | 0.018674 | -66.7544 | 56.139 | 56.2847 | 56.1872 | -66.992 | -0.16881 | -0.057676 | -0.037361 | 0.000529 | 0.16934 | -0.23107 | -0.024727 | -0.33244 | -0.13386 | -0.042052 | -0.094872 | 0.23757 | 0.011843 | -0.085684 | 122.8748 | 122.7014 | 122.9077 | 66.693 | -123.1012 | 122.7986 | 122.9443 | 122.8468 | 66.6782 | -123.2649
34.2656 | 123.1888 | -66.6367 | 56.2958 | 0.057412 | -0.00098476 | -0.0010997 | 0.057439 | 0.0011413 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.064245 | -0.0023781 | 0.066801 | -66.6923 | 0.042614 | -66.659 | 56.2289 | 56.0327 | 56.2482 | -66.8284 | -66.7016 | 0.03241 | -66.7498 | 56.1436 | 56.2802 | 56.233 | -66.9828 | -0.1917 | -0.066829 | -0.05567 | -0.022359 | 0.16934 | -0.26312 | -0.047615 | -0.34617 | -0.15217 | -0.06494 | -0.11318 | 0.23299 | -0.015623 | -0.062786 | 122.8656 | 122.6693 | 122.8848 | 66.6793 | -123.1241 | 122.7803 | 122.9168 | 122.8696 | 66.6691 | -123.2786
35.2656 | 123.2208 | -66.6321 | 56.2729 | 0.087936 | 8.4235e-05 | -3.1667e-05 | 0.056371 | 0.0011413 | 0.055941 | 0.088667 | 0.00062833 | -0.0010156 | 0.065314 | -0.0013091 | 0.065733 | -66.6969 | 0.038035 | -66.6636 | 56.2198 | 56.0327 | 56.2436 | -66.8238 | -66.7016 | 0.03241 | -66.759 | 56.139 | 56.2893 | 56.2467 | -66.992 | -0.1917 | -0.053098 | -0.064827 | -0.031516 | 0.16018 | -0.24023 | -0.029305 | -0.35991 | -0.13386 | -0.069518 | -0.12692 | 0.23299 | 0.016422 | -0.026163 | 122.8519 | 122.6647 | 122.8757 | 66.6701 | -123.0967 | 122.7711 | 122.9214 | 122.8788 | 66.6645 | -123.2649
36.2656 | 123.2574 | -66.6641 | 56.2592 | 0.087936 | 0.0032892 | -3.1667e-05 | 0.055302 | 0.0011413 | 0.055941 | 0.088667 | -0.00043967 | 5.2373e-05 | 0.06745 | -0.00024112 | 0.065733 | -66.6969 | 0.033457 | -66.6544 | 56.2289 | 56.0281 | 56.2436 | -66.8238 | -66.7016 | 0.027831 | -66.7544 | 56.139 | 56.2893 | 56.1735 | -66.9874 | -0.15965 | -0.030208 | -0.032783 | 0.009685 | 0.16934 | -0.23107 | -0.015572 | -0.32328 | -0.12013 | -0.037474 | -0.090294 | 0.23299 | 0.030155 | -0.085687 | 122.8931 | 122.6922 | 122.9077 | 66.6976 | -123.0829 | 122.8031 | 122.9534 | 122.8376 | 66.692 | -123.2466
37.2656 | 123.2346 | -66.6504 | 56.2866 | 0.072674 | 0.0011522 | -3.1667e-05 | 0.057439 | -0.0009947 | 0.058078 | 0.073406 | 0.00062833 | -0.0020846 | 0.064245 | -0.0023781 | 0.065733 | -66.7015 | 0.028878 | -66.6682 | 56.2335 | 56.0418 | 56.2344 | -66.8192 | -66.697 | 0.023253 | -66.7498 | 56.1482 | 56.2802 | 56.146 | -66.9874 | -0.16881 | -0.053096 | -0.051094 | -0.017783 | 0.15102 | -0.2448 | -0.052196 | -0.33702 | -0.13844 | -0.046628 | -0.099448 | 0.23757 | -0.006468 | -0.14062 | 122.8839 | 122.6922 | 122.8848 | 66.6793 | -123.1058 | 122.7986 | 122.9305 | 122.7964 | 66.6736 | -123.274
38.2656 | 123.2254 | -66.6458 | 56.2775 | 0.057412 | 8.4235e-05 | -3.1667e-05 | 0.057439 | -0.0009947 | 0.05701 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.066382 | -0.00024112 | 0.065733 | -66.6877 | 0.028878 | -66.6636 | 56.2244 | 56.0372 | 56.2482 | -66.8146 | -66.697 | 0.03241 | -66.7453 | 56.1436 | 56.2939 | 56.1689 | -66.9874 | -0.16881 | -0.053098 | -0.041937 | -0.017783 | 0.15102 | -0.24023 | -0.029305 | -0.34159 | -0.13386 | -0.051206 | -0.099447 | 0.24215 | 0.016423 | -0.10858 | 122.8702 | 122.6831 | 122.894 | 66.6747 | -123.0921 | 122.7894 | 122.9397 | 122.8147 | 66.6782 | -123.2649
39.2656 | 123.1934 | -66.6779 | 56.2729 | 0.057412 | 0.0011522 | 0.0021053 | 0.056371 | 7.3304e-05 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.065314 | -0.0023781 | 0.064664 | -66.7015 | 0.028878 | -66.6544 | 56.2244 | 56.0327 | 56.2436 | -66.8238 | -66.697 | 0.027831 | -66.7498 | 56.1344 | 56.2802 | 56.2147 | -66.9874 | -0.14592 | -0.04852 | -0.023629 | 0.023417 | 0.16934 | -0.24023 | -0.029305 | -0.30955 | -0.13844 | -0.019163 | -0.071983 | 0.23757 | 0.007265 | -0.058213 | 122.9022 | 122.7105 | 122.9214 | 66.7067 | -123.0967 | 122.8123 | 122.958 | 122.8925 | 66.7057 | -123.2603
40.2656 | 123.2483 | -66.6367 | 56.2775 | 0.072674 | 8.4235e-05 | 0.0010373 | 0.057439 | 0.0011413 | 0.055941 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.063177 | -0.00024112 | 0.065733 | -66.7015 | 0.038035 | -66.6544 | 56.2289 | 56.0372 | 56.2436 | -66.8192 | -66.7016 | 0.023253 | -66.7498 | 56.139 | 56.2847 | 56.2238 | -66.9828 | -0.18254 | -0.048519 | -0.064827 | -0.017781 | 0.16476 | -0.24023 | -0.033883 | -0.34617 | -0.13844 | -0.06494 | -0.11318 | 0.23299 | 0.007265 | -0.053634 | 122.8656 | 122.6739 | 122.8802 | 66.6747 | -123.0967 | 122.7757 | 122.9214 | 122.8605 | 66.6599 | -123.2603
41.2656 | 123.2117 | -66.655 | 56.2592 | 0.072674 | 0.0011522 | -3.1667e-05 | 0.056371 | 7.3304e-05 | 0.058078 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.065314 | -0.0013091 | 0.064664 | -66.6923 | 0.028878 | -66.659 | 56.2244 | 56.0281 | 56.2436 | -66.8238 | -66.697 | 0.03241 | -66.7544 | 56.139 | 56.2893 | 56.2147 | -66.9874 | -0.16881 | -0.034787 | -0.03736 | -0.004049 | 0.16476 | -0.23107 | -0.015572 | -0.33244 | -0.12013 | -0.042051 | -0.09945 | 0.23299 | 0.030155 | -0.04448 | 122.8793 | 122.683 | 122.8986 | 66.6838 | -123.0829 | 122.794 | 122.9443 | 122.8696 | 66.6874 | -123.2466
42.2656 | 123.2346 | -66.6321 | 56.2637 | 0.072674 | 0.0011522 | -0.0021677 | 0.056371 | 0.0022103 | 0.054873 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.064245 | -0.00024112 | 0.064664 | -66.6969 | 0.038035 | -66.659 | 56.2289 | 56.0372 | 56.2436 | -66.8146 | -66.7016 | 0.027831 | -66.7498 | 56.1344 | 56.2893 | 56.1964 | -66.9874 | -0.18254 | -0.034786 | -0.064827 | -0.026937 | 0.1556 | -0.22649 | -0.02015 | -0.35533 | -0.12929 | -0.069518 | -0.11776 | 0.23757 | 0.025577 | -0.067372 | 122.861 | 122.6693 | 122.8757 | 66.6701 | -123.0784 | 122.7665 | 122.9214 | 122.8284 | 66.6599 | -123.2511
43.2656 | 123.2758 | -66.6367 | 56.2637 | 0.057412 | 0.0011522 | -0.0010997 | 0.056371 | 7.3304e-05 | 0.058078 | 0.073406 | -0.00043967 | 0.0021894 | 0.065314 | -0.00024112 | 0.063596 | -66.6969 | 0.033457 | -66.659 | 56.2244 | 56.0327 | 56.2527 | -66.8192 | -66.7062 | 0.023253 | -66.7544 | 56.139 | 56.2985 | 56.1964 | -66.9874 | -0.18254 | -0.039365 | -0.060249 | -0.022359 | 0.16018 | -0.23107 | -0.010993 | -0.35075 | -0.12471 | -0.069518 | -0.11776 | 0.23299 | 0.034734 | -0.067372 | 122.861 | 122.6693 | 122.8894 | 66.6701 | -123.0829 | 122.7757 | 122.9351 | 122.833 | 66.6599 | -123.2511
44.2656 | 123.2254 | -66.6504 | 56.2592 | 0.057412 | 8.4235e-05 | -3.1667e-05 | 0.057439 | 0.0011413 | 0.055941 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.066382 | -0.0013091 | 0.065733 | -66.7061 | 0.033457 | -66.659 | 56.2289 | 56.0372 | 56.2436 | -66.8146 | -66.697 | 0.03241 | -66.7498 | 56.1482 | 56.2893 | 56.2238 | -66.992 | -0.16423 | -0.030208 | -0.055673 | -0.008626 | 0.1556 | -0.22192 | -0.015572 | -0.34159 | -0.11097 | -0.046628 | -0.099448 | 0.24215 | 0.030155 | -0.035323 | 122.8793 | 122.6876 | 122.894 | 66.6838 | -123.0738 | 122.7986 | 122.9397 | 122.8742 | 66.6828 | -123.2511
45.2656 | 123.2254 | -66.6412 | 56.282 | 0.057412 | 8.4235e-05 | 0.0010373 | 0.056371 | 0.0011413 | 0.058078 | 0.073406 | 0.0027643 | 5.2373e-05 | 0.065314 | 0.00082788 | 0.064664 | -66.6923 | 0.033457 | -66.659 | 56.2198 | 56.0372 | 56.2436 | -66.8192 | -66.6833 | 0.023253 | -66.7498 | 56.1436 | 56.2847 | 56.1323 | -66.992 | -0.17796 | -0.062253 | -0.051093 | -0.017782 | 0.16018 | -0.2448 | -0.03846 | -0.35075 | -0.13844 | -0.042048 | -0.1086 | 0.24215 | 0.002688 | -0.14978 | 122.861 | 122.6785 | 122.8848 | 66.6747 | -123.1012 | 122.7848 | 122.926 | 122.7735 | 66.6645 | -123.274
46.2656 | 123.1979 | -66.6595 | 56.2683 | 0.04215 | 8.4235e-05 | 0.0010373 | 0.057439 | 0.0022103 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.00082788 | 0.065733 | -66.7015 | 0.033457 | -66.6544 | 56.2289 | 56.0418 | 56.2482 | -66.8238 | -66.7016 | 0.027831 | -66.7498 | 56.139 | 56.2893 | 56.1872 | -66.9874 | -0.16423 | -0.039364 | -0.041939 | 0.005107 | 0.16934 | -0.22649 | -0.02015 | -0.32786 | -0.12929 | -0.042052 | -0.090293 | 0.23757 | 0.020999 | -0.081107 | 122.8885 | 122.7014 | 122.9077 | 66.693 | -123.0921 | 122.7986 | 122.9489 | 122.8468 | 66.6874 | -123.2557
47.2656 | 123.2529 | -66.6458 | 56.2683 | 0.057412 | -0.00098476 | -3.1667e-05 | 0.056371 | 7.3304e-05 | 0.058078 | 0.042884 | -0.00043967 | 0.0011204 | 0.064245 | 0.00082788 | 0.065733 | -66.7015 | 0.033457 | -66.6544 | 56.2244 | 56.0372 | 56.239 | -66.8238 | -66.6924 | 0.027831 | -66.7453 | 56.139 | 56.2939 | 56.2421 | -66.9874 | -0.17796 | -0.043943 | -0.055672 | -0.008626 | 0.16934 | -0.23107 | -0.029307 | -0.34159 | -0.12929 | -0.046627 | -0.099447 | 0.24215 | 0.025578 | -0.026164 | 122.8702 | 122.6831 | 122.8848 | 66.6793 | -123.0921 | 122.7848 | 122.9397 | 122.888 | 66.6736 | -123.2557
48.2656 | 123.1934 | -66.6458 | 56.3004 | 0.057412 | -0.00098476 | -0.0021677 | 0.057439 | 7.3304e-05 | 0.05701 | 0.088667 | 0.00062833 | 5.2373e-05 | 0.065314 | -0.00024112 | 0.064664 | -66.6923 | 0.028878 | -66.6636 | 56.2335 | 56.0372 | 56.2436 | -66.8192 | -66.6924 | 0.027831 | -66.7544 | 56.1436 | 56.2939 | 56.1735 | -66.992 | -0.17338 | -0.066829 | -0.046515 | -0.017783 | 0.1556 | -0.26312 | -0.056771 | -0.34617 | -0.15675 | -0.046627 | -0.1086 | 0.23757 | -0.006465 | -0.12689 | 122.8793 | 122.6831 | 122.8894 | 66.6747 | -123.1196 | 122.7894 | 122.9397 | 122.8193 | 66.6736 | -123.2923
49.2656 | 123.2437 | -66.6412 | 56.2592 | 0.072674 | 8.4235e-05 | -3.1667e-05 | 0.057439 | 0.0011413 | 0.058078 | 0.088667 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.00082788 | 0.065733 | -66.7015 | 0.028878 | -66.659 | 56.2244 | 56.0327 | 56.239 | -66.8146 | -66.697 | 0.027831 | -66.7544 | 56.139 | 56.2893 | 56.1048 | -66.992 | -0.17338 | -0.034787 | -0.06025 | -0.017782 | 0.1556 | -0.2265 | -0.020151 | -0.35075 | -0.12013 | -0.055784 | -0.11318 | 0.23757 | 0.030155 | -0.15437 | 122.8656 | 122.6739 | 122.8802 | 66.6701 | -123.0738 | 122.7803 | 122.9305 | 122.746 | 66.6691 | -123.2511
50.2656 | 123.2483 | -66.6275 | 56.25 | 0.04215 | -0.00098476 | -0.0010997 | 0.056371 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | -0.0010156 | 0.065314 | -0.00024112 | 0.064664 | -66.7015 | 0.033457 | -66.659 | 56.2289 | 56.0372 | 56.2436 | -66.8192 | -66.7016 | 0.023253 | -66.7453 | 56.1436 | 56.2893 | 56.1689 | -66.9874 | -0.1917 | -0.021053 | -0.073983 | -0.031515 | 0.16018 | -0.21276 | -0.006417 | -0.3599 | -0.1064 | -0.074096 | -0.11776 | 0.24215 | 0.03931 | -0.081111 | 122.8564 | 122.6647 | 122.8711 | 66.661 | -123.0692 | 122.7711 | 122.9168 | 122.7964 | 66.6508 | -123.2374
51.2656 | 123.2025 | -66.6367 | 56.2637 | 0.057412 | -0.00098476 | -0.0010997 | 0.058508 | 0.0011413 | 0.055941 | 0.058145 | -0.00043967 | -0.0010156 | 0.066382 | 0.00082788 | 0.062528 | -66.7015 | 0.028878 | -66.6682 | 56.2289 | 56.0372 | 56.2482 | -66.8284 | -66.7016 | 0.027831 | -66.7498 | 56.139 | 56.2847 | 56.2421 | -66.9966 | -0.1917 | -0.034786 | -0.064827 | -0.031516 | 0.16018 | -0.22649 | -0.015572 | -0.35991 | -0.12471 | -0.06494 | -0.11318 | 0.24673 | 0.020998 | -0.021586 | 122.8656 | 122.6739 | 122.8848 | 66.6655 | -123.0921 | 122.7757 | 122.9214 | 122.8788 | 66.6645 | -123.2603
52.2656 | 123.2483 | -66.6504 | 56.2683 | 0.057412 | 8.4235e-05 | -3.1667e-05 | 0.056371 | 7.3304e-05 | 0.05701 | 0.058145 | -0.00043967 | -0.0010156 | 0.066382 | 0.0018959 | 0.063596 | -66.6923 | 0.028878 | -66.659 | 56.2198 | 56.0372 | 56.2482 | -66.8284 | -66.7016 | 0.027831 | -66.7544 | 56.1436 | 56.2939 | 56.2376 | -66.992 | -0.17797 | -0.048521 | -0.041937 | -0.008626 | 0.16934 | -0.23107 | -0.02015 | -0.34159 | -0.12471 | -0.051207 | -0.10403 | 0.23757 | 0.025578 | -0.030743 | 122.8702 | 122.6876 | 122.8986 | 66.6793 | -123.0967 | 122.794 | 122.9443 | 122.888 | 66.6782 | -123.2603
53.2656 | 123.2208 | -66.6138 | 56.2729 | 0.072674 | -0.00098476 | -3.1667e-05 | 0.057439 | 7.3304e-05 | 0.055941 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.065314 | 0.00082788 | 0.063596 | -66.6969 | 0.042614 | -66.6636 | 56.2244 | 56.0372 | 56.2436 | -66.8146 | -66.697 | 0.023253 | -66.7544 | 56.1344 | 56.2985 | 56.2376 | -66.9966 | -0.20085 | -0.04852 | -0.083137 | -0.049826 | 0.15102 | -0.23565 | -0.029305 | -0.3828 | -0.13844 | -0.083249 | -0.14065 | 0.24215 | 0.025579 | -0.03532 | 122.8381 | 122.651 | 122.8574 | 66.6564 | -123.0875 | 122.7482 | 122.9122 | 122.8513 | 66.637 | -123.2695
54.2656 | 123.23 | -66.6367 | 56.2408 | 0.057412 | -0.0020528 | -0.0010997 | 0.055302 | -0.0009947 | 0.058078 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.064245 | -0.00024112 | 0.064664 | -66.7061 | 0.028878 | -66.659 | 56.2289 | 56.0327 | 56.2527 | -66.8192 | -66.6924 | 0.023253 | -66.759 | 56.1436 | 56.2847 | 56.1918 | -66.992 | -0.18254 | -0.011898 | -0.069406 | -0.022359 | 0.16018 | -0.20819 | 0.011895 | -0.35533 | -0.097242 | -0.055782 | -0.12234 | 0.23299 | 0.043886 | -0.049063 | 122.8656 | 122.6693 | 122.8894 | 66.6655 | -123.06 | 122.7803 | 122.9214 | 122.8284 | 66.6599 | -123.2328
55.2656 | 123.175 | -66.6458 | 56.2866 | 0.072674 | 8.4235e-05 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.055941 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.066382 | -0.00024112 | 0.064664 | -66.6832 | 0.038035 | -66.6636 | 56.2289 | 56.0372 | 56.2527 | -66.8146 | -66.697 | 0.023253 | -66.7498 | 56.1436 | 56.2893 | 56.2376 | -66.9874 | -0.16881 | -0.057674 | -0.037359 | -0.017783 | 0.15102 | -0.24938 | -0.033881 | -0.34159 | -0.14302 | -0.051206 | -0.10403 | 0.23757 | 0.002689 | -0.049053 | 122.8748 | 122.6831 | 122.8986 | 66.6838 | -123.1012 | 122.7894 | 122.9351 | 122.8834 | 66.6691 | -123.274
56.2656 | 123.2483 | -66.6412 | 56.25 | 0.072674 | 8.4235e-05 | -0.0010997 | 0.055302 | 7.3304e-05 | 0.055941 | 0.088667 | 0.0016963 | -0.0010156 | 0.065314 | -0.00024112 | 0.063596 | -66.6969 | 0.038035 | -66.659 | 56.2289 | 56.0372 | 56.2527 | -66.8192 | -66.697 | 0.027831 | -66.759 | 56.1436 | 56.2847 | 56.1918 | -66.992 | -0.17796 | -0.021053 | -0.055672 | -0.017782 | 0.16018 | -0.21276 | 0.00274 | -0.35075 | -0.1064 | -0.055784 | -0.11776 | 0.23299 | 0.034731 | -0.058218 | 122.8702 | 122.6785 | 122.894 | 66.6793 | -123.0692 | 122.7848 | 122.926 | 122.833 | 66.6691 | -123.242
57.2656 | 123.2574 | -66.6458 | 56.2454 | 0.04215 | 8.4235e-05 | -3.1667e-05 | 0.057439 | 7.3304e-05 | 0.05701 | 0.042884 | 0.00062833 | 0.0011204 | 0.066382 | 0.00082788 | 0.065733 | -66.7061 | 0.028878 | -66.659 | 56.2335 | 56.0372 | 56.2436 | -66.8192 | -66.697 | 0.023253 | -66.759 | 56.1344 | 56.2985 | 56.1323 | -66.992 | -0.17338 | -0.011897 | -0.060251 | -0.013204 | 0.16018 | -0.20818 | -0.001839 | -0.34617 | -0.11098 | -0.051206 | -0.11318 | 0.23299 | 0.053045 | -0.11316 | 122.8793 | 122.6831 | 122.8894 | 66.6747 | -123.0646 | 122.7803 | 122.9443 | 122.7781 | 66.6691 | -123.2374
58.2656 | 123.2254 | -66.6458 | 56.2912 | 0.04215 | -0.00098476 | -0.0010997 | 0.056371 | 0.0022103 | 0.05701 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.065314 | -0.00024112 | 0.064664 | -66.6969 | 0.028878 | -66.6636 | 56.2289 | 56.0372 | 56.2436 | -66.8146 | -66.7016 | 0.027831 | -66.7498 | 56.1299 | 56.2847 | 56.1735 | -66.992 | -0.16881 | -0.062252 | -0.051094 | -0.017783 | 0.15102 | -0.25396 | -0.047616 | -0.34617 | -0.16133 | -0.055785 | -0.10403 | 0.24215 | -0.006468 | -0.11773 | 122.8748 | 122.6831 | 122.8894 | 66.6747 | -123.1058 | 122.7757 | 122.9305 | 122.8193 | 66.6736 | -123.2832
59.2656 | 123.2346 | -66.6321 | 56.2454 | 0.057412 | -0.0031218 | 0.0010373 | 0.056371 | 7.3304e-05 | 0.05701 | 0.058145 | -0.00043967 | -0.0010156 | 0.065314 | -0.0013091 | 0.064664 | -66.6969 | 0.033457 | -66.659 | 56.2198 | 56.0372 | 56.2482 | -66.8284 | -66.697 | 0.018674 | -66.7453 | 56.1482 | 56.2985 | 56.2055 | -66.9966 | -0.19628 | -0.025632 | -0.064827 | -0.026937 | 0.16934 | -0.20818 | 0.002739 | -0.36449 | -0.09724 | -0.064939 | -0.11318 | 0.25131 | 0.053045 | -0.039904 | 122.8519 | 122.6693 | 122.8802 | 66.6655 | -123.0738 | 122.7803 | 122.9305 | 122.8376 | 66.6508 | -123.242
60.2656 | 123.2483 | -66.6412 | 56.2683 | 0.057412 | -0.00098476 | -0.0010997 | 0.057439 | -0.0009947 | 0.05701 | 0.073406 | -0.00043967 | -0.0010156 | 0.066382 | 0.0018959 | 0.064664 | -66.7015 | 0.033457 | -66.6636 | 56.2198 | 56.0281 | 56.2482 | -66.8146 | -66.7016 | 0.023253 | -66.7453 | 56.139 | 56.2939 | 56.1964 | -66.992 | -0.17338 | -0.048521 | -0.06025 | -0.022361 | 0.15102 | -0.24023 | -0.02015 | -0.35075 | -0.12929 | -0.060363 | -0.10403 | 0.24673 | 0.025578 | -0.07195 | 122.861 | 122.6693 | 122.8894 | 66.6747 | -123.0829 | 122.7803 | 122.9351 | 122.8376 | 66.6645 | -123.2603
61.2656 | 123.262 | -66.6275 | 56.2546 | 0.04215 | -0.00098476 | 0.0010373 | 0.056371 | 7.3304e-05 | 0.05701 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.065314 | 0.0018959 | 0.063596 | -66.6969 | 0.033457 | -66.659 | 56.2289 | 56.0327 | 56.2527 | -66.8192 | -66.6924 | 0.027831 | -66.759 | 56.139 | 56.2939 | 56.1826 | -66.992 | -0.1917 | -0.025631 | -0.069405 | -0.031515 | 0.16018 | -0.22192 | -0.001838 | -0.36448 | -0.11555 | -0.064938 | -0.13149 | 0.23299 | 0.039311 | -0.071953 | 122.8564 | 122.6602 | 122.8802 | 66.661 | -123.0738 | 122.7665 | 122.9214 | 122.8101 | 66.6553 | -123.2466
62.2656 | 123.2574 | -66.6458 | 56.2454 | 0.057412 | 8.4235e-05 | -3.1667e-05 | 0.055302 | 7.3304e-05 | 0.05701 | 0.088667 | 0.00062833 | 0.0011204 | 0.06745 | 0.00082788 | 0.064664 | -66.7015 | 0.033457 | -66.659 | 56.2289 | 56.0327 | 56.2482 | -66.8192 | -66.697 | 0.027831 | -66.759 | 56.1436 | 56.2847 | 56.233 | -66.992 | -0.17338 | -0.016475 | -0.055672 | -0.013204 | 0.16018 | -0.21276 | 0.002739 | -0.34617 | -0.10182 | -0.051206 | -0.11318 | 0.23299 | 0.039309 | -0.012432 | 122.8748 | 122.6785 | 122.894 | 66.6793 | -123.0646 | 122.7894 | 122.9305 | 122.8788 | 66.6736 | -123.2374
63.2656 | 123.2483 | -66.6504 | 56.2729 | 0.072674 | -0.00098476 | -0.0010997 | 0.056371 | -0.0009947 | 0.05701 | 0.073406 | -0.0015087 | 0.0011204 | 0.064245 | 0.00082788 | 0.063596 | -66.7061 | 0.028878 | -66.6636 | 56.2289 | 56.0372 | 56.2527 | -66.8192 | -66.7062 | 0.03241 | -66.7498 | 56.1436 | 56.2893 | 56.2147 | -66.9874 | -0.16881 | -0.043941 | -0.055673 | -0.013205 | 0.1556 | -0.23565 | -0.020148 | -0.33702 | -0.12929 | -0.055785 | -0.099448 | 0.23757 | 0.016422 | -0.058213 | 122.8793 | 122.6876 | 122.9031 | 66.6793 | -123.0921 | 122.794 | 122.9397 | 122.8651 | 66.6828 | -123.2603
64.2656 | 123.262 | -66.6687 | 56.25 | 0.087936 | -0.00098476 | -0.0010997 | 0.057439 | -0.0031317 | 0.058078 | 0.042884 | -0.00043967 | -0.0010156 | 0.062109 | 0.0018959 | 0.064664 | -66.6969 | 0.033457 | -66.6636 | 56.2289 | 56.0372 | 56.2527 | -66.8192 | -66.7016 | 0.027831 | -66.7544 | 56.1344 | 56.2847 | 56.2238 | -66.9874 | -0.1505 | -0.021053 | -0.028206 | 0.005105 | 0.1556 | -0.21276 | 0.00274 | -0.31871 | -0.11555 | -0.032897 | -0.085717 | 0.23299 | 0.034731 | -0.026168 | 122.8976 | 122.7059 | 122.9214 | 66.7022 | -123.0692 | 122.8031 | 122.9534 | 122.8925 | 66.6965 | -123.2374
65.2656 | 123.2483 | -66.6412 | 56.2775 | 0.057412 | -0.00098476 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.058078 | 0.058145 | -0.00043967 | 0.0011204 | 0.065314 | 0.0029639 | 0.064664 | -66.6969 | 0.028878 | -66.6544 | 56.2289 | 56.0418 | 56.2527 | -66.8192 | -66.7016 | 0.03241 | -66.7544 | 56.1436 | 56.2893 | 56.1826 | -66.9966 | -0.17796 | -0.048519 | -0.055672 | -0.013204 | 0.16476 | -0.23565 | -0.024726 | -0.35533 | -0.13386 | -0.060363 | -0.11318 | 0.24215 | 0.011844 | -0.094841 | 122.8702 | 122.6831 | 122.894 | 66.6701 | -123.0967 | 122.7848 | 122.9305 | 122.8239 | 66.6736 | -123.274
66.2656 | 123.2483 | -66.6412 | 56.2683 | 0.04215 | 8.4235e-05 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.05701 | 0.058145 | 0.00062833 | 0.0021894 | 0.065314 | 0.00082788 | 0.064664 | -66.6969 | 0.033457 | -66.6544 | 56.2244 | 56.0418 | 56.2482 | -66.8192 | -66.697 | 0.03241 | -66.759 | 56.1482 | 56.2985 | 56.1597 | -66.9966 | -0.17796 | -0.043943 | -0.055672 | -0.013204 | 0.16476 | -0.22649 | -0.02015 | -0.35533 | -0.12013 | -0.055784 | -0.11776 | 0.23757 | 0.030156 | -0.10858 | 122.8656 | 122.6831 | 122.8894 | 66.6747 | -123.0875 | 122.7894 | 122.9397 | 122.801 | 66.6736 | -123.2649
67.2656 | 123.2162 | -66.6504 | 56.2637 | 0.057412 | 8.4235e-05 | 0.0010373 | 0.057439 | 0.0022103 | 0.058078 | 0.088667 | 0.0016963 | 5.2373e-05 | 0.065314 | 0.00082788 | 0.065733 | -66.6969 | 0.028878 | -66.6544 | 56.2335 | 56.0418 | 56.2436 | -66.8146 | -66.6924 | 0.027831 | -66.7544 | 56.1482 | 56.2893 | 56.178 | -66.992 | -0.16423 | -0.030208 | -0.046516 | -0.004048 | 0.16018 | -0.22192 | -0.02015 | -0.34159 | -0.11555 | -0.042049 | -0.10403 | 0.23757 | 0.025577 | -0.085687 | 122.8839 | 122.6922 | 122.894 | 66.6793 | -123.0784 | 122.7986 | 122.9397 | 122.8284 | 66.6782 | -123.2557
68.2656 | 123.23 | -66.655 | 56.2637 | 0.04215 | -0.00098476 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.065314 | 0.0029639 | 0.064664 | -66.6923 | 0.0243 | -66.659 | 56.2244 | 56.0372 | 56.2573 | -66.8238 | -66.697 | 0.023253 | -66.7544 | 56.1436 | 56.2939 | 56.178 | -66.9966 | -0.16881 | -0.039365 | -0.03736 | -0.004049 | 0.16476 | -0.22649 | -0.006415 | -0.3416 | -0.12013 | -0.042051 | -0.09945 | 0.24215 | 0.030156 | -0.085687 | 122.8793 | 122.6922 | 122.9123 | 66.6793 | -123.0875 | 122.7986 | 122.9489 | 122.833 | 66.6782 | -123.2603
69.2656 | 123.2391 | -66.6458 | 56.25 | 0.04215 | -0.0020528 | -0.0010997 | 0.056371 | 7.3304e-05 | 0.054873 | 0.058145 | -0.00043967 | -0.0010156 | 0.066382 | 0.0018959 | 0.064664 | -66.6969 | 0.033457 | -66.6544 | 56.2289 | 56.0372 | 56.2482 | -66.8238 | -66.6879 | 0.027831 | -66.7636 | 56.139 | 56.2847 | 56.2513 | -66.992 | -0.17796 | -0.021053 | -0.051094 | -0.008626 | 0.16934 | -0.21276 | -0.001839 | -0.34617 | -0.11098 | -0.042048 | -0.11776 | 0.22841 | 0.034731 | 0.001304 | 122.8748 | 122.6831 | 122.894 | 66.6793 | -123.0738 | 122.7848 | 122.9305 | 122.8971 | 66.6736 | -123.242
70.2656 | 123.1979 | -66.6641 | 56.2592 | 0.057412 | -0.00098476 | 0.0010373 | 0.056371 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | 0.0011204 | 0.06745 | 0.00082788 | 0.064664 | -66.6969 | 0.028878 | -66.659 | 56.2289 | 56.0327 | 56.2482 | -66.8192 | -66.6924 | 0.027831 | -66.7544 | 56.139 | 56.2893 | 56.2376 | -66.9966 | -0.15507 | -0.030208 | -0.032783 | 0.005107 | 0.16018 | -0.2265 | -0.010994 | -0.33244 | -0.12013 | -0.028316 | -0.090294 | 0.24215 | 0.030155 | -0.021587 | 122.8931 | 122.6968 | 122.9123 | 66.693 | -123.0784 | 122.8031 | 122.9534 | 122.9017 | 66.692 | -123.2557
71.2656 | 123.2666 | -66.6367 | 56.2592 | 0.04215 | -0.00098476 | -3.1667e-05 | 0.057439 | -0.0020637 | 0.055941 | 0.058145 | -0.00043967 | 0.0011204 | 0.065314 | 0.0018959 | 0.064664 | -66.7015 | 0.028878 | -66.6544 | 56.2289 | 56.0418 | 56.2482 | -66.8146 | -66.6924 | 0.027831 | -66.7544 | 56.1436 | 56.2802 | 56.2193 | -66.9966 | -0.17796 | -0.030208 | -0.064827 | -0.017781 | 0.16018 | -0.21734 | -0.010994 | -0.35991 | -0.11555 | -0.055782 | -0.11776 | 0.24215 | 0.020998 | -0.039901 | 122.8656 | 122.6785 | 122.8848 | 66.6655 | -123.0738 | 122.7803 | 122.9168 | 122.8559 | 66.6645 | -123.2557
72.2656 | 123.2071 | -66.6641 | 56.2317 | 0.057412 | -0.00098476 | -0.0010997 | 0.055302 | 7.3304e-05 | 0.058078 | 0.073406 | -0.00043967 | 0.0011204 | 0.063177 | 0.0018959 | 0.064664 | -66.6923 | 0.033457 | -66.6544 | 56.2289 | 56.0372 | 56.2482 | -66.8238 | -66.6924 | 0.018674 | -66.759 | 56.1436 | 56.2939 | 56.2284 | -66.992 | -0.15965 | -0.002742 | -0.028204 | 0.009685 | 0.16934 | -0.19445 | 0.016472 | -0.32786 | -0.088086 | -0.028316 | -0.094872 | 0.23299 | 0.0622 | -0.003278 | 122.8931 | 122.7014 | 122.9123 | 66.6976 | -123.0555 | 122.8077 | 122.958 | 122.8925 | 66.6828 | -123.2237
73.2656 | 123.2346 | -66.655 | 56.2775 | 0.04215 | -0.0020528 | -0.0010997 | 0.055302 | -0.0020637 | 0.058078 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.065314 | 0.0029639 | 0.065733 | -66.6969 | 0.038035 | -66.659 | 56.2335 | 56.0372 | 56.2527 | -66.8238 | -66.6879 | 0.027831 | -66.7544 | 56.139 | 56.2893 | 56.2101 | -67.0011 | -0.16881 | -0.043941 | -0.041939 | -0.004049 | 0.16476 | -0.24023 | -0.024726 | -0.34618 | -0.13844 | -0.032893 | -0.09945 | 0.24672 | 0.011844 | -0.067369 | 122.8885 | 122.6922 | 122.9077 | 66.693 | -123.1012 | 122.794 | 122.9443 | 122.8651 | 66.6828 | -123.2786
74.2656 | 123.1979 | -66.655 | 56.2729 | 0.04215 | -0.0031218 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.065314 | 0.00082788 | 0.063596 | -66.7015 | 0.033457 | -66.659 | 56.2289 | 56.0372 | 56.2482 | -66.8284 | -66.697 | 0.03241 | -66.7498 | 56.1482 | 56.2939 | 56.2421 | -66.9966 | -0.17339 | -0.043941 | -0.046517 | -0.004049 | 0.16934 | -0.23565 | -0.024727 | -0.3416 | -0.12471 | -0.042051 | -0.094871 | 0.24673 | 0.021001 | -0.030741 | 122.8839 | 122.6922 | 122.9031 | 66.6884 | -123.1012 | 122.8031 | 122.9489 | 122.8971 | 66.6874 | -123.2695
75.2656 | 123.175 | -66.7099 | 56.25 | 0.057412 | -0.00098476 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.054873 | 0.073406 | -0.00043967 | 0.0011204 | 0.066382 | 0.0018959 | 0.064664 | -66.7015 | 0.033457 | -66.6544 | 56.2244 | 56.0418 | 56.2436 | -66.8192 | -66.697 | 0.027831 | -66.7498 | 56.1299 | 56.2893 | 56.1506 | -66.9874 | -0.1093 | -0.025632 | 0.008415 | 0.055461 | 0.16476 | -0.20818 | -0.006417 | -0.27751 | -0.12013 | 0.012881 | -0.039939 | 0.23757 | 0.03931 | -0.099425 | 122.9343 | 122.7517 | 122.9535 | 66.7434 | -123.0692 | 122.8398 | 122.9992 | 122.8605 | 66.7377 | -123.2374
76.2656 | 123.2025 | -66.6824 | 56.2729 | 0.04215 | -0.0031218 | 0.0010373 | 0.056371 | -0.0020637 | 0.05701 | 0.058145 | -0.00043967 | 0.0011204 | 0.063177 | 0.00082788 | 0.065733 | -66.7015 | 0.033457 | -66.6544 | 56.2244 | 56.0372 | 56.2482 | -66.8146 | -66.6924 | 0.027831 | -66.7544 | 56.1344 | 56.2847 | 56.1689 | -66.9966 | -0.13218 | -0.04852 | -0.019051 | 0.027995 | 0.16018 | -0.23565 | -0.024727 | -0.31413 | -0.13844 | -0.010006 | -0.071984 | 0.24215 | 0.011843 | -0.104 | 122.9068 | 122.7197 | 122.9306 | 66.7159 | -123.0875 | 122.8169 | 122.9672 | 122.8513 | 66.7103 | -123.2695
77.2656 | 123.1934 | -66.6733 | 56.25 | 0.072674 | -0.0031218 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.066382 | 0.0029639 | 0.064664 | -66.7015 | 0.028878 | -66.659 | 56.2289 | 56.0327 | 56.2527 | -66.8192 | -66.697 | 0.027831 | -66.7544 | 56.139 | 56.2847 | 56.1643 | -66.9966 | -0.14592 | -0.021053 | -0.028206 | 0.014262 | 0.16018 | -0.21734 | 0.00274 | -0.32329 | -0.11098 | -0.02374 | -0.081139 | 0.24215 | 0.034731 | -0.085689 | 122.9022 | 122.7059 | 122.926 | 66.7022 | -123.0692 | 122.8123 | 122.958 | 122.8376 | 66.7011 | -123.2466
78.2656 | 123.23 | -66.6687 | 56.2408 | 0.057412 | -0.0041898 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.05701 | 0.058145 | 0.00062833 | 0.0011204 | 0.064245 | 0.0029639 | 0.064664 | -66.6969 | 0.028878 | -66.6544 | 56.2289 | 56.0464 | 56.2436 | -66.8146 | -66.697 | 0.023253 | -66.7498 | 56.1436 | 56.2985 | 56.2467 | -66.992 | -0.14592 | -0.011898 | -0.028206 | 0.014262 | 0.16018 | -0.19445 | 0.002738 | -0.32328 | -0.097242 | -0.028318 | -0.081138 | 0.24215 | 0.057622 | 0.00588 | 122.8976 | 122.7151 | 122.9123 | 66.6976 | -123.0555 | 122.8123 | 122.9672 | 122.9154 | 66.692 | -123.2328
79.2656 | 123.2391 | -66.6275 | 56.2775 | 0.057412 | -0.0031218 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.05701 | 0.073406 | 0.0016963 | 5.2373e-05 | 0.065314 | 0.0018959 | 0.063596 | -66.6969 | 0.033457 | -66.6544 | 56.2289 | 56.0327 | 56.2482 | -66.8238 | -66.7016 | 0.023253 | -66.759 | 56.1436 | 56.2939 | 56.2376 | -66.9874 | -0.19627 | -0.048519 | -0.069405 | -0.026937 | 0.16934 | -0.24481 | -0.029305 | -0.3599 | -0.13386 | -0.074096 | -0.13149 | 0.22841 | 0.016423 | -0.039898 | 122.8564 | 122.6602 | 122.8757 | 66.661 | -123.1012 | 122.7711 | 122.9214 | 122.8651 | 66.6508 | -123.2649
80.2656 | 123.2117 | -66.6595 | 56.2042 | 0.026888 | -0.0031218 | -3.1667e-05 | 0.055302 | 7.3304e-05 | 0.054873 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.0029639 | 0.066801 | -66.7015 | 0.038035 | -66.6636 | 56.2244 | 56.0372 | 56.2527 | -66.8146 | -66.7062 | 0.023253 | -66.759 | 56.1436 | 56.2893 | 56.1506 | -66.9966 | -0.15507 | 0.020144 | -0.041939 | -0.00405 | 0.15102 | -0.16699 | 0.048516 | -0.33702 | -0.060621 | -0.04663 | -0.09945 | 0.23757 | 0.085086 | -0.053649 | 122.8839 | 122.6968 | 122.9123 | 66.6976 | -123.0188 | 122.8031 | 122.9489 | 122.8101 | 66.6828 | -123.2008
81.2656 | 123.2162 | -66.6733 | 56.2363 | 0.057412 | -0.0031218 | -0.0010997 | 0.056371 | 7.3304e-05 | 0.05701 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.0029639 | 0.065733 | -66.7061 | 0.028878 | -66.6544 | 56.2289 | 56.0418 | 56.2482 | -66.8146 | -66.7016 | 0.03241 | -66.7453 | 56.139 | 56.2939 | 56.2559 | -66.992 | -0.14134 | -0.00732 | -0.032785 | 0.01884 | 0.16018 | -0.19445 | 0.011894 | -0.31871 | -0.097242 | -0.028319 | -0.071981 | 0.24673 | 0.057622 | 0.019616 | 122.9022 | 122.7151 | 122.9214 | 66.7022 | -123.0509 | 122.8123 | 122.9672 | 122.9292 | 66.7057 | -123.2283
82.2656 | 123.2437 | -66.6412 | 56.2317 | 0.04215 | -0.00098476 | -3.1667e-05 | 0.056371 | 0.0011413 | 0.055941 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.064245 | 0.0029639 | 0.063596 | -66.6969 | 0.028878 | -66.659 | 56.2335 | 56.0372 | 56.2482 | -66.8192 | -66.7016 | 0.027831 | -66.7498 | 56.139 | 56.2893 | 56.178 | -66.992 | -0.17796 | 0.001836 | -0.055672 | -0.017782 | 0.16018 | -0.19445 | 0.016472 | -0.35075 | -0.092664 | -0.060363 | -0.1086 | 0.24215 | 0.057621 | -0.053643 | 122.8748 | 122.6785 | 122.8894 | 66.6701 | -123.0509 | 122.7803 | 122.9305 | 122.8193 | 66.6691 | -123.2237
83.2656 | 123.1934 | -66.6321 | 56.2454 | 0.057412 | -0.0020528 | -3.1667e-05 | 0.055302 | -0.0020637 | 0.058078 | 0.088667 | -0.00043967 | 0.0011204 | 0.063177 | 0.0040329 | 0.062528 | -66.6969 | 0.038035 | -66.659 | 56.2289 | 56.0418 | 56.2527 | -66.8238 | -66.697 | 0.027831 | -66.7498 | 56.1436 | 56.2847 | 56.2421 | -66.992 | -0.1917 | -0.016475 | -0.064827 | -0.026937 | 0.16476 | -0.20361 | 0.007318 | -0.35991 | -0.10182 | -0.064939 | -0.11776 | 0.24215 | 0.039309 | -0.003275 | 122.861 | 122.6739 | 122.8848 | 66.6701 | -123.0692 | 122.7757 | 122.9168 | 122.8742 | 66.6599 | -123.2374
84.2656 | 123.2391 | -66.6824 | 56.2408 | 0.04215 | -0.0031218 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.055941 | 0.073406 | 0.00062833 | -0.0010156 | 0.064245 | 0.0029639 | 0.064664 | -66.6923 | 0.033457 | -66.6499 | 56.2335 | 56.0327 | 56.2482 | -66.8238 | -66.6924 | 0.023253 | -66.7544 | 56.1436 | 56.2939 | 56.1964 | -66.9966 | -0.14134 | -0.00732 | -0.009894 | 0.032573 | 0.17392 | -0.20819 | 0.007316 | -0.31413 | -0.097242 | -0.010006 | -0.071984 | 0.24215 | 0.053044 | -0.044484 | 122.916 | 122.7151 | 122.9306 | 66.7159 | -123.0646 | 122.826 | 122.9763 | 122.8788 | 66.7057 | -123.2374
85.2656 | 123.262 | -66.6641 | 56.2408 | 0.026888 | -0.0020528 | 0.0010373 | 0.053166 | -0.0009947 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.065314 | 0.0018959 | 0.064664 | -66.7061 | 0.0243 | -66.6544 | 56.2289 | 56.0464 | 56.2527 | -66.8238 | -66.697 | 0.027831 | -66.7544 | 56.1482 | 56.2847 | 56.1323 | -66.992 | -0.15965 | -0.011898 | -0.04194 | 0.009685 | 0.16934 | -0.19445 | 0.011895 | -0.32786 | -0.092663 | -0.032895 | -0.090294 | 0.23757 | 0.043886 | -0.10858 | 122.8931 | 122.7105 | 122.9169 | 66.6884 | -123.0646 | 122.8123 | 122.9489 | 122.7964 | 66.692 | -123.2328
86.2656 | 123.2208 | -66.6321 | 56.2454 | 0.057412 | -0.0041898 | -0.0010997 | 0.055302 | 7.3304e-05 | 0.058078 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.065314 | 0.0040329 | 0.065733 | -66.6969 | 0.038035 | -66.6544 | 56.2289 | 56.0372 | 56.2482 | -66.8192 | -66.697 | 0.03241 | -66.7544 | 56.1436 | 56.2939 | 56.2376 | -66.9966 | -0.18712 | -0.016475 | -0.064827 | -0.022359 | 0.16476 | -0.20818 | 0.002739 | -0.36449 | -0.10182 | -0.064939 | -0.12234 | 0.24215 | 0.048467 | -0.007854 | 122.861 | 122.6693 | 122.8802 | 66.6701 | -123.0646 | 122.7757 | 122.926 | 122.8696 | 66.6645 | -123.242
87.2656 | 123.2483 | -66.6504 | 56.218 | 0.057412 | -0.0020528 | -3.1667e-05 | 0.056371 | -0.0020637 | 0.05701 | 0.088667 | -0.0015087 | -0.0010156 | 0.063177 | 0.0040329 | 0.065733 | -66.6923 | 0.033457 | -66.659 | 56.2335 | 56.0372 | 56.2436 | -66.8192 | -66.7016 | 0.027831 | -66.7453 | 56.139 | 56.2985 | 56.1826 | -66.992 | -0.16881 | 0.015568 | -0.041937 | -0.008626 | 0.16018 | -0.18072 | 0.025626 | -0.34159 | -0.078932 | -0.051207 | -0.094869 | 0.24673 | 0.08051 | -0.035332 | 122.8839 | 122.6876 | 122.894 | 66.6838 | -123.0372 | 122.7894 | 122.9489 | 122.833 | 66.6782 | -123.2099
88.2656 | 123.2758 | -66.6641 | 56.2271 | 0.057412 | -0.0041898 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.05701 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.064245 | 0.0040329 | 0.064664 | -66.6969 | 0.033457 | -66.6544 | 56.2289 | 56.0327 | 56.2573 | -66.8284 | -66.7016 | 0.023253 | -66.7498 | 56.139 | 56.2939 | 56.1689 | -66.992 | -0.16423 | 0.001835 | -0.032783 | 0.009685 | 0.17392 | -0.19445 | 0.030206 | -0.32786 | -0.088087 | -0.037474 | -0.085715 | 0.24215 | 0.066777 | -0.058223 | 122.8931 | 122.6968 | 122.9214 | 66.6976 | -123.0555 | 122.8031 | 122.958 | 122.833 | 66.6874 | -123.2191
89.2656 | 123.23 | -66.6595 | 56.25 | 0.072674 | -0.0041898 | 0.0010373 | 0.054234 | -0.0020637 | 0.055941 | 0.058145 | 0.00062833 | -0.0010156 | 0.064245 | 0.0040329 | 0.064664 | -66.6877 | 0.033457 | -66.6544 | 56.2335 | 56.0418 | 56.2573 | -66.8238 | -66.7016 | 0.027831 | -66.7498 | 56.139 | 56.2939 | 56.2238 | -66.9966 | -0.16423 | -0.016475 | -0.028204 | 0.005107 | 0.16934 | -0.20818 | 0.007318 | -0.33702 | -0.11098 | -0.042052 | -0.090293 | 0.24673 | 0.043889 | -0.026168 | 122.8931 | 122.7014 | 122.9169 | 66.693 | -123.0738 | 122.7986 | 122.9534 | 122.8834 | 66.6874 | -123.2466
90.2656 | 123.2666 | -66.6595 | 56.2454 | 0.026888 | -0.0041898 | -0.0010997 | 0.056371 | -0.0009947 | 0.055941 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.064245 | 0.0029639 | 0.065733 | -66.6969 | 0.038035 | -66.6636 | 56.2289 | 56.0327 | 56.2573 | -66.8238 | -66.7016 | 0.027831 | -66.7544 | 56.1436 | 56.2939 | 56.1872 | -66.9966 | -0.16423 | -0.016475 | -0.037361 | -0.00405 | 0.16018 | -0.21276 | 0.011896 | -0.33702 | -0.10182 | -0.042052 | -0.094872 | 0.24215 | 0.048467 | -0.058218 | 122.8885 | 122.6922 | 122.9169 | 66.6976 | -123.0692 | 122.8031 | 122.9534 | 122.8468 | 66.6874 | -123.242
91.2656 | 123.1476 | -66.6962 | 56.2546 | 0.04215 | -0.0041898 | -0.0010997 | 0.056371 | -0.0020637 | 0.055941 | 0.042884 | 0.0016963 | -0.0010156 | 0.065314 | 0.0029639 | 0.064664 | -66.6969 | 0.038035 | -66.6544 | 56.2289 | 56.0418 | 56.2527 | -66.8238 | -66.7016 | 0.027831 | -66.7498 | 56.1344 | 56.2939 | 56.2055 | -67.0011 | -0.12761 | -0.025631 | -0.00074 | 0.041728 | 0.16934 | -0.21276 | -0.001838 | -0.30498 | -0.12013 | -0.005431 | -0.053672 | 0.2513 | 0.039311 | -0.04906 | 122.9251 | 122.738 | 122.9489 | 66.7342 | -123.0784 | 122.8306 | 122.9901 | 122.9017 | 66.724 | -123.2557
92.2656 | 123.2758 | -66.6687 | 56.2088 | 0.057412 | -0.0052578 | -3.1667e-05 | 0.055302 | 0.0011413 | 0.055941 | 0.027623 | 0.00062833 | 5.2373e-05 | 0.065314 | 0.0040329 | 0.064664 | -66.6969 | 0.033457 | -66.6499 | 56.2244 | 56.0418 | 56.2573 | -66.8192 | -66.697 | 0.023253 | -66.7453 | 56.1436 | 56.2939 | 56.233 | -66.9874 | -0.1505 | 0.015567 | -0.028206 | 0.01884 | 0.16934 | -0.16699 | 0.048517 | -0.31871 | -0.065198 | -0.028318 | -0.076559 | 0.24215 | 0.085088 | 0.024189 | 122.8931 | 122.7105 | 122.926 | 66.7022 | -123.028 | 122.8123 | 122.9626 | 122.9017 | 66.692 | -123.1962
93.2656 | 123.1796 | -66.7007 | 56.2271 | 0.04215 | -0.0031218 | -0.0021677 | 0.056371 | -0.0020637 | 0.055941 | 0.088667 | -0.00043967 | 5.2373e-05 | 0.065314 | 0.0040329 | 0.065733 | -66.6923 | 0.038035 | -66.659 | 56.2244 | 56.0372 | 56.2527 | -66.8284 | -66.6924 | 0.027831 | -66.7544 | 56.1436 | 56.2939 | 56.1689 | -66.992 | -0.12761 | -0.002744 | 0.008417 | 0.041728 | 0.16934 | -0.18987 | 0.025628 | -0.29124 | -0.083509 | 0.008305 | -0.053673 | 0.23757 | 0.066777 | -0.058223 | 122.9251 | 122.738 | 122.9535 | 66.7388 | -123.0555 | 122.8443 | 122.9946 | 122.8696 | 66.7286 | -123.2191
94.2656 | 123.175 | -66.6641 | 56.2592 | 0.072674 | -0.0041898 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.065314 | 0.0029639 | 0.064664 | -66.6923 | 0.033457 | -66.6499 | 56.2244 | 56.0418 | 56.2482 | -66.8146 | -66.7016 | 0.027831 | -66.7544 | 56.1436 | 56.2985 | 56.1002 | -66.9966 | -0.15049 | -0.034787 | -0.028204 | 0.014263 | 0.16476 | -0.21734 | -0.010994 | -0.33244 | -0.11555 | -0.037474 | -0.090294 | 0.24215 | 0.039312 | -0.15895 | 122.8885 | 122.7059 | 122.9123 | 66.6976 | -123.0738 | 122.8077 | 122.9626 | 122.7643 | 66.692 | -123.2557
95.2656 | 123.1247 | -66.6779 | 56.25 | 0.04215 | -0.0041898 | -3.1667e-05 | 0.056371 | 0.0022103 | 0.05701 | 0.042884 | 0.00062833 | 0.0011204 | 0.065314 | 0.0040329 | 0.065733 | -66.6969 | 0.038035 | -66.6544 | 56.2335 | 56.0418 | 56.2573 | -66.8329 | -66.697 | 0.014095 | -66.759 | 56.1482 | 56.2939 | 56.1643 | -66.9966 | -0.15508 | -0.016475 | -0.019051 | 0.023417 | 0.1785 | -0.20818 | 0.007318 | -0.31871 | -0.10182 | -0.019163 | -0.08114 | 0.23757 | 0.043889 | -0.085689 | 122.9114 | 122.7197 | 122.9352 | 66.7159 | -123.0829 | 122.826 | 122.9717 | 122.8422 | 66.692 | -123.2466
96.2656 | 123.262 | -66.6733 | 56.2592 | 0.072674 | -0.0041898 | -3.1667e-05 | 0.056371 | 7.3304e-05 | 0.054873 | 0.058145 | 0.00062833 | 0.0011204 | 0.065314 | 0.0040329 | 0.064664 | -66.6969 | 0.038035 | -66.6499 | 56.2289 | 56.0372 | 56.2482 | -66.8284 | -66.697 | 0.023253 | -66.7453 | 56.1436 | 56.2893 | 56.2376 | -66.9966 | -0.15508 | -0.030208 | -0.023628 | 0.023418 | 0.17849 | -0.22192 | -0.010994 | -0.32329 | -0.11555 | -0.02374 | -0.071981 | 0.25131 | 0.030155 | -0.021587 | 122.9022 | 122.7105 | 122.9214 | 66.7113 | -123.0875 | 122.8169 | 122.9626 | 122.9108 | 66.6965 | -123.2557
97.2656 | 123.1934 | -66.6962 | 56.2271 | 0.057412 | -0.0031218 | -3.1667e-05 | 0.057439 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.0040329 | 0.063596 | -66.7015 | 0.038035 | -66.6453 | 56.2198 | 56.0418 | 56.2573 | -66.8192 | -66.697 | 0.027831 | -66.7498 | 56.139 | 56.303 | 56.1872 | -66.9966 | -0.12303 | -0.007322 | -0.005318 | 0.050884 | 0.17391 | -0.1853 | 0.030206 | -0.3004 | -0.088087 | -0.000852 | -0.053672 | 0.24673 | 0.075934 | -0.039908 | 122.916 | 122.738 | 122.9535 | 66.7342 | -123.0463 | 122.8352 | 122.9992 | 122.8834 | 66.724 | -123.2237
98.2656 | 123.0927 | -66.7145 | 56.2637 | 0.072674 | -0.0041898 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | 0.0011204 | 0.063177 | 0.0029639 | 0.064664 | -66.7061 | 0.038035 | -66.6544 | 56.2289 | 56.0372 | 56.2573 | -66.8284 | -66.6879 | 0.018674 | -66.7544 | 56.1482 | 56.2985 | 56.2193 | -66.9966 | -0.11388 | -0.034786 | 0.008414 | 0.060039 | 0.17392 | -0.22649 | -0.006415 | -0.28209 | -0.11555 | 0.026617 | -0.03994 | 0.24215 | 0.034734 | -0.044479 | 122.9434 | 122.7517 | 122.9718 | 66.7525 | -123.0921 | 122.8627 | 123.0129 | 122.9337 | 66.7332 | -123.2603
99.2656 | 123.1384 | -66.6962 | 56.2592 | 0.04215 | -0.0052578 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.0040329 | 0.063596 | -66.6923 | 0.033457 | -66.659 | 56.2335 | 56.0372 | 56.2527 | -66.8192 | -66.7016 | 0.027831 | -66.7498 | 56.1344 | 56.303 | 56.2559 | -67.0011 | -0.12303 | -0.02563 | 0.003839 | 0.03715 | 0.16018 | -0.22192 | -0.006415 | -0.30498 | -0.12471 | -0.005431 | -0.053672 | 0.2513 | 0.043891 | -0.003272 | 122.9297 | 122.7334 | 122.9489 | 66.7296 | -123.0784 | 122.8306 | 122.9992 | 122.952 | 66.724 | -123.2603
100.2656 | 123.0835 | -66.687 | 56.2271 | 0.057412 | -0.0031218 | -3.1667e-05 | 0.055302 | 0.0011413 | 0.05701 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.063177 | 0.0051009 | 0.064664 | -66.7015 | 0.0243 | -66.6544 | 56.2289 | 56.0418 | 56.2482 | -66.8329 | -66.6879 | 0.036989 | -66.7498 | 56.1436 | 56.2893 | 56.2467 | -66.992 | -0.14592 | 0.001835 | -0.014473 | 0.032573 | 0.1785 | -0.1853 | 0.021049 | -0.30497 | -0.083509 | -0.000849 | -0.062827 | 0.24215 | 0.062198 | 0.019613 | 122.916 | 122.7288 | 122.9352 | 66.7113 | -123.06 | 122.8306 | 122.9763 | 122.9337 | 66.724 | -123.2191
101.2656 | 123.2895 | -66.6458 | 56.25 | 0.04215 | -0.0041898 | -3.1667e-05 | 0.056371 | -0.0020637 | 0.058078 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.066382 | 0.0061689 | 0.063596 | -66.6923 | 0.028878 | -66.6499 | 56.2335 | 56.0372 | 56.2573 | -66.8238 | -66.6924 | 0.023253 | -66.759 | 56.1436 | 56.2985 | 56.2513 | -67.0011 | -0.17796 | -0.016475 | -0.046515 | -0.004048 | 0.17392 | -0.21276 | 0.007318 | -0.35533 | -0.1064 | -0.046627 | -0.11318 | 0.24215 | 0.048467 | 0.001304 | 122.8793 | 122.6831 | 122.9031 | 66.6747 | -123.0738 | 122.7894 | 122.9443 | 122.8971 | 66.6691 | -123.2511
102.2656 | 123.0743 | -66.7099 | 56.282 | 0.057412 | -0.0052578 | -3.1667e-05 | 0.055302 | 7.3304e-05 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.0051009 | 0.063596 | -66.7015 | 0.033457 | -66.6544 | 56.2289 | 56.0464 | 56.2573 | -66.8192 | -66.6924 | 0.023253 | -66.7544 | 56.1436 | 56.2939 | 56.2238 | -66.992 | -0.1093 | -0.053096 | 0.008415 | 0.055461 | 0.16476 | -0.23565 | -0.024725 | -0.28209 | -0.13844 | 0.01746 | -0.044518 | 0.23757 | 0.011846 | -0.058211 | 122.9388 | 122.7563 | 122.9672 | 66.7434 | -123.1012 | 122.8535 | 123.0038 | 122.9337 | 66.7332 | -123.274
103.2656 | 123.1247 | -66.7099 | 56.2683 | 0.087936 | -0.0041898 | -3.1667e-05 | 0.055302 | -0.0020637 | 0.05701 | 0.042884 | 0.00062833 | 0.0011204 | 0.063177 | 0.0051009 | 0.065733 | -66.6923 | 0.038035 | -66.6544 | 56.2381 | 56.0418 | 56.2573 | -66.8192 | -66.7016 | 0.03241 | -66.7498 | 56.1436 | 56.303 | 56.2193 | -66.9966 | -0.1093 | -0.030207 | 0.017572 | 0.055461 | 0.16476 | -0.22649 | -0.010993 | -0.28666 | -0.12471 | 0.008302 | -0.039939 | 0.24673 | 0.034735 | -0.049057 | 122.948 | 122.7517 | 122.9672 | 66.7479 | -123.0875 | 122.8535 | 123.0129 | 122.9292 | 66.7423 | -123.2649
104.2656 | 123.1018 | -66.7191 | 56.2912 | 0.026888 | -0.0041898 | 0.0010373 | 0.054234 | 7.3304e-05 | 0.05701 | 0.058145 | 0.00062833 | 0.0011204 | 0.065314 | 0.0051009 | 0.064664 | -66.7015 | 0.0243 | -66.659 | 56.2289 | 56.0464 | 56.2527 | -66.8238 | -66.697 | 0.027831 | -66.7498 | 56.139 | 56.2985 | 56.2009 | -67.0011 | -0.10472 | -0.062252 | 0.01757 | 0.060038 | 0.16476 | -0.2448 | -0.038459 | -0.28209 | -0.15217 | 0.022036 | -0.030784 | 0.2513 | 0.007268 | -0.09026 | 122.948 | 122.7654 | 122.9718 | 66.7434 | -123.115 | 122.8581 | 123.0175 | 122.92 | 66.7469 | -123.2923
105.2656 | 123.1522 | -66.6779 | 56.2958 | 0.04215 | -0.0052578 | -3.1667e-05 | 0.057439 | -0.0020637 | 0.055941 | 0.073406 | -0.00043967 | -0.0010156 | 0.064245 | 0.0061689 | 0.064664 | -66.6969 | 0.033457 | -66.659 | 56.2335 | 56.0418 | 56.2573 | -66.8192 | -66.7016 | 0.023253 | -66.7498 | 56.1436 | 56.2893 | 56.2513 | -66.9874 | -0.14134 | -0.062251 | -0.019051 | 0.018839 | 0.16018 | -0.25396 | -0.038458 | -0.30955 | -0.15217 | -0.023742 | -0.071983 | 0.23757 | -0.006466 | -0.044472 | 122.9114 | 122.7197 | 122.9352 | 66.7113 | -123.115 | 122.8215 | 122.9672 | 122.9292 | 66.7011 | -123.2832
106.2656 | 123.2529 | -66.6733 | 56.2225 | 0.04215 | -0.0041898 | -0.0021677 | 0.057439 | 0.0011413 | 0.05701 | 0.058145 | 0.00062833 | 0.0011204 | 0.065314 | 0.0051009 | 0.062528 | -66.7015 | 0.033457 | -66.6544 | 56.2335 | 56.0418 | 56.2619 | -66.8238 | -66.6879 | 0.023253 | -66.7544 | 56.1482 | 56.2939 | 56.1414 | -67.0011 | -0.1505 | 0.010991 | -0.028206 | 0.01884 | 0.16934 | -0.18072 | 0.039363 | -0.32786 | -0.074352 | -0.014582 | -0.081139 | 0.24672 | 0.071355 | -0.081116 | 122.9068 | 122.7151 | 122.9352 | 66.7067 | -123.0463 | 122.8215 | 122.9672 | 122.8147 | 66.6965 | -123.2237
107.2656 | 123.1064 | -66.7007 | 56.2729 | 0.057412 | -0.0031218 | 0.0010373 | 0.056371 | 0.0011413 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.066382 | 0.0040329 | 0.064664 | -66.6969 | 0.033457 | -66.659 | 56.2289 | 56.0464 | 56.2527 | -66.8284 | -66.6924 | 0.023253 | -66.7544 | 56.1482 | 56.2985 | 56.2421 | -66.9874 | -0.12761 | -0.043941 | 0.003838 | 0.041728 | 0.16934 | -0.22649 | -0.020148 | -0.28666 | -0.12471 | 0.008305 | -0.053673 | 0.23299 | 0.025579 | -0.030741 | 122.9297 | 122.7471 | 122.9535 | 66.7342 | -123.1012 | 122.8489 | 122.9992 | 122.9429 | 66.724 | -123.2603
108.2656 | 123.1613 | -66.7053 | 56.2912 | 0.072674 | -0.0073948 | -3.1667e-05 | 0.054234 | -0.0009947 | 0.05701 | 0.088667 | 0.00062833 | 5.2373e-05 | 0.064245 | 0.0051009 | 0.065733 | -66.7015 | 0.0243 | -66.659 | 56.2289 | 56.0372 | 56.2665 | -66.8192 | -66.697 | 0.027831 | -66.759 | 56.1436 | 56.2985 | 56.2284 | -66.992 | -0.11388 | -0.062252 | 0.003837 | 0.046305 | 0.16018 | -0.25396 | -0.024723 | -0.28666 | -0.1476 | 0.008303 | -0.053674 | 0.23299 | 0.007268 | -0.062788 | 122.9343 | 122.7426 | 122.9718 | 66.7296 | -123.1104 | 122.8489 | 123.0038 | 122.9337 | 66.7332 | -123.2832
109.2656 | 123.1659 | -66.6779 | 56.2729 | 0.057412 | -0.0031218 | -0.0032367 | 0.057439 | 7.3304e-05 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.0051009 | 0.062528 | -66.7015 | 0.033457 | -66.659 | 56.2335 | 56.0464 | 56.2619 | -66.8238 | -66.7016 | 0.018674 | -66.7498 | 56.1436 | 56.2985 | 56.1872 | -66.9966 | -0.14592 | -0.039363 | -0.023629 | 0.018839 | 0.16476 | -0.22649 | -0.010991 | -0.31871 | -0.12929 | -0.023742 | -0.071983 | 0.24673 | 0.025579 | -0.085684 | 122.9114 | 122.7243 | 122.9398 | 66.7113 | -123.0967 | 122.8215 | 122.9763 | 122.8651 | 66.6965 | -123.2695
110.2656 | 123.1522 | -66.6962 | 56.282 | 0.057412 | -0.0041898 | -0.0010997 | 0.056371 | -0.0009947 | 0.054873 | 0.073406 | 0.0016963 | 0.0011204 | 0.063177 | 0.0072379 | 0.065733 | -66.6923 | 0.028878 | -66.6544 | 56.2427 | 56.0464 | 56.2573 | -66.8329 | -66.697 | 0.018674 | -66.7544 | 56.1436 | 56.2939 | 56.1597 | -66.9966 | -0.13677 | -0.039361 | 0.003839 | 0.041728 | 0.1785 | -0.23565 | -0.024725 | -0.3004 | -0.13844 | -0.000852 | -0.058251 | 0.24215 | 0.011846 | -0.12231 | 122.9388 | 122.7426 | 122.9535 | 66.725 | -123.115 | 122.8398 | 122.9901 | 122.8559 | 66.7148 | -123.2786
111.2656 | 123.2346 | -66.6824 | 56.2546 | 0.072674 | -0.0052578 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.058078 | 0.073406 | 0.00062833 | 0.0011204 | 0.064245 | 0.0051009 | 0.064664 | -66.6923 | 0.019721 | -66.6544 | 56.2244 | 56.0418 | 56.2573 | -66.8192 | -66.6924 | 0.018674 | -66.7544 | 56.139 | 56.2939 | 56.2421 | -67.0011 | -0.13676 | -0.03021 | -0.009894 | 0.027995 | 0.16476 | -0.21276 | 0.00274 | -0.31871 | -0.11555 | -0.010006 | -0.071984 | 0.24672 | 0.039311 | -0.012431 | 122.9068 | 122.7242 | 122.9398 | 66.7022 | -123.0738 | 122.8215 | 122.9763 | 122.9246 | 66.7011 | -123.2557
112.2656 | 123.1567 | -66.6641 | 56.2729 | 0.072674 | -0.0063268 | -0.0010997 | 0.056371 | -0.0031317 | 0.05701 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.062109 | 0.0061689 | 0.065733 | -66.6877 | 0.028878 | -66.659 | 56.2244 | 56.0464 | 56.2573 | -66.8284 | -66.7016 | 0.023253 | -66.7544 | 56.1482 | 56.2939 | 56.1918 | -66.9874 | -0.16423 | -0.04852 | -0.023626 | 0.005107 | 0.16934 | -0.22649 | -0.01557 | -0.32328 | -0.12471 | -0.037474 | -0.090294 | 0.23299 | 0.021001 | -0.081106 | 122.8885 | 122.7105 | 122.9214 | 66.693 | -123.1012 | 122.8123 | 122.958 | 122.8559 | 66.6874 | -123.2603
113.2656 | 123.2025 | -66.6687 | 56.2775 | 0.057412 | -0.0052578 | -0.0010997 | 0.054234 | -0.0009947 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.063177 | 0.0061689 | 0.064664 | -66.6923 | 0.028878 | -66.6544 | 56.2289 | 56.0464 | 56.2573 | -66.8238 | -66.6879 | 0.027831 | -66.7544 | 56.1482 | 56.2985 | 56.265 | -66.9966 | -0.15508 | -0.048519 | -0.023627 | 0.014262 | 0.16934 | -0.23107 | -0.020148 | -0.32786 | -0.12928 | -0.01916 | -0.085717 | 0.24215 | 0.021001 | -0.012426 | 122.8976 | 122.7151 | 122.926 | 66.6976 | -123.1012 | 122.8169 | 122.9672 | 122.9337 | 66.6965 | -123.274
114.2656 | 123.1567 | -66.687 | 56.2729 | 0.057412 | -0.0041898 | -3.1667e-05 | 0.056371 | -0.0020637 | 0.05701 | 0.073406 | -0.00043967 | 0.0011204 | 0.066382 | 0.0061689 | 0.065733 | -66.7015 | 0.028878 | -66.659 | 56.2289 | 56.0464 | 56.2619 | -66.8238 | -66.6924 | 0.018674 | -66.759 | 56.1436 | 56.2985 | 56.1735 | -66.992 | -0.13677 | -0.043941 | -0.014473 | 0.027995 | 0.16476 | -0.22649 | -0.010991 | -0.30497 | -0.12929 | -0.005428 | -0.071984 | 0.23299 | 0.025579 | -0.09942 | 122.916 | 122.7334 | 122.9489 | 66.7159 | -123.0967 | 122.8306 | 122.9855 | 122.8605 | 66.7057 | -123.2649
115.2656 | 123.1796 | -66.6824 | 56.2958 | 0.057412 | -0.0041898 | -0.0010997 | 0.056371 | -0.0009947 | 0.05701 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.064245 | 0.0061689 | 0.06146 | -66.6969 | 0.0243 | -66.6499 | 56.2381 | 56.0464 | 56.2665 | -66.8284 | -66.7016 | 0.014095 | -66.759 | 56.1436 | 56.2893 | 56.2193 | -67.0057 | -0.14592 | -0.057672 | -0.014473 | 0.032573 | 0.17849 | -0.24938 | -0.0293 | -0.32329 | -0.15217 | -0.019164 | -0.076562 | 0.24673 | -0.006466 | -0.076522 | 122.9205 | 122.7288 | 122.9489 | 66.7067 | -123.1241 | 122.826 | 122.9717 | 122.9017 | 66.6965 | -123.3015
116.2656 | 123.2437 | -66.6916 | 56.2225 | 0.072674 | -0.0063268 | -0.0021677 | 0.054234 | 7.3304e-05 | 0.055941 | 0.042884 | 0.00062833 | 5.2373e-05 | 0.062109 | 0.0072379 | 0.062528 | -66.6923 | 0.033457 | -66.6499 | 56.2335 | 56.0464 | 56.2573 | -66.8284 | -66.6924 | 0.018674 | -66.7498 | 56.1436 | 56.2939 | 56.2559 | -66.992 | -0.13677 | 0.010991 | -0.000739 | 0.041728 | 0.17849 | -0.17614 | 0.034784 | -0.3004 | -0.078931 | -0.000851 | -0.05825 | 0.24215 | 0.071355 | 0.033349 | 122.9251 | 122.738 | 122.9489 | 66.725 | -123.0509 | 122.8352 | 122.9855 | 122.9475 | 66.7103 | -123.2145
117.2656 | 123.1567 | -66.687 | 56.2912 | 0.04215 | -0.0052578 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.058078 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.063177 | 0.0051009 | 0.063596 | -66.6923 | 0.0243 | -66.6544 | 56.2289 | 56.0556 | 56.2527 | -66.8284 | -66.6924 | 0.018674 | -66.7498 | 56.1436 | 56.2893 | 56.233 | -66.9966 | -0.14134 | -0.062252 | -0.005316 | 0.032573 | 0.17392 | -0.23565 | -0.038459 | -0.30955 | -0.1476 | -0.005428 | -0.062827 | 0.24673 | -0.001889 | -0.058209 | 122.916 | 122.7426 | 122.9398 | 66.7113 | -123.1196 | 122.8306 | 122.9763 | 122.92 | 66.7057 | -123.2878
118.2656 | 123.1293 | -66.6779 | 56.2958 | 0.057412 | -0.0041898 | -0.0010997 | 0.056371 | -0.0020637 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.0083059 | 0.064664 | -66.6969 | 0.0243 | -66.6499 | 56.2335 | 56.0556 | 56.2573 | -66.8238 | -66.697 | 0.014095 | -66.7453 | 56.1482 | 56.303 | 56.2467 | -66.9966 | -0.14592 | -0.062251 | -0.019051 | 0.027995 | 0.17392 | -0.24022 | -0.038458 | -0.31871 | -0.14759 | -0.019163 | -0.067404 | 0.25131 | 0.00727 | -0.049051 | 122.9114 | 122.7334 | 122.9352 | 66.7022 | -123.1196 | 122.826 | 122.9809 | 122.9246 | 66.692 | -123.2923
119.2656 | 123.1064 | -66.687 | 56.3141 | 0.072674 | -0.0073948 | -3.1667e-05 | 0.057439 | -0.0020637 | 0.054873 | 0.042884 | -0.0015087 | -0.0020846 | 0.065314 | 0.0061689 | 0.064664 | -66.7015 | 0.0243 | -66.6544 | 56.2289 | 56.0556 | 56.2573 | -66.8284 | -66.6924 | 0.014095 | -66.7544 | 56.1436 | 56.2985 | 56.2009 | -66.992 | -0.14134 | -0.08514 | -0.014473 | 0.032573 | 0.17392 | -0.25853 | -0.056769 | -0.30497 | -0.17048 | -0.005428 | -0.067406 | 0.23757 | -0.01562 | -0.11315 | 122.916 | 122.7426 | 122.9443 | 66.7113 | -123.1424 | 122.8306 | 122.9855 | 122.888 | 66.7011 | -123.3061
120.2656 | 123.111 | -66.687 | 56.282 | 0.057412 | -0.0031218 | -0.0010997 | 0.056371 | -0.0009947 | 0.05701 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.064245 | 0.0072379 | 0.064664 | -66.6923 | 0.019721 | -66.6544 | 56.2381 | 56.0464 | 56.2573 | -66.8284 | -66.7016 | 0.018674 | -66.7498 | 56.1344 | 56.2939 | 56.1689 | -66.992 | -0.14134 | -0.043939 | -0.005316 | 0.032573 | 0.17392 | -0.23565 | -0.024725 | -0.30497 | -0.1476 | -0.014586 | -0.062827 | 0.24215 | 0.011846 | -0.11315 | 122.9251 | 122.7334 | 122.9443 | 66.7067 | -123.1104 | 122.8215 | 122.9809 | 122.8559 | 66.7057 | -123.274
121.2656 | 123.1338 | -66.6641 | 56.2958 | 0.057412 | -0.0063268 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.05701 | 0.058145 | -0.00043967 | -0.0020846 | 0.063177 | 0.0061689 | 0.063596 | -66.6923 | 0.0243 | -66.6453 | 56.2335 | 56.051 | 56.2619 | -66.8284 | -66.6924 | 0.023253 | -66.7544 | 56.1482 | 56.2939 | 56.2513 | -66.9966 | -0.16423 | -0.062251 | -0.028204 | 0.018841 | 0.18307 | -0.2448 | -0.033879 | -0.33244 | -0.14759 | -0.028316 | -0.090294 | 0.24215 | -0.001887 | -0.044472 | 122.8976 | 122.7151 | 122.926 | 66.6884 | -123.1241 | 122.8123 | 122.958 | 122.9154 | 66.6874 | -123.2923
122.2656 | 123.1018 | -66.6733 | 56.3095 | 0.04215 | -0.0041898 | -3.1667e-05 | 0.055302 | 0.0011413 | 0.05701 | 0.088667 | 0.00062833 | -0.0020846 | 0.064245 | 0.0061689 | 0.062528 | -66.7015 | 0.019721 | -66.6499 | 56.2381 | 56.051 | 56.2573 | -66.8192 | -66.6879 | 0.018674 | -66.7544 | 56.1436 | 56.2893 | 56.2605 | -66.992 | -0.14592 | -0.071405 | -0.028206 | 0.023418 | 0.16934 | -0.25854 | -0.052191 | -0.31871 | -0.16591 | -0.014582 | -0.081139 | 0.23757 | -0.020199 | -0.049048 | 122.9114 | 122.7243 | 122.9306 | 66.693 | -123.1287 | 122.8169 | 122.9626 | 122.9337 | 66.692 | -123.3015
123.2656 | 123.1522 | -66.6733 | 56.3187 | 0.057412 | -0.0073948 | -0.0010997 | 0.055302 | -0.0009947 | 0.055941 | 0.073406 | -0.0015087 | 0.0011204 | 0.064245 | 0.0061689 | 0.064664 | -66.6877 | 0.019721 | -66.6499 | 56.2335 | 56.0418 | 56.2573 | -66.8284 | -66.697 | 0.014095 | -66.7544 | 56.1436 | 56.2939 | 56.1689 | -67.0011 | -0.15508 | -0.08514 | -0.014471 | 0.023418 | 0.17849 | -0.27685 | -0.061347 | -0.32786 | -0.17506 | -0.02374 | -0.081139 | 0.24672 | -0.024776 | -0.14978 | 122.9068 | 122.7151 | 122.9306 | 66.693 | -123.147 | 122.8169 | 122.9672 | 122.8422 | 66.6874 | -123.3198
124.2656 | 123.1155 | -66.6733 | 56.2958 | 0.04215 | -0.0063268 | -3.1667e-05 | 0.055302 | -0.0031317 | 0.05701 | 0.058145 | -0.00043967 | 0.0011204 | 0.063177 | 0.0061689 | 0.063596 | -66.6969 | 0.0243 | -66.6544 | 56.2381 | 56.0418 | 56.2573 | -66.8238 | -66.6924 | 0.018674 | -66.7544 | 56.1436 | 56.2985 | 56.1368 | -66.992 | -0.1505 | -0.057672 | -0.023628 | 0.01884 | 0.16934 | -0.25396 | -0.038458 | -0.31871 | -0.15217 | -0.019161 | -0.081139 | 0.23757 | 0.002691 | -0.15894 | 122.9114 | 122.7151 | 122.9306 | 66.6976 | -123.1196 | 122.8169 | 122.9717 | 122.8101 | 66.692 | -123.2878
125.2656 | 123.2254 | -66.6367 | 56.2546 | 0.072674 | -0.0073948 | -0.0021677 | 0.056371 | 7.3304e-05 | 0.054873 | 0.058145 | -0.0015087 | -0.0020846 | 0.064245 | 0.0061689 | 0.064664 | -66.6969 | 0.028878 | -66.6544 | 56.2335 | 56.051 | 56.2527 | -66.8192 | -66.697 | 0.018674 | -66.7544 | 56.139 | 56.2939 | 56.2559 | -67.0011 | -0.18254 | -0.021053 | -0.060249 | -0.017781 | 0.16476 | -0.2036 | -0.001838 | -0.36449 | -0.11555 | -0.060361 | -0.11776 | 0.24672 | 0.039311 | 0.001305 | 122.8702 | 122.6876 | 122.8894 | 66.6655 | -123.0738 | 122.7757 | 122.9305 | 122.8925 | 66.6553 | -123.2557
126.2656 | 123.2117 | -66.6595 | 56.2775 | 0.057412 | -0.0073948 | -0.0010997 | 0.055302 | -0.0020637 | 0.055941 | 0.073406 | -0.00043967 | -0.0010156 | 0.063177 | 0.0061689 | 0.063596 | -66.6832 | 0.010564 | -66.6453 | 56.2289 | 56.0464 | 56.2619 | -66.8284 | -66.7016 | 0.014095 | -66.7498 | 56.1436 | 56.2939 | 56.1918 | -66.9966 | -0.16881 | -0.048519 | -0.023626 | 0.014263 | 0.18307 | -0.23107 | -0.015569 | -0.33702 | -0.13386 | -0.042052 | -0.090293 | 0.24673 | 0.016423 | -0.085684 | 122.8885 | 122.7059 | 122.9214 | 66.6701 | -123.1058 | 122.8031 | 122.9534 | 122.8513 | 66.6736 | -123.274
127.2656 | 123.1796 | -66.6504 | 56.2912 | 0.072674 | -0.0063268 | -0.0021677 | 0.056371 | -0.0020637 | 0.055941 | 0.073406 | -0.00043967 | -0.0010156 | 0.063177 | 0.0051009 | 0.062528 | -66.6923 | 0.019721 | -66.6544 | 56.2381 | 56.0418 | 56.2527 | -66.8192 | -66.7062 | 0.009516 | -66.7544 | 56.139 | 56.2847 | 56.2376 | -66.9966 | -0.16881 | -0.053095 | -0.041937 | -0.004048 | 0.16476 | -0.24938 | -0.038459 | -0.34617 | -0.15217 | -0.055785 | -0.10403 | 0.24215 | -0.006468 | -0.053631 | 122.8885 | 122.6922 | 122.9031 | 66.6701 | -123.1104 | 122.7894 | 122.9351 | 122.888 | 66.6599 | -123.2878
128.2656 | 123.23 | -66.6641 | 56.2866 | 0.057412 | -0.0073948 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.0061689 | 0.064664 | -66.6877 | 0.028878 | -66.6544 | 56.2381 | 56.051 | 56.2527 | -66.8192 | -66.6924 | 0.009516 | -66.7544 | 56.1482 | 56.303 | 56.2559 | -67.0011 | -0.15507 | -0.048517 | -0.023626 | 0.009685 | 0.16476 | -0.23565 | -0.033881 | -0.33702 | -0.13844 | -0.028316 | -0.090294 | 0.24672 | 0.016425 | -0.030738 | 122.9022 | 122.7151 | 122.9169 | 66.693 | -123.1058 | 122.8123 | 122.9672 | 122.92 | 66.6736 | -123.2878
129.2656 | 123.2254 | -66.6321 | 56.2866 | 0.04215 | -0.0063268 | -3.1667e-05 | 0.056371 | -0.0020637 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.0072379 | 0.065733 | -66.6969 | 0.010564 | -66.6407 | 56.2289 | 56.051 | 56.2619 | -66.8284 | -66.6924 | 0.004938 | -66.7544 | 56.1482 | 56.303 | 56.1872 | -67.0011 | -0.19628 | -0.057674 | -0.064827 | -0.008624 | 0.18765 | -0.23565 | -0.024724 | -0.36906 | -0.13844 | -0.06036 | -0.12234 | 0.24672 | 0.016425 | -0.099417 | 122.861 | 122.6831 | 122.894 | 66.6426 | -123.115 | 122.7803 | 122.9351 | 122.8193 | 66.637 | -123.2878
130.2656 | 123.2391 | -66.6183 | 56.2912 | 0.057412 | -0.0063268 | -0.0021677 | 0.056371 | -0.0041997 | 0.054873 | 0.073406 | -0.0015087 | -0.0010156 | 0.063177 | 0.0072379 | 0.063596 | -66.6969 | 0.019721 | -66.6407 | 56.2198 | 56.0418 | 56.2482 | -66.8009 | -66.697 | -0.00422 | -66.7544 | 56.1528 | 56.2939 | 56.1002 | -66.992 | -0.18254 | -0.071409 | -0.07856 | -0.022357 | 0.16018 | -0.24938 | -0.043038 | -0.37364 | -0.13844 | -0.078672 | -0.13607 | 0.23757 | 0.00269 | -0.19099 | 122.8381 | 122.6602 | 122.8665 | 66.6381 | -123.0921 | 122.7711 | 122.9122 | 122.7186 | 66.6141 | -123.2832
131.2656 | 123.1064 | -66.6687 | 56.3004 | 0.04215 | -0.012737 | 0.0010373 | 0.056371 | -0.0063367 | 0.051668 | 0.10393 | 0.0016963 | -0.0042206 | 0.058904 | 0.0072379 | 0.065733 | -66.6969 | 0.019721 | -66.7094 | 56.2885 | 56.0784 | 56.2482 | -66.81 | -66.7382 | 0.004938 | -66.7544 | 56.139 | 56.2939 | 56.0865 | -66.9966 | -0.14134 | -0.011888 | -0.028206 | -0.040678 | 0.10066 | -0.22191 | -0.052193 | -0.32786 | -0.16133 | -0.069526 | -0.085717 | 0.24215 | -0.006465 | -0.21388 | 122.9572 | 122.7471 | 122.9169 | 66.6884 | -123.1104 | 122.8077 | 122.9626 | 122.7552 | 66.6736 | -123.2969
132.2656 | 123.2391 | -66.6367 | 56.2637 | 0.057412 | -0.012737 | -0.0010997 | 0.056371 | -0.0052687 | 0.051668 | 0.10393 | -0.00043967 | -0.0042206 | 0.059972 | 0.0072379 | 0.064664 | -66.6923 | 0.010564 | -66.714 | 56.2885 | 56.0464 | 56.2527 | -66.7963 | -66.7428 | 0.000359 | -66.759 | 56.1344 | 56.2939 | 56.0865 | -66.9966 | -0.15965 | 0.024733 | -0.05567 | -0.077299 | 0.082347 | -0.21734 | -0.010993 | -0.35991 | -0.12929 | -0.10615 | -0.12234 | 0.23757 | 0.030156 | -0.17726 | 122.9251 | 122.6831 | 122.8894 | 66.6472 | -123.06 | 122.7711 | 122.9305 | 122.7231 | 66.637 | -123.2603
133.2656 | 123.2758 | -66.655 | 56.2592 | 0.057412 | -0.011668 | 0.0021053 | 0.055302 | -0.0052687 | 0.05701 | 0.058145 | -0.0015087 | -0.0020846 | 0.061041 | 0.0061689 | 0.063596 | -66.6877 | 0.010564 | -66.7048 | 56.2564 | 56.0464 | 56.2619 | -66.7917 | -66.7382 | 0.000359 | -66.7544 | 56.1528 | 56.2939 | 56.1048 | -66.9966 | -0.13676 | -0.002738 | -0.032782 | -0.049832 | 0.086925 | -0.21276 | 0.002742 | -0.3416 | -0.10639 | -0.083259 | -0.09945 | 0.24215 | 0.034734 | -0.15437 | 122.9114 | 122.7014 | 122.9169 | 66.6655 | -123.0509 | 122.8077 | 122.9489 | 122.7598 | 66.6553 | -123.2557
134.2656 | 123.1979 | -66.655 | 56.3141 | 0.026888 | -0.0084628 | -3.1667e-05 | 0.054234 | -0.0020637 | 0.055941 | 0.073406 | -0.00043967 | -0.0010156 | 0.063177 | 0.0072379 | 0.064664 | -66.6877 | 0.005985 | -66.659 | 56.2244 | 56.0418 | 56.2573 | -66.8055 | -66.7016 | 0.000359 | -66.7544 | 56.1344 | 56.2939 | 56.1048 | -66.9874 | -0.15049 | -0.089719 | -0.032782 | -0.004049 | 0.14644 | -0.27227 | -0.056769 | -0.33244 | -0.17964 | -0.04663 | -0.09945 | 0.23299 | -0.020198 | -0.2093 | 122.8793 | 122.6968 | 122.9123 | 66.661 | -123.1195 | 122.7894 | 122.9489 | 122.7598 | 66.6553 | -123.3015
135.2656 | 123.2712 | -66.6367 | 56.2729 | 0.057412 | -0.0095318 | -0.0021677 | 0.056371 | -0.0020637 | 0.054873 | 0.073406 | -0.00043967 | -0.0010156 | 0.063177 | 0.0093739 | 0.063596 | -66.6969 | 0.005985 | -66.6636 | 56.2244 | 56.0418 | 56.2573 | -66.81 | -66.697 | -0.00422 | -66.7498 | 56.1528 | 56.2939 | 56.0911 | -66.992 | -0.17338 | -0.04852 | -0.060249 | -0.026938 | 0.14644 | -0.23107 | -0.01557 | -0.35533 | -0.12013 | -0.060361 | -0.11318 | 0.24215 | 0.021001 | -0.18183 | 122.861 | 122.6785 | 122.894 | 66.6426 | -123.0829 | 122.7894 | 122.9305 | 122.7277 | 66.6324 | -123.2649
136.2656 | 123.2071 | -66.6458 | 56.2866 | 0.057412 | -0.0084628 | -0.0021677 | 0.056371 | -0.0031317 | 0.055941 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.061041 | 0.010443 | 0.062528 | -66.6923 | 0.001407 | -66.6499 | 56.2198 | 56.0372 | 56.2527 | -66.8055 | -66.697 | -0.00422 | -66.7498 | 56.1528 | 56.2939 | 56.0911 | -66.992 | -0.15965 | -0.066831 | -0.046515 | -0.004048 | 0.1556 | -0.24938 | -0.033881 | -0.34617 | -0.13386 | -0.051206 | -0.10403 | 0.24215 | 0.007268 | -0.19557 | 122.8656 | 122.6831 | 122.8986 | 66.6472 | -123.0921 | 122.7986 | 122.9397 | 122.7369 | 66.6416 | -123.2786
137.2656 | 123.2437 | -66.6229 | 56.2729 | 0.026888 | -0.0095318 | -0.0010997 | 0.054234 | -0.0031317 | 0.054873 | 0.088667 | -0.00043967 | -0.0020846 | 0.063177 | 0.0083059 | 0.065733 | -66.6877 | -0.003172 | -66.6453 | 56.2289 | 56.0464 | 56.2527 | -66.8055 | -66.6924 | -0.013377 | -66.7544 | 56.1528 | 56.2939 | 56.1048 | -67.0011 | -0.18254 | -0.043941 | -0.064825 | -0.022358 | 0.16018 | -0.22649 | -0.020148 | -0.37822 | -0.12013 | -0.069515 | -0.13149 | 0.24672 | 0.021001 | -0.1681 | 122.8519 | 122.6693 | 122.8757 | 66.6198 | -123.0783 | 122.7757 | 122.9168 | 122.7277 | 66.6095 | -123.274
138.2656 | 123.2483 | -66.6412 | 56.2729 | 0.04215 | -0.0095318 | -0.0010997 | 0.055302 | -0.0041997 | 0.053805 | 0.058145 | -0.0025767 | -0.0010156 | 0.061041 | 0.0093739 | 0.064664 | -66.6923 | 0.005985 | -66.659 | 56.2289 | 56.0372 | 56.2527 | -66.7963 | -66.7062 | -0.013377 | -66.7498 | 56.1436 | 56.303 | 56.1002 | -66.992 | -0.15507 | -0.043941 | -0.051093 | -0.017782 | 0.13729 | -0.23565 | -0.020148 | -0.35075 | -0.12929 | -0.064941 | -0.1086 | 0.24215 | 0.030158 | -0.17268 | 122.8702 | 122.6785 | 122.894 | 66.6472 | -123.0692 | 122.7848 | 122.9443 | 122.7414 | 66.6279 | -123.2649
139.2656 | 123.2758 | -66.6138 | 56.2729 | 0.072674 | -0.0084628 | -0.0021677 | 0.055302 | -0.0031317 | 0.055941 | 0.058145 | -0.0015087 | -0.0010156 | 0.062109 | 0.0083059 | 0.064664 | -66.6923 | 0.001407 | -66.6544 | 56.2335 | 56.0327 | 56.2436 | -66.7963 | -66.7062 | -0.017956 | -66.7498 | 56.1482 | 56.2985 | 56.0911 | -66.9966 | -0.18253 | -0.039363 | -0.078558 | -0.040669 | 0.14187 | -0.24023 | -0.029305 | -0.3828 | -0.12471 | -0.092406 | -0.13607 | 0.24673 | 0.025579 | -0.18183 | 122.8473 | 122.6464 | 122.8574 | 66.6152 | -123.0692 | 122.762 | 122.9122 | 122.7048 | 66.5958 | -123.2695
140.2656 | 123.2803 | -66.6458 | 56.2683 | 0.057412 | -0.0095318 | -0.0010997 | 0.054234 | -0.0020637 | 0.055941 | 0.073406 | -0.0015087 | -0.0010156 | 0.061041 | 0.0072379 | 0.063596 | -66.6969 | -0.007751 | -66.659 | 56.2244 | 56.0281 | 56.2436 | -66.81 | -66.697 | -0.022535 | -66.7544 | 56.1482 | 56.303 | 56.0956 | -67.0011 | -0.16423 | -0.043943 | -0.051094 | -0.013204 | 0.15102 | -0.24023 | -0.024728 | -0.35533 | -0.12013 | -0.051206 | -0.1086 | 0.24672 | 0.034735 | -0.17268 | 122.8702 | 122.6739 | 122.8894 | 66.6381 | -123.0784 | 122.794 | 122.9489 | 122.7414 | 66.6233 | -123.2695
141.2656 | 123.2254 | -66.5955 | 56.2775 | 0.057412 | -0.0095318 | -0.0021677 | 0.057439 | -0.0009947 | 0.055941 | 0.058145 | -0.0015087 | -0.0010156 | 0.061041 | 0.0093739 | 0.063596 | -66.6877 | -0.012329 | -66.659 | 56.2244 | 56.0372 | 56.2482 | -66.8009 | -66.697 | -0.017956 | -66.7498 | 56.139 | 56.2893 | 56.1094 | -66.992 | -0.20542 | -0.053098 | -0.092291 | -0.063558 | 0.14186 | -0.24023 | -0.029305 | -0.39653 | -0.13844 | -0.10156 | -0.15438 | 0.24215 | 0.011844 | -0.1681 | 122.8198 | 122.6327 | 122.8436 | 66.5831 | -123.0783 | 122.7345 | 122.8848 | 122.7048 | 66.5775 | -123.2695
142.2656 | 123.2574 | -66.6275 | 56.2592 | 0.026888 | -0.0073948 | -3.1667e-05 | 0.053166 | -0.0009947 | 0.054873 | 0.073406 | 0.00062833 | -0.0010156 | 0.063177 | 0.0083059 | 0.062528 | -66.6877 | -0.007751 | -66.6544 | 56.2289 | 56.0464 | 56.2436 | -66.7643 | -66.697 | -0.031692 | -66.7498 | 56.1482 | 56.2985 | 56.1094 | -67.0011 | -0.13675 | -0.030208 | -0.060248 | -0.026937 | 0.10981 | -0.21276 | -0.015572 | -0.37364 | -0.11097 | -0.069517 | -0.12234 | 0.2513 | 0.039312 | -0.14979 | 122.8564 | 122.6739 | 122.8711 | 66.6198 | -123.0234 | 122.7757 | 122.926 | 122.7369 | 66.5958 | -123.2603
143.2656 | 123.2803 | -66.6321 | 56.2546 | 0.057412 | -0.0084628 | -3.1667e-05 | 0.055302 | -0.0020637 | 0.054873 | 0.073406 | 0.00062833 | -0.0010156 | 0.062109 | 0.0083059 | 0.064664 | -66.6877 | -0.016908 | -66.6544 | 56.2244 | 56.0372 | 56.2573 | -66.7963 | -66.7016 | -0.031692 | -66.7498 | 56.1482 | 56.2939 | 56.1094 | -66.9874 | -0.16422 | -0.03021 | -0.05567 | -0.022359 | 0.14187 | -0.21734 | 0.00274 | -0.35533 | -0.1064 | -0.069518 | -0.11776 | 0.23757 | 0.039311 | -0.14521 | 122.8564 | 122.6693 | 122.8894 | 66.6152 | -123.0509 | 122.7803 | 122.926 | 122.7414 | 66.6004 | -123.242
144.2656 | 123.2895 | -66.6367 | 56.2866 | 0.072674 | -0.0095318 | -0.0010997 | 0.054234 | -0.0020637 | 0.054873 | 0.088667 | -0.0015087 | -0.0010156 | 0.063177 | 0.0083059 | 0.062528 | -66.6832 | -0.026065 | -66.6544 | 56.2289 | 56.0418 | 56.2573 | -66.8055 | -66.697 | -0.036271 | -66.7498 | 56.1528 | 56.2985 | 56.1094 | -66.992 | -0.1688 | -0.057674 | -0.046514 | -0.017781 | 0.15102 | -0.2448 | -0.029303 | -0.35533 | -0.13386 | -0.060361 | -0.11318 | 0.24215 | 0.011846 | -0.17725 | 122.8656 | 122.6785 | 122.894 | 66.6106 | -123.0921 | 122.7894 | 122.9351 | 122.746 | 66.6004 | -123.2786
145.2656 | 123.2712 | -66.6275 | 56.282 | 0.072674 | -0.0095318 | -0.0010997 | 0.054234 | -0.0009947 | 0.054873 | 0.088667 | -0.00043967 | -0.0010156 | 0.063177 | 0.0083059 | 0.063596 | -66.6923 | -0.021486 | -66.6453 | 56.2244 | 56.0464 | 56.2482 | -66.7917 | -66.7016 | -0.045428 | -66.7498 | 56.1482 | 56.303 | 56.0636 | -66.992 | -0.16422 | -0.057675 | -0.064826 | -0.017781 | 0.14644 | -0.23565 | -0.033882 | -0.36448 | -0.13386 | -0.074096 | -0.12234 | 0.24215 | 0.021003 | -0.21846 | 122.8519 | 122.6739 | 122.8757 | 66.606 | -123.0738 | 122.7757 | 122.9305 | 122.6911 | 66.5821 | -123.274
146.2656 | 123.2529 | -66.6321 | 56.25 | 0.057412 | -0.0095318 | -0.0021677 | 0.055302 | -0.0031317 | 0.055941 | 0.073406 | -0.00043967 | -0.0020846 | 0.063177 | 0.0083059 | 0.064664 | -66.6969 | -0.026065 | -66.6499 | 56.2289 | 56.0372 | 56.2573 | -66.7826 | -66.6924 | -0.045428 | -66.7498 | 56.1482 | 56.2939 | 55.9583 | -66.9966 | -0.15049 | -0.021053 | -0.064827 | -0.017781 | 0.13271 | -0.21276 | 0.007318 | -0.36449 | -0.10182 | -0.06036 | -0.11776 | 0.24673 | 0.043889 | -0.29173 | 122.861 | 122.6693 | 122.8894 | 66.606 | -123.0326 | 122.7803 | 122.926 | 122.5904 | 66.5867 | -123.2466
147.2656 | 123.2712 | -66.6321 | 56.2729 | 0.057412 | -0.0106 | -0.0010997 | 0.054234 | -0.0031317 | 0.053805 | 0.073406 | -0.00043967 | -0.0020846 | 0.062109 | 0.0083059 | 0.064664 | -66.6832 | -0.026065 | -66.6453 | 56.2335 | 56.0418 | 56.2482 | -66.7963 | -66.6924 | -0.050007 | -66.7361 | 56.1528 | 56.303 | 55.972 | -66.992 | -0.16422 | -0.039363 | -0.051092 | -0.013203 | 0.15102 | -0.23107 | -0.024727 | -0.35991 | -0.12013 | -0.06036 | -0.10402 | 0.25588 | 0.030158 | -0.30088 | 122.8656 | 122.6739 | 122.8802 | 66.606 | -123.0692 | 122.7848 | 122.9351 | 122.6041 | 66.5821 | -123.2649
148.2656 | 123.2712 | -66.6275 | 56.2729 | 0.026888 | -0.0095318 | -3.1667e-05 | 0.054234 | -0.0020637 | 0.055941 | 0.073406 | -0.0015087 | -0.0020846 | 0.063177 | 0.010443 | 0.062528 | -66.6832 | -0.030644 | -66.6499 | 56.2289 | 56.0372 | 56.2573 | -66.8009 | -66.6879 | -0.054586 | -66.7407 | 56.1528 | 56.303 | 56.1048 | -66.992 | -0.17338 | -0.043941 | -0.05567 | -0.022359 | 0.15102 | -0.23565 | -0.01557 | -0.36448 | -0.12013 | -0.060359 | -0.11318 | 0.25131 | 0.030158 | -0.1681 | 122.8564 | 122.6647 | 122.8848 | 66.5969 | -123.0738 | 122.7803 | 122.9305 | 122.7323 | 66.5729 | -123.2649
149.2656 | 123.2712 | -66.6412 | 56.2775 | 0.072674 | -0.0106 | -0.0010997 | 0.055302 | -0.0020637 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.0083059 | 0.063596 | -66.6786 | -0.044379 | -66.6544 | 56.2289 | 56.0464 | 56.2573 | -66.81 | -66.6879 | -0.068322 | -66.7453 | 56.1528 | 56.2985 | 56.1048 | -66.992 | -0.16881 | -0.048519 | -0.037358 | -0.013204 | 0.1556 | -0.23107 | -0.020148 | -0.35075 | -0.12471 | -0.046626 | -0.10403 | 0.24673 | 0.021001 | -0.17268 | 122.8702 | 122.6876 | 122.8986 | 66.5969 | -123.0875 | 122.794 | 122.9397 | 122.746 | 66.5729 | -123.2695
150.2656 | 123.262 | -66.6092 | 56.2729 | 0.057412 | -0.013805 | -0.0010997 | 0.056371 | -0.0074047 | 0.0506 | 0.058145 | -0.00043967 | -0.0052886 | 0.059972 | 0.0093739 | 0.064664 | -66.6877 | -0.053537 | -66.7048 | 56.3022 | 56.0739 | 56.2619 | -66.7963 | -66.7291 | -0.0729 | -66.7453 | 56.1573 | 56.3076 | 56.0865 | -66.9874 | -0.18711 | 0.029313 | -0.078558 | -0.095608 | 0.091504 | -0.19902 | -0.010991 | -0.37822 | -0.11555 | -0.11988 | -0.13607 | 0.24215 | 0.034736 | -0.18641 | 122.9114 | 122.6831 | 122.8711 | 66.5557 | -123.0692 | 122.7665 | 122.9168 | 122.6957 | 66.5363 | -123.2603
151.2656 | 123.2346 | -66.6275 | 56.2775 | 0.057412 | -0.013805 | -0.0010997 | 0.055302 | -0.0041997 | 0.051668 | 0.073406 | -0.0025767 | -0.0031526 | 0.061041 | 0.011511 | 0.062528 | -66.6832 | -0.026065 | -66.6911 | 56.3022 | 56.2112 | 56.3214 | -66.8787 | -66.7153 | -0.068322 | -66.7361 | 56.1573 | 56.303 | 56.1231 | -66.9874 | -0.25122 | 0.024735 | -0.05567 | -0.063563 | 0.18766 | -0.066229 | 0.043953 | -0.3599 | -0.12013 | -0.087832 | -0.1086 | 0.2513 | 0.02558 | -0.15436 | 122.9297 | 122.8387 | 122.9489 | 66.6014 | -123.1562 | 122.7848 | 122.9305 | 122.7506 | 66.5592 | -123.2649
152.2656 | 123.2208 | -66.6229 | 56.2958 | 0.057412 | -0.011668 | -3.1667e-05 | 0.056371 | -0.0020637 | 0.051668 | 0.073406 | -0.0015087 | -0.0020846 | 0.062109 | 0.0083059 | 0.064664 | -66.6877 | -0.035222 | -66.6819 | 56.293 | 56.2021 | 56.3214 | -66.8696 | -66.7108 | -0.063743 | -66.7361 | 56.1573 | 56.303 | 56.2193 | -66.992 | -0.24664 | -0.002732 | -0.064825 | -0.058984 | 0.18766 | -0.093697 | 0.025643 | -0.36906 | -0.13844 | -0.08783 | -0.11318 | 0.25588 | 0.00727 | -0.076522 | 122.916 | 122.825 | 122.9443 | 66.5877 | -123.1653 | 122.7803 | 122.926 | 122.8422 | 66.5592 | -123.2878
153.2656 | 123.2849 | -66.6183 | 56.2775 | 0.04215 | -0.0095318 | -0.0010997 | 0.055302 | -0.0020637 | 0.053805 | 0.073406 | -0.00043967 | -0.0010156 | 0.064245 | 0.0083059 | 0.063596 | -66.6786 | -0.044379 | -66.6682 | 56.2839 | 56.1838 | 56.3077 | -66.8513 | -66.697 | -0.063743 | -66.7407 | 56.1665 | 56.303 | 56.0773 | -66.9874 | -0.2329 | 0.006421 | -0.060246 | -0.049827 | 0.18308 | -0.093703 | 0.030217 | -0.36906 | -0.11097 | -0.078672 | -0.12233 | 0.24673 | 0.02558 | -0.20015 | 122.9022 | 122.8021 | 122.926 | 66.574 | -123.1287 | 122.7848 | 122.9214 | 122.6957 | 66.5546 | -123.2649
154.3281 | 123.2071 | -66.6138 | 56.2866 | 0.072674 | -0.0106 | -0.0010997 | 0.056371 | -0.0031317 | 0.055941 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.065314 | 0.0093739 | 0.062528 | -66.6786 | -0.053537 | -66.6544 | 56.2656 | 56.1746 | 56.2985 | -66.8375 | -66.6879 | -0.0729 | -66.7361 | 56.1573 | 56.3076 | 56.1323 | -66.9874 | -0.22374 | -0.021047 | -0.064823 | -0.040669 | 0.18308 | -0.11202 | 0.011905 | -0.37364 | -0.12928 | -0.074091 | -0.12233 | 0.2513 | 0.021003 | -0.15436 | 122.8793 | 122.7884 | 122.9123 | 66.5602 | -123.1241 | 122.7711 | 122.9214 | 122.746 | 66.5409 | -123.274
155.2656 | 123.23 | -66.6229 | 56.3049 | 0.04215 | -0.0095318 | -0.0010997 | 0.053166 | -0.0020637 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.0072379 | 0.063596 | -66.6786 | -0.058115 | -66.6499 | 56.2656 | 56.1792 | 56.2894 | -66.8284 | -66.6787 | -0.091215 | -66.7315 | 56.1573 | 56.3076 | 56.2376 | -66.9828 | -0.20543 | -0.039358 | -0.055668 | -0.026936 | 0.17849 | -0.12575 | -0.015563 | -0.3599 | -0.14759 | -0.055779 | -0.1086 | 0.2513 | 0.002692 | -0.067364 | 122.8885 | 122.8021 | 122.9123 | 66.5648 | -123.1333 | 122.7803 | 122.9305 | 122.8605 | 66.5317 | -123.2878
156.2656 | 123.2025 | -66.6275 | 56.2958 | 0.04215 | -0.0095318 | -3.1667e-05 | 0.055302 | -0.0031317 | 0.055941 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.062109 | 0.0093739 | 0.065733 | -66.674 | -0.085587 | -66.6361 | 56.2564 | 56.0922 | 56.2802 | -66.8192 | -66.6741 | -0.10953 | -66.7361 | 56.1619 | 56.3122 | 56.2925 | -66.9828 | -0.1917 | -0.039359 | -0.046513 | -0.008624 | 0.18307 | -0.20359 | -0.015565 | -0.35533 | -0.13386 | -0.046623 | -0.1086 | 0.24672 | 0.016427 | -0.003265 | 122.8839 | 122.7197 | 122.9077 | 66.5419 | -123.115 | 122.7894 | 122.9397 | 122.92 | 66.518 | -123.2786
157.2656 | 123.2254 | -66.6229 | 56.2775 | 0.072674 | -0.0095318 | -3.1667e-05 | 0.056371 | -0.0031317 | 0.05701 | 0.058145 | -0.0015087 | -0.0010156 | 0.063177 | 0.0093739 | 0.064664 | -66.6786 | -0.081008 | -66.6315 | 56.261 | 56.0739 | 56.2985 | -66.8192 | -66.6558 | -0.11869 | -66.7315 | 56.1619 | 56.3076 | 56.2879 | -66.9874 | -0.19627 | -0.016471 | -0.055668 | -0.008623 | 0.18765 | -0.2036 | 0.02106 | -0.36448 | -0.11555 | -0.032885 | -0.1086 | 0.25588 | 0.030158 | 0.010467 | 122.8839 | 122.6968 | 122.9215 | 66.5419 | -123.0967 | 122.7848 | 122.9305 | 122.9109 | 66.5042 | -123.2649
158.2656 | 123.2071 | -66.6275 | 56.3049 | 0.04215 | -0.011668 | 0.0021053 | 0.055302 | -0.0020637 | 0.05701 | 0.073406 | 0.00062833 | 0.0021894 | 0.063177 | 0.0093739 | 0.063596 | -66.6694 | -0.1039 | -66.6224 | 56.261 | 56.083 | 56.2939 | -66.8238 | -66.665 | -0.13242 | -66.7269 | 56.1619 | 56.3122 | 56.2925 | -66.9737 | -0.19627 | -0.043937 | -0.041934 | 0.005111 | 0.20139 | -0.2219 | -0.010985 | -0.34617 | -0.14301 | -0.037466 | -0.099443 | 0.24672 | 0.007271 | -0.012421 | 122.8885 | 122.7105 | 122.9214 | 66.5236 | -123.1287 | 122.7894 | 122.9397 | 122.92 | 66.4951 | -123.2786
159.2656 | 123.1338 | -66.655 | 56.3095 | 0.026888 | -0.0106 | -3.1667e-05 | 0.054234 | -0.0031317 | 0.05701 | 0.088667 | 0.00062833 | 5.2373e-05 | 0.063177 | 0.0083059 | 0.063596 | -66.6694 | -0.11764 | -66.6224 | 56.2564 | 56.083 | 56.2848 | -66.8146 | -66.6695 | -0.15074 | -66.7224 | 56.1619 | 56.3168 | 56.2925 | -66.9737 | -0.15965 | -0.053092 | -0.014468 | 0.032577 | 0.19223 | -0.22648 | -0.024719 | -0.3187 | -0.14759 | -0.014579 | -0.067399 | 0.2513 | 0.007273 | -0.016998 | 122.9114 | 122.738 | 122.9398 | 66.5373 | -123.1241 | 122.8169 | 122.9718 | 122.9475 | 66.5042 | -123.2832
160.2656 | 123.2346 | -66.6138 | 56.3049 | 0.04215 | -0.0084628 | -3.1667e-05 | 0.055302 | -0.0031317 | 0.055941 | 0.073406 | 0.00062833 | 0.0011204 | 0.062109 | 0.010443 | 0.063596 | -66.6649 | -0.13595 | -66.6224 | 56.2564 | 56.083 | 56.2985 | -66.8146 | -66.6512 | -0.18737 | -66.7132 | 56.1711 | 56.3214 | 56.2925 | -66.9782 | -0.20085 | -0.048515 | -0.051088 | -0.008621 | 0.19223 | -0.2219 | -0.006406 | -0.36448 | -0.13386 | -0.037462 | -0.099439 | 0.26504 | 0.016428 | -0.012421 | 122.8702 | 122.6968 | 122.9123 | 66.4778 | -123.1196 | 122.7848 | 122.9351 | 122.9063 | 66.4264 | -123.2832
161.2656 | 123.143 | -66.655 | 56.3232 | 0.04215 | -0.0073948 | -3.1667e-05 | 0.055302 | -0.0020637 | 0.058078 | 0.088667 | -0.00043967 | -0.0010156 | 0.063177 | 0.011511 | 0.06146 | -66.6603 | -0.15427 | -66.6178 | 56.2702 | 56.0876 | 56.2939 | -66.81 | -66.6558 | -0.21942 | -66.7132 | 56.1757 | 56.3168 | 56.2971 | -66.9737 | -0.15507 | -0.05309 | -0.005312 | 0.037155 | 0.19223 | -0.23564 | -0.029295 | -0.3187 | -0.14759 | -0.000842 | -0.058241 | 0.26046 | -0.00646 | -0.026152 | 122.9251 | 122.7426 | 122.9489 | 66.5007 | -123.1333 | 122.8306 | 122.9718 | 122.9521 | 66.4355 | -123.2969
162.2656 | 123.2437 | -66.6183 | 56.3324 | 0.072674 | -0.0095318 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.058078 | 0.027623 | -0.00043967 | 0.0011204 | 0.063177 | 0.0093739 | 0.062528 | -66.6603 | -0.18174 | -66.6132 | 56.2702 | 56.0922 | 56.2939 | -66.8009 | -66.6467 | -0.26063 | -66.7086 | 56.1757 | 56.3214 | 56.3108 | -66.9782 | -0.18254 | -0.062245 | -0.041933 | 0.005112 | 0.18765 | -0.24021 | -0.03845 | -0.3599 | -0.15674 | -0.028306 | -0.090283 | 0.26962 | -0.011037 | -0.021571 | 122.8885 | 122.7105 | 122.9123 | 66.4366 | -123.1333 | 122.794 | 122.9397 | 122.9292 | 66.3577 | -123.3106
163.2656 | 123.1796 | -66.6367 | 56.3049 | 0.04215 | -0.0084628 | -0.0010997 | 0.056371 | -0.0031317 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.0093739 | 0.065733 | -66.6511 | -0.21837 | -66.6132 | 56.2747 | 56.0968 | 56.3077 | -66.8055 | -66.6421 | -0.31099 | -66.6995 | 56.1848 | 56.3259 | 56.3108 | -66.9737 | -0.1688 | -0.030201 | -0.014465 | 0.023423 | 0.19223 | -0.20817 | 0.002751 | -0.33701 | -0.12012 | -0.005416 | -0.062815 | 0.2742 | 0.021007 | 0.005894 | 122.9114 | 122.7334 | 122.9443 | 66.4183 | -123.1104 | 122.8215 | 122.9626 | 122.9475 | 66.3257 | -123.2786
164.2656 | 123.2162 | -66.6092 | 56.3141 | 0.057412 | -0.0106 | -0.0010997 | 0.055302 | -0.0020637 | 0.05701 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.062109 | 0.011511 | 0.063596 | -66.642 | -0.25957 | -66.5995 | 56.2747 | 56.1059 | 56.3123 | -66.7963 | -66.6375 | -0.37052 | -66.6995 | 56.1802 | 56.3351 | 56.3154 | -66.9691 | -0.18711 | -0.039356 | -0.032774 | 0.009692 | 0.1968 | -0.20817 | -0.001825 | -0.3599 | -0.13386 | -0.028304 | -0.090281 | 0.26962 | 0.021009 | 0.001317 | 122.8839 | 122.7151 | 122.9215 | 66.3496 | -123.1104 | 122.7894 | 122.9443 | 122.9246 | 66.2387 | -123.2832
165.2656 | 123.1522 | -66.6275 | 56.3416 | 0.072674 | -0.0106 | -0.0021677 | 0.055302 | -0.0020637 | 0.055941 | 0.073406 | -0.00043967 | 0.0011204 | 0.063177 | 0.011511 | 0.065733 | -66.6328 | -0.30994 | -66.6087 | 56.2793 | 56.1288 | 56.3214 | -66.81 | -66.6421 | -0.43462 | -66.6903 | 56.1894 | 56.3351 | 56.32 | -66.9599 | -0.18254 | -0.062244 | -0.005307 | 0.018846 | 0.20138 | -0.21274 | -0.020134 | -0.33243 | -0.15216 | -0.014572 | -0.062814 | 0.26962 | -0.006457 | -0.02157 | 122.9068 | 122.7563 | 122.9489 | 66.3176 | -123.1516 | 122.8169 | 122.9626 | 122.9475 | 66.1929 | -123.3015
166.2656 | 123.1888 | -66.6092 | 56.3507 | 0.057412 | -0.0095318 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.058078 | 0.088667 | -0.00043967 | -0.0010156 | 0.063177 | 0.010443 | 0.065733 | -66.6374 | -0.3603 | -66.6041 | 56.2976 | 56.1792 | 56.326 | -66.7963 | -66.6329 | -0.5033 | -66.6903 | 56.194 | 56.3351 | 56.3246 | -66.9554 | -0.18711 | -0.053085 | -0.028196 | 0.005114 | 0.19223 | -0.17152 | -0.024711 | -0.34616 | -0.15674 | -0.023725 | -0.081124 | 0.26504 | -0.015612 | -0.026146 | 122.9068 | 122.7884 | 122.9352 | 66.2489 | -123.147 | 122.8032 | 122.9443 | 122.9338 | 66.1059 | -123.3061
167.2656 | 123.2529 | -66.5817 | 56.3141 | 0.04215 | -0.0106 | -0.0010997 | 0.053166 | -0.0009947 | 0.058078 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.061041 | 0.011511 | 0.063596 | -66.6282 | -0.41525 | -66.5995 | 56.2885 | 56.1838 | 56.326 | -66.8009 | -66.6329 | -0.59945 | -66.6903 | 56.194 | 56.3397 | 56.2742 | -66.9508 | -0.21916 | -0.025621 | -0.046505 | -0.017774 | 0.20138 | -0.13032 | 0.01191 | -0.36905 | -0.12012 | -0.051191 | -0.10859 | 0.26046 | 0.025588 | -0.03989 | 122.8702 | 122.7655 | 122.9077 | 66.1665 | -123.115 | 122.7757 | 122.9214 | 122.8559 | 65.9823 | -123.2649
168.2656 | 123.2254 | -66.5634 | 56.3232 | 0.057412 | -0.011668 | -3.1667e-05 | 0.056371 | -0.0009947 | 0.058078 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.010443 | 0.063596 | -66.6282 | -0.47935 | -66.5949 | 56.3068 | 56.2021 | 56.3352 | -66.7963 | -66.6283 | -0.70934 | -66.672 | 56.2077 | 56.3626 | 56.2879 | -66.9462 | -0.23289 | -0.016463 | -0.064815 | -0.031506 | 0.20138 | -0.12116 | 0.011913 | -0.38278 | -0.11554 | -0.064922 | -0.10858 | 0.2742 | 0.039326 | -0.035309 | 122.8702 | 122.7655 | 122.8986 | 66.0841 | -123.1195 | 122.7711 | 122.926 | 122.8513 | 65.8541 | -123.2694
169.2656 | 123.2574 | -66.5588 | 56.3232 | 0.057412 | -0.0106 | -3.1667e-05 | 0.055302 | -0.0031317 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.0093739 | 0.064664 | -66.6191 | -0.5526 | -66.5903 | 56.3068 | 56.225 | 56.3397 | -66.7871 | -66.6146 | -0.82839 | -66.672 | 56.2031 | 56.3488 | 56.1872 | -66.9508 | -0.22831 | -0.016463 | -0.060236 | -0.031505 | 0.1968 | -0.098269 | 0.016491 | -0.39194 | -0.12012 | -0.055764 | -0.11316 | 0.27878 | 0.02559 | -0.13604 | 122.8656 | 122.7838 | 122.8986 | 66.0062 | -123.1104 | 122.762 | 122.9077 | 122.746 | 65.7304 | -123.274
170.2656 | 123.2391 | -66.568 | 56.3187 | 0.04215 | -0.0106 | -3.1667e-05 | 0.054234 | -0.0009947 | 0.055941 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.010443 | 0.064664 | -66.6099 | -0.64875 | -66.572 | 56.3205 | 56.2067 | 56.3489 | -66.7871 | -66.61 | -0.97033 | -66.6583 | 56.2123 | 56.358 | 56.2055 | -66.937 | -0.21915 | 0.001849 | -0.041924 | -0.004037 | 0.21512 | -0.11201 | 0.030225 | -0.36905 | -0.10638 | -0.04203 | -0.090272 | 0.27877 | 0.039324 | -0.11315 | 122.8885 | 122.7747 | 122.9169 | 65.9192 | -123.1058 | 122.7803 | 122.926 | 122.7735 | 65.5977 | -123.2557
171.2656 | 123.2803 | -66.5634 | 56.3461 | 0.087936 | -0.0095318 | -0.0010997 | 0.054234 | -0.0020637 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.0093739 | 0.062528 | -66.5916 | -0.73117 | -66.572 | 56.3205 | 56.2296 | 56.3535 | -66.7826 | -66.5963 | -1.126 | -66.6445 | 56.2169 | 56.3717 | 56.233 | -66.9325 | -0.21915 | -0.025616 | -0.028188 | -0.008614 | 0.21054 | -0.11658 | 0.007339 | -0.36904 | -0.12927 | -0.032871 | -0.081113 | 0.28793 | 0.025595 | -0.11314 | 122.8839 | 122.793 | 122.9169 | 65.8322 | -123.1287 | 122.7803 | 122.9351 | 122.7964 | 65.4374 | -123.2786
172.2656 | 123.23 | -66.568 | 56.3599 | 0.04215 | -0.0095318 | -0.0010997 | 0.054234 | -0.0009947 | 0.058078 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.011511 | 0.064664 | -66.5916 | -0.86853 | -66.5583 | 56.3297 | 56.2479 | 56.3535 | -66.7688 | -66.5963 | -1.3 | -66.6399 | 56.2214 | 56.3717 | 56.2696 | -66.9233 | -0.20084 | -0.030192 | -0.023611 | 0.009698 | 0.21053 | -0.112 | -0.006394 | -0.35531 | -0.13842 | -0.028294 | -0.071957 | 0.28335 | 0.011862 | -0.090245 | 122.8977 | 122.8159 | 122.9215 | 65.6995 | -123.1287 | 122.7894 | 122.9397 | 122.8376 | 65.268 | -123.2832
173.3281 | 123.2574 | -66.5863 | 56.3232 | 0.026888 | -0.0106 | -0.0010997 | 0.055302 | -0.0020637 | 0.05701 | 0.042884 | 0.00062833 | 5.2373e-05 | 0.063177 | 0.010443 | 0.063596 | -66.587 | -0.99215 | -66.5537 | 56.3297 | 56.2433 | 56.3718 | -66.7643 | -66.5826 | -1.4602 | -66.6354 | 56.2352 | 56.3855 | 56.3154 | -66.9096 | -0.17795 | 0.006429 | -0.000722 | 0.032587 | 0.21053 | -0.079953 | 0.048542 | -0.32326 | -0.088069 | 0.003753 | -0.049067 | 0.2742 | 0.062219 | -0.007838 | 122.916 | 122.8296 | 122.9581 | 65.5942 | -123.0875 | 122.8215 | 122.9718 | 122.9017 | 65.1261 | -123.2328
174.2656 | 123.2437 | -66.5726 | 56.3461 | 0.057412 | -0.011668 | -3.1667e-05 | 0.055302 | -0.0031317 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.011511 | 0.063596 | -66.5733 | -1.1478 | -66.5446 | 56.3388 | 56.2524 | 56.3718 | -66.7551 | -66.578 | -1.6617 | -66.6262 | 56.2306 | 56.3946 | 56.3612 | -66.9096 | -0.18252 | -0.007302 | -0.000719 | 0.028011 | 0.21053 | -0.093683 | 0.025654 | -0.337 | -0.11554 | -0.005401 | -0.053643 | 0.28335 | 0.048488 | 0.01506 | 122.9114 | 122.825 | 122.9444 | 65.4247 | -123.1012 | 122.8032 | 122.9672 | 122.9338 | 64.9109 | -123.2557
175.2656 | 123.2391 | -66.5497 | 56.3828 | 0.057412 | -0.0106 | 0.0010373 | 0.055302 | -0.0031317 | 0.05701 | 0.058145 | 0.0016963 | -0.0010156 | 0.062109 | 0.011511 | 0.063596 | -66.5641 | -1.2852 | -66.5354 | 56.348 | 56.257 | 56.3809 | -66.7505 | -66.5597 | -1.854 | -66.6262 | 56.2489 | 56.4038 | 56.3749 | -66.9004 | -0.20083 | -0.034766 | -0.014451 | 0.014279 | 0.21511 | -0.12572 | -0.00181 | -0.35073 | -0.13384 | -0.009975 | -0.076531 | 0.27419 | 0.021024 | -0.007825 | 122.8977 | 122.8067 | 122.9306 | 65.2645 | -123.1333 | 122.7986 | 122.9535 | 122.9246 | 64.6957 | -123.2832
176.2656 | 123.2391 | -66.5405 | 56.3461 | 0.057412 | -0.0106 | -0.0010997 | 0.053166 | -0.0031317 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.010443 | 0.06146 | -66.5596 | -1.4729 | -66.5125 | 56.3526 | 56.2341 | 56.3764 | -66.7459 | -66.5459 | -2.0601 | -66.6079 | 56.2535 | 56.4084 | 56.3795 | -66.905 | -0.20541 | 0.006433 | -0.019028 | 0.028014 | 0.23342 | -0.112 | 0.030232 | -0.36446 | -0.092643 | -0.005394 | -0.067372 | 0.29709 | 0.062224 | 0.033375 | 122.8931 | 122.7747 | 122.9169 | 65.0676 | -123.0921 | 122.794 | 122.9489 | 122.92 | 64.4805 | -123.2511
177.2656 | 123.262 | -66.5543 | 56.3599 | 0.057412 | -0.011668 | -3.1667e-05 | 0.055302 | -0.0009947 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.011511 | 0.063596 | -66.5412 | -1.6606 | -66.5079 | 56.3526 | 56.2296 | 56.3901 | -66.7322 | -66.5368 | -2.2936 | -66.5942 | 56.2626 | 56.4129 | 56.3841 | -66.8958 | -0.17794 | -0.0073 | 0.013018 | 0.046326 | 0.22426 | -0.13031 | 0.030235 | -0.34157 | -0.097219 | 0.017496 | -0.039903 | 0.30167 | 0.053069 | 0.02422 | 122.9068 | 122.7838 | 122.9444 | 64.8936 | -123.0921 | 122.8169 | 122.9672 | 122.9383 | 64.2607 | -123.2557
178.2656 | 123.23 | -66.4993 | 56.3873 | 0.04215 | -0.0106 | -3.1667e-05 | 0.054234 | -0.0009947 | 0.055941 | 0.073406 | 0.00062833 | 0.0011204 | 0.064245 | 0.011511 | 0.064664 | -66.5367 | -1.8712 | -66.4988 | 56.3617 | 56.2524 | 56.3901 | -66.723 | -66.5322 | -2.4905 | -66.585 | 56.2672 | 56.4221 | 56.407 | -66.8821 | -0.22371 | -0.025609 | -0.037334 | 0.000551 | 0.22426 | -0.13488 | 0.002769 | -0.38276 | -0.12011 | -0.032856 | -0.085676 | 0.29709 | 0.034761 | 0.019647 | 122.861 | 122.7518 | 122.8894 | 64.6281 | -123.1104 | 122.7666 | 122.9214 | 122.9063 | 64.0089 | -123.2694
179.2656 | 123.262 | -66.5222 | 56.4011 | 0.072674 | -0.013805 | -0.0010997 | 0.053166 | -0.0020637 | 0.05701 | 0.042884 | 0.00062833 | 5.2373e-05 | 0.065314 | 0.010443 | 0.062528 | -66.5183 | -2.0681 | -66.4896 | 56.3663 | 56.2662 | 56.4038 | -66.7139 | -66.5093 | -2.7011 | -66.5804 | 56.2718 | 56.4312 | 56.4116 | -66.8684 | -0.19167 | -0.034764 | 0.003867 | 0.032596 | 0.22426 | -0.13488 | 0.002772 | -0.34614 | -0.12926 | 0.012925 | -0.05821 | 0.28793 | 0.030185 | 0.010493 | 122.8885 | 122.7884 | 122.9261 | 64.4541 | -123.1149 | 122.794 | 122.9535 | 122.9338 | 63.8211 | -123.2694
180.2656 | 123.2071 | -66.5268 | 56.4056 | 0.026888 | -0.0106 | 0.0010373 | 0.054234 | -0.0031317 | 0.05701 | 0.058145 | -0.0015087 | -0.0010156 | 0.064245 | 0.011511 | 0.063596 | -66.5046 | -2.2742 | -66.4667 | 56.3892 | 56.2433 | 56.4038 | -66.6956 | -66.4956 | -2.8705 | -66.5575 | 56.281 | 56.4358 | 56.4253 | -66.8638 | -0.16877 | -0.01645 | 0.022179 | 0.060064 | 0.22884 | -0.16235 | -0.001806 | -0.33698 | -0.12468 | 0.031238 | -0.030739 | 0.30625 | 0.030185 | 0.019651 | 122.916 | 122.7701 | 122.9306 | 64.2526 | -123.1012 | 122.8078 | 122.9626 | 122.9521 | 63.6563 | -123.2694
181.2656 | 123.1934 | -66.4993 | 56.4377 | 0.057412 | -0.011668 | -3.1667e-05 | 0.054234 | -0.0031317 | 0.058078 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.011511 | 0.064664 | -66.4955 | -2.5031 | -66.4713 | 56.3938 | 56.2799 | 56.4221 | -66.6956 | -66.491 | -3.0674 | -66.5438 | 56.2993 | 56.4541 | 56.4344 | -66.8546 | -0.19624 | -0.043914 | 0.003871 | 0.028021 | 0.22426 | -0.15776 | -0.015535 | -0.35529 | -0.13841 | 0.008352 | -0.044468 | 0.31082 | 0.016457 | -0.003235 | 122.8931 | 122.7793 | 122.9215 | 63.9962 | -123.1333 | 122.7986 | 122.9535 | 122.9338 | 63.432 | -123.2923
182.2656 | 123.1064 | -66.5543 | 56.4789 | 0.087936 | -0.0106 | -3.1667e-05 | 0.055302 | -0.0041997 | 0.055941 | 0.058145 | 0.00062833 | 0.0011204 | 0.063177 | 0.010443 | 0.064664 | -66.4817 | -2.7595 | -66.4576 | 56.4029 | 56.2937 | 56.4313 | -66.691 | -66.4818 | -3.2917 | -66.5301 | 56.2993 | 56.4587 | 56.439 | -66.85 | -0.13673 | -0.075957 | 0.072537 | 0.096687 | 0.23342 | -0.18522 | -0.047577 | -0.29578 | -0.17961 | 0.072441 | 0.024199 | 0.31998 | -0.020164 | -0.039855 | 122.9572 | 122.8479 | 122.9856 | 63.7948 | -123.1699 | 122.8535 | 123.013 | 122.9933 | 63.2625 | -123.3289
183.2656 | 123.23 | -66.4856 | 56.4102 | 0.057412 | -0.0106 | -0.0010997 | 0.055302 | -0.0020637 | 0.058078 | 0.073406 | 0.0016963 | 5.2373e-05 | 0.064245 | 0.011511 | 0.062528 | -66.468 | -3.0159 | -66.4393 | 56.4121 | 56.3211 | 56.4405 | -66.6727 | -66.4635 | -3.4062 | -66.5301 | 56.3084 | 56.4587 | 56.4344 | -66.8363 | -0.18708 | 0.001865 | 0.017609 | 0.046336 | 0.23341 | -0.089086 | 0.030246 | -0.35071 | -0.10179 | 0.022091 | -0.044465 | 0.30624 | 0.048501 | 0.024231 | 122.8977 | 122.8067 | 122.9261 | 63.4697 | -123.0829 | 122.794 | 122.9443 | 122.92 | 63.0794 | -123.2465
184.2656 | 123.1888 | -66.5039 | 56.4377 | 0.026888 | -0.012737 | -0.0021677 | 0.053166 | -0.0041997 | 0.055941 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.063177 | 0.01258 | 0.062528 | -66.468 | -3.2586 | -66.4393 | 56.4258 | 56.312 | 56.4496 | -66.6727 | -66.4543 | -3.5985 | -66.5117 | 56.3176 | 56.477 | 56.4024 | -66.8226 | -0.16877 | -0.011866 | 0.035919 | 0.064646 | 0.23341 | -0.12571 | 0.011937 | -0.31866 | -0.1201 | 0.049559 | -0.00784 | 0.31082 | 0.03935 | -0.035285 | 122.9297 | 122.8159 | 122.9535 | 63.2453 | -123.1104 | 122.8215 | 122.9809 | 122.9063 | 62.9054 | -123.2603
185.2656 | 123.2025 | -66.4856 | 56.4377 | 0.057412 | -0.012737 | -0.0021677 | 0.055302 | -0.0041997 | 0.055941 | 0.058145 | -0.00043967 | -0.0010156 | 0.062109 | 0.01258 | 0.064664 | -66.4451 | -3.5058 | -66.4164 | 56.435 | 56.3394 | 56.4542 | -66.6589 | -66.4498 | -3.7359 | -66.5117 | 56.3267 | 56.4816 | 56.4665 | -66.8226 | -0.17334 | -0.002709 | 0.040501 | 0.069227 | 0.24257 | -0.098236 | 0.016515 | -0.33697 | -0.11094 | 0.035827 | -0.02615 | 0.31082 | 0.043928 | 0.028815 | 122.9206 | 122.825 | 122.9398 | 62.9798 | -123.0966 | 122.8123 | 122.9672 | 122.9521 | 62.7497 | -123.2603
186.2656 | 123.2117 | -66.4536 | 56.456 | 0.04215 | -0.011668 | -3.1667e-05 | 0.056371 | -0.0031317 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.063177 | 0.011511 | 0.064664 | -66.4222 | -3.7485 | -66.4026 | 56.435 | 56.3349 | 56.4725 | -66.6498 | -66.4269 | -3.887 | -66.4934 | 56.3405 | 56.4908 | 56.4757 | -66.8088 | -0.19623 | -0.02102 | 0.031348 | 0.050918 | 0.24714 | -0.12113 | 0.016519 | -0.35528 | -0.11552 | 0.026677 | -0.039879 | 0.3154 | 0.034775 | 0.019662 | 122.8885 | 122.7884 | 122.9261 | 62.7051 | -123.1058 | 122.794 | 122.9443 | 122.9292 | 62.5666 | -123.2648
187.2656 | 123.1018 | -66.4581 | 56.5018 | 0.087936 | -0.011668 | -0.0010997 | 0.055302 | -0.0031317 | 0.054873 | 0.058145 | -0.0015087 | 0.0011204 | 0.064245 | 0.011511 | 0.064664 | -66.4222 | -3.9728 | -66.3935 | 56.4533 | 56.2753 | 56.4817 | -66.6406 | -66.4131 | -4.0197 | -66.4797 | 56.3496 | 56.4999 | 56.4802 | -66.7997 | -0.18249 | -0.048482 | 0.035926 | 0.064653 | 0.24714 | -0.22643 | -0.0201 | -0.34154 | -0.15214 | 0.044991 | -0.021565 | 0.31998 | -0.001844 | -0.021536 | 122.9114 | 122.7335 | 122.9398 | 62.4853 | -123.1424 | 122.8078 | 122.9581 | 122.9384 | 62.4384 | -123.3014
188.2656 | 123.1888 | -66.4581 | 56.4606 | 0.04215 | -0.012737 | -0.0010997 | 0.055302 | -0.0020637 | 0.054873 | 0.042884 | -0.0015087 | -0.0010156 | 0.065314 | 0.01258 | 0.064664 | -66.4039 | -4.1422 | -66.3797 | 56.4579 | 56.2799 | 56.4908 | -66.6223 | -66.3948 | -4.061 | -66.4705 | 56.3634 | 56.5182 | 56.494 | -66.7905 | -0.16417 | -0.002705 | 0.05424 | 0.078388 | 0.24256 | -0.18065 | 0.030256 | -0.33239 | -0.0972 | 0.063306 | -0.012408 | 0.31998 | 0.057669 | 0.033399 | 122.916 | 122.7381 | 122.949 | 62.3159 | -123.0829 | 122.8215 | 122.9764 | 122.9521 | 62.3972 | -123.2511
189.2656 | 123.2025 | -66.4261 | 56.4789 | 0.04215 | -0.0106 | -0.0021677 | 0.055302 | -0.0031317 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.064245 | 0.01258 | 0.064664 | -66.3902 | -4.3208 | -66.366 | 56.4716 | 56.2937 | 56.5 | -66.6086 | -66.3857 | -4.148 | -66.4476 | 56.3771 | 56.5274 | 56.5077 | -66.7814 | -0.18248 | -0.007281 | 0.035931 | 0.060078 | 0.24256 | -0.18522 | 0.021102 | -0.35527 | -0.10178 | 0.040419 | -0.021558 | 0.33372 | 0.048515 | 0.028824 | 122.8977 | 122.7197 | 122.9261 | 62.1053 | -123.0875 | 122.8032 | 122.9535 | 122.9338 | 62.2781 | -123.2602
190.2656 | 123.1979 | -66.4124 | 56.4972 | 0.026888 | -0.011668 | -0.0021677 | 0.056371 | -0.0009947 | 0.058078 | 0.058145 | 0.00062833 | 0.0011204 | 0.062109 | 0.013648 | 0.063596 | -66.3673 | -4.4765 | -66.3385 | 56.4808 | 56.2982 | 56.5137 | -66.5994 | -66.3628 | -4.1708 | -66.4293 | 56.3908 | 56.5366 | 56.5214 | -66.7676 | -0.18706 | -0.016434 | 0.045091 | 0.073816 | 0.26087 | -0.19896 | 0.016528 | -0.35527 | -0.10635 | 0.049581 | -0.016975 | 0.3383 | 0.039363 | 0.02425 | 122.8931 | 122.7106 | 122.9261 | 61.9359 | -123.0966 | 122.8032 | 122.9489 | 122.9338 | 62.2415 | -123.2648
191.2656 | 123.056 | -66.3803 | 56.4926 | 0.026888 | -0.012737 | -3.1667e-05 | 0.055302 | -0.0031317 | 0.05701 | 0.073406 | -0.00043967 | -0.0010156 | 0.063177 | 0.011511 | 0.063596 | -66.3489 | -4.568 | -66.3294 | 56.4945 | 56.3166 | 56.5366 | -66.5765 | -66.3399 | -4.1937 | -66.4202 | 56.4046 | 56.5549 | 56.5352 | -66.7447 | -0.19621 | 0.001878 | 0.031361 | 0.050929 | 0.24713 | -0.17606 | 0.043998 | -0.36442 | -0.088038 | 0.040431 | -0.039862 | 0.32456 | 0.062254 | 0.042562 | 122.8748 | 122.6969 | 122.9169 | 61.8123 | -123.0691 | 122.7849 | 122.9352 | 122.9155 | 62.1866 | -123.2373
192.2656 | 123.1293 | -66.4032 | 56.5796 | 0.057412 | -0.011668 | -3.1667e-05 | 0.054234 | -0.0031317 | 0.05701 | 0.073406 | -0.00043967 | 0.0011204 | 0.064245 | 0.011511 | 0.064664 | -66.3261 | -4.6779 | -66.3065 | 56.5174 | 56.344 | 56.5412 | -66.5628 | -66.3261 | -4.1434 | -66.4019 | 56.4183 | 56.5686 | 56.5489 | -66.7356 | -0.15958 | -0.062205 | 0.077141 | 0.096708 | 0.25629 | -0.23557 | -0.038398 | -0.33237 | -0.16128 | 0.077055 | 0.001341 | 0.33371 | -0.010985 | -0.030677 | 122.9206 | 122.7472 | 122.9444 | 61.7253 | -123.1424 | 122.8215 | 122.9718 | 122.9521 | 62.2598 | -123.3152
193.2656 | 123.1934 | -66.3803 | 56.5109 | 0.04215 | -0.013805 | -3.1667e-05 | 0.055302 | -0.0041997 | 0.058078 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.064245 | 0.01258 | 0.064664 | -66.3077 | -4.6779 | -66.2882 | 56.5311 | 56.3578 | 56.5687 | -66.5445 | -66.3033 | -4.1205 | -66.3835 | 56.4412 | 56.5915 | 56.5672 | -66.7081 | -0.16415 | 0.020195 | 0.072566 | 0.092133 | 0.25629 | -0.15316 | 0.057738 | -0.32779 | -0.06972 | 0.07706 | -0.003232 | 0.32456 | 0.080573 | 0.056303 | 122.9114 | 122.7381 | 122.949 | 61.7024 | -123.0554 | 122.8215 | 122.9718 | 122.9475 | 62.2598 | -123.219
194.2656 | 123.2437 | -66.3391 | 56.5338 | 0.026888 | -0.012737 | -0.0021677 | 0.053166 | -0.0041997 | 0.05701 | 0.058145 | -0.00043967 | 0.0011204 | 0.061041 | 0.01258 | 0.063596 | -66.294 | -4.6871 | -66.2699 | 56.5586 | 56.3761 | 56.5778 | -66.5216 | -66.2895 | -4.0564 | -66.3698 | 56.4549 | 56.6098 | 56.5855 | -66.6989 | -0.18246 | 0.024778 | 0.045102 | 0.069247 | 0.2517 | -0.15774 | 0.044008 | -0.35983 | -0.078872 | 0.049597 | -0.030695 | 0.32914 | 0.075999 | 0.051729 | 122.8977 | 122.7152 | 122.9169 | 61.652 | -123.0554 | 122.7941 | 122.9489 | 122.9247 | 62.2827 | -123.2328
195.2656 | 123.2391 | -66.3391 | 56.5567 | 0.057412 | -0.012737 | -0.0021677 | 0.054234 | -0.0041997 | 0.05701 | 0.073406 | 0.0016963 | -0.0010156 | 0.064245 | 0.013648 | 0.064664 | -66.2757 | -4.6642 | -66.2653 | 56.5723 | 56.3807 | 56.5916 | -66.5124 | -66.2758 | -4.0197 | -66.3515 | 56.4687 | 56.619 | 56.5855 | -66.676 | -0.1733 | 0.015624 | 0.063416 | 0.073826 | 0.24712 | -0.17605 | 0.034854 | -0.33694 | -0.088026 | 0.063333 | -0.01238 | 0.32456 | 0.062267 | 0.02884 | 122.9114 | 122.7198 | 122.9307 | 61.6749 | -123.0691 | 122.8078 | 122.9581 | 122.9247 | 62.3194 | -123.2327
196.2656 | 123.2346 | -66.3208 | 56.5796 | 0.057412 | -0.012737 | -0.0010997 | 0.055302 | -0.0031317 | 0.058078 | 0.058145 | -0.0025767 | -0.0020846 | 0.062109 | 0.014716 | 0.063596 | -66.2528 | -4.5955 | -66.2332 | 56.5769 | 56.399 | 56.6144 | -66.5033 | -66.2575 | -3.9099 | -66.3332 | 56.4824 | 56.6327 | 56.6176 | -66.6669 | -0.18245 | -0.002686 | 0.067998 | 0.087564 | 0.27002 | -0.18062 | 0.034859 | -0.34609 | -0.097178 | 0.063338 | -0.012375 | 0.33371 | 0.053115 | 0.038002 | 122.8977 | 122.7198 | 122.9352 | 61.7253 | -123.0828 | 122.8032 | 122.9535 | 122.9384 | 62.4109 | -123.2465
197.2656 | 123.2437 | -66.2796 | 56.6437 | 0.04215 | -0.014874 | -0.0010997 | 0.053166 | -0.0020637 | 0.05701 | 0.073406 | 0.00062833 | 0.0011204 | 0.063177 | 0.01258 | 0.062528 | -66.2391 | -4.5177 | -66.2287 | 56.5815 | 56.4219 | 56.6282 | -66.4804 | -66.2437 | -3.8274 | -66.324 | 56.5007 | 56.6464 | 56.6313 | -66.6486 | -0.20076 | -0.062194 | 0.040534 | 0.050943 | 0.2517 | -0.22181 | -0.015492 | -0.36897 | -0.14295 | 0.035875 | -0.044417 | 0.32455 | 0.002764 | -0.012349 | 122.8611 | 122.7015 | 122.9078 | 61.7619 | -123.124 | 122.7803 | 122.926 | 122.9109 | 62.4522 | -123.2923
198.2656 | 123.262 | -66.2979 | 56.5887 | 0.026888 | -0.013805 | -3.1667e-05 | 0.054234 | -0.0020637 | 0.055941 | 0.027623 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.013648 | 0.063596 | -66.2253 | -4.4215 | -66.2103 | 56.609 | 56.431 | 56.6373 | -66.462 | -66.2391 | -3.7404 | -66.3057 | 56.5145 | 56.6693 | 56.6359 | -66.644 | -0.16413 | 0.020208 | 0.07258 | 0.087567 | 0.2517 | -0.15772 | 0.048597 | -0.34608 | -0.074284 | 0.058765 | -0.007791 | 0.33829 | 0.080589 | 0.047162 | 122.9069 | 122.7289 | 122.9353 | 61.8764 | -123.0508 | 122.8124 | 122.9672 | 122.9338 | 62.5575 | -123.2327
199.2656 | 123.2574 | -66.2796 | 56.5979 | 0.011626 | -0.013805 | -0.0010997 | 0.055302 | -0.0031317 | 0.05701 | 0.058145 | -0.00043967 | -0.0010156 | 0.064245 | 0.01258 | 0.063596 | -66.207 | -4.3483 | -66.1966 | 56.6181 | 56.431 | 56.6511 | -66.4575 | -66.2163 | -3.6351 | -66.2965 | 56.5282 | 56.6739 | 56.6496 | -66.6257 | -0.17786 | 0.02021 | 0.072583 | 0.082991 | 0.26085 | -0.16688 | 0.053178 | -0.34608 | -0.069703 | 0.063348 | -0.016945 | 0.32913 | 0.076013 | 0.051742 | 122.8977 | 122.7106 | 122.9307 | 61.9313 | -123.0554 | 122.8078 | 122.9535 | 122.9292 | 62.6445 | -123.2236
200.2656 | 123.2529 | -66.2796 | 56.6116 | 0.04215 | -0.013805 | -0.0010997 | 0.054234 | -0.0041997 | 0.05701 | 0.058145 | -0.0015087 | -0.0010156 | 0.063177 | 0.011511 | 0.062528 | -66.1979 | -4.1789 | -66.1829 | 56.6318 | 56.4539 | 56.6694 | -66.4437 | -66.2071 | -3.5024 | -66.2874 | 56.5374 | 56.6922 | 56.668 | -66.6165 | -0.16412 | 0.020212 | 0.081739 | 0.096726 | 0.26085 | -0.15771 | 0.05776 | -0.33692 | -0.074279 | 0.072505 | -0.007787 | 0.32913 | 0.080594 | 0.056324 | 122.9114 | 122.7335 | 122.949 | 62.1007 | -123.0554 | 122.817 | 122.9718 | 122.9476 | 62.7772 | -123.2282
201.2656 | 123.1934 | -66.2842 | 56.662 | 0.04215 | -0.012737 | -0.0021677 | 0.054234 | -0.0020637 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.013648 | 0.064664 | -66.1887 | -4.0323 | -66.1783 | 56.641 | 56.4631 | 56.6786 | -66.4437 | -66.2025 | -3.4062 | -66.2782 | 56.5511 | 56.6968 | 56.6725 | -66.6074 | -0.15955 | -0.020985 | 0.095474 | 0.10588 | 0.26543 | -0.19891 | 0.016563 | -0.32318 | -0.1109 | 0.081662 | 0.005948 | 0.32913 | 0.034819 | 0.010548 | 122.9252 | 122.7473 | 122.9627 | 62.2518 | -123.1057 | 122.8353 | 122.981 | 122.9567 | 62.878 | -123.2694
202.2656 | 123.1567 | -66.2979 | 56.6528 | 0.04215 | -0.013805 | -0.0010997 | 0.053166 | -0.0031317 | 0.05701 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.014716 | 0.063596 | -66.175 | -3.8721 | -66.1646 | 56.641 | 56.4631 | 56.6877 | -66.4254 | -66.1888 | -3.2688 | -66.2645 | 56.5557 | 56.706 | 56.6863 | -66.5936 | -0.1275 | -0.01183 | 0.12294 | 0.13335 | 0.26085 | -0.18975 | 0.034875 | -0.29572 | -0.097164 | 0.10913 | 0.033417 | 0.32913 | 0.053131 | 0.033439 | 122.9389 | 122.761 | 122.9856 | 62.4258 | -123.0782 | 122.8536 | 123.0039 | 122.9842 | 63.0291 | -123.2465
203.2656 | 123.2117 | -66.2704 | 56.6345 | 0.057412 | -0.011668 | -0.0010997 | 0.055302 | -0.0041997 | 0.05701 | 0.027623 | 0.00062833 | 5.2373e-05 | 0.063177 | 0.011511 | 0.062528 | -66.1704 | -3.7302 | -66.1691 | 56.6502 | 56.4722 | 56.6831 | -66.43 | -66.1888 | -3.1498 | -66.2599 | 56.5602 | 56.7105 | 56.6817 | -66.5936 | -0.15954 | 0.015637 | 0.10005 | 0.10131 | 0.26085 | -0.16229 | 0.048607 | -0.32318 | -0.074275 | 0.081665 | 0.01053 | 0.33371 | 0.07602 | 0.047172 | 122.9206 | 122.7427 | 122.9536 | 62.5403 | -123.0645 | 122.8307 | 122.981 | 122.9521 | 63.1207 | -123.2281
204.2656 | 123.1613 | -66.2704 | 56.6711 | 0.04215 | -0.013805 | -0.0010997 | 0.056371 | -0.0020637 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.062109 | 0.013648 | 0.064664 | -66.1658 | -3.5836 | -66.16 | 56.6502 | 56.4722 | 56.6923 | -66.4163 | -66.1842 | -2.9941 | -66.2508 | 56.5648 | 56.7105 | 56.6908 | -66.5845 | -0.14581 | -0.020985 | 0.10463 | 0.11046 | 0.25627 | -0.19891 | 0.021143 | -0.31402 | -0.10632 | 0.086244 | 0.019688 | 0.33371 | 0.039398 | 0.019707 | 122.9206 | 122.7427 | 122.9627 | 62.6868 | -123.0874 | 122.8353 | 122.981 | 122.9613 | 63.2763 | -123.2556
205.2656 | 123.1293 | -66.2979 | 56.6803 | 0.04215 | -0.013805 | -0.0010997 | 0.053166 | -0.0009947 | 0.058078 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.01258 | 0.063596 | -66.1704 | -3.4463 | -66.16 | 56.6502 | 56.4768 | 56.6877 | -66.4254 | -66.1979 | -2.9071 | -66.2553 | 56.5602 | 56.7197 | 56.6863 | -66.5891 | -0.1275 | -0.03014 | 0.12752 | 0.13793 | 0.26543 | -0.20348 | 0.007409 | -0.29114 | -0.12005 | 0.099974 | 0.042575 | 0.33371 | 0.039401 | 0.005973 | 122.9481 | 122.7747 | 122.9856 | 62.8516 | -123.1057 | 122.8582 | 123.0176 | 122.9842 | 63.3908 | -123.2693
206.2656 | 123.1384 | -66.2933 | 56.6986 | 0.057412 | -0.012737 | -0.0021677 | 0.055302 | -0.0031317 | 0.054873 | 0.042884 | -0.0025767 | -0.0020846 | 0.062109 | 0.013648 | 0.063596 | -66.1795 | -3.2998 | -66.16 | 56.6456 | 56.486 | 56.6786 | -66.4117 | -66.1934 | -2.7927 | -66.2691 | 56.5648 | 56.7151 | 56.6863 | -66.5982 | -0.11834 | -0.053028 | 0.11379 | 0.13335 | 0.25169 | -0.21264 | -0.020058 | -0.30487 | -0.13378 | 0.099974 | 0.024261 | 0.32913 | 0.016512 | -0.012337 | 122.9389 | 122.7793 | 122.9719 | 62.9936 | -123.1103 | 122.8582 | 123.0085 | 122.9796 | 63.5007 | -123.2968
207.2656 | 123.1476 | -66.3116 | 56.6666 | 0.057412 | -0.015942 | -3.1667e-05 | 0.054234 | -0.0020637 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.062109 | 0.013648 | 0.062528 | -66.1795 | -3.167 | -66.1646 | 56.641 | 56.4814 | 56.6694 | -66.4208 | -66.2025 | -2.6873 | -66.2599 | 56.5557 | 56.7105 | 56.6771 | -66.5891 | -0.10919 | -0.025563 | 0.1321 | 0.14708 | 0.25627 | -0.18517 | 0.002828 | -0.2774 | -0.1109 | 0.10913 | 0.051729 | 0.32913 | 0.043976 | 0.010549 | 122.9526 | 122.793 | 122.981 | 63.1447 | -123.0874 | 122.8673 | 123.0222 | 122.9888 | 63.6243 | -123.2556
208.2656 | 123.0927 | -66.3071 | 56.662 | 0.057412 | -0.014874 | -0.0010997 | 0.054234 | -0.0031317 | 0.05701 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.061041 | 0.015785 | 0.063596 | -66.1841 | -3.0296 | -66.1737 | 56.6364 | 56.4997 | 56.6694 | -66.4208 | -66.2025 | -2.5729 | -66.2691 | 56.5511 | 56.7105 | 56.6817 | -66.5982 | -0.11376 | -0.025564 | 0.12294 | 0.13335 | 0.24711 | -0.16228 | 0.007406 | -0.29114 | -0.1109 | 0.10455 | 0.037994 | 0.32913 | 0.048554 | 0.019706 | 122.9435 | 122.8068 | 122.9765 | 63.2774 | -123.0828 | 122.8582 | 123.0176 | 122.9888 | 63.7342 | -123.2602
209.2656 | 123.0927 | -66.3071 | 56.6711 | 0.057412 | -0.013805 | -0.0010997 | 0.054234 | -0.0031317 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.014716 | 0.062528 | -66.1795 | -2.874 | -66.1691 | 56.6456 | 56.4906 | 56.674 | -66.43 | -66.1979 | -2.4401 | -66.2782 | 56.5511 | 56.706 | 56.6817 | -66.6028 | -0.12292 | -0.025563 | 0.12752 | 0.13793 | 0.26085 | -0.18059 | 0.002828 | -0.29572 | -0.12005 | 0.10913 | 0.028836 | 0.32455 | 0.03482 | 0.01055 | 122.9526 | 122.7976 | 122.981 | 63.4331 | -123.1011 | 122.8582 | 123.013 | 122.9888 | 63.867 | -123.2739
210.2656 | 123.1155 | -66.3025 | 56.6757 | 0.04215 | -0.012737 | -0.0021677 | 0.055302 | -0.0031317 | 0.055941 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.062109 | 0.014716 | 0.063596 | -66.1933 | -2.7412 | -66.1875 | 56.6318 | 56.4814 | 56.6694 | -66.4391 | -66.2071 | -2.2982 | -66.2782 | 56.5465 | 56.706 | 56.6634 | -66.6074 | -0.13666 | -0.043875 | 0.10921 | 0.11504 | 0.25169 | -0.19433 | -0.006327 | -0.30487 | -0.12921 | 0.095393 | 0.024258 | 0.32913 | 0.030243 | -0.012342 | 122.9343 | 122.7839 | 122.9719 | 63.5613 | -123.1149 | 122.849 | 123.0085 | 122.9659 | 64.0043 | -123.2831
211.2656 | 123.1476 | -66.3345 | 56.662 | 0.04215 | -0.011668 | -0.0021677 | 0.054234 | -0.0020637 | 0.054873 | 0.058145 | 0.00062833 | 0.0011204 | 0.062109 | 0.014716 | 0.063596 | -66.1933 | -2.6359 | -66.1829 | 56.6181 | 56.4631 | 56.6602 | -66.4437 | -66.2208 | -2.1837 | -66.292 | 56.5374 | 56.6876 | 56.6588 | -66.6165 | -0.10919 | -0.043877 | 0.14125 | 0.15166 | 0.26085 | -0.19891 | -0.001752 | -0.28199 | -0.12463 | 0.1137 | 0.042566 | 0.32456 | 0.025661 | -0.003187 | 122.9526 | 122.7976 | 122.9948 | 63.6987 | -123.1057 | 122.8719 | 123.0222 | 122.9933 | 64.1508 | -123.2785
212.2656 | 123.1018 | -66.3391 | 56.6528 | 0.04215 | -0.013805 | -0.0021677 | 0.053166 | -0.0041997 | 0.05701 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.063177 | 0.013648 | 0.062528 | -66.2162 | -2.5214 | -66.2103 | 56.609 | 56.4493 | 56.6465 | -66.4529 | -66.23 | -2.0601 | -66.3057 | 56.5328 | 56.6785 | 56.6496 | -66.6211 | -0.11377 | -0.043879 | 0.12293 | 0.12877 | 0.24254 | -0.20349 | -0.006332 | -0.28199 | -0.12006 | 0.10912 | 0.033407 | 0.3154 | 0.025659 | -0.00319 | 122.9481 | 122.7885 | 122.9856 | 63.8177 | -123.1057 | 122.8719 | 123.0176 | 122.9888 | 64.2791 | -123.2739
213.2656 | 123.1018 | -66.3483 | 56.6757 | 0.04215 | -0.015942 | -0.0010997 | 0.056371 | -0.0020637 | 0.055941 | 0.058145 | -0.0015087 | -0.0010156 | 0.061041 | 0.014716 | 0.062528 | -66.2253 | -2.4069 | -66.2058 | 56.609 | 56.4356 | 56.6373 | -66.462 | -66.2391 | -1.9273 | -66.3194 | 56.5145 | 56.6693 | 56.6359 | -66.6394 | -0.11377 | -0.066767 | 0.12293 | 0.1425 | 0.25627 | -0.24012 | -0.038378 | -0.29115 | -0.16126 | 0.10912 | 0.028827 | 0.31998 | -0.006386 | -0.039813 | 122.9572 | 122.7839 | 122.9856 | 63.9413 | -123.1378 | 122.8627 | 123.0176 | 122.9842 | 64.421 | -123.3151
214.2656 | 123.111 | -66.3528 | 56.6528 | 0.04215 | -0.013805 | -0.0010997 | 0.053166 | -0.0020637 | 0.058078 | 0.058145 | -0.00043967 | 0.0011204 | 0.063177 | 0.015785 | 0.062528 | -66.2391 | -2.2513 | -66.2195 | 56.5998 | 56.431 | 56.6373 | -66.4804 | -66.2483 | -1.8128 | -66.3194 | 56.5053 | 56.6556 | 56.6405 | -66.644 | -0.12751 | -0.053036 | 0.11378 | 0.13334 | 0.26085 | -0.22181 | -0.01549 | -0.29115 | -0.14753 | 0.10454 | 0.033404 | 0.32456 | 0.002766 | -0.012347 | 122.9526 | 122.7839 | 122.9902 | 64.1016 | -123.1332 | 122.8581 | 123.0084 | 122.9933 | 64.54 | -123.2968
215.2656 | 123.1705 | -66.3574 | 56.5613 | 0.04215 | -0.014874 | -0.0021677 | 0.053166 | -0.0041997 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.015785 | 0.063596 | -66.2482 | -2.1414 | -66.247 | 56.5861 | 56.4127 | 56.6282 | -66.4941 | -66.2575 | -1.68 | -66.3378 | 56.4916 | 56.651 | 56.6222 | -66.6532 | -0.13667 | 0.024782 | 0.1092 | 0.11045 | 0.24712 | -0.14857 | 0.066906 | -0.29573 | -0.06971 | 0.099959 | 0.019667 | 0.3154 | 0.089741 | 0.060892 | 122.9435 | 122.7701 | 122.9856 | 64.216 | -123.0554 | 122.849 | 123.0084 | 122.9796 | 64.6774 | -123.2144
216.2656 | 123.1293 | -66.3712 | 56.6299 | 0.04215 | -0.015942 | -0.0010997 | 0.055302 | -0.0020637 | 0.054873 | 0.058145 | -0.0015087 | -0.0010156 | 0.062109 | 0.016853 | 0.062528 | -66.2665 | -2.0452 | -66.2607 | 56.5723 | 56.4036 | 56.6144 | -66.5078 | -66.2804 | -1.5747 | -66.3515 | 56.4824 | 56.6327 | 56.6176 | -66.676 | -0.13668 | -0.057618 | 0.10462 | 0.11045 | 0.24712 | -0.22639 | -0.015495 | -0.30489 | -0.14753 | 0.090799 | 0.019664 | 0.32456 | 0.002761 | -0.012352 | 122.9435 | 122.7747 | 122.9856 | 64.3259 | -123.1378 | 122.8536 | 123.0039 | 122.9887 | 64.7964 | -123.306
217.2656 | 123.0972 | -66.394 | 56.5933 | 0.011626 | -0.014874 | -0.0010997 | 0.053166 | -0.0020637 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.014716 | 0.063596 | -66.2574 | -1.9124 | -66.2653 | 56.5586 | 56.3898 | 56.5961 | -66.5124 | -66.2895 | -1.4374 | -66.3561 | 56.4687 | 56.6281 | 56.5947 | -66.6806 | -0.11837 | -0.034732 | 0.13666 | 0.12876 | 0.24712 | -0.20351 | 0.002812 | -0.28658 | -0.12465 | 0.10453 | 0.037973 | 0.32456 | 0.034804 | 0.001376 | 122.9526 | 122.7839 | 122.9902 | 64.4816 | -123.1057 | 122.8627 | 123.0222 | 122.9887 | 64.9567 | -123.2739
218.2656 | 123.0927 | -66.3712 | 56.5979 | 0.04215 | -0.014874 | -0.0021677 | 0.054234 | -0.0031317 | 0.055941 | 0.073406 | -0.00043967 | 0.0021894 | 0.062109 | 0.014716 | 0.062528 | -66.2849 | -1.8071 | -66.2699 | 56.5449 | 56.3807 | 56.587 | -66.517 | -66.3033 | -1.3275 | -66.3698 | 56.4595 | 56.6144 | 56.5901 | -66.6944 | -0.14583 | -0.053044 | 0.086303 | 0.10129 | 0.24712 | -0.21724 | -0.010922 | -0.32321 | -0.13838 | 0.067905 | 0.001349 | 0.32456 | 0.016491 | -0.007779 | 122.916 | 122.7518 | 122.9581 | 64.564 | -123.1149 | 122.8307 | 122.9855 | 122.9613 | 65.0437 | -123.2923
219.2656 | 123.1659 | -66.3666 | 56.5887 | 0.026888 | -0.013805 | -0.0021677 | 0.054234 | -0.0041997 | 0.058078 | 0.058145 | -0.0015087 | 0.0021894 | 0.059972 | 0.013648 | 0.062528 | -66.2986 | -1.6652 | -66.279 | 56.5494 | 56.3715 | 56.5778 | -66.5399 | -66.3124 | -1.2084 | -66.3835 | 56.4641 | 56.6052 | 56.5764 | -66.7035 | -0.17331 | -0.039311 | 0.06799 | 0.087557 | 0.26086 | -0.21725 | -0.010924 | -0.33694 | -0.12465 | 0.05417 | -0.016965 | 0.31998 | 0.016489 | -0.01236 | 122.916 | 122.7381 | 122.9444 | 64.7014 | -123.1286 | 122.8307 | 122.9718 | 122.943 | 65.1582 | -123.2923
220.2656 | 123.3353 | -66.4261 | 56.5887 | 0.026888 | -0.01701 | -0.0010997 | 0.053166 | -0.0031317 | 0.05701 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.063177 | 0.014716 | 0.063596 | -66.3123 | -1.537 | -66.3019 | 56.5357 | 56.3623 | 56.5641 | -66.5399 | -66.3261 | -1.0802 | -66.4019 | 56.4412 | 56.5961 | 56.5672 | -66.7081 | -0.1138 | -0.053046 | 0.11376 | 0.12417 | 0.23797 | -0.2264 | -0.02466 | -0.28201 | -0.14754 | 0.099943 | 0.024229 | 0.30624 | 0.007331 | -0.021517 | 122.9618 | 122.7884 | 122.9902 | 64.8891 | -123.1286 | 122.8673 | 123.0222 | 122.9933 | 65.3459 | -123.2968
221.2656 | 123.0835 | -66.4444 | 56.5475 | 0.04215 | -0.013805 | -3.1667e-05 | 0.054234 | -0.0041997 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.061041 | 0.014716 | 0.06146 | -66.3261 | -1.4088 | -66.3111 | 56.5265 | 56.344 | 56.5549 | -66.549 | -66.3445 | -0.9978 | -66.411 | 56.432 | 56.5732 | 56.5626 | -66.7218 | -0.10465 | -0.021004 | 0.11834 | 0.13333 | 0.23797 | -0.20352 | 0.007382 | -0.27744 | -0.1155 | 0.099939 | 0.033383 | 0.31082 | 0.025637 | 0.015103 | 122.9709 | 122.7884 | 122.9993 | 65.0356 | -123.0966 | 122.8764 | 123.0176 | 123.007 | 65.4466 | -123.2694
222.2656 | 123.1705 | -66.4215 | 56.5109 | 0.057412 | -0.014874 | -3.1667e-05 | 0.057439 | -0.0031317 | 0.05701 | 0.073406 | -0.00043967 | -0.0010156 | 0.063177 | 0.013648 | 0.063596 | -66.3444 | -1.2989 | -66.3294 | 56.5174 | 56.3394 | 56.5458 | -66.5719 | -66.3628 | -0.90165 | -66.4156 | 56.4183 | 56.5732 | 56.5443 | -66.7402 | -0.15043 | 0.00646 | 0.077138 | 0.092128 | 0.24255 | -0.17148 | 0.034845 | -0.31864 | -0.092612 | 0.058736 | 0.005916 | 0.32456 | 0.062258 | 0.03341 | 122.9389 | 122.761 | 122.9673 | 65.1226 | -123.0829 | 122.8398 | 122.9947 | 122.9658 | 65.5199 | -123.2511
223.2656 | 123.1476 | -66.4352 | 56.5567 | 0.057412 | -0.015942 | -0.0010997 | 0.053166 | -0.0031317 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.015785 | 0.063596 | -66.3581 | -1.2119 | -66.3385 | 56.5037 | 56.3257 | 56.5366 | -66.5765 | -66.3765 | -0.80092 | -66.4431 | 56.4092 | 56.5549 | 56.5352 | -66.7493 | -0.14127 | -0.053052 | 0.077136 | 0.096704 | 0.23798 | -0.23099 | -0.020089 | -0.31407 | -0.14755 | 0.058733 | -0.007823 | 0.30624 | -0.001833 | -0.021525 | 122.9389 | 122.761 | 122.9719 | 65.2233 | -123.1332 | 122.8444 | 122.9901 | 122.9704 | 65.6343 | -123.306
224.2656 | 123.1018 | -66.4764 | 56.5201 | 0.026888 | -0.013805 | -0.0010997 | 0.054234 | -0.0031317 | 0.059146 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.015785 | 0.062528 | -66.3764 | -1.1249 | -66.3477 | 56.4899 | 56.312 | 56.532 | -66.5948 | -66.3902 | -0.72308 | -66.4476 | 56.3954 | 56.5457 | 56.526 | -66.763 | -0.11839 | -0.030166 | 0.10002 | 0.12875 | 0.24714 | -0.20811 | 0.011954 | -0.28661 | -0.12466 | 0.086195 | 0.028796 | 0.3154 | 0.025631 | 0.005939 | 122.9664 | 122.7884 | 123.0085 | 65.3515 | -123.1149 | 122.8719 | 123.0222 | 123.0025 | 65.7534 | -123.2831
225.2656 | 123.1201 | -66.4719 | 56.5155 | 0.04215 | -0.015942 | -0.0010997 | 0.054234 | -0.0041997 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.063177 | 0.014716 | 0.062528 | -66.381 | -1.0425 | -66.366 | 56.4808 | 56.2982 | 56.5137 | -66.6086 | -66.3948 | -0.64066 | -66.4614 | 56.3817 | 56.5366 | 56.5077 | -66.7814 | -0.13671 | -0.034745 | 0.090865 | 0.10586 | 0.24256 | -0.21727 | -0.001783 | -0.3095 | -0.13382 | 0.077039 | 0.010483 | 0.31998 | 0.021052 | -0.007797 | 122.9526 | 122.7701 | 122.9856 | 65.4293 | -123.1241 | 122.8535 | 123.0084 | 122.9796 | 65.8312 | -123.2969
226.2656 | 123.0972 | -66.481 | 56.4926 | 0.057412 | -0.014874 | -0.0010997 | 0.053166 | -0.0041997 | 0.054873 | 0.088667 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.013648 | 0.062528 | -66.3902 | -0.96926 | -66.3752 | 56.4579 | 56.2937 | 56.5 | -66.5994 | -66.4086 | -0.5674 | -66.4705 | 56.3725 | 56.532 | 56.4985 | -66.7768 | -0.11839 | -0.034749 | 0.090863 | 0.10585 | 0.22425 | -0.19896 | 0.007369 | -0.29576 | -0.12009 | 0.072458 | 0.01048 | 0.30624 | 0.039361 | 0.005934 | 122.9389 | 122.7747 | 122.981 | 65.5118 | -123.092 | 122.8535 | 123.013 | 122.9796 | 65.9136 | -123.2694
227.2656 | 123.1659 | -66.4856 | 56.4743 | 0.04215 | -0.015942 | -0.0032367 | 0.056371 | -0.0041997 | 0.053805 | 0.058145 | -0.00043967 | 0.0011204 | 0.063177 | 0.017921 | 0.06146 | -66.4039 | -0.89142 | -66.3889 | 56.4441 | 56.3074 | 56.4908 | -66.6086 | -66.4177 | -0.51704 | -66.4889 | 56.3679 | 56.5137 | 56.4848 | -66.7905 | -0.12297 | -0.030173 | 0.081706 | 0.096697 | 0.21967 | -0.16691 | 0.016523 | -0.30492 | -0.10635 | 0.067878 | -0.003256 | 0.30167 | 0.039358 | 0.010509 | 122.9297 | 122.793 | 122.9764 | 65.5942 | -123.0829 | 122.8535 | 122.9993 | 122.9704 | 65.9686 | -123.2648
228.2656 | 123.1476 | -66.5222 | 56.4743 | 0.026888 | -0.014874 | -0.0021677 | 0.056371 | -0.0041997 | 0.05701 | 0.058145 | 0.00062833 | -0.0010156 | 0.062109 | 0.016853 | 0.063596 | -66.413 | -0.81359 | -66.3935 | 56.435 | 56.3532 | 56.4725 | -66.6269 | -66.436 | -0.44378 | -66.4889 | 56.3542 | 56.5045 | 56.4757 | -66.7997 | -0.10467 | -0.03933 | 0.10917 | 0.12874 | 0.23341 | -0.12112 | -0.001791 | -0.27746 | -0.12009 | 0.086185 | 0.033365 | 0.31082 | 0.0302 | 0.001352 | 122.9572 | 122.8754 | 122.9947 | 65.7086 | -123.1012 | 122.8764 | 123.0267 | 122.9979 | 66.0784 | -123.274
229.2656 | 123.1247 | -66.4948 | 56.4789 | 0.057412 | -0.014874 | -0.0021677 | 0.055302 | -0.0052687 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.061041 | 0.015785 | 0.063596 | -66.4268 | -0.74948 | -66.4118 | 56.4304 | 56.2982 | 56.4725 | -66.6406 | -66.4498 | -0.39799 | -66.5072 | 56.3405 | 56.5045 | 56.4665 | -66.8043 | -0.14587 | -0.048486 | 0.067969 | 0.082961 | 0.22883 | -0.18065 | -0.006369 | -0.3095 | -0.1384 | 0.044982 | -0.012416 | 0.29709 | 0.025622 | -0.012384 | 122.9251 | 122.793 | 122.9673 | 65.7453 | -123.1195 | 122.8352 | 122.9993 | 122.9612 | 66.0968 | -123.2831
230.2656 | 123.1201 | -66.5176 | 56.4056 | 0.057412 | -0.015942 | -0.0021677 | 0.055302 | -0.0041997 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.015785 | 0.06146 | -66.4405 | -0.68996 | -66.4255 | 56.4212 | 56.312 | 56.4588 | -66.6452 | -66.4543 | -0.3522 | -66.5209 | 56.3313 | 56.4862 | 56.4528 | -66.8271 | -0.12756 | 0.015599 | 0.077122 | 0.092114 | 0.21967 | -0.093667 | 0.053137 | -0.30951 | -0.074319 | 0.063292 | -0.003264 | 0.30624 | 0.08055 | 0.047122 | 122.9389 | 122.8296 | 122.9764 | 65.8277 | -123.0508 | 122.849 | 123.0038 | 122.9704 | 66.1654 | -123.2328
231.2656 | 123.111 | -66.5314 | 56.4377 | 0.04215 | -0.014874 | -0.0021677 | 0.055302 | -0.0031317 | 0.05701 | 0.042884 | 0.00062833 | 5.2373e-05 | 0.062109 | 0.015785 | 0.060391 | -66.4497 | -0.62586 | -66.4347 | 56.4167 | 56.312 | 56.4496 | -66.6498 | -66.4589 | -0.32473 | -66.5301 | 56.3267 | 56.4816 | 56.4482 | -66.8226 | -0.11841 | -0.021022 | 0.081698 | 0.09669 | 0.2151 | -0.12571 | 0.011937 | -0.2912 | -0.11094 | 0.072446 | 0.001311 | 0.29251 | 0.043928 | 0.010501 | 122.948 | 122.8433 | 122.981 | 65.9055 | -123.0875 | 122.8581 | 123.013 | 122.9796 | 66.2066 | -123.2603
232.2656 | 123.1293 | -66.5588 | 56.4606 | 0.026888 | -0.015942 | -0.0021677 | 0.054234 | -0.0041997 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.016853 | 0.062528 | -66.4634 | -0.56634 | -66.4393 | 56.4029 | 56.3211 | 56.4405 | -66.6635 | -66.4727 | -0.29726 | -66.5346 | 56.3222 | 56.4679 | 56.4344 | -66.8363 | -0.10468 | -0.057646 | 0.095429 | 0.11958 | 0.22425 | -0.13944 | -0.020108 | -0.27747 | -0.13841 | 0.086176 | 0.024199 | 0.30167 | 0.007305 | -0.026123 | 122.9618 | 122.88 | 122.9993 | 65.9925 | -123.1241 | 122.881 | 123.0267 | 122.9933 | 66.2616 | -123.2969
233.2656 | 123.0927 | -66.5405 | 56.4423 | 0.057412 | -0.015942 | -0.0021677 | 0.055302 | -0.0052687 | 0.055941 | 0.058145 | -0.0015087 | -0.0010156 | 0.062109 | 0.015785 | 0.062528 | -66.468 | -0.50682 | -66.4484 | 56.3938 | 56.3074 | 56.4267 | -66.6635 | -66.4864 | -0.25147 | -66.5484 | 56.3084 | 56.4587 | 56.4344 | -66.8455 | -0.12299 | -0.048492 | 0.07254 | 0.09211 | 0.2151 | -0.13487 | -0.015534 | -0.30494 | -0.13383 | 0.054129 | -0.007849 | 0.29709 | 0.016457 | -0.007813 | 122.9343 | 122.8479 | 122.9673 | 66.0337 | -123.1058 | 122.849 | 122.9992 | 122.975 | 66.2891 | -123.2877
234.2656 | 123.1201 | -66.5405 | 56.4239 | 0.026888 | -0.014874 | -0.0010997 | 0.054234 | -0.0041997 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.016853 | 0.06146 | -66.4863 | -0.47477 | -66.4576 | 56.3846 | 56.2982 | 56.4221 | -66.6727 | -66.491 | -0.24231 | -66.553 | 56.2901 | 56.4633 | 56.4161 | -66.8592 | -0.13215 | -0.039338 | 0.054226 | 0.082954 | 0.2151 | -0.12571 | -0.001802 | -0.31867 | -0.13383 | 0.04955 | -0.012427 | 0.30625 | 0.039347 | -0.007816 | 122.9251 | 122.8388 | 122.9627 | 66.0658 | -123.0966 | 122.8306 | 123.0038 | 122.9567 | 66.2982 | -123.2832
235.2656 | 123.1247 | -66.5588 | 56.4194 | 0.04215 | -0.01701 | -0.0021677 | 0.053166 | -0.0020637 | 0.055941 | 0.073406 | -0.0015087 | 0.0011204 | 0.061041 | 0.015785 | 0.062528 | -66.4909 | -0.43356 | -66.4713 | 56.3709 | 56.2799 | 56.413 | -66.6864 | -66.5093 | -0.23316 | -66.5621 | 56.2947 | 56.445 | 56.407 | -66.8638 | -0.12757 | -0.048496 | 0.067959 | 0.08753 | 0.2151 | -0.13945 | -0.006382 | -0.30494 | -0.12468 | 0.049546 | -0.003274 | 0.30167 | 0.02561 | -0.012397 | 122.9297 | 122.8388 | 122.9718 | 66.1253 | -123.1058 | 122.8535 | 123.0038 | 122.9658 | 66.3257 | -123.2832
236.2656 | 123.0286 | -66.568 | 56.3736 | 0.04215 | -0.01701 | -0.0010997 | 0.055302 | -0.0041997 | 0.055941 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.061041 | 0.017921 | 0.063596 | -66.5 | -0.40609 | -66.4759 | 56.3709 | 56.2753 | 56.4038 | -66.6818 | -66.5093 | -0.21026 | -66.5713 | 56.2855 | 56.4312 | 56.4024 | -66.8684 | -0.11384 | -0.002719 | 0.067957 | 0.092107 | 0.20594 | -0.098254 | 0.030238 | -0.30036 | -0.08806 | 0.058701 | -0.003276 | 0.29709 | 0.057651 | 0.028802 | 122.9389 | 122.8433 | 122.9718 | 66.1619 | -123.0554 | 122.8535 | 122.9992 | 122.9704 | 66.3577 | -123.242
237.2656 | 123.111 | -66.5726 | 56.4239 | 0.04215 | -0.01701 | -0.0010997 | 0.054234 | -0.0031317 | 0.05701 | 0.042884 | -0.00043967 | 0.0011204 | 0.063177 | 0.015785 | 0.06146 | -66.5 | -0.37862 | -66.4805 | 56.3663 | 56.2753 | 56.3947 | -66.7001 | -66.5139 | -0.20568 | -66.5758 | 56.2718 | 56.4267 | 56.3978 | -66.8821 | -0.12758 | -0.057652 | 0.072535 | 0.092106 | 0.21968 | -0.14861 | -0.029273 | -0.30952 | -0.15215 | 0.058701 | -0.003277 | 0.30625 | 0.002718 | -0.026131 | 122.9389 | 122.8479 | 122.9672 | 66.194 | -123.1241 | 122.8444 | 122.9992 | 122.9704 | 66.3669 | -123.306
238.2656 | 123.1018 | -66.5863 | 56.3782 | 0.057412 | -0.015942 | -0.0021677 | 0.053166 | -0.0031317 | 0.05701 | 0.042884 | 0.0016963 | 5.2373e-05 | 0.061041 | 0.015785 | 0.062528 | -66.5092 | -0.34657 | -66.4942 | 56.3526 | 56.2662 | 56.3901 | -66.6956 | -66.523 | -0.2011 | -66.5758 | 56.2764 | 56.4312 | 56.3887 | -66.8821 | -0.10926 | -0.025611 | 0.077111 | 0.092105 | 0.20137 | -0.11199 | 0.011924 | -0.29579 | -0.1018 | 0.063276 | 0.010456 | 0.30625 | 0.053073 | 0.010488 | 122.9389 | 122.8525 | 122.9764 | 66.2397 | -123.0737 | 122.8627 | 123.0176 | 122.975 | 66.3852 | -123.2603
239.2656 | 123.143 | -66.5771 | 56.4194 | 0.057412 | -0.018079 | -0.0032367 | 0.055302 | -0.0041997 | 0.054873 | 0.058145 | -0.0015087 | -0.0020846 | 0.061041 | 0.015785 | 0.062528 | -66.5046 | -0.33283 | -66.5034 | 56.3571 | 56.2616 | 56.3855 | -66.7047 | -66.5368 | -0.2011 | -66.585 | 56.2718 | 56.4221 | 56.3932 | -66.8821 | -0.12758 | -0.062231 | 0.072533 | 0.073792 | 0.20137 | -0.15777 | -0.033854 | -0.30495 | -0.14757 | 0.040384 | -0.007857 | 0.29709 | 0.002717 | -0.026132 | 122.9343 | 122.8388 | 122.9627 | 66.2443 | -123.1241 | 122.8489 | 122.9992 | 122.9704 | 66.376 | -123.3015
240.2656 | 123.1247 | -66.568 | 56.369 | 0.072674 | -0.01701 | -0.0021677 | 0.054234 | -0.0031317 | 0.055941 | 0.073406 | -0.00043967 | -0.0010156 | 0.062109 | 0.01899 | 0.06146 | -66.5275 | -0.30994 | -66.5125 | 56.3526 | 56.2753 | 56.3809 | -66.7139 | -66.5368 | -0.2011 | -66.5987 | 56.2672 | 56.4175 | 56.3841 | -66.8958 | -0.14589 | -0.016456 | 0.040487 | 0.05548 | 0.20137 | -0.093677 | 0.011922 | -0.32784 | -0.1018 | 0.031229 | -0.030748 | 0.29709 | 0.048492 | 0.015064 | 122.9206 | 122.8433 | 122.9489 | 66.2581 | -123.0829 | 122.8352 | 122.9855 | 122.9521 | 66.3669 | -123.2648
241.2656 | 123.0835 | -66.6092 | 56.3782 | 0.026888 | -0.01701 | -0.0021677 | 0.056371 | -0.0031317 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.063177 | 0.016853 | 0.062528 | -66.5229 | -0.29162 | -66.5079 | 56.348 | 56.2616 | 56.3855 | -66.7139 | -66.5459 | -0.19195 | -66.5987 | 56.2626 | 56.4175 | 56.3841 | -66.8913 | -0.10469 | -0.030189 | 0.086264 | 0.10126 | 0.20595 | -0.11657 | 0.007345 | -0.28206 | -0.11553 | 0.063271 | 0.010451 | 0.29251 | 0.039337 | 0.005909 | 122.9572 | 122.8708 | 122.9947 | 66.3176 | -123.0921 | 122.8718 | 123.0267 | 122.9933 | 66.4172 | -123.2694
242.2656 | 123.1338 | -66.5771 | 56.3873 | 0.04215 | -0.01701 | -0.0021677 | 0.054234 | -0.0041997 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.017921 | 0.063596 | -66.5275 | -0.28247 | -66.5171 | 56.348 | 56.2616 | 56.3809 | -66.7185 | -66.5368 | -0.19195 | -66.6079 | 56.2535 | 56.4129 | 56.3841 | -66.905 | -0.14131 | -0.039344 | 0.049642 | 0.060057 | 0.20137 | -0.12572 | -0.006388 | -0.32784 | -0.13384 | 0.040384 | -0.030751 | 0.29709 | 0.025603 | -0.003246 | 122.9251 | 122.8388 | 122.9581 | 66.2947 | -123.1058 | 122.8306 | 122.9901 | 122.9612 | 66.3852 | -123.2923
243.2656 | 123.1796 | -66.5863 | 56.3965 | 0.04215 | -0.019147 | -0.0021677 | 0.054234 | -0.0041997 | 0.055941 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.062109 | 0.01899 | 0.063596 | -66.5321 | -0.27789 | -66.5125 | 56.348 | 56.2662 | 56.3855 | -66.7139 | -66.5322 | -0.19653 | -66.6125 | 56.2626 | 56.4084 | 56.3795 | -66.905 | -0.12758 | -0.048499 | 0.054219 | 0.073791 | 0.20137 | -0.1303 | -0.010965 | -0.31868 | -0.13384 | 0.054119 | -0.026174 | 0.29251 | 0.01187 | -0.016979 | 122.9343 | 122.8525 | 122.9718 | 66.3084 | -123.1104 | 122.8489 | 122.9947 | 122.9658 | 66.3898 | -123.3015
244.2656 | 123.2025 | -66.5771 | 56.3782 | 0.057412 | -0.01701 | -0.0021677 | 0.053166 | -0.0031317 | 0.052737 | 0.058145 | -0.0015087 | 0.0011204 | 0.059972 | 0.017921 | 0.063596 | -66.5367 | -0.26873 | -66.5262 | 56.3388 | 56.257 | 56.3764 | -66.723 | -66.5505 | -0.18737 | -66.6033 | 56.2626 | 56.4084 | 56.3749 | -66.905 | -0.14589 | -0.039346 | 0.040485 | 0.050901 | 0.19679 | -0.12115 | -0.001812 | -0.32784 | -0.11553 | 0.026648 | -0.026172 | 0.30167 | 0.03018 | -0.003248 | 122.916 | 122.8342 | 122.9535 | 66.3084 | -123.1012 | 122.8398 | 122.9855 | 122.9521 | 66.3898 | -123.2832
245.2656 | 123.1384 | -66.5909 | 56.3828 | 0.04215 | -0.01701 | -0.0032367 | 0.054234 | -0.0031317 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.016853 | 0.064664 | -66.5458 | -0.255 | -66.5217 | 56.348 | 56.2524 | 56.3809 | -66.7276 | -66.5642 | -0.18737 | -66.6171 | 56.2581 | 56.4038 | 56.3795 | -66.9096 | -0.13674 | -0.034766 | 0.045061 | 0.069212 | 0.20595 | -0.1303 | -0.00181 | -0.31869 | -0.12469 | 0.026645 | -0.026175 | 0.29251 | 0.021024 | -0.003246 | 122.9389 | 122.8433 | 122.9718 | 66.3359 | -123.1104 | 122.8489 | 122.9947 | 122.9704 | 66.4035 | -123.2923
246.2656 | 123.1796 | -66.5771 | 56.3736 | 0.057412 | -0.01701 | -0.0021677 | 0.055302 | -0.0041997 | 0.055941 | 0.058145 | -0.00043967 | -0.0010156 | 0.061041 | 0.016853 | 0.062528 | -66.5458 | -0.24584 | -66.5308 | 56.3297 | 56.257 | 56.3809 | -66.7276 | -66.5688 | -0.19195 | -66.6171 | 56.2535 | 56.4038 | 56.3703 | -66.905 | -0.15047 | -0.043925 | 0.031328 | 0.046322 | 0.19679 | -0.11657 | 0.007345 | -0.32784 | -0.12011 | 0.008333 | -0.039908 | 0.28793 | 0.030179 | -0.003248 | 122.9068 | 122.8342 | 122.9581 | 66.3313 | -123.1012 | 122.8306 | 122.9809 | 122.9475 | 66.3852 | -123.2786
247.2656 | 123.1842 | -66.5863 | 56.3644 | 0.057412 | -0.01701 | -3.1667e-05 | 0.054234 | -0.0052687 | 0.054873 | 0.058145 | -0.00043967 | -0.0010156 | 0.063177 | 0.016853 | 0.062528 | -66.555 | -0.23668 | -66.54 | 56.3388 | 56.2524 | 56.3764 | -66.7322 | -66.5597 | -0.18279 | -66.6262 | 56.2489 | 56.3992 | 56.3749 | -66.905 | -0.14589 | -0.025613 | 0.031327 | 0.046322 | 0.19222 | -0.11199 | 0.011921 | -0.31868 | -0.11553 | 0.026646 | -0.03991 | 0.27877 | 0.034756 | 0.010485 | 122.9251 | 122.8388 | 122.9627 | 66.3496 | -123.0966 | 122.8352 | 122.9855 | 122.9612 | 66.4035 | -123.2694
248.2656 | 123.1476 | -66.6092 | 56.3599 | 0.057412 | -0.018079 | -0.0010997 | 0.055302 | -0.0041997 | 0.055941 | 0.073406 | -0.0015087 | -0.0010156 | 0.063177 | 0.016853 | 0.06146 | -66.5504 | -0.2321 | -66.5354 | 56.3251 | 56.2433 | 56.3672 | -66.7276 | -66.5642 | -0.17363 | -66.6216 | 56.2489 | 56.3946 | 56.3658 | -66.9187 | -0.11843 | -0.03477 | 0.058794 | 0.073788 | 0.19222 | -0.11657 | 0.007342 | -0.30953 | -0.11095 | 0.044956 | -0.012443 | 0.29709 | 0.034755 | 0.005906 | 122.9343 | 122.8525 | 122.9764 | 66.3771 | -123.0875 | 122.8581 | 123.0038 | 122.975 | 66.4356 | -123.2786
249.2656 | 123.1476 | -66.5909 | 56.3599 | 0.057412 | -0.019147 | -0.0021677 | 0.054234 | -0.0031317 | 0.05701 | 0.088667 | -0.00043967 | 0.0011204 | 0.062109 | 0.016853 | 0.063596 | -66.5504 | -0.22752 | -66.5308 | 56.3297 | 56.2433 | 56.3764 | -66.7368 | -66.5642 | -0.16905 | -66.6308 | 56.2398 | 56.4038 | 56.3658 | -66.9096 | -0.1459 | -0.030192 | 0.040483 | 0.060055 | 0.20595 | -0.11657 | 0.016499 | -0.31869 | -0.12011 | 0.026645 | -0.039911 | 0.27877 | 0.043912 | 0.005906 | 122.9206 | 122.8342 | 122.9672 | 66.3634 | -123.0966 | 122.8306 | 122.9947 | 122.9566 | 66.4218 | -123.2694
250.2656 | 123.1888 | -66.5909 | 56.3599 | 0.057412 | -0.019147 | -0.0021677 | 0.053166 | -0.0041997 | 0.05701 | 0.073406 | -0.0025767 | 0.0011204 | 0.061041 | 0.016853 | 0.063596 | -66.555 | -0.21379 | -66.54 | 56.3297 | 56.2433 | 56.3626 | -66.7368 | -66.5734 | -0.17821 | -66.6262 | 56.2489 | 56.4038 | 56.3658 | -66.9141 | -0.1459 | -0.030192 | 0.035904 | 0.050899 | 0.1968 | -0.11657 | 0.002763 | -0.32327 | -0.11095 | 0.017487 | -0.035333 | 0.28793 | 0.043912 | 0.005906 | 122.9206 | 122.8342 | 122.9535 | 66.3771 | -123.0966 | 122.8398 | 122.9947 | 122.9566 | 66.4127 | -123.274
251.2656 | 123.1567 | -66.5771 | 56.3873 | 0.057412 | -0.018079 | -0.0010997 | 0.055302 | -0.0041997 | 0.055941 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.059972 | 0.016853 | 0.063596 | -66.5504 | -0.21379 | -66.5354 | 56.3205 | 56.2387 | 56.3626 | -66.7414 | -66.5688 | -0.16448 | -66.6308 | 56.2443 | 56.3946 | 56.3658 | -66.9187 | -0.16421 | -0.066815 | 0.02675 | 0.041744 | 0.20595 | -0.14862 | -0.024703 | -0.34158 | -0.143 | 0.008333 | -0.053644 | 0.28793 | 0.007289 | -0.02156 | 122.8977 | 122.8159 | 122.9398 | 66.3634 | -123.1287 | 122.8215 | 122.9718 | 122.9429 | 66.4127 | -123.3061
252.2656 | 123.1934 | -66.5817 | 56.3324 | 0.04215 | -0.018079 | -0.0032367 | 0.053166 | -0.0041997 | 0.054873 | 0.042884 | 0.00062833 | 5.2373e-05 | 0.062109 | 0.016853 | 0.062528 | -66.5641 | -0.20463 | -66.54 | 56.3388 | 56.225 | 56.3626 | -66.7322 | -66.578 | -0.1599 | -66.6354 | 56.2535 | 56.3946 | 56.352 | -66.9233 | -0.15047 | 0.006431 | 0.017592 | 0.041744 | 0.19222 | -0.10742 | 0.030229 | -0.34158 | -0.07891 | 0.003754 | -0.053645 | 0.28793 | 0.062221 | 0.019636 | 122.9206 | 122.8067 | 122.9444 | 66.3771 | -123.0646 | 122.8352 | 122.9763 | 122.9338 | 66.4218 | -123.2557
253.2656 | 123.1659 | -66.5817 | 56.369 | 0.057412 | -0.018079 | -0.0010997 | 0.055302 | -0.0041997 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.017921 | 0.06146 | -66.5596 | -0.20005 | -66.5491 | 56.3297 | 56.225 | 56.3672 | -66.7368 | -66.578 | -0.1599 | -66.6262 | 56.2443 | 56.3992 | 56.3658 | -66.9187 | -0.15505 | -0.039348 | 0.022171 | 0.032587 | 0.18764 | -0.14405 | -0.001814 | -0.337 | -0.12469 | 0.003754 | -0.044488 | 0.29251 | 0.030178 | -0.00325 | 122.9114 | 122.8067 | 122.9489 | 66.3817 | -123.1058 | 122.8261 | 122.9809 | 122.9475 | 66.4218 | -123.2877
254.2656 | 123.1567 | -66.5817 | 56.3736 | 0.072674 | -0.018079 | -0.0032367 | 0.053166 | -0.0052687 | 0.054873 | 0.058145 | -0.0025767 | -0.0010156 | 0.061041 | 0.017921 | 0.06146 | -66.5641 | -0.20005 | -66.54 | 56.3205 | 56.225 | 56.3718 | -66.7414 | -66.5826 | -0.16448 | -66.6308 | 56.2398 | 56.3946 | 56.3566 | -66.9141 | -0.15963 | -0.053082 | 0.017592 | 0.041744 | 0.20137 | -0.14862 | -0.001812 | -0.33242 | -0.13385 | -0.000825 | -0.049066 | 0.28335 | 0.021022 | -0.016984 | 122.9022 | 122.8067 | 122.9535 | 66.3817 | -123.115 | 122.8215 | 122.9763 | 122.9383 | 66.4173 | -123.2877
255.2656 | 123.1705 | -66.5955 | 56.3599 | 0.026888 | -0.019147 | -0.0021677 | 0.054234 | -0.0041997 | 0.054873 | 0.073406 | 0.00062833 | -0.0010156 | 0.062109 | 0.020058 | 0.062528 | -66.5641 | -0.19547 | -66.5446 | 56.3251 | 56.225 | 56.358 | -66.7368 | -66.5826 | -0.16905 | -66.6354 | 56.2443 | 56.3946 | 56.352 | -66.9096 | -0.14132 | -0.03477 | 0.031325 | 0.050899 | 0.19222 | -0.13489 | -0.001815 | -0.31411 | -0.11553 | 0.012908 | -0.039912 | 0.2742 | 0.034755 | -0.00783 | 122.9206 | 122.8204 | 122.9535 | 66.4 | -123.0966 | 122.8398 | 122.9901 | 122.9475 | 66.4264 | -123.2694
256.2656 | 123.1613 | -66.5955 | 56.3782 | 0.087936 | -0.018079 | -0.0021677 | 0.054234 | -0.0031317 | 0.053805 | 0.042884 | -0.00043967 | 0.0011204 | 0.063177 | 0.017921 | 0.063596 | -66.5687 | -0.18632 | -66.5491 | 56.3297 | 56.2112 | 56.3718 | -66.7414 | -66.5826 | -0.16905 | -66.6354 | 56.2398 | 56.3946 | 56.3612 | -66.9279 | -0.1459 | -0.048503 | 0.026747 | 0.04632 | 0.19222 | -0.16694 | -0.00639 | -0.33242 | -0.13842 | 0.012908 | -0.039912 | 0.29251 | 0.016444 | -0.016984 | 122.9251 | 122.8067 | 122.9672 | 66.4091 | -123.1195 | 122.8352 | 122.9901 | 122.9566 | 66.4264 | -123.3061
257.2656 | 123.1476 | -66.5955 | 56.3644 | 0.04215 | -0.018079 | -0.0021677 | 0.054234 | -0.0041997 | 0.055941 | 0.088667 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.020058 | 0.062528 | -66.5641 | -0.19547 | -66.5537 | 56.3205 | 56.225 | 56.3672 | -66.7368 | -66.578 | -0.1599 | -66.6399 | 56.2352 | 56.3946 | 56.3566 | -66.9233 | -0.14132 | -0.043927 | 0.031325 | 0.041742 | 0.18306 | -0.13947 | 0.002764 | -0.32784 | -0.12927 | 0.017487 | -0.044491 | 0.28335 | 0.030177 | -0.007829 | 122.916 | 122.8204 | 122.9627 | 66.4 | -123.1012 | 122.8306 | 122.9901 | 122.9521 | 66.4356 | -123.2877
258.2656 | 123.1934 | -66.5726 | 56.369 | 0.057412 | -0.018079 | -0.0021677 | 0.053166 | -0.0041997 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.061041 | 0.01899 | 0.063596 | -66.5641 | -0.18174 | -66.5491 | 56.3205 | 56.2112 | 56.358 | -66.7414 | -66.5871 | -0.16448 | -66.6445 | 56.2398 | 56.39 | 56.352 | -66.9233 | -0.16878 | -0.048505 | 0.008437 | 0.023432 | 0.19222 | -0.15778 | -0.010971 | -0.35073 | -0.12927 | -0.014559 | -0.071958 | 0.27877 | 0.02102 | -0.016986 | 122.8931 | 122.7838 | 122.9306 | 66.3908 | -123.1104 | 122.8123 | 122.9626 | 122.9246 | 66.4081 | -123.2923
259.2656 | 123.2208 | -66.5817 | 56.3828 | 0.057412 | -0.019147 | -0.0021677 | 0.055302 | -0.0020637 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.01899 | 0.063596 | -66.5733 | -0.17258 | -66.5583 | 56.3251 | 56.2158 | 56.3626 | -66.7459 | -66.5826 | -0.15532 | -66.6491 | 56.2306 | 56.3855 | 56.352 | -66.9187 | -0.16421 | -0.057658 | 0.008436 | 0.023431 | 0.18764 | -0.16694 | -0.020125 | -0.337 | -0.15216 | -0.000825 | -0.067381 | 0.26962 | 0.00271 | -0.030718 | 122.9068 | 122.7975 | 122.9444 | 66.4091 | -123.1287 | 122.8123 | 122.9672 | 122.9338 | 66.4264 | -123.3015
260.2656 | 123.1888 | -66.6 | 56.3919 | 0.04215 | -0.021284 | -0.0010997 | 0.054234 | -0.0031317 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.059972 | 0.01899 | 0.063596 | -66.5641 | -0.168 | -66.5491 | 56.3205 | 56.2112 | 56.358 | -66.7276 | -66.5826 | -0.16448 | -66.6399 | 56.2443 | 56.3946 | 56.3566 | -66.9187 | -0.12758 | -0.071393 | 0.035903 | 0.050898 | 0.17848 | -0.18067 | -0.033859 | -0.31869 | -0.14758 | 0.017486 | -0.039913 | 0.27877 | 0.002711 | -0.035295 | 122.9206 | 122.8113 | 122.9581 | 66.432 | -123.1195 | 122.8444 | 122.9947 | 122.9566 | 66.4356 | -123.3106
261.2656 | 123.175 | -66.6092 | 56.369 | 0.026888 | -0.019147 | -0.0021677 | 0.054234 | -0.0052687 | 0.053805 | 0.073406 | -0.00043967 | 0.0011204 | 0.062109 | 0.01899 | 0.063596 | -66.5733 | -0.15427 | -66.5583 | 56.3205 | 56.1929 | 56.3626 | -66.7322 | -66.5826 | -0.1599 | -66.6445 | 56.2306 | 56.3946 | 56.3475 | -66.9141 | -0.12301 | -0.048505 | 0.035902 | 0.050897 | 0.1739 | -0.1761 | -0.006393 | -0.30495 | -0.13842 | 0.026641 | -0.035337 | 0.26962 | 0.025599 | -0.021564 | 122.9297 | 122.8021 | 122.9718 | 66.4549 | -123.1012 | 122.8398 | 123.0038 | 122.9566 | 66.4493 | -123.2832
262.2656 | 123.1613 | -66.568 | 56.3782 | 0.057412 | -0.020215 | -0.0032367 | 0.056371 | -0.0041997 | 0.054873 | 0.073406 | -0.0036447 | -0.0010156 | 0.061041 | 0.01899 | 0.063596 | -66.5733 | -0.15884 | -66.5537 | 56.3251 | 56.1654 | 56.358 | -66.7322 | -66.5871 | -0.15532 | -66.6445 | 56.2306 | 56.3763 | 56.2971 | -66.9187 | -0.16421 | -0.053081 | -0.005297 | 0.014276 | 0.17848 | -0.21273 | -0.020126 | -0.35073 | -0.14758 | -0.019137 | -0.076536 | 0.2742 | -0.001871 | -0.081084 | 122.8931 | 122.7334 | 122.926 | 66.4091 | -123.1104 | 122.7986 | 122.9443 | 122.8651 | 66.4127 | -123.2969
263.2656 | 123.3124 | -66.6138 | 56.3644 | 0.04215 | -0.018079 | -0.0021677 | 0.054234 | -0.0020637 | 0.054873 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.063177 | 0.016853 | 0.064664 | -66.5733 | -0.15427 | -66.5446 | 56.3159 | 56.1609 | 56.358 | -66.7414 | -66.5826 | -0.15074 | -66.6445 | 56.2398 | 56.3809 | 56.3429 | -66.9233 | -0.12759 | -0.048505 | 0.04048 | 0.06921 | 0.1968 | -0.20357 | -0.006393 | -0.30953 | -0.12469 | 0.031219 | -0.030759 | 0.27877 | 0.016441 | -0.021565 | 122.9297 | 122.7746 | 122.9718 | 66.4595 | -123.1058 | 122.8535 | 122.9947 | 122.9566 | 66.463 | -123.2877
264.2656 | 123.1155 | -66.5771 | 56.4056 | 0.026888 | -0.019147 | -3.1667e-05 | 0.054234 | -0.0020637 | 0.053805 | 0.058145 | -0.0025767 | 0.0011204 | 0.062109 | 0.020058 | 0.063596 | -66.5733 | -0.15884 | -66.5537 | 56.3251 | 56.2021 | 56.3626 | -66.7368 | -66.5871 | -0.15532 | -66.6491 | 56.2398 | 56.3855 | 56.3475 | -66.9233 | -0.15963 | -0.080547 | 0.003858 | 0.023431 | 0.18306 | -0.20356 | -0.043014 | -0.34616 | -0.16589 | -0.009982 | -0.071959 | 0.2742 | -0.020179 | -0.058185 | 122.9022 | 122.7792 | 122.9398 | 66.4183 | -123.1424 | 122.8169 | 122.9626 | 122.9246 | 66.4218 | -123.3289
265.2656 | 123.1476 | -66.5909 | 56.3644 | 0.026888 | -0.019147 | -0.0021677 | 0.055302 | -0.0052687 | 0.055941 | 0.088667 | 0.00062833 | 5.2373e-05 | 0.061041 | 0.020058 | 0.063596 | -66.5733 | -0.14053 | -66.5491 | 56.3251 | 56.2112 | 56.3535 | -66.7414 | -66.5917 | -0.15074 | -66.6445 | 56.2306 | 56.3809 | 56.352 | -66.9233 | -0.15048 | -0.039348 | 0.017591 | 0.041742 | 0.19222 | -0.1532 | -0.010972 | -0.33242 | -0.13385 | -0.000828 | -0.053648 | 0.27877 | 0.016441 | -0.012408 | 122.916 | 122.8021 | 122.9443 | 66.4504 | -123.1058 | 122.8215 | 122.9718 | 122.9429 | 66.4401 | -123.2877
266.2656 | 123.1476 | -66.6046 | 56.3736 | 0.04215 | -0.019147 | -0.0021677 | 0.056371 | -0.0031317 | 0.055941 | 0.073406 | 0.00062833 | 5.2373e-05 | 0.061041 | 0.01899 | 0.063596 | -66.5779 | -0.14511 | -66.5491 | 56.3205 | 56.2296 | 56.3626 | -66.7276 | -66.5826 | -0.137 | -66.6399 | 56.2352 | 56.3809 | 56.3566 | -66.9233 | -0.12301 | -0.053082 | 0.026745 | 0.055475 | 0.17848 | -0.14404 | -0.01097 | -0.31869 | -0.13842 | 0.022063 | -0.035336 | 0.28335 | 0.007286 | -0.016984 | 122.9251 | 122.8342 | 122.9672 | 66.4595 | -123.1012 | 122.8398 | 122.9855 | 122.9612 | 66.4676 | -123.2969
267.2656 | 123.1338 | -66.5955 | 56.3828 | 0.057412 | -0.020215 | -0.0021677 | 0.053166 | -0.0041997 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.059972 | 0.01899 | 0.062528 | -66.5687 | -0.14053 | -66.5537 | 56.3205 | 56.225 | 56.3489 | -66.7368 | -66.5826 | -0.14158 | -66.6399 | 56.2443 | 56.39 | 56.3612 | -66.9187 | -0.14132 | -0.062237 | 0.026747 | 0.041742 | 0.18306 | -0.15778 | -0.033861 | -0.32327 | -0.13842 | 0.012908 | -0.044491 | 0.27877 | 0.007288 | -0.021561 | 122.916 | 122.8204 | 122.9443 | 66.4549 | -123.1195 | 122.8398 | 122.9855 | 122.9566 | 66.4539 | -123.3015
268.2656 | 123.2254 | -66.5771 | 56.3232 | 0.057412 | -0.020215 | -0.0043047 | 0.053166 | -0.0031317 | 0.054873 | 0.058145 | 0.00062833 | -0.0010156 | 0.061041 | 0.01899 | 0.06146 | -66.5687 | -0.14053 | -66.5491 | 56.3205 | 56.2387 | 56.3626 | -66.7368 | -66.5826 | -0.15074 | -66.6445 | 56.2398 | 56.3992 | 56.3566 | -66.9141 | -0.15963 | -0.002728 | 0.008436 | 0.028009 | 0.18764 | -0.084532 | 0.039384 | -0.337 | -0.083491 | -0.005403 | -0.067381 | 0.26962 | 0.075955 | 0.03337 | 122.8977 | 122.8159 | 122.9398 | 66.4366 | -123.06 | 122.8169 | 122.9763 | 122.9338 | 66.4264 | -123.2374
269.2656 | 123.143 | -66.5863 | 56.3828 | 0.057412 | -0.018079 | -0.0010997 | 0.054234 | -0.0031317 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.058904 | 0.01899 | 0.06146 | -66.5733 | -0.13595 | -66.5446 | 56.3251 | 56.2433 | 56.358 | -66.7414 | -66.578 | -0.14158 | -66.6445 | 56.2443 | 56.3946 | 56.3566 | -66.9187 | -0.15505 | -0.057658 | 0.013014 | 0.041744 | 0.1968 | -0.13946 | -0.024703 | -0.33242 | -0.13842 | 0.008332 | -0.058225 | 0.2742 | 0.011867 | -0.026139 | 122.9114 | 122.8296 | 122.9444 | 66.4504 | -123.1241 | 122.8306 | 122.9809 | 122.9429 | 66.4447 | -123.3015
270.2656 | 123.111 | -66.6229 | 56.4011 | 0.057412 | -0.020215 | -0.0010997 | 0.055302 | -0.0031317 | 0.055941 | 0.088667 | -0.0015087 | 0.0011204 | 0.062109 | 0.01899 | 0.063596 | -66.5733 | -0.12222 | -66.5491 | 56.3251 | 56.2341 | 56.3672 | -66.7414 | -66.5917 | -0.14158 | -66.6399 | 56.2443 | 56.3992 | 56.3658 | -66.9187 | -0.11843 | -0.075969 | 0.049635 | 0.073786 | 0.19222 | -0.16693 | -0.033857 | -0.2958 | -0.15673 | 0.031216 | -0.017025 | 0.27877 | -0.001865 | -0.035293 | 122.948 | 122.8571 | 122.9901 | 66.5007 | -123.1424 | 122.8673 | 123.0221 | 122.9887 | 66.4813 | -123.3198
271.2656 | 123.1155 | -66.6 | 56.3873 | 0.057412 | -0.01701 | -0.0010997 | 0.054234 | -0.0041997 | 0.055941 | 0.042884 | -0.0015087 | -0.0010156 | 0.061041 | 0.021126 | 0.062528 | -66.5687 | -0.12222 | -66.5491 | 56.3297 | 56.2387 | 56.3626 | -66.7459 | -66.578 | -0.137 | -66.6445 | 56.2443 | 56.39 | 56.3658 | -66.9096 | -0.1459 | -0.057658 | 0.031325 | 0.050898 | 0.1968 | -0.14862 | -0.024703 | -0.30953 | -0.143 | 0.022065 | -0.044492 | 0.26504 | 0.00271 | -0.02156 | 122.9297 | 122.8387 | 122.9627 | 66.4778 | -123.1333 | 122.8444 | 122.9901 | 122.9658 | 66.463 | -123.2969
272.2656 | 123.1155 | -66.6 | 56.4056 | 0.04215 | -0.022352 | -0.0010997 | 0.055302 | -0.0041997 | 0.054873 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.063177 | 0.01899 | 0.063596 | -66.5687 | -0.12679 | -66.54 | 56.3251 | 56.2341 | 56.3718 | -66.7368 | -66.5826 | -0.13242 | -66.6354 | 56.2489 | 56.3946 | 56.3658 | -66.9187 | -0.13674 | -0.080547 | 0.031325 | 0.060055 | 0.1968 | -0.17151 | -0.033856 | -0.31869 | -0.15673 | 0.017486 | -0.035334 | 0.28335 | -0.011022 | -0.039871 | 122.9251 | 122.8342 | 122.9718 | 66.4732 | -123.1424 | 122.8489 | 122.9947 | 122.9658 | 66.4676 | -123.3244
273.2656 | 123.2437 | -66.5817 | 56.3232 | 0.026888 | -0.019147 | -0.0021677 | 0.053166 | -0.0031317 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.061041 | 0.01899 | 0.06146 | -66.5733 | -0.12679 | -66.5491 | 56.3297 | 56.2021 | 56.3764 | -66.7368 | -66.578 | -0.137 | -66.6399 | 56.2398 | 56.3946 | 56.3612 | -66.9187 | -0.15505 | 0.006429 | 0.008436 | 0.032587 | 0.18764 | -0.12116 | 0.05312 | -0.337 | -0.083491 | 0.003754 | -0.058224 | 0.27877 | 0.071376 | 0.037948 | 122.9114 | 122.7838 | 122.9581 | 66.4549 | -123.06 | 122.8215 | 122.9763 | 122.9429 | 66.4447 | -123.242
274.2656 | 123.111 | -66.6 | 56.3919 | 0.04215 | -0.020215 | -0.0021677 | 0.055302 | -0.0031317 | 0.054873 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.062109 | 0.020058 | 0.06146 | -66.5779 | -0.13595 | -66.5491 | 56.3251 | 56.2524 | 56.3764 | -66.7368 | -66.5734 | -0.13242 | -66.6445 | 56.2443 | 56.3992 | 56.3658 | -66.9187 | -0.13674 | -0.066814 | 0.022168 | 0.050898 | 0.18764 | -0.13946 | -0.015545 | -0.31869 | -0.14758 | 0.026643 | -0.044492 | 0.2742 | 0.00729 | -0.026138 | 122.9251 | 122.8525 | 122.9764 | 66.4641 | -123.1287 | 122.8444 | 122.9992 | 122.9658 | 66.4676 | -123.3106
275.2656 | 123.1247 | -66.5817 | 56.3873 | 0.057412 | -0.018079 | -0.0021677 | 0.053166 | -0.0041997 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.020058 | 0.062528 | -66.5779 | -0.11764 | -66.54 | 56.3388 | 56.2479 | 56.3672 | -66.7368 | -66.578 | -0.137 | -66.6354 | 56.2443 | 56.3946 | 56.3658 | -66.9187 | -0.15505 | -0.048501 | 0.003857 | 0.041744 | 0.1968 | -0.13946 | -0.020124 | -0.337 | -0.143 | 0.003754 | -0.053645 | 0.28335 | 0.007289 | -0.02156 | 122.9206 | 122.8296 | 122.9489 | 66.4641 | -123.1241 | 122.8261 | 122.9763 | 122.9475 | 66.4447 | -123.3061
276.2656 | 123.1247 | -66.6 | 56.4056 | 0.057412 | -0.019147 | -0.0010997 | 0.053166 | -0.0041997 | 0.054873 | 0.058145 | -0.00043967 | 0.0011204 | 0.062109 | 0.01899 | 0.062528 | -66.5733 | -0.12222 | -66.5491 | 56.3297 | 56.2433 | 56.3718 | -66.7368 | -66.578 | -0.14158 | -66.6354 | 56.2489 | 56.3946 | 56.3749 | -66.9187 | -0.13674 | -0.075969 | 0.026747 | 0.050898 | 0.18764 | -0.16235 | -0.033856 | -0.31869 | -0.15673 | 0.022065 | -0.035334 | 0.28335 | -0.011022 | -0.030714 | 122.9297 | 122.8433 | 122.9718 | 66.4778 | -123.1424 | 122.8489 | 122.9947 | 122.975 | 66.4585 | -123.3244
277.2656 | 123.1293 | -66.6092 | 56.4056 | 0.057412 | -0.020215 | -0.0021677 | 0.054234 | -0.0031317 | 0.055941 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.064245 | 0.020058 | 0.064664 | -66.5687 | -0.12222 | -66.5491 | 56.3297 | 56.2479 | 56.3672 | -66.7322 | -66.5871 | -0.12327 | -66.6399 | 56.2443 | 56.3992 | 56.3658 | -66.9004 | -0.12301 | -0.075969 | 0.04048 | 0.060053 | 0.18306 | -0.15777 | -0.038435 | -0.29122 | -0.16131 | 0.022062 | -0.030758 | 0.26046 | -0.006443 | -0.039871 | 122.9389 | 122.8571 | 122.9764 | 66.487 | -123.1378 | 122.8535 | 123.0084 | 122.975 | 66.4859 | -123.306
278.2656 | 123.2346 | -66.5405 | 56.3278 | 0.057412 | -0.021284 | -0.0021677 | 0.054234 | -0.0031317 | 0.05701 | 0.042884 | -0.0025767 | -0.0010156 | 0.059972 | 0.01899 | 0.06146 | -66.5687 | -0.11764 | -66.54 | 56.3205 | 56.2433 | 56.3718 | -66.7368 | -66.5642 | -0.13242 | -66.6399 | 56.2443 | 56.4038 | 56.3612 | -66.9141 | -0.19625 | -0.007306 | -0.028185 | 0.000545 | 0.1968 | -0.084531 | 0.043964 | -0.37362 | -0.08349 | -0.023709 | -0.099423 | 0.2742 | 0.075955 | 0.03337 | 122.861 | 122.7838 | 122.9123 | 66.4229 | -123.0646 | 122.7849 | 122.9443 | 122.9017 | 66.4081 | -123.242
279.2656 | 123.1384 | -66.5726 | 56.4239 | 0.04215 | -0.020215 | -0.0010997 | 0.054234 | -0.0063367 | 0.054873 | 0.058145 | -0.0015087 | 0.0011204 | 0.062109 | 0.01899 | 0.062528 | -66.5733 | -0.11306 | -66.54 | 56.3297 | 56.2341 | 56.3672 | -66.723 | -66.5642 | -0.13242 | -66.6354 | 56.2443 | 56.3946 | 56.3658 | -66.905 | -0.15047 | -0.094279 | -0.000719 | 0.032589 | 0.18306 | -0.18982 | -0.056745 | -0.33242 | -0.17962 | 0.008335 | -0.0628 | 0.26962 | -0.029332 | -0.058181 | 122.9022 | 122.8067 | 122.9398 | 66.4595 | -123.147 | 122.8169 | 122.9672 | 122.9383 | 66.4401 | -123.3289
280.2656 | 123.1201 | -66.6 | 56.4194 | 0.04215 | -0.020215 | -0.0010997 | 0.055302 | -0.0052687 | 0.055941 | 0.088667 | -0.0025767 | 5.2373e-05 | 0.059972 | 0.021126 | 0.063596 | -66.5641 | -0.12222 | -66.5446 | 56.3342 | 56.2387 | 56.3718 | -66.7276 | -66.5688 | -0.13242 | -66.6354 | 56.2489 | 56.3992 | 56.3612 | -66.9096 | -0.12758 | -0.085123 | 0.035903 | 0.055477 | 0.18306 | -0.18066 | -0.047589 | -0.30953 | -0.17047 | 0.031222 | -0.035334 | 0.2742 | -0.020176 | -0.058183 | 122.9343 | 122.8387 | 122.9718 | 66.4778 | -123.147 | 122.8489 | 122.9992 | 122.9612 | 66.4676 | -123.3289
281.2656 | 123.1293 | -66.5817 | 56.4102 | 0.057412 | -0.020215 | -0.0043047 | 0.054234 | -0.0041997 | 0.05701 | 0.058145 | -0.0015087 | -0.0010156 | 0.062109 | 0.01899 | 0.062528 | -66.5779 | -0.11764 | -66.5446 | 56.3388 | 56.2387 | 56.3718 | -66.7322 | -66.578 | -0.12327 | -66.6399 | 56.2489 | 56.3992 | 56.3612 | -66.905 | -0.15047 | -0.071389 | 0.003857 | 0.037166 | 0.18764 | -0.17151 | -0.038433 | -0.32326 | -0.16131 | 0.003754 | -0.058224 | 0.26504 | -0.01102 | -0.049027 | 122.9206 | 122.8204 | 122.9535 | 66.4641 | -123.1424 | 122.8306 | 122.9809 | 122.9429 | 66.4585 | -123.3152
282.3281 | 123.2712 | -66.5268 | 56.369 | 0.057412 | -0.020215 | -0.0032367 | 0.053166 | -0.0041997 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.021126 | 0.063596 | -66.5641 | -0.12222 | -66.5446 | 56.3342 | 56.2112 | 56.3718 | -66.7276 | -66.5734 | -0.12784 | -66.6399 | 56.2443 | 56.4038 | 56.3566 | -66.9141 | -0.20083 | -0.034769 | -0.03734 | -0.017766 | 0.18306 | -0.15778 | 0.002765 | -0.38735 | -0.12469 | -0.0466 | -0.11316 | 0.2742 | 0.034756 | -0.012407 | 122.861 | 122.738 | 122.8986 | 66.4046 | -123.0966 | 122.7711 | 122.9306 | 122.8834 | 66.3989 | -123.2832
283.2656 | 123.1338 | -66.6092 | 56.3736 | 0.057412 | -0.021284 | -0.0021677 | 0.055302 | -0.0041997 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.061041 | 0.022195 | 0.062528 | -66.5641 | -0.11306 | -66.5491 | 56.3297 | 56.2204 | 56.3718 | -66.7276 | -66.5688 | -0.12327 | -66.6354 | 56.2489 | 56.4084 | 56.3703 | -66.9141 | -0.11843 | -0.043925 | 0.045058 | 0.060053 | 0.17848 | -0.1532 | -0.001812 | -0.30495 | -0.12469 | 0.040377 | -0.026179 | 0.27877 | 0.034758 | -0.003248 | 122.9389 | 122.8296 | 122.981 | 66.4961 | -123.1012 | 122.8581 | 123.0175 | 122.9795 | 66.4859 | -123.2877
284.2656 | 123.1293 | -66.5771 | 56.4331 | 0.04215 | -0.022352 | -0.0032367 | 0.054234 | -0.0041997 | 0.05701 | 0.058145 | -0.0025767 | 0.0011204 | 0.063177 | 0.021126 | 0.06146 | -66.5687 | -0.12222 | -66.54 | 56.3388 | 56.2387 | 56.3764 | -66.7276 | -66.5688 | -0.11869 | -66.6354 | 56.2489 | 56.4038 | 56.3658 | -66.9141 | -0.15047 | -0.094277 | 0.008436 | 0.037166 | 0.18764 | -0.1944 | -0.056743 | -0.337 | -0.1842 | 0.008333 | -0.058223 | 0.27877 | -0.02933 | -0.067336 | 122.916 | 122.8159 | 122.9535 | 66.4549 | -123.1607 | 122.8261 | 122.9809 | 122.9429 | 66.4585 | -123.3473
285.2656 | 123.1659 | -66.5222 | 56.369 | 0.04215 | -0.020215 | -0.0021677 | 0.056371 | -0.0052687 | 0.05701 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.021126 | 0.062528 | -66.5687 | -0.12222 | -66.5446 | 56.3434 | 56.225 | 56.3855 | -66.723 | -66.5642 | -0.11869 | -66.6262 | 56.2489 | 56.4038 | 56.3658 | -66.905 | -0.20082 | -0.025613 | -0.046495 | -0.022343 | 0.17848 | -0.14405 | 0.0165 | -0.38277 | -0.12011 | -0.042019 | -0.104 | 0.27877 | 0.034756 | -0.00325 | 122.8656 | 122.7472 | 122.9077 | 66.4 | -123.0921 | 122.7711 | 122.926 | 122.888 | 66.4035 | -123.274
286.2656 | 123.1384 | -66.5771 | 56.4148 | 0.04215 | -0.021284 | -0.0021677 | 0.054234 | -0.0063367 | 0.055941 | 0.073406 | 0.00062833 | 0.0021894 | 0.062109 | 0.021126 | 0.062528 | -66.5641 | -0.12222 | -66.54 | 56.3388 | 56.2204 | 56.3718 | -66.723 | -66.5642 | -0.11869 | -66.6354 | 56.2535 | 56.4038 | 56.3658 | -66.9096 | -0.14589 | -0.075967 | 0.013014 | 0.037166 | 0.18306 | -0.1944 | -0.043011 | -0.33242 | -0.16131 | 0.012912 | -0.058223 | 0.2742 | -0.01102 | -0.049026 | 122.916 | 122.7975 | 122.9489 | 66.4549 | -123.1378 | 122.8306 | 122.9809 | 122.9429 | 66.4585 | -123.3244
287.2656 | 123.143 | -66.5955 | 56.3919 | 0.026888 | -0.020215 | -0.0010997 | 0.054234 | -0.0041997 | 0.054873 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.022195 | 0.063596 | -66.5687 | -0.12222 | -66.5446 | 56.3388 | 56.2479 | 56.3855 | -66.7276 | -66.5688 | -0.12327 | -66.6308 | 56.2535 | 56.4038 | 56.3749 | -66.9096 | -0.13216 | -0.053079 | 0.026747 | 0.050899 | 0.18306 | -0.14404 | -0.006388 | -0.31411 | -0.13842 | 0.026644 | -0.035333 | 0.27877 | 0.011868 | -0.016981 | 122.9343 | 122.8433 | 122.981 | 66.4732 | -123.1195 | 122.8489 | 122.9992 | 122.9704 | 66.4722 | -123.3015
288.2656 | 123.1155 | -66.5817 | 56.3873 | 0.026888 | -0.020215 | -0.0032367 | 0.054234 | -0.0052687 | 0.05701 | 0.042884 | -0.00043967 | 0.0011204 | 0.061041 | 0.022195 | 0.062528 | -66.5596 | -0.11306 | -66.5446 | 56.348 | 56.2662 | 56.3855 | -66.7276 | -66.5688 | -0.11411 | -66.6399 | 56.2535 | 56.4084 | 56.3703 | -66.905 | -0.14589 | -0.039344 | 0.022171 | 0.037166 | 0.18306 | -0.12114 | -0.00181 | -0.32326 | -0.13384 | 0.012911 | -0.058224 | 0.26504 | 0.021025 | -0.016981 | 122.9297 | 122.8479 | 122.9672 | 66.4687 | -123.1149 | 122.8352 | 122.9901 | 122.9521 | 66.4676 | -123.2923
289.2656 | 123.143 | -66.5863 | 56.4011 | 0.04215 | -0.019147 | -0.0010997 | 0.052097 | -0.0041997 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.059972 | 0.020058 | 0.062528 | -66.5687 | -0.12222 | -66.5446 | 56.3297 | 56.2616 | 56.3809 | -66.723 | -66.5688 | -0.11411 | -66.6262 | 56.2535 | 56.4038 | 56.3749 | -66.9004 | -0.13674 | -0.071391 | 0.017592 | 0.041744 | 0.17848 | -0.13946 | -0.020121 | -0.3141 | -0.14758 | 0.017489 | -0.03991 | 0.27419 | 0.002713 | -0.026136 | 122.916 | 122.8479 | 122.9672 | 66.4641 | -123.1241 | 122.8398 | 122.9901 | 122.9612 | 66.4722 | -123.3015
290.2656 | 123.1247 | -66.5771 | 56.4239 | 0.026888 | -0.021284 | -0.0021677 | 0.055302 | -0.0031317 | 0.055941 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.059972 | 0.020058 | 0.06146 | -66.5687 | -0.12222 | -66.54 | 56.3388 | 56.2479 | 56.3855 | -66.7276 | -66.5642 | -0.10495 | -66.6216 | 56.2581 | 56.4084 | 56.3749 | -66.9004 | -0.15047 | -0.085122 | 0.008436 | 0.037166 | 0.18764 | -0.17608 | -0.038431 | -0.32326 | -0.16588 | 0.012912 | -0.044487 | 0.27877 | -0.015596 | -0.049024 | 122.916 | 122.825 | 122.9627 | 66.4549 | -123.1516 | 122.8352 | 122.9855 | 122.9521 | 66.4722 | -123.3244
291.2656 | 123.2025 | -66.5314 | 56.3873 | 0.057412 | -0.021284 | -3.1667e-05 | 0.054234 | -0.0041997 | 0.05701 | 0.088667 | 0.00062833 | 5.2373e-05 | 0.058904 | 0.022195 | 0.06146 | -66.5641 | -0.11764 | -66.5446 | 56.3388 | 56.2479 | 56.3809 | -66.7185 | -66.5688 | -0.10953 | -66.6308 | 56.2581 | 56.4129 | 56.3703 | -66.905 | -0.18709 | -0.048501 | -0.032762 | -0.013188 | 0.1739 | -0.13946 | -0.006388 | -0.37362 | -0.12926 | -0.037443 | -0.09942 | 0.2742 | 0.025603 | -0.016981 | 122.8702 | 122.7792 | 122.9123 | 66.4137 | -123.1058 | 122.7894 | 122.9443 | 122.9017 | 66.4218 | -123.2923
292.4219 | 123.2666 | -66.5588 | 56.3232 | 0.057412 | -0.021284 | -0.0021677 | 0.054234 | -0.0041997 | 0.053805 | 0.027623 | -0.00043967 | -0.0010156 | 0.059972 | 0.021126 | 0.06146 | -66.5641 | -0.11764 | -66.5308 | 56.3388 | 56.2524 | 56.3855 | -66.723 | -66.5688 | -0.10953 | -66.6262 | 56.2489 | 56.4084 | 56.3703 | -66.905 | -0.1642 | 0.015586 | -0.005296 | 0.028012 | 0.19221 | -0.070795 | 0.062277 | -0.34615 | -0.074334 | -0.009977 | -0.067376 | 0.27877 | 0.085112 | 0.047106 | 122.8977 | 122.8113 | 122.9444 | 66.4412 | -123.0463 | 122.8077 | 122.9672 | 122.9292 | 66.4493 | -123.2282
293.7656 | 123.1888 | -66.5817 | 56.3644 | 0.026888 | -0.020215 | -0.0032367 | 0.054234 | -0.0031317 | 0.055941 | 0.073406 | -0.00043967 | 0.0011204 | 0.059972 | 0.020058 | 0.06146 | -66.5596 | -0.12222 | -66.54 | 56.3342 | 56.2387 | 56.3809 | -66.7185 | -66.5642 | -0.10495 | -66.6308 | 56.2489 | 56.4084 | 56.3749 | -66.905 | -0.13674 | -0.030191 | 0.022171 | 0.041744 | 0.17848 | -0.12573 | 0.0165 | -0.32326 | -0.11553 | 0.01749 | -0.049066 | 0.2742 | 0.043913 | 0.010485 | 122.916 | 122.8204 | 122.9627 | 66.4595 | -123.0829 | 122.8306 | 122.9901 | 122.9567 | 66.4768 | -123.2694
294.6406 | 123.1293 | -66.6 | 56.3919 | 0.04215 | -0.021284 | -0.0032367 | 0.054234 | -0.0041997 | 0.059146 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.059972 | 0.022195 | 0.06146 | -66.5687 | -0.10848 | -66.5491 | 56.3388 | 56.2433 | 56.3809 | -66.723 | -66.5597 | -0.10037 | -66.6262 | 56.2535 | 56.4175 | 56.3749 | -66.9004 | -0.123 | -0.053079 | 0.031325 | 0.050898 | 0.1739 | -0.14862 | -0.010966 | -0.30037 | -0.13842 | 0.040379 | -0.026177 | 0.27419 | 0.025604 | -0.016981 | 122.9389 | 122.8433 | 122.981 | 66.4916 | -123.1149 | 122.8535 | 123.0175 | 122.975 | 66.4997 | -123.2923
295.9688 | 123.1979 | -66.5451 | 56.3828 | 0.04215 | -0.020215 | -0.0021677 | 0.053166 | -0.0041997 | 0.055941 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.061041 | 0.01899 | 0.062528 | -66.5641 | -0.12222 | -66.5491 | 56.3434 | 56.2296 | 56.3809 | -66.723 | -66.5688 | -0.091215 | -66.6262 | 56.2581 | 56.4129 | 56.3658 | -66.9004 | -0.17794 | -0.039345 | -0.019029 | -0.004034 | 0.1739 | -0.1532 | -0.00181 | -0.3553 | -0.12469 | -0.02371 | -0.081109 | 0.27419 | 0.030181 | -0.016982 | 122.8885 | 122.7747 | 122.926 | 66.4229 | -123.1058 | 122.8032 | 122.958 | 122.9109 | 66.4539 | -123.2832
297.5156 | 123.2025 | -66.568 | 56.3782 | 0.072674 | -0.021284 | -0.0043047 | 0.053166 | -0.0052687 | 0.055941 | 0.058145 | -0.00043967 | -0.0010156 | 0.062109 | 0.022195 | 0.060391 | -66.5641 | -0.11306 | -66.54 | 56.3434 | 56.2341 | 56.3764 | -66.723 | -66.5642 | -0.095794 | -66.6308 | 56.2581 | 56.4175 | 56.3612 | -66.9004 | -0.15505 | -0.034768 | 0.003859 | 0.028011 | 0.18306 | -0.14404 | -0.001812 | -0.33242 | -0.12011 | 0.003757 | -0.062799 | 0.26962 | 0.039337 | -0.016984 | 122.9114 | 122.8021 | 122.9444 | 66.4549 | -123.1012 | 122.8261 | 122.9855 | 122.9292 | 66.4722 | -123.2786
298.7969 | 123.2666 | -66.5497 | 56.3736 | 0.04215 | -0.021284 | -0.0021677 | 0.054234 | -0.0052687 | 0.05701 | 0.073406 | -0.0015087 | 0.0011204 | 0.062109 | 0.023263 | 0.062528 | -66.5733 | -0.11764 | -66.5446 | 56.3434 | 56.1975 | 56.3855 | -66.723 | -66.5597 | -0.095794 | -66.6354 | 56.2672 | 56.4129 | 56.3658 | -66.9141 | -0.17336 | -0.03019 | -0.023607 | 0.005123 | 0.17848 | -0.1761 | 0.011923 | -0.36446 | -0.10637 | -0.009975 | -0.085688 | 0.27877 | 0.039336 | -0.007827 | 122.8931 | 122.7472 | 122.9352 | 66.432 | -123.0966 | 122.8169 | 122.9626 | 122.9155 | 66.4539 | -123.2877
299.5781 | 123.2712 | -66.5405 | 56.3507 | 0.026888 | -0.020215 | -0.0010997 | 0.055302 | -0.0052687 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.022195 | 0.062528 | -66.555 | -0.11306 | -66.54 | 56.3342 | 56.2112 | 56.3855 | -66.7185 | -66.5642 | -0.10037 | -66.6262 | 56.2672 | 56.4129 | 56.3566 | -66.905 | -0.17794 | -0.016458 | -0.01445 | 0.000545 | 0.17848 | -0.13947 | 0.034811 | -0.36446 | -0.083486 | -0.023709 | -0.085687 | 0.27877 | 0.062224 | 0.005904 | 122.8748 | 122.7518 | 122.926 | 66.4275 | -123.0692 | 122.8077 | 122.9535 | 122.8971 | 66.4402 | -123.2557
300.5781 | 123.1201 | -66.5817 | 56.3919 | 0.057412 | -0.02342 | -0.0043047 | 0.054234 | -0.0041997 | 0.054873 | 0.058145 | -0.00043967 | 0.0011204 | 0.062109 | 0.021126 | 0.062528 | -66.5596 | -0.11764 | -66.5491 | 56.3434 | 56.1838 | 56.3809 | -66.7139 | -66.5642 | -0.091215 | -66.6216 | 56.2581 | 56.4038 | 56.3108 | -66.9004 | -0.13216 | -0.048501 | 0.022171 | 0.032587 | 0.16474 | -0.20814 | -0.010966 | -0.31868 | -0.13384 | 0.01749 | -0.039909 | 0.27877 | 0.011868 | -0.081081 | 122.9251 | 122.7655 | 122.9627 | 66.4641 | -123.1058 | 122.8398 | 122.9855 | 122.8926 | 66.4905 | -123.2923
301.3125 | 123.175 | -66.6046 | 56.3324 | 0.057412 | -0.02342 | -0.0021677 | 0.053166 | -0.0052687 | 0.05701 | 0.027623 | -0.00043967 | 5.2373e-05 | 0.059972 | 0.022195 | 0.063596 | -66.5596 | -0.11306 | -66.54 | 56.3434 | 56.1929 | 56.3947 | -66.7185 | -66.5642 | -0.10037 | -66.6216 | 56.2672 | 56.4084 | 56.3566 | -66.9096 | -0.11385 | 0.011009 | 0.045059 | 0.064632 | 0.17848 | -0.13948 | 0.06228 | -0.30495 | -0.065175 | 0.040378 | -0.017021 | 0.28793 | 0.075957 | 0.024215 | 122.948 | 122.7975 | 122.9993 | 66.4916 | -123.0509 | 122.8718 | 123.013 | 122.9612 | 66.5042 | -123.242
305.3906 | 123.2712 | -66.5405 | 56.3553 | 0.057412 | -0.021284 | -0.0021677 | 0.054234 | -0.0041997 | 0.055941 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.021126 | 0.060391 | -66.5596 | -0.12222 | -66.54 | 56.3526 | 56.2341 | 56.3855 | -66.7185 | -66.5551 | -0.10037 | -66.6308 | 56.2718 | 56.4175 | 56.3795 | -66.905 | -0.17794 | -0.002723 | -0.019028 | 0.000545 | 0.17848 | -0.12116 | 0.030233 | -0.36446 | -0.083485 | -0.014552 | -0.090265 | 0.2742 | 0.062225 | 0.024219 | 122.8931 | 122.7747 | 122.926 | 66.4183 | -123.0737 | 122.8123 | 122.958 | 122.92 | 66.4402 | -123.2603
306.2656 | 123.2391 | -66.5588 | 56.3782 | 0.04215 | -0.02342 | -0.0032367 | 0.055302 | -0.0031317 | 0.05701 | 0.088667 | -0.0015087 | 0.0011204 | 0.061041 | 0.022195 | 0.06146 | -66.5641 | -0.11764 | -66.54 | 56.3434 | 56.257 | 56.3901 | -66.7139 | -66.5551 | -0.086637 | -66.6262 | 56.2626 | 56.4175 | 56.3795 | -66.8958 | -0.15505 | -0.034768 | -0.005296 | 0.018856 | 0.1739 | -0.12115 | 0.011924 | -0.33699 | -0.11553 | 0.003759 | -0.067376 | 0.26962 | 0.039337 | 0.001331 | 122.9022 | 122.8159 | 122.9489 | 66.4412 | -123.0921 | 122.8215 | 122.9763 | 122.9383 | 66.4722 | -123.274
307.3281 | 123.23 | -66.5176 | 56.3828 | 0.04215 | -0.021284 | -0.0032367 | 0.054234 | -0.0041997 | 0.05701 | 0.058145 | -0.0025767 | -0.0010156 | 0.061041 | 0.023263 | 0.06146 | -66.5596 | -0.11306 | -66.5308 | 56.3434 | 56.2433 | 56.3855 | -66.7185 | -66.5551 | -0.091215 | -66.6262 | 56.2489 | 56.4175 | 56.3795 | -66.8958 | -0.20082 | -0.039345 | -0.041916 | -0.013187 | 0.18764 | -0.13946 | 0.002768 | -0.37819 | -0.13384 | -0.03744 | -0.10858 | 0.26962 | 0.03476 | -0.003246 | 122.861 | 122.7609 | 122.9032 | 66.4046 | -123.1012 | 122.7665 | 122.9351 | 122.8971 | 66.4264 | -123.2786
308.2656 | 123.2071 | -66.5451 | 56.3873 | 0.04215 | -0.021284 | -0.0053737 | 0.052097 | -0.0031317 | 0.05701 | 0.073406 | -0.00043967 | 0.0011204 | 0.061041 | 0.023263 | 0.062528 | -66.555 | -0.12222 | -66.5354 | 56.3526 | 56.2387 | 56.3855 | -66.7276 | -66.5551 | -0.091215 | -66.6262 | 56.2626 | 56.4129 | 56.3749 | -66.9004 | -0.18251 | -0.034766 | -0.009872 | 0.009701 | 0.19222 | -0.14862 | -0.00181 | -0.3553 | -0.12468 | -0.009974 | -0.081109 | 0.27419 | 0.025603 | -0.012403 | 122.8977 | 122.7838 | 122.9306 | 66.4229 | -123.1149 | 122.8077 | 122.958 | 122.92 | 66.4539 | -123.2877
309.3281 | 123.1293 | -66.5909 | 56.4011 | 0.057412 | -0.021284 | -0.0010997 | 0.054234 | -0.0041997 | 0.055941 | 0.042884 | -0.00043967 | 0.0032574 | 0.059972 | 0.024332 | 0.062528 | -66.555 | -0.11306 | -66.5446 | 56.3571 | 56.2341 | 56.3993 | -66.7185 | -66.5551 | -0.095794 | -66.6262 | 56.2718 | 56.4175 | 56.3841 | -66.9096 | -0.12758 | -0.04392 | 0.035904 | 0.046321 | 0.1739 | -0.16693 | -0.001807 | -0.31869 | -0.12926 | 0.035802 | -0.035333 | 0.28335 | 0.016449 | -0.016979 | 122.948 | 122.825 | 122.9901 | 66.4778 | -123.1195 | 122.8627 | 123.0084 | 122.975 | 66.4951 | -123.3106
310.2656 | 123.1979 | -66.5634 | 56.3736 | 0.057412 | -0.021284 | -0.0021677 | 0.054234 | -0.0041997 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.061041 | 0.022195 | 0.060391 | -66.555 | -0.11764 | -66.5354 | 56.348 | 56.2433 | 56.3993 | -66.7139 | -66.5551 | -0.095794 | -66.6262 | 56.2581 | 56.4221 | 56.3795 | -66.8958 | -0.15047 | -0.025611 | 0.008439 | 0.028012 | 0.17848 | -0.13031 | 0.025659 | -0.33241 | -0.11553 | 0.008337 | -0.062798 | 0.26962 | 0.048494 | 0.005909 | 122.9114 | 122.8067 | 122.9627 | 66.4458 | -123.0875 | 122.8215 | 122.9855 | 122.9429 | 66.4676 | -123.2694
311.2656 | 123.2117 | -66.5176 | 56.3782 | 0.026888 | -0.020215 | -0.0021677 | 0.052097 | -0.0041997 | 0.05701 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.059972 | 0.022195 | 0.060391 | -66.555 | -0.11764 | -66.54 | 56.3617 | 56.2387 | 56.3947 | -66.7139 | -66.5551 | -0.095794 | -66.6262 | 56.2764 | 56.4175 | 56.3841 | -66.8958 | -0.19624 | -0.016454 | -0.037338 | -0.022343 | 0.1739 | -0.13946 | 0.016503 | -0.37819 | -0.1018 | -0.03744 | -0.10858 | 0.26962 | 0.039337 | 0.005909 | 122.8794 | 122.7563 | 122.9123 | 66.4 | -123.0921 | 122.794 | 122.9351 | 122.9017 | 66.4218 | -123.274
312.2656 | 123.1934 | -66.5268 | 56.3461 | 0.026888 | -0.022352 | -0.0021677 | 0.053166 | -0.0052687 | 0.05701 | 0.073406 | -0.0025767 | 0.0021894 | 0.062109 | 0.022195 | 0.06146 | -66.5641 | -0.12222 | -66.5354 | 56.348 | 56.2524 | 56.3855 | -66.7093 | -66.5551 | -0.095794 | -66.6216 | 56.2718 | 56.4267 | 56.3887 | -66.8958 | -0.18251 | 0.001855 | -0.03734 | -0.00861 | 0.1739 | -0.093683 | 0.039389 | -0.36904 | -0.074329 | -0.028285 | -0.094841 | 0.2742 | 0.080538 | 0.042532 | 122.8748 | 122.7792 | 122.9123 | 66.4046 | -123.0554 | 122.7986 | 122.9535 | 122.9155 | 66.431 | -123.242
313.2656 | 123.2117 | -66.5543 | 56.3736 | 0.04215 | -0.02342 | -0.0010997 | 0.053166 | -0.0041997 | 0.054873 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.023263 | 0.062528 | -66.5596 | -0.11306 | -66.5354 | 56.3526 | 56.2479 | 56.3901 | -66.7093 | -66.5505 | -0.10037 | -66.6216 | 56.2718 | 56.4175 | 56.3841 | -66.8958 | -0.15504 | -0.021033 | -0.005295 | 0.018856 | 0.1739 | -0.12573 | 0.016502 | -0.34157 | -0.10179 | 0.00376 | -0.067375 | 0.2742 | 0.043915 | 0.010487 | 122.9068 | 122.8021 | 122.9444 | 66.4412 | -123.0829 | 122.8261 | 122.9718 | 122.9383 | 66.4539 | -123.2694
314.2656 | 123.2025 | -66.5222 | 56.3416 | 0.026888 | -0.021284 | -0.0032367 | 0.054234 | -0.0041997 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.058904 | 0.022195 | 0.062528 | -66.5458 | -0.11764 | -66.5354 | 56.348 | 56.257 | 56.3855 | -66.7093 | -66.5459 | -0.10037 | -66.6216 | 56.2718 | 56.4221 | 56.3841 | -66.9004 | -0.18709 | 0.006432 | -0.023603 | -0.013187 | 0.1739 | -0.084527 | 0.043966 | -0.37819 | -0.069752 | -0.023704 | -0.099418 | 0.27877 | 0.080537 | 0.04253 | 122.8702 | 122.7792 | 122.9077 | 66.4046 | -123.0509 | 122.794 | 122.9443 | 122.9063 | 66.4218 | -123.242
315.2656 | 123.23 | -66.5268 | 56.3461 | 0.04215 | -0.021284 | -0.0043047 | 0.054234 | -0.0031317 | 0.054873 | 0.042884 | -0.0025767 | 0.0011204 | 0.061041 | 0.023263 | 0.06146 | -66.555 | -0.11764 | -66.5354 | 56.3571 | 56.2479 | 56.3855 | -66.7093 | -66.5551 | -0.10495 | -66.6262 | 56.2672 | 56.4221 | 56.3887 | -66.8958 | -0.18251 | 0.011012 | -0.028183 | -0.00861 | 0.1739 | -0.098262 | 0.039389 | -0.36904 | -0.078908 | -0.028285 | -0.09942 | 0.26962 | 0.07596 | 0.042532 | 122.8839 | 122.7747 | 122.9123 | 66.4092 | -123.0554 | 122.794 | 122.9489 | 122.9155 | 66.4218 | -123.242
316.2656 | 123.2437 | -66.5314 | 56.369 | 0.04215 | -0.021284 | -0.0021677 | 0.056371 | -0.0052687 | 0.05701 | -0.0028987 | -0.0025767 | 0.0011204 | 0.059972 | 0.023263 | 0.06146 | -66.555 | -0.12222 | -66.5308 | 56.3526 | 56.2433 | 56.3993 | -66.7047 | -66.5459 | -0.11869 | -66.6216 | 56.2672 | 56.4175 | 56.3887 | -66.8958 | -0.17335 | -0.016456 | -0.023605 | 0.000546 | 0.1739 | -0.12573 | 0.030236 | -0.36446 | -0.1018 | -0.014549 | -0.090263 | 0.2742 | 0.048492 | 0.019643 | 122.8839 | 122.7747 | 122.9306 | 66.4092 | -123.0737 | 122.7986 | 122.9489 | 122.92 | 66.4127 | -123.2648
317.2656 | 123.2117 | -66.5405 | 56.369 | 0.04215 | -0.022352 | -0.0043047 | 0.054234 | -0.0052687 | 0.055941 | 0.058145 | 0.0016963 | 5.2373e-05 | 0.061041 | 0.023263 | 0.062528 | -66.555 | -0.11764 | -66.5308 | 56.3663 | 56.2479 | 56.3947 | -66.7093 | -66.5505 | -0.11869 | -66.6171 | 56.2764 | 56.4221 | 56.3887 | -66.8958 | -0.16878 | -0.002721 | -0.01445 | 0.009701 | 0.17848 | -0.12115 | 0.025658 | -0.3553 | -0.09264 | -0.009973 | -0.076529 | 0.27877 | 0.053071 | 0.019643 | 122.9068 | 122.7884 | 122.9352 | 66.4229 | -123.0783 | 122.8169 | 122.9626 | 122.9292 | 66.4218 | -123.2648
318.2656 | 123.2162 | -66.5497 | 56.3782 | 0.057412 | -0.022352 | -0.0032367 | 0.052097 | -0.0041997 | 0.054873 | 0.027623 | -0.0015087 | 5.2373e-05 | 0.062109 | 0.022195 | 0.060391 | -66.5504 | -0.12222 | -66.5308 | 56.348 | 56.2524 | 56.4038 | -66.7047 | -66.5459 | -0.11411 | -66.6171 | 56.2764 | 56.4221 | 56.3887 | -66.8867 | -0.15504 | -0.030189 | -0.000715 | 0.018857 | 0.1739 | -0.12573 | 0.02566 | -0.33699 | -0.1018 | 0.003762 | -0.067373 | 0.26962 | 0.043916 | 0.010488 | 122.8977 | 122.8021 | 122.9535 | 66.4275 | -123.0829 | 122.8261 | 122.9718 | 122.9383 | 66.4356 | -123.2648
319.2656 | 123.1201 | -66.4993 | 56.3553 | 0.057412 | -0.02342 | -0.0021677 | 0.053166 | -0.0052687 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.022195 | 0.062528 | -66.555 | -0.11764 | -66.5354 | 56.3663 | 56.257 | 56.4038 | -66.7047 | -66.5459 | -0.11411 | -66.6216 | 56.2718 | 56.4312 | 56.3932 | -66.8867 | -0.2054 | 0.011012 | -0.055648 | -0.036075 | 0.16932 | -0.09826 | 0.048548 | -0.38734 | -0.083485 | -0.046592 | -0.12231 | 0.26504 | 0.075961 | 0.037955 | 122.8656 | 122.7564 | 122.9032 | 66.3817 | -123.06 | 122.7711 | 122.9306 | 122.8926 | 66.3852 | -123.242
320.2656 | 123.2574 | -66.5359 | 56.3599 | 0.072674 | -0.02342 | -0.0032367 | 0.053166 | -0.0063367 | 0.055941 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.023263 | 0.06146 | -66.555 | -0.12222 | -66.5308 | 56.3571 | 56.2479 | 56.3947 | -66.7001 | -66.5505 | -0.11869 | -66.6171 | 56.2718 | 56.4267 | 56.3887 | -66.8913 | -0.1642 | -0.002721 | -0.019027 | 0.005124 | 0.16932 | -0.112 | 0.034814 | -0.3553 | -0.088062 | -0.01455 | -0.081106 | 0.2742 | 0.066805 | 0.028799 | 122.8931 | 122.7838 | 122.9306 | 66.4137 | -123.06 | 122.8078 | 122.9626 | 122.9246 | 66.4173 | -123.2511
321.3281 | 123.2529 | -66.5359 | 56.3644 | 0.057412 | -0.02342 | -0.0043047 | 0.053166 | -0.0052687 | 0.05701 | 0.042884 | -0.00043967 | 0.0011204 | 0.061041 | 0.022195 | 0.06146 | -66.5504 | -0.13137 | -66.5308 | 56.3526 | 56.2433 | 56.4084 | -66.7047 | -66.5505 | -0.11869 | -66.6171 | 56.2718 | 56.4312 | 56.3795 | -66.8821 | -0.16877 | -0.011878 | -0.014448 | 0.005124 | 0.1739 | -0.12115 | 0.043971 | -0.34614 | -0.09264 | -0.01455 | -0.081106 | 0.26504 | 0.066806 | 0.015064 | 122.8885 | 122.7792 | 122.9444 | 66.4046 | -123.0692 | 122.8078 | 122.9672 | 122.9155 | 66.4173 | -123.2465
322.2656 | 123.262 | -66.5726 | 56.3828 | 0.04215 | -0.022352 | -0.0010997 | 0.053166 | -0.0063367 | 0.054873 | 0.058145 | -0.00043967 | 0.0011204 | 0.061041 | 0.024332 | 0.062528 | -66.555 | -0.12222 | -66.5262 | 56.3571 | 56.2616 | 56.4038 | -66.7047 | -66.5551 | -0.12327 | -66.6125 | 56.281 | 56.4267 | 56.3932 | -66.8913 | -0.13215 | -0.025609 | 0.017594 | 0.046324 | 0.17848 | -0.12115 | 0.021083 | -0.31868 | -0.10179 | 0.017492 | -0.039907 | 0.27877 | 0.043917 | 0.01049 | 122.9297 | 122.8342 | 122.9764 | 66.4504 | -123.0875 | 122.8535 | 122.9992 | 122.9658 | 66.4493 | -123.274
323.2656 | 123.2574 | -66.5268 | 56.3782 | 0.04215 | -0.025557 | -0.0010997 | 0.053166 | -0.0052687 | 0.055941 | 0.027623 | -0.0015087 | -0.0010156 | 0.061041 | 0.023263 | 0.060391 | -66.5412 | -0.12222 | -66.5308 | 56.3526 | 56.2524 | 56.4038 | -66.7139 | -66.5505 | -0.12327 | -66.6079 | 56.2718 | 56.4221 | 56.3841 | -66.8867 | -0.18709 | -0.025611 | -0.014448 | -0.004032 | 0.18306 | -0.12573 | 0.02566 | -0.35988 | -0.10637 | -0.023706 | -0.081105 | 0.27877 | 0.043916 | 0.005909 | 122.8794 | 122.7792 | 122.9306 | 66.4046 | -123.0921 | 122.7986 | 122.9489 | 122.9109 | 66.4035 | -123.2648
324.2656 | 123.2208 | -66.5497 | 56.3782 | 0.057412 | -0.022352 | -0.0032367 | 0.054234 | -0.0041997 | 0.055941 | 0.073406 | -0.0015087 | 0.0011204 | 0.062109 | 0.023263 | 0.062528 | -66.5504 | -0.13595 | -66.5262 | 56.3617 | 56.2341 | 56.3993 | -66.7001 | -66.5459 | -0.13242 | -66.6171 | 56.2855 | 56.4221 | 56.3841 | -66.8913 | -0.15046 | -0.016454 | -0.000715 | 0.023436 | 0.1739 | -0.14404 | 0.021081 | -0.34157 | -0.092638 | 0.003762 | -0.067373 | 0.2742 | 0.043916 | 0.005909 | 122.9114 | 122.7838 | 122.9489 | 66.4137 | -123.0783 | 122.8352 | 122.9718 | 122.9338 | 66.4173 | -123.2694
325.2656 | 123.262 | -66.5451 | 56.3553 | 0.026888 | -0.02342 | -0.0032367 | 0.053166 | -0.0052687 | 0.055941 | 0.042884 | 0.00062833 | 0.0021894 | 0.061041 | 0.024332 | 0.06146 | -66.555 | -0.13137 | -66.5308 | 56.3617 | 56.257 | 56.4038 | -66.7093 | -66.5505 | -0.137 | -66.6171 | 56.2764 | 56.4221 | 56.3978 | -66.8913 | -0.1642 | 0.006434 | -0.009872 | 0.014279 | 0.17848 | -0.09826 | 0.048548 | -0.34615 | -0.078907 | -0.005395 | -0.071951 | 0.2742 | 0.066804 | 0.042533 | 122.9068 | 122.8021 | 122.9489 | 66.4137 | -123.0646 | 122.8215 | 122.9672 | 122.9429 | 66.4081 | -123.2465
326.2656 | 123.2254 | -66.568 | 56.3553 | 0.057412 | -0.02342 | -0.0032367 | 0.054234 | -0.0041997 | 0.05701 | 0.073406 | -0.00043967 | 0.0011204 | 0.059972 | 0.023263 | 0.06146 | -66.5458 | -0.13137 | -66.5262 | 56.3571 | 56.2341 | 56.4084 | -66.7047 | -66.5505 | -0.12327 | -66.6125 | 56.2718 | 56.4267 | 56.3887 | -66.8821 | -0.13673 | 0.001856 | 0.022173 | 0.041746 | 0.17848 | -0.12116 | 0.053126 | -0.3141 | -0.083485 | 0.017493 | -0.044485 | 0.26962 | 0.071382 | 0.033376 | 122.9251 | 122.8021 | 122.9764 | 66.4366 | -123.06 | 122.8398 | 122.9947 | 122.9567 | 66.4447 | -123.2374
327.2656 | 123.1888 | -66.5451 | 56.3873 | 0.026888 | -0.024489 | -0.0043047 | 0.052097 | -0.0041997 | 0.05701 | 0.042884 | -0.00043967 | 0.0011204 | 0.062109 | 0.024332 | 0.06146 | -66.5412 | -0.13595 | -66.5308 | 56.3617 | 56.2204 | 56.4038 | -66.7047 | -66.5551 | -0.137 | -66.6171 | 56.281 | 56.4175 | 56.3841 | -66.8821 | -0.15962 | -0.025609 | 0.003863 | 0.014279 | 0.1739 | -0.16693 | 0.016505 | -0.33699 | -0.10637 | -0.009974 | -0.071951 | 0.26504 | 0.030182 | -0.003246 | 122.9068 | 122.7655 | 122.9489 | 66.4092 | -123.0921 | 122.8261 | 122.9626 | 122.9292 | 66.4081 | -123.2694
328.2656 | 123.2254 | -66.5405 | 56.3553 | 0.04215 | -0.024489 | -0.0021677 | 0.055302 | -0.0052687 | 0.055941 | 0.027623 | -0.0025767 | 5.2373e-05 | 0.059972 | 0.023263 | 0.06146 | -66.5504 | -0.13137 | -66.5354 | 56.3663 | 56.2341 | 56.4084 | -66.7093 | -66.5505 | -0.137 | -66.6171 | 56.2764 | 56.4267 | 56.3841 | -66.8867 | -0.16878 | 0.011012 | -0.009871 | 0.005123 | 0.1739 | -0.12116 | 0.053126 | -0.34615 | -0.078907 | -0.009973 | -0.076529 | 0.26962 | 0.071382 | 0.028797 | 122.9068 | 122.7747 | 122.9489 | 66.4092 | -123.0646 | 122.8169 | 122.9672 | 122.9246 | 66.4035 | -123.242
329.2656 | 123.2529 | -66.5497 | 56.4011 | 0.057412 | -0.024489 | -0.0010997 | 0.053166 | -0.0031317 | 0.055941 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.024332 | 0.060391 | -66.5504 | -0.14053 | -66.5262 | 56.3571 | 56.2524 | 56.4038 | -66.7001 | -66.5459 | -0.137 | -66.6216 | 56.2764 | 56.4267 | 56.3887 | -66.8913 | -0.15046 | -0.04392 | -0.000715 | 0.023436 | 0.1739 | -0.14862 | 0.002772 | -0.34157 | -0.12468 | 0.003762 | -0.071952 | 0.26962 | 0.025606 | -0.0124 | 122.9068 | 122.8021 | 122.9535 | 66.4092 | -123.1012 | 122.8261 | 122.9764 | 122.9383 | 66.4127 | -123.2923
330.2656 | 123.3215 | -66.5588 | 56.3782 | 0.057412 | -0.024489 | -0.0032367 | 0.055302 | -0.0041997 | 0.058078 | 0.042884 | -0.00043967 | 0.0021894 | 0.059972 | 0.023263 | 0.06146 | -66.5504 | -0.14969 | -66.5308 | 56.3617 | 56.2616 | 56.4038 | -66.7093 | -66.5459 | -0.14616 | -66.6171 | 56.281 | 56.4267 | 56.3932 | -66.8913 | -0.15047 | -0.016454 | 0.00844 | 0.028012 | 0.17848 | -0.11657 | 0.02566 | -0.33241 | -0.097216 | 0.012917 | -0.058218 | 0.2742 | 0.048494 | 0.015067 | 122.9206 | 122.8204 | 122.9627 | 66.4092 | -123.0875 | 122.8398 | 122.9855 | 122.9521 | 66.4127 | -123.2694
331.2656 | 123.2666 | -66.5451 | 56.3644 | 0.026888 | -0.024489 | -0.0010997 | 0.054234 | -0.0041997 | 0.054873 | 0.073406 | 0.0016963 | 0.0021894 | 0.058904 | 0.024332 | 0.063596 | -66.5412 | -0.14053 | -66.5262 | 56.3663 | 56.2387 | 56.4038 | -66.6956 | -66.5413 | -0.14158 | -66.6216 | 56.281 | 56.4312 | 56.3841 | -66.8958 | -0.15046 | 0.001857 | 0.003863 | 0.018858 | 0.16932 | -0.12573 | 0.039393 | -0.35073 | -0.083483 | 0.003762 | -0.07653 | 0.2742 | 0.066806 | 0.019642 | 122.9114 | 122.7838 | 122.9489 | 66.4046 | -123.06 | 122.8261 | 122.9764 | 122.9292 | 66.4035 | -123.2603
332.2656 | 123.2437 | -66.5405 | 56.3782 | 0.057412 | -0.026626 | -0.0043047 | 0.054234 | -0.0052687 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.059972 | 0.023263 | 0.062528 | -66.5504 | -0.13595 | -66.5262 | 56.3663 | 56.2158 | 56.4038 | -66.7001 | -66.5413 | -0.15074 | -66.6171 | 56.281 | 56.4358 | 56.3841 | -66.8913 | -0.15962 | -0.011876 | -0.009871 | 0.01428 | 0.1739 | -0.16236 | 0.02566 | -0.35072 | -0.097216 | -0.000816 | -0.076529 | 0.2742 | 0.057651 | 0.005909 | 122.9068 | 122.7563 | 122.9444 | 66.4046 | -123.0783 | 122.8215 | 122.9764 | 122.9246 | 66.3898 | -123.2694
333.2656 | 123.1659 | -66.568 | 56.3828 | 0.011626 | -0.024489 | -0.0021677 | 0.054234 | -0.0041997 | 0.055941 | 0.042884 | -0.0015087 | 0.0011204 | 0.059972 | 0.023263 | 0.06146 | -66.555 | -0.14969 | -66.5262 | 56.3663 | 56.2021 | 56.4084 | -66.7093 | -66.5459 | -0.137 | -66.6125 | 56.281 | 56.4267 | 56.3429 | -66.8913 | -0.14131 | -0.016453 | 0.013016 | 0.041746 | 0.18306 | -0.18067 | 0.025661 | -0.32326 | -0.10179 | 0.022072 | -0.044485 | 0.27877 | 0.043917 | -0.039875 | 122.9343 | 122.7701 | 122.9764 | 66.4183 | -123.0921 | 122.849 | 122.9947 | 122.9109 | 66.431 | -123.274
334.2656 | 123.2025 | -66.5359 | 56.3873 | 0.04215 | -0.024489 | -0.0032367 | 0.055302 | -0.0052687 | 0.05701 | 0.073406 | -0.0025767 | 0.0011204 | 0.062109 | 0.024332 | 0.06146 | -66.5504 | -0.14511 | -66.5308 | 56.3709 | 56.2112 | 56.4038 | -66.7047 | -66.5505 | -0.15532 | -66.6171 | 56.281 | 56.4267 | 56.3795 | -66.9004 | -0.16877 | -0.016452 | -0.014448 | 0.005124 | 0.1739 | -0.17609 | 0.016505 | -0.36446 | -0.10637 | -0.01455 | -0.081106 | 0.28335 | 0.039339 | -0.007824 | 122.9068 | 122.7472 | 122.9398 | 66.3908 | -123.0921 | 122.8169 | 122.9626 | 122.9155 | 66.3806 | -123.2877
335.2656 | 123.2391 | -66.5359 | 56.3828 | 0.04215 | -0.02342 | -0.0032367 | 0.054234 | -0.0041997 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.059972 | 0.024332 | 0.06146 | -66.5458 | -0.14053 | -66.5308 | 56.3617 | 56.2067 | 56.4038 | -66.7047 | -66.5459 | -0.15532 | -66.6171 | 56.2855 | 56.4267 | 56.3703 | -66.8958 | -0.16877 | -0.021031 | -0.00987 | 0.005124 | 0.1739 | -0.17609 | 0.021083 | -0.35988 | -0.097215 | -0.009971 | -0.081106 | 0.27877 | 0.043917 | -0.012403 | 122.8977 | 122.7426 | 122.9398 | 66.3954 | -123.0875 | 122.8215 | 122.9626 | 122.9063 | 66.3806 | -123.2786
336.2656 | 123.1476 | -66.5863 | 56.3416 | 0.04215 | -0.02342 | -0.0021677 | 0.054234 | -0.0041997 | 0.05701 | 0.073406 | -0.0015087 | 0.0011204 | 0.059972 | 0.023263 | 0.06146 | -66.555 | -0.14511 | -66.5262 | 56.3571 | 56.2112 | 56.4084 | -66.7047 | -66.5597 | -0.15074 | -66.6079 | 56.2718 | 56.4267 | 56.3062 | -66.8913 | -0.11842 | 0.015589 | 0.031327 | 0.060057 | 0.17848 | -0.13032 | 0.066859 | -0.30495 | -0.069752 | 0.026646 | -0.021595 | 0.28335 | 0.085115 | -0.035306 | 122.9434 | 122.7975 | 122.9947 | 66.4412 | -123.0463 | 122.8581 | 123.013 | 122.8926 | 66.4356 | -123.2328
337.2656 | 123.2208 | -66.5314 | 56.3507 | 0.057412 | -0.02342 | -0.0032367 | 0.053166 | -0.0041997 | 0.054873 | 0.058145 | -0.00043967 | 0.0011204 | 0.059972 | 0.024332 | 0.062528 | -66.5412 | -0.15427 | -66.5308 | 56.3617 | 56.2387 | 56.4038 | -66.6956 | -66.5459 | -0.15074 | -66.6171 | 56.281 | 56.4221 | 56.352 | -66.8867 | -0.16419 | 0.011012 | -0.00987 | 0.000546 | 0.16474 | -0.112 | 0.053126 | -0.3553 | -0.06975 | -0.014549 | -0.085684 | 0.26962 | 0.071382 | 0.001325 | 122.8931 | 122.7701 | 122.9352 | 66.3771 | -123.0463 | 122.8123 | 122.9535 | 122.8834 | 66.3806 | -123.2374
338.2656 | 123.262 | -66.5359 | 56.3599 | 0.026888 | -0.025557 | -0.0032367 | 0.052097 | -0.0052687 | 0.058078 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.024332 | 0.060391 | -66.5458 | -0.15427 | -66.5262 | 56.3617 | 56.2387 | 56.413 | -66.7047 | -66.5459 | -0.1599 | -66.6171 | 56.2718 | 56.4267 | 56.3841 | -66.8913 | -0.16877 | 0.001857 | -0.00987 | 0.009703 | 0.17848 | -0.12115 | 0.053128 | -0.3553 | -0.088062 | -0.009971 | -0.081106 | 0.2742 | 0.066805 | 0.02422 | 122.8977 | 122.7747 | 122.9489 | 66.3817 | -123.0646 | 122.8078 | 122.9626 | 122.92 | 66.3761 | -123.2511
339.2656 | 123.1659 | -66.5588 | 56.4148 | 0.026888 | -0.02342 | -0.0032367 | 0.054234 | -0.0052687 | 0.055941 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.026468 | 0.06146 | -66.5458 | -0.16342 | -66.5262 | 56.3617 | 56.2524 | 56.4176 | -66.7093 | -66.5505 | -0.1599 | -66.6171 | 56.2718 | 56.4267 | 56.3887 | -66.8958 | -0.15047 | -0.053075 | 0.013018 | 0.032591 | 0.18306 | -0.16235 | 0.002775 | -0.33699 | -0.14299 | 0.008338 | -0.058218 | 0.27877 | 0.011873 | -0.026133 | 122.9206 | 122.8113 | 122.9764 | 66.3954 | -123.1241 | 122.8306 | 122.9855 | 122.9475 | 66.3989 | -123.3106
340.2656 | 123.1522 | -66.5634 | 56.3919 | 0.026888 | -0.024489 | -0.0032367 | 0.054234 | -0.0074047 | 0.055941 | 0.042884 | -0.0025767 | -0.0010156 | 0.061041 | 0.024332 | 0.062528 | -66.5504 | -0.15884 | -66.5262 | 56.3617 | 56.2708 | 56.4038 | -66.7093 | -66.5505 | -0.1599 | -66.6171 | 56.281 | 56.4267 | 56.3978 | -66.8913 | -0.14589 | -0.030187 | 0.013018 | 0.037169 | 0.18306 | -0.12114 | 0.011927 | -0.32784 | -0.11095 | 0.012916 | -0.05364 | 0.2742 | 0.034761 | 0.005912 | 122.9251 | 122.8342 | 122.9673 | 66.4046 | -123.1012 | 122.8444 | 122.9901 | 122.9612 | 66.4035 | -123.2832
341.2656 | 123.2162 | -66.5268 | 56.3507 | 0.04215 | -0.02342 | -0.0010997 | 0.052097 | -0.0052687 | 0.054873 | 0.042884 | 0.00062833 | -0.0010156 | 0.061041 | 0.024332 | 0.06146 | -66.5458 | -0.15884 | -66.5354 | 56.3663 | 56.2753 | 56.4084 | -66.7093 | -66.5505 | -0.15532 | -66.6125 | 56.2855 | 56.4267 | 56.3978 | -66.8913 | -0.18251 | 0.01559 | -0.019026 | -0.00861 | 0.1739 | -0.075366 | 0.057704 | -0.36446 | -0.065172 | -0.023706 | -0.085684 | 0.27877 | 0.07596 | 0.047111 | 122.8931 | 122.8021 | 122.9352 | 66.3679 | -123.06 | 122.8123 | 122.9535 | 122.9246 | 66.3715 | -123.242
342.2656 | 123.2254 | -66.5405 | 56.3736 | 0.026888 | -0.025557 | -0.0043047 | 0.053166 | -0.0052687 | 0.05701 | 0.058145 | 0.00062833 | 0.0011204 | 0.061041 | 0.022195 | 0.060391 | -66.5458 | -0.14053 | -66.5308 | 56.3663 | 56.2799 | 56.4084 | -66.7047 | -66.5459 | -0.15532 | -66.6125 | 56.2718 | 56.4267 | 56.3887 | -66.8867 | -0.1642 | -0.007298 | -0.005293 | 0.009701 | 0.1739 | -0.093675 | 0.034816 | -0.34615 | -0.10179 | -0.005394 | -0.071951 | 0.2742 | 0.053072 | 0.015066 | 122.9068 | 122.8204 | 122.9489 | 66.4 | -123.0783 | 122.8123 | 122.9672 | 122.9292 | 66.3852 | -123.2603
343.2656 | 123.262 | -66.5634 | 56.4011 | 0.057412 | -0.025557 | -0.0053737 | 0.055302 | -0.0041997 | 0.05701 | 0.042884 | -0.0015087 | 0.0011204 | 0.061041 | 0.0254 | 0.06146 | -66.5458 | -0.13595 | -66.5308 | 56.3617 | 56.2891 | 56.413 | -66.7093 | -66.5505 | -0.15532 | -66.6171 | 56.2764 | 56.4312 | 56.3978 | -66.8913 | -0.14589 | -0.039342 | 0.017596 | 0.03259 | 0.17848 | -0.11198 | 0.011929 | -0.32784 | -0.12468 | 0.012916 | -0.05364 | 0.2742 | 0.030185 | -0.003243 | 122.9251 | 122.8525 | 122.9764 | 66.4275 | -123.1104 | 122.8398 | 122.9947 | 122.9612 | 66.4081 | -123.2923
344.2812 | 123.1338 | -66.5726 | 56.4194 | 0.04215 | -0.025557 | -0.0032367 | 0.053166 | -0.0041997 | 0.05701 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.026468 | 0.060391 | -66.5504 | -0.12679 | -66.5308 | 56.3617 | 56.2799 | 56.4176 | -66.7093 | -66.5505 | -0.16448 | -66.6125 | 56.2764 | 56.4312 | 56.3978 | -66.8913 | -0.13673 | -0.057653 | 0.022173 | 0.041745 | 0.17848 | -0.13945 | -0.001803 | -0.31868 | -0.14299 | 0.022071 | -0.039907 | 0.27877 | 0.011874 | -0.021554 | 122.9343 | 122.8525 | 122.9901 | 66.4458 | -123.1287 | 122.849 | 123.0038 | 122.9704 | 66.4081 | -123.3106
345.2656 | 123.2391 | -66.5588 | 56.3461 | 0.026888 | -0.02342 | -0.0032367 | 0.055302 | -0.0052687 | 0.05701 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.024332 | 0.060391 | -66.5458 | -0.11764 | -66.5354 | 56.3617 | 56.2845 | 56.4038 | -66.7047 | -66.5551 | -0.16448 | -66.6171 | 56.2718 | 56.4312 | 56.3978 | -66.8913 | -0.14589 | 0.01559 | 0.013018 | 0.023434 | 0.16932 | -0.061631 | 0.057704 | -0.33241 | -0.074329 | 0.003759 | -0.058218 | 0.2742 | 0.085117 | 0.051689 | 122.9206 | 122.8433 | 122.9627 | 66.4412 | -123.0509 | 122.8306 | 122.9901 | 122.9567 | 66.3944 | -123.2374
346.2656 | 123.1888 | -66.5405 | 56.3644 | 0.04215 | -0.026626 | -0.0010997 | 0.052097 | -0.0052687 | 0.053805 | 0.073406 | -0.0025767 | 0.0011204 | 0.058904 | 0.024332 | 0.06146 | -66.5504 | -0.11306 | -66.5217 | 56.3663 | 56.2891 | 56.413 | -66.7047 | -66.5551 | -0.16448 | -66.6171 | 56.281 | 56.4358 | 56.3978 | -66.8867 | -0.1642 | 0.001857 | -0.009871 | 0.018858 | 0.18306 | -0.075363 | 0.04855 | -0.34615 | -0.083483 | -0.014552 | -0.076529 | 0.26962 | 0.071384 | 0.033378 | 122.9068 | 122.8296 | 122.9535 | 66.4275 | -123.0692 | 122.8215 | 122.9764 | 122.9383 | 66.3761 | -123.2511
347.2656 | 123.1796 | -66.5634 | 56.3828 | 0.026888 | -0.025557 | -0.0053737 | 0.054234 | -0.0052687 | 0.055941 | 0.073406 | -0.0015087 | -0.0010156 | 0.061041 | 0.0254 | 0.062528 | -66.5504 | -0.11306 | -66.5308 | 56.3663 | 56.2845 | 56.4038 | -66.7047 | -66.5459 | -0.1599 | -66.6079 | 56.281 | 56.4267 | 56.3932 | -66.8821 | -0.14131 | -0.016453 | 0.013018 | 0.03259 | 0.1739 | -0.098252 | 0.021083 | -0.31868 | -0.10179 | 0.017495 | -0.044483 | 0.27419 | 0.043917 | 0.01049 | 122.9297 | 122.8479 | 122.9673 | 66.4504 | -123.0875 | 122.8444 | 122.9901 | 122.9567 | 66.4035 | -123.2648
348.2656 | 123.2391 | -66.5405 | 56.3644 | 0.04215 | -0.026626 | -0.0032367 | 0.053166 | -0.0052687 | 0.058078 | 0.058145 | 0.00062833 | 5.2373e-05 | 0.059972 | 0.024332 | 0.06146 | -66.5412 | -0.10848 | -66.5354 | 56.3663 | 56.2799 | 56.4084 | -66.7001 | -66.5459 | -0.16905 | -66.6079 | 56.2764 | 56.4358 | 56.3932 | -66.8867 | -0.15962 | 0.001857 | -0.000715 | 0.005123 | 0.16474 | -0.08452 | 0.043971 | -0.34615 | -0.088062 | -0.005394 | -0.067372 | 0.27877 | 0.071384 | 0.0288 | 122.9068 | 122.8204 | 122.9489 | 66.432 | -123.0646 | 122.8169 | 122.9764 | 122.9338 | 66.3715 | -123.2511
349.2812 | 123.2071 | -66.5771 | 56.3965 | 0.057412 | -0.024489 | -0.0032367 | 0.053166 | -0.0052687 | 0.05701 | 0.058145 | 0.00062833 | -0.0010156 | 0.059972 | 0.027537 | 0.06146 | -66.5458 | -0.10848 | -66.5308 | 56.3617 | 56.2799 | 56.413 | -66.7047 | -66.5459 | -0.16448 | -66.6125 | 56.281 | 56.4358 | 56.3887 | -66.8958 | -0.12758 | -0.034764 | 0.031328 | 0.046322 | 0.1739 | -0.11656 | 0.016507 | -0.31868 | -0.11553 | 0.031227 | -0.03533 | 0.28335 | 0.039341 | -0.007822 | 122.9389 | 122.8571 | 122.9901 | 66.4687 | -123.1012 | 122.8581 | 123.013 | 122.9658 | 66.4127 | -123.2923
350.2656 | 123.1293 | -66.5359 | 56.4148 | 0.057412 | -0.026626 | -0.0043047 | 0.053166 | -0.0052687 | 0.054873 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.061041 | 0.026468 | 0.06146 | -66.5504 | -0.10848 | -66.5262 | 56.3617 | 56.2845 | 56.4176 | -66.7139 | -66.5459 | -0.1599 | -66.6125 | 56.281 | 56.4358 | 56.3978 | -66.8867 | -0.17793 | -0.053075 | -0.014448 | 0.009703 | 0.18764 | -0.1303 | 0.002775 | -0.35072 | -0.13384 | -0.009971 | -0.076528 | 0.2742 | 0.02103 | -0.016976 | 122.8977 | 122.8204 | 122.9535 | 66.4275 | -123.1287 | 122.8169 | 122.9718 | 122.9338 | 66.3761 | -123.3015
351.2656 | 123.262 | -66.5497 | 56.3736 | 0.057412 | -0.026626 | -0.0043047 | 0.054234 | -0.0052687 | 0.05701 | 0.058145 | -0.00043967 | 0.0011204 | 0.058904 | 0.026468 | 0.060391 | -66.5458 | -0.099323 | -66.5262 | 56.3663 | 56.2845 | 56.4084 | -66.7001 | -66.5459 | -0.16448 | -66.6125 | 56.2764 | 56.4358 | 56.4024 | -66.8913 | -0.15046 | -0.007298 | 0.003863 | 0.023436 | 0.1739 | -0.089097 | 0.034816 | -0.34157 | -0.097217 | 0.003762 | -0.062795 | 0.27877 | 0.062229 | 0.028802 | 122.916 | 122.8342 | 122.9581 | 66.4504 | -123.0737 | 122.8261 | 122.9855 | 122.9521 | 66.3852 | -123.2648
352.2656 | 123.2254 | -66.5314 | 56.3782 | 0.04215 | -0.027694 | -0.0043047 | 0.054234 | -0.0052687 | 0.05701 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.062109 | 0.0254 | 0.060391 | -66.5458 | -0.099323 | -66.5262 | 56.3617 | 56.2799 | 56.413 | -66.7047 | -66.5459 | -0.16905 | -66.6033 | 56.2764 | 56.4358 | 56.3978 | -66.9004 | -0.17335 | -0.016454 | -0.014448 | 0.005125 | 0.17848 | -0.098253 | 0.034817 | -0.36904 | -0.1018 | -0.014549 | -0.071948 | 0.29709 | 0.057651 | 0.019645 | 122.8931 | 122.8113 | 122.9444 | 66.432 | -123.0829 | 122.8078 | 122.9672 | 122.9292 | 66.3623 | -123.2786
353.2656 | 123.1384 | -66.5588 | 56.4239 | 0.057412 | -0.026626 | -0.0032367 | 0.053166 | -0.0052687 | 0.05701 | 0.073406 | -0.00043967 | 5.2373e-05 | 0.059972 | 0.0254 | 0.059323 | -66.5504 | -0.10848 | -66.5262 | 56.3571 | 56.2845 | 56.4084 | -66.7047 | -66.5505 | -0.16905 | -66.6079 | 56.281 | 56.4496 | 56.4024 | -66.8867 | -0.14589 | -0.066808 | 0.00844 | 0.032591 | 0.17848 | -0.13945 | -0.015538 | -0.32784 | -0.14299 | 0.008338 | -0.049061 | 0.27877 | 0.025611 | -0.021552 | 122.916 | 122.8433 | 122.9672 | 66.4504 | -123.1287 | 122.8398 | 123.0084 | 122.9612 | 66.3898 | -123.3106
354.2656 | 123.2574 | -66.5726 | 56.3644 | 0.026888 | -0.02342 | -0.0043047 | 0.052097 | -0.0052687 | 0.055941 | 0.042884 | -0.0025767 | 0.0011204 | 0.062109 | 0.024332 | 0.060391 | -66.5412 | -0.1039 | -66.5217 | 56.3617 | 56.2845 | 56.413 | -66.7093 | -66.5551 | -0.17363 | -66.6079 | 56.2855 | 56.4358 | 56.4024 | -66.8867 | -0.13673 | -0.002721 | 0.031329 | 0.050902 | 0.18764 | -0.079942 | 0.04855 | -0.3141 | -0.078905 | 0.017492 | -0.035328 | 0.27877 | 0.071384 | 0.037957 | 122.9343 | 122.8571 | 122.9856 | 66.4687 | -123.0737 | 122.8581 | 123.0084 | 122.975 | 66.3989 | -123.2511
355.2656 | 123.2758 | -66.5405 | 56.3782 | 0.04215 | -0.025557 | -0.0032367 | 0.054234 | -0.0063367 | 0.054873 | 0.042884 | -0.00043967 | 0.0011204 | 0.058904 | 0.026468 | 0.06146 | -66.5458 | -0.10848 | -66.5308 | 56.3617 | 56.2799 | 56.4176 | -66.7001 | -66.5459 | -0.17821 | -66.6125 | 56.2764 | 56.4312 | 56.3978 | -66.8867 | -0.15962 | -0.016454 | -0.005293 | 0.009701 | 0.16932 | -0.098253 | 0.039396 | -0.34615 | -0.1018 | -0.005394 | -0.071951 | 0.2742 | 0.053073 | 0.019645 | 122.9022 | 122.8204 | 122.9581 | 66.432 | -123.0783 | 122.8169 | 122.9718 | 122.9383 | 66.3623 | -123.2648
356.2656 | 123.2254 | -66.5451 | 56.3736 | 0.04215 | -0.026626 | -0.0043047 | 0.053166 | -0.0041997 | 0.054873 | 0.058145 | -0.0015087 | 0.0021894 | 0.061041 | 0.027537 | 0.06146 | -66.5458 | -0.099323 | -66.5262 | 56.3617 | 56.2891 | 56.413 | -66.7001 | -66.5505 | -0.17821 | -66.6079 | 56.2855 | 56.4312 | 56.3932 | -66.8913 | -0.15504 | -0.011876 | -0.000715 | 0.018858 | 0.1739 | -0.084518 | 0.039395 | -0.34615 | -0.08806 | -0.005395 | -0.062794 | 0.28335 | 0.057651 | 0.019645 | 122.9068 | 122.8342 | 122.9581 | 66.4458 | -123.0737 | 122.8306 | 122.9764 | 122.9383 | 66.3669 | -123.2648
357.2656 | 123.2529 | -66.5451 | 56.3599 | 0.026888 | -0.026626 | -0.0043047 | 0.052097 | -0.0041997 | 0.054873 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.027537 | 0.062528 | -66.5504 | -0.1039 | -66.5262 | 56.3663 | 56.2891 | 56.4084 | -66.7047 | -66.5459 | -0.17821 | -66.6125 | 56.281 | 56.4312 | 56.4024 | -66.8958 | -0.15962 | 0.006435 | -0.005293 | 0.018858 | 0.17848 | -0.070785 | 0.048549 | -0.35073 | -0.078905 | -0.000816 | -0.067373 | 0.28335 | 0.071384 | 0.042535 | 122.9114 | 122.8342 | 122.9535 | 66.4412 | -123.0646 | 122.8261 | 122.9764 | 122.9475 | 66.3669 | -123.2557
358.2656 | 123.2758 | -66.5497 | 56.3324 | 0.04215 | -0.026626 | -0.0032367 | 0.053166 | -0.0041997 | 0.054873 | 0.058145 | -0.0025767 | 0.0011204 | 0.059972 | 0.026468 | 0.062528 | -66.5504 | -0.1039 | -66.5171 | 56.3663 | 56.2891 | 56.4176 | -66.7047 | -66.5505 | -0.17821 | -66.6033 | 56.281 | 56.4312 | 56.3978 | -66.8867 | -0.15504 | 0.033901 | -0.000715 | 0.032592 | 0.18763 | -0.043319 | 0.085173 | -0.33699 | -0.051439 | -0.000817 | -0.053637 | 0.28335 | 0.09885 | 0.065422 | 122.916 | 122.8388 | 122.9673 | 66.4458 | -123.0371 | 122.8306 | 122.9809 | 122.9475 | 66.3715 | -123.2191
359.2656 | 123.1338 | -66.568 | 56.4148 | 0.026888 | -0.026626 | -0.0043047 | 0.053166 | -0.0063367 | 0.053805 | 0.073406 | -0.0025767 | -0.0010156 | 0.059972 | 0.028605 | 0.060391 | -66.5412 | -0.10848 | -66.5217 | 56.3709 | 56.2937 | 56.4084 | -66.7093 | -66.5551 | -0.18279 | -66.6079 | 56.2855 | 56.4404 | 56.407 | -66.8913 | -0.14131 | -0.043918 | 0.026751 | 0.046324 | 0.18764 | -0.12114 | -0.006383 | -0.32326 | -0.12926 | 0.012914 | -0.039906 | 0.28335 | 0.025609 | -0.007819 | 122.9389 | 122.8616 | 122.9764 | 66.4595 | -123.1241 | 122.8535 | 123.0084 | 122.975 | 66.3852 | -123.306
360.2656 | 123.1705 | -66.5497 | 56.4285 | 0.057412 | -0.026626 | -0.0021677 | 0.055302 | -0.0063367 | 0.054873 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.027537 | 0.06146 | -66.5504 | -0.099323 | -66.5308 | 56.3709 | 56.2845 | 56.4176 | -66.7047 | -66.5597 | -0.18279 | -66.6125 | 56.281 | 56.4312 | 56.4024 | -66.8867 | -0.15504 | -0.057651 | -0.000715 | 0.018857 | 0.1739 | -0.14403 | -0.010958 | -0.33699 | -0.14757 | -0.009975 | -0.062795 | 0.2742 | 0.002719 | -0.02613 | 122.9206 | 122.8342 | 122.9673 | 66.4504 | -123.1333 | 122.8306 | 122.9809 | 122.9521 | 66.3669 | -123.3152
361.2656 | 123.2071 | -66.5405 | 56.3324 | 0.04215 | -0.025557 | -0.0043047 | 0.054234 | -0.0041997 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.0254 | 0.060391 | -66.5504 | -0.099323 | -66.5262 | 56.3663 | 56.2845 | 56.4084 | -66.7047 | -66.5551 | -0.18279 | -66.6079 | 56.281 | 56.4312 | 56.3978 | -66.8867 | -0.1642 | 0.033901 | -0.009871 | 0.01428 | 0.17848 | -0.047898 | 0.076015 | -0.34615 | -0.051439 | -0.014552 | -0.067372 | 0.27877 | 0.09885 | 0.065422 | 122.9068 | 122.825 | 122.9489 | 66.4412 | -123.0371 | 122.8215 | 122.9718 | 122.9383 | 66.3577 | -123.2191
362.2656 | 123.262 | -66.5359 | 56.3644 | 0.057412 | -0.027694 | -0.0043047 | 0.053166 | -0.0052687 | 0.055941 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.062109 | 0.026468 | 0.060391 | -66.5458 | -0.1039 | -66.5262 | 56.3663 | 56.2799 | 56.413 | -66.7001 | -66.5459 | -0.19195 | -66.6125 | 56.281 | 56.4312 | 56.3932 | -66.8913 | -0.1642 | 0.001857 | -0.00987 | 0.009703 | 0.1739 | -0.08452 | 0.04855 | -0.3553 | -0.083483 | -0.009971 | -0.076528 | 0.27877 | 0.066806 | 0.0288 | 122.9022 | 122.8159 | 122.9489 | 66.432 | -123.0646 | 122.8169 | 122.9672 | 122.9292 | 66.344 | -123.2557
363.2656 | 123.2346 | -66.5405 | 56.3553 | 0.04215 | -0.026626 | -0.0032367 | 0.053166 | -0.0052687 | 0.058078 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.061041 | 0.026468 | 0.060391 | -66.5458 | -0.10848 | -66.5262 | 56.3663 | 56.2845 | 56.4221 | -66.7001 | -66.5459 | -0.17821 | -66.6079 | 56.2764 | 56.4312 | 56.4024 | -66.8913 | -0.15962 | 0.011012 | -0.005293 | 0.01428 | 0.1739 | -0.070787 | 0.066862 | -0.35072 | -0.078907 | -0.005394 | -0.067372 | 0.28335 | 0.075961 | 0.047112 | 122.9068 | 122.825 | 122.9627 | 66.432 | -123.0554 | 122.8169 | 122.9718 | 122.9429 | 66.3623 | -123.2465
364.2656 | 123.2529 | -66.5085 | 56.4148 | 0.026888 | -0.025557 | -0.0032367 | 0.054234 | -0.0041997 | 0.055941 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.027537 | 0.060391 | -66.5504 | -0.1039 | -66.5262 | 56.3663 | 56.257 | 56.4038 | -66.7001 | -66.5505 | -0.19195 | -66.6171 | 56.2901 | 56.4312 | 56.3932 | -66.8913 | -0.19166 | -0.048497 | -0.041914 | -0.017763 | 0.1739 | -0.15777 | -0.010961 | -0.38277 | -0.12468 | -0.042016 | -0.10857 | 0.2742 | 0.016452 | -0.021554 | 122.8748 | 122.7655 | 122.9123 | 66.4046 | -123.1149 | 122.7986 | 122.9397 | 122.9017 | 66.3165 | -123.306
365.2656 | 123.1659 | -66.5039 | 56.4972 | 0.057412 | -0.028762 | -0.0043047 | 0.052097 | -0.0052687 | 0.053805 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.061041 | 0.0254 | 0.06146 | -66.5458 | -0.094744 | -66.5308 | 56.3709 | 56.2753 | 56.4084 | -66.7047 | -66.5551 | -0.19195 | -66.6125 | 56.2855 | 56.4267 | 56.4024 | -66.8867 | -0.20082 | -0.12631 | -0.041914 | -0.02692 | 0.1739 | -0.22185 | -0.08878 | -0.38277 | -0.21166 | -0.051173 | -0.10857 | 0.2742 | -0.070524 | -0.094794 | 122.8748 | 122.7792 | 122.9123 | 66.4092 | -123.2019 | 122.7894 | 122.9306 | 122.9063 | 66.312 | -123.3839
366.2656 | 123.2025 | -66.5771 | 56.3416 | 0.011626 | -0.026626 | -0.0021677 | 0.054234 | -0.0063367 | 0.055941 | 0.042884 | -0.00043967 | 0.0011204 | 0.059972 | 0.026468 | 0.062528 | -66.5458 | -0.1039 | -66.5308 | 56.3663 | 56.2662 | 56.413 | -66.6956 | -66.5505 | -0.19195 | -66.6125 | 56.2855 | 56.4267 | 56.3932 | -66.8867 | -0.11842 | 0.024745 | 0.031328 | 0.046322 | 0.16474 | -0.075369 | 0.071438 | -0.30953 | -0.056017 | 0.026648 | -0.03533 | 0.2742 | 0.085115 | 0.051688 | 122.9434 | 122.8433 | 122.9901 | 66.4732 | -123.0371 | 122.8627 | 123.0038 | 122.9704 | 66.3852 | -123.2282
367.2656 | 123.1384 | -66.6 | 56.4102 | 0.04215 | -0.028762 | -0.0032367 | 0.052097 | -0.0052687 | 0.05701 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.061041 | 0.0254 | 0.060391 | -66.5367 | -0.094744 | -66.5308 | 56.3617 | 56.2158 | 56.4176 | -66.7139 | -66.5368 | -0.19653 | -66.6079 | 56.2855 | 56.4312 | 56.3749 | -66.8867 | -0.11385 | -0.048497 | 0.063374 | 0.069211 | 0.18306 | -0.1944 | 0.007353 | -0.28664 | -0.12468 | 0.063273 | -0.007862 | 0.27877 | 0.02103 | -0.035291 | 122.9618 | 122.8159 | 123.0176 | 66.5053 | -123.1241 | 122.8856 | 123.0313 | 122.975 | 66.4035 | -123.2969
368.2656 | 123.2346 | -66.5405 | 56.369 | 0.04215 | -0.026626 | -0.0043047 | 0.054234 | -0.0063367 | 0.05701 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.059972 | 0.026468 | 0.058255 | -66.5412 | -0.099323 | -66.5217 | 56.3663 | 56.2112 | 56.4176 | -66.6956 | -66.5413 | -0.19195 | -66.6171 | 56.2764 | 56.4312 | 56.3703 | -66.8958 | -0.15504 | -0.002721 | -0.000715 | 0.018858 | 0.1739 | -0.15778 | 0.048551 | -0.3553 | -0.09264 | -0.000816 | -0.076529 | 0.27877 | 0.062228 | 0.001329 | 122.9068 | 122.7518 | 122.9581 | 66.4412 | -123.0646 | 122.8169 | 122.9718 | 122.9109 | 66.3486 | -123.2648
369.2656 | 123.175 | -66.5359 | 56.3828 | 0.04215 | -0.029831 | -0.0032367 | 0.053166 | -0.0052687 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.061041 | 0.027537 | 0.06146 | -66.5504 | -0.094744 | -66.5308 | 56.3663 | 56.2021 | 56.413 | -66.7001 | -66.5551 | -0.2011 | -66.6125 | 56.2764 | 56.4312 | 56.3658 | -66.8913 | -0.1642 | -0.016453 | -0.014448 | 0.005124 | 0.16932 | -0.18067 | 0.03024 | -0.3553 | -0.10637 | -0.019129 | -0.076528 | 0.27877 | 0.048496 | -0.016982 | 122.9022 | 122.738 | 122.9489 | 66.4412 | -123.0829 | 122.8123 | 122.9672 | 122.9017 | 66.3348 | -123.274
370.2656 | 123.2071 | -66.5451 | 56.4011 | 0.072674 | -0.027694 | -0.0032367 | 0.052097 | -0.0052687 | 0.053805 | 0.058145 | -0.0015087 | 0.0011204 | 0.058904 | 0.028605 | 0.060391 | -66.5504 | -0.094744 | -66.5217 | 56.3617 | 56.225 | 56.4084 | -66.7047 | -66.5505 | -0.19653 | -66.6079 | 56.281 | 56.4221 | 56.3795 | -66.8821 | -0.15962 | -0.039342 | -0.005293 | 0.023436 | 0.18306 | -0.17609 | 0.00735 | -0.33699 | -0.1201 | -0.005395 | -0.062794 | 0.27419 | 0.021028 | -0.021557 | 122.9068 | 122.7701 | 122.9535 | 66.4504 | -123.1058 | 122.8261 | 122.9672 | 122.9246 | 66.3486 | -123.2832
371.2656 | 123.1842 | -66.5588 | 56.3965 | 0.026888 | -0.027694 | -0.0032367 | 0.053166 | -0.0052687 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.059972 | 0.027537 | 0.06146 | -66.5458 | -0.099323 | -66.5262 | 56.3617 | 56.2341 | 56.413 | -66.7047 | -66.5459 | -0.2011 | -66.6079 | 56.281 | 56.4404 | 56.3978 | -66.8867 | -0.14589 | -0.034764 | 0.013018 | 0.032591 | 0.17848 | -0.16235 | 0.016507 | -0.32784 | -0.11553 | 0.012917 | -0.049061 | 0.27877 | 0.04392 | 0.001335 | 122.9206 | 122.793 | 122.9718 | 66.4595 | -123.1012 | 122.8398 | 122.9992 | 122.9567 | 66.3577 | -123.2832
372.2656 | 123.2437 | -66.5543 | 56.3644 | 0.057412 | -0.027694 | -0.0032367 | 0.053166 | -0.0052687 | 0.054873 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.061041 | 0.027537 | 0.06146 | -66.5458 | -0.099323 | -66.5262 | 56.3617 | 56.257 | 56.4084 | -66.7093 | -66.5459 | -0.20568 | -66.6079 | 56.2855 | 56.4312 | 56.3978 | -66.8867 | -0.15504 | -0.002721 | 0.00844 | 0.028013 | 0.18306 | -0.10741 | 0.043971 | -0.33241 | -0.078905 | 0.008339 | -0.053639 | 0.27877 | 0.066806 | 0.033378 | 122.916 | 122.8113 | 122.9627 | 66.4549 | -123.0737 | 122.8398 | 122.9855 | 122.9521 | 66.3486 | -123.2511
373.2656 | 123.2208 | -66.5771 | 56.3736 | 0.057412 | -0.027694 | -0.0032367 | 0.053166 | -0.0052687 | 0.054873 | 0.042884 | -0.0025767 | -0.0010156 | 0.059972 | 0.027537 | 0.060391 | -66.5504 | -0.094744 | -66.5217 | 56.3663 | 56.2479 | 56.4176 | -66.7047 | -66.5505 | -0.19653 | -66.6125 | 56.2901 | 56.4358 | 56.4024 | -66.9004 | -0.12758 | -0.007298 | 0.02675 | 0.055479 | 0.18306 | -0.12573 | 0.043974 | -0.32326 | -0.083481 | 0.026648 | -0.03533 | 0.28793 | 0.062229 | 0.028802 | 122.9434 | 122.825 | 122.9947 | 66.4824 | -123.0783 | 122.8673 | 123.013 | 122.9795 | 66.3806 | -123.274
374.2656 | 123.2208 | -66.5268 | 56.4102 | 0.026888 | -0.027694 | -0.0043047 | 0.053166 | -0.0052687 | 0.05701 | 0.073406 | -0.0015087 | 0.0021894 | 0.061041 | 0.027537 | 0.06146 | -66.5458 | -0.094744 | -66.5308 | 56.3663 | 56.257 | 56.4084 | -66.7047 | -66.5505 | -0.2011 | -66.5987 | 56.281 | 56.4267 | 56.3978 | -66.8913 | -0.17793 | -0.043919 | -0.019026 | -0.004032 | 0.1739 | -0.15319 | -0.001805 | -0.36446 | -0.12926 | -0.023706 | -0.071947 | 0.29251 | 0.016451 | -0.012398 | 122.8931 | 122.7838 | 122.9352 | 66.432 | -123.1149 | 122.8078 | 122.9535 | 122.9246 | 66.3257 | -123.3015
375.2656 | 123.262 | -66.5726 | 56.4285 | 0.057412 | -0.028762 | -0.0043047 | 0.053166 | -0.0041997 | 0.05701 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.029673 | 0.06146 | -66.5458 | -0.1039 | -66.5262 | 56.3709 | 56.2708 | 56.4084 | -66.7093 | -66.5413 | -0.21026 | -66.6033 | 56.2901 | 56.4358 | 56.407 | -66.8958 | -0.13673 | -0.057651 | 0.026751 | 0.046324 | 0.18306 | -0.15776 | -0.020116 | -0.32326 | -0.13841 | 0.031228 | -0.030749 | 0.29251 | 0.007297 | -0.021552 | 122.9434 | 122.8433 | 122.981 | 66.4687 | -123.1378 | 122.8627 | 123.0084 | 122.9795 | 66.3623 | -123.3244
376.2656 | 123.3032 | -66.5588 | 56.3324 | 0.04215 | -0.029831 | -0.0021677 | 0.052097 | -0.0052687 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.059972 | 0.027537 | 0.06146 | -66.5458 | -0.099323 | -66.5217 | 56.3663 | 56.2753 | 56.4176 | -66.7001 | -66.5505 | -0.21026 | -66.6125 | 56.2855 | 56.4404 | 56.3978 | -66.8913 | -0.14131 | 0.033901 | 0.013018 | 0.037169 | 0.17848 | -0.057055 | 0.085173 | -0.33241 | -0.046861 | 0.008338 | -0.05364 | 0.27877 | 0.10801 | 0.065422 | 122.9251 | 122.8342 | 122.9764 | 66.4595 | -123.0325 | 122.8444 | 122.9992 | 122.9567 | 66.3486 | -123.2236
377.2656 | 123.1613 | -66.6 | 56.3828 | 0.057412 | -0.028762 | -0.0043047 | 0.053166 | -0.0063367 | 0.055941 | 0.027623 | -0.0036447 | 0.0021894 | 0.061041 | 0.027537 | 0.060391 | -66.5504 | -0.094744 | -66.5171 | 56.3617 | 56.2891 | 56.4176 | -66.7047 | -66.5642 | -0.21026 | -66.6079 | 56.2901 | 56.4358 | 56.407 | -66.8867 | -0.10469 | -0.021031 | 0.049639 | 0.082946 | 0.18763 | -0.093673 | 0.034819 | -0.28664 | -0.092636 | 0.035801 | -0.007862 | 0.27877 | 0.053074 | 0.024225 | 122.9618 | 122.8891 | 123.0176 | 66.5053 | -123.0875 | 122.8902 | 123.0359 | 123.007 | 66.3898 | -123.2694
378.2656 | 123.1155 | -66.5863 | 56.3919 | 0.04215 | -0.027694 | -0.0032367 | 0.053166 | -0.0063367 | 0.053805 | 0.073406 | -0.0015087 | 0.0011204 | 0.061041 | 0.028605 | 0.06146 | -66.5412 | -0.099323 | -66.5217 | 56.3617 | 56.2891 | 56.413 | -66.7047 | -66.5505 | -0.21026 | -66.6079 | 56.2855 | 56.4358 | 56.4024 | -66.8913 | -0.11842 | -0.030187 | 0.045062 | 0.064635 | 0.18306 | -0.10283 | 0.021084 | -0.30495 | -0.10637 | 0.035804 | -0.021595 | 0.28335 | 0.043918 | 0.010491 | 122.948 | 122.8754 | 122.9993 | 66.487 | -123.0966 | 122.8718 | 123.0221 | 122.9887 | 66.376 | -123.2832
379.2656 | 123.1934 | -66.5726 | 56.3507 | 0.04215 | -0.028762 | -0.0032367 | 0.051029 | -0.0063367 | 0.05701 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.062109 | 0.026468 | 0.060391 | -66.5504 | -0.085587 | -66.5262 | 56.3663 | 56.2937 | 56.413 | -66.7047 | -66.5505 | -0.21026 | -66.6079 | 56.2901 | 56.4358 | 56.3978 | -66.8821 | -0.13215 | 0.01559 | 0.022173 | 0.046324 | 0.17848 | -0.057051 | 0.062283 | -0.30952 | -0.060593 | 0.022071 | -0.035328 | 0.27419 | 0.085117 | 0.047111 | 122.9389 | 122.8662 | 122.9856 | 66.487 | -123.0554 | 122.8627 | 123.0084 | 122.9704 | 66.3623 | -123.2328
380.2656 | 123.175 | -66.5909 | 56.3965 | 0.026888 | -0.028762 | -0.0032367 | 0.052097 | -0.0052687 | 0.05701 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.059972 | 0.028605 | 0.06146 | -66.5504 | -0.094744 | -66.5171 | 56.3709 | 56.2616 | 56.4084 | -66.7047 | -66.5551 | -0.21484 | -66.6125 | 56.2764 | 56.4404 | 56.4024 | -66.8913 | -0.11384 | -0.025607 | 0.040483 | 0.07379 | 0.18763 | -0.13488 | 0.011928 | -0.30037 | -0.12011 | 0.035802 | -0.021597 | 0.27877 | 0.04392 | 0.005914 | 122.9618 | 122.8525 | 122.9993 | 66.4961 | -123.1012 | 122.8673 | 123.0313 | 122.9933 | 66.376 | -123.2877
381.2656 | 123.1476 | -66.5726 | 56.4102 | 0.026888 | -0.028762 | -0.0032367 | 0.052097 | -0.0052687 | 0.054873 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.030742 | 0.060391 | -66.5412 | -0.094744 | -66.5217 | 56.38 | 56.225 | 56.4221 | -66.7047 | -66.5459 | -0.21026 | -66.6125 | 56.281 | 56.4404 | 56.4116 | -66.8913 | -0.13215 | -0.030183 | 0.031329 | 0.050902 | 0.18306 | -0.18524 | 0.011931 | -0.31868 | -0.12926 | 0.02665 | -0.039907 | 0.27877 | 0.030187 | 0.001338 | 122.9526 | 122.7975 | 122.9947 | 66.4778 | -123.1149 | 122.8535 | 123.013 | 122.9841 | 66.3623 | -123.3015
382.2656 | 123.175 | -66.5405 | 56.4056 | 0.072674 | -0.028762 | -0.0032367 | 0.054234 | -0.0063367 | 0.055941 | 0.058145 | -0.00043967 | 0.0021894 | 0.059972 | 0.026468 | 0.062528 | -66.5412 | -0.099323 | -66.5217 | 56.38 | 56.2387 | 56.4267 | -66.7139 | -66.5505 | -0.21484 | -66.6079 | 56.2764 | 56.4404 | 56.407 | -66.8913 | -0.17336 | -0.025606 | -0.000715 | 0.018858 | 0.19221 | -0.16693 | 0.021087 | -0.35072 | -0.12926 | -0.009973 | -0.067372 | 0.28335 | 0.034764 | 0.001336 | 122.9206 | 122.7792 | 122.9673 | 66.4412 | -123.1195 | 122.8169 | 122.9809 | 122.9475 | 66.3257 | -123.2969
383.2656 | 123.1522 | -66.5405 | 56.4011 | 0.057412 | -0.029831 | -0.0032367 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.061041 | 0.028605 | 0.060391 | -66.5458 | -0.090166 | -66.5171 | 56.3709 | 56.2937 | 56.4176 | -66.7001 | -66.5459 | -0.21026 | -66.6033 | 56.281 | 56.445 | 56.3978 | -66.8958 | -0.15962 | -0.030185 | -0.005293 | 0.023436 | 0.18306 | -0.1074 | 0.016508 | -0.3553 | -0.1201 | -0.005394 | -0.062793 | 0.29251 | 0.043921 | -0.003243 | 122.9114 | 122.8342 | 122.9581 | 66.4504 | -123.1012 | 122.8215 | 122.9855 | 122.9383 | 66.3303 | -123.2969
384.2656 | 123.4039 | -66.5497 | 56.3599 | 0.04215 | -0.028762 | -0.0043047 | 0.054234 | -0.0052687 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.029673 | 0.060391 | -66.5458 | -0.094744 | -66.5217 | 56.3663 | 56.2891 | 56.4176 | -66.7047 | -66.5505 | -0.21942 | -66.6079 | 56.2718 | 56.4358 | 56.3978 | -66.8867 | -0.15504 | 0.006435 | 0.003863 | 0.028014 | 0.18306 | -0.070785 | 0.057707 | -0.33699 | -0.088062 | -0.000817 | -0.058216 | 0.27877 | 0.075962 | 0.037956 | 122.916 | 122.8388 | 122.9673 | 66.4549 | -123.0646 | 122.8215 | 122.9855 | 122.9475 | 66.3303 | -123.2465
385.2656 | 123.1384 | -66.5497 | 56.4331 | 0.026888 | -0.029831 | -0.0032367 | 0.054234 | -0.0063367 | 0.058078 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.029673 | 0.060391 | -66.5458 | -0.099323 | -66.5262 | 56.3663 | 56.2662 | 56.413 | -66.7001 | -66.5459 | -0.21026 | -66.6033 | 56.2855 | 56.4404 | 56.4024 | -66.8867 | -0.15046 | -0.066807 | 0.003863 | 0.023436 | 0.1739 | -0.16692 | -0.020114 | -0.33699 | -0.14757 | 0.003762 | -0.053637 | 0.28335 | 0.007299 | -0.030707 | 122.916 | 122.8159 | 122.9627 | 66.4504 | -123.1333 | 122.8352 | 122.9901 | 122.9521 | 66.3394 | -123.3198
386.2656 | 123.1842 | -66.5314 | 56.3782 | 0.026888 | -0.027694 | -0.0010997 | 0.052097 | -0.0052687 | 0.05701 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.059972 | 0.027537 | 0.062528 | -66.5412 | -0.099323 | -66.5171 | 56.3709 | 56.2662 | 56.413 | -66.7001 | -66.5505 | -0.21026 | -66.6079 | 56.2764 | 56.4358 | 56.3978 | -66.8913 | -0.16877 | -0.007297 | -0.00987 | 0.014281 | 0.18306 | -0.11199 | 0.034817 | -0.35988 | -0.1018 | -0.019128 | -0.076527 | 0.28335 | 0.057651 | 0.019645 | 122.9022 | 122.7976 | 122.9444 | 66.432 | -123.0783 | 122.8078 | 122.9672 | 122.9292 | 66.3211 | -123.2694
387.2656 | 123.1613 | -66.5634 | 56.4239 | 0.057412 | -0.029831 | -0.0021677 | 0.053166 | -0.0063367 | 0.052737 | 0.073406 | -0.0025767 | -0.0010156 | 0.061041 | 0.029673 | 0.060391 | -66.5412 | -0.099323 | -66.5217 | 56.3755 | 56.2799 | 56.4267 | -66.7047 | -66.5459 | -0.224 | -66.6079 | 56.2901 | 56.4358 | 56.4024 | -66.8867 | -0.14131 | -0.048495 | 0.022174 | 0.041747 | 0.18306 | -0.14403 | 0.002777 | -0.32326 | -0.13383 | 0.017495 | -0.044483 | 0.27877 | 0.011875 | -0.021552 | 122.9389 | 122.8433 | 122.9901 | 66.4641 | -123.1287 | 122.8535 | 122.9992 | 122.9658 | 66.3394 | -123.3106
388.2656 | 123.1659 | -66.5451 | 56.4148 | 0.026888 | -0.027694 | -0.0032367 | 0.051029 | -0.0063367 | 0.05701 | 0.073406 | -0.0015087 | 0.0021894 | 0.057836 | 0.030742 | 0.060391 | -66.5412 | -0.099323 | -66.5171 | 56.3755 | 56.2753 | 56.4267 | -66.7093 | -66.5505 | -0.22858 | -66.6033 | 56.2855 | 56.4404 | 56.4161 | -66.8867 | -0.1642 | -0.03934 | 0.003863 | 0.028014 | 0.19221 | -0.13945 | 0.011932 | -0.34157 | -0.12926 | -0.005395 | -0.058215 | 0.28335 | 0.025609 | 0.001339 | 122.9206 | 122.8204 | 122.9718 | 66.4458 | -123.1241 | 122.8306 | 122.9855 | 122.9612 | 66.3165 | -123.3015
389.2656 | 123.1659 | -66.5588 | 56.4056 | 0.026888 | -0.029831 | -0.0032367 | 0.053166 | -0.0052687 | 0.055941 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.058904 | 0.028605 | 0.06146 | -66.5458 | -0.1039 | -66.5171 | 56.38 | 56.2753 | 56.4221 | -66.7047 | -66.5505 | -0.224 | -66.6079 | 56.2855 | 56.4358 | 56.4116 | -66.8913 | -0.14589 | -0.025606 | 0.013018 | 0.041747 | 0.18763 | -0.1303 | 0.016508 | -0.33241 | -0.1201 | 0.008338 | -0.049061 | 0.28335 | 0.030185 | 0.005915 | 122.9389 | 122.8342 | 122.981 | 66.4549 | -123.1104 | 122.8444 | 122.9947 | 122.9704 | 66.3348 | -123.2969
390.2656 | 123.2941 | -66.5588 | 56.4194 | 0.04215 | -0.028762 | -0.0032367 | 0.053166 | -0.0074047 | 0.05701 | 0.058145 | -0.0025767 | 0.0011204 | 0.059972 | 0.028605 | 0.06146 | -66.5412 | -0.094744 | -66.5171 | 56.3755 | 56.2937 | 56.4176 | -66.7047 | -66.5505 | -0.23316 | -66.6079 | 56.2855 | 56.4404 | 56.4161 | -66.8867 | -0.14589 | -0.043918 | 0.017596 | 0.041747 | 0.18763 | -0.12572 | -0.001803 | -0.32784 | -0.13384 | 0.008338 | -0.049061 | 0.27877 | 0.021031 | -0.003239 | 122.9343 | 122.8525 | 122.9764 | 66.4641 | -123.1241 | 122.8444 | 122.9992 | 122.975 | 66.3257 | -123.306
391.2656 | 123.175 | -66.5497 | 56.4239 | 0.04215 | -0.028762 | -0.0021677 | 0.054234 | -0.0052687 | 0.054873 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.062109 | 0.029673 | 0.060391 | -66.5321 | -0.099323 | -66.5217 | 56.3709 | 56.2891 | 56.413 | -66.7093 | -66.5459 | -0.21942 | -66.6033 | 56.281 | 56.4404 | 56.407 | -66.8867 | -0.15962 | -0.053073 | 0.017598 | 0.028014 | 0.18764 | -0.13487 | -0.010959 | -0.33699 | -0.14299 | 0.003762 | -0.053637 | 0.28335 | 0.016454 | -0.016974 | 122.9206 | 122.8388 | 122.9627 | 66.4504 | -123.1333 | 122.8306 | 122.9901 | 122.9567 | 66.3303 | -123.3106
392.2656 | 123.1796 | -66.5497 | 56.3873 | 0.057412 | -0.030899 | -0.0032367 | 0.052097 | -0.0052687 | 0.055941 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.061041 | 0.030742 | 0.059323 | -66.5367 | -0.099323 | -66.5217 | 56.3755 | 56.2891 | 56.4267 | -66.7047 | -66.5459 | -0.21484 | -66.6033 | 56.2855 | 56.4404 | 56.407 | -66.8913 | -0.15504 | -0.011874 | 0.01302 | 0.028014 | 0.18306 | -0.098251 | 0.039398 | -0.34157 | -0.10179 | 0.003762 | -0.053637 | 0.28793 | 0.053075 | 0.019647 | 122.9251 | 122.8388 | 122.9764 | 66.4504 | -123.0921 | 122.8352 | 122.9901 | 122.9567 | 66.3348 | -123.2786
393.2656 | 123.1888 | -66.5176 | 56.4377 | 0.026888 | -0.031967 | -0.0053737 | 0.054234 | -0.0041997 | 0.054873 | 0.073406 | -0.0025767 | 0.0011204 | 0.057836 | 0.028605 | 0.059323 | -66.5412 | -0.1039 | -66.5171 | 56.3663 | 56.2937 | 56.4267 | -66.7001 | -66.5459 | -0.22858 | -66.5987 | 56.2855 | 56.4404 | 56.407 | -66.8913 | -0.18251 | -0.071385 | -0.023603 | 0.000548 | 0.18306 | -0.14403 | -0.010956 | -0.37361 | -0.15215 | -0.028282 | -0.081102 | 0.29251 | 0.002721 | -0.030707 | 122.8839 | 122.8113 | 122.9444 | 66.4137 | -123.1378 | 122.8032 | 122.958 | 122.9246 | 66.2891 | -123.3289
394.2656 | 123.262 | -66.5085 | 56.369 | 0.04215 | -0.030899 | -0.0053737 | 0.054234 | -0.0052687 | 0.055941 | 0.073406 | -0.0015087 | 0.0011204 | 0.058904 | 0.029673 | 0.06146 | -66.5412 | -0.1039 | -66.5125 | 56.3709 | 56.2982 | 56.4267 | -66.7001 | -66.5413 | -0.22858 | -66.6033 | 56.2855 | 56.4404 | 56.4024 | -66.8913 | -0.19166 | 0.001858 | -0.032758 | -0.004029 | 0.18763 | -0.070783 | 0.057708 | -0.38277 | -0.083483 | -0.032859 | -0.094836 | 0.28793 | 0.071385 | 0.033379 | 122.8794 | 122.8067 | 122.9352 | 66.4046 | -123.0692 | 122.794 | 122.9489 | 122.9109 | 66.2799 | -123.2603
395.2656 | 123.1201 | -66.568 | 56.4331 | 0.057412 | -0.028762 | -0.0032367 | 0.052097 | -0.0041997 | 0.054873 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.028605 | 0.060391 | -66.5412 | -0.10848 | -66.5125 | 56.3755 | 56.2937 | 56.4221 | -66.7001 | -66.5459 | -0.22858 | -66.5987 | 56.2855 | 56.445 | 56.407 | -66.8867 | -0.13215 | -0.05765 | 0.026751 | 0.05548 | 0.18763 | -0.13945 | -0.010957 | -0.31868 | -0.14757 | 0.022072 | -0.030748 | 0.28793 | 0.011878 | -0.026129 | 122.9434 | 122.8616 | 122.9901 | 66.4595 | -123.1333 | 122.8535 | 123.013 | 122.975 | 66.3394 | -123.3198
396.2656 | 123.1384 | -66.568 | 56.4331 | 0.04215 | -0.030899 | -0.0053737 | 0.053166 | -0.0052687 | 0.05701 | 0.073406 | -0.0025767 | 0.0011204 | 0.061041 | 0.027537 | 0.059323 | -66.5412 | -0.1039 | -66.5125 | 56.38 | 56.2433 | 56.4313 | -66.7047 | -66.5505 | -0.23316 | -66.5987 | 56.281 | 56.4496 | 56.4161 | -66.8867 | -0.13673 | -0.053071 | 0.026751 | 0.05548 | 0.19221 | -0.18982 | -0.0018 | -0.31868 | -0.15215 | 0.017493 | -0.030748 | 0.28793 | 0.016456 | -0.016971 | 122.948 | 122.8113 | 122.9993 | 66.4641 | -123.1378 | 122.849 | 123.0176 | 122.9841 | 66.3348 | -123.3198
397.2656 | 123.1888 | -66.5451 | 56.4194 | 0.072674 | -0.029831 | -0.0053737 | 0.056371 | -0.0052687 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.059972 | 0.028605 | 0.06146 | -66.5458 | -0.10848 | -66.5262 | 56.3755 | 56.2341 | 56.4313 | -66.7047 | -66.5459 | -0.23316 | -66.6033 | 56.2947 | 56.445 | 56.4116 | -66.8867 | -0.15962 | -0.043918 | -0.000715 | 0.018858 | 0.17848 | -0.18524 | 0.011932 | -0.34157 | -0.12468 | -0.000816 | -0.058215 | 0.28335 | 0.02561 | -0.007818 | 122.9206 | 122.7792 | 122.9764 | 66.4366 | -123.1241 | 122.8398 | 122.9901 | 122.9567 | 66.312 | -123.306
398.2656 | 123.1201 | -66.5726 | 56.4377 | 0.057412 | -0.030899 | -0.0053737 | 0.053166 | -0.0063367 | 0.055941 | 0.088667 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.030742 | 0.060391 | -66.5412 | -0.10848 | -66.5125 | 56.3755 | 56.2387 | 56.4359 | -66.7093 | -66.5413 | -0.224 | -66.6033 | 56.2947 | 56.4496 | 56.407 | -66.8867 | -0.13673 | -0.062228 | 0.031329 | 0.060058 | 0.19679 | -0.19897 | -0.001799 | -0.3141 | -0.14299 | 0.031228 | -0.030749 | 0.28335 | 0.011878 | -0.030707 | 122.948 | 122.8113 | 123.0085 | 66.4641 | -123.147 | 122.8673 | 123.0221 | 122.9795 | 66.3486 | -123.3244
399.2656 | 123.1476 | -66.5314 | 56.4468 | 0.04215 | -0.029831 | -0.0043047 | 0.054234 | -0.0052687 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.03181 | 0.06146 | -66.5412 | -0.1039 | -66.5125 | 56.3846 | 56.2479 | 56.4313 | -66.7093 | -66.5368 | -0.224 | -66.5942 | 56.2855 | 56.445 | 56.4161 | -66.8821 | -0.17793 | -0.062226 | -0.00987 | 0.018859 | 0.19679 | -0.19897 | -0.015533 | -0.35072 | -0.1613 | -0.005392 | -0.062791 | 0.28793 | -0.001855 | -0.030704 | 122.916 | 122.7792 | 122.9627 | 66.4275 | -123.1561 | 122.8169 | 122.9764 | 122.9475 | 66.3074 | -123.3289
400.2656 | 123.1613 | -66.5359 | 56.4102 | 0.057412 | -0.028762 | -0.0032367 | 0.053166 | -0.0063367 | 0.054873 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.030742 | 0.060391 | -66.5367 | -0.11306 | -66.5125 | 56.3755 | 56.2982 | 56.4267 | -66.7047 | -66.5368 | -0.224 | -66.5987 | 56.2901 | 56.4404 | 56.4116 | -66.8821 | -0.16877 | -0.034762 | -0.000713 | 0.023437 | 0.19221 | -0.11198 | 0.01651 | -0.34614 | -0.1201 | -0.000814 | -0.062791 | 0.28335 | 0.030187 | 0.001338 | 122.9114 | 122.8342 | 122.9627 | 66.4229 | -123.1149 | 122.8261 | 122.9764 | 122.9475 | 66.312 | -123.2923
401.2656 | 123.143 | -66.5497 | 56.4194 | 0.057412 | -0.029831 | -0.0032367 | 0.052097 | -0.0074047 | 0.05701 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.061041 | 0.028605 | 0.060391 | -66.5367 | -0.1039 | -66.5171 | 56.38 | 56.3028 | 56.4313 | -66.6956 | -66.5322 | -0.23316 | -66.5942 | 56.2947 | 56.4404 | 56.4161 | -66.8867 | -0.14588 | -0.039339 | 0.01302 | 0.032592 | 0.17848 | -0.11656 | 0.011932 | -0.33699 | -0.12468 | 0.017498 | -0.04448 | 0.29251 | 0.021031 | -0.003239 | 122.9297 | 122.8525 | 122.981 | 66.4458 | -123.1149 | 122.8444 | 122.9901 | 122.9658 | 66.3165 | -123.306
402.2656 | 123.1934 | -66.5543 | 56.4423 | 0.026888 | -0.029831 | -0.0032367 | 0.052097 | -0.0052687 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.059972 | 0.030742 | 0.060391 | -66.5275 | -0.094744 | -66.5079 | 56.3846 | 56.2937 | 56.4267 | -66.6956 | -66.5413 | -0.22858 | -66.6033 | 56.2993 | 56.4496 | 56.4161 | -66.8867 | -0.14131 | -0.057649 | 0.026754 | 0.046326 | 0.18763 | -0.1486 | -0.015534 | -0.33241 | -0.14299 | 0.012917 | -0.04906 | 0.28335 | 0.0073 | -0.026127 | 122.9389 | 122.8479 | 122.981 | 66.4595 | -123.1378 | 122.8535 | 123.0038 | 122.9704 | 66.3257 | -123.3289
403.2656 | 123.1888 | -66.5222 | 56.4056 | 0.057412 | -0.029831 | -0.0021677 | 0.052097 | -0.0052687 | 0.054873 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.030742 | 0.060391 | -66.5367 | -0.1039 | -66.5171 | 56.38 | 56.2937 | 56.4267 | -66.7001 | -66.5413 | -0.21942 | -66.5942 | 56.2993 | 56.445 | 56.4116 | -66.8821 | -0.17793 | -0.025606 | -0.014446 | 0.005126 | 0.18306 | -0.11198 | 0.021087 | -0.35988 | -0.10637 | -0.019126 | -0.071946 | 0.28793 | 0.039343 | 0.005915 | 122.9023 | 122.8159 | 122.9489 | 66.4183 | -123.1058 | 122.8215 | 122.9672 | 122.9338 | 66.3028 | -123.2877
404.2656 | 123.1384 | -66.5497 | 56.3919 | 0.04215 | -0.031967 | -0.0043047 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.058904 | 0.028605 | 0.062528 | -66.5321 | -0.099323 | -66.5125 | 56.3755 | 56.2845 | 56.4313 | -66.6956 | -66.5322 | -0.20568 | -66.5942 | 56.2901 | 56.4496 | 56.407 | -66.8821 | -0.14588 | -0.016452 | 0.017598 | 0.03717 | 0.18305 | -0.10741 | 0.039398 | -0.33241 | -0.10179 | 0.017498 | -0.04448 | 0.28793 | 0.057654 | 0.015069 | 122.9251 | 122.8342 | 122.981 | 66.4504 | -123.0875 | 122.8398 | 122.9992 | 122.9567 | 66.344 | -123.274
405.2656 | 123.1476 | -66.5543 | 56.4468 | 0.057412 | -0.030899 | -0.0043047 | 0.052097 | -0.0074047 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.030742 | 0.060391 | -66.5275 | -0.099323 | -66.5079 | 56.3755 | 56.2937 | 56.4313 | -66.7001 | -66.5322 | -0.2011 | -66.5987 | 56.2947 | 56.4541 | 56.407 | -66.8913 | -0.14589 | -0.071383 | 0.026754 | 0.046326 | 0.19221 | -0.15318 | -0.015533 | -0.33699 | -0.15214 | 0.022075 | -0.044481 | 0.29251 | 0.007302 | -0.039862 | 122.9297 | 122.8479 | 122.9856 | 66.4549 | -123.147 | 122.849 | 123.0084 | 122.9612 | 66.3532 | -123.3381
406.2656 | 123.1888 | -66.5314 | 56.4285 | 0.04215 | -0.030899 | -0.0032367 | 0.053166 | -0.0041997 | 0.055941 | 0.042884 | -0.0036447 | 0.0011204 | 0.057836 | 0.03181 | 0.06146 | -66.5321 | -0.10848 | -66.5079 | 56.3846 | 56.2708 | 56.4267 | -66.7001 | -66.5276 | -0.2011 | -66.5987 | 56.2901 | 56.4496 | 56.4161 | -66.8729 | -0.16877 | -0.043916 | -0.000713 | 0.023438 | 0.19221 | -0.15776 | -0.001801 | -0.34156 | -0.13841 | 0.003765 | -0.067369 | 0.27419 | 0.021033 | -0.012394 | 122.916 | 122.8021 | 122.9581 | 66.4229 | -123.1287 | 122.8215 | 122.9809 | 122.9475 | 66.3303 | -123.3015
407.2656 | 123.1384 | -66.5634 | 56.4468 | 0.04215 | -0.030899 | -0.0043047 | 0.052097 | -0.0063367 | 0.055941 | 0.073406 | -0.0015087 | 0.0021894 | 0.058904 | 0.030742 | 0.060391 | -66.5229 | -0.11306 | -66.5079 | 56.3846 | 56.2937 | 56.4313 | -66.6956 | -66.5276 | -0.19653 | -66.5942 | 56.3038 | 56.4679 | 56.4253 | -66.8821 | -0.13215 | -0.062226 | 0.040488 | 0.055482 | 0.18763 | -0.15318 | -0.015533 | -0.31868 | -0.14299 | 0.035809 | -0.030747 | 0.28793 | 0.021038 | -0.021547 | 122.948 | 122.8571 | 122.9947 | 66.4504 | -123.1424 | 122.8673 | 123.0313 | 122.9887 | 66.3669 | -123.3289
408.2656 | 123.1659 | -66.5359 | 56.4331 | 0.057412 | -0.030899 | -0.0032367 | 0.053166 | -0.0074047 | 0.054873 | 0.088667 | -0.0025767 | 0.0011204 | 0.057836 | 0.028605 | 0.06146 | -66.5229 | -0.11306 | -66.5079 | 56.3846 | 56.2937 | 56.4359 | -66.691 | -66.5413 | -0.20568 | -66.5896 | 56.2993 | 56.4541 | 56.4207 | -66.8729 | -0.15504 | -0.048493 | 0.013022 | 0.028016 | 0.18305 | -0.13945 | 0.002779 | -0.33699 | -0.13383 | -0.005393 | -0.053634 | 0.28335 | 0.021035 | -0.012393 | 122.9206 | 122.8296 | 122.9718 | 66.4229 | -123.1241 | 122.8352 | 122.9901 | 122.9567 | 66.3303 | -123.306
409.2812 | 123.2208 | -66.5359 | 56.4239 | 0.057412 | -0.029831 | -0.0053737 | 0.051029 | -0.0041997 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.058904 | 0.029673 | 0.060391 | -66.5275 | -0.11764 | -66.5079 | 56.3846 | 56.2708 | 56.4313 | -66.691 | -66.5368 | -0.20568 | -66.585 | 56.2993 | 56.4587 | 56.4116 | -66.8821 | -0.15504 | -0.039338 | 0.008444 | 0.028016 | 0.18305 | -0.15319 | 0.007355 | -0.34614 | -0.12468 | -0.000814 | -0.049055 | 0.29709 | 0.034768 | -0.012395 | 122.9206 | 122.8067 | 122.9673 | 66.4183 | -123.1149 | 122.8352 | 122.9947 | 122.9475 | 66.3303 | -123.306
410.2656 | 123.1613 | -66.5359 | 56.4377 | 0.04215 | -0.031967 | -0.0032367 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.059972 | 0.029673 | 0.060391 | -66.5275 | -0.10848 | -66.5034 | 56.3755 | 56.2753 | 56.4267 | -66.691 | -66.5322 | -0.2011 | -66.5987 | 56.2993 | 56.4541 | 56.4161 | -66.8775 | -0.15504 | -0.062228 | 0.008444 | 0.032594 | 0.18763 | -0.16234 | -0.010956 | -0.34157 | -0.13841 | 0.003765 | -0.062791 | 0.27877 | 0.016457 | -0.021549 | 122.9114 | 122.8113 | 122.9627 | 66.4275 | -123.1287 | 122.8352 | 122.9901 | 122.9521 | 66.3348 | -123.3152
411.3281 | 123.2803 | -66.5039 | 56.3965 | 0.04215 | -0.029831 | -0.0053737 | 0.052097 | -0.0052687 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.061041 | 0.030742 | 0.059323 | -66.5275 | -0.11764 | -66.4988 | 56.3938 | 56.2753 | 56.4313 | -66.691 | -66.5322 | -0.20568 | -66.585 | 56.2993 | 56.4541 | 56.4207 | -66.8821 | -0.18708 | -0.002715 | -0.0236 | 0.005128 | 0.19221 | -0.12114 | 0.034821 | -0.37819 | -0.097212 | -0.028279 | -0.081099 | 0.29709 | 0.057656 | 0.024228 | 122.8977 | 122.7792 | 122.9352 | 66.3863 | -123.0875 | 122.8032 | 122.958 | 122.9246 | 66.2982 | -123.2786
412.2656 | 123.1476 | -66.5268 | 56.4651 | 0.057412 | -0.033036 | -0.0043047 | 0.051029 | -0.0052687 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.059972 | 0.03181 | 0.06146 | -66.5229 | -0.12222 | -66.4988 | 56.38 | 56.3074 | 56.4313 | -66.691 | -66.5322 | -0.2011 | -66.5896 | 56.2993 | 56.4541 | 56.4116 | -66.8821 | -0.16419 | -0.085115 | 0.003866 | 0.028016 | 0.19221 | -0.15775 | -0.033844 | -0.3553 | -0.16588 | -0.005391 | -0.06279 | 0.29251 | -0.011009 | -0.053594 | 122.9068 | 122.8342 | 122.9581 | 66.4046 | -123.1561 | 122.8261 | 122.9809 | 122.9383 | 66.3257 | -123.3472
413.2656 | 123.1338 | -66.4993 | 56.4377 | 0.04215 | -0.031967 | -0.0053737 | 0.053166 | -0.0052687 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.058904 | 0.03181 | 0.059323 | -66.5275 | -0.11764 | -66.4988 | 56.3938 | 56.3074 | 56.445 | -66.7001 | -66.5276 | -0.21026 | -66.5896 | 56.2993 | 56.4587 | 56.4299 | -66.8684 | -0.20082 | -0.043914 | -0.028177 | 0.000551 | 0.20137 | -0.13029 | 0.007358 | -0.36903 | -0.13841 | -0.028278 | -0.090255 | 0.27877 | 0.021035 | -0.007814 | 122.8931 | 122.8067 | 122.9444 | 66.3817 | -123.1378 | 122.7986 | 122.958 | 122.9292 | 66.2891 | -123.306
414.2656 | 123.1705 | -66.5359 | 56.3919 | 0.04215 | -0.031967 | -0.0043047 | 0.053166 | -0.0063367 | 0.058078 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.030742 | 0.058255 | -66.5183 | -0.11764 | -66.5034 | 56.3846 | 56.2433 | 56.4405 | -66.7001 | -66.5276 | -0.20568 | -66.5804 | 56.3084 | 56.4587 | 56.4253 | -66.8729 | -0.1642 | -0.007295 | 0.0176 | 0.032594 | 0.19679 | -0.14862 | 0.048556 | -0.33699 | -0.083478 | 0.008343 | -0.044477 | 0.29251 | 0.066811 | 0.033384 | 122.9206 | 122.7792 | 122.9764 | 66.4183 | -123.0921 | 122.8444 | 122.9947 | 122.9612 | 66.3303 | -123.2648
415.2656 | 123.1842 | -66.5176 | 56.4148 | 0.04215 | -0.031967 | -0.0053737 | 0.052097 | -0.0063367 | 0.058078 | 0.058145 | -0.0015087 | 0.0021894 | 0.059972 | 0.03181 | 0.060391 | -66.5229 | -0.12222 | -66.4988 | 56.3983 | 56.2387 | 56.4405 | -66.7001 | -66.5276 | -0.21026 | -66.585 | 56.3084 | 56.4633 | 56.4253 | -66.8775 | -0.18251 | -0.016448 | -0.005289 | 0.018861 | 0.20137 | -0.17609 | 0.025668 | -0.35988 | -0.10637 | -0.009968 | -0.067366 | 0.29251 | 0.048502 | 0.010496 | 122.916 | 122.7563 | 122.9581 | 66.3954 | -123.1149 | 122.8261 | 122.9809 | 122.9429 | 66.3074 | -123.2923
416.2656 | 123.2483 | -66.4764 | 56.4239 | 0.026888 | -0.033036 | -0.0021677 | 0.053166 | -0.0052687 | 0.055941 | 0.058145 | -0.0015087 | 0.0032574 | 0.058904 | 0.030742 | 0.060391 | -66.5321 | -0.12679 | -66.4942 | 56.3983 | 56.2387 | 56.4496 | -66.6956 | -66.5276 | -0.21484 | -66.5896 | 56.3038 | 56.4496 | 56.4253 | -66.8729 | -0.21913 | -0.025603 | -0.055645 | -0.017759 | 0.20137 | -0.18524 | 0.02567 | -0.3965 | -0.1201 | -0.051167 | -0.11314 | 0.28335 | 0.025611 | 0.001341 | 122.8748 | 122.7151 | 122.9261 | 66.3496 | -123.1195 | 122.7803 | 122.926 | 122.9017 | 66.2616 | -123.2969
417.2656 | 123.1018 | -66.5359 | 56.4285 | 0.057412 | -0.031967 | -0.0043047 | 0.054234 | -0.0052687 | 0.055941 | 0.042884 | -0.0025767 | 0.0011204 | 0.058904 | 0.030742 | 0.060391 | -66.5229 | -0.12679 | -66.4988 | 56.3938 | 56.2524 | 56.445 | -66.6956 | -66.5276 | -0.21484 | -66.5804 | 56.3038 | 56.4587 | 56.4344 | -66.8684 | -0.15962 | -0.034759 | 0.013022 | 0.037172 | 0.19679 | -0.17608 | 0.016513 | -0.33241 | -0.12468 | 0.008343 | -0.044477 | 0.28793 | 0.03019 | 0.00592 | 122.9297 | 122.7884 | 122.981 | 66.4092 | -123.1241 | 122.8398 | 122.9947 | 122.9704 | 66.3211 | -123.2969
418.2656 | 123.1522 | -66.5268 | 56.456 | 0.04215 | -0.030899 | -0.0032367 | 0.055302 | -0.0052687 | 0.055941 | 0.088667 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.030742 | 0.06146 | -66.5275 | -0.12679 | -66.4896 | 56.3938 | 56.2433 | 56.4496 | -66.6956 | -66.523 | -0.21484 | -66.585 | 56.3038 | 56.4587 | 56.4299 | -66.8729 | -0.16877 | -0.062225 | -0.000712 | 0.037173 | 0.20595 | -0.2127 | -0.006374 | -0.34614 | -0.15214 | 0.003766 | -0.058211 | 0.28793 | 0.002724 | -0.026125 | 122.9206 | 122.7701 | 122.9764 | 66.4 | -123.1516 | 122.8306 | 122.9855 | 122.9567 | 66.312 | -123.3289
419.2656 | 123.1842 | -66.5359 | 56.4239 | 0.057412 | -0.033036 | -0.0043047 | 0.053166 | -0.0052687 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.061041 | 0.03181 | 0.06146 | -66.5229 | -0.13137 | -66.4988 | 56.3983 | 56.2387 | 56.4588 | -66.6956 | -66.523 | -0.21026 | -66.5804 | 56.3084 | 56.4587 | 56.439 | -66.8684 | -0.15962 | -0.025603 | 0.013022 | 0.037172 | 0.19679 | -0.18524 | 0.034827 | -0.33241 | -0.11552 | 0.012922 | -0.044477 | 0.28793 | 0.034768 | 0.015077 | 122.9343 | 122.7747 | 122.9947 | 66.4046 | -123.1195 | 122.8444 | 122.9947 | 122.975 | 66.3257 | -123.2923
420.2656 | 123.2254 | -66.5176 | 56.4377 | 0.04215 | -0.031967 | -0.0032367 | 0.053166 | -0.0052687 | 0.05701 | 0.042884 | -0.0015087 | 0.0011204 | 0.059972 | 0.030742 | 0.060391 | -66.5229 | -0.14053 | -66.4942 | 56.3983 | 56.2387 | 56.4542 | -66.691 | -66.523 | -0.20568 | -66.585 | 56.3084 | 56.4587 | 56.4344 | -66.8729 | -0.17335 | -0.039336 | -0.005289 | 0.02344 | 0.19679 | -0.19897 | 0.016515 | -0.3553 | -0.12925 | -0.005389 | -0.067366 | 0.28793 | 0.021035 | -0.003235 | 122.916 | 122.7563 | 122.9718 | 66.3771 | -123.1287 | 122.8261 | 122.9764 | 122.9521 | 66.312 | -123.3106
421.2656 | 123.1201 | -66.5314 | 56.4697 | 0.057412 | -0.031967 | -0.0021677 | 0.054234 | -0.0063367 | 0.05701 | 0.073406 | -0.0025767 | -0.0010156 | 0.058904 | 0.03181 | 0.060391 | -66.5229 | -0.13595 | -66.4988 | 56.4029 | 56.2524 | 56.445 | -66.6864 | -66.5184 | -0.21026 | -66.5804 | 56.2993 | 56.4633 | 56.439 | -66.8684 | -0.15504 | -0.066802 | 0.008444 | 0.032594 | 0.18763 | -0.21728 | -0.024686 | -0.33699 | -0.17045 | 0.012923 | -0.049055 | 0.28793 | -0.00643 | -0.0307 | 122.9343 | 122.7838 | 122.9764 | 66.3954 | -123.1561 | 122.8306 | 122.9947 | 122.9704 | 66.3211 | -123.3381
422.2656 | 123.1567 | -66.5131 | 56.4468 | 0.04215 | -0.034104 | -0.0032367 | 0.054234 | -0.0074047 | 0.055941 | 0.073406 | -0.0025767 | 0.0021894 | 0.057836 | 0.03181 | 0.059323 | -66.5229 | -0.13595 | -66.4942 | 56.4029 | 56.2524 | 56.4496 | -66.6956 | -66.5276 | -0.21484 | -66.5804 | 56.313 | 56.4587 | 56.4344 | -66.8729 | -0.1825 | -0.043913 | -0.009866 | 0.018863 | 0.20137 | -0.19439 | 0.002782 | -0.35987 | -0.13383 | -0.014545 | -0.067365 | 0.29251 | 0.01188 | -0.01239 | 122.916 | 122.7655 | 122.9627 | 66.3771 | -123.1424 | 122.8261 | 122.9718 | 122.9475 | 66.2982 | -123.3198
423.2656 | 123.2849 | -66.4948 | 56.4194 | 0.04215 | -0.033036 | -0.0032367 | 0.051029 | -0.0074047 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.030742 | 0.060391 | -66.5183 | -0.13595 | -66.4942 | 56.4029 | 56.2433 | 56.4542 | -66.6864 | -66.523 | -0.21484 | -66.5713 | 56.3084 | 56.4679 | 56.439 | -66.8729 | -0.19166 | -0.016448 | -0.023599 | 0.000552 | 0.19221 | -0.17608 | 0.034825 | -0.37819 | -0.11094 | -0.028277 | -0.076518 | 0.30167 | 0.048503 | 0.019654 | 122.8977 | 122.738 | 122.9489 | 66.3588 | -123.1058 | 122.8032 | 122.9626 | 122.9338 | 66.2799 | -123.2923
424.2656 | 123.1476 | -66.5543 | 56.4239 | 0.04215 | -0.031967 | -0.0021677 | 0.052097 | -0.0074047 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.029673 | 0.06146 | -66.5229 | -0.14053 | -66.4942 | 56.4029 | 56.257 | 56.4588 | -66.6864 | -66.5276 | -0.21484 | -66.5713 | 56.3084 | 56.4633 | 56.4344 | -66.8684 | -0.13215 | -0.021025 | 0.031332 | 0.060061 | 0.19221 | -0.16692 | 0.034827 | -0.3141 | -0.11552 | 0.026653 | -0.017009 | 0.29709 | 0.039347 | 0.010498 | 122.9572 | 122.8113 | 123.013 | 66.4137 | -123.1104 | 122.8627 | 123.0176 | 122.9887 | 66.3394 | -123.2923
425.2656 | 123.1476 | -66.5268 | 56.4606 | 0.057412 | -0.031967 | -0.0032367 | 0.052097 | -0.0063367 | 0.054873 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.030742 | 0.059323 | -66.5183 | -0.14511 | -66.4896 | 56.3983 | 56.2479 | 56.4634 | -66.6818 | -66.5184 | -0.21484 | -66.5667 | 56.313 | 56.4587 | 56.439 | -66.8684 | -0.15504 | -0.062224 | 0.008444 | 0.037173 | 0.19221 | -0.2127 | 0.002785 | -0.34156 | -0.14756 | 0.008345 | -0.039896 | 0.30167 | -0.001853 | -0.021544 | 122.9251 | 122.7747 | 122.9901 | 66.3817 | -123.1424 | 122.8398 | 122.9855 | 122.9658 | 66.312 | -123.3289
426.2656 | 123.262 | -66.4627 | 56.4285 | 0.026888 | -0.033036 | -0.0043047 | 0.051029 | -0.0074047 | 0.053805 | 0.058145 | -0.0036447 | 0.0011204 | 0.058904 | 0.030742 | 0.06146 | -66.5183 | -0.13595 | -66.4896 | 56.3983 | 56.2524 | 56.4588 | -66.691 | -66.523 | -0.21484 | -66.5804 | 56.3084 | 56.4633 | 56.4299 | -66.8684 | -0.22828 | -0.030181 | -0.055642 | -0.026913 | 0.20137 | -0.17608 | 0.030249 | -0.40565 | -0.1201 | -0.06032 | -0.11772 | 0.28793 | 0.034769 | 0.001341 | 122.8611 | 122.7152 | 122.9215 | 66.3268 | -123.1195 | 122.7711 | 122.926 | 122.8926 | 66.2479 | -123.2969
427.2656 | 123.2391 | -66.4719 | 56.4377 | 0.072674 | -0.033036 | -0.0021677 | 0.053166 | -0.0063367 | 0.055941 | 0.042884 | -0.0025767 | 0.0011204 | 0.059972 | 0.03181 | 0.060391 | -66.5183 | -0.14053 | -66.4942 | 56.3983 | 56.3257 | 56.4405 | -66.6818 | -66.523 | -0.21942 | -66.5758 | 56.3176 | 56.4541 | 56.4253 | -66.8729 | -0.20997 | -0.039336 | -0.046487 | -0.022336 | 0.18763 | -0.11197 | 0.00278 | -0.40107 | -0.1201 | -0.051165 | -0.10398 | 0.29709 | 0.016457 | -0.012392 | 122.8702 | 122.7976 | 122.9123 | 66.3313 | -123.1195 | 122.7894 | 122.926 | 122.8972 | 66.2524 | -123.3106
428.2656 | 123.1293 | -66.5314 | 56.4697 | 0.057412 | -0.034104 | -0.0053737 | 0.053166 | -0.0052687 | 0.05701 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.03181 | 0.060391 | -66.5183 | -0.13595 | -66.4896 | 56.4029 | 56.3166 | 56.4496 | -66.6773 | -66.523 | -0.21484 | -66.5713 | 56.3222 | 56.4679 | 56.439 | -66.8638 | -0.14588 | -0.066802 | 0.013022 | 0.041751 | 0.18763 | -0.15317 | -0.020107 | -0.33241 | -0.14756 | 0.008344 | -0.039897 | 0.29251 | -0.001851 | -0.0307 | 122.9343 | 122.8479 | 122.981 | 66.3954 | -123.147 | 122.8535 | 122.9992 | 122.9704 | 66.3165 | -123.3335
429.2656 | 123.1567 | -66.5085 | 56.4606 | 0.057412 | -0.033036 | -0.0032367 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.030742 | 0.060391 | -66.5092 | -0.14053 | -66.485 | 56.3983 | 56.3028 | 56.4542 | -66.6818 | -66.5093 | -0.21484 | -66.5713 | 56.313 | 56.4587 | 56.439 | -66.8684 | -0.17335 | -0.062224 | -0.000709 | 0.023441 | 0.19679 | -0.15776 | -0.006373 | -0.35987 | -0.14756 | -0.000808 | -0.062785 | 0.29709 | -0.001853 | -0.021544 | 122.9068 | 122.8113 | 122.9627 | 66.368 | -123.1424 | 122.8215 | 122.9672 | 122.9475 | 66.2936 | -123.3289
430.2656 | 123.1201 | -66.5176 | 56.4514 | 0.057412 | -0.034104 | -0.0043047 | 0.052097 | -0.0052687 | 0.05701 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.059972 | 0.03181 | 0.06146 | -66.5092 | -0.14053 | -66.485 | 56.4075 | 56.2937 | 56.4542 | -66.6773 | -66.5139 | -0.21942 | -66.5667 | 56.3084 | 56.4679 | 56.439 | -66.8638 | -0.15961 | -0.043912 | 0.008446 | 0.032596 | 0.19221 | -0.15776 | 0.002782 | -0.34614 | -0.14299 | 0.003769 | -0.049051 | 0.29709 | 0.01646 | -0.012389 | 122.9251 | 122.8113 | 122.9718 | 66.3771 | -123.1287 | 122.8261 | 122.9855 | 122.9567 | 66.2982 | -123.3152
431.2656 | 123.2666 | -66.4352 | 56.4239 | 0.026888 | -0.031967 | -0.0021677 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0015087 | -0.0010156 | 0.058904 | 0.03181 | 0.060391 | -66.5092 | -0.14511 | -66.485 | 56.4029 | 56.3028 | 56.4542 | -66.6681 | -66.5139 | -0.224 | -66.5667 | 56.3222 | 56.4725 | 56.4253 | -66.8638 | -0.23285 | -0.021025 | -0.073951 | -0.049801 | 0.18305 | -0.12113 | 0.030248 | -0.42854 | -0.10179 | -0.078628 | -0.13145 | 0.29709 | 0.048504 | 0.001341 | 122.8382 | 122.7381 | 122.8894 | 66.2901 | -123.092 | 122.7574 | 122.9077 | 122.8605 | 66.2112 | -123.2877
432.2656 | 123.23 | -66.4536 | 56.4468 | 0.057412 | -0.033036 | -0.0032367 | 0.051029 | -0.0063367 | 0.055941 | 0.042884 | -0.0025767 | 0.0021894 | 0.059972 | 0.032879 | 0.059323 | -66.5183 | -0.14053 | -66.4805 | 56.4075 | 56.2845 | 56.4542 | -66.6727 | -66.5093 | -0.21484 | -66.5758 | 56.3222 | 56.4679 | 56.439 | -66.8592 | -0.21912 | -0.039334 | -0.064798 | -0.026913 | 0.19221 | -0.16234 | 0.00736 | -0.40565 | -0.12467 | -0.05574 | -0.1223 | 0.28335 | 0.021038 | -0.007811 | 122.8611 | 122.7381 | 122.9077 | 66.313 | -123.1195 | 122.7757 | 122.9214 | 122.8926 | 66.2387 | -123.306
433.2656 | 123.2574 | -66.4856 | 56.4285 | 0.026888 | -0.035172 | -0.0032367 | 0.052097 | -0.0063367 | 0.055941 | 0.10393 | -0.0036447 | 0.0011204 | 0.058904 | 0.032879 | 0.059323 | -66.5138 | -0.14511 | -66.485 | 56.4029 | 56.312 | 56.4542 | -66.6681 | -66.5184 | -0.224 | -66.5621 | 56.3267 | 56.477 | 56.439 | -66.8592 | -0.1825 | -0.025603 | -0.028175 | 0.000553 | 0.18305 | -0.11655 | 0.02567 | -0.3736 | -0.10178 | -0.032853 | -0.076516 | 0.29709 | 0.048505 | 0.010499 | 122.8885 | 122.7976 | 122.9398 | 66.3405 | -123.0966 | 122.8123 | 122.9626 | 122.9246 | 66.2616 | -123.2877
434.2656 | 123.1567 | -66.5131 | 56.4423 | 0.04215 | -0.033036 | -0.0032367 | 0.052097 | -0.0074047 | 0.055941 | 0.058145 | -0.0036447 | -0.0010156 | 0.057836 | 0.030742 | 0.06146 | -66.5138 | -0.14053 | -66.4805 | 56.4075 | 56.3257 | 56.4679 | -66.6727 | -66.5184 | -0.21942 | -66.5621 | 56.3222 | 56.4725 | 56.439 | -66.85 | -0.15961 | -0.034757 | -0.000709 | 0.032597 | 0.19221 | -0.11655 | 0.025673 | -0.33698 | -0.1201 | -0.005387 | -0.04905 | 0.28793 | 0.030193 | -0.003234 | 122.9206 | 122.8388 | 122.981 | 66.3725 | -123.1149 | 122.8352 | 122.9855 | 122.9521 | 66.2936 | -123.2923
435.2656 | 123.2483 | -66.4902 | 56.4194 | 0.04215 | -0.033036 | -0.0053737 | 0.053166 | -0.0084737 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.058904 | 0.033947 | 0.060391 | -66.5092 | -0.14511 | -66.4759 | 56.4029 | 56.3211 | 56.4542 | -66.6681 | -66.5139 | -0.21484 | -66.5575 | 56.3267 | 56.4725 | 56.4482 | -66.8592 | -0.17792 | -0.016448 | -0.01902 | 0.014287 | 0.19221 | -0.098242 | 0.034825 | -0.36903 | -0.09263 | -0.023697 | -0.06736 | 0.30167 | 0.053081 | 0.028811 | 122.8931 | 122.8113 | 122.9444 | 66.3451 | -123.0875 | 122.8169 | 122.9626 | 122.9384 | 66.2753 | -123.2786
436.2656 | 123.0927 | -66.5268 | 56.456 | 0.04215 | -0.034104 | -0.0053737 | 0.055302 | -0.0074047 | 0.054873 | 0.058145 | -0.0025767 | -0.0010156 | 0.058904 | 0.032879 | 0.059323 | -66.5046 | -0.15427 | -66.4805 | 56.4167 | 56.3257 | 56.4542 | -66.6727 | -66.5093 | -0.21942 | -66.553 | 56.3176 | 56.4725 | 56.439 | -66.8592 | -0.14588 | -0.039333 | 0.022179 | 0.046329 | 0.19221 | -0.13028 | -0.001796 | -0.33241 | -0.13841 | 0.017502 | -0.02616 | 0.30625 | 0.01646 | -0.016967 | 122.9435 | 122.8525 | 122.981 | 66.3725 | -123.1287 | 122.8444 | 122.9992 | 122.9658 | 66.3074 | -123.3152
437.2656 | 123.2071 | -66.5039 | 56.4194 | 0.057412 | -0.035172 | -0.0043047 | 0.053166 | -0.0063367 | 0.054873 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.03181 | 0.060391 | -66.5046 | -0.15884 | -66.4713 | 56.4075 | 56.3303 | 56.4542 | -66.6635 | -66.5047 | -0.21484 | -66.5621 | 56.3313 | 56.4679 | 56.439 | -66.8546 | -0.15961 | -0.011869 | -0.000709 | 0.032598 | 0.19221 | -0.089084 | 0.034825 | -0.35071 | -0.088052 | -0.000807 | -0.058206 | 0.29251 | 0.048503 | 0.019654 | 122.9114 | 122.8342 | 122.9581 | 66.3451 | -123.0829 | 122.8352 | 122.9718 | 122.9429 | 66.2891 | -123.274
438.3438 | 123.2071 | -66.4673 | 56.4331 | 0.04215 | -0.035172 | -0.0032367 | 0.053166 | -0.0063367 | 0.055941 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.033947 | 0.059323 | -66.5046 | -0.15884 | -66.4713 | 56.4167 | 56.3349 | 56.4679 | -66.6681 | -66.5001 | -0.21942 | -66.5621 | 56.3313 | 56.4725 | 56.4528 | -66.85 | -0.20081 | -0.016444 | -0.03733 | -0.004023 | 0.19679 | -0.098237 | 0.034829 | -0.38276 | -0.10178 | -0.032849 | -0.094827 | 0.28793 | 0.039349 | 0.019657 | 122.8839 | 122.8022 | 122.9352 | 66.3084 | -123.1012 | 122.7986 | 122.9397 | 122.92 | 66.2479 | -123.2831
439.2812 | 123.2437 | -66.4764 | 56.4331 | 0.072674 | -0.033036 | -0.0032367 | 0.051029 | -0.0074047 | 0.055941 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.033947 | 0.06146 | -66.5 | -0.15427 | -66.4622 | 56.4212 | 56.3349 | 56.4588 | -66.6681 | -66.4956 | -0.21942 | -66.5575 | 56.3313 | 56.4816 | 56.4482 | -66.85 | -0.19165 | -0.011866 | -0.023596 | 0.014289 | 0.20594 | -0.098237 | 0.025672 | -0.3736 | -0.10178 | -0.019116 | -0.081093 | 0.29251 | 0.048506 | 0.015079 | 122.8977 | 122.8113 | 122.9352 | 66.3222 | -123.1012 | 122.8078 | 122.9581 | 122.9246 | 66.257 | -123.2831
440.2656 | 123.2208 | -66.481 | 56.4514 | 0.057412 | -0.035172 | -0.0064417 | 0.051029 | -0.0063367 | 0.054873 | 0.058145 | -0.0025767 | 0.0021894 | 0.058904 | 0.03181 | 0.060391 | -66.5046 | -0.15884 | -66.4713 | 56.4212 | 56.3394 | 56.4679 | -66.6681 | -66.4956 | -0.22858 | -66.553 | 56.3359 | 56.477 | 56.4482 | -66.85 | -0.18708 | -0.030177 | -0.023597 | 0.00971 | 0.19679 | -0.11197 | 0.016518 | -0.36902 | -0.11552 | -0.014538 | -0.071936 | 0.29709 | 0.025617 | -0.003232 | 122.9023 | 122.8205 | 122.949 | 66.3222 | -123.1195 | 122.8169 | 122.9581 | 122.9292 | 66.2524 | -123.3015
441.2656 | 123.2025 | -66.5039 | 56.4331 | 0.057412 | -0.033036 | -0.0032367 | 0.052097 | -0.0063367 | 0.058078 | 0.058145 | -0.0015087 | 0.0011204 | 0.058904 | 0.032879 | 0.06146 | -66.4955 | -0.16342 | -66.4759 | 56.4212 | 56.3349 | 56.4725 | -66.6635 | -66.5001 | -0.224 | -66.5575 | 56.3313 | 56.477 | 56.4528 | -66.8546 | -0.15961 | -0.011866 | 0.008448 | 0.02802 | 0.18763 | -0.098237 | 0.039408 | -0.35071 | -0.10178 | 0.003772 | -0.053627 | 0.29709 | 0.043928 | 0.019657 | 122.9251 | 122.8388 | 122.9764 | 66.3405 | -123.0966 | 122.8352 | 122.9809 | 122.9567 | 66.2799 | -123.2877
442.2656 | 123.1934 | -66.4948 | 56.4285 | 0.04215 | -0.034104 | -0.0053737 | 0.052097 | -0.0063367 | 0.055941 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.058904 | 0.033947 | 0.060391 | -66.4955 | -0.16342 | -66.4667 | 56.4258 | 56.3028 | 56.4679 | -66.6589 | -66.491 | -0.22858 | -66.553 | 56.3359 | 56.4862 | 56.4528 | -66.8455 | -0.16419 | -0.002711 | -0.000707 | 0.028021 | 0.19221 | -0.12571 | 0.039406 | -0.35071 | -0.092628 | 0.003774 | -0.058203 | 0.29251 | 0.057662 | 0.024234 | 122.9206 | 122.7976 | 122.9627 | 66.3313 | -123.0875 | 122.8307 | 122.9809 | 122.9475 | 66.2662 | -123.274
443.2656 | 123.262 | -66.4627 | 56.4011 | 0.011626 | -0.035172 | -0.0053737 | 0.053166 | -0.0063367 | 0.055941 | 0.027623 | -0.0025767 | 0.0011204 | 0.061041 | 0.035015 | 0.06146 | -66.4909 | -0.15427 | -66.4713 | 56.4167 | 56.2753 | 56.4817 | -66.6681 | -66.491 | -0.224 | -66.5484 | 56.3359 | 56.4862 | 56.4528 | -66.85 | -0.20539 | 0.015599 | -0.028171 | -0.0086 | 0.19679 | -0.12572 | 0.080608 | -0.38733 | -0.065162 | -0.028269 | -0.085668 | 0.30167 | 0.085128 | 0.0517 | 122.8794 | 122.7381 | 122.9444 | 66.3084 | -123.0692 | 122.7986 | 122.9489 | 122.9155 | 66.2387 | -123.2511
444.2656 | 123.2483 | -66.4764 | 56.4377 | 0.057412 | -0.036241 | -0.0043047 | 0.053166 | -0.0074047 | 0.055941 | 0.042884 | -0.0025767 | 0.0021894 | 0.059972 | 0.033947 | 0.060391 | -66.5046 | -0.16342 | -66.4667 | 56.4258 | 56.2753 | 56.4725 | -66.6589 | -66.4956 | -0.22858 | -66.5484 | 56.3313 | 56.4862 | 56.4573 | -66.8455 | -0.1825 | -0.011866 | -0.028175 | 0.00971 | 0.19221 | -0.16234 | 0.03483 | -0.36902 | -0.10636 | -0.019116 | -0.071936 | 0.29709 | 0.048507 | 0.019658 | 122.9023 | 122.7518 | 122.949 | 66.313 | -123.0966 | 122.8078 | 122.9626 | 122.9338 | 66.2479 | -123.2831
445.2656 | 123.2071 | -66.4764 | 56.4194 | 0.057412 | -0.035172 | -0.0032367 | 0.053166 | -0.0063367 | 0.053805 | 0.058145 | -0.00043967 | 0.0011204 | 0.061041 | 0.033947 | 0.060391 | -66.4909 | -0.15884 | -66.4622 | 56.4258 | 56.344 | 56.4771 | -66.6589 | -66.4956 | -0.224 | -66.553 | 56.3405 | 56.4908 | 56.4573 | -66.8409 | -0.1825 | 0.006444 | -0.014439 | 0.014289 | 0.19678 | -0.075348 | 0.057718 | -0.36445 | -0.078895 | -0.019116 | -0.076514 | 0.28793 | 0.071396 | 0.037968 | 122.9023 | 122.8205 | 122.9535 | 66.3176 | -123.0783 | 122.8169 | 122.9672 | 122.9338 | 66.2524 | -123.2603
446.2656 | 123.2346 | -66.4902 | 56.4056 | 0.057412 | -0.034104 | -0.0053737 | 0.052097 | -0.0063367 | 0.055941 | 0.058145 | -0.0015087 | 0.0021894 | 0.059972 | 0.033947 | 0.060391 | -66.4863 | -0.16342 | -66.4484 | 56.4167 | 56.3394 | 56.4771 | -66.6544 | -66.4818 | -0.21942 | -66.5392 | 56.3359 | 56.4908 | 56.4482 | -66.8455 | -0.16418 | 0.011021 | 0.003872 | 0.041756 | 0.20594 | -0.066193 | 0.071451 | -0.35529 | -0.06974 | 0.008354 | -0.049045 | 0.30625 | 0.085129 | 0.042544 | 122.9068 | 122.8296 | 122.9673 | 66.3268 | -123.06 | 122.8261 | 122.9809 | 122.9384 | 66.2708 | -123.2511
447.25 | 123.2803 | -66.4719 | 56.4285 | 0.026888 | -0.035172 | -0.0032367 | 0.053166 | -0.0063367 | 0.055941 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.058904 | 0.032879 | 0.059323 | -66.4863 | -0.168 | -66.4576 | 56.4304 | 56.3486 | 56.4771 | -66.6544 | -66.491 | -0.22858 | -66.5438 | 56.3405 | 56.4908 | 56.4573 | -66.8455 | -0.18249 | 0.001868 | -0.014438 | 0.01429 | 0.19678 | -0.079924 | 0.048563 | -0.3736 | -0.08805 | -0.019114 | -0.071934 | 0.30167 | 0.062241 | 0.028813 | 122.9023 | 122.8205 | 122.949 | 66.3039 | -123.0829 | 122.8123 | 122.9626 | 122.9292 | 66.2433 | -123.274
448.2656 | 123.349 | -66.4536 | 56.4239 | 0.04215 | -0.035172 | -0.0043047 | 0.054234 | -0.0074047 | 0.054873 | 0.042884 | -0.0025767 | -0.0010156 | 0.058904 | 0.033947 | 0.060391 | -66.4909 | -0.168 | -66.453 | 56.4304 | 56.344 | 56.4679 | -66.6589 | -66.4818 | -0.224 | -66.5438 | 56.3405 | 56.4953 | 56.4573 | -66.8409 | -0.20538 | 0.006446 | -0.037327 | 0.000557 | 0.20594 | -0.079925 | 0.043984 | -0.38733 | -0.083472 | -0.028267 | -0.090245 | 0.29709 | 0.071397 | 0.033391 | 122.8839 | 122.7976 | 122.9215 | 66.2856 | -123.0829 | 122.794 | 122.9489 | 122.9109 | 66.2296 | -123.2648
449.2656 | 123.2666 | -66.4764 | 56.4743 | 0.072674 | -0.035172 | -0.0043047 | 0.052097 | -0.0052687 | 0.05701 | 0.073406 | -0.0036447 | 0.0011204 | 0.059972 | 0.033947 | 0.060391 | -66.4863 | -0.168 | -66.4576 | 56.4258 | 56.344 | 56.4771 | -66.6498 | -66.4818 | -0.224 | -66.5484 | 56.3451 | 56.4953 | 56.4573 | -66.8409 | -0.17334 | -0.048487 | -0.009861 | 0.018867 | 0.19221 | -0.13028 | 0.002787 | -0.36445 | -0.12925 | -0.005379 | -0.071936 | 0.29251 | 0.021043 | -0.016963 | 122.9023 | 122.8205 | 122.9535 | 66.3084 | -123.1241 | 122.8215 | 122.9718 | 122.9338 | 66.2524 | -123.3152
450.2656 | 123.1934 | -66.4764 | 56.4239 | 0.057412 | -0.035172 | -0.0032367 | 0.052097 | -0.0052687 | 0.055941 | 0.042884 | -0.0015087 | 0.0011204 | 0.057836 | 0.035015 | 0.060391 | -66.4909 | -0.17258 | -66.4576 | 56.4304 | 56.3532 | 56.4862 | -66.6544 | -66.4727 | -0.23316 | -66.5392 | 56.3405 | 56.4953 | 56.4665 | -66.8271 | -0.17792 | 0.006446 | -0.014439 | 0.018867 | 0.19678 | -0.070767 | 0.062299 | -0.35071 | -0.083472 | 0.003778 | -0.062778 | 0.28793 | 0.071397 | 0.042548 | 122.9068 | 122.8296 | 122.9627 | 66.3039 | -123.0783 | 122.8169 | 122.9718 | 122.9429 | 66.2433 | -123.2511
451.2656 | 123.1613 | -66.5085 | 56.4606 | 0.057412 | -0.036241 | -0.0053737 | 0.054234 | -0.0084737 | 0.058078 | 0.042884 | -0.0015087 | 0.0021894 | 0.058904 | 0.036084 | 0.059323 | -66.4817 | -0.16342 | -66.4576 | 56.4304 | 56.3532 | 56.4862 | -66.6498 | -66.4727 | -0.224 | -66.5392 | 56.3405 | 56.5045 | 56.4665 | -66.8363 | -0.14129 | -0.030175 | 0.026761 | 0.050911 | 0.19221 | -0.10739 | 0.025678 | -0.32782 | -0.12009 | 0.035822 | -0.030734 | 0.29709 | 0.043933 | 0.005927 | 122.9389 | 122.8617 | 122.9947 | 66.3451 | -123.1103 | 122.849 | 123.013 | 122.975 | 66.2845 | -123.2969
452.2656 | 123.2346 | -66.4536 | 56.4468 | 0.011626 | -0.035172 | -0.0053737 | 0.054234 | -0.0084737 | 0.053805 | 0.042884 | -0.0015087 | 0.0011204 | 0.061041 | 0.033947 | 0.06146 | -66.4817 | -0.168 | -66.4438 | 56.435 | 56.3623 | 56.4862 | -66.6498 | -66.4681 | -0.23316 | -66.5392 | 56.3405 | 56.4953 | 56.4619 | -66.8317 | -0.19623 | -0.011864 | -0.028171 | 0.009714 | 0.20594 | -0.084497 | 0.039411 | -0.37817 | -0.10636 | -0.014531 | -0.085666 | 0.29251 | 0.048509 | 0.015082 | 122.8885 | 122.8159 | 122.9398 | 66.2856 | -123.0966 | 122.794 | 122.9489 | 122.9155 | 66.2204 | -123.2786
453.2656 | 123.2346 | -66.4902 | 56.4377 | 0.011626 | -0.035172 | -0.0043047 | 0.051029 | -0.0074047 | 0.054873 | 0.027623 | -0.0025767 | 0.0021894 | 0.058904 | 0.033947 | 0.060391 | -66.4817 | -0.18632 | -66.453 | 56.435 | 56.3303 | 56.4908 | -66.6452 | -66.4727 | -0.22858 | -66.5346 | 56.3542 | 56.5045 | 56.4665 | -66.8363 | -0.15503 | -0.002709 | 0.00845 | 0.037178 | 0.1922 | -0.10739 | 0.053144 | -0.34613 | -0.083469 | 0.017511 | -0.044466 | 0.30167 | 0.066821 | 0.028815 | 122.9251 | 122.8205 | 122.981 | 66.3039 | -123.0829 | 122.8444 | 122.9947 | 122.9567 | 66.2616 | -123.274
454.2656 | 123.23 | -66.4352 | 56.4835 | 0.057412 | -0.034104 | -0.0043047 | 0.052097 | -0.0052687 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.059972 | 0.035015 | 0.059323 | -66.4771 | -0.17716 | -66.4484 | 56.4396 | 56.3486 | 56.4862 | -66.6498 | -66.4772 | -0.24231 | -66.5301 | 56.3588 | 56.5045 | 56.4711 | -66.8317 | -0.21454 | -0.043906 | -0.041902 | -0.013175 | 0.20136 | -0.13486 | 0.00279 | -0.39648 | -0.12467 | -0.041999 | -0.094819 | 0.30167 | 0.021045 | -0.012382 | 122.8748 | 122.7838 | 122.9215 | 66.2581 | -123.1332 | 122.794 | 122.9397 | 122.9063 | 66.1929 | -123.3152
455.2656 | 123.2391 | -66.4444 | 56.4377 | 0.04215 | -0.035172 | -0.0032367 | 0.052097 | -0.0074047 | 0.055941 | 0.042884 | -0.0015087 | 0.0011204 | 0.057836 | 0.033947 | 0.060391 | -66.4771 | -0.17716 | -66.453 | 56.4396 | 56.3623 | 56.4954 | -66.636 | -66.4681 | -0.22858 | -66.5301 | 56.3542 | 56.5045 | 56.4711 | -66.8317 | -0.19164 | 0.00187 | -0.032747 | -0.008598 | 0.18305 | -0.075342 | 0.057723 | -0.38733 | -0.083469 | -0.023686 | -0.085664 | 0.30167 | 0.066821 | 0.033394 | 122.8839 | 122.8067 | 122.9398 | 66.2672 | -123.0737 | 122.7986 | 122.9489 | 122.9155 | 66.2158 | -123.2694
456.2656 | 123.1705 | -66.5131 | 56.4056 | 0.057412 | -0.035172 | -0.0032367 | 0.053166 | -0.0074047 | 0.055941 | 0.042884 | -0.0015087 | 0.0021894 | 0.056768 | 0.035015 | 0.058255 | -66.4771 | -0.168 | -66.4393 | 56.4441 | 56.3623 | 56.5 | -66.6315 | -66.4727 | -0.23773 | -66.5255 | 56.3588 | 56.5045 | 56.4757 | -66.8317 | -0.1184 | 0.038491 | 0.035918 | 0.073802 | 0.1922 | -0.043299 | 0.094344 | -0.31866 | -0.046848 | 0.0404 | -0.01242 | 0.30625 | 0.098864 | 0.070016 | 122.9572 | 122.8754 | 123.013 | 66.3451 | -123.0371 | 122.8719 | 123.0176 | 122.9887 | 66.2753 | -123.2374
457.2656 | 123.1613 | -66.4856 | 56.4606 | 0.057412 | -0.035172 | -0.0053737 | 0.051029 | -0.0063367 | 0.05701 | 0.073406 | -0.0015087 | -0.0010156 | 0.058904 | 0.032879 | 0.060391 | -66.4726 | -0.17716 | -66.4438 | 56.4487 | 56.3623 | 56.5 | -66.6406 | -66.4681 | -0.23773 | -66.5255 | 56.3542 | 56.5137 | 56.4757 | -66.8317 | -0.15502 | -0.011862 | 0.01303 | 0.041758 | 0.19678 | -0.09823 | 0.039413 | -0.34613 | -0.10636 | 0.017513 | -0.039886 | 0.30625 | 0.053091 | 0.015085 | 122.9343 | 122.8479 | 122.9856 | 66.3084 | -123.1012 | 122.8398 | 122.9993 | 122.9613 | 66.2479 | -123.2923
458.2656 | 123.1934 | -66.4902 | 56.4056 | 0.011626 | -0.034104 | -0.0043047 | 0.053166 | -0.0063367 | 0.054873 | 0.042884 | -0.0036447 | 0.0011204 | 0.057836 | 0.033947 | 0.059323 | -66.468 | -0.17716 | -66.4438 | 56.4396 | 56.3623 | 56.4954 | -66.636 | -66.4681 | -0.23316 | -66.5209 | 56.3634 | 56.5091 | 56.4757 | -66.8226 | -0.14587 | 0.033913 | 0.022186 | 0.046335 | 0.1922 | -0.043299 | 0.089766 | -0.3324 | -0.042269 | 0.02209 | -0.03073 | 0.30167 | 0.10344 | 0.070016 | 122.9297 | 122.8525 | 122.9856 | 66.313 | -123.0417 | 122.8535 | 122.9993 | 122.9658 | 66.257 | -123.2282
459.2656 | 123.2346 | -66.4673 | 56.4514 | 0.04215 | -0.034104 | -0.0043047 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.058904 | 0.037152 | 0.060391 | -66.4726 | -0.17716 | -66.4438 | 56.4441 | 56.3669 | 56.5046 | -66.636 | -66.4589 | -0.23316 | -66.5255 | 56.3634 | 56.5228 | 56.4802 | -66.8226 | -0.16876 | -0.007285 | -0.005281 | 0.023447 | 0.1922 | -0.084496 | 0.053147 | -0.35528 | -0.088045 | 0.008359 | -0.058197 | 0.29709 | 0.071403 | 0.028818 | 122.9114 | 122.8342 | 122.9718 | 66.2901 | -123.0875 | 122.8307 | 122.9901 | 122.9475 | 66.2341 | -123.274
460.2656 | 123.1155 | -66.5085 | 56.488 | 0.057412 | -0.036241 | -0.0043047 | 0.052097 | -0.0074047 | 0.054873 | 0.058145 | -0.0025767 | 0.0021894 | 0.058904 | 0.033947 | 0.060391 | -66.468 | -0.18174 | -66.4393 | 56.4441 | 56.3303 | 56.5046 | -66.6223 | -66.4589 | -0.23773 | -66.5117 | 56.3679 | 56.5182 | 56.4848 | -66.8317 | -0.11382 | -0.043906 | 0.040497 | 0.069224 | 0.18304 | -0.15775 | 0.016526 | -0.32324 | -0.12009 | 0.049558 | -0.003262 | 0.31998 | 0.030203 | -0.003224 | 122.9526 | 122.8388 | 123.013 | 66.3267 | -123.1103 | 122.8764 | 123.0267 | 122.9933 | 66.2707 | -123.3198
461.2656 | 123.1293 | -66.4856 | 56.4743 | 0.04215 | -0.036241 | -0.0043047 | 0.053166 | -0.0063367 | 0.055941 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.059972 | 0.036084 | 0.058255 | -66.4634 | -0.18174 | -66.4393 | 56.4487 | 56.3532 | 56.5091 | -66.636 | -66.4635 | -0.22858 | -66.5163 | 56.3634 | 56.5182 | 56.4894 | -66.8226 | -0.15045 | -0.025595 | 0.022187 | 0.046336 | 0.19678 | -0.12112 | 0.034838 | -0.33697 | -0.11093 | 0.022091 | -0.030729 | 0.30624 | 0.043936 | 0.015087 | 122.9343 | 122.8388 | 122.9947 | 66.3039 | -123.1103 | 122.849 | 123.0038 | 122.975 | 66.257 | -123.2969
462.2656 | 123.2803 | -66.4673 | 56.456 | 0.072674 | -0.035172 | -0.0053737 | 0.053166 | -0.0084737 | 0.054873 | 0.042884 | -0.0025767 | 0.0011204 | 0.058904 | 0.036084 | 0.060391 | -66.4634 | -0.17258 | -66.4347 | 56.4487 | 56.3623 | 56.5046 | -66.6315 | -66.4589 | -0.224 | -66.5163 | 56.3679 | 56.5182 | 56.4757 | -66.818 | -0.16418 | -0.007285 | 0.003876 | 0.032603 | 0.19678 | -0.093653 | 0.048569 | -0.35071 | -0.088045 | 0.008359 | -0.04904 | 0.30167 | 0.062246 | 0.019662 | 122.916 | 122.8296 | 122.9718 | 66.2947 | -123.0875 | 122.8352 | 122.9855 | 122.9429 | 66.2433 | -123.274
463.2656 | 123.1247 | -66.4993 | 56.4972 | 0.026888 | -0.037309 | -0.0043047 | 0.054234 | -0.0074047 | 0.053805 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.059972 | 0.035015 | 0.060391 | -66.4634 | -0.17258 | -66.4347 | 56.4533 | 56.3715 | 56.5091 | -66.6269 | -66.4543 | -0.23773 | -66.5117 | 56.3679 | 56.532 | 56.4894 | -66.818 | -0.12755 | -0.043904 | 0.03592 | 0.064647 | 0.1922 | -0.12569 | 0.01195 | -0.31866 | -0.12924 | 0.044982 | -0.012417 | 0.30625 | 0.034784 | -0.007801 | 122.9526 | 122.8708 | 123.0085 | 66.3267 | -123.1241 | 122.8673 | 123.0313 | 122.9887 | 66.2616 | -123.3152
464.2656 | 123.2346 | -66.4536 | 56.4514 | 0.026888 | -0.036241 | -0.0043047 | 0.051029 | -0.0074047 | 0.05701 | 0.042884 | -0.0025767 | 0.0011204 | 0.058904 | 0.035015 | 0.060391 | -66.4543 | -0.17716 | -66.4255 | 56.4579 | 56.3486 | 56.5137 | -66.6223 | -66.4498 | -0.23316 | -66.5163 | 56.3725 | 56.5228 | 56.4894 | -66.8088 | -0.16875 | 0.00645 | -0.0007 | 0.028027 | 0.19678 | -0.10281 | 0.062304 | -0.35528 | -0.078888 | 0.003783 | -0.062773 | 0.29251 | 0.071403 | 0.037975 | 122.9114 | 122.8022 | 122.9673 | 66.2764 | -123.0737 | 122.8261 | 122.9764 | 122.9429 | 66.2204 | -123.2602
465.2656 | 123.1934 | -66.4902 | 56.488 | 0.057412 | -0.036241 | -0.0064417 | 0.052097 | -0.0074047 | 0.055941 | 0.042884 | -0.0025767 | 0.0011204 | 0.058904 | 0.035015 | 0.059323 | -66.4543 | -0.18632 | -66.4255 | 56.467 | 56.3166 | 56.5183 | -66.636 | -66.4543 | -0.23773 | -66.5072 | 56.3725 | 56.5228 | 56.494 | -66.8134 | -0.14587 | -0.021014 | 0.035921 | 0.064648 | 0.21052 | -0.17148 | 0.030262 | -0.32324 | -0.11551 | 0.035826 | -0.016994 | 0.30625 | 0.034782 | 0.005933 | 122.9572 | 122.8067 | 123.0085 | 66.3039 | -123.1241 | 122.8627 | 123.013 | 122.9841 | 66.2524 | -123.3014
466.2656 | 123.1384 | -66.5222 | 56.4743 | 0.026888 | -0.035172 | -0.0021677 | 0.054234 | -0.0063367 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.058904 | 0.033947 | 0.058255 | -66.4588 | -0.18632 | -66.4164 | 56.467 | 56.312 | 56.5183 | -66.6269 | -66.4543 | -0.23316 | -66.5072 | 56.3679 | 56.5228 | 56.494 | -66.8134 | -0.10467 | -0.007281 | 0.063386 | 0.10585 | 0.21051 | -0.16233 | 0.043995 | -0.2912 | -0.10635 | 0.06787 | 0.01505 | 0.30625 | 0.048515 | 0.019666 | 122.9892 | 122.8342 | 123.0405 | 66.3359 | -123.1012 | 122.8902 | 123.045 | 123.0162 | 66.2891 | -123.2877
467.2656 | 123.175 | -66.4719 | 56.5201 | 0.04215 | -0.035172 | -0.0021677 | 0.052097 | -0.0084737 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.056768 | 0.037152 | 0.060391 | -66.4451 | -0.18174 | -66.4347 | 56.4624 | 56.3166 | 56.5183 | -66.6269 | -66.4406 | -0.23316 | -66.498 | 56.3725 | 56.532 | 56.5031 | -66.8088 | -0.15502 | -0.057636 | 0.026768 | 0.037181 | 0.1922 | -0.20353 | -0.001782 | -0.33697 | -0.14755 | 0.031252 | -0.026147 | 0.31082 | 0.011895 | -0.016954 | 122.9343 | 122.7884 | 122.9902 | 66.2901 | -123.147 | 122.8444 | 123.0038 | 122.975 | 66.2387 | -123.3289
468.2656 | 123.1842 | -66.4581 | 56.4972 | 0.04215 | -0.037309 | -0.0053737 | 0.052097 | -0.0063367 | 0.053805 | 0.058145 | -0.0015087 | 0.0021894 | 0.058904 | 0.035015 | 0.058255 | -66.4497 | -0.1909 | -66.4209 | 56.467 | 56.3257 | 56.5275 | -66.6223 | -66.436 | -0.24231 | -66.5072 | 56.3817 | 56.532 | 56.5077 | -66.7997 | -0.16417 | -0.030169 | 0.008456 | 0.037183 | 0.20136 | -0.17148 | 0.030264 | -0.34154 | -0.11551 | 0.022098 | -0.049037 | 0.29251 | 0.034784 | 0.010514 | 122.9252 | 122.7838 | 122.9856 | 66.2672 | -123.1195 | 122.8398 | 122.9901 | 122.9658 | 66.2158 | -123.2969
469.2656 | 123.143 | -66.5131 | 56.488 | 0.04215 | -0.036241 | -0.0053737 | 0.053166 | -0.0052687 | 0.055941 | 0.042884 | -0.0025767 | 0.0011204 | 0.058904 | 0.037152 | 0.059323 | -66.4543 | -0.1909 | -66.4209 | 56.467 | 56.3211 | 56.5183 | -66.6223 | -66.4406 | -0.22858 | -66.5026 | 56.3817 | 56.5366 | 56.4985 | -66.8043 | -0.10924 | -0.021014 | 0.05881 | 0.092115 | 0.20136 | -0.16691 | 0.030262 | -0.29119 | -0.10635 | 0.072451 | 0.010474 | 0.30167 | 0.048518 | 0.010512 | 122.9801 | 122.8342 | 123.0314 | 66.3222 | -123.1103 | 122.8947 | 123.0496 | 123.0116 | 66.2845 | -123.2923
470.2656 | 123.1155 | -66.481 | 56.488 | 0.04215 | -0.038378 | -0.0043047 | 0.054234 | -0.0084737 | 0.054873 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.037152 | 0.059323 | -66.4405 | -0.1909 | -66.4118 | 56.4762 | 56.3166 | 56.5275 | -66.6269 | -66.4452 | -0.23773 | -66.498 | 56.3817 | 56.5411 | 56.5077 | -66.7997 | -0.14587 | -0.011857 | 0.040501 | 0.069228 | 0.21509 | -0.17148 | 0.039419 | -0.31866 | -0.10635 | 0.035828 | -0.016992 | 0.30166 | 0.053096 | 0.019669 | 122.9572 | 122.7976 | 123.0085 | 66.2901 | -123.1149 | 122.8627 | 123.0222 | 122.9887 | 66.2433 | -123.2877
471.2656 | 123.1384 | -66.4627 | 56.5155 | 0.057412 | -0.035172 | -0.0043047 | 0.053166 | -0.0084737 | 0.055941 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.057836 | 0.037152 | 0.058255 | -66.4497 | -0.1909 | -66.4164 | 56.4716 | 56.3211 | 56.5229 | -66.6177 | -66.436 | -0.24231 | -66.498 | 56.3863 | 56.5457 | 56.5077 | -66.8088 | -0.15502 | -0.043902 | 0.013034 | 0.046339 | 0.20136 | -0.19437 | 0.007374 | -0.34613 | -0.12924 | 0.026676 | -0.035302 | 0.31082 | 0.030209 | -0.007797 | 122.9343 | 122.7838 | 122.9856 | 66.2718 | -123.1332 | 122.849 | 123.0084 | 122.9704 | 66.2204 | -123.3243
472.2656 | 123.1842 | -66.4581 | 56.5109 | 0.057412 | -0.038378 | -0.0043047 | 0.051029 | -0.0063367 | 0.054873 | 0.058145 | -0.00043967 | -0.0010156 | 0.057836 | 0.036084 | 0.059323 | -66.4405 | -0.1909 | -66.4118 | 56.4762 | 56.3349 | 56.532 | -66.6177 | -66.4406 | -0.23773 | -66.4889 | 56.3863 | 56.5411 | 56.5123 | -66.7997 | -0.15959 | -0.034745 | 0.017613 | 0.04634 | 0.20593 | -0.17606 | 0.02111 | -0.34154 | -0.12466 | 0.017519 | -0.030722 | 0.31082 | 0.030208 | 0.001359 | 122.9343 | 122.793 | 122.9902 | 66.2672 | -123.1286 | 122.8444 | 122.9993 | 122.9704 | 66.2204 | -123.3106
473.2656 | 123.1705 | -66.4444 | 56.4972 | 0.026888 | -0.036241 | -0.0043047 | 0.054234 | -0.0084737 | 0.05701 | 0.073406 | -0.0015087 | 5.2373e-05 | 0.057836 | 0.036084 | 0.058255 | -66.4405 | -0.1909 | -66.4209 | 56.4716 | 56.3394 | 56.5412 | -66.6131 | -66.436 | -0.23316 | -66.4934 | 56.3863 | 56.5457 | 56.5123 | -66.7997 | -0.16875 | -0.025591 | 0.00388 | 0.02345 | 0.1922 | -0.15774 | 0.044 | -0.35528 | -0.11093 | 0.008365 | -0.049034 | 0.30624 | 0.04852 | 0.015092 | 122.916 | 122.7838 | 122.9856 | 66.2535 | -123.1103 | 122.8307 | 122.9901 | 122.9567 | 66.2112 | -123.2969
474.2656 | 123.1201 | -66.4993 | 56.4926 | 0.057412 | -0.036241 | -0.0043047 | 0.053166 | -0.0063367 | 0.054873 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.059972 | 0.037152 | 0.060391 | -66.4359 | -0.1909 | -66.4118 | 56.4853 | 56.3303 | 56.5412 | -66.6131 | -66.4315 | -0.23773 | -66.4934 | 56.3817 | 56.5411 | 56.5123 | -66.7997 | -0.11382 | -0.007279 | 0.06339 | 0.087539 | 0.20136 | -0.16233 | 0.048577 | -0.30035 | -0.11093 | 0.067875 | 0.005898 | 0.30624 | 0.048518 | 0.019669 | 122.9847 | 122.8296 | 123.0405 | 66.3084 | -123.1058 | 122.881 | 123.0405 | 123.0116 | 66.2616 | -123.2923
475.2656 | 123.1293 | -66.4627 | 56.5063 | 0.04215 | -0.038378 | -0.0053737 | 0.053166 | -0.0074047 | 0.054873 | 0.058145 | -0.00043967 | 0.0011204 | 0.057836 | 0.037152 | 0.059323 | -66.4405 | -0.18632 | -66.4118 | 56.4853 | 56.3303 | 56.5366 | -66.6131 | -66.4315 | -0.23316 | -66.4843 | 56.3863 | 56.5411 | 56.5169 | -66.7997 | -0.15044 | -0.021012 | 0.022191 | 0.050918 | 0.20136 | -0.17606 | 0.030265 | -0.33697 | -0.12009 | 0.031254 | -0.021566 | 0.3154 | 0.034785 | 0.010515 | 122.948 | 122.793 | 122.9993 | 66.2764 | -123.1195 | 122.849 | 123.0038 | 122.9796 | 66.2296 | -123.306
476.2656 | 123.175 | -66.4581 | 56.5155 | 0.04215 | -0.038378 | -0.0053737 | 0.055302 | -0.0074047 | 0.055941 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.037152 | 0.060391 | -66.4359 | -0.19547 | -66.4026 | 56.4853 | 56.3349 | 56.5412 | -66.6086 | -66.4269 | -0.23773 | -66.4889 | 56.3954 | 56.5457 | 56.5214 | -66.7951 | -0.15044 | -0.030167 | 0.022191 | 0.055496 | 0.20593 | -0.18064 | 0.025689 | -0.33697 | -0.12008 | 0.031255 | -0.030722 | 0.30625 | 0.030209 | 0.005939 | 122.9435 | 122.793 | 122.9993 | 66.2627 | -123.1241 | 122.8535 | 123.0038 | 122.9796 | 66.2204 | -123.3106
477.2656 | 123.1705 | -66.4215 | 56.5201 | 0.04215 | -0.038378 | -0.0043047 | 0.053166 | -0.0084737 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.058904 | 0.035015 | 0.058255 | -66.4405 | -0.1909 | -66.4072 | 56.4899 | 56.344 | 56.5366 | -66.6086 | -66.4269 | -0.23773 | -66.4843 | 56.3954 | 56.5503 | 56.5214 | -66.7905 | -0.18706 | -0.030166 | -0.019008 | 0.014297 | 0.20136 | -0.17606 | 0.016532 | -0.36901 | -0.12466 | -0.005366 | -0.062765 | 0.30624 | 0.030209 | 0.001361 | 122.9114 | 122.7655 | 122.9581 | 66.2306 | -123.1286 | 122.8169 | 122.9718 | 122.943 | 66.1838 | -123.3106
478.2656 | 123.1476 | -66.4261 | 56.5155 | 0.04215 | -0.037309 | -0.0032367 | 0.053166 | -0.0084737 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.057836 | 0.035015 | 0.06146 | -66.4314 | -0.19547 | -66.4118 | 56.4853 | 56.344 | 56.5503 | -66.6086 | -66.4223 | -0.23773 | -66.4751 | 56.3908 | 56.5549 | 56.526 | -66.7905 | -0.18248 | -0.030167 | -0.005274 | 0.014296 | 0.19678 | -0.17148 | 0.034846 | -0.36443 | -0.12466 | 0.00379 | -0.04903 | 0.3154 | 0.039366 | 0.010517 | 122.9114 | 122.7701 | 122.9764 | 66.2306 | -123.1241 | 122.8169 | 122.981 | 122.9521 | 66.1884 | -123.306
479.2656 | 123.1522 | -66.4169 | 56.5247 | 0.072674 | -0.037309 | -0.0032367 | 0.053166 | -0.0074047 | 0.05701 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.037152 | 0.060391 | -66.4222 | -0.1909 | -66.4072 | 56.4853 | 56.399 | 56.5412 | -66.5948 | -66.4177 | -0.24231 | -66.4797 | 56.3863 | 56.5503 | 56.5214 | -66.7905 | -0.1779 | -0.039322 | -0.005273 | 0.009719 | 0.18762 | -0.12569 | 0.016534 | -0.37359 | -0.1384 | -0.000787 | -0.062764 | 0.31082 | 0.025632 | -0.003216 | 122.9023 | 122.8159 | 122.9581 | 66.226 | -123.1195 | 122.8032 | 122.9672 | 122.9384 | 66.1746 | -123.3152
480.2656 | 123.1842 | -66.4307 | 56.5292 | 0.04215 | -0.039446 | -0.0053737 | 0.04996 | -0.0074047 | 0.055941 | 0.042884 | -0.0015087 | 0.0011204 | 0.057836 | 0.037152 | 0.060391 | -66.4268 | -0.19547 | -66.4026 | 56.4899 | 56.4127 | 56.5412 | -66.5994 | -66.4177 | -0.24689 | -66.4705 | 56.4046 | 56.5549 | 56.526 | -66.7814 | -0.16875 | -0.039321 | 0.003882 | 0.02803 | 0.19678 | -0.11653 | 0.011956 | -0.3507 | -0.12466 | 0.012946 | -0.039874 | 0.31082 | 0.025633 | -0.003216 | 122.9206 | 122.8434 | 122.9719 | 66.2352 | -123.1286 | 122.8352 | 122.9855 | 122.9567 | 66.1838 | -123.3106
481.2656 | 123.1796 | -66.4032 | 56.5521 | 0.04215 | -0.038378 | -0.0043047 | 0.053166 | -0.0084737 | 0.055941 | 0.088667 | -0.0047127 | 5.2373e-05 | 0.057836 | 0.035015 | 0.058255 | -66.4268 | -0.20005 | -66.3935 | 56.4899 | 56.4127 | 56.5458 | -66.5903 | -66.4223 | -0.24231 | -66.466 | 56.4 | 56.5549 | 56.526 | -66.7859 | -0.18705 | -0.062209 | -0.023584 | 0.009721 | 0.19678 | -0.13941 | -0.006354 | -0.38274 | -0.15212 | -0.019098 | -0.062761 | 0.31998 | 0.002745 | -0.026104 | 122.8931 | 122.8159 | 122.949 | 66.2031 | -123.1424 | 122.8032 | 122.9581 | 122.9292 | 66.1609 | -123.3381
482.2656 | 123.0743 | -66.4398 | 56.5613 | 0.011626 | -0.037309 | -0.0032367 | 0.053166 | -0.0084737 | 0.053805 | 0.042884 | -0.0025767 | 0.0011204 | 0.056768 | 0.033947 | 0.059323 | -66.4176 | -0.18632 | -66.3935 | 56.4945 | 56.4173 | 56.5549 | -66.5948 | -66.4131 | -0.23773 | -66.466 | 56.4046 | 56.564 | 56.5306 | -66.7768 | -0.15501 | -0.066786 | 0.022194 | 0.046342 | 0.20135 | -0.14399 | -0.006351 | -0.33696 | -0.1567 | 0.02668 | -0.02614 | 0.31082 | 0.002747 | -0.03068 | 122.9343 | 122.8571 | 122.9947 | 66.2535 | -123.1561 | 122.8444 | 123.0038 | 122.9704 | 66.2021 | -123.3381
483.2656 | 123.175 | -66.4352 | 56.5247 | 0.04215 | -0.037309 | -0.0053737 | 0.053166 | -0.0084737 | 0.055941 | 0.058145 | -0.0036447 | -0.0010156 | 0.057836 | 0.037152 | 0.060391 | -66.4222 | -0.19547 | -66.3981 | 56.5037 | 56.4127 | 56.5549 | -66.5948 | -66.4177 | -0.24689 | -66.4568 | 56.4092 | 56.5594 | 56.5306 | -66.7768 | -0.15959 | -0.021008 | 0.013038 | 0.037187 | 0.19678 | -0.11195 | 0.03027 | -0.34154 | -0.1155 | 0.017524 | -0.021559 | 0.31998 | 0.03479 | 0.005941 | 122.9389 | 122.848 | 122.9902 | 66.2398 | -123.1195 | 122.8444 | 122.9947 | 122.9658 | 66.1884 | -123.3014
484.2656 | 123.0972 | -66.4444 | 56.5338 | 0.072674 | -0.038378 | -0.0043047 | 0.053166 | -0.0084737 | 0.054873 | 0.058145 | -0.0025767 | 0.0011204 | 0.057836 | 0.037152 | 0.060391 | -66.413 | -0.1909 | -66.3889 | 56.5037 | 56.4219 | 56.5549 | -66.5903 | -66.4086 | -0.25605 | -66.4614 | 56.4183 | 56.564 | 56.526 | -66.7768 | -0.14586 | -0.030163 | 0.03135 | 0.055498 | 0.20135 | -0.11195 | 0.021115 | -0.33238 | -0.1155 | 0.035837 | -0.016983 | 0.3154 | 0.030213 | -0.007793 | 122.948 | 122.8663 | 122.9993 | 66.2535 | -123.1241 | 122.8627 | 123.0084 | 122.9704 | 66.1883 | -123.3106
485.2656 | 123.1247 | -66.4444 | 56.5659 | 0.057412 | -0.039446 | -0.0053737 | 0.052097 | -0.0095417 | 0.054873 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.037152 | 0.059323 | -66.413 | -0.1909 | -66.3889 | 56.4945 | 56.4264 | 56.5595 | -66.5903 | -66.404 | -0.24231 | -66.4614 | 56.4183 | 56.564 | 56.5306 | -66.7722 | -0.14586 | -0.071364 | 0.03135 | 0.055498 | 0.20135 | -0.13941 | -0.006351 | -0.32781 | -0.14754 | 0.040416 | -0.016983 | 0.31082 | -0.001831 | -0.035258 | 122.9389 | 122.8708 | 123.0039 | 66.2535 | -123.1561 | 122.8627 | 123.0084 | 122.975 | 66.2021 | -123.3381
486.2656 | 123.175 | -66.4261 | 56.5475 | 0.057412 | -0.037309 | -0.0043047 | 0.055302 | -0.0095417 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.058904 | 0.036084 | 0.059323 | -66.413 | -0.20005 | -66.3889 | 56.5082 | 56.4081 | 56.5687 | -66.5857 | -66.3994 | -0.24689 | -66.4705 | 56.4183 | 56.5686 | 56.5443 | -66.7768 | -0.15959 | -0.039318 | 0.013039 | 0.037187 | 0.19677 | -0.13942 | 0.021117 | -0.3507 | -0.12923 | 0.026683 | -0.044452 | 0.30624 | 0.021059 | -0.003211 | 122.9343 | 122.8342 | 122.9947 | 66.226 | -123.1332 | 122.8444 | 122.9947 | 122.9704 | 66.1792 | -123.3243
487.2656 | 123.1338 | -66.4261 | 56.575 | 0.057412 | -0.039446 | -0.0053737 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.037152 | 0.060391 | -66.4039 | -0.19547 | -66.3889 | 56.5037 | 56.3669 | 56.5641 | -66.5903 | -66.3994 | -0.25605 | -66.4614 | 56.4229 | 56.5732 | 56.5443 | -66.7676 | -0.16417 | -0.071362 | 0.022196 | 0.037187 | 0.20135 | -0.20809 | -0.010927 | -0.34154 | -0.15212 | 0.026683 | -0.035294 | 0.30624 | -0.001829 | -0.030677 | 122.9297 | 122.793 | 122.9902 | 66.2306 | -123.1653 | 122.849 | 122.9993 | 122.9704 | 66.17 | -123.3426
488.2656 | 123.1842 | -66.4444 | 56.5521 | 0.04215 | -0.038378 | -0.0043047 | 0.053166 | -0.0095417 | 0.05701 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.037152 | 0.059323 | -66.4085 | -0.1909 | -66.3843 | 56.5174 | 56.3669 | 56.5595 | -66.5857 | -66.3994 | -0.25147 | -66.4614 | 56.4183 | 56.5686 | 56.5352 | -66.763 | -0.14128 | -0.034739 | 0.035929 | 0.060076 | 0.20135 | -0.1852 | 0.007382 | -0.31865 | -0.13381 | 0.044994 | -0.016983 | 0.30166 | 0.016481 | -0.016947 | 122.9618 | 122.8113 | 123.0039 | 66.2535 | -123.1378 | 122.8627 | 123.013 | 122.9796 | 66.1929 | -123.3152
489.2656 | 123.0057 | -66.4856 | 56.5521 | 0.057412 | -0.037309 | -0.0053737 | 0.052097 | -0.0063367 | 0.055941 | 0.042884 | -0.0047127 | 0.0011204 | 0.056768 | 0.039289 | 0.058255 | -66.4085 | -0.19547 | -66.3843 | 56.5174 | 56.3852 | 56.5778 | -66.5765 | -66.3948 | -0.24689 | -66.4568 | 56.4229 | 56.5823 | 56.5489 | -66.7722 | -0.090919 | -0.034739 | 0.077128 | 0.10128 | 0.19219 | -0.16689 | 0.025697 | -0.28661 | -0.12923 | 0.090772 | 0.028795 | 0.3154 | 0.030217 | -0.003211 | 123.003 | 122.8708 | 123.0634 | 66.2901 | -123.1286 | 122.9085 | 123.0679 | 123.0345 | 66.2387 | -123.3243
490.2656 | 123.1384 | -66.4398 | 56.5338 | 0.04215 | -0.036241 | -0.0053737 | 0.053166 | -0.0074047 | 0.05701 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.037152 | 0.058255 | -66.4085 | -0.19547 | -66.3797 | 56.5128 | 56.431 | 56.5641 | -66.5765 | -66.3902 | -0.24231 | -66.4568 | 56.4275 | 56.5778 | 56.5443 | -66.763 | -0.1367 | -0.021006 | 0.031351 | 0.060077 | 0.19677 | -0.10279 | 0.030272 | -0.32323 | -0.10634 | 0.049574 | -0.016982 | 0.30624 | 0.043949 | 0.010522 | 122.9526 | 122.8708 | 123.0039 | 66.2443 | -123.1103 | 122.8673 | 123.0176 | 122.9842 | 66.1975 | -123.2969
491.2656 | 123.1476 | -66.4169 | 56.5567 | 0.04215 | -0.037309 | -0.0043047 | 0.053166 | -0.0084737 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.058904 | 0.03822 | 0.059323 | -66.4039 | -0.19547 | -66.3752 | 56.5082 | 56.4219 | 56.5687 | -66.5765 | -66.3902 | -0.24689 | -66.4476 | 56.432 | 56.5778 | 56.5535 | -66.763 | -0.15958 | -0.048474 | 0.013041 | 0.041767 | 0.20135 | -0.13484 | 0.011961 | -0.34611 | -0.12465 | 0.026686 | -0.030713 | 0.3154 | 0.02106 | -0.00321 | 122.9252 | 122.8388 | 122.9856 | 66.2215 | -123.1332 | 122.849 | 122.9947 | 122.9704 | 66.17 | -123.3197
492.2656 | 123.2666 | -66.4261 | 56.575 | 0.057412 | -0.037309 | -0.0043047 | 0.053166 | -0.0084737 | 0.055941 | 0.042884 | -0.00043967 | 5.2373e-05 | 0.057836 | 0.037152 | 0.058255 | -66.3993 | -0.19547 | -66.3752 | 56.5128 | 56.4173 | 56.5687 | -66.5765 | -66.3857 | -0.25147 | -66.4568 | 56.432 | 56.5869 | 56.5443 | -66.763 | -0.15043 | -0.062205 | 0.026774 | 0.050922 | 0.20135 | -0.15772 | -0.006349 | -0.33696 | -0.14296 | 0.040419 | -0.030715 | 0.30624 | 0.011907 | -0.030677 | 122.9389 | 122.8434 | 122.9947 | 66.2306 | -123.1515 | 122.8581 | 123.013 | 122.9704 | 66.1746 | -123.3381
493.2656 | 123.143 | -66.4215 | 56.5796 | 0.072674 | -0.038378 | -0.0043047 | 0.053166 | -0.0084737 | 0.058078 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.057836 | 0.036084 | 0.058255 | -66.3993 | -0.20005 | -66.3752 | 56.5128 | 56.4173 | 56.5824 | -66.5719 | -66.3902 | -0.24231 | -66.4476 | 56.4275 | 56.5823 | 56.5535 | -66.7585 | -0.15043 | -0.066783 | 0.022197 | 0.046345 | 0.19677 | -0.1623 | 0.002809 | -0.33696 | -0.15212 | 0.031264 | -0.026135 | 0.31082 | 0.002751 | -0.026098 | 122.9343 | 122.8388 | 123.0039 | 66.2215 | -123.1515 | 122.849 | 123.0038 | 122.975 | 66.1792 | -123.3381
494.2656 | 123.1338 | -66.4169 | 56.5384 | 0.026888 | -0.038378 | -0.0032367 | 0.052097 | -0.0063367 | 0.054873 | 0.042884 | -0.0036447 | 0.0011204 | 0.058904 | 0.03822 | 0.060391 | -66.3856 | -0.20005 | -66.3752 | 56.5265 | 56.4173 | 56.5732 | -66.5628 | -66.3765 | -0.24231 | -66.4431 | 56.432 | 56.5869 | 56.5581 | -66.7585 | -0.14585 | -0.011849 | 0.031355 | 0.041767 | 0.18761 | -0.1211 | 0.034851 | -0.34153 | -0.10634 | 0.040422 | -0.026134 | 0.3154 | 0.048528 | 0.019679 | 122.9435 | 122.8342 | 122.9902 | 66.2169 | -123.1012 | 122.849 | 123.0038 | 122.975 | 66.1746 | -123.2969
495.2656 | 123.1384 | -66.3895 | 56.6116 | 0.04215 | -0.037309 | -0.0053737 | 0.053166 | -0.0084737 | 0.055941 | 0.058145 | -0.0036447 | -0.0010156 | 0.061041 | 0.037152 | 0.058255 | -66.3902 | -0.19547 | -66.366 | 56.522 | 56.4081 | 56.5778 | -66.5674 | -66.3811 | -0.24689 | -66.4431 | 56.432 | 56.5961 | 56.5535 | -66.7539 | -0.17789 | -0.089669 | -0.00069 | 0.023457 | 0.20135 | -0.2035 | -0.033812 | -0.36442 | -0.17958 | 0.008377 | -0.0536 | 0.31082 | -0.015557 | -0.058141 | 122.9114 | 122.7976 | 122.9673 | 66.194 | -123.179 | 122.8215 | 122.9855 | 122.943 | 66.1426 | -123.3655
496.2656 | 123.0377 | -66.4169 | 56.5567 | 0.04215 | -0.039446 | -0.0053737 | 0.051029 | -0.0084737 | 0.055941 | 0.058145 | -0.00043967 | 5.2373e-05 | 0.057836 | 0.036084 | 0.059323 | -66.3902 | -0.19547 | -66.3614 | 56.5311 | 56.4219 | 56.587 | -66.5582 | -66.3765 | -0.24689 | -66.4385 | 56.4366 | 56.5869 | 56.5626 | -66.7493 | -0.14127 | -0.025582 | 0.026776 | 0.055502 | 0.19677 | -0.13484 | 0.030276 | -0.33238 | -0.12007 | 0.040422 | -0.021556 | 0.31082 | 0.030217 | 0.005947 | 122.9481 | 122.8388 | 123.0039 | 66.2215 | -123.1149 | 122.8536 | 123.0038 | 122.9796 | 66.17 | -123.306
497.2656 | 123.1476 | -66.3666 | 56.5979 | 0.04215 | -0.038378 | -0.0053737 | 0.052097 | -0.0063367 | 0.054873 | 0.073406 | -0.0047127 | 0.0011204 | 0.057836 | 0.03822 | 0.060391 | -66.3902 | -0.20005 | -66.3706 | 56.5311 | 56.4402 | 56.5824 | -66.5582 | -66.3765 | -0.24231 | -66.4339 | 56.4366 | 56.5869 | 56.5581 | -66.7447 | -0.19162 | -0.06678 | -0.023578 | -0.004009 | 0.18761 | -0.15772 | -0.015501 | -0.37815 | -0.16127 | -0.009932 | -0.067331 | 0.31082 | -0.010981 | -0.03983 | 122.8977 | 122.8068 | 122.949 | 66.1665 | -123.1561 | 122.8032 | 122.9535 | 122.9246 | 66.1243 | -123.3426
498.2656 | 123.1384 | -66.4124 | 56.5796 | 0.072674 | -0.037309 | -0.0064417 | 0.053166 | -0.0063367 | 0.055941 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.037152 | 0.059323 | -66.3856 | -0.20005 | -66.3523 | 56.5403 | 56.4539 | 56.587 | -66.5536 | -66.3765 | -0.24231 | -66.4293 | 56.4504 | 56.5961 | 56.5626 | -66.7539 | -0.14127 | -0.039313 | 0.026778 | 0.060081 | 0.20135 | -0.12567 | 0.007388 | -0.34153 | -0.12923 | 0.035845 | -0.016975 | 0.32456 | 0.016486 | -0.016941 | 122.9526 | 122.8663 | 122.9993 | 66.2123 | -123.1332 | 122.8627 | 123.0084 | 122.975 | 66.17 | -123.3335
499.2656 | 123.2025 | -66.3712 | 56.5613 | 0.057412 | -0.040514 | -0.0043047 | 0.053166 | -0.0074047 | 0.05701 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.03822 | 0.059323 | -66.381 | -0.20463 | -66.3614 | 56.5357 | 56.3944 | 56.5961 | -66.5536 | -66.3674 | -0.24689 | -66.4248 | 56.4458 | 56.5961 | 56.5718 | -66.7402 | -0.18247 | -0.02558 | -0.009843 | 0.009726 | 0.19219 | -0.16689 | 0.034856 | -0.369 | -0.11549 | 0.003803 | -0.053595 | 0.3154 | 0.034797 | 0.010527 | 122.9069 | 122.7655 | 122.9673 | 66.1665 | -123.1149 | 122.8169 | 122.9672 | 122.943 | 66.1243 | -123.3014
500.2656 | 123.1338 | -66.3895 | 56.5979 | 0.04215 | -0.038378 | -0.0043047 | 0.052097 | -0.0074047 | 0.05701 | 0.058145 | -0.0015087 | 0.0021894 | 0.058904 | 0.036084 | 0.059323 | -66.3718 | -0.20005 | -66.3523 | 56.5357 | 56.3898 | 56.5961 | -66.5582 | -66.3582 | -0.24689 | -66.4293 | 56.4504 | 56.5915 | 56.5718 | -66.7402 | -0.16873 | -0.062201 | 0.017624 | 0.037192 | 0.20593 | -0.20809 | -0.001765 | -0.35069 | -0.14754 | 0.031271 | -0.039864 | 0.31082 | -0.006402 | -0.026094 | 122.9252 | 122.7793 | 122.9856 | 66.1894 | -123.1561 | 122.8398 | 122.981 | 122.9613 | 66.1426 | -123.3381
501.2656 | 123.1659 | -66.3849 | 56.6025 | 0.057412 | -0.037309 | -0.0064417 | 0.053166 | -0.0084737 | 0.05701 | 0.073406 | -0.00043967 | -0.0010156 | 0.058904 | 0.039289 | 0.058255 | -66.381 | -0.20005 | -66.3477 | 56.5311 | 56.3898 | 56.5961 | -66.5582 | -66.3536 | -0.24689 | -66.4202 | 56.4504 | 56.6098 | 56.5718 | -66.7447 | -0.17331 | -0.071358 | 0.00389 | 0.037194 | 0.2105 | -0.21266 | -0.006343 | -0.35984 | -0.15212 | 0.031272 | -0.035284 | 0.32456 | 0.007334 | -0.030672 | 122.916 | 122.7747 | 122.981 | 66.1848 | -123.1607 | 122.8353 | 122.9947 | 122.9567 | 66.138 | -123.3472
502.2656 | 123.143 | -66.3849 | 56.5933 | 0.072674 | -0.040514 | -0.0043047 | 0.052097 | -0.0095417 | 0.054873 | 0.073406 | -0.0015087 | 0.0011204 | 0.056768 | 0.037152 | 0.058255 | -66.3718 | -0.20005 | -66.3477 | 56.5357 | 56.4402 | 56.587 | -66.5582 | -66.3628 | -0.24689 | -66.4248 | 56.4549 | 56.6098 | 56.5764 | -66.7402 | -0.17331 | -0.057624 | 0.013047 | 0.037194 | 0.2105 | -0.15314 | -0.006345 | -0.35526 | -0.13838 | 0.022115 | -0.039862 | 0.3154 | 0.016489 | -0.016938 | 122.9206 | 122.8251 | 122.9719 | 66.1848 | -123.1515 | 122.8398 | 122.9947 | 122.9613 | 66.138 | -123.3335
503.2656 | 123.1796 | -66.3986 | 56.5933 | 0.057412 | -0.037309 | -0.0032367 | 0.052097 | -0.0074047 | 0.055941 | 0.058145 | -0.0025767 | 0.0021894 | 0.057836 | 0.03822 | 0.059323 | -66.3627 | -0.1909 | -66.3477 | 56.5449 | 56.4677 | 56.5961 | -66.549 | -66.349 | -0.24231 | -66.4202 | 56.4595 | 56.6144 | 56.5764 | -66.7356 | -0.15042 | -0.048467 | 0.035936 | 0.050927 | 0.20135 | -0.12567 | 0.002812 | -0.33695 | -0.1338 | 0.049584 | -0.021551 | 0.3154 | 0.021068 | -0.016938 | 122.9435 | 122.8663 | 122.9948 | 66.2077 | -123.1424 | 122.8581 | 123.013 | 122.975 | 66.1563 | -123.3289
504.2656 | 123.1155 | -66.3849 | 56.6025 | 0.04215 | -0.039446 | -0.0043047 | 0.052097 | -0.0095417 | 0.05701 | 0.073406 | -0.0036447 | 0.0011204 | 0.057836 | 0.037152 | 0.060391 | -66.3673 | -0.20921 | -66.3477 | 56.5403 | 56.4631 | 56.6007 | -66.549 | -66.3536 | -0.25147 | -66.4156 | 56.4595 | 56.6144 | 56.581 | -66.731 | -0.16415 | -0.062201 | 0.017625 | 0.037194 | 0.20135 | -0.1394 | -0.001764 | -0.3461 | -0.14296 | 0.031272 | -0.030705 | 0.3154 | 0.011913 | -0.021515 | 122.9252 | 122.848 | 122.9856 | 66.1757 | -123.1515 | 122.8444 | 122.9993 | 122.9659 | 66.1334 | -123.3335
505.2656 | 123.2346 | -66.3483 | 56.5887 | 0.04215 | -0.037309 | -0.0043047 | 0.051029 | -0.0095417 | 0.055941 | 0.042884 | -0.0036447 | 0.0021894 | 0.059972 | 0.036084 | 0.059323 | -66.3673 | -0.20463 | -66.3431 | 56.5449 | 56.4677 | 56.6007 | -66.5399 | -66.3536 | -0.24689 | -66.4156 | 56.4595 | 56.619 | 56.5764 | -66.7402 | -0.19162 | -0.043889 | -0.018996 | 0.005151 | 0.19677 | -0.12109 | 0.011969 | -0.39188 | -0.12923 | -0.005349 | -0.067326 | 0.32456 | 0.030224 | -0.01236 | 122.8931 | 122.8159 | 122.949 | 66.1436 | -123.1286 | 122.8078 | 122.9672 | 122.9247 | 66.1014 | -123.3289
506.2656 | 123.1018 | -66.3986 | 56.6162 | 0.057412 | -0.039446 | -0.0043047 | 0.052097 | -0.0074047 | 0.054873 | 0.088667 | -0.0047127 | 0.0021894 | 0.057836 | 0.037152 | 0.059323 | -66.3627 | -0.20921 | -66.334 | 56.5449 | 56.4722 | 56.6007 | -66.5399 | -66.3582 | -0.24689 | -66.4156 | 56.4595 | 56.619 | 56.581 | -66.7356 | -0.14126 | -0.071355 | 0.035936 | 0.064661 | 0.20592 | -0.14398 | -0.015497 | -0.33695 | -0.15669 | 0.040427 | -0.016972 | 0.31998 | 0.002758 | -0.035248 | 122.9435 | 122.8709 | 122.9993 | 66.1894 | -123.1561 | 122.8581 | 123.0176 | 122.9796 | 66.1517 | -123.3518
507.2656 | 123.2529 | -66.3116 | 56.5704 | 0.04215 | -0.039446 | -0.0053737 | 0.052097 | -0.0074047 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.059972 | 0.039289 | 0.058255 | -66.3627 | -0.20463 | -66.3385 | 56.5449 | 56.4722 | 56.6007 | -66.5399 | -66.349 | -0.24689 | -66.4019 | 56.4549 | 56.619 | 56.581 | -66.7218 | -0.22824 | -0.025579 | -0.051039 | -0.026892 | 0.20135 | -0.0982 | 0.030279 | -0.41019 | -0.11549 | -0.037391 | -0.090211 | 0.31998 | 0.048534 | 0.010528 | 122.8565 | 122.7839 | 122.9124 | 66.107 | -123.1103 | 122.7666 | 122.9306 | 122.8926 | 66.0648 | -123.2923
508.2656 | 123.2437 | -66.3345 | 56.6116 | 0.057412 | -0.039446 | -0.0043047 | 0.052097 | -0.0063367 | 0.054873 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.037152 | 0.060391 | -66.3581 | -0.20463 | -66.3385 | 56.5586 | 56.4127 | 56.6099 | -66.5399 | -66.349 | -0.24231 | -66.4064 | 56.4687 | 56.6235 | 56.5855 | -66.7264 | -0.20535 | -0.053042 | -0.023572 | -0.004004 | 0.20135 | -0.19892 | -0.001762 | -0.39188 | -0.14296 | -0.014503 | -0.071902 | 0.31998 | 0.011915 | -0.026091 | 122.8931 | 122.7472 | 122.9444 | 66.1299 | -123.1515 | 122.8032 | 122.9581 | 122.9201 | 66.0922 | -123.338
509.2656 | 123.2941 | -66.3162 | 56.5887 | 0.04215 | -0.041583 | -0.0043047 | 0.052097 | -0.0084737 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.057836 | 0.03822 | 0.059323 | -66.3581 | -0.20921 | -66.3294 | 56.5586 | 56.4127 | 56.6144 | -66.5399 | -66.3399 | -0.25147 | -66.4064 | 56.4595 | 56.619 | 56.5901 | -66.7173 | -0.22366 | -0.030154 | -0.041883 | -0.013158 | 0.2105 | -0.17604 | 0.025704 | -0.40103 | -0.12923 | -0.023656 | -0.090213 | 0.31082 | 0.030224 | 0.001376 | 122.8748 | 122.7289 | 122.9307 | 66.107 | -123.1286 | 122.7757 | 122.9352 | 122.9063 | 66.0648 | -123.306
510.2656 | 123.1293 | -66.3849 | 56.6162 | 0.057412 | -0.038378 | -0.0053737 | 0.054234 | -0.0084737 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.058904 | 0.037152 | 0.058255 | -66.3627 | -0.20921 | -66.3294 | 56.5677 | 56.4173 | 56.6236 | -66.549 | -66.3353 | -0.24231 | -66.4019 | 56.4641 | 56.619 | 56.5947 | -66.7218 | -0.16415 | -0.048464 | 0.022203 | 0.055507 | 0.21966 | -0.19892 | 0.007396 | -0.33695 | -0.15211 | 0.049587 | -0.016969 | 0.31998 | 0.002758 | -0.021512 | 122.9526 | 122.8022 | 123.0085 | 66.1757 | -123.1653 | 122.849 | 123.0039 | 122.9796 | 66.1426 | -123.338
511.2656 | 123.1796 | -66.3803 | 56.5979 | 0.026888 | -0.039446 | -0.0053737 | 0.052097 | -0.0084737 | 0.05701 | 0.073406 | -0.0047127 | 0.0032574 | 0.057836 | 0.03822 | 0.060391 | -66.3535 | -0.20921 | -66.3385 | 56.5677 | 56.4448 | 56.6236 | -66.5399 | -66.3399 | -0.24231 | -66.4019 | 56.4733 | 56.6281 | 56.5993 | -66.7173 | -0.15957 | -0.030153 | 0.026782 | 0.041772 | 0.20135 | -0.15314 | 0.025707 | -0.33695 | -0.12465 | 0.040431 | -0.021547 | 0.3154 | 0.030227 | 0.001378 | 122.9481 | 122.8251 | 123.0039 | 66.1711 | -123.1378 | 122.8536 | 123.0084 | 122.9796 | 66.138 | -123.3152
512.2656 | 123.2391 | -66.3254 | 56.5796 | 0.04215 | -0.039446 | -0.0053737 | 0.04996 | -0.0084737 | 0.058078 | 0.042884 | -0.0025767 | 0.0011204 | 0.058904 | 0.03822 | 0.059323 | -66.3581 | -0.20463 | -66.3294 | 56.5677 | 56.4402 | 56.6282 | -66.5399 | -66.3353 | -0.23773 | -66.4019 | 56.4733 | 56.6327 | 56.5993 | -66.7173 | -0.21451 | -0.011843 | -0.032728 | -0.004003 | 0.2105 | -0.13941 | 0.048595 | -0.39188 | -0.10634 | -0.009923 | -0.076479 | 0.3154 | 0.053115 | 0.019688 | 122.8931 | 122.7656 | 122.9536 | 66.1207 | -123.1195 | 122.7986 | 122.9581 | 122.9247 | 66.0876 | -123.2968
513.2656 | 123.2117 | -66.3391 | 56.575 | 0.04215 | -0.040514 | -0.0075097 | 0.054234 | -0.0084737 | 0.055941 | 0.073406 | -0.0015087 | 0.0011204 | 0.059972 | 0.041425 | 0.059323 | -66.3489 | -0.20463 | -66.3248 | 56.5723 | 56.4402 | 56.6328 | -66.5353 | -66.3307 | -0.24231 | -66.4019 | 56.4733 | 56.6281 | 56.6039 | -66.7173 | -0.19619 | -0.002686 | -0.009838 | 0.014308 | 0.2105 | -0.13483 | 0.057752 | -0.37815 | -0.10176 | 0.008389 | -0.062746 | 0.3154 | 0.053115 | 0.028844 | 122.9114 | 122.7793 | 122.9719 | 66.1345 | -123.1103 | 122.8124 | 122.9672 | 122.943 | 66.0968 | -123.2923
514.2656 | 123.2574 | -66.3254 | 56.5887 | 0.04215 | -0.037309 | -0.0043047 | 0.052097 | -0.0084737 | 0.054873 | 0.058145 | -0.0025767 | 0.0011204 | 0.058904 | 0.037152 | 0.059323 | -66.3444 | -0.20921 | -66.3248 | 56.5723 | 56.4677 | 56.6328 | -66.5353 | -66.3353 | -0.25147 | -66.3927 | 56.4733 | 56.6327 | 56.613 | -66.7127 | -0.20993 | -0.016419 | -0.018993 | 0.000575 | 0.2105 | -0.12109 | 0.044019 | -0.3873 | -0.11549 | -0.009923 | -0.067321 | 0.31998 | 0.04396 | 0.024269 | 122.8977 | 122.793 | 122.9581 | 66.1162 | -123.124 | 122.7986 | 122.9581 | 122.9384 | 66.0739 | -123.3014
515.2656 | 123.262 | -66.3345 | 56.5887 | 0.026888 | -0.039446 | -0.0064417 | 0.053166 | -0.0074047 | 0.055941 | 0.042884 | -0.0025767 | 0.0011204 | 0.058904 | 0.037152 | 0.059323 | -66.3535 | -0.20463 | -66.3248 | 56.5815 | 56.4493 | 56.6328 | -66.5353 | -66.3353 | -0.24231 | -66.3927 | 56.4824 | 56.6419 | 56.6084 | -66.7173 | -0.20077 | -0.007262 | -0.018994 | 0.009731 | 0.2105 | -0.1394 | 0.044019 | -0.38272 | -0.10633 | -0.000767 | -0.058165 | 0.32456 | 0.053117 | 0.01969 | 122.916 | 122.7839 | 122.9673 | 66.1299 | -123.124 | 122.8169 | 122.9764 | 122.943 | 66.0922 | -123.306
516.2656 | 123.1934 | -66.33 | 56.5933 | 0.04215 | -0.040514 | -0.0053737 | 0.052097 | -0.0084737 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.057836 | 0.039289 | 0.060391 | -66.3398 | -0.20921 | -66.3248 | 56.5769 | 56.4631 | 56.6419 | -66.5307 | -66.3261 | -0.24231 | -66.3835 | 56.4778 | 56.6327 | 56.613 | -66.7081 | -0.20077 | -0.016419 | -0.009837 | 0.005153 | 0.20592 | -0.13024 | 0.048598 | -0.37814 | -0.11549 | 0.003813 | -0.053586 | 0.32456 | 0.039382 | 0.019691 | 122.9069 | 122.793 | 122.9719 | 66.1207 | -123.124 | 122.8078 | 122.9627 | 122.943 | 66.0876 | -123.3014
517.2656 | 123.2574 | -66.3391 | 56.5933 | 0.04215 | -0.038378 | -0.0043047 | 0.052097 | -0.0063367 | 0.055941 | 0.058145 | -0.0025767 | 0.0021894 | 0.058904 | 0.03822 | 0.058255 | -66.3444 | -0.20921 | -66.3111 | 56.5815 | 56.431 | 56.6328 | -66.5261 | -66.3216 | -0.24689 | -66.3927 | 56.4824 | 56.6419 | 56.6084 | -66.7081 | -0.18704 | -0.01184 | -0.00526 | 0.028043 | 0.21508 | -0.1623 | 0.039441 | -0.36899 | -0.11091 | 0.017546 | -0.053588 | 0.3154 | 0.048539 | 0.015112 | 122.9206 | 122.7701 | 122.9719 | 66.1299 | -123.1195 | 122.8215 | 122.981 | 122.9475 | 66.0922 | -123.3014
518.2656 | 123.2712 | -66.3116 | 56.6162 | 0.072674 | -0.040514 | -0.0053737 | 0.052097 | -0.0074047 | 0.055941 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.058904 | 0.039289 | 0.058255 | -66.3398 | -0.20463 | -66.3156 | 56.5861 | 56.4448 | 56.6419 | -66.517 | -66.3261 | -0.24689 | -66.3835 | 56.487 | 56.6419 | 56.613 | -66.7081 | -0.20534 | -0.03015 | -0.028147 | -0.004 | 0.20134 | -0.17145 | 0.02571 | -0.39645 | -0.12922 | -0.014497 | -0.071896 | 0.32456 | 0.025651 | -0.003197 | 122.8977 | 122.7564 | 122.9536 | 66.107 | -123.1332 | 122.7986 | 122.9535 | 122.9247 | 66.0648 | -123.3243
519.2656 | 123.2712 | -66.2933 | 56.5933 | 0.057412 | -0.040514 | -0.0064417 | 0.052097 | -0.0084737 | 0.054873 | 0.042884 | -0.0025767 | 0.0021894 | 0.056768 | 0.03822 | 0.058255 | -66.3352 | -0.20463 | -66.3156 | 56.5769 | 56.431 | 56.6328 | -66.5216 | -66.317 | -0.25605 | -66.3835 | 56.487 | 56.6464 | 56.6176 | -66.7035 | -0.22823 | -0.016419 | -0.041879 | -0.022311 | 0.20592 | -0.1623 | 0.039441 | -0.41018 | -0.10633 | -0.023651 | -0.090207 | 0.31998 | 0.053118 | 0.024269 | 122.8702 | 122.7244 | 122.9261 | 66.0887 | -123.1149 | 122.7803 | 122.9398 | 122.9109 | 66.0373 | -123.2968
520.2656 | 123.1796 | -66.3437 | 56.6071 | 0.072674 | -0.039446 | -0.0032367 | 0.053166 | -0.0084737 | 0.05701 | 0.073406 | -0.0047127 | 0.0032574 | 0.058904 | 0.039289 | 0.058255 | -66.3398 | -0.20005 | -66.3065 | 56.5861 | 56.431 | 56.6328 | -66.5124 | -66.3216 | -0.23773 | -66.3835 | 56.4916 | 56.6373 | 56.6084 | -66.7035 | -0.16872 | -0.020995 | 0.003896 | 0.037199 | 0.20592 | -0.17603 | 0.025708 | -0.35983 | -0.11549 | 0.022124 | -0.039853 | 0.31998 | 0.030228 | 0.001379 | 122.9297 | 122.7747 | 122.9765 | 66.1436 | -123.1195 | 122.8353 | 122.981 | 122.9521 | 66.106 | -123.3106
521.2656 | 123.2117 | -66.3528 | 56.6071 | 0.04215 | -0.038378 | -0.0043047 | 0.04996 | -0.0095417 | 0.058078 | 0.073406 | -0.0015087 | 0.0011204 | 0.059972 | 0.03822 | 0.059323 | -66.3306 | -0.19547 | -66.3065 | 56.5861 | 56.4585 | 56.6511 | -66.5124 | -66.3124 | -0.24231 | -66.3835 | 56.4961 | 56.6464 | 56.613 | -66.6989 | -0.15957 | -0.020995 | 0.022208 | 0.046354 | 0.20592 | -0.14856 | 0.044022 | -0.3461 | -0.11091 | 0.040437 | -0.030698 | 0.3154 | 0.039385 | 0.005958 | 122.9389 | 122.8113 | 123.0039 | 66.1574 | -123.1195 | 122.849 | 122.9993 | 122.9659 | 66.1105 | -123.306
522.2656 | 123.2574 | -66.3071 | 56.6025 | 0.04215 | -0.042651 | -0.0053737 | 0.052097 | -0.0084737 | 0.055941 | 0.088667 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.041425 | 0.059323 | -66.3261 | -0.20005 | -66.3111 | 56.5769 | 56.4722 | 56.6419 | -66.517 | -66.317 | -0.24689 | -66.3744 | 56.4916 | 56.651 | 56.6176 | -66.6944 | -0.20992 | -0.025574 | -0.018989 | -0.004 | 0.20592 | -0.13024 | 0.039443 | -0.38729 | -0.11091 | -0.009918 | -0.067317 | 0.31998 | 0.048542 | 0.015114 | 122.884 | 122.7793 | 122.949 | 66.107 | -123.1195 | 122.7986 | 122.9581 | 122.9247 | 66.0602 | -123.2968
523.2656 | 123.2254 | -66.3116 | 56.5887 | 0.04215 | -0.040514 | -0.0032367 | 0.052097 | -0.0084737 | 0.05701 | 0.073406 | -0.0036447 | 0.0011204 | 0.057836 | 0.041425 | 0.058255 | -66.3306 | -0.19547 | -66.3065 | 56.5861 | 56.4722 | 56.6419 | -66.517 | -66.3078 | -0.24231 | -66.379 | 56.5007 | 56.6556 | 56.613 | -66.6944 | -0.20534 | -0.002684 | -0.01899 | 0.005156 | 0.2105 | -0.11651 | 0.053176 | -0.38272 | -0.088019 | 0.003818 | -0.067317 | 0.3154 | 0.066853 | 0.024269 | 122.8977 | 122.7839 | 122.9536 | 66.1162 | -123.1057 | 122.8124 | 122.9672 | 122.9247 | 66.0693 | -123.2831
524.2656 | 123.2849 | -66.2842 | 56.6345 | 0.04215 | -0.039446 | -0.0032367 | 0.052097 | -0.0084737 | 0.05701 | 0.042884 | -0.0036447 | 0.0021894 | 0.057836 | 0.041425 | 0.058255 | -66.3261 | -0.20463 | -66.3019 | 56.5906 | 56.4631 | 56.6465 | -66.5033 | -66.3078 | -0.24231 | -66.3652 | 56.5053 | 56.6464 | 56.6176 | -66.6989 | -0.21907 | -0.043882 | -0.041877 | -0.017732 | 0.20134 | -0.17144 | 0.011979 | -0.41476 | -0.12922 | -0.023648 | -0.081047 | 0.33371 | 0.01192 | -0.016929 | 122.8748 | 122.7473 | 122.9307 | 66.0795 | -123.1378 | 122.7895 | 122.9306 | 122.9018 | 66.0419 | -123.3335
525.2656 | 123.2117 | -66.3254 | 56.6116 | 0.057412 | -0.040514 | -0.0053737 | 0.052097 | -0.0084737 | 0.054873 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.058904 | 0.040357 | 0.058255 | -66.3261 | -0.20463 | -66.3019 | 56.5906 | 56.5043 | 56.6465 | -66.5033 | -66.3033 | -0.24231 | -66.3744 | 56.5053 | 56.651 | 56.6222 | -66.6989 | -0.17787 | -0.020994 | -0.000679 | 0.023466 | 0.20134 | -0.10734 | 0.034867 | -0.37356 | -0.10633 | 0.022128 | -0.049007 | 0.32456 | 0.039387 | 0.010538 | 122.916 | 122.8297 | 122.9719 | 66.1207 | -123.1149 | 122.8307 | 122.9764 | 122.9475 | 66.0831 | -123.3106
526.2656 | 123.2437 | -66.2979 | 56.5979 | 0.026888 | -0.040514 | -0.0053737 | 0.051029 | -0.0074047 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.057836 | 0.040357 | 0.058255 | -66.3215 | -0.20463 | -66.2928 | 56.5906 | 56.5134 | 56.6511 | -66.4895 | -66.3033 | -0.23773 | -66.3698 | 56.5099 | 56.6556 | 56.6222 | -66.6898 | -0.1916 | -0.007261 | -0.023566 | 0.005158 | 0.19676 | -0.084454 | 0.053178 | -0.39187 | -0.088017 | -0.005337 | -0.071893 | 0.31998 | 0.057698 | 0.024271 | 122.8886 | 122.8114 | 122.949 | 66.0933 | -123.0874 | 122.8078 | 122.9535 | 122.9201 | 66.0602 | -123.2877
527.2656 | 123.1934 | -66.3162 | 56.6299 | 0.057412 | -0.039446 | -0.0043047 | 0.052097 | -0.0084737 | 0.05701 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.058904 | 0.040357 | 0.059323 | -66.3123 | -0.20005 | -66.3065 | 56.5952 | 56.5134 | 56.6557 | -66.4987 | -66.2941 | -0.24231 | -66.3606 | 56.5053 | 56.6648 | 56.6222 | -66.6898 | -0.18245 | -0.034726 | 0.003901 | 0.009733 | 0.19218 | -0.1165 | 0.025713 | -0.37356 | -0.12464 | 0.022131 | -0.044425 | 0.32914 | 0.034811 | -0.007773 | 122.9114 | 122.8297 | 122.9719 | 66.1162 | -123.1286 | 122.8215 | 122.981 | 122.9384 | 66.0739 | -123.3197
528.2656 | 123.2712 | -66.3254 | 56.5979 | 0.04215 | -0.041583 | -0.0053737 | 0.051029 | -0.0084737 | 0.054873 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.056768 | 0.039289 | 0.057187 | -66.3123 | -0.20005 | -66.2928 | 56.5998 | 56.5134 | 56.6557 | -66.4987 | -66.2941 | -0.24231 | -66.3606 | 56.5007 | 56.6556 | 56.6267 | -66.6852 | -0.17329 | 0.001896 | 0.013056 | 0.032623 | 0.20592 | -0.084454 | 0.057757 | -0.35983 | -0.097174 | 0.031286 | -0.03527 | 0.32456 | 0.057698 | 0.028849 | 122.9252 | 122.8388 | 122.981 | 66.1253 | -123.0966 | 122.8261 | 122.981 | 122.9521 | 66.0831 | -123.2831
529.2656 | 123.23 | -66.3254 | 56.5933 | 0.04215 | -0.040514 | -0.0053737 | 0.052097 | -0.0084737 | 0.054873 | 0.058145 | -0.0025767 | 0.0011204 | 0.057836 | 0.040357 | 0.058255 | -66.2986 | -0.20005 | -66.2882 | 56.5998 | 56.4906 | 56.6648 | -66.4895 | -66.2941 | -0.23773 | -66.3606 | 56.5099 | 56.6648 | 56.6359 | -66.6806 | -0.16414 | 0.006473 | 0.026791 | 0.037201 | 0.20134 | -0.10277 | 0.071491 | -0.35525 | -0.08344 | 0.031286 | -0.03527 | 0.31998 | 0.071432 | 0.042584 | 122.9252 | 122.8159 | 122.9902 | 66.1253 | -123.0828 | 122.8353 | 122.9901 | 122.9613 | 66.0876 | -123.2739
530.2656 | 123.2346 | -66.3208 | 56.6071 | 0.057412 | -0.042651 | -0.0053737 | 0.052097 | -0.0074047 | 0.05701 | 0.042884 | -0.0036447 | 0.0032574 | 0.057836 | 0.040357 | 0.058255 | -66.3077 | -0.19547 | -66.2882 | 56.6044 | 56.486 | 56.6557 | -66.4941 | -66.2895 | -0.24231 | -66.3561 | 56.519 | 56.6648 | 56.6267 | -66.6806 | -0.17329 | -0.002681 | 0.013057 | 0.032624 | 0.20592 | -0.12108 | 0.048601 | -0.35983 | -0.088016 | 0.031287 | -0.035269 | 0.32456 | 0.057699 | 0.019693 | 122.9252 | 122.8068 | 122.9765 | 66.1253 | -123.1012 | 122.8398 | 122.9856 | 122.9476 | 66.0785 | -123.2877
531.2656 | 123.2117 | -66.3116 | 56.6391 | 0.04215 | -0.041583 | -0.0043047 | 0.053166 | -0.0084737 | 0.05701 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.056768 | 0.040357 | 0.056118 | -66.3032 | -0.20463 | -66.2882 | 56.5998 | 56.486 | 56.6557 | -66.4849 | -66.2987 | -0.24231 | -66.3561 | 56.5099 | 56.6693 | 56.6313 | -66.6852 | -0.17329 | -0.039303 | 0.008481 | 0.023469 | 0.19676 | -0.15313 | 0.016558 | -0.37356 | -0.12922 | 0.012975 | -0.044424 | 0.32913 | 0.030235 | -0.007771 | 122.9114 | 122.7976 | 122.9673 | 66.107 | -123.124 | 122.8215 | 122.981 | 122.943 | 66.0693 | -123.3243
532.2656 | 123.143 | -66.3345 | 56.6666 | 0.04215 | -0.041583 | -0.0053737 | 0.052097 | -0.0095417 | 0.055941 | 0.073406 | -0.0025767 | -0.0010156 | 0.058904 | 0.040357 | 0.056118 | -66.3032 | -0.20463 | -66.2836 | 56.5998 | 56.5134 | 56.6648 | -66.4849 | -66.2849 | -0.24231 | -66.3515 | 56.519 | 56.6648 | 56.6313 | -66.6806 | -0.1504 | -0.066769 | 0.031369 | 0.050936 | 0.20134 | -0.15312 | -0.001751 | -0.34609 | -0.14753 | 0.049599 | -0.016957 | 0.32914 | -0.00181 | -0.035237 | 122.9343 | 122.848 | 122.9993 | 66.1299 | -123.1515 | 122.8536 | 122.9993 | 122.9659 | 66.0922 | -123.3472
533.2656 | 123.2346 | -66.2979 | 56.5842 | 0.04215 | -0.040514 | -0.0053737 | 0.051029 | -0.0074047 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.057836 | 0.040357 | 0.059323 | -66.2986 | -0.19547 | -66.279 | 56.609 | 56.518 | 56.6694 | -66.4804 | -66.2895 | -0.24231 | -66.3515 | 56.5145 | 56.6739 | 56.6405 | -66.676 | -0.18245 | 0.024786 | -0.000674 | 0.018893 | 0.20134 | -0.066142 | 0.085226 | -0.37813 | -0.069706 | 0.008399 | -0.053578 | 0.32456 | 0.089746 | 0.056318 | 122.9069 | 122.8159 | 122.9673 | 66.1024 | -123.0645 | 122.8124 | 122.9718 | 122.9384 | 66.0556 | -123.2602
534.2656 | 123.2666 | -66.2567 | 56.6025 | 0.072674 | -0.039446 | -0.0053737 | 0.051029 | -0.0084737 | 0.055941 | 0.042884 | -0.0047127 | 5.2373e-05 | 0.058904 | 0.040357 | 0.057187 | -66.2986 | -0.20005 | -66.2744 | 56.5998 | 56.5089 | 56.6602 | -66.4758 | -66.2895 | -0.24231 | -66.3515 | 56.5282 | 56.6693 | 56.6359 | -66.6806 | -0.21907 | -0.002682 | -0.041873 | -0.017728 | 0.20134 | -0.093611 | 0.057757 | -0.42391 | -0.074281 | -0.0328 | -0.094777 | 0.32914 | 0.066856 | 0.033429 | 122.8565 | 122.7656 | 122.9169 | 66.0567 | -123.0783 | 122.7849 | 122.926 | 122.8926 | 66.0144 | -123.2831
535.2656 | 123.1934 | -66.3071 | 56.6208 | 0.04215 | -0.040514 | -0.0064417 | 0.04996 | -0.0095417 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.056768 | 0.041425 | 0.058255 | -66.2986 | -0.20005 | -66.2699 | 56.609 | 56.4997 | 56.6694 | -66.4804 | -66.2804 | -0.23773 | -66.3469 | 56.5282 | 56.6831 | 56.6359 | -66.6669 | -0.17329 | -0.011836 | 0.008481 | 0.037204 | 0.21049 | -0.12108 | 0.048604 | -0.35982 | -0.092592 | 0.026712 | -0.039844 | 0.31998 | 0.062281 | 0.015118 | 122.916 | 122.8068 | 122.9765 | 66.107 | -123.1011 | 122.8353 | 122.9901 | 122.943 | 66.0693 | -123.2877
536.2656 | 123.2346 | -66.2842 | 56.6254 | 0.04215 | -0.039446 | -0.0064417 | 0.04996 | -0.0095417 | 0.054873 | 0.073406 | -0.0036447 | 0.0011204 | 0.057836 | 0.039289 | 0.057187 | -66.2894 | -0.1909 | -66.2836 | 56.609 | 56.5318 | 56.6694 | -66.4804 | -66.2849 | -0.24689 | -66.3515 | 56.5145 | 56.6785 | 56.6405 | -66.676 | -0.19618 | -0.016413 | -0.00525 | 0.000582 | 0.19676 | -0.093605 | 0.044027 | -0.39187 | -0.11091 | -0.000755 | -0.067311 | 0.32456 | 0.053125 | 0.015119 | 122.8931 | 122.8159 | 122.9536 | 66.0933 | -123.1057 | 122.7986 | 122.9627 | 122.9247 | 66.0373 | -123.3014
537.2656 | 123.1567 | -66.3208 | 56.6757 | 0.04215 | -0.041583 | -0.0053737 | 0.052097 | -0.0074047 | 0.05701 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.056768 | 0.041425 | 0.059323 | -66.2894 | -0.20005 | -66.2744 | 56.6135 | 56.5409 | 56.6786 | -66.4758 | -66.2758 | -0.24231 | -66.3378 | 56.5282 | 56.6785 | 56.6542 | -66.6623 | -0.15498 | -0.062189 | 0.031371 | 0.046359 | 0.20134 | -0.1348 | 0.00283 | -0.34151 | -0.14752 | 0.045023 | -0.016954 | 0.32456 | 0.002771 | -0.021499 | 122.9343 | 122.8617 | 122.9994 | 66.1207 | -123.1515 | 122.849 | 122.9993 | 122.975 | 66.0785 | -123.338
538.2656 | 123.23 | -66.2933 | 56.6299 | 0.04215 | -0.040514 | -0.0053737 | 0.04996 | -0.0084737 | 0.054873 | 0.058145 | -0.0015087 | 0.0011204 | 0.058904 | 0.041425 | 0.058255 | -66.2894 | -0.20005 | -66.2744 | 56.6181 | 56.5363 | 56.6831 | -66.4758 | -66.2804 | -0.24231 | -66.3423 | 56.5236 | 56.6876 | 56.6451 | -66.6623 | -0.18244 | -0.011834 | 0.003905 | 0.018893 | 0.20134 | -0.093604 | 0.053184 | -0.36898 | -0.10633 | 0.012979 | -0.048999 | 0.31998 | 0.057704 | 0.01512 | 122.9114 | 122.8297 | 122.9765 | 66.0933 | -123.1057 | 122.817 | 122.981 | 122.9384 | 66.051 | -123.2923
539.2656 | 123.2208 | -66.2704 | 56.6574 | 0.057412 | -0.041583 | -0.0053737 | 0.051029 | -0.0074047 | 0.05701 | 0.058145 | -0.0025767 | 0.0011204 | 0.057836 | 0.042494 | 0.059323 | -66.2803 | -0.19547 | -66.2744 | 56.6227 | 56.5455 | 56.674 | -66.4666 | -66.2712 | -0.24231 | -66.3423 | 56.5328 | 56.6876 | 56.6496 | -66.6623 | -0.19617 | -0.034722 | -0.009827 | -0.003995 | 0.19218 | -0.11191 | 0.016561 | -0.39186 | -0.12463 | -0.000752 | -0.071887 | 0.31998 | 0.030238 | -0.007768 | 122.8931 | 122.8159 | 122.9444 | 66.075 | -123.124 | 122.8032 | 122.9581 | 122.9201 | 66.0281 | -123.3197
540.2656 | 123.2391 | -66.2933 | 56.6391 | 0.072674 | -0.042651 | -0.0053737 | 0.051029 | -0.0095417 | 0.053805 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.040357 | 0.056118 | -66.2894 | -0.20005 | -66.2653 | 56.6227 | 56.5455 | 56.674 | -66.4666 | -66.2666 | -0.24231 | -66.3378 | 56.5328 | 56.6785 | 56.6496 | -66.6623 | -0.17329 | -0.016411 | 0.003905 | 0.02805 | 0.20134 | -0.093601 | 0.034872 | -0.36898 | -0.10632 | 0.026715 | -0.04442 | 0.32456 | 0.039392 | 0.010543 | 122.916 | 122.8388 | 122.9673 | 66.0933 | -123.1057 | 122.8261 | 122.9718 | 122.943 | 66.051 | -123.3014
541.2656 | 123.2758 | -66.275 | 56.6345 | 0.04215 | -0.041583 | -0.0064417 | 0.052097 | -0.0084737 | 0.055941 | 0.058145 | -0.0047127 | -0.0020846 | 0.056768 | 0.040357 | 0.058255 | -66.2849 | -0.20463 | -66.2607 | 56.6181 | 56.5409 | 56.6786 | -66.4712 | -66.2712 | -0.24689 | -66.3286 | 56.5328 | 56.6922 | 56.6542 | -66.6623 | -0.19618 | -0.016411 | -0.009828 | 0.014317 | 0.21049 | -0.093602 | 0.044029 | -0.38729 | -0.10175 | 0.003825 | -0.053574 | 0.33371 | 0.057706 | 0.0197 | 122.8931 | 122.8159 | 122.9536 | 66.0704 | -123.1057 | 122.8078 | 122.9673 | 122.9292 | 66.0281 | -123.2968
542.2656 | 123.3078 | -66.275 | 56.6299 | 0.04215 | -0.042651 | -0.0053737 | 0.051029 | -0.01061 | 0.053805 | 0.058145 | -0.0047127 | 0.0011204 | 0.056768 | 0.041425 | 0.059323 | -66.2849 | -0.20921 | -66.2607 | 56.6227 | 56.4951 | 56.6831 | -66.4758 | -66.2712 | -0.24689 | -66.3332 | 56.5282 | 56.6922 | 56.6588 | -66.6577 | -0.20076 | -0.007256 | -0.009828 | 0.014317 | 0.21507 | -0.13481 | 0.053184 | -0.38271 | -0.10175 | 0.003825 | -0.058152 | 0.32456 | 0.062283 | 0.028856 | 122.8977 | 122.7702 | 122.9582 | 66.0658 | -123.1057 | 122.8032 | 122.9673 | 122.9338 | 66.0281 | -123.2877
543.2656 | 123.2529 | -66.2933 | 56.6299 | 0.04215 | -0.042651 | -0.0064417 | 0.04996 | -0.0074047 | 0.055941 | 0.042884 | -0.0015087 | 5.2373e-05 | 0.057836 | 0.041425 | 0.058255 | -66.2849 | -0.20921 | -66.2561 | 56.6273 | 56.4768 | 56.6877 | -66.4758 | -66.2575 | -0.24231 | -66.3332 | 56.5374 | 56.6922 | 56.6588 | -66.6532 | -0.18244 | -0.002678 | 0.008483 | 0.037206 | 0.21965 | -0.15313 | 0.057763 | -0.35982 | -0.09259 | 0.035872 | -0.039841 | 0.31998 | 0.062283 | 0.028856 | 122.9206 | 122.7701 | 122.981 | 66.0841 | -123.1057 | 122.8307 | 122.9856 | 122.9521 | 66.051 | -123.2831
544.2656 | 123.2986 | -66.2704 | 56.6574 | 0.057412 | -0.041583 | -0.0043047 | 0.053166 | -0.0095417 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.056768 | 0.043562 | 0.057187 | -66.2711 | -0.21379 | -66.2561 | 56.6318 | 56.486 | 56.6969 | -66.4712 | -66.262 | -0.25147 | -66.3286 | 56.5374 | 56.7014 | 56.6588 | -66.6577 | -0.20075 | -0.025565 | -0.00067 | 0.014318 | 0.21507 | -0.17144 | 0.039454 | -0.38728 | -0.12006 | 0.008406 | -0.058151 | 0.32913 | 0.043974 | 0.00139 | 122.9023 | 122.7564 | 122.9673 | 66.0567 | -123.1286 | 122.8078 | 122.9718 | 122.9292 | 66.019 | -123.3151
545.2656 | 123.2803 | -66.2933 | 56.6208 | 0.026888 | -0.041583 | -0.0064417 | 0.051029 | -0.0084737 | 0.05701 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.058904 | 0.041425 | 0.058255 | -66.2849 | -0.21837 | -66.2561 | 56.6318 | 56.4814 | 56.6969 | -66.4666 | -66.2529 | -0.25147 | -66.3332 | 56.5374 | 56.6922 | 56.668 | -66.6577 | -0.17329 | 0.011056 | 0.008483 | 0.037206 | 0.21049 | -0.1394 | 0.076075 | -0.3644 | -0.083435 | 0.040451 | -0.039841 | 0.32456 | 0.071438 | 0.047168 | 122.9252 | 122.7747 | 122.9902 | 66.075 | -123.0874 | 122.8307 | 122.9856 | 122.9613 | 66.0419 | -123.2785
546.2656 | 123.2162 | -66.2796 | 56.6437 | 0.026888 | -0.042651 | -0.0053737 | 0.051029 | -0.0084737 | 0.055941 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.057836 | 0.041425 | 0.056118 | -66.2757 | -0.21837 | -66.2561 | 56.6318 | 56.4951 | 56.7014 | -66.462 | -66.2529 | -0.24689 | -66.3332 | 56.5465 | 56.7014 | 56.6725 | -66.6486 | -0.18244 | -0.011832 | 0.003907 | 0.023473 | 0.20591 | -0.14855 | 0.057766 | -0.36897 | -0.097166 | 0.026718 | -0.053574 | 0.3154 | 0.057707 | 0.028858 | 122.9114 | 122.7747 | 122.981 | 66.0612 | -123.1057 | 122.8261 | 122.981 | 122.9521 | 66.0327 | -123.2923
547.2656 | 123.2346 | -66.2476 | 56.6757 | 0.057412 | -0.041583 | -0.0064417 | 0.051029 | -0.0084737 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.057836 | 0.042494 | 0.057187 | -66.2757 | -0.21837 | -66.2516 | 56.641 | 56.5043 | 56.7014 | -66.4804 | -66.2575 | -0.24231 | -66.324 | 56.5465 | 56.706 | 56.668 | -66.6532 | -0.2328 | -0.034718 | -0.028136 | -0.003992 | 0.22881 | -0.17143 | 0.025723 | -0.40559 | -0.12921 | -0.009904 | -0.07646 | 0.32913 | 0.030243 | -0.007763 | 122.8886 | 122.7518 | 122.949 | 66.0292 | -123.1561 | 122.7941 | 122.9535 | 122.9155 | 66.0052 | -123.3289
548.2656 | 123.2346 | -66.2659 | 56.6254 | 0.04215 | -0.043719 | -0.0053737 | 0.052097 | -0.0084737 | 0.054873 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.056768 | 0.040357 | 0.058255 | -66.2665 | -0.21837 | -66.2561 | 56.6456 | 56.5318 | 56.6969 | -66.462 | -66.2575 | -0.24689 | -66.3194 | 56.5465 | 56.7014 | 56.6771 | -66.6577 | -0.19617 | 0.020214 | -0.000669 | 0.00974 | 0.20591 | -0.093605 | 0.071498 | -0.39186 | -0.078855 | 0.008406 | -0.053571 | 0.33829 | 0.076018 | 0.051748 | 122.9114 | 122.7976 | 122.9627 | 66.0475 | -123.0874 | 122.8124 | 122.9673 | 122.943 | 66.019 | -123.2831
549.2656 | 123.2117 | -66.2704 | 56.662 | 0.04215 | -0.041583 | -0.0053737 | 0.051029 | -0.0084737 | 0.055941 | 0.042884 | -0.0025767 | 0.0021894 | 0.058904 | 0.041425 | 0.058255 | -66.2757 | -0.22752 | -66.2516 | 56.6456 | 56.5409 | 56.7014 | -66.462 | -66.2483 | -0.24689 | -66.3332 | 56.5557 | 56.706 | 56.6771 | -66.6532 | -0.19159 | -0.016407 | -0.005248 | 0.018896 | 0.21049 | -0.12107 | 0.039456 | -0.38271 | -0.10632 | 0.022142 | -0.062729 | 0.31998 | 0.043976 | 0.015127 | 122.916 | 122.8114 | 122.9719 | 66.0429 | -123.124 | 122.8261 | 122.9764 | 122.9476 | 66.0236 | -123.3151
550.2656 | 123.1979 | -66.2888 | 56.6437 | 0.072674 | -0.040514 | -0.0064417 | 0.052097 | -0.0074047 | 0.055941 | 0.073406 | -0.0036447 | 0.0021894 | 0.056768 | 0.041425 | 0.057187 | -66.262 | -0.22752 | -66.2516 | 56.6456 | 56.5592 | 56.7152 | -66.4758 | -66.2529 | -0.25605 | -66.3194 | 56.5557 | 56.7105 | 56.6817 | -66.644 | -0.18702 | 0.001903 | 0.026797 | 0.037206 | 0.22423 | -0.084442 | 0.071502 | -0.35524 | -0.088009 | 0.035873 | -0.030683 | 0.32456 | 0.066864 | 0.038016 | 122.9343 | 122.848 | 123.0039 | 66.0612 | -123.1195 | 122.8444 | 122.9993 | 122.9704 | 66.0327 | -123.2877
551.2656 | 123.2666 | -66.2933 | 56.6254 | 0.04215 | -0.043719 | -0.0064417 | 0.04996 | -0.0084737 | 0.05701 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.0557 | 0.041425 | 0.057187 | -66.2711 | -0.2321 | -66.2561 | 56.6502 | 56.5547 | 56.706 | -66.462 | -66.2437 | -0.25147 | -66.324 | 56.5511 | 56.7014 | 56.6817 | -66.6577 | -0.16871 | 0.024792 | 0.022218 | 0.037206 | 0.20591 | -0.07071 | 0.080655 | -0.3644 | -0.074277 | 0.049608 | -0.030684 | 0.33371 | 0.076018 | 0.056327 | 122.9435 | 122.848 | 122.9994 | 66.0612 | -123.0874 | 122.8444 | 122.9947 | 122.975 | 66.0419 | -123.2831
552.2656 | 123.1842 | -66.2933 | 56.6803 | 0.04215 | -0.043719 | -0.0064417 | 0.051029 | -0.0084737 | 0.054873 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.042494 | 0.057187 | -66.262 | -0.22752 | -66.2561 | 56.6502 | 56.5455 | 56.7152 | -66.4666 | -66.2483 | -0.25605 | -66.3103 | 56.5511 | 56.706 | 56.6908 | -66.644 | -0.17329 | -0.03014 | 0.031375 | 0.037206 | 0.21049 | -0.1348 | 0.034881 | -0.35066 | -0.12921 | 0.04503 | -0.016948 | 0.33371 | 0.025665 | 0.010552 | 122.9435 | 122.8388 | 123.0085 | 66.0658 | -123.1469 | 122.8444 | 122.9993 | 122.9842 | 66.0373 | -123.3243
553.2656 | 123.2574 | -66.2659 | 56.6345 | 0.057412 | -0.041583 | -0.0064417 | 0.051029 | -0.0084737 | 0.05701 | 0.073406 | -0.0015087 | 0.0011204 | 0.057836 | 0.043562 | 0.058255 | -66.2665 | -0.23668 | -66.247 | 56.6456 | 56.4997 | 56.706 | -66.4529 | -66.2437 | -0.25147 | -66.3194 | 56.5465 | 56.7151 | 56.6817 | -66.6486 | -0.18702 | 0.011059 | -0.000669 | 0.018897 | 0.20591 | -0.13481 | 0.0715 | -0.38271 | -0.08801 | 0.022142 | -0.053571 | 0.32913 | 0.080599 | 0.047172 | 122.9114 | 122.7656 | 122.9719 | 66.0292 | -123.0874 | 122.8124 | 122.981 | 122.9476 | 66.0144 | -123.2831
554.2656 | 123.2574 | -66.2704 | 56.6711 | 0.04215 | -0.041583 | -0.0053737 | 0.051029 | -0.0063367 | 0.05701 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.057836 | 0.042494 | 0.058255 | -66.262 | -0.23668 | -66.2424 | 56.641 | 56.5043 | 56.706 | -66.4529 | -66.2391 | -0.25147 | -66.3103 | 56.5557 | 56.7105 | 56.6771 | -66.644 | -0.18244 | -0.030141 | 0.008487 | 0.028053 | 0.21049 | -0.16685 | 0.034878 | -0.37355 | -0.11548 | 0.031299 | -0.039836 | 0.33371 | 0.039398 | 0.005971 | 122.9114 | 122.7747 | 122.9765 | 66.0338 | -123.124 | 122.8261 | 122.981 | 122.9476 | 66.019 | -123.3151
555.2656 | 123.2483 | -66.2521 | 56.6345 | 0.04215 | -0.042651 | -0.0053737 | 0.052097 | -0.0095417 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.057836 | 0.042494 | 0.058255 | -66.2574 | -0.24126 | -66.2378 | 56.6547 | 56.5592 | 56.7106 | -66.4437 | -66.23 | -0.24689 | -66.3057 | 56.5557 | 56.7243 | 56.6725 | -66.6394 | -0.19159 | 0.020216 | -0.005246 | 0.01432 | 0.20591 | -0.075286 | 0.076079 | -0.38728 | -0.078853 | 0.022146 | -0.053568 | 0.33371 | 0.089756 | 0.038014 | 122.9069 | 122.8114 | 122.9627 | 66.0109 | -123.0782 | 122.8078 | 122.9764 | 122.9247 | 66.0052 | -123.2739
556.2656 | 123.2346 | -66.2613 | 56.6345 | 0.04215 | -0.042651 | -0.0075097 | 0.052097 | -0.0084737 | 0.05701 | 0.073406 | -0.0015087 | 0.0011204 | 0.057836 | 0.042494 | 0.058255 | -66.262 | -0.24126 | -66.2516 | 56.6456 | 56.5638 | 56.706 | -66.4437 | -66.2346 | -0.24689 | -66.3149 | 56.5602 | 56.7197 | 56.6817 | -66.6394 | -0.18243 | 0.011059 | -0.000668 | 0.009741 | 0.19217 | -0.070707 | 0.0715 | -0.37812 | -0.074275 | 0.026723 | -0.053569 | 0.32456 | 0.085178 | 0.047172 | 122.9069 | 122.8251 | 122.9673 | 66.02 | -123.0782 | 122.8215 | 122.981 | 122.943 | 66.0144 | -123.2739
557.2656 | 123.2895 | -66.2842 | 56.6711 | 0.04215 | -0.044788 | -0.0064417 | 0.048892 | -0.0063367 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.057836 | 0.041425 | 0.057187 | -66.2574 | -0.24126 | -66.2378 | 56.6456 | 56.5776 | 56.706 | -66.4437 | -66.2346 | -0.25147 | -66.3149 | 56.5557 | 56.7151 | 56.6863 | -66.6394 | -0.15955 | -0.025563 | 0.026798 | 0.046364 | 0.20591 | -0.093592 | 0.034878 | -0.35524 | -0.11548 | 0.049611 | -0.030681 | 0.32456 | 0.043977 | 0.015128 | 122.9298 | 122.8617 | 122.9902 | 66.0429 | -123.1149 | 122.8398 | 122.9993 | 122.9705 | 66.0327 | -123.3106
558.2656 | 123.2437 | -66.2659 | 56.6208 | 0.057412 | -0.042651 | -0.0053737 | 0.052097 | -0.0084737 | 0.053805 | 0.058145 | -0.0047127 | 0.0021894 | 0.057836 | 0.044631 | 0.057187 | -66.2574 | -0.24126 | -66.247 | 56.6502 | 56.5363 | 56.7106 | -66.4437 | -66.23 | -0.25147 | -66.3011 | 56.5648 | 56.7197 | 56.6817 | -66.6348 | -0.17786 | 0.029369 | 0.008487 | 0.018897 | 0.19675 | -0.084449 | 0.089811 | -0.36897 | -0.055964 | 0.035879 | -0.035256 | 0.33371 | 0.09891 | 0.060904 | 122.916 | 122.8022 | 122.9765 | 66.0246 | -123.0645 | 122.8307 | 122.9856 | 122.9476 | 66.0144 | -123.2556
559.2656 | 123.1934 | -66.3025 | 56.6711 | 0.04215 | -0.043719 | -0.0075097 | 0.051029 | -0.0095417 | 0.055941 | 0.058145 | -0.0047127 | 0.0021894 | 0.056768 | 0.042494 | 0.058255 | -66.2482 | -0.255 | -66.2378 | 56.6502 | 56.5089 | 56.7152 | -66.4483 | -66.2346 | -0.25147 | -66.2965 | 56.5602 | 56.7197 | 56.6863 | -66.6303 | -0.14581 | -0.020985 | 0.054265 | 0.064674 | 0.21049 | -0.16228 | 0.044036 | -0.32777 | -0.1109 | 0.067921 | 0.005943 | 0.33371 | 0.048556 | 0.015128 | 122.9526 | 122.8114 | 123.0177 | 66.0475 | -123.1194 | 122.8627 | 123.0222 | 122.9888 | 66.051 | -123.3014
560.2656 | 123.2162 | -66.2476 | 56.6666 | 0.057412 | -0.043719 | -0.0064417 | 0.051029 | -0.0084737 | 0.055941 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.043562 | 0.057187 | -66.2574 | -0.255 | -66.2424 | 56.6547 | 56.5592 | 56.7106 | -66.4391 | -66.2254 | -0.24689 | -66.3057 | 56.5602 | 56.7197 | 56.6954 | -66.6394 | -0.19159 | -0.011828 | -0.009823 | 0.005165 | 0.19675 | -0.10733 | 0.044035 | -0.39186 | -0.10632 | 0.022147 | -0.058145 | 0.33371 | 0.053134 | 0.028863 | 122.9023 | 122.8068 | 122.9582 | 65.9926 | -123.1057 | 122.8078 | 122.9673 | 122.943 | 66.0007 | -123.306
561.2656 | 123.1659 | -66.2888 | 56.6711 | 0.026888 | -0.043719 | -0.0053737 | 0.053166 | -0.0074047 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.057836 | 0.044631 | 0.058255 | -66.2574 | -0.25042 | -66.2378 | 56.6502 | 56.5821 | 56.7106 | -66.4346 | -66.2254 | -0.24231 | -66.2965 | 56.5602 | 56.7243 | 56.6863 | -66.6303 | -0.14581 | -0.020985 | 0.031375 | 0.050941 | 0.19675 | -0.089013 | 0.039457 | -0.3415 | -0.1109 | 0.063345 | -0.00779 | 0.33371 | 0.053134 | 0.015128 | 122.9389 | 122.8709 | 122.9994 | 66.0383 | -123.1057 | 122.849 | 123.013 | 122.975 | 66.0464 | -123.3014
562.2656 | 123.262 | -66.2613 | 56.6528 | 0.011626 | -0.044788 | -0.0053737 | 0.052097 | -0.0095417 | 0.05701 | 0.042884 | -0.0047127 | 0.0011204 | 0.056768 | 0.041425 | 0.057187 | -66.2482 | -0.25042 | -66.2287 | 56.6547 | 56.5867 | 56.7106 | -66.4346 | -66.23 | -0.25147 | -66.292 | 56.5602 | 56.7289 | 56.6771 | -66.6257 | -0.17328 | 0.001905 | 0.013067 | 0.032633 | 0.20591 | -0.066124 | 0.057768 | -0.36439 | -0.092586 | 0.031302 | -0.030676 | 0.33371 | 0.076024 | 0.024282 | 122.916 | 122.848 | 122.9719 | 66.0109 | -123.0874 | 122.8215 | 122.9901 | 122.9384 | 66.0098 | -123.2785
563.2656 | 123.2346 | -66.243 | 56.6528 | 0.057412 | -0.042651 | -0.0053737 | 0.051029 | -0.0095417 | 0.05701 | 0.027623 | -0.0025767 | 0.0011204 | 0.057836 | 0.044631 | 0.057187 | -66.2482 | -0.25042 | -66.2332 | 56.6502 | 56.5867 | 56.7198 | -66.4391 | -66.2254 | -0.24689 | -66.3011 | 56.5602 | 56.7289 | 56.6817 | -66.6348 | -0.19617 | -0.002674 | -0.005244 | 0.009744 | 0.20591 | -0.066124 | 0.066925 | -0.39186 | -0.092586 | 0.017569 | -0.058144 | 0.33371 | 0.076024 | 0.028861 | 122.8931 | 122.8297 | 122.9627 | 65.9926 | -123.092 | 122.8032 | 122.9718 | 122.9247 | 65.9961 | -123.2877
564.2656 | 123.2574 | -66.275 | 56.6849 | 0.04215 | -0.041583 | -0.0053737 | 0.052097 | -0.0095417 | 0.054873 | 0.073406 | -0.0025767 | 0.0011204 | 0.0557 | 0.043562 | 0.056118 | -66.2482 | -0.255 | -66.2332 | 56.6593 | 56.5913 | 56.7198 | -66.4346 | -66.2208 | -0.25605 | -66.3011 | 56.5694 | 56.7289 | 56.6908 | -66.6303 | -0.15954 | -0.02556 | 0.026799 | 0.041787 | 0.20133 | -0.093588 | 0.034882 | -0.35523 | -0.11547 | 0.054191 | -0.026101 | 0.32913 | 0.043981 | 0.005975 | 122.9343 | 122.8663 | 122.9948 | 66.02 | -123.1194 | 122.8444 | 123.0039 | 122.9659 | 66.019 | -123.3151
565.2656 | 123.1888 | -66.3116 | 56.6254 | 0.04215 | -0.043719 | -0.0075097 | 0.04996 | -0.0084737 | 0.055941 | 0.027623 | -0.0025767 | 0.0011204 | 0.056768 | 0.043562 | 0.059323 | -66.2482 | -0.25957 | -66.2332 | 56.6639 | 56.5821 | 56.7289 | -66.4346 | -66.2254 | -0.25147 | -66.292 | 56.574 | 56.7334 | 56.6908 | -66.6303 | -0.12292 | 0.038528 | 0.063421 | 0.078409 | 0.20133 | -0.043236 | 0.10355 | -0.31861 | -0.051384 | 0.086234 | 0.019678 | 0.33829 | 0.10807 | 0.065484 | 122.9755 | 122.8938 | 123.0406 | 66.0521 | -123.0599 | 122.8856 | 123.0451 | 123.0025 | 66.0602 | -123.2556
566.2656 | 123.2758 | -66.2613 | 56.6391 | 0.026888 | -0.043719 | -0.0053737 | 0.053166 | -0.01061 | 0.055941 | 0.042884 | -0.0036447 | 0.0021894 | 0.057836 | 0.043562 | 0.059323 | -66.2482 | -0.255 | -66.2332 | 56.6547 | 56.573 | 56.7243 | -66.4254 | -66.2254 | -0.24689 | -66.3011 | 56.574 | 56.7334 | 56.6954 | -66.6257 | -0.16412 | 0.015638 | 0.013067 | 0.028055 | 0.19217 | -0.066127 | 0.085237 | -0.36439 | -0.065117 | 0.03588 | -0.039833 | 0.32456 | 0.094335 | 0.056329 | 122.916 | 122.8343 | 122.9856 | 66.0063 | -123.0645 | 122.8353 | 122.9947 | 122.9567 | 66.0144 | -123.2648
567.2656 | 123.23 | -66.2659 | 56.6711 | 0.04215 | -0.044788 | -0.0053737 | 0.052097 | -0.0084737 | 0.055941 | 0.073406 | -0.0036447 | 0.0011204 | 0.056768 | 0.043562 | 0.058255 | -66.2436 | -0.255 | -66.2332 | 56.6685 | 56.5134 | 56.7289 | -66.4346 | -66.2117 | -0.24689 | -66.292 | 56.574 | 56.7334 | 56.6863 | -66.6211 | -0.1687 | -0.002671 | 0.022223 | 0.032632 | 0.20133 | -0.1577 | 0.057771 | -0.35523 | -0.097161 | 0.054193 | -0.026099 | 0.32913 | 0.062291 | 0.015128 | 122.9343 | 122.7793 | 122.9948 | 66.0109 | -123.1057 | 122.8399 | 122.9993 | 122.9521 | 66.019 | -123.2922
568.2656 | 123.0927 | -66.3071 | 56.694 | 0.04215 | -0.043719 | -0.0064417 | 0.053166 | -0.0074047 | 0.05701 | 0.058145 | -0.0025767 | 0.0021894 | 0.057836 | 0.044631 | 0.058255 | -66.2345 | -0.24584 | -66.2149 | 56.6731 | 56.5226 | 56.7335 | -66.4391 | -66.2208 | -0.25147 | -66.2874 | 56.574 | 56.7243 | 56.7 | -66.6257 | -0.13208 | -0.020981 | 0.072578 | 0.092144 | 0.22422 | -0.17143 | 0.039462 | -0.31861 | -0.12005 | 0.086235 | 0.019679 | 0.33829 | 0.030246 | 0.005976 | 122.9801 | 122.8297 | 123.0406 | 66.0612 | -123.1332 | 122.8811 | 123.0313 | 123.0071 | 66.0556 | -123.3197
569.2656 | 123.2391 | -66.275 | 56.6711 | 0.026888 | -0.043719 | -0.0053737 | 0.051029 | -0.0095417 | 0.05701 | 0.058145 | -0.0025767 | 0.0011204 | 0.056768 | 0.044631 | 0.059323 | -66.2436 | -0.25042 | -66.2241 | 56.6731 | 56.5226 | 56.7289 | -66.43 | -66.2163 | -0.24689 | -66.3011 | 56.574 | 56.7426 | 56.7 | -66.6257 | -0.15497 | 0.001907 | 0.031378 | 0.050943 | 0.20591 | -0.14854 | 0.057771 | -0.35066 | -0.097161 | 0.05877 | -0.026101 | 0.32456 | 0.071449 | 0.028864 | 122.9481 | 122.7976 | 123.0039 | 66.0246 | -123.1011 | 122.849 | 123.0176 | 122.975 | 66.0281 | -123.2968
570.2656 | 123.2666 | -66.2613 | 56.662 | 0.04215 | -0.043719 | -0.0053737 | 0.051029 | -0.0084737 | 0.054873 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.057836 | 0.042494 | 0.058255 | -66.2391 | -0.25042 | -66.2241 | 56.6731 | 56.5318 | 56.7335 | -66.4346 | -66.2117 | -0.24689 | -66.2874 | 56.5786 | 56.7334 | 56.7046 | -66.6257 | -0.17328 | 0.011063 | 0.022224 | 0.037211 | 0.21049 | -0.13023 | 0.071506 | -0.36439 | -0.083427 | 0.049616 | -0.026097 | 0.33829 | 0.071447 | 0.042599 | 122.9343 | 122.7931 | 122.9948 | 66.0109 | -123.0966 | 122.8399 | 122.9947 | 122.9659 | 66.0144 | -123.2877
571.2656 | 123.2437 | -66.2659 | 56.6711 | 0.026888 | -0.043719 | -0.0075097 | 0.051029 | -0.0095417 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.056768 | 0.044631 | 0.057187 | -66.2391 | -0.25042 | -66.2149 | 56.6685 | 56.5318 | 56.7381 | -66.4391 | -66.2117 | -0.23773 | -66.292 | 56.574 | 56.738 | 56.7046 | -66.6257 | -0.17328 | -0.002671 | 0.026801 | 0.050945 | 0.22422 | -0.13938 | 0.066929 | -0.35981 | -0.097161 | 0.054193 | -0.026099 | 0.33371 | 0.06687 | 0.033443 | 122.9343 | 122.7976 | 123.0039 | 66.0155 | -123.1103 | 122.8399 | 123.0039 | 122.9705 | 66.0281 | -123.2968
572.2656 | 123.1247 | -66.3116 | 56.694 | 0.057412 | -0.043719 | -0.0064417 | 0.053166 | -0.0095417 | 0.059146 | 0.027623 | -0.0047127 | 0.0011204 | 0.056768 | 0.044631 | 0.059323 | -66.2345 | -0.24584 | -66.2241 | 56.6731 | 56.5272 | 56.7381 | -66.4346 | -66.2071 | -0.24231 | -66.2782 | 56.5831 | 56.738 | 56.7137 | -66.6211 | -0.12292 | -0.020981 | 0.077156 | 0.087565 | 0.21049 | -0.16685 | 0.044041 | -0.30946 | -0.11089 | 0.10455 | 0.033414 | 0.34287 | 0.043982 | 0.019712 | 122.9847 | 122.8388 | 123.0497 | 66.0658 | -123.1286 | 122.8948 | 123.0497 | 123.0254 | 66.0693 | -123.3151
573.2656 | 123.1201 | -66.2796 | 56.6986 | 0.04215 | -0.043719 | -0.0064417 | 0.051029 | -0.0074047 | 0.05701 | 0.073406 | -0.0025767 | 0.0011204 | 0.056768 | 0.045699 | 0.057187 | -66.2345 | -0.25042 | -66.2195 | 56.6731 | 56.5272 | 56.7426 | -66.4254 | -66.2163 | -0.24689 | -66.292 | 56.5786 | 56.7426 | 56.7137 | -66.6119 | -0.14581 | -0.025558 | 0.045112 | 0.060099 | 0.20591 | -0.17143 | 0.044042 | -0.33234 | -0.12005 | 0.063348 | -0.012366 | 0.31998 | 0.043984 | 0.015135 | 122.9527 | 122.8068 | 123.0223 | 66.0292 | -123.124 | 122.8582 | 123.0222 | 122.9933 | 66.0327 | -123.3106
574.2656 | 123.1888 | -66.2842 | 56.6162 | -0.0036356 | -0.045856 | -0.0053737 | 0.04996 | -0.0095417 | 0.05701 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.044631 | 0.057187 | -66.2299 | -0.25042 | -66.2195 | 56.6776 | 56.5363 | 56.7426 | -66.4254 | -66.2117 | -0.24231 | -66.2828 | 56.5831 | 56.7426 | 56.7137 | -66.6257 | -0.14123 | 0.061418 | 0.054269 | 0.064677 | 0.20591 | -0.079871 | 0.12644 | -0.3415 | -0.033072 | 0.072504 | 0.00137 | 0.34287 | 0.12638 | 0.097532 | 122.9618 | 122.8205 | 123.0268 | 66.0338 | -123.0416 | 122.8673 | 123.0268 | 122.9979 | 66.0419 | -123.2419
575.2656 | 123.1201 | -66.2979 | 56.7032 | 0.04215 | -0.043719 | -0.0075097 | 0.052097 | -0.0095417 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.057836 | 0.043562 | 0.057187 | -66.2299 | -0.24584 | -66.2058 | 56.6731 | 56.5318 | 56.7472 | -66.43 | -66.2071 | -0.24689 | -66.2828 | 56.5923 | 56.7426 | 56.7 | -66.6165 | -0.13208 | -0.030136 | 0.068002 | 0.092145 | 0.22422 | -0.17142 | 0.044043 | -0.31861 | -0.11089 | 0.090816 | 0.015103 | 0.33371 | 0.039406 | -0.003179 | 122.971 | 122.8297 | 123.0451 | 66.0521 | -123.1332 | 122.8902 | 123.0405 | 122.9979 | 66.051 | -123.3197
576.2656 | 123.0331 | -66.3162 | 56.7078 | 0.04215 | -0.043719 | -0.0075097 | 0.04996 | -0.0084737 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.043562 | 0.058255 | -66.2253 | -0.25042 | -66.2103 | 56.6822 | 56.5455 | 56.7426 | -66.4208 | -66.2117 | -0.24231 | -66.2874 | 56.5923 | 56.7472 | 56.7092 | -66.6165 | -0.10461 | -0.025557 | 0.09089 | 0.10588 | 0.21049 | -0.16227 | 0.034886 | -0.3003 | -0.11547 | 0.10455 | 0.028834 | 0.32913 | 0.039406 | 0.0014 | 122.9984 | 122.8617 | 123.0589 | 66.0658 | -123.1286 | 122.9085 | 123.0634 | 123.0254 | 66.0739 | -123.3243
577.2656 | 123.1338 | -66.275 | 56.694 | 0.04215 | -0.044788 | -0.0053737 | 0.051029 | -0.0084737 | 0.055941 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.056768 | 0.046767 | 0.058255 | -66.2253 | -0.24584 | -66.2195 | 56.6776 | 56.5363 | 56.7472 | -66.4254 | -66.2025 | -0.24689 | -66.2874 | 56.5877 | 56.7472 | 56.7137 | -66.6165 | -0.15039 | -0.016402 | 0.049691 | 0.055521 | 0.20591 | -0.15769 | 0.053198 | -0.3415 | -0.10631 | 0.072506 | -0.012365 | 0.32913 | 0.053139 | 0.019712 | 122.9527 | 122.8114 | 123.0223 | 66.0292 | -123.1194 | 122.8627 | 123.0222 | 122.9888 | 66.0281 | -123.3106
578.2656 | 123.1613 | -66.2796 | 56.6849 | 0.04215 | -0.044788 | -0.0064417 | 0.04996 | -0.0074047 | 0.058078 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.046767 | 0.057187 | -66.2253 | -0.24584 | -66.2149 | 56.6868 | 56.5363 | 56.7381 | -66.4254 | -66.2025 | -0.24231 | -66.2874 | 56.5877 | 56.7472 | 56.7137 | -66.6074 | -0.14581 | 0.001911 | 0.054269 | 0.064678 | 0.21049 | -0.14853 | 0.053197 | -0.32776 | -0.097158 | 0.077084 | -0.007787 | 0.31998 | 0.062295 | 0.028868 | 122.9664 | 122.8159 | 123.0177 | 66.0338 | -123.1103 | 122.8673 | 123.0268 | 122.9933 | 66.0373 | -123.2922
579.2656 | 123.143 | -66.2933 | 56.6895 | 0.026888 | -0.043719 | -0.0085787 | 0.051029 | -0.0084737 | 0.05701 | 0.042884 | -0.0025767 | 0.0011204 | 0.056768 | 0.043562 | 0.058255 | -66.2299 | -0.25042 | -66.2103 | 56.6868 | 56.5409 | 56.7472 | -66.4208 | -66.1979 | -0.24231 | -66.2782 | 56.5923 | 56.7517 | 56.7183 | -66.6074 | -0.1275 | -0.002667 | 0.063424 | 0.082989 | 0.21049 | -0.14853 | 0.057776 | -0.31403 | -0.097157 | 0.095396 | 0.015103 | 0.32913 | 0.062296 | 0.028868 | 122.9801 | 122.8343 | 123.0406 | 66.0429 | -123.1103 | 122.8856 | 123.0451 | 123.0117 | 66.051 | -123.2968
580.2656 | 123.1522 | -66.2888 | 56.7169 | 0.04215 | -0.044788 | -0.0043047 | 0.051029 | -0.01061 | 0.054873 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.056768 | 0.044631 | 0.059323 | -66.2208 | -0.24584 | -66.2103 | 56.6776 | 56.5409 | 56.7472 | -66.4254 | -66.1934 | -0.24231 | -66.2737 | 56.5923 | 56.7426 | 56.7275 | -66.6028 | -0.13665 | -0.03929 | 0.068003 | 0.078411 | 0.21506 | -0.176 | 0.03031 | -0.31403 | -0.12462 | 0.095396 | 0.015104 | 0.32913 | 0.025673 | 0.01056 | 122.9664 | 122.8297 | 123.036 | 66.0429 | -123.1423 | 122.8811 | 123.0313 | 123.0162 | 66.0464 | -123.3197
581.2656 | 123.1201 | -66.2704 | 56.7169 | 0.057412 | -0.044788 | -0.0085787 | 0.04996 | -0.01061 | 0.054873 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.054631 | 0.044631 | 0.058255 | -66.2253 | -0.24584 | -66.2103 | 56.6914 | 56.5455 | 56.7564 | -66.4163 | -66.2071 | -0.24231 | -66.2737 | 56.5923 | 56.7426 | 56.7183 | -66.6119 | -0.14581 | -0.025555 | 0.045114 | 0.060101 | 0.20591 | -0.17142 | 0.039467 | -0.3415 | -0.12462 | 0.06335 | -0.003206 | 0.33829 | 0.025673 | 0.001402 | 122.9618 | 122.8159 | 123.0268 | 66.0246 | -123.1332 | 122.8627 | 123.013 | 122.9888 | 66.0281 | -123.3289
582.2656 | 123.1934 | -66.275 | 56.7123 | 0.04215 | -0.044788 | -0.0064417 | 0.051029 | -0.0095417 | 0.054873 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.056768 | 0.045699 | 0.057187 | -66.2208 | -0.24126 | -66.2012 | 56.6868 | 56.5501 | 56.7472 | -66.4117 | -66.1979 | -0.25147 | -66.2691 | 56.5923 | 56.7472 | 56.7229 | -66.6119 | -0.13665 | -0.025555 | 0.05427 | 0.073835 | 0.21049 | -0.16226 | 0.034888 | -0.33692 | -0.12005 | 0.077085 | 0.00595 | 0.34287 | 0.034829 | 0.010559 | 122.9618 | 122.8251 | 123.0223 | 66.0338 | -123.124 | 122.8673 | 123.0222 | 122.9979 | 66.0236 | -123.3243
583.2656 | 123.2666 | -66.2933 | 56.6574 | 0.04215 | -0.044788 | -0.0064417 | 0.052097 | -0.011679 | 0.055941 | 0.073406 | -0.0025767 | -0.0010156 | 0.056768 | 0.045699 | 0.057187 | -66.2162 | -0.24126 | -66.2103 | 56.6914 | 56.5547 | 56.7518 | -66.4208 | -66.1979 | -0.25147 | -66.2737 | 56.5923 | 56.7517 | 56.7183 | -66.6074 | -0.1275 | 0.033954 | 0.077159 | 0.082989 | 0.21049 | -0.10275 | 0.094398 | -0.31403 | -0.065114 | 0.095396 | 0.019682 | 0.33371 | 0.094339 | 0.060911 | 122.9847 | 122.848 | 123.0451 | 66.0521 | -123.0782 | 122.8856 | 123.0451 | 123.0117 | 66.0419 | -123.2648
584.2656 | 123.1476 | -66.2384 | 56.7032 | 0.04215 | -0.043719 | -0.0075097 | 0.052097 | -0.01061 | 0.055941 | 0.073406 | -0.0047127 | 0.0021894 | 0.056768 | 0.044631 | 0.056118 | -66.2162 | -0.24126 | -66.2058 | 56.6868 | 56.6188 | 56.7472 | -66.4163 | -66.1934 | -0.25147 | -66.2691 | 56.5923 | 56.7517 | 56.7183 | -66.6165 | -0.17785 | -0.0164 | 0.022227 | 0.032635 | 0.21048 | -0.084425 | 0.044043 | -0.37812 | -0.11089 | 0.045042 | -0.030671 | 0.34745 | 0.048563 | 0.015135 | 122.9252 | 122.8572 | 122.9856 | 65.9971 | -123.1194 | 122.8307 | 122.9902 | 122.9567 | 65.9869 | -123.3197
585.2656 | 123.1842 | -66.2613 | 56.7307 | 0.057412 | -0.045856 | -0.0064417 | 0.051029 | -0.0084737 | 0.055941 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.044631 | 0.057187 | -66.2162 | -0.24584 | -66.2058 | 56.6914 | 56.6142 | 56.7564 | -66.4117 | -66.1934 | -0.23773 | -66.2645 | 56.5923 | 56.7563 | 56.7229 | -66.6028 | -0.15038 | -0.039288 | 0.045116 | 0.055524 | 0.20591 | -0.11647 | 0.025734 | -0.34149 | -0.13836 | 0.067931 | -0.003204 | 0.33829 | 0.025676 | -0.007752 | 122.9527 | 122.8755 | 123.0177 | 66.0155 | -123.1423 | 122.8536 | 123.0176 | 122.9842 | 66.0236 | -123.3334
586.2656 | 123.143 | -66.2933 | 56.7078 | 0.026888 | -0.045856 | -0.0053737 | 0.051029 | -0.01061 | 0.054873 | 0.042884 | -0.0025767 | -0.0010156 | 0.0557 | 0.046767 | 0.058255 | -66.2162 | -0.24126 | -66.2149 | 56.6868 | 56.6142 | 56.7472 | -66.3979 | -66.1888 | -0.24689 | -66.2645 | 56.606 | 56.7517 | 56.7229 | -66.6028 | -0.1046 | -0.020978 | 0.077159 | 0.078411 | 0.18301 | -0.093582 | 0.039465 | -0.30945 | -0.10173 | 0.10455 | 0.028839 | 0.33829 | 0.043985 | 0.015136 | 122.9801 | 122.9075 | 123.0406 | 66.0521 | -123.1057 | 122.8994 | 123.0451 | 123.0162 | 66.0464 | -123.3105
587.2656 | 123.111 | -66.2567 | 56.7307 | 0.04215 | -0.045856 | -0.0053737 | 0.051029 | -0.0095417 | 0.054873 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.044631 | 0.058255 | -66.2162 | -0.23668 | -66.2058 | 56.6959 | 56.6188 | 56.7564 | -66.4208 | -66.1888 | -0.23773 | -66.2645 | 56.5969 | 56.7609 | 56.7183 | -66.5982 | -0.16412 | -0.03471 | 0.040538 | 0.050946 | 0.21506 | -0.11189 | 0.025734 | -0.34149 | -0.13378 | 0.067932 | -0.007782 | 0.33371 | 0.030254 | -0.012331 | 122.9527 | 122.8755 | 123.0131 | 66.02 | -123.1515 | 122.8536 | 123.0176 | 122.975 | 66.019 | -123.3289
588.2656 | 123.1796 | -66.2659 | 56.7032 | 0.057412 | -0.045856 | -0.0075097 | 0.051029 | -0.011679 | 0.053805 | 0.058145 | -0.0057807 | 5.2373e-05 | 0.056768 | 0.046767 | 0.059323 | -66.2116 | -0.24126 | -66.2103 | 56.6868 | 56.6188 | 56.761 | -66.4071 | -66.1842 | -0.24231 | -66.2599 | 56.5969 | 56.7655 | 56.7275 | -66.5982 | -0.14123 | -0.0164 | 0.054271 | 0.055523 | 0.19675 | -0.084425 | 0.057779 | -0.33234 | -0.10631 | 0.081666 | 0.005952 | 0.33829 | 0.062299 | 0.024293 | 122.9527 | 122.8846 | 123.0268 | 66.0246 | -123.1103 | 122.8627 | 123.0314 | 122.9933 | 66.0236 | -123.3014
589.2656 | 123.1796 | -66.2567 | 56.7078 | 0.04215 | -0.045856 | -0.0064417 | 0.051029 | -0.011679 | 0.05701 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.056768 | 0.045699 | 0.057187 | -66.207 | -0.24126 | -66.2012 | 56.6914 | 56.6096 | 56.7564 | -66.4117 | -66.1796 | -0.24231 | -66.2599 | 56.6015 | 56.7655 | 56.7321 | -66.5936 | -0.15496 | -0.0164 | 0.049695 | 0.055525 | 0.21049 | -0.098161 | 0.048622 | -0.33692 | -0.10631 | 0.077089 | -0.003203 | 0.33371 | 0.057721 | 0.024293 | 122.9481 | 122.8663 | 123.0131 | 66.0155 | -123.1194 | 122.8582 | 123.0222 | 122.9888 | 66.0144 | -123.3014
590.2656 | 123.1659 | -66.2338 | 56.7398 | 0.057412 | -0.044788 | -0.0053737 | 0.051029 | -0.011679 | 0.054873 | 0.027623 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.044631 | 0.057187 | -66.207 | -0.23668 | -66.1966 | 56.7005 | 56.5592 | 56.7564 | -66.4117 | -66.1842 | -0.23773 | -66.2553 | 56.606 | 56.7655 | 56.7275 | -66.5936 | -0.17785 | -0.039286 | 0.026807 | 0.037215 | 0.21506 | -0.18057 | 0.016579 | -0.3598 | -0.13378 | 0.049623 | -0.021512 | 0.33829 | 0.025678 | -0.012328 | 122.9343 | 122.7931 | 122.9902 | 65.9971 | -123.1515 | 122.8399 | 122.9993 | 122.9613 | 65.9961 | -123.3334
591.2656 | 123.2071 | -66.2292 | 56.7261 | 0.057412 | -0.044788 | -0.0064417 | 0.051029 | -0.011679 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.054631 | 0.045699 | 0.057187 | -66.2024 | -0.23668 | -66.1966 | 56.7005 | 56.5592 | 56.7655 | -66.3934 | -66.1796 | -0.23773 | -66.2553 | 56.606 | 56.7746 | 56.7366 | -66.5936 | -0.16411 | -0.025553 | 0.026807 | 0.032637 | 0.19675 | -0.16684 | 0.039469 | -0.36438 | -0.12004 | 0.049623 | -0.02609 | 0.33829 | 0.048568 | 0.010562 | 122.9298 | 122.7885 | 122.9948 | 65.9926 | -123.1194 | 122.8353 | 123.0039 | 122.9659 | 65.9915 | -123.3197
592.2656 | 123.175 | -66.243 | 56.7078 | 0.026888 | -0.046924 | -0.0064417 | 0.052097 | -0.011679 | 0.055941 | 0.073406 | -0.0047127 | 0.0011204 | 0.0557 | 0.046767 | 0.058255 | -66.207 | -0.23668 | -66.1966 | 56.7051 | 56.573 | 56.7655 | -66.3979 | -66.175 | -0.23316 | -66.2553 | 56.6106 | 56.7655 | 56.7275 | -66.5936 | -0.15496 | -0.002665 | 0.035962 | 0.04637 | 0.20133 | -0.13479 | 0.057779 | -0.35065 | -0.097154 | 0.067935 | -0.012357 | 0.33829 | 0.057721 | 0.019715 | 122.9481 | 122.816 | 123.0085 | 66.0063 | -123.1057 | 122.8536 | 123.0085 | 122.9705 | 66.0098 | -123.3014
593.2656 | 123.1567 | -66.243 | 56.7398 | 0.04215 | -0.045856 | -0.0064417 | 0.052097 | -0.0074047 | 0.053805 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.0557 | 0.045699 | 0.057187 | -66.2024 | -0.2321 | -66.1966 | 56.7051 | 56.5959 | 56.761 | -66.4071 | -66.175 | -0.23773 | -66.2599 | 56.6198 | 56.7609 | 56.7275 | -66.5891 | -0.16411 | -0.034708 | 0.04054 | 0.04637 | 0.21048 | -0.14394 | 0.021158 | -0.34607 | -0.12004 | 0.067935 | -0.016936 | 0.32913 | 0.021099 | -0.012328 | 122.9481 | 122.8388 | 123.0039 | 66.0109 | -123.1469 | 122.8627 | 123.0039 | 122.9705 | 66.0052 | -123.3289
594.2656 | 123.1705 | -66.2521 | 56.7444 | 0.026888 | -0.045856 | -0.0064417 | 0.051029 | -0.0095417 | 0.055941 | 0.088667 | -0.0036447 | 0.0011204 | 0.056768 | 0.047836 | 0.058255 | -66.2024 | -0.2321 | -66.1875 | 56.7097 | 56.5684 | 56.7655 | -66.3979 | -66.175 | -0.23773 | -66.2508 | 56.606 | 56.7701 | 56.7366 | -66.5936 | -0.1458 | -0.034708 | 0.049695 | 0.064681 | 0.21048 | -0.17599 | 0.021158 | -0.34149 | -0.13835 | 0.07709 | 0.001377 | 0.34287 | 0.025678 | -0.007749 | 122.9618 | 122.8205 | 123.0177 | 66.02 | -123.1423 | 122.8582 | 123.0222 | 122.9888 | 66.0144 | -123.338
595.2656 | 123.1613 | -66.2567 | 56.7398 | 0.04215 | -0.045856 | -0.0053737 | 0.052097 | -0.01061 | 0.055941 | 0.058145 | -0.0036447 | -0.0010156 | 0.0557 | 0.045699 | 0.058255 | -66.1979 | -0.22752 | -66.1966 | 56.7097 | 56.5638 | 56.7747 | -66.4025 | -66.175 | -0.23773 | -66.2508 | 56.6152 | 56.7655 | 56.7366 | -66.5891 | -0.1458 | -0.03013 | 0.058851 | 0.060103 | 0.20591 | -0.17599 | 0.034894 | -0.33234 | -0.12462 | 0.081668 | 0.005955 | 0.33829 | 0.025678 | -0.003171 | 122.9664 | 122.8205 | 123.0314 | 66.0292 | -123.1423 | 122.8719 | 123.0222 | 122.9933 | 66.019 | -123.3289
596.2656 | 123.143 | -66.2338 | 56.7764 | 0.057412 | -0.045856 | -0.0053737 | 0.051029 | -0.0084737 | 0.055941 | 0.042884 | -0.00043967 | -0.0010156 | 0.0557 | 0.046767 | 0.057187 | -66.1979 | -0.24126 | -66.192 | 56.7097 | 56.605 | 56.7655 | -66.4025 | -66.1613 | -0.23773 | -66.2553 | 56.6015 | 56.7746 | 56.7458 | -66.5845 | -0.16869 | -0.066751 | 0.035963 | 0.041793 | 0.21048 | -0.1714 | -0.010885 | -0.35065 | -0.17498 | 0.072516 | -0.021512 | 0.32913 | -0.001786 | -0.030635 | 122.9435 | 122.8388 | 122.9994 | 65.9926 | -123.1789 | 122.8353 | 123.0085 | 122.9796 | 65.9961 | -123.3609
597.2656 | 123.1796 | -66.2064 | 56.749 | 0.04215 | -0.045856 | -0.0053737 | 0.051029 | -0.011679 | 0.055941 | 0.073406 | -0.0036447 | 0.0021894 | 0.0557 | 0.045699 | 0.059323 | -66.2024 | -0.2321 | -66.1875 | 56.7051 | 56.6096 | 56.7747 | -66.3934 | -66.175 | -0.23773 | -66.2599 | 56.6106 | 56.7792 | 56.7366 | -66.5891 | -0.187 | -0.043863 | 0.003919 | 0.018905 | 0.2059 | -0.13936 | 0.025739 | -0.38269 | -0.13835 | 0.031314 | -0.053557 | 0.32913 | 0.030259 | -0.012326 | 122.9115 | 122.816 | 122.9811 | 65.9743 | -123.1423 | 122.817 | 122.9856 | 122.943 | 65.9686 | -123.338
598.2656 | 123.2437 | -66.2201 | 56.749 | 0.072674 | -0.045856 | -0.0075097 | 0.04996 | -0.0095417 | 0.054873 | 0.088667 | -0.0047127 | 5.2373e-05 | 0.056768 | 0.045699 | 0.058255 | -66.1979 | -0.2321 | -66.1875 | 56.7097 | 56.6325 | 56.7747 | -66.3934 | -66.1659 | -0.23773 | -66.2462 | 56.6106 | 56.7701 | 56.7321 | -66.5845 | -0.17327 | -0.039285 | 0.02223 | 0.032638 | 0.2059 | -0.11646 | 0.025739 | -0.36438 | -0.13835 | 0.054205 | -0.026088 | 0.33829 | 0.021101 | -0.016905 | 122.9298 | 122.8526 | 122.9948 | 65.988 | -123.1423 | 122.8307 | 122.9902 | 122.9522 | 65.9824 | -123.3334
599.2656 | 123.1659 | -66.2247 | 56.7535 | 0.026888 | -0.045856 | -0.0064417 | 0.051029 | -0.01061 | 0.054873 | 0.058145 | -0.0047127 | 0.0021894 | 0.0557 | 0.046767 | 0.058255 | -66.1979 | -0.22752 | -66.1875 | 56.7143 | 56.6371 | 56.7701 | -66.3842 | -66.1613 | -0.23316 | -66.2462 | 56.6243 | 56.7792 | 56.7366 | -66.5891 | -0.15953 | -0.039284 | 0.026807 | 0.037215 | 0.19675 | -0.11646 | 0.016582 | -0.36438 | -0.1292 | 0.06336 | -0.021511 | 0.34287 | 0.025681 | -0.016904 | 122.9389 | 122.8617 | 122.9948 | 65.9971 | -123.1377 | 122.849 | 123.0039 | 122.9613 | 65.9915 | -123.3426
600.2656 | 123.1613 | -66.2338 | 56.7398 | 0.072674 | -0.047993 | -0.0064417 | 0.04996 | -0.01061 | 0.054873 | 0.073406 | -0.0036447 | 0.0021894 | 0.056768 | 0.046767 | 0.057187 | -66.1933 | -0.21837 | -66.1783 | 56.7097 | 56.6325 | 56.7701 | -66.3934 | -66.1613 | -0.23316 | -66.2508 | 56.6198 | 56.7746 | 56.7412 | -66.5799 | -0.15953 | -0.03013 | 0.040542 | 0.055528 | 0.21506 | -0.10731 | 0.030315 | -0.34607 | -0.12004 | 0.072516 | -0.016933 | 0.32913 | 0.034835 | 0.001407 | 122.9435 | 122.8663 | 123.0039 | 66.0155 | -123.1332 | 122.8536 | 123.0085 | 122.975 | 66.0007 | -123.3197
601.2656 | 123.1796 | -66.2384 | 56.7352 | 0.026888 | -0.045856 | -0.0043047 | 0.051029 | -0.01061 | 0.055941 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.054631 | 0.047836 | 0.058255 | -66.1933 | -0.22295 | -66.1829 | 56.7143 | 56.6371 | 56.7793 | -66.3934 | -66.1613 | -0.23316 | -66.2416 | 56.6198 | 56.7792 | 56.7412 | -66.5845 | -0.15496 | -0.020973 | 0.045119 | 0.055527 | 0.21048 | -0.098152 | 0.04405 | -0.34607 | -0.11546 | 0.077093 | -0.003199 | 0.34287 | 0.043992 | 0.005985 | 122.9527 | 122.8755 | 123.0177 | 66.0155 | -123.1286 | 122.8582 | 123.0176 | 122.9796 | 66.0052 | -123.3197
602.2656 | 123.1384 | -66.2567 | 56.7398 | 0.072674 | -0.046924 | -0.0075097 | 0.04996 | -0.01061 | 0.054873 | 0.058145 | -0.0036447 | -0.0010156 | 0.056768 | 0.045699 | 0.058255 | -66.1841 | -0.22752 | -66.1875 | 56.7143 | 56.6279 | 56.7747 | -66.3979 | -66.1567 | -0.23316 | -66.2416 | 56.6198 | 56.7792 | 56.7458 | -66.5753 | -0.14122 | -0.025551 | 0.072587 | 0.069259 | 0.21048 | -0.11189 | 0.034894 | -0.3186 | -0.12004 | 0.099983 | 0.015112 | 0.33371 | 0.039414 | 0.005986 | 122.971 | 122.8846 | 123.0314 | 66.0292 | -123.1377 | 122.8765 | 123.0359 | 123.0025 | 66.0236 | -123.3151
603.2656 | 123.175 | -66.2521 | 56.7215 | 0.04215 | -0.046924 | -0.0053737 | 0.051029 | -0.0095417 | 0.054873 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.054631 | 0.046767 | 0.059323 | -66.1887 | -0.22295 | -66.1966 | 56.7234 | 56.6462 | 56.7747 | -66.3842 | -66.1567 | -0.22858 | -66.237 | 56.6198 | 56.7838 | 56.7412 | -66.5799 | -0.13206 | 0.001916 | 0.06343 | 0.055525 | 0.18759 | -0.075263 | 0.053204 | -0.32776 | -0.10173 | 0.095405 | 0.015113 | 0.34287 | 0.062302 | 0.019717 | 122.9755 | 122.8984 | 123.0268 | 66.0292 | -123.1057 | 122.8719 | 123.0359 | 122.9933 | 66.0236 | -123.3014
604.2656 | 123.1201 | -66.2109 | 56.7673 | 0.026888 | -0.046924 | -0.0075097 | 0.051029 | -0.0095417 | 0.054873 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.057836 | 0.046767 | 0.058255 | -66.1841 | -0.22295 | -66.192 | 56.7097 | 56.6417 | 56.7793 | -66.3796 | -66.1522 | -0.23773 | -66.2416 | 56.6198 | 56.7792 | 56.7458 | -66.5753 | -0.16868 | -0.057596 | 0.02681 | 0.018904 | 0.18759 | -0.12562 | 0.012006 | -0.36438 | -0.14751 | 0.058785 | -0.030665 | 0.33371 | 0.011948 | -0.02148 | 122.9206 | 122.8526 | 122.9902 | 65.988 | -123.1469 | 122.8307 | 122.9902 | 122.9567 | 65.9732 | -123.3426
605.2656 | 123.1705 | -66.2064 | 56.7535 | 0.072674 | -0.049061 | -0.0064417 | 0.051029 | -0.0095417 | 0.055941 | 0.058145 | -0.0025767 | 0.0021894 | 0.056768 | 0.046767 | 0.059323 | -66.1841 | -0.22752 | -66.1783 | 56.7097 | 56.6371 | 56.7747 | -66.3934 | -66.1567 | -0.23773 | -66.2416 | 56.6198 | 56.7746 | 56.7412 | -66.5799 | -0.187 | -0.043863 | 0.022233 | 0.028062 | 0.21506 | -0.11646 | 0.021161 | -0.37353 | -0.13377 | 0.049629 | -0.035242 | 0.33829 | 0.021102 | -0.012326 | 122.916 | 122.8434 | 122.9811 | 65.9788 | -123.1469 | 122.8261 | 122.981 | 122.9476 | 65.9686 | -123.3334
606.2656 | 123.2025 | -66.2384 | 56.7215 | 0.04215 | -0.046924 | -0.0053737 | 0.052097 | -0.0095417 | 0.053805 | 0.058145 | -0.0025767 | 0.0021894 | 0.056768 | 0.045699 | 0.057187 | -66.1887 | -0.22752 | -66.1829 | 56.7097 | 56.6004 | 56.7793 | -66.3888 | -66.1613 | -0.23316 | -66.237 | 56.6198 | 56.7746 | 56.755 | -66.5753 | -0.15038 | -0.01182 | 0.049697 | 0.055527 | 0.2059 | -0.12105 | 0.057782 | -0.33691 | -0.10173 | 0.077093 | 0.00138 | 0.33829 | 0.053145 | 0.033453 | 122.9481 | 122.8388 | 123.0177 | 66.0109 | -123.1103 | 122.8582 | 123.013 | 122.9934 | 66.0052 | -123.2968
607.2656 | 123.1796 | -66.2155 | 56.749 | 0.04215 | -0.046924 | -0.0043047 | 0.053166 | -0.0095417 | 0.055941 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.056768 | 0.047836 | 0.056118 | -66.1887 | -0.21837 | -66.1783 | 56.7143 | 56.6004 | 56.7793 | -66.3842 | -66.1476 | -0.22858 | -66.237 | 56.6243 | 56.7746 | 56.7458 | -66.5753 | -0.16869 | -0.034706 | 0.026809 | 0.037217 | 0.2059 | -0.14852 | 0.030317 | -0.3598 | -0.12462 | 0.067941 | -0.021508 | 0.33829 | 0.02568 | -0.003169 | 122.9298 | 122.816 | 122.9948 | 65.9971 | -123.1332 | 122.8399 | 122.9902 | 122.9613 | 65.9869 | -123.3243
608.2656 | 123.1934 | -66.2201 | 56.749 | 0.04215 | -0.045856 | -0.0064417 | 0.04996 | -0.0095417 | 0.058078 | 0.088667 | -0.0047127 | 0.0011204 | 0.057836 | 0.049972 | 0.059323 | -66.1887 | -0.22295 | -66.1783 | 56.7143 | 56.5959 | 56.7793 | -66.3842 | -66.1567 | -0.23316 | -66.2324 | 56.6198 | 56.7792 | 56.7458 | -66.5707 | -0.16411 | -0.034706 | 0.031387 | 0.041795 | 0.2059 | -0.1531 | 0.030317 | -0.35064 | -0.12919 | 0.063362 | -0.012352 | 0.33829 | 0.030259 | -0.003169 | 122.9343 | 122.816 | 122.9994 | 65.9971 | -123.1332 | 122.8399 | 122.9993 | 122.9659 | 65.9869 | -123.3197
609.2656 | 123.1201 | -66.2338 | 56.7535 | 0.026888 | -0.045856 | -0.0075097 | 0.04996 | -0.01061 | 0.054873 | 0.058145 | -0.0036447 | 0.0021894 | 0.0557 | 0.047836 | 0.058255 | -66.1841 | -0.21379 | -66.1783 | 56.7143 | 56.6188 | 56.7793 | -66.3842 | -66.1522 | -0.22858 | -66.237 | 56.6289 | 56.7838 | 56.755 | -66.5845 | -0.15037 | -0.039284 | 0.049699 | 0.055528 | 0.2059 | -0.13478 | 0.025739 | -0.35065 | -0.12462 | 0.081674 | -0.003197 | 0.34745 | 0.030259 | 0.00141 | 122.9481 | 122.8526 | 123.0131 | 66.02 | -123.1377 | 122.8627 | 123.0176 | 122.9888 | 66.0052 | -123.338
610.2656 | 123.1522 | -66.2201 | 56.7856 | 0.057412 | -0.047993 | -0.0053737 | 0.052097 | -0.01061 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.047836 | 0.057187 | -66.1841 | -0.22295 | -66.1829 | 56.7188 | 56.6142 | 56.7884 | -66.3842 | -66.1476 | -0.23773 | -66.237 | 56.6243 | 56.793 | 56.7595 | -66.5753 | -0.16411 | -0.066749 | 0.035966 | 0.037217 | 0.20132 | -0.1714 | 0.002853 | -0.35522 | -0.16124 | 0.072519 | -0.01693 | 0.33829 | 0.007373 | -0.026054 | 122.9389 | 122.8343 | 123.0085 | 65.9971 | -123.1698 | 122.8444 | 123.013 | 122.9796 | 65.9824 | -123.3609
611.2656 | 123.143 | -66.2201 | 56.7307 | 0.072674 | -0.046924 | -0.0075097 | 0.051029 | -0.0095417 | 0.053805 | 0.058145 | -0.0036447 | 0.0021894 | 0.056768 | 0.047836 | 0.057187 | -66.1887 | -0.22752 | -66.1783 | 56.7143 | 56.6371 | 56.7839 | -66.3796 | -66.1476 | -0.22858 | -66.237 | 56.6243 | 56.7838 | 56.7458 | -66.5799 | -0.15953 | -0.016396 | 0.031387 | 0.041795 | 0.20132 | -0.093575 | 0.053206 | -0.3598 | -0.10631 | 0.072519 | -0.01693 | 0.34287 | 0.053147 | 0.015141 | 122.9343 | 122.8572 | 123.004 | 65.9926 | -123.1103 | 122.8444 | 123.0039 | 122.9659 | 65.9915 | -123.3105
612.2656 | 123.1934 | -66.243 | 56.7535 | 0.04215 | -0.046924 | -0.0064417 | 0.04996 | -0.011679 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.0557 | 0.049972 | 0.057187 | -66.1841 | -0.22295 | -66.1783 | 56.7188 | 56.5959 | 56.7793 | -66.3842 | -66.1476 | -0.224 | -66.237 | 56.6289 | 56.7884 | 56.7595 | -66.5753 | -0.14122 | -0.034706 | 0.058854 | 0.064683 | 0.2059 | -0.15767 | 0.025739 | -0.33233 | -0.12462 | 0.095407 | 0.005958 | 0.33829 | 0.034838 | 0.005989 | 122.9618 | 122.8388 | 123.0223 | 66.02 | -123.1377 | 122.8719 | 123.0314 | 123.0025 | 66.019 | -123.3289
613.2656 | 123.1567 | -66.2247 | 56.7169 | 0.057412 | -0.047993 | -0.0075097 | 0.051029 | -0.0095417 | 0.05701 | 0.073406 | -0.0036447 | 0.0011204 | 0.056768 | 0.046767 | 0.058255 | -66.1841 | -0.21837 | -66.1783 | 56.7234 | 56.5867 | 56.7884 | -66.3934 | -66.143 | -0.224 | -66.237 | 56.6243 | 56.7792 | 56.755 | -66.5753 | -0.16869 | 0.006494 | 0.040543 | 0.046372 | 0.21506 | -0.13021 | 0.071517 | -0.35064 | -0.092574 | 0.081675 | -0.012353 | 0.33829 | 0.062302 | 0.038031 | 122.9481 | 122.8114 | 123.0131 | 66.0063 | -123.1103 | 122.849 | 123.0039 | 122.9796 | 66.0007 | -123.2922
614.2656 | 123.1659 | -66.1743 | 56.7627 | 0.057412 | -0.047993 | -0.0064417 | 0.051029 | -0.012747 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.057836 | 0.047836 | 0.056118 | -66.1841 | -0.21837 | -66.1783 | 56.7188 | 56.5821 | 56.7793 | -66.3888 | -66.1476 | -0.224 | -66.237 | 56.6243 | 56.7884 | 56.755 | -66.5753 | -0.21446 | -0.043861 | -0.009811 | -0.003982 | 0.21048 | -0.18057 | 0.016584 | -0.401 | -0.13835 | 0.026742 | -0.062707 | 0.33829 | 0.025683 | -0.007745 | 122.8932 | 122.7564 | 122.9536 | 65.956 | -123.1515 | 122.7987 | 122.9627 | 122.9293 | 65.9503 | -123.338
615.2656 | 123.1842 | -66.1972 | 56.7398 | 0.026888 | -0.047993 | -0.0053737 | 0.051029 | -0.0095417 | 0.055941 | 0.073406 | -0.0025767 | -0.0010156 | 0.057836 | 0.046767 | 0.058255 | -66.1841 | -0.22295 | -66.1737 | 56.7143 | 56.5913 | 56.7793 | -66.3842 | -66.1476 | -0.22858 | -66.237 | 56.6289 | 56.7792 | 56.755 | -66.5799 | -0.187 | -0.025551 | 0.013078 | 0.023485 | 0.21048 | -0.14852 | 0.039472 | -0.38269 | -0.11088 | 0.049631 | -0.039818 | 0.34287 | 0.039414 | 0.015143 | 122.9115 | 122.7885 | 122.9765 | 65.9743 | -123.124 | 122.8261 | 122.9764 | 122.9522 | 65.9686 | -123.3197
616.2656 | 123.1522 | -66.2064 | 56.7673 | 0.057412 | -0.044788 | -0.0053737 | 0.052097 | -0.01061 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.0557 | 0.047836 | 0.057187 | -66.1841 | -0.21379 | -66.1829 | 56.7188 | 56.5821 | 56.7839 | -66.3842 | -66.143 | -0.224 | -66.237 | 56.6243 | 56.7792 | 56.7504 | -66.5799 | -0.17784 | -0.048439 | 0.022233 | 0.023484 | 0.20132 | -0.18514 | 0.016585 | -0.37353 | -0.14293 | 0.063365 | -0.030663 | 0.34287 | 0.011948 | -0.016901 | 122.9252 | 122.7885 | 122.9902 | 65.9926 | -123.1515 | 122.8307 | 122.9856 | 122.9567 | 65.9824 | -123.3472
617.2656 | 123.1247 | -66.2155 | 56.7581 | 0.057412 | -0.046924 | -0.0064417 | 0.051029 | -0.0095417 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.045699 | 0.057187 | -66.1841 | -0.21837 | -66.1783 | 56.7097 | 56.5821 | 56.7839 | -66.3888 | -66.143 | -0.23316 | -66.237 | 56.6243 | 56.7792 | 56.7504 | -66.5799 | -0.17326 | -0.048441 | 0.031388 | 0.037217 | 0.21048 | -0.17599 | 0.02574 | -0.36438 | -0.13377 | 0.07252 | -0.021508 | 0.34287 | 0.021103 | -0.007746 | 122.9252 | 122.7976 | 122.9994 | 65.9971 | -123.1469 | 122.8399 | 122.9947 | 122.9659 | 65.9824 | -123.338
618.2656 | 123.1842 | -66.2338 | 56.7627 | 0.057412 | -0.049061 | -0.0064417 | 0.052097 | -0.01061 | 0.055941 | 0.058145 | -0.0047127 | 0.0021894 | 0.056768 | 0.048904 | 0.058255 | -66.1795 | -0.21379 | -66.1829 | 56.7188 | 56.5776 | 56.7839 | -66.3842 | -66.143 | -0.224 | -66.2324 | 56.6198 | 56.7838 | 56.7504 | -66.5753 | -0.15037 | -0.043861 | 0.054277 | 0.05095 | 0.20132 | -0.18514 | 0.021163 | -0.34149 | -0.14293 | 0.090831 | 0.001381 | 0.34287 | 0.021104 | -0.012323 | 122.9527 | 122.8114 | 123.0177 | 66.02 | -123.1469 | 122.8536 | 123.0176 | 122.9842 | 66.0098 | -123.338
619.2656 | 123.175 | -66.2476 | 56.7581 | 0.026888 | -0.047993 | -0.0064417 | 0.051029 | -0.0095417 | 0.05701 | 0.073406 | -0.0025767 | 0.0011204 | 0.057836 | 0.047836 | 0.057187 | -66.1841 | -0.22752 | -66.1829 | 56.7188 | 56.5821 | 56.7839 | -66.3888 | -66.143 | -0.21484 | -66.2416 | 56.6243 | 56.7884 | 56.755 | -66.5845 | -0.14122 | -0.039284 | 0.063432 | 0.064683 | 0.2059 | -0.17599 | 0.02574 | -0.33691 | -0.13377 | 0.10456 | 0.005957 | 0.34287 | 0.03026 | -0.003168 | 122.9664 | 122.8297 | 123.0314 | 66.02 | -123.1469 | 122.8719 | 123.0359 | 123.0025 | 66.0327 | -123.3426
620.2656 | 123.2025 | -66.2521 | 56.7581 | 0.011626 | -0.049061 | -0.0053737 | 0.04996 | -0.0095417 | 0.054873 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.051041 | 0.057187 | -66.1887 | -0.21379 | -66.1783 | 56.7188 | 56.605 | 56.7839 | -66.3934 | -66.1476 | -0.22858 | -66.2462 | 56.6243 | 56.7701 | 56.755 | -66.5753 | -0.14122 | -0.039284 | 0.06343 | 0.073838 | 0.21506 | -0.15309 | 0.02574 | -0.32318 | -0.13377 | 0.10456 | 0.005955 | 0.32913 | 0.011945 | -0.003168 | 122.971 | 122.8572 | 123.036 | 66.0383 | -123.1515 | 122.8765 | 123.0222 | 123.0071 | 66.0236 | -123.3334
621.2656 | 123.1293 | -66.2247 | 56.749 | 0.011626 | -0.045856 | -0.0075097 | 0.048892 | -0.01061 | 0.054873 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.0557 | 0.049972 | 0.058255 | -66.1841 | -0.21837 | -66.1783 | 56.7188 | 56.6233 | 56.7839 | -66.4025 | -66.143 | -0.22858 | -66.2462 | 56.6289 | 56.7792 | 56.7595 | -66.5845 | -0.17785 | -0.030128 | 0.040543 | 0.046372 | 0.22422 | -0.12562 | 0.034896 | -0.3598 | -0.12004 | 0.081675 | -0.021511 | 0.33829 | 0.030259 | 0.010567 | 122.9435 | 122.848 | 123.0085 | 66.0063 | -123.1515 | 122.8536 | 123.0039 | 122.9842 | 65.9961 | -123.3334
622.2656 | 123.0652 | -66.2384 | 56.7764 | 0.04215 | -0.047993 | -0.0075097 | 0.052097 | -0.013815 | 0.05701 | 0.058145 | -0.0047127 | 0.0011204 | 0.056768 | 0.047836 | 0.058255 | -66.1887 | -0.22295 | -66.1829 | 56.7188 | 56.6325 | 56.7884 | -66.3979 | -66.143 | -0.21942 | -66.2462 | 56.6243 | 56.7746 | 56.755 | -66.5891 | -0.15953 | -0.057594 | 0.049697 | 0.055527 | 0.21506 | -0.14393 | 0.012008 | -0.35065 | -0.15208 | 0.095408 | -0.007778 | 0.34287 | -0.001786 | -0.021478 | 122.9572 | 122.8709 | 123.0268 | 66.0155 | -123.1744 | 122.8627 | 123.013 | 122.9934 | 66.019 | -123.3655
623.2656 | 123.111 | -66.2247 | 56.7627 | 0.057412 | -0.046924 | -0.0064417 | 0.051029 | -0.01061 | 0.053805 | 0.10393 | -0.0047127 | 5.2373e-05 | 0.056768 | 0.047836 | 0.056118 | -66.1841 | -0.21837 | -66.1829 | 56.7143 | 56.6188 | 56.7839 | -66.4025 | -66.1476 | -0.224 | -66.2416 | 56.6198 | 56.7701 | 56.7595 | -66.5845 | -0.17785 | -0.048439 | 0.040543 | 0.041794 | 0.21964 | -0.14393 | 0.021163 | -0.3598 | -0.14293 | 0.077096 | -0.016932 | 0.34287 | 0.007368 | -0.003166 | 122.9389 | 122.8434 | 123.0085 | 66.0063 | -123.1652 | 122.8444 | 122.9947 | 122.9842 | 66.0007 | -123.3472
624.2656 | 123.1293 | -66.2384 | 56.7856 | 0.057412 | -0.049061 | -0.0085787 | 0.04996 | -0.01061 | 0.054873 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.0557 | 0.048904 | 0.058255 | -66.1841 | -0.21837 | -66.1829 | 56.7143 | 56.5821 | 56.7839 | -66.3979 | -66.1384 | -0.21484 | -66.2462 | 56.6198 | 56.7746 | 56.7504 | -66.5753 | -0.15953 | -0.071327 | 0.054276 | 0.055527 | 0.21506 | -0.20345 | -0.001725 | -0.33691 | -0.16582 | 0.099987 | -0.007778 | 0.32913 | -0.010941 | -0.035211 | 122.9527 | 122.8205 | 123.0223 | 66.02 | -123.1835 | 122.8582 | 123.013 | 122.9888 | 66.0236 | -123.3609
625.2656 | 123.1567 | -66.2201 | 56.7444 | 0.072674 | -0.047993 | -0.0075097 | 0.04996 | -0.01061 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.047836 | 0.057187 | -66.1841 | -0.22295 | -66.1875 | 56.7143 | 56.573 | 56.7839 | -66.4071 | -66.1476 | -0.21484 | -66.2416 | 56.6198 | 56.7701 | 56.7458 | -66.5891 | -0.187 | -0.030129 | 0.035966 | 0.032638 | 0.21964 | -0.17141 | 0.039473 | -0.36896 | -0.12462 | 0.072519 | -0.021509 | 0.34745 | 0.025678 | 0.001408 | 122.9343 | 122.7931 | 123.004 | 65.9971 | -123.1515 | 122.8399 | 122.9902 | 122.9659 | 66.0053 | -123.3334
626.2656 | 123.1247 | -66.2338 | 56.7627 | 0.04215 | -0.046924 | -0.0075097 | 0.048892 | -0.01061 | 0.054873 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.054631 | 0.047836 | 0.059323 | -66.1841 | -0.20921 | -66.1875 | 56.7097 | 56.5638 | 56.7839 | -66.4025 | -66.143 | -0.21484 | -66.2462 | 56.6198 | 56.7746 | 56.7458 | -66.5891 | -0.16869 | -0.053018 | 0.049699 | 0.046371 | 0.21506 | -0.19888 | 0.021163 | -0.35522 | -0.14293 | 0.090831 | -0.012355 | 0.34287 | 0.011947 | -0.016902 | 122.9435 | 122.7976 | 123.0177 | 66.0246 | -123.1652 | 122.8536 | 123.0085 | 122.9796 | 66.019 | -123.3517
627.2656 | 123.1659 | -66.2292 | 56.7444 | 0.057412 | -0.046924 | -0.0064417 | 0.052097 | -0.01061 | 0.055941 | 0.042884 | -0.0036447 | 0.0011204 | 0.056768 | 0.048904 | 0.057187 | -66.1887 | -0.22295 | -66.1783 | 56.7051 | 56.6188 | 56.7701 | -66.3888 | -66.143 | -0.20568 | -66.2416 | 56.6243 | 56.7746 | 56.7412 | -66.5936 | -0.15953 | -0.039286 | 0.040542 | 0.05095 | 0.21048 | -0.12562 | 0.025737 | -0.36438 | -0.12004 | 0.086253 | -0.012354 | 0.35203 | 0.030257 | -0.003171 | 122.9343 | 122.848 | 122.9994 | 66.0063 | -123.1332 | 122.8536 | 123.0039 | 122.9705 | 66.0236 | -123.338
628.2656 | 123.1522 | -66.2384 | 56.7307 | 0.04215 | -0.047993 | -0.0064417 | 0.051029 | -0.01061 | 0.05701 | 0.042884 | -0.0047127 | 0.0021894 | 0.0557 | 0.047836 | 0.058255 | -66.1933 | -0.22295 | -66.192 | 56.7051 | 56.6279 | 56.7747 | -66.3934 | -66.1476 | -0.21484 | -66.2508 | 56.606 | 56.7701 | 56.7412 | -66.5845 | -0.15496 | -0.025553 | 0.045119 | 0.04637 | 0.20133 | -0.10273 | 0.044049 | -0.34607 | -0.12462 | 0.090829 | -0.012356 | 0.33371 | 0.039411 | 0.010562 | 122.9435 | 122.8663 | 123.0131 | 66.0155 | -123.124 | 122.8444 | 123.0085 | 122.9796 | 66.0236 | -123.3151
629.2656 | 123.1659 | -66.2476 | 56.7535 | 0.057412 | -0.046924 | -0.0064417 | 0.051029 | -0.01061 | 0.054873 | 0.027623 | -0.0047127 | 0.0021894 | 0.056768 | 0.048904 | 0.057187 | -66.1933 | -0.22295 | -66.1829 | 56.7051 | 56.6188 | 56.7655 | -66.3934 | -66.1567 | -0.21484 | -66.2416 | 56.6152 | 56.7701 | 56.7366 | -66.5936 | -0.1458 | -0.048441 | 0.054275 | 0.064683 | 0.21048 | -0.13478 | 0.012003 | -0.34607 | -0.13835 | 0.090828 | 0.005957 | 0.35203 | 0.016523 | -0.016904 | 122.9527 | 122.8663 | 123.0131 | 66.0246 | -123.1469 | 122.8627 | 123.0176 | 122.9842 | 66.0327 | -123.3472
630.2656 | 123.1522 | -66.2476 | 56.7719 | 0.04215 | -0.047993 | -0.0085787 | 0.048892 | -0.01061 | 0.055941 | 0.073406 | -0.0047127 | 0.0011204 | 0.0557 | 0.048904 | 0.057187 | -66.1979 | -0.21379 | -66.1875 | 56.7005 | 56.6325 | 56.7701 | -66.3934 | -66.1476 | -0.20568 | -66.2508 | 56.6106 | 56.7746 | 56.7321 | -66.5982 | -0.1458 | -0.07133 | 0.049696 | 0.060104 | 0.2059 | -0.13935 | -0.001729 | -0.35065 | -0.16124 | 0.099985 | -0.0032 | 0.34745 | 0.002791 | -0.039794 | 122.9481 | 122.8801 | 123.0177 | 66.0338 | -123.1652 | 122.8582 | 123.0222 | 122.9796 | 66.0419 | -123.3701
631.2656 | 123.1201 | -66.243 | 56.7398 | 0.072674 | -0.046924 | -0.0053737 | 0.048892 | -0.01061 | 0.054873 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.057836 | 0.049972 | 0.056118 | -66.1887 | -0.21379 | -66.192 | 56.7051 | 56.6279 | 56.7655 | -66.3888 | -66.143 | -0.20568 | -66.2508 | 56.6106 | 56.7746 | 56.7366 | -66.5982 | -0.1458 | -0.034708 | 0.054275 | 0.050948 | 0.19675 | -0.11189 | 0.025736 | -0.35523 | -0.1292 | 0.099986 | -0.007778 | 0.34745 | 0.034835 | -0.003171 | 122.9481 | 122.8709 | 123.0085 | 66.0292 | -123.1286 | 122.8536 | 123.0176 | 122.9796 | 66.0373 | -123.338
632.2656 | 123.1293 | -66.2247 | 56.781 | 0.057412 | -0.047993 | -0.0075097 | 0.051029 | -0.011679 | 0.054873 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.0557 | 0.049972 | 0.056118 | -66.1887 | -0.21379 | -66.1966 | 56.7097 | 56.6325 | 56.7701 | -66.3979 | -66.1522 | -0.2011 | -66.2462 | 56.6198 | 56.7655 | 56.7321 | -66.5982 | -0.17327 | -0.071329 | 0.035964 | 0.028059 | 0.20133 | -0.14851 | -0.010884 | -0.37354 | -0.16124 | 0.072518 | -0.021511 | 0.35203 | -0.015521 | -0.048949 | 122.9343 | 122.8572 | 122.9948 | 66.0109 | -123.1789 | 122.8444 | 122.9902 | 122.9567 | 66.0236 | -123.3792
633.2656 | 123.1522 | -66.2521 | 56.7581 | 0.057412 | -0.049061 | -0.0096467 | 0.051029 | -0.01061 | 0.053805 | 0.042884 | -0.0057807 | 5.2373e-05 | 0.056768 | 0.048904 | 0.056118 | -66.1887 | -0.21837 | -66.1875 | 56.6959 | 56.6188 | 56.7655 | -66.4025 | -66.143 | -0.20568 | -66.2462 | 56.6106 | 56.7701 | 56.7275 | -66.5936 | -0.15038 | -0.062176 | 0.06343 | 0.064681 | 0.21506 | -0.13936 | 0.007425 | -0.34149 | -0.14751 | 0.10914 | 0.005955 | 0.34745 | 0.011945 | -0.030639 | 122.9481 | 122.8709 | 123.0177 | 66.0338 | -123.1606 | 122.8627 | 123.0222 | 122.9796 | 66.0465 | -123.3517
634.2656 | 123.1293 | -66.2384 | 56.7444 | 0.072674 | -0.047993 | -0.0064417 | 0.052097 | -0.011679 | 0.054873 | 0.073406 | -0.0047127 | 0.0011204 | 0.0557 | 0.047836 | 0.056118 | -66.1887 | -0.20921 | -66.192 | 56.7051 | 56.6142 | 56.7747 | -66.4025 | -66.143 | -0.20568 | -66.2416 | 56.6106 | 56.7746 | 56.7366 | -66.5936 | -0.16411 | -0.039286 | 0.049697 | 0.04637 | 0.21048 | -0.1302 | 0.030316 | -0.35523 | -0.13377 | 0.095408 | -0.003199 | 0.35203 | 0.030257 | -0.007749 | 122.9435 | 122.8526 | 123.0131 | 66.0292 | -123.1469 | 122.849 | 123.013 | 122.975 | 66.0327 | -123.338
635.2656 | 123.143 | -66.2567 | 56.7581 | 0.04215 | -0.046924 | -0.0075097 | 0.052097 | -0.01061 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.056768 | 0.048904 | 0.057187 | -66.1887 | -0.22295 | -66.1875 | 56.7051 | 56.6188 | 56.7747 | -66.3979 | -66.143 | -0.20568 | -66.2462 | 56.6106 | 56.7701 | 56.7366 | -66.5891 | -0.14122 | -0.053019 | 0.068008 | 0.069259 | 0.21048 | -0.13936 | 0.016583 | -0.33234 | -0.14751 | 0.11372 | 0.010533 | 0.34287 | 0.011945 | -0.021482 | 122.9618 | 122.8755 | 123.0314 | 66.0338 | -123.1561 | 122.8673 | 123.0268 | 122.9933 | 66.051 | -123.3472
636.2656 | 123.111 | -66.2384 | 56.7444 | 0.072674 | -0.05013 | -0.0053737 | 0.04996 | -0.0095417 | 0.054873 | 0.058145 | -0.0047127 | 0.0032574 | 0.057836 | 0.049972 | 0.058255 | -66.1795 | -0.21379 | -66.1875 | 56.7051 | 56.5867 | 56.7747 | -66.3979 | -66.143 | -0.20568 | -66.2462 | 56.6106 | 56.7701 | 56.7366 | -66.5982 | -0.15953 | -0.039286 | 0.058854 | 0.050948 | 0.21048 | -0.15768 | 0.030316 | -0.3598 | -0.13377 | 0.095408 | -0.007778 | 0.35203 | 0.025678 | -0.007749 | 122.9435 | 122.8251 | 123.0131 | 66.0246 | -123.1423 | 122.849 | 123.0085 | 122.975 | 66.0327 | -123.3426
637.2656 | 123.1293 | -66.2292 | 56.7444 | 0.04215 | -0.051198 | -0.0075097 | 0.052097 | -0.01061 | 0.053805 | 0.073406 | -0.0025767 | 0.0011204 | 0.0557 | 0.049972 | 0.057187 | -66.1795 | -0.20921 | -66.192 | 56.7051 | 56.5684 | 56.7701 | -66.3979 | -66.1476 | -0.2011 | -66.2462 | 56.6152 | 56.7701 | 56.7321 | -66.5936 | -0.16869 | -0.039286 | 0.049699 | 0.037215 | 0.2059 | -0.17599 | 0.025737 | -0.36438 | -0.1292 | 0.081674 | -0.016933 | 0.34745 | 0.025678 | -0.012328 | 122.9343 | 122.7976 | 122.9994 | 66.02 | -123.1423 | 122.8444 | 122.9993 | 122.9613 | 66.0281 | -123.338
638.2656 | 123.2254 | -66.2476 | 56.749 | 0.04215 | -0.047993 | -0.0075097 | 0.051029 | -0.0084737 | 0.055941 | 0.042884 | -0.0047127 | 5.2373e-05 | 0.0557 | 0.049972 | 0.056118 | -66.1887 | -0.20921 | -66.1829 | 56.7051 | 56.573 | 56.7747 | -66.4025 | -66.1384 | -0.19195 | -66.2416 | 56.6198 | 56.7746 | 56.7321 | -66.5936 | -0.15496 | -0.043863 | 0.058853 | 0.064683 | 0.21964 | -0.17599 | 0.025739 | -0.34607 | -0.12919 | 0.10914 | 0.005957 | 0.35203 | 0.02568 | -0.016905 | 122.9527 | 122.8205 | 123.0223 | 66.0383 | -123.1515 | 122.8673 | 123.0222 | 122.9796 | 66.0556 | -123.3426
639.2656 | 123.1338 | -66.2292 | 56.7627 | 0.026888 | -0.049061 | -0.0064417 | 0.04996 | -0.0095417 | 0.053805 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.0557 | 0.053177 | 0.057187 | -66.1841 | -0.21837 | -66.1829 | 56.7097 | 56.573 | 56.7747 | -66.3979 | -66.1384 | -0.19195 | -66.2416 | 56.6106 | 56.7792 | 56.7412 | -66.5936 | -0.16869 | -0.053018 | 0.045121 | 0.046372 | 0.21506 | -0.18972 | 0.012006 | -0.36438 | -0.15208 | 0.090832 | -0.012354 | 0.35203 | 0.016526 | -0.021481 | 122.9389 | 122.8022 | 123.0039 | 66.0109 | -123.1606 | 122.8399 | 123.0085 | 122.9705 | 66.0373 | -123.3563
640.2656 | 123.1659 | -66.2247 | 56.749 | 0.04215 | -0.05013 | -0.0075097 | 0.051029 | -0.0095417 | 0.055941 | 0.027623 | -0.0015087 | 0.0021894 | 0.0557 | 0.049972 | 0.057187 | -66.175 | -0.20921 | -66.1829 | 56.7051 | 56.6004 | 56.7701 | -66.3934 | -66.1293 | -0.19653 | -66.2324 | 56.6198 | 56.7746 | 56.7366 | -66.5982 | -0.16869 | -0.043863 | 0.049699 | 0.041794 | 0.21048 | -0.14852 | 0.02116 | -0.37354 | -0.12919 | 0.095411 | -0.007775 | 0.36576 | 0.02568 | -0.012326 | 122.9298 | 122.8251 | 122.9948 | 66.0155 | -123.1423 | 122.8444 | 122.9993 | 122.9613 | 66.0281 | -123.3472
641.2656 | 123.1338 | -66.2476 | 56.7719 | 0.072674 | -0.047993 | -0.0064417 | 0.051029 | -0.01061 | 0.055941 | 0.042884 | -0.0057807 | 5.2373e-05 | 0.0557 | 0.049972 | 0.056118 | -66.175 | -0.21379 | -66.1829 | 56.7143 | 56.5776 | 56.7747 | -66.3934 | -66.1247 | -0.19195 | -66.237 | 56.6106 | 56.7746 | 56.7412 | -66.5936 | -0.1458 | -0.057595 | 0.072588 | 0.064683 | 0.21048 | -0.1943 | 0.00285 | -0.34607 | -0.16124 | 0.12288 | 0.010536 | 0.35661 | 0.002791 | -0.030637 | 122.9618 | 122.8251 | 123.0223 | 66.0338 | -123.1652 | 122.8582 | 123.0222 | 122.9888 | 66.0556 | -123.3655
642.2656 | 123.143 | -66.2384 | 56.7535 | 0.057412 | -0.05013 | -0.0064417 | 0.04996 | -0.0084737 | 0.053805 | 0.073406 | -0.0025767 | 0.0021894 | 0.056768 | 0.051041 | 0.057187 | -66.1887 | -0.21379 | -66.1783 | 56.7143 | 56.573 | 56.7839 | -66.3888 | -66.1293 | -0.19195 | -66.237 | 56.6152 | 56.7746 | 56.7458 | -66.5936 | -0.15038 | -0.039284 | 0.049697 | 0.060105 | 0.21048 | -0.18057 | 0.030318 | -0.35523 | -0.13835 | 0.10914 | 0.00138 | 0.35661 | 0.021102 | -0.007747 | 122.9527 | 122.8114 | 123.0223 | 66.0246 | -123.1423 | 122.8536 | 123.013 | 122.9842 | 66.0465 | -123.3472
643.2656 | 123.1567 | -66.2109 | 56.7719 | 0.04215 | -0.051198 | -0.0075097 | 0.051029 | -0.0084737 | 0.055941 | 0.042884 | -0.0047127 | 0.0011204 | 0.0557 | 0.048904 | 0.057187 | -66.175 | -0.21379 | -66.1737 | 56.7097 | 56.5867 | 56.7747 | -66.3888 | -66.1201 | -0.19195 | -66.237 | 56.6198 | 56.793 | 56.7458 | -66.5891 | -0.17784 | -0.062174 | 0.035966 | 0.037217 | 0.21506 | -0.18514 | 0.00285 | -0.37811 | -0.15208 | 0.090836 | -0.026086 | 0.35203 | 0.021105 | -0.026058 | 122.9206 | 122.7976 | 122.9856 | 65.9971 | -123.1606 | 122.8307 | 123.0039 | 122.9567 | 66.019 | -123.3609
644.2656 | 123.2346 | -66.2064 | 56.7398 | 0.04215 | -0.049061 | -0.0075097 | 0.048892 | -0.0095417 | 0.05701 | 0.073406 | -0.0036447 | 0.0021894 | 0.056768 | 0.048904 | 0.057187 | -66.1795 | -0.20921 | -66.1783 | 56.7097 | 56.5776 | 56.7793 | -66.3979 | -66.1201 | -0.18279 | -66.2324 | 56.6243 | 56.7838 | 56.7458 | -66.5891 | -0.19158 | -0.03013 | 0.026811 | 0.028062 | 0.21964 | -0.16226 | 0.039472 | -0.38269 | -0.11546 | 0.086259 | -0.026085 | 0.35661 | 0.043992 | 0.005986 | 122.916 | 122.7839 | 122.9856 | 65.9972 | -123.1377 | 122.8307 | 122.9902 | 122.9522 | 66.0236 | -123.3289
645.2656 | 123.2483 | -66.1789 | 56.7307 | 0.057412 | -0.049061 | -0.0064417 | 0.051029 | -0.0084737 | 0.05701 | 0.088667 | -0.0025767 | 0.0011204 | 0.056768 | 0.051041 | 0.056118 | -66.1704 | -0.21379 | -66.1737 | 56.7143 | 56.5684 | 56.7884 | -66.3888 | -66.1155 | -0.18279 | -66.2324 | 56.6243 | 56.7792 | 56.755 | -66.5753 | -0.20988 | -0.016396 | 0.008502 | 0.005174 | 0.21506 | -0.16226 | 0.057784 | -0.39642 | -0.10631 | 0.063371 | -0.053551 | 0.34287 | 0.048569 | 0.024298 | 122.8931 | 122.7473 | 122.9673 | 65.9651 | -123.1194 | 122.8032 | 122.9581 | 122.9338 | 65.9961 | -123.306
646.2656 | 123.2117 | -66.1789 | 56.7398 | 0.04215 | -0.049061 | -0.0064417 | 0.051029 | -0.0095417 | 0.05701 | 0.073406 | -0.0025767 | 0.0032574 | 0.054631 | 0.051041 | 0.056118 | -66.1612 | -0.21379 | -66.1783 | 56.7188 | 56.6004 | 56.7976 | -66.3934 | -66.1064 | -0.18737 | -66.2233 | 56.6243 | 56.793 | 56.7595 | -66.5799 | -0.21446 | -0.020973 | 0.017659 | 0.000596 | 0.21506 | -0.13936 | 0.057787 | -0.401 | -0.11546 | 0.072529 | -0.044393 | 0.35661 | 0.053149 | 0.019722 | 122.8977 | 122.7793 | 122.9765 | 65.9651 | -123.1332 | 122.8032 | 122.9718 | 122.9384 | 65.9915 | -123.3197
647.2656 | 123.23 | -66.1835 | 56.7627 | 0.057412 | -0.051198 | -0.0064417 | 0.051029 | -0.01061 | 0.05701 | 0.073406 | -0.0025767 | 0.0021894 | 0.0557 | 0.051041 | 0.058255 | -66.1612 | -0.21379 | -66.1691 | 56.7326 | 56.6325 | 56.793 | -66.3934 | -66.1155 | -0.18279 | -66.2187 | 56.6243 | 56.793 | 56.755 | -66.5753 | -0.20989 | -0.030126 | 0.022237 | 0.014331 | 0.22422 | -0.1302 | 0.03032 | -0.39184 | -0.13835 | 0.067949 | -0.035236 | 0.3566 | 0.030261 | -0.007745 | 122.916 | 122.816 | 122.9765 | 65.9697 | -123.1561 | 122.8078 | 122.9764 | 122.9384 | 66.0007 | -123.338
648.2656 | 123.1247 | -66.2155 | 56.7535 | 0.04215 | -0.049061 | -0.0075097 | 0.04996 | -0.01061 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.049972 | 0.056118 | -66.1521 | -0.21379 | -66.1783 | 56.728 | 56.6279 | 56.7976 | -66.3888 | -66.0972 | -0.17821 | -66.2141 | 56.6381 | 56.8067 | 56.7687 | -66.5753 | -0.17326 | -0.025549 | 0.063436 | 0.037217 | 0.21048 | -0.12562 | 0.044054 | -0.3598 | -0.11546 | 0.11831 | 0.001385 | 0.36118 | 0.053152 | 0.015146 | 122.9435 | 122.8434 | 123.0131 | 66.0017 | -123.1423 | 122.8536 | 123.0222 | 122.9842 | 66.0373 | -123.3289
649.2656 | 123.23 | -66.1835 | 56.7902 | 0.057412 | -0.049061 | -0.0064417 | 0.052097 | -0.0095417 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.052109 | 0.057187 | -66.1567 | -0.21837 | -66.1646 | 56.7371 | 56.6508 | 56.8113 | -66.3842 | -66.0926 | -0.18279 | -66.205 | 56.6381 | 56.7975 | 56.7687 | -66.5662 | -0.20073 | -0.053013 | 0.026815 | 0.018909 | 0.21964 | -0.13935 | 0.021168 | -0.38268 | -0.15208 | 0.090843 | -0.0215 | 0.36118 | 0.007374 | -0.021475 | 122.9206 | 122.8343 | 122.9948 | 65.9651 | -123.1744 | 122.8216 | 122.981 | 122.9522 | 66.0007 | -123.3563
650.2656 | 123.1842 | -66.1652 | 56.7764 | 0.057412 | -0.05013 | -0.0075097 | 0.04996 | -0.0095417 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.049972 | 0.059323 | -66.1475 | -0.20921 | -66.16 | 56.7463 | 56.6462 | 56.8068 | -66.3796 | -66.0972 | -0.17821 | -66.205 | 56.6427 | 56.7975 | 56.7733 | -66.5707 | -0.21446 | -0.030123 | 0.017661 | 0.005176 | 0.21964 | -0.13019 | 0.030323 | -0.40557 | -0.13377 | 0.067953 | -0.039811 | 0.36576 | 0.021107 | -0.003163 | 122.9115 | 122.8114 | 122.9719 | 65.956 | -123.156 | 122.8078 | 122.9627 | 122.9384 | 65.9869 | -123.3472
651.2656 | 123.2941 | -66.1652 | 56.7444 | 0.026888 | -0.051198 | -0.0096467 | 0.048892 | -0.0095417 | 0.054873 | 0.042884 | -0.0025767 | 5.2373e-05 | 0.0557 | 0.051041 | 0.056118 | -66.1475 | -0.21379 | -66.1508 | 56.7463 | 56.6142 | 56.8068 | -66.3796 | -66.0926 | -0.16448 | -66.1958 | 56.6518 | 56.8021 | 56.7733 | -66.5616 | -0.21446 | 0.00192 | 0.017661 | 0.014333 | 0.22879 | -0.1302 | 0.062366 | -0.39642 | -0.092569 | 0.072532 | -0.030654 | 0.36576 | 0.057729 | 0.02888 | 122.9115 | 122.7793 | 122.9719 | 65.9514 | -123.124 | 122.817 | 122.9673 | 122.9384 | 66.0007 | -123.306
652.2656 | 123.2574 | -66.156 | 56.7581 | 0.04215 | -0.05013 | -0.0064417 | 0.051029 | -0.01061 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.0557 | 0.048904 | 0.059323 | -66.1383 | -0.21379 | -66.1508 | 56.7417 | 56.6004 | 56.8113 | -66.3659 | -66.0789 | -0.17363 | -66.1958 | 56.6564 | 56.8067 | 56.7733 | -66.557 | -0.20988 | -0.016392 | 0.017663 | 0.005178 | 0.21506 | -0.15767 | 0.053211 | -0.40099 | -0.10172 | 0.077113 | -0.039809 | 0.36118 | 0.048574 | 0.015147 | 122.8977 | 122.7565 | 122.9673 | 65.9422 | -123.124 | 122.8124 | 122.9627 | 122.9293 | 65.9824 | -123.3151
653.2656 | 123.1567 | -66.1972 | 56.7993 | 0.026888 | -0.046924 | -0.0075097 | 0.04996 | -0.01061 | 0.055941 | 0.042884 | -0.0036447 | 0.0021894 | 0.056768 | 0.051041 | 0.05505 | -66.1292 | -0.20921 | -66.1417 | 56.7463 | 56.6004 | 56.8159 | -66.3659 | -66.0789 | -0.16448 | -66.1912 | 56.6472 | 56.8204 | 56.7824 | -66.5433 | -0.16868 | -0.053011 | 0.068018 | 0.055533 | 0.22421 | -0.19887 | 0.016592 | -0.34606 | -0.15208 | 0.11831 | 0.005969 | 0.35203 | 0.021112 | -0.016894 | 122.9435 | 122.7977 | 123.0131 | 65.988 | -123.1652 | 122.8444 | 123.0176 | 122.9796 | 66.0327 | -123.3426
654.2656 | 123.1842 | -66.1697 | 56.7902 | 0.057412 | -0.051198 | -0.0064417 | 0.051029 | -0.011679 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.056768 | 0.049972 | 0.057187 | -66.1292 | -0.20921 | -66.1417 | 56.7555 | 56.6233 | 56.8251 | -66.3567 | -66.0652 | -0.16448 | -66.1821 | 56.6564 | 56.8158 | 56.7824 | -66.5478 | -0.18699 | -0.0347 | 0.040552 | 0.028067 | 0.21506 | -0.16682 | 0.034904 | -0.3781 | -0.13377 | 0.10458 | -0.01234 | 0.36576 | 0.025688 | -0.007739 | 122.9252 | 122.7931 | 122.9948 | 65.9605 | -123.1469 | 122.8261 | 122.9856 | 122.9522 | 66.0053 | -123.338
655.2656 | 123.2208 | -66.1652 | 56.8085 | 0.026888 | -0.05013 | -0.0075097 | 0.051029 | -0.01061 | 0.053805 | 0.042884 | -0.0047127 | 0.0021894 | 0.0557 | 0.051041 | 0.056118 | -66.12 | -0.20921 | -66.1325 | 56.76 | 56.6279 | 56.8205 | -66.343 | -66.0606 | -0.15532 | -66.1775 | 56.6656 | 56.8296 | 56.7916 | -66.5433 | -0.17783 | -0.048432 | 0.045131 | 0.032646 | 0.21048 | -0.18055 | 0.012015 | -0.3781 | -0.14292 | 0.10458 | -0.012339 | 0.36576 | 0.021113 | -0.016893 | 122.9252 | 122.7931 | 122.9856 | 65.956 | -123.1515 | 122.8307 | 122.9947 | 122.9567 | 66.0098 | -123.3517
656.2656 | 123.2162 | -66.1423 | 56.7856 | 0.057412 | -0.052266 | -0.0096467 | 0.051029 | -0.0095417 | 0.054873 | 0.027623 | -0.0025767 | 5.2373e-05 | 0.056768 | 0.053177 | 0.056118 | -66.1155 | -0.21379 | -66.1279 | 56.7646 | 56.6279 | 56.8342 | -66.3384 | -66.0423 | -0.15074 | -66.1592 | 56.6793 | 56.8342 | 56.8007 | -66.5341 | -0.19614 | -0.020965 | 0.026821 | 0.014336 | 0.21047 | -0.15766 | 0.048639 | -0.39183 | -0.1063 | 0.10001 | -0.016912 | 0.37492 | 0.048581 | 0.015153 | 122.9069 | 122.7702 | 122.9765 | 65.9285 | -123.124 | 122.8216 | 122.9764 | 122.943 | 65.9915 | -123.3197
657.2656 | 123.2574 | -66.1377 | 56.7947 | 0.072674 | -0.05013 | -0.0064417 | 0.04996 | -0.011679 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.056768 | 0.048904 | 0.057187 | -66.1063 | -0.21379 | -66.1142 | 56.7692 | 56.6325 | 56.8388 | -66.343 | -66.0377 | -0.15532 | -66.1638 | 56.6839 | 56.8342 | 56.8053 | -66.5204 | -0.2053 | -0.025542 | 0.0314 | 0.023493 | 0.22879 | -0.16224 | 0.044062 | -0.38267 | -0.11087 | 0.10001 | -0.026069 | 0.3566 | 0.039425 | 0.010576 | 122.9069 | 122.7702 | 122.9765 | 65.9239 | -123.1377 | 122.8216 | 122.9719 | 122.943 | 65.9824 | -123.3151
658.2656 | 123.1201 | -66.2155 | 56.7947 | 0.026888 | -0.05013 | -0.0075097 | 0.04996 | -0.011679 | 0.054873 | 0.073406 | -0.0047127 | 0.0011204 | 0.0557 | 0.051041 | 0.057187 | -66.1017 | -0.21379 | -66.1096 | 56.7784 | 56.6417 | 56.848 | -66.3293 | -66.0377 | -0.1599 | -66.1592 | 56.6793 | 56.8433 | 56.8145 | -66.5158 | -0.11374 | -0.016386 | 0.1138 | 0.10589 | 0.21963 | -0.15308 | 0.053219 | -0.30027 | -0.11545 | 0.17783 | 0.05633 | 0.3566 | 0.048582 | 0.019733 | 122.9939 | 122.8572 | 123.0635 | 66.0017 | -123.124 | 122.8948 | 123.0588 | 123.03 | 66.0556 | -123.3105
659.2656 | 123.262 | -66.1011 | 56.7902 | 0.04215 | -0.051198 | -0.0075097 | 0.048892 | -0.01061 | 0.054873 | 0.042884 | -0.0025767 | -0.0010156 | 0.0557 | 0.051041 | 0.057187 | -66.088 | -0.20921 | -66.1005 | 56.7829 | 56.6462 | 56.8525 | -66.3247 | -66.0285 | -0.14158 | -66.1409 | 56.6976 | 56.8525 | 56.8191 | -66.5158 | -0.2236 | -0.007229 | 0.013093 | 0.000607 | 0.22421 | -0.14393 | 0.062376 | -0.41472 | -0.09256 | 0.072547 | -0.039796 | 0.37492 | 0.062317 | 0.02889 | 122.884 | 122.7473 | 122.9536 | 65.8919 | -123.1148 | 122.7987 | 122.9536 | 122.9201 | 65.9595 | -123.3059
660.2656 | 123.2529 | -66.124 | 56.7993 | 0.057412 | -0.051198 | -0.0053737 | 0.051029 | -0.0095417 | 0.05701 | 0.073406 | -0.0036447 | 0.0021894 | 0.057836 | 0.052109 | 0.056118 | -66.0834 | -0.20921 | -66.1005 | 56.7875 | 56.6462 | 56.8617 | -66.3247 | -66.0239 | -0.15532 | -66.1363 | 56.6976 | 56.8525 | 56.8236 | -66.5066 | -0.20071 | -0.011806 | 0.040559 | 0.023495 | 0.22421 | -0.15308 | 0.062378 | -0.38267 | -0.10171 | 0.10001 | -0.01233 | 0.37034 | 0.053162 | 0.024313 | 122.9115 | 122.7702 | 122.9857 | 65.9148 | -123.124 | 122.8216 | 122.9764 | 122.9476 | 65.9686 | -123.3059
661.2656 | 123.1934 | -66.1148 | 56.8268 | 0.057412 | -0.051198 | -0.0064417 | 0.04996 | -0.011679 | 0.05701 | 0.073406 | -0.0036447 | 0.0021894 | 0.0557 | 0.051041 | 0.056118 | -66.0788 | -0.20463 | -66.0913 | 56.8012 | 56.66 | 56.8663 | -66.3201 | -66.0148 | -0.15074 | -66.1363 | 56.7022 | 56.8662 | 56.8374 | -66.5066 | -0.20529 | -0.025537 | 0.035983 | 0.023496 | 0.22878 | -0.16681 | 0.039491 | -0.39182 | -0.1246 | 0.10002 | -0.021485 | 0.37034 | 0.039432 | 0.010583 | 122.9161 | 122.7748 | 122.9811 | 65.9102 | -123.1469 | 122.817 | 122.981 | 122.9522 | 65.9641 | -123.3334
662.2656 | 123.1979 | -66.1194 | 56.813 | 0.04215 | -0.05013 | -0.0075097 | 0.04996 | -0.011679 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.056768 | 0.052109 | 0.056118 | -66.0651 | -0.20921 | -66.0822 | 56.8012 | 56.6737 | 56.88 | -66.3018 | -65.9965 | -0.137 | -66.118 | 56.7159 | 56.8662 | 56.8374 | -66.5066 | -0.18239 | -0.011804 | 0.054296 | 0.037231 | 0.21963 | -0.13934 | 0.066959 | -0.38725 | -0.097134 | 0.12291 | 0.001408 | 0.38865 | 0.053165 | 0.024316 | 122.9206 | 122.7931 | 122.9994 | 65.9102 | -123.1148 | 122.8353 | 122.9856 | 122.9567 | 65.9824 | -123.3197
663.2656 | 123.1293 | -66.1652 | 56.8359 | 0.026888 | -0.052266 | -0.0064417 | 0.052097 | -0.0095417 | 0.054873 | 0.042884 | -0.0057807 | 0.0011204 | 0.054631 | 0.051041 | 0.057187 | -66.0605 | -0.20463 | -66.073 | 56.8104 | 56.6966 | 56.8892 | -66.3064 | -65.9965 | -0.137 | -66.1088 | 56.7159 | 56.8754 | 56.8465 | -66.4975 | -0.1412 | -0.025535 | 0.10465 | 0.092163 | 0.23336 | -0.13933 | 0.053229 | -0.33231 | -0.12002 | 0.16868 | 0.056342 | 0.38865 | 0.039434 | 0.010585 | 122.9756 | 122.8618 | 123.0543 | 65.9605 | -123.1423 | 122.8811 | 123.0405 | 123.0117 | 66.0282 | -123.3334
664.2656 | 123.262 | -66.0965 | 56.8314 | 0.04215 | -0.05013 | -0.0053737 | 0.051029 | -0.011679 | 0.05701 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.054631 | 0.052109 | 0.057187 | -66.0468 | -0.21379 | -66.0593 | 56.8196 | 56.7195 | 56.8892 | -66.2972 | -65.9736 | -0.14158 | -66.0997 | 56.7251 | 56.8845 | 56.8557 | -66.4837 | -0.2007 | -0.011801 | 0.049721 | 0.037234 | 0.23794 | -0.11186 | 0.057806 | -0.38724 | -0.10629 | 0.12291 | -0.003165 | 0.38408 | 0.053168 | 0.02432 | 122.9161 | 122.816 | 122.9857 | 65.8827 | -123.1286 | 122.8216 | 122.981 | 122.9522 | 65.9549 | -123.3151
665.2656 | 123.2666 | -66.069 | 56.8405 | 0.057412 | -0.051198 | -0.0064417 | 0.04996 | -0.01061 | 0.05701 | 0.058145 | -0.0047127 | 0.0011204 | 0.0557 | 0.052109 | 0.05505 | -66.0422 | -0.20463 | -66.0593 | 56.8333 | 56.7195 | 56.8983 | -66.2926 | -65.969 | -0.137 | -66.0951 | 56.7296 | 56.8891 | 56.8648 | -66.4792 | -0.22359 | -0.007221 | 0.026834 | 0.009768 | 0.23336 | -0.12102 | 0.057808 | -0.41013 | -0.11087 | 0.10003 | -0.026052 | 0.38407 | 0.048592 | 0.024322 | 122.9023 | 122.7885 | 122.9674 | 65.8644 | -123.1331 | 122.7987 | 122.9581 | 122.9339 | 65.932 | -123.3197
666.2656 | 123.2895 | -66.0828 | 56.868 | 0.026888 | -0.051198 | -0.0053737 | 0.048892 | -0.0095417 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.056768 | 0.052109 | 0.057187 | -66.0376 | -0.20005 | -66.0501 | 56.8379 | 56.7332 | 56.9075 | -66.2789 | -65.9644 | -0.137 | -66.0859 | 56.7434 | 56.9074 | 56.874 | -66.47 | -0.19612 | -0.030109 | 0.045145 | 0.032658 | 0.22878 | -0.13475 | 0.039499 | -0.38724 | -0.12459 | 0.11834 | -0.003162 | 0.38407 | 0.03944 | 0.006013 | 122.9206 | 122.816 | 122.9902 | 65.8827 | -123.1469 | 122.8261 | 122.9902 | 122.9568 | 65.9458 | -123.338
667.3125 | 123.143 | -66.1514 | 56.8634 | 0.04215 | -0.052266 | -0.0064417 | 0.04996 | -0.011679 | 0.055941 | 0.058145 | -0.0025767 | 0.0011204 | 0.057836 | 0.051041 | 0.057187 | -66.0285 | -0.20005 | -66.0364 | 56.847 | 56.7241 | 56.9212 | -66.2743 | -65.9553 | -0.137 | -66.0676 | 56.748 | 56.9074 | 56.8786 | -66.4608 | -0.12288 | -0.016374 | 0.12297 | 0.11506 | 0.23793 | -0.13933 | 0.057813 | -0.30942 | -0.11544 | 0.19616 | 0.083817 | 0.39323 | 0.044018 | 0.01517 | 122.9985 | 122.8755 | 123.0726 | 65.9514 | -123.1377 | 122.8994 | 123.0588 | 123.03 | 66.0144 | -123.3242
668.2656 | 123.1888 | -66.1102 | 56.868 | 0.04215 | -0.05013 | -0.0053737 | 0.04996 | -0.01061 | 0.05701 | 0.058145 | -0.0047127 | 0.0011204 | 0.056768 | 0.052109 | 0.056118 | -66.0147 | -0.19547 | -66.0318 | 56.8608 | 56.7332 | 56.9212 | -66.2606 | -65.937 | -0.12327 | -66.0676 | 56.7617 | 56.912 | 56.8877 | -66.4425 | -0.15034 | -0.007217 | 0.095502 | 0.078436 | 0.22878 | -0.13475 | 0.053235 | -0.3323 | -0.10628 | 0.17328 | 0.042618 | 0.37492 | 0.044019 | 0.019749 | 122.971 | 122.8435 | 123.0314 | 65.9148 | -123.1286 | 122.8719 | 123.0222 | 122.998 | 65.987 | -123.3105
669.2656 | 123.2254 | -66.0599 | 56.8954 | 0.057412 | -0.051198 | -0.0075097 | 0.048892 | -0.011679 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.0557 | 0.051041 | 0.05505 | -66.0056 | -0.20005 | -66.0089 | 56.8608 | 56.7287 | 56.935 | -66.2606 | -65.9278 | -0.12784 | -66.063 | 56.7709 | 56.9257 | 56.8923 | -66.4517 | -0.20069 | -0.034683 | 0.054305 | 0.050973 | 0.25167 | -0.16679 | 0.039505 | -0.39181 | -0.12459 | 0.13208 | -0.003157 | 0.38865 | 0.030289 | -0.003139 | 122.9206 | 122.7885 | 122.9948 | 65.8598 | -123.156 | 122.8307 | 122.9856 | 122.9522 | 65.932 | -123.3471
670.2656 | 123.2437 | -66.0507 | 56.9 | 0.057412 | -0.051198 | -0.0075097 | 0.051029 | -0.0095417 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.0557 | 0.052109 | 0.056118 | -65.9964 | -0.20463 | -66.0043 | 56.8699 | 56.7287 | 56.935 | -66.2468 | -65.9095 | -0.12327 | -66.0447 | 56.7709 | 56.9349 | 56.906 | -66.4288 | -0.19611 | -0.030103 | 0.054307 | 0.046397 | 0.24251 | -0.17137 | 0.034928 | -0.37807 | -0.12917 | 0.14124 | 0.006002 | 0.38407 | 0.034869 | 0.00602 | 122.9206 | 122.7794 | 122.9857 | 65.8461 | -123.1469 | 122.8216 | 122.9856 | 122.9568 | 65.9275 | -123.3288
671.2656 | 123.2712 | -66.0233 | 56.8863 | 0.04215 | -0.051198 | -0.0085787 | 0.04996 | -0.0095417 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.052109 | 0.058255 | -65.9918 | -0.19547 | -65.9952 | 56.8745 | 56.7332 | 56.9487 | -66.2377 | -65.9049 | -0.11411 | -66.0401 | 56.7846 | 56.9349 | 56.9106 | -66.4334 | -0.21442 | -0.011793 | 0.031419 | 0.028087 | 0.24251 | -0.15306 | 0.062395 | -0.41012 | -0.1017 | 0.11835 | -0.016885 | 0.39323 | 0.048601 | 0.024331 | 122.8978 | 122.7565 | 122.9719 | 65.8278 | -123.124 | 122.8078 | 122.9581 | 122.9339 | 65.9091 | -123.3197
672.2656 | 123.2529 | -66.0049 | 56.8863 | 0.04215 | -0.05013 | -0.0075097 | 0.04996 | -0.011679 | 0.053805 | 0.073406 | -0.0036447 | 0.0011204 | 0.057836 | 0.053177 | 0.056118 | -65.9827 | -0.20005 | -65.986 | 56.8928 | 56.7424 | 56.9578 | -66.2194 | -65.8912 | -0.11411 | -66.0264 | 56.7937 | 56.9532 | 56.9198 | -66.4151 | -0.21442 | 0.006521 | 0.022266 | 0.018934 | 0.23335 | -0.1439 | 0.071553 | -0.41011 | -0.092543 | 0.11378 | -0.021459 | 0.38865 | 0.066915 | 0.033488 | 122.8978 | 122.7473 | 122.9628 | 65.8049 | -123.1057 | 122.7987 | 122.9582 | 122.9247 | 65.8908 | -123.3013
673.2656 | 123.1934 | -66.0599 | 56.9046 | 0.04215 | -0.052266 | -0.0064417 | 0.048892 | -0.01061 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.054631 | 0.053177 | 0.056118 | -65.9552 | -0.20463 | -65.9769 | 56.902 | 56.7653 | 56.9716 | -66.2102 | -65.8866 | -0.10953 | -66.0081 | 56.8029 | 56.9624 | 56.9335 | -66.4013 | -0.15033 | -0.002632 | 0.10467 | 0.083021 | 0.23335 | -0.13931 | 0.066978 | -0.34144 | -0.1017 | 0.17329 | 0.051787 | 0.39323 | 0.057763 | 0.028914 | 122.9618 | 122.8252 | 123.0315 | 65.8552 | -123.1148 | 122.8628 | 123.0222 | 122.9934 | 65.9503 | -123.3059
674.2656 | 123.2437 | -66.0004 | 56.9229 | 0.026888 | -0.051198 | -0.0053737 | 0.051029 | -0.01061 | 0.055941 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.054631 | 0.052109 | 0.056118 | -65.9461 | -0.19547 | -65.9631 | 56.9111 | 56.7653 | 56.9762 | -66.2056 | -65.8729 | -0.10495 | -66.0035 | 56.8121 | 56.9715 | 56.9381 | -66.4013 | -0.20526 | -0.011786 | 0.054315 | 0.037247 | 0.2425 | -0.15763 | 0.053246 | -0.40095 | -0.11085 | 0.12752 | -0.003143 | 0.39781 | 0.048609 | 0.015181 | 122.9115 | 122.7657 | 122.9765 | 65.8049 | -123.1285 | 122.8124 | 122.9719 | 122.9385 | 65.8954 | -123.3242
675.2656 | 123.1979 | -65.9866 | 56.9641 | 0.072674 | -0.051198 | -0.0075097 | 0.051029 | -0.011679 | 0.05701 | 0.088667 | -0.0015087 | 0.0011204 | 0.0557 | 0.052109 | 0.056118 | -65.9415 | -0.19547 | -65.954 | 56.9157 | 56.8065 | 56.9899 | -66.1965 | -65.8637 | -0.10953 | -65.9898 | 56.8304 | 56.9898 | 56.9518 | -66.3876 | -0.20983 | -0.048406 | 0.04516 | 0.032671 | 0.2425 | -0.15761 | 0.025784 | -0.40095 | -0.13373 | 0.12294 | -0.00314 | 0.39781 | 0.025725 | -0.012281 | 122.9023 | 122.7931 | 122.9765 | 65.7912 | -123.1606 | 122.817 | 122.9765 | 122.9385 | 65.8771 | -123.3517
676.2656 | 123.2437 | -65.9546 | 56.9595 | 0.057412 | -0.051198 | -0.0075097 | 0.04996 | -0.011679 | 0.055941 | 0.073406 | -0.0025767 | 5.2373e-05 | 0.0557 | 0.052109 | 0.057187 | -65.9277 | -0.19547 | -65.9494 | 56.9249 | 56.8385 | 56.9899 | -66.1781 | -65.8454 | -0.10953 | -65.9852 | 56.8304 | 56.9944 | 56.9564 | -66.383 | -0.22356 | -0.034672 | 0.026852 | 0.005206 | 0.22877 | -0.12098 | 0.030361 | -0.42841 | -0.12916 | 0.10921 | -0.030604 | 0.39781 | 0.034881 | -0.003125 | 122.8795 | 122.7931 | 122.9445 | 65.7591 | -123.1377 | 122.785 | 122.949 | 122.911 | 65.8451 | -123.3425
677.2656 | 123.2254 | -65.9683 | 56.9458 | 0.04215 | -0.05013 | -0.0075097 | 0.04996 | -0.01061 | 0.054873 | 0.073406 | -0.0015087 | 0.0021894 | 0.056768 | 0.053177 | 0.057187 | -65.9186 | -0.19547 | -65.9311 | 56.9294 | 56.8569 | 57.0036 | -66.1736 | -65.8316 | -0.095794 | -65.9715 | 56.8395 | 57.0036 | 56.9701 | -66.3738 | -0.20525 | -0.016361 | 0.049742 | 0.037252 | 0.2425 | -0.088936 | 0.05783 | -0.40552 | -0.10627 | 0.13668 | -0.003135 | 0.40239 | 0.057771 | 0.024344 | 122.8978 | 122.8252 | 122.972 | 65.7728 | -123.1194 | 122.8079 | 122.9719 | 122.9385 | 65.8725 | -123.3196
678.2656 | 123.1979 | -66.0141 | 56.9412 | 0.072674 | -0.051198 | -0.0075097 | 0.04996 | -0.011679 | 0.055941 | 0.042884 | -0.0015087 | 0.0011204 | 0.056768 | 0.054246 | 0.056118 | -65.914 | -0.1909 | -65.9219 | 56.9478 | 56.8202 | 57.0174 | -66.1598 | -65.8225 | -0.10037 | -65.9531 | 56.8578 | 57.0127 | 56.9793 | -66.3647 | -0.14573 | 0.006531 | 0.1001 | 0.092185 | 0.23792 | -0.12099 | 0.076143 | -0.35059 | -0.083375 | 0.19161 | 0.060956 | 0.41155 | 0.071506 | 0.038079 | 122.9619 | 122.8343 | 123.0315 | 65.8232 | -123.1011 | 122.8719 | 123.0268 | 122.9934 | 65.9137 | -123.3059
679.2656 | 123.2437 | -65.9821 | 56.9916 | 0.04215 | -0.052266 | -0.0075097 | 0.04996 | -0.011679 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.0557 | 0.053177 | 0.057187 | -65.9003 | -0.19547 | -65.9082 | 56.9569 | 56.8157 | 57.0174 | -66.1507 | -65.8042 | -0.10495 | -65.944 | 56.867 | 57.0127 | 56.993 | -66.3418 | -0.16862 | -0.034667 | 0.081789 | 0.073877 | 0.2425 | -0.17592 | 0.025789 | -0.35974 | -0.12457 | 0.17789 | 0.03807 | 0.39781 | 0.021152 | 0.001461 | 122.939 | 122.7977 | 122.9994 | 65.7866 | -123.1423 | 122.8491 | 122.9948 | 122.9751 | 65.8771 | -123.3334
680.2656 | 123.2712 | -65.9134 | 56.987 | 0.04215 | -0.053335 | -0.0085787 | 0.048892 | -0.01061 | 0.05701 | 0.073406 | -0.0057807 | 0.0021894 | 0.056768 | 0.052109 | 0.057187 | -65.8957 | -0.18632 | -65.9036 | 56.9661 | 56.8248 | 57.0357 | -66.1415 | -65.7996 | -0.10037 | -65.9394 | 56.8716 | 57.0356 | 56.9976 | -66.3464 | -0.22813 | -0.020933 | 0.017702 | 0.00979 | 0.23792 | -0.16219 | 0.048681 | -0.43298 | -0.11542 | 0.1138 | -0.026016 | 0.40697 | 0.048622 | 0.010616 | 122.8795 | 122.7382 | 122.9491 | 65.7271 | -123.1285 | 122.785 | 122.949 | 122.911 | 65.813 | -123.3334
681.2656 | 123.2941 | -65.9134 | 56.987 | 0.04215 | -0.052266 | -0.0085787 | 0.04996 | -0.0084737 | 0.05701 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.053177 | 0.058255 | -65.8774 | -0.19547 | -65.8853 | 56.9798 | 56.8431 | 57.0494 | -66.1324 | -65.7904 | -0.095794 | -65.9211 | 56.8762 | 57.0448 | 57.0114 | -66.3281 | -0.21897 | -0.007198 | 0.036016 | 0.028103 | 0.24707 | -0.14387 | 0.062417 | -0.41467 | -0.11084 | 0.12296 | -0.007701 | 0.40696 | 0.057779 | 0.024352 | 122.8932 | 122.7565 | 122.9628 | 65.7179 | -123.1194 | 122.7896 | 122.9582 | 122.9247 | 65.8176 | -123.3151
682.2656 | 123.2437 | -65.9225 | 57.0145 | 0.026888 | -0.052266 | -0.0064417 | 0.04996 | -0.013815 | 0.055941 | 0.042884 | -0.0036447 | 0.0011204 | 0.0557 | 0.053177 | 0.05505 | -65.8682 | -0.18632 | -65.8807 | 56.9844 | 56.8706 | 57.0586 | -66.1186 | -65.7721 | -0.095794 | -65.9119 | 56.8945 | 57.0494 | 57.0251 | -66.3189 | -0.19608 | -0.030084 | 0.054327 | 0.041836 | 0.23791 | -0.14386 | 0.044109 | -0.39635 | -0.11999 | 0.15043 | 0.010611 | 0.40696 | 0.034893 | 0.010623 | 122.9069 | 122.7931 | 122.9811 | 65.7362 | -123.1331 | 122.817 | 122.9719 | 122.9476 | 65.8268 | -123.3334
683.2656 | 123.2483 | -65.8997 | 57.0053 | 0.04215 | -0.05013 | -0.0085787 | 0.048892 | -0.01061 | 0.053805 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.053177 | 0.05505 | -65.8545 | -0.18174 | -65.8624 | 56.9981 | 56.8843 | 57.0723 | -66.114 | -65.7584 | -0.091215 | -65.8936 | 56.9082 | 57.0677 | 57.0342 | -66.3006 | -0.21439 | -0.007194 | 0.045175 | 0.037261 | 0.25165 | -0.12097 | 0.067 | -0.40093 | -0.097098 | 0.14128 | 0.006038 | 0.40696 | 0.062362 | 0.028935 | 122.8978 | 122.784 | 122.972 | 65.7179 | -123.1194 | 122.8079 | 122.9673 | 122.9339 | 65.8084 | -123.3059
684.2656 | 123.2986 | -65.8859 | 57.0236 | 0.026888 | -0.054403 | -0.0064417 | 0.048892 | -0.0095417 | 0.054873 | 0.042884 | -0.0025767 | 0.0021894 | 0.0557 | 0.053177 | 0.056118 | -65.8362 | -0.18632 | -65.8532 | 57.021 | 56.9118 | 57.086 | -66.1049 | -65.7355 | -0.091215 | -65.8799 | 56.9265 | 57.0814 | 57.048 | -66.296 | -0.21896 | -0.002613 | 0.049755 | 0.032685 | 0.25165 | -0.11181 | 0.062424 | -0.41008 | -0.097095 | 0.15044 | 0.006041 | 0.41612 | 0.057787 | 0.02436 | 122.9069 | 122.7977 | 122.972 | 65.6996 | -123.1285 | 122.8125 | 122.9673 | 122.9339 | 65.7947 | -123.3196
685.2656 | 123.2346 | -65.8859 | 57.0282 | 0.026888 | -0.052266 | -0.0075097 | 0.04996 | -0.01061 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.053563 | 0.051041 | 0.057187 | -65.8224 | -0.18632 | -65.8349 | 57.0256 | 56.9439 | 57.0998 | -66.0911 | -65.7263 | -0.086637 | -65.8661 | 56.9311 | 57.0951 | 57.0526 | -66.2823 | -0.20522 | -0.002612 | 0.06349 | 0.050998 | 0.25622 | -0.084333 | 0.071583 | -0.39634 | -0.097094 | 0.15959 | 0.019777 | 0.41612 | 0.066946 | 0.024361 | 122.9115 | 122.8298 | 122.9857 | 65.6996 | -123.1193 | 122.817 | 122.9811 | 122.9385 | 65.7993 | -123.3105
686.2656 | 123.2254 | -65.8905 | 57.0419 | 0.057412 | -0.052266 | -0.0075097 | 0.04996 | -0.011679 | 0.058078 | 0.058145 | -0.0047127 | 0.0011204 | 0.0557 | 0.053177 | 0.057187 | -65.8179 | -0.18174 | -65.8258 | 57.0393 | 56.9393 | 57.1135 | -66.0728 | -65.708 | -0.082058 | -65.8616 | 56.9494 | 57.0997 | 57.0709 | -66.2685 | -0.18233 | -0.00261 | 0.072647 | 0.064733 | 0.24706 | -0.10264 | 0.071586 | -0.37803 | -0.092513 | 0.18248 | 0.028934 | 0.40696 | 0.057792 | 0.028943 | 122.9298 | 122.8298 | 123.004 | 65.7088 | -123.1148 | 122.8399 | 122.9902 | 122.9614 | 65.8084 | -123.3105
687.2656 | 123.2529 | -65.8951 | 57.0694 | 0.057412 | -0.051198 | -0.0053737 | 0.051029 | -0.01061 | 0.054873 | 0.073406 | -0.0036447 | 0.0021894 | 0.054631 | 0.052109 | 0.057187 | -65.7995 | -0.18174 | -65.812 | 57.0485 | 56.9393 | 57.1273 | -66.0637 | -65.7126 | -0.091215 | -65.8387 | 56.9586 | 57.1135 | 57.08 | -66.2594 | -0.16859 | -0.020919 | 0.095538 | 0.083045 | 0.25164 | -0.13011 | 0.057856 | -0.36429 | -0.11082 | 0.18248 | 0.056405 | 0.4207 | 0.044062 | 0.010634 | 122.9436 | 122.8344 | 123.0223 | 65.7133 | -123.1331 | 122.8537 | 123.0085 | 122.9751 | 65.8039 | -123.3288
688.2656 | 123.2574 | -65.8676 | 57.0877 | 0.057412 | -0.052266 | -0.0075097 | 0.04996 | -0.01061 | 0.05701 | 0.058145 | -0.0015087 | 5.2373e-05 | 0.0557 | 0.053177 | 0.057187 | -65.7904 | -0.17716 | -65.7937 | 57.0622 | 56.9576 | 57.1273 | -66.0591 | -65.6897 | -0.086637 | -65.8295 | 56.9632 | 57.1226 | 57.0892 | -66.2411 | -0.19148 | -0.025495 | 0.077229 | 0.073893 | 0.26537 | -0.13011 | 0.039545 | -0.37345 | -0.12455 | 0.17791 | 0.038097 | 0.41154 | 0.034908 | 0.00148 | 122.9298 | 122.8252 | 122.9949 | 65.6905 | -123.1468 | 122.8308 | 122.9902 | 122.9568 | 65.781 | -123.3288
689.2656 | 123.0469 | -65.8356 | 57.1198 | 0.04215 | -0.053335 | -0.0085787 | 0.047824 | -0.013815 | 0.055941 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.054631 | 0.054246 | 0.056118 | -65.7767 | -0.18174 | -65.7891 | 57.0714 | 56.9851 | 57.141 | -66.0499 | -65.6714 | -0.086637 | -65.8158 | 56.9769 | 57.1364 | 57.1075 | -66.2365 | -0.21437 | -0.048381 | 0.05892 | 0.046427 | 0.2608 | -0.13468 | 0.021238 | -0.40091 | -0.14286 | 0.16418 | 0.019789 | 0.4207 | 0.016601 | -0.012248 | 122.9069 | 122.8206 | 122.9766 | 65.6538 | -123.1697 | 122.8125 | 122.9719 | 122.9431 | 65.7489 | -123.3562
690.2656 | 123.2529 | -65.8356 | 57.0831 | 0.026888 | -0.052266 | -0.0064417 | 0.051029 | -0.01061 | 0.05701 | 0.058145 | -0.0036447 | 0.0032574 | 0.0557 | 0.054246 | 0.056118 | -65.7721 | -0.18632 | -65.7846 | 57.0897 | 57.008 | 57.1547 | -66.0362 | -65.6577 | -0.086637 | -65.802 | 56.986 | 57.1455 | 57.1167 | -66.2273 | -0.20063 | 0.006554 | 0.063499 | 0.051005 | 0.25164 | -0.07516 | 0.071595 | -0.39175 | -0.097084 | 0.17792 | 0.033525 | 0.42528 | 0.062379 | 0.03353 | 122.9253 | 122.8435 | 122.9903 | 65.6493 | -123.1193 | 122.8216 | 122.9811 | 122.9522 | 65.7489 | -123.3105
691.2656 | 123.2162 | -65.8447 | 57.0923 | 0.04215 | -0.052266 | -0.0075097 | 0.04996 | -0.01061 | 0.055941 | 0.073406 | -0.0025767 | 0.0032574 | 0.0557 | 0.053177 | 0.056118 | -65.7583 | -0.17716 | -65.7708 | 57.0943 | 56.9713 | 57.1593 | -66.0225 | -65.6439 | -0.082058 | -65.7929 | 57.0044 | 57.1547 | 57.1258 | -66.2136 | -0.17774 | 0.001977 | 0.08639 | 0.073896 | 0.25163 | -0.12095 | 0.067018 | -0.36886 | -0.087925 | 0.20081 | 0.051839 | 0.4207 | 0.062381 | 0.033532 | 122.939 | 122.8161 | 123.004 | 65.6676 | -123.1147 | 122.8491 | 122.9994 | 122.9705 | 65.7627 | -123.3059
692.2656 | 123.2071 | -65.8218 | 57.1106 | 0.026888 | -0.053335 | -0.0075097 | 0.048892 | -0.01061 | 0.055941 | 0.058145 | -0.0036447 | 0.0053944 | 0.056768 | 0.053177 | 0.056118 | -65.7492 | -0.18174 | -65.7525 | 57.108 | 56.9668 | 57.173 | -66.0087 | -65.6302 | -0.086637 | -65.7792 | 57.0044 | 57.173 | 57.1304 | -66.2044 | -0.18689 | -0.002599 | 0.072657 | 0.06932 | 0.25621 | -0.14384 | 0.062443 | -0.38259 | -0.10624 | 0.19166 | 0.042686 | 0.42528 | 0.062384 | 0.0198 | 122.9298 | 122.7886 | 122.9949 | 65.6401 | -123.1193 | 122.8262 | 122.9948 | 122.9522 | 65.7352 | -123.315
693.2656 | 123.2025 | -65.7944 | 57.1014 | 0.057412 | -0.053335 | -0.0064417 | 0.04996 | -0.012747 | 0.055941 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.0557 | 0.054246 | 0.058255 | -65.7263 | -0.18174 | -65.7296 | 57.1126 | 56.9759 | 57.1868 | -65.9904 | -65.621 | -0.082058 | -65.77 | 57.0227 | 57.1776 | 57.1533 | -66.1907 | -0.19604 | 0.011136 | 0.068084 | 0.064746 | 0.26079 | -0.12552 | 0.085335 | -0.39632 | -0.078766 | 0.17335 | 0.024378 | 0.4207 | 0.076119 | 0.051849 | 122.9069 | 122.7703 | 122.9811 | 65.6126 | -123.0919 | 122.817 | 122.9719 | 122.9477 | 65.7123 | -123.2921
694.2656 | 123.2346 | -65.8035 | 57.1014 | 0.057412 | -0.055471 | -0.0064417 | 0.048892 | -0.01061 | 0.058078 | 0.088667 | -0.0025767 | 0.0021894 | 0.0557 | 0.054246 | 0.058255 | -65.7171 | -0.17716 | -65.7296 | 57.1309 | 56.9897 | 57.2005 | -65.9813 | -65.6119 | -0.086637 | -65.7563 | 57.041 | 57.1913 | 57.167 | -66.1724 | -0.17773 | 0.029449 | 0.086396 | 0.073901 | 0.25163 | -0.11179 | 0.099071 | -0.36885 | -0.060452 | 0.19166 | 0.047269 | 0.41612 | 0.089855 | 0.065584 | 122.9344 | 122.7932 | 123.004 | 65.6264 | -123.0827 | 122.8445 | 122.9948 | 122.9706 | 65.7169 | -123.2738
695.2656 | 123.1888 | -65.7852 | 57.1472 | 0.04215 | -0.052266 | -0.0064417 | 0.048892 | -0.0095417 | 0.058078 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.054631 | 0.054246 | 0.057187 | -65.708 | -0.17716 | -65.7159 | 57.1355 | 57.0034 | 57.2097 | -65.9675 | -65.589 | -0.082058 | -65.7334 | 57.0547 | 57.2005 | 57.1624 | -66.1632 | -0.1823 | -0.011749 | 0.077242 | 0.069325 | 0.25163 | -0.14383 | 0.062451 | -0.378 | -0.092493 | 0.19625 | 0.051852 | 0.42985 | 0.053235 | 0.015229 | 122.9207 | 122.7886 | 122.9949 | 65.6081 | -123.1147 | 122.8399 | 122.9857 | 122.9477 | 65.7032 | -123.3104
696.2656 | 123.2117 | -65.7898 | 57.1747 | 0.04215 | -0.054403 | -0.0064417 | 0.04996 | -0.012747 | 0.05701 | 0.058145 | -0.0015087 | 0.0011204 | 0.056768 | 0.053177 | 0.056118 | -65.6988 | -0.17716 | -65.7022 | 57.1492 | 57.0354 | 57.2188 | -65.9584 | -65.5752 | -0.082058 | -65.7242 | 57.0547 | 57.2142 | 57.1808 | -66.1495 | -0.16857 | -0.02548 | 0.090977 | 0.087638 | 0.2562 | -0.13924 | 0.044142 | -0.35969 | -0.11996 | 0.21456 | 0.065587 | 0.42527 | 0.039505 | 0.006077 | 122.939 | 122.8252 | 123.0086 | 65.6126 | -123.133 | 122.8445 | 123.004 | 122.9706 | 65.7077 | -123.3242
697.2656 | 123.23 | -65.7715 | 57.1701 | 0.04215 | -0.053335 | -0.0064417 | 0.04996 | -0.01061 | 0.05701 | 0.058145 | -0.0025767 | 0.0011204 | 0.056768 | 0.053177 | 0.056118 | -65.6851 | -0.17258 | -65.6884 | 57.1584 | 57.0492 | 57.2234 | -65.9538 | -65.5523 | -0.082058 | -65.7059 | 57.0685 | 57.2279 | 57.1853 | -66.1449 | -0.1823 | -0.011746 | 0.086401 | 0.083062 | 0.26536 | -0.12092 | 0.053299 | -0.37342 | -0.10165 | 0.21914 | 0.065591 | 0.43901 | 0.057819 | 0.015234 | 122.9298 | 122.8207 | 122.9949 | 65.5989 | -123.1239 | 122.8399 | 122.9994 | 122.9568 | 65.6894 | -123.315
698.2656 | 123.2346 | -65.7532 | 57.1609 | 0.026888 | -0.052266 | -0.0085787 | 0.051029 | -0.01061 | 0.05701 | 0.042884 | -0.0025767 | 0.0011204 | 0.054631 | 0.055314 | 0.05505 | -65.6759 | -0.17258 | -65.6838 | 57.1675 | 57.0675 | 57.2417 | -65.9446 | -65.5386 | -0.086637 | -65.7013 | 57.0822 | 57.2371 | 57.2128 | -66.1312 | -0.19145 | 0.006566 | 0.077248 | 0.06933 | 0.26078 | -0.093454 | 0.080768 | -0.37799 | -0.078755 | 0.21457 | 0.05186 | 0.42985 | 0.076131 | 0.051861 | 122.9207 | 122.8207 | 122.9949 | 65.5806 | -123.1056 | 122.8354 | 122.9903 | 122.966 | 65.6665 | -123.2921
699.2656 | 123.2529 | -65.7486 | 57.1793 | 0.026888 | -0.053335 | -0.0075097 | 0.051029 | -0.012747 | 0.055941 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.0557 | 0.054246 | 0.058255 | -65.6622 | -0.18174 | -65.6655 | 57.1858 | 57.0492 | 57.2555 | -65.9263 | -65.534 | -0.086637 | -65.6876 | 57.0868 | 57.2554 | 57.2174 | -66.122 | -0.17771 | 0.00657 | 0.086405 | 0.083065 | 0.26078 | -0.13008 | 0.076194 | -0.37341 | -0.092487 | 0.21457 | 0.061018 | 0.43443 | 0.076135 | 0.038129 | 122.9344 | 122.7978 | 123.0041 | 65.5669 | -123.1056 | 122.8354 | 123.004 | 122.966 | 65.662 | -123.3013
700.2656 | 123.2529 | -65.7349 | 57.2067 | 0.026888 | -0.054403 | -0.0075097 | 0.048892 | -0.0095417 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.054631 | 0.054246 | 0.058255 | -65.653 | -0.168 | -65.6564 | 57.1904 | 57.0904 | 57.2783 | -65.9217 | -65.5203 | -0.0729 | -65.6693 | 57.1005 | 57.26 | 57.2174 | -66.1174 | -0.18687 | -0.016318 | 0.081829 | 0.078489 | 0.26535 | -0.11634 | 0.071621 | -0.38257 | -0.10622 | 0.21457 | 0.0656 | 0.44817 | 0.053248 | 0.010663 | 122.9253 | 122.8253 | 123.0132 | 65.5669 | -123.1285 | 122.8354 | 122.9948 | 122.9523 | 65.662 | -123.3242
701.2656 | 123.2529 | -65.7257 | 57.193 | 0.04215 | -0.055471 | -0.0085787 | 0.04996 | -0.012747 | 0.055941 | 0.042884 | -0.0057807 | 0.0011204 | 0.053563 | 0.054246 | 0.058255 | -65.6393 | -0.17716 | -65.6472 | 57.2087 | 57.127 | 57.2783 | -65.9126 | -65.502 | -0.086637 | -65.6647 | 57.1188 | 57.2737 | 57.2403 | -66.0991 | -0.18686 | 0.015729 | 0.086409 | 0.078491 | 0.26535 | -0.065971 | 0.085354 | -0.37341 | -0.07417 | 0.22373 | 0.061023 | 0.43443 | 0.080717 | 0.047289 | 122.9344 | 122.8527 | 123.0041 | 65.5485 | -123.1056 | 122.8445 | 122.9994 | 122.966 | 65.6391 | -123.2921
702.2656 | 123.2712 | -65.6937 | 57.2159 | 0.057412 | -0.054403 | -0.0064417 | 0.04996 | -0.012747 | 0.055941 | 0.042884 | -0.0036447 | 0.0011204 | 0.0557 | 0.054246 | 0.056118 | -65.621 | -0.17258 | -65.6243 | 57.2225 | 57.1499 | 57.3012 | -65.8988 | -65.4974 | -0.086637 | -65.6509 | 57.128 | 57.2829 | 57.254 | -66.0854 | -0.20517 | 0.006576 | 0.072679 | 0.069339 | 0.27451 | -0.065965 | 0.085359 | -0.39172 | -0.087901 | 0.19627 | 0.042717 | 0.43443 | 0.066986 | 0.038137 | 122.9161 | 122.8436 | 122.9949 | 65.5211 | -123.1147 | 122.8216 | 122.9765 | 122.9477 | 65.607 | -123.3013
703.2656 | 123.2529 | -65.6754 | 57.2296 | 0.026888 | -0.053335 | -0.0064417 | 0.051029 | -0.012747 | 0.054873 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.0557 | 0.054246 | 0.056118 | -65.6073 | -0.18174 | -65.6152 | 57.2408 | 57.1728 | 57.3058 | -65.8943 | -65.4791 | -0.091215 | -65.6326 | 57.1371 | 57.2874 | 57.2678 | -66.0808 | -0.2189 | 0.011156 | 0.068103 | 0.060184 | 0.27908 | -0.056803 | 0.076204 | -0.40545 | -0.092477 | 0.19627 | 0.04272 | 0.44817 | 0.057831 | 0.03814 | 122.9161 | 122.8482 | 122.9812 | 65.4936 | -123.1239 | 122.8125 | 122.9628 | 122.9431 | 65.5841 | -123.3104
704.2656 | 123.2529 | -65.6754 | 57.2113 | 0.026888 | -0.054403 | -0.0096467 | 0.051029 | -0.012747 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.052109 | 0.057187 | -65.5981 | -0.17716 | -65.6014 | 57.2453 | 57.1865 | 57.3241 | -65.8805 | -65.4608 | -0.082058 | -65.6143 | 57.1463 | 57.3103 | 57.2815 | -66.0671 | -0.20517 | 0.034045 | 0.07726 | 0.073919 | 0.27908 | -0.024756 | 0.11283 | -0.39171 | -0.06501 | 0.21459 | 0.061035 | 0.45275 | 0.099034 | 0.070186 | 122.9207 | 122.8619 | 122.9995 | 65.4982 | -123.0918 | 122.8216 | 122.9857 | 122.9568 | 65.5933 | -123.2784
705.2656 | 123.2254 | -65.6891 | 57.2388 | 0.026888 | -0.054403 | -0.0075097 | 0.052097 | -0.011679 | 0.058078 | 0.073406 | -0.0036447 | 0.0011204 | 0.0557 | 0.055314 | 0.056118 | -65.5798 | -0.18174 | -65.5877 | 57.2591 | 57.1865 | 57.3379 | -65.8622 | -65.447 | -0.086637 | -65.6006 | 57.1692 | 57.3195 | 57.2906 | -66.0533 | -0.17312 | 0.020314 | 0.10931 | 0.10139 | 0.2745 | -0.052222 | 0.099099 | -0.36424 | -0.069584 | 0.24206 | 0.088504 | 0.45274 | 0.080726 | 0.051877 | 122.9482 | 122.8756 | 123.027 | 65.5073 | -123.101 | 122.8583 | 123.0086 | 122.9797 | 65.6025 | -123.2921
706.2656 | 123.1247 | -65.7211 | 57.28 | 0.057412 | -0.054403 | -0.0075097 | 0.048892 | -0.01061 | 0.054873 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.056768 | 0.056383 | 0.058255 | -65.5752 | -0.18632 | -65.5785 | 57.2728 | 57.1957 | 57.3424 | -65.8576 | -65.4379 | -0.091215 | -65.5914 | 57.1738 | 57.3287 | 57.2998 | -66.0533 | -0.13649 | -0.007149 | 0.14593 | 0.14259 | 0.27908 | -0.084263 | 0.062479 | -0.3322 | -0.1062 | 0.28326 | 0.12971 | 0.4619 | 0.048685 | 0.019836 | 122.9939 | 122.9168 | 123.0636 | 65.5348 | -123.1376 | 122.8949 | 123.0498 | 123.0209 | 65.6299 | -123.3333
707.2656 | 123.1201 | -65.6799 | 57.28 | 0.04215 | -0.052266 | -0.0075097 | 0.04996 | -0.011679 | 0.054873 | 0.042884 | -0.0025767 | 0.0011204 | 0.0557 | 0.053177 | 0.057187 | -65.566 | -0.18632 | -65.5694 | 57.282 | 57.2003 | 57.3608 | -65.8439 | -65.4287 | -0.086637 | -65.5777 | 57.1875 | 57.347 | 57.3135 | -66.0304 | -0.16396 | 0.002008 | 0.11389 | 0.11054 | 0.2745 | -0.079684 | 0.080794 | -0.3505 | -0.092468 | 0.25122 | 0.10224 | 0.45274 | 0.066999 | 0.033572 | 122.9619 | 122.8802 | 123.0407 | 65.4936 | -123.1239 | 122.8674 | 123.0269 | 122.9935 | 65.5933 | -123.3104
708.2656 | 123.143 | -65.6845 | 57.3212 | 0.026888 | -0.054403 | -0.0064417 | 0.048892 | -0.011679 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.054631 | 0.056383 | 0.058255 | -65.5569 | -0.18632 | -65.5511 | 57.2957 | 57.1774 | 57.3608 | -65.821 | -65.415 | -0.086637 | -65.5731 | 57.1921 | 57.347 | 57.3273 | -66.0213 | -0.13648 | -0.025456 | 0.12762 | 0.13344 | 0.26992 | -0.14378 | 0.039595 | -0.33677 | -0.12909 | 0.26953 | 0.1114 | 0.44817 | 0.0258 | 0.006109 | 122.9802 | 122.8619 | 123.0453 | 65.4982 | -123.1422 | 122.8766 | 123.0315 | 123.0118 | 65.5979 | -123.3424
709.2656 | 123.1064 | -65.6662 | 57.3029 | 0.04215 | -0.053335 | -0.0064417 | 0.04996 | -0.012747 | 0.054873 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.056383 | 0.056118 | -65.5294 | -0.18632 | -65.5373 | 57.3049 | 57.1637 | 57.3791 | -65.8164 | -65.3921 | -0.086637 | -65.5502 | 57.215 | 57.3744 | 57.3273 | -66.0075 | -0.15021 | 0.002012 | 0.13678 | 0.12886 | 0.27907 | -0.1392 | 0.07622 | -0.34134 | -0.087885 | 0.27411 | 0.11598 | 0.45732 | 0.071583 | 0.02442 | 122.9711 | 122.8299 | 123.0453 | 65.4799 | -123.1193 | 122.8812 | 123.0406 | 122.9935 | 65.5796 | -123.3104
710.2656 | 123.1338 | -65.6799 | 57.3257 | 0.057412 | -0.055471 | -0.0064417 | 0.048892 | -0.011679 | 0.054873 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.0557 | 0.057451 | 0.057187 | -65.5248 | -0.1909 | -65.5282 | 57.314 | 57.182 | 57.3882 | -65.7935 | -65.3738 | -0.10037 | -65.5365 | 57.2195 | 57.3744 | 57.3502 | -65.9938 | -0.11359 | -0.01172 | 0.15509 | 0.15175 | 0.26534 | -0.14378 | 0.062488 | -0.31387 | -0.1062 | 0.30616 | 0.14345 | 0.45732 | 0.048694 | 0.024424 | 122.994 | 122.8619 | 123.0682 | 65.489 | -123.1193 | 122.8995 | 123.0544 | 123.0301 | 65.5796 | -123.3195
711.2656 | 123.1338 | -65.6616 | 57.3578 | 0.026888 | -0.053335 | -0.0075097 | 0.048892 | -0.011679 | 0.055941 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.0557 | 0.055314 | 0.056118 | -65.5157 | -0.20005 | -65.5099 | 57.3278 | 57.2003 | 57.3974 | -65.7844 | -65.36 | -0.095794 | -65.5182 | 57.2379 | 57.3973 | 57.3547 | -65.9755 | -0.12274 | -0.030028 | 0.14594 | 0.15175 | 0.27449 | -0.1575 | 0.039602 | -0.31387 | -0.11993 | 0.30159 | 0.14346 | 0.45732 | 0.039544 | -0.003041 | 122.9894 | 122.8619 | 123.059 | 65.4616 | -123.1421 | 122.8995 | 123.059 | 123.0164 | 65.5658 | -123.3333
712.2656 | 123.111 | -65.6387 | 57.3532 | 0.026888 | -0.053335 | -0.0085787 | 0.04996 | -0.01061 | 0.055941 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.0557 | 0.055314 | 0.05505 | -65.4974 | -0.20463 | -65.5053 | 57.3461 | 57.2415 | 57.4065 | -65.7706 | -65.3509 | -0.095794 | -65.509 | 57.2516 | 57.4019 | 57.3731 | -65.9618 | -0.13189 | -0.007137 | 0.14136 | 0.13344 | 0.26533 | -0.11171 | 0.053338 | -0.32302 | -0.10161 | 0.28786 | 0.12973 | 0.45274 | 0.0487 | 0.019852 | 122.9848 | 122.8802 | 123.0453 | 65.4341 | -123.1238 | 122.8903 | 123.0406 | 123.0118 | 65.5429 | -123.315
713.2656 | 123.1659 | -65.6158 | 57.3669 | 0.057412 | -0.054403 | -0.0085787 | 0.04996 | -0.012747 | 0.055941 | 0.073406 | -0.0025767 | 0.0011204 | 0.056768 | 0.056383 | 0.056118 | -65.4836 | -0.20463 | -65.487 | 57.3507 | 57.2552 | 57.4249 | -65.7615 | -65.3371 | -0.095794 | -65.4907 | 57.2608 | 57.4294 | 57.3822 | -65.9572 | -0.14562 | -0.016291 | 0.13221 | 0.12887 | 0.27449 | -0.11171 | 0.057919 | -0.34133 | -0.10619 | 0.2787 | 0.12515 | 0.46648 | 0.062439 | 0.015276 | 122.9665 | 122.8711 | 123.0407 | 65.4112 | -123.1284 | 122.8766 | 123.0452 | 122.9981 | 65.5201 | -123.3241
714.2656 | 123.1613 | -65.6021 | 57.4127 | 0.057412 | -0.053335 | -0.0085787 | 0.04996 | -0.012747 | 0.054873 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.053563 | 0.057451 | 0.057187 | -65.4745 | -0.20463 | -65.4824 | 57.369 | 57.269 | 57.434 | -65.7477 | -65.3234 | -0.091215 | -65.4815 | 57.2745 | 57.434 | 57.396 | -65.9389 | -0.14562 | -0.043755 | 0.12764 | 0.11971 | 0.26533 | -0.14375 | 0.021299 | -0.33675 | -0.13823 | 0.27871 | 0.12058 | 0.45732 | 0.021241 | -0.016765 | 122.9711 | 122.8711 | 123.0361 | 65.3975 | -123.1604 | 122.8766 | 123.0361 | 122.9981 | 65.5109 | -123.3516
715.2656 | 123.1659 | -65.5975 | 57.4265 | 0.011626 | -0.054403 | -0.0075097 | 0.048892 | -0.011679 | 0.054873 | 0.073406 | -0.0036447 | 0.0021894 | 0.053563 | 0.056383 | 0.057187 | -65.4653 | -0.20463 | -65.4687 | 57.369 | 57.2552 | 57.4478 | -65.734 | -65.3097 | -0.086637 | -65.4678 | 57.2791 | 57.4523 | 57.4097 | -65.9343 | -0.13646 | -0.057488 | 0.13221 | 0.12887 | 0.26533 | -0.17122 | 0.021302 | -0.33675 | -0.14738 | 0.28786 | 0.12973 | 0.46648 | 0.025822 | -0.016763 | 122.9665 | 122.8528 | 123.0453 | 65.3929 | -123.1604 | 122.8766 | 123.0498 | 123.0072 | 65.5109 | -123.3607
716.2656 | 123.1476 | -65.5655 | 57.4265 | 0.057412 | -0.055471 | -0.0075097 | 0.051029 | -0.014884 | 0.055941 | 0.073406 | -0.0057807 | 0.0021894 | 0.054631 | 0.056383 | 0.057187 | -65.447 | -0.20921 | -65.4458 | 57.3919 | 57.2507 | 57.4615 | -65.7294 | -65.2959 | -0.095794 | -65.4541 | 57.2974 | 57.4569 | 57.4234 | -65.9205 | -0.16392 | -0.034596 | 0.11848 | 0.11972 | 0.28364 | -0.1758 | 0.035038 | -0.35505 | -0.12907 | 0.26956 | 0.11143 | 0.46648 | 0.030401 | -0.003027 | 122.9573 | 122.8161 | 123.027 | 65.3563 | -123.1559 | 122.8629 | 123.0223 | 122.9889 | 65.4697 | -123.347
717.2656 | 123.1476 | -65.5472 | 57.4493 | 0.04215 | -0.05654 | -0.0075097 | 0.04996 | -0.01061 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.052495 | 0.056383 | 0.057187 | -65.447 | -0.20921 | -65.432 | 57.3964 | 57.2919 | 57.4706 | -65.7203 | -65.2822 | -0.10037 | -65.4357 | 57.3065 | 57.4614 | 57.4326 | -65.9068 | -0.17308 | -0.052905 | 0.10017 | 0.11514 | 0.28822 | -0.15748 | 0.021307 | -0.35963 | -0.1428 | 0.26498 | 0.11143 | 0.47106 | 0.012091 | -0.016758 | 122.9436 | 122.839 | 123.0178 | 65.338 | -123.1696 | 122.8537 | 123.0086 | 122.9798 | 65.4468 | -123.3561
718.2656 | 123.1293 | -65.5197 | 57.4448 | 0.026888 | -0.054403 | -0.0064417 | 0.048892 | -0.011679 | 0.055941 | 0.073406 | -0.0036447 | 0.0021894 | 0.0557 | 0.057451 | 0.05505 | -65.4287 | -0.21837 | -65.4275 | 57.4102 | 57.301 | 57.489 | -65.7019 | -65.273 | -0.10037 | -65.4266 | 57.3203 | 57.4797 | 57.4417 | -65.8976 | -0.18223 | -0.034592 | 0.091021 | 0.092254 | 0.27448 | -0.14374 | 0.0442 | -0.37793 | -0.12449 | 0.24667 | 0.093122 | 0.47106 | 0.034984 | -0.003022 | 122.9299 | 122.8207 | 123.0087 | 65.3013 | -123.1467 | 122.84 | 122.9995 | 122.9615 | 65.4193 | -123.3424
719.2656 | 123.143 | -65.5472 | 57.4356 | 0.04215 | -0.055471 | -0.0075097 | 0.051029 | -0.011679 | 0.053805 | 0.058145 | -0.0025767 | 0.0021894 | 0.0557 | 0.055314 | 0.056118 | -65.415 | -0.22295 | -65.4183 | 57.4285 | 57.3056 | 57.4981 | -65.6882 | -65.2501 | -0.10037 | -65.4129 | 57.3294 | 57.4889 | 57.4463 | -65.8885 | -0.14102 | -0.007124 | 0.13222 | 0.12888 | 0.2699 | -0.13001 | 0.062512 | -0.34131 | -0.10618 | 0.29703 | 0.13432 | 0.47563 | 0.053296 | 0.010711 | 122.9757 | 122.8528 | 123.0453 | 65.3242 | -123.1238 | 122.8766 | 123.0361 | 122.9935 | 65.4468 | -123.3241
720.2656 | 123.1705 | -65.5197 | 57.4448 | 0.057412 | -0.055471 | -0.0075097 | 0.051029 | -0.0095417 | 0.055941 | 0.058145 | -0.0057807 | 0.0021894 | 0.0557 | 0.056383 | 0.056118 | -65.4058 | -0.22295 | -65.4091 | 57.4239 | 57.301 | 57.5027 | -65.6836 | -65.241 | -0.10495 | -65.3945 | 57.3432 | 57.4981 | 57.4601 | -65.8748 | -0.16391 | -0.020857 | 0.11391 | 0.11057 | 0.27448 | -0.14374 | 0.057935 | -0.35504 | -0.10159 | 0.27872 | 0.12517 | 0.48021 | 0.053298 | 0.015292 | 122.9436 | 122.8207 | 123.0224 | 65.2968 | -123.1284 | 122.8629 | 123.0178 | 122.9798 | 65.4148 | -123.3195
721.2656 | 123.1796 | -65.5151 | 57.4814 | 0.04215 | -0.054403 | -0.0085787 | 0.048892 | -0.011679 | 0.055941 | 0.042884 | -0.0025767 | 0.0021894 | 0.0557 | 0.057451 | 0.056118 | -65.3875 | -0.2321 | -65.3863 | 57.4422 | 57.3148 | 57.5164 | -65.679 | -65.2318 | -0.10953 | -65.3854 | 57.3523 | 57.5026 | 57.4784 | -65.8656 | -0.16391 | -0.039164 | 0.12765 | 0.12888 | 0.29279 | -0.16663 | 0.03505 | -0.35046 | -0.12906 | 0.2833 | 0.12975 | 0.48021 | 0.021256 | -0.003015 | 122.9574 | 122.8299 | 123.0316 | 65.283 | -123.1604 | 122.8675 | 123.0178 | 122.9935 | 65.4056 | -123.347
722.2656 | 123.1613 | -65.4877 | 57.4814 | 0.04215 | -0.055471 | -0.0085787 | 0.047824 | -0.011679 | 0.055941 | 0.058145 | -0.0025767 | 5.2373e-05 | 0.054631 | 0.056383 | 0.057187 | -65.3783 | -0.23668 | -65.3817 | 57.4514 | 57.356 | 57.5302 | -65.6745 | -65.2227 | -0.10495 | -65.3762 | 57.3661 | 57.5164 | 57.4921 | -65.861 | -0.1868 | -0.030008 | 0.10934 | 0.10599 | 0.29279 | -0.12542 | 0.048786 | -0.37335 | -0.11532 | 0.265 | 0.11145 | 0.48479 | 0.034992 | 0.010721 | 122.939 | 122.8436 | 123.0178 | 65.251 | -123.1559 | 122.8537 | 123.004 | 122.9798 | 65.3827 | -123.3424
723.2656 | 123.1293 | -65.4968 | 57.4722 | 0.04215 | -0.055471 | -0.0085787 | 0.047824 | -0.0095417 | 0.054873 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.054631 | 0.054246 | 0.057187 | -65.3692 | -0.23668 | -65.3679 | 57.4697 | 57.3789 | 57.5485 | -65.647 | -65.2044 | -0.11411 | -65.3625 | 57.3706 | 57.5347 | 57.4967 | -65.8519 | -0.15017 | -0.002539 | 0.12765 | 0.12888 | 0.27905 | -0.093367 | 0.076255 | -0.35503 | -0.10159 | 0.29247 | 0.13434 | 0.48937 | 0.062461 | 0.024455 | 122.9665 | 122.8757 | 123.0453 | 65.2601 | -123.1192 | 122.8675 | 123.0315 | 122.9935 | 65.3827 | -123.3241
724.2656 | 123.1567 | -65.4831 | 57.5043 | 0.04215 | -0.055471 | -0.0085787 | 0.04996 | -0.011679 | 0.055941 | 0.073406 | -0.0036447 | 0.0011204 | 0.054631 | 0.058519 | 0.058255 | -65.3554 | -0.24584 | -65.3588 | 57.4788 | 57.3697 | 57.5485 | -65.647 | -65.1906 | -0.11411 | -65.3579 | 57.389 | 57.5438 | 57.515 | -65.8335 | -0.1639 | -0.025425 | 0.12765 | 0.12431 | 0.28821 | -0.13457 | 0.044212 | -0.35045 | -0.11532 | 0.29247 | 0.12518 | 0.47563 | 0.039575 | 0.010726 | 122.9619 | 122.8528 | 123.0316 | 65.2373 | -123.1513 | 122.872 | 123.0269 | 122.9981 | 65.369 | -123.3378
725.2656 | 123.1888 | -65.4739 | 57.5043 | 0.04215 | -0.057608 | -0.0064417 | 0.051029 | -0.011679 | 0.05701 | 0.073406 | -0.0036447 | 0.0021894 | 0.054631 | 0.058519 | 0.057187 | -65.3509 | -0.24584 | -65.3451 | 57.488 | 57.4018 | 57.5576 | -65.6424 | -65.1815 | -0.11869 | -65.3442 | 57.3798 | 57.553 | 57.5196 | -65.829 | -0.16848 | -0.016269 | 0.12308 | 0.12889 | 0.29736 | -0.10251 | 0.05337 | -0.35503 | -0.12447 | 0.29247 | 0.12976 | 0.48479 | 0.048732 | 0.015305 | 122.9619 | 122.8757 | 123.0316 | 65.2281 | -123.1467 | 122.8537 | 123.0269 | 122.9935 | 65.3553 | -123.3332
726.2656 | 123.175 | -65.451 | 57.5043 | 0.04215 | -0.055471 | -0.0064417 | 0.048892 | -0.01061 | 0.054873 | 0.088667 | -0.0036447 | 0.0011204 | 0.053563 | 0.058519 | 0.057187 | -65.3417 | -0.25042 | -65.3359 | 57.5017 | 57.443 | 57.5714 | -65.6333 | -65.1632 | -0.11869 | -65.3259 | 57.4027 | 57.5576 | 57.5333 | -65.8244 | -0.18221 | -0.002533 | 0.10935 | 0.11516 | 0.29736 | -0.061305 | 0.067105 | -0.37334 | -0.10158 | 0.2879 | 0.12519 | 0.49853 | 0.053311 | 0.029041 | 122.9528 | 122.894 | 123.0224 | 65.2006 | -123.1375 | 122.8537 | 123.0086 | 122.9844 | 65.3324 | -123.3287
727.2656 | 123.1888 | -65.4419 | 57.5409 | 0.04215 | -0.05654 | -0.0053737 | 0.04996 | -0.011679 | 0.054873 | 0.088667 | -0.0025767 | 0.0011204 | 0.054631 | 0.055314 | 0.056118 | -65.328 | -0.25042 | -65.3359 | 57.5109 | 57.4338 | 57.5851 | -65.6241 | -65.1586 | -0.12784 | -65.3213 | 57.4073 | 57.5667 | 57.5425 | -65.8061 | -0.1822 | -0.029999 | 0.11393 | 0.106 | 0.28821 | -0.10708 | 0.044219 | -0.36418 | -0.13363 | 0.28332 | 0.12061 | 0.48479 | 0.025846 | 0.001576 | 122.9528 | 122.8757 | 123.027 | 65.1915 | -123.165 | 122.8492 | 123.0086 | 122.9844 | 65.3141 | -123.347
728.2656 | 123.1888 | -65.4236 | 57.5363 | 0.057412 | -0.05654 | -0.0064417 | 0.048892 | -0.01061 | 0.054873 | 0.058145 | -0.0025767 | 0.0032574 | 0.054631 | 0.057451 | 0.057187 | -65.3188 | -0.26415 | -65.3176 | 57.5201 | 57.4521 | 57.5851 | -65.6149 | -65.1494 | -0.12327 | -65.3167 | 57.421 | 57.5759 | 57.5516 | -65.7878 | -0.19136 | -0.016264 | 0.10477 | 0.106 | 0.29736 | -0.084191 | 0.048797 | -0.36417 | -0.11531 | 0.27417 | 0.10688 | 0.47105 | 0.039581 | 0.015311 | 122.9436 | 122.8757 | 123.0087 | 65.1594 | -123.1513 | 122.8446 | 122.9995 | 122.9752 | 65.3003 | -123.3241
729.2656 | 123.1705 | -65.4236 | 57.5363 | 0.011626 | -0.05654 | -0.0085787 | 0.048892 | -0.012747 | 0.055941 | 0.042884 | -0.0025767 | 0.0043254 | 0.054631 | 0.055314 | 0.053982 | -65.3142 | -0.26415 | -65.3084 | 57.5246 | 57.4567 | 57.5988 | -65.6149 | -65.1357 | -0.12327 | -65.2892 | 57.4347 | 57.5896 | 57.5562 | -65.7878 | -0.19136 | -0.011685 | 0.10935 | 0.11516 | 0.30652 | -0.079612 | 0.062533 | -0.36417 | -0.10158 | 0.28791 | 0.13435 | 0.49853 | 0.053317 | 0.01989 | 122.9482 | 122.8803 | 123.0224 | 65.1594 | -123.1513 | 122.8583 | 123.0132 | 122.9798 | 65.3003 | -123.3241
730.2656 | 123.1567 | -65.451 | 57.55 | 0.072674 | -0.055471 | -0.0064417 | 0.051029 | -0.011679 | 0.055941 | 0.042884 | -0.0047127 | 0.0011204 | 0.054631 | 0.058519 | 0.056118 | -65.3051 | -0.26415 | -65.2993 | 57.5338 | 57.4659 | 57.608 | -65.5966 | -65.1265 | -0.13242 | -65.2892 | 57.4347 | 57.5942 | 57.5699 | -65.7878 | -0.14558 | -0.016262 | 0.14597 | 0.15178 | 0.29736 | -0.084187 | 0.057957 | -0.33671 | -0.11531 | 0.32453 | 0.16182 | 0.49853 | 0.044163 | 0.019893 | 122.9848 | 122.9169 | 123.0591 | 65.1869 | -123.1467 | 122.8858 | 123.0453 | 123.021 | 65.3186 | -123.3378
731.2656 | 123.2025 | -65.4099 | 57.5409 | 0.04215 | -0.054403 | -0.0075097 | 0.048892 | -0.012747 | 0.054873 | 0.042884 | -0.0025767 | 0.0021894 | 0.0557 | 0.056383 | 0.05505 | -65.3005 | -0.27331 | -65.2901 | 57.5521 | 57.4704 | 57.6172 | -65.5875 | -65.1128 | -0.137 | -65.2801 | 57.4439 | 57.6034 | 57.5699 | -65.7694 | -0.17762 | 0.011207 | 0.10935 | 0.11974 | 0.29736 | -0.070453 | 0.076269 | -0.35959 | -0.096998 | 0.29707 | 0.12978 | 0.48937 | 0.062475 | 0.029048 | 122.962 | 122.8803 | 123.027 | 65.1365 | -123.1284 | 122.8537 | 123.0132 | 122.9798 | 65.2728 | -123.3103
732.2656 | 123.1842 | -65.4099 | 57.5546 | 0.04215 | -0.055471 | -0.010716 | 0.047824 | -0.011679 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.056768 | 0.058519 | 0.057187 | -65.2776 | -0.28247 | -65.2855 | 57.5567 | 57.4796 | 57.6309 | -65.5737 | -65.1036 | -0.12784 | -65.2709 | 57.4531 | 57.6079 | 57.5837 | -65.7649 | -0.16388 | 0.002053 | 0.13224 | 0.12432 | 0.2882 | -0.075027 | 0.076273 | -0.35501 | -0.10157 | 0.30622 | 0.13894 | 0.49395 | 0.053322 | 0.029051 | 122.9665 | 122.8895 | 123.0408 | 65.1274 | -123.1284 | 122.8629 | 123.0178 | 122.9935 | 65.282 | -123.3195
733.2656 | 123.1659 | -65.4007 | 57.5592 | 0.04215 | -0.055471 | -0.0075097 | 0.048892 | -0.011679 | 0.055941 | 0.073406 | -0.0047127 | 0.0011204 | 0.053563 | 0.057451 | 0.056118 | -65.273 | -0.28247 | -65.2718 | 57.5567 | 57.4338 | 57.6263 | -65.5646 | -65.0945 | -0.14158 | -65.2572 | 57.4622 | 57.6171 | 57.5837 | -65.7465 | -0.16388 | -0.002525 | 0.12767 | 0.1289 | 0.29277 | -0.12539 | 0.067117 | -0.34585 | -0.096994 | 0.30623 | 0.14352 | 0.48937 | 0.057901 | 0.024473 | 122.9574 | 122.8345 | 123.027 | 65.1182 | -123.1238 | 122.8629 | 123.0178 | 122.9844 | 65.2591 | -123.3058
734.2656 | 123.1384 | -65.3687 | 57.5684 | 0.057412 | -0.055471 | -0.0085787 | 0.04996 | -0.012747 | 0.058078 | 0.058145 | -0.0047127 | 0.0021894 | 0.053563 | 0.057451 | 0.056118 | -65.2685 | -0.28704 | -65.2672 | 57.5613 | 57.4292 | 57.6401 | -65.5554 | -65.0853 | -0.137 | -65.248 | 57.4668 | 57.6263 | 57.5883 | -65.742 | -0.18676 | -0.007101 | 0.1002 | 0.10143 | 0.2882 | -0.13913 | 0.071697 | -0.37332 | -0.10157 | 0.28334 | 0.12063 | 0.49395 | 0.057903 | 0.019897 | 122.9299 | 122.7979 | 123.0087 | 65.0816 | -123.1238 | 122.8354 | 122.9949 | 122.9569 | 65.2317 | -123.3103
735.2656 | 123.1888 | -65.3915 | 57.605 | 0.057412 | -0.055471 | -0.0064417 | 0.04996 | -0.012747 | 0.058078 | 0.042884 | -0.0025767 | 0.0021894 | 0.053563 | 0.057451 | 0.057187 | -65.2501 | -0.27789 | -65.2489 | 57.575 | 57.443 | 57.6446 | -65.5463 | -65.0716 | -0.15532 | -65.2434 | 57.4805 | 57.6308 | 57.6066 | -65.7374 | -0.15472 | -0.029987 | 0.14141 | 0.14263 | 0.29735 | -0.16201 | 0.039655 | -0.34585 | -0.12446 | 0.31996 | 0.1481 | 0.49395 | 0.025861 | 0.00159 | 122.9665 | 122.8345 | 123.0362 | 65.1137 | -123.1512 | 122.8721 | 123.0224 | 122.9981 | 65.2362 | -123.3424
736.2656 | 123.2529 | -65.3549 | 57.6233 | 0.057412 | -0.05654 | -0.0075097 | 0.04996 | -0.011679 | 0.05701 | 0.058145 | -0.0025767 | 0.0032574 | 0.052495 | 0.058519 | 0.056118 | -65.2456 | -0.29162 | -65.2443 | 57.5887 | 57.4521 | 57.6492 | -65.5371 | -65.067 | -0.14158 | -65.2343 | 57.4897 | 57.6446 | 57.6111 | -65.7328 | -0.18218 | -0.034563 | 0.10936 | 0.11059 | 0.29277 | -0.17117 | 0.025923 | -0.37789 | -0.13361 | 0.28792 | 0.12063 | 0.49853 | 0.021285 | -0.012142 | 122.9436 | 122.807 | 123.0041 | 65.0633 | -123.1604 | 122.8446 | 122.9995 | 122.9661 | 65.2133 | -123.3561
737.2656 | 123.1842 | -65.3412 | 57.6141 | 0.04215 | -0.055471 | -0.0053737 | 0.04996 | -0.01061 | 0.058078 | 0.042884 | -0.0025767 | 0.0011204 | 0.0557 | 0.060656 | 0.057187 | -65.2364 | -0.2962 | -65.2306 | 57.5887 | 57.4659 | 57.6629 | -65.5325 | -65.0533 | -0.15074 | -65.216 | 57.4897 | 57.6492 | 57.6157 | -65.7237 | -0.19133 | -0.025408 | 0.10479 | 0.11059 | 0.30193 | -0.14827 | 0.048813 | -0.38247 | -0.12446 | 0.28793 | 0.12522 | 0.50768 | 0.035019 | 0.001592 | 122.9299 | 122.807 | 123.0041 | 65.045 | -123.1467 | 122.8309 | 122.9903 | 122.9569 | 65.1904 | -123.3378
738.2656 | 123.1842 | -65.3595 | 57.6508 | 0.04215 | -0.055471 | -0.0085787 | 0.052097 | -0.012747 | 0.058078 | 0.058145 | -0.0025767 | -0.0010156 | 0.053563 | 0.056383 | 0.056118 | -65.2272 | -0.2962 | -65.2214 | 57.6025 | 57.4842 | 57.6675 | -65.5188 | -65.0349 | -0.1599 | -65.2068 | 57.4988 | 57.6492 | 57.634 | -65.7191 | -0.15929 | -0.048294 | 0.13225 | 0.13806 | 0.29735 | -0.16658 | 0.016771 | -0.35958 | -0.15192 | 0.32455 | 0.15268 | 0.51226 | -0.001602 | -0.016715 | 122.962 | 122.8437 | 123.027 | 65.0633 | -123.1695 | 122.8583 | 123.0087 | 122.9935 | 65.1996 | -123.3698
739.2656 | 123.1796 | -65.3275 | 57.6279 | 0.026888 | -0.055471 | -0.0085787 | 0.048892 | -0.011679 | 0.058078 | 0.073406 | -0.0036447 | 0.0011204 | 0.0557 | 0.057451 | 0.057187 | -65.2181 | -0.30078 | -65.2123 | 57.6025 | 57.5025 | 57.6721 | -65.5096 | -65.0349 | -0.1599 | -65.1977 | 57.508 | 57.6675 | 57.6295 | -65.7008 | -0.18217 | -0.025406 | 0.10937 | 0.11517 | 0.29734 | -0.12538 | 0.044238 | -0.37331 | -0.11987 | 0.29251 | 0.1298 | 0.5031 | 0.0396 | 0.001594 | 122.9299 | 122.8299 | 122.9996 | 65.0267 | -123.1375 | 122.8354 | 122.9949 | 122.9569 | 65.1676 | -123.3286
740.2656 | 123.1064 | -65.3412 | 57.6599 | 0.057412 | -0.055471 | -0.0064417 | 0.04996 | -0.013815 | 0.058078 | 0.058145 | -0.0047127 | 0.0021894 | 0.054631 | 0.061724 | 0.057187 | -65.1998 | -0.30536 | -65.2031 | 57.6162 | 57.4979 | 57.6858 | -65.5005 | -65.0212 | -0.1599 | -65.1977 | 57.5217 | 57.6766 | 57.6432 | -65.6962 | -0.15928 | -0.043714 | 0.14141 | 0.13806 | 0.29734 | -0.162 | 0.02593 | -0.35499 | -0.13818 | 0.31998 | 0.14353 | 0.49852 | 0.016715 | -0.016713 | 122.9574 | 122.8391 | 123.027 | 65.0358 | -123.1604 | 122.8629 | 123.0178 | 122.9844 | 65.1813 | -123.3561
741.2656 | 123.1613 | -65.3595 | 57.6874 | 0.04215 | -0.057608 | -0.0075097 | 0.051029 | -0.012747 | 0.055941 | 0.042884 | -0.0015087 | 0.0011204 | 0.054631 | 0.059588 | 0.05505 | -65.1906 | -0.30994 | -65.2031 | 57.6208 | 57.5162 | 57.695 | -65.4913 | -65.0212 | -0.16448 | -65.1793 | 57.5309 | 57.6766 | 57.6524 | -65.687 | -0.13181 | -0.066601 | 0.16888 | 0.15637 | 0.28819 | -0.17115 | 0.007622 | -0.32753 | -0.15649 | 0.33829 | 0.18016 | 0.50768 | -0.010751 | -0.035022 | 122.9803 | 122.8757 | 123.0545 | 65.0496 | -123.1787 | 122.8904 | 123.0361 | 123.0119 | 65.195 | -123.3744
742.2656 | 123.143 | -65.332 | 57.6599 | 0.057412 | -0.057608 | -0.0064417 | 0.04996 | -0.011679 | 0.05701 | 0.058145 | -0.0036447 | 0.0021894 | 0.054631 | 0.058519 | 0.057187 | -65.1906 | -0.30994 | -65.194 | 57.6299 | 57.5208 | 57.6996 | -65.4913 | -65.0075 | -0.1599 | -65.1702 | 57.5309 | 57.6949 | 57.6569 | -65.6824 | -0.15928 | -0.029979 | 0.14141 | 0.13806 | 0.29734 | -0.1391 | 0.039666 | -0.35041 | -0.12902 | 0.32456 | 0.16185 | 0.51226 | 0.035029 | -0.002977 | 122.962 | 122.8528 | 123.0316 | 65.0221 | -123.1512 | 122.8629 | 123.027 | 122.989 | 65.1721 | -123.3424
743.2656 | 123.1522 | -65.332 | 57.6691 | 0.04215 | -0.057608 | -0.0075097 | 0.048892 | -0.012747 | 0.058078 | 0.073406 | -0.0047127 | 0.0021894 | 0.052495 | 0.057451 | 0.057187 | -65.1906 | -0.30536 | -65.1848 | 57.6254 | 57.5208 | 57.7087 | -65.4776 | -64.9983 | -0.17363 | -65.1656 | 57.5355 | 57.6995 | 57.6661 | -65.6779 | -0.14554 | -0.043712 | 0.14141 | 0.14722 | 0.29276 | -0.14826 | 0.039668 | -0.34583 | -0.1336 | 0.33371 | 0.16643 | 0.51226 | 0.030453 | -0.002975 | 122.9574 | 122.8528 | 123.0408 | 65.0267 | -123.1466 | 122.8675 | 123.0316 | 122.9981 | 65.1584 | -123.3469
744.2656 | 123.175 | -65.3183 | 57.6508 | 0.057412 | -0.057608 | -0.0075097 | 0.048892 | -0.011679 | 0.055941 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.056768 | 0.059588 | 0.056118 | -65.1723 | -0.31452 | -65.1848 | 57.6345 | 57.5117 | 57.7133 | -65.4776 | -64.9983 | -0.17821 | -65.1564 | 57.54 | 57.7133 | 57.6707 | -65.6779 | -0.15928 | -0.016245 | 0.14599 | 0.13349 | 0.29276 | -0.13911 | 0.062557 | -0.35957 | -0.11071 | 0.31998 | 0.16185 | 0.52142 | 0.062498 | 0.019914 | 122.9528 | 122.8299 | 123.0316 | 65.0038 | -123.1283 | 122.8583 | 123.0316 | 122.989 | 65.1401 | -123.3286
745.2656 | 123.1705 | -65.2954 | 57.7057 | 0.072674 | -0.05654 | -0.0075097 | 0.04996 | -0.01061 | 0.055941 | 0.073406 | -0.0047127 | 0.0021894 | 0.054631 | 0.059588 | 0.05505 | -65.1723 | -0.3191 | -65.1711 | 57.6528 | 57.5162 | 57.7179 | -65.473 | -64.9892 | -0.17821 | -65.1473 | 57.5538 | 57.7178 | 57.689 | -65.6595 | -0.17758 | -0.052863 | 0.12311 | 0.12433 | 0.30192 | -0.18946 | 0.012205 | -0.36414 | -0.15191 | 0.30625 | 0.14812 | 0.51226 | 0.012146 | -0.016703 | 122.9482 | 122.8116 | 123.0133 | 64.9763 | -123.1787 | 122.8492 | 123.0132 | 122.9844 | 65.1172 | -123.3652
746.2656 | 123.1384 | -65.3046 | 57.7286 | 0.04215 | -0.05654 | -0.0064417 | 0.04996 | -0.0095417 | 0.055941 | 0.042884 | -0.0047127 | 0.0011204 | 0.054631 | 0.058519 | 0.05505 | -65.1723 | -0.3191 | -65.1573 | 57.6528 | 57.5208 | 57.7362 | -65.4638 | -64.98 | -0.18279 | -65.1427 | 57.5629 | 57.7133 | 57.689 | -65.655 | -0.15927 | -0.075752 | 0.13226 | 0.14722 | 0.3065 | -0.20777 | 0.00763 | -0.35041 | -0.16564 | 0.32456 | 0.16185 | 0.51226 | -0.015322 | -0.039592 | 122.9574 | 122.8254 | 123.0408 | 64.9855 | -123.1924 | 122.8675 | 123.0178 | 122.9935 | 65.1218 | -123.3835
747.2656 | 123.1522 | -65.2954 | 57.7011 | 0.057412 | -0.057608 | -0.0085787 | 0.04996 | -0.012747 | 0.055941 | 0.058145 | -0.0047127 | 0.0021894 | 0.052495 | 0.057451 | 0.05505 | -65.1494 | -0.31452 | -65.1573 | 57.6574 | 57.53 | 57.7316 | -65.4593 | -64.9754 | -0.19195 | -65.1473 | 57.5675 | 57.7133 | 57.6936 | -65.6504 | -0.16385 | -0.043707 | 0.146 | 0.13807 | 0.30192 | -0.17114 | 0.030517 | -0.35498 | -0.1336 | 0.31999 | 0.14812 | 0.5031 | 0.012144 | -0.007547 | 122.9528 | 122.8254 | 123.027 | 64.9809 | -123.1604 | 122.8629 | 123.0087 | 122.989 | 65.1035 | -123.3515
748.2656 | 123.1613 | -65.2771 | 57.724 | 0.057412 | -0.055471 | -0.0085787 | 0.04996 | -0.011679 | 0.05701 | 0.058145 | -0.0047127 | 0.0021894 | 0.054631 | 0.057451 | 0.058255 | -65.1448 | -0.3191 | -65.1528 | 57.662 | 57.5254 | 57.7316 | -65.4547 | -64.9617 | -0.2011 | -65.1336 | 57.5675 | 57.727 | 57.6981 | -65.6504 | -0.17758 | -0.062017 | 0.13227 | 0.12434 | 0.30192 | -0.19861 | 0.007629 | -0.37329 | -0.15648 | 0.31541 | 0.14355 | 0.51684 | 0.002992 | -0.025857 | 122.9391 | 122.8025 | 123.0087 | 64.958 | -123.1787 | 122.8446 | 123.0041 | 122.9752 | 65.076 | -123.3744
749.2656 | 123.1384 | -65.2863 | 57.7057 | 0.057412 | -0.055471 | -0.0085787 | 0.047824 | -0.012747 | 0.05701 | 0.058145 | -0.0068487 | 0.0011204 | 0.053563 | 0.059588 | 0.056118 | -65.1448 | -0.33283 | -65.1528 | 57.6757 | 57.5574 | 57.7408 | -65.4547 | -64.9525 | -0.20568 | -65.1244 | 57.5767 | 57.7316 | 57.7027 | -65.6458 | -0.16842 | -0.029971 | 0.14142 | 0.13349 | 0.30192 | -0.14825 | 0.035098 | -0.35956 | -0.12902 | 0.33373 | 0.16186 | 0.52142 | 0.025882 | -0.002967 | 122.962 | 122.8437 | 123.027 | 64.9534 | -123.1604 | 122.8629 | 123.0178 | 122.989 | 65.0806 | -123.3515
750.2656 | 123.1567 | -65.2542 | 57.7057 | 0.072674 | -0.05654 | -0.0064417 | 0.04996 | -0.012747 | 0.058078 | 0.058145 | -0.0047127 | 0.0021894 | 0.0557 | 0.058519 | 0.056118 | -65.1357 | -0.32367 | -65.139 | 57.6711 | 57.5483 | 57.7499 | -65.4409 | -64.9571 | -0.21484 | -65.1152 | 57.5813 | 57.7407 | 57.7073 | -65.6367 | -0.18673 | -0.034549 | 0.11853 | 0.11518 | 0.30191 | -0.15741 | 0.044255 | -0.38245 | -0.12444 | 0.2971 | 0.13897 | 0.52142 | 0.035039 | 0.001612 | 122.9253 | 122.8025 | 123.0042 | 64.9305 | -123.1466 | 122.8355 | 122.9949 | 122.9615 | 65.0394 | -123.3423
751.2656 | 123.1659 | -65.2588 | 57.7194 | 0.026888 | -0.05654 | -0.0075097 | 0.04996 | -0.011679 | 0.05701 | 0.027623 | -0.0036447 | 5.2373e-05 | 0.0557 | 0.058519 | 0.057187 | -65.1311 | -0.32825 | -65.139 | 57.6711 | 57.5666 | 57.7545 | -65.4409 | -64.948 | -0.21942 | -65.1152 | 57.5858 | 57.7453 | 57.7119 | -65.6367 | -0.18215 | -0.048282 | 0.12769 | 0.11976 | 0.30191 | -0.15282 | 0.0351 | -0.37787 | -0.13359 | 0.31084 | 0.14355 | 0.52142 | 0.025885 | -0.007543 | 122.9299 | 122.8254 | 123.0133 | 64.9305 | -123.1604 | 122.8446 | 123.0041 | 122.9707 | 65.0394 | -123.3561
752.2656 | 123.1338 | -65.2588 | 57.7057 | 0.026888 | -0.055471 | -0.0064417 | 0.04996 | -0.011679 | 0.054873 | 0.058145 | -0.0025767 | 0.0032574 | 0.054631 | 0.057451 | 0.056118 | -65.1219 | -0.32825 | -65.139 | 57.6895 | 57.6032 | 57.7637 | -65.4455 | -64.9434 | -0.21942 | -65.1107 | 57.5858 | 57.7453 | 57.721 | -65.6229 | -0.18673 | -0.016236 | 0.13685 | 0.11976 | 0.30649 | -0.10246 | 0.057991 | -0.36413 | -0.11986 | 0.31542 | 0.14813 | 0.51226 | 0.039618 | 0.015347 | 122.9482 | 122.862 | 123.0225 | 64.9305 | -123.1512 | 122.8446 | 123.0041 | 122.9798 | 65.0394 | -123.3286
753.2656 | 123.1567 | -65.2634 | 57.7286 | 0.072674 | -0.057608 | -0.0075097 | 0.04996 | -0.012747 | 0.058078 | 0.042884 | -0.0036447 | 0.0032574 | 0.0557 | 0.059588 | 0.05505 | -65.1128 | -0.33741 | -65.1253 | 57.6895 | 57.6215 | 57.7591 | -65.4318 | -64.9342 | -0.23316 | -65.1107 | 57.5904 | 57.7499 | 57.721 | -65.6275 | -0.16842 | -0.039125 | 0.15058 | 0.13807 | 0.30649 | -0.10703 | 0.030523 | -0.36413 | -0.13817 | 0.32915 | 0.15271 | 0.51684 | 0.021307 | -0.007542 | 122.9528 | 122.8849 | 123.0225 | 64.926 | -123.1604 | 122.8538 | 123.0133 | 122.9844 | 65.0302 | -123.3561
754.2656 | 123.2574 | -65.2267 | 57.6965 | 0.011626 | -0.057608 | -0.0085787 | 0.04996 | -0.011679 | 0.05701 | 0.058145 | -0.0036447 | 0.0021894 | 0.054631 | 0.058519 | 0.058255 | -65.1174 | -0.33283 | -65.1253 | 57.6986 | 57.6032 | 57.7683 | -65.4364 | -64.9342 | -0.23316 | -65.1061 | 57.5904 | 57.7636 | 57.721 | -65.6183 | -0.20962 | 0.002076 | 0.10938 | 0.10145 | 0.31107 | -0.093303 | 0.071724 | -0.39159 | -0.10613 | 0.29253 | 0.12066 | 0.51226 | 0.067087 | 0.024502 | 122.9254 | 122.83 | 122.995 | 64.8939 | -123.1329 | 122.8172 | 122.9904 | 122.9478 | 64.9936 | -123.3149
755.2656 | 123.262 | -65.2176 | 57.7057 | 0.04215 | -0.05654 | -0.0075097 | 0.048892 | -0.012747 | 0.054873 | 0.042884 | -0.0036447 | 0.0021894 | 0.0557 | 0.059588 | 0.058255 | -65.1082 | -0.33741 | -65.1207 | 57.6986 | 57.5895 | 57.7728 | -65.4226 | -64.9342 | -0.23773 | -65.1061 | 57.5996 | 57.759 | 57.7302 | -65.6138 | -0.20504 | -0.007079 | 0.10938 | 0.096875 | 0.30191 | -0.1162 | 0.067148 | -0.39617 | -0.10612 | 0.28337 | 0.11151 | 0.50768 | 0.053353 | 0.024505 | 122.9162 | 122.8071 | 122.9904 | 64.8802 | -123.1283 | 122.8172 | 122.9766 | 122.9478 | 64.9799 | -123.3194
756.2656 | 123.23 | -65.1993 | 57.7377 | 0.04215 | -0.059745 | -0.0075097 | 0.048892 | -0.012747 | 0.05701 | 0.042884 | -0.0036447 | 0.0021894 | 0.0557 | 0.058519 | 0.057187 | -65.0945 | -0.34199 | -65.1207 | 57.7078 | 57.6078 | 57.782 | -65.418 | -64.9342 | -0.24689 | -65.1015 | 57.6041 | 57.7636 | 57.7348 | -65.6183 | -0.21877 | -0.029966 | 0.10481 | 0.078565 | 0.29733 | -0.12992 | 0.044261 | -0.41906 | -0.13359 | 0.26506 | 0.097777 | 0.51684 | 0.025888 | -0.002961 | 122.907 | 122.8071 | 122.9813 | 64.8573 | -123.1558 | 122.8034 | 122.9629 | 122.9341 | 64.9524 | -123.3561
757.2656 | 123.2529 | -65.213 | 57.692 | 0.057412 | -0.05654 | -0.0064417 | 0.04996 | -0.011679 | 0.055941 | 0.073406 | -0.0036447 | 0.0032574 | 0.054631 | 0.057451 | 0.057187 | -65.0945 | -0.34199 | -65.1161 | 57.7078 | 57.5803 | 57.7774 | -65.418 | -64.9296 | -0.26063 | -65.0969 | 57.6179 | 57.7682 | 57.7302 | -65.6183 | -0.20503 | 0.01581 | 0.11854 | 0.096876 | 0.30191 | -0.11162 | 0.085458 | -0.40533 | -0.074077 | 0.28338 | 0.11609 | 0.52142 | 0.076243 | 0.038237 | 122.9208 | 122.7933 | 122.9904 | 64.871 | -123.11 | 122.8309 | 122.9812 | 122.9432 | 64.9524 | -123.3103
758.2656 | 123.2162 | -65.2176 | 57.7148 | 0.057412 | -0.058677 | -0.0085787 | 0.048892 | -0.012747 | 0.055941 | 0.088667 | -0.0036447 | 5.2373e-05 | 0.054631 | 0.059588 | 0.056118 | -65.0899 | -0.34199 | -65.107 | 57.7032 | 57.5987 | 57.782 | -65.4226 | -64.9296 | -0.26521 | -65.0923 | 57.6041 | 57.7682 | 57.7348 | -65.6092 | -0.20504 | -0.011656 | 0.1277 | 0.11061 | 0.31565 | -0.11619 | 0.067149 | -0.39159 | -0.1107 | 0.28795 | 0.12524 | 0.51684 | 0.053355 | 0.019927 | 122.9208 | 122.8162 | 122.9996 | 64.8756 | -123.1375 | 122.8217 | 122.9858 | 122.9524 | 64.9524 | -123.324
759.2656 | 123.23 | -65.2039 | 57.6965 | 0.011626 | -0.057608 | -0.0075097 | 0.04996 | -0.011679 | 0.05701 | 0.058145 | -0.0047127 | 0.0021894 | 0.054631 | 0.058519 | 0.057187 | -65.0945 | -0.34657 | -65.107 | 57.7123 | 57.5987 | 57.7774 | -65.4135 | -64.9205 | -0.26521 | -65.0878 | 57.6179 | 57.7728 | 57.7348 | -65.6046 | -0.20961 | 0.015811 | 0.10939 | 0.096877 | 0.30649 | -0.097882 | 0.080881 | -0.40075 | -0.078654 | 0.28338 | 0.11609 | 0.51684 | 0.076244 | 0.038238 | 122.9162 | 122.8025 | 122.9813 | 64.8573 | -123.11 | 122.8217 | 122.9766 | 122.9386 | 64.9387 | -123.3011
760.2656 | 123.2437 | -65.2176 | 57.692 | 0.072674 | -0.057608 | -0.0075097 | 0.051029 | -0.011679 | 0.05701 | 0.088667 | -0.0036447 | -0.0010156 | 0.0557 | 0.059588 | 0.057187 | -65.0899 | -0.34657 | -65.107 | 57.7078 | 57.5895 | 57.7912 | -65.4089 | -64.9159 | -0.26978 | -65.0832 | 57.6041 | 57.7728 | 57.7485 | -65.6046 | -0.1913 | 0.01581 | 0.1277 | 0.11061 | 0.30191 | -0.10246 | 0.099194 | -0.38701 | -0.087813 | 0.30169 | 0.1344 | 0.52142 | 0.080821 | 0.056551 | 122.9254 | 122.8071 | 123.0087 | 64.871 | -123.1008 | 122.8217 | 122.9904 | 122.9661 | 64.9478 | -123.2966
761.2656 | 123.4543 | -65.1718 | 57.7057 | 0.04215 | -0.058677 | -0.0053737 | 0.047824 | -0.011679 | 0.055941 | 0.042884 | -0.0057807 | 5.2373e-05 | 0.054631 | 0.058519 | 0.056118 | -65.0853 | -0.35572 | -65.1024 | 57.7123 | 57.5987 | 57.8003 | -65.4135 | -64.9159 | -0.27436 | -65.0878 | 57.6133 | 57.7728 | 57.7439 | -65.6092 | -0.24165 | 0.006656 | 0.0865 | 0.069412 | 0.31107 | -0.10704 | 0.094619 | -0.43737 | -0.092388 | 0.25591 | 0.084047 | 0.52142 | 0.067089 | 0.03824 | 122.8842 | 122.7705 | 122.9721 | 64.8161 | -123.1192 | 122.7851 | 122.9446 | 122.9157 | 64.8974 | -123.3149
762.2656 | 123.2346 | -65.213 | 57.7286 | 0.04215 | -0.057608 | -0.0096467 | 0.048892 | -0.01061 | 0.058078 | 0.042884 | -0.0036447 | 0.0021894 | 0.054631 | 0.058519 | 0.058255 | -65.0853 | -0.3603 | -65.1024 | 57.7078 | 57.6215 | 57.7866 | -65.4135 | -64.9159 | -0.2881 | -65.0832 | 57.6179 | 57.7774 | 57.7394 | -65.6 | -0.20045 | -0.020811 | 0.1277 | 0.11061 | 0.31107 | -0.10703 | 0.057995 | -0.38701 | -0.1107 | 0.29711 | 0.12982 | 0.51684 | 0.048779 | 0.010773 | 122.9208 | 122.8346 | 122.9996 | 64.8527 | -123.142 | 122.8309 | 122.9904 | 122.9524 | 64.9249 | -123.3286
763.2656 | 123.2803 | -65.1993 | 57.7148 | 0.057412 | -0.05654 | -0.0075097 | 0.048892 | -0.013815 | 0.055941 | 0.088667 | -0.0036447 | 0.0021894 | 0.054631 | 0.060656 | 0.057187 | -65.0716 | -0.35115 | -65.107 | 57.7078 | 57.6124 | 57.7866 | -65.4043 | -64.9205 | -0.2881 | -65.0786 | 57.6225 | 57.7819 | 57.7439 | -65.5954 | -0.20503 | -0.007078 | 0.1277 | 0.0923 | 0.29733 | -0.10246 | 0.071728 | -0.39617 | -0.092387 | 0.2788 | 0.12067 | 0.51684 | 0.06709 | 0.029084 | 122.907 | 122.8117 | 122.9859 | 64.8481 | -123.1192 | 122.8217 | 122.9812 | 122.9432 | 64.9112 | -123.3103
764.2656 | 123.2437 | -65.2039 | 57.7194 | 0.057412 | -0.05654 | -0.0075097 | 0.048892 | -0.011679 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.0557 | 0.058519 | 0.056118 | -65.0807 | -0.35115 | -65.0978 | 57.7169 | 57.6307 | 57.7912 | -65.4089 | -64.9022 | -0.29726 | -65.0832 | 57.6225 | 57.7819 | 57.7394 | -65.5909 | -0.20503 | -0.002498 | 0.12312 | 0.10603 | 0.31106 | -0.088718 | 0.071729 | -0.38701 | -0.096964 | 0.30169 | 0.12067 | 0.50768 | 0.062513 | 0.019929 | 122.9208 | 122.8346 | 122.995 | 64.8527 | -123.1283 | 122.8263 | 122.9858 | 122.9432 | 64.9066 | -123.3103
765.2656 | 123.2758 | -65.1993 | 57.724 | 0.087936 | -0.058677 | -0.0064417 | 0.046755 | -0.011679 | 0.059146 | 0.073406 | -0.0047127 | 0.0043254 | 0.054631 | 0.059588 | 0.05505 | -65.0807 | -0.37404 | -65.0978 | 57.7123 | 57.5941 | 57.7866 | -65.4089 | -64.9113 | -0.30184 | -65.0832 | 57.6225 | 57.7774 | 57.7485 | -65.6046 | -0.20961 | -0.011655 | 0.11854 | 0.10146 | 0.31106 | -0.12993 | 0.062573 | -0.40532 | -0.10154 | 0.28796 | 0.11609 | 0.52142 | 0.053357 | 0.024508 | 122.9116 | 122.7934 | 122.9859 | 64.8252 | -123.1329 | 122.8217 | 122.9766 | 122.9478 | 64.8974 | -123.3286
766.2656 | 123.2346 | -65.1901 | 57.7469 | 0.072674 | -0.057608 | -0.0075097 | 0.047824 | -0.011679 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.061724 | 0.058255 | -65.0716 | -0.36946 | -65.1024 | 57.7169 | 57.617 | 57.8003 | -65.4043 | -64.9113 | -0.30184 | -65.0786 | 57.6179 | 57.7774 | 57.7485 | -65.5954 | -0.21419 | -0.029964 | 0.11855 | 0.087723 | 0.30191 | -0.12992 | 0.05342 | -0.40532 | -0.12901 | 0.2788 | 0.11151 | 0.51684 | 0.030469 | 0.00162 | 122.907 | 122.8071 | 122.9904 | 64.8207 | -123.1512 | 122.808 | 122.9675 | 122.9386 | 64.8883 | -123.3423
767.2656 | 123.262 | -65.1993 | 57.7194 | 0.057412 | -0.057608 | -0.0064417 | 0.047824 | -0.01061 | 0.055941 | 0.088667 | -0.0036447 | 0.0021894 | 0.054631 | 0.058519 | 0.058255 | -65.0716 | -0.35572 | -65.0932 | 57.7169 | 57.5941 | 57.7957 | -65.4089 | -64.9159 | -0.31557 | -65.0832 | 57.6225 | 57.7819 | 57.7531 | -65.6 | -0.20961 | -0.002498 | 0.1277 | 0.10603 | 0.31564 | -0.12535 | 0.076308 | -0.40075 | -0.096964 | 0.28338 | 0.11609 | 0.51684 | 0.062513 | 0.033665 | 122.9162 | 122.7934 | 122.995 | 64.8436 | -123.1283 | 122.8217 | 122.9812 | 122.9524 | 64.8837 | -123.3194
768.2656 | 123.2162 | -65.213 | 57.7057 | 0.04215 | -0.057608 | -0.0075097 | 0.048892 | -0.012747 | 0.055941 | 0.073406 | -0.0036447 | 0.0021894 | 0.053563 | 0.061724 | 0.057187 | -65.067 | -0.36946 | -65.0978 | 57.7169 | 57.6215 | 57.7912 | -65.4043 | -64.9113 | -0.31557 | -65.0832 | 57.6179 | 57.7819 | 57.7485 | -65.6 | -0.1913 | 0.011235 | 0.14601 | 0.11519 | 0.30649 | -0.084143 | 0.085462 | -0.38701 | -0.087809 | 0.30169 | 0.12982 | 0.51684 | 0.076246 | 0.042819 | 122.9299 | 122.8346 | 123.0042 | 64.8436 | -123.11 | 122.8309 | 122.9949 | 122.9615 | 64.8974 | -123.3057
769.2656 | 123.2574 | -65.2222 | 57.7377 | 0.04215 | -0.059745 | -0.0085787 | 0.047824 | -0.011679 | 0.058078 | 0.027623 | -0.0025767 | 0.0011204 | 0.056768 | 0.060656 | 0.058255 | -65.067 | -0.37862 | -65.1024 | 57.7169 | 57.6307 | 57.7957 | -65.4043 | -64.9113 | -0.32015 | -65.0832 | 57.627 | 57.7819 | 57.7485 | -65.6 | -0.18214 | -0.020809 | 0.15517 | 0.11977 | 0.30191 | -0.10703 | 0.057997 | -0.37786 | -0.1107 | 0.31085 | 0.13898 | 0.51684 | 0.044202 | 0.010775 | 122.9391 | 122.8529 | 123.0179 | 64.8436 | -123.142 | 122.8492 | 123.0041 | 122.9707 | 64.902 | -123.3378
770.2656 | 123.23 | -65.2222 | 57.7194 | 0.026888 | -0.057608 | -0.0075097 | 0.048892 | -0.01061 | 0.055941 | 0.042884 | -0.0025767 | 0.0011204 | 0.054631 | 0.058519 | 0.056118 | -65.067 | -0.37862 | -65.1024 | 57.7169 | 57.617 | 57.7912 | -65.3997 | -64.9067 | -0.32931 | -65.0832 | 57.6179 | 57.7819 | 57.7394 | -65.5909 | -0.17756 | -0.002498 | 0.15517 | 0.11977 | 0.29733 | -0.10245 | 0.071729 | -0.3687 | -0.10154 | 0.31542 | 0.13898 | 0.50768 | 0.062513 | 0.019929 | 122.9391 | 122.8391 | 123.0133 | 64.8436 | -123.1192 | 122.84 | 123.0041 | 122.9615 | 64.8929 | -123.3103
771.2656 | 123.2162 | -65.2222 | 57.6965 | 0.04215 | -0.057608 | -0.0075097 | 0.047824 | -0.011679 | 0.055941 | 0.073406 | -0.0015087 | 0.0011204 | 0.053563 | 0.059588 | 0.057187 | -65.067 | -0.3832 | -65.0978 | 57.7261 | 57.5758 | 57.7912 | -65.3997 | -64.9022 | -0.32931 | -65.0786 | 57.6179 | 57.7865 | 57.7485 | -65.6092 | -0.17756 | 0.029547 | 0.15517 | 0.12434 | 0.30191 | -0.12078 | 0.094617 | -0.38702 | -0.078654 | 0.32 | 0.14356 | 0.53057 | 0.08998 | 0.051974 | 122.9482 | 122.7979 | 123.0133 | 64.839 | -123.0963 | 122.84 | 123.0087 | 122.9707 | 64.8929 | -123.3057
772.2656 | 123.1934 | -65.2176 | 57.7148 | 0.057412 | -0.05654 | -0.0085787 | 0.04996 | -0.011679 | 0.05701 | 0.027623 | -0.0036447 | 0.0011204 | 0.0557 | 0.059588 | 0.056118 | -65.0624 | -0.3832 | -65.0978 | 57.7123 | 57.5803 | 57.7912 | -65.4043 | -64.9159 | -0.34762 | -65.0786 | 57.627 | 57.7819 | 57.7531 | -65.6 | -0.18672 | -0.0025 | 0.15517 | 0.11977 | 0.30649 | -0.13451 | 0.076306 | -0.38244 | -0.087808 | 0.30169 | 0.13898 | 0.52142 | 0.06709 | 0.038242 | 122.9299 | 122.7979 | 123.0087 | 64.8344 | -123.1192 | 122.8446 | 122.9995 | 122.9707 | 64.87 | -123.3149
773.2656 | 123.2071 | -65.2313 | 57.7194 | 0.057412 | -0.058677 | -0.0085787 | 0.04996 | -0.012747 | 0.054873 | 0.027623 | -0.0047127 | 0.0021894 | 0.054631 | 0.059588 | 0.058255 | -65.067 | -0.3832 | -65.1024 | 57.7078 | 57.5803 | 57.7957 | -65.4043 | -64.9159 | -0.34762 | -65.0832 | 57.6179 | 57.7774 | 57.7439 | -65.6 | -0.17299 | -0.011655 | 0.16432 | 0.12892 | 0.30191 | -0.13909 | 0.076308 | -0.3687 | -0.10154 | 0.31542 | 0.14813 | 0.51684 | 0.057935 | 0.024507 | 122.9391 | 122.8117 | 123.0271 | 64.8481 | -123.1237 | 122.8492 | 123.0087 | 122.9753 | 64.8837 | -123.3194
774.2656 | 123.1338 | -65.2176 | 57.756 | 0.026888 | -0.058677 | -0.0085787 | 0.048892 | -0.012747 | 0.055941 | 0.058145 | -0.0015087 | 0.0011204 | 0.0557 | 0.060656 | 0.057187 | -65.0716 | -0.39693 | -65.0978 | 57.7078 | 57.5849 | 57.7866 | -65.4089 | -64.9205 | -0.35678 | -65.0832 | 57.6179 | 57.7819 | 57.7439 | -65.6138 | -0.1913 | -0.048276 | 0.14601 | 0.11977 | 0.31106 | -0.17113 | 0.03053 | -0.39617 | -0.13816 | 0.29711 | 0.1344 | 0.53057 | 0.025892 | -0.012114 | 122.9254 | 122.8025 | 123.0042 | 64.8207 | -123.1649 | 122.8355 | 122.9995 | 122.9615 | 64.8608 | -123.3698
775.2656 | 123.2574 | -65.2451 | 57.6736 | 0.026888 | -0.057608 | -0.0096467 | 0.04996 | -0.012747 | 0.058078 | 0.058145 | -0.0036447 | 0.0011204 | 0.052495 | 0.060656 | 0.057187 | -65.0624 | -0.39235 | -65.1024 | 57.7169 | 57.5803 | 57.7912 | -65.4043 | -64.9251 | -0.37052 | -65.0878 | 57.6179 | 57.7774 | 57.7394 | -65.6046 | -0.15925 | 0.043278 | 0.18263 | 0.14265 | 0.30191 | -0.09331 | 0.11751 | -0.35955 | -0.055766 | 0.32 | 0.15729 | 0.51684 | 0.10371 | 0.065705 | 122.962 | 122.8254 | 123.0362 | 64.8527 | -123.078 | 122.8629 | 123.0224 | 122.9844 | 64.8745 | -123.2782
776.2656 | 123.2529 | -65.2084 | 57.6874 | 0.04215 | -0.059745 | -0.0075097 | 0.048892 | -0.014884 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.054631 | 0.059588 | 0.057187 | -65.067 | -0.39235 | -65.1024 | 57.7123 | 57.5758 | 57.7866 | -65.4135 | -64.9205 | -0.37052 | -65.0832 | 57.6179 | 57.7819 | 57.7439 | -65.6092 | -0.20503 | 0.024966 | 0.14143 | 0.10603 | 0.31107 | -0.11162 | 0.099194 | -0.40075 | -0.069499 | 0.28796 | 0.12525 | 0.52599 | 0.094556 | 0.05655 | 122.9208 | 122.7842 | 122.995 | 64.8161 | -123.1008 | 122.8263 | 122.9904 | 122.9524 | 64.8379 | -123.2966
777.2656 | 123.2529 | -65.213 | 57.6874 | 0.04215 | -0.060813 | -0.0096467 | 0.048892 | -0.014884 | 0.055941 | 0.042884 | -0.0057807 | -0.0010156 | 0.0557 | 0.057451 | 0.057187 | -65.0624 | -0.39693 | -65.1024 | 57.7169 | 57.5758 | 57.782 | -65.4089 | -64.9205 | -0.37967 | -65.0832 | 57.6225 | 57.7819 | 57.7394 | -65.6 | -0.19588 | 0.029545 | 0.15059 | 0.11061 | 0.30649 | -0.11162 | 0.094615 | -0.38701 | -0.064921 | 0.29253 | 0.12982 | 0.51684 | 0.094556 | 0.051972 | 122.9299 | 122.7888 | 122.995 | 64.8161 | -123.0963 | 122.8355 | 122.9949 | 122.9524 | 64.8333 | -123.2874
778.2656 | 123.2391 | -65.1993 | 57.7103 | 0.04215 | -0.059745 | -0.0075097 | 0.047824 | -0.012747 | 0.05701 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.053563 | 0.059588 | 0.056118 | -65.0624 | -0.40151 | -65.107 | 57.7169 | 57.5758 | 57.7866 | -65.418 | -64.9205 | -0.38425 | -65.0832 | 57.6133 | 57.7819 | 57.7439 | -65.6 | -0.21877 | 0.006657 | 0.13686 | 0.0923 | 0.31107 | -0.13451 | 0.076306 | -0.40075 | -0.096966 | 0.2788 | 0.11609 | 0.51684 | 0.071668 | 0.033662 | 122.9162 | 122.775 | 122.9859 | 64.7978 | -123.1283 | 122.8126 | 122.9812 | 122.9432 | 64.815 | -123.3103
779.2656 | 123.143 | -65.2267 | 57.7652 | 0.04215 | -0.058677 | -0.0085787 | 0.048892 | -0.012747 | 0.058078 | 0.073406 | -0.0015087 | 0.0011204 | 0.0557 | 0.058519 | 0.05505 | -65.0624 | -0.41067 | -65.107 | 57.7123 | 57.5895 | 57.7774 | -65.4043 | -64.9251 | -0.38883 | -65.0832 | 57.6179 | 57.7728 | 57.7394 | -65.6046 | -0.17756 | -0.052854 | 0.16432 | 0.11977 | 0.29733 | -0.17571 | 0.012216 | -0.37786 | -0.14732 | 0.30169 | 0.14356 | 0.52142 | 0.007579 | -0.025848 | 122.9391 | 122.8162 | 123.0042 | 64.8161 | -123.1695 | 122.8446 | 122.9995 | 122.9661 | 64.8379 | -123.3698
780.2656 | 123.2529 | -65.2084 | 57.6782 | 0.057412 | -0.059745 | -0.0053737 | 0.048892 | -0.012747 | 0.05701 | 0.073406 | -0.0036447 | 0.0011204 | 0.054631 | 0.060656 | 0.056118 | -65.0624 | -0.40609 | -65.1024 | 57.7078 | 57.5803 | 57.7774 | -65.4226 | -64.9296 | -0.39341 | -65.0832 | 57.6133 | 57.7774 | 57.7439 | -65.6092 | -0.21419 | 0.029543 | 0.14601 | 0.10603 | 0.32022 | -0.097888 | 0.099191 | -0.40075 | -0.064923 | 0.2788 | 0.12525 | 0.52599 | 0.099133 | 0.065705 | 122.9162 | 122.7888 | 122.9858 | 64.8023 | -123.1008 | 122.8217 | 122.9858 | 122.9524 | 64.815 | -123.2874
781.2656 | 123.2437 | -65.2359 | 57.6782 | 0.026888 | -0.059745 | -0.0096467 | 0.048892 | -0.013815 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.054631 | 0.061724 | 0.05505 | -65.067 | -0.40609 | -65.107 | 57.7078 | 57.5849 | 57.7866 | -65.4135 | -64.9296 | -0.39799 | -65.0878 | 57.6133 | 57.7728 | 57.7302 | -65.6 | -0.17757 | 0.029543 | 0.1689 | 0.12892 | 0.30649 | -0.093309 | 0.10835 | -0.36412 | -0.064923 | 0.30626 | 0.14813 | 0.51226 | 0.094554 | 0.05197 | 122.9437 | 122.8208 | 123.0225 | 64.8298 | -123.0917 | 122.8492 | 123.0087 | 122.9661 | 64.8379 | -123.2782
782.2656 | 123.1659 | -65.2634 | 57.7194 | 0.026888 | -0.060813 | -0.0085787 | 0.04996 | -0.012747 | 0.055941 | 0.042884 | -0.0047127 | 0.0021894 | 0.054631 | 0.058519 | 0.056118 | -65.0624 | -0.41983 | -65.107 | 57.7123 | 57.5666 | 57.7774 | -65.4089 | -64.9251 | -0.41173 | -65.0923 | 57.6179 | 57.7728 | 57.7348 | -65.6046 | -0.14552 | -0.007077 | 0.20095 | 0.15639 | 0.30191 | -0.15282 | 0.057993 | -0.34124 | -0.10154 | 0.33831 | 0.17102 | 0.51226 | 0.053356 | 0.01535 | 122.9757 | 122.83 | 123.0408 | 64.8435 | -123.1283 | 122.8812 | 123.0361 | 122.9981 | 64.8516 | -123.324
783.2656 | 123.175 | -65.2679 | 57.7057 | 0.04215 | -0.058677 | -0.0085787 | 0.04996 | -0.013815 | 0.058078 | 0.058145 | -0.0057807 | 0.0021894 | 0.053563 | 0.061724 | 0.056118 | -65.067 | -0.4244 | -65.1024 | 57.6986 | 57.5849 | 57.7774 | -65.418 | -64.9342 | -0.42088 | -65.0878 | 57.6041 | 57.7682 | 57.7439 | -65.6092 | -0.1501 | -0.007079 | 0.20094 | 0.16554 | 0.31565 | -0.12077 | 0.071726 | -0.34124 | -0.10155 | 0.33373 | 0.18018 | 0.52142 | 0.062511 | 0.03824 | 122.9666 | 122.8529 | 123.0454 | 64.8435 | -123.1237 | 122.8721 | 123.0361 | 123.0119 | 64.8471 | -123.3149
784.2656 | 123.23 | -65.2267 | 57.6874 | 0.04215 | -0.059745 | -0.0085787 | 0.048892 | -0.011679 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.053563 | 0.061724 | 0.057187 | -65.0716 | -0.42898 | -65.0978 | 57.7078 | 57.5803 | 57.7728 | -65.4226 | -64.9342 | -0.42088 | -65.0878 | 57.6087 | 57.7728 | 57.7302 | -65.6138 | -0.19588 | 0.020388 | 0.15517 | 0.12892 | 0.3248 | -0.10704 | 0.085458 | -0.38702 | -0.078656 | 0.29253 | 0.13898 | 0.52599 | 0.085399 | 0.042815 | 122.9345 | 122.8071 | 122.9996 | 64.7978 | -123.11 | 122.8355 | 122.9995 | 122.9569 | 64.8059 | -123.3011
785.2656 | 123.1613 | -65.2176 | 57.6828 | 0.026888 | -0.059745 | -0.0085787 | 0.048892 | -0.014884 | 0.055941 | 0.058145 | -0.0025767 | 0.0032574 | 0.054631 | 0.061724 | 0.057187 | -65.0624 | -0.42898 | -65.1161 | 57.7032 | 57.5758 | 57.7774 | -65.4226 | -64.9388 | -0.43004 | -65.0923 | 57.6041 | 57.7682 | 57.7302 | -65.6183 | -0.20504 | 0.020388 | 0.15517 | 0.10145 | 0.30649 | -0.10704 | 0.094614 | -0.40075 | -0.078657 | 0.2788 | 0.12524 | 0.52599 | 0.085399 | 0.047393 | 122.9208 | 122.7933 | 122.995 | 64.7886 | -123.1054 | 122.8217 | 122.9858 | 122.9478 | 64.7875 | -123.3011
786.2656 | 123.1659 | -65.2725 | 57.7286 | 0.026888 | -0.058677 | -0.0064417 | 0.04996 | -0.012747 | 0.054873 | 0.042884 | -0.0036447 | 0.0021894 | 0.0557 | 0.062793 | 0.057187 | -65.067 | -0.42898 | -65.1161 | 57.7032 | 57.6078 | 57.7774 | -65.4318 | -64.9525 | -0.43462 | -65.0969 | 57.5996 | 57.7682 | 57.7302 | -65.6229 | -0.15926 | -0.025389 | 0.20552 | 0.15639 | 0.31565 | -0.12077 | 0.048837 | -0.3504 | -0.12901 | 0.31999 | 0.1756 | 0.52599 | 0.039622 | 0.001616 | 122.9757 | 122.8803 | 123.0499 | 64.8435 | -123.1604 | 122.8721 | 123.0407 | 123.0027 | 64.8379 | -123.3515
787.2656 | 123.1705 | -65.2908 | 57.6965 | 0.057412 | -0.059745 | -0.0085787 | 0.048892 | -0.012747 | 0.05701 | 0.042884 | -0.0036447 | 0.0021894 | 0.054631 | 0.062793 | 0.057187 | -65.0716 | -0.43814 | -65.1116 | 57.7032 | 57.5758 | 57.7774 | -65.4226 | -64.948 | -0.4392 | -65.0969 | 57.595 | 57.7682 | 57.7256 | -65.6229 | -0.13179 | 0.006655 | 0.21925 | 0.17927 | 0.31107 | -0.12078 | 0.080881 | -0.33209 | -0.10155 | 0.34288 | 0.19391 | 0.52599 | 0.071666 | 0.029081 | 122.994 | 122.8666 | 123.0682 | 64.8527 | -123.1192 | 122.8858 | 123.059 | 123.0164 | 64.8516 | -123.3195
788.2656 | 123.1155 | -65.2863 | 57.7148 | 0.04215 | -0.059745 | -0.0096467 | 0.04996 | -0.011679 | 0.054873 | 0.058145 | -0.0025767 | 0.0032574 | 0.053563 | 0.061724 | 0.057187 | -65.0716 | -0.44272 | -65.1207 | 57.6849 | 57.5666 | 57.7774 | -65.4272 | -64.948 | -0.45293 | -65.0969 | 57.5996 | 57.7636 | 57.721 | -65.6183 | -0.14095 | -0.02997 | 0.21468 | 0.16554 | 0.30649 | -0.14825 | 0.06257 | -0.33209 | -0.11528 | 0.3383 | 0.18933 | 0.52142 | 0.048776 | 0.006191 | 122.9711 | 122.8529 | 123.0637 | 64.8435 | -123.142 | 122.8858 | 123.0499 | 123.0073 | 64.8333 | -123.3332
789.2656 | 123.2391 | -65.2176 | 57.6874 | 0.072674 | -0.061882 | -0.0053737 | 0.04996 | -0.012747 | 0.05701 | 0.058145 | -0.0047127 | 0.0021894 | 0.0557 | 0.062793 | 0.056118 | -65.0807 | -0.4473 | -65.1207 | 57.694 | 57.5574 | 57.7683 | -65.4272 | -64.9525 | -0.45751 | -65.1152 | 57.5996 | 57.7545 | 57.7256 | -65.6275 | -0.20961 | 0.006653 | 0.13685 | 0.096875 | 0.30649 | -0.12994 | 0.080879 | -0.40991 | -0.087813 | 0.26506 | 0.10235 | 0.51226 | 0.067085 | 0.038236 | 122.9116 | 122.775 | 122.9858 | 64.7703 | -123.1146 | 122.8172 | 122.9721 | 122.9432 | 64.7601 | -123.3149
790.2656 | 123.1613 | -65.2679 | 57.724 | 0.04215 | -0.060813 | -0.0096467 | 0.046755 | -0.012747 | 0.05701 | 0.073406 | -0.0036447 | 0.0021894 | 0.052495 | 0.063861 | 0.05505 | -65.0716 | -0.45188 | -65.1161 | 57.6895 | 57.5712 | 57.7637 | -65.4364 | -64.9617 | -0.47125 | -65.1061 | 57.5996 | 57.7499 | 57.7256 | -65.6275 | -0.16842 | -0.034547 | 0.19637 | 0.15181 | 0.32023 | -0.15282 | 0.03968 | -0.35955 | -0.12443 | 0.30626 | 0.16186 | 0.52142 | 0.025885 | 0.001615 | 122.9574 | 122.8391 | 123.0316 | 64.8161 | -123.1604 | 122.8675 | 123.0178 | 122.9936 | 64.7967 | -123.3515
791.2656 | 123.1384 | -65.2771 | 57.7057 | 0.057412 | -0.059745 | -0.0085787 | 0.04996 | -0.013815 | 0.05701 | 0.058145 | -0.0047127 | 0.0011204 | 0.0557 | 0.063861 | 0.057187 | -65.0807 | -0.46103 | -65.1207 | 57.6895 | 57.562 | 57.7683 | -65.4409 | -64.9617 | -0.47583 | -65.1107 | 57.5904 | 57.7499 | 57.7165 | -65.6321 | -0.16384 | -0.016236 | 0.19636 | 0.15639 | 0.32023 | -0.14367 | 0.062569 | -0.35498 | -0.11528 | 0.31541 | 0.16644 | 0.52142 | 0.044196 | 0.010769 | 122.9666 | 122.8391 | 123.0454 | 64.8161 | -123.1466 | 122.8675 | 123.027 | 122.9936 | 64.8013 | -123.3378
792.2656 | 123.1155 | -65.2863 | 57.6874 | 0.04215 | -0.059745 | -0.0096467 | 0.04996 | -0.013815 | 0.055941 | 0.058145 | -0.0057807 | 5.2373e-05 | 0.054631 | 0.060656 | 0.056118 | -65.0853 | -0.46103 | -65.1299 | 57.6895 | 57.562 | 57.7683 | -65.4409 | -64.9708 | -0.48041 | -65.1198 | 57.5904 | 57.7545 | 57.7119 | -65.6412 | -0.15469 | 0.002074 | 0.20094 | 0.15638 | 0.31107 | -0.12536 | 0.080879 | -0.35498 | -0.09697 | 0.31541 | 0.16644 | 0.52142 | 0.067085 | 0.0245 | 122.9757 | 122.8483 | 123.0545 | 64.8252 | -123.1283 | 122.8767 | 123.0407 | 122.9981 | 64.8058 | -123.3286
793.2656 | 123.1567 | -65.2771 | 57.692 | 0.057412 | -0.059745 | -0.0085787 | 0.047824 | -0.013815 | 0.054873 | 0.042884 | -0.0047127 | 0.0011204 | 0.053563 | 0.061724 | 0.056118 | -65.0899 | -0.45645 | -65.1345 | 57.6849 | 57.5941 | 57.7591 | -65.4501 | -64.9708 | -0.48956 | -65.1198 | 57.5813 | 57.7499 | 57.7165 | -65.6367 | -0.173 | -0.007082 | 0.18721 | 0.14265 | 0.31565 | -0.097884 | 0.067144 | -0.35956 | -0.1107 | 0.30626 | 0.15728 | 0.51684 | 0.057928 | 0.024501 | 122.962 | 122.8712 | 123.0362 | 64.8206 | -123.1421 | 122.8584 | 123.027 | 122.9936 | 64.7875 | -123.3286
794.2656 | 123.2529 | -65.2588 | 57.637 | 0.026888 | -0.059745 | -0.0085787 | 0.047824 | -0.012747 | 0.05701 | 0.073406 | -0.0036447 | 0.0011204 | 0.054631 | 0.061724 | 0.058255 | -65.0853 | -0.46561 | -65.1345 | 57.6803 | 57.6215 | 57.7545 | -65.4501 | -64.9617 | -0.48956 | -65.1244 | 57.5904 | 57.7407 | 57.7073 | -65.6458 | -0.19131 | 0.043272 | 0.17347 | 0.12434 | 0.31565 | -0.015479 | 0.1175 | -0.38702 | -0.046616 | 0.2971 | 0.13439 | 0.52142 | 0.1037 | 0.070276 | 122.9391 | 122.8803 | 123.0133 | 64.7932 | -123.0871 | 122.8492 | 122.9995 | 122.9661 | 64.7692 | -123.2828
795.2656 | 123.1888 | -65.3 | 57.7057 | 0.072674 | -0.059745 | -0.0096467 | 0.051029 | -0.011679 | 0.05701 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.053563 | 0.061724 | 0.057187 | -65.0853 | -0.47935 | -65.1345 | 57.6849 | 57.6124 | 57.7545 | -65.4547 | -64.9846 | -0.51246 | -65.129 | 57.5767 | 57.7407 | 57.7119 | -65.6367 | -0.15469 | -0.020814 | 0.21467 | 0.16554 | 0.32023 | -0.0933 | 0.048833 | -0.33667 | -0.12902 | 0.31541 | 0.17101 | 0.50768 | 0.035039 | 0.00619 | 122.9849 | 122.9124 | 123.0545 | 64.8206 | -123.1604 | 122.8767 | 123.0407 | 123.0119 | 64.7875 | -123.3423
796.2656 | 123.1888 | -65.2771 | 57.7148 | 0.04215 | -0.060813 | -0.0075097 | 0.048892 | -0.012747 | 0.05701 | 0.073406 | -0.0036447 | 5.2373e-05 | 0.052495 | 0.061724 | 0.056118 | -65.0899 | -0.48392 | -65.139 | 57.6757 | 57.562 | 57.7499 | -65.4501 | -64.9892 | -0.51246 | -65.1336 | 57.5721 | 57.7361 | 57.7027 | -65.6504 | -0.173 | -0.039127 | 0.18721 | 0.13807 | 0.31107 | -0.15282 | 0.035099 | -0.37329 | -0.14275 | 0.28794 | 0.14355 | 0.51684 | 0.021304 | -0.012123 | 122.9528 | 122.8391 | 123.027 | 64.7932 | -123.1649 | 122.8492 | 123.0132 | 122.9798 | 64.7646 | -123.3652
797.2656 | 123.1522 | -65.3046 | 57.7057 | 0.04215 | -0.060813 | -0.0075097 | 0.048892 | -0.013815 | 0.054873 | 0.073406 | -0.0025767 | 0.0021894 | 0.052495 | 0.062793 | 0.05505 | -65.0853 | -0.49308 | -65.1436 | 57.6757 | 57.5483 | 57.7499 | -65.4593 | -64.9846 | -0.53077 | -65.1381 | 57.5767 | 57.727 | 57.7027 | -65.655 | -0.15469 | -0.029971 | 0.21925 | 0.16096 | 0.31565 | -0.15741 | 0.044255 | -0.35041 | -0.12902 | 0.31998 | 0.16643 | 0.51684 | 0.021303 | -0.002967 | 122.9803 | 122.8528 | 123.0545 | 64.8115 | -123.1649 | 122.8812 | 123.0316 | 123.0073 | 64.7738 | -123.3607
798.2656 | 123.175 | -65.2954 | 57.7103 | 0.057412 | -0.061882 | -0.0075097 | 0.047824 | -0.014884 | 0.055941 | 0.073406 | -0.0036447 | 0.0021894 | 0.052495 | 0.064929 | 0.056118 | -65.099 | -0.49308 | -65.139 | 57.6757 | 57.53 | 57.7454 | -65.4638 | -64.9846 | -0.53535 | -65.1381 | 57.5675 | 57.7316 | 57.6981 | -65.655 | -0.16843 | -0.034549 | 0.19636 | 0.15638 | 0.32481 | -0.1803 | 0.035098 | -0.35956 | -0.14275 | 0.31083 | 0.15728 | 0.51684 | 0.021304 | -0.012124 | 122.9711 | 122.8254 | 123.0408 | 64.8023 | -123.1741 | 122.8629 | 123.027 | 122.9936 | 64.7601 | -123.3652
799.2656 | 123.2803 | -65.3046 | 57.6462 | 0.026888 | -0.061882 | -0.0085787 | 0.048892 | -0.012747 | 0.054873 | 0.042884 | -0.0047127 | 0.0021894 | 0.0557 | 0.063861 | 0.057187 | -65.099 | -0.48392 | -65.139 | 57.662 | 57.5208 | 57.7408 | -65.4593 | -64.9892 | -0.54451 | -65.1473 | 57.5675 | 57.7316 | 57.689 | -65.6504 | -0.15469 | 0.015803 | 0.20552 | 0.16554 | 0.32023 | -0.12537 | 0.094607 | -0.34583 | -0.078664 | 0.3154 | 0.15727 | 0.5031 | 0.085391 | 0.042806 | 122.9665 | 122.8254 | 123.0454 | 64.8206 | -123.1054 | 122.8721 | 123.0361 | 122.9935 | 64.7601 | -123.2966
800.2656 | 123.1796 | -65.3 | 57.6874 | 0.057412 | -0.06295 | -0.0096467 | 0.04996 | -0.014884 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.054631 | 0.063861 | 0.05505 | -65.1036 | -0.49766 | -65.1528 | 57.6666 | 57.5529 | 57.7362 | -65.4638 | -64.9983 | -0.55366 | -65.1427 | 57.5629 | 57.7224 | 57.689 | -65.6595 | -0.16385 | -0.020817 | 0.19636 | 0.14723 | 0.31107 | -0.13452 | 0.048829 | -0.35956 | -0.12444 | 0.30167 | 0.15728 | 0.51684 | 0.035035 | 0.001607 | 122.9665 | 122.8528 | 123.0362 | 64.8023 | -123.1512 | 122.8629 | 123.0224 | 122.989 | 64.7463 | -123.3469
801.2656 | 123.1293 | -65.3046 | 57.6782 | 0.057412 | -0.064018 | -0.0075097 | 0.051029 | -0.012747 | 0.058078 | 0.073406 | -0.0036447 | 0.0011204 | 0.054631 | 0.062793 | 0.056118 | -65.1036 | -0.50224 | -65.1573 | 57.6711 | 57.5529 | 57.7316 | -65.473 | -65.0029 | -0.55366 | -65.1519 | 57.5584 | 57.7224 | 57.689 | -65.6687 | -0.16843 | -0.007084 | 0.20094 | 0.14722 | 0.31565 | -0.12536 | 0.053405 | -0.36414 | -0.11987 | 0.30167 | 0.1527 | 0.51684 | 0.04419 | 0.010762 | 122.9757 | 122.8574 | 123.0362 | 64.8023 | -123.1512 | 122.8629 | 123.027 | 122.9935 | 64.7509 | -123.3469
802.2656 | 123.1522 | -65.3 | 57.6828 | 0.04215 | -0.061882 | -0.0064417 | 0.047824 | -0.011679 | 0.058078 | 0.073406 | -0.0036447 | 0.0011204 | 0.053563 | 0.062793 | 0.05505 | -65.1036 | -0.5114 | -65.1528 | 57.6574 | 57.5391 | 57.7362 | -65.4776 | -65.0075 | -0.57656 | -65.1519 | 57.5492 | 57.7178 | 57.6798 | -65.6641 | -0.17759 | -0.025396 | 0.19636 | 0.14723 | 0.32481 | -0.14368 | 0.053407 | -0.36414 | -0.1336 | 0.29251 | 0.14812 | 0.51226 | 0.035034 | -0.002972 | 122.9574 | 122.8391 | 123.0362 | 64.7886 | -123.1604 | 122.8492 | 123.0178 | 122.9798 | 64.7234 | -123.3469
803.2656 | 123.1613 | -65.3229 | 57.6828 | 0.057412 | -0.061882 | -0.0075097 | 0.047824 | -0.012747 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.0557 | 0.065998 | 0.053982 | -65.1128 | -0.51598 | -65.1711 | 57.6528 | 57.5712 | 57.7316 | -65.4822 | -65.0166 | -0.57656 | -65.1656 | 57.5538 | 57.7178 | 57.6798 | -65.6733 | -0.15928 | -0.029975 | 0.21009 | 0.1518 | 0.31108 | -0.11162 | 0.048828 | -0.35041 | -0.12902 | 0.30624 | 0.15727 | 0.50768 | 0.035034 | -0.002972 | 122.9757 | 122.8941 | 123.0545 | 64.8069 | -123.165 | 122.8767 | 123.0407 | 123.0027 | 64.7463 | -123.3561
804.2656 | 123.1888 | -65.3046 | 57.6508 | 0.04215 | -0.06295 | -0.0075097 | 0.046755 | -0.014884 | 0.058078 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.052495 | 0.062793 | 0.056118 | -65.1128 | -0.52971 | -65.1802 | 57.6528 | 57.5758 | 57.7316 | -65.4822 | -65.0166 | -0.5903 | -65.1564 | 57.5538 | 57.7087 | 57.6844 | -65.6824 | -0.17759 | 0.002068 | 0.19178 | 0.12433 | 0.30192 | -0.075001 | 0.080871 | -0.37788 | -0.096977 | 0.28793 | 0.14812 | 0.526 | 0.05792 | 0.03365 | 122.9574 | 122.8803 | 123.0362 | 64.7749 | -123.1329 | 122.8583 | 123.0132 | 122.989 | 64.7143 | -123.3332
805.2656 | 123.175 | -65.2954 | 57.7011 | 0.04215 | -0.061882 | -0.0075097 | 0.04996 | -0.013815 | 0.054873 | 0.058145 | -0.0025767 | 0.0021894 | 0.053563 | 0.062793 | 0.056118 | -65.1174 | -0.53429 | -65.1619 | 57.6391 | 57.5574 | 57.7225 | -65.4867 | -65.0258 | -0.60403 | -65.1564 | 57.5492 | 57.7041 | 57.6798 | -65.6733 | -0.19132 | -0.062021 | 0.17805 | 0.13349 | 0.32481 | -0.14367 | 0.02136 | -0.37788 | -0.15191 | 0.26962 | 0.13896 | 0.51684 | 0.002987 | -0.021283 | 122.9345 | 122.8529 | 123.0179 | 64.7611 | -123.1878 | 122.8446 | 122.9995 | 122.9752 | 64.6914 | -123.3744
806.2656 | 123.1155 | -65.3229 | 57.6553 | 0.04215 | -0.064018 | -0.0075097 | 0.04996 | -0.014884 | 0.05701 | 0.058145 | -0.0047127 | 0.0011204 | 0.054631 | 0.063861 | 0.056118 | -65.1265 | -0.53887 | -65.1665 | 57.6391 | 57.5483 | 57.7179 | -65.5005 | -65.0258 | -0.62235 | -65.1702 | 57.5446 | 57.7041 | 57.6707 | -65.6824 | -0.17759 | -0.016244 | 0.19636 | 0.15638 | 0.33397 | -0.10705 | 0.062559 | -0.35957 | -0.11071 | 0.29709 | 0.15269 | 0.51226 | 0.048764 | 0.015337 | 122.962 | 122.8712 | 123.0408 | 64.784 | -123.1558 | 122.8675 | 123.027 | 122.9935 | 64.7005 | -123.3378
807.2656 | 123.1384 | -65.3137 | 57.7057 | 0.026888 | -0.06295 | -0.0075097 | 0.047824 | -0.012747 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.053563 | 0.063861 | 0.057187 | -65.1311 | -0.5526 | -65.1619 | 57.6391 | 57.5437 | 57.7087 | -65.4822 | -65.0349 | -0.62235 | -65.1656 | 57.5446 | 57.6995 | 57.6661 | -65.6824 | -0.16843 | -0.066598 | 0.18262 | 0.1518 | 0.32023 | -0.16198 | 0.003047 | -0.36872 | -0.16107 | 0.27877 | 0.14812 | 0.51684 | -0.006168 | -0.039596 | 122.9528 | 122.8574 | 123.0225 | 64.7611 | -123.1878 | 122.8583 | 123.0132 | 122.9798 | 64.6914 | -123.3881
808.2656 | 123.1384 | -65.3229 | 57.6416 | 0.057412 | -0.060813 | -0.0085787 | 0.051029 | -0.012747 | 0.05701 | 0.058145 | -0.0057807 | 0.0021894 | 0.053563 | 0.063861 | 0.057187 | -65.1357 | -0.5526 | -65.1711 | 57.6345 | 57.5437 | 57.7087 | -65.5005 | -65.0395 | -0.64524 | -65.1702 | 57.54 | 57.6949 | 57.6615 | -65.6916 | -0.17759 | -0.00709 | 0.1872 | 0.1518 | 0.32939 | -0.097898 | 0.067133 | -0.36873 | -0.10156 | 0.28335 | 0.15269 | 0.52142 | 0.053339 | 0.019912 | 122.9574 | 122.8666 | 123.0316 | 64.7703 | -123.1421 | 122.8629 | 123.0178 | 122.9844 | 64.6776 | -123.3332
809.2656 | 123.1705 | -65.3046 | 57.6691 | 0.04215 | -0.06295 | -0.0075097 | 0.047824 | -0.013815 | 0.058078 | 0.058145 | -0.0047127 | 0.0032574 | 0.056768 | 0.061724 | 0.05505 | -65.1311 | -0.56634 | -65.1757 | 57.6299 | 57.5483 | 57.7087 | -65.5005 | -65.0395 | -0.6544 | -65.1839 | 57.5355 | 57.6904 | 57.6615 | -65.6916 | -0.1959 | -0.039134 | 0.17347 | 0.12891 | 0.32481 | -0.12078 | 0.039668 | -0.38704 | -0.1336 | 0.26504 | 0.12064 | 0.50768 | 0.021295 | -0.007553 | 122.9345 | 122.8528 | 123.0133 | 64.7382 | -123.1695 | 122.84 | 122.9949 | 122.9661 | 64.6502 | -123.3607
810.2656 | 123.2391 | -65.3 | 57.6279 | 0.057412 | -0.061882 | -0.0075097 | 0.048892 | -0.011679 | 0.054873 | 0.088667 | -0.0047127 | 0.0021894 | 0.053563 | 0.062793 | 0.05505 | -65.1403 | -0.56634 | -65.1802 | 57.6299 | 57.5529 | 57.7087 | -65.5096 | -65.0533 | -0.65897 | -65.1885 | 57.5263 | 57.6858 | 57.6524 | -65.6962 | -0.20964 | 0.002064 | 0.15973 | 0.11975 | 0.32939 | -0.075007 | 0.080866 | -0.39619 | -0.10156 | 0.24673 | 0.11149 | 0.50768 | 0.057915 | 0.024487 | 122.9299 | 122.8528 | 123.0087 | 64.7336 | -123.1375 | 122.8263 | 122.9858 | 122.9523 | 64.641 | -123.324
811.2656 | 123.2574 | -65.3046 | 57.6279 | 0.057412 | -0.061882 | -0.0075097 | 0.047824 | -0.013815 | 0.058078 | 0.058145 | -0.0047127 | 0.0011204 | 0.054631 | 0.063861 | 0.056118 | -65.1403 | -0.58008 | -65.1894 | 57.6254 | 57.5666 | 57.7087 | -65.5142 | -65.0487 | -0.67729 | -65.1977 | 57.5172 | 57.6766 | 57.6569 | -65.7008 | -0.20964 | -0.002514 | 0.16431 | 0.11518 | 0.32482 | -0.061271 | 0.080866 | -0.39619 | -0.11072 | 0.25588 | 0.10691 | 0.5031 | 0.048758 | 0.029066 | 122.9299 | 122.8712 | 123.0133 | 64.7245 | -123.1421 | 122.8217 | 122.9812 | 122.9615 | 64.6273 | -123.3286
812.2656 | 123.2483 | -65.3 | 57.6279 | 0.04215 | -0.061882 | -0.0075097 | 0.047824 | -0.013815 | 0.05701 | 0.042884 | -0.0057807 | 0.0032574 | 0.053563 | 0.063861 | 0.05505 | -65.154 | -0.58466 | -65.1894 | 57.6208 | 57.5483 | 57.6996 | -65.5188 | -65.0533 | -0.68645 | -65.1931 | 57.5263 | 57.6766 | 57.6524 | -65.7008 | -0.2188 | -0.007092 | 0.146 | 0.1106 | 0.32939 | -0.079586 | 0.071709 | -0.40077 | -0.10156 | 0.24673 | 0.10691 | 0.50768 | 0.048758 | 0.024487 | 122.9208 | 122.8483 | 122.9996 | 64.7153 | -123.1467 | 122.8263 | 122.9766 | 122.9523 | 64.6135 | -123.3286
813.2656 | 123.2254 | -65.3183 | 57.6187 | 0.057412 | -0.061882 | -0.0075097 | 0.04996 | -0.012747 | 0.05701 | 0.042884 | -0.0036447 | 0.0011204 | 0.054631 | 0.063861 | 0.05505 | -65.1494 | -0.60297 | -65.194 | 57.6162 | 57.5529 | 57.6996 | -65.5188 | -65.0624 | -0.70476 | -65.2068 | 57.5172 | 57.6766 | 57.6386 | -65.7099 | -0.20049 | -0.002515 | 0.16889 | 0.12433 | 0.32482 | -0.065851 | 0.080865 | -0.39162 | -0.10156 | 0.25588 | 0.11148 | 0.5031 | 0.057914 | 0.019908 | 122.9345 | 122.8712 | 123.0179 | 64.7153 | -123.1375 | 122.8355 | 122.9949 | 122.9569 | 64.6135 | -123.3286
814.2656 | 123.2712 | -65.2954 | 57.6004 | 0.057412 | -0.060813 | -0.0075097 | 0.04996 | -0.013815 | 0.055941 | 0.073406 | -0.0047127 | 0.0021894 | 0.054631 | 0.064929 | 0.053982 | -65.154 | -0.60755 | -65.2031 | 57.607 | 57.5437 | 57.6858 | -65.5234 | -65.0624 | -0.7185 | -65.2068 | 57.508 | 57.672 | 57.6386 | -65.7145 | -0.22795 | 0.006638 | 0.14142 | 0.092286 | 0.32024 | -0.056699 | 0.085439 | -0.41909 | -0.092408 | 0.23299 | 0.088596 | 0.50768 | 0.071645 | 0.038218 | 122.9025 | 122.8391 | 122.9813 | 64.6879 | -123.1238 | 122.8034 | 122.9675 | 122.934 | 64.5769 | -123.3149
815.2656 | 123.2666 | -65.3137 | 57.605 | 0.026888 | -0.06295 | -0.0075097 | 0.048892 | -0.013815 | 0.053805 | 0.042884 | -0.0047127 | 0.0021894 | 0.054631 | 0.063861 | 0.056118 | -65.1586 | -0.63044 | -65.1985 | 57.6025 | 57.5208 | 57.6904 | -65.5279 | -65.0762 | -0.72766 | -65.216 | 57.508 | 57.6629 | 57.6386 | -65.7237 | -0.21422 | -0.002517 | 0.15515 | 0.11518 | 0.3294 | -0.084171 | 0.085441 | -0.40993 | -0.096985 | 0.23757 | 0.09775 | 0.50768 | 0.057911 | 0.033641 | 122.9162 | 122.8345 | 123.0041 | 64.6833 | -123.1329 | 122.8217 | 122.9766 | 122.9523 | 64.5861 | -123.3286
816.2656 | 123.2025 | -65.3275 | 57.5638 | 0.057412 | -0.064018 | -0.0064417 | 0.047824 | -0.012747 | 0.055941 | 0.042884 | -0.0047127 | 0.0011204 | 0.053563 | 0.063861 | 0.056118 | -65.1631 | -0.6396 | -65.2123 | 57.5933 | 57.5254 | 57.6813 | -65.5325 | -65.0899 | -0.74597 | -65.2114 | 57.4988 | 57.6583 | 57.634 | -65.7282 | -0.20507 | 0.029524 | 0.16431 | 0.11517 | 0.32024 | -0.038394 | 0.11748 | -0.40078 | -0.064944 | 0.23756 | 0.11606 | 0.51684 | 0.09453 | 0.07026 | 122.9208 | 122.8528 | 123.0087 | 64.6879 | -123.0963 | 122.8263 | 122.9858 | 122.9615 | 64.5815 | -123.292
817.2656 | 123.2437 | -65.3275 | 57.5958 | 0.057412 | -0.060813 | -0.0064417 | 0.048892 | -0.014884 | 0.055941 | 0.088667 | -0.0036447 | 0.0021894 | 0.054631 | 0.064929 | 0.056118 | -65.1723 | -0.65333 | -65.2123 | 57.5933 | 57.475 | 57.6675 | -65.5325 | -65.0807 | -0.75971 | -65.2206 | 57.4988 | 57.6583 | 57.6157 | -65.7282 | -0.20507 | -0.002519 | 0.15515 | 0.11517 | 0.32024 | -0.1208 | 0.071703 | -0.40078 | -0.096987 | 0.24672 | 0.1069 | 0.50768 | 0.062487 | 0.019903 | 122.9208 | 122.8025 | 122.995 | 64.6741 | -123.1283 | 122.8263 | 122.9858 | 122.9432 | 64.5677 | -123.3241
818.2656 | 123.2758 | -65.3366 | 57.5638 | 0.04215 | -0.064018 | -0.0064417 | 0.048892 | -0.013815 | 0.055941 | 0.088667 | -0.0057807 | 5.2373e-05 | 0.053563 | 0.064929 | 0.053982 | -65.1723 | -0.66249 | -65.2169 | 57.5842 | 57.4567 | 57.6584 | -65.5371 | -65.0899 | -0.77802 | -65.2389 | 57.4943 | 57.6446 | 57.6203 | -65.7328 | -0.20049 | 0.020368 | 0.1643 | 0.11975 | 0.32024 | -0.10708 | 0.094589 | -0.3962 | -0.069523 | 0.24672 | 0.097744 | 0.49395 | 0.080794 | 0.056524 | 122.9208 | 122.7933 | 122.995 | 64.6741 | -123.1009 | 122.8309 | 122.9812 | 122.9569 | 64.5586 | -123.2966
819.2656 | 123.2803 | -65.3275 | 57.5821 | 0.04215 | -0.061882 | -0.0064417 | 0.048892 | -0.011679 | 0.05701 | 0.027623 | -0.0047127 | 0.0011204 | 0.053563 | 0.062793 | 0.05505 | -65.1815 | -0.6808 | -65.226 | 57.5796 | 57.4659 | 57.6629 | -65.5417 | -65.099 | -0.78718 | -65.2389 | 57.4897 | 57.6354 | 57.6111 | -65.742 | -0.21422 | -0.002521 | 0.14599 | 0.10144 | 0.31566 | -0.11623 | 0.080857 | -0.41451 | -0.092411 | 0.22841 | 0.088589 | 0.5031 | 0.053327 | 0.029057 | 122.907 | 122.7933 | 122.9904 | 64.6466 | -123.1238 | 122.8171 | 122.9629 | 122.9386 | 64.5403 | -123.3241
820.2656 | 123.2483 | -65.3595 | 57.5867 | 0.057412 | -0.06295 | -0.0075097 | 0.047824 | -0.011679 | 0.055941 | 0.058145 | -0.0047127 | 0.0021894 | 0.053563 | 0.063861 | 0.056118 | -65.1815 | -0.69454 | -65.226 | 57.575 | 57.4933 | 57.6538 | -65.5554 | -65.1036 | -0.80092 | -65.2343 | 57.4805 | 57.64 | 57.6111 | -65.7465 | -0.19592 | -0.011677 | 0.17804 | 0.13348 | 0.3294 | -0.093334 | 0.067122 | -0.38705 | -0.10615 | 0.25587 | 0.12521 | 0.51226 | 0.053328 | 0.024479 | 122.9345 | 122.8528 | 123.0133 | 64.665 | -123.1421 | 122.84 | 122.9995 | 122.9706 | 64.5586 | -123.3332
821.2656 | 123.1064 | -65.3366 | 57.5546 | 0.057412 | -0.064018 | -0.0064417 | 0.048892 | -0.013815 | 0.053805 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.053563 | 0.063861 | 0.053982 | -65.1952 | -0.72201 | -65.226 | 57.5796 | 57.5208 | 57.6584 | -65.5646 | -65.1128 | -0.81465 | -65.2434 | 57.4805 | 57.6354 | 57.602 | -65.7557 | -0.22796 | 0.024945 | 0.14141 | 0.11059 | 0.33856 | -0.033817 | 0.10375 | -0.4191 | -0.074102 | 0.22382 | 0.093166 | 0.51226 | 0.080793 | 0.047366 | 122.9162 | 122.8574 | 122.995 | 64.6146 | -123.1192 | 122.8171 | 122.972 | 122.9386 | 64.522 | -123.3103
822.2656 | 123.23 | -65.3458 | 57.5821 | 0.057412 | -0.064018 | -0.0075097 | 0.04996 | -0.013815 | 0.055941 | 0.042884 | -0.0057807 | 0.0011204 | 0.0557 | 0.064929 | 0.05505 | -65.1952 | -0.72659 | -65.2398 | 57.575 | 57.5117 | 57.6584 | -65.56 | -65.1128 | -0.83297 | -65.2526 | 57.4714 | 57.6354 | 57.602 | -65.7603 | -0.21423 | -0.007099 | 0.15057 | 0.10601 | 0.32024 | -0.070441 | 0.076279 | -0.41452 | -0.11073 | 0.23298 | 0.093163 | 0.50768 | 0.053327 | 0.0199 | 122.9208 | 122.8574 | 123.0041 | 64.6192 | -123.1421 | 122.8171 | 122.9812 | 122.9478 | 64.5128 | -123.3424
823.2656 | 123.2117 | -65.3595 | 57.5821 | 0.04215 | -0.06295 | -0.0075097 | 0.047824 | -0.013815 | 0.055941 | 0.073406 | -0.0047127 | 0.0011204 | 0.054631 | 0.064929 | 0.056118 | -65.1906 | -0.74033 | -65.2398 | 57.5704 | 57.4933 | 57.6492 | -65.56 | -65.1265 | -0.84212 | -65.2526 | 57.4668 | 57.6263 | 57.6066 | -65.7603 | -0.2005 | -0.011678 | 0.16888 | 0.11975 | 0.32024 | -0.088756 | 0.067122 | -0.40079 | -0.1153 | 0.23298 | 0.1069 | 0.50768 | 0.04417 | 0.024478 | 122.9299 | 122.8528 | 123.0087 | 64.6192 | -123.1421 | 122.8263 | 122.9858 | 122.9661 | 64.5174 | -123.3424
824.2656 | 123.1979 | -65.3961 | 57.5363 | 0.04215 | -0.06295 | -0.0085787 | 0.047824 | -0.013815 | 0.05701 | 0.073406 | -0.0036447 | 0.0011204 | 0.054631 | 0.064929 | 0.056118 | -65.2044 | -0.76322 | -65.2398 | 57.5567 | 57.4979 | 57.6446 | -65.5737 | -65.1265 | -0.8696 | -65.2663 | 57.4576 | 57.6263 | 57.5928 | -65.7649 | -0.17761 | 0.020363 | 0.19177 | 0.15637 | 0.33398 | -0.038402 | 0.10832 | -0.36875 | -0.078685 | 0.2696 | 0.12978 | 0.49853 | 0.089946 | 0.056519 | 122.9528 | 122.894 | 123.0408 | 64.6329 | -123.11 | 122.8537 | 123.0224 | 122.989 | 64.5265 | -123.3012
825.2656 | 123.2025 | -65.3915 | 57.5546 | 0.04215 | -0.065087 | -0.0064417 | 0.04996 | -0.014884 | 0.055941 | 0.058145 | -0.0047127 | 0.0032574 | 0.0557 | 0.063861 | 0.05505 | -65.2044 | -0.78153 | -65.2489 | 57.5567 | 57.4979 | 57.6401 | -65.5737 | -65.1357 | -0.88791 | -65.2663 | 57.4668 | 57.6125 | 57.5837 | -65.7694 | -0.18219 | 0.002053 | 0.18719 | 0.14263 | 0.32482 | -0.056712 | 0.08543 | -0.3779 | -0.087838 | 0.25586 | 0.1252 | 0.50311 | 0.0579 | 0.029051 | 122.9482 | 122.8895 | 123.0316 | 64.61 | -123.1284 | 122.8583 | 123.0041 | 122.9752 | 64.5036 | -123.3241
826.2656 | 123.2071 | -65.4099 | 57.5363 | 0.026888 | -0.061882 | -0.010716 | 0.048892 | -0.012747 | 0.054873 | 0.042884 | -0.0036447 | 0.0021894 | 0.054631 | 0.064929 | 0.053982 | -65.2135 | -0.79069 | -65.2535 | 57.5567 | 57.4933 | 57.6263 | -65.5875 | -65.1448 | -0.9108 | -65.2709 | 57.4531 | 57.6125 | 57.5883 | -65.7786 | -0.17762 | 0.020363 | 0.19634 | 0.15637 | 0.33398 | -0.04298 | 0.090005 | -0.36875 | -0.083263 | 0.26502 | 0.13894 | 0.50768 | 0.07621 | 0.05194 | 122.9665 | 122.9032 | 123.0362 | 64.6192 | -123.1238 | 122.8629 | 123.0224 | 122.9981 | 64.499 | -123.3149
827.2656 | 123.2391 | -65.387 | 57.5592 | 0.026888 | -0.06295 | -0.0085787 | 0.04996 | -0.012747 | 0.055941 | 0.042884 | -0.0047127 | 0.0021894 | 0.054631 | 0.063861 | 0.056118 | -65.2135 | -0.80901 | -65.2581 | 57.5429 | 57.4888 | 57.6355 | -65.592 | -65.1494 | -0.92454 | -65.2801 | 57.4531 | 57.6079 | 57.5791 | -65.7786 | -0.20508 | -0.01626 | 0.17345 | 0.1289 | 0.33398 | -0.070447 | 0.076274 | -0.39164 | -0.10615 | 0.23755 | 0.10689 | 0.49853 | 0.048744 | 0.019895 | 122.9299 | 122.8757 | 123.0224 | 64.578 | -123.1513 | 122.84 | 122.9949 | 122.9661 | 64.4624 | -123.3378
828.2656 | 123.1979 | -65.4007 | 57.5592 | 0.057412 | -0.06295 | -0.0064417 | 0.04996 | -0.013815 | 0.058078 | 0.058145 | -0.0047127 | 0.0011204 | 0.053563 | 0.065998 | 0.05505 | -65.2318 | -0.81816 | -65.2626 | 57.5429 | 57.4842 | 57.6172 | -65.5966 | -65.1494 | -0.94285 | -65.2847 | 57.4485 | 57.6079 | 57.5791 | -65.7878 | -0.19593 | -0.01626 | 0.16887 | 0.13805 | 0.33398 | -0.075026 | 0.057959 | -0.38706 | -0.11073 | 0.25128 | 0.11604 | 0.50311 | 0.048744 | 0.019895 | 122.9436 | 122.8849 | 123.0179 | 64.5825 | -123.1558 | 122.8492 | 123.0086 | 122.9798 | 64.4578 | -123.347
829.3281 | 123.1201 | -65.4465 | 57.5409 | 0.04215 | -0.06295 | -0.0085787 | 0.046755 | -0.012747 | 0.054873 | 0.042884 | -0.0047127 | 0.0032574 | 0.053563 | 0.067066 | 0.053982 | -65.2227 | -0.8319 | -65.2626 | 57.5429 | 57.4796 | 57.6217 | -65.6012 | -65.154 | -0.96117 | -65.2984 | 57.4439 | 57.5896 | 57.5791 | -65.7878 | -0.15473 | 0.00205 | 0.22381 | 0.18383 | 0.33856 | -0.061295 | 0.080848 | -0.34128 | -0.096998 | 0.29248 | 0.14808 | 0.48937 | 0.048739 | 0.038205 | 122.9894 | 122.9261 | 123.0682 | 64.6146 | -123.1421 | 122.8904 | 123.0361 | 123.0256 | 64.4853 | -123.3287
830.2656 | 123.262 | -65.4053 | 57.4951 | 0.026888 | -0.061882 | -0.0085787 | 0.047824 | -0.012747 | 0.05701 | 0.058145 | -0.0047127 | 0.0043254 | 0.054631 | 0.063861 | 0.05505 | -65.2318 | -0.84564 | -65.2718 | 57.5384 | 57.475 | 57.6172 | -65.5966 | -65.1586 | -0.98406 | -65.2938 | 57.4439 | 57.5988 | 57.5608 | -65.7923 | -0.19135 | 0.043249 | 0.17345 | 0.13347 | 0.32483 | -0.020097 | 0.12205 | -0.38706 | -0.051221 | 0.2467 | 0.11146 | 0.49853 | 0.10367 | 0.065667 | 122.9436 | 122.8803 | 123.0224 | 64.5596 | -123.0917 | 122.8492 | 123.0041 | 122.9661 | 64.4212 | -123.2875
831.2656 | 123.2346 | -65.387 | 57.4951 | 0.057412 | -0.06295 | -0.0096467 | 0.048892 | -0.013815 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.054631 | 0.063861 | 0.05505 | -65.2318 | -0.86395 | -65.281 | 57.5292 | 57.475 | 57.608 | -65.6058 | -65.1723 | -1.0024 | -65.2938 | 57.4347 | 57.5896 | 57.5654 | -65.8061 | -0.21882 | 0.034092 | 0.15514 | 0.10601 | 0.32483 | -0.020097 | 0.11289 | -0.41911 | -0.060378 | 0.21465 | 0.093154 | 0.51226 | 0.094516 | 0.070246 | 122.9162 | 122.862 | 122.995 | 64.523 | -123.1009 | 122.8217 | 122.9766 | 122.9523 | 64.3846 | -123.3012
832.2656 | 123.2574 | -65.3915 | 57.4951 | 0.057412 | -0.06295 | -0.0075097 | 0.048892 | -0.012747 | 0.053805 | 0.058145 | -0.0057807 | 0.0021894 | 0.054631 | 0.067066 | 0.05505 | -65.241 | -0.87311 | -65.281 | 57.5292 | 57.4567 | 57.608 | -65.6104 | -65.1769 | -1.0253 | -65.2984 | 57.4256 | 57.5759 | 57.5562 | -65.8015 | -0.21882 | 0.034092 | 0.15056 | 0.11059 | 0.32941 | -0.038413 | 0.11289 | -0.40995 | -0.069535 | 0.21465 | 0.093153 | 0.5031 | 0.08078 | 0.061089 | 122.9207 | 122.8482 | 122.9995 | 64.5184 | -123.1055 | 122.8171 | 122.9674 | 122.9477 | 64.3663 | -123.2966
833.2656 | 123.2574 | -65.4053 | 57.4722 | 0.057412 | -0.065087 | -0.0096467 | 0.048892 | -0.015952 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.052495 | 0.063861 | 0.05505 | -65.241 | -0.896 | -65.2901 | 57.5292 | 57.4567 | 57.5988 | -65.6149 | -65.1769 | -1.0482 | -65.303 | 57.4256 | 57.5851 | 57.5425 | -65.8015 | -0.20967 | 0.05698 | 0.16429 | 0.11516 | 0.32483 | -0.015525 | 0.12662 | -0.39622 | -0.046647 | 0.22839 | 0.10231 | 0.49853 | 0.11283 | 0.070241 | 122.9345 | 122.862 | 123.0041 | 64.5093 | -123.0872 | 122.8309 | 122.9903 | 122.9477 | 64.3571 | -123.2737
834.2656 | 123.2483 | -65.4053 | 57.4768 | 0.04215 | -0.064018 | -0.0075097 | 0.047824 | -0.012747 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.053563 | 0.064929 | 0.053982 | -65.2593 | -0.91431 | -65.2901 | 57.5109 | 57.4567 | 57.5988 | -65.6195 | -65.186 | -1.0665 | -65.3167 | 57.421 | 57.5805 | 57.547 | -65.8107 | -0.21425 | 0.034088 | 0.14598 | 0.11516 | 0.32941 | -0.020103 | 0.12204 | -0.40538 | -0.055804 | 0.21923 | 0.08857 | 0.49395 | 0.10367 | 0.070241 | 122.9162 | 122.862 | 123.0041 | 64.491 | -123.0963 | 122.8263 | 122.9857 | 122.9523 | 64.3388 | -123.2875
835.2656 | 123.2437 | -65.4144 | 57.4814 | 0.026888 | -0.06295 | -0.0085787 | 0.048892 | -0.011679 | 0.05701 | 0.058145 | -0.0047127 | 0.0021894 | 0.054631 | 0.064929 | 0.053982 | -65.2501 | -0.92805 | -65.2855 | 57.5063 | 57.443 | 57.5897 | -65.6195 | -65.1952 | -1.0985 | -65.3213 | 57.4164 | 57.5759 | 57.5425 | -65.8152 | -0.20509 | 0.024933 | 0.16429 | 0.1289 | 0.33399 | -0.038417 | 0.10831 | -0.4008 | -0.064959 | 0.21923 | 0.093148 | 0.49395 | 0.094513 | 0.061086 | 122.9207 | 122.8574 | 123.0041 | 64.4864 | -123.1009 | 122.8309 | 122.9903 | 122.9569 | 64.3159 | -123.2966
836.2656 | 123.262 | -65.4327 | 57.486 | 0.026888 | -0.064018 | -0.0075097 | 0.048892 | -0.013815 | 0.055941 | 0.042884 | -0.0036447 | 0.0032574 | 0.053563 | 0.065998 | 0.052914 | -65.2593 | -0.9601 | -65.3038 | 57.5109 | 57.4292 | 57.5897 | -65.6287 | -65.1998 | -1.1214 | -65.3167 | 57.4164 | 57.5667 | 57.5425 | -65.8198 | -0.19594 | 0.024933 | 0.17345 | 0.12889 | 0.32483 | -0.056731 | 0.10373 | -0.38707 | -0.069537 | 0.23296 | 0.11604 | 0.50311 | 0.080778 | 0.056508 | 122.9436 | 122.862 | 123.0224 | 64.4726 | -123.1146 | 122.8492 | 122.9995 | 122.9752 | 64.3113 | -123.3058
837.2656 | 123.1522 | -65.4648 | 57.5317 | 0.072674 | -0.065087 | -0.0085787 | 0.048892 | -0.014884 | 0.058078 | 0.042884 | -0.0025767 | 0.0021894 | 0.053563 | 0.064929 | 0.05505 | -65.273 | -0.98299 | -65.3084 | 57.5017 | 57.3926 | 57.576 | -65.6333 | -65.2044 | -1.1535 | -65.3442 | 57.4027 | 57.5622 | 57.5287 | -65.829 | -0.16847 | -0.029999 | 0.19176 | 0.15636 | 0.32483 | -0.13914 | 0.044218 | -0.36418 | -0.12905 | 0.26042 | 0.12061 | 0.48479 | 0.030424 | -0.003004 | 122.9665 | 122.8574 | 123.0407 | 64.4818 | -123.165 | 122.8675 | 123.0269 | 122.9935 | 64.3113 | -123.3607
838.2656 | 123.1842 | -65.4556 | 57.4997 | 0.04215 | -0.06295 | -0.0085787 | 0.048892 | -0.015952 | 0.055941 | 0.073406 | -0.0036447 | 0.0011204 | 0.054631 | 0.067066 | 0.05505 | -65.2685 | -1.0013 | -65.313 | 57.488 | 57.3651 | 57.5714 | -65.647 | -65.2044 | -1.1764 | -65.335 | 57.3981 | 57.5622 | 57.5242 | -65.829 | -0.19137 | -0.011692 | 0.18718 | 0.14262 | 0.33399 | -0.13457 | 0.071682 | -0.37334 | -0.10158 | 0.25127 | 0.12061 | 0.49395 | 0.062467 | 0.02446 | 122.9436 | 122.8208 | 123.027 | 64.4543 | -123.1467 | 122.8537 | 123.0178 | 122.9798 | 64.2793 | -123.3287
839.2656 | 123.1613 | -65.4968 | 57.5043 | 0.026888 | -0.06295 | -0.0075097 | 0.048892 | -0.014884 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.051427 | 0.067066 | 0.056118 | -65.2776 | -1.015 | -65.3176 | 57.4834 | 57.356 | 57.5668 | -65.6378 | -65.2181 | -1.1993 | -65.3442 | 57.3935 | 57.553 | 57.5196 | -65.8381 | -0.14101 | -0.020847 | 0.21922 | 0.17924 | 0.32025 | -0.1483 | 0.062527 | -0.3413 | -0.11074 | 0.27873 | 0.15265 | 0.49395 | 0.048732 | 0.015305 | 122.9803 | 122.8528 | 123.0636 | 64.4818 | -123.1421 | 122.8904 | 123.0498 | 123.0164 | 64.2976 | -123.3424
840.2656 | 123.1384 | -65.5151 | 57.4768 | 0.011626 | -0.068292 | -0.0085787 | 0.052097 | -0.014884 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.054631 | 0.065998 | 0.05505 | -65.2913 | -1.0334 | -65.3313 | 57.4788 | 57.3697 | 57.5714 | -65.6516 | -65.2273 | -1.245 | -65.3442 | 57.389 | 57.5484 | 57.5058 | -65.8473 | -0.13644 | 0.00204 | 0.22379 | 0.18382 | 0.32026 | -0.1071 | 0.09457 | -0.33214 | -0.087853 | 0.28788 | 0.17096 | 0.50311 | 0.071619 | 0.029034 | 122.994 | 122.8848 | 123.0865 | 64.4818 | -123.1284 | 122.9041 | 123.0636 | 123.021 | 64.2701 | -123.3241
841.2656 | 123.1384 | -65.4785 | 57.4951 | 0.04215 | -0.064018 | -0.0075097 | 0.04996 | -0.013815 | 0.055941 | 0.042884 | -0.0047127 | 0.0021894 | 0.054631 | 0.064929 | 0.05505 | -65.2959 | -1.0517 | -65.3222 | 57.4743 | 57.3514 | 57.5622 | -65.6562 | -65.2273 | -1.2679 | -65.3488 | 57.3798 | 57.5393 | 57.5104 | -65.8519 | -0.17763 | -0.020849 | 0.1826 | 0.15636 | 0.33399 | -0.14373 | 0.067103 | -0.37334 | -0.11532 | 0.25126 | 0.12976 | 0.50311 | 0.044152 | 0.015303 | 122.9528 | 122.8299 | 123.0407 | 64.4268 | -123.1513 | 122.8583 | 123.0178 | 122.9889 | 64.2106 | -123.347
842.2656 | 123.1201 | -65.5243 | 57.5043 | 0.026888 | -0.065087 | -0.0064417 | 0.047824 | -0.013815 | 0.052737 | 0.088667 | -0.0047127 | 0.0011204 | 0.054631 | 0.063861 | 0.053982 | -65.2959 | -1.0883 | -65.3359 | 57.4651 | 57.3422 | 57.5576 | -65.6562 | -65.2456 | -1.3 | -65.3579 | 57.3752 | 57.5347 | 57.5013 | -65.861 | -0.13186 | -0.039161 | 0.22837 | 0.1884 | 0.32026 | -0.16204 | 0.05337 | -0.33673 | -0.12905 | 0.27872 | 0.16638 | 0.50311 | 0.030418 | -0.00301 | 122.9894 | 122.8665 | 123.0819 | 64.436 | -123.1604 | 122.8995 | 123.059 | 123.0256 | 64.2243 | -123.3653
843.2656 | 123.1522 | -65.5289 | 57.4814 | 0.04215 | -0.066155 | -0.0064417 | 0.04996 | -0.011679 | 0.055941 | 0.042884 | -0.0036447 | 5.2373e-05 | 0.054631 | 0.064929 | 0.053982 | -65.3097 | -1.1158 | -65.3405 | 57.4605 | 57.3422 | 57.5347 | -65.6607 | -65.2456 | -1.3275 | -65.3716 | 57.3706 | 57.521 | 57.4921 | -65.861 | -0.13186 | -0.020851 | 0.21921 | 0.1884 | 0.32026 | -0.13915 | 0.053365 | -0.33215 | -0.11074 | 0.2833 | 0.15722 | 0.48937 | 0.03957 | 0.010721 | 122.9894 | 122.8711 | 123.0636 | 64.4131 | -123.1421 | 122.8995 | 123.0498 | 123.021 | 64.2014 | -123.3424
844.2656 | 123.1659 | -65.4968 | 57.4631 | 0.026888 | -0.065087 | -0.0085787 | 0.048892 | -0.013815 | 0.05701 | 0.058145 | -0.0047127 | 0.0021894 | 0.052495 | 0.067066 | 0.05505 | -65.3097 | -1.1341 | -65.3542 | 57.4605 | 57.3834 | 57.5439 | -65.679 | -65.2593 | -1.3641 | -65.3808 | 57.3661 | 57.5164 | 57.4921 | -65.8748 | -0.18222 | -0.002541 | 0.18717 | 0.14262 | 0.32484 | -0.079633 | 0.080832 | -0.37793 | -0.097013 | 0.23752 | 0.11602 | 0.49395 | 0.053302 | 0.029031 | 122.9574 | 122.8803 | 123.0407 | 64.3627 | -123.1421 | 122.8629 | 123.0132 | 122.9889 | 64.1327 | -123.3378
845.2656 | 123.1705 | -65.5014 | 57.486 | 0.026888 | -0.064018 | -0.0085787 | 0.048892 | -0.012747 | 0.054873 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.053563 | 0.067066 | 0.052914 | -65.3188 | -1.1707 | -65.3588 | 57.456 | 57.388 | 57.5347 | -65.679 | -65.2593 | -1.4053 | -65.3854 | 57.3569 | 57.5164 | 57.4829 | -65.8748 | -0.17764 | -0.030007 | 0.18259 | 0.14262 | 0.32026 | -0.097942 | 0.048787 | -0.37335 | -0.12906 | 0.2421 | 0.11602 | 0.48937 | 0.030414 | -0.003014 | 122.9574 | 122.8894 | 123.0362 | 64.3307 | -123.165 | 122.8583 | 123.0178 | 122.9844 | 64.0961 | -123.3607
846.2656 | 123.143 | -65.538 | 57.4356 | 0.057412 | -0.066155 | -0.0085787 | 0.048892 | -0.013815 | 0.054873 | 0.027623 | -0.0036447 | 0.0021894 | 0.053563 | 0.067066 | 0.056118 | -65.3234 | -1.1982 | -65.3634 | 57.4331 | 57.3148 | 57.5256 | -65.6882 | -65.2776 | -1.4419 | -65.3854 | 57.3523 | 57.5118 | 57.4738 | -65.8885 | -0.15018 | -0.002545 | 0.21464 | 0.17466 | 0.32484 | -0.12085 | 0.089983 | -0.35047 | -0.083282 | 0.26041 | 0.15264 | 0.50311 | 0.076189 | 0.038183 | 122.9711 | 122.8528 | 123.0636 | 64.3398 | -123.1238 | 122.8904 | 123.0498 | 123.0118 | 64.0961 | -123.3241
847.2656 | 123.1567 | -65.5472 | 57.4585 | 0.04215 | -0.065087 | -0.0085787 | 0.04996 | -0.013815 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.054631 | 0.065998 | 0.056118 | -65.3417 | -1.2531 | -65.3771 | 57.4376 | 57.3056 | 57.5164 | -65.6928 | -65.2868 | -1.4877 | -65.4083 | 57.3432 | 57.4981 | 57.4692 | -65.8931 | -0.1456 | -0.020855 | 0.20548 | 0.17008 | 0.31568 | -0.1529 | 0.057938 | -0.34589 | -0.11533 | 0.2604 | 0.1389 | 0.48479 | 0.039565 | 0.010716 | 122.9848 | 122.8528 | 123.0636 | 64.294 | -123.1513 | 122.8903 | 123.0452 | 123.0164 | 64.0595 | -123.3516
848.2656 | 123.1705 | -65.5426 | 57.4448 | 0.04215 | -0.064018 | -0.0085787 | 0.04996 | -0.014884 | 0.055941 | 0.073406 | -0.0047127 | 0.0011204 | 0.052495 | 0.067066 | 0.052914 | -65.3463 | -1.3081 | -65.3771 | 57.4285 | 57.301 | 57.5119 | -65.7111 | -65.2868 | -1.5244 | -65.4037 | 57.334 | 57.4935 | 57.4646 | -65.8976 | -0.1685 | -0.016279 | 0.19632 | 0.1655 | 0.334 | -0.14374 | 0.067093 | -0.35505 | -0.11075 | 0.25583 | 0.1389 | 0.49395 | 0.04872 | 0.019871 | 122.9711 | 122.8436 | 123.0545 | 64.2345 | -123.1559 | 122.8766 | 123.0361 | 123.0072 | 64.0183 | -123.3424
849.2656 | 123.1705 | -65.5563 | 57.431 | 0.057412 | -0.065087 | -0.0075097 | 0.048892 | -0.013815 | 0.058078 | 0.058145 | -0.0057807 | 0.0021894 | 0.054631 | 0.068135 | 0.053982 | -65.3463 | -1.3355 | -65.4 | 57.4193 | 57.2919 | 57.5073 | -65.7111 | -65.3005 | -1.5701 | -65.4174 | 57.3203 | 57.4889 | 57.4463 | -65.9068 | -0.15476 | -0.011702 | 0.21005 | 0.15635 | 0.31111 | -0.13917 | 0.076247 | -0.35047 | -0.11075 | 0.25582 | 0.1389 | 0.48937 | 0.057874 | 0.015289 | 122.9757 | 122.8482 | 123.0636 | 64.2208 | -123.1421 | 122.8766 | 123.0452 | 123.0027 | 63.9862 | -123.3378
850.2656 | 123.1705 | -65.5472 | 57.4814 | 0.04215 | -0.065087 | -0.0075097 | 0.048892 | -0.014884 | 0.05701 | 0.042884 | -0.0047127 | 0.0021894 | 0.053563 | 0.068135 | 0.05505 | -65.3509 | -1.3539 | -65.3954 | 57.4193 | 57.3193 | 57.4981 | -65.7157 | -65.3097 | -1.6022 | -65.4266 | 57.3203 | 57.4797 | 57.4463 | -65.916 | -0.1685 | -0.062056 | 0.19632 | 0.15177 | 0.32027 | -0.16205 | 0.016736 | -0.36878 | -0.16111 | 0.23751 | 0.12059 | 0.48937 | -0.001637 | -0.035065 | 122.9665 | 122.8665 | 123.0453 | 64.1933 | -123.1971 | 122.8675 | 123.0269 | 122.9935 | 63.945 | -123.3973
851.2656 | 123.1247 | -65.5701 | 57.4448 | 0.04215 | -0.065087 | -0.0085787 | 0.04996 | -0.014884 | 0.05701 | 0.058145 | -0.0047127 | 0.0021894 | 0.054631 | 0.068135 | 0.056118 | -65.36 | -1.3813 | -65.4091 | 57.4147 | 57.3285 | 57.4935 | -65.7203 | -65.3142 | -1.6526 | -65.422 | 57.3157 | 57.4843 | 57.4372 | -65.9251 | -0.15019 | -0.030014 | 0.21005 | 0.16092 | 0.31111 | -0.11627 | 0.048778 | -0.35505 | -0.12907 | 0.25582 | 0.14805 | 0.50311 | 0.039562 | -0.007601 | 122.9848 | 122.8986 | 123.0636 | 64.1887 | -123.165 | 122.8858 | 123.0544 | 123.0072 | 63.9175 | -123.3699
852.2656 | 123.1567 | -65.5426 | 57.4219 | 0.04215 | -0.066155 | -0.0075097 | 0.047824 | -0.013815 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.053563 | 0.067066 | 0.053982 | -65.3738 | -1.4134 | -65.4091 | 57.401 | 57.3377 | 57.4798 | -65.7294 | -65.3234 | -1.6983 | -65.4357 | 57.3111 | 57.4614 | 57.4372 | -65.9205 | -0.18681 | -0.020861 | 0.16885 | 0.13346 | 0.32027 | -0.084223 | 0.05793 | -0.37794 | -0.11076 | 0.2192 | 0.10685 | 0.48479 | 0.039557 | 0.015287 | 122.9436 | 122.8803 | 123.0224 | 64.1292 | -123.1513 | 122.8537 | 123.004 | 122.9798 | 63.8443 | -123.3424
853.2656 | 123.1384 | -65.5655 | 57.4585 | 0.04215 | -0.067223 | -0.010716 | 0.048892 | -0.014884 | 0.055941 | 0.073406 | -0.0047127 | -0.0010156 | 0.053563 | 0.067066 | 0.05505 | -65.3783 | -1.4409 | -65.4275 | 57.3964 | 57.3285 | 57.489 | -65.7432 | -65.3371 | -1.7579 | -65.4495 | 57.302 | 57.4569 | 57.428 | -65.9297 | -0.17766 | -0.06206 | 0.18716 | 0.13803 | 0.31569 | -0.13 | 0.030467 | -0.36421 | -0.15653 | 0.22835 | 0.11601 | 0.48022 | -0.001642 | -0.030491 | 122.9619 | 122.894 | 123.0545 | 64.1246 | -123.2016 | 122.8675 | 123.0223 | 122.9935 | 63.8076 | -123.3882
854.2656 | 123.1293 | -65.5701 | 57.3853 | 0.04215 | -0.066155 | -0.0064417 | 0.048892 | -0.013815 | 0.05701 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.053563 | 0.069203 | 0.053982 | -65.3829 | -1.4592 | -65.4275 | 57.3873 | 57.3239 | 57.4706 | -65.7523 | -65.3463 | -1.8082 | -65.4586 | 57.2882 | 57.4523 | 57.4234 | -65.9434 | -0.18224 | 0.002025 | 0.18716 | 0.14261 | 0.32485 | -0.061339 | 0.085394 | -0.37337 | -0.097027 | 0.22377 | 0.11143 | 0.48479 | 0.067021 | 0.038172 | 122.9573 | 122.894 | 123.0407 | 64.1109 | -123.1376 | 122.8583 | 123.0223 | 122.9935 | 63.7618 | -123.3287
855.2656 | 123.143 | -65.6021 | 57.3944 | 0.04215 | -0.065087 | -0.0064417 | 0.051029 | -0.013815 | 0.054873 | 0.058145 | -0.0047127 | 0.0032574 | 0.053563 | 0.065998 | 0.053982 | -65.4012 | -1.4775 | -65.4504 | 57.3873 | 57.3239 | 57.4569 | -65.7615 | -65.3555 | -1.9227 | -65.4724 | 57.2745 | 57.4385 | 57.4097 | -65.9572 | -0.15935 | -0.00713 | 0.20089 | 0.15176 | 0.31112 | -0.070494 | 0.062503 | -0.35506 | -0.11992 | 0.24666 | 0.12973 | 0.48479 | 0.04413 | 0.015281 | 122.9894 | 122.926 | 123.059 | 64.1246 | -123.1559 | 122.8766 | 123.0407 | 123.0118 | 63.6794 | -123.3516
856.2656 | 123.1888 | -65.5792 | 57.3807 | 0.057412 | -0.067223 | -0.0085787 | 0.048892 | -0.013815 | 0.05701 | 0.073406 | -0.0036447 | 0.0032574 | 0.053563 | 0.065998 | 0.05505 | -65.4195 | -1.5095 | -65.4504 | 57.369 | 57.3056 | 57.4569 | -65.7706 | -65.3692 | -1.9914 | -65.4815 | 57.2653 | 57.4248 | 57.3914 | -65.9618 | -0.1914 | -0.011711 | 0.15969 | 0.12887 | 0.32027 | -0.075076 | 0.076236 | -0.38253 | -0.11534 | 0.21003 | 0.097688 | 0.48022 | 0.044127 | 0.0107 | 122.9482 | 122.8848 | 123.0361 | 64.0697 | -123.1513 | 122.8446 | 123.004 | 122.9706 | 63.5878 | -123.3424
857.2656 | 123.2162 | -65.5655 | 57.3669 | 0.057412 | -0.064018 | -0.0085787 | 0.04996 | -0.012747 | 0.055941 | 0.073406 | -0.0036447 | 0.0043254 | 0.052495 | 0.065998 | 0.053982 | -65.4195 | -1.5278 | -65.4549 | 57.3598 | 57.301 | 57.4478 | -65.7798 | -65.3875 | -2.0692 | -65.4861 | 57.2608 | 57.4248 | 57.3914 | -65.9709 | -0.21429 | -0.007134 | 0.14595 | 0.11056 | 0.32485 | -0.065922 | 0.080812 | -0.40542 | -0.10619 | 0.17798 | 0.079376 | 0.48479 | 0.05786 | 0.024433 | 122.9253 | 122.8665 | 123.0132 | 64.0376 | -123.1467 | 122.8262 | 122.9903 | 122.9569 | 63.4963 | -123.3379
858.2656 | 123.3032 | -65.5563 | 57.3669 | 0.04215 | -0.066155 | -0.0075097 | 0.047824 | -0.014884 | 0.055941 | 0.073406 | -0.0047127 | 0.0021894 | 0.054631 | 0.067066 | 0.053982 | -65.4287 | -1.5828 | -65.4687 | 57.3415 | 57.2827 | 57.434 | -65.7889 | -65.4012 | -2.1333 | -65.4953 | 57.247 | 57.4111 | 57.3822 | -65.9846 | -0.2326 | -0.025448 | 0.12764 | 0.08767 | 0.32027 | -0.084238 | 0.067076 | -0.42831 | -0.11992 | 0.15509 | 0.061063 | 0.48937 | 0.044125 | 0.015276 | 122.8978 | 122.839 | 122.9904 | 63.9735 | -123.1559 | 122.8034 | 122.9674 | 122.9386 | 63.423 | -123.3516
859.2656 | 123.2437 | -65.5792 | 57.3532 | 0.04215 | -0.065087 | -0.0075097 | 0.04996 | -0.014884 | 0.05701 | 0.088667 | -0.0057807 | 0.0011204 | 0.053563 | 0.067066 | 0.053982 | -65.4378 | -1.6744 | -65.487 | 57.3369 | 57.2598 | 57.4111 | -65.7935 | -65.4104 | -2.1974 | -65.5227 | 57.2379 | 57.4019 | 57.3685 | -66.0121 | -0.2143 | -0.016293 | 0.14137 | 0.092246 | 0.30654 | -0.0934 | 0.057916 | -0.4329 | -0.11535 | 0.16882 | 0.056479 | 0.48937 | 0.0487 | 0.015273 | 122.9161 | 122.839 | 122.9904 | 63.9049 | -123.1467 | 122.8171 | 122.9811 | 122.9477 | 63.3818 | -123.3653
860.2656 | 123.2483 | -65.6113 | 57.3166 | 0.04215 | -0.066155 | -0.0075097 | 0.048892 | -0.013815 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.052495 | 0.067066 | 0.053982 | -65.4562 | -1.711 | -65.4961 | 57.3278 | 57.2415 | 57.4157 | -65.8118 | -65.4104 | -2.2569 | -65.5273 | 57.2333 | 57.3928 | 57.3639 | -66.0075 | -0.20057 | 0.011171 | 0.1551 | 0.11513 | 0.3157 | -0.075094 | 0.099116 | -0.39627 | -0.083304 | 0.20087 | 0.083944 | 0.48022 | 0.076164 | 0.047315 | 122.939 | 122.8528 | 123.027 | 63.9003 | -123.1284 | 122.8446 | 123.004 | 122.9752 | 63.3543 | -123.3241
861.2656 | 123.2758 | -65.593 | 57.3349 | 0.057412 | -0.067223 | -0.0075097 | 0.04996 | -0.013815 | 0.053805 | 0.058145 | -0.0057807 | 0.0011204 | 0.052495 | 0.067066 | 0.052914 | -65.4607 | -1.7476 | -65.4961 | 57.3186 | 57.2094 | 57.3974 | -65.8118 | -65.4241 | -2.3027 | -65.5411 | 57.2195 | 57.3744 | 57.3502 | -66.0167 | -0.21888 | -0.016297 | 0.13222 | 0.096823 | 0.3157 | -0.12546 | 0.06249 | -0.42374 | -0.11535 | 0.16882 | 0.051898 | 0.47564 | 0.039539 | 0.015269 | 122.9116 | 122.8024 | 122.9903 | 63.8453 | -123.1467 | 122.8125 | 122.9674 | 122.9431 | 63.2902 | -123.3516
862.2656 | 123.262 | -65.5975 | 57.2891 | 0.057412 | -0.067223 | -0.0075097 | 0.048892 | -0.014884 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.054631 | 0.065998 | 0.052914 | -65.4745 | -1.7797 | -65.5144 | 57.3049 | 57.2278 | 57.3974 | -65.8302 | -65.4333 | -2.3577 | -65.5411 | 57.2104 | 57.3744 | 57.3364 | -66.0259 | -0.23262 | 0.015744 | 0.12306 | 0.083087 | 0.3157 | -0.061366 | 0.10827 | -0.42832 | -0.078732 | 0.16424 | 0.056475 | 0.4848 | 0.085315 | 0.047309 | 122.9024 | 122.8253 | 122.9949 | 63.8179 | -123.1193 | 122.8079 | 122.972 | 122.934 | 63.2399 | -123.315
863.2656 | 123.2666 | -65.6158 | 57.3029 | 0.087936 | -0.067223 | -0.0075097 | 0.048892 | -0.013815 | 0.055941 | 0.042884 | -0.0036447 | 0.0021894 | 0.053563 | 0.068135 | 0.052914 | -65.4791 | -1.8255 | -65.5144 | 57.3003 | 57.2323 | 57.3791 | -65.8393 | -65.4425 | -2.408 | -65.5548 | 57.2058 | 57.3607 | 57.3319 | -66.0396 | -0.22346 | -0.002566 | 0.13679 | 0.1014 | 0.32486 | -0.070519 | 0.07622 | -0.42375 | -0.097042 | 0.17339 | 0.061049 | 0.4848 | 0.057847 | 0.028998 | 122.9161 | 122.8482 | 122.9949 | 63.7904 | -123.1422 | 122.8217 | 122.9765 | 122.9477 | 63.2078 | -123.3424
864.2656 | 123.2574 | -65.625 | 57.3029 | 0.057412 | -0.066155 | -0.0075097 | 0.048892 | -0.012747 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.054631 | 0.068135 | 0.052914 | -65.4836 | -1.8438 | -65.5328 | 57.2866 | 57.2278 | 57.3791 | -65.8485 | -65.447 | -2.4584 | -65.5594 | 57.1921 | 57.3515 | 57.3227 | -66.0442 | -0.22347 | -0.016302 | 0.14137 | 0.09224 | 0.31571 | -0.075098 | 0.07622 | -0.41917 | -0.11078 | 0.17797 | 0.065626 | 0.4848 | 0.04869 | 0.019841 | 122.9116 | 122.8528 | 123.0041 | 63.7812 | -123.1513 | 122.8171 | 122.9765 | 122.9477 | 63.1666 | -123.347
865.2656 | 123.2346 | -65.6479 | 57.28 | 0.057412 | -0.066155 | -0.0064417 | 0.047824 | -0.014884 | 0.054873 | 0.042884 | -0.0036447 | 0.0021894 | 0.053563 | 0.068135 | 0.053982 | -65.4974 | -1.8621 | -65.5373 | 57.2866 | 57.2323 | 57.3653 | -65.8576 | -65.4699 | -2.5088 | -65.5777 | 57.1921 | 57.3378 | 57.3227 | -66.0487 | -0.20974 | 0.006586 | 0.15052 | 0.11055 | 0.32028 | -0.047631 | 0.085372 | -0.40086 | -0.08789 | 0.17796 | 0.070199 | 0.47106 | 0.057842 | 0.042729 | 122.9344 | 122.8802 | 123.0132 | 63.7858 | -123.1376 | 122.84 | 122.9857 | 122.9706 | 63.1391 | -123.3287
866.2656 | 123.23 | -65.657 | 57.2891 | 0.04215 | -0.066155 | -0.0064417 | 0.047824 | -0.014884 | 0.054873 | 0.073406 | -0.0036447 | 0.0011204 | 0.053563 | 0.067066 | 0.053982 | -65.5065 | -1.8896 | -65.5465 | 57.2774 | 57.2094 | 57.3562 | -65.8576 | -65.4791 | -2.5683 | -65.5777 | 57.1829 | 57.3287 | 57.309 | -66.0533 | -0.20058 | -0.011726 | 0.15052 | 0.11055 | 0.31113 | -0.079682 | 0.067059 | -0.39628 | -0.1062 | 0.17796 | 0.079354 | 0.47564 | 0.039529 | 0.019837 | 122.9344 | 122.8665 | 123.0132 | 63.7675 | -123.1467 | 122.84 | 122.9857 | 122.966 | 63.0887 | -123.3425
867.2656 | 123.2574 | -65.6799 | 57.2754 | 0.04215 | -0.067223 | -0.0075097 | 0.048892 | -0.013815 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.052495 | 0.065998 | 0.053982 | -65.5203 | -1.8941 | -65.5557 | 57.2637 | 57.2094 | 57.3516 | -65.8714 | -65.4837 | -2.6278 | -65.6006 | 57.1692 | 57.3287 | 57.2952 | -66.0671 | -0.19143 | -0.011729 | 0.15967 | 0.12428 | 0.31571 | -0.065949 | 0.076213 | -0.38713 | -0.1062 | 0.19627 | 0.079349 | 0.46648 | 0.053262 | 0.019834 | 122.9436 | 122.8894 | 123.0315 | 63.7858 | -123.1468 | 122.8491 | 123.0086 | 122.9752 | 63.0521 | -123.3425
868.2656 | 123.468 | -65.6433 | 57.2845 | 0.026888 | -0.065087 | -0.0085787 | 0.048892 | -0.013815 | 0.055941 | 0.058145 | -0.0047127 | 0.0021894 | 0.0557 | 0.067066 | 0.05505 | -65.5248 | -1.9079 | -65.5694 | 57.2591 | 57.1911 | 57.3424 | -65.8805 | -65.4974 | -2.6828 | -65.6006 | 57.1555 | 57.3195 | 57.2861 | -66.0808 | -0.23721 | -0.025462 | 0.11847 | 0.073924 | 0.31113 | -0.093419 | 0.057901 | -0.43749 | -0.12909 | 0.14591 | 0.042728 | 0.48022 | 0.03495 | 0.001522 | 122.9024 | 122.8344 | 122.9858 | 63.7354 | -123.1651 | 122.7988 | 122.9628 | 122.9294 | 62.9605 | -123.3653
869.2656 | 123.2437 | -65.6799 | 57.2342 | 0.04215 | -0.065087 | -0.0085787 | 0.048892 | -0.012747 | 0.055941 | 0.058145 | -0.0068487 | 0.0021894 | 0.053563 | 0.070271 | 0.052914 | -65.5294 | -1.9216 | -65.5785 | 57.2453 | 57.1911 | 57.3333 | -65.8943 | -65.5111 | -2.7514 | -65.6143 | 57.1509 | 57.3103 | 57.2678 | -66.0854 | -0.21432 | 0.011157 | 0.15051 | 0.10139 | 0.31571 | -0.043065 | 0.099098 | -0.40545 | -0.08332 | 0.1688 | 0.065613 | 0.47106 | 0.076146 | 0.033562 | 122.9253 | 122.8711 | 123.0132 | 63.7583 | -123.1284 | 122.8308 | 122.9903 | 122.9477 | 62.9285 | -123.3196
870.2656 | 123.2346 | -65.7074 | 57.2571 | 0.04215 | -0.066155 | -0.0075097 | 0.047824 | -0.012747 | 0.05701 | 0.073406 | -0.0047127 | 0.0011204 | 0.053563 | 0.069203 | 0.052914 | -65.5386 | -1.9308 | -65.5877 | 57.2362 | 57.182 | 57.3241 | -65.8943 | -65.5157 | -2.8201 | -65.6281 | 57.1417 | 57.3012 | 57.2678 | -66.09 | -0.18686 | -0.020888 | 0.16882 | 0.1197 | 0.30656 | -0.075111 | 0.067053 | -0.38256 | -0.11537 | 0.19169 | 0.079342 | 0.4619 | 0.044101 | 0.010674 | 122.9436 | 122.8894 | 123.0315 | 63.7766 | -123.1513 | 122.8491 | 123.0086 | 122.9752 | 62.8873 | -123.347
871.2656 | 123.2208 | -65.6982 | 57.2433 | 0.04215 | -0.067223 | -0.0096467 | 0.047824 | -0.014884 | 0.05701 | 0.073406 | -0.0047127 | 0.0032574 | 0.053563 | 0.068135 | 0.056118 | -65.5477 | -1.9491 | -65.5923 | 57.2225 | 57.1499 | 57.315 | -65.9126 | -65.5249 | -2.8705 | -65.6326 | 57.1326 | 57.292 | 57.2632 | -66.1129 | -0.21433 | -0.02089 | 0.15051 | 0.10596 | 0.32029 | -0.093431 | 0.071629 | -0.41461 | -0.11079 | 0.17337 | 0.065608 | 0.48022 | 0.048677 | 0.019828 | 122.9207 | 122.8482 | 123.0132 | 63.7492 | -123.1559 | 122.8308 | 122.9903 | 122.9614 | 62.8277 | -123.3562
872.2656 | 123.2162 | -65.7211 | 57.2296 | 0.04215 | -0.068292 | -0.0085787 | 0.048892 | -0.014884 | 0.055941 | 0.027623 | -0.0036447 | 0.0021894 | 0.052495 | 0.069203 | 0.056118 | -65.5569 | -1.9537 | -65.606 | 57.2133 | 57.127 | 57.3012 | -65.9126 | -65.5386 | -2.9209 | -65.6464 | 57.1234 | 57.2783 | 57.2449 | -66.1174 | -0.19144 | -0.016314 | 0.16424 | 0.11512 | 0.30656 | -0.10259 | 0.071626 | -0.3963 | -0.10621 | 0.18252 | 0.07476 | 0.47106 | 0.048674 | 0.015247 | 122.9344 | 122.8482 | 123.0224 | 63.7675 | -123.1422 | 122.8445 | 122.9994 | 122.966 | 62.8003 | -123.347
873.2656 | 123.2071 | -65.7211 | 57.1976 | 0.057412 | -0.066155 | -0.0075097 | 0.047824 | -0.015952 | 0.055941 | 0.058145 | -0.0036447 | 0.0021894 | 0.051427 | 0.068135 | 0.053982 | -65.5752 | -1.972 | -65.6197 | 57.1996 | 57.1453 | 57.2967 | -65.9263 | -65.5523 | -2.985 | -65.6509 | 57.1097 | 57.2691 | 57.2311 | -66.122 | -0.20518 | 0.001994 | 0.14593 | 0.10138 | 0.30656 | -0.052234 | 0.09909 | -0.40088 | -0.087905 | 0.16879 | 0.070182 | 0.47106 | 0.07156 | 0.033554 | 122.9207 | 122.8665 | 123.0178 | 63.7492 | -123.1239 | 122.8308 | 122.9903 | 122.9523 | 62.7362 | -123.3196
874.2656 | 123.2208 | -65.7715 | 57.225 | 0.04215 | -0.067223 | -0.0085787 | 0.048892 | -0.015952 | 0.055941 | 0.042884 | -0.0036447 | 0.0021894 | 0.053563 | 0.067066 | 0.053982 | -65.5798 | -1.9857 | -65.6197 | 57.195 | 57.127 | 57.2829 | -65.9355 | -65.5707 | -3.0399 | -65.6693 | 57.1051 | 57.2646 | 57.2311 | -66.1357 | -0.16398 | -0.03005 | 0.1917 | 0.15174 | 0.31572 | -0.098015 | 0.057888 | -0.36426 | -0.11995 | 0.20083 | 0.10222 | 0.46648 | 0.039515 | 0.006088 | 122.9665 | 122.8985 | 123.0544 | 63.7858 | -123.1605 | 122.8766 | 123.036 | 123.0026 | 62.7316 | -123.3608
875.2656 | 123.2071 | -65.7623 | 57.193 | 0.04215 | -0.066155 | -0.0085787 | 0.047824 | -0.013815 | 0.058078 | 0.058145 | -0.0057807 | 0.0011204 | 0.052495 | 0.068135 | 0.053982 | -65.5889 | -1.9811 | -65.6381 | 57.1904 | 57.1316 | 57.2783 | -65.9446 | -65.5798 | -3.1177 | -65.6738 | 57.0914 | 57.2554 | 57.2174 | -66.1495 | -0.1823 | -0.002585 | 0.17339 | 0.12427 | 0.30656 | -0.061393 | 0.085354 | -0.38715 | -0.10164 | 0.18251 | 0.088487 | 0.47564 | 0.062402 | 0.024396 | 122.9527 | 122.8939 | 123.0407 | 63.7812 | -123.1376 | 122.8537 | 123.0177 | 122.9797 | 62.6446 | -123.3425
876.2656 | 123.2025 | -65.7623 | 57.1976 | 0.04215 | -0.067223 | -0.0096467 | 0.047824 | -0.013815 | 0.055941 | 0.042884 | -0.0047127 | 0.0021894 | 0.053563 | 0.068135 | 0.052914 | -65.6027 | -1.9949 | -65.6426 | 57.1813 | 57.1179 | 57.2692 | -65.9629 | -65.5935 | -3.1406 | -65.6876 | 57.0776 | 57.2508 | 57.2082 | -66.1586 | -0.20061 | -0.01632 | 0.15966 | 0.11969 | 0.3203 | -0.079707 | 0.071619 | -0.39631 | -0.11996 | 0.16878 | 0.074751 | 0.47106 | 0.053246 | 0.010661 | 122.9436 | 122.8802 | 123.0315 | 63.7675 | -123.1605 | 122.8399 | 123.0131 | 122.9706 | 62.6217 | -123.3562
877.2656 | 123.2071 | -65.7715 | 57.1426 | 0.026888 | -0.068292 | -0.0075097 | 0.048892 | -0.012747 | 0.055941 | 0.073406 | -0.0047127 | 0.0032574 | 0.052495 | 0.069203 | 0.05505 | -65.6164 | -2.0086 | -65.6564 | 57.1721 | 57.1179 | 57.26 | -65.9675 | -65.5935 | -3.1818 | -65.6967 | 57.0685 | 57.2279 | 57.2037 | -66.1678 | -0.19603 | 0.029456 | 0.15508 | 0.11511 | 0.31114 | -0.024775 | 0.11739 | -0.39632 | -0.07418 | 0.17793 | 0.074748 | 0.47106 | 0.085285 | 0.061014 | 122.9436 | 122.8893 | 123.0315 | 63.7629 | -123.1102 | 122.8399 | 122.9994 | 122.9751 | 62.5896 | -123.3104
878.2656 | 123.2162 | -65.7715 | 57.1472 | 0.072674 | -0.06936 | -0.0085787 | 0.04996 | -0.014884 | 0.05701 | 0.058145 | -0.0036447 | 0.0011204 | 0.051427 | 0.068135 | 0.053982 | -65.621 | -2.0178 | -65.6655 | 57.1538 | 57.1133 | 57.2463 | -65.9904 | -65.6119 | -3.2459 | -65.7013 | 57.0593 | 57.2233 | 57.1945 | -66.177 | -0.21893 | 0.006564 | 0.1505 | 0.10595 | 0.32488 | -0.033932 | 0.09908 | -0.40547 | -0.087915 | 0.15962 | 0.07017 | 0.47564 | 0.076128 | 0.047279 | 122.9253 | 122.8848 | 123.0178 | 63.7537 | -123.1376 | 122.8308 | 122.9948 | 122.966 | 62.5255 | -123.3242
879.2656 | 123.2254 | -65.7852 | 57.1289 | 0.057412 | -0.068292 | -0.0085787 | 0.04996 | -0.012747 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.051427 | 0.068135 | 0.053982 | -65.6347 | -2.0269 | -65.6793 | 57.1492 | 57.095 | 57.2417 | -65.9858 | -65.6164 | -3.2917 | -65.7196 | 57.0547 | 57.2005 | 57.1808 | -66.1861 | -0.20062 | 0.020297 | 0.1505 | 0.10595 | 0.30657 | -0.033937 | 0.11281 | -0.4009 | -0.074182 | 0.16877 | 0.065588 | 0.46649 | 0.071546 | 0.051854 | 122.9344 | 122.8802 | 123.0269 | 63.7583 | -123.1147 | 122.8399 | 122.9857 | 122.966 | 62.4935 | -123.315
880.2656 | 123.2758 | -65.799 | 57.0923 | 0.04215 | -0.067223 | -0.0085787 | 0.051029 | -0.014884 | 0.053805 | 0.058145 | -0.0047127 | 0.0021894 | 0.052495 | 0.069203 | 0.053982 | -65.6393 | -2.0452 | -65.6884 | 57.14 | 57.0721 | 57.228 | -66.0041 | -65.6256 | -3.3421 | -65.7242 | 57.041 | 57.2005 | 57.167 | -66.1998 | -0.2052 | 0.047761 | 0.15965 | 0.11053 | 0.31573 | -0.020211 | 0.1357 | -0.4009 | -0.051297 | 0.17335 | 0.074742 | 0.47564 | 0.10817 | 0.074739 | 122.939 | 122.871 | 123.0269 | 63.7537 | -123.0964 | 122.8399 | 122.9994 | 122.966 | 62.4569 | -123.2921
881.2656 | 123.2529 | -65.8035 | 57.1106 | 0.026888 | -0.068292 | -0.0085787 | 0.04996 | -0.013815 | 0.055941 | 0.042884 | -0.0057807 | 0.0021894 | 0.053563 | 0.068135 | 0.053982 | -65.6576 | -2.059 | -65.6976 | 57.1263 | 57.0675 | 57.2097 | -66.0179 | -65.6439 | -3.4108 | -65.7425 | 57.0273 | 57.1959 | 57.1533 | -66.2044 | -0.21436 | 0.015715 | 0.14592 | 0.10595 | 0.32031 | -0.0431 | 0.099072 | -0.4009 | -0.083343 | 0.15961 | 0.061005 | 0.46191 | 0.085277 | 0.042693 | 122.9298 | 122.871 | 123.0132 | 63.7446 | -123.1285 | 122.8308 | 122.9994 | 122.9568 | 62.3927 | -123.315
882.2656 | 123.2483 | -65.8173 | 57.0831 | 0.011626 | -0.068292 | -0.0085787 | 0.046755 | -0.014884 | 0.05701 | 0.058145 | -0.0068487 | 0.0021894 | 0.053563 | 0.069203 | 0.053982 | -65.6713 | -2.0635 | -65.7113 | 57.1172 | 57.0629 | 57.2051 | -66.0225 | -65.6577 | -3.4474 | -65.7563 | 57.0181 | 57.173 | 57.1487 | -66.2182 | -0.2052 | 0.034024 | 0.14591 | 0.10595 | 0.31115 | -0.020213 | 0.12196 | -0.4009 | -0.065034 | 0.15961 | 0.061002 | 0.46191 | 0.08985 | 0.06558 | 122.9344 | 122.8802 | 123.0224 | 63.7537 | -123.1056 | 122.8354 | 122.9902 | 122.966 | 62.3699 | -123.3013
883.2656 | 123.2437 | -65.8356 | 57.0877 | 0.011626 | -0.066155 | -0.0085787 | 0.04996 | -0.013815 | 0.054873 | 0.058145 | -0.0068487 | 5.2373e-05 | 0.050358 | 0.070271 | 0.052914 | -65.6851 | -2.0681 | -65.725 | 57.108 | 57.0538 | 57.1914 | -66.0408 | -65.6622 | -3.5161 | -65.7608 | 57.0135 | 57.1638 | 57.135 | -66.2273 | -0.20521 | 0.020289 | 0.15049 | 0.11052 | 0.31573 | -0.033949 | 0.10365 | -0.39175 | -0.074191 | 0.17334 | 0.074733 | 0.46648 | 0.076115 | 0.047266 | 122.9436 | 122.8893 | 123.0269 | 63.7674 | -123.1285 | 122.8491 | 122.9994 | 122.9705 | 62.3195 | -123.315
884.2656 | 123.2574 | -65.8447 | 57.0648 | 0.04215 | -0.06936 | -0.0096467 | 0.04996 | -0.013815 | 0.055941 | 0.042884 | -0.0047127 | 0.0021894 | 0.052495 | 0.069203 | 0.05505 | -65.6897 | -2.091 | -65.7342 | 57.0943 | 57.04 | 57.1776 | -66.0408 | -65.6805 | -3.5848 | -65.77 | 56.9952 | 57.1592 | 57.1258 | -66.2411 | -0.19605 | 0.029443 | 0.15507 | 0.11052 | 0.30658 | -0.024797 | 0.1128 | -0.39633 | -0.069616 | 0.16418 | 0.074732 | 0.47107 | 0.094426 | 0.060998 | 122.939 | 122.8847 | 123.0223 | 63.7537 | -123.1056 | 122.8399 | 123.004 | 122.9705 | 62.26 | -123.3059
885.2656 | 123.2391 | -65.8401 | 57.0511 | 0.011626 | -0.06936 | -0.0096467 | 0.047824 | -0.014884 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.053563 | 0.069203 | 0.052914 | -65.7034 | -2.1093 | -65.7388 | 57.0851 | 57.0125 | 57.1685 | -66.0591 | -65.7034 | -3.6535 | -65.802 | 56.9815 | 57.1455 | 57.1121 | -66.264 | -0.21895 | 0.034019 | 0.13675 | 0.10137 | 0.32031 | -0.038538 | 0.11737 | -0.42381 | -0.069618 | 0.13671 | 0.038103 | 0.46191 | 0.094423 | 0.060995 | 122.9253 | 122.8527 | 123.0086 | 63.7308 | -123.1102 | 122.8216 | 122.9857 | 122.9522 | 62.1867 | -123.315
886.2656 | 123.1796 | -65.8905 | 57.0557 | 0.026888 | -0.068292 | -0.0075097 | 0.04996 | -0.015952 | 0.054873 | 0.027623 | -0.0057807 | 0.0011204 | 0.054631 | 0.070271 | 0.052914 | -65.7217 | -2.1185 | -65.7571 | 57.0714 | 56.9988 | 57.1501 | -66.0728 | -65.7126 | -3.7176 | -65.8066 | 56.9723 | 57.1226 | 57.1029 | -66.2731 | -0.18233 | 0.015706 | 0.16879 | 0.13341 | 0.31574 | -0.056852 | 0.094482 | -0.38261 | -0.083353 | 0.17791 | 0.083878 | 0.46649 | 0.066952 | 0.04726 | 122.9619 | 122.8893 | 123.0406 | 63.772 | -123.1285 | 122.8628 | 123.0131 | 122.9934 | 62.1729 | -123.3288
887.2656 | 123.2346 | -65.9088 | 57.0557 | 0.057412 | -0.06936 | -0.010716 | 0.04996 | -0.014884 | 0.055941 | 0.027623 | -0.0047127 | 5.2373e-05 | 0.051427 | 0.069203 | 0.052914 | -65.74 | -2.1322 | -65.7708 | 57.0622 | 56.9988 | 57.1501 | -66.0866 | -65.7218 | -3.7633 | -65.8204 | 56.9586 | 57.118 | 57.0938 | -66.2731 | -0.17776 | 0.006549 | 0.16879 | 0.13798 | 0.31574 | -0.056852 | 0.094482 | -0.3643 | -0.097089 | 0.18706 | 0.088452 | 0.45275 | 0.062373 | 0.038103 | 122.971 | 122.9076 | 123.059 | 63.7766 | -123.1422 | 122.8674 | 123.0268 | 123.0026 | 62.1455 | -123.3288
888.2656 | 123.1934 | -65.9454 | 57.0282 | 0.026888 | -0.06936 | -0.0085787 | 0.048892 | -0.014884 | 0.055941 | 0.088667 | -0.0047127 | 0.0021894 | 0.053563 | 0.069203 | 0.053982 | -65.7446 | -2.1414 | -65.78 | 57.0485 | 56.9897 | 57.1364 | -66.0957 | -65.7355 | -3.8091 | -65.8341 | 56.954 | 57.1089 | 57.08 | -66.296 | -0.15029 | 0.02028 | 0.20083 | 0.16545 | 0.31574 | -0.038544 | 0.10821 | -0.35057 | -0.074201 | 0.20995 | 0.11134 | 0.46191 | 0.080682 | 0.051833 | 122.9939 | 122.9351 | 123.0818 | 63.8041 | -123.1239 | 122.8994 | 123.0543 | 123.0255 | 62.1363 | -123.3242
889.2656 | 123.2254 | -65.9454 | 57.0236 | 0.04215 | -0.06936 | -0.0096467 | 0.04996 | -0.015952 | 0.055941 | 0.073406 | -0.0079177 | 5.2373e-05 | 0.051427 | 0.069203 | 0.053982 | -65.7583 | -2.146 | -65.7937 | 57.0393 | 56.9805 | 57.1181 | -66.1003 | -65.7492 | -3.8458 | -65.8387 | 56.9357 | 57.1043 | 57.0709 | -66.296 | -0.15487 | 0.0157 | 0.1871 | 0.15171 | 0.30658 | -0.043125 | 0.094475 | -0.35057 | -0.087938 | 0.19621 | 0.10676 | 0.45733 | 0.08068 | 0.047253 | 122.9848 | 122.9259 | 123.0635 | 63.7995 | -123.1239 | 122.8811 | 123.0497 | 123.0163 | 62.0997 | -123.3196
890.2656 | 123.175 | -65.9592 | 56.9962 | 0.026888 | -0.067223 | -0.010716 | 0.04996 | -0.014884 | 0.055941 | 0.073406 | -0.0047127 | 0.0032574 | 0.050358 | 0.07134 | 0.053982 | -65.7583 | -2.1551 | -65.8075 | 57.0256 | 56.9713 | 57.1135 | -66.114 | -65.7584 | -3.8915 | -65.8524 | 56.9265 | 57.0906 | 57.0617 | -66.3052 | -0.15488 | 0.029431 | 0.20083 | 0.15171 | 0.30659 | -0.024817 | 0.11736 | -0.346 | -0.069629 | 0.20078 | 0.10675 | 0.45275 | 0.09441 | 0.065562 | 122.9848 | 122.9305 | 123.0727 | 63.8041 | -123.1102 | 122.8857 | 123.0497 | 123.0209 | 62.0676 | -123.3013
891.2656 | 123.143 | -65.95 | 57.0099 | 0.04215 | -0.068292 | -0.010716 | 0.047824 | -0.014884 | 0.054873 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.051427 | 0.068135 | 0.052914 | -65.7675 | -2.1689 | -65.8166 | 57.021 | 56.9622 | 57.0998 | -66.1278 | -65.7675 | -3.9419 | -65.8707 | 56.9174 | 57.0723 | 57.0434 | -66.3281 | -0.17777 | 0.01112 | 0.18252 | 0.1334 | 0.31117 | -0.047708 | 0.089893 | -0.37805 | -0.092519 | 0.18247 | 0.079285 | 0.45733 | 0.062363 | 0.033514 | 122.971 | 122.9122 | 123.0498 | 63.7812 | -123.1377 | 122.8674 | 123.0223 | 122.9934 | 62.0081 | -123.3379
892.2656 | 123.1384 | -65.9546 | 57.0145 | 0.04215 | -0.06936 | -0.0075097 | 0.051029 | -0.014884 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.052495 | 0.069203 | 0.05505 | -65.7858 | -2.1826 | -65.8303 | 57.0164 | 56.953 | 57.0952 | -66.1415 | -65.7859 | -3.9785 | -65.8707 | 56.9082 | 57.0677 | 57.0388 | -66.3281 | -0.18693 | 0.001964 | 0.16878 | 0.12424 | 0.31117 | -0.061443 | 0.080738 | -0.37347 | -0.10625 | 0.16873 | 0.083863 | 0.45733 | 0.053207 | 0.024359 | 122.971 | 122.9076 | 123.0498 | 63.772 | -123.156 | 122.8628 | 123.0223 | 122.9934 | 61.976 | -123.3425
893.2656 | 123.1476 | -66.0004 | 57.0053 | 0.026888 | -0.06936 | -0.0085787 | 0.051029 | -0.014884 | 0.055941 | 0.058145 | -0.0068487 | -0.0010156 | 0.052495 | 0.072408 | 0.053982 | -65.7904 | -2.1872 | -65.8349 | 57.0027 | 56.8752 | 57.0769 | -66.1415 | -65.7813 | -4.0197 | -65.8845 | 56.8899 | 57.0585 | 57.0297 | -66.3372 | -0.14115 | -0.002616 | 0.20998 | 0.16544 | 0.30659 | -0.13013 | 0.071578 | -0.33685 | -0.11541 | 0.21909 | 0.1159 | 0.45275 | 0.053205 | 0.024356 | 123.0031 | 122.8755 | 123.0773 | 63.8132 | -123.1468 | 122.8903 | 123.0589 | 123.03 | 61.9806 | -123.3425
894.2656 | 123.1064 | -65.9912 | 57.0236 | 0.057412 | -0.06936 | -0.0096467 | 0.04996 | -0.012747 | 0.054873 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.052495 | 0.070271 | 0.052914 | -65.7995 | -2.1963 | -65.8487 | 56.9844 | 56.8614 | 57.0677 | -66.1461 | -65.7996 | -4.0564 | -65.8936 | 56.8899 | 57.0494 | 57.0159 | -66.3418 | -0.15488 | -0.03924 | 0.19167 | 0.14255 | 0.29743 | -0.16218 | 0.04411 | -0.35058 | -0.13372 | 0.19162 | 0.097591 | 0.44817 | 0.025737 | -0.00769 | 122.9756 | 122.8527 | 123.0589 | 63.7949 | -123.1697 | 122.8811 | 123.0406 | 123.0071 | 61.9348 | -123.3654
895.2656 | 123.0927 | -65.9775 | 56.9412 | 0.026888 | -0.068292 | -0.0085787 | 0.048892 | -0.015952 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.052495 | 0.069203 | 0.053982 | -65.8179 | -2.2101 | -65.8578 | 56.9706 | 56.866 | 57.054 | -66.1644 | -65.8133 | -4.1159 | -65.9074 | 56.8762 | 57.0356 | 56.993 | -66.3647 | -0.18693 | 0.029423 | 0.15962 | 0.11966 | 0.30659 | -0.0752 | 0.11277 | -0.38721 | -0.065061 | 0.16415 | 0.070122 | 0.45733 | 0.094399 | 0.051815 | 122.9481 | 122.8435 | 123.0315 | 63.7674 | -123.1056 | 122.8536 | 123.0131 | 122.9705 | 61.8616 | -123.3059
896.2656 | 123.2346 | -66.0049 | 57.0099 | 0.026888 | -0.072565 | -0.0096467 | 0.04996 | -0.015952 | 0.055941 | 0.042884 | -0.0047127 | 0.0011204 | 0.051427 | 0.069203 | 0.053982 | -65.8362 | -2.2192 | -65.8624 | 56.9615 | 56.834 | 57.0448 | -66.1736 | -65.8271 | -4.1754 | -65.9211 | 56.8624 | 57.0219 | 56.993 | -66.3784 | -0.16863 | -0.048399 | 0.16877 | 0.14255 | 0.31117 | -0.17592 | 0.03495 | -0.37348 | -0.14746 | 0.17788 | 0.083852 | 0.45733 | 0.011998 | -0.01685 | 122.9664 | 122.8389 | 123.0498 | 63.7857 | -123.1835 | 122.8674 | 123.0268 | 122.998 | 61.8295 | -123.3883
897.2656 | 123.175 | -66.0324 | 56.9733 | 0.04215 | -0.06936 | -0.0085787 | 0.04996 | -0.014884 | 0.052737 | 0.027623 | -0.0047127 | 0.0032574 | 0.052495 | 0.069203 | 0.053982 | -65.8407 | -2.2375 | -65.8761 | 56.9523 | 56.8294 | 57.0448 | -66.1781 | -65.8408 | -4.2029 | -65.9303 | 56.8624 | 57.0173 | 56.9885 | -66.383 | -0.14574 | -0.020935 | 0.19166 | 0.15628 | 0.30202 | -0.14388 | 0.071571 | -0.35059 | -0.11084 | 0.19161 | 0.10216 | 0.45275 | 0.044041 | 0.015192 | 122.9847 | 122.8618 | 123.0772 | 63.7949 | -123.1514 | 122.8948 | 123.0497 | 123.0209 | 61.8295 | -123.3563
898.2656 | 123.1659 | -66.0141 | 56.9687 | 0.057412 | -0.070429 | -0.0096467 | 0.04996 | -0.013815 | 0.055941 | 0.058145 | -0.0057807 | 0.0021894 | 0.052495 | 0.07134 | 0.053982 | -65.8407 | -2.2467 | -65.8853 | 56.9478 | 56.8614 | 57.0357 | -66.201 | -65.8637 | -4.2349 | -65.944 | 56.8487 | 57.0082 | 56.9747 | -66.3922 | -0.18694 | -0.020935 | 0.17335 | 0.12881 | 0.31575 | -0.10724 | 0.066992 | -0.37806 | -0.12 | 0.15041 | 0.070113 | 0.44818 | 0.039462 | 0.006034 | 122.9619 | 122.8755 | 123.0498 | 63.7674 | -123.1697 | 122.8628 | 123.0222 | 122.9888 | 61.7792 | -123.3608
899.2656 | 123.1842 | -66.0141 | 56.9733 | 0.04215 | -0.070429 | -0.0075097 | 0.051029 | -0.014884 | 0.053805 | 0.073406 | -0.0036447 | 0.0032574 | 0.052495 | 0.070271 | 0.052914 | -65.8636 | -2.2604 | -65.8944 | 56.9294 | 56.8569 | 57.0265 | -66.201 | -65.8637 | -4.2624 | -65.9486 | 56.8395 | 56.9944 | 56.9701 | -66.3967 | -0.18694 | -0.043827 | 0.15046 | 0.11965 | 0.3066 | -0.1164 | 0.053257 | -0.38264 | -0.13373 | 0.15041 | 0.065534 | 0.44817 | 0.021148 | -0.003122 | 122.9435 | 122.871 | 123.0406 | 63.7537 | -123.1743 | 122.8536 | 123.0085 | 122.9842 | 61.7517 | -123.37
900.2656 | 123.2117 | -66.0278 | 56.9 | 0.04215 | -0.070429 | -0.0085787 | 0.048892 | -0.012747 | 0.054873 | 0.058145 | -0.0057807 | 5.2373e-05 | 0.053563 | 0.07134 | 0.053982 | -65.8636 | -2.2696 | -65.9036 | 56.9157 | 56.8523 | 57.0174 | -66.2102 | -65.8683 | -4.2991 | -65.9577 | 56.835 | 56.9853 | 56.9518 | -66.4196 | -0.18237 | 0.015681 | 0.16419 | 0.12423 | 0.3066 | -0.047738 | 0.11734 | -0.3918 | -0.065068 | 0.15956 | 0.07011 | 0.46191 | 0.085234 | 0.051806 | 122.9435 | 122.8801 | 123.0452 | 63.7583 | -123.1102 | 122.8628 | 123.0131 | 122.9797 | 61.7288 | -123.3197
901.2656 | 123.1522 | -66.0187 | 56.9733 | 0.04215 | -0.06936 | -0.0096467 | 0.048892 | -0.015952 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.051427 | 0.07134 | 0.052914 | -65.8728 | -2.2971 | -65.9082 | 56.9203 | 56.8614 | 57.0128 | -66.2194 | -65.882 | -4.3403 | -65.9806 | 56.8258 | 56.9761 | 56.9518 | -66.4196 | -0.20068 | -0.052984 | 0.14588 | 0.1105 | 0.31118 | -0.11182 | 0.039521 | -0.40096 | -0.14747 | 0.13667 | 0.038061 | 0.43902 | 0.002833 | -0.021437 | 122.939 | 122.8801 | 123.0315 | 63.7216 | -123.1926 | 122.8445 | 122.9948 | 122.9705 | 61.6784 | -123.3929
902.2656 | 123.1796 | -66.069 | 56.9366 | 0.057412 | -0.071497 | -0.0085787 | 0.04996 | -0.015952 | 0.054873 | 0.073406 | -0.0068487 | 0.0011204 | 0.053563 | 0.07134 | 0.052914 | -65.8865 | -2.3154 | -65.9219 | 56.9065 | 56.7836 | 56.9899 | -66.2377 | -65.8957 | -4.3586 | -65.9806 | 56.8166 | 56.9669 | 56.9381 | -66.4288 | -0.16864 | -0.030098 | 0.1825 | 0.14712 | 0.31576 | -0.15304 | 0.053249 | -0.35976 | -0.12 | 0.17329 | 0.088415 | 0.44818 | 0.030297 | 0.001448 | 122.9756 | 122.8526 | 123.0589 | 63.7537 | -123.1743 | 122.8857 | 123.036 | 123.0071 | 61.7105 | -123.3654
903.2656 | 123.1613 | -66.0416 | 56.9138 | 0.057412 | -0.072565 | -0.0096467 | 0.048892 | -0.014884 | 0.052737 | 0.058145 | -0.0068487 | 0.0011204 | 0.052495 | 0.072408 | 0.053982 | -65.8957 | -2.3337 | -65.9356 | 56.8928 | 56.8065 | 56.9807 | -66.2468 | -65.9049 | -4.386 | -65.9989 | 56.8075 | 56.9669 | 56.9335 | -66.4425 | -0.20527 | -0.020944 | 0.14588 | 0.10592 | 0.31118 | -0.10726 | 0.066981 | -0.40096 | -0.10627 | 0.13666 | 0.042635 | 0.4436 | 0.053186 | 0.019759 | 122.9344 | 122.8481 | 123.0223 | 63.7079 | -123.1606 | 122.8491 | 123.0085 | 122.9751 | 61.6555 | -123.3563
904.2656 | 123.1659 | -66.0736 | 56.9412 | 0.026888 | -0.06936 | -0.0085787 | 0.046755 | -0.014884 | 0.054873 | 0.058145 | -0.0057807 | 0.0021894 | 0.053563 | 0.07134 | 0.052914 | -65.9048 | -2.3703 | -65.9356 | 56.8882 | 56.8111 | 56.9807 | -66.2468 | -65.9186 | -4.4181 | -65.9944 | 56.7892 | 56.9486 | 56.9198 | -66.4471 | -0.17323 | -0.052988 | 0.16876 | 0.13796 | 0.31118 | -0.13015 | 0.039515 | -0.3735 | -0.15205 | 0.15497 | 0.079256 | 0.45275 | 0.007406 | -0.021443 | 122.9618 | 122.8847 | 123.0543 | 63.7033 | -123.1881 | 122.8628 | 123.0222 | 122.9934 | 61.6555 | -123.3883
905.2656 | 123.2574 | -66.0736 | 56.8314 | 0.04215 | -0.06936 | -0.0085787 | 0.047824 | -0.014884 | 0.053805 | 0.058145 | -0.0047127 | -0.0010156 | 0.053563 | 0.072408 | 0.052914 | -65.914 | -2.384 | -65.9494 | 56.8745 | 56.8202 | 56.9762 | -66.2606 | -65.9232 | -4.441 | -66.0127 | 56.7846 | 56.944 | 56.9106 | -66.4517 | -0.18696 | 0.043139 | 0.15961 | 0.12422 | 0.31119 | -0.011126 | 0.1448 | -0.37808 | -0.046768 | 0.15039 | 0.060941 | 0.43902 | 0.11269 | 0.079263 | 122.9481 | 122.8938 | 123.0498 | 63.6896 | -123.0919 | 122.8582 | 123.0177 | 122.9842 | 61.6326 | -123.283
906.2656 | 123.175 | -66.1102 | 56.9183 | 0.026888 | -0.070429 | -0.0096467 | 0.047824 | -0.015952 | 0.053805 | 0.088667 | -0.0047127 | 0.0021894 | 0.051427 | 0.070271 | 0.053982 | -65.9232 | -2.4115 | -65.9585 | 56.8791 | 56.8111 | 56.9716 | -66.2651 | -65.9324 | -4.4685 | -66.0172 | 56.7663 | 56.9303 | 56.9015 | -66.4608 | -0.15492 | -0.039257 | 0.18707 | 0.15169 | 0.30661 | -0.10726 | 0.053245 | -0.35061 | -0.15206 | 0.17786 | 0.092984 | 0.4436 | 0.011979 | -0.016869 | 122.9893 | 122.9213 | 123.0818 | 63.6987 | -123.1835 | 122.8765 | 123.0405 | 123.0117 | 61.6418 | -123.3792
907.2656 | 123.2117 | -66.1148 | 56.8817 | 0.04215 | -0.070429 | -0.0096467 | 0.047824 | -0.013815 | 0.055941 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.051427 | 0.072408 | 0.051845 | -65.9415 | -2.4344 | -65.9769 | 56.8653 | 56.8019 | 56.9487 | -66.2835 | -65.9461 | -4.4914 | -66.031 | 56.7617 | 56.9257 | 56.8923 | -66.4792 | -0.16866 | -0.016371 | 0.17333 | 0.13795 | 0.30661 | -0.079796 | 0.066973 | -0.36435 | -0.12001 | 0.1687 | 0.083826 | 0.44818 | 0.044022 | 0.010594 | 122.9802 | 122.9167 | 123.0635 | 63.6804 | -123.1652 | 122.8765 | 123.0405 | 123.0071 | 61.6235 | -123.3609
908.2656 | 123.1522 | -66.124 | 56.8771 | 0.04215 | -0.06936 | -0.0085787 | 0.048892 | -0.015952 | 0.052737 | 0.073406 | -0.0068487 | 0.0011204 | 0.052495 | 0.072408 | 0.053982 | -65.9506 | -2.4573 | -65.9814 | 56.8562 | 56.7973 | 56.9441 | -66.2926 | -65.9507 | -4.5051 | -66.0401 | 56.7525 | 56.912 | 56.8832 | -66.4883 | -0.16866 | -0.02095 | 0.17333 | 0.14253 | 0.31119 | -0.079797 | 0.066973 | -0.36435 | -0.12459 | 0.17327 | 0.083823 | 0.44818 | 0.034864 | 0.006015 | 122.9801 | 122.9213 | 123.0681 | 63.6667 | -123.1698 | 122.8765 | 123.036 | 123.0071 | 61.6189 | -123.3655
909.2656 | 123.2071 | -66.1194 | 56.8817 | 0.04215 | -0.06936 | -0.0085787 | 0.047824 | -0.015952 | 0.052737 | 0.073406 | -0.0047127 | 5.2373e-05 | 0.053563 | 0.073476 | 0.053982 | -65.9552 | -2.471 | -65.9906 | 56.847 | 56.7928 | 56.9533 | -66.3018 | -65.969 | -4.5234 | -66.0401 | 56.748 | 56.912 | 56.8832 | -66.4929 | -0.18239 | -0.034685 | 0.16418 | 0.1288 | 0.31119 | -0.088954 | 0.071552 | -0.37351 | -0.13375 | 0.15038 | 0.079246 | 0.45276 | 0.030286 | 0.001437 | 122.9664 | 122.9121 | 123.0727 | 63.6483 | -123.1835 | 122.8673 | 123.0314 | 123.0025 | 61.596 | -123.3746
910.2656 | 123.1293 | -66.156 | 56.8451 | 0.04215 | -0.070429 | -0.0096467 | 0.047824 | -0.015952 | 0.055941 | 0.027623 | -0.0047127 | 5.2373e-05 | 0.054631 | 0.072408 | 0.05505 | -65.9598 | -2.4802 | -65.9997 | 56.847 | 56.7882 | 56.9258 | -66.3109 | -65.969 | -4.528 | -66.063 | 56.7388 | 56.8983 | 56.8648 | -66.5066 | -0.15493 | 0.001936 | 0.19622 | 0.15626 | 0.31119 | -0.056912 | 0.080701 | -0.35062 | -0.10629 | 0.187 | 0.092974 | 0.4436 | 0.053171 | 0.019744 | 123.003 | 122.9442 | 123.0818 | 63.6758 | -123.156 | 122.8948 | 123.0543 | 123.0208 | 61.628 | -123.3517
911.2656 | 123.1338 | -66.1423 | 56.868 | 0.026888 | -0.070429 | -0.0085787 | 0.046755 | -0.013815 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.052495 | 0.07134 | 0.052914 | -65.9689 | -2.5031 | -66.0089 | 56.8333 | 56.7744 | 56.9166 | -66.3064 | -65.9736 | -4.5371 | -66.0676 | 56.7342 | 56.8891 | 56.8603 | -66.5204 | -0.16409 | -0.034687 | 0.17333 | 0.13337 | 0.29746 | -0.093537 | 0.048656 | -0.3781 | -0.13375 | 0.16869 | 0.074662 | 0.45276 | 0.021126 | -0.007723 | 122.9756 | 122.9167 | 123.0589 | 63.6392 | -123.1743 | 122.8765 | 123.0314 | 123.0025 | 61.6051 | -123.3883
912.2656 | 123.2254 | -66.1377 | 56.8222 | 0.026888 | -0.071497 | -0.0075097 | 0.048892 | -0.014884 | 0.053805 | 0.088667 | -0.0057807 | 0.0011204 | 0.053563 | 0.07134 | 0.053982 | -65.9781 | -2.5122 | -66.0135 | 56.8287 | 56.7653 | 56.9121 | -66.3201 | -65.9919 | -4.5509 | -66.0676 | 56.7251 | 56.8845 | 56.8557 | -66.5204 | -0.1824 | 0.006511 | 0.15959 | 0.12421 | 0.30661 | -0.056918 | 0.089854 | -0.38267 | -0.097133 | 0.1458 | 0.070084 | 0.45276 | 0.062323 | 0.033475 | 122.9664 | 122.903 | 123.0498 | 63.6254 | -123.1423 | 122.8628 | 123.0222 | 122.9934 | 61.5868 | -123.3426
913.2656 | 123.2758 | -66.1102 | 56.8359 | 0.04215 | -0.068292 | -0.0085787 | 0.047824 | -0.015952 | 0.055941 | 0.042884 | -0.0057807 | 5.2373e-05 | 0.051427 | 0.072408 | 0.052914 | -65.9918 | -2.526 | -66.0226 | 56.8196 | 56.7607 | 56.9029 | -66.3293 | -65.9919 | -4.56 | -66.0813 | 56.7205 | 56.88 | 56.8419 | -66.5249 | -0.21902 | -0.016378 | 0.11839 | 0.087593 | 0.30662 | -0.075229 | 0.066964 | -0.41472 | -0.11544 | 0.11833 | 0.028882 | 0.4436 | 0.044013 | 0.006007 | 122.9298 | 122.8709 | 123.0131 | 63.5842 | -123.1652 | 122.8307 | 122.9902 | 122.9522 | 61.5502 | -123.3609
914.2656 | 123.2712 | -66.1102 | 56.8222 | 0.057412 | -0.070429 | -0.0096467 | 0.048892 | -0.015952 | 0.054873 | 0.088667 | -0.0047127 | 0.0032574 | 0.053563 | 0.07134 | 0.052914 | -65.9918 | -2.5397 | -66.0226 | 56.815 | 56.7561 | 56.8937 | -66.3384 | -66.0011 | -4.5692 | -66.0859 | 56.7068 | 56.8708 | 56.8374 | -66.5341 | -0.22818 | -0.007225 | 0.11839 | 0.087593 | 0.31577 | -0.066076 | 0.071539 | -0.42387 | -0.11545 | 0.10917 | 0.024303 | 0.44818 | 0.048588 | 0.01516 | 122.9252 | 122.8664 | 123.004 | 63.5705 | -123.1606 | 122.817 | 122.981 | 122.9476 | 61.541 | -123.3563
915.2656 | 123.1567 | -66.188 | 56.7902 | 0.04215 | -0.070429 | -0.010716 | 0.04996 | -0.015952 | 0.053805 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.051427 | 0.072408 | 0.053982 | -66.0101 | -2.558 | -66.0364 | 56.815 | 56.747 | 56.8937 | -66.343 | -66.0102 | -4.5784 | -66.0997 | 56.7022 | 56.8662 | 56.8328 | -66.5387 | -0.15494 | 0.024819 | 0.1779 | 0.15168 | 0.30662 | -0.04319 | 0.10358 | -0.35063 | -0.087981 | 0.17784 | 0.088387 | 0.43902 | 0.076053 | 0.042626 | 123.003 | 122.935 | 123.0818 | 63.63 | -123.1332 | 122.8902 | 123.0543 | 123.0208 | 61.6097 | -123.3288
916.2656 | 123.2529 | -66.124 | 56.8085 | 0.04215 | -0.06936 | -0.010716 | 0.047824 | -0.015952 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.052495 | 0.069203 | 0.05505 | -66.0056 | -2.5763 | -66.0364 | 56.8058 | 56.7241 | 56.8892 | -66.3476 | -66.0148 | -4.5921 | -66.1042 | 56.6976 | 56.8525 | 56.8191 | -66.5478 | -0.22361 | -0.002648 | 0.11839 | 0.087591 | 0.3112 | -0.084396 | 0.080694 | -0.42388 | -0.11087 | 0.10917 | 0.019721 | 0.4436 | 0.044006 | 0.010579 | 122.9298 | 122.848 | 123.0131 | 63.5476 | -123.156 | 122.8216 | 122.9764 | 122.943 | 61.5319 | -123.3563
917.2656 | 123.2529 | -66.1331 | 56.7719 | 0.04215 | -0.070429 | -0.0085787 | 0.048892 | -0.013815 | 0.054873 | 0.088667 | -0.0047127 | 0.0032574 | 0.051427 | 0.070271 | 0.052914 | -66.0193 | -2.5809 | -66.0547 | 56.7829 | 56.7195 | 56.88 | -66.3613 | -66.0239 | -4.6241 | -66.118 | 56.693 | 56.8571 | 56.8099 | -66.5524 | -0.22819 | 0.011081 | 0.11381 | 0.078434 | 0.30662 | -0.052354 | 0.10816 | -0.4193 | -0.078828 | 0.10917 | 0.015141 | 0.43444 | 0.085206 | 0.038042 | 122.916 | 122.8526 | 123.0131 | 63.5522 | -123.1332 | 122.8261 | 122.9902 | 122.943 | 61.509 | -123.3243
918.2656 | 123.2712 | -66.1423 | 56.7719 | 0.072674 | -0.070429 | -0.0085787 | 0.046755 | -0.015952 | 0.054873 | 0.073406 | -0.0047127 | 0.0011204 | 0.051427 | 0.07134 | 0.051845 | -66.033 | -2.5947 | -66.0547 | 56.7738 | 56.7103 | 56.8617 | -66.3567 | -66.0285 | -4.6333 | -66.1226 | 56.6747 | 56.8433 | 56.8145 | -66.5662 | -0.21445 | 0.001924 | 0.10923 | 0.087589 | 0.30204 | -0.061512 | 0.089843 | -0.42388 | -0.097142 | 0.11375 | 0.019717 | 0.4436 | 0.07147 | 0.042621 | 122.916 | 122.8526 | 123.004 | 63.5476 | -123.1286 | 122.817 | 122.9856 | 122.9567 | 61.509 | -123.338
919.2656 | 123.2666 | -66.1652 | 56.7444 | 0.04215 | -0.072565 | -0.0096467 | 0.048892 | -0.01702 | 0.054873 | 0.073406 | -0.0057807 | 0.0021894 | 0.053563 | 0.07134 | 0.052914 | -66.0376 | -2.613 | -66.0593 | 56.76 | 56.6829 | 56.8663 | -66.3659 | -66.0514 | -4.6516 | -66.1363 | 56.6747 | 56.8342 | 56.7962 | -66.5662 | -0.20072 | 0.015655 | 0.12754 | 0.1059 | 0.30662 | -0.061519 | 0.12189 | -0.401 | -0.069676 | 0.11374 | 0.028869 | 0.42986 | 0.089779 | 0.051773 | 122.9252 | 122.848 | 123.0314 | 63.5522 | -123.1103 | 122.8399 | 122.9993 | 122.9613 | 61.5136 | -123.3105
920.2656 | 123.1796 | -66.1697 | 56.7993 | 0.057412 | -0.071497 | -0.0096467 | 0.046755 | -0.013815 | 0.053805 | 0.042884 | -0.0068487 | 0.0021894 | 0.053563 | 0.07134 | 0.052914 | -66.0422 | -2.6221 | -66.0638 | 56.7646 | 56.6783 | 56.8571 | -66.3705 | -66.0468 | -4.6562 | -66.1317 | 56.6701 | 56.825 | 56.8007 | -66.5707 | -0.20072 | -0.034698 | 0.12754 | 0.1059 | 0.30662 | -0.12103 | 0.057799 | -0.401 | -0.12919 | 0.1229 | 0.038026 | 0.43902 | 0.025691 | 0.00142 | 122.9344 | 122.848 | 123.0269 | 63.5476 | -123.1698 | 122.8399 | 122.9947 | 122.9705 | 61.5136 | -123.3701
921.2656 | 123.2162 | -66.156 | 56.7673 | 0.057412 | -0.071497 | -0.010716 | 0.048892 | -0.015952 | 0.054873 | 0.042884 | -0.0068487 | 0.0021894 | 0.053563 | 0.072408 | 0.053982 | -66.0468 | -2.6359 | -66.0776 | 56.76 | 56.6829 | 56.8525 | -66.3796 | -66.056 | -4.6745 | -66.1454 | 56.6656 | 56.8204 | 56.787 | -66.5799 | -0.22361 | -0.007233 | 0.10923 | 0.07843 | 0.30205 | -0.084407 | 0.085264 | -0.42389 | -0.10172 | 0.10001 | 0.010557 | 0.43444 | 0.053155 | 0.019727 | 122.916 | 122.8389 | 123.0085 | 63.5201 | -123.1469 | 122.8216 | 122.9764 | 122.943 | 61.4815 | -123.3472
922.2656 | 123.2437 | -66.1789 | 56.7169 | 0.04215 | -0.072565 | -0.0096467 | 0.046755 | -0.01702 | 0.053805 | 0.042884 | -0.0057807 | 0.0021894 | 0.050358 | 0.073476 | 0.053982 | -66.0559 | -2.6496 | -66.0913 | 56.7509 | 56.692 | 56.8434 | -66.3979 | -66.0652 | -4.7111 | -66.15 | 56.6518 | 56.8158 | 56.7824 | -66.5891 | -0.21904 | 0.033964 | 0.12296 | 0.087583 | 0.30663 | -0.024895 | 0.12646 | -0.41016 | -0.065103 | 0.11374 | 0.028866 | 0.43902 | 0.09893 | 0.065503 | 122.9298 | 122.8709 | 123.0223 | 63.5293 | -123.1149 | 122.8307 | 122.9947 | 122.9613 | 61.4678 | -123.306
923.3125 | 123.1705 | -66.2292 | 56.7902 | 0.057412 | -0.071497 | -0.010716 | 0.047824 | -0.015952 | 0.052737 | 0.058145 | -0.0047127 | 0.0011204 | 0.052495 | 0.07134 | 0.053982 | -66.0697 | -2.6633 | -66.0959 | 56.7371 | 56.6142 | 56.8342 | -66.3934 | -66.0789 | -4.7615 | -66.1683 | 56.6472 | 56.8113 | 56.7687 | -66.6028 | -0.16411 | -0.053013 | 0.15958 | 0.13336 | 0.29747 | -0.17598 | 0.044061 | -0.37354 | -0.14292 | 0.15036 | 0.060905 | 0.43444 | 0.02111 | -0.021475 | 122.9664 | 122.8434 | 123.0635 | 63.5659 | -123.1835 | 122.8765 | 123.0405 | 122.9979 | 61.4677 | -123.3929
924.2656 | 123.2346 | -66.1972 | 56.7398 | 0.057412 | -0.071497 | -0.0096467 | 0.046755 | -0.014884 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.053563 | 0.07134 | 0.052914 | -66.0742 | -2.6633 | -66.1005 | 56.728 | 56.6142 | 56.8342 | -66.3979 | -66.0835 | -4.7661 | -66.1683 | 56.6427 | 56.8067 | 56.7641 | -66.6028 | -0.20073 | -0.011816 | 0.12296 | 0.096738 | 0.29747 | -0.12562 | 0.094415 | -0.40558 | -0.097148 | 0.11373 | 0.028862 | 0.43444 | 0.066885 | 0.0243 | 122.9252 | 122.8114 | 123.0314 | 63.5339 | -123.1377 | 122.8399 | 123.0039 | 122.9613 | 61.4311 | -123.3426
925.2656 | 123.2666 | -66.2064 | 56.7398 | 0.04215 | -0.070429 | -0.0096467 | 0.047824 | -0.013815 | 0.055941 | 0.073406 | -0.0036447 | 0.0011204 | 0.052495 | 0.073476 | 0.053982 | -66.0742 | -2.6771 | -66.105 | 56.728 | 56.605 | 56.8205 | -66.4117 | -66.088 | -4.7752 | -66.1683 | 56.6381 | 56.793 | 56.7504 | -66.6028 | -0.20531 | -0.011816 | 0.13211 | 0.10131 | 0.30663 | -0.13478 | 0.08068 | -0.39643 | -0.10173 | 0.11831 | 0.038017 | 0.43444 | 0.053149 | 0.010565 | 122.9344 | 122.8114 | 123.0268 | 63.5293 | -123.1515 | 122.8444 | 122.9993 | 122.9567 | 61.4311 | -123.3426
926.2656 | 123.1979 | -66.2201 | 56.7169 | 0.04215 | -0.072565 | -0.010716 | 0.046755 | -0.014884 | 0.054873 | 0.042884 | -0.0047127 | 0.0011204 | 0.053563 | 0.073476 | 0.053982 | -66.088 | -2.6817 | -66.1142 | 56.7188 | 56.6004 | 56.8068 | -66.4163 | -66.1018 | -4.7752 | -66.1867 | 56.6335 | 56.7884 | 56.755 | -66.6119 | -0.19616 | 0.001915 | 0.13211 | 0.10589 | 0.30205 | -0.11647 | 0.089832 | -0.39185 | -0.083417 | 0.11831 | 0.033435 | 0.42529 | 0.071459 | 0.038031 | 122.9389 | 122.8205 | 123.0268 | 63.5384 | -123.1332 | 122.8536 | 123.0085 | 122.975 | 61.4449 | -123.3289
927.2656 | 123.2437 | -66.2247 | 56.7032 | 0.04215 | -0.071497 | -0.010716 | 0.047824 | -0.015952 | 0.052737 | 0.027623 | -0.0047127 | 0.0021894 | 0.050358 | 0.07134 | 0.052914 | -66.0971 | -2.6862 | -66.1188 | 56.7188 | 56.5913 | 56.8068 | -66.4208 | -66.1064 | -4.789 | -66.1912 | 56.6289 | 56.7838 | 56.7412 | -66.6257 | -0.19616 | 0.015648 | 0.12753 | 0.10589 | 0.30205 | -0.1119 | 0.10356 | -0.40101 | -0.074262 | 0.11831 | 0.033434 | 0.43444 | 0.080613 | 0.038028 | 122.9435 | 122.816 | 123.0314 | 63.5384 | -123.124 | 122.8536 | 123.0085 | 122.9659 | 61.4357 | -123.3289
928.2656 | 123.2666 | -66.2201 | 56.6895 | 0.011626 | -0.072565 | -0.0085787 | 0.04996 | -0.015952 | 0.053805 | 0.042884 | -0.0047127 | 0.0011204 | 0.050358 | 0.072408 | 0.052914 | -66.1017 | -2.7 | -66.1234 | 56.7143 | 56.6462 | 56.8022 | -66.4254 | -66.1109 | -4.7844 | -66.1958 | 56.6152 | 56.7838 | 56.7458 | -66.6257 | -0.20532 | 0.024803 | 0.11838 | 0.096734 | 0.30205 | -0.043219 | 0.11272 | -0.40559 | -0.074265 | 0.10915 | 0.024278 | 0.42987 | 0.094346 | 0.05634 | 122.9343 | 122.8663 | 123.0223 | 63.5201 | -123.1149 | 122.8353 | 123.0039 | 122.9659 | 61.4357 | -123.3151
929.2656 | 123.23 | -66.2247 | 56.7032 | 0.04215 | -0.070429 | -0.010716 | 0.046755 | -0.01702 | 0.053805 | 0.042884 | -0.0057807 | 0.0032574 | 0.053563 | 0.07134 | 0.052914 | -66.1063 | -2.7 | -66.1234 | 56.7097 | 56.6508 | 56.8022 | -66.4346 | -66.1155 | -4.7707 | -66.1958 | 56.6152 | 56.7746 | 56.7412 | -66.6348 | -0.2099 | 0.006491 | 0.11838 | 0.10131 | 0.31121 | -0.052373 | 0.098986 | -0.41017 | -0.087998 | 0.10915 | 0.028855 | 0.43902 | 0.071456 | 0.038028 | 122.9343 | 122.8755 | 123.0268 | 63.5247 | -123.1378 | 122.8399 | 122.9993 | 122.9659 | 61.454 | -123.338
930.2656 | 123.2391 | -66.2567 | 56.6757 | 0.057412 | -0.071497 | -0.0085787 | 0.046755 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.051427 | 0.073476 | 0.053982 | -66.1063 | -2.7137 | -66.1325 | 56.7051 | 56.6371 | 56.7976 | -66.4346 | -66.1201 | -4.7707 | -66.205 | 56.606 | 56.7701 | 56.7275 | -66.6394 | -0.17785 | 0.029379 | 0.15042 | 0.1242 | 0.30205 | -0.038643 | 0.12187 | -0.3827 | -0.069689 | 0.13661 | 0.051742 | 0.43444 | 0.094343 | 0.051759 | 122.9618 | 122.8938 | 123.0543 | 63.543 | -123.1103 | 122.8627 | 123.0268 | 122.9842 | 61.4861 | -123.3151
931.2656 | 123.1705 | -66.2247 | 56.6711 | 0.026888 | -0.071497 | -0.0085787 | 0.047824 | -0.015952 | 0.055941 | 0.058145 | -0.0057807 | 0.0021894 | 0.053563 | 0.072408 | 0.052914 | -66.1109 | -2.6954 | -66.1417 | 56.7005 | 56.6417 | 56.793 | -66.4483 | -66.1293 | -4.7752 | -66.2187 | 56.5969 | 56.7701 | 56.7321 | -66.6486 | -0.22364 | 0.029378 | 0.1138 | 0.082998 | 0.30663 | -0.029487 | 0.12187 | -0.4239 | -0.074269 | 0.095411 | 0.005962 | 0.42987 | 0.09892 | 0.060914 | 122.9252 | 122.8663 | 123.0177 | 63.5293 | -123.1194 | 122.8215 | 122.9947 | 122.9567 | 61.4494 | -123.3197
932.2656 | 123.23 | -66.2521 | 56.6895 | 0.04215 | -0.072565 | -0.0096467 | 0.047824 | -0.013815 | 0.054873 | 0.058145 | -0.0057807 | 0.0021894 | 0.052495 | 0.074545 | 0.051845 | -66.1155 | -2.7137 | -66.1417 | 56.6914 | 56.6462 | 56.7839 | -66.4483 | -66.1293 | -4.7661 | -66.2187 | 56.5969 | 56.7746 | 56.7321 | -66.644 | -0.19617 | 0.001911 | 0.13668 | 0.11046 | 0.30663 | -0.043219 | 0.094405 | -0.39186 | -0.092579 | 0.12288 | 0.033428 | 0.42529 | 0.085189 | 0.042604 | 122.9435 | 122.8984 | 123.036 | 63.5384 | -123.1378 | 122.849 | 123.0268 | 122.9842 | 61.4861 | -123.3334
933.2656 | 123.2437 | -66.2521 | 56.662 | 0.026888 | -0.070429 | -0.0085787 | 0.047824 | -0.015952 | 0.053805 | 0.058145 | -0.0068487 | 5.2373e-05 | 0.051427 | 0.073476 | 0.053982 | -66.1292 | -2.7137 | -66.1554 | 56.6959 | 56.6417 | 56.7884 | -66.4529 | -66.143 | -4.7615 | -66.2233 | 56.5969 | 56.7472 | 56.7183 | -66.6577 | -0.20075 | 0.033955 | 0.12295 | 0.096729 | 0.29748 | -0.020331 | 0.12645 | -0.4056 | -0.065113 | 0.10914 | 0.028849 | 0.43444 | 0.085183 | 0.056334 | 122.9481 | 122.8938 | 123.0406 | 63.5384 | -123.1149 | 122.849 | 122.9993 | 122.9705 | 61.4906 | -123.3197
934.2656 | 123.2529 | -66.2521 | 56.6711 | 0.04215 | -0.073634 | -0.0096467 | 0.04996 | -0.015952 | 0.05701 | 0.042884 | -0.0057807 | 0.0011204 | 0.051427 | 0.072408 | 0.053982 | -66.1338 | -2.7274 | -66.1554 | 56.6959 | 56.6371 | 56.7839 | -66.4575 | -66.143 | -4.7615 | -66.2187 | 56.5877 | 56.7517 | 56.7275 | -66.6577 | -0.20533 | 0.024799 | 0.11837 | 0.096729 | 0.30206 | -0.034066 | 0.11272 | -0.4056 | -0.083426 | 0.10914 | 0.033428 | 0.43902 | 0.080606 | 0.056336 | 122.9481 | 122.8892 | 123.036 | 63.5247 | -123.1286 | 122.8399 | 123.0039 | 122.9796 | 61.4906 | -123.3289
935.2656 | 123.1979 | -66.2842 | 56.6574 | 0.04215 | -0.072565 | -0.0096467 | 0.047824 | -0.015952 | 0.053805 | 0.042884 | -0.0057807 | 0.0011204 | 0.050358 | 0.072408 | 0.052914 | -66.1338 | -2.7229 | -66.1646 | 56.6776 | 56.6417 | 56.7839 | -66.4712 | -66.143 | -4.7523 | -66.237 | 56.5877 | 56.7472 | 56.7092 | -66.6623 | -0.18702 | 0.020219 | 0.15042 | 0.11962 | 0.30664 | -0.015754 | 0.12645 | -0.37813 | -0.069693 | 0.14119 | 0.047157 | 0.42529 | 0.08976 | 0.051754 | 122.9618 | 122.9258 | 123.068 | 63.5613 | -123.1286 | 122.8719 | 123.0314 | 122.9933 | 61.5318 | -123.3197
936.2656 | 123.2437 | -66.2613 | 56.6574 | 0.04215 | -0.071497 | -0.0085787 | 0.046755 | -0.015952 | 0.055941 | 0.027623 | -0.0057807 | 0.0032574 | 0.052495 | 0.07134 | 0.052914 | -66.1292 | -2.732 | -66.1737 | 56.6776 | 56.6233 | 56.7655 | -66.4758 | -66.1476 | -4.7478 | -66.237 | 56.5831 | 56.7426 | 56.7137 | -66.6715 | -0.21449 | 0.020219 | 0.1321 | 0.087572 | 0.30206 | -0.03407 | 0.10813 | -0.41018 | -0.074271 | 0.11372 | 0.024269 | 0.43445 | 0.085182 | 0.056333 | 122.9389 | 122.8846 | 123.0268 | 63.5293 | -123.1332 | 122.8444 | 123.0039 | 122.975 | 61.5135 | -123.3289
937.2656 | 123.2437 | -66.2796 | 56.6437 | 0.026888 | -0.071497 | -0.0096467 | 0.048892 | -0.014884 | 0.053805 | 0.042884 | -0.0036447 | 0.0021894 | 0.052495 | 0.072408 | 0.05505 | -66.1475 | -2.7274 | -66.1737 | 56.6822 | 56.6233 | 56.7655 | -66.4758 | -66.1567 | -4.7478 | -66.2416 | 56.5831 | 56.7426 | 56.7046 | -66.6669 | -0.19618 | 0.03853 | 0.1321 | 0.10588 | 0.30206 | -0.020337 | 0.12187 | -0.38729 | -0.060538 | 0.12287 | 0.038 | 0.42529 | 0.098915 | 0.060909 | 122.9618 | 122.9029 | 123.0451 | 63.5522 | -123.1195 | 122.8627 | 123.0222 | 122.9842 | 61.5318 | -123.3106
938.2656 | 123.2529 | -66.2704 | 56.6345 | 0.04215 | -0.072565 | -0.010716 | 0.046755 | -0.013815 | 0.055941 | 0.058145 | -0.0057807 | 0.0032574 | 0.051427 | 0.072408 | 0.053982 | -66.1521 | -2.7366 | -66.1829 | 56.6685 | 56.6279 | 56.761 | -66.4804 | -66.1705 | -4.7386 | -66.2508 | 56.5694 | 56.7334 | 56.7 | -66.676 | -0.20991 | 0.033951 | 0.11837 | 0.087571 | 0.29748 | -0.006602 | 0.12644 | -0.4056 | -0.065118 | 0.09998 | 0.019688 | 0.42529 | 0.098913 | 0.065486 | 122.9389 | 122.8984 | 123.0314 | 63.5338 | -123.1149 | 122.8399 | 123.0039 | 122.9705 | 61.5318 | -123.3106
939.2656 | 123.2254 | -66.2933 | 56.6483 | 0.026888 | -0.071497 | -0.0096467 | 0.046755 | -0.014884 | 0.054873 | 0.027623 | -0.0057807 | 5.2373e-05 | 0.051427 | 0.072408 | 0.053982 | -66.1567 | -2.7274 | -66.1875 | 56.6685 | 56.5959 | 56.7564 | -66.4895 | -66.1705 | -4.734 | -66.2508 | 56.5602 | 56.7289 | 56.6908 | -66.676 | -0.19618 | 0.020218 | 0.13668 | 0.10588 | 0.30206 | -0.052388 | 0.10813 | -0.38271 | -0.088008 | 0.12287 | 0.042576 | 0.42529 | 0.080602 | 0.042596 | 122.9618 | 122.8892 | 123.0497 | 63.5659 | -123.1378 | 122.8536 | 123.0222 | 122.9842 | 61.5593 | -123.3243
940.2656 | 123.2162 | -66.3025 | 56.6528 | 0.011626 | -0.073634 | -0.0075097 | 0.047824 | -0.015952 | 0.054873 | 0.073406 | -0.0047127 | 0.0021894 | 0.051427 | 0.074545 | 0.052914 | -66.1521 | -2.7366 | -66.1783 | 56.6593 | 56.5867 | 56.761 | -66.4895 | -66.175 | -4.7249 | -66.2553 | 56.5602 | 56.7243 | 56.6954 | -66.6852 | -0.18703 | 0.006483 | 0.15041 | 0.12419 | 0.31122 | -0.066124 | 0.10813 | -0.38271 | -0.092586 | 0.12744 | 0.047152 | 0.42987 | 0.071445 | 0.042596 | 122.9618 | 122.8892 | 123.0635 | 63.5659 | -123.1423 | 122.8627 | 123.0268 | 122.9979 | 61.5776 | -123.338
941.2656 | 123.111 | -66.3391 | 56.6391 | 0.026888 | -0.073634 | -0.0085787 | 0.047824 | -0.015952 | 0.053805 | 0.058145 | -0.0047127 | 0.0021894 | 0.052495 | 0.073476 | 0.053982 | -66.1704 | -2.7412 | -66.1966 | 56.6502 | 56.5409 | 56.7426 | -66.4941 | -66.1705 | -4.7157 | -66.2691 | 56.5511 | 56.7151 | 56.6817 | -66.6898 | -0.15498 | 0.011059 | 0.16872 | 0.1425 | 0.29748 | -0.09818 | 0.10355 | -0.35067 | -0.08801 | 0.16864 | 0.070037 | 0.42071 | 0.076021 | 0.042594 | 122.9893 | 122.88 | 123.0818 | 63.5979 | -123.1332 | 122.8902 | 123.0542 | 123.0208 | 61.6234 | -123.3289
942.2656 | 123.111 | -66.3437 | 56.6574 | 0.04215 | -0.070429 | -0.0096467 | 0.048892 | -0.015952 | 0.052737 | 0.042884 | -0.0047127 | 0.0021894 | 0.051427 | 0.074545 | 0.052914 | -66.1704 | -2.7503 | -66.2058 | 56.641 | 56.5363 | 56.7335 | -66.4941 | -66.1934 | -4.7157 | -66.2691 | 56.5465 | 56.7105 | 56.6634 | -66.6944 | -0.15041 | -0.016408 | 0.1733 | 0.13792 | 0.28833 | -0.12107 | 0.076083 | -0.35067 | -0.1109 | 0.15033 | 0.074615 | 0.42529 | 0.053131 | 0.005968 | 122.9847 | 122.88 | 123.0772 | 63.5934 | -123.1515 | 122.8902 | 123.0542 | 123.0071 | 61.628 | -123.3518
943.2656 | 123.1476 | -66.3483 | 56.6757 | 0.04215 | -0.072565 | -0.0085787 | 0.047824 | -0.014884 | 0.053805 | 0.058145 | -0.0036447 | 0.0021894 | 0.050358 | 0.074545 | 0.053982 | -66.175 | -2.7549 | -66.2012 | 56.6456 | 56.518 | 56.7381 | -66.4941 | -66.1979 | -4.7066 | -66.2691 | 56.5511 | 56.7151 | 56.6725 | -66.7035 | -0.14583 | -0.03014 | 0.1733 | 0.14708 | 0.29291 | -0.15769 | 0.062352 | -0.35525 | -0.12463 | 0.15033 | 0.079193 | 0.43445 | 0.0394 | -0.003185 | 122.9938 | 122.8663 | 123.0863 | 63.5934 | -123.1698 | 122.8994 | 123.0634 | 123.0208 | 61.6417 | -123.3792
944.2656 | 123.1613 | -66.3528 | 56.6116 | 0.04215 | -0.072565 | -0.0085787 | 0.047824 | -0.014884 | 0.053805 | 0.027623 | -0.0047127 | 0.0021894 | 0.053563 | 0.073476 | 0.05505 | -66.1887 | -2.7595 | -66.2058 | 56.6456 | 56.5134 | 56.7243 | -66.4987 | -66.1934 | -4.702 | -66.2737 | 56.5374 | 56.7151 | 56.6542 | -66.7035 | -0.14583 | 0.033947 | 0.16414 | 0.14708 | 0.2929 | -0.098187 | 0.1127 | -0.35068 | -0.074279 | 0.15948 | 0.079191 | 0.42987 | 0.10349 | 0.042588 | 122.9984 | 122.8663 | 123.0772 | 63.5934 | -123.1103 | 122.8902 | 123.068 | 123.0071 | 61.6509 | -123.3152
945.2656 | 123.1842 | -66.3437 | 56.6391 | 0.04215 | -0.071497 | -0.0096467 | 0.047824 | -0.01702 | 0.054873 | 0.073406 | -0.0057807 | 0.0011204 | 0.051427 | 0.073476 | 0.052914 | -66.1841 | -2.7641 | -66.2103 | 56.6273 | 56.5089 | 56.7198 | -66.5078 | -66.2025 | -4.702 | -66.2782 | 56.5465 | 56.7014 | 56.6588 | -66.7081 | -0.16414 | -0.011833 | 0.15956 | 0.13334 | 0.29748 | -0.13023 | 0.080658 | -0.36441 | -0.092588 | 0.14117 | 0.065457 | 0.42987 | 0.062285 | 0.019701 | 122.971 | 122.8526 | 123.0634 | 63.5796 | -123.1469 | 122.8902 | 123.0451 | 123.0025 | 61.6417 | -123.3472
946.2656 | 123.111 | -66.3666 | 56.6483 | 0.057412 | -0.070429 | -0.010716 | 0.051029 | -0.015952 | 0.053805 | 0.073406 | -0.0057807 | 0.0011204 | 0.052495 | 0.074545 | 0.053982 | -66.1887 | -2.7824 | -66.2195 | 56.6318 | 56.5089 | 56.7243 | -66.5078 | -66.2117 | -4.6928 | -66.292 | 56.5282 | 56.6968 | 56.6588 | -66.7035 | -0.14125 | -0.016409 | 0.17787 | 0.14707 | 0.28833 | -0.13939 | 0.076082 | -0.33694 | -0.12006 | 0.1549 | 0.074609 | 0.41155 | 0.048552 | 0.010546 | 122.9984 | 122.8754 | 123.0909 | 63.5842 | -123.1561 | 122.8948 | 123.0634 | 123.0254 | 61.6738 | -123.3518
947.2656 | 123.143 | -66.362 | 56.6299 | 0.026888 | -0.074702 | -0.010716 | 0.047824 | -0.013815 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.051427 | 0.075613 | 0.051845 | -66.2024 | -2.7824 | -66.2241 | 56.6273 | 56.4997 | 56.7106 | -66.517 | -66.2117 | -4.6882 | -66.292 | 56.5282 | 56.6968 | 56.6496 | -66.7218 | -0.15499 | -0.002678 | 0.15956 | 0.13792 | 0.29291 | -0.13023 | 0.080656 | -0.35984 | -0.10175 | 0.15032 | 0.070032 | 0.42987 | 0.066862 | 0.019698 | 122.9893 | 122.8617 | 123.0726 | 63.5796 | -123.1469 | 122.8902 | 123.0588 | 123.0116 | 61.6738 | -123.3518
948.2656 | 123.1567 | -66.3437 | 56.6528 | 0.04215 | -0.071497 | -0.0085787 | 0.04996 | -0.014884 | 0.052737 | 0.042884 | -0.0057807 | 0.0011204 | 0.052495 | 0.075613 | 0.051845 | -66.2024 | -2.8053 | -66.2241 | 56.6227 | 56.4997 | 56.7198 | -66.5261 | -66.2163 | -4.6882 | -66.3057 | 56.5236 | 56.6785 | 56.6542 | -66.7173 | -0.18246 | -0.030144 | 0.14125 | 0.11961 | 0.30207 | -0.15312 | 0.066925 | -0.37357 | -0.12921 | 0.12743 | 0.037985 | 0.41155 | 0.025659 | 0.001389 | 122.9664 | 122.8434 | 123.0634 | 63.5384 | -123.179 | 122.8673 | 123.0222 | 122.9979 | 61.6554 | -123.3701
949.2656 | 123.1705 | -66.3483 | 56.6208 | 0.057412 | -0.073634 | -0.0096467 | 0.046755 | -0.013815 | 0.053805 | 0.058145 | -0.0047127 | 0.0021894 | 0.053563 | 0.073476 | 0.052914 | -66.207 | -2.8144 | -66.2424 | 56.6135 | 56.518 | 56.7152 | -66.5307 | -66.2254 | -4.6745 | -66.3057 | 56.519 | 56.6876 | 56.6451 | -66.7356 | -0.18246 | -0.007258 | 0.14125 | 0.10587 | 0.28833 | -0.10276 | 0.09439 | -0.3873 | -0.10175 | 0.12286 | 0.042563 | 0.42987 | 0.066859 | 0.024275 | 122.9618 | 122.8663 | 123.0634 | 63.5338 | -123.1515 | 122.8673 | 123.0359 | 122.9933 | 61.6738 | -123.3564
950.2656 | 123.1476 | -66.3849 | 56.6299 | 0.026888 | -0.073634 | -0.0085787 | 0.047824 | -0.015952 | 0.053805 | 0.027623 | -0.0068487 | 0.0011204 | 0.050358 | 0.075613 | 0.053982 | -66.2208 | -2.8465 | -66.2332 | 56.6044 | 56.5501 | 56.706 | -66.5307 | -66.2391 | -4.6699 | -66.3149 | 56.5053 | 56.6739 | 56.6405 | -66.731 | -0.14584 | -0.025569 | 0.16413 | 0.15165 | 0.29749 | -0.079867 | 0.076077 | -0.3461 | -0.12464 | 0.14574 | 0.070027 | 0.41613 | 0.043969 | 0.010541 | 122.9893 | 122.935 | 123.0909 | 63.5384 | -123.1607 | 122.8902 | 123.0588 | 123.0254 | 61.715 | -123.3609
951.2656 | 123.1476 | -66.3574 | 56.662 | 0.04215 | -0.074702 | -0.0085787 | 0.048892 | -0.015952 | 0.054873 | 0.088667 | -0.0047127 | 0.0032574 | 0.050358 | 0.075613 | 0.051845 | -66.2208 | -2.8602 | -66.2516 | 56.6181 | 56.5547 | 56.7014 | -66.549 | -66.2437 | -4.6653 | -66.3286 | 56.5099 | 56.6602 | 56.6313 | -66.7356 | -0.19162 | -0.043877 | 0.13667 | 0.10587 | 0.29749 | -0.10733 | 0.039456 | -0.37815 | -0.1521 | 0.11369 | 0.028824 | 0.40697 | -0.00181 | -0.030659 | 122.9755 | 122.9121 | 123.0589 | 63.4972 | -123.211 | 122.8673 | 123.0176 | 122.9888 | 61.6921 | -123.3976
952.2656 | 123.1476 | -66.3895 | 56.6254 | 0.057412 | -0.074702 | -0.0096467 | 0.046755 | -0.015952 | 0.054873 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.050358 | 0.074545 | 0.053982 | -66.2299 | -2.8556 | -66.2561 | 56.6135 | 56.5547 | 56.6923 | -66.5536 | -66.2437 | -4.6699 | -66.324 | 56.5007 | 56.6693 | 56.6313 | -66.7356 | -0.16416 | -0.011835 | 0.15955 | 0.13334 | 0.29749 | -0.07071 | 0.06692 | -0.34611 | -0.12464 | 0.14574 | 0.065446 | 0.41155 | 0.043968 | 0.005962 | 123.003 | 122.9441 | 123.0818 | 63.5338 | -123.179 | 122.8902 | 123.0588 | 123.0208 | 61.7195 | -123.3609
953.2656 | 123.1522 | -66.3712 | 56.5933 | 0.026888 | -0.071497 | -0.0075097 | 0.047824 | -0.015952 | 0.054873 | 0.058145 | -0.0068487 | 0.0032574 | 0.052495 | 0.074545 | 0.053982 | -66.2299 | -2.8694 | -66.2516 | 56.5998 | 56.5409 | 56.6969 | -66.5582 | -66.2483 | -4.6562 | -66.3332 | 56.5099 | 56.6648 | 56.6359 | -66.7447 | -0.18704 | 0.006473 | 0.14124 | 0.1196 | 0.30665 | -0.052404 | 0.10354 | -0.37358 | -0.08344 | 0.12285 | 0.037979 | 0.41155 | 0.071432 | 0.042584 | 122.971 | 122.9121 | 123.068 | 63.5018 | -123.1515 | 122.881 | 123.0359 | 123.0071 | 61.715 | -123.3381
954.2656 | 123.1796 | -66.3712 | 56.6025 | 0.026888 | -0.074702 | -0.010716 | 0.048892 | -0.015952 | 0.053805 | 0.073406 | -0.0057807 | 0.0011204 | 0.051427 | 0.074545 | 0.052914 | -66.2345 | -2.8556 | -66.2607 | 56.5952 | 56.5409 | 56.6923 | -66.5536 | -66.2529 | -4.647 | -66.3332 | 56.4961 | 56.6602 | 56.6313 | -66.7585 | -0.18247 | -0.00726 | 0.13667 | 0.11045 | 0.29291 | -0.061559 | 0.089808 | -0.38731 | -0.10633 | 0.11827 | 0.037979 | 0.42529 | 0.057699 | 0.02885 | 122.9664 | 122.9121 | 123.0634 | 63.5155 | -123.1561 | 122.8673 | 123.0313 | 123.0025 | 61.7241 | -123.3609
955.2656 | 123.1796 | -66.3986 | 56.5933 | 0.057412 | -0.072565 | -0.0096467 | 0.048892 | -0.015952 | 0.053805 | 0.073406 | -0.0047127 | 0.0021894 | 0.051427 | 0.074545 | 0.053982 | -66.2391 | -2.8465 | -66.2561 | 56.5906 | 56.5409 | 56.6831 | -66.5582 | -66.2529 | -4.6379 | -66.3378 | 56.4961 | 56.651 | 56.613 | -66.7539 | -0.15958 | -0.002684 | 0.15955 | 0.14249 | 0.30207 | -0.052404 | 0.089805 | -0.35527 | -0.097176 | 0.14574 | 0.060866 | 0.41613 | 0.057697 | 0.019691 | 122.9893 | 122.9395 | 123.0817 | 63.5521 | -123.1515 | 122.8948 | 123.0496 | 123.0116 | 61.7607 | -123.3472
956.2656 | 123.1155 | -66.3803 | 56.6345 | 0.026888 | -0.073634 | -0.0096467 | 0.04996 | -0.01702 | 0.054873 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.050358 | 0.073476 | 0.050777 | -66.2482 | -2.8373 | -66.2653 | 56.5861 | 56.5363 | 56.6786 | -66.5582 | -66.262 | -4.6425 | -66.3378 | 56.4824 | 56.651 | 56.6267 | -66.763 | -0.17789 | -0.04846 | 0.13208 | 0.11502 | 0.29291 | -0.098181 | 0.044029 | -0.38274 | -0.15211 | 0.11827 | 0.042555 | 0.42529 | 0.016499 | -0.007772 | 122.9664 | 122.9167 | 123.0589 | 63.543 | -123.1927 | 122.8627 | 123.0313 | 123.0071 | 61.7379 | -123.3976
957.2656 | 123.175 | -66.3803 | 56.6116 | 0.026888 | -0.07577 | -0.010716 | 0.048892 | -0.013815 | 0.052737 | 0.058145 | -0.0079177 | 0.0021894 | 0.052495 | 0.075613 | 0.053982 | -66.2391 | -2.819 | -66.2653 | 56.5861 | 56.5318 | 56.6786 | -66.5628 | -66.2712 | -4.6516 | -66.3378 | 56.4916 | 56.6464 | 56.6222 | -66.7676 | -0.18247 | -0.025572 | 0.14124 | 0.11502 | 0.29749 | -0.079872 | 0.066917 | -0.38731 | -0.12006 | 0.10911 | 0.042555 | 0.42987 | 0.034808 | 0.010538 | 122.9664 | 122.9121 | 123.0589 | 63.5613 | -123.1744 | 122.8719 | 123.0268 | 123.0025 | 61.7287 | -123.3793
958.2656 | 123.175 | -66.3849 | 56.5842 | 0.026888 | -0.074702 | -0.010716 | 0.048892 | -0.01702 | 0.054873 | 0.073406 | -0.0068487 | 5.2373e-05 | 0.051427 | 0.074545 | 0.051845 | -66.2482 | -2.8053 | -66.279 | 56.5906 | 56.5226 | 56.6786 | -66.5674 | -66.262 | -4.647 | -66.3515 | 56.4824 | 56.6464 | 56.6176 | -66.7539 | -0.18247 | 0.006472 | 0.13666 | 0.10587 | 0.28834 | -0.061563 | 0.094383 | -0.369 | -0.10176 | 0.12285 | 0.033397 | 0.4024 | 0.062274 | 0.033425 | 122.9755 | 122.9075 | 123.0634 | 63.5796 | -123.1515 | 122.8673 | 123.0313 | 123.0025 | 61.7379 | -123.3381
959.2656 | 123.2071 | -66.3712 | 56.5704 | 0.04215 | -0.07577 | -0.0096467 | 0.048892 | -0.014884 | 0.055941 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.051427 | 0.075613 | 0.053982 | -66.2482 | -2.7824 | -66.2744 | 56.5815 | 56.5318 | 56.674 | -66.5719 | -66.2712 | -4.6425 | -66.3515 | 56.4824 | 56.6419 | 56.613 | -66.7676 | -0.20078 | 0.011048 | 0.12293 | 0.096713 | 0.29749 | -0.038674 | 0.10354 | -0.39647 | -0.088023 | 0.099956 | 0.019664 | 0.41613 | 0.071427 | 0.042579 | 122.9526 | 122.9029 | 123.0451 | 63.5888 | -123.1424 | 122.8536 | 123.013 | 122.9842 | 61.7287 | -123.3381
960.2656 | 123.1705 | -66.3803 | 56.6025 | 0.087936 | -0.074702 | -0.010716 | 0.047824 | -0.01702 | 0.053805 | 0.042884 | -0.0047127 | 0.0011204 | 0.051427 | 0.075613 | 0.052914 | -66.2528 | -2.7732 | -66.2744 | 56.5677 | 56.5272 | 56.6694 | -66.5674 | -66.2758 | -4.6562 | -66.3469 | 56.4824 | 56.6373 | 56.6039 | -66.7722 | -0.18705 | -0.034731 | 0.12751 | 0.10587 | 0.29292 | -0.075296 | 0.066915 | -0.39189 | -0.12007 | 0.10453 | 0.033398 | 0.42529 | 0.034806 | 0.001378 | 122.9481 | 122.9075 | 123.0497 | 63.6071 | -123.1698 | 122.8627 | 123.0176 | 122.9842 | 61.7241 | -123.3747
961.2656 | 123.143 | -66.3986 | 56.6116 | 0.04215 | -0.074702 | -0.0096467 | 0.048892 | -0.014884 | 0.053805 | 0.058145 | -0.0057807 | 0.0032574 | 0.050358 | 0.074545 | 0.052914 | -66.2528 | -2.7686 | -66.279 | 56.5815 | 56.5226 | 56.6694 | -66.5765 | -66.2804 | -4.6516 | -66.3469 | 56.4778 | 56.6327 | 56.613 | -66.7722 | -0.17789 | -0.03015 | 0.14582 | 0.1196 | 0.29749 | -0.089029 | 0.05776 | -0.37358 | -0.1338 | 0.11827 | 0.051709 | 0.42529 | 0.021072 | 0.001381 | 122.9801 | 122.9212 | 123.068 | 63.63 | -123.1881 | 122.8765 | 123.0313 | 123.0116 | 61.747 | -123.3838
962.2656 | 123.1293 | -66.394 | 56.5933 | 0.057412 | -0.074702 | -0.0096467 | 0.048892 | -0.015952 | 0.055941 | 0.073406 | -0.0057807 | 0.0011204 | 0.051427 | 0.075613 | 0.052914 | -66.2528 | -2.7549 | -66.2836 | 56.5677 | 56.5134 | 56.6648 | -66.5765 | -66.2804 | -4.6562 | -66.3469 | 56.4733 | 56.6419 | 56.6039 | -66.7722 | -0.18247 | -0.025576 | 0.14124 | 0.11044 | 0.29292 | -0.079877 | 0.071491 | -0.37816 | -0.12007 | 0.11369 | 0.047131 | 0.42529 | 0.048539 | 0.010533 | 122.9618 | 122.9075 | 123.0589 | 63.6391 | -123.1698 | 122.8673 | 123.0359 | 122.9979 | 61.7379 | -123.3655
963.2656 | 123.1384 | -66.4078 | 56.5887 | 0.026888 | -0.074702 | -0.0085787 | 0.048892 | -0.01702 | 0.053805 | 0.058145 | -0.0057807 | 0.0032574 | 0.051427 | 0.074545 | 0.052914 | -66.2574 | -2.7458 | -66.279 | 56.5723 | 56.5089 | 56.6602 | -66.5811 | -66.2804 | -4.6608 | -66.3652 | 56.4687 | 56.6327 | 56.5993 | -66.7722 | -0.17332 | -0.016419 | 0.15039 | 0.12876 | 0.30207 | -0.079878 | 0.07149 | -0.36443 | -0.12007 | 0.12742 | 0.042549 | 0.40698 | 0.04396 | 0.010533 | 122.9801 | 122.9166 | 123.068 | 63.662 | -123.1698 | 122.8765 | 123.0405 | 123.0071 | 61.747 | -123.3609
964.2656 | 123.1201 | -66.4124 | 56.6208 | 0.04215 | -0.074702 | -0.0096467 | 0.047824 | -0.014884 | 0.053805 | 0.042884 | -0.0047127 | 0.0011204 | 0.051427 | 0.075613 | 0.052914 | -66.2665 | -2.7274 | -66.2928 | 56.5677 | 56.5134 | 56.6557 | -66.5811 | -66.2849 | -4.6562 | -66.3606 | 56.4733 | 56.6235 | 56.5993 | -66.7768 | -0.16874 | -0.053042 | 0.14582 | 0.1196 | 0.28834 | -0.10734 | 0.034868 | -0.36443 | -0.14753 | 0.12742 | 0.051706 | 0.41613 | 0.002759 | -0.021511 | 122.9801 | 122.9258 | 123.068 | 63.6849 | -123.2019 | 122.8856 | 123.0359 | 123.0116 | 61.7562 | -123.3976
965.2656 | 123.1567 | -66.4124 | 56.6162 | 0.04215 | -0.073634 | -0.010716 | 0.047824 | -0.015952 | 0.054873 | 0.042884 | -0.0057807 | 0.0032574 | 0.052495 | 0.074545 | 0.052914 | -66.2574 | -2.7137 | -66.2882 | 56.5586 | 56.518 | 56.6648 | -66.5765 | -66.2895 | -4.6653 | -66.3652 | 56.4687 | 56.6281 | 56.5993 | -66.7814 | -0.16416 | -0.05762 | 0.15497 | 0.12418 | 0.28834 | -0.098186 | 0.048603 | -0.36901 | -0.14753 | 0.12284 | 0.047127 | 0.41613 | 0.011916 | -0.016933 | 122.9709 | 122.9304 | 123.0772 | 63.6986 | -123.1927 | 122.881 | 123.0405 | 123.0116 | 61.747 | -123.3976
966.2656 | 123.1247 | -66.394 | 56.5887 | 0.04215 | -0.074702 | -0.0096467 | 0.048892 | -0.015952 | 0.054873 | 0.042884 | -0.0057807 | 0.0021894 | 0.052495 | 0.075613 | 0.053982 | -66.2711 | -2.7045 | -66.2928 | 56.5632 | 56.518 | 56.6602 | -66.5857 | -66.2987 | -4.6653 | -66.3698 | 56.4733 | 56.6281 | 56.5947 | -66.7859 | -0.19163 | -0.025576 | 0.12293 | 0.10129 | 0.29292 | -0.07072 | 0.07149 | -0.3919 | -0.11549 | 0.095372 | 0.024237 | 0.41613 | 0.039382 | 0.005954 | 122.9572 | 122.9121 | 123.0543 | 63.6895 | -123.1744 | 122.8673 | 123.0222 | 122.9887 | 61.7287 | -123.3747
967.2656 | 123.1338 | -66.4169 | 56.6208 | 0.04215 | -0.073634 | -0.0096467 | 0.048892 | -0.018088 | 0.053805 | 0.073406 | -0.0047127 | 0.0021894 | 0.051427 | 0.076681 | 0.052914 | -66.2711 | -2.6954 | -66.2973 | 56.5632 | 56.518 | 56.6602 | -66.5903 | -66.2941 | -4.6699 | -66.3652 | 56.4687 | 56.6144 | 56.5993 | -66.7814 | -0.17332 | -0.05762 | 0.14581 | 0.1196 | 0.29292 | -0.10276 | 0.039446 | -0.36443 | -0.15211 | 0.12284 | 0.051704 | 0.41613 | -0.006398 | -0.021511 | 122.9801 | 122.935 | 123.0772 | 63.7215 | -123.211 | 122.8856 | 123.0313 | 123.0162 | 61.747 | -123.4021
968.2656 | 123.2437 | -66.394 | 56.5796 | 0.057412 | -0.074702 | -0.010716 | 0.048892 | -0.015952 | 0.051668 | 0.073406 | -0.0057807 | 0.0011204 | 0.051427 | 0.074545 | 0.052914 | -66.2803 | -2.6862 | -66.2928 | 56.5677 | 56.5043 | 56.6648 | -66.5948 | -66.2987 | -4.6653 | -66.3698 | 56.4549 | 56.619 | 56.5947 | -66.7951 | -0.20079 | -0.011843 | 0.11377 | 0.10129 | 0.30208 | -0.075302 | 0.085224 | -0.40105 | -0.12465 | 0.095372 | 0.024237 | 0.42529 | 0.039379 | 0.015109 | 122.9618 | 122.8983 | 123.0589 | 63.7078 | -123.1744 | 122.849 | 123.013 | 122.9887 | 61.7287 | -123.3747
969.2656 | 123.1979 | -66.362 | 56.5796 | 0.04215 | -0.074702 | -0.0085787 | 0.04996 | -0.015952 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.051427 | 0.076681 | 0.052914 | -66.2803 | -2.6725 | -66.2928 | 56.5632 | 56.5089 | 56.6557 | -66.5903 | -66.3078 | -4.6608 | -66.379 | 56.4595 | 56.619 | 56.5901 | -66.7905 | -0.22825 | -0.016421 | 0.081726 | 0.069245 | 0.2975 | -0.070723 | 0.076067 | -0.42852 | -0.12007 | 0.054172 | -0.016963 | 0.41156 | 0.039379 | 0.010531 | 122.9252 | 122.8709 | 123.0177 | 63.6895 | -123.1698 | 122.8215 | 122.981 | 122.9521 | 61.7012 | -123.3701
970.2656 | 123.1476 | -66.4124 | 56.5933 | 0.04215 | -0.073634 | -0.0085787 | 0.046755 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 5.2373e-05 | 0.050358 | 0.074545 | 0.051845 | -66.2803 | -2.6633 | -66.2928 | 56.554 | 56.4997 | 56.6511 | -66.5948 | -66.3033 | -4.6699 | -66.379 | 56.4687 | 56.619 | 56.5901 | -66.7951 | -0.18248 | -0.039311 | 0.13208 | 0.1196 | 0.30208 | -0.093614 | 0.057755 | -0.38274 | -0.12465 | 0.1091 | 0.033391 | 0.41613 | 0.025646 | -0.003202 | 122.9664 | 122.9121 | 123.0634 | 63.749 | -123.1882 | 122.881 | 123.0313 | 123.0025 | 61.7424 | -123.3884
971.2656 | 123.1247 | -66.4169 | 56.5933 | 0.057412 | -0.07577 | -0.010716 | 0.048892 | -0.014884 | 0.052737 | 0.073406 | -0.0047127 | 0.0021894 | 0.051427 | 0.074545 | 0.052914 | -66.2803 | -2.6588 | -66.3019 | 56.5677 | 56.5089 | 56.6557 | -66.5948 | -66.3078 | -4.6745 | -66.379 | 56.4504 | 56.6098 | 56.5901 | -66.7951 | -0.1779 | -0.025576 | 0.13666 | 0.11502 | 0.29292 | -0.084456 | 0.062334 | -0.37817 | -0.14296 | 0.1091 | 0.037968 | 0.41613 | 0.016489 | -0.003202 | 122.9847 | 122.9258 | 123.0726 | 63.7582 | -123.1882 | 122.8673 | 123.0267 | 123.0071 | 61.7424 | -123.3884
972.2656 | 123.143 | -66.4215 | 56.6071 | 0.057412 | -0.07577 | -0.010716 | 0.047824 | -0.01702 | 0.053805 | 0.088667 | -0.0068487 | 0.0011204 | 0.051427 | 0.074545 | 0.053982 | -66.2849 | -2.6359 | -66.2973 | 56.554 | 56.4951 | 56.6511 | -66.5994 | -66.3078 | -4.6653 | -66.3927 | 56.4549 | 56.6144 | 56.5855 | -66.7905 | -0.1779 | -0.053044 | 0.13666 | 0.12418 | 0.30208 | -0.11193 | 0.044022 | -0.36901 | -0.15212 | 0.11368 | 0.02881 | 0.39782 | 0.007335 | -0.021514 | 122.9755 | 122.9166 | 123.0726 | 63.7856 | -123.2065 | 122.8765 | 123.0359 | 123.0071 | 61.7562 | -123.3976
973.2656 | 123.1888 | -66.4078 | 56.5796 | 0.026888 | -0.074702 | -0.0096467 | 0.048892 | -0.018088 | 0.053805 | 0.073406 | -0.0057807 | 0.0021894 | 0.051427 | 0.074545 | 0.052914 | -66.2849 | -2.6359 | -66.3065 | 56.5494 | 56.4951 | 56.6465 | -66.5948 | -66.3216 | -4.6791 | -66.3973 | 56.4504 | 56.6098 | 56.5764 | -66.8043 | -0.18706 | -0.030156 | 0.12292 | 0.10129 | 0.28834 | -0.08446 | 0.06691 | -0.39648 | -0.12923 | 0.086211 | 0.010498 | 0.40698 | 0.030222 | -0.003205 | 122.9572 | 122.9029 | 123.0543 | 63.7719 | -123.1744 | 122.8581 | 123.0176 | 122.9842 | 61.7287 | -123.3838
974.2656 | 123.1842 | -66.3574 | 56.5659 | 0.057412 | -0.076839 | -0.0096467 | 0.047824 | -0.01702 | 0.053805 | 0.042884 | -0.0068487 | 5.2373e-05 | 0.052495 | 0.076681 | 0.053982 | -66.2849 | -2.6313 | -66.3065 | 56.554 | 56.486 | 56.6328 | -66.5903 | -66.3124 | -4.6745 | -66.3881 | 56.4504 | 56.6098 | 56.5764 | -66.7997 | -0.23283 | -0.011845 | 0.07257 | 0.050932 | 0.28376 | -0.079885 | 0.066907 | -0.44225 | -0.1155 | 0.045015 | -0.030699 | 0.41155 | 0.043955 | 0.010528 | 122.9114 | 122.8434 | 122.9902 | 63.7261 | -123.1561 | 122.8078 | 122.9672 | 122.9338 | 61.6829 | -123.3655
975.2656 | 123.23 | -66.3712 | 56.5521 | 0.057412 | -0.07577 | -0.010716 | 0.047824 | -0.015952 | 0.053805 | 0.073406 | -0.0057807 | 0.0021894 | 0.051427 | 0.075613 | 0.052914 | -66.2849 | -2.6221 | -66.3019 | 56.5403 | 56.4951 | 56.6328 | -66.5994 | -66.3124 | -4.6837 | -66.3881 | 56.4504 | 56.6144 | 56.5764 | -66.8043 | -0.22826 | -0.011847 | 0.086303 | 0.069243 | 0.2975 | -0.056994 | 0.08064 | -0.4331 | -0.10176 | 0.058748 | -0.016966 | 0.41613 | 0.062267 | 0.024261 | 122.9114 | 122.8663 | 123.0039 | 63.749 | -123.1515 | 122.8215 | 122.9855 | 122.9475 | 61.6875 | -123.3564
976.2656 | 123.2574 | -66.3757 | 56.5475 | 0.057412 | -0.074702 | -0.011784 | 0.047824 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 0.0011204 | 0.051427 | 0.075613 | 0.052914 | -66.294 | -2.6221 | -66.3019 | 56.5494 | 56.4951 | 56.6328 | -66.604 | -66.3124 | -4.6745 | -66.3881 | 56.4504 | 56.6144 | 56.5764 | -66.8088 | -0.22826 | 0.001888 | 0.081723 | 0.07382 | 0.30208 | -0.052416 | 0.085218 | -0.4331 | -0.097184 | 0.063325 | -0.012389 | 0.42071 | 0.066845 | 0.028839 | 122.9252 | 122.8709 | 123.0085 | 63.7536 | -123.1515 | 122.8261 | 122.9901 | 122.9521 | 61.7012 | -123.3564
977.2656 | 123.2666 | -66.3849 | 56.5659 | 0.04215 | -0.07577 | -0.011784 | 0.047824 | -0.01702 | 0.054873 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.051427 | 0.076681 | 0.053982 | -66.2849 | -2.6267 | -66.3065 | 56.5494 | 56.4951 | 56.6373 | -66.5994 | -66.3216 | -4.6837 | -66.3973 | 56.4458 | 56.6052 | 56.5764 | -66.8043 | -0.21452 | -0.016423 | 0.10004 | 0.078398 | 0.29292 | -0.070727 | 0.071485 | -0.41937 | -0.12007 | 0.063323 | -0.01239 | 0.40698 | 0.039377 | 0.010528 | 122.9343 | 122.88 | 123.0222 | 63.7582 | -123.1653 | 122.8307 | 122.9901 | 122.9613 | 61.7012 | -123.3701
978.2656 | 123.2117 | -66.3895 | 56.5659 | 0.057412 | -0.07577 | -0.011784 | 0.048892 | -0.015952 | 0.053805 | 0.058145 | -0.0057807 | 0.0011204 | 0.050358 | 0.075613 | 0.051845 | -66.2894 | -2.6221 | -66.3111 | 56.5403 | 56.4951 | 56.6419 | -66.6131 | -66.317 | -4.6791 | -66.3881 | 56.4504 | 56.6052 | 56.5764 | -66.7997 | -0.22368 | -0.02558 | 0.10004 | 0.078397 | 0.30208 | -0.070727 | 0.076064 | -0.41021 | -0.1155 | 0.072479 | 0.001344 | 0.41155 | 0.039377 | 0.010528 | 122.9297 | 122.8846 | 123.0314 | 63.7673 | -123.179 | 122.8398 | 122.9947 | 122.9659 | 61.7104 | -123.3655
979.2656 | 123.2254 | -66.3757 | 56.543 | 0.04215 | -0.076839 | -0.010716 | 0.048892 | -0.01702 | 0.055941 | 0.058145 | -0.0057807 | 0.0032574 | 0.051427 | 0.07775 | 0.051845 | -66.294 | -2.6176 | -66.3065 | 56.5494 | 56.4951 | 56.6282 | -66.6086 | -66.3216 | -4.6882 | -66.4019 | 56.4412 | 56.6052 | 56.5718 | -66.8134 | -0.23284 | 0.006465 | 0.081723 | 0.069242 | 0.30208 | -0.047839 | 0.085216 | -0.43768 | -0.10176 | 0.054167 | -0.026125 | 0.41155 | 0.062265 | 0.028837 | 122.9252 | 122.8709 | 123.0039 | 63.7582 | -123.1515 | 122.8169 | 122.981 | 122.9475 | 61.6875 | -123.3564
980.2656 | 123.1338 | -66.394 | 56.5475 | 0.057412 | -0.07577 | -0.011784 | 0.047824 | -0.015952 | 0.052737 | 0.058145 | -0.0047127 | 0.0011204 | 0.052495 | 0.074545 | 0.051845 | -66.3032 | -2.6176 | -66.3156 | 56.5311 | 56.4814 | 56.6328 | -66.6086 | -66.3307 | -4.6928 | -66.3927 | 56.4412 | 56.6052 | 56.5672 | -66.8043 | -0.21453 | -0.016426 | 0.090878 | 0.078397 | 0.29292 | -0.066153 | 0.085218 | -0.41021 | -0.10634 | 0.063321 | 0.001344 | 0.41156 | 0.057688 | 0.019682 | 122.9252 | 122.8754 | 123.0268 | 63.7765 | -123.1561 | 122.8352 | 122.9993 | 122.9613 | 61.7012 | -123.3518
981.2656 | 123.2849 | -66.3895 | 56.5475 | 0.057412 | -0.07577 | -0.0096467 | 0.047824 | -0.01702 | 0.053805 | 0.073406 | -0.0057807 | 0.0021894 | 0.051427 | 0.075613 | 0.052914 | -66.3077 | -2.6038 | -66.3294 | 56.5357 | 56.4768 | 56.6328 | -66.6086 | -66.3261 | -4.6974 | -66.411 | 56.4412 | 56.6007 | 56.5581 | -66.8043 | -0.2191 | -0.011847 | 0.081721 | 0.060084 | 0.27919 | -0.070732 | 0.085218 | -0.41479 | -0.10634 | 0.063322 | -0.021549 | 0.39324 | 0.053109 | 0.010524 | 122.9252 | 122.8663 | 123.0222 | 63.7856 | -123.1561 | 122.8307 | 122.9901 | 122.9475 | 61.6921 | -123.3518
982.2656 | 123.2391 | -66.3895 | 56.5018 | 0.026888 | -0.074702 | -0.011784 | 0.046755 | -0.014884 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.052495 | 0.076681 | 0.053982 | -66.3077 | -2.5992 | -66.3111 | 56.5357 | 56.4768 | 56.6282 | -66.6086 | -66.3307 | -4.702 | -66.411 | 56.4412 | 56.5961 | 56.5626 | -66.8134 | -0.2191 | 0.033929 | 0.081721 | 0.078397 | 0.2975 | -0.024956 | 0.12642 | -0.42395 | -0.060565 | 0.058743 | -0.021549 | 0.4024 | 0.094306 | 0.060879 | 122.9252 | 122.8663 | 123.0177 | 63.7902 | -123.1103 | 122.8307 | 122.9855 | 122.9521 | 61.6875 | -123.3152
983.2656 | 123.2895 | -66.394 | 56.5338 | 0.04215 | -0.076839 | -0.0096467 | 0.047824 | -0.015952 | 0.055941 | 0.073406 | -0.0057807 | 0.0011204 | 0.051427 | 0.075613 | 0.052914 | -66.3032 | -2.5901 | -66.3248 | 56.5311 | 56.4814 | 56.6328 | -66.6131 | -66.3307 | -4.7066 | -66.4156 | 56.432 | 56.6007 | 56.5718 | -66.8134 | -0.2191 | -0.002693 | 0.090878 | 0.06924 | 0.28834 | -0.05242 | 0.098951 | -0.41937 | -0.10177 | 0.063321 | -0.02155 | 0.39782 | 0.066842 | 0.037993 | 122.9252 | 122.8754 | 123.0268 | 63.804 | -123.147 | 122.8261 | 122.9947 | 122.9658 | 61.6875 | -123.3472
984.2656 | 123.2483 | -66.3757 | 56.5521 | 0.04215 | -0.07577 | -0.010716 | 0.046755 | -0.018088 | 0.054873 | 0.058145 | -0.0047127 | 0.0021894 | 0.050358 | 0.076681 | 0.051845 | -66.3169 | -2.5947 | -66.3202 | 56.5311 | 56.486 | 56.6282 | -66.6086 | -66.3353 | -4.7249 | -66.411 | 56.4412 | 56.5869 | 56.5581 | -66.8088 | -0.23284 | -0.021004 | 0.058831 | 0.055507 | 0.28834 | -0.066152 | 0.076061 | -0.4331 | -0.11092 | 0.040431 | -0.035282 | 0.39782 | 0.034795 | 0.005946 | 122.9069 | 122.8617 | 123.0039 | 63.7811 | -123.1607 | 122.8169 | 122.9627 | 122.9338 | 61.6509 | -123.361
985.2656 | 123.2391 | -66.3895 | 56.5659 | 0.072674 | -0.07577 | -0.0096467 | 0.048892 | -0.01702 | 0.053805 | 0.058145 | -0.0068487 | 0.0021894 | 0.051427 | 0.07775 | 0.051845 | -66.3169 | -2.5855 | -66.3248 | 56.5311 | 56.4814 | 56.6236 | -66.6177 | -66.3399 | -4.734 | -66.4156 | 56.4275 | 56.6007 | 56.5626 | -66.818 | -0.22826 | -0.034737 | 0.072564 | 0.064662 | 0.29292 | -0.084464 | 0.05775 | -0.42853 | -0.13839 | 0.049586 | -0.026128 | 0.4024 | 0.034798 | -0.003208 | 122.9206 | 122.8709 | 123.0131 | 63.804 | -123.1836 | 122.8169 | 122.9901 | 122.9521 | 61.6554 | -123.3838
986.2656 | 123.2574 | -66.4124 | 56.5475 | 0.04215 | -0.076839 | -0.0096467 | 0.046755 | -0.01702 | 0.055941 | 0.042884 | -0.0057807 | 0.0011204 | 0.051427 | 0.07775 | 0.052914 | -66.3123 | -2.5763 | -66.334 | 56.5265 | 56.4768 | 56.6236 | -66.6223 | -66.3399 | -4.7432 | -66.4156 | 56.432 | 56.5961 | 56.5626 | -66.8088 | -0.20995 | -0.021004 | 0.10003 | 0.078394 | 0.28834 | -0.070732 | 0.076061 | -0.39648 | -0.1155 | 0.072475 | -0.003239 | 0.39324 | 0.04853 | 0.015103 | 122.9389 | 122.8892 | 123.036 | 63.836 | -123.1698 | 122.8444 | 123.0084 | 122.975 | 61.6692 | -123.3564
987.2656 | 123.262 | -66.4261 | 56.5384 | 0.04215 | -0.07577 | -0.010716 | 0.046755 | -0.018088 | 0.053805 | 0.073406 | -0.0036447 | 0.0032574 | 0.051427 | 0.075613 | 0.052914 | -66.3169 | -2.5672 | -66.3385 | 56.5265 | 56.4814 | 56.6282 | -66.6269 | -66.349 | -4.7478 | -66.4248 | 56.432 | 56.5869 | 56.5535 | -66.818 | -0.2008 | -0.011849 | 0.10918 | 0.087548 | 0.28835 | -0.056998 | 0.089794 | -0.39191 | -0.10634 | 0.077049 | 0.001336 | 0.39324 | 0.048528 | 0.015101 | 122.9526 | 122.9075 | 123.0543 | 63.8589 | -123.1653 | 122.8581 | 123.013 | 122.9796 | 61.6783 | -123.3564
988.2656 | 123.262 | -66.3895 | 56.5292 | 0.057412 | -0.07577 | -0.0096467 | 0.047824 | -0.01702 | 0.052737 | 0.058145 | -0.0079177 | 0.0011204 | 0.050358 | 0.076681 | 0.050777 | -66.3261 | -2.5672 | -66.334 | 56.5311 | 56.4768 | 56.6236 | -66.6223 | -66.3582 | -4.7569 | -66.4156 | 56.4229 | 56.5869 | 56.5535 | -66.8271 | -0.23284 | 0.001884 | 0.063408 | 0.055505 | 0.28834 | -0.052422 | 0.094371 | -0.43768 | -0.10634 | 0.031271 | -0.026128 | 0.41155 | 0.057683 | 0.024256 | 122.9206 | 122.8663 | 123.0131 | 63.8223 | -123.1515 | 122.8124 | 122.9764 | 122.943 | 61.6325 | -123.3564
989.2656 | 123.2437 | -66.3986 | 56.5018 | 0.057412 | -0.074702 | -0.011784 | 0.048892 | -0.01702 | 0.055941 | 0.073406 | -0.0068487 | 0.0011204 | 0.051427 | 0.076681 | 0.051845 | -66.3215 | -2.5718 | -66.334 | 56.5265 | 56.4631 | 56.6144 | -66.6223 | -66.349 | -4.7661 | -66.4339 | 56.4229 | 56.5823 | 56.5535 | -66.818 | -0.22368 | 0.024772 | 0.077142 | 0.064661 | 0.28834 | -0.038692 | 0.11268 | -0.41937 | -0.078879 | 0.049584 | -0.035287 | 0.38408 | 0.080571 | 0.051722 | 122.9252 | 122.8617 | 123.0131 | 63.8269 | -123.1241 | 122.8215 | 122.981 | 122.9521 | 61.6325 | -123.3198
990.2656 | 123.4268 | -66.3712 | 56.5338 | 0.04215 | -0.074702 | -0.011784 | 0.046755 | -0.015952 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.04929 | 0.07775 | 0.051845 | -66.3306 | -2.558 | -66.334 | 56.5174 | 56.399 | 56.6144 | -66.6223 | -66.3628 | -4.7752 | -66.4293 | 56.4275 | 56.5961 | 56.5489 | -66.8271 | -0.25115 | -0.016428 | 0.040519 | 0.037195 | 0.28834 | -0.13484 | 0.080636 | -0.45599 | -0.10634 | 0.008382 | -0.058174 | 0.39782 | 0.062263 | 0.0151 | 122.8885 | 122.7701 | 122.9856 | 63.8131 | -123.1561 | 122.7986 | 122.9672 | 122.9201 | 61.5959 | -123.361
991.2656 | 123.2529 | -66.3895 | 56.5201 | 0.057412 | -0.076839 | -0.011784 | 0.047824 | -0.01702 | 0.054873 | 0.073406 | -0.0047127 | 0.0011204 | 0.051427 | 0.07775 | 0.052914 | -66.3261 | -2.5626 | -66.3431 | 56.522 | 56.3944 | 56.6144 | -66.6223 | -66.3536 | -4.7752 | -66.4248 | 56.4183 | 56.5823 | 56.5443 | -66.8271 | -0.23284 | 0.001883 | 0.063408 | 0.046349 | 0.27919 | -0.12569 | 0.094368 | -0.43768 | -0.10177 | 0.035849 | -0.035285 | 0.4024 | 0.06226 | 0.024254 | 122.9114 | 122.7839 | 123.0039 | 63.8269 | -123.1424 | 122.8078 | 122.9718 | 122.9338 | 61.6142 | -123.3472
992.2656 | 123.2849 | -66.3895 | 56.5109 | 0.057412 | -0.076839 | -0.0096467 | 0.04996 | -0.01702 | 0.053805 | 0.073406 | -0.0079177 | 0.0021894 | 0.052495 | 0.076681 | 0.052914 | -66.3306 | -2.558 | -66.3431 | 56.5082 | 56.3944 | 56.6099 | -66.6269 | -66.3582 | -4.7844 | -66.4293 | 56.4275 | 56.5823 | 56.5398 | -66.8271 | -0.23742 | -0.002697 | 0.058829 | 0.046349 | 0.28377 | -0.11653 | 0.098946 | -0.43768 | -0.083455 | 0.031271 | -0.039864 | 0.39782 | 0.071416 | 0.028831 | 122.8977 | 122.7839 | 122.9993 | 63.8314 | -123.1378 | 122.8169 | 122.9718 | 122.9292 | 61.6051 | -123.3381
993.2656 | 123.262 | -66.4261 | 56.4972 | 0.057412 | -0.077907 | -0.011784 | 0.047824 | -0.01702 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.050358 | 0.075613 | 0.053982 | -66.3352 | -2.5397 | -66.3431 | 56.5174 | 56.3898 | 56.6099 | -66.6223 | -66.3582 | -4.7844 | -66.4248 | 56.4229 | 56.5778 | 56.5443 | -66.8271 | -0.19622 | 0.020193 | 0.090872 | 0.08297 | 0.27919 | -0.10738 | 0.11268 | -0.40106 | -0.074301 | 0.067892 | 0.001336 | 0.4024 | 0.08057 | 0.047143 | 122.9435 | 122.8159 | 123.036 | 63.8864 | -123.1195 | 122.849 | 123.0038 | 122.9704 | 61.6417 | -123.3243
994.2656 | 123.2483 | -66.4124 | 56.5155 | 0.026888 | -0.077907 | -0.0096467 | 0.048892 | -0.01702 | 0.054873 | 0.042884 | -0.0057807 | 0.0011204 | 0.052495 | 0.076681 | 0.051845 | -66.3352 | -2.5306 | -66.3431 | 56.5037 | 56.3898 | 56.6099 | -66.636 | -66.3582 | -4.7844 | -66.4339 | 56.4137 | 56.5823 | 56.5352 | -66.8363 | -0.22369 | -0.011853 | 0.07714 | 0.069238 | 0.29293 | -0.12569 | 0.094368 | -0.42395 | -0.10177 | 0.05416 | -0.021554 | 0.4024 | 0.066838 | 0.019674 | 122.916 | 122.8022 | 123.0222 | 63.8818 | -123.1515 | 122.8261 | 122.9947 | 122.9475 | 61.628 | -123.3518
995.2656 | 123.2803 | -66.4032 | 56.4972 | 0.057412 | -0.076839 | -0.011784 | 0.047824 | -0.018088 | 0.054873 | 0.042884 | -0.0068487 | 0.0021894 | 0.050358 | 0.078818 | 0.052914 | -66.3398 | -2.5351 | -66.3477 | 56.5082 | 56.3898 | 56.6007 | -66.6269 | -66.3628 | -4.7981 | -66.4339 | 56.4137 | 56.5869 | 56.5352 | -66.8455 | -0.22369 | 0.011036 | 0.063405 | 0.055504 | 0.27919 | -0.10738 | 0.10352 | -0.44227 | -0.083458 | 0.040425 | -0.03071 | 0.41156 | 0.089727 | 0.037985 | 122.9114 | 122.793 | 123.0039 | 63.8681 | -123.1241 | 122.8169 | 122.9901 | 122.9384 | 61.6051 | -123.3427
996.2656 | 123.2346 | -66.4352 | 56.5018 | 0.04215 | -0.076839 | -0.012852 | 0.048892 | -0.01702 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.050358 | 0.075613 | 0.052914 | -66.3352 | -2.5168 | -66.3477 | 56.5128 | 56.3852 | 56.6007 | -66.6315 | -66.3628 | -4.7935 | -66.4339 | 56.4137 | 56.5823 | 56.5398 | -66.8363 | -0.19622 | 0.011037 | 0.10003 | 0.087548 | 0.28377 | -0.11653 | 0.098944 | -0.40106 | -0.088036 | 0.072469 | 0.001334 | 0.4024 | 0.080571 | 0.037986 | 122.948 | 122.8205 | 123.036 | 63.9184 | -123.1332 | 122.849 | 123.0176 | 122.975 | 61.6417 | -123.3381
997.2656 | 123.2208 | -66.4215 | 56.5018 | 0.04215 | -0.076839 | -0.0096467 | 0.047824 | -0.01702 | 0.054873 | 0.088667 | -0.0047127 | 5.2373e-05 | 0.051427 | 0.078818 | 0.052914 | -66.3398 | -2.5077 | -66.3477 | 56.5037 | 56.3898 | 56.6007 | -66.636 | -66.3719 | -4.8027 | -66.4522 | 56.4 | 56.5732 | 56.5352 | -66.8363 | -0.21453 | 0.00188 | 0.081716 | 0.073815 | 0.28835 | -0.11196 | 0.098944 | -0.4148 | -0.10177 | 0.049579 | -0.030714 | 0.38408 | 0.071413 | 0.033407 | 122.9252 | 122.8113 | 123.0222 | 63.9138 | -123.1378 | 122.8215 | 122.9947 | 122.9567 | 61.6188 | -123.3381
998.2656 | 123.2849 | -66.4398 | 56.4743 | 0.072674 | -0.076839 | -0.010716 | 0.048892 | -0.01702 | 0.054873 | 0.058145 | -0.0057807 | 0.0011204 | 0.052495 | 0.076681 | 0.050777 | -66.3398 | -2.5168 | -66.3569 | 56.5082 | 56.399 | 56.6007 | -66.636 | -66.3674 | -4.8119 | -66.4431 | 56.4137 | 56.5778 | 56.5352 | -66.8409 | -0.19622 | 0.033924 | 0.10003 | 0.082968 | 0.27919 | -0.075331 | 0.12641 | -0.40107 | -0.06057 | 0.072467 | -0.003246 | 0.39782 | 0.10346 | 0.060873 | 122.948 | 122.8388 | 123.0405 | 63.923 | -123.1103 | 122.8536 | 123.0176 | 122.975 | 61.628 | -123.3152
999.2656 | 123.2803 | -66.3895 | 56.5338 | 0.04215 | -0.07577 | -0.011784 | 0.047824 | -0.019157 | 0.053805 | 0.073406 | -0.0057807 | 0.0032574 | 0.04929 | 0.078818 | 0.051845 | -66.3306 | -2.5031 | -66.3523 | 56.4945 | 56.4127 | 56.6053 | -66.6315 | -66.3719 | -4.8164 | -66.4385 | 56.4092 | 56.5778 | 56.5306 | -66.8409 | -0.242 | -0.03932 | 0.058829 | 0.037192 | 0.27919 | -0.1211 | 0.071479 | -0.45142 | -0.12466 | 0.017535 | -0.049022 | 0.4024 | 0.043949 | -0.003214 | 122.884 | 122.8022 | 122.9948 | 63.8864 | -123.1653 | 122.7986 | 122.9672 | 122.9201 | 61.573 | -123.3747
1000.2656 | 123.2712 | -66.4215 | 56.5247 | 0.04215 | -0.077907 | -0.011784 | 0.045687 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 0.0011204 | 0.050358 | 0.078818 | 0.052914 | -66.3398 | -2.5122 | -66.3523 | 56.4991 | 56.4493 | 56.6007 | -66.6452 | -66.3765 | -4.8256 | -66.4522 | 56.4046 | 56.5686 | 56.5306 | -66.85 | -0.22369 | -0.025586 | 0.081716 | 0.069236 | 0.29293 | -0.075317 | 0.076056 | -0.42853 | -0.12008 | 0.045 | -0.030714 | 0.39782 | 0.043947 | 0.005941 | 122.9206 | 122.8708 | 123.0222 | 63.9093 | -123.1699 | 122.8261 | 122.9901 | 122.9521 | 61.5959 | -123.3747
1001.2656 | 123.2849 | -66.4215 | 56.4743 | 0.026888 | -0.077907 | -0.010716 | 0.047824 | -0.014884 | 0.055941 | 0.058145 | -0.0068487 | 0.0011204 | 0.051427 | 0.079887 | 0.051845 | -66.3489 | -2.5122 | -66.3523 | 56.5082 | 56.4539 | 56.5961 | -66.6406 | -66.3719 | -4.821 | -66.4476 | 56.4 | 56.564 | 56.526 | -66.8363 | -0.21911 | 0.033924 | 0.07256 | 0.069236 | 0.28835 | -0.020384 | 0.12183 | -0.4148 | -0.074305 | 0.049579 | -0.026135 | 0.38866 | 0.089722 | 0.051716 | 122.9297 | 122.8754 | 123.0176 | 63.9093 | -123.1149 | 122.8215 | 122.9855 | 122.9475 | 61.6005 | -123.3106
1002.2656 | 123.262 | -66.4215 | 56.4972 | 0.04215 | -0.077907 | -0.0096467 | 0.046755 | -0.018088 | 0.053805 | 0.042884 | -0.0057807 | 0.0021894 | 0.052495 | 0.076681 | 0.052914 | -66.3535 | -2.5077 | -66.366 | 56.5037 | 56.4539 | 56.6007 | -66.6406 | -66.3811 | -4.8256 | -66.4568 | 56.4046 | 56.5686 | 56.5398 | -66.85 | -0.21911 | 0.006458 | 0.067981 | 0.055501 | 0.27461 | -0.043272 | 0.10352 | -0.42853 | -0.092615 | 0.040421 | -0.035292 | 0.39324 | 0.071413 | 0.042564 | 122.9252 | 122.8754 | 123.0222 | 63.9138 | -123.1378 | 122.8261 | 122.9901 | 122.9613 | 61.5959 | -123.3472
1003.2656 | 123.2529 | -66.4764 | 56.4972 | 0.04215 | -0.077907 | -0.010716 | 0.048892 | -0.018088 | 0.053805 | 0.088667 | -0.0068487 | 5.2373e-05 | 0.051427 | 0.078818 | 0.052914 | -66.3489 | -2.4985 | -66.3706 | 56.5037 | 56.4448 | 56.6007 | -66.6498 | -66.3811 | -4.8256 | -66.4614 | 56.4 | 56.5686 | 56.5306 | -66.8546 | -0.17334 | 0.006458 | 0.12749 | 0.10585 | 0.27919 | -0.05243 | 0.10352 | -0.37818 | -0.097193 | 0.095352 | 0.01506 | 0.39324 | 0.071413 | 0.033407 | 122.9801 | 122.9212 | 123.0772 | 63.9779 | -123.147 | 122.8764 | 123.045 | 123.007 | 61.6508 | -123.3518
1004.2656 | 123.2437 | -66.4627 | 56.5063 | 0.026888 | -0.077907 | -0.010716 | 0.047824 | -0.015952 | 0.052737 | 0.073406 | -0.0057807 | 0.0021894 | 0.04929 | 0.07775 | 0.051845 | -66.3535 | -2.4985 | -66.3614 | 56.4991 | 56.4493 | 56.6007 | -66.6498 | -66.3765 | -4.8348 | -66.4568 | 56.3954 | 56.5594 | 56.526 | -66.85 | -0.18707 | -0.007276 | 0.10918 | 0.10128 | 0.28835 | -0.057007 | 0.094366 | -0.38733 | -0.11093 | 0.086199 | 0.005907 | 0.39324 | 0.0531 | 0.019672 | 122.9618 | 122.912 | 123.0634 | 63.9642 | -123.1561 | 122.8581 | 123.0222 | 122.9887 | 61.6279 | -123.3564
1005.2656 | 123.2483 | -66.4444 | 56.4926 | 0.04215 | -0.076839 | -0.010716 | 0.047824 | -0.019157 | 0.055941 | 0.042884 | -0.0057807 | 0.0021894 | 0.051427 | 0.078818 | 0.052914 | -66.3535 | -2.4894 | -66.3614 | 56.4991 | 56.4448 | 56.587 | -66.6544 | -66.3857 | -4.8302 | -66.4522 | 56.4046 | 56.564 | 56.526 | -66.8546 | -0.20996 | 0.006457 | 0.090869 | 0.082968 | 0.29293 | -0.047853 | 0.094363 | -0.41022 | -0.088038 | 0.05873 | -0.007826 | 0.4024 | 0.071411 | 0.033405 | 122.9435 | 122.8892 | 123.0314 | 63.955 | -123.147 | 122.849 | 123.0084 | 122.9704 | 61.6142 | -123.3472
1006.2656 | 123.2712 | -66.4398 | 56.4926 | 0.072674 | -0.078975 | -0.010716 | 0.047824 | -0.01702 | 0.053805 | 0.042884 | -0.0057807 | 5.2373e-05 | 0.04929 | 0.078818 | 0.051845 | -66.3581 | -2.4939 | -66.366 | 56.4899 | 56.4356 | 56.587 | -66.6498 | -66.3902 | -4.8485 | -66.4614 | 56.3908 | 56.5594 | 56.5214 | -66.8546 | -0.20996 | -0.0027 | 0.081713 | 0.073811 | 0.28377 | -0.057011 | 0.094363 | -0.4148 | -0.10177 | 0.049574 | -0.021561 | 0.39324 | 0.066833 | 0.028827 | 122.9297 | 122.8754 | 123.0268 | 63.9459 | -123.1424 | 122.8307 | 122.9993 | 122.9613 | 61.5913 | -123.3472
1007.2656 | 123.317 | -66.4444 | 56.4606 | 0.057412 | -0.077907 | -0.010716 | 0.045687 | -0.015952 | 0.053805 | 0.027623 | -0.0068487 | 0.0011204 | 0.051427 | 0.079887 | 0.051845 | -66.3673 | -2.4939 | -66.3752 | 56.4853 | 56.399 | 56.587 | -66.6498 | -66.3948 | -4.8439 | -66.4614 | 56.3954 | 56.5594 | 56.5214 | -66.8546 | -0.20538 | 0.024765 | 0.077134 | 0.069233 | 0.27461 | -0.061598 | 0.12641 | -0.41022 | -0.065151 | 0.049573 | -0.016983 | 0.39324 | 0.098877 | 0.060871 | 122.9297 | 122.8434 | 123.0314 | 63.9505 | -123.1103 | 122.8398 | 123.0038 | 122.9658 | 61.6005 | -123.3152
1008.2656 | 123.2803 | -66.4307 | 56.4697 | 0.026888 | -0.077907 | -0.011784 | 0.047824 | -0.01702 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.050358 | 0.076681 | 0.053982 | -66.3627 | -2.4894 | -66.3706 | 56.4899 | 56.3807 | 56.5916 | -66.6498 | -66.3948 | -4.8485 | -66.466 | 56.4 | 56.5594 | 56.5214 | -66.8546 | -0.21911 | 0.020188 | 0.067979 | 0.060078 | 0.27919 | -0.08907 | 0.12183 | -0.42396 | -0.069728 | 0.03584 | -0.035295 | 0.38866 | 0.089721 | 0.051715 | 122.9206 | 122.8113 | 123.0222 | 63.9413 | -123.1195 | 122.8307 | 122.9901 | 122.9521 | 61.5822 | -123.3243
1009.2656 | 123.2758 | -66.4261 | 56.4835 | 0.057412 | -0.078975 | -0.011784 | 0.046755 | -0.018088 | 0.055941 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.050358 | 0.078818 | 0.050777 | -66.3627 | -2.4848 | -66.3706 | 56.4899 | 56.3623 | 56.5961 | -66.6498 | -66.3902 | -4.8485 | -66.466 | 56.3954 | 56.5594 | 56.5123 | -66.8638 | -0.22369 | 0.006456 | 0.063401 | 0.0555 | 0.27919 | -0.12112 | 0.11268 | -0.43769 | -0.088039 | 0.035841 | -0.039873 | 0.39782 | 0.075989 | 0.028825 | 122.916 | 122.7884 | 123.0222 | 63.9413 | -123.1332 | 122.8215 | 122.9855 | 122.9384 | 61.5776 | -123.3472
1010.2656 | 123.2437 | -66.4536 | 56.4926 | 0.026888 | -0.07577 | -0.010716 | 0.047824 | -0.018088 | 0.055941 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.04929 | 0.079887 | 0.052914 | -66.3627 | -2.4894 | -66.3752 | 56.4899 | 56.3669 | 56.587 | -66.6544 | -66.3902 | -4.8622 | -66.4705 | 56.3908 | 56.5549 | 56.5214 | -66.8592 | -0.20081 | -0.0027 | 0.090867 | 0.078388 | 0.27919 | -0.1257 | 0.094363 | -0.40565 | -0.10177 | 0.063307 | -0.016986 | 0.38866 | 0.062254 | 0.028827 | 122.9435 | 122.8205 | 123.0405 | 63.9642 | -123.147 | 122.8444 | 123.0084 | 122.975 | 61.5913 | -123.3518
1011.2656 | 123.2208 | -66.4627 | 56.4835 | 0.04215 | -0.077907 | -0.010716 | 0.048892 | -0.014884 | 0.053805 | 0.058145 | -0.0068487 | 0.0021894 | 0.051427 | 0.078818 | 0.051845 | -66.3673 | -2.4802 | -66.3706 | 56.4853 | 56.3623 | 56.587 | -66.6589 | -66.3902 | -4.8577 | -66.4705 | 56.3954 | 56.5503 | 56.5169 | -66.85 | -0.19623 | 0.001877 | 0.095445 | 0.092122 | 0.28835 | -0.12112 | 0.10352 | -0.38733 | -0.088039 | 0.072463 | -0.00783 | 0.3795 | 0.066831 | 0.033404 | 122.948 | 122.825 | 123.0497 | 63.9825 | -123.1424 | 122.8581 | 123.013 | 122.9796 | 61.6051 | -123.3335
1012.2656 | 123.2208 | -66.4444 | 56.4926 | 0.04215 | -0.078975 | -0.0096467 | 0.045687 | -0.018088 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.052495 | 0.079887 | 0.051845 | -66.3673 | -2.4802 | -66.3706 | 56.4853 | 56.3623 | 56.5916 | -66.6544 | -66.3902 | -4.8668 | -66.466 | 56.4 | 56.5594 | 56.5169 | -66.8592 | -0.20996 | -0.007279 | 0.077134 | 0.073811 | 0.28377 | -0.13027 | 0.098941 | -0.4148 | -0.092616 | 0.054152 | -0.021562 | 0.39324 | 0.066833 | 0.024248 | 122.9297 | 122.8067 | 123.036 | 63.9642 | -123.147 | 122.8444 | 123.0038 | 122.9613 | 61.5776 | -123.3518
1013.2656 | 123.262 | -66.4444 | 56.4972 | 0.057412 | -0.078975 | -0.0085787 | 0.047824 | -0.01702 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.050358 | 0.07775 | 0.050777 | -66.3673 | -2.4802 | -66.3752 | 56.4853 | 56.3807 | 56.5824 | -66.6589 | -66.404 | -4.8622 | -66.4705 | 56.3908 | 56.5549 | 56.5077 | -66.8684 | -0.21454 | -0.011856 | 0.077134 | 0.069233 | 0.28377 | -0.11653 | 0.085207 | -0.42396 | -0.10635 | 0.040416 | -0.026141 | 0.39782 | 0.057677 | 0.010514 | 122.9297 | 122.8251 | 123.0268 | 63.9642 | -123.1561 | 122.8352 | 122.9993 | 122.9521 | 61.5822 | -123.3655
1014.2656 | 123.2712 | -66.4352 | 56.5063 | 0.057412 | -0.078975 | -0.010716 | 0.048892 | -0.013815 | 0.053805 | 0.058145 | -0.0057807 | 0.0043254 | 0.050358 | 0.080955 | 0.051845 | -66.3673 | -2.4802 | -66.3843 | 56.4808 | 56.3761 | 56.5778 | -66.6544 | -66.3948 | -4.8714 | -66.4751 | 56.3908 | 56.5594 | 56.5123 | -66.8592 | -0.21912 | -0.02559 | 0.067979 | 0.050921 | 0.27004 | -0.13027 | 0.071473 | -0.42396 | -0.11551 | 0.040418 | -0.039874 | 0.38408 | 0.0531 | 0.005936 | 122.916 | 122.8113 | 123.0131 | 63.955 | -123.1607 | 122.8261 | 122.9947 | 122.9475 | 61.5639 | -123.3655
1015.2656 | 123.1934 | -66.4673 | 56.5109 | 0.057412 | -0.077907 | -0.0085787 | 0.047824 | -0.015952 | 0.052737 | 0.058145 | -0.0057807 | 0.0021894 | 0.050358 | 0.079887 | 0.050777 | -66.3718 | -2.4665 | -66.3797 | 56.4808 | 56.3852 | 56.5824 | -66.6589 | -66.3994 | -4.876 | -66.4705 | 56.3863 | 56.5503 | 56.4985 | -66.8684 | -0.19165 | -0.030167 | 0.095444 | 0.087543 | 0.27919 | -0.12569 | 0.071474 | -0.40107 | -0.12466 | 0.067882 | -0.003253 | 0.39782 | 0.039365 | -0.012376 | 122.948 | 122.8525 | 123.0497 | 64.0008 | -123.1699 | 122.8535 | 123.0176 | 122.9658 | 61.5913 | -123.3793
1016.2656 | 123.1338 | -66.4673 | 56.5384 | 0.04215 | -0.078975 | -0.011784 | 0.048892 | -0.018088 | 0.052737 | 0.073406 | -0.0057807 | 0.0021894 | 0.051427 | 0.07775 | 0.051845 | -66.3627 | -2.4756 | -66.3797 | 56.4853 | 56.3807 | 56.5778 | -66.6589 | -66.3994 | -4.8668 | -66.466 | 56.3863 | 56.5503 | 56.5123 | -66.8684 | -0.19165 | -0.053055 | 0.1046 | 0.087543 | 0.27919 | -0.15773 | 0.03943 | -0.40107 | -0.15213 | 0.067882 | 0.001326 | 0.4024 | 0.011899 | -0.026107 | 122.9526 | 122.8479 | 123.0451 | 63.9917 | -123.1973 | 122.8535 | 123.0176 | 122.9796 | 61.6005 | -123.4067
1017.2656 | 123.2346 | -66.4398 | 56.456 | 0.026888 | -0.077907 | -0.012852 | 0.045687 | -0.018088 | 0.052737 | 0.042884 | -0.0068487 | 0.0021894 | 0.052495 | 0.078818 | 0.050777 | -66.3673 | -2.4619 | -66.3843 | 56.4762 | 56.3578 | 56.5778 | -66.6635 | -66.404 | -4.876 | -66.4797 | 56.3908 | 56.5549 | 56.5031 | -66.8638 | -0.2237 | 0.020186 | 0.072556 | 0.055498 | 0.27919 | -0.098232 | 0.12183 | -0.42396 | -0.065152 | 0.035838 | -0.039876 | 0.38408 | 0.098875 | 0.047133 | 122.916 | 122.7976 | 123.0176 | 63.9779 | -123.1195 | 122.8307 | 122.9947 | 122.9429 | 61.5639 | -123.3198
1018.2656 | 123.2712 | -66.4627 | 56.4606 | 0.04215 | -0.077907 | -0.011784 | 0.048892 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 0.0011204 | 0.051427 | 0.079887 | 0.052914 | -66.3673 | -2.4665 | -66.3843 | 56.4716 | 56.3623 | 56.5732 | -66.6589 | -66.4086 | -4.8668 | -66.4751 | 56.3863 | 56.5503 | 56.5031 | -66.8592 | -0.19623 | 0.01103 | 0.095445 | 0.078387 | 0.27461 | -0.09823 | 0.11267 | -0.39649 | -0.074308 | 0.054148 | -0.012408 | 0.38408 | 0.089719 | 0.042556 | 122.9343 | 122.825 | 123.036 | 63.9962 | -123.1195 | 122.849 | 123.013 | 122.9658 | 61.5959 | -123.3198
1019.2656 | 123.2208 | -66.4581 | 56.4651 | 0.04215 | -0.077907 | -0.010716 | 0.046755 | -0.015952 | 0.054873 | 0.042884 | -0.0057807 | 0.0011204 | 0.054631 | 0.079887 | 0.051845 | -66.3718 | -2.4665 | -66.3843 | 56.4762 | 56.3578 | 56.5778 | -66.6635 | -66.3994 | -4.876 | -66.4751 | 56.3908 | 56.5503 | 56.5077 | -66.8638 | -0.20539 | 0.011031 | 0.086289 | 0.073809 | 0.27919 | -0.10739 | 0.11267 | -0.40565 | -0.074307 | 0.058727 | -0.016986 | 0.38866 | 0.085141 | 0.042557 | 122.9343 | 122.8159 | 123.036 | 63.9917 | -123.1287 | 122.849 | 123.0084 | 122.9658 | 61.5822 | -123.3289
1020.2656 | 123.23 | -66.4764 | 56.4606 | 0.04215 | -0.076839 | -0.013921 | 0.046755 | -0.018088 | 0.053805 | 0.027623 | -0.0068487 | 5.2373e-05 | 0.050358 | 0.07775 | 0.050777 | -66.3718 | -2.4619 | -66.3843 | 56.4716 | 56.4173 | 56.5778 | -66.6681 | -66.4086 | -4.8714 | -66.4705 | 56.3771 | 56.5411 | 56.5077 | -66.8638 | -0.19165 | 0.01103 | 0.1046 | 0.092119 | 0.28377 | -0.043283 | 0.11725 | -0.38734 | -0.083465 | 0.06788 | 0.005902 | 0.39324 | 0.080562 | 0.047135 | 122.948 | 122.8937 | 123.0543 | 64.0146 | -123.1287 | 122.8535 | 123.0176 | 122.9841 | 61.6051 | -123.3243
1021.2656 | 123.1934 | -66.4948 | 56.5475 | 0.011626 | -0.078975 | -0.010716 | 0.048892 | -0.01702 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.051427 | 0.079887 | 0.051845 | -66.3718 | -2.4665 | -66.3889 | 56.4762 | 56.431 | 56.5778 | -66.6727 | -66.404 | -4.876 | -66.4751 | 56.3817 | 56.5411 | 56.5169 | -66.8684 | -0.17792 | -0.071366 | 0.12291 | 0.10585 | 0.28377 | -0.11652 | 0.030275 | -0.37361 | -0.16586 | 0.09077 | 0.019635 | 0.39324 | -0.006413 | -0.030683 | 122.9709 | 122.9258 | 123.0726 | 64.0283 | -123.2202 | 122.8764 | 123.0359 | 123.0116 | 61.6188 | -123.4159
1022.2656 | 123.2483 | -66.4627 | 56.4239 | 0.057412 | -0.077907 | -0.011784 | 0.047824 | -0.015952 | 0.054873 | 0.073406 | -0.0047127 | 0.0011204 | 0.051427 | 0.079887 | 0.051845 | -66.3764 | -2.4665 | -66.3889 | 56.4808 | 56.4264 | 56.5824 | -66.6681 | -66.4086 | -4.8714 | -66.4797 | 56.3908 | 56.5457 | 56.5031 | -66.8729 | -0.20539 | 0.056808 | 0.086288 | 0.073809 | 0.2792 | 0.002496 | 0.15845 | -0.41023 | -0.033108 | 0.054148 | -0.016987 | 0.39324 | 0.12176 | 0.079177 | 122.9435 | 122.8892 | 123.0451 | 63.9962 | -123.092 | 122.8536 | 123.0084 | 122.9658 | 61.5913 | -123.2969
1023.2656 | 123.2437 | -66.4627 | 56.4926 | 0.026888 | -0.077907 | -0.011784 | 0.046755 | -0.01702 | 0.053805 | 0.073406 | -0.0047127 | 0.0032574 | 0.051427 | 0.078818 | 0.051845 | -66.3856 | -2.4573 | -66.3935 | 56.4762 | 56.4356 | 56.5732 | -66.6727 | -66.4086 | -4.8668 | -66.4797 | 56.3863 | 56.5366 | 56.5123 | -66.8684 | -0.20996 | -0.016435 | 0.077132 | 0.069231 | 0.2792 | -0.057011 | 0.080627 | -0.40565 | -0.10635 | 0.054148 | -0.016987 | 0.38866 | 0.04394 | 0.019669 | 122.9389 | 122.8983 | 123.036 | 64.0054 | -123.1653 | 122.849 | 122.9993 | 122.975 | 61.5959 | -123.361
1024.2656 | 123.2437 | -66.481 | 56.4606 | 0.026888 | -0.078975 | -0.0096467 | 0.047824 | -0.01702 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.050358 | 0.079887 | 0.049709 | -66.3764 | -2.4619 | -66.3889 | 56.4853 | 56.4264 | 56.5687 | -66.6727 | -66.4131 | -4.8622 | -66.4751 | 56.3771 | 56.5503 | 56.5077 | -66.8684 | -0.19165 | 0.024765 | 0.1046 | 0.092119 | 0.28377 | -0.034125 | 0.10809 | -0.38734 | -0.083465 | 0.067879 | 0.005902 | 0.39324 | 0.089719 | 0.047135 | 122.9664 | 122.9075 | 123.0497 | 64.0191 | -123.1332 | 122.8581 | 123.0313 | 122.9887 | 61.6188 | -123.3289
1025.2656 | 123.2346 | -66.4902 | 56.4743 | 0.04215 | -0.077907 | -0.011784 | 0.047824 | -0.015952 | 0.053805 | 0.058145 | -0.0057807 | 0.0021894 | 0.04929 | 0.080955 | 0.052914 | -66.3856 | -2.471 | -66.3935 | 56.4899 | 56.4356 | 56.5824 | -66.6818 | -66.4086 | -4.8622 | -66.4889 | 56.3771 | 56.5503 | 56.5169 | -66.8638 | -0.19166 | 0.015611 | 0.1046 | 0.096696 | 0.28835 | -0.0387 | 0.1081 | -0.37361 | -0.097198 | 0.081613 | 0.001321 | 0.37493 | 0.075986 | 0.042559 | 122.9801 | 122.9258 | 123.0726 | 64.0191 | -123.1561 | 122.8673 | 123.0405 | 123.007 | 61.6279 | -123.3381
1026.2656 | 123.262 | -66.449 | 56.4514 | 0.04215 | -0.076839 | -0.010716 | 0.046755 | -0.018088 | 0.055941 | 0.073406 | -0.0068487 | 0.0021894 | 0.051427 | 0.082023 | 0.052914 | -66.3856 | -2.4619 | -66.3889 | 56.4808 | 56.4356 | 56.5824 | -66.6773 | -66.4131 | -4.8668 | -66.4843 | 56.3817 | 56.5411 | 56.5169 | -66.8729 | -0.22828 | 0.029342 | 0.063399 | 0.060076 | 0.28835 | -0.015812 | 0.13098 | -0.42396 | -0.069731 | 0.035836 | -0.035299 | 0.38866 | 0.089717 | 0.065447 | 122.9297 | 122.8846 | 123.0314 | 63.9871 | -123.1287 | 122.8307 | 122.9901 | 122.9658 | 61.5822 | -123.3244
1027.2656 | 123.2391 | -66.4719 | 56.4606 | 0.057412 | -0.077907 | -0.010716 | 0.048892 | -0.01702 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.052495 | 0.079887 | 0.050777 | -66.3902 | -2.4619 | -66.3981 | 56.4899 | 56.4356 | 56.5778 | -66.6864 | -66.4086 | -4.8622 | -66.4934 | 56.3725 | 56.5457 | 56.5123 | -66.8729 | -0.21455 | 0.029344 | 0.081708 | 0.073808 | 0.28835 | -0.024967 | 0.11725 | -0.40107 | -0.088043 | 0.063303 | -0.021568 | 0.3795 | 0.085141 | 0.051713 | 122.9618 | 122.9075 | 123.0497 | 64.01 | -123.147 | 122.8444 | 123.0176 | 122.9841 | 61.6096 | -123.3335
1028.2656 | 123.262 | -66.4856 | 56.456 | 0.026888 | -0.078975 | -0.010716 | 0.048892 | -0.015952 | 0.053805 | 0.042884 | -0.0057807 | 0.0032574 | 0.051427 | 0.079887 | 0.050777 | -66.3902 | -2.4665 | -66.3935 | 56.4808 | 56.4356 | 56.5778 | -66.6773 | -66.4086 | -4.8577 | -66.4797 | 56.3771 | 56.5457 | 56.5031 | -66.8775 | -0.19166 | 0.024764 | 0.095441 | 0.092119 | 0.28377 | -0.02039 | 0.12183 | -0.39192 | -0.078888 | 0.077036 | 0.005901 | 0.39782 | 0.089718 | 0.047133 | 122.9664 | 122.9212 | 123.0634 | 64.0191 | -123.1332 | 122.8627 | 123.0313 | 122.9887 | 61.6279 | -123.3335
1029.2656 | 123.2346 | -66.4536 | 56.4331 | 0.026888 | -0.078975 | -0.010716 | 0.048892 | -0.01702 | 0.05701 | 0.058145 | -0.0057807 | 0.0011204 | 0.04929 | 0.079887 | 0.051845 | -66.3947 | -2.4573 | -66.3981 | 56.4762 | 56.4356 | 56.5824 | -66.6818 | -66.4086 | -4.8577 | -66.4843 | 56.3725 | 56.5366 | 56.5077 | -66.8729 | -0.22828 | 0.043075 | 0.058819 | 0.055497 | 0.28378 | 0.002499 | 0.14929 | -0.41938 | -0.060577 | 0.044992 | -0.030722 | 0.38866 | 0.10345 | 0.074601 | 122.9297 | 122.8892 | 123.036 | 63.9962 | -123.1149 | 122.8261 | 122.9901 | 122.9613 | 61.5959 | -123.306
1030.2656 | 123.2437 | -66.4856 | 56.4606 | 0.04215 | -0.078975 | -0.012852 | 0.048892 | -0.01702 | 0.053805 | 0.073406 | -0.0036447 | 0.0021894 | 0.04929 | 0.080955 | 0.052914 | -66.3856 | -2.4619 | -66.3935 | 56.4762 | 56.4219 | 56.5732 | -66.6818 | -66.4177 | -4.8577 | -66.4889 | 56.3817 | 56.5411 | 56.5123 | -66.8729 | -0.19623 | 0.015609 | 0.10002 | 0.092119 | 0.28835 | -0.038704 | 0.11267 | -0.38734 | -0.078886 | 0.067878 | -0.003256 | 0.38408 | 0.080562 | 0.051713 | 122.9618 | 122.9075 | 123.0588 | 64.0237 | -123.1424 | 122.8673 | 123.0267 | 122.9979 | 61.6279 | -123.3335
1031.2656 | 123.1247 | -66.5085 | 56.5384 | 0.057412 | -0.080044 | -0.010716 | 0.047824 | -0.018088 | 0.055941 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.050358 | 0.079887 | 0.051845 | -66.3947 | -2.4665 | -66.4026 | 56.4808 | 56.4219 | 56.5732 | -66.6818 | -66.4131 | -4.8622 | -66.4889 | 56.3817 | 56.5411 | 56.5031 | -66.8729 | -0.17335 | -0.057633 | 0.11375 | 0.10585 | 0.2792 | -0.11652 | 0.034851 | -0.36445 | -0.15671 | 0.095345 | 0.019632 | 0.38408 | 0.002742 | -0.035264 | 122.9892 | 122.9304 | 123.0817 | 64.042 | -123.2202 | 122.8902 | 123.0496 | 123.0116 | 61.6463 | -123.4113
1032.2656 | 123.1659 | -66.5039 | 56.4697 | 0.026888 | -0.081112 | -0.010716 | 0.048892 | -0.01702 | 0.055941 | 0.027623 | -0.0057807 | 0.0021894 | 0.04929 | 0.079887 | 0.051845 | -66.3856 | -2.4573 | -66.3981 | 56.4808 | 56.4264 | 56.5732 | -66.6818 | -66.4131 | -4.8622 | -66.4934 | 56.3725 | 56.5411 | 56.5077 | -66.8775 | -0.17792 | 0.011031 | 0.11833 | 0.10585 | 0.28378 | -0.043281 | 0.10352 | -0.37361 | -0.097199 | 0.090767 | 0.010475 | 0.38408 | 0.071406 | 0.037979 | 122.9847 | 122.9304 | 123.0771 | 64.0466 | -123.1516 | 122.8764 | 123.045 | 123.0116 | 61.6417 | -123.3472
1033.2656 | 123.143 | -66.4948 | 56.4468 | 0.026888 | -0.080044 | -0.012852 | 0.047824 | -0.01702 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.050358 | 0.080955 | 0.050777 | -66.3947 | -2.4619 | -66.4026 | 56.4716 | 56.4219 | 56.5687 | -66.6773 | -66.4177 | -4.8531 | -66.4843 | 56.3771 | 56.5366 | 56.5077 | -66.8775 | -0.1825 | 0.024763 | 0.10002 | 0.092117 | 0.27462 | -0.024971 | 0.12183 | -0.38276 | -0.069732 | 0.077033 | 0.010477 | 0.39324 | 0.089717 | 0.060868 | 122.9664 | 122.9166 | 123.0634 | 64.0329 | -123.1241 | 122.8719 | 123.0313 | 123.0025 | 61.6417 | -123.3244
1034.2656 | 123.1796 | -66.5222 | 56.456 | 0.04215 | -0.078975 | -0.010716 | 0.047824 | -0.018088 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.050358 | 0.080955 | 0.052914 | -66.3902 | -2.4619 | -66.3981 | 56.467 | 56.431 | 56.5687 | -66.6773 | -66.4177 | -4.8439 | -66.4843 | 56.3771 | 56.5366 | 56.5031 | -66.8775 | -0.15503 | 0.011029 | 0.13206 | 0.12416 | 0.2792 | -0.024969 | 0.11267 | -0.3553 | -0.078888 | 0.1045 | 0.037943 | 0.39324 | 0.080561 | 0.047133 | 122.9892 | 122.9532 | 123.0909 | 64.0603 | -123.1332 | 122.8993 | 123.0588 | 123.0253 | 61.6783 | -123.3335
1035.2656 | 123.1384 | -66.5176 | 56.456 | 0.026888 | -0.077907 | -0.010716 | 0.046755 | -0.018088 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.050358 | 0.082023 | 0.052914 | -66.3902 | -2.471 | -66.3935 | 56.467 | 56.4264 | 56.5687 | -66.6864 | -66.4177 | -4.8531 | -66.498 | 56.3725 | 56.5366 | 56.5077 | -66.8821 | -0.16877 | 0.011029 | 0.12748 | 0.12416 | 0.29293 | -0.029548 | 0.11267 | -0.36445 | -0.083466 | 0.099921 | 0.019629 | 0.38408 | 0.080561 | 0.051712 | 122.9847 | 122.9441 | 123.0863 | 64.0466 | -123.1424 | 122.8902 | 123.0542 | 123.0253 | 61.6646 | -123.3381
1036.2656 | 123.1934 | -66.481 | 56.4606 | 0.04215 | -0.078975 | -0.010716 | 0.046755 | -0.014884 | 0.054873 | 0.058145 | -0.0068487 | 0.0032574 | 0.051427 | 0.082023 | 0.051845 | -66.3902 | -2.4665 | -66.3981 | 56.4716 | 56.4264 | 56.5687 | -66.6818 | -66.4223 | -4.8439 | -66.4889 | 56.3725 | 56.5366 | 56.5077 | -66.8821 | -0.20081 | 0.01103 | 0.090863 | 0.082963 | 0.28378 | -0.034125 | 0.10809 | -0.40108 | -0.088043 | 0.058722 | -0.007834 | 0.39324 | 0.075984 | 0.047135 | 122.9526 | 122.9075 | 123.0497 | 64.0146 | -123.1424 | 122.8535 | 123.0176 | 122.9887 | 61.6371 | -123.3427
1037.2656 | 123.1247 | -66.5314 | 56.488 | 0.026888 | -0.078975 | -0.011784 | 0.047824 | -0.018088 | 0.05701 | 0.073406 | -0.0057807 | 0.0021894 | 0.051427 | 0.082023 | 0.053982 | -66.3947 | -2.4756 | -66.3981 | 56.4808 | 56.4219 | 56.5687 | -66.6864 | -66.4177 | -4.8393 | -66.498 | 56.3771 | 56.532 | 56.5077 | -66.8867 | -0.15504 | -0.007279 | 0.13664 | 0.13332 | 0.28835 | -0.06617 | 0.080626 | -0.3553 | -0.11093 | 0.11365 | 0.033362 | 0.38866 | 0.043939 | 0.019669 | 123.0121 | 122.9532 | 123.1 | 64.0558 | -123.1744 | 122.9085 | 123.0633 | 123.0391 | 61.692 | -123.3747
1038.2656 | 123.1567 | -66.5039 | 56.4972 | 0.04215 | -0.078975 | -0.010716 | 0.046755 | -0.01702 | 0.055941 | 0.058145 | -0.0068487 | 0.0021894 | 0.050358 | 0.082023 | 0.051845 | -66.3947 | -2.471 | -66.4072 | 56.4808 | 56.4219 | 56.5778 | -66.6864 | -66.4223 | -4.8348 | -66.498 | 56.3679 | 56.532 | 56.5031 | -66.8821 | -0.1825 | -0.016434 | 0.10917 | 0.096694 | 0.2792 | -0.075325 | 0.080629 | -0.37819 | -0.12924 | 0.08161 | 0.005896 | 0.38408 | 0.034784 | 0.005935 | 122.9847 | 122.9258 | 123.0817 | 64.0329 | -123.1836 | 122.8719 | 123.0359 | 123.007 | 61.6691 | -123.3793
1039.2656 | 123.1247 | -66.5176 | 56.4606 | 0.011626 | -0.080044 | -0.0096467 | 0.046755 | -0.01702 | 0.053805 | 0.058145 | -0.0036447 | 5.2373e-05 | 0.04929 | 0.079887 | 0.051845 | -66.4039 | -2.4802 | -66.4072 | 56.467 | 56.4173 | 56.5732 | -66.6818 | -66.4223 | -4.8348 | -66.4889 | 56.3771 | 56.532 | 56.4985 | -66.8775 | -0.16419 | 0.006452 | 0.11375 | 0.11043 | 0.27462 | -0.043283 | 0.11267 | -0.35988 | -0.083465 | 0.095343 | 0.028787 | 0.38866 | 0.071405 | 0.037978 | 122.9847 | 122.9349 | 123.0909 | 64.0374 | -123.1424 | 122.8947 | 123.0496 | 123.0162 | 61.6829 | -123.3381
1040.2656 | 122.9691 | -66.5543 | 56.4468 | 0.04215 | -0.080044 | -0.012852 | 0.046755 | -0.018088 | 0.054873 | 0.042884 | -0.0047127 | 0.0021894 | 0.050358 | 0.082023 | 0.051845 | -66.3947 | -2.4848 | -66.4026 | 56.4716 | 56.4219 | 56.5687 | -66.6864 | -66.4223 | -4.8348 | -66.4889 | 56.3725 | 56.532 | 56.5031 | -66.8775 | -0.13215 | 0.024763 | 0.15953 | 0.15163 | 0.28377 | -0.024971 | 0.12183 | -0.32326 | -0.07431 | 0.13196 | 0.065408 | 0.38866 | 0.085138 | 0.056289 | 123.0259 | 122.9761 | 123.1229 | 64.0695 | -123.1332 | 122.9268 | 123.0862 | 123.0574 | 61.7195 | -123.3244
1041.2656 | 123.2666 | -66.4719 | 56.4651 | 0.04215 | -0.077907 | -0.012852 | 0.04996 | -0.018088 | 0.055941 | 0.058145 | -0.0068487 | 0.0021894 | 0.04929 | 0.082023 | 0.050777 | -66.3993 | -2.4848 | -66.4072 | 56.4716 | 56.431 | 56.5732 | -66.6864 | -66.4177 | -4.8256 | -66.5026 | 56.3679 | 56.532 | 56.5031 | -66.8867 | -0.21455 | 0.006452 | 0.072551 | 0.064651 | 0.2792 | -0.034124 | 0.10809 | -0.41481 | -0.0972 | 0.054145 | -0.030725 | 0.38408 | 0.066827 | 0.037978 | 122.9435 | 122.9029 | 123.0451 | 63.9871 | -123.1516 | 122.8398 | 123.0038 | 122.975 | 61.6463 | -123.3518
1042.2656 | 123.1522 | -66.5039 | 56.488 | 0.026888 | -0.078975 | -0.012852 | 0.048892 | -0.018088 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.04929 | 0.082023 | 0.052914 | -66.3993 | -2.4894 | -66.4026 | 56.4716 | 56.4264 | 56.5732 | -66.6818 | -66.4177 | -4.8393 | -66.4934 | 56.3771 | 56.532 | 56.5031 | -66.8821 | -0.17792 | -0.016436 | 0.10459 | 0.10127 | 0.2792 | -0.061591 | 0.085205 | -0.37819 | -0.11093 | 0.086188 | 0.010475 | 0.38866 | 0.043939 | 0.01509 | 122.9755 | 122.9304 | 123.0771 | 64.0146 | -123.1699 | 122.881 | 123.0359 | 123.007 | 61.6646 | -123.3701
1043.2656 | 123.1705 | -66.5131 | 56.4835 | 0.057412 | -0.080044 | -0.0096467 | 0.046755 | -0.019157 | 0.053805 | 0.058145 | -0.0068487 | 0.0021894 | 0.050358 | 0.082023 | 0.052914 | -66.4039 | -2.4985 | -66.4072 | 56.4808 | 56.4219 | 56.5778 | -66.6864 | -66.4223 | -4.821 | -66.5026 | 56.3771 | 56.5274 | 56.5031 | -66.8821 | -0.17335 | -0.002701 | 0.10917 | 0.10585 | 0.2792 | -0.061592 | 0.094362 | -0.36903 | -0.10635 | 0.090766 | 0.010474 | 0.37951 | 0.043938 | 0.019668 | 122.9938 | 122.9349 | 123.0909 | 64.0146 | -123.1699 | 122.8902 | 123.0405 | 123.0162 | 61.692 | -123.3656
1044.2656 | 123.1567 | -66.4993 | 56.4743 | 0.026888 | -0.080044 | -0.011784 | 0.047824 | -0.019157 | 0.053805 | 0.088667 | -0.0057807 | 0.0011204 | 0.050358 | 0.082023 | 0.052914 | -66.4039 | -2.5077 | -66.4118 | 56.4762 | 56.4264 | 56.5732 | -66.6818 | -66.4223 | -4.821 | -66.498 | 56.3679 | 56.532 | 56.5031 | -66.8867 | -0.1825 | 0.001876 | 0.095439 | 0.087539 | 0.27004 | -0.047858 | 0.098938 | -0.38734 | -0.10635 | 0.077033 | 0.001319 | 0.38866 | 0.057672 | 0.028823 | 122.9755 | 122.9258 | 123.0726 | 63.9917 | -123.1561 | 122.8673 | 123.0313 | 123.0025 | 61.6783 | -123.361
1045.2656 | 123.1979 | -66.4948 | 56.4789 | 0.057412 | -0.078975 | -0.011784 | 0.046755 | -0.01702 | 0.054873 | 0.058145 | -0.0057807 | 5.2373e-05 | 0.051427 | 0.080955 | 0.049709 | -66.3993 | -2.5031 | -66.4118 | 56.4716 | 56.4264 | 56.5778 | -66.6818 | -66.4315 | -4.8119 | -66.5026 | 56.3725 | 56.5366 | 56.5031 | -66.8821 | -0.18708 | -0.007281 | 0.095439 | 0.082961 | 0.27004 | -0.052436 | 0.098939 | -0.38734 | -0.10635 | 0.063297 | -0.007837 | 0.37951 | 0.057673 | 0.024245 | 122.9664 | 122.9212 | 123.0726 | 63.9917 | -123.1607 | 122.8673 | 123.0313 | 122.9979 | 61.6829 | -123.361
1046.6719 | 123.1338 | -66.5131 | 56.4743 | 0.072674 | -0.078975 | -0.012852 | 0.047824 | -0.019157 | 0.053805 | 0.042884 | -0.0079177 | 0.0032574 | 0.051427 | 0.079887 | 0.050777 | -66.4039 | -2.5077 | -66.4072 | 56.4762 | 56.4173 | 56.5687 | -66.6773 | -66.4223 | -4.8164 | -66.5026 | 56.3634 | 56.5366 | 56.5031 | -66.8867 | -0.16419 | 0.001876 | 0.10917 | 0.10585 | 0.27004 | -0.057016 | 0.094359 | -0.37361 | -0.11093 | 0.090766 | 0.010474 | 0.38408 | 0.062251 | 0.028823 | 122.9892 | 122.9304 | 123.0817 | 64.0054 | -123.1516 | 122.8764 | 123.0496 | 123.0162 | 61.6966 | -123.361
1047.3281 | 123.1613 | -66.5222 | 56.4514 | 0.04215 | -0.080044 | -0.012852 | 0.048892 | -0.018088 | 0.055941 | 0.058145 | -0.0036447 | 0.0011204 | 0.050358 | 0.079887 | 0.051845 | -66.4085 | -2.5122 | -66.4118 | 56.467 | 56.4219 | 56.5641 | -66.6818 | -66.4223 | -4.8256 | -66.4934 | 56.3634 | 56.5366 | 56.5031 | -66.8821 | -0.15961 | 0.015607 | 0.11375 | 0.11043 | 0.27004 | -0.029549 | 0.11267 | -0.35988 | -0.088045 | 0.099921 | 0.028786 | 0.38866 | 0.085139 | 0.051711 | 122.9892 | 122.9441 | 123.0863 | 64.01 | -123.1332 | 122.8856 | 123.0588 | 123.0253 | 61.6966 | -123.3335
1048.2656 | 123.2162 | -66.4993 | 56.4606 | 0.04215 | -0.081112 | -0.012852 | 0.048892 | -0.01702 | 0.053805 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.04929 | 0.083092 | 0.051845 | -66.4039 | -2.5031 | -66.4072 | 56.467 | 56.4127 | 56.5778 | -66.691 | -66.4315 | -4.8256 | -66.4934 | 56.3679 | 56.5366 | 56.494 | -66.8867 | -0.19166 | 0.006452 | 0.095439 | 0.092117 | 0.28378 | -0.047862 | 0.11725 | -0.38734 | -0.092622 | 0.067875 | 0.005898 | 0.39324 | 0.075984 | 0.033399 | 122.9664 | 122.912 | 123.0772 | 63.9962 | -123.1516 | 122.8673 | 123.0359 | 122.9933 | 61.6737 | -123.3472
1049.2656 | 123.1979 | -66.5176 | 56.4835 | 0.04215 | -0.078975 | -0.012852 | 0.047824 | -0.019157 | 0.052737 | 0.058145 | -0.0057807 | 5.2373e-05 | 0.052495 | 0.082023 | 0.053982 | -66.4039 | -2.5168 | -66.4118 | 56.4579 | 56.3578 | 56.5641 | -66.6864 | -66.436 | -4.8164 | -66.5026 | 56.3679 | 56.5274 | 56.4985 | -66.8867 | -0.16877 | -0.025593 | 0.11375 | 0.10585 | 0.27462 | -0.1257 | 0.080626 | -0.36903 | -0.11551 | 0.081607 | 0.015051 | 0.38408 | 0.043938 | 0.01509 | 122.9755 | 122.8754 | 123.0817 | 64.0008 | -123.1699 | 122.8856 | 123.045 | 123.0162 | 61.7012 | -123.3701
1050.2656 | 123.1934 | -66.5176 | 56.488 | 0.04215 | -0.081112 | -0.012852 | 0.047824 | -0.015952 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.04929 | 0.08416 | 0.051845 | -66.4039 | -2.5214 | -66.4209 | 56.467 | 56.3532 | 56.5687 | -66.6864 | -66.436 | -4.821 | -66.5026 | 56.3679 | 56.5274 | 56.4894 | -66.8821 | -0.16877 | -0.021014 | 0.11375 | 0.096692 | 0.26546 | -0.13485 | 0.080626 | -0.36445 | -0.12009 | 0.081607 | 0.015051 | 0.37951 | 0.03936 | 0.001354 | 122.9847 | 122.8708 | 123.0863 | 63.9962 | -123.1744 | 122.8856 | 123.045 | 123.007 | 61.6966 | -123.3701
1051.2656 | 123.175 | -66.5085 | 56.5109 | 0.04215 | -0.080044 | -0.011784 | 0.047824 | -0.01702 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.04929 | 0.082023 | 0.052914 | -66.4085 | -2.5122 | -66.4164 | 56.467 | 56.3761 | 56.5687 | -66.6864 | -66.4406 | -4.8119 | -66.5072 | 56.3679 | 56.532 | 56.494 | -66.8821 | -0.17793 | -0.043902 | 0.10002 | 0.092115 | 0.27004 | -0.13485 | 0.057738 | -0.37361 | -0.14298 | 0.067873 | 0.001317 | 0.37493 | 0.021051 | -0.016955 | 122.9755 | 122.8846 | 123.0771 | 63.9962 | -123.1973 | 122.8764 | 123.0405 | 123.0025 | 61.6966 | -123.393
1052.2656 | 123.1476 | -66.5176 | 56.4835 | 0.057412 | -0.080044 | -0.010716 | 0.047824 | -0.01702 | 0.052737 | 0.073406 | -0.0057807 | 5.2373e-05 | 0.050358 | 0.082023 | 0.051845 | -66.4039 | -2.5122 | -66.4255 | 56.4624 | 56.3807 | 56.5687 | -66.6864 | -66.4406 | -4.8119 | -66.5072 | 56.3634 | 56.532 | 56.4985 | -66.8913 | -0.16877 | -0.021014 | 0.11375 | 0.092114 | 0.26088 | -0.1028 | 0.085204 | -0.37361 | -0.12009 | 0.077028 | 0.010472 | 0.38408 | 0.048517 | 0.01509 | 122.9801 | 122.8983 | 123.0863 | 64.0054 | -123.1699 | 122.881 | 123.0496 | 123.0162 | 61.7058 | -123.3747
1053.2656 | 123.3124 | -66.4948 | 56.4789 | 0.04215 | -0.080044 | -0.011784 | 0.048892 | -0.019157 | 0.054873 | 0.073406 | -0.0057807 | 0.0011204 | 0.051427 | 0.082023 | 0.050777 | -66.4039 | -2.5168 | -66.4209 | 56.4624 | 56.4036 | 56.5687 | -66.6864 | -66.4315 | -4.8073 | -66.5072 | 56.3679 | 56.532 | 56.4985 | -66.8867 | -0.19166 | -0.016437 | 0.090861 | 0.073804 | 0.26546 | -0.075331 | 0.089781 | -0.39192 | -0.11093 | 0.063297 | -0.012416 | 0.37951 | 0.053094 | 0.019667 | 122.9572 | 122.8983 | 123.0634 | 63.9779 | -123.1653 | 122.8627 | 123.0267 | 122.9933 | 61.6875 | -123.3656
1054.2656 | 123.1888 | -66.5131 | 56.4697 | 0.026888 | -0.080044 | -0.011784 | 0.04996 | -0.019157 | 0.053805 | 0.058145 | -0.0079177 | 0.0011204 | 0.053563 | 0.082023 | 0.050777 | -66.3993 | -2.526 | -66.4164 | 56.4624 | 56.4173 | 56.5641 | -66.6956 | -66.436 | -4.8027 | -66.5072 | 56.3679 | 56.532 | 56.494 | -66.8867 | -0.1825 | -0.007282 | 0.11375 | 0.096693 | 0.2792 | -0.052439 | 0.094358 | -0.37361 | -0.10178 | 0.07703 | 0.005895 | 0.37951 | 0.062249 | 0.024243 | 122.9755 | 122.9304 | 123.0771 | 63.9871 | -123.1653 | 122.881 | 123.045 | 123.007 | 61.7104 | -123.3564
1055.2656 | 123.1888 | -66.5222 | 56.4606 | 0.04215 | -0.082181 | -0.010716 | 0.047824 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.048222 | 0.083092 | 0.051845 | -66.4039 | -2.5168 | -66.4209 | 56.4716 | 56.4219 | 56.5641 | -66.691 | -66.4452 | -4.7981 | -66.5072 | 56.3679 | 56.532 | 56.494 | -66.8867 | -0.16877 | 0.01103 | 0.11833 | 0.10127 | 0.27004 | -0.038704 | 0.10351 | -0.36446 | -0.092622 | 0.077027 | 0.01505 | 0.37951 | 0.071405 | 0.033399 | 122.9938 | 122.9441 | 123.0863 | 64.0054 | -123.1516 | 122.8902 | 123.0542 | 123.0162 | 61.7241 | -123.3472
1056.2656 | 123.1934 | -66.5085 | 56.4743 | 0.026888 | -0.081112 | -0.011784 | 0.047824 | -0.019157 | 0.053805 | 0.027623 | -0.0068487 | 0.0011204 | 0.04929 | 0.083092 | 0.050777 | -66.4085 | -2.526 | -66.4301 | 56.4624 | 56.4173 | 56.5687 | -66.6956 | -66.436 | -4.7935 | -66.5072 | 56.3679 | 56.5274 | 56.4985 | -66.8913 | -0.18708 | -0.011859 | 0.10002 | 0.078381 | 0.26546 | -0.057016 | 0.094359 | -0.38277 | -0.10635 | 0.072452 | 0.001317 | 0.38408 | 0.053093 | 0.024245 | 122.9709 | 122.9258 | 123.0771 | 63.9825 | -123.1699 | 122.8764 | 123.0359 | 123.007 | 61.7149 | -123.3656
1057.2656 | 123.1842 | -66.4993 | 56.4835 | 0.026888 | -0.082181 | -0.011784 | 0.048892 | -0.018088 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.050358 | 0.083092 | 0.052914 | -66.4085 | -2.5168 | -66.4255 | 56.4716 | 56.4127 | 56.5732 | -66.691 | -66.4452 | -4.789 | -66.5117 | 56.3634 | 56.532 | 56.5031 | -66.8913 | -0.19166 | -0.011858 | 0.090861 | 0.073804 | 0.26546 | -0.07075 | 0.089783 | -0.39192 | -0.12009 | 0.054139 | -0.012417 | 0.37951 | 0.048517 | 0.019668 | 122.9709 | 122.912 | 123.0726 | 63.9825 | -123.1744 | 122.8627 | 123.0313 | 123.0025 | 61.7104 | -123.3747
1058.2656 | 123.1796 | -66.5131 | 56.4926 | 0.026888 | -0.081112 | -0.011784 | 0.047824 | -0.019157 | 0.053805 | 0.042884 | -0.0089857 | 0.0011204 | 0.04929 | 0.082023 | 0.051845 | -66.4085 | -2.5168 | -66.4255 | 56.4716 | 56.4219 | 56.5687 | -66.6864 | -66.4406 | -4.789 | -66.5117 | 56.3634 | 56.5274 | 56.4985 | -66.8867 | -0.17335 | -0.021014 | 0.10459 | 0.087537 | 0.26088 | -0.070748 | 0.076048 | -0.37361 | -0.12924 | 0.072451 | 0.001316 | 0.37493 | 0.034782 | 0.005934 | 122.9847 | 122.9349 | 123.0817 | 63.9962 | -123.179 | 122.8764 | 123.0405 | 123.0116 | 61.7241 | -123.3793
1059.2656 | 123.2346 | -66.4993 | 56.488 | 0.026888 | -0.082181 | -0.0096467 | 0.047824 | -0.019157 | 0.055941 | 0.073406 | -0.0068487 | 0.0011204 | 0.048222 | 0.079887 | 0.051845 | -66.4039 | -2.5168 | -66.4301 | 56.4624 | 56.4173 | 56.5732 | -66.6956 | -66.4406 | -4.789 | -66.5072 | 56.3725 | 56.532 | 56.494 | -66.8913 | -0.19624 | -0.025592 | 0.095439 | 0.069226 | 0.26546 | -0.070749 | 0.085205 | -0.39192 | -0.11551 | 0.058718 | -0.007838 | 0.38408 | 0.043939 | 0.005933 | 122.9618 | 122.9166 | 123.0726 | 63.9825 | -123.1836 | 122.8719 | 123.0313 | 122.9933 | 61.7104 | -123.3793
1060.2656 | 123.1842 | -66.5085 | 56.4423 | 0.026888 | -0.082181 | -0.011784 | 0.047824 | -0.019157 | 0.054873 | 0.073406 | -0.0057807 | 0.0011204 | 0.050358 | 0.083092 | 0.051845 | -66.4039 | -2.5214 | -66.4301 | 56.467 | 56.4127 | 56.5687 | -66.6956 | -66.4406 | -4.7798 | -66.5072 | 56.3679 | 56.5228 | 56.4985 | -66.8867 | -0.18708 | 0.024762 | 0.10459 | 0.078381 | 0.26546 | -0.029552 | 0.1264 | -0.37819 | -0.074312 | 0.067873 | 0.001317 | 0.37951 | 0.080558 | 0.056288 | 122.9755 | 122.9212 | 123.0771 | 63.9871 | -123.1378 | 122.8764 | 123.0313 | 123.007 | 61.7287 | -123.3289
1061.2656 | 123.175 | -66.5131 | 56.4468 | 0.057412 | -0.081112 | -0.010716 | 0.048892 | -0.01702 | 0.053805 | 0.042884 | -0.0057807 | 0.0021894 | 0.04929 | 0.080955 | 0.051845 | -66.413 | -2.5168 | -66.4301 | 56.467 | 56.4219 | 56.5687 | -66.6956 | -66.4452 | -4.7798 | -66.5072 | 56.3679 | 56.5228 | 56.4985 | -66.8867 | -0.1825 | 0.020185 | 0.10001 | 0.082959 | 0.26546 | -0.024971 | 0.12183 | -0.37361 | -0.078889 | 0.067872 | 0.005895 | 0.37951 | 0.075981 | 0.051711 | 122.9801 | 122.9349 | 123.0817 | 63.9962 | -123.1424 | 122.881 | 123.0359 | 123.0116 | 61.7332 | -123.3335
1062.2656 | 123.175 | -66.4993 | 56.4651 | 0.04215 | -0.080044 | -0.011784 | 0.048892 | -0.018088 | 0.054873 | 0.058145 | -0.0089857 | 5.2373e-05 | 0.050358 | 0.08416 | 0.051845 | -66.413 | -2.5214 | -66.4255 | 56.4716 | 56.4219 | 56.5687 | -66.6956 | -66.436 | -4.7752 | -66.5117 | 56.3634 | 56.5228 | 56.5031 | -66.8867 | -0.19624 | 0.006452 | 0.086282 | 0.073804 | 0.27004 | -0.043282 | 0.10351 | -0.38734 | -0.10178 | 0.063297 | -0.012417 | 0.37493 | 0.05767 | 0.037978 | 122.9709 | 122.9212 | 123.068 | 63.9779 | -123.1607 | 122.8627 | 123.0221 | 123.0025 | 61.7241 | -123.3518
1063.2656 | 123.1842 | -66.5085 | 56.456 | 0.057412 | -0.082181 | -0.010716 | 0.048892 | -0.018088 | 0.053805 | 0.058145 | -0.0068487 | 0.0021894 | 0.04929 | 0.083092 | 0.053982 | -66.4085 | -2.5168 | -66.4255 | 56.4624 | 56.4173 | 56.5778 | -66.6956 | -66.4406 | -4.7752 | -66.5072 | 56.3634 | 56.5274 | 56.4985 | -66.8913 | -0.18708 | 0.006451 | 0.10002 | 0.082959 | 0.27004 | -0.038706 | 0.12183 | -0.38277 | -0.092623 | 0.067873 | 0.001317 | 0.38408 | 0.071403 | 0.042555 | 122.9709 | 122.9258 | 123.0863 | 63.9917 | -123.1516 | 122.8719 | 123.0359 | 123.007 | 61.7332 | -123.3472
1064.2656 | 123.1979 | -66.5039 | 56.4606 | 0.04215 | -0.081112 | -0.0096467 | 0.048892 | -0.01702 | 0.052737 | 0.042884 | -0.0047127 | 5.2373e-05 | 0.050358 | 0.083092 | 0.052914 | -66.413 | -2.5214 | -66.4347 | 56.4716 | 56.4264 | 56.5778 | -66.691 | -66.4498 | -4.7707 | -66.5117 | 56.3634 | 56.532 | 56.5031 | -66.8867 | -0.18708 | 0.01103 | 0.090859 | 0.069224 | 0.25631 | -0.034125 | 0.11725 | -0.38277 | -0.0972 | 0.054137 | -0.00784 | 0.37493 | 0.071405 | 0.042556 | 122.9755 | 122.9304 | 123.0817 | 63.9825 | -123.1516 | 122.8673 | 123.0359 | 123.007 | 61.7332 | -123.3472
1065.2656 | 123.175 | -66.5131 | 56.4789 | 0.057412 | -0.081112 | -0.010716 | 0.048892 | -0.01702 | 0.055941 | 0.042884 | -0.0079177 | 0.0011204 | 0.052495 | 0.082023 | 0.052914 | -66.4176 | -2.5214 | -66.4209 | 56.467 | 56.4127 | 56.5641 | -66.691 | -66.4452 | -4.7569 | -66.5117 | 56.3634 | 56.5228 | 56.4985 | -66.8958 | -0.17793 | -0.011859 | 0.095437 | 0.092115 | 0.27004 | -0.066173 | 0.085203 | -0.38277 | -0.11551 | 0.067872 | 0.001316 | 0.38408 | 0.043937 | 0.019667 | 122.9801 | 122.9258 | 123.0771 | 63.9917 | -123.1699 | 122.8764 | 123.0359 | 123.0116 | 61.7561 | -123.3747
1066.2656 | 123.2025 | -66.4993 | 56.4972 | 0.04215 | -0.082181 | -0.011784 | 0.047824 | -0.018088 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.04929 | 0.082023 | 0.050777 | -66.413 | -2.5168 | -66.4301 | 56.4624 | 56.4127 | 56.5687 | -66.691 | -66.4498 | -4.7569 | -66.5117 | 56.3588 | 56.5228 | 56.4894 | -66.8867 | -0.19166 | -0.034747 | 0.086282 | 0.069226 | 0.26089 | -0.084483 | 0.071471 | -0.38734 | -0.1384 | 0.04956 | -0.012417 | 0.37493 | 0.025627 | -0.007801 | 122.9618 | 122.912 | 123.068 | 63.9825 | -123.1882 | 122.8581 | 123.0221 | 122.9887 | 61.7424 | -123.3839
1067.2656 | 123.1888 | -66.5039 | 56.4651 | 0.057412 | -0.082181 | -0.012852 | 0.046755 | -0.019157 | 0.054873 | 0.073406 | -0.0068487 | 0.0011204 | 0.04929 | 0.082023 | 0.052914 | -66.4176 | -2.526 | -66.4347 | 56.467 | 56.4127 | 56.5641 | -66.691 | -66.4498 | -4.7523 | -66.5117 | 56.3634 | 56.5228 | 56.4894 | -66.8958 | -0.18708 | 0.001874 | 0.086281 | 0.069224 | 0.25631 | -0.05244 | 0.098936 | -0.39193 | -0.10178 | 0.054137 | -0.00784 | 0.38408 | 0.05767 | 0.024242 | 122.9709 | 122.9166 | 123.068 | 63.9779 | -123.1561 | 122.8673 | 123.0267 | 122.9933 | 61.7516 | -123.361
1068.2656 | 123.1613 | -66.4948 | 56.4377 | 0.04215 | -0.083249 | -0.010716 | 0.048892 | -0.018088 | 0.052737 | 0.058145 | -0.0047127 | 5.2373e-05 | 0.051427 | 0.08416 | 0.049709 | -66.4268 | -2.5214 | -66.4347 | 56.467 | 56.4036 | 56.5641 | -66.691 | -66.4452 | -4.7523 | -66.5072 | 56.3588 | 56.5228 | 56.4894 | -66.8913 | -0.19624 | 0.02934 | 0.067969 | 0.060069 | 0.25631 | -0.034132 | 0.1264 | -0.3965 | -0.078891 | 0.049561 | -0.012416 | 0.38408 | 0.085136 | 0.051708 | 122.9618 | 122.8983 | 123.0588 | 63.9733 | -123.1287 | 122.8535 | 123.0176 | 122.9841 | 61.7424 | -123.3289
1069.2656 | 123.1979 | -66.5131 | 56.456 | 0.072674 | -0.082181 | -0.010716 | 0.048892 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 5.2373e-05 | 0.04929 | 0.083092 | 0.051845 | -66.4176 | -2.5214 | -66.4301 | 56.467 | 56.4036 | 56.5687 | -66.7001 | -66.4498 | -4.7478 | -66.5117 | 56.3634 | 56.5228 | 56.4894 | -66.8958 | -0.18708 | 0.011029 | 0.095437 | 0.082959 | 0.27004 | -0.052443 | 0.11267 | -0.38277 | -0.092623 | 0.063293 | 0.001316 | 0.38408 | 0.066825 | 0.033397 | 122.9801 | 122.9166 | 123.0817 | 63.9917 | -123.1561 | 122.8764 | 123.0359 | 123.0025 | 61.7653 | -123.3518
1070.2656 | 123.2025 | -66.481 | 56.4743 | 0.04215 | -0.082181 | -0.012852 | 0.047824 | -0.018088 | 0.054873 | 0.058145 | -0.0047127 | 0.0032574 | 0.050358 | 0.085228 | 0.050777 | -66.4222 | -2.526 | -66.4347 | 56.467 | 56.4173 | 56.5687 | -66.6956 | -66.4452 | -4.7478 | -66.5163 | 56.3588 | 56.5228 | 56.4894 | -66.8958 | -0.21455 | -0.007281 | 0.058814 | 0.046336 | 0.26089 | -0.057016 | 0.094359 | -0.41481 | -0.11551 | 0.035828 | -0.035307 | 0.37951 | 0.048515 | 0.015087 | 122.948 | 122.8983 | 123.0497 | 63.955 | -123.1699 | 122.8398 | 123.0038 | 122.9704 | 61.7333 | -123.3701
1071.2656 | 123.1842 | -66.5314 | 56.4835 | 0.057412 | -0.082181 | -0.010716 | 0.048892 | -0.018088 | 0.052737 | 0.073406 | -0.0068487 | 0.0021894 | 0.04929 | 0.083092 | 0.049709 | -66.4176 | -2.5214 | -66.4393 | 56.4716 | 56.4127 | 56.5687 | -66.7001 | -66.4543 | -4.7432 | -66.5163 | 56.3588 | 56.5182 | 56.4985 | -66.8958 | -0.16877 | -0.011858 | 0.11375 | 0.092112 | 0.26089 | -0.07075 | 0.085204 | -0.36446 | -0.12467 | 0.077025 | 0.015047 | 0.37951 | 0.034781 | 0.01509 | 123.003 | 122.9441 | 123.1 | 64.01 | -123.1836 | 122.8902 | 123.0496 | 123.0299 | 61.7882 | -123.3793
1072.2656 | 123.175 | -66.4902 | 56.5018 | 0.04215 | -0.080044 | -0.011784 | 0.047824 | -0.01702 | 0.055941 | 0.058145 | -0.0057807 | 0.0011204 | 0.04929 | 0.083092 | 0.048641 | -66.4222 | -2.5168 | -66.4438 | 56.467 | 56.4127 | 56.5732 | -66.7093 | -66.4452 | -4.7478 | -66.5117 | 56.3588 | 56.5228 | 56.494 | -66.8913 | -0.21913 | -0.034747 | 0.067969 | 0.046335 | 0.26547 | -0.089061 | 0.071472 | -0.40108 | -0.14298 | 0.044983 | -0.021573 | 0.37951 | 0.021049 | -0.0078 | 122.9572 | 122.9029 | 123.0634 | 63.9733 | -123.2111 | 122.849 | 123.013 | 122.9841 | 61.7424 | -123.393
1073.2656 | 123.1522 | -66.5222 | 56.5018 | 0.057412 | -0.082181 | -0.012852 | 0.048892 | -0.019157 | 0.055941 | 0.073406 | -0.0057807 | 0.0011204 | 0.050358 | 0.083092 | 0.051845 | -66.4222 | -2.5168 | -66.4393 | 56.4624 | 56.4219 | 56.5687 | -66.7047 | -66.4452 | -4.7432 | -66.5117 | 56.3679 | 56.5274 | 56.4985 | -66.905 | -0.18251 | -0.039325 | 0.10001 | 0.082957 | 0.26546 | -0.079903 | 0.066893 | -0.38277 | -0.13382 | 0.077027 | 0.010471 | 0.39324 | 0.025627 | -0.003221 | 122.9847 | 122.9441 | 123.0909 | 64.0054 | -123.2065 | 122.8902 | 123.0496 | 123.0208 | 61.779 | -123.4068
1074.2656 | 123.2208 | -66.5085 | 56.4972 | 0.072674 | -0.080044 | -0.011784 | 0.047824 | -0.018088 | 0.053805 | 0.042884 | -0.0079177 | 0.0021894 | 0.04929 | 0.085228 | 0.051845 | -66.4176 | -2.526 | -66.4347 | 56.467 | 56.4264 | 56.5641 | -66.7047 | -66.4589 | -4.7386 | -66.5255 | 56.3588 | 56.5274 | 56.494 | -66.9004 | -0.19624 | -0.030169 | 0.090859 | 0.073802 | 0.27004 | -0.070746 | 0.066893 | -0.39193 | -0.1384 | 0.049558 | -0.016998 | 0.37493 | 0.030205 | -0.003222 | 122.9755 | 122.9349 | 123.0726 | 63.9825 | -123.2019 | 122.8673 | 123.0359 | 123.0025 | 61.7699 | -123.3976
1075.2656 | 123.1934 | -66.5131 | 56.4606 | 0.04215 | -0.081112 | -0.011784 | 0.048892 | -0.018088 | 0.054873 | 0.073406 | -0.0068487 | 0.0032574 | 0.048222 | 0.08416 | 0.053982 | -66.4176 | -2.5122 | -66.4347 | 56.4579 | 56.4173 | 56.5687 | -66.7093 | -66.4498 | -4.7294 | -66.5163 | 56.3634 | 56.5182 | 56.494 | -66.8958 | -0.19624 | -0.002705 | 0.095437 | 0.07838 | 0.27462 | -0.043283 | 0.10809 | -0.38277 | -0.0972 | 0.063293 | -0.003263 | 0.37951 | 0.057669 | 0.033399 | 122.9709 | 122.9304 | 123.0817 | 64.0008 | -123.1699 | 122.8764 | 123.0313 | 123.007 | 61.7836 | -123.3564
1076.2656 | 123.1796 | -66.5176 | 56.4606 | 0.072674 | -0.083249 | -0.011784 | 0.047824 | -0.018088 | 0.053805 | 0.058145 | -0.0068487 | 0.0011204 | 0.04929 | 0.083092 | 0.051845 | -66.4222 | -2.5122 | -66.4347 | 56.4716 | 56.4173 | 56.5595 | -66.7001 | -66.4543 | -4.7294 | -66.5163 | 56.3634 | 56.5137 | 56.494 | -66.9004 | -0.18251 | 0.01103 | 0.095435 | 0.082957 | 0.26546 | -0.043283 | 0.098935 | -0.38277 | -0.0972 | 0.063292 | 0.001314 | 0.38408 | 0.053091 | 0.033399 | 122.9892 | 122.9349 | 123.0771 | 64.0054 | -123.1607 | 122.881 | 123.0313 | 123.0116 | 61.7882 | -123.361
1077.2656 | 123.175 | -66.5039 | 56.488 | 0.04215 | -0.082181 | -0.012852 | 0.04996 | -0.018088 | 0.055941 | 0.073406 | -0.0068487 | 0.0021894 | 0.050358 | 0.082023 | 0.050777 | -66.4268 | -2.5031 | -66.4301 | 56.4579 | 56.4173 | 56.5595 | -66.7047 | -66.4452 | -4.7249 | -66.5163 | 56.3542 | 56.5182 | 56.494 | -66.8913 | -0.20082 | -0.030171 | 0.077124 | 0.073803 | 0.27462 | -0.070749 | 0.071469 | -0.38735 | -0.13382 | 0.058716 | -0.012419 | 0.37493 | 0.030203 | 0.005933 | 122.9618 | 122.9212 | 123.0634 | 64.0008 | -123.1928 | 122.8581 | 123.0221 | 122.9979 | 61.779 | -123.3793
1078.2656 | 123.2025 | -66.5222 | 56.4972 | 0.04215 | -0.083249 | -0.011784 | 0.046755 | -0.018088 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.051427 | 0.083092 | 0.051845 | -66.4176 | -2.5077 | -66.4393 | 56.4579 | 56.4081 | 56.5641 | -66.7001 | -66.4543 | -4.7111 | -66.5209 | 56.3588 | 56.5228 | 56.4894 | -66.9004 | -0.17793 | -0.039326 | 0.10459 | 0.082957 | 0.26089 | -0.089062 | 0.066893 | -0.37819 | -0.1384 | 0.06787 | 0.001314 | 0.37951 | 0.025627 | -0.007801 | 122.9801 | 122.9303 | 123.0863 | 64.0145 | -123.1973 | 122.881 | 123.045 | 123.0116 | 61.8111 | -123.3976
1079.2656 | 123.143 | -66.5131 | 56.4743 | 0.057412 | -0.082181 | -0.010716 | 0.048892 | -0.018088 | 0.053805 | 0.042884 | -0.0057807 | 5.2373e-05 | 0.051427 | 0.085228 | 0.050777 | -66.413 | -2.5077 | -66.4347 | 56.4533 | 56.4127 | 56.5641 | -66.7047 | -66.4498 | -4.7203 | -66.5255 | 56.3634 | 56.5182 | 56.4894 | -66.8958 | -0.19166 | -0.021016 | 0.10001 | 0.07838 | 0.27004 | -0.061595 | 0.089781 | -0.38277 | -0.11093 | 0.063293 | -0.01242 | 0.37035 | 0.043936 | 0.015087 | 122.9664 | 122.9258 | 123.0771 | 64.0054 | -123.179 | 122.8764 | 123.0313 | 123.0025 | 61.7928 | -123.3701
1080.2656 | 123.1659 | -66.5268 | 56.488 | 0.057412 | -0.083249 | -0.010716 | 0.046755 | -0.018088 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.04929 | 0.08416 | 0.050777 | -66.4268 | -2.5077 | -66.4347 | 56.4579 | 56.4036 | 56.5641 | -66.7001 | -66.4498 | -4.7157 | -66.5209 | 56.3588 | 56.5182 | 56.4802 | -66.9004 | -0.17335 | -0.030171 | 0.10001 | 0.092112 | 0.26546 | -0.084486 | 0.076048 | -0.37362 | -0.12924 | 0.077025 | 0.005891 | 0.37951 | 0.030203 | -0.007803 | 122.9847 | 122.9303 | 123.0909 | 64.0191 | -123.1882 | 122.8856 | 123.045 | 123.007 | 61.8111 | -123.3884
1081.2656 | 123.1476 | -66.5176 | 56.488 | 0.057412 | -0.083249 | -0.0096467 | 0.047824 | -0.015952 | 0.054873 | 0.058145 | -0.0079177 | 0.0021894 | 0.050358 | 0.08416 | 0.051845 | -66.4222 | -2.4985 | -66.4393 | 56.4579 | 56.4127 | 56.5687 | -66.7047 | -66.4589 | -4.7157 | -66.5255 | 56.3542 | 56.5228 | 56.4894 | -66.905 | -0.18709 | -0.030171 | 0.095435 | 0.078379 | 0.26546 | -0.075328 | 0.080626 | -0.38735 | -0.13382 | 0.058713 | -0.007843 | 0.37951 | 0.034782 | 0.001354 | 122.9755 | 122.9303 | 123.0863 | 64.0191 | -123.1928 | 122.8719 | 123.0405 | 123.007 | 61.8019 | -123.393
1082.2656 | 123.2117 | -66.5405 | 56.4651 | 0.04215 | -0.082181 | -0.0096467 | 0.046755 | -0.018088 | 0.055941 | 0.088667 | -0.0079177 | 0.0021894 | 0.048222 | 0.08416 | 0.050777 | -66.4222 | -2.5077 | -66.4347 | 56.4579 | 56.4127 | 56.5641 | -66.7001 | -66.4543 | -4.7157 | -66.5255 | 56.3542 | 56.5182 | 56.494 | -66.9004 | -0.15962 | -0.007283 | 0.11832 | 0.10585 | 0.26546 | -0.05244 | 0.098936 | -0.35988 | -0.11093 | 0.08618 | 0.015045 | 0.37493 | 0.053091 | 0.028821 | 122.9984 | 122.9532 | 123.1046 | 64.0329 | -123.1653 | 122.8947 | 123.0588 | 123.0345 | 61.8248 | -123.3656
1083.2656 | 123.1613 | -66.5085 | 56.4835 | 0.026888 | -0.082181 | -0.0096467 | 0.048892 | -0.019157 | 0.053805 | 0.042884 | -0.0079177 | 0.0021894 | 0.048222 | 0.08416 | 0.050777 | -66.4268 | -2.4939 | -66.4393 | 56.4579 | 56.4127 | 56.5595 | -66.7047 | -66.4543 | -4.7157 | -66.5117 | 56.3634 | 56.5091 | 56.4848 | -66.9096 | -0.19624 | -0.025593 | 0.081702 | 0.069224 | 0.26546 | -0.07075 | 0.076047 | -0.40108 | -0.12009 | 0.054137 | -0.003262 | 0.39782 | 0.025624 | 0.001354 | 122.9664 | 122.9212 | 123.068 | 64.0146 | -123.1882 | 122.8719 | 123.0176 | 122.9933 | 61.7928 | -123.393
1084.2656 | 123.1567 | -66.5222 | 56.4972 | 0.057412 | -0.084317 | -0.011784 | 0.046755 | -0.018088 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.052495 | 0.08416 | 0.052914 | -66.4314 | -2.4894 | -66.4393 | 56.4624 | 56.4127 | 56.5641 | -66.7047 | -66.436 | -4.7066 | -66.5255 | 56.3542 | 56.5182 | 56.4848 | -66.8958 | -0.18251 | -0.034747 | 0.090857 | 0.082957 | 0.26546 | -0.084483 | 0.066893 | -0.37361 | -0.14298 | 0.086185 | -0.003265 | 0.37035 | 0.021048 | -0.012379 | 122.9847 | 122.9349 | 123.0863 | 64.0329 | -123.2019 | 122.8764 | 123.0405 | 123.007 | 61.8157 | -123.393
1085.2656 | 123.1476 | -66.5405 | 56.488 | 0.057412 | -0.084317 | -0.010716 | 0.046755 | -0.01702 | 0.053805 | 0.073406 | -0.0057807 | 0.0011204 | 0.04929 | 0.08416 | 0.051845 | -66.4268 | -2.5031 | -66.4438 | 56.4579 | 56.4173 | 56.5732 | -66.7047 | -66.4543 | -4.7111 | -66.5255 | 56.3542 | 56.5182 | 56.494 | -66.9004 | -0.1642 | -0.030171 | 0.11374 | 0.096689 | 0.26089 | -0.070749 | 0.085205 | -0.35988 | -0.13382 | 0.08618 | 0.015045 | 0.37493 | 0.030203 | 0.005933 | 122.9984 | 122.9578 | 123.1138 | 64.0374 | -123.1928 | 122.8947 | 123.0588 | 123.0345 | 61.8294 | -123.3884
1086.2656 | 123.1476 | -66.5176 | 56.4651 | 0.04215 | -0.082181 | -0.010716 | 0.047824 | -0.018088 | 0.052737 | 0.058145 | -0.0079177 | 0.0011204 | 0.050358 | 0.08416 | 0.049709 | -66.4268 | -2.4939 | -66.4438 | 56.4579 | 56.4127 | 56.5641 | -66.7047 | -66.4543 | -4.702 | -66.5209 | 56.3496 | 56.5137 | 56.4848 | -66.8958 | -0.18709 | -0.007283 | 0.090857 | 0.073801 | 0.26089 | -0.05244 | 0.098936 | -0.37819 | -0.11551 | 0.063292 | -0.003264 | 0.37493 | 0.048513 | 0.019664 | 122.9755 | 122.9303 | 123.0817 | 64.0237 | -123.1699 | 122.8673 | 123.0313 | 123.0025 | 61.8157 | -123.361
1087.2656 | 123.2025 | -66.5176 | 56.4789 | 0.04215 | -0.082181 | -0.010716 | 0.046755 | -0.018088 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.04929 | 0.08416 | 0.050777 | -66.4222 | -2.4939 | -66.4347 | 56.4579 | 56.4081 | 56.5641 | -66.7047 | -66.4498 | -4.6928 | -66.5255 | 56.3496 | 56.5228 | 56.4848 | -66.905 | -0.18709 | -0.021016 | 0.095435 | 0.082957 | 0.27004 | -0.070752 | 0.085203 | -0.38735 | -0.12925 | 0.06787 | -0.007843 | 0.37951 | 0.043937 | 0.005931 | 122.9755 | 122.9258 | 123.0817 | 64.0237 | -123.1836 | 122.8673 | 123.0405 | 123.0025 | 61.8248 | -123.3839
1088.2656 | 123.1476 | -66.5131 | 56.5018 | 0.04215 | -0.083249 | -0.010716 | 0.046755 | -0.018088 | 0.055941 | 0.088667 | -0.0079177 | 0.0021894 | 0.048222 | 0.08416 | 0.052914 | -66.4314 | -2.5077 | -66.4393 | 56.4579 | 56.4036 | 56.5641 | -66.7047 | -66.4543 | -4.6928 | -66.5255 | 56.3542 | 56.5182 | 56.4848 | -66.905 | -0.19166 | -0.043904 | 0.081702 | 0.073802 | 0.26546 | -0.098219 | 0.062315 | -0.39193 | -0.14756 | 0.058715 | -0.01242 | 0.37951 | 0.01647 | -0.016957 | 122.9709 | 122.9166 | 123.0771 | 64.0054 | -123.2065 | 122.8673 | 123.0313 | 122.9979 | 61.8202 | -123.4068
1089.2656 | 123.1522 | -66.5176 | 56.4926 | 0.057412 | -0.082181 | -0.011784 | 0.048892 | -0.018088 | 0.055941 | 0.042884 | -0.0068487 | 0.0011204 | 0.050358 | 0.08416 | 0.050777 | -66.4314 | -2.5031 | -66.4393 | 56.4624 | 56.4081 | 56.5641 | -66.7093 | -66.4452 | -4.6928 | -66.5255 | 56.3496 | 56.5091 | 56.4802 | -66.9096 | -0.19167 | -0.03017 | 0.086279 | 0.078379 | 0.27004 | -0.084485 | 0.07147 | -0.39193 | -0.14298 | 0.072449 | -0.007843 | 0.38408 | 0.016468 | -0.012381 | 122.9801 | 122.9258 | 123.0817 | 64.0145 | -123.2019 | 122.8673 | 123.0267 | 122.9979 | 61.8248 | -123.4022
1090.2656 | 123.1476 | -66.5176 | 56.488 | 0.04215 | -0.083249 | -0.0096467 | 0.046755 | -0.01702 | 0.053805 | 0.073406 | -0.0068487 | 5.2373e-05 | 0.04929 | 0.083092 | 0.050777 | -66.4268 | -2.5031 | -66.4438 | 56.467 | 56.4081 | 56.5687 | -66.7001 | -66.4589 | -4.6928 | -66.5255 | 56.3542 | 56.5182 | 56.4802 | -66.905 | -0.18251 | -0.021014 | 0.090857 | 0.073801 | 0.25631 | -0.079907 | 0.080626 | -0.38735 | -0.13382 | 0.058713 | -0.007843 | 0.37951 | 0.030203 | -0.007803 | 122.9847 | 122.9258 | 123.0863 | 64.0145 | -123.1882 | 122.8719 | 123.0359 | 122.9979 | 61.8248 | -123.393
1091.2656 | 123.111 | -66.5222 | 56.4926 | 0.026888 | -0.085386 | -0.011784 | 0.047824 | -0.018088 | 0.055941 | 0.042884 | -0.0047127 | 0.0032574 | 0.04929 | 0.086297 | 0.051845 | -66.4314 | -2.5031 | -66.4484 | 56.4533 | 56.4081 | 56.5641 | -66.7001 | -66.4543 | -4.6791 | -66.5209 | 56.3496 | 56.5274 | 56.4848 | -66.9004 | -0.17793 | -0.039327 | 0.090857 | 0.0738 | 0.25173 | -0.084485 | 0.07147 | -0.37819 | -0.14298 | 0.06787 | 0.001314 | 0.37951 | 0.034782 | -0.007802 | 122.9755 | 122.9303 | 123.0863 | 64.0191 | -123.1928 | 122.8719 | 123.0496 | 123.007 | 61.8431 | -123.393
1092.2656 | 123.1522 | -66.5131 | 56.5063 | 0.04215 | -0.083249 | -0.011784 | 0.047824 | -0.01702 | 0.055941 | 0.058145 | -0.0068487 | 0.0021894 | 0.050358 | 0.085228 | 0.050777 | -66.4268 | -2.5122 | -66.4438 | 56.4579 | 56.399 | 56.5595 | -66.7047 | -66.4589 | -4.6882 | -66.5255 | 56.3542 | 56.5045 | 56.4802 | -66.9004 | -0.19166 | -0.048482 | 0.08628 | 0.069224 | 0.26089 | -0.10738 | 0.053158 | -0.38735 | -0.15213 | 0.054136 | -0.01242 | 0.37493 | -0.001844 | -0.026114 | 122.9709 | 122.912 | 123.0726 | 64.0008 | -123.2111 | 122.8673 | 123.0176 | 122.9933 | 61.8248 | -123.4068
1093.2656 | 123.2162 | -66.4902 | 56.4835 | 0.057412 | -0.082181 | -0.011784 | 0.045687 | -0.019157 | 0.053805 | 0.073406 | -0.0057807 | 0.0053944 | 0.051427 | 0.086297 | 0.050777 | -66.4314 | -2.5077 | -66.4393 | 56.4487 | 56.3669 | 56.5595 | -66.7001 | -66.4589 | -4.6791 | -66.5301 | 56.3496 | 56.5137 | 56.4802 | -66.9141 | -0.20997 | -0.03475 | 0.058813 | 0.050913 | 0.26089 | -0.11654 | 0.076047 | -0.42397 | -0.13382 | 0.031247 | -0.039888 | 0.38408 | 0.030203 | -0.003225 | 122.9389 | 122.8571 | 123.0497 | 63.9825 | -123.1836 | 122.8398 | 123.0038 | 122.9704 | 61.8111 | -123.3976
1094.2656 | 123.2346 | -66.4719 | 56.4468 | 0.057412 | -0.083249 | -0.012852 | 0.047824 | -0.018088 | 0.054873 | 0.058145 | -0.0057807 | 0.0043254 | 0.050358 | 0.082023 | 0.050777 | -66.4359 | -2.5077 | -66.4484 | 56.4487 | 56.3486 | 56.5549 | -66.7047 | -66.4543 | -4.6745 | -66.5255 | 56.3496 | 56.5228 | 56.4848 | -66.905 | -0.23286 | 0.001871 | 0.035924 | 0.023446 | 0.25631 | -0.098234 | 0.10809 | -0.43313 | -0.097203 | 0.017516 | -0.053619 | 0.37951 | 0.075981 | 0.037975 | 122.9206 | 122.8205 | 123.0268 | 63.9642 | -123.1516 | 122.8215 | 122.9947 | 122.9567 | 61.7974 | -123.3518
1095.2656 | 123.1155 | -66.5176 | 56.488 | 0.04215 | -0.082181 | -0.010716 | 0.047824 | -0.018088 | 0.055941 | 0.088667 | -0.0057807 | 0.0021894 | 0.048222 | 0.085228 | 0.051845 | -66.4314 | -2.5077 | -66.4438 | 56.4441 | 56.3532 | 56.5458 | -66.7001 | -66.4589 | -4.6699 | -66.5255 | 56.3542 | 56.5182 | 56.4802 | -66.905 | -0.18251 | -0.043906 | 0.086279 | 0.073801 | 0.25631 | -0.13485 | 0.057733 | -0.38735 | -0.13382 | 0.058713 | -0.007843 | 0.37951 | 0.030203 | -0.007803 | 122.9618 | 122.8708 | 123.0634 | 64.01 | -123.1882 | 122.8719 | 123.0359 | 122.9979 | 61.8477 | -123.393
1096.2656 | 123.1476 | -66.5222 | 56.4926 | 0.04215 | -0.083249 | -0.012852 | 0.047824 | -0.020225 | 0.055941 | 0.073406 | -0.0057807 | 0.0021894 | 0.050358 | 0.085228 | 0.051845 | -66.4359 | -2.5077 | -66.4484 | 56.4533 | 56.3578 | 56.5549 | -66.7001 | -66.4543 | -4.6699 | -66.5209 | 56.3496 | 56.5137 | 56.4802 | -66.9096 | -0.17793 | -0.039327 | 0.086278 | 0.0738 | 0.25173 | -0.13485 | 0.062313 | -0.38735 | -0.14298 | 0.06787 | 0.001314 | 0.38866 | 0.021047 | -0.012381 | 122.9755 | 122.88 | 123.0771 | 64.0145 | -123.1928 | 122.8719 | 123.0359 | 123.0025 | 61.8523 | -123.4022
1097.2656 | 123.1705 | -66.5268 | 56.4972 | 0.026888 | -0.084317 | -0.011784 | 0.048892 | -0.019157 | 0.054873 | 0.073406 | -0.0047127 | 0.0021894 | 0.051427 | 0.085228 | 0.051845 | -66.4359 | -2.4985 | -66.4484 | 56.4487 | 56.3532 | 56.5595 | -66.7047 | -66.4589 | -4.6653 | -66.5301 | 56.3542 | 56.5182 | 56.4757 | -66.9004 | -0.17793 | -0.048483 | 0.090855 | 0.078377 | 0.25631 | -0.14401 | 0.062314 | -0.37362 | -0.14298 | 0.067868 | -0.003267 | 0.37035 | 0.021048 | -0.021536 | 122.9755 | 122.88 | 123.0863 | 64.0283 | -123.2019 | 122.881 | 123.045 | 123.0024 | 61.8614 | -123.3976
1098.2656 | 123.1384 | -66.5085 | 56.488 | 0.04215 | -0.084317 | -0.011784 | 0.047824 | -0.019157 | 0.053805 | 0.042884 | -0.0068487 | 0.0032574 | 0.048222 | 0.085228 | 0.050777 | -66.4268 | -2.5031 | -66.4393 | 56.4487 | 56.3898 | 56.5549 | -66.7047 | -66.4589 | -4.6653 | -66.5346 | 56.3496 | 56.5182 | 56.4848 | -66.9004 | -0.19624 | -0.039328 | 0.081702 | 0.069224 | 0.26546 | -0.098222 | 0.066891 | -0.39193 | -0.1384 | 0.049558 | -0.026155 | 0.36577 | 0.030203 | -0.003224 | 122.9572 | 122.8983 | 123.0634 | 64.0054 | -123.1928 | 122.8581 | 123.0267 | 122.9933 | 61.8431 | -123.3884
1099.2656 | 123.2346 | -66.4856 | 56.4743 | 0.057412 | -0.083249 | -0.011784 | 0.047824 | -0.020225 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.04929 | 0.08416 | 0.049709 | -66.4314 | -2.5031 | -66.4438 | 56.4487 | 56.3944 | 56.5549 | -66.7047 | -66.4589 | -4.6608 | -66.5301 | 56.3496 | 56.5091 | 56.4848 | -66.9004 | -0.21913 | -0.025595 | 0.054236 | 0.041758 | 0.26089 | -0.07991 | 0.080624 | -0.41481 | -0.12467 | 0.02667 | -0.044465 | 0.37035 | 0.034779 | 0.010509 | 122.9343 | 122.88 | 123.0405 | 63.9825 | -123.179 | 122.8352 | 122.9947 | 122.9704 | 61.8248 | -123.3747
1100.2656 | 123.262 | -66.4902 | 56.4514 | 0.026888 | -0.082181 | -0.012852 | 0.047824 | -0.018088 | 0.054873 | 0.058145 | -0.0047127 | 0.0011204 | 0.051427 | 0.08416 | 0.052914 | -66.4314 | -2.5031 | -66.4438 | 56.4487 | 56.4081 | 56.5595 | -66.7093 | -66.4635 | -4.6608 | -66.5346 | 56.3496 | 56.5137 | 56.4757 | -66.905 | -0.21913 | -0.002707 | 0.058813 | 0.046335 | 0.26547 | -0.043286 | 0.10809 | -0.41482 | -0.10178 | 0.026668 | -0.044466 | 0.37035 | 0.062246 | 0.02424 | 122.9389 | 122.8983 | 123.0497 | 63.9871 | -123.1607 | 122.8398 | 123.0038 | 122.9658 | 61.8294 | -123.3564
1101.2656 | 123.2849 | -66.4719 | 56.4377 | 0.026888 | -0.082181 | -0.011784 | 0.046755 | -0.020225 | 0.054873 | 0.058145 | -0.0068487 | 0.0032574 | 0.050358 | 0.087365 | 0.052914 | -66.4314 | -2.5077 | -66.4484 | 56.4579 | 56.3944 | 56.5641 | -66.7093 | -66.4589 | -4.6562 | -66.5301 | 56.3496 | 56.5091 | 56.494 | -66.9004 | -0.23744 | 0.020183 | 0.040503 | 0.023446 | 0.26089 | -0.043289 | 0.1264 | -0.42855 | -0.088048 | 0.012937 | -0.058198 | 0.37035 | 0.0714 | 0.056287 | 122.9297 | 122.8663 | 123.0359 | 63.9642 | -123.147 | 122.8215 | 122.9809 | 122.9658 | 61.8157 | -123.3381
1102.2656 | 123.2162 | -66.5039 | 56.4789 | 0.057412 | -0.083249 | -0.012852 | 0.046755 | -0.019157 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.04929 | 0.086297 | 0.050777 | -66.4314 | -2.5077 | -66.4576 | 56.4579 | 56.4173 | 56.5595 | -66.7093 | -66.4589 | -4.647 | -66.5346 | 56.3542 | 56.5137 | 56.4802 | -66.905 | -0.2054 | -0.021016 | 0.072546 | 0.046333 | 0.25173 | -0.061594 | 0.080624 | -0.40108 | -0.12467 | 0.04498 | -0.030733 | 0.37035 | 0.03478 | 0.001352 | 122.9618 | 122.9212 | 123.0634 | 63.9962 | -123.1882 | 122.8581 | 123.0176 | 122.9841 | 61.8569 | -123.3839
1103.2656 | 123.2254 | -66.4856 | 56.4423 | 0.04215 | -0.084317 | -0.011784 | 0.047824 | -0.019157 | 0.054873 | 0.073406 | -0.0057807 | 0.0032574 | 0.051427 | 0.086297 | 0.050777 | -66.4405 | -2.4985 | -66.4393 | 56.4579 | 56.4081 | 56.5641 | -66.7139 | -66.4635 | -4.6425 | -66.5301 | 56.3496 | 56.5182 | 56.4802 | -66.9096 | -0.22829 | 0.015605 | 0.045079 | 0.046336 | 0.27462 | -0.034131 | 0.12182 | -0.42397 | -0.092626 | 0.022091 | -0.044465 | 0.37951 | 0.075979 | 0.037973 | 122.9435 | 122.8937 | 123.0497 | 63.9871 | -123.1561 | 122.8352 | 123.0038 | 122.9658 | 61.8431 | -123.3518
1104.2656 | 123.23 | -66.4902 | 56.456 | 0.04215 | -0.084317 | -0.011784 | 0.047824 | -0.018088 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.050358 | 0.088434 | 0.050777 | -66.4451 | -2.5031 | -66.4438 | 56.4579 | 56.4081 | 56.5641 | -66.7093 | -66.4635 | -4.647 | -66.5346 | 56.3542 | 56.5091 | 56.4848 | -66.9004 | -0.21913 | 0.001872 | 0.045078 | 0.046335 | 0.26547 | -0.047864 | 0.10809 | -0.41024 | -0.10178 | 0.026668 | -0.044466 | 0.36577 | 0.053089 | 0.028819 | 122.948 | 122.8983 | 123.0543 | 63.9871 | -123.1653 | 122.8444 | 122.9993 | 122.975 | 61.8431 | -123.3564
1105.2656 | 123.262 | -66.4764 | 56.4468 | 0.04215 | -0.082181 | -0.011784 | 0.047824 | -0.01702 | 0.05701 | 0.073406 | -0.0068487 | 0.0032574 | 0.04929 | 0.086297 | 0.052914 | -66.4359 | -2.5077 | -66.453 | 56.4624 | 56.4036 | 56.5641 | -66.7139 | -66.4635 | -4.6333 | -66.5301 | 56.3496 | 56.5182 | 56.4757 | -66.9141 | -0.23744 | 0.015607 | 0.040501 | 0.023445 | 0.26089 | -0.043287 | 0.11725 | -0.43771 | -0.097203 | 0.012935 | -0.053621 | 0.38408 | 0.071402 | 0.028818 | 122.9389 | 122.88 | 123.0405 | 63.9688 | -123.1607 | 122.8261 | 122.9947 | 122.9521 | 61.8431 | -123.361
1106.2656 | 123.2758 | -66.4856 | 56.4377 | 0.057412 | -0.084317 | -0.010716 | 0.047824 | -0.019157 | 0.054873 | 0.042884 | -0.0068487 | 0.0021894 | 0.050358 | 0.085228 | 0.050777 | -66.4359 | -2.5168 | -66.453 | 56.4533 | 56.4036 | 56.5595 | -66.7093 | -66.4589 | -4.6333 | -66.5301 | 56.3496 | 56.5182 | 56.4802 | -66.9096 | -0.22371 | 0.015605 | 0.049657 | 0.032601 | 0.25631 | -0.034132 | 0.12182 | -0.42397 | -0.088048 | 0.02667 | -0.044465 | 0.37951 | 0.080557 | 0.042551 | 122.9389 | 122.8891 | 123.0451 | 63.9688 | -123.147 | 122.8352 | 123.0038 | 122.9658 | 61.8523 | -123.3473
1107.2656 | 123.2071 | -66.4856 | 56.4606 | 0.057412 | -0.082181 | -0.011784 | 0.045687 | -0.019157 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.050358 | 0.085228 | 0.049709 | -66.4314 | -2.5214 | -66.4576 | 56.4533 | 56.4036 | 56.5641 | -66.7139 | -66.4681 | -4.6241 | -66.5301 | 56.3451 | 56.5137 | 56.4757 | -66.9096 | -0.22829 | -0.007283 | 0.054236 | 0.028023 | 0.25631 | -0.05702 | 0.10351 | -0.42397 | -0.11551 | 0.017513 | -0.044465 | 0.37951 | 0.053091 | 0.015085 | 122.9389 | 122.8891 | 123.0497 | 63.9642 | -123.1745 | 122.8307 | 122.9993 | 122.9613 | 61.8615 | -123.3701
1108.2656 | 123.317 | -66.4856 | 56.4331 | 0.026888 | -0.083249 | -0.011784 | 0.046755 | -0.018088 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.050358 | 0.086297 | 0.049709 | -66.4451 | -2.526 | -66.4622 | 56.4533 | 56.4036 | 56.5549 | -66.7093 | -66.4589 | -4.6287 | -66.5346 | 56.3451 | 56.5228 | 56.4802 | -66.905 | -0.22371 | 0.020183 | 0.040501 | 0.023445 | 0.24715 | -0.029554 | 0.12182 | -0.41939 | -0.088048 | 0.02667 | -0.049043 | 0.37035 | 0.089714 | 0.047129 | 122.9389 | 122.8891 | 123.0405 | 63.9596 | -123.1424 | 122.8307 | 123.0084 | 122.9658 | 61.8569 | -123.3381
1109.2656 | 123.2758 | -66.4764 | 56.4423 | 0.072674 | -0.086454 | -0.012852 | 0.046755 | -0.020225 | 0.054873 | 0.088667 | -0.0079177 | 0.0021894 | 0.050358 | 0.087365 | 0.050777 | -66.4359 | -2.5306 | -66.453 | 56.4533 | 56.4036 | 56.5549 | -66.7139 | -66.4681 | -4.6287 | -66.5301 | 56.3451 | 56.5182 | 56.494 | -66.905 | -0.23744 | 0.011027 | 0.040501 | 0.023445 | 0.26089 | -0.03871 | 0.11267 | -0.42855 | -0.097204 | 0.008357 | -0.053621 | 0.37493 | 0.075979 | 0.051709 | 122.9297 | 122.88 | 123.0314 | 63.9459 | -123.1561 | 122.8215 | 122.9947 | 122.9704 | 61.8477 | -123.3472
1110.2656 | 123.2803 | -66.4581 | 56.4514 | 0.057412 | -0.083249 | -0.011784 | 0.047824 | -0.021293 | 0.054873 | 0.058145 | -0.0057807 | 0.0032574 | 0.051427 | 0.087365 | 0.051845 | -66.4359 | -2.5397 | -66.453 | 56.4579 | 56.4081 | 56.5595 | -66.7139 | -66.4635 | -4.6241 | -66.5346 | 56.3496 | 56.5091 | 56.4848 | -66.9187 | -0.25575 | 0.00645 | 0.022191 | 0.005135 | 0.26089 | -0.043286 | 0.10809 | -0.46059 | -0.10178 | -0.005375 | -0.076509 | 0.38409 | 0.057667 | 0.033397 | 122.916 | 122.8663 | 123.0176 | 63.9184 | -123.1653 | 122.8078 | 122.9672 | 122.9429 | 61.834 | -123.3701
1111.2656 | 123.2803 | -66.4673 | 56.4468 | 0.04215 | -0.084317 | -0.011784 | 0.048892 | -0.019157 | 0.054873 | 0.027623 | -0.0057807 | 0.0032574 | 0.050358 | 0.085228 | 0.051845 | -66.4359 | -2.5489 | -66.4622 | 56.4441 | 56.4081 | 56.5549 | -66.7139 | -66.4635 | -4.6196 | -66.5346 | 56.3496 | 56.5182 | 56.4848 | -66.9141 | -0.2466 | -0.002707 | 0.031346 | 0.005134 | 0.25173 | -0.038708 | 0.10809 | -0.44686 | -0.097203 | 0.00378 | -0.067354 | 0.37951 | 0.071402 | 0.037975 | 122.9114 | 122.8754 | 123.0222 | 63.9184 | -123.1607 | 122.8169 | 122.9855 | 122.9521 | 61.8477 | -123.361
1112.2656 | 123.262 | -66.4948 | 56.4468 | 0.072674 | -0.083249 | -0.011784 | 0.048892 | -0.018088 | 0.054873 | 0.073406 | -0.0068487 | 5.2373e-05 | 0.050358 | 0.085228 | 0.053982 | -66.4405 | -2.558 | -66.4576 | 56.4533 | 56.4081 | 56.5595 | -66.7093 | -66.4727 | -4.6241 | -66.5301 | 56.3496 | 56.5137 | 56.4802 | -66.905 | -0.21455 | 0.00645 | 0.054234 | 0.037178 | 0.25173 | -0.038708 | 0.11267 | -0.41024 | -0.097203 | 0.022089 | -0.03531 | 0.37493 | 0.066824 | 0.033396 | 122.948 | 122.9029 | 123.0543 | 63.9367 | -123.1561 | 122.8444 | 123.0084 | 122.975 | 61.8706 | -123.3518
1113.2656 | 123.2483 | -66.5039 | 56.4377 | 0.072674 | -0.085386 | -0.010716 | 0.046755 | -0.018088 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.048222 | 0.086297 | 0.050777 | -66.4405 | -2.5535 | -66.4622 | 56.4533 | 56.399 | 56.5549 | -66.7093 | -66.4727 | -4.615 | -66.5301 | 56.3496 | 56.5045 | 56.4757 | -66.9141 | -0.2054 | 0.015605 | 0.063389 | 0.041755 | 0.24715 | -0.03871 | 0.11724 | -0.41024 | -0.088048 | 0.031244 | -0.026155 | 0.38408 | 0.066821 | 0.037973 | 122.9572 | 122.9029 | 123.0588 | 63.9505 | -123.147 | 122.8535 | 123.0084 | 122.9796 | 61.8889 | -123.3518
1114.2656 | 123.2254 | -66.4948 | 56.4651 | 0.026888 | -0.085386 | -0.011784 | 0.046755 | -0.015952 | 0.053805 | 0.058145 | -0.0068487 | 0.0011204 | 0.048222 | 0.086297 | 0.050777 | -66.4405 | -2.5535 | -66.4622 | 56.4487 | 56.4081 | 56.5595 | -66.7093 | -66.4635 | -4.615 | -66.5346 | 56.3451 | 56.5137 | 56.4848 | -66.9141 | -0.21455 | -0.01644 | 0.054234 | 0.0326 | 0.24715 | -0.057019 | 0.094357 | -0.4194 | -0.12009 | 0.031246 | -0.039888 | 0.37951 | 0.048513 | 0.019664 | 122.9435 | 122.9029 | 123.0543 | 63.9413 | -123.1745 | 122.8398 | 123.0084 | 122.9796 | 61.8798 | -123.3793
1115.2656 | 123.2483 | -66.4764 | 56.4377 | 0.04215 | -0.086454 | -0.011784 | 0.047824 | -0.019157 | 0.055941 | 0.058145 | -0.0047127 | 0.0011204 | 0.050358 | 0.086297 | 0.049709 | -66.4497 | -2.5626 | -66.4622 | 56.4533 | 56.4036 | 56.5503 | -66.7185 | -66.4681 | -4.6104 | -66.5392 | 56.3496 | 56.5137 | 56.4802 | -66.9096 | -0.24202 | 0.015605 | 0.026766 | 0.014289 | 0.25631 | -0.034132 | 0.11267 | -0.43313 | -0.088048 | 0.008357 | -0.062778 | 0.37035 | 0.075979 | 0.042551 | 122.9297 | 122.88 | 123.0268 | 63.9138 | -123.1561 | 122.8261 | 122.9901 | 122.9567 | 61.866 | -123.3473
1116.2656 | 123.2071 | -66.4856 | 56.4468 | 0.026888 | -0.084317 | -0.012852 | 0.047824 | -0.019157 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.048222 | 0.085228 | 0.050777 | -66.4451 | -2.5535 | -66.4576 | 56.4533 | 56.4036 | 56.5595 | -66.7185 | -66.4681 | -4.615 | -66.5392 | 56.3451 | 56.5091 | 56.4802 | -66.9187 | -0.23287 | 0.00645 | 0.040501 | 0.028023 | 0.26089 | -0.043287 | 0.11267 | -0.43313 | -0.10178 | 0.017513 | -0.053622 | 0.37951 | 0.062245 | 0.033396 | 122.9389 | 122.8891 | 123.0451 | 63.9321 | -123.1653 | 122.8307 | 122.9947 | 122.9658 | 61.8706 | -123.3656
1117.2656 | 123.1384 | -66.5314 | 56.4926 | 0.026888 | -0.085386 | -0.011784 | 0.045687 | -0.018088 | 0.052737 | 0.058145 | -0.0079177 | 0.0032574 | 0.048222 | 0.086297 | 0.051845 | -66.4451 | -2.5626 | -66.4622 | 56.4487 | 56.4081 | 56.5595 | -66.7139 | -66.4681 | -4.6104 | -66.5301 | 56.3451 | 56.5228 | 56.4757 | -66.9187 | -0.18251 | -0.043906 | 0.086277 | 0.069221 | 0.25173 | -0.084485 | 0.066891 | -0.38735 | -0.14756 | 0.063289 | 0.001311 | 0.38866 | 0.030204 | -0.016959 | 122.9801 | 122.9395 | 123.0909 | 63.9688 | -123.2065 | 122.8764 | 123.0542 | 123.007 | 61.921 | -123.4113
1118.2656 | 123.262 | -66.4948 | 56.4423 | 0.011626 | -0.085386 | -0.012852 | 0.044618 | -0.018088 | 0.053805 | 0.027623 | -0.0068487 | 0.0011204 | 0.048222 | 0.086297 | 0.049709 | -66.4359 | -2.5672 | -66.4576 | 56.4396 | 56.4036 | 56.5595 | -66.7139 | -66.4727 | -4.6058 | -66.5438 | 56.3451 | 56.5137 | 56.4802 | -66.9187 | -0.21913 | -0.002708 | 0.058812 | 0.037178 | 0.25631 | -0.03871 | 0.11724 | -0.42397 | -0.097204 | 0.022089 | -0.049046 | 0.37493 | 0.071401 | 0.037973 | 122.9343 | 122.8983 | 123.0543 | 63.9276 | -123.1561 | 122.8398 | 123.0084 | 122.975 | 61.8889 | -123.361
1119.2656 | 123.2254 | -66.5039 | 56.456 | 0.026888 | -0.085386 | -0.011784 | 0.047824 | -0.019157 | 0.053805 | 0.058145 | -0.0079177 | 0.0021894 | 0.050358 | 0.087365 | 0.050777 | -66.4497 | -2.5626 | -66.4667 | 56.4441 | 56.3944 | 56.5549 | -66.7093 | -66.4681 | -4.5967 | -66.5438 | 56.3451 | 56.5182 | 56.4757 | -66.9141 | -0.2054 | -0.011863 | 0.054232 | 0.037176 | 0.24257 | -0.0616 | 0.098934 | -0.41024 | -0.11094 | 0.035823 | -0.039891 | 0.37035 | 0.062246 | 0.019662 | 122.948 | 122.8983 | 123.0588 | 63.9413 | -123.1653 | 122.849 | 123.0221 | 122.9796 | 61.9072 | -123.3701
1120.2656 | 123.1934 | -66.5039 | 56.4102 | 0.04215 | -0.084317 | -0.011784 | 0.048892 | -0.020225 | 0.055941 | 0.027623 | -0.0057807 | 0.0021894 | 0.050358 | 0.089502 | 0.051845 | -66.4451 | -2.5626 | -66.4667 | 56.4487 | 56.4036 | 56.5549 | -66.7093 | -66.4772 | -4.5967 | -66.5346 | 56.3496 | 56.5137 | 56.4802 | -66.9141 | -0.2054 | 0.038492 | 0.058811 | 0.037176 | 0.24257 | -0.006666 | 0.14471 | -0.41024 | -0.060582 | 0.026665 | -0.030733 | 0.37951 | 0.10344 | 0.070017 | 122.9526 | 122.9075 | 123.0588 | 63.9413 | -123.1195 | 122.8535 | 123.0176 | 122.9841 | 61.9072 | -123.3244
1121.2656 | 123.2391 | -66.5222 | 56.4102 | 0.057412 | -0.086454 | -0.011784 | 0.047824 | -0.019157 | 0.053805 | 0.042884 | -0.0068487 | 0.0021894 | 0.048222 | 0.088434 | 0.048641 | -66.4497 | -2.5672 | -66.453 | 56.4441 | 56.3944 | 56.5503 | -66.7139 | -66.4818 | -4.5967 | -66.5484 | 56.3496 | 56.5045 | 56.4757 | -66.9141 | -0.19167 | 0.033914 | 0.072543 | 0.069222 | 0.26089 | -0.015823 | 0.14013 | -0.39193 | -0.060582 | 0.040398 | -0.026159 | 0.36577 | 0.094287 | 0.065439 | 122.9663 | 122.9166 | 123.0726 | 63.955 | -123.1241 | 122.8719 | 123.0267 | 122.9979 | 61.9256 | -123.3244
1122.2656 | 123.2666 | -66.4902 | 56.4606 | 0.072674 | -0.085386 | -0.011784 | 0.047824 | -0.018088 | 0.053805 | 0.042884 | -0.0057807 | 0.0021894 | 0.04929 | 0.087365 | 0.051845 | -66.4451 | -2.5626 | -66.4667 | 56.4487 | 56.4036 | 56.5503 | -66.7139 | -66.4727 | -4.5875 | -66.5484 | 56.3542 | 56.5182 | 56.4757 | -66.9141 | -0.22371 | -0.011862 | 0.045078 | 0.023443 | 0.24715 | -0.05702 | 0.089778 | -0.42397 | -0.10636 | 0.017511 | -0.058203 | 0.36577 | 0.057669 | 0.015085 | 122.9389 | 122.8937 | 123.0405 | 63.9276 | -123.1745 | 122.8444 | 123.0084 | 122.9658 | 61.9027 | -123.3747
1123.2656 | 123.2071 | -66.5314 | 56.4468 | 0.026888 | -0.085386 | -0.011784 | 0.046755 | -0.018088 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.048222 | 0.086297 | 0.050777 | -66.4497 | -2.5626 | -66.4622 | 56.4441 | 56.399 | 56.5549 | -66.7047 | -66.4772 | -4.5829 | -66.5392 | 56.3451 | 56.5137 | 56.4711 | -66.9141 | -0.17335 | -0.002707 | 0.081698 | 0.069221 | 0.24257 | -0.047865 | 0.10809 | -0.38277 | -0.10178 | 0.054131 | -0.007846 | 0.37493 | 0.066824 | 0.024239 | 122.9755 | 122.9303 | 123.0863 | 63.9688 | -123.1516 | 122.8764 | 123.045 | 123.0024 | 61.9484 | -123.361
1124.2656 | 123.2071 | -66.5268 | 56.4148 | 0.026888 | -0.085386 | -0.011784 | 0.046755 | -0.019157 | 0.053805 | 0.058145 | -0.0057807 | 0.0021894 | 0.04929 | 0.087365 | 0.050777 | -66.4497 | -2.5672 | -66.4713 | 56.4441 | 56.3944 | 56.5458 | -66.7139 | -66.4727 | -4.5784 | -66.5301 | 56.3451 | 56.5137 | 56.4711 | -66.9187 | -0.18709 | 0.029336 | 0.07712 | 0.055486 | 0.24258 | -0.020401 | 0.13097 | -0.39193 | -0.069738 | 0.054132 | -0.003267 | 0.38866 | 0.098867 | 0.056282 | 122.9709 | 122.9212 | 123.0726 | 63.9596 | -123.1287 | 122.8719 | 123.0405 | 122.9979 | 61.9484 | -123.3335
1125.2656 | 123.2208 | -66.5131 | 56.4194 | 0.026888 | -0.084317 | -0.010716 | 0.047824 | -0.019157 | 0.053805 | 0.042884 | -0.0068487 | 0.0032574 | 0.047154 | 0.088434 | 0.050777 | -66.4405 | -2.5626 | -66.4667 | 56.4441 | 56.344 | 56.5458 | -66.7093 | -66.4681 | -4.5829 | -66.5484 | 56.3451 | 56.4999 | 56.4665 | -66.9233 | -0.19624 | 0.024758 | 0.072545 | 0.046332 | 0.24257 | -0.075348 | 0.1264 | -0.41024 | -0.074316 | 0.044979 | -0.035314 | 0.37493 | 0.080553 | 0.047125 | 122.9572 | 122.8571 | 123.0588 | 63.9505 | -123.1287 | 122.8581 | 123.013 | 122.9796 | 61.9301 | -123.3427
1126.2656 | 123.2849 | -66.5131 | 56.4377 | 0.057412 | -0.085386 | -0.010716 | 0.046755 | -0.01702 | 0.05701 | 0.073406 | -0.0068487 | 5.2373e-05 | 0.04929 | 0.087365 | 0.050777 | -66.4451 | -2.5718 | -66.4667 | 56.4441 | 56.3623 | 56.5503 | -66.7139 | -66.4727 | -4.5784 | -66.5484 | 56.3405 | 56.5091 | 56.4711 | -66.9233 | -0.20082 | 0.006448 | 0.067967 | 0.046332 | 0.24715 | -0.075342 | 0.11267 | -0.41024 | -0.097205 | 0.0404 | -0.035314 | 0.37493 | 0.0714 | 0.033394 | 122.9572 | 122.8754 | 123.0634 | 63.9413 | -123.1516 | 122.8535 | 123.0221 | 122.9841 | 61.9347 | -123.361
1127.2656 | 123.143 | -66.5359 | 56.5109 | 0.026888 | -0.085386 | -0.013921 | 0.047824 | -0.019157 | 0.052737 | 0.058145 | -0.0057807 | 0.0021894 | 0.050358 | 0.086297 | 0.050777 | -66.4543 | -2.5763 | -66.4713 | 56.4487 | 56.3669 | 56.5549 | -66.7093 | -66.4818 | -4.5829 | -66.5484 | 56.3405 | 56.5137 | 56.4665 | -66.9187 | -0.17335 | -0.062216 | 0.081698 | 0.064642 | 0.238 | -0.144 | 0.044003 | -0.38277 | -0.17045 | 0.054131 | -0.012426 | 0.37035 | 0.002737 | -0.044427 | 122.9847 | 122.9029 | 123.0909 | 63.9596 | -123.2202 | 122.8764 | 123.0496 | 123.0024 | 61.953 | -123.4296
1128.2656 | 123.2483 | -66.5039 | 56.4239 | 0.011626 | -0.085386 | -0.012852 | 0.046755 | -0.01702 | 0.055941 | 0.042884 | -0.0068487 | 0.0021894 | 0.04929 | 0.087365 | 0.050777 | -66.4497 | -2.5718 | -66.4713 | 56.4441 | 56.3852 | 56.5549 | -66.7139 | -66.4727 | -4.5692 | -66.5438 | 56.3405 | 56.5182 | 56.4757 | -66.9187 | -0.20998 | 0.020181 | 0.054232 | 0.032598 | 0.24258 | -0.038714 | 0.13098 | -0.41482 | -0.083472 | 0.031244 | -0.039891 | 0.37493 | 0.09429 | 0.051706 | 122.948 | 122.8891 | 123.0588 | 63.9321 | -123.1378 | 122.8444 | 123.0221 | 122.9796 | 61.9347 | -123.3427
1129.2656 | 123.262 | -66.4902 | 56.4194 | 0.04215 | -0.085386 | -0.012852 | 0.045687 | -0.019157 | 0.054873 | 0.042884 | -0.0057807 | 0.0021894 | 0.048222 | 0.087365 | 0.049709 | -66.4451 | -2.5855 | -66.4667 | 56.4441 | 56.3944 | 56.5458 | -66.7139 | -66.4772 | -4.5738 | -66.5484 | 56.3405 | 56.5091 | 56.4711 | -66.9096 | -0.22371 | 0.024758 | 0.045078 | 0.023443 | 0.24715 | -0.024979 | 0.1264 | -0.41939 | -0.078895 | 0.012932 | -0.058203 | 0.36119 | 0.08971 | 0.051704 | 122.9343 | 122.8846 | 123.0359 | 63.9047 | -123.1333 | 122.8307 | 122.9993 | 122.9613 | 61.9164 | -123.3289
1130.2656 | 123.3032 | -66.5131 | 56.3965 | 0.026888 | -0.084317 | -0.012852 | 0.048892 | -0.018088 | 0.053805 | 0.042884 | -0.0068487 | 0.0032574 | 0.04929 | 0.086297 | 0.050777 | -66.4497 | -2.5809 | -66.4713 | 56.4441 | 56.3761 | 56.5503 | -66.7185 | -66.4727 | -4.5646 | -66.5438 | 56.3405 | 56.5091 | 56.4757 | -66.9279 | -0.2054 | 0.047647 | 0.063388 | 0.041754 | 0.24715 | -0.020406 | 0.15386 | -0.41482 | -0.056006 | 0.0404 | -0.030735 | 0.38408 | 0.1126 | 0.079172 | 122.9572 | 122.8891 | 123.0634 | 63.9321 | -123.1149 | 122.8535 | 123.0221 | 122.9887 | 61.9484 | -123.3244
1131.2656 | 123.2391 | -66.5222 | 56.3965 | 0.026888 | -0.085386 | -0.011784 | 0.048892 | -0.01702 | 0.05701 | 0.042884 | -0.0068487 | 0.0021894 | 0.050358 | 0.087365 | 0.050777 | -66.4497 | -2.5947 | -66.4713 | 56.4396 | 56.3669 | 56.5503 | -66.7139 | -66.4727 | -4.5555 | -66.5438 | 56.3451 | 56.5137 | 56.4619 | -66.9187 | -0.19167 | 0.043069 | 0.072543 | 0.050909 | 0.24258 | -0.029564 | 0.15386 | -0.39651 | -0.051427 | 0.049555 | -0.02158 | 0.37493 | 0.11718 | 0.065436 | 122.9618 | 122.8891 | 123.0726 | 63.9276 | -123.1104 | 122.8673 | 123.0359 | 122.9841 | 61.9668 | -123.3152
1132.2656 | 123.1247 | -66.5359 | 56.4789 | 0.04215 | -0.086454 | -0.012852 | 0.046755 | -0.020225 | 0.054873 | 0.042884 | -0.0089857 | 0.0021894 | 0.04929 | 0.086297 | 0.052914 | -66.4543 | -2.5901 | -66.4667 | 56.435 | 56.399 | 56.5503 | -66.723 | -66.4681 | -4.5509 | -66.5484 | 56.3405 | 56.5091 | 56.4711 | -66.9141 | -0.18709 | -0.043908 | 0.081698 | 0.06922 | 0.25631 | -0.079909 | 0.071467 | -0.3782 | -0.1384 | 0.067867 | -0.012426 | 0.36577 | 0.030201 | -0.007805 | 122.9709 | 122.9349 | 123.0863 | 63.9459 | -123.2019 | 122.8764 | 123.045 | 123.007 | 61.9851 | -123.393
1133.2656 | 123.2666 | -66.5222 | 56.4194 | 0.04215 | -0.085386 | -0.011784 | 0.046755 | -0.019157 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.048222 | 0.088434 | 0.049709 | -66.4451 | -2.5947 | -66.4713 | 56.4487 | 56.399 | 56.5458 | -66.7185 | -66.4818 | -4.5555 | -66.5438 | 56.3451 | 56.5137 | 56.4665 | -66.9141 | -0.19625 | 0.029336 | 0.077122 | 0.050909 | 0.24715 | -0.0204 | 0.1264 | -0.39193 | -0.074316 | 0.040398 | -0.02158 | 0.37035 | 0.094289 | 0.047125 | 122.9709 | 122.9212 | 123.068 | 63.9276 | -123.1378 | 122.8673 | 123.0359 | 122.9887 | 61.9668 | -123.3335
1134.2656 | 123.1705 | -66.5497 | 56.4331 | 0.011626 | -0.085386 | -0.010716 | 0.048892 | -0.01702 | 0.055941 | 0.073406 | -0.0068487 | 0.0021894 | 0.048222 | 0.087365 | 0.049709 | -66.4543 | -2.5992 | -66.4713 | 56.4441 | 56.399 | 56.5549 | -66.7093 | -66.4818 | -4.5463 | -66.5484 | 56.3496 | 56.5091 | 56.4802 | -66.9187 | -0.15962 | 0.011026 | 0.095431 | 0.078375 | 0.238 | -0.034132 | 0.12182 | -0.36904 | -0.08347 | 0.067864 | 0.001307 | 0.37035 | 0.075978 | 0.047129 | 122.9938 | 122.9487 | 123.1046 | 63.9504 | -123.1424 | 122.8993 | 123.0588 | 123.0299 | 62.0034 | -123.3518
1135.2656 | 123.1659 | -66.5451 | 56.4606 | 0.04215 | -0.085386 | -0.011784 | 0.046755 | -0.018088 | 0.054873 | 0.058145 | -0.0068487 | 0.0032574 | 0.04929 | 0.088434 | 0.051845 | -66.4451 | -2.5992 | -66.4667 | 56.4441 | 56.399 | 56.5503 | -66.7185 | -66.4818 | -4.5555 | -66.5484 | 56.3405 | 56.5091 | 56.4711 | -66.9187 | -0.17336 | -0.01644 | 0.10001 | 0.078375 | 0.25173 | -0.061598 | 0.089778 | -0.37362 | -0.12009 | 0.063286 | -0.003271 | 0.37035 | 0.048512 | 0.010506 | 122.9892 | 122.9441 | 123.0955 | 63.9459 | -123.179 | 122.8856 | 123.0542 | 123.0162 | 61.9896 | -123.3793
1136.2656 | 123.1796 | -66.5085 | 56.4377 | 0.04215 | -0.085386 | -0.012852 | 0.047824 | -0.018088 | 0.055941 | 0.042884 | -0.0068487 | 0.0011204 | 0.04929 | 0.086297 | 0.051845 | -66.4497 | -2.5992 | -66.4759 | 56.4533 | 56.3944 | 56.5549 | -66.723 | -66.4772 | -4.5509 | -66.553 | 56.3405 | 56.5091 | 56.4711 | -66.9187 | -0.21456 | 0.015605 | 0.05881 | 0.032598 | 0.24715 | -0.043289 | 0.11724 | -0.41024 | -0.097205 | 0.031243 | -0.04447 | 0.36577 | 0.0714 | 0.033394 | 122.9618 | 122.9029 | 123.0634 | 63.9092 | -123.1607 | 122.849 | 123.0176 | 122.9796 | 61.9576 | -123.3564
1137.2656 | 123.3124 | -66.5039 | 56.3965 | 0.04215 | -0.085386 | -0.012852 | 0.046755 | -0.019157 | 0.05701 | 0.088667 | -0.0068487 | 0.0021894 | 0.04929 | 0.086297 | 0.049709 | -66.4497 | -2.6038 | -66.4713 | 56.4396 | 56.399 | 56.5503 | -66.723 | -66.4727 | -4.5463 | -66.553 | 56.3451 | 56.5091 | 56.4757 | -66.9279 | -0.21913 | 0.043069 | 0.054232 | 0.032598 | 0.25173 | 0.002489 | 0.15386 | -0.42398 | -0.051427 | 0.031244 | -0.049048 | 0.37493 | 0.1126 | 0.079172 | 122.9435 | 122.9029 | 123.0543 | 63.9001 | -123.1195 | 122.849 | 123.013 | 122.9796 | 61.9576 | -123.3244
1138.2656 | 123.2391 | -66.4948 | 56.4102 | 0.04215 | -0.086454 | -0.011784 | 0.046755 | -0.019157 | 0.053805 | 0.073406 | -0.0068487 | 0.0021894 | 0.050358 | 0.088434 | 0.049709 | -66.4451 | -2.5947 | -66.4805 | 56.4441 | 56.4036 | 56.5595 | -66.723 | -66.4864 | -4.5371 | -66.5438 | 56.3359 | 56.5091 | 56.4802 | -66.9279 | -0.22829 | 0.033914 | 0.049656 | 0.014286 | 0.24258 | -0.006666 | 0.14929 | -0.43313 | -0.074317 | 0.008353 | -0.049046 | 0.38408 | 0.098866 | 0.070017 | 122.9389 | 122.8983 | 123.0543 | 63.9001 | -123.1333 | 122.8307 | 123.0038 | 122.975 | 61.9576 | -123.3381
1139.2656 | 123.2758 | -66.5131 | 56.4194 | 0.026888 | -0.087522 | -0.011784 | 0.045687 | -0.01702 | 0.054873 | 0.027623 | -0.0068487 | 0.0011204 | 0.048222 | 0.086297 | 0.051845 | -66.4543 | -2.613 | -66.4667 | 56.4441 | 56.4036 | 56.5503 | -66.7139 | -66.4864 | -4.5371 | -66.553 | 56.3359 | 56.5045 | 56.4711 | -66.9141 | -0.20082 | 0.024758 | 0.05881 | 0.046332 | 0.24715 | -0.015822 | 0.13098 | -0.40108 | -0.083473 | 0.026664 | -0.039892 | 0.36119 | 0.085131 | 0.051704 | 122.9572 | 122.9166 | 123.0634 | 63.9001 | -123.1333 | 122.849 | 123.0176 | 122.9841 | 61.9759 | -123.3335
1140.2656 | 123.2254 | -66.5359 | 56.4011 | 0.057412 | -0.086454 | -0.010716 | 0.045687 | -0.018088 | 0.053805 | 0.042884 | -0.0068487 | 0.0011204 | 0.048222 | 0.088434 | 0.050777 | -66.4543 | -2.6176 | -66.4713 | 56.4441 | 56.399 | 56.5458 | -66.7185 | -66.4818 | -4.5326 | -66.5484 | 56.3405 | 56.4999 | 56.4802 | -66.9141 | -0.18251 | 0.043069 | 0.081698 | 0.064642 | 0.24715 | -0.002089 | 0.14471 | -0.3782 | -0.060584 | 0.054131 | -0.012426 | 0.36577 | 0.098864 | 0.079172 | 122.9801 | 122.9349 | 123.0817 | 63.9184 | -123.1195 | 122.8764 | 123.0359 | 123.0162 | 62.0034 | -123.3152
1141.2656 | 123.143 | -66.5634 | 56.4423 | 0.04215 | -0.086454 | -0.012852 | 0.048892 | -0.020225 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.048222 | 0.088434 | 0.052914 | -66.4543 | -2.6176 | -66.4713 | 56.4487 | 56.399 | 56.5549 | -66.723 | -66.4772 | -4.5326 | -66.5484 | 56.3405 | 56.5045 | 56.4711 | -66.9233 | -0.15962 | 0.006448 | 0.10916 | 0.092108 | 0.25173 | -0.043288 | 0.11267 | -0.35989 | -0.10178 | 0.086175 | 0.01504 | 0.37493 | 0.062243 | 0.028816 | 123.0121 | 122.9624 | 123.1183 | 63.9459 | -123.1653 | 122.9039 | 123.0679 | 123.0345 | 62.0309 | -123.3656
1142.2656 | 123.2346 | -66.5176 | 56.3965 | 0.026888 | -0.086454 | -0.012852 | 0.046755 | -0.020225 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.04929 | 0.089502 | 0.050777 | -66.4543 | -2.6176 | -66.4713 | 56.4396 | 56.399 | 56.5503 | -66.7185 | -66.4818 | -4.528 | -66.5438 | 56.3451 | 56.5045 | 56.4665 | -66.9187 | -0.20082 | 0.043069 | 0.063387 | 0.046331 | 0.24715 | 0.002489 | 0.15386 | -0.40109 | -0.051427 | 0.03582 | -0.026158 | 0.37493 | 0.10802 | 0.070014 | 122.9572 | 122.9166 | 123.068 | 63.9001 | -123.1149 | 122.8627 | 123.0221 | 122.9841 | 61.9897 | -123.3152
1143.2656 | 123.23 | -66.4948 | 56.4239 | 0.057412 | -0.085386 | -0.010716 | 0.047824 | -0.018088 | 0.055941 | 0.058145 | -0.0068487 | 0.0011204 | 0.04929 | 0.089502 | 0.050777 | -66.4588 | -2.6038 | -66.4667 | 56.4396 | 56.399 | 56.5549 | -66.7093 | -66.4818 | -4.5326 | -66.553 | 56.3405 | 56.4953 | 56.4757 | -66.9233 | -0.21455 | 0.015603 | 0.03592 | 0.028021 | 0.24257 | -0.024977 | 0.13098 | -0.42855 | -0.083472 | 0.012932 | -0.058203 | 0.37035 | 0.071397 | 0.051706 | 122.9343 | 122.8937 | 123.0497 | 63.8909 | -123.1333 | 122.8352 | 122.9901 | 122.9704 | 61.9622 | -123.3473
1144.2656 | 123.2574 | -66.5131 | 56.3965 | 0.026888 | -0.085386 | -0.010716 | 0.045687 | -0.019157 | 0.054873 | 0.027623 | -0.0068487 | 0.0032574 | 0.04929 | 0.089502 | 0.049709 | -66.4543 | -2.6084 | -66.4759 | 56.4441 | 56.3852 | 56.5503 | -66.7139 | -66.4818 | -4.528 | -66.553 | 56.3451 | 56.5091 | 56.4665 | -66.9233 | -0.20082 | 0.047647 | 0.05881 | 0.037176 | 0.238 | -0.011248 | 0.15386 | -0.41024 | -0.051427 | 0.031243 | -0.039892 | 0.37035 | 0.1126 | 0.070014 | 122.9572 | 122.8983 | 123.0634 | 63.9047 | -123.1104 | 122.8581 | 123.0221 | 122.9796 | 61.9851 | -123.3198
1145.2656 | 123.2529 | -66.5405 | 56.4102 | 0.04215 | -0.085386 | -0.011784 | 0.044618 | -0.019157 | 0.052737 | 0.058145 | -0.0057807 | 0.0011204 | 0.050358 | 0.088434 | 0.049709 | -66.4588 | -2.613 | -66.4713 | 56.4396 | 56.3532 | 56.5412 | -66.723 | -66.4772 | -4.5234 | -66.553 | 56.3451 | 56.5045 | 56.4665 | -66.9187 | -0.18251 | 0.029336 | 0.081696 | 0.069219 | 0.25173 | -0.057034 | 0.13097 | -0.3782 | -0.06516 | 0.063286 | -0.012427 | 0.36577 | 0.094287 | 0.056281 | 122.9801 | 122.8937 | 123.0817 | 63.9276 | -123.1333 | 122.8856 | 123.045 | 123.007 | 62.0171 | -123.3289
1146.2656 | 123.2071 | -66.5268 | 56.4285 | 0.04215 | -0.087522 | -0.012852 | 0.045687 | -0.018088 | 0.053805 | 0.042884 | -0.0057807 | 0.0032574 | 0.04929 | 0.087365 | 0.050777 | -66.4543 | -2.6176 | -66.4713 | 56.435 | 56.3394 | 56.5549 | -66.7139 | -66.491 | -4.5234 | -66.5484 | 56.3451 | 56.5091 | 56.4711 | -66.9187 | -0.18709 | 0.006446 | 0.072542 | 0.055486 | 0.24258 | -0.089081 | 0.1264 | -0.39193 | -0.083471 | 0.035817 | -0.021582 | 0.37035 | 0.080555 | 0.042549 | 122.9618 | 122.8662 | 123.0817 | 63.9092 | -123.1424 | 122.8719 | 123.0359 | 122.9979 | 62.0034 | -123.3473
1147.2656 | 123.2712 | -66.5176 | 56.4194 | 0.04215 | -0.087522 | -0.010716 | 0.046755 | -0.019157 | 0.055941 | 0.058145 | -0.0057807 | 0.0021894 | 0.04929 | 0.088434 | 0.051845 | -66.4588 | -2.6221 | -66.485 | 56.435 | 56.3303 | 56.5503 | -66.723 | -66.491 | -4.5188 | -66.5484 | 56.3359 | 56.5045 | 56.4619 | -66.9187 | -0.2054 | 0.015601 | 0.058808 | 0.032596 | 0.238 | -0.089084 | 0.13098 | -0.40109 | -0.083473 | 0.026662 | -0.030737 | 0.37035 | 0.085131 | 0.042547 | 122.9526 | 122.8479 | 123.068 | 63.8955 | -123.1424 | 122.8535 | 123.0221 | 122.9796 | 61.9988 | -123.3381
1148.2656 | 123.1293 | -66.5268 | 56.4468 | 0.04215 | -0.087522 | -0.011784 | 0.048892 | -0.018088 | 0.055941 | 0.042884 | -0.0057807 | 0.0032574 | 0.048222 | 0.087365 | 0.051845 | -66.4543 | -2.6176 | -66.4713 | 56.4441 | 56.3394 | 56.5458 | -66.7139 | -66.4864 | -4.5234 | -66.5484 | 56.3496 | 56.5091 | 56.4665 | -66.9325 | -0.18709 | -0.002707 | 0.072542 | 0.055486 | 0.24258 | -0.10739 | 0.098932 | -0.40567 | -0.097203 | 0.040396 | -0.021582 | 0.38408 | 0.062245 | 0.01966 | 122.9709 | 122.8662 | 123.0726 | 63.9092 | -123.1607 | 122.8764 | 123.0359 | 122.9933 | 62.0034 | -123.3793
1149.2656 | 123.1476 | -66.5726 | 56.4148 | 0.026888 | -0.086454 | -0.012852 | 0.045687 | -0.018088 | 0.055941 | 0.058145 | -0.0068487 | 0.0021894 | 0.047154 | 0.087365 | 0.051845 | -66.4497 | -2.6176 | -66.4759 | 56.435 | 56.3715 | 56.5503 | -66.7185 | -66.4864 | -4.5142 | -66.5575 | 56.3405 | 56.5137 | 56.4619 | -66.9233 | -0.14589 | 0.020179 | 0.1229 | 0.096685 | 0.24258 | -0.043296 | 0.13555 | -0.35073 | -0.074317 | 0.086173 | 0.015038 | 0.36577 | 0.098867 | 0.047125 | 123.0075 | 122.9441 | 123.1229 | 63.955 | -123.1333 | 122.913 | 123.0862 | 123.0345 | 62.0583 | -123.3381
1150.2656 | 123.143 | -66.5359 | 56.4239 | 0.026888 | -0.085386 | -0.010716 | 0.047824 | -0.018088 | 0.052737 | 0.058145 | -0.0068487 | 0.0043254 | 0.048222 | 0.09057 | 0.050777 | -66.4543 | -2.6176 | -66.4759 | 56.4396 | 56.3944 | 56.5458 | -66.7185 | -66.491 | -4.5142 | -66.5575 | 56.3359 | 56.5045 | 56.4665 | -66.9233 | -0.18251 | 0.015603 | 0.081698 | 0.060064 | 0.24258 | -0.029556 | 0.12182 | -0.38735 | -0.08805 | 0.044973 | -0.021583 | 0.36577 | 0.080554 | 0.042548 | 122.9755 | 122.9303 | 123.0817 | 63.9184 | -123.1424 | 122.8718 | 123.0405 | 123.0024 | 62.0217 | -123.3473
1151.2656 | 123.1934 | -66.5451 | 56.4011 | 0.04215 | -0.088591 | -0.010716 | 0.045687 | -0.020225 | 0.055941 | 0.058145 | -0.0057807 | 0.0021894 | 0.04929 | 0.089502 | 0.051845 | -66.4588 | -2.6176 | -66.4759 | 56.4396 | 56.3944 | 56.5503 | -66.7276 | -66.4864 | -4.5051 | -66.553 | 56.3359 | 56.5182 | 56.4665 | -66.9233 | -0.18251 | 0.038491 | 0.086274 | 0.069219 | 0.25173 | -0.006668 | 0.14929 | -0.3782 | -0.065162 | 0.058707 | -0.007849 | 0.37035 | 0.11718 | 0.065436 | 122.9847 | 122.9395 | 123.0955 | 63.9276 | -123.1287 | 122.881 | 123.0633 | 123.0116 | 62.04 | -123.3244
1152.2656 | 123.1613 | -66.5543 | 56.4285 | 0.04215 | -0.087522 | -0.010716 | 0.048892 | -0.019157 | 0.054873 | 0.042884 | -0.0057807 | 0.0043254 | 0.048222 | 0.089502 | 0.050777 | -66.4588 | -2.6267 | -66.4896 | 56.4304 | 56.3944 | 56.5503 | -66.7185 | -66.4772 | -4.5097 | -66.553 | 56.3359 | 56.5045 | 56.4665 | -66.9279 | -0.1642 | 0.001868 | 0.095429 | 0.064639 | 0.22884 | -0.034134 | 0.12182 | -0.37362 | -0.092628 | 0.077019 | 0.001306 | 0.37493 | 0.075976 | 0.03797 | 122.9847 | 122.9487 | 123.1046 | 63.9275 | -123.147 | 122.8902 | 123.0588 | 123.0208 | 62.0446 | -123.3564
1153.2656 | 123.1659 | -66.568 | 56.4377 | 0.04215 | -0.086454 | -0.011784 | 0.047824 | -0.019157 | 0.055941 | 0.058145 | -0.0068487 | 0.0032574 | 0.048222 | 0.089502 | 0.049709 | -66.4543 | -2.6313 | -66.485 | 56.4396 | 56.399 | 56.5458 | -66.723 | -66.4818 | -4.5005 | -66.5484 | 56.3451 | 56.4999 | 56.4665 | -66.9187 | -0.15505 | 0.00187 | 0.11374 | 0.08295 | 0.238 | -0.03871 | 0.10809 | -0.35073 | -0.092626 | 0.086174 | 0.019617 | 0.37035 | 0.062243 | 0.028815 | 123.0075 | 122.967 | 123.1138 | 63.9367 | -123.1607 | 122.913 | 123.0679 | 123.0345 | 62.0675 | -123.3564
1154.2656 | 123.143 | -66.5543 | 56.4377 | 0.026888 | -0.086454 | -0.011784 | 0.046755 | -0.019157 | 0.055941 | 0.042884 | -0.0068487 | 0.0021894 | 0.048222 | 0.089502 | 0.050777 | -66.4543 | -2.6359 | -66.485 | 56.4441 | 56.3852 | 56.5458 | -66.7139 | -66.4864 | -4.5005 | -66.5484 | 56.3313 | 56.5045 | 56.4619 | -66.9279 | -0.15962 | 0.006448 | 0.10001 | 0.069217 | 0.22884 | -0.052447 | 0.10809 | -0.37362 | -0.10636 | 0.067862 | 0.005884 | 0.37951 | 0.066821 | 0.024237 | 122.9984 | 122.9395 | 123.1 | 63.9184 | -123.1516 | 122.8856 | 123.0588 | 123.0162 | 62.0537 | -123.3656
1155.2656 | 123.143 | -66.5817 | 56.4789 | 0.026888 | -0.087522 | -0.013921 | 0.045687 | -0.018088 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.048222 | 0.09057 | 0.053982 | -66.4497 | -2.6404 | -66.4805 | 56.4396 | 56.3898 | 56.5503 | -66.723 | -66.491 | -4.5051 | -66.5575 | 56.3313 | 56.4999 | 56.4665 | -66.9187 | -0.14131 | -0.039329 | 0.13205 | 0.10126 | 0.24258 | -0.089067 | 0.071467 | -0.337 | -0.14756 | 0.090749 | 0.024193 | 0.36119 | 0.021044 | -0.012384 | 123.0213 | 122.9715 | 123.1321 | 63.9413 | -123.2019 | 122.913 | 123.0817 | 123.0482 | 62.0766 | -123.3976
1156.2656 | 123.1155 | -66.5588 | 56.4606 | 0.04215 | -0.088591 | -0.011784 | 0.046755 | -0.019157 | 0.055941 | 0.012362 | -0.0068487 | 0.0011204 | 0.048222 | 0.09057 | 0.051845 | -66.4497 | -2.6359 | -66.4759 | 56.4441 | 56.399 | 56.5595 | -66.723 | -66.4864 | -4.5005 | -66.553 | 56.3359 | 56.5045 | 56.4711 | -66.9279 | -0.1642 | -0.01644 | 0.10916 | 0.082952 | 0.24715 | -0.061598 | 0.098935 | -0.36904 | -0.12467 | 0.07244 | 0.005884 | 0.37493 | 0.043933 | 0.010506 | 123.003 | 122.9578 | 123.1183 | 63.923 | -123.1836 | 122.8947 | 123.0633 | 123.0299 | 62.0583 | -123.3885
1157.2656 | 123.143 | -66.5451 | 56.4331 | 0.04215 | -0.087522 | -0.013921 | 0.046755 | -0.020225 | 0.054873 | 0.027623 | -0.0089857 | 0.0021894 | 0.04929 | 0.09057 | 0.048641 | -66.4543 | -2.6404 | -66.485 | 56.4396 | 56.399 | 56.5503 | -66.7276 | -66.4864 | -4.4868 | -66.553 | 56.3359 | 56.4953 | 56.4665 | -66.9279 | -0.18251 | 0.006448 | 0.090853 | 0.060062 | 0.24258 | -0.034132 | 0.11724 | -0.38278 | -0.097205 | 0.058707 | -0.007849 | 0.37493 | 0.062242 | 0.033393 | 122.9847 | 122.9441 | 123.0955 | 63.9047 | -123.1607 | 122.881 | 123.0405 | 123.0116 | 62.0583 | -123.361
1158.2656 | 123.1247 | -66.5451 | 56.4285 | 0.026888 | -0.087522 | -0.012852 | 0.047824 | -0.019157 | 0.054873 | 0.042884 | -0.0068487 | 0.0021894 | 0.048222 | 0.089502 | 0.050777 | -66.4588 | -2.6404 | -66.485 | 56.4441 | 56.399 | 56.5503 | -66.723 | -66.4864 | -4.4914 | -66.5575 | 56.3405 | 56.4999 | 56.4665 | -66.9279 | -0.17794 | 0.015603 | 0.086274 | 0.060062 | 0.238 | -0.029555 | 0.12182 | -0.38278 | -0.08805 | 0.058707 | -0.012428 | 0.37035 | 0.071398 | 0.03797 | 122.9892 | 122.9441 | 123.0955 | 63.9047 | -123.1516 | 122.8856 | 123.045 | 123.0116 | 62.0538 | -123.3564
1159.2656 | 123.1567 | -66.5909 | 56.4423 | 0.04215 | -0.087522 | -0.012852 | 0.047824 | -0.020225 | 0.055941 | 0.042884 | -0.0079177 | 0.0032574 | 0.04929 | 0.089502 | 0.050777 | -66.4543 | -2.6404 | -66.485 | 56.4441 | 56.4036 | 56.5458 | -66.723 | -66.491 | -4.4868 | -66.5621 | 56.3405 | 56.4953 | 56.4757 | -66.9279 | -0.13216 | 0.00187 | 0.13663 | 0.10584 | 0.238 | -0.03871 | 0.10351 | -0.337 | -0.10178 | 0.099904 | 0.028769 | 0.36577 | 0.053086 | 0.033395 | 123.035 | 122.9944 | 123.1367 | 63.9504 | -123.1653 | 122.9314 | 123.0862 | 123.0665 | 62.1041 | -123.3701
1160.2656 | 123.0972 | -66.5726 | 56.4331 | 0.026888 | -0.086454 | -0.013921 | 0.045687 | -0.021293 | 0.054873 | 0.027623 | -0.0068487 | 0.0011204 | 0.047154 | 0.089502 | 0.050777 | -66.4543 | -2.6496 | -66.4896 | 56.4487 | 56.4036 | 56.5458 | -66.7322 | -66.4864 | -4.4822 | -66.553 | 56.3405 | 56.4999 | 56.4711 | -66.9233 | -0.15963 | 0.015604 | 0.11832 | 0.08295 | 0.24258 | -0.029554 | 0.11266 | -0.35073 | -0.092627 | 0.086173 | 0.019617 | 0.37035 | 0.066821 | 0.037972 | 123.0213 | 122.9761 | 123.1183 | 63.923 | -123.1653 | 122.913 | 123.0725 | 123.0436 | 62.0904 | -123.3564
1161.2656 | 123.1247 | -66.568 | 56.4468 | 0.057412 | -0.088591 | -0.011784 | 0.044618 | -0.019157 | 0.054873 | 0.073406 | -0.0079177 | 0.0011204 | 0.048222 | 0.09057 | 0.049709 | -66.4588 | -2.6496 | -66.4896 | 56.4441 | 56.399 | 56.5595 | -66.7322 | -66.491 | -4.4776 | -66.5621 | 56.3405 | 56.4999 | 56.4757 | -66.9233 | -0.16421 | -0.002707 | 0.10916 | 0.078372 | 0.24258 | -0.047865 | 0.11267 | -0.35531 | -0.10636 | 0.077016 | 0.005881 | 0.36119 | 0.053088 | 0.028818 | 123.0121 | 122.967 | 123.1275 | 63.9184 | -123.179 | 122.9085 | 123.0679 | 123.0436 | 62.0904 | -123.3701
1162.2656 | 123.175 | -66.5405 | 56.456 | 0.04215 | -0.089659 | -0.011784 | 0.046755 | -0.021293 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.04929 | 0.089502 | 0.050777 | -66.4634 | -2.6404 | -66.485 | 56.4396 | 56.4036 | 56.5503 | -66.7322 | -66.4818 | -4.473 | -66.5575 | 56.3359 | 56.4999 | 56.4665 | -66.9325 | -0.19167 | -0.016441 | 0.077118 | 0.055484 | 0.24716 | -0.052443 | 0.094355 | -0.39193 | -0.12009 | 0.058708 | -0.017006 | 0.37493 | 0.043932 | 0.010504 | 122.9801 | 122.9441 | 123.0909 | 63.9001 | -123.1882 | 122.8764 | 123.0405 | 123.007 | 62.0675 | -123.3885
1163.2656 | 123.1567 | -66.5314 | 56.4468 | 0.057412 | -0.087522 | -0.012852 | 0.047824 | -0.018088 | 0.054873 | 0.058145 | -0.0089857 | 0.0011204 | 0.047154 | 0.089502 | 0.050777 | -66.4588 | -2.6496 | -66.485 | 56.4487 | 56.399 | 56.5458 | -66.7276 | -66.491 | -4.4776 | -66.5575 | 56.3405 | 56.5045 | 56.4757 | -66.9233 | -0.19625 | 0.001871 | 0.072541 | 0.046329 | 0.24258 | -0.047865 | 0.098932 | -0.39193 | -0.10636 | 0.040395 | -0.026161 | 0.36577 | 0.057666 | 0.028818 | 122.9801 | 122.9303 | 123.0771 | 63.8818 | -123.1745 | 122.8718 | 123.0359 | 123.007 | 62.0538 | -123.3701
1164.2656 | 123.1247 | -66.5863 | 56.4423 | 0.04215 | -0.088591 | -0.010716 | 0.046755 | -0.019157 | 0.052737 | 0.073406 | -0.0068487 | 0.0032574 | 0.04929 | 0.089502 | 0.050777 | -66.4634 | -2.6496 | -66.485 | 56.4441 | 56.3944 | 56.5549 | -66.7276 | -66.4956 | -4.4639 | -66.5484 | 56.3405 | 56.4953 | 56.4665 | -66.9279 | -0.14132 | 0.00187 | 0.12289 | 0.10126 | 0.24258 | -0.047867 | 0.11267 | -0.34158 | -0.10178 | 0.090748 | 0.037928 | 0.37951 | 0.053086 | 0.024237 | 123.0304 | 122.9807 | 123.1412 | 63.9367 | -123.1699 | 122.9268 | 123.0817 | 123.0528 | 62.1224 | -123.3701
1165.2656 | 123.1476 | -66.568 | 56.4606 | 0.026888 | -0.087522 | -0.013921 | 0.045687 | -0.019157 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.048222 | 0.09057 | 0.052914 | -66.468 | -2.645 | -66.4896 | 56.4441 | 56.399 | 56.5458 | -66.7368 | -66.4864 | -4.4685 | -66.5575 | 56.3313 | 56.5091 | 56.4665 | -66.9325 | -0.16878 | -0.01644 | 0.10001 | 0.078372 | 0.24716 | -0.061598 | 0.085199 | -0.36447 | -0.12925 | 0.081595 | 0.01046 | 0.37493 | 0.048512 | 0.005927 | 123.0121 | 122.967 | 123.1138 | 63.923 | -123.1973 | 122.8993 | 123.0771 | 123.0345 | 62.0995 | -123.393
1166.2656 | 123.1476 | -66.5634 | 56.4468 | 0.026888 | -0.087522 | -0.011784 | 0.047824 | -0.019157 | 0.055941 | 0.058145 | -0.0068487 | 0.0032574 | 0.04929 | 0.09057 | 0.049709 | -66.4588 | -2.645 | -66.4896 | 56.4396 | 56.399 | 56.5503 | -66.7322 | -66.491 | -4.4639 | -66.5575 | 56.3359 | 56.5045 | 56.4711 | -66.9279 | -0.16878 | -0.007285 | 0.10459 | 0.073795 | 0.24258 | -0.047865 | 0.10351 | -0.36447 | -0.11094 | 0.072439 | 0.005883 | 0.37035 | 0.057666 | 0.024239 | 123.003 | 122.9624 | 123.1138 | 63.9184 | -123.179 | 122.8993 | 123.0679 | 123.0345 | 62.0995 | -123.3747
1167.2656 | 123.1522 | -66.5726 | 56.4468 | 0.04215 | -0.087522 | -0.012852 | 0.047824 | -0.021293 | 0.055941 | 0.058145 | -0.0079177 | 0.0032574 | 0.047154 | 0.09057 | 0.052914 | -66.4634 | -2.645 | -66.4896 | 56.4441 | 56.3944 | 56.5503 | -66.7368 | -66.4864 | -4.4639 | -66.5575 | 56.3359 | 56.4953 | 56.4665 | -66.937 | -0.16421 | -0.002707 | 0.10916 | 0.08295 | 0.24716 | -0.052444 | 0.10351 | -0.36447 | -0.11094 | 0.086173 | 0.015038 | 0.37951 | 0.048509 | 0.01966 | 123.0167 | 122.967 | 123.1229 | 63.9275 | -123.1836 | 122.9085 | 123.0679 | 123.0391 | 62.1087 | -123.3839
1168.2656 | 123.1338 | -66.5268 | 56.4423 | 0.026888 | -0.089659 | -0.013921 | 0.047824 | -0.018088 | 0.054873 | 0.042884 | -0.0079177 | 0.0032574 | 0.048222 | 0.09057 | 0.050777 | -66.4634 | -2.6542 | -66.4896 | 56.4487 | 56.399 | 56.5595 | -66.7276 | -66.491 | -4.4593 | -66.5575 | 56.3267 | 56.5045 | 56.4711 | -66.937 | -0.20083 | 0.006448 | 0.063385 | 0.037173 | 0.238 | -0.043288 | 0.11724 | -0.41025 | -0.11552 | 0.035817 | -0.030739 | 0.37951 | 0.062243 | 0.028816 | 122.9755 | 122.9258 | 123.0863 | 63.8726 | -123.1699 | 122.8535 | 123.0313 | 122.9979 | 62.0675 | -123.3793
1169.2656 | 123.2071 | -66.5222 | 56.4423 | 0.04215 | -0.087522 | -0.012852 | 0.046755 | -0.018088 | 0.054873 | 0.088667 | -0.0079177 | 0.0021894 | 0.047154 | 0.09057 | 0.050777 | -66.468 | -2.6542 | -66.485 | 56.435 | 56.399 | 56.5458 | -66.7322 | -66.5001 | -4.4593 | -66.5575 | 56.3359 | 56.5045 | 56.4665 | -66.9279 | -0.20998 | -0.007287 | 0.05423 | 0.037174 | 0.24716 | -0.043288 | 0.10351 | -0.40566 | -0.10636 | 0.022083 | -0.035316 | 0.37035 | 0.062243 | 0.024237 | 122.9572 | 122.9212 | 123.068 | 63.868 | -123.1745 | 122.8581 | 123.0267 | 122.9887 | 62.0629 | -123.3701
1170.2656 | 123.2025 | -66.5451 | 56.456 | 0.04215 | -0.087522 | -0.010716 | 0.046755 | -0.018088 | 0.054873 | 0.073406 | -0.0068487 | 0.0021894 | 0.04929 | 0.091639 | 0.050777 | -66.4634 | -2.6588 | -66.4896 | 56.435 | 56.399 | 56.5458 | -66.7276 | -66.491 | -4.4547 | -66.5667 | 56.3359 | 56.4953 | 56.4711 | -66.937 | -0.18251 | -0.02102 | 0.081696 | 0.055484 | 0.238 | -0.057021 | 0.089776 | -0.39193 | -0.12009 | 0.054128 | -0.021585 | 0.37035 | 0.039353 | 0.015083 | 122.9801 | 122.9441 | 123.0909 | 63.8863 | -123.1836 | 122.881 | 123.0405 | 123.0162 | 62.0904 | -123.393
1171.2656 | 123.175 | -66.568 | 56.4423 | 0.04215 | -0.087522 | -0.012852 | 0.047824 | -0.018088 | 0.05701 | 0.058145 | -0.0079177 | 0.0011204 | 0.048222 | 0.092707 | 0.049709 | -66.4634 | -2.6679 | -66.4988 | 56.4396 | 56.399 | 56.5503 | -66.7322 | -66.5001 | -4.4593 | -66.5621 | 56.3359 | 56.4999 | 56.4665 | -66.9325 | -0.16421 | -0.002708 | 0.10458 | 0.069215 | 0.23342 | -0.043288 | 0.10809 | -0.36447 | -0.10636 | 0.067859 | 0.005881 | 0.37035 | 0.057665 | 0.024237 | 123.0075 | 122.967 | 123.1183 | 63.9001 | -123.1745 | 122.9039 | 123.0679 | 123.0345 | 62.1087 | -123.3747
1172.2656 | 123.1934 | -66.5405 | 56.4468 | 0.057412 | -0.089659 | -0.013921 | 0.047824 | -0.020225 | 0.05701 | 0.058145 | -0.0068487 | 0.0021894 | 0.047154 | 0.091639 | 0.049709 | -66.4634 | -2.6588 | -66.5034 | 56.4396 | 56.4081 | 56.5503 | -66.7276 | -66.491 | -4.4501 | -66.5575 | 56.3313 | 56.4999 | 56.4665 | -66.9325 | -0.18709 | -0.007285 | 0.077118 | 0.037171 | 0.22426 | -0.038708 | 0.10351 | -0.39193 | -0.11552 | 0.04955 | -0.017006 | 0.37493 | 0.053088 | 0.01966 | 122.9801 | 122.9487 | 123.0909 | 63.8818 | -123.1745 | 122.8718 | 123.0405 | 123.007 | 62.0904 | -123.3793
1173.2656 | 123.1934 | -66.5451 | 56.456 | 0.026888 | -0.087522 | -0.012852 | 0.047824 | -0.019157 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.048222 | 0.09057 | 0.051845 | -66.468 | -2.6679 | -66.4988 | 56.435 | 56.399 | 56.5503 | -66.7322 | -66.491 | -4.4501 | -66.5621 | 56.3405 | 56.4999 | 56.4711 | -66.937 | -0.18709 | -0.02102 | 0.077118 | 0.046327 | 0.23342 | -0.057021 | 0.094355 | -0.39193 | -0.11552 | 0.054128 | -0.017007 | 0.37493 | 0.043932 | 0.015083 | 122.9801 | 122.9441 | 123.0955 | 63.8772 | -123.1882 | 122.8856 | 123.045 | 123.0162 | 62.095 | -123.393
1174.2656 | 123.1888 | -66.5497 | 56.4468 | 0.04215 | -0.087522 | -0.011784 | 0.047824 | -0.020225 | 0.053805 | 0.058145 | -0.0079177 | 0.0021894 | 0.047154 | 0.09057 | 0.050777 | -66.4634 | -2.6679 | -66.4942 | 56.435 | 56.3898 | 56.5412 | -66.7322 | -66.5001 | -4.4456 | -66.5575 | 56.3313 | 56.4953 | 56.4619 | -66.9325 | -0.18252 | -0.011864 | 0.086274 | 0.055484 | 0.238 | -0.057023 | 0.094354 | -0.38278 | -0.11552 | 0.049549 | -0.00785 | 0.37493 | 0.048509 | 0.015082 | 122.9847 | 122.9395 | 123.0909 | 63.8818 | -123.179 | 122.881 | 123.045 | 123.0116 | 62.1041 | -123.3793
1175.2656 | 123.2025 | -66.5176 | 56.456 | 0.057412 | -0.089659 | -0.012852 | 0.046755 | -0.018088 | 0.052737 | 0.058145 | -0.0068487 | 0.0021894 | 0.048222 | 0.09057 | 0.050777 | -66.468 | -2.6679 | -66.4942 | 56.435 | 56.3898 | 56.5366 | -66.7322 | -66.5001 | -4.4456 | -66.5575 | 56.3313 | 56.4953 | 56.4665 | -66.9233 | -0.21456 | -0.02102 | 0.049652 | 0.02344 | 0.238 | -0.066179 | 0.080619 | -0.40566 | -0.12467 | 0.017505 | -0.039894 | 0.36577 | 0.039353 | 0.010504 | 122.9526 | 122.9075 | 123.0543 | 63.8497 | -123.1882 | 122.849 | 123.013 | 122.9841 | 62.0721 | -123.3793
1176.2656 | 123.1659 | -66.5543 | 56.4606 | 0.057412 | -0.089659 | -0.012852 | 0.046755 | -0.020225 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.04929 | 0.09057 | 0.050777 | -66.468 | -2.6679 | -66.4988 | 56.435 | 56.3944 | 56.5412 | -66.7276 | -66.4956 | -4.441 | -66.5667 | 56.3359 | 56.4862 | 56.4619 | -66.9325 | -0.17336 | -0.025597 | 0.086273 | 0.055482 | 0.22884 | -0.066177 | 0.080621 | -0.3782 | -0.12467 | 0.058704 | -0.01243 | 0.36577 | 0.025619 | 0.001349 | 122.9892 | 122.9487 | 123.0955 | 63.8863 | -123.1882 | 122.8902 | 123.0404 | 123.0162 | 62.1133 | -123.393
1177.2656 | 123.1522 | -66.5543 | 56.4423 | 0.04215 | -0.088591 | -0.011784 | 0.046755 | -0.018088 | 0.055941 | 0.042884 | -0.0089857 | 0.0011204 | 0.046085 | 0.09057 | 0.050777 | -66.4726 | -2.6725 | -66.5034 | 56.4441 | 56.3898 | 56.5503 | -66.7368 | -66.4956 | -4.4456 | -66.5667 | 56.3267 | 56.4908 | 56.4619 | -66.9325 | -0.18252 | 0.00187 | 0.081694 | 0.050904 | 0.23342 | -0.052446 | 0.10809 | -0.3782 | -0.11552 | 0.058704 | -0.01243 | 0.36577 | 0.048508 | 0.019659 | 122.9984 | 122.9441 | 123.1046 | 63.8818 | -123.179 | 122.881 | 123.045 | 123.0162 | 62.1087 | -123.3747
1178.2656 | 123.2254 | -66.5405 | 56.5018 | 0.026888 | -0.087522 | -0.012852 | 0.047824 | -0.020225 | 0.055941 | 0.042884 | -0.0068487 | 0.0011204 | 0.048222 | 0.092707 | 0.051845 | -66.4726 | -2.6771 | -66.4988 | 56.435 | 56.3898 | 56.5503 | -66.7322 | -66.5001 | -4.4318 | -66.5621 | 56.3222 | 56.4953 | 56.4711 | -66.9416 | -0.19167 | -0.066796 | 0.067961 | 0.041749 | 0.23342 | -0.11196 | 0.048579 | -0.40109 | -0.17961 | 0.040393 | -0.021585 | 0.37951 | -0.006423 | -0.030693 | 122.9755 | 122.9303 | 123.0909 | 63.8635 | -123.234 | 122.8627 | 123.0359 | 123.0116 | 62.1087 | -123.4434
1179.3281 | 123.2025 | -66.5131 | 56.4011 | 0.057412 | -0.089659 | -0.013921 | 0.046755 | -0.019157 | 0.058078 | 0.042884 | -0.0079177 | 0.0021894 | 0.048222 | 0.091639 | 0.050777 | -66.4726 | -2.6725 | -66.4942 | 56.4396 | 56.3898 | 56.5412 | -66.7368 | -66.4956 | -4.441 | -66.5621 | 56.3313 | 56.5045 | 56.4665 | -66.937 | -0.22372 | 0.038491 | 0.040496 | 0.018863 | 0.24258 | -0.011247 | 0.14013 | -0.42398 | -0.069741 | 0.017506 | -0.04905 | 0.37493 | 0.10344 | 0.065436 | 122.9526 | 122.9029 | 123.0543 | 63.8406 | -123.1378 | 122.8444 | 123.0176 | 122.9796 | 62.0721 | -123.3381
1180.2656 | 123.1659 | -66.5405 | 56.4743 | 0.04215 | -0.089659 | -0.011784 | 0.046755 | -0.021293 | 0.054873 | 0.058145 | -0.0079177 | 0.0032574 | 0.050358 | 0.091639 | 0.050777 | -66.4726 | -2.6771 | -66.4942 | 56.4396 | 56.3898 | 56.5503 | -66.7322 | -66.5047 | -4.4273 | -66.5621 | 56.3267 | 56.4999 | 56.4619 | -66.9416 | -0.19167 | -0.034751 | 0.067961 | 0.046328 | 0.238 | -0.084489 | 0.076045 | -0.40109 | -0.14756 | 0.035814 | -0.021585 | 0.37951 | 0.025622 | -0.012384 | 122.9801 | 122.9303 | 123.0909 | 63.8635 | -123.2065 | 122.8673 | 123.0405 | 123.0024 | 62.1133 | -123.4159
1181.2656 | 123.175 | -66.5634 | 56.456 | 0.04215 | -0.088591 | -0.012852 | 0.046755 | -0.020225 | 0.05701 | 0.073406 | -0.0089857 | 0.0032574 | 0.048222 | 0.091639 | 0.051845 | -66.4634 | -2.6908 | -66.4942 | 56.4304 | 56.3944 | 56.5503 | -66.7414 | -66.5001 | -4.4181 | -66.5621 | 56.3313 | 56.4953 | 56.4711 | -66.937 | -0.17794 | -0.025598 | 0.10001 | 0.069217 | 0.24716 | -0.0616 | 0.094355 | -0.37362 | -0.12467 | 0.063282 | 0.001304 | 0.37493 | 0.039353 | 0.015083 | 122.9938 | 122.9578 | 123.1138 | 63.8726 | -123.1974 | 122.8947 | 123.0588 | 123.0345 | 62.1453 | -123.393
1182.2656 | 123.1247 | -66.5588 | 56.4697 | 0.057412 | -0.089659 | -0.012852 | 0.045687 | -0.019157 | 0.055941 | 0.073406 | -0.0057807 | 0.0032574 | 0.048222 | 0.091639 | 0.051845 | -66.4726 | -2.6908 | -66.4942 | 56.4441 | 56.3898 | 56.5503 | -66.7414 | -66.491 | -4.4181 | -66.5621 | 56.3267 | 56.4999 | 56.4619 | -66.937 | -0.18252 | -0.025596 | 0.086272 | 0.064639 | 0.24716 | -0.079912 | 0.080622 | -0.3782 | -0.14298 | 0.067861 | -0.003274 | 0.37493 | 0.030199 | -0.007807 | 123.003 | 122.9487 | 123.1092 | 63.868 | -123.2111 | 122.8856 | 123.0588 | 123.0208 | 62.1407 | -123.4068
1183.2656 | 123.1384 | -66.4856 | 56.4606 | 0.057412 | -0.087522 | -0.012852 | 0.047824 | -0.020225 | 0.054873 | 0.073406 | -0.0057807 | 0.0032574 | 0.048222 | 0.091639 | 0.051845 | -66.4726 | -2.7 | -66.4896 | 56.4304 | 56.399 | 56.5458 | -66.7368 | -66.5001 | -4.4181 | -66.5621 | 56.3267 | 56.4908 | 56.4619 | -66.9416 | -0.25118 | -0.030175 | 0.01303 | -0.004025 | 0.24716 | -0.061598 | 0.085199 | -0.45602 | -0.13383 | -0.014538 | -0.076516 | 0.37951 | 0.030198 | 0.001349 | 122.916 | 122.8846 | 123.0314 | 63.7856 | -123.1973 | 122.8123 | 122.9764 | 122.9475 | 62.0675 | -123.4022
1184.2656 | 123.1476 | -66.5497 | 56.4789 | 0.057412 | -0.090727 | -0.011784 | 0.047824 | -0.018088 | 0.055941 | 0.073406 | -0.0068487 | 0.0011204 | 0.048222 | 0.091639 | 0.051845 | -66.4771 | -2.6954 | -66.4942 | 56.435 | 56.3898 | 56.5412 | -66.7414 | -66.4956 | -4.4089 | -66.5713 | 56.3313 | 56.4908 | 56.4619 | -66.9416 | -0.19167 | -0.043908 | 0.072539 | 0.055484 | 0.24716 | -0.089067 | 0.06231 | -0.39194 | -0.14756 | 0.054127 | -0.021586 | 0.37035 | 0.011887 | -0.016962 | 122.9847 | 122.9395 | 123.0909 | 63.8543 | -123.2202 | 122.881 | 123.0405 | 123.0116 | 62.1407 | -123.4205
1185.2656 | 123.1338 | -66.5497 | 56.4743 | 0.026888 | -0.088591 | -0.011784 | 0.045687 | -0.019157 | 0.05701 | 0.058145 | -0.0057807 | 0.0032574 | 0.048222 | 0.092707 | 0.051845 | -66.4771 | -2.7091 | -66.4942 | 56.435 | 56.3944 | 56.5458 | -66.7414 | -66.4956 | -4.4089 | -66.5713 | 56.3267 | 56.4999 | 56.4619 | -66.9416 | -0.19167 | -0.03933 | 0.072539 | 0.055484 | 0.24716 | -0.07991 | 0.071466 | -0.39194 | -0.14756 | 0.054127 | -0.021586 | 0.37035 | 0.025622 | -0.012384 | 122.9847 | 122.9441 | 123.0955 | 63.8406 | -123.2157 | 122.8764 | 123.0496 | 123.0116 | 62.1407 | -123.4159
1186.2656 | 123.1338 | -66.5543 | 56.4697 | 0.04215 | -0.087522 | -0.010716 | 0.046755 | -0.020225 | 0.055941 | 0.073406 | -0.0089857 | 0.0021894 | 0.048222 | 0.091639 | 0.048641 | -66.468 | -2.7137 | -66.4988 | 56.4304 | 56.3944 | 56.5503 | -66.7414 | -66.5047 | -4.4089 | -66.5713 | 56.3267 | 56.4908 | 56.4619 | -66.9325 | -0.1871 | -0.039331 | 0.086273 | 0.055482 | 0.24258 | -0.075333 | 0.080622 | -0.3782 | -0.14298 | 0.049547 | -0.017009 | 0.36119 | 0.021042 | -0.007807 | 122.9847 | 122.9487 | 123.1046 | 63.8406 | -123.2111 | 122.881 | 123.045 | 123.0162 | 62.1453 | -123.4022
1187.2656 | 123.1476 | -66.5497 | 56.4651 | 0.026888 | -0.089659 | -0.013921 | 0.046755 | -0.019157 | 0.054873 | 0.042884 | -0.0068487 | 0.0011204 | 0.047154 | 0.091639 | 0.051845 | -66.4817 | -2.7229 | -66.5079 | 56.435 | 56.3944 | 56.5412 | -66.7414 | -66.5047 | -4.4089 | -66.5667 | 56.3313 | 56.4953 | 56.4665 | -66.9416 | -0.19167 | -0.030175 | 0.06796 | 0.041749 | 0.23342 | -0.070755 | 0.076043 | -0.39194 | -0.13383 | 0.04497 | -0.017007 | 0.37493 | 0.030198 | 0.001349 | 122.9847 | 122.9441 | 123.0909 | 63.8268 | -123.2065 | 122.881 | 123.045 | 123.0162 | 62.1407 | -123.4068
1188.2656 | 123.1476 | -66.5588 | 56.4789 | 0.026888 | -0.088591 | -0.013921 | 0.045687 | -0.020225 | 0.055941 | 0.073406 | -0.0089857 | 0.0011204 | 0.048222 | 0.093775 | 0.051845 | -66.4863 | -2.7458 | -66.5079 | 56.435 | 56.3898 | 56.5458 | -66.7368 | -66.5001 | -4.4089 | -66.5621 | 56.3267 | 56.4908 | 56.4573 | -66.9416 | -0.17794 | -0.043908 | 0.072537 | 0.050904 | 0.22884 | -0.089067 | 0.066888 | -0.38278 | -0.15214 | 0.058704 | -0.003274 | 0.37951 | 0.011887 | -0.021541 | 122.9938 | 122.9487 | 123.1046 | 63.8131 | -123.2157 | 122.8856 | 123.0496 | 123.0162 | 62.1499 | -123.4205
1189.2656 | 123.2483 | -66.5268 | 56.4102 | 0.026888 | -0.087522 | -0.013921 | 0.044618 | -0.021293 | 0.053805 | 0.042884 | -0.0079177 | 0.0032574 | 0.048222 | 0.091639 | 0.049709 | -66.4726 | -2.7641 | -66.5079 | 56.4304 | 56.3807 | 56.5458 | -66.7276 | -66.5047 | -4.4044 | -66.5713 | 56.3267 | 56.4999 | 56.4619 | -66.9462 | -0.20083 | 0.020179 | 0.054228 | 0.01886 | 0.21969 | -0.02956 | 0.13555 | -0.4194 | -0.083474 | 0.022081 | -0.044475 | 0.37493 | 0.089709 | 0.051703 | 122.9572 | 122.9075 | 123.0726 | 63.7627 | -123.1378 | 122.8535 | 123.0267 | 122.9887 | 62.1224 | -123.3564
1190.2656 | 123.2803 | -66.5039 | 56.4331 | 0.04215 | -0.089659 | -0.013921 | 0.045687 | -0.020225 | 0.054873 | 0.073406 | -0.0068487 | 0.0032574 | 0.048222 | 0.091639 | 0.049709 | -66.4726 | -2.7961 | -66.5079 | 56.435 | 56.3852 | 56.5412 | -66.7459 | -66.491 | -4.3998 | -66.5758 | 56.3313 | 56.4999 | 56.4528 | -66.9462 | -0.24203 | 0.001869 | 0.03134 | -0.004028 | 0.238 | -0.047869 | 0.10809 | -0.44229 | -0.10178 | 0.012929 | -0.071942 | 0.37035 | 0.066821 | 0.019657 | 122.9389 | 122.8891 | 123.0451 | 63.7078 | -123.179 | 122.8352 | 123.0038 | 122.9567 | 62.1041 | -123.3793
1191.2656 | 123.2025 | -66.5222 | 56.4423 | 0.057412 | -0.090727 | -0.012852 | 0.045687 | -0.021293 | 0.055941 | 0.042884 | -0.0068487 | 0.0021894 | 0.047154 | 0.092707 | 0.049709 | -66.4909 | -2.8785 | -66.5171 | 56.435 | 56.3852 | 56.5366 | -66.7459 | -66.5184 | -4.4044 | -66.5758 | 56.3267 | 56.4862 | 56.4528 | -66.9462 | -0.22372 | -0.007287 | 0.031338 | 0.005126 | 0.22884 | -0.057025 | 0.094352 | -0.42398 | -0.11552 | 0.003768 | -0.053631 | 0.37035 | 0.043929 | 0.010501 | 122.9572 | 122.9075 | 123.0588 | 63.6437 | -123.1882 | 122.849 | 123.0084 | 122.975 | 62.1179 | -123.3885
1192.2656 | 123.1522 | -66.5405 | 56.4606 | 0.057412 | -0.090727 | -0.012852 | 0.047824 | -0.021293 | 0.052737 | 0.073406 | -0.0057807 | 0.0021894 | 0.048222 | 0.091639 | 0.050777 | -66.4863 | -3.0159 | -66.5125 | 56.4304 | 56.3761 | 56.5366 | -66.7597 | -66.5184 | -4.3906 | -66.5804 | 56.313 | 56.4862 | 56.4482 | -66.9508 | -0.21914 | -0.030175 | 0.054226 | 0.028014 | 0.24716 | -0.084493 | 0.076042 | -0.41025 | -0.14756 | 0.022078 | -0.0399 | 0.37035 | 0.025619 | -0.012387 | 122.9709 | 122.9166 | 123.0771 | 63.5246 | -123.2202 | 122.8535 | 123.0267 | 122.9887 | 62.1499 | -123.4113
1193.2656 | 123.1522 | -66.5451 | 56.4468 | 0.057412 | -0.089659 | -0.013921 | 0.045687 | -0.019157 | 0.053805 | 0.058145 | -0.0089857 | 0.0021894 | 0.04929 | 0.09057 | 0.048641 | -66.5046 | -3.5104 | -66.5262 | 56.4075 | 56.3669 | 56.5229 | -66.7643 | -66.5276 | -4.4044 | -66.5804 | 56.3038 | 56.4679 | 56.4344 | -66.9645 | -0.21915 | -0.039334 | 0.04049 | 0.018858 | 0.238 | -0.079918 | 0.076039 | -0.41941 | -0.14299 | 0.017498 | -0.035322 | 0.38409 | 0.021038 | -0.01239 | 122.9526 | 122.912 | 123.068 | 63.0347 | -123.2111 | 122.849 | 123.013 | 122.9796 | 62.1407 | -123.4114
1194.2656 | 123.2117 | -66.5588 | 56.4285 | 0.026888 | -0.088591 | -0.013921 | 0.046755 | -0.019157 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.048222 | 0.092707 | 0.049709 | -66.5138 | -3.808 | -66.5446 | 56.4029 | 56.3578 | 56.5091 | -66.7734 | -66.5413 | -4.3952 | -66.6033 | 56.2901 | 56.4496 | 56.4253 | -66.9782 | -0.21457 | -0.025603 | 0.045067 | 0.014278 | 0.22885 | -0.070766 | 0.080614 | -0.41941 | -0.13841 | 0.017495 | -0.044482 | 0.37493 | 0.021033 | -0.003237 | 122.9618 | 122.9166 | 123.068 | 62.7508 | -123.2019 | 122.849 | 123.0084 | 122.9841 | 62.1636 | -123.4068
1195.2656 | 123.2071 | -66.5588 | 56.4148 | 0.026888 | -0.089659 | -0.011784 | 0.044618 | -0.021293 | 0.054873 | 0.073406 | -0.0068487 | 0.0032574 | 0.047154 | 0.092707 | 0.050777 | -66.5229 | -4.1056 | -66.5537 | 56.3938 | 56.344 | 56.5 | -66.7826 | -66.5505 | -4.3998 | -66.6125 | 56.2855 | 56.4496 | 56.4161 | -66.9966 | -0.22373 | -0.021026 | 0.03591 | 0.005121 | 0.22885 | -0.07077 | 0.085189 | -0.43773 | -0.12926 | 0.008338 | -0.05364 | 0.38409 | 0.034766 | 0.001339 | 122.9526 | 122.9029 | 123.0588 | 62.4532 | -123.1974 | 122.8444 | 123.0084 | 122.975 | 62.1591 | -123.4114
1196.2656 | 123.2666 | -66.5726 | 56.3828 | 0.04215 | -0.089659 | -0.012852 | 0.045687 | -0.019157 | 0.055941 | 0.042884 | -0.0079177 | 0.0021894 | 0.047154 | 0.091639 | 0.050777 | -66.5367 | -4.4627 | -66.5675 | 56.3846 | 56.3349 | 56.4908 | -66.7917 | -66.5597 | -4.4044 | -66.6216 | 56.2672 | 56.4358 | 56.4024 | -66.992 | -0.21915 | 0.001861 | 0.035908 | 0.005119 | 0.22427 | -0.047883 | 0.10808 | -0.41942 | -0.11553 | 0.012913 | -0.049064 | 0.37035 | 0.053074 | 0.019647 | 122.9572 | 122.9074 | 123.0634 | 62.1098 | -123.1745 | 122.8398 | 123.0084 | 122.975 | 62.1682 | -123.3747
1197.2656 | 123.2895 | -66.5543 | 56.3416 | 0.057412 | -0.090727 | -0.012852 | 0.047824 | -0.019157 | 0.054873 | 0.042884 | -0.0057807 | 0.0021894 | 0.047154 | 0.092707 | 0.049709 | -66.5321 | -4.4994 | -66.5675 | 56.3755 | 56.3349 | 56.4908 | -66.7917 | -66.5551 | -4.3952 | -66.6308 | 56.281 | 56.4358 | 56.407 | -66.9966 | -0.23747 | 0.033902 | 0.022175 | -0.013192 | 0.22427 | -0.006685 | 0.14927 | -0.44231 | -0.060595 | -0.000819 | -0.076532 | 0.36577 | 0.094272 | 0.065423 | 122.9297 | 122.8891 | 123.0451 | 62.0549 | -123.1333 | 122.8352 | 122.9901 | 122.9612 | 62.1591 | -123.3381
1198.2656 | 123.2803 | -66.5634 | 56.3828 | 0.011626 | -0.088591 | -0.013921 | 0.046755 | -0.019157 | 0.054873 | 0.042884 | -0.0068487 | 0.0032574 | 0.048222 | 0.092707 | 0.048641 | -66.5321 | -4.5314 | -66.5675 | 56.3709 | 56.3394 | 56.4862 | -66.7963 | -66.5642 | -4.3952 | -66.6308 | 56.2718 | 56.4358 | 56.3932 | -66.9966 | -0.23289 | -0.011874 | 0.031331 | -0.004036 | 0.22885 | -0.043304 | 0.1035 | -0.43315 | -0.11095 | -0.00082 | -0.067376 | 0.36577 | 0.053074 | 0.01049 | 122.9343 | 122.9029 | 123.0497 | 62.032 | -123.1791 | 122.8352 | 122.9992 | 122.9567 | 62.1682 | -123.3793
1199.2656 | 123.2529 | -66.568 | 56.3599 | 0.057412 | -0.089659 | -0.012852 | 0.046755 | -0.020225 | 0.055941 | 0.073406 | -0.0068487 | 0.0021894 | 0.046085 | 0.09057 | 0.048641 | -66.5412 | -4.5497 | -66.572 | 56.3709 | 56.3257 | 56.4771 | -66.7917 | -66.5642 | -4.3998 | -66.6262 | 56.2718 | 56.4267 | 56.4024 | -67.0057 | -0.22373 | 0.011014 | 0.026751 | -0.004037 | 0.2197 | -0.034153 | 0.11723 | -0.43773 | -0.088062 | 0.003757 | -0.058221 | 0.37951 | 0.066805 | 0.042535 | 122.9389 | 122.8937 | 123.0451 | 62.0183 | -123.1516 | 122.8398 | 122.9947 | 122.9704 | 62.1682 | -123.3656
1200.2656 | 123.2758 | -66.5497 | 56.369 | 0.057412 | -0.092864 | -0.012852 | 0.045687 | -0.020225 | 0.055941 | 0.042884 | -0.0079177 | 0.0021894 | 0.04929 | 0.092707 | 0.049709 | -66.5458 | -4.5818 | -66.5675 | 56.3709 | 56.3257 | 56.4817 | -66.7917 | -66.5597 | -4.4089 | -66.6308 | 56.2672 | 56.4358 | 56.3978 | -66.992 | -0.24204 | 0.001858 | 0.003863 | -0.017769 | 0.22427 | -0.043309 | 0.11265 | -0.4423 | -0.1018 | -0.009975 | -0.081109 | 0.36119 | 0.066806 | 0.0288 | 122.9206 | 122.8754 | 123.0314 | 61.9679 | -123.1607 | 122.8169 | 122.9855 | 122.9475 | 62.1407 | -123.361
1201.2656 | 123.2483 | -66.5863 | 56.369 | 0.057412 | -0.089659 | -0.013921 | 0.046755 | -0.020225 | 0.054873 | 0.042884 | -0.0057807 | 0.0032574 | 0.048222 | 0.091639 | 0.048641 | -66.5458 | -4.6092 | -66.572 | 56.3709 | 56.3074 | 56.4817 | -66.7917 | -66.5597 | -4.3906 | -66.6354 | 56.2718 | 56.4358 | 56.3978 | -66.9966 | -0.20542 | 0.001858 | 0.040484 | 0.014274 | 0.2197 | -0.061625 | 0.11265 | -0.41026 | -0.097218 | 0.026646 | -0.049067 | 0.36119 | 0.066806 | 0.0288 | 122.9572 | 122.8937 | 123.068 | 61.9771 | -123.1607 | 122.8581 | 123.0221 | 122.9841 | 62.1957 | -123.3656
1202.2656 | 123.3078 | -66.5543 | 56.3736 | 0.011626 | -0.090727 | -0.011784 | 0.045687 | -0.020225 | 0.055941 | 0.073406 | -0.0089857 | 0.0043254 | 0.048222 | 0.093775 | 0.051845 | -66.5504 | -4.6138 | -66.5675 | 56.3709 | 56.3257 | 56.4771 | -66.8055 | -66.5642 | -4.3998 | -66.6399 | 56.2672 | 56.4267 | 56.3978 | -67.0011 | -0.2512 | -0.002719 | 0.003862 | -0.013192 | 0.23801 | -0.047886 | 0.1035 | -0.44688 | -0.10637 | -0.009976 | -0.08569 | 0.36119 | 0.053072 | 0.024223 | 122.9251 | 122.88 | 123.0314 | 61.9404 | -123.1791 | 122.8215 | 122.9809 | 122.9521 | 62.1545 | -123.3747
1203.2656 | 123.2437 | -66.5955 | 56.3965 | 0.057412 | -0.091796 | -0.012852 | 0.044618 | -0.021293 | 0.054873 | 0.058145 | -0.0089857 | 5.2373e-05 | 0.047154 | 0.092707 | 0.049709 | -66.5504 | -4.6092 | -66.5675 | 56.3663 | 56.3303 | 56.4817 | -66.7963 | -66.5688 | -4.3906 | -66.6308 | 56.2718 | 56.4312 | 56.3978 | -66.9966 | -0.20085 | -0.030186 | 0.045061 | 0.028007 | 0.22885 | -0.066195 | 0.085186 | -0.40111 | -0.12468 | 0.026644 | -0.035333 | 0.36577 | 0.034763 | 0.001335 | 122.9618 | 122.9257 | 123.0771 | 61.9862 | -123.1928 | 122.8673 | 123.0267 | 122.9933 | 62.2048 | -123.393
1204.2656 | 123.2437 | -66.5909 | 56.3599 | 0.04215 | -0.091796 | -0.012852 | 0.046755 | -0.021293 | 0.053805 | 0.042884 | -0.0089857 | 0.0021894 | 0.047154 | 0.091639 | 0.051845 | -66.5367 | -4.6138 | -66.572 | 56.3617 | 56.3028 | 56.4817 | -66.7963 | -66.5688 | -4.3952 | -66.6308 | 56.2718 | 56.4267 | 56.3841 | -67.0011 | -0.20542 | 0.001857 | 0.054218 | 0.018851 | 0.22427 | -0.057048 | 0.12181 | -0.41026 | -0.088062 | 0.022066 | -0.039911 | 0.37035 | 0.066805 | 0.02422 | 122.9526 | 122.8937 | 123.0726 | 61.9771 | -123.1562 | 122.8627 | 123.0175 | 122.975 | 62.1957 | -123.361
1205.2656 | 123.262 | -66.5909 | 56.369 | 0.04215 | -0.090727 | -0.012852 | 0.046755 | -0.021293 | 0.055941 | 0.058145 | -0.0068487 | 0.0021894 | 0.047154 | 0.092707 | 0.049709 | -66.5458 | -4.6367 | -66.5675 | 56.3617 | 56.3028 | 56.4771 | -66.8009 | -66.5642 | -4.3952 | -66.6262 | 56.2718 | 56.4312 | 56.3932 | -67.0011 | -0.21 | -0.007299 | 0.045061 | 0.023429 | 0.23343 | -0.066204 | 0.10807 | -0.41026 | -0.097218 | 0.026645 | -0.035333 | 0.37493 | 0.062228 | 0.024222 | 122.9526 | 122.8937 | 123.068 | 61.9542 | -123.1699 | 122.8627 | 123.0221 | 122.9841 | 62.1957 | -123.3702
1206.2656 | 123.2758 | -66.5543 | 56.3461 | 0.057412 | -0.090727 | -0.013921 | 0.044618 | -0.018088 | 0.054873 | 0.058145 | -0.0089857 | 0.0032574 | 0.048222 | 0.093775 | 0.048641 | -66.5504 | -4.6367 | -66.5675 | 56.3709 | 56.2708 | 56.4725 | -66.7917 | -66.5597 | -4.3952 | -66.6445 | 56.2764 | 56.4267 | 56.3887 | -66.9966 | -0.23747 | 0.024747 | 0.003862 | -0.013192 | 0.22427 | -0.075367 | 0.12638 | -0.44231 | -0.069751 | -0.005398 | -0.090269 | 0.35204 | 0.080538 | 0.042532 | 122.9251 | 122.825 | 123.0268 | 61.9175 | -123.1379 | 122.8306 | 122.9809 | 122.9429 | 62.1591 | -123.3427
1207.2656 | 123.3673 | -66.5451 | 56.3599 | 0.04215 | -0.090727 | -0.013921 | 0.045687 | -0.021293 | 0.055941 | 0.042884 | -0.0068487 | 0.0021894 | 0.048222 | 0.093775 | 0.049709 | -66.5412 | -4.6413 | -66.572 | 56.3617 | 56.2753 | 56.4771 | -66.7963 | -66.5688 | -4.386 | -66.6308 | 56.2718 | 56.4267 | 56.3932 | -67.0149 | -0.2512 | 0.001857 | 0.003863 | -0.026925 | 0.22427 | -0.084521 | 0.11723 | -0.46977 | -0.088062 | -0.02371 | -0.085687 | 0.38409 | 0.066805 | 0.033378 | 122.9068 | 122.8204 | 123.0222 | 61.9038 | -123.1562 | 122.8169 | 122.9718 | 122.9383 | 62.1591 | -123.3747
1208.2656 | 123.2666 | -66.5817 | 56.3828 | 0.04215 | -0.090727 | -0.013921 | 0.045687 | -0.020225 | 0.053805 | 0.088667 | -0.0079177 | 0.0021894 | 0.050358 | 0.094844 | 0.050777 | -66.5504 | -4.6505 | -66.5812 | 56.3663 | 56.2616 | 56.4771 | -66.7917 | -66.578 | -4.386 | -66.6308 | 56.2626 | 56.4312 | 56.3932 | -66.9966 | -0.21 | -0.016453 | 0.031328 | 0.000539 | 0.21054 | -0.12115 | 0.09434 | -0.41484 | -0.12011 | 0.003754 | -0.049066 | 0.36577 | 0.048496 | 0.01049 | 122.948 | 122.8433 | 123.0588 | 61.9313 | -123.1745 | 122.8444 | 123.013 | 122.975 | 62.1957 | -123.3793
1209.2656 | 123.2483 | -66.5817 | 56.369 | 0.04215 | -0.091796 | -0.013921 | 0.045687 | -0.021293 | 0.052737 | 0.088667 | -0.0068487 | 0.0032574 | 0.047154 | 0.093775 | 0.051845 | -66.5412 | -4.6459 | -66.5812 | 56.3663 | 56.257 | 56.4771 | -66.8009 | -66.5642 | -4.386 | -66.6262 | 56.2718 | 56.4267 | 56.3841 | -66.9966 | -0.21916 | -0.002721 | 0.040484 | 0.000539 | 0.2197 | -0.11199 | 0.10807 | -0.41484 | -0.097218 | 0.01749 | -0.044488 | 0.37035 | 0.057649 | 0.015064 | 122.948 | 122.8388 | 123.0588 | 61.9359 | -123.1699 | 122.8535 | 123.0084 | 122.9658 | 62.1957 | -123.3656
1210.2656 | 123.23 | -66.5863 | 56.3599 | 0.04215 | -0.091796 | -0.012852 | 0.046755 | -0.021293 | 0.054873 | 0.042884 | -0.0079177 | 0.0032574 | 0.046085 | 0.092707 | 0.050777 | -66.5412 | -4.6413 | -66.5812 | 56.3617 | 56.2479 | 56.4771 | -66.8009 | -66.5688 | -4.3769 | -66.6354 | 56.2764 | 56.4312 | 56.3887 | -67.0011 | -0.21458 | 0.001857 | 0.045062 | 0.005117 | 0.2197 | -0.112 | 0.11723 | -0.41484 | -0.083484 | 0.017489 | -0.049067 | 0.36577 | 0.071384 | 0.028799 | 122.948 | 122.8342 | 123.0634 | 61.945 | -123.1607 | 122.8627 | 123.0176 | 122.975 | 62.2094 | -123.361
1211.2656 | 123.2437 | -66.6229 | 56.3553 | 0.026888 | -0.092864 | -0.013921 | 0.045687 | -0.020225 | 0.054873 | 0.073406 | -0.0079177 | 0.0021894 | 0.047154 | 0.092707 | 0.050777 | -66.5504 | -4.6505 | -66.572 | 56.3571 | 56.257 | 56.4725 | -66.7917 | -66.5688 | -4.3815 | -66.6308 | 56.2672 | 56.4358 | 56.3887 | -67.0057 | -0.1688 | 0.001856 | 0.072527 | 0.050895 | 0.2197 | -0.09826 | 0.11723 | -0.3828 | -0.088064 | 0.05411 | -0.007867 | 0.37493 | 0.080539 | 0.033376 | 122.9801 | 122.88 | 123.0954 | 61.9725 | -123.147 | 122.8901 | 123.0588 | 123.0116 | 62.2415 | -123.361
1212.2656 | 123.2208 | -66.5909 | 56.3599 | 0.04215 | -0.091796 | -0.013921 | 0.045687 | -0.022362 | 0.055941 | 0.042884 | -0.0079177 | 0.0032574 | 0.048222 | 0.093775 | 0.049709 | -66.5412 | -4.6459 | -66.5766 | 56.3663 | 56.257 | 56.4771 | -66.7917 | -66.5734 | -4.3815 | -66.6308 | 56.2764 | 56.4358 | 56.3887 | -67.0057 | -0.20084 | 0.006435 | 0.049639 | 0.014273 | 0.21512 | -0.10284 | 0.11723 | -0.41484 | -0.083484 | 0.017487 | -0.039911 | 0.37493 | 0.075962 | 0.028799 | 122.9572 | 122.8479 | 123.068 | 61.945 | -123.1516 | 122.8673 | 123.0267 | 122.9795 | 62.2094 | -123.3656
1213.2656 | 123.2437 | -66.5909 | 56.3553 | 0.04215 | -0.092864 | -0.012852 | 0.046755 | -0.020225 | 0.055941 | 0.027623 | -0.0079177 | 0.0011204 | 0.048222 | 0.092707 | 0.050777 | -66.5504 | -4.6505 | -66.5812 | 56.3663 | 56.2799 | 56.4771 | -66.7917 | -66.5734 | -4.3769 | -66.6354 | 56.2626 | 56.4312 | 56.3887 | -67.0103 | -0.20084 | 0.011012 | 0.040483 | 0.009694 | 0.21054 | -0.075365 | 0.12181 | -0.41942 | -0.092642 | 0.017487 | -0.04449 | 0.37493 | 0.075961 | 0.033376 | 122.9572 | 122.8708 | 123.068 | 61.9404 | -123.147 | 122.8535 | 123.0221 | 122.9795 | 62.214 | -123.3656
1214.2656 | 123.2254 | -66.5863 | 56.3828 | 0.04215 | -0.091796 | -0.013921 | 0.045687 | -0.020225 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.047154 | 0.093775 | 0.050777 | -66.5458 | -4.6505 | -66.5812 | 56.3663 | 56.312 | 56.4817 | -66.7917 | -66.5734 | -4.3723 | -66.6354 | 56.2672 | 56.4404 | 56.3887 | -67.0103 | -0.20542 | -0.016453 | 0.040484 | 0.005117 | 0.21054 | -0.070778 | 0.098919 | -0.424 | -0.11553 | 0.01291 | -0.049067 | 0.37493 | 0.057653 | 0.005911 | 122.9526 | 122.8983 | 123.068 | 61.9359 | -123.1745 | 122.8535 | 123.0267 | 122.975 | 62.214 | -123.3931
1215.2656 | 123.2391 | -66.5909 | 56.3599 | 0.04215 | -0.092864 | -0.011784 | 0.046755 | -0.021293 | 0.054873 | 0.088667 | -0.0089857 | 0.0021894 | 0.047154 | 0.092707 | 0.048641 | -66.5504 | -4.6505 | -66.5766 | 56.3571 | 56.3166 | 56.4817 | -66.8009 | -66.5734 | -4.3632 | -66.6308 | 56.2672 | 56.4312 | 56.3978 | -67.0057 | -0.21 | -0.002721 | 0.040483 | 0.014273 | 0.22427 | -0.043311 | 0.12181 | -0.41484 | -0.092641 | 0.017487 | -0.039911 | 0.37493 | 0.071384 | 0.037956 | 122.948 | 122.9074 | 123.0726 | 61.9404 | -123.1607 | 122.8581 | 123.0221 | 122.9887 | 62.2277 | -123.3656
1216.2656 | 123.2254 | -66.5909 | 56.3553 | 0.04215 | -0.090727 | -0.013921 | 0.044618 | -0.020225 | 0.052737 | 0.058145 | -0.0068487 | 0.0021894 | 0.048222 | 0.094844 | 0.048641 | -66.5504 | -4.655 | -66.5766 | 56.3709 | 56.3257 | 56.4771 | -66.7963 | -66.5688 | -4.3723 | -66.6399 | 56.2672 | 56.4312 | 56.4024 | -67.0057 | -0.20542 | 0.015591 | 0.040483 | 0.014273 | 0.2197 | -0.029576 | 0.12181 | -0.41484 | -0.088064 | 0.022066 | -0.049069 | 0.36577 | 0.075961 | 0.047112 | 122.9618 | 122.9166 | 123.068 | 61.9358 | -123.1516 | 122.8581 | 123.0221 | 122.9933 | 62.2186 | -123.361
1217.2656 | 123.2574 | -66.5726 | 56.337 | 0.04215 | -0.089659 | -0.014989 | 0.04355 | -0.020225 | 0.054873 | 0.042884 | -0.0079177 | 0.0011204 | 0.048222 | 0.094844 | 0.049709 | -66.555 | -4.655 | -66.5812 | 56.3755 | 56.3211 | 56.4771 | -66.8009 | -66.5688 | -4.3632 | -66.6354 | 56.2626 | 56.4312 | 56.4024 | -67.0011 | -0.22831 | 0.03848 | 0.017594 | -0.008616 | 0.2197 | -0.015844 | 0.14012 | -0.42857 | -0.074331 | 0.003756 | -0.0628 | 0.36577 | 0.094272 | 0.065423 | 122.948 | 122.8937 | 123.0497 | 61.9175 | -123.1379 | 122.8352 | 123.0038 | 122.975 | 62.2094 | -123.3381
1218.2656 | 123.2391 | -66.5909 | 56.3324 | 0.04215 | -0.091796 | -0.011784 | 0.045687 | -0.020225 | 0.055941 | 0.058145 | -0.0089857 | 0.0021894 | 0.048222 | 0.093775 | 0.049709 | -66.555 | -4.6459 | -66.5812 | 56.3755 | 56.3303 | 56.4862 | -66.81 | -66.5688 | -4.3677 | -66.6262 | 56.2672 | 56.4221 | 56.4024 | -67.0057 | -0.21916 | 0.043058 | 0.035904 | 0.009694 | 0.22885 | -0.002108 | 0.15385 | -0.41484 | -0.065175 | 0.022066 | -0.035333 | 0.37951 | 0.089693 | 0.070001 | 122.9663 | 122.9212 | 123.0771 | 61.945 | -123.1424 | 122.8581 | 123.013 | 122.9933 | 62.2232 | -123.3381
1219.2656 | 123.2025 | -66.6367 | 56.3461 | 0.04215 | -0.090727 | -0.013921 | 0.045687 | -0.019157 | 0.053805 | 0.058145 | -0.0068487 | 0.0021894 | 0.047154 | 0.09698 | 0.049709 | -66.5504 | -4.6459 | -66.5903 | 56.3755 | 56.3257 | 56.4908 | -66.8146 | -66.578 | -4.3677 | -66.6354 | 56.2718 | 56.4267 | 56.407 | -67.0103 | -0.17796 | 0.029325 | 0.08626 | 0.046315 | 0.22428 | -0.02042 | 0.1447 | -0.37364 | -0.074329 | 0.058686 | 0.001287 | 0.37493 | 0.080538 | 0.060846 | 123.0121 | 122.9624 | 123.1275 | 61.9908 | -123.1607 | 122.9085 | 123.0633 | 123.0436 | 62.2689 | -123.3564
1220.2656 | 123.2346 | -66.5909 | 56.3416 | 0.057412 | -0.092864 | -0.010716 | 0.045687 | -0.020225 | 0.053805 | 0.042884 | -0.0079177 | 0.0011204 | 0.04929 | 0.093775 | 0.048641 | -66.5504 | -4.6459 | -66.5858 | 56.3755 | 56.3303 | 56.4908 | -66.8192 | -66.5688 | -4.3723 | -66.6354 | 56.2672 | 56.4267 | 56.4024 | -67.0103 | -0.22832 | 0.033902 | 0.040483 | 0.005116 | 0.23343 | -0.011264 | 0.14927 | -0.41942 | -0.074331 | 0.022066 | -0.04449 | 0.37493 | 0.085115 | 0.060845 | 122.9663 | 122.9212 | 123.0817 | 61.945 | -123.1608 | 122.8581 | 123.0175 | 122.9933 | 62.2186 | -123.3519
1221.2656 | 123.2208 | -66.6 | 56.337 | 0.026888 | -0.091796 | -0.013921 | 0.047824 | -0.020225 | 0.054873 | 0.058145 | -0.0079177 | 0.0021894 | 0.048222 | 0.092707 | 0.049709 | -66.5458 | -4.6505 | -66.5858 | 56.3709 | 56.3349 | 56.4908 | -66.81 | -66.5642 | -4.3632 | -66.6354 | 56.2626 | 56.4312 | 56.3978 | -67.0103 | -0.21 | 0.033902 | 0.054217 | 0.014272 | 0.22428 | -0.002107 | 0.15385 | -0.41026 | -0.074331 | 0.035801 | -0.035334 | 0.37493 | 0.094272 | 0.060844 | 122.9709 | 122.9349 | 123.0909 | 61.9496 | -123.147 | 122.8627 | 123.0313 | 122.9979 | 62.2369 | -123.3473
1222.2656 | 123.2117 | -66.5955 | 56.337 | 0.057412 | -0.091796 | -0.012852 | 0.045687 | -0.020225 | 0.055941 | 0.027623 | -0.0079177 | 0.0011204 | 0.048222 | 0.093775 | 0.049709 | -66.555 | -4.6505 | -66.5903 | 56.3709 | 56.3349 | 56.4862 | -66.8009 | -66.5734 | -4.3632 | -66.6399 | 56.2626 | 56.4312 | 56.3978 | -67.0103 | -0.20542 | 0.033902 | 0.040482 | 0.005116 | 0.21054 | -0.002107 | 0.14927 | -0.41484 | -0.074331 | 0.022065 | -0.044491 | 0.37035 | 0.094272 | 0.060844 | 122.9663 | 122.9303 | 123.0817 | 61.945 | -123.1379 | 122.8581 | 123.0267 | 122.9933 | 62.2323 | -123.3473
1223.2656 | 123.2162 | -66.6275 | 56.3232 | 0.04215 | -0.092864 | -0.013921 | 0.046755 | -0.022362 | 0.055941 | 0.042884 | -0.0068487 | 0.0011204 | 0.048222 | 0.094844 | 0.050777 | -66.555 | -4.6505 | -66.5766 | 56.38 | 56.3349 | 56.4817 | -66.8055 | -66.5688 | -4.3632 | -66.6308 | 56.2718 | 56.4221 | 56.3978 | -67.0057 | -0.17796 | 0.056792 | 0.072525 | 0.050894 | 0.22885 | 0.011626 | 0.15843 | -0.37822 | -0.051441 | 0.058687 | -0.00329 | 0.37493 | 0.098848 | 0.074577 | 123.0075 | 122.9624 | 123.1092 | 61.977 | -123.1287 | 122.8993 | 123.0496 | 123.0253 | 62.2644 | -123.329
1224.2656 | 123.2666 | -66.5863 | 56.3278 | 0.026888 | -0.091796 | -0.013921 | 0.045687 | -0.021293 | 0.054873 | 0.073406 | -0.0068487 | 0.0032574 | 0.048222 | 0.093775 | 0.049709 | -66.555 | -4.655 | -66.5812 | 56.3663 | 56.3257 | 56.4771 | -66.8009 | -66.5642 | -4.3494 | -66.6399 | 56.2718 | 56.4221 | 56.3932 | -67.0057 | -0.21458 | 0.038478 | 0.031327 | 0.005117 | 0.2197 | -0.00211 | 0.14927 | -0.41942 | -0.056019 | 0.022068 | -0.053646 | 0.36577 | 0.09427 | 0.065421 | 122.9526 | 122.912 | 123.0634 | 61.9313 | -123.1287 | 122.8581 | 123.0084 | 122.9795 | 62.2369 | -123.3335
1225.2656 | 123.2712 | -66.5771 | 56.3324 | 0.026888 | -0.091796 | -0.013921 | 0.045687 | -0.020225 | 0.054873 | 0.058145 | -0.0068487 | 0.0011204 | 0.047154 | 0.094844 | 0.050777 | -66.5641 | -4.655 | -66.5858 | 56.3617 | 56.2799 | 56.4771 | -66.7963 | -66.5734 | -4.3494 | -66.6354 | 56.2672 | 56.4267 | 56.3887 | -67.0103 | -0.21916 | 0.029323 | 0.013014 | -0.008617 | 0.21054 | -0.052476 | 0.14469 | -0.43315 | -0.065175 | 0.003754 | -0.058223 | 0.37493 | 0.094271 | 0.056265 | 122.9389 | 122.8571 | 123.0542 | 61.9221 | -123.1287 | 122.8444 | 123.0038 | 122.9658 | 62.2277 | -123.3427
1226.2656 | 123.2437 | -66.5909 | 56.3187 | 0.04215 | -0.092864 | -0.013921 | 0.046755 | -0.020225 | 0.054873 | 0.058145 | -0.0089857 | 0.0011204 | 0.048222 | 0.095912 | 0.049709 | -66.5504 | -4.655 | -66.5858 | 56.3663 | 56.2616 | 56.4771 | -66.7963 | -66.578 | -4.3494 | -66.6354 | 56.2672 | 56.4221 | 56.3932 | -67.0149 | -0.20542 | 0.047633 | 0.040483 | 0.005116 | 0.21054 | -0.05706 | 0.15843 | -0.424 | -0.051443 | 0.012909 | -0.04449 | 0.37951 | 0.10342 | 0.074576 | 122.9572 | 122.8525 | 123.068 | 61.9358 | -123.115 | 122.8581 | 123.013 | 122.9841 | 62.2415 | -123.3335
1227.2656 | 123.2254 | -66.6092 | 56.3278 | 0.04215 | -0.092864 | -0.012852 | 0.045687 | -0.019157 | 0.052737 | 0.027623 | -0.0068487 | 0.0021894 | 0.048222 | 0.094844 | 0.047572 | -66.5596 | -4.6505 | -66.5858 | 56.3663 | 56.2616 | 56.4725 | -66.8055 | -66.5688 | -4.3494 | -66.6399 | 56.2718 | 56.4267 | 56.3887 | -67.0103 | -0.19627 | 0.038478 | 0.049637 | 0.023427 | 0.2197 | -0.066215 | 0.14469 | -0.40111 | -0.056019 | 0.040377 | -0.030758 | 0.37035 | 0.098848 | 0.060842 | 122.9755 | 122.8708 | 123.0817 | 61.9587 | -123.1333 | 122.881 | 123.0359 | 122.9979 | 62.2598 | -123.3381
1228.2656 | 123.2529 | -66.6046 | 56.3324 | 0.026888 | -0.095001 | -0.012852 | 0.046755 | -0.020225 | 0.054873 | 0.027623 | -0.0079177 | 0.0021894 | 0.04929 | 0.093775 | 0.049709 | -66.555 | -4.655 | -66.5812 | 56.3663 | 56.2708 | 56.4771 | -66.8009 | -66.5734 | -4.3403 | -66.6399 | 56.2626 | 56.4221 | 56.3887 | -67.0103 | -0.19627 | 0.033901 | 0.049637 | 0.023427 | 0.2197 | -0.061634 | 0.14469 | -0.40569 | -0.069753 | 0.03122 | -0.035336 | 0.37035 | 0.089693 | 0.056265 | 122.9709 | 122.8754 | 123.0817 | 61.9496 | -123.1333 | 122.8673 | 123.0267 | 122.9933 | 62.2644 | -123.3427
1229.2656 | 123.2803 | -66.5909 | 56.3416 | 0.057412 | -0.095001 | -0.014989 | 0.046755 | -0.021293 | 0.055941 | 0.042884 | -0.0079177 | 0.0011204 | 0.048222 | 0.095912 | 0.049709 | -66.555 | -4.655 | -66.5812 | 56.3663 | 56.2799 | 56.4862 | -66.7963 | -66.5734 | -4.3448 | -66.6399 | 56.2672 | 56.4312 | 56.3841 | -67.0057 | -0.20542 | 0.024745 | 0.035904 | 0.009694 | 0.21512 | -0.061632 | 0.1447 | -0.41484 | -0.074331 | 0.017487 | -0.049069 | 0.36577 | 0.089694 | 0.04253 | 122.9572 | 122.8708 | 123.0771 | 61.9358 | -123.1379 | 122.8581 | 123.0221 | 122.975 | 62.246 | -123.3473
1230.2656 | 123.2574 | -66.5955 | 56.3461 | 0.04215 | -0.091796 | -0.013921 | 0.045687 | -0.022362 | 0.05701 | 0.042884 | -0.0089857 | 5.2373e-05 | 0.047154 | 0.094844 | 0.050777 | -66.555 | -4.655 | -66.5858 | 56.3526 | 56.2937 | 56.4771 | -66.8009 | -66.5688 | -4.3403 | -66.6491 | 56.2718 | 56.4267 | 56.3887 | -67.0057 | -0.20542 | 0.006433 | 0.040482 | 0.009694 | 0.21512 | -0.052473 | 0.13096 | -0.41026 | -0.074329 | 0.026644 | -0.053648 | 0.35662 | 0.080538 | 0.042532 | 122.948 | 122.8891 | 123.0726 | 61.9404 | -123.147 | 122.8673 | 123.0221 | 122.9841 | 62.2552 | -123.3519
1231.2656 | 123.2162 | -66.6321 | 56.369 | 0.04215 | -0.092864 | -0.012852 | 0.045687 | -0.020225 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.047154 | 0.094844 | 0.047572 | -66.5504 | -4.655 | -66.5858 | 56.3663 | 56.312 | 56.4771 | -66.7917 | -66.578 | -4.3265 | -66.6308 | 56.2626 | 56.4267 | 56.3841 | -67.0057 | -0.15964 | -0.002721 | 0.081682 | 0.046315 | 0.20596 | -0.057046 | 0.10807 | -0.37364 | -0.10637 | 0.054108 | 0.001288 | 0.37493 | 0.057649 | 0.015064 | 122.9984 | 122.9441 | 123.1092 | 61.977 | -123.1607 | 122.8947 | 123.0587 | 123.0162 | 62.3056 | -123.3747
1232.2656 | 123.2529 | -66.6046 | 56.3507 | 0.011626 | -0.093933 | -0.013921 | 0.04355 | -0.021293 | 0.054873 | 0.027623 | -0.0089857 | 0.0021894 | 0.048222 | 0.094844 | 0.048641 | -66.555 | -4.6505 | -66.5858 | 56.3617 | 56.3166 | 56.4771 | -66.8055 | -66.578 | -4.3311 | -66.6399 | 56.2672 | 56.4312 | 56.3932 | -67.0103 | -0.20085 | 0.011012 | 0.049637 | 0.018849 | 0.2197 | -0.034156 | 0.12638 | -0.40569 | -0.083486 | 0.026642 | -0.035336 | 0.37035 | 0.080539 | 0.042533 | 122.9663 | 122.9212 | 123.0817 | 61.9542 | -123.1562 | 122.8718 | 123.0359 | 122.9979 | 62.2735 | -123.361
1233.2656 | 123.2758 | -66.5863 | 56.3141 | 0.04215 | -0.093933 | -0.011784 | 0.045687 | -0.021293 | 0.055941 | 0.073406 | -0.0089857 | 0.0011204 | 0.047154 | 0.095912 | 0.049709 | -66.555 | -4.6596 | -66.5903 | 56.3755 | 56.3211 | 56.4817 | -66.81 | -66.5734 | -4.3311 | -66.6399 | 56.2626 | 56.4312 | 56.3887 | -67.0103 | -0.22374 | 0.061368 | 0.031327 | -0.004039 | 0.2197 | 0.007044 | 0.16758 | -0.424 | -0.051443 | 0.01291 | -0.053646 | 0.37035 | 0.11716 | 0.074575 | 122.9618 | 122.9074 | 123.068 | 61.9267 | -123.1241 | 122.8489 | 123.0176 | 122.975 | 62.2552 | -123.3244
1234.2656 | 123.2483 | -66.6 | 56.3141 | 0.026888 | -0.093933 | -0.011784 | 0.045687 | -0.021293 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.048222 | 0.095912 | 0.050777 | -66.555 | -4.6505 | -66.5812 | 56.3709 | 56.3349 | 56.4817 | -66.81 | -66.5734 | -4.3265 | -66.6354 | 56.2672 | 56.4221 | 56.3978 | -67.0103 | -0.21 | 0.05679 | 0.04506 | 0.01885 | 0.22885 | 0.020781 | 0.16758 | -0.41026 | -0.046865 | 0.026643 | -0.035334 | 0.37493 | 0.108 | 0.083732 | 122.9709 | 122.9349 | 123.0817 | 61.9496 | -123.1241 | 122.8673 | 123.0221 | 122.9979 | 62.2735 | -123.3244
1235.2656 | 123.2529 | -66.6229 | 56.3324 | 0.04215 | -0.093933 | -0.012852 | 0.045687 | -0.021293 | 0.054873 | 0.042884 | -0.0079177 | 0.0032574 | 0.047154 | 0.09698 | 0.049709 | -66.5641 | -4.655 | -66.5858 | 56.3709 | 56.3257 | 56.4862 | -66.8055 | -66.5734 | -4.3265 | -66.6399 | 56.2626 | 56.4267 | 56.4024 | -67.0057 | -0.18254 | 0.03848 | 0.058791 | 0.03716 | 0.2197 | -0.006687 | 0.15385 | -0.3828 | -0.069753 | 0.049531 | -0.017025 | 0.36577 | 0.094271 | 0.070001 | 122.9938 | 122.9486 | 123.1092 | 61.9679 | -123.1379 | 122.8856 | 123.0496 | 123.0253 | 62.2964 | -123.3381
1236.2656 | 123.2117 | -66.6229 | 56.3507 | 0.057412 | -0.092864 | -0.013921 | 0.046755 | -0.020225 | 0.055941 | 0.042884 | -0.0079177 | 0.0021894 | 0.047154 | 0.095912 | 0.049709 | -66.5596 | -4.655 | -66.5858 | 56.3663 | 56.3303 | 56.4771 | -66.81 | -66.5734 | -4.3219 | -66.6354 | 56.2672 | 56.4221 | 56.3978 | -67.0103 | -0.18712 | 0.01559 | 0.06337 | 0.03716 | 0.22428 | -0.020419 | 0.12638 | -0.38738 | -0.083486 | 0.049531 | -0.012446 | 0.37493 | 0.071382 | 0.047111 | 122.9892 | 122.9532 | 123.1 | 61.9679 | -123.1607 | 122.8901 | 123.045 | 123.0207 | 62.301 | -123.361
1237.2656 | 123.1888 | -66.6275 | 56.369 | 0.04215 | -0.093933 | -0.013921 | 0.046755 | -0.020225 | 0.054873 | 0.073406 | -0.0079177 | 0.0011204 | 0.046085 | 0.09698 | 0.050777 | -66.5504 | -4.6459 | -66.5812 | 56.3663 | 56.3303 | 56.4817 | -66.81 | -66.5688 | -4.3219 | -66.6399 | 56.2672 | 56.4221 | 56.4024 | -67.0103 | -0.18254 | -0.002721 | 0.077104 | 0.046315 | 0.22885 | -0.03873 | 0.11265 | -0.3828 | -0.1018 | 0.058687 | -0.012448 | 0.37035 | 0.053071 | 0.033379 | 122.9938 | 122.9578 | 123.1092 | 61.9816 | -123.1791 | 122.8947 | 123.0496 | 123.0299 | 62.3056 | -123.3793
1238.2656 | 123.2117 | -66.6046 | 56.3507 | 0.04215 | -0.093933 | -0.011784 | 0.046755 | -0.021293 | 0.054873 | 0.042884 | -0.0068487 | 0.0011204 | 0.047154 | 0.094844 | 0.049709 | -66.5596 | -4.6505 | -66.5812 | 56.3663 | 56.3303 | 56.4817 | -66.8146 | -66.578 | -4.3174 | -66.6491 | 56.2718 | 56.4221 | 56.3978 | -67.0057 | -0.21 | 0.01559 | 0.045059 | 0.023427 | 0.23343 | -0.020419 | 0.13096 | -0.40111 | -0.078907 | 0.026642 | -0.044493 | 0.35662 | 0.071382 | 0.047111 | 122.9709 | 122.9349 | 123.0863 | 61.9542 | -123.1653 | 122.8764 | 123.0267 | 123.0024 | 62.2873 | -123.3564
1239.2656 | 123.1384 | -66.6092 | 56.4011 | 0.04215 | -0.095001 | -0.012852 | 0.045687 | -0.020225 | 0.053805 | 0.058145 | -0.0079177 | 0.0021894 | 0.048222 | 0.09698 | 0.050777 | -66.5596 | -4.6505 | -66.5903 | 56.3709 | 56.3349 | 56.4817 | -66.81 | -66.5826 | -4.3174 | -66.6445 | 56.2672 | 56.4267 | 56.4024 | -67.0103 | -0.20085 | -0.030185 | 0.049637 | 0.018849 | 0.2197 | -0.066194 | 0.080608 | -0.40111 | -0.13384 | 0.026641 | -0.035337 | 0.36577 | 0.025606 | 0.001336 | 122.9801 | 122.9441 | 123.0909 | 61.9587 | -123.2111 | 122.8764 | 123.0359 | 123.0116 | 62.2918 | -123.4114
1240.2656 | 123.1338 | -66.6275 | 56.369 | 0.026888 | -0.096069 | -0.012852 | 0.045687 | -0.020225 | 0.053805 | 0.058145 | -0.0079177 | 5.2373e-05 | 0.047154 | 0.094844 | 0.049709 | -66.555 | -4.6459 | -66.5995 | 56.3709 | 56.3257 | 56.4817 | -66.81 | -66.5688 | -4.3082 | -66.6399 | 56.2672 | 56.4267 | 56.4024 | -67.0057 | -0.18254 | 0.001858 | 0.072525 | 0.028002 | 0.21054 | -0.043309 | 0.11265 | -0.37822 | -0.1018 | 0.058687 | -0.012448 | 0.36577 | 0.057649 | 0.033379 | 122.9984 | 122.9532 | 123.1092 | 61.9816 | -123.1791 | 122.8947 | 123.0542 | 123.0299 | 62.3193 | -123.3747
1241.2656 | 123.1476 | -66.6183 | 56.3553 | 0.026888 | -0.093933 | -0.014989 | 0.046755 | -0.020225 | 0.055941 | 0.058145 | -0.0089857 | 0.0032574 | 0.046085 | 0.094844 | 0.049709 | -66.5687 | -4.6505 | -66.5995 | 56.3709 | 56.3257 | 56.4908 | -66.81 | -66.5688 | -4.3174 | -66.6399 | 56.2672 | 56.4221 | 56.3978 | -67.0195 | -0.19169 | 0.015591 | 0.049635 | 0.018847 | 0.21054 | -0.029576 | 0.13554 | -0.40111 | -0.088064 | 0.049532 | -0.021603 | 0.37951 | 0.066804 | 0.042533 | 122.9892 | 122.9441 | 123.1092 | 61.9679 | -123.1653 | 122.8856 | 123.0404 | 123.0162 | 62.301 | -123.3747
1242.2656 | 123.1293 | -66.6458 | 56.3461 | 0.026888 | -0.093933 | -0.014989 | 0.045687 | -0.022362 | 0.053805 | 0.042884 | -0.0079177 | 0.0032574 | 0.048222 | 0.09698 | 0.048641 | -66.5596 | -4.6459 | -66.5858 | 56.38 | 56.3349 | 56.4862 | -66.8146 | -66.5826 | -4.3082 | -66.6399 | 56.2581 | 56.4221 | 56.3978 | -67.0103 | -0.16881 | 0.033904 | 0.086258 | 0.060048 | 0.22885 | -0.011262 | 0.14012 | -0.36449 | -0.088065 | 0.063262 | 0.005863 | 0.37035 | 0.07596 | 0.051689 | 123.0258 | 122.9807 | 123.1321 | 61.9999 | -123.1607 | 122.9039 | 123.0679 | 123.0436 | 62.3376 | -123.3564
1243.2656 | 123.2895 | -66.5726 | 56.337 | 0.057412 | -0.093933 | -0.012852 | 0.045687 | -0.020225 | 0.05701 | 0.073406 | -0.0068487 | 0.0011204 | 0.047154 | 0.09698 | 0.048641 | -66.5641 | -4.6459 | -66.5858 | 56.3663 | 56.3257 | 56.4862 | -66.8146 | -66.5871 | -4.3036 | -66.6445 | 56.2672 | 56.4221 | 56.3932 | -67.0149 | -0.24205 | 0.029323 | 0.008437 | -0.013194 | 0.22885 | -0.011265 | 0.14927 | -0.44231 | -0.069753 | -0.014559 | -0.071958 | 0.37035 | 0.085115 | 0.056266 | 122.9389 | 122.8983 | 123.0588 | 61.9267 | -123.1516 | 122.8398 | 122.9947 | 122.9658 | 62.2689 | -123.3519
1244.2656 | 122.9965 | -66.6687 | 56.369 | 0.04215 | -0.093933 | -0.012852 | 0.048892 | -0.021293 | 0.053805 | 0.042884 | -0.0079177 | 0.0032574 | 0.048222 | 0.094844 | 0.049709 | -66.5641 | -4.6413 | -66.5858 | 56.3709 | 56.3303 | 56.4862 | -66.81 | -66.5688 | -4.3036 | -66.6308 | 56.2672 | 56.4267 | 56.3978 | -67.0057 | -0.14134 | 0.001858 | 0.10457 | 0.082936 | 0.22428 | -0.03873 | 0.11723 | -0.33702 | -0.1018 | 0.099886 | 0.037909 | 0.37493 | 0.057649 | 0.0288 | 123.0396 | 122.999 | 123.1549 | 62.0274 | -123.1791 | 122.9359 | 123.0954 | 123.0665 | 62.3651 | -123.3747
1245.2656 | 123.2071 | -66.6138 | 56.3782 | 0.04215 | -0.096069 | -0.012852 | 0.045687 | -0.021293 | 0.054873 | 0.027623 | -0.0079177 | 0.0021894 | 0.047154 | 0.09698 | 0.050777 | -66.5596 | -4.6413 | -66.5858 | 56.3709 | 56.3303 | 56.4954 | -66.81 | -66.578 | -4.3036 | -66.6445 | 56.2718 | 56.4312 | 56.4024 | -67.0103 | -0.19627 | -0.007297 | 0.054215 | 0.028005 | 0.22428 | -0.047885 | 0.11723 | -0.39653 | -0.10637 | 0.035798 | -0.030759 | 0.36577 | 0.053073 | 0.024224 | 122.9846 | 122.9441 | 123.1092 | 61.9725 | -123.1882 | 122.8856 | 123.045 | 123.0162 | 62.3101 | -123.3885
1246.2656 | 123.1842 | -66.6367 | 56.3782 | 0.04215 | -0.096069 | -0.012852 | 0.044618 | -0.020225 | 0.054873 | 0.073406 | -0.0079177 | 0.0021894 | 0.047154 | 0.095912 | 0.050777 | -66.555 | -4.6459 | -66.5812 | 56.3663 | 56.3303 | 56.4862 | -66.7963 | -66.5826 | -4.3128 | -66.6445 | 56.2581 | 56.4312 | 56.3932 | -67.0103 | -0.15965 | -0.011876 | 0.081681 | 0.055471 | 0.21512 | -0.047885 | 0.10807 | -0.37364 | -0.12011 | 0.054107 | -0.007871 | 0.36577 | 0.053073 | 0.015067 | 123.003 | 122.9669 | 123.1229 | 61.9908 | -123.1745 | 122.8947 | 123.0679 | 123.0299 | 62.3239 | -123.3885
1247.2656 | 123.1522 | -66.6138 | 56.3736 | 0.04215 | -0.096069 | -0.012852 | 0.046755 | -0.022362 | 0.053805 | 0.042884 | -0.011122 | 0.0021894 | 0.046085 | 0.095912 | 0.049709 | -66.5641 | -4.6367 | -66.5858 | 56.3663 | 56.3211 | 56.4862 | -66.81 | -66.5734 | -4.3036 | -66.6399 | 56.2626 | 56.4267 | 56.3978 | -67.0149 | -0.19627 | -0.007298 | 0.049636 | 0.028005 | 0.22428 | -0.052465 | 0.11265 | -0.40111 | -0.11095 | 0.040376 | -0.02618 | 0.37493 | 0.053072 | 0.024223 | 122.9801 | 122.9349 | 123.1 | 61.9771 | -123.1836 | 122.8764 | 123.0404 | 123.0116 | 62.3101 | -123.3885
1248.2656 | 123.2666 | -66.6 | 56.3141 | 0.057412 | -0.093933 | -0.013921 | 0.046755 | -0.020225 | 0.055941 | 0.042884 | -0.0068487 | 0.0021894 | 0.047154 | 0.09698 | 0.049709 | -66.555 | -4.6367 | -66.5858 | 56.3617 | 56.3211 | 56.4771 | -66.8009 | -66.578 | -4.2945 | -66.6445 | 56.2581 | 56.4267 | 56.3932 | -67.0103 | -0.20085 | 0.047633 | 0.04506 | 0.014272 | 0.21512 | 0.007044 | 0.163 | -0.41026 | -0.056022 | 0.022065 | -0.044492 | 0.36577 | 0.11258 | 0.079154 | 122.9618 | 122.9212 | 123.0771 | 61.9633 | -123.115 | 122.8581 | 123.0267 | 122.9933 | 62.3056 | -123.3244
1249.2656 | 123.1934 | -66.6367 | 56.3873 | 0.04215 | -0.093933 | -0.012852 | 0.045687 | -0.020225 | 0.053805 | 0.058145 | -0.0089857 | 0.0011204 | 0.046085 | 0.095912 | 0.048641 | -66.555 | -4.6321 | -66.5858 | 56.3709 | 56.3303 | 56.4862 | -66.81 | -66.5688 | -4.2945 | -66.6445 | 56.2672 | 56.4267 | 56.3932 | -67.0103 | -0.17338 | -0.016452 | 0.081681 | 0.050893 | 0.22428 | -0.05704 | 0.09892 | -0.37364 | -0.12011 | 0.067843 | -0.007871 | 0.36577 | 0.039339 | 0.005912 | 123.0075 | 122.9669 | 123.1229 | 62.0045 | -123.1974 | 122.9039 | 123.0633 | 123.0299 | 62.3422 | -123.3976
1250.2656 | 123.1888 | -66.6412 | 56.3644 | 0.026888 | -0.095001 | -0.012852 | 0.045687 | -0.018088 | 0.053805 | 0.042884 | -0.0079177 | 0.0021894 | 0.046085 | 0.095912 | 0.049709 | -66.5596 | -4.6367 | -66.5949 | 56.3709 | 56.3303 | 56.4817 | -66.81 | -66.5826 | -4.2991 | -66.6354 | 56.2626 | 56.4312 | 56.3978 | -67.0103 | -0.16881 | 0.006436 | 0.08168 | 0.046313 | 0.21512 | -0.034152 | 0.11723 | -0.36907 | -0.1018 | 0.058684 | 0.005864 | 0.37493 | 0.066806 | 0.033378 | 123.0121 | 122.9715 | 123.1229 | 62.0045 | -123.1745 | 122.9039 | 123.0725 | 123.0391 | 62.3422 | -123.3747
1251.2656 | 123.1842 | -66.6138 | 56.3599 | 0.057412 | -0.095001 | -0.012852 | 0.046755 | -0.020225 | 0.055941 | 0.042884 | -0.0068487 | 0.0011204 | 0.047154 | 0.098049 | 0.049709 | -66.5641 | -4.6276 | -66.5903 | 56.3709 | 56.3211 | 56.4817 | -66.8055 | -66.578 | -4.2945 | -66.6399 | 56.2672 | 56.4358 | 56.3932 | -67.0103 | -0.19169 | 0.011014 | 0.049636 | 0.023427 | 0.21512 | -0.038732 | 0.12181 | -0.39653 | -0.092641 | 0.035798 | -0.02618 | 0.37035 | 0.075962 | 0.033378 | 122.9846 | 122.9349 | 123.0954 | 61.9862 | -123.1653 | 122.881 | 123.0496 | 123.007 | 62.3193 | -123.3702
1252.2656 | 123.175 | -66.6229 | 56.3782 | 0.04215 | -0.095001 | -0.012852 | 0.045687 | -0.019157 | 0.054873 | 0.058145 | -0.0079177 | 0.0021894 | 0.047154 | 0.098049 | 0.051845 | -66.5641 | -4.6184 | -66.5903 | 56.3663 | 56.3257 | 56.4725 | -66.8009 | -66.578 | -4.2991 | -66.6445 | 56.2626 | 56.4221 | 56.3932 | -67.0103 | -0.17796 | -0.011876 | 0.058791 | 0.032582 | 0.21054 | -0.052464 | 0.094339 | -0.38738 | -0.11553 | 0.044953 | -0.021604 | 0.36577 | 0.043916 | 0.015067 | 122.9892 | 122.9486 | 123.0954 | 62.0045 | -123.1791 | 122.8856 | 123.045 | 123.0162 | 62.3239 | -123.3885
1253.2656 | 123.2346 | -66.5863 | 56.3095 | 0.04215 | -0.093933 | -0.011784 | 0.045687 | -0.020225 | 0.053805 | 0.042884 | -0.0089857 | 0.0011204 | 0.046085 | 0.09698 | 0.050777 | -66.5641 | -4.6184 | -66.5858 | 56.3617 | 56.3074 | 56.4771 | -66.7963 | -66.5734 | -4.2945 | -66.6445 | 56.2672 | 56.4312 | 56.3887 | -67.0103 | -0.21 | 0.052211 | 0.02217 | 0.000539 | 0.21054 | -0.002115 | 0.16758 | -0.424 | -0.042287 | 0.01291 | -0.058225 | 0.36577 | 0.12174 | 0.079153 | 122.948 | 122.8937 | 123.0634 | 61.9679 | -123.1058 | 122.8535 | 123.0176 | 122.975 | 62.2918 | -123.3198
1254.2656 | 123.2162 | -66.6046 | 56.3736 | 0.057412 | -0.096069 | -0.013921 | 0.045687 | -0.021293 | 0.053805 | 0.073406 | -0.0068487 | 0.0011204 | 0.046085 | 0.09698 | 0.049709 | -66.555 | -4.623 | -66.5949 | 56.3663 | 56.3028 | 56.4817 | -66.8055 | -66.5826 | -4.2991 | -66.6399 | 56.2672 | 56.4404 | 56.3887 | -67.0149 | -0.20085 | -0.007298 | 0.049637 | 0.009692 | 0.21054 | -0.070781 | 0.10807 | -0.41027 | -0.10637 | 0.022063 | -0.035336 | 0.37493 | 0.066808 | 0.015066 | 122.9709 | 122.9074 | 123.0863 | 61.9816 | -123.1791 | 122.8718 | 123.045 | 122.9933 | 62.3056 | -123.3885
1255.2656 | 123.1934 | -66.6046 | 56.3873 | 0.072674 | -0.097138 | -0.013921 | 0.046755 | -0.020225 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.047154 | 0.095912 | 0.050777 | -66.5596 | -4.6092 | -66.5903 | 56.3663 | 56.3257 | 56.4817 | -66.81 | -66.5826 | -4.3036 | -66.6399 | 56.2718 | 56.4267 | 56.3978 | -67.0195 | -0.20543 | -0.021031 | 0.045059 | 0.014271 | 0.2197 | -0.061619 | 0.094341 | -0.41484 | -0.11553 | 0.022063 | -0.035336 | 0.37951 | 0.039339 | 0.01049 | 122.9709 | 122.9303 | 123.0863 | 61.9954 | -123.1974 | 122.8764 | 123.0313 | 123.0024 | 62.301 | -123.4068
1256.2656 | 123.1705 | -66.6183 | 56.369 | 0.026888 | -0.095001 | -0.013921 | 0.044618 | -0.021293 | 0.054873 | 0.073406 | -0.0089857 | 0.0032574 | 0.047154 | 0.09698 | 0.050777 | -66.5641 | -4.6092 | -66.5903 | 56.3663 | 56.3257 | 56.4817 | -66.8055 | -66.578 | -4.2991 | -66.6399 | 56.2581 | 56.4312 | 56.3932 | -67.0149 | -0.18711 | -0.002721 | 0.054213 | 0.028004 | 0.21512 | -0.043309 | 0.11265 | -0.39653 | -0.11095 | 0.040375 | -0.021603 | 0.37493 | 0.062228 | 0.024222 | 122.9846 | 122.9441 | 123.1 | 62.0091 | -123.1745 | 122.8764 | 123.0496 | 123.0116 | 62.3193 | -123.3839
1257.2656 | 123.1705 | -66.6321 | 56.3828 | 0.04215 | -0.097138 | -0.012852 | 0.046755 | -0.022362 | 0.05701 | 0.042884 | -0.0079177 | 0.0032574 | 0.047154 | 0.094844 | 0.048641 | -66.5641 | -4.5955 | -66.5858 | 56.3709 | 56.3349 | 56.4862 | -66.8146 | -66.5826 | -4.2899 | -66.6399 | 56.2581 | 56.4312 | 56.3978 | -67.0149 | -0.18254 | -0.011874 | 0.067946 | 0.046315 | 0.22885 | -0.047883 | 0.1035 | -0.3828 | -0.12469 | 0.049529 | -0.00787 | 0.37493 | 0.048496 | 0.015068 | 123.003 | 122.9669 | 123.1183 | 62.0366 | -123.1974 | 122.8901 | 123.0633 | 123.0299 | 62.3422 | -123.3976
1258.2656 | 123.143 | -66.6275 | 56.3644 | 0.057412 | -0.096069 | -0.012852 | 0.044618 | -0.020225 | 0.053805 | 0.058145 | -0.0079177 | 0.0032574 | 0.046085 | 0.09698 | 0.049709 | -66.5641 | -4.6047 | -66.5949 | 56.3709 | 56.3257 | 56.4862 | -66.81 | -66.5871 | -4.2945 | -66.6399 | 56.2581 | 56.4267 | 56.4024 | -67.0103 | -0.18254 | 0.006436 | 0.063368 | 0.03258 | 0.21512 | -0.038731 | 0.12181 | -0.3828 | -0.10638 | 0.040372 | -0.012448 | 0.37035 | 0.062227 | 0.037957 | 122.9984 | 122.9532 | 123.1138 | 62.0228 | -123.1745 | 122.8856 | 123.0542 | 123.0299 | 62.333 | -123.3747
1259.2656 | 123.1705 | -66.6412 | 56.3736 | 0.026888 | -0.097138 | -0.013921 | 0.045687 | -0.022362 | 0.055941 | 0.073406 | -0.0089857 | 0.0032574 | 0.047154 | 0.095912 | 0.050777 | -66.5687 | -4.5909 | -66.5903 | 56.3755 | 56.3257 | 56.4771 | -66.81 | -66.578 | -4.2945 | -66.6399 | 56.2626 | 56.4358 | 56.3978 | -67.0103 | -0.16881 | 0.001859 | 0.072523 | 0.050892 | 0.2197 | -0.047886 | 0.1035 | -0.36907 | -0.11095 | 0.063263 | 0.001285 | 0.37035 | 0.062229 | 0.024223 | 123.0167 | 122.9669 | 123.1183 | 62.0503 | -123.1836 | 122.9039 | 123.0771 | 123.0391 | 62.3468 | -123.3839
1260.2656 | 123.1293 | -66.6321 | 56.4056 | 0.026888 | -0.096069 | -0.013921 | 0.047824 | -0.020225 | 0.054873 | 0.042884 | -0.0079177 | 0.0032574 | 0.045017 | 0.095912 | 0.050777 | -66.5596 | -4.5726 | -66.5903 | 56.3709 | 56.3303 | 56.4817 | -66.81 | -66.578 | -4.2945 | -66.6445 | 56.2626 | 56.4267 | 56.3932 | -67.0149 | -0.17796 | -0.034763 | 0.072525 | 0.041737 | 0.2197 | -0.075351 | 0.07603 | -0.3828 | -0.143 | 0.054108 | -0.012449 | 0.37035 | 0.021028 | -0.012399 | 123.003 | 122.9624 | 123.1138 | 62.0595 | -123.2157 | 122.8947 | 123.0587 | 123.0253 | 62.3376 | -123.4205
1261.2656 | 123.143 | -66.6412 | 56.3782 | 0.04215 | -0.095001 | -0.014989 | 0.046755 | -0.022362 | 0.055941 | 0.027623 | -0.0068487 | 0.0043254 | 0.047154 | 0.098049 | 0.050777 | -66.5687 | -4.5726 | -66.5903 | 56.3709 | 56.3349 | 56.4771 | -66.81 | -66.578 | -4.3036 | -66.6399 | 56.2672 | 56.4267 | 56.407 | -67.0195 | -0.16881 | -0.007297 | 0.072523 | 0.050892 | 0.2197 | -0.043306 | 0.098917 | -0.37822 | -0.11095 | 0.063263 | 0.001285 | 0.37951 | 0.048494 | 0.028802 | 123.0121 | 122.9761 | 123.1183 | 62.0686 | -123.1882 | 122.9085 | 123.0679 | 123.0482 | 62.3376 | -123.3976
1262.2656 | 123.1338 | -66.6138 | 56.3919 | 0.057412 | -0.096069 | -0.012852 | 0.047824 | -0.020225 | 0.05701 | 0.058145 | -0.0079177 | 5.2373e-05 | 0.045017 | 0.098049 | 0.048641 | -66.5641 | -4.5726 | -66.5858 | 56.3709 | 56.3211 | 56.4817 | -66.8146 | -66.5826 | -4.2991 | -66.6491 | 56.2581 | 56.4312 | 56.3978 | -67.0103 | -0.20085 | -0.02103 | 0.049636 | 0.028005 | 0.22885 | -0.070776 | 0.089763 | -0.39653 | -0.13384 | 0.031219 | -0.035337 | 0.36119 | 0.03934 | 0.005912 | 122.9846 | 122.9349 | 123.0954 | 62.0412 | -123.2065 | 122.8718 | 123.045 | 123.0116 | 62.3147 | -123.4022
1263.2656 | 123.2666 | -66.6046 | 56.3095 | 0.026888 | -0.095001 | -0.013921 | 0.046755 | -0.02343 | 0.054873 | 0.058145 | -0.0089857 | 0.0043254 | 0.047154 | 0.09698 | 0.048641 | -66.5641 | -4.5543 | -66.5903 | 56.3709 | 56.3257 | 56.4817 | -66.8009 | -66.5826 | -4.2899 | -66.6399 | 56.2626 | 56.4267 | 56.3932 | -67.0149 | -0.19627 | 0.061368 | 0.04048 | 0.014271 | 0.21054 | 0.016201 | 0.17216 | -0.41027 | -0.046865 | 0.022063 | -0.035336 | 0.37493 | 0.11716 | 0.083732 | 122.9755 | 122.9303 | 123.0863 | 62.0503 | -123.1104 | 122.8673 | 123.0313 | 122.9979 | 62.3147 | -123.3244
1264.2656 | 123.1247 | -66.6321 | 56.3873 | 0.04215 | -0.096069 | -0.011784 | 0.046755 | -0.02343 | 0.05701 | 0.088667 | -0.010054 | 0.0021894 | 0.048222 | 0.095912 | 0.049709 | -66.5641 | -4.5497 | -66.5903 | 56.3709 | 56.3303 | 56.4862 | -66.81 | -66.5826 | -4.2899 | -66.6399 | 56.2626 | 56.4267 | 56.3932 | -67.0057 | -0.17796 | -0.016452 | 0.067946 | 0.041737 | 0.2197 | -0.05704 | 0.09892 | -0.37364 | -0.12468 | 0.049529 | -0.00787 | 0.36577 | 0.039339 | 0.005912 | 123.003 | 122.9624 | 123.1183 | 62.0824 | -123.1974 | 122.8947 | 123.0587 | 123.0253 | 62.3422 | -123.3931
1265.2656 | 123.2483 | -66.5817 | 56.3644 | 0.057412 | -0.095001 | -0.014989 | 0.044618 | -0.021293 | 0.054873 | 0.042884 | -0.011122 | 0.0021894 | 0.047154 | 0.098049 | 0.049709 | -66.555 | -4.5406 | -66.5949 | 56.3663 | 56.3257 | 56.4862 | -66.81 | -66.5871 | -4.2853 | -66.6491 | 56.2626 | 56.4221 | 56.4024 | -67.0195 | -0.22831 | 0.001857 | 0.026749 | -0.013196 | 0.21512 | -0.038731 | 0.12181 | -0.43773 | -0.1018 | -0.005404 | -0.067381 | 0.37035 | 0.057649 | 0.037957 | 122.948 | 122.9074 | 123.068 | 62.0412 | -123.1745 | 122.8444 | 123.0038 | 122.9841 | 62.2964 | -123.3839
1266.2656 | 123.2758 | -66.5817 | 56.3644 | 0.057412 | -0.095001 | -0.012852 | 0.045687 | -0.020225 | 0.054873 | 0.073406 | -0.0079177 | 0.0011204 | 0.045017 | 0.09698 | 0.049709 | -66.5687 | -4.5314 | -66.5903 | 56.3617 | 56.3211 | 56.4954 | -66.81 | -66.5826 | -4.2945 | -66.6491 | 56.2626 | 56.4312 | 56.3978 | -67.0195 | -0.22831 | -0.002721 | 0.013014 | -0.008617 | 0.2197 | -0.04331 | 0.13097 | -0.43773 | -0.1018 | -0.000825 | -0.067381 | 0.37035 | 0.066806 | 0.033378 | 122.9434 | 122.9029 | 123.0771 | 62.0503 | -123.1745 | 122.8444 | 123.013 | 122.9795 | 62.2873 | -123.3839
1267.2656 | 123.2254 | -66.5771 | 56.3736 | 0.057412 | -0.098206 | -0.014989 | 0.045687 | -0.021293 | 0.053805 | 0.058145 | -0.010054 | 0.0021894 | 0.047154 | 0.09698 | 0.049709 | -66.5641 | -4.5268 | -66.5949 | 56.3709 | 56.3211 | 56.4817 | -66.81 | -66.578 | -4.2853 | -66.6399 | 56.2626 | 56.4358 | 56.3978 | -67.0103 | -0.23289 | -0.002719 | 0.013014 | -0.017774 | 0.21512 | -0.052465 | 0.10807 | -0.43315 | -0.11095 | -0.000824 | -0.062802 | 0.37035 | 0.062229 | 0.024223 | 122.948 | 122.8983 | 123.0588 | 62.0503 | -123.1836 | 122.8398 | 123.013 | 122.975 | 62.2918 | -123.3839
1268.2656 | 123.1613 | -66.6275 | 56.3828 | 0.057412 | -0.096069 | -0.013921 | 0.045687 | -0.021293 | 0.054873 | 0.058145 | -0.0089857 | 0.0011204 | 0.047154 | 0.09698 | 0.050777 | -66.5687 | -4.5177 | -66.5949 | 56.3663 | 56.3349 | 56.4862 | -66.81 | -66.5871 | -4.2853 | -66.6399 | 56.2581 | 56.4312 | 56.3932 | -67.0103 | -0.18254 | -0.016453 | 0.05879 | 0.03258 | 0.21512 | -0.047883 | 0.1035 | -0.3828 | -0.12469 | 0.040372 | -0.012448 | 0.37035 | 0.048496 | 0.01049 | 122.9938 | 122.9624 | 123.1138 | 62.1098 | -123.1928 | 122.8856 | 123.0587 | 123.0207 | 62.3422 | -123.3931
1269.2656 | 123.2025 | -66.6046 | 56.3644 | 0.057412 | -0.096069 | -0.013921 | 0.045687 | -0.021293 | 0.054873 | 0.058145 | -0.0089857 | 0.0032574 | 0.046085 | 0.099117 | 0.049709 | -66.5687 | -4.4994 | -66.5858 | 56.3709 | 56.3349 | 56.4908 | -66.81 | -66.578 | -4.2899 | -66.6399 | 56.2626 | 56.4267 | 56.3887 | -67.0195 | -0.20543 | 0.006436 | 0.035902 | 0.018849 | 0.22428 | -0.029573 | 0.12639 | -0.41484 | -0.1018 | 0.026642 | -0.035336 | 0.37951 | 0.062227 | 0.024221 | 122.9755 | 122.9395 | 123.0954 | 62.1053 | -123.1745 | 122.8673 | 123.0313 | 122.9933 | 62.3147 | -123.3839
1270.2656 | 123.2437 | -66.5909 | 56.3644 | 0.057412 | -0.097138 | -0.014989 | 0.045687 | -0.020225 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.046085 | 0.098049 | 0.049709 | -66.5687 | -4.4902 | -66.5858 | 56.3663 | 56.3303 | 56.4771 | -66.81 | -66.5826 | -4.2899 | -66.6491 | 56.2626 | 56.4358 | 56.3932 | -67.0195 | -0.21916 | 0.001857 | 0.022169 | 0.005116 | 0.22428 | -0.034152 | 0.11265 | -0.42858 | -0.1018 | 0.00833 | -0.058226 | 0.37035 | 0.071384 | 0.0288 | 122.9572 | 122.9212 | 123.068 | 62.1007 | -123.1745 | 122.8535 | 123.0267 | 122.9841 | 62.301 | -123.3839
1271.2656 | 123.2712 | -66.5771 | 56.3644 | 0.04215 | -0.096069 | -0.011784 | 0.046755 | -0.02343 | 0.054873 | 0.042884 | -0.0068487 | 0.0032574 | 0.046085 | 0.095912 | 0.048641 | -66.5687 | -4.4902 | -66.5903 | 56.3755 | 56.3257 | 56.4817 | -66.81 | -66.578 | -4.2807 | -66.6445 | 56.2672 | 56.4267 | 56.3932 | -67.0149 | -0.23289 | 0.011014 | 0.008436 | -0.013195 | 0.2197 | -0.038731 | 0.11723 | -0.43773 | -0.097219 | -0.000824 | -0.067381 | 0.37035 | 0.062227 | 0.0288 | 122.9526 | 122.9029 | 123.0588 | 62.0869 | -123.1745 | 122.8444 | 123.0038 | 122.9704 | 62.2964 | -123.3793
1272.2656 | 123.2941 | -66.5726 | 56.3232 | 0.026888 | -0.097138 | -0.013921 | 0.045687 | -0.020225 | 0.054873 | 0.042884 | -0.0079177 | 0.0011204 | 0.047154 | 0.098049 | 0.050777 | -66.5733 | -4.481 | -66.5949 | 56.3709 | 56.3211 | 56.4771 | -66.81 | -66.5826 | -4.2807 | -66.6445 | 56.2626 | 56.4221 | 56.3932 | -67.0195 | -0.23747 | 0.047635 | -0.000719 | -0.022351 | 0.21512 | -0.002111 | 0.15385 | -0.44689 | -0.060598 | -0.00998 | -0.071958 | 0.37493 | 0.098848 | 0.069999 | 122.9434 | 122.8937 | 123.0497 | 62.0915 | -123.1333 | 122.8352 | 122.9947 | 122.9658 | 62.2918 | -123.3427
1273.2656 | 123.2071 | -66.5955 | 56.3324 | 0.057412 | -0.097138 | -0.013921 | 0.044618 | -0.021293 | 0.05701 | 0.058145 | -0.0089857 | 0.0032574 | 0.047154 | 0.09698 | 0.048641 | -66.5733 | -4.4536 | -66.5949 | 56.3663 | 56.3257 | 56.4771 | -66.81 | -66.578 | -4.2762 | -66.6537 | 56.2581 | 56.4312 | 56.3978 | -67.0149 | -0.21458 | 0.033901 | 0.022169 | 0.000537 | 0.21512 | -0.006687 | 0.14469 | -0.41942 | -0.074332 | 0.017487 | -0.058227 | 0.36119 | 0.09885 | 0.065422 | 122.9618 | 122.9212 | 123.0726 | 62.1419 | -123.1424 | 122.8535 | 123.0267 | 122.9933 | 62.3193 | -123.3473
1274.2656 | 123.2712 | -66.568 | 56.3324 | 0.057412 | -0.096069 | -0.014989 | 0.044618 | -0.022362 | 0.054873 | 0.058145 | -0.010054 | 0.0021894 | 0.046085 | 0.099117 | 0.048641 | -66.5733 | -4.4536 | -66.5949 | 56.3663 | 56.3211 | 56.4862 | -66.8146 | -66.5871 | -4.2762 | -66.6445 | 56.2626 | 56.4267 | 56.3932 | -67.0149 | -0.24663 | 0.033901 | -0.005297 | -0.026929 | 0.2197 | -0.011266 | 0.15385 | -0.44689 | -0.069753 | -0.019137 | -0.076536 | 0.37035 | 0.094271 | 0.060844 | 122.9343 | 122.8891 | 123.0542 | 62.1144 | -123.147 | 122.8306 | 122.9947 | 122.9612 | 62.2918 | -123.3473
1275.2656 | 123.2666 | -66.6 | 56.3644 | 0.057412 | -0.097138 | -0.013921 | 0.045687 | -0.021293 | 0.055941 | 0.073406 | -0.010054 | 0.0011204 | 0.046085 | 0.098049 | 0.048641 | -66.5687 | -4.4353 | -66.5903 | 56.3709 | 56.3257 | 56.4771 | -66.8009 | -66.5826 | -4.2853 | -66.6491 | 56.2626 | 56.4221 | 56.3932 | -67.0195 | -0.20085 | 0.006436 | 0.031325 | 0.009694 | 0.21054 | -0.038731 | 0.11265 | -0.41942 | -0.1018 | 0.017486 | -0.04907 | 0.37035 | 0.057649 | 0.0288 | 122.9709 | 122.9257 | 123.0771 | 62.1648 | -123.1653 | 122.8627 | 123.0221 | 122.9933 | 62.3147 | -123.3839
1276.2656 | 123.2483 | -66.5634 | 56.3553 | 0.04215 | -0.098206 | -0.013921 | 0.045687 | -0.022362 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.046085 | 0.09698 | 0.049709 | -66.5687 | -4.4307 | -66.5949 | 56.3709 | 56.312 | 56.4771 | -66.8055 | -66.5826 | -4.2807 | -66.6445 | 56.2626 | 56.4221 | 56.3841 | -67.0149 | -0.24204 | 0.015591 | -0.005296 | -0.031506 | 0.21054 | -0.043313 | 0.12181 | -0.45146 | -0.092642 | -0.019135 | -0.081113 | 0.37035 | 0.066804 | 0.028797 | 122.9343 | 122.8754 | 123.0405 | 62.1327 | -123.1607 | 122.8261 | 122.9855 | 122.9475 | 62.2827 | -123.3702
1277.2656 | 123.2849 | -66.5909 | 56.3644 | 0.04215 | -0.096069 | -0.014989 | 0.04355 | -0.022362 | 0.055941 | 0.058145 | -0.0089857 | 5.2373e-05 | 0.047154 | 0.099117 | 0.050777 | -66.5779 | -4.4169 | -66.5949 | 56.3617 | 56.3211 | 56.4771 | -66.81 | -66.5871 | -4.2899 | -66.6491 | 56.2672 | 56.4267 | 56.3887 | -67.0195 | -0.21916 | -0.002721 | 0.013012 | -0.004041 | 0.21512 | -0.04331 | 0.11265 | -0.42858 | -0.097219 | 0.003751 | -0.058226 | 0.37035 | 0.062227 | 0.024221 | 122.9526 | 122.912 | 123.068 | 62.1739 | -123.1745 | 122.8581 | 123.0175 | 122.9795 | 62.301 | -123.3839
1278.2656 | 123.2849 | -66.5863 | 56.3461 | 0.057412 | -0.097138 | -0.013921 | 0.044618 | -0.02343 | 0.055941 | 0.058145 | -0.011122 | 0.0021894 | 0.045017 | 0.098049 | 0.048641 | -66.5687 | -4.4215 | -66.5949 | 56.3571 | 56.3211 | 56.4771 | -66.8055 | -66.578 | -4.2807 | -66.6445 | 56.2626 | 56.4267 | 56.3932 | -67.0195 | -0.21916 | 0.011012 | 0.017592 | -0.008618 | 0.21054 | -0.024999 | 0.13096 | -0.43315 | -0.083486 | 0.008332 | -0.058225 | 0.37493 | 0.080538 | 0.047111 | 122.9434 | 122.9074 | 123.0634 | 62.1648 | -123.1516 | 122.8489 | 123.013 | 122.9795 | 62.3056 | -123.3656
1279.2656 | 123.23 | -66.5909 | 56.337 | 0.057412 | -0.097138 | -0.013921 | 0.045687 | -0.02343 | 0.054873 | 0.073406 | -0.0079177 | 0.0011204 | 0.046085 | 0.099117 | 0.048641 | -66.5641 | -4.4124 | -66.5949 | 56.3663 | 56.3211 | 56.4771 | -66.81 | -66.5871 | -4.2762 | -66.6491 | 56.2672 | 56.4267 | 56.3887 | -67.0195 | -0.21916 | 0.029323 | 0.026747 | -0.004041 | 0.21512 | -0.015844 | 0.14012 | -0.42858 | -0.069753 | 0.003751 | -0.058226 | 0.37035 | 0.089693 | 0.051687 | 122.9572 | 122.912 | 123.068 | 62.1785 | -123.147 | 122.8581 | 123.0175 | 122.9795 | 62.3147 | -123.3564
1280.2656 | 123.23 | -66.6183 | 56.3507 | 0.04215 | -0.097138 | -0.014989 | 0.044618 | -0.020225 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.046085 | 0.098049 | 0.049709 | -66.5687 | -4.3941 | -66.5995 | 56.3663 | 56.3303 | 56.4771 | -66.81 | -66.5871 | -4.2807 | -66.6445 | 56.2581 | 56.4221 | 56.3932 | -67.0103 | -0.19169 | 0.01559 | 0.049635 | 0.018847 | 0.21054 | -0.020419 | 0.12638 | -0.39195 | -0.092643 | 0.031217 | -0.026182 | 0.36577 | 0.071382 | 0.042533 | 122.9846 | 122.9486 | 123.0954 | 62.2243 | -123.1607 | 122.8764 | 123.0404 | 123.0116 | 62.3376 | -123.361
1281.2656 | 123.2895 | -66.5817 | 56.3232 | 0.057412 | -0.097138 | -0.013921 | 0.044618 | -0.02343 | 0.055941 | 0.088667 | -0.0089857 | 0.0021894 | 0.047154 | 0.099117 | 0.049709 | -66.5687 | -4.3895 | -66.5949 | 56.3617 | 56.3211 | 56.4817 | -66.81 | -66.5871 | -4.2762 | -66.6445 | 56.2581 | 56.4267 | 56.3932 | -67.0195 | -0.22831 | 0.038478 | 0.013014 | -0.013196 | 0.21512 | -0.002111 | 0.15843 | -0.43773 | -0.065177 | -0.005404 | -0.062803 | 0.37493 | 0.10343 | 0.069999 | 122.9434 | 122.9029 | 123.0634 | 62.1923 | -123.1333 | 122.8398 | 123.0084 | 122.975 | 62.3056 | -123.3427
1282.2656 | 123.3261 | -66.5863 | 56.3187 | 0.057412 | -0.096069 | -0.014989 | 0.045687 | -0.022362 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.046085 | 0.099117 | 0.048641 | -66.5687 | -4.3803 | -66.5903 | 56.3617 | 56.3166 | 56.4862 | -66.81 | -66.5917 | -4.2853 | -66.6445 | 56.2581 | 56.4267 | 56.3932 | -67.0195 | -0.22374 | 0.043055 | 0.017592 | -0.004039 | 0.2197 | -0.002113 | 0.16758 | -0.43315 | -0.0606 | -0.005405 | -0.058225 | 0.37493 | 0.108 | 0.074576 | 122.948 | 122.9029 | 123.0726 | 62.206 | -123.1287 | 122.8444 | 123.013 | 122.9795 | 62.301 | -123.3381
1283.2656 | 123.2483 | -66.5955 | 56.3461 | 0.072674 | -0.096069 | -0.013921 | 0.045687 | -0.022362 | 0.054873 | 0.042884 | -0.0068487 | 0.0011204 | 0.048222 | 0.098049 | 0.048641 | -66.5733 | -4.3666 | -66.5949 | 56.3663 | 56.3257 | 56.4725 | -66.81 | -66.5826 | -4.2716 | -66.6491 | 56.2626 | 56.4312 | 56.3841 | -67.0195 | -0.21458 | 0.020168 | 0.022169 | 0.000537 | 0.21512 | -0.02042 | 0.12638 | -0.424 | -0.083486 | 0.012908 | -0.053648 | 0.37035 | 0.085117 | 0.037953 | 122.9618 | 122.9212 | 123.068 | 62.2289 | -123.1562 | 122.8581 | 123.0267 | 122.9795 | 62.3239 | -123.3656
1284.2656 | 123.2712 | -66.5955 | 56.3599 | 0.04215 | -0.097138 | -0.014989 | 0.045687 | -0.022362 | 0.053805 | 0.073406 | -0.0089857 | 0.0021894 | 0.047154 | 0.098049 | 0.048641 | -66.5687 | -4.3666 | -66.5949 | 56.3571 | 56.3074 | 56.4771 | -66.81 | -66.5871 | -4.2807 | -66.6491 | 56.2672 | 56.4267 | 56.3887 | -67.0195 | -0.21458 | -0.002721 | 0.026747 | 0.000537 | 0.21512 | -0.052469 | 0.11723 | -0.424 | -0.092641 | 0.008329 | -0.053648 | 0.37035 | 0.066805 | 0.028799 | 122.9526 | 122.9029 | 123.0726 | 62.2289 | -123.1699 | 122.8627 | 123.0221 | 122.9841 | 62.3147 | -123.3793
1285.2656 | 123.262 | -66.5863 | 56.369 | 0.057412 | -0.098206 | -0.014989 | 0.045687 | -0.021293 | 0.055941 | 0.012362 | -0.0079177 | 0.0011204 | 0.048222 | 0.098049 | 0.050777 | -66.5733 | -4.3528 | -66.5903 | 56.3571 | 56.2982 | 56.4771 | -66.8055 | -66.578 | -4.2716 | -66.6537 | 56.2626 | 56.4312 | 56.3841 | -67.0149 | -0.21916 | -0.011877 | 0.013014 | -0.004039 | 0.21512 | -0.070783 | 0.10807 | -0.42858 | -0.10637 | 0.008332 | -0.067382 | 0.36119 | 0.062228 | 0.015064 | 122.9434 | 122.8845 | 123.0634 | 62.2335 | -123.1745 | 122.8489 | 123.0176 | 122.9704 | 62.3147 | -123.3839
1286.2656 | 123.1842 | -66.6183 | 56.337 | 0.04215 | -0.097138 | -0.012852 | 0.04355 | -0.02343 | 0.055941 | 0.058145 | -0.0079177 | 0.0011204 | 0.046085 | 0.099117 | 0.048641 | -66.5733 | -4.3528 | -66.5949 | 56.3617 | 56.2937 | 56.4725 | -66.8009 | -66.5826 | -4.2716 | -66.6445 | 56.2626 | 56.4312 | 56.3887 | -67.0286 | -0.18254 | 0.024745 | 0.045057 | 0.023425 | 0.20596 | -0.043318 | 0.13554 | -0.41027 | -0.074331 | 0.035796 | -0.026182 | 0.38409 | 0.094272 | 0.051687 | 122.9801 | 122.912 | 123.0909 | 62.2655 | -123.1379 | 122.881 | 123.0496 | 123.007 | 62.3468 | -123.3656
1287.2656 | 123.23 | -66.6092 | 56.3278 | 0.04215 | -0.097138 | -0.014989 | 0.045687 | -0.021293 | 0.055941 | 0.027623 | -0.0068487 | 0.0032574 | 0.047154 | 0.10019 | 0.048641 | -66.5733 | -4.3345 | -66.5949 | 56.3571 | 56.3166 | 56.4725 | -66.8146 | -66.5917 | -4.2624 | -66.6491 | 56.2626 | 56.4221 | 56.3887 | -67.0195 | -0.20543 | 0.029322 | 0.035902 | 0.01427 | 0.2197 | -0.011268 | 0.14469 | -0.41027 | -0.065176 | 0.017483 | -0.039915 | 0.37035 | 0.09427 | 0.060842 | 122.9663 | 122.9257 | 123.0817 | 62.2747 | -123.1424 | 122.8718 | 123.0313 | 122.9979 | 62.3468 | -123.3473
1288.2656 | 123.262 | -66.5955 | 56.3599 | 0.04215 | -0.097138 | -0.012852 | 0.045687 | -0.022362 | 0.05701 | 0.058145 | -0.0089857 | 0.0021894 | 0.045017 | 0.099117 | 0.048641 | -66.5733 | -4.33 | -66.5995 | 56.3709 | 56.3211 | 56.4862 | -66.8055 | -66.5871 | -4.2533 | -66.6491 | 56.2626 | 56.4267 | 56.3887 | -67.0149 | -0.21 | 0.011014 | 0.022169 | -0.004041 | 0.20596 | -0.038732 | 0.12639 | -0.41942 | -0.097219 | 0.008329 | -0.053648 | 0.36577 | 0.066805 | 0.028799 | 122.9663 | 122.9166 | 123.0817 | 62.2655 | -123.1653 | 122.8581 | 123.0221 | 122.9841 | 62.3422 | -123.3747
1289.2656 | 123.2254 | -66.6046 | 56.3416 | 0.057412 | -0.097138 | -0.013921 | 0.044618 | -0.022362 | 0.055941 | 0.042884 | -0.0089857 | 0.0032574 | 0.046085 | 0.099117 | 0.047572 | -66.5687 | -4.33 | -66.5995 | 56.3571 | 56.3257 | 56.4771 | -66.8055 | -66.5826 | -4.2487 | -66.6583 | 56.2581 | 56.4312 | 56.3841 | -67.0195 | -0.20085 | 0.015589 | 0.035902 | 0.005114 | 0.20596 | -0.015843 | 0.13554 | -0.41484 | -0.083488 | 0.022063 | -0.053651 | 0.36119 | 0.089694 | 0.04253 | 122.9618 | 122.9303 | 123.0817 | 62.2747 | -123.147 | 122.8627 | 123.0359 | 122.9887 | 62.3559 | -123.361
1290.2656 | 123.2391 | -66.6229 | 56.3599 | 0.057412 | -0.099274 | -0.013921 | 0.044618 | -0.024498 | 0.052737 | 0.027623 | -0.0079177 | 0.0032574 | 0.046085 | 0.099117 | 0.048641 | -66.5687 | -4.3162 | -66.5949 | 56.3617 | 56.3211 | 56.4817 | -66.8009 | -66.5917 | -4.2624 | -66.6445 | 56.2535 | 56.4221 | 56.3887 | -67.0195 | -0.17796 | 0.001857 | 0.054213 | 0.028003 | 0.20596 | -0.038732 | 0.12181 | -0.39653 | -0.10638 | 0.031216 | -0.021604 | 0.37493 | 0.062227 | 0.028799 | 122.9846 | 122.9441 | 123.1046 | 62.3067 | -123.1607 | 122.8764 | 123.045 | 123.0116 | 62.3605 | -123.3793
1291.2656 | 123.2208 | -66.6183 | 56.3599 | 0.04215 | -0.098206 | -0.013921 | 0.044618 | -0.02343 | 0.055941 | 0.058145 | -0.0079177 | 0.0032574 | 0.047154 | 0.10019 | 0.047572 | -66.5733 | -4.3071 | -66.5903 | 56.3617 | 56.3257 | 56.4771 | -66.8146 | -66.5826 | -4.2487 | -66.6445 | 56.2581 | 56.4175 | 56.3887 | -67.024 | -0.19627 | 0.001857 | 0.045057 | 0.028004 | 0.22428 | -0.034153 | 0.11723 | -0.40569 | -0.1018 | 0.035796 | -0.026182 | 0.37951 | 0.057648 | 0.028799 | 122.9801 | 122.9441 | 123.0954 | 62.3113 | -123.1745 | 122.8764 | 123.0359 | 123.007 | 62.3697 | -123.3839
1292.2656 | 123.2117 | -66.5955 | 56.3461 | 0.04215 | -0.097138 | -0.013921 | 0.045687 | -0.021293 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.046085 | 0.099117 | 0.048641 | -66.5733 | -4.2979 | -66.5995 | 56.3617 | 56.3303 | 56.4771 | -66.81 | -66.5917 | -4.2533 | -66.6445 | 56.2581 | 56.4221 | 56.3932 | -67.0195 | -0.21458 | 0.01559 | 0.022169 | -0.004041 | 0.21054 | -0.015841 | 0.13096 | -0.424 | -0.088065 | 0.00375 | -0.04907 | 0.37493 | 0.07596 | 0.047111 | 122.9572 | 122.9257 | 123.0726 | 62.2976 | -123.1562 | 122.8535 | 123.0175 | 122.9887 | 62.3422 | -123.3656
1293.2656 | 123.23 | -66.5955 | 56.3187 | 0.026888 | -0.097138 | -0.013921 | 0.044618 | -0.022362 | 0.054873 | 0.058145 | -0.0068487 | 0.0021894 | 0.046085 | 0.10019 | 0.049709 | -66.5779 | -4.2979 | -66.5995 | 56.3617 | 56.3211 | 56.4771 | -66.81 | -66.5871 | -4.2487 | -66.6537 | 56.2626 | 56.4267 | 56.3887 | -67.0195 | -0.21458 | 0.043055 | 0.01759 | -0.004041 | 0.21054 | 0.002466 | 0.15843 | -0.424 | -0.056021 | 0.008329 | -0.058227 | 0.36577 | 0.108 | 0.069997 | 122.9572 | 122.9166 | 123.0726 | 62.2976 | -123.1287 | 122.8581 | 123.0221 | 122.9841 | 62.3468 | -123.3381
1294.2656 | 123.2483 | -66.5955 | 56.3324 | 0.04215 | -0.096069 | -0.014989 | 0.047824 | -0.021293 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.048222 | 0.099117 | 0.047572 | -66.5779 | -4.2842 | -66.5903 | 56.3571 | 56.3257 | 56.4771 | -66.8146 | -66.578 | -4.2487 | -66.6491 | 56.2581 | 56.4267 | 56.3932 | -67.0149 | -0.21916 | 0.024745 | 0.01759 | 0.005116 | 0.22428 | -0.006687 | 0.14469 | -0.41942 | -0.074332 | 0.017487 | -0.053648 | 0.36577 | 0.094271 | 0.060844 | 122.9526 | 122.9212 | 123.0726 | 62.3113 | -123.147 | 122.8535 | 123.0221 | 122.9887 | 62.3468 | -123.3473
1295.2656 | 123.2208 | -66.6 | 56.3461 | 0.04215 | -0.099274 | -0.014989 | 0.044618 | -0.022362 | 0.055941 | 0.088667 | -0.0079177 | 0.0011204 | 0.046085 | 0.099117 | 0.049709 | -66.5733 | -4.275 | -66.5949 | 56.3663 | 56.3166 | 56.4771 | -66.8146 | -66.5871 | -4.2395 | -66.6537 | 56.2626 | 56.4267 | 56.3887 | -67.0195 | -0.21458 | 0.020168 | 0.026747 | 0.005115 | 0.2197 | -0.029578 | 0.13096 | -0.41942 | -0.083486 | 0.012907 | -0.053649 | 0.36577 | 0.080538 | 0.042532 | 122.9663 | 122.9166 | 123.0771 | 62.325 | -123.1607 | 122.8627 | 123.0267 | 122.9887 | 62.3605 | -123.3656
1296.2656 | 123.23 | -66.5955 | 56.3416 | 0.057412 | -0.098206 | -0.014989 | 0.045687 | -0.021293 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.046085 | 0.099117 | 0.048641 | -66.5779 | -4.2704 | -66.5949 | 56.3617 | 56.3211 | 56.4862 | -66.8192 | -66.5871 | -4.2487 | -66.6491 | 56.2672 | 56.4221 | 56.3978 | -67.0195 | -0.22374 | 0.020167 | 0.01759 | 0.000537 | 0.22428 | -0.020422 | 0.1447 | -0.424 | -0.074331 | 0.008329 | -0.053648 | 0.37035 | 0.080537 | 0.056266 | 122.9572 | 122.9166 | 123.0817 | 62.325 | -123.1608 | 122.8627 | 123.0175 | 122.9933 | 62.3468 | -123.361
1297.2656 | 123.1659 | -66.5955 | 56.3232 | 0.04215 | -0.099274 | -0.014989 | 0.046755 | -0.021293 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.047154 | 0.099117 | 0.048641 | -66.5641 | -4.2659 | -66.5949 | 56.3617 | 56.3211 | 56.4817 | -66.81 | -66.5871 | -4.2487 | -66.6445 | 56.2626 | 56.4312 | 56.3978 | -67.024 | -0.21458 | 0.038478 | 0.031325 | 0.000537 | 0.21512 | -0.002111 | 0.15843 | -0.42858 | -0.060598 | 0.008329 | -0.04907 | 0.37951 | 0.108 | 0.074577 | 122.9572 | 122.9166 | 123.0771 | 62.3296 | -123.1333 | 122.8581 | 123.0267 | 122.9933 | 62.3468 | -123.3473
1298.2656 | 123.2208 | -66.6229 | 56.3461 | 0.072674 | -0.097138 | -0.013921 | 0.04355 | -0.022362 | 0.055941 | 0.058145 | -0.0079177 | 0.0011204 | 0.046085 | 0.098049 | 0.048641 | -66.5779 | -4.2567 | -66.5995 | 56.3617 | 56.3211 | 56.4817 | -66.8146 | -66.5826 | -4.2487 | -66.6445 | 56.2672 | 56.4221 | 56.3795 | -67.0286 | -0.19169 | 0.01559 | 0.045056 | 0.023425 | 0.21512 | -0.024999 | 0.13554 | -0.40569 | -0.078908 | 0.040374 | -0.021604 | 0.38409 | 0.07596 | 0.033375 | 122.9846 | 122.9441 | 123.1046 | 62.3662 | -123.1607 | 122.8901 | 123.045 | 123.0024 | 62.3742 | -123.3747
1299.2656 | 123.2574 | -66.6275 | 56.3553 | 0.04215 | -0.099274 | -0.014989 | 0.046755 | -0.020225 | 0.055941 | 0.058145 | -0.0079177 | 0.0032574 | 0.045017 | 0.10019 | 0.049709 | -66.5733 | -4.243 | -66.5903 | 56.3617 | 56.3257 | 56.4817 | -66.8146 | -66.5826 | -4.2441 | -66.6491 | 56.2626 | 56.4312 | 56.3978 | -67.0195 | -0.18712 | 0.006434 | 0.054212 | 0.037159 | 0.22428 | -0.029576 | 0.12638 | -0.39196 | -0.092642 | 0.044951 | -0.021605 | 0.37035 | 0.075961 | 0.042533 | 122.9892 | 122.9532 | 123.1092 | 62.3845 | -123.1699 | 122.8901 | 123.0587 | 123.0253 | 62.3834 | -123.3747
1300.2656 | 123.2071 | -66.6046 | 56.3507 | 0.04215 | -0.098206 | -0.012852 | 0.045687 | -0.022362 | 0.055941 | 0.058145 | -0.0089857 | 0.0021894 | 0.047154 | 0.099117 | 0.048641 | -66.5733 | -4.2338 | -66.5995 | 56.3709 | 56.3211 | 56.4862 | -66.81 | -66.578 | -4.2441 | -66.6537 | 56.2535 | 56.4267 | 56.3932 | -67.0195 | -0.20543 | 0.020169 | 0.031324 | 0.005114 | 0.21054 | -0.029577 | 0.13554 | -0.41484 | -0.097221 | 0.026642 | -0.049072 | 0.36577 | 0.07596 | 0.042533 | 122.9755 | 122.9257 | 123.0909 | 62.3708 | -123.1607 | 122.8581 | 123.0313 | 122.9979 | 62.3605 | -123.3702
1301.2656 | 123.262 | -66.6 | 56.3095 | 0.04215 | -0.099274 | -0.014989 | 0.044618 | -0.021293 | 0.054873 | 0.042884 | -0.0079177 | 5.2373e-05 | 0.046085 | 0.10019 | 0.049709 | -66.5733 | -4.2292 | -66.5995 | 56.3663 | 56.3303 | 56.4908 | -66.81 | -66.5871 | -4.2441 | -66.6491 | 56.2489 | 56.4312 | 56.3887 | -67.0195 | -0.21 | 0.056789 | 0.026747 | 0.000537 | 0.21054 | 0.02078 | 0.18132 | -0.41942 | -0.060601 | 0.012907 | -0.04907 | 0.37035 | 0.12174 | 0.079153 | 122.9663 | 122.9303 | 123.0909 | 62.3708 | -123.1195 | 122.8489 | 123.0313 | 122.9887 | 62.3559 | -123.329
1302.2656 | 123.262 | -66.5955 | 56.3141 | 0.026888 | -0.097138 | -0.012852 | 0.045687 | -0.02343 | 0.053805 | 0.058145 | -0.0068487 | 0.0032574 | 0.046085 | 0.10019 | 0.048641 | -66.5733 | -4.2246 | -66.5949 | 56.3709 | 56.3211 | 56.4771 | -66.81 | -66.5734 | -4.2441 | -66.6491 | 56.2581 | 56.4267 | 56.3887 | -67.0195 | -0.21458 | 0.05679 | 0.022169 | 0.000537 | 0.21512 | 0.007044 | 0.163 | -0.424 | -0.056022 | 0.022065 | -0.053648 | 0.37035 | 0.11258 | 0.074575 | 122.9663 | 122.9166 | 123.0726 | 62.3708 | -123.1241 | 122.8535 | 123.0221 | 122.9841 | 62.3514 | -123.3335
1303.2656 | 123.2529 | -66.6 | 56.2958 | 0.011626 | -0.098206 | -0.013921 | 0.045687 | -0.022362 | 0.055941 | 0.042884 | -0.0089857 | 0.0021894 | 0.046085 | 0.099117 | 0.050777 | -66.5824 | -4.2201 | -66.5995 | 56.3617 | 56.3166 | 56.4862 | -66.81 | -66.578 | -4.2441 | -66.6445 | 56.2626 | 56.4267 | 56.3887 | -67.0195 | -0.21 | 0.065944 | 0.01759 | 0.000537 | 0.21054 | 0.020776 | 0.19047 | -0.41942 | -0.033132 | 0.022065 | -0.044492 | 0.37493 | 0.13089 | 0.092886 | 122.9618 | 122.9166 | 123.0863 | 62.38 | -123.1058 | 122.8627 | 123.0267 | 122.9887 | 62.3559 | -123.3152
1304.2656 | 123.2849 | -66.6229 | 56.3416 | 0.04215 | -0.10034 | -0.013921 | 0.045687 | -0.022362 | 0.053805 | 0.042884 | -0.0079177 | 0.0021894 | 0.046085 | 0.10019 | 0.047572 | -66.5779 | -4.2109 | -66.6041 | 56.3571 | 56.3211 | 56.4817 | -66.81 | -66.6009 | -4.2349 | -66.6537 | 56.2626 | 56.4221 | 56.3841 | -67.0195 | -0.18712 | 0.015589 | 0.045056 | 0.018847 | 0.20596 | -0.020422 | 0.14012 | -0.39653 | -0.078909 | 0.022059 | -0.030761 | 0.36577 | 0.080537 | 0.04253 | 122.9801 | 122.9441 | 123.1046 | 62.412 | -123.1516 | 122.8856 | 123.045 | 123.007 | 62.388 | -123.361
1305.2656 | 123.1888 | -66.6229 | 56.337 | 0.04215 | -0.098206 | -0.013921 | 0.04355 | -0.021293 | 0.055941 | 0.058145 | -0.0079177 | 0.0043254 | 0.046085 | 0.10019 | 0.047572 | -66.5733 | -4.2018 | -66.5995 | 56.3617 | 56.3303 | 56.4771 | -66.8192 | -66.5871 | -4.2349 | -66.6491 | 56.2581 | 56.4267 | 56.3887 | -67.0286 | -0.19627 | 0.024745 | 0.049635 | 0.023425 | 0.2197 | -0.006686 | 0.14012 | -0.40569 | -0.07891 | 0.035795 | -0.026182 | 0.37951 | 0.089693 | 0.051687 | 122.9846 | 122.9532 | 123.1 | 62.4212 | -123.1562 | 122.881 | 123.0496 | 123.0116 | 62.388 | -123.3656
1306.2656 | 123.1476 | -66.6412 | 56.3187 | 0.011626 | -0.099274 | -0.012852 | 0.044618 | -0.021293 | 0.054873 | 0.042884 | -0.0068487 | 0.0043254 | 0.045017 | 0.10125 | 0.049709 | -66.5687 | -4.2018 | -66.6041 | 56.3617 | 56.3257 | 56.4908 | -66.8192 | -66.5871 | -4.2349 | -66.6445 | 56.2581 | 56.4312 | 56.3932 | -67.024 | -0.17796 | 0.043055 | 0.072523 | 0.037157 | 0.21512 | 0.007045 | 0.17216 | -0.3828 | -0.0606 | 0.054105 | -0.003294 | 0.37951 | 0.11258 | 0.074576 | 123.003 | 122.9669 | 123.1321 | 62.4395 | -123.1379 | 122.8993 | 123.0725 | 123.0345 | 62.4063 | -123.3427
1307.2656 | 123.1247 | -66.6458 | 56.3553 | 0.026888 | -0.10034 | -0.014989 | 0.046755 | -0.021293 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.046085 | 0.10019 | 0.047572 | -66.5733 | -4.188 | -66.5949 | 56.3709 | 56.3303 | 56.4862 | -66.81 | -66.5826 | -4.2395 | -66.6537 | 56.2535 | 56.4267 | 56.3887 | -67.0286 | -0.16423 | 0.015591 | 0.072523 | 0.050891 | 0.21512 | -0.024997 | 0.13096 | -0.3828 | -0.1018 | 0.063262 | -0.007873 | 0.37493 | 0.071382 | 0.033376 | 123.0167 | 122.9761 | 123.1321 | 62.4578 | -123.1653 | 122.8993 | 123.0725 | 123.0345 | 62.4063 | -123.3839
1308.2656 | 123.1293 | -66.6321 | 56.3736 | 0.057412 | -0.099274 | -0.013921 | 0.045687 | -0.022362 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.048222 | 0.10019 | 0.049709 | -66.5779 | -4.1789 | -66.6041 | 56.3663 | 56.3257 | 56.4862 | -66.8192 | -66.5871 | -4.2395 | -66.6537 | 56.2581 | 56.4267 | 56.3978 | -67.0195 | -0.18712 | -0.007298 | 0.054211 | 0.028002 | 0.21512 | -0.047886 | 0.11265 | -0.38738 | -0.11553 | 0.04495 | -0.021606 | 0.36577 | 0.053072 | 0.024223 | 122.9984 | 122.9578 | 123.1183 | 62.4532 | -123.1928 | 122.8901 | 123.0587 | 123.0299 | 62.3926 | -123.3931
1309.2656 | 123.2117 | -66.6046 | 56.3278 | 0.057412 | -0.10141 | -0.014989 | 0.045687 | -0.02343 | 0.055941 | 0.042884 | -0.0089857 | 0.0032574 | 0.045017 | 0.10019 | 0.048641 | -66.5824 | -4.1789 | -66.5949 | 56.3663 | 56.3303 | 56.4862 | -66.8146 | -66.5826 | -4.2395 | -66.6491 | 56.2581 | 56.4312 | 56.3932 | -67.0195 | -0.21 | 0.038478 | 0.022167 | 0.009692 | 0.2197 | 0.002469 | 0.15843 | -0.41484 | -0.069755 | 0.022063 | -0.044493 | 0.37035 | 0.10343 | 0.065421 | 122.9709 | 122.9349 | 123.0909 | 62.4258 | -123.1424 | 122.8627 | 123.0359 | 122.9979 | 62.3651 | -123.3473
1310.2656 | 123.1567 | -66.6092 | 56.3507 | 0.057412 | -0.10034 | -0.012852 | 0.046755 | -0.02343 | 0.055941 | 0.042884 | -0.0089857 | 0.0021894 | 0.046085 | 0.10019 | 0.049709 | -66.5824 | -4.1605 | -66.6041 | 56.3709 | 56.3303 | 56.4908 | -66.8192 | -66.5917 | -4.2304 | -66.6445 | 56.2626 | 56.4267 | 56.3978 | -67.0195 | -0.21001 | 0.020169 | 0.026745 | 0.005114 | 0.21512 | -0.020419 | 0.14012 | -0.41027 | -0.088064 | 0.017483 | -0.035337 | 0.37493 | 0.07596 | 0.047111 | 122.9801 | 122.9395 | 123.1 | 62.4486 | -123.1699 | 122.8718 | 123.0359 | 123.007 | 62.3788 | -123.3702
1311.2656 | 123.1155 | -66.6641 | 56.3736 | 0.04215 | -0.097138 | -0.012852 | 0.044618 | -0.02343 | 0.054873 | 0.042884 | -0.0068487 | 5.2373e-05 | 0.046085 | 0.10125 | 0.049709 | -66.5779 | -4.1514 | -66.5995 | 56.3663 | 56.3257 | 56.4817 | -66.8284 | -66.5917 | -4.2395 | -66.6537 | 56.2581 | 56.4358 | 56.3978 | -67.0286 | -0.16423 | -0.007298 | 0.086255 | 0.064624 | 0.22886 | -0.047886 | 0.10807 | -0.36449 | -0.11553 | 0.072415 | 0.010438 | 0.37493 | 0.062229 | 0.024223 | 123.0304 | 122.9898 | 123.1458 | 62.5127 | -123.202 | 122.9222 | 123.0999 | 123.0619 | 62.4246 | -123.4022
1312.2656 | 123.1842 | -66.6595 | 56.3828 | 0.057412 | -0.098206 | -0.014989 | 0.045687 | -0.02343 | 0.05701 | 0.042884 | -0.0089857 | 0.0011204 | 0.046085 | 0.10019 | 0.048641 | -66.5687 | -4.1468 | -66.5995 | 56.3663 | 56.3257 | 56.4908 | -66.8238 | -66.5917 | -4.2441 | -66.6537 | 56.2535 | 56.4267 | 56.3978 | -67.024 | -0.16423 | -0.016453 | 0.090834 | 0.060046 | 0.22428 | -0.057041 | 0.10808 | -0.36449 | -0.12926 | 0.067837 | 0.00586 | 0.37035 | 0.043917 | 0.015068 | 123.0258 | 122.9853 | 123.1504 | 62.5127 | -123.2065 | 122.913 | 123.0862 | 123.0574 | 62.4154 | -123.4068
1313.2656 | 123.1842 | -66.6275 | 56.3416 | 0.057412 | -0.099274 | -0.011784 | 0.045687 | -0.02343 | 0.054873 | 0.042884 | -0.0068487 | 0.0021894 | 0.047154 | 0.10232 | 0.049709 | -66.5779 | -4.1422 | -66.5995 | 56.3709 | 56.3303 | 56.4908 | -66.8146 | -66.5963 | -4.2349 | -66.6491 | 56.2672 | 56.4221 | 56.3932 | -67.024 | -0.18712 | 0.029324 | 0.049633 | 0.028002 | 0.21512 | -0.011264 | 0.14927 | -0.39654 | -0.074331 | 0.031215 | -0.021605 | 0.37493 | 0.080537 | 0.051688 | 122.9984 | 122.9578 | 123.1183 | 62.4853 | -123.1562 | 122.8947 | 123.0496 | 123.0207 | 62.3926 | -123.3656
1314.2656 | 123.1796 | -66.6367 | 56.3187 | 0.026888 | -0.099274 | -0.014989 | 0.044618 | -0.022362 | 0.055941 | 0.042884 | -0.0089857 | 0.0021894 | 0.045017 | 0.10019 | 0.049709 | -66.5779 | -4.1285 | -66.6132 | 56.3663 | 56.3211 | 56.4908 | -66.8146 | -66.5871 | -4.2395 | -66.6491 | 56.2672 | 56.4267 | 56.3978 | -67.0195 | -0.17796 | 0.047633 | 0.058789 | 0.023423 | 0.20138 | 0.002466 | 0.17216 | -0.3828 | -0.051443 | 0.049528 | -0.012449 | 0.37035 | 0.108 | 0.079154 | 123.003 | 122.9578 | 123.1275 | 62.5082 | -123.1333 | 122.9039 | 123.0633 | 123.0345 | 62.3971 | -123.3381
1315.2656 | 123.2208 | -66.6229 | 56.3828 | 0.04215 | -0.099274 | -0.014989 | 0.046755 | -0.020225 | 0.054873 | 0.058145 | -0.0079177 | 0.0021894 | 0.046085 | 0.10232 | 0.049709 | -66.5733 | -4.1285 | -66.6041 | 56.3709 | 56.3303 | 56.4862 | -66.8192 | -66.5826 | -4.2441 | -66.6491 | 56.2581 | 56.4221 | 56.3978 | -67.024 | -0.19627 | -0.011874 | 0.049635 | 0.018847 | 0.21512 | -0.052462 | 0.1035 | -0.40111 | -0.12469 | 0.040374 | -0.026182 | 0.37493 | 0.039339 | 0.015068 | 122.9938 | 122.9532 | 123.1092 | 62.4944 | -123.2019 | 122.881 | 123.045 | 123.0207 | 62.3788 | -123.4068
1316.2656 | 123.1659 | -66.6275 | 56.3553 | 0.026888 | -0.10034 | -0.016058 | 0.045687 | -0.022362 | 0.055941 | 0.042884 | -0.0089857 | 0.0021894 | 0.046085 | 0.10019 | 0.048641 | -66.5779 | -4.1193 | -66.6087 | 56.3709 | 56.3349 | 56.5 | -66.8284 | -66.5917 | -4.2304 | -66.6537 | 56.2581 | 56.4175 | 56.3978 | -67.0195 | -0.20085 | 0.015591 | 0.049633 | 0.018846 | 0.2197 | -0.020418 | 0.1447 | -0.39196 | -0.097221 | 0.035793 | -0.026184 | 0.36577 | 0.062225 | 0.042533 | 122.9984 | 122.9624 | 123.1275 | 62.5082 | -123.1836 | 122.8856 | 123.045 | 123.0253 | 62.3971 | -123.3747
1317.2656 | 123.175 | -66.6229 | 56.3644 | 0.011626 | -0.10034 | -0.014989 | 0.046755 | -0.022362 | 0.05701 | 0.042884 | -0.0079177 | 0.0032574 | 0.047154 | 0.10125 | 0.048641 | -66.5733 | -4.1056 | -66.6041 | 56.3663 | 56.3349 | 56.4954 | -66.8284 | -66.5871 | -4.2349 | -66.6491 | 56.2672 | 56.4221 | 56.3932 | -67.0332 | -0.20543 | 0.001857 | 0.049635 | 0.018847 | 0.22428 | -0.029573 | 0.13097 | -0.41027 | -0.097219 | 0.035795 | -0.026182 | 0.38409 | 0.057649 | 0.0288 | 122.9892 | 122.9578 | 123.1183 | 62.5173 | -123.1928 | 122.8901 | 123.045 | 123.0162 | 62.388 | -123.3976
1318.2656 | 123.2117 | -66.6504 | 56.3599 | 0.04215 | -0.099274 | -0.014989 | 0.044618 | -0.021293 | 0.053805 | 0.073406 | -0.0089857 | 0.0032574 | 0.046085 | 0.10019 | 0.048641 | -66.5779 | -4.1056 | -66.6087 | 56.3663 | 56.3303 | 56.4954 | -66.8146 | -66.5871 | -4.2304 | -66.6583 | 56.2626 | 56.4175 | 56.3978 | -67.0195 | -0.16423 | 0.006435 | 0.072522 | 0.041735 | 0.20596 | -0.029574 | 0.13554 | -0.36907 | -0.097219 | 0.063261 | -0.007874 | 0.36119 | 0.057648 | 0.037956 | 123.0167 | 122.9807 | 123.1458 | 62.5448 | -123.1745 | 122.913 | 123.0679 | 123.0482 | 62.42 | -123.3793
1319.2656 | 123.1567 | -66.6229 | 56.3416 | 0.04215 | -0.099274 | -0.014989 | 0.042482 | -0.024498 | 0.055941 | 0.027623 | -0.010054 | 0.0043254 | 0.048222 | 0.10232 | 0.049709 | -66.587 | -4.0919 | -66.5949 | 56.3663 | 56.3303 | 56.4771 | -66.8192 | -66.5871 | -4.2258 | -66.6537 | 56.2626 | 56.4221 | 56.3978 | -67.0332 | -0.19627 | 0.024745 | 0.035899 | 0.028003 | 0.22428 | -0.011264 | 0.13554 | -0.41027 | -0.078909 | 0.035795 | -0.030761 | 0.37951 | 0.080537 | 0.056266 | 122.9892 | 122.9532 | 123.1 | 62.5311 | -123.1608 | 122.8856 | 123.045 | 123.0207 | 62.3971 | -123.3747
1320.2656 | 123.1934 | -66.6229 | 56.3507 | 0.04215 | -0.098206 | -0.014989 | 0.046755 | -0.022362 | 0.053805 | 0.058145 | -0.0068487 | 0.0011204 | 0.045017 | 0.10339 | 0.048641 | -66.5779 | -4.0873 | -66.6087 | 56.3617 | 56.3257 | 56.4771 | -66.8146 | -66.5871 | -4.2304 | -66.6537 | 56.2672 | 56.4175 | 56.3932 | -67.024 | -0.19169 | 0.011012 | 0.045056 | 0.014269 | 0.20596 | -0.024998 | 0.12638 | -0.40111 | -0.083486 | 0.035795 | -0.030761 | 0.37035 | 0.066803 | 0.042533 | 122.9846 | 122.9486 | 123.1 | 62.5356 | -123.1653 | 122.8901 | 123.0404 | 123.0162 | 62.3926 | -123.3747
1321.2656 | 123.1613 | -66.6458 | 56.4102 | 0.04215 | -0.098206 | -0.016058 | 0.044618 | -0.02343 | 0.053805 | 0.073406 | -0.0079177 | 0.0032574 | 0.046085 | 0.10339 | 0.048641 | -66.5779 | -4.0827 | -66.6041 | 56.3617 | 56.3257 | 56.4817 | -66.8146 | -66.5871 | -4.2212 | -66.6491 | 56.2581 | 56.4267 | 56.3887 | -67.0149 | -0.16881 | -0.048497 | 0.067944 | 0.041735 | 0.21054 | -0.084507 | 0.071453 | -0.36907 | -0.15215 | 0.058683 | -0.003294 | 0.36577 | 0.016451 | -0.021555 | 123.0075 | 122.9715 | 123.1275 | 62.5631 | -123.2248 | 122.9039 | 123.0725 | 123.0345 | 62.4246 | -123.4251
1322.2656 | 123.143 | -66.6275 | 56.3919 | 0.04215 | -0.10034 | -0.014989 | 0.045687 | -0.02343 | 0.053805 | 0.073406 | -0.0079177 | 0.0032574 | 0.046085 | 0.10339 | 0.048641 | -66.5779 | -4.0781 | -66.6041 | 56.3663 | 56.3257 | 56.4817 | -66.8192 | -66.5963 | -4.2304 | -66.6537 | 56.2672 | 56.4175 | 56.3932 | -67.0195 | -0.1917 | -0.025609 | 0.049633 | 0.023424 | 0.21512 | -0.066197 | 0.089763 | -0.39196 | -0.12469 | 0.031215 | -0.026184 | 0.36577 | 0.025604 | 0.001334 | 122.9938 | 122.9532 | 123.1092 | 62.5494 | -123.2111 | 122.8947 | 123.045 | 123.0207 | 62.3971 | -123.4114
1323.2656 | 123.1659 | -66.6138 | 56.369 | 0.057412 | -0.099274 | -0.013921 | 0.044618 | -0.024498 | 0.054873 | 0.073406 | -0.010054 | 0.0043254 | 0.045017 | 0.10232 | 0.048641 | -66.5779 | -4.0736 | -66.6087 | 56.3571 | 56.3211 | 56.4771 | -66.8192 | -66.5963 | -4.2304 | -66.6674 | 56.2626 | 56.4221 | 56.3887 | -67.0286 | -0.20543 | -0.011877 | 0.035901 | 0.005114 | 0.21054 | -0.047888 | 0.10807 | -0.41485 | -0.10637 | 0.017483 | -0.053652 | 0.36119 | 0.053071 | 0.019643 | 122.9709 | 122.9349 | 123.0909 | 62.5402 | -123.1882 | 122.8764 | 123.0359 | 123.0024 | 62.3834 | -123.3976
1324.2656 | 123.1247 | -66.6504 | 56.3507 | 0.026888 | -0.10034 | -0.013921 | 0.045687 | -0.02343 | 0.054873 | 0.058145 | -0.0079177 | 0.0032574 | 0.043949 | 0.10125 | 0.048641 | -66.5733 | -4.069 | -66.5995 | 56.3617 | 56.2982 | 56.4817 | -66.8146 | -66.5917 | -4.2212 | -66.6583 | 56.2626 | 56.4267 | 56.3841 | -67.0195 | -0.16423 | 0.011012 | 0.077101 | 0.050891 | 0.21512 | -0.052472 | 0.13096 | -0.36907 | -0.088064 | 0.058682 | -0.007874 | 0.36119 | 0.07596 | 0.033375 | 123.0121 | 122.9486 | 123.1321 | 62.5814 | -123.1653 | 122.913 | 123.0771 | 123.0345 | 62.4292 | -123.3702
1325.2656 | 123.1247 | -66.6367 | 56.3736 | 0.04215 | -0.099274 | -0.014989 | 0.04355 | -0.022362 | 0.053805 | 0.027623 | -0.0079177 | 0.0043254 | 0.045017 | 0.10125 | 0.048641 | -66.5824 | -4.0598 | -66.6132 | 56.3571 | 56.3028 | 56.4862 | -66.81 | -66.5917 | -4.2212 | -66.6491 | 56.2626 | 56.4312 | 56.3887 | -67.0332 | -0.17338 | -0.016454 | 0.054211 | 0.023423 | 0.1968 | -0.070781 | 0.11265 | -0.39654 | -0.11095 | 0.044949 | -0.012449 | 0.38409 | 0.057651 | 0.015066 | 122.9938 | 122.9395 | 123.1229 | 62.5768 | -123.1836 | 122.8993 | 123.0679 | 123.0253 | 62.4154 | -123.4068
1326.2656 | 123.1384 | -66.5863 | 56.3965 | 0.057412 | -0.10141 | -0.013921 | 0.044618 | -0.02343 | 0.05701 | 0.073406 | -0.0089857 | 0.0021894 | 0.046085 | 0.10125 | 0.049709 | -66.5779 | -4.0461 | -66.6087 | 56.3526 | 56.312 | 56.4817 | -66.8055 | -66.5917 | -4.2258 | -66.6491 | 56.2626 | 56.4312 | 56.3841 | -67.0286 | -0.21916 | -0.043921 | 0.008435 | -0.022352 | 0.1968 | -0.084511 | 0.085186 | -0.44231 | -0.13384 | -0.005405 | -0.062803 | 0.37951 | 0.034763 | -0.012401 | 122.9389 | 122.8983 | 123.068 | 62.5402 | -123.2019 | 122.8489 | 123.0176 | 122.9704 | 62.3605 | -123.4251
1327.2656 | 123.1888 | -66.6229 | 56.3873 | 0.072674 | -0.10141 | -0.013921 | 0.044618 | -0.02343 | 0.053805 | 0.088667 | -0.0079177 | 0.0011204 | 0.046085 | 0.10339 | 0.047572 | -66.5779 | -4.0461 | -66.6041 | 56.3571 | 56.312 | 56.4771 | -66.81 | -66.6009 | -4.2258 | -66.6491 | 56.2626 | 56.4312 | 56.3887 | -67.0286 | -0.18712 | -0.030187 | 0.045056 | 0.018847 | 0.20596 | -0.075356 | 0.089762 | -0.40569 | -0.12468 | 0.022059 | -0.026182 | 0.37951 | 0.043918 | 0.001333 | 122.9801 | 122.9349 | 123.1 | 62.5768 | -123.1974 | 122.8856 | 123.0542 | 123.0116 | 62.3971 | -123.4159
1328.2656 | 123.2758 | -66.5817 | 56.3553 | 0.04215 | -0.099274 | -0.016058 | 0.047824 | -0.02343 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.047154 | 0.10232 | 0.047572 | -66.5733 | -4.0415 | -66.6041 | 56.3617 | 56.3257 | 56.4725 | -66.8146 | -66.5871 | -4.2166 | -66.6628 | 56.2626 | 56.4267 | 56.3841 | -67.0286 | -0.23289 | 0.006434 | 0.008436 | -0.022352 | 0.21054 | -0.029576 | 0.11723 | -0.44689 | -0.092642 | -0.005404 | -0.081117 | 0.36577 | 0.071382 | 0.028797 | 122.9434 | 122.9074 | 123.0542 | 62.5402 | -123.1699 | 122.8444 | 123.0084 | 122.9658 | 62.3651 | -123.3839
1329.2656 | 123.143 | -66.6595 | 56.3553 | 0.011626 | -0.099274 | -0.013921 | 0.046755 | -0.024498 | 0.054873 | 0.042884 | -0.0089857 | 0.0032574 | 0.046085 | 0.10125 | 0.047572 | -66.5779 | -4.0278 | -66.6087 | 56.3617 | 56.3211 | 56.4862 | -66.8192 | -66.5871 | -4.2212 | -66.6491 | 56.2535 | 56.4221 | 56.3795 | -67.0286 | -0.15965 | 0.006434 | 0.081677 | 0.05089 | 0.21054 | -0.034155 | 0.13096 | -0.36907 | -0.1018 | 0.072416 | 0.010439 | 0.37951 | 0.066804 | 0.024219 | 123.0213 | 122.9807 | 123.1458 | 62.6318 | -123.1745 | 122.913 | 123.0816 | 123.0391 | 62.4383 | -123.3839
1330.2656 | 123.1522 | -66.5955 | 56.3644 | 0.057412 | -0.10034 | -0.013921 | 0.044618 | -0.024498 | 0.053805 | 0.073406 | -0.010054 | 0.0011204 | 0.046085 | 0.10232 | 0.048641 | -66.5733 | -4.0323 | -66.6041 | 56.3571 | 56.3211 | 56.4817 | -66.8146 | -66.5871 | -4.2121 | -66.6537 | 56.2672 | 56.4221 | 56.3887 | -67.0286 | -0.21916 | -0.007299 | 0.022169 | -0.008619 | 0.21054 | -0.04331 | 0.11723 | -0.43316 | -0.097219 | 0.008329 | -0.058227 | 0.37493 | 0.057649 | 0.024221 | 122.9526 | 122.9166 | 123.0771 | 62.5631 | -123.1791 | 122.8627 | 123.0175 | 122.9841 | 62.3834 | -123.3931
1331.2656 | 123.2529 | -66.5955 | 56.3782 | 0.04215 | -0.10034 | -0.014989 | 0.044618 | -0.02343 | 0.055941 | 0.073406 | -0.0079177 | 0.0021894 | 0.046085 | 0.10232 | 0.047572 | -66.5733 | -4.0232 | -66.6087 | 56.3617 | 56.3211 | 56.4908 | -66.8192 | -66.5871 | -4.2121 | -66.6583 | 56.2581 | 56.4267 | 56.3887 | -67.024 | -0.22374 | -0.016454 | 0.022169 | -0.013197 | 0.21054 | -0.057043 | 0.11265 | -0.42858 | -0.12011 | 0.008329 | -0.062806 | 0.36577 | 0.048494 | 0.010488 | 122.9572 | 122.9166 | 123.0863 | 62.5723 | -123.1974 | 122.8535 | 123.0221 | 122.9841 | 62.3834 | -123.4022
1332.2656 | 123.2803 | -66.5634 | 56.369 | 0.04215 | -0.10034 | -0.014989 | 0.045687 | -0.022362 | 0.054873 | 0.058145 | -0.0079177 | 0.0032574 | 0.046085 | 0.10232 | 0.047572 | -66.5733 | -4.014 | -66.6087 | 56.3571 | 56.3257 | 56.4771 | -66.8238 | -66.5871 | -4.2166 | -66.6537 | 56.2581 | 56.4221 | 56.3887 | -67.0286 | -0.26036 | -0.011877 | -0.009874 | -0.04524 | 0.21512 | -0.043309 | 0.10807 | -0.4652 | -0.11095 | -0.023714 | -0.09027 | 0.37493 | 0.053071 | 0.019643 | 122.9206 | 122.8891 | 123.0405 | 62.5494 | -123.1928 | 122.8215 | 122.9855 | 122.9521 | 62.3468 | -123.3976
1333.2656 | 123.2529 | -66.5817 | 56.3416 | 0.057412 | -0.099274 | -0.014989 | 0.045687 | -0.021293 | 0.055941 | 0.058145 | -0.0068487 | 0.0043254 | 0.045017 | 0.10339 | 0.050777 | -66.5779 | -4.0049 | -66.6087 | 56.3663 | 56.3303 | 56.4862 | -66.81 | -66.5871 | -4.2166 | -66.6583 | 56.2581 | 56.4312 | 56.3932 | -67.0286 | -0.22831 | 0.024745 | 0.003857 | -0.02693 | 0.20138 | -0.011264 | 0.1447 | -0.44689 | -0.083488 | -0.005404 | -0.076539 | 0.37035 | 0.089694 | 0.051688 | 122.948 | 122.912 | 123.068 | 62.5769 | -123.1516 | 122.8398 | 123.013 | 122.975 | 62.3651 | -123.3702
1334.2656 | 123.2803 | -66.6092 | 56.3278 | 0.04215 | -0.10034 | -0.012852 | 0.045687 | -0.02343 | 0.055941 | 0.073406 | -0.0079177 | 0.0032574 | 0.047154 | 0.10125 | 0.048641 | -66.5824 | -4.0003 | -66.6132 | 56.3663 | 56.3349 | 56.4862 | -66.8192 | -66.5871 | -4.2121 | -66.6537 | 56.2535 | 56.4267 | 56.3887 | -67.0286 | -0.21001 | 0.038478 | 0.026745 | -0.004043 | 0.20596 | 0.007048 | 0.15843 | -0.41942 | -0.074333 | 0.022062 | -0.044494 | 0.37493 | 0.098848 | 0.060842 | 122.9755 | 122.9441 | 123.0954 | 62.6089 | -123.147 | 122.8627 | 123.0359 | 122.9979 | 62.3971 | -123.3564
1335.2656 | 123.2574 | -66.6046 | 56.3507 | 0.011626 | -0.10141 | -0.012852 | 0.044618 | -0.021293 | 0.054873 | 0.042884 | -0.0089857 | 0.0011204 | 0.043949 | 0.10232 | 0.047572 | -66.587 | -4.0003 | -66.6041 | 56.3663 | 56.3257 | 56.4862 | -66.8238 | -66.5871 | -4.2121 | -66.6537 | 56.2581 | 56.4267 | 56.3887 | -67.024 | -0.21916 | 0.01559 | 0.017588 | 0.000536 | 0.2197 | -0.024998 | 0.13554 | -0.41942 | -0.092643 | 0.017484 | -0.049072 | 0.37035 | 0.07596 | 0.037954 | 122.9709 | 122.9303 | 123.0909 | 62.6043 | -123.1745 | 122.8627 | 123.0313 | 122.9933 | 62.3926 | -123.3747
1336.2656 | 123.2712 | -66.5863 | 56.3553 | 0.087936 | -0.099274 | -0.014989 | 0.04355 | -0.022362 | 0.05701 | 0.042884 | -0.0079177 | 5.2373e-05 | 0.046085 | 0.10232 | 0.048641 | -66.5779 | -3.9911 | -66.6087 | 56.3663 | 56.3303 | 56.4954 | -66.8238 | -66.5871 | -4.2075 | -66.6628 | 56.2672 | 56.4129 | 56.3932 | -67.0286 | -0.23747 | 0.011012 | 0.008435 | -0.022352 | 0.21512 | -0.024997 | 0.14012 | -0.44231 | -0.088064 | -0.000826 | -0.076539 | 0.36577 | 0.057646 | 0.037955 | 122.9526 | 122.9166 | 123.0817 | 62.5952 | -123.1791 | 122.8535 | 122.9992 | 122.9795 | 62.3788 | -123.3839
1337.2656 | 123.2803 | -66.5817 | 56.3599 | 0.072674 | -0.098206 | -0.014989 | 0.04355 | -0.020225 | 0.055941 | 0.088667 | -0.0089857 | 0.0032574 | 0.045017 | 0.10446 | 0.047572 | -66.5824 | -3.982 | -66.6132 | 56.3663 | 56.3349 | 56.4771 | -66.8192 | -66.5917 | -4.2121 | -66.6628 | 56.2535 | 56.4267 | 56.3932 | -67.024 | -0.23747 | 0.006435 | -0.000721 | -0.031509 | 0.20596 | -0.024995 | 0.11723 | -0.44231 | -0.10638 | -0.009983 | -0.081117 | 0.36119 | 0.066805 | 0.033378 | 122.948 | 122.9166 | 123.0588 | 62.5997 | -123.1791 | 122.8352 | 123.0084 | 122.975 | 62.3697 | -123.3839
1338.2656 | 123.262 | -66.5909 | 56.3599 | 0.057412 | -0.10034 | -0.013921 | 0.044618 | -0.022362 | 0.05701 | 0.058145 | -0.0068487 | 0.0032574 | 0.046085 | 0.10232 | 0.048641 | -66.5824 | -3.9866 | -66.6087 | 56.3617 | 56.3303 | 56.4817 | -66.8238 | -66.5826 | -4.2121 | -66.6491 | 56.2581 | 56.4221 | 56.3887 | -67.0286 | -0.2329 | 0.001857 | 0.008434 | -0.017775 | 0.21512 | -0.029574 | 0.12181 | -0.43774 | -0.1018 | 0.00833 | -0.058226 | 0.37951 | 0.062227 | 0.028799 | 122.9526 | 122.9212 | 123.0726 | 62.6043 | -123.1836 | 122.8489 | 123.013 | 122.9795 | 62.3788 | -123.3885
1339.2812 | 123.2574 | -66.5726 | 56.3553 | 0.026888 | -0.099274 | -0.014989 | 0.044618 | -0.021293 | 0.055941 | 0.042884 | -0.0079177 | 0.0043254 | 0.046085 | 0.10339 | 0.047572 | -66.5779 | -3.9728 | -66.6132 | 56.3663 | 56.3303 | 56.4817 | -66.8238 | -66.578 | -4.2075 | -66.6583 | 56.2626 | 56.4312 | 56.3887 | -67.0378 | -0.25121 | 0.011012 | -0.005298 | -0.040664 | 0.21054 | -0.024997 | 0.12638 | -0.4652 | -0.092642 | -0.005401 | -0.085694 | 0.37951 | 0.075961 | 0.033376 | 122.9389 | 122.9029 | 123.0542 | 62.5998 | -123.1791 | 122.8352 | 123.0038 | 122.9612 | 62.3651 | -123.3931
1340.2656 | 123.3032 | -66.5634 | 56.3461 | 0.04215 | -0.10141 | -0.016058 | 0.044618 | -0.02343 | 0.053805 | 0.073406 | -0.0079177 | 0.0011204 | 0.045017 | 0.10232 | 0.048641 | -66.587 | -3.9682 | -66.6041 | 56.3617 | 56.3257 | 56.4817 | -66.8192 | -66.5871 | -4.2121 | -66.6628 | 56.2626 | 56.4175 | 56.3932 | -67.0286 | -0.25578 | 0.01559 | -0.02361 | -0.040662 | 0.21512 | -0.02042 | 0.13554 | -0.4652 | -0.083486 | -0.023714 | -0.099427 | 0.36577 | 0.071381 | 0.047111 | 122.9251 | 122.8891 | 123.0451 | 62.5952 | -123.1653 | 122.8261 | 122.9809 | 122.9567 | 62.3514 | -123.3747
1341.2656 | 123.1522 | -66.6229 | 56.3782 | 0.04215 | -0.10141 | -0.013921 | 0.044618 | -0.022362 | 0.054873 | 0.058145 | -0.010054 | 0.0032574 | 0.046085 | 0.10339 | 0.047572 | -66.5824 | -3.9682 | -66.6132 | 56.3526 | 56.3257 | 56.4862 | -66.81 | -66.5871 | -4.1937 | -66.6537 | 56.2626 | 56.4221 | 56.3887 | -67.0332 | -0.18712 | -0.025611 | 0.040478 | 0.00969 | 0.1968 | -0.052464 | 0.10807 | -0.41027 | -0.11553 | 0.035795 | -0.030761 | 0.37951 | 0.043916 | 0.010488 | 122.9755 | 122.9486 | 123.1092 | 62.6547 | -123.1882 | 122.8856 | 123.045 | 123.0116 | 62.4292 | -123.4114
1342.2656 | 123.2208 | -66.6046 | 56.3324 | 0.026888 | -0.10034 | -0.014989 | 0.044618 | -0.02343 | 0.05701 | 0.058145 | -0.0089857 | 0.0011204 | 0.047154 | 0.10232 | 0.048641 | -66.587 | -3.9637 | -66.6132 | 56.3526 | 56.3303 | 56.4771 | -66.8192 | -66.5826 | -4.2029 | -66.6537 | 56.2535 | 56.4221 | 56.3887 | -67.0195 | -0.21458 | 0.020166 | 0.017588 | -0.008621 | 0.20596 | -0.002108 | 0.14469 | -0.41484 | -0.07891 | 0.022063 | -0.049072 | 0.36577 | 0.089693 | 0.056265 | 122.9572 | 122.9349 | 123.0817 | 62.641 | -123.1516 | 122.8581 | 123.0267 | 122.9933 | 62.4017 | -123.3519
1343.2656 | 123.2666 | -66.5863 | 56.3599 | 0.072674 | -0.10034 | -0.013921 | 0.045687 | -0.02343 | 0.053805 | 0.042884 | -0.0079177 | 0.0021894 | 0.046085 | 0.10339 | 0.048641 | -66.587 | -3.9545 | -66.6132 | 56.3571 | 56.3257 | 56.4771 | -66.8192 | -66.6009 | -4.2029 | -66.6537 | 56.2626 | 56.4221 | 56.3795 | -67.024 | -0.23289 | -0.002721 | -0.000722 | -0.026931 | 0.20596 | -0.034153 | 0.11723 | -0.43773 | -0.097219 | -0.014562 | -0.067382 | 0.37035 | 0.062227 | 0.019642 | 122.9434 | 122.912 | 123.0634 | 62.6318 | -123.1791 | 122.8489 | 123.0084 | 122.9658 | 62.3834 | -123.3839
1344.2812 | 123.2437 | -66.5817 | 56.3278 | 0.026888 | -0.10034 | -0.014989 | 0.044618 | -0.021293 | 0.054873 | 0.073406 | -0.0079177 | 0.0032574 | 0.046085 | 0.10232 | 0.047572 | -66.5824 | -3.9453 | -66.6132 | 56.3571 | 56.3211 | 56.4817 | -66.8192 | -66.5917 | -4.1983 | -66.6583 | 56.2581 | 56.4221 | 56.3841 | -67.0286 | -0.23747 | 0.029322 | -0.000721 | -0.031509 | 0.20596 | -0.006689 | 0.15385 | -0.44689 | -0.069755 | -0.009983 | -0.076539 | 0.37035 | 0.09427 | 0.056263 | 122.9389 | 122.9029 | 123.0634 | 62.6364 | -123.147 | 122.8398 | 123.0038 | 122.9658 | 62.3834 | -123.3564
1345.2656 | 123.2574 | -66.5909 | 56.3736 | 0.04215 | -0.10141 | -0.014989 | 0.04355 | -0.022362 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.045017 | 0.10232 | 0.048641 | -66.5779 | -3.9545 | -66.6087 | 56.3617 | 56.3303 | 56.4817 | -66.81 | -66.5917 | -4.1983 | -66.6491 | 56.2581 | 56.4175 | 56.3887 | -67.0332 | -0.21916 | -0.011876 | 0.013012 | -0.017775 | 0.20138 | -0.043307 | 0.10807 | -0.44231 | -0.11553 | -0.000828 | -0.058226 | 0.38409 | 0.043915 | 0.015066 | 122.9526 | 122.9212 | 123.0726 | 62.6364 | -123.1836 | 122.8489 | 123.0084 | 122.9795 | 62.3926 | -123.4068
1346.2656 | 123.2254 | -66.6229 | 56.337 | 0.057412 | -0.10034 | -0.016058 | 0.044618 | -0.022362 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.045017 | 0.10232 | 0.048641 | -66.5779 | -3.9316 | -66.6041 | 56.3617 | 56.3166 | 56.4771 | -66.8192 | -66.5963 | -4.1937 | -66.6583 | 56.2626 | 56.4175 | 56.3841 | -67.0378 | -0.19627 | 0.024745 | 0.045056 | 0.018847 | 0.21512 | -0.020423 | 0.14012 | -0.41485 | -0.074331 | 0.026638 | -0.03534 | 0.37951 | 0.080536 | 0.047108 | 122.9846 | 122.9395 | 123.1 | 62.6913 | -123.1562 | 122.8856 | 123.0404 | 123.007 | 62.4292 | -123.3747
1347.2656 | 123.3032 | -66.5634 | 56.3507 | 0.011626 | -0.10141 | -0.013921 | 0.042482 | -0.021293 | 0.055941 | 0.073406 | -0.0079177 | 0.0021894 | 0.047154 | 0.10232 | 0.047572 | -66.587 | -3.927 | -66.6178 | 56.3526 | 56.3257 | 56.4771 | -66.8146 | -66.5917 | -4.1983 | -66.6491 | 56.2535 | 56.4267 | 56.3795 | -67.0332 | -0.2512 | 0.001855 | -0.02361 | -0.054397 | 0.19681 | -0.024998 | 0.12638 | -0.46978 | -0.097221 | -0.028293 | -0.085691 | 0.38409 | 0.07596 | 0.028797 | 122.916 | 122.8891 | 123.0405 | 62.6364 | -123.1653 | 122.8169 | 122.9901 | 122.9429 | 62.3651 | -123.3839
1348.2656 | 123.2666 | -66.6183 | 56.3736 | 0.04215 | -0.10248 | -0.013921 | 0.042482 | -0.02343 | 0.05701 | 0.058145 | -0.0089857 | 0.0032574 | 0.046085 | 0.10339 | 0.049709 | -66.5733 | -3.9133 | -66.6132 | 56.3617 | 56.3166 | 56.4817 | -66.8238 | -66.5917 | -4.1937 | -66.6628 | 56.2581 | 56.4267 | 56.3887 | -67.0332 | -0.20543 | -0.011876 | 0.045057 | 0.005112 | 0.21054 | -0.057044 | 0.10807 | -0.41485 | -0.11553 | 0.026638 | -0.044496 | 0.37035 | 0.053072 | 0.015066 | 122.9801 | 122.9349 | 123.1 | 62.705 | -123.1974 | 122.8764 | 123.045 | 123.007 | 62.4246 | -123.4068
1349.2812 | 123.1613 | -66.6275 | 56.3873 | 0.04215 | -0.10248 | -0.014989 | 0.044618 | -0.022362 | 0.055941 | 0.058145 | -0.0089857 | 0.0021894 | 0.046085 | 0.10339 | 0.048641 | -66.5916 | -3.9133 | -66.6041 | 56.3709 | 56.3257 | 56.4817 | -66.8192 | -66.5871 | -4.1983 | -66.6491 | 56.2581 | 56.4221 | 56.3978 | -67.0286 | -0.1917 | -0.016452 | 0.035898 | 0.023424 | 0.21512 | -0.061619 | 0.094341 | -0.40111 | -0.12926 | 0.040372 | -0.021605 | 0.37951 | 0.034761 | 0.01049 | 122.9984 | 122.9532 | 123.1092 | 62.7142 | -123.2065 | 122.8856 | 123.0496 | 123.0253 | 62.4292 | -123.4159
1350.2656 | 123.2758 | -66.5634 | 56.3416 | 0.057412 | -0.10141 | -0.013921 | 0.04355 | -0.02343 | 0.055941 | 0.073406 | -0.0089857 | 0.0032574 | 0.047154 | 0.10446 | 0.048641 | -66.587 | -3.9041 | -66.6041 | 56.3571 | 56.3211 | 56.4817 | -66.8146 | -66.5871 | -4.1983 | -66.6628 | 56.2581 | 56.4221 | 56.3887 | -67.0332 | -0.2512 | 0.015589 | -0.02361 | -0.040662 | 0.21054 | -0.020422 | 0.14012 | -0.46978 | -0.083488 | -0.023714 | -0.099427 | 0.37035 | 0.080537 | 0.047109 | 122.9206 | 122.8845 | 123.0451 | 62.6593 | -123.1562 | 122.8215 | 122.9855 | 122.9521 | 62.3651 | -123.3747
1351.2656 | 123.2529 | -66.5817 | 56.3461 | 0.057412 | -0.10141 | -0.013921 | 0.04355 | -0.02343 | 0.05701 | 0.042884 | -0.0079177 | 0.0032574 | 0.047154 | 0.10446 | 0.048641 | -66.5824 | -3.8996 | -66.6041 | 56.3617 | 56.3211 | 56.4908 | -66.8192 | -66.5826 | -4.2121 | -66.6537 | 56.2581 | 56.4221 | 56.3795 | -67.0286 | -0.23747 | 0.01559 | -0.000721 | -0.022352 | 0.21512 | -0.024999 | 0.1447 | -0.44689 | -0.088065 | -0.000825 | -0.07196 | 0.37493 | 0.07596 | 0.033375 | 122.9434 | 122.9029 | 123.0726 | 62.6822 | -123.1653 | 122.8398 | 123.0038 | 122.9612 | 62.3697 | -123.3747
1352.2656 | 123.2529 | -66.6092 | 56.3278 | 0.04215 | -0.10034 | -0.013921 | 0.04355 | -0.022362 | 0.05701 | 0.058145 | -0.0079177 | 0.0032574 | 0.046085 | 0.10339 | 0.048641 | -66.5275 | -3.8812 | -66.6041 | 56.3663 | 56.3257 | 56.4817 | -66.8146 | -66.5826 | -4.1159 | -66.6491 | 56.2626 | 56.4267 | 56.3887 | -67.0286 | -0.20543 | 0.038478 | 0.081686 | 0.005114 | 0.21054 | -0.00211 | 0.15385 | -0.41942 | -0.065176 | 0.026641 | -0.039915 | 0.37951 | 0.098848 | 0.060842 | 122.9755 | 122.9349 | 123.0909 | 62.7279 | -123.1424 | 122.8718 | 123.0359 | 122.9979 | 62.4933 | -123.3564
1353.2656 | 129.1809 | -66.5817 | 56.3232 | 0.04215 | -0.099274 | -0.014989 | 0.044618 | -0.02343 | 0.055941 | 0.073406 | -0.0057807 | 0.0011204 | 0.047154 | 0.10232 | 0.049709 | -66.4039 | -3.808 | -66.3202 | 56.3663 | 56.3211 | 56.4771 | -66.8238 | -66.5276 | -4.0472 | -66.6537 | 56.2581 | 56.4175 | 56.3795 | -67.024 | -0.24205 | 0.043056 | 0.17784 | 0.2615 | 0.50355 | -0.002111 | 0.15385 | -0.44231 | -0.065177 | 0.054119 | -0.07196 | 0.37035 | 0.094269 | 0.056263 | 122.948 | 122.9029 | 123.0588 | 62.7737 | -123.147 | 122.8398 | 122.9992 | 122.9612 | 62.5345 | -123.3473
1354.2812 | 123.0927 | -66.6412 | 56.4056 | 0.057412 | -0.10141 | -0.014989 | 0.04355 | -0.02343 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.045017 | 0.10553 | 0.049709 | -66.555 | -3.8721 | -66.6041 | 56.3526 | 56.3257 | 56.4771 | -66.8238 | -66.5917 | -4.1846 | -66.6537 | 56.2581 | 56.4221 | 56.3887 | -67.0286 | -0.18254 | -0.053077 | 0.086258 | 0.037157 | 0.2197 | -0.07993 | 0.071451 | -0.38738 | -0.14757 | 0.049526 | -0.012451 | 0.37493 | 0.01645 | -0.016978 | 122.9938 | 122.9669 | 123.1183 | 62.7691 | -123.2294 | 122.8993 | 123.0633 | 123.0299 | 62.4567 | -123.4343
1355.2656 | 123.2208 | -66.6 | 56.3507 | 0.026888 | -0.10141 | -0.014989 | 0.042482 | -0.02343 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.047154 | 0.10446 | 0.050777 | -66.5824 | -3.8767 | -66.6087 | 56.3617 | 56.3257 | 56.4817 | -66.8192 | -66.5871 | -4.1983 | -66.6628 | 56.2626 | 56.4267 | 56.3887 | -67.0286 | -0.21916 | 0.011012 | 0.01759 | -0.008619 | 0.21054 | -0.024998 | 0.13096 | -0.42858 | -0.088064 | 0.012907 | -0.062806 | 0.36577 | 0.07596 | 0.037954 | 122.9618 | 122.9257 | 123.0817 | 62.7234 | -123.1699 | 122.8627 | 123.0267 | 122.9887 | 62.4017 | -123.3793
1356.2656 | 123.2437 | -66.6092 | 56.3416 | 0.026888 | -0.10141 | -0.014989 | 0.044618 | -0.022362 | 0.054873 | 0.058145 | -0.0079177 | 0.0032574 | 0.047154 | 0.10125 | 0.047572 | -66.5779 | -3.8675 | -66.6041 | 56.3571 | 56.3257 | 56.4862 | -66.8238 | -66.5871 | -4.1892 | -66.6583 | 56.2581 | 56.4129 | 56.3887 | -67.0332 | -0.21459 | 0.015589 | 0.031323 | 0.005114 | 0.2197 | -0.015843 | 0.1447 | -0.424 | -0.083488 | 0.022062 | -0.049073 | 0.37493 | 0.071379 | 0.047109 | 122.9663 | 122.9349 | 123.0954 | 62.7417 | -123.1653 | 122.8673 | 123.0221 | 122.9979 | 62.42 | -123.3747
1357.2656 | 123.2254 | -66.5863 | 56.3736 | 0.04215 | -0.10141 | -0.014989 | 0.044618 | -0.024498 | 0.054873 | 0.073406 | -0.0079177 | 0.0032574 | 0.047154 | 0.10446 | 0.047572 | -66.5779 | -3.8675 | -66.6087 | 56.3526 | 56.3211 | 56.4908 | -66.8146 | -66.5963 | -4.2029 | -66.6583 | 56.2626 | 56.4221 | 56.3932 | -67.0286 | -0.22831 | -0.021033 | 0.008435 | -0.022352 | 0.20596 | -0.052465 | 0.11723 | -0.44231 | -0.11095 | -0.009983 | -0.071961 | 0.37035 | 0.048494 | 0.019645 | 122.9389 | 122.9074 | 123.0771 | 62.7188 | -123.1882 | 122.8489 | 123.0084 | 122.9795 | 62.3834 | -123.4022
1358.2656 | 123.2162 | -66.6092 | 56.3553 | 0.026888 | -0.10141 | -0.014989 | 0.04355 | -0.021293 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.046085 | 0.10339 | 0.049709 | -66.5779 | -3.8584 | -66.6132 | 56.3571 | 56.3303 | 56.4908 | -66.8238 | -66.5963 | -4.2029 | -66.6537 | 56.2626 | 56.4221 | 56.3887 | -67.0286 | -0.21459 | 0.001856 | 0.031323 | -0.004043 | 0.21054 | -0.024997 | 0.13554 | -0.41942 | -0.092642 | 0.012905 | -0.044494 | 0.37493 | 0.066804 | 0.033376 | 122.9663 | 122.9395 | 123.1 | 62.7508 | -123.1791 | 122.8718 | 123.0313 | 122.9979 | 62.4063 | -123.3839
1359.2812 | 123.1155 | -66.655 | 56.3828 | 0.011626 | -0.10248 | -0.016058 | 0.044618 | -0.024498 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.046085 | 0.10339 | 0.050777 | -66.5779 | -3.8629 | -66.6087 | 56.3755 | 56.3303 | 56.4862 | -66.8238 | -66.5871 | -4.1937 | -66.6537 | 56.2581 | 56.4221 | 56.3887 | -67.0286 | -0.16881 | -0.007296 | 0.077099 | 0.046312 | 0.21512 | -0.052462 | 0.1035 | -0.37365 | -0.12469 | 0.067838 | 0.001282 | 0.37493 | 0.039339 | 0.005911 | 123.0304 | 122.9853 | 123.1412 | 62.792 | -123.2065 | 122.913 | 123.0771 | 123.0436 | 62.4612 | -123.4114
1360.2656 | 128.3249 | -66.6412 | 56.3187 | -0.0036356 | -0.10141 | -0.014989 | 0.04355 | -0.02343 | 0.055941 | 0.042884 | -0.0079177 | 0.0032574 | 0.046085 | 0.10446 | 0.048641 | -66.5779 | -3.8538 | -66.6087 | 56.3663 | 56.3257 | 56.4862 | -66.8284 | -66.5963 | -4.1937 | -66.6628 | 56.2581 | 56.4267 | 56.3932 | -67.0332 | -0.18712 | 0.047633 | 0.063366 | 0.032579 | 0.2197 | 0.007045 | 0.16758 | -0.39196 | -0.0606 | 0.044948 | -0.021608 | 0.37035 | 0.108 | 0.074576 | 123.0075 | 122.9669 | 123.1275 | 62.7875 | -123.147 | 122.8993 | 123.0679 | 123.0345 | 62.4475 | -123.3519
1361.2656 | 129.5242 | -66.6 | 56.3324 | 0.026888 | -0.10141 | -0.014989 | 0.04355 | -0.024498 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.043949 | 0.10446 | 0.048641 | -66.6282 | -3.7897 | -66.4576 | 56.3709 | 56.3257 | 56.4908 | -66.8192 | -66.5184 | -4.061 | -66.6628 | 56.2626 | 56.4175 | 56.3932 | -67.0286 | -0.21916 | 0.03848 | -0.028194 | 0.14246 | 0.36163 | -0.006687 | 0.15843 | -0.42858 | -0.069753 | 0.081588 | -0.062806 | 0.36577 | 0.085114 | 0.060844 | 122.9709 | 122.9257 | 123.0909 | 62.8104 | -123.1516 | 122.8627 | 123.0175 | 122.9933 | 62.5391 | -123.361
1362.2656 | 131.163 | -66.6138 | 56.3461 | 0.057412 | -0.10248 | -0.016058 | 0.04355 | -0.02343 | 0.053805 | 0.058145 | -0.0068487 | 0.0032574 | 0.045017 | 0.10446 | 0.048641 | -66.4909 | -3.808 | -66.4622 | 56.3663 | 56.3349 | 56.4817 | -66.8284 | -66.5139 | -4.0655 | -66.6583 | 56.2581 | 56.4221 | 56.3932 | -67.0286 | -0.21459 | 0.020168 | 0.12289 | 0.15162 | 0.3662 | -0.011262 | 0.13554 | -0.41485 | -0.088065 | 0.0999 | -0.044495 | 0.37035 | 0.07596 | 0.047111 | 122.9801 | 122.9486 | 123.0954 | 62.8058 | -123.1745 | 122.8718 | 123.0359 | 123.007 | 62.5482 | -123.3747
1363.2656 | 123.1796 | -66.6367 | 56.3278 | 0.026888 | -0.10248 | -0.013921 | 0.04355 | -0.022362 | 0.055941 | 0.058145 | -0.010054 | 0.0032574 | 0.045017 | 0.10553 | 0.048641 | -66.587 | -3.8217 | -66.6178 | 56.3617 | 56.3257 | 56.4817 | -66.8284 | -66.5963 | -4.1892 | -66.6583 | 56.2535 | 56.4267 | 56.3932 | -67.0332 | -0.1917 | 0.0339 | 0.049632 | 0.018845 | 0.21054 | -0.00211 | 0.15385 | -0.39654 | -0.074333 | 0.040371 | -0.021607 | 0.37493 | 0.098848 | 0.065421 | 122.9984 | 122.9624 | 123.1183 | 62.8149 | -123.1562 | 122.8901 | 123.0633 | 123.0299 | 62.4475 | -123.361
1364.2656 | 123.175 | -66.6275 | 56.3782 | 0.011626 | -0.10141 | -0.013921 | 0.044618 | -0.024498 | 0.052737 | 0.058145 | -0.0089857 | 0.0021894 | 0.045017 | 0.10446 | 0.048641 | -66.587 | -3.8217 | -66.6178 | 56.3709 | 56.3394 | 56.4954 | -66.8329 | -66.5963 | -4.1846 | -66.6583 | 56.2672 | 56.4221 | 56.3932 | -67.0332 | -0.20543 | -0.007297 | 0.040476 | 0.009689 | 0.21512 | -0.038727 | 0.11723 | -0.40569 | -0.11095 | 0.031215 | -0.030763 | 0.37493 | 0.043916 | 0.015067 | 122.9984 | 122.9669 | 123.1229 | 62.8058 | -123.2111 | 122.8947 | 123.0496 | 123.0207 | 62.4429 | -123.4114
1365.2656 | 123.2574 | -66.6046 | 56.3095 | 0.04215 | -0.10355 | -0.016058 | 0.04355 | -0.022362 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.046085 | 0.10553 | 0.046504 | -66.587 | -3.8034 | -66.6087 | 56.3709 | 56.3303 | 56.4862 | -66.8146 | -66.6009 | -4.1846 | -66.6628 | 56.2626 | 56.4221 | 56.3887 | -67.0286 | -0.21 | 0.061368 | 0.017588 | -0.004042 | 0.20596 | 0.02078 | 0.17674 | -0.424 | -0.046865 | 0.003748 | -0.058229 | 0.36577 | 0.11258 | 0.079153 | 122.9755 | 122.9349 | 123.0909 | 62.8012 | -123.1241 | 122.8673 | 123.0267 | 122.9933 | 62.42 | -123.3381
1366.2656 | 123.2391 | -66.6183 | 56.3141 | 0.057412 | -0.10248 | -0.016058 | 0.04355 | -0.024498 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.046085 | 0.10446 | 0.048641 | -66.5962 | -3.7988 | -66.6041 | 56.3571 | 56.3211 | 56.4771 | -66.8192 | -66.5917 | -4.1846 | -66.6583 | 56.2626 | 56.4267 | 56.3887 | -67.0332 | -0.20085 | 0.043055 | 0.022165 | 0.014269 | 0.21512 | 0.007044 | 0.163 | -0.41485 | -0.051443 | 0.026638 | -0.039918 | 0.37493 | 0.11258 | 0.074575 | 122.9755 | 122.9395 | 123.0954 | 62.8195 | -123.1333 | 122.881 | 123.045 | 123.007 | 62.4338 | -123.3473
1367.2656 | 123.2483 | -66.6138 | 56.3232 | 0.04215 | -0.10248 | -0.014989 | 0.042482 | -0.02343 | 0.055941 | 0.058145 | -0.0089857 | 5.2373e-05 | 0.045017 | 0.1066 | 0.047572 | -66.587 | -3.7943 | -66.6132 | 56.3617 | 56.3257 | 56.4862 | -66.8192 | -66.6054 | -4.1892 | -66.6583 | 56.2581 | 56.4175 | 56.3841 | -67.0332 | -0.20543 | 0.038478 | 0.026744 | 0.000535 | 0.20596 | 0.002468 | 0.16301 | -0.41943 | -0.065177 | 0.008325 | -0.044495 | 0.37493 | 0.094269 | 0.060841 | 122.9755 | 122.9395 | 123.1 | 62.8195 | -123.1424 | 122.8718 | 123.0313 | 122.9979 | 62.4246 | -123.3564
1368.2656 | 123.1384 | -66.6458 | 56.3644 | 0.04215 | -0.10248 | -0.013921 | 0.04355 | -0.02343 | 0.052737 | 0.073406 | -0.0089857 | 0.0021894 | 0.046085 | 0.10553 | 0.047572 | -66.5824 | -3.7805 | -66.6132 | 56.3617 | 56.3257 | 56.4862 | -66.8238 | -66.5871 | -4.1892 | -66.6674 | 56.2535 | 56.4221 | 56.3932 | -67.024 | -0.17796 | -0.002721 | 0.063366 | 0.032578 | 0.21054 | -0.038731 | 0.12181 | -0.37822 | -0.11095 | 0.058683 | -0.021609 | 0.35662 | 0.057649 | 0.0288 | 123.0075 | 122.9715 | 123.1321 | 62.8653 | -123.1882 | 122.8993 | 123.0679 | 123.0391 | 62.4567 | -123.3885
1369.2656 | 123.1567 | -66.6183 | 56.3828 | 0.057412 | -0.10462 | -0.013921 | 0.044618 | -0.02343 | 0.053805 | 0.088667 | -0.0089857 | 0.0021894 | 0.046085 | 0.10339 | 0.049709 | -66.5916 | -3.7897 | -66.6178 | 56.3617 | 56.3303 | 56.4817 | -66.8284 | -66.5963 | -4.1892 | -66.6583 | 56.2626 | 56.4175 | 56.3841 | -67.0332 | -0.21001 | -0.021031 | 0.026743 | 0.000534 | 0.21054 | -0.052462 | 0.098919 | -0.41485 | -0.12011 | 0.02206 | -0.039918 | 0.37493 | 0.03476 | 0.001332 | 122.9801 | 122.9486 | 123.1 | 62.8287 | -123.2111 | 122.881 | 123.0359 | 123.0024 | 62.4292 | -123.4159
1370.2656 | 123.1934 | -66.6275 | 56.3461 | 0.057412 | -0.10355 | -0.013921 | 0.04355 | -0.022362 | 0.054873 | 0.042884 | -0.0089857 | 0.0021894 | 0.046085 | 0.10553 | 0.048641 | -66.5779 | -3.7851 | -66.6178 | 56.3663 | 56.3303 | 56.4908 | -66.8146 | -66.6009 | -4.1983 | -66.6583 | 56.2626 | 56.4221 | 56.3887 | -67.0378 | -0.18712 | 0.020168 | 0.049633 | 0.009689 | 0.19681 | -0.015841 | 0.1447 | -0.41027 | -0.083486 | 0.026636 | -0.030763 | 0.37951 | 0.07596 | 0.042532 | 122.9938 | 122.9578 | 123.1183 | 62.8424 | -123.1607 | 122.8901 | 123.0496 | 123.0162 | 62.4292 | -123.3839
1371.2656 | 123.2529 | -66.6229 | 56.3141 | 0.011626 | -0.10355 | -0.014989 | 0.044618 | -0.024498 | 0.054873 | 0.042884 | -0.0079177 | 0.0011204 | 0.042881 | 0.10553 | 0.048641 | -66.5916 | -3.7714 | -66.6178 | 56.3663 | 56.3211 | 56.4817 | -66.8192 | -66.5963 | -4.1846 | -66.6628 | 56.2489 | 56.4312 | 56.3795 | -67.0332 | -0.19627 | 0.052211 | 0.031321 | 0.005112 | 0.20139 | 0.007044 | 0.16758 | -0.41027 | -0.065179 | 0.026638 | -0.039918 | 0.37035 | 0.11716 | 0.065418 | 122.9892 | 122.9441 | 123.1046 | 62.8516 | -123.1333 | 122.8718 | 123.0542 | 123.0024 | 62.4383 | -123.3473
1372.2656 | 123.1384 | -66.6595 | 56.3461 | 0.04215 | -0.10355 | -0.013921 | 0.04355 | -0.02343 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.043949 | 0.10446 | 0.047572 | -66.5916 | -3.7576 | -66.6132 | 56.3571 | 56.2937 | 56.4817 | -66.8192 | -66.5963 | -4.1937 | -66.6491 | 56.2535 | 56.4175 | 56.3841 | -67.0286 | -0.15965 | 0.011012 | 0.067942 | 0.046311 | 0.20596 | -0.052473 | 0.13554 | -0.36907 | -0.092643 | 0.063259 | 0.010439 | 0.37951 | 0.071381 | 0.037953 | 123.0167 | 122.9532 | 123.1412 | 62.9019 | -123.1653 | 122.913 | 123.0771 | 123.0436 | 62.4658 | -123.3747
1373.2656 | 123.262 | -66.6183 | 56.3095 | 0.04215 | -0.10355 | -0.016058 | 0.042482 | -0.024498 | 0.054873 | 0.042884 | -0.0089857 | 0.0021894 | 0.045017 | 0.1066 | 0.047572 | -66.5916 | -3.7485 | -66.6178 | 56.3571 | 56.2845 | 56.4817 | -66.81 | -66.5963 | -4.1846 | -66.6628 | 56.2626 | 56.4221 | 56.3749 | -67.0286 | -0.19169 | 0.047633 | 0.026743 | 0.000534 | 0.19223 | -0.02501 | 0.17216 | -0.41027 | -0.046865 | 0.02206 | -0.044496 | 0.36577 | 0.11258 | 0.065417 | 122.9755 | 122.9028 | 123.1 | 62.8699 | -123.1195 | 122.881 | 123.0404 | 122.9933 | 62.4338 | -123.3381
1374.2812 | 123.2071 | -66.5909 | 56.3873 | 0.04215 | -0.10248 | -0.017126 | 0.04355 | -0.022362 | 0.052737 | 0.042884 | -0.0089857 | 0.0021894 | 0.046085 | 0.1066 | 0.048641 | -66.587 | -3.753 | -66.6132 | 56.3571 | 56.312 | 56.4817 | -66.8238 | -66.6054 | -4.1754 | -66.6628 | 56.2581 | 56.4221 | 56.3887 | -67.0286 | -0.2329 | -0.030187 | 0.003855 | -0.022354 | 0.21054 | -0.075356 | 0.094341 | -0.43774 | -0.12926 | -0.014564 | -0.071962 | 0.36577 | 0.034761 | 0.001333 | 122.948 | 122.9029 | 123.0726 | 62.8378 | -123.2111 | 122.8489 | 123.013 | 122.9795 | 62.4155 | -123.4159
1375.2656 | 131.6986 | -66.6275 | 56.3232 | 0.04215 | -0.10782 | -0.016058 | 0.044618 | -0.02343 | 0.054873 | 0.027623 | -0.011122 | 0.0011204 | 0.045017 | 0.10446 | 0.048641 | -66.9167 | -3.0663 | -66.1737 | 56.3571 | 56.3166 | 56.4725 | -66.8192 | -66.0011 | -3.8274 | -66.6262 | 56.2535 | 56.4175 | 56.3795 | -67.0332 | -0.1917 | 0.0339 | -0.28917 | 0.45378 | 0.64548 | -0.00669 | 0.14927 | -0.40569 | -0.069755 | 0.62645 | 0.001288 | 0.40698 | 0.094269 | 0.056263 | 122.9846 | 122.9441 | 123.1 | 63.5612 | -123.1424 | 122.881 | 123.045 | 123.007 | 62.8001 | -123.3564
1376.2656 | 129.7989 | -66.6046 | 56.337 | 0.026888 | -0.10462 | -0.013921 | 0.04355 | -0.026635 | 0.053805 | 0.042884 | -0.0089857 | 0.0032574 | 0.043949 | 0.10446 | 0.048641 | -66.8388 | -3.2311 | -66.1966 | 56.3663 | 56.3211 | 56.4862 | -66.8238 | -66.1476 | -3.9602 | -66.6354 | 56.2581 | 56.4175 | 56.3795 | -67.0378 | -0.21916 | 0.029323 | -0.23422 | 0.408 | 0.62717 | -0.015844 | 0.14927 | -0.43316 | -0.07891 | 0.45704 | -0.030757 | 0.4024 | 0.080536 | 0.04253 | 122.9709 | 122.9257 | 123.0909 | 63.3735 | -123.1608 | 122.8627 | 123.0221 | 122.9841 | 62.6444 | -123.3747
1377.2656 | 131.4056 | -66.5771 | 56.3095 | 0.026888 | -0.10462 | -0.014989 | 0.045687 | -0.024498 | 0.055941 | 0.058145 | -0.0079177 | 0.0032574 | 0.045017 | 0.10553 | 0.047572 | -66.8159 | -3.1761 | -66.192 | 56.3617 | 56.3211 | 56.4725 | -66.8192 | -66.2163 | -3.9694 | -66.6171 | 56.2535 | 56.4221 | 56.3795 | -67.0332 | -0.24205 | 0.052211 | -0.2388 | 0.38511 | 0.62717 | 0.011622 | 0.163 | -0.45605 | -0.056022 | 0.36089 | -0.039908 | 0.41614 | 0.11258 | 0.069996 | 122.9389 | 122.8983 | 123.0497 | 63.401 | -123.1287 | 122.8306 | 122.9992 | 122.9567 | 62.6078 | -123.3427
1378.2656 | 133.2779 | -66.5726 | 56.3141 | 0.011626 | -0.10462 | -0.014989 | 0.045687 | -0.024498 | 0.05701 | 0.042884 | -0.0079177 | 0.0021894 | 0.043949 | 0.1066 | 0.048641 | -66.381 | -2.8877 | -66.0867 | 56.3617 | 56.3257 | 56.4679 | -66.8192 | -66.143 | -3.8366 | -66.6445 | 56.2581 | 56.4084 | 56.3749 | -67.024 | -0.24663 | 0.047633 | 0.19157 | 0.48584 | 0.73247 | 0.011623 | 0.15385 | -0.45147 | -0.056022 | 0.42958 | -0.071958 | 0.37951 | 0.094267 | 0.060839 | 122.9343 | 122.8983 | 123.0405 | 63.6849 | -123.1333 | 122.8306 | 122.9809 | 122.9475 | 62.736 | -123.3381
1379.2656 | 123.2071 | -66.6092 | 56.3736 | 0.04215 | -0.10355 | -0.014989 | 0.045687 | -0.02343 | 0.054873 | 0.058145 | -0.010054 | 0.0021894 | 0.046085 | 0.1066 | 0.046504 | -66.5824 | -3.7118 | -66.6132 | 56.3571 | 56.3257 | 56.4908 | -66.8284 | -66.6054 | -4.1754 | -66.6628 | 56.2626 | 56.4267 | 56.3887 | -67.0332 | -0.21916 | -0.016454 | 0.026745 | -0.004043 | 0.21512 | -0.047886 | 0.11723 | -0.424 | -0.11095 | 0.003747 | -0.053651 | 0.37035 | 0.053072 | 0.015066 | 122.9663 | 122.9349 | 123.1 | 62.8974 | -123.202 | 122.8718 | 123.0359 | 122.9979 | 62.4338 | -123.4068
1380.2656 | 123.1293 | -66.6458 | 56.337 | 0.026888 | -0.10355 | -0.016058 | 0.042482 | -0.024498 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.046085 | 0.1066 | 0.047572 | -66.587 | -3.7073 | -66.6178 | 56.3571 | 56.3257 | 56.4908 | -66.8238 | -66.5963 | -4.18 | -66.6628 | 56.2626 | 56.4267 | 56.3978 | -67.0286 | -0.17796 | 0.020167 | 0.058787 | 0.028 | 0.20596 | -0.011265 | 0.15385 | -0.3828 | -0.074331 | 0.049526 | -0.01703 | 0.36577 | 0.089693 | 0.060844 | 123.003 | 122.9715 | 123.1366 | 62.9386 | -123.1608 | 122.9085 | 123.0725 | 123.0436 | 62.4658 | -123.3656
1381.2656 | 123.2437 | -66.6458 | 56.3141 | 0.04215 | -0.10248 | -0.017126 | 0.044618 | -0.02343 | 0.054873 | 0.042884 | -0.0068487 | 0.0021894 | 0.043949 | 0.10339 | 0.048641 | -66.5916 | -3.6981 | -66.6132 | 56.3663 | 56.3257 | 56.4862 | -66.8238 | -66.5963 | -4.1754 | -66.6537 | 56.2672 | 56.4175 | 56.3841 | -67.0332 | -0.17796 | 0.052211 | 0.054209 | 0.032578 | 0.21054 | 0.011623 | 0.17216 | -0.38738 | -0.046865 | 0.049526 | -0.007873 | 0.37951 | 0.10342 | 0.069996 | 123.0121 | 122.9715 | 123.1321 | 62.9477 | -123.1379 | 122.913 | 123.0633 | 123.0299 | 62.4704 | -123.3473
1382.2656 | 123.1659 | -66.6458 | 56.3553 | 0.057412 | -0.10355 | -0.012852 | 0.04355 | -0.022362 | 0.054873 | 0.027623 | -0.0089857 | 0.0021894 | 0.045017 | 0.10553 | 0.048641 | -66.587 | -3.6935 | -66.6132 | 56.3571 | 56.3303 | 56.4817 | -66.8329 | -66.6009 | -4.1708 | -66.6537 | 56.2581 | 56.4175 | 56.3932 | -67.0332 | -0.18712 | 0.001856 | 0.058787 | 0.032578 | 0.2197 | -0.024997 | 0.12638 | -0.38738 | -0.097221 | 0.044947 | -0.007873 | 0.37951 | 0.062225 | 0.037955 | 123.003 | 122.9761 | 123.1275 | 62.9523 | -123.1882 | 122.9039 | 123.0633 | 123.0391 | 62.475 | -123.3885
1383.2656 | 123.0972 | -66.6275 | 56.3736 | 0.026888 | -0.10462 | -0.013921 | 0.04355 | -0.022362 | 0.054873 | 0.058145 | -0.010054 | 0.0043254 | 0.045017 | 0.1066 | 0.048641 | -66.587 | -3.6935 | -66.6224 | 56.3617 | 56.3257 | 56.4862 | -66.8238 | -66.5917 | -4.1754 | -66.6583 | 56.2535 | 56.4267 | 56.3841 | -67.0332 | -0.19627 | -0.011876 | 0.040476 | 0.005111 | 0.20139 | -0.047886 | 0.11265 | -0.40569 | -0.12011 | 0.035793 | -0.030763 | 0.37493 | 0.053072 | 0.010487 | 122.9892 | 122.9532 | 123.1138 | 62.934 | -123.1974 | 122.881 | 123.0542 | 123.0116 | 62.4521 | -123.4068
1384.2656 | 123.2529 | -66.6183 | 56.3004 | 0.04215 | -0.10462 | -0.013921 | 0.042482 | -0.022362 | 0.055941 | 0.058145 | -0.0089857 | 0.0032574 | 0.046085 | 0.10766 | 0.049709 | -66.5779 | -3.6798 | -66.6224 | 56.3617 | 56.3257 | 56.4862 | -66.8192 | -66.5917 | -4.1754 | -66.6537 | 56.2581 | 56.4221 | 56.3887 | -67.0332 | -0.20085 | 0.061366 | 0.040478 | -0.004044 | 0.19681 | 0.025356 | 0.1859 | -0.41485 | -0.042289 | 0.026638 | -0.035339 | 0.37951 | 0.12174 | 0.088308 | 122.9801 | 122.9441 | 123.1046 | 62.9386 | -123.1196 | 122.8764 | 123.0404 | 123.007 | 62.4429 | -123.3335
1385.2656 | 123.1842 | -66.6321 | 56.3416 | 0.026888 | -0.10248 | -0.016058 | 0.044618 | -0.02343 | 0.05701 | 0.042884 | -0.0079177 | 0.0032574 | 0.045017 | 0.10446 | 0.048641 | -66.5779 | -3.6752 | -66.6178 | 56.3617 | 56.3257 | 56.4908 | -66.8192 | -66.5917 | -4.1708 | -66.6628 | 56.2581 | 56.4221 | 56.3841 | -67.0332 | -0.18712 | 0.020167 | 0.054211 | 0.014267 | 0.20139 | -0.015843 | 0.14927 | -0.40112 | -0.083488 | 0.040371 | -0.030763 | 0.37035 | 0.080537 | 0.04253 | 122.9938 | 122.9578 | 123.1229 | 62.9569 | -123.1608 | 122.8901 | 123.0542 | 123.0162 | 62.4612 | -123.3747
1386.2656 | 123.1247 | -66.6595 | 56.3828 | 0.026888 | -0.10462 | -0.018194 | 0.044618 | -0.024498 | 0.053805 | 0.058145 | -0.010054 | 0.0011204 | 0.045017 | 0.10553 | 0.048641 | -66.5916 | -3.6752 | -66.6178 | 56.3663 | 56.3303 | 56.4862 | -66.8284 | -66.6009 | -4.1708 | -66.6628 | 56.2581 | 56.4221 | 56.3887 | -67.0332 | -0.16881 | -0.016453 | 0.067942 | 0.041733 | 0.21054 | -0.052462 | 0.1035 | -0.37365 | -0.12469 | 0.05868 | -0.003297 | 0.37035 | 0.039339 | 0.005911 | 123.0258 | 122.9898 | 123.1458 | 62.9843 | -123.2111 | 122.9176 | 123.0816 | 123.0482 | 62.4887 | -123.4159
1387.2656 | 123.1522 | -66.6595 | 56.3644 | 0.026888 | -0.10462 | -0.014989 | 0.044618 | -0.02343 | 0.053805 | 0.058145 | -0.010054 | 0.0011204 | 0.047154 | 0.10766 | 0.047572 | -66.587 | -3.6706 | -66.6224 | 56.3755 | 56.3257 | 56.4862 | -66.8238 | -66.5963 | -4.1754 | -66.6628 | 56.2626 | 56.4175 | 56.3841 | -67.0332 | -0.16423 | 0.011014 | 0.07252 | 0.037155 | 0.20139 | -0.038731 | 0.12181 | -0.37365 | -0.1018 | 0.063259 | -0.003297 | 0.37035 | 0.05307 | 0.019642 | 123.035 | 122.9853 | 123.1458 | 62.9889 | -123.1882 | 122.9222 | 123.0771 | 123.0436 | 62.4841 | -123.3976
1388.2656 | 123.1522 | -66.6641 | 56.3599 | 0.04215 | -0.10568 | -0.014989 | 0.045687 | -0.02343 | 0.054873 | 0.058145 | -0.0079177 | 0.0043254 | 0.046085 | 0.10553 | 0.048641 | -66.5916 | -3.6615 | -66.627 | 56.3709 | 56.3303 | 56.4908 | -66.8329 | -66.6054 | -4.1708 | -66.6583 | 56.2581 | 56.4221 | 56.3887 | -67.0378 | -0.16881 | 0.011014 | 0.07252 | 0.037154 | 0.20597 | -0.029574 | 0.13096 | -0.37365 | -0.1018 | 0.058679 | 0.005859 | 0.37951 | 0.062227 | 0.028799 | 123.035 | 122.9944 | 123.155 | 63.0026 | -123.1928 | 122.9222 | 123.0862 | 123.0528 | 62.4933 | -123.3976
1389.2656 | 123.2025 | -66.6183 | 56.3141 | 0.057412 | -0.10355 | -0.014989 | 0.042482 | -0.022362 | 0.054873 | 0.058145 | -0.0079177 | 0.0032574 | 0.047154 | 0.1066 | 0.047572 | -66.587 | -3.6432 | -66.6178 | 56.3663 | 56.3349 | 56.4954 | -66.8329 | -66.6009 | -4.1708 | -66.6674 | 56.2672 | 56.4221 | 56.3887 | -67.0378 | -0.21459 | 0.052211 | 0.031321 | 0.000534 | 0.21512 | 0.020781 | 0.18132 | -0.41943 | -0.046865 | 0.017481 | -0.049075 | 0.37035 | 0.108 | 0.074575 | 122.9846 | 122.9532 | 123.1138 | 62.9752 | -123.147 | 122.8856 | 123.0404 | 123.007 | 62.4475 | -123.3519
1390.2656 | 123.1567 | -66.655 | 56.3599 | 0.04215 | -0.10355 | -0.013921 | 0.044618 | -0.02343 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.043949 | 0.10553 | 0.049709 | -66.587 | -3.6569 | -66.6224 | 56.3709 | 56.3257 | 56.4954 | -66.8329 | -66.5963 | -4.1708 | -66.6583 | 56.2626 | 56.4084 | 56.3932 | -67.0378 | -0.17797 | 0.011014 | 0.067942 | 0.032577 | 0.21054 | -0.034153 | 0.13554 | -0.38281 | -0.097219 | 0.058681 | -0.003297 | 0.37951 | 0.048491 | 0.033378 | 123.0258 | 122.9807 | 123.1504 | 62.9981 | -123.1928 | 122.9176 | 123.0633 | 123.0482 | 62.4841 | -123.3976
1391.2656 | 123.175 | -66.6595 | 56.3644 | 0.026888 | -0.10462 | -0.017126 | 0.04355 | -0.02343 | 0.054873 | 0.027623 | -0.0068487 | 0.0021894 | 0.045017 | 0.1066 | 0.049709 | -66.587 | -3.6477 | -66.6224 | 56.3709 | 56.3349 | 56.4954 | -66.8284 | -66.6054 | -4.1708 | -66.6537 | 56.2626 | 56.4175 | 56.3841 | -67.0332 | -0.16881 | 0.006436 | 0.07252 | 0.037155 | 0.20597 | -0.029573 | 0.13097 | -0.37365 | -0.1018 | 0.054101 | 0.00586 | 0.37951 | 0.05307 | 0.019642 | 123.0304 | 122.9944 | 123.155 | 63.0118 | -123.1928 | 122.9222 | 123.0771 | 123.0436 | 62.4887 | -123.3976
1392.2656 | 123.1659 | -66.6367 | 56.369 | 0.04215 | -0.10568 | -0.014989 | 0.045687 | -0.02343 | 0.052737 | 0.058145 | -0.0068487 | 5.2373e-05 | 0.046085 | 0.10553 | 0.048641 | -66.5824 | -3.6386 | -66.6178 | 56.3709 | 56.3349 | 56.4954 | -66.8329 | -66.6009 | -4.1617 | -66.6674 | 56.2535 | 56.4267 | 56.3978 | -67.0332 | -0.19628 | 0.001858 | 0.054211 | 0.018845 | 0.21512 | -0.034151 | 0.12639 | -0.39654 | -0.11553 | 0.035792 | -0.030764 | 0.36577 | 0.057649 | 0.0288 | 123.0075 | 122.9715 | 123.1321 | 62.9981 | -123.202 | 122.8901 | 123.0633 | 123.0345 | 62.475 | -123.4022
1393.2656 | 123.143 | -66.6504 | 56.3599 | 0.04215 | -0.10568 | -0.014989 | 0.046755 | -0.024498 | 0.052737 | 0.042884 | -0.0079177 | 0.0032574 | 0.046085 | 0.1066 | 0.046504 | -66.587 | -3.634 | -66.6178 | 56.3617 | 56.3349 | 56.4954 | -66.8284 | -66.5917 | -4.1663 | -66.6628 | 56.2581 | 56.4267 | 56.3932 | -67.0286 | -0.17797 | 0.001857 | 0.063365 | 0.032578 | 0.21054 | -0.024995 | 0.13554 | -0.37823 | -0.1018 | 0.058682 | -0.012452 | 0.36577 | 0.066805 | 0.033378 | 123.0121 | 122.9853 | 123.1458 | 63.0164 | -123.1882 | 122.9085 | 123.0771 | 123.0436 | 62.4841 | -123.3885
1394.2656 | 123.2437 | -66.6138 | 56.2958 | 0.04215 | -0.10568 | -0.014989 | 0.044618 | -0.022362 | 0.052737 | 0.073406 | -0.0079177 | 0.0032574 | 0.043949 | 0.1066 | 0.048641 | -66.587 | -3.6432 | -66.6224 | 56.3709 | 56.3303 | 56.4817 | -66.8238 | -66.5963 | -4.1617 | -66.6628 | 56.2581 | 56.4267 | 56.3887 | -67.0286 | -0.21001 | 0.075101 | 0.026744 | -0.008621 | 0.20139 | 0.034513 | 0.18589 | -0.41485 | -0.037711 | 0.017483 | -0.049073 | 0.36577 | 0.13089 | 0.092886 | 122.9846 | 122.9441 | 123.0954 | 62.9706 | -123.1196 | 122.8718 | 123.0404 | 123.0024 | 62.4521 | -123.3244
1395.2656 | 126.7181 | -66.6183 | 56.3599 | 0.026888 | -0.10355 | -0.016058 | 0.045687 | -0.024498 | 0.055941 | 0.058145 | -0.0089857 | 5.2373e-05 | 0.043949 | 0.10873 | 0.046504 | -66.2757 | -3.4509 | -66.0455 | 56.3663 | 56.3257 | 56.5 | -66.8329 | -66.2804 | -3.7679 | -66.6537 | 56.2581 | 56.4221 | 56.3841 | -67.0378 | -0.21459 | 0.006435 | 0.34265 | 0.57282 | 0.78741 | -0.034153 | 0.14012 | -0.41943 | -0.1018 | 0.33799 | -0.035339 | 0.38409 | 0.062227 | 0.02422 | 122.9846 | 122.9441 | 123.1183 | 63.1675 | -123.1928 | 122.8764 | 123.0404 | 123.0024 | 62.8504 | -123.3976
1396.2656 | 126.6724 | -66.6183 | 56.3736 | 0.057412 | -0.10462 | -0.014989 | 0.045687 | -0.02343 | 0.055941 | 0.073406 | -0.0089857 | 0.0032574 | 0.045017 | 0.10446 | 0.047572 | -66.3993 | -3.5012 | -66.0867 | 56.3571 | 56.3257 | 56.4908 | -66.8284 | -66.3033 | -3.7817 | -66.6674 | 56.2581 | 56.4221 | 56.3978 | -67.0332 | -0.21001 | -0.016454 | 0.21904 | 0.53162 | 0.74162 | -0.047886 | 0.11723 | -0.41485 | -0.11553 | 0.3151 | -0.049075 | 0.36577 | 0.048494 | 0.024223 | 122.9755 | 122.9441 | 123.1092 | 63.1171 | -123.202 | 122.8764 | 123.0404 | 123.0162 | 62.8367 | -123.4068
1397.2656 | 123.2025 | -66.6412 | 56.3644 | 0.04215 | -0.10355 | -0.017126 | 0.045687 | -0.02343 | 0.055941 | 0.073406 | -0.0089857 | 0.0032574 | 0.046085 | 0.10873 | 0.046504 | -66.5138 | -3.6157 | -66.6132 | 56.3617 | 56.3349 | 56.4862 | -66.8284 | -66.5963 | -4.1388 | -66.6628 | 56.2626 | 56.4221 | 56.3887 | -67.0424 | -0.18712 | -0.002721 | 0.12746 | 0.028 | 0.21512 | -0.029573 | 0.12181 | -0.40112 | -0.1018 | 0.044948 | -0.021608 | 0.37951 | 0.057649 | 0.024221 | 123.003 | 122.9761 | 123.1275 | 63.0255 | -123.1928 | 122.9039 | 123.0633 | 123.0299 | 62.5024 | -123.4068
1398.2656 | 123.175 | -66.6367 | 56.3965 | 0.04215 | -0.10568 | -0.014989 | 0.046755 | -0.024498 | 0.053805 | 0.058145 | -0.0089857 | 0.0021894 | 0.043949 | 0.1066 | 0.049709 | -66.5916 | -3.6111 | -66.6224 | 56.3617 | 56.3257 | 56.4862 | -66.8284 | -66.6054 | -4.1617 | -66.6583 | 56.2535 | 56.4267 | 56.3795 | -67.0378 | -0.1917 | -0.034764 | 0.045054 | 0.014267 | 0.20597 | -0.070774 | 0.089765 | -0.40112 | -0.143 | 0.031213 | -0.021607 | 0.37951 | 0.030184 | -0.016979 | 122.9984 | 122.9624 | 123.1229 | 63.0255 | -123.2248 | 122.8901 | 123.0633 | 123.0162 | 62.475 | -123.4343
1399.2656 | 123.2712 | -66.6138 | 56.3095 | 0.026888 | -0.10462 | -0.016058 | 0.045687 | -0.02343 | 0.055941 | 0.042884 | -0.0089857 | 0.0021894 | 0.043949 | 0.10766 | 0.048641 | -66.5824 | -3.6065 | -66.6178 | 56.3617 | 56.3257 | 56.4862 | -66.8238 | -66.5917 | -4.1708 | -66.6628 | 56.2581 | 56.4312 | 56.3887 | -67.0378 | -0.21001 | 0.052211 | 0.031323 | -0.004043 | 0.20596 | 0.016201 | 0.17674 | -0.424 | -0.051444 | 0.022061 | -0.049073 | 0.37493 | 0.12174 | 0.079153 | 122.9755 | 122.9395 | 123.1 | 63.0072 | -123.1333 | 122.8718 | 123.045 | 123.0024 | 62.4429 | -123.3473
1400.2656 | 123.1338 | -66.6458 | 56.3782 | 0.04215 | -0.10568 | -0.013921 | 0.042482 | -0.024498 | 0.054873 | 0.058145 | -0.010054 | 0.0032574 | 0.045017 | 0.10766 | 0.047572 | -66.587 | -3.602 | -66.6178 | 56.3617 | 56.3166 | 56.4817 | -66.8192 | -66.5917 | -4.1708 | -66.6628 | 56.2626 | 56.4267 | 56.3887 | -67.0332 | -0.17338 | -0.016454 | 0.058787 | 0.028 | 0.20139 | -0.061622 | 0.1035 | -0.38738 | -0.11553 | 0.054104 | -0.01703 | 0.37035 | 0.048494 | 0.010488 | 123.0075 | 122.9624 | 123.1275 | 63.0439 | -123.1974 | 122.9085 | 123.0725 | 123.0345 | 62.475 | -123.4114
1401.2656 | 123.2346 | -66.6321 | 56.337 | 0.072674 | -0.10355 | -0.016058 | 0.044618 | -0.024498 | 0.055941 | 0.058145 | -0.0089857 | 0.0043254 | 0.045017 | 0.1066 | 0.047572 | -66.5916 | -3.5974 | -66.6178 | 56.3571 | 56.3257 | 56.4862 | -66.8192 | -66.5917 | -4.1708 | -66.6674 | 56.2535 | 56.4267 | 56.3932 | -67.0424 | -0.18712 | 0.020167 | 0.040476 | 0.014267 | 0.20139 | -0.011265 | 0.14927 | -0.41027 | -0.083488 | 0.040371 | -0.035342 | 0.37493 | 0.089693 | 0.056266 | 122.9892 | 122.9578 | 123.1183 | 63.0347 | -123.1562 | 122.8856 | 123.0587 | 123.0253 | 62.4612 | -123.3793
1402.2656 | 123.1384 | -66.6504 | 56.3965 | 0.057412 | -0.10462 | -0.014989 | 0.044618 | -0.022362 | 0.054873 | 0.073406 | -0.010054 | 0.0021894 | 0.045017 | 0.1066 | 0.047572 | -66.5916 | -3.5882 | -66.6224 | 56.3571 | 56.3257 | 56.4862 | -66.8238 | -66.6009 | -4.1663 | -66.6674 | 56.2535 | 56.4267 | 56.3932 | -67.0286 | -0.17339 | -0.039342 | 0.058787 | 0.028 | 0.20139 | -0.070774 | 0.089765 | -0.37823 | -0.143 | 0.049525 | -0.017031 | 0.36119 | 0.030184 | -0.003243 | 123.0075 | 122.9761 | 123.1366 | 63.0622 | -123.2203 | 122.9039 | 123.0771 | 123.0436 | 62.4841 | -123.4251
1403.2656 | 123.143 | -66.6412 | 56.3782 | 0.026888 | -0.10568 | -0.013921 | 0.044618 | -0.024498 | 0.055941 | 0.058145 | -0.0089857 | 0.0011204 | 0.045017 | 0.1066 | 0.048641 | -66.5916 | -3.5882 | -66.6224 | 56.3571 | 56.3211 | 56.4954 | -66.8192 | -66.6009 | -4.1617 | -66.6583 | 56.2535 | 56.4221 | 56.3887 | -67.0378 | -0.17796 | -0.021032 | 0.049631 | 0.018844 | 0.19681 | -0.057043 | 0.11723 | -0.39654 | -0.12469 | 0.040369 | -0.01703 | 0.37951 | 0.043916 | 0.010488 | 122.9984 | 122.9624 | 123.1366 | 63.053 | -123.1974 | 122.8947 | 123.0633 | 123.0299 | 62.4795 | -123.4159
1404.2656 | 123.2574 | -66.5863 | 56.3553 | 0.026888 | -0.10355 | -0.014989 | 0.044618 | -0.025567 | 0.055941 | 0.058145 | -0.0089857 | 0.0043254 | 0.046085 | 0.10873 | 0.048641 | -66.587 | -3.5882 | -66.6178 | 56.3526 | 56.3166 | 56.4908 | -66.8192 | -66.5963 | -4.1571 | -66.6583 | 56.2581 | 56.4267 | 56.3887 | -67.0286 | -0.23289 | -0.002723 | -0.000722 | -0.031509 | 0.20139 | -0.038734 | 0.13554 | -0.44231 | -0.097221 | -0.009983 | -0.071961 | 0.37035 | 0.071382 | 0.033376 | 122.9389 | 122.9029 | 123.0771 | 62.9981 | -123.1745 | 122.8444 | 123.013 | 122.975 | 62.4292 | -123.3839
1405.2656 | 123.1842 | -66.6321 | 56.3828 | 0.057412 | -0.10462 | -0.014989 | 0.044618 | -0.025567 | 0.054873 | 0.042884 | -0.0089857 | 0.0011204 | 0.045017 | 0.1066 | 0.048641 | -66.5962 | -3.5836 | -66.6178 | 56.3617 | 56.3349 | 56.4862 | -66.8284 | -66.6009 | -4.1708 | -66.6537 | 56.2626 | 56.4267 | 56.3841 | -67.0332 | -0.19628 | -0.021031 | 0.035898 | 0.014267 | 0.21054 | -0.047883 | 0.1035 | -0.40112 | -0.12011 | 0.031214 | -0.021606 | 0.37951 | 0.043917 | 0.001332 | 122.9938 | 122.9669 | 123.1183 | 63.0484 | -123.2111 | 122.8947 | 123.0587 | 123.0162 | 62.4612 | -123.4159
1406.2656 | 123.111 | -66.5817 | 56.369 | 0.072674 | -0.10462 | -0.013921 | 0.044618 | -0.025567 | 0.053805 | 0.027623 | -0.0089857 | 0.0032574 | 0.046085 | 0.1066 | 0.047572 | -66.587 | -3.5791 | -66.6178 | 56.3617 | 56.3303 | 56.4908 | -66.8284 | -66.5963 | -4.1663 | -66.6628 | 56.2581 | 56.4267 | 56.3887 | -67.0332 | -0.24663 | -0.007299 | -0.0053 | -0.036087 | 0.21054 | -0.03873 | 0.12181 | -0.45147 | -0.11095 | -0.014561 | -0.081117 | 0.37035 | 0.057649 | 0.019643 | 122.9434 | 122.912 | 123.0726 | 63.0027 | -123.1974 | 122.8398 | 123.0084 | 122.9704 | 62.4155 | -123.4022
1407.2656 | 123.1842 | -66.6275 | 56.3965 | 0.026888 | -0.10568 | -0.014989 | 0.045687 | -0.022362 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.046085 | 0.10766 | 0.047572 | -66.5916 | -3.5836 | -66.6224 | 56.3571 | 56.3349 | 56.4908 | -66.8284 | -66.5963 | -4.1617 | -66.6628 | 56.2535 | 56.4312 | 56.3841 | -67.0332 | -0.20085 | -0.039342 | 0.035898 | 0.005111 | 0.20597 | -0.061616 | 0.094343 | -0.40569 | -0.143 | 0.031215 | -0.035341 | 0.37035 | 0.034763 | -0.012401 | 122.9846 | 122.9624 | 123.1183 | 63.0439 | -123.2248 | 122.881 | 123.0587 | 123.0116 | 62.4658 | -123.4297
1408.2656 | 123.3261 | -66.5771 | 56.3187 | 0.04215 | -0.10462 | -0.013921 | 0.045687 | -0.025567 | 0.052737 | 0.058145 | -0.0089857 | 0.0021894 | 0.042881 | 0.1066 | 0.047572 | -66.5962 | -3.5791 | -66.6224 | 56.3663 | 56.3211 | 56.4908 | -66.8284 | -66.6009 | -4.1617 | -66.6674 | 56.2626 | 56.4312 | 56.3841 | -67.0332 | -0.25121 | 0.047633 | -0.019034 | -0.045243 | 0.20597 | 0.002466 | 0.17216 | -0.45605 | -0.056021 | -0.023718 | -0.090274 | 0.36577 | 0.11258 | 0.065418 | 122.9434 | 122.8983 | 123.068 | 62.9981 | -123.147 | 122.8398 | 123.0084 | 122.9612 | 62.4155 | -123.3519
1409.2656 | 123.2803 | -66.6641 | 56.3782 | 0.011626 | -0.10675 | -0.016058 | 0.047824 | -0.02343 | 0.054873 | 0.058145 | -0.011122 | 0.0021894 | 0.046085 | 0.10766 | 0.046504 | -66.587 | -3.5745 | -66.6132 | 56.3617 | 56.3303 | 56.4908 | -66.8329 | -66.6054 | -4.1617 | -66.6583 | 56.2672 | 56.4312 | 56.3932 | -67.0378 | -0.16881 | -0.016454 | 0.077098 | 0.050889 | 0.2197 | -0.047885 | 0.11265 | -0.37365 | -0.11095 | 0.058679 | 0.005859 | 0.37951 | 0.053073 | 0.015067 | 123.0258 | 122.9944 | 123.155 | 63.0896 | -123.2111 | 122.9313 | 123.0954 | 123.0574 | 62.5024 | -123.4159
1410.2656 | 123.3078 | -66.5863 | 56.3278 | 0.057412 | -0.10462 | -0.014989 | 0.045687 | -0.02343 | 0.055941 | 0.073406 | -0.010054 | 0.0021894 | 0.046085 | 0.1066 | 0.048641 | -66.5916 | -3.5653 | -66.6087 | 56.3663 | 56.3349 | 56.5 | -66.8284 | -66.5917 | -4.1525 | -66.6583 | 56.2535 | 56.4267 | 56.3887 | -67.0378 | -0.24205 | 0.038478 | -0.0053 | -0.022352 | 0.2197 | 0.007048 | 0.17216 | -0.45147 | -0.074333 | -0.005405 | -0.071961 | 0.37951 | 0.098848 | 0.060842 | 122.9526 | 122.9212 | 123.0863 | 63.021 | -123.1562 | 122.8398 | 123.013 | 122.975 | 62.4338 | -123.3656
1411.2656 | 123.2391 | -66.6138 | 56.3599 | 0.04215 | -0.10675 | -0.018194 | 0.045687 | -0.024498 | 0.055941 | 0.012362 | -0.0089857 | 0.0021894 | 0.046085 | 0.10766 | 0.048641 | -66.5962 | -3.5562 | -66.6224 | 56.3663 | 56.3211 | 56.4908 | -66.8238 | -66.5963 | -4.1617 | -66.6537 | 56.2626 | 56.4267 | 56.3887 | -67.0378 | -0.21001 | 0.006435 | 0.017588 | -0.008621 | 0.20139 | -0.038732 | 0.13096 | -0.424 | -0.097219 | 0.017483 | -0.039916 | 0.38409 | 0.066805 | 0.028799 | 122.9801 | 122.9349 | 123.1046 | 63.0576 | -123.1836 | 122.8764 | 123.0404 | 123.0024 | 62.4521 | -123.3976
1412.2656 | 123.4177 | -66.5726 | 56.4056 | 0.04215 | -0.10675 | -0.013921 | 0.04355 | -0.02343 | 0.055941 | 0.042884 | -0.0068487 | 0.0011204 | 0.045017 | 0.10766 | 0.046504 | -66.5916 | -3.5607 | -66.6178 | 56.3663 | 56.3211 | 56.4862 | -66.8238 | -66.6054 | -4.1571 | -66.6583 | 56.2535 | 56.4221 | 56.3887 | -67.0332 | -0.25121 | -0.039342 | -0.019033 | -0.045242 | 0.20596 | -0.084509 | 0.080609 | -0.46062 | -0.15215 | -0.032874 | -0.085694 | 0.37493 | 0.01645 | -0.016978 | 122.9389 | 122.8937 | 123.0588 | 63.0118 | -123.2294 | 122.8261 | 122.9947 | 122.9612 | 62.4155 | -123.4388
1413.2656 | 123.2574 | -66.6 | 56.3461 | 0.057412 | -0.10675 | -0.013921 | 0.046755 | -0.02343 | 0.053805 | 0.073406 | -0.010054 | 0.0021894 | 0.046085 | 0.10873 | 0.048641 | -66.5916 | -3.5516 | -66.6178 | 56.3571 | 56.3211 | 56.4862 | -66.8284 | -66.6054 | -4.1571 | -66.6537 | 56.2626 | 56.4267 | 56.3841 | -67.0332 | -0.22832 | 0.011012 | 0.008433 | -0.017776 | 0.21054 | -0.024999 | 0.14012 | -0.43316 | -0.083486 | -0.005408 | -0.053649 | 0.37951 | 0.080538 | 0.037953 | 122.9572 | 122.9212 | 123.0863 | 63.0484 | -123.1745 | 122.8627 | 123.0267 | 122.9841 | 62.4429 | -123.3793
1414.2656 | 123.1522 | -66.6412 | 56.3828 | 0.04215 | -0.10782 | -0.016058 | 0.044618 | -0.02343 | 0.053805 | 0.073406 | -0.010054 | 0.0032574 | 0.045017 | 0.10873 | 0.046504 | -66.5916 | -3.5424 | -66.6178 | 56.3617 | 56.3257 | 56.4954 | -66.8238 | -66.6009 | -4.148 | -66.6628 | 56.2535 | 56.4267 | 56.3887 | -67.0378 | -0.18254 | -0.021031 | 0.049631 | 0.023422 | 0.20596 | -0.057041 | 0.11266 | -0.39654 | -0.12926 | 0.040369 | -0.021608 | 0.37493 | 0.043917 | 0.005911 | 123.003 | 122.9669 | 123.1366 | 63.0988 | -123.2065 | 122.8947 | 123.0679 | 123.0299 | 62.4933 | -123.4205
1415.2656 | 123.1338 | -66.6183 | 56.3599 | 0.011626 | -0.10782 | -0.014989 | 0.044618 | -0.022362 | 0.054873 | 0.058145 | -0.0089857 | 0.0032574 | 0.043949 | 0.10873 | 0.048641 | -66.5916 | -3.5516 | -66.6224 | 56.3617 | 56.3257 | 56.5 | -66.8192 | -66.5963 | -4.1525 | -66.6628 | 56.2672 | 56.4221 | 56.3932 | -67.0424 | -0.20085 | 0.001857 | 0.026743 | -0.004044 | 0.19681 | -0.034153 | 0.14012 | -0.42401 | -0.092641 | 0.02206 | -0.044496 | 0.37951 | 0.062227 | 0.033378 | 122.9801 | 122.9441 | 123.1183 | 63.0668 | -123.1791 | 122.8856 | 123.0404 | 123.0116 | 62.4658 | -123.4022
1416.2656 | 123.2162 | -66.6046 | 56.369 | 0.026888 | -0.10782 | -0.014989 | 0.04355 | -0.02343 | 0.053805 | 0.042884 | -0.010054 | 0.0021894 | 0.046085 | 0.10766 | 0.047572 | -66.5916 | -3.547 | -66.6224 | 56.3617 | 56.3257 | 56.4817 | -66.8284 | -66.61 | -4.148 | -66.6583 | 56.2626 | 56.4221 | 56.3841 | -67.0332 | -0.22374 | -0.007299 | 0.01301 | -0.017777 | 0.20597 | -0.043309 | 0.11265 | -0.42858 | -0.10637 | -0.005409 | -0.053651 | 0.37493 | 0.053071 | 0.015064 | 122.9663 | 122.9303 | 123.0863 | 63.0576 | -123.1974 | 122.8673 | 123.0267 | 122.9887 | 62.4567 | -123.4022
1417.2656 | 123.2849 | -66.5771 | 56.337 | 0.04215 | -0.10675 | -0.016058 | 0.04355 | -0.025567 | 0.053805 | 0.073406 | -0.010054 | 0.0021894 | 0.045017 | 0.10766 | 0.047572 | -66.5962 | -3.547 | -66.6178 | 56.3663 | 56.3211 | 56.4862 | -66.8238 | -66.6009 | -4.148 | -66.6674 | 56.2672 | 56.4221 | 56.3795 | -67.0424 | -0.24663 | 0.029323 | -0.019034 | -0.040665 | 0.20596 | -0.015844 | 0.14927 | -0.46521 | -0.069753 | -0.023718 | -0.090274 | 0.37493 | 0.085115 | 0.04253 | 122.9434 | 122.8983 | 123.0634 | 63.0301 | -123.1608 | 122.8444 | 122.9992 | 122.9567 | 62.4292 | -123.3793
1418.2656 | 123.23 | -66.6138 | 56.3461 | 0.057412 | -0.10782 | -0.013921 | 0.045687 | -0.02343 | 0.055941 | 0.042884 | -0.0089857 | 0.0021894 | 0.043949 | 0.10873 | 0.048641 | -66.5916 | -3.5379 | -66.6224 | 56.3617 | 56.3303 | 56.4862 | -66.8238 | -66.5963 | -4.148 | -66.672 | 56.2626 | 56.4221 | 56.3841 | -67.0378 | -0.21001 | 0.01559 | 0.022166 | -0.008621 | 0.20139 | -0.015841 | 0.14012 | -0.424 | -0.083486 | 0.017483 | -0.058231 | 0.36577 | 0.07596 | 0.037953 | 122.9755 | 122.9441 | 123.1 | 63.0759 | -123.1699 | 122.8764 | 123.0359 | 122.9979 | 62.4658 | -123.3839
1419.2656 | 123.1384 | -66.6 | 56.4239 | 0.04215 | -0.10675 | -0.014989 | 0.044618 | -0.024498 | 0.053805 | 0.073406 | -0.0089857 | 0.0021894 | 0.045017 | 0.10873 | 0.048641 | -66.5916 | -3.5379 | -66.6178 | 56.3571 | 56.3349 | 56.4954 | -66.8192 | -66.6054 | -4.1525 | -66.672 | 56.2626 | 56.4175 | 56.3887 | -67.0424 | -0.21916 | -0.066808 | 0.008433 | -0.017776 | 0.20139 | -0.089082 | 0.071456 | -0.44232 | -0.16131 | -0.005408 | -0.071964 | 0.37035 | -0.006439 | -0.035288 | 122.9572 | 122.9349 | 123.0954 | 63.0622 | -123.2431 | 122.8627 | 123.0175 | 122.9887 | 62.4475 | -123.4663
1420.2656 | 123.2208 | -66.6275 | 56.3461 | 0.04215 | -0.10782 | -0.013921 | 0.042482 | -0.02343 | 0.052737 | 0.058145 | -0.010054 | 0.0021894 | 0.045017 | 0.10873 | 0.046504 | -66.5962 | -3.5424 | -66.6178 | 56.3617 | 56.3303 | 56.4954 | -66.8238 | -66.6054 | -4.1525 | -66.6628 | 56.2672 | 56.4267 | 56.3841 | -67.0286 | -0.19627 | 0.01559 | 0.03132 | 0.009689 | 0.20596 | -0.015841 | 0.14928 | -0.40111 | -0.078908 | 0.022057 | -0.035341 | 0.36577 | 0.080538 | 0.037953 | 122.9892 | 122.9578 | 123.1229 | 63.0851 | -123.1699 | 122.8947 | 123.0542 | 123.0116 | 62.475 | -123.3747
1421.2656 | 123.2986 | -66.5863 | 56.3736 | 0.011626 | -0.10782 | -0.014989 | 0.046755 | -0.024498 | 0.054873 | 0.058145 | -0.010054 | 0.0021894 | 0.045017 | 0.10766 | 0.048641 | -66.5962 | -3.5287 | -66.627 | 56.3709 | 56.3303 | 56.4954 | -66.8284 | -66.6009 | -4.1525 | -66.6628 | 56.2535 | 56.4221 | 56.3932 | -67.0424 | -0.24205 | -0.002719 | -0.009878 | -0.040666 | 0.20139 | -0.043307 | 0.12181 | -0.45605 | -0.12011 | -0.014562 | -0.076539 | 0.37951 | 0.048494 | 0.019645 | 122.9572 | 122.9166 | 123.0817 | 63.0576 | -123.202 | 122.8398 | 123.0084 | 122.9795 | 62.4338 | -123.4159
1422.2656 | 123.2391 | -66.6412 | 56.337 | 0.04215 | -0.10675 | -0.014989 | 0.044618 | -0.024498 | 0.054873 | 0.058145 | -0.010054 | 0.0032574 | 0.045017 | 0.10873 | 0.048641 | -66.5962 | -3.5287 | -66.6178 | 56.3663 | 56.3394 | 56.4954 | -66.8284 | -66.5963 | -4.148 | -66.6674 | 56.2581 | 56.4221 | 56.3887 | -67.0332 | -0.18712 | 0.029323 | 0.045053 | 0.023422 | 0.21054 | 0.002472 | 0.15843 | -0.39196 | -0.07891 | 0.044948 | -0.026187 | 0.36577 | 0.085115 | 0.051687 | 123.0075 | 122.9807 | 123.1366 | 63.1125 | -123.1653 | 122.8993 | 123.0633 | 123.0299 | 62.4933 | -123.3702
1423.2656 | 123.2254 | -66.6046 | 56.3553 | 0.026888 | -0.10782 | -0.014989 | 0.045687 | -0.02343 | 0.053805 | 0.058145 | -0.0089857 | 0.0021894 | 0.045017 | 0.1098 | 0.048641 | -66.5916 | -3.5241 | -66.6224 | 56.3663 | 56.3257 | 56.5 | -66.8238 | -66.6054 | -4.1525 | -66.672 | 56.2672 | 56.4221 | 56.3932 | -67.0332 | -0.21916 | 0.011012 | 0.01301 | -0.017777 | 0.20139 | -0.029576 | 0.1447 | -0.42858 | -0.088064 | -0.000831 | -0.067387 | 0.36119 | 0.066804 | 0.037955 | 122.9709 | 122.9303 | 123.1046 | 63.0805 | -123.1791 | 122.8718 | 123.0267 | 122.9979 | 62.4521 | -123.3885
1424.2656 | 123.1522 | -66.6183 | 56.3919 | 0.057412 | -0.10675 | -0.014989 | 0.04355 | -0.022362 | 0.055941 | 0.073406 | -0.0079177 | 0.0021894 | 0.046085 | 0.10873 | 0.045436 | -66.5916 | -3.5241 | -66.6178 | 56.3617 | 56.3303 | 56.4908 | -66.8238 | -66.6054 | -4.1388 | -66.6537 | 56.2535 | 56.4221 | 56.3887 | -67.0378 | -0.20543 | -0.030187 | 0.026743 | 0.000534 | 0.20596 | -0.061618 | 0.09892 | -0.41943 | -0.13842 | 0.012902 | -0.035339 | 0.38409 | 0.030183 | -0.003245 | 122.9801 | 122.9486 | 123.1092 | 63.0942 | -123.2157 | 122.8718 | 123.0404 | 123.007 | 62.4796 | -123.4297
1425.2656 | 123.2025 | -66.6 | 56.337 | 0.04215 | -0.10889 | -0.014989 | 0.04355 | -0.024498 | 0.052737 | 0.027623 | -0.0079177 | 0.0021894 | 0.042881 | 0.10766 | 0.047572 | -66.6008 | -3.5241 | -66.6224 | 56.3663 | 56.3303 | 56.4908 | -66.8284 | -66.61 | -4.148 | -66.6674 | 56.2581 | 56.4175 | 56.3932 | -67.0332 | -0.22832 | 0.029323 | -0.000724 | -0.022354 | 0.20597 | -0.006686 | 0.15385 | -0.43316 | -0.07891 | -0.009986 | -0.067385 | 0.36577 | 0.080536 | 0.056266 | 122.9663 | 122.9303 | 123.0909 | 63.0759 | -123.1653 | 122.8581 | 123.0175 | 122.9933 | 62.4521 | -123.3702
1426.2656 | 123.2254 | -66.5955 | 56.3553 | 0.04215 | -0.10675 | -0.013921 | 0.042482 | -0.02343 | 0.053805 | 0.042884 | -0.0079177 | 0.0032574 | 0.043949 | 0.1098 | 0.048641 | -66.5916 | -3.515 | -66.6178 | 56.3663 | 56.3349 | 56.4954 | -66.8284 | -66.6009 | -4.148 | -66.6583 | 56.2535 | 56.4221 | 56.3841 | -67.0424 | -0.2329 | 0.011012 | 0.003855 | -0.022354 | 0.21054 | -0.020418 | 0.14012 | -0.44689 | -0.1018 | -0.005407 | -0.062806 | 0.38409 | 0.066804 | 0.028797 | 122.9618 | 122.9303 | 123.0909 | 63.0805 | -123.1836 | 122.8489 | 123.0175 | 122.9795 | 62.4475 | -123.3976
1427.2656 | 123.2895 | -66.5771 | 56.3461 | 0.04215 | -0.10675 | -0.014989 | 0.045687 | -0.024498 | 0.053805 | 0.042884 | -0.010054 | 0.0011204 | 0.045017 | 0.10873 | 0.047572 | -66.5916 | -3.515 | -66.6315 | 56.3709 | 56.3257 | 56.4954 | -66.8238 | -66.6009 | -4.148 | -66.6628 | 56.2535 | 56.4221 | 56.3932 | -67.0424 | -0.24663 | 0.024747 | -0.014456 | -0.0544 | 0.19223 | -0.02042 | 0.14928 | -0.46521 | -0.092643 | -0.023718 | -0.085695 | 0.37951 | 0.07596 | 0.047111 | 122.948 | 122.9029 | 123.0726 | 63.0622 | -123.1699 | 122.8306 | 122.9992 | 122.9704 | 62.4292 | -123.3885
1428.2656 | 123.2254 | -66.5955 | 56.3187 | 0.04215 | -0.10889 | -0.018194 | 0.04355 | -0.02343 | 0.055941 | 0.042884 | -0.0089857 | 5.2373e-05 | 0.043949 | 0.1098 | 0.046504 | -66.5962 | -3.515 | -66.6224 | 56.3663 | 56.3349 | 56.4908 | -66.8284 | -66.5963 | -4.1525 | -66.6537 | 56.2581 | 56.4312 | 56.3887 | -67.0424 | -0.2329 | 0.047633 | -0.000723 | -0.026932 | 0.20597 | 0.016203 | 0.17216 | -0.44689 | -0.0606 | -0.000828 | -0.058227 | 0.38867 | 0.11258 | 0.069997 | 122.9618 | 122.9303 | 123.0863 | 63.0805 | -123.147 | 122.8535 | 123.0267 | 122.9841 | 62.4429 | -123.361
1429.2656 | 123.175 | -66.6229 | 56.3782 | 0.026888 | -0.10568 | -0.016058 | 0.045687 | -0.02343 | 0.053805 | 0.058145 | -0.0089857 | 0.0021894 | 0.042881 | 0.1098 | 0.048641 | -66.5916 | -3.5104 | -66.627 | 56.3663 | 56.3349 | 56.4908 | -66.8238 | -66.5963 | -4.148 | -66.6674 | 56.2535 | 56.4175 | 56.3932 | -67.0378 | -0.20085 | -0.011876 | 0.031321 | -0.004045 | 0.19681 | -0.043306 | 0.11265 | -0.41485 | -0.12469 | 0.026638 | -0.044497 | 0.37035 | 0.039337 | 0.015067 | 122.9892 | 122.9578 | 123.1138 | 63.1125 | -123.202 | 122.8764 | 123.0404 | 123.0162 | 62.475 | -123.4159
1430.2656 | 123.2071 | -66.6138 | 56.3644 | 0.026888 | -0.10782 | -0.014989 | 0.044618 | -0.024498 | 0.054873 | 0.058145 | -0.0089857 | 0.0053944 | 0.045017 | 0.10873 | 0.048641 | -66.5916 | -3.5058 | -66.6178 | 56.3663 | 56.3303 | 56.4954 | -66.8238 | -66.6009 | -4.1525 | -66.6674 | 56.2672 | 56.4267 | 56.3887 | -67.0378 | -0.21001 | 0.001857 | 0.022166 | -0.004043 | 0.20596 | -0.034152 | 0.13097 | -0.424 | -0.097219 | 0.012904 | -0.053652 | 0.37035 | 0.062227 | 0.024221 | 122.9801 | 122.9441 | 123.1092 | 63.108 | -123.1882 | 122.881 | 123.0404 | 123.0024 | 62.4612 | -123.4022
1431.2656 | 123.3124 | -66.6 | 56.3644 | 0.04215 | -0.10889 | -0.016058 | 0.042482 | -0.024498 | 0.052737 | 0.073406 | -0.0079177 | 0.0021894 | 0.045017 | 0.11087 | 0.047572 | -66.6008 | -3.5058 | -66.6224 | 56.3663 | 56.3303 | 56.4954 | -66.8238 | -66.6054 | -4.1525 | -66.6583 | 56.2626 | 56.4175 | 56.3932 | -67.0332 | -0.22374 | 0.001857 | -0.000724 | -0.022354 | 0.20139 | -0.034152 | 0.13097 | -0.43316 | -0.1018 | -0.005408 | -0.058228 | 0.37493 | 0.05307 | 0.0288 | 122.9663 | 122.9303 | 123.0954 | 63.0942 | -123.1882 | 122.8627 | 123.0175 | 122.9933 | 62.4475 | -123.3976
1432.2656 | 123.2712 | -66.6092 | 56.3095 | 0.026888 | -0.10782 | -0.014989 | 0.045687 | -0.024498 | 0.053805 | 0.073406 | -0.0079177 | 0.0021894 | 0.042881 | 0.10766 | 0.047572 | -66.5916 | -3.4966 | -66.6224 | 56.3617 | 56.3257 | 56.4862 | -66.8192 | -66.6054 | -4.1434 | -66.6583 | 56.2626 | 56.4221 | 56.3887 | -67.0424 | -0.21001 | 0.052211 | 0.017588 | -0.013199 | 0.19681 | 0.016201 | 0.17674 | -0.43316 | -0.046865 | 0.003747 | -0.049073 | 0.38409 | 0.11258 | 0.079153 | 122.9709 | 122.9349 | 123.0954 | 63.1125 | -123.1287 | 122.8718 | 123.0313 | 122.9979 | 62.4658 | -123.3519
1433.2656 | 123.2574 | -66.5909 | 56.3416 | 0.04215 | -0.10782 | -0.013921 | 0.044618 | -0.024498 | 0.053805 | 0.073406 | -0.0089857 | 0.0021894 | 0.045017 | 0.1098 | 0.047572 | -66.5916 | -3.515 | -66.6315 | 56.3663 | 56.3257 | 56.4862 | -66.8238 | -66.6054 | -4.1434 | -66.6628 | 56.2535 | 56.4312 | 56.3887 | -67.0332 | -0.2329 | 0.024745 | -0.000723 | -0.040667 | 0.19223 | -0.015843 | 0.1447 | -0.44231 | -0.088066 | -0.014564 | -0.071962 | 0.37035 | 0.089694 | 0.047109 | 122.9572 | 122.9166 | 123.0771 | 63.0759 | -123.1653 | 122.8444 | 123.0221 | 122.9795 | 62.4475 | -123.3747
1434.2812 | 123.2025 | -66.6183 | 56.4148 | 0.04215 | -0.10889 | -0.013921 | 0.045687 | -0.025567 | 0.052737 | 0.042884 | -0.0079177 | 0.0032574 | 0.045017 | 0.10766 | 0.047572 | -66.6008 | -3.5058 | -66.6224 | 56.3709 | 56.3349 | 56.5 | -66.8284 | -66.6054 | -4.1388 | -66.6674 | 56.2581 | 56.4267 | 56.3887 | -67.0332 | -0.21001 | -0.043918 | 0.017586 | -0.004044 | 0.20597 | -0.079927 | 0.085189 | -0.41485 | -0.15673 | 0.012902 | -0.049075 | 0.36577 | 0.011873 | -0.026133 | 122.9892 | 122.9532 | 123.1183 | 63.1125 | -123.2432 | 122.8764 | 123.045 | 123.007 | 62.4796 | -123.448
1435.3281 | 123.2437 | -66.6138 | 56.3278 | 0.057412 | -0.10889 | -0.014989 | 0.04355 | -0.024498 | 0.052737 | 0.073406 | -0.0089857 | 0.0032574 | 0.042881 | 0.10873 | 0.047572 | -66.5962 | -3.4966 | -66.6224 | 56.3663 | 56.3257 | 56.4862 | -66.8284 | -66.6009 | -4.1388 | -66.6628 | 56.2718 | 56.4312 | 56.3932 | -67.0378 | -0.21459 | 0.038478 | 0.017588 | -0.008621 | 0.20597 | -0.00211 | 0.15843 | -0.424 | -0.056019 | 0.012904 | -0.049073 | 0.37493 | 0.10343 | 0.065421 | 122.9801 | 122.9395 | 123.1 | 63.1171 | -123.1562 | 122.8856 | 123.045 | 123.007 | 62.475 | -123.3656
1436.2656 | 123.2025 | -66.6138 | 56.337 | 0.057412 | -0.10782 | -0.014989 | 0.04355 | -0.025567 | 0.055941 | 0.058145 | -0.010054 | 0.0032574 | 0.043949 | 0.10873 | 0.047572 | -66.5962 | -3.4921 | -66.6224 | 56.3663 | 56.3349 | 56.5 | -66.8284 | -66.5963 | -4.1342 | -66.6674 | 56.2581 | 56.4267 | 56.3841 | -67.0286 | -0.21459 | 0.029323 | 0.017588 | -0.008621 | 0.20597 | -0.002107 | 0.16301 | -0.41485 | -0.07891 | 0.017483 | -0.053652 | 0.36119 | 0.089693 | 0.047108 | 122.9801 | 122.9486 | 123.1138 | 63.1217 | -123.1653 | 122.8718 | 123.0404 | 122.9979 | 62.4796 | -123.3656
1437.2656 | 123.4634 | -66.5771 | 56.3599 | 0.026888 | -0.10889 | -0.014989 | 0.042482 | -0.025567 | 0.055941 | 0.058145 | -0.0089857 | 0.0021894 | 0.043949 | 0.10873 | 0.047572 | -66.5916 | -3.4921 | -66.627 | 56.3617 | 56.3303 | 56.4908 | -66.8238 | -66.6009 | -4.1342 | -66.6628 | 56.2581 | 56.4312 | 56.3841 | -67.0378 | -0.24663 | 0.001857 | -0.014456 | -0.049822 | 0.19681 | -0.029574 | 0.13096 | -0.46063 | -0.1018 | -0.023718 | -0.085695 | 0.37493 | 0.071384 | 0.02422 | 122.9389 | 122.9074 | 123.068 | 63.0851 | -123.1836 | 122.8352 | 123.0084 | 122.9612 | 62.4429 | -123.3976
1438.2656 | 123.2391 | -66.6138 | 56.3095 | 0.026888 | -0.10675 | -0.016058 | 0.044618 | -0.02343 | 0.053805 | 0.042884 | -0.0089857 | 0.0021894 | 0.045017 | 0.11087 | 0.046504 | -66.5916 | -3.4921 | -66.627 | 56.3617 | 56.3303 | 56.4862 | -66.8238 | -66.6009 | -4.1388 | -66.6674 | 56.2672 | 56.4175 | 56.3887 | -67.0378 | -0.21001 | 0.052211 | 0.022166 | -0.0132 | 0.19681 | 0.02078 | 0.17674 | -0.424 | -0.042287 | 0.012904 | -0.053652 | 0.37035 | 0.108 | 0.079153 | 122.9755 | 122.9441 | 123.1 | 63.1217 | -123.1333 | 122.881 | 123.0313 | 123.0024 | 62.475 | -123.3473
1439.2656 | 123.1613 | -66.655 | 56.3965 | 0.057412 | -0.10996 | -0.016058 | 0.04355 | -0.02343 | 0.053805 | 0.058145 | -0.010054 | 0.0011204 | 0.043949 | 0.1098 | 0.048641 | -66.587 | -3.4829 | -66.6224 | 56.3617 | 56.3349 | 56.5 | -66.8284 | -66.5963 | -4.1388 | -66.6628 | 56.2489 | 56.4267 | 56.3887 | -67.0424 | -0.17339 | -0.034764 | 0.067942 | 0.032577 | 0.20597 | -0.061616 | 0.1035 | -0.38739 | -0.14758 | 0.058681 | -0.007875 | 0.37951 | 0.030184 | -0.007822 | 123.0167 | 122.9898 | 123.155 | 63.1721 | -123.2248 | 122.9039 | 123.0816 | 123.0436 | 62.5162 | -123.4388
1440.2656 | 123.2117 | -66.6412 | 56.3507 | 0.04215 | -0.10675 | -0.017126 | 0.044618 | -0.02343 | 0.052737 | 0.058145 | -0.0089857 | 0.0021894 | 0.045017 | 0.1098 | 0.047572 | -66.5962 | -3.4783 | -66.6178 | 56.3617 | 56.3349 | 56.5 | -66.8238 | -66.6054 | -4.1296 | -66.672 | 56.2581 | 56.4267 | 56.3749 | -67.0424 | -0.18254 | 0.011012 | 0.045053 | 0.023422 | 0.20596 | -0.01584 | 0.14928 | -0.40112 | -0.092643 | 0.03579 | -0.030766 | 0.37035 | 0.07596 | 0.024218 | 123.003 | 122.9761 | 123.1412 | 63.1629 | -123.1745 | 122.8993 | 123.0679 | 123.0162 | 62.5116 | -123.3931
1441.2656 | 123.23 | -66.6046 | 56.3553 | 0.026888 | -0.10889 | -0.016058 | 0.045687 | -0.024498 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.043949 | 0.1098 | 0.049709 | -66.5962 | -3.4783 | -66.6224 | 56.3663 | 56.3303 | 56.4954 | -66.8284 | -66.61 | -4.1342 | -66.6628 | 56.2581 | 56.4221 | 56.3932 | -67.0378 | -0.22374 | 0.011012 | 0.008432 | -0.017777 | 0.20597 | -0.024997 | 0.14012 | -0.43316 | -0.097221 | -0.005409 | -0.058229 | 0.37493 | 0.066804 | 0.037955 | 122.9709 | 122.9349 | 123.1 | 63.1263 | -123.1836 | 122.8627 | 123.0267 | 122.9979 | 62.4704 | -123.3931
1442.2656 | 123.0881 | -66.6183 | 56.3049 | 0.011626 | -0.10782 | -0.013921 | 0.042482 | -0.024498 | 0.055941 | 0.058145 | -0.0089857 | 0.0043254 | 0.046085 | 0.11194 | 0.048641 | -66.5962 | -3.4783 | -66.6178 | 56.3617 | 56.3303 | 56.4862 | -66.8238 | -66.6054 | -4.1434 | -66.6766 | 56.2626 | 56.4221 | 56.3841 | -67.0424 | -0.20543 | 0.056788 | 0.022165 | 0.000534 | 0.20596 | 0.025357 | 0.18132 | -0.42401 | -0.042288 | 0.012902 | -0.058232 | 0.36577 | 0.11716 | 0.079151 | 122.9801 | 122.9486 | 123.1046 | 63.14 | -123.1287 | 122.881 | 123.0404 | 123.0024 | 62.475 | -123.3473
1443.2656 | 123.2986 | -66.5863 | 56.3553 | 0.026888 | -0.10996 | -0.013921 | 0.045687 | -0.02343 | 0.055941 | 0.042884 | -0.0079177 | 0.0011204 | 0.046085 | 0.11087 | 0.047572 | -66.5962 | -3.4692 | -66.6224 | 56.3663 | 56.3257 | 56.4954 | -66.8192 | -66.6009 | -4.1296 | -66.672 | 56.2626 | 56.4221 | 56.3795 | -67.0378 | -0.23289 | 0.011012 | -0.009878 | -0.036087 | 0.19681 | -0.029576 | 0.14012 | -0.45147 | -0.092642 | -0.014562 | -0.085697 | 0.36577 | 0.066804 | 0.024219 | 122.9526 | 122.912 | 123.0817 | 63.1171 | -123.1745 | 122.8489 | 123.0084 | 122.9658 | 62.4567 | -123.3931
1444.2656 | 123.2803 | -66.5726 | 56.3507 | 0.04215 | -0.10996 | -0.016058 | 0.04355 | -0.02343 | 0.054873 | 0.042884 | -0.0079177 | 0.0043254 | 0.045017 | 0.11087 | 0.048641 | -66.587 | -3.4783 | -66.6178 | 56.3617 | 56.3303 | 56.4908 | -66.8238 | -66.6009 | -4.1342 | -66.6628 | 56.2581 | 56.4267 | 56.3841 | -67.0424 | -0.25121 | 0.011012 | -0.014455 | -0.045242 | 0.20596 | -0.020419 | 0.14012 | -0.46978 | -0.092643 | -0.028295 | -0.090272 | 0.37951 | 0.07596 | 0.033375 | 122.9343 | 122.9029 | 123.0634 | 63.0942 | -123.1745 | 122.8306 | 122.9992 | 122.9567 | 62.4384 | -123.3931
1445.2656 | 123.2483 | -66.6229 | 56.3324 | 0.026888 | -0.10996 | -0.014989 | 0.044618 | -0.024498 | 0.055941 | 0.058145 | -0.0068487 | 0.0032574 | 0.043949 | 0.11087 | 0.048641 | -66.5916 | -3.4738 | -66.6224 | 56.3617 | 56.3349 | 56.4908 | -66.8238 | -66.6054 | -4.1296 | -66.6628 | 56.2535 | 56.4129 | 56.3932 | -67.0378 | -0.20085 | 0.029323 | 0.031321 | 0.000534 | 0.20139 | 0.002471 | 0.15843 | -0.41485 | -0.07891 | 0.01748 | -0.039918 | 0.37493 | 0.080535 | 0.060844 | 122.9846 | 122.9578 | 123.1138 | 63.1492 | -123.1562 | 122.8764 | 123.0359 | 123.0162 | 62.4933 | -123.3702
1446.2656 | 123.2437 | -66.6367 | 56.3187 | 0.026888 | -0.10996 | -0.013921 | 0.044618 | -0.02343 | 0.054873 | 0.027623 | -0.0089857 | 0.0011204 | 0.043949 | 0.1098 | 0.047572 | -66.6053 | -3.4783 | -66.6224 | 56.3617 | 56.3303 | 56.4954 | -66.8192 | -66.61 | -4.1342 | -66.672 | 56.2626 | 56.4221 | 56.3887 | -67.0515 | -0.18254 | 0.043055 | 0.031319 | 0.014267 | 0.19681 | 0.011624 | 0.17674 | -0.41485 | -0.056021 | 0.026635 | -0.035343 | 0.37951 | 0.10342 | 0.069997 | 122.9984 | 122.9669 | 123.1321 | 63.1583 | -123.1379 | 122.8993 | 123.0587 | 123.0253 | 62.5024 | -123.3702
1447.2656 | 123.2483 | -66.6229 | 56.3507 | 0.057412 | -0.10889 | -0.013921 | 0.045687 | -0.024498 | 0.053805 | 0.058145 | -0.0079177 | 0.0021894 | 0.046085 | 0.11087 | 0.047572 | -66.5916 | -3.4738 | -66.6315 | 56.3617 | 56.3349 | 56.4862 | -66.8329 | -66.61 | -4.1296 | -66.6674 | 56.2581 | 56.4267 | 56.3887 | -67.0378 | -0.21001 | 0.011012 | 0.031321 | -0.008623 | 0.20139 | -0.01584 | 0.13554 | -0.41485 | -0.092643 | 0.012902 | -0.044497 | 0.37035 | 0.07596 | 0.037954 | 122.9846 | 122.9578 | 123.1092 | 63.1492 | -123.1836 | 122.881 | 123.0496 | 123.0116 | 62.4933 | -123.3885
1448.2656 | 123.2437 | -66.6458 | 56.3553 | 0.04215 | -0.10675 | -0.014989 | 0.04355 | -0.022362 | 0.052737 | 0.058145 | -0.0079177 | 0.0043254 | 0.043949 | 0.10873 | 0.047572 | -66.5962 | -3.4692 | -66.6224 | 56.3709 | 56.3303 | 56.4954 | -66.8375 | -66.6054 | -4.1296 | -66.6628 | 56.2626 | 56.4312 | 56.3887 | -67.0424 | -0.1917 | 0.015591 | 0.049631 | 0.023422 | 0.21512 | -0.024997 | 0.14012 | -0.39654 | -0.092642 | 0.040368 | -0.01703 | 0.37951 | 0.075961 | 0.033376 | 123.0167 | 122.9761 | 123.1412 | 63.1766 | -123.1928 | 122.9085 | 123.0771 | 123.0345 | 62.5162 | -123.3976
1449.2656 | 123.1384 | -66.6367 | 56.3965 | 0.072674 | -0.10889 | -0.014989 | 0.04355 | -0.025567 | 0.054873 | 0.058145 | -0.010054 | 0.0043254 | 0.042881 | 0.11087 | 0.048641 | -66.5916 | -3.4692 | -66.627 | 56.3709 | 56.344 | 56.4908 | -66.8284 | -66.5963 | -4.1251 | -66.6674 | 56.2581 | 56.4221 | 56.3932 | -67.0378 | -0.1917 | -0.025607 | 0.045054 | 0.009688 | 0.20139 | -0.052459 | 0.094343 | -0.40112 | -0.13842 | 0.040371 | -0.030764 | 0.37035 | 0.025606 | -0.003243 | 123.0075 | 122.9807 | 123.1275 | 63.1675 | -123.2248 | 122.8947 | 123.0587 | 123.0299 | 62.5116 | -123.4343
1450.2656 | 123.23 | -66.6092 | 56.3644 | 0.011626 | -0.10889 | -0.016058 | 0.04355 | -0.021293 | 0.054873 | 0.073406 | -0.0079177 | 0.0021894 | 0.045017 | 0.11087 | 0.049709 | -66.5962 | -3.46 | -66.6132 | 56.3663 | 56.3303 | 56.4862 | -66.8284 | -66.61 | -4.1296 | -66.6674 | 56.2626 | 56.4221 | 56.3887 | -67.0378 | -0.21916 | 0.001857 | 0.01301 | -0.004043 | 0.21512 | -0.034152 | 0.12181 | -0.42858 | -0.1018 | -0.000831 | -0.05823 | 0.37035 | 0.057649 | 0.024221 | 122.9755 | 122.9395 | 123.0954 | 63.1492 | -123.1928 | 122.8718 | 123.0313 | 122.9979 | 62.4796 | -123.4022
1451.2656 | 123.2025 | -66.6367 | 56.3324 | 0.04215 | -0.11103 | -0.014989 | 0.045687 | -0.02343 | 0.055941 | 0.058145 | -0.0089857 | 0.0021894 | 0.045017 | 0.11087 | 0.048641 | -66.6008 | -3.4554 | -66.6178 | 56.3663 | 56.3303 | 56.4954 | -66.8284 | -66.6054 | -4.1388 | -66.672 | 56.2626 | 56.4267 | 56.3887 | -67.0469 | -0.1917 | 0.033901 | 0.035897 | 0.018845 | 0.21054 | -0.002108 | 0.16301 | -0.41027 | -0.069753 | 0.031213 | -0.035343 | 0.37493 | 0.094271 | 0.056265 | 123.003 | 122.9669 | 123.1321 | 63.1812 | -123.1608 | 122.8993 | 123.0633 | 123.0253 | 62.4979 | -123.3793
1452.2656 | 123.2162 | -66.6229 | 56.337 | 0.011626 | -0.10889 | -0.014989 | 0.045687 | -0.022362 | 0.055941 | 0.073406 | -0.010054 | 0.0032574 | 0.045017 | 0.1098 | 0.046504 | -66.5916 | -3.46 | -66.6178 | 56.3617 | 56.3349 | 56.5046 | -66.8329 | -66.6054 | -4.1388 | -66.6766 | 56.2581 | 56.4221 | 56.3749 | -67.0424 | -0.21001 | 0.024745 | 0.031321 | 0.005112 | 0.21512 | -0.002107 | 0.16759 | -0.41943 | -0.07891 | 0.01748 | -0.053654 | 0.36577 | 0.085115 | 0.037951 | 122.9846 | 122.9578 | 123.1275 | 63.1629 | -123.1699 | 122.881 | 123.045 | 122.9979 | 62.4841 | -123.3793
1453.2656 | 123.262 | -66.6 | 56.3416 | 0.04215 | -0.10889 | -0.013921 | 0.04355 | -0.02343 | 0.055941 | 0.073406 | -0.0079177 | 0.0032574 | 0.042881 | 0.11194 | 0.047572 | -66.5916 | -3.4554 | -66.627 | 56.3617 | 56.3303 | 56.4954 | -66.8375 | -66.6009 | -4.1296 | -66.6628 | 56.2672 | 56.4221 | 56.3841 | -67.0469 | -0.23748 | 0.020167 | 0.008433 | -0.026933 | 0.21054 | -0.011264 | 0.15385 | -0.44689 | -0.074331 | -0.000829 | -0.062806 | 0.38409 | 0.080537 | 0.04253 | 122.9618 | 122.9303 | 123.0954 | 63.1446 | -123.1791 | 122.8673 | 123.0221 | 122.9841 | 62.4704 | -123.3885
1454.2656 | 123.2254 | -66.6458 | 56.3278 | 0.026888 | -0.10996 | -0.016058 | 0.045687 | -0.02343 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.043949 | 0.11087 | 0.048641 | -66.5962 | -3.46 | -66.6224 | 56.3617 | 56.3394 | 56.4908 | -66.8284 | -66.61 | -4.1342 | -66.6674 | 56.2535 | 56.4267 | 56.3795 | -67.0332 | -0.18254 | 0.0339 | 0.049631 | 0.023422 | 0.20597 | 0.011627 | 0.16301 | -0.38738 | -0.074333 | 0.03579 | -0.021609 | 0.36577 | 0.098848 | 0.051685 | 123.0075 | 122.9853 | 123.1366 | 63.1858 | -123.1562 | 122.8993 | 123.0725 | 123.0253 | 62.5116 | -123.361
1455.2656 | 123.2254 | -66.6183 | 56.3324 | 0.072674 | -0.10889 | -0.016058 | 0.044618 | -0.024498 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.045017 | 0.1098 | 0.048641 | -66.6008 | -3.4509 | -66.6224 | 56.3663 | 56.3303 | 56.4954 | -66.8284 | -66.6054 | -4.1342 | -66.6628 | 56.2535 | 56.4221 | 56.3932 | -67.0378 | -0.21001 | 0.033901 | 0.017586 | -0.004044 | 0.20597 | -0.002108 | 0.16301 | -0.41943 | -0.07891 | 0.012902 | -0.044496 | 0.37493 | 0.089693 | 0.060844 | 122.9846 | 122.9486 | 123.1138 | 63.1675 | -123.1608 | 122.8718 | 123.0404 | 123.0116 | 62.4841 | -123.3702
1456.2656 | 123.2391 | -66.6138 | 56.3553 | 0.026888 | -0.10782 | -0.014989 | 0.04355 | -0.024498 | 0.055941 | 0.058145 | -0.010054 | 0.0011204 | 0.043949 | 0.11194 | 0.048641 | -66.5962 | -3.4509 | -66.627 | 56.3617 | 56.3349 | 56.4954 | -66.8329 | -66.61 | -4.1296 | -66.6766 | 56.2626 | 56.4267 | 56.3887 | -67.0424 | -0.21917 | 0.006434 | 0.017588 | -0.0132 | 0.20597 | -0.020418 | 0.14012 | -0.42858 | -0.092642 | 0.003747 | -0.062809 | 0.36577 | 0.071382 | 0.033376 | 122.9755 | 122.9486 | 123.1092 | 63.1629 | -123.1882 | 122.8764 | 123.0404 | 123.0024 | 62.4841 | -123.3976
1457.2656 | 123.2254 | -66.6183 | 56.3599 | 0.04215 | -0.11103 | -0.016058 | 0.044618 | -0.025567 | 0.054873 | 0.058145 | -0.0089857 | 0.0032574 | 0.042881 | 0.10873 | 0.047572 | -66.6008 | -3.4554 | -66.627 | 56.3617 | 56.3349 | 56.5 | -66.8284 | -66.6054 | -4.1251 | -66.672 | 56.2535 | 56.4267 | 56.3841 | -67.0424 | -0.21001 | 0.001857 | 0.017586 | -0.008623 | 0.20139 | -0.024995 | 0.14012 | -0.42401 | -0.10638 | 0.012902 | -0.053654 | 0.37035 | 0.066805 | 0.02422 | 122.9801 | 122.9532 | 123.1183 | 63.1629 | -123.1882 | 122.8718 | 123.045 | 123.0024 | 62.4933 | -123.4022
1458.2656 | 123.2849 | -66.6138 | 56.3324 | 0.026888 | -0.10996 | -0.016058 | 0.044618 | -0.02343 | 0.054873 | 0.058145 | -0.011122 | 0.0021894 | 0.045017 | 0.11087 | 0.047572 | -66.5916 | -3.4509 | -66.627 | 56.3663 | 56.3349 | 56.5 | -66.8284 | -66.5963 | -4.1296 | -66.6674 | 56.2581 | 56.4267 | 56.3932 | -67.0332 | -0.21459 | 0.033901 | 0.022166 | -0.0132 | 0.20139 | 0.002471 | 0.16759 | -0.41943 | -0.074332 | 0.017483 | -0.053652 | 0.36577 | 0.094271 | 0.060844 | 122.9801 | 122.9486 | 123.1138 | 63.1629 | -123.1608 | 122.8718 | 123.0404 | 123.007 | 62.4841 | -123.3656
1459.2656 | 123.175 | -66.6504 | 56.3965 | 0.04215 | -0.11103 | -0.016058 | 0.044618 | -0.024498 | 0.052737 | 0.073406 | -0.0089857 | 0.0043254 | 0.042881 | 0.1098 | 0.047572 | -66.5962 | -3.4463 | -66.627 | 56.3663 | 56.3303 | 56.4862 | -66.8329 | -66.61 | -4.1342 | -66.6674 | 56.2581 | 56.4221 | 56.3841 | -67.0424 | -0.18254 | -0.030186 | 0.054209 | 0.023421 | 0.20597 | -0.066195 | 0.089765 | -0.39196 | -0.13842 | 0.040368 | -0.017031 | 0.37493 | 0.025606 | -0.012401 | 123.0167 | 122.9807 | 123.1366 | 63.2041 | -123.2294 | 122.9085 | 123.0725 | 123.0345 | 62.5162 | -123.4388
1460.2656 | 123.2162 | -66.6138 | 56.3232 | 0.04215 | -0.11103 | -0.014989 | 0.045687 | -0.024498 | 0.055941 | 0.058145 | -0.0079177 | 0.0032574 | 0.043949 | 0.11194 | 0.048641 | -66.5962 | -3.4371 | -66.6224 | 56.3709 | 56.3349 | 56.4954 | -66.8238 | -66.6009 | -4.1296 | -66.6674 | 56.2581 | 56.4221 | 56.3887 | -67.0378 | -0.21001 | 0.047635 | 0.017588 | -0.008621 | 0.20139 | 0.011626 | 0.17216 | -0.424 | -0.065177 | 0.012904 | -0.053652 | 0.37035 | 0.098848 | 0.06542 | 122.9846 | 122.9486 | 123.1092 | 63.1766 | -123.147 | 122.8718 | 123.0359 | 123.0024 | 62.4841 | -123.361
1461.2656 | 123.2208 | -66.6229 | 56.3278 | 0.026888 | -0.11103 | -0.016058 | 0.044618 | -0.025567 | 0.054873 | 0.058145 | -0.0079177 | 0.0021894 | 0.042881 | 0.11087 | 0.047572 | -66.5916 | -3.4417 | -66.627 | 56.3617 | 56.3211 | 56.4862 | -66.8284 | -66.6054 | -4.1296 | -66.6628 | 56.2626 | 56.4267 | 56.3887 | -67.0424 | -0.20543 | 0.0339 | 0.031321 | -0.004045 | 0.20139 | -0.006689 | 0.15843 | -0.41943 | -0.065176 | 0.01748 | -0.039918 | 0.37951 | 0.098848 | 0.060842 | 122.9846 | 122.9441 | 123.1092 | 63.1812 | -123.1562 | 122.8856 | 123.0496 | 123.0116 | 62.4933 | -123.3702
1462.2656 | 123.262 | -66.6229 | 56.3232 | 0.026888 | -0.10996 | -0.016058 | 0.045687 | -0.02343 | 0.054873 | 0.042884 | -0.010054 | 0.0011204 | 0.043949 | 0.11087 | 0.047572 | -66.5916 | -3.4509 | -66.6224 | 56.3526 | 56.3303 | 56.4954 | -66.8329 | -66.61 | -4.1251 | -66.6674 | 56.2581 | 56.4267 | 56.3841 | -67.0424 | -0.21001 | 0.029321 | 0.031321 | 0.000534 | 0.21054 | 0.007047 | 0.17216 | -0.41943 | -0.065177 | 0.012902 | -0.044497 | 0.37493 | 0.10343 | 0.060841 | 122.9755 | 122.9532 | 123.1183 | 63.1721 | -123.1562 | 122.881 | 123.0496 | 123.007 | 62.4979 | -123.3656
1463.2656 | 123.1476 | -66.6092 | 56.3141 | 0.057412 | -0.10889 | -0.013921 | 0.04355 | -0.024498 | 0.055941 | 0.042884 | -0.0089857 | 0.0032574 | 0.045017 | 0.11194 | 0.046504 | -66.5962 | -3.4463 | -66.6224 | 56.3617 | 56.3303 | 56.4954 | -66.8238 | -66.6009 | -4.1342 | -66.6674 | 56.2626 | 56.4267 | 56.3887 | -67.0469 | -0.21459 | 0.047633 | 0.01301 | -0.013199 | 0.20139 | 0.016202 | 0.18132 | -0.43774 | -0.051443 | 0.008326 | -0.05823 | 0.37951 | 0.11258 | 0.074575 | 122.9709 | 122.9395 | 123.1046 | 63.1629 | -123.1379 | 122.8718 | 123.0359 | 122.9979 | 62.475 | -123.361
1464.2656 | 123.2483 | -66.6229 | 56.3049 | 0.026888 | -0.10889 | -0.014989 | 0.044618 | -0.024498 | 0.054873 | 0.058145 | -0.011122 | 0.0032574 | 0.046085 | 0.11087 | 0.047572 | -66.5962 | -3.4509 | -66.6224 | 56.3617 | 56.3303 | 56.4954 | -66.8238 | -66.6009 | -4.1296 | -66.6674 | 56.2535 | 56.4312 | 56.3887 | -67.0424 | -0.20085 | 0.056788 | 0.026743 | 0.000534 | 0.20139 | 0.025357 | 0.19047 | -0.41943 | -0.051445 | 0.022059 | -0.044497 | 0.37493 | 0.12631 | 0.08373 | 122.9846 | 122.9532 | 123.1183 | 63.1721 | -123.1287 | 122.8764 | 123.0542 | 123.0116 | 62.4933 | -123.3473
1465.2656 | 123.23 | -66.6504 | 56.3324 | -0.0036356 | -0.10889 | -0.014989 | 0.04355 | -0.02343 | 0.054873 | 0.058145 | -0.010054 | 0.0032574 | 0.046085 | 0.11194 | 0.048641 | -66.5962 | -3.4371 | -66.6224 | 56.3663 | 56.3257 | 56.4908 | -66.8284 | -66.6054 | -4.1251 | -66.6583 | 56.2672 | 56.4312 | 56.3887 | -67.0424 | -0.17797 | 0.033901 | 0.054209 | 0.028 | 0.20597 | -0.006687 | 0.15843 | -0.39196 | -0.065175 | 0.044946 | -0.007874 | 0.38409 | 0.09885 | 0.056265 | 123.0167 | 122.9761 | 123.1412 | 63.2133 | -123.1608 | 122.9176 | 123.0816 | 123.0391 | 62.5253 | -123.3748
1466.2656 | 123.1522 | -66.655 | 56.3644 | 0.011626 | -0.11103 | -0.016058 | 0.044618 | -0.027703 | 0.05701 | 0.073406 | -0.0089857 | 0.0011204 | 0.042881 | 0.10873 | 0.048641 | -66.5962 | -3.4371 | -66.627 | 56.3663 | 56.3349 | 56.4908 | -66.8329 | -66.6009 | -4.1388 | -66.6628 | 56.2626 | 56.4267 | 56.3932 | -67.0424 | -0.17797 | 0.001857 | 0.058786 | 0.027998 | 0.20597 | -0.029573 | 0.12639 | -0.38739 | -0.1018 | 0.054102 | -0.007875 | 0.37951 | 0.062227 | 0.0288 | 123.0213 | 122.9898 | 123.1458 | 63.2178 | -123.1974 | 122.9176 | 123.0816 | 123.0482 | 62.5162 | -123.4068
1467.2656 | 123.2849 | -66.6367 | 56.3187 | 0.04215 | -0.11103 | -0.014989 | 0.044618 | -0.024498 | 0.05701 | 0.058145 | -0.010054 | 0.0021894 | 0.043949 | 0.11194 | 0.048641 | -66.6008 | -3.4325 | -66.627 | 56.3617 | 56.3303 | 56.5 | -66.8284 | -66.6054 | -4.1296 | -66.672 | 56.2672 | 56.4312 | 56.3932 | -67.0378 | -0.1917 | 0.043055 | 0.035897 | 0.009688 | 0.20139 | 0.011624 | 0.18132 | -0.40112 | -0.051443 | 0.031213 | -0.035343 | 0.36577 | 0.11258 | 0.074576 | 122.9984 | 122.9669 | 123.1366 | 63.2041 | -123.147 | 122.9039 | 123.0679 | 123.0299 | 62.507 | -123.3564
1468.2656 | 123.1888 | -66.6321 | 56.3187 | 0.04215 | -0.11209 | -0.016058 | 0.044618 | -0.025567 | 0.054873 | 0.058145 | -0.010054 | 0.0021894 | 0.045017 | 0.11087 | 0.046504 | -66.5962 | -3.4371 | -66.6224 | 56.3617 | 56.3349 | 56.5 | -66.8329 | -66.5963 | -4.1296 | -66.6628 | 56.2535 | 56.4267 | 56.3887 | -67.0469 | -0.20086 | 0.043055 | 0.035898 | 0.009689 | 0.21054 | 0.016203 | 0.18132 | -0.41485 | -0.065178 | 0.035793 | -0.030763 | 0.38409 | 0.108 | 0.069997 | 122.9938 | 122.9669 | 123.1321 | 63.195 | -123.1516 | 122.8856 | 123.0587 | 123.0207 | 62.5024 | -123.3656
1469.2656 | 123.2574 | -66.6321 | 56.2958 | 0.011626 | -0.11103 | -0.012852 | 0.04355 | -0.02343 | 0.053805 | 0.058145 | -0.0079177 | 0.0011204 | 0.045017 | 0.11087 | 0.047572 | -66.5962 | -3.4371 | -66.6224 | 56.3663 | 56.3349 | 56.4954 | -66.8284 | -66.6009 | -4.1296 | -66.6628 | 56.2535 | 56.4267 | 56.3795 | -67.0469 | -0.19628 | 0.070522 | 0.035898 | 0.009689 | 0.20597 | 0.039092 | 0.19963 | -0.41485 | -0.042289 | 0.031214 | -0.030763 | 0.38409 | 0.13089 | 0.083729 | 122.9984 | 122.9669 | 123.1275 | 63.195 | -123.1241 | 122.8856 | 123.0587 | 123.0116 | 62.5024 | -123.3427
1470.2656 | 123.349 | -66.5955 | 56.3049 | 0.026888 | -0.10996 | -0.013921 | 0.044618 | -0.025567 | 0.055941 | 0.027623 | -0.0079177 | 0.0021894 | 0.045017 | 0.11194 | 0.046504 | -66.6008 | -3.4371 | -66.6224 | 56.3617 | 56.3349 | 56.4862 | -66.8284 | -66.61 | -4.1296 | -66.6674 | 56.2581 | 56.4312 | 56.3932 | -67.0286 | -0.2329 | 0.056788 | -0.005302 | -0.026932 | 0.20597 | 0.029936 | 0.18132 | -0.43316 | -0.046867 | -0.014564 | -0.071963 | 0.36119 | 0.12631 | 0.088309 | 122.9572 | 122.9303 | 123.0817 | 63.1583 | -123.1333 | 122.8535 | 123.0267 | 122.9887 | 62.4658 | -123.3335
1471.2656 | 123.1567 | -66.655 | 56.3461 | 0.04215 | -0.10996 | -0.013921 | 0.044618 | -0.02343 | 0.055941 | 0.012362 | -0.010054 | 0.0032574 | 0.043949 | 0.11194 | 0.048641 | -66.5962 | -3.4371 | -66.6315 | 56.3617 | 56.3349 | 56.4954 | -66.8238 | -66.5963 | -4.1296 | -66.6628 | 56.2626 | 56.4312 | 56.3887 | -67.0424 | -0.16881 | 0.01559 | 0.058786 | 0.02342 | 0.19223 | -0.011262 | 0.14928 | -0.38739 | -0.083486 | 0.058681 | -0.007875 | 0.37951 | 0.085117 | 0.042532 | 123.0167 | 122.9898 | 123.1504 | 63.2178 | -123.1699 | 122.9176 | 123.0862 | 123.0436 | 62.5253 | -123.3885
1472.2656 | 123.262 | -66.6138 | 56.3324 | 0.04215 | -0.11103 | -0.016058 | 0.044618 | -0.025567 | 0.05701 | 0.058145 | -0.0079177 | 0.0032574 | 0.043949 | 0.11194 | 0.045436 | -66.6053 | -3.4417 | -66.6224 | 56.3617 | 56.3303 | 56.4862 | -66.8192 | -66.61 | -4.1342 | -66.6674 | 56.2581 | 56.4312 | 56.3887 | -67.0378 | -0.20543 | 0.029323 | 0.008431 | -0.008621 | 0.19681 | -0.002108 | 0.15385 | -0.424 | -0.074332 | 0.003747 | -0.053652 | 0.37035 | 0.09885 | 0.056265 | 122.9755 | 122.9441 | 123.1 | 63.1721 | -123.1516 | 122.8718 | 123.045 | 123.0024 | 62.4796 | -123.3702
1473.2656 | 123.143 | -66.6504 | 56.3507 | 0.04215 | -0.10996 | -0.016058 | 0.045687 | -0.025567 | 0.055941 | 0.042884 | -0.0079177 | 0.0032574 | 0.045017 | 0.11301 | 0.047572 | -66.5962 | -3.4463 | -66.627 | 56.3709 | 56.3394 | 56.5 | -66.8329 | -66.61 | -4.1296 | -66.6583 | 56.2626 | 56.4312 | 56.3887 | -67.0378 | -0.18254 | 0.020169 | 0.054209 | 0.023421 | 0.20597 | -0.011261 | 0.14928 | -0.38738 | -0.088064 | 0.040368 | -0.007874 | 0.37951 | 0.080539 | 0.037954 | 123.0213 | 122.9898 | 123.1504 | 63.2041 | -123.1836 | 122.913 | 123.0816 | 123.0391 | 62.5208 | -123.3885
1474.2656 | 123.2071 | -66.6504 | 56.3004 | 0.04215 | -0.10996 | -0.016058 | 0.04355 | -0.02343 | 0.05701 | 0.073406 | -0.011122 | 0.0021894 | 0.043949 | 0.11301 | 0.048641 | -66.5962 | -3.4463 | -66.627 | 56.3571 | 56.3349 | 56.5 | -66.8238 | -66.5963 | -4.1296 | -66.672 | 56.2581 | 56.4312 | 56.3887 | -67.0469 | -0.17339 | 0.056788 | 0.054209 | 0.023421 | 0.19681 | 0.034514 | 0.19963 | -0.39654 | -0.042289 | 0.054104 | -0.02161 | 0.37493 | 0.13089 | 0.088308 | 123.0075 | 122.9853 | 123.1504 | 63.2041 | -123.1241 | 122.9085 | 123.0816 | 123.0391 | 62.5208 | -123.3473
1475.2656 | 123.1247 | -66.5955 | 56.3232 | 0.04215 | -0.10996 | -0.014989 | 0.045687 | -0.024498 | 0.055941 | 0.058145 | -0.010054 | 0.0032574 | 0.045017 | 0.11194 | 0.046504 | -66.5916 | -3.4371 | -66.627 | 56.3663 | 56.3303 | 56.4908 | -66.8284 | -66.6009 | -4.1296 | -66.672 | 56.2489 | 56.4267 | 56.3887 | -67.0378 | -0.2329 | 0.043056 | 0.003855 | -0.031511 | 0.20139 | 0.007047 | 0.16759 | -0.44231 | -0.074334 | -0.005407 | -0.076542 | 0.36577 | 0.10343 | 0.06542 | 122.9618 | 122.9257 | 123.0863 | 63.1583 | -123.1516 | 122.8444 | 123.0221 | 122.9841 | 62.4658 | -123.361
1476.2656 | 123.1247 | -66.6595 | 56.3599 | 0.026888 | -0.10996 | -0.016058 | 0.044618 | -0.025567 | 0.054873 | 0.058145 | -0.0079177 | 0.0021894 | 0.043949 | 0.11194 | 0.048641 | -66.5962 | -3.4325 | -66.627 | 56.3663 | 56.3303 | 56.5091 | -66.8238 | -66.6054 | -4.1251 | -66.6628 | 56.2626 | 56.4267 | 56.3795 | -67.0378 | -0.16423 | 0.006435 | 0.063364 | 0.032576 | 0.19681 | -0.029574 | 0.14928 | -0.37823 | -0.097219 | 0.054101 | -0.003297 | 0.37493 | 0.066805 | 0.019642 | 123.0258 | 122.9898 | 123.1687 | 63.227 | -123.1836 | 122.9222 | 123.0862 | 123.0391 | 62.5345 | -123.3976
1477.2656 | 123.0377 | -66.6779 | 56.2958 | 0.057412 | -0.11103 | -0.016058 | 0.045687 | -0.024498 | 0.055941 | 0.058145 | -0.0079177 | 0.0021894 | 0.043949 | 0.11301 | 0.048641 | -66.6008 | -3.4325 | -66.6315 | 56.3709 | 56.3394 | 56.5 | -66.8375 | -66.61 | -4.1251 | -66.672 | 56.2626 | 56.4267 | 56.3887 | -67.0469 | -0.15966 | 0.075101 | 0.077095 | 0.046308 | 0.20597 | 0.043671 | 0.20421 | -0.36908 | -0.033132 | 0.067833 | 0.005855 | 0.37493 | 0.13089 | 0.092886 | 123.0487 | 123.0173 | 123.1778 | 63.2453 | -123.1333 | 122.9405 | 123.1045 | 123.0665 | 62.5528 | -123.3427
1478.2656 | 123.1934 | -66.6229 | 56.3416 | 0.026888 | -0.11103 | -0.016058 | 0.044618 | -0.026635 | 0.054873 | 0.042884 | -0.0089857 | 0.0032574 | 0.043949 | 0.11301 | 0.047572 | -66.5962 | -3.428 | -66.6315 | 56.3709 | 56.3349 | 56.5046 | -66.8375 | -66.6054 | -4.1251 | -66.6628 | 56.2535 | 56.4267 | 56.3887 | -67.0424 | -0.21459 | 0.029324 | 0.026743 | -0.008623 | 0.20597 | -0.006685 | 0.16301 | -0.41943 | -0.088066 | 0.01748 | -0.039918 | 0.37951 | 0.085115 | 0.047109 | 122.9938 | 122.9578 | 123.1275 | 63.195 | -123.1791 | 122.8764 | 123.0496 | 123.0116 | 62.4979 | -123.3839
1479.2656 | 123.2712 | -66.6183 | 56.2958 | 0.026888 | -0.10996 | -0.017126 | 0.044618 | -0.02343 | 0.055941 | 0.042884 | -0.010054 | 0.0021894 | 0.045017 | 0.11194 | 0.048641 | -66.6053 | -3.4188 | -66.6224 | 56.3709 | 56.3349 | 56.4908 | -66.8375 | -66.6054 | -4.1205 | -66.6674 | 56.2581 | 56.4267 | 56.3841 | -67.0424 | -0.21917 | 0.075101 | 0.013008 | -0.004044 | 0.21512 | 0.039092 | 0.19505 | -0.42401 | -0.037711 | 0.012902 | -0.049075 | 0.37493 | 0.13089 | 0.088307 | 122.9892 | 122.9532 | 123.1092 | 63.1995 | -123.1333 | 122.8764 | 123.045 | 123.0024 | 62.4979 | -123.3381
1480.2656 | 123.2529 | -66.6183 | 56.337 | 0.04215 | -0.11103 | -0.013921 | 0.044618 | -0.025567 | 0.053805 | 0.058145 | -0.010054 | 0.0021894 | 0.042881 | 0.1098 | 0.048641 | -66.5962 | -3.428 | -66.6224 | 56.3617 | 56.3349 | 56.5046 | -66.8284 | -66.6054 | -4.1205 | -66.672 | 56.2581 | 56.4267 | 56.3932 | -67.0469 | -0.21001 | 0.024745 | 0.022165 | -0.004044 | 0.20597 | -0.002107 | 0.16759 | -0.42858 | -0.07891 | 0.012902 | -0.053654 | 0.37493 | 0.089693 | 0.056266 | 122.9801 | 122.9532 | 123.1229 | 63.1904 | -123.1653 | 122.8764 | 123.045 | 123.0116 | 62.4979 | -123.3839
1481.2656 | 123.1384 | -66.6275 | 56.3416 | 0.011626 | -0.10996 | -0.017126 | 0.044618 | -0.025567 | 0.055941 | 0.058145 | -0.011122 | 0.0011204 | 0.045017 | 0.11194 | 0.045436 | -66.5962 | -3.4188 | -66.6315 | 56.3663 | 56.344 | 56.5046 | -66.8421 | -66.6054 | -4.1296 | -66.6628 | 56.2626 | 56.4221 | 56.3887 | -67.0515 | -0.21459 | 0.024745 | 0.03132 | -0.004046 | 0.21055 | 0.002472 | 0.16301 | -0.42401 | -0.078909 | 0.022057 | -0.035341 | 0.38867 | 0.080537 | 0.047109 | 122.9938 | 122.9715 | 123.1321 | 63.2087 | -123.1836 | 122.8901 | 123.0496 | 123.0162 | 62.4979 | -123.3931
1482.2656 | 123.1979 | -66.6183 | 56.369 | 0.04215 | -0.11103 | -0.016058 | 0.044618 | -0.024498 | 0.055941 | 0.027623 | -0.010054 | 0.0021894 | 0.043949 | 0.11301 | 0.047572 | -66.5962 | -3.4188 | -66.627 | 56.3663 | 56.3394 | 56.4954 | -66.8329 | -66.61 | -4.1342 | -66.6674 | 56.2626 | 56.4312 | 56.3978 | -67.0378 | -0.21459 | -0.002721 | 0.022165 | -0.008623 | 0.20597 | -0.029572 | 0.12639 | -0.41943 | -0.10637 | 0.008324 | -0.049075 | 0.37035 | 0.062228 | 0.0288 | 122.9846 | 122.9578 | 123.1138 | 63.1995 | -123.202 | 122.881 | 123.0496 | 123.0162 | 62.4841 | -123.4068
1483.2656 | 123.143 | -66.6641 | 56.3461 | 0.04215 | -0.11103 | -0.016058 | 0.044618 | -0.024498 | 0.055941 | 0.042884 | -0.010054 | 0.0032574 | 0.043949 | 0.11301 | 0.046504 | -66.5962 | -3.4188 | -66.627 | 56.3663 | 56.3349 | 56.5 | -66.8375 | -66.6054 | -4.1296 | -66.6674 | 56.2535 | 56.4221 | 56.3841 | -67.0332 | -0.17339 | 0.020168 | 0.067942 | 0.037154 | 0.21054 | -0.011262 | 0.15385 | -0.36907 | -0.092643 | 0.058679 | -0.003298 | 0.36577 | 0.07596 | 0.037953 | 123.0304 | 122.999 | 123.1641 | 63.2453 | -123.1836 | 122.9176 | 123.0862 | 123.0482 | 62.5345 | -123.3793
1484.2656 | 123.1155 | -66.655 | 56.3644 | 0.04215 | -0.11103 | -0.014989 | 0.046755 | -0.025567 | 0.054873 | 0.042884 | -0.010054 | 0.0021894 | 0.043949 | 0.11301 | 0.048641 | -66.6008 | -3.4142 | -66.6178 | 56.3663 | 56.3349 | 56.4954 | -66.8375 | -66.6009 | -4.1342 | -66.6674 | 56.2581 | 56.4221 | 56.3887 | -67.0424 | -0.18255 | 0.001857 | 0.054207 | 0.037155 | 0.2197 | -0.029573 | 0.13097 | -0.38739 | -0.10638 | 0.054102 | -0.012454 | 0.37493 | 0.057649 | 0.024221 | 123.0213 | 122.9898 | 123.1504 | 63.2407 | -123.202 | 122.913 | 123.0771 | 123.0436 | 62.5208 | -123.4068
1485.2656 | 123.2162 | -66.6458 | 56.3278 | 0.026888 | -0.11103 | -0.017126 | 0.045687 | -0.025567 | 0.054873 | 0.058145 | -0.010054 | 0.0032574 | 0.043949 | 0.11407 | 0.048641 | -66.6008 | -3.4142 | -66.6224 | 56.3663 | 56.3303 | 56.4862 | -66.8329 | -66.6054 | -4.1342 | -66.6674 | 56.2626 | 56.4221 | 56.3795 | -67.0378 | -0.18712 | 0.038478 | 0.045052 | 0.023422 | 0.21054 | 0.002469 | 0.15843 | -0.39196 | -0.065176 | 0.040368 | -0.021609 | 0.37035 | 0.09427 | 0.051685 | 123.0121 | 122.9761 | 123.1321 | 63.2316 | -123.1608 | 122.9085 | 123.0679 | 123.0253 | 62.5116 | -123.3656
1486.2656 | 123.1384 | -66.6458 | 56.3919 | 0.057412 | -0.11209 | -0.016058 | 0.044618 | -0.026635 | 0.054873 | 0.058145 | -0.0079177 | 0.0021894 | 0.043949 | 0.11194 | 0.047572 | -66.6053 | -3.4188 | -66.6315 | 56.3709 | 56.3349 | 56.4954 | -66.8329 | -66.6009 | -4.1342 | -66.672 | 56.2626 | 56.4267 | 56.3978 | -67.0424 | -0.18712 | -0.02103 | 0.040474 | 0.014265 | 0.20139 | -0.057039 | 0.1035 | -0.39654 | -0.12926 | 0.044947 | -0.026188 | 0.37035 | 0.034761 | 0.005912 | 123.0167 | 122.9807 | 123.1412 | 63.227 | -123.2248 | 122.9085 | 123.0725 | 123.0436 | 62.5116 | -123.4343
1487.2656 | 123.1659 | -66.6458 | 56.3553 | 0.04215 | -0.11103 | -0.014989 | 0.045687 | -0.025567 | 0.054873 | 0.058145 | -0.0089857 | 0.0032574 | 0.043949 | 0.11407 | 0.049709 | -66.5916 | -3.4234 | -66.6361 | 56.3617 | 56.3349 | 56.4954 | -66.8329 | -66.61 | -4.1342 | -66.6674 | 56.2672 | 56.4175 | 56.3932 | -67.0424 | -0.18712 | 0.006434 | 0.054209 | 0.009687 | 0.19681 | -0.020418 | 0.14012 | -0.39654 | -0.088064 | 0.03579 | -0.021609 | 0.37493 | 0.062225 | 0.037955 | 123.0075 | 122.9807 | 123.1412 | 63.2224 | -123.1882 | 122.913 | 123.0633 | 123.0391 | 62.5116 | -123.3976
1488.2656 | 123.1979 | -66.6367 | 56.3644 | 0.072674 | -0.10996 | -0.014989 | 0.04355 | -0.025567 | 0.055941 | 0.042884 | -0.0089857 | 0.0032574 | 0.042881 | 0.11194 | 0.047572 | -66.5916 | -3.4142 | -66.6315 | 56.3755 | 56.3349 | 56.5046 | -66.8329 | -66.61 | -4.1388 | -66.6674 | 56.2581 | 56.4175 | 56.3978 | -67.0424 | -0.19628 | 0.011014 | 0.045054 | 0.00511 | 0.20139 | -0.029573 | 0.14012 | -0.4057 | -0.10638 | 0.026635 | -0.030764 | 0.37493 | 0.05307 | 0.033378 | 123.0121 | 122.9715 | 123.1412 | 63.2224 | -123.1974 | 122.8947 | 123.0542 | 123.0345 | 62.4979 | -123.4068
1489.2656 | 123.2071 | -66.6321 | 56.3232 | 0.026888 | -0.11316 | -0.016058 | 0.044618 | -0.024498 | 0.054873 | 0.042884 | -0.0079177 | 0.0021894 | 0.043949 | 0.11194 | 0.047572 | -66.5962 | -3.4051 | -66.6315 | 56.3663 | 56.3394 | 56.4954 | -66.8329 | -66.6009 | -4.1342 | -66.6674 | 56.2672 | 56.4175 | 56.3978 | -67.0469 | -0.20086 | 0.043056 | 0.035898 | 0.000532 | 0.20139 | 0.016205 | 0.17216 | -0.41485 | -0.05602 | 0.031214 | -0.035342 | 0.37951 | 0.094269 | 0.074577 | 122.9984 | 122.9715 | 123.1275 | 63.227 | -123.1562 | 122.8993 | 123.0496 | 123.0299 | 62.4979 | -123.3702
1490.2656 | 123.2483 | -66.6183 | 56.3232 | 0.011626 | -0.11209 | -0.017126 | 0.04355 | -0.024498 | 0.054873 | 0.058145 | -0.0089857 | 0.0032574 | 0.043949 | 0.11194 | 0.046504 | -66.5962 | -3.4097 | -66.627 | 56.3617 | 56.3303 | 56.5091 | -66.8421 | -66.6009 | -4.1434 | -66.6628 | 56.2626 | 56.4312 | 56.3932 | -67.0424 | -0.22375 | 0.038478 | 0.022165 | -0.008623 | 0.21512 | 0.007047 | 0.1859 | -0.42401 | -0.060598 | 0.017481 | -0.044496 | 0.37951 | 0.108 | 0.069999 | 122.9801 | 122.9486 | 123.1275 | 63.2087 | -123.1653 | 122.881 | 123.0496 | 123.0116 | 62.475 | -123.3656
1491.2656 | 123.1567 | -66.6412 | 56.3736 | 0.026888 | -0.10996 | -0.017126 | 0.045687 | -0.025567 | 0.05701 | 0.058145 | -0.0089857 | 0.0043254 | 0.043949 | 0.11301 | 0.046504 | -66.5962 | -3.4005 | -66.6315 | 56.3617 | 56.3394 | 56.5046 | -66.8421 | -66.6054 | -4.1388 | -66.672 | 56.2626 | 56.4267 | 56.3932 | -67.0378 | -0.20086 | -0.011876 | 0.045053 | 0.009687 | 0.21055 | -0.034149 | 0.13097 | -0.39654 | -0.11095 | 0.03579 | -0.030766 | 0.36577 | 0.053072 | 0.019645 | 123.003 | 122.9807 | 123.1458 | 63.2407 | -123.2157 | 122.9039 | 123.0679 | 123.0345 | 62.5024 | -123.4114
1492.2656 | 123.1888 | -66.6046 | 56.369 | 0.057412 | -0.11209 | -0.016058 | 0.044618 | -0.025567 | 0.053805 | 0.042884 | -0.0079177 | 0.0011204 | 0.045017 | 0.11301 | 0.048641 | -66.5916 | -3.4005 | -66.627 | 56.3663 | 56.3394 | 56.5 | -66.8375 | -66.6009 | -4.1388 | -66.6674 | 56.2581 | 56.4312 | 56.3978 | -67.0424 | -0.2329 | -0.002721 | 0.01301 | -0.022356 | 0.21054 | -0.029572 | 0.13096 | -0.43774 | -0.11095 | 0.003748 | -0.062808 | 0.37493 | 0.062228 | 0.0288 | 122.9709 | 122.9441 | 123.1046 | 63.2041 | -123.2065 | 122.8627 | 123.0359 | 123.0024 | 62.4658 | -123.4114
1493.2656 | 123.1842 | -66.6367 | 56.369 | 0.057412 | -0.11103 | -0.018194 | 0.045687 | -0.024498 | 0.054873 | 0.058145 | -0.011122 | 0.0032574 | 0.041812 | 0.11407 | 0.047572 | -66.5962 | -3.4005 | -66.6315 | 56.3663 | 56.3394 | 56.5046 | -66.8421 | -66.6009 | -4.1388 | -66.6583 | 56.2535 | 56.4312 | 56.3887 | -67.0469 | -0.20544 | -0.002721 | 0.040476 | 0.00511 | 0.21055 | -0.029572 | 0.13554 | -0.41027 | -0.11553 | 0.035792 | -0.021607 | 0.38867 | 0.062228 | 0.019643 | 123.003 | 122.9761 | 123.1412 | 63.2362 | -123.2111 | 122.8901 | 123.0679 | 123.0253 | 62.4979 | -123.416
1494.2656 | 123.1522 | -66.6687 | 56.369 | 0.04215 | -0.11209 | -0.016058 | 0.04355 | -0.025567 | 0.055941 | 0.027623 | -0.011122 | 0.0032574 | 0.043949 | 0.11301 | 0.047572 | -66.6053 | -3.3913 | -66.6361 | 56.3663 | 56.3303 | 56.5046 | -66.8329 | -66.61 | -4.1342 | -66.6674 | 56.2535 | 56.4129 | 56.3978 | -67.0424 | -0.16423 | -0.002721 | 0.063362 | 0.032575 | 0.19681 | -0.03873 | 0.13554 | -0.37365 | -0.11553 | 0.058678 | 0.001279 | 0.37493 | 0.043913 | 0.0288 | 123.035 | 122.999 | 123.1733 | 63.2774 | -123.202 | 122.9222 | 123.0816 | 123.0665 | 62.5345 | -123.4114
1495.2656 | 123.2437 | -66.6412 | 56.3095 | 0.011626 | -0.11103 | -0.016058 | 0.04355 | -0.025567 | 0.054873 | 0.042884 | -0.0089857 | 0.0021894 | 0.045017 | 0.11301 | 0.047572 | -66.5962 | -3.3913 | -66.6315 | 56.3617 | 56.3303 | 56.4954 | -66.8329 | -66.6054 | -4.1434 | -66.672 | 56.2581 | 56.4267 | 56.3841 | -67.0469 | -0.1917 | 0.052211 | 0.045053 | 0.009687 | 0.20139 | 0.02078 | 0.1859 | -0.4057 | -0.051444 | 0.03579 | -0.030766 | 0.37493 | 0.11716 | 0.074574 | 123.003 | 122.9715 | 123.1366 | 63.2499 | -123.1424 | 122.8993 | 123.0679 | 123.0253 | 62.4979 | -123.3564
1496.2656 | 123.1613 | -66.655 | 56.3919 | 0.04215 | -0.11103 | -0.014989 | 0.042482 | -0.025567 | 0.055941 | 0.042884 | -0.0089857 | 0.0032574 | 0.043949 | 0.11301 | 0.046504 | -66.6008 | -3.4005 | -66.627 | 56.3709 | 56.3303 | 56.4954 | -66.8329 | -66.61 | -4.1434 | -66.672 | 56.2581 | 56.4175 | 56.3932 | -67.0378 | -0.17797 | -0.02103 | 0.054207 | 0.027998 | 0.20597 | -0.061618 | 0.1035 | -0.38281 | -0.13384 | 0.044945 | -0.017033 | 0.36577 | 0.025604 | 0.001334 | 123.0258 | 122.9853 | 123.1504 | 63.2545 | -123.2248 | 122.913 | 123.0725 | 123.0482 | 62.5116 | -123.4297
1497.2656 | 123.175 | -66.6367 | 56.3461 | 0.026888 | -0.11316 | -0.016058 | 0.044618 | -0.026635 | 0.055941 | 0.027623 | -0.0089857 | 0.0053944 | 0.045017 | 0.11407 | 0.046504 | -66.5962 | -3.3868 | -66.627 | 56.3663 | 56.3303 | 56.5 | -66.8375 | -66.61 | -4.1434 | -66.672 | 56.2581 | 56.4175 | 56.3841 | -67.0515 | -0.20086 | 0.020168 | 0.040476 | 0.009688 | 0.21054 | -0.015841 | 0.15385 | -0.41485 | -0.088065 | 0.026635 | -0.035343 | 0.37951 | 0.071381 | 0.037953 | 123.003 | 122.9669 | 123.1366 | 63.2499 | -123.1836 | 122.8947 | 123.0542 | 123.0207 | 62.4933 | -123.3976
1498.2656 | 123.1613 | -66.6229 | 56.3644 | 0.026888 | -0.11316 | -0.017126 | 0.04355 | -0.024498 | 0.055941 | 0.058145 | -0.011122 | 0.0032574 | 0.043949 | 0.11407 | 0.047572 | -66.6008 | -3.3776 | -66.627 | 56.3617 | 56.312 | 56.4862 | -66.8284 | -66.5963 | -4.1525 | -66.6628 | 56.2626 | 56.4267 | 56.3841 | -67.0424 | -0.20543 | -0.002721 | 0.022164 | -0.004045 | 0.20139 | -0.052468 | 0.12181 | -0.41943 | -0.1018 | 0.026638 | -0.039918 | 0.37951 | 0.062227 | 0.019642 | 122.9846 | 122.9349 | 123.1092 | 63.2453 | -123.1928 | 122.8856 | 123.0496 | 123.007 | 62.4704 | -123.4068
1499.2656 | 123.1888 | -66.6458 | 56.3507 | 0.011626 | -0.11103 | -0.014989 | 0.044618 | -0.025567 | 0.055941 | 0.058145 | -0.010054 | 0.0043254 | 0.043949 | 0.11407 | 0.047572 | -66.6053 | -3.3822 | -66.6315 | 56.3617 | 56.2937 | 56.4954 | -66.8329 | -66.6054 | -4.1434 | -66.6674 | 56.2626 | 56.4221 | 56.3841 | -67.0515 | -0.18712 | 0.011012 | 0.040474 | 0.014265 | 0.20139 | -0.057051 | 0.1447 | -0.4057 | -0.088064 | 0.040368 | -0.021609 | 0.38409 | 0.071382 | 0.033375 | 123.0075 | 122.9395 | 123.1412 | 63.2636 | -123.1836 | 122.9085 | 123.0679 | 123.0299 | 62.5024 | -123.4022
1500.2656 | 123.2391 | -66.5955 | 56.3507 | 0.04215 | -0.11423 | -0.016058 | 0.045687 | -0.026635 | 0.054873 | 0.058145 | -0.010054 | 0.0011204 | 0.043949 | 0.11301 | 0.048641 | -66.5962 | -3.3868 | -66.6315 | 56.3663 | 56.3211 | 56.4954 | -66.8238 | -66.6146 | -4.1434 | -66.6674 | 56.2581 | 56.4267 | 56.3841 | -67.0469 | -0.22832 | 0.01559 | -0.000723 | -0.036089 | 0.19223 | -0.029577 | 0.1447 | -0.45147 | -0.092643 | -0.019143 | -0.071963 | 0.37951 | 0.07596 | 0.033375 | 122.9618 | 122.9166 | 123.0909 | 63.2087 | -123.1745 | 122.8535 | 123.0221 | 122.9795 | 62.4521 | -123.3976
1501.2656 | 123.1842 | -66.6229 | 56.3736 | 0.057412 | -0.11316 | -0.016058 | 0.04355 | -0.025567 | 0.054873 | 0.042884 | -0.0089857 | 0.0011204 | 0.043949 | 0.11407 | 0.048641 | -66.6008 | -3.3822 | -66.6315 | 56.3571 | 56.3257 | 56.4954 | -66.8192 | -66.6009 | -4.148 | -66.6674 | 56.2626 | 56.4267 | 56.3795 | -67.0469 | -0.19627 | -0.016454 | 0.022164 | -0.008623 | 0.18765 | -0.047886 | 0.12181 | -0.42401 | -0.11095 | 0.022059 | -0.044497 | 0.37951 | 0.053072 | 0.005909 | 122.9801 | 122.9486 | 123.1183 | 63.2407 | -123.1928 | 122.8856 | 123.0496 | 123.0024 | 62.475 | -123.4205
1502.2656 | 123.2437 | -66.5817 | 56.337 | 0.04215 | -0.11209 | -0.014989 | 0.044618 | -0.02343 | 0.054873 | 0.073406 | -0.010054 | 0.0032574 | 0.042881 | 0.11301 | 0.047572 | -66.6008 | -3.3776 | -66.627 | 56.3571 | 56.3303 | 56.5046 | -66.8329 | -66.6054 | -4.1434 | -66.6674 | 56.2535 | 56.4221 | 56.3841 | -67.0469 | -0.25121 | 0.020167 | -0.019035 | -0.045244 | 0.20597 | -0.006686 | 0.16759 | -0.46521 | -0.083488 | -0.023719 | -0.085696 | 0.37951 | 0.085115 | 0.047108 | 122.9389 | 122.912 | 123.0863 | 63.2041 | -123.1699 | 122.8352 | 123.0038 | 122.9658 | 62.4384 | -123.3839
1503.2656 | 123.1659 | -66.6275 | 56.3965 | 0.04215 | -0.11103 | -0.014989 | 0.042482 | -0.025567 | 0.055941 | 0.073406 | -0.0089857 | 0.0021894 | 0.045017 | 0.11301 | 0.047572 | -66.6053 | -3.373 | -66.6315 | 56.3571 | 56.3211 | 56.5046 | -66.8284 | -66.6054 | -4.1434 | -66.6674 | 56.2626 | 56.4312 | 56.3795 | -67.0424 | -0.20085 | -0.039342 | 0.022163 | -0.004046 | 0.19681 | -0.075353 | 0.10808 | -0.41485 | -0.13384 | 0.022057 | -0.03992 | 0.37493 | 0.034763 | -0.016979 | 122.9846 | 122.9486 | 123.1321 | 63.2545 | -123.2248 | 122.8901 | 123.0587 | 123.007 | 62.4841 | -123.4388
1504.2656 | 123.1613 | -66.6321 | 56.3782 | 0.04215 | -0.11103 | -0.016058 | 0.04355 | -0.026635 | 0.055941 | 0.058145 | -0.0089857 | 0.0032574 | 0.043949 | 0.11514 | 0.048641 | -66.5962 | -3.3822 | -66.6224 | 56.3617 | 56.3394 | 56.4954 | -66.8284 | -66.61 | -4.1434 | -66.6674 | 56.2626 | 56.4267 | 56.3795 | -67.0469 | -0.19628 | -0.016454 | 0.035898 | 0.009689 | 0.20597 | -0.038727 | 0.11723 | -0.41485 | -0.11553 | 0.022057 | -0.035342 | 0.37951 | 0.048494 | 0.001331 | 122.9938 | 122.9715 | 123.1275 | 63.2499 | -123.2065 | 122.8947 | 123.0587 | 123.0116 | 62.4887 | -123.4251
1505.2656 | 123.1888 | -66.6138 | 56.3736 | 0.057412 | -0.11316 | -0.014989 | 0.04355 | -0.026635 | 0.054873 | 0.058145 | -0.0079177 | 0.0011204 | 0.041812 | 0.11407 | 0.046504 | -66.5962 | -3.3822 | -66.627 | 56.3571 | 56.3303 | 56.4954 | -66.8238 | -66.6009 | -4.148 | -66.672 | 56.2581 | 56.4312 | 56.3841 | -67.0515 | -0.21001 | -0.016454 | 0.017588 | -0.0132 | 0.19681 | -0.043307 | 0.12181 | -0.43774 | -0.11553 | 0.012904 | -0.058231 | 0.37951 | 0.057651 | 0.010487 | 122.9709 | 122.9441 | 123.1092 | 63.2316 | -123.1974 | 122.8718 | 123.045 | 122.9979 | 62.4658 | -123.4251
1506.2656 | 123.2986 | -66.6092 | 56.337 | 0.04215 | -0.11209 | -0.014989 | 0.044618 | -0.024498 | 0.054873 | 0.042884 | -0.0089857 | 0.0032574 | 0.045017 | 0.11407 | 0.046504 | -66.6053 | -3.3822 | -66.627 | 56.3571 | 56.3211 | 56.4954 | -66.8284 | -66.61 | -4.1388 | -66.672 | 56.2581 | 56.4267 | 56.3887 | -67.0424 | -0.21916 | 0.020167 | 0.003853 | -0.017778 | 0.20139 | -0.015844 | 0.15843 | -0.43316 | -0.07891 | -0.000831 | -0.062809 | 0.37035 | 0.089693 | 0.051687 | 122.9663 | 122.9303 | 123.1046 | 63.227 | -123.1653 | 122.8673 | 123.0359 | 122.9979 | 62.4704 | -123.3793
1507.2656 | 123.1384 | -66.6092 | 56.3873 | 0.04215 | -0.11209 | -0.013921 | 0.04355 | -0.027703 | 0.054873 | 0.058145 | -0.0089857 | 0.0043254 | 0.043949 | 0.11514 | 0.047572 | -66.5962 | -3.3776 | -66.6178 | 56.3617 | 56.3303 | 56.5046 | -66.8375 | -66.6009 | -4.148 | -66.672 | 56.2581 | 56.4267 | 56.3795 | -67.0469 | -0.22832 | -0.025609 | 0.01301 | -0.008621 | 0.2197 | -0.05704 | 0.11723 | -0.43774 | -0.12926 | 0.008326 | -0.062809 | 0.37493 | 0.039339 | -0.007824 | 122.9709 | 122.9395 | 123.1138 | 63.2316 | -123.2248 | 122.8673 | 123.0359 | 122.9887 | 62.4612 | -123.4343
1508.2656 | 123.2346 | -66.6092 | 56.3187 | 0.026888 | -0.11103 | -0.014989 | 0.042482 | -0.025567 | 0.054873 | 0.058145 | -0.0089857 | 0.0032574 | 0.042881 | 0.11514 | 0.047572 | -66.6053 | -3.3684 | -66.627 | 56.3663 | 56.3303 | 56.5091 | -66.8284 | -66.6054 | -4.1434 | -66.672 | 56.2626 | 56.4221 | 56.3887 | -67.0424 | -0.21916 | 0.047633 | 0.003853 | -0.017778 | 0.20139 | 0.011624 | 0.19048 | -0.43316 | -0.056021 | 0.003747 | -0.062809 | 0.37035 | 0.10342 | 0.069997 | 122.9755 | 122.9395 | 123.1183 | 63.2407 | -123.147 | 122.8718 | 123.0313 | 122.9979 | 62.4658 | -123.361
1509.2656 | 123.1796 | -66.6046 | 56.3965 | 0.026888 | -0.11316 | -0.016058 | 0.04355 | -0.026635 | 0.055941 | 0.058145 | -0.0089857 | 0.0032574 | 0.042881 | 0.11407 | 0.048641 | -66.6008 | -3.3684 | -66.627 | 56.3709 | 56.344 | 56.5046 | -66.8375 | -66.6009 | -4.1388 | -66.672 | 56.2535 | 56.4267 | 56.3887 | -67.0424 | -0.2329 | -0.025607 | 0.003853 | -0.022356 | 0.21054 | -0.052459 | 0.10808 | -0.43774 | -0.143 | 0.003748 | -0.067387 | 0.37035 | 0.030184 | -0.007822 | 122.9755 | 122.9486 | 123.1092 | 63.2362 | -123.234 | 122.8581 | 123.0313 | 122.9933 | 62.4658 | -123.4388
1510.2656 | 123.4314 | -66.6 | 56.3461 | 0.04215 | -0.11316 | -0.014989 | 0.042482 | -0.026635 | 0.055941 | 0.058145 | -0.0089857 | 0.0021894 | 0.046085 | 0.11407 | 0.047572 | -66.5916 | -3.3684 | -66.6224 | 56.3663 | 56.3349 | 56.5 | -66.8375 | -66.6009 | -4.1434 | -66.672 | 56.2535 | 56.4267 | 56.3887 | -67.0469 | -0.23748 | 0.020168 | 0.008433 | -0.022354 | 0.21512 | -0.011262 | 0.15385 | -0.44689 | -0.092643 | -0.000829 | -0.071964 | 0.37493 | 0.080538 | 0.042532 | 122.9663 | 122.9349 | 123.1 | 63.2316 | -123.1836 | 122.8535 | 123.0267 | 122.9887 | 62.4567 | -123.3931
1511.2656 | 123.2986 | -66.6046 | 56.3416 | 0.026888 | -0.11209 | -0.014989 | 0.044618 | -0.024498 | 0.05701 | 0.058145 | -0.010054 | 0.0043254 | 0.042881 | 0.11301 | 0.048641 | -66.6053 | -3.3684 | -66.6178 | 56.3709 | 56.3349 | 56.5046 | -66.8375 | -66.6054 | -4.1434 | -66.6766 | 56.2535 | 56.4312 | 56.3978 | -67.0424 | -0.2329 | 0.029324 | -0.000725 | -0.013199 | 0.2197 | -0.006685 | 0.16301 | -0.43774 | -0.088066 | -0.000831 | -0.071965 | 0.36577 | 0.089694 | 0.056266 | 122.9755 | 122.9395 | 123.1092 | 63.2362 | -123.1791 | 122.8581 | 123.0359 | 123.0024 | 62.4612 | -123.3839
1512.2656 | 123.3398 | -66.5863 | 56.3095 | 0.057412 | -0.11423 | -0.013921 | 0.041413 | -0.025567 | 0.055941 | 0.10393 | -0.0089857 | 0.0021894 | 0.042881 | 0.11407 | 0.048641 | -66.5962 | -3.3639 | -66.6224 | 56.3617 | 56.3257 | 56.5046 | -66.8284 | -66.6054 | -4.1388 | -66.672 | 56.2626 | 56.4267 | 56.3932 | -67.0469 | -0.24205 | 0.052211 | -0.009878 | -0.036087 | 0.20597 | 0.016201 | 0.19505 | -0.46063 | -0.046865 | -0.019141 | -0.085697 | 0.37493 | 0.11716 | 0.083732 | 122.948 | 122.912 | 123.0909 | 63.2224 | -123.1379 | 122.8489 | 123.013 | 122.9795 | 62.4475 | -123.3564
1513.2656 | 123.2117 | -66.6275 | 56.3828 | 0.057412 | -0.11316 | -0.016058 | 0.04355 | -0.025567 | 0.055941 | 0.073406 | -0.0089857 | 0.0032574 | 0.045017 | 0.11407 | 0.048641 | -66.6008 | -3.373 | -66.627 | 56.3617 | 56.3303 | 56.5046 | -66.8238 | -66.6054 | -4.1342 | -66.6628 | 56.2626 | 56.4358 | 56.3841 | -67.0469 | -0.19627 | -0.021031 | 0.026741 | 0.000532 | 0.19681 | -0.052462 | 0.12181 | -0.41943 | -0.12011 | 0.022057 | -0.035341 | 0.38409 | 0.053074 | 0.001332 | 122.9892 | 122.9578 | 123.1321 | 63.2545 | -123.2065 | 122.8901 | 123.0633 | 123.0116 | 62.4933 | -123.4297
1514.2656 | 123.2529 | -66.5955 | 56.3507 | 0.04215 | -0.11103 | -0.014989 | 0.044618 | -0.026635 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.041812 | 0.11407 | 0.047572 | -66.6008 | -3.3684 | -66.6224 | 56.3663 | 56.3257 | 56.5 | -66.8284 | -66.61 | -4.148 | -66.672 | 56.2535 | 56.4267 | 56.3932 | -67.0469 | -0.2329 | 0.01559 | -0.005302 | -0.026932 | 0.20597 | -0.024998 | 0.14928 | -0.45147 | -0.097221 | -0.014564 | -0.076542 | 0.37493 | 0.07596 | 0.042533 | 122.9618 | 122.9212 | 123.0954 | 63.227 | -123.1791 | 122.8489 | 123.0221 | 122.9887 | 62.4475 | -123.3976
1515.2656 | 123.2529 | -66.5909 | 56.3553 | 0.04215 | -0.11423 | -0.013921 | 0.04355 | -0.025567 | 0.055941 | 0.042884 | -0.011122 | 0.0053944 | 0.043949 | 0.11621 | 0.048641 | -66.6053 | -3.3684 | -66.6224 | 56.3663 | 56.3257 | 56.5 | -66.8284 | -66.61 | -4.148 | -66.6674 | 56.2581 | 56.4221 | 56.3932 | -67.0469 | -0.23748 | 0.011012 | -0.014458 | -0.03151 | 0.20597 | -0.029576 | 0.1447 | -0.45605 | -0.097221 | -0.019142 | -0.076541 | 0.37951 | 0.066804 | 0.037955 | 122.9572 | 122.9166 | 123.0909 | 63.2224 | -123.1836 | 122.8489 | 123.013 | 122.9841 | 62.4429 | -123.4022
1516.2656 | 123.23 | -66.6092 | 56.3324 | 0.04215 | -0.11316 | -0.016058 | 0.04355 | -0.026635 | 0.058078 | 0.027623 | -0.0079177 | 0.0032574 | 0.042881 | 0.11621 | 0.047572 | -66.6008 | -3.3639 | -66.6361 | 56.3663 | 56.3303 | 56.5 | -66.8375 | -66.6146 | -4.1388 | -66.6674 | 56.2581 | 56.4267 | 56.3932 | -67.0469 | -0.22832 | 0.033901 | 0.008431 | -0.026934 | 0.20139 | -0.002108 | 0.16759 | -0.43774 | -0.074332 | -0.00541 | -0.05823 | 0.37951 | 0.094271 | 0.060844 | 122.9755 | 122.9395 | 123.1092 | 63.2453 | -123.1699 | 122.8673 | 123.0359 | 123.0024 | 62.4704 | -123.3793
1517.2656 | 123.2208 | -66.6046 | 56.3553 | 0.04215 | -0.11316 | -0.014989 | 0.04355 | -0.025567 | 0.055941 | 0.058145 | -0.011122 | 0.0043254 | 0.043949 | 0.11407 | 0.047572 | -66.5916 | -3.3684 | -66.6315 | 56.3617 | 56.3394 | 56.4954 | -66.8329 | -66.6054 | -4.1342 | -66.672 | 56.2626 | 56.4267 | 56.3932 | -67.0424 | -0.22832 | 0.006434 | 0.01301 | -0.026934 | 0.20139 | -0.015839 | 0.14012 | -0.43774 | -0.092642 | -0.000831 | -0.067387 | 0.37035 | 0.071382 | 0.037955 | 122.9663 | 122.9441 | 123.1 | 63.2362 | -123.1882 | 122.8673 | 123.0313 | 122.9979 | 62.4704 | -123.3976
1518.2656 | 123.2986 | -66.6046 | 56.3278 | 0.057412 | -0.11316 | -0.014989 | 0.042482 | -0.024498 | 0.055941 | 0.058145 | -0.010054 | 0.0032574 | 0.042881 | 0.11621 | 0.047572 | -66.6008 | -3.373 | -66.627 | 56.3617 | 56.3394 | 56.5 | -66.8329 | -66.61 | -4.1434 | -66.6674 | 56.2672 | 56.4312 | 56.3932 | -67.0424 | -0.22832 | 0.0339 | 0.003853 | -0.022356 | 0.20597 | 0.011627 | 0.17216 | -0.43774 | -0.060598 | -0.005409 | -0.062808 | 0.37493 | 0.10343 | 0.065421 | 122.9663 | 122.9441 | 123.1046 | 63.2316 | -123.1608 | 122.8718 | 123.0359 | 122.9979 | 62.4612 | -123.3702
1519.2656 | 123.2941 | -66.5817 | 56.3644 | 0.057412 | -0.11209 | -0.016058 | 0.04355 | -0.026635 | 0.053805 | 0.058145 | -0.0089857 | 0.0032574 | 0.042881 | 0.11407 | 0.046504 | -66.5962 | -3.373 | -66.627 | 56.3663 | 56.3303 | 56.5 | -66.8329 | -66.61 | -4.1525 | -66.672 | 56.2672 | 56.4267 | 56.3932 | -67.0469 | -0.25121 | 0.001857 | -0.014456 | -0.045244 | 0.20597 | -0.034152 | 0.13554 | -0.46521 | -0.097219 | -0.028297 | -0.090275 | 0.37493 | 0.062227 | 0.0288 | 122.948 | 122.912 | 123.0817 | 63.2087 | -123.1974 | 122.8489 | 123.0084 | 122.975 | 62.4292 | -123.4114
1520.2656 | 123.1842 | -66.6183 | 56.3324 | 0.057412 | -0.1153 | -0.017126 | 0.04355 | -0.026635 | 0.053805 | 0.042884 | -0.0089857 | 0.0021894 | 0.042881 | 0.11407 | 0.047572 | -66.6008 | -3.3684 | -66.6315 | 56.3617 | 56.3349 | 56.5 | -66.8284 | -66.61 | -4.148 | -66.672 | 56.2581 | 56.4221 | 56.3887 | -67.0378 | -0.21001 | 0.029323 | 0.017586 | -0.013201 | 0.19681 | 0.002471 | 0.16759 | -0.41943 | -0.074332 | 0.008324 | -0.053654 | 0.36577 | 0.089693 | 0.056265 | 122.9801 | 122.9532 | 123.1183 | 63.2499 | -123.1608 | 122.8764 | 123.0404 | 123.007 | 62.4704 | -123.3702
1521.2656 | 123.262 | -66.5863 | 56.3461 | 0.04215 | -0.11423 | -0.014989 | 0.044618 | -0.025567 | 0.054873 | 0.027623 | -0.010054 | 0.0021894 | 0.043949 | 0.11514 | 0.046504 | -66.6008 | -3.3593 | -66.6224 | 56.3617 | 56.3349 | 56.5 | -66.8375 | -66.6054 | -4.1434 | -66.6628 | 56.2581 | 56.4221 | 56.3932 | -67.0378 | -0.25121 | 0.01559 | -0.014457 | -0.036087 | 0.21512 | -0.011262 | 0.15385 | -0.45147 | -0.088065 | -0.019141 | -0.076539 | 0.37493 | 0.07596 | 0.047111 | 122.948 | 122.9212 | 123.0863 | 63.227 | -123.1836 | 122.8444 | 123.0084 | 122.9795 | 62.4429 | -123.3839
1522.2656 | 123.2208 | -66.6504 | 56.3324 | 0.04215 | -0.11423 | -0.016058 | 0.04355 | -0.025567 | 0.054873 | 0.058145 | -0.010054 | 0.0032574 | 0.043949 | 0.11407 | 0.046504 | -66.5962 | -3.3547 | -66.627 | 56.3663 | 56.3394 | 56.5 | -66.8284 | -66.6054 | -4.1434 | -66.6628 | 56.2581 | 56.4175 | 56.3841 | -67.0515 | -0.17797 | 0.033901 | 0.054209 | 0.023421 | 0.20139 | 0.00705 | 0.16759 | -0.40112 | -0.074332 | 0.044946 | -0.012452 | 0.38867 | 0.085114 | 0.051686 | 123.0167 | 122.9898 | 123.1504 | 63.2957 | -123.1608 | 122.9085 | 123.0679 | 123.0345 | 62.507 | -123.3839
1523.2656 | 123.2346 | -66.6321 | 56.3507 | 0.026888 | -0.11423 | -0.016058 | 0.04355 | -0.026635 | 0.055941 | 0.073406 | -0.0089857 | 0.0032574 | 0.045017 | 0.11621 | 0.047572 | -66.5962 | -3.3684 | -66.6224 | 56.3617 | 56.3349 | 56.5 | -66.8329 | -66.6054 | -4.1388 | -66.672 | 56.2581 | 56.4221 | 56.3887 | -67.0424 | -0.20086 | 0.011012 | 0.035898 | 0.009689 | 0.21054 | -0.01584 | 0.14928 | -0.41027 | -0.092643 | 0.026635 | -0.039921 | 0.37035 | 0.071382 | 0.037954 | 122.9938 | 122.9669 | 123.1321 | 63.2636 | -123.1836 | 122.8901 | 123.0542 | 123.0207 | 62.4933 | -123.3931
1524.2656 | 123.2391 | -66.6092 | 56.3599 | 0.04215 | -0.11316 | -0.016058 | 0.045687 | -0.025567 | 0.055941 | 0.042884 | -0.010054 | 0.0021894 | 0.042881 | 0.11407 | 0.047572 | -66.6008 | -3.3684 | -66.627 | 56.3617 | 56.3349 | 56.5046 | -66.8329 | -66.6009 | -4.1388 | -66.672 | 56.2581 | 56.4221 | 56.3932 | -67.0424 | -0.22374 | 0.001857 | 0.008431 | -0.017778 | 0.20597 | -0.024995 | 0.1447 | -0.43316 | -0.1018 | 0.008326 | -0.062809 | 0.37035 | 0.062227 | 0.033378 | 122.9709 | 122.9441 | 123.1138 | 63.2407 | -123.1928 | 122.8673 | 123.0313 | 123.0024 | 62.4704 | -123.4022
1525.2656 | 123.2529 | -66.6183 | 56.3461 | 0.057412 | -0.11423 | -0.014989 | 0.044618 | -0.027703 | 0.054873 | 0.058145 | -0.010054 | 0.0021894 | 0.042881 | 0.11835 | 0.047572 | -66.5962 | -3.3639 | -66.6315 | 56.3663 | 56.3394 | 56.5 | -66.8421 | -66.6054 | -4.1388 | -66.6674 | 56.2626 | 56.4267 | 56.3932 | -67.0469 | -0.22375 | 0.020168 | 0.022165 | -0.013201 | 0.21055 | -0.006683 | 0.15385 | -0.42858 | -0.083486 | 0.012902 | -0.049075 | 0.37951 | 0.080538 | 0.047111 | 122.9846 | 122.9578 | 123.1183 | 63.2545 | -123.1882 | 122.881 | 123.045 | 123.0116 | 62.4796 | -123.3931
1526.2656 | 123.1384 | -66.6458 | 56.3416 | 0.04215 | -0.1153 | -0.013921 | 0.045687 | -0.026635 | 0.054873 | 0.058145 | -0.010054 | 0.0021894 | 0.041812 | 0.11621 | 0.046504 | -66.6008 | -3.3639 | -66.6224 | 56.3571 | 56.3486 | 56.5 | -66.8284 | -66.6054 | -4.1388 | -66.6766 | 56.2626 | 56.4267 | 56.3841 | -67.0469 | -0.18254 | 0.015589 | 0.045052 | 0.023422 | 0.20597 | 0.007051 | 0.15843 | -0.40112 | -0.078909 | 0.040368 | -0.030766 | 0.37035 | 0.085115 | 0.04253 | 123.003 | 122.9944 | 123.1458 | 63.2819 | -123.1699 | 122.9085 | 123.0725 | 123.0299 | 62.507 | -123.3885
1527.2656 | 123.2574 | -66.6412 | 56.3049 | 0.057412 | -0.1153 | -0.016058 | 0.044618 | -0.028772 | 0.054873 | 0.042884 | -0.010054 | 0.0021894 | 0.041812 | 0.11407 | 0.046504 | -66.6008 | -3.3593 | -66.627 | 56.3709 | 56.344 | 56.4954 | -66.8375 | -66.6009 | -4.1434 | -66.6766 | 56.2672 | 56.4221 | 56.3932 | -67.0378 | -0.19628 | 0.065945 | 0.040474 | 0.014265 | 0.21054 | 0.039093 | 0.19047 | -0.39654 | -0.03771 | 0.040369 | -0.035344 | 0.36119 | 0.11716 | 0.088309 | 123.0121 | 122.9853 | 123.1366 | 63.2819 | -123.1424 | 122.9085 | 123.0633 | 123.0345 | 62.4979 | -123.3427
1528.2656 | 123.1888 | -66.6504 | 56.3507 | 0.04215 | -0.11209 | -0.014989 | 0.044618 | -0.025567 | 0.05701 | 0.073406 | -0.0079177 | 0.0032574 | 0.042881 | 0.11407 | 0.047572 | -66.5962 | -3.3547 | -66.6224 | 56.3755 | 56.344 | 56.5046 | -66.8329 | -66.6146 | -4.1388 | -66.6583 | 56.2672 | 56.4221 | 56.3887 | -67.0469 | -0.18254 | 0.024747 | 0.054209 | 0.028 | 0.21054 | -0.006683 | 0.15386 | -0.39654 | -0.083486 | 0.035789 | -0.007874 | 0.38867 | 0.071382 | 0.037954 | 123.0258 | 122.9944 | 123.155 | 63.2957 | -123.1836 | 122.9176 | 123.0725 | 123.0391 | 62.5116 | -123.3976
1529.2656 | 123.2208 | -66.6092 | 56.337 | 0.04215 | -0.11209 | -0.016058 | 0.042482 | -0.025567 | 0.054873 | 0.042884 | -0.0089857 | 0.0021894 | 0.045017 | 0.11621 | 0.047572 | -66.6053 | -3.3547 | -66.6315 | 56.3709 | 56.3394 | 56.5046 | -66.8375 | -66.6054 | -4.1388 | -66.672 | 56.2672 | 56.4221 | 56.3887 | -67.0515 | -0.22832 | 0.033902 | 0.003853 | -0.022356 | 0.20597 | 0.002472 | 0.16759 | -0.44232 | -0.069753 | 0.003747 | -0.062809 | 0.37951 | 0.085115 | 0.051687 | 122.9801 | 122.9486 | 123.1138 | 63.2545 | -123.1745 | 122.8764 | 123.0313 | 122.9979 | 62.4704 | -123.3885
1530.2656 | 123.2574 | -66.6092 | 56.3095 | 0.026888 | -0.11423 | -0.014989 | 0.04355 | -0.026635 | 0.05701 | 0.058145 | -0.010054 | 0.0021894 | 0.042881 | 0.11514 | 0.047572 | -66.6008 | -3.3547 | -66.6315 | 56.3709 | 56.3349 | 56.5046 | -66.8375 | -66.6054 | -4.1342 | -66.672 | 56.2626 | 56.4267 | 56.3887 | -67.0469 | -0.22832 | 0.061368 | 0.008431 | -0.022356 | 0.20597 | 0.025359 | 0.19505 | -0.43774 | -0.046865 | 0.003747 | -0.062809 | 0.37493 | 0.11716 | 0.079153 | 122.9801 | 122.9441 | 123.1138 | 63.2545 | -123.147 | 122.8718 | 123.0359 | 122.9979 | 62.475 | -123.3564
1531.2656 | 123.2712 | -66.6138 | 56.337 | 0.011626 | -0.11423 | -0.016058 | 0.044618 | -0.024498 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.043949 | 0.11514 | 0.047572 | -66.6008 | -3.3547 | -66.6315 | 56.3755 | 56.3394 | 56.5 | -66.8375 | -66.6054 | -4.1342 | -66.6674 | 56.2672 | 56.4312 | 56.3932 | -67.0515 | -0.22374 | 0.03848 | 0.013009 | -0.017778 | 0.20597 | 0.002472 | 0.16301 | -0.43774 | -0.069753 | 0.008325 | -0.053652 | 0.38409 | 0.094272 | 0.056266 | 122.9892 | 122.9532 | 123.1138 | 63.2591 | -123.1745 | 122.881 | 123.045 | 123.007 | 62.4796 | -123.3885
1532.2656 | 123.1476 | -66.655 | 56.3461 | 0.04215 | -0.11316 | -0.014989 | 0.044618 | -0.025567 | 0.054873 | 0.058145 | -0.0089857 | 0.0011204 | 0.042881 | 0.11514 | 0.045436 | -66.6053 | -3.3547 | -66.627 | 56.3709 | 56.3349 | 56.5091 | -66.8375 | -66.61 | -4.1342 | -66.672 | 56.2581 | 56.4267 | 56.3932 | -67.0469 | -0.18255 | 0.024747 | 0.049629 | 0.027998 | 0.21054 | -0.011262 | 0.16301 | -0.39196 | -0.088065 | 0.044945 | -0.017033 | 0.37493 | 0.080538 | 0.047111 | 123.0258 | 122.9898 | 123.1641 | 63.3003 | -123.1836 | 122.913 | 123.0816 | 123.0482 | 62.5208 | -123.3931
1533.2656 | 123.262 | -66.6183 | 56.3141 | 0.026888 | -0.1153 | -0.016058 | 0.042482 | -0.025567 | 0.0506 | 0.073406 | -0.011122 | 0.0021894 | 0.043949 | 0.11835 | 0.045436 | -66.6008 | -3.3593 | -66.627 | 56.3663 | 56.3349 | 56.5046 | -66.8329 | -66.61 | -4.1342 | -66.6674 | 56.2672 | 56.4267 | 56.3887 | -67.0469 | -0.21459 | 0.052211 | 0.017586 | -0.008623 | 0.20597 | 0.020781 | 0.19048 | -0.42858 | -0.046865 | 0.008324 | -0.049075 | 0.37951 | 0.11258 | 0.074575 | 122.9846 | 122.9532 | 123.1229 | 63.2591 | -123.147 | 122.8856 | 123.045 | 123.007 | 62.4841 | -123.361
1534.2656 | 123.262 | -66.6046 | 56.3141 | 0.057412 | -0.11423 | -0.017126 | 0.04355 | -0.025567 | 0.054873 | 0.042884 | -0.0089857 | 0.0032574 | 0.043949 | 0.11514 | 0.044367 | -66.6053 | -3.3456 | -66.6361 | 56.3709 | 56.344 | 56.5091 | -66.8421 | -66.6054 | -4.1388 | -66.672 | 56.2581 | 56.4267 | 56.3932 | -67.0469 | -0.23748 | 0.05679 | -0.000725 | -0.031512 | 0.20597 | 0.029938 | 0.19505 | -0.44232 | -0.056022 | -0.000831 | -0.067387 | 0.37493 | 0.11258 | 0.079154 | 122.9755 | 122.9486 | 123.1138 | 63.2591 | -123.1562 | 122.8627 | 123.0313 | 122.9979 | 62.4658 | -123.361
1535.2656 | 123.1659 | -66.6458 | 56.3324 | 0.04215 | -0.1153 | -0.016058 | 0.04355 | -0.024498 | 0.055941 | 0.073406 | -0.0089857 | 0.0021894 | 0.041812 | 0.11728 | 0.047572 | -66.6008 | -3.3456 | -66.6315 | 56.3663 | 56.344 | 56.5046 | -66.8421 | -66.6009 | -4.1342 | -66.672 | 56.2535 | 56.4221 | 56.3887 | -67.0469 | -0.19628 | 0.033901 | 0.045052 | 0.014265 | 0.21055 | 0.011628 | 0.17217 | -0.40112 | -0.07891 | 0.044947 | -0.026188 | 0.37493 | 0.089693 | 0.056265 | 123.0121 | 122.9898 | 123.1504 | 63.3003 | -123.1745 | 122.8993 | 123.0679 | 123.0345 | 62.5116 | -123.3793
1536.2656 | 123.1338 | -66.6641 | 56.3278 | 0.04215 | -0.11423 | -0.016058 | 0.044618 | -0.025567 | 0.054873 | 0.042884 | -0.0089857 | 0.0011204 | 0.043949 | 0.11621 | 0.047572 | -66.6008 | -3.3456 | -66.6315 | 56.3663 | 56.3394 | 56.5091 | -66.8421 | -66.6054 | -4.1342 | -66.6766 | 56.2626 | 56.4267 | 56.3932 | -67.0469 | -0.17797 | 0.038478 | 0.063363 | 0.032576 | 0.21055 | 0.011627 | 0.18132 | -0.38281 | -0.065176 | 0.058679 | -0.012455 | 0.37035 | 0.098848 | 0.065421 | 123.0304 | 123.0036 | 123.1733 | 63.3186 | -123.1699 | 122.9268 | 123.0908 | 123.0574 | 62.5299 | -123.3748
1537.2656 | 123.2529 | -66.5909 | 56.3004 | 0.04215 | -0.1153 | -0.016058 | 0.04355 | -0.026635 | 0.05701 | 0.058145 | -0.010054 | 0.0011204 | 0.045017 | 0.11407 | 0.047572 | -66.5962 | -3.3456 | -66.6361 | 56.3663 | 56.344 | 56.5091 | -66.8421 | -66.6009 | -4.1342 | -66.672 | 56.2581 | 56.4267 | 56.3932 | -67.0469 | -0.25121 | 0.065944 | -0.005301 | -0.045245 | 0.20597 | 0.043671 | 0.20879 | -0.45605 | -0.042289 | -0.009985 | -0.08112 | 0.37493 | 0.12631 | 0.092887 | 122.9572 | 122.9349 | 123.1 | 63.2453 | -123.1424 | 122.8489 | 123.0175 | 122.9841 | 62.4567 | -123.3473
1538.2656 | 123.2849 | -66.6229 | 56.3278 | 0.04215 | -0.1153 | -0.018194 | 0.044618 | -0.025567 | 0.055941 | 0.058145 | -0.0079177 | 0.0032574 | 0.045017 | 0.11514 | 0.046504 | -66.6053 | -3.3501 | -66.6315 | 56.3709 | 56.344 | 56.5091 | -66.8284 | -66.6054 | -4.1342 | -66.672 | 56.2535 | 56.4221 | 56.3841 | -67.0515 | -0.20543 | 0.043057 | 0.017586 | -0.008623 | 0.19681 | 0.016205 | 0.18132 | -0.42858 | -0.074333 | 0.01748 | -0.049076 | 0.37951 | 0.09427 | 0.056263 | 122.9938 | 122.9669 | 123.1321 | 63.2728 | -123.1562 | 122.8764 | 123.045 | 123.007 | 62.4887 | -123.3793
1539.2656 | 123.2986 | -66.6046 | 56.3141 | 0.026888 | -0.11637 | -0.016058 | 0.042482 | -0.026635 | 0.055941 | 0.042884 | -0.010054 | 0.0032574 | 0.043949 | 0.11621 | 0.046504 | -66.6053 | -3.3501 | -66.6315 | 56.3617 | 56.3349 | 56.5137 | -66.8375 | -66.6009 | -4.1296 | -66.6628 | 56.2626 | 56.4312 | 56.3841 | -67.0469 | -0.2329 | 0.047633 | -0.000725 | -0.026934 | 0.20597 | 0.020781 | 0.19963 | -0.44232 | -0.051443 | 0.003748 | -0.058229 | 0.38409 | 0.11716 | 0.069996 | 122.9663 | 122.9395 | 123.1183 | 63.2545 | -123.1516 | 122.8673 | 123.0359 | 122.9887 | 62.475 | -123.361
1540.2656 | 123.1293 | -66.6733 | 56.3828 | 0.04215 | -0.1153 | -0.014989 | 0.04355 | -0.027703 | 0.054873 | 0.058145 | -0.010054 | 0.0053944 | 0.045017 | 0.11621 | 0.047572 | -66.6053 | -3.3501 | -66.6361 | 56.3617 | 56.3394 | 56.5046 | -66.8329 | -66.61 | -4.1251 | -66.6766 | 56.2626 | 56.4312 | 56.3887 | -67.0515 | -0.15966 | -0.021031 | 0.06794 | 0.037153 | 0.19681 | -0.043304 | 0.12181 | -0.37823 | -0.12011 | 0.063256 | -0.0033 | 0.37493 | 0.048496 | 0.005911 | 123.035 | 123.0127 | 123.1778 | 63.3231 | -123.2157 | 122.9359 | 123.1045 | 123.0619 | 62.5482 | -123.4343
1541.2656 | 123.1659 | -66.6779 | 56.337 | 0.026888 | -0.1153 | -0.013921 | 0.046755 | -0.025567 | 0.05701 | 0.042884 | -0.010054 | 0.0032574 | 0.041812 | 0.11621 | 0.046504 | -66.5962 | -3.3456 | -66.627 | 56.3663 | 56.3394 | 56.5046 | -66.8284 | -66.6054 | -4.1296 | -66.672 | 56.2581 | 56.4267 | 56.3841 | -67.0515 | -0.1505 | 0.029323 | 0.081674 | 0.050886 | 0.20139 | 0.002472 | 0.16759 | -0.37365 | -0.07891 | 0.072411 | 0.005855 | 0.37951 | 0.089693 | 0.047108 | 123.0442 | 123.0173 | 123.1824 | 63.3323 | -123.1653 | 122.9359 | 123.1045 | 123.0619 | 62.5482 | -123.3885
1542.2656 | 123.1567 | -66.6458 | 56.369 | 0.04215 | -0.11744 | -0.013921 | 0.044618 | -0.026635 | 0.052737 | 0.073406 | -0.0089857 | 0.0011204 | 0.045017 | 0.11835 | 0.046504 | -66.5962 | -3.3456 | -66.6361 | 56.3663 | 56.3303 | 56.5091 | -66.8329 | -66.61 | -4.1388 | -66.6674 | 56.2626 | 56.4312 | 56.3887 | -67.0469 | -0.18712 | -0.002721 | 0.049631 | 0.009687 | 0.19681 | -0.03873 | 0.14012 | -0.40112 | -0.10637 | 0.03579 | -0.021609 | 0.37951 | 0.062228 | 0.019643 | 123.0121 | 122.9761 | 123.155 | 63.3003 | -123.202 | 122.9085 | 123.0771 | 123.0345 | 62.507 | -123.416
1543.2656 | 123.1888 | -66.6412 | 56.3324 | 0.04215 | -0.11423 | -0.017126 | 0.04355 | -0.027703 | 0.054873 | 0.058145 | -0.0089857 | 0.0021894 | 0.042881 | 0.11728 | 0.049709 | -66.6008 | -3.3456 | -66.6361 | 56.3663 | 56.3349 | 56.5046 | -66.8284 | -66.6146 | -4.1388 | -66.672 | 56.2581 | 56.4267 | 56.3841 | -67.0469 | -0.18712 | 0.033901 | 0.040474 | 0.005109 | 0.19223 | 0.002471 | 0.17217 | -0.4057 | -0.074332 | 0.026633 | -0.030766 | 0.37493 | 0.094271 | 0.051686 | 123.0075 | 122.9761 | 123.1458 | 63.2957 | -123.1608 | 122.8993 | 123.0679 | 123.0253 | 62.5024 | -123.3793
1544.2656 | 123.2758 | -66.6275 | 56.3004 | 0.026888 | -0.11637 | -0.016058 | 0.04355 | -0.026635 | 0.053805 | 0.042884 | -0.0089857 | 0.0021894 | 0.042881 | 0.11621 | 0.047572 | -66.5962 | -3.341 | -66.6361 | 56.3617 | 56.3303 | 56.5046 | -66.8329 | -66.61 | -4.1296 | -66.6766 | 56.2581 | 56.4312 | 56.3841 | -67.0469 | -0.20543 | 0.061366 | 0.03132 | -0.008624 | 0.19681 | 0.029935 | 0.20421 | -0.41943 | -0.042289 | 0.017479 | -0.049077 | 0.37035 | 0.13089 | 0.083729 | 122.9892 | 122.9578 | 123.1321 | 63.2865 | -123.1333 | 122.8856 | 123.0587 | 123.0116 | 62.4979 | -123.3473
1545.2656 | 123.2849 | -66.6321 | 56.3324 | 0.026888 | -0.11637 | -0.016058 | 0.041413 | -0.026635 | 0.054873 | 0.042884 | -0.010054 | 0.0021894 | 0.045017 | 0.11728 | 0.046504 | -66.6008 | -3.3456 | -66.6361 | 56.3617 | 56.3349 | 56.5137 | -66.8284 | -66.61 | -4.1296 | -66.6812 | 56.2672 | 56.4312 | 56.3887 | -67.0469 | -0.19628 | 0.029323 | 0.031319 | -0.004046 | 0.19223 | 0.002471 | 0.18132 | -0.41485 | -0.065175 | 0.022057 | -0.049078 | 0.36577 | 0.09885 | 0.056265 | 122.9938 | 122.9669 | 123.1458 | 63.2865 | -123.1608 | 122.8993 | 123.0633 | 123.0207 | 62.5024 | -123.3793
1546.2656 | 123.2208 | -66.6458 | 56.3324 | 0.026888 | -0.1153 | -0.014989 | 0.046755 | -0.027703 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.042881 | 0.11621 | 0.045436 | -66.6008 | -3.3456 | -66.627 | 56.3709 | 56.3349 | 56.5046 | -66.8329 | -66.6054 | -4.1296 | -66.672 | 56.2626 | 56.4358 | 56.3887 | -67.0424 | -0.18712 | 0.03848 | 0.045052 | 0.018843 | 0.20597 | 0.002471 | 0.17217 | -0.39654 | -0.069753 | 0.040368 | -0.026188 | 0.37035 | 0.10343 | 0.056265 | 123.0167 | 122.9807 | 123.1504 | 63.3003 | -123.1653 | 122.9085 | 123.0816 | 123.0345 | 62.5162 | -123.3748
1547.2656 | 123.1338 | -66.6641 | 56.3553 | 0.026888 | -0.11744 | -0.016058 | 0.044618 | -0.027703 | 0.054873 | 0.073406 | -0.0079177 | 0.0021894 | 0.043949 | 0.11728 | 0.047572 | -66.6008 | -3.3364 | -66.627 | 56.3663 | 56.3394 | 56.5046 | -66.8329 | -66.61 | -4.1342 | -66.6766 | 56.2672 | 56.4358 | 56.3841 | -67.0469 | -0.16881 | 0.011012 | 0.063363 | 0.037154 | 0.20597 | -0.015839 | 0.14928 | -0.38281 | -0.088064 | 0.054101 | -0.012455 | 0.37035 | 0.080539 | 0.028797 | 123.0304 | 123.0036 | 123.1687 | 63.3277 | -123.1882 | 122.9313 | 123.0999 | 123.0482 | 62.5299 | -123.4022
1548.2656 | 123.143 | -66.655 | 56.3416 | 0.04215 | -0.11744 | -0.017126 | 0.044618 | -0.026635 | 0.055941 | 0.073406 | -0.0089857 | 0.0021894 | 0.040744 | 0.11728 | 0.047572 | -66.6008 | -3.3456 | -66.6315 | 56.3663 | 56.3349 | 56.5046 | -66.8421 | -66.6054 | -4.1342 | -66.6674 | 56.2626 | 56.4221 | 56.3887 | -67.0515 | -0.18713 | 0.024745 | 0.054207 | 0.02342 | 0.21055 | -0.006685 | 0.16301 | -0.39654 | -0.078909 | 0.049523 | -0.012454 | 0.38409 | 0.080537 | 0.047109 | 123.0213 | 122.9898 | 123.1595 | 63.3094 | -123.1836 | 122.9176 | 123.0771 | 123.0436 | 62.5208 | -123.3931
1549.2656 | 123.2483 | -66.6367 | 56.3141 | 0.04215 | -0.11744 | -0.016058 | 0.04355 | -0.026635 | 0.055941 | 0.042884 | -0.010054 | 0.0021894 | 0.041812 | 0.11728 | 0.048641 | -66.6053 | -3.3547 | -66.6315 | 56.3663 | 56.3394 | 56.5091 | -66.8284 | -66.61 | -4.1388 | -66.6674 | 56.2626 | 56.4312 | 56.3841 | -67.0561 | -0.1917 | 0.052211 | 0.031319 | 0.00511 | 0.19681 | 0.02536 | 0.19505 | -0.41943 | -0.051443 | 0.026635 | -0.030764 | 0.38867 | 0.11716 | 0.069996 | 123.003 | 122.9761 | 123.1458 | 63.2819 | -123.1424 | 122.8993 | 123.0679 | 123.0207 | 62.4979 | -123.3702
1550.2656 | 123.1659 | -66.6779 | 56.3553 | 0.057412 | -0.11423 | -0.014989 | 0.044618 | -0.027703 | 0.054873 | 0.058145 | -0.010054 | 0.0043254 | 0.042881 | 0.11728 | 0.046504 | -66.6008 | -3.341 | -66.6361 | 56.3709 | 56.3394 | 56.5046 | -66.8375 | -66.6054 | -4.1388 | -66.6674 | 56.2581 | 56.4312 | 56.3841 | -67.0469 | -0.15966 | 0.015591 | 0.077095 | 0.04173 | 0.20139 | -0.015839 | 0.14928 | -0.36908 | -0.097221 | 0.072411 | 0.010434 | 0.37951 | 0.075961 | 0.028797 | 123.0487 | 123.0173 | 123.1824 | 63.3369 | -123.1928 | 122.9359 | 123.1091 | 123.0619 | 62.5391 | -123.4022
1551.2656 | 123.1842 | -66.655 | 56.337 | 0.04215 | -0.1153 | -0.016058 | 0.044618 | -0.028772 | 0.05701 | 0.042884 | -0.010054 | 0.0021894 | 0.041812 | 0.11835 | 0.045436 | -66.6008 | -3.3364 | -66.6224 | 56.3663 | 56.3349 | 56.5046 | -66.8284 | -66.6054 | -4.1342 | -66.672 | 56.2626 | 56.4404 | 56.3932 | -67.0469 | -0.17339 | 0.029323 | 0.054207 | 0.032577 | 0.20597 | -0.002107 | 0.16759 | -0.39196 | -0.074331 | 0.049523 | -0.017033 | 0.37493 | 0.10343 | 0.056266 | 123.0213 | 122.9898 | 123.1595 | 63.3186 | -123.1653 | 122.9176 | 123.0954 | 123.0482 | 62.5208 | -123.3839
1552.2656 | 123.1567 | -66.6641 | 56.3736 | 0.011626 | -0.11744 | -0.014989 | 0.045687 | -0.026635 | 0.055941 | 0.058145 | -0.010054 | 0.0053944 | 0.041812 | 0.11835 | 0.047572 | -66.6008 | -3.3456 | -66.627 | 56.3709 | 56.3486 | 56.5 | -66.8375 | -66.6009 | -4.1342 | -66.6766 | 56.2672 | 56.4267 | 56.3978 | -67.0515 | -0.17339 | -0.002719 | 0.063363 | 0.037154 | 0.21054 | -0.024992 | 0.12639 | -0.38739 | -0.10637 | 0.063258 | -0.012455 | 0.37493 | 0.053072 | 0.024223 | 123.035 | 123.0127 | 123.1641 | 63.3186 | -123.2111 | 122.9313 | 123.0908 | 123.0619 | 62.5299 | -123.4251
1553.2656 | 123.2483 | -66.6412 | 56.2912 | 0.011626 | -0.1153 | -0.014989 | 0.04355 | -0.026635 | 0.055941 | 0.042884 | -0.0089857 | 0.0043254 | 0.041812 | 0.11942 | 0.046504 | -66.6099 | -3.341 | -66.6361 | 56.3663 | 56.3394 | 56.5046 | -66.8284 | -66.6146 | -4.1342 | -66.672 | 56.2672 | 56.4221 | 56.3887 | -67.0469 | -0.18712 | 0.075099 | 0.031318 | 0.005109 | 0.19223 | 0.048248 | 0.21336 | -0.4057 | -0.023977 | 0.026633 | -0.030766 | 0.37493 | 0.13089 | 0.097463 | 123.0075 | 122.9807 | 123.1458 | 63.3003 | -123.1196 | 122.9085 | 123.0633 | 123.0299 | 62.507 | -123.3381
1554.2656 | 123.2254 | -66.5955 | 56.369 | 0.04215 | -0.11637 | -0.017126 | 0.04355 | -0.026635 | 0.054873 | 0.073406 | -0.01219 | 0.0021894 | 0.041812 | 0.11728 | 0.047572 | -66.5916 | -3.3501 | -66.6361 | 56.3663 | 56.3394 | 56.5091 | -66.8467 | -66.61 | -4.1342 | -66.672 | 56.2626 | 56.4267 | 56.3887 | -67.0561 | -0.25121 | -0.002721 | 0.003855 | -0.040667 | 0.21055 | -0.029572 | 0.14012 | -0.46063 | -0.10637 | -0.014564 | -0.076542 | 0.38409 | 0.057649 | 0.019643 | 122.9618 | 122.9349 | 123.1046 | 63.2453 | -123.2157 | 122.8581 | 123.0221 | 122.9841 | 62.4612 | -123.4251
1555.2656 | 123.1155 | -66.6916 | 56.3416 | 0.011626 | -0.1185 | -0.016058 | 0.044618 | -0.027703 | 0.054873 | 0.042884 | -0.010054 | 0.0021894 | 0.042881 | 0.11621 | 0.045436 | -66.6008 | -3.3456 | -66.6315 | 56.3755 | 56.3394 | 56.5091 | -66.8421 | -66.61 | -4.1388 | -66.6766 | 56.2672 | 56.4312 | 56.3932 | -67.0515 | -0.1505 | 0.033902 | 0.090828 | 0.060041 | 0.21055 | -0.002106 | 0.16759 | -0.35992 | -0.074331 | 0.081566 | 0.01501 | 0.37493 | 0.089694 | 0.051688 | 123.067 | 123.031 | 123.2007 | 63.346 | -123.1836 | 122.9588 | 123.1228 | 123.0848 | 62.5528 | -123.3931
1556.2656 | 123.175 | -66.6458 | 56.3507 | 0.04215 | -0.11637 | -0.017126 | 0.04355 | -0.026635 | 0.054873 | 0.027623 | -0.011122 | 0.0043254 | 0.042881 | 0.11728 | 0.047572 | -66.6008 | -3.3547 | -66.627 | 56.38 | 56.344 | 56.5183 | -66.8375 | -66.6146 | -4.1342 | -66.672 | 56.2581 | 56.4312 | 56.3932 | -67.0515 | -0.1917 | 0.029326 | 0.045052 | 0.018843 | 0.21054 | -0.006683 | 0.16759 | -0.4057 | -0.092643 | 0.031211 | -0.026188 | 0.37951 | 0.080539 | 0.042533 | 123.0258 | 122.9898 | 123.1641 | 63.2911 | -123.1882 | 122.9039 | 123.0771 | 123.0391 | 62.5116 | -123.4022
1557.2656 | 123.1934 | -66.655 | 56.3507 | 0.057412 | -0.11744 | -0.016058 | 0.04355 | -0.025567 | 0.053805 | 0.058145 | -0.011122 | 0.0011204 | 0.042881 | 0.11728 | 0.045436 | -66.6053 | -3.3501 | -66.627 | 56.3663 | 56.344 | 56.5137 | -66.8375 | -66.6146 | -4.1342 | -66.6766 | 56.2626 | 56.4312 | 56.3887 | -67.0561 | -0.18255 | 0.01559 | 0.049629 | 0.027998 | 0.21054 | -0.006683 | 0.16301 | -0.40112 | -0.088064 | 0.040366 | -0.021611 | 0.37951 | 0.080539 | 0.037954 | 123.0213 | 122.999 | 123.1687 | 63.3048 | -123.1882 | 122.9176 | 123.0862 | 123.0436 | 62.5208 | -123.4068
1558.2656 | 123.1613 | -66.6595 | 56.3278 | 0.026888 | -0.11744 | -0.017126 | 0.044618 | -0.027703 | 0.053805 | 0.058145 | -0.0089857 | 0.0032574 | 0.042881 | 0.11728 | 0.046504 | -66.6008 | -3.341 | -66.627 | 56.3709 | 56.3394 | 56.5091 | -66.8467 | -66.61 | -4.1342 | -66.6766 | 56.2626 | 56.4221 | 56.3887 | -67.0469 | -0.18713 | 0.043057 | 0.058785 | 0.032576 | 0.2197 | 0.011627 | 0.18132 | -0.38739 | -0.065176 | 0.049523 | -0.017033 | 0.37035 | 0.09427 | 0.060842 | 123.0304 | 122.999 | 123.1687 | 63.3186 | -123.1745 | 122.9222 | 123.0816 | 123.0482 | 62.5253 | -123.3748
1559.2656 | 123.3444 | -66.6229 | 56.3095 | 0.011626 | -0.11744 | -0.016058 | 0.042482 | -0.026635 | 0.055941 | 0.058145 | -0.0079177 | 0.0032574 | 0.042881 | 0.11728 | 0.045436 | -66.6053 | -3.3456 | -66.6361 | 56.3755 | 56.3486 | 56.5091 | -66.8329 | -66.6054 | -4.1388 | -66.672 | 56.2626 | 56.4358 | 56.3932 | -67.0515 | -0.21001 | 0.065946 | 0.017586 | -0.013201 | 0.19681 | 0.039095 | 0.19963 | -0.42858 | -0.046865 | 0.01748 | -0.049076 | 0.37951 | 0.12632 | 0.083732 | 122.9984 | 122.9715 | 123.1321 | 63.2774 | -123.1424 | 122.8856 | 123.0588 | 123.0162 | 62.4841 | -123.361
1560.2656 | 123.1522 | -66.6412 | 56.3599 | 0.026888 | -0.11744 | -0.016058 | 0.044618 | -0.024498 | 0.054873 | 0.058145 | -0.011122 | 0.0032574 | 0.042881 | 0.11835 | 0.046504 | -66.6008 | -3.3456 | -66.6453 | 56.3709 | 56.344 | 56.5137 | -66.8421 | -66.61 | -4.1434 | -66.672 | 56.2581 | 56.4267 | 56.3978 | -67.0469 | -0.20086 | 0.011014 | 0.040474 | -0.004048 | 0.19681 | -0.015838 | 0.15386 | -0.4057 | -0.1018 | 0.031212 | -0.030766 | 0.37493 | 0.066805 | 0.037956 | 123.0121 | 122.9853 | 123.155 | 63.2957 | -123.202 | 122.8993 | 123.0679 | 123.0391 | 62.4979 | -123.4068
1561.2656 | 123.1338 | -66.6504 | 56.3599 | 0.026888 | -0.1185 | -0.016058 | 0.04355 | -0.027703 | 0.054873 | 0.073406 | -0.0089857 | 0.0021894 | 0.042881 | 0.11621 | 0.046504 | -66.6008 | -3.3501 | -66.6361 | 56.3709 | 56.3486 | 56.5183 | -66.8513 | -66.6054 | -4.1434 | -66.6674 | 56.2626 | 56.4358 | 56.3932 | -67.0515 | -0.20086 | 0.011014 | 0.04963 | 0.014265 | 0.21513 | -0.011259 | 0.15844 | -0.40112 | -0.097219 | 0.044946 | -0.017031 | 0.38409 | 0.075962 | 0.033378 | 123.0213 | 122.999 | 123.1687 | 63.3003 | -123.2111 | 122.913 | 123.0862 | 123.0436 | 62.507 | -123.4114
1562.2656 | 123.1659 | -66.6641 | 56.3324 | 0.04215 | -0.11744 | -0.017126 | 0.04355 | -0.027703 | 0.055941 | 0.058145 | -0.0089857 | 0.0032574 | 0.043949 | 0.11728 | 0.046504 | -66.6053 | -3.3456 | -66.6315 | 56.3755 | 56.344 | 56.5183 | -66.8375 | -66.6146 | -4.1434 | -66.6674 | 56.2535 | 56.4267 | 56.3932 | -67.0515 | -0.17339 | 0.043058 | 0.058785 | 0.032576 | 0.20597 | 0.011628 | 0.1859 | -0.38739 | -0.07891 | 0.049522 | -0.003298 | 0.38409 | 0.094271 | 0.060844 | 123.0396 | 123.0081 | 123.1824 | 63.3186 | -123.1699 | 122.9176 | 123.0908 | 123.0574 | 62.5208 | -123.3839
1563.2656 | 123.1384 | -66.6412 | 56.3736 | 0.04215 | -0.1185 | -0.017126 | 0.046755 | -0.027703 | 0.054873 | 0.027623 | -0.011122 | 0.0032574 | 0.043949 | 0.11835 | 0.046504 | -66.5962 | -3.3456 | -66.6315 | 56.3755 | 56.3394 | 56.5137 | -66.8375 | -66.6054 | -4.1342 | -66.6674 | 56.2672 | 56.4312 | 56.3978 | -67.0469 | -0.19628 | 0.001859 | 0.045053 | 0.009687 | 0.20597 | -0.034149 | 0.14012 | -0.4057 | -0.10637 | 0.03579 | -0.026187 | 0.37951 | 0.057651 | 0.024223 | 123.0167 | 122.9807 | 123.155 | 63.2957 | -123.2111 | 122.9085 | 123.0725 | 123.0391 | 62.507 | -123.4205
1564.2656 | 123.2712 | -66.6321 | 56.3004 | 0.026888 | -0.11744 | -0.016058 | 0.042482 | -0.026635 | 0.054873 | 0.042884 | -0.010054 | 0.0021894 | 0.045017 | 0.11728 | 0.046504 | -66.6053 | -3.3364 | -66.627 | 56.3755 | 56.344 | 56.5137 | -66.8421 | -66.6054 | -4.1434 | -66.672 | 56.2626 | 56.4404 | 56.3978 | -67.0515 | -0.21001 | 0.075101 | 0.026741 | 0.00511 | 0.21512 | 0.043671 | 0.21337 | -0.41943 | -0.03771 | 0.026635 | -0.039921 | 0.37951 | 0.14005 | 0.097465 | 123.0075 | 122.9761 | 123.1458 | 63.2957 | -123.1424 | 122.8947 | 123.0725 | 123.0299 | 62.4887 | -123.3519
1565.2656 | 123.143 | -66.6641 | 56.3416 | 0.057412 | -0.1153 | -0.018194 | 0.042482 | -0.026635 | 0.055941 | 0.042884 | -0.010054 | 0.0021894 | 0.042881 | 0.11728 | 0.045436 | -66.6053 | -3.3456 | -66.6315 | 56.3709 | 56.344 | 56.5137 | -66.8375 | -66.6054 | -4.148 | -66.672 | 56.2672 | 56.4312 | 56.3978 | -67.0469 | -0.17339 | 0.029324 | 0.058785 | 0.032576 | 0.20597 | 0.002472 | 0.17217 | -0.38281 | -0.074331 | 0.058679 | -0.007877 | 0.37493 | 0.089694 | 0.056266 | 123.035 | 123.0081 | 123.1778 | 63.3186 | -123.1791 | 122.9313 | 123.0954 | 123.0619 | 62.5162 | -123.3885
1566.2656 | 123.1567 | -66.6367 | 56.3507 | 0.026888 | -0.11744 | -0.014989 | 0.042482 | -0.027703 | 0.054873 | 0.027623 | -0.010054 | 0.0011204 | 0.042881 | 0.11835 | 0.045436 | -66.6008 | -3.3364 | -66.6315 | 56.3709 | 56.344 | 56.5137 | -66.8329 | -66.6146 | -4.1525 | -66.6766 | 56.2626 | 56.4221 | 56.3932 | -67.0515 | -0.19628 | 0.020169 | 0.035897 | 0.00511 | 0.20139 | -0.006683 | 0.16301 | -0.41485 | -0.088064 | 0.022056 | -0.039921 | 0.37493 | 0.071382 | 0.042533 | 123.0075 | 122.9807 | 123.1504 | 63.3003 | -123.1836 | 122.8993 | 123.0587 | 123.0299 | 62.4841 | -123.4022

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.574 | 42.4423 | 27.8236 | 28.0462
0.426 | 42.4358 | 27.834 | 28.0551
1.426 | 42.6797 | 27.846 | 28.0593
2.426 | 43.5559 | 27.8473 | 28.0703
3.426 | 45.1485 | 27.8559 | 28.0838
4.426 | 47.3765 | 27.8703 | 28.0921
5.426 | 50.1665 | 27.8831 | 28.1058
6.426 | 53.3765 | 27.9022 | 28.1181
7.426 | 57.0262 | 27.9198 | 28.1427
8.426 | 61.0148 | 27.944 | 28.1816
9.426 | 65.2857 | 27.9742 | 28.223
10.426 | 69.8023 | 28.0029 | 28.2595
11.426 | 74.5295 | 28.0429 | 28.3137
12.426 | 79.4514 | 28.1036 | 28.3751
13.426 | 84.5312 | 28.1517 | 28.4429
14.426 | 89.7533 | 28.211 | 28.5166
15.426 | 95.1115 | 28.2882 | 28.6077
16.426 | 100.606 | 28.3588 | 28.7095
17.426 | 106.2058 | 28.4587 | 28.8167
18.426 | 111.8025 | 28.5511 | 28.9451
19.426 | 117.5219 | 28.6647 | 29.0797
20.426 | 123.3085 | 28.7844 | 29.2262
21.426 | 129.1299 | 28.9095 | 29.3955
22.426 | 135.0655 | 29.0534 | 29.5644
23.426 | 141.0418 | 29.2024 | 29.7614
24.426 | 146.9106 | 29.3724 | 29.963
25.426 | 152.8329 | 29.5463 | 30.1912
26.426 | 158.6907 | 29.7421 | 30.4219
27.426 | 164.5206 | 29.9398 | 30.6865
28.426 | 170.4283 | 30.1641 | 30.9492
29.426 | 176.3811 | 30.397 | 31.2341
30.426 | 182.3075 | 30.6398 | 31.5316
31.426 | 188.1771 | 30.9005 | 31.8459
32.426 | 194.0733 | 31.1756 | 32.1929
33.426 | 200.0571 | 31.4704 | 32.5418
34.426 | 206.023 | 31.7713 | 32.922
35.426 | 211.8499 | 32.094 | 33.3095
36.426 | 217.5286 | 32.4296 | 33.7209
37.426 | 223.3331 | 32.7784 | 34.1539
38.426 | 229.2461 | 33.1436 | 34.6127
39.426 | 235.0869 | 33.5271 | 35.0912
40.426 | 240.8965 | 33.9271 | 35.5822
41.426 | 246.6849 | 34.3348 | 36.1074
42.426 | 252.4745 | 34.7762 | 36.6444
43.426 | 258.2988 | 35.244 | 37.1918
44.426 | 264.0324 | 35.7237 | 37.7745
45.426 | 269.7656 | 36.2308 | 38.3776
46.426 | 275.4716 | 36.7506 | 39.003
47.426 | 281.0686 | 37.2754 | 39.6529
48.426 | 286.6477 | 37.8323 | 40.3289
49.426 | 292.3312 | 38.3995 | 41.0145
50.426 | 297.946 | 38.9862 | 41.7319
51.426 | 303.4683 | 39.5815 | 42.4726
52.426 | 309.0443 | 40.2031 | 43.2298
53.426 | 314.589 | 40.8349 | 44.0172
54.426 | 320.0061 | 41.4945 | 44.8144
55.426 | 325.4025 | 42.1787 | 45.6564
56.426 | 330.5188 | 42.8901 | 46.5033
57.426 | 335.7077 | 43.6082 | 47.3914
58.426 | 341.1229 | 44.3676 | 48.2898
59.426 | 346.5501 | 45.1459 | 49.2405
60.426 | 351.8681 | 45.954 | 50.2021
61.426 | 357.1221 | 46.7729 | 51.193
62.426 | 362.4739 | 47.6207 | 52.214
63.426 | 367.6605 | 48.4812 | 53.266
64.426 | 372.6861 | 49.3575 | 54.3142
65.426 | 377.7774 | 50.28 | 55.3959
66.426 | 382.7751 | 51.1929 | 56.4805
67.426 | 387.9129 | 52.1485 | 57.5946
68.426 | 393.0448 | 53.1177 | 58.7261
69.426 | 398.0771 | 54.1176 | 59.871
70.426 | 403.1156 | 55.137 | 61.0389
71.426 | 408.152 | 56.1513 | 62.2213
72.426 | 413.115 | 57.2165 | 63.4377
73.426 | 417.8663 | 58.2994 | 64.6651
74.426 | 422.5367 | 59.4288 | 65.9362
75.426 | 427.1736 | 60.553 | 67.2856
76.426 | 431.977 | 61.7411 | 68.6777
77.426 | 436.7701 | 62.9458 | 70.103
78.426 | 441.4557 | 64.1842 | 71.5491
79.426 | 445.9865 | 65.4386 | 73.0195
80.426 | 450.6636 | 66.7307 | 74.5211
81.426 | 455.3211 | 68.0528 | 76.0387
82.426 | 459.9092 | 69.4163 | 77.6019
83.426 | 464.3798 | 70.7954 | 79.2082
84.426 | 468.7879 | 72.2304 | 80.8368
85.426 | 473.23 | 73.7081 | 82.5142
86.426 | 477.7316 | 75.208 | 84.2581
87.426 | 482.1998 | 76.7454 | 86.0145
88.426 | 486.7612 | 78.3294 | 87.8362
89.426 | 491.0984 | 79.9481 | 89.7244
90.426 | 495.4758 | 81.6117 | 91.6609
91.426 | 499.7851 | 83.3298 | 93.6672
92.426 | 503.8836 | 85.0727 | 95.7711
93.426 | 507.744 | 86.8547 | 97.9682
94.426 | 511.6427 | 88.6907 | 100.2039
95.426 | 515.6324 | 90.5643 | 102.5001
96.426 | 519.6429 | 92.5036 | 104.8441
97.426 | 523.6938 | 94.4712 | 107.2377
98.426 | 527.6835 | 96.4936 | 109.6888
99.426 | 531.6522 | 98.5874 | 112.2311
100.426 | 535.2714 | 100.7058 | 114.8161
101.426 | 538.9131 | 102.8812 | 117.4379
102.426 | 542.6125 | 105.1015 | 120.0942
103.426 | 546.274 | 107.3728 | 122.7849
104.426 | 549.8732 | 109.6636 | 125.4698
105.426 | 553.4927 | 112.0276 | 128.1839
106.426 | 556.7745 | 114.402 | 130.9277
107.426 | 560.1923 | 116.8006 | 133.6982
108.426 | 563.4418 | 119.2433 | 136.4793
109.426 | 566.5179 | 121.6768 | 139.2714
110.426 | 569.4525 | 124.0691 | 142.0264
111.426 | 572.0271 | 126.4159 | 144.7198
112.426 | 574.8353 | 128.7789 | 147.3708
113.426 | 577.388 | 131.1359 | 150.0262
114.426 | 580.1646 | 133.4881 | 152.6383
115.426 | 582.964 | 135.8496 | 155.225
116.426 | 585.7909 | 138.2123 | 157.8261
117.426 | 588.2856 | 140.6041 | 160.4631
118.426 | 591.2336 | 143.027 | 163.1006
119.426 | 594.2342 | 145.4487 | 165.745
120.426 | 597.3069 | 147.9072 | 168.4293
121.426 | 600.1613 | 150.422 | 171.1461
122.426 | 602.6764 | 152.9785 | 173.8876
123.426 | 605.4126 | 155.5483 | 176.6362
124.426 | 608.412 | 158.1448 | 179.4197
125.426 | 611.1698 | 160.7869 | 182.2276
126.426 | 613.8248 | 163.4405 | 185.0717
127.426 | 616.791 | 166.1361 | 187.9776
128.426 | 619.7351 | 168.9031 | 190.955
129.426 | 622.6641 | 171.7277 | 193.9527
130.426 | 625.5712 | 174.614 | 196.984
131.426 | 628.6874 | 177.5488 | 200.0599
132.426 | 631.8278 | 180.5642 | 203.1873
133.426 | 634.5136 | 183.6258 | 206.3689
134.426 | 637.0981 | 186.7088 | 209.6142
135.426 | 639.8195 | 189.8423 | 212.8832
136.426 | 642.3352 | 193.0248 | 216.19
137.426 | 644.597 | 196.237 | 219.6061
138.426 | 646.6304 | 199.4333 | 223.0854
139.426 | 649.0551 | 202.518 | 226.5969
140.426 | 650.6742 | 205.5795 | 230.0836
141.426 | 652.7328 | 208.6122 | 233.5173
142.426 | 654.5249 | 211.5648 | 236.8326
143.426 | 656.4099 | 214.4729 | 240.1684
144.426 | 658.2889 | 217.5327 | 243.5052
145.426 | 660.0873 | 220.8405 | 246.7516
146.426 | 661.5658 | 224.3064 | 250.0182
147.426 | 662.9659 | 228.0077 | 253.2777
148.426 | 664.5812 | 231.8311 | 256.3053
149.426 | 666.3622 | 235.5483 | 259.4948
150.426 | 668.3403 | 239.0015 | 262.6262
151.426 | 670.0008 | 242.1791 | 265.7461
152.426 | 671.5978 | 245.1086 | 268.9223
153.426 | 673.0178 | 247.9329 | 272.076
154.426 | 675.0936 | 250.6248 | 275.0993
155.426 | 677.1257 | 253.0778 | 277.9045
156.426 | 678.8297 | 255.6333 | 280.7798
157.426 | 680.0644 | 258.9742 | 285.1585
158.426 | 681.6162 | 264.0249 | 291.7486
159.426 | 683.2557 | 269.579 | 298.6528
160.426 | 684.7716 | 275.2645 | 305.3213
161.426 | 686.1808 | 280.9237 | 312.0836
162.426 | 687.5671 | 286.317 | 318.7279
163.426 | 688.6774 | 291.3994 | 325.539
164.426 | 689.7258 | 296.3251 | 332.6322
165.426 | 690.6612 | 300.815 | 339.9413
166.426 | 691.4897 | 305.4828 | 347.8247
167.426 | 691.8364 | 310.8109 | 356.3111
168.426 | 692.2573 | 316.4274 | 364.7279
169.426 | 692.1797 | 322.3727 | 373.2949
170.426 | 692.1947 | 328.395 | 382.2082
171.426 | 692.229 | 333.2406 | 391.4926
172.426 | 692.4498 | 338.4815 | 400.1096
173.426 | 692.8664 | 344.777 | 409.2852
174.426 | 693.3518 | 350.2108 | 418.2128
175.426 | 693.6479 | 355.5982 | 426.8634
176.426 | 693.5575 | 361.086 | 434.649
177.426 | 694.0179 | 366.1545 | 443.178
178.426 | 694.4014 | 372.4083 | 450.2323
179.426 | 694.8907 | 378.5272 | 457.2239
180.426 | 695.1745 | 384.1347 | 463.6886
181.426 | 695.3832 | 388.8071 | 469.5087
182.426 | 695.3487 | 393.951 | 474.9613
183.426 | 695.998 | 400.0921 | 480.3611
184.426 | 696.4104 | 406.0655 | 486.0895
185.426 | 696.686 | 411.9096 | 491.1068
186.426 | 697.2364 | 417.1401 | 495.4229
187.426 | 697.4409 | 421.4179 | 499.6322
188.426 | 697.7482 | 426.1707 | 504.4214
189.426 | 698.1927 | 430.399 | 508.7435
190.426 | 698.5437 | 434.1883 | 512.1624
191.426 | 698.7613 | 437.5172 | 515.8152
192.426 | 699.3067 | 441.0176 | 520.7246
193.426 | 699.4753 | 444.2776 | 524.4521
194.426 | 699.4853 | 447.8186 | 527.562
195.426 | 699.7702 | 451.2648 | 531.0386
196.426 | 700.05 | 454.7631 | 533.925
197.426 | 699.9158 | 457.7841 | 537.31
198.426 | 700.1919 | 461.0204 | 541.1065
199.426 | 700.1969 | 464.3288 | 544.0506
200.426 | 700.3065 | 467.76 | 546.8878
201.426 | 700.3065 | 471.012 | 549.5774
202.426 | 700.2052 | 474.0393 | 552.698
203.426 | 700.3145 | 477.402 | 555.4122
204.426 | 700.3036 | 480.7781 | 559.0057
205.426 | 700.4132 | 484.3167 | 561.3654
206.426 | 700.4134 | 487.1924 | 564.3376
207.426 | 700.1751 | 490.6442 | 566.465
208.426 | 700.3388 | 493.682 | 568.7642
209.426 | 700.7046 | 497.0187 | 571.3262
210.426 | 700.7839 | 499.8298 | 573.2181
211.426 | 700.9598 | 502.6586 | 575.0968
212.426 | 700.8351 | 505.7274 | 577.5986
213.426 | 700.765 | 508.7768 | 579.1555
214.426 | 700.7183 | 511.5204 | 581.3015
215.426 | 700.7158 | 514.2428 | 582.9678
216.426 | 700.9088 | 516.5383 | 585.2097
217.426 | 700.8035 | 518.933 | 586.5562
218.426 | 700.7844 | 521.5822 | 588.0596
219.426 | 700.823 | 524.3754 | 589.5187
220.426 | 701.0218 | 527.5484 | 591.3357
221.426 | 701.2072 | 530.5898 | 592.446
222.426 | 701.4255 | 533.5196 | 593.73
223.426 | 701.5401 | 536.3851 | 595.0052
224.426 | 701.6359 | 539.0496 | 596.5237
225.426 | 701.6828 | 542.2154 | 597.9277
226.426 | 701.9458 | 545.5316 | 599.4604
227.426 | 702.3754 | 548.4071 | 601.0556
228.426 | 702.3587 | 551.2357 | 602.0265
229.426 | 702.294 | 554.1599 | 603.0756
230.426 | 702.1774 | 557.2711 | 604.1848
231.426 | 702.2385 | 560.154 | 605.0213
232.426 | 702.6153 | 562.7951 | 605.9528
233.426 | 703.0347 | 566.0221 | 607.1671
234.426 | 703.2489 | 568.7562 | 608.3399
235.426 | 703.3558 | 571.1662 | 609.4818
236.426 | 703.3606 | 574.0613 | 610.9797
237.426 | 703.2839 | 576.5382 | 612.8372
238.426 | 703.2464 | 579.4546 | 614.7604
239.426 | 703.3581 | 582.2706 | 616.0013
240.426 | 703.4129 | 584.8395 | 617.1571
241.426 | 703.5128 | 587.1345 | 618.1922
242.426 | 703.3325 | 589.4453 | 619.7439
243.426 | 703.3055 | 591.8538 | 621.1539
244.426 | 703.5778 | 594.6071 | 622.7668
245.426 | 703.7142 | 597.5407 | 624.4633
246.426 | 703.5954 | 599.9509 | 625.7936
247.426 | 703.5817 | 602.0463 | 626.7959
248.426 | 703.4126 | 604.0375 | 627.9134
249.426 | 703.3907 | 605.977 | 629.1809
250.426 | 703.3853 | 607.6856 | 630.5015
251.426 | 703.398 | 609.788 | 631.6857
252.426 | 703.4236 | 611.6508 | 632.6861
253.426 | 703.4154 | 613.4048 | 633.8887
254.426 | 703.8326 | 615.2616 | 635.2672
255.426 | 703.6891 | 617.0904 | 636.3528
256.426 | 703.6402 | 618.9793 | 637.5229
257.426 | 703.5981 | 620.7271 | 638.6814
258.426 | 703.5831 | 622.3869 | 639.9024
259.426 | 703.5923 | 624.2572 | 641.0505
260.426 | 703.4786 | 626.1476 | 642.2477
261.426 | 703.5672 | 627.9723 | 643.2953
262.426 | 703.5469 | 629.8909 | 644.0827
263.426 | 703.4385 | 631.9549 | 644.994
264.426 | 703.485 | 633.6849 | 645.9636
265.426 | 703.4388 | 635.3338 | 647.0005
266.426 | 703.364 | 637.1301 | 648.1864
267.426 | 703.3328 | 638.6862 | 649.2435
268.426 | 703.0802 | 640.4044 | 650.1552
269.426 | 703.0504 | 642.381 | 651.076
270.426 | 702.8046 | 643.997 | 652.0058
271.426 | 702.6065 | 645.6984 | 652.8534
272.426 | 702.722 | 647.2779 | 653.5787
273.426 | 702.8332 | 648.8181 | 654.4684
274.426 | 702.7881 | 650.3939 | 655.4382
275.426 | 702.7491 | 651.9338 | 656.0595
276.426 | 702.7752 | 653.1767 | 656.6719
277.426 | 702.9257 | 654.4164 | 657.4381
278.426 | 702.9343 | 655.6975 | 658.2267
279.426 | 702.9264 | 657.0255 | 658.9357
280.426 | 702.9609 | 658.3185 | 659.3369
281.426 | 702.9815 | 659.5028 | 659.8833
282.426 | 702.9524 | 660.6868 | 660.4474
283.426 | 703.1301 | 661.7902 | 661.0086
284.426 | 703.2394 | 662.7654 | 661.6787
285.426 | 703.2062 | 663.8468 | 661.7782
286.426 | 703.0058 | 665.006 | 662.4428
287.426 | 703.1587 | 666.3471 | 663.1058
288.426 | 703.3152 | 667.6547 | 664.0548
289.426 | 703.4104 | 668.9255 | 664.5499
290.426 | 703.3196 | 670.0804 | 664.6135
291.426 | 703.2162 | 671.1998 | 664.8674
292.426 | 703.1956 | 672.2042 | 665.3478
293.426 | 703.1311 | 673.2867 | 665.7001
294.426 | 703.0858 | 674.3815 | 666.3013
295.426 | 703.0981 | 675.4595 | 666.4272
296.426 | 703.275 | 676.3608 | 666.7289
297.426 | 703.5769 | 677.1947 | 667.316
298.426 | 703.6483 | 678.0704 | 667.6039
299.426 | 703.4809 | 679.0788 | 668.1905
300.426 | 703.7414 | 679.9722 | 668.2049
301.426 | 703.6539 | 680.7783 | 667.9729
302.426 | 703.6502 | 681.5489 | 668.538
303.426 | 703.5611 | 682.335 | 668.9779
304.426 | 703.545 | 683.134 | 669.7492
305.426 | 703.8812 | 683.7972 | 669.7822
306.426 | 703.8866 | 684.629 | 669.6721
307.426 | 703.6651 | 685.4996 | 669.8372
308.426 | 703.5595 | 686.2142 | 669.6946
309.426 | 703.3732 | 686.8721 | 670.2156
310.426 | 703.1077 | 687.3195 | 669.8155
311.426 | 702.9407 | 687.7641 | 669.5968
312.426 | 702.81 | 688.1953 | 670.0368
313.426 | 702.8423 | 688.6563 | 670.3903
314.426 | 702.9627 | 689.243 | 671.145
315.426 | 703.0731 | 689.692 | 670.8951
316.426 | 702.8591 | 690.1207 | 670.9833
317.426 | 702.7721 | 690.6876 | 672.6296
318.426 | 702.795 | 691.0332 | 671.7773
319.426 | 702.9254 | 691.494 | 672.7656
320.426 | 702.9166 | 691.8867 | 672.8787
321.426 | 702.8591 | 692.3046 | 673.3034
322.426 | 702.8678 | 692.6162 | 673.2858
323.426 | 702.8554 | 692.863 | 673.1583
324.426 | 702.961 | 693.1789 | 673.6088
325.426 | 702.7239 | 693.4616 | 672.9353
326.426 | 702.4423 | 693.7146 | 672.8644
327.426 | 702.5582 | 693.8357 | 672.672
328.426 | 702.6032 | 693.9772 | 672.8492
329.426 | 702.606 | 694.2133 | 673.8098
330.4417 | 702.5222 | 694.2275 | 673.1751
331.426 | 702.5301 | 694.4205 | 673.173
332.426 | 702.6101 | 694.6453 | 673.0884
333.426 | 702.5796 | 694.8619 | 673.5035
334.426 | 702.5107 | 695.1089 | 674.2986
335.426 | 702.4789 | 695.133 | 673.931
336.426 | 702.3325 | 695.144 | 674.024
337.426 | 702.1317 | 695.2648 | 674.3601
338.426 | 701.9681 | 695.1975 | 674.4358
339.426 | 701.795 | 695.481 | 676.0388
340.426 | 701.7257 | 695.4818 | 676.0919
341.426 | 701.6479 | 695.6161 | 676.723
342.426 | 701.7724 | 695.7021 | 677.0223
343.426 | 701.6462 | 695.8403 | 677.538
344.426 | 701.5123 | 696.0021 | 678.407
345.426 | 701.556 | 695.8548 | 678.0832
346.426 | 701.5545 | 695.7158 | 678.4564
347.426 | 701.1447 | 695.8173 | 679.6007
348.426 | 701.0595 | 695.7293 | 679.7183
349.426 | 701.1625 | 695.7808 | 680.906
350.426 | 701.3132 | 695.5247 | 681.0077
351.426 | 701.4774 | 695.3393 | 681.1983
352.426 | 701.5457 | 695.1675 | 681.2469
353.426 | 701.6912 | 694.9479 | 681.4602
354.426 | 701.8603 | 695.0174 | 682.1941
355.426 | 702.0127 | 694.6524 | 682.2818
356.426 | 702.0013 | 694.7017 | 683.2072
357.426 | 701.9176 | 694.7818 | 684.5479
358.426 | 702.0101 | 694.6568 | 684.479
359.426 | 701.9978 | 694.9754 | 685.5444
360.426 | 701.9443 | 694.6824 | 684.9621
361.426 | 702.2178 | 694.7581 | 685.8596
362.426 | 702.2654 | 694.7847 | 687.5214
363.426 | 702.3493 | 694.6689 | 688.441
364.426 | 702.4931 | 694.8342 | 689.6314
365.426 | 702.5232 | 694.5636 | 689.6126
366.426 | 702.4835 | 694.4108 | 690.06
367.426 | 702.5017 | 694.3961 | 691.0362
368.426 | 702.6015 | 694.2388 | 691.7255
369.426 | 702.7778 | 694.4613 | 693.6931
370.426 | 702.6745 | 694.2224 | 694.0935
371.426 | 702.6273 | 694.1605 | 694.4331
372.426 | 702.7041 | 694.1808 | 694.604
373.426 | 702.6853 | 694.0575 | 694.9646
374.426 | 702.7923 | 694.0662 | 696.1567
375.426 | 702.4536 | 693.7612 | 697.168
376.426 | 702.1262 | 693.5039 | 697.7812
377.426 | 702.0132 | 693.4717 | 698.6922
378.426 | 701.8619 | 693.2374 | 699.3087
379.426 | 701.8859 | 693.3879 | 701.5551
380.426 | 701.6066 | 692.9832 | 702.2469
381.426 | 701.702 | 692.9576 | 702.9525
382.426 | 701.7601 | 692.8769 | 703.4734
383.426 | 701.6566 | 692.9928 | 706.4184
384.426 | 701.7216 | 693.1959 | 708.7139
385.426 | 701.6744 | 692.9899 | 709.6174
386.426 | 701.6018 | 693.2315 | 710.9202
387.426 | 701.6687 | 692.9023 | 710.9666
388.426 | 701.5977 | 692.7529 | 711.6503
389.426 | 701.6253 | 692.9682 | 712.883
390.426 | 701.7448 | 692.4377 | 712.8396
391.426 | 701.8504 | 692.3512 | 713.3196
392.426 | 701.914 | 692.2094 | 714.2174
393.426 | 702.0349 | 691.955 | 714.2628
394.426 | 702.0482 | 692.1274 | 715.684
395.426 | 702.1412 | 691.73 | 715.9568
396.426 | 702.1722 | 691.4807 | 716.5116
397.426 | 702.2025 | 691.5643 | 716.9032
398.426 | 702.2969 | 691.4034 | 717.6966
399.426 | 702.2056 | 691.6518 | 719.1064
400.426 | 702.1453 | 691.1482 | 718.8325
401.426 | 702.3874 | 691.2694 | 720.2679
402.426 | 702.3846 | 691.2614 | 720.3754
403.426 | 702.4849 | 691.2459 | 720.5068
404.426 | 702.5729 | 691.321 | 720.5659
405.426 | 702.6324 | 690.7787 | 720.033
406.426 | 702.5021 | 690.6823 | 720.0835
407.426 | 702.5683 | 690.6453 | 720.4249
408.426 | 702.6382 | 690.4221 | 720.7245
409.426 | 702.6254 | 690.8024 | 721.7396
410.426 | 702.727 | 690.2182 | 721.9304
411.426 | 702.7034 | 690.2628 | 722.5566
412.426 | 702.2416 | 690.1595 | 722.8182
413.426 | 702.1828 | 690.0815 | 723.5227
414.426 | 702.2049 | 690.2441 | 723.9802
415.426 | 702.1607 | 689.7493 | 723.3813
416.426 | 702.1881 | 689.577 | 724.0186
417.426 | 702.0286 | 689.5609 | 724.7057
418.426 | 701.8607 | 689.2077 | 724.3345
419.426 | 701.8517 | 689.7346 | 725.3575
420.426 | 701.7944 | 689.0442 | 724.9477
421.426 | 701.8732 | 688.9336 | 724.9926
422.426 | 701.8474 | 688.8633 | 724.8159
423.426 | 701.7328 | 688.6539 | 724.7334
424.426 | 701.8146 | 689.0603 | 725.5807
425.426 | 701.6827 | 688.3632 | 725.2245
426.426 | 701.858 | 688.4572 | 725.3991
427.426 | 701.9092 | 688.5104 | 725.6809
428.426 | 702.0218 | 688.4662 | 725.6439
429.426 | 701.9572 | 689.0675 | 726.444
430.426 | 701.9959 | 688.6611 | 725.8994
431.426 | 702.2136 | 688.1754 | 725.353
432.426 | 702.2929 | 688.3368 | 725.6523
433.426 | 702.5629 | 688.2647 | 725.7042
434.426 | 702.8234 | 689.0218 | 726.4274
435.426 | 703.0915 | 688.4762 | 725.9547
436.426 | 703.1649 | 688.7373 | 726.225
437.426 | 703.1202 | 689.0374 | 726.6875
438.426 | 703.0198 | 689.1133 | 726.6439
439.426 | 702.8561 | 689.7453 | 727.7398
440.426 | 702.8357 | 689.2378 | 726.8628
441.426 | 702.7112 | 689.5166 | 726.8548
442.426 | 702.7968 | 689.8885 | 727.2343
443.426 | 702.8808 | 689.4146 | 726.469
444.426 | 702.6825 | 690.1696 | 726.6966
445.426 | 702.5311 | 689.6393 | 726.2169
446.426 | 702.6774 | 689.757 | 726.2038
447.426 | 702.7209 | 691.095 | 727.6704
448.426 | 702.5541 | 691.1967 | 728.1095
449.426 | 702.6209 | 692.0699 | 729.3185
450.426 | 702.5227 | 691.6517 | 729.0034
451.426 | 702.4709 | 691.8432 | 729.2378
452.426 | 702.3763 | 692.1038 | 729.2672
453.426 | 702.6317 | 692.273 | 729.2601
454.426 | 702.8535 | 693.1823 | 730.2061
455.426 | 702.9141 | 692.8397 | 729.6826
456.426 | 702.796 | 693.2035 | 729.9984
457.426 | 702.5704 | 693.6952 | 730.4065
458.426 | 702.4226 | 694.0975 | 730.8995
459.426 | 702.3841 | 695.1273 | 732.296
460.426 | 702.1254 | 694.883 | 732.1972
461.426 | 702.0896 | 695.1424 | 732.158
462.426 | 702.0722 | 695.7696 | 732.8592
463.426 | 702.1381 | 696.0207 | 732.8438
464.426 | 702.343 | 697.0165 | 733.1783
465.426 | 702.4428 | 696.4427 | 731.9003
466.426 | 702.4128 | 696.7826 | 732.0942
467.426 | 702.1003 | 697.129 | 732.3225
468.426 | 702.003 | 697.42 | 732.7949
469.426 | 701.8886 | 698.1933 | 733.3141
470.426 | 701.8999 | 698.0945 | 733.475
471.426 | 701.9776 | 698.1898 | 733.2094
472.426 | 701.7994 | 698.5992 | 733.8502
473.426 | 701.5845 | 698.5741 | 733.8267
474.426 | 701.8522 | 699.6339 | 734.9679
475.426 | 702.0112 | 699.2703 | 734.3687
476.426 | 701.9841 | 699.5219 | 734.5272
477.426 | 701.9168 | 700.5812 | 735.618
478.426 | 701.8884 | 699.9645 | 734.5268
479.426 | 701.9545 | 700.7587 | 735.3224
480.426 | 701.9139 | 700.5966 | 735.1814
481.426 | 701.9208 | 700.9007 | 735.4544
482.426 | 702.0876 | 701.2892 | 735.6837
483.426 | 702.2729 | 701.3623 | 735.4137
484.426 | 702.4309 | 702.0464 | 735.6376
485.426 | 702.7761 | 701.6928 | 735.561
486.426 | 702.964 | 701.8708 | 736.0348
487.426 | 702.9702 | 702.3981 | 736.6409
488.426 | 702.8314 | 702.2405 | 736.4318
489.426 | 702.6363 | 703.1926 | 737.3323
490.426 | 702.6566 | 702.9456 | 736.9881
491.426 | 702.5803 | 703.23 | 736.9323
492.426 | 702.348 | 703.5775 | 736.9861
493.426 | 701.9632 | 703.8155 | 737.1123
494.426 | 702.0837 | 704.6459 | 737.633
495.426 | 702.0219 | 704.3832 | 737.2186
496.426 | 702.13 | 704.5779 | 737.4312
497.426 | 702.186 | 704.8877 | 737.705
498.426 | 702.2193 | 706.1167 | 739.4125
499.426 | 702.155 | 706.1734 | 739.0163
500.426 | 702.2083 | 705.855 | 738.4013
501.426 | 702.0673 | 706.2134 | 738.6352
502.426 | 701.8886 | 706.5036 | 739.0332
503.426 | 701.7475 | 706.6364 | 738.9609
504.426 | 701.4547 | 707.5042 | 739.6301
505.426 | 701.2312 | 707.224 | 739.295
506.426 | 701.1257 | 707.4097 | 739.3731
507.426 | 701.1373 | 708.073 | 739.6509
508.426 | 700.9415 | 708.2377 | 739.55
509.426 | 701.0862 | 709.1447 | 739.7638
510.426 | 701.2707 | 708.7539 | 739.4834
511.426 | 701.2855 | 709.143 | 740.027
512.426 | 701.3368 | 709.5316 | 740.3631
513.426 | 701.0914 | 709.7783 | 740.5634
514.426 | 700.9745 | 710.8187 | 741.3955
515.426 | 700.729 | 710.6256 | 740.9307
516.426 | 700.6942 | 710.8346 | 740.8243
517.426 | 700.9026 | 711.168 | 740.6619
518.426 | 700.9014 | 711.1802 | 740.5042
519.426 | 700.8923 | 712.3676 | 742.0064
520.426 | 700.9851 | 712.0992 | 741.1451
521.426 | 701.1213 | 712.222 | 740.4266
522.426 | 701.52 | 712.6196 | 740.4848
523.426 | 701.8449 | 715.4163 | 743.4
524.426 | 702.137 | 715.6468 | 743.5004
525.426 | 702.4961 | 715.1006 | 742.6742
526.426 | 702.658 | 715.2651 | 742.7243
527.426 | 702.8497 | 715.4373 | 742.9621
528.426 | 702.9762 | 715.4887 | 742.624
529.426 | 702.9073 | 716.1799 | 743.0844
530.426 | 702.7885 | 715.8986 | 742.6152
531.426 | 702.5228 | 716.102 | 742.2504
532.426 | 702.2531 | 716.6436 | 742.4104
533.426 | 702.356 | 716.9704 | 742.5277
534.426 | 702.6185 | 717.7735 | 742.9429
535.426 | 702.7143 | 717.5767 | 742.4634
536.426 | 702.5083 | 718.0208 | 743.0223
537.426 | 702.3574 | 718.354 | 742.9636
538.426 | 702.1339 | 718.6516 | 742.7763
539.426 | 701.9604 | 719.5987 | 742.9476
540.426 | 701.858 | 719.4558 | 742.4942
541.426 | 701.7437 | 719.5412 | 742.3057
542.426 | 701.7727 | 719.8536 | 742.5199
543.426 | 701.6722 | 719.9672 | 742.6931
544.426 | 701.5018 | 720.9978 | 743.5971
545.426 | 701.3614 | 720.8296 | 743.4063
546.426 | 701.2273 | 721.1326 | 743.5382
547.426 | 701.0269 | 721.5579 | 743.7169
548.426 | 700.8983 | 721.9176 | 744.1776
549.426 | 700.8853 | 722.5997 | 744.9321
550.426 | 700.7557 | 722.3816 | 744.5633
551.426 | 700.686 | 722.715 | 745.028
552.426 | 700.6823 | 723.1839 | 745.2817
553.426 | 700.7535 | 723.5153 | 745.6202
554.426 | 700.7887 | 724.2 | 745.8431
555.426 | 701.09 | 724.1377 | 745.0733
556.426 | 701.1962 | 724.6325 | 745.0268
557.426 | 701.2806 | 725.0341 | 744.9146
558.426 | 701.7974 | 725.4666 | 745.466
559.426 | 701.9855 | 726.394 | 745.9537
560.426 | 702.2347 | 726.3914 | 745.5041
561.426 | 702.3462 | 726.7761 | 745.6453
562.426 | 702.482 | 727.2914 | 745.862
563.426 | 702.5405 | 727.6589 | 745.4856
564.426 | 702.4122 | 728.476 | 745.4285
565.426 | 702.4984 | 728.5205 | 744.6989
566.426 | 702.404 | 729.0676 | 744.7423
567.426 | 702.3602 | 729.6305 | 744.9476
568.426 | 702.229 | 730.115 | 745.1035
569.426 | 702.2141 | 731.2165 | 745.8809
570.426 | 702.2696 | 730.961 | 745.1013
571.426 | 702.3871 | 731.3502 | 744.8919
572.426 | 702.5809 | 731.7366 | 744.4793
573.426 | 702.5001 | 732.0394 | 744.3113
574.426 | 702.2907 | 733.112 | 745.0983
575.426 | 702.1519 | 733.1264 | 744.8624
576.426 | 701.9838 | 733.6203 | 745.1353
577.426 | 702.0414 | 734.2543 | 745.8677
578.426 | 702.1388 | 734.706 | 746.1385
579.426 | 701.9872 | 735.5889 | 746.7187
580.426 | 702.1677 | 735.7066 | 745.9164
581.426 | 702.1964 | 736.0357 | 745.5266
582.426 | 702.2283 | 736.572 | 745.6079
583.426 | 702.3372 | 736.7186 | 745.0982
584.426 | 702.4583 | 737.5047 | 745.7891
585.426 | 702.4481 | 737.7819 | 745.8536
586.426 | 702.3509 | 738.1887 | 746.1002
587.426 | 702.4976 | 738.7769 | 746.3935
588.426 | 702.5784 | 739.6269 | 746.2448
589.426 | 702.7637 | 740.093 | 746.0262
590.426 | 702.9339 | 740.0838 | 745.3011
591.426 | 702.9949 | 740.538 | 745.1335
592.426 | 702.8654 | 740.8549 | 744.7687
593.426 | 702.7208 | 741.1159 | 744.2697
594.426 | 702.8194 | 741.8132 | 744.5141
595.426 | 702.8838 | 741.8221 | 743.8502
596.426 | 702.8671 | 742.0718 | 743.4813
597.426 | 702.8673 | 742.4647 | 743.4298
598.426 | 702.7228 | 742.785 | 743.5847
599.426 | 702.5658 | 743.4849 | 744.2062
600.426 | 702.6861 | 743.2791 | 743.4563
601.426 | 702.5405 | 743.6478 | 743.6796
602.426 | 702.4834 | 744.1848 | 744.1884
603.426 | 702.3672 | 744.4296 | 743.709
604.426 | 702.3513 | 745.046 | 743.859
605.426 | 702.2623 | 745.0214 | 742.7731
606.426 | 702.1689 | 745.3396 | 742.5696
607.426 | 701.9891 | 745.6255 | 742.43
608.426 | 701.8389 | 745.7514 | 742.0784
609.426 | 701.7539 | 746.2063 | 742.4064
610.426 | 701.5673 | 746.1753 | 742.0407
611.426 | 701.287 | 746.3255 | 741.7005
612.426 | 701.1372 | 746.7683 | 741.8156
613.426 | 701.1533 | 746.8305 | 741.342
614.426 | 701.1348 | 747.2709 | 741.5293
615.426 | 701.2429 | 747.176 | 740.5799
616.426 | 701.2208 | 747.2484 | 739.7499
617.426 | 701.1944 | 747.3995 | 739.0943
618.426 | 701.2214 | 747.423 | 738.4535
619.426 | 701.1965 | 747.7325 | 738.0498
620.426 | 701.1591 | 747.6258 | 737.1883
621.426 | 701.2243 | 747.6948 | 736.6052
622.426 | 701.1855 | 747.8392 | 736.0689
623.426 | 700.9663 | 747.9215 | 735.2077
624.426 | 701.0071 | 748.205 | 734.7997
625.426 | 700.6999 | 748.0812 | 733.7635
626.426 | 700.7325 | 748.0042 | 732.9501
627.426 | 700.6464 | 748.3702 | 733.0479
628.426 | 700.728 | 748.3762 | 732.098
629.426 | 700.8024 | 748.7118 | 731.9103
630.426 | 700.8277 | 748.4643 | 730.6923
631.426 | 700.8718 | 748.8823 | 730.5571
632.426 | 700.9191 | 748.7044 | 729.2636
633.426 | 700.747 | 748.7834 | 728.6291
634.426 | 700.8675 | 749.0513 | 728.2043
635.426 | 700.9279 | 748.8054 | 726.8805
636.426 | 701.021 | 748.8237 | 726.0321
637.426 | 701.0822 | 748.9697 | 725.3587
638.426 | 700.9386 | 749.0617 | 724.4719
639.426 | 700.7753 | 749.523 | 724.3264
640.426 | 700.6012 | 749.3783 | 722.9719
641.426 | 700.5847 | 749.4965 | 722.1041
642.426 | 700.734 | 749.5847 | 721.2056
643.426 | 700.7411 | 749.7864 | 720.7583
644.426 | 700.7602 | 750.1936 | 720.7195
645.426 | 700.9128 | 750.0512 | 719.5716
646.426 | 700.793 | 750.0816 | 718.7095
647.426 | 700.6837 | 750.1826 | 717.8751
648.426 | 700.7288 | 750.4891 | 717.4153
649.426 | 700.7044 | 750.5342 | 716.6766
650.426 | 700.7722 | 750.4135 | 715.4496
651.426 | 700.8409 | 750.373 | 714.4738
652.426 | 700.8055 | 750.5601 | 713.9209
653.426 | 700.6884 | 750.5971 | 713.0854
654.426 | 700.6435 | 750.7965 | 712.5455
655.426 | 700.7149 | 750.5913 | 711.2222
656.426 | 700.7523 | 750.6144 | 710.2903
657.426 | 700.9475 | 750.7561 | 709.5299
658.426 | 701.2576 | 750.8456 | 708.9521
659.426 | 701.3673 | 751.1657 | 708.6897
660.426 | 701.3332 | 751.0354 | 707.5824
661.426 | 701.2348 | 751.1939 | 707.0496
662.426 | 701.4409 | 751.1288 | 706.1322
663.426 | 701.5751 | 751.1663 | 705.3834
664.426 | 701.6629 | 751.6763 | 705.5522
665.426 | 701.4695 | 751.4348 | 704.117
666.426 | 701.2483 | 751.5293 | 703.4771
667.426 | 701.4248 | 751.6378 | 702.8118
668.426 | 701.4196 | 751.968 | 702.629
669.426 | 701.3452 | 751.9678 | 701.8146
670.426 | 701.4104 | 751.8575 | 700.8787
671.426 | 701.5684 | 751.9514 | 700.1469
672.426 | 701.7787 | 752.0424 | 699.4918
673.426 | 701.8865 | 752.0992 | 698.815
674.426 | 701.8603 | 752.4977 | 698.7571
675.426 | 701.8962 | 752.4148 | 697.7798
676.426 | 701.9453 | 752.4601 | 697.0875
677.426 | 702.0885 | 752.5627 | 696.4929
678.426 | 702.2722 | 752.738 | 696.1343
679.426 | 702.3946 | 752.9482 | 695.9142
680.426 | 702.4136 | 752.9427 | 695.4025
681.426 | 702.4092 | 753.0585 | 695.0867
682.426 | 702.2765 | 753.2806 | 694.8238
683.426 | 702.1988 | 753.3377 | 694.4784
684.426 | 702.1122 | 753.6644 | 694.5186
685.426 | 702.1159 | 753.5196 | 693.703
686.426 | 701.9702 | 753.5484 | 693.2007
687.426 | 701.7559 | 753.8441 | 693.2622
688.426 | 701.796 | 753.6815 | 692.4547
689.426 | 701.7362 | 753.9756 | 692.5332
690.426 | 701.6653 | 754.0263 | 692.0204
691.426 | 701.6429 | 754.2347 | 691.6864
692.426 | 701.6749 | 754.4929 | 691.7653
693.426 | 701.4746 | 754.4479 | 690.9221
694.426 | 701.5613 | 754.794 | 690.975
695.426 | 701.6924 | 754.7116 | 690.1687
696.426 | 701.6983 | 754.7651 | 689.5078
697.426 | 701.7682 | 754.9916 | 689.4583
698.426 | 701.97 | 754.9539 | 688.9325
699.426 | 702.1418 | 755.1626 | 688.8797
700.426 | 702.3224 | 755.1148 | 688.3967
701.426 | 702.2763 | 755.2532 | 688.0445
702.426 | 702.3199 | 755.3987 | 687.7193
703.426 | 702.2318 | 755.5617 | 687.3818
704.426 | 702.0666 | 755.9646 | 687.7018
705.426 | 701.9235 | 755.8891 | 686.9585
706.426 | 701.9631 | 756.0645 | 686.8018
707.426 | 701.9273 | 756.1353 | 686.4675
708.426 | 701.8025 | 756.3894 | 686.5874
709.426 | 701.7517 | 756.5565 | 686.557
710.426 | 702.0476 | 756.3473 | 685.7109
711.426 | 702.1744 | 756.378 | 685.42
712.426 | 702.2199 | 756.3272 | 684.9478
713.426 | 702.4079 | 756.1701 | 684.4226
714.426 | 702.7366 | 756.4209 | 684.6498
715.426 | 702.7917 | 756.2707 | 684.0188
716.426 | 702.7264 | 756.2475 | 683.6676
717.426 | 702.666 | 756.3469 | 683.5753
718.426 | 702.7571 | 756.3193 | 683.2394
719.426 | 702.5382 | 756.5262 | 683.2169
720.426 | 702.4606 | 756.38 | 682.558
721.426 | 702.5164 | 756.4742 | 682.4166
722.426 | 702.4705 | 756.563 | 682.113
723.426 | 702.4988 | 756.557 | 681.6827
724.426 | 702.2706 | 756.827 | 681.7645
725.426 | 702.182 | 756.8263 | 681.346
726.426 | 702.2397 | 756.7713 | 680.8983
727.426 | 702.1502 | 756.8477 | 680.736
728.426 | 702.0889 | 756.8568 | 680.4202
729.426 | 701.9815 | 757.14 | 680.7408
730.426 | 701.9769 | 756.9688 | 680.0286
731.426 | 701.9754 | 756.9794 | 679.7528
732.426 | 701.8616 | 757.0411 | 679.5161
733.426 | 701.9591 | 757.0427 | 679.1723
734.426 | 702.182 | 757.3899 | 679.4218
735.426 | 702.2347 | 757.2656 | 678.7639
736.426 | 702.1397 | 757.3199 | 678.5029
737.426 | 702.1912 | 757.4124 | 678.224
738.426 | 702.3916 | 757.405 | 677.8965
739.426 | 702.4393 | 757.5912 | 678.0457
740.426 | 702.4468 | 757.4401 | 677.3026
741.426 | 702.6521 | 757.4272 | 677.0148
742.426 | 702.6586 | 757.4943 | 676.9675
743.426 | 702.4748 | 757.4721 | 676.6601
744.426 | 702.4245 | 757.6858 | 676.9019
745.426 | 702.5471 | 757.3743 | 676.0798
746.426 | 702.5924 | 757.4944 | 676.0744
747.426 | 702.5467 | 757.5818 | 676.0677
748.426 | 702.3194 | 757.5813 | 675.8761
749.426 | 702.1336 | 757.8196 | 676.236
750.426 | 701.7863 | 757.6022 | 675.4849
751.426 | 701.5669 | 757.6087 | 675.3141
752.426 | 701.5564 | 757.6852 | 675.1724
753.426 | 701.5066 | 757.7546 | 675.0026
754.426 | 701.5675 | 758.0315 | 675.3642
755.426 | 701.7317 | 757.8175 | 674.701
756.426 | 701.7775 | 757.8221 | 674.5066
757.426 | 701.7079 | 757.9075 | 674.4714
758.426 | 701.6051 | 757.8491 | 674.1755
759.426 | 701.5445 | 758.0905 | 674.5103
760.426 | 701.4925 | 757.9435 | 673.8964
761.426 | 701.653 | 758.0043 | 673.8166
762.426 | 701.6268 | 758.0831 | 673.8496
763.426 | 701.6419 | 758.109 | 673.755
764.426 | 701.5257 | 758.3488 | 674.199
765.426 | 701.7836 | 758.1635 | 673.6556
766.426 | 701.9686 | 758.2071 | 673.441
767.426 | 702.0378 | 758.3552 | 673.4842
768.426 | 702.1504 | 758.3455 | 673.306
769.426 | 702.2661 | 758.6511 | 673.7179
770.426 | 702.1875 | 758.5322 | 673.1766
771.426 | 702.1494 | 758.6163 | 673.0671
772.426 | 702.0242 | 758.7646 | 673.2312
773.426 | 702.0284 | 758.6099 | 672.7371
774.426 | 702.0258 | 758.9344 | 672.9365
775.426 | 702.0341 | 758.8644 | 672.3285
776.426 | 702.1261 | 758.9782 | 672.3296
777.426 | 701.9649 | 759.0972 | 672.3325
778.426 | 702.0641 | 759.0387 | 672.137
779.426 | 701.9899 | 759.2268 | 672.5362
780.426 | 702.1157 | 759.0408 | 672.026
781.426 | 702.1959 | 758.9906 | 671.8845
782.426 | 701.8804 | 759.1138 | 671.9795
783.426 | 701.7322 | 759.2893 | 672.2063
784.426 | 701.7655 | 759.3209 | 672.1608
785.426 | 701.7149 | 759.1644 | 671.6819
786.426 | 701.6311 | 759.1844 | 671.6841
787.426 | 701.6043 | 759.2706 | 671.8735
788.426 | 701.5564 | 759.3338 | 671.9812
789.426 | 701.3901 | 759.5175 | 672.3279
790.426 | 701.1214 | 759.4254 | 672.114
791.426 | 701.0985 | 759.4855 | 672.2511
792.426 | 701.3086 | 759.77 | 672.7261
793.426 | 701.376 | 759.6349 | 672.1738
794.426 | 701.3899 | 759.9155 | 672.5533
795.426 | 701.4037 | 759.8418 | 672.2049
796.426 | 701.1547 | 759.9577 | 672.3048
797.426 | 701.1991 | 760.0332 | 672.534
798.426 | 701.1113 | 759.9903 | 672.3751
799.426 | 701.1448 | 760.2236 | 672.5531
800.426 | 701.2523 | 760.0417 | 672.0037
801.426 | 701.1861 | 760.0324 | 671.9436
802.426 | 701.3193 | 760.1538 | 672.2285
803.426 | 701.2387 | 760.1392 | 672.0426
804.426 | 701.3426 | 760.3225 | 672.3965
805.426 | 701.3 | 760.4265 | 672.5689
806.426 | 701.2736 | 760.3895 | 672.3064
807.426 | 701.1914 | 760.5567 | 672.5488
808.426 | 701.2023 | 760.5827 | 672.4435
809.426 | 701.1791 | 760.7929 | 673.0215
810.426 | 701.2701 | 760.7098 | 672.7636
811.426 | 701.3991 | 760.7964 | 673.2126
812.426 | 701.1997 | 760.8749 | 673.5895
813.426 | 701.1848 | 760.9544 | 673.8333
814.426 | 701.187 | 761.2457 | 674.5782
815.426 | 701.2494 | 761.2125 | 674.6055
816.426 | 701.221 | 761.2282 | 674.5939
817.426 | 701.1951 | 761.22 | 674.6376
818.426 | 701.1648 | 761.246 | 674.7565
819.426 | 701.0913 | 761.447 | 675.1993
820.426 | 700.9991 | 761.3515 | 675.0152
821.426 | 701.1138 | 761.3701 | 675.1724
822.426 | 701.2996 | 761.714 | 675.643
823.426 | 701.3737 | 761.6763 | 675.3266
824.426 | 701.137 | 761.8606 | 675.5079
825.426 | 701.1166 | 761.8671 | 675.2489
826.426 | 700.9171 | 762.0362 | 675.4746
827.426 | 701.1269 | 762.0732 | 675.2802
828.426 | 701.2232 | 762.1506 | 675.2663
829.426 | 701.4356 | 762.3105 | 675.6124
830.426 | 701.4338 | 762.2792 | 675.5835
831.426 | 701.3343 | 762.4696 | 676.1011
832.426 | 701.1557 | 762.4353 | 675.9738
833.426 | 701.2009 | 762.4202 | 675.9361
834.426 | 701.4428 | 762.5498 | 676.168
835.426 | 701.6173 | 762.5761 | 676.3006
836.426 | 701.8279 | 762.6956 | 676.4876
837.426 | 701.8573 | 762.8289 | 676.6361
838.426 | 701.8096 | 763.0694 | 677.0332
839.426 | 701.7591 | 763.2791 | 677.209
840.426 | 701.8425 | 763.2682 | 677.0116
841.426 | 701.8234 | 763.3238 | 677.0713
842.426 | 701.839 | 763.4935 | 677.2512
843.426 | 701.7753 | 763.5152 | 677.1986
844.426 | 702.0784 | 763.5953 | 676.8968
845.426 | 701.9468 | 763.4868 | 676.4938
846.426 | 701.7166 | 763.4426 | 676.4472
847.426 | 701.7574 | 763.6787 | 676.8404
848.426 | 701.647 | 763.5661 | 676.4806
849.426 | 701.5913 | 763.6989 | 676.7639
850.426 | 701.6939 | 763.5322 | 676.5965
851.426 | 701.7212 | 763.5479 | 676.9194
852.426 | 701.6591 | 763.6472 | 677.3929
853.426 | 701.428 | 763.7299 | 677.373
854.426 | 701.241 | 763.8721 | 677.6345
855.426 | 701.2152 | 763.8355 | 677.4373
856.426 | 700.9884 | 763.9632 | 677.6633
857.426 | 700.7457 | 764.2478 | 678.0804
858.426 | 700.7002 | 764.2981 | 677.7673
859.426 | 700.6554 | 764.3418 | 677.4492
860.426 | 700.6486 | 764.3282 | 676.9739
861.426 | 700.9036 | 764.3908 | 676.8104
862.426 | 700.9017 | 764.5195 | 677.0355
863.426 | 700.9955 | 764.5247 | 676.9837
864.426 | 700.9745 | 764.4286 | 676.7984
865.426 | 701.0766 | 764.3959 | 676.5035
866.426 | 701.0647 | 764.3831 | 676.3038
867.426 | 700.9331 | 764.4869 | 676.3766
868.426 | 701.1888 | 764.5306 | 676.2955
869.426 | 701.2797 | 764.5792 | 676.4078
870.426 | 701.1864 | 764.498 | 676.1723
871.426 | 700.8897 | 764.5693 | 676.3619
872.426 | 700.8066 | 764.7468 | 676.6754
873.426 | 700.7653 | 764.7643 | 676.761
874.426 | 700.6289 | 765.0139 | 677.4434
875.426 | 700.5317 | 765.035 | 677.4848
876.426 | 700.7267 | 765.0965 | 677.6928
877.426 | 700.5585 | 765.1162 | 677.7373
878.426 | 700.7416 | 765.1663 | 677.6958
879.426 | 700.7362 | 765.3216 | 677.7913
880.426 | 700.5135 | 765.1957 | 677.5367
881.426 | 700.6722 | 765.1864 | 677.5918
882.426 | 701.0142 | 765.1387 | 677.5562
883.426 | 701.2037 | 765.2004 | 677.6372
884.426 | 701.2321 | 765.322 | 677.9538
885.426 | 701.282 | 765.2883 | 678.1652
886.426 | 701.2994 | 765.3721 | 678.5549
887.426 | 701.2885 | 765.2206 | 678.7226
888.426 | 701.3578 | 765.3295 | 679.3176
889.426 | 701.517 | 765.4228 | 679.5617
890.426 | 701.727 | 765.3872 | 679.6399
891.426 | 701.8601 | 765.3802 | 679.7616
892.426 | 701.7247 | 765.5014 | 680.1904
893.426 | 701.8299 | 765.5659 | 680.4465
894.426 | 701.9037 | 765.5857 | 680.6239
895.426 | 701.9784 | 765.489 | 680.5858
896.426 | 702.1345 | 765.4212 | 680.5609
897.426 | 702.1909 | 765.4253 | 680.7476
898.426 | 702.0804 | 765.4074 | 680.7171
899.426 | 701.9004 | 765.3646 | 680.6405
900.426 | 702.0627 | 765.2934 | 680.6004
901.426 | 701.9883 | 765.3226 | 680.6017
902.426 | 701.8434 | 765.3303 | 680.7279
903.426 | 701.7331 | 765.4436 | 680.9357
904.426 | 701.6981 | 765.4115 | 680.9015
905.426 | 701.7296 | 765.3743 | 680.9612
906.426 | 701.7489 | 765.3499 | 681.0016
907.426 | 701.6718 | 765.4851 | 681.5257
908.426 | 701.6545 | 765.5456 | 681.7963
909.426 | 701.6786 | 765.5312 | 681.872
910.426 | 701.6342 | 765.461 | 681.7147
911.426 | 701.639 | 765.4276 | 681.774
912.426 | 701.6221 | 765.373 | 681.8654
913.426 | 701.5658 | 765.4219 | 681.8699
914.426 | 701.5937 | 765.4879 | 681.8026
915.426 | 701.5629 | 765.4517 | 681.61
916.426 | 701.6629 | 765.3774 | 681.3361
917.426 | 701.5077 | 765.3288 | 681.2382
918.426 | 701.6502 | 765.2951 | 681.1048
919.426 | 701.7207 | 765.3563 | 681.0236
920.426 | 701.7073 | 765.4798 | 680.7902
921.426 | 701.7819 | 765.5221 | 680.6558
922.426 | 701.7638 | 765.5716 | 680.5975
923.426 | 701.7849 | 765.5682 | 680.5848
924.426 | 701.7436 | 765.5938 | 680.6738
925.426 | 701.6334 | 765.4552 | 680.5589
926.426 | 701.6917 | 765.3702 | 680.5731
927.426 | 702.0514 | 765.3928 | 680.6496
928.426 | 702.0851 | 765.2859 | 680.7696
929.426 | 702.0795 | 765.2886 | 680.9483
930.426 | 702.0299 | 765.3223 | 681.002
931.426 | 701.9898 | 765.3122 | 681.1684
932.426 | 702.0454 | 765.4364 | 681.2736
933.426 | 701.8013 | 765.5636 | 681.2495
934.426 | 701.5667 | 765.6199 | 681.2069
935.426 | 701.5137 | 765.6392 | 681.1471
936.426 | 701.4876 | 765.6676 | 681.0999
937.426 | 701.433 | 765.7178 | 681.1435
938.426 | 701.5502 | 765.6429 | 681.229
939.426 | 701.5997 | 765.6577 | 681.4634
940.426 | 701.2813 | 765.6388 | 681.5932
941.426 | 701.0865 | 765.6751 | 681.7635
942.426 | 701.0687 | 765.6441 | 681.9643
943.426 | 701.1717 | 765.6271 | 682.0586
944.426 | 701.4545 | 765.5794 | 682.2053
945.426 | 701.5968 | 765.5572 | 682.2493
946.426 | 701.5988 | 765.6048 | 682.2961
947.426 | 701.5651 | 765.5601 | 682.3609
948.426 | 701.7718 | 765.5488 | 682.3966
949.426 | 701.75 | 765.6204 | 682.4629
950.426 | 701.6679 | 765.6449 | 682.5212
951.426 | 701.7439 | 765.6517 | 682.6527
952.426 | 701.7148 | 765.5214 | 682.6413
953.426 | 701.5818 | 765.3173 | 682.7287
954.426 | 701.4786 | 765.2019 | 682.8016
955.426 | 701.4008 | 765.1433 | 682.7628
956.426 | 701.1626 | 765.0595 | 682.7463
957.426 | 700.9135 | 764.9694 | 682.7603
958.426 | 700.9251 | 764.9142 | 682.6858
959.426 | 700.9691 | 764.8384 | 682.57
960.426 | 700.8089 | 764.7377 | 682.4944
961.426 | 700.7627 | 764.6467 | 682.3931
962.426 | 700.8603 | 764.6006 | 682.323
963.426 | 700.9064 | 764.3919 | 682.2251
964.426 | 701.0452 | 764.2941 | 682.1093
965.426 | 701.1377 | 764.1611 | 681.9624
966.426 | 701.0886 | 764.0642 | 681.8559
967.426 | 700.9972 | 763.9599 | 681.7472
968.426 | 700.9308 | 763.8954 | 681.6366
969.426 | 700.9967 | 763.8049 | 681.5665
970.426 | 701.0898 | 763.6946 | 681.5012
971.426 | 700.9602 | 763.7365 | 681.4314
972.426 | 701.1074 | 763.725 | 681.3339
973.426 | 701.169 | 763.6426 | 681.1821
974.426 | 701.4157 | 763.4746 | 681.0141
975.426 | 701.542 | 763.4045 | 680.8665
976.426 | 701.428 | 763.2171 | 680.7364
977.426 | 701.4623 | 763.0796 | 680.6003
978.426 | 701.466 | 762.9495 | 680.4452
979.426 | 701.5657 | 762.7979 | 680.2789
980.426 | 701.5048 | 762.6873 | 680.1276
981.426 | 701.2222 | 762.5942 | 679.9951
982.426 | 701.2979 | 762.407 | 679.8963
983.426 | 701.5624 | 762.2339 | 679.7735
984.426 | 701.8168 | 762.1127 | 679.6666
985.426 | 702.0542 | 762.0508 | 679.5706
986.426 | 702.1809 | 761.9818 | 679.4851
987.426 | 702.2229 | 761.8439 | 679.4209
988.426 | 702.4559 | 761.7438 | 679.386
989.426 | 702.5145 | 761.5568 | 679.3514
990.426 | 702.4876 | 761.3882 | 679.2432
991.426 | 702.337 | 761.2261 | 679.1387
992.426 | 702.3186 | 761.1115 | 679.0539
993.426 | 702.2193 | 761.0342 | 678.9836
994.426 | 702.2177 | 760.8233 | 678.9136
995.426 | 702.2316 | 760.636 | 678.8923
996.426 | 702.2294 | 760.5764 | 678.8627
997.426 | 702.4037 | 760.5557 | 678.7798
998.426 | 702.4803 | 760.4775 | 678.649
999.426 | 702.4305 | 760.359 | 678.5207
1000.426 | 702.5035 | 760.1032 | 678.4221
1001.426 | 702.5618 | 759.8552 | 678.3494
1002.426 | 702.3155 | 759.6649 | 678.2921
1003.426 | 702.2735 | 759.5198 | 678.185
1004.426 | 702.3985 | 759.3302 | 678.0448
1005.426 | 702.3903 | 759.1969 | 677.8905
1006.426 | 702.3743 | 759.0622 | 677.6864
1007.426 | 702.4387 | 758.7694 | 677.5012
1008.426 | 702.5264 | 758.4757 | 677.3752
1009.426 | 702.3945 | 758.1842 | 677.306
1010.426 | 702.225 | 757.8407 | 677.2643
1011.426 | 702.2709 | 757.5918 | 677.2271
1012.426 | 702.1914 | 757.3923 | 677.1873
1013.426 | 702.0464 | 757.1858 | 677.1294
1014.426 | 702.037 | 757.0501 | 677.0615
1015.426 | 702.0277 | 756.8618 | 676.9517
1016.426 | 702.1221 | 756.5984 | 676.7849
1017.426 | 702.1588 | 756.2465 | 676.703
1018.426 | 701.997 | 755.9084 | 676.6219
1019.426 | 701.9713 | 755.5322 | 676.5908
1020.426 | 701.7251 | 755.1685 | 676.5785
1021.426 | 701.7465 | 754.8706 | 676.5723
1022.426 | 701.4324 | 754.6065 | 676.5346
1023.426 | 701.0881 | 754.2517 | 676.4349
1024.426 | 700.984 | 753.9747 | 676.306
1025.426 | 701.0801 | 753.6218 | 676.1553
1026.426 | 701.1142 | 753.2448 | 676.0356
1027.426 | 700.7785 | 752.9526 | 675.9147
1028.426 | 700.6848 | 752.598 | 675.7767
1029.426 | 700.4778 | 752.2268 | 675.7011
1030.426 | 700.2601 | 751.8394 | 675.6689
1031.426 | 700.5225 | 751.4873 | 675.664
1032.426 | 700.5781 | 751.104 | 675.6551
1033.426 | 700.5909 | 750.7166 | 675.6209
1034.426 | 700.598 | 750.3903 | 675.5429
1035.426 | 700.586 | 750.008 | 675.4437
1036.426 | 700.5974 | 749.5988 | 675.3414
1037.426 | 700.7466 | 749.1981 | 675.2082
1038.426 | 700.9557 | 748.8488 | 675.0576
1039.426 | 700.8863 | 748.4813 | 674.9023
1040.426 | 700.8741 | 748.0353 | 674.7756
1041.426 | 700.7439 | 747.6019 | 674.6624
1042.426 | 700.7835 | 747.1575 | 674.5233
1043.426 | 700.8379 | 746.7036 | 674.3394
1044.426 | 700.9577 | 746.2258 | 674.1888
1045.426 | 701.0192 | 745.7487 | 674.0429
1046.426 | 701.0496 | 745.1953 | 673.8841
1047.426 | 701.2059 | 744.657 | 673.7183
1048.426 | 701.3962 | 743.993 | 673.5535
1049.426 | 701.3639 | 743.3199 | 673.3855
1050.426 | 701.3166 | 742.6509 | 673.202
1051.426 | 701.1511 | 741.8889 | 673.044
1052.426 | 701.1368 | 741.1387 | 672.8978
1053.426 | 701.0837 | 740.3675 | 672.7679
1054.426 | 701.3022 | 739.5542 | 672.6154
1055.426 | 701.1664 | 738.7372 | 672.4731
1056.426 | 701.0145 | 737.8817 | 672.3199
1057.426 | 700.9711 | 737.0133 | 672.1645
1058.426 | 701.0097 | 736.0883 | 672.0216
1059.426 | 700.8852 | 735.1621 | 671.89
1060.426 | 700.7791 | 734.2598 | 671.7584
1061.426 | 700.8914 | 733.3604 | 671.6206
1062.426 | 700.9291 | 732.4238 | 671.5088
1063.426 | 700.9527 | 731.4605 | 671.4536
1064.426 | 700.9932 | 730.5231 | 671.4322
1065.426 | 701.2769 | 729.5598 | 671.3912
1066.426 | 701.5214 | 728.6295 | 671.3212
1067.426 | 701.5249 | 727.7147 | 671.2074
1068.426 | 701.4622 | 726.7792 | 671.0664
1069.426 | 701.4134 | 725.8726 | 670.9049
1070.426 | 701.3801 | 724.9494 | 670.7208
1071.426 | 701.5268 | 724.0303 | 670.5474
1072.426 | 701.4453 | 723.1384 | 670.397
1073.426 | 701.5004 | 722.2483 | 670.3056
1074.426 | 701.714 | 721.3776 | 670.2298
1075.426 | 701.7354 | 720.4891 | 670.1645
1076.426 | 701.7808 | 719.618 | 670.1041
1077.426 | 701.7607 | 718.8186 | 670.04
1078.426 | 701.7874 | 717.9769 | 669.9607
1079.426 | 701.8724 | 717.1806 | 669.8561
1080.426 | 701.8649 | 716.4031 | 669.7223
1081.426 | 701.8282 | 715.6524 | 669.5711
1082.426 | 701.7711 | 714.9227 | 669.435
1083.426 | 701.7644 | 714.2152 | 669.2526
1084.426 | 701.7219 | 713.5127 | 669.0668
1085.426 | 701.7578 | 712.8347 | 668.9329
1086.426 | 701.8459 | 712.1705 | 668.8219
1087.426 | 701.9768 | 711.5075 | 668.6829
1088.426 | 701.7392 | 710.8675 | 668.5579
1089.426 | 701.724 | 710.2516 | 668.488
1090.426 | 701.782 | 709.6554 | 668.4658
1091.426 | 701.9425 | 709.0838 | 668.4294
1092.426 | 702.069 | 708.5116 | 668.3649
1093.426 | 702.0166 | 707.9665 | 668.3255
1094.426 | 701.9926 | 707.4397 | 668.2583
1095.426 | 702.0503 | 706.921 | 668.2041
1096.426 | 702.0607 | 706.4134 | 668.1198
1097.426 | 702.1862 | 705.9151 | 668.0117
1098.426 | 702.1329 | 705.4216 | 667.8852
1099.426 | 701.9595 | 704.9474 | 667.7731
1100.426 | 702.0499 | 704.5003 | 667.6655
1101.426 | 702.1919 | 704.0313 | 667.5675
1102.426 | 702.2674 | 703.5791 | 667.4525
1103.426 | 702.178 | 703.1693 | 667.3394
1104.426 | 702.0553 | 702.7551 | 667.2707
1105.426 | 701.9731 | 702.3676 | 667.2234
1106.426 | 701.8691 | 701.9642 | 667.1732
1107.426 | 702.0672 | 701.5781 | 667.0951
1108.426 | 702.0514 | 701.1932 | 667.0307
1109.426 | 702.05 | 700.8557 | 666.9916
1110.426 | 702.1413 | 700.5119 | 666.9439
1111.426 | 702.1844 | 700.1723 | 666.8902
1112.426 | 702.1794 | 699.8389 | 666.8419
1113.426 | 702.1222 | 699.5283 | 666.8075
1114.426 | 702.0202 | 699.2282 | 666.7731
1115.426 | 702.1657 | 698.948 | 666.7503
1116.426 | 702.2065 | 698.6705 | 666.7316
1117.426 | 702.5174 | 698.3947 | 666.7093
1118.426 | 702.4612 | 698.1185 | 666.666
1119.426 | 702.591 | 697.8456 | 666.609
1120.426 | 702.5167 | 697.5789 | 666.526
1121.426 | 702.4633 | 697.3185 | 666.4445
1122.426 | 702.423 | 697.0823 | 666.3698
1123.426 | 702.5009 | 696.8462 | 666.3549
1124.426 | 702.6321 | 696.6047 | 666.3358
1125.426 | 702.6854 | 696.3658 | 666.3015
1126.426 | 702.7325 | 696.1286 | 666.2271
1127.426 | 702.9937 | 695.9056 | 666.1268
1128.426 | 703.0504 | 695.6672 | 666.0106
1129.426 | 702.9962 | 695.4395 | 665.9412
1130.426 | 702.9526 | 695.2058 | 665.8766
1131.426 | 702.9013 | 694.9756 | 665.811
1132.426 | 702.8773 | 694.7704 | 665.7527
1133.426 | 702.762 | 694.5589 | 665.6851
1134.426 | 702.5436 | 694.3754 | 665.6276
1135.426 | 702.3936 | 694.1818 | 665.5482
1136.426 | 702.3672 | 694.002 | 665.4741
1137.426 | 702.2391 | 693.7914 | 665.3813
1138.426 | 701.9683 | 693.5803 | 665.2455
1139.426 | 701.9041 | 693.3902 | 665.1333
1140.426 | 702.0559 | 693.176 | 665.0344
1141.426 | 701.7939 | 692.9682 | 664.8838
1142.426 | 701.7968 | 692.766 | 664.7347
1143.426 | 701.7559 | 692.5709 | 664.5951
1144.426 | 701.9088 | 692.3763 | 664.4635
1145.426 | 702.0509 | 692.1662 | 664.2917
1146.426 | 701.9004 | 691.9521 | 664.0807
1147.426 | 701.996 | 691.7681 | 663.9083
1148.426 | 702.0774 | 691.5876 | 663.7768
1149.426 | 702.1774 | 691.4161 | 663.7011
1150.426 | 702.1936 | 691.2428 | 663.6708
1151.426 | 702.2378 | 691.075 | 663.6653
1152.426 | 702.3854 | 690.9181 | 663.6673
1153.426 | 702.0956 | 690.737 | 663.6805
1154.426 | 701.9141 | 690.5783 | 663.6839
1155.426 | 701.8621 | 690.4181 | 663.681
1156.426 | 701.6265 | 690.244 | 663.6837
1157.426 | 701.4477 | 690.0743 | 663.6988
1158.426 | 701.4742 | 689.9074 | 663.6995
1159.426 | 701.3809 | 689.7347 | 663.6982
1160.426 | 701.3387 | 689.5446 | 663.6529
1161.426 | 701.4613 | 689.343 | 663.5956
1162.426 | 701.5021 | 689.1418 | 663.5258
1163.426 | 701.6921 | 688.9478 | 663.4563
1164.426 | 701.9178 | 688.7481 | 663.3971
1165.426 | 701.8395 | 688.524 | 663.3452
1166.426 | 701.8694 | 688.3284 | 663.2719
1167.426 | 701.8359 | 688.1284 | 663.2115
1168.426 | 701.768 | 687.9151 | 663.1455
1169.426 | 701.659 | 687.7032 | 663.0382
1170.426 | 701.4639 | 687.4903 | 662.9185
1171.426 | 701.4411 | 687.2901 | 662.8095
1172.426 | 701.4199 | 687.1001 | 662.702
1173.426 | 701.3858 | 686.8956 | 662.589
1174.426 | 701.4482 | 686.7121 | 662.4805
1175.426 | 701.5147 | 686.5389 | 662.3948
1176.426 | 701.6631 | 686.3611 | 662.3228
1177.426 | 701.8462 | 686.2078 | 662.2655
1178.426 | 701.9429 | 686.0475 | 662.2524
1179.426 | 701.933 | 685.8828 | 662.2471
1180.426 | 702.0486 | 685.7217 | 662.1988
1181.426 | 702.1163 | 685.5589 | 662.1364
1182.426 | 701.9812 | 685.391 | 662.1087
1183.426 | 701.9907 | 685.2141 | 662.0813
1184.426 | 701.9384 | 685.0399 | 662.0168
1185.426 | 701.9959 | 684.8451 | 661.9357
1186.426 | 702.1637 | 684.667 | 661.8401
1187.426 | 702.2185 | 684.4831 | 661.7379
1188.426 | 701.9596 | 684.2841 | 661.6311
1189.426 | 701.9729 | 684.0999 | 661.5489
1190.426 | 702.0543 | 683.9267 | 661.5128
1191.426 | 702.1992 | 683.7094 | 661.4702
1192.426 | 702.3263 | 683.5157 | 661.4269
1193.426 | 702.1579 | 683.3171 | 661.3876
1194.426 | 702.1516 | 683.1359 | 661.3529
1195.426 | 702.1865 | 682.9565 | 661.2515
1196.426 | 702.2237 | 682.7708 | 661.2228
1197.426 | 702.1418 | 682.5791 | 661.0969
1198.426 | 702.4023 | 682.3724 | 660.9701
1199.426 | 702.3997 | 682.1699 | 660.8785
1200.426 | 702.4912 | 681.9669 | 660.7827
1201.426 | 702.4586 | 681.7887 | 660.6899
1202.426 | 702.2313 | 681.6048 | 660.6105
1203.426 | 702.2441 | 681.4345 | 660.5388
1204.426 | 702.4983 | 681.2752 | 660.5078
1205.426 | 702.4337 | 681.1165 | 660.4736
1206.426 | 702.375 | 680.9703 | 660.4256
1207.426 | 702.373 | 680.8137 | 660.3778
1208.426 | 702.3331 | 680.6524 | 660.3479
1209.426 | 702.3083 | 680.4793 | 660.3235
1210.426 | 702.0543 | 680.3109 | 660.3269
1211.426 | 702.0005 | 680.157 | 660.3806
1212.426 | 702.0064 | 679.9951 | 660.4445
1213.426 | 702.0584 | 679.8455 | 660.469
1214.426 | 702.1527 | 679.7135 | 660.4803
1215.426 | 702.1029 | 679.5806 | 660.487
1216.426 | 702.0107 | 679.4301 | 660.4719
1217.426 | 701.7841 | 679.3076 | 660.4699
1218.426 | 701.5671 | 679.1816 | 660.4519
1219.426 | 701.505 | 679.0338 | 660.4088
1220.426 | 701.1993 | 678.9037 | 660.3173
1221.426 | 701.1349 | 678.754 | 660.238
1222.426 | 700.9912 | 678.6332 | 660.1397
1223.426 | 700.9184 | 678.5149 | 660.0665
1224.426 | 700.9231 | 678.3886 | 660.0107
1225.426 | 701.1303 | 678.2647 | 659.9577
1226.426 | 701.0439 | 678.127 | 659.9362
1227.426 | 701.1546 | 677.9983 | 659.9417
1228.426 | 701.3306 | 677.8981 | 659.9692
1229.426 | 701.5715 | 677.7887 | 659.9419
1230.426 | 701.6921 | 677.6623 | 659.8358
1231.426 | 701.9097 | 677.5374 | 659.7196
1232.426 | 701.9321 | 677.4061 | 659.5758
1233.426 | 702.0066 | 677.2725 | 659.4537
1234.426 | 702.0595 | 677.1379 | 659.3706
1235.426 | 701.8968 | 676.9818 | 659.2939
1236.426 | 701.6712 | 676.8332 | 659.1973
1237.426 | 701.4108 | 676.6807 | 659.096
1238.426 | 701.1323 | 676.5232 | 658.5751
1239.426 | 701.0807 | 676.3849 | 658.5344
1240.426 | 701.1412 | 676.2619 | 658.5367
1241.426 | 701.1998 | 676.1376 | 658.5799
1242.426 | 701.2023 | 676.0252 | 658.6532
1243.426 | 701.1812 | 675.9042 | 658.712
1244.426 | 700.9931 | 675.7891 | 658.7516
1245.426 | 700.9454 | 675.6801 | 658.7575
1246.426 | 701.0284 | 675.5644 | 658.7504
1247.426 | 701.0876 | 675.4485 | 658.7153
1248.426 | 701.0659 | 675.3172 | 658.6149
1249.426 | 701.1653 | 675.2002 | 658.5297
1250.426 | 701.1081 | 675.09 | 658.4999
1251.426 | 701.4351 | 674.9743 | 658.4858
1252.426 | 701.4537 | 674.8577 | 658.4805
1253.426 | 701.5634 | 674.7453 | 658.4492
1254.426 | 701.4845 | 674.6423 | 658.3937
1255.426 | 701.4527 | 674.5335 | 658.3116
1256.426 | 701.4396 | 674.4216 | 658.217
1257.426 | 701.4258 | 674.3237 | 658.1571
1258.426 | 701.3143 | 674.2033 | 658.0827
1259.426 | 701.1881 | 674.1122 | 657.9924
1260.426 | 701.2078 | 674.0083 | 657.9212
1261.426 | 701.1586 | 673.8975 | 657.8751
1262.426 | 700.9862 | 673.8005 | 657.8685
1263.426 | 700.9549 | 673.7067 | 657.8791
1264.426 | 700.9247 | 673.6201 | 657.8925
1265.426 | 701.0882 | 673.5411 | 657.9255
1266.426 | 701.1441 | 673.4749 | 657.9944
1267.426 | 701.2883 | 673.4105 | 657.9962
1268.426 | 701.4113 | 673.3182 | 657.98
1269.426 | 701.3498 | 673.2277 | 657.9495
1270.426 | 701.4698 | 673.1356 | 657.9156
1271.426 | 701.8497 | 673.0376 | 657.8726
1272.426 | 701.9807 | 672.9502 | 657.8137
1273.426 | 701.8619 | 672.8538 | 657.7548
1274.426 | 701.9921 | 672.7526 | 657.7036
1275.426 | 701.7951 | 672.6486 | 657.6636
1276.426 | 701.8083 | 672.5354 | 657.6429
1277.426 | 701.7502 | 672.4364 | 657.6176
1278.426 | 701.8838 | 672.3199 | 657.5829
1279.426 | 701.9203 | 672.2163 | 657.5216
1280.426 | 701.9565 | 672.1111 | 657.4411
1281.426 | 702.177 | 672.0267 | 657.349
1282.426 | 702.011 | 671.9398 | 657.2609
1283.426 | 701.9905 | 671.866 | 657.1916
1284.426 | 701.955 | 671.7806 | 657.1696
1285.426 | 701.9063 | 671.6995 | 657.1279
1286.426 | 701.9754 | 671.6176 | 657.078
1287.426 | 702.0974 | 671.5308 | 657.0084
1288.426 | 702.1186 | 671.4617 | 656.9772
1289.426 | 702.2122 | 671.3789 | 656.9644
1290.426 | 702.3436 | 671.2843 | 656.9452
1291.426 | 702.2732 | 671.1721 | 656.8645
1292.426 | 702.1602 | 671.0674 | 656.7229
1293.426 | 702.2387 | 670.9559 | 656.5453
1294.426 | 701.9147 | 670.8644 | 656.3691
1295.426 | 701.5906 | 670.7502 | 656.2389
1296.426 | 701.6407 | 670.655 | 656.0843
1297.426 | 701.629 | 670.5398 | 655.9496
1298.426 | 701.6008 | 670.4201 | 655.8347
1299.426 | 701.4541 | 670.3206 | 655.7744
1300.426 | 701.3236 | 670.2111 | 655.7245
1301.426 | 701.4859 | 670.1267 | 655.6613
1302.426 | 701.5503 | 670.0486 | 655.5994
1303.426 | 701.5282 | 669.9608 | 655.4816
1304.426 | 701.5632 | 669.8774 | 655.3548
1305.426 | 701.5393 | 669.7954 | 655.2364
1306.426 | 701.5331 | 669.731 | 655.1299
1307.426 | 701.7159 | 669.6413 | 655.067
1308.426 | 701.605 | 669.5784 | 654.9894
1309.426 | 701.6534 | 669.4999 | 654.9095
1310.426 | 701.5725 | 669.426 | 654.8403
1311.426 | 701.518 | 669.3505 | 654.8027
1312.426 | 701.3716 | 669.3023 | 654.7695
1313.426 | 701.1746 | 669.2534 | 654.747
1314.426 | 701.23 | 669.1938 | 654.7316
1315.426 | 701.2847 | 669.1333 | 654.6954
1316.426 | 701.1948 | 669.0649 | 654.6404
1317.426 | 701.2027 | 669.0084 | 654.5626
1318.426 | 701.2248 | 668.9486 | 654.4785
1319.426 | 701.3649 | 668.9117 | 654.3984
1320.426 | 701.5828 | 668.8438 | 654.3128
1321.426 | 701.5132 | 668.7665 | 654.1957
1322.426 | 701.574 | 668.7121 | 654.0949
1323.426 | 701.6488 | 668.6535 | 654.0063
1324.426 | 701.6539 | 668.6033 | 653.9626
1325.426 | 701.7089 | 668.5508 | 653.9753
1326.426 | 701.8316 | 668.4911 | 653.9815
1327.426 | 702.022 | 668.407 | 653.9481
1328.426 | 702.1981 | 668.3328 | 653.8827
1329.426 | 702.1183 | 668.2442 | 653.7991
1330.426 | 701.9846 | 668.1646 | 653.7235
1331.426 | 702.0766 | 668.0695 | 653.6365
1332.426 | 702.0012 | 667.9768 | 653.4664
1333.426 | 701.9678 | 667.8751 | 653.2587
1334.426 | 702.0204 | 667.7782 | 653.0582
1335.426 | 701.7405 | 667.6408 | 652.8958
1336.426 | 701.5689 | 667.5288 | 652.7562
1337.426 | 701.6807 | 667.4029 | 652.6316
1338.426 | 701.6872 | 667.2872 | 652.5256
1339.426 | 701.7382 | 667.1883 | 652.4439
1340.426 | 701.6467 | 667.0958 | 652.3557
1341.426 | 701.5639 | 667.0161 | 652.2752
1342.426 | 701.4061 | 666.903 | 652.183
1343.426 | 701.5546 | 666.8148 | 652.0636
1344.426 | 701.7811 | 666.7483 | 651.9823
1345.426 | 702.1124 | 666.6839 | 651.9712
1346.426 | 702.1135 | 666.6316 | 651.97
1347.426 | 702.2129 | 666.5801 | 651.9518
1348.426 | 702.1918 | 666.5342 | 651.9083
1349.426 | 702.1528 | 666.4941 | 651.8751
1350.426 | 701.9616 | 666.4515 | 651.8662
1351.426 | 701.9514 | 666.3872 | 651.8547
1352.426 | 701.8274 | 666.3129 | 651.8207
1353.426 | 701.8258 | 666.2833 | 651.793
1354.426 | 701.7705 | 666.2419 | 651.7976
1355.426 | 701.8326 | 666.184 | 651.8422
1356.426 | 701.9252 | 666.1466 | 651.8903
1357.426 | 702.0174 | 666.1085 | 651.9564
1358.426 | 702.0182 | 666.068 | 652.0185
1359.426 | 702.0063 | 666.0346 | 652.0675
1360.426 | 701.8738 | 665.9849 | 652.0975
1361.426 | 701.7608 | 665.9359 | 652.1249
1362.426 | 701.7048 | 665.8919 | 652.1524
1363.426 | 701.7602 | 665.8074 | 652.1757
1364.426 | 701.7808 | 665.7534 | 652.1729
1365.426 | 701.8265 | 665.685 | 652.1509
1366.426 | 701.9284 | 665.5974 | 652.0721
1367.426 | 701.7796 | 665.4941 | 651.9214
1368.426 | 701.7891 | 665.3934 | 651.7638
1369.426 | 701.849 | 665.3171 | 651.6413
1370.426 | 701.8901 | 665.2696 | 651.5497
1371.426 | 701.7982 | 665.2213 | 651.49
1372.426 | 701.9832 | 665.1856 | 651.4808
1373.426 | 702.1548 | 665.1551 | 651.4704
1374.426 | 702.1291 | 665.1197 | 651.4229
1375.426 | 702.1013 | 665.092 | 651.3641
1376.426 | 701.89 | 665.0624 | 651.3149
1377.426 | 701.7816 | 665.0312 | 651.2847
1378.426 | 701.8261 | 665.0017 | 651.2446
1379.426 | 702.0137 | 664.9631 | 651.2092
1380.426 | 701.8315 | 664.9267 | 651.1892
1381.426 | 701.8588 | 664.8694 | 651.1975
1382.426 | 701.8279 | 664.8428 | 651.2031
1383.426 | 701.7726 | 664.7753 | 651.1513
1384.426 | 701.4723 | 664.7039 | 651.0992
1385.426 | 701.3332 | 664.6316 | 651.0496
1386.426 | 700.9577 | 664.5818 | 651.0137
1387.426 | 700.8346 | 664.5256 | 650.989
1388.426 | 700.8338 | 664.4622 | 650.9722
1389.426 | 701.0037 | 664.4241 | 650.9654
1390.426 | 701.1206 | 664.3475 | 650.9469
1391.426 | 701.1915 | 664.307 | 650.9262
1392.426 | 701.2156 | 664.2449 | 650.9062
1393.426 | 701.1879 | 664.1879 | 650.8993
1394.426 | 700.9994 | 664.1355 | 650.9034
1395.426 | 700.971 | 664.0738 | 650.9219
1396.426 | 701.0209 | 664.0236 | 650.9199
1397.426 | 701.0655 | 663.9747 | 650.9167
1398.426 | 701.2632 | 663.9135 | 650.8961
1399.426 | 701.2596 | 663.8617 | 650.8663
1400.426 | 701.1821 | 663.8057 | 650.8156
1401.426 | 701.1372 | 663.7441 | 650.7464
1402.426 | 701.1256 | 663.6976 | 650.6244
1403.426 | 701.4751 | 663.6532 | 650.5305
1404.426 | 701.6992 | 663.5733 | 650.4834
1405.426 | 701.8117 | 663.5264 | 650.4434
1406.426 | 701.896 | 663.4557 | 650.3751
1407.426 | 701.8766 | 663.3615 | 650.3028
1408.426 | 701.6615 | 663.2781 | 650.2382
1409.426 | 701.4879 | 663.1987 | 650.1442
1410.426 | 701.2465 | 663.1345 | 650.0247
1411.426 | 701.1755 | 663.0753 | 649.9349
1412.426 | 701.2845 | 663.0306 | 649.8468
1413.426 | 701.2706 | 662.9643 | 649.7149
1414.426 | 701.2156 | 662.9128 | 649.5861
1415.426 | 701.4304 | 662.8629 | 649.4529
1416.426 | 701.4455 | 662.8034 | 649.3332
1417.426 | 701.445 | 662.7377 | 649.2155
1418.426 | 701.4811 | 662.6671 | 649.0613
1419.426 | 701.4021 | 662.5876 | 648.8947
1420.426 | 701.3519 | 662.5312 | 648.7684
1421.426 | 701.2356 | 662.475 | 648.6938
1422.426 | 701.1433 | 662.44 | 648.6598
1423.426 | 701.221 | 662.3902 | 648.66
1424.426 | 701.0335 | 662.3596 | 648.6744
1425.426 | 700.9189 | 662.3071 | 648.6479
1426.426 | 700.8487 | 662.2459 | 648.5742
1427.426 | 700.82 | 662.1886 | 648.4811
1428.426 | 701.0335 | 662.1262 | 648.404
1429.426 | 701.0764 | 662.0625 | 648.3255
1430.426 | 701.2633 | 661.9938 | 648.2538
1431.426 | 701.3764 | 661.9428 | 648.1754
1432.426 | 701.3822 | 661.9034 | 648.0921
1433.426 | 701.4398 | 661.8553 | 647.9886
1434.426 | 701.5023 | 661.8269 | 647.8301
1435.426 | 701.5806 | 661.7738 | 647.6534
1436.426 | 701.6539 | 661.7259 | 647.5097
1437.426 | 701.9006 | 661.6833 | 647.385
1438.426 | 701.9545 | 661.6287 | 647.2575
1439.426 | 701.9922 | 661.5737 | 647.1052
1440.426 | 701.9449 | 661.5038 | 646.9316
1441.426 | 702.0554 | 661.4421 | 646.771
1442.426 | 701.9749 | 661.4027 | 646.6498
1443.426 | 702.0001 | 661.3446 | 646.5753
1444.426 | 701.7499 | 661.2974 | 646.5391
1445.426 | 701.6109 | 661.2576 | 646.5183
1446.426 | 701.5627 | 661.2283 | 646.4984
1447.426 | 701.7096 | 661.1672 | 646.4534
1448.426 | 701.7615 | 661.1254 | 646.4255
1449.426 | 701.6785 | 661.079 | 646.372
1450.426 | 701.7851 | 661.0472 | 646.3303
1451.426 | 701.8068 | 661.0118 | 646.2049
1452.426 | 701.9432 | 660.9752 | 646.2431
1453.426 | 701.7946 | 660.9435 | 646.1725
1454.426 | 701.6628 | 660.9098 | 646.1291
1455.426 | 701.5896 | 660.8697 | 646.0905
1456.426 | 701.5823 | 660.8396 | 646
1457.426 | 701.5614 | 660.7938 | 645.9302
1458.426 | 701.4423 | 660.7473 | 645.8549
1459.426 | 701.4363 | 660.704 | 645.7995
1460.426 | 701.5714 | 660.6627 | 645.7732
1461.426 | 701.688 | 660.6096 | 645.7482
1462.426 | 701.8089 | 660.5679 | 645.6971
1463.426 | 701.6808 | 660.5301 | 645.672
1464.426 | 701.7895 | 660.4765 | 645.6603
1465.426 | 701.9093 | 660.4443 | 645.7125
1466.426 | 702.0153 | 660.4176 | 645.7914
1467.426 | 702.057 | 660.3804 | 645.8648
1468.426 | 701.9042 | 660.3481 | 645.9048
1469.426 | 702.0588 | 660.3158 | 645.9148
1470.426 | 702.0604 | 660.2913 | 645.8831
1471.426 | 702.093 | 660.2516 | 645.8035
1472.426 | 702.1642 | 660.253 | 645.74
1473.426 | 702.2195 | 660.2278 | 645.6982
1474.426 | 702.1824 | 660.2046 | 645.647
1475.426 | 702.0395 | 660.1976 | 645.6125
1476.426 | 701.7244 | 660.1594 | 645.5618
1477.426 | 701.6623 | 660.1582 | 645.5234
1478.426 | 701.5514 | 660.1533 | 645.4986
1479.426 | 701.6709 | 660.137 | 645.476
1480.426 | 701.9208 | 660.1174 | 645.4441
1481.426 | 701.6078 | 660.0979 | 645.3782
1482.426 | 701.7849 | 660.0706 | 645.2989
1483.426 | 701.7184 | 660.0359 | 645.2085
1484.426 | 701.7311 | 659.9946 | 645.1497
1485.426 | 701.8448 | 659.9742 | 645.1406
1486.426 | 701.7951 | 659.9439 | 645.1763
1487.426 | 701.8728 | 659.9268 | 645.2079
1488.426 | 701.7722 | 659.9185 | 645.2321
1489.426 | 701.6959 | 659.8923 | 645.2312
1490.426 | 701.7843 | 659.8606 | 645.2235
1491.426 | 701.7308 | 659.8475 | 645.228
1492.426 | 701.7358 | 659.8269 | 645.2584
1493.426 | 701.7684 | 659.8095 | 645.263
1494.426 | 701.725 | 659.7791 | 645.2511
1495.426 | 701.7309 | 659.7161 | 645.2178
1496.426 | 701.8717 | 659.6527 | 645.1502
1497.426 | 701.6794 | 659.6093 | 645.1155
1498.426 | 701.5795 | 659.5764 | 645.1102
1499.426 | 701.6022 | 659.556 | 645.1706
1500.426 | 701.7227 | 659.5429 | 645.253
1501.426 | 701.633 | 659.5323 | 645.345
1502.426 | 701.6363 | 659.5272 | 645.4022
1503.426 | 701.6897 | 659.5249 | 645.4247
1504.426 | 701.8296 | 659.5174 | 645.4296
1505.426 | 701.8279 | 659.4972 | 645.4474
1506.426 | 701.7204 | 659.4563 | 645.4595
1507.426 | 701.7308 | 659.4051 | 645.4659
1508.426 | 701.5158 | 659.3504 | 645.4383
1509.426 | 701.4006 | 659.2803 | 645.4238
1510.426 | 701.4692 | 659.2123 | 645.4172
1511.426 | 701.2565 | 659.1503 | 645.4183
1512.426 | 701.1392 | 659.0923 | 645.404
1513.426 | 701.0851 | 659.0356 | 645.4078
1514.426 | 700.9605 | 658.9752 | 645.4205
1515.426 | 700.8298 | 658.9269 | 645.4126
1516.426 | 700.8539 | 658.894 | 645.4095
1517.426 | 700.9319 | 658.8589 | 645.4043
1518.426 | 701.0374 | 658.8394 | 645.3677
1519.426 | 701.1337 | 658.7912 | 645.3032
1520.426 | 701.2466 | 658.7613 | 645.2005
1521.426 | 701.3585 | 658.7318 | 645.1428
1522.426 | 701.346 | 658.698 | 645.1136
1523.426 | 701.4391 | 658.6646 | 645.1337
1524.426 | 701.2213 | 658.6455 | 645.1791
1525.426 | 701.1731 | 658.631 | 645.2305
1526.426 | 701.0589 | 658.6173 | 645.2634
1527.426 | 701.06 | 658.6106 | 645.2799
1528.426 | 701.1812 | 658.587 | 645.3141
1529.426 | 701.2476 | 658.5715 | 645.3265
1530.426 | 701.2048 | 658.5633 | 645.3547
1531.426 | 701.2511 | 658.5566 | 645.3855
1532.426 | 701.2723 | 658.5622 | 645.3965
1533.426 | 701.3463 | 658.5489 | 645.3729
1534.426 | 701.2948 | 658.5326 | 645.3407
1535.426 | 701.2297 | 658.5033 | 645.2825
1536.426 | 701.153 | 658.4763 | 645.2338
1537.426 | 701.2852 | 658.4462 | 645.2119
1538.426 | 701.3444 | 658.427 | 645.1968
1539.426 | 701.1341 | 658.4016 | 645.159
1540.426 | 701.1273 | 658.3517 | 645.0828
1541.426 | 701.267 | 658.3168 | 645.0557
1542.426 | 701.372 | 658.2953 | 645.0904
1543.426 | 701.4461 | 658.269 | 645.1214
1544.426 | 701.6203 | 658.2462 | 645.1131
1545.426 | 701.6152 | 658.2187 | 645.0784
1546.426 | 701.5704 | 658.1948 | 645.0591
1547.426 | 701.6529 | 658.1676 | 645.0615
1548.426 | 701.6482 | 658.1677 | 645.0575
1549.426 | 701.645 | 658.1436 | 645.0599
1550.426 | 701.6445 | 658.13 | 645.0792
1551.426 | 701.5868 | 658.1132 | 645.1074
1552.426 | 701.5593 | 658.113 | 645.1632
1553.426 | 701.3356 | 658.1133 | 645.1938
1554.426 | 700.9332 | 658.1007 | 645.2142
1555.426 | 700.865 | 658.0979 | 645.2288
1556.426 | 700.8787 | 658.0865 | 645.2459
1557.426 | 700.9214 | 658.0614 | 645.2621
1558.426 | 701.0357 | 658.0647 | 645.238
1559.426 | 700.9092 | 658.0597 | 645.2256
1560.426 | 700.9227 | 658.0434 | 645.2213