## Test Conditions
DESIREE-FIRE Test Number 45 - Circuit Simulator Data Only
Test Date: | 2009-10-09
DCSim DAQ Start Time | 8:37
DCSim Time for Synchronization | 9:21
Heat Source Synchronization | 11:31 | minutes:seconds
Heat Source DAQ Start Time | 9:09
Fire Time | 9:27
Offset | 0:50 | minutes:seconds | This is the time after the DCSim DAQ was started and the heat source was initiated.
| 3000 | seconds
Heat Source Offset | 0:18 | minutes:seconds | This is the time after the Heat Source DAQ was started and the heat source was initiated.
| 1051 | seconds
Heat Source Stop Time | 10:04
Test Duration | 0:37 | minutes:seconds
| 2220 | seconds
Cable Information: | Record info about cable type on each circuit and which of the cable thermocouples corresponds to cable and air temperature
Unit number | Cable Type |  | Cable TC channel | Air TC Channel
XLPE/CSPE, 7c, 12AWG
A Note on Data Conversion and Accuracy:
Two different types of voltage transducers were used for each circuit. A bidirectional transducer (Ohio Semitronics, model number VT7-005X5-11) produces a 0 - 5V output signal which is directly proportional to the DC input ranging from 0 - 150VDC. The accuracy of this device is +/-0.25% full scale at DC and the response time is 50 mircoseconds. The unidirectional DC voltage isolator (Ohio Semitronics, model number VTU-005X5) used throughout tests also produces a 0 - 5V output over a 0 - 150VDC range. The accuracy of this device is +/-0.25% Rdg., +/-1% full scale at DC and the response time is 500 microseconds.
The readings were monitored using a National Instruments SCXI-1100 modules attached to SCXI-1300 multiplexers and housed within a SCXI-1001, 12-slot chassis. The "Raw Data" worksheet has been previously converted by LabView program created for this test series. The nominal zero point readings for each current transducer was taken before each test due to an electromagnetic effect created by direct current power. Zero Point values are provided, and the full run is documented in a separate data sheet (see "Current Offsets" worksheet). The converted data are presented as nominal indications of circuit path voltage and current. The data gathering equipment (transducers and DAQ card) have not been subject to specific calibration beyond that provided by the manufacturers. The accuracy of the converted data is estimated at +/-2%.

## Electrical Data
Fire Time (s) | Ground_VT7_1 | Ground_VTU_1 | Ground_VTU_2 | Int-Cab_VT7-T1 | Int-Cab_VT7-T2 | Int-Cab_VT7-T3 | Int-Cab_VT7-T4 | Int-Cab_VT7-T5 | Int-Cab_VT7-T6 | Int-Cab_VT7-T7 | Int-Cab_VTU-S1+a | Int-Cab_VTU-S1+b | Int-Cab_VTU-S2+a | Int-Cab_VTU-S2+b | Int-Cab_VTU-S1-a | Int-Cab_VTU-S1-b | Int-Cab_VTU-S2-a | Int-Cab_VTU-S2-b | T1-V(Batt -) | T2 -V(Batt -) | T3 - V(Batt -) | T4 - V(Batt -) | T5 - V(Batt -) | T6 - V(Batt -) | T7 - V(Batt -) | {S1+a} - V(Batt - ) | {S1+b} - V(Batt - ) | {S2+a} - V(Batt - ) | {S2+b} - V(Batt - ) | {S1-a} - V(Batt -) | {S1-b} - V(Batt - ) | {S2-a} - V(Batt - ) | {S2-b} - V(Batt - ) | {S1+a} - {S1-a} | {S1+a} - {S2-a} | {S2+a} - {S1-a} | {S2+a} - {S2-a}
-0.10938 | 123.2025 | -61.4182 | 61.5692 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4593 | 0.12501 | 61.4088 | -0.055996 | 0.007032 | 61.5158 | 0.003143 | 61.4084 | 61.4393 | 61.3776 | 61.4016 | 61.4114 | 61.4407 | 61.4305 | 61.4378 | 122.8774 | 61.5432 | 122.827 | 61.3622 | 61.4252 | 122.934 | 61.4213 | 122.8266 | 61.4522 | 61.4561 | 61.4018 | 61.4057
0.89062 | 123.1247 | -61.4136 | 61.615 | 0.030283 | -0.0451 | -0.016578 | -0.011281 | 0.027109 | 0.00775 | 0.015112 | 61.4501 | 0.11585 | 61.3859 | -0.092628 | 0.002454 | 61.5112 | -0.006014 | 61.4863 | 61.4439 | 61.3685 | 61.397 | 61.4023 | 61.4407 | 61.4213 | 61.4287 | 122.8637 | 61.5294 | 122.7995 | 61.3209 | 61.416 | 122.9248 | 61.4076 | 122.8998 | 61.4477 | 61.4561 | 61.3835 | 61.392
1.8906 | 123.1476 | -61.4502 | 61.5875 | 0.016548 | -0.0451 | -0.016578 | -0.01586 | 0.022531 | 0.003172 | 0.015112 | 61.4455 | 0.12501 | 61.3905 | -0.088049 | 0.007032 | 61.5204 | -0.033484 | 61.4954 | 61.4667 | 61.4051 | 61.4336 | 61.4343 | 61.4727 | 61.4534 | 61.4653 | 122.8957 | 61.5752 | 122.8407 | 61.3621 | 61.4572 | 122.9706 | 61.4167 | 122.9456 | 61.4385 | 61.479 | 61.3835 | 61.424
2.8906 | 123.175 | -61.4273 | 61.5967 | 0.025705 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4455 | 0.12501 | 61.3905 | -0.088049 | 0.002454 | 61.5158 | -0.019749 | 61.2848 | 61.453 | 61.3822 | 61.4199 | 61.4206 | 61.4498 | 61.4396 | 61.447 | 122.8728 | 61.5523 | 122.8178 | 61.3393 | 61.4298 | 122.9431 | 61.4076 | 122.7121 | 61.4431 | 61.4653 | 61.3881 | 61.4103
3.8906 | 123.1476 | -61.4502 | 61.5921 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | 0.00775 | 0.015112 | 61.4455 | 0.12501 | 61.3859 | -0.092628 | 0.002454 | 61.5112 | -0.024328 | 61.2894 | 61.4713 | 61.4097 | 61.4336 | 61.4389 | 61.4773 | 61.4579 | 61.4653 | 122.8957 | 61.5752 | 122.8361 | 61.3576 | 61.4526 | 122.9614 | 61.4259 | 122.7396 | 61.4431 | 61.4699 | 61.3835 | 61.4103
4.8906 | 123.143 | -61.4502 | 61.5738 | 0.021127 | -0.054257 | -0.012 | -0.011281 | 0.022531 | 0.00775 | 0.010533 | 61.441 | 0.12501 | 61.3905 | -0.08347 | 0.007032 | 61.5066 | -0.024328 | 61.2757 | 61.4713 | 61.3959 | 61.4382 | 61.4389 | 61.4727 | 61.4579 | 61.4607 | 122.8911 | 61.5752 | 122.8407 | 61.3667 | 61.4572 | 122.9568 | 61.4259 | 122.7259 | 61.4339 | 61.4653 | 61.3835 | 61.4149
5.8906 | 123.1476 | -61.4456 | 61.5875 | 0.025705 | -0.0451 | -0.007421 | -0.011281 | 0.022531 | 0.003172 | 0.015112 | 61.4455 | 0.12958 | 61.3905 | -0.08347 | 0.007032 | 61.5204 | -0.019749 | 61.2894 | 61.4713 | 61.4005 | 61.4382 | 61.4343 | 61.4681 | 61.4488 | 61.4607 | 122.8911 | 61.5752 | 122.8361 | 61.3621 | 61.4527 | 122.966 | 61.4259 | 122.735 | 61.4385 | 61.4653 | 61.3835 | 61.4103
6.8906 | 123.1705 | -61.441 | 61.5967 | 0.01197 | -0.040521 | -0.007421 | -0.006703 | 0.017953 | 0.012329 | 0.01969 | 61.4455 | 0.12501 | 61.3951 | -0.092628 | 0.01161 | 61.5112 | -0.024328 | 61.2848 | 61.453 | 61.4005 | 61.4336 | 61.4343 | 61.459 | 61.4534 | 61.4607 | 122.8866 | 61.566 | 122.8361 | 61.3484 | 61.4526 | 122.9523 | 61.4167 | 122.7259 | 61.4339 | 61.4699 | 61.3835 | 61.4194
7.8906 | 123.1567 | -61.4548 | 61.6058 | 0.016548 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.012329 | 0.015112 | 61.4501 | 0.12501 | 61.3951 | -0.088049 | 0.007032 | 61.5112 | -0.019749 | 61.2803 | 61.4713 | 61.4143 | 61.4382 | 61.4481 | 61.4819 | 61.4671 | 61.4699 | 122.9049 | 61.5798 | 122.8499 | 61.3667 | 61.4618 | 122.966 | 61.435 | 122.735 | 61.4431 | 61.4699 | 61.3881 | 61.4148
8.8906 | 123.2117 | -61.4136 | 61.5967 | 0.021127 | -0.040521 | -0.012 | -0.006703 | 0.027109 | 0.003172 | 0.01969 | 61.4501 | 0.12958 | 61.3905 | -0.088049 | 0.01161 | 61.5158 | -0.015171 | 61.2803 | 61.4347 | 61.3731 | 61.4016 | 61.4069 | 61.4407 | 61.4167 | 61.4333 | 122.8637 | 61.5432 | 122.8041 | 61.3255 | 61.4252 | 122.9294 | 61.3984 | 122.6938 | 61.4385 | 61.4653 | 61.3789 | 61.4057
9.8906 | 123.2117 | -61.4594 | 61.5738 | 0.025705 | -0.0451 | -0.012 | -0.011281 | 0.027109 | 0.012329 | 0.010533 | 61.4501 | 0.12958 | 61.3859 | -0.088049 | 0.007032 | 61.5112 | -0.028906 | 61.2803 | 61.4851 | 61.4143 | 61.4474 | 61.4481 | 61.4865 | 61.4717 | 61.4699 | 122.9095 | 61.5889 | 122.8453 | 61.3713 | 61.4664 | 122.9706 | 61.4304 | 122.7396 | 61.4431 | 61.479 | 61.3789 | 61.4149
10.8906 | 123.1934 | -61.4273 | 61.5738 | 0.016548 | -0.0451 | -0.012 | -0.011281 | 0.017953 | 0.016907 | 0.024268 | 61.4501 | 0.12958 | 61.3951 | -0.092628 | -0.002124 | 61.5158 | -0.024328 | 61.2894 | 61.4439 | 61.3822 | 61.4153 | 61.416 | 61.4453 | 61.4442 | 61.4516 | 122.8774 | 61.5569 | 122.8224 | 61.3347 | 61.4252 | 122.9431 | 61.403 | 122.7167 | 61.4522 | 61.4744 | 61.3972 | 61.4194
11.8906 | 123.1659 | -61.4456 | 61.5875 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.017953 | 0.003172 | 0.015112 | 61.4455 | 0.12501 | 61.3951 | -0.088049 | 0.007032 | 61.5158 | -0.015171 | 61.2894 | 61.4667 | 61.4005 | 61.429 | 61.4389 | 61.4636 | 61.4488 | 61.4607 | 122.8911 | 61.5706 | 122.8407 | 61.3576 | 61.4527 | 122.9614 | 61.4304 | 122.735 | 61.4385 | 61.4607 | 61.3881 | 61.4103
12.8906 | 123.2117 | -61.4319 | 61.615 | 0.01197 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.012329 | 0.024268 | 61.4455 | 0.12958 | 61.3951 | -0.08347 | 0.007032 | 61.5112 | -0.019749 | 61.2894 | 61.4439 | 61.3868 | 61.4245 | 61.4252 | 61.4544 | 61.4442 | 61.4562 | 122.8774 | 61.5615 | 122.827 | 61.3484 | 61.4389 | 122.9431 | 61.4121 | 122.7213 | 61.4385 | 61.4653 | 61.3881 | 61.4148
13.8906 | 123.2071 | -61.4365 | 61.5692 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.027109 | 0.021485 | 0.01969 | 61.4501 | 0.13416 | 61.3951 | -0.088049 | -0.002124 | 61.5066 | -0.019749 | 61.2848 | 61.453 | 61.3959 | 61.4245 | 61.4298 | 61.4636 | 61.4579 | 61.4562 | 122.8866 | 61.5706 | 122.8316 | 61.3484 | 61.4343 | 122.9431 | 61.4167 | 122.7213 | 61.4522 | 61.4699 | 61.3972 | 61.4148
14.8906 | 123.1613 | -61.4319 | 61.5875 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.015112 | 61.4455 | 0.13416 | 61.3905 | -0.08347 | -0.002124 | 61.5112 | -0.028906 | 61.2848 | 61.4484 | 61.3914 | 61.4199 | 61.4343 | 61.459 | 61.4396 | 61.447 | 122.8774 | 61.566 | 122.8224 | 61.3484 | 61.4298 | 122.9431 | 61.403 | 122.7167 | 61.4477 | 61.4744 | 61.3926 | 61.4194
15.8906 | 123.1705 | -61.4502 | 61.5692 | 0.025705 | -0.040521 | -0.007421 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4455 | 0.12501 | 61.3859 | -0.088049 | 0.007032 | 61.5112 | -0.019749 | 61.2848 | 61.4759 | 61.4097 | 61.4428 | 61.4435 | 61.4727 | 61.4625 | 61.4699 | 122.8957 | 61.5752 | 122.8361 | 61.3621 | 61.4572 | 122.9614 | 61.4304 | 122.735 | 61.4385 | 61.4653 | 61.3789 | 61.4057
16.8906 | 123.1888 | -61.4319 | 61.5601 | 0.016548 | -0.035942 | -0.007421 | -0.006703 | 0.027109 | 0.00775 | 0.015112 | 61.4455 | 0.13416 | 61.3905 | -0.092628 | 0.01161 | 61.5112 | -0.028906 | 61.2803 | 61.4484 | 61.3959 | 61.4245 | 61.4252 | 61.459 | 61.4396 | 61.447 | 122.8774 | 61.566 | 122.8224 | 61.3393 | 61.4435 | 122.9431 | 61.403 | 122.7121 | 61.4339 | 61.4744 | 61.3789 | 61.4194
17.8906 | 123.1155 | -61.4822 | 61.5463 | 0.01197 | -0.040521 | -0.012 | -0.006703 | 0.017953 | 0.012329 | 0.015112 | 61.4501 | 0.13416 | 61.3905 | -0.088049 | 0.002454 | 61.5112 | -0.019749 | 61.2803 | 61.4942 | 61.4417 | 61.4702 | 61.4755 | 61.5002 | 61.4946 | 61.4974 | 122.9323 | 61.6164 | 122.8728 | 61.3942 | 61.4847 | 122.9935 | 61.4625 | 122.7625 | 61.4477 | 61.4699 | 61.3881 | 61.4103
18.8906 | 123.1613 | -61.4136 | 61.5646 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.005955 | 61.4501 | 0.12958 | 61.3905 | -0.092628 | 0.002454 | 61.5158 | -0.024328 | 61.2894 | 61.4347 | 61.3731 | 61.397 | 61.4114 | 61.4407 | 61.4259 | 61.4195 | 122.8637 | 61.5432 | 122.8041 | 61.3209 | 61.416 | 122.9294 | 61.3892 | 122.703 | 61.4477 | 61.4744 | 61.3881 | 61.4149
19.8906 | 123.1842 | -61.4227 | 61.5692 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.4547 | 0.12958 | 61.3951 | -0.088049 | 0.002454 | 61.5204 | -0.024328 | 61.2894 | 61.4439 | 61.3822 | 61.4153 | 61.4252 | 61.4453 | 61.4351 | 61.4424 | 122.8774 | 61.5523 | 122.8178 | 61.3347 | 61.4252 | 122.9431 | 61.3984 | 122.7121 | 61.4522 | 61.479 | 61.3926 | 61.4194
20.8906 | 123.1613 | -61.4594 | 61.5509 | 0.016548 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | 0.016907 | 0.015112 | 61.4501 | 0.13416 | 61.3951 | -0.092628 | 0.002454 | 61.5158 | -0.028906 | 61.2848 | 61.4759 | 61.4188 | 61.4428 | 61.4481 | 61.4865 | 61.4763 | 61.4745 | 122.9095 | 61.5935 | 122.8545 | 61.3667 | 61.4618 | 122.9752 | 61.4304 | 122.7442 | 61.4477 | 61.479 | 61.3926 | 61.424
21.8906 | 123.111 | -61.4685 | 61.5692 | 0.021127 | -0.0451 | -0.007421 | -0.011281 | 0.022531 | 0.00775 | 0.015112 | 61.4501 | 0.12501 | 61.3997 | -0.088049 | 0.002454 | 61.5112 | -0.028906 | 61.2848 | 61.4896 | 61.4234 | 61.4611 | 61.4572 | 61.491 | 61.4763 | 61.4836 | 122.9186 | 61.5935 | 122.8682 | 61.3805 | 61.471 | 122.9797 | 61.4396 | 122.7533 | 61.4477 | 61.479 | 61.3972 | 61.4286
22.8906 | 123.1613 | -61.4639 | 61.5692 | 0.016548 | -0.0451 | -0.012 | -0.006703 | 0.022531 | 0.016907 | 0.01969 | 61.4455 | 0.12501 | 61.3951 | -0.092628 | 0.007032 | 61.5158 | -0.028906 | 61.2803 | 61.4805 | 61.4188 | 61.4519 | 61.4572 | 61.4865 | 61.4808 | 61.4836 | 122.9095 | 61.5889 | 122.859 | 61.3713 | 61.471 | 122.9797 | 61.435 | 122.7442 | 61.4385 | 61.4744 | 61.3881 | 61.424
23.8906 | 123.23 | -61.441 | 61.5509 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.015112 | 61.4455 | 0.12501 | 61.3951 | -0.092628 | 0.002454 | 61.5204 | -0.024328 | 61.2803 | 61.4667 | 61.3959 | 61.429 | 61.4343 | 61.4636 | 61.4488 | 61.4562 | 122.8866 | 61.566 | 122.8361 | 61.3484 | 61.4435 | 122.9614 | 61.4167 | 122.7213 | 61.4431 | 61.4699 | 61.3926 | 61.4194
24.8906 | 123.1064 | -61.5051 | 61.5234 | 0.016548 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.012329 | 0.015112 | 61.4501 | 0.13416 | 61.3905 | -0.088049 | -0.002124 | 61.5066 | -0.019749 | 61.2803 | 61.5217 | 61.46 | 61.4977 | 61.4984 | 61.5277 | 61.5175 | 61.5202 | 122.9552 | 61.6393 | 122.8957 | 61.4171 | 61.503 | 123.0118 | 61.4854 | 122.7854 | 61.4522 | 61.4699 | 61.3926 | 61.4103
25.8906 | 123.1201 | -61.441 | 61.5784 | 0.021127 | -0.049678 | -0.016578 | -0.006703 | 0.017953 | 0.012329 | 0.015112 | 61.4547 | 0.12043 | 61.3905 | -0.088049 | 0.002454 | 61.5066 | -0.028906 | 61.2848 | 61.4622 | 61.3914 | 61.4245 | 61.4343 | 61.459 | 61.4534 | 61.4562 | 122.8957 | 61.5615 | 122.8316 | 61.353 | 61.4435 | 122.9477 | 61.4121 | 122.7259 | 61.4522 | 61.4836 | 61.3881 | 61.4194
26.8906 | 123.1842 | -61.4456 | 61.5875 | 0.021127 | -0.040521 | -0.007421 | -0.006703 | 0.022531 | 0.012329 | 0.024268 | 61.4501 | 0.12501 | 61.3951 | -0.08347 | 0.002454 | 61.5112 | -0.028906 | 61.2894 | 61.4667 | 61.4051 | 61.4382 | 61.4389 | 61.4681 | 61.4579 | 61.4699 | 122.8957 | 61.5706 | 122.8407 | 61.3621 | 61.4481 | 122.9568 | 61.4167 | 122.735 | 61.4477 | 61.479 | 61.3926 | 61.424
27.8906 | 123.1613 | -61.4822 | 61.5509 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.022531 | 0.00775 | 0.024268 | 61.4501 | 0.12958 | 61.3859 | -0.088049 | -0.006702 | 61.5066 | -0.024328 | 61.2803 | 61.4988 | 61.4371 | 61.4657 | 61.4801 | 61.5048 | 61.49 | 61.5065 | 122.9323 | 61.6118 | 122.8682 | 61.3942 | 61.4755 | 122.9889 | 61.4579 | 122.7625 | 61.4568 | 61.4744 | 61.3926 | 61.4103
28.8906 | 123.2941 | -61.3953 | 61.5372 | 0.016548 | -0.0451 | -0.016578 | -0.011281 | 0.027109 | 0.003172 | 0.015112 | 61.441 | 0.12958 | 61.3951 | -0.088049 | 0.002454 | 61.5112 | -0.015171 | 61.2848 | 61.4118 | 61.3502 | 61.3787 | 61.384 | 61.4224 | 61.3984 | 61.4104 | 122.8362 | 61.5248 | 122.7904 | 61.3072 | 61.3977 | 122.9065 | 61.3801 | 122.6801 | 61.4385 | 61.4561 | 61.3926 | 61.4103
29.8906 | 123.2071 | -61.441 | 61.5372 | 0.016548 | -0.0451 | -0.002842 | -0.002124 | 0.022531 | 0.016907 | 0.015112 | 61.4501 | 0.13416 | 61.3951 | -0.088049 | 0.002454 | 61.5112 | -0.024328 | 61.2848 | 61.4576 | 61.3959 | 61.4382 | 61.4389 | 61.4636 | 61.4579 | 61.4562 | 122.8911 | 61.5752 | 122.8361 | 61.353 | 61.4435 | 122.9523 | 61.4167 | 122.7259 | 61.4477 | 61.4744 | 61.3926 | 61.4194
30.8906 | 123.1705 | -61.4319 | 61.528 | 0.021127 | -0.040521 | -0.007421 | -0.011281 | 0.017953 | 0.012329 | 0.015112 | 61.4501 | 0.13416 | 61.3905 | -0.088049 | 0.007032 | 61.5112 | -0.024328 | 61.2848 | 61.453 | 61.3914 | 61.4245 | 61.4206 | 61.4498 | 61.4442 | 61.447 | 122.882 | 61.566 | 122.8224 | 61.3438 | 61.4389 | 122.9431 | 61.4076 | 122.7167 | 61.4431 | 61.4744 | 61.3835 | 61.4149
31.8906 | 123.1796 | -61.4685 | 61.5372 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.012329 | 0.010533 | 61.4501 | 0.12501 | 61.3905 | -0.088049 | 0.007032 | 61.5021 | -0.024328 | 61.2848 | 61.4851 | 61.428 | 61.4565 | 61.4618 | 61.491 | 61.4808 | 61.479 | 122.9186 | 61.5935 | 122.859 | 61.3805 | 61.4755 | 122.9706 | 61.4442 | 122.7533 | 61.4431 | 61.4744 | 61.3835 | 61.4149
32.8906 | 123.2162 | -61.4594 | 61.5417 | 0.01197 | -0.0451 | -0.007421 | -0.006703 | 0.027109 | 0.016907 | 0.015112 | 61.441 | 0.13416 | 61.3859 | -0.097207 | -0.002124 | 61.5066 | -0.028906 | 61.2803 | 61.4713 | 61.4143 | 61.4519 | 61.4526 | 61.4865 | 61.4763 | 61.4745 | 122.9003 | 61.5935 | 122.8453 | 61.3621 | 61.4572 | 122.966 | 61.4304 | 122.7396 | 61.4431 | 61.4699 | 61.3881 | 61.4149
33.8906 | 123.2254 | -61.4456 | 61.5234 | 0.01197 | -0.040521 | -0.012 | -0.01586 | 0.022531 | 0.00775 | 0.010533 | 61.4501 | 0.12501 | 61.3905 | -0.08347 | -0.002124 | 61.5158 | -0.015171 | 61.2803 | 61.4576 | 61.4051 | 61.4336 | 61.4298 | 61.4681 | 61.4534 | 61.4562 | 122.8957 | 61.5706 | 122.8361 | 61.3621 | 61.4435 | 122.9614 | 61.4304 | 122.7259 | 61.4522 | 61.4653 | 61.3926 | 61.4057
34.8906 | 123.2025 | -61.4319 | 61.5417 | 0.021127 | -0.040521 | -0.012 | -0.011281 | 0.027109 | 0.012329 | 0.015112 | 61.4501 | 0.12501 | 61.3997 | -0.092628 | 0.002454 | 61.5112 | -0.019749 | 61.2848 | 61.453 | 61.3914 | 61.4199 | 61.4206 | 61.459 | 61.4442 | 61.447 | 122.882 | 61.5569 | 122.8316 | 61.3393 | 61.4343 | 122.9431 | 61.4121 | 122.7167 | 61.4477 | 61.4699 | 61.3972 | 61.4194
35.8906 | 123.2574 | -61.4227 | 61.5143 | 0.021127 | -0.0451 | -0.012 | -0.006703 | 0.017953 | 0.012329 | 0.01969 | 61.4501 | 0.13416 | 61.4043 | -0.092628 | 0.002454 | 61.5066 | -0.015171 | 61.2803 | 61.4439 | 61.3776 | 61.4107 | 61.416 | 61.4407 | 61.4351 | 61.4424 | 122.8728 | 61.5569 | 122.827 | 61.3301 | 61.4252 | 122.9294 | 61.4076 | 122.703 | 61.4477 | 61.4653 | 61.4018 | 61.4194
36.8906 | 123.3124 | -61.409 | 61.528 | 0.01197 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.016907 | 0.015112 | 61.4455 | 0.12501 | 61.3905 | -0.088049 | 0.007032 | 61.5204 | -0.024328 | 61.2757 | 61.421 | 61.3639 | 61.4016 | 61.4023 | 61.4315 | 61.4259 | 61.4241 | 122.8545 | 61.534 | 122.7995 | 61.3209 | 61.416 | 122.9294 | 61.3847 | 122.6847 | 61.4385 | 61.4699 | 61.3835 | 61.4149
37.8906 | 123.2483 | -61.4227 | 61.5234 | 0.016548 | -0.040521 | -0.016578 | -0.011281 | 0.022531 | 0.012329 | 0.015112 | 61.4547 | 0.12958 | 61.3951 | -0.092628 | -0.002124 | 61.5112 | -0.024328 | 61.2803 | 61.4393 | 61.3822 | 61.4062 | 61.4114 | 61.4453 | 61.4351 | 61.4378 | 122.8774 | 61.5523 | 122.8178 | 61.3301 | 61.4206 | 122.934 | 61.3984 | 122.703 | 61.4568 | 61.479 | 61.3972 | 61.4194
38.8906 | 123.2529 | -61.4182 | 61.5555 | 0.016548 | -0.040521 | -0.012 | -0.011281 | 0.017953 | 0.00775 | 0.015112 | 61.4501 | 0.12958 | 61.3951 | -0.092628 | 0.002454 | 61.5021 | -0.019749 | 61.2848 | 61.4347 | 61.3776 | 61.4062 | 61.4069 | 61.4361 | 61.4259 | 61.4333 | 122.8683 | 61.5477 | 122.8133 | 61.3255 | 61.4206 | 122.9202 | 61.3984 | 122.703 | 61.4477 | 61.4699 | 61.3926 | 61.4148
39.8906 | 123.2391 | -61.4227 | 61.5189 | 0.016548 | -0.0451 | -0.012 | -0.006703 | 0.017953 | 0.012329 | 0.015112 | 61.4547 | 0.12958 | 61.3951 | -0.088049 | 0.002454 | 61.5112 | -0.019749 | 61.2803 | 61.4393 | 61.3776 | 61.4107 | 61.416 | 61.4407 | 61.4351 | 61.4378 | 122.8774 | 61.5523 | 122.8178 | 61.3347 | 61.4252 | 122.934 | 61.403 | 122.703 | 61.4522 | 61.4744 | 61.3926 | 61.4148
40.8906 | 123.2758 | -61.441 | 61.5234 | 0.016548 | -0.049678 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4455 | 0.13874 | 61.3951 | -0.092628 | 0.007032 | 61.5066 | -0.028906 | 61.2894 | 61.4576 | 61.3914 | 61.4245 | 61.4389 | 61.4681 | 61.4534 | 61.4607 | 122.8866 | 61.5798 | 122.8361 | 61.3484 | 61.4481 | 122.9477 | 61.4121 | 122.7305 | 61.4385 | 61.4744 | 61.3881 | 61.424
41.8906 | 123.2712 | -61.4365 | 61.528 | 0.021127 | -0.035942 | -0.016578 | -0.011281 | 0.013375 | 0.021485 | 0.015112 | 61.4501 | 0.12958 | 61.3951 | -0.092628 | -0.002124 | 61.5066 | -0.024328 | 61.2803 | 61.4576 | 61.4005 | 61.4199 | 61.4252 | 61.4498 | 61.4579 | 61.4516 | 122.8866 | 61.566 | 122.8316 | 61.3438 | 61.4343 | 122.9431 | 61.4121 | 122.7167 | 61.4522 | 61.4744 | 61.3972 | 61.4194
42.8906 | 123.2437 | -61.4227 | 61.5234 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | 0.012329 | 0.015112 | 61.4455 | 0.12958 | 61.3905 | -0.088049 | 0.007032 | 61.5158 | -0.015171 | 61.2757 | 61.4439 | 61.3822 | 61.4062 | 61.4114 | 61.4498 | 61.4351 | 61.4378 | 122.8683 | 61.5523 | 122.8133 | 61.3347 | 61.4298 | 122.9385 | 61.4076 | 122.6984 | 61.4385 | 61.4607 | 61.3835 | 61.4057
43.8906 | 123.2712 | -61.4182 | 61.5234 | 0.016548 | -0.035942 | -0.012 | -0.006703 | 0.022531 | 0.012329 | 0.005955 | 61.4501 | 0.12958 | 61.3859 | -0.08347 | 0.002454 | 61.5112 | -0.019749 | 61.2848 | 61.4347 | 61.3822 | 61.4062 | 61.4114 | 61.4407 | 61.4305 | 61.4241 | 122.8683 | 61.5477 | 122.8041 | 61.3347 | 61.4206 | 122.9294 | 61.3984 | 122.703 | 61.4477 | 61.4699 | 61.3835 | 61.4057
44.8906 | 123.23 | -61.4273 | 61.528 | 0.021127 | -0.049678 | -0.007421 | -0.01586 | 0.017953 | 0.012329 | 0.005955 | 61.4501 | 0.12958 | 61.3997 | -0.088049 | 0.002454 | 61.5158 | -0.019749 | 61.2803 | 61.4484 | 61.3776 | 61.4199 | 61.4114 | 61.4453 | 61.4396 | 61.4333 | 122.8774 | 61.5569 | 122.827 | 61.3393 | 61.4298 | 122.9431 | 61.4076 | 122.7076 | 61.4477 | 61.4699 | 61.3972 | 61.4194
45.8906 | 123.2254 | -61.4273 | 61.5143 | 0.021127 | -0.035942 | -0.012 | -0.006703 | 0.027109 | 0.012329 | 0.010533 | 61.4501 | 0.12958 | 61.3951 | -0.088049 | 0.002454 | 61.5112 | -0.024328 | 61.2848 | 61.4484 | 61.3914 | 61.4153 | 61.4206 | 61.4544 | 61.4396 | 61.4378 | 122.8774 | 61.5569 | 122.8224 | 61.3393 | 61.4298 | 122.9385 | 61.403 | 122.7121 | 61.4477 | 61.4744 | 61.3926 | 61.4194
46.8906 | 123.2758 | -61.4227 | 61.528 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.008797 | 0.00775 | 0.015112 | 61.4501 | 0.12958 | 61.3951 | -0.08347 | -0.002124 | 61.5158 | -0.019749 | 61.2848 | 61.4393 | 61.3776 | 61.4107 | 61.4206 | 61.4315 | 61.4305 | 61.4378 | 122.8728 | 61.5523 | 122.8178 | 61.3393 | 61.4206 | 122.9385 | 61.403 | 122.7076 | 61.4522 | 61.4699 | 61.3972 | 61.4148
47.8906 | 123.2986 | -61.3998 | 61.5646 | 0.021127 | -0.049678 | -0.016578 | -0.011281 | 0.022531 | 0.00775 | 0.010533 | 61.4501 | 0.12958 | 61.3951 | -0.092628 | 0.002454 | 61.5112 | -0.024328 | 61.2803 | 61.421 | 61.3502 | 61.3833 | 61.3886 | 61.4224 | 61.4076 | 61.4104 | 122.8499 | 61.5294 | 122.7949 | 61.3072 | 61.4023 | 122.9111 | 61.3755 | 122.6801 | 61.4477 | 61.4744 | 61.3926 | 61.4194
48.8906 | 123.2025 | -61.441 | 61.5372 | 0.021127 | -0.0451 | -0.016578 | -0.011281 | 0.022531 | 0.003172 | 0.010533 | 61.4501 | 0.12958 | 61.3951 | -0.08347 | -0.002124 | 61.5158 | -0.019749 | 61.2757 | 61.4622 | 61.3959 | 61.4245 | 61.4298 | 61.4636 | 61.4442 | 61.4516 | 122.8911 | 61.5706 | 122.8361 | 61.3576 | 61.4389 | 122.9568 | 61.4213 | 122.7167 | 61.4522 | 61.4699 | 61.3972 | 61.4148
49.8906 | 123.2529 | -61.4227 | 61.5509 | 0.016548 | -0.054257 | -0.016578 | -0.006703 | 0.022531 | -0.001406 | 0.005955 | 61.4547 | 0.13416 | 61.3905 | -0.088049 | 0.007032 | 61.5158 | -0.019749 | 61.2803 | 61.4393 | 61.3685 | 61.4062 | 61.416 | 61.4453 | 61.4213 | 61.4287 | 122.8774 | 61.5569 | 122.8133 | 61.3347 | 61.4298 | 122.9385 | 61.403 | 122.703 | 61.4477 | 61.4744 | 61.3835 | 61.4103
50.8906 | 123.2574 | -61.4273 | 61.5234 | 0.021127 | -0.0451 | -0.025735 | -0.002124 | 0.022531 | 0.003172 | 0.015112 | 61.4501 | 0.13416 | 61.3951 | -0.08347 | 0.01161 | 61.5066 | -0.019749 | 61.2848 | 61.4484 | 61.3822 | 61.4016 | 61.4252 | 61.4498 | 61.4305 | 61.4424 | 122.8774 | 61.5615 | 122.8224 | 61.3438 | 61.4389 | 122.934 | 61.4076 | 122.7121 | 61.4385 | 61.4699 | 61.3835 | 61.4148
51.8906 | 123.2071 | -61.4319 | 61.5417 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.017953 | 0.00775 | 0.015112 | 61.4501 | 0.13874 | 61.3905 | -0.092628 | 0.002454 | 61.5112 | -0.024328 | 61.2848 | 61.453 | 61.3914 | 61.4199 | 61.4298 | 61.4498 | 61.4396 | 61.447 | 122.882 | 61.5706 | 122.8224 | 61.3393 | 61.4343 | 122.9431 | 61.4076 | 122.7167 | 61.4477 | 61.4744 | 61.3881 | 61.4149
52.8906 | 123.2117 | -61.441 | 61.5692 | 0.021127 | -0.049678 | -0.016578 | -0.006703 | 0.031687 | 0.012329 | 0.015112 | 61.4547 | 0.13416 | 61.3997 | -0.088049 | 0.002454 | 61.5158 | -0.024328 | 61.2894 | 61.4622 | 61.3914 | 61.4245 | 61.4343 | 61.4727 | 61.4534 | 61.4562 | 122.8957 | 61.5752 | 122.8407 | 61.353 | 61.4435 | 122.9568 | 61.4167 | 122.7305 | 61.4522 | 61.479 | 61.3972 | 61.424
53.8906 | 123.2117 | -61.4365 | 61.5326 | 0.016548 | -0.0451 | -0.007421 | -0.011281 | 0.022531 | 0.012329 | 0.015112 | 61.4501 | 0.12958 | 61.3905 | -0.088049 | -0.002124 | 61.5066 | -0.019749 | 61.2894 | 61.453 | 61.3914 | 61.429 | 61.4252 | 61.459 | 61.4488 | 61.4516 | 122.8866 | 61.566 | 122.827 | 61.3484 | 61.4343 | 122.9431 | 61.4167 | 122.7259 | 61.4522 | 61.4699 | 61.3926 | 61.4103
54.8906 | 123.2437 | -61.441 | 61.5143 | 0.016548 | -0.0451 | -0.012 | -0.011281 | 0.022531 | 0.003172 | 0.015112 | 61.4501 | 0.12958 | 61.3905 | -0.08347 | 0.002454 | 61.5112 | -0.019749 | 61.294 | 61.4576 | 61.3959 | 61.429 | 61.4298 | 61.4636 | 61.4442 | 61.4562 | 122.8911 | 61.5706 | 122.8316 | 61.3576 | 61.4435 | 122.9523 | 61.4213 | 122.735 | 61.4477 | 61.4699 | 61.3881 | 61.4103
55.8906 | 123.2437 | -61.4456 | 61.5463 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | 0.00775 | 0.015112 | 61.4501 | 0.13416 | 61.3905 | -0.08347 | 0.007032 | 61.5112 | -0.028906 | 61.294 | 61.4667 | 61.4051 | 61.429 | 61.4343 | 61.4636 | 61.4534 | 61.4607 | 122.8957 | 61.5798 | 122.8361 | 61.3621 | 61.4527 | 122.9568 | 61.4167 | 122.7396 | 61.4431 | 61.479 | 61.3835 | 61.4194
56.8906 | 123.2758 | -61.4319 | 61.5417 | 0.016548 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | 0.00775 | 0.010533 | 61.4501 | 0.13416 | 61.3951 | -0.092628 | 0.002454 | 61.5112 | -0.024328 | 61.2848 | 61.4484 | 61.3868 | 61.4153 | 61.4252 | 61.459 | 61.4396 | 61.4424 | 122.882 | 61.566 | 122.827 | 61.3393 | 61.4343 | 122.9431 | 61.4076 | 122.7167 | 61.4477 | 61.4744 | 61.3926 | 61.4194
57.8906 | 123.2437 | -61.4136 | 61.5051 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.00775 | 0.01969 | 61.4593 | 0.12958 | 61.3951 | -0.092628 | 0.007032 | 61.5158 | -0.024328 | 61.2848 | 61.4347 | 61.3731 | 61.4016 | 61.4114 | 61.4361 | 61.4213 | 61.4333 | 122.8728 | 61.5432 | 122.8087 | 61.3209 | 61.4206 | 122.9294 | 61.3892 | 122.6984 | 61.4522 | 61.4836 | 61.3881 | 61.4194
58.8906 | 123.2574 | -61.4227 | 61.528 | 0.016548 | -0.0451 | -0.021157 | -0.002124 | 0.022531 | 0.00775 | 0.015112 | 61.4547 | 0.12958 | 61.3997 | -0.088049 | 0.002454 | 61.5112 | -0.024328 | 61.2848 | 61.4393 | 61.3776 | 61.4016 | 61.4206 | 61.4453 | 61.4305 | 61.4378 | 122.8774 | 61.5523 | 122.8224 | 61.3347 | 61.4252 | 122.934 | 61.3984 | 122.7076 | 61.4522 | 61.479 | 61.3972 | 61.424
59.8906 | 123.2849 | -61.4273 | 61.5189 | 0.025705 | -0.049678 | -0.016578 | -0.01586 | 0.022531 | 0.012329 | 0.015112 | 61.4593 | 0.12958 | 61.3951 | -0.08347 | 0.002454 | 61.5158 | -0.019749 | 61.2848 | 61.453 | 61.3776 | 61.4107 | 61.4114 | 61.4498 | 61.4396 | 61.4424 | 122.8866 | 61.5569 | 122.8224 | 61.3438 | 61.4298 | 122.9431 | 61.4076 | 122.7121 | 61.4568 | 61.479 | 61.3926 | 61.4148
60.8906 | 123.3078 | -61.3998 | 61.5372 | 0.021127 | -0.049678 | -0.016578 | -0.01586 | 0.017953 | 0.003172 | 0.01969 | 61.4547 | 0.13416 | 61.3997 | -0.092628 | 0.002454 | 61.5112 | -0.015171 | 61.2894 | 61.421 | 61.3502 | 61.3833 | 61.384 | 61.4178 | 61.403 | 61.4195 | 122.8545 | 61.534 | 122.7995 | 61.3072 | 61.4023 | 122.9111 | 61.3847 | 122.6893 | 61.4522 | 61.4699 | 61.3972 | 61.4149
61.8906 | 123.2666 | -61.4182 | 61.5509 | 0.025705 | -0.049678 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.015112 | 61.4593 | 0.12501 | 61.3905 | -0.088049 | 0.002454 | 61.5112 | -0.024328 | 61.2848 | 61.4439 | 61.3685 | 61.4062 | 61.4114 | 61.4407 | 61.4259 | 61.4333 | 122.8774 | 61.5432 | 122.8087 | 61.3301 | 61.4206 | 122.9294 | 61.3938 | 122.703 | 61.4568 | 61.4836 | 61.3881 | 61.4149
62.9062 | 123.1979 | -61.4639 | 61.528 | 0.016548 | -0.0451 | -0.007421 | -0.011281 | 0.022531 | 0.012329 | 0.010533 | 61.4547 | 0.13416 | 61.3951 | -0.092628 | 0.007032 | 61.5112 | -0.015171 | 61.2848 | 61.4805 | 61.4188 | 61.4565 | 61.4526 | 61.4865 | 61.4763 | 61.4745 | 122.9186 | 61.5981 | 122.859 | 61.3713 | 61.471 | 122.9752 | 61.4488 | 122.7488 | 61.4477 | 61.4699 | 61.3881 | 61.4103
63.8906 | 123.2208 | -61.4227 | 61.5372 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.017953 | 0.00775 | 0.015112 | 61.4593 | 0.12958 | 61.3951 | -0.08347 | 0.002454 | 61.5204 | -0.024328 | 61.294 | 61.4393 | 61.3822 | 61.4107 | 61.416 | 61.4407 | 61.4305 | 61.4378 | 122.882 | 61.5523 | 122.8178 | 61.3393 | 61.4252 | 122.9431 | 61.3984 | 122.7167 | 61.4568 | 61.4836 | 61.3926 | 61.4194
64.8906 | 123.2666 | -61.4273 | 61.5372 | 0.025705 | -0.0451 | -0.012 | -0.011281 | 0.022531 | 0.00775 | 0.010533 | 61.4547 | 0.12958 | 61.3997 | -0.08347 | 0.01161 | 61.5021 | -0.024328 | 61.294 | 61.453 | 61.3822 | 61.4153 | 61.416 | 61.4498 | 61.4351 | 61.4378 | 122.882 | 61.5569 | 122.827 | 61.3438 | 61.4389 | 122.9294 | 61.403 | 122.7213 | 61.4431 | 61.479 | 61.3881 | 61.424
65.8906 | 123.2483 | -61.4044 | 61.5555 | 0.025705 | -0.0451 | -0.012 | -0.011281 | 0.027109 | 0.00775 | 0.01969 | 61.4501 | 0.12958 | 61.3997 | -0.092628 | 0.002454 | 61.5112 | -0.024328 | 61.2894 | 61.4301 | 61.3593 | 61.3924 | 61.3931 | 61.4315 | 61.4122 | 61.4241 | 122.8545 | 61.534 | 122.8041 | 61.3118 | 61.4069 | 122.9156 | 61.3801 | 122.6938 | 61.4477 | 61.4744 | 61.3972 | 61.424
66.8906 | 123.1979 | -61.4136 | 61.5967 | 0.021127 | -0.0451 | -0.012 | -0.006703 | 0.017953 | 0.016907 | 0.01969 | 61.4501 | 0.13416 | 61.3951 | -0.097207 | 0.007032 | 61.5158 | -0.015171 | 61.2848 | 61.4347 | 61.3685 | 61.4016 | 61.4069 | 61.4315 | 61.4305 | 61.4333 | 122.8637 | 61.5477 | 122.8087 | 61.3164 | 61.4206 | 122.9294 | 61.3984 | 122.6984 | 61.4431 | 61.4653 | 61.3881 | 61.4103
67.9062 | 123.1522 | -61.4456 | 61.5967 | 0.021127 | -0.049678 | -0.007421 | -0.006703 | 0.027109 | 0.012329 | 0.01969 | 61.4547 | 0.12958 | 61.3905 | -0.10179 | 0.01161 | 61.525 | -0.024328 | 61.2894 | 61.4667 | 61.3959 | 61.4382 | 61.4389 | 61.4727 | 61.4579 | 61.4653 | 122.9003 | 61.5752 | 122.8361 | 61.3438 | 61.4572 | 122.9706 | 61.4213 | 122.735 | 61.4431 | 61.479 | 61.3789 | 61.4149
68.8906 | 123.2117 | -61.409 | 61.5738 | 0.021127 | -0.049678 | -0.012 | -0.006703 | 0.017953 | 0.00775 | 0.010533 | 61.4547 | 0.12958 | 61.3997 | -0.092628 | 0.007032 | 61.5158 | -0.028906 | 61.294 | 61.4301 | 61.3593 | 61.397 | 61.4023 | 61.4269 | 61.4167 | 61.4195 | 122.8637 | 61.5386 | 122.8087 | 61.3164 | 61.416 | 122.9248 | 61.3801 | 122.703 | 61.4477 | 61.4836 | 61.3926 | 61.4286
69.8906 | 123.175 | -61.4365 | 61.5829 | 0.016548 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.016907 | 0.01969 | 61.4593 | 0.13416 | 61.3997 | -0.088049 | 0.002454 | 61.5158 | -0.015171 | 61.2848 | 61.453 | 61.3914 | 61.429 | 61.4298 | 61.459 | 61.4534 | 61.4562 | 122.8957 | 61.5706 | 122.8361 | 61.3484 | 61.4389 | 122.9523 | 61.4213 | 122.7213 | 61.4568 | 61.4744 | 61.3972 | 61.4149
70.8906 | 123.1338 | -61.4319 | 61.5875 | 0.021127 | -0.0451 | -0.007421 | -0.006703 | 0.017953 | 0.016907 | 0.015112 | 61.4501 | 0.13416 | 61.3951 | -0.092628 | -0.002124 | 61.5158 | -0.024328 | 61.2848 | 61.453 | 61.3868 | 61.4245 | 61.4252 | 61.4498 | 61.4488 | 61.447 | 122.882 | 61.566 | 122.827 | 61.3393 | 61.4298 | 122.9477 | 61.4076 | 122.7167 | 61.4522 | 61.4744 | 61.3972 | 61.4194
71.8906 | 123.2254 | -61.4319 | 61.5738 | 0.021127 | -0.0451 | -0.007421 | -0.002124 | 0.027109 | 0.00775 | 0.015112 | 61.4547 | 0.12958 | 61.3997 | -0.08347 | 0.002454 | 61.5112 | -0.019749 | 61.2848 | 61.453 | 61.3868 | 61.4245 | 61.4298 | 61.459 | 61.4396 | 61.447 | 122.8866 | 61.5615 | 122.8316 | 61.3484 | 61.4343 | 122.9431 | 61.4121 | 122.7167 | 61.4522 | 61.4744 | 61.3972 | 61.4194
72.8906 | 123.2849 | -61.3861 | 61.5417 | 0.021127 | -0.049678 | -0.007421 | -0.006703 | 0.022531 | 0.003172 | 0.010533 | 61.4547 | 0.12958 | 61.3951 | -0.08347 | 0.007032 | 61.5112 | -0.019749 | 61.2803 | 61.4072 | 61.3364 | 61.3787 | 61.3794 | 61.4086 | 61.3893 | 61.3966 | 122.8408 | 61.5157 | 122.7812 | 61.3026 | 61.3931 | 122.8973 | 61.3664 | 122.6664 | 61.4477 | 61.4744 | 61.3881 | 61.4148
73.8906 | 123.1705 | -61.4273 | 61.5921 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.015112 | 61.4501 | 0.12958 | 61.3997 | -0.10179 | 0.007032 | 61.5112 | -0.033484 | 61.2803 | 61.4484 | 61.3822 | 61.4153 | 61.4252 | 61.459 | 61.4351 | 61.4424 | 122.8774 | 61.5569 | 122.827 | 61.3255 | 61.4343 | 122.9385 | 61.3938 | 122.7076 | 61.4431 | 61.4836 | 61.3926 | 61.4332
74.8906 | 123.2529 | -61.4456 | 61.528 | 0.021127 | -0.031363 | -0.016578 | -0.006703 | 0.027109 | 0.012329 | 0.010533 | 61.4867 | 0.12958 | 61.4317 | -0.055996 | 0.007032 | 61.5158 | -0.024328 | 61.3169 | 61.4667 | 61.4143 | 61.429 | 61.4389 | 61.4727 | 61.4579 | 61.4562 | 122.9324 | 61.5752 | 122.8773 | 61.3896 | 61.4527 | 122.9614 | 61.4213 | 122.7625 | 61.4797 | 61.5111 | 61.4247 | 61.4561
75.8906 | 123.2437 | -61.4273 | 61.6058 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.031687 | 0.012329 | 0.028846 | 61.4822 | 0.13416 | 61.4226 | -0.046838 | 0.01161 | 61.5066 | -0.019749 | 61.3169 | 61.453 | 61.3822 | 61.4153 | 61.4206 | 61.459 | 61.4396 | 61.4562 | 122.9095 | 61.5615 | 122.8499 | 61.3805 | 61.4389 | 122.934 | 61.4076 | 122.7442 | 61.4705 | 61.5019 | 61.411 | 61.4423
76.8906 | 123.1796 | -61.409 | 61.5784 | 0.025705 | -0.035942 | -0.012 | -0.006703 | 0.031687 | 0.016907 | 0.01969 | 61.4822 | 0.13416 | 61.4317 | -0.046838 | 0.007032 | 61.5158 | -0.024328 | 61.3215 | 61.4347 | 61.3731 | 61.397 | 61.4023 | 61.4407 | 61.4259 | 61.4287 | 122.8912 | 61.5432 | 122.8407 | 61.3622 | 61.416 | 122.9248 | 61.3847 | 122.7305 | 61.4751 | 61.5065 | 61.4247 | 61.4561
77.8906 | 123.1705 | -61.4319 | 61.5875 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.040843 | 0.016907 | 0.024268 | 61.4867 | 0.12958 | 61.4317 | -0.055996 | 0.002454 | 61.5204 | -0.019749 | 61.326 | 61.453 | 61.3868 | 61.4199 | 61.4298 | 61.4727 | 61.4488 | 61.4562 | 122.9186 | 61.5615 | 122.8636 | 61.3759 | 61.4343 | 122.9523 | 61.4121 | 122.7579 | 61.4843 | 61.5065 | 61.4293 | 61.4515
78.8906 | 123.2208 | -61.441 | 61.5601 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.040843 | 0.021485 | 0.028846 | 61.4913 | 0.13416 | 61.4317 | -0.051417 | 0.007032 | 61.5158 | -0.019749 | 61.3215 | 61.4713 | 61.4005 | 61.429 | 61.4389 | 61.4819 | 61.4625 | 61.4699 | 122.9324 | 61.5752 | 122.8728 | 61.3896 | 61.4481 | 122.9568 | 61.4213 | 122.7625 | 61.4843 | 61.5111 | 61.4247 | 61.4515
79.8906 | 123.1842 | -61.4502 | 61.5646 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.028846 | 61.4867 | 0.13416 | 61.4317 | -0.046838 | 0.007032 | 61.5158 | -0.019749 | 61.3306 | 61.4805 | 61.4051 | 61.4382 | 61.4526 | 61.4865 | 61.4625 | 61.479 | 122.9369 | 61.5844 | 122.8819 | 61.4034 | 61.4572 | 122.966 | 61.4304 | 122.7808 | 61.4797 | 61.5065 | 61.4247 | 61.4515
80.8906 | 123.1888 | -61.441 | 61.5784 | 0.034862 | -0.0451 | -0.007421 | 0.002454 | 0.036265 | 0.021485 | 0.028846 | 61.5096 | 0.12958 | 61.4409 | -0.055996 | 0.016188 | 61.5204 | -0.033484 | 61.3215 | 61.4759 | 61.3959 | 61.4336 | 61.4435 | 61.4773 | 61.4625 | 61.4699 | 122.9507 | 61.5706 | 122.8819 | 61.385 | 61.4572 | 122.9614 | 61.4076 | 122.7625 | 61.4934 | 61.5431 | 61.4247 | 61.4744
81.8906 | 123.1613 | -61.441 | 61.5875 | 0.034862 | -0.049678 | -0.021157 | 0.007033 | 0.040843 | 0.021485 | 0.01969 | 61.5005 | 0.13416 | 61.4455 | -0.088049 | 0.01161 | 61.5158 | -0.042641 | 61.3169 | 61.4759 | 61.3914 | 61.4199 | 61.4481 | 61.4819 | 61.4625 | 61.4607 | 122.9415 | 61.5752 | 122.8865 | 61.353 | 61.4526 | 122.9568 | 61.3984 | 122.7579 | 61.4889 | 61.5431 | 61.4339 | 61.4881
82.8906 | 123.1613 | -61.4594 | 61.5417 | 0.025705 | -0.031363 | -0.007421 | -0.006703 | 0.040843 | 0.016907 | 0.028846 | 61.4959 | 0.13416 | 61.4409 | -0.092628 | 0.002454 | 61.5158 | -0.028906 | 61.3077 | 61.4851 | 61.428 | 61.4519 | 61.4526 | 61.5002 | 61.4763 | 61.4882 | 122.9552 | 61.5935 | 122.9002 | 61.3667 | 61.4618 | 122.9752 | 61.4304 | 122.7671 | 61.4934 | 61.5248 | 61.4384 | 61.4698
83.8906 | 123.1293 | -61.4456 | 61.5784 | 0.030283 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.016907 | 0.01969 | 61.4913 | 0.14332 | 61.4363 | -0.042259 | 0.007032 | 61.5158 | -0.028906 | 61.3123 | 61.4759 | 61.4051 | 61.4336 | 61.4435 | 61.4727 | 61.4625 | 61.4653 | 122.9369 | 61.5889 | 122.8819 | 61.4034 | 61.4527 | 122.9614 | 61.4167 | 122.7579 | 61.4843 | 61.5202 | 61.4293 | 61.4652
84.8906 | 123.175 | -61.4731 | 61.5509 | 0.016548 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.012329 | 0.024268 | 61.473 | 0.13416 | 61.418 | -0.060575 | 0.007032 | 61.5158 | -0.065533 | 61.3123 | 61.4896 | 61.428 | 61.4611 | 61.4664 | 61.5002 | 61.4854 | 61.4974 | 122.9461 | 61.6072 | 122.8911 | 61.4125 | 61.4801 | 122.9889 | 61.4076 | 122.7854 | 61.466 | 61.5385 | 61.411 | 61.4835
85.8906 | 123.1934 | -61.4502 | 61.5829 | 0.021127 | -0.0451 | -0.007421 | -0.006703 | 0.036265 | 0.012329 | 0.01969 | 61.4638 | 0.13416 | 61.4043 | -0.051417 | -0.002124 | 61.5158 | -0.015171 | 61.3031 | 61.4713 | 61.4051 | 61.4428 | 61.4435 | 61.4865 | 61.4625 | 61.4699 | 122.914 | 61.5844 | 122.8545 | 61.3988 | 61.4481 | 122.966 | 61.435 | 122.7533 | 61.466 | 61.479 | 61.4064 | 61.4194
86.8906 | 123.1522 | -61.4548 | 61.5601 | 0.01197 | -0.049678 | -0.012 | -0.011281 | 0.022531 | 0.012329 | 0.015112 | 61.4593 | 0.13416 | 61.3951 | -0.046838 | -0.006702 | 61.5112 | 0.003143 | 61.2848 | 61.4667 | 61.4051 | 61.4428 | 61.4435 | 61.4773 | 61.4671 | 61.4699 | 122.914 | 61.5889 | 122.8499 | 61.4079 | 61.4481 | 122.966 | 61.4579 | 122.7396 | 61.466 | 61.4561 | 61.4018 | 61.392
87.8906 | 123.2849 | -61.409 | 61.5601 | 0.016548 | -0.049678 | -0.016578 | -0.01586 | 0.027109 | 0.012329 | 0.010533 | 61.4638 | 0.13416 | 61.3768 | -0.042259 | 0.025345 | 61.5112 | 0.007721 | 61.294 | 61.4255 | 61.3593 | 61.3924 | 61.3931 | 61.4361 | 61.4213 | 61.4195 | 122.8728 | 61.5432 | 122.7858 | 61.3667 | 61.4343 | 122.9202 | 61.4167 | 122.703 | 61.4385 | 61.4561 | 61.3514 | 61.3691
88.8906 | 123.1796 | -61.4548 | 61.5463 | 0.025705 | -0.049678 | -0.016578 | -0.006703 | 0.031687 | 0.012329 | 0.015112 | 61.473 | 0.12958 | 61.3447 | -0.092628 | 0.002454 | 61.5112 | -0.001436 | 61.5046 | 61.4805 | 61.4051 | 61.4382 | 61.4481 | 61.4865 | 61.4671 | 61.4699 | 122.9278 | 61.5844 | 122.7995 | 61.3621 | 61.4572 | 122.966 | 61.4533 | 122.9594 | 61.4705 | 61.4744 | 61.3423 | 61.3462
89.8906 | 123.175 | -61.4136 | 61.5967 | 0.021127 | -0.0451 | -0.012 | -0.006703 | 0.036265 | 0.012329 | 0.015112 | 61.4593 | 0.13416 | 61.4043 | -0.088049 | 0.007032 | 61.5066 | 0.003143 | 61.4954 | 61.4347 | 61.3685 | 61.4016 | 61.4069 | 61.4498 | 61.4259 | 61.4287 | 122.8728 | 61.5477 | 122.8178 | 61.3255 | 61.4206 | 122.9202 | 61.4167 | 122.909 | 61.4522 | 61.4561 | 61.3972 | 61.4011
90.8906 | 123.1567 | -61.441 | 61.5417 | 0.01197 | -0.040521 | -0.016578 | -0.011281 | 0.017953 | 0.003172 | 0.015112 | 61.4638 | 0.13416 | 61.3997 | -0.092628 | 0.002454 | 61.5158 | -0.001436 | 61.294 | 61.453 | 61.4005 | 61.4245 | 61.4298 | 61.459 | 61.4442 | 61.4562 | 122.9049 | 61.5752 | 122.8407 | 61.3484 | 61.4435 | 122.9568 | 61.4396 | 122.735 | 61.4614 | 61.4653 | 61.3972 | 61.4011
91.8906 | 123.2803 | -61.4365 | 61.5326 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.015112 | 61.4638 | 0.13874 | 61.3997 | -0.060575 | 0.002454 | 61.5158 | -0.010593 | 61.2986 | 61.453 | 61.3959 | 61.4245 | 61.4298 | 61.459 | 61.4442 | 61.4516 | 122.9003 | 61.5752 | 122.8361 | 61.3759 | 61.4389 | 122.9523 | 61.4259 | 122.735 | 61.4614 | 61.4744 | 61.3972 | 61.4103
92.8906 | 123.2346 | -61.441 | 61.5601 | 0.016548 | -0.049678 | -0.007421 | -0.006703 | 0.022531 | 0.00775 | 0.010533 | 61.4684 | 0.13874 | 61.4043 | -0.055996 | 0.002454 | 61.5204 | 0.003143 | 61.2986 | 61.4576 | 61.3914 | 61.4336 | 61.4343 | 61.4636 | 61.4488 | 61.4516 | 122.9095 | 61.5798 | 122.8453 | 61.385 | 61.4435 | 122.9614 | 61.4442 | 122.7396 | 61.466 | 61.4653 | 61.4018 | 61.4011
93.8906 | 123.2712 | -61.4044 | 61.5143 | 0.016548 | -0.049678 | -0.016578 | -0.006703 | 0.022531 | 0.012329 | 0.024268 | 61.4638 | 0.13416 | 61.4088 | -0.060575 | 0.002454 | 61.5158 | -0.006014 | 61.2986 | 61.421 | 61.3547 | 61.3878 | 61.3977 | 61.4269 | 61.4167 | 61.4287 | 122.8683 | 61.5386 | 122.8133 | 61.3438 | 61.4069 | 122.9202 | 61.3984 | 122.703 | 61.4614 | 61.4699 | 61.4064 | 61.4149
94.8906 | 123.2071 | -61.4136 | 61.5143 | 0.021127 | -0.049678 | -0.016578 | -0.011281 | 0.022531 | 0.016907 | 0.010533 | 61.4593 | 0.12958 | 61.4088 | -0.065154 | 0.01161 | 61.5112 | 0.003143 | 61.2986 | 61.4347 | 61.3639 | 61.397 | 61.4023 | 61.4361 | 61.4305 | 61.4241 | 122.8728 | 61.5432 | 122.8224 | 61.3484 | 61.4252 | 122.9248 | 61.4167 | 122.7121 | 61.4477 | 61.4561 | 61.3972 | 61.4057
95.8906 | 123.1842 | -61.4731 | 61.5509 | 0.030283 | -0.040521 | -0.007421 | -0.002124 | 0.027109 | 0.016907 | 0.01969 | 61.4684 | 0.13874 | 61.4043 | -0.065154 | 0.002454 | 61.5112 | 0.007721 | 61.2986 | 61.5034 | 61.4326 | 61.4657 | 61.471 | 61.5002 | 61.49 | 61.4928 | 122.9415 | 61.6118 | 122.8773 | 61.4079 | 61.4755 | 122.9843 | 61.4808 | 122.7717 | 61.466 | 61.4607 | 61.4018 | 61.3965
96.8906 | 123.2666 | -61.4502 | 61.5189 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.031687 | 0.012329 | 0.01969 | 61.4684 | 0.13874 | 61.3997 | -0.069733 | 0.002454 | 61.5158 | 0.003143 | 61.3031 | 61.4713 | 61.4097 | 61.4336 | 61.4435 | 61.4819 | 61.4625 | 61.4699 | 122.9186 | 61.5889 | 122.8499 | 61.3805 | 61.4526 | 122.966 | 61.4533 | 122.7533 | 61.466 | 61.4653 | 61.3972 | 61.3965
97.8906 | 123.3124 | -61.409 | 61.5372 | 0.016548 | -0.0451 | -0.016578 | -0.011281 | 0.031687 | 0.00775 | 0.015112 | 61.4593 | 0.13874 | 61.4043 | -0.065154 | 0.01161 | 61.5112 | 0.003143 | 61.294 | 61.4255 | 61.3639 | 61.3924 | 61.3977 | 61.4407 | 61.4167 | 61.4241 | 122.8683 | 61.5477 | 122.8133 | 61.3438 | 61.4206 | 122.9202 | 61.4121 | 122.703 | 61.4477 | 61.4561 | 61.3926 | 61.4011
98.8906 | 123.2574 | -61.409 | 61.5143 | 0.01197 | -0.040521 | -0.007421 | -0.006703 | 0.027109 | 0.016907 | 0.01969 | 61.4638 | 0.13874 | 61.4043 | -0.065154 | 0.002454 | 61.5158 | 0.003143 | 61.2986 | 61.421 | 61.3685 | 61.4016 | 61.4023 | 61.4361 | 61.4259 | 61.4287 | 122.8728 | 61.5477 | 122.8133 | 61.3438 | 61.4115 | 122.9248 | 61.4121 | 122.7076 | 61.4614 | 61.4607 | 61.4018 | 61.4011
99.8906 | 123.2529 | -61.4319 | 61.5417 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.005955 | 61.4684 | 0.12958 | 61.4134 | -0.065154 | 0.01161 | 61.5158 | -0.001436 | 61.3031 | 61.453 | 61.3868 | 61.4199 | 61.4298 | 61.459 | 61.4442 | 61.4378 | 122.9003 | 61.5615 | 122.8453 | 61.3667 | 61.4435 | 122.9477 | 61.4304 | 122.735 | 61.4568 | 61.4699 | 61.4018 | 61.4149
100.8906 | 123.2666 | -61.4273 | 61.5097 | 0.021127 | -0.049678 | -0.012 | -0.006703 | 0.022531 | 0.021485 | 0.015112 | 61.4684 | 0.13416 | 61.3951 | -0.060575 | 0.002454 | 61.5158 | 0.007721 | 61.3031 | 61.4484 | 61.3776 | 61.4153 | 61.4206 | 61.4498 | 61.4488 | 61.4424 | 122.8957 | 61.5615 | 122.8224 | 61.3667 | 61.4298 | 122.9431 | 61.435 | 122.7305 | 61.466 | 61.4607 | 61.3926 | 61.3874
101.8906 | 123.2208 | -61.4456 | 61.528 | 0.016548 | -0.054257 | -0.016578 | -0.006703 | 0.027109 | 0.003172 | 0.015112 | 61.4638 | 0.13874 | 61.4043 | -0.069733 | 0.007032 | 61.5112 | -0.006014 | 61.2894 | 61.4622 | 61.3914 | 61.429 | 61.4389 | 61.4727 | 61.4488 | 61.4607 | 122.9095 | 61.5844 | 122.8499 | 61.3759 | 61.4527 | 122.9568 | 61.4396 | 122.735 | 61.4568 | 61.4699 | 61.3972 | 61.4103
102.8906 | 123.1659 | -61.4456 | 61.5784 | 0.016548 | -0.0451 | -0.007421 | -0.006703 | 0.031687 | 0.016907 | 0.015112 | 61.473 | 0.13874 | 61.4088 | -0.055996 | 0.016188 | 61.5204 | 0.003143 | 61.3031 | 61.4622 | 61.4005 | 61.4382 | 61.4389 | 61.4773 | 61.4625 | 61.4607 | 122.9186 | 61.5844 | 122.8545 | 61.3896 | 61.4618 | 122.966 | 61.4488 | 122.7488 | 61.4568 | 61.4699 | 61.3926 | 61.4057
103.8906 | 123.2712 | -61.441 | 61.5189 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.017953 | 0.00775 | 0.01969 | 61.4638 | 0.12958 | 61.4043 | -0.051417 | 0.01161 | 61.5112 | 0.003143 | 61.2986 | 61.4576 | 61.3959 | 61.429 | 61.4389 | 61.459 | 61.4488 | 61.4607 | 122.9049 | 61.5706 | 122.8453 | 61.3896 | 61.4526 | 122.9523 | 61.4442 | 122.7396 | 61.4522 | 61.4607 | 61.3926 | 61.4011
104.8906 | 123.262 | -61.4456 | 61.5234 | 0.01197 | -0.049678 | -0.007421 | -0.002124 | 0.027109 | 0.00775 | 0.015112 | 61.4638 | 0.14332 | 61.4043 | -0.060575 | 0.002454 | 61.5158 | 0.007721 | 61.2894 | 61.4576 | 61.3959 | 61.4382 | 61.4435 | 61.4727 | 61.4534 | 61.4607 | 122.9095 | 61.5889 | 122.8499 | 61.385 | 61.4481 | 122.9614 | 61.4533 | 122.735 | 61.4614 | 61.4561 | 61.4018 | 61.3965
105.8906 | 123.2254 | -61.4365 | 61.5463 | 0.025705 | -0.0451 | -0.007421 | -0.006703 | 0.027109 | 0.003172 | 0.015112 | 61.4638 | 0.14332 | 61.3997 | -0.069733 | 0.01161 | 61.5158 | 0.003143 | 61.2986 | 61.4622 | 61.3914 | 61.429 | 61.4298 | 61.4636 | 61.4396 | 61.4516 | 122.9003 | 61.5798 | 122.8361 | 61.3667 | 61.4481 | 122.9523 | 61.4396 | 122.735 | 61.4522 | 61.4607 | 61.3881 | 61.3965
106.8906 | 123.2391 | -61.4365 | 61.5372 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.012329 | 0.015112 | 61.4593 | 0.12958 | 61.4088 | -0.074312 | 0.007032 | 61.5204 | -0.001436 | 61.2894 | 61.4576 | 61.3959 | 61.4199 | 61.4298 | 61.4636 | 61.4488 | 61.4516 | 122.8957 | 61.566 | 122.8453 | 61.3621 | 61.4435 | 122.9568 | 61.435 | 122.7259 | 61.4522 | 61.4607 | 61.4018 | 61.4103
107.8906 | 123.1842 | -61.4182 | 61.5509 | 0.021127 | -0.0451 | -0.021157 | -0.011281 | 0.027109 | 0.00775 | 0.015112 | 61.473 | 0.13416 | 61.4088 | -0.060575 | -0.006702 | 61.5158 | -0.006014 | 61.2986 | 61.4393 | 61.3731 | 61.397 | 61.4069 | 61.4453 | 61.4259 | 61.4333 | 122.8912 | 61.5523 | 122.827 | 61.3576 | 61.4115 | 122.934 | 61.4121 | 122.7167 | 61.4797 | 61.479 | 61.4155 | 61.4149
108.8906 | 123.2803 | -61.4273 | 61.5097 | 0.016548 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.01969 | 61.473 | 0.13416 | 61.4088 | -0.088049 | -0.002124 | 61.5204 | -0.006014 | 61.294 | 61.4439 | 61.3822 | 61.4153 | 61.4206 | 61.4544 | 61.4351 | 61.447 | 122.9003 | 61.5615 | 122.8361 | 61.3393 | 61.4252 | 122.9477 | 61.4213 | 122.7213 | 61.4751 | 61.479 | 61.411 | 61.4149
109.8906 | 123.2574 | -61.4136 | 61.5555 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | 0.00775 | 0.015112 | 61.4638 | 0.13416 | 61.4043 | -0.092628 | 0.007032 | 61.5112 | 0.003143 | 61.3031 | 61.4347 | 61.3776 | 61.397 | 61.4069 | 61.4407 | 61.4213 | 61.4287 | 122.8774 | 61.5477 | 122.8178 | 61.3209 | 61.4206 | 122.9248 | 61.4167 | 122.7167 | 61.4568 | 61.4607 | 61.3972 | 61.4011
110.8906 | 123.2666 | -61.4319 | 61.5646 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.017953 | 0.012329 | 0.01969 | 61.4684 | 0.13416 | 61.4043 | -0.092628 | 0.016188 | 61.5204 | -0.006014 | 61.2894 | 61.4484 | 61.3868 | 61.4153 | 61.4298 | 61.4498 | 61.4442 | 61.4516 | 122.9003 | 61.566 | 122.8361 | 61.3393 | 61.4481 | 122.9523 | 61.4259 | 122.7213 | 61.4522 | 61.4744 | 61.3881 | 61.4103
111.8906 | 123.2941 | -61.3815 | 61.5555 | 0.025705 | -0.049678 | -0.016578 | -0.011281 | 0.027109 | -0.001406 | 0.01969 | 61.4593 | 0.13416 | 61.3951 | -0.092628 | 0.007032 | 61.5112 | -0.001436 | 61.3031 | 61.4072 | 61.3319 | 61.365 | 61.3703 | 61.4086 | 61.3801 | 61.4012 | 122.8408 | 61.5157 | 122.7766 | 61.2889 | 61.3886 | 122.8928 | 61.3801 | 122.6847 | 61.4522 | 61.4607 | 61.3881 | 61.3965
112.8906 | 123.262 | -61.4136 | 61.5692 | 0.021127 | -0.054257 | -0.012 | -0.011281 | 0.022531 | 0.012329 | 0.01969 | 61.4593 | 0.12958 | 61.4043 | -0.065154 | 0.01161 | 61.5158 | -0.001436 | 61.2986 | 61.4347 | 61.3593 | 61.4016 | 61.4023 | 61.4361 | 61.4259 | 61.4333 | 122.8728 | 61.5432 | 122.8178 | 61.3484 | 61.4252 | 122.9294 | 61.4121 | 122.7121 | 61.4477 | 61.4607 | 61.3926 | 61.4057
113.8906 | 123.2437 | -61.4456 | 61.5417 | 0.021127 | -0.040521 | -0.021157 | -0.01586 | 0.022531 | 0.012329 | 0.010533 | 61.4638 | 0.14332 | 61.4043 | -0.065154 | 0.016188 | 61.5158 | 0.003143 | 61.2986 | 61.4667 | 61.4051 | 61.4245 | 61.4298 | 61.4681 | 61.4579 | 61.4562 | 122.9095 | 61.5889 | 122.8499 | 61.3805 | 61.4618 | 122.9614 | 61.4488 | 122.7442 | 61.4477 | 61.4607 | 61.3881 | 61.4011
114.8906 | 123.1384 | -61.4319 | 61.5326 | 0.016548 | -0.049678 | -0.012 | -0.01586 | 0.036265 | 0.012329 | 0.024268 | 61.4593 | 0.12958 | 61.4043 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.2894 | 61.4484 | 61.3822 | 61.4199 | 61.416 | 61.4682 | 61.4442 | 61.4562 | 122.8912 | 61.5615 | 122.8361 | 61.3759 | 61.4435 | 122.9523 | 61.435 | 122.7213 | 61.4477 | 61.4561 | 61.3926 | 61.4011
115.8906 | 123.3261 | -61.4136 | 61.5143 | 0.021127 | -0.049678 | -0.007421 | -0.006703 | 0.027109 | 0.012329 | 0.01969 | 61.473 | 0.12958 | 61.4088 | -0.055996 | 0.002454 | 61.5204 | 0.003143 | 61.3077 | 61.4347 | 61.3639 | 61.4062 | 61.4069 | 61.4407 | 61.4259 | 61.4333 | 122.8866 | 61.5432 | 122.8224 | 61.3576 | 61.416 | 122.934 | 61.4167 | 122.7213 | 61.4705 | 61.4699 | 61.4064 | 61.4057
116.8906 | 123.2483 | -61.4365 | 61.5463 | 0.016548 | -0.054257 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.005955 | 61.4638 | 0.12958 | 61.4043 | -0.060575 | 0.002454 | 61.5066 | 0.003143 | 61.294 | 61.453 | 61.3822 | 61.4245 | 61.4343 | 61.4636 | 61.4396 | 61.4424 | 122.9003 | 61.566 | 122.8407 | 61.3759 | 61.4389 | 122.9431 | 61.4396 | 122.7305 | 61.4614 | 61.4607 | 61.4018 | 61.4011
117.8906 | 123.262 | -61.3953 | 61.5417 | 0.021127 | -0.0451 | -0.021157 | -0.011281 | 0.022531 | 0.00775 | 0.015112 | 61.4684 | 0.13416 | 61.3997 | -0.055996 | 0.01161 | 61.5158 | 0.003143 | 61.2986 | 61.4164 | 61.3502 | 61.3741 | 61.384 | 61.4178 | 61.403 | 61.4104 | 122.8637 | 61.5294 | 122.7949 | 61.3393 | 61.4069 | 122.9111 | 61.3984 | 122.6938 | 61.4568 | 61.4653 | 61.3881 | 61.3965
118.8906 | 123.2758 | -61.409 | 61.5417 | 0.030283 | -0.040521 | -0.012 | -0.011281 | 0.022531 | 0.00775 | 0.015112 | 61.4593 | 0.12958 | 61.4043 | -0.060575 | 0.01161 | 61.5112 | 0.003143 | 61.2986 | 61.4393 | 61.3685 | 61.397 | 61.3977 | 61.4315 | 61.4167 | 61.4241 | 122.8683 | 61.5386 | 122.8133 | 61.3484 | 61.4206 | 122.9202 | 61.4121 | 122.7076 | 61.4477 | 61.4561 | 61.3926 | 61.4011
119.8906 | 123.175 | -61.441 | 61.5738 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4684 | 0.13874 | 61.4043 | -0.055996 | 0.007032 | 61.5112 | -0.001436 | 61.3031 | 61.4667 | 61.4005 | 61.4245 | 61.4343 | 61.4636 | 61.4534 | 61.4607 | 122.9095 | 61.5798 | 122.8453 | 61.385 | 61.4481 | 122.9523 | 61.4396 | 122.7442 | 61.4614 | 61.4699 | 61.3972 | 61.4057
120.8906 | 123.2712 | -61.4227 | 61.5372 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.015112 | 61.4684 | 0.13874 | 61.4088 | -0.060575 | 0.016188 | 61.525 | -0.001436 | 61.3031 | 61.4439 | 61.3776 | 61.4062 | 61.416 | 61.4498 | 61.4396 | 61.4378 | 122.8912 | 61.5615 | 122.8316 | 61.3622 | 61.4389 | 122.9477 | 61.4213 | 122.7259 | 61.4522 | 61.4699 | 61.3926 | 61.4103
121.8906 | 123.3124 | -61.4136 | 61.5417 | 0.016548 | -0.040521 | -0.016578 | -0.01586 | 0.017953 | 0.012329 | 0.01969 | 61.4638 | 0.14332 | 61.4043 | -0.060575 | 0.002454 | 61.5112 | 0.003143 | 61.2986 | 61.4301 | 61.3731 | 61.397 | 61.3977 | 61.4315 | 61.4259 | 61.4333 | 122.8774 | 61.5569 | 122.8178 | 61.353 | 61.416 | 122.9248 | 61.4167 | 122.7121 | 61.4614 | 61.4607 | 61.4018 | 61.4011
122.8906 | 123.1338 | -61.4548 | 61.5738 | 0.025705 | -0.049678 | -0.012 | -0.002124 | 0.017953 | 0.012329 | 0.01969 | 61.4684 | 0.13874 | 61.4043 | -0.060575 | 0.002454 | 61.5112 | 0.003143 | 61.2986 | 61.4805 | 61.4051 | 61.4428 | 61.4526 | 61.4727 | 61.4671 | 61.4745 | 122.9232 | 61.5935 | 122.859 | 61.3942 | 61.4572 | 122.966 | 61.4579 | 122.7533 | 61.466 | 61.4653 | 61.4018 | 61.4011
123.8906 | 123.2574 | -61.441 | 61.5738 | 0.016548 | -0.049678 | -0.012 | 0.002454 | 0.017953 | 0.00775 | 0.01969 | 61.4684 | 0.13874 | 61.4088 | -0.055996 | 0.01161 | 61.5158 | 0.007721 | 61.3077 | 61.4576 | 61.3914 | 61.429 | 61.4435 | 61.459 | 61.4488 | 61.4607 | 122.9095 | 61.5798 | 122.8499 | 61.385 | 61.4526 | 122.9568 | 61.4488 | 122.7488 | 61.4568 | 61.4607 | 61.3972 | 61.4011
124.8906 | 123.2529 | -61.4227 | 61.496 | 0.016548 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4684 | 0.13416 | 61.4088 | -0.065154 | -0.002124 | 61.5112 | -0.001436 | 61.294 | 61.4393 | 61.3868 | 61.4107 | 61.4206 | 61.4498 | 61.4305 | 61.4424 | 122.8912 | 61.5569 | 122.8316 | 61.3576 | 61.4206 | 122.934 | 61.4213 | 122.7167 | 61.4705 | 61.4699 | 61.411 | 61.4103
125.8906 | 123.143 | -61.441 | 61.5967 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.022531 | 0.00775 | 0.01969 | 61.4684 | 0.13416 | 61.4088 | -0.060575 | 0.002454 | 61.5158 | 0.003143 | 61.3077 | 61.4622 | 61.3959 | 61.4245 | 61.4343 | 61.4636 | 61.4488 | 61.4607 | 122.9095 | 61.5752 | 122.8499 | 61.3805 | 61.4435 | 122.9568 | 61.4442 | 122.7488 | 61.466 | 61.4653 | 61.4064 | 61.4057
126.8906 | 123.175 | -61.4136 | 61.6013 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.015112 | 61.4638 | 0.13416 | 61.4134 | -0.060575 | 0.002454 | 61.5112 | 0.007721 | 61.3031 | 61.4301 | 61.3685 | 61.4016 | 61.4114 | 61.4407 | 61.4213 | 61.4287 | 122.8774 | 61.5477 | 122.827 | 61.353 | 61.416 | 122.9248 | 61.4213 | 122.7167 | 61.4614 | 61.4561 | 61.411 | 61.4057
127.8906 | 123.2162 | -61.4365 | 61.5234 | 0.021127 | -0.049678 | -0.016578 | -0.006703 | 0.022531 | 0.00775 | 0.015112 | 61.4638 | 0.13874 | 61.4134 | -0.055996 | 0.007032 | 61.5158 | 0.003143 | 61.2986 | 61.4576 | 61.3868 | 61.4199 | 61.4298 | 61.459 | 61.4442 | 61.4516 | 122.9003 | 61.5752 | 122.8499 | 61.3805 | 61.4435 | 122.9523 | 61.4396 | 122.735 | 61.4568 | 61.4607 | 61.4064 | 61.4103
128.8906 | 123.23 | -61.4365 | 61.5601 | 0.021127 | -0.0451 | -0.007421 | -0.011281 | 0.027109 | 0.012329 | 0.01969 | 61.473 | 0.12958 | 61.4134 | -0.060575 | 0.007032 | 61.5158 | 0.007721 | 61.3031 | 61.4576 | 61.3914 | 61.429 | 61.4252 | 61.4636 | 61.4488 | 61.4562 | 122.9095 | 61.566 | 122.8499 | 61.3759 | 61.4435 | 122.9523 | 61.4442 | 122.7396 | 61.466 | 61.4653 | 61.4064 | 61.4057
129.8906 | 123.2162 | -61.3953 | 61.5463 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.015112 | 61.4684 | 0.12958 | 61.4088 | -0.055996 | 0.007032 | 61.5204 | -0.001436 | 61.3031 | 61.4164 | 61.3502 | 61.3787 | 61.3886 | 61.4224 | 61.4122 | 61.4104 | 122.8637 | 61.5248 | 122.8041 | 61.3393 | 61.4023 | 122.9156 | 61.3938 | 122.6984 | 61.4614 | 61.4699 | 61.4018 | 61.4103
130.8906 | 123.1888 | -61.4319 | 61.6013 | 0.025705 | -0.049678 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.473 | 0.14332 | 61.4043 | -0.065154 | 0.002454 | 61.5112 | 0.007721 | 61.3031 | 61.4576 | 61.3822 | 61.4153 | 61.4343 | 61.459 | 61.4351 | 61.4562 | 122.9049 | 61.5752 | 122.8361 | 61.3667 | 61.4343 | 122.9431 | 61.4396 | 122.735 | 61.4705 | 61.4653 | 61.4018 | 61.3965
131.8906 | 123.1201 | -61.4365 | 61.6013 | 0.025705 | -0.035942 | -0.007421 | -0.006703 | 0.027109 | 0.003172 | 0.024268 | 61.4638 | 0.14332 | 61.4088 | -0.055996 | 0.007032 | 61.5158 | 0.003143 | 61.3031 | 61.4622 | 61.4005 | 61.429 | 61.4298 | 61.4636 | 61.4396 | 61.4607 | 122.9003 | 61.5798 | 122.8453 | 61.3805 | 61.4435 | 122.9523 | 61.4396 | 122.7396 | 61.4568 | 61.4607 | 61.4018 | 61.4057
132.8906 | 123.2529 | -61.4319 | 61.5143 | 0.01197 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | 0.003172 | 0.015112 | 61.4776 | 0.13874 | 61.4088 | -0.055996 | 0.007032 | 61.5204 | 0.007721 | 61.3031 | 61.4439 | 61.3914 | 61.4153 | 61.4206 | 61.459 | 61.4351 | 61.447 | 122.9095 | 61.5706 | 122.8407 | 61.3759 | 61.4389 | 122.9523 | 61.4396 | 122.735 | 61.4705 | 61.4699 | 61.4018 | 61.4011
133.8906 | 123.1888 | -61.4227 | 61.5875 | 0.016548 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.00775 | 0.015112 | 61.4684 | 0.13416 | 61.4088 | -0.065154 | 0.002454 | 61.5112 | -0.001436 | 61.2986 | 61.4393 | 61.3776 | 61.4153 | 61.416 | 61.4453 | 61.4305 | 61.4378 | 122.8912 | 61.5569 | 122.8316 | 61.3576 | 61.4252 | 122.934 | 61.4213 | 122.7213 | 61.466 | 61.4699 | 61.4064 | 61.4103
134.8906 | 123.3124 | -61.4365 | 61.5417 | 0.021127 | -0.040521 | -0.007421 | -0.006703 | 0.022531 | 0.016907 | 0.015112 | 61.4684 | 0.13874 | 61.3997 | -0.069733 | -0.002124 | 61.5112 | -0.001436 | 61.2894 | 61.4576 | 61.3959 | 61.429 | 61.4298 | 61.459 | 61.4534 | 61.4516 | 122.9049 | 61.5752 | 122.8361 | 61.3667 | 61.4343 | 122.9477 | 61.435 | 122.7259 | 61.4705 | 61.4699 | 61.4018 | 61.4011
135.8906 | 123.2162 | -61.441 | 61.5875 | 0.025705 | -0.0451 | -0.016578 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.13874 | 61.4134 | -0.060575 | 0.002454 | 61.5112 | 0.003143 | 61.3077 | 61.4667 | 61.3959 | 61.4245 | 61.4343 | 61.4636 | 61.4534 | 61.4607 | 122.9186 | 61.5798 | 122.8545 | 61.3805 | 61.4435 | 122.9523 | 61.4442 | 122.7488 | 61.4751 | 61.4744 | 61.411 | 61.4103
136.8906 | 123.2025 | -61.4365 | 61.5692 | 0.025705 | -0.049678 | -0.012 | -0.006703 | 0.022531 | 0.003172 | 0.01969 | 61.473 | 0.13874 | 61.418 | -0.060575 | 0.002454 | 61.5158 | -0.001436 | 61.2986 | 61.4622 | 61.3868 | 61.4245 | 61.4298 | 61.459 | 61.4396 | 61.4562 | 122.9095 | 61.5752 | 122.8545 | 61.3759 | 61.4389 | 122.9523 | 61.435 | 122.735 | 61.4705 | 61.4744 | 61.4155 | 61.4194
137.8906 | 123.2071 | -61.441 | 61.5829 | 0.025705 | -0.049678 | -0.007421 | -0.006703 | 0.027109 | 0.012329 | 0.01969 | 61.473 | 0.13416 | 61.4088 | -0.055996 | 0.007032 | 61.5158 | -0.001436 | 61.2986 | 61.4667 | 61.3914 | 61.4336 | 61.4343 | 61.4681 | 61.4534 | 61.4607 | 122.914 | 61.5752 | 122.8499 | 61.385 | 61.4481 | 122.9568 | 61.4396 | 122.7396 | 61.466 | 61.4744 | 61.4018 | 61.4103
138.8906 | 123.2208 | -61.4273 | 61.5829 | 0.021127 | -0.054257 | -0.021157 | -0.006703 | 0.027109 | 0.012329 | 0.01969 | 61.4684 | 0.12958 | 61.4043 | -0.055996 | 0.01161 | 61.5158 | -0.001436 | 61.3031 | 61.4484 | 61.373 | 61.4061 | 61.4206 | 61.4544 | 61.4396 | 61.447 | 122.8957 | 61.5569 | 122.8316 | 61.3713 | 61.4389 | 122.9431 | 61.4259 | 122.7305 | 61.4568 | 61.4699 | 61.3926 | 61.4057
139.8906 | 123.1888 | -61.4227 | 61.5509 | 0.021127 | -0.040521 | -0.007421 | -0.006703 | 0.031687 | 0.00775 | 0.015112 | 61.4638 | 0.14332 | 61.4088 | -0.060575 | 0.01161 | 61.525 | -0.001436 | 61.2986 | 61.4439 | 61.3822 | 61.4153 | 61.416 | 61.4544 | 61.4305 | 61.4378 | 122.8866 | 61.566 | 122.8316 | 61.3622 | 61.4343 | 122.9477 | 61.4213 | 122.7213 | 61.4522 | 61.4653 | 61.3972 | 61.4103
140.8906 | 123.1842 | -61.4502 | 61.5784 | 0.034862 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.024268 | 61.4684 | 0.13874 | 61.4134 | -0.060575 | 0.007032 | 61.5204 | -0.001436 | 61.2986 | 61.4851 | 61.4051 | 61.4336 | 61.4481 | 61.4819 | 61.4671 | 61.4745 | 122.9186 | 61.5889 | 122.8636 | 61.3896 | 61.4572 | 122.9706 | 61.4488 | 122.7488 | 61.4614 | 61.4699 | 61.4064 | 61.4149
141.8906 | 123.1247 | -61.4227 | 61.5646 | 0.016548 | -0.049678 | -0.007421 | -0.006703 | 0.027109 | 0.00775 | 0.01969 | 61.4776 | 0.1479 | 61.4134 | -0.055996 | 0.007032 | 61.5158 | -0.001436 | 61.3031 | 61.4393 | 61.3731 | 61.4153 | 61.416 | 61.4498 | 61.4305 | 61.4424 | 122.9003 | 61.5706 | 122.8361 | 61.3667 | 61.4298 | 122.9385 | 61.4213 | 122.7259 | 61.4705 | 61.479 | 61.4064 | 61.4149
142.8906 | 123.1934 | -61.4502 | 61.5417 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.13874 | 61.4043 | -0.060575 | 0.002454 | 61.5204 | 0.003143 | 61.2894 | 61.4713 | 61.4097 | 61.4336 | 61.4526 | 61.4727 | 61.4625 | 61.4699 | 122.9278 | 61.5889 | 122.8545 | 61.3896 | 61.4526 | 122.9706 | 61.4533 | 122.7396 | 61.4751 | 61.4744 | 61.4018 | 61.4011
143.8906 | 123.2071 | -61.4136 | 61.5784 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.473 | 0.13874 | 61.4134 | -0.060575 | 0.002454 | 61.5158 | -0.001436 | 61.2986 | 61.4347 | 61.3731 | 61.397 | 61.4114 | 61.4407 | 61.4259 | 61.4378 | 122.8866 | 61.5523 | 122.827 | 61.353 | 61.416 | 122.9294 | 61.4121 | 122.7121 | 61.4705 | 61.4744 | 61.411 | 61.4149
144.8906 | 123.111 | -61.4502 | 61.5738 | 0.025705 | -0.0451 | -0.007421 | -0.006703 | 0.027109 | 0.00775 | 0.024268 | 61.4684 | 0.13874 | 61.4134 | -0.065154 | 0.002454 | 61.5204 | -0.001436 | 61.2894 | 61.4759 | 61.4051 | 61.4428 | 61.4435 | 61.4773 | 61.4579 | 61.4745 | 122.9186 | 61.5889 | 122.8636 | 61.385 | 61.4526 | 122.9706 | 61.4488 | 122.7396 | 61.466 | 61.4699 | 61.411 | 61.4149
145.8906 | 123.1384 | -61.4319 | 61.5692 | 0.021127 | -0.0451 | -0.021157 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4684 | 0.14332 | 61.4088 | -0.065154 | 0.002454 | 61.5158 | -0.001436 | 61.3031 | 61.453 | 61.3868 | 61.4107 | 61.4298 | 61.4544 | 61.4442 | 61.4516 | 122.9003 | 61.5752 | 122.8407 | 61.3667 | 61.4343 | 122.9477 | 61.4304 | 122.735 | 61.466 | 61.4699 | 61.4064 | 61.4103
146.8906 | 123.1796 | -61.4731 | 61.5692 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.012329 | 0.015112 | 61.4776 | 0.13874 | 61.4088 | -0.065154 | 0.007032 | 61.5158 | 0.003143 | 61.3031 | 61.4896 | 61.4326 | 61.4657 | 61.4755 | 61.5048 | 61.4854 | 61.4882 | 122.9507 | 61.6118 | 122.8819 | 61.4079 | 61.4801 | 122.9889 | 61.4762 | 122.7762 | 61.4705 | 61.4744 | 61.4018 | 61.4057
147.8906 | 123.1476 | -61.4822 | 61.5646 | 0.025705 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.016907 | 0.01969 | 61.4776 | 0.13874 | 61.3997 | -0.055996 | 0.007032 | 61.5158 | 0.003143 | 61.2986 | 61.5079 | 61.4371 | 61.4748 | 61.4755 | 61.5048 | 61.4991 | 61.5019 | 122.9598 | 61.621 | 122.8819 | 61.4262 | 61.4893 | 122.998 | 61.4854 | 122.7808 | 61.4705 | 61.4744 | 61.3926 | 61.3965
148.8906 | 123.1796 | -61.4594 | 61.5692 | 0.025705 | -0.049678 | -0.007421 | -0.011281 | 0.027109 | 0.012329 | 0.024268 | 61.4776 | 0.13874 | 61.4043 | -0.060575 | 0.007032 | 61.5204 | -0.001436 | 61.3077 | 61.4851 | 61.4097 | 61.4519 | 61.4481 | 61.4865 | 61.4717 | 61.4836 | 122.9369 | 61.5981 | 122.8636 | 61.3988 | 61.4664 | 122.9797 | 61.4579 | 122.7671 | 61.4705 | 61.479 | 61.3972 | 61.4057
149.8906 | 123.1888 | -61.4456 | 61.5921 | 0.016548 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.010533 | 61.4638 | 0.13416 | 61.4043 | -0.060575 | 0.007032 | 61.5158 | 0.007721 | 61.2986 | 61.4622 | 61.4005 | 61.4336 | 61.4389 | 61.4727 | 61.4534 | 61.4562 | 122.9095 | 61.5798 | 122.8499 | 61.385 | 61.4527 | 122.9614 | 61.4533 | 122.7442 | 61.4568 | 61.4561 | 61.3972 | 61.3965
150.8906 | 123.1567 | -61.4456 | 61.5692 | 0.021127 | -0.0451 | -0.007421 | -0.01586 | 0.027109 | 0.012329 | 0.01969 | 61.4684 | 0.13874 | 61.4088 | -0.055996 | 0.01161 | 61.5112 | 0.003143 | 61.2986 | 61.4667 | 61.4005 | 61.4382 | 61.4298 | 61.4727 | 61.4579 | 61.4653 | 122.914 | 61.5844 | 122.8545 | 61.3896 | 61.4572 | 122.9568 | 61.4488 | 122.7442 | 61.4568 | 61.4653 | 61.3972 | 61.4057
151.8906 | 123.1567 | -61.4777 | 61.5692 | 0.021127 | -0.0451 | -0.012 | -0.011281 | 0.036265 | 0.00775 | 0.01969 | 61.4638 | 0.1479 | 61.4134 | -0.051417 | 0.007032 | 61.5158 | 0.003143 | 61.3031 | 61.4988 | 61.4326 | 61.4657 | 61.4664 | 61.5139 | 61.4854 | 61.4974 | 122.9415 | 61.6256 | 122.8911 | 61.4262 | 61.4847 | 122.9935 | 61.4808 | 122.7808 | 61.4568 | 61.4607 | 61.4064 | 61.4103
152.8906 | 123.2574 | -61.4319 | 61.528 | 0.025705 | -0.0451 | -0.016578 | -0.011281 | 0.022531 | 0.00775 | 0.015112 | 61.4776 | 0.13874 | 61.4088 | -0.065154 | -0.002124 | 61.5112 | 0.007721 | 61.294 | 61.4576 | 61.3868 | 61.4153 | 61.4206 | 61.4544 | 61.4396 | 61.447 | 122.9095 | 61.5706 | 122.8407 | 61.3667 | 61.4298 | 122.9431 | 61.4396 | 122.7259 | 61.4797 | 61.4699 | 61.411 | 61.4011
153.8906 | 123.1338 | -61.4822 | 61.5417 | 0.016548 | -0.049678 | -0.012 | -0.002124 | 0.017953 | 0.012329 | 0.010533 | 61.4684 | 0.15248 | 61.4088 | -0.055996 | 0.002454 | 61.5112 | -0.001436 | 61.294 | 61.4988 | 61.4326 | 61.4702 | 61.4801 | 61.5002 | 61.4946 | 61.4928 | 122.9507 | 61.6347 | 122.8911 | 61.4262 | 61.4847 | 122.9935 | 61.4808 | 122.7762 | 61.466 | 61.4699 | 61.4064 | 61.4103
154.8906 | 123.1888 | -61.4594 | 61.5555 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.016907 | 0.010533 | 61.4684 | 0.13416 | 61.4043 | -0.060575 | 0.002454 | 61.5204 | -0.001436 | 61.3031 | 61.4851 | 61.4143 | 61.4474 | 61.4572 | 61.4819 | 61.4763 | 61.4699 | 122.9278 | 61.5935 | 122.8636 | 61.3988 | 61.4618 | 122.9797 | 61.4579 | 122.7625 | 61.466 | 61.4699 | 61.4018 | 61.4057
155.8906 | 123.2254 | -61.4182 | 61.5326 | 0.021127 | -0.049678 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.028846 | 61.473 | 0.14332 | 61.4043 | -0.060575 | 0.002454 | 61.5112 | -0.001436 | 61.2986 | 61.4393 | 61.3685 | 61.4062 | 61.4114 | 61.4407 | 61.4259 | 61.447 | 122.8912 | 61.5615 | 122.8224 | 61.3576 | 61.4206 | 122.9294 | 61.4167 | 122.7167 | 61.4705 | 61.4744 | 61.4018 | 61.4057
156.8906 | 123.2941 | -61.4456 | 61.5051 | 0.016548 | -0.0451 | -0.007421 | -0.011281 | 0.027109 | 0.00775 | 0.015112 | 61.4684 | 0.1479 | 61.3951 | -0.065154 | 0.007032 | 61.5158 | -0.001436 | 61.3077 | 61.4622 | 61.4005 | 61.4382 | 61.4343 | 61.4727 | 61.4534 | 61.4607 | 122.914 | 61.5935 | 122.8407 | 61.3805 | 61.4527 | 122.9614 | 61.4442 | 122.7533 | 61.4614 | 61.4699 | 61.3881 | 61.3965
157.8906 | 123.1888 | -61.441 | 61.528 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.473 | 0.13874 | 61.4134 | -0.051417 | 0.007032 | 61.5204 | -0.001436 | 61.2986 | 61.4622 | 61.3959 | 61.429 | 61.4389 | 61.4681 | 61.4534 | 61.4607 | 122.914 | 61.5798 | 122.8545 | 61.3896 | 61.4481 | 122.9614 | 61.4396 | 122.7396 | 61.466 | 61.4744 | 61.4064 | 61.4149
158.8906 | 123.2391 | -61.4456 | 61.5372 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.473 | 0.14332 | 61.4088 | -0.060575 | 0.01161 | 61.5158 | 0.003143 | 61.3077 | 61.4667 | 61.4051 | 61.429 | 61.4435 | 61.4727 | 61.4534 | 61.4653 | 122.9186 | 61.5889 | 122.8545 | 61.385 | 61.4572 | 122.9614 | 61.4488 | 122.7533 | 61.4614 | 61.4699 | 61.3972 | 61.4057
159.8906 | 123.2895 | -61.4182 | 61.528 | 0.021127 | -0.049678 | -0.012 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4684 | 0.14332 | 61.4134 | -0.055996 | 0.007032 | 61.5112 | -0.001436 | 61.294 | 61.4393 | 61.3685 | 61.4062 | 61.4114 | 61.4407 | 61.4305 | 61.4378 | 122.8866 | 61.5615 | 122.8316 | 61.3622 | 61.4252 | 122.9294 | 61.4167 | 122.7121 | 61.4614 | 61.4699 | 61.4064 | 61.4149
160.8906 | 123.2895 | -61.4136 | 61.5509 | 0.01197 | -0.049678 | -0.016578 | -0.002124 | 0.022531 | 0.00775 | 0.01969 | 61.4684 | 0.13874 | 61.4134 | -0.060575 | -0.002124 | 61.5158 | -0.006014 | 61.294 | 61.4255 | 61.3639 | 61.397 | 61.4114 | 61.4361 | 61.4213 | 61.4333 | 122.882 | 61.5523 | 122.827 | 61.353 | 61.4114 | 122.9294 | 61.4076 | 122.7076 | 61.4705 | 61.4744 | 61.4155 | 61.4194
161.8906 | 123.3078 | -61.409 | 61.5143 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.012329 | 0.024268 | 61.4638 | 0.14332 | 61.4088 | -0.065154 | 0.01161 | 61.5112 | 0.003143 | 61.2894 | 61.4255 | 61.3685 | 61.397 | 61.4023 | 61.4315 | 61.4213 | 61.4333 | 122.8728 | 61.5523 | 122.8178 | 61.3438 | 61.4206 | 122.9202 | 61.4121 | 122.6984 | 61.4522 | 61.4607 | 61.3972 | 61.4057
162.8906 | 123.2758 | -61.4594 | 61.4868 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.015112 | 61.4684 | 0.13416 | 61.4088 | -0.055996 | 0.007032 | 61.5158 | 0.003143 | 61.3031 | 61.4805 | 61.4188 | 61.4428 | 61.4572 | 61.4865 | 61.4625 | 61.4745 | 122.9278 | 61.5935 | 122.8682 | 61.4034 | 61.4664 | 122.9752 | 61.4625 | 122.7625 | 61.4614 | 61.4653 | 61.4018 | 61.4057
163.8906 | 123.2483 | -61.4456 | 61.5051 | 0.016548 | -0.049678 | -0.021157 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4638 | 0.1479 | 61.4088 | -0.065154 | 0.002454 | 61.5158 | 0.003143 | 61.294 | 61.4622 | 61.3959 | 61.4245 | 61.4435 | 61.4727 | 61.4534 | 61.4653 | 122.9095 | 61.5935 | 122.8545 | 61.3805 | 61.4481 | 122.9614 | 61.4488 | 122.7396 | 61.4614 | 61.4607 | 61.4064 | 61.4057
164.8906 | 123.2529 | -61.4456 | 61.5189 | 0.016548 | -0.049678 | -0.012 | -0.006703 | 0.022531 | -0.001406 | 0.01969 | 61.473 | 0.13874 | 61.4088 | -0.060575 | 0.01161 | 61.5204 | -0.006014 | 61.2986 | 61.4622 | 61.3959 | 61.4336 | 61.4389 | 61.4681 | 61.4442 | 61.4653 | 122.9186 | 61.5844 | 122.8545 | 61.385 | 61.4572 | 122.966 | 61.4396 | 122.7442 | 61.4614 | 61.479 | 61.3972 | 61.4149
165.8906 | 123.2483 | -61.4319 | 61.5143 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.010533 | 61.473 | 0.14332 | 61.4088 | -0.060575 | 0.002454 | 61.5066 | 0.003143 | 61.2986 | 61.4576 | 61.3914 | 61.4199 | 61.4298 | 61.459 | 61.4442 | 61.4424 | 122.9049 | 61.5752 | 122.8407 | 61.3713 | 61.4343 | 122.9385 | 61.435 | 122.7305 | 61.4705 | 61.4699 | 61.4064 | 61.4057
166.8906 | 123.2712 | -61.4319 | 61.5372 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.01969 | 61.4684 | 0.14332 | 61.4134 | -0.060575 | 0.002454 | 61.5204 | 0.003143 | 61.3031 | 61.453 | 61.3914 | 61.4245 | 61.4343 | 61.459 | 61.4442 | 61.4516 | 122.9003 | 61.5752 | 122.8453 | 61.3713 | 61.4343 | 122.9523 | 61.435 | 122.735 | 61.466 | 61.4653 | 61.411 | 61.4103
167.8906 | 123.3032 | -61.4319 | 61.5326 | 0.016548 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.00775 | 0.015112 | 61.4776 | 0.14332 | 61.4134 | -0.051417 | 0.007032 | 61.5158 | 0.007721 | 61.3031 | 61.4484 | 61.3914 | 61.4153 | 61.4252 | 61.459 | 61.4396 | 61.447 | 122.9095 | 61.5752 | 122.8453 | 61.3805 | 61.4389 | 122.9477 | 61.4396 | 122.735 | 61.4705 | 61.4699 | 61.4064 | 61.4057
168.8906 | 123.2666 | -61.4365 | 61.5417 | 0.01197 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.473 | 0.14332 | 61.4134 | -0.065154 | 0.01161 | 61.5204 | 0.003143 | 61.2986 | 61.4484 | 61.3914 | 61.4245 | 61.4343 | 61.459 | 61.4488 | 61.4562 | 122.9095 | 61.5798 | 122.8499 | 61.3713 | 61.4481 | 122.9568 | 61.4396 | 122.735 | 61.4614 | 61.4699 | 61.4018 | 61.4103
169.8906 | 123.3032 | -61.4182 | 61.5417 | 0.01197 | -0.0451 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.01969 | 61.473 | 0.14332 | 61.4088 | -0.055996 | 0.007032 | 61.5204 | 0.003143 | 61.2894 | 61.4301 | 61.3731 | 61.4062 | 61.4114 | 61.4407 | 61.4259 | 61.4378 | 122.8912 | 61.5615 | 122.827 | 61.3622 | 61.4252 | 122.9385 | 61.4213 | 122.7076 | 61.466 | 61.4699 | 61.4018 | 61.4057
170.8906 | 123.2208 | -61.4136 | 61.5463 | 0.016548 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.01969 | 61.4684 | 0.13874 | 61.4134 | -0.065154 | 0.007032 | 61.5112 | 0.003143 | 61.3031 | 61.4301 | 61.3685 | 61.4016 | 61.4069 | 61.4407 | 61.4213 | 61.4333 | 122.882 | 61.5523 | 122.827 | 61.3484 | 61.4206 | 122.9248 | 61.4167 | 122.7167 | 61.4614 | 61.4653 | 61.4064 | 61.4103
171.8906 | 123.23 | -61.4365 | 61.5372 | 0.021127 | -0.040521 | -0.016578 | -0.01586 | 0.022531 | 0.016907 | 0.024268 | 61.473 | 0.14332 | 61.418 | -0.060575 | 0.007032 | 61.5158 | -0.001436 | 61.3031 | 61.4576 | 61.3959 | 61.4199 | 61.4206 | 61.459 | 61.4534 | 61.4607 | 122.9095 | 61.5798 | 122.8545 | 61.3759 | 61.4435 | 122.9523 | 61.435 | 122.7396 | 61.466 | 61.4744 | 61.411 | 61.4194
172.8906 | 123.23 | -61.4227 | 61.5326 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.017953 | 0.00775 | 0.015112 | 61.4776 | 0.13874 | 61.4088 | -0.060575 | 0.01161 | 61.5112 | -0.001436 | 61.2986 | 61.4439 | 61.3776 | 61.4062 | 61.416 | 61.4407 | 61.4305 | 61.4378 | 122.9003 | 61.5615 | 122.8316 | 61.3622 | 61.4343 | 122.934 | 61.4213 | 122.7213 | 61.466 | 61.479 | 61.3972 | 61.4103
173.8906 | 123.2986 | -61.4044 | 61.5326 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.473 | 0.13874 | 61.418 | -0.065154 | 0.007032 | 61.5112 | 0.003143 | 61.3031 | 61.421 | 61.3593 | 61.3878 | 61.4023 | 61.4269 | 61.4167 | 61.4287 | 122.8774 | 61.5432 | 122.8224 | 61.3393 | 61.4115 | 122.9156 | 61.4076 | 122.7076 | 61.466 | 61.4699 | 61.411 | 61.4148
174.8906 | 123.2712 | -61.4594 | 61.5463 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.016907 | 0.028846 | 61.473 | 0.14332 | 61.4134 | -0.051417 | 0.01161 | 61.525 | -0.001436 | 61.2986 | 61.4759 | 61.4188 | 61.4519 | 61.4618 | 61.4865 | 61.4763 | 61.4882 | 122.9324 | 61.6027 | 122.8728 | 61.4079 | 61.471 | 122.9843 | 61.4579 | 122.7579 | 61.4614 | 61.4744 | 61.4018 | 61.4149
175.8906 | 123.23 | -61.4594 | 61.5692 | 0.01197 | -0.049678 | -0.016578 | -0.006703 | 0.022531 | 0.00775 | 0.010533 | 61.473 | 0.13416 | 61.4134 | -0.060575 | 0.007032 | 61.5158 | 0.003143 | 61.3031 | 61.4713 | 61.4097 | 61.4428 | 61.4526 | 61.4819 | 61.4671 | 61.4699 | 122.9324 | 61.5935 | 122.8728 | 61.3988 | 61.4664 | 122.9752 | 61.4625 | 122.7625 | 61.466 | 61.4699 | 61.4064 | 61.4103
176.8906 | 123.2895 | -61.3953 | 61.5372 | 0.016548 | -0.049678 | -0.012 | 0.002454 | 0.022531 | 0.012329 | 0.015112 | 61.4684 | 0.14332 | 61.4043 | -0.055996 | 0.007032 | 61.5158 | 0.007721 | 61.3123 | 61.4118 | 61.3456 | 61.3833 | 61.3977 | 61.4178 | 61.4076 | 61.4104 | 122.8637 | 61.5386 | 122.7995 | 61.3393 | 61.4023 | 122.9111 | 61.403 | 122.7076 | 61.4614 | 61.4607 | 61.3972 | 61.3965
177.8906 | 123.1567 | -61.441 | 61.615 | 0.016548 | -0.040521 | -0.007421 | -0.006703 | 0.027109 | 0.00775 | 0.01969 | 61.473 | 0.13874 | 61.4088 | -0.065154 | 0.002454 | 61.5204 | 0.003143 | 61.3077 | 61.4576 | 61.4005 | 61.4336 | 61.4343 | 61.4681 | 61.4488 | 61.4607 | 122.914 | 61.5798 | 122.8499 | 61.3759 | 61.4435 | 122.9614 | 61.4442 | 122.7488 | 61.4705 | 61.4699 | 61.4064 | 61.4057
178.8906 | 123.2758 | -61.4456 | 61.528 | 0.025705 | -0.0451 | -0.012 | -0.011281 | 0.031687 | 0.016907 | 0.015112 | 61.4684 | 0.14332 | 61.4088 | -0.060575 | 0.007032 | 61.5112 | 0.003143 | 61.2986 | 61.4713 | 61.4005 | 61.4336 | 61.4343 | 61.4773 | 61.4625 | 61.4607 | 122.914 | 61.5889 | 122.8545 | 61.385 | 61.4527 | 122.9568 | 61.4488 | 122.7442 | 61.4614 | 61.4653 | 61.4018 | 61.4057
179.8906 | 123.2712 | -61.4273 | 61.5189 | 0.01197 | -0.049678 | -0.012 | -0.011281 | 0.031687 | 0.012329 | 0.01969 | 61.4776 | 0.13874 | 61.4088 | -0.055996 | 0.007032 | 61.5204 | 0.007721 | 61.3031 | 61.4393 | 61.3776 | 61.4153 | 61.416 | 61.459 | 61.4396 | 61.447 | 122.9049 | 61.566 | 122.8361 | 61.3713 | 61.4343 | 122.9477 | 61.435 | 122.7305 | 61.4705 | 61.4699 | 61.4018 | 61.4011
180.8906 | 123.2529 | -61.4136 | 61.5509 | 0.021127 | -0.0451 | -0.021157 | -0.011281 | 0.027109 | 0.00775 | 0.015112 | 61.473 | 0.13416 | 61.418 | -0.060575 | 0.01161 | 61.5112 | -0.006014 | 61.3077 | 61.4347 | 61.3685 | 61.3924 | 61.4023 | 61.4407 | 61.4213 | 61.4287 | 122.8866 | 61.5477 | 122.8316 | 61.353 | 61.4252 | 122.9248 | 61.4076 | 122.7213 | 61.4614 | 61.479 | 61.4064 | 61.424
181.9062 | 123.2483 | -61.4273 | 61.528 | 0.025705 | -0.049678 | -0.016578 | -0.002124 | 0.017953 | 0.012329 | 0.015112 | 61.4684 | 0.13874 | 61.4088 | -0.065154 | 0.002454 | 61.5158 | -0.001436 | 61.3077 | 61.453 | 61.3776 | 61.4107 | 61.4252 | 61.4453 | 61.4396 | 61.4424 | 122.8957 | 61.566 | 122.8361 | 61.3622 | 61.4298 | 122.9431 | 61.4259 | 122.735 | 61.466 | 61.4699 | 61.4064 | 61.4103
182.8906 | 123.143 | -61.4365 | 61.5829 | 0.016548 | -0.0451 | -0.012 | -0.011281 | 0.027109 | 0.012329 | 0.01969 | 61.4776 | 0.13416 | 61.4134 | -0.069733 | 0.007032 | 61.5112 | -0.001436 | 61.3077 | 61.453 | 61.3914 | 61.4245 | 61.4252 | 61.4636 | 61.4488 | 61.4562 | 122.914 | 61.5706 | 122.8499 | 61.3667 | 61.4435 | 122.9477 | 61.435 | 122.7442 | 61.4705 | 61.479 | 61.4064 | 61.4149
183.8906 | 123.1476 | -61.441 | 61.5875 | 0.016548 | -0.054257 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.015112 | 61.4684 | 0.13874 | 61.4134 | -0.069733 | 0.007032 | 61.5158 | -0.001436 | 61.3077 | 61.4576 | 61.3868 | 61.4245 | 61.4389 | 61.4727 | 61.4534 | 61.4562 | 122.9095 | 61.5798 | 122.8545 | 61.3713 | 61.4481 | 122.9568 | 61.4396 | 122.7488 | 61.4614 | 61.4699 | 61.4064 | 61.4149
184.8906 | 123.1338 | -61.4273 | 61.6196 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.473 | 0.13416 | 61.418 | -0.060575 | 0.007032 | 61.5158 | 0.012299 | 61.3031 | 61.4484 | 61.3868 | 61.4107 | 61.4298 | 61.4544 | 61.4351 | 61.4516 | 122.9003 | 61.5615 | 122.8453 | 61.3667 | 61.4343 | 122.9431 | 61.4396 | 122.7305 | 61.466 | 61.4607 | 61.411 | 61.4057
185.8906 | 123.1888 | -61.4136 | 61.6562 | 0.016548 | -0.040521 | -0.007421 | -0.006703 | 0.027109 | 0.003172 | 0.015112 | 61.4684 | 0.14332 | 61.4134 | -0.051417 | 0.007032 | 61.5158 | 0.007721 | 61.3077 | 61.4301 | 61.3731 | 61.4062 | 61.4069 | 61.4407 | 61.4167 | 61.4287 | 122.882 | 61.5569 | 122.827 | 61.3622 | 61.4206 | 122.9294 | 61.4213 | 122.7213 | 61.4614 | 61.4607 | 61.4064 | 61.4057
186.8906 | 123.2895 | -61.3998 | 61.5738 | 0.016548 | -0.049678 | -0.021157 | -0.002124 | 0.031687 | 0.016907 | 0.028846 | 61.4776 | 0.14332 | 61.4043 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4164 | 61.3502 | 61.3787 | 61.3977 | 61.4315 | 61.4167 | 61.4287 | 122.8774 | 61.5432 | 122.8041 | 61.3393 | 61.4115 | 122.9202 | 61.403 | 122.7076 | 61.466 | 61.4744 | 61.3926 | 61.4011
187.8906 | 123.1247 | -61.4365 | 61.6241 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.4822 | 0.1479 | 61.4088 | -0.055996 | 0.01161 | 61.5158 | 0.007721 | 61.3077 | 61.453 | 61.3914 | 61.4245 | 61.4343 | 61.459 | 61.4488 | 61.4607 | 122.9186 | 61.5844 | 122.8453 | 61.3805 | 61.4481 | 122.9523 | 61.4442 | 122.7442 | 61.4705 | 61.4744 | 61.3972 | 61.4011
188.8906 | 123.2254 | -61.4456 | 61.6058 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.031687 | 0.00775 | 0.015112 | 61.4867 | 0.14332 | 61.4134 | -0.055996 | 0.01161 | 61.5112 | 0.003143 | 61.3031 | 61.4713 | 61.4005 | 61.4245 | 61.4481 | 61.4773 | 61.4534 | 61.4607 | 122.9324 | 61.5889 | 122.859 | 61.3896 | 61.4572 | 122.9568 | 61.4488 | 122.7488 | 61.4751 | 61.4836 | 61.4018 | 61.4103
189.8906 | 123.2254 | -61.4319 | 61.5921 | 0.030283 | -0.049678 | -0.012 | -0.006703 | 0.031687 | 0.00775 | 0.028846 | 61.473 | 0.13416 | 61.4226 | -0.060575 | 0.007032 | 61.5112 | 0.003143 | 61.3077 | 61.4622 | 61.3822 | 61.4199 | 61.4252 | 61.4636 | 61.4396 | 61.4607 | 122.9049 | 61.566 | 122.8545 | 61.3713 | 61.4389 | 122.9431 | 61.435 | 122.7396 | 61.466 | 61.4699 | 61.4155 | 61.4194
190.8906 | 123.1567 | -61.4273 | 61.5921 | 0.016548 | -0.049678 | -0.012 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4867 | 0.1479 | 61.4134 | -0.051417 | 0.01161 | 61.5204 | 0.003143 | 61.2986 | 61.4439 | 61.3776 | 61.4153 | 61.4206 | 61.4498 | 61.4396 | 61.447 | 122.914 | 61.5752 | 122.8407 | 61.3759 | 61.4389 | 122.9477 | 61.4305 | 122.7259 | 61.4751 | 61.4836 | 61.4018 | 61.4103
191.8906 | 123.2071 | -61.441 | 61.5875 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.01969 | 61.4822 | 0.14332 | 61.4088 | -0.055996 | 0.007032 | 61.5158 | -0.006014 | 61.3077 | 61.4576 | 61.4005 | 61.4245 | 61.4435 | 61.4727 | 61.4534 | 61.4607 | 122.9232 | 61.5844 | 122.8499 | 61.385 | 61.4481 | 122.9568 | 61.435 | 122.7488 | 61.4751 | 61.4882 | 61.4018 | 61.4149
192.8906 | 123.2117 | -61.4502 | 61.5829 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.01969 | 61.4684 | 0.13874 | 61.4134 | -0.060575 | 0.016188 | 61.5204 | 0.003143 | 61.3077 | 61.4713 | 61.4097 | 61.4382 | 61.4526 | 61.4773 | 61.4625 | 61.4699 | 122.9186 | 61.5889 | 122.8636 | 61.3896 | 61.4664 | 122.9706 | 61.4533 | 122.7579 | 61.4522 | 61.4653 | 61.3972 | 61.4103
193.8906 | 123.1979 | -61.4044 | 61.5829 | 0.021127 | -0.0451 | -0.012 | -0.006703 | 0.022531 | 0.016907 | 0.015112 | 61.4638 | 0.13874 | 61.4134 | -0.060575 | 0.007032 | 61.5158 | -0.001436 | 61.3077 | 61.4255 | 61.3593 | 61.3924 | 61.3977 | 61.4269 | 61.4213 | 61.4195 | 122.8683 | 61.5432 | 122.8178 | 61.3438 | 61.4115 | 122.9202 | 61.403 | 122.7121 | 61.4568 | 61.4653 | 61.4064 | 61.4149
194.8906 | 123.1934 | -61.4685 | 61.5372 | 0.021127 | -0.040521 | -0.007421 | -0.006703 | 0.031687 | 0.00775 | 0.024268 | 61.4776 | 0.14332 | 61.418 | -0.055996 | 0.007032 | 61.5204 | -0.001436 | 61.3031 | 61.4896 | 61.428 | 61.4611 | 61.4618 | 61.5002 | 61.4763 | 61.4928 | 122.9461 | 61.6118 | 122.8865 | 61.4125 | 61.4755 | 122.9889 | 61.4671 | 122.7717 | 61.4705 | 61.479 | 61.411 | 61.4194
195.8906 | 123.2574 | -61.4182 | 61.5601 | 0.025705 | -0.054257 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.015112 | 61.4776 | 0.14332 | 61.418 | -0.055996 | 0.016188 | 61.5204 | -0.001436 | 61.2986 | 61.4439 | 61.3639 | 61.4062 | 61.4114 | 61.4407 | 61.4259 | 61.4333 | 122.8957 | 61.5615 | 122.8361 | 61.3622 | 61.4343 | 122.9385 | 61.4167 | 122.7167 | 61.4614 | 61.479 | 61.4018 | 61.4194
196.8906 | 123.1979 | -61.4319 | 61.5875 | 0.01197 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.14332 | 61.4134 | -0.055996 | 0.002454 | 61.5204 | -0.001436 | 61.3031 | 61.4439 | 61.3868 | 61.4153 | 61.4343 | 61.4544 | 61.4442 | 61.4516 | 122.9095 | 61.5752 | 122.8453 | 61.3759 | 61.4343 | 122.9523 | 61.4304 | 122.735 | 61.4751 | 61.479 | 61.411 | 61.4149
197.8906 | 123.317 | -61.4365 | 61.5143 | 0.01197 | -0.049678 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.015112 | 61.4684 | 0.13874 | 61.4088 | -0.055996 | 0.01161 | 61.5204 | -0.001436 | 61.2986 | 61.4484 | 61.3868 | 61.4199 | 61.4298 | 61.4636 | 61.4534 | 61.4516 | 122.9049 | 61.5752 | 122.8453 | 61.3805 | 61.4481 | 122.9568 | 61.435 | 122.735 | 61.4568 | 61.4699 | 61.3972 | 61.4103
198.8906 | 123.1613 | -61.4456 | 61.5555 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.016907 | 0.01969 | 61.4822 | 0.14332 | 61.418 | -0.055996 | 0.01161 | 61.5158 | -0.001436 | 61.3031 | 61.4622 | 61.4005 | 61.4336 | 61.4435 | 61.4681 | 61.4625 | 61.4653 | 122.9278 | 61.5889 | 122.8636 | 61.3896 | 61.4572 | 122.9614 | 61.4442 | 122.7488 | 61.4705 | 61.4836 | 61.4064 | 61.4194
199.8906 | 123.1705 | -61.4456 | 61.5921 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | 0.00775 | 0.01969 | 61.4822 | 0.14332 | 61.418 | -0.055996 | 0.007032 | 61.5158 | -0.001436 | 61.3077 | 61.4713 | 61.4005 | 61.429 | 61.4481 | 61.4681 | 61.4534 | 61.4653 | 122.9278 | 61.5889 | 122.8636 | 61.3896 | 61.4527 | 122.9614 | 61.4442 | 122.7533 | 61.4751 | 61.4836 | 61.411 | 61.4194
200.8906 | 123.2849 | -61.4182 | 61.5189 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.022531 | 0.012329 | 0.015112 | 61.473 | 0.13874 | 61.4088 | -0.055996 | 0.01161 | 61.5158 | 0.003143 | 61.2986 | 61.4393 | 61.3731 | 61.4016 | 61.4114 | 61.4407 | 61.4305 | 61.4333 | 122.8912 | 61.5569 | 122.827 | 61.3622 | 61.4298 | 122.934 | 61.4213 | 122.7167 | 61.4614 | 61.4699 | 61.3972 | 61.4057
201.8906 | 123.1613 | -61.4731 | 61.5692 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.4822 | 0.15248 | 61.4088 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.2986 | 61.4942 | 61.428 | 61.4611 | 61.471 | 61.5048 | 61.4763 | 61.4974 | 122.9552 | 61.6256 | 122.8819 | 61.4125 | 61.4847 | 122.9935 | 61.4762 | 122.7717 | 61.4705 | 61.479 | 61.3972 | 61.4057
202.8906 | 123.2529 | -61.4182 | 61.5189 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.031687 | 0.00775 | 0.01969 | 61.4822 | 0.15248 | 61.4088 | -0.060575 | 0.002454 | 61.5158 | -0.001436 | 61.3031 | 61.4393 | 61.3731 | 61.4016 | 61.4114 | 61.4498 | 61.4259 | 61.4378 | 122.9003 | 61.5706 | 122.827 | 61.3576 | 61.4206 | 122.934 | 61.4167 | 122.7213 | 61.4797 | 61.4836 | 61.4064 | 61.4103
203.8906 | 123.1293 | -61.4456 | 61.5784 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.024268 | 61.473 | 0.13416 | 61.4134 | -0.055996 | 0.007032 | 61.5204 | 0.003143 | 61.3031 | 61.4713 | 61.4005 | 61.4336 | 61.4389 | 61.4727 | 61.4534 | 61.4699 | 122.9186 | 61.5798 | 122.859 | 61.3896 | 61.4527 | 122.966 | 61.4488 | 122.7488 | 61.466 | 61.4699 | 61.4064 | 61.4103
204.8906 | 123.175 | -61.4365 | 61.5784 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.024268 | 61.473 | 0.1479 | 61.4226 | -0.065154 | 0.01161 | 61.5204 | 0.003143 | 61.3031 | 61.4576 | 61.3959 | 61.4199 | 61.4298 | 61.4636 | 61.4534 | 61.4607 | 122.9095 | 61.5844 | 122.859 | 61.3713 | 61.4481 | 122.9568 | 61.4396 | 122.7396 | 61.4614 | 61.4699 | 61.411 | 61.4194
205.8906 | 123.262 | -61.441 | 61.5417 | 0.021127 | -0.054257 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.14332 | 61.4134 | -0.065154 | 0.002454 | 61.5204 | 0.003143 | 61.3031 | 61.4622 | 61.3868 | 61.4245 | 61.4389 | 61.4636 | 61.4534 | 61.4607 | 122.9186 | 61.5844 | 122.8545 | 61.3759 | 61.4435 | 122.9614 | 61.4442 | 122.7442 | 61.4751 | 61.4744 | 61.411 | 61.4103
206.8906 | 123.1522 | -61.4365 | 61.5784 | 0.021127 | -0.040521 | -0.012 | -0.006703 | 0.027109 | 0.012329 | 0.024268 | 61.4822 | 0.13874 | 61.4134 | -0.065154 | 0.007032 | 61.5204 | 0.003143 | 61.2986 | 61.4576 | 61.3959 | 61.4245 | 61.4298 | 61.4636 | 61.4488 | 61.4607 | 122.9186 | 61.5752 | 122.8499 | 61.3713 | 61.4435 | 122.9568 | 61.4396 | 122.735 | 61.4751 | 61.479 | 61.4064 | 61.4103
207.8906 | 123.2025 | -61.4502 | 61.5234 | 0.025705 | -0.049678 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.010533 | 61.4776 | 0.1479 | 61.418 | -0.055996 | 0.007032 | 61.525 | 0.003143 | 61.3031 | 61.4759 | 61.4005 | 61.4382 | 61.4481 | 61.4773 | 61.4579 | 61.4607 | 122.9278 | 61.5981 | 122.8682 | 61.3942 | 61.4572 | 122.9752 | 61.4533 | 122.7533 | 61.4705 | 61.4744 | 61.411 | 61.4148
208.8906 | 122.937 | -61.4685 | 61.4822 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.4822 | 0.13874 | 61.418 | -0.060575 | -0.002124 | 61.5158 | -0.001436 | 61.3031 | 61.4942 | 61.428 | 61.4519 | 61.4664 | 61.491 | 61.4717 | 61.4928 | 122.9507 | 61.6072 | 122.8865 | 61.4079 | 61.4664 | 122.9843 | 61.4671 | 122.7717 | 61.4843 | 61.4836 | 61.4201 | 61.4194
209.8906 | 123.2437 | -61.4136 | 61.5234 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | 0.016907 | 0.015112 | 61.4822 | 0.14332 | 61.4134 | -0.065154 | 0.007032 | 61.5158 | 0.007721 | 61.2986 | 61.4347 | 61.3731 | 61.3924 | 61.416 | 61.4407 | 61.4305 | 61.4287 | 122.8957 | 61.5569 | 122.827 | 61.3484 | 61.4206 | 122.9294 | 61.4213 | 122.7121 | 61.4751 | 61.4744 | 61.4064 | 61.4057
210.8906 | 123.2849 | -61.4365 | 61.5829 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.015112 | 61.4822 | 0.14332 | 61.418 | -0.055996 | 0.01161 | 61.5158 | 0.012299 | 61.3077 | 61.453 | 61.3959 | 61.4199 | 61.4343 | 61.4636 | 61.4396 | 61.4516 | 122.9186 | 61.5798 | 122.8545 | 61.3805 | 61.4481 | 122.9523 | 61.4488 | 122.7442 | 61.4705 | 61.4699 | 61.4064 | 61.4057
211.8906 | 123.0881 | -61.4685 | 61.5555 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.022531 | 0.016907 | 0.024268 | 61.4913 | 0.14332 | 61.4226 | -0.055996 | 0.002454 | 61.5112 | 0.003143 | 61.2986 | 61.4896 | 61.4326 | 61.4519 | 61.471 | 61.491 | 61.4854 | 61.4928 | 122.9598 | 61.6118 | 122.8911 | 61.4125 | 61.471 | 122.9797 | 61.4716 | 122.7671 | 61.4889 | 61.4882 | 61.4201 | 61.4194
212.8906 | 123.1842 | -61.4502 | 61.5692 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.012329 | 0.01969 | 61.4822 | 0.14332 | 61.4271 | -0.065154 | 0.01161 | 61.5158 | -0.006014 | 61.3077 | 61.4759 | 61.4051 | 61.4382 | 61.4435 | 61.4773 | 61.4625 | 61.4699 | 122.9324 | 61.5935 | 122.8773 | 61.385 | 61.4618 | 122.966 | 61.4442 | 122.7579 | 61.4705 | 61.4882 | 61.4155 | 61.4332
213.8906 | 123.2117 | -61.4319 | 61.5692 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.024268 | 61.473 | 0.12958 | 61.4134 | -0.060575 | 0.002454 | 61.5158 | 0.003143 | 61.2986 | 61.4576 | 61.3914 | 61.4153 | 61.4298 | 61.4636 | 61.4442 | 61.4562 | 122.9049 | 61.5615 | 122.8453 | 61.3713 | 61.4343 | 122.9477 | 61.435 | 122.7305 | 61.4705 | 61.4699 | 61.411 | 61.4103
214.8906 | 123.2346 | -61.4273 | 61.5189 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.473 | 0.14332 | 61.4226 | -0.055996 | 0.007032 | 61.5204 | 0.003143 | 61.2986 | 61.4484 | 61.3868 | 61.4153 | 61.4252 | 61.4544 | 61.4396 | 61.447 | 122.9003 | 61.5706 | 122.8499 | 61.3713 | 61.4343 | 122.9477 | 61.4305 | 122.7259 | 61.466 | 61.4699 | 61.4155 | 61.4194
215.8906 | 123.175 | -61.4594 | 61.5692 | 0.016548 | -0.040521 | -0.007421 | -0.002124 | 0.036265 | 0.016907 | 0.028846 | 61.4822 | 0.14332 | 61.4134 | -0.051417 | 0.016188 | 61.5158 | -0.001436 | 61.2986 | 61.4759 | 61.4188 | 61.4519 | 61.4572 | 61.4956 | 61.4763 | 61.4882 | 122.9415 | 61.6027 | 122.8728 | 61.4079 | 61.4755 | 122.9752 | 61.4579 | 122.7579 | 61.466 | 61.4836 | 61.3972 | 61.4149
216.8906 | 123.111 | -61.4639 | 61.5509 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.003172 | 0.015112 | 61.4776 | 0.1479 | 61.4134 | -0.060575 | 0.007032 | 61.5341 | 0.003143 | 61.3077 | 61.4896 | 61.4188 | 61.4519 | 61.4618 | 61.4956 | 61.4671 | 61.479 | 122.9415 | 61.6118 | 122.8773 | 61.4034 | 61.471 | 122.998 | 61.4671 | 122.7717 | 61.4705 | 61.4744 | 61.4064 | 61.4103
217.8906 | 123.2849 | -61.4273 | 61.5189 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.031687 | 0.012329 | 0.01969 | 61.4776 | 0.14332 | 61.418 | -0.060575 | 0.002454 | 61.5204 | 0.003143 | 61.2986 | 61.453 | 61.3868 | 61.4107 | 61.4206 | 61.459 | 61.4396 | 61.447 | 122.9049 | 61.5706 | 122.8453 | 61.3667 | 61.4298 | 122.9477 | 61.4305 | 122.7259 | 61.4751 | 61.4744 | 61.4155 | 61.4148
218.8906 | 123.2529 | -61.4456 | 61.5326 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.016907 | 0.024268 | 61.4822 | 0.1479 | 61.4088 | -0.060575 | 0.002454 | 61.5158 | -0.001436 | 61.3031 | 61.4622 | 61.4051 | 61.4336 | 61.4389 | 61.4681 | 61.4625 | 61.4699 | 122.9278 | 61.5935 | 122.8545 | 61.385 | 61.4481 | 122.9614 | 61.4442 | 122.7488 | 61.4797 | 61.4836 | 61.4064 | 61.4103
219.8906 | 123.1934 | -61.4365 | 61.5601 | 0.016548 | -0.0451 | -0.007421 | -0.011281 | 0.027109 | 0.00775 | 0.024268 | 61.4776 | 0.1479 | 61.4134 | -0.055996 | -0.002124 | 61.5158 | -0.001436 | 61.2986 | 61.453 | 61.3914 | 61.429 | 61.4252 | 61.4636 | 61.4442 | 61.4607 | 122.914 | 61.5844 | 122.8499 | 61.3805 | 61.4343 | 122.9523 | 61.435 | 122.735 | 61.4797 | 61.479 | 61.4155 | 61.4149
220.8906 | 123.1659 | -61.4502 | 61.5555 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4822 | 0.1479 | 61.4226 | -0.065154 | 0.002454 | 61.5158 | -0.001436 | 61.2986 | 61.4667 | 61.4097 | 61.4336 | 61.4481 | 61.4773 | 61.4579 | 61.4699 | 122.9324 | 61.5981 | 122.8728 | 61.385 | 61.4526 | 122.966 | 61.4488 | 122.7488 | 61.4797 | 61.4836 | 61.4201 | 61.424
221.8906 | 123.1567 | -61.441 | 61.5646 | 0.025705 | -0.035942 | -0.007421 | -0.002124 | 0.022531 | 0.003172 | 0.01969 | 61.4822 | 0.1479 | 61.4134 | -0.060575 | 0.002454 | 61.5158 | 0.012299 | 61.2986 | 61.4667 | 61.4051 | 61.4336 | 61.4389 | 61.4636 | 61.4442 | 61.4607 | 122.9232 | 61.5889 | 122.8545 | 61.3805 | 61.4435 | 122.9568 | 61.4533 | 122.7396 | 61.4797 | 61.4699 | 61.411 | 61.4011
222.8906 | 123.2025 | -61.4136 | 61.5326 | 0.016548 | -0.049678 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4776 | 0.15248 | 61.4134 | -0.060575 | 0.007032 | 61.5158 | 0.007721 | 61.2986 | 61.4301 | 61.3639 | 61.4016 | 61.4114 | 61.4407 | 61.4213 | 61.4333 | 122.8912 | 61.5661 | 122.827 | 61.353 | 61.4206 | 122.9294 | 61.4213 | 122.7121 | 61.4705 | 61.4699 | 61.4064 | 61.4057
223.8906 | 123.23 | -61.409 | 61.5417 | 0.021127 | -0.049678 | -0.021157 | -0.006703 | 0.027109 | 0.012329 | 0.015112 | 61.4822 | 0.1479 | 61.4088 | -0.060575 | 0.007032 | 61.525 | 0.003143 | 61.294 | 61.4301 | 61.3593 | 61.3878 | 61.4023 | 61.4361 | 61.4213 | 61.4241 | 122.8912 | 61.5569 | 122.8178 | 61.3484 | 61.416 | 122.934 | 61.4121 | 122.703 | 61.4751 | 61.479 | 61.4018 | 61.4057
224.8906 | 123.2117 | -61.4502 | 61.5372 | 0.016548 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.473 | 0.1479 | 61.418 | -0.060575 | 0.007032 | 61.525 | -0.001436 | 61.2986 | 61.4667 | 61.4097 | 61.429 | 61.4481 | 61.4773 | 61.4625 | 61.4699 | 122.9232 | 61.5981 | 122.8682 | 61.3896 | 61.4572 | 122.9752 | 61.4488 | 122.7488 | 61.466 | 61.4744 | 61.411 | 61.4194
225.8906 | 123.317 | -61.4273 | 61.5005 | 0.016548 | -0.040521 | -0.016578 | -0.011281 | 0.027109 | 0.00775 | 0.015112 | 61.4776 | 0.14332 | 61.418 | -0.065154 | 0.007032 | 61.5204 | 0.003143 | 61.3031 | 61.4439 | 61.3868 | 61.4107 | 61.416 | 61.4544 | 61.4351 | 61.4424 | 122.9049 | 61.5706 | 122.8453 | 61.3622 | 61.4343 | 122.9477 | 61.4305 | 122.7305 | 61.4705 | 61.4744 | 61.411 | 61.4148
226.8906 | 123.2803 | -61.4182 | 61.5189 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.028846 | 61.4776 | 0.14332 | 61.418 | -0.069733 | 0.01161 | 61.5158 | 0.003143 | 61.3031 | 61.4347 | 61.3776 | 61.4062 | 61.4114 | 61.4407 | 61.4259 | 61.447 | 122.8957 | 61.5615 | 122.8361 | 61.3484 | 61.4298 | 122.934 | 61.4213 | 122.7213 | 61.466 | 61.4744 | 61.4064 | 61.4148
227.8906 | 123.2666 | -61.4319 | 61.5372 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.017953 | 0.012329 | 0.015112 | 61.4776 | 0.14332 | 61.418 | -0.060575 | 0.01161 | 61.5112 | 0.003143 | 61.2986 | 61.4484 | 61.3868 | 61.4199 | 61.4298 | 61.4498 | 61.4442 | 61.447 | 122.9095 | 61.5752 | 122.8499 | 61.3713 | 61.4435 | 122.9431 | 61.435 | 122.7305 | 61.466 | 61.4744 | 61.4064 | 61.4148
228.8906 | 123.2849 | -61.3815 | 61.5097 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.022531 | 0.003172 | 0.01969 | 61.4776 | 0.13874 | 61.418 | -0.065154 | 0.01161 | 61.5158 | 0.007721 | 61.3031 | 61.4072 | 61.3364 | 61.3695 | 61.3748 | 61.4041 | 61.3847 | 61.4012 | 122.8591 | 61.5203 | 122.7995 | 61.3164 | 61.3931 | 122.8973 | 61.3893 | 122.6847 | 61.466 | 61.4699 | 61.4064 | 61.4103
229.8906 | 123.2712 | -61.441 | 61.5372 | 0.016548 | -0.0451 | -0.007421 | -0.006703 | 0.022531 | 0.003172 | 0.01969 | 61.473 | 0.15248 | 61.4134 | -0.065154 | 0.007032 | 61.5204 | 0.003143 | 61.3077 | 61.4576 | 61.3959 | 61.4336 | 61.4343 | 61.4636 | 61.4442 | 61.4607 | 122.914 | 61.5935 | 122.8545 | 61.3759 | 61.4481 | 122.9614 | 61.4442 | 122.7488 | 61.466 | 61.4699 | 61.4064 | 61.4103
230.8906 | 123.2391 | -61.4502 | 61.528 | 0.016548 | -0.0451 | -0.021157 | -0.006703 | 0.036265 | 0.012329 | 0.010533 | 61.473 | 0.1479 | 61.4134 | -0.060575 | 0.002454 | 61.5204 | 0.003143 | 61.2986 | 61.4667 | 61.4051 | 61.429 | 61.4435 | 61.4865 | 61.4625 | 61.4607 | 122.9232 | 61.5981 | 122.8636 | 61.3896 | 61.4526 | 122.9706 | 61.4533 | 122.7488 | 61.4705 | 61.4699 | 61.411 | 61.4103
231.8906 | 123.262 | -61.4136 | 61.5143 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.4822 | 0.14332 | 61.418 | -0.060575 | 0.01161 | 61.5204 | 0.007721 | 61.2986 | 61.4347 | 61.3685 | 61.397 | 61.4114 | 61.4361 | 61.4167 | 61.4378 | 122.8957 | 61.5569 | 122.8316 | 61.353 | 61.4252 | 122.934 | 61.4213 | 122.7121 | 61.4705 | 61.4744 | 61.4064 | 61.4103
232.8906 | 123.2529 | -61.4319 | 61.5463 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.015112 | 61.4776 | 0.1479 | 61.418 | -0.055996 | 0.007032 | 61.5158 | -0.001436 | 61.3031 | 61.4576 | 61.3868 | 61.4199 | 61.4298 | 61.459 | 61.4396 | 61.447 | 122.9095 | 61.5798 | 122.8499 | 61.3759 | 61.4389 | 122.9477 | 61.4304 | 122.735 | 61.4705 | 61.479 | 61.411 | 61.4194
233.8906 | 123.262 | -61.441 | 61.5005 | 0.01197 | -0.035942 | -0.012 | 0.002454 | 0.017953 | 0.016907 | 0.028846 | 61.4822 | 0.1479 | 61.4226 | -0.065154 | 0.01161 | 61.5204 | 0.003143 | 61.3031 | 61.453 | 61.4051 | 61.429 | 61.4435 | 61.459 | 61.4579 | 61.4699 | 122.9232 | 61.5889 | 122.8636 | 61.3759 | 61.4526 | 122.9614 | 61.4442 | 122.7442 | 61.4705 | 61.479 | 61.411 | 61.4194
234.8906 | 123.2483 | -61.4456 | 61.5417 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.010533 | 61.473 | 0.14332 | 61.4134 | -0.055996 | 0.01161 | 61.5204 | 0.012299 | 61.294 | 61.4667 | 61.4005 | 61.429 | 61.4435 | 61.4681 | 61.4579 | 61.4562 | 122.9186 | 61.5889 | 122.859 | 61.3896 | 61.4572 | 122.966 | 61.4579 | 122.7396 | 61.4614 | 61.4607 | 61.4018 | 61.4011
235.8906 | 123.2254 | -61.4319 | 61.5509 | 0.016548 | -0.049678 | -0.021157 | -0.006703 | 0.022531 | 0.012329 | 0.024268 | 61.473 | 0.13416 | 61.4134 | -0.060575 | 0.002454 | 61.5204 | 0.003143 | 61.2986 | 61.4484 | 61.3822 | 61.4107 | 61.4252 | 61.4544 | 61.4442 | 61.4562 | 122.9049 | 61.566 | 122.8453 | 61.3713 | 61.4343 | 122.9523 | 61.435 | 122.7305 | 61.4705 | 61.4699 | 61.411 | 61.4103
236.8906 | 123.23 | -61.4182 | 61.528 | 0.016548 | -0.049678 | -0.025735 | -0.006703 | 0.027109 | 0.012329 | 0.024268 | 61.4867 | 0.14332 | 61.4134 | -0.051417 | 0.007032 | 61.5204 | 0.007721 | 61.2986 | 61.4347 | 61.3685 | 61.3924 | 61.4114 | 61.4453 | 61.4305 | 61.4424 | 122.9049 | 61.5615 | 122.8316 | 61.3667 | 61.4252 | 122.9385 | 61.4259 | 122.7167 | 61.4797 | 61.479 | 61.4064 | 61.4057
237.8906 | 123.2162 | -61.409 | 61.5784 | 0.021127 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4822 | 0.14332 | 61.418 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3123 | 61.4301 | 61.3685 | 61.397 | 61.4023 | 61.4315 | 61.4213 | 61.4287 | 122.8912 | 61.5523 | 122.827 | 61.353 | 61.4206 | 122.9294 | 61.4167 | 122.7213 | 61.4705 | 61.4744 | 61.4064 | 61.4103
238.8906 | 123.2346 | -61.4365 | 61.5463 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.017953 | 0.012329 | 0.015112 | 61.4776 | 0.1479 | 61.418 | -0.055996 | 0.01161 | 61.5158 | 0.003143 | 61.2986 | 61.453 | 61.3914 | 61.4199 | 61.4343 | 61.4544 | 61.4488 | 61.4516 | 122.914 | 61.5844 | 122.8545 | 61.3805 | 61.4481 | 122.9523 | 61.4396 | 122.735 | 61.466 | 61.4744 | 61.4064 | 61.4148
239.8906 | 123.2117 | -61.4502 | 61.5372 | 0.021127 | -0.0451 | -0.007421 | -0.006703 | 0.017953 | 0.012329 | 0.015112 | 61.4684 | 0.14332 | 61.4134 | -0.060575 | 0.007032 | 61.5112 | 0.003143 | 61.3031 | 61.4713 | 61.4051 | 61.4428 | 61.4435 | 61.4681 | 61.4625 | 61.4653 | 122.9186 | 61.5935 | 122.8636 | 61.3896 | 61.4572 | 122.9614 | 61.4533 | 122.7533 | 61.4614 | 61.4653 | 61.4064 | 61.4103
240.8906 | 123.23 | -61.4365 | 61.5372 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.027109 | 0.012329 | 0.024268 | 61.4822 | 0.15706 | 61.4088 | -0.065154 | 0.007032 | 61.5204 | 0.003143 | 61.2986 | 61.453 | 61.3959 | 61.4245 | 61.4298 | 61.4636 | 61.4488 | 61.4607 | 122.9186 | 61.5935 | 122.8453 | 61.3713 | 61.4435 | 122.9568 | 61.4396 | 122.735 | 61.4751 | 61.479 | 61.4018 | 61.4057
241.8906 | 123.2849 | -61.4456 | 61.5555 | 0.025705 | -0.054257 | -0.007421 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.15248 | 61.418 | -0.055996 | 0.007032 | 61.5066 | 0.003143 | 61.2986 | 61.4713 | 61.3914 | 61.4382 | 61.4435 | 61.4681 | 61.4579 | 61.4653 | 122.9232 | 61.5981 | 122.8636 | 61.3896 | 61.4527 | 122.9523 | 61.4488 | 122.7442 | 61.4705 | 61.4744 | 61.411 | 61.4148
242.8906 | 123.2529 | -61.4227 | 61.5921 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.017953 | 0.012329 | 0.01969 | 61.4776 | 0.14332 | 61.4134 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3031 | 61.4393 | 61.3822 | 61.4062 | 61.4206 | 61.4407 | 61.4351 | 61.4424 | 122.9003 | 61.566 | 122.8361 | 61.3667 | 61.4389 | 122.9477 | 61.4304 | 122.7259 | 61.4614 | 61.4699 | 61.3972 | 61.4057
243.8906 | 123.3124 | -61.409 | 61.5646 | 0.021127 | -0.0451 | -0.021157 | -0.002124 | 0.027109 | 0.00775 | 0.015112 | 61.4776 | 0.15248 | 61.4088 | -0.051417 | 0.01161 | 61.5204 | -0.001436 | 61.2986 | 61.4301 | 61.3639 | 61.3878 | 61.4069 | 61.4361 | 61.4167 | 61.4241 | 122.8866 | 61.5615 | 122.8178 | 61.3576 | 61.4206 | 122.9294 | 61.4076 | 122.7076 | 61.466 | 61.479 | 61.3972 | 61.4103
244.8906 | 123.262 | -61.4182 | 61.5555 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.1479 | 61.4226 | -0.055996 | 0.020767 | 61.525 | -0.001436 | 61.3031 | 61.4347 | 61.3776 | 61.4062 | 61.416 | 61.4407 | 61.4305 | 61.4378 | 122.8957 | 61.5661 | 122.8407 | 61.3622 | 61.4389 | 122.9431 | 61.4167 | 122.7213 | 61.4568 | 61.479 | 61.4018 | 61.424
245.8906 | 123.2712 | -61.4182 | 61.5326 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4776 | 0.14332 | 61.418 | -0.060575 | 0.007032 | 61.5158 | 0.003143 | 61.3031 | 61.4439 | 61.3776 | 61.4062 | 61.416 | 61.4453 | 61.4259 | 61.4378 | 122.8957 | 61.5615 | 122.8361 | 61.3576 | 61.4252 | 122.934 | 61.4213 | 122.7213 | 61.4705 | 61.4744 | 61.411 | 61.4148
246.8906 | 123.2803 | -61.409 | 61.5509 | 0.021127 | -0.0451 | -0.021157 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.1479 | 61.4088 | -0.055996 | 0.016188 | 61.5204 | 0.003143 | 61.3031 | 61.4301 | 61.3639 | 61.3878 | 61.4069 | 61.4315 | 61.4213 | 61.4287 | 122.8866 | 61.5569 | 122.8178 | 61.353 | 61.4252 | 122.9294 | 61.4121 | 122.7121 | 61.4614 | 61.4744 | 61.3926 | 61.4057
247.8906 | 123.2437 | -61.3998 | 61.5555 | 0.021127 | -0.049678 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4867 | 0.14332 | 61.418 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.421 | 61.3502 | 61.3833 | 61.3977 | 61.4224 | 61.4122 | 61.4195 | 122.8866 | 61.5432 | 122.8178 | 61.3438 | 61.4115 | 122.9202 | 61.4076 | 122.7076 | 61.4751 | 61.479 | 61.4064 | 61.4103
248.8906 | 123.2574 | -61.4365 | 61.5326 | 0.01197 | -0.049678 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.01969 | 61.4776 | 0.14332 | 61.4134 | -0.065154 | 0.016188 | 61.5204 | 0.003143 | 61.3123 | 61.4484 | 61.3868 | 61.4245 | 61.4298 | 61.4636 | 61.4442 | 61.4562 | 122.914 | 61.5798 | 122.8499 | 61.3713 | 61.4526 | 122.9568 | 61.4396 | 122.7488 | 61.4614 | 61.4744 | 61.3972 | 61.4103
249.8906 | 123.2666 | -61.4319 | 61.5738 | 0.016548 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.015112 | 61.4776 | 0.14332 | 61.4226 | -0.055996 | 0.002454 | 61.5112 | 0.007721 | 61.2986 | 61.4484 | 61.3868 | 61.4199 | 61.4252 | 61.459 | 61.4396 | 61.447 | 122.9095 | 61.5752 | 122.8545 | 61.3759 | 61.4343 | 122.9431 | 61.4396 | 122.7305 | 61.4751 | 61.4699 | 61.4201 | 61.4149
250.8906 | 123.2483 | -61.4502 | 61.5875 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.016907 | 0.01969 | 61.4822 | 0.1479 | 61.418 | -0.060575 | 0.016188 | 61.5158 | 0.007721 | 61.2986 | 61.4713 | 61.4097 | 61.4382 | 61.4481 | 61.4819 | 61.4671 | 61.4699 | 122.9324 | 61.5981 | 122.8682 | 61.3896 | 61.4664 | 122.966 | 61.4579 | 122.7488 | 61.466 | 61.4744 | 61.4018 | 61.4103
251.8906 | 123.143 | -61.4456 | 61.6104 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.4822 | 0.14332 | 61.418 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4667 | 61.4005 | 61.4336 | 61.4435 | 61.4727 | 61.4534 | 61.4699 | 122.9278 | 61.5889 | 122.8636 | 61.385 | 61.4572 | 122.966 | 61.4488 | 122.7533 | 61.4705 | 61.479 | 61.4064 | 61.4148
252.8906 | 123.262 | -61.4136 | 61.5692 | 0.016548 | -0.049678 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.015112 | 61.4776 | 0.15248 | 61.4226 | -0.055996 | 0.016188 | 61.5112 | -0.001436 | 61.3077 | 61.4301 | 61.3639 | 61.4016 | 61.4114 | 61.4361 | 61.4259 | 61.4287 | 122.8912 | 61.5661 | 122.8361 | 61.3576 | 61.4298 | 122.9248 | 61.4121 | 122.7213 | 61.4614 | 61.479 | 61.4064 | 61.424
253.8906 | 123.1979 | -61.4182 | 61.5509 | 0.021127 | -0.054257 | -0.016578 | -0.006703 | 0.031687 | 0.003172 | 0.010533 | 61.4867 | 0.1479 | 61.4226 | -0.055996 | 0.01161 | 61.5158 | 0.003143 | 61.3077 | 61.4393 | 61.3639 | 61.4016 | 61.4114 | 61.4498 | 61.4213 | 61.4287 | 122.9049 | 61.5661 | 122.8407 | 61.3622 | 61.4298 | 122.934 | 61.4213 | 122.7259 | 61.4751 | 61.4836 | 61.411 | 61.4194
254.8906 | 123.1613 | -61.4822 | 61.5417 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.4867 | 0.1479 | 61.4271 | -0.069733 | 0.007032 | 61.5204 | 0.003143 | 61.2986 | 61.5034 | 61.4371 | 61.4657 | 61.4847 | 61.5048 | 61.4946 | 61.5019 | 122.969 | 61.6301 | 122.9094 | 61.4125 | 61.4893 | 123.0026 | 61.4854 | 122.7808 | 61.4797 | 61.4836 | 61.4201 | 61.424
255.8906 | 123.3124 | -61.4182 | 61.5555 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4822 | 0.1479 | 61.4134 | -0.055996 | 0.016188 | 61.5204 | -0.001436 | 61.3123 | 61.4439 | 61.3776 | 61.397 | 61.416 | 61.4453 | 61.4305 | 61.4378 | 122.9003 | 61.5661 | 122.8316 | 61.3622 | 61.4343 | 122.9385 | 61.4167 | 122.7305 | 61.466 | 61.4836 | 61.3972 | 61.4149
256.8906 | 123.2803 | -61.4227 | 61.5646 | 0.016548 | -0.0451 | -0.021157 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4822 | 0.1479 | 61.4226 | -0.060575 | 0.007032 | 61.5204 | 0.007721 | 61.2986 | 61.4393 | 61.3776 | 61.4016 | 61.4206 | 61.4498 | 61.4305 | 61.4424 | 122.9049 | 61.5706 | 122.8453 | 61.3622 | 61.4298 | 122.9431 | 61.4304 | 122.7213 | 61.4751 | 61.4744 | 61.4155 | 61.4149
257.8906 | 123.2758 | -61.4182 | 61.5509 | 0.01197 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.4822 | 0.14332 | 61.418 | -0.055996 | 0.020767 | 61.5204 | -0.001436 | 61.3077 | 61.4301 | 61.3731 | 61.4062 | 61.416 | 61.4407 | 61.4305 | 61.4424 | 122.9003 | 61.5615 | 122.8361 | 61.3622 | 61.4389 | 122.9385 | 61.4167 | 122.7259 | 61.4614 | 61.4836 | 61.3972 | 61.4194
258.8906 | 123.1476 | -61.4319 | 61.6104 | 0.016548 | -0.049678 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4867 | 0.15248 | 61.4271 | -0.060575 | 0.016188 | 61.5204 | 0.003143 | 61.2986 | 61.4484 | 61.3822 | 61.4199 | 61.4298 | 61.4544 | 61.4442 | 61.4516 | 122.9186 | 61.5844 | 122.859 | 61.3713 | 61.4481 | 122.9523 | 61.435 | 122.7305 | 61.4705 | 61.4836 | 61.411 | 61.424
259.8906 | 123.1842 | -61.4456 | 61.5921 | 0.030283 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.016907 | 0.01969 | 61.4913 | 0.1479 | 61.418 | -0.046838 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4759 | 61.4051 | 61.4336 | 61.4389 | 61.4681 | 61.4625 | 61.4653 | 122.9369 | 61.5935 | 122.8636 | 61.3988 | 61.4572 | 122.966 | 61.4488 | 122.7533 | 61.4797 | 61.4882 | 61.4064 | 61.4148
260.8906 | 123.2574 | -61.409 | 61.5738 | 0.021127 | -0.049678 | -0.021157 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.4913 | 0.15248 | 61.4226 | -0.046838 | 0.016188 | 61.5112 | 0.012299 | 61.3077 | 61.4301 | 61.3593 | 61.3878 | 61.4115 | 61.4361 | 61.4167 | 61.4333 | 122.9003 | 61.5615 | 122.8316 | 61.3622 | 61.4252 | 122.9202 | 61.4213 | 122.7167 | 61.4751 | 61.479 | 61.4064 | 61.4103
261.8906 | 123.2437 | -61.4227 | 61.5784 | 0.01197 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.01969 | 61.4867 | 0.15248 | 61.418 | -0.065154 | 0.01161 | 61.5158 | 0.003143 | 61.3031 | 61.4347 | 61.3776 | 61.4107 | 61.4206 | 61.4498 | 61.4259 | 61.4424 | 122.9095 | 61.5752 | 122.8407 | 61.3576 | 61.4343 | 122.9385 | 61.4259 | 122.7259 | 61.4751 | 61.4836 | 61.4064 | 61.4148
262.8906 | 123.1888 | -61.4502 | 61.615 | 0.034862 | -0.054257 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.015112 | 61.4822 | 0.1479 | 61.418 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4851 | 61.3959 | 61.4382 | 61.4526 | 61.4727 | 61.4579 | 61.4653 | 122.9324 | 61.5981 | 122.8682 | 61.3896 | 61.4618 | 122.9706 | 61.4533 | 122.7579 | 61.4705 | 61.479 | 61.4064 | 61.4148
263.8906 | 123.2254 | -61.4365 | 61.5875 | 0.025705 | -0.049678 | -0.007421 | -0.006703 | 0.027109 | 0.016907 | 0.01969 | 61.4867 | 0.14332 | 61.4271 | -0.060575 | 0.01161 | 61.5158 | 0.007721 | 61.3077 | 61.4622 | 61.3868 | 61.429 | 61.4298 | 61.4636 | 61.4534 | 61.4562 | 122.9232 | 61.5798 | 122.8636 | 61.3759 | 61.4481 | 122.9523 | 61.4442 | 122.7442 | 61.4751 | 61.479 | 61.4155 | 61.4194
264.8906 | 123.1842 | -61.4365 | 61.6058 | 0.007391 | -0.054257 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4913 | 0.15248 | 61.4226 | -0.060575 | 0.016188 | 61.5204 | 0.007721 | 61.3123 | 61.4439 | 61.3822 | 61.4153 | 61.4343 | 61.4636 | 61.4488 | 61.4562 | 122.9278 | 61.5889 | 122.859 | 61.3759 | 61.4526 | 122.9568 | 61.4442 | 122.7488 | 61.4751 | 61.4836 | 61.4064 | 61.4149
265.8906 | 123.175 | -61.4456 | 61.5921 | 0.007391 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.016907 | 0.024268 | 61.4822 | 0.1479 | 61.4226 | -0.060575 | 0.01161 | 61.5158 | 0.003143 | 61.3077 | 61.453 | 61.4005 | 61.4336 | 61.4435 | 61.4681 | 61.4625 | 61.4699 | 122.9278 | 61.5935 | 122.8682 | 61.385 | 61.4572 | 122.9614 | 61.4488 | 122.7533 | 61.4705 | 61.479 | 61.411 | 61.4194
266.8906 | 123.1613 | -61.4548 | 61.6058 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.4776 | 0.15248 | 61.4226 | -0.060575 | 0.007032 | 61.525 | -0.001436 | 61.3077 | 61.4759 | 61.4097 | 61.4382 | 61.4526 | 61.4819 | 61.4579 | 61.479 | 122.9324 | 61.6073 | 122.8773 | 61.3942 | 61.4618 | 122.9797 | 61.4533 | 122.7625 | 61.4705 | 61.479 | 61.4155 | 61.424
267.8906 | 123.175 | -61.4319 | 61.5875 | 0.016548 | -0.049678 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4913 | 0.1479 | 61.4271 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3123 | 61.4484 | 61.3822 | 61.4153 | 61.4298 | 61.459 | 61.4442 | 61.4516 | 122.9232 | 61.5798 | 122.859 | 61.3759 | 61.4435 | 122.9523 | 61.435 | 122.7442 | 61.4797 | 61.4882 | 61.4155 | 61.424
268.8906 | 123.2208 | -61.4456 | 61.5829 | 0.016548 | -0.049678 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.010533 | 61.4867 | 0.1479 | 61.4226 | -0.055996 | 0.01161 | 61.5112 | 0.003143 | 61.3077 | 61.4622 | 61.3959 | 61.4336 | 61.4435 | 61.4727 | 61.4579 | 61.4562 | 122.9324 | 61.5935 | 122.8682 | 61.3896 | 61.4572 | 122.9568 | 61.4488 | 122.7533 | 61.4751 | 61.4836 | 61.411 | 61.4194
269.8906 | 123.2071 | -61.441 | 61.5875 | 0.016548 | -0.0451 | -0.002842 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4776 | 0.1479 | 61.418 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3169 | 61.4576 | 61.3959 | 61.4382 | 61.4343 | 61.4636 | 61.4534 | 61.4607 | 122.9186 | 61.5889 | 122.859 | 61.385 | 61.4526 | 122.9614 | 61.4488 | 122.7579 | 61.466 | 61.4699 | 61.4064 | 61.4103
270.8906 | 123.1934 | -61.4502 | 61.5967 | 0.021127 | -0.040521 | -0.012 | -0.011281 | 0.027109 | 0.00775 | 0.024268 | 61.4822 | 0.1479 | 61.418 | -0.055996 | 0.01161 | 61.5158 | 0.007721 | 61.3169 | 61.4713 | 61.4097 | 61.4382 | 61.4389 | 61.4773 | 61.4579 | 61.4745 | 122.9324 | 61.5981 | 122.8682 | 61.3942 | 61.4618 | 122.966 | 61.4579 | 122.7671 | 61.4705 | 61.4744 | 61.4064 | 61.4103
271.8906 | 123.143 | -61.4502 | 61.6104 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.4913 | 0.14332 | 61.418 | -0.051417 | 0.016188 | 61.5204 | 0.003143 | 61.3123 | 61.4713 | 61.4097 | 61.4336 | 61.4526 | 61.4727 | 61.4625 | 61.4745 | 122.9415 | 61.5935 | 122.8682 | 61.3988 | 61.4664 | 122.9706 | 61.4533 | 122.7625 | 61.4751 | 61.4882 | 61.4018 | 61.4148
272.8906 | 123.2208 | -61.441 | 61.5784 | 0.021127 | -0.049678 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4822 | 0.15248 | 61.4226 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4622 | 61.3914 | 61.4199 | 61.4389 | 61.4681 | 61.4534 | 61.4607 | 122.9232 | 61.5935 | 122.8636 | 61.3805 | 61.4526 | 122.9614 | 61.4442 | 122.7488 | 61.4705 | 61.479 | 61.411 | 61.4194
273.8906 | 123.2071 | -61.441 | 61.6379 | 0.01197 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.024268 | 61.4867 | 0.1479 | 61.4317 | -0.055996 | 0.016188 | 61.5204 | -0.001436 | 61.3077 | 61.453 | 61.3959 | 61.4245 | 61.4343 | 61.4681 | 61.4579 | 61.4653 | 122.9278 | 61.5889 | 122.8728 | 61.385 | 61.4572 | 122.9614 | 61.4396 | 122.7488 | 61.4705 | 61.4882 | 61.4155 | 61.4332
274.8906 | 123.1659 | -61.4227 | 61.5921 | 0.01197 | -0.035942 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.028846 | 61.4913 | 0.1479 | 61.4226 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3031 | 61.4347 | 61.3868 | 61.4107 | 61.416 | 61.4498 | 61.4305 | 61.4516 | 122.914 | 61.5706 | 122.8453 | 61.3667 | 61.4343 | 122.9431 | 61.4304 | 122.7259 | 61.4797 | 61.4836 | 61.411 | 61.4149
275.8906 | 123.1796 | -61.4273 | 61.615 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4822 | 0.15706 | 61.4226 | -0.060575 | 0.01161 | 61.5066 | 0.003143 | 61.3077 | 61.4484 | 61.3868 | 61.4107 | 61.4252 | 61.4544 | 61.4396 | 61.4516 | 122.9095 | 61.5844 | 122.8499 | 61.3667 | 61.4389 | 122.934 | 61.4305 | 122.735 | 61.4705 | 61.479 | 61.411 | 61.4194
276.8906 | 123.2071 | -61.4319 | 61.5738 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.016907 | 0.033424 | 61.4913 | 0.1479 | 61.4226 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.2986 | 61.453 | 61.3914 | 61.4199 | 61.4389 | 61.459 | 61.4488 | 61.4653 | 122.9232 | 61.5798 | 122.8545 | 61.3759 | 61.4481 | 122.9523 | 61.4396 | 122.7305 | 61.4751 | 61.4836 | 61.4064 | 61.4149
277.8906 | 123.1384 | -61.4319 | 61.6104 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4867 | 0.15248 | 61.418 | -0.055996 | 0.002454 | 61.5204 | 0.012299 | 61.3031 | 61.453 | 61.3868 | 61.4199 | 61.4298 | 61.459 | 61.4396 | 61.4516 | 122.9186 | 61.5844 | 122.8499 | 61.3759 | 61.4343 | 122.9523 | 61.4442 | 122.735 | 61.4843 | 61.4744 | 61.4155 | 61.4057
278.8906 | 123.1796 | -61.4319 | 61.5692 | 0.01197 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.4822 | 0.15706 | 61.4226 | -0.060575 | 0.016188 | 61.5158 | 0.003143 | 61.3031 | 61.4439 | 61.3914 | 61.4153 | 61.4298 | 61.4544 | 61.4442 | 61.4562 | 122.914 | 61.5889 | 122.8545 | 61.3713 | 61.4481 | 122.9477 | 61.435 | 122.735 | 61.466 | 61.479 | 61.4064 | 61.4194
279.8906 | 123.1888 | -61.4731 | 61.5738 | 0.016548 | -0.040521 | -0.025735 | -0.002124 | 0.022531 | 0.012329 | 0.015112 | 61.4867 | 0.1479 | 61.418 | -0.055996 | 0.007032 | 61.5158 | -0.001436 | 61.2986 | 61.4896 | 61.4326 | 61.4473 | 61.471 | 61.4956 | 61.4854 | 61.4882 | 122.9598 | 61.621 | 122.8911 | 61.4171 | 61.4801 | 122.9889 | 61.4716 | 122.7717 | 61.4797 | 61.4882 | 61.411 | 61.4194
280.8906 | 123.2162 | -61.4456 | 61.5738 | 0.021127 | -0.035942 | -0.021157 | 0.007033 | 0.027109 | 0.012329 | 0.01969 | 61.4913 | 0.15248 | 61.4226 | -0.060575 | 0.007032 | 61.5158 | 0.003143 | 61.3077 | 61.4667 | 61.4097 | 61.4245 | 61.4527 | 61.4727 | 61.4579 | 61.4653 | 122.9369 | 61.5981 | 122.8682 | 61.385 | 61.4527 | 122.9614 | 61.4488 | 122.7533 | 61.4843 | 61.4882 | 61.4155 | 61.4194
281.8906 | 123.23 | -61.4273 | 61.5601 | 0.021127 | -0.0451 | -0.007421 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.4913 | 0.1479 | 61.4317 | -0.060575 | 0.01161 | 61.5204 | -0.001436 | 61.3123 | 61.4484 | 61.3822 | 61.4199 | 61.4298 | 61.4544 | 61.4351 | 61.4516 | 122.9186 | 61.5752 | 122.859 | 61.3667 | 61.4389 | 122.9477 | 61.4259 | 122.7396 | 61.4797 | 61.4928 | 61.4201 | 61.4332
282.8906 | 123.2162 | -61.4319 | 61.5829 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.016907 | 0.015112 | 61.4867 | 0.1479 | 61.4317 | -0.055996 | 0.007032 | 61.5204 | 0.003143 | 61.3077 | 61.4484 | 61.3914 | 61.4153 | 61.4298 | 61.459 | 61.4488 | 61.447 | 122.9186 | 61.5798 | 122.8636 | 61.3759 | 61.4389 | 122.9523 | 61.435 | 122.7396 | 61.4797 | 61.4836 | 61.4247 | 61.4286
283.8906 | 123.1888 | -61.4273 | 61.5555 | 0.030283 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4776 | 0.16164 | 61.4226 | -0.060575 | 0.01161 | 61.5204 | -0.001436 | 61.3077 | 61.4576 | 61.3822 | 61.4107 | 61.4252 | 61.4544 | 61.4351 | 61.447 | 122.9049 | 61.5889 | 122.8499 | 61.3667 | 61.4389 | 122.9477 | 61.4259 | 122.735 | 61.466 | 61.479 | 61.411 | 61.424
284.8906 | 123.1796 | -61.4456 | 61.5829 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4913 | 0.1479 | 61.4226 | -0.060575 | 0.016188 | 61.5158 | 0.007721 | 61.3169 | 61.4667 | 61.4051 | 61.4336 | 61.4435 | 61.4727 | 61.4579 | 61.4699 | 122.9369 | 61.5935 | 122.8682 | 61.385 | 61.4618 | 122.9614 | 61.4533 | 122.7625 | 61.4751 | 61.4836 | 61.4064 | 61.4149
285.8906 | 123.1613 | -61.4548 | 61.5967 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4867 | 0.16164 | 61.4226 | -0.065154 | 0.01161 | 61.5295 | 0.003143 | 61.3031 | 61.4759 | 61.4097 | 61.4428 | 61.4526 | 61.4819 | 61.4671 | 61.479 | 122.9415 | 61.6164 | 122.8773 | 61.3896 | 61.4664 | 122.9843 | 61.4579 | 122.7579 | 61.4751 | 61.4836 | 61.411 | 61.4194
286.8906 | 123.2025 | -61.4548 | 61.5738 | 0.01197 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.01969 | 61.4776 | 0.1479 | 61.4226 | -0.065154 | 0.007032 | 61.5204 | -0.001436 | 61.294 | 61.4667 | 61.4143 | 61.4382 | 61.4526 | 61.4865 | 61.4717 | 61.4745 | 122.9324 | 61.6027 | 122.8773 | 61.3896 | 61.4618 | 122.9752 | 61.4533 | 122.7488 | 61.4705 | 61.479 | 61.4155 | 61.424
287.8906 | 123.1293 | -61.4365 | 61.5784 | 0.021127 | -0.040521 | -0.012 | -0.011281 | 0.022531 | 0.012329 | 0.024268 | 61.4867 | 0.14332 | 61.4317 | -0.055996 | 0.007032 | 61.525 | -0.001436 | 61.2986 | 61.4576 | 61.3959 | 61.4245 | 61.4252 | 61.459 | 61.4488 | 61.4607 | 122.9232 | 61.5798 | 122.8682 | 61.3805 | 61.4435 | 122.9614 | 61.435 | 122.735 | 61.4797 | 61.4882 | 61.4247 | 61.4332
288.8906 | 123.1476 | -61.4777 | 61.5692 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.01969 | 61.4822 | 0.15248 | 61.4271 | -0.060575 | 0.002454 | 61.5295 | -0.001436 | 61.3077 | 61.4988 | 61.4326 | 61.4657 | 61.4801 | 61.5093 | 61.4946 | 61.4974 | 122.9598 | 61.6301 | 122.9048 | 61.4171 | 61.4801 | 123.0072 | 61.4762 | 122.7854 | 61.4797 | 61.4836 | 61.4247 | 61.4286
289.8906 | 123.2117 | -61.4319 | 61.5829 | 0.021127 | -0.0451 | -0.007421 | -0.002124 | 0.036265 | 0.00775 | 0.024268 | 61.4913 | 0.15248 | 61.4271 | -0.065154 | 0.01161 | 61.525 | 0.003143 | 61.3123 | 61.453 | 61.3868 | 61.4245 | 61.4298 | 61.4682 | 61.4396 | 61.4562 | 122.9232 | 61.5844 | 122.859 | 61.3667 | 61.4435 | 122.9568 | 61.435 | 122.7442 | 61.4797 | 61.4882 | 61.4155 | 61.424
290.8906 | 123.1567 | -61.4594 | 61.5967 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4913 | 0.15706 | 61.4271 | -0.065154 | 0.007032 | 61.5158 | 0.003143 | 61.2986 | 61.4759 | 61.4143 | 61.4474 | 61.4572 | 61.4865 | 61.4717 | 61.479 | 122.9507 | 61.6164 | 122.8865 | 61.3942 | 61.4664 | 122.9752 | 61.4625 | 122.7579 | 61.4843 | 61.4882 | 61.4201 | 61.424
291.8906 | 123.143 | -61.4365 | 61.6058 | 0.016548 | -0.054257 | -0.021157 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.4913 | 0.14332 | 61.4271 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3031 | 61.453 | 61.3822 | 61.4153 | 61.4389 | 61.459 | 61.4488 | 61.4607 | 122.9278 | 61.5798 | 122.8636 | 61.3805 | 61.4481 | 122.9568 | 61.4396 | 122.7396 | 61.4797 | 61.4882 | 61.4155 | 61.424
292.8906 | 123.1705 | -61.4639 | 61.5555 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.4867 | 0.15248 | 61.4271 | -0.060575 | 0.002454 | 61.5204 | -0.001436 | 61.2986 | 61.4851 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4717 | 61.4882 | 122.9507 | 61.6164 | 122.8911 | 61.4034 | 61.4664 | 122.9843 | 61.4625 | 122.7625 | 61.4843 | 61.4882 | 61.4247 | 61.4286
293.8906 | 123.1293 | -61.4685 | 61.5875 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.022531 | 0.012329 | 0.015112 | 61.4822 | 0.15248 | 61.4226 | -0.065154 | 0.01161 | 61.5295 | -0.001436 | 61.3031 | 61.4896 | 61.4234 | 61.4565 | 61.471 | 61.491 | 61.4808 | 61.4836 | 122.9507 | 61.621 | 122.8911 | 61.4034 | 61.4801 | 122.998 | 61.4671 | 122.7717 | 61.4705 | 61.4836 | 61.411 | 61.424
294.8906 | 123.2025 | -61.4548 | 61.5692 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.031687 | 0.012329 | 0.028846 | 61.4867 | 0.1479 | 61.4271 | -0.065154 | 0.007032 | 61.5158 | 0.003143 | 61.3031 | 61.4805 | 61.4143 | 61.4382 | 61.4481 | 61.4865 | 61.4671 | 61.4836 | 122.9415 | 61.6027 | 122.8819 | 61.3896 | 61.4618 | 122.9706 | 61.4579 | 122.7579 | 61.4797 | 61.4836 | 61.4201 | 61.424
295.8906 | 123.1705 | -61.4456 | 61.5372 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | 0.016907 | 0.024268 | 61.4867 | 0.15248 | 61.4226 | -0.060575 | 0.01161 | 61.5158 | 0.003143 | 61.2986 | 61.4713 | 61.4051 | 61.4245 | 61.4435 | 61.4727 | 61.4625 | 61.4699 | 122.9324 | 61.5981 | 122.8682 | 61.385 | 61.4572 | 122.9614 | 61.4488 | 122.7442 | 61.4751 | 61.4836 | 61.411 | 61.4194
296.8906 | 123.2071 | -61.3998 | 61.6241 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.022531 | 0.012329 | 0.024268 | 61.4867 | 0.15248 | 61.4226 | -0.060575 | 0.020767 | 61.5295 | 0.003143 | 61.3077 | 61.4301 | 61.3547 | 61.3878 | 61.4069 | 61.4224 | 61.4122 | 61.4241 | 122.8866 | 61.5523 | 122.8224 | 61.3393 | 61.4206 | 122.9294 | 61.403 | 122.7076 | 61.466 | 61.4836 | 61.4018 | 61.4194
297.8906 | 123.2117 | -61.4273 | 61.528 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.036265 | 0.012329 | 0.028846 | 61.4822 | 0.14332 | 61.4226 | -0.051417 | 0.002454 | 61.525 | 0.012299 | 61.3031 | 61.4439 | 61.3868 | 61.4107 | 61.4252 | 61.4636 | 61.4396 | 61.4562 | 122.9095 | 61.5706 | 122.8499 | 61.3759 | 61.4298 | 122.9523 | 61.4396 | 122.7305 | 61.4797 | 61.4699 | 61.4201 | 61.4103
298.8906 | 123.2529 | -61.4319 | 61.4685 | 0.016548 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | 0.012329 | 0.015112 | 61.4776 | 0.15248 | 61.418 | -0.055996 | 0.016188 | 61.5158 | 0.007721 | 61.3031 | 61.4484 | 61.3914 | 61.4153 | 61.4252 | 61.4544 | 61.4442 | 61.447 | 122.9095 | 61.5844 | 122.8499 | 61.3759 | 61.4481 | 122.9477 | 61.4396 | 122.735 | 61.4614 | 61.4699 | 61.4018 | 61.4103
299.8906 | 123.3124 | -61.4136 | 61.5463 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.015112 | 61.4867 | 0.15248 | 61.418 | -0.051417 | 0.01161 | 61.5204 | 0.012299 | 61.3077 | 61.4301 | 61.3685 | 61.397 | 61.4114 | 61.4453 | 61.4305 | 61.4287 | 122.9003 | 61.5661 | 122.8316 | 61.3622 | 61.4252 | 122.934 | 61.4259 | 122.7213 | 61.4751 | 61.4744 | 61.4064 | 61.4057
300.8906 | 123.2986 | -61.441 | 61.5143 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | 0.00775 | 0.01969 | 61.4776 | 0.1479 | 61.418 | -0.055996 | 0.007032 | 61.525 | -0.001436 | 61.3031 | 61.4667 | 61.4051 | 61.4245 | 61.4343 | 61.4681 | 61.4488 | 61.4607 | 122.9186 | 61.5889 | 122.859 | 61.385 | 61.4481 | 122.966 | 61.4396 | 122.7442 | 61.4705 | 61.479 | 61.411 | 61.4194
301.8906 | 123.3307 | -61.409 | 61.5509 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.013375 | 0.00775 | 0.024268 | 61.4867 | 0.15248 | 61.4226 | -0.055996 | 0.01161 | 61.5158 | 0.007721 | 61.3077 | 61.4255 | 61.3639 | 61.3924 | 61.4115 | 61.4224 | 61.4167 | 61.4333 | 122.8957 | 61.5615 | 122.8316 | 61.353 | 61.4206 | 122.9248 | 61.4167 | 122.7167 | 61.4751 | 61.479 | 61.411 | 61.4149
302.8906 | 123.2803 | -61.4456 | 61.528 | 0.025705 | -0.0451 | -0.021157 | -0.006703 | 0.027109 | 0.00775 | 0.024268 | 61.4867 | 0.14332 | 61.4271 | -0.051417 | 0.007032 | 61.5204 | -0.001436 | 61.2986 | 61.4713 | 61.4005 | 61.4245 | 61.4389 | 61.4727 | 61.4534 | 61.4699 | 122.9324 | 61.5889 | 122.8728 | 61.3942 | 61.4527 | 122.966 | 61.4442 | 122.7442 | 61.4797 | 61.4882 | 61.4201 | 61.4286
303.8906 | 123.2346 | -61.4182 | 61.5372 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4913 | 0.15248 | 61.4226 | -0.065154 | 0.007032 | 61.5295 | -0.001436 | 61.2986 | 61.4347 | 61.3731 | 61.4062 | 61.416 | 61.4453 | 61.4305 | 61.4378 | 122.9095 | 61.5706 | 122.8407 | 61.353 | 61.4252 | 122.9477 | 61.4167 | 122.7167 | 61.4843 | 61.4928 | 61.4155 | 61.424
304.8906 | 123.2941 | -61.4182 | 61.5234 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.012329 | 0.01969 | 61.4867 | 0.15706 | 61.4271 | -0.060575 | 0.002454 | 61.5204 | 0.007721 | 61.2986 | 61.4347 | 61.3776 | 61.4062 | 61.4114 | 61.4407 | 61.4305 | 61.4378 | 122.9049 | 61.5752 | 122.8453 | 61.3576 | 61.4206 | 122.9385 | 61.4259 | 122.7167 | 61.4843 | 61.479 | 61.4247 | 61.4194
305.8906 | 123.2254 | -61.4227 | 61.528 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.012329 | 0.01969 | 61.4913 | 0.15248 | 61.4271 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3031 | 61.4393 | 61.3776 | 61.4107 | 61.4206 | 61.4544 | 61.4351 | 61.4424 | 122.914 | 61.5752 | 122.8499 | 61.3622 | 61.4343 | 122.9431 | 61.4259 | 122.7259 | 61.4797 | 61.4882 | 61.4155 | 61.424
306.8906 | 123.1842 | -61.4365 | 61.6241 | 0.030283 | -0.0451 | -0.012 | 0.007033 | 0.027109 | 0.003172 | 0.024268 | 61.4913 | 0.15706 | 61.4271 | -0.055996 | 0.007032 | 61.5204 | 0.007721 | 61.3077 | 61.4667 | 61.3914 | 61.4245 | 61.4435 | 61.4636 | 61.4396 | 61.4607 | 122.9278 | 61.5935 | 122.8636 | 61.3805 | 61.4435 | 122.9568 | 61.4442 | 122.7442 | 61.4843 | 61.4836 | 61.4201 | 61.4194
307.8906 | 123.2346 | -61.4182 | 61.5509 | 0.016548 | -0.035942 | -0.021157 | 0.002454 | 0.017953 | 0.016907 | 0.01969 | 61.4822 | 0.15706 | 61.418 | -0.065154 | 0.007032 | 61.5158 | -0.001436 | 61.3031 | 61.4347 | 61.3822 | 61.397 | 61.4206 | 61.4361 | 61.4351 | 61.4378 | 122.9003 | 61.5752 | 122.8361 | 61.353 | 61.4252 | 122.934 | 61.4167 | 122.7213 | 61.4751 | 61.4836 | 61.411 | 61.4194
308.8906 | 123.23 | -61.4227 | 61.528 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.4822 | 0.15248 | 61.4226 | -0.065154 | 0.007032 | 61.5204 | 0.007721 | 61.3077 | 61.4439 | 61.3822 | 61.4062 | 61.4206 | 61.4453 | 61.4351 | 61.447 | 122.9049 | 61.5752 | 122.8453 | 61.3576 | 61.4298 | 122.9431 | 61.4304 | 122.7305 | 61.4751 | 61.4744 | 61.4155 | 61.4149
309.8906 | 123.2529 | -61.4319 | 61.5326 | 0.016548 | -0.035942 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.024268 | 61.4867 | 0.1479 | 61.4226 | -0.060575 | 0.007032 | 61.5204 | 0.007721 | 61.3031 | 61.4484 | 61.3959 | 61.4199 | 61.4252 | 61.459 | 61.4396 | 61.4562 | 122.9186 | 61.5798 | 122.8545 | 61.3713 | 61.4389 | 122.9523 | 61.4396 | 122.735 | 61.4797 | 61.479 | 61.4155 | 61.4149
310.8906 | 123.2712 | -61.4456 | 61.5372 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.01969 | 61.4867 | 0.15248 | 61.418 | -0.060575 | 0.002454 | 61.5295 | 0.003143 | 61.3123 | 61.4667 | 61.4005 | 61.4336 | 61.4481 | 61.4681 | 61.4534 | 61.4653 | 122.9324 | 61.5981 | 122.8636 | 61.385 | 61.4481 | 122.9752 | 61.4488 | 122.7579 | 61.4843 | 61.4836 | 61.4155 | 61.4148
311.8906 | 123.1842 | -61.4731 | 61.5646 | 0.025705 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | 0.012329 | 0.033424 | 61.4822 | 0.15248 | 61.4317 | -0.060575 | 0.01161 | 61.5204 | -0.006014 | 61.3031 | 61.4988 | 61.4326 | 61.4565 | 61.4664 | 61.4956 | 61.4854 | 61.5065 | 122.9552 | 61.6256 | 122.9048 | 61.4125 | 61.4847 | 122.9935 | 61.4671 | 122.7762 | 61.4705 | 61.4882 | 61.4201 | 61.4377
312.8906 | 123.2941 | -61.409 | 61.5463 | 0.021127 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.012329 | 0.015112 | 61.4867 | 0.15248 | 61.4271 | -0.055996 | 0.007032 | 61.5158 | -0.001436 | 61.3077 | 61.4301 | 61.3685 | 61.3924 | 61.4023 | 61.4361 | 61.4213 | 61.4241 | 122.8957 | 61.5615 | 122.8361 | 61.353 | 61.416 | 122.9248 | 61.4076 | 122.7167 | 61.4797 | 61.4882 | 61.4201 | 61.4286
313.8906 | 123.2483 | -61.4319 | 61.528 | 0.01197 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.00775 | 0.01969 | 61.4913 | 0.15248 | 61.4226 | -0.065154 | 0.007032 | 61.5158 | 0.007721 | 61.3077 | 61.4439 | 61.3914 | 61.4199 | 61.4298 | 61.4544 | 61.4396 | 61.4516 | 122.9232 | 61.5844 | 122.8545 | 61.3667 | 61.4389 | 122.9477 | 61.4396 | 122.7396 | 61.4843 | 61.4836 | 61.4155 | 61.4149
314.8906 | 123.3032 | -61.4182 | 61.5463 | 0.016548 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.015112 | 61.4822 | 0.15248 | 61.4226 | -0.055996 | 0.01161 | 61.5204 | -0.001436 | 61.3031 | 61.4347 | 61.3822 | 61.4016 | 61.416 | 61.4453 | 61.4305 | 61.4333 | 122.9003 | 61.5706 | 122.8407 | 61.3622 | 61.4298 | 122.9385 | 61.4167 | 122.7213 | 61.4705 | 61.4836 | 61.411 | 61.424
315.8906 | 123.2986 | -61.4182 | 61.5646 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.028846 | 61.4867 | 0.1479 | 61.4226 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4439 | 61.3731 | 61.4016 | 61.416 | 61.4453 | 61.4213 | 61.447 | 122.9049 | 61.5661 | 122.8407 | 61.3622 | 61.4343 | 122.9431 | 61.4259 | 122.7259 | 61.4705 | 61.479 | 61.4064 | 61.4149
316.8906 | 123.2758 | -61.4319 | 61.5417 | 0.016548 | -0.040521 | -0.021157 | -0.002124 | 0.031687 | 0.012329 | 0.024268 | 61.4913 | 0.1479 | 61.4271 | -0.051417 | 0.007032 | 61.5204 | 0.012299 | 61.3077 | 61.4484 | 61.3914 | 61.4107 | 61.4298 | 61.4636 | 61.4442 | 61.4562 | 122.9232 | 61.5798 | 122.859 | 61.3805 | 61.4389 | 122.9523 | 61.4442 | 122.7396 | 61.4843 | 61.479 | 61.4201 | 61.4149
317.8906 | 123.2803 | -61.4319 | 61.5646 | 0.01197 | -0.035942 | -0.012 | -0.002124 | 0.022531 | 0.00775 | 0.024268 | 61.4867 | 0.15706 | 61.4271 | -0.065154 | 0.002454 | 61.5158 | 0.007721 | 61.2986 | 61.4439 | 61.3959 | 61.4199 | 61.4298 | 61.4544 | 61.4396 | 61.4562 | 122.9186 | 61.5889 | 122.859 | 61.3667 | 61.4343 | 122.9477 | 61.4396 | 122.7305 | 61.4843 | 61.479 | 61.4247 | 61.4194
318.8906 | 123.2986 | -61.409 | 61.5829 | 0.016548 | -0.049678 | -0.016578 | 0.002454 | 0.017953 | 0.00775 | 0.024268 | 61.4959 | 0.15706 | 61.4226 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3077 | 61.4255 | 61.3593 | 61.3924 | 61.4115 | 61.4269 | 61.4167 | 61.4333 | 122.9049 | 61.5661 | 122.8316 | 61.353 | 61.4252 | 122.934 | 61.4121 | 122.7167 | 61.4797 | 61.4928 | 61.4064 | 61.4194
319.8906 | 123.2437 | -61.4319 | 61.5692 | 0.021127 | -0.0451 | -0.007421 | -0.006703 | 0.017953 | 0.00775 | 0.024268 | 61.4867 | 0.15248 | 61.4226 | -0.055996 | 0.020767 | 61.5295 | 0.003143 | 61.3077 | 61.453 | 61.3868 | 61.4245 | 61.4252 | 61.4498 | 61.4396 | 61.4562 | 122.9186 | 61.5844 | 122.8545 | 61.3759 | 61.4527 | 122.9614 | 61.435 | 122.7396 | 61.466 | 61.4836 | 61.4018 | 61.4194
320.8906 | 123.1384 | -61.4365 | 61.5967 | 0.021127 | -0.049678 | -0.016578 | 0.007033 | 0.031687 | 0.012329 | 0.028846 | 61.4913 | 0.16164 | 61.4317 | -0.055996 | 0.007032 | 61.525 | 0.007721 | 61.3169 | 61.4576 | 61.3868 | 61.4199 | 61.4435 | 61.4681 | 61.4488 | 61.4653 | 122.9278 | 61.5981 | 122.8682 | 61.3805 | 61.4435 | 122.9614 | 61.4442 | 122.7533 | 61.4843 | 61.4836 | 61.4247 | 61.424
321.8906 | 123.1247 | -61.4548 | 61.6104 | 0.016548 | -0.0451 | -0.007421 | -0.006703 | 0.027109 | 0.012329 | 0.024268 | 61.4867 | 0.16164 | 61.4271 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3031 | 61.4713 | 61.4097 | 61.4474 | 61.4481 | 61.4819 | 61.4671 | 61.479 | 122.9415 | 61.6164 | 122.8819 | 61.3988 | 61.471 | 122.9797 | 61.4625 | 122.7579 | 61.4705 | 61.479 | 61.411 | 61.4194
322.8906 | 123.1934 | -61.4548 | 61.5829 | 0.016548 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4959 | 0.15706 | 61.4271 | -0.051417 | 0.016188 | 61.5204 | 0.007721 | 61.3123 | 61.4713 | 61.4143 | 61.4336 | 61.4526 | 61.4819 | 61.4671 | 61.479 | 122.9507 | 61.6118 | 122.8819 | 61.4034 | 61.471 | 122.9752 | 61.4625 | 122.7671 | 61.4797 | 61.4882 | 61.411 | 61.4194
323.8906 | 123.1476 | -61.4456 | 61.5921 | 0.016548 | -0.0451 | -0.007421 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4913 | 0.15248 | 61.4271 | -0.051417 | 0.01161 | 61.5158 | 0.003143 | 61.3077 | 61.4622 | 61.4005 | 61.4382 | 61.4435 | 61.4727 | 61.4579 | 61.4699 | 122.9369 | 61.5981 | 122.8728 | 61.3942 | 61.4572 | 122.9614 | 61.4488 | 122.7533 | 61.4797 | 61.4882 | 61.4155 | 61.424
324.8906 | 123.1338 | -61.4594 | 61.6104 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4913 | 0.15248 | 61.4271 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3123 | 61.4805 | 61.4234 | 61.4474 | 61.4572 | 61.4865 | 61.4717 | 61.4836 | 122.9507 | 61.6118 | 122.8865 | 61.3988 | 61.471 | 122.9797 | 61.4625 | 122.7717 | 61.4797 | 61.4882 | 61.4155 | 61.424
325.8906 | 123.1888 | -61.4456 | 61.5784 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.4913 | 0.15248 | 61.4271 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4713 | 61.4005 | 61.4336 | 61.4481 | 61.4727 | 61.4534 | 61.4699 | 122.9369 | 61.5981 | 122.8728 | 61.3896 | 61.4618 | 122.966 | 61.4533 | 122.7533 | 61.4751 | 61.4836 | 61.411 | 61.4194
326.8906 | 123.2025 | -61.4639 | 61.5921 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.016907 | 0.028846 | 61.4913 | 0.1479 | 61.4409 | -0.060575 | 0.020767 | 61.5112 | 0.007721 | 61.3123 | 61.4851 | 61.4188 | 61.4519 | 61.4618 | 61.4956 | 61.4808 | 61.4928 | 122.9552 | 61.6118 | 122.9048 | 61.4034 | 61.4847 | 122.9752 | 61.4716 | 122.7762 | 61.4705 | 61.4836 | 61.4201 | 61.4332
327.8906 | 123.2162 | -61.4639 | 61.5829 | 0.016548 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.4867 | 0.15248 | 61.4271 | -0.060575 | 0.01161 | 61.5204 | 0.007721 | 61.3123 | 61.4805 | 61.428 | 61.4519 | 61.4618 | 61.491 | 61.4717 | 61.4882 | 122.9507 | 61.6164 | 122.8911 | 61.4034 | 61.4755 | 122.9843 | 61.4716 | 122.7762 | 61.4751 | 61.479 | 61.4155 | 61.4194
328.8906 | 123.1659 | -61.441 | 61.5692 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.036265 | 0.021485 | 0.024268 | 61.505 | 0.1479 | 61.4317 | -0.055996 | 0.007032 | 61.5204 | 0.007721 | 61.3077 | 61.4667 | 61.4005 | 61.4336 | 61.4435 | 61.4773 | 61.4625 | 61.4653 | 122.9461 | 61.5889 | 122.8728 | 61.385 | 61.4481 | 122.9614 | 61.4488 | 122.7488 | 61.498 | 61.4973 | 61.4247 | 61.424
329.8906 | 123.1613 | -61.441 | 61.5784 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.4959 | 0.15248 | 61.4317 | -0.065154 | -0.002124 | 61.5204 | 0.007721 | 61.3123 | 61.4667 | 61.4051 | 61.429 | 61.4435 | 61.4681 | 61.4534 | 61.4699 | 122.9369 | 61.5935 | 122.8728 | 61.3759 | 61.4389 | 122.9614 | 61.4488 | 122.7533 | 61.498 | 61.4882 | 61.4339 | 61.424
330.8906 | 123.1476 | -61.4685 | 61.5784 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4867 | 0.15248 | 61.418 | -0.060575 | 0.01161 | 61.5204 | -0.001436 | 61.2986 | 61.4896 | 61.428 | 61.4565 | 61.4664 | 61.4956 | 61.4808 | 61.4928 | 122.9552 | 61.621 | 122.8865 | 61.4079 | 61.4801 | 122.9889 | 61.4671 | 122.7671 | 61.4751 | 61.4882 | 61.4064 | 61.4194
331.8906 | 123.1338 | -61.4456 | 61.5784 | 0.025705 | -0.035942 | -0.021157 | -0.006703 | 0.027109 | 0.012329 | 0.028846 | 61.5005 | 0.15248 | 61.4226 | -0.065154 | 0.01161 | 61.5158 | 0.003143 | 61.3077 | 61.4713 | 61.4097 | 61.4245 | 61.4389 | 61.4727 | 61.4579 | 61.4745 | 122.9461 | 61.5981 | 122.8682 | 61.3805 | 61.4572 | 122.9614 | 61.4488 | 122.7533 | 61.4889 | 61.4973 | 61.411 | 61.4194
332.8906 | 123.1842 | -61.4639 | 61.5601 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.4913 | 0.16164 | 61.4226 | -0.055996 | 0.01161 | 61.525 | 0.003143 | 61.3077 | 61.4805 | 61.4234 | 61.4474 | 61.4664 | 61.4956 | 61.4763 | 61.4882 | 122.9552 | 61.6256 | 122.8865 | 61.4079 | 61.4755 | 122.9889 | 61.4671 | 122.7717 | 61.4797 | 61.4882 | 61.411 | 61.4194
333.8906 | 123.2162 | -61.4456 | 61.5692 | 0.016548 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.01969 | 61.4776 | 0.1479 | 61.4226 | -0.055996 | 0.007032 | 61.525 | 0.007721 | 61.2986 | 61.4622 | 61.4097 | 61.429 | 61.4481 | 61.4727 | 61.4625 | 61.4653 | 122.9232 | 61.5935 | 122.8682 | 61.3896 | 61.4527 | 122.9706 | 61.4533 | 122.7442 | 61.4705 | 61.4699 | 61.4155 | 61.4149
334.8906 | 123.2712 | -61.4319 | 61.5234 | 0.021127 | -0.0451 | -0.021157 | -0.002124 | 0.017953 | 0.012329 | 0.024268 | 61.4913 | 0.15706 | 61.4271 | -0.055996 | 0.01161 | 61.5158 | -0.006014 | 61.3077 | 61.453 | 61.3868 | 61.4107 | 61.4298 | 61.4498 | 61.4442 | 61.4562 | 122.9232 | 61.5889 | 122.859 | 61.3759 | 61.4435 | 122.9477 | 61.4259 | 122.7396 | 61.4797 | 61.4973 | 61.4155 | 61.4332
335.8906 | 123.2895 | -61.4319 | 61.4639 | 0.016548 | -0.040521 | -0.007421 | -0.006703 | 0.031687 | 0.00775 | 0.015112 | 61.4913 | 0.15248 | 61.4317 | -0.060575 | 0.007032 | 61.5158 | 0.003143 | 61.2986 | 61.4484 | 61.3914 | 61.4245 | 61.4252 | 61.4636 | 61.4396 | 61.447 | 122.9232 | 61.5844 | 122.8636 | 61.3713 | 61.4389 | 122.9477 | 61.435 | 122.7305 | 61.4843 | 61.4882 | 61.4247 | 61.4286
336.8906 | 123.262 | -61.3998 | 61.5234 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.01969 | 61.4913 | 0.1479 | 61.4271 | -0.065154 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.4255 | 61.3639 | 61.3878 | 61.4023 | 61.4224 | 61.4076 | 61.4195 | 122.8912 | 61.5477 | 122.827 | 61.3347 | 61.4115 | 122.9248 | 61.4076 | 122.7076 | 61.4797 | 61.4836 | 61.4155 | 61.4194
337.8906 | 123.2895 | -61.4273 | 61.5189 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.4913 | 0.15248 | 61.4317 | -0.060575 | 0.007032 | 61.5204 | 0.007721 | 61.2986 | 61.4439 | 61.3822 | 61.4107 | 61.4298 | 61.4498 | 61.4396 | 61.447 | 122.9186 | 61.5798 | 122.859 | 61.3667 | 61.4343 | 122.9477 | 61.435 | 122.7259 | 61.4843 | 61.4836 | 61.4247 | 61.424
338.8906 | 123.2849 | -61.4227 | 61.5372 | 0.025705 | -0.026784 | -0.021157 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.4959 | 0.15248 | 61.4271 | -0.055996 | 0.002454 | 61.5158 | 0.007721 | 61.2986 | 61.4484 | 61.3959 | 61.4016 | 61.4252 | 61.4453 | 61.4351 | 61.447 | 122.9186 | 61.5752 | 122.8499 | 61.3667 | 61.4252 | 122.9385 | 61.4304 | 122.7213 | 61.4934 | 61.4882 | 61.4247 | 61.4194
339.8906 | 123.2346 | -61.4319 | 61.5189 | 0.021127 | -0.035942 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.028846 | 61.4867 | 0.1479 | 61.4271 | -0.065154 | 0.01161 | 61.5158 | 0.007721 | 61.3031 | 61.453 | 61.3959 | 61.4107 | 61.4298 | 61.459 | 61.4442 | 61.4607 | 122.9186 | 61.5798 | 122.859 | 61.3667 | 61.4435 | 122.9477 | 61.4396 | 122.735 | 61.4751 | 61.479 | 61.4155 | 61.4194
340.8906 | 123.2346 | -61.4548 | 61.5417 | 0.016548 | -0.0451 | -0.016578 | -0.011281 | 0.027109 | 0.012329 | 0.015112 | 61.4776 | 0.15706 | 61.4226 | -0.055996 | 0.007032 | 61.5204 | 0.003143 | 61.3077 | 61.4713 | 61.4097 | 61.4382 | 61.4435 | 61.4819 | 61.4671 | 61.4699 | 122.9324 | 61.6118 | 122.8773 | 61.3988 | 61.4618 | 122.9752 | 61.4579 | 122.7625 | 61.4705 | 61.4744 | 61.4155 | 61.4194
341.8906 | 123.23 | -61.4227 | 61.5601 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.01969 | 61.4867 | 0.15706 | 61.4317 | -0.060575 | 0.01161 | 61.5204 | -0.001436 | 61.2986 | 61.4439 | 61.3868 | 61.4062 | 61.4252 | 61.4498 | 61.4305 | 61.4424 | 122.9095 | 61.5798 | 122.8545 | 61.3622 | 61.4343 | 122.9431 | 61.4213 | 122.7213 | 61.4751 | 61.4882 | 61.4201 | 61.4332
342.8906 | 123.2574 | -61.4548 | 61.5509 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.015112 | 61.4913 | 0.15248 | 61.4226 | -0.055996 | 0.007032 | 61.5204 | 0.012299 | 61.3031 | 61.4805 | 61.4097 | 61.4382 | 61.4618 | 61.4819 | 61.4625 | 61.4699 | 122.9461 | 61.6073 | 122.8773 | 61.3988 | 61.4618 | 122.9752 | 61.4671 | 122.7579 | 61.4843 | 61.479 | 61.4155 | 61.4103
343.8906 | 123.2574 | -61.4227 | 61.5372 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.4867 | 0.15248 | 61.4317 | -0.060575 | 0.01161 | 61.5158 | 0.012299 | 61.3031 | 61.4484 | 61.3868 | 61.4062 | 61.4206 | 61.4498 | 61.4305 | 61.447 | 122.9095 | 61.5752 | 122.8545 | 61.3622 | 61.4343 | 122.9385 | 61.435 | 122.7259 | 61.4751 | 61.4744 | 61.4201 | 61.4194
344.8906 | 123.2117 | -61.4319 | 61.5417 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4913 | 0.15706 | 61.4226 | -0.065154 | 0.01161 | 61.5158 | 0.007721 | 61.3031 | 61.4576 | 61.3914 | 61.4153 | 61.4298 | 61.459 | 61.4396 | 61.4516 | 122.9232 | 61.5889 | 122.8545 | 61.3667 | 61.4435 | 122.9477 | 61.4396 | 122.735 | 61.4797 | 61.4836 | 61.411 | 61.4149
345.8906 | 123.262 | -61.4365 | 61.5463 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5005 | 0.15248 | 61.4317 | -0.060575 | 0.01161 | 61.525 | -0.001436 | 61.3031 | 61.453 | 61.4005 | 61.4245 | 61.4389 | 61.4636 | 61.4396 | 61.4607 | 122.9369 | 61.5889 | 122.8682 | 61.3759 | 61.4481 | 122.9614 | 61.435 | 122.7396 | 61.4889 | 61.5019 | 61.4201 | 61.4332
346.8906 | 123.2941 | -61.4182 | 61.5555 | 0.01197 | -0.049678 | -0.021157 | -0.011281 | 0.022531 | 0.012329 | 0.01969 | 61.4867 | 0.15248 | 61.4317 | -0.060575 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4301 | 61.3685 | 61.397 | 61.4069 | 61.4407 | 61.4305 | 61.4378 | 122.9049 | 61.5706 | 122.8499 | 61.3576 | 61.4343 | 122.9385 | 61.4259 | 122.7259 | 61.4705 | 61.479 | 61.4155 | 61.424
347.8906 | 123.3536 | -61.4136 | 61.5738 | 0.021127 | -0.026784 | -0.016578 | -0.002124 | 0.027109 | 0.016907 | 0.024268 | 61.4913 | 0.14332 | 61.4226 | -0.060575 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4347 | 61.3868 | 61.397 | 61.4114 | 61.4407 | 61.4305 | 61.4378 | 122.9049 | 61.5569 | 122.8361 | 61.353 | 61.4252 | 122.934 | 61.4213 | 122.7213 | 61.4797 | 61.4836 | 61.411 | 61.4149
348.8906 | 123.2574 | -61.4273 | 61.5509 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.4913 | 0.15248 | 61.4317 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3077 | 61.4484 | 61.3914 | 61.4153 | 61.4252 | 61.4544 | 61.4351 | 61.4516 | 122.9186 | 61.5798 | 122.859 | 61.3713 | 61.4389 | 122.9523 | 61.4396 | 122.735 | 61.4797 | 61.479 | 61.4201 | 61.4194
349.8906 | 123.3078 | -61.3953 | 61.5417 | 0.01197 | -0.035942 | -0.016578 | -0.006703 | 0.027109 | 0.00775 | 0.01969 | 61.4867 | 0.15248 | 61.4317 | -0.060575 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4072 | 61.3593 | 61.3787 | 61.3886 | 61.4224 | 61.403 | 61.415 | 122.882 | 61.5477 | 122.827 | 61.3347 | 61.4115 | 122.9156 | 61.403 | 122.703 | 61.4705 | 61.479 | 61.4155 | 61.424
350.8906 | 123.2895 | -61.3953 | 61.5692 | 0.021127 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.028846 | 61.4913 | 0.16622 | 61.4271 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.4164 | 61.3639 | 61.3787 | 61.3931 | 61.4224 | 61.4076 | 61.4241 | 122.8866 | 61.5615 | 122.8224 | 61.3393 | 61.4069 | 122.9202 | 61.403 | 122.7076 | 61.4797 | 61.4836 | 61.4155 | 61.4194
351.8906 | 123.2803 | -61.4227 | 61.5555 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | 0.003172 | 0.01969 | 61.5005 | 0.15706 | 61.4317 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3031 | 61.4439 | 61.3776 | 61.4062 | 61.416 | 61.4498 | 61.4259 | 61.4424 | 122.9232 | 61.5798 | 122.8545 | 61.3667 | 61.4389 | 122.9477 | 61.4259 | 122.7259 | 61.4843 | 61.4973 | 61.4155 | 61.4286
352.8906 | 123.3032 | -61.4044 | 61.5692 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.4913 | 0.15706 | 61.4317 | -0.055996 | 0.01161 | 61.5158 | 0.007721 | 61.3031 | 61.421 | 61.3593 | 61.3878 | 61.4023 | 61.4315 | 61.4167 | 61.4241 | 122.8957 | 61.5615 | 122.8361 | 61.3484 | 61.416 | 122.9202 | 61.4121 | 122.7076 | 61.4797 | 61.4836 | 61.4201 | 61.424
353.8906 | 123.175 | -61.4365 | 61.6058 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.4867 | 0.15248 | 61.4317 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3123 | 61.4576 | 61.3959 | 61.4245 | 61.4343 | 61.4636 | 61.4442 | 61.4607 | 122.9232 | 61.5889 | 122.8682 | 61.3805 | 61.4526 | 122.9568 | 61.4442 | 122.7488 | 61.4705 | 61.479 | 61.4155 | 61.424
354.8906 | 123.175 | -61.4456 | 61.6425 | 0.007391 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.5005 | 0.15706 | 61.4271 | -0.055996 | 0.020767 | 61.525 | 0.003143 | 61.3123 | 61.453 | 61.4097 | 61.429 | 61.4435 | 61.4727 | 61.4534 | 61.4699 | 122.9461 | 61.6027 | 122.8728 | 61.3896 | 61.4664 | 122.9706 | 61.4488 | 122.7579 | 61.4797 | 61.4973 | 61.4064 | 61.424
355.8906 | 123.175 | -61.4685 | 61.6104 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.024268 | 61.4959 | 0.15706 | 61.4317 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4896 | 61.428 | 61.4565 | 61.4664 | 61.5002 | 61.4763 | 61.4928 | 122.9644 | 61.6256 | 122.9002 | 61.4125 | 61.4847 | 122.9935 | 61.4762 | 122.7808 | 61.4797 | 61.4882 | 61.4155 | 61.424
356.8906 | 123.0698 | -61.4319 | 61.5829 | 0.01197 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.4913 | 0.15706 | 61.4317 | -0.060575 | 0.01161 | 61.5158 | 0.007721 | 61.3077 | 61.4439 | 61.3959 | 61.4199 | 61.4298 | 61.459 | 61.4396 | 61.4516 | 122.9232 | 61.5889 | 122.8636 | 61.3713 | 61.4435 | 122.9477 | 61.4396 | 122.7396 | 61.4797 | 61.4836 | 61.4201 | 61.424
357.8906 | 123.1659 | -61.4548 | 61.6241 | 0.016548 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.00775 | 0.028846 | 61.4913 | 0.15706 | 61.4317 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.4713 | 61.4143 | 61.4382 | 61.4481 | 61.4819 | 61.4625 | 61.4836 | 122.9461 | 61.6118 | 122.8865 | 61.3988 | 61.4664 | 122.9797 | 61.4625 | 122.7625 | 61.4797 | 61.4836 | 61.4201 | 61.424
358.8906 | 123.2025 | -61.4456 | 61.615 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.4913 | 0.15248 | 61.4409 | -0.065154 | 0.020767 | 61.5204 | 0.016878 | 61.3077 | 61.4622 | 61.4051 | 61.4336 | 61.4481 | 61.4773 | 61.4579 | 61.4699 | 122.9369 | 61.5981 | 122.8865 | 61.3805 | 61.4664 | 122.966 | 61.4625 | 122.7533 | 61.4705 | 61.4744 | 61.4201 | 61.424
359.8906 | 123.1796 | -61.4273 | 61.6196 | 0.025705 | -0.031363 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.024268 | 61.5005 | 0.15248 | 61.4226 | -0.060575 | 0.01161 | 61.5204 | 0.007721 | 61.3169 | 61.453 | 61.3959 | 61.4107 | 61.4252 | 61.459 | 61.4396 | 61.4516 | 122.9278 | 61.5798 | 122.8499 | 61.3667 | 61.4389 | 122.9477 | 61.435 | 122.7442 | 61.4889 | 61.4928 | 61.411 | 61.4149
360.8906 | 123.1979 | -61.4319 | 61.5875 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.4959 | 0.15248 | 61.4317 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4484 | 61.3959 | 61.4199 | 61.4343 | 61.4544 | 61.4442 | 61.4562 | 122.9278 | 61.5844 | 122.8636 | 61.3759 | 61.4481 | 122.9523 | 61.4396 | 122.7396 | 61.4797 | 61.4882 | 61.4155 | 61.424
361.8906 | 123.2391 | -61.4044 | 61.6013 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.024268 | 61.4959 | 0.15248 | 61.4363 | -0.055996 | 0.020767 | 61.525 | 0.007721 | 61.3123 | 61.4255 | 61.3639 | 61.3924 | 61.4115 | 61.4407 | 61.4167 | 61.4287 | 122.9003 | 61.5569 | 122.8407 | 61.3484 | 61.4252 | 122.9294 | 61.4121 | 122.7167 | 61.4751 | 61.4882 | 61.4155 | 61.4286
362.8906 | 123.2117 | -61.4273 | 61.5829 | 0.01197 | -0.040521 | -0.021157 | -0.006703 | 0.031687 | 0.012329 | 0.024268 | 61.4959 | 0.15248 | 61.4317 | -0.055996 | 0.016188 | 61.5204 | 0.003143 | 61.3123 | 61.4393 | 61.3868 | 61.4061 | 61.4206 | 61.459 | 61.4396 | 61.4516 | 122.9232 | 61.5798 | 122.859 | 61.3713 | 61.4435 | 122.9477 | 61.4305 | 122.7396 | 61.4797 | 61.4928 | 61.4155 | 61.4286
363.8906 | 123.1796 | -61.4365 | 61.5829 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.01969 | 61.4959 | 0.15706 | 61.4226 | -0.060575 | 0.016188 | 61.5204 | 0.007721 | 61.3031 | 61.453 | 61.3959 | 61.4245 | 61.4435 | 61.4681 | 61.4488 | 61.4562 | 122.9324 | 61.5935 | 122.859 | 61.3759 | 61.4526 | 122.9568 | 61.4442 | 122.7396 | 61.4797 | 61.4882 | 61.4064 | 61.4149
364.8906 | 123.2254 | -61.4502 | 61.5692 | 0.016548 | -0.040521 | -0.021157 | -0.002124 | 0.031687 | 0.026064 | 0.024268 | 61.5005 | 0.15248 | 61.4317 | -0.055996 | 0.020767 | 61.5204 | -0.001436 | 61.3077 | 61.4667 | 61.4097 | 61.429 | 61.4481 | 61.4819 | 61.4763 | 61.4745 | 122.9507 | 61.6027 | 122.8819 | 61.3942 | 61.471 | 122.9706 | 61.4488 | 122.7579 | 61.4797 | 61.5019 | 61.411 | 61.4332
365.8906 | 123.2162 | -61.409 | 61.615 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.026064 | 0.028846 | 61.5005 | 0.15706 | 61.4363 | -0.051417 | 0.016188 | 61.5204 | 0.003143 | 61.3123 | 61.4347 | 61.3685 | 61.397 | 61.416 | 61.4361 | 61.4351 | 61.4378 | 122.9095 | 61.5661 | 122.8453 | 61.3576 | 61.4252 | 122.9294 | 61.4121 | 122.7213 | 61.4843 | 61.4973 | 61.4201 | 61.4332
366.8906 | 123.1842 | -61.4273 | 61.6287 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.4913 | 0.15706 | 61.4271 | -0.060575 | 0.01161 | 61.525 | 0.012299 | 61.3031 | 61.453 | 61.3868 | 61.4061 | 61.4252 | 61.459 | 61.4351 | 61.4562 | 122.9186 | 61.5844 | 122.8545 | 61.3667 | 61.4389 | 122.9523 | 61.4396 | 122.7305 | 61.4797 | 61.479 | 61.4155 | 61.4149
367.8906 | 123.1613 | -61.4731 | 61.5692 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.5096 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4942 | 61.4326 | 61.4565 | 61.471 | 61.4956 | 61.4854 | 61.4928 | 122.9827 | 61.6347 | 122.9048 | 61.4171 | 61.4847 | 122.9935 | 61.4808 | 122.7808 | 61.498 | 61.5019 | 61.4201 | 61.424
368.8906 | 123.1796 | -61.4182 | 61.5601 | 0.030283 | -0.040521 | -0.007421 | 0.002454 | 0.022531 | 0.012329 | 0.028846 | 61.4959 | 0.15706 | 61.4317 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3123 | 61.4484 | 61.3776 | 61.4107 | 61.4206 | 61.4407 | 61.4305 | 61.447 | 122.914 | 61.5752 | 122.8499 | 61.3576 | 61.4298 | 122.9385 | 61.4213 | 122.7305 | 61.4843 | 61.4928 | 61.4201 | 61.4286
369.8906 | 123.1979 | -61.4182 | 61.5509 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.4959 | 0.15706 | 61.4271 | -0.060575 | 0.007032 | 61.5204 | 0.012299 | 61.3123 | 61.4393 | 61.3822 | 61.4062 | 61.416 | 61.4498 | 61.4259 | 61.447 | 122.914 | 61.5752 | 122.8453 | 61.3576 | 61.4252 | 122.9385 | 61.4305 | 122.7305 | 61.4889 | 61.4836 | 61.4201 | 61.4149
370.8906 | 123.1476 | -61.4502 | 61.5784 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5005 | 0.15248 | 61.4271 | -0.051417 | 0.01161 | 61.525 | 0.003143 | 61.3031 | 61.4713 | 61.4097 | 61.4336 | 61.4526 | 61.4773 | 61.4625 | 61.479 | 122.9507 | 61.6027 | 122.8773 | 61.3988 | 61.4618 | 122.9752 | 61.4533 | 122.7533 | 61.4889 | 61.4973 | 61.4155 | 61.424
371.8906 | 123.1888 | -61.441 | 61.5921 | 0.021127 | -0.035942 | -0.021157 | 0.007033 | 0.031687 | 0.012329 | 0.024268 | 61.5005 | 0.16164 | 61.4363 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.2986 | 61.4622 | 61.4051 | 61.4199 | 61.4481 | 61.4727 | 61.4534 | 61.4653 | 122.9415 | 61.6027 | 122.8773 | 61.385 | 61.4526 | 122.966 | 61.4488 | 122.7396 | 61.4889 | 61.4928 | 61.4247 | 61.4286
372.8906 | 123.2071 | -61.4273 | 61.5921 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.5005 | 0.15706 | 61.4271 | -0.055996 | 0.002454 | 61.5158 | 0.003143 | 61.3077 | 61.453 | 61.3868 | 61.4107 | 61.4252 | 61.4544 | 61.4396 | 61.4516 | 122.9278 | 61.5844 | 122.8545 | 61.3713 | 61.4298 | 122.9431 | 61.4305 | 122.735 | 61.498 | 61.4973 | 61.4247 | 61.424
373.8906 | 123.1888 | -61.4227 | 61.5921 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.028846 | 61.4959 | 0.1479 | 61.4271 | -0.060575 | 0.016188 | 61.5204 | 0.007721 | 61.3123 | 61.4484 | 61.3822 | 61.4107 | 61.4206 | 61.4498 | 61.4305 | 61.4516 | 122.9186 | 61.5706 | 122.8499 | 61.3622 | 61.4389 | 122.9431 | 61.4304 | 122.735 | 61.4797 | 61.4882 | 61.411 | 61.4194
374.8906 | 123.1567 | -61.4365 | 61.5692 | 0.021127 | -0.035942 | -0.007421 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4913 | 0.15248 | 61.4317 | -0.055996 | 0.01161 | 61.5295 | -0.001436 | 61.3031 | 61.4576 | 61.4005 | 61.429 | 61.4343 | 61.4636 | 61.4488 | 61.4607 | 122.9278 | 61.5889 | 122.8682 | 61.3805 | 61.4481 | 122.966 | 61.435 | 122.7396 | 61.4797 | 61.4928 | 61.4201 | 61.4332
375.8906 | 123.111 | -61.4731 | 61.5784 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.016907 | 0.024268 | 61.4959 | 0.15706 | 61.4271 | -0.065154 | 0.01161 | 61.5158 | 0.012299 | 61.3077 | 61.4988 | 61.4326 | 61.4611 | 61.471 | 61.5002 | 61.49 | 61.4974 | 122.969 | 61.6301 | 122.9002 | 61.4079 | 61.4847 | 122.9889 | 61.4854 | 122.7808 | 61.4843 | 61.4836 | 61.4155 | 61.4149
376.8906 | 123.1476 | -61.4639 | 61.5738 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.024268 | 61.4959 | 0.16164 | 61.4363 | -0.065154 | 0.007032 | 61.5204 | -0.001436 | 61.3077 | 61.4896 | 61.428 | 61.4474 | 61.4618 | 61.4956 | 61.4808 | 61.4882 | 122.9598 | 61.6256 | 122.9002 | 61.3988 | 61.471 | 122.9843 | 61.4625 | 122.7717 | 61.4889 | 61.4973 | 61.4293 | 61.4377
377.8906 | 123.1247 | -61.4502 | 61.5738 | 0.021127 | -0.031363 | -0.016578 | 0.007033 | 0.027109 | 0.012329 | 0.033424 | 61.5005 | 0.15248 | 61.4317 | -0.060575 | 0.016188 | 61.5204 | 0.003143 | 61.3031 | 61.4713 | 61.4188 | 61.4336 | 61.4572 | 61.4773 | 61.4625 | 61.4836 | 122.9507 | 61.6027 | 122.8819 | 61.3896 | 61.4664 | 122.9706 | 61.4533 | 122.7533 | 61.4843 | 61.4973 | 61.4155 | 61.4286
378.8906 | 123.111 | -61.4548 | 61.5555 | 0.021127 | -0.040521 | -0.007421 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.4959 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.525 | 0.003143 | 61.2986 | 61.4759 | 61.4143 | 61.4474 | 61.4618 | 61.4865 | 61.4625 | 61.4882 | 122.9507 | 61.6164 | 122.8865 | 61.3988 | 61.4664 | 122.9797 | 61.4579 | 122.7533 | 61.4843 | 61.4928 | 61.4201 | 61.4286
379.8906 | 123.1705 | -61.4365 | 61.5784 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.021485 | 0.028846 | 61.4959 | 0.15706 | 61.4409 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.453 | 61.3959 | 61.429 | 61.4389 | 61.4681 | 61.4579 | 61.4653 | 122.9324 | 61.5935 | 122.8773 | 61.3805 | 61.4526 | 122.9614 | 61.4442 | 122.7442 | 61.4797 | 61.4882 | 61.4247 | 61.4332
380.8906 | 123.1842 | -61.4273 | 61.5692 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.028846 | 61.4959 | 0.16164 | 61.4317 | -0.051417 | 0.016188 | 61.5204 | 0.007721 | 61.3031 | 61.4484 | 61.3868 | 61.4107 | 61.4298 | 61.4498 | 61.4396 | 61.4562 | 122.9232 | 61.5889 | 122.859 | 61.3759 | 61.4435 | 122.9477 | 61.435 | 122.7305 | 61.4797 | 61.4882 | 61.4155 | 61.424
381.8906 | 123.1842 | -61.4548 | 61.5463 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4913 | 0.16164 | 61.4317 | -0.060575 | 0.01161 | 61.5112 | -0.001436 | 61.3031 | 61.4805 | 61.4097 | 61.4382 | 61.4526 | 61.4819 | 61.4671 | 61.479 | 122.9461 | 61.6164 | 122.8865 | 61.3942 | 61.4664 | 122.966 | 61.4533 | 122.7579 | 61.4797 | 61.4928 | 61.4201 | 61.4332
382.8906 | 123.23 | -61.4548 | 61.5463 | 0.016548 | -0.0451 | -0.021157 | 0.002454 | 0.027109 | 0.016907 | 0.01969 | 61.5005 | 0.16164 | 61.4317 | -0.060575 | 0.020767 | 61.5204 | 0.007721 | 61.3031 | 61.4713 | 61.4097 | 61.4336 | 61.4572 | 61.4819 | 61.4717 | 61.4745 | 122.9552 | 61.6164 | 122.8865 | 61.3942 | 61.4755 | 122.9752 | 61.4625 | 122.7579 | 61.4797 | 61.4928 | 61.411 | 61.424
383.8906 | 123.1567 | -61.4502 | 61.5463 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.5005 | 0.15706 | 61.4363 | -0.055996 | 0.007032 | 61.5204 | -0.001436 | 61.2986 | 61.4713 | 61.4143 | 61.4382 | 61.4481 | 61.4773 | 61.4579 | 61.4699 | 122.9507 | 61.6073 | 122.8865 | 61.3942 | 61.4572 | 122.9706 | 61.4488 | 122.7488 | 61.4934 | 61.5019 | 61.4293 | 61.4377
384.8906 | 123.2208 | -61.4456 | 61.5417 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.00775 | 0.01969 | 61.4959 | 0.1479 | 61.4363 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3031 | 61.4622 | 61.4051 | 61.429 | 61.4481 | 61.4681 | 61.4534 | 61.4653 | 122.9415 | 61.5935 | 122.8819 | 61.3896 | 61.4618 | 122.9706 | 61.4488 | 122.7488 | 61.4797 | 61.4928 | 61.4201 | 61.4332
385.8906 | 123.1934 | -61.4456 | 61.5417 | 0.025705 | -0.040521 | -0.007421 | -0.006703 | 0.031687 | 0.012329 | 0.024268 | 61.4913 | 0.15248 | 61.4226 | -0.055996 | 0.007032 | 61.5204 | 0.003143 | 61.3031 | 61.4713 | 61.4051 | 61.4382 | 61.4389 | 61.4773 | 61.4579 | 61.4699 | 122.9369 | 61.5981 | 122.8682 | 61.3896 | 61.4527 | 122.966 | 61.4488 | 122.7488 | 61.4843 | 61.4882 | 61.4155 | 61.4194
386.8906 | 123.1155 | -61.4548 | 61.5738 | 0.025705 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.028846 | 61.5005 | 0.15706 | 61.4317 | -0.060575 | 0.002454 | 61.525 | 0.007721 | 61.3077 | 61.4805 | 61.4097 | 61.4382 | 61.4526 | 61.4865 | 61.4671 | 61.4836 | 122.9552 | 61.6118 | 122.8865 | 61.3942 | 61.4572 | 122.9797 | 61.4625 | 122.7625 | 61.498 | 61.4928 | 61.4293 | 61.424
387.8906 | 123.2849 | -61.4227 | 61.5189 | 0.016548 | -0.031363 | -0.007421 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.4959 | 0.15248 | 61.4363 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4393 | 61.3914 | 61.4153 | 61.4252 | 61.4453 | 61.4351 | 61.447 | 122.9186 | 61.5752 | 122.859 | 61.3667 | 61.4343 | 122.9431 | 61.4259 | 122.7305 | 61.4843 | 61.4928 | 61.4247 | 61.4332
388.8906 | 123.2529 | -61.4365 | 61.528 | 0.021127 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.5005 | 0.16164 | 61.4317 | -0.055996 | 0.002454 | 61.525 | 0.003143 | 61.3077 | 61.4576 | 61.3959 | 61.4153 | 61.4343 | 61.4636 | 61.4488 | 61.4607 | 122.9369 | 61.5981 | 122.8682 | 61.3805 | 61.4389 | 122.9614 | 61.4396 | 122.7442 | 61.498 | 61.4973 | 61.4293 | 61.4286
389.8906 | 123.3078 | -61.4456 | 61.5097 | 0.025705 | -0.049678 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.4913 | 0.15706 | 61.4317 | -0.060575 | 0.016188 | 61.525 | 0.012299 | 61.3031 | 61.4713 | 61.3959 | 61.4336 | 61.4481 | 61.4727 | 61.4534 | 61.4699 | 122.9369 | 61.6027 | 122.8773 | 61.385 | 61.4618 | 122.9706 | 61.4579 | 122.7488 | 61.4751 | 61.479 | 61.4155 | 61.4194
390.8906 | 123.2712 | -61.4227 | 61.5051 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.4959 | 0.15706 | 61.4317 | -0.065154 | 0.01161 | 61.5204 | 0.003143 | 61.3031 | 61.4484 | 61.3868 | 61.4062 | 61.4252 | 61.4498 | 61.4305 | 61.4562 | 122.9186 | 61.5798 | 122.8545 | 61.3576 | 61.4343 | 122.9431 | 61.4259 | 122.7259 | 61.4843 | 61.4928 | 61.4201 | 61.4286
391.8906 | 123.262 | -61.4227 | 61.4914 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.4913 | 0.16164 | 61.4317 | -0.060575 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4393 | 61.3776 | 61.4062 | 61.4252 | 61.4453 | 61.4351 | 61.4424 | 122.914 | 61.5844 | 122.8545 | 61.3622 | 61.4389 | 122.9477 | 61.4259 | 122.735 | 61.4751 | 61.4882 | 61.4155 | 61.4286
392.8906 | 123.2666 | -61.441 | 61.5326 | 0.025705 | -0.040521 | -0.007421 | -0.006703 | 0.027109 | 0.012329 | 0.024268 | 61.4913 | 0.16164 | 61.4317 | -0.060575 | 0.01161 | 61.525 | 0.003143 | 61.2986 | 61.4667 | 61.4005 | 61.4336 | 61.4343 | 61.4681 | 61.4534 | 61.4653 | 122.9324 | 61.6027 | 122.8728 | 61.3805 | 61.4526 | 122.966 | 61.4442 | 122.7396 | 61.4797 | 61.4882 | 61.4201 | 61.4286
393.8906 | 123.2986 | -61.4273 | 61.5234 | 0.016548 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4959 | 0.15706 | 61.4363 | -0.055996 | 0.002454 | 61.5204 | -0.001436 | 61.3031 | 61.4439 | 61.3914 | 61.4107 | 61.4252 | 61.4544 | 61.4396 | 61.4516 | 122.9232 | 61.5844 | 122.8636 | 61.3713 | 61.4298 | 122.9477 | 61.4259 | 122.7305 | 61.4934 | 61.4973 | 61.4339 | 61.4377
394.8906 | 123.2346 | -61.441 | 61.5646 | 0.016548 | -0.0451 | -0.021157 | -0.002124 | 0.022531 | 0.00775 | 0.024268 | 61.5005 | 0.16164 | 61.4317 | -0.055996 | 0.002454 | 61.5204 | 0.007721 | 61.2986 | 61.4576 | 61.3959 | 61.4199 | 61.4389 | 61.4636 | 61.4488 | 61.4653 | 122.9415 | 61.6027 | 122.8728 | 61.385 | 61.4435 | 122.9614 | 61.4488 | 122.7396 | 61.498 | 61.4928 | 61.4293 | 61.424
395.8906 | 123.262 | -61.4365 | 61.5417 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.4959 | 0.15706 | 61.4317 | -0.060575 | 0.016188 | 61.5158 | 0.003143 | 61.3077 | 61.453 | 61.3959 | 61.4199 | 61.4389 | 61.4636 | 61.4442 | 61.4607 | 122.9324 | 61.5935 | 122.8682 | 61.3759 | 61.4526 | 122.9523 | 61.4396 | 122.7442 | 61.4797 | 61.4928 | 61.4155 | 61.4286
396.8906 | 123.2574 | -61.4365 | 61.5601 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5005 | 0.1479 | 61.4363 | -0.055996 | 0.01161 | 61.5204 | 0.012299 | 61.3077 | 61.4622 | 61.4005 | 61.4245 | 61.4389 | 61.4681 | 61.4488 | 61.4653 | 122.9369 | 61.5844 | 122.8728 | 61.3805 | 61.4481 | 122.9568 | 61.4488 | 122.7442 | 61.4889 | 61.4882 | 61.4247 | 61.424
397.8906 | 123.3078 | -61.4456 | 61.5326 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.01969 | 61.4959 | 0.15706 | 61.4271 | -0.055996 | 0.016188 | 61.5295 | 0.003143 | 61.3031 | 61.4622 | 61.4051 | 61.4336 | 61.4389 | 61.4681 | 61.4534 | 61.4653 | 122.9415 | 61.6027 | 122.8728 | 61.3896 | 61.4618 | 122.9752 | 61.4488 | 122.7488 | 61.4797 | 61.4928 | 61.411 | 61.424
398.8906 | 123.2391 | -61.4502 | 61.5326 | 0.030283 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.028846 | 61.4959 | 0.16164 | 61.4317 | -0.065154 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4805 | 61.4097 | 61.4336 | 61.4435 | 61.4773 | 61.4671 | 61.479 | 122.9461 | 61.6118 | 122.8819 | 61.385 | 61.4618 | 122.9706 | 61.4533 | 122.7579 | 61.4843 | 61.4928 | 61.4201 | 61.4286
399.8906 | 123.2803 | -61.4273 | 61.5509 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.5005 | 0.15248 | 61.4363 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3031 | 61.4439 | 61.3868 | 61.4153 | 61.4252 | 61.4498 | 61.4396 | 61.4516 | 122.9278 | 61.5798 | 122.8636 | 61.3713 | 61.4435 | 122.9523 | 61.4305 | 122.7305 | 61.4843 | 61.4973 | 61.4201 | 61.4332
400.8906 | 123.2895 | -61.3815 | 61.5555 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.024268 | 61.4959 | 0.16164 | 61.4271 | -0.060575 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4027 | 61.3364 | 61.365 | 61.3794 | 61.4132 | 61.3939 | 61.4058 | 122.8774 | 61.5432 | 122.8087 | 61.321 | 61.3977 | 122.9111 | 61.3893 | 122.6893 | 61.4797 | 61.4882 | 61.411 | 61.4194
401.8906 | 123.2803 | -61.4136 | 61.5555 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.5005 | 0.16164 | 61.4226 | -0.055996 | 0.016188 | 61.5204 | 0.003143 | 61.3077 | 61.4347 | 61.3685 | 61.4016 | 61.4114 | 61.4407 | 61.4259 | 61.4333 | 122.914 | 61.5752 | 122.8361 | 61.3576 | 61.4298 | 122.934 | 61.4167 | 122.7213 | 61.4843 | 61.4973 | 61.4064 | 61.4194
402.8906 | 123.1705 | -61.4548 | 61.5784 | 0.025705 | -0.049678 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.01969 | 61.4959 | 0.15706 | 61.4363 | -0.060575 | 0.016188 | 61.525 | 0.003143 | 61.3031 | 61.4805 | 61.4051 | 61.4382 | 61.4572 | 61.4865 | 61.4671 | 61.4745 | 122.9507 | 61.6118 | 122.8911 | 61.3942 | 61.471 | 122.9797 | 61.4579 | 122.7579 | 61.4797 | 61.4928 | 61.4201 | 61.4332
403.8906 | 123.2574 | -61.3953 | 61.5646 | 0.025705 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.4959 | 0.15706 | 61.4409 | -0.051417 | 0.016188 | 61.5204 | 0.012299 | 61.3031 | 61.421 | 61.3502 | 61.3833 | 61.3931 | 61.4178 | 61.3984 | 61.4195 | 122.8912 | 61.5523 | 122.8361 | 61.3438 | 61.4115 | 122.9156 | 61.4076 | 122.6984 | 61.4797 | 61.4836 | 61.4247 | 61.4286
404.8906 | 123.2437 | -61.4685 | 61.5875 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.028846 | 61.4959 | 0.16164 | 61.4363 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3169 | 61.4942 | 61.428 | 61.4565 | 61.471 | 61.491 | 61.4763 | 61.4974 | 122.9644 | 61.6301 | 122.9048 | 61.4171 | 61.4847 | 122.9935 | 61.4762 | 122.7854 | 61.4797 | 61.4882 | 61.4201 | 61.4286
405.8906 | 123.1888 | -61.4136 | 61.615 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.505 | 0.16164 | 61.4363 | -0.060575 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.4347 | 61.3731 | 61.397 | 61.416 | 61.4407 | 61.4213 | 61.4378 | 122.9186 | 61.5752 | 122.8499 | 61.353 | 61.4252 | 122.9385 | 61.4213 | 122.7259 | 61.4934 | 61.4973 | 61.4247 | 61.4286
406.8906 | 123.1567 | -61.4273 | 61.5784 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.01969 | 61.4959 | 0.15706 | 61.4363 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3031 | 61.4484 | 61.3868 | 61.4153 | 61.4298 | 61.459 | 61.4351 | 61.447 | 122.9232 | 61.5844 | 122.8636 | 61.3713 | 61.4435 | 122.9477 | 61.435 | 122.7305 | 61.4797 | 61.4882 | 61.4201 | 61.4286
407.8906 | 123.2391 | -61.4136 | 61.528 | 0.025705 | -0.031363 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.024268 | 61.5005 | 0.15248 | 61.4271 | -0.051417 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4393 | 61.3822 | 61.4016 | 61.416 | 61.4361 | 61.4213 | 61.4378 | 122.914 | 61.5661 | 122.8407 | 61.3622 | 61.4252 | 122.934 | 61.4167 | 122.7213 | 61.4889 | 61.4973 | 61.4155 | 61.424
408.8906 | 123.1659 | -61.4319 | 61.6287 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.028846 | 61.4959 | 0.16164 | 61.4363 | -0.055996 | 0.01161 | 61.5204 | 0.012299 | 61.3169 | 61.4484 | 61.3868 | 61.4153 | 61.4298 | 61.4636 | 61.4488 | 61.4607 | 122.9278 | 61.5935 | 122.8682 | 61.3759 | 61.4435 | 122.9523 | 61.4442 | 122.7488 | 61.4843 | 61.4836 | 61.4247 | 61.424
409.8906 | 123.1979 | -61.4227 | 61.6104 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.024268 | 61.4913 | 0.16164 | 61.4363 | -0.051417 | 0.01161 | 61.5204 | 0.007721 | 61.3169 | 61.4439 | 61.3868 | 61.4062 | 61.4252 | 61.4498 | 61.4396 | 61.447 | 122.914 | 61.5844 | 122.859 | 61.3713 | 61.4343 | 122.9431 | 61.4304 | 122.7396 | 61.4797 | 61.4836 | 61.4247 | 61.4286
410.8906 | 123.2162 | -61.409 | 61.5921 | 0.025705 | -0.035942 | -0.016578 | -0.006703 | 0.022531 | 0.016907 | 0.024268 | 61.5005 | 0.16164 | 61.4363 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4347 | 61.3731 | 61.3924 | 61.4023 | 61.4315 | 61.4259 | 61.4333 | 122.9095 | 61.5706 | 122.8453 | 61.353 | 61.4206 | 122.9294 | 61.4167 | 122.7167 | 61.4889 | 61.4928 | 61.4247 | 61.4286
411.8906 | 123.1842 | -61.4365 | 61.6196 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | 0.016907 | 0.024268 | 61.5005 | 0.15706 | 61.4271 | -0.060575 | 0.01161 | 61.525 | -0.001436 | 61.3123 | 61.4622 | 61.3914 | 61.4199 | 61.4389 | 61.459 | 61.4534 | 61.4607 | 122.9369 | 61.5935 | 122.8636 | 61.3759 | 61.4481 | 122.9614 | 61.435 | 122.7488 | 61.4889 | 61.5019 | 61.4155 | 61.4286
412.8906 | 123.1384 | -61.4639 | 61.5555 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.4959 | 0.15706 | 61.4363 | -0.060575 | 0.007032 | 61.5204 | 0.003143 | 61.3123 | 61.4896 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4717 | 61.4882 | 122.9598 | 61.621 | 122.9002 | 61.4034 | 61.471 | 122.9843 | 61.4671 | 122.7762 | 61.4889 | 61.4928 | 61.4293 | 61.4332
413.8906 | 123.1888 | -61.4365 | 61.5646 | 0.016548 | -0.040521 | -0.021157 | -0.006703 | 0.036265 | 0.016907 | 0.033424 | 61.4959 | 0.16164 | 61.4317 | -0.060575 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.453 | 61.3959 | 61.4153 | 61.4298 | 61.4727 | 61.4534 | 61.4699 | 122.9324 | 61.5981 | 122.8682 | 61.3759 | 61.4526 | 122.9614 | 61.4396 | 122.7488 | 61.4797 | 61.4928 | 61.4155 | 61.4286
414.8906 | 123.1842 | -61.4273 | 61.5738 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.022531 | 0.016907 | 0.024268 | 61.5005 | 0.16164 | 61.4363 | -0.060575 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4439 | 61.3868 | 61.4107 | 61.4343 | 61.4498 | 61.4442 | 61.4516 | 122.9278 | 61.5889 | 122.8636 | 61.3667 | 61.4435 | 122.9523 | 61.4305 | 122.7396 | 61.4843 | 61.4973 | 61.4201 | 61.4332
415.8906 | 123.1705 | -61.4319 | 61.5692 | 0.021127 | -0.031363 | -0.007421 | -0.006703 | 0.027109 | 0.003172 | 0.024268 | 61.505 | 0.15706 | 61.4317 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.453 | 61.4005 | 61.4245 | 61.4252 | 61.459 | 61.4351 | 61.4562 | 122.9369 | 61.5889 | 122.8636 | 61.3805 | 61.4481 | 122.9568 | 61.4396 | 122.7396 | 61.4889 | 61.4973 | 61.4155 | 61.424
416.8906 | 123.1567 | -61.4548 | 61.5784 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.01969 | 61.4959 | 0.15706 | 61.4317 | -0.055996 | 0.007032 | 61.5204 | -0.001436 | 61.3123 | 61.4759 | 61.4097 | 61.4382 | 61.4572 | 61.4819 | 61.4671 | 61.4745 | 122.9507 | 61.6118 | 122.8865 | 61.3988 | 61.4618 | 122.9752 | 61.4533 | 122.7671 | 61.4889 | 61.4973 | 61.4247 | 61.4332
417.8906 | 123.2712 | -61.4594 | 61.5463 | 0.025705 | -0.035942 | -0.007421 | 0.002454 | 0.022531 | 0.00775 | 0.024268 | 61.5005 | 0.16164 | 61.4363 | -0.055996 | 0.016188 | 61.5295 | 0.003143 | 61.3031 | 61.4851 | 61.4234 | 61.4519 | 61.4618 | 61.4819 | 61.4671 | 61.4836 | 122.9598 | 61.621 | 122.8957 | 61.4034 | 61.4755 | 122.9889 | 61.4625 | 122.7625 | 61.4843 | 61.4973 | 61.4201 | 61.4332
418.8906 | 123.143 | -61.4914 | 61.5555 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.00775 | 0.028846 | 61.5005 | 0.16622 | 61.4409 | -0.051417 | 0.01161 | 61.525 | 0.012299 | 61.3031 | 61.5125 | 61.4509 | 61.4748 | 61.4984 | 61.5277 | 61.4991 | 61.5202 | 122.9919 | 61.6576 | 122.9323 | 61.44 | 61.503 | 123.0164 | 61.5037 | 122.7945 | 61.4889 | 61.4882 | 61.4293 | 61.4286
419.8906 | 123.143 | -61.4548 | 61.5555 | 0.030283 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.016907 | 0.028846 | 61.4959 | 0.15706 | 61.4409 | -0.055996 | 0.01161 | 61.5204 | 0.012299 | 61.2986 | 61.4851 | 61.4143 | 61.4382 | 61.4572 | 61.4865 | 61.4717 | 61.4836 | 122.9507 | 61.6118 | 122.8957 | 61.3988 | 61.4664 | 122.9752 | 61.4671 | 122.7533 | 61.4843 | 61.4836 | 61.4293 | 61.4286
420.8906 | 123.1659 | -61.4456 | 61.5509 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.4959 | 0.16164 | 61.4317 | -0.060575 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.4622 | 61.4051 | 61.429 | 61.4435 | 61.4727 | 61.4534 | 61.4699 | 122.9415 | 61.6073 | 122.8773 | 61.385 | 61.4572 | 122.9706 | 61.4533 | 122.7533 | 61.4843 | 61.4882 | 61.4201 | 61.424
421.8906 | 123.1705 | -61.4502 | 61.5555 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.4959 | 0.16164 | 61.4363 | -0.055996 | 0.007032 | 61.525 | 0.003143 | 61.3123 | 61.4759 | 61.4097 | 61.4382 | 61.4526 | 61.4819 | 61.4579 | 61.4745 | 122.9461 | 61.6118 | 122.8865 | 61.3942 | 61.4572 | 122.9752 | 61.4533 | 122.7625 | 61.4889 | 61.4928 | 61.4293 | 61.4332
422.8906 | 123.1796 | -61.4731 | 61.5463 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.022531 | 0.016907 | 0.028846 | 61.505 | 0.16622 | 61.4363 | -0.055996 | 0.01161 | 61.525 | -0.001436 | 61.3077 | 61.4988 | 61.4326 | 61.4519 | 61.471 | 61.4956 | 61.49 | 61.5019 | 122.9781 | 61.6393 | 122.9094 | 61.4171 | 61.4847 | 122.998 | 61.4716 | 122.7808 | 61.4934 | 61.5065 | 61.4247 | 61.4377
423.8906 | 123.3078 | -61.409 | 61.5463 | 0.021127 | -0.0451 | -0.021157 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.4913 | 0.15706 | 61.4271 | -0.060575 | 0.01161 | 61.5158 | 0.003143 | 61.3123 | 61.4301 | 61.3639 | 61.3878 | 61.4115 | 61.4361 | 61.4122 | 61.4333 | 122.9003 | 61.5661 | 122.8361 | 61.3484 | 61.4206 | 122.9248 | 61.4121 | 122.7213 | 61.4797 | 61.4882 | 61.4155 | 61.424
424.8906 | 123.262 | -61.4044 | 61.5143 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.5005 | 0.16164 | 61.4363 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.421 | 61.3593 | 61.3924 | 61.4069 | 61.4361 | 61.4167 | 61.4287 | 122.9049 | 61.5661 | 122.8407 | 61.3484 | 61.416 | 122.9294 | 61.4121 | 122.7167 | 61.4889 | 61.4928 | 61.4247 | 61.4286
425.8906 | 123.3307 | -61.4319 | 61.5143 | 0.016548 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.016907 | 0.024268 | 61.5005 | 0.15706 | 61.4363 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.2986 | 61.4484 | 61.3959 | 61.4153 | 61.4298 | 61.459 | 61.4488 | 61.4562 | 122.9324 | 61.5889 | 122.8682 | 61.3759 | 61.4527 | 122.9568 | 61.4442 | 122.7305 | 61.4797 | 61.4882 | 61.4155 | 61.424
426.8906 | 123.2803 | -61.4182 | 61.5326 | 0.021127 | -0.035942 | -0.021157 | 0.007033 | 0.036265 | 0.012329 | 0.024268 | 61.4959 | 0.15706 | 61.4363 | -0.060575 | 0.016188 | 61.5204 | 0.003143 | 61.2986 | 61.4393 | 61.3822 | 61.397 | 61.4252 | 61.4544 | 61.4305 | 61.4424 | 122.914 | 61.5752 | 122.8545 | 61.3576 | 61.4343 | 122.9385 | 61.4213 | 122.7167 | 61.4797 | 61.4928 | 61.4201 | 61.4332
427.8906 | 123.2574 | -61.4227 | 61.5372 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.01969 | 61.4913 | 0.16164 | 61.4409 | -0.060575 | 0.007032 | 61.5204 | 0.007721 | 61.3031 | 61.4393 | 61.3822 | 61.4107 | 61.4206 | 61.4453 | 61.4351 | 61.4424 | 122.914 | 61.5844 | 122.8636 | 61.3622 | 61.4298 | 122.9431 | 61.4304 | 122.7259 | 61.4843 | 61.4836 | 61.4339 | 61.4332
428.8906 | 123.262 | -61.4548 | 61.5234 | 0.021127 | -0.040521 | -0.007421 | 0.007033 | 0.027109 | 0.012329 | 0.028846 | 61.5005 | 0.16164 | 61.4317 | -0.065154 | 0.01161 | 61.525 | 0.007721 | 61.3031 | 61.4759 | 61.4143 | 61.4474 | 61.4618 | 61.4819 | 61.4671 | 61.4836 | 122.9552 | 61.6164 | 122.8865 | 61.3896 | 61.4664 | 122.9797 | 61.4625 | 122.7579 | 61.4889 | 61.4928 | 61.4201 | 61.424
429.8906 | 123.2346 | -61.4136 | 61.5326 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5005 | 0.15706 | 61.4363 | -0.055996 | 0.01161 | 61.5158 | -0.001436 | 61.3077 | 61.4393 | 61.3731 | 61.4062 | 61.416 | 61.4407 | 61.4259 | 61.4378 | 122.914 | 61.5706 | 122.8499 | 61.3576 | 61.4252 | 122.9294 | 61.4121 | 122.7213 | 61.4889 | 61.5019 | 61.4247 | 61.4377
430.8906 | 123.2483 | -61.441 | 61.5326 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.012329 | 0.024268 | 61.5005 | 0.16164 | 61.4317 | -0.055996 | 0.016188 | 61.5295 | -0.001436 | 61.3031 | 61.4667 | 61.4005 | 61.429 | 61.4389 | 61.4727 | 61.4534 | 61.4653 | 122.9415 | 61.6027 | 122.8728 | 61.385 | 61.4572 | 122.9706 | 61.4396 | 122.7442 | 61.4843 | 61.5019 | 61.4155 | 61.4332
431.8906 | 123.2529 | -61.4548 | 61.5372 | 0.021127 | -0.035942 | -0.016578 | -0.006703 | 0.031687 | 0.00775 | 0.015112 | 61.505 | 0.15706 | 61.4317 | -0.051417 | 0.002454 | 61.5204 | 0.007721 | 61.3077 | 61.4759 | 61.4188 | 61.4382 | 61.4481 | 61.4865 | 61.4625 | 61.4699 | 122.9598 | 61.6118 | 122.8865 | 61.4034 | 61.4572 | 122.9752 | 61.4625 | 122.7625 | 61.5026 | 61.4973 | 61.4293 | 61.424
432.8906 | 123.2162 | -61.441 | 61.5417 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.028846 | 61.5005 | 0.15706 | 61.4317 | -0.055996 | 0.020767 | 61.5204 | 0.012299 | 61.3123 | 61.4667 | 61.4005 | 61.4245 | 61.4389 | 61.4681 | 61.4534 | 61.4699 | 122.9415 | 61.5981 | 122.8728 | 61.385 | 61.4618 | 122.9614 | 61.4533 | 122.7533 | 61.4797 | 61.4882 | 61.411 | 61.4194
433.8906 | 123.2712 | -61.4594 | 61.5555 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.024268 | 61.4959 | 0.15706 | 61.4363 | -0.060575 | 0.01161 | 61.5204 | 0.012299 | 61.3123 | 61.4759 | 61.4188 | 61.4428 | 61.4618 | 61.4865 | 61.4763 | 61.4836 | 122.9552 | 61.6164 | 122.8957 | 61.3988 | 61.471 | 122.9797 | 61.4716 | 122.7717 | 61.4843 | 61.4836 | 61.4247 | 61.424
434.8906 | 123.2666 | -61.4319 | 61.5555 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.017953 | 0.012329 | 0.024268 | 61.5005 | 0.16164 | 61.4363 | -0.051417 | 0.01161 | 61.525 | 0.012299 | 61.3077 | 61.453 | 61.3914 | 61.4153 | 61.4389 | 61.4498 | 61.4442 | 61.4562 | 122.9324 | 61.5935 | 122.8682 | 61.3805 | 61.4435 | 122.9568 | 61.4442 | 122.7396 | 61.4889 | 61.4882 | 61.4247 | 61.424
435.8906 | 123.2483 | -61.4456 | 61.528 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.505 | 0.16164 | 61.4363 | -0.060575 | 0.01161 | 61.5204 | 0.012299 | 61.3031 | 61.4667 | 61.4005 | 61.429 | 61.4481 | 61.4727 | 61.4534 | 61.4699 | 122.9507 | 61.6073 | 122.8819 | 61.385 | 61.4572 | 122.966 | 61.4579 | 122.7488 | 61.4934 | 61.4928 | 61.4247 | 61.424
436.8906 | 123.2986 | -61.4273 | 61.5463 | 0.021127 | -0.0451 | -0.021157 | -0.006703 | 0.022531 | 0.00775 | 0.024268 | 61.4913 | 0.16164 | 61.4409 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3123 | 61.4484 | 61.3822 | 61.4061 | 61.4206 | 61.4498 | 61.4351 | 61.4516 | 122.9186 | 61.5889 | 122.8682 | 61.3713 | 61.4435 | 122.9477 | 61.435 | 122.7396 | 61.4751 | 61.4836 | 61.4247 | 61.4332
437.8906 | 123.2986 | -61.4227 | 61.5738 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.5005 | 0.15706 | 61.4317 | -0.060575 | 0.016188 | 61.5204 | 0.012299 | 61.3123 | 61.4393 | 61.3822 | 61.4107 | 61.4206 | 61.4498 | 61.4259 | 61.447 | 122.9232 | 61.5798 | 122.8545 | 61.3622 | 61.4389 | 122.9431 | 61.435 | 122.735 | 61.4843 | 61.4882 | 61.4155 | 61.4194
438.8906 | 123.2758 | -61.3998 | 61.5601 | 0.021127 | -0.040521 | -0.007421 | -0.002124 | 0.036265 | 0.012329 | 0.024268 | 61.505 | 0.17079 | 61.4363 | -0.051417 | 0.01161 | 61.5295 | 0.007721 | 61.3077 | 61.421 | 61.3593 | 61.3924 | 61.3977 | 61.4361 | 61.4122 | 61.4241 | 122.9049 | 61.5706 | 122.8361 | 61.3484 | 61.4115 | 122.9294 | 61.4076 | 122.7076 | 61.4934 | 61.4973 | 61.4247 | 61.4286
439.8906 | 123.3078 | -61.4182 | 61.5601 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.01969 | 61.5005 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3031 | 61.4393 | 61.3731 | 61.4016 | 61.416 | 61.4453 | 61.4305 | 61.4378 | 122.9186 | 61.5798 | 122.8499 | 61.3622 | 61.4298 | 122.9431 | 61.4259 | 122.7213 | 61.4889 | 61.4928 | 61.4201 | 61.424
440.8906 | 123.2986 | -61.4136 | 61.5646 | 0.025705 | -0.031363 | -0.007421 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.4959 | 0.15706 | 61.4317 | -0.060575 | 0.016188 | 61.5204 | 0.012299 | 61.3123 | 61.4393 | 61.3822 | 61.4062 | 61.416 | 61.4361 | 61.4259 | 61.4333 | 122.9095 | 61.5706 | 122.8453 | 61.353 | 61.4298 | 122.934 | 61.4259 | 122.7259 | 61.4797 | 61.4836 | 61.4155 | 61.4194
441.8906 | 123.2437 | -61.4227 | 61.5829 | 0.025705 | -0.040521 | -0.021157 | 0.002454 | 0.022531 | 0.012329 | 0.028846 | 61.5005 | 0.16164 | 61.4409 | -0.055996 | 0.020767 | 61.5204 | 0.003143 | 61.3077 | 61.4484 | 61.3822 | 61.4016 | 61.4252 | 61.4453 | 61.4351 | 61.4516 | 122.9232 | 61.5844 | 122.8636 | 61.3667 | 61.4435 | 122.9431 | 61.4259 | 122.7305 | 61.4797 | 61.4973 | 61.4201 | 61.4377
442.8906 | 123.2391 | -61.4182 | 61.5646 | 0.021127 | -0.049678 | -0.016578 | -0.006703 | 0.027109 | 0.003172 | 0.024268 | 61.5005 | 0.15706 | 61.4317 | -0.060575 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.4393 | 61.3685 | 61.4016 | 61.4114 | 61.4453 | 61.4213 | 61.4424 | 122.9186 | 61.5752 | 122.8499 | 61.3576 | 61.4298 | 122.9431 | 61.4259 | 122.7305 | 61.4889 | 61.4928 | 61.4201 | 61.424
443.8906 | 123.1888 | -61.4273 | 61.5875 | 0.021127 | -0.0451 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.024268 | 61.505 | 0.16164 | 61.4363 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4484 | 61.3822 | 61.4107 | 61.4206 | 61.4544 | 61.4442 | 61.4516 | 122.9324 | 61.5889 | 122.8636 | 61.3713 | 61.4435 | 122.9523 | 61.435 | 122.7396 | 61.4889 | 61.4973 | 61.4201 | 61.4286
444.8906 | 123.1705 | -61.4365 | 61.615 | 0.025705 | -0.049678 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.024268 | 61.4959 | 0.15706 | 61.4409 | -0.046838 | 0.01161 | 61.5204 | 0.007721 | 61.3123 | 61.4622 | 61.3868 | 61.4245 | 61.4343 | 61.4681 | 61.4442 | 61.4607 | 122.9324 | 61.5935 | 122.8773 | 61.3896 | 61.4481 | 122.9568 | 61.4442 | 122.7488 | 61.4843 | 61.4882 | 61.4293 | 61.4332
445.8906 | 123.1934 | -61.4456 | 61.6013 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.4959 | 0.15706 | 61.4363 | -0.060575 | 0.01161 | 61.5204 | 0.012299 | 61.3077 | 61.4713 | 61.4097 | 61.4336 | 61.4481 | 61.4727 | 61.4534 | 61.479 | 122.9415 | 61.6027 | 122.8819 | 61.385 | 61.4572 | 122.966 | 61.4579 | 122.7533 | 61.4843 | 61.4836 | 61.4247 | 61.424
446.8906 | 123.143 | -61.4639 | 61.6196 | 0.021127 | -0.035942 | -0.007421 | -0.002124 | 0.027109 | 0.016907 | 0.024268 | 61.4959 | 0.15248 | 61.4317 | -0.055996 | 0.016188 | 61.5204 | 0.016878 | 61.3077 | 61.4851 | 61.428 | 61.4565 | 61.4618 | 61.491 | 61.4808 | 61.4882 | 122.9598 | 61.6164 | 122.8957 | 61.4079 | 61.4801 | 122.9843 | 61.4808 | 122.7717 | 61.4797 | 61.479 | 61.4155 | 61.4148
447.8906 | 123.1888 | -61.4639 | 61.6196 | 0.021127 | -0.0451 | -0.007421 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.505 | 0.16164 | 61.4409 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4851 | 61.4188 | 61.4565 | 61.4664 | 61.4956 | 61.4763 | 61.4928 | 122.969 | 61.6256 | 122.9048 | 61.4079 | 61.4755 | 122.9843 | 61.4671 | 122.7717 | 61.4934 | 61.5019 | 61.4293 | 61.4377
448.8906 | 123.175 | -61.4182 | 61.6287 | 0.021127 | -0.049678 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.028846 | 61.5005 | 0.16164 | 61.4409 | -0.046838 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4393 | 61.3685 | 61.4062 | 61.416 | 61.4407 | 61.4305 | 61.447 | 122.9186 | 61.5798 | 122.859 | 61.3713 | 61.4298 | 122.9385 | 61.4259 | 122.7259 | 61.4889 | 61.4928 | 61.4293 | 61.4332
449.8906 | 123.1338 | -61.4456 | 61.6196 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.505 | 0.16622 | 61.4409 | -0.060575 | 0.007032 | 61.5204 | 0.012299 | 61.3169 | 61.4622 | 61.4051 | 61.4382 | 61.4481 | 61.4727 | 61.4579 | 61.4699 | 122.9507 | 61.6118 | 122.8865 | 61.385 | 61.4527 | 122.966 | 61.4579 | 122.7625 | 61.498 | 61.4928 | 61.4339 | 61.4286
450.8906 | 123.2483 | -61.4456 | 61.5967 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.024268 | 61.505 | 0.16622 | 61.4409 | -0.055996 | 0.007032 | 61.5295 | 0.007721 | 61.3123 | 61.4622 | 61.4005 | 61.4336 | 61.4481 | 61.4773 | 61.4625 | 61.4699 | 122.9507 | 61.6118 | 122.8865 | 61.3896 | 61.4527 | 122.9752 | 61.4533 | 122.7579 | 61.498 | 61.4973 | 61.4339 | 61.4332
451.8906 | 123.2117 | -61.4365 | 61.5601 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.033424 | 61.505 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3123 | 61.4576 | 61.3959 | 61.4199 | 61.4343 | 61.4681 | 61.4488 | 61.4699 | 122.9415 | 61.5981 | 122.8682 | 61.3805 | 61.4481 | 122.9568 | 61.4396 | 122.7488 | 61.4934 | 61.5019 | 61.4201 | 61.4286
452.8906 | 123.1705 | -61.4136 | 61.5829 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.024268 | 61.505 | 0.16164 | 61.4409 | -0.055996 | 0.002454 | 61.5295 | 0.007721 | 61.3077 | 61.4347 | 61.3731 | 61.4016 | 61.416 | 61.4498 | 61.4213 | 61.4378 | 122.9186 | 61.5752 | 122.8545 | 61.3576 | 61.416 | 122.9431 | 61.4213 | 122.7213 | 61.5026 | 61.4973 | 61.4384 | 61.4332
453.8906 | 123.1888 | -61.4456 | 61.5646 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.028846 | 61.5005 | 0.16164 | 61.4363 | -0.051417 | 0.007032 | 61.5204 | 0.003143 | 61.3077 | 61.4713 | 61.4051 | 61.429 | 61.4435 | 61.4727 | 61.4579 | 61.4745 | 122.9461 | 61.6073 | 122.8819 | 61.3942 | 61.4527 | 122.966 | 61.4488 | 122.7533 | 61.4934 | 61.4973 | 61.4293 | 61.4332
454.8906 | 123.1384 | -61.4594 | 61.5646 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.012329 | 0.028846 | 61.5005 | 0.16164 | 61.4363 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4851 | 61.4188 | 61.4474 | 61.4572 | 61.491 | 61.4717 | 61.4882 | 122.9598 | 61.621 | 122.8957 | 61.4034 | 61.4755 | 122.9843 | 61.4671 | 122.7717 | 61.4843 | 61.4928 | 61.4201 | 61.4286
455.8906 | 123.1796 | -61.4594 | 61.5784 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.024268 | 61.5005 | 0.16164 | 61.4317 | -0.055996 | 0.007032 | 61.525 | 0.007721 | 61.3077 | 61.4759 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4671 | 61.4836 | 122.9598 | 61.621 | 122.8911 | 61.4034 | 61.4664 | 122.9843 | 61.4671 | 122.7671 | 61.4934 | 61.4928 | 61.4247 | 61.424
456.8906 | 123.2071 | -61.441 | 61.5829 | 0.021127 | -0.0451 | -0.007421 | -0.002124 | 0.022531 | 0.021485 | 0.028846 | 61.505 | 0.15248 | 61.4409 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3123 | 61.4622 | 61.3959 | 61.4336 | 61.4389 | 61.4636 | 61.4625 | 61.4699 | 122.9461 | 61.5935 | 122.8819 | 61.385 | 61.4526 | 122.9614 | 61.4442 | 122.7533 | 61.4934 | 61.5019 | 61.4293 | 61.4377
457.8906 | 123.143 | -61.4548 | 61.5738 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.012329 | 0.028846 | 61.505 | 0.15706 | 61.4455 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.2986 | 61.4713 | 61.4143 | 61.4428 | 61.4618 | 61.4819 | 61.4671 | 61.4836 | 122.9598 | 61.6118 | 122.9002 | 61.3988 | 61.4664 | 122.9797 | 61.4625 | 122.7533 | 61.4934 | 61.4973 | 61.4339 | 61.4377
458.8906 | 123.2208 | -61.4685 | 61.5555 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.5005 | 0.17079 | 61.4363 | -0.055996 | 0.01161 | 61.525 | -0.001436 | 61.3031 | 61.4896 | 61.428 | 61.4519 | 61.4664 | 61.4956 | 61.4808 | 61.4928 | 122.969 | 61.6393 | 122.9048 | 61.4125 | 61.4801 | 122.9935 | 61.4671 | 122.7717 | 61.4889 | 61.5019 | 61.4247 | 61.4377
459.8906 | 123.1796 | -61.441 | 61.5692 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.036265 | 0.00775 | 0.01969 | 61.505 | 0.16164 | 61.4409 | -0.055996 | 0.016188 | 61.5204 | 0.012299 | 61.3077 | 61.4622 | 61.4005 | 61.4245 | 61.4389 | 61.4773 | 61.4488 | 61.4607 | 122.9461 | 61.6027 | 122.8819 | 61.385 | 61.4572 | 122.9614 | 61.4533 | 122.7488 | 61.4889 | 61.4928 | 61.4247 | 61.4286
460.8906 | 123.1888 | -61.4502 | 61.5555 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5005 | 0.16622 | 61.4363 | -0.055996 | 0.007032 | 61.5204 | 0.007721 | 61.3077 | 61.4759 | 61.4097 | 61.4336 | 61.4526 | 61.4773 | 61.4625 | 61.479 | 122.9507 | 61.6164 | 122.8865 | 61.3942 | 61.4572 | 122.9706 | 61.4579 | 122.7579 | 61.4934 | 61.4928 | 61.4293 | 61.4286
461.8906 | 123.2025 | -61.4182 | 61.5463 | 0.021127 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.024268 | 61.505 | 0.16164 | 61.4317 | -0.046838 | 0.01161 | 61.5158 | 0.007721 | 61.3077 | 61.4393 | 61.3731 | 61.4062 | 61.4114 | 61.4453 | 61.4259 | 61.4424 | 122.9232 | 61.5798 | 122.8499 | 61.3713 | 61.4298 | 122.934 | 61.4259 | 122.7259 | 61.4934 | 61.4973 | 61.4201 | 61.424
462.8906 | 123.2117 | -61.441 | 61.5463 | 0.01197 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | 0.00775 | 0.033424 | 61.5005 | 0.15706 | 61.4409 | -0.046838 | 0.01161 | 61.5204 | 0.012299 | 61.3031 | 61.453 | 61.4005 | 61.4199 | 61.4389 | 61.4681 | 61.4488 | 61.4745 | 122.9415 | 61.5981 | 122.8819 | 61.3942 | 61.4526 | 122.9614 | 61.4533 | 122.7442 | 61.4889 | 61.4882 | 61.4293 | 61.4286
463.8906 | 123.143 | -61.4868 | 61.5738 | 0.025705 | -0.035942 | -0.012 | -0.006703 | 0.027109 | 0.012329 | 0.028846 | 61.5005 | 0.16622 | 61.4409 | -0.051417 | 0.007032 | 61.525 | 0.003143 | 61.3031 | 61.5125 | 61.4509 | 61.4748 | 61.4801 | 61.5139 | 61.4991 | 61.5157 | 122.9873 | 61.653 | 122.9277 | 61.4354 | 61.4938 | 123.0118 | 61.49 | 122.79 | 61.4934 | 61.4973 | 61.4339 | 61.4377
464.8906 | 123.3215 | -61.4731 | 61.5051 | 0.016548 | -0.035942 | -0.012 | -0.006703 | 0.022531 | 0.00775 | 0.024268 | 61.505 | 0.17537 | 61.4363 | -0.051417 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4896 | 61.4371 | 61.4611 | 61.4664 | 61.4956 | 61.4808 | 61.4974 | 122.9781 | 61.6485 | 122.9094 | 61.4217 | 61.4847 | 122.9935 | 61.4808 | 122.7808 | 61.4934 | 61.4973 | 61.4247 | 61.4286
465.8906 | 123.3307 | -61.441 | 61.5097 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.024268 | 61.4959 | 0.16164 | 61.4363 | -0.060575 | 0.01161 | 61.5204 | -0.001436 | 61.3123 | 61.4622 | 61.4005 | 61.4245 | 61.4435 | 61.4681 | 61.4579 | 61.4653 | 122.9369 | 61.6027 | 122.8773 | 61.3805 | 61.4526 | 122.9614 | 61.4396 | 122.7533 | 61.4843 | 61.4973 | 61.4247 | 61.4377
466.8906 | 123.3765 | -61.4273 | 61.5417 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.00775 | 0.024268 | 61.5005 | 0.16164 | 61.4409 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3031 | 61.453 | 61.3914 | 61.4107 | 61.4252 | 61.4636 | 61.4351 | 61.4516 | 122.9278 | 61.5889 | 122.8682 | 61.3713 | 61.4389 | 122.9523 | 61.435 | 122.7305 | 61.4889 | 61.4928 | 61.4293 | 61.4332
467.8906 | 123.349 | -61.3953 | 61.5417 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.5096 | 0.16164 | 61.4409 | -0.051417 | 0.01161 | 61.525 | 0.007721 | 61.3031 | 61.421 | 61.3547 | 61.3787 | 61.3977 | 61.427 | 61.403 | 61.4195 | 122.9049 | 61.5569 | 122.8361 | 61.3438 | 61.4069 | 122.9202 | 61.403 | 122.6984 | 61.498 | 61.5019 | 61.4293 | 61.4332
468.8906 | 123.2895 | -61.4044 | 61.5372 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.505 | 0.16622 | 61.4271 | -0.060575 | 0.01161 | 61.5158 | 0.007721 | 61.3077 | 61.421 | 61.3639 | 61.3878 | 61.4069 | 61.4315 | 61.4122 | 61.4333 | 122.9095 | 61.5706 | 122.8316 | 61.3438 | 61.416 | 122.9202 | 61.4121 | 122.7121 | 61.4934 | 61.4973 | 61.4155 | 61.4194
469.8906 | 123.349 | -61.3998 | 61.5372 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.5096 | 0.16622 | 61.4317 | -0.060575 | 0.016188 | 61.5295 | 0.003143 | 61.3077 | 61.421 | 61.3639 | 61.3833 | 61.3977 | 61.427 | 61.4076 | 61.4241 | 122.9095 | 61.5661 | 122.8316 | 61.3393 | 61.416 | 122.9294 | 61.403 | 122.7076 | 61.4934 | 61.5065 | 61.4155 | 61.4286
470.8906 | 123.3032 | -61.4594 | 61.5326 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.016907 | 0.024268 | 61.505 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3031 | 61.4805 | 61.4188 | 61.4428 | 61.4618 | 61.491 | 61.4763 | 61.4836 | 122.9644 | 61.621 | 122.8911 | 61.4034 | 61.471 | 122.9797 | 61.4671 | 122.7625 | 61.4934 | 61.4973 | 61.4201 | 61.424
471.8906 | 123.2666 | -61.4182 | 61.528 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.021485 | 0.028846 | 61.5005 | 0.16622 | 61.4363 | -0.051417 | 0.007032 | 61.525 | 0.012299 | 61.3077 | 61.4347 | 61.3776 | 61.4062 | 61.416 | 61.4407 | 61.4396 | 61.447 | 122.9186 | 61.5844 | 122.8545 | 61.3667 | 61.4252 | 122.9431 | 61.4305 | 122.7259 | 61.4934 | 61.4882 | 61.4293 | 61.424
472.8906 | 123.2895 | -61.4319 | 61.5463 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.5005 | 0.16164 | 61.4409 | -0.060575 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.453 | 61.3914 | 61.4153 | 61.4343 | 61.459 | 61.4396 | 61.4562 | 122.9324 | 61.5935 | 122.8728 | 61.3713 | 61.4435 | 122.9568 | 61.4396 | 122.7442 | 61.4889 | 61.4928 | 61.4293 | 61.4332
473.8906 | 123.2391 | -61.4365 | 61.5234 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.505 | 0.15248 | 61.4409 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.2986 | 61.4576 | 61.4005 | 61.4199 | 61.4343 | 61.4636 | 61.4488 | 61.4607 | 122.9415 | 61.5889 | 122.8773 | 61.3805 | 61.4481 | 122.9568 | 61.4442 | 122.735 | 61.4934 | 61.4973 | 61.4293 | 61.4332
474.8906 | 123.2574 | -61.441 | 61.496 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.016907 | 0.024268 | 61.5005 | 0.16164 | 61.4409 | -0.060575 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.4622 | 61.4005 | 61.429 | 61.4481 | 61.4681 | 61.4579 | 61.4653 | 122.9415 | 61.6027 | 122.8819 | 61.3805 | 61.4526 | 122.966 | 61.4488 | 122.7488 | 61.4889 | 61.4928 | 61.4293 | 61.4332
475.8906 | 123.2849 | -61.4182 | 61.5326 | 0.025705 | -0.031363 | -0.007421 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.5096 | 0.16622 | 61.4271 | -0.060575 | 0.020767 | 61.5204 | -0.001436 | 61.2986 | 61.4439 | 61.3868 | 61.4107 | 61.416 | 61.4453 | 61.4259 | 61.4424 | 122.9278 | 61.5844 | 122.8453 | 61.3576 | 61.4389 | 122.9385 | 61.4167 | 122.7167 | 61.4889 | 61.5111 | 61.4064 | 61.4286
476.8906 | 123.2941 | -61.409 | 61.5417 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.012329 | 0.024268 | 61.5005 | 0.16164 | 61.4363 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3031 | 61.4347 | 61.3685 | 61.3924 | 61.416 | 61.4361 | 61.4213 | 61.4333 | 122.9095 | 61.5706 | 122.8453 | 61.353 | 61.4252 | 122.934 | 61.4167 | 122.7121 | 61.4843 | 61.4928 | 61.4201 | 61.4286
477.8906 | 123.2849 | -61.4273 | 61.5234 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.00775 | 0.028846 | 61.505 | 0.16622 | 61.4409 | -0.051417 | 0.01161 | 61.525 | 0.007721 | 61.3031 | 61.4484 | 61.3868 | 61.4107 | 61.4298 | 61.4498 | 61.4351 | 61.4562 | 122.9324 | 61.5935 | 122.8682 | 61.3759 | 61.4389 | 122.9523 | 61.435 | 122.7305 | 61.4934 | 61.4973 | 61.4293 | 61.4332
478.8906 | 123.2208 | -61.441 | 61.5463 | 0.016548 | -0.040521 | -0.016578 | -0.006703 | 0.027109 | 0.016907 | 0.024268 | 61.505 | 0.15706 | 61.4409 | -0.046838 | 0.016188 | 61.525 | 0.007721 | 61.3031 | 61.4576 | 61.4005 | 61.4245 | 61.4343 | 61.4681 | 61.4579 | 61.4653 | 122.9461 | 61.5981 | 122.8819 | 61.3942 | 61.4572 | 122.966 | 61.4488 | 122.7442 | 61.4889 | 61.4973 | 61.4247 | 61.4332
479.8906 | 123.2483 | -61.4456 | 61.5509 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.01969 | 61.5005 | 0.15706 | 61.4409 | -0.065154 | 0.016188 | 61.5204 | 0.007721 | 61.3031 | 61.4713 | 61.4097 | 61.429 | 61.4481 | 61.4773 | 61.4534 | 61.4653 | 122.9461 | 61.6027 | 122.8865 | 61.3805 | 61.4618 | 122.966 | 61.4533 | 122.7488 | 61.4843 | 61.4928 | 61.4247 | 61.4332
480.8906 | 123.2849 | -61.4319 | 61.5463 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.5096 | 0.16622 | 61.4409 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3077 | 61.4576 | 61.3914 | 61.4199 | 61.4298 | 61.4544 | 61.4351 | 61.4562 | 122.9415 | 61.5981 | 122.8728 | 61.3759 | 61.4435 | 122.9568 | 61.4442 | 122.7396 | 61.498 | 61.4973 | 61.4293 | 61.4286
481.8906 | 123.2574 | -61.4273 | 61.5692 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.4959 | 0.16622 | 61.4409 | -0.060575 | 0.016188 | 61.5204 | 0.003143 | 61.3031 | 61.4484 | 61.3868 | 61.4107 | 61.4252 | 61.4544 | 61.4396 | 61.4516 | 122.9232 | 61.5935 | 122.8682 | 61.3667 | 61.4435 | 122.9477 | 61.4305 | 122.7305 | 61.4797 | 61.4928 | 61.4247 | 61.4377
482.8906 | 123.2574 | -61.4227 | 61.5509 | 0.021127 | -0.040521 | -0.021157 | -0.002124 | 0.022531 | 0.012329 | 0.028846 | 61.505 | 0.16622 | 61.4317 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3031 | 61.4439 | 61.3822 | 61.4016 | 61.4206 | 61.4453 | 61.4351 | 61.4516 | 122.9278 | 61.5889 | 122.8545 | 61.3667 | 61.4343 | 122.9431 | 61.4259 | 122.7259 | 61.4934 | 61.5019 | 61.4201 | 61.4286
483.8906 | 123.2666 | -61.4502 | 61.5189 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.01969 | 61.505 | 0.16164 | 61.4317 | -0.060575 | 0.002454 | 61.525 | 0.007721 | 61.3123 | 61.4713 | 61.4097 | 61.4336 | 61.4526 | 61.4773 | 61.4579 | 61.4699 | 122.9552 | 61.6118 | 122.8819 | 61.3896 | 61.4526 | 122.9752 | 61.4579 | 122.7625 | 61.5026 | 61.4973 | 61.4293 | 61.424
484.8906 | 123.3078 | -61.4136 | 61.528 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.01969 | 61.505 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4301 | 61.3731 | 61.397 | 61.416 | 61.4407 | 61.4213 | 61.4333 | 122.9186 | 61.5752 | 122.8453 | 61.3576 | 61.4252 | 122.934 | 61.4213 | 122.7213 | 61.4934 | 61.4973 | 61.4201 | 61.424
485.8906 | 123.2529 | -61.4365 | 61.5417 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.01969 | 61.5096 | 0.16164 | 61.4363 | -0.051417 | 0.01161 | 61.5204 | 0.007721 | 61.3031 | 61.4622 | 61.3959 | 61.4199 | 61.4389 | 61.4636 | 61.4396 | 61.4562 | 122.9461 | 61.5981 | 122.8728 | 61.385 | 61.4481 | 122.9568 | 61.4442 | 122.7396 | 61.498 | 61.5019 | 61.4247 | 61.4286
486.8906 | 123.2391 | -61.4227 | 61.5372 | 0.025705 | -0.040521 | -0.021157 | -0.002124 | 0.027109 | -0.001406 | 0.01969 | 61.505 | 0.16622 | 61.4317 | -0.051417 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4484 | 61.3822 | 61.4016 | 61.4206 | 61.4498 | 61.4213 | 61.4424 | 122.9278 | 61.5889 | 122.8545 | 61.3713 | 61.4343 | 122.9431 | 61.4304 | 122.7305 | 61.4934 | 61.4973 | 61.4201 | 61.424
487.8906 | 123.2483 | -61.4456 | 61.5601 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.021485 | 0.028846 | 61.5005 | 0.16164 | 61.4409 | -0.051417 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4622 | 61.4051 | 61.4336 | 61.4435 | 61.4727 | 61.4671 | 61.4745 | 122.9461 | 61.6073 | 122.8865 | 61.3942 | 61.4618 | 122.966 | 61.4533 | 122.7533 | 61.4843 | 61.4928 | 61.4247 | 61.4332
488.8906 | 123.2895 | -61.4319 | 61.5555 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.024268 | 61.505 | 0.16164 | 61.4409 | -0.046838 | 0.01161 | 61.525 | 0.003143 | 61.3077 | 61.4484 | 61.3868 | 61.4153 | 61.4298 | 61.4636 | 61.4442 | 61.4562 | 122.9369 | 61.5935 | 122.8728 | 61.385 | 61.4435 | 122.9568 | 61.435 | 122.7396 | 61.4934 | 61.5019 | 61.4293 | 61.4377
489.8906 | 123.2803 | -61.441 | 61.5509 | 0.01197 | -0.040521 | -0.016578 | -0.006703 | 0.022531 | 0.003172 | 0.01969 | 61.505 | 0.16164 | 61.4363 | -0.051417 | 0.01161 | 61.5204 | 0.007721 | 61.3031 | 61.453 | 61.4005 | 61.4245 | 61.4343 | 61.4636 | 61.4442 | 61.4607 | 122.9461 | 61.6027 | 122.8773 | 61.3896 | 61.4526 | 122.9614 | 61.4488 | 122.7442 | 61.4934 | 61.4973 | 61.4247 | 61.4286
490.8906 | 123.2483 | -61.4502 | 61.528 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.033424 | 61.5005 | 0.16164 | 61.4363 | -0.055996 | 0.01161 | 61.5295 | 0.007721 | 61.3077 | 61.4713 | 61.4097 | 61.4336 | 61.4526 | 61.4727 | 61.4625 | 61.4836 | 122.9507 | 61.6118 | 122.8865 | 61.3942 | 61.4618 | 122.9797 | 61.4579 | 122.7579 | 61.4889 | 61.4928 | 61.4247 | 61.4286
491.8906 | 123.2391 | -61.4319 | 61.5646 | 0.030283 | -0.035942 | -0.002842 | -0.002124 | 0.036265 | 0.012329 | 0.028846 | 61.505 | 0.16164 | 61.4455 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4622 | 61.3959 | 61.429 | 61.4298 | 61.4682 | 61.4442 | 61.4607 | 122.9369 | 61.5935 | 122.8773 | 61.3713 | 61.4481 | 122.9568 | 61.4396 | 122.7396 | 61.4889 | 61.4973 | 61.4293 | 61.4377
492.8906 | 123.2254 | -61.4319 | 61.5555 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.022531 | 0.016907 | 0.024268 | 61.505 | 0.17079 | 61.4363 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3031 | 61.4576 | 61.3868 | 61.4199 | 61.4389 | 61.4544 | 61.4488 | 61.4562 | 122.9369 | 61.6027 | 122.8682 | 61.3713 | 61.4481 | 122.9568 | 61.4396 | 122.735 | 61.4889 | 61.4973 | 61.4201 | 61.4286
493.8906 | 123.23 | -61.441 | 61.5326 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.003172 | 0.01969 | 61.505 | 0.17079 | 61.4409 | -0.060575 | 0.016188 | 61.525 | 0.016878 | 61.3077 | 61.4576 | 61.4005 | 61.4245 | 61.4481 | 61.4727 | 61.4442 | 61.4607 | 122.9461 | 61.6118 | 122.8819 | 61.3805 | 61.4572 | 122.966 | 61.4579 | 122.7488 | 61.4889 | 61.4882 | 61.4247 | 61.424
494.8906 | 123.2529 | -61.3907 | 61.5509 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.022531 | 0.003172 | 0.028846 | 61.505 | 0.16164 | 61.4455 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4164 | 61.3547 | 61.3787 | 61.3931 | 61.4132 | 61.3939 | 61.4195 | 122.8957 | 61.5523 | 122.8361 | 61.3393 | 61.4069 | 122.9202 | 61.3984 | 122.6938 | 61.4889 | 61.4973 | 61.4293 | 61.4377
495.8906 | 123.2162 | -61.4227 | 61.5555 | 0.021127 | -0.040521 | -0.016578 | -0.011281 | 0.031687 | 0.012329 | 0.01969 | 61.505 | 0.17079 | 61.4363 | -0.046838 | 0.016188 | 61.5204 | 0.003143 | 61.3077 | 61.4439 | 61.3822 | 61.4062 | 61.4114 | 61.4544 | 61.4351 | 61.4424 | 122.9278 | 61.5935 | 122.859 | 61.3759 | 61.4389 | 122.9431 | 61.4259 | 122.7305 | 61.4889 | 61.5019 | 61.4201 | 61.4332
496.8906 | 123.2483 | -61.409 | 61.5463 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.015112 | 61.505 | 0.16622 | 61.4363 | -0.051417 | 0.007032 | 61.525 | 0.007721 | 61.3077 | 61.4347 | 61.3685 | 61.3924 | 61.4115 | 61.4361 | 61.4167 | 61.4241 | 122.914 | 61.5752 | 122.8453 | 61.3576 | 61.416 | 122.934 | 61.4167 | 122.7167 | 61.498 | 61.4973 | 61.4293 | 61.4286
497.8906 | 123.2712 | -61.4639 | 61.5234 | 0.025705 | -0.035942 | -0.016578 | 0.007033 | 0.022531 | 0.00775 | 0.01969 | 61.5005 | 0.16622 | 61.4271 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4896 | 61.428 | 61.4474 | 61.471 | 61.4865 | 61.4717 | 61.4836 | 122.9644 | 61.6301 | 122.8911 | 61.4125 | 61.4801 | 122.9889 | 61.4716 | 122.7717 | 61.4843 | 61.4928 | 61.411 | 61.4194
498.8906 | 123.262 | -61.4319 | 61.5143 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.01969 | 61.505 | 0.16622 | 61.4409 | -0.055996 | 0.016188 | 61.5295 | 0.012299 | 61.3169 | 61.453 | 61.3914 | 61.4153 | 61.4298 | 61.459 | 61.4351 | 61.4516 | 122.9369 | 61.5981 | 122.8728 | 61.3759 | 61.4481 | 122.9614 | 61.4442 | 122.7488 | 61.4889 | 61.4928 | 61.4247 | 61.4286
499.8906 | 123.2803 | -61.4273 | 61.5601 | 0.01197 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.024268 | 61.505 | 0.16622 | 61.4409 | -0.055996 | 0.007032 | 61.5295 | 0.003143 | 61.3077 | 61.4393 | 61.3868 | 61.4107 | 61.4252 | 61.4544 | 61.4305 | 61.4516 | 122.9324 | 61.5935 | 122.8682 | 61.3713 | 61.4343 | 122.9568 | 61.4305 | 122.735 | 61.498 | 61.5019 | 61.4339 | 61.4377
500.8906 | 123.2483 | -61.4227 | 61.5372 | 0.021127 | -0.0451 | -0.007421 | -0.006703 | 0.027109 | 0.016907 | 0.024268 | 61.5096 | 0.16622 | 61.4409 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4439 | 61.3776 | 61.4153 | 61.416 | 61.4498 | 61.4396 | 61.447 | 122.9324 | 61.5889 | 122.8636 | 61.3667 | 61.4343 | 122.9431 | 61.4259 | 122.7305 | 61.498 | 61.5065 | 61.4293 | 61.4377
501.8906 | 123.2162 | -61.4273 | 61.5463 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.024268 | 61.505 | 0.16622 | 61.4455 | -0.060575 | 0.007032 | 61.525 | 0.003143 | 61.3031 | 61.4439 | 61.3868 | 61.4153 | 61.4298 | 61.459 | 61.4442 | 61.4516 | 122.9324 | 61.5935 | 122.8728 | 61.3667 | 61.4343 | 122.9523 | 61.4305 | 122.7305 | 61.498 | 61.5019 | 61.4384 | 61.4423
502.8906 | 123.2483 | -61.4365 | 61.5326 | 0.025705 | -0.049678 | -0.012 | 0.007033 | 0.027109 | 0.012329 | 0.01969 | 61.5005 | 0.17079 | 61.4317 | -0.055996 | 0.01161 | 61.525 | 0.003143 | 61.3031 | 61.4622 | 61.3868 | 61.4245 | 61.4435 | 61.4636 | 61.4488 | 61.4562 | 122.9369 | 61.6073 | 122.8682 | 61.3805 | 61.4481 | 122.9614 | 61.4396 | 122.7396 | 61.4889 | 61.4973 | 61.4201 | 61.4286
503.8906 | 123.3032 | -61.4456 | 61.5555 | 0.016548 | -0.049678 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.028846 | 61.5096 | 0.17079 | 61.45 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4622 | 61.3959 | 61.429 | 61.4435 | 61.4681 | 61.4579 | 61.4745 | 122.9552 | 61.6164 | 122.8957 | 61.385 | 61.4618 | 122.9706 | 61.4533 | 122.7533 | 61.4934 | 61.5019 | 61.4339 | 61.4423
504.8906 | 123.2117 | -61.4319 | 61.5555 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.028846 | 61.5096 | 0.16622 | 61.4317 | -0.060575 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.4484 | 61.3868 | 61.4153 | 61.4343 | 61.4544 | 61.4442 | 61.4607 | 122.9415 | 61.5981 | 122.8636 | 61.3713 | 61.4435 | 122.9568 | 61.4396 | 122.7396 | 61.498 | 61.5019 | 61.4201 | 61.424
505.8906 | 123.2254 | -61.4273 | 61.5509 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.5096 | 0.16164 | 61.45 | -0.055996 | 0.016188 | 61.525 | 0.012299 | 61.3077 | 61.4484 | 61.3868 | 61.4153 | 61.4252 | 61.4498 | 61.4396 | 61.4516 | 122.9369 | 61.5889 | 122.8773 | 61.3713 | 61.4435 | 122.9523 | 61.4396 | 122.735 | 61.4934 | 61.4973 | 61.4339 | 61.4377
506.8906 | 123.23 | -61.4456 | 61.5509 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.01969 | 61.505 | 0.16164 | 61.4409 | -0.055996 | 0.01161 | 61.525 | -0.001436 | 61.3077 | 61.4667 | 61.4005 | 61.429 | 61.4481 | 61.4727 | 61.4625 | 61.4653 | 122.9507 | 61.6073 | 122.8865 | 61.3896 | 61.4572 | 122.9706 | 61.4442 | 122.7533 | 61.4934 | 61.5065 | 61.4293 | 61.4423
507.8906 | 123.2574 | -61.4365 | 61.5555 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5005 | 0.16622 | 61.4409 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3077 | 61.4576 | 61.3914 | 61.4199 | 61.4389 | 61.4636 | 61.4396 | 61.4607 | 122.9369 | 61.6027 | 122.8773 | 61.3805 | 61.4481 | 122.9614 | 61.4488 | 122.7442 | 61.4889 | 61.4882 | 61.4293 | 61.4286
508.8906 | 123.2162 | -61.4319 | 61.5646 | 0.021127 | -0.040521 | -0.021157 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.505 | 0.16164 | 61.4317 | -0.055996 | 0.01161 | 61.5295 | 0.012299 | 61.3031 | 61.453 | 61.3914 | 61.4107 | 61.4298 | 61.4636 | 61.4351 | 61.4562 | 122.9369 | 61.5935 | 122.8636 | 61.3759 | 61.4435 | 122.9614 | 61.4442 | 122.735 | 61.4934 | 61.4928 | 61.4201 | 61.4194
509.8906 | 123.2254 | -61.4594 | 61.5601 | 0.016548 | -0.0451 | -0.007421 | 0.002454 | 0.022531 | 0.003172 | 0.024268 | 61.505 | 0.17079 | 61.4455 | -0.060575 | 0.01161 | 61.5158 | 0.007721 | 61.3031 | 61.4759 | 61.4143 | 61.4519 | 61.4618 | 61.4819 | 61.4625 | 61.4836 | 122.9644 | 61.6301 | 122.9048 | 61.3988 | 61.471 | 122.9752 | 61.4671 | 122.7625 | 61.4934 | 61.4973 | 61.4339 | 61.4377
510.8906 | 123.262 | -61.4502 | 61.5326 | 0.016548 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.015112 | 61.505 | 0.16622 | 61.4409 | -0.055996 | 0.007032 | 61.5158 | 0.003143 | 61.3077 | 61.4667 | 61.4143 | 61.4336 | 61.4526 | 61.4773 | 61.4625 | 61.4653 | 122.9552 | 61.6164 | 122.8911 | 61.3942 | 61.4572 | 122.966 | 61.4533 | 122.7579 | 61.498 | 61.5019 | 61.4339 | 61.4377
511.8906 | 123.262 | -61.4456 | 61.5372 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.505 | 0.16622 | 61.45 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.3077 | 61.4667 | 61.4051 | 61.4245 | 61.4481 | 61.4727 | 61.4579 | 61.4699 | 122.9507 | 61.6118 | 122.8957 | 61.3896 | 61.4664 | 122.9706 | 61.4579 | 122.7533 | 61.4843 | 61.4928 | 61.4293 | 61.4377
512.8906 | 123.3307 | -61.4182 | 61.5372 | 0.01197 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.01969 | 61.505 | 0.17079 | 61.4317 | -0.051417 | 0.01161 | 61.525 | 0.003143 | 61.3077 | 61.4301 | 61.3731 | 61.4062 | 61.416 | 61.4453 | 61.4259 | 61.4378 | 122.9232 | 61.5889 | 122.8499 | 61.3667 | 61.4298 | 122.9431 | 61.4213 | 122.7259 | 61.4934 | 61.5019 | 61.4201 | 61.4286
513.8906 | 123.1522 | -61.441 | 61.6104 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.027109 | 0.016907 | 0.024268 | 61.5142 | 0.16622 | 61.45 | -0.051417 | 0.01161 | 61.5341 | 0.007721 | 61.3031 | 61.4622 | 61.4051 | 61.429 | 61.4389 | 61.4681 | 61.4579 | 61.4653 | 122.9552 | 61.6073 | 122.8911 | 61.3896 | 61.4526 | 122.9752 | 61.4488 | 122.7442 | 61.5026 | 61.5065 | 61.4384 | 61.4423
514.8906 | 123.2712 | -61.4136 | 61.5372 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.01969 | 61.5096 | 0.16622 | 61.4409 | -0.060575 | 0.01161 | 61.5204 | 0.007721 | 61.3077 | 61.4347 | 61.3731 | 61.397 | 61.4114 | 61.4361 | 61.4167 | 61.4333 | 122.9232 | 61.5798 | 122.8545 | 61.353 | 61.4252 | 122.934 | 61.4213 | 122.7213 | 61.498 | 61.5019 | 61.4293 | 61.4332
515.8906 | 123.2803 | -61.4502 | 61.5692 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.003172 | 0.01969 | 61.5005 | 0.17079 | 61.4455 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4713 | 61.4143 | 61.4382 | 61.4526 | 61.4865 | 61.4534 | 61.4699 | 122.9507 | 61.621 | 122.8957 | 61.3896 | 61.4664 | 122.9752 | 61.4579 | 122.7579 | 61.4843 | 61.4928 | 61.4293 | 61.4377
516.8906 | 123.2574 | -61.4456 | 61.5646 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.022531 | 0.00775 | 0.024268 | 61.5096 | 0.17079 | 61.4409 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3077 | 61.4667 | 61.4097 | 61.4336 | 61.4527 | 61.4681 | 61.4534 | 61.4699 | 122.9552 | 61.6164 | 122.8865 | 61.3942 | 61.4618 | 122.9752 | 61.4579 | 122.7533 | 61.4934 | 61.4973 | 61.4247 | 61.4286
517.8906 | 123.23 | -61.4594 | 61.5417 | 0.021127 | -0.035942 | -0.007421 | 0.007033 | 0.027109 | 0.016907 | 0.01969 | 61.5005 | 0.16622 | 61.4409 | -0.055996 | 0.007032 | 61.525 | 0.007721 | 61.3077 | 61.4805 | 61.4234 | 61.4519 | 61.4664 | 61.4865 | 61.4763 | 61.479 | 122.9598 | 61.6256 | 122.9002 | 61.4034 | 61.4664 | 122.9843 | 61.4671 | 122.7671 | 61.4934 | 61.4928 | 61.4339 | 61.4332
518.8906 | 123.2391 | -61.4456 | 61.6058 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.505 | 0.16622 | 61.4409 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3123 | 61.4622 | 61.4051 | 61.4336 | 61.4481 | 61.4727 | 61.4534 | 61.4699 | 122.9507 | 61.6118 | 122.8865 | 61.3896 | 61.4618 | 122.966 | 61.4533 | 122.7579 | 61.4889 | 61.4973 | 61.4247 | 61.4332
519.8906 | 123.2712 | -61.4319 | 61.5646 | 0.016548 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.505 | 0.17079 | 61.4409 | -0.055996 | 0.016188 | 61.5204 | 0.003143 | 61.3077 | 61.4484 | 61.3868 | 61.4153 | 61.4298 | 61.459 | 61.4442 | 61.4562 | 122.9369 | 61.6027 | 122.8728 | 61.3759 | 61.4481 | 122.9523 | 61.435 | 122.7396 | 61.4889 | 61.5019 | 61.4247 | 61.4377
520.8906 | 123.317 | -61.4136 | 61.5509 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.016907 | 0.024268 | 61.505 | 0.16164 | 61.4409 | -0.060575 | 0.016188 | 61.5204 | 0.007721 | 61.3169 | 61.4301 | 61.3731 | 61.397 | 61.4206 | 61.4407 | 61.4305 | 61.4378 | 122.9186 | 61.5752 | 122.8545 | 61.353 | 61.4298 | 122.934 | 61.4213 | 122.7305 | 61.4889 | 61.4973 | 61.4247 | 61.4332
521.8906 | 123.2895 | -61.4456 | 61.5967 | 0.025705 | -0.040521 | -0.021157 | -0.006703 | 0.027109 | 0.012329 | 0.028846 | 61.5096 | 0.17079 | 61.4363 | -0.060575 | 0.01161 | 61.525 | 0.012299 | 61.3031 | 61.4713 | 61.4051 | 61.4245 | 61.4389 | 61.4727 | 61.4579 | 61.4745 | 122.9552 | 61.6164 | 122.8819 | 61.385 | 61.4572 | 122.9706 | 61.4579 | 122.7488 | 61.498 | 61.4973 | 61.4247 | 61.424
522.8906 | 123.3078 | -61.3953 | 61.5509 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5096 | 0.16622 | 61.4455 | -0.060575 | 0.016188 | 61.5204 | 0.003143 | 61.3031 | 61.4164 | 61.3547 | 61.3787 | 61.3977 | 61.4224 | 61.4076 | 61.4195 | 122.9049 | 61.5615 | 122.8407 | 61.3347 | 61.4115 | 122.9156 | 61.3984 | 122.6984 | 61.4934 | 61.5065 | 61.4293 | 61.4423
523.8906 | 123.1888 | -61.4273 | 61.6196 | 0.021127 | -0.0451 | -0.021157 | 0.002454 | 0.027109 | 0.016907 | 0.028846 | 61.5142 | 0.16622 | 61.4455 | -0.051417 | 0.020767 | 61.5204 | 0.007721 | 61.3123 | 61.4484 | 61.3822 | 61.4061 | 61.4298 | 61.4544 | 61.4442 | 61.4562 | 122.9415 | 61.5935 | 122.8728 | 61.3759 | 61.4481 | 122.9477 | 61.435 | 122.7396 | 61.4934 | 61.5065 | 61.4247 | 61.4377
524.8906 | 123.3353 | -61.3907 | 61.5829 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.505 | 0.16164 | 61.4455 | -0.055996 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.4118 | 61.3502 | 61.3787 | 61.3886 | 61.4178 | 61.3984 | 61.415 | 122.8957 | 61.5523 | 122.8361 | 61.3347 | 61.4115 | 122.9202 | 61.3938 | 122.703 | 61.4843 | 61.5019 | 61.4247 | 61.4423
525.8906 | 123.2529 | -61.4365 | 61.5417 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.024268 | 61.505 | 0.16622 | 61.4409 | -0.051417 | 0.01161 | 61.525 | 0.012299 | 61.3123 | 61.453 | 61.3959 | 61.4245 | 61.4389 | 61.459 | 61.4442 | 61.4607 | 122.9415 | 61.6027 | 122.8773 | 61.385 | 61.4481 | 122.9614 | 61.4488 | 122.7488 | 61.4934 | 61.4928 | 61.4293 | 61.4286
526.8906 | 123.3124 | -61.409 | 61.5555 | 0.021127 | -0.0451 | -0.007421 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.5096 | 0.16622 | 61.4409 | -0.060575 | 0.007032 | 61.5341 | 0.003143 | 61.3077 | 61.4301 | 61.3639 | 61.4016 | 61.4115 | 61.4315 | 61.4213 | 61.4287 | 122.9186 | 61.5752 | 122.8499 | 61.3484 | 61.416 | 122.9431 | 61.4121 | 122.7167 | 61.5026 | 61.5065 | 61.4339 | 61.4377
527.8906 | 123.317 | -61.4044 | 61.5463 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.01969 | 61.505 | 0.17079 | 61.4363 | -0.060575 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4255 | 61.3593 | 61.3878 | 61.4023 | 61.4361 | 61.4213 | 61.4241 | 122.9095 | 61.5752 | 122.8407 | 61.3438 | 61.416 | 122.9248 | 61.4076 | 122.7121 | 61.4934 | 61.5019 | 61.4247 | 61.4332
528.8906 | 123.0789 | -61.5005 | 61.5509 | 0.021127 | -0.049678 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.024268 | 61.5096 | 0.16622 | 61.4363 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.5217 | 61.4509 | 61.4885 | 61.503 | 61.5322 | 61.5037 | 61.5248 | 123.0102 | 61.6668 | 122.9369 | 61.4446 | 61.5167 | 123.0255 | 61.5083 | 122.8083 | 61.4934 | 61.5019 | 61.4201 | 61.4286
529.8906 | 123.317 | -61.409 | 61.5692 | 0.016548 | -0.0451 | -0.012 | -0.011281 | 0.027109 | 0.016907 | 0.024268 | 61.5096 | 0.17079 | 61.4455 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3077 | 61.4255 | 61.3639 | 61.397 | 61.3977 | 61.4361 | 61.4259 | 61.4333 | 122.9186 | 61.5798 | 122.8545 | 61.353 | 61.4206 | 122.934 | 61.4213 | 122.7167 | 61.498 | 61.4973 | 61.4339 | 61.4332
530.8906 | 123.2895 | -61.409 | 61.5463 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.028846 | 61.5096 | 0.16622 | 61.4409 | -0.046838 | 0.016188 | 61.5204 | 0.003143 | 61.3077 | 61.4301 | 61.3685 | 61.397 | 61.416 | 61.4453 | 61.4167 | 61.4378 | 122.9186 | 61.5752 | 122.8499 | 61.3622 | 61.4252 | 122.9294 | 61.4121 | 122.7167 | 61.4934 | 61.5065 | 61.4247 | 61.4377
531.8906 | 123.2941 | -61.4136 | 61.5646 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.00775 | 0.015112 | 61.5096 | 0.16164 | 61.45 | -0.060575 | 0.016188 | 61.5341 | 0.012299 | 61.3077 | 61.4347 | 61.3731 | 61.4062 | 61.416 | 61.4407 | 61.4213 | 61.4287 | 122.9232 | 61.5752 | 122.8636 | 61.353 | 61.4298 | 122.9477 | 61.4259 | 122.7213 | 61.4934 | 61.4973 | 61.4339 | 61.4377
532.8906 | 123.3353 | -61.4182 | 61.5555 | 0.01197 | -0.0451 | -0.012 | -0.006703 | 0.027109 | 0.016907 | 0.024268 | 61.5188 | 0.16622 | 61.4409 | -0.055996 | 0.016188 | 61.5295 | 0.003143 | 61.3169 | 61.4301 | 61.3731 | 61.4062 | 61.4114 | 61.4453 | 61.4351 | 61.4424 | 122.9369 | 61.5844 | 122.859 | 61.3622 | 61.4343 | 122.9477 | 61.4213 | 122.735 | 61.5026 | 61.5156 | 61.4247 | 61.4377
533.8906 | 123.2941 | -61.4136 | 61.5417 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5096 | 0.16164 | 61.45 | -0.055996 | 0.01161 | 61.525 | 0.003143 | 61.3123 | 61.4301 | 61.3731 | 61.397 | 61.416 | 61.4407 | 61.4259 | 61.4378 | 122.9232 | 61.5752 | 122.8636 | 61.3576 | 61.4252 | 122.9385 | 61.4167 | 122.7259 | 61.498 | 61.5065 | 61.4384 | 61.4469
534.8906 | 123.3261 | -61.409 | 61.5738 | 0.01197 | -0.040521 | -0.007421 | 0.002454 | 0.036265 | 0.012329 | 0.028846 | 61.5096 | 0.16622 | 61.4409 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3123 | 61.421 | 61.3685 | 61.4016 | 61.4115 | 61.4453 | 61.4213 | 61.4378 | 122.9186 | 61.5752 | 122.8499 | 61.3576 | 61.4252 | 122.9385 | 61.4167 | 122.7213 | 61.4934 | 61.5019 | 61.4247 | 61.4332
535.8906 | 123.1796 | -61.4502 | 61.6241 | 0.021127 | -0.040521 | -0.007421 | -0.006703 | 0.027109 | 0.012329 | 0.024268 | 61.5096 | 0.17079 | 61.4409 | -0.051417 | 0.016188 | 61.525 | 0.003143 | 61.3077 | 61.4713 | 61.4097 | 61.4428 | 61.4435 | 61.4773 | 61.4625 | 61.4745 | 122.9598 | 61.621 | 122.8911 | 61.3988 | 61.4664 | 122.9752 | 61.4533 | 122.7579 | 61.4934 | 61.5065 | 61.4247 | 61.4377
536.8906 | 123.2895 | -61.409 | 61.5784 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.505 | 0.17079 | 61.4455 | -0.051417 | 0.01161 | 61.525 | 0.012299 | 61.3031 | 61.4301 | 61.3639 | 61.3924 | 61.4115 | 61.4361 | 61.4213 | 61.4378 | 122.914 | 61.5798 | 122.8545 | 61.3576 | 61.4206 | 122.934 | 61.4213 | 122.7121 | 61.4934 | 61.4928 | 61.4339 | 61.4332
537.8906 | 123.2254 | -61.4273 | 61.5784 | 0.021127 | -0.035942 | -0.025735 | -0.002124 | 0.027109 | 0.012329 | 0.028846 | 61.5096 | 0.16164 | 61.4455 | -0.051417 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4484 | 61.3914 | 61.4016 | 61.4252 | 61.4544 | 61.4396 | 61.4562 | 122.9369 | 61.5889 | 122.8728 | 61.3759 | 61.4435 | 122.9523 | 61.4305 | 122.7396 | 61.4934 | 61.5065 | 61.4293 | 61.4423
538.8906 | 123.262 | -61.409 | 61.5784 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.028846 | 61.5142 | 0.16622 | 61.45 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4301 | 61.3731 | 61.3924 | 61.4069 | 61.4407 | 61.4259 | 61.4378 | 122.9232 | 61.5752 | 122.859 | 61.3484 | 61.4252 | 122.934 | 61.4167 | 122.7213 | 61.498 | 61.5065 | 61.4339 | 61.4423
539.8906 | 123.349 | -61.4136 | 61.5555 | 0.021127 | -0.049678 | -0.007421 | 0.002454 | 0.022531 | 0.00775 | 0.024268 | 61.5096 | 0.16164 | 61.4409 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4347 | 61.3639 | 61.4062 | 61.416 | 61.4361 | 61.4213 | 61.4378 | 122.9232 | 61.5752 | 122.8545 | 61.3576 | 61.4298 | 122.9385 | 61.4167 | 122.7259 | 61.4934 | 61.5065 | 61.4247 | 61.4377
540.8906 | 123.2346 | -61.4044 | 61.5738 | 0.021127 | -0.049678 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.5096 | 0.17079 | 61.45 | -0.060575 | 0.020767 | 61.525 | 0.012299 | 61.3123 | 61.4255 | 61.3547 | 61.3878 | 61.4069 | 61.4361 | 61.4122 | 61.4287 | 122.914 | 61.5752 | 122.8545 | 61.3438 | 61.4252 | 122.9294 | 61.4167 | 122.7167 | 61.4889 | 61.4973 | 61.4293 | 61.4377
541.8906 | 123.1934 | -61.4365 | 61.6058 | 0.025705 | -0.0451 | -0.007421 | -0.002124 | 0.040843 | 0.012329 | 0.028846 | 61.5142 | 0.16622 | 61.4455 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3123 | 61.4622 | 61.3914 | 61.429 | 61.4343 | 61.4773 | 61.4488 | 61.4653 | 122.9507 | 61.6027 | 122.8819 | 61.385 | 61.4572 | 122.9614 | 61.4442 | 122.7488 | 61.4934 | 61.5065 | 61.4247 | 61.4377
542.8906 | 123.1522 | -61.4548 | 61.6287 | 0.025705 | -0.0451 | -0.021157 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.505 | 0.17079 | 61.4455 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3077 | 61.4805 | 61.4097 | 61.4336 | 61.4572 | 61.4773 | 61.4671 | 61.479 | 122.9598 | 61.6256 | 122.9002 | 61.3988 | 61.4755 | 122.9843 | 61.4625 | 122.7625 | 61.4843 | 61.4973 | 61.4247 | 61.4377
543.8906 | 123.1613 | -61.4639 | 61.6379 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.5188 | 0.16164 | 61.4409 | -0.055996 | 0.016188 | 61.5204 | 0.012299 | 61.3123 | 61.4805 | 61.4188 | 61.4519 | 61.4664 | 61.4956 | 61.4717 | 61.4882 | 122.9827 | 61.6256 | 122.9048 | 61.4079 | 61.4801 | 122.9843 | 61.4762 | 122.7762 | 61.5026 | 61.5065 | 61.4247 | 61.4286
544.8906 | 123.2025 | -61.4365 | 61.6058 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.5142 | 0.17079 | 61.4455 | -0.051417 | 0.025345 | 61.5295 | 0.007721 | 61.3169 | 61.4576 | 61.3959 | 61.4199 | 61.4389 | 61.459 | 61.4488 | 61.4607 | 122.9507 | 61.6073 | 122.8819 | 61.385 | 61.4618 | 122.966 | 61.4442 | 122.7533 | 61.4889 | 61.5065 | 61.4201 | 61.4377
545.8906 | 123.1567 | -61.4639 | 61.6196 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5188 | 0.16622 | 61.4455 | -0.046838 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4851 | 61.4188 | 61.4519 | 61.4664 | 61.491 | 61.4717 | 61.4928 | 122.9827 | 61.6301 | 122.9094 | 61.4171 | 61.4847 | 122.9935 | 61.4716 | 122.7762 | 61.498 | 61.5111 | 61.4247 | 61.4377
546.8906 | 123.2391 | -61.4319 | 61.5921 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.024268 | 61.5096 | 0.16622 | 61.4409 | -0.060575 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4576 | 61.3914 | 61.4153 | 61.4343 | 61.459 | 61.4488 | 61.4562 | 122.9415 | 61.5981 | 122.8728 | 61.3713 | 61.4481 | 122.9568 | 61.435 | 122.7442 | 61.4934 | 61.5065 | 61.4247 | 61.4377
547.8906 | 123.1064 | -61.4456 | 61.615 | 0.025705 | -0.049678 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.024268 | 61.5096 | 0.16164 | 61.4546 | -0.051417 | 0.020767 | 61.525 | 0.012299 | 61.3123 | 61.4713 | 61.3959 | 61.429 | 61.4527 | 61.4727 | 61.4534 | 61.4699 | 122.9552 | 61.6073 | 122.9002 | 61.3942 | 61.4664 | 122.9706 | 61.4579 | 122.7579 | 61.4889 | 61.4973 | 61.4339 | 61.4423
548.8906 | 123.1796 | -61.4365 | 61.6241 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.021485 | 0.024268 | 61.5096 | 0.16622 | 61.4409 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3123 | 61.4576 | 61.3959 | 61.4245 | 61.4389 | 61.4636 | 61.4579 | 61.4607 | 122.9461 | 61.6027 | 122.8773 | 61.385 | 61.4526 | 122.966 | 61.4442 | 122.7488 | 61.4934 | 61.5019 | 61.4247 | 61.4332
549.8906 | 123.2391 | -61.4136 | 61.5921 | 0.021127 | -0.040521 | -0.002842 | 0.002454 | 0.022531 | 0.012329 | 0.028846 | 61.5142 | 0.16622 | 61.45 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.4347 | 61.3731 | 61.4107 | 61.416 | 61.4361 | 61.4259 | 61.4424 | 122.9278 | 61.5798 | 122.8636 | 61.3576 | 61.4252 | 122.9385 | 61.4213 | 122.7259 | 61.5026 | 61.5065 | 61.4384 | 61.4423
550.8906 | 123.1705 | -61.4319 | 61.5921 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.5142 | 0.16622 | 61.45 | -0.060575 | 0.016188 | 61.5158 | 0.012299 | 61.3077 | 61.4576 | 61.3914 | 61.4199 | 61.4343 | 61.4544 | 61.4442 | 61.4562 | 122.9461 | 61.5981 | 122.8819 | 61.3713 | 61.4481 | 122.9477 | 61.4442 | 122.7396 | 61.498 | 61.5019 | 61.4339 | 61.4377
551.8906 | 123.2574 | -61.4182 | 61.6104 | 0.025705 | -0.049678 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.038003 | 61.5096 | 0.17079 | 61.4455 | -0.060575 | 0.01161 | 61.5295 | 0.007721 | 61.3215 | 61.4439 | 61.3685 | 61.4016 | 61.4206 | 61.4453 | 61.4259 | 61.4562 | 122.9278 | 61.5889 | 122.8636 | 61.3576 | 61.4298 | 122.9477 | 61.4259 | 122.7396 | 61.498 | 61.5019 | 61.4339 | 61.4377
552.8906 | 123.1934 | -61.4365 | 61.5829 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.028846 | 61.5096 | 0.16622 | 61.45 | -0.051417 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.4622 | 61.3959 | 61.4199 | 61.4343 | 61.4681 | 61.4488 | 61.4653 | 122.9461 | 61.6027 | 122.8865 | 61.385 | 61.4481 | 122.9614 | 61.4442 | 122.7488 | 61.498 | 61.5019 | 61.4384 | 61.4423
553.8906 | 123.1934 | -61.4182 | 61.5967 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.00775 | 0.024268 | 61.5142 | 0.16622 | 61.4409 | -0.046838 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4439 | 61.3776 | 61.4016 | 61.4206 | 61.4407 | 61.4259 | 61.4424 | 122.9324 | 61.5844 | 122.859 | 61.3713 | 61.4343 | 122.9431 | 61.4259 | 122.7259 | 61.498 | 61.5065 | 61.4247 | 61.4332
554.8906 | 123.1796 | -61.4548 | 61.5875 | 0.034862 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.028846 | 61.5096 | 0.16622 | 61.4455 | -0.046838 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4896 | 61.4188 | 61.4474 | 61.4618 | 61.491 | 61.4671 | 61.4836 | 122.9644 | 61.621 | 122.9002 | 61.4079 | 61.471 | 122.9752 | 61.4625 | 122.7625 | 61.4934 | 61.5019 | 61.4293 | 61.4377
555.8906 | 123.1384 | -61.4502 | 61.5921 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.5188 | 0.16622 | 61.4455 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3077 | 61.4713 | 61.4143 | 61.4382 | 61.4481 | 61.4819 | 61.4579 | 61.479 | 122.969 | 61.6164 | 122.8957 | 61.3942 | 61.4664 | 122.9752 | 61.4533 | 122.7579 | 61.5026 | 61.5156 | 61.4293 | 61.4423
556.8906 | 123.1613 | -61.4594 | 61.5875 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.505 | 0.16164 | 61.4455 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4851 | 61.4188 | 61.4428 | 61.4618 | 61.4865 | 61.4717 | 61.4836 | 122.9644 | 61.621 | 122.9048 | 61.4034 | 61.4755 | 122.9843 | 61.4671 | 122.7717 | 61.4889 | 61.4973 | 61.4293 | 61.4377
557.8906 | 123.1796 | -61.4548 | 61.5829 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.033424 | 61.5096 | 0.17079 | 61.4455 | -0.051417 | 0.01161 | 61.5204 | 0.012299 | 61.3031 | 61.4805 | 61.4097 | 61.4428 | 61.4618 | 61.491 | 61.4625 | 61.4882 | 122.9644 | 61.6256 | 122.9002 | 61.4034 | 61.4664 | 122.9752 | 61.4671 | 122.7579 | 61.498 | 61.4973 | 61.4339 | 61.4332
558.8906 | 123.1384 | -61.4685 | 61.5555 | 0.025705 | -0.040521 | -0.007421 | -0.006703 | 0.031687 | 0.012329 | 0.033424 | 61.5096 | 0.17537 | 61.45 | -0.051417 | 0.007032 | 61.5341 | 0.012299 | 61.3123 | 61.4942 | 61.428 | 61.4611 | 61.4618 | 61.5002 | 61.4808 | 61.5019 | 122.9781 | 61.6439 | 122.9185 | 61.4171 | 61.4755 | 123.0026 | 61.4808 | 122.7808 | 61.5026 | 61.4973 | 61.443 | 61.4377
559.8906 | 123.143 | -61.4502 | 61.5784 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.033424 | 61.5096 | 0.17079 | 61.4409 | -0.051417 | 0.01161 | 61.5204 | 0.003143 | 61.3077 | 61.4713 | 61.4051 | 61.4382 | 61.4526 | 61.4819 | 61.4671 | 61.4836 | 122.9598 | 61.621 | 122.8911 | 61.3988 | 61.4618 | 122.9706 | 61.4533 | 122.7579 | 61.498 | 61.5065 | 61.4293 | 61.4377
560.8906 | 123.2574 | -61.4594 | 61.5555 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5142 | 0.17079 | 61.4455 | -0.046838 | 0.016188 | 61.5204 | 0.003143 | 61.3077 | 61.4805 | 61.4188 | 61.4474 | 61.4618 | 61.4865 | 61.4717 | 61.4836 | 122.9736 | 61.6301 | 122.9048 | 61.4125 | 61.4755 | 122.9797 | 61.4625 | 122.7671 | 61.498 | 61.5111 | 61.4293 | 61.4423
561.8906 | 123.1888 | -61.4594 | 61.5646 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.00775 | 0.028846 | 61.5142 | 0.17079 | 61.4363 | -0.065154 | 0.016188 | 61.5295 | 0.007721 | 61.3123 | 61.4759 | 61.4188 | 61.4519 | 61.4618 | 61.491 | 61.4671 | 61.4882 | 122.9736 | 61.6301 | 122.8957 | 61.3942 | 61.4755 | 122.9889 | 61.4671 | 122.7717 | 61.498 | 61.5065 | 61.4201 | 61.4286
562.8906 | 123.3215 | -61.4365 | 61.5234 | 0.030283 | -0.035942 | -0.012 | -0.002124 | 0.031687 | 0.012329 | 0.028846 | 61.5096 | 0.17079 | 61.45 | -0.065154 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4667 | 61.4005 | 61.4245 | 61.4343 | 61.4681 | 61.4488 | 61.4653 | 122.9461 | 61.6073 | 122.8865 | 61.3713 | 61.4526 | 122.966 | 61.4442 | 122.7442 | 61.4934 | 61.5019 | 61.4339 | 61.4423
563.8906 | 123.2849 | -61.4456 | 61.5555 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.5096 | 0.16622 | 61.4409 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4667 | 61.4005 | 61.429 | 61.4435 | 61.4727 | 61.4579 | 61.4699 | 122.9552 | 61.6118 | 122.8865 | 61.385 | 61.4618 | 122.9706 | 61.4533 | 122.7579 | 61.4934 | 61.5019 | 61.4247 | 61.4332
564.8906 | 123.2758 | -61.409 | 61.5143 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.505 | 0.17079 | 61.4455 | -0.060575 | 0.01161 | 61.525 | 0.012299 | 61.3031 | 61.4301 | 61.3685 | 61.4016 | 61.4115 | 61.4361 | 61.4213 | 61.4333 | 122.914 | 61.5798 | 122.8545 | 61.3484 | 61.4206 | 122.934 | 61.4213 | 122.7121 | 61.4934 | 61.4928 | 61.4339 | 61.4332
565.8906 | 123.3261 | -61.4456 | 61.5326 | 0.025705 | -0.049678 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5142 | 0.17079 | 61.45 | -0.060575 | 0.016188 | 61.5295 | 0.003143 | 61.3077 | 61.4713 | 61.3959 | 61.429 | 61.4481 | 61.4727 | 61.4579 | 61.4745 | 122.9598 | 61.6164 | 122.8957 | 61.385 | 61.4618 | 122.9752 | 61.4488 | 122.7533 | 61.498 | 61.5111 | 61.4339 | 61.4469
566.8906 | 123.2391 | -61.4136 | 61.5143 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.022531 | 0.012329 | 0.024268 | 61.505 | 0.17995 | 61.4409 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.2986 | 61.4393 | 61.3731 | 61.4016 | 61.4114 | 61.4361 | 61.4259 | 61.4378 | 122.9186 | 61.5935 | 122.8545 | 61.3576 | 61.4343 | 122.9431 | 61.4213 | 122.7121 | 61.4843 | 61.4973 | 61.4201 | 61.4332
567.8906 | 123.2666 | -61.4273 | 61.5417 | 0.025705 | -0.0451 | -0.012 | -0.006703 | 0.031687 | 0.012329 | 0.033424 | 61.5142 | 0.17079 | 61.4455 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.453 | 61.3822 | 61.4153 | 61.4206 | 61.459 | 61.4396 | 61.4607 | 122.9415 | 61.5981 | 122.8728 | 61.3713 | 61.4435 | 122.9568 | 61.435 | 122.7305 | 61.498 | 61.5065 | 61.4293 | 61.4377
568.8906 | 123.2574 | -61.4136 | 61.5372 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.022531 | 0.012329 | 0.01969 | 61.5188 | 0.17079 | 61.45 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3031 | 61.4347 | 61.3685 | 61.4016 | 61.416 | 61.4361 | 61.4259 | 61.4333 | 122.9324 | 61.5844 | 122.8636 | 61.3622 | 61.4298 | 122.9385 | 61.4213 | 122.7167 | 61.5026 | 61.5111 | 61.4339 | 61.4423
569.8906 | 123.23 | -61.4319 | 61.5143 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.5096 | 0.17079 | 61.45 | -0.055996 | 0.01161 | 61.5295 | 0.016878 | 61.3077 | 61.4576 | 61.3914 | 61.4153 | 61.4343 | 61.459 | 61.4396 | 61.4562 | 122.9415 | 61.6027 | 122.8819 | 61.3759 | 61.4435 | 122.9614 | 61.4488 | 122.7396 | 61.498 | 61.4928 | 61.4384 | 61.4332
570.8906 | 123.2712 | -61.4502 | 61.5463 | 0.025705 | -0.035942 | -0.021157 | -0.002124 | 0.022531 | 0.00775 | 0.024268 | 61.5142 | 0.16622 | 61.45 | -0.055996 | 0.01161 | 61.5295 | 0.007721 | 61.2986 | 61.4759 | 61.4143 | 61.429 | 61.4481 | 61.4727 | 61.4579 | 61.4745 | 122.9644 | 61.6164 | 122.9002 | 61.3942 | 61.4618 | 122.9797 | 61.4579 | 122.7488 | 61.5026 | 61.5065 | 61.4384 | 61.4423
571.8906 | 123.23 | -61.4227 | 61.5509 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5142 | 0.17079 | 61.4409 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3031 | 61.4393 | 61.3822 | 61.4107 | 61.4252 | 61.4498 | 61.4259 | 61.447 | 122.9369 | 61.5935 | 122.8636 | 61.3667 | 61.4389 | 122.9477 | 61.4304 | 122.7259 | 61.498 | 61.5065 | 61.4247 | 61.4332
572.8906 | 123.2346 | -61.4319 | 61.5509 | 0.016548 | -0.049678 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.01969 | 61.5096 | 0.17537 | 61.45 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4484 | 61.3822 | 61.4153 | 61.4298 | 61.4636 | 61.4442 | 61.4516 | 122.9415 | 61.6073 | 122.8819 | 61.3759 | 61.4481 | 122.9568 | 61.4396 | 122.7442 | 61.4934 | 61.5019 | 61.4339 | 61.4423
573.8906 | 123.2803 | -61.4227 | 61.5417 | 0.021127 | -0.0451 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.5142 | 0.17079 | 61.4409 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3077 | 61.4439 | 61.3776 | 61.4016 | 61.4206 | 61.4498 | 61.4351 | 61.447 | 122.9369 | 61.5935 | 122.8636 | 61.3667 | 61.4389 | 122.9477 | 61.4259 | 122.7305 | 61.498 | 61.5111 | 61.4247 | 61.4377
574.8906 | 123.2849 | -61.4182 | 61.5372 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.022531 | 0.012329 | 0.028846 | 61.5142 | 0.17079 | 61.45 | -0.060575 | 0.016188 | 61.525 | 0.012299 | 61.3169 | 61.4393 | 61.3822 | 61.4016 | 61.416 | 61.4407 | 61.4305 | 61.447 | 122.9324 | 61.5889 | 122.8682 | 61.3576 | 61.4343 | 122.9431 | 61.4305 | 122.735 | 61.498 | 61.5019 | 61.4339 | 61.4377
575.8906 | 123.317 | -61.4273 | 61.5555 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.505 | 0.17537 | 61.4455 | -0.060575 | 0.016188 | 61.5204 | 0.003143 | 61.3123 | 61.4484 | 61.3822 | 61.4153 | 61.4298 | 61.459 | 61.4396 | 61.4516 | 122.9324 | 61.6027 | 122.8728 | 61.3667 | 61.4435 | 122.9477 | 61.4305 | 122.7396 | 61.4889 | 61.5019 | 61.4293 | 61.4423
576.8906 | 123.2254 | -61.4273 | 61.6013 | 0.025705 | -0.040521 | -0.012 | -0.006703 | 0.027109 | 0.00775 | 0.028846 | 61.5142 | 0.17537 | 61.4409 | -0.060575 | 0.016188 | 61.5158 | 0.003143 | 61.3169 | 61.453 | 61.3868 | 61.4153 | 61.4206 | 61.4544 | 61.4351 | 61.4562 | 122.9415 | 61.6027 | 122.8682 | 61.3667 | 61.4435 | 122.9431 | 61.4305 | 122.7442 | 61.498 | 61.5111 | 61.4247 | 61.4377
577.8906 | 123.2849 | -61.3953 | 61.5829 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.5096 | 0.17079 | 61.4455 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3169 | 61.421 | 61.3547 | 61.3787 | 61.3931 | 61.427 | 61.403 | 61.4241 | 122.9049 | 61.5661 | 122.8407 | 61.3393 | 61.4069 | 122.9202 | 61.4076 | 122.7121 | 61.498 | 61.4973 | 61.4339 | 61.4332
578.8906 | 123.2986 | -61.4136 | 61.5875 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.01969 | 61.5142 | 0.16164 | 61.4409 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3077 | 61.4347 | 61.3731 | 61.397 | 61.416 | 61.4407 | 61.4259 | 61.4333 | 122.9278 | 61.5752 | 122.8545 | 61.3576 | 61.4298 | 122.9477 | 61.4213 | 122.7213 | 61.498 | 61.5065 | 61.4247 | 61.4332
579.8906 | 123.2529 | -61.4456 | 61.5784 | 0.025705 | -0.0451 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.028846 | 61.5188 | 0.17079 | 61.4455 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4713 | 61.4005 | 61.429 | 61.4527 | 61.4727 | 61.4534 | 61.4745 | 122.9644 | 61.6164 | 122.8911 | 61.3942 | 61.4618 | 122.9706 | 61.4533 | 122.7533 | 61.5026 | 61.5111 | 61.4293 | 61.4377
580.8906 | 123.2483 | -61.4227 | 61.5646 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.022531 | 0.016907 | 0.028846 | 61.5096 | 0.17079 | 61.4455 | -0.051417 | 0.01161 | 61.525 | 0.003143 | 61.3169 | 61.4393 | 61.3776 | 61.4107 | 61.4206 | 61.4453 | 61.4396 | 61.4516 | 122.9324 | 61.5935 | 122.8682 | 61.3713 | 61.4343 | 122.9477 | 61.4259 | 122.7396 | 61.498 | 61.5065 | 61.4339 | 61.4423
581.8906 | 123.2071 | -61.4273 | 61.6058 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.024268 | 61.5142 | 0.16622 | 61.45 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3169 | 61.453 | 61.3868 | 61.4107 | 61.4252 | 61.4544 | 61.4351 | 61.4516 | 122.9415 | 61.5935 | 122.8773 | 61.3713 | 61.4435 | 122.9614 | 61.435 | 122.7442 | 61.498 | 61.5065 | 61.4339 | 61.4423
582.8906 | 123.1522 | -61.4365 | 61.6241 | 0.021127 | -0.035942 | -0.021157 | -0.002124 | 0.027109 | 0.012329 | 0.038003 | 61.5096 | 0.17995 | 61.4455 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3169 | 61.4576 | 61.4005 | 61.4153 | 61.4343 | 61.4636 | 61.4488 | 61.4745 | 122.9461 | 61.6164 | 122.8819 | 61.385 | 61.4572 | 122.9614 | 61.4442 | 122.7533 | 61.4889 | 61.5019 | 61.4247 | 61.4377
583.8906 | 123.1979 | -61.441 | 61.6058 | 0.021127 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5234 | 0.17537 | 61.45 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3169 | 61.4622 | 61.3959 | 61.4245 | 61.4435 | 61.4681 | 61.4534 | 61.4699 | 122.9644 | 61.6164 | 122.8911 | 61.3896 | 61.4618 | 122.966 | 61.4488 | 122.7579 | 61.5026 | 61.5156 | 61.4293 | 61.4423
584.8906 | 123.2025 | -61.4639 | 61.5967 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.033424 | 61.5234 | 0.17995 | 61.4455 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3123 | 61.4851 | 61.4234 | 61.4519 | 61.4664 | 61.5002 | 61.4763 | 61.4974 | 122.9873 | 61.6439 | 122.9094 | 61.4079 | 61.4755 | 122.9889 | 61.4716 | 122.7762 | 61.5118 | 61.5156 | 61.4339 | 61.4377
585.8906 | 123.2346 | -61.4136 | 61.6104 | 0.025705 | -0.031363 | -0.012 | -0.002124 | 0.036265 | 0.012329 | 0.028846 | 61.5142 | 0.17537 | 61.4546 | -0.042259 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4393 | 61.3822 | 61.4016 | 61.4114 | 61.4498 | 61.4259 | 61.4424 | 122.9278 | 61.5889 | 122.8682 | 61.3713 | 61.4298 | 122.9385 | 61.4213 | 122.7259 | 61.498 | 61.5065 | 61.4384 | 61.4469
586.8906 | 123.23 | -61.4227 | 61.6058 | 0.025705 | -0.0451 | -0.007421 | 0.002454 | 0.022531 | 0.012329 | 0.033424 | 61.5188 | 0.17079 | 61.45 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3169 | 61.4484 | 61.3776 | 61.4153 | 61.4252 | 61.4453 | 61.4351 | 61.4562 | 122.9415 | 61.5935 | 122.8728 | 61.3622 | 61.4389 | 122.9477 | 61.4304 | 122.7396 | 61.5026 | 61.5111 | 61.4339 | 61.4423
587.8906 | 123.2025 | -61.4273 | 61.6196 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5188 | 0.17537 | 61.4409 | -0.046838 | 0.016188 | 61.5295 | 0.003143 | 61.3169 | 61.453 | 61.3868 | 61.4153 | 61.4298 | 61.4544 | 61.4396 | 61.4607 | 122.9461 | 61.6027 | 122.8682 | 61.3805 | 61.4435 | 122.9568 | 61.4305 | 122.7442 | 61.5026 | 61.5156 | 61.4247 | 61.4377
588.8906 | 123.2162 | -61.4182 | 61.5738 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5188 | 0.17079 | 61.4546 | -0.042259 | 0.020767 | 61.5295 | 0.012299 | 61.3215 | 61.4439 | 61.3776 | 61.4062 | 61.4206 | 61.4453 | 61.4213 | 61.4516 | 122.9369 | 61.5889 | 122.8728 | 61.3759 | 61.4389 | 122.9477 | 61.4305 | 122.7396 | 61.498 | 61.5065 | 61.4339 | 61.4423
589.8906 | 123.2071 | -61.4273 | 61.5784 | 0.025705 | -0.031363 | -0.012 | -0.006703 | 0.031687 | 0.012329 | 0.028846 | 61.5234 | 0.17995 | 61.45 | -0.060575 | 0.01161 | 61.525 | 0.012299 | 61.3123 | 61.453 | 61.3959 | 61.4153 | 61.4206 | 61.459 | 61.4396 | 61.4562 | 122.9507 | 61.6073 | 122.8773 | 61.3667 | 61.4389 | 122.9523 | 61.4396 | 122.7396 | 61.5118 | 61.5111 | 61.4384 | 61.4377
590.8906 | 123.1567 | -61.4456 | 61.5967 | 0.034862 | -0.0451 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5234 | 0.16622 | 61.4546 | -0.055996 | 0.020767 | 61.525 | 0.007721 | 61.3169 | 61.4805 | 61.4005 | 61.429 | 61.4481 | 61.4773 | 61.4579 | 61.4745 | 122.969 | 61.6118 | 122.9002 | 61.3896 | 61.4664 | 122.9706 | 61.4533 | 122.7625 | 61.5026 | 61.5156 | 61.4339 | 61.4469
591.8906 | 123.175 | -61.4365 | 61.5784 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5188 | 0.17079 | 61.4546 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3169 | 61.4622 | 61.4005 | 61.4199 | 61.4389 | 61.4636 | 61.4442 | 61.4653 | 122.9552 | 61.6073 | 122.8911 | 61.3805 | 61.4572 | 122.966 | 61.4442 | 122.7533 | 61.498 | 61.5111 | 61.4339 | 61.4469
592.8906 | 123.0698 | -61.4731 | 61.5601 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5142 | 0.17079 | 61.45 | -0.051417 | 0.01161 | 61.5295 | 0.007721 | 61.3077 | 61.4988 | 61.4371 | 61.4565 | 61.4755 | 61.5002 | 61.4854 | 61.5019 | 122.9873 | 61.6439 | 122.9231 | 61.4217 | 61.4847 | 123.0026 | 61.4808 | 122.7808 | 61.5026 | 61.5065 | 61.4384 | 61.4423
593.8906 | 123.1522 | -61.4731 | 61.5921 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.012329 | 0.024268 | 61.5142 | 0.17537 | 61.4455 | -0.046838 | 0.01161 | 61.5204 | -0.001436 | 61.3123 | 61.4988 | 61.4326 | 61.4565 | 61.4755 | 61.5093 | 61.4854 | 61.4974 | 122.9873 | 61.6485 | 122.9185 | 61.4262 | 61.4847 | 122.9935 | 61.4716 | 122.7854 | 61.5026 | 61.5156 | 61.4339 | 61.4469
594.8906 | 123.1979 | -61.4502 | 61.5875 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5188 | 0.16622 | 61.4455 | -0.051417 | 0.01161 | 61.525 | 0.007721 | 61.3031 | 61.4759 | 61.4097 | 61.4428 | 61.4526 | 61.4773 | 61.4625 | 61.4836 | 122.969 | 61.6164 | 122.8957 | 61.3988 | 61.4618 | 122.9752 | 61.4579 | 122.7533 | 61.5072 | 61.5111 | 61.4339 | 61.4377
595.8906 | 123.1567 | -61.4548 | 61.5738 | 0.030283 | -0.031363 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5096 | 0.17537 | 61.4455 | -0.046838 | 0.01161 | 61.5295 | 0.003143 | 61.3123 | 61.4851 | 61.4234 | 61.4428 | 61.4572 | 61.4819 | 61.4671 | 61.4836 | 122.9644 | 61.6301 | 122.9002 | 61.4079 | 61.4664 | 122.9843 | 61.4579 | 122.7671 | 61.498 | 61.5065 | 61.4339 | 61.4423
596.8906 | 123.1888 | -61.4685 | 61.5875 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.016907 | 0.028846 | 61.5142 | 0.16622 | 61.4455 | -0.051417 | 0.016188 | 61.525 | 0.012299 | 61.3077 | 61.4896 | 61.428 | 61.4519 | 61.471 | 61.5002 | 61.4854 | 61.4974 | 122.9827 | 61.6347 | 122.914 | 61.4171 | 61.4847 | 122.9935 | 61.4808 | 122.7762 | 61.498 | 61.5019 | 61.4293 | 61.4332
597.8906 | 123.2025 | -61.4594 | 61.6013 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | 0.012329 | 0.024268 | 61.5096 | 0.17537 | 61.45 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4896 | 61.4234 | 61.4428 | 61.4664 | 61.4956 | 61.4717 | 61.4836 | 122.969 | 61.6347 | 122.9094 | 61.4034 | 61.4755 | 122.9843 | 61.4625 | 122.7717 | 61.4934 | 61.5065 | 61.4339 | 61.4469
598.8906 | 123.1888 | -61.4594 | 61.5601 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5188 | 0.16164 | 61.45 | -0.055996 | 0.016188 | 61.5295 | 0.003143 | 61.3031 | 61.4896 | 61.4143 | 61.4428 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 122.9781 | 61.621 | 122.9094 | 61.4034 | 61.4755 | 122.9889 | 61.4625 | 122.7625 | 61.5026 | 61.5156 | 61.4339 | 61.4469
599.8906 | 123.1613 | -61.4548 | 61.5646 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.016907 | 0.028846 | 61.5234 | 0.17079 | 61.4455 | -0.046838 | 0.01161 | 61.525 | 0.012299 | 61.3031 | 61.4759 | 61.4097 | 61.4428 | 61.4526 | 61.4865 | 61.4717 | 61.4836 | 122.9781 | 61.6256 | 122.9002 | 61.4079 | 61.4664 | 122.9797 | 61.4671 | 122.7579 | 61.5118 | 61.5111 | 61.4339 | 61.4332
600.8906 | 123.1888 | -61.4777 | 61.5417 | 0.030283 | -0.035942 | -0.021157 | 0.007033 | 0.031687 | 0.00775 | 0.024268 | 61.5188 | 0.17079 | 61.4455 | -0.060575 | 0.016188 | 61.5295 | 0.007721 | 61.2986 | 61.5079 | 61.4417 | 61.4565 | 61.4847 | 61.5093 | 61.4854 | 61.5019 | 122.9964 | 61.6485 | 122.9231 | 61.4171 | 61.4938 | 123.0072 | 61.4854 | 122.7762 | 61.5026 | 61.5111 | 61.4293 | 61.4377
601.8906 | 123.2071 | -61.4502 | 61.5784 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.024268 | 61.5142 | 0.17537 | 61.45 | -0.051417 | 0.016188 | 61.5295 | 0.003143 | 61.3077 | 61.4759 | 61.4051 | 61.4382 | 61.4572 | 61.4819 | 61.4579 | 61.4745 | 122.9644 | 61.6256 | 122.9002 | 61.3988 | 61.4664 | 122.9797 | 61.4533 | 122.7579 | 61.498 | 61.5111 | 61.4339 | 61.4469
602.8906 | 123.1842 | -61.4639 | 61.5646 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.028846 | 61.5096 | 0.17079 | 61.45 | -0.051417 | 0.020767 | 61.5204 | 0.003143 | 61.3077 | 61.4851 | 61.428 | 61.4474 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 122.9736 | 61.6347 | 122.914 | 61.4125 | 61.4847 | 122.9843 | 61.4671 | 122.7717 | 61.4889 | 61.5065 | 61.4293 | 61.4469
603.8906 | 123.3124 | -61.4227 | 61.5143 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.033424 | 61.5096 | 0.17537 | 61.4455 | -0.055996 | 0.01161 | 61.5204 | 0.003143 | 61.3031 | 61.4439 | 61.3822 | 61.4062 | 61.4252 | 61.4544 | 61.4305 | 61.4562 | 122.9324 | 61.5981 | 122.8682 | 61.3667 | 61.4343 | 122.9431 | 61.4259 | 122.7259 | 61.498 | 61.5065 | 61.4339 | 61.4423
604.8906 | 123.3078 | -61.4136 | 61.5555 | 0.021127 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.016907 | 0.028846 | 61.5096 | 0.17537 | 61.4455 | -0.060575 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.4347 | 61.3822 | 61.397 | 61.416 | 61.4498 | 61.4305 | 61.4424 | 122.9232 | 61.5889 | 122.859 | 61.353 | 61.4252 | 122.9385 | 61.4213 | 122.7213 | 61.498 | 61.5019 | 61.4339 | 61.4377
605.8906 | 123.3032 | -61.4319 | 61.5189 | 0.016548 | -0.040521 | -0.025735 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5188 | 0.17537 | 61.4409 | -0.055996 | 0.01161 | 61.5295 | 0.007721 | 61.3031 | 61.4484 | 61.3914 | 61.4062 | 61.4343 | 61.459 | 61.4442 | 61.4562 | 122.9507 | 61.6073 | 122.8728 | 61.3759 | 61.4435 | 122.9614 | 61.4396 | 122.735 | 61.5072 | 61.5111 | 61.4293 | 61.4332
606.8906 | 123.3032 | -61.4273 | 61.5143 | 0.021127 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.5188 | 0.17079 | 61.45 | -0.051417 | 0.007032 | 61.525 | 0.007721 | 61.3077 | 61.4484 | 61.3868 | 61.4199 | 61.4298 | 61.459 | 61.4351 | 61.4516 | 122.9461 | 61.5981 | 122.8773 | 61.3759 | 61.4343 | 122.9523 | 61.435 | 122.735 | 61.5118 | 61.5111 | 61.443 | 61.4423
607.8906 | 123.2758 | -61.4182 | 61.5509 | 0.025705 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.033424 | 61.5188 | 0.17537 | 61.45 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.2986 | 61.4439 | 61.3731 | 61.4016 | 61.4206 | 61.4453 | 61.4351 | 61.4516 | 122.9369 | 61.5935 | 122.8682 | 61.3667 | 61.4343 | 122.9477 | 61.4259 | 122.7167 | 61.5026 | 61.5111 | 61.4339 | 61.4423
608.8906 | 123.2208 | -61.4502 | 61.5326 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.028846 | 61.5188 | 0.16622 | 61.4455 | -0.055996 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.4759 | 61.4097 | 61.4382 | 61.4481 | 61.4773 | 61.4625 | 61.479 | 122.969 | 61.6164 | 122.8957 | 61.3942 | 61.4618 | 122.9752 | 61.4579 | 122.7579 | 61.5072 | 61.5111 | 61.4339 | 61.4377
609.8906 | 123.2666 | -61.441 | 61.5601 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.5142 | 0.17079 | 61.4409 | -0.051417 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4622 | 61.4005 | 61.429 | 61.4435 | 61.4681 | 61.4488 | 61.4653 | 122.9552 | 61.6118 | 122.8819 | 61.3896 | 61.4572 | 122.9614 | 61.4488 | 122.7488 | 61.498 | 61.5065 | 61.4247 | 61.4332
610.8906 | 123.2529 | -61.4365 | 61.5234 | 0.01197 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.012329 | 0.024268 | 61.5142 | 0.17079 | 61.4455 | -0.055996 | 0.01161 | 61.5295 | 0.003143 | 61.3123 | 61.4484 | 61.3959 | 61.4245 | 61.4343 | 61.4681 | 61.4488 | 61.4607 | 122.9507 | 61.6073 | 122.8819 | 61.3805 | 61.4481 | 122.966 | 61.4396 | 122.7488 | 61.5026 | 61.5111 | 61.4339 | 61.4423
611.8906 | 123.2803 | -61.4273 | 61.5234 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.033424 | 61.5188 | 0.17995 | 61.4455 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3123 | 61.453 | 61.3868 | 61.4107 | 61.4252 | 61.459 | 61.4396 | 61.4607 | 122.9461 | 61.6073 | 122.8728 | 61.3713 | 61.4389 | 122.9523 | 61.4396 | 122.7396 | 61.5072 | 61.5065 | 61.4339 | 61.4332
612.8906 | 123.262 | -61.4548 | 61.5234 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.033424 | 61.5142 | 0.17079 | 61.4546 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4759 | 61.4143 | 61.4428 | 61.4572 | 61.4773 | 61.4625 | 61.4882 | 122.969 | 61.6256 | 122.9094 | 61.4034 | 61.471 | 122.9797 | 61.4625 | 122.7625 | 61.498 | 61.5065 | 61.4384 | 61.4469
613.8906 | 123.2208 | -61.4456 | 61.5509 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5188 | 0.16622 | 61.4409 | -0.051417 | 0.016188 | 61.5204 | 0.012299 | 61.3031 | 61.4667 | 61.4051 | 61.429 | 61.4481 | 61.4773 | 61.4579 | 61.4745 | 122.9644 | 61.6118 | 122.8865 | 61.3942 | 61.4618 | 122.966 | 61.4579 | 122.7488 | 61.5026 | 61.5065 | 61.4247 | 61.4286
614.8906 | 123.2437 | -61.441 | 61.5189 | 0.016548 | -0.031363 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.01969 | 61.5142 | 0.17079 | 61.45 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4576 | 61.4097 | 61.429 | 61.4435 | 61.4727 | 61.4579 | 61.4607 | 122.9552 | 61.6118 | 122.8911 | 61.385 | 61.4572 | 122.9706 | 61.4488 | 122.7442 | 61.498 | 61.5065 | 61.4339 | 61.4423
615.8906 | 123.2986 | -61.4319 | 61.5189 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.012329 | 0.024268 | 61.5142 | 0.17537 | 61.4455 | -0.051417 | 0.01161 | 61.5295 | 0.003143 | 61.3123 | 61.453 | 61.3914 | 61.4199 | 61.4389 | 61.459 | 61.4442 | 61.4562 | 122.9461 | 61.6073 | 122.8773 | 61.3805 | 61.4435 | 122.9614 | 61.435 | 122.7442 | 61.5026 | 61.5111 | 61.4339 | 61.4423
616.8906 | 123.2391 | -61.4319 | 61.5326 | 0.030283 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.016907 | 0.024268 | 61.5142 | 0.17079 | 61.45 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4622 | 61.3959 | 61.4153 | 61.4389 | 61.4636 | 61.4488 | 61.4562 | 122.9461 | 61.6027 | 122.8819 | 61.3759 | 61.4481 | 122.9568 | 61.435 | 122.7442 | 61.498 | 61.5111 | 61.4339 | 61.4469
617.8906 | 123.2986 | -61.4227 | 61.5692 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | 0.012329 | 0.028846 | 61.5142 | 0.17537 | 61.45 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3077 | 61.4439 | 61.3868 | 61.4062 | 61.4298 | 61.4498 | 61.4351 | 61.4516 | 122.9369 | 61.5981 | 122.8728 | 61.3667 | 61.4343 | 122.9477 | 61.435 | 122.7305 | 61.5026 | 61.5019 | 61.4384 | 61.4377
618.8906 | 123.2895 | -61.4502 | 61.5509 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.5142 | 0.17537 | 61.4455 | -0.055996 | 0.016188 | 61.5295 | 0.012299 | 61.3077 | 61.4759 | 61.4097 | 61.4336 | 61.4526 | 61.4773 | 61.4534 | 61.479 | 122.9644 | 61.6256 | 122.8957 | 61.3942 | 61.4664 | 122.9797 | 61.4625 | 122.7579 | 61.498 | 61.5019 | 61.4293 | 61.4332
619.8906 | 123.2117 | -61.4182 | 61.5829 | 0.021127 | -0.040521 | -0.012 | -0.002124 | 0.036265 | 0.016907 | 0.028846 | 61.5096 | 0.16622 | 61.45 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3077 | 61.4393 | 61.3776 | 61.4062 | 61.416 | 61.4544 | 61.4351 | 61.447 | 122.9278 | 61.5844 | 122.8682 | 61.3667 | 61.4343 | 122.9477 | 61.4305 | 122.7259 | 61.4934 | 61.4973 | 61.4339 | 61.4377
620.8906 | 123.3398 | -61.3953 | 61.5555 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5188 | 0.16164 | 61.4455 | -0.051417 | 0.01161 | 61.5295 | 0.003143 | 61.3169 | 61.421 | 61.3593 | 61.3833 | 61.3977 | 61.427 | 61.4076 | 61.4241 | 122.9141 | 61.5569 | 122.8407 | 61.3438 | 61.4069 | 122.9248 | 61.3984 | 122.7121 | 61.5072 | 61.5156 | 61.4339 | 61.4423
621.8906 | 123.2803 | -61.4044 | 61.5555 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.028846 | 61.5188 | 0.17537 | 61.4546 | -0.060575 | 0.016188 | 61.5341 | 0.012299 | 61.3077 | 61.4255 | 61.3593 | 61.3924 | 61.4069 | 61.4361 | 61.4213 | 61.4333 | 122.9232 | 61.5798 | 122.859 | 61.3438 | 61.4206 | 122.9385 | 61.4167 | 122.7121 | 61.5026 | 61.5065 | 61.4384 | 61.4423
622.8906 | 123.2391 | -61.4456 | 61.5601 | 0.025705 | -0.031363 | -0.021157 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.5142 | 0.17537 | 61.4546 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4713 | 61.4143 | 61.4245 | 61.4481 | 61.4727 | 61.4534 | 61.4699 | 122.9598 | 61.621 | 122.9002 | 61.3942 | 61.4618 | 122.9706 | 61.4533 | 122.7579 | 61.498 | 61.5065 | 61.4384 | 61.4469
623.8906 | 123.3032 | -61.4227 | 61.5509 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5234 | 0.17537 | 61.45 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4484 | 61.3868 | 61.4062 | 61.4252 | 61.4498 | 61.4351 | 61.4516 | 122.9461 | 61.5981 | 122.8728 | 61.3622 | 61.4389 | 122.9477 | 61.4304 | 122.7305 | 61.5072 | 61.5156 | 61.4339 | 61.4423
624.8906 | 123.2254 | -61.441 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.038003 | 61.5188 | 0.17537 | 61.45 | -0.051417 | 0.016188 | 61.5341 | 0.012299 | 61.3031 | 61.4667 | 61.4005 | 61.4245 | 61.4435 | 61.4727 | 61.4534 | 61.479 | 122.9598 | 61.6164 | 122.8911 | 61.3896 | 61.4572 | 122.9752 | 61.4533 | 122.7442 | 61.5026 | 61.5065 | 61.4339 | 61.4377
625.8906 | 123.2529 | -61.4273 | 61.5417 | 0.016548 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.024268 | 61.5188 | 0.18453 | 61.4455 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3123 | 61.4439 | 61.3914 | 61.4107 | 61.4298 | 61.4544 | 61.4351 | 61.4516 | 122.9461 | 61.6118 | 122.8728 | 61.3713 | 61.4435 | 122.9614 | 61.435 | 122.7396 | 61.5026 | 61.5111 | 61.4293 | 61.4377
626.8906 | 123.3215 | -61.441 | 61.5601 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.012329 | 0.024268 | 61.5142 | 0.17537 | 61.4455 | -0.051417 | 0.01161 | 61.525 | 0.003143 | 61.3169 | 61.4713 | 61.4051 | 61.4245 | 61.4435 | 61.4773 | 61.4534 | 61.4653 | 122.9552 | 61.6164 | 122.8865 | 61.3896 | 61.4526 | 122.966 | 61.4442 | 122.7579 | 61.5026 | 61.5111 | 61.4339 | 61.4423
627.8906 | 123.3307 | -61.409 | 61.5829 | 0.016548 | -0.0451 | -0.007421 | 0.002454 | 0.031687 | 0.003172 | 0.01969 | 61.5234 | 0.17537 | 61.4455 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4255 | 61.3639 | 61.4016 | 61.4115 | 61.4407 | 61.4122 | 61.4287 | 122.9324 | 61.5844 | 122.8545 | 61.3576 | 61.4252 | 122.9385 | 61.4213 | 122.7213 | 61.5072 | 61.5111 | 61.4293 | 61.4332
628.8906 | 123.2986 | -61.3998 | 61.5875 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.01969 | 61.5142 | 0.17537 | 61.4546 | -0.055996 | 0.007032 | 61.5341 | 0.007721 | 61.3215 | 61.4255 | 61.3593 | 61.3833 | 61.4023 | 61.427 | 61.4122 | 61.4195 | 122.914 | 61.5752 | 122.8545 | 61.3438 | 61.4069 | 122.934 | 61.4076 | 122.7213 | 61.5072 | 61.5065 | 61.4476 | 61.4469
629.8906 | 123.175 | -61.4731 | 61.5784 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.024268 | 61.5188 | 0.17995 | 61.4546 | -0.051417 | 0.01161 | 61.5295 | 0.016878 | 61.3077 | 61.4942 | 61.4371 | 61.4611 | 61.4801 | 61.5048 | 61.4854 | 61.4974 | 122.9919 | 61.653 | 122.9277 | 61.4217 | 61.4847 | 123.0026 | 61.49 | 122.7808 | 61.5072 | 61.5019 | 61.443 | 61.4377
630.8906 | 123.2712 | -61.4227 | 61.5829 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.024268 | 61.5188 | 0.17537 | 61.4455 | -0.055996 | 0.025345 | 61.5295 | 0.007721 | 61.3077 | 61.4393 | 61.3776 | 61.4107 | 61.4252 | 61.459 | 61.4351 | 61.447 | 122.9415 | 61.5981 | 122.8682 | 61.3667 | 61.4481 | 122.9523 | 61.4304 | 122.7305 | 61.4934 | 61.5111 | 61.4201 | 61.4377
631.8906 | 123.2254 | -61.4227 | 61.6104 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.022531 | 0.003172 | 0.038003 | 61.5142 | 0.17537 | 61.45 | -0.051417 | 0.016188 | 61.5295 | 0.016878 | 61.3077 | 61.4484 | 61.3776 | 61.4107 | 61.4252 | 61.4453 | 61.4259 | 61.4607 | 122.9369 | 61.5981 | 122.8728 | 61.3713 | 61.4389 | 122.9523 | 61.4396 | 122.7305 | 61.498 | 61.4973 | 61.4339 | 61.4332
632.8906 | 123.2117 | -61.4273 | 61.6241 | 0.025705 | -0.0451 | -0.025735 | 0.002454 | 0.027109 | 0.016907 | 0.038003 | 61.5188 | 0.17079 | 61.45 | -0.046838 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.453 | 61.3822 | 61.4016 | 61.4298 | 61.4544 | 61.4442 | 61.4653 | 122.9461 | 61.5981 | 122.8773 | 61.3805 | 61.4435 | 122.9568 | 61.4396 | 122.7396 | 61.5026 | 61.5065 | 61.4339 | 61.4377
633.8906 | 123.143 | -61.4365 | 61.6196 | 0.025705 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.5142 | 0.17537 | 61.4455 | -0.051417 | 0.01161 | 61.5295 | 0.007721 | 61.3123 | 61.4622 | 61.3959 | 61.4199 | 61.4343 | 61.4681 | 61.4442 | 61.4653 | 122.9507 | 61.6118 | 122.8819 | 61.385 | 61.4481 | 122.966 | 61.4442 | 122.7488 | 61.5026 | 61.5065 | 61.4339 | 61.4377
634.8906 | 123.1659 | -61.4365 | 61.6379 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.5188 | 0.17537 | 61.4455 | -0.060575 | 0.016188 | 61.5204 | 0.007721 | 61.3123 | 61.4622 | 61.3959 | 61.4245 | 61.4389 | 61.4681 | 61.4442 | 61.4607 | 122.9552 | 61.6118 | 122.8819 | 61.3759 | 61.4526 | 122.9568 | 61.4442 | 122.7488 | 61.5026 | 61.5111 | 61.4293 | 61.4377
635.8906 | 123.2025 | -61.4319 | 61.6287 | 0.030283 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.016907 | 0.033424 | 61.5188 | 0.17079 | 61.4592 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4622 | 61.3868 | 61.4199 | 61.4343 | 61.4682 | 61.4488 | 61.4653 | 122.9507 | 61.6027 | 122.8911 | 61.3759 | 61.4481 | 122.9523 | 61.4396 | 122.7396 | 61.5026 | 61.5111 | 61.443 | 61.4515
636.8906 | 123.2529 | -61.4136 | 61.5967 | 0.025705 | -0.0451 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5234 | 0.17995 | 61.45 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.3169 | 61.4393 | 61.3685 | 61.4016 | 61.416 | 61.4407 | 61.4213 | 61.4424 | 122.9369 | 61.5935 | 122.8636 | 61.3576 | 61.4343 | 122.9385 | 61.4259 | 122.7305 | 61.5026 | 61.5111 | 61.4293 | 61.4377
637.8906 | 123.2025 | -61.4456 | 61.6196 | 0.021127 | -0.035942 | -0.021157 | 0.007033 | 0.031687 | 0.012329 | 0.024268 | 61.5142 | 0.17537 | 61.4546 | -0.055996 | 0.016188 | 61.525 | 0.012299 | 61.3031 | 61.4667 | 61.4097 | 61.4245 | 61.4527 | 61.4773 | 61.4579 | 61.4699 | 122.9598 | 61.621 | 122.9002 | 61.3896 | 61.4618 | 122.9706 | 61.4579 | 122.7488 | 61.498 | 61.5019 | 61.4384 | 61.4423
638.8906 | 123.1659 | -61.4502 | 61.615 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.016907 | 0.024268 | 61.5188 | 0.17995 | 61.45 | -0.060575 | 0.020767 | 61.5295 | 0.007721 | 61.3077 | 61.4759 | 61.4097 | 61.4382 | 61.4572 | 61.4773 | 61.4671 | 61.4745 | 122.969 | 61.6301 | 122.9002 | 61.3896 | 61.471 | 122.9797 | 61.4579 | 122.7579 | 61.498 | 61.5111 | 61.4293 | 61.4423
639.8906 | 123.1613 | -61.4502 | 61.6333 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.022531 | 0.016907 | 0.033424 | 61.5234 | 0.17537 | 61.4546 | -0.046838 | 0.01161 | 61.5341 | 0.012299 | 61.3123 | 61.4713 | 61.4143 | 61.4382 | 61.4526 | 61.4727 | 61.4671 | 61.4836 | 122.9736 | 61.6256 | 122.9048 | 61.4034 | 61.4618 | 122.9843 | 61.4625 | 122.7625 | 61.5118 | 61.5111 | 61.443 | 61.4423
640.8906 | 123.1842 | -61.4456 | 61.615 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.5188 | 0.17079 | 61.4546 | -0.051417 | 0.020767 | 61.5341 | 0.016878 | 61.3123 | 61.4713 | 61.4051 | 61.4336 | 61.4481 | 61.4773 | 61.4579 | 61.4699 | 122.9644 | 61.6164 | 122.9002 | 61.3942 | 61.4664 | 122.9797 | 61.4625 | 122.7579 | 61.498 | 61.5019 | 61.4339 | 61.4377
641.8906 | 123.143 | -61.4456 | 61.6104 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.012329 | 0.033424 | 61.5234 | 0.16622 | 61.4546 | -0.046838 | 0.020767 | 61.525 | 0.012299 | 61.3169 | 61.4667 | 61.4051 | 61.429 | 61.4435 | 61.4773 | 61.4579 | 61.479 | 122.969 | 61.6118 | 122.9002 | 61.3988 | 61.4664 | 122.9706 | 61.4579 | 122.7625 | 61.5026 | 61.5111 | 61.4339 | 61.4423
642.8906 | 123.1796 | -61.4548 | 61.615 | 0.021127 | -0.035942 | -0.012 | -0.002124 | 0.031687 | 0.003172 | 0.033424 | 61.5142 | 0.17079 | 61.45 | -0.051417 | 0.020767 | 61.5295 | 0.016878 | 61.3215 | 61.4759 | 61.4188 | 61.4428 | 61.4526 | 61.4865 | 61.4579 | 61.4882 | 122.969 | 61.6256 | 122.9048 | 61.4034 | 61.4755 | 122.9843 | 61.4717 | 122.7762 | 61.4934 | 61.4973 | 61.4293 | 61.4332
643.8906 | 123.1796 | -61.4639 | 61.6104 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.024268 | 61.5188 | 0.17995 | 61.45 | -0.051417 | 0.020767 | 61.5295 | 0.016878 | 61.3123 | 61.4805 | 61.4188 | 61.4519 | 61.4618 | 61.4956 | 61.4717 | 61.4882 | 122.9827 | 61.6439 | 122.914 | 61.4125 | 61.4847 | 122.9935 | 61.4808 | 122.7762 | 61.498 | 61.5019 | 61.4293 | 61.4332
644.8906 | 123.1888 | -61.441 | 61.5875 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5234 | 0.17079 | 61.45 | -0.055996 | 0.020767 | 61.525 | 0.007721 | 61.3123 | 61.4622 | 61.4051 | 61.429 | 61.4435 | 61.4727 | 61.4534 | 61.4699 | 122.9644 | 61.6118 | 122.8911 | 61.385 | 61.4618 | 122.966 | 61.4488 | 122.7533 | 61.5026 | 61.5156 | 61.4293 | 61.4423
645.8906 | 123.2162 | -61.4273 | 61.5692 | 0.025705 | -0.035942 | -0.016578 | -0.002124 | 0.036265 | 0.016907 | 0.01969 | 61.5142 | 0.16622 | 61.4546 | -0.055996 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.453 | 61.3914 | 61.4107 | 61.4252 | 61.4636 | 61.4442 | 61.447 | 122.9415 | 61.5935 | 122.8819 | 61.3713 | 61.4435 | 122.9568 | 61.4396 | 122.7396 | 61.498 | 61.5019 | 61.4384 | 61.4423
646.8906 | 123.23 | -61.441 | 61.5921 | 0.016548 | -0.031363 | -0.021157 | 0.007033 | 0.027109 | 0.012329 | 0.028846 | 61.5142 | 0.17079 | 61.4546 | -0.051417 | 0.016188 | 61.5387 | 0.012299 | 61.3169 | 61.4576 | 61.4097 | 61.4199 | 61.4481 | 61.4681 | 61.4534 | 61.4699 | 122.9552 | 61.6118 | 122.8957 | 61.3896 | 61.4572 | 122.9797 | 61.4533 | 122.7579 | 61.498 | 61.5019 | 61.4384 | 61.4423
647.8906 | 123.1888 | -61.4319 | 61.5738 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.033424 | 61.5234 | 0.17079 | 61.4592 | -0.060575 | 0.020767 | 61.525 | 0.007721 | 61.3123 | 61.4484 | 61.3959 | 61.4199 | 61.4389 | 61.4636 | 61.4442 | 61.4653 | 122.9552 | 61.6027 | 122.8911 | 61.3713 | 61.4527 | 122.9568 | 61.4396 | 122.7442 | 61.5026 | 61.5156 | 61.4384 | 61.4515
648.8906 | 123.1888 | -61.4548 | 61.6013 | 0.030283 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.028846 | 61.5142 | 0.17995 | 61.45 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3077 | 61.4851 | 61.4188 | 61.4382 | 61.4572 | 61.4819 | 61.4717 | 61.4836 | 122.969 | 61.6347 | 122.9048 | 61.4034 | 61.4755 | 122.9797 | 61.4625 | 122.7625 | 61.4934 | 61.5065 | 61.4293 | 61.4423
649.8906 | 123.111 | -61.4456 | 61.5463 | 0.021127 | -0.0451 | -0.012 | -0.002124 | 0.027109 | 0.016907 | 0.024268 | 61.5234 | 0.17079 | 61.4546 | -0.055996 | 0.01161 | 61.5341 | 0.012299 | 61.3123 | 61.4667 | 61.4005 | 61.4336 | 61.4435 | 61.4727 | 61.4625 | 61.4699 | 122.969 | 61.6164 | 122.9002 | 61.3896 | 61.4572 | 122.9797 | 61.4579 | 122.7579 | 61.5118 | 61.5111 | 61.443 | 61.4423
650.8906 | 123.2346 | -61.4502 | 61.5921 | 0.021127 | -0.031363 | -0.007421 | 0.011611 | 0.027109 | 0.016907 | 0.024268 | 61.5234 | 0.17995 | 61.4546 | -0.051417 | 0.020767 | 61.525 | 0.012299 | 61.3077 | 61.4713 | 61.4188 | 61.4428 | 61.4618 | 61.4773 | 61.4671 | 61.4745 | 122.9736 | 61.6301 | 122.9048 | 61.3988 | 61.471 | 122.9752 | 61.4625 | 122.7579 | 61.5026 | 61.5111 | 61.4339 | 61.4423
651.8906 | 123.2208 | -61.4502 | 61.5875 | 0.021127 | -0.035942 | -0.007421 | 0.007033 | 0.027109 | 0.00775 | 0.028846 | 61.5188 | 0.16622 | 61.4546 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4713 | 61.4143 | 61.4428 | 61.4572 | 61.4773 | 61.4579 | 61.479 | 122.969 | 61.6164 | 122.9048 | 61.3988 | 61.4664 | 122.9797 | 61.4625 | 122.7625 | 61.5026 | 61.5065 | 61.4384 | 61.4423
652.8906 | 123.1247 | -61.4456 | 61.5829 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.016907 | 0.028846 | 61.5188 | 0.17537 | 61.4546 | -0.060575 | 0.01161 | 61.525 | 0.016878 | 61.3077 | 61.4667 | 61.4051 | 61.4336 | 61.4527 | 61.4773 | 61.4625 | 61.4745 | 122.9644 | 61.621 | 122.9002 | 61.385 | 61.4572 | 122.9706 | 61.4625 | 122.7533 | 61.5072 | 61.5019 | 61.443 | 61.4377
653.8906 | 123.1796 | -61.4365 | 61.6058 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.012329 | 0.033424 | 61.5234 | 0.17079 | 61.45 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4576 | 61.4005 | 61.4199 | 61.4389 | 61.4727 | 61.4488 | 61.4699 | 122.9598 | 61.6073 | 122.8865 | 61.3805 | 61.4526 | 122.9614 | 61.4442 | 122.7488 | 61.5072 | 61.5156 | 61.4339 | 61.4423
654.8906 | 123.1934 | -61.4594 | 61.5784 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.00775 | 0.033424 | 61.5279 | 0.17537 | 61.4546 | -0.060575 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4805 | 61.4188 | 61.4474 | 61.4664 | 61.4865 | 61.4671 | 61.4928 | 122.9873 | 61.6347 | 122.914 | 61.3988 | 61.4755 | 122.9889 | 61.4716 | 122.7717 | 61.5118 | 61.5156 | 61.4384 | 61.4423
655.8906 | 123.143 | -61.4456 | 61.5738 | 0.025705 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5188 | 0.17079 | 61.4546 | -0.055996 | 0.016188 | 61.525 | 0.012299 | 61.3077 | 61.4713 | 61.4051 | 61.4382 | 61.4527 | 61.4819 | 61.4579 | 61.4836 | 122.9644 | 61.6164 | 122.9002 | 61.3896 | 61.4618 | 122.9706 | 61.4579 | 122.7533 | 61.5026 | 61.5065 | 61.4384 | 61.4423
656.8906 | 123.1842 | -61.4548 | 61.6013 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.021485 | 0.033424 | 61.5279 | 0.17995 | 61.4546 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3031 | 61.4759 | 61.4143 | 61.4382 | 61.4618 | 61.4865 | 61.4763 | 61.4882 | 122.9827 | 61.6347 | 122.9094 | 61.3988 | 61.471 | 122.9797 | 61.4579 | 122.7579 | 61.5118 | 61.5248 | 61.4384 | 61.4515
657.8906 | 123.1842 | -61.4365 | 61.5967 | 0.025705 | -0.031363 | -0.007421 | -0.002124 | 0.027109 | 0.016907 | 0.028846 | 61.5188 | 0.17537 | 61.45 | -0.051417 | 0.020767 | 61.5295 | 0.012299 | 61.3169 | 61.4622 | 61.4051 | 61.429 | 61.4343 | 61.4636 | 61.4534 | 61.4653 | 122.9552 | 61.6118 | 122.8865 | 61.385 | 61.4572 | 122.966 | 61.4488 | 122.7533 | 61.498 | 61.5065 | 61.4293 | 61.4377
658.8906 | 123.2071 | -61.4594 | 61.6058 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5234 | 0.17537 | 61.4592 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3169 | 61.4805 | 61.4188 | 61.4474 | 61.4618 | 61.4865 | 61.4717 | 61.4928 | 122.9827 | 61.6347 | 122.9185 | 61.3988 | 61.4755 | 122.9843 | 61.4671 | 122.7762 | 61.5072 | 61.5156 | 61.443 | 61.4515
659.8906 | 123.2208 | -61.4548 | 61.5601 | 0.021127 | -0.035942 | -0.007421 | 0.007033 | 0.031687 | 0.012329 | 0.038003 | 61.5188 | 0.17995 | 61.4455 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3169 | 61.4759 | 61.4188 | 61.4474 | 61.4618 | 61.4865 | 61.4671 | 61.4928 | 122.9736 | 61.6347 | 122.9002 | 61.3988 | 61.471 | 122.9889 | 61.4625 | 122.7717 | 61.5026 | 61.5111 | 61.4293 | 61.4377
660.8906 | 123.2437 | -61.4456 | 61.5463 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.022531 | 0.016907 | 0.028846 | 61.5188 | 0.17537 | 61.4546 | -0.051417 | 0.01161 | 61.525 | 0.003143 | 61.3123 | 61.4622 | 61.4051 | 61.4382 | 61.4481 | 61.4681 | 61.4625 | 61.4745 | 122.9644 | 61.621 | 122.9002 | 61.3942 | 61.4572 | 122.9706 | 61.4488 | 122.7579 | 61.5072 | 61.5156 | 61.443 | 61.4515
661.8906 | 123.2574 | -61.4182 | 61.5326 | 0.016548 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5142 | 0.17537 | 61.45 | -0.055996 | 0.016188 | 61.5204 | 0.007721 | 61.3077 | 61.4347 | 61.3731 | 61.4016 | 61.4206 | 61.4453 | 61.4305 | 61.4516 | 122.9324 | 61.5935 | 122.8682 | 61.3622 | 61.4343 | 122.9385 | 61.4259 | 122.7259 | 61.498 | 61.5065 | 61.4339 | 61.4423
662.8906 | 123.262 | -61.4548 | 61.5326 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.012329 | 0.024268 | 61.5142 | 0.17079 | 61.4546 | -0.055996 | 0.007032 | 61.525 | 0.007721 | 61.3077 | 61.4805 | 61.4143 | 61.4382 | 61.4618 | 61.491 | 61.4671 | 61.479 | 122.969 | 61.6256 | 122.9094 | 61.3988 | 61.4618 | 122.9797 | 61.4625 | 122.7625 | 61.5072 | 61.5065 | 61.4476 | 61.4469
663.8906 | 123.2803 | -61.4502 | 61.5326 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.022531 | 0.00775 | 0.028846 | 61.5188 | 0.17995 | 61.4409 | -0.051417 | 0.020767 | 61.5341 | 0.007721 | 61.3077 | 61.4759 | 61.4143 | 61.4382 | 61.4481 | 61.4727 | 61.4579 | 61.479 | 122.969 | 61.6301 | 122.8911 | 61.3988 | 61.471 | 122.9843 | 61.4579 | 122.7579 | 61.498 | 61.5111 | 61.4201 | 61.4332
664.8906 | 123.2666 | -61.4319 | 61.5555 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5188 | 0.17537 | 61.4455 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4576 | 61.3914 | 61.4245 | 61.4343 | 61.459 | 61.4442 | 61.4653 | 122.9507 | 61.6073 | 122.8773 | 61.3805 | 61.4481 | 122.9614 | 61.4396 | 122.7396 | 61.5026 | 61.5111 | 61.4293 | 61.4377
665.8906 | 123.3124 | -61.4227 | 61.5372 | 0.025705 | -0.0451 | -0.007421 | 0.002454 | 0.036265 | 0.012329 | 0.024268 | 61.5142 | 0.17537 | 61.4546 | -0.051417 | 0.016188 | 61.525 | 0.012299 | 61.3123 | 61.4484 | 61.3776 | 61.4153 | 61.4252 | 61.459 | 61.4351 | 61.447 | 122.9369 | 61.5981 | 122.8773 | 61.3713 | 61.4389 | 122.9477 | 61.435 | 122.735 | 61.498 | 61.5019 | 61.4384 | 61.4423
666.8906 | 123.2254 | -61.4227 | 61.5417 | 0.021127 | -0.040521 | -0.002842 | -0.002124 | 0.031687 | 0.00775 | 0.033424 | 61.505 | 0.17537 | 61.45 | -0.060575 | 0.01161 | 61.5341 | 0.007721 | 61.3031 | 61.4439 | 61.3822 | 61.4199 | 61.4206 | 61.4544 | 61.4305 | 61.4562 | 122.9278 | 61.5981 | 122.8728 | 61.3622 | 61.4343 | 122.9568 | 61.4304 | 122.7259 | 61.4934 | 61.4973 | 61.4384 | 61.4423
667.8906 | 123.2254 | -61.4365 | 61.5326 | 0.025705 | -0.035942 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.5188 | 0.18453 | 61.45 | -0.055996 | 0.016188 | 61.5295 | 0.003143 | 61.2986 | 61.4622 | 61.4005 | 61.4245 | 61.4343 | 61.4681 | 61.4442 | 61.4653 | 122.9552 | 61.621 | 122.8865 | 61.3805 | 61.4526 | 122.966 | 61.4396 | 122.735 | 61.5026 | 61.5156 | 61.4339 | 61.4469
668.8906 | 123.2346 | -61.4273 | 61.5509 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5142 | 0.17537 | 61.45 | -0.065154 | 0.025345 | 61.5295 | 0.007721 | 61.3123 | 61.4484 | 61.3914 | 61.4153 | 61.4298 | 61.4544 | 61.4351 | 61.4562 | 122.9415 | 61.6027 | 122.8773 | 61.3622 | 61.4527 | 122.9568 | 61.435 | 122.7396 | 61.4889 | 61.5065 | 61.4247 | 61.4423
669.8906 | 123.2025 | -61.441 | 61.5784 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.033424 | 61.5142 | 0.18453 | 61.4546 | -0.055996 | 0.01161 | 61.5387 | 0.012299 | 61.3169 | 61.4667 | 61.4051 | 61.429 | 61.4435 | 61.4727 | 61.4488 | 61.4745 | 122.9552 | 61.6256 | 122.8957 | 61.385 | 61.4526 | 122.9797 | 61.4533 | 122.7579 | 61.5026 | 61.5019 | 61.443 | 61.4423
670.8906 | 123.2666 | -61.441 | 61.5646 | 0.021127 | -0.049678 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5142 | 0.17537 | 61.4546 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3077 | 61.4622 | 61.3914 | 61.4245 | 61.4435 | 61.4681 | 61.4534 | 61.4699 | 122.9552 | 61.6164 | 122.8957 | 61.3896 | 61.4572 | 122.9706 | 61.4533 | 122.7488 | 61.498 | 61.5019 | 61.4384 | 61.4423
671.8906 | 123.2941 | -61.4319 | 61.5555 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.00775 | 0.033424 | 61.5234 | 0.17995 | 61.45 | -0.051417 | 0.016188 | 61.5295 | 0.003143 | 61.3031 | 61.453 | 61.3959 | 61.4199 | 61.4343 | 61.4682 | 61.4396 | 61.4653 | 122.9552 | 61.6118 | 122.8819 | 61.3805 | 61.4481 | 122.9614 | 61.435 | 122.735 | 61.5072 | 61.5202 | 61.4339 | 61.4469
672.8906 | 123.2666 | -61.4319 | 61.5601 | 0.021127 | -0.035942 | -0.016578 | 0.011611 | 0.036265 | 0.012329 | 0.028846 | 61.5279 | 0.17995 | 61.4592 | -0.051417 | 0.01161 | 61.525 | 0.007721 | 61.3077 | 61.453 | 61.3959 | 61.4153 | 61.4435 | 61.4682 | 61.4442 | 61.4607 | 122.9598 | 61.6118 | 122.8911 | 61.3805 | 61.4435 | 122.9568 | 61.4396 | 122.7396 | 61.5163 | 61.5202 | 61.4476 | 61.4515
673.8906 | 123.3124 | -61.4044 | 61.5738 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.028846 | 61.5188 | 0.17995 | 61.45 | -0.055996 | 0.020767 | 61.525 | 0.003143 | 61.3215 | 61.4347 | 61.3639 | 61.3924 | 61.4115 | 61.4361 | 61.4167 | 61.4333 | 122.9232 | 61.5844 | 122.8545 | 61.3484 | 61.4252 | 122.9294 | 61.4076 | 122.7259 | 61.498 | 61.5156 | 61.4293 | 61.4469
674.8906 | 123.2712 | -61.4182 | 61.5967 | 0.016548 | -0.0451 | -0.012 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.5234 | 0.16622 | 61.45 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4347 | 61.3731 | 61.4062 | 61.416 | 61.4498 | 61.4213 | 61.4424 | 122.9415 | 61.5844 | 122.8682 | 61.3622 | 61.4343 | 122.9431 | 61.4259 | 122.7259 | 61.5072 | 61.5156 | 61.4339 | 61.4423
675.8906 | 123.2803 | -61.4273 | 61.5601 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.012329 | 0.033424 | 61.5188 | 0.17995 | 61.4546 | -0.065154 | 0.020767 | 61.525 | 0.012299 | 61.3169 | 61.4484 | 61.3868 | 61.4107 | 61.4343 | 61.459 | 61.4396 | 61.4607 | 122.9461 | 61.6073 | 122.8819 | 61.3622 | 61.4481 | 122.9523 | 61.4396 | 122.7442 | 61.498 | 61.5065 | 61.4339 | 61.4423
676.8906 | 123.2162 | -61.4044 | 61.6058 | 0.021127 | -0.040521 | -0.007421 | 0.007033 | 0.027109 | 0.012329 | 0.033424 | 61.5279 | 0.17537 | 61.4455 | -0.051417 | 0.016188 | 61.525 | 0.012299 | 61.3123 | 61.4255 | 61.3639 | 61.397 | 61.4115 | 61.4315 | 61.4167 | 61.4378 | 122.9324 | 61.5798 | 122.8499 | 61.353 | 61.4206 | 122.9294 | 61.4167 | 122.7167 | 61.5118 | 61.5156 | 61.4293 | 61.4332
677.8906 | 123.1613 | -61.4319 | 61.615 | 0.025705 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | 0.00775 | 0.024268 | 61.5234 | 0.17995 | 61.4592 | -0.051417 | 0.01161 | 61.5295 | 0.012299 | 61.3123 | 61.4576 | 61.3914 | 61.4245 | 61.4389 | 61.4682 | 61.4396 | 61.4562 | 122.9552 | 61.6118 | 122.8911 | 61.3805 | 61.4435 | 122.9614 | 61.4442 | 122.7442 | 61.5118 | 61.5111 | 61.4476 | 61.4469
678.8906 | 123.2346 | -61.4273 | 61.5967 | 0.021127 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | 0.012329 | 0.033424 | 61.5279 | 0.17995 | 61.4546 | -0.055996 | 0.020767 | 61.5204 | 0.007721 | 61.3215 | 61.4484 | 61.3868 | 61.4199 | 61.4252 | 61.459 | 61.4396 | 61.4607 | 122.9553 | 61.6073 | 122.8819 | 61.3713 | 61.4481 | 122.9477 | 61.435 | 122.7488 | 61.5072 | 61.5202 | 61.4339 | 61.4469
679.8906 | 123.1613 | -61.4594 | 61.6058 | 0.030283 | -0.035942 | -0.002842 | 0.002454 | 0.031687 | 0.016907 | 0.033424 | 61.5142 | 0.17537 | 61.4546 | -0.060575 | 0.016188 | 61.5295 | 0.021456 | 61.3123 | 61.4896 | 61.4234 | 61.4565 | 61.4618 | 61.491 | 61.4763 | 61.4928 | 122.9736 | 61.6347 | 122.914 | 61.3988 | 61.4755 | 122.9889 | 61.4808 | 122.7717 | 61.498 | 61.4928 | 61.4384 | 61.4332
680.8906 | 123.2025 | -61.4319 | 61.6425 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.024268 | 61.5279 | 0.17995 | 61.4546 | -0.055996 | 0.020767 | 61.5295 | 0.003143 | 61.3215 | 61.453 | 61.3914 | 61.4199 | 61.4389 | 61.4636 | 61.4442 | 61.4562 | 122.9598 | 61.6118 | 122.8865 | 61.3759 | 61.4527 | 122.9614 | 61.435 | 122.7533 | 61.5072 | 61.5248 | 61.4339 | 61.4515
681.8906 | 123.2117 | -61.4456 | 61.5829 | 0.016548 | -0.035942 | -0.016578 | -0.002124 | 0.031687 | 0.016907 | 0.033424 | 61.5279 | 0.18453 | 61.4546 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4622 | 61.4097 | 61.429 | 61.4435 | 61.4773 | 61.4625 | 61.479 | 122.9736 | 61.6301 | 122.9002 | 61.3896 | 61.4618 | 122.9752 | 61.4533 | 122.7533 | 61.5118 | 61.5202 | 61.4384 | 61.4469
682.8906 | 123.1888 | -61.4365 | 61.5875 | 0.021127 | -0.0451 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.5188 | 0.17537 | 61.4592 | -0.051417 | 0.025345 | 61.525 | 0.007721 | 61.3077 | 61.4576 | 61.3914 | 61.4245 | 61.4435 | 61.4681 | 61.4442 | 61.4699 | 122.9552 | 61.6118 | 122.8957 | 61.385 | 61.4618 | 122.9614 | 61.4442 | 122.7442 | 61.4934 | 61.5111 | 61.4339 | 61.4515
683.8906 | 123.2437 | -61.4594 | 61.5967 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5279 | 0.17537 | 61.4592 | -0.046838 | 0.016188 | 61.5295 | 0.007721 | 61.3123 | 61.4851 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 122.9873 | 61.6347 | 122.9185 | 61.4125 | 61.4755 | 122.9889 | 61.4671 | 122.7717 | 61.5118 | 61.5202 | 61.443 | 61.4515
684.8906 | 123.2117 | -61.4273 | 61.6058 | 0.025705 | -0.040521 | -0.007421 | 0.002454 | 0.040843 | 0.012329 | 0.033424 | 61.5188 | 0.17537 | 61.4592 | -0.055996 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.453 | 61.3868 | 61.4199 | 61.4298 | 61.4682 | 61.4396 | 61.4607 | 122.9461 | 61.6027 | 122.8865 | 61.3713 | 61.4435 | 122.9568 | 61.4396 | 122.7396 | 61.5026 | 61.5065 | 61.443 | 61.4469
685.8906 | 123.1842 | -61.409 | 61.6196 | 0.025705 | -0.0451 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5279 | 0.17995 | 61.45 | -0.046838 | 0.01161 | 61.525 | 0.003143 | 61.3077 | 61.4347 | 61.3639 | 61.397 | 61.416 | 61.4453 | 61.4213 | 61.447 | 122.9369 | 61.5889 | 122.859 | 61.3622 | 61.4206 | 122.934 | 61.4121 | 122.7167 | 61.5163 | 61.5248 | 61.4384 | 61.4469
686.8906 | 123.2025 | -61.441 | 61.5875 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5279 | 0.18453 | 61.4546 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3077 | 61.4622 | 61.4051 | 61.4245 | 61.4435 | 61.4681 | 61.4534 | 61.4653 | 122.969 | 61.6256 | 122.8957 | 61.385 | 61.4572 | 122.9752 | 61.4488 | 122.7488 | 61.5118 | 61.5202 | 61.4384 | 61.4469
687.8906 | 123.1659 | -61.4685 | 61.5921 | 0.030283 | -0.040521 | -0.007421 | 0.007033 | 0.031687 | 0.026064 | 0.033424 | 61.5279 | 0.17995 | 61.4592 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4988 | 61.428 | 61.4611 | 61.4755 | 61.5002 | 61.4946 | 61.5019 | 122.9964 | 61.6485 | 122.9277 | 61.4125 | 61.4893 | 122.998 | 61.4762 | 122.7808 | 61.5072 | 61.5202 | 61.4384 | 61.4515
688.8906 | 123.1888 | -61.4548 | 61.5921 | 0.021127 | -0.0451 | -0.016578 | 0.007033 | 0.036265 | 0.012329 | 0.033424 | 61.5188 | 0.17537 | 61.45 | -0.051417 | 0.020767 | 61.5341 | 0.007721 | 61.3077 | 61.4759 | 61.4097 | 61.4382 | 61.4618 | 61.491 | 61.4671 | 61.4882 | 122.9736 | 61.6301 | 122.9048 | 61.4034 | 61.4755 | 122.9889 | 61.4625 | 122.7625 | 61.498 | 61.5111 | 61.4293 | 61.4423
689.8906 | 123.143 | -61.4548 | 61.6058 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5279 | 0.17537 | 61.4546 | -0.046838 | 0.01161 | 61.5204 | 0.007721 | 61.3031 | 61.4805 | 61.4143 | 61.4428 | 61.4572 | 61.4865 | 61.4671 | 61.4882 | 122.9827 | 61.6301 | 122.9094 | 61.4079 | 61.4664 | 122.9752 | 61.4625 | 122.7579 | 61.5163 | 61.5202 | 61.443 | 61.4469
690.8906 | 123.143 | -61.4594 | 61.5967 | 0.025705 | -0.035942 | -0.012 | 0.011611 | 0.031687 | 0.00775 | 0.033424 | 61.5234 | 0.17537 | 61.45 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4851 | 61.4234 | 61.4474 | 61.471 | 61.491 | 61.4671 | 61.4928 | 122.9827 | 61.6347 | 122.9094 | 61.4034 | 61.4801 | 122.9889 | 61.4671 | 122.7717 | 61.5026 | 61.5156 | 61.4293 | 61.4423
691.8906 | 123.1659 | -61.4777 | 61.5921 | 0.021127 | -0.031363 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.5234 | 0.18453 | 61.45 | -0.065154 | 0.016188 | 61.525 | 0.007721 | 61.3169 | 61.4988 | 61.4463 | 61.4657 | 61.4801 | 61.5093 | 61.49 | 61.5019 | 123.001 | 61.6622 | 122.9277 | 61.4125 | 61.4938 | 123.0026 | 61.4854 | 122.7945 | 61.5072 | 61.5156 | 61.4339 | 61.4423
692.8906 | 123.2254 | -61.4731 | 61.615 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5188 | 0.18453 | 61.45 | -0.046838 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4942 | 61.4371 | 61.4565 | 61.4755 | 61.5002 | 61.4854 | 61.5065 | 122.9919 | 61.6576 | 122.9231 | 61.4262 | 61.4893 | 123.0026 | 61.4854 | 122.7854 | 61.5026 | 61.5065 | 61.4339 | 61.4377
693.8906 | 123.23 | -61.4685 | 61.5601 | 0.021127 | -0.035942 | -0.021157 | 0.007033 | 0.031687 | 0.012329 | 0.033424 | 61.5234 | 0.17995 | 61.4592 | -0.055996 | 0.01161 | 61.5295 | 0.007721 | 61.3123 | 61.4896 | 61.4326 | 61.4473 | 61.4755 | 61.5002 | 61.4808 | 61.5019 | 122.9919 | 61.6485 | 122.9277 | 61.4125 | 61.4801 | 122.998 | 61.4762 | 122.7808 | 61.5118 | 61.5156 | 61.4476 | 61.4515
694.8906 | 123.2208 | -61.4548 | 61.5738 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.016907 | 0.028846 | 61.5188 | 0.17537 | 61.45 | -0.060575 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4805 | 61.4143 | 61.4428 | 61.4572 | 61.4819 | 61.4717 | 61.4836 | 122.9736 | 61.6301 | 122.9048 | 61.3942 | 61.471 | 122.9797 | 61.4625 | 122.7625 | 61.5026 | 61.5111 | 61.4339 | 61.4423
695.8906 | 123.2895 | -61.4594 | 61.5463 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5234 | 0.17537 | 61.4638 | -0.065154 | 0.01161 | 61.5295 | 0.003143 | 61.3077 | 61.4851 | 61.4234 | 61.4474 | 61.4618 | 61.4865 | 61.4717 | 61.4882 | 122.9827 | 61.6347 | 122.9231 | 61.3942 | 61.471 | 122.9889 | 61.4625 | 122.7671 | 61.5118 | 61.5202 | 61.4522 | 61.4606
696.8906 | 123.3261 | -61.4136 | 61.528 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.012329 | 0.024268 | 61.5279 | 0.17995 | 61.45 | -0.051417 | 0.025345 | 61.525 | 0.012299 | 61.3031 | 61.4347 | 61.3731 | 61.4016 | 61.4206 | 61.4407 | 61.4259 | 61.4378 | 122.9415 | 61.5935 | 122.8636 | 61.3622 | 61.4389 | 122.9385 | 61.4259 | 122.7167 | 61.5026 | 61.5156 | 61.4247 | 61.4377
697.8906 | 123.2803 | -61.3998 | 61.5234 | 0.021127 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | 0.012329 | 0.028846 | 61.5234 | 0.18453 | 61.4546 | -0.055996 | 0.01161 | 61.5295 | 0.007721 | 61.3077 | 61.421 | 61.3593 | 61.3924 | 61.3977 | 61.4315 | 61.4122 | 61.4287 | 122.9232 | 61.5844 | 122.8545 | 61.3438 | 61.4115 | 122.9294 | 61.4076 | 122.7076 | 61.5118 | 61.5156 | 61.443 | 61.4469
698.8906 | 123.2803 | -61.4182 | 61.5372 | 0.021127 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.5188 | 0.17537 | 61.4592 | -0.055996 | 0.016188 | 61.5204 | 0.012299 | 61.3077 | 61.4393 | 61.3822 | 61.4016 | 61.4206 | 61.4498 | 61.4305 | 61.4424 | 122.9369 | 61.5935 | 122.8773 | 61.3622 | 61.4343 | 122.9385 | 61.4305 | 122.7259 | 61.5026 | 61.5065 | 61.443 | 61.4469
699.8906 | 123.3582 | -61.4594 | 61.5143 | 0.016548 | -0.040521 | -0.012 | -0.006703 | 0.031687 | 0.012329 | 0.028846 | 61.5188 | 0.17537 | 61.45 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3031 | 61.4759 | 61.4188 | 61.4474 | 61.4526 | 61.491 | 61.4717 | 61.4882 | 122.9781 | 61.6347 | 122.9094 | 61.4034 | 61.4755 | 122.9935 | 61.4671 | 122.7625 | 61.5026 | 61.5111 | 61.4339 | 61.4423
700.8906 | 123.2712 | -61.4319 | 61.5463 | 0.021127 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.5234 | 0.17995 | 61.4592 | -0.051417 | 0.016188 | 61.5341 | 0.016878 | 61.3123 | 61.453 | 61.3959 | 61.4245 | 61.4343 | 61.459 | 61.4396 | 61.4653 | 122.9552 | 61.6118 | 122.8911 | 61.3805 | 61.4481 | 122.966 | 61.4488 | 122.7442 | 61.5072 | 61.5065 | 61.443 | 61.4423
701.8906 | 123.2712 | -61.4227 | 61.5417 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.024268 | 61.5188 | 0.18453 | 61.4546 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4484 | 61.3822 | 61.4062 | 61.4298 | 61.4498 | 61.4305 | 61.447 | 122.9415 | 61.6073 | 122.8773 | 61.3713 | 61.4389 | 122.9523 | 61.435 | 122.735 | 61.5026 | 61.5065 | 61.4384 | 61.4423
702.8906 | 123.2254 | -61.4182 | 61.5417 | 0.01197 | -0.0451 | -0.012 | 0.002454 | 0.022531 | 0.016907 | 0.028846 | 61.5234 | 0.17079 | 61.45 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3077 | 61.4301 | 61.3731 | 61.4062 | 61.4206 | 61.4407 | 61.4351 | 61.447 | 122.9415 | 61.5889 | 122.8682 | 61.3622 | 61.4343 | 122.9431 | 61.4213 | 122.7259 | 61.5072 | 61.5202 | 61.4339 | 61.4469
703.8906 | 123.2346 | -61.4365 | 61.5463 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.028846 | 61.5142 | 0.17537 | 61.45 | -0.051417 | 0.020767 | 61.5341 | 0.007721 | 61.3077 | 61.4576 | 61.3959 | 61.4245 | 61.4389 | 61.4727 | 61.4488 | 61.4653 | 122.9507 | 61.6118 | 122.8865 | 61.385 | 61.4572 | 122.9706 | 61.4442 | 122.7442 | 61.4934 | 61.5065 | 61.4293 | 61.4423
704.8906 | 123.2437 | -61.4273 | 61.5417 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.028846 | 61.5234 | 0.17995 | 61.4546 | -0.051417 | 0.01161 | 61.5295 | 0.007721 | 61.3169 | 61.4439 | 61.3868 | 61.4107 | 61.4298 | 61.459 | 61.4351 | 61.4562 | 122.9507 | 61.6073 | 122.8819 | 61.3759 | 61.4389 | 122.9568 | 61.435 | 122.7442 | 61.5118 | 61.5156 | 61.443 | 61.4469
705.8906 | 123.2346 | -61.4365 | 61.5875 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.00775 | 0.024268 | 61.5234 | 0.17995 | 61.45 | -0.046838 | 0.01161 | 61.525 | -0.001436 | 61.3077 | 61.4622 | 61.3959 | 61.4245 | 61.4435 | 61.4636 | 61.4442 | 61.4607 | 122.9598 | 61.6164 | 122.8865 | 61.3896 | 61.4481 | 122.9614 | 61.435 | 122.7442 | 61.5118 | 61.5248 | 61.4384 | 61.4515
706.8906 | 123.262 | -61.4365 | 61.5372 | 0.021127 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.00775 | 0.028846 | 61.5279 | 0.17995 | 61.4455 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3169 | 61.4576 | 61.4051 | 61.429 | 61.4389 | 61.4727 | 61.4442 | 61.4653 | 122.9644 | 61.6164 | 122.8819 | 61.385 | 61.4526 | 122.966 | 61.4488 | 122.7533 | 61.5118 | 61.5156 | 61.4293 | 61.4332
707.8906 | 123.2666 | -61.441 | 61.5738 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.024268 | 61.5188 | 0.17079 | 61.45 | -0.060575 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4576 | 61.4005 | 61.429 | 61.4481 | 61.4727 | 61.4534 | 61.4653 | 122.9598 | 61.6118 | 122.8911 | 61.3805 | 61.4572 | 122.9706 | 61.4488 | 122.7488 | 61.5026 | 61.5111 | 61.4339 | 61.4423
708.8906 | 123.2529 | -61.4273 | 61.5738 | 0.025705 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.028846 | 61.5142 | 0.17995 | 61.45 | -0.046838 | 0.020767 | 61.525 | 0.007721 | 61.3169 | 61.453 | 61.3868 | 61.4107 | 61.4343 | 61.459 | 61.4351 | 61.4562 | 122.9415 | 61.6073 | 122.8773 | 61.3805 | 61.4481 | 122.9523 | 61.435 | 122.7442 | 61.4934 | 61.5065 | 61.4293 | 61.4423
709.8906 | 123.2895 | -61.4319 | 61.5463 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.016907 | 0.01969 | 61.5279 | 0.17079 | 61.4546 | -0.051417 | 0.020767 | 61.5204 | 0.016878 | 61.3123 | 61.4484 | 61.3914 | 61.4199 | 61.4343 | 61.459 | 61.4488 | 61.4516 | 122.9598 | 61.6027 | 122.8865 | 61.3805 | 61.4527 | 122.9523 | 61.4488 | 122.7442 | 61.5072 | 61.5111 | 61.4339 | 61.4377
710.8906 | 123.2254 | -61.441 | 61.5738 | 0.016548 | -0.035942 | -0.007421 | 0.011611 | 0.036265 | 0.016907 | 0.033424 | 61.5325 | 0.18453 | 61.4592 | -0.055996 | 0.020767 | 61.525 | 0.007721 | 61.3169 | 61.4576 | 61.4051 | 61.4336 | 61.4527 | 61.4773 | 61.4579 | 61.4745 | 122.9736 | 61.6256 | 122.9002 | 61.385 | 61.4618 | 122.966 | 61.4488 | 122.7579 | 61.5118 | 61.5248 | 61.4384 | 61.4515
711.8906 | 123.2666 | -61.4273 | 61.5463 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.033424 | 61.5279 | 0.17995 | 61.4592 | -0.046838 | 0.020767 | 61.525 | 0.012299 | 61.3077 | 61.4484 | 61.3822 | 61.4153 | 61.4298 | 61.4544 | 61.4305 | 61.4607 | 122.9553 | 61.6073 | 122.8865 | 61.3805 | 61.4481 | 122.9523 | 61.4396 | 122.735 | 61.5072 | 61.5156 | 61.4384 | 61.4469
712.8906 | 123.2803 | -61.4365 | 61.5555 | 0.01197 | -0.040521 | -0.007421 | 0.002454 | 0.031687 | 0.00775 | 0.033424 | 61.5188 | 0.17995 | 61.4546 | -0.046838 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4484 | 61.3959 | 61.429 | 61.4389 | 61.4681 | 61.4442 | 61.4699 | 122.9552 | 61.6164 | 122.8911 | 61.3896 | 61.4526 | 122.966 | 61.4442 | 122.7396 | 61.5026 | 61.5111 | 61.4384 | 61.4469
713.8906 | 123.3215 | -61.4456 | 61.5646 | 0.025705 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.033424 | 61.5279 | 0.17537 | 61.4592 | -0.051417 | 0.025345 | 61.5295 | 0.007721 | 61.3077 | 61.4713 | 61.4051 | 61.4336 | 61.4435 | 61.4727 | 61.4579 | 61.479 | 122.9736 | 61.621 | 122.9048 | 61.3942 | 61.471 | 122.9752 | 61.4533 | 122.7533 | 61.5026 | 61.5202 | 61.4339 | 61.4515
714.8906 | 123.3353 | -61.3953 | 61.5463 | 0.016548 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5188 | 0.17995 | 61.4592 | -0.060575 | 0.016188 | 61.5295 | 0.007721 | 61.3169 | 61.4118 | 61.3547 | 61.3741 | 61.3977 | 61.4224 | 61.403 | 61.4241 | 122.9141 | 61.5752 | 122.8545 | 61.3347 | 61.4115 | 122.9248 | 61.403 | 122.7121 | 61.5026 | 61.5111 | 61.443 | 61.4515
715.8906 | 123.0743 | -61.5005 | 61.528 | 0.021127 | -0.0451 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.038003 | 61.5279 | 0.17995 | 61.4546 | -0.046838 | 0.007032 | 61.5341 | 0.012299 | 61.3123 | 61.5217 | 61.4554 | 61.484 | 61.4984 | 61.5277 | 61.5083 | 61.5386 | 123.0285 | 61.6805 | 122.9552 | 61.4537 | 61.5076 | 123.0347 | 61.5128 | 122.8129 | 61.5209 | 61.5156 | 61.4476 | 61.4423
716.8906 | 123.2895 | -61.4182 | 61.5646 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.016907 | 0.024268 | 61.5279 | 0.17995 | 61.4592 | -0.046838 | 0.016188 | 61.5341 | 0.007721 | 61.3123 | 61.4393 | 61.3822 | 61.4016 | 61.4252 | 61.4498 | 61.4351 | 61.4424 | 122.9461 | 61.5981 | 122.8773 | 61.3713 | 61.4343 | 122.9523 | 61.4259 | 122.7305 | 61.5118 | 61.5202 | 61.443 | 61.4515
717.8906 | 123.3398 | -61.4136 | 61.5646 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.024268 | 61.5279 | 0.17537 | 61.4592 | -0.060575 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4301 | 61.3685 | 61.4016 | 61.416 | 61.4453 | 61.4259 | 61.4378 | 122.9415 | 61.5889 | 122.8728 | 61.353 | 61.4298 | 122.9431 | 61.4259 | 122.7259 | 61.5118 | 61.5156 | 61.443 | 61.4469
718.8906 | 123.3124 | -61.4365 | 61.5875 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.016907 | 0.038003 | 61.5234 | 0.17995 | 61.4592 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3169 | 61.4576 | 61.3959 | 61.4245 | 61.4389 | 61.459 | 61.4534 | 61.4745 | 122.9598 | 61.6164 | 122.8957 | 61.3805 | 61.4572 | 122.966 | 61.4442 | 122.7533 | 61.5026 | 61.5156 | 61.4384 | 61.4515
719.8906 | 123.2712 | -61.4227 | 61.5601 | 0.01197 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.012329 | 0.024268 | 61.5234 | 0.17537 | 61.4592 | -0.060575 | 0.025345 | 61.5341 | 0.012299 | 61.3169 | 61.4347 | 61.3822 | 61.4107 | 61.4252 | 61.4453 | 61.4351 | 61.447 | 122.9461 | 61.5981 | 122.8819 | 61.3622 | 61.4481 | 122.9568 | 61.435 | 122.7396 | 61.498 | 61.5111 | 61.4339 | 61.4469
720.8906 | 123.2986 | -61.4182 | 61.5463 | 0.016548 | -0.035942 | -0.012 | 0.01619 | 0.031687 | 0.00775 | 0.033424 | 61.5234 | 0.17995 | 61.45 | -0.046838 | 0.020767 | 61.5295 | 0.007721 | 61.3169 | 61.4347 | 61.3822 | 61.4062 | 61.4343 | 61.4498 | 61.4259 | 61.4516 | 122.9415 | 61.5981 | 122.8682 | 61.3713 | 61.4389 | 122.9477 | 61.4259 | 122.735 | 61.5026 | 61.5156 | 61.4293 | 61.4423
721.8906 | 123.2483 | -61.3907 | 61.5829 | 0.016548 | -0.040521 | -0.012 | -0.002124 | 0.027109 | 0.012329 | 0.033424 | 61.5234 | 0.17995 | 61.4546 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3077 | 61.4072 | 61.3502 | 61.3787 | 61.3886 | 61.4178 | 61.403 | 61.4241 | 122.9141 | 61.5706 | 122.8453 | 61.3393 | 61.4115 | 122.9156 | 61.3984 | 122.6984 | 61.5026 | 61.5156 | 61.4339 | 61.4469
722.8906 | 123.2758 | -61.441 | 61.5692 | 0.030283 | -0.0451 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5188 | 0.17537 | 61.4592 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.3077 | 61.4713 | 61.3959 | 61.4245 | 61.4435 | 61.4681 | 61.4534 | 61.4653 | 122.9598 | 61.6164 | 122.9002 | 61.385 | 61.4618 | 122.966 | 61.4533 | 122.7488 | 61.498 | 61.5065 | 61.4384 | 61.4469
723.8906 | 123.2849 | -61.3998 | 61.5921 | 0.021127 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.038003 | 61.5188 | 0.17537 | 61.4546 | -0.046838 | 0.016188 | 61.5295 | 0.003143 | 61.3123 | 61.421 | 61.3639 | 61.3924 | 61.4023 | 61.427 | 61.4122 | 61.4378 | 122.9186 | 61.5752 | 122.8545 | 61.353 | 61.416 | 122.9294 | 61.403 | 122.7121 | 61.5026 | 61.5156 | 61.4384 | 61.4515
724.8906 | 123.23 | -61.4136 | 61.6013 | 0.016548 | -0.035942 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5279 | 0.18453 | 61.4592 | -0.046838 | 0.016188 | 61.525 | 0.016878 | 61.3215 | 61.4301 | 61.3776 | 61.397 | 61.416 | 61.4453 | 61.4259 | 61.4424 | 122.9415 | 61.5981 | 122.8728 | 61.3667 | 61.4298 | 122.9385 | 61.4305 | 122.735 | 61.5118 | 61.5111 | 61.443 | 61.4423
725.8906 | 123.1842 | -61.4777 | 61.5784 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.033424 | 61.5234 | 0.18453 | 61.4592 | -0.046838 | 0.020767 | 61.525 | -0.001436 | 61.3123 | 61.4988 | 61.4371 | 61.4611 | 61.4847 | 61.5048 | 61.4854 | 61.5111 | 123.001 | 61.6622 | 122.9369 | 61.4308 | 61.4984 | 123.0026 | 61.4762 | 122.79 | 61.5026 | 61.5248 | 61.4384 | 61.4606
726.8906 | 123.3032 | -61.3907 | 61.5967 | 0.016548 | -0.035942 | -0.012 | -0.002124 | 0.036265 | 0.00775 | 0.028846 | 61.5279 | 0.17995 | 61.4592 | -0.046838 | 0.016188 | 61.5158 | 0.007721 | 61.3077 | 61.4072 | 61.3547 | 61.3787 | 61.3886 | 61.427 | 61.3984 | 61.4195 | 122.9186 | 61.5706 | 122.8499 | 61.3438 | 61.4069 | 122.9065 | 61.3984 | 122.6984 | 61.5118 | 61.5202 | 61.443 | 61.4515
727.8906 | 123.2162 | -61.4227 | 61.5967 | 0.021127 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.5234 | 0.17537 | 61.4592 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4439 | 61.3822 | 61.4107 | 61.4252 | 61.4498 | 61.4305 | 61.4562 | 122.9461 | 61.5981 | 122.8819 | 61.3667 | 61.4389 | 122.9523 | 61.4304 | 122.7305 | 61.5072 | 61.5156 | 61.443 | 61.4515
728.8906 | 123.175 | -61.4502 | 61.6333 | 0.016548 | -0.0451 | -0.007421 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5279 | 0.17537 | 61.45 | -0.046838 | 0.016188 | 61.5341 | 0.016878 | 61.3123 | 61.4667 | 61.4051 | 61.4428 | 61.4526 | 61.4819 | 61.4625 | 61.4836 | 122.9781 | 61.6256 | 122.9002 | 61.4034 | 61.4664 | 122.9843 | 61.4671 | 122.7625 | 61.5118 | 61.5111 | 61.4339 | 61.4332
729.8906 | 123.1567 | -61.4456 | 61.6333 | 0.021127 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.024268 | 61.5279 | 0.17995 | 61.4546 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3215 | 61.4667 | 61.4143 | 61.4336 | 61.4527 | 61.4773 | 61.4534 | 61.4699 | 122.9736 | 61.6256 | 122.9002 | 61.3942 | 61.4664 | 122.9706 | 61.4533 | 122.7671 | 61.5072 | 61.5202 | 61.4339 | 61.4469
730.8906 | 123.1705 | -61.4319 | 61.6241 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.016907 | 0.028846 | 61.5234 | 0.17995 | 61.4546 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.3123 | 61.4484 | 61.3914 | 61.4199 | 61.4343 | 61.459 | 61.4488 | 61.4607 | 122.9552 | 61.6118 | 122.8865 | 61.3759 | 61.4527 | 122.9568 | 61.4442 | 122.7442 | 61.5026 | 61.5111 | 61.4339 | 61.4423
731.8906 | 123.1979 | -61.4731 | 61.5829 | 0.007391 | -0.035942 | -0.007421 | 0.002454 | 0.036265 | 0.021485 | 0.028846 | 61.5234 | 0.17079 | 61.4592 | -0.055996 | 0.020767 | 61.5295 | 0.012299 | 61.3123 | 61.4805 | 61.4371 | 61.4657 | 61.4755 | 61.5093 | 61.4946 | 61.5019 | 122.9964 | 61.6439 | 122.9323 | 61.4171 | 61.4939 | 123.0026 | 61.4854 | 122.7854 | 61.5026 | 61.5111 | 61.4384 | 61.4469
732.8906 | 123.143 | -61.4456 | 61.6196 | 0.016548 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | 0.012329 | 0.033424 | 61.5279 | 0.17995 | 61.4592 | -0.055996 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.4622 | 61.4097 | 61.429 | 61.4527 | 61.4819 | 61.4579 | 61.479 | 122.9736 | 61.6256 | 122.9048 | 61.3896 | 61.4664 | 122.9752 | 61.4488 | 122.7579 | 61.5072 | 61.5248 | 61.4384 | 61.4561
733.8906 | 123.1979 | -61.4365 | 61.6516 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5279 | 0.18911 | 61.4592 | -0.060575 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4622 | 61.3959 | 61.4199 | 61.4389 | 61.4636 | 61.4488 | 61.4699 | 122.9644 | 61.6256 | 122.8957 | 61.3759 | 61.4526 | 122.966 | 61.4488 | 122.7488 | 61.5118 | 61.5156 | 61.443 | 61.4469
734.8906 | 123.2025 | -61.4548 | 61.6058 | 0.021127 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.012329 | 0.042581 | 61.5234 | 0.17995 | 61.4592 | -0.051417 | 0.025345 | 61.525 | 0.007721 | 61.3077 | 61.4759 | 61.4188 | 61.4336 | 61.4572 | 61.491 | 61.4671 | 61.4974 | 122.9781 | 61.6347 | 122.914 | 61.4034 | 61.4801 | 122.9797 | 61.4625 | 122.7625 | 61.498 | 61.5156 | 61.4339 | 61.4515
735.8906 | 123.2117 | -61.441 | 61.5967 | 0.016548 | -0.035942 | -0.002842 | -0.002124 | 0.031687 | 0.00775 | 0.033424 | 61.5279 | 0.17995 | 61.4546 | -0.046838 | 0.020767 | 61.5204 | 0.007721 | 61.3077 | 61.4576 | 61.4051 | 61.4382 | 61.4389 | 61.4727 | 61.4488 | 61.4745 | 122.969 | 61.621 | 122.8957 | 61.3942 | 61.4618 | 122.9614 | 61.4488 | 122.7488 | 61.5072 | 61.5202 | 61.4339 | 61.4469
736.8906 | 123.2666 | -61.4594 | 61.5738 | 0.025705 | -0.031363 | -0.012 | 0.011611 | 0.027109 | 0.00775 | 0.033424 | 61.5234 | 0.17537 | 61.4638 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3077 | 61.4851 | 61.428 | 61.4474 | 61.471 | 61.4865 | 61.4671 | 61.4928 | 122.9827 | 61.6347 | 122.9231 | 61.4034 | 61.4801 | 122.9889 | 61.4671 | 122.7671 | 61.5026 | 61.5156 | 61.443 | 61.4561
737.8906 | 123.2346 | -61.4594 | 61.6058 | 0.01197 | -0.031363 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5325 | 0.17537 | 61.4546 | -0.051417 | 0.025345 | 61.525 | 0.012299 | 61.3169 | 61.4713 | 61.428 | 61.4474 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 122.9919 | 61.6347 | 122.914 | 61.4079 | 61.4847 | 122.9843 | 61.4716 | 122.7762 | 61.5072 | 61.5202 | 61.4293 | 61.4423
738.8906 | 123.1979 | -61.4456 | 61.5967 | 0.025705 | -0.031363 | -0.007421 | 0.002454 | 0.031687 | 0.012329 | 0.038003 | 61.5279 | 0.17537 | 61.4546 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4713 | 61.4143 | 61.4382 | 61.4481 | 61.4773 | 61.4579 | 61.4836 | 122.9736 | 61.621 | 122.9002 | 61.3896 | 61.4664 | 122.9752 | 61.4533 | 122.7579 | 61.5072 | 61.5202 | 61.4339 | 61.4469
739.8906 | 123.23 | -61.4456 | 61.5646 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.038003 | 61.5279 | 0.17995 | 61.4638 | -0.046838 | 0.016188 | 61.525 | 0.012299 | 61.3169 | 61.4667 | 61.4097 | 61.4336 | 61.4527 | 61.4819 | 61.4534 | 61.4836 | 122.9736 | 61.6256 | 122.9094 | 61.3988 | 61.4618 | 122.9706 | 61.4579 | 122.7625 | 61.5118 | 61.5156 | 61.4476 | 61.4515
740.8906 | 123.2208 | -61.441 | 61.5921 | 0.025705 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.016907 | 0.028846 | 61.5325 | 0.17079 | 61.4592 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4667 | 61.4051 | 61.4245 | 61.4435 | 61.4773 | 61.4579 | 61.4699 | 122.9736 | 61.6118 | 122.9002 | 61.3896 | 61.4572 | 122.9706 | 61.4488 | 122.7488 | 61.5163 | 61.5248 | 61.443 | 61.4515
741.8906 | 123.1796 | -61.4273 | 61.5784 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.024268 | 61.5325 | 0.18453 | 61.4546 | -0.046838 | 0.020767 | 61.525 | 0.016878 | 61.3123 | 61.453 | 61.3914 | 61.4153 | 61.4298 | 61.4636 | 61.4396 | 61.4516 | 122.9598 | 61.6118 | 122.8819 | 61.3805 | 61.4481 | 122.9523 | 61.4442 | 122.7396 | 61.5118 | 61.5156 | 61.4339 | 61.4377
742.8906 | 123.1796 | -61.4685 | 61.5921 | 0.016548 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | 0.016907 | 0.028846 | 61.5279 | 0.18911 | 61.4638 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.3169 | 61.4851 | 61.4371 | 61.4611 | 61.4801 | 61.5002 | 61.4854 | 61.4974 | 122.9964 | 61.6576 | 122.9323 | 61.4171 | 61.4847 | 122.998 | 61.4808 | 122.7854 | 61.5118 | 61.5156 | 61.4476 | 61.4515
743.8906 | 123.1338 | -61.4594 | 61.5829 | 0.025705 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.021485 | 0.033424 | 61.5325 | 0.17995 | 61.4592 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4851 | 61.4234 | 61.4519 | 61.4664 | 61.4956 | 61.4808 | 61.4928 | 122.9919 | 61.6393 | 122.9185 | 61.4079 | 61.4755 | 122.9889 | 61.4671 | 122.7625 | 61.5163 | 61.5248 | 61.443 | 61.4515
744.8906 | 123.1979 | -61.4456 | 61.5921 | 0.016548 | -0.035942 | -0.016578 | 0.007033 | 0.022531 | 0.012329 | 0.033424 | 61.5234 | 0.17537 | 61.45 | -0.042259 | 0.01161 | 61.5295 | 0.003143 | 61.3123 | 61.4622 | 61.4097 | 61.429 | 61.4527 | 61.4681 | 61.4579 | 61.479 | 122.969 | 61.621 | 122.8957 | 61.4034 | 61.4572 | 122.9752 | 61.4488 | 122.7579 | 61.5118 | 61.5202 | 61.4384 | 61.4469
745.8906 | 123.1842 | -61.4548 | 61.5784 | 0.016548 | -0.035942 | -0.021157 | 0.011611 | 0.027109 | 0.016907 | 0.038003 | 61.5234 | 0.18911 | 61.4592 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.2986 | 61.4713 | 61.4188 | 61.4336 | 61.4664 | 61.4819 | 61.4717 | 61.4928 | 122.9781 | 61.6439 | 122.914 | 61.4034 | 61.471 | 122.9797 | 61.4625 | 122.7533 | 61.5072 | 61.5156 | 61.443 | 61.4515
746.8906 | 123.1293 | -61.4639 | 61.5829 | 0.021127 | -0.031363 | -0.012 | 0.007033 | 0.027109 | 0.012329 | 0.028846 | 61.5279 | 0.18453 | 61.4546 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4851 | 61.4326 | 61.4519 | 61.471 | 61.491 | 61.4763 | 61.4928 | 122.9919 | 61.6485 | 122.9185 | 61.4125 | 61.4801 | 122.9889 | 61.4716 | 122.7762 | 61.5118 | 61.5202 | 61.4384 | 61.4469
747.8906 | 123.1934 | -61.4639 | 61.5875 | 0.016548 | -0.026784 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.033424 | 61.5371 | 0.18453 | 61.4592 | -0.060575 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4805 | 61.4371 | 61.4519 | 61.4664 | 61.4956 | 61.4808 | 61.4974 | 123.001 | 61.6485 | 122.9231 | 61.4034 | 61.4801 | 122.9935 | 61.4762 | 122.7762 | 61.5209 | 61.5248 | 61.443 | 61.4469
748.8906 | 123.1247 | -61.4685 | 61.5829 | 0.021127 | -0.031363 | -0.012 | 0.002454 | 0.040843 | 0.00775 | 0.024268 | 61.5279 | 0.18911 | 61.4592 | -0.051417 | 0.020767 | 61.5341 | 0.007721 | 61.3169 | 61.4896 | 61.4371 | 61.4565 | 61.471 | 61.5093 | 61.4763 | 61.4928 | 122.9964 | 61.6576 | 122.9277 | 61.4171 | 61.4893 | 123.0026 | 61.4762 | 122.7854 | 61.5072 | 61.5202 | 61.4384 | 61.4515
749.8906 | 123.1888 | -61.4548 | 61.5555 | 0.025705 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.021485 | 0.042581 | 61.5279 | 0.18911 | 61.4638 | -0.051417 | 0.01161 | 61.525 | 0.012299 | 61.3077 | 61.4805 | 61.4234 | 61.4474 | 61.4572 | 61.491 | 61.4763 | 61.4974 | 122.9827 | 61.6439 | 122.9185 | 61.4034 | 61.4664 | 122.9797 | 61.4671 | 122.7625 | 61.5163 | 61.5156 | 61.4522 | 61.4515
750.8906 | 123.2071 | -61.4777 | 61.5692 | 0.016548 | -0.035942 | -0.021157 | 0.007033 | 0.031687 | 0.012329 | 0.038003 | 61.5279 | 0.18453 | 61.4592 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4942 | 61.4417 | 61.4565 | 61.4847 | 61.5093 | 61.49 | 61.5157 | 123.0056 | 61.6622 | 122.9369 | 61.4217 | 61.4938 | 123.0072 | 61.4854 | 122.7854 | 61.5118 | 61.5202 | 61.443 | 61.4515
751.8906 | 123.1659 | -61.4639 | 61.5784 | 0.025705 | -0.026784 | -0.016578 | 0.007033 | 0.031687 | 0.012329 | 0.024268 | 61.5279 | 0.18453 | 61.4592 | -0.046838 | 0.01161 | 61.5295 | 0.007721 | 61.3077 | 61.4896 | 61.4371 | 61.4474 | 61.471 | 61.4956 | 61.4763 | 61.4882 | 122.9919 | 61.6485 | 122.9231 | 61.4171 | 61.4755 | 122.9935 | 61.4716 | 122.7717 | 61.5163 | 61.5202 | 61.4476 | 61.4515
752.8906 | 123.2071 | -61.4365 | 61.5646 | 0.021127 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.024268 | 61.5279 | 0.17995 | 61.4592 | -0.051417 | 0.016188 | 61.525 | 0.007721 | 61.3077 | 61.4576 | 61.4005 | 61.4199 | 61.4343 | 61.4636 | 61.4488 | 61.4607 | 122.9644 | 61.6164 | 122.8957 | 61.385 | 61.4526 | 122.9614 | 61.4442 | 122.7442 | 61.5118 | 61.5202 | 61.443 | 61.4515
753.8906 | 123.2025 | -61.4639 | 61.5646 | 0.016548 | -0.031363 | -0.021157 | 0.002454 | 0.031687 | 0.00775 | 0.033424 | 61.5325 | 0.17079 | 61.4638 | -0.046838 | 0.025345 | 61.525 | 0.007721 | 61.3169 | 61.4805 | 61.4326 | 61.4428 | 61.4664 | 61.4956 | 61.4717 | 61.4974 | 122.9964 | 61.6347 | 122.9277 | 61.4171 | 61.4893 | 122.9889 | 61.4716 | 122.7808 | 61.5072 | 61.5248 | 61.4384 | 61.4561
754.8906 | 123.1659 | -61.4456 | 61.5829 | 0.025705 | -0.035942 | -0.002842 | 0.002454 | 0.031687 | 0.012329 | 0.038003 | 61.5325 | 0.18453 | 61.4592 | -0.051417 | 0.020767 | 61.5295 | 0.007721 | 61.3077 | 61.4713 | 61.4097 | 61.4428 | 61.4481 | 61.4773 | 61.4579 | 61.4836 | 122.9781 | 61.6301 | 122.9048 | 61.3942 | 61.4664 | 122.9752 | 61.4533 | 122.7533 | 61.5118 | 61.5248 | 61.4384 | 61.4515
755.8906 | 123.2437 | -61.4639 | 61.5417 | 0.01197 | -0.035942 | -0.021157 | 0.002454 | 0.031687 | 0.012329 | 0.038003 | 61.5234 | 0.17995 | 61.4638 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4759 | 61.428 | 61.4428 | 61.4664 | 61.4956 | 61.4763 | 61.5019 | 122.9873 | 61.6439 | 122.9277 | 61.4079 | 61.4801 | 122.9935 | 61.4716 | 122.7717 | 61.5072 | 61.5156 | 61.4476 | 61.4561
756.8906 | 123.2986 | -61.4227 | 61.5372 | 0.025705 | -0.035942 | -0.016578 | 0.011611 | 0.022531 | 0.012329 | 0.033424 | 61.5234 | 0.18453 | 61.4592 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3169 | 61.4484 | 61.3868 | 61.4062 | 61.4343 | 61.4453 | 61.4351 | 61.4562 | 122.9461 | 61.6073 | 122.8819 | 61.3667 | 61.4389 | 122.9477 | 61.4304 | 122.7396 | 61.5072 | 61.5156 | 61.443 | 61.4515
757.8906 | 123.317 | -61.4273 | 61.528 | 0.021127 | -0.040521 | -0.007421 | -0.002124 | 0.031687 | 0.016907 | 0.024268 | 61.5188 | 0.18453 | 61.45 | -0.055996 | 0.016188 | 61.5204 | 0.003143 | 61.3077 | 61.4484 | 61.3868 | 61.4199 | 61.4252 | 61.459 | 61.4442 | 61.4516 | 122.9461 | 61.6118 | 122.8773 | 61.3713 | 61.4435 | 122.9477 | 61.4305 | 122.735 | 61.5026 | 61.5156 | 61.4339 | 61.4469
758.8906 | 123.2986 | -61.4136 | 61.5051 | 0.021127 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | 0.00775 | 0.042581 | 61.5234 | 0.17537 | 61.4638 | -0.055996 | 0.020767 | 61.5295 | 0.012299 | 61.3077 | 61.4347 | 61.3776 | 61.4062 | 61.416 | 61.4407 | 61.4213 | 61.4562 | 122.9369 | 61.5889 | 122.8773 | 61.3576 | 61.4343 | 122.9431 | 61.4259 | 122.7213 | 61.5026 | 61.5111 | 61.443 | 61.4515
759.8906 | 123.2895 | -61.4182 | 61.5097 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.022531 | 0.00775 | 0.033424 | 61.5325 | 0.18453 | 61.4546 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4393 | 61.3776 | 61.4016 | 61.4206 | 61.4407 | 61.4259 | 61.4516 | 122.9507 | 61.6027 | 122.8728 | 61.3622 | 61.4343 | 122.9477 | 61.4259 | 122.7213 | 61.5163 | 61.5248 | 61.4384 | 61.4469
760.8906 | 123.2803 | -61.4319 | 61.5463 | 0.025705 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5142 | 0.18453 | 61.4592 | -0.046838 | 0.016188 | 61.5341 | 0.007721 | 61.3077 | 61.4576 | 61.3959 | 61.4245 | 61.4343 | 61.459 | 61.4442 | 61.4607 | 122.9461 | 61.6164 | 122.8911 | 61.385 | 61.4481 | 122.966 | 61.4396 | 122.7396 | 61.498 | 61.5065 | 61.443 | 61.4515
761.8906 | 123.3078 | -61.4227 | 61.528 | 0.021127 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.016907 | 0.033424 | 61.5234 | 0.18911 | 61.45 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4439 | 61.3868 | 61.4153 | 61.4298 | 61.459 | 61.4396 | 61.4562 | 122.9461 | 61.6118 | 122.8728 | 61.3713 | 61.4389 | 122.9523 | 61.4304 | 122.7259 | 61.5072 | 61.5156 | 61.4339 | 61.4423
762.8906 | 123.2895 | -61.409 | 61.5372 | 0.021127 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.016907 | 0.024268 | 61.5325 | 0.18453 | 61.4592 | -0.055996 | 0.01161 | 61.5295 | 0.012299 | 61.3077 | 61.4301 | 61.3776 | 61.397 | 61.416 | 61.4453 | 61.4259 | 61.4333 | 122.9415 | 61.5935 | 122.8682 | 61.353 | 61.4206 | 122.9385 | 61.4213 | 122.7167 | 61.5209 | 61.5202 | 61.4476 | 61.4469
763.8906 | 123.3215 | -61.4273 | 61.5417 | 0.01197 | -0.040521 | -0.007421 | -0.002124 | 0.036265 | 0.00775 | 0.028846 | 61.5279 | 0.17995 | 61.4638 | -0.046838 | 0.020767 | 61.5341 | 0.012299 | 61.3077 | 61.4393 | 61.3868 | 61.4199 | 61.4252 | 61.4636 | 61.4351 | 61.4562 | 122.9553 | 61.6073 | 122.8911 | 61.3805 | 61.4481 | 122.9614 | 61.4396 | 122.735 | 61.5072 | 61.5156 | 61.443 | 61.4515
764.8906 | 123.2941 | -61.409 | 61.5234 | 0.021127 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | 0.003172 | 0.038003 | 61.5279 | 0.18911 | 61.4546 | -0.046838 | 0.016188 | 61.525 | 0.012299 | 61.3031 | 61.4301 | 61.3731 | 61.4016 | 61.4115 | 61.4407 | 61.4122 | 61.447 | 122.9369 | 61.5981 | 122.8636 | 61.3622 | 61.4252 | 122.934 | 61.4213 | 122.7121 | 61.5118 | 61.5156 | 61.4384 | 61.4423
765.8906 | 123.2849 | -61.4365 | 61.5189 | 0.016548 | -0.031363 | -0.016578 | -0.002124 | 0.027109 | 0.012329 | 0.038003 | 61.5279 | 0.18911 | 61.4546 | -0.051417 | 0.01161 | 61.5295 | 0.003143 | 61.3123 | 61.453 | 61.4051 | 61.4199 | 61.4343 | 61.4636 | 61.4488 | 61.4745 | 122.9644 | 61.6256 | 122.8911 | 61.385 | 61.4481 | 122.966 | 61.4396 | 122.7488 | 61.5163 | 61.5248 | 61.443 | 61.4515
766.8906 | 123.3124 | -61.4685 | 61.5372 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.024268 | 61.5279 | 0.18911 | 61.4592 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4851 | 61.4326 | 61.4565 | 61.471 | 61.4956 | 61.4717 | 61.4928 | 122.9964 | 61.6576 | 122.9277 | 61.4125 | 61.4893 | 122.998 | 61.4762 | 122.7808 | 61.5072 | 61.5202 | 61.4384 | 61.4515
767.8906 | 123.2712 | -61.4319 | 61.5509 | 0.016548 | -0.035942 | -0.021157 | -0.006703 | 0.031687 | 0.016907 | 0.038003 | 61.5279 | 0.18453 | 61.4546 | -0.055996 | 0.01161 | 61.525 | 0.012299 | 61.3031 | 61.4484 | 61.3959 | 61.4107 | 61.4252 | 61.4636 | 61.4488 | 61.4699 | 122.9598 | 61.6164 | 122.8865 | 61.3759 | 61.4435 | 122.9568 | 61.4442 | 122.735 | 61.5163 | 61.5156 | 61.443 | 61.4423
768.8906 | 123.2803 | -61.441 | 61.5234 | 0.016548 | -0.035942 | -0.007421 | 0.007033 | 0.027109 | 0.00775 | 0.028846 | 61.5325 | 0.17537 | 61.4592 | -0.051417 | 0.020767 | 61.5204 | 0.012299 | 61.3077 | 61.4576 | 61.4051 | 61.4336 | 61.4481 | 61.4681 | 61.4488 | 61.4699 | 122.9736 | 61.6164 | 122.9002 | 61.3896 | 61.4618 | 122.9614 | 61.4533 | 122.7488 | 61.5118 | 61.5202 | 61.4384 | 61.4469
769.8906 | 123.2483 | -61.4227 | 61.5372 | 0.016548 | -0.035942 | -0.021157 | 0.007033 | 0.040843 | 0.012329 | 0.033424 | 61.5325 | 0.17995 | 61.4592 | -0.046838 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4393 | 61.3868 | 61.4016 | 61.4298 | 61.4636 | 61.4351 | 61.4562 | 122.9553 | 61.6027 | 122.8819 | 61.3759 | 61.4435 | 122.9523 | 61.4304 | 122.735 | 61.5118 | 61.5248 | 61.4384 | 61.4515
770.8906 | 123.2803 | -61.441 | 61.5417 | 0.01197 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.028846 | 61.5325 | 0.17537 | 61.4638 | -0.055996 | 0.016188 | 61.525 | 0.012299 | 61.3077 | 61.453 | 61.4051 | 61.429 | 61.4435 | 61.4727 | 61.4488 | 61.4699 | 122.9736 | 61.6164 | 122.9048 | 61.385 | 61.4572 | 122.966 | 61.4533 | 122.7488 | 61.5163 | 61.5202 | 61.4476 | 61.4515
772.4219 | 123.3124 | -61.4136 | 61.5829 | 0.01197 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.024268 | 61.5279 | 0.18453 | 61.4546 | -0.055996 | 0.016188 | 61.5295 | 0.016878 | 61.3123 | 61.4255 | 61.3731 | 61.4062 | 61.416 | 61.4407 | 61.4259 | 61.4378 | 122.9415 | 61.5981 | 122.8682 | 61.3576 | 61.4298 | 122.9431 | 61.4305 | 122.7259 | 61.5118 | 61.5111 | 61.4384 | 61.4377
772.9844 | 123.1796 | -61.4456 | 61.5875 | 0.021127 | -0.035942 | -0.016578 | 0.011611 | 0.027109 | 0.016907 | 0.033424 | 61.5325 | 0.18453 | 61.4684 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4667 | 61.4097 | 61.429 | 61.4572 | 61.4727 | 61.4625 | 61.479 | 122.9781 | 61.6301 | 122.914 | 61.3896 | 61.4664 | 122.9752 | 61.4533 | 122.7579 | 61.5118 | 61.5248 | 61.4476 | 61.4606
774.5312 | 123.262 | -61.4044 | 61.5875 | 0.01197 | -0.0451 | -0.016578 | 0.011611 | 0.027109 | 0.016907 | 0.038003 | 61.5279 | 0.18453 | 61.4546 | -0.060575 | 0.020767 | 61.525 | 0.012299 | 61.3077 | 61.4164 | 61.3593 | 61.3878 | 61.416 | 61.4315 | 61.4213 | 61.4424 | 122.9324 | 61.5889 | 122.859 | 61.3438 | 61.4252 | 122.9294 | 61.4167 | 122.7121 | 61.5072 | 61.5156 | 61.4339 | 61.4423
774.9531 | 123.2895 | -61.4319 | 61.5463 | 0.01197 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.016907 | 0.033424 | 61.5371 | 0.18453 | 61.45 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3077 | 61.4439 | 61.3914 | 61.4199 | 61.4389 | 61.4636 | 61.4488 | 61.4653 | 122.969 | 61.6164 | 122.8819 | 61.3759 | 61.4527 | 122.9614 | 61.4396 | 122.7396 | 61.5163 | 61.5294 | 61.4293 | 61.4423
776.8125 | 123.23 | -61.4273 | 61.6013 | 0.025705 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.028846 | 61.5371 | 0.18453 | 61.4638 | -0.051417 | 0.016188 | 61.525 | 0.012299 | 61.3123 | 61.453 | 61.3914 | 61.4153 | 61.4298 | 61.459 | 61.4442 | 61.4562 | 122.9644 | 61.6118 | 122.8911 | 61.3759 | 61.4435 | 122.9523 | 61.4396 | 122.7396 | 61.5209 | 61.5248 | 61.4476 | 61.4515
777.5625 | 123.2758 | -61.4227 | 61.5417 | 0.016548 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5234 | 0.17995 | 61.4638 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3123 | 61.4393 | 61.3868 | 61.4153 | 61.4252 | 61.4498 | 61.4305 | 61.4516 | 122.9461 | 61.6027 | 122.8865 | 61.3667 | 61.4389 | 122.9568 | 61.4304 | 122.735 | 61.5072 | 61.5156 | 61.4476 | 61.4561
778.1875 | 123.3582 | -61.4502 | 61.5555 | 0.016548 | -0.035942 | -0.007421 | 0.002454 | 0.036265 | 0.016907 | 0.042581 | 61.5234 | 0.18453 | 61.4592 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3123 | 61.4667 | 61.4143 | 61.4428 | 61.4526 | 61.4865 | 61.4671 | 61.4928 | 122.9736 | 61.6347 | 122.9094 | 61.3988 | 61.471 | 122.9752 | 61.4579 | 122.7625 | 61.5026 | 61.5156 | 61.4384 | 61.4515
779.2031 | 123.2483 | -61.4273 | 61.5646 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.033424 | 61.5279 | 0.17995 | 61.4684 | -0.042259 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.4484 | 61.3914 | 61.4107 | 61.4343 | 61.4636 | 61.4305 | 61.4607 | 122.9553 | 61.6073 | 122.8957 | 61.385 | 61.4435 | 122.9568 | 61.435 | 122.735 | 61.5118 | 61.5202 | 61.4522 | 61.4606
783.2812 | 123.317 | -61.3953 | 61.5784 | 0.016548 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5325 | 0.17995 | 61.4592 | -0.046838 | 0.020767 | 61.5295 | 0.016878 | 61.3169 | 61.4118 | 61.3639 | 61.3787 | 61.3977 | 61.427 | 61.4076 | 61.4241 | 122.9278 | 61.5752 | 122.8545 | 61.3484 | 61.416 | 122.9248 | 61.4121 | 122.7121 | 61.5118 | 61.5156 | 61.4384 | 61.4423
783.7031 | 123.2758 | -61.4227 | 61.5509 | 0.021127 | -0.031363 | -0.021157 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5325 | 0.18911 | 61.4684 | -0.046838 | 0.01161 | 61.5295 | 0.003143 | 61.3123 | 61.4439 | 61.3914 | 61.4016 | 61.4252 | 61.4544 | 61.4351 | 61.4562 | 122.9553 | 61.6118 | 122.8911 | 61.3759 | 61.4343 | 122.9523 | 61.4259 | 122.735 | 61.5209 | 61.5294 | 61.4567 | 61.4652
784.125 | 123.2117 | -61.4273 | 61.5921 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.016907 | 0.028846 | 61.5325 | 0.18911 | 61.4638 | -0.055996 | 0.025345 | 61.5295 | 0.012299 | 61.3077 | 61.4439 | 61.3914 | 61.4153 | 61.4343 | 61.4636 | 61.4442 | 61.4562 | 122.9598 | 61.6164 | 122.8911 | 61.3713 | 61.4527 | 122.9568 | 61.4396 | 122.735 | 61.5072 | 61.5202 | 61.4384 | 61.4515
784.8906 | 123.3124 | -61.4182 | 61.5646 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.024268 | 61.5234 | 0.17995 | 61.45 | -0.051417 | 0.020767 | 61.5341 | 0.012299 | 61.3169 | 61.4393 | 61.3776 | 61.4062 | 61.4298 | 61.4544 | 61.4305 | 61.4424 | 122.9415 | 61.5981 | 122.8682 | 61.3667 | 61.4389 | 122.9523 | 61.4305 | 122.735 | 61.5026 | 61.5111 | 61.4293 | 61.4377
785.8906 | 123.2712 | -61.4044 | 61.5829 | 0.016548 | -0.040521 | -0.007421 | 0.007033 | 0.027109 | 0.012329 | 0.033424 | 61.5325 | 0.18453 | 61.4638 | -0.046838 | 0.016188 | 61.5295 | 0.012299 | 61.3169 | 61.421 | 61.3639 | 61.397 | 61.4115 | 61.4315 | 61.4167 | 61.4378 | 122.9369 | 61.5889 | 122.8682 | 61.3576 | 61.4206 | 122.934 | 61.4167 | 122.7213 | 61.5163 | 61.5202 | 61.4476 | 61.4515
786.8906 | 123.3307 | -61.4136 | 61.5646 | 0.016548 | -0.040521 | -0.021157 | 0.007033 | 0.036265 | 0.00775 | 0.033424 | 61.5279 | 0.18453 | 61.4638 | -0.046838 | 0.016188 | 61.5295 | 0.012299 | 61.3169 | 61.4301 | 61.3731 | 61.3924 | 61.4206 | 61.4498 | 61.4213 | 61.447 | 122.9415 | 61.5981 | 122.8773 | 61.3667 | 61.4298 | 122.9431 | 61.4259 | 122.7305 | 61.5118 | 61.5156 | 61.4476 | 61.4515
787.8906 | 123.2025 | -61.441 | 61.5967 | 0.025705 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.028846 | 61.5325 | 0.18453 | 61.4638 | -0.051417 | 0.020767 | 61.5387 | 0.012299 | 61.3215 | 61.4667 | 61.4005 | 61.429 | 61.4481 | 61.4773 | 61.4534 | 61.4699 | 122.9736 | 61.6256 | 122.9048 | 61.3896 | 61.4618 | 122.9797 | 61.4533 | 122.7625 | 61.5118 | 61.5202 | 61.443 | 61.4515
788.8906 | 123.2666 | -61.4273 | 61.5921 | 0.021127 | -0.040521 | -0.016578 | -0.002124 | 0.027109 | 0.00775 | 0.038003 | 61.5325 | 0.18453 | 61.4592 | -0.042259 | 0.020767 | 61.5295 | 0.016878 | 61.3123 | 61.4484 | 61.3868 | 61.4107 | 61.4252 | 61.4544 | 61.4351 | 61.4653 | 122.9598 | 61.6118 | 122.8865 | 61.385 | 61.4481 | 122.9568 | 61.4442 | 122.7396 | 61.5118 | 61.5156 | 61.4384 | 61.4423
789.8906 | 123.3032 | -61.3953 | 61.6333 | 0.016548 | -0.040521 | -0.021157 | 0.002454 | 0.031687 | 0.012329 | 0.038003 | 61.5325 | 0.17995 | 61.4546 | -0.051417 | 0.025345 | 61.5295 | 0.012299 | 61.3123 | 61.4118 | 61.3547 | 61.3741 | 61.3977 | 61.427 | 61.4076 | 61.4333 | 122.9278 | 61.5752 | 122.8499 | 61.3438 | 61.4206 | 122.9248 | 61.4076 | 122.7076 | 61.5072 | 61.5202 | 61.4293 | 61.4423
790.8906 | 123.3307 | -61.4136 | 61.5555 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.016907 | 0.028846 | 61.5234 | 0.18453 | 61.45 | -0.060575 | 0.016188 | 61.525 | 0.012299 | 61.3169 | 61.4347 | 61.3731 | 61.397 | 61.4206 | 61.4453 | 61.4305 | 61.4424 | 122.9369 | 61.5981 | 122.8636 | 61.353 | 61.4298 | 122.9385 | 61.4259 | 122.7305 | 61.5072 | 61.5111 | 61.4339 | 61.4377
791.8906 | 123.262 | -61.409 | 61.5738 | 0.016548 | -0.040521 | -0.021157 | 0.007033 | 0.031687 | 0.012329 | 0.033424 | 61.5234 | 0.18453 | 61.4592 | -0.051417 | 0.020767 | 61.525 | 0.021456 | 61.3123 | 61.4255 | 61.3685 | 61.3878 | 61.416 | 61.4407 | 61.4213 | 61.4424 | 122.9324 | 61.5935 | 122.8682 | 61.3576 | 61.4298 | 122.934 | 61.4305 | 122.7213 | 61.5026 | 61.5019 | 61.4384 | 61.4377
792.8906 | 123.2574 | -61.4319 | 61.5921 | 0.01197 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.5325 | 0.17995 | 61.4638 | -0.042259 | 0.016188 | 61.5295 | 0.012299 | 61.3123 | 61.4439 | 61.3959 | 61.4199 | 61.4389 | 61.4636 | 61.4396 | 61.4653 | 122.9644 | 61.6118 | 122.8957 | 61.3896 | 61.4481 | 122.9614 | 61.4442 | 122.7442 | 61.5163 | 61.5202 | 61.4476 | 61.4515
793.8906 | 123.1934 | -61.4456 | 61.615 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.027109 | 0.016907 | 0.033424 | 61.5279 | 0.18453 | 61.4684 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3077 | 61.4622 | 61.4097 | 61.4336 | 61.4527 | 61.4727 | 61.4625 | 61.479 | 122.9736 | 61.6301 | 122.914 | 61.3988 | 61.4664 | 122.9752 | 61.4488 | 122.7533 | 61.5072 | 61.5248 | 61.4476 | 61.4652
794.8906 | 123.2391 | -61.4273 | 61.6379 | 0.025705 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5279 | 0.17995 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | 0.012299 | 61.3169 | 61.453 | 61.3868 | 61.4153 | 61.4298 | 61.4544 | 61.4396 | 61.4562 | 122.9553 | 61.6073 | 122.8911 | 61.3759 | 61.4481 | 122.9568 | 61.4396 | 122.7442 | 61.5072 | 61.5156 | 61.443 | 61.4515
795.8906 | 123.1796 | -61.441 | 61.6104 | 0.016548 | -0.0451 | -0.021157 | 0.011611 | 0.031687 | 0.00775 | 0.033424 | 61.5234 | 0.18453 | 61.4592 | -0.051417 | 0.020767 | 61.5295 | 0.016878 | 61.3123 | 61.4576 | 61.3959 | 61.4199 | 61.4527 | 61.4727 | 61.4488 | 61.4745 | 122.9644 | 61.6256 | 122.9002 | 61.3896 | 61.4618 | 122.9706 | 61.4579 | 122.7533 | 61.5026 | 61.5065 | 61.4384 | 61.4423
796.8906 | 123.1934 | -61.4273 | 61.6241 | 0.030283 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.00775 | 0.033424 | 61.5279 | 0.18911 | 61.4592 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3169 | 61.4576 | 61.3914 | 61.4153 | 61.4343 | 61.4636 | 61.4351 | 61.4607 | 122.9553 | 61.6164 | 122.8865 | 61.3759 | 61.4481 | 122.9523 | 61.435 | 122.7442 | 61.5072 | 61.5202 | 61.4384 | 61.4515
797.8906 | 123.1613 | -61.4639 | 61.5875 | 0.016548 | -0.035942 | -0.016578 | 0.011611 | 0.036265 | 0.016907 | 0.038003 | 61.5234 | 0.18453 | 61.4638 | -0.055996 | 0.01161 | 61.525 | 0.003143 | 61.3031 | 61.4805 | 61.428 | 61.4474 | 61.4755 | 61.5002 | 61.4808 | 61.5019 | 122.9873 | 61.6485 | 122.9277 | 61.4079 | 61.4755 | 122.9889 | 61.4671 | 122.7671 | 61.5118 | 61.5202 | 61.4522 | 61.4606
798.8906 | 123.2117 | -61.441 | 61.6196 | 0.01197 | -0.035942 | -0.016578 | 0.011611 | 0.040843 | 0.00775 | 0.038003 | 61.5325 | 0.17995 | 61.4638 | -0.055996 | 0.025345 | 61.5341 | 0.016878 | 61.3169 | 61.453 | 61.4051 | 61.4245 | 61.4527 | 61.4819 | 61.4488 | 61.479 | 122.9736 | 61.621 | 122.9048 | 61.385 | 61.4664 | 122.9752 | 61.4579 | 122.7579 | 61.5072 | 61.5156 | 61.4384 | 61.4469
799.8906 | 123.2529 | -61.4456 | 61.6196 | 0.025705 | -0.035942 | -0.007421 | 0.007033 | 0.031687 | 0.016907 | 0.038003 | 61.5325 | 0.17537 | 61.4592 | -0.046838 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4713 | 61.4097 | 61.4382 | 61.4527 | 61.4773 | 61.4625 | 61.4836 | 122.9781 | 61.621 | 122.9048 | 61.3988 | 61.4618 | 122.9706 | 61.4533 | 122.7579 | 61.5163 | 61.5248 | 61.443 | 61.4515
800.8906 | 123.2162 | -61.4319 | 61.6241 | 0.021127 | -0.031363 | -0.007421 | 0.011611 | 0.027109 | 0.012329 | 0.038003 | 61.5371 | 0.17995 | 61.4592 | -0.051417 | 0.016188 | 61.5295 | 0.012299 | 61.326 | 61.453 | 61.4005 | 61.4245 | 61.4435 | 61.459 | 61.4442 | 61.4699 | 122.969 | 61.6118 | 122.8911 | 61.3805 | 61.4481 | 122.9614 | 61.4442 | 122.7579 | 61.5209 | 61.5248 | 61.443 | 61.4469
801.8906 | 123.262 | -61.4685 | 61.5738 | 0.016548 | -0.040521 | -0.007421 | 0.011611 | 0.040843 | 0.00775 | 0.028846 | 61.5279 | 0.18453 | 61.4592 | -0.051417 | 0.016188 | 61.525 | 0.016878 | 61.3169 | 61.4851 | 61.428 | 61.4611 | 61.4801 | 61.5093 | 61.4763 | 61.4974 | 122.9964 | 61.653 | 122.9277 | 61.4171 | 61.4847 | 122.9935 | 61.4854 | 122.7854 | 61.5118 | 61.5111 | 61.443 | 61.4423
802.8906 | 123.2574 | -61.4227 | 61.5417 | 0.016548 | -0.031363 | -0.016578 | 0.002454 | 0.036265 | 0.016907 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.525 | 0.012299 | 61.3077 | 61.4393 | 61.3914 | 61.4062 | 61.4252 | 61.459 | 61.4396 | 61.4562 | 122.9553 | 61.6118 | 122.8865 | 61.3713 | 61.4435 | 122.9477 | 61.435 | 122.7305 | 61.5118 | 61.5202 | 61.443 | 61.4515
803.8906 | 123.23 | -61.4319 | 61.5784 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.016907 | 0.033424 | 61.5325 | 0.17995 | 61.4592 | -0.055996 | 0.020767 | 61.525 | 0.007721 | 61.3215 | 61.453 | 61.3959 | 61.4199 | 61.4389 | 61.4727 | 61.4488 | 61.4653 | 122.9644 | 61.6118 | 122.8911 | 61.3759 | 61.4527 | 122.9568 | 61.4396 | 122.7533 | 61.5118 | 61.5248 | 61.4384 | 61.4515
804.8906 | 123.2391 | -61.4594 | 61.6104 | 0.030283 | -0.040521 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.033424 | 61.5325 | 0.17537 | 61.4638 | -0.051417 | 0.025345 | 61.5341 | 0.012299 | 61.3077 | 61.4896 | 61.4188 | 61.4474 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 122.9919 | 61.6347 | 122.9231 | 61.4079 | 61.4847 | 122.9935 | 61.4716 | 122.7671 | 61.5072 | 61.5202 | 61.4384 | 61.4515
805.8906 | 123.2071 | -61.4227 | 61.5921 | 0.025705 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.5279 | 0.18453 | 61.4638 | -0.046838 | 0.016188 | 61.5295 | 0.003143 | 61.3169 | 61.4484 | 61.3822 | 61.4062 | 61.4252 | 61.4498 | 61.4305 | 61.4562 | 122.9507 | 61.6073 | 122.8865 | 61.3759 | 61.4389 | 122.9523 | 61.4259 | 122.7396 | 61.5118 | 61.5248 | 61.4476 | 61.4606
806.8906 | 123.23 | -61.4136 | 61.6058 | 0.021127 | -0.031363 | -0.007421 | 0.007033 | 0.031687 | 0.012329 | 0.038003 | 61.5371 | 0.18911 | 61.4592 | -0.046838 | 0.016188 | 61.5295 | 0.012299 | 61.3215 | 61.4347 | 61.3822 | 61.4062 | 61.4206 | 61.4453 | 61.4259 | 61.4516 | 122.9507 | 61.6027 | 122.8728 | 61.3667 | 61.4298 | 122.9431 | 61.4259 | 122.735 | 61.5209 | 61.5248 | 61.443 | 61.4469
807.8906 | 123.3261 | -61.4456 | 61.5372 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.024268 | 61.5279 | 0.18911 | 61.4638 | -0.055996 | 0.016188 | 61.5295 | 0.016878 | 61.3077 | 61.4622 | 61.4051 | 61.4336 | 61.4481 | 61.4773 | 61.4625 | 61.4699 | 122.9736 | 61.6347 | 122.9094 | 61.3896 | 61.4618 | 122.9752 | 61.4625 | 122.7533 | 61.5118 | 61.5111 | 61.4476 | 61.4469
808.8906 | 123.1705 | -61.4227 | 61.5875 | 0.021127 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.012329 | 0.028846 | 61.5325 | 0.18453 | 61.4729 | -0.046838 | 0.025345 | 61.5341 | 0.016878 | 61.3169 | 61.4439 | 61.3868 | 61.4062 | 61.4298 | 61.4544 | 61.4351 | 61.4516 | 122.9553 | 61.6073 | 122.8957 | 61.3759 | 61.4481 | 122.9568 | 61.4396 | 122.7396 | 61.5072 | 61.5156 | 61.4476 | 61.4561
809.8906 | 123.1979 | -61.4319 | 61.6013 | 0.016548 | -0.035942 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.038003 | 61.5279 | 0.18453 | 61.4592 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.3123 | 61.4484 | 61.3959 | 61.4199 | 61.4435 | 61.4682 | 61.4442 | 61.4699 | 122.9598 | 61.6164 | 122.8911 | 61.3759 | 61.4527 | 122.9568 | 61.4442 | 122.7442 | 61.5072 | 61.5156 | 61.4384 | 61.4469
810.8906 | 123.2391 | -61.441 | 61.5738 | 0.016548 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.016907 | 0.028846 | 61.5325 | 0.17995 | 61.4684 | -0.055996 | 0.025345 | 61.5295 | 0.007721 | 61.3077 | 61.4576 | 61.4005 | 61.4245 | 61.4435 | 61.4773 | 61.4579 | 61.4699 | 122.9736 | 61.621 | 122.9094 | 61.385 | 61.4664 | 122.9706 | 61.4488 | 122.7488 | 61.5072 | 61.5248 | 61.443 | 61.4606
811.8906 | 123.1522 | -61.4456 | 61.5875 | 0.021127 | -0.035942 | -0.016578 | 0.011611 | 0.031687 | 0.026064 | 0.033424 | 61.5371 | 0.18911 | 61.4684 | -0.042259 | 0.016188 | 61.525 | 0.012299 | 61.3215 | 61.4667 | 61.4097 | 61.429 | 61.4572 | 61.4773 | 61.4717 | 61.479 | 122.9827 | 61.6347 | 122.914 | 61.4034 | 61.4618 | 122.9706 | 61.4579 | 122.7671 | 61.5209 | 61.5248 | 61.4522 | 61.4561
812.8906 | 123.2758 | -61.4182 | 61.5601 | 0.01197 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.003172 | 0.028846 | 61.5279 | 0.17995 | 61.4638 | -0.055996 | 0.020767 | 61.5341 | 0.016878 | 61.3169 | 61.4301 | 61.3822 | 61.397 | 61.4206 | 61.4544 | 61.4213 | 61.447 | 122.9461 | 61.5981 | 122.8819 | 61.3622 | 61.4389 | 122.9523 | 61.435 | 122.735 | 61.5072 | 61.5111 | 61.443 | 61.4469
813.8906 | 123.1522 | -61.441 | 61.5967 | 0.016548 | -0.035942 | -0.002842 | 0.007033 | 0.031687 | 0.012329 | 0.042581 | 61.5371 | 0.18453 | 61.4592 | -0.055996 | 0.025345 | 61.5341 | 0.012299 | 61.3123 | 61.4576 | 61.4051 | 61.4382 | 61.4481 | 61.4727 | 61.4534 | 61.4836 | 122.9781 | 61.6256 | 122.9002 | 61.385 | 61.4664 | 122.9752 | 61.4533 | 122.7533 | 61.5118 | 61.5248 | 61.4339 | 61.4469
814.8906 | 123.1934 | -61.4456 | 61.5829 | 0.007391 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.033424 | 61.5325 | 0.18453 | 61.4638 | -0.060575 | 0.016188 | 61.5341 | 0.003143 | 61.3123 | 61.453 | 61.4097 | 61.4382 | 61.4527 | 61.4819 | 61.4579 | 61.479 | 122.9781 | 61.6301 | 122.9094 | 61.385 | 61.4618 | 122.9797 | 61.4488 | 122.7579 | 61.5163 | 61.5294 | 61.4476 | 61.4606
815.8906 | 123.1979 | -61.441 | 61.5601 | 0.021127 | -0.040521 | -0.002842 | 0.007033 | 0.027109 | 0.012329 | 0.033424 | 61.5325 | 0.18911 | 61.4684 | -0.055996 | 0.020767 | 61.5204 | 0.012299 | 61.3077 | 61.4622 | 61.4005 | 61.4382 | 61.4481 | 61.4681 | 61.4534 | 61.4745 | 122.9736 | 61.6301 | 122.9094 | 61.385 | 61.4618 | 122.9614 | 61.4533 | 122.7488 | 61.5118 | 61.5202 | 61.4476 | 61.4561
816.8906 | 123.143 | -61.4456 | 61.5738 | 0.025705 | -0.035942 | -0.012 | 0.01619 | 0.031687 | 0.012329 | 0.033424 | 61.5371 | 0.17995 | 61.4592 | -0.051417 | 0.020767 | 61.5295 | 0.003143 | 61.3077 | 61.4713 | 61.4097 | 61.4336 | 61.4618 | 61.4773 | 61.4579 | 61.479 | 122.9827 | 61.6256 | 122.9048 | 61.3942 | 61.4664 | 122.9752 | 61.4488 | 122.7533 | 61.5163 | 61.534 | 61.4384 | 61.4561
817.8906 | 123.1705 | -61.4639 | 61.5784 | 0.021127 | -0.040521 | -0.007421 | 0.007033 | 0.031687 | 0.012329 | 0.038003 | 61.5325 | 0.17995 | 61.4592 | -0.051417 | 0.016188 | 61.5387 | 0.003143 | 61.3169 | 61.4851 | 61.4234 | 61.4565 | 61.471 | 61.4956 | 61.4763 | 61.5019 | 122.9964 | 61.6439 | 122.9231 | 61.4125 | 61.4801 | 123.0026 | 61.4671 | 122.7808 | 61.5163 | 61.5294 | 61.443 | 61.4561
818.8906 | 123.1659 | -61.4685 | 61.5692 | 0.016548 | -0.031363 | -0.007421 | 0.007033 | 0.027109 | 0.016907 | 0.033424 | 61.5234 | 0.18453 | 61.4638 | -0.051417 | 0.01161 | 61.5295 | 0.012299 | 61.3123 | 61.4851 | 61.4371 | 61.4611 | 61.4755 | 61.4956 | 61.4854 | 61.5019 | 122.9919 | 61.653 | 122.9323 | 61.4171 | 61.4801 | 122.998 | 61.4808 | 122.7808 | 61.5118 | 61.5111 | 61.4522 | 61.4515
819.8906 | 123.1659 | -61.4548 | 61.5875 | 0.016548 | -0.031363 | -0.012 | 0.007033 | 0.027109 | 0.016907 | 0.033424 | 61.5279 | 0.18911 | 61.4638 | -0.055996 | 0.016188 | 61.525 | 0.007721 | 61.3123 | 61.4713 | 61.4234 | 61.4428 | 61.4618 | 61.4819 | 61.4717 | 61.4882 | 122.9827 | 61.6439 | 122.9185 | 61.3988 | 61.471 | 122.9797 | 61.4625 | 122.7671 | 61.5118 | 61.5202 | 61.4476 | 61.4561
820.8906 | 123.23 | -61.4365 | 61.5326 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.028846 | 61.5325 | 0.19369 | 61.4592 | -0.051417 | 0.020767 | 61.5295 | 0.003143 | 61.3031 | 61.453 | 61.3959 | 61.4245 | 61.4389 | 61.4727 | 61.4488 | 61.4653 | 122.969 | 61.6302 | 122.8957 | 61.385 | 61.4572 | 122.966 | 61.4396 | 122.7396 | 61.5118 | 61.5294 | 61.4384 | 61.4561
821.8906 | 123.1659 | -61.4548 | 61.5967 | 0.016548 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.016907 | 0.038003 | 61.5371 | 0.18911 | 61.4638 | -0.055996 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4713 | 61.4234 | 61.4428 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 122.9919 | 61.6439 | 122.9185 | 61.3988 | 61.471 | 122.9843 | 61.4625 | 122.7579 | 61.5209 | 61.5294 | 61.4476 | 61.4561
822.8906 | 123.2712 | -61.4594 | 61.5417 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.031687 | 0.012329 | 0.038003 | 61.5325 | 0.18453 | 61.4592 | -0.051417 | 0.016188 | 61.5341 | 0.012299 | 61.3123 | 61.4805 | 61.4188 | 61.4474 | 61.471 | 61.491 | 61.4717 | 61.4974 | 122.9919 | 61.6439 | 122.9185 | 61.4079 | 61.4755 | 122.9935 | 61.4716 | 122.7717 | 61.5163 | 61.5202 | 61.443 | 61.4469
823.8906 | 123.2391 | -61.4456 | 61.5692 | 0.021127 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.016907 | 0.024268 | 61.5279 | 0.19369 | 61.4546 | -0.046838 | 0.020767 | 61.5295 | 0.012299 | 61.3031 | 61.4667 | 61.4051 | 61.429 | 61.4527 | 61.4727 | 61.4625 | 61.4699 | 122.9736 | 61.6393 | 122.9002 | 61.3988 | 61.4664 | 122.9752 | 61.4579 | 122.7488 | 61.5072 | 61.5156 | 61.4339 | 61.4423
824.8906 | 123.2025 | -61.4548 | 61.5738 | 0.021127 | -0.040521 | -0.012 | 0.007033 | 0.040843 | 0.012329 | 0.038003 | 61.5417 | 0.18453 | 61.4684 | -0.060575 | 0.020767 | 61.5341 | 0.007721 | 61.3123 | 61.4759 | 61.4143 | 61.4428 | 61.4618 | 61.4956 | 61.4671 | 61.4928 | 122.9965 | 61.6393 | 122.9231 | 61.3942 | 61.4755 | 122.9889 | 61.4625 | 122.7671 | 61.5209 | 61.534 | 61.4476 | 61.4606
825.8906 | 123.2346 | -61.4319 | 61.5417 | 0.021127 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.033424 | 61.5325 | 0.18911 | 61.4684 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3077 | 61.453 | 61.3959 | 61.4199 | 61.4343 | 61.4682 | 61.4442 | 61.4653 | 122.9644 | 61.621 | 122.9002 | 61.3805 | 61.4481 | 122.9614 | 61.4396 | 122.7396 | 61.5163 | 61.5248 | 61.4522 | 61.4606
826.8906 | 123.2208 | -61.4182 | 61.5372 | 0.01197 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5371 | 0.18453 | 61.4592 | -0.051417 | 0.016188 | 61.5387 | 0.007721 | 61.3123 | 61.4301 | 61.3822 | 61.4107 | 61.4206 | 61.4498 | 61.4305 | 61.4516 | 122.9553 | 61.6027 | 122.8773 | 61.3667 | 61.4343 | 122.9568 | 61.4259 | 122.7305 | 61.5209 | 61.5294 | 61.443 | 61.4515
827.8906 | 123.2071 | -61.4548 | 61.5509 | 0.016548 | -0.040521 | -0.021157 | 0.011611 | 0.031687 | 0.012329 | 0.038003 | 61.5325 | 0.18453 | 61.4592 | -0.060575 | 0.025345 | 61.5341 | 0.007721 | 61.3031 | 61.4713 | 61.4143 | 61.4336 | 61.4664 | 61.4865 | 61.4671 | 61.4928 | 122.9873 | 61.6393 | 122.914 | 61.3942 | 61.4801 | 122.9889 | 61.4625 | 122.7579 | 61.5072 | 61.5248 | 61.4339 | 61.4515
828.8906 | 123.262 | -61.4227 | 61.5143 | 0.016548 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.033424 | 61.5371 | 0.17995 | 61.4638 | -0.046838 | 0.025345 | 61.5341 | 0.016878 | 61.3031 | 61.4393 | 61.3914 | 61.4107 | 61.4298 | 61.4544 | 61.4351 | 61.4562 | 122.9598 | 61.6027 | 122.8865 | 61.3759 | 61.4481 | 122.9568 | 61.4396 | 122.7259 | 61.5118 | 61.5202 | 61.4384 | 61.4469
829.8906 | 123.2895 | -61.4227 | 61.5143 | 0.021127 | -0.031363 | -0.007421 | -0.002124 | 0.027109 | 0.012329 | 0.028846 | 61.5325 | 0.19369 | 61.4546 | -0.055996 | 0.016188 | 61.5341 | 0.012299 | 61.3031 | 61.4439 | 61.3914 | 61.4153 | 61.4206 | 61.4498 | 61.4351 | 61.4516 | 122.9553 | 61.6164 | 122.8773 | 61.3667 | 61.4389 | 122.9568 | 61.435 | 122.7259 | 61.5163 | 61.5202 | 61.4384 | 61.4423
830.8906 | 123.2574 | -61.4365 | 61.528 | 0.016548 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.028846 | 61.5279 | 0.18453 | 61.4546 | -0.051417 | 0.01161 | 61.525 | 0.003143 | 61.3123 | 61.453 | 61.4051 | 61.4245 | 61.4481 | 61.4727 | 61.4488 | 61.4653 | 122.9644 | 61.621 | 122.8911 | 61.385 | 61.4481 | 122.9614 | 61.4396 | 122.7488 | 61.5163 | 61.5248 | 61.443 | 61.4515
831.8906 | 123.1979 | -61.4639 | 61.5829 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.016907 | 0.038003 | 61.5325 | 0.18911 | 61.4638 | -0.042259 | 0.016188 | 61.5387 | 0.007721 | 61.3031 | 61.4805 | 61.428 | 61.4519 | 61.4664 | 61.5002 | 61.4808 | 61.5019 | 122.9964 | 61.653 | 122.9277 | 61.4217 | 61.4801 | 123.0026 | 61.4716 | 122.7671 | 61.5163 | 61.5248 | 61.4476 | 61.4561
832.8906 | 123.317 | -61.4319 | 61.5463 | 0.016548 | -0.0451 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.038003 | 61.5371 | 0.18911 | 61.4638 | -0.042259 | 0.016188 | 61.525 | 0.003143 | 61.3077 | 61.4484 | 61.3868 | 61.4245 | 61.4343 | 61.459 | 61.4442 | 61.4699 | 122.969 | 61.621 | 122.8957 | 61.3896 | 61.4481 | 122.9568 | 61.435 | 122.7396 | 61.5209 | 61.534 | 61.4476 | 61.4606
833.8906 | 123.2758 | -61.4136 | 61.528 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.016907 | 0.042581 | 61.5371 | 0.18453 | 61.4638 | -0.051417 | 0.016188 | 61.5295 | 0.007721 | 61.3031 | 61.4301 | 61.3776 | 61.4016 | 61.4206 | 61.4544 | 61.4305 | 61.4562 | 122.9507 | 61.5981 | 122.8773 | 61.3622 | 61.4298 | 122.9431 | 61.4213 | 122.7167 | 61.5209 | 61.5294 | 61.4476 | 61.4561
834.8906 | 123.2941 | -61.4319 | 61.5372 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.028846 | 61.5279 | 0.18911 | 61.4592 | -0.055996 | 0.020767 | 61.5341 | 0.003143 | 61.3169 | 61.4484 | 61.3959 | 61.4199 | 61.4343 | 61.4682 | 61.4442 | 61.4607 | 122.9598 | 61.621 | 122.8911 | 61.3759 | 61.4527 | 122.966 | 61.435 | 122.7488 | 61.5072 | 61.5248 | 61.4384 | 61.4561
835.8906 | 123.2758 | -61.441 | 61.528 | 0.021127 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5325 | 0.18453 | 61.4638 | -0.051417 | 0.01161 | 61.5341 | 0.007721 | 61.3031 | 61.4622 | 61.4051 | 61.4336 | 61.4435 | 61.4727 | 61.4534 | 61.4699 | 122.9736 | 61.6256 | 122.9048 | 61.3896 | 61.4526 | 122.9752 | 61.4488 | 122.7442 | 61.5209 | 61.5248 | 61.4522 | 61.4561
836.8906 | 123.262 | -61.4182 | 61.528 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.012329 | 0.038003 | 61.5279 | 0.17995 | 61.4592 | -0.046838 | 0.016188 | 61.5341 | 0.007721 | 61.3077 | 61.4347 | 61.3776 | 61.4016 | 61.4252 | 61.4453 | 61.4305 | 61.4562 | 122.9461 | 61.5981 | 122.8773 | 61.3713 | 61.4343 | 122.9523 | 61.4259 | 122.7259 | 61.5118 | 61.5202 | 61.443 | 61.4515
837.8906 | 123.3078 | -61.4365 | 61.5463 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.00775 | 0.024268 | 61.5371 | 0.18911 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | 0.007721 | 61.3077 | 61.453 | 61.4005 | 61.4245 | 61.4389 | 61.4681 | 61.4442 | 61.4607 | 122.9736 | 61.6256 | 122.9048 | 61.385 | 61.4572 | 122.9706 | 61.4442 | 122.7442 | 61.5163 | 61.5294 | 61.4476 | 61.4606
838.8906 | 123.2529 | -61.441 | 61.5417 | 0.016548 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | 0.00775 | 0.033424 | 61.5417 | 0.18453 | 61.4684 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.3123 | 61.4576 | 61.4097 | 61.4336 | 61.4527 | 61.4727 | 61.4488 | 61.4745 | 122.9827 | 61.6256 | 122.9094 | 61.385 | 61.4618 | 122.966 | 61.4533 | 122.7533 | 61.5209 | 61.5294 | 61.4476 | 61.4561
839.8906 | 123.3215 | -61.409 | 61.5372 | 0.01197 | -0.035942 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.046838 | 0.016188 | 61.5341 | 0.016878 | 61.3123 | 61.421 | 61.3731 | 61.3924 | 61.4115 | 61.4361 | 61.4259 | 61.4424 | 122.9415 | 61.5981 | 122.8728 | 61.3622 | 61.4252 | 122.9431 | 61.4259 | 122.7213 | 61.5163 | 61.5156 | 61.4476 | 61.4469
840.8906 | 123.3078 | -61.4136 | 61.5417 | 0.01197 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.028846 | 61.5371 | 0.18911 | 61.4592 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3077 | 61.4255 | 61.3731 | 61.397 | 61.4206 | 61.4407 | 61.4213 | 61.4424 | 122.9507 | 61.6027 | 122.8728 | 61.3576 | 61.4343 | 122.9431 | 61.4213 | 122.7213 | 61.5163 | 61.5294 | 61.4384 | 61.4515
841.8906 | 123.2437 | -61.4456 | 61.5372 | 0.021127 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.038003 | 61.5325 | 0.18911 | 61.4592 | -0.046838 | 0.020767 | 61.5341 | 0.012299 | 61.3031 | 61.4667 | 61.4005 | 61.4336 | 61.4481 | 61.4819 | 61.4579 | 61.4836 | 122.9781 | 61.6347 | 122.9048 | 61.3988 | 61.4664 | 122.9797 | 61.4579 | 122.7488 | 61.5118 | 61.5202 | 61.4384 | 61.4469
842.8906 | 123.2758 | -61.4136 | 61.5234 | 0.021127 | -0.040521 | -0.016578 | 0.002454 | 0.027109 | 0.016907 | 0.028846 | 61.5325 | 0.18911 | 61.4638 | -0.055996 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.4347 | 61.3731 | 61.397 | 61.416 | 61.4407 | 61.4305 | 61.4424 | 122.9461 | 61.6027 | 122.8773 | 61.3576 | 61.4343 | 122.9431 | 61.4121 | 122.7259 | 61.5118 | 61.534 | 61.443 | 61.4652
843.8906 | 123.2254 | -61.4319 | 61.5143 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.028846 | 61.5325 | 0.18453 | 61.4638 | -0.055996 | 0.016188 | 61.5387 | 0.007721 | 61.3123 | 61.453 | 61.3959 | 61.4199 | 61.4389 | 61.4636 | 61.4396 | 61.4607 | 122.9644 | 61.6164 | 122.8957 | 61.3759 | 61.4481 | 122.9706 | 61.4396 | 122.7442 | 61.5163 | 61.5248 | 61.4476 | 61.4561
844.8906 | 123.2895 | -61.4319 | 61.5143 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.027109 | 0.016907 | 0.038003 | 61.5325 | 0.18911 | 61.4638 | -0.046838 | 0.020767 | 61.5341 | 0.007721 | 61.3077 | 61.453 | 61.3959 | 61.4199 | 61.4389 | 61.459 | 61.4488 | 61.4699 | 122.9644 | 61.621 | 122.8957 | 61.385 | 61.4527 | 122.966 | 61.4396 | 122.7396 | 61.5118 | 61.5248 | 61.443 | 61.4561
845.8906 | 123.3353 | -61.4136 | 61.5372 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.00775 | 0.033424 | 61.5371 | 0.19827 | 61.4684 | -0.051417 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4301 | 61.3731 | 61.397 | 61.4206 | 61.4498 | 61.4213 | 61.447 | 122.9507 | 61.6118 | 122.8819 | 61.3622 | 61.4343 | 122.9431 | 61.4213 | 122.7259 | 61.5163 | 61.5294 | 61.4476 | 61.4606
846.8906 | 123.2529 | -61.4502 | 61.5417 | 0.016548 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.016907 | 0.033424 | 61.5325 | 0.18453 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | 0.021456 | 61.3031 | 61.4667 | 61.4143 | 61.4428 | 61.4572 | 61.4865 | 61.4671 | 61.4836 | 122.9827 | 61.6347 | 122.914 | 61.3988 | 61.471 | 122.9797 | 61.4717 | 122.7533 | 61.5118 | 61.5111 | 61.443 | 61.4423
847.8906 | 123.2803 | -61.4365 | 61.5417 | 0.021127 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | 0.00775 | 0.028846 | 61.5371 | 0.18911 | 61.4592 | -0.055996 | 0.016188 | 61.5341 | 0.007721 | 61.3123 | 61.4576 | 61.4051 | 61.429 | 61.4481 | 61.4681 | 61.4442 | 61.4653 | 122.9736 | 61.6256 | 122.8957 | 61.3805 | 61.4526 | 122.9706 | 61.4442 | 122.7488 | 61.5209 | 61.5294 | 61.443 | 61.4515
848.8906 | 123.2712 | -61.4227 | 61.5784 | 0.021127 | -0.040521 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.024268 | 61.5371 | 0.18453 | 61.4592 | -0.051417 | 0.020767 | 61.5341 | 0.012299 | 61.3123 | 61.4439 | 61.3822 | 61.4107 | 61.4343 | 61.4636 | 61.4305 | 61.447 | 122.9598 | 61.6073 | 122.8819 | 61.3713 | 61.4435 | 122.9568 | 61.435 | 122.735 | 61.5163 | 61.5248 | 61.4384 | 61.4469
849.8906 | 123.2895 | -61.4182 | 61.5738 | 0.016548 | -0.040521 | -0.007421 | 0.007033 | 0.031687 | 0.012329 | 0.038003 | 61.5279 | 0.18453 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | 0.012299 | 61.3123 | 61.4347 | 61.3776 | 61.4107 | 61.4252 | 61.4498 | 61.4305 | 61.4562 | 122.9461 | 61.6027 | 122.8819 | 61.3667 | 61.4389 | 122.9477 | 61.4305 | 122.7305 | 61.5072 | 61.5156 | 61.443 | 61.4515
850.8906 | 123.2025 | -61.4502 | 61.5555 | 0.016548 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.016907 | 0.033424 | 61.5371 | 0.18911 | 61.4638 | -0.055996 | 0.020767 | 61.5295 | 0.012299 | 61.3077 | 61.4667 | 61.4143 | 61.4336 | 61.4572 | 61.4819 | 61.4671 | 61.4836 | 122.9873 | 61.6393 | 122.914 | 61.3942 | 61.471 | 122.9797 | 61.4625 | 122.7579 | 61.5163 | 61.5248 | 61.443 | 61.4515
851.8906 | 123.2483 | -61.4594 | 61.5601 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.027109 | 0.016907 | 0.033424 | 61.5279 | 0.18453 | 61.4592 | -0.055996 | 0.020767 | 61.525 | 0.012299 | 61.3031 | 61.4759 | 61.4188 | 61.4474 | 61.4664 | 61.4865 | 61.4763 | 61.4928 | 122.9873 | 61.6439 | 122.9185 | 61.4034 | 61.4801 | 122.9843 | 61.4716 | 122.7625 | 61.5072 | 61.5156 | 61.4384 | 61.4469
852.8906 | 123.2986 | -61.4548 | 61.5509 | 0.01197 | -0.0451 | -0.007421 | 0.002454 | 0.036265 | 0.00775 | 0.024268 | 61.5325 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5204 | 0.016878 | 61.3123 | 61.4667 | 61.4097 | 61.4474 | 61.4572 | 61.491 | 61.4625 | 61.479 | 122.9873 | 61.6439 | 122.9185 | 61.4034 | 61.4755 | 122.9752 | 61.4717 | 122.7671 | 61.5118 | 61.5156 | 61.443 | 61.4469
853.8906 | 123.317 | -61.4319 | 61.5738 | 0.01197 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | 0.016907 | 0.028846 | 61.5279 | 0.18453 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | 0.016878 | 61.3123 | 61.4439 | 61.3914 | 61.4245 | 61.4389 | 61.4682 | 61.4488 | 61.4607 | 122.9598 | 61.6164 | 122.8957 | 61.3805 | 61.4527 | 122.9614 | 61.4488 | 122.7442 | 61.5072 | 61.5111 | 61.443 | 61.4469
854.8906 | 123.3353 | -61.4136 | 61.5646 | 0.007391 | -0.035942 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.060575 | 0.020767 | 61.5295 | 0.016878 | 61.326 | 61.421 | 61.3776 | 61.4062 | 61.416 | 61.4407 | 61.4259 | 61.447 | 122.9461 | 61.6027 | 122.8773 | 61.353 | 61.4343 | 122.9431 | 61.4305 | 122.7396 | 61.5118 | 61.5156 | 61.443 | 61.4469
855.8906 | 123.3215 | -61.4273 | 61.5601 | 0.01197 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.5371 | 0.17995 | 61.4684 | -0.051417 | 0.025345 | 61.5295 | 0.007721 | 61.3123 | 61.4393 | 61.3868 | 61.4199 | 61.4298 | 61.4544 | 61.4351 | 61.4607 | 122.9644 | 61.6073 | 122.8957 | 61.3759 | 61.4527 | 122.9568 | 61.435 | 122.7396 | 61.5118 | 61.5294 | 61.443 | 61.4606
856.8906 | 123.3444 | -61.4227 | 61.5601 | 0.016548 | -0.035942 | -0.012 | 0.007033 | 0.027109 | 0.012329 | 0.033424 | 61.5325 | 0.18453 | 61.4638 | -0.055996 | 0.025345 | 61.525 | 0.012299 | 61.3031 | 61.4393 | 61.3868 | 61.4107 | 61.4298 | 61.4498 | 61.4351 | 61.4562 | 122.9553 | 61.6073 | 122.8865 | 61.3667 | 61.4481 | 122.9477 | 61.435 | 122.7259 | 61.5072 | 61.5202 | 61.4384 | 61.4515
857.8906 | 123.262 | -61.441 | 61.5372 | 0.007391 | -0.040521 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.033424 | 61.5371 | 0.18911 | 61.4592 | -0.055996 | 0.020767 | 61.5341 | 0.016878 | 61.3077 | 61.4484 | 61.4005 | 61.4336 | 61.4481 | 61.4773 | 61.4534 | 61.4745 | 122.9781 | 61.6301 | 122.9002 | 61.385 | 61.4618 | 122.9752 | 61.4579 | 122.7488 | 61.5163 | 61.5202 | 61.4384 | 61.4423
858.8906 | 123.2712 | -61.4136 | 61.5646 | 0.016548 | -0.031363 | -0.007421 | 0.007033 | 0.027109 | 0.00775 | 0.033424 | 61.5371 | 0.18453 | 61.4729 | -0.055996 | 0.029923 | 61.5295 | 0.012299 | 61.3169 | 61.4301 | 61.3822 | 61.4062 | 61.4206 | 61.4407 | 61.4213 | 61.447 | 122.9507 | 61.5981 | 122.8865 | 61.3576 | 61.4435 | 122.9431 | 61.4259 | 122.7305 | 61.5072 | 61.5248 | 61.443 | 61.4606
859.8906 | 123.2803 | -61.4319 | 61.6013 | 0.01197 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.012329 | 0.042581 | 61.5417 | 0.19369 | 61.4638 | -0.051417 | 0.025345 | 61.525 | 0.012299 | 61.3123 | 61.4439 | 61.3914 | 61.4245 | 61.4343 | 61.459 | 61.4442 | 61.4745 | 122.9736 | 61.6256 | 122.8957 | 61.3805 | 61.4572 | 122.9568 | 61.4442 | 122.7442 | 61.5163 | 61.5294 | 61.4384 | 61.4515
860.8906 | 123.1842 | -61.4227 | 61.5875 | 0.021127 | -0.040521 | -0.012 | 0.01619 | 0.036265 | 0.016907 | 0.038003 | 61.5279 | 0.19827 | 61.4638 | -0.055996 | 0.029923 | 61.5387 | 0.007721 | 61.3123 | 61.4439 | 61.3822 | 61.4107 | 61.4389 | 61.459 | 61.4396 | 61.4607 | 122.9507 | 61.621 | 122.8865 | 61.3667 | 61.4527 | 122.9614 | 61.4304 | 122.735 | 61.498 | 61.5202 | 61.4339 | 61.4561
861.8906 | 123.1934 | -61.4502 | 61.6287 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | 0.012329 | 0.038003 | 61.5371 | 0.17537 | 61.4684 | -0.051417 | 0.020767 | 61.525 | 0.003143 | 61.3077 | 61.4622 | 61.4188 | 61.4428 | 61.4618 | 61.4819 | 61.4625 | 61.4882 | 122.9873 | 61.6256 | 122.9185 | 61.3988 | 61.471 | 122.9752 | 61.4533 | 122.7579 | 61.5163 | 61.534 | 61.4476 | 61.4652
862.8906 | 123.1979 | -61.4548 | 61.647 | 0.01197 | -0.040521 | -0.007421 | 0.011611 | 0.031687 | 0.016907 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3215 | 61.4667 | 61.4143 | 61.4474 | 61.4664 | 61.4865 | 61.4717 | 61.4882 | 122.9873 | 61.6439 | 122.9185 | 61.4034 | 61.4755 | 122.9889 | 61.4533 | 122.7762 | 61.5118 | 61.534 | 61.443 | 61.4652
863.8906 | 123.1659 | -61.4456 | 61.6196 | 0.016548 | -0.040521 | -0.007421 | 0.002454 | 0.027109 | 0.016907 | 0.038003 | 61.5279 | 0.17995 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3169 | 61.4622 | 61.4051 | 61.4382 | 61.4481 | 61.4727 | 61.4625 | 61.4836 | 122.9736 | 61.6256 | 122.9094 | 61.3942 | 61.4664 | 122.9752 | 61.4442 | 122.7625 | 61.5072 | 61.5294 | 61.443 | 61.4652
864.8906 | 123.1842 | -61.4456 | 61.6287 | 0.007391 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.033424 | 61.5325 | 0.18911 | 61.4684 | -0.051417 | 0.025345 | 61.525 | -0.001436 | 61.3123 | 61.453 | 61.4097 | 61.4336 | 61.4527 | 61.4819 | 61.4579 | 61.479 | 122.9781 | 61.6347 | 122.914 | 61.3942 | 61.471 | 122.9706 | 61.4442 | 122.7579 | 61.5072 | 61.534 | 61.443 | 61.4698
865.8906 | 123.2071 | -61.4273 | 61.615 | 0.016548 | -0.035942 | -0.002842 | 0.007033 | 0.031687 | 0.016907 | 0.033424 | 61.5325 | 0.18911 | 61.4592 | -0.055996 | 0.016188 | 61.5295 | -0.010593 | 61.3169 | 61.4439 | 61.3914 | 61.4245 | 61.4343 | 61.459 | 61.4442 | 61.4607 | 122.9598 | 61.6164 | 122.8865 | 61.3713 | 61.4435 | 122.9568 | 61.4167 | 122.7442 | 61.5163 | 61.5431 | 61.443 | 61.4698
866.8906 | 123.1842 | -61.4685 | 61.6379 | 0.01197 | -0.035942 | -0.012 | 0.011611 | 0.036265 | 0.016907 | 0.033424 | 61.5279 | 0.17995 | 61.4592 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3169 | 61.4805 | 61.4326 | 61.4565 | 61.4801 | 61.5048 | 61.4854 | 61.5019 | 122.9964 | 61.6485 | 122.9277 | 61.4217 | 61.4893 | 123.0026 | 61.4671 | 122.7854 | 61.5072 | 61.5294 | 61.4384 | 61.4606
867.8906 | 123.2025 | -61.4456 | 61.6058 | 0.016548 | -0.035942 | -0.007421 | 0.007033 | 0.031687 | 0.016907 | 0.033424 | 61.5325 | 0.18453 | 61.4592 | -0.046838 | 0.025345 | 61.5341 | 0.003143 | 61.3123 | 61.4622 | 61.4097 | 61.4382 | 61.4527 | 61.4773 | 61.4625 | 61.479 | 122.9781 | 61.6301 | 122.9048 | 61.3988 | 61.471 | 122.9797 | 61.4488 | 122.7579 | 61.5072 | 61.5294 | 61.4339 | 61.4561
868.8906 | 123.2025 | -61.4182 | 61.5967 | 0.01197 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.003172 | 0.028846 | 61.5371 | 0.18453 | 61.4592 | -0.042259 | 0.020767 | 61.5387 | -0.006014 | 61.3306 | 61.4301 | 61.3868 | 61.4062 | 61.4252 | 61.4498 | 61.4213 | 61.447 | 122.9553 | 61.6027 | 122.8773 | 61.3759 | 61.4389 | 122.9568 | 61.4121 | 122.7488 | 61.5163 | 61.5431 | 61.4384 | 61.4652
869.8906 | 123.2483 | -61.4365 | 61.6104 | 0.021127 | -0.035942 | -0.012 | 0.01619 | 0.040843 | 0.016907 | 0.038003 | 61.5279 | 0.17995 | 61.4592 | -0.055996 | 0.016188 | 61.5341 | -0.001436 | 61.3169 | 61.4576 | 61.4005 | 61.4245 | 61.4527 | 61.4773 | 61.4534 | 61.4745 | 122.9644 | 61.6164 | 122.8957 | 61.3805 | 61.4526 | 122.9706 | 61.435 | 122.7533 | 61.5118 | 61.5294 | 61.443 | 61.4606
870.8906 | 123.2071 | -61.441 | 61.5967 | 0.016548 | -0.040521 | -0.012 | 0.01619 | 0.027109 | 0.021485 | 0.028846 | 61.5325 | 0.18911 | 61.4684 | -0.051417 | 0.016188 | 61.5295 | -0.001436 | 61.3215 | 61.4576 | 61.4005 | 61.429 | 61.4572 | 61.4681 | 61.4625 | 61.4699 | 122.9736 | 61.6301 | 122.9094 | 61.3896 | 61.4572 | 122.9706 | 61.4396 | 122.7625 | 61.5163 | 61.534 | 61.4522 | 61.4698
871.8906 | 123.1888 | -61.4456 | 61.5875 | 0.025705 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.038003 | 61.5325 | 0.18911 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3077 | 61.4713 | 61.4143 | 61.4336 | 61.4572 | 61.4819 | 61.4579 | 61.4836 | 122.9781 | 61.6347 | 122.914 | 61.3942 | 61.4664 | 122.9797 | 61.4396 | 122.7533 | 61.5118 | 61.5385 | 61.4476 | 61.4744
872.8906 | 123.2254 | -61.4273 | 61.5921 | 0.016548 | -0.040521 | -0.007421 | 0.011611 | 0.031687 | 0.012329 | 0.038003 | 61.5279 | 0.18453 | 61.4592 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3215 | 61.4439 | 61.3868 | 61.4199 | 61.4389 | 61.459 | 61.4396 | 61.4653 | 122.9553 | 61.6118 | 122.8865 | 61.3759 | 61.4481 | 122.9614 | 61.4213 | 122.7488 | 61.5072 | 61.534 | 61.4384 | 61.4652
873.8906 | 123.2071 | -61.4365 | 61.6058 | 0.01197 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.012329 | 0.038003 | 61.5325 | 0.18453 | 61.4638 | -0.055996 | 0.025345 | 61.5341 | -0.001436 | 61.3306 | 61.4484 | 61.4005 | 61.4199 | 61.4389 | 61.4727 | 61.4488 | 61.4745 | 122.969 | 61.621 | 122.9002 | 61.3805 | 61.4618 | 122.9706 | 61.435 | 122.7671 | 61.5072 | 61.534 | 61.4384 | 61.4652
874.8906 | 123.2071 | -61.4548 | 61.5921 | 0.016548 | -0.035942 | -0.016578 | 0.01619 | 0.036265 | 0.016907 | 0.038003 | 61.5325 | 0.18911 | 61.4638 | -0.046838 | 0.016188 | 61.5387 | -0.001436 | 61.3169 | 61.4713 | 61.4188 | 61.4382 | 61.471 | 61.491 | 61.4717 | 61.4928 | 122.9873 | 61.6439 | 122.9185 | 61.4079 | 61.471 | 122.9935 | 61.4533 | 122.7717 | 61.5163 | 61.534 | 61.4476 | 61.4652
875.8906 | 123.1384 | -61.4639 | 61.5829 | 0.016548 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.016907 | 0.038003 | 61.5279 | 0.19369 | 61.4592 | -0.055996 | 0.016188 | 61.5295 | -0.001436 | 61.3215 | 61.4805 | 61.4326 | 61.4519 | 61.471 | 61.4956 | 61.4808 | 61.5019 | 122.9919 | 61.6576 | 122.9231 | 61.4079 | 61.4801 | 122.9935 | 61.4625 | 122.7854 | 61.5118 | 61.5294 | 61.443 | 61.4606
876.8906 | 123.143 | -61.4868 | 61.5829 | 0.016548 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.021485 | 0.038003 | 61.5371 | 0.18911 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3123 | 61.5034 | 61.4509 | 61.4794 | 61.4984 | 61.5277 | 61.5083 | 61.5248 | 123.0239 | 61.6759 | 122.9552 | 61.4354 | 61.5076 | 123.0209 | 61.4854 | 122.7991 | 61.5163 | 61.5385 | 61.4476 | 61.4698
877.8906 | 123.1934 | -61.4594 | 61.5829 | 0.01197 | -0.035942 | -0.007421 | 0.01619 | 0.036265 | 0.016907 | 0.038003 | 61.5279 | 0.19369 | 61.4638 | -0.042259 | 0.016188 | 61.5341 | -0.001436 | 61.3169 | 61.4713 | 61.4234 | 61.4519 | 61.4755 | 61.4956 | 61.4763 | 61.4974 | 122.9873 | 61.653 | 122.9231 | 61.4171 | 61.4755 | 122.9935 | 61.4579 | 122.7762 | 61.5118 | 61.5294 | 61.4476 | 61.4652
878.8906 | 123.1522 | -61.4731 | 61.6013 | 0.016548 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.033424 | 61.5279 | 0.18911 | 61.4684 | -0.055996 | 0.025345 | 61.5295 | 0.003143 | 61.3077 | 61.4896 | 61.4417 | 61.4611 | 61.4847 | 61.5093 | 61.4854 | 61.5065 | 123.001 | 61.6622 | 122.9414 | 61.4171 | 61.4984 | 123.0026 | 61.4762 | 122.7808 | 61.5026 | 61.5248 | 61.443 | 61.4652
879.8906 | 123.2071 | -61.4594 | 61.5601 | 0.007391 | -0.031363 | -0.012 | 0.011611 | 0.040843 | 0.016907 | 0.033424 | 61.5417 | 0.18911 | 61.4638 | -0.051417 | 0.016188 | 61.5295 | -0.006014 | 61.3123 | 61.4667 | 61.428 | 61.4474 | 61.471 | 61.5002 | 61.4763 | 61.4928 | 123.001 | 61.6485 | 122.9231 | 61.4079 | 61.4755 | 122.9889 | 61.4533 | 122.7717 | 61.5255 | 61.5477 | 61.4476 | 61.4698
880.8906 | 123.1979 | -61.4639 | 61.5829 | 0.021127 | -0.022205 | -0.012 | 0.007033 | 0.040843 | 0.012329 | 0.042581 | 61.5279 | 0.18911 | 61.4592 | -0.051417 | 0.020767 | 61.5295 | -0.010593 | 61.3169 | 61.4851 | 61.4417 | 61.4519 | 61.471 | 61.5048 | 61.4763 | 61.5065 | 122.9919 | 61.653 | 122.9231 | 61.4125 | 61.4847 | 122.9935 | 61.4533 | 122.7808 | 61.5072 | 61.5385 | 61.4384 | 61.4698
881.8906 | 123.317 | -61.4502 | 61.5463 | 0.007391 | -0.0451 | -0.002842 | 0.01619 | 0.040843 | 0.003172 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3123 | 61.4576 | 61.4051 | 61.4474 | 61.4664 | 61.491 | 61.4534 | 61.4836 | 122.9827 | 61.6393 | 122.914 | 61.3988 | 61.471 | 122.9843 | 61.4488 | 122.7625 | 61.5118 | 61.534 | 61.443 | 61.4652
882.8906 | 123.3032 | -61.4273 | 61.5417 | 0.01197 | -0.040521 | -0.016578 | 0.002454 | 0.036265 | 0.016907 | 0.033424 | 61.5325 | 0.19369 | 61.4638 | -0.055996 | 0.016188 | 61.5341 | -0.006014 | 61.3169 | 61.4393 | 61.3868 | 61.4107 | 61.4298 | 61.4636 | 61.4442 | 61.4607 | 122.9598 | 61.621 | 122.8911 | 61.3713 | 61.4435 | 122.9614 | 61.4213 | 122.7442 | 61.5163 | 61.5385 | 61.4476 | 61.4698
883.8906 | 123.2986 | -61.441 | 61.5463 | 0.016548 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.021485 | 0.038003 | 61.5371 | 0.19369 | 61.4592 | -0.055996 | 0.016188 | 61.5387 | -0.001436 | 61.3123 | 61.4576 | 61.4097 | 61.429 | 61.4481 | 61.4773 | 61.4625 | 61.479 | 122.9781 | 61.6347 | 122.9002 | 61.385 | 61.4572 | 122.9797 | 61.4396 | 122.7533 | 61.5209 | 61.5385 | 61.443 | 61.4606
884.8906 | 123.2941 | -61.4273 | 61.5463 | 0.01197 | -0.026784 | -0.012 | 0.007033 | 0.027109 | 0.012329 | 0.038003 | 61.5325 | 0.18453 | 61.4592 | -0.051417 | 0.020767 | 61.5387 | -0.006014 | 61.3123 | 61.4393 | 61.4005 | 61.4153 | 61.4343 | 61.4544 | 61.4396 | 61.4653 | 122.9598 | 61.6118 | 122.8865 | 61.3759 | 61.4481 | 122.966 | 61.4213 | 122.7396 | 61.5118 | 61.5385 | 61.4384 | 61.4652
885.8906 | 123.2208 | -61.441 | 61.5372 | 0.016548 | -0.035942 | -0.012 | 0.01619 | 0.036265 | 0.012329 | 0.033424 | 61.5279 | 0.19369 | 61.4592 | -0.046838 | 0.016188 | 61.5295 | -0.006014 | 61.3123 | 61.4576 | 61.4051 | 61.429 | 61.4572 | 61.4773 | 61.4534 | 61.4745 | 122.969 | 61.6347 | 122.9002 | 61.3942 | 61.4572 | 122.9706 | 61.435 | 122.7533 | 61.5118 | 61.534 | 61.443 | 61.4652
886.8906 | 123.2712 | -61.409 | 61.5463 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.016907 | 0.033424 | 61.5234 | 0.18911 | 61.4638 | -0.046838 | 0.016188 | 61.5387 | -0.001436 | 61.3123 | 61.4255 | 61.3685 | 61.3924 | 61.416 | 61.4453 | 61.4259 | 61.4424 | 122.9324 | 61.5981 | 122.8728 | 61.3622 | 61.4252 | 122.9477 | 61.4076 | 122.7213 | 61.5072 | 61.5248 | 61.4476 | 61.4652
887.8906 | 123.3353 | -61.4365 | 61.5692 | 0.016548 | -0.035942 | -0.016578 | 0.002454 | 0.036265 | 0.012329 | 0.033424 | 61.5325 | 0.19369 | 61.4546 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.453 | 61.4005 | 61.4199 | 61.4389 | 61.4727 | 61.4488 | 61.4699 | 122.969 | 61.6302 | 122.8911 | 61.385 | 61.4572 | 122.966 | 61.435 | 122.7442 | 61.5118 | 61.534 | 61.4339 | 61.4561
888.8906 | 123.2803 | -61.4273 | 61.5234 | 0.007391 | -0.035942 | -0.007421 | 0.002454 | 0.036265 | 0.003172 | 0.028846 | 61.5371 | 0.19827 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3169 | 61.4347 | 61.3914 | 61.4199 | 61.4298 | 61.4636 | 61.4305 | 61.4562 | 122.9644 | 61.6256 | 122.8911 | 61.3759 | 61.4481 | 122.9568 | 61.4259 | 122.7442 | 61.5163 | 61.5385 | 61.443 | 61.4652
889.8906 | 123.3215 | -61.4227 | 61.5555 | 0.01197 | -0.040521 | -0.016578 | 0.011611 | 0.031687 | 0.012329 | 0.028846 | 61.5234 | 0.19369 | 61.4592 | -0.055996 | 0.025345 | 61.5295 | -0.010593 | 61.3123 | 61.4347 | 61.3822 | 61.4062 | 61.4343 | 61.4544 | 61.4351 | 61.4516 | 122.9461 | 61.6164 | 122.8819 | 61.3667 | 61.4481 | 122.9523 | 61.4121 | 122.735 | 61.498 | 61.534 | 61.4339 | 61.4698
890.8906 | 123.2849 | -61.4182 | 61.5646 | 0.01197 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.021485 | 0.033424 | 61.5325 | 0.18911 | 61.4684 | -0.055996 | 0.020767 | 61.5295 | 0.007721 | 61.3123 | 61.4301 | 61.3868 | 61.4016 | 61.4206 | 61.4498 | 61.4396 | 61.4516 | 122.9507 | 61.6073 | 122.8865 | 61.3622 | 61.4389 | 122.9477 | 61.4259 | 122.7305 | 61.5118 | 61.5248 | 61.4476 | 61.4606
891.8906 | 123.3307 | -61.4182 | 61.5601 | 0.007391 | -0.035942 | -0.012 | 0.002454 | 0.027109 | 0.012329 | 0.028846 | 61.5325 | 0.19827 | 61.4592 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3169 | 61.4255 | 61.3822 | 61.4062 | 61.4206 | 61.4453 | 61.4305 | 61.447 | 122.9507 | 61.6164 | 122.8773 | 61.3667 | 61.4389 | 122.9523 | 61.4167 | 122.735 | 61.5118 | 61.534 | 61.4384 | 61.4606
892.8906 | 123.3398 | -61.4136 | 61.5738 | 0.007391 | -0.031363 | -0.012 | -0.002124 | 0.036265 | 0.012329 | 0.033424 | 61.5325 | 0.18453 | 61.4684 | -0.060575 | 0.020767 | 61.5341 | -0.001436 | 61.3123 | 61.421 | 61.3822 | 61.4016 | 61.4114 | 61.4498 | 61.4259 | 61.447 | 122.9461 | 61.5981 | 122.8819 | 61.353 | 61.4343 | 122.9477 | 61.4121 | 122.7259 | 61.5118 | 61.534 | 61.4476 | 61.4698
893.8906 | 123.3215 | -61.3998 | 61.5921 | 0.01197 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.033424 | 61.5325 | 0.18453 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3215 | 61.4118 | 61.3593 | 61.3878 | 61.4023 | 61.4315 | 61.4122 | 61.4333 | 122.9324 | 61.5844 | 122.8682 | 61.3484 | 61.4206 | 122.934 | 61.403 | 122.7213 | 61.5118 | 61.5294 | 61.4476 | 61.4652
894.8906 | 123.317 | -61.4227 | 61.5463 | 0.021127 | -0.031363 | -0.007421 | 0.007033 | 0.022531 | 0.00775 | 0.042581 | 61.5325 | 0.18453 | 61.4638 | -0.046838 | 0.029923 | 61.5341 | 0.007721 | 61.3169 | 61.4439 | 61.3914 | 61.4153 | 61.4298 | 61.4453 | 61.4305 | 61.4653 | 122.9553 | 61.6073 | 122.8865 | 61.3759 | 61.4527 | 122.9568 | 61.4304 | 122.7396 | 61.5026 | 61.5248 | 61.4339 | 61.4561
895.8906 | 123.23 | -61.4365 | 61.6241 | 0.01197 | -0.031363 | -0.012 | 0.002454 | 0.036265 | 0.021485 | 0.038003 | 61.5417 | 0.18453 | 61.4592 | -0.051417 | 0.025345 | 61.5433 | 0.007721 | 61.3169 | 61.4484 | 61.4051 | 61.4245 | 61.4389 | 61.4727 | 61.4579 | 61.4745 | 122.9781 | 61.621 | 122.8957 | 61.385 | 61.4618 | 122.9797 | 61.4442 | 122.7533 | 61.5163 | 61.534 | 61.4339 | 61.4515
896.8906 | 123.2437 | -61.3998 | 61.5829 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.031687 | 0.012329 | 0.033424 | 61.5279 | 0.19369 | 61.4546 | -0.051417 | 0.016188 | 61.5341 | -0.010593 | 61.3123 | 61.4164 | 61.3593 | 61.3878 | 61.4069 | 61.4315 | 61.4122 | 61.4333 | 122.9278 | 61.5935 | 122.8545 | 61.3484 | 61.416 | 122.934 | 61.3892 | 122.7121 | 61.5118 | 61.5385 | 61.4384 | 61.4652
897.8906 | 123.1338 | -61.4227 | 61.6104 | 0.016548 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.021485 | 0.038003 | 61.5325 | 0.19827 | 61.4684 | -0.055996 | 0.025345 | 61.5341 | 0.003143 | 61.3169 | 61.4393 | 61.3959 | 61.4107 | 61.4298 | 61.4636 | 61.4442 | 61.4607 | 122.9553 | 61.621 | 122.8911 | 61.3667 | 61.4481 | 122.9568 | 61.4259 | 122.7396 | 61.5072 | 61.5294 | 61.443 | 61.4652
898.8906 | 123.3078 | -61.4456 | 61.528 | 0.01197 | -0.035942 | -0.012 | 0.007033 | 0.040843 | 0.012329 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.055996 | 0.020767 | 61.5341 | 0.003143 | 61.3031 | 61.4576 | 61.4097 | 61.4336 | 61.4527 | 61.4865 | 61.4579 | 61.479 | 122.9781 | 61.6347 | 122.9094 | 61.3896 | 61.4664 | 122.9797 | 61.4488 | 122.7488 | 61.5118 | 61.5294 | 61.443 | 61.4606
899.8906 | 123.2208 | -61.441 | 61.615 | 0.016548 | -0.031363 | -0.012 | 0.007033 | 0.040843 | 0.016907 | 0.033424 | 61.5279 | 0.18453 | 61.4592 | -0.046838 | 0.020767 | 61.5387 | 0.016878 | 61.3123 | 61.4576 | 61.4097 | 61.429 | 61.4481 | 61.4819 | 61.4579 | 61.4745 | 122.969 | 61.6256 | 122.9002 | 61.3942 | 61.4618 | 122.9797 | 61.4579 | 122.7533 | 61.5072 | 61.5111 | 61.4384 | 61.4423
900.8906 | 123.1522 | -61.4731 | 61.5967 | 0.016548 | -0.035942 | -0.016578 | 0.011611 | 0.036265 | 0.012329 | 0.033424 | 61.5371 | 0.18911 | 61.4592 | -0.055996 | 0.025345 | 61.5295 | 0.003143 | 61.3169 | 61.4896 | 61.4371 | 61.4565 | 61.4847 | 61.5093 | 61.4854 | 61.5065 | 123.0102 | 61.6622 | 122.9323 | 61.4171 | 61.4984 | 123.0026 | 61.4762 | 122.79 | 61.5118 | 61.534 | 61.4339 | 61.4561
901.8906 | 123.1659 | -61.4456 | 61.6104 | 0.016548 | -0.031363 | -0.002842 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5417 | 0.19369 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3215 | 61.4622 | 61.4143 | 61.4428 | 61.4527 | 61.4819 | 61.4579 | 61.4836 | 122.9873 | 61.6393 | 122.914 | 61.3942 | 61.4664 | 122.9797 | 61.4396 | 122.7671 | 61.5209 | 61.5477 | 61.4476 | 61.4744
902.8906 | 123.1476 | -61.4594 | 61.6196 | 0.016548 | -0.035942 | -0.007421 | 0.020768 | 0.036265 | 0.00775 | 0.038003 | 61.5325 | 0.18911 | 61.4638 | -0.055996 | 0.020767 | 61.5295 | 0.003143 | 61.3215 | 61.4759 | 61.4234 | 61.4519 | 61.4801 | 61.4956 | 61.4671 | 61.4974 | 122.9919 | 61.6485 | 122.9231 | 61.4034 | 61.4801 | 122.9889 | 61.4625 | 122.7808 | 61.5118 | 61.5294 | 61.443 | 61.4606
903.8906 | 123.1613 | -61.4594 | 61.5921 | 0.016548 | -0.022205 | -0.012 | 0.01619 | 0.036265 | 0.016907 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3077 | 61.4759 | 61.4371 | 61.4474 | 61.4755 | 61.4956 | 61.4763 | 61.4928 | 122.9919 | 61.6485 | 122.9231 | 61.4125 | 61.4847 | 122.9935 | 61.4579 | 122.7671 | 61.5072 | 61.534 | 61.4384 | 61.4652
904.8906 | 123.1796 | -61.4456 | 61.6333 | 0.01197 | -0.035942 | -0.007421 | 0.020768 | 0.031687 | 0.021485 | 0.038003 | 61.5371 | 0.18911 | 61.4684 | -0.055996 | 0.016188 | 61.5387 | -0.001436 | 61.3123 | 61.4576 | 61.4097 | 61.4382 | 61.4664 | 61.4773 | 61.4671 | 61.4836 | 122.9827 | 61.6347 | 122.914 | 61.3896 | 61.4618 | 122.9843 | 61.4442 | 122.7579 | 61.5209 | 61.5385 | 61.4522 | 61.4698
905.8906 | 123.2254 | -61.4456 | 61.6058 | 0.016548 | -0.026784 | -0.007421 | 0.020768 | 0.036265 | 0.012329 | 0.042581 | 61.5417 | 0.18911 | 61.4729 | -0.046838 | 0.020767 | 61.5341 | -0.006014 | 61.3169 | 61.4622 | 61.4188 | 61.4382 | 61.4664 | 61.4819 | 61.4579 | 61.4882 | 122.9873 | 61.6347 | 122.9186 | 61.3988 | 61.4664 | 122.9797 | 61.4396 | 122.7625 | 61.5209 | 61.5477 | 61.4522 | 61.4789
906.8906 | 123.2071 | -61.4456 | 61.6196 | 0.01197 | -0.031363 | -0.016578 | 0.01619 | 0.031687 | 0.016907 | 0.042581 | 61.5371 | 0.18911 | 61.4684 | -0.046838 | 0.020767 | 61.5387 | 0.003143 | 61.3215 | 61.4576 | 61.4143 | 61.429 | 61.4618 | 61.4773 | 61.4625 | 61.4882 | 122.9827 | 61.6347 | 122.914 | 61.3988 | 61.4664 | 122.9843 | 61.4488 | 122.7671 | 61.5163 | 61.534 | 61.4476 | 61.4652
907.8906 | 123.1979 | -61.4273 | 61.5921 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.038003 | 61.5417 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.4439 | 61.3914 | 61.4153 | 61.4298 | 61.4636 | 61.4396 | 61.4653 | 122.969 | 61.6164 | 122.8911 | 61.3759 | 61.4481 | 122.9568 | 61.4259 | 122.735 | 61.5209 | 61.5431 | 61.443 | 61.4652
908.8906 | 123.1705 | -61.4548 | 61.5829 | 0.01197 | -0.031363 | -0.002842 | 0.011611 | 0.036265 | 0.016907 | 0.038003 | 61.5279 | 0.19827 | 61.4638 | -0.051417 | 0.020767 | 61.5341 | -0.010593 | 61.3123 | 61.4667 | 61.4234 | 61.4519 | 61.4664 | 61.491 | 61.4717 | 61.4928 | 122.9827 | 61.653 | 122.9185 | 61.4034 | 61.4755 | 122.9889 | 61.4442 | 122.7671 | 61.5072 | 61.5385 | 61.443 | 61.4744
909.8906 | 123.2437 | -61.4456 | 61.5875 | 0.016548 | -0.035942 | -0.007421 | 0.002454 | 0.036265 | 0.021485 | 0.038003 | 61.5279 | 0.18911 | 61.4592 | -0.051417 | 0.01161 | 61.5295 | 0.007721 | 61.3215 | 61.4622 | 61.4097 | 61.4382 | 61.4481 | 61.4819 | 61.4671 | 61.4836 | 122.9736 | 61.6347 | 122.9048 | 61.3942 | 61.4572 | 122.9752 | 61.4533 | 122.7671 | 61.5163 | 61.5202 | 61.4476 | 61.4515
910.8906 | 123.1842 | -61.4365 | 61.6104 | 0.016548 | -0.031363 | -0.012 | 0.011611 | 0.040843 | 0.016907 | 0.033424 | 61.5371 | 0.18911 | 61.4684 | -0.055996 | 0.016188 | 61.5341 | 0.012299 | 61.3169 | 61.453 | 61.4051 | 61.4245 | 61.4481 | 61.4773 | 61.4534 | 61.4699 | 122.9736 | 61.6256 | 122.9048 | 61.3805 | 61.4526 | 122.9706 | 61.4488 | 122.7533 | 61.5209 | 61.5248 | 61.4522 | 61.4561
911.8906 | 123.2254 | -61.4365 | 61.5784 | 0.007391 | -0.026784 | -0.007421 | 0.01619 | 0.031687 | 0.021485 | 0.042581 | 61.5463 | 0.19369 | 61.4729 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3169 | 61.4439 | 61.4097 | 61.429 | 61.4527 | 61.4681 | 61.4579 | 61.479 | 122.9827 | 61.6302 | 122.9094 | 61.385 | 61.4572 | 122.9706 | 61.4396 | 122.7533 | 61.5255 | 61.5431 | 61.4522 | 61.4698
912.8906 | 123.2483 | -61.4319 | 61.6013 | 0.01197 | -0.035942 | -0.012 | 0.011611 | 0.036265 | 0.021485 | 0.038003 | 61.5325 | 0.19369 | 61.4592 | -0.046838 | 0.020767 | 61.5433 | -0.001436 | 61.3123 | 61.4439 | 61.3959 | 61.4199 | 61.4435 | 61.4682 | 61.4534 | 61.4699 | 122.9644 | 61.6256 | 122.8911 | 61.385 | 61.4527 | 122.9752 | 61.4304 | 122.7442 | 61.5118 | 61.534 | 61.4384 | 61.4606
913.8906 | 123.262 | -61.4319 | 61.5417 | 0.01197 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.016907 | 0.033424 | 61.5325 | 0.19369 | 61.4638 | -0.051417 | 0.020767 | 61.525 | 0.007721 | 61.3169 | 61.4439 | 61.3959 | 61.4199 | 61.4343 | 61.4682 | 61.4488 | 61.4653 | 122.9644 | 61.6256 | 122.8957 | 61.3805 | 61.4527 | 122.9568 | 61.4396 | 122.7488 | 61.5118 | 61.5248 | 61.443 | 61.4561
914.8906 | 123.2712 | -61.441 | 61.615 | 0.01197 | -0.026784 | -0.007421 | 0.011611 | 0.036265 | 0.012329 | 0.042581 | 61.5325 | 0.20284 | 61.4684 | -0.046838 | 0.016188 | 61.5341 | -0.001436 | 61.3169 | 61.453 | 61.4143 | 61.4336 | 61.4527 | 61.4773 | 61.4534 | 61.4836 | 122.9736 | 61.6439 | 122.9094 | 61.3942 | 61.4572 | 122.9752 | 61.4396 | 122.7579 | 61.5163 | 61.534 | 61.4522 | 61.4698
915.8906 | 123.1888 | -61.4456 | 61.5829 | 0.01197 | -0.031363 | -0.016578 | 0.011611 | 0.036265 | 0.016907 | 0.042581 | 61.5371 | 0.19827 | 61.4592 | -0.042259 | 0.020767 | 61.5341 | 0.003143 | 61.3169 | 61.4576 | 61.4143 | 61.429 | 61.4572 | 61.4819 | 61.4625 | 61.4882 | 122.9827 | 61.6439 | 122.9048 | 61.4034 | 61.4664 | 122.9797 | 61.4488 | 122.7625 | 61.5163 | 61.534 | 61.4384 | 61.4561
916.8906 | 123.1979 | -61.4548 | 61.6013 | 0.016548 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.021485 | 0.038003 | 61.5325 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5387 | -0.006014 | 61.3123 | 61.4713 | 61.4234 | 61.4428 | 61.4664 | 61.491 | 61.4763 | 61.4928 | 122.9873 | 61.6439 | 122.9185 | 61.4034 | 61.4755 | 122.9935 | 61.4488 | 122.7671 | 61.5118 | 61.5385 | 61.443 | 61.4698
917.8906 | 123.175 | -61.4456 | 61.5738 | 0.01197 | -0.031363 | -0.002842 | 0.011611 | 0.045421 | 0.016907 | 0.038003 | 61.5417 | 0.19369 | 61.4592 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3123 | 61.4576 | 61.4143 | 61.4428 | 61.4572 | 61.491 | 61.4625 | 61.4836 | 122.9873 | 61.6393 | 122.9048 | 61.3942 | 61.4664 | 122.9797 | 61.4396 | 122.7579 | 61.5209 | 61.5477 | 61.4384 | 61.4652
918.8906 | 123.1613 | -61.4548 | 61.6013 | 0.016548 | -0.031363 | -0.007421 | 0.002454 | 0.031687 | 0.016907 | 0.038003 | 61.5417 | 0.18911 | 61.4638 | -0.051417 | 0.01161 | 61.5341 | -0.006014 | 61.3123 | 61.4713 | 61.4234 | 61.4474 | 61.4572 | 61.4865 | 61.4717 | 61.4928 | 122.9965 | 61.6439 | 122.9185 | 61.4034 | 61.4664 | 122.9889 | 61.4488 | 122.7671 | 61.5301 | 61.5477 | 61.4522 | 61.4698
919.8906 | 123.1522 | -61.4456 | 61.5738 | 0.021127 | -0.026784 | -0.002842 | 0.011611 | 0.045421 | 0.00775 | 0.042581 | 61.5417 | 0.18911 | 61.4638 | -0.055996 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4667 | 61.4188 | 61.4428 | 61.4572 | 61.491 | 61.4534 | 61.4882 | 122.9873 | 61.6347 | 122.9094 | 61.3896 | 61.471 | 122.9797 | 61.4442 | 122.7625 | 61.5163 | 61.5431 | 61.4384 | 61.4652
920.8906 | 123.1567 | -61.4548 | 61.5875 | 0.025705 | -0.031363 | -0.002842 | 0.007033 | 0.036265 | 0.016907 | 0.038003 | 61.5325 | 0.19827 | 61.4684 | -0.055996 | 0.020767 | 61.5387 | -0.006014 | 61.3123 | 61.4805 | 61.4234 | 61.4519 | 61.4618 | 61.491 | 61.4717 | 61.4928 | 122.9873 | 61.653 | 122.9231 | 61.3988 | 61.4755 | 122.9935 | 61.4488 | 122.7671 | 61.5118 | 61.5385 | 61.4476 | 61.4744
921.8906 | 123.1338 | -61.4548 | 61.5555 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.045421 | 0.016907 | 0.042581 | 61.5463 | 0.18911 | 61.4638 | -0.051417 | 0.016188 | 61.5295 | -0.001436 | 61.3169 | 61.4667 | 61.4234 | 61.4474 | 61.4664 | 61.5002 | 61.4717 | 61.4974 | 123.001 | 61.6439 | 122.9185 | 61.4034 | 61.471 | 122.9843 | 61.4533 | 122.7717 | 61.5301 | 61.5477 | 61.4476 | 61.4652
922.8906 | 123.2758 | -61.5005 | 61.6013 | 0.016548 | -0.026784 | -0.007421 | 0.007033 | 0.031687 | 0.012329 | 0.038003 | 61.5371 | 0.19369 | 61.4729 | -0.046838 | 0.020767 | 61.525 | -0.006014 | 61.3169 | 61.5171 | 61.4738 | 61.4931 | 61.5076 | 61.5322 | 61.5129 | 61.5386 | 123.0376 | 61.6942 | 122.9735 | 61.4537 | 61.5213 | 123.0255 | 61.4945 | 122.8174 | 61.5163 | 61.5431 | 61.4522 | 61.4789
923.8906 | 123.2712 | -61.4456 | 61.5234 | 0.016548 | -0.031363 | -0.007421 | 0.002454 | 0.036265 | 0.012329 | 0.033424 | 61.5371 | 0.19827 | 61.4684 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3169 | 61.4622 | 61.4143 | 61.4382 | 61.4481 | 61.4819 | 61.4579 | 61.479 | 122.9827 | 61.6439 | 122.914 | 61.3988 | 61.4664 | 122.9752 | 61.4442 | 122.7625 | 61.5163 | 61.5385 | 61.4476 | 61.4698
924.8906 | 123.23 | -61.4777 | 61.5509 | 0.007391 | -0.035942 | -0.007421 | 0.011611 | 0.036265 | 0.021485 | 0.042581 | 61.5325 | 0.19369 | 61.4592 | -0.055996 | 0.025345 | 61.525 | -0.006014 | 61.3077 | 61.4851 | 61.4417 | 61.4702 | 61.4893 | 61.5139 | 61.4991 | 61.5202 | 123.0102 | 61.6713 | 122.9369 | 61.4217 | 61.503 | 123.0026 | 61.4716 | 122.7854 | 61.5072 | 61.5385 | 61.4339 | 61.4652
925.8906 | 123.2574 | -61.4502 | 61.5417 | 0.016548 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.042581 | 61.5279 | 0.19369 | 61.4638 | -0.055996 | 0.01161 | 61.525 | 0.003143 | 61.3169 | 61.4667 | 61.4188 | 61.4382 | 61.4572 | 61.4865 | 61.4625 | 61.4928 | 122.9781 | 61.6439 | 122.914 | 61.3942 | 61.4618 | 122.9752 | 61.4533 | 122.7671 | 61.5163 | 61.5248 | 61.4522 | 61.4606
926.8906 | 123.23 | -61.4456 | 61.5463 | 0.016548 | -0.026784 | -0.012 | 0.007033 | 0.040843 | 0.021485 | 0.042581 | 61.5325 | 0.19827 | 61.4592 | -0.051417 | 0.016188 | 61.5387 | -0.001436 | 61.3123 | 61.4622 | 61.4188 | 61.4336 | 61.4527 | 61.4865 | 61.4671 | 61.4882 | 122.9781 | 61.6439 | 122.9048 | 61.3942 | 61.4618 | 122.9843 | 61.4442 | 122.7579 | 61.5163 | 61.534 | 61.443 | 61.4606
927.8906 | 123.2803 | -61.4365 | 61.5234 | 0.007391 | -0.031363 | -0.012 | 0.01619 | 0.045421 | 0.016907 | 0.042581 | 61.5325 | 0.19369 | 61.4638 | -0.060575 | 0.020767 | 61.5387 | -0.001436 | 61.3077 | 61.4439 | 61.4051 | 61.4245 | 61.4527 | 61.4819 | 61.4534 | 61.479 | 122.969 | 61.6302 | 122.9002 | 61.3759 | 61.4572 | 122.9752 | 61.435 | 122.7442 | 61.5118 | 61.534 | 61.443 | 61.4652
928.8906 | 123.2803 | -61.4273 | 61.5326 | 0.016548 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.042581 | 61.5325 | 0.18453 | 61.4638 | -0.046838 | 0.020767 | 61.5341 | -0.006014 | 61.3123 | 61.4439 | 61.3914 | 61.4153 | 61.4298 | 61.459 | 61.4396 | 61.4699 | 122.9598 | 61.6118 | 122.8911 | 61.3805 | 61.4481 | 122.9614 | 61.4213 | 122.7396 | 61.5118 | 61.5385 | 61.443 | 61.4698
929.8906 | 123.2712 | -61.4273 | 61.5097 | 0.021127 | -0.031363 | -0.007421 | 0.007033 | 0.040843 | 0.003172 | 0.033424 | 61.5371 | 0.19369 | 61.4684 | -0.051417 | 0.020767 | 61.5295 | -0.006014 | 61.3031 | 61.4484 | 61.3959 | 61.4199 | 61.4343 | 61.4682 | 61.4305 | 61.4607 | 122.9644 | 61.621 | 122.8957 | 61.3759 | 61.4481 | 122.9568 | 61.4213 | 122.7305 | 61.5163 | 61.5431 | 61.4476 | 61.4744
930.8906 | 123.317 | -61.4502 | 61.5143 | 0.01197 | -0.031363 | -0.012 | 0.01619 | 0.036265 | 0.021485 | 0.033424 | 61.5463 | 0.18911 | 61.4592 | -0.051417 | 0.020767 | 61.5387 | -0.001436 | 61.3077 | 61.4622 | 61.4188 | 61.4382 | 61.4664 | 61.4865 | 61.4717 | 61.4836 | 122.9965 | 61.6393 | 122.9094 | 61.3988 | 61.471 | 122.9889 | 61.4488 | 122.7579 | 61.5255 | 61.5477 | 61.4384 | 61.4606
931.8906 | 123.23 | -61.4136 | 61.5463 | 0.016548 | -0.026784 | -0.012 | 0.01619 | 0.040843 | 0.016907 | 0.038003 | 61.5417 | 0.19369 | 61.4638 | -0.046838 | 0.01161 | 61.5341 | 0.003143 | 61.3123 | 61.4301 | 61.3868 | 61.4016 | 61.4298 | 61.4544 | 61.4305 | 61.4516 | 122.9553 | 61.6073 | 122.8773 | 61.3667 | 61.4252 | 122.9477 | 61.4167 | 122.7259 | 61.5301 | 61.5385 | 61.4522 | 61.4606
932.8906 | 123.3124 | -61.4273 | 61.5417 | 0.007391 | -0.040521 | -0.012 | 0.011611 | 0.036265 | 0.016907 | 0.033424 | 61.5279 | 0.19369 | 61.4592 | -0.046838 | 0.025345 | 61.5341 | 0.007721 | 61.3123 | 61.4347 | 61.3868 | 61.4153 | 61.4389 | 61.4636 | 61.4442 | 61.4607 | 122.9553 | 61.621 | 122.8865 | 61.3805 | 61.4527 | 122.9614 | 61.435 | 122.7396 | 61.5026 | 61.5202 | 61.4339 | 61.4515
933.8906 | 123.3078 | -61.4456 | 61.5372 | 0.016548 | -0.031363 | -0.012 | 0.002454 | 0.036265 | 0.016907 | 0.033424 | 61.5463 | 0.18911 | 61.4684 | -0.051417 | 0.01161 | 61.5295 | 0.003143 | 61.3123 | 61.4622 | 61.4143 | 61.4336 | 61.4481 | 61.4819 | 61.4625 | 61.479 | 122.9919 | 61.6347 | 122.914 | 61.3942 | 61.4572 | 122.9752 | 61.4488 | 122.7579 | 61.5346 | 61.5431 | 61.4567 | 61.4652
934.8906 | 123.2574 | -61.4456 | 61.5509 | 0.007391 | -0.035942 | -0.012 | 0.011611 | 0.031687 | 0.016907 | 0.038003 | 61.5417 | 0.19827 | 61.4638 | -0.055996 | 0.025345 | 61.5341 | -0.006014 | 61.3123 | 61.453 | 61.4097 | 61.4336 | 61.4572 | 61.4773 | 61.4625 | 61.4836 | 122.9873 | 61.6439 | 122.9094 | 61.3896 | 61.471 | 122.9797 | 61.4396 | 122.7579 | 61.5163 | 61.5477 | 61.4384 | 61.4698
935.8906 | 123.2849 | -61.441 | 61.528 | 0.01197 | -0.031363 | 0.001736 | 0.011611 | 0.040843 | 0.012329 | 0.042581 | 61.5325 | 0.19827 | 61.4684 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.453 | 61.4097 | 61.4428 | 61.4527 | 61.4819 | 61.4534 | 61.4836 | 122.9736 | 61.6393 | 122.9094 | 61.3942 | 61.4664 | 122.9752 | 61.4396 | 122.7579 | 61.5072 | 61.534 | 61.443 | 61.4698
936.8906 | 123.2346 | -61.4182 | 61.5646 | 0.002813 | -0.031363 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5325 | 0.19369 | 61.4684 | -0.051417 | 0.025345 | 61.5341 | 0.003143 | 61.3123 | 61.421 | 61.3868 | 61.4107 | 61.4252 | 61.4544 | 61.4305 | 61.4562 | 122.9507 | 61.6118 | 122.8865 | 61.3667 | 61.4435 | 122.9523 | 61.4213 | 122.7305 | 61.5072 | 61.5294 | 61.443 | 61.4652
937.8906 | 123.2666 | -61.4319 | 61.5601 | 0.016548 | -0.031363 | 0.001736 | 0.011611 | 0.031687 | 0.016907 | 0.033424 | 61.5279 | 0.18453 | 61.4684 | -0.051417 | 0.020767 | 61.5387 | -0.001436 | 61.3215 | 61.4484 | 61.4005 | 61.4336 | 61.4435 | 61.4636 | 61.4488 | 61.4653 | 122.9598 | 61.6164 | 122.9002 | 61.3805 | 61.4527 | 122.9706 | 61.4304 | 122.7533 | 61.5072 | 61.5294 | 61.4476 | 61.4698
938.8906 | 123.2666 | -61.4639 | 61.5601 | 0.007391 | -0.035942 | -0.016578 | 0.007033 | 0.045421 | 0.00775 | 0.033424 | 61.5325 | 0.18911 | 61.4684 | -0.051417 | 0.016188 | 61.5341 | -0.001436 | 61.3123 | 61.4713 | 61.428 | 61.4474 | 61.471 | 61.5093 | 61.4717 | 61.4974 | 122.9964 | 61.653 | 122.9323 | 61.4125 | 61.4801 | 122.998 | 61.4625 | 122.7762 | 61.5163 | 61.534 | 61.4522 | 61.4698
939.8906 | 123.3078 | -61.4227 | 61.5601 | 0.01197 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.028846 | 61.5371 | 0.19369 | 61.4775 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3077 | 61.4347 | 61.3868 | 61.4107 | 61.4298 | 61.459 | 61.4351 | 61.4516 | 122.9598 | 61.6164 | 122.9002 | 61.3713 | 61.4435 | 122.9568 | 61.4259 | 122.7305 | 61.5163 | 61.534 | 61.4567 | 61.4744
940.8906 | 123.2803 | -61.4319 | 61.5646 | 0.007391 | -0.026784 | -0.016578 | 0.011611 | 0.031687 | 0.003172 | 0.033424 | 61.5279 | 0.19369 | 61.4638 | -0.051417 | 0.016188 | 61.5295 | 0.003143 | 61.3123 | 61.4393 | 61.4051 | 61.4153 | 61.4435 | 61.4636 | 61.4351 | 61.4653 | 122.9598 | 61.6256 | 122.8957 | 61.3805 | 61.4481 | 122.9614 | 61.435 | 122.7442 | 61.5118 | 61.5248 | 61.4476 | 61.4606
941.8906 | 123.2803 | -61.4182 | 61.5692 | 0.007391 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | 0.003172 | 0.038003 | 61.5371 | 0.18911 | 61.4684 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3031 | 61.4255 | 61.3776 | 61.4016 | 61.4298 | 61.4544 | 61.4213 | 61.4562 | 122.9553 | 61.6073 | 122.8865 | 61.3713 | 61.4435 | 122.9523 | 61.4167 | 122.7213 | 61.5118 | 61.5385 | 61.443 | 61.4698
942.8906 | 123.2895 | -61.4273 | 61.5738 | 0.01197 | -0.0451 | -0.016578 | 0.007033 | 0.022531 | 0.012329 | 0.024268 | 61.5325 | 0.18911 | 61.4638 | -0.046838 | 0.025345 | 61.5341 | -0.006014 | 61.3077 | 61.4393 | 61.3822 | 61.4107 | 61.4343 | 61.4498 | 61.4396 | 61.4516 | 122.9598 | 61.6164 | 122.8911 | 61.3805 | 61.4527 | 122.9614 | 61.4213 | 122.735 | 61.5072 | 61.5385 | 61.4384 | 61.4698
943.8906 | 123.2529 | -61.3953 | 61.615 | 0.01197 | -0.035942 | -0.021157 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5463 | 0.19369 | 61.4729 | -0.042259 | 0.020767 | 61.5341 | 0.003143 | 61.3169 | 61.4072 | 61.3593 | 61.3741 | 61.3977 | 61.4224 | 61.403 | 61.4241 | 122.9415 | 61.589 | 122.8682 | 61.353 | 61.416 | 122.9294 | 61.3984 | 122.7121 | 61.5255 | 61.5431 | 61.4522 | 61.4698
944.8906 | 123.3215 | -61.4273 | 61.5692 | 0.016548 | -0.040521 | -0.012 | 0.007033 | 0.022531 | 0.00775 | 0.028846 | 61.5325 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3215 | 61.4439 | 61.3868 | 61.4153 | 61.4343 | 61.4498 | 61.4351 | 61.4562 | 122.9598 | 61.6164 | 122.8911 | 61.3759 | 61.4481 | 122.9614 | 61.4259 | 122.7488 | 61.5118 | 61.534 | 61.443 | 61.4652
945.8906 | 123.2895 | -61.4365 | 61.5875 | 0.016548 | -0.035942 | -0.016578 | 0.011611 | 0.031687 | 0.00775 | 0.033424 | 61.5325 | 0.18911 | 61.4638 | -0.055996 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.453 | 61.4005 | 61.4199 | 61.4481 | 61.4681 | 61.4442 | 61.4699 | 122.969 | 61.6256 | 122.9002 | 61.3805 | 61.4572 | 122.966 | 61.4396 | 122.7488 | 61.5118 | 61.5294 | 61.443 | 61.4606
946.8906 | 123.2758 | -61.4182 | 61.5921 | 0.01197 | -0.040521 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.038003 | 61.5371 | 0.19827 | 61.4729 | -0.046838 | 0.020767 | 61.5295 | -0.006014 | 61.3215 | 61.4301 | 61.3776 | 61.4016 | 61.4252 | 61.4498 | 61.4259 | 61.4562 | 122.9553 | 61.6164 | 122.8911 | 61.3713 | 61.4389 | 122.9477 | 61.4121 | 122.7396 | 61.5163 | 61.5431 | 61.4522 | 61.4789
947.8906 | 123.2025 | -61.4365 | 61.6058 | 0.007391 | -0.0451 | -0.012 | 0.002454 | 0.036265 | 0.012329 | 0.028846 | 61.5371 | 0.18911 | 61.4729 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.326 | 61.4439 | 61.3914 | 61.4245 | 61.4389 | 61.4727 | 61.4488 | 61.4653 | 122.9736 | 61.6256 | 122.9094 | 61.3896 | 61.4572 | 122.966 | 61.435 | 122.7625 | 61.5163 | 61.5385 | 61.4522 | 61.4744
948.8906 | 123.2803 | -61.3953 | 61.6058 | 0.01197 | -0.040521 | -0.021157 | 0.002454 | 0.027109 | 0.00775 | 0.033424 | 61.5371 | 0.18453 | 61.4684 | -0.060575 | 0.025345 | 61.5295 | 0.003143 | 61.3123 | 61.4072 | 61.3547 | 61.3741 | 61.3977 | 61.4224 | 61.403 | 61.4287 | 122.9324 | 61.5798 | 122.8636 | 61.3347 | 61.4206 | 122.9248 | 61.3984 | 122.7076 | 61.5118 | 61.534 | 61.443 | 61.4652
949.8906 | 123.175 | -61.4548 | 61.6241 | 0.01197 | -0.040521 | -0.021157 | 0.007033 | 0.031687 | 0.012329 | 0.033424 | 61.5417 | 0.19827 | 61.4684 | -0.055996 | 0.020767 | 61.5341 | -0.001436 | 61.326 | 61.4667 | 61.4143 | 61.4336 | 61.4618 | 61.4865 | 61.4671 | 61.4882 | 122.9965 | 61.653 | 122.9231 | 61.3988 | 61.4755 | 122.9889 | 61.4533 | 122.7808 | 61.5209 | 61.5431 | 61.4476 | 61.4698
950.8906 | 123.262 | -61.3998 | 61.5738 | 0.007391 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.00775 | 0.024268 | 61.5463 | 0.19369 | 61.4729 | -0.055996 | 0.016188 | 61.5341 | -0.006014 | 61.3123 | 61.4072 | 61.3593 | 61.3878 | 61.4023 | 61.4224 | 61.4076 | 61.4241 | 122.9461 | 61.5935 | 122.8728 | 61.3438 | 61.416 | 122.934 | 61.3938 | 122.7121 | 61.5301 | 61.5523 | 61.4567 | 61.4789
951.8906 | 123.2071 | -61.4502 | 61.6058 | 0.01197 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.00775 | 0.033424 | 61.5417 | 0.18911 | 61.4684 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3169 | 61.4622 | 61.4188 | 61.4382 | 61.4618 | 61.4865 | 61.4579 | 61.4836 | 122.9919 | 61.6393 | 122.9185 | 61.3988 | 61.4755 | 122.9797 | 61.4488 | 122.7671 | 61.5163 | 61.5431 | 61.443 | 61.4698
952.8906 | 123.2346 | -61.4365 | 61.6241 | 0.021127 | -0.031363 | -0.012 | 0.002454 | 0.027109 | 0.016907 | 0.033424 | 61.5417 | 0.19369 | 61.4729 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3215 | 61.4576 | 61.4051 | 61.4245 | 61.4389 | 61.4636 | 61.4534 | 61.4699 | 122.9781 | 61.6302 | 122.9094 | 61.385 | 61.4572 | 122.966 | 61.435 | 122.7579 | 61.5209 | 61.5431 | 61.4522 | 61.4744
953.8906 | 123.2208 | -61.4594 | 61.6104 | 0.016548 | -0.031363 | -0.007421 | 0.002454 | 0.027109 | 0.016907 | 0.038003 | 61.5371 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | -0.006014 | 61.3077 | 61.4759 | 61.428 | 61.4519 | 61.4618 | 61.4865 | 61.4763 | 61.4974 | 122.9965 | 61.6485 | 122.9231 | 61.4079 | 61.4801 | 122.9889 | 61.4533 | 122.7671 | 61.5163 | 61.5431 | 61.443 | 61.4698
954.8906 | 123.1888 | -61.441 | 61.6013 | 0.01197 | -0.031363 | -0.012 | 0.007033 | 0.031687 | 0.00775 | 0.033424 | 61.5463 | 0.18911 | 61.4684 | -0.046838 | 0.029923 | 61.5295 | 0.003143 | 61.3215 | 61.453 | 61.4097 | 61.429 | 61.4481 | 61.4727 | 61.4488 | 61.4745 | 122.9873 | 61.6301 | 122.9094 | 61.3942 | 61.471 | 122.9706 | 61.4442 | 122.7625 | 61.5163 | 61.5431 | 61.4384 | 61.4652
955.8906 | 123.23 | -61.4456 | 61.6058 | 0.01197 | -0.040521 | -0.021157 | 0.011611 | 0.036265 | 0.00775 | 0.033424 | 61.5417 | 0.18911 | 61.4729 | -0.051417 | 0.020767 | 61.5295 | -0.010593 | 61.3215 | 61.4576 | 61.4051 | 61.4245 | 61.4572 | 61.4819 | 61.4534 | 61.479 | 122.9873 | 61.6347 | 122.9186 | 61.3942 | 61.4664 | 122.9752 | 61.435 | 122.7671 | 61.5209 | 61.5523 | 61.4522 | 61.4835
956.8906 | 123.2071 | -61.4319 | 61.6058 | 0.01197 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.033424 | 61.5371 | 0.19369 | 61.4684 | -0.055996 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4439 | 61.3914 | 61.4153 | 61.4389 | 61.459 | 61.4396 | 61.4653 | 122.969 | 61.6256 | 122.9002 | 61.3759 | 61.4572 | 122.966 | 61.4304 | 122.7488 | 61.5118 | 61.5385 | 61.443 | 61.4698
957.8906 | 123.2208 | -61.4227 | 61.615 | 0.007391 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.00775 | 0.028846 | 61.5417 | 0.19369 | 61.4729 | -0.051417 | 0.016188 | 61.5341 | -0.006014 | 61.3123 | 61.4301 | 61.3868 | 61.4062 | 61.4298 | 61.4544 | 61.4305 | 61.4516 | 122.9644 | 61.6164 | 122.8957 | 61.3713 | 61.4389 | 122.9568 | 61.4167 | 122.735 | 61.5255 | 61.5477 | 61.4567 | 61.4789
958.8906 | 123.1796 | -61.4365 | 61.5692 | 0.01197 | -0.0451 | -0.016578 | 0.011611 | 0.036265 | 0.012329 | 0.028846 | 61.5417 | 0.19369 | 61.4775 | -0.051417 | 0.016188 | 61.5295 | -0.006014 | 61.3077 | 61.4484 | 61.3914 | 61.4199 | 61.4481 | 61.4727 | 61.4488 | 61.4653 | 122.9781 | 61.6302 | 122.914 | 61.385 | 61.4526 | 122.966 | 61.4304 | 122.7442 | 61.5255 | 61.5477 | 61.4613 | 61.4835
959.8906 | 123.2162 | -61.4594 | 61.615 | 0.016548 | -0.031363 | -0.016578 | -0.002124 | 0.040843 | 0.012329 | 0.033424 | 61.5417 | 0.19369 | 61.4638 | -0.051417 | 0.020767 | 61.5295 | -0.006014 | 61.3123 | 61.4759 | 61.428 | 61.4428 | 61.4572 | 61.5002 | 61.4717 | 61.4928 | 123.001 | 61.653 | 122.9231 | 61.4079 | 61.4801 | 122.9889 | 61.4533 | 122.7717 | 61.5209 | 61.5477 | 61.443 | 61.4698
960.8906 | 123.2117 | -61.4456 | 61.6013 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.027109 | 0.016907 | 0.038003 | 61.5417 | 0.19369 | 61.4684 | -0.051417 | 0.020767 | 61.5387 | -0.006014 | 61.3215 | 61.4576 | 61.4143 | 61.4382 | 61.4572 | 61.4727 | 61.4625 | 61.4836 | 122.9873 | 61.6393 | 122.914 | 61.3942 | 61.4664 | 122.9843 | 61.4396 | 122.7671 | 61.5209 | 61.5477 | 61.4476 | 61.4744
961.8906 | 123.1659 | -61.4594 | 61.5784 | 0.016548 | -0.026784 | -0.025735 | 0.007033 | 0.036265 | 0.016907 | 0.042581 | 61.5417 | 0.19827 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.4759 | 61.4326 | 61.4336 | 61.4664 | 61.4956 | 61.4763 | 61.5019 | 123.001 | 61.6576 | 122.9369 | 61.4125 | 61.4801 | 122.9889 | 61.4579 | 122.7717 | 61.5209 | 61.5431 | 61.4567 | 61.4789
962.8906 | 123.1705 | -61.4731 | 61.5967 | 0.016548 | -0.0451 | -0.012 | 0.002454 | 0.022531 | 0.012329 | 0.033424 | 61.5325 | 0.19369 | 61.4729 | -0.046838 | 0.020767 | 61.5341 | -0.006014 | 61.3031 | 61.4896 | 61.428 | 61.4611 | 61.4755 | 61.4956 | 61.4854 | 61.5065 | 123.0056 | 61.6668 | 122.946 | 61.4262 | 61.4939 | 123.0072 | 61.4671 | 122.7762 | 61.5118 | 61.5385 | 61.4522 | 61.4789
963.8906 | 123.1613 | -61.4502 | 61.5646 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | 0.012329 | 0.033424 | 61.5325 | 0.19369 | 61.4684 | -0.055996 | 0.029923 | 61.5341 | 0.003143 | 61.3077 | 61.4622 | 61.4188 | 61.4428 | 61.4618 | 61.4819 | 61.4625 | 61.4836 | 122.9827 | 61.6439 | 122.9185 | 61.3942 | 61.4801 | 122.9843 | 61.4533 | 122.7579 | 61.5026 | 61.5294 | 61.4384 | 61.4652
964.8906 | 123.1888 | -61.441 | 61.5692 | 0.016548 | -0.035942 | -0.016578 | 0.007033 | 0.031687 | 0.016907 | 0.028846 | 61.5417 | 0.18911 | 61.4775 | -0.046838 | 0.01161 | 61.5295 | -0.001436 | 61.3123 | 61.4576 | 61.4051 | 61.4245 | 61.4481 | 61.4727 | 61.4579 | 61.4699 | 122.9827 | 61.6301 | 122.9186 | 61.3942 | 61.4526 | 122.9706 | 61.4396 | 122.7533 | 61.5301 | 61.5431 | 61.4659 | 61.4789
965.8906 | 123.1705 | -61.441 | 61.5967 | 0.021127 | -0.040521 | -0.021157 | 0.002454 | 0.031687 | 0.012329 | 0.028846 | 61.5371 | 0.19827 | 61.4729 | -0.055996 | 0.020767 | 61.5295 | -0.006014 | 61.3077 | 61.4622 | 61.4005 | 61.4199 | 61.4435 | 61.4727 | 61.4534 | 61.4699 | 122.9781 | 61.6393 | 122.914 | 61.385 | 61.4618 | 122.9706 | 61.435 | 122.7488 | 61.5163 | 61.5431 | 61.4522 | 61.4789
966.8906 | 123.1613 | -61.4822 | 61.5875 | 0.016548 | -0.040521 | -0.021157 | 0.007033 | 0.031687 | 0.00775 | 0.028846 | 61.5371 | 0.19827 | 61.4638 | -0.051417 | 0.025345 | 61.525 | -0.001436 | 61.3031 | 61.4988 | 61.4417 | 61.4611 | 61.4893 | 61.5139 | 61.49 | 61.5111 | 123.0193 | 61.6805 | 122.946 | 61.4308 | 61.5076 | 123.0072 | 61.4808 | 122.7854 | 61.5118 | 61.5385 | 61.4384 | 61.4652
967.8906 | 123.2162 | -61.4456 | 61.5646 | 0.01197 | -0.040521 | -0.012 | -0.002124 | 0.031687 | 0.00775 | 0.028846 | 61.5417 | 0.19827 | 61.4684 | -0.051417 | 0.020767 | 61.5295 | 0.003143 | 61.3077 | 61.4576 | 61.4051 | 61.4336 | 61.4435 | 61.4773 | 61.4534 | 61.4745 | 122.9873 | 61.6439 | 122.914 | 61.3942 | 61.4664 | 122.9752 | 61.4488 | 122.7533 | 61.5209 | 61.5385 | 61.4476 | 61.4652
968.8906 | 123.175 | -61.4548 | 61.5646 | 0.016548 | -0.031363 | -0.016578 | 0.002454 | 0.031687 | 0.00775 | 0.038003 | 61.5463 | 0.20284 | 61.4775 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.4713 | 61.4234 | 61.4382 | 61.4572 | 61.4865 | 61.4625 | 61.4928 | 123.001 | 61.6576 | 122.9323 | 61.4034 | 61.4801 | 122.9843 | 61.4533 | 122.7625 | 61.5209 | 61.5477 | 61.4522 | 61.4789
969.8906 | 123.2162 | -61.441 | 61.5601 | 0.016548 | -0.040521 | -0.016578 | -0.002124 | 0.031687 | 0.003172 | 0.024268 | 61.5417 | 0.18911 | 61.4729 | -0.051417 | 0.025345 | 61.5387 | -0.001436 | 61.3031 | 61.4576 | 61.4005 | 61.4245 | 61.4389 | 61.4727 | 61.4442 | 61.4653 | 122.9827 | 61.6301 | 122.914 | 61.3896 | 61.4664 | 122.9797 | 61.4396 | 122.7442 | 61.5163 | 61.5431 | 61.4476 | 61.4744
970.8906 | 123.2574 | -61.4502 | 61.528 | 0.01197 | -0.035942 | -0.016578 | 0.007033 | 0.027109 | 0.00775 | 0.028846 | 61.5371 | 0.19369 | 61.4775 | -0.051417 | 0.020767 | 61.525 | -0.006014 | 61.3169 | 61.4622 | 61.4143 | 61.4336 | 61.4572 | 61.4773 | 61.4579 | 61.479 | 122.9873 | 61.6439 | 122.9277 | 61.3988 | 61.471 | 122.9752 | 61.4442 | 122.7671 | 61.5163 | 61.5431 | 61.4567 | 61.4835
971.8906 | 123.23 | -61.4502 | 61.5051 | 0.016548 | -0.040521 | -0.016578 | 0.007033 | 0.036265 | 0.003172 | 0.028846 | 61.5371 | 0.19827 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3169 | 61.4667 | 61.4097 | 61.4336 | 61.4572 | 61.4865 | 61.4534 | 61.479 | 122.9873 | 61.6485 | 122.9185 | 61.3988 | 61.471 | 122.9843 | 61.4533 | 122.7671 | 61.5163 | 61.534 | 61.4476 | 61.4652
972.8906 | 123.3307 | -61.4319 | 61.5463 | 0.01197 | -0.040521 | -0.012 | 0.002454 | 0.022531 | 0.016907 | 0.033424 | 61.5417 | 0.19369 | 61.4684 | -0.046838 | 0.016188 | 61.5341 | -0.010593 | 61.3123 | 61.4439 | 61.3914 | 61.4199 | 61.4343 | 61.4544 | 61.4488 | 61.4653 | 122.9736 | 61.6256 | 122.9002 | 61.385 | 61.4481 | 122.966 | 61.4213 | 122.7442 | 61.5255 | 61.5523 | 61.4522 | 61.4789
973.8906 | 123.3078 | -61.4273 | 61.5372 | 0.01197 | -0.035942 | -0.016578 | -0.002124 | 0.027109 | 0.003172 | 0.033424 | 61.5417 | 0.18911 | 61.4729 | -0.051417 | 0.025345 | 61.5295 | -0.010593 | 61.3123 | 61.4393 | 61.3914 | 61.4107 | 61.4252 | 61.4544 | 61.4305 | 61.4607 | 122.969 | 61.6164 | 122.9002 | 61.3759 | 61.4527 | 122.9568 | 61.4167 | 122.7396 | 61.5163 | 61.5523 | 61.4476 | 61.4835
974.8906 | 123.2803 | -61.4319 | 61.528 | 0.01197 | -0.035942 | -0.025735 | 0.007033 | 0.027109 | 0.016907 | 0.028846 | 61.5371 | 0.19369 | 61.4684 | -0.051417 | 0.020767 | 61.5295 | -0.010593 | 61.3123 | 61.4439 | 61.3959 | 61.4062 | 61.4389 | 61.459 | 61.4488 | 61.4607 | 122.969 | 61.6256 | 122.9002 | 61.3805 | 61.4527 | 122.9614 | 61.4213 | 122.7442 | 61.5163 | 61.5477 | 61.4476 | 61.4789
975.8906 | 123.2986 | -61.4136 | 61.5417 | 0.016548 | -0.040521 | -0.012 | 0.002454 | 0.031687 | 0.003172 | 0.028846 | 61.5325 | 0.18911 | 61.4638 | -0.051417 | 0.016188 | 61.5387 | -0.006014 | 61.3077 | 61.4301 | 61.3731 | 61.4016 | 61.416 | 61.4453 | 61.4167 | 61.4424 | 122.9461 | 61.6027 | 122.8773 | 61.3622 | 61.4298 | 122.9523 | 61.4076 | 122.7213 | 61.5163 | 61.5385 | 61.4476 | 61.4698
976.8906 | 123.23 | -61.4182 | 61.5555 | 0.01197 | -0.035942 | -0.016578 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5371 | 0.18911 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | -0.006014 | 61.3077 | 61.4301 | 61.3822 | 61.4016 | 61.4206 | 61.4407 | 61.4167 | 61.447 | 122.9553 | 61.6073 | 122.8957 | 61.3713 | 61.4389 | 122.9477 | 61.4121 | 122.7259 | 61.5163 | 61.5431 | 61.4567 | 61.4835
977.8906 | 123.2529 | -61.441 | 61.5463 | 0.021127 | -0.040521 | -0.016578 | 0.011611 | 0.036265 | 0.00775 | 0.038003 | 61.5417 | 0.19827 | 61.4684 | -0.055996 | 0.025345 | 61.5387 | -0.001436 | 61.3077 | 61.4622 | 61.4005 | 61.4245 | 61.4527 | 61.4773 | 61.4488 | 61.479 | 122.9827 | 61.6393 | 122.9094 | 61.385 | 61.4664 | 122.9797 | 61.4396 | 122.7488 | 61.5163 | 61.5431 | 61.443 | 61.4698
978.8906 | 123.2483 | -61.4548 | 61.5692 | 0.016548 | -0.035942 | -0.021157 | 0.011611 | 0.022531 | 0.003172 | 0.024268 | 61.5417 | 0.20284 | 61.4729 | -0.060575 | 0.025345 | 61.5295 | 0.003143 | 61.3169 | 61.4713 | 61.4188 | 61.4336 | 61.4664 | 61.4773 | 61.4579 | 61.479 | 122.9965 | 61.6576 | 122.9277 | 61.3942 | 61.4801 | 122.9843 | 61.4579 | 122.7717 | 61.5163 | 61.5385 | 61.4476 | 61.4698
979.8906 | 123.2529 | -61.4319 | 61.5463 | 0.01197 | -0.049678 | -0.016578 | 0.002454 | 0.027109 | 0.00775 | 0.028846 | 61.5417 | 0.20284 | 61.4638 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3031 | 61.4439 | 61.3822 | 61.4153 | 61.4343 | 61.459 | 61.4396 | 61.4607 | 122.9736 | 61.6347 | 122.8957 | 61.385 | 61.4527 | 122.9614 | 61.4304 | 122.735 | 61.5209 | 61.5431 | 61.443 | 61.4652
980.8906 | 123.2803 | -61.4365 | 61.5463 | 0.007391 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.003172 | 0.033424 | 61.5417 | 0.18911 | 61.4638 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3123 | 61.4439 | 61.3959 | 61.4199 | 61.4435 | 61.4636 | 61.4396 | 61.4699 | 122.9781 | 61.6256 | 122.9002 | 61.385 | 61.4572 | 122.9706 | 61.4396 | 122.7488 | 61.5209 | 61.5385 | 61.443 | 61.4606
981.8906 | 123.2483 | -61.4456 | 61.5601 | 0.007391 | -0.040521 | -0.016578 | 0.007033 | 0.027109 | 0.003172 | 0.024268 | 61.5463 | 0.19827 | 61.4729 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3077 | 61.453 | 61.4051 | 61.429 | 61.4527 | 61.4727 | 61.4488 | 61.4699 | 122.9919 | 61.6439 | 122.9186 | 61.3988 | 61.4664 | 122.9797 | 61.4442 | 122.7533 | 61.5255 | 61.5477 | 61.4522 | 61.4744
982.8906 | 123.2712 | -61.4365 | 61.5555 | 0.007391 | -0.040521 | -0.012 | 0.002454 | 0.027109 | 0.003172 | 0.028846 | 61.5508 | 0.18911 | 61.4592 | -0.051417 | 0.025345 | 61.525 | 0.003143 | 61.3169 | 61.4439 | 61.3959 | 61.4245 | 61.4389 | 61.4636 | 61.4396 | 61.4653 | 122.9873 | 61.6256 | 122.8957 | 61.385 | 61.4618 | 122.9614 | 61.4396 | 122.7533 | 61.5255 | 61.5477 | 61.4339 | 61.4561
983.8906 | 123.3078 | -61.4182 | 61.5509 | 0.007391 | -0.0451 | -0.025735 | 0.002454 | 0.027109 | -0.001406 | 0.033424 | 61.5325 | 0.19369 | 61.4684 | -0.055996 | 0.020767 | 61.5341 | 0.003143 | 61.3123 | 61.4255 | 61.3731 | 61.3924 | 61.4206 | 61.4453 | 61.4167 | 61.4516 | 122.9507 | 61.6118 | 122.8865 | 61.3622 | 61.4389 | 122.9523 | 61.4213 | 122.7305 | 61.5118 | 61.5294 | 61.4476 | 61.4652
984.8906 | 123.2712 | -61.4319 | 61.5921 | 0.01197 | -0.031363 | -0.016578 | 0.011611 | 0.027109 | -0.001406 | 0.028846 | 61.5325 | 0.19369 | 61.4638 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4439 | 61.4005 | 61.4153 | 61.4435 | 61.459 | 61.4305 | 61.4607 | 122.9644 | 61.6256 | 122.8957 | 61.385 | 61.4572 | 122.9614 | 61.4304 | 122.7442 | 61.5072 | 61.534 | 61.4384 | 61.4652
985.8906 | 123.3444 | -61.4227 | 61.5601 | 0.007391 | -0.035942 | -0.007421 | 0.01619 | 0.040843 | 0.012329 | 0.042581 | 61.5463 | 0.19369 | 61.4638 | -0.046838 | 0.020767 | 61.5295 | -0.010593 | 61.3123 | 61.4301 | 61.3868 | 61.4153 | 61.4389 | 61.4636 | 61.4351 | 61.4653 | 122.969 | 61.6164 | 122.8865 | 61.3759 | 61.4435 | 122.9523 | 61.4121 | 122.735 | 61.5255 | 61.5568 | 61.443 | 61.4744
986.8906 | 123.2941 | -61.3998 | 61.5646 | 0.007391 | -0.031363 | -0.002842 | 0.01619 | 0.040843 | 0.026064 | 0.042581 | 61.5371 | 0.19369 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3169 | 61.4072 | 61.3685 | 61.397 | 61.416 | 61.4407 | 61.4259 | 61.4424 | 122.9369 | 61.5935 | 122.8682 | 61.3484 | 61.4206 | 122.934 | 61.3938 | 122.7167 | 61.5163 | 61.5431 | 61.4476 | 61.4744
987.8906 | 123.2986 | -61.4182 | 61.5784 | 0.007391 | -0.022205 | -0.002842 | 0.01619 | 0.036265 | 0.021485 | 0.038003 | 61.5371 | 0.19369 | 61.4684 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4255 | 61.3959 | 61.4153 | 61.4343 | 61.4544 | 61.4396 | 61.4562 | 122.9553 | 61.6118 | 122.8865 | 61.3667 | 61.4435 | 122.9477 | 61.4167 | 122.7305 | 61.5118 | 61.5385 | 61.443 | 61.4698
988.8906 | 123.317 | -61.3907 | 61.5738 | 0.01197 | -0.031363 | -0.002842 | 0.01619 | 0.045421 | 0.021485 | 0.042581 | 61.5371 | 0.19369 | 61.4729 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.4027 | 61.3593 | 61.3878 | 61.4069 | 61.4361 | 61.4122 | 61.4333 | 122.9278 | 61.5844 | 122.8636 | 61.3438 | 61.4115 | 122.9202 | 61.3893 | 122.6984 | 61.5163 | 61.5385 | 61.4522 | 61.4744
989.8906 | 123.1934 | -61.4731 | 61.615 | 0.01197 | -0.026784 | 0.001736 | 0.01619 | 0.040843 | 0.021485 | 0.047159 | 61.5417 | 0.20284 | 61.4684 | -0.046838 | 0.025345 | 61.5387 | -0.001436 | 61.3169 | 61.4851 | 61.4463 | 61.4748 | 61.4893 | 61.5139 | 61.4946 | 61.5202 | 123.0148 | 61.6759 | 122.9414 | 61.4262 | 61.4984 | 123.0118 | 61.4716 | 122.79 | 61.5163 | 61.5431 | 61.443 | 61.4698
990.8906 | 123.2849 | -61.4136 | 61.6058 | 0.007391 | -0.031363 | -0.007421 | 0.01619 | 0.045421 | 0.021485 | 0.056315 | 61.5417 | 0.19827 | 61.4775 | -0.055996 | 0.020767 | 61.5387 | 0.003143 | 61.3077 | 61.421 | 61.3822 | 61.4062 | 61.4298 | 61.459 | 61.4351 | 61.4699 | 122.9553 | 61.6118 | 122.8911 | 61.3576 | 61.4343 | 122.9523 | 61.4167 | 122.7213 | 61.5209 | 61.5385 | 61.4567 | 61.4744
991.8906 | 123.2986 | -61.4136 | 61.615 | 0.007391 | -0.017627 | -0.007421 | 0.020768 | 0.040843 | 0.026064 | 0.047159 | 61.5417 | 0.19369 | 61.4729 | -0.051417 | 0.025345 | 61.5387 | -0.001436 | 61.3077 | 61.421 | 61.3959 | 61.4062 | 61.4343 | 61.4544 | 61.4396 | 61.4607 | 122.9553 | 61.6073 | 122.8865 | 61.3622 | 61.4389 | 122.9523 | 61.4121 | 122.7213 | 61.5163 | 61.5431 | 61.4476 | 61.4744
992.8906 | 123.1567 | -61.441 | 61.6241 | 0.01197 | -0.031363 | 0.001736 | 0.01619 | 0.049999 | 0.026064 | 0.042581 | 61.5417 | 0.18911 | 61.4775 | -0.051417 | 0.025345 | 61.5295 | 0.003143 | 61.3215 | 61.453 | 61.4097 | 61.4428 | 61.4572 | 61.491 | 61.4671 | 61.4836 | 122.9827 | 61.6301 | 122.9186 | 61.3896 | 61.4664 | 122.9706 | 61.4442 | 122.7625 | 61.5163 | 61.5385 | 61.4522 | 61.4744
993.8906 | 123.1934 | -61.4273 | 61.6425 | 0.01197 | -0.026784 | -0.007421 | 0.01619 | 0.045421 | 0.012329 | 0.042581 | 61.5417 | 0.18453 | 61.4729 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4393 | 61.4005 | 61.4199 | 61.4435 | 61.4727 | 61.4396 | 61.4699 | 122.969 | 61.6118 | 122.9002 | 61.3805 | 61.4527 | 122.9614 | 61.4259 | 122.7442 | 61.5163 | 61.5431 | 61.4476 | 61.4744
994.8906 | 123.262 | -61.4227 | 61.5372 | 0.01197 | -0.031363 | 0.001736 | 0.01619 | 0.040843 | 0.021485 | 0.038003 | 61.5371 | 0.19369 | 61.4684 | -0.055996 | 0.020767 | 61.5341 | 0.007721 | 61.3169 | 61.4347 | 61.3914 | 61.4245 | 61.4389 | 61.4636 | 61.4442 | 61.4607 | 122.9598 | 61.6164 | 122.8911 | 61.3667 | 61.4435 | 122.9568 | 61.4304 | 122.7396 | 61.5163 | 61.5294 | 61.4476 | 61.4606
995.8906 | 123.2437 | -61.4273 | 61.615 | 0.016548 | -0.026784 | -0.002842 | 0.020768 | 0.045421 | 0.021485 | 0.047159 | 61.5371 | 0.18911 | 61.4684 | -0.060575 | 0.029923 | 61.5341 | -0.001436 | 61.3169 | 61.4439 | 61.4005 | 61.4245 | 61.4481 | 61.4727 | 61.4488 | 61.4745 | 122.9644 | 61.6164 | 122.8957 | 61.3667 | 61.4572 | 122.9614 | 61.4259 | 122.7442 | 61.5072 | 61.5385 | 61.4384 | 61.4698
996.8906 | 123.1979 | -61.4319 | 61.647 | 0.016548 | -0.022205 | 0.001736 | 0.01619 | 0.045421 | 0.021485 | 0.042581 | 61.5325 | 0.19827 | 61.4684 | -0.046838 | 0.016188 | 61.5387 | -0.001436 | 61.3123 | 61.4484 | 61.4097 | 61.4336 | 61.4481 | 61.4773 | 61.4534 | 61.4745 | 122.9644 | 61.6302 | 122.9002 | 61.385 | 61.4481 | 122.9706 | 61.4304 | 122.7442 | 61.5163 | 61.534 | 61.4522 | 61.4698
997.8906 | 123.175 | -61.4365 | 61.6196 | 0.01197 | -0.013048 | -0.002842 | 0.01619 | 0.045421 | 0.016907 | 0.051737 | 61.5417 | 0.19827 | 61.4775 | -0.051417 | 0.025345 | 61.5387 | -0.001436 | 61.3169 | 61.4484 | 61.4234 | 61.4336 | 61.4527 | 61.4819 | 61.4534 | 61.4882 | 122.9781 | 61.6347 | 122.914 | 61.385 | 61.4618 | 122.9752 | 61.435 | 122.7533 | 61.5163 | 61.5431 | 61.4522 | 61.4789
998.8906 | 123.1613 | -61.4548 | 61.6287 | 0.007391 | -0.035942 | 0.001736 | 0.020768 | 0.049999 | 0.016907 | 0.051737 | 61.5417 | 0.19827 | 61.4684 | -0.046838 | 0.01161 | 61.5295 | 0.003143 | 61.3215 | 61.4622 | 61.4188 | 61.4565 | 61.4755 | 61.5048 | 61.4717 | 61.5065 | 122.9965 | 61.653 | 122.9231 | 61.4079 | 61.4664 | 122.9843 | 61.4579 | 122.7762 | 61.5301 | 61.5385 | 61.4567 | 61.4652
999.8906 | 123.2849 | -61.4365 | 61.5875 | 0.01197 | -0.026784 | -0.007421 | 0.020768 | 0.040843 | 0.016907 | 0.042581 | 61.5325 | 0.18911 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3123 | 61.4484 | 61.4097 | 61.429 | 61.4572 | 61.4773 | 61.4534 | 61.479 | 122.969 | 61.6256 | 122.9048 | 61.385 | 61.4572 | 122.9706 | 61.4396 | 122.7488 | 61.5118 | 61.5294 | 61.4476 | 61.4652
1000.8906 | 123.2162 | -61.4044 | 61.615 | 0.007391 | -0.017627 | 0.001736 | 0.029925 | 0.049999 | 0.016907 | 0.047159 | 61.5508 | 0.18911 | 61.4684 | -0.055996 | 0.029923 | 61.5387 | -0.010593 | 61.3123 | 61.4118 | 61.3868 | 61.4062 | 61.4343 | 61.4544 | 61.4213 | 61.4516 | 122.9553 | 61.5935 | 122.8728 | 61.3484 | 61.4343 | 122.9431 | 61.3938 | 122.7167 | 61.5209 | 61.5614 | 61.4384 | 61.4789
1001.8906 | 123.2391 | -61.4456 | 61.5738 | 0.016548 | -0.026784 | 0.001736 | 0.020768 | 0.045421 | 0.026064 | 0.047159 | 61.5463 | 0.18911 | 61.4775 | -0.042259 | 0.020767 | 61.5387 | -0.001436 | 61.3123 | 61.4622 | 61.4188 | 61.4474 | 61.4664 | 61.491 | 61.4717 | 61.4928 | 122.9919 | 61.6347 | 122.9231 | 61.4034 | 61.4664 | 122.9843 | 61.4442 | 122.7579 | 61.5255 | 61.5477 | 61.4567 | 61.4789
1002.8906 | 123.1659 | -61.4456 | 61.5967 | 0.016548 | -0.026784 | 0.006315 | 0.011611 | 0.045421 | 0.026064 | 0.042581 | 61.5554 | 0.19369 | 61.4775 | -0.046838 | 0.020767 | 61.5341 | 0.003143 | 61.3215 | 61.4622 | 61.4188 | 61.4519 | 61.4572 | 61.491 | 61.4717 | 61.4882 | 123.001 | 61.6393 | 122.9231 | 61.3988 | 61.4664 | 122.9797 | 61.4488 | 122.7671 | 61.5346 | 61.5523 | 61.4567 | 61.4744
1003.8906 | 123.2071 | -61.441 | 61.6013 | 0.016548 | -0.022205 | -0.002842 | 0.01619 | 0.045421 | 0.021485 | 0.047159 | 61.5463 | 0.19369 | 61.4775 | -0.046838 | 0.025345 | 61.5295 | -0.006014 | 61.3123 | 61.4576 | 61.4188 | 61.4382 | 61.4572 | 61.4865 | 61.4625 | 61.4882 | 122.9873 | 61.6347 | 122.9186 | 61.3942 | 61.4664 | 122.9706 | 61.435 | 122.7533 | 61.5209 | 61.5523 | 61.4522 | 61.4835
1004.8906 | 123.3078 | -61.409 | 61.5692 | 0.01197 | -0.022205 | -0.002842 | 0.01619 | 0.045421 | 0.026064 | 0.047159 | 61.5371 | 0.19827 | 61.4729 | -0.051417 | 0.025345 | 61.5295 | 0.003143 | 61.3169 | 61.421 | 61.3868 | 61.4062 | 61.4252 | 61.4544 | 61.4351 | 61.4562 | 122.9461 | 61.6073 | 122.8819 | 61.3576 | 61.4343 | 122.9385 | 61.4121 | 122.7259 | 61.5118 | 61.534 | 61.4476 | 61.4698
1005.8906 | 123.1567 | -61.4456 | 61.5829 | 0.007391 | -0.017627 | 0.001736 | 0.025347 | 0.045421 | 0.026064 | 0.051737 | 61.5463 | 0.19827 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.453 | 61.428 | 61.4474 | 61.471 | 61.491 | 61.4717 | 61.4974 | 122.9919 | 61.6439 | 122.9231 | 61.3988 | 61.4664 | 122.9752 | 61.4442 | 122.7579 | 61.5255 | 61.5477 | 61.4567 | 61.4789
1006.8906 | 123.1934 | -61.4731 | 61.5921 | 0.01197 | -0.022205 | -0.007421 | 0.025347 | 0.049999 | 0.026064 | 0.042581 | 61.5417 | 0.19827 | 61.4775 | -0.055996 | 0.020767 | 61.5341 | -0.006014 | 61.3215 | 61.4851 | 61.4509 | 61.4657 | 61.4984 | 61.5231 | 61.4991 | 61.5157 | 123.0148 | 61.6713 | 122.9506 | 61.4171 | 61.4939 | 123.0072 | 61.4671 | 122.7945 | 61.5209 | 61.5477 | 61.4567 | 61.4835
1007.8906 | 123.1338 | -61.4594 | 61.5921 | 0.007391 | -0.022205 | 0.001736 | 0.025347 | 0.054577 | 0.030642 | 0.051737 | 61.5463 | 0.19369 | 61.4821 | -0.046838 | 0.016188 | 61.5295 | 0.003143 | 61.3169 | 61.4667 | 61.4371 | 61.4611 | 61.4847 | 61.5139 | 61.49 | 61.5111 | 123.0056 | 61.653 | 122.9414 | 61.4125 | 61.4755 | 122.9889 | 61.4625 | 122.7762 | 61.5301 | 61.5431 | 61.4659 | 61.4789
1008.8906 | 123.1842 | -61.441 | 61.5509 | 0.01197 | -0.026784 | 0.001736 | 0.020768 | 0.040843 | 0.030642 | 0.051737 | 61.5417 | 0.19827 | 61.4684 | -0.051417 | 0.016188 | 61.5295 | 0.003143 | 61.3169 | 61.453 | 61.4143 | 61.4428 | 61.4618 | 61.4819 | 61.4717 | 61.4928 | 122.9827 | 61.6393 | 122.9094 | 61.3896 | 61.4572 | 122.9706 | 61.4442 | 122.7579 | 61.5255 | 61.5385 | 61.4522 | 61.4652
1009.8906 | 123.2071 | -61.4548 | 61.6013 | 0.01197 | -0.022205 | 0.001736 | 0.020768 | 0.045421 | 0.026064 | 0.042581 | 61.5508 | 0.18911 | 61.4638 | -0.051417 | 0.025345 | 61.5295 | 0.003143 | 61.3123 | 61.4667 | 61.4326 | 61.4565 | 61.4755 | 61.5002 | 61.4808 | 61.4974 | 123.0056 | 61.6439 | 122.9185 | 61.4034 | 61.4801 | 122.9843 | 61.4579 | 122.7671 | 61.5255 | 61.5477 | 61.4384 | 61.4606
1010.8906 | 123.2712 | -61.4044 | 61.5463 | 0.007391 | -0.022205 | -0.002842 | 0.020768 | 0.045421 | 0.016907 | 0.038003 | 61.5417 | 0.19369 | 61.4684 | -0.046838 | 0.016188 | 61.525 | 0.003143 | 61.3077 | 61.4118 | 61.3822 | 61.4016 | 61.4252 | 61.4498 | 61.4213 | 61.4424 | 122.9461 | 61.5981 | 122.8728 | 61.3576 | 61.4206 | 122.9294 | 61.4076 | 122.7121 | 61.5255 | 61.5385 | 61.4522 | 61.4652
1011.8906 | 123.2712 | -61.4502 | 61.5234 | 0.007391 | -0.026784 | -0.002842 | 0.01619 | 0.040843 | 0.021485 | 0.038003 | 61.5417 | 0.20284 | 61.4684 | -0.055996 | 0.020767 | 61.5341 | -0.001436 | 61.3123 | 61.4576 | 61.4234 | 61.4474 | 61.4664 | 61.491 | 61.4717 | 61.4882 | 122.9919 | 61.653 | 122.9185 | 61.3942 | 61.471 | 122.9843 | 61.4488 | 122.7625 | 61.5209 | 61.5431 | 61.4476 | 61.4698
1012.8906 | 123.2941 | -61.4502 | 61.528 | 0.016548 | -0.031363 | 0.001736 | 0.020768 | 0.054577 | 0.026064 | 0.047159 | 61.5417 | 0.19369 | 61.4684 | -0.055996 | 0.020767 | 61.5341 | -0.001436 | 61.3169 | 61.4667 | 61.4188 | 61.4519 | 61.471 | 61.5048 | 61.4763 | 61.4974 | 122.9919 | 61.6439 | 122.9185 | 61.3942 | 61.471 | 122.9843 | 61.4488 | 122.7671 | 61.5209 | 61.5431 | 61.4476 | 61.4698
1013.8906 | 123.2712 | -61.441 | 61.5189 | 0.002813 | -0.026784 | 0.001736 | 0.020768 | 0.049999 | 0.021485 | 0.047159 | 61.5508 | 0.19827 | 61.4684 | -0.055996 | 0.020767 | 61.5341 | 0.003143 | 61.3077 | 61.4439 | 61.4143 | 61.4428 | 61.4618 | 61.491 | 61.4625 | 61.4882 | 122.9919 | 61.6393 | 122.9094 | 61.385 | 61.4618 | 122.9752 | 61.4442 | 122.7488 | 61.5301 | 61.5477 | 61.4476 | 61.4652
1014.8906 | 123.3078 | -61.4227 | 61.5326 | 0.01197 | -0.022205 | -0.002842 | 0.01619 | 0.045421 | 0.026064 | 0.051737 | 61.5417 | 0.19369 | 61.4729 | -0.051417 | 0.020767 | 61.5387 | -0.001436 | 61.2986 | 61.4347 | 61.4005 | 61.4199 | 61.4389 | 61.4681 | 61.4488 | 61.4745 | 122.9644 | 61.6164 | 122.8957 | 61.3713 | 61.4435 | 122.9614 | 61.4213 | 122.7213 | 61.5209 | 61.5431 | 61.4522 | 61.4744
1015.8906 | 123.2162 | -61.4548 | 61.5463 | 0.016548 | -0.022205 | -0.002842 | 0.020768 | 0.054577 | 0.021485 | 0.047159 | 61.5463 | 0.19827 | 61.4775 | -0.046838 | 0.016188 | 61.5341 | -0.001436 | 61.3031 | 61.4713 | 61.4326 | 61.4519 | 61.4755 | 61.5094 | 61.4763 | 61.5019 | 123.001 | 61.653 | 122.9323 | 61.4079 | 61.471 | 122.9889 | 61.4533 | 122.7579 | 61.5301 | 61.5477 | 61.4613 | 61.4789
1016.8906 | 123.317 | -61.4319 | 61.5234 | 0.016548 | -0.013048 | -0.002842 | 0.020768 | 0.045421 | 0.021485 | 0.051737 | 61.5417 | 0.19827 | 61.4729 | -0.055996 | 0.025345 | 61.5295 | 0.003143 | 61.3077 | 61.4484 | 61.4188 | 61.429 | 61.4527 | 61.4773 | 61.4534 | 61.4836 | 122.9736 | 61.6302 | 122.9048 | 61.3759 | 61.4572 | 122.9614 | 61.435 | 122.7396 | 61.5163 | 61.5385 | 61.4476 | 61.4698
1017.8906 | 123.2712 | -61.4273 | 61.5417 | 0.01197 | -0.022205 | 0.001736 | 0.020768 | 0.049999 | 0.026064 | 0.047159 | 61.5508 | 0.18453 | 61.4729 | -0.055996 | 0.020767 | 61.5387 | 0.003143 | 61.3123 | 61.4393 | 61.4051 | 61.429 | 61.4481 | 61.4773 | 61.4534 | 61.4745 | 122.9781 | 61.6118 | 122.9002 | 61.3713 | 61.4481 | 122.966 | 61.4305 | 122.7396 | 61.5301 | 61.5477 | 61.4522 | 61.4698
1018.8906 | 123.2895 | -61.4182 | 61.528 | 0.01197 | -0.017627 | 0.001736 | 0.020768 | 0.054577 | 0.026064 | 0.042581 | 61.5417 | 0.19827 | 61.4684 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3077 | 61.4301 | 61.4005 | 61.4199 | 61.4389 | 61.4727 | 61.4442 | 61.4607 | 122.9598 | 61.6164 | 122.8865 | 61.3713 | 61.4435 | 122.9523 | 61.4167 | 122.7259 | 61.5163 | 61.5431 | 61.443 | 61.4698
1019.8906 | 123.3124 | -61.441 | 61.5372 | 0.016548 | -0.017627 | 0.006315 | 0.029925 | 0.045421 | 0.026064 | 0.047159 | 61.5417 | 0.19827 | 61.4684 | -0.055996 | 0.016188 | 61.5341 | -0.010593 | 61.3031 | 61.4576 | 61.4234 | 61.4474 | 61.471 | 61.4865 | 61.4671 | 61.4882 | 122.9827 | 61.6393 | 122.9094 | 61.385 | 61.4572 | 122.9752 | 61.4304 | 122.7442 | 61.5255 | 61.5523 | 61.4522 | 61.4789
1020.8906 | 123.2346 | -61.4365 | 61.5417 | 0.016548 | -0.017627 | 0.006315 | 0.025347 | 0.040843 | 0.026064 | 0.047159 | 61.5325 | 0.19369 | 61.4729 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3077 | 61.453 | 61.4188 | 61.4428 | 61.4618 | 61.4773 | 61.4625 | 61.4836 | 122.969 | 61.6302 | 122.9094 | 61.3896 | 61.4572 | 122.966 | 61.4396 | 122.7442 | 61.5118 | 61.5294 | 61.4522 | 61.4698
1021.8906 | 123.2941 | -61.4273 | 61.5463 | 0.007391 | -0.017627 | 0.006315 | 0.025347 | 0.049999 | 0.021485 | 0.042581 | 61.5463 | 0.19827 | 61.4729 | -0.046838 | 0.020767 | 61.5387 | -0.001436 | 61.3031 | 61.4347 | 61.4097 | 61.4336 | 61.4527 | 61.4773 | 61.4488 | 61.4699 | 122.9736 | 61.6256 | 122.9002 | 61.3805 | 61.4481 | 122.966 | 61.4259 | 122.7305 | 61.5255 | 61.5477 | 61.4522 | 61.4744
1022.8906 | 123.262 | -61.4594 | 61.5463 | 0.007391 | -0.022205 | 0.006315 | 0.025347 | 0.054577 | 0.016907 | 0.042581 | 61.5371 | 0.19827 | 61.4684 | -0.046838 | 0.025345 | 61.525 | -0.006014 | 61.3123 | 61.4667 | 61.4371 | 61.4657 | 61.4847 | 61.5139 | 61.4763 | 61.5019 | 122.9965 | 61.6576 | 122.9277 | 61.4125 | 61.4847 | 122.9843 | 61.4533 | 122.7717 | 61.5118 | 61.5431 | 61.443 | 61.4744
1023.8906 | 123.2666 | -61.441 | 61.5555 | 0.01197 | -0.022205 | -0.002842 | 0.025347 | 0.040843 | 0.021485 | 0.042581 | 61.5417 | 0.19827 | 61.4775 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3077 | 61.453 | 61.4188 | 61.4382 | 61.4664 | 61.4819 | 61.4625 | 61.4836 | 122.9827 | 61.6393 | 122.9186 | 61.3942 | 61.4618 | 122.9752 | 61.4396 | 122.7488 | 61.5209 | 61.5431 | 61.4567 | 61.4789
1024.8906 | 123.262 | -61.4594 | 61.5784 | 0.007391 | -0.026784 | -0.002842 | 0.01619 | 0.045421 | 0.026064 | 0.047159 | 61.5463 | 0.19369 | 61.4684 | -0.051417 | 0.025345 | 61.5341 | -0.006014 | 61.3031 | 61.4667 | 61.4326 | 61.4565 | 61.4755 | 61.5048 | 61.4854 | 61.5065 | 123.0056 | 61.653 | 122.9277 | 61.4079 | 61.4847 | 122.9935 | 61.4533 | 122.7625 | 61.5209 | 61.5523 | 61.443 | 61.4744
1025.8906 | 123.23 | -61.4319 | 61.5555 | 0.01197 | -0.017627 | 0.001736 | 0.025347 | 0.049999 | 0.016907 | 0.065472 | 61.5463 | 0.20284 | 61.4729 | -0.046838 | 0.016188 | 61.5341 | -0.006014 | 61.3077 | 61.4439 | 61.4143 | 61.4336 | 61.4572 | 61.4819 | 61.4488 | 61.4974 | 122.9781 | 61.6347 | 122.9048 | 61.385 | 61.4481 | 122.966 | 61.4259 | 122.7396 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1026.8906 | 123.2849 | -61.4456 | 61.5692 | 0.01197 | -0.008469 | 0.001736 | 0.020768 | 0.049999 | 0.026064 | 0.047159 | 61.5463 | 0.19369 | 61.4684 | -0.055996 | 0.025345 | 61.5295 | 0.003143 | 61.3123 | 61.4576 | 61.4371 | 61.4474 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 122.9919 | 61.6393 | 122.914 | 61.3896 | 61.471 | 122.9752 | 61.4488 | 122.7579 | 61.5209 | 61.5431 | 61.443 | 61.4652
1027.8906 | 123.2391 | -61.441 | 61.5692 | 0.016548 | -0.022205 | 0.001736 | 0.025347 | 0.049999 | 0.026064 | 0.047159 | 61.5417 | 0.18911 | 61.4729 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.4576 | 61.4188 | 61.4428 | 61.4664 | 61.491 | 61.4671 | 61.4882 | 122.9827 | 61.6301 | 122.914 | 61.3942 | 61.4664 | 122.9706 | 61.4396 | 122.7488 | 61.5163 | 61.5431 | 61.4476 | 61.4744
1028.8906 | 123.262 | -61.4273 | 61.5555 | 0.007391 | -0.022205 | 0.001736 | 0.025347 | 0.040843 | 0.021485 | 0.056315 | 61.5463 | 0.19827 | 61.4684 | -0.03768 | 0.025345 | 61.5387 | 0.003143 | 61.3123 | 61.4347 | 61.4051 | 61.429 | 61.4527 | 61.4682 | 61.4488 | 61.4836 | 122.9736 | 61.6256 | 122.8957 | 61.3896 | 61.4527 | 122.966 | 61.4305 | 122.7396 | 61.5209 | 61.5431 | 61.443 | 61.4652
1029.8906 | 123.3032 | -61.4227 | 61.5692 | 0.007391 | -0.022205 | 0.006315 | 0.025347 | 0.040843 | 0.026064 | 0.051737 | 61.5463 | 0.20284 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | -0.006014 | 61.3031 | 61.4301 | 61.4005 | 61.429 | 61.4481 | 61.4636 | 61.4488 | 61.4745 | 122.969 | 61.6256 | 122.9002 | 61.3759 | 61.4435 | 122.9523 | 61.4167 | 122.7259 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1030.8906 | 123.2941 | -61.4227 | 61.5784 | 0.007391 | -0.017627 | -0.002842 | 0.01619 | 0.049999 | 0.026064 | 0.047159 | 61.5463 | 0.18911 | 61.4684 | -0.042259 | 0.029923 | 61.525 | -0.001436 | 61.3169 | 61.4301 | 61.4051 | 61.4199 | 61.4389 | 61.4727 | 61.4488 | 61.4699 | 122.969 | 61.6118 | 122.8911 | 61.3805 | 61.4527 | 122.9477 | 61.4213 | 122.7396 | 61.5163 | 61.5477 | 61.4384 | 61.4698
1031.8906 | 123.3078 | -61.4365 | 61.5555 | 0.007391 | -0.026784 | -0.002842 | 0.025347 | 0.045421 | 0.030642 | 0.042581 | 61.5508 | 0.19369 | 61.4821 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3031 | 61.4439 | 61.4097 | 61.4336 | 61.4618 | 61.4819 | 61.4671 | 61.479 | 122.9873 | 61.6302 | 122.9185 | 61.3896 | 61.4572 | 122.966 | 61.4396 | 122.7396 | 61.5301 | 61.5477 | 61.4613 | 61.4789
1032.8906 | 123.2483 | -61.4365 | 61.5646 | 0.01197 | -0.022205 | -0.007421 | 0.020768 | 0.045421 | 0.021485 | 0.051737 | 61.5417 | 0.19827 | 61.4684 | -0.055996 | 0.029923 | 61.5341 | -0.006014 | 61.3123 | 61.4484 | 61.4143 | 61.429 | 61.4572 | 61.4819 | 61.4579 | 61.4882 | 122.9781 | 61.6347 | 122.9048 | 61.3805 | 61.4664 | 122.9706 | 61.4304 | 122.7488 | 61.5118 | 61.5477 | 61.4384 | 61.4744
1033.8906 | 123.2803 | -61.4273 | 61.5601 | 0.002813 | -0.026784 | -0.002842 | 0.029925 | 0.049999 | 0.021485 | 0.051737 | 61.5417 | 0.20284 | 61.4729 | -0.046838 | 0.016188 | 61.5295 | -0.001436 | 61.3169 | 61.4301 | 61.4005 | 61.4245 | 61.4572 | 61.4773 | 61.4488 | 61.479 | 122.969 | 61.6302 | 122.9002 | 61.3805 | 61.4435 | 122.9568 | 61.4259 | 122.7442 | 61.5255 | 61.5431 | 61.4567 | 61.4744
1034.8906 | 123.3353 | -61.409 | 61.5921 | 0.007391 | -0.026784 | -0.007421 | 0.025347 | 0.045421 | 0.026064 | 0.051737 | 61.5508 | 0.19827 | 61.4729 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3123 | 61.4164 | 61.3822 | 61.4016 | 61.4343 | 61.4544 | 61.4351 | 61.4607 | 122.9598 | 61.6073 | 122.8819 | 61.3576 | 61.4298 | 122.9431 | 61.403 | 122.7213 | 61.5301 | 61.5568 | 61.4522 | 61.4789
1035.8906 | 123.2803 | -61.4227 | 61.5189 | 0.01197 | -0.017627 | 0.001736 | 0.020768 | 0.049999 | 0.030642 | 0.056315 | 61.5508 | 0.19827 | 61.4684 | -0.046838 | 0.020767 | 61.5341 | -0.006014 | 61.3123 | 61.4347 | 61.4051 | 61.4245 | 61.4435 | 61.4727 | 61.4534 | 61.479 | 122.9736 | 61.621 | 122.8911 | 61.3759 | 61.4435 | 122.9568 | 61.4167 | 122.735 | 61.5301 | 61.5568 | 61.4476 | 61.4744
1036.8906 | 123.349 | -61.377 | 61.6058 | 0.01197 | -0.017627 | 0.001736 | 0.01619 | 0.045421 | 0.026064 | 0.051737 | 61.5463 | 0.19369 | 61.4684 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3169 | 61.3889 | 61.3593 | 61.3787 | 61.3931 | 61.4224 | 61.403 | 61.4287 | 122.9232 | 61.5706 | 122.8453 | 61.3255 | 61.3977 | 122.9111 | 61.3755 | 122.6938 | 61.5255 | 61.5477 | 61.4476 | 61.4698
1037.8906 | 123.317 | -61.4273 | 61.5463 | 0.007391 | -0.022205 | 0.006315 | 0.025347 | 0.049999 | 0.021485 | 0.051737 | 61.5417 | 0.19369 | 61.4775 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4347 | 61.4051 | 61.4336 | 61.4527 | 61.4773 | 61.4488 | 61.479 | 122.969 | 61.621 | 122.9048 | 61.3805 | 61.4527 | 122.9614 | 61.4259 | 122.7442 | 61.5163 | 61.5431 | 61.4522 | 61.4789
1038.8906 | 123.2849 | -61.4182 | 61.5921 | 0.007391 | -0.022205 | 0.001736 | 0.025347 | 0.049999 | 0.030642 | 0.051737 | 61.5371 | 0.19827 | 61.4729 | -0.051417 | 0.020767 | 61.5387 | 0.003143 | 61.3215 | 61.4255 | 61.3959 | 61.4199 | 61.4435 | 61.4682 | 61.4488 | 61.4699 | 122.9553 | 61.6164 | 122.8911 | 61.3667 | 61.4389 | 122.9568 | 61.4213 | 122.7396 | 61.5163 | 61.534 | 61.4522 | 61.4698
1039.8906 | 123.3444 | -61.3998 | 61.5372 | 0.016548 | -0.026784 | 0.001736 | 0.029925 | 0.049999 | 0.030642 | 0.056315 | 61.5417 | 0.19827 | 61.4684 | -0.046838 | 0.020767 | 61.5387 | -0.001436 | 61.3123 | 61.4164 | 61.3731 | 61.4016 | 61.4298 | 61.4498 | 61.4305 | 61.4562 | 122.9415 | 61.5981 | 122.8682 | 61.353 | 61.4206 | 122.9385 | 61.3984 | 122.7121 | 61.5209 | 61.5431 | 61.4476 | 61.4698
1040.8906 | 123.1522 | -61.4548 | 61.6104 | 0.007391 | -0.017627 | 0.010893 | 0.025347 | 0.045421 | 0.021485 | 0.056315 | 61.5463 | 0.19827 | 61.4729 | -0.046838 | 0.020767 | 61.5341 | 0.003143 | 61.3169 | 61.4622 | 61.4371 | 61.4657 | 61.4801 | 61.5002 | 61.4763 | 61.5111 | 123.001 | 61.653 | 122.9277 | 61.4079 | 61.4755 | 122.9889 | 61.4579 | 122.7717 | 61.5255 | 61.5431 | 61.4522 | 61.4698
1041.8906 | 123.2483 | -61.4136 | 61.6241 | 0.016548 | -0.022205 | 0.006315 | 0.029925 | 0.054577 | 0.035221 | 0.051737 | 61.5417 | 0.19369 | 61.4729 | -0.046838 | 0.025345 | 61.5387 | -0.001436 | 61.3169 | 61.4301 | 61.3914 | 61.4199 | 61.4435 | 61.4682 | 61.4488 | 61.4653 | 122.9553 | 61.6073 | 122.8865 | 61.3667 | 61.4389 | 122.9523 | 61.4121 | 122.7305 | 61.5163 | 61.5431 | 61.4476 | 61.4744
1042.8906 | 123.2712 | -61.4182 | 61.6013 | 0.01197 | -0.017627 | 0.006315 | 0.025347 | 0.054577 | 0.035221 | 0.056315 | 61.5417 | 0.19369 | 61.4729 | -0.046838 | 0.025345 | 61.5341 | 0.003143 | 61.3077 | 61.4301 | 61.4005 | 61.4245 | 61.4435 | 61.4727 | 61.4534 | 61.4745 | 122.9598 | 61.6118 | 122.8911 | 61.3713 | 61.4435 | 122.9523 | 61.4213 | 122.7259 | 61.5163 | 61.5385 | 61.4476 | 61.4698
1043.8906 | 123.2346 | -61.4227 | 61.5875 | 0.007391 | -0.022205 | 0.001736 | 0.029925 | 0.049999 | 0.026064 | 0.051737 | 61.5463 | 0.19827 | 61.4821 | -0.051417 | 0.029923 | 61.5295 | -0.006014 | 61.3169 | 61.4301 | 61.4005 | 61.4245 | 61.4527 | 61.4727 | 61.4488 | 61.4745 | 122.969 | 61.621 | 122.9048 | 61.3713 | 61.4527 | 122.9523 | 61.4167 | 122.7396 | 61.5163 | 61.5523 | 61.4522 | 61.4881
1044.8906 | 123.2712 | -61.3998 | 61.6013 | 0.01197 | -0.022205 | -0.002842 | 0.029925 | 0.049999 | 0.030642 | 0.056315 | 61.5508 | 0.19369 | 61.4775 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3169 | 61.4118 | 61.3776 | 61.397 | 61.4298 | 61.4498 | 61.4305 | 61.4562 | 122.9507 | 61.5935 | 122.8774 | 61.3484 | 61.4206 | 122.934 | 61.403 | 122.7167 | 61.5301 | 61.5477 | 61.4567 | 61.4744
1045.8906 | 123.2208 | -61.4548 | 61.615 | 0.01197 | -0.022205 | 0.006315 | 0.025347 | 0.045421 | 0.035221 | 0.056315 | 61.5463 | 0.19369 | 61.4684 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3123 | 61.4667 | 61.4326 | 61.4611 | 61.4801 | 61.5002 | 61.49 | 61.5111 | 123.001 | 61.6485 | 122.9231 | 61.4079 | 61.4755 | 122.9889 | 61.4533 | 122.7671 | 61.5255 | 61.5477 | 61.4476 | 61.4698
1046.8906 | 123.2346 | -61.4273 | 61.615 | 0.016548 | -0.022205 | 0.006315 | 0.020768 | 0.054577 | 0.030642 | 0.047159 | 61.5463 | 0.19827 | 61.4729 | -0.055996 | 0.025345 | 61.5295 | -0.001436 | 61.3169 | 61.4439 | 61.4051 | 61.4336 | 61.4481 | 61.4819 | 61.4579 | 61.4745 | 122.9736 | 61.6256 | 122.9002 | 61.3713 | 61.4527 | 122.9568 | 61.4259 | 122.7442 | 61.5209 | 61.5477 | 61.4476 | 61.4744
1047.8906 | 123.2758 | -61.4273 | 61.6287 | 0.007391 | -0.026784 | 0.006315 | 0.029925 | 0.054577 | 0.026064 | 0.056315 | 61.5417 | 0.18453 | 61.4684 | -0.055996 | 0.016188 | 61.5295 | 0.003143 | 61.3123 | 61.4347 | 61.4005 | 61.4336 | 61.4572 | 61.4819 | 61.4534 | 61.4836 | 122.969 | 61.6118 | 122.8957 | 61.3713 | 61.4435 | 122.9568 | 61.4305 | 122.7396 | 61.5255 | 61.5385 | 61.4522 | 61.4652
1048.8906 | 123.1613 | -61.4365 | 61.6196 | 0.007391 | -0.022205 | 0.006315 | 0.029925 | 0.049999 | 0.030642 | 0.051737 | 61.5371 | 0.19827 | 61.4821 | -0.042259 | 0.016188 | 61.5341 | 0.003143 | 61.3169 | 61.4439 | 61.4143 | 61.4428 | 61.4664 | 61.4865 | 61.4671 | 61.4882 | 122.9736 | 61.6347 | 122.9185 | 61.3942 | 61.4526 | 122.9706 | 61.4396 | 122.7533 | 61.5209 | 61.534 | 61.4659 | 61.4789
1049.8906 | 123.1659 | -61.409 | 61.6196 | 0.01197 | -0.026784 | 0.010893 | 0.025347 | 0.063733 | 0.039799 | 0.051737 | 61.5508 | 0.19369 | 61.4729 | -0.046838 | 0.025345 | 61.5295 | 0.003143 | 61.3169 | 61.421 | 61.3822 | 61.4199 | 61.4343 | 61.4727 | 61.4488 | 61.4607 | 122.9598 | 61.6027 | 122.8819 | 61.3622 | 61.4343 | 122.9385 | 61.4121 | 122.7259 | 61.5255 | 61.5477 | 61.4476 | 61.4698
1050.8906 | 123.262 | -61.4548 | 61.6104 | 0.01197 | -0.017627 | 0.010893 | 0.025347 | 0.054577 | 0.026064 | 0.047159 | 61.5417 | 0.19827 | 61.4729 | -0.051417 | 0.020767 | 61.5295 | -0.006014 | 61.3031 | 61.4667 | 61.4371 | 61.4657 | 61.4801 | 61.5094 | 61.4808 | 61.5019 | 122.9965 | 61.653 | 122.9277 | 61.4034 | 61.4755 | 122.9843 | 61.4488 | 122.7579 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1051.8906 | 123.1888 | -61.4319 | 61.6333 | 0.007391 | -0.017627 | 0.006315 | 0.025347 | 0.054577 | 0.035221 | 0.051737 | 61.5463 | 0.19827 | 61.4684 | -0.046838 | 0.020767 | 61.5387 | 0.003143 | 61.3077 | 61.4393 | 61.4143 | 61.4382 | 61.4572 | 61.4865 | 61.4671 | 61.4836 | 122.9781 | 61.6302 | 122.9002 | 61.385 | 61.4527 | 122.9706 | 61.435 | 122.7396 | 61.5255 | 61.5431 | 61.4476 | 61.4652
1052.8906 | 123.2162 | -61.4273 | 61.615 | 0.007391 | -0.013048 | -0.007421 | 0.025347 | 0.059155 | 0.026064 | 0.060893 | 61.5463 | 0.20284 | 61.4775 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3169 | 61.4347 | 61.4143 | 61.4199 | 61.4527 | 61.4865 | 61.4534 | 61.4882 | 122.9736 | 61.6302 | 122.9048 | 61.3759 | 61.4481 | 122.9614 | 61.4259 | 122.7442 | 61.5255 | 61.5477 | 61.4567 | 61.4789
1053.8906 | 123.2208 | -61.4456 | 61.6241 | 0.016548 | -0.022205 | 0.006315 | 0.025347 | 0.045421 | 0.026064 | 0.051737 | 61.5417 | 0.20284 | 61.4638 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3169 | 61.4622 | 61.4234 | 61.4519 | 61.471 | 61.491 | 61.4717 | 61.4974 | 122.9873 | 61.6485 | 122.9094 | 61.3988 | 61.471 | 122.9752 | 61.4442 | 122.7625 | 61.5163 | 61.5431 | 61.4384 | 61.4652
1054.8906 | 123.1201 | -61.4365 | 61.6241 | 0.01197 | -0.022205 | 0.006315 | 0.025347 | 0.049999 | 0.030642 | 0.051737 | 61.5417 | 0.19369 | 61.4729 | -0.042259 | 0.025345 | 61.5387 | 0.003143 | 61.3215 | 61.4484 | 61.4143 | 61.4428 | 61.4618 | 61.4865 | 61.4671 | 61.4882 | 122.9781 | 61.6302 | 122.9094 | 61.3942 | 61.4618 | 122.9752 | 61.4396 | 122.7579 | 61.5163 | 61.5385 | 61.4476 | 61.4698
1055.8906 | 123.3078 | -61.4227 | 61.5967 | 0.01197 | -0.017627 | 0.010893 | 0.029925 | 0.059155 | 0.030642 | 0.060893 | 61.5508 | 0.19827 | 61.4729 | -0.051417 | 0.025345 | 61.5341 | 0.007721 | 61.3123 | 61.4347 | 61.4051 | 61.4336 | 61.4527 | 61.4819 | 61.4534 | 61.4836 | 122.9736 | 61.621 | 122.8957 | 61.3713 | 61.4481 | 122.9568 | 61.4304 | 122.735 | 61.5255 | 61.5431 | 61.4476 | 61.4652
1056.8906 | 123.1018 | -61.4044 | 61.6287 | 0.002813 | -0.017627 | 0.006315 | 0.025347 | 0.049999 | 0.035221 | 0.060893 | 61.5417 | 0.19827 | 61.4775 | -0.046838 | 0.029923 | 61.5387 | -0.006014 | 61.3169 | 61.4072 | 61.3868 | 61.4107 | 61.4298 | 61.4544 | 61.4396 | 61.4653 | 122.9461 | 61.6027 | 122.8819 | 61.3576 | 61.4343 | 122.9431 | 61.3984 | 122.7213 | 61.5118 | 61.5477 | 61.4476 | 61.4835
1057.8906 | 123.1522 | -61.4685 | 61.6241 | 0.01197 | -0.017627 | 0.001736 | 0.020768 | 0.049999 | 0.030642 | 0.051737 | 61.5463 | 0.20742 | 61.4775 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3169 | 61.4805 | 61.4509 | 61.4702 | 61.4893 | 61.5185 | 61.4991 | 61.5202 | 123.0148 | 61.6759 | 122.946 | 61.4171 | 61.4939 | 122.998 | 61.4671 | 122.7854 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1058.8906 | 123.2346 | -61.4502 | 61.6241 | 0.007391 | -0.026784 | -0.012 | 0.01619 | 0.036265 | 0.012329 | 0.042581 | 61.5371 | 0.20284 | 61.4729 | -0.051417 | 0.020767 | 61.5295 | 0.007721 | 61.3215 | 61.4576 | 61.4234 | 61.4382 | 61.4664 | 61.4865 | 61.4625 | 61.4928 | 122.9873 | 61.653 | 122.9231 | 61.3988 | 61.471 | 122.9797 | 61.4579 | 122.7717 | 61.5163 | 61.5294 | 61.4522 | 61.4652
1059.8906 | 123.1522 | -61.441 | 61.6241 | 0.01197 | -0.026784 | -0.012 | 0.01619 | 0.045421 | 0.021485 | 0.047159 | 61.5463 | 0.18911 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.453 | 61.4143 | 61.429 | 61.4572 | 61.4865 | 61.4625 | 61.4882 | 122.9873 | 61.6301 | 122.9186 | 61.3942 | 61.4618 | 122.9706 | 61.4442 | 122.7533 | 61.5255 | 61.5431 | 61.4567 | 61.4744
1060.9062 | 123.2117 | -61.441 | 61.6241 | 0.007391 | -0.031363 | -0.016578 | 0.011611 | 0.049999 | 0.016907 | 0.047159 | 61.5508 | 0.18911 | 61.4821 | -0.046838 | 0.025345 | 61.525 | -0.001436 | 61.3169 | 61.4484 | 61.4097 | 61.4245 | 61.4527 | 61.491 | 61.4579 | 61.4882 | 122.9919 | 61.6301 | 122.9231 | 61.3942 | 61.4664 | 122.966 | 61.4396 | 122.7579 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1061.8906 | 123.2346 | -61.4136 | 61.5875 | 0.01197 | -0.035942 | -0.007421 | 0.01619 | 0.036265 | 0.012329 | 0.047159 | 61.5463 | 0.19827 | 61.4729 | -0.046838 | 0.029923 | 61.525 | 0.003143 | 61.3077 | 61.4255 | 61.3776 | 61.4062 | 61.4298 | 61.4498 | 61.4259 | 61.4607 | 122.9598 | 61.6118 | 122.8865 | 61.3667 | 61.4435 | 122.9385 | 61.4167 | 122.7213 | 61.5163 | 61.5431 | 61.443 | 61.4698
1062.8906 | 123.2162 | -61.4273 | 61.5921 | 0.016548 | -0.031363 | 0.001736 | 0.011611 | 0.040843 | 0.016907 | 0.038003 | 61.5508 | 0.20284 | 61.4729 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3077 | 61.4439 | 61.3959 | 61.429 | 61.4389 | 61.4682 | 61.4442 | 61.4653 | 122.9781 | 61.6302 | 122.9002 | 61.3805 | 61.4527 | 122.9614 | 61.4259 | 122.735 | 61.5255 | 61.5523 | 61.4476 | 61.4744
1063.8906 | 123.1247 | -61.4502 | 61.5921 | 0.01197 | -0.022205 | -0.012 | 0.011611 | 0.040843 | 0.012329 | 0.042581 | 61.5417 | 0.20284 | 61.4821 | -0.046838 | 0.016188 | 61.5387 | -0.001436 | 61.3169 | 61.4622 | 61.428 | 61.4382 | 61.4618 | 61.491 | 61.4625 | 61.4928 | 122.9919 | 61.653 | 122.9323 | 61.4034 | 61.4664 | 122.9889 | 61.4488 | 122.7671 | 61.5255 | 61.5431 | 61.4659 | 61.4835
1064.8906 | 123.1888 | -61.441 | 61.6104 | 0.007391 | -0.031363 | -0.007421 | 0.007033 | 0.040843 | 0.012329 | 0.042581 | 61.5463 | 0.19369 | 61.4821 | -0.051417 | 0.020767 | 61.5295 | -0.006014 | 61.3215 | 61.4484 | 61.4097 | 61.4336 | 61.4481 | 61.4819 | 61.4534 | 61.4836 | 122.9873 | 61.6347 | 122.9231 | 61.3896 | 61.4618 | 122.9706 | 61.435 | 122.7625 | 61.5255 | 61.5523 | 61.4613 | 61.4881
1065.9062 | 123.1567 | -61.4456 | 61.5829 | 0.016548 | -0.031363 | 0.001736 | 0.020768 | 0.031687 | 0.021485 | 0.038003 | 61.5508 | 0.19827 | 61.4775 | -0.051417 | 0.020767 | 61.5387 | -0.006014 | 61.3031 | 61.4622 | 61.4143 | 61.4474 | 61.4664 | 61.4773 | 61.4671 | 61.4836 | 122.9965 | 61.6439 | 122.9231 | 61.3942 | 61.4664 | 122.9843 | 61.4396 | 122.7488 | 61.5301 | 61.5568 | 61.4567 | 61.4835
1066.8906 | 123.2483 | -61.409 | 61.5967 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.040843 | 0.016907 | 0.038003 | 61.5417 | 0.19827 | 61.4775 | -0.046838 | 0.016188 | 61.5341 | -0.006014 | 61.3123 | 61.421 | 61.3776 | 61.4016 | 61.4206 | 61.4498 | 61.4259 | 61.447 | 122.9507 | 61.6073 | 122.8865 | 61.3622 | 61.4252 | 122.9431 | 61.403 | 122.7213 | 61.5255 | 61.5477 | 61.4613 | 61.4835
1067.8906 | 123.1796 | -61.4502 | 61.5829 | 0.016548 | -0.031363 | -0.002842 | 0.01619 | 0.040843 | 0.012329 | 0.051737 | 61.5463 | 0.19369 | 61.4867 | -0.051417 | 0.025345 | 61.5295 | -0.006014 | 61.3123 | 61.4667 | 61.4188 | 61.4474 | 61.4664 | 61.491 | 61.4625 | 61.5019 | 122.9965 | 61.6439 | 122.9369 | 61.3988 | 61.4755 | 122.9797 | 61.4442 | 122.7625 | 61.5209 | 61.5523 | 61.4613 | 61.4927
1068.8906 | 123.2346 | -61.4548 | 61.5875 | 0.016548 | -0.031363 | -0.007421 | 0.011611 | 0.040843 | 0.016907 | 0.042581 | 61.5508 | 0.18911 | 61.4867 | -0.046838 | 0.025345 | 61.5295 | -0.006014 | 61.3123 | 61.4713 | 61.4234 | 61.4474 | 61.4664 | 61.4956 | 61.4717 | 61.4974 | 123.0056 | 61.6439 | 122.9414 | 61.4079 | 61.4801 | 122.9843 | 61.4488 | 122.7671 | 61.5255 | 61.5568 | 61.4613 | 61.4927
1069.8906 | 123.2208 | -61.4227 | 61.6013 | 0.01197 | -0.035942 | -0.007421 | 0.01619 | 0.040843 | 0.012329 | 0.038003 | 61.5417 | 0.19827 | 61.4729 | -0.051417 | 0.025345 | 61.5341 | 0.003143 | 61.3123 | 61.4347 | 61.3868 | 61.4153 | 61.4389 | 61.4636 | 61.4351 | 61.4607 | 122.9644 | 61.621 | 122.8957 | 61.3713 | 61.4481 | 122.9568 | 61.4259 | 122.735 | 61.5163 | 61.5385 | 61.4476 | 61.4698
1070.9062 | 123.2162 | -61.441 | 61.6241 | 0.016548 | -0.040521 | -0.002842 | 0.007033 | 0.040843 | 0.016907 | 0.042581 | 61.5508 | 0.19369 | 61.4729 | -0.051417 | 0.025345 | 61.5295 | 0.003143 | 61.3123 | 61.4576 | 61.4005 | 61.4382 | 61.4481 | 61.4819 | 61.4579 | 61.4836 | 122.9919 | 61.6347 | 122.914 | 61.3896 | 61.4664 | 122.9706 | 61.4442 | 122.7533 | 61.5255 | 61.5477 | 61.4476 | 61.4698
1071.8906 | 123.2254 | -61.4456 | 61.6013 | 0.007391 | -0.031363 | -0.007421 | 0.020768 | 0.040843 | 0.016907 | 0.047159 | 61.5417 | 0.19827 | 61.4821 | -0.042259 | 0.029923 | 61.525 | -0.001436 | 61.3077 | 61.453 | 61.4143 | 61.4382 | 61.4664 | 61.4865 | 61.4625 | 61.4928 | 122.9873 | 61.6439 | 122.9277 | 61.4034 | 61.4755 | 122.9706 | 61.4442 | 122.7533 | 61.5118 | 61.5431 | 61.4522 | 61.4835
1072.8906 | 123.2391 | -61.4548 | 61.5967 | 0.01197 | -0.040521 | -0.012 | 0.020768 | 0.040843 | 0.021485 | 0.042581 | 61.5508 | 0.20284 | 61.4775 | -0.046838 | 0.020767 | 61.5341 | 0.007721 | 61.3123 | 61.4667 | 61.4143 | 61.4428 | 61.4755 | 61.4956 | 61.4763 | 61.4974 | 123.0056 | 61.6576 | 122.9323 | 61.4079 | 61.4755 | 122.9889 | 61.4625 | 122.7671 | 61.5301 | 61.5431 | 61.4567 | 61.4698
1073.8906 | 123.1888 | -61.4456 | 61.5967 | 0.01197 | -0.026784 | -0.007421 | 0.020768 | 0.040843 | 0.026064 | 0.042581 | 61.5463 | 0.20284 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.4576 | 61.4188 | 61.4382 | 61.4664 | 61.4865 | 61.4717 | 61.4882 | 122.9919 | 61.6485 | 122.9231 | 61.3988 | 61.4664 | 122.9752 | 61.4442 | 122.7579 | 61.5255 | 61.5477 | 61.4567 | 61.4789
1074.8906 | 123.1842 | -61.4548 | 61.6196 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.040843 | 0.021485 | 0.047159 | 61.5463 | 0.20284 | 61.4775 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3077 | 61.4667 | 61.4234 | 61.4474 | 61.4664 | 61.4956 | 61.4763 | 61.5019 | 123.001 | 61.6576 | 122.9323 | 61.4034 | 61.4755 | 122.9889 | 61.4533 | 122.7625 | 61.5255 | 61.5477 | 61.4567 | 61.4789
1075.9062 | 123.1888 | -61.4319 | 61.5921 | 0.01197 | -0.026784 | -0.002842 | 0.01619 | 0.045421 | 0.021485 | 0.051737 | 61.5508 | 0.19827 | 61.4821 | -0.046838 | 0.016188 | 61.5295 | 0.003143 | 61.3123 | 61.4439 | 61.4051 | 61.429 | 61.4481 | 61.4773 | 61.4534 | 61.4836 | 122.9827 | 61.6302 | 122.914 | 61.385 | 61.4481 | 122.9614 | 61.435 | 122.7442 | 61.5346 | 61.5477 | 61.4659 | 61.4789
1076.8906 | 123.1796 | -61.4639 | 61.615 | 0.01197 | -0.031363 | -0.002842 | 0.01619 | 0.045421 | 0.016907 | 0.047159 | 61.5463 | 0.19827 | 61.4775 | -0.046838 | 0.016188 | 61.5341 | -0.006014 | 61.3077 | 61.4759 | 61.4326 | 61.4611 | 61.4801 | 61.5093 | 61.4808 | 61.5111 | 123.0102 | 61.6622 | 122.9414 | 61.4171 | 61.4801 | 122.998 | 61.4579 | 122.7717 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1077.8906 | 123.2758 | -61.441 | 61.5509 | 0.016548 | -0.031363 | -0.007421 | 0.01619 | 0.045421 | 0.016907 | 0.047159 | 61.5417 | 0.19369 | 61.4867 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3077 | 61.4576 | 61.4097 | 61.4336 | 61.4572 | 61.4865 | 61.4579 | 61.4882 | 122.9827 | 61.6347 | 122.9277 | 61.3896 | 61.4618 | 122.9752 | 61.435 | 122.7488 | 61.5209 | 61.5477 | 61.4659 | 61.4927
1078.8906 | 123.317 | -61.4319 | 61.5326 | 0.01197 | -0.035942 | -0.016578 | 0.011611 | 0.036265 | 0.012329 | 0.033424 | 61.5371 | 0.20284 | 61.4684 | -0.046838 | 0.016188 | 61.5387 | -0.006014 | 61.294 | 61.4439 | 61.3959 | 61.4153 | 61.4435 | 61.4682 | 61.4442 | 61.4653 | 122.969 | 61.6347 | 122.9002 | 61.385 | 61.4481 | 122.9706 | 61.4259 | 122.7259 | 61.5209 | 61.5431 | 61.4522 | 61.4744
1079.8906 | 123.1796 | -61.4456 | 61.5738 | 0.021127 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.016907 | 0.042581 | 61.5463 | 0.20284 | 61.4821 | -0.055996 | 0.029923 | 61.5295 | -0.010593 | 61.3123 | 61.4667 | 61.4097 | 61.4336 | 61.4527 | 61.4819 | 61.4625 | 61.4882 | 122.9919 | 61.6485 | 122.9277 | 61.3896 | 61.4755 | 122.9752 | 61.435 | 122.7579 | 61.5163 | 61.5568 | 61.4522 | 61.4927
1080.8906 | 123.1934 | -61.4365 | 61.6241 | 0.01197 | -0.035942 | -0.007421 | 0.011611 | 0.040843 | 0.016907 | 0.033424 | 61.5463 | 0.19369 | 61.4775 | -0.051417 | 0.034501 | 61.5295 | -0.001436 | 61.3123 | 61.4484 | 61.4005 | 61.429 | 61.4481 | 61.4773 | 61.4534 | 61.4699 | 122.9827 | 61.6302 | 122.914 | 61.385 | 61.471 | 122.966 | 61.435 | 122.7488 | 61.5118 | 61.5477 | 61.443 | 61.4789
1081.8906 | 123.1522 | -61.4548 | 61.5921 | 0.01197 | -0.026784 | -0.007421 | 0.011611 | 0.040843 | 0.016907 | 0.038003 | 61.5463 | 0.19827 | 61.4821 | -0.051417 | 0.025345 | 61.5295 | -0.006014 | 61.3169 | 61.4667 | 61.428 | 61.4474 | 61.4664 | 61.4956 | 61.4717 | 61.4928 | 123.001 | 61.653 | 122.9369 | 61.4034 | 61.4801 | 122.9843 | 61.4488 | 122.7717 | 61.5209 | 61.5523 | 61.4567 | 61.4881
1082.8906 | 123.2025 | -61.4548 | 61.615 | 0.01197 | -0.035942 | -0.016578 | 0.01619 | 0.049999 | 0.016907 | 0.042581 | 61.5463 | 0.20284 | 61.4729 | -0.046838 | 0.029923 | 61.5295 | -0.001436 | 61.3077 | 61.4667 | 61.4188 | 61.4382 | 61.471 | 61.5048 | 61.4717 | 61.4974 | 123.001 | 61.6576 | 122.9277 | 61.4079 | 61.4847 | 122.9843 | 61.4533 | 122.7625 | 61.5163 | 61.5477 | 61.443 | 61.4744
1083.8906 | 123.317 | -61.441 | 61.5234 | 0.016548 | -0.031363 | -0.007421 | 0.011611 | 0.040843 | 0.016907 | 0.042581 | 61.5463 | 0.19827 | 61.4684 | -0.051417 | 0.020767 | 61.525 | -0.010593 | 61.3077 | 61.4576 | 61.4097 | 61.4336 | 61.4527 | 61.4819 | 61.4579 | 61.4836 | 122.9873 | 61.6393 | 122.9094 | 61.3896 | 61.4618 | 122.966 | 61.4304 | 122.7488 | 61.5255 | 61.5568 | 61.4476 | 61.4789
1084.8906 | 123.1979 | -61.4594 | 61.5692 | 0.021127 | -0.031363 | -0.007421 | 0.007033 | 0.040843 | 0.016907 | 0.042581 | 61.5463 | 0.19827 | 61.4729 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.4805 | 61.428 | 61.4519 | 61.4664 | 61.5002 | 61.4763 | 61.5019 | 123.0056 | 61.6576 | 122.9323 | 61.4079 | 61.4801 | 122.9889 | 61.4579 | 122.7717 | 61.5255 | 61.5477 | 61.4522 | 61.4744
1085.8906 | 123.2712 | -61.4273 | 61.5417 | 0.016548 | -0.035942 | -0.007421 | 0.011611 | 0.036265 | 0.016907 | 0.033424 | 61.5463 | 0.20284 | 61.4729 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3031 | 61.4439 | 61.3914 | 61.4199 | 61.4389 | 61.4636 | 61.4442 | 61.4607 | 122.9736 | 61.6302 | 122.9002 | 61.3805 | 61.4481 | 122.9614 | 61.4259 | 122.7305 | 61.5255 | 61.5477 | 61.4522 | 61.4744
1086.8906 | 123.3215 | -61.4273 | 61.5463 | 0.016548 | -0.026784 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.047159 | 61.5463 | 0.19827 | 61.4729 | -0.046838 | 0.016188 | 61.5387 | 0.003143 | 61.3169 | 61.4439 | 61.4005 | 61.4153 | 61.4389 | 61.4636 | 61.4396 | 61.4745 | 122.9736 | 61.6256 | 122.9002 | 61.3805 | 61.4435 | 122.966 | 61.4305 | 122.7442 | 61.5301 | 61.5431 | 61.4567 | 61.4698
1087.8906 | 123.2803 | -61.4182 | 61.5417 | 0.01197 | -0.035942 | -0.002842 | 0.011611 | 0.036265 | 0.012329 | 0.033424 | 61.5463 | 0.19827 | 61.4729 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.4301 | 61.3822 | 61.4153 | 61.4298 | 61.4544 | 61.4305 | 61.4516 | 122.9644 | 61.6164 | 122.8911 | 61.3667 | 61.4435 | 122.9477 | 61.4167 | 122.7259 | 61.5209 | 61.5477 | 61.4476 | 61.4744
1088.8906 | 123.2117 | -61.4594 | 61.5692 | 0.01197 | -0.040521 | -0.002842 | 0.011611 | 0.040843 | 0.012329 | 0.042581 | 61.5463 | 0.20284 | 61.4775 | -0.051417 | 0.020767 | 61.5341 | 0.007721 | 61.3077 | 61.4713 | 61.4188 | 61.4565 | 61.471 | 61.5002 | 61.4717 | 61.5019 | 123.0056 | 61.6622 | 122.9369 | 61.4079 | 61.4801 | 122.9935 | 61.4671 | 122.7671 | 61.5255 | 61.5385 | 61.4567 | 61.4698
1089.8906 | 123.317 | -61.4182 | 61.5234 | 0.01197 | -0.031363 | -0.012 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5417 | 0.19827 | 61.4729 | -0.042259 | 0.020767 | 61.5341 | -0.006014 | 61.3077 | 61.4301 | 61.3868 | 61.4062 | 61.4252 | 61.4544 | 61.4305 | 61.4562 | 122.9598 | 61.6164 | 122.8911 | 61.3759 | 61.4389 | 122.9523 | 61.4121 | 122.7259 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1090.8906 | 123.2574 | -61.4319 | 61.5646 | 0.01197 | -0.035942 | -0.012 | 0.007033 | 0.036265 | 0.016907 | 0.038003 | 61.5417 | 0.19369 | 61.4775 | -0.051417 | 0.016188 | 61.5341 | 0.003143 | 61.3123 | 61.4439 | 61.3959 | 61.4199 | 61.4389 | 61.4682 | 61.4488 | 61.4699 | 122.9736 | 61.6256 | 122.9094 | 61.3805 | 61.4481 | 122.966 | 61.435 | 122.7442 | 61.5255 | 61.5385 | 61.4613 | 61.4744
1091.8906 | 123.2483 | -61.441 | 61.5646 | 0.01197 | -0.035942 | -0.012 | 0.002454 | 0.036265 | 0.016907 | 0.042581 | 61.5463 | 0.19827 | 61.4684 | -0.055996 | 0.020767 | 61.5341 | -0.001436 | 61.3077 | 61.453 | 61.4051 | 61.429 | 61.4435 | 61.4773 | 61.4579 | 61.4836 | 122.9873 | 61.6393 | 122.9094 | 61.385 | 61.4618 | 122.9752 | 61.4396 | 122.7488 | 61.5255 | 61.5477 | 61.4476 | 61.4698
1092.8906 | 123.3032 | -61.3998 | 61.5189 | 0.007391 | -0.031363 | -0.012 | 0.011611 | 0.036265 | 0.016907 | 0.042581 | 61.5463 | 0.20742 | 61.4684 | -0.051417 | 0.020767 | 61.5204 | -0.001436 | 61.3077 | 61.4072 | 61.3685 | 61.3878 | 61.4115 | 61.4361 | 61.4167 | 61.4424 | 122.9461 | 61.6073 | 122.8682 | 61.3484 | 61.4206 | 122.9202 | 61.3984 | 122.7076 | 61.5255 | 61.5477 | 61.4476 | 61.4698
1093.8906 | 123.3124 | -61.441 | 61.528 | 0.01197 | -0.035942 | -0.012 | 0.01619 | 0.040843 | 0.00775 | 0.038003 | 61.5417 | 0.19369 | 61.4775 | -0.042259 | 0.020767 | 61.5295 | -0.006014 | 61.3077 | 61.453 | 61.4051 | 61.429 | 61.4572 | 61.4819 | 61.4488 | 61.479 | 122.9827 | 61.6347 | 122.9186 | 61.3988 | 61.4618 | 122.9706 | 61.435 | 122.7488 | 61.5209 | 61.5477 | 61.4567 | 61.4835
1094.8906 | 123.2208 | -61.4319 | 61.5646 | 0.016548 | -0.031363 | -0.012 | 0.011611 | 0.045421 | 0.012329 | 0.042581 | 61.5463 | 0.19827 | 61.4729 | -0.046838 | 0.029923 | 61.5295 | -0.001436 | 61.3123 | 61.4484 | 61.4005 | 61.4199 | 61.4435 | 61.4773 | 61.4442 | 61.4745 | 122.9781 | 61.6302 | 122.9048 | 61.385 | 61.4618 | 122.9614 | 61.4304 | 122.7442 | 61.5163 | 61.5477 | 61.443 | 61.4744
1095.9062 | 123.2254 | -61.4319 | 61.6425 | 0.007391 | -0.026784 | -0.007421 | 0.01619 | 0.036265 | 0.021485 | 0.047159 | 61.56 | 0.19369 | 61.4775 | -0.051417 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4393 | 61.4051 | 61.4245 | 61.4481 | 61.4682 | 61.4534 | 61.479 | 122.9919 | 61.6256 | 122.9094 | 61.3805 | 61.4572 | 122.966 | 61.4304 | 122.7488 | 61.5346 | 61.5614 | 61.4522 | 61.4789
1096.8906 | 123.2895 | -61.4456 | 61.5417 | 0.01197 | -0.026784 | -0.012 | 0.002454 | 0.031687 | 0.016907 | 0.038003 | 61.5508 | 0.20284 | 61.4684 | -0.046838 | 0.020767 | 61.5387 | -0.010593 | 61.3031 | 61.4576 | 61.4188 | 61.4336 | 61.4481 | 61.4773 | 61.4625 | 61.4836 | 122.9965 | 61.6485 | 122.914 | 61.3988 | 61.4664 | 122.9843 | 61.435 | 122.7488 | 61.5301 | 61.5614 | 61.4476 | 61.4789
1097.8906 | 123.2437 | -61.4548 | 61.5326 | 0.016548 | -0.040521 | -0.012 | 0.011611 | 0.036265 | 0.00775 | 0.038003 | 61.5508 | 0.19827 | 61.4684 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3123 | 61.4713 | 61.4143 | 61.4428 | 61.4664 | 61.491 | 61.4625 | 61.4928 | 123.0056 | 61.653 | 122.9231 | 61.4079 | 61.4755 | 122.9889 | 61.4533 | 122.7671 | 61.5301 | 61.5523 | 61.4476 | 61.4698
1098.8906 | 123.2437 | -61.4456 | 61.5784 | -0.001765 | -0.035942 | -0.007421 | 0.002454 | 0.040843 | 0.012329 | 0.038003 | 61.5463 | 0.19369 | 61.4775 | -0.051417 | 0.01161 | 61.5387 | -0.001436 | 61.3169 | 61.4439 | 61.4097 | 61.4382 | 61.4481 | 61.4865 | 61.4579 | 61.4836 | 122.9919 | 61.6393 | 122.9231 | 61.3942 | 61.4572 | 122.9843 | 61.4442 | 122.7625 | 61.5346 | 61.5477 | 61.4659 | 61.4789
1099.8906 | 123.262 | -61.4182 | 61.5601 | 0.01197 | -0.026784 | -0.007421 | 0.007033 | 0.040843 | 0.021485 | 0.038003 | 61.5508 | 0.20284 | 61.4684 | -0.051417 | 0.016188 | 61.5341 | 0.003143 | 61.3123 | 61.4301 | 61.3914 | 61.4107 | 61.4252 | 61.459 | 61.4396 | 61.4562 | 122.969 | 61.621 | 122.8865 | 61.3667 | 61.4343 | 122.9523 | 61.4213 | 122.7305 | 61.5346 | 61.5477 | 61.4522 | 61.4652
1100.8906 | 123.3032 | -61.409 | 61.5509 | 0.01197 | -0.031363 | -0.016578 | 0.011611 | 0.040843 | 0.012329 | 0.047159 | 61.5417 | 0.20284 | 61.4729 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3031 | 61.421 | 61.3776 | 61.3924 | 61.4206 | 61.4498 | 61.4213 | 61.4562 | 122.9507 | 61.6118 | 122.8819 | 61.3576 | 61.4298 | 122.9431 | 61.403 | 122.7121 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1101.8906 | 123.2391 | -61.4594 | 61.5509 | 0.01197 | -0.031363 | -0.007421 | 0.01619 | 0.027109 | 0.00775 | 0.047159 | 61.5554 | 0.19827 | 61.4821 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.4713 | 61.428 | 61.4519 | 61.4755 | 61.4865 | 61.4671 | 61.5065 | 123.0148 | 61.6576 | 122.9414 | 61.4079 | 61.4801 | 122.9889 | 61.4579 | 122.7717 | 61.5346 | 61.5568 | 61.4613 | 61.4835
1102.8906 | 123.2208 | -61.441 | 61.5555 | 0.007391 | -0.035942 | -0.012 | 0.01619 | 0.031687 | 0.016907 | 0.033424 | 61.5508 | 0.19827 | 61.4775 | -0.046838 | 0.016188 | 61.5341 | 0.003143 | 61.3169 | 61.4484 | 61.4051 | 61.429 | 61.4572 | 61.4727 | 61.4579 | 61.4745 | 122.9919 | 61.6393 | 122.9186 | 61.3942 | 61.4572 | 122.9752 | 61.4442 | 122.7579 | 61.5346 | 61.5477 | 61.4613 | 61.4744
1103.8906 | 123.2986 | -61.4502 | 61.5646 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | 0.016907 | 0.038003 | 61.5463 | 0.19827 | 61.4775 | -0.042259 | 0.020767 | 61.525 | -0.006014 | 61.3123 | 61.4622 | 61.4188 | 61.4428 | 61.4618 | 61.4819 | 61.4671 | 61.4882 | 122.9965 | 61.6485 | 122.9277 | 61.4079 | 61.471 | 122.9752 | 61.4442 | 122.7625 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1104.8906 | 123.317 | -61.4456 | 61.5646 | 0.016548 | -0.026784 | -0.007421 | 0.011611 | 0.036265 | 0.012329 | 0.033424 | 61.5463 | 0.19827 | 61.4775 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.4622 | 61.4188 | 61.4382 | 61.4572 | 61.4819 | 61.4579 | 61.479 | 122.9919 | 61.6439 | 122.9231 | 61.3988 | 61.471 | 122.9752 | 61.4442 | 122.7533 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1105.8906 | 123.1796 | -61.4273 | 61.5967 | 0.01197 | -0.035942 | -0.002842 | 0.020768 | 0.040843 | 0.021485 | 0.042581 | 61.5463 | 0.19827 | 61.4867 | -0.046838 | 0.025345 | 61.525 | -0.006014 | 61.3169 | 61.4393 | 61.3914 | 61.4245 | 61.4481 | 61.4682 | 61.4488 | 61.4699 | 122.9736 | 61.6256 | 122.914 | 61.3805 | 61.4527 | 122.9523 | 61.4213 | 122.7442 | 61.5209 | 61.5523 | 61.4613 | 61.4927
1106.8906 | 123.262 | -61.4456 | 61.5646 | 0.007391 | -0.0451 | -0.007421 | 0.007033 | 0.040843 | 0.00775 | 0.042581 | 61.5463 | 0.19369 | 61.4684 | -0.046838 | 0.01161 | 61.5295 | -0.001436 | 61.3077 | 61.453 | 61.4005 | 61.4382 | 61.4527 | 61.4865 | 61.4534 | 61.4882 | 122.9919 | 61.6393 | 122.914 | 61.3988 | 61.4572 | 122.9752 | 61.4442 | 122.7533 | 61.5346 | 61.5477 | 61.4567 | 61.4698
1107.8906 | 123.3261 | -61.4273 | 61.5555 | 0.01197 | -0.035942 | -0.007421 | 0.007033 | 0.040843 | 0.016907 | 0.038003 | 61.5371 | 0.20742 | 61.4729 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4393 | 61.3914 | 61.4199 | 61.4343 | 61.4682 | 61.4442 | 61.4653 | 122.9644 | 61.6347 | 122.9002 | 61.3759 | 61.4527 | 122.9568 | 61.4259 | 122.7396 | 61.5118 | 61.5385 | 61.4476 | 61.4744
1108.8906 | 123.2666 | -61.4182 | 61.5555 | 0.007391 | -0.031363 | -0.007421 | 0.011611 | 0.036265 | 0.021485 | 0.047159 | 61.5508 | 0.19369 | 61.4775 | -0.055996 | 0.025345 | 61.5295 | 0.007721 | 61.3169 | 61.4255 | 61.3868 | 61.4107 | 61.4298 | 61.4544 | 61.4396 | 61.4653 | 122.969 | 61.6118 | 122.8957 | 61.3622 | 61.4435 | 122.9477 | 61.4259 | 122.735 | 61.5255 | 61.5431 | 61.4522 | 61.4698
1109.8906 | 123.2254 | -61.441 | 61.5646 | 0.007391 | -0.031363 | -0.002842 | 0.011611 | 0.040843 | 0.021485 | 0.038003 | 61.5417 | 0.19369 | 61.4775 | -0.051417 | 0.029923 | 61.5295 | -0.006014 | 61.3077 | 61.4484 | 61.4097 | 61.4382 | 61.4527 | 61.4819 | 61.4625 | 61.479 | 122.9827 | 61.6347 | 122.9186 | 61.3896 | 61.471 | 122.9706 | 61.435 | 122.7488 | 61.5118 | 61.5477 | 61.4476 | 61.4835
1110.8906 | 123.2574 | -61.4456 | 61.5326 | 0.01197 | -0.026784 | -0.007421 | 0.01619 | 0.045421 | 0.012329 | 0.033424 | 61.5554 | 0.20284 | 61.4729 | -0.055996 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.4576 | 61.4188 | 61.4382 | 61.4618 | 61.491 | 61.4579 | 61.479 | 123.001 | 61.6485 | 122.9186 | 61.3896 | 61.4664 | 122.9752 | 61.4442 | 122.7533 | 61.5346 | 61.5568 | 61.4522 | 61.4744
1111.8906 | 123.2941 | -61.4227 | 61.5601 | 0.016548 | -0.031363 | -0.002842 | 0.01619 | 0.036265 | 0.012329 | 0.042581 | 61.5463 | 0.20284 | 61.4821 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3077 | 61.4393 | 61.3914 | 61.4199 | 61.4389 | 61.459 | 61.4351 | 61.4653 | 122.969 | 61.6256 | 122.9048 | 61.3713 | 61.4435 | 122.9568 | 61.4259 | 122.7305 | 61.5255 | 61.5431 | 61.4613 | 61.4789
1112.8906 | 123.2849 | -61.4365 | 61.5921 | 0.007391 | -0.031363 | 0.006315 | 0.007033 | 0.040843 | 0.00775 | 0.038003 | 61.5463 | 0.20284 | 61.4775 | -0.051417 | 0.025345 | 61.5295 | -0.006014 | 61.3169 | 61.4439 | 61.4051 | 61.4428 | 61.4435 | 61.4773 | 61.4442 | 61.4745 | 122.9827 | 61.6393 | 122.914 | 61.385 | 61.4618 | 122.966 | 61.4304 | 122.7533 | 61.5209 | 61.5523 | 61.4522 | 61.4835
1113.8906 | 123.2437 | -61.4502 | 61.5646 | 0.016548 | -0.031363 | -0.007421 | 0.020768 | 0.040843 | 0.016907 | 0.042581 | 61.5508 | 0.19369 | 61.4867 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3077 | 61.4667 | 61.4188 | 61.4428 | 61.471 | 61.491 | 61.4671 | 61.4928 | 123.001 | 61.6439 | 122.9369 | 61.4034 | 61.471 | 122.9843 | 61.4488 | 122.7579 | 61.5301 | 61.5523 | 61.4659 | 61.4881
1114.8906 | 123.317 | -61.4136 | 61.5555 | 0.007391 | -0.035942 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.042581 | 61.5463 | 0.19827 | 61.4775 | -0.051417 | 0.029923 | 61.5341 | 0.003143 | 61.3123 | 61.421 | 61.3776 | 61.4016 | 61.4252 | 61.4498 | 61.4259 | 61.4562 | 122.9598 | 61.6118 | 122.8911 | 61.3622 | 61.4435 | 122.9477 | 61.4167 | 122.7259 | 61.5163 | 61.5431 | 61.4476 | 61.4744
1115.8906 | 123.1705 | -61.4731 | 61.6013 | 0.007391 | -0.031363 | -0.007421 | 0.025347 | 0.045421 | 0.016907 | 0.047159 | 61.5463 | 0.19827 | 61.4729 | -0.042259 | 0.016188 | 61.5341 | -0.010593 | 61.3123 | 61.4805 | 61.4417 | 61.4657 | 61.4984 | 61.5185 | 61.49 | 61.5202 | 123.0193 | 61.6713 | 122.946 | 61.4308 | 61.4893 | 123.0072 | 61.4625 | 122.7854 | 61.5301 | 61.5568 | 61.4567 | 61.4835
1116.8906 | 123.3032 | -61.3998 | 61.5601 | 0.016548 | -0.026784 | -0.002842 | 0.011611 | 0.045421 | 0.012329 | 0.038003 | 61.5463 | 0.20284 | 61.4729 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4164 | 61.3731 | 61.397 | 61.4115 | 61.4453 | 61.4122 | 61.4378 | 122.9461 | 61.6027 | 122.8728 | 61.3484 | 61.4252 | 122.9294 | 61.3984 | 122.7121 | 61.5209 | 61.5477 | 61.4476 | 61.4744
1117.8906 | 123.317 | -61.4044 | 61.5555 | 0.016548 | -0.040521 | -0.002842 | 0.01619 | 0.040843 | 0.016907 | 0.042581 | 61.5417 | 0.19369 | 61.4775 | -0.046838 | 0.025345 | 61.5341 | 0.003143 | 61.3169 | 61.421 | 61.3639 | 61.4016 | 61.4206 | 61.4453 | 61.4213 | 61.447 | 122.9461 | 61.5981 | 122.8819 | 61.3576 | 61.4298 | 122.9385 | 61.4076 | 122.7213 | 61.5163 | 61.5385 | 61.4522 | 61.4744
1118.8906 | 123.2574 | -61.4319 | 61.5875 | 0.021127 | -0.031363 | -0.002842 | 0.01619 | 0.040843 | 0.012329 | 0.038003 | 61.5508 | 0.19827 | 61.4684 | -0.046838 | 0.016188 | 61.5295 | -0.006014 | 61.3077 | 61.453 | 61.4005 | 61.429 | 61.4481 | 61.4727 | 61.4442 | 61.4699 | 122.9827 | 61.6302 | 122.9002 | 61.385 | 61.4481 | 122.9614 | 61.4259 | 122.7396 | 61.5346 | 61.5568 | 61.4522 | 61.4744
1119.8906 | 123.2986 | -61.4273 | 61.5646 | 0.016548 | -0.031363 | -0.007421 | 0.01619 | 0.045421 | 0.012329 | 0.042581 | 61.5508 | 0.19827 | 61.4775 | -0.051417 | 0.025345 | 61.5341 | -0.001436 | 61.3123 | 61.4439 | 61.3959 | 61.4199 | 61.4435 | 61.4727 | 61.4396 | 61.4699 | 122.9781 | 61.6256 | 122.9048 | 61.3759 | 61.4527 | 122.9614 | 61.4259 | 122.7396 | 61.5255 | 61.5523 | 61.4522 | 61.4789
1120.8906 | 123.1796 | -61.4502 | 61.5967 | 0.016548 | -0.022205 | -0.012 | 0.025347 | 0.040843 | 0.026064 | 0.042581 | 61.5463 | 0.20284 | 61.4729 | -0.046838 | 0.025345 | 61.5295 | 0.003143 | 61.3169 | 61.4667 | 61.428 | 61.4382 | 61.4755 | 61.491 | 61.4763 | 61.4928 | 122.9965 | 61.653 | 122.9231 | 61.4034 | 61.4755 | 122.9797 | 61.4533 | 122.7671 | 61.5209 | 61.5431 | 61.4476 | 61.4698
1121.8906 | 123.2071 | -61.4502 | 61.5601 | 0.016548 | -0.026784 | -0.012 | 0.01619 | 0.045421 | 0.00775 | 0.042581 | 61.5417 | 0.20742 | 61.4775 | -0.051417 | 0.016188 | 61.5341 | -0.001436 | 61.3123 | 61.4667 | 61.4234 | 61.4382 | 61.4664 | 61.4956 | 61.4579 | 61.4928 | 122.9919 | 61.6576 | 122.9277 | 61.3988 | 61.4664 | 122.9843 | 61.4488 | 122.7625 | 61.5255 | 61.5431 | 61.4613 | 61.4789
1122.8906 | 123.2941 | -61.4502 | 61.5509 | 0.016548 | -0.031363 | 0.001736 | 0.01619 | 0.036265 | 0.021485 | 0.042581 | 61.5646 | 0.20284 | 61.4821 | -0.055996 | 0.016188 | 61.525 | 0.003143 | 61.3123 | 61.4667 | 61.4188 | 61.4519 | 61.4664 | 61.4865 | 61.4717 | 61.4928 | 123.0148 | 61.653 | 122.9323 | 61.3942 | 61.4664 | 122.9752 | 61.4533 | 122.7625 | 61.5484 | 61.5614 | 61.4659 | 61.4789
1123.8906 | 123.2986 | -61.4136 | 61.5509 | 0.016548 | -0.035942 | -0.012 | 0.011611 | 0.040843 | 0.012329 | 0.042581 | 61.5463 | 0.20284 | 61.4729 | -0.046838 | 0.025345 | 61.5341 | -0.006014 | 61.326 | 61.4301 | 61.3776 | 61.4016 | 61.4252 | 61.4544 | 61.4259 | 61.4562 | 122.9598 | 61.6164 | 122.8865 | 61.3667 | 61.4389 | 122.9477 | 61.4076 | 122.7396 | 61.5209 | 61.5523 | 61.4476 | 61.4789
1124.8906 | 123.1842 | -61.4182 | 61.5555 | 0.007391 | -0.031363 | -0.012 | 0.011611 | 0.040843 | 0.012329 | 0.042581 | 61.5463 | 0.19369 | 61.4821 | -0.055996 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4255 | 61.3868 | 61.4062 | 61.4298 | 61.459 | 61.4305 | 61.4607 | 122.9644 | 61.6118 | 122.9002 | 61.3622 | 61.4435 | 122.9477 | 61.4167 | 122.7305 | 61.5209 | 61.5477 | 61.4567 | 61.4835
1125.8906 | 123.2117 | -61.4273 | 61.5784 | 0.021127 | -0.031363 | -0.002842 | 0.025347 | 0.049999 | 0.016907 | 0.042581 | 61.5554 | 0.20284 | 61.4775 | -0.051417 | 0.025345 | 61.5341 | -0.001436 | 61.3123 | 61.4484 | 61.3959 | 61.4245 | 61.4527 | 61.4773 | 61.4442 | 61.4699 | 122.9827 | 61.6302 | 122.9048 | 61.3759 | 61.4527 | 122.9614 | 61.4259 | 122.7396 | 61.5301 | 61.5568 | 61.4522 | 61.4789
1126.8906 | 123.2254 | -61.441 | 61.5692 | 0.01197 | -0.026784 | 0.001736 | 0.011611 | 0.045421 | 0.012329 | 0.042581 | 61.5554 | 0.19827 | 61.4775 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3169 | 61.453 | 61.4143 | 61.4428 | 61.4527 | 61.4865 | 61.4534 | 61.4836 | 122.9965 | 61.6393 | 122.9186 | 61.3942 | 61.4664 | 122.9706 | 61.4396 | 122.7579 | 61.5301 | 61.5568 | 61.4522 | 61.4789
1127.8906 | 123.2986 | -61.3907 | 61.5692 | 0.01197 | -0.035942 | -0.002842 | 0.011611 | 0.036265 | 0.016907 | 0.042581 | 61.5463 | 0.20284 | 61.4775 | -0.042259 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.4027 | 61.3547 | 61.3878 | 61.4023 | 61.427 | 61.4076 | 61.4333 | 122.9369 | 61.5935 | 122.8682 | 61.3484 | 61.4115 | 122.9202 | 61.3938 | 122.703 | 61.5255 | 61.5431 | 61.4567 | 61.4744
1128.8906 | 123.3398 | -61.4136 | 61.5509 | 0.01197 | -0.031363 | 0.001736 | 0.01619 | 0.045421 | 0.012329 | 0.042581 | 61.5508 | 0.20284 | 61.4775 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3215 | 61.4255 | 61.3822 | 61.4153 | 61.4298 | 61.459 | 61.4259 | 61.4562 | 122.9644 | 61.6164 | 122.8911 | 61.3622 | 61.4343 | 122.9477 | 61.4121 | 122.735 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1129.8906 | 123.2895 | -61.4365 | 61.5738 | 0.01197 | -0.035942 | -0.012 | 0.01619 | 0.040843 | 0.00775 | 0.038003 | 61.5463 | 0.19827 | 61.4729 | -0.042259 | 0.025345 | 61.5341 | -0.001436 | 61.3123 | 61.4484 | 61.4005 | 61.4245 | 61.4527 | 61.4773 | 61.4442 | 61.4745 | 122.9827 | 61.6347 | 122.9094 | 61.3942 | 61.4618 | 122.9706 | 61.435 | 122.7488 | 61.5209 | 61.5477 | 61.4476 | 61.4744
1130.8906 | 123.1888 | -61.4594 | 61.5738 | 0.021127 | -0.031363 | -0.007421 | 0.025347 | 0.049999 | 0.021485 | 0.047159 | 61.5508 | 0.20284 | 61.4775 | -0.055996 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.4805 | 61.428 | 61.4519 | 61.4847 | 61.5093 | 61.4808 | 61.5065 | 123.0102 | 61.6622 | 122.9369 | 61.4034 | 61.4801 | 122.9889 | 61.4579 | 122.7717 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1131.8906 | 123.317 | -61.4044 | 61.5417 | 0.01197 | -0.040521 | 0.001736 | 0.011611 | 0.045421 | 0.016907 | 0.042581 | 61.5508 | 0.212 | 61.4775 | -0.046838 | 0.020767 | 61.5341 | -0.001436 | 61.3215 | 61.4164 | 61.3639 | 61.4062 | 61.416 | 61.4498 | 61.4213 | 61.447 | 122.9553 | 61.6164 | 122.8819 | 61.3576 | 61.4252 | 122.9385 | 61.403 | 122.7259 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1132.8906 | 123.3078 | -61.4273 | 61.5784 | 0.01197 | -0.026784 | -0.007421 | 0.020768 | 0.036265 | 0.016907 | 0.042581 | 61.5508 | 0.19827 | 61.4775 | -0.042259 | 0.025345 | 61.525 | -0.001436 | 61.3123 | 61.4393 | 61.4005 | 61.4199 | 61.4481 | 61.4636 | 61.4442 | 61.4699 | 122.9781 | 61.6256 | 122.9048 | 61.385 | 61.4527 | 122.9523 | 61.4259 | 122.7396 | 61.5255 | 61.5523 | 61.4522 | 61.4789
1133.8906 | 123.2483 | -61.441 | 61.5509 | 0.01197 | -0.031363 | -0.002842 | 0.01619 | 0.040843 | 0.012329 | 0.042581 | 61.5508 | 0.20742 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.453 | 61.4097 | 61.4382 | 61.4572 | 61.4819 | 61.4534 | 61.4836 | 122.9919 | 61.6485 | 122.9186 | 61.3942 | 61.4618 | 122.9706 | 61.4396 | 122.7488 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1134.8906 | 123.2208 | -61.4136 | 61.5784 | 0.007391 | -0.031363 | -0.002842 | 0.011611 | 0.036265 | 0.021485 | 0.042581 | 61.5508 | 0.20284 | 61.4775 | -0.046838 | 0.020767 | 61.5204 | -0.006014 | 61.3123 | 61.421 | 61.3822 | 61.4107 | 61.4252 | 61.4498 | 61.4351 | 61.4562 | 122.9644 | 61.6164 | 122.8911 | 61.3667 | 61.4343 | 122.934 | 61.4076 | 122.7259 | 61.5301 | 61.5568 | 61.4567 | 61.4835
1135.8906 | 123.2391 | -61.4273 | 61.6013 | 0.002813 | -0.031363 | -0.007421 | 0.020768 | 0.040843 | 0.016907 | 0.042581 | 61.5463 | 0.19369 | 61.4775 | -0.051417 | 0.020767 | 61.525 | -0.006014 | 61.3123 | 61.4301 | 61.3959 | 61.4199 | 61.4481 | 61.4682 | 61.4442 | 61.4699 | 122.9736 | 61.621 | 122.9048 | 61.3759 | 61.4481 | 122.9523 | 61.4213 | 122.7396 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1136.8906 | 123.2071 | -61.3724 | 61.6104 | 0.021127 | -0.035942 | -0.007421 | 0.01619 | 0.036265 | 0.021485 | 0.042581 | 61.5417 | 0.19827 | 61.4775 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3123 | 61.3935 | 61.3364 | 61.365 | 61.3886 | 61.4086 | 61.3939 | 61.415 | 122.9141 | 61.5706 | 122.8499 | 61.321 | 61.3931 | 122.9065 | 61.3709 | 122.6847 | 61.5209 | 61.5431 | 61.4567 | 61.4789
1137.8906 | 123.2758 | -61.4182 | 61.5601 | 0.007391 | -0.031363 | -0.012 | 0.01619 | 0.027109 | 0.00775 | 0.038003 | 61.5508 | 0.20284 | 61.4867 | -0.051417 | 0.016188 | 61.5295 | 0.003143 | 61.3077 | 61.4255 | 61.3868 | 61.4062 | 61.4343 | 61.4453 | 61.4259 | 61.4562 | 122.969 | 61.621 | 122.9048 | 61.3667 | 61.4343 | 122.9477 | 61.4213 | 122.7259 | 61.5346 | 61.5477 | 61.4705 | 61.4835
1138.8906 | 123.2849 | -61.4044 | 61.5738 | 0.01197 | -0.040521 | -0.007421 | 0.011611 | 0.040843 | 0.012329 | 0.042581 | 61.5463 | 0.20284 | 61.4821 | -0.051417 | 0.025345 | 61.525 | 0.003143 | 61.3077 | 61.4164 | 61.3639 | 61.397 | 61.416 | 61.4453 | 61.4167 | 61.447 | 122.9507 | 61.6073 | 122.8865 | 61.353 | 61.4298 | 122.9294 | 61.4076 | 122.7121 | 61.5209 | 61.5431 | 61.4567 | 61.4789
1139.8906 | 123.2986 | -61.4182 | 61.5875 | 0.01197 | -0.040521 | -0.007421 | 0.007033 | 0.031687 | 0.012329 | 0.038003 | 61.5417 | 0.20284 | 61.4821 | -0.042259 | 0.020767 | 61.5341 | 0.007721 | 61.3169 | 61.4301 | 61.3776 | 61.4107 | 61.4252 | 61.4498 | 61.4305 | 61.4562 | 122.9598 | 61.621 | 122.9002 | 61.3759 | 61.4389 | 122.9523 | 61.4259 | 122.735 | 61.5209 | 61.534 | 61.4613 | 61.4744
1140.8906 | 123.1842 | -61.4365 | 61.6058 | 0.016548 | -0.031363 | -0.016578 | 0.01619 | 0.040843 | 0.016907 | 0.051737 | 61.5508 | 0.19369 | 61.4821 | -0.046838 | 0.029923 | 61.5295 | -0.006014 | 61.3123 | 61.453 | 61.4051 | 61.4199 | 61.4527 | 61.4773 | 61.4534 | 61.4882 | 122.9873 | 61.6302 | 122.9185 | 61.3896 | 61.4664 | 122.966 | 61.4304 | 122.7488 | 61.5209 | 61.5568 | 61.4522 | 61.4881
1141.8906 | 123.1979 | -61.409 | 61.6379 | 0.01197 | -0.035942 | -0.007421 | 0.002454 | 0.031687 | 0.012329 | 0.042581 | 61.5508 | 0.20284 | 61.4775 | -0.051417 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.421 | 61.3731 | 61.4016 | 61.4115 | 61.4407 | 61.4213 | 61.4516 | 122.9598 | 61.6118 | 122.8865 | 61.3576 | 61.4298 | 122.9385 | 61.4076 | 122.7167 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1142.8906 | 123.3032 | -61.4227 | 61.5646 | 0.007391 | -0.035942 | -0.012 | 0.002454 | 0.040843 | 0.012329 | 0.038003 | 61.5463 | 0.20284 | 61.4775 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4301 | 61.3868 | 61.4107 | 61.4252 | 61.4636 | 61.4351 | 61.4607 | 122.969 | 61.6256 | 122.9002 | 61.3759 | 61.4481 | 122.9568 | 61.4213 | 122.7396 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1143.8906 | 123.3261 | -61.409 | 61.5738 | 0.016548 | -0.035942 | -0.012 | 0.011611 | 0.036265 | 0.012329 | 0.042581 | 61.5554 | 0.20742 | 61.4775 | -0.055996 | 0.029923 | 61.5295 | 0.003143 | 61.3031 | 61.4255 | 61.3731 | 61.397 | 61.4206 | 61.4453 | 61.4213 | 61.4516 | 122.9644 | 61.6164 | 122.8865 | 61.353 | 61.4389 | 122.9385 | 61.4121 | 122.7121 | 61.5255 | 61.5523 | 61.4476 | 61.4744
1144.8906 | 123.262 | -61.3907 | 61.5601 | 0.007391 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.012329 | 0.038003 | 61.5417 | 0.19827 | 61.4821 | -0.042259 | 0.025345 | 61.525 | 0.003143 | 61.3123 | 61.3981 | 61.3547 | 61.3833 | 61.3977 | 61.427 | 61.403 | 61.4287 | 122.9324 | 61.589 | 122.8728 | 61.3484 | 61.416 | 122.9156 | 61.3938 | 122.703 | 61.5163 | 61.5385 | 61.4567 | 61.4789
1145.8906 | 123.143 | -61.4639 | 61.615 | 0.01197 | -0.035942 | -0.007421 | 0.011611 | 0.036265 | 0.012329 | 0.047159 | 61.5508 | 0.19827 | 61.4775 | -0.055996 | 0.025345 | 61.5295 | 0.003143 | 61.3169 | 61.4759 | 61.428 | 61.4565 | 61.4755 | 61.5002 | 61.4763 | 61.5111 | 123.0148 | 61.6622 | 122.9414 | 61.4079 | 61.4893 | 122.9935 | 61.4671 | 122.7808 | 61.5255 | 61.5477 | 61.4522 | 61.4744
1146.8906 | 123.2803 | -61.409 | 61.5738 | 0.01197 | -0.040521 | -0.002842 | 0.011611 | 0.036265 | 0.012329 | 0.042581 | 61.5417 | 0.19827 | 61.4775 | -0.046838 | 0.025345 | 61.5387 | 0.003143 | 61.3123 | 61.421 | 61.3685 | 61.4062 | 61.4206 | 61.4453 | 61.4213 | 61.4516 | 122.9507 | 61.6073 | 122.8865 | 61.3622 | 61.4343 | 122.9477 | 61.4121 | 122.7213 | 61.5163 | 61.5385 | 61.4522 | 61.4744
1147.8906 | 123.1979 | -61.4273 | 61.5921 | 0.01197 | -0.040521 | -0.007421 | 0.01619 | 0.036265 | 0.012329 | 0.042581 | 61.5463 | 0.20284 | 61.4821 | -0.042259 | 0.020767 | 61.5295 | -0.001436 | 61.3215 | 61.4393 | 61.3868 | 61.4199 | 61.4435 | 61.4636 | 61.4396 | 61.4699 | 122.9736 | 61.6302 | 122.9094 | 61.385 | 61.4481 | 122.9568 | 61.4259 | 122.7488 | 61.5255 | 61.5477 | 61.4613 | 61.4835
1148.8906 | 123.2071 | -61.4273 | 61.6653 | 0.01197 | -0.040521 | -0.012 | 0.011611 | 0.040843 | 0.012329 | 0.038003 | 61.5554 | 0.20284 | 61.4684 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4393 | 61.3868 | 61.4153 | 61.4389 | 61.4682 | 61.4396 | 61.4653 | 122.9827 | 61.6302 | 122.8957 | 61.3759 | 61.4527 | 122.9568 | 61.4259 | 122.7396 | 61.5301 | 61.5568 | 61.443 | 61.4698
1149.8906 | 123.2574 | -61.4182 | 61.5829 | 0.007391 | -0.035942 | -0.007421 | 0.007033 | 0.036265 | 0.021485 | 0.042581 | 61.5554 | 0.19827 | 61.4821 | -0.051417 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.4255 | 61.3822 | 61.4107 | 61.4252 | 61.4544 | 61.4396 | 61.4607 | 122.9736 | 61.6164 | 122.9002 | 61.3667 | 61.4389 | 122.9477 | 61.4213 | 122.7305 | 61.5346 | 61.5523 | 61.4613 | 61.4789
1150.8906 | 123.1888 | -61.4548 | 61.6058 | 0.007391 | -0.0451 | -0.025735 | 0.007033 | 0.031687 | 0.012329 | 0.042581 | 61.5508 | 0.19827 | 61.4775 | -0.055996 | 0.029923 | 61.5341 | -0.001436 | 61.3169 | 61.4622 | 61.4097 | 61.429 | 61.4618 | 61.4865 | 61.4671 | 61.4974 | 123.0056 | 61.653 | 122.9323 | 61.3988 | 61.4847 | 122.9889 | 61.4533 | 122.7717 | 61.5209 | 61.5523 | 61.4476 | 61.4789
1151.8906 | 123.2712 | -61.409 | 61.6013 | 0.007391 | -0.031363 | -0.007421 | 0.011611 | 0.040843 | 0.016907 | 0.042581 | 61.5508 | 0.20742 | 61.4729 | -0.055996 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4164 | 61.3776 | 61.4016 | 61.4206 | 61.4498 | 61.4259 | 61.4516 | 122.9598 | 61.6164 | 122.8819 | 61.353 | 61.4343 | 122.9385 | 61.4076 | 122.7213 | 61.5255 | 61.5523 | 61.4476 | 61.4744
1152.8906 | 123.1705 | -61.4365 | 61.6058 | 0.007391 | -0.035942 | -0.002842 | 0.007033 | 0.040843 | 0.016907 | 0.038003 | 61.56 | 0.20284 | 61.4775 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4439 | 61.4005 | 61.4336 | 61.4435 | 61.4773 | 61.4534 | 61.4745 | 122.9965 | 61.6393 | 122.914 | 61.3896 | 61.4618 | 122.966 | 61.435 | 122.7488 | 61.5346 | 61.5614 | 61.4522 | 61.4789
1153.8906 | 123.1476 | -61.4456 | 61.6196 | 0.007391 | -0.031363 | -0.002842 | 0.002454 | 0.031687 | 0.016907 | 0.042581 | 61.5508 | 0.20742 | 61.4821 | -0.046838 | 0.025345 | 61.5341 | 0.003143 | 61.3169 | 61.453 | 61.4143 | 61.4428 | 61.4481 | 61.4773 | 61.4625 | 61.4882 | 122.9965 | 61.653 | 122.9277 | 61.3988 | 61.471 | 122.9797 | 61.4488 | 122.7625 | 61.5255 | 61.5477 | 61.4567 | 61.4789
1154.8906 | 123.1659 | -61.4456 | 61.6104 | 0.01197 | -0.031363 | -0.007421 | 0.011611 | 0.031687 | 0.003172 | 0.028846 | 61.5417 | 0.19827 | 61.4729 | -0.042259 | 0.020767 | 61.5295 | 0.003143 | 61.3169 | 61.4576 | 61.4143 | 61.4382 | 61.4572 | 61.4773 | 61.4488 | 61.4745 | 122.9873 | 61.6439 | 122.9186 | 61.4034 | 61.4664 | 122.9752 | 61.4488 | 122.7625 | 61.5209 | 61.5385 | 61.4522 | 61.4698
1155.8906 | 123.2529 | -61.4365 | 61.5784 | 0.007391 | -0.035942 | -0.021157 | 0.002454 | 0.036265 | 0.00775 | 0.033424 | 61.5508 | 0.20742 | 61.4775 | -0.051417 | 0.020767 | 61.5204 | 0.003143 | 61.3031 | 61.4439 | 61.4005 | 61.4153 | 61.4389 | 61.4727 | 61.4442 | 61.4699 | 122.9873 | 61.6439 | 122.914 | 61.385 | 61.4572 | 122.9568 | 61.4396 | 122.7396 | 61.5301 | 61.5477 | 61.4567 | 61.4744
1156.8906 | 123.2346 | -61.4182 | 61.6104 | 0.01197 | -0.049678 | -0.016578 | -0.002124 | 0.036265 | 0.00775 | 0.038003 | 61.5554 | 0.20284 | 61.4821 | -0.051417 | 0.034501 | 61.525 | -0.006014 | 61.3077 | 61.4301 | 61.3685 | 61.4016 | 61.416 | 61.4544 | 61.4259 | 61.4562 | 122.9736 | 61.621 | 122.9002 | 61.3667 | 61.4527 | 122.9431 | 61.4121 | 122.7259 | 61.5209 | 61.5614 | 61.4476 | 61.4881
1157.8906 | 123.1796 | -61.4182 | 61.6104 | 0.01197 | -0.035942 | -0.012 | 0.002454 | 0.031687 | 0.012329 | 0.042581 | 61.5508 | 0.19369 | 61.4775 | -0.046838 | 0.025345 | 61.5295 | 0.003143 | 61.3077 | 61.4301 | 61.3822 | 61.4062 | 61.4206 | 61.4498 | 61.4305 | 61.4607 | 122.969 | 61.6118 | 122.8957 | 61.3713 | 61.4435 | 122.9477 | 61.4213 | 122.7259 | 61.5255 | 61.5477 | 61.4522 | 61.4744
1158.8906 | 123.1567 | -61.4227 | 61.6425 | 0.01197 | -0.049678 | -0.007421 | 0.007033 | 0.031687 | 0.00775 | 0.038003 | 61.5508 | 0.19369 | 61.4821 | -0.046838 | 0.025345 | 61.5295 | -0.006014 | 61.3169 | 61.4347 | 61.3731 | 61.4153 | 61.4298 | 61.4544 | 61.4305 | 61.4607 | 122.9736 | 61.6164 | 122.9048 | 61.3759 | 61.4481 | 122.9523 | 61.4167 | 122.7396 | 61.5255 | 61.5568 | 61.4567 | 61.4881
1159.8906 | 123.2346 | -61.4594 | 61.6013 | 0.016548 | -0.049678 | -0.021157 | 0.011611 | 0.027109 | 0.00775 | 0.028846 | 61.5463 | 0.19827 | 61.4867 | -0.046838 | 0.016188 | 61.5295 | -0.001436 | 61.3123 | 61.4759 | 61.4097 | 61.4382 | 61.471 | 61.4865 | 61.4671 | 61.4882 | 123.0056 | 61.6576 | 122.946 | 61.4125 | 61.4755 | 122.9889 | 61.4579 | 122.7717 | 61.5301 | 61.5477 | 61.4705 | 61.4881
1160.8906 | 123.1888 | -61.4639 | 61.615 | 0.007391 | -0.049678 | -0.025735 | -0.006703 | 0.022531 | 0.003172 | 0.028846 | 61.5463 | 0.19827 | 61.4729 | -0.051417 | 0.034501 | 61.5295 | -0.001436 | 61.3123 | 61.4713 | 61.4143 | 61.4382 | 61.4572 | 61.4865 | 61.4671 | 61.4928 | 123.0102 | 61.6622 | 122.9369 | 61.4125 | 61.4984 | 122.9935 | 61.4625 | 122.7762 | 61.5118 | 61.5477 | 61.4384 | 61.4744
1161.8906 | 123.2346 | -61.4456 | 61.6013 | 0.007391 | -0.049678 | -0.021157 | -0.006703 | 0.022531 | -0.001406 | 0.028846 | 61.5554 | 0.20742 | 61.4775 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.453 | 61.3959 | 61.4245 | 61.4389 | 61.4681 | 61.4442 | 61.4745 | 123.001 | 61.653 | 122.9231 | 61.3942 | 61.471 | 122.9752 | 61.4442 | 122.7579 | 61.5301 | 61.5568 | 61.4522 | 61.4789
1162.8906 | 123.2346 | -61.4182 | 61.6516 | 0.016548 | -0.063415 | -0.021157 | -0.011281 | 0.017953 | -0.005985 | 0.024268 | 61.5554 | 0.19827 | 61.4867 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3077 | 61.4347 | 61.3547 | 61.397 | 61.4069 | 61.4361 | 61.4122 | 61.4424 | 122.9736 | 61.6164 | 122.9048 | 61.3713 | 61.4389 | 122.9477 | 61.4213 | 122.7259 | 61.5346 | 61.5523 | 61.4659 | 61.4835
1163.8906 | 123.2071 | -61.4639 | 61.6013 | 0.016548 | -0.058836 | -0.025735 | -0.01586 | 0.013375 | -0.001406 | 0.01969 | 61.5554 | 0.20284 | 61.4867 | -0.042259 | 0.016188 | 61.5341 | -0.006014 | 61.3077 | 61.4805 | 61.4051 | 61.4382 | 61.4481 | 61.4773 | 61.4625 | 61.4836 | 123.0193 | 61.6668 | 122.9506 | 61.4217 | 61.4801 | 122.998 | 61.4579 | 122.7717 | 61.5392 | 61.5614 | 61.4705 | 61.4927
1164.8906 | 123.2346 | -61.4456 | 61.6196 | 0.007391 | -0.072572 | -0.039471 | -0.020438 | 0.017953 | -0.005985 | 0.005955 | 61.5554 | 0.20742 | 61.4821 | -0.042259 | 0.020767 | 61.5204 | 0.003143 | 61.3123 | 61.453 | 61.373 | 61.4061 | 61.4252 | 61.4636 | 61.4396 | 61.4516 | 123.001 | 61.653 | 122.9277 | 61.4034 | 61.4664 | 122.966 | 61.4488 | 122.7579 | 61.5346 | 61.5523 | 61.4613 | 61.4789
1165.8906 | 123.2254 | -61.4365 | 61.5784 | 0.01197 | -0.049678 | -0.030314 | -0.020438 | 0.013375 | -0.010563 | 0.01969 | 61.5463 | 0.19827 | 61.4775 | -0.046838 | 0.01161 | 61.5295 | 0.007721 | 61.3031 | 61.4484 | 61.3868 | 61.4061 | 61.416 | 61.4498 | 61.4259 | 61.4562 | 122.9827 | 61.6347 | 122.914 | 61.3896 | 61.4481 | 122.966 | 61.4442 | 122.7396 | 61.5346 | 61.5385 | 61.4659 | 61.4698
1166.8906 | 123.1934 | -61.441 | 61.6058 | 0.01197 | -0.063415 | -0.034893 | -0.01586 | 0.008797 | -0.015142 | 0.015112 | 61.5508 | 0.20284 | 61.4821 | -0.046838 | 0.029923 | 61.5295 | -0.001436 | 61.3077 | 61.453 | 61.3776 | 61.4061 | 61.4252 | 61.4498 | 61.4259 | 61.4562 | 122.9919 | 61.6439 | 122.9231 | 61.3942 | 61.471 | 122.9706 | 61.4396 | 122.7488 | 61.5209 | 61.5523 | 61.4522 | 61.4835
1167.8906 | 123.23 | -61.441 | 61.6013 | 0.007391 | -0.054257 | -0.039471 | -0.011281 | 0.013375 | -0.015142 | 0.01969 | 61.5554 | 0.20742 | 61.4867 | -0.046838 | 0.025345 | 61.525 | -0.006014 | 61.3077 | 61.4484 | 61.3868 | 61.4016 | 61.4298 | 61.4544 | 61.4259 | 61.4607 | 122.9965 | 61.6485 | 122.9277 | 61.3942 | 61.4664 | 122.966 | 61.435 | 122.7488 | 61.5301 | 61.5614 | 61.4613 | 61.4927
1168.8906 | 123.143 | -61.4548 | 61.5921 | 0.007391 | -0.063415 | -0.039471 | -0.025017 | 0.008797 | -0.024298 | 0.005955 | 61.5554 | 0.20742 | 61.4821 | -0.042259 | 0.020767 | 61.5341 | -0.001436 | 61.3169 | 61.4622 | 61.3914 | 61.4153 | 61.4298 | 61.4636 | 61.4305 | 61.4607 | 123.0102 | 61.6622 | 122.9369 | 61.4125 | 61.4755 | 122.9889 | 61.4533 | 122.7717 | 61.5346 | 61.5568 | 61.4613 | 61.4835
1169.8906 | 123.1796 | -61.4685 | 61.5921 | 0.016548 | -0.067994 | -0.04405 | -0.034174 | -0.000359 | -0.024298 | -0.003201 | 61.5463 | 0.20742 | 61.4775 | -0.051417 | 0.016188 | 61.5341 | -0.006014 | 61.3077 | 61.4851 | 61.4005 | 61.4245 | 61.4343 | 61.4681 | 61.4442 | 61.4653 | 123.0148 | 61.6759 | 122.946 | 61.4171 | 61.4847 | 123.0026 | 61.4625 | 122.7762 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1170.8906 | 123.317 | -61.4319 | 61.528 | 0.007391 | -0.077151 | -0.048628 | -0.034174 | -0.009515 | -0.024298 | 0.001377 | 61.5508 | 0.19827 | 61.4867 | -0.042259 | 0.020767 | 61.525 | -0.006014 | 61.3077 | 61.4393 | 61.3547 | 61.3833 | 61.3977 | 61.4224 | 61.4076 | 61.4333 | 122.9827 | 61.6302 | 122.9186 | 61.3896 | 61.4527 | 122.9568 | 61.4259 | 122.7396 | 61.5301 | 61.5568 | 61.4659 | 61.4927
1171.8906 | 123.1476 | -61.4685 | 61.5875 | 0.007391 | -0.086309 | -0.053207 | -0.043331 | -0.004937 | -0.033455 | 0.001377 | 61.5554 | 0.19827 | 61.4867 | -0.042259 | 0.020767 | 61.525 | -0.001436 | 61.3077 | 61.4759 | 61.3822 | 61.4153 | 61.4252 | 61.4636 | 61.4351 | 61.4699 | 123.0239 | 61.6668 | 122.9552 | 61.4262 | 61.4893 | 122.9935 | 61.4671 | 122.7762 | 61.5346 | 61.5568 | 61.4659 | 61.4881
1172.8906 | 123.2117 | -61.4319 | 61.6013 | 0.021127 | -0.090888 | -0.062364 | -0.038752 | -0.014093 | -0.033455 | -0.007779 | 61.56 | 0.19827 | 61.4821 | -0.042259 | 0.029923 | 61.5295 | -0.001436 | 61.3169 | 61.453 | 61.341 | 61.3695 | 61.3931 | 61.4178 | 61.3984 | 61.4241 | 122.9919 | 61.6302 | 122.914 | 61.3896 | 61.4618 | 122.9614 | 61.4304 | 122.7488 | 61.5301 | 61.5614 | 61.4522 | 61.4835
1173.8906 | 123.2803 | -61.4319 | 61.5692 | 0.016548 | -0.086309 | -0.062364 | -0.043331 | -0.023249 | -0.038034 | -0.012357 | 61.56 | 0.20284 | 61.4867 | -0.046838 | 0.016188 | 61.5204 | -0.006014 | 61.2986 | 61.4484 | 61.3456 | 61.3695 | 61.3886 | 61.4086 | 61.3939 | 61.4195 | 122.9919 | 61.6347 | 122.9186 | 61.385 | 61.4481 | 122.9523 | 61.4259 | 122.7305 | 61.5438 | 61.566 | 61.4705 | 61.4927
1174.8906 | 123.1567 | -61.4548 | 61.5875 | 0.007391 | -0.095467 | -0.066943 | -0.047909 | -0.018671 | -0.038034 | -0.021514 | 61.5554 | 0.20742 | 61.4821 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3031 | 61.4622 | 61.3593 | 61.3878 | 61.4069 | 61.4361 | 61.4167 | 61.4333 | 123.0102 | 61.6622 | 122.9369 | 61.4079 | 61.4755 | 122.9843 | 61.4533 | 122.7579 | 61.5346 | 61.5568 | 61.4613 | 61.4835
1175.8906 | 123.2712 | -61.4365 | 61.5372 | 0.01197 | -0.10462 | -0.0761 | -0.052488 | -0.032405 | -0.051769 | -0.021514 | 61.5463 | 0.212 | 61.4867 | -0.042259 | 0.020767 | 61.5204 | -0.006014 | 61.3169 | 61.4484 | 61.3318 | 61.3604 | 61.384 | 61.4041 | 61.3847 | 61.4149 | 122.9827 | 61.6485 | 122.9231 | 61.3942 | 61.4572 | 122.9568 | 61.4304 | 122.7533 | 61.5255 | 61.5523 | 61.4659 | 61.4927
1176.8906 | 123.2208 | -61.4502 | 61.5738 | 0.007391 | -0.10462 | -0.0761 | -0.061645 | -0.041561 | -0.060926 | -0.03067 | 61.5508 | 0.20742 | 61.4912 | -0.051417 | 0.025345 | 61.5341 | -0.006014 | 61.2986 | 61.4576 | 61.3456 | 61.3741 | 61.3886 | 61.4086 | 61.3893 | 61.4195 | 123.001 | 61.6576 | 122.9414 | 61.3988 | 61.4755 | 122.9843 | 61.4442 | 122.7488 | 61.5255 | 61.5568 | 61.4659 | 61.4973
1177.8906 | 123.2437 | -61.4182 | 61.528 | 0.01197 | -0.10004 | -0.085257 | -0.066223 | -0.032405 | -0.056347 | -0.03067 | 61.5508 | 0.20742 | 61.4775 | -0.051417 | 0.029923 | 61.5204 | 0.007721 | 61.3031 | 61.4301 | 61.3181 | 61.3329 | 61.3519 | 61.3857 | 61.3618 | 61.3875 | 122.969 | 61.6256 | 122.8957 | 61.3667 | 61.4481 | 122.9385 | 61.4259 | 122.7213 | 61.5209 | 61.5431 | 61.4476 | 61.4698
1178.8906 | 123.1522 | -61.4365 | 61.6241 | 0.007391 | -0.10462 | -0.089836 | -0.066223 | -0.036983 | -0.056347 | -0.026092 | 61.5463 | 0.20284 | 61.4912 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.4439 | 61.3318 | 61.3466 | 61.3702 | 61.3995 | 61.3801 | 61.4104 | 122.9827 | 61.6393 | 122.9277 | 61.3896 | 61.4618 | 122.966 | 61.435 | 122.7442 | 61.5209 | 61.5477 | 61.4659 | 61.4927
1179.8906 | 123.3078 | -61.4182 | 61.5738 | 0.002813 | -0.1092 | -0.089836 | -0.070802 | -0.036983 | -0.056347 | -0.039826 | 61.5554 | 0.20284 | 61.4821 | -0.046838 | 0.016188 | 61.5341 | -0.006014 | 61.2986 | 61.421 | 61.3089 | 61.3283 | 61.3473 | 61.3812 | 61.3618 | 61.3783 | 122.9736 | 61.621 | 122.9002 | 61.3713 | 61.4343 | 122.9523 | 61.4121 | 122.7167 | 61.5392 | 61.5614 | 61.4659 | 61.4881
1180.8906 | 123.262 | -61.3998 | 61.5646 | 0.007391 | -0.1092 | -0.080679 | -0.079959 | -0.046138 | -0.056347 | -0.039826 | 61.5463 | 0.19827 | 61.4821 | -0.042259 | 0.025345 | 61.5204 | 0.012299 | 61.3077 | 61.4072 | 61.2906 | 61.3192 | 61.3199 | 61.3537 | 61.3435 | 61.36 | 122.9461 | 61.5981 | 122.8819 | 61.3576 | 61.4252 | 122.9202 | 61.4121 | 122.7076 | 61.5209 | 61.534 | 61.4567 | 61.4698
1181.8906 | 123.2895 | -61.4319 | 61.5601 | 0.007391 | -0.12294 | -0.089836 | -0.07538 | -0.041561 | -0.065504 | -0.039826 | 61.5554 | 0.20742 | 61.4867 | -0.051417 | 0.020767 | 61.525 | 0.003143 | 61.3077 | 61.4393 | 61.3089 | 61.342 | 61.3565 | 61.3903 | 61.3664 | 61.3921 | 122.9873 | 61.6393 | 122.9186 | 61.3805 | 61.4527 | 122.9568 | 61.435 | 122.7396 | 61.5346 | 61.5523 | 61.4659 | 61.4835
1182.8906 | 123.2437 | -61.4182 | 61.5692 | 0.016548 | -0.1092 | -0.085257 | -0.066223 | -0.032405 | -0.060926 | -0.035248 | 61.5554 | 0.19827 | 61.4912 | -0.046838 | 0.025345 | 61.5341 | 0.003143 | 61.3077 | 61.4347 | 61.3089 | 61.3329 | 61.3519 | 61.3857 | 61.3572 | 61.3829 | 122.9736 | 61.6164 | 122.9094 | 61.3713 | 61.4435 | 122.9523 | 61.4213 | 122.7259 | 61.5301 | 61.5523 | 61.4659 | 61.4881
1183.8906 | 123.3078 | -61.4227 | 61.5509 | 0.007391 | -0.1092 | -0.080679 | -0.066223 | -0.041561 | -0.060926 | -0.035248 | 61.56 | 0.20742 | 61.4867 | -0.042259 | 0.020767 | 61.5204 | -0.006014 | 61.3031 | 61.4301 | 61.3135 | 61.342 | 61.3565 | 61.3812 | 61.3618 | 61.3875 | 122.9827 | 61.6302 | 122.9094 | 61.3805 | 61.4435 | 122.9431 | 61.4167 | 122.7259 | 61.5392 | 61.566 | 61.4659 | 61.4927
1184.8906 | 123.2895 | -61.409 | 61.5463 | 0.01197 | -0.11378 | -0.094414 | -0.070802 | -0.046138 | -0.065504 | -0.039826 | 61.5508 | 0.19827 | 61.4821 | -0.046838 | 0.020767 | 61.525 | -0.001436 | 61.3031 | 61.421 | 61.2952 | 61.3146 | 61.3382 | 61.3629 | 61.3435 | 61.3692 | 122.9598 | 61.6073 | 122.8911 | 61.3622 | 61.4298 | 122.934 | 61.4076 | 122.7121 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1185.8906 | 123.2254 | -61.4273 | 61.6058 | 0.01197 | -0.11378 | -0.085257 | -0.07538 | -0.046138 | -0.070082 | -0.035248 | 61.5554 | 0.20284 | 61.4958 | -0.055996 | 0.029923 | 61.5204 | -0.001436 | 61.3123 | 61.4393 | 61.3135 | 61.3421 | 61.3519 | 61.3812 | 61.3572 | 61.3921 | 122.9827 | 61.6302 | 122.9231 | 61.3713 | 61.4572 | 122.9477 | 61.4259 | 122.7396 | 61.5255 | 61.5568 | 61.4659 | 61.4973
1186.8906 | 123.2758 | -61.441 | 61.5417 | 0.01197 | -0.1092 | -0.085257 | -0.07538 | -0.050716 | -0.065504 | -0.035248 | 61.5508 | 0.20742 | 61.4775 | -0.046838 | 0.020767 | 61.5204 | -0.001436 | 61.294 | 61.453 | 61.3318 | 61.3558 | 61.3657 | 61.3903 | 61.3755 | 61.4058 | 122.9919 | 61.6485 | 122.9186 | 61.3942 | 61.4618 | 122.9614 | 61.4396 | 122.735 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1187.8906 | 123.2712 | -61.4044 | 61.5463 | 0.007391 | -0.1092 | -0.089836 | -0.066223 | -0.041561 | -0.060926 | -0.035248 | 61.5646 | 0.212 | 61.4867 | -0.051417 | 0.020767 | 61.5158 | -0.006014 | 61.3077 | 61.4118 | 61.2952 | 61.3146 | 61.3382 | 61.3629 | 61.3435 | 61.3692 | 122.969 | 61.6164 | 122.8911 | 61.353 | 61.4252 | 122.9202 | 61.3984 | 122.7121 | 61.5438 | 61.5706 | 61.4659 | 61.4927
1188.8906 | 123.2391 | -61.4365 | 61.5738 | 0.01197 | -0.10004 | -0.0761 | -0.066223 | -0.036983 | -0.051769 | -0.026092 | 61.5508 | 0.212 | 61.4821 | -0.051417 | 0.029923 | 61.5295 | 0.003143 | 61.2986 | 61.4484 | 61.3364 | 61.3604 | 61.3702 | 61.3995 | 61.3847 | 61.4104 | 122.9873 | 61.6485 | 122.9185 | 61.385 | 61.4664 | 122.966 | 61.4396 | 122.735 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1189.8906 | 123.2849 | -61.4273 | 61.5646 | 0.007391 | -0.1092 | -0.080679 | -0.066223 | -0.036983 | -0.065504 | -0.039826 | 61.5463 | 0.212 | 61.4821 | -0.051417 | 0.020767 | 61.5341 | -0.001436 | 61.3077 | 61.4347 | 61.3181 | 61.3466 | 61.3611 | 61.3903 | 61.3618 | 61.3875 | 122.9736 | 61.6393 | 122.9094 | 61.3759 | 61.4481 | 122.9614 | 61.4259 | 122.735 | 61.5255 | 61.5477 | 61.4613 | 61.4835
1190.8906 | 123.3032 | -61.4502 | 61.5646 | 0.002813 | -0.11378 | -0.089836 | -0.070802 | -0.041561 | -0.060926 | -0.035248 | 61.5554 | 0.20742 | 61.4821 | -0.046838 | 0.025345 | 61.525 | -0.006014 | 61.3077 | 61.453 | 61.3364 | 61.3604 | 61.3794 | 61.4086 | 61.3893 | 61.4149 | 123.0056 | 61.6576 | 122.9323 | 61.4034 | 61.4755 | 122.9752 | 61.4442 | 122.7579 | 61.5301 | 61.5614 | 61.4567 | 61.4881
1191.8906 | 123.2803 | -61.4136 | 61.5738 | 0.016548 | -0.1092 | -0.094414 | -0.070802 | -0.050716 | -0.065504 | -0.035248 | 61.5508 | 0.20284 | 61.4821 | -0.051417 | 0.016188 | 61.5204 | -0.001436 | 61.2986 | 61.4301 | 61.3044 | 61.3192 | 61.3428 | 61.3629 | 61.3481 | 61.3783 | 122.9644 | 61.6164 | 122.8957 | 61.3622 | 61.4298 | 122.934 | 61.4121 | 122.7121 | 61.5346 | 61.5523 | 61.4659 | 61.4835
1192.8906 | 123.262 | -61.4136 | 61.5326 | 0.01197 | -0.11378 | -0.080679 | -0.070802 | -0.046138 | -0.065504 | -0.035248 | 61.5554 | 0.212 | 61.4729 | -0.03768 | 0.020767 | 61.525 | 0.003143 | 61.3077 | 61.4255 | 61.2998 | 61.3329 | 61.3428 | 61.3674 | 61.3481 | 61.3783 | 122.969 | 61.6256 | 122.8865 | 61.3759 | 61.4343 | 122.9385 | 61.4167 | 122.7213 | 61.5346 | 61.5523 | 61.4522 | 61.4698
1193.8906 | 123.2758 | -61.4273 | 61.5601 | 0.002813 | -0.1092 | -0.085257 | -0.070802 | -0.046138 | -0.065504 | -0.035248 | 61.56 | 0.212 | 61.4821 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.4301 | 61.3181 | 61.3421 | 61.3565 | 61.3812 | 61.3618 | 61.3921 | 122.9873 | 61.6393 | 122.9094 | 61.3805 | 61.4481 | 122.9568 | 61.4259 | 122.735 | 61.5392 | 61.5614 | 61.4613 | 61.4835
1194.8906 | 123.2574 | -61.4227 | 61.5738 | 0.01197 | -0.10462 | -0.0761 | -0.066223 | -0.036983 | -0.056347 | -0.03067 | 61.56 | 0.19827 | 61.4775 | -0.051417 | 0.025345 | 61.525 | -0.001436 | 61.3123 | 61.4347 | 61.3181 | 61.3466 | 61.3565 | 61.3857 | 61.3664 | 61.3921 | 122.9827 | 61.621 | 122.9002 | 61.3713 | 61.4481 | 122.9477 | 61.4213 | 122.735 | 61.5346 | 61.5614 | 61.4522 | 61.4789
1195.8906 | 123.1659 | -61.4502 | 61.6196 | 0.007391 | -0.090888 | -0.066943 | -0.061645 | -0.023249 | -0.051769 | -0.026092 | 61.5463 | 0.20284 | 61.4867 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.4576 | 61.3593 | 61.3833 | 61.3886 | 61.4269 | 61.3984 | 61.4241 | 122.9965 | 61.653 | 122.9369 | 61.3988 | 61.4755 | 122.9797 | 61.4488 | 122.7579 | 61.5209 | 61.5477 | 61.4613 | 61.4881
1196.8906 | 123.3124 | -61.4365 | 61.5738 | 0.007391 | -0.086309 | -0.0761 | -0.047909 | -0.014093 | -0.033455 | -0.012357 | 61.56 | 0.20742 | 61.4912 | -0.03768 | 0.020767 | 61.5295 | -0.006014 | 61.3169 | 61.4439 | 61.3502 | 61.3604 | 61.3886 | 61.4224 | 61.403 | 61.4241 | 122.9965 | 61.6439 | 122.9277 | 61.3988 | 61.4572 | 122.966 | 61.4304 | 122.7533 | 61.5392 | 61.566 | 61.4705 | 61.4973
1197.8906 | 123.2666 | -61.4273 | 61.5829 | 0.007391 | -0.086309 | -0.066943 | -0.052488 | -0.018671 | -0.038034 | -0.016936 | 61.5554 | 0.20284 | 61.4821 | -0.046838 | 0.025345 | 61.5295 | 0.003143 | 61.3077 | 61.4347 | 61.341 | 61.3604 | 61.3748 | 61.4086 | 61.3893 | 61.4104 | 122.9827 | 61.6302 | 122.9094 | 61.3805 | 61.4527 | 122.9568 | 61.4305 | 122.735 | 61.5301 | 61.5523 | 61.4567 | 61.4789
1198.8906 | 123.1796 | -61.4365 | 61.6196 | 0.007391 | -0.086309 | -0.062364 | -0.047909 | -0.014093 | -0.038034 | -0.012357 | 61.5508 | 0.19369 | 61.4867 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.4439 | 61.3502 | 61.3741 | 61.3886 | 61.4224 | 61.3984 | 61.4241 | 122.9873 | 61.6302 | 122.9231 | 61.3896 | 61.4572 | 122.966 | 61.4396 | 122.7488 | 61.5301 | 61.5477 | 61.4659 | 61.4835
1199.8906 | 123.2941 | -61.4136 | 61.5875 | -0.001765 | -0.08173 | -0.057786 | -0.043331 | -0.014093 | -0.038034 | -0.012357 | 61.5554 | 0.20742 | 61.4867 | -0.042259 | 0.025345 | 61.5295 | 0.003143 | 61.3123 | 61.4118 | 61.3318 | 61.3558 | 61.3702 | 61.3995 | 61.3755 | 61.4012 | 122.969 | 61.621 | 122.9002 | 61.3713 | 61.4389 | 122.9431 | 61.4167 | 122.7259 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1200.8906 | 123.1934 | -61.441 | 61.6287 | 0.007391 | -0.072572 | -0.062364 | -0.038752 | -0.009515 | -0.028877 | 0.001377 | 61.5554 | 0.212 | 61.4867 | -0.046838 | 0.025345 | 61.525 | 0.003143 | 61.3077 | 61.4484 | 61.3685 | 61.3787 | 61.4023 | 61.4315 | 61.4122 | 61.4424 | 122.9965 | 61.653 | 122.9277 | 61.3942 | 61.4664 | 122.966 | 61.4442 | 122.7488 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1201.8906 | 123.3032 | -61.4044 | 61.5601 | 0.01197 | -0.08173 | -0.053207 | -0.038752 | -0.014093 | -0.038034 | -0.007779 | 61.5554 | 0.20284 | 61.4821 | -0.051417 | 0.01161 | 61.525 | -0.001436 | 61.2986 | 61.4164 | 61.3227 | 61.3512 | 61.3657 | 61.3903 | 61.3664 | 61.3966 | 122.9598 | 61.6073 | 122.8865 | 61.353 | 61.416 | 122.9294 | 61.403 | 122.703 | 61.5438 | 61.5568 | 61.4705 | 61.4835
1202.8906 | 123.1247 | -61.4456 | 61.6196 | 0.002813 | -0.067994 | -0.04405 | -0.034174 | -0.004937 | -0.028877 | -0.003201 | 61.5554 | 0.20742 | 61.4867 | -0.042259 | 0.029923 | 61.5295 | 0.003143 | 61.3123 | 61.4484 | 61.3776 | 61.4016 | 61.4114 | 61.4407 | 61.4167 | 61.4424 | 123.001 | 61.653 | 122.9323 | 61.4034 | 61.4755 | 122.9752 | 61.4488 | 122.7579 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1203.8906 | 123.2346 | -61.4227 | 61.5784 | 0.002813 | -0.058836 | -0.039471 | -0.020438 | -0.000359 | -0.01972 | 0.005955 | 61.5508 | 0.19827 | 61.4867 | -0.051417 | 0.029923 | 61.5295 | -0.001436 | 61.3077 | 61.4255 | 61.3639 | 61.3833 | 61.4023 | 61.4224 | 61.403 | 61.4287 | 122.9736 | 61.621 | 122.9094 | 61.3713 | 61.4527 | 122.9523 | 61.4213 | 122.7305 | 61.5209 | 61.5523 | 61.4567 | 61.4881
1204.8906 | 123.1934 | -61.4456 | 61.6241 | 0.002813 | -0.067994 | -0.04405 | -0.025017 | -0.000359 | -0.028877 | 0.015112 | 61.5554 | 0.20742 | 61.4821 | -0.046838 | 0.029923 | 61.5295 | 0.003143 | 61.3031 | 61.4484 | 61.3776 | 61.4016 | 61.4206 | 61.4453 | 61.4167 | 61.4607 | 123.001 | 61.653 | 122.9277 | 61.3988 | 61.4755 | 122.9752 | 61.4488 | 122.7488 | 61.5255 | 61.5523 | 61.4522 | 61.4789
1205.8906 | 123.1567 | -61.4456 | 61.6013 | 0.01197 | -0.063415 | -0.04405 | -0.025017 | -0.000359 | -0.01972 | 0.005955 | 61.56 | 0.212 | 61.4867 | -0.042259 | 0.025345 | 61.525 | -0.001436 | 61.3077 | 61.4576 | 61.3822 | 61.4016 | 61.4206 | 61.4453 | 61.4259 | 61.4516 | 123.0056 | 61.6576 | 122.9323 | 61.4034 | 61.471 | 122.9706 | 61.4442 | 122.7533 | 61.5346 | 61.5614 | 61.4613 | 61.4881
1206.9062 | 123.2666 | -61.3998 | 61.5921 | 0.01197 | -0.067994 | -0.04405 | -0.020438 | -0.004937 | -0.024298 | 0.005955 | 61.5554 | 0.20284 | 61.4821 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4118 | 61.3318 | 61.3558 | 61.3794 | 61.3949 | 61.3755 | 61.4058 | 122.9553 | 61.6027 | 122.8819 | 61.353 | 61.4252 | 122.934 | 61.3984 | 122.7167 | 61.5301 | 61.5568 | 61.4567 | 61.4835
1207.8906 | 123.1476 | -61.4044 | 61.6333 | 0.01197 | -0.08173 | -0.053207 | -0.029595 | -0.004937 | -0.028877 | -0.007779 | 61.5508 | 0.20742 | 61.4867 | -0.051417 | 0.025345 | 61.5341 | -0.001436 | 61.3077 | 61.4164 | 61.3227 | 61.3512 | 61.3748 | 61.3995 | 61.3755 | 61.3966 | 122.9553 | 61.6118 | 122.8911 | 61.353 | 61.4298 | 122.9385 | 61.403 | 122.7121 | 61.5255 | 61.5523 | 61.4613 | 61.4881
1208.8906 | 123.1705 | -61.4502 | 61.6333 | 0.007391 | -0.086309 | -0.057786 | -0.038752 | -0.018671 | -0.038034 | -0.007779 | 61.5646 | 0.20284 | 61.4821 | -0.051417 | 0.034501 | 61.525 | -0.006014 | 61.3123 | 61.4576 | 61.3639 | 61.3924 | 61.4114 | 61.4315 | 61.4122 | 61.4424 | 123.0148 | 61.653 | 122.9323 | 61.3988 | 61.4847 | 122.9752 | 61.4442 | 122.7625 | 61.5301 | 61.5706 | 61.4476 | 61.4881
1209.8906 | 123.23 | -61.4456 | 61.6241 | 0.016548 | -0.072572 | -0.053207 | -0.034174 | -0.014093 | -0.028877 | 0.001377 | 61.5554 | 0.20284 | 61.4775 | -0.046838 | 0.029923 | 61.5204 | -0.001436 | 61.3169 | 61.4622 | 61.373 | 61.3924 | 61.4114 | 61.4315 | 61.4167 | 61.447 | 123.001 | 61.6485 | 122.9231 | 61.3988 | 61.4755 | 122.966 | 61.4442 | 122.7625 | 61.5255 | 61.5568 | 61.4476 | 61.4789
1210.8906 | 123.1888 | -61.441 | 61.6058 | 0.007391 | -0.077151 | -0.057786 | -0.034174 | -0.014093 | -0.024298 | 0.001377 | 61.5554 | 0.20284 | 61.4821 | -0.046838 | 0.025345 | 61.525 | -0.001436 | 61.3123 | 61.4484 | 61.3639 | 61.3833 | 61.4069 | 61.4269 | 61.4167 | 61.4424 | 122.9965 | 61.6439 | 122.9231 | 61.3942 | 61.4664 | 122.966 | 61.4396 | 122.7533 | 61.5301 | 61.5568 | 61.4567 | 61.4835
1211.8906 | 123.2941 | -61.4456 | 61.5189 | 0.007391 | -0.077151 | -0.053207 | -0.043331 | -0.009515 | -0.028877 | -0.003201 | 61.5508 | 0.19827 | 61.4912 | -0.055996 | 0.016188 | 61.5341 | -0.006014 | 61.3077 | 61.453 | 61.3685 | 61.3924 | 61.4023 | 61.4361 | 61.4167 | 61.4424 | 122.9965 | 61.6439 | 122.9369 | 61.3896 | 61.4618 | 122.9797 | 61.4396 | 122.7533 | 61.5346 | 61.5568 | 61.4751 | 61.4973
1212.8906 | 123.23 | -61.4182 | 61.5967 | 0.01197 | -0.077151 | -0.053207 | -0.029595 | -0.004937 | -0.028877 | -0.003201 | 61.5554 | 0.20742 | 61.4867 | -0.046838 | 0.025345 | 61.5204 | 0.003143 | 61.3031 | 61.4301 | 61.341 | 61.3649 | 61.3886 | 61.4132 | 61.3893 | 61.415 | 122.9736 | 61.6256 | 122.9048 | 61.3713 | 61.4435 | 122.9385 | 61.4213 | 122.7213 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1213.8906 | 123.2254 | -61.4502 | 61.6287 | 0.01197 | -0.077151 | -0.062364 | -0.038752 | -0.009515 | -0.038034 | -0.007779 | 61.56 | 0.20284 | 61.4821 | -0.046838 | 0.029923 | 61.5295 | 0.007721 | 61.2986 | 61.4622 | 61.373 | 61.3878 | 61.4114 | 61.4407 | 61.4122 | 61.4424 | 123.0102 | 61.653 | 122.9323 | 61.4034 | 61.4801 | 122.9797 | 61.4579 | 122.7488 | 61.5301 | 61.5523 | 61.4522 | 61.4744
1214.8906 | 123.2162 | -61.4319 | 61.6196 | 0.007391 | -0.08173 | -0.066943 | -0.047909 | -0.014093 | -0.038034 | -0.007779 | 61.5554 | 0.20742 | 61.4958 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.4393 | 61.3502 | 61.3649 | 61.384 | 61.4178 | 61.3939 | 61.4241 | 122.9873 | 61.6393 | 122.9277 | 61.385 | 61.4527 | 122.9614 | 61.4304 | 122.7396 | 61.5346 | 61.5568 | 61.4751 | 61.4973
1215.8906 | 123.2712 | -61.4136 | 61.5738 | 0.007391 | -0.08173 | -0.062364 | -0.047909 | -0.018671 | -0.042612 | -0.007779 | 61.5508 | 0.212 | 61.4912 | -0.046838 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.421 | 61.3318 | 61.3512 | 61.3657 | 61.3949 | 61.371 | 61.4058 | 122.9644 | 61.6256 | 122.9048 | 61.3667 | 61.4389 | 122.9431 | 61.4121 | 122.7213 | 61.5255 | 61.5523 | 61.4659 | 61.4927
1216.8906 | 123.2758 | -61.441 | 61.5738 | 0.01197 | -0.08173 | -0.057786 | -0.043331 | -0.014093 | -0.038034 | -0.007779 | 61.56 | 0.212 | 61.4775 | -0.055996 | 0.025345 | 61.5158 | 0.007721 | 61.3077 | 61.453 | 61.3593 | 61.3833 | 61.3977 | 61.4269 | 61.403 | 61.4333 | 123.001 | 61.653 | 122.9186 | 61.385 | 61.4664 | 122.9568 | 61.4488 | 122.7488 | 61.5346 | 61.5523 | 61.4522 | 61.4698
1217.8906 | 123.2254 | -61.4273 | 61.5921 | 0.016548 | -0.08173 | -0.048628 | -0.038752 | -0.000359 | -0.038034 | 0.001377 | 61.5646 | 0.20284 | 61.4912 | -0.051417 | 0.029923 | 61.5341 | -0.006014 | 61.3123 | 61.4439 | 61.3456 | 61.3787 | 61.3886 | 61.4269 | 61.3893 | 61.4287 | 122.9919 | 61.6302 | 122.9186 | 61.3759 | 61.4572 | 122.9614 | 61.4213 | 122.7396 | 61.5346 | 61.5706 | 61.4613 | 61.4973
1218.8906 | 123.1934 | -61.4273 | 61.5967 | 0.007391 | -0.086309 | -0.053207 | -0.043331 | -0.014093 | -0.038034 | 0.005955 | 61.5554 | 0.19827 | 61.4912 | -0.042259 | 0.025345 | 61.5295 | -0.006014 | 61.3123 | 61.4347 | 61.341 | 61.3741 | 61.384 | 61.4132 | 61.3893 | 61.4333 | 122.9827 | 61.6256 | 122.9186 | 61.385 | 61.4527 | 122.9568 | 61.4213 | 122.7396 | 61.5301 | 61.5614 | 61.4659 | 61.4973
1219.8906 | 123.2071 | -61.4227 | 61.6058 | 0.007391 | -0.090888 | -0.066943 | -0.043331 | -0.023249 | -0.038034 | -0.007779 | 61.5554 | 0.20284 | 61.4912 | -0.046838 | 0.025345 | 61.525 | 0.003143 | 61.3031 | 61.4301 | 61.3318 | 61.3558 | 61.3794 | 61.3995 | 61.3847 | 61.4149 | 122.9781 | 61.6256 | 122.914 | 61.3759 | 61.4481 | 122.9477 | 61.4259 | 122.7259 | 61.5301 | 61.5523 | 61.4659 | 61.4881
1220.8906 | 123.1155 | -61.4594 | 61.6241 | 0.01197 | -0.086309 | -0.062364 | -0.043331 | -0.014093 | -0.033455 | -0.007779 | 61.5554 | 0.212 | 61.4958 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.4713 | 61.373 | 61.397 | 61.416 | 61.4453 | 61.4259 | 61.4516 | 123.0148 | 61.6714 | 122.9552 | 61.4125 | 61.4801 | 122.9889 | 61.4579 | 122.7671 | 61.5346 | 61.5568 | 61.4751 | 61.4973
1221.8906 | 123.1979 | -61.4502 | 61.6104 | 0.01197 | -0.08173 | -0.062364 | -0.034174 | -0.014093 | -0.033455 | -0.007779 | 61.56 | 0.20742 | 61.4867 | -0.03768 | 0.016188 | 61.5295 | -0.001436 | 61.3077 | 61.4622 | 61.3685 | 61.3878 | 61.416 | 61.4361 | 61.4167 | 61.4424 | 123.0102 | 61.6576 | 122.9369 | 61.4125 | 61.4664 | 122.9797 | 61.4488 | 122.7579 | 61.5438 | 61.5614 | 61.4705 | 61.4881
1222.8906 | 123.1338 | -61.4502 | 61.5738 | 0.007391 | -0.077151 | -0.048628 | -0.038752 | -0.000359 | -0.024298 | 0.001377 | 61.5554 | 0.20742 | 61.4912 | -0.046838 | 0.029923 | 61.5295 | -0.001436 | 61.3077 | 61.4576 | 61.373 | 61.4016 | 61.4114 | 61.4498 | 61.4259 | 61.4516 | 123.0056 | 61.6576 | 122.9414 | 61.4034 | 61.4801 | 122.9797 | 61.4488 | 122.7579 | 61.5255 | 61.5568 | 61.4613 | 61.4927
1223.8906 | 123.2208 | -61.4273 | 61.5921 | 0.01197 | -0.067994 | -0.04405 | -0.020438 | -0.000359 | -0.015142 | 0.010533 | 61.5554 | 0.19369 | 61.4867 | -0.046838 | 0.020767 | 61.5341 | -0.006014 | 61.3031 | 61.4393 | 61.3593 | 61.3833 | 61.4069 | 61.4269 | 61.4122 | 61.4378 | 122.9827 | 61.621 | 122.914 | 61.3805 | 61.4481 | 122.9614 | 61.4213 | 122.7305 | 61.5346 | 61.5614 | 61.4659 | 61.4927
1224.8906 | 123.1796 | -61.4548 | 61.5921 | 0.016548 | -0.072572 | -0.039471 | -0.020438 | 0.004219 | -0.01972 | 0.005955 | 61.5554 | 0.20742 | 61.4821 | -0.046838 | 0.029923 | 61.5204 | 0.003143 | 61.3031 | 61.4713 | 61.3822 | 61.4153 | 61.4343 | 61.459 | 61.4351 | 61.4607 | 123.0102 | 61.6622 | 122.9369 | 61.4079 | 61.4847 | 122.9752 | 61.4579 | 122.7579 | 61.5255 | 61.5523 | 61.4522 | 61.4789
1225.8906 | 123.2941 | -61.3861 | 61.5509 | 0.01197 | -0.063415 | -0.030314 | -0.020438 | 0.013375 | -0.015142 | 0.015112 | 61.5554 | 0.20284 | 61.4821 | -0.046838 | 0.025345 | 61.5341 | -0.006014 | 61.3031 | 61.3981 | 61.3227 | 61.3558 | 61.3657 | 61.3995 | 61.371 | 61.4012 | 122.9415 | 61.589 | 122.8682 | 61.3393 | 61.4115 | 122.9202 | 61.3801 | 122.6893 | 61.5301 | 61.5614 | 61.4567 | 61.4881
1226.8906 | 123.1064 | -61.4868 | 61.6013 | 0.021127 | -0.054257 | -0.034893 | -0.006703 | 0.004219 | -0.005985 | 0.010533 | 61.5508 | 0.20742 | 61.4775 | -0.051417 | 0.025345 | 61.5341 | -0.001436 | 61.3077 | 61.5079 | 61.4326 | 61.4519 | 61.4801 | 61.491 | 61.4808 | 61.4973 | 123.0377 | 61.6942 | 122.9643 | 61.4354 | 61.5122 | 123.0209 | 61.4854 | 122.7945 | 61.5255 | 61.5523 | 61.4522 | 61.4789
1227.8906 | 123.1659 | -61.4731 | 61.5692 | 0.021127 | -0.058836 | -0.025735 | -0.006703 | 0.022531 | -0.005985 | 0.024268 | 61.5508 | 0.212 | 61.4821 | -0.051417 | 0.020767 | 61.525 | 0.003143 | 61.3031 | 61.4942 | 61.4142 | 61.4473 | 61.4664 | 61.4956 | 61.4671 | 61.4974 | 123.0239 | 61.6851 | 122.9552 | 61.4217 | 61.4939 | 122.998 | 61.4762 | 122.7762 | 61.5301 | 61.5477 | 61.4613 | 61.4789
1228.8906 | 123.175 | -61.441 | 61.5829 | 0.021127 | -0.054257 | -0.030314 | -0.006703 | 0.022531 | -0.005985 | 0.01969 | 61.5508 | 0.212 | 61.4958 | -0.046838 | 0.016188 | 61.525 | -0.006014 | 61.3031 | 61.4622 | 61.3868 | 61.4107 | 61.4343 | 61.4636 | 61.4351 | 61.4607 | 122.9919 | 61.653 | 122.9369 | 61.3942 | 61.4572 | 122.966 | 61.435 | 122.7442 | 61.5346 | 61.5568 | 61.4796 | 61.5018
1229.8906 | 123.1522 | -61.4548 | 61.5967 | 0.007391 | -0.063415 | -0.034893 | -0.01586 | 0.008797 | -0.01972 | 0.015112 | 61.5554 | 0.212 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | -0.006014 | 61.3031 | 61.4622 | 61.3914 | 61.4199 | 61.4389 | 61.4636 | 61.4351 | 61.4699 | 123.0102 | 61.6668 | 122.9323 | 61.4079 | 61.4755 | 122.9843 | 61.4488 | 122.7579 | 61.5346 | 61.5614 | 61.4567 | 61.4835
1230.8906 | 123.2254 | -61.441 | 61.5509 | 0.007391 | -0.077151 | -0.053207 | -0.034174 | -0.004937 | -0.028877 | 0.005955 | 61.5508 | 0.20742 | 61.4821 | -0.051417 | 0.029923 | 61.5295 | 0.003143 | 61.2986 | 61.4484 | 61.3639 | 61.3878 | 61.4069 | 61.4361 | 61.4122 | 61.447 | 122.9919 | 61.6485 | 122.9231 | 61.3896 | 61.471 | 122.9706 | 61.4442 | 122.7396 | 61.5209 | 61.5477 | 61.4522 | 61.4789
1231.8906 | 123.1567 | -61.4273 | 61.6013 | 0.016548 | -0.063415 | -0.039471 | -0.020438 | -0.000359 | -0.024298 | 0.001377 | 61.5554 | 0.20284 | 61.4867 | -0.051417 | 0.025345 | 61.5295 | -0.010593 | 61.3077 | 61.4439 | 61.3639 | 61.3878 | 61.4069 | 61.4269 | 61.403 | 61.4287 | 122.9827 | 61.6302 | 122.914 | 61.3759 | 61.4527 | 122.9568 | 61.4167 | 122.735 | 61.5301 | 61.566 | 61.4613 | 61.4973
1232.8906 | 123.1842 | -61.4639 | 61.5967 | 0.007391 | -0.067994 | -0.039471 | -0.01586 | 0.004219 | -0.015142 | 0.010533 | 61.5554 | 0.20284 | 61.4821 | -0.046838 | 0.020767 | 61.5295 | -0.010593 | 61.3031 | 61.4713 | 61.3959 | 61.4245 | 61.4481 | 61.4681 | 61.4488 | 61.4745 | 123.0193 | 61.6668 | 122.946 | 61.4171 | 61.4847 | 122.9935 | 61.4533 | 122.7671 | 61.5346 | 61.566 | 61.4613 | 61.4927
1233.8906 | 123.2162 | -61.4456 | 61.5875 | 0.01197 | -0.077151 | -0.048628 | -0.029595 | 0.004219 | -0.028877 | 0.001377 | 61.5554 | 0.20742 | 61.4821 | -0.046838 | 0.025345 | 61.525 | -0.001436 | 61.3123 | 61.4576 | 61.3685 | 61.397 | 61.416 | 61.4498 | 61.4167 | 61.447 | 123.001 | 61.653 | 122.9277 | 61.3988 | 61.471 | 122.9706 | 61.4442 | 122.7579 | 61.5301 | 61.5568 | 61.4567 | 61.4835
1234.8906 | 123.2208 | -61.4731 | 61.5875 | 0.01197 | -0.077151 | -0.04405 | -0.025017 | -0.004937 | -0.01972 | 0.005955 | 61.5554 | 0.20742 | 61.4867 | -0.042259 | 0.016188 | 61.5295 | 0.003143 | 61.3077 | 61.4851 | 61.3959 | 61.429 | 61.4481 | 61.4681 | 61.4534 | 61.479 | 123.0285 | 61.6805 | 122.9597 | 61.4308 | 61.4893 | 123.0026 | 61.4762 | 122.7808 | 61.5392 | 61.5523 | 61.4705 | 61.4835
1235.8906 | 123.2574 | -61.409 | 61.5417 | 0.007391 | -0.072572 | -0.04405 | -0.029595 | -0.000359 | -0.024298 | 0.005955 | 61.5508 | 0.20742 | 61.4821 | -0.042259 | 0.025345 | 61.525 | -0.001436 | 61.3077 | 61.4164 | 61.3364 | 61.3649 | 61.3794 | 61.4086 | 61.3847 | 61.415 | 122.9598 | 61.6164 | 122.8911 | 61.3667 | 61.4343 | 122.934 | 61.4076 | 122.7167 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1236.8906 | 123.143 | -61.4685 | 61.5784 | 0.01197 | -0.077151 | -0.053207 | -0.034174 | -0.004937 | -0.028877 | 0.005955 | 61.56 | 0.20742 | 61.4912 | -0.046838 | 0.025345 | 61.525 | -0.001436 | 61.3031 | 61.4805 | 61.3914 | 61.4153 | 61.4343 | 61.4636 | 61.4396 | 61.4745 | 123.0285 | 61.6759 | 122.9598 | 61.4217 | 61.4939 | 122.9935 | 61.4671 | 122.7717 | 61.5346 | 61.5614 | 61.4659 | 61.4927
1237.8906 | 123.2025 | -61.4548 | 61.5738 | 0.007391 | -0.086309 | -0.062364 | -0.034174 | -0.014093 | -0.028877 | -0.003201 | 61.5554 | 0.20742 | 61.4912 | -0.046838 | 0.025345 | 61.525 | -0.006014 | 61.2986 | 61.4622 | 61.3685 | 61.3924 | 61.4206 | 61.4407 | 61.4259 | 61.4516 | 123.0102 | 61.6622 | 122.946 | 61.4079 | 61.4801 | 122.9797 | 61.4488 | 122.7533 | 61.5301 | 61.5614 | 61.4659 | 61.4973
1238.8906 | 123.262 | -61.4273 | 61.528 | 0.007391 | -0.08173 | -0.057786 | -0.038752 | -0.014093 | -0.024298 | -0.012357 | 61.5508 | 0.20742 | 61.4912 | -0.046838 | 0.025345 | 61.525 | -0.010593 | 61.3077 | 61.4347 | 61.3456 | 61.3695 | 61.3886 | 61.4132 | 61.403 | 61.4149 | 122.9781 | 61.6347 | 122.9186 | 61.3805 | 61.4527 | 122.9523 | 61.4167 | 122.735 | 61.5255 | 61.5614 | 61.4659 | 61.5018
1239.8906 | 123.317 | -61.3953 | 61.5463 | 0.007391 | -0.086309 | -0.057786 | -0.034174 | -0.014093 | -0.033455 | 0.001377 | 61.5463 | 0.20284 | 61.4867 | -0.046838 | 0.016188 | 61.525 | 0.003143 | 61.2986 | 61.4027 | 61.309 | 61.3375 | 61.3611 | 61.3812 | 61.3618 | 61.3966 | 122.9415 | 61.5981 | 122.8819 | 61.3484 | 61.4115 | 122.9202 | 61.3984 | 122.6938 | 61.5301 | 61.5431 | 61.4705 | 61.4835
1240.8906 | 123.2529 | -61.4182 | 61.5601 | 0.007391 | -0.08173 | -0.053207 | -0.038752 | -0.009515 | -0.033455 | -0.012357 | 61.5508 | 0.20284 | 61.4821 | -0.046838 | 0.020767 | 61.525 | -0.001436 | 61.3031 | 61.4255 | 61.3364 | 61.3649 | 61.3794 | 61.4086 | 61.3847 | 61.4058 | 122.969 | 61.621 | 122.9002 | 61.3713 | 61.4389 | 122.9431 | 61.4167 | 122.7213 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1241.8906 | 123.1796 | -61.4777 | 61.5829 | 0.016548 | -0.067994 | -0.030314 | -0.01586 | 0.013375 | -0.005985 | 0.01969 | 61.56 | 0.19827 | 61.4912 | -0.051417 | 0.020767 | 61.5204 | 0.003143 | 61.3077 | 61.4942 | 61.4097 | 61.4473 | 61.4618 | 61.491 | 61.4717 | 61.4974 | 123.0377 | 61.6759 | 122.9689 | 61.4262 | 61.4984 | 122.998 | 61.4808 | 122.7854 | 61.5392 | 61.5568 | 61.4705 | 61.4881
1242.8906 | 123.3124 | -61.441 | 61.5372 | 0.01197 | -0.0451 | -0.030314 | 0.002454 | 0.022531 | -0.001406 | 0.028846 | 61.5508 | 0.20742 | 61.4867 | -0.051417 | 0.01161 | 61.5295 | -0.001436 | 61.3123 | 61.453 | 61.3959 | 61.4107 | 61.4435 | 61.4636 | 61.4396 | 61.4699 | 122.9919 | 61.6485 | 122.9277 | 61.3896 | 61.4526 | 122.9706 | 61.4396 | 122.7533 | 61.5392 | 61.5523 | 61.4751 | 61.4881
1243.8906 | 123.2529 | -61.4502 | 61.5601 | 0.007391 | -0.058836 | -0.034893 | -0.011281 | 0.022531 | -0.005985 | 0.015112 | 61.5554 | 0.20284 | 61.4775 | -0.051417 | 0.020767 | 61.525 | -0.001436 | 61.3123 | 61.4576 | 61.3914 | 61.4153 | 61.4389 | 61.4727 | 61.4442 | 61.4653 | 123.0056 | 61.653 | 122.9277 | 61.3988 | 61.471 | 122.9752 | 61.4488 | 122.7625 | 61.5346 | 61.5568 | 61.4567 | 61.4789
1244.8906 | 123.2437 | -61.4319 | 61.5372 | 0.01197 | -0.058836 | -0.030314 | -0.006703 | 0.017953 | -0.001406 | 0.024268 | 61.5554 | 0.212 | 61.4912 | -0.046838 | 0.029923 | 61.5295 | -0.001436 | 61.3077 | 61.4439 | 61.373 | 61.4016 | 61.4252 | 61.4498 | 61.4305 | 61.4562 | 122.9873 | 61.6439 | 122.9231 | 61.385 | 61.4618 | 122.9614 | 61.4304 | 122.7396 | 61.5255 | 61.5568 | 61.4613 | 61.4927
1245.8906 | 123.2895 | -61.4136 | 61.5555 | 0.007391 | -0.08173 | -0.048628 | -0.025017 | -0.000359 | -0.01972 | 0.010533 | 61.5554 | 0.20742 | 61.4867 | -0.046838 | 0.020767 | 61.5204 | -0.001436 | 61.3077 | 61.421 | 61.3318 | 61.3649 | 61.3886 | 61.4132 | 61.3939 | 61.4241 | 122.969 | 61.621 | 122.9002 | 61.3667 | 61.4343 | 122.934 | 61.4121 | 122.7213 | 61.5346 | 61.5568 | 61.4659 | 61.4881
1246.8906 | 123.2574 | -61.4182 | 61.528 | 0.002813 | -0.067994 | -0.039471 | -0.020438 | 0.008797 | -0.01972 | 0.005955 | 61.5554 | 0.19827 | 61.4821 | -0.051417 | 0.020767 | 61.5295 | -0.006014 | 61.3123 | 61.421 | 61.3502 | 61.3787 | 61.3977 | 61.4269 | 61.3984 | 61.4241 | 122.9736 | 61.6164 | 122.9002 | 61.3667 | 61.4389 | 122.9477 | 61.4121 | 122.7305 | 61.5346 | 61.5614 | 61.4613 | 61.4881
1247.8906 | 123.2803 | -61.4319 | 61.5692 | 0.01197 | -0.072572 | -0.034893 | -0.020438 | -0.000359 | -0.028877 | 0.001377 | 61.56 | 0.20742 | 61.4775 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3123 | 61.4439 | 61.3593 | 61.397 | 61.4114 | 61.4315 | 61.403 | 61.4333 | 122.9919 | 61.6393 | 122.9094 | 61.385 | 61.4527 | 122.9614 | 61.435 | 122.7442 | 61.5392 | 61.5568 | 61.4567 | 61.4744
1248.8906 | 123.2895 | -61.4182 | 61.5189 | 0.01197 | -0.058836 | -0.034893 | -0.01586 | 0.004219 | -0.010563 | 0.010533 | 61.5508 | 0.20284 | 61.4867 | -0.042259 | 0.020767 | 61.5341 | -0.001436 | 61.2986 | 61.4301 | 61.3593 | 61.3833 | 61.4023 | 61.4224 | 61.4076 | 61.4287 | 122.969 | 61.621 | 122.9048 | 61.3759 | 61.4389 | 122.9523 | 61.4167 | 122.7167 | 61.5301 | 61.5523 | 61.4659 | 61.4881
1249.8906 | 123.2437 | -61.4273 | 61.5372 | 0.01197 | -0.067994 | -0.04405 | -0.025017 | -0.000359 | -0.01972 | 0.005955 | 61.5554 | 0.21658 | 61.4867 | -0.046838 | 0.016188 | 61.5295 | 0.003143 | 61.3031 | 61.4393 | 61.3593 | 61.3833 | 61.4023 | 61.4269 | 61.4076 | 61.4333 | 122.9827 | 61.6439 | 122.914 | 61.3805 | 61.4435 | 122.9568 | 61.4305 | 122.7305 | 61.5392 | 61.5523 | 61.4705 | 61.4835
1250.8906 | 123.1842 | -61.4182 | 61.5875 | 0.01197 | -0.077151 | -0.053207 | -0.025017 | -0.000359 | -0.01972 | 0.005955 | 61.5554 | 0.20742 | 61.4867 | -0.051417 | 0.029923 | 61.525 | 0.003143 | 61.3215 | 61.4301 | 61.341 | 61.3649 | 61.3931 | 61.4178 | 61.3984 | 61.4241 | 122.9736 | 61.6256 | 122.9048 | 61.3667 | 61.4481 | 122.9431 | 61.4213 | 122.7396 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1251.8906 | 123.2208 | -61.4227 | 61.5555 | 0.021127 | -0.08173 | -0.053207 | -0.025017 | -0.000359 | -0.024298 | 0.001377 | 61.5508 | 0.22116 | 61.4912 | -0.051417 | 0.020767 | 61.5295 | -0.006014 | 61.3031 | 61.4439 | 61.341 | 61.3695 | 61.3977 | 61.4224 | 61.3984 | 61.4241 | 122.9736 | 61.6439 | 122.914 | 61.3713 | 61.4435 | 122.9523 | 61.4167 | 122.7259 | 61.5301 | 61.5568 | 61.4705 | 61.4973
1252.8906 | 123.2666 | -61.4227 | 61.5646 | 0.007391 | -0.077151 | -0.048628 | -0.025017 | 0.004219 | -0.028877 | 0.005955 | 61.5508 | 0.20742 | 61.4821 | -0.055996 | 0.020767 | 61.5295 | -0.006014 | 61.3031 | 61.4301 | 61.3456 | 61.3741 | 61.3977 | 61.4269 | 61.3939 | 61.4287 | 122.9736 | 61.6302 | 122.9048 | 61.3667 | 61.4435 | 122.9523 | 61.4167 | 122.7259 | 61.5301 | 61.5568 | 61.4613 | 61.4881
1253.8906 | 123.23 | -61.4182 | 61.5784 | 0.007391 | -0.072572 | -0.048628 | -0.029595 | -0.000359 | -0.033455 | 0.001377 | 61.5508 | 0.212 | 61.4867 | -0.055996 | 0.025345 | 61.5204 | -0.001436 | 61.2986 | 61.4255 | 61.3456 | 61.3695 | 61.3886 | 61.4178 | 61.3847 | 61.4195 | 122.969 | 61.6302 | 122.9048 | 61.3622 | 61.4435 | 122.9385 | 61.4167 | 122.7167 | 61.5255 | 61.5523 | 61.4613 | 61.4881
1254.8906 | 123.2437 | -61.4594 | 61.5646 | 0.007391 | -0.090888 | -0.057786 | -0.034174 | -0.009515 | -0.033455 | -0.007779 | 61.5508 | 0.20742 | 61.4821 | -0.046838 | 0.025345 | 61.5341 | 0.003143 | 61.3077 | 61.4667 | 61.3685 | 61.4016 | 61.4252 | 61.4498 | 61.4259 | 61.4516 | 123.0102 | 61.6668 | 122.9414 | 61.4125 | 61.4847 | 122.9935 | 61.4625 | 122.7671 | 61.5255 | 61.5477 | 61.4567 | 61.4789
1255.8906 | 123.2941 | -61.3953 | 61.5829 | 0.002813 | -0.090888 | -0.057786 | -0.038752 | -0.014093 | -0.038034 | -0.003201 | 61.5554 | 0.212 | 61.4912 | -0.051417 | 0.020767 | 61.525 | -0.010593 | 61.3077 | 61.3981 | 61.3044 | 61.3375 | 61.3565 | 61.3812 | 61.3572 | 61.3921 | 122.9507 | 61.6073 | 122.8865 | 61.3438 | 61.416 | 122.9202 | 61.3847 | 122.703 | 61.5346 | 61.566 | 61.4705 | 61.5018
1256.8906 | 123.2162 | -61.4319 | 61.5601 | 0.007391 | -0.086309 | -0.053207 | -0.043331 | -0.014093 | -0.033455 | -0.007779 | 61.56 | 0.212 | 61.4867 | -0.051417 | 0.020767 | 61.525 | -0.006014 | 61.3077 | 61.4393 | 61.3456 | 61.3787 | 61.3886 | 61.4178 | 61.3984 | 61.4241 | 122.9919 | 61.6439 | 122.9186 | 61.3805 | 61.4527 | 122.9568 | 61.4259 | 122.7396 | 61.5392 | 61.566 | 61.4659 | 61.4927
1257.8906 | 123.2437 | -61.4365 | 61.5417 | 0.002813 | -0.086309 | -0.053207 | -0.034174 | -0.009515 | -0.028877 | -0.007779 | 61.56 | 0.212 | 61.4912 | -0.046838 | 0.020767 | 61.5295 | -0.010593 | 61.3031 | 61.4393 | 61.3502 | 61.3833 | 61.4023 | 61.4269 | 61.4076 | 61.4287 | 122.9965 | 61.6485 | 122.9277 | 61.3896 | 61.4572 | 122.966 | 61.4259 | 122.7396 | 61.5392 | 61.5706 | 61.4705 | 61.5018
1258.8906 | 123.2712 | -61.3907 | 61.5784 | 0.002813 | -0.072572 | -0.053207 | -0.034174 | -0.009515 | -0.033455 | -0.007779 | 61.56 | 0.20284 | 61.4867 | -0.042259 | 0.025345 | 61.525 | -0.006014 | 61.2986 | 61.3935 | 61.3181 | 61.3375 | 61.3565 | 61.3812 | 61.3572 | 61.3829 | 122.9507 | 61.5935 | 122.8774 | 61.3484 | 61.416 | 122.9156 | 61.3847 | 122.6893 | 61.5346 | 61.566 | 61.4613 | 61.4927
1259.8906 | 123.2391 | -61.4227 | 61.5509 | 0.01197 | -0.086309 | -0.062364 | -0.038752 | -0.014093 | -0.033455 | -0.003201 | 61.5554 | 0.21658 | 61.4912 | -0.055996 | 0.020767 | 61.5295 | -0.001436 | 61.3077 | 61.4347 | 61.3364 | 61.3604 | 61.384 | 61.4086 | 61.3893 | 61.4195 | 122.9781 | 61.6393 | 122.914 | 61.3667 | 61.4435 | 122.9523 | 61.4213 | 122.7305 | 61.5346 | 61.5568 | 61.4705 | 61.4927
1260.8906 | 123.1934 | -61.4639 | 61.6333 | 0.002813 | -0.086309 | -0.057786 | -0.038752 | -0.009515 | -0.033455 | -0.007779 | 61.5646 | 0.212 | 61.4867 | -0.046838 | 0.029923 | 61.5295 | -0.006014 | 61.3123 | 61.4667 | 61.3776 | 61.4061 | 61.4252 | 61.4544 | 61.4305 | 61.4561 | 123.0285 | 61.6759 | 122.9506 | 61.4171 | 61.4939 | 122.9935 | 61.4579 | 122.7762 | 61.5346 | 61.5706 | 61.4567 | 61.4927
1261.8906 | 123.2529 | -61.4227 | 61.5555 | 0.01197 | -0.08173 | -0.053207 | -0.029595 | -0.009515 | -0.033455 | 0.010533 | 61.56 | 0.20742 | 61.4912 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3123 | 61.4347 | 61.341 | 61.3695 | 61.3931 | 61.4132 | 61.3893 | 61.4333 | 122.9827 | 61.6302 | 122.914 | 61.3713 | 61.4481 | 122.9523 | 61.4213 | 122.735 | 61.5346 | 61.5614 | 61.4659 | 61.4927
1262.8906 | 123.3307 | -61.409 | 61.5555 | 0.007391 | -0.086309 | -0.057786 | -0.034174 | -0.014093 | -0.033455 | -0.003201 | 61.56 | 0.212 | 61.4821 | -0.051417 | 0.025345 | 61.5341 | 0.003143 | 61.3123 | 61.4164 | 61.3227 | 61.3512 | 61.3748 | 61.3949 | 61.3755 | 61.4058 | 122.969 | 61.621 | 122.8911 | 61.3576 | 61.4343 | 122.9431 | 61.4121 | 122.7213 | 61.5346 | 61.5568 | 61.4567 | 61.4789
1263.8906 | 123.3078 | -61.4136 | 61.5692 | 0.007391 | -0.077151 | -0.04405 | -0.025017 | -0.000359 | -0.028877 | 0.005955 | 61.56 | 0.20742 | 61.4912 | -0.042259 | 0.020767 | 61.5295 | -0.006014 | 61.3077 | 61.421 | 61.3364 | 61.3695 | 61.3886 | 61.4132 | 61.3847 | 61.4195 | 122.9736 | 61.621 | 122.9048 | 61.3713 | 61.4343 | 122.9431 | 61.4076 | 122.7213 | 61.5392 | 61.566 | 61.4705 | 61.4973
1264.8906 | 123.2712 | -61.409 | 61.5463 | 0.016548 | -0.08173 | -0.053207 | -0.038752 | -0.018671 | -0.038034 | -0.003201 | 61.5508 | 0.20742 | 61.4867 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.2986 | 61.4255 | 61.3273 | 61.3558 | 61.3702 | 61.3903 | 61.371 | 61.4058 | 122.9598 | 61.6164 | 122.8957 | 61.3576 | 61.4343 | 122.9385 | 61.4076 | 122.7076 | 61.5255 | 61.5523 | 61.4613 | 61.4881
1265.8906 | 123.3032 | -61.3998 | 61.5692 | 0.01197 | -0.086309 | -0.062364 | -0.034174 | -0.014093 | -0.033455 | -0.003201 | 61.5508 | 0.212 | 61.4821 | -0.046838 | 0.020767 | 61.5295 | -0.006014 | 61.3031 | 61.4118 | 61.3135 | 61.3375 | 61.3657 | 61.3857 | 61.3664 | 61.3966 | 122.9507 | 61.6118 | 122.8819 | 61.353 | 61.4206 | 122.9294 | 61.3938 | 122.703 | 61.5301 | 61.5568 | 61.4613 | 61.4881
1266.8906 | 123.2391 | -61.4182 | 61.5692 | 0.002813 | -0.086309 | -0.057786 | -0.038752 | -0.004937 | -0.028877 | -0.007779 | 61.5554 | 0.20284 | 61.4912 | -0.051417 | 0.020767 | 61.5341 | -0.006014 | 61.3123 | 61.421 | 61.3318 | 61.3604 | 61.3794 | 61.4132 | 61.3893 | 61.4104 | 122.9736 | 61.621 | 122.9094 | 61.3667 | 61.4389 | 122.9523 | 61.4121 | 122.7305 | 61.5346 | 61.5614 | 61.4705 | 61.4973
1267.8906 | 123.3261 | -61.3907 | 61.5509 | 0.007391 | -0.08173 | -0.057786 | -0.034174 | -0.009515 | -0.038034 | -0.007779 | 61.56 | 0.20742 | 61.4958 | -0.051417 | 0.025345 | 61.5204 | -0.001436 | 61.3077 | 61.3981 | 61.309 | 61.3329 | 61.3565 | 61.3812 | 61.3527 | 61.3829 | 122.9507 | 61.5981 | 122.8865 | 61.3393 | 61.416 | 122.9111 | 61.3893 | 122.6984 | 61.5346 | 61.5614 | 61.4705 | 61.4973
1268.8906 | 123.2758 | -61.4365 | 61.5509 | 0.002813 | -0.08173 | -0.057786 | -0.029595 | -0.014093 | -0.033455 | -0.007779 | 61.56 | 0.20284 | 61.4912 | -0.042259 | 0.025345 | 61.5341 | -0.010593 | 61.3169 | 61.4393 | 61.3547 | 61.3787 | 61.4069 | 61.4224 | 61.403 | 61.4287 | 122.9965 | 61.6393 | 122.9277 | 61.3942 | 61.4618 | 122.9706 | 61.4259 | 122.7533 | 61.5346 | 61.5706 | 61.4659 | 61.5018
1269.8906 | 123.3124 | -61.3953 | 61.5784 | 0.01197 | -0.086309 | -0.057786 | -0.043331 | -0.023249 | -0.042612 | -0.007779 | 61.56 | 0.20742 | 61.4867 | -0.046838 | 0.025345 | 61.5295 | 0.003143 | 61.3077 | 61.4072 | 61.309 | 61.3375 | 61.3519 | 61.372 | 61.3527 | 61.3875 | 122.9553 | 61.6027 | 122.8819 | 61.3484 | 61.4206 | 122.9248 | 61.3984 | 122.703 | 61.5346 | 61.5568 | 61.4613 | 61.4835
1270.8906 | 123.2986 | -61.3953 | 61.5555 | 0.016548 | -0.072572 | -0.039471 | -0.01586 | 0.008797 | -0.01972 | 0.015112 | 61.5508 | 0.212 | 61.4775 | -0.046838 | 0.029923 | 61.5341 | 0.003143 | 61.3169 | 61.4118 | 61.3227 | 61.3558 | 61.3794 | 61.4041 | 61.3755 | 61.4104 | 122.9461 | 61.6073 | 122.8728 | 61.3484 | 61.4252 | 122.9294 | 61.3984 | 122.7121 | 61.5209 | 61.5477 | 61.4476 | 61.4744
1271.8906 | 123.2941 | -61.4136 | 61.5601 | 0.01197 | -0.090888 | -0.066943 | -0.052488 | -0.027827 | -0.04719 | -0.012357 | 61.5508 | 0.20742 | 61.4867 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.3031 | 61.4255 | 61.3227 | 61.3466 | 61.3611 | 61.3857 | 61.3664 | 61.4012 | 122.9644 | 61.621 | 122.9002 | 61.3622 | 61.4389 | 122.9431 | 61.4121 | 122.7167 | 61.5255 | 61.5523 | 61.4613 | 61.4881
1272.8906 | 123.3398 | -61.4136 | 61.5784 | 0.002813 | -0.10004 | -0.066943 | -0.052488 | -0.027827 | -0.042612 | -0.012357 | 61.5646 | 0.21658 | 61.4912 | -0.051417 | 0.020767 | 61.5204 | -0.006014 | 61.3123 | 61.4164 | 61.3135 | 61.3466 | 61.3611 | 61.3857 | 61.371 | 61.4012 | 122.9781 | 61.6302 | 122.9048 | 61.3622 | 61.4343 | 122.934 | 61.4076 | 122.7259 | 61.5438 | 61.5706 | 61.4705 | 61.4973
1273.8906 | 123.2712 | -61.3998 | 61.5921 | -0.001765 | -0.077151 | -0.053207 | -0.029595 | -0.009515 | -0.033455 | -0.012357 | 61.5554 | 0.20742 | 61.4867 | -0.051417 | 0.025345 | 61.5295 | -0.001436 | 61.2986 | 61.3981 | 61.3227 | 61.3466 | 61.3702 | 61.3903 | 61.3664 | 61.3875 | 122.9553 | 61.6073 | 122.8865 | 61.3484 | 61.4252 | 122.9294 | 61.3984 | 122.6984 | 61.5301 | 61.5568 | 61.4613 | 61.4881
1274.8906 | 123.23 | -61.3907 | 61.6104 | 0.002813 | -0.08173 | -0.071521 | -0.043331 | -0.014093 | -0.042612 | -0.007779 | 61.5508 | 0.20742 | 61.4958 | -0.046838 | 0.029923 | 61.5295 | -0.001436 | 61.3077 | 61.3935 | 61.309 | 61.3192 | 61.3474 | 61.3766 | 61.3481 | 61.3829 | 122.9415 | 61.5981 | 122.8865 | 61.3438 | 61.4206 | 122.9202 | 61.3893 | 122.6984 | 61.5209 | 61.5523 | 61.4659 | 61.4973
1275.9062 | 123.143 | -61.4502 | 61.5967 | 0.002813 | -0.086309 | -0.053207 | -0.043331 | -0.000359 | -0.033455 | 0.001377 | 61.5508 | 0.20742 | 61.4867 | -0.046838 | 0.025345 | 61.525 | -0.006014 | 61.3077 | 61.453 | 61.3639 | 61.397 | 61.4069 | 61.4498 | 61.4167 | 61.4516 | 123.001 | 61.6576 | 122.9369 | 61.4034 | 61.4755 | 122.9752 | 61.4442 | 122.7579 | 61.5255 | 61.5568 | 61.4613 | 61.4927
1276.8906 | 123.2895 | -61.3953 | 61.5738 | -0.001765 | -0.086309 | -0.062364 | -0.038752 | -0.018671 | -0.038034 | -0.007779 | 61.5554 | 0.20284 | 61.4867 | -0.051417 | 0.020767 | 61.5341 | 0.003143 | 61.3077 | 61.3935 | 61.309 | 61.3329 | 61.3565 | 61.3766 | 61.3572 | 61.3875 | 122.9507 | 61.5981 | 122.8819 | 61.3438 | 61.416 | 122.9294 | 61.3984 | 122.703 | 61.5346 | 61.5523 | 61.4659 | 61.4835
1277.8906 | 123.3032 | -61.4044 | 61.5967 | 0.002813 | -0.08173 | -0.057786 | -0.043331 | -0.014093 | -0.038034 | -0.007779 | 61.5554 | 0.20284 | 61.4912 | -0.046838 | 0.025345 | 61.5295 | -0.006014 | 61.3077 | 61.4072 | 61.3227 | 61.3466 | 61.3611 | 61.3903 | 61.3664 | 61.3966 | 122.9598 | 61.6073 | 122.8957 | 61.3576 | 61.4298 | 122.934 | 61.3984 | 122.7121 | 61.5301 | 61.5614 | 61.4659 | 61.4973
1278.8906 | 123.1888 | -61.4319 | 61.6241 | -0.001765 | -0.08173 | -0.04405 | -0.029595 | -0.009515 | -0.024298 | -0.003201 | 61.5508 | 0.212 | 61.4912 | -0.046838 | 0.025345 | 61.5341 | -0.001436 | 61.3169 | 61.4301 | 61.3502 | 61.3878 | 61.4023 | 61.4224 | 61.4076 | 61.4287 | 122.9827 | 61.6439 | 122.9231 | 61.385 | 61.4572 | 122.966 | 61.4304 | 122.7488 | 61.5255 | 61.5523 | 61.4659 | 61.4927
1279.8906 | 123.2986 | -61.3953 | 61.5601 | 0.007391 | -0.08173 | -0.057786 | -0.034174 | -0.014093 | -0.028877 | -0.003201 | 61.5554 | 0.20742 | 61.4867 | -0.051417 | 0.025345 | 61.525 | 0.003143 | 61.3031 | 61.4027 | 61.3135 | 61.3375 | 61.3611 | 61.3812 | 61.3664 | 61.3921 | 122.9507 | 61.6027 | 122.8819 | 61.3438 | 61.4206 | 122.9202 | 61.3984 | 122.6984 | 61.5301 | 61.5523 | 61.4613 | 61.4835
1280.8906 | 123.3215 | -61.4273 | 61.5921 | 0.007391 | -0.08173 | -0.048628 | -0.034174 | -0.004937 | -0.033455 | -0.012357 | 61.56 | 0.20742 | 61.4912 | -0.046838 | 0.020767 | 61.5295 | -0.001436 | 61.3123 | 61.4347 | 61.3456 | 61.3787 | 61.3931 | 61.4224 | 61.3939 | 61.4149 | 122.9873 | 61.6347 | 122.9186 | 61.3805 | 61.4481 | 122.9568 | 61.4259 | 122.7396 | 61.5392 | 61.5614 | 61.4705 | 61.4927
1281.8906 | 123.2025 | -61.3907 | 61.5417 | 0.002813 | -0.08173 | -0.053207 | -0.043331 | -0.009515 | -0.033455 | -0.016936 | 61.5554 | 0.20742 | 61.4867 | -0.046838 | 0.025345 | 61.5204 | -0.001436 | 61.3031 | 61.3935 | 61.309 | 61.3375 | 61.3474 | 61.3812 | 61.3572 | 61.3738 | 122.9461 | 61.5981 | 122.8774 | 61.3438 | 61.416 | 122.9111 | 61.3893 | 122.6938 | 61.5301 | 61.5568 | 61.4613 | 61.4881
1282.8906 | 123.3215 | -61.4227 | 61.5784 | 0.01197 | -0.08173 | -0.053207 | -0.029595 | -0.004937 | -0.024298 | 0.001377 | 61.5646 | 0.21658 | 61.4821 | -0.046838 | 0.025345 | 61.5204 | -0.006014 | 61.3077 | 61.4347 | 61.341 | 61.3695 | 61.3931 | 61.4178 | 61.3984 | 61.4241 | 122.9873 | 61.6393 | 122.9048 | 61.3759 | 61.4481 | 122.9431 | 61.4167 | 122.7305 | 61.5392 | 61.5706 | 61.4567 | 61.4881
1283.8906 | 123.2712 | -61.4182 | 61.5784 | 0.01197 | -0.072572 | -0.048628 | -0.029595 | -0.009515 | -0.033455 | -0.007779 | 61.56 | 0.19827 | 61.4867 | -0.046838 | 0.020767 | 61.5204 | -0.001436 | 61.3077 | 61.4301 | 61.3456 | 61.3695 | 61.3886 | 61.4086 | 61.3847 | 61.4104 | 122.9781 | 61.6164 | 122.9048 | 61.3713 | 61.4389 | 122.9385 | 61.4167 | 122.7259 | 61.5392 | 61.5614 | 61.4659 | 61.4881
1284.8906 | 123.3124 | -61.3998 | 61.5921 | 0.007391 | -0.086309 | -0.04405 | -0.034174 | -0.009515 | -0.024298 | 0.001377 | 61.5463 | 0.20742 | 61.4912 | -0.042259 | 0.025345 | 61.5341 | -0.006014 | 61.3169 | 61.4072 | 61.3135 | 61.3558 | 61.3657 | 61.3903 | 61.3755 | 61.4012 | 122.9461 | 61.6073 | 122.8911 | 61.3576 | 61.4252 | 122.934 | 61.3938 | 122.7167 | 61.5209 | 61.5523 | 61.4659 | 61.4973
1285.8906 | 123.2986 | -61.409 | 61.5784 | 0.002813 | -0.077151 | -0.048628 | -0.034174 | -0.000359 | -0.01972 | -0.007779 | 61.56 | 0.21658 | 61.4867 | -0.046838 | 0.029923 | 61.5295 | -0.001436 | 61.3123 | 61.4118 | 61.3318 | 61.3604 | 61.3748 | 61.4086 | 61.3893 | 61.4012 | 122.969 | 61.6256 | 122.8957 | 61.3622 | 61.4389 | 122.9385 | 61.4076 | 122.7213 | 61.5301 | 61.5614 | 61.4567 | 61.4881
1286.8906 | 123.3032 | -61.4044 | 61.5646 | 0.016548 | -0.077151 | -0.053207 | -0.038752 | -0.009515 | -0.033455 | -0.003201 | 61.56 | 0.20742 | 61.4867 | -0.046838 | 0.034501 | 61.5341 | 0.003143 | 61.3077 | 61.421 | 61.3273 | 61.3512 | 61.3657 | 61.3949 | 61.371 | 61.4012 | 122.9644 | 61.6118 | 122.8911 | 61.3576 | 61.4389 | 122.9385 | 61.4076 | 122.7121 | 61.5255 | 61.5568 | 61.4522 | 61.4835
1287.8906 | 123.3444 | -61.4227 | 61.5601 | 0.007391 | -0.077151 | -0.048628 | -0.034174 | -0.009515 | -0.028877 | -0.003201 | 61.5554 | 0.20742 | 61.4912 | -0.042259 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 61.4301 | 61.3456 | 61.3741 | 61.3886 | 61.4132 | 61.3939 | 61.4195 | 122.9781 | 61.6302 | 122.914 | 61.3805 | 61.4481 | 122.9523 | 61.4213 | 122.7305 | 61.5301 | 61.5568 | 61.4659 | 61.4927
1288.8906 | 123.2437 | -61.409 | 61.5738 | 0.007391 | -0.08173 | -0.04405 | -0.025017 | 0.004219 | -0.028877 | 0.001377 | 61.5554 | 0.20284 | 61.5004 | -0.055996 | 0.029923 | 61.525 | -0.001436 | 61.3215 | 61.4164 | 61.3273 | 61.3649 | 61.384 | 61.4132 | 61.3801 | 61.4104 | 122.9644 | 61.6118 | 122.9094 | 61.353 | 61.4389 | 122.934 | 61.4076 | 122.7305 | 61.5255 | 61.5568 | 61.4705 | 61.5018
1289.8906 | 123.3353 | -61.4044 | 61.5921 | 0.007391 | -0.067994 | -0.048628 | -0.025017 | -0.000359 | -0.01972 | 0.001377 | 61.56 | 0.212 | 61.4958 | -0.055996 | 0.025345 | 61.525 | -0.001436 | 61.3031 | 61.4118 | 61.3364 | 61.3558 | 61.3794 | 61.4041 | 61.3847 | 61.4058 | 122.9644 | 61.6164 | 122.9002 | 61.3484 | 61.4298 | 122.9294 | 61.403 | 122.7076 | 61.5346 | 61.5614 | 61.4705 | 61.4973
1290.8906 | 123.3444 | -61.409 | 61.5784 | 0.007391 | -0.072572 | -0.034893 | -0.029595 | 0.004219 | -0.024298 | 0.010533 | 61.5554 | 0.20742 | 61.4912 | -0.046838 | 0.020767 | 61.525 | -0.001436 | 61.3077 | 61.4164 | 61.3364 | 61.3741 | 61.3794 | 61.4132 | 61.3847 | 61.4195 | 122.9644 | 61.6164 | 122.9002 | 61.3622 | 61.4298 | 122.934 | 61.4076 | 122.7167 | 61.5346 | 61.5568 | 61.4705 | 61.4927
1291.8906 | 123.262 | -61.3815 | 61.5875 | 0.007391 | -0.067994 | -0.04405 | -0.025017 | -0.000359 | -0.01972 | 0.005955 | 61.56 | 0.212 | 61.4867 | -0.051417 | 0.034501 | 61.525 | -0.001436 | 61.2986 | 61.3889 | 61.3135 | 61.3375 | 61.3565 | 61.3812 | 61.3618 | 61.3875 | 122.9415 | 61.5935 | 122.8682 | 61.3301 | 61.416 | 122.9065 | 61.3801 | 122.6801 | 61.5255 | 61.5614 | 61.4522 | 61.4881
1292.8906 | 123.3078 | -61.4044 | 61.5967 | 0.01197 | -0.067994 | -0.039471 | -0.011281 | 0.013375 | -0.015142 | 0.01969 | 61.56 | 0.212 | 61.4867 | -0.042259 | 0.020767 | 61.525 | -0.006014 | 61.3077 | 61.4164 | 61.3364 | 61.3649 | 61.3931 | 61.4178 | 61.3893 | 61.4241 | 122.9644 | 61.6164 | 122.8911 | 61.3622 | 61.4252 | 122.9294 | 61.3984 | 122.7121 | 61.5392 | 61.566 | 61.4659 | 61.4927
1293.8906 | 123.2803 | -61.4319 | 61.6013 | 0.007391 | -0.067994 | -0.04405 | -0.01586 | 0.008797 | -0.015142 | 0.010533 | 61.5646 | 0.21658 | 61.4912 | -0.046838 | 0.025345 | 61.5295 | 0.003143 | 61.3123 | 61.4393 | 61.3639 | 61.3878 | 61.416 | 61.4407 | 61.4167 | 61.4424 | 122.9965 | 61.6485 | 122.9231 | 61.385 | 61.4572 | 122.9614 | 61.435 | 122.7442 | 61.5392 | 61.5614 | 61.4659 | 61.4881
1294.8906 | 123.2941 | -61.3998 | 61.5967 | 0.007391 | -0.067994 | -0.039471 | -0.020438 | 0.004219 | -0.015142 | 0.005955 | 61.5646 | 0.20284 | 61.4912 | -0.051417 | 0.029923 | 61.5341 | -0.006014 | 61.3123 | 61.4072 | 61.3318 | 61.3604 | 61.3794 | 61.4041 | 61.3847 | 61.4058 | 122.9644 | 61.6027 | 122.8911 | 61.3484 | 61.4298 | 122.934 | 61.3938 | 122.7121 | 61.5346 | 61.5706 | 61.4613 | 61.4973
1295.8906 | 123.1842 | -61.409 | 61.6241 | 0.007391 | -0.058836 | -0.034893 | -0.01586 | 0.004219 | -0.010563 | 0.01969 | 61.5646 | 0.20742 | 61.4867 | -0.046838 | 0.029923 | 61.525 | -0.001436 | 61.3077 | 61.4164 | 61.3502 | 61.3741 | 61.3931 | 61.4132 | 61.3984 | 61.4287 | 122.9736 | 61.6164 | 122.8957 | 61.3622 | 61.4389 | 122.934 | 61.4076 | 122.7167 | 61.5346 | 61.566 | 61.4567 | 61.4881
1296.8906 | 123.2712 | -61.4044 | 61.6104 | 0.007391 | -0.063415 | -0.025735 | -0.01586 | 0.013375 | -0.015142 | 0.010533 | 61.56 | 0.20284 | 61.4958 | -0.051417 | 0.020767 | 61.5204 | 0.003143 | 61.3123 | 61.4118 | 61.341 | 61.3787 | 61.3886 | 61.4178 | 61.3893 | 61.415 | 122.9644 | 61.6073 | 122.9002 | 61.353 | 61.4252 | 122.9248 | 61.4076 | 122.7167 | 61.5392 | 61.5568 | 61.4751 | 61.4927
1297.8906 | 123.1888 | -61.4456 | 61.6333 | 0.007391 | -0.067994 | -0.039471 | -0.020438 | 0.004219 | -0.015142 | 0.01969 | 61.5554 | 0.212 | 61.4958 | -0.042259 | 0.020767 | 61.525 | -0.001436 | 61.3123 | 61.453 | 61.3776 | 61.4061 | 61.4252 | 61.4498 | 61.4305 | 61.4653 | 123.001 | 61.6576 | 122.9414 | 61.4034 | 61.4664 | 122.9706 | 61.4442 | 122.7579 | 61.5346 | 61.5568 | 61.4751 | 61.4973
1298.8906 | 123.1338 | -61.4365 | 61.6608 | 0.01197 | -0.08173 | -0.053207 | -0.038752 | -0.000359 | -0.028877 | -0.003201 | 61.5646 | 0.212 | 61.5004 | -0.042259 | 0.029923 | 61.5158 | -0.001436 | 61.3031 | 61.4484 | 61.3547 | 61.3833 | 61.3977 | 61.4361 | 61.4076 | 61.4333 | 123.001 | 61.6485 | 122.9369 | 61.3942 | 61.4664 | 122.9523 | 61.435 | 122.7396 | 61.5346 | 61.566 | 61.4705 | 61.5018
1299.8906 | 123.2025 | -61.4273 | 61.6379 | 0.01197 | -0.077151 | -0.053207 | -0.029595 | -0.004937 | -0.028877 | 0.001377 | 61.5691 | 0.212 | 61.4867 | -0.055996 | 0.025345 | 61.525 | -0.006014 | 61.3077 | 61.4393 | 61.3502 | 61.3741 | 61.3977 | 61.4224 | 61.3984 | 61.4287 | 122.9965 | 61.6393 | 122.914 | 61.3713 | 61.4527 | 122.9523 | 61.4213 | 122.735 | 61.5438 | 61.5752 | 61.4613 | 61.4927
1300.8906 | 123.1705 | -61.4548 | 61.6333 | 0.007391 | -0.086309 | -0.039471 | -0.029595 | -0.004937 | -0.024298 | 0.001377 | 61.56 | 0.20742 | 61.4912 | -0.046838 | 0.020767 | 61.5295 | 0.003143 | 61.3031 | 61.4622 | 61.3685 | 61.4153 | 61.4252 | 61.4498 | 61.4305 | 61.4562 | 123.0148 | 61.6622 | 122.946 | 61.4079 | 61.4755 | 122.9843 | 61.4579 | 122.7579 | 61.5392 | 61.5568 | 61.4705 | 61.4881
1301.8906 | 123.1659 | -61.4365 | 61.6333 | 0.01197 | -0.086309 | -0.057786 | -0.043331 | -0.014093 | -0.033455 | -0.003201 | 61.56 | 0.20742 | 61.4958 | -0.046838 | 0.034501 | 61.5204 | 0.003143 | 61.3077 | 61.4484 | 61.3502 | 61.3787 | 61.3931 | 61.4224 | 61.403 | 61.4333 | 122.9965 | 61.6439 | 122.9323 | 61.3896 | 61.471 | 122.9568 | 61.4396 | 122.7442 | 61.5255 | 61.5568 | 61.4613 | 61.4927
1302.8906 | 123.2849 | -61.3907 | 61.5463 | 0.016548 | -0.077151 | -0.04405 | -0.029595 | -0.009515 | -0.028877 | 0.001377 | 61.5691 | 0.20742 | 61.5004 | -0.055996 | 0.020767 | 61.5158 | -0.001436 | 61.2894 | 61.4072 | 61.3135 | 61.3466 | 61.3611 | 61.3812 | 61.3618 | 61.3921 | 122.9598 | 61.5981 | 122.8911 | 61.3347 | 61.4115 | 122.9065 | 61.3893 | 122.6801 | 61.5484 | 61.5706 | 61.4796 | 61.5018
1303.8906 | 123.1522 | -61.4182 | 61.6379 | 0.007391 | -0.077151 | -0.048628 | -0.025017 | 0.004219 | -0.01972 | 0.005955 | 61.5691 | 0.20742 | 61.4958 | -0.046838 | 0.029923 | 61.525 | -0.010593 | 61.2986 | 61.4255 | 61.341 | 61.3695 | 61.3931 | 61.4224 | 61.3984 | 61.4241 | 122.9873 | 61.6256 | 122.914 | 61.3713 | 61.4481 | 122.9431 | 61.4076 | 122.7167 | 61.5392 | 61.5797 | 61.4659 | 61.5064
1304.8906 | 123.2071 | -61.4456 | 61.6379 | 0.01197 | -0.086309 | -0.053207 | -0.038752 | -0.014093 | -0.024298 | -0.007779 | 61.5646 | 0.20742 | 61.4912 | -0.042259 | 0.034501 | 61.525 | -0.001436 | 61.3077 | 61.4576 | 61.3593 | 61.3924 | 61.4069 | 61.4315 | 61.4213 | 61.4378 | 123.0102 | 61.653 | 122.9369 | 61.4034 | 61.4801 | 122.9706 | 61.4442 | 122.7533 | 61.5301 | 61.566 | 61.4567 | 61.4927
1305.8906 | 123.175 | -61.409 | 61.6379 | 0.002813 | -0.077151 | -0.062364 | -0.029595 | -0.009515 | -0.01972 | -0.003201 | 61.56 | 0.20742 | 61.4958 | -0.046838 | 0.029923 | 61.5204 | -0.001436 | 61.3077 | 61.4118 | 61.3318 | 61.3466 | 61.3794 | 61.3995 | 61.3893 | 61.4058 | 122.969 | 61.6164 | 122.9048 | 61.3622 | 61.4389 | 122.9294 | 61.4076 | 122.7167 | 61.5301 | 61.5614 | 61.4659 | 61.4973
1306.8906 | 123.2254 | -61.409 | 61.6013 | 0.007391 | -0.086309 | -0.053207 | -0.038752 | -0.000359 | -0.028877 | 0.001377 | 61.56 | 0.212 | 61.5004 | -0.046838 | 0.025345 | 61.5341 | 0.003143 | 61.2986 | 61.4164 | 61.3227 | 61.3558 | 61.3702 | 61.4086 | 61.3801 | 61.4104 | 122.969 | 61.621 | 122.9094 | 61.3622 | 61.4343 | 122.9431 | 61.4121 | 122.7076 | 61.5346 | 61.5568 | 61.4751 | 61.4973
1307.8906 | 123.2529 | -61.441 | 61.5555 | 0.002813 | -0.08173 | -0.048628 | -0.029595 | -0.009515 | -0.028877 | 0.001377 | 61.5646 | 0.212 | 61.5004 | -0.046838 | 0.016188 | 61.525 | -0.010593 | 61.2986 | 61.4439 | 61.3593 | 61.3924 | 61.4114 | 61.4315 | 61.4122 | 61.4424 | 123.0056 | 61.653 | 122.9414 | 61.3942 | 61.4572 | 122.966 | 61.4304 | 122.7396 | 61.5484 | 61.5752 | 61.4842 | 61.511
1308.8906 | 123.2071 | -61.409 | 61.5967 | 0.01197 | -0.077151 | -0.04405 | -0.025017 | -0.000359 | -0.015142 | 0.005955 | 61.5737 | 0.20742 | 61.5141 | -0.051417 | 0.029923 | 61.5158 | 0.003143 | 61.3031 | 61.421 | 61.3318 | 61.3649 | 61.384 | 61.4086 | 61.3939 | 61.415 | 122.9827 | 61.6164 | 122.9231 | 61.3576 | 61.4389 | 122.9248 | 61.4121 | 122.7121 | 61.5438 | 61.5706 | 61.4842 | 61.511
1309.8906 | 123.175 | -61.4182 | 61.6013 | 0.016548 | -0.077151 | -0.053207 | -0.034174 | -0.000359 | -0.028877 | 0.005955 | 61.5691 | 0.20742 | 61.5004 | -0.042259 | 0.029923 | 61.5158 | 0.003143 | 61.3031 | 61.4347 | 61.341 | 61.3649 | 61.384 | 61.4178 | 61.3893 | 61.4241 | 122.9873 | 61.6256 | 122.9186 | 61.3759 | 61.4481 | 122.934 | 61.4213 | 122.7213 | 61.5392 | 61.566 | 61.4705 | 61.4973
1310.8906 | 123.262 | -61.4365 | 61.5875 | 0.021127 | -0.077151 | -0.04405 | -0.01586 | 0.008797 | -0.024298 | 0.010533 | 61.5646 | 0.20742 | 61.4867 | -0.046838 | 0.025345 | 61.525 | 0.003143 | 61.3077 | 61.4576 | 61.3593 | 61.3924 | 61.4206 | 61.4453 | 61.4122 | 61.447 | 123.001 | 61.6439 | 122.9231 | 61.3896 | 61.4618 | 122.9614 | 61.4396 | 122.7442 | 61.5392 | 61.5614 | 61.4613 | 61.4835
1311.8906 | 123.2117 | -61.409 | 61.6013 | 0.01197 | -0.072572 | -0.039471 | -0.006703 | 0.013375 | -0.015142 | 0.015112 | 61.5691 | 0.212 | 61.5004 | -0.046838 | 0.029923 | 61.5066 | -0.010593 | 61.2894 | 61.421 | 61.3364 | 61.3695 | 61.4023 | 61.4224 | 61.3939 | 61.4241 | 122.9781 | 61.621 | 122.9094 | 61.3622 | 61.4389 | 122.9156 | 61.3984 | 122.6984 | 61.5392 | 61.5797 | 61.4705 | 61.511
1312.8906 | 123.2803 | -61.3998 | 61.5463 | 0.01197 | -0.067994 | -0.04405 | -0.029595 | 0.008797 | -0.01972 | 0.005955 | 61.5691 | 0.21658 | 61.4912 | -0.046838 | 0.020767 | 61.5158 | -0.006014 | 61.2986 | 61.4118 | 61.3318 | 61.3558 | 61.3702 | 61.4086 | 61.3801 | 61.4058 | 122.969 | 61.6164 | 122.8911 | 61.353 | 61.4206 | 122.9156 | 61.3938 | 122.6984 | 61.5484 | 61.5752 | 61.4705 | 61.4973
1313.8906 | 123.1979 | -61.4136 | 61.6058 | 0.007391 | -0.072572 | -0.034893 | -0.020438 | 0.008797 | -0.015142 | 0.015112 | 61.5783 | 0.212 | 61.505 | -0.046838 | 0.020767 | 61.5112 | -0.001436 | 61.294 | 61.421 | 61.341 | 61.3787 | 61.3931 | 61.4224 | 61.3984 | 61.4287 | 122.9919 | 61.6256 | 122.9186 | 61.3667 | 61.4343 | 122.9248 | 61.4121 | 122.7076 | 61.5575 | 61.5797 | 61.4842 | 61.5064
1314.8906 | 123.1522 | -61.4365 | 61.6013 | 0.01197 | -0.058836 | -0.034893 | -0.01586 | 0.008797 | -0.010563 | 0.01969 | 61.56 | 0.212 | 61.4912 | -0.042259 | 0.020767 | 61.5204 | 0.003143 | 61.294 | 61.4484 | 61.3776 | 61.4016 | 61.4206 | 61.4453 | 61.4259 | 61.4562 | 122.9965 | 61.6485 | 122.9277 | 61.3942 | 61.4572 | 122.9568 | 61.4396 | 122.7305 | 61.5392 | 61.5568 | 61.4705 | 61.4881
1315.8906 | 123.1934 | -61.4273 | 61.6379 | 0.01197 | -0.072572 | -0.025735 | -0.01586 | 0.013375 | -0.005985 | 0.015112 | 61.5783 | 0.212 | 61.5004 | -0.051417 | 0.025345 | 61.5158 | -0.006014 | 61.2986 | 61.4393 | 61.3547 | 61.4016 | 61.4114 | 61.4407 | 61.4213 | 61.4424 | 123.0056 | 61.6393 | 122.9277 | 61.3759 | 61.4527 | 122.9431 | 61.4213 | 122.7259 | 61.553 | 61.5843 | 61.4751 | 61.5064
1316.8906 | 123.1842 | -61.4456 | 61.5234 | 0.01197 | -0.072572 | -0.04405 | -0.020438 | -0.000359 | -0.01972 | 0.010533 | 61.5737 | 0.21658 | 61.5004 | -0.046838 | 0.025345 | 61.5204 | -0.006014 | 61.294 | 61.4576 | 61.373 | 61.4016 | 61.4252 | 61.4453 | 61.4259 | 61.4562 | 123.0193 | 61.6622 | 122.946 | 61.3988 | 61.471 | 122.966 | 61.4396 | 122.7396 | 61.5484 | 61.5797 | 61.4751 | 61.5064
1317.8906 | 123.1293 | -61.4182 | 61.615 | 0.016548 | -0.067994 | -0.025735 | -0.006703 | 0.017953 | -0.005985 | 0.024268 | 61.5829 | 0.20742 | 61.5141 | -0.042259 | 0.029923 | 61.5112 | -0.001436 | 61.2986 | 61.4347 | 61.3502 | 61.3924 | 61.4114 | 61.4361 | 61.4122 | 61.4424 | 123.001 | 61.6256 | 122.9323 | 61.3759 | 61.4481 | 122.9294 | 61.4167 | 122.7167 | 61.553 | 61.5843 | 61.4842 | 61.5156
1318.8906 | 123.2391 | -61.4044 | 61.6241 | 0.01197 | -0.054257 | -0.025735 | -0.002124 | 0.017953 | -0.005985 | 0.024268 | 61.5783 | 0.20742 | 61.5096 | -0.046838 | 0.025345 | 61.5112 | -0.010593 | 61.2894 | 61.4164 | 61.3502 | 61.3787 | 61.4023 | 61.4224 | 61.3984 | 61.4287 | 122.9827 | 61.6118 | 122.914 | 61.3576 | 61.4298 | 122.9156 | 61.3938 | 122.6938 | 61.553 | 61.5889 | 61.4842 | 61.5202
1319.8906 | 123.1705 | -61.4456 | 61.5829 | 0.007391 | -0.058836 | -0.016578 | 0.002454 | 0.027109 | -0.001406 | 0.024268 | 61.5737 | 0.212 | 61.4958 | -0.046838 | 0.025345 | 61.5066 | -0.001436 | 61.3031 | 61.453 | 61.3868 | 61.429 | 61.4481 | 61.4727 | 61.4442 | 61.4699 | 123.0193 | 61.6576 | 122.9414 | 61.3988 | 61.471 | 122.9523 | 61.4442 | 122.7488 | 61.5484 | 61.5752 | 61.4705 | 61.4973
1320.8906 | 123.2162 | -61.4136 | 61.5875 | 0.01197 | -0.058836 | -0.016578 | -0.002124 | 0.022531 | 0.003172 | 0.024268 | 61.5646 | 0.20742 | 61.5004 | -0.046838 | 0.016188 | 61.5158 | -0.001436 | 61.294 | 61.4255 | 61.3547 | 61.397 | 61.4114 | 61.4361 | 61.4167 | 61.4378 | 122.9781 | 61.621 | 122.914 | 61.3667 | 61.4298 | 122.9294 | 61.4121 | 122.7076 | 61.5484 | 61.566 | 61.4842 | 61.5018
1321.8906 | 123.1842 | -61.4502 | 61.5646 | 0.01197 | -0.058836 | -0.030314 | 0.002454 | 0.022531 | -0.005985 | 0.028846 | 61.5691 | 0.20742 | 61.5004 | -0.046838 | 0.025345 | 61.5158 | -0.010593 | 61.2894 | 61.4622 | 61.3914 | 61.4199 | 61.4526 | 61.4727 | 61.4442 | 61.479 | 123.0193 | 61.6576 | 122.9506 | 61.4034 | 61.4755 | 122.966 | 61.4396 | 122.7396 | 61.5438 | 61.5797 | 61.4751 | 61.511
1322.8906 | 123.1659 | -61.4456 | 61.6196 | 0.016548 | -0.063415 | -0.025735 | 0.007033 | 0.022531 | -0.001406 | 0.028846 | 61.5691 | 0.212 | 61.4958 | -0.051417 | 0.020767 | 61.5204 | -0.006014 | 61.294 | 61.4622 | 61.3822 | 61.4199 | 61.4527 | 61.4681 | 61.4442 | 61.4745 | 123.0148 | 61.6576 | 122.9414 | 61.3942 | 61.4664 | 122.966 | 61.4396 | 122.7396 | 61.5484 | 61.5752 | 61.4751 | 61.5018
1323.8906 | 123.23 | -61.4182 | 61.5509 | 0.007391 | -0.054257 | -0.021157 | -0.002124 | 0.027109 | -0.010563 | 0.024268 | 61.5737 | 0.21658 | 61.5004 | -0.046838 | 0.020767 | 61.5158 | -0.006014 | 61.2894 | 61.4255 | 61.3639 | 61.397 | 61.416 | 61.4453 | 61.4076 | 61.4424 | 122.9919 | 61.6347 | 122.9186 | 61.3713 | 61.4389 | 122.934 | 61.4121 | 122.7076 | 61.553 | 61.5797 | 61.4796 | 61.5064
1324.8906 | 123.175 | -61.4365 | 61.5601 | 0.021127 | -0.0451 | -0.012 | 0.011611 | 0.027109 | -0.001406 | 0.028846 | 61.5691 | 0.20742 | 61.5004 | -0.042259 | 0.029923 | 61.5158 | -0.001436 | 61.3031 | 61.4576 | 61.3914 | 61.4245 | 61.4481 | 61.4636 | 61.4351 | 61.4653 | 123.0056 | 61.6439 | 122.9369 | 61.3942 | 61.4664 | 122.9523 | 61.435 | 122.7396 | 61.5392 | 61.5706 | 61.4705 | 61.5018
1325.8906 | 123.2849 | -61.4227 | 61.5692 | 0.016548 | -0.054257 | -0.016578 | 0.007033 | 0.017953 | 0.003172 | 0.01969 | 61.5691 | 0.212 | 61.5096 | -0.046838 | 0.025345 | 61.5112 | -0.001436 | 61.294 | 61.4393 | 61.3685 | 61.4062 | 61.4298 | 61.4407 | 61.4259 | 61.4424 | 122.9919 | 61.6347 | 122.9323 | 61.3759 | 61.4481 | 122.934 | 61.4213 | 122.7167 | 61.5438 | 61.5706 | 61.4842 | 61.511
1326.8906 | 123.2895 | -61.4227 | 61.5417 | 0.021127 | -0.0451 | -0.012 | 0.01619 | 0.036265 | 0.012329 | 0.042581 | 61.5691 | 0.212 | 61.5004 | -0.046838 | 0.016188 | 61.5112 | -0.006014 | 61.2986 | 61.4439 | 61.3776 | 61.4107 | 61.4389 | 61.459 | 61.4351 | 61.4653 | 122.9919 | 61.6347 | 122.9231 | 61.3759 | 61.4389 | 122.934 | 61.4167 | 122.7213 | 61.553 | 61.5752 | 61.4842 | 61.5064
1327.8906 | 123.3215 | -61.3998 | 61.5417 | 0.016548 | -0.049678 | -0.012 | 0.011611 | 0.031687 | 0.003172 | 0.038003 | 61.5737 | 0.21658 | 61.5004 | -0.055996 | 0.025345 | 61.5158 | -0.001436 | 61.2986 | 61.4164 | 61.3502 | 61.3878 | 61.4115 | 61.4315 | 61.403 | 61.4378 | 122.9736 | 61.6164 | 122.9002 | 61.3438 | 61.4252 | 122.9156 | 61.3984 | 122.6984 | 61.5484 | 61.5752 | 61.4751 | 61.5018
1328.8906 | 123.2895 | -61.377 | 61.5784 | 0.016548 | -0.040521 | -0.012 | 0.01619 | 0.049999 | 0.016907 | 0.042581 | 61.5875 | 0.212 | 61.5096 | -0.055996 | 0.020767 | 61.5066 | -0.010593 | 61.2848 | 61.3935 | 61.3364 | 61.365 | 61.3931 | 61.427 | 61.3939 | 61.4195 | 122.9644 | 61.589 | 122.8865 | 61.321 | 61.3977 | 122.8836 | 61.3664 | 122.6618 | 61.5667 | 61.5981 | 61.4888 | 61.5202
1329.8906 | 123.317 | -61.4136 | 61.528 | 0.016548 | -0.035942 | -0.007421 | 0.011611 | 0.045421 | 0.012329 | 0.042581 | 61.5691 | 0.20284 | 61.5004 | -0.046838 | 0.016188 | 61.5158 | -0.006014 | 61.2986 | 61.4301 | 61.3776 | 61.4062 | 61.4252 | 61.459 | 61.4259 | 61.4562 | 122.9827 | 61.6164 | 122.914 | 61.3667 | 61.4298 | 122.9294 | 61.4076 | 122.7121 | 61.553 | 61.5752 | 61.4842 | 61.5064
1330.8906 | 123.2666 | -61.4044 | 61.5372 | 0.01197 | -0.0451 | -0.016578 | 0.002454 | 0.036265 | 0.00775 | 0.038003 | 61.5646 | 0.20742 | 61.5004 | -0.046838 | 0.025345 | 61.5204 | 0.003143 | 61.294 | 61.4164 | 61.3593 | 61.3878 | 61.4069 | 61.4407 | 61.4122 | 61.4424 | 122.969 | 61.6118 | 122.9048 | 61.3576 | 61.4298 | 122.9248 | 61.4076 | 122.6984 | 61.5392 | 61.5614 | 61.4751 | 61.4973
1331.8906 | 123.3398 | -61.4182 | 61.5509 | 0.01197 | -0.049678 | -0.012 | 0.011611 | 0.040843 | 0.012329 | 0.051737 | 61.5737 | 0.212 | 61.5004 | -0.051417 | 0.020767 | 61.5158 | -0.001436 | 61.294 | 61.4301 | 61.3685 | 61.4062 | 61.4298 | 61.459 | 61.4305 | 61.4699 | 122.9919 | 61.6302 | 122.9186 | 61.3667 | 61.4389 | 122.934 | 61.4167 | 122.7121 | 61.553 | 61.5752 | 61.4796 | 61.5018
1332.8906 | 123.2529 | -61.4044 | 61.528 | 0.01197 | -0.026784 | 0.006315 | 0.029925 | 0.063733 | 0.030642 | 0.060893 | 61.5646 | 0.19827 | 61.5004 | -0.051417 | 0.020767 | 61.5204 | -0.006014 | 61.2986 | 61.4164 | 61.3776 | 61.4107 | 61.4343 | 61.4682 | 61.4351 | 61.4653 | 122.969 | 61.6027 | 122.9048 | 61.353 | 61.4252 | 122.9248 | 61.3984 | 122.703 | 61.5438 | 61.5706 | 61.4796 | 61.5064
1333.8906 | 123.2529 | -61.4365 | 61.5509 | 0.016548 | -0.013048 | 0.020051 | 0.048239 | 0.077466 | 0.044377 | 0.074628 | 61.5508 | 0.212 | 61.4912 | -0.046838 | 0.016188 | 61.525 | -0.006014 | 61.294 | 61.453 | 61.4234 | 61.4565 | 61.4847 | 61.5139 | 61.4808 | 61.5111 | 122.9873 | 61.6485 | 122.9277 | 61.3896 | 61.4526 | 122.9614 | 61.4304 | 122.7305 | 61.5346 | 61.5568 | 61.4751 | 61.4973
1334.8906 | 123.2346 | -61.4319 | 61.5601 | 0.016548 | -0.022205 | 0.001736 | 0.034504 | 0.059155 | 0.026064 | 0.060893 | 61.5737 | 0.20742 | 61.5096 | -0.055996 | 0.016188 | 61.5204 | -0.006014 | 61.2894 | 61.4484 | 61.4097 | 61.4336 | 61.4664 | 61.491 | 61.4579 | 61.4928 | 123.0056 | 61.6393 | 122.9414 | 61.3759 | 61.4481 | 122.9523 | 61.4259 | 122.7213 | 61.5575 | 61.5797 | 61.4934 | 61.5156
1335.8906 | 123.2391 | -61.4227 | 61.5509 | 0.01197 | -0.035942 | -0.002842 | 0.01619 | 0.045421 | 0.012329 | 0.047159 | 61.56 | 0.21658 | 61.4867 | -0.051417 | 0.025345 | 61.5204 | -0.001436 | 61.3077 | 61.4347 | 61.3868 | 61.4199 | 61.4389 | 61.4681 | 61.4351 | 61.4699 | 122.9827 | 61.6393 | 122.9094 | 61.3713 | 61.4481 | 122.9431 | 61.4213 | 122.7305 | 61.5346 | 61.5614 | 61.4613 | 61.4881
1336.8906 | 123.2483 | -61.4319 | 61.5601 | 0.016548 | -0.026784 | 0.006315 | 0.025347 | 0.059155 | 0.030642 | 0.065472 | 61.5737 | 0.212 | 61.5004 | -0.051417 | 0.020767 | 61.5158 | -0.001436 | 61.2986 | 61.4484 | 61.4051 | 61.4382 | 61.4572 | 61.491 | 61.4625 | 61.4974 | 123.0056 | 61.6439 | 122.9323 | 61.3805 | 61.4527 | 122.9477 | 61.4304 | 122.7305 | 61.553 | 61.5752 | 61.4796 | 61.5018
1337.8906 | 123.2529 | -61.4136 | 61.5463 | 0.021127 | -0.031363 | 0.006315 | 0.034504 | 0.063733 | 0.026064 | 0.056315 | 61.5691 | 0.21658 | 61.5004 | -0.046838 | 0.025345 | 61.525 | -0.006014 | 61.294 | 61.4347 | 61.3822 | 61.4199 | 61.4481 | 61.4773 | 61.4396 | 61.4699 | 122.9827 | 61.6302 | 122.914 | 61.3667 | 61.4389 | 122.9385 | 61.4076 | 122.7076 | 61.5438 | 61.5752 | 61.4751 | 61.5064
1338.8906 | 123.2712 | -61.4273 | 61.5646 | 0.021127 | -0.013048 | 0.020051 | 0.034504 | 0.06831 | 0.039799 | 0.074628 | 61.5691 | 0.20742 | 61.5004 | -0.046838 | 0.034501 | 61.5158 | -0.006014 | 61.2986 | 61.4484 | 61.4143 | 61.4474 | 61.4618 | 61.4956 | 61.4671 | 61.5019 | 122.9965 | 61.6347 | 122.9277 | 61.3805 | 61.4618 | 122.9431 | 61.4213 | 122.7259 | 61.5346 | 61.5752 | 61.4659 | 61.5064
1339.8906 | 123.1979 | -61.4319 | 61.5875 | 0.01197 | -0.040521 | -0.012 | 0.011611 | 0.040843 | 0.00775 | 0.042581 | 61.5783 | 0.212 | 61.505 | -0.046838 | 0.020767 | 61.5158 | -0.006014 | 61.294 | 61.4439 | 61.3914 | 61.4199 | 61.4435 | 61.4727 | 61.4396 | 61.4745 | 123.0102 | 61.6439 | 122.9369 | 61.385 | 61.4527 | 122.9477 | 61.4259 | 122.7259 | 61.5575 | 61.5843 | 61.4842 | 61.511
1340.8906 | 123.2666 | -61.4044 | 61.5784 | 0.007391 | -0.022205 | 0.006315 | 0.029925 | 0.059155 | 0.035221 | 0.065472 | 61.5737 | 0.20742 | 61.5187 | -0.046838 | 0.025345 | 61.5112 | -0.006014 | 61.2894 | 61.4118 | 61.3822 | 61.4107 | 61.4343 | 61.4636 | 61.4396 | 61.4699 | 122.9781 | 61.6118 | 122.9231 | 61.3576 | 61.4298 | 122.9156 | 61.3984 | 122.6938 | 61.5484 | 61.5797 | 61.4934 | 61.5247
1341.8906 | 123.23 | -61.409 | 61.5738 | 0.01197 | -0.026784 | 0.006315 | 0.025347 | 0.063733 | 0.030642 | 0.060893 | 61.5783 | 0.20284 | 61.505 | -0.055996 | 0.016188 | 61.5112 | -0.001436 | 61.294 | 61.421 | 61.3822 | 61.4153 | 61.4343 | 61.4727 | 61.4396 | 61.4699 | 122.9873 | 61.6118 | 122.914 | 61.353 | 61.4252 | 122.9202 | 61.4076 | 122.703 | 61.5621 | 61.5797 | 61.4888 | 61.5064
1342.8906 | 123.2391 | -61.4044 | 61.5555 | 0.007391 | -0.058836 | -0.030314 | -0.006703 | 0.017953 | -0.005985 | 0.028846 | 61.5783 | 0.212 | 61.5187 | -0.051417 | 0.020767 | 61.5204 | -0.010593 | 61.2757 | 61.4118 | 61.3456 | 61.3741 | 61.3977 | 61.4224 | 61.3984 | 61.4333 | 122.9827 | 61.6164 | 122.9231 | 61.353 | 61.4252 | 122.9248 | 61.3938 | 122.6801 | 61.5575 | 61.5889 | 61.4979 | 61.5293
1343.8906 | 123.2529 | -61.3953 | 61.6013 | 0.016548 | -0.077151 | -0.053207 | -0.034174 | -0.004937 | -0.024298 | 0.001377 | 61.5691 | 0.212 | 61.5141 | -0.046838 | 0.029923 | 61.5158 | -0.010593 | 61.2848 | 61.4118 | 61.3181 | 61.3421 | 61.3611 | 61.3903 | 61.371 | 61.3966 | 122.9644 | 61.6073 | 122.9094 | 61.3484 | 61.4252 | 122.9111 | 61.3847 | 122.6801 | 61.5392 | 61.5797 | 61.4842 | 61.5247
1344.8906 | 123.2437 | -61.4136 | 61.5784 | 0.01197 | -0.072572 | -0.04405 | -0.020438 | 0.008797 | -0.024298 | 0.005955 | 61.5691 | 0.20284 | 61.5096 | -0.046838 | 0.025345 | 61.5112 | -0.006014 | 61.294 | 61.4255 | 61.341 | 61.3695 | 61.3931 | 61.4224 | 61.3893 | 61.4195 | 122.9827 | 61.6164 | 122.9231 | 61.3667 | 61.4389 | 122.9248 | 61.4076 | 122.7076 | 61.5438 | 61.5752 | 61.4842 | 61.5156
1345.8906 | 123.262 | -61.3907 | 61.5692 | 0.01197 | -0.10462 | -0.062364 | -0.043331 | -0.014093 | -0.033455 | -0.003201 | 61.5691 | 0.212 | 61.5004 | -0.051417 | 0.025345 | 61.5112 | -0.010593 | 61.2894 | 61.4027 | 61.2861 | 61.3283 | 61.3474 | 61.3766 | 61.3572 | 61.3875 | 122.9598 | 61.6027 | 122.8911 | 61.3393 | 61.416 | 122.9019 | 61.3801 | 122.6801 | 61.5438 | 61.5797 | 61.4751 | 61.511
1346.8906 | 123.262 | -61.4273 | 61.5921 | 0.002813 | -0.058836 | -0.034893 | -0.006703 | 0.013375 | -0.005985 | 0.024268 | 61.5737 | 0.22116 | 61.5141 | -0.051417 | 0.029923 | 61.5112 | -0.006014 | 61.2894 | 61.4301 | 61.3685 | 61.3924 | 61.4206 | 61.4407 | 61.4213 | 61.4516 | 123.001 | 61.6485 | 122.9414 | 61.3759 | 61.4572 | 122.9385 | 61.4213 | 122.7167 | 61.5438 | 61.5797 | 61.4842 | 61.5202
1347.8906 | 123.2529 | -61.3998 | 61.6013 | 0.007391 | -0.054257 | -0.021157 | -0.002124 | 0.027109 | -0.001406 | 0.024268 | 61.5783 | 0.212 | 61.5096 | -0.042259 | 0.020767 | 61.5112 | 0.003143 | 61.294 | 61.4072 | 61.3456 | 61.3787 | 61.3977 | 61.427 | 61.3984 | 61.4241 | 122.9781 | 61.6118 | 122.9094 | 61.3576 | 61.4206 | 122.9111 | 61.403 | 122.6938 | 61.5575 | 61.5752 | 61.4888 | 61.5064
1348.8906 | 123.2574 | -61.4227 | 61.6058 | 0.002813 | -0.08173 | -0.057786 | -0.038752 | -0.009515 | -0.033455 | -0.003201 | 61.5783 | 0.20284 | 61.5096 | -0.042259 | 0.025345 | 61.5066 | -0.006014 | 61.2848 | 61.4255 | 61.341 | 61.3649 | 61.384 | 61.4132 | 61.3893 | 61.4195 | 123.001 | 61.6256 | 122.9323 | 61.3805 | 61.4481 | 122.9294 | 61.4167 | 122.7076 | 61.553 | 61.5843 | 61.4842 | 61.5156
1349.8906 | 123.2758 | -61.3861 | 61.5921 | 0.007391 | -0.12294 | -0.085257 | -0.070802 | -0.050716 | -0.060926 | -0.035248 | 61.5875 | 0.21658 | 61.5096 | -0.042259 | 0.020767 | 61.5066 | -0.010593 | 61.2803 | 61.3935 | 61.2632 | 61.3009 | 61.3153 | 61.3354 | 61.3252 | 61.3509 | 122.9736 | 61.6027 | 122.8957 | 61.3438 | 61.4069 | 122.8928 | 61.3755 | 122.6664 | 61.5667 | 61.5981 | 61.4888 | 61.5202
1350.8906 | 123.2712 | -61.4044 | 61.5875 | 0.007391 | -0.17331 | -0.13104 | -0.11659 | -0.082762 | -0.11129 | -0.085608 | 61.5783 | 0.212 | 61.505 | -0.046838 | 0.025345 | 61.5112 | -0.001436 | 61.2848 | 61.4118 | 61.2311 | 61.2734 | 61.2878 | 61.3217 | 61.2931 | 61.3188 | 122.9827 | 61.6164 | 122.9094 | 61.3576 | 61.4298 | 122.9156 | 61.403 | 122.6893 | 61.553 | 61.5797 | 61.4796 | 61.5064
1351.8906 | 123.2758 | -61.4044 | 61.6013 | 0.002813 | -0.17331 | -0.1402 | -0.12574 | -0.08734 | -0.11587 | -0.085608 | 61.5875 | 0.212 | 61.5187 | -0.042259 | 0.025345 | 61.5021 | -0.006014 | 61.2803 | 61.4072 | 61.2311 | 61.2642 | 61.2787 | 61.3171 | 61.2886 | 61.3188 | 122.9919 | 61.6164 | 122.9231 | 61.3622 | 61.4298 | 122.9065 | 61.3984 | 122.6847 | 61.5621 | 61.5935 | 61.4934 | 61.5247
1352.8906 | 123.2941 | -61.3953 | 61.6104 | 0.01197 | -0.17788 | -0.14478 | -0.12574 | -0.096496 | -0.11129 | -0.085608 | 61.5875 | 0.212 | 61.5233 | -0.051417 | 0.025345 | 61.5021 | -0.010593 | 61.2848 | 61.4072 | 61.2174 | 61.2505 | 61.2695 | 61.2988 | 61.284 | 61.3097 | 122.9827 | 61.6073 | 122.9186 | 61.3438 | 61.4206 | 122.8973 | 61.3847 | 122.6801 | 61.5621 | 61.5981 | 61.4979 | 61.5339
1353.8906 | 123.3307 | -61.4044 | 61.5875 | 0.007391 | -0.15041 | -0.12189 | -0.10285 | -0.073606 | -0.097553 | -0.067295 | 61.5783 | 0.20742 | 61.5141 | -0.042259 | 0.020767 | 61.5112 | -0.006014 | 61.2894 | 61.4118 | 61.254 | 61.2825 | 61.3016 | 61.3308 | 61.3069 | 61.3371 | 122.9827 | 61.6118 | 122.9186 | 61.3622 | 61.4252 | 122.9156 | 61.3984 | 122.6938 | 61.5575 | 61.5843 | 61.4934 | 61.5202
1354.8906 | 123.3307 | -61.3861 | 61.5921 | 0.007391 | -0.15499 | -0.12646 | -0.10743 | -0.069028 | -0.092974 | -0.058139 | 61.5875 | 0.21658 | 61.5141 | -0.046838 | 0.034501 | 61.5112 | 0.003143 | 61.2803 | 61.3935 | 61.2311 | 61.2596 | 61.2787 | 61.3171 | 61.2931 | 61.328 | 122.9736 | 61.6027 | 122.9002 | 61.3393 | 61.4206 | 122.8973 | 61.3893 | 122.6664 | 61.553 | 61.5843 | 61.4796 | 61.511
1355.8906 | 123.3215 | -61.3861 | 61.6013 | 0.007391 | -0.18246 | -0.14936 | -0.1349 | -0.10107 | -0.12502 | -0.090186 | 61.5829 | 0.22116 | 61.5233 | -0.055996 | 0.029923 | 61.5021 | -0.006014 | 61.2848 | 61.3935 | 61.2036 | 61.2368 | 61.2512 | 61.285 | 61.2611 | 61.2959 | 122.969 | 61.6073 | 122.9094 | 61.3301 | 61.416 | 122.8882 | 61.3801 | 122.6709 | 61.553 | 61.5889 | 61.4934 | 61.5293
1356.8906 | 123.2895 | -61.3815 | 61.6058 | 0.01197 | -0.16415 | -0.13104 | -0.11201 | -0.078184 | -0.10671 | -0.08103 | 61.5783 | 0.20742 | 61.5141 | -0.042259 | 0.029923 | 61.5158 | -0.006014 | 61.2848 | 61.3935 | 61.2174 | 61.2505 | 61.2695 | 61.3033 | 61.2748 | 61.3005 | 122.9598 | 61.589 | 122.8957 | 61.3393 | 61.4115 | 122.8973 | 61.3755 | 122.6664 | 61.5484 | 61.5843 | 61.4842 | 61.5202
1357.8906 | 123.2758 | -61.377 | 61.6058 | 0.007391 | -0.15499 | -0.13104 | -0.11201 | -0.078184 | -0.097553 | -0.071874 | 61.5875 | 0.212 | 61.5096 | -0.055996 | 0.029923 | 61.5021 | -0.006014 | 61.2894 | 61.3843 | 61.222 | 61.2459 | 61.2649 | 61.2988 | 61.2794 | 61.3051 | 122.9644 | 61.589 | 122.8865 | 61.321 | 61.4069 | 122.879 | 61.3709 | 122.6664 | 61.5575 | 61.5935 | 61.4796 | 61.5156
1358.8906 | 123.3032 | -61.4136 | 61.5875 | 0.01197 | -0.15957 | -0.12646 | -0.10743 | -0.073606 | -0.10671 | -0.067295 | 61.5737 | 0.21658 | 61.5187 | -0.042259 | 0.025345 | 61.4975 | -0.001436 | 61.2894 | 61.4255 | 61.254 | 61.2871 | 61.3061 | 61.34 | 61.3069 | 61.3463 | 122.9873 | 61.6302 | 122.9323 | 61.3713 | 61.4389 | 122.9111 | 61.4121 | 122.703 | 61.5484 | 61.5752 | 61.4934 | 61.5202
1359.8906 | 123.349 | -61.3815 | 61.6104 | 0.002813 | -0.16873 | -0.14478 | -0.12574 | -0.08734 | -0.11129 | -0.085608 | 61.5875 | 0.212 | 61.5141 | -0.042259 | 0.025345 | 61.5021 | 0.003143 | 61.2803 | 61.3843 | 61.2128 | 61.2368 | 61.2558 | 61.2942 | 61.2702 | 61.2959 | 122.969 | 61.5935 | 122.8957 | 61.3393 | 61.4069 | 122.8836 | 61.3847 | 122.6618 | 61.5621 | 61.5843 | 61.4888 | 61.511
1360.8906 | 123.2529 | -61.3907 | 61.5967 | 0.007391 | -0.22367 | -0.2043 | -0.17611 | -0.14228 | -0.16623 | -0.12223 | 61.5829 | 0.22116 | 61.505 | -0.046838 | 0.025345 | 61.5112 | -0.001436 | 61.294 | 61.3981 | 61.167 | 61.1864 | 61.2146 | 61.2484 | 61.2245 | 61.2685 | 122.9736 | 61.6118 | 122.8957 | 61.3438 | 61.416 | 122.9019 | 61.3893 | 122.6847 | 61.5575 | 61.5843 | 61.4796 | 61.5064
1361.8906 | 123.349 | -61.3815 | 61.5921 | 0.007391 | -0.2191 | -0.19514 | -0.18069 | -0.14228 | -0.16165 | -0.13139 | 61.5829 | 0.21658 | 61.5187 | -0.046838 | 0.020767 | 61.5021 | -0.001436 | 61.2894 | 61.3889 | 61.1624 | 61.1864 | 61.2008 | 61.2393 | 61.2199 | 61.2501 | 122.9644 | 61.5981 | 122.9002 | 61.3347 | 61.4023 | 122.8836 | 61.3801 | 122.6709 | 61.5621 | 61.5843 | 61.4979 | 61.5202
1362.8906 | 123.2574 | -61.3861 | 61.5875 | 0.007391 | -0.22367 | -0.20888 | -0.17611 | -0.14685 | -0.16623 | -0.13139 | 61.5875 | 0.20742 | 61.5233 | -0.046838 | 0.034501 | 61.4975 | -0.001436 | 61.2848 | 61.3935 | 61.1624 | 61.1772 | 61.21 | 61.2393 | 61.2199 | 61.2547 | 122.9736 | 61.5935 | 122.9094 | 61.3393 | 61.4206 | 122.8836 | 61.3847 | 122.6709 | 61.553 | 61.5889 | 61.4888 | 61.5247
1363.8906 | 123.2254 | -61.377 | 61.5875 | 0.007391 | -0.19162 | -0.16767 | -0.14406 | -0.11939 | -0.13876 | -0.10392 | 61.5875 | 0.212 | 61.5233 | -0.046838 | 0.034501 | 61.4975 | 0.003143 | 61.2848 | 61.3843 | 61.1853 | 61.2093 | 61.2329 | 61.2576 | 61.2382 | 61.273 | 122.9644 | 61.589 | 122.9002 | 61.3301 | 61.4115 | 122.8744 | 61.3801 | 122.6618 | 61.553 | 61.5843 | 61.4888 | 61.5202
1364.8906 | 123.2437 | -61.3678 | 61.615 | 0.01197 | -0.19162 | -0.17225 | -0.14406 | -0.10565 | -0.13418 | -0.1085 | 61.5966 | 0.212 | 61.5233 | -0.046838 | 0.029923 | 61.4975 | 0.003143 | 61.2848 | 61.3798 | 61.1762 | 61.1955 | 61.2237 | 61.2621 | 61.2336 | 61.2593 | 122.9644 | 61.5798 | 122.8911 | 61.321 | 61.3977 | 122.8653 | 61.3709 | 122.6526 | 61.5667 | 61.5935 | 61.4934 | 61.5202
1365.8906 | 123.2529 | -61.3724 | 61.6425 | 0.01197 | -0.18704 | -0.14936 | -0.13032 | -0.096496 | -0.12502 | -0.090186 | 61.592 | 0.22116 | 61.5233 | -0.051417 | 0.020767 | 61.5021 | 0.003143 | 61.2803 | 61.3843 | 61.1853 | 61.223 | 61.2421 | 61.2759 | 61.2474 | 61.2822 | 122.9644 | 61.5935 | 122.8957 | 61.321 | 61.3931 | 122.8744 | 61.3755 | 122.6526 | 61.5713 | 61.5889 | 61.5025 | 61.5202
1366.8906 | 123.3261 | -61.3586 | 61.615 | 0.01197 | -0.15957 | -0.1402 | -0.12116 | -0.08734 | -0.10213 | -0.08103 | 61.5829 | 0.20742 | 61.5096 | -0.051417 | 0.020767 | 61.5066 | 0.003143 | 61.2848 | 61.3706 | 61.1991 | 61.2184 | 61.2375 | 61.2713 | 61.2565 | 61.2776 | 122.9415 | 61.5661 | 122.8682 | 61.3072 | 61.3794 | 122.8653 | 61.3618 | 122.6435 | 61.5621 | 61.5797 | 61.4888 | 61.5064
1367.8906 | 123.2529 | -61.3953 | 61.6058 | 0.007391 | -0.25572 | -0.23177 | -0.20816 | -0.17432 | -0.19828 | -0.16801 | 61.5829 | 0.22116 | 61.5233 | -0.046838 | 0.025345 | 61.5021 | -0.006014 | 61.2894 | 61.4027 | 61.1395 | 61.1635 | 61.1871 | 61.2209 | 61.197 | 61.2272 | 122.9781 | 61.6164 | 122.9186 | 61.3484 | 61.4206 | 122.8973 | 61.3892 | 122.6847 | 61.5575 | 61.5889 | 61.4979 | 61.5293
1368.8906 | 123.2941 | -61.377 | 61.6104 | 0.002813 | -0.2603 | -0.23635 | -0.21274 | -0.16974 | -0.19828 | -0.15886 | 61.5783 | 0.21658 | 61.505 | -0.046838 | 0.029923 | 61.5112 | -0.001436 | 61.2894 | 61.3798 | 61.1166 | 61.1406 | 61.1642 | 61.2072 | 61.1787 | 61.2181 | 122.9553 | 61.5935 | 122.8819 | 61.3301 | 61.4069 | 122.8882 | 61.3755 | 122.6664 | 61.5484 | 61.5797 | 61.4751 | 61.5064
1369.8906 | 123.262 | -61.3724 | 61.615 | 0.01197 | -0.2191 | -0.19514 | -0.16695 | -0.12396 | -0.15707 | -0.13139 | 61.5875 | 0.20284 | 61.5233 | -0.042259 | 0.025345 | 61.5021 | -0.006014 | 61.2757 | 61.3843 | 61.1533 | 61.1772 | 61.2054 | 61.2484 | 61.2153 | 61.241 | 122.9598 | 61.5752 | 122.8957 | 61.3301 | 61.3977 | 122.8744 | 61.3664 | 122.6481 | 61.5621 | 61.5935 | 61.4979 | 61.5293
1370.8906 | 123.2849 | -61.3907 | 61.6013 | 0.007391 | -0.26946 | -0.24551 | -0.21274 | -0.16974 | -0.20286 | -0.16801 | 61.592 | 0.20742 | 61.5141 | -0.046838 | 0.029923 | 61.5021 | -0.001436 | 61.2848 | 61.3981 | 61.1212 | 61.1452 | 61.178 | 61.2209 | 61.1878 | 61.2227 | 122.9827 | 61.5981 | 122.9048 | 61.3438 | 61.4206 | 122.8928 | 61.3893 | 122.6755 | 61.5621 | 61.5935 | 61.4842 | 61.5156
1371.8906 | 123.1888 | -61.3953 | 61.6425 | 0.007391 | -0.33357 | -0.30045 | -0.28141 | -0.23841 | -0.26695 | -0.22753 | 61.5966 | 0.212 | 61.5279 | -0.046838 | 0.029923 | 61.4883 | -0.006014 | 61.2711 | 61.4027 | 61.0617 | 61.0948 | 61.1139 | 61.1569 | 61.1283 | 61.1677 | 122.9919 | 61.6073 | 122.9231 | 61.3484 | 61.4252 | 122.8836 | 61.3892 | 122.6664 | 61.5667 | 61.6026 | 61.4979 | 61.5339
1372.8906 | 123.2941 | -61.377 | 61.6379 | 0.016548 | -0.31983 | -0.29129 | -0.26768 | -0.22468 | -0.25322 | -0.2138 | 61.5829 | 0.21658 | 61.5187 | -0.046838 | 0.029923 | 61.5021 | -0.015171 | 61.2894 | 61.3935 | 61.0571 | 61.0857 | 61.1093 | 61.1523 | 61.1237 | 61.1632 | 122.9598 | 61.5935 | 122.8957 | 61.3301 | 61.4069 | 122.879 | 61.3618 | 122.6664 | 61.553 | 61.5981 | 61.4888 | 61.5339
1373.8906 | 123.3078 | -61.3724 | 61.6516 | 0.002813 | -0.33814 | -0.30961 | -0.28141 | -0.23383 | -0.27153 | -0.23211 | 61.5966 | 0.212 | 61.5279 | -0.042259 | 0.025345 | 61.4929 | -0.001436 | 61.2848 | 61.3752 | 61.0342 | 61.0628 | 61.091 | 61.1385 | 61.1008 | 61.1403 | 122.969 | 61.5844 | 122.9002 | 61.3301 | 61.3977 | 122.8653 | 61.3709 | 122.6572 | 61.5713 | 61.5981 | 61.5025 | 61.5293
1374.8906 | 123.1705 | -61.3815 | 61.6379 | 0.01197 | -0.27862 | -0.25924 | -0.22189 | -0.19263 | -0.22575 | -0.18175 | 61.6058 | 0.212 | 61.5324 | -0.046838 | 0.020767 | 61.4883 | -0.006014 | 61.2711 | 61.3935 | 61.1029 | 61.1223 | 61.1596 | 61.1889 | 61.1558 | 61.1998 | 122.9873 | 61.5935 | 122.914 | 61.3347 | 61.4023 | 122.8699 | 61.3755 | 122.6526 | 61.585 | 61.6118 | 61.5117 | 61.5385
1375.8906 | 123.2208 | -61.4136 | 61.6562 | 0.007391 | -0.29693 | -0.27298 | -0.24936 | -0.21094 | -0.23948 | -0.20922 | 61.592 | 0.212 | 61.5233 | -0.042259 | 0.025345 | 61.4929 | -0.006014 | 61.2757 | 61.421 | 61.1166 | 61.1406 | 61.1642 | 61.2026 | 61.1741 | 61.2044 | 123.0056 | 61.6256 | 122.9369 | 61.3713 | 61.4389 | 122.9065 | 61.4076 | 122.6893 | 61.5667 | 61.5981 | 61.4979 | 61.5293
1376.8906 | 123.1659 | -61.3998 | 61.647 | 0.007391 | -0.28778 | -0.26382 | -0.24479 | -0.19721 | -0.22575 | -0.19548 | 61.592 | 0.20284 | 61.5233 | -0.046838 | 0.029923 | 61.4929 | -0.001436 | 61.2803 | 61.4072 | 61.1121 | 61.136 | 61.1551 | 61.2026 | 61.1741 | 61.2044 | 122.9919 | 61.6027 | 122.9231 | 61.353 | 61.4298 | 122.8928 | 61.3984 | 122.6801 | 61.5621 | 61.5935 | 61.4934 | 61.5247
1377.8906 | 123.1384 | -61.3998 | 61.6653 | 0.007391 | -0.33814 | -0.31419 | -0.29057 | -0.24299 | -0.27611 | -0.23669 | 61.6012 | 0.212 | 61.5279 | -0.046838 | 0.025345 | 61.4883 | -0.001436 | 61.2803 | 61.4072 | 61.0617 | 61.0857 | 61.1093 | 61.1568 | 61.1237 | 61.1632 | 123.001 | 61.6118 | 122.9277 | 61.353 | 61.4252 | 122.8882 | 61.3984 | 122.6801 | 61.5759 | 61.6026 | 61.5025 | 61.5293
1378.8906 | 123.143 | -61.409 | 61.6882 | 0.002813 | -0.40225 | -0.38744 | -0.35467 | -0.30708 | -0.34479 | -0.30536 | 61.6058 | 0.20742 | 61.537 | -0.055996 | 0.020767 | 61.4883 | -0.001436 | 61.2711 | 61.4118 | 61.0067 | 61.0216 | 61.0543 | 61.1019 | 61.0642 | 61.1036 | 123.0148 | 61.6164 | 122.946 | 61.353 | 61.4298 | 122.8973 | 61.4076 | 122.6801 | 61.585 | 61.6072 | 61.5163 | 61.5385
1379.8906 | 123.1705 | -61.3998 | 61.6516 | 0.002813 | -0.39767 | -0.37371 | -0.35467 | -0.31166 | -0.33563 | -0.30078 | 61.6058 | 0.212 | 61.5324 | -0.055996 | 0.029923 | 61.4929 | 0.003143 | 61.2665 | 61.4027 | 61.0022 | 61.0261 | 61.0452 | 61.0882 | 61.0642 | 61.0991 | 123.0056 | 61.6118 | 122.9323 | 61.3438 | 61.4298 | 122.8928 | 61.403 | 122.6664 | 61.5759 | 61.6026 | 61.5025 | 61.5293
1380.8906 | 123.1842 | -61.377 | 61.6882 | 0.002813 | -0.37477 | -0.35997 | -0.32262 | -0.28877 | -0.31732 | -0.27789 | 61.6149 | 0.20742 | 61.537 | -0.046838 | 0.029923 | 61.4929 | -0.001436 | 61.2619 | 61.3798 | 61.0022 | 61.017 | 61.0543 | 61.0882 | 61.0596 | 61.0991 | 122.9919 | 61.5844 | 122.914 | 61.3301 | 61.4069 | 122.8699 | 61.3755 | 122.6389 | 61.585 | 61.6164 | 61.5071 | 61.5385
1381.8906 | 123.1842 | -61.3907 | 61.6653 | 0.002813 | -0.36562 | -0.34166 | -0.31804 | -0.27504 | -0.30816 | -0.26874 | 61.6058 | 0.212 | 61.537 | -0.046838 | 0.029923 | 61.4792 | -0.001436 | 61.2757 | 61.3935 | 61.0251 | 61.049 | 61.0726 | 61.1157 | 61.0825 | 61.122 | 122.9965 | 61.6027 | 122.9277 | 61.3438 | 61.4206 | 122.8699 | 61.3893 | 122.6664 | 61.5759 | 61.6072 | 61.5071 | 61.5385
1382.8906 | 123.2162 | -61.3907 | 61.6791 | 0.01197 | -0.3702 | -0.35082 | -0.31804 | -0.27046 | -0.30816 | -0.26874 | 61.6104 | 0.212 | 61.5462 | -0.042259 | 0.029923 | 61.4792 | 0.003143 | 61.2711 | 61.4027 | 61.0205 | 61.0399 | 61.0726 | 61.1202 | 61.0825 | 61.122 | 123.001 | 61.6027 | 122.9369 | 61.3484 | 61.4206 | 122.8699 | 61.3938 | 122.6618 | 61.5804 | 61.6072 | 61.5163 | 61.543
1383.8906 | 123.1705 | -61.3815 | 61.6791 | 0.002813 | -0.40683 | -0.38287 | -0.35925 | -0.30708 | -0.34021 | -0.30078 | 61.6012 | 0.22116 | 61.5416 | -0.042259 | 0.029923 | 61.4883 | 0.003143 | 61.2848 | 61.3843 | 60.9747 | 60.9987 | 61.0223 | 61.0744 | 61.0413 | 61.0807 | 122.9827 | 61.6027 | 122.9231 | 61.3393 | 61.4115 | 122.8699 | 61.3847 | 122.6664 | 61.5713 | 61.5981 | 61.5117 | 61.5385
1384.8906 | 123.23 | -61.377 | 61.6837 | 0.002813 | -0.4343 | -0.40118 | -0.38214 | -0.32997 | -0.36768 | -0.32825 | 61.6012 | 0.21658 | 61.5324 | -0.051417 | 0.039079 | 61.4929 | -0.001436 | 61.2894 | 61.3798 | 60.9427 | 60.9758 | 60.9948 | 61.047 | 61.0093 | 61.0487 | 122.9782 | 61.5935 | 122.9094 | 61.3255 | 61.416 | 122.8699 | 61.3755 | 122.6664 | 61.5621 | 61.6026 | 61.4934 | 61.5339
1385.8906 | 123.1888 | -61.3678 | 61.6516 | -0.001765 | -0.48924 | -0.45612 | -0.43708 | -0.38949 | -0.41346 | -0.38777 | 61.6104 | 0.212 | 61.5416 | -0.046838 | 0.029923 | 61.4746 | -0.001436 | 61.2757 | 61.366 | 60.8786 | 60.9117 | 60.9307 | 60.9783 | 60.9543 | 60.98 | 122.9782 | 61.5798 | 122.9094 | 61.321 | 61.3977 | 122.8424 | 61.3664 | 122.6435 | 61.5804 | 61.6118 | 61.5117 | 61.543
1386.8906 | 123.2208 | -61.3998 | 61.6608 | -0.006344 | -0.51672 | -0.47902 | -0.46455 | -0.42153 | -0.45009 | -0.41066 | 61.6149 | 0.21658 | 61.5324 | -0.042259 | 0.039079 | 61.4838 | -0.010593 | 61.2803 | 61.3935 | 60.8831 | 60.9208 | 60.9353 | 60.9783 | 60.9498 | 60.9892 | 123.0148 | 61.6164 | 122.9323 | 61.3576 | 61.4389 | 122.8836 | 61.3892 | 122.6801 | 61.5759 | 61.6255 | 61.4934 | 61.543
1387.8906 | 123.2437 | -61.4044 | 61.6562 | -0.015501 | -0.56708 | -0.52938 | -0.51492 | -0.46273 | -0.49587 | -0.44728 | 61.6104 | 0.212 | 61.537 | -0.042259 | 0.025345 | 61.4792 | -0.001436 | 61.2803 | 61.3889 | 60.8373 | 60.875 | 60.8895 | 60.9417 | 60.9085 | 60.9571 | 123.0148 | 61.6164 | 122.9414 | 61.3622 | 61.4298 | 122.8836 | 61.403 | 122.6847 | 61.585 | 61.6118 | 61.5117 | 61.5385
1388.8906 | 123.3032 | -61.3861 | 61.6058 | -0.001765 | -0.53961 | -0.51107 | -0.48745 | -0.43984 | -0.47298 | -0.44271 | 61.6058 | 0.212 | 61.5416 | -0.055996 | 0.025345 | 61.4838 | -0.010593 | 61.2803 | 61.3843 | 60.8465 | 60.875 | 60.8987 | 60.9463 | 60.9131 | 60.9434 | 122.9919 | 61.5981 | 122.9277 | 61.3301 | 61.4115 | 122.8699 | 61.3755 | 122.6664 | 61.5804 | 61.6164 | 61.5163 | 61.5522
1389.8906 | 123.1796 | -61.3907 | 61.6333 | -0.010922 | -0.53503 | -0.50649 | -0.48287 | -0.44442 | -0.47298 | -0.42897 | 61.6149 | 0.212 | 61.5553 | -0.046838 | 0.020767 | 61.4746 | -0.001436 | 61.2894 | 61.3798 | 60.8557 | 60.8842 | 60.9078 | 60.9463 | 60.9177 | 60.9617 | 123.0056 | 61.6027 | 122.946 | 61.3438 | 61.4115 | 122.8653 | 61.3893 | 122.6801 | 61.5942 | 61.6164 | 61.5346 | 61.5568
1390.8906 | 123.1613 | -61.3907 | 61.6653 | -0.015501 | -0.57624 | -0.55685 | -0.53781 | -0.48562 | -0.51876 | -0.47933 | 61.6195 | 0.212 | 61.5553 | -0.051417 | 0.025345 | 61.47 | -0.006014 | 61.2711 | 61.3752 | 60.8144 | 60.8338 | 60.8529 | 60.9051 | 60.8719 | 60.9114 | 123.0102 | 61.6027 | 122.946 | 61.3393 | 61.416 | 122.8607 | 61.3847 | 122.6618 | 61.5942 | 61.6255 | 61.53 | 61.5614
1391.8906 | 123.175 | -61.3907 | 61.6699 | -0.015501 | -0.61745 | -0.59348 | -0.56528 | -0.52225 | -0.55539 | -0.51138 | 61.6195 | 0.20742 | 61.5553 | -0.046838 | 0.029923 | 61.4746 | -0.006014 | 61.2711 | 61.3752 | 60.7732 | 60.7972 | 60.8254 | 60.8684 | 60.8353 | 60.8793 | 123.0102 | 61.5981 | 122.946 | 61.3438 | 61.4206 | 122.8653 | 61.3847 | 122.6618 | 61.5896 | 61.6255 | 61.5254 | 61.5614
1392.8906 | 123.175 | -61.409 | 61.6653 | -0.024657 | -0.62661 | -0.60264 | -0.56986 | -0.52225 | -0.55539 | -0.52053 | 61.6149 | 0.212 | 61.5508 | -0.055996 | 0.034501 | 61.47 | -0.006014 | 61.2665 | 61.3843 | 60.7824 | 60.8064 | 60.8391 | 60.8868 | 60.8536 | 60.8885 | 123.0239 | 61.621 | 122.9598 | 61.353 | 61.4435 | 122.879 | 61.403 | 122.6755 | 61.5804 | 61.6209 | 61.5163 | 61.5568
1393.8906 | 123.2941 | -61.3586 | 61.6241 | -0.029236 | -0.61745 | -0.59348 | -0.58359 | -0.52682 | -0.55539 | -0.51596 | 61.6195 | 0.212 | 61.5462 | -0.046838 | 0.029923 | 61.47 | -0.001436 | 61.2665 | 61.3294 | 60.7412 | 60.7652 | 60.7751 | 60.8318 | 60.8033 | 60.8427 | 122.9782 | 61.5706 | 122.9048 | 61.3118 | 61.3886 | 122.8287 | 61.3572 | 122.6252 | 61.5896 | 61.6209 | 61.5163 | 61.5476
1394.8906 | 123.1613 | -61.4136 | 61.5738 | -0.024657 | -0.60372 | -0.59348 | -0.56528 | -0.52225 | -0.55539 | -0.5068 | 61.6012 | 0.20742 | 61.537 | -0.055996 | 0.025345 | 61.4746 | -0.006014 | 61.2711 | 61.3889 | 60.8099 | 60.8201 | 60.8483 | 60.8913 | 60.8582 | 60.9068 | 123.0148 | 61.621 | 122.9506 | 61.3576 | 61.4389 | 122.8882 | 61.4076 | 122.6847 | 61.5759 | 61.6072 | 61.5117 | 61.543
1395.8906 | 123.2162 | -61.3815 | 61.6058 | -0.033814 | -0.69987 | -0.68505 | -0.65227 | -0.60007 | -0.64696 | -0.59836 | 61.6149 | 0.22574 | 61.5416 | -0.051417 | 0.025345 | 61.4746 | -0.006014 | 61.2574 | 61.3477 | 60.6817 | 60.6965 | 60.7293 | 60.7815 | 60.7346 | 60.7832 | 122.9965 | 61.6073 | 122.9231 | 61.3301 | 61.4069 | 122.8561 | 61.3755 | 122.6389 | 61.5896 | 61.6209 | 61.5163 | 61.5476
1396.8906 | 123.2666 | -61.3586 | 61.6058 | -0.042971 | -0.71819 | -0.69879 | -0.67516 | -0.62296 | -0.66069 | -0.60752 | 61.6287 | 0.21658 | 61.5553 | -0.051417 | 0.025345 | 61.4609 | -0.001436 | 61.2574 | 61.3157 | 60.6405 | 60.6599 | 60.6835 | 60.7357 | 60.6979 | 60.7511 | 122.9873 | 61.5752 | 122.914 | 61.3072 | 61.384 | 122.8195 | 61.3572 | 122.616 | 61.6033 | 61.6301 | 61.53 | 61.5568
1397.8906 | 123.2666 | -61.3815 | 61.6058 | -0.038393 | -0.71361 | -0.71253 | -0.67516 | -0.62296 | -0.65612 | -0.61668 | 61.6104 | 0.20742 | 61.537 | -0.055996 | 0.025345 | 61.4792 | -0.006014 | 61.2711 | 61.3431 | 60.6679 | 60.669 | 60.7064 | 60.7586 | 60.7254 | 60.7649 | 122.9919 | 61.589 | 122.9186 | 61.3255 | 61.4069 | 122.8607 | 61.3755 | 122.6526 | 61.585 | 61.6164 | 61.5117 | 61.543
1398.8906 | 123.1522 | -61.3907 | 61.6699 | -0.052128 | -0.71361 | -0.69421 | -0.66601 | -0.61381 | -0.64238 | -0.60752 | 61.6195 | 0.21658 | 61.5553 | -0.051417 | 0.029923 | 61.4746 | 0.003143 | 61.2711 | 61.3386 | 60.6771 | 60.6965 | 60.7247 | 60.7769 | 60.7483 | 60.7832 | 123.0102 | 61.6073 | 122.946 | 61.3393 | 61.4206 | 122.8653 | 61.3938 | 122.6618 | 61.5896 | 61.6164 | 61.5254 | 61.5522
1399.8906 | 123.2849 | -61.377 | 61.5967 | -0.061284 | -0.7594 | -0.73084 | -0.70263 | -0.65958 | -0.69274 | -0.64872 | 61.6195 | 0.21658 | 61.5416 | -0.042259 | 0.029923 | 61.4838 | -0.006014 | 61.2665 | 61.3157 | 60.6176 | 60.6461 | 60.6743 | 60.7174 | 60.6842 | 60.7282 | 122.9965 | 61.5935 | 122.9186 | 61.3347 | 61.4069 | 122.8607 | 61.3709 | 122.6435 | 61.5896 | 61.6255 | 61.5117 | 61.5476
1400.8906 | 123.3215 | -61.3724 | 61.6058 | -0.056706 | -0.72734 | -0.70337 | -0.6889 | -0.64127 | -0.66985 | -0.62583 | 61.6332 | 0.22116 | 61.5599 | -0.042259 | 0.025345 | 61.4654 | -0.001436 | 61.2528 | 61.3157 | 60.645 | 60.669 | 60.6835 | 60.7311 | 60.7025 | 60.7465 | 123.0056 | 61.5935 | 122.9323 | 61.3301 | 61.3977 | 122.8378 | 61.3709 | 122.6252 | 61.6079 | 61.6347 | 61.5346 | 61.5614
1401.8906 | 123.262 | -61.3586 | 61.6287 | -0.070441 | -0.76397 | -0.74458 | -0.72095 | -0.67332 | -0.69274 | -0.66704 | 61.6332 | 0.21658 | 61.5645 | -0.046838 | 0.020767 | 61.4654 | -0.001436 | 61.2436 | 61.2882 | 60.5947 | 60.6141 | 60.6377 | 60.6853 | 60.6659 | 60.6916 | 122.9919 | 61.5752 | 122.9231 | 61.3118 | 61.3794 | 122.8241 | 61.3572 | 122.6023 | 61.6125 | 61.6347 | 61.5437 | 61.5659
1402.8906 | 123.2712 | -61.3815 | 61.6287 | -0.070441 | -0.77313 | -0.75373 | -0.73011 | -0.67332 | -0.70648 | -0.66246 | 61.6149 | 0.21658 | 61.5462 | -0.046838 | 0.025345 | 61.4746 | -0.010593 | 61.2482 | 61.3111 | 60.6084 | 60.6278 | 60.6514 | 60.7082 | 60.6751 | 60.7191 | 122.9965 | 61.5981 | 122.9277 | 61.3347 | 61.4069 | 122.8561 | 61.3709 | 122.6297 | 61.5896 | 61.6255 | 61.5208 | 61.5568
1403.8906 | 123.2849 | -61.3449 | 61.6196 | -0.079598 | -0.78229 | -0.76289 | -0.73926 | -0.68248 | -0.71106 | -0.67161 | 61.6287 | 0.21658 | 61.5553 | -0.042259 | 0.029923 | 61.4654 | 0.003143 | 61.2436 | 61.2653 | 60.5626 | 60.582 | 60.6056 | 60.6624 | 60.6339 | 60.6733 | 122.9736 | 61.5615 | 122.9003 | 61.3027 | 61.3748 | 122.8104 | 61.3481 | 122.5885 | 61.5987 | 61.6255 | 61.5254 | 61.5522
1404.8906 | 123.262 | -61.3724 | 61.615 | -0.084176 | -0.8006 | -0.77663 | -0.75758 | -0.70079 | -0.73853 | -0.68993 | 61.6195 | 0.21658 | 61.5462 | -0.051417 | 0.029923 | 61.47 | -0.006014 | 61.2482 | 61.2882 | 60.5718 | 60.5957 | 60.6148 | 60.6716 | 60.6338 | 60.6824 | 122.9919 | 61.589 | 122.9186 | 61.321 | 61.4023 | 122.8424 | 61.3664 | 122.6206 | 61.5896 | 61.6255 | 61.5163 | 61.5522
1405.8906 | 123.262 | -61.3724 | 61.5967 | -0.084176 | -0.84639 | -0.82241 | -0.7942 | -0.74657 | -0.77058 | -0.73571 | 61.6195 | 0.21658 | 61.5553 | -0.046838 | 0.020767 | 61.4654 | -0.001436 | 61.2391 | 61.2882 | 60.526 | 60.55 | 60.5782 | 60.6258 | 60.6018 | 60.6367 | 122.9919 | 61.589 | 122.9277 | 61.3255 | 61.3931 | 122.8378 | 61.3709 | 122.6114 | 61.5987 | 61.6209 | 61.5346 | 61.5568
1406.8906 | 123.2391 | -61.3815 | 61.615 | -0.10249 | -0.89218 | -0.8682 | -0.83999 | -0.78319 | -0.82552 | -0.78149 | 61.6195 | 0.21658 | 61.5508 | -0.046838 | 0.025345 | 61.4746 | -0.010593 | 61.2482 | 61.279 | 60.4894 | 60.5133 | 60.5415 | 60.5983 | 60.556 | 60.6 | 123.001 | 61.5981 | 122.9323 | 61.3347 | 61.4069 | 122.8561 | 61.3709 | 122.6297 | 61.5942 | 61.6301 | 61.5254 | 61.5614
1407.8906 | 123.2895 | -61.377 | 61.5921 | -0.1208 | -0.93797 | -0.91856 | -0.89493 | -0.8427 | -0.88504 | -0.83185 | 61.6287 | 0.212 | 61.5553 | -0.055996 | 0.025345 | 61.4609 | -0.010593 | 61.2391 | 61.2561 | 60.439 | 60.4584 | 60.482 | 60.5343 | 60.4919 | 60.5451 | 123.0056 | 61.589 | 122.9323 | 61.321 | 61.4023 | 122.8378 | 61.3664 | 122.616 | 61.6033 | 61.6393 | 61.53 | 61.5659
1408.8906 | 123.2986 | -61.3815 | 61.6196 | -0.11165 | -0.91965 | -0.89567 | -0.86288 | -0.81524 | -0.84841 | -0.80896 | 61.6332 | 0.21658 | 61.5599 | -0.042259 | 0.025345 | 61.4654 | -0.006014 | 61.2345 | 61.2699 | 60.4619 | 60.4859 | 60.5186 | 60.5663 | 60.5331 | 60.5726 | 123.0148 | 61.5981 | 122.9415 | 61.3393 | 61.4069 | 122.847 | 61.3755 | 122.616 | 61.6079 | 61.6393 | 61.5346 | 61.5659
1409.8906 | 123.2117 | -61.3632 | 61.6425 | -0.11165 | -0.89676 | -0.87278 | -0.84457 | -0.79235 | -0.8301 | -0.78607 | 61.6241 | 0.212 | 61.5691 | -0.046838 | 0.020767 | 61.4609 | -0.001436 | 61.2391 | 61.2516 | 60.4665 | 60.4904 | 60.5187 | 60.5709 | 60.5331 | 60.5772 | 122.9873 | 61.5752 | 122.9323 | 61.3164 | 61.384 | 122.8241 | 61.3618 | 122.6023 | 61.6033 | 61.6255 | 61.5483 | 61.5705
1410.8906 | 123.2346 | -61.3449 | 61.6287 | -0.12996 | -0.92423 | -0.90483 | -0.86746 | -0.82439 | -0.85299 | -0.80896 | 61.6287 | 0.20742 | 61.5553 | -0.051417 | 0.025345 | 61.4654 | -0.006014 | 61.2391 | 61.215 | 60.4207 | 60.4401 | 60.4774 | 60.5205 | 60.4919 | 60.5359 | 122.9736 | 61.5523 | 122.9003 | 61.2935 | 61.3703 | 122.8104 | 61.3389 | 122.584 | 61.6033 | 61.6347 | 61.53 | 61.5614
1411.8906 | 123.2391 | -61.3861 | 61.6196 | -0.1208 | -0.94255 | -0.91398 | -0.88577 | -0.83355 | -0.8713 | -0.82727 | 61.6287 | 0.21658 | 61.5599 | -0.051417 | 0.025345 | 61.4609 | -0.001436 | 61.2391 | 61.2653 | 60.4436 | 60.4721 | 60.5003 | 60.5526 | 60.5148 | 60.5588 | 123.0148 | 61.6027 | 122.946 | 61.3347 | 61.4115 | 122.847 | 61.3847 | 122.6252 | 61.6033 | 61.6301 | 61.5346 | 61.5614
1412.8906 | 123.2529 | -61.3678 | 61.6104 | -0.13912 | -0.96086 | -0.94146 | -0.91324 | -0.85644 | -0.89419 | -0.85474 | 61.6332 | 0.21658 | 61.5645 | -0.051417 | 0.020767 | 61.4563 | -0.006014 | 61.2436 | 61.2287 | 60.4069 | 60.4263 | 60.4546 | 60.5114 | 60.4736 | 60.5131 | 123.001 | 61.5844 | 122.9323 | 61.3164 | 61.3886 | 122.8241 | 61.3618 | 122.6114 | 61.6125 | 61.6393 | 61.5437 | 61.5705
1413.8906 | 123.262 | -61.3358 | 61.6379 | -0.15285 | -1.0341 | -1.0147 | -0.97734 | -0.93426 | -0.96745 | -0.92341 | 61.6332 | 0.21658 | 61.5599 | -0.042259 | 0.025345 | 61.4517 | -0.006014 | 61.2436 | 61.1829 | 60.3016 | 60.321 | 60.3584 | 60.4015 | 60.3683 | 60.4123 | 122.969 | 61.5523 | 122.8957 | 61.2935 | 61.3611 | 122.7875 | 61.3297 | 122.5794 | 61.6079 | 61.6393 | 61.5346 | 61.5659
1414.8906 | 123.2895 | -61.3541 | 61.6379 | -0.16659 | -1.0433 | -1.0239 | -0.99566 | -0.93884 | -0.9766 | -0.93715 | 61.6516 | 0.21658 | 61.5828 | -0.046838 | 0.020767 | 61.4563 | -0.006014 | 61.2207 | 61.1875 | 60.3108 | 60.3302 | 60.3584 | 60.4152 | 60.3775 | 60.4169 | 123.0056 | 61.5706 | 122.9369 | 61.3072 | 61.3748 | 122.8104 | 61.3481 | 122.5748 | 61.6308 | 61.6576 | 61.562 | 61.5888
1415.8906 | 123.2208 | -61.3678 | 61.6333 | -0.16659 | -1.0662 | -1.0376 | -1.014 | -0.96631 | -0.99492 | -0.96004 | 61.6287 | 0.21658 | 61.5599 | -0.046838 | 0.020767 | 61.4563 | -0.001436 | 61.2391 | 61.2012 | 60.3016 | 60.3302 | 60.3538 | 60.4015 | 60.3729 | 60.4078 | 122.9965 | 61.5844 | 122.9277 | 61.321 | 61.3886 | 122.8241 | 61.3664 | 122.6068 | 61.6079 | 61.6301 | 61.5392 | 61.5614
1416.8906 | 123.2712 | -61.3541 | 61.6379 | -0.17574 | -1.0524 | -1.033 | -1.0094 | -0.95715 | -0.99034 | -0.95088 | 61.6287 | 0.22116 | 61.5599 | -0.051417 | 0.029923 | 61.4609 | 0.007721 | 61.2436 | 61.1783 | 60.3016 | 60.321 | 60.3447 | 60.3969 | 60.3637 | 60.4032 | 122.9827 | 61.5752 | 122.914 | 61.3026 | 61.384 | 122.8149 | 61.3618 | 122.5977 | 61.5987 | 61.6209 | 61.53 | 61.5522
1417.8906 | 123.2529 | -61.3861 | 61.6013 | -0.1849 | -1.0799 | -1.0605 | -1.0369 | -0.98462 | -1.0224 | -0.9692 | 61.6241 | 0.22116 | 61.5553 | -0.042259 | 0.025345 | 61.47 | -0.006014 | 61.2482 | 61.2012 | 60.3062 | 60.3256 | 60.3492 | 60.4015 | 60.3637 | 60.4169 | 123.0102 | 61.6073 | 122.9414 | 61.3438 | 61.4115 | 122.8561 | 61.3801 | 122.6343 | 61.5987 | 61.6301 | 61.53 | 61.5614
1418.8906 | 123.2254 | -61.3541 | 61.6241 | -0.19406 | -1.0845 | -1.0697 | -1.0414 | -0.99378 | -1.0315 | -0.98293 | 61.6378 | 0.21658 | 61.5645 | -0.03768 | 0.025345 | 61.4563 | -0.006014 | 61.2345 | 61.16 | 60.2696 | 60.2844 | 60.3126 | 60.3603 | 60.3225 | 60.3711 | 122.9919 | 61.5706 | 122.9186 | 61.3164 | 61.3794 | 122.8104 | 61.3481 | 122.5885 | 61.6125 | 61.6438 | 61.5392 | 61.5705
1419.8906 | 123.2346 | -61.3449 | 61.6608 | -0.20321 | -1.0936 | -1.0742 | -1.0414 | -0.99378 | -1.027 | -0.98751 | 61.6378 | 0.21658 | 61.5645 | -0.046838 | 0.020767 | 61.4517 | -0.006014 | 61.2345 | 61.1417 | 60.2513 | 60.2707 | 60.3035 | 60.3511 | 60.3179 | 60.3574 | 122.9827 | 61.5615 | 122.9094 | 61.2981 | 61.3657 | 122.7966 | 61.3389 | 122.5794 | 61.6171 | 61.6438 | 61.5437 | 61.5705
1420.8906 | 123.2849 | -61.3358 | 61.6333 | -0.1849 | -1.0433 | -1.0193 | -0.99566 | -0.948 | -0.98576 | -0.93257 | 61.6195 | 0.22116 | 61.5508 | -0.051417 | 0.025345 | 61.4654 | -0.001436 | 61.2482 | 61.1509 | 60.2925 | 60.3165 | 60.3401 | 60.3878 | 60.35 | 60.4032 | 122.9553 | 61.5569 | 122.8865 | 61.2843 | 61.3611 | 122.8012 | 61.3343 | 122.584 | 61.5942 | 61.6209 | 61.5254 | 61.5522
1421.8906 | 123.2895 | -61.3724 | 61.6241 | -0.20779 | -1.0982 | -1.0697 | -1.0369 | -0.9892 | -1.027 | -0.98293 | 61.6378 | 0.22116 | 61.5645 | -0.046838 | 0.020767 | 61.4609 | -0.006014 | 61.2436 | 61.1646 | 60.2741 | 60.3027 | 60.3355 | 60.3832 | 60.3454 | 60.3894 | 123.0102 | 61.5935 | 122.9369 | 61.3255 | 61.3931 | 122.8332 | 61.3664 | 122.616 | 61.6171 | 61.6438 | 61.5437 | 61.5705
1422.8906 | 123.23 | -61.3541 | 61.647 | -0.22153 | -1.0936 | -1.0605 | -1.0369 | -0.98462 | -1.0224 | -0.97377 | 61.6332 | 0.22574 | 61.5553 | -0.046838 | 0.020767 | 61.4563 | 0.003143 | 61.2619 | 61.1325 | 60.2604 | 60.2936 | 60.3172 | 60.3694 | 60.3317 | 60.3803 | 122.9873 | 61.5798 | 122.9094 | 61.3072 | 61.3748 | 122.8104 | 61.3572 | 122.616 | 61.6125 | 61.6301 | 61.5346 | 61.5522
1423.8906 | 123.2941 | -61.3358 | 61.6562 | -0.23069 | -1.1394 | -1.1109 | -1.0918 | -1.035 | -1.0727 | -1.0333 | 61.6287 | 0.21658 | 61.5691 | -0.055996 | 0.029923 | 61.4609 | -0.006014 | 61.2528 | 61.1051 | 60.1963 | 60.2249 | 60.2439 | 60.3008 | 60.263 | 60.3025 | 122.9644 | 61.5523 | 122.9048 | 61.2798 | 61.3657 | 122.7966 | 61.3297 | 122.5885 | 61.5987 | 61.6347 | 61.5392 | 61.5751
1424.8906 | 123.2986 | -61.3586 | 61.6562 | -0.23984 | -1.1257 | -1.0971 | -1.0735 | -1.0167 | -1.059 | -1.0058 | 61.6241 | 0.22116 | 61.5599 | -0.051417 | 0.029923 | 61.4563 | -0.001436 | 61.2619 | 61.1188 | 60.2329 | 60.2615 | 60.2852 | 60.342 | 60.2996 | 60.3528 | 122.9827 | 61.5798 | 122.9186 | 61.3072 | 61.3886 | 122.8149 | 61.3572 | 122.6206 | 61.5942 | 61.6255 | 61.53 | 61.5614
1425.8906 | 123.2849 | -61.3449 | 61.6196 | -0.24442 | -1.144 | -1.1154 | -1.0918 | -1.035 | -1.0773 | -1.0287 | 61.6241 | 0.22116 | 61.5645 | -0.051417 | 0.025345 | 61.4654 | -0.006014 | 61.2528 | 61.1005 | 60.2009 | 60.2295 | 60.2531 | 60.3099 | 60.2676 | 60.3162 | 122.969 | 61.5661 | 122.9094 | 61.2935 | 61.3703 | 122.8104 | 61.3389 | 122.5977 | 61.5987 | 61.6301 | 61.5392 | 61.5705
1426.8906 | 123.3124 | -61.3266 | 61.6516 | -0.25816 | -1.1532 | -1.1383 | -1.101 | -1.0533 | -1.0956 | -1.047 | 61.6241 | 0.22116 | 61.5599 | -0.051417 | 0.025345 | 61.4609 | -0.001436 | 61.2574 | 61.0684 | 60.1734 | 60.1883 | 60.2256 | 60.2733 | 60.231 | 60.2796 | 122.9507 | 61.5478 | 122.8865 | 61.2752 | 61.3519 | 122.7875 | 61.3252 | 122.584 | 61.5987 | 61.6255 | 61.5346 | 61.5614
1427.8906 | 123.23 | -61.2946 | 61.6791 | -0.27647 | -1.1852 | -1.1658 | -1.133 | -1.0762 | -1.1185 | -1.0745 | 61.6378 | 0.22116 | 61.5599 | -0.046838 | 0.029923 | 61.4517 | -0.001436 | 61.2482 | 61.0181 | 60.1093 | 60.1287 | 60.1615 | 60.2184 | 60.176 | 60.2201 | 122.9324 | 61.5157 | 122.8545 | 61.2477 | 61.3245 | 122.7463 | 61.2931 | 122.5428 | 61.6079 | 61.6393 | 61.53 | 61.5614
1428.8906 | 123.3215 | -61.3037 | 61.7203 | -0.26731 | -1.1623 | -1.1429 | -1.1193 | -1.067 | -1.1002 | -1.0562 | 61.6332 | 0.21658 | 61.5553 | -0.046838 | 0.029923 | 61.4609 | -0.001436 | 61.2574 | 61.0364 | 60.1414 | 60.1608 | 60.1844 | 60.2367 | 60.2035 | 60.2475 | 122.937 | 61.5203 | 122.8591 | 61.2569 | 61.3336 | 122.7646 | 61.3023 | 122.5611 | 61.6033 | 61.6347 | 61.5254 | 61.5568
1429.8906 | 123.3307 | -61.2717 | 61.6928 | -0.27647 | -1.1532 | -1.1338 | -1.1101 | -1.0624 | -1.0956 | -1.0516 | 61.6378 | 0.22116 | 61.5645 | -0.046838 | 0.029923 | 61.4609 | -0.001436 | 61.2528 | 60.9952 | 60.1185 | 60.1379 | 60.1615 | 60.2092 | 60.176 | 60.2201 | 122.9095 | 61.4928 | 122.8362 | 61.2248 | 61.3016 | 122.7325 | 61.2702 | 122.5245 | 61.6079 | 61.6393 | 61.5346 | 61.5659
1430.8906 | 123.2803 | -61.3403 | 61.702 | -0.28105 | -1.1669 | -1.1475 | -1.1284 | -1.067 | -1.1002 | -1.0608 | 61.6424 | 0.21658 | 61.5691 | -0.055996 | 0.034501 | 61.4517 | 0.003143 | 61.2528 | 61.0593 | 60.1734 | 60.1928 | 60.2119 | 60.2733 | 60.2401 | 60.2796 | 122.9827 | 61.5569 | 122.9094 | 61.2843 | 61.3748 | 122.792 | 61.3435 | 122.5931 | 61.6079 | 61.6393 | 61.5346 | 61.5659
1431.8906 | 123.2437 | -61.3312 | 61.6287 | -0.29936 | -1.2035 | -1.1887 | -1.1651 | -1.1128 | -1.1368 | -1.102 | 61.6378 | 0.212 | 61.5599 | -0.042259 | 0.029923 | 61.4563 | 0.007721 | 61.2665 | 61.0318 | 60.1276 | 60.1425 | 60.1661 | 60.2184 | 60.1943 | 60.2292 | 122.969 | 61.5432 | 122.8911 | 61.2889 | 61.3611 | 122.7875 | 61.3389 | 122.5977 | 61.6079 | 61.6301 | 61.53 | 61.5522
1432.8906 | 123.2803 | -61.3403 | 61.6333 | -0.30852 | -1.2356 | -1.2116 | -1.188 | -1.1357 | -1.1826 | -1.134 | 61.6287 | 0.21658 | 61.5645 | -0.046838 | 0.029923 | 61.4609 | 0.003143 | 61.2619 | 61.0318 | 60.1047 | 60.1287 | 60.1524 | 60.2046 | 60.1577 | 60.2063 | 122.969 | 61.5569 | 122.9048 | 61.2935 | 61.3703 | 122.8012 | 61.3435 | 122.6023 | 61.5987 | 61.6255 | 61.5346 | 61.5614
1433.8906 | 123.3307 | -61.3403 | 61.615 | -0.32683 | -1.2676 | -1.2436 | -1.2154 | -1.1677 | -1.2009 | -1.1523 | 61.6287 | 0.22116 | 61.5599 | -0.046838 | 0.025345 | 61.4563 | -0.001436 | 61.2711 | 61.0135 | 60.0727 | 60.0967 | 60.1249 | 60.1726 | 60.1394 | 60.188 | 122.969 | 61.5615 | 122.9003 | 61.2935 | 61.3657 | 122.7966 | 61.3389 | 122.6114 | 61.6033 | 61.6301 | 61.5346 | 61.5614
1434.8906 | 123.1842 | -61.3495 | 61.6837 | -0.34057 | -1.3089 | -1.2803 | -1.2566 | -1.1998 | -1.2376 | -1.1981 | 61.6332 | 0.20742 | 61.5691 | -0.03768 | 0.029923 | 61.4563 | -0.001436 | 61.2665 | 61.0089 | 60.0406 | 60.0692 | 60.0929 | 60.1497 | 60.1119 | 60.1514 | 122.9827 | 61.5569 | 122.9186 | 61.3118 | 61.3794 | 122.8058 | 61.3481 | 122.616 | 61.6033 | 61.6347 | 61.5392 | 61.5705
1435.8906 | 123.2483 | -61.3449 | 61.6791 | -0.3543 | -1.3134 | -1.2894 | -1.2612 | -1.2089 | -1.2422 | -1.1981 | 61.6378 | 0.21658 | 61.5782 | -0.051417 | 0.025345 | 61.4517 | -0.001436 | 61.2619 | 60.9906 | 60.0315 | 60.0555 | 60.0837 | 60.136 | 60.1028 | 60.1468 | 122.9827 | 61.5615 | 122.9231 | 61.2935 | 61.3703 | 122.7966 | 61.3435 | 122.6069 | 61.6125 | 61.6393 | 61.5529 | 61.5797
1436.8906 | 123.1659 | -61.3449 | 61.6837 | -0.34514 | -1.2951 | -1.2665 | -1.2429 | -1.1952 | -1.2238 | -1.1752 | 61.6332 | 0.22116 | 61.5599 | -0.046838 | 0.029923 | 61.4563 | -0.006014 | 61.2528 | 60.9998 | 60.0498 | 60.0784 | 60.102 | 60.1497 | 60.1211 | 60.1697 | 122.9782 | 61.5661 | 122.9048 | 61.2981 | 61.3748 | 122.8012 | 61.3389 | 122.5977 | 61.6033 | 61.6393 | 61.53 | 61.5659
1437.8906 | 123.1384 | -61.3495 | 61.7203 | -0.37261 | -1.3501 | -1.3215 | -1.2887 | -1.241 | -1.2696 | -1.2302 | 61.6287 | 0.21658 | 61.5645 | -0.051417 | 0.020767 | 61.4517 | -0.001436 | 61.2482 | 60.9769 | 59.9994 | 60.028 | 60.0608 | 60.1085 | 60.0799 | 60.1193 | 122.9782 | 61.5661 | 122.914 | 61.2981 | 61.3703 | 122.8012 | 61.3481 | 122.5977 | 61.6079 | 61.6301 | 61.5437 | 61.5659
1438.8906 | 123.1796 | -61.3586 | 61.6928 | -0.39093 | -1.3592 | -1.349 | -1.3162 | -1.2593 | -1.3017 | -1.2576 | 61.6332 | 0.22116 | 61.5599 | -0.051417 | 0.029923 | 61.4654 | -0.001436 | 61.2665 | 60.9677 | 59.9994 | 60.0097 | 60.0425 | 60.0993 | 60.057 | 60.101 | 122.9919 | 61.5798 | 122.9186 | 61.3072 | 61.3886 | 122.8241 | 61.3572 | 122.6252 | 61.6033 | 61.6347 | 61.53 | 61.5614
1439.8906 | 123.1796 | -61.3861 | 61.6882 | -0.39551 | -1.3867 | -1.3535 | -1.339 | -1.2776 | -1.32 | -1.2759 | 61.6378 | 0.21658 | 61.5645 | -0.042259 | 0.025345 | 61.4563 | -0.001436 | 61.2528 | 60.9906 | 59.9994 | 60.0326 | 60.0471 | 60.1085 | 60.0661 | 60.1102 | 123.0239 | 61.6027 | 122.9506 | 61.3438 | 61.4115 | 122.8424 | 61.3847 | 122.6389 | 61.6125 | 61.6393 | 61.5392 | 61.5659
1440.8906 | 123.1522 | -61.3632 | 61.7111 | -0.4184 | -1.4142 | -1.3902 | -1.3665 | -1.3142 | -1.352 | -1.3034 | 61.6332 | 0.22116 | 61.5645 | -0.046838 | 0.034501 | 61.4609 | 0.003143 | 61.2528 | 60.9448 | 59.9491 | 59.9731 | 59.9967 | 60.049 | 60.0112 | 60.0598 | 122.9965 | 61.5844 | 122.9277 | 61.3164 | 61.3977 | 122.8241 | 61.3664 | 122.616 | 61.5987 | 61.6301 | 61.53 | 61.5614
1441.8906 | 123.175 | -61.3586 | 61.6745 | -0.40924 | -1.3959 | -1.3673 | -1.3436 | -1.2959 | -1.3246 | -1.2851 | 61.6378 | 0.22116 | 61.5553 | -0.042259 | 0.020767 | 61.4471 | -0.010593 | 61.2345 | 60.9494 | 59.9628 | 59.9914 | 60.015 | 60.0627 | 60.0341 | 60.0736 | 122.9965 | 61.5798 | 122.914 | 61.3164 | 61.3794 | 122.8058 | 61.3481 | 122.5931 | 61.6171 | 61.6484 | 61.5346 | 61.5659
1442.8906 | 123.1613 | -61.3678 | 61.6974 | -0.40466 | -1.3455 | -1.3261 | -1.3024 | -1.241 | -1.2879 | -1.2393 | 61.6241 | 0.22116 | 61.5553 | -0.046838 | 0.025345 | 61.4654 | 0.007721 | 61.2482 | 60.9631 | 60.0223 | 60.0417 | 60.0654 | 60.1268 | 60.0799 | 60.1285 | 122.9919 | 61.589 | 122.9231 | 61.321 | 61.3931 | 122.8332 | 61.3755 | 122.616 | 61.5987 | 61.6164 | 61.53 | 61.5476
1443.8906 | 123.1934 | -61.3861 | 61.6608 | -0.40009 | -1.3272 | -1.3077 | -1.2749 | -1.2273 | -1.2605 | -1.2164 | 61.6241 | 0.212 | 61.5645 | -0.051417 | 0.025345 | 61.4746 | -0.001436 | 61.2528 | 60.986 | 60.0589 | 60.0784 | 60.1112 | 60.1589 | 60.1256 | 60.1697 | 123.0102 | 61.5981 | 122.9506 | 61.3347 | 61.4115 | 122.8607 | 61.3847 | 122.6389 | 61.5987 | 61.6255 | 61.5392 | 61.5659
1444.8906 | 123.2025 | -61.3861 | 61.6745 | -0.40009 | -1.3455 | -1.3261 | -1.2887 | -1.2456 | -1.2788 | -1.2302 | 61.6241 | 0.21658 | 61.5508 | -0.046838 | 0.025345 | 61.4654 | 0.003143 | 61.2528 | 60.986 | 60.0406 | 60.06 | 60.0974 | 60.1405 | 60.1073 | 60.156 | 123.0102 | 61.6027 | 122.9369 | 61.3393 | 61.4115 | 122.8516 | 61.3893 | 122.6389 | 61.5987 | 61.6209 | 61.5254 | 61.5476
1445.8906 | 123.1842 | -61.377 | 61.6653 | -0.40466 | -1.3272 | -1.3169 | -1.2749 | -1.2364 | -1.265 | -1.2164 | 61.6241 | 0.21658 | 61.5599 | -0.046838 | 0.025345 | 61.4654 | -0.010593 | 61.2528 | 60.9723 | 60.0498 | 60.0601 | 60.102 | 60.1405 | 60.1119 | 60.1605 | 123.001 | 61.5935 | 122.9369 | 61.3301 | 61.4023 | 122.8424 | 61.3664 | 122.6297 | 61.5987 | 61.6347 | 61.5346 | 61.5705
1446.8906 | 123.2162 | -61.3724 | 61.647 | -0.41382 | -1.2997 | -1.2849 | -1.2612 | -1.2089 | -1.2422 | -1.2027 | 61.6195 | 0.21658 | 61.5553 | -0.046838 | 0.034501 | 61.47 | -0.006014 | 61.2528 | 60.9586 | 60.0727 | 60.0875 | 60.1112 | 60.1634 | 60.1302 | 60.1697 | 122.9919 | 61.589 | 122.9277 | 61.3255 | 61.4069 | 122.8424 | 61.3664 | 122.6252 | 61.585 | 61.6255 | 61.5208 | 61.5614
1447.8906 | 123.23 | -61.377 | 61.6699 | -0.41382 | -1.318 | -1.2894 | -1.2566 | -1.2089 | -1.2467 | -1.2027 | 61.6241 | 0.212 | 61.5462 | -0.051417 | 0.029923 | 61.4746 | -0.006014 | 61.2528 | 60.9631 | 60.0589 | 60.0875 | 60.1203 | 60.168 | 60.1302 | 60.1743 | 123.001 | 61.589 | 122.9231 | 61.3255 | 61.4069 | 122.8516 | 61.3709 | 122.6297 | 61.5942 | 61.6301 | 61.5163 | 61.5522
1448.8906 | 123.2071 | -61.3907 | 61.6333 | -0.4184 | -1.3226 | -1.294 | -1.2704 | -1.2227 | -1.2559 | -1.2073 | 61.6195 | 0.21658 | 61.537 | -0.046838 | 0.025345 | 61.4838 | 0.003143 | 61.2574 | 60.9723 | 60.0681 | 60.0967 | 60.1203 | 60.168 | 60.1348 | 60.1834 | 123.0102 | 61.6073 | 122.9277 | 61.3438 | 61.416 | 122.8744 | 61.3938 | 122.6481 | 61.5942 | 61.6164 | 61.5117 | 61.5339
1449.8906 | 123.1979 | -61.377 | 61.6562 | -0.40924 | -1.2951 | -1.2757 | -1.2475 | -1.1998 | -1.233 | -1.1844 | 61.6012 | 0.21658 | 61.5279 | -0.03768 | 0.025345 | 61.4838 | -0.006014 | 61.2711 | 60.9677 | 60.0818 | 60.1013 | 60.1295 | 60.1772 | 60.144 | 60.1926 | 122.9782 | 61.5935 | 122.9048 | 61.3393 | 61.4023 | 122.8607 | 61.3709 | 122.6481 | 61.5759 | 61.6072 | 61.5025 | 61.5339
1450.8906 | 123.2071 | -61.3815 | 61.647 | -0.43213 | -1.318 | -1.2849 | -1.2521 | -1.2089 | -1.2422 | -1.2027 | 61.6104 | 0.22116 | 61.5416 | -0.042259 | 0.025345 | 61.4746 | 0.003143 | 61.2619 | 60.9494 | 60.0635 | 60.0967 | 60.1295 | 60.1726 | 60.1394 | 60.1788 | 122.9919 | 61.6027 | 122.9231 | 61.3393 | 61.4069 | 122.8561 | 61.3847 | 122.6435 | 61.585 | 61.6072 | 61.5163 | 61.5385
1451.8906 | 123.1705 | -61.377 | 61.6196 | -0.42756 | -1.2997 | -1.2665 | -1.2475 | -1.1906 | -1.233 | -1.1798 | 61.6058 | 0.212 | 61.537 | -0.051417 | 0.025345 | 61.4929 | -0.006014 | 61.2665 | 60.9494 | 60.0773 | 60.1104 | 60.1295 | 60.1863 | 60.144 | 60.1972 | 122.9827 | 61.589 | 122.914 | 61.3255 | 61.4023 | 122.8699 | 61.3709 | 122.6435 | 61.5804 | 61.6118 | 61.5117 | 61.543
1452.8906 | 123.2346 | -61.3953 | 61.6379 | -0.43671 | -1.318 | -1.294 | -1.2704 | -1.2181 | -1.2513 | -1.2027 | 61.6104 | 0.21658 | 61.537 | -0.046838 | 0.025345 | 61.4929 | 0.003143 | 61.2757 | 60.9586 | 60.0773 | 60.1013 | 60.1249 | 60.1772 | 60.144 | 60.1926 | 123.0056 | 61.6118 | 122.9323 | 61.3484 | 61.4206 | 122.8882 | 61.3984 | 122.6709 | 61.585 | 61.6072 | 61.5117 | 61.5339
1453.8906 | 123.1705 | -61.4044 | 61.6333 | -0.44129 | -1.3089 | -1.2849 | -1.2612 | -1.1998 | -1.2422 | -1.1981 | 61.6058 | 0.22116 | 61.537 | -0.042259 | 0.016188 | 61.4792 | -0.010593 | 61.2757 | 60.9631 | 60.0956 | 60.1196 | 60.1432 | 60.2046 | 60.1623 | 60.2063 | 123.0102 | 61.6256 | 122.9414 | 61.3622 | 61.4206 | 122.8836 | 61.3938 | 122.6801 | 61.5896 | 61.6164 | 61.5208 | 61.5476
1454.8906 | 123.23 | -61.3815 | 61.6516 | -0.45045 | -1.3409 | -1.3169 | -1.2841 | -1.2318 | -1.2696 | -1.2302 | 61.6012 | 0.22116 | 61.537 | -0.042259 | 0.025345 | 61.4838 | -0.006014 | 61.2803 | 60.9311 | 60.0406 | 60.0646 | 60.0974 | 60.1497 | 60.1119 | 60.1514 | 122.9827 | 61.6027 | 122.9186 | 61.3393 | 61.4069 | 122.8653 | 61.3755 | 122.6618 | 61.5759 | 61.6072 | 61.5117 | 61.543
1455.8906 | 123.1338 | -61.4182 | 61.647 | -0.45045 | -1.2951 | -1.2803 | -1.2521 | -1.1952 | -1.233 | -1.1889 | 61.6012 | 0.22116 | 61.537 | -0.046838 | 0.029923 | 61.4883 | 0.003143 | 61.2803 | 60.9677 | 60.123 | 60.1379 | 60.1661 | 60.2229 | 60.1852 | 60.2292 | 123.0194 | 61.6393 | 122.9552 | 61.3713 | 61.4481 | 122.9065 | 61.4213 | 122.6984 | 61.5713 | 61.5981 | 61.5071 | 61.5339
1456.8906 | 123.1201 | -61.3998 | 61.6196 | -0.45045 | -1.2722 | -1.2482 | -1.2292 | -1.1677 | -1.2055 | -1.1615 | 61.5966 | 0.22116 | 61.5233 | -0.046838 | 0.034501 | 61.5021 | -0.006014 | 61.2848 | 60.9494 | 60.1276 | 60.1516 | 60.1707 | 60.2321 | 60.1943 | 60.2384 | 122.9965 | 61.621 | 122.9231 | 61.353 | 61.4343 | 122.9019 | 61.3938 | 122.6847 | 61.5621 | 61.6026 | 61.4888 | 61.5293
1457.8906 | 123.1613 | -61.4227 | 61.6379 | -0.45045 | -1.2722 | -1.2528 | -1.2246 | -1.1677 | -1.2101 | -1.1661 | 61.592 | 0.21658 | 61.5233 | -0.046838 | 0.020767 | 61.4929 | -0.006014 | 61.2848 | 60.9723 | 60.1505 | 60.1699 | 60.1981 | 60.255 | 60.2126 | 60.2567 | 123.0148 | 61.6393 | 122.946 | 61.3759 | 61.4435 | 122.9156 | 61.4167 | 122.7076 | 61.5713 | 61.5981 | 61.5025 | 61.5293
1458.8906 | 123.1338 | -61.4273 | 61.6013 | -0.45503 | -1.2631 | -1.2528 | -1.2246 | -1.1677 | -1.2009 | -1.1661 | 61.5875 | 0.21658 | 61.5096 | -0.051417 | 0.025345 | 61.4975 | -0.006014 | 61.2894 | 60.9723 | 60.1642 | 60.1745 | 60.2027 | 60.2596 | 60.2264 | 60.2612 | 123.0148 | 61.6439 | 122.9369 | 61.3759 | 61.4527 | 122.9248 | 61.4213 | 122.7167 | 61.5621 | 61.5935 | 61.4842 | 61.5156
1459.8906 | 123.1659 | -61.4273 | 61.6196 | -0.45503 | -1.2402 | -1.2253 | -1.1925 | -1.1403 | -1.1735 | -1.1294 | 61.5783 | 0.22574 | 61.5141 | -0.046838 | 0.025345 | 61.5112 | -0.006014 | 61.2848 | 60.9723 | 60.1871 | 60.202 | 60.2348 | 60.287 | 60.2538 | 60.2979 | 123.0056 | 61.653 | 122.9414 | 61.3805 | 61.4527 | 122.9385 | 61.4213 | 122.7121 | 61.553 | 61.5843 | 61.4888 | 61.5202
1460.8906 | 123.1842 | -61.4456 | 61.6104 | -0.45503 | -1.2493 | -1.2299 | -1.1925 | -1.154 | -1.1781 | -1.1432 | 61.5783 | 0.22574 | 61.5096 | -0.046838 | 0.020767 | 61.5158 | -0.001436 | 61.2894 | 60.9906 | 60.1963 | 60.2157 | 60.2531 | 60.2916 | 60.2676 | 60.3025 | 123.0239 | 61.6714 | 122.9552 | 61.3988 | 61.4664 | 122.9614 | 61.4442 | 122.735 | 61.5575 | 61.5797 | 61.4888 | 61.511
1461.8906 | 123.1705 | -61.4456 | 61.5784 | -0.45503 | -1.2448 | -1.2299 | -1.1925 | -1.1448 | -1.1781 | -1.134 | 61.5783 | 0.22116 | 61.5187 | -0.051417 | 0.025345 | 61.5066 | -0.006014 | 61.2986 | 60.9906 | 60.2009 | 60.2157 | 60.2531 | 60.3008 | 60.2676 | 60.3116 | 123.0239 | 61.6668 | 122.9643 | 61.3942 | 61.471 | 122.9523 | 61.4396 | 122.7442 | 61.553 | 61.5843 | 61.4934 | 61.5247
1462.8906 | 123.1384 | -61.4594 | 61.5555 | -0.45045 | -1.2173 | -1.1933 | -1.1605 | -1.1174 | -1.1552 | -1.102 | 61.56 | 0.212 | 61.4958 | -0.046838 | 0.025345 | 61.5295 | 0.003143 | 61.3077 | 61.0089 | 60.2421 | 60.2661 | 60.2989 | 60.342 | 60.3042 | 60.3574 | 123.0193 | 61.6714 | 122.9552 | 61.4125 | 61.4847 | 122.9889 | 61.4625 | 122.7671 | 61.5346 | 61.5568 | 61.4705 | 61.4927
1463.8906 | 123.1888 | -61.4227 | 61.6104 | -0.45045 | -1.2081 | -1.1887 | -1.1605 | -1.1128 | -1.1506 | -1.102 | 61.5646 | 0.21658 | 61.4958 | -0.046838 | 0.029923 | 61.5204 | -0.001436 | 61.294 | 60.9723 | 60.2146 | 60.234 | 60.2622 | 60.3099 | 60.2721 | 60.3208 | 122.9873 | 61.6393 | 122.9186 | 61.3759 | 61.4527 | 122.9431 | 61.4213 | 122.7167 | 61.5346 | 61.566 | 61.4659 | 61.4973
1464.8906 | 123.2391 | -61.4365 | 61.5372 | -0.45503 | -1.2127 | -1.1841 | -1.1605 | -1.1082 | -1.1368 | -1.102 | 61.5554 | 0.23032 | 61.4867 | -0.055996 | 0.020767 | 61.5295 | -0.001436 | 61.3031 | 60.9814 | 60.2238 | 60.2523 | 60.276 | 60.3282 | 60.2996 | 60.3345 | 122.9919 | 61.6668 | 122.9231 | 61.3805 | 61.4572 | 122.966 | 61.435 | 122.7396 | 61.5346 | 61.5568 | 61.4659 | 61.4881
1465.8906 | 123.2391 | -61.4456 | 61.5326 | -0.45503 | -1.1944 | -1.175 | -1.1513 | -1.0945 | -1.1323 | -1.0882 | 61.5508 | 0.21658 | 61.4821 | -0.042259 | 0.025345 | 61.5295 | -0.001436 | 61.3077 | 60.9906 | 60.2512 | 60.2707 | 60.2943 | 60.3511 | 60.3133 | 60.3574 | 122.9965 | 61.6622 | 122.9277 | 61.4034 | 61.471 | 122.9752 | 61.4442 | 122.7533 | 61.5255 | 61.5523 | 61.4567 | 61.4835
1466.8906 | 123.2849 | -61.4502 | 61.4822 | -0.4596 | -1.1715 | -1.1612 | -1.133 | -1.0808 | -1.1185 | -1.0745 | 61.5508 | 0.21658 | 61.4775 | -0.042259 | 0.025345 | 61.5341 | 0.007721 | 61.3077 | 60.9906 | 60.2787 | 60.289 | 60.3172 | 60.3694 | 60.3317 | 60.3757 | 123.001 | 61.6668 | 122.9277 | 61.4079 | 61.4755 | 122.9843 | 61.4579 | 122.7579 | 61.5255 | 61.5431 | 61.4522 | 61.4698
1467.8906 | 123.2849 | -61.441 | 61.5189 | -0.45503 | -1.1669 | -1.1566 | -1.1193 | -1.0716 | -1.1048 | -1.0608 | 61.5417 | 0.212 | 61.4684 | -0.051417 | 0.025345 | 61.5387 | -0.001436 | 61.326 | 60.986 | 60.2741 | 60.2844 | 60.3218 | 60.3694 | 60.3362 | 60.3803 | 122.9827 | 61.653 | 122.9094 | 61.3896 | 61.4664 | 122.9797 | 61.4396 | 122.7671 | 61.5163 | 61.5431 | 61.443 | 61.4698
1468.8906 | 123.2849 | -61.4273 | 61.5234 | -0.43671 | -1.1303 | -1.1154 | -1.0781 | -1.0304 | -1.059 | -1.015 | 61.5325 | 0.21658 | 61.4821 | -0.046838 | 0.025345 | 61.5433 | -0.006014 | 61.3215 | 60.9906 | 60.297 | 60.3119 | 60.3492 | 60.3969 | 60.3683 | 60.4123 | 122.9598 | 61.6439 | 122.9094 | 61.3805 | 61.4527 | 122.9706 | 61.4213 | 122.7488 | 61.5072 | 61.5385 | 61.4567 | 61.4881
1469.8906 | 123.2895 | -61.4456 | 61.5372 | -0.45045 | -1.1578 | -1.1338 | -1.1101 | -1.0579 | -1.0865 | -1.0379 | 61.5508 | 0.21658 | 61.4775 | -0.046838 | 0.020767 | 61.5341 | -0.006014 | 61.3169 | 60.9952 | 60.2879 | 60.3119 | 60.3355 | 60.3878 | 60.3591 | 60.4078 | 122.9965 | 61.6622 | 122.9231 | 61.3988 | 61.4664 | 122.9797 | 61.4396 | 122.7625 | 61.5301 | 61.5568 | 61.4567 | 61.4835
1470.8906 | 123.2712 | -61.4456 | 61.5097 | -0.44587 | -1.1623 | -1.1292 | -1.1147 | -1.0533 | -1.0956 | -1.047 | 61.5371 | 0.22116 | 61.4729 | -0.046838 | 0.020767 | 61.5387 | 0.003143 | 61.3398 | 60.9997 | 60.2833 | 60.3164 | 60.3309 | 60.3923 | 60.35 | 60.3986 | 122.9827 | 61.6668 | 122.9186 | 61.3988 | 61.4664 | 122.9843 | 61.4488 | 122.7854 | 61.5163 | 61.534 | 61.4522 | 61.4698
1471.8906 | 123.262 | -61.4594 | 61.496 | -0.4596 | -1.1532 | -1.1338 | -1.101 | -1.0441 | -1.0819 | -1.0379 | 61.5417 | 0.21658 | 61.4684 | -0.042259 | 0.029923 | 61.5524 | -0.006014 | 61.3306 | 60.9997 | 60.3062 | 60.3256 | 60.3584 | 60.4152 | 60.3774 | 60.4215 | 123.001 | 61.6759 | 122.9277 | 61.4171 | 61.4893 | 123.0118 | 61.4533 | 122.79 | 61.5118 | 61.5477 | 61.4384 | 61.4744
1472.8906 | 123.2712 | -61.4502 | 61.496 | -0.4596 | -1.1349 | -1.1154 | -1.0872 | -1.035 | -1.0682 | -1.0287 | 61.5325 | 0.21658 | 61.4638 | -0.051417 | 0.025345 | 61.5524 | -0.006014 | 61.3306 | 60.9906 | 60.3153 | 60.3348 | 60.363 | 60.4152 | 60.382 | 60.4215 | 122.9827 | 61.6668 | 122.914 | 61.3988 | 61.4755 | 123.0026 | 61.4442 | 122.7808 | 61.5072 | 61.5385 | 61.4384 | 61.4698
1473.8906 | 123.2437 | -61.4594 | 61.5005 | -0.47792 | -1.1532 | -1.1383 | -1.1147 | -1.0533 | -1.0865 | -1.0379 | 61.5234 | 0.22116 | 61.4546 | -0.051417 | 0.020767 | 61.557 | -0.006014 | 61.3398 | 60.9814 | 60.3062 | 60.321 | 60.3447 | 60.4061 | 60.3729 | 60.4215 | 122.9827 | 61.6805 | 122.914 | 61.4079 | 61.4801 | 123.0164 | 61.4533 | 122.7991 | 61.5026 | 61.5294 | 61.4339 | 61.4606
1474.8906 | 123.2529 | -61.4594 | 61.5463 | -0.45045 | -1.0936 | -1.0697 | -1.046 | -0.97546 | -1.027 | -0.97835 | 61.5142 | 0.22116 | 61.4455 | -0.046838 | 0.029923 | 61.5662 | -0.001436 | 61.3443 | 61.0089 | 60.3657 | 60.3897 | 60.4133 | 60.4839 | 60.4324 | 60.481 | 122.9736 | 61.6805 | 122.9048 | 61.4125 | 61.4893 | 123.0255 | 61.4579 | 122.8037 | 61.4843 | 61.5156 | 61.4155 | 61.4469
1475.8906 | 123.175 | -61.4777 | 61.5417 | -0.47792 | -1.1761 | -1.1383 | -1.1101 | -1.0716 | -1.0956 | -1.047 | 61.5096 | 0.23032 | 61.4363 | -0.042259 | 0.034501 | 61.5707 | -0.001436 | 61.3443 | 60.9997 | 60.3016 | 60.3393 | 60.3675 | 60.4061 | 60.382 | 60.4306 | 122.9873 | 61.708 | 122.914 | 61.4354 | 61.5122 | 123.0484 | 61.4762 | 122.822 | 61.4751 | 61.5111 | 61.4018 | 61.4377
1476.8906 | 123.2254 | -61.5005 | 61.5143 | -0.47334 | -1.1211 | -1.0925 | -1.0826 | -1.0258 | -1.0544 | -1.0104 | 61.505 | 0.21658 | 61.4317 | -0.046838 | 0.029923 | 61.5799 | 0.003143 | 61.3627 | 61.0272 | 60.3794 | 60.408 | 60.4179 | 60.4747 | 60.4461 | 60.4901 | 123.0056 | 61.7171 | 122.9323 | 61.4537 | 61.5305 | 123.0804 | 61.5037 | 122.8632 | 61.4751 | 61.5019 | 61.4018 | 61.4286
1477.8906 | 123.2391 | -61.4868 | 61.5051 | -0.50081 | -1.1806 | -1.1704 | -1.1422 | -1.0853 | -1.1231 | -1.0745 | 61.4913 | 0.22116 | 61.4317 | -0.042259 | 0.025345 | 61.5845 | -0.006014 | 61.3672 | 60.986 | 60.3062 | 60.3164 | 60.3446 | 60.4015 | 60.3637 | 60.4123 | 122.9781 | 61.708 | 122.9185 | 61.4446 | 61.5122 | 123.0713 | 61.4808 | 122.8541 | 61.466 | 61.4973 | 61.4064 | 61.4377
1478.8906 | 123.2162 | -61.496 | 61.5189 | -0.51455 | -1.2356 | -1.207 | -1.1742 | -1.1265 | -1.1597 | -1.1203 | 61.5005 | 0.22116 | 61.4317 | -0.055996 | 0.020767 | 61.5799 | 0.003143 | 61.3764 | 60.9814 | 60.2604 | 60.289 | 60.3218 | 60.3694 | 60.3362 | 60.3757 | 122.9964 | 61.7171 | 122.9277 | 61.44 | 61.5167 | 123.0759 | 61.4991 | 122.8724 | 61.4797 | 61.4973 | 61.411 | 61.4286
1479.8906 | 123.1659 | -61.5143 | 61.5097 | -0.50539 | -1.1715 | -1.1566 | -1.1284 | -1.0716 | -1.1048 | -1.0653 | 61.505 | 0.21658 | 61.4226 | -0.046838 | 0.020767 | 61.5891 | -0.006014 | 61.3856 | 61.0089 | 60.3428 | 60.3576 | 60.3858 | 60.4427 | 60.4095 | 60.4489 | 123.0193 | 61.7309 | 122.9369 | 61.4674 | 61.535 | 123.1033 | 61.5083 | 122.8998 | 61.4843 | 61.5111 | 61.4018 | 61.4286
1480.8906 | 123.2574 | -61.4822 | 61.4777 | -0.45503 | -1.0891 | -1.0742 | -1.0414 | -0.98462 | -1.0178 | -0.97835 | 61.4822 | 0.22116 | 61.418 | -0.046838 | 0.025345 | 61.6074 | -0.001436 | 61.3993 | 61.0272 | 60.3932 | 60.408 | 60.4408 | 60.4976 | 60.4644 | 60.5039 | 122.9644 | 61.7034 | 122.9002 | 61.4354 | 61.5076 | 123.0896 | 61.4808 | 122.8815 | 61.4568 | 61.4836 | 61.3926 | 61.4194
1481.8906 | 123.3078 | -61.5005 | 61.4822 | -0.46876 | -1.0845 | -1.0697 | -1.046 | -0.99378 | -1.0178 | -0.98293 | 61.4684 | 0.22574 | 61.4088 | -0.046838 | 0.029923 | 61.6211 | -0.001436 | 61.4084 | 61.0318 | 60.4161 | 60.4309 | 60.4545 | 60.5068 | 60.4827 | 60.5176 | 122.969 | 61.7263 | 122.9094 | 61.4537 | 61.5305 | 123.1216 | 61.4991 | 122.909 | 61.4385 | 61.4699 | 61.3789 | 61.4103
1482.8906 | 123.2483 | -61.5234 | 61.4639 | -0.45503 | -1.0479 | -1.0422 | -1.0094 | -0.95715 | -0.98576 | -0.9463 | 61.4593 | 0.22574 | 61.3951 | -0.046838 | 0.029923 | 61.6303 | -0.001436 | 61.4176 | 61.0684 | 60.4756 | 60.4813 | 60.514 | 60.5663 | 60.5377 | 60.5771 | 122.9827 | 61.7492 | 122.9185 | 61.4766 | 61.5534 | 123.1537 | 61.522 | 122.941 | 61.4293 | 61.4607 | 61.3652 | 61.3965
1483.8906 | 123.3032 | -61.5234 | 61.4639 | -0.45503 | -1.0433 | -1.0239 | -1.0002 | -0.948 | -0.9766 | -0.93257 | 61.4547 | 0.22574 | 61.3814 | -0.042259 | 0.025345 | 61.6348 | -0.001436 | 61.4176 | 61.0684 | 60.4802 | 60.4996 | 60.5232 | 60.5754 | 60.5468 | 60.5909 | 122.9781 | 61.7492 | 122.9048 | 61.4812 | 61.5488 | 123.1583 | 61.522 | 122.941 | 61.4293 | 61.4561 | 61.356 | 61.3828
1484.8906 | 123.2117 | -61.5555 | 61.4502 | -0.44129 | -1.0158 | -1.001 | -0.96819 | -0.91595 | -0.93998 | -0.90052 | 61.4501 | 0.21658 | 61.3814 | -0.051417 | 0.020767 | 61.644 | -0.001436 | 61.4313 | 61.1142 | 60.5397 | 60.5545 | 60.5873 | 60.6395 | 60.6155 | 60.655 | 123.0056 | 61.7721 | 122.9368 | 61.5041 | 61.5762 | 123.1995 | 61.554 | 122.9868 | 61.4293 | 61.4515 | 61.3606 | 61.3828
1485.8906 | 123.2803 | -61.5417 | 61.4502 | -0.42298 | -0.95628 | -0.94146 | -0.91782 | -0.86101 | -0.88504 | -0.85016 | 61.4364 | 0.23032 | 61.3676 | -0.046838 | 0.029923 | 61.6394 | 0.007721 | 61.4405 | 61.1188 | 60.5855 | 60.6003 | 60.6239 | 60.6807 | 60.6567 | 60.6916 | 122.9781 | 61.7721 | 122.9094 | 61.4949 | 61.5717 | 123.1812 | 61.5495 | 122.9822 | 61.4065 | 61.4287 | 61.3377 | 61.3599
1486.8906 | 123.3398 | -61.5417 | 61.4365 | -0.36804 | -0.85555 | -0.83157 | -0.80794 | -0.75114 | -0.77515 | -0.73113 | 61.4364 | 0.22116 | 61.3676 | -0.042259 | 0.029923 | 61.6531 | 0.007721 | 61.4451 | 61.1737 | 60.6862 | 60.7102 | 60.7338 | 60.7906 | 60.7666 | 60.8106 | 122.9781 | 61.7629 | 122.9094 | 61.4995 | 61.5717 | 123.1949 | 61.5495 | 122.9868 | 61.4065 | 61.4287 | 61.3377 | 61.3599
1487.8906 | 123.2941 | -61.5372 | 61.4365 | -0.37261 | -0.8235 | -0.80868 | -0.77589 | -0.72825 | -0.75684 | -0.70824 | 61.4364 | 0.21658 | 61.3631 | -0.046838 | 0.029923 | 61.6623 | -0.006014 | 61.4405 | 61.1646 | 60.7137 | 60.7285 | 60.7613 | 60.8089 | 60.7803 | 60.8289 | 122.9735 | 61.7538 | 122.9002 | 61.4903 | 61.5671 | 123.1995 | 61.5312 | 122.9777 | 61.4065 | 61.4424 | 61.3331 | 61.3691
1488.8906 | 123.3124 | -61.5601 | 61.4319 | -0.3543 | -0.79603 | -0.78578 | -0.75758 | -0.70079 | -0.72937 | -0.68535 | 61.4181 | 0.212 | 61.3447 | -0.046838 | 0.020767 | 61.6669 | -0.001436 | 61.4634 | 61.2058 | 60.764 | 60.7743 | 60.8025 | 60.8593 | 60.8307 | 60.8747 | 122.9781 | 61.7721 | 122.9048 | 61.5132 | 61.5808 | 123.2269 | 61.5586 | 123.0234 | 61.3973 | 61.4195 | 61.324 | 61.3462
1489.8906 | 123.2346 | -61.6013 | 61.4182 | -0.34972 | -0.79145 | -0.78121 | -0.74842 | -0.68705 | -0.72021 | -0.67619 | 61.3952 | 0.22574 | 61.3356 | -0.055996 | 0.025345 | 61.6852 | -0.001436 | 61.4725 | 61.2515 | 60.8098 | 60.8201 | 60.8528 | 60.9142 | 60.881 | 60.9251 | 122.9964 | 61.827 | 122.9368 | 61.5453 | 61.6266 | 123.2864 | 61.5998 | 123.0738 | 61.3698 | 61.3966 | 61.3102 | 61.337
1490.8906 | 123.3124 | -61.5463 | 61.4136 | -0.32683 | -0.73192 | -0.7171 | -0.6889 | -0.63212 | -0.66069 | -0.62125 | 61.386 | 0.22116 | 61.3173 | -0.046838 | 0.029923 | 61.7035 | -0.006014 | 61.5092 | 61.2195 | 60.8144 | 60.8292 | 60.8574 | 60.9142 | 60.8856 | 60.9251 | 122.9323 | 61.7675 | 122.8636 | 61.4995 | 61.5762 | 123.2498 | 61.5403 | 123.0555 | 61.3561 | 61.392 | 61.2873 | 61.3233
1491.8906 | 123.262 | -61.5555 | 61.377 | -0.33599 | -0.75482 | -0.73084 | -0.70263 | -0.65501 | -0.67901 | -0.63499 | 61.3723 | 0.22116 | 61.3081 | -0.051417 | 0.025345 | 61.7035 | 0.007721 | 61.5092 | 61.2195 | 60.8007 | 60.8246 | 60.8528 | 60.9005 | 60.8765 | 60.9205 | 122.9278 | 61.7766 | 122.8636 | 61.5041 | 61.5808 | 123.259 | 61.5632 | 123.0646 | 61.3469 | 61.3646 | 61.2828 | 61.3004
1492.8906 | 123.1979 | -61.6013 | 61.3998 | -0.34514 | -0.7594 | -0.74 | -0.70721 | -0.64585 | -0.67901 | -0.63957 | 61.3723 | 0.22116 | 61.299 | -0.046838 | 0.029923 | 61.7218 | -0.006014 | 61.4954 | 61.2561 | 60.8419 | 60.8613 | 60.894 | 60.9554 | 60.9222 | 60.9617 | 122.9735 | 61.8224 | 122.9002 | 61.5544 | 61.6312 | 123.3231 | 61.5952 | 123.0967 | 61.3424 | 61.3783 | 61.269 | 61.305
1493.8906 | 123.23 | -61.5875 | 61.4136 | -0.36804 | -0.80518 | -0.78578 | -0.75758 | -0.69621 | -0.72937 | -0.68535 | 61.3677 | 0.22574 | 61.3081 | -0.051417 | 0.020767 | 61.7172 | -0.006014 | 61.5 | 61.2195 | 60.7823 | 60.8017 | 60.8299 | 60.8913 | 60.8582 | 60.9022 | 122.9552 | 61.8133 | 122.8956 | 61.5361 | 61.6083 | 123.3048 | 61.5815 | 123.0875 | 61.3469 | 61.3737 | 61.2873 | 61.3141
1494.8906 | 123.1888 | -61.6379 | 61.3907 | -0.35888 | -0.79145 | -0.77205 | -0.74384 | -0.69163 | -0.72021 | -0.68077 | 61.3494 | 0.212 | 61.2898 | -0.042259 | 0.029923 | 61.7264 | -0.001436 | 61.5275 | 61.279 | 60.8464 | 60.8658 | 60.894 | 60.9462 | 60.9177 | 60.9571 | 122.9873 | 61.8499 | 122.9277 | 61.5956 | 61.6678 | 123.3643 | 61.6364 | 123.1654 | 61.3195 | 61.3508 | 61.2599 | 61.2912
1495.8906 | 123.2071 | -61.6516 | 61.4044 | -0.38177 | -0.83266 | -0.80868 | -0.78047 | -0.72825 | -0.75226 | -0.70824 | 61.3448 | 0.21658 | 61.2715 | -0.051417 | 0.029923 | 61.7401 | -0.001436 | 61.5412 | 61.2698 | 60.819 | 60.8429 | 60.8711 | 60.9234 | 60.8993 | 60.9434 | 122.9964 | 61.8682 | 122.9231 | 61.6002 | 61.6815 | 123.3917 | 61.6502 | 123.1928 | 61.3149 | 61.3462 | 61.2416 | 61.2729
1496.8906 | 123.1522 | -61.6791 | 61.3632 | -0.37719 | -0.80976 | -0.79494 | -0.76673 | -0.70994 | -0.73853 | -0.69451 | 61.3219 | 0.21658 | 61.2532 | -0.042259 | 0.029923 | 61.7722 | 0.003143 | 61.5641 | 61.3019 | 60.8693 | 60.8841 | 60.9123 | 60.9691 | 60.9406 | 60.9846 | 123.001 | 61.8957 | 122.9323 | 61.6368 | 61.709 | 123.4513 | 61.6822 | 123.2432 | 61.292 | 61.3188 | 61.2233 | 61.25
1497.8906 | 123.1659 | -61.6882 | 61.377 | -0.38177 | -0.8235 | -0.8041 | -0.77131 | -0.7191 | -0.74311 | -0.70824 | 61.2944 | 0.22116 | 61.2211 | -0.042259 | 0.025345 | 61.7859 | -0.001436 | 61.5733 | 61.3065 | 60.8647 | 60.8841 | 60.9169 | 60.9691 | 60.9451 | 60.98 | 122.9827 | 61.9094 | 122.9094 | 61.646 | 61.7136 | 123.4741 | 61.6868 | 123.2615 | 61.2691 | 61.2959 | 61.1958 | 61.2226
1498.8906 | 123.1842 | -61.6745 | 61.3358 | -0.39551 | -0.84181 | -0.83157 | -0.79878 | -0.74199 | -0.77058 | -0.73113 | 61.2899 | 0.21658 | 61.2211 | -0.03768 | 0.029923 | 61.7951 | -0.006014 | 61.5733 | 61.279 | 60.8327 | 60.8429 | 60.8757 | 60.9325 | 60.9039 | 60.9434 | 122.9644 | 61.8911 | 122.8956 | 61.6368 | 61.7044 | 123.4696 | 61.6685 | 123.2478 | 61.2599 | 61.2959 | 61.1912 | 61.2271
1499.8906 | 123.175 | -61.6791 | 61.3312 | -0.40466 | -0.85097 | -0.84073 | -0.79878 | -0.74199 | -0.78431 | -0.73113 | 61.2944 | 0.22116 | 61.2349 | -0.046838 | 0.025345 | 61.7905 | 0.003143 | 61.5687 | 61.2744 | 60.8281 | 60.8383 | 60.8803 | 60.9371 | 60.8948 | 60.9479 | 122.9735 | 61.9002 | 122.9139 | 61.6322 | 61.7044 | 123.4696 | 61.6822 | 123.2478 | 61.2691 | 61.2913 | 61.2095 | 61.2317
1500.8906 | 123.1796 | -61.702 | 61.3266 | -0.42298 | -0.86929 | -0.84988 | -0.82168 | -0.7603 | -0.79347 | -0.75402 | 61.3036 | 0.21658 | 61.2257 | -0.046838 | 0.034501 | 61.7951 | 0.003143 | 61.5733 | 61.279 | 60.8327 | 60.8521 | 60.8803 | 60.9417 | 60.9085 | 60.9479 | 123.0056 | 61.9185 | 122.9277 | 61.6551 | 61.7365 | 123.497 | 61.7051 | 123.2752 | 61.2691 | 61.3005 | 61.1912 | 61.2226
1501.8906 | 123.2025 | -61.7065 | 61.3266 | -0.43671 | -0.87387 | -0.85904 | -0.82625 | -0.77403 | -0.79805 | -0.7586 | 61.2761 | 0.22116 | 61.2074 | -0.046838 | 0.029923 | 61.8042 | -0.001436 | 61.5916 | 61.2698 | 60.8327 | 60.8475 | 60.8803 | 60.9325 | 60.9085 | 60.9479 | 122.9827 | 61.9277 | 122.9139 | 61.6597 | 61.7365 | 123.5108 | 61.7051 | 123.2981 | 61.2462 | 61.2776 | 61.1775 | 61.2088
1502.8906 | 123.1979 | -61.7386 | 61.2946 | -0.42298 | -0.87844 | -0.8682 | -0.84457 | -0.78777 | -0.81178 | -0.76776 | 61.2532 | 0.21658 | 61.1891 | -0.042259 | 0.029923 | 61.8271 | 0.003143 | 61.6099 | 61.3156 | 60.8601 | 60.8704 | 60.894 | 60.9508 | 60.9268 | 60.9708 | 122.9918 | 61.9552 | 122.9277 | 61.6963 | 61.7685 | 123.5657 | 61.7417 | 123.3485 | 61.2233 | 61.2501 | 61.1592 | 61.1859
1503.8906 | 123.1796 | -61.7523 | 61.2671 | -0.42298 | -0.84639 | -0.83157 | -0.79878 | -0.74199 | -0.77058 | -0.74029 | 61.2441 | 0.22574 | 61.1845 | -0.03768 | 0.025345 | 61.8408 | -0.001436 | 61.6236 | 61.3293 | 60.9059 | 60.9207 | 60.9535 | 61.0103 | 60.9817 | 61.012 | 122.9964 | 61.9781 | 122.9368 | 61.7146 | 61.7777 | 123.5932 | 61.7509 | 123.3759 | 61.2187 | 61.2455 | 61.1592 | 61.1859
1504.8906 | 123.1888 | -61.7432 | 61.2396 | -0.42756 | -0.86013 | -0.84073 | -0.81252 | -0.7603 | -0.77973 | -0.74029 | 61.2349 | 0.22116 | 61.1662 | -0.042259 | 0.029923 | 61.85 | -0.006014 | 61.6419 | 61.3156 | 60.883 | 60.9024 | 60.9306 | 60.9829 | 60.9634 | 61.0029 | 122.9781 | 61.9643 | 122.9094 | 61.7009 | 61.7731 | 123.5932 | 61.7371 | 123.3851 | 61.205 | 61.2409 | 61.1363 | 61.1722
1505.8906 | 123.1796 | -61.7752 | 61.2488 | -0.42756 | -0.85555 | -0.8453 | -0.81252 | -0.7603 | -0.78889 | -0.74486 | 61.2258 | 0.212 | 61.1525 | -0.046838 | 0.025345 | 61.8637 | 0.003143 | 61.6465 | 61.3477 | 60.9197 | 60.9299 | 60.9627 | 61.0149 | 60.9863 | 61.0303 | 123.001 | 61.9872 | 122.9277 | 61.7284 | 61.8006 | 123.6389 | 61.7784 | 123.4217 | 61.2004 | 61.2226 | 61.1271 | 61.1493
1506.8906 | 123.1384 | -61.8027 | 61.2259 | -0.4184 | -0.81892 | -0.8041 | -0.78047 | -0.72825 | -0.74311 | -0.69908 | 61.2029 | 0.22574 | 61.1296 | -0.051417 | 0.029923 | 61.8775 | -0.001436 | 61.6602 | 61.3843 | 60.9838 | 60.9986 | 61.0222 | 61.0744 | 61.0596 | 61.1036 | 123.0055 | 62.0284 | 122.9322 | 61.7513 | 61.8326 | 123.6801 | 61.8012 | 123.4629 | 61.1729 | 61.2043 | 61.0996 | 61.131
1507.8906 | 123.1522 | -61.8301 | 61.2213 | -0.43671 | -0.86471 | -0.84988 | -0.82625 | -0.76488 | -0.78889 | -0.74486 | 61.1937 | 0.21658 | 61.1341 | -0.03768 | 0.034501 | 61.8912 | 0.003143 | 61.674 | 61.3934 | 60.9654 | 60.9803 | 61.0039 | 61.0653 | 61.0413 | 61.0853 | 123.0239 | 62.0467 | 122.9643 | 61.7925 | 61.8646 | 123.7213 | 61.8333 | 123.5041 | 61.1592 | 61.1906 | 61.0996 | 61.131
1508.8906 | 123.1842 | -61.8347 | 61.2076 | -0.4596 | -0.87844 | -0.87278 | -0.84457 | -0.78777 | -0.8072 | -0.76318 | 61.1662 | 0.22116 | 61.1067 | -0.051417 | 0.025345 | 61.9141 | -0.001436 | 61.7014 | 61.3751 | 60.9563 | 60.9619 | 60.9901 | 61.0469 | 61.0275 | 61.0715 | 123.001 | 62.0559 | 122.9414 | 61.7833 | 61.8601 | 123.7488 | 61.8333 | 123.5362 | 61.1409 | 61.1677 | 61.0813 | 61.1081
1509.8906 | 123.1613 | -61.8347 | 61.1938 | -0.45045 | -0.86929 | -0.85904 | -0.82625 | -0.77403 | -0.78889 | -0.7586 | 61.1708 | 0.21658 | 61.0975 | -0.042259 | 0.025345 | 61.9187 | -0.006014 | 61.706 | 61.3843 | 60.9654 | 60.9757 | 61.0085 | 61.0607 | 61.0458 | 61.0761 | 123.0055 | 62.0513 | 122.9322 | 61.7925 | 61.8601 | 123.7534 | 61.8287 | 123.5407 | 61.1455 | 61.1768 | 61.0722 | 61.1035
1510.8906 | 123.2758 | -61.8164 | 61.1389 | -0.47792 | -0.90134 | -0.90025 | -0.86288 | -0.8015 | -0.8301 | -0.78149 | 61.1525 | 0.22116 | 61.0884 | -0.046838 | 0.029923 | 61.9324 | -0.001436 | 61.706 | 61.3385 | 60.9151 | 60.9162 | 60.9535 | 61.0149 | 60.9863 | 61.0349 | 122.9689 | 62.0376 | 122.9048 | 61.7696 | 61.8463 | 123.7488 | 61.815 | 123.5224 | 61.1226 | 61.1539 | 61.0584 | 61.0898
1511.8906 | 123.1979 | -61.8896 | 61.1069 | -0.40924 | -0.79603 | -0.78121 | -0.74842 | -0.68705 | -0.72479 | -0.67161 | 61.1113 | 0.21658 | 61.038 | -0.051417 | 0.020767 | 61.9782 | -0.001436 | 61.7518 | 61.4804 | 61.0936 | 61.1084 | 61.1412 | 61.2026 | 61.1649 | 61.218 | 123.0009 | 62.1062 | 122.9276 | 61.8382 | 61.9104 | 123.8678 | 61.8882 | 123.6415 | 61.0905 | 61.1127 | 61.0172 | 61.0394
1512.8906 | 123.2758 | -61.8942 | 61.0474 | -0.4596 | -0.86013 | -0.85904 | -0.82625 | -0.77403 | -0.79347 | -0.74486 | 61.0747 | 0.22116 | 61.0105 | -0.042259 | 0.029923 | 62.0102 | -0.006014 | 61.793 | 61.4346 | 61.0341 | 61.0352 | 61.068 | 61.1202 | 61.1008 | 61.1494 | 122.9689 | 62.1154 | 122.9048 | 61.852 | 61.9241 | 123.9045 | 61.8882 | 123.6872 | 61.0447 | 61.0807 | 60.9806 | 61.0165
1513.8906 | 123.262 | -61.9217 | 61.0291 | -0.46418 | -0.87844 | -0.8682 | -0.84915 | -0.77861 | -0.8072 | -0.7586 | 61.0472 | 0.22116 | 60.9831 | -0.03768 | 0.020767 | 62.0377 | -0.006014 | 61.8205 | 61.4575 | 61.0432 | 61.0535 | 61.0725 | 61.1431 | 61.1145 | 61.1631 | 122.9689 | 62.1429 | 122.9047 | 61.884 | 61.9425 | 123.9594 | 61.9157 | 123.7422 | 61.0264 | 61.0532 | 60.9623 | 60.9891
1514.8906 | 123.2849 | -61.9354 | 60.9833 | -0.4596 | -0.87387 | -0.86362 | -0.83999 | -0.78319 | -0.8072 | -0.76318 | 61.0243 | 0.22116 | 60.9602 | -0.046838 | 0.029923 | 62.056 | -0.001436 | 61.8479 | 61.4758 | 61.0616 | 61.0718 | 61.0954 | 61.1522 | 61.1282 | 61.1722 | 122.9597 | 62.1566 | 122.8956 | 61.8886 | 61.9653 | 123.9914 | 61.934 | 123.7834 | 60.9944 | 61.0257 | 60.9302 | 60.9616
1515.8906 | 123.262 | -61.9537 | 60.997 | -0.47334 | -0.89218 | -0.87735 | -0.84457 | -0.79692 | -0.82094 | -0.76776 | 61.0243 | 0.22116 | 60.9647 | -0.051417 | 0.020767 | 62.056 | -0.010593 | 61.8434 | 61.4804 | 61.0616 | 61.0764 | 61.1092 | 61.1568 | 61.1328 | 61.186 | 122.978 | 62.1749 | 122.9185 | 61.9023 | 61.9745 | 124.0097 | 61.9431 | 123.7971 | 61.0035 | 61.0349 | 60.944 | 60.9753
1516.8906 | 123.2346 | -61.9492 | 60.9879 | -0.46876 | -0.86929 | -0.85904 | -0.83541 | -0.77403 | -0.8072 | -0.74944 | 61.0243 | 0.21658 | 60.951 | -0.051417 | 0.025345 | 62.0606 | -0.001436 | 61.8479 | 61.4804 | 61.0799 | 61.0901 | 61.1137 | 61.1751 | 61.142 | 61.1997 | 122.9735 | 62.1657 | 122.9002 | 61.8977 | 61.9745 | 124.0097 | 61.9477 | 123.7971 | 60.999 | 61.0257 | 60.9257 | 60.9524
1517.8906 | 123.2346 | -61.9629 | 60.997 | -0.49623 | -0.9105 | -0.90483 | -0.88577 | -0.82439 | -0.83925 | -0.79522 | 61.0106 | 0.212 | 60.9464 | -0.046838 | 0.020767 | 62.0606 | 0.003143 | 61.8663 | 61.4667 | 61.0524 | 61.0581 | 61.0771 | 61.1385 | 61.1236 | 61.1677 | 122.9735 | 62.1749 | 122.9093 | 61.9161 | 61.9837 | 124.0235 | 61.966 | 123.8292 | 60.9898 | 61.0074 | 60.9257 | 60.9433
1518.8906 | 123.23 | -62.0087 | 60.9421 | -0.49165 | -0.90134 | -0.90025 | -0.87204 | -0.80608 | -0.83925 | -0.78607 | 60.9785 | 0.22116 | 60.9144 | -0.046838 | 0.029923 | 62.1018 | -0.006014 | 61.8983 | 61.517 | 61.1073 | 61.1084 | 61.1366 | 61.2026 | 61.1694 | 61.2226 | 122.9872 | 62.2298 | 122.923 | 61.9618 | 62.0386 | 124.1105 | 62.0027 | 123.907 | 60.9486 | 60.9845 | 60.8845 | 60.9204
1519.8906 | 123.2483 | -62.059 | 60.9238 | -0.50081 | -0.91965 | -0.90483 | -0.88577 | -0.82439 | -0.84841 | -0.80896 | 60.9236 | 0.22116 | 60.8594 | -0.046838 | 0.034501 | 62.1522 | 0.003143 | 61.9349 | 61.5582 | 61.1394 | 61.1542 | 61.1732 | 61.2346 | 61.2106 | 61.2501 | 122.9826 | 62.2802 | 122.9185 | 62.0122 | 62.0935 | 124.2112 | 62.0622 | 123.994 | 60.8891 | 60.9204 | 60.8249 | 60.8563
1520.8906 | 123.2071 | -62.0636 | 60.9009 | -0.54659 | -0.98376 | -0.97808 | -0.95445 | -0.89306 | -0.92166 | -0.86848 | 60.9098 | 0.21658 | 60.8457 | -0.042259 | 0.025345 | 62.1705 | 0.003143 | 61.9624 | 61.517 | 61.0798 | 61.0855 | 61.1091 | 61.1705 | 61.1419 | 61.1951 | 122.9734 | 62.2802 | 122.9093 | 62.0213 | 62.0889 | 124.2341 | 62.0667 | 124.026 | 60.8845 | 60.9067 | 60.8204 | 60.8426
1521.8906 | 123.2666 | -62.0773 | 60.8917 | -0.54659 | -0.9746 | -0.96893 | -0.93614 | -0.87933 | -0.90335 | -0.8639 | 60.8915 | 0.22116 | 60.8228 | -0.055996 | 0.020767 | 62.2025 | -0.006014 | 61.9899 | 61.5307 | 61.1027 | 61.1084 | 61.1412 | 61.198 | 61.174 | 61.2134 | 122.9689 | 62.2985 | 122.9001 | 62.0213 | 62.0981 | 124.2798 | 62.0713 | 124.0672 | 60.8708 | 60.8975 | 60.802 | 60.8288
1522.8906 | 123.2574 | -62.0819 | 60.8871 | -0.57406 | -1.0112 | -0.9964 | -0.97276 | -0.91595 | -0.94913 | -0.89594 | 60.8824 | 0.22116 | 60.8091 | -0.046838 | 0.029923 | 62.2025 | 0.003143 | 61.9807 | 61.5078 | 61.0707 | 61.0855 | 61.1091 | 61.166 | 61.1328 | 61.186 | 122.9643 | 62.3031 | 122.891 | 62.0351 | 62.1118 | 124.2844 | 62.0851 | 124.0626 | 60.8525 | 60.8792 | 60.7792 | 60.8059
1523.8906 | 123.3078 | -62.0911 | 60.8597 | -0.59238 | -1.0387 | -1.0239 | -1.0048 | -0.94342 | -0.9766 | -0.92799 | 60.8549 | 0.22574 | 60.8045 | -0.055996 | 0.025345 | 62.2208 | 0.003143 | 61.9945 | 61.4987 | 61.0524 | 61.0672 | 61.0862 | 61.1476 | 61.1145 | 61.1631 | 122.946 | 62.3168 | 122.8956 | 62.0351 | 62.1164 | 124.3119 | 62.0942 | 124.0855 | 60.8296 | 60.8518 | 60.7792 | 60.8014
1524.8906 | 123.2941 | -62.0911 | 60.8551 | -0.58322 | -1.0021 | -0.9964 | -0.96819 | -0.91137 | -0.94455 | -0.88679 | 60.8595 | 0.22116 | 60.7953 | -0.03768 | 0.020767 | 62.23 | -0.001436 | 62.0128 | 61.5078 | 61.089 | 61.0947 | 61.1229 | 61.1797 | 61.1465 | 61.2043 | 122.9505 | 62.3122 | 122.8864 | 62.0534 | 62.1118 | 124.321 | 62.0896 | 124.1038 | 60.8387 | 60.8609 | 60.7746 | 60.7968
1525.8906 | 123.2758 | -62.1506 | 60.8231 | -0.59238 | -1.0112 | -1.0056 | -0.97276 | -0.91595 | -0.93998 | -0.89594 | 60.8274 | 0.22116 | 60.7633 | -0.046838 | 0.029923 | 62.2437 | -0.001436 | 62.0448 | 61.5582 | 61.1393 | 61.145 | 61.1778 | 61.2346 | 61.2106 | 61.2546 | 122.978 | 62.3717 | 122.9139 | 62.1037 | 62.1805 | 124.3943 | 62.1491 | 124.1954 | 60.7975 | 60.8289 | 60.7334 | 60.7647
1526.8906 | 123.2986 | -62.1826 | 60.7544 | -0.61069 | -1.0295 | -1.0239 | -0.99566 | -0.94342 | -0.96287 | -0.91426 | 60.7771 | 0.21658 | 60.7129 | -0.042259 | 0.020767 | 62.3032 | -0.001436 | 62.086 | 61.5719 | 61.1531 | 61.1587 | 61.187 | 61.2392 | 61.2197 | 61.2684 | 122.9597 | 62.3992 | 122.8956 | 62.1404 | 62.2034 | 124.4858 | 62.1812 | 124.2686 | 60.7563 | 60.7785 | 60.6922 | 60.7144
1527.8906 | 123.2895 | -62.2238 | 60.7407 | -0.6519 | -1.0845 | -1.0834 | -1.0506 | -0.99835 | -1.027 | -0.97377 | 60.7267 | 0.21658 | 60.6626 | -0.042259 | 0.029923 | 62.3444 | -0.001436 | 62.1272 | 61.5719 | 61.1393 | 61.1404 | 61.1732 | 61.2255 | 61.1969 | 61.25 | 122.9505 | 62.4404 | 122.8864 | 62.1816 | 62.2537 | 124.5682 | 62.2224 | 124.351 | 60.6968 | 60.7281 | 60.6327 | 60.664
1528.8906 | 123.3582 | -62.2192 | 60.7544 | -0.66105 | -1.0891 | -1.0834 | -1.0598 | -1.0075 | -1.0361 | -0.98751 | 60.7038 | 0.22574 | 60.6443 | -0.051417 | 0.025345 | 62.3811 | -0.001436 | 62.1638 | 61.5582 | 61.1302 | 61.1358 | 61.1595 | 61.2117 | 61.1831 | 61.2317 | 122.9231 | 62.445 | 122.8635 | 62.1678 | 62.2446 | 124.6003 | 62.2178 | 124.3831 | 60.6785 | 60.7052 | 60.6189 | 60.6457
1529.8906 | 123.2758 | -62.2879 | 60.6628 | -0.66563 | -1.1028 | -1.088 | -1.0643 | -1.0029 | -1.0315 | -0.98293 | 60.6855 | 0.212 | 60.6122 | -0.03768 | 0.025345 | 62.4085 | 0.003143 | 62.1913 | 61.6223 | 61.1851 | 61.1999 | 61.2236 | 61.285 | 61.2564 | 61.305 | 122.9734 | 62.4999 | 122.9001 | 62.2502 | 62.3132 | 124.6964 | 62.291 | 124.4792 | 60.6602 | 60.6824 | 60.5869 | 60.6091
1530.8906 | 123.2895 | -62.2879 | 60.6857 | -0.66105 | -1.0753 | -1.0742 | -1.0506 | -0.9892 | -1.0178 | -0.9692 | 60.6992 | 0.22116 | 60.6351 | -0.046838 | 0.029923 | 62.3948 | -0.001436 | 62.1684 | 61.6268 | 61.2126 | 61.2137 | 61.2373 | 61.2987 | 61.2701 | 61.3187 | 122.9871 | 62.5091 | 122.923 | 62.2411 | 62.3178 | 124.6827 | 62.2865 | 124.4563 | 60.6693 | 60.7007 | 60.6052 | 60.6365
1531.8906 | 123.1659 | -62.2833 | 60.7224 | -0.67021 | -1.0753 | -1.088 | -1.0506 | -0.99835 | -1.0178 | -0.98293 | 60.6763 | 0.22116 | 60.6076 | -0.046838 | 0.029923 | 62.4039 | -0.006014 | 62.1822 | 61.6131 | 61.208 | 61.1954 | 61.2327 | 61.285 | 61.2655 | 61.3004 | 122.9597 | 62.5045 | 122.891 | 62.2365 | 62.3132 | 124.6873 | 62.2773 | 124.4655 | 60.6464 | 60.6824 | 60.5777 | 60.6137
1532.8906 | 123.2803 | -62.2971 | 60.6583 | -0.72515 | -1.1669 | -1.1612 | -1.1376 | -1.0762 | -1.0956 | -1.0562 | 60.6397 | 0.22116 | 60.571 | -0.042259 | 0.029923 | 62.436 | 0.003143 | 62.2188 | 61.5719 | 61.1301 | 61.1358 | 61.1595 | 61.2209 | 61.2014 | 61.2409 | 122.9368 | 62.5182 | 122.8681 | 62.2548 | 62.327 | 124.7331 | 62.3002 | 124.5158 | 60.6098 | 60.6366 | 60.5411 | 60.5679
1533.8906 | 123.1522 | -62.3932 | 60.6308 | -0.72515 | -1.1669 | -1.1566 | -1.1284 | -1.0716 | -1.1048 | -1.0562 | 60.5894 | 0.22574 | 60.5252 | -0.042259 | 0.029923 | 62.4955 | 0.003143 | 62.2829 | 61.668 | 61.2263 | 61.2365 | 61.2648 | 61.3216 | 61.2884 | 61.337 | 122.9825 | 62.6189 | 122.9184 | 62.3509 | 62.4231 | 124.8887 | 62.3963 | 124.6761 | 60.5594 | 60.5862 | 60.4953 | 60.5221
1534.8906 | 123.1522 | -62.4573 | 60.6125 | -0.73431 | -1.1578 | -1.1521 | -1.133 | -1.0762 | -1.0911 | -1.0516 | 60.5527 | 0.22116 | 60.4886 | -0.046838 | 0.029923 | 62.5321 | -0.001436 | 62.3149 | 61.723 | 61.2995 | 61.3052 | 61.3243 | 61.3811 | 61.3662 | 61.4057 | 123.01 | 62.6784 | 122.9459 | 62.4104 | 62.4872 | 124.9894 | 62.4558 | 124.7722 | 60.5228 | 60.5542 | 60.4587 | 60.49
1535.8906 | 123.1705 | -62.4481 | 60.6216 | -0.76178 | -1.2173 | -1.1979 | -1.1742 | -1.122 | -1.1552 | -1.102 | 60.5344 | 0.21658 | 60.4657 | -0.046838 | 0.020767 | 62.5459 | -0.001436 | 62.3332 | 61.6863 | 61.2308 | 61.2503 | 61.2739 | 61.3262 | 61.293 | 61.3462 | 122.9825 | 62.6647 | 122.9138 | 62.4013 | 62.4689 | 124.994 | 62.4467 | 124.7814 | 60.5136 | 60.5358 | 60.4449 | 60.4671
1536.8906 | 123.1338 | -62.4619 | 60.6033 | -0.77094 | -1.2081 | -1.207 | -1.1742 | -1.1265 | -1.146 | -1.102 | 60.539 | 0.22116 | 60.4703 | -0.046838 | 0.025345 | 62.5459 | 0.003143 | 62.3241 | 61.6909 | 61.2537 | 61.2548 | 61.2876 | 61.3353 | 61.3158 | 61.3599 | 123.0008 | 62.683 | 122.9321 | 62.415 | 62.4872 | 125.0077 | 62.465 | 124.7859 | 60.5136 | 60.5358 | 60.4449 | 60.4671
1537.8906 | 123.1934 | -62.5259 | 60.5026 | -0.77551 | -1.2127 | -1.207 | -1.1742 | -1.1357 | -1.146 | -1.0928 | 60.4657 | 0.22116 | 60.397 | -0.051417 | 0.034501 | 62.6054 | -0.001436 | 62.3928 | 61.7504 | 61.3132 | 61.3189 | 61.3517 | 61.3902 | 61.3799 | 61.4331 | 122.9917 | 62.7471 | 122.923 | 62.4745 | 62.5604 | 125.1313 | 62.5245 | 124.9187 | 60.4312 | 60.4672 | 60.3625 | 60.3985
1538.8906 | 123.1659 | -62.5763 | 60.4797 | -0.8213 | -1.2631 | -1.2528 | -1.2292 | -1.1769 | -1.2009 | -1.1523 | 60.4337 | 0.22574 | 60.3604 | -0.042259 | 0.025345 | 62.6512 | -0.001436 | 62.434 | 61.755 | 61.3132 | 61.3235 | 61.3471 | 61.3994 | 61.3753 | 61.424 | 123.01 | 62.802 | 122.9367 | 62.534 | 62.6016 | 125.2275 | 62.5749 | 125.0102 | 60.4083 | 60.4351 | 60.3351 | 60.3618
1539.8906 | 123.1567 | -62.5809 | 60.4385 | -0.84419 | -1.286 | -1.2849 | -1.2521 | -1.1998 | -1.2284 | -1.1752 | 60.3971 | 0.22116 | 60.3329 | -0.042259 | 0.029923 | 62.6786 | 0.003143 | 62.4706 | 61.7367 | 61.2949 | 61.296 | 61.3288 | 61.3811 | 61.3525 | 61.4057 | 122.9779 | 62.802 | 122.9138 | 62.5386 | 62.6108 | 125.2595 | 62.584 | 125.0515 | 60.3671 | 60.3939 | 60.303 | 60.3298
1540.8906 | 123.1522 | -62.6404 | 60.4202 | -0.84877 | -1.2951 | -1.2849 | -1.2612 | -1.2089 | -1.233 | -1.1889 | 60.3421 | 0.22574 | 60.278 | -0.051417 | 0.029923 | 62.7244 | -0.001436 | 62.5164 | 61.7916 | 61.3453 | 61.3555 | 61.3792 | 61.4314 | 61.4074 | 61.4514 | 122.9825 | 62.8661 | 122.9184 | 62.589 | 62.6703 | 125.3648 | 62.6389 | 125.1567 | 60.3122 | 60.3435 | 60.2481 | 60.2794
1541.8906 | 123.1888 | -62.6266 | 60.3607 | -0.89455 | -1.3363 | -1.3306 | -1.2978 | -1.2456 | -1.2696 | -1.2256 | 60.3421 | 0.21658 | 60.278 | -0.046838 | 0.034501 | 62.7473 | 0.003143 | 62.5301 | 61.7321 | 61.2903 | 61.296 | 61.3288 | 61.3811 | 61.357 | 61.4011 | 122.9688 | 62.8432 | 122.9046 | 62.5798 | 62.6611 | 125.3739 | 62.6298 | 125.1567 | 60.3076 | 60.339 | 60.2435 | 60.2749
1542.8906 | 123.2025 | -62.6724 | 60.3424 | -0.91287 | -1.3684 | -1.3581 | -1.3345 | -1.2776 | -1.3062 | -1.2576 | 60.3101 | 0.22574 | 60.2322 | -0.042259 | 0.029923 | 62.7793 | -0.001436 | 62.5621 | 61.7596 | 61.304 | 61.3143 | 61.338 | 61.3948 | 61.3662 | 61.4148 | 122.9825 | 62.8982 | 122.9046 | 62.6302 | 62.7023 | 125.4518 | 62.671 | 125.2346 | 60.2801 | 60.3115 | 60.2023 | 60.2337
1543.8906 | 123.2025 | -62.6587 | 60.3607 | -0.83503 | -1.2585 | -1.2528 | -1.2292 | -1.1769 | -1.2009 | -1.1477 | 60.3192 | 0.21658 | 60.2505 | -0.046838 | 0.025345 | 62.7656 | 0.003143 | 62.5438 | 61.8237 | 61.4002 | 61.4059 | 61.4295 | 61.4818 | 61.4577 | 61.5109 | 122.9779 | 62.8753 | 122.9092 | 62.6119 | 62.684 | 125.4243 | 62.6618 | 125.2025 | 60.2939 | 60.3161 | 60.2252 | 60.2474
1544.8906 | 123.2117 | -62.6999 | 60.3287 | -0.88997 | -1.3134 | -1.3077 | -1.2887 | -1.2318 | -1.2605 | -1.2027 | 60.2917 | 0.22116 | 60.2322 | -0.03768 | 0.034501 | 62.7931 | 0.003143 | 62.5621 | 61.8099 | 61.3865 | 61.3921 | 61.4112 | 61.4681 | 61.4394 | 61.4972 | 122.9916 | 62.9211 | 122.9321 | 62.6622 | 62.7344 | 125.493 | 62.703 | 125.262 | 60.2572 | 60.2886 | 60.1977 | 60.2291
1545.8906 | 123.2025 | -62.7869 | 60.2234 | -0.87624 | -1.3089 | -1.2986 | -1.2658 | -1.2181 | -1.2422 | -1.1844 | 60.2093 | 0.22116 | 60.1407 | -0.046838 | 0.029923 | 62.8755 | -0.001436 | 62.6629 | 61.9106 | 61.478 | 61.4883 | 61.5211 | 61.5688 | 61.5447 | 61.6025 | 122.9962 | 63.008 | 122.9275 | 62.74 | 62.8168 | 125.6624 | 62.7854 | 125.4497 | 60.1794 | 60.2108 | 60.1107 | 60.1421
1546.8906 | 123.1842 | -62.8601 | 60.1593 | -0.90829 | -1.3409 | -1.3261 | -1.2978 | -1.241 | -1.2696 | -1.2256 | 60.1361 | 0.22574 | 60.0628 | -0.046838 | 0.025345 | 62.9487 | 0.003143 | 62.7361 | 61.9518 | 61.5192 | 61.534 | 61.5623 | 61.6191 | 61.5905 | 61.6345 | 122.9962 | 63.0858 | 122.9229 | 62.8133 | 62.8855 | 125.8088 | 62.8633 | 125.5962 | 60.1107 | 60.1329 | 60.0375 | 60.0597
1547.8906 | 123.2208 | -62.8784 | 60.1456 | -0.85792 | -1.2631 | -1.2482 | -1.22 | -1.1677 | -1.1918 | -1.1523 | 60.104 | 0.21658 | 60.0262 | -0.051417 | 0.029923 | 62.9899 | -0.001436 | 62.7727 | 62.0205 | 61.6154 | 61.6302 | 61.6584 | 61.7107 | 61.6866 | 61.7261 | 122.9824 | 63.095 | 122.9046 | 62.827 | 62.9083 | 125.8684 | 62.877 | 125.6512 | 60.0741 | 60.1055 | 59.9963 | 60.0276
1548.8906 | 123.1522 | -62.915 | 60.0906 | -0.89913 | -1.2997 | -1.2986 | -1.2749 | -1.2227 | -1.2422 | -1.1935 | 60.072 | 0.22116 | 59.9896 | -0.046838 | 0.025345 | 63.0174 | -0.006014 | 62.8002 | 62.0159 | 61.6153 | 61.6165 | 61.6401 | 61.6924 | 61.6729 | 61.7215 | 122.987 | 63.1362 | 122.9046 | 62.8682 | 62.9404 | 125.9324 | 62.909 | 125.7152 | 60.0466 | 60.078 | 59.9642 | 59.9956
1549.8906 | 123.1796 | -62.8693 | 60.1685 | -0.91744 | -1.3317 | -1.3215 | -1.2933 | -1.2364 | -1.265 | -1.2164 | 60.1086 | 0.21658 | 60.0399 | -0.046838 | 0.029923 | 62.9716 | -0.010593 | 62.7498 | 61.9518 | 61.5375 | 61.5478 | 61.576 | 61.6329 | 61.6042 | 61.6528 | 122.9779 | 63.0858 | 122.9092 | 62.8224 | 62.8992 | 125.8409 | 62.8587 | 125.6191 | 60.0787 | 60.1192 | 60.01 | 60.0505
1550.8906 | 123.1384 | -62.9105 | 60.1227 | -0.94034 | -1.3455 | -1.3352 | -1.307 | -1.2639 | -1.2788 | -1.2302 | 60.104 | 0.22116 | 60.0445 | -0.046838 | 0.029923 | 62.9808 | 0.007721 | 62.7682 | 61.9701 | 61.565 | 61.5752 | 61.6035 | 61.6466 | 61.6317 | 61.6803 | 123.0145 | 63.1316 | 122.955 | 62.8636 | 62.9404 | 125.8912 | 62.9182 | 125.6786 | 60.0741 | 60.0963 | 60.0146 | 60.0368
1551.8906 | 123.1567 | -62.9837 | 60.0174 | -0.93576 | -1.3317 | -1.3261 | -1.3024 | -1.241 | -1.2696 | -1.221 | 60.0125 | 0.22116 | 59.9484 | -0.046838 | 0.029923 | 63.0678 | -0.001436 | 62.8551 | 62.0479 | 61.652 | 61.6576 | 61.6813 | 61.7427 | 61.7141 | 61.7627 | 122.9962 | 63.2049 | 122.9321 | 62.9369 | 63.0136 | 126.0515 | 62.9823 | 125.8389 | 59.9825 | 60.0139 | 59.9184 | 59.9498
1552.8906 | 123.1613 | -63.0707 | 59.9533 | -0.96781 | -1.373 | -1.3581 | -1.339 | -1.2822 | -1.3017 | -1.2576 | 59.9529 | 0.22116 | 59.8751 | -0.055996 | 0.029923 | 63.1319 | -0.001436 | 62.9101 | 62.1029 | 61.6977 | 61.7126 | 61.7316 | 61.7885 | 61.769 | 61.8131 | 123.0236 | 63.2918 | 122.9458 | 63.0147 | 63.1006 | 126.2025 | 63.0692 | 125.9808 | 59.923 | 59.9544 | 59.8452 | 59.8765
1553.8906 | 123.1522 | -63.1393 | 59.8755 | -0.89913 | -1.2676 | -1.2574 | -1.2292 | -1.1723 | -1.2101 | -1.1477 | 59.8568 | 0.22574 | 59.7973 | -0.042259 | 0.025345 | 63.2188 | -0.006014 | 63.0016 | 62.2402 | 61.8717 | 61.882 | 61.9102 | 61.967 | 61.9292 | 61.9916 | 122.9961 | 63.3651 | 122.9366 | 63.0971 | 63.1647 | 126.3582 | 63.1333 | 126.141 | 59.8314 | 59.8628 | 59.7719 | 59.8033
1554.8906 | 123.2758 | -63.1577 | 59.7931 | -0.88539 | -1.2585 | -1.2574 | -1.2292 | -1.1723 | -1.1964 | -1.1477 | 59.8247 | 0.22574 | 59.7561 | -0.051417 | 0.025345 | 63.26 | -0.006014 | 63.0383 | 62.2723 | 61.8992 | 61.9003 | 61.9285 | 61.9853 | 61.9613 | 62.0099 | 122.9824 | 63.3834 | 122.9137 | 63.1062 | 63.183 | 126.4177 | 63.1516 | 126.1959 | 59.7994 | 59.8308 | 59.7307 | 59.7621
1555.8906 | 123.2574 | -63.1805 | 59.7473 | -0.91744 | -1.286 | -1.2803 | -1.2521 | -1.1998 | -1.2284 | -1.1706 | 59.7927 | 0.22574 | 59.7195 | -0.055996 | 0.025345 | 63.2967 | 0.003143 | 63.0749 | 62.2631 | 61.8946 | 61.9003 | 61.9285 | 61.9808 | 61.9521 | 62.0099 | 122.9732 | 63.4063 | 122.9 | 63.1245 | 63.2059 | 126.4772 | 63.1837 | 126.2554 | 59.7673 | 59.7895 | 59.6941 | 59.7163
1556.8906 | 123.2758 | -63.1439 | 59.8022 | -0.87624 | -1.2356 | -1.2253 | -1.1971 | -1.1403 | -1.1689 | -1.1294 | 59.8385 | 0.23032 | 59.7607 | -0.042259 | 0.025345 | 63.2372 | -0.006014 | 63.0154 | 62.2677 | 61.9083 | 61.9186 | 61.9468 | 62.0037 | 61.975 | 62.0145 | 122.9824 | 63.3742 | 122.9046 | 63.1017 | 63.1693 | 126.3811 | 63.1379 | 126.1593 | 59.8131 | 59.8445 | 59.7353 | 59.7667
1557.8906 | 123.2529 | -63.1668 | 59.7519 | -0.92202 | -1.2905 | -1.2757 | -1.2521 | -1.1998 | -1.2193 | -1.1752 | 59.7927 | 0.22116 | 59.7286 | -0.046838 | 0.020767 | 63.2784 | -0.006014 | 63.0566 | 62.2448 | 61.8763 | 61.8911 | 61.9148 | 61.967 | 61.9476 | 61.9916 | 122.9595 | 63.388 | 122.8954 | 63.12 | 63.1876 | 126.4452 | 63.1608 | 126.2234 | 59.7719 | 59.7987 | 59.7078 | 59.7346
1558.8906 | 123.2529 | -63.2721 | 59.6832 | -0.93576 | -1.3043 | -1.294 | -1.2704 | -1.2135 | -1.233 | -1.1889 | 59.7194 | 0.22574 | 59.6554 | -0.046838 | 0.025345 | 63.3653 | -0.001436 | 63.1344 | 62.3363 | 61.9678 | 61.9781 | 62.0017 | 62.0586 | 62.0391 | 62.0831 | 122.9915 | 63.4978 | 122.9274 | 63.2253 | 63.2974 | 126.6374 | 63.2707 | 126.4065 | 59.6941 | 59.7209 | 59.63 | 59.6568
1559.8906 | 123.1979 | -63.3453 | 59.6466 | -0.95865 | -1.3043 | -1.3077 | -1.2795 | -1.2181 | -1.2422 | -1.2027 | 59.6416 | 0.22116 | 59.5684 | -0.03768 | 0.025345 | 63.434 | 0.003143 | 63.2122 | 62.3867 | 62.0411 | 62.0376 | 62.0658 | 62.1272 | 62.1032 | 62.1427 | 122.9869 | 63.5665 | 122.9137 | 63.3077 | 63.3707 | 126.7793 | 63.3485 | 126.5576 | 59.6163 | 59.6385 | 59.543 | 59.5652
1560.8906 | 123.1979 | -63.3865 | 59.5642 | -1.0502 | -1.4325 | -1.4268 | -1.3986 | -1.3417 | -1.3658 | -1.3126 | 59.5775 | 0.22574 | 59.5134 | -0.046838 | 0.025345 | 63.4935 | 0.003143 | 63.2626 | 62.3363 | 61.9541 | 61.9597 | 61.988 | 62.0448 | 62.0208 | 62.074 | 122.964 | 63.6123 | 122.9 | 63.3397 | 63.4119 | 126.8801 | 63.3897 | 126.6491 | 59.5522 | 59.5744 | 59.4881 | 59.5103
1561.8906 | 123.2574 | -63.4644 | 59.5047 | -1.0777 | -1.4508 | -1.4497 | -1.4169 | -1.3509 | -1.3795 | -1.3354 | 59.5088 | 0.22574 | 59.4539 | -0.046838 | 0.029923 | 63.5576 | -0.001436 | 63.345 | 62.3867 | 62.0136 | 62.0147 | 62.0475 | 62.1135 | 62.0849 | 62.1289 | 122.9732 | 63.6901 | 122.9183 | 63.4175 | 63.4943 | 127.022 | 63.4629 | 126.8094 | 59.4789 | 59.5103 | 59.424 | 59.4553
1562.8906 | 123.2391 | -63.4827 | 59.4772 | -1.0914 | -1.4645 | -1.4588 | -1.4352 | -1.3829 | -1.4116 | -1.3492 | 59.4722 | 0.22116 | 59.399 | -0.055996 | 0.025345 | 63.5988 | -0.006014 | 63.3862 | 62.3912 | 62.0181 | 62.0238 | 62.0475 | 62.0998 | 62.0711 | 62.1335 | 122.9549 | 63.7038 | 122.8816 | 63.4267 | 63.508 | 127.0815 | 63.4767 | 126.8689 | 59.4469 | 59.4782 | 59.3736 | 59.405
1563.8906 | 123.2849 | -63.4644 | 59.5276 | -1.0914 | -1.46 | -1.4451 | -1.4169 | -1.36 | -1.3841 | -1.3354 | 59.518 | 0.22116 | 59.4585 | -0.042259 | 0.025345 | 63.5576 | -0.001436 | 63.3359 | 62.3729 | 62.0044 | 62.0193 | 62.0475 | 62.1043 | 62.0803 | 62.1289 | 122.9823 | 63.6855 | 122.9228 | 63.4221 | 63.4897 | 127.022 | 63.4629 | 126.8002 | 59.4926 | 59.5194 | 59.4331 | 59.4599
1564.8906 | 123.2574 | -63.4781 | 59.491 | -1.1189 | -1.4828 | -1.4726 | -1.4535 | -1.3875 | -1.4161 | -1.3721 | 59.4768 | 0.23032 | 59.4081 | -0.03768 | 0.034501 | 63.6034 | 0.003143 | 63.3771 | 62.3592 | 61.9952 | 62.0055 | 62.0246 | 62.0906 | 62.062 | 62.106 | 122.9549 | 63.7084 | 122.8862 | 63.4404 | 63.5126 | 127.0815 | 63.4812 | 126.8551 | 59.4423 | 59.4736 | 59.3736 | 59.405
1565.8906 | 123.3444 | -63.5651 | 59.3857 | -1.1921 | -1.5698 | -1.5596 | -1.5313 | -1.4699 | -1.5077 | -1.4499 | 59.3623 | 0.22116 | 59.2982 | -0.03768 | 0.034501 | 63.7133 | 0.003143 | 63.4915 | 62.3729 | 61.9952 | 62.0055 | 62.0337 | 62.0952 | 62.0574 | 62.1152 | 122.9274 | 63.7862 | 122.8633 | 63.5274 | 63.5996 | 127.2783 | 63.5682 | 127.0566 | 59.3278 | 59.3592 | 59.2637 | 59.2951
1566.8906 | 123.262 | -63.62 | 59.3399 | -1.2013 | -1.579 | -1.5641 | -1.5405 | -1.4745 | -1.5031 | -1.4545 | 59.3257 | 0.22574 | 59.2525 | -0.042259 | 0.029923 | 63.7545 | -0.006014 | 63.5327 | 62.4187 | 62.041 | 62.0558 | 62.0795 | 62.1455 | 62.1169 | 62.1655 | 122.9457 | 63.8457 | 122.8725 | 63.5777 | 63.6499 | 127.3745 | 63.614 | 127.1527 | 59.2958 | 59.3317 | 59.2225 | 59.2585
1567.8906 | 123.2849 | -63.6703 | 59.3033 | -1.2196 | -1.6065 | -1.5916 | -1.5588 | -1.5019 | -1.526 | -1.4865 | 59.2707 | 0.21658 | 59.2067 | -0.046838 | 0.034501 | 63.7957 | 0.003143 | 63.5877 | 62.4507 | 62.0639 | 62.0787 | 62.1115 | 62.1684 | 62.1443 | 62.1838 | 122.9411 | 63.8869 | 122.877 | 63.6235 | 63.7049 | 127.466 | 63.6735 | 127.258 | 59.2362 | 59.2676 | 59.1722 | 59.2035
1568.8906 | 123.2483 | -63.6658 | 59.3262 | -1.2059 | -1.5653 | -1.555 | -1.5268 | -1.4699 | -1.494 | -1.4453 | 59.3165 | 0.21658 | 59.2433 | -0.042259 | 0.029923 | 63.7682 | 0.007721 | 63.5465 | 62.4599 | 62.1005 | 62.1108 | 62.139 | 62.1959 | 62.1718 | 62.2204 | 122.9823 | 63.8824 | 122.9091 | 63.6235 | 63.6957 | 127.434 | 63.6735 | 127.2122 | 59.2866 | 59.3088 | 59.2134 | 59.2356
1569.8906 | 123.175 | -63.739 | 59.2484 | -1.2196 | -1.5882 | -1.5687 | -1.5313 | -1.4882 | -1.5077 | -1.4682 | 59.2204 | 0.22574 | 59.1609 | -0.046838 | 0.029923 | 63.8506 | -0.001436 | 63.6243 | 62.5194 | 62.1509 | 62.1703 | 62.2077 | 62.2508 | 62.2313 | 62.2708 | 122.9594 | 63.9648 | 122.8999 | 63.6922 | 63.7689 | 127.5896 | 63.7376 | 127.3633 | 59.1905 | 59.2218 | 59.131 | 59.1623
1570.8906 | 123.2254 | -63.8443 | 59.1431 | -1.2196 | -1.5698 | -1.555 | -1.5222 | -1.4699 | -1.494 | -1.4407 | 59.1242 | 0.21658 | 59.0556 | -0.046838 | 0.025345 | 63.9422 | -0.001436 | 63.7296 | 62.6247 | 62.2745 | 62.2893 | 62.3221 | 62.3744 | 62.3503 | 62.4036 | 122.9685 | 64.0609 | 122.8999 | 63.7975 | 63.8696 | 127.7865 | 63.8429 | 127.5739 | 59.0989 | 59.1257 | 59.0303 | 59.057
1571.8906 | 123.1476 | -63.9359 | 59.111 | -1.2334 | -1.5882 | -1.5825 | -1.5359 | -1.4836 | -1.5077 | -1.4728 | 59.0601 | 0.21658 | 58.9869 | -0.042259 | 0.029923 | 64.02 | -0.001436 | 63.8028 | 62.7025 | 62.3477 | 62.3534 | 62.3999 | 62.4522 | 62.4282 | 62.4631 | 122.996 | 64.1524 | 122.9228 | 63.8936 | 63.9658 | 127.9559 | 63.9344 | 127.7387 | 59.0302 | 59.0616 | 58.957 | 58.9884
1572.8906 | 123.1796 | -63.9725 | 59.0561 | -1.2929 | -1.6431 | -1.6328 | -1.5954 | -1.5386 | -1.5764 | -1.514 | 58.996 | 0.21658 | 58.9411 | -0.046838 | 0.029923 | 64.0749 | -0.001436 | 63.8532 | 62.6796 | 62.3294 | 62.3396 | 62.377 | 62.4339 | 62.3961 | 62.4585 | 122.9685 | 64.1891 | 122.9136 | 63.9256 | 64.0024 | 128.0474 | 63.971 | 127.8257 | 58.9661 | 58.9975 | 58.9112 | 58.9426
1573.8906 | 123.1934 | -64.0091 | 59.0057 | -1.5126 | -1.9041 | -1.8892 | -1.8656 | -1.7995 | -1.8373 | -1.7887 | 58.9777 | 0.22116 | 58.9045 | -0.046838 | 0.029923 | 64.0978 | -0.001436 | 63.8807 | 62.4965 | 62.105 | 62.1199 | 62.1435 | 62.2096 | 62.1718 | 62.2204 | 122.9868 | 64.2303 | 122.9136 | 63.9623 | 64.039 | 128.1069 | 64.0077 | 127.8898 | 58.9478 | 58.9792 | 58.8746 | 58.906
1574.8906 | 123.1888 | -64.0457 | 58.9554 | -1.5264 | -1.9087 | -1.9075 | -1.8656 | -1.8178 | -1.8419 | -1.7933 | 58.9319 | 0.22116 | 58.8587 | -0.042259 | 0.034501 | 64.1482 | -0.001436 | 63.931 | 62.5193 | 62.137 | 62.1382 | 62.1801 | 62.2279 | 62.2038 | 62.2524 | 122.9777 | 64.2669 | 122.9044 | 64.0035 | 64.0802 | 128.1939 | 64.0443 | 127.9767 | 58.8974 | 58.9334 | 58.8242 | 58.8602
1575.8906 | 123.2071 | -64.0823 | 58.8821 | -1.5584 | -1.9499 | -1.9442 | -1.9068 | -1.8453 | -1.874 | -1.8299 | 58.8816 | 0.22574 | 58.813 | -0.042259 | 0.016188 | 64.194 | -0.006014 | 63.9768 | 62.5239 | 62.1324 | 62.1382 | 62.1756 | 62.2371 | 62.2084 | 62.2524 | 122.9639 | 64.3081 | 122.8953 | 64.0401 | 64.0985 | 128.2763 | 64.0763 | 128.0591 | 58.8654 | 58.8876 | 58.7968 | 58.819
1576.8906 | 123.1888 | -64.1556 | 58.8409 | -1.563 | -1.9453 | -1.9442 | -1.8976 | -1.8361 | -1.874 | -1.8299 | 58.8221 | 0.22574 | 58.758 | -0.046838 | 0.029923 | 64.2581 | -0.006014 | 64.0455 | 62.5926 | 62.2103 | 62.2114 | 62.258 | 62.3195 | 62.2816 | 62.3257 | 122.9776 | 64.3813 | 122.9136 | 64.1087 | 64.1855 | 128.4136 | 64.1496 | 128.2011 | 58.7921 | 58.8281 | 58.7281 | 58.764
1577.8906 | 123.1842 | -64.2426 | 58.786 | -1.6134 | -1.9957 | -1.9854 | -1.9434 | -1.8956 | -1.9152 | -1.8757 | 58.7717 | 0.22116 | 58.6985 | -0.042259 | 0.029923 | 64.3038 | -0.001436 | 64.0958 | 62.6292 | 62.2469 | 62.2572 | 62.2991 | 62.3469 | 62.3274 | 62.3669 | 123.0142 | 64.4637 | 122.941 | 64.2003 | 64.2725 | 128.5464 | 64.2411 | 128.3384 | 58.7418 | 58.7731 | 58.6686 | 58.6999
1578.8906 | 123.1659 | -64.2883 | 58.7448 | -1.6134 | -1.9865 | -1.99 | -1.9526 | -1.8819 | -1.9152 | -1.8665 | 58.7122 | 0.22574 | 58.6436 | -0.042259 | 0.025345 | 64.3634 | -0.006014 | 64.1462 | 62.675 | 62.3018 | 62.2984 | 62.3358 | 62.4064 | 62.3732 | 62.4218 | 123.0005 | 64.5141 | 122.9319 | 64.2461 | 64.3137 | 128.6517 | 64.2823 | 128.4345 | 58.6868 | 58.7182 | 58.6182 | 58.6496
1579.8906 | 123.1201 | -64.3616 | 58.6716 | -1.4577 | -1.7851 | -1.7793 | -1.742 | -1.6805 | -1.7046 | -1.6605 | 58.6481 | 0.22116 | 58.5795 | -0.046838 | 0.025345 | 64.432 | 0.003143 | 64.2103 | 62.9039 | 62.5765 | 62.5822 | 62.6196 | 62.6811 | 62.657 | 62.7011 | 123.0096 | 64.5827 | 122.941 | 64.3147 | 64.3869 | 128.7936 | 64.3647 | 128.5719 | 58.6227 | 58.6449 | 58.5541 | 58.5763
1580.8906 | 123.2758 | -64.357 | 58.5709 | -1.4485 | -1.7713 | -1.7702 | -1.7328 | -1.6667 | -1.6863 | -1.6468 | 58.5977 | 0.22574 | 58.5245 | -0.046838 | 0.020767 | 64.487 | 0.003143 | 64.279 | 62.9085 | 62.5857 | 62.5868 | 62.6242 | 62.6903 | 62.6707 | 62.7102 | 122.9547 | 64.5827 | 122.8815 | 64.3102 | 64.3778 | 128.844 | 64.3601 | 128.636 | 58.5769 | 58.5946 | 58.5038 | 58.5214
1581.8906 | 123.1384 | -64.4531 | 58.5663 | -1.4485 | -1.7759 | -1.761 | -1.7328 | -1.6622 | -1.6863 | -1.6468 | 58.5657 | 0.22116 | 58.4879 | -0.03768 | 0.020767 | 64.519 | -0.006014 | 64.2973 | 63.0046 | 62.6772 | 62.6921 | 62.7203 | 62.791 | 62.7669 | 62.8064 | 123.0188 | 64.6743 | 122.941 | 64.4154 | 64.4739 | 128.9721 | 64.4471 | 128.7504 | 58.5449 | 58.5717 | 58.4671 | 58.4939
1582.8906 | 123.2162 | -64.4669 | 58.5251 | -1.4714 | -1.7851 | -1.7748 | -1.7328 | -1.6667 | -1.6908 | -1.6468 | 58.5153 | 0.21658 | 58.4513 | -0.046838 | 0.029923 | 64.5694 | -0.001436 | 64.3431 | 62.9954 | 62.6818 | 62.6921 | 62.7341 | 62.8001 | 62.776 | 62.8201 | 122.9822 | 64.6834 | 122.9181 | 64.42 | 64.4968 | 129.0362 | 64.4654 | 128.8099 | 58.4854 | 58.5167 | 58.4213 | 58.4527
1583.8906 | 123.1796 | -64.5264 | 58.4381 | -1.5126 | -1.8217 | -1.816 | -1.7694 | -1.7079 | -1.7412 | -1.7063 | 58.4695 | 0.22116 | 58.3963 | -0.051417 | 0.016188 | 64.606 | -0.001436 | 64.3888 | 63.0137 | 62.7047 | 62.7104 | 62.7569 | 62.8184 | 62.7852 | 62.8201 | 122.9959 | 64.7475 | 122.9227 | 64.4749 | 64.5426 | 129.1324 | 64.5249 | 128.9152 | 58.4533 | 58.4709 | 58.3801 | 58.3978
1584.8906 | 123.2574 | -64.5905 | 58.3557 | -1.5401 | -1.8492 | -1.8389 | -1.7923 | -1.7354 | -1.7595 | -1.7292 | 58.3779 | 0.22574 | 58.3139 | -0.046838 | 0.025345 | 64.693 | -0.006014 | 64.4804 | 63.0503 | 62.7413 | 62.7516 | 62.7981 | 62.855 | 62.8309 | 62.8613 | 122.9684 | 64.8162 | 122.9044 | 64.5436 | 64.6158 | 129.2834 | 64.5844 | 129.0709 | 58.3526 | 58.384 | 58.2886 | 58.3199
1585.8906 | 123.1979 | -64.65 | 58.3008 | -1.5767 | -1.8904 | -1.8801 | -1.8335 | -1.772 | -1.8099 | -1.7704 | 58.3184 | 0.22116 | 58.2498 | -0.042259 | 0.025345 | 64.7525 | -0.001436 | 64.5308 | 63.0732 | 62.7596 | 62.7699 | 62.8164 | 62.8779 | 62.8401 | 62.8796 | 122.9684 | 64.8711 | 122.8998 | 64.6077 | 64.6753 | 129.4025 | 64.6485 | 129.1807 | 58.2931 | 58.3199 | 58.2245 | 58.2513
1586.8906 | 123.2712 | -64.6866 | 58.287 | -1.6362 | -1.9499 | -1.9396 | -1.893 | -1.8315 | -1.8557 | -1.8253 | 58.2909 | 0.22116 | 58.2132 | -0.051417 | 0.029923 | 64.78 | -0.001436 | 64.5628 | 63.0503 | 62.7367 | 62.747 | 62.7935 | 62.855 | 62.8309 | 62.8613 | 122.9775 | 64.9077 | 122.8998 | 64.6352 | 64.7165 | 129.4665 | 64.6851 | 129.2494 | 58.261 | 58.2924 | 58.1833 | 58.2146
1587.8906 | 123.2712 | -64.7095 | 58.223 | -1.6179 | -1.9178 | -1.903 | -1.8564 | -1.7903 | -1.8282 | -1.7933 | 58.2497 | 0.22116 | 58.1811 | -0.051417 | 0.025345 | 64.812 | 0.003143 | 64.604 | 63.0915 | 62.7916 | 62.8065 | 62.8531 | 62.9191 | 62.8813 | 62.9162 | 122.9592 | 64.9306 | 122.8906 | 64.6581 | 64.7348 | 129.5215 | 64.7126 | 129.3135 | 58.2244 | 58.2466 | 58.1558 | 58.178
1588.8906 | 123.2529 | -64.7415 | 58.1589 | -1.7324 | -2.046 | -2.0403 | -1.9892 | -1.9185 | -1.961 | -1.9169 | 58.2268 | 0.23032 | 58.1537 | -0.046838 | 0.029923 | 64.8578 | -0.001436 | 64.6315 | 63.0091 | 62.6955 | 62.7012 | 62.7523 | 62.823 | 62.7806 | 62.8246 | 122.9684 | 64.9718 | 122.8952 | 64.6947 | 64.7714 | 129.5993 | 64.7401 | 129.373 | 58.1969 | 58.2283 | 58.1238 | 58.1551
1589.8906 | 123.2437 | -64.8193 | 58.1314 | -1.9247 | -2.2567 | -2.2464 | -2.1906 | -2.1291 | -2.1578 | -2.1275 | 58.149 | 0.22574 | 58.0896 | -0.042259 | 0.025345 | 64.9173 | -0.001436 | 64.6956 | 62.8946 | 62.5627 | 62.573 | 62.6287 | 62.6902 | 62.6615 | 62.6919 | 122.9683 | 65.0451 | 122.9089 | 64.7771 | 64.8447 | 129.7366 | 64.8179 | 129.5149 | 58.1237 | 58.1504 | 58.0642 | 58.091
1590.8906 | 123.1979 | -64.888 | 58.0719 | -1.943 | -2.2704 | -2.2509 | -2.2044 | -2.1474 | -2.1761 | -2.1412 | 58.0758 | 0.22116 | 58.0072 | -0.046838 | 0.025345 | 64.9906 | -0.001436 | 64.7642 | 62.945 | 62.6176 | 62.6371 | 62.6836 | 62.7406 | 62.7119 | 62.7468 | 122.9638 | 65.1092 | 122.8952 | 64.8412 | 64.9133 | 129.8786 | 64.8866 | 129.6522 | 58.0504 | 58.0772 | 57.9818 | 58.0086
1591.8906 | 123.2529 | -64.9384 | 58.049 | -1.9293 | -2.2475 | -2.2326 | -2.1861 | -2.1154 | -2.1487 | -2.1092 | 58.0391 | 0.22574 | 57.966 | -0.051417 | 0.025345 | 65.0409 | -0.001436 | 64.81 | 63.0091 | 62.6908 | 62.7057 | 62.7523 | 62.823 | 62.7897 | 62.8292 | 122.9775 | 65.1641 | 122.9043 | 64.8869 | 64.9637 | 129.9793 | 64.9369 | 129.7484 | 58.0138 | 58.0406 | 57.9406 | 57.9674
1592.8906 | 123.1979 | -64.9796 | 58.0261 | -2.03 | -2.3574 | -2.3517 | -2.296 | -2.2298 | -2.2677 | -2.2282 | 58.0254 | 0.22574 | 57.9568 | -0.042259 | 0.020767 | 65.0501 | 0.003143 | 64.8375 | 62.9496 | 62.6222 | 62.6279 | 62.6836 | 62.7497 | 62.7118 | 62.7514 | 123.0049 | 65.2053 | 122.9364 | 64.9373 | 65.0003 | 130.0296 | 64.9827 | 129.817 | 58.0046 | 58.0223 | 57.936 | 57.9537
1593.8906 | 123.2346 | -65.0024 | 57.9758 | -2.0758 | -2.3986 | -2.3929 | -2.3326 | -2.2664 | -2.3043 | -2.2694 | 57.9842 | 0.21658 | 57.9202 | -0.051417 | 0.034501 | 65.0913 | -0.001436 | 64.8695 | 62.9267 | 62.6038 | 62.6096 | 62.6699 | 62.736 | 62.6981 | 62.733 | 122.9866 | 65.219 | 122.9226 | 64.951 | 65.0369 | 130.0937 | 65.001 | 129.872 | 57.9497 | 57.9856 | 57.8857 | 57.9216
1594.8906 | 123.262 | -64.9292 | 58.049 | -2.1216 | -2.4444 | -2.4341 | -2.3829 | -2.3122 | -2.3501 | -2.3198 | 58.062 | 0.22116 | 57.9889 | -0.042259 | 0.025345 | 65.0272 | 0.007721 | 64.8009 | 62.8076 | 62.4848 | 62.4951 | 62.5463 | 62.617 | 62.5791 | 62.6094 | 122.9912 | 65.1504 | 122.9181 | 64.8869 | 64.9545 | 129.9564 | 64.9369 | 129.7301 | 58.0367 | 58.0543 | 57.9635 | 57.9811
1595.8906 | 123.1934 | -65.062 | 57.9025 | -2.1353 | -2.4444 | -2.4341 | -2.3738 | -2.3077 | -2.341 | -2.306 | 57.9247 | 0.22574 | 57.8561 | -0.042259 | 0.029923 | 65.1416 | -0.001436 | 64.9245 | 62.9267 | 62.6176 | 62.6279 | 62.6882 | 62.7543 | 62.721 | 62.7559 | 122.9866 | 65.2877 | 122.918 | 65.0197 | 65.0919 | 130.2036 | 65.0605 | 129.9864 | 57.8947 | 57.9261 | 57.8262 | 57.8575
1596.8906 | 123.2803 | -65.1901 | 57.7698 | -2.1628 | -2.4719 | -2.4524 | -2.3921 | -2.3214 | -2.373 | -2.3335 | 57.7644 | 0.22574 | 57.7004 | -0.03768 | 0.029923 | 65.3064 | 0.003143 | 65.0893 | 63.0274 | 62.7183 | 62.7377 | 62.798 | 62.8687 | 62.8171 | 62.8566 | 122.9545 | 65.4159 | 122.8906 | 65.1524 | 65.22 | 130.4966 | 65.1933 | 130.2794 | 57.7345 | 57.7613 | 57.6705 | 57.6973
1597.8906 | 123.2758 | -65.2084 | 57.7332 | -2.1673 | -2.481 | -2.4661 | -2.4013 | -2.3397 | -2.373 | -2.3335 | 57.7278 | 0.22574 | 57.6684 | -0.046838 | 0.029923 | 65.3385 | -0.001436 | 65.1259 | 63.0411 | 62.7274 | 62.7423 | 62.8072 | 62.8687 | 62.8354 | 62.8749 | 122.9362 | 65.4342 | 122.8768 | 65.1616 | 65.2384 | 130.5469 | 65.207 | 130.3344 | 57.6979 | 57.7292 | 57.6385 | 57.6698
1598.8906 | 123.2986 | -65.2679 | 57.6645 | -2.1765 | -2.481 | -2.4707 | -2.415 | -2.3351 | -2.3822 | -2.3426 | 57.6728 | 0.22116 | 57.6134 | -0.03768 | 0.025345 | 65.3934 | -0.001436 | 65.1717 | 63.0914 | 62.7869 | 62.7972 | 62.853 | 62.9328 | 62.8858 | 62.9253 | 122.9408 | 65.4891 | 122.8814 | 65.2303 | 65.2933 | 130.6614 | 65.2665 | 130.4396 | 57.6475 | 57.6743 | 57.5881 | 57.6149
1599.8906 | 123.2346 | -65.3961 | 57.5546 | -2.1307 | -2.4215 | -2.402 | -2.3463 | -2.2756 | -2.3089 | -2.2786 | 57.563 | 0.22574 | 57.4944 | -0.042259 | 0.029923 | 65.5033 | 0.003143 | 65.2907 | 63.2654 | 62.9746 | 62.9941 | 63.0498 | 63.1205 | 63.0872 | 63.1176 | 122.9591 | 65.6219 | 122.8905 | 65.3539 | 65.426 | 130.8994 | 65.3993 | 130.6869 | 57.533 | 57.5598 | 57.4645 | 57.4913
1600.8906 | 123.2437 | -65.4831 | 57.5089 | -2.0437 | -2.3299 | -2.3059 | -2.2502 | -2.1703 | -2.2036 | -2.1824 | 57.4851 | 0.22574 | 57.4074 | -0.03768 | 0.029923 | 65.5903 | 0.003143 | 65.3777 | 63.4394 | 63.1532 | 63.1772 | 63.2329 | 63.3128 | 63.2795 | 63.3007 | 122.9682 | 65.7088 | 122.8905 | 65.4454 | 65.513 | 131.0734 | 65.4862 | 130.8608 | 57.4552 | 57.482 | 57.3775 | 57.4043
1601.8906 | 123.2803 | -65.4922 | 57.4265 | -2.1124 | -2.4032 | -2.3791 | -2.3188 | -2.2481 | -2.2723 | -2.2511 | 57.4531 | 0.21658 | 57.3754 | -0.046838 | 0.039079 | 65.6269 | 0.003143 | 65.4052 | 63.3798 | 63.0891 | 63.1131 | 63.1734 | 63.2441 | 63.22 | 63.2412 | 122.9453 | 65.7088 | 122.8676 | 65.4454 | 65.5313 | 131.1192 | 65.4954 | 130.8974 | 57.414 | 57.4499 | 57.3363 | 57.3722
1602.8906 | 123.2254 | -65.5838 | 57.399 | -2.0712 | -2.3482 | -2.3288 | -2.2685 | -2.1932 | -2.2219 | -2.2007 | 57.3752 | 0.22574 | 57.3113 | -0.03768 | 0.029923 | 65.7002 | -0.006014 | 65.4784 | 63.5126 | 63.2356 | 63.255 | 63.3153 | 63.3906 | 63.3619 | 63.3831 | 122.959 | 65.8095 | 122.8951 | 65.5461 | 65.6137 | 131.284 | 65.5778 | 131.0622 | 57.3453 | 57.3813 | 57.2814 | 57.3173
1603.8906 | 123.1522 | -65.6525 | 57.3944 | -2.1628 | -2.4352 | -2.4341 | -2.36 | -2.2802 | -2.3226 | -2.2923 | 57.3295 | 0.22574 | 57.2563 | -0.046838 | 0.039079 | 65.7459 | -0.006014 | 65.5196 | 63.4897 | 63.2172 | 63.2184 | 63.2924 | 63.3723 | 63.3298 | 63.3602 | 122.9819 | 65.8782 | 122.9088 | 65.6056 | 65.6915 | 131.3984 | 65.6465 | 131.1721 | 57.2904 | 57.3355 | 57.2173 | 57.2623
1604.8906 | 123.1476 | -65.7394 | 57.3212 | -2.1032 | -2.3666 | -2.3471 | -2.2914 | -2.2024 | -2.2402 | -2.2145 | 57.2471 | 0.22116 | 57.1739 | -0.042259 | 0.025345 | 65.8329 | -0.001436 | 65.6066 | 63.6362 | 63.3729 | 63.3924 | 63.4481 | 63.5371 | 63.4992 | 63.525 | 122.9865 | 65.9606 | 122.9134 | 65.6972 | 65.7648 | 131.5724 | 65.738 | 131.3461 | 57.2217 | 57.2485 | 57.1486 | 57.1754
1605.8906 | 123.175 | -65.7898 | 57.2388 | -2.0346 | -2.2933 | -2.2601 | -2.2044 | -2.1245 | -2.1624 | -2.1458 | 57.1784 | 0.23032 | 57.0961 | -0.042259 | 0.029923 | 65.9016 | -0.001436 | 65.6845 | 63.7552 | 63.4965 | 63.5297 | 63.5854 | 63.6653 | 63.6274 | 63.644 | 122.9682 | 66.0201 | 122.8859 | 65.7475 | 65.8197 | 131.6914 | 65.7884 | 131.4743 | 57.1484 | 57.1798 | 57.0662 | 57.0975
1606.8906 | 123.1247 | -65.8768 | 57.1655 | -1.9201 | -2.1742 | -2.1548 | -2.0945 | -2.0055 | -2.0388 | -2.0176 | 57.1189 | 0.20742 | 57.0595 | -0.042259 | 0.025345 | 65.9519 | 0.007721 | 65.7348 | 63.9567 | 63.7025 | 63.722 | 63.7823 | 63.8713 | 63.838 | 63.8592 | 122.9956 | 66.0842 | 122.9362 | 65.8345 | 65.9021 | 131.8287 | 65.8845 | 131.6116 | 57.0935 | 57.1111 | 57.0341 | 57.0517
1607.8906 | 123.1979 | -65.9134 | 57.106 | -1.9613 | -2.1971 | -2.1868 | -2.122 | -2.0467 | -2.0663 | -2.0451 | 57.0822 | 0.22116 | 57.0091 | -0.042259 | 0.034501 | 65.9931 | -0.010593 | 65.7806 | 63.9521 | 63.7162 | 63.7266 | 63.7914 | 63.8667 | 63.8471 | 63.8683 | 122.9956 | 66.1346 | 122.9225 | 65.8711 | 65.9479 | 131.9065 | 65.9028 | 131.694 | 57.0477 | 57.0928 | 56.9746 | 57.0197
1608.8906 | 123.1842 | -65.95 | 57.0602 | -1.9659 | -2.2017 | -2.1914 | -2.1174 | -2.033 | -2.0663 | -2.0542 | 57.0181 | 0.23032 | 56.9542 | -0.046838 | 0.029923 | 66.0527 | 0.003143 | 65.8355 | 63.9841 | 63.7483 | 63.7586 | 63.8326 | 63.917 | 63.8838 | 63.8958 | 122.9681 | 66.1803 | 122.9042 | 65.9032 | 65.9799 | 132.0027 | 65.9532 | 131.7855 | 56.9882 | 57.015 | 56.9242 | 56.951
1609.8906 | 123.175 | -65.9592 | 57.0557 | -2.0437 | -2.2796 | -2.2601 | -2.1861 | -2.1062 | -2.1395 | -2.1275 | 57.0044 | 0.21658 | 56.9359 | -0.051417 | 0.029923 | 66.0618 | -0.001436 | 65.8493 | 63.9154 | 63.6796 | 63.6991 | 63.7731 | 63.8529 | 63.8197 | 63.8317 | 122.9636 | 66.1757 | 122.895 | 65.9077 | 65.9891 | 132.021 | 65.9577 | 131.8084 | 56.9745 | 57.0058 | 56.9059 | 56.9373
1610.8906 | 123.2071 | -66.0507 | 56.955 | -2.0163 | -2.2475 | -2.2235 | -2.1586 | -2.0696 | -2.1075 | -2.0908 | 56.9311 | 0.22116 | 56.858 | -0.042259 | 0.029923 | 66.1488 | -0.001436 | 65.9225 | 64.0345 | 63.8032 | 63.8273 | 63.8921 | 63.9811 | 63.9433 | 63.9599 | 122.9819 | 66.2719 | 122.9087 | 66.0085 | 66.0806 | 132.1995 | 66.0493 | 131.9732 | 56.9012 | 56.9326 | 56.8281 | 56.8595
1611.8906 | 123.1613 | -66.156 | 56.8405 | -2.1307 | -2.3528 | -2.3425 | -2.2776 | -2.1886 | -2.2219 | -2.2007 | 56.8167 | 0.22574 | 56.7573 | -0.046838 | 0.025345 | 66.2495 | 0.007721 | 66.0324 | 64.0253 | 63.8032 | 63.8135 | 63.8784 | 63.9674 | 63.9341 | 63.9553 | 122.9727 | 66.3817 | 122.9133 | 66.1092 | 66.1814 | 132.4055 | 66.1637 | 132.1884 | 56.7913 | 56.809 | 56.732 | 56.7496
1612.8906 | 123.1796 | -66.2292 | 56.7902 | -2.3596 | -2.6001 | -2.5852 | -2.5157 | -2.4313 | -2.4737 | -2.4479 | 56.748 | 0.21658 | 56.6703 | -0.042259 | 0.034501 | 66.3182 | 0.003143 | 66.1011 | 63.8696 | 63.6292 | 63.6441 | 63.7135 | 63.798 | 63.7555 | 63.7813 | 122.9772 | 66.4458 | 122.8996 | 66.187 | 66.2637 | 132.5474 | 66.2324 | 132.3303 | 56.7135 | 56.7449 | 56.6358 | 56.6672
1613.8906 | 123.1338 | -66.2521 | 56.7307 | -2.3093 | -2.5406 | -2.5211 | -2.4608 | -2.3672 | -2.4051 | -2.3793 | 56.7159 | 0.22574 | 56.652 | -0.051417 | 0.029923 | 66.3457 | 0.003143 | 66.1285 | 63.9429 | 63.7116 | 63.7311 | 63.7914 | 63.885 | 63.8471 | 63.8729 | 122.9681 | 66.4779 | 122.9041 | 66.2007 | 66.2821 | 132.5978 | 66.2553 | 132.3807 | 56.686 | 56.7128 | 56.6221 | 56.6489
1614.8906 | 123.143 | -66.394 | 56.5842 | -2.3093 | -2.536 | -2.5211 | -2.447 | -2.3626 | -2.4051 | -2.3747 | 56.6015 | 0.22574 | 56.5421 | -0.046838 | 0.029923 | 66.4601 | -0.006014 | 66.243 | 64.0848 | 63.8581 | 63.873 | 63.947 | 64.0315 | 63.989 | 64.0193 | 122.9955 | 66.6198 | 122.9362 | 66.3472 | 66.424 | 132.8542 | 66.388 | 132.637 | 56.5716 | 56.6075 | 56.5122 | 56.5481
1615.8906 | 123.1476 | -66.5039 | 56.5247 | -2.3093 | -2.536 | -2.5073 | -2.447 | -2.358 | -2.3959 | -2.3747 | 56.5053 | 0.22574 | 56.4277 | -0.051417 | 0.029923 | 66.5654 | -0.001436 | 66.3437 | 64.1946 | 63.9679 | 63.9966 | 64.0569 | 64.1459 | 64.108 | 64.1292 | 123.0092 | 66.7296 | 122.9316 | 66.4525 | 66.5338 | 133.0693 | 66.5025 | 132.8476 | 56.4754 | 56.5068 | 56.3977 | 56.4291
1616.8906 | 123.1522 | -66.4764 | 56.5521 | -2.2223 | -2.4352 | -2.4203 | -2.3372 | -2.2619 | -2.2952 | -2.274 | 56.5145 | 0.22574 | 56.4368 | -0.046838 | 0.029923 | 66.5563 | -0.006014 | 66.3254 | 64.2542 | 64.0412 | 64.0561 | 64.1393 | 64.2146 | 64.1813 | 64.2025 | 122.9909 | 66.7022 | 122.9133 | 66.4296 | 66.5064 | 133.0327 | 66.4704 | 132.8018 | 56.4846 | 56.5205 | 56.4069 | 56.4428
1617.8906 | 123.1567 | -66.5543 | 56.4194 | -2.1765 | -2.3895 | -2.37 | -2.3005 | -2.2207 | -2.2494 | -2.2328 | 56.4275 | 0.22574 | 56.3498 | -0.042259 | 0.034501 | 66.6341 | 0.003143 | 66.4215 | 64.3778 | 64.1648 | 64.1843 | 64.2537 | 64.3336 | 64.3049 | 64.3215 | 122.9818 | 66.78 | 122.9041 | 66.512 | 66.5888 | 133.1883 | 66.5574 | 132.9758 | 56.393 | 56.4244 | 56.3153 | 56.3467
1618.8906 | 123.1705 | -66.655 | 56.3416 | -2.0804 | -2.2933 | -2.2784 | -2.2044 | -2.1154 | -2.1487 | -2.1275 | 56.3542 | 0.22574 | 56.2766 | -0.046838 | 0.034501 | 66.7165 | -0.006014 | 66.4994 | 64.5746 | 64.3617 | 64.3766 | 64.4506 | 64.5396 | 64.5063 | 64.5275 | 123.0092 | 66.8807 | 122.9316 | 66.6081 | 66.6895 | 133.3715 | 66.649 | 133.1543 | 56.3197 | 56.3603 | 56.2421 | 56.2826
1619.8906 | 123.1934 | -66.687 | 56.282 | -2.0437 | -2.2567 | -2.2372 | -2.1678 | -2.0788 | -2.112 | -2.0954 | 56.3039 | 0.21658 | 56.2354 | -0.042259 | 0.025345 | 66.7623 | 0.003143 | 66.5406 | 64.6433 | 64.4303 | 64.4498 | 64.5193 | 64.6083 | 64.575 | 64.5916 | 122.9909 | 66.9036 | 122.9224 | 66.6448 | 66.7124 | 133.4493 | 66.6902 | 133.2276 | 56.2785 | 56.3007 | 56.21 | 56.2322
1620.8906 | 123.23 | -66.7099 | 56.2408 | -1.8652 | -2.0552 | -2.0403 | -1.9663 | -1.8819 | -1.906 | -1.8894 | 56.2489 | 0.22574 | 56.1759 | -0.051417 | 0.020767 | 66.8264 | -0.001436 | 66.6001 | 64.8447 | 64.6547 | 64.6696 | 64.7436 | 64.828 | 64.8039 | 64.8205 | 122.9588 | 66.9356 | 122.8858 | 66.6585 | 66.7307 | 133.5363 | 66.7085 | 133.31 | 56.2282 | 56.2504 | 56.1551 | 56.1773
1621.8906 | 123.262 | -66.7282 | 56.1722 | -1.824 | -2.0048 | -1.99 | -1.9159 | -1.8361 | -1.8557 | -1.839 | 56.2123 | 0.22116 | 56.1347 | -0.042259 | 0.029923 | 66.863 | 0.007721 | 66.6321 | 64.9042 | 64.7234 | 64.7383 | 64.8123 | 64.8921 | 64.8726 | 64.8892 | 122.9405 | 66.9494 | 122.8629 | 66.686 | 66.7581 | 133.5912 | 66.7359 | 133.3604 | 56.1824 | 56.2046 | 56.1047 | 56.1269
1622.8906 | 123.2574 | -66.8793 | 56.0761 | -1.6225 | -1.7988 | -1.7885 | -1.7191 | -1.6255 | -1.6496 | -1.633 | 56.107 | 0.2349 | 56.0385 | -0.046838 | 0.025345 | 66.9591 | -0.006014 | 66.7466 | 65.2568 | 65.0805 | 65.0908 | 65.1602 | 65.2537 | 65.2296 | 65.2462 | 122.9863 | 67.1142 | 122.9178 | 66.8324 | 66.9046 | 133.8384 | 66.8733 | 133.6259 | 56.0817 | 56.113 | 56.0132 | 56.0445
1623.8906 | 123.2803 | -66.9388 | 56.0165 | -1.6042 | -1.7896 | -1.7656 | -1.7007 | -1.6026 | -1.6359 | -1.6239 | 56.0383 | 0.23032 | 55.9836 | -0.046838 | 0.025345 | 67.0232 | -0.001436 | 66.8015 | 65.3346 | 65.1492 | 65.1732 | 65.238 | 65.3361 | 65.3029 | 65.3149 | 122.9771 | 67.1691 | 122.9224 | 66.8919 | 66.9641 | 133.962 | 66.9373 | 133.7403 | 56.013 | 56.0398 | 55.9582 | 55.985
1624.8906 | 123.2346 | -66.9846 | 55.9616 | -1.595 | -1.7622 | -1.7427 | -1.6733 | -1.5843 | -1.6176 | -1.5918 | 55.9742 | 0.22574 | 55.9057 | -0.046838 | 0.029923 | 67.0965 | 0.003143 | 66.8702 | 65.3895 | 65.2224 | 65.2418 | 65.3113 | 65.4002 | 65.367 | 65.3927 | 122.9588 | 67.2103 | 122.8903 | 66.9377 | 67.0145 | 134.081 | 66.9877 | 133.8548 | 55.9443 | 55.9711 | 55.8758 | 55.9026
1625.8906 | 123.2162 | -67.012 | 55.9341 | -1.5676 | -1.7438 | -1.7198 | -1.6458 | -1.5569 | -1.581 | -1.5598 | 55.9513 | 0.22116 | 55.8691 | -0.046838 | 0.020767 | 67.1239 | 0.003143 | 66.8977 | 65.4445 | 65.2682 | 65.2922 | 65.3662 | 65.4552 | 65.4311 | 65.4522 | 122.9634 | 67.2332 | 122.8811 | 66.9652 | 67.0328 | 134.136 | 67.0152 | 133.9097 | 55.9306 | 55.9482 | 55.8483 | 55.866
1626.8906 | 123.2208 | -67.1036 | 55.8334 | -1.6637 | -1.8354 | -1.8114 | -1.7511 | -1.6576 | -1.6817 | -1.6605 | 55.8506 | 0.22574 | 55.7776 | -0.051417 | 0.034501 | 67.2155 | -0.006014 | 66.9938 | 65.4399 | 65.2682 | 65.2922 | 65.3525 | 65.446 | 65.4219 | 65.4431 | 122.9542 | 67.3293 | 122.8811 | 67.0522 | 67.1381 | 134.3191 | 67.0976 | 134.0974 | 55.8161 | 55.8566 | 55.7431 | 55.7836
1627.8906 | 123.2162 | -67.2134 | 55.751 | -1.5447 | -1.7164 | -1.6969 | -1.6229 | -1.5386 | -1.5672 | -1.5323 | 55.7682 | 0.22116 | 55.7043 | -0.042259 | 0.029923 | 67.2979 | -0.001436 | 67.0762 | 65.6688 | 65.4971 | 65.5165 | 65.5905 | 65.6749 | 65.6462 | 65.6811 | 122.9816 | 67.4346 | 122.9177 | 67.1712 | 67.2434 | 134.5113 | 67.212 | 134.2897 | 55.7383 | 55.7696 | 55.6744 | 55.7057
1628.8906 | 123.2025 | -67.2455 | 55.6961 | -1.4577 | -1.6156 | -1.6008 | -1.5359 | -1.4424 | -1.4619 | -1.4453 | 55.7087 | 0.22116 | 55.6448 | -0.042259 | 0.029923 | 67.3574 | -0.001436 | 67.1357 | 65.7878 | 65.6298 | 65.6447 | 65.7096 | 65.8031 | 65.7836 | 65.8002 | 122.9542 | 67.4666 | 122.8903 | 67.2032 | 67.2754 | 134.6029 | 67.244 | 134.3812 | 55.6788 | 55.7101 | 55.6149 | 55.6462
1629.8906 | 123.1934 | -67.3096 | 55.6595 | -1.5081 | -1.6706 | -1.6511 | -1.5817 | -1.4928 | -1.5123 | -1.4911 | 55.6537 | 0.22116 | 55.5853 | -0.042259 | 0.020767 | 67.4078 | -0.001436 | 67.1861 | 65.8015 | 65.639 | 65.6584 | 65.7279 | 65.8168 | 65.7973 | 65.8185 | 122.9633 | 67.5307 | 122.8948 | 67.2673 | 67.3303 | 134.7173 | 67.3081 | 134.4957 | 55.633 | 55.6552 | 55.5645 | 55.5867
1630.8906 | 123.2346 | -67.3737 | 55.5908 | -1.5584 | -1.7164 | -1.6969 | -1.6275 | -1.5523 | -1.5672 | -1.5415 | 55.6034 | 0.22116 | 55.5395 | -0.055996 | 0.029923 | 67.4627 | -0.001436 | 67.2273 | 65.8152 | 65.6573 | 65.6767 | 65.7462 | 65.8214 | 65.8064 | 65.8322 | 122.977 | 67.5948 | 122.9131 | 67.3177 | 67.4036 | 134.8364 | 67.3722 | 134.601 | 55.5734 | 55.6048 | 55.5096 | 55.5409
1631.8906 | 123.2529 | -67.5018 | 55.4626 | -1.65 | -1.8034 | -1.7885 | -1.7145 | -1.6347 | -1.6542 | -1.6376 | 55.466 | 0.22574 | 55.4021 | -0.051417 | 0.029923 | 67.5955 | -0.001436 | 67.3784 | 65.8518 | 65.6985 | 65.7133 | 65.7873 | 65.8671 | 65.8476 | 65.8642 | 122.9678 | 67.7276 | 122.904 | 67.4504 | 67.5318 | 135.0973 | 67.5004 | 134.8802 | 55.4361 | 55.4675 | 55.3722 | 55.4036
1632.8906 | 123.2437 | -67.5613 | 55.3848 | -1.943 | -2.1193 | -2.0998 | -2.0258 | -1.9323 | -1.9655 | -1.9443 | 55.3836 | 0.22116 | 55.3197 | -0.042259 | 0.020767 | 67.6779 | -0.001436 | 67.4471 | 65.6183 | 65.442 | 65.4615 | 65.5355 | 65.6291 | 65.5958 | 65.617 | 122.9449 | 67.7825 | 122.8811 | 67.5191 | 67.5821 | 135.2392 | 67.5599 | 135.0084 | 55.3628 | 55.385 | 55.299 | 55.3212
1633.8906 | 123.2849 | -67.5705 | 55.394 | -2.1261 | -2.2887 | -2.2738 | -2.1998 | -2.1108 | -2.1487 | -2.1183 | 55.3973 | 0.22574 | 55.3151 | -0.042259 | 0.039079 | 67.6687 | 0.003143 | 67.4379 | 65.4444 | 65.2818 | 65.2967 | 65.3707 | 65.4597 | 65.4218 | 65.4522 | 122.9678 | 67.7962 | 122.8856 | 67.5282 | 67.6096 | 135.2392 | 67.5736 | 135.0084 | 55.3583 | 55.3942 | 55.2761 | 55.312
1634.8906 | 123.2574 | -67.6575 | 55.2979 | -2.0895 | -2.2704 | -2.2464 | -2.1723 | -2.0879 | -2.1166 | -2.0908 | 55.3149 | 0.21658 | 55.2373 | -0.046838 | 0.025345 | 67.7465 | -0.001436 | 67.5249 | 65.568 | 65.3871 | 65.4111 | 65.4851 | 65.5696 | 65.5408 | 65.5666 | 122.9724 | 67.8741 | 122.8948 | 67.6106 | 67.6828 | 135.404 | 67.656 | 135.1824 | 55.2896 | 55.3164 | 55.212 | 55.2387
1635.8906 | 123.2574 | -67.6941 | 55.2658 | -2.1399 | -2.3299 | -2.3105 | -2.2227 | -2.1383 | -2.1716 | -2.1549 | 55.2646 | 0.22574 | 55.1824 | -0.055996 | 0.025345 | 67.7969 | -0.001436 | 67.5798 | 65.5542 | 65.3642 | 65.3836 | 65.4714 | 65.5558 | 65.5225 | 65.5391 | 122.9587 | 67.9198 | 122.8765 | 67.6381 | 67.7194 | 135.491 | 67.6927 | 135.2739 | 55.2392 | 55.266 | 55.157 | 55.1838
1636.8906 | 123.2803 | -67.749 | 55.2017 | -2.0529 | -2.2246 | -2.2006 | -2.1311 | -2.0421 | -2.0708 | -2.0451 | 55.1913 | 0.22116 | 55.1183 | -0.046838 | 0.025345 | 67.8656 | -0.001436 | 67.6439 | 65.6961 | 65.5244 | 65.5485 | 65.6179 | 65.7069 | 65.6782 | 65.704 | 122.9403 | 67.9702 | 122.8673 | 67.7022 | 67.7744 | 135.6146 | 67.7476 | 135.3929 | 55.166 | 55.1927 | 55.0929 | 55.1197
1637.8906 | 123.23 | -67.8131 | 55.1559 | -1.9613 | -2.1514 | -2.1182 | -2.0441 | -1.9551 | -1.9701 | -1.9581 | 55.1501 | 0.22116 | 55.0817 | -0.042259 | 0.029923 | 67.9114 | -0.001436 | 67.6943 | 65.8518 | 65.6618 | 65.695 | 65.769 | 65.858 | 65.843 | 65.855 | 122.9632 | 68.0343 | 122.8948 | 67.7709 | 67.843 | 135.7245 | 67.8117 | 135.5074 | 55.1202 | 55.1515 | 55.0517 | 55.0831
1638.8906 | 123.2758 | -67.8726 | 55.0919 | -1.8835 | -2.0644 | -2.0403 | -1.9663 | -1.8819 | -1.8969 | -1.8803 | 55.0723 | 0.22574 | 55.0038 | -0.051417 | 0.029923 | 67.9892 | -0.006014 | 67.7675 | 65.9891 | 65.8083 | 65.8323 | 65.9063 | 65.9907 | 65.9758 | 65.9924 | 122.9449 | 68.0984 | 122.8764 | 67.8212 | 67.9025 | 135.8618 | 67.8666 | 135.6401 | 55.0423 | 55.0783 | 54.9739 | 55.0098
1639.8906 | 123.2254 | -67.923 | 55.0415 | -2.0346 | -2.2109 | -2.1823 | -2.1037 | -2.0238 | -2.0525 | -2.0313 | 55.0265 | 0.22116 | 54.9535 | -0.042259 | 0.029923 | 68.035 | -0.001436 | 67.8133 | 65.8884 | 65.7121 | 65.7407 | 65.8193 | 65.8992 | 65.8704 | 65.8916 | 122.9495 | 68.1441 | 122.8764 | 67.8807 | 67.9529 | 135.9579 | 67.9215 | 135.7363 | 54.9966 | 55.0279 | 54.9235 | 54.9549
1640.8906 | 123.2803 | -67.9596 | 55.0369 | -2.2131 | -2.3986 | -2.3746 | -2.2868 | -2.2115 | -2.2311 | -2.2099 | 54.9899 | 0.22116 | 54.9077 | -0.051417 | 0.029923 | 68.067 | -0.001436 | 67.8454 | 65.7465 | 65.561 | 65.585 | 65.6728 | 65.7481 | 65.7285 | 65.7497 | 122.9494 | 68.1808 | 122.8673 | 67.9082 | 67.9895 | 136.0266 | 67.9582 | 135.8049 | 54.9599 | 54.9913 | 54.8778 | 54.9091
1641.8906 | 123.2117 | -68.0145 | 54.95 | -2.2772 | -2.449 | -2.4249 | -2.3417 | -2.2573 | -2.2814 | -2.2648 | 54.9395 | 0.22116 | 54.8619 | -0.042259 | 0.034501 | 68.1219 | -0.001436 | 67.9095 | 65.7373 | 65.5655 | 65.5896 | 65.6728 | 65.7572 | 65.7331 | 65.7497 | 122.954 | 68.2357 | 122.8764 | 67.9723 | 68.049 | 136.1365 | 68.0131 | 135.924 | 54.905 | 54.9409 | 54.8274 | 54.8633
1642.8906 | 123.1384 | -68.0878 | 54.9271 | -2.3459 | -2.536 | -2.5028 | -2.4196 | -2.3305 | -2.3593 | -2.3335 | 54.8891 | 0.22116 | 54.8207 | -0.042259 | 0.029923 | 68.1769 | -0.010593 | 67.9644 | 65.7419 | 65.5518 | 65.585 | 65.6682 | 65.7572 | 65.7285 | 65.7543 | 122.9769 | 68.3089 | 122.9085 | 68.0455 | 68.1177 | 136.2647 | 68.0772 | 136.0522 | 54.8592 | 54.8997 | 54.7908 | 54.8313
1643.8906 | 123.2208 | -68.074 | 54.9088 | -2.41 | -2.5955 | -2.5623 | -2.4791 | -2.3901 | -2.4188 | -2.393 | 54.8708 | 0.22116 | 54.7932 | -0.042259 | 0.029923 | 68.1998 | -0.006014 | 67.9781 | 65.664 | 65.4785 | 65.5118 | 65.5949 | 65.684 | 65.6552 | 65.681 | 122.9448 | 68.2952 | 122.8673 | 68.0318 | 68.104 | 136.2738 | 68.068 | 136.0522 | 54.8409 | 54.8768 | 54.7633 | 54.7992
1644.8906 | 123.1934 | -68.1381 | 54.8172 | -2.5199 | -2.7008 | -2.6767 | -2.5936 | -2.5091 | -2.5378 | -2.5075 | 54.8159 | 0.22574 | 54.7337 | -0.042259 | 0.025345 | 68.2547 | -0.001436 | 68.0331 | 65.6182 | 65.4373 | 65.4614 | 65.5446 | 65.629 | 65.6003 | 65.6307 | 122.954 | 68.3639 | 122.8718 | 68.0959 | 68.1635 | 136.3928 | 68.1367 | 136.1712 | 54.7905 | 54.8173 | 54.7084 | 54.7351
1645.8906 | 123.1293 | -68.2434 | 54.808 | -2.5107 | -2.6917 | -2.6584 | -2.589 | -2.4953 | -2.5241 | -2.4937 | 54.7426 | 0.22116 | 54.6559 | -0.051417 | 0.029923 | 68.328 | 0.007721 | 68.1017 | 65.7327 | 65.5518 | 65.585 | 65.6544 | 65.7481 | 65.7193 | 65.7497 | 122.986 | 68.4646 | 122.8993 | 68.192 | 68.2733 | 136.5714 | 68.2511 | 136.3451 | 54.7127 | 54.7349 | 54.6259 | 54.6482
1646.8906 | 123.1522 | -68.2892 | 54.7623 | -2.5611 | -2.7466 | -2.718 | -2.6256 | -2.5457 | -2.5745 | -2.5532 | 54.6648 | 0.22574 | 54.5826 | -0.03768 | 0.025345 | 68.4012 | 0.007721 | 68.1658 | 65.7281 | 65.5426 | 65.5712 | 65.6636 | 65.7435 | 65.7147 | 65.7359 | 122.954 | 68.5149 | 122.8718 | 68.2515 | 68.3145 | 136.6904 | 68.2969 | 136.455 | 54.6394 | 54.6571 | 54.5573 | 54.5749
1647.8906 | 123.1384 | -68.4082 | 54.6021 | -2.5519 | -2.7283 | -2.6905 | -2.6119 | -2.5365 | -2.5607 | -2.5304 | 54.5732 | 0.22574 | 54.4956 | -0.03768 | 0.034501 | 68.4882 | 0.003143 | 68.2757 | 65.8563 | 65.6799 | 65.7177 | 65.7963 | 65.8717 | 65.8475 | 65.8778 | 122.9814 | 68.6339 | 122.9038 | 68.3705 | 68.4427 | 136.8964 | 68.4113 | 136.6839 | 54.5387 | 54.5701 | 54.4611 | 54.4925
1648.8906 | 123.1201 | -68.4448 | 54.5746 | -2.7946 | -2.971 | -2.9423 | -2.8591 | -2.7792 | -2.808 | -2.7776 | 54.5183 | 0.22116 | 54.4544 | -0.042259 | 0.029923 | 68.5477 | 0.003143 | 68.3261 | 65.6502 | 65.4739 | 65.5025 | 65.5857 | 65.6656 | 65.6369 | 65.6672 | 122.9631 | 68.666 | 122.8993 | 68.4026 | 68.4747 | 136.9925 | 68.448 | 136.7709 | 54.4883 | 54.5151 | 54.4245 | 54.4513
1649.8906 | 123.1842 | -68.5226 | 54.4922 | -3.0281 | -3.2091 | -3.1804 | -3.088 | -3.0127 | -3.0415 | -3.0202 | 54.4587 | 0.21658 | 54.3903 | -0.046838 | 0.025345 | 68.6026 | 0.003143 | 68.381 | 65.4946 | 65.3136 | 65.3423 | 65.4346 | 65.51 | 65.4812 | 65.5024 | 122.9814 | 68.7392 | 122.913 | 68.4758 | 68.548 | 137.1253 | 68.5258 | 136.9036 | 54.4334 | 54.4556 | 54.365 | 54.3872
1650.8906 | 123.1476 | -68.5593 | 54.4601 | -2.8816 | -3.0671 | -3.0247 | -2.9553 | -2.8707 | -2.8995 | -2.8691 | 54.3992 | 0.22574 | 54.3308 | -0.042259 | 0.029923 | 68.6667 | 0.003143 | 68.4451 | 65.6777 | 65.4921 | 65.5345 | 65.604 | 65.6885 | 65.6597 | 65.6901 | 122.9585 | 68.785 | 122.8901 | 68.517 | 68.5892 | 137.226 | 68.5624 | 137.0044 | 54.3693 | 54.3961 | 54.3009 | 54.3277
1651.8906 | 123.1338 | -68.6142 | 54.3823 | -3.1242 | -3.3052 | -3.272 | -3.1888 | -3.1042 | -3.1468 | -3.1209 | 54.3397 | 0.23032 | 54.2667 | -0.046838 | 0.029923 | 68.7217 | 0.003143 | 68.5 | 65.49 | 65.309 | 65.3422 | 65.4254 | 65.51 | 65.4674 | 65.4933 | 122.9539 | 68.8445 | 122.8809 | 68.5674 | 68.6441 | 137.3359 | 68.6173 | 137.1142 | 54.3098 | 54.3366 | 54.2368 | 54.2636
1652.8906 | 123.1979 | -68.7332 | 54.2587 | -3.1288 | -3.3144 | -3.2811 | -3.2025 | -3.1179 | -3.1559 | -3.1209 | 54.2344 | 0.22574 | 54.1614 | -0.046838 | 0.029923 | 68.8178 | -0.001436 | 68.6008 | 65.6044 | 65.4188 | 65.4521 | 65.5307 | 65.6153 | 65.5773 | 65.6123 | 122.9676 | 68.959 | 122.8946 | 68.6864 | 68.7631 | 137.551 | 68.7318 | 137.334 | 54.2045 | 54.2358 | 54.1315 | 54.1629
1653.8906 | 123.1796 | -68.811 | 54.1946 | -3.2158 | -3.4014 | -3.359 | -3.2895 | -3.2004 | -3.2475 | -3.2079 | 54.1566 | 0.21658 | 54.079 | -0.046838 | 0.025345 | 68.9002 | -0.001436 | 68.674 | 65.5952 | 65.4097 | 65.4521 | 65.5216 | 65.6107 | 65.5636 | 65.6031 | 122.9676 | 69.0276 | 122.89 | 68.7642 | 68.8364 | 137.7113 | 68.8096 | 137.485 | 54.1312 | 54.158 | 54.0537 | 54.0804
1654.8906 | 123.1888 | -68.8339 | 54.126 | -3.0784 | -3.2503 | -3.217 | -3.1384 | -3.0584 | -3.0964 | -3.0614 | 54.1108 | 0.21658 | 54.0149 | -0.046838 | 0.034501 | 68.9597 | 0.007721 | 68.7244 | 65.7555 | 65.5837 | 65.6169 | 65.6955 | 65.7755 | 65.7375 | 65.7725 | 122.9447 | 69.0505 | 122.8488 | 68.7871 | 68.8684 | 137.7937 | 68.8416 | 137.5583 | 54.0763 | 54.1031 | 53.9804 | 54.0072
1655.8906 | 123.143 | -68.8522 | 54.1306 | -3.1059 | -3.2823 | -3.2536 | -3.175 | -3.0905 | -3.133 | -3.0889 | 54.0879 | 0.22574 | 54.0012 | -0.042259 | 0.029923 | 68.9689 | 0.003143 | 68.7473 | 65.7463 | 65.5699 | 65.5986 | 65.6772 | 65.7618 | 65.7192 | 65.7633 | 122.9401 | 69.078 | 122.8534 | 68.81 | 68.8822 | 137.8211 | 68.8554 | 137.5995 | 54.058 | 54.0847 | 53.9713 | 53.998
1656.8906 | 123.2483 | -68.9255 | 54.0207 | -3.376 | -3.5571 | -3.5284 | -3.4497 | -3.356 | -3.394 | -3.3636 | 54.0375 | 0.22116 | 53.96 | -0.03768 | 0.025345 | 69.0193 | -0.001436 | 68.793 | 65.5494 | 65.3684 | 65.3971 | 65.4757 | 65.5695 | 65.5315 | 65.5619 | 122.963 | 69.1466 | 122.8854 | 68.8878 | 68.9508 | 137.9447 | 68.924 | 137.7185 | 54.0122 | 54.039 | 53.9346 | 53.9614
1657.8906 | 123.1064 | -68.9529 | 54.0619 | -3.5638 | -3.7494 | -3.7115 | -3.6374 | -3.5483 | -3.5954 | -3.5559 | 54.0284 | 0.22574 | 53.9554 | -0.042259 | 0.025345 | 69.033 | -0.001436 | 68.8114 | 65.3892 | 65.2036 | 65.2414 | 65.3155 | 65.4047 | 65.3575 | 65.3971 | 122.9813 | 69.1787 | 122.9083 | 68.9107 | 68.9783 | 137.9859 | 68.9515 | 137.7643 | 54.003 | 54.0298 | 53.9301 | 53.9568
1658.8906 | 123.1201 | -68.985 | 54.0115 | -3.7698 | -3.9508 | -3.9313 | -3.8526 | -3.7589 | -3.806 | -3.7619 | 53.978 | 0.23032 | 53.9142 | -0.046838 | 0.020767 | 69.0742 | -0.001436 | 68.8571 | 65.2152 | 65.0342 | 65.0537 | 65.1323 | 65.2261 | 65.1789 | 65.2231 | 122.963 | 69.2153 | 122.8992 | 68.9381 | 69.0058 | 138.0592 | 68.9835 | 137.8421 | 53.9572 | 53.9794 | 53.8934 | 53.9156
1659.8906 | 123.143 | -69.0948 | 53.8376 | -3.7286 | -3.9096 | -3.8855 | -3.816 | -3.7177 | -3.7603 | -3.7253 | 53.891 | 0.23032 | 53.818 | -0.042259 | 0.034501 | 69.1612 | -0.001436 | 68.9304 | 65.3663 | 65.1852 | 65.2094 | 65.2788 | 65.3772 | 65.3346 | 65.3696 | 122.9859 | 69.3252 | 122.9129 | 69.0526 | 69.1294 | 138.256 | 69.0934 | 138.0252 | 53.8565 | 53.8924 | 53.7835 | 53.8195
1660.8906 | 123.1659 | -69.1269 | 53.8651 | -4.0262 | -4.2164 | -4.1877 | -4.1045 | -4.0198 | -4.0624 | -4.0091 | 53.8544 | 0.23032 | 53.7768 | -0.046838 | 0.025345 | 69.2024 | -0.001436 | 68.9807 | 65.1007 | 64.9105 | 64.9392 | 65.0224 | 65.1071 | 65.0645 | 65.1178 | 122.9813 | 69.3572 | 122.9037 | 69.0801 | 69.1522 | 138.3293 | 69.1255 | 138.1076 | 53.829 | 53.8558 | 53.7515 | 53.7783
1661.8906 | 123.262 | -69.1177 | 53.7964 | -4.1635 | -4.3538 | -4.325 | -4.251 | -4.1571 | -4.2044 | -4.1602 | 53.7857 | 0.22116 | 53.7173 | -0.046838 | 0.029923 | 69.2573 | 0.003143 | 69.0403 | 64.9542 | 64.764 | 64.7927 | 64.8668 | 64.9606 | 64.9134 | 64.9576 | 122.9034 | 69.3389 | 122.8351 | 69.0709 | 69.1477 | 138.375 | 69.1209 | 138.158 | 53.7558 | 53.7826 | 53.6874 | 53.7142
1662.8906 | 123.1888 | -69.2368 | 53.7186 | -4.3192 | -4.5094 | -4.4853 | -4.3975 | -4.3174 | -4.3509 | -4.3021 | 53.7308 | 0.22116 | 53.6441 | -0.042259 | 0.025345 | 69.3214 | -0.001436 | 69.0952 | 64.9176 | 64.7273 | 64.7515 | 64.8393 | 64.9194 | 64.8859 | 64.9346 | 122.9675 | 69.4579 | 122.8808 | 69.1945 | 69.2621 | 138.5582 | 69.2353 | 138.332 | 53.7054 | 53.7322 | 53.6187 | 53.6455
1663.8906 | 123.2666 | -69.2734 | 53.6499 | -4.2276 | -4.4041 | -4.3708 | -4.2968 | -4.2075 | -4.2456 | -4.2105 | 53.6712 | 0.22574 | 53.5891 | -0.042259 | 0.029923 | 69.3763 | -0.001436 | 69.1456 | 65.0458 | 64.8692 | 64.9025 | 64.9766 | 65.0659 | 65.0278 | 65.0628 | 122.9446 | 69.4991 | 122.8625 | 69.2311 | 69.3033 | 138.6497 | 69.2719 | 138.4189 | 53.6413 | 53.6727 | 53.5592 | 53.5906
1664.8906 | 123.1384 | -69.3329 | 53.627 | -4.2414 | -4.4453 | -4.412 | -4.3334 | -4.2441 | -4.2868 | -4.2289 | 53.6438 | 0.23032 | 53.5662 | -0.042259 | 0.025345 | 69.3992 | 0.003143 | 69.1639 | 65.0915 | 64.8875 | 64.9208 | 64.9995 | 65.0888 | 65.0461 | 65.104 | 122.9767 | 69.5632 | 122.8991 | 69.2906 | 69.3582 | 138.7321 | 69.336 | 138.4968 | 53.6184 | 53.6406 | 53.5409 | 53.5631
1665.8906 | 123.1796 | -69.3237 | 53.6087 | -4.2963 | -4.4957 | -4.4624 | -4.3929 | -4.2899 | -4.328 | -4.2838 | 53.6117 | 0.22574 | 53.5159 | -0.03768 | 0.025345 | 69.4221 | 0.003143 | 69.2051 | 65.0274 | 64.828 | 64.8613 | 64.9308 | 65.0338 | 64.9957 | 65.0399 | 122.9355 | 69.5495 | 122.8396 | 69.2861 | 69.3491 | 138.7459 | 69.3269 | 138.5288 | 53.5864 | 53.6086 | 53.4905 | 53.5127
1666.8906 | 123.1155 | -69.4153 | 53.6453 | -4.4291 | -4.6239 | -4.5952 | -4.5074 | -4.4135 | -4.4562 | -4.3982 | 53.5843 | 0.22574 | 53.5159 | -0.03768 | 0.029923 | 69.4633 | 0.003143 | 69.2463 | 64.9862 | 64.7914 | 64.8201 | 64.9079 | 65.0018 | 64.9591 | 65.017 | 122.9995 | 69.641 | 122.9312 | 69.3776 | 69.4452 | 138.8786 | 69.4184 | 138.6616 | 53.5543 | 53.5811 | 53.486 | 53.5127
1667.8906 | 123.262 | -69.4244 | 53.4988 | -4.3558 | -4.5461 | -4.5173 | -4.4433 | -4.3448 | -4.3875 | -4.3387 | 53.5247 | 0.22574 | 53.4472 | -0.046838 | 0.025345 | 69.5274 | -0.001436 | 69.2966 | 65.0686 | 64.8784 | 64.9071 | 64.9812 | 65.0796 | 65.0369 | 65.0857 | 122.9492 | 69.6502 | 122.8716 | 69.3776 | 69.4498 | 138.9519 | 69.423 | 138.7211 | 53.4994 | 53.5262 | 53.4219 | 53.4486
1668.8906 | 123.2574 | -69.516 | 53.421 | -4.2734 | -4.4545 | -4.4304 | -4.3471 | -4.267 | -4.2959 | -4.2472 | 53.4332 | 0.22116 | 53.3602 | -0.046838 | 0.020767 | 69.6052 | -0.001436 | 69.3745 | 65.2426 | 65.0615 | 65.0856 | 65.1689 | 65.249 | 65.2201 | 65.2688 | 122.9492 | 69.7372 | 122.8762 | 69.4692 | 69.5368 | 139.1212 | 69.5146 | 138.8905 | 53.4124 | 53.4346 | 53.3395 | 53.3617
1669.8906 | 123.1934 | -69.5892 | 53.3112 | -4.3421 | -4.5507 | -4.5219 | -4.4341 | -4.3448 | -4.3783 | -4.3342 | 53.3416 | 0.23032 | 53.2641 | -0.046838 | 0.034501 | 69.706 | -0.001436 | 69.4798 | 65.2472 | 65.0386 | 65.0673 | 65.1551 | 65.2444 | 65.2109 | 65.2551 | 122.9308 | 69.8196 | 122.8533 | 69.5424 | 69.6237 | 139.2952 | 69.5878 | 139.069 | 53.3071 | 53.343 | 53.2296 | 53.2655
1670.8906 | 123.2025 | -69.6396 | 53.2974 | -4.3238 | -4.5186 | -4.499 | -4.4204 | -4.3174 | -4.3417 | -4.3067 | 53.305 | 0.22574 | 53.2274 | -0.051417 | 0.020767 | 69.738 | 0.003143 | 69.5072 | 65.3158 | 65.121 | 65.1406 | 65.2192 | 65.3222 | 65.2979 | 65.3329 | 122.9446 | 69.8653 | 122.867 | 69.5882 | 69.6604 | 139.3776 | 69.6427 | 139.1468 | 53.2842 | 53.3018 | 53.2067 | 53.2243
1671.8906 | 123.1064 | -69.6442 | 53.3478 | -4.4977 | -4.688 | -4.673 | -4.5898 | -4.4913 | -4.5294 | -4.4761 | 53.305 | 0.22574 | 53.2137 | -0.042259 | 0.029923 | 69.7426 | -0.001436 | 69.521 | 65.1464 | 64.9561 | 64.9711 | 65.0544 | 65.1528 | 65.1147 | 65.1681 | 122.9491 | 69.8699 | 122.8579 | 69.6019 | 69.6741 | 139.3868 | 69.6427 | 139.1651 | 53.275 | 53.3064 | 53.1838 | 53.2152
1672.8906 | 123.2346 | -69.6259 | 53.2837 | -4.7038 | -4.8941 | -4.8745 | -4.8004 | -4.6928 | -4.7309 | -4.6729 | 53.2958 | 0.23032 | 53.2183 | -0.042259 | 0.034501 | 69.7517 | 0.003143 | 69.521 | 64.9221 | 64.7318 | 64.7514 | 64.8255 | 64.9331 | 64.895 | 64.9529 | 122.9217 | 69.8562 | 122.8441 | 69.5836 | 69.6604 | 139.3776 | 69.629 | 139.1468 | 53.2613 | 53.2927 | 53.1838 | 53.2151
1673.8906 | 123.175 | -69.6396 | 53.27 | -4.6534 | -4.8437 | -4.8241 | -4.7363 | -4.6378 | -4.6759 | -4.6226 | 53.2867 | 0.23032 | 53.2137 | -0.046838 | 0.020767 | 69.7609 | 0.007721 | 69.5393 | 64.9862 | 64.7959 | 64.8155 | 64.9033 | 65.0018 | 64.9636 | 65.017 | 122.9262 | 69.8699 | 122.8533 | 69.5927 | 69.6604 | 139.4005 | 69.6473 | 139.1789 | 53.2659 | 53.2789 | 53.1929 | 53.206
1674.8906 | 123.2025 | -69.7266 | 53.1967 | -4.7083 | -4.9078 | -4.8882 | -4.8004 | -4.7065 | -4.7446 | -4.6821 | 53.2088 | 0.23032 | 53.1267 | -0.03768 | 0.034501 | 69.8341 | -0.006014 | 69.6171 | 65.0182 | 64.8188 | 64.8384 | 64.9262 | 65.0201 | 64.9819 | 65.0445 | 122.9354 | 69.9569 | 122.8533 | 69.6889 | 69.7611 | 139.5607 | 69.7205 | 139.3437 | 53.1743 | 53.2148 | 53.0922 | 53.1327
1675.8906 | 123.1522 | -69.8044 | 53.1006 | -4.7129 | -4.9032 | -4.8836 | -4.8004 | -4.7019 | -4.7446 | -4.6821 | 53.1218 | 0.22116 | 53.0397 | -0.042259 | 0.034501 | 69.9166 | -0.006014 | 69.6858 | 65.0915 | 64.9012 | 64.9207 | 65.004 | 65.1025 | 65.0598 | 65.1223 | 122.9262 | 70.0255 | 122.8441 | 69.7621 | 69.8389 | 139.7209 | 69.7984 | 139.4902 | 53.0873 | 53.1278 | 53.0052 | 53.0458
1676.8906 | 123.1613 | -69.8914 | 53.0502 | -4.5802 | -4.7613 | -4.7417 | -4.663 | -4.56 | -4.6027 | -4.5493 | 53.0623 | 0.22574 | 52.9802 | -0.046838 | 0.029923 | 69.9761 | -0.001436 | 69.7407 | 65.3112 | 65.1301 | 65.1497 | 65.2283 | 65.3314 | 65.2887 | 65.342 | 122.9537 | 70.1171 | 122.8716 | 69.8445 | 69.9213 | 139.8674 | 69.8899 | 139.6321 | 53.0324 | 53.0637 | 52.9503 | 52.9817
1677.8906 | 123.1796 | -69.9188 | 53.0045 | -4.5344 | -4.7201 | -4.7005 | -4.6264 | -4.5234 | -4.5523 | -4.5035 | 53.0119 | 0.23032 | 52.9344 | -0.046838 | 0.029923 | 70.0264 | 0.003143 | 69.8002 | 65.3845 | 65.1988 | 65.2183 | 65.2924 | 65.3954 | 65.3665 | 65.4153 | 122.9308 | 70.1491 | 122.8533 | 69.872 | 69.9487 | 139.9452 | 69.922 | 139.7191 | 52.982 | 53.0088 | 52.9045 | 52.9313
1678.8906 | 123.1842 | -70.0195 | 52.9083 | -4.5573 | -4.7384 | -4.7188 | -4.6401 | -4.5417 | -4.5798 | -4.5264 | 52.9204 | 0.23032 | 52.8475 | -0.046838 | 0.029923 | 70.1271 | -0.006014 | 69.901 | 65.4623 | 65.2811 | 65.3007 | 65.3794 | 65.4778 | 65.4397 | 65.4931 | 122.9399 | 70.2498 | 122.867 | 69.9727 | 70.0495 | 140.1467 | 70.0135 | 139.9205 | 52.8904 | 52.9264 | 52.8175 | 52.8535
1679.8906 | 123.1705 | -70.1111 | 52.8305 | -4.5985 | -4.7888 | -4.7692 | -4.6859 | -4.5875 | -4.6256 | -4.5631 | 52.8151 | 0.23032 | 52.7513 | -0.03768 | 0.029923 | 70.2187 | -0.006014 | 69.9879 | 65.5126 | 65.3223 | 65.3419 | 65.4252 | 65.5236 | 65.4855 | 65.548 | 122.9262 | 70.3414 | 122.8624 | 70.0734 | 70.141 | 140.3298 | 70.1051 | 140.099 | 52.7851 | 52.8211 | 52.7214 | 52.7573
1680.8906 | 123.1567 | -70.1111 | 52.8214 | -4.8777 | -5.0681 | -5.0485 | -4.9561 | -4.8667 | -4.9049 | -4.8469 | 52.8151 | 0.23032 | 52.7376 | -0.051417 | 0.020767 | 70.2279 | 0.003143 | 69.9925 | 65.2333 | 65.043 | 65.0626 | 65.155 | 65.2444 | 65.2062 | 65.2642 | 122.9262 | 70.3414 | 122.8487 | 70.0597 | 70.1319 | 140.3389 | 70.1142 | 140.1036 | 52.7943 | 52.8119 | 52.7168 | 52.7344
1681.8906 | 123.2162 | -70.1706 | 52.7618 | -4.8503 | -5.036 | -5.0256 | -4.9423 | -4.8347 | -4.8865 | -4.824 | 52.7784 | 0.22116 | 52.6918 | -0.046838 | 0.025345 | 70.2553 | 0.007721 | 70.0291 | 65.3203 | 65.1346 | 65.145 | 65.2283 | 65.3359 | 65.284 | 65.3466 | 122.949 | 70.3918 | 122.8624 | 70.1238 | 70.1959 | 140.4259 | 70.1783 | 140.1997 | 52.7531 | 52.7707 | 52.6664 | 52.6841
1682.8906 | 123.1842 | -70.1889 | 52.7481 | -4.7221 | -4.9078 | -4.8928 | -4.8141 | -4.7019 | -4.7446 | -4.6867 | 52.7372 | 0.22574 | 52.6552 | -0.03768 | 0.020767 | 70.2874 | 0.003143 | 70.0566 | 65.4668 | 65.2811 | 65.2961 | 65.3748 | 65.487 | 65.4443 | 65.5022 | 122.9261 | 70.4146 | 122.8441 | 70.1512 | 70.2097 | 140.4763 | 70.192 | 140.2455 | 52.7165 | 52.7341 | 52.6344 | 52.652
1683.8906 | 123.2162 | -70.2164 | 52.7069 | -4.7175 | -4.9032 | -4.8928 | -4.805 | -4.7065 | -4.74 | -4.6867 | 52.7052 | 0.22574 | 52.6185 | -0.042259 | 0.029923 | 70.3286 | -0.001436 | 70.0978 | 65.4989 | 65.3131 | 65.3236 | 65.4114 | 65.5099 | 65.4763 | 65.5297 | 122.9216 | 70.4421 | 122.8349 | 70.1741 | 70.2463 | 140.5449 | 70.2149 | 140.3142 | 52.6753 | 52.7066 | 52.5886 | 52.62
1684.8906 | 123.1842 | -70.2759 | 52.6749 | -4.6671 | -4.8529 | -4.8333 | -4.7546 | -4.6516 | -4.6851 | -4.6363 | 52.664 | 0.23032 | 52.5956 | -0.051417 | 0.029923 | 70.356 | 0.003143 | 70.1344 | 65.6087 | 65.423 | 65.4426 | 65.5213 | 65.6243 | 65.5908 | 65.6396 | 122.9399 | 70.5062 | 122.8715 | 70.2245 | 70.3058 | 140.6319 | 70.279 | 140.4103 | 52.6341 | 52.6608 | 52.5657 | 52.5925
1685.8906 | 123.1705 | -70.3079 | 52.6108 | -4.7724 | -4.949 | -4.9294 | -4.8508 | -4.7523 | -4.7858 | -4.7233 | 52.609 | 0.23032 | 52.5178 | -0.042259 | 0.034501 | 70.4201 | -0.006014 | 70.1985 | 65.5355 | 65.3589 | 65.3785 | 65.4572 | 65.5556 | 65.5221 | 65.5846 | 122.917 | 70.5382 | 122.8257 | 70.2657 | 70.3424 | 140.7281 | 70.3019 | 140.5065 | 52.5745 | 52.615 | 52.4833 | 52.5238
1686.8906 | 123.2117 | -70.2988 | 52.597 | -4.6076 | -4.775 | -4.7737 | -4.6951 | -4.5921 | -4.6256 | -4.5768 | 52.6136 | 0.22574 | 52.5316 | -0.051417 | 0.020767 | 70.4201 | -0.001436 | 70.1985 | 65.6911 | 65.5237 | 65.525 | 65.6037 | 65.7067 | 65.6732 | 65.722 | 122.9124 | 70.5245 | 122.8303 | 70.2473 | 70.3195 | 140.7189 | 70.2973 | 140.4973 | 52.5928 | 52.615 | 52.5108 | 52.533
1687.8906 | 123.1659 | -70.3079 | 52.6428 | -4.7541 | -4.9353 | -4.9111 | -4.8324 | -4.7202 | -4.7629 | -4.705 | 52.6319 | 0.22574 | 52.559 | -0.046838 | 0.034501 | 70.3881 | -0.001436 | 70.1665 | 65.5538 | 65.3726 | 65.3968 | 65.4755 | 65.5877 | 65.545 | 65.6029 | 122.9398 | 70.5337 | 122.8669 | 70.2611 | 70.3424 | 140.696 | 70.3065 | 140.4744 | 52.5974 | 52.6334 | 52.5245 | 52.5605
1688.8906 | 123.1934 | -70.372 | 52.5421 | -4.7404 | -4.9124 | -4.9019 | -4.8279 | -4.7111 | -4.7538 | -4.7004 | 52.5587 | 0.22574 | 52.4858 | -0.03768 | 0.034501 | 70.4659 | 0.003143 | 70.2443 | 65.6316 | 65.4596 | 65.4701 | 65.5442 | 65.6609 | 65.6182 | 65.6716 | 122.9307 | 70.5977 | 122.8578 | 70.3343 | 70.4065 | 140.8379 | 70.3752 | 140.6163 | 52.5242 | 52.5555 | 52.4513 | 52.4826
1689.8906 | 123.1979 | -70.4269 | 52.5101 | -4.6763 | -4.8391 | -4.8287 | -4.75 | -4.6516 | -4.6851 | -4.6226 | 52.5083 | 0.23032 | 52.4354 | -0.051417 | 0.029923 | 70.5209 | -0.001436 | 70.2947 | 65.7506 | 65.5878 | 65.5983 | 65.6769 | 65.7754 | 65.7418 | 65.8044 | 122.9352 | 70.6573 | 122.8623 | 70.3755 | 70.4569 | 140.9478 | 70.4255 | 140.7216 | 52.4784 | 52.5097 | 52.4055 | 52.4368
1690.8906 | 123.2162 | -70.4132 | 52.5146 | -4.8732 | -5.0543 | -5.0485 | -4.9515 | -4.853 | -4.8865 | -4.8286 | 52.5266 | 0.22574 | 52.4491 | -0.046838 | 0.025345 | 70.498 | -0.001436 | 70.2764 | 65.54 | 65.3589 | 65.3647 | 65.4617 | 65.5602 | 65.5267 | 65.5846 | 122.9398 | 70.6389 | 122.8623 | 70.3664 | 70.4386 | 140.9112 | 70.4118 | 140.6896 | 52.5013 | 52.5281 | 52.4238 | 52.4506
1691.8906 | 123.2391 | -70.4453 | 52.4551 | -4.8365 | -5.0177 | -5.0073 | -4.9149 | -4.8164 | -4.8499 | -4.7965 | 52.4854 | 0.23032 | 52.3988 | -0.03768 | 0.029923 | 70.5437 | 0.003143 | 70.3221 | 65.6087 | 65.4276 | 65.438 | 65.5304 | 65.6289 | 65.5953 | 65.6487 | 122.9307 | 70.6756 | 122.844 | 70.4076 | 70.4752 | 140.989 | 70.4484 | 140.7674 | 52.4555 | 52.4823 | 52.3689 | 52.3956
1692.8906 | 123.1613 | -70.5093 | 52.4094 | -4.8274 | -5.004 | -4.9889 | -4.9149 | -4.8026 | -4.827 | -4.7691 | 52.4213 | 0.21658 | 52.3301 | -0.042259 | 0.025345 | 70.5987 | -0.001436 | 70.3771 | 65.682 | 65.5054 | 65.5204 | 65.5945 | 65.7067 | 65.6823 | 65.7403 | 122.9307 | 70.7259 | 122.8394 | 70.4671 | 70.5347 | 141.108 | 70.5079 | 140.8864 | 52.396 | 52.4228 | 52.3048 | 52.3315
1693.8906 | 123.2346 | -70.5872 | 52.3499 | -4.7267 | -4.9078 | -4.8974 | -4.8141 | -4.7019 | -4.7217 | -4.6775 | 52.3435 | 0.22574 | 52.266 | -0.051417 | 0.029923 | 70.6765 | -0.001436 | 70.4458 | 65.8605 | 65.6794 | 65.6898 | 65.773 | 65.8852 | 65.8654 | 65.9096 | 122.9306 | 70.8129 | 122.8532 | 70.5357 | 70.6171 | 141.2637 | 70.5857 | 141.0329 | 52.3136 | 52.3449 | 52.2361 | 52.2674
1694.8906 | 123.2071 | -70.5551 | 52.3544 | -4.7587 | -4.9215 | -4.9157 | -4.8324 | -4.7294 | -4.7538 | -4.6958 | 52.3526 | 0.23032 | 52.2752 | -0.046838 | 0.020767 | 70.6719 | 0.003143 | 70.4549 | 65.7964 | 65.6336 | 65.6394 | 65.7227 | 65.8257 | 65.8013 | 65.8593 | 122.9078 | 70.7854 | 122.8303 | 70.5083 | 70.5759 | 141.227 | 70.5583 | 141.01 | 52.3319 | 52.3495 | 52.2544 | 52.272
1695.8906 | 123.23 | -70.6558 | 52.2263 | -5.0884 | -5.2604 | -5.2591 | -5.1667 | -5.0682 | -5.0972 | -5.0438 | 52.2382 | 0.22574 | 52.1653 | -0.042259 | 0.029923 | 70.7864 | 0.003143 | 70.5556 | 65.5675 | 65.3955 | 65.3967 | 65.4892 | 65.5877 | 65.5587 | 65.6121 | 122.894 | 70.8816 | 122.8211 | 70.6136 | 70.6857 | 141.4422 | 70.659 | 141.2115 | 52.2083 | 52.235 | 52.1354 | 52.1621
1696.8906 | 123.2071 | -70.7291 | 52.1896 | -5.244 | -5.4252 | -5.4148 | -5.3361 | -5.2238 | -5.2574 | -5.204 | 52.197 | 0.22574 | 52.1058 | -0.051417 | 0.039079 | 70.823 | 0.007721 | 70.6014 | 65.485 | 65.3039 | 65.3143 | 65.393 | 65.5053 | 65.4717 | 65.5251 | 122.926 | 70.9548 | 122.8348 | 70.6776 | 70.7681 | 141.5521 | 70.7368 | 141.3305 | 52.1579 | 52.1892 | 52.0667 | 52.098
1697.8906 | 123.2071 | -70.6924 | 52.1576 | -5.6469 | -5.8373 | -5.8268 | -5.7344 | -5.6358 | -5.674 | -5.6252 | 52.1878 | 0.22574 | 52.092 | -0.03768 | 0.034501 | 70.8276 | -0.001436 | 70.606 | 65.0455 | 64.8551 | 64.8656 | 64.958 | 65.0566 | 65.0184 | 65.0672 | 122.8803 | 70.9182 | 122.7845 | 70.6548 | 70.7269 | 141.52 | 70.691 | 141.2984 | 52.1533 | 52.1892 | 52.0575 | 52.0935
1698.8906 | 123.1796 | -70.7108 | 52.1851 | -5.972 | -6.1624 | -6.1473 | -6.0595 | -5.9563 | -5.9945 | -5.9365 | 52.1878 | 0.22574 | 52.1103 | -0.042259 | 0.029923 | 70.8276 | -0.001436 | 70.6014 | 64.7388 | 64.5484 | 64.5634 | 64.6513 | 64.7545 | 64.7162 | 64.7742 | 122.8986 | 70.9365 | 122.8211 | 70.6685 | 70.7407 | 141.5383 | 70.7093 | 141.3122 | 52.1579 | 52.1892 | 52.0804 | 52.1118
1699.8906 | 123.2391 | -70.7428 | 52.1439 | -6.0086 | -6.2036 | -6.184 | -6.1007 | -5.9929 | -6.0311 | -5.9686 | 52.1466 | 0.23032 | 52.0691 | -0.042259 | 0.034501 | 70.8825 | -0.001436 | 70.6609 | 64.7342 | 64.5392 | 64.5588 | 64.6421 | 64.7499 | 64.7117 | 64.7742 | 122.8894 | 70.9731 | 122.8119 | 70.7005 | 70.7773 | 141.6253 | 70.7414 | 141.4037 | 52.1121 | 52.148 | 52.0346 | 52.0706
1700.8906 | 123.2346 | -70.7657 | 52.1622 | -6.9243 | -7.1377 | -7.1134 | -7.021 | -6.9131 | -6.9651 | -6.9071 | 52.1329 | 0.22574 | 52.0554 | -0.046838 | 0.029923 | 70.8825 | 0.003143 | 70.6655 | 63.8414 | 63.628 | 63.6523 | 63.7447 | 63.8526 | 63.8006 | 63.8586 | 122.8986 | 70.9914 | 122.8211 | 70.7188 | 70.7956 | 141.6482 | 70.7688 | 141.4312 | 52.1029 | 52.1297 | 52.0255 | 52.0523
1701.8906 | 123.2071 | -70.8344 | 52.0889 | -7.2402 | -7.4628 | -7.4385 | -7.3506 | -7.2381 | -7.2902 | -7.223 | 52.0688 | 0.22116 | 51.9913 | -0.046838 | 0.025345 | 70.9375 | 0.003143 | 70.7159 | 63.5942 | 63.3716 | 63.3959 | 63.4837 | 63.5962 | 63.5442 | 63.6114 | 122.9031 | 71.0555 | 122.8257 | 70.7875 | 70.8597 | 141.7718 | 70.8375 | 141.5502 | 52.0434 | 52.0656 | 51.966 | 51.9882
1702.8906 | 123.1796 | -70.8115 | 52.0935 | -7.0616 | -7.2567 | -7.2508 | -7.1537 | -7.0596 | -7.1162 | -7.0444 | 52.0733 | 0.22574 | 51.9822 | -0.03768 | 0.029923 | 70.9466 | 0.003143 | 70.7159 | 63.7498 | 63.5547 | 63.5607 | 63.6577 | 63.7519 | 63.6952 | 63.767 | 122.8848 | 71.0372 | 122.7936 | 70.7738 | 70.8414 | 141.7581 | 70.8146 | 141.5273 | 52.0434 | 52.0702 | 51.9522 | 51.979
1703.8906 | 123.2025 | -70.8298 | 52.0615 | -7.1028 | -7.3117 | -7.292 | -7.2041 | -7.1008 | -7.1574 | -7.0948 | 52.055 | 0.22574 | 51.9776 | -0.046838 | 0.034501 | 70.9558 | 0.003143 | 70.7342 | 63.7269 | 63.5181 | 63.5378 | 63.6257 | 63.729 | 63.6723 | 63.735 | 122.8848 | 71.0555 | 122.8074 | 70.7829 | 70.8643 | 141.7855 | 70.8329 | 141.564 | 52.0205 | 52.0519 | 51.9431 | 51.9744
1704.8906 | 123.0743 | -70.8801 | 52.0752 | -7.4737 | -7.6917 | -7.6628 | -7.5795 | -7.4716 | -7.5374 | -7.4702 | 52.0367 | 0.22574 | 51.9684 | -0.046838 | 0.029923 | 70.9832 | -0.006014 | 70.7525 | 63.4064 | 63.1884 | 63.2173 | 63.3006 | 63.4085 | 63.3427 | 63.4099 | 122.9168 | 71.1059 | 122.8485 | 70.8333 | 70.91 | 141.8634 | 70.8741 | 141.6326 | 52.0068 | 52.0427 | 51.9385 | 51.9744
1705.8906 | 123.1705 | -70.9213 | 52.0248 | -7.2997 | -7.4994 | -7.4751 | -7.3964 | -7.2885 | -7.3406 | -7.2779 | 51.9955 | 0.22574 | 51.9135 | -0.046838 | 0.025345 | 71.0199 | -0.001436 | 70.7891 | 63.6216 | 63.4219 | 63.4462 | 63.5249 | 63.6329 | 63.5808 | 63.6434 | 122.9168 | 71.1471 | 122.8348 | 70.8745 | 70.9467 | 141.9412 | 70.9199 | 141.7104 | 51.9702 | 51.997 | 51.8881 | 51.9149
1706.8906 | 123.1384 | -70.9808 | 51.9608 | -7.318 | -7.5223 | -7.498 | -7.4147 | -7.3114 | -7.368 | -7.2917 | 51.9131 | 0.22574 | 51.8219 | -0.046838 | 0.029923 | 71.0977 | -0.001436 | 70.8715 | 63.6628 | 63.4585 | 63.4828 | 63.5661 | 63.6695 | 63.6128 | 63.6892 | 122.8939 | 71.2066 | 122.8028 | 70.934 | 71.0108 | 142.0785 | 70.9794 | 141.8524 | 51.8832 | 51.9145 | 51.792 | 51.8234
1707.8906 | 123.056 | -71.077 | 51.8921 | -7.3684 | -7.5589 | -7.5484 | -7.4742 | -7.3571 | -7.4138 | -7.3512 | 51.849 | 0.22574 | 51.7807 | -0.042259 | 0.034501 | 71.1526 | -0.001436 | 70.9356 | 63.7086 | 63.518 | 63.5286 | 63.6027 | 63.7198 | 63.6631 | 63.7258 | 122.926 | 71.3027 | 122.8577 | 71.0347 | 71.1115 | 142.2296 | 71.0755 | 142.0126 | 51.8145 | 51.8504 | 51.7462 | 51.7821
1708.8906 | 123.0743 | -71.077 | 51.8967 | -7.3592 | -7.5635 | -7.5392 | -7.4605 | -7.3434 | -7.4138 | -7.3466 | 51.8444 | 0.2349 | 51.7761 | -0.03768 | 0.034501 | 71.1618 | 0.007721 | 70.9356 | 63.7177 | 63.5134 | 63.5377 | 63.6165 | 63.7336 | 63.6631 | 63.7304 | 122.9214 | 71.3119 | 122.8531 | 71.0393 | 71.1115 | 142.2388 | 71.0847 | 142.0126 | 51.8099 | 51.8367 | 51.7416 | 51.7684
1709.8906 | 123.0515 | -71.0449 | 51.9424 | -7.3226 | -7.5177 | -7.5072 | -7.433 | -7.3068 | -7.3726 | -7.3145 | 51.8719 | 0.21658 | 51.7853 | -0.042259 | 0.034501 | 71.1435 | -0.001436 | 70.9219 | 63.7223 | 63.5272 | 63.5378 | 63.6119 | 63.7381 | 63.6723 | 63.7304 | 122.9168 | 71.2615 | 122.8302 | 71.0027 | 71.0794 | 142.1884 | 71.0435 | 141.9668 | 51.8374 | 51.8733 | 51.7508 | 51.7867
1710.8906 | 123.1338 | -70.99 | 51.9745 | -7.2631 | -7.4628 | -7.4385 | -7.3689 | -7.2564 | -7.3085 | -7.255 | 51.8902 | 0.22574 | 51.8082 | -0.046838 | 0.029923 | 71.1114 | -0.001436 | 70.8807 | 63.7269 | 63.5272 | 63.5515 | 63.6211 | 63.7336 | 63.6815 | 63.735 | 122.8802 | 71.2157 | 122.7982 | 70.9432 | 71.0199 | 142.1014 | 70.9886 | 141.8707 | 51.8603 | 51.8916 | 51.7783 | 51.8096
1711.8906 | 123.0881 | -70.9396 | 52.0248 | -7.199 | -7.3895 | -7.3835 | -7.2957 | -7.174 | -7.2398 | -7.168 | 51.9589 | 0.22574 | 51.8677 | -0.042259 | 0.029923 | 71.0473 | -0.001436 | 70.8257 | 63.7406 | 63.5501 | 63.5561 | 63.644 | 63.7656 | 63.6998 | 63.7716 | 122.8985 | 71.1654 | 122.8073 | 70.8974 | 70.9696 | 141.987 | 70.9382 | 141.7654 | 51.929 | 51.9603 | 51.8378 | 51.8691
1712.8906 | 123.1293 | -70.9122 | 52.0523 | -7.0067 | -7.1926 | -7.1867 | -7.1034 | -6.9955 | -7.0384 | -6.9712 | 51.9955 | 0.22574 | 51.9181 | -0.03768 | 0.029923 | 70.997 | 0.007721 | 70.7754 | 63.9055 | 63.7195 | 63.7255 | 63.8088 | 63.9167 | 63.8738 | 63.941 | 122.9077 | 71.1379 | 122.8302 | 70.8745 | 70.9421 | 141.9091 | 70.9199 | 141.6876 | 51.9656 | 51.9878 | 51.8881 | 51.9103
1713.8906 | 123.056 | -70.8847 | 52.1027 | -7.1441 | -7.3254 | -7.3194 | -7.2407 | -7.1328 | -7.1757 | -7.1039 | 52.0321 | 0.22574 | 51.9364 | -0.03768 | 0.034501 | 70.9695 | -0.006014 | 70.7388 | 63.7407 | 63.5593 | 63.5653 | 63.644 | 63.7519 | 63.709 | 63.7808 | 122.9168 | 71.1104 | 122.8211 | 70.847 | 70.9192 | 141.8542 | 70.8787 | 141.6235 | 51.9976 | 52.0382 | 51.9019 | 51.9424
1714.8906 | 123.1247 | -70.8664 | 52.0248 | -7.2127 | -7.3987 | -7.3927 | -7.314 | -7.1969 | -7.2444 | -7.1864 | 51.9955 | 0.22574 | 51.8997 | -0.042259 | 0.029923 | 70.9832 | 0.007721 | 70.7433 | 63.6537 | 63.4677 | 63.4737 | 63.5524 | 63.6695 | 63.622 | 63.68 | 122.8619 | 71.0921 | 122.7661 | 70.8241 | 70.8963 | 141.8496 | 70.8741 | 141.6097 | 51.9656 | 51.9878 | 51.8698 | 51.892
1715.8906 | 123.1155 | -70.9351 | 51.9653 | -6.6908 | -6.8813 | -6.8524 | -6.792 | -6.6704 | -6.7179 | -6.6644 | 51.936 | 0.23948 | 51.8631 | -0.046838 | 0.034501 | 71.0244 | 0.003143 | 70.7891 | 64.2443 | 64.0538 | 64.0826 | 64.143 | 64.2646 | 64.2172 | 64.2706 | 122.8711 | 71.1745 | 122.7982 | 70.8882 | 70.9696 | 141.9595 | 70.9382 | 141.7242 | 51.9015 | 51.9329 | 51.8286 | 51.86
1716.8906 | 123.0743 | -70.903 | 52.0248 | -7.1028 | -7.2796 | -7.2782 | -7.1995 | -7.087 | -7.1345 | -7.0719 | 51.9818 | 0.23032 | 51.8997 | -0.03768 | 0.034501 | 70.997 | -0.006014 | 70.7754 | 63.8002 | 63.6234 | 63.6248 | 63.7035 | 63.816 | 63.7685 | 63.8311 | 122.8848 | 71.1333 | 122.8028 | 70.8653 | 70.9375 | 141.9 | 70.897 | 141.6784 | 51.9473 | 51.9878 | 51.8652 | 51.9058
1717.8906 | 123.1064 | -70.9396 | 51.9562 | -7.1898 | -7.3849 | -7.3607 | -7.2774 | -7.1649 | -7.2169 | -7.1543 | 51.9543 | 0.2349 | 51.8677 | -0.042259 | 0.034501 | 71.0382 | -0.001436 | 70.8212 | 63.7498 | 63.5547 | 63.579 | 63.6623 | 63.7748 | 63.7227 | 63.7853 | 122.8939 | 71.1745 | 122.8073 | 70.8974 | 70.9741 | 141.9778 | 70.9382 | 141.7608 | 51.9198 | 51.9557 | 51.8332 | 51.8691
1718.8906 | 123.0927 | -71.0266 | 51.9058 | -7.0616 | -7.2476 | -7.2233 | -7.1537 | -7.0367 | -7.0888 | -7.0215 | 51.8765 | 0.22574 | 51.8036 | -0.046838 | 0.034501 | 71.0977 | -0.006014 | 70.8761 | 63.965 | 63.779 | 63.8033 | 63.8729 | 63.9899 | 63.9379 | 64.0051 | 122.9031 | 71.2524 | 122.8302 | 70.9798 | 71.0611 | 142.1243 | 71.0206 | 141.9027 | 51.842 | 51.8825 | 51.7691 | 51.8096
1719.8906 | 123.111 | -71.0907 | 51.8234 | -7.1349 | -7.3117 | -7.2966 | -7.2178 | -7.1099 | -7.162 | -7.0994 | 51.7941 | 0.22116 | 51.7075 | -0.03768 | 0.029923 | 71.1893 | 0.003143 | 70.9631 | 63.9558 | 63.779 | 63.7941 | 63.8729 | 63.9808 | 63.9287 | 63.9913 | 122.8848 | 71.3119 | 122.7982 | 71.053 | 71.1206 | 142.28 | 71.0938 | 142.0538 | 51.7641 | 51.7909 | 51.6775 | 51.7043
1720.8906 | 123.111 | -71.1685 | 51.7639 | -6.938 | -7.1194 | -7.0905 | -7.021 | -6.9131 | -6.9697 | -6.9025 | 51.7345 | 0.22574 | 51.6479 | -0.03768 | 0.025345 | 71.2442 | -0.006014 | 71.0272 | 64.2305 | 64.0491 | 64.078 | 64.1476 | 64.2554 | 64.1988 | 64.266 | 122.9031 | 71.3943 | 122.8165 | 71.1308 | 71.1939 | 142.4127 | 71.1625 | 142.1957 | 51.7092 | 51.7406 | 51.6226 | 51.654
1721.8906 | 123.1018 | -71.2006 | 51.7319 | -6.4573 | -6.6249 | -6.6143 | -6.5402 | -6.4278 | -6.4752 | -6.4126 | 51.7025 | 0.22116 | 51.6251 | -0.046838 | 0.029923 | 71.2808 | -0.001436 | 71.0638 | 64.7433 | 64.5757 | 64.5862 | 64.6603 | 64.7727 | 64.7253 | 64.7879 | 122.9031 | 71.4217 | 122.8256 | 71.1537 | 71.2305 | 142.4814 | 71.1991 | 142.2644 | 51.6726 | 51.7039 | 51.5951 | 51.6265
1722.8906 | 123.0743 | -71.228 | 51.6815 | -6.3978 | -6.5608 | -6.5457 | -6.4761 | -6.3591 | -6.4111 | -6.3485 | 51.6613 | 0.22116 | 51.5838 | -0.03768 | 0.029923 | 71.322 | -0.001436 | 71.0913 | 64.8303 | 64.6673 | 64.6824 | 64.7519 | 64.8689 | 64.8169 | 64.8795 | 122.8893 | 71.4492 | 122.8119 | 71.1903 | 71.2579 | 142.55 | 71.2266 | 142.3193 | 51.6314 | 51.6627 | 51.5539 | 51.5853
1723.8906 | 123.0789 | -71.2738 | 51.6312 | -6.0452 | -6.199 | -6.1931 | -6.1282 | -6.0204 | -6.0586 | -5.9915 | 51.6109 | 0.22574 | 51.5335 | -0.042259 | 0.034501 | 71.377 | 0.003143 | 71.1416 | 65.2286 | 65.0748 | 65.0807 | 65.1457 | 65.2534 | 65.2152 | 65.2824 | 122.8847 | 71.4995 | 122.8073 | 71.2315 | 71.3083 | 142.6508 | 71.2769 | 142.4154 | 51.5764 | 51.6078 | 51.499 | 51.5303
1724.8906 | 123.0652 | -71.2967 | 51.6129 | -5.2165 | -5.3565 | -5.3552 | -5.2857 | -5.1826 | -5.2116 | -5.1536 | 51.5926 | 0.23032 | 51.5014 | -0.046838 | 0.029923 | 71.3861 | 0.003143 | 71.16 | 66.0801 | 65.9402 | 65.9415 | 66.011 | 66.1141 | 66.0851 | 66.143 | 122.8893 | 71.527 | 122.7981 | 71.2499 | 71.3266 | 142.6828 | 71.2998 | 142.4566 | 51.5627 | 51.5895 | 51.4715 | 51.4983
1725.8906 | 123.0377 | -71.3882 | 51.5167 | -4.7129 | -4.8483 | -4.8378 | -4.7775 | -4.6699 | -4.6943 | -4.6409 | 51.5194 | 0.2349 | 51.4328 | -0.042259 | 0.025345 | 71.4456 | -0.006014 | 71.2149 | 66.6753 | 66.54 | 66.5504 | 66.6107 | 66.7184 | 66.694 | 66.7474 | 122.9076 | 71.6231 | 122.821 | 71.346 | 71.4136 | 142.8339 | 71.3822 | 142.6031 | 51.494 | 51.5254 | 51.4074 | 51.4388
1726.8906 | 123.0515 | -71.4066 | 51.4801 | -4.4657 | -4.6056 | -4.5952 | -4.5303 | -4.4227 | -4.4516 | -4.4028 | 51.4919 | 0.23032 | 51.4053 | -0.046838 | 0.025345 | 71.4777 | 0.003143 | 71.2515 | 66.9409 | 66.801 | 66.8114 | 66.8763 | 66.9839 | 66.955 | 67.0037 | 122.8984 | 71.6369 | 122.8118 | 71.3597 | 71.4319 | 142.8842 | 71.4097 | 142.6581 | 51.4665 | 51.4887 | 51.3799 | 51.4021
1727.8906 | 123.024 | -71.347 | 51.5259 | -5.6607 | -5.8144 | -5.8039 | -5.739 | -5.6358 | -5.6557 | -5.5932 | 51.501 | 0.23032 | 51.4236 | -0.046838 | 0.034501 | 71.4639 | -0.006014 | 71.2515 | 65.6864 | 65.5326 | 65.5431 | 65.6081 | 65.7112 | 65.6913 | 65.7539 | 122.8481 | 71.5774 | 122.7707 | 71.3002 | 71.3815 | 142.811 | 71.341 | 142.5986 | 51.4665 | 51.5071 | 51.3891 | 51.4296
1728.8906 | 123.0148 | -71.3745 | 51.5625 | -5.8713 | -6.0296 | -6.0237 | -5.945 | -5.8373 | -5.8709 | -5.8083 | 51.5148 | 0.22574 | 51.4373 | -0.046838 | 0.029923 | 71.4502 | 0.003143 | 71.224 | 65.5033 | 65.3449 | 65.3508 | 65.4295 | 65.5373 | 65.5036 | 65.5662 | 122.8893 | 71.6003 | 122.8119 | 71.3277 | 71.4044 | 142.8247 | 71.3777 | 142.5986 | 51.4849 | 51.5116 | 51.4074 | 51.4342
1729.8906 | 123.0743 | -71.2738 | 51.5991 | -5.885 | -6.0479 | -6.0374 | -5.9587 | -5.8601 | -5.8938 | -5.8312 | 51.5926 | 0.22574 | 51.5014 | -0.03768 | 0.029923 | 71.3678 | 0.003143 | 71.1416 | 65.3888 | 65.2259 | 65.2364 | 65.3151 | 65.4137 | 65.38 | 65.4426 | 122.8664 | 71.4995 | 122.7752 | 71.2361 | 71.3037 | 142.6416 | 71.2769 | 142.4154 | 51.5627 | 51.5895 | 51.4715 | 51.4983
1730.8906 | 123.0148 | -71.315 | 51.6037 | -6.2558 | -6.4188 | -6.4175 | -6.3342 | -6.231 | -6.2692 | -6.1929 | 51.5606 | 0.23032 | 51.4877 | -0.03768 | 0.020767 | 71.3998 | -0.006014 | 71.1737 | 65.0592 | 64.8962 | 64.8975 | 64.9808 | 65.084 | 65.0458 | 65.1221 | 122.8756 | 71.5453 | 122.8027 | 71.2773 | 71.3358 | 142.7148 | 71.309 | 142.4887 | 51.5398 | 51.5666 | 51.4669 | 51.4937
1731.8906 | 123.0698 | -71.315 | 51.5808 | -6.7228 | -6.8859 | -6.8799 | -6.8012 | -6.6933 | -6.7316 | -6.6599 | 51.5651 | 0.2349 | 51.4923 | -0.055996 | 0.025345 | 71.3953 | -0.001436 | 71.1645 | 64.5922 | 64.4292 | 64.4351 | 64.5138 | 64.6217 | 64.5834 | 64.6551 | 122.8801 | 71.5499 | 122.8073 | 71.259 | 71.3403 | 142.7103 | 71.3136 | 142.4795 | 51.5398 | 51.5666 | 51.4669 | 51.4937
1732.8906 | 123.0515 | -71.3013 | 51.5808 | -7.6019 | -7.7833 | -7.7682 | -7.6848 | -7.5723 | -7.6244 | -7.5572 | 51.588 | 0.22574 | 51.4969 | -0.042259 | 0.025345 | 71.3724 | -0.006014 | 71.1416 | 63.6994 | 63.518 | 63.5331 | 63.6164 | 63.729 | 63.6768 | 63.7441 | 122.8893 | 71.527 | 122.7981 | 71.259 | 71.3266 | 142.6736 | 71.2953 | 142.4429 | 51.5627 | 51.594 | 51.4715 | 51.5029
1733.8906 | 123.0423 | -71.3837 | 51.5076 | -7.7438 | -7.9252 | -7.9192 | -7.8451 | -7.7234 | -7.7709 | -7.6991 | 51.4965 | 0.23032 | 51.4053 | -0.046838 | 0.025345 | 71.4685 | -0.001436 | 71.2195 | 63.6398 | 63.4584 | 63.4644 | 63.5386 | 63.6603 | 63.6127 | 63.6846 | 122.8801 | 71.614 | 122.789 | 71.3368 | 71.409 | 142.8522 | 71.3822 | 142.6031 | 51.4711 | 51.4979 | 51.3799 | 51.4067
1734.8906 | 123.0331 | -71.3791 | 51.5076 | -7.2814 | -7.4536 | -7.4614 | -7.3781 | -7.2564 | -7.2994 | -7.2367 | 51.4827 | 0.22574 | 51.4007 | -0.042259 | 0.020767 | 71.4685 | 0.007721 | 71.2378 | 64.0977 | 63.9255 | 63.9177 | 64.001 | 64.1227 | 64.0797 | 64.1424 | 122.8618 | 71.6048 | 122.7798 | 71.3368 | 71.3999 | 142.8476 | 71.3868 | 142.6169 | 51.462 | 51.475 | 51.3799 | 51.393
1735.8906 | 123.143 | -71.434 | 51.4023 | -6.732 | -6.895 | -6.8891 | -6.8103 | -6.6933 | -6.7271 | -6.6736 | 51.4324 | 0.2349 | 51.3504 | -0.042259 | 0.020767 | 71.5326 | -0.006014 | 71.3065 | 64.702 | 64.539 | 64.545 | 64.6237 | 64.7407 | 64.707 | 64.7604 | 122.8664 | 71.6689 | 122.7844 | 71.3918 | 71.4548 | 142.9666 | 71.428 | 142.7405 | 51.4116 | 51.4384 | 51.3296 | 51.3564
1736.8906 | 123.1293 | -71.3333 | 51.4618 | -7.8857 | -8.0672 | -8.0383 | -7.9641 | -7.8516 | -7.9037 | -7.8365 | 51.5056 | 0.22574 | 51.4282 | -0.046838 | 0.029923 | 71.4502 | -0.006014 | 71.224 | 63.4476 | 63.2661 | 63.295 | 63.3692 | 63.4818 | 63.4296 | 63.4969 | 122.8389 | 71.5591 | 122.7615 | 71.2865 | 71.3632 | 142.7835 | 71.3273 | 142.5574 | 51.4757 | 51.5116 | 51.3983 | 51.4342
1737.8906 | 123.0423 | -71.3425 | 51.5442 | -8.2566 | -8.4289 | -8.4229 | -8.3258 | -8.2132 | -8.2791 | -8.2073 | 51.4965 | 0.22574 | 51.4007 | -0.046838 | 0.034501 | 71.4685 | 0.003143 | 71.2286 | 63.0859 | 62.9136 | 62.9196 | 63.0166 | 63.1293 | 63.0633 | 63.1352 | 122.8389 | 71.5682 | 122.7432 | 71.2956 | 71.377 | 142.811 | 71.3456 | 142.5711 | 51.462 | 51.4933 | 51.3662 | 51.3976
1738.8906 | 123.1613 | -71.3608 | 51.4847 | -7.959 | -8.145 | -8.1299 | -8.042 | -7.9294 | -7.9907 | -7.9189 | 51.4965 | 0.23032 | 51.4099 | -0.046838 | 0.025345 | 71.4639 | -0.006014 | 71.224 | 63.4018 | 63.2158 | 63.2309 | 63.3188 | 63.4314 | 63.3701 | 63.4419 | 122.8572 | 71.5911 | 122.7706 | 71.3139 | 71.3861 | 142.8247 | 71.3548 | 142.5848 | 51.4711 | 51.5025 | 51.3845 | 51.4159
1739.8906 | 123.1384 | -71.4157 | 51.4206 | -7.4783 | -7.6597 | -7.6491 | -7.5658 | -7.4441 | -7.51 | -7.429 | 51.4324 | 0.23032 | 51.3549 | -0.046838 | 0.020767 | 71.5097 | -0.001436 | 71.2927 | 63.9374 | 63.756 | 63.7666 | 63.8499 | 63.9716 | 63.9057 | 63.9867 | 122.8481 | 71.646 | 122.7706 | 71.3689 | 71.4365 | 142.9254 | 71.4143 | 142.7084 | 51.4116 | 51.4338 | 51.3342 | 51.3564
1740.8906 | 123.1522 | -71.4615 | 51.3519 | -7.0708 | -7.2384 | -7.2279 | -7.1492 | -7.0458 | -7.0842 | -7.017 | 51.3912 | 0.23032 | 51.3137 | -0.051417 | 0.025345 | 71.5601 | -0.001436 | 71.3385 | 64.3907 | 64.2231 | 64.2336 | 64.3123 | 64.4156 | 64.3773 | 64.4445 | 122.8526 | 71.6918 | 122.7752 | 71.4101 | 71.4868 | 143.0216 | 71.4601 | 142.8 | 51.3658 | 51.3926 | 51.2884 | 51.3152
1741.8906 | 123.1613 | -71.4706 | 51.3107 | -7.2494 | -7.4262 | -7.4202 | -7.3323 | -7.2244 | -7.2673 | -7.1955 | 51.3499 | 0.2349 | 51.2588 | -0.042259 | 0.029923 | 71.6013 | 0.003143 | 71.3705 | 64.2213 | 64.0445 | 64.0505 | 64.1383 | 64.2463 | 64.2033 | 64.2751 | 122.8206 | 71.7055 | 122.7294 | 71.4284 | 71.5006 | 143.0719 | 71.4738 | 142.8412 | 51.32 | 51.3468 | 51.2289 | 51.2556
1742.8906 | 123.1888 | -71.4569 | 51.3336 | -7.3501 | -7.5269 | -7.5118 | -7.4239 | -7.3159 | -7.3589 | -7.3008 | 51.3408 | 0.23032 | 51.2359 | -0.046838 | 0.039079 | 71.615 | -0.001436 | 71.3843 | 64.1068 | 63.93 | 63.9452 | 64.033 | 64.141 | 64.098 | 64.1561 | 122.7977 | 71.6872 | 122.6928 | 71.4101 | 71.496 | 143.0719 | 71.4555 | 142.8412 | 51.3017 | 51.3422 | 51.1968 | 51.2373
1743.8906 | 123.1384 | -71.5347 | 51.2924 | -7.1532 | -7.3117 | -7.3057 | -7.227 | -7.1237 | -7.1757 | -7.0856 | 51.2996 | 0.22574 | 51.213 | -0.046838 | 0.025345 | 71.6516 | -0.001436 | 71.4118 | 64.3815 | 64.223 | 64.229 | 64.3077 | 64.4111 | 64.359 | 64.4491 | 122.8343 | 71.7605 | 122.7477 | 71.4879 | 71.5601 | 143.1864 | 71.5333 | 142.9465 | 51.2742 | 51.301 | 51.1877 | 51.2144
1744.8906 | 123.111 | -71.5439 | 51.2741 | -6.9792 | -7.1468 | -7.1363 | -7.0576 | -6.9497 | -6.988 | -6.9117 | 51.3133 | 0.2349 | 51.2451 | -0.046838 | 0.029923 | 71.6379 | -0.001436 | 71.4026 | 64.5647 | 64.397 | 64.4076 | 64.4863 | 64.5942 | 64.5559 | 64.6322 | 122.8572 | 71.7788 | 122.7889 | 71.497 | 71.5738 | 143.1818 | 71.5424 | 142.9465 | 51.2834 | 51.3148 | 51.2151 | 51.2465
1745.8906 | 123.0789 | -71.5576 | 51.2924 | -7.1578 | -7.3208 | -7.3149 | -7.2361 | -7.1282 | -7.1712 | -7.0902 | 51.295 | 0.22574 | 51.2084 | -0.042259 | 0.034501 | 71.6516 | 0.003143 | 71.4163 | 64.3998 | 64.2368 | 64.2427 | 64.3215 | 64.4294 | 64.3865 | 64.4674 | 122.8526 | 71.7834 | 122.766 | 71.5154 | 71.5921 | 143.2093 | 71.5608 | 142.9739 | 51.2605 | 51.2919 | 51.1739 | 51.2053
1746.8906 | 123.1338 | -71.5118 | 51.3382 | -7.8354 | -7.9985 | -7.9925 | -7.9092 | -7.8058 | -7.8579 | -7.7724 | 51.3271 | 0.23032 | 51.2359 | -0.046838 | 0.025345 | 71.6196 | 0.003143 | 71.3797 | 63.6765 | 63.5133 | 63.5193 | 63.6027 | 63.7061 | 63.6539 | 63.7395 | 122.8389 | 71.7422 | 122.7477 | 71.465 | 71.5372 | 143.1314 | 71.515 | 142.8915 | 51.3017 | 51.3239 | 51.2106 | 51.2328
1747.8906 | 123.0423 | -71.5759 | 51.3474 | -7.8262 | -7.9893 | -7.9833 | -7.9046 | -7.8104 | -7.8579 | -7.7678 | 51.2904 | 0.2349 | 51.1993 | -0.042259 | 0.029923 | 71.6562 | 0.007721 | 71.4255 | 63.7497 | 63.5866 | 63.5926 | 63.6713 | 63.7656 | 63.718 | 63.8081 | 122.8664 | 71.8108 | 122.7752 | 71.5337 | 71.6059 | 143.2321 | 71.5836 | 143.0014 | 51.2605 | 51.2827 | 51.1693 | 51.1915
1748.8906 | 123.1338 | -71.6125 | 51.2329 | -7.4142 | -7.5727 | -7.5575 | -7.488 | -7.3709 | -7.4138 | -7.3466 | 51.2263 | 0.22574 | 51.1489 | -0.042259 | 0.025345 | 71.7157 | -0.006014 | 71.4804 | 64.1984 | 64.0399 | 64.055 | 64.1246 | 64.2417 | 64.1987 | 64.266 | 122.8389 | 71.8383 | 122.7615 | 71.5703 | 71.6379 | 143.3283 | 71.6065 | 143.093 | 51.201 | 51.2323 | 51.1236 | 51.1549
1749.8906 | 123.1018 | -71.6171 | 51.2375 | -7.7255 | -7.8978 | -7.8826 | -7.7993 | -7.7005 | -7.7526 | -7.6625 | 51.2263 | 0.23032 | 51.1535 | -0.042259 | 0.029923 | 71.7157 | -0.001436 | 71.485 | 63.8916 | 63.7194 | 63.7345 | 63.8178 | 63.9166 | 63.8645 | 63.9546 | 122.8435 | 71.8474 | 122.7706 | 71.5749 | 71.647 | 143.3329 | 71.6157 | 143.1021 | 51.1964 | 51.2278 | 51.1236 | 51.1549
1750.8906 | 123.1247 | -71.6629 | 51.1917 | -7.492 | -7.6551 | -7.6308 | -7.5612 | -7.4533 | -7.5008 | -7.4244 | 51.1805 | 0.22116 | 51.1123 | -0.046838 | 0.025345 | 71.7524 | -0.001436 | 71.5216 | 64.1709 | 64.0078 | 64.0321 | 64.1017 | 64.2096 | 64.1621 | 64.2385 | 122.8434 | 71.8841 | 122.7752 | 71.6161 | 71.6882 | 143.4153 | 71.6615 | 143.1845 | 51.1552 | 51.182 | 51.0869 | 51.1137
1751.8906 | 123.1018 | -71.6125 | 51.2421 | -7.4737 | -7.6276 | -7.6171 | -7.5429 | -7.4487 | -7.4962 | -7.4061 | 51.2172 | 0.23032 | 51.1352 | -0.046838 | 0.029923 | 71.7112 | -0.001436 | 71.4896 | 64.1389 | 63.9849 | 63.9955 | 64.0696 | 64.1639 | 64.1163 | 64.2064 | 122.8297 | 71.8429 | 122.7477 | 71.5657 | 71.6425 | 143.3237 | 71.6111 | 143.1021 | 51.1872 | 51.2186 | 51.1053 | 51.1366
1752.8906 | 122.9782 | -71.6675 | 51.2421 | -7.3547 | -7.5132 | -7.4934 | -7.4147 | -7.3114 | -7.3589 | -7.2779 | 51.2034 | 0.22574 | 51.126 | -0.042259 | 0.029923 | 71.7386 | -0.006014 | 71.5033 | 64.3128 | 64.1543 | 64.174 | 64.2528 | 64.3561 | 64.3086 | 64.3896 | 122.8709 | 71.8932 | 122.7935 | 71.6252 | 71.6974 | 143.4061 | 71.6615 | 143.1708 | 51.1735 | 51.2095 | 51.0961 | 51.132
1753.8906 | 123.0835 | -71.7087 | 51.1093 | -6.6542 | -6.8172 | -6.7883 | -6.7234 | -6.6109 | -6.663 | -6.5866 | 51.1027 | 0.22574 | 51.0161 | -0.042259 | 0.029923 | 71.8393 | -0.006014 | 71.6132 | 65.0545 | 64.8915 | 64.9203 | 64.9853 | 65.0977 | 65.0457 | 65.1221 | 122.8114 | 71.9344 | 122.7248 | 71.6664 | 71.7386 | 143.548 | 71.7027 | 143.3219 | 51.0728 | 51.1087 | 50.9862 | 51.0222
1754.8906 | 123.1247 | -71.7224 | 51.1002 | -6.6038 | -6.7348 | -6.738 | -6.6638 | -6.556 | -6.5943 | -6.5134 | 51.1027 | 0.2349 | 51.0253 | -0.042259 | 0.034501 | 71.8302 | 0.007721 | 71.5949 | 65.1186 | 64.9877 | 64.9844 | 65.0586 | 65.1664 | 65.1281 | 65.209 | 122.8251 | 71.9573 | 122.7477 | 71.6802 | 71.7569 | 143.5526 | 71.7301 | 143.3173 | 51.0682 | 51.095 | 50.9908 | 51.0176
1755.8906 | 123.1796 | -71.7178 | 51.1002 | -5.917 | -6.0525 | -6.0512 | -5.9816 | -5.8739 | -5.9121 | -5.8404 | 51.0844 | 0.22574 | 50.9841 | -0.042259 | 0.025345 | 71.8485 | -0.001436 | 71.6269 | 65.8008 | 65.6653 | 65.6667 | 65.7362 | 65.844 | 65.8057 | 65.8775 | 122.8022 | 71.9436 | 122.7019 | 71.6756 | 71.7432 | 143.5663 | 71.7164 | 143.3448 | 51.059 | 51.0858 | 50.9587 | 50.9855
1756.8906 | 123.1247 | -71.7224 | 51.123 | -6.3611 | -6.4967 | -6.4861 | -6.4258 | -6.3134 | -6.3562 | -6.2753 | 51.0844 | 0.23032 | 51.0116 | -0.042259 | 0.034501 | 71.8485 | -0.001436 | 71.6223 | 65.3613 | 65.2258 | 65.2363 | 65.2967 | 65.409 | 65.3662 | 65.4471 | 122.8068 | 71.9527 | 122.734 | 71.6802 | 71.7569 | 143.5709 | 71.721 | 143.3448 | 51.0499 | 51.0858 | 50.9771 | 51.013
1757.8906 | 123.0835 | -71.6629 | 51.1551 | -6.1872 | -6.3043 | -6.3167 | -6.238 | -6.144 | -6.2005 | -6.0968 | 51.121 | 0.23032 | 51.0345 | -0.046838 | 0.034501 | 71.8165 | 0.003143 | 71.5811 | 65.4757 | 65.3586 | 65.3462 | 65.4249 | 65.5189 | 65.4624 | 65.5662 | 122.7839 | 71.8932 | 122.6974 | 71.6161 | 71.6974 | 143.4794 | 71.666 | 143.244 | 51.0865 | 51.1179 | 51 | 51.0313
1758.8906 | 123.0972 | -71.7407 | 51.1002 | -5.8117 | -5.9335 | -5.9413 | -5.8672 | -5.7594 | -5.7976 | -5.7168 | 51.0752 | 0.22574 | 50.9795 | -0.042259 | 0.039079 | 71.8439 | 0.012299 | 71.6086 | 65.929 | 65.8073 | 65.7994 | 65.8735 | 65.9813 | 65.9431 | 66.024 | 122.816 | 71.9665 | 122.7202 | 71.6985 | 71.7798 | 143.5846 | 71.753 | 143.3493 | 51.0362 | 51.0629 | 50.9404 | 50.9672
1759.8906 | 123.024 | -71.759 | 51.1414 | -5.4638 | -5.5946 | -5.5796 | -5.5284 | -5.4207 | -5.4405 | -5.3871 | 51.0981 | 0.23032 | 51.0116 | -0.046838 | 0.034501 | 71.8348 | 0.007721 | 71.6178 | 66.2953 | 66.1644 | 66.1795 | 66.2307 | 66.3384 | 66.3185 | 66.3719 | 122.8572 | 71.9894 | 122.7706 | 71.7122 | 71.7935 | 143.5938 | 71.7668 | 143.3768 | 51.0636 | 51.0904 | 50.9771 | 51.0038
1760.8906 | 123.024 | -71.7728 | 51.1276 | -5.3173 | -5.4252 | -5.4376 | -5.3681 | -5.265 | -5.294 | -5.2269 | 51.0432 | 0.23032 | 50.9566 | -0.042259 | 0.034501 | 71.8943 | -0.001436 | 71.6544 | 66.4555 | 66.3476 | 66.3351 | 66.4046 | 66.5078 | 66.4787 | 66.5459 | 122.816 | 72.0031 | 122.7294 | 71.7305 | 71.8073 | 143.667 | 71.7713 | 143.4272 | 51.0087 | 51.0446 | 50.9221 | 50.9581
1761.8906 | 123.0515 | -71.7911 | 51.0773 | -4.9602 | -5.0681 | -5.0759 | -5.0156 | -4.9125 | -4.9506 | -4.8652 | 51.0386 | 0.22574 | 50.9429 | -0.046838 | 0.034501 | 71.8851 | -0.001436 | 71.659 | 66.8309 | 66.723 | 66.7151 | 66.7755 | 66.8786 | 66.8404 | 66.9259 | 122.8297 | 72.0168 | 122.734 | 71.7442 | 71.8256 | 143.6762 | 71.7896 | 143.4501 | 51.0041 | 51.04 | 50.9084 | 50.9443
1762.8906 | 123.0148 | -71.8735 | 50.9949 | -4.3283 | -4.4362 | -4.4578 | -4.3792 | -4.2945 | -4.3097 | -4.2334 | 50.9791 | 0.23032 | 50.8879 | -0.042259 | 0.029923 | 71.9446 | 0.003143 | 71.7231 | 67.5451 | 67.4373 | 67.4157 | 67.4943 | 67.579 | 67.5638 | 67.64 | 122.8526 | 72.1038 | 122.7614 | 71.8312 | 71.9034 | 143.8181 | 71.8766 | 143.5965 | 50.9492 | 50.9759 | 50.858 | 50.8848
1763.8906 | 122.9874 | -71.9055 | 50.9949 | -4.5023 | -4.601 | -4.6089 | -4.5486 | -4.4639 | -4.4745 | -4.4028 | 50.9013 | 0.22116 | 50.8147 | -0.042259 | 0.025345 | 72.0179 | -0.001436 | 71.7734 | 67.4032 | 67.3045 | 67.2966 | 67.3569 | 67.4416 | 67.431 | 67.5027 | 122.8068 | 72.1267 | 122.7202 | 71.8633 | 71.9309 | 143.9234 | 71.9041 | 143.6789 | 50.8759 | 50.9027 | 50.7893 | 50.8161
1764.8906 | 122.9645 | -71.9238 | 50.9171 | -4.2688 | -4.3767 | -4.3891 | -4.3196 | -4.2304 | -4.2364 | -4.1739 | 50.8738 | 0.2349 | 50.7964 | -0.042259 | 0.025345 | 72.0454 | -0.006014 | 71.8101 | 67.655 | 67.5472 | 67.5347 | 67.6042 | 67.6934 | 67.6874 | 67.7499 | 122.7976 | 72.1587 | 122.7202 | 71.8816 | 71.9492 | 143.9692 | 71.9178 | 143.7339 | 50.8484 | 50.8798 | 50.771 | 50.8024
1765.8906 | 122.9919 | -71.9833 | 50.9216 | -4.5344 | -4.6239 | -4.6593 | -4.5898 | -4.4868 | -4.5065 | -4.444 | 50.8555 | 0.23032 | 50.7598 | -0.042259 | 0.034501 | 72.0682 | 0.003143 | 71.8375 | 67.449 | 67.3594 | 67.3241 | 67.3936 | 67.4966 | 67.4768 | 67.5393 | 122.8388 | 72.2137 | 122.7431 | 71.9411 | 72.0178 | 144.0516 | 71.9865 | 143.8209 | 50.821 | 50.8523 | 50.7253 | 50.7566
1766.8906 | 123.0148 | -72.052 | 50.8438 | -4.3421 | -4.4545 | -4.467 | -4.3975 | -4.2945 | -4.3097 | -4.2426 | 50.7776 | 0.22574 | 50.6773 | -0.046838 | 0.029923 | 72.1415 | 0.003143 | 71.9108 | 67.7099 | 67.5975 | 67.585 | 67.6545 | 67.7575 | 67.7423 | 67.8094 | 122.8296 | 72.2777 | 122.7293 | 72.0052 | 72.0819 | 144.1935 | 72.0551 | 143.9628 | 50.7477 | 50.7745 | 50.6474 | 50.6742
1767.8906 | 123.0148 | -72.0337 | 50.8163 | -4.6809 | -4.7933 | -4.8012 | -4.7317 | -4.6378 | -4.6439 | -4.5814 | 50.7639 | 0.22574 | 50.6773 | -0.046838 | 0.039079 | 72.1369 | -0.006014 | 71.9154 | 67.3528 | 67.2404 | 67.2325 | 67.302 | 67.3959 | 67.3898 | 67.4523 | 122.7976 | 72.2594 | 122.711 | 71.9869 | 72.0728 | 144.1706 | 72.0277 | 143.949 | 50.7248 | 50.7699 | 50.6383 | 50.6834
1768.8906 | 123.0194 | -72.02 | 50.8072 | -4.8503 | -4.9582 | -4.966 | -4.9057 | -4.8026 | -4.8179 | -4.7553 | 50.7639 | 0.22574 | 50.6682 | -0.046838 | 0.020767 | 72.1415 | -0.010593 | 71.9062 | 67.1697 | 67.0618 | 67.0539 | 67.1143 | 67.2173 | 67.2021 | 67.2646 | 122.7839 | 72.2457 | 122.6881 | 71.9731 | 72.0407 | 144.1615 | 72.0094 | 143.9262 | 50.7431 | 50.7745 | 50.6474 | 50.6788
1769.8906 | 123.0103 | -72.0428 | 50.8301 | -4.0994 | -4.2027 | -4.2197 | -4.1548 | -4.0519 | -4.067 | -3.9862 | 50.7502 | 0.2349 | 50.6636 | -0.042259 | 0.025345 | 72.1461 | 0.003143 | 71.9199 | 67.9434 | 67.8402 | 67.8231 | 67.888 | 67.991 | 67.9758 | 68.0566 | 122.793 | 72.2777 | 122.7065 | 72.0006 | 72.0682 | 144.1889 | 72.046 | 143.9628 | 50.7248 | 50.747 | 50.6383 | 50.6605
1770.8906 | 122.9919 | -72.0108 | 50.8484 | -4.0491 | -4.1431 | -4.1648 | -4.0999 | -4.0015 | -4.0029 | -3.9313 | 50.7731 | 0.23032 | 50.6865 | -0.03768 | 0.020767 | 72.1323 | 0.003143 | 71.897 | 67.9617 | 67.8677 | 67.846 | 67.9109 | 68.0093 | 68.0079 | 68.0795 | 122.7839 | 72.2411 | 122.6973 | 71.9731 | 72.0316 | 144.1431 | 72.0139 | 143.9078 | 50.7523 | 50.7699 | 50.6657 | 50.6834
1771.8906 | 123.0194 | -72.0108 | 50.8484 | -4.0491 | -4.1157 | -4.1602 | -4.0861 | -3.9878 | -4.0121 | -3.9267 | 50.7547 | 0.23032 | 50.6453 | -0.03768 | 0.034501 | 72.1415 | 0.003143 | 71.9062 | 67.9617 | 67.8951 | 67.8506 | 67.9247 | 68.023 | 67.9987 | 68.0841 | 122.7655 | 72.2411 | 122.6561 | 71.9731 | 72.0453 | 144.1523 | 72.0139 | 143.917 | 50.7202 | 50.7516 | 50.6108 | 50.6422
1772.8906 | 123.0011 | -72.0108 | 50.8347 | -3.8797 | -3.9737 | -3.9862 | -3.9213 | -3.8275 | -3.8381 | -3.771 | 50.7776 | 0.2349 | 50.6911 | -0.03768 | 0.025345 | 72.1186 | -0.006014 | 71.8787 | 68.1311 | 68.0371 | 68.0246 | 68.0895 | 68.1833 | 68.1727 | 68.2398 | 122.7884 | 72.2457 | 122.7019 | 71.9731 | 72.0361 | 144.1294 | 72.0048 | 143.8895 | 50.7523 | 50.7837 | 50.6657 | 50.6971
1773.8906 | 123.0148 | -71.9513 | 50.8667 | -3.7744 | -3.8776 | -3.8992 | -3.8297 | -3.7314 | -3.7419 | -3.6795 | 50.8143 | 0.23032 | 50.714 | -0.042259 | 0.025345 | 72.0682 | -0.001436 | 71.8238 | 68.1769 | 68.0737 | 68.0521 | 68.1215 | 68.2199 | 68.2093 | 68.2718 | 122.7656 | 72.1816 | 122.6653 | 71.909 | 71.9766 | 144.0195 | 71.9499 | 143.7751 | 50.7889 | 50.8157 | 50.6886 | 50.7154
1774.8906 | 122.9691 | -71.965 | 50.8255 | -3.4722 | -3.5616 | -3.5925 | -3.5276 | -3.4201 | -3.4169 | -3.3544 | 50.7914 | 0.2349 | 50.6865 | -0.042259 | 0.029923 | 72.082 | -0.006014 | 71.8375 | 68.4928 | 68.4034 | 68.3726 | 68.4375 | 68.5449 | 68.5481 | 68.6106 | 122.7564 | 72.1999 | 122.6515 | 71.9228 | 71.995 | 144.047 | 71.959 | 143.8025 | 50.7614 | 50.7974 | 50.6566 | 50.6925
1775.8906 | 122.9691 | -72.0154 | 50.7523 | -3.1929 | -3.2823 | -3.304 | -3.2345 | -3.1317 | -3.133 | -3.0706 | 50.7456 | 0.23948 | 50.627 | -0.046838 | 0.029923 | 72.1186 | 0.003143 | 71.865 | 68.8225 | 68.7331 | 68.7114 | 68.7808 | 68.8837 | 68.8824 | 68.9448 | 122.761 | 72.2549 | 122.6424 | 71.9685 | 72.0453 | 144.134 | 72.0185 | 143.8804 | 50.7157 | 50.7424 | 50.5971 | 50.6238
1776.8906 | 123.0011 | -72.0062 | 50.7614 | -3.1654 | -3.2411 | -3.2674 | -3.2071 | -3.1042 | -3.0964 | -3.0477 | 50.7227 | 0.23032 | 50.6087 | -0.042259 | 0.034501 | 72.1278 | 0.003143 | 71.8558 | 68.8408 | 68.7651 | 68.7388 | 68.7992 | 68.902 | 68.9098 | 68.9585 | 122.7289 | 72.2365 | 122.6149 | 71.964 | 72.0407 | 144.134 | 72.0094 | 143.8621 | 50.6882 | 50.7196 | 50.5742 | 50.6055
1777.8906 | 122.9233 | -72.0428 | 50.7614 | -3.7881 | -3.8913 | -3.8901 | -3.8297 | -3.7177 | -3.7328 | -3.6795 | 50.7319 | 0.23032 | 50.6087 | -0.046838 | 0.029923 | 72.0911 | -0.001436 | 71.8284 | 68.2548 | 68.1515 | 68.1528 | 68.2131 | 68.3252 | 68.3101 | 68.3634 | 122.7747 | 72.2732 | 122.6515 | 71.996 | 72.0728 | 144.134 | 72.0414 | 143.8712 | 50.7019 | 50.7333 | 50.5787 | 50.6101
1778.8906 | 122.9553 | -72.0612 | 50.6927 | -2.6847 | -2.7741 | -2.8049 | -2.7401 | -2.6327 | -2.6157 | -2.5624 | 50.6723 | 0.22574 | 50.5766 | -0.03768 | 0.020767 | 72.1827 | -0.001436 | 71.9428 | 69.3765 | 69.2871 | 69.2562 | 69.3211 | 69.4285 | 69.4455 | 69.4988 | 122.7335 | 72.2869 | 122.6378 | 72.0235 | 72.0819 | 144.2439 | 72.0597 | 144.004 | 50.6516 | 50.6738 | 50.5559 | 50.5781
1779.8906 | 122.937 | -72.1298 | 50.6973 | -2.7213 | -2.8107 | -2.8507 | -2.7767 | -2.6739 | -2.6569 | -2.5899 | 50.6494 | 0.23032 | 50.572 | -0.042259 | 0.034501 | 72.2056 | -0.001436 | 71.9794 | 69.4085 | 69.3191 | 69.2791 | 69.3531 | 69.4559 | 69.473 | 69.54 | 122.7793 | 72.3601 | 122.7019 | 72.0876 | 72.1643 | 144.3354 | 72.1284 | 144.1093 | 50.6149 | 50.6509 | 50.5375 | 50.5735
1780.8906 | 122.9141 | -72.0108 | 50.8026 | -4.4703 | -4.5781 | -4.5906 | -4.5165 | -4.4135 | -4.4241 | -4.3662 | 50.7364 | 0.22116 | 50.659 | -0.046838 | 0.034501 | 72.1278 | -0.001436 | 71.9016 | 67.5405 | 67.4327 | 67.4202 | 67.4943 | 67.5973 | 67.5867 | 67.6446 | 122.7472 | 72.232 | 122.6698 | 71.964 | 72.0453 | 144.1386 | 72.0094 | 143.9124 | 50.7019 | 50.7379 | 50.6245 | 50.6605
1781.8906 | 122.9919 | -72.052 | 50.7339 | -4.2047 | -4.3217 | -4.3205 | -4.2464 | -4.148 | -4.154 | -4.1052 | 50.7319 | 0.2349 | 50.6499 | -0.046838 | 0.029923 | 72.1461 | -0.006014 | 71.9199 | 67.8473 | 67.7303 | 67.7315 | 67.8056 | 67.904 | 67.898 | 67.9468 | 122.7839 | 72.2869 | 122.7019 | 72.0052 | 72.0819 | 144.1981 | 72.046 | 143.9719 | 50.7019 | 50.7379 | 50.62 | 50.6559
1782.8906 | 122.9095 | -72.1069 | 50.7248 | -3.0968 | -3.1999 | -3.2124 | -3.1476 | -3.0401 | -3.0277 | -2.9973 | 50.6769 | 0.23032 | 50.5904 | -0.042259 | 0.029923 | 72.1964 | -0.001436 | 71.9657 | 69.0102 | 68.907 | 68.8945 | 68.9594 | 69.0668 | 69.0792 | 69.1096 | 122.7838 | 72.3373 | 122.6973 | 72.0647 | 72.1369 | 144.3034 | 72.1055 | 144.0726 | 50.647 | 50.6783 | 50.5604 | 50.5918
1783.8906 | 122.9324 | -72.2031 | 50.6561 | -3.7332 | -3.8409 | -3.8489 | -3.7702 | -3.6765 | -3.6733 | -3.6291 | 50.6082 | 0.2349 | 50.5446 | -0.046838 | 0.020767 | 72.2743 | -0.001436 | 72.0481 | 68.4699 | 68.3621 | 68.3542 | 68.4328 | 68.5266 | 68.5298 | 68.5739 | 122.8113 | 72.438 | 122.7476 | 72.1562 | 72.2238 | 144.4773 | 72.2016 | 144.2512 | 50.5875 | 50.6097 | 50.5238 | 50.546
1784.8906 | 122.9782 | -72.0886 | 50.7019 | -4.69 | -4.8071 | -4.815 | -4.7363 | -4.6241 | -4.6347 | -4.586 | 50.6998 | 0.23032 | 50.6041 | -0.046838 | 0.029923 | 72.1919 | 0.003143 | 71.9566 | 67.3986 | 67.2816 | 67.2737 | 67.3523 | 67.4645 | 67.4539 | 67.5027 | 122.7884 | 72.3189 | 122.6927 | 72.0418 | 72.1185 | 144.2805 | 72.0918 | 144.0452 | 50.6699 | 50.6967 | 50.5742 | 50.601
1785.8906 | 123.024 | -72.0749 | 50.7019 | -5.3127 | -5.4252 | -5.4285 | -5.3452 | -5.233 | -5.2482 | -5.1994 | 50.7181 | 0.2349 | 50.6453 | -0.051417 | 0.034501 | 72.1644 | 0.003143 | 71.9428 | 66.7622 | 66.6497 | 66.6464 | 66.7297 | 66.8419 | 66.8267 | 66.8755 | 122.793 | 72.3098 | 122.7202 | 72.0235 | 72.1094 | 144.2393 | 72.078 | 144.0177 | 50.6836 | 50.715 | 50.6108 | 50.6422
1786.8906 | 123.0606 | -72.0978 | 50.6882 | -5.6744 | -5.8053 | -5.7948 | -5.7161 | -5.6038 | -5.6191 | -5.5748 | 50.6952 | 0.2349 | 50.6087 | -0.042259 | 0.029923 | 72.1919 | -0.001436 | 71.9611 | 66.4234 | 66.2925 | 66.303 | 66.3817 | 66.494 | 66.4787 | 66.5229 | 122.793 | 72.3327 | 122.7065 | 72.0555 | 72.1277 | 144.2896 | 72.0963 | 144.0589 | 50.6653 | 50.6967 | 50.5787 | 50.6101
1787.8906 | 123.0835 | -72.0749 | 50.679 | -5.7568 | -5.9014 | -5.8955 | -5.7939 | -5.6862 | -5.7061 | -5.671 | 50.6952 | 0.22574 | 50.627 | -0.046838 | 0.020767 | 72.1781 | -0.001436 | 71.9566 | 66.3181 | 66.1735 | 66.1794 | 66.281 | 66.3887 | 66.3688 | 66.4039 | 122.7701 | 72.3006 | 122.7019 | 72.0281 | 72.0957 | 144.253 | 72.0735 | 144.0314 | 50.6745 | 50.6967 | 50.6062 | 50.6284
1788.8906 | 123.0972 | -71.9559 | 50.8209 | -6.4161 | -6.547 | -6.5411 | -6.4532 | -6.3363 | -6.3608 | -6.3165 | 50.8143 | 0.23032 | 50.7277 | -0.042259 | 0.029923 | 72.0637 | 0.003143 | 71.8421 | 65.5398 | 65.4089 | 65.4148 | 65.5026 | 65.6196 | 65.5951 | 65.6394 | 122.7701 | 72.1862 | 122.6836 | 71.9136 | 71.9858 | 144.0195 | 71.959 | 143.798 | 50.7843 | 50.8111 | 50.6978 | 50.7246
1789.8906 | 123.1247 | -71.8918 | 50.8438 | -6.5351 | -6.6706 | -6.6556 | -6.5723 | -6.4507 | -6.4798 | -6.431 | 50.8784 | 0.22574 | 50.8147 | -0.051417 | 0.034501 | 72.0179 | 0.007721 | 71.7872 | 65.3567 | 65.2211 | 65.2362 | 65.3195 | 65.4411 | 65.412 | 65.4608 | 122.7701 | 72.1175 | 122.7065 | 71.8404 | 71.9263 | 143.9097 | 71.8995 | 143.6789 | 50.8439 | 50.8706 | 50.7802 | 50.807
1790.8906 | 123.0881 | -71.9238 | 50.8255 | -6.1368 | -6.2677 | -6.2618 | -6.1785 | -6.0616 | -6.0907 | -6.0372 | 50.8509 | 0.23032 | 50.7689 | -0.042259 | 0.034501 | 72.0408 | -0.001436 | 71.8101 | 65.787 | 65.6561 | 65.662 | 65.7453 | 65.8623 | 65.8332 | 65.8866 | 122.7747 | 72.1541 | 122.6927 | 71.8816 | 71.9583 | 143.9646 | 71.9224 | 143.7339 | 50.8164 | 50.8523 | 50.7344 | 50.7703
1791.8906 | 123.111 | -72.0108 | 50.7614 | -5.8484 | -5.9747 | -5.9596 | -5.8901 | -5.7732 | -5.7839 | -5.7351 | 50.7731 | 0.2349 | 50.6819 | -0.042259 | 0.029923 | 72.1186 | 0.003143 | 71.897 | 66.1624 | 66.0361 | 66.0512 | 66.1207 | 66.2376 | 66.2269 | 66.2757 | 122.7839 | 72.2457 | 122.6927 | 71.9685 | 72.0407 | 144.1294 | 72.0139 | 143.9078 | 50.7431 | 50.7699 | 50.652 | 50.6788
1792.8906 | 123.0469 | -72.0062 | 50.7935 | -6.1048 | -6.2311 | -6.2389 | -6.151 | -6.0341 | -6.0403 | -5.996 | 50.8097 | 0.2349 | 50.7369 | -0.051417 | 0.034501 | 72.0866 | -0.001436 | 71.8604 | 65.9015 | 65.7751 | 65.7673 | 65.8552 | 65.9721 | 65.9659 | 66.0102 | 122.8159 | 72.2411 | 122.7431 | 71.9548 | 72.0407 | 144.0928 | 72.0048 | 143.8666 | 50.7752 | 50.8111 | 50.7024 | 50.7383
1793.8906 | 123.0652 | -71.9696 | 50.8255 | -6.0086 | -6.1349 | -6.1427 | -6.0549 | -5.9334 | -5.9396 | -5.9045 | 50.8234 | 0.2349 | 50.7323 | -0.03768 | 0.025345 | 72.0728 | 0.003143 | 71.8421 | 65.961 | 65.8347 | 65.8269 | 65.9147 | 66.0362 | 66.03 | 66.0651 | 122.793 | 72.2045 | 122.7019 | 71.9319 | 71.9949 | 144.0424 | 71.9727 | 143.8117 | 50.7981 | 50.8203 | 50.7069 | 50.7291
1794.8906 | 123.0606 | -71.9833 | 50.798 | -5.7476 | -5.8877 | -5.8909 | -5.7939 | -5.677 | -5.6832 | -5.6344 | 50.8051 | 0.23032 | 50.7277 | -0.042259 | 0.034501 | 72.0866 | -0.001436 | 71.865 | 66.2357 | 66.0957 | 66.0924 | 66.1894 | 66.3063 | 66.3002 | 66.349 | 122.7884 | 72.2137 | 122.711 | 71.9411 | 72.0178 | 144.0699 | 71.9819 | 143.8483 | 50.7706 | 50.8065 | 50.6932 | 50.7291
1795.8906 | 123.0469 | -71.9833 | 50.8118 | -5.5325 | -5.677 | -5.6757 | -5.5879 | -5.4619 | -5.4588 | -5.4146 | 50.8005 | 0.23032 | 50.7231 | -0.042259 | 0.020767 | 72.0957 | 0.003143 | 71.8833 | 66.4509 | 66.3063 | 66.3076 | 66.3954 | 66.5215 | 66.5245 | 66.5687 | 122.7839 | 72.2137 | 122.7065 | 71.9411 | 72.0041 | 144.079 | 71.9865 | 143.8666 | 50.7798 | 50.7974 | 50.7024 | 50.72
1796.8906 | 123.0927 | -71.9971 | 50.7523 | -5.9216 | -6.0617 | -6.0558 | -5.9725 | -5.8327 | -5.8343 | -5.7992 | 50.7868 | 0.22574 | 50.7002 | -0.03768 | 0.025345 | 72.1049 | 0.003143 | 71.8741 | 66.0754 | 65.9354 | 65.9413 | 66.0246 | 66.1644 | 66.1628 | 66.1979 | 122.7839 | 72.2228 | 122.6973 | 71.9594 | 72.0224 | 144.1019 | 72.0002 | 143.8712 | 50.7614 | 50.7837 | 50.6749 | 50.6971
1797.8906 | 123.0469 | -72.1069 | 50.6927 | -4.9739 | -5.1001 | -5.108 | -5.0064 | -4.885 | -4.8774 | -4.8515 | 50.6952 | 0.22574 | 50.6133 | -0.042259 | 0.025345 | 72.2102 | -0.001436 | 71.9749 | 67.133 | 67.0068 | 66.9989 | 67.1005 | 67.2219 | 67.2295 | 67.2554 | 122.8022 | 72.3327 | 122.7202 | 72.0647 | 72.1323 | 144.3171 | 72.1055 | 144.0818 | 50.6699 | 50.6967 | 50.5879 | 50.6147
1798.8906 | 123.0972 | -72.1115 | 50.6607 | -3.9071 | -4.0745 | -4.0595 | -3.9396 | -3.7772 | -3.7923 | -3.8122 | 50.6723 | 0.22574 | 50.6041 | -0.046838 | 0.039079 | 72.2193 | -0.001436 | 71.9886 | 68.2044 | 68.0371 | 68.052 | 68.1719 | 68.3343 | 68.3192 | 68.2993 | 122.7838 | 72.3372 | 122.7156 | 72.0647 | 72.1506 | 144.3308 | 72.1101 | 144.1001 | 50.6333 | 50.6738 | 50.565 | 50.6055
1799.8906 | 123.056 | -72.0886 | 50.7294 | -4.0307 | -4.2072 | -4.1877 | -4.0404 | -3.8916 | -3.9205 | -3.9267 | 50.7135 | 0.23032 | 50.6178 | -0.046838 | 0.025345 | 72.1873 | -0.001436 | 71.952 | 68.0579 | 67.8814 | 67.9009 | 68.0483 | 68.197 | 68.1681 | 68.1619 | 122.8022 | 72.3189 | 122.7065 | 72.0418 | 72.114 | 144.2759 | 72.0872 | 144.0406 | 50.6882 | 50.715 | 50.5925 | 50.6193
1800.8906 | 123.0469 | -72.1802 | 50.6332 | -3.9895 | -4.1706 | -4.1327 | -3.9854 | -3.8275 | -3.8701 | -3.8855 | 50.6449 | 0.22574 | 50.5812 | -0.046838 | 0.029923 | 72.2468 | 0.003143 | 72.0206 | 68.1906 | 68.0096 | 68.0474 | 68.1948 | 68.3526 | 68.31 | 68.2947 | 122.825 | 72.4059 | 122.7614 | 72.1333 | 72.2101 | 144.427 | 72.1833 | 144.2008 | 50.6149 | 50.6417 | 50.5513 | 50.5781
1801.8906 | 123.0652 | -72.1619 | 50.6287 | -3.3577 | -3.5433 | -3.5055 | -3.3536 | -3.1958 | -3.2246 | -3.2629 | 50.6265 | 0.23032 | 50.5583 | -0.042259 | 0.029923 | 72.2605 | 0.003143 | 72.0298 | 68.8041 | 68.6185 | 68.6564 | 68.8083 | 68.9661 | 68.9373 | 68.899 | 122.7884 | 72.3922 | 122.7202 | 72.1196 | 72.1918 | 144.4224 | 72.165 | 144.1917 | 50.5966 | 50.6234 | 50.5284 | 50.5552
1802.8906 | 123.0515 | -72.2809 | 50.5325 | -1.0273 | -1.2035 | -1.1887 | -1.046 | -0.86559 | -0.88504 | -0.90968 | 50.5167 | 0.2349 | 50.4255 | -0.042259 | 0.025345 | 72.3704 | 0.003143 | 72.1488 | 71.2536 | 71.0773 | 71.0922 | 71.2349 | 71.4153 | 71.3958 | 71.3712 | 122.7975 | 72.5158 | 122.7064 | 72.2386 | 72.3062 | 144.6513 | 72.284 | 144.4297 | 50.4913 | 50.5135 | 50.4002 | 50.4224
1803.8906 | 123.0423 | -72.3084 | 50.4684 | -0.029236 | -0.15957 | -0.14936 | -0.020438 | 0.11867 | 0.1039 | 0.083784 | 50.4846 | 0.23032 | 50.3981 | -0.042259 | 0.029923 | 72.407 | 0.003143 | 72.1809 | 72.2791 | 72.1488 | 72.159 | 72.2879 | 72.427 | 72.4122 | 72.3921 | 122.793 | 72.5387 | 122.7064 | 72.2661 | 72.3383 | 144.7154 | 72.3115 | 144.4892 | 50.4547 | 50.4815 | 50.3681 | 50.3949
1804.8906 | 123.0331 | -72.3038 | 50.5096 | 0.30041 | 0.15179 | 0.16657 | 0.31379 | 0.45744 | 0.4427 | 0.41341 | 50.5167 | 0.23032 | 50.4393 | -0.042259 | 0.029923 | 72.375 | 0.003143 | 72.1626 | 72.6042 | 72.4556 | 72.4703 | 72.6176 | 72.7612 | 72.7465 | 72.7172 | 122.8204 | 72.5341 | 122.743 | 72.2615 | 72.3337 | 144.6787 | 72.3069 | 144.4663 | 50.4867 | 50.5135 | 50.4094 | 50.4361
1805.8906 | 123.0652 | -72.3312 | 50.4456 | 0.84066 | 0.67378 | 0.70226 | 0.87695 | 1.0205 | 0.9921 | 0.98111 | 50.4434 | 0.23032 | 50.3569 | -0.042259 | 0.034501 | 72.4436 | 0.003143 | 72.2175 | 73.1719 | 73.005 | 73.0335 | 73.2082 | 73.3518 | 73.3233 | 73.3123 | 122.7746 | 72.5616 | 122.6881 | 72.289 | 72.3657 | 144.7749 | 72.3344 | 144.5487 | 50.4089 | 50.4403 | 50.3224 | 50.3537
1806.8906 | 123.0927 | -72.3724 | 50.3998 | 0.46523 | 0.30289 | 0.32224 | 0.49235 | 0.64513 | 0.63041 | 0.6057 | 50.4388 | 0.2349 | 50.3614 | -0.03768 | 0.034501 | 72.4665 | 0.003143 | 72.2404 | 72.8377 | 72.6753 | 72.6947 | 72.8648 | 73.0176 | 73.0028 | 72.9781 | 122.8113 | 72.6073 | 122.7339 | 72.3348 | 72.4069 | 144.839 | 72.3756 | 144.6128 | 50.4043 | 50.4357 | 50.3269 | 50.3583
1807.8906 | 123.0652 | -72.377 | 50.4181 | 0.89102 | 0.7104 | 0.72515 | 0.92273 | 1.0709 | 1.047 | 1.0269 | 50.4342 | 0.23032 | 50.3523 | -0.046838 | 0.039079 | 72.4665 | 0.003143 | 72.245 | 73.268 | 73.0874 | 73.1022 | 73.2997 | 73.4479 | 73.4241 | 73.4039 | 122.8113 | 72.6073 | 122.7293 | 72.3302 | 72.4161 | 144.8435 | 72.3802 | 144.622 | 50.3952 | 50.4311 | 50.3132 | 50.3491
1808.8906 | 123.0972 | -72.3312 | 50.4227 | 1.3443 | 1.1683 | 1.1876 | 1.3714 | 1.5333 | 1.5049 | 1.4984 | 50.4251 | 0.22574 | 50.3569 | -0.03768 | 0.034501 | 72.4574 | 0.003143 | 72.2312 | 73.6755 | 73.4995 | 73.5188 | 73.7027 | 73.8645 | 73.8361 | 73.8297 | 122.7563 | 72.557 | 122.6881 | 72.2936 | 72.3657 | 144.7886 | 72.3344 | 144.5625 | 50.3906 | 50.4219 | 50.3224 | 50.3537
1809.8906 | 123.0469 | -72.4228 | 50.354 | 1.4038 | 1.2141 | 1.238 | 1.4264 | 1.5973 | 1.5598 | 1.5534 | 50.3976 | 0.22574 | 50.3111 | -0.042259 | 0.034501 | 72.4986 | -0.001436 | 72.2724 | 73.8266 | 73.6369 | 73.6608 | 73.8492 | 74.0201 | 73.9826 | 73.9762 | 122.8204 | 72.6485 | 122.7339 | 72.3805 | 72.4573 | 144.9214 | 72.4214 | 144.6952 | 50.3631 | 50.3991 | 50.2766 | 50.3125
1810.8906 | 123.0515 | -72.4182 | 50.3906 | 1.6465 | 1.4613 | 1.4898 | 1.6873 | 1.8446 | 1.8116 | 1.7914 | 50.3976 | 0.22574 | 50.3248 | -0.042259 | 0.034501 | 72.494 | 0.003143 | 72.2679 | 74.0647 | 73.8795 | 73.908 | 74.1056 | 74.2628 | 74.2298 | 74.2097 | 122.8158 | 72.644 | 122.743 | 72.376 | 72.4527 | 144.9122 | 72.4214 | 144.6861 | 50.3631 | 50.3945 | 50.2903 | 50.3217
1811.8906 | 123.056 | -72.3633 | 50.3769 | 2.4294 | 2.258 | 2.2727 | 2.4748 | 2.6274 | 2.6083 | 2.5972 | 50.3839 | 0.22574 | 50.2973 | -0.046838 | 0.034501 | 72.5077 | 0.003143 | 72.2862 | 74.7926 | 74.6213 | 74.636 | 74.8381 | 74.9907 | 74.9716 | 74.9605 | 122.7472 | 72.589 | 122.6606 | 72.3164 | 72.3978 | 144.871 | 72.3664 | 144.6495 | 50.3494 | 50.3807 | 50.2628 | 50.2942
1812.8906 | 123.0743 | -72.3175 | 50.4684 | 2.2233 | 2.0566 | 2.0758 | 2.2734 | 2.4305 | 2.3931 | 2.3866 | 50.4709 | 0.23032 | 50.3752 | -0.046838 | 0.025345 | 72.4253 | 0.003143 | 72.2038 | 74.5408 | 74.3741 | 74.3933 | 74.5909 | 74.748 | 74.7106 | 74.7041 | 122.7884 | 72.5478 | 122.6927 | 72.2707 | 72.3428 | 144.7428 | 72.3206 | 144.5213 | 50.4455 | 50.4677 | 50.3498 | 50.372
1813.8906 | 123.0835 | -72.3587 | 50.3998 | 2.2325 | 2.0703 | 2.085 | 2.2917 | 2.4351 | 2.4022 | 2.3958 | 50.4159 | 0.22574 | 50.3477 | -0.042259 | 0.025345 | 72.4711 | -0.001436 | 72.2541 | 74.5912 | 74.429 | 74.4437 | 74.6504 | 74.7938 | 74.761 | 74.7545 | 122.7746 | 72.5844 | 122.7064 | 72.3164 | 72.384 | 144.8298 | 72.3573 | 144.6128 | 50.3906 | 50.4174 | 50.3224 | 50.3491
1814.8906 | 123.0331 | -72.4136 | 50.386 | 2.8139 | 2.6472 | 2.6573 | 2.8594 | 3.0119 | 2.9837 | 2.9726 | 50.3885 | 0.23032 | 50.3111 | -0.051417 | 0.025345 | 72.5032 | -0.006014 | 72.2724 | 75.2276 | 75.0609 | 75.071 | 75.2731 | 75.4256 | 75.3973 | 75.3862 | 122.8021 | 72.644 | 122.7247 | 72.3622 | 72.439 | 144.9168 | 72.4076 | 144.6861 | 50.3631 | 50.3945 | 50.2857 | 50.3171
1815.8906 | 123.111 | -72.4091 | 50.386 | 3.1482 | 2.9907 | 3.0053 | 3.212 | 3.3599 | 3.3271 | 3.3297 | 50.361 | 0.23032 | 50.2973 | -0.046838 | 0.029923 | 72.5169 | -0.001436 | 72.2953 | 75.5572 | 75.3997 | 75.4144 | 75.621 | 75.7689 | 75.7361 | 75.7388 | 122.7701 | 72.6394 | 122.7064 | 72.3622 | 72.439 | 144.926 | 72.4076 | 144.7044 | 50.3311 | 50.3624 | 50.2674 | 50.2988
1816.8906 | 123.0606 | -72.3495 | 50.4318 | 3.1939 | 3.0227 | 3.0465 | 3.2578 | 3.4056 | 3.3637 | 3.3618 | 50.4251 | 0.23032 | 50.3386 | -0.042259 | 0.025345 | 72.462 | 0.003143 | 72.2404 | 75.5435 | 75.3723 | 75.3961 | 75.6073 | 75.7552 | 75.7133 | 75.7113 | 122.7746 | 72.5799 | 122.6881 | 72.3073 | 72.3749 | 144.8115 | 72.3527 | 144.5899 | 50.3997 | 50.4219 | 50.3132 | 50.3354
1817.8906 | 123.0469 | -72.2534 | 50.528 | 3.3084 | 3.1326 | 3.1701 | 3.386 | 3.5201 | 3.4782 | 3.4625 | 50.4892 | 0.23032 | 50.421 | -0.042259 | 0.034501 | 72.3796 | 0.007721 | 72.1534 | 75.5618 | 75.386 | 75.4235 | 75.6394 | 75.7735 | 75.7316 | 75.7159 | 122.7426 | 72.4837 | 122.6744 | 72.2112 | 72.2879 | 144.633 | 72.2611 | 144.4068 | 50.4547 | 50.4815 | 50.3865 | 50.4132
1818.8906 | 123.0606 | -72.2488 | 50.5051 | 3.6747 | 3.5081 | 3.5456 | 3.7522 | 3.9001 | 3.8444 | 3.847 | 50.4892 | 0.22116 | 50.4118 | -0.046838 | 0.025345 | 72.3841 | -0.001436 | 72.1626 | 75.9235 | 75.7569 | 75.7944 | 76.0011 | 76.1489 | 76.0933 | 76.0959 | 122.738 | 72.47 | 122.6606 | 72.202 | 72.2742 | 144.633 | 72.2474 | 144.4114 | 50.4638 | 50.4906 | 50.3865 | 50.4132
1819.8906 | 123.1064 | -72.2443 | 50.4776 | 4.4026 | 4.2407 | 4.2782 | 4.4894 | 4.628 | 4.577 | 4.5841 | 50.4846 | 0.2349 | 50.4072 | -0.042259 | 0.034501 | 72.3933 | 0.003143 | 72.1626 | 76.6469 | 76.4849 | 76.5224 | 76.7336 | 76.8722 | 76.8212 | 76.8284 | 122.7289 | 72.4792 | 122.6515 | 72.202 | 72.2788 | 144.6375 | 72.2474 | 144.4068 | 50.4501 | 50.4815 | 50.3727 | 50.4041
1820.8906 | 123.0881 | -72.2992 | 50.4456 | 4.5034 | 4.3323 | 4.388 | 4.6038 | 4.7378 | 4.6777 | 4.662 | 50.4617 | 0.2349 | 50.3706 | -0.03768 | 0.029923 | 72.4116 | -0.001436 | 72.19 | 76.8026 | 76.6314 | 76.6872 | 76.903 | 77.037 | 76.9769 | 76.9612 | 122.7609 | 72.5341 | 122.6698 | 72.2615 | 72.3291 | 144.7108 | 72.2978 | 144.4892 | 50.4318 | 50.4632 | 50.3407 | 50.372
1821.8906 | 123.0652 | -72.2946 | 50.4501 | 4.4438 | 4.2681 | 4.3148 | 4.5352 | 4.692 | 4.6273 | 4.607 | 50.448 | 0.22574 | 50.3706 | -0.046838 | 0.029923 | 72.4162 | 0.007721 | 72.1855 | 76.7385 | 76.5628 | 76.6094 | 76.8298 | 76.9867 | 76.922 | 76.9016 | 122.7426 | 72.5204 | 122.6652 | 72.2478 | 72.3245 | 144.7108 | 72.3023 | 144.4801 | 50.4181 | 50.4403 | 50.3407 | 50.3629
1822.8906 | 123.0286 | -72.2992 | 50.473 | 4.2882 | 4.0987 | 4.1545 | 4.3795 | 4.5318 | 4.4625 | 4.4376 | 50.4617 | 0.23032 | 50.3843 | -0.051417 | 0.034501 | 72.3933 | -0.001436 | 72.1672 | 76.5874 | 76.3979 | 76.4537 | 76.6787 | 76.831 | 76.7617 | 76.7368 | 122.7609 | 72.5295 | 122.6835 | 72.2478 | 72.3337 | 144.6925 | 72.2978 | 144.4663 | 50.4272 | 50.4632 | 50.3498 | 50.3858
1823.8906 | 123.0652 | -72.2122 | 50.5234 | 3.6701 | 3.476 | 3.5364 | 3.7751 | 3.9138 | 3.8399 | 3.8104 | 50.5029 | 0.23032 | 50.4347 | -0.046838 | 0.025345 | 72.3429 | -0.001436 | 72.1214 | 75.8823 | 75.6882 | 75.7486 | 75.9874 | 76.126 | 76.0521 | 76.0226 | 122.7151 | 72.4425 | 122.6469 | 72.1654 | 72.2376 | 144.5551 | 72.2108 | 144.3336 | 50.4776 | 50.5044 | 50.4094 | 50.4361
1824.8906 | 123.0469 | -72.1573 | 50.6104 | 2.0081 | 1.7956 | 1.8698 | 2.1131 | 2.2383 | 2.123 | 2.1028 | 50.5808 | 0.23032 | 50.4896 | -0.042259 | 0.029923 | 72.288 | 0.003143 | 72.0481 | 74.1654 | 73.9529 | 74.0271 | 74.2704 | 74.3956 | 74.2803 | 74.26 | 122.738 | 72.3876 | 122.6469 | 72.115 | 72.1872 | 144.4453 | 72.1604 | 144.2054 | 50.5508 | 50.5776 | 50.4597 | 50.4865
1825.8906 | 122.9553 | -72.139 | 50.6699 | 1.4679 | 1.2415 | 1.3341 | 1.5775 | 1.6843 | 1.5507 | 1.5351 | 50.5991 | 0.2349 | 50.508 | -0.042259 | 0.025345 | 72.2468 | 0.003143 | 72.0161 | 73.6069 | 73.3805 | 73.4731 | 73.7164 | 73.8233 | 73.6896 | 73.674 | 122.7381 | 72.3739 | 122.6469 | 72.0967 | 72.1643 | 144.3858 | 72.1421 | 144.155 | 50.5737 | 50.5959 | 50.4826 | 50.5048
1826.8906 | 122.937 | -72.1756 | 50.6287 | 1.9257 | 1.7223 | 1.8194 | 2.049 | 2.1375 | 2.0085 | 2.0112 | 50.5808 | 0.22574 | 50.4759 | -0.042259 | 0.029923 | 72.2697 | 0.003143 | 72.0344 | 74.1013 | 73.8979 | 73.995 | 74.2246 | 74.3131 | 74.1841 | 74.1868 | 122.7564 | 72.4013 | 122.6515 | 72.1333 | 72.2055 | 144.4453 | 72.1787 | 144.21 | 50.5508 | 50.5776 | 50.446 | 50.4728
1827.8906 | 122.9416 | -72.139 | 50.6607 | 2.4843 | 2.2947 | 2.3872 | 2.6305 | 2.7144 | 2.5716 | 2.556 | 50.5945 | 0.23032 | 50.5034 | -0.042259 | 0.039079 | 72.2422 | -0.001436 | 72.0161 | 74.6233 | 74.4337 | 74.5262 | 74.7695 | 74.8533 | 74.7106 | 74.695 | 122.7335 | 72.3693 | 122.6423 | 72.0967 | 72.1781 | 144.3812 | 72.1375 | 144.155 | 50.5554 | 50.5959 | 50.4643 | 50.5048
1828.8906 | 123.0469 | -72.1069 | 50.6149 | 2.6674 | 2.4687 | 2.5703 | 2.8228 | 2.8838 | 2.7273 | 2.73 | 50.6403 | 0.23032 | 50.5537 | -0.042259 | 0.029923 | 72.1919 | -0.001436 | 71.952 | 74.7744 | 74.5756 | 74.6773 | 74.9297 | 74.9907 | 74.8342 | 74.8369 | 122.7472 | 72.3373 | 122.6607 | 72.0647 | 72.1369 | 144.2988 | 72.1055 | 144.0589 | 50.6104 | 50.6417 | 50.5238 | 50.5552
1829.8906 | 122.8958 | -72.1436 | 50.6561 | 2.5484 | 2.3634 | 2.465 | 2.7221 | 2.7693 | 2.5854 | 2.6201 | 50.6265 | 0.23032 | 50.54 | -0.051417 | 0.029923 | 72.2102 | 0.003143 | 71.9703 | 74.692 | 74.5069 | 74.6086 | 74.8656 | 74.9129 | 74.7289 | 74.7636 | 122.7701 | 72.3739 | 122.6836 | 72.0921 | 72.1735 | 144.3537 | 72.1467 | 144.1138 | 50.5966 | 50.6234 | 50.5101 | 50.5369
1830.8906 | 122.8729 | -72.1207 | 50.647 | 2.1638 | 1.9787 | 2.0713 | 2.3421 | 2.3619 | 2.2054 | 2.2172 | 50.5945 | 0.23032 | 50.4896 | -0.042259 | 0.039079 | 72.2239 | 0.003143 | 71.9886 | 74.2845 | 74.0994 | 74.1919 | 74.4627 | 74.4825 | 74.326 | 74.3379 | 122.7152 | 72.351 | 122.6103 | 72.0784 | 72.1597 | 144.3446 | 72.1238 | 144.1093 | 50.5554 | 50.5914 | 50.4506 | 50.4865
1831.8906 | 122.9095 | -72.1344 | 50.6744 | 2.878 | 2.6839 | 2.8038 | 3.0563 | 3.1172 | 2.9242 | 2.9223 | 50.5853 | 0.23032 | 50.5034 | -0.03768 | 0.034501 | 72.2285 | -0.006014 | 71.984 | 75.0124 | 74.8183 | 74.9382 | 75.1907 | 75.2516 | 75.0586 | 75.0567 | 122.7197 | 72.3647 | 122.6378 | 72.0967 | 72.1689 | 144.3629 | 72.1284 | 144.1184 | 50.5508 | 50.5914 | 50.4689 | 50.5094
1832.8906 | 122.9187 | -72.0703 | 50.7339 | 3.432 | 3.2333 | 3.3762 | 3.6424 | 3.6757 | 3.4736 | 3.4762 | 50.6586 | 0.23948 | 50.572 | -0.03768 | 0.039079 | 72.1506 | -0.001436 | 71.9108 | 75.5023 | 75.3036 | 75.4465 | 75.7127 | 75.7461 | 75.5439 | 75.5465 | 122.7289 | 72.3098 | 122.6424 | 72.0326 | 72.1094 | 144.221 | 72.0689 | 143.9811 | 50.6195 | 50.66 | 50.533 | 50.5735
1833.8906 | 122.9736 | -72.0474 | 50.6516 | 3.5465 | 3.3615 | 3.4952 | 3.7706 | 3.8177 | 3.5835 | 3.5861 | 50.6769 | 0.2349 | 50.5995 | -0.03768 | 0.029923 | 72.1278 | -0.001436 | 71.8741 | 75.5939 | 75.409 | 75.5426 | 75.818 | 75.8651 | 75.6309 | 75.6335 | 122.7243 | 72.2823 | 122.6469 | 72.0097 | 72.0773 | 144.1752 | 72.046 | 143.9216 | 50.647 | 50.6783 | 50.5696 | 50.601
1834.8906 | 122.9279 | -72.0337 | 50.7065 | 4.0547 | 3.8377 | 3.976 | 4.2788 | 4.3533 | 4.11 | 4.0851 | 50.6632 | 0.23948 | 50.572 | -0.03768 | 0.034501 | 72.1278 | -0.001436 | 71.8787 | 76.0884 | 75.8714 | 76.0097 | 76.3125 | 76.387 | 76.1437 | 76.1188 | 122.6969 | 72.2732 | 122.6057 | 71.996 | 72.0682 | 144.1614 | 72.0323 | 143.9124 | 50.6287 | 50.6646 | 50.5375 | 50.5735
1835.8906 | 122.9324 | -72.02 | 50.6973 | 4.0776 | 3.8698 | 4.0172 | 4.3154 | 4.3807 | 4.1466 | 4.0988 | 50.654 | 0.22574 | 50.5629 | -0.03768 | 0.029923 | 72.1278 | -0.001436 | 71.8879 | 76.0975 | 75.8897 | 76.0371 | 76.3354 | 76.4007 | 76.1666 | 76.1188 | 122.674 | 72.2457 | 122.5828 | 71.9823 | 72.0499 | 144.1477 | 72.0185 | 143.9078 | 50.6241 | 50.6555 | 50.533 | 50.5643
1836.8906 | 122.905 | -72.0337 | 50.6836 | 4.1966 | 3.9888 | 4.1408 | 4.4573 | 4.5181 | 4.2611 | 4.2225 | 50.6265 | 0.23032 | 50.5308 | -0.03768 | 0.029923 | 72.1506 | 0.003143 | 71.9108 | 76.2303 | 76.0225 | 76.1745 | 76.491 | 76.5518 | 76.2948 | 76.2561 | 122.6602 | 72.264 | 122.5645 | 71.996 | 72.0636 | 144.1843 | 72.0368 | 143.9445 | 50.5966 | 50.6234 | 50.5009 | 50.5277
1837.8906 | 122.8775 | -72.0566 | 50.6516 | 4.5446 | 4.3551 | 4.4979 | 4.8007 | 4.866 | 4.6182 | 4.5841 | 50.6403 | 0.22116 | 50.5446 | -0.03768 | 0.025345 | 72.1415 | 0.003143 | 71.8925 | 76.6012 | 76.4117 | 76.5545 | 76.8573 | 76.9226 | 76.6748 | 76.6407 | 122.6969 | 72.2777 | 122.6012 | 72.0189 | 72.0819 | 144.1981 | 72.0597 | 143.949 | 50.6149 | 50.6371 | 50.5192 | 50.5414
1838.8906 | 122.8592 | -72.0657 | 50.6241 | 3.9723 | 3.7462 | 3.9119 | 4.2192 | 4.28 | 4.0138 | 3.9569 | 50.6403 | 0.23032 | 50.5446 | -0.046838 | 0.029923 | 72.1232 | -0.001436 | 71.8787 | 76.038 | 75.8119 | 75.9776 | 76.285 | 76.3458 | 76.0796 | 76.0227 | 122.706 | 72.2961 | 122.6103 | 72.0189 | 72.0957 | 144.1889 | 72.0643 | 143.9445 | 50.6104 | 50.6417 | 50.5147 | 50.546
1839.8906 | 122.85 | -72.0154 | 50.6927 | 4.1875 | 3.9751 | 4.1408 | 4.4528 | 4.486 | 4.2382 | 4.1904 | 50.6632 | 0.23032 | 50.5354 | -0.03768 | 0.029923 | 72.1003 | -0.006014 | 71.8467 | 76.2028 | 75.9905 | 76.1562 | 76.4681 | 76.5014 | 76.2536 | 76.2058 | 122.6786 | 72.2457 | 122.5508 | 71.9777 | 72.0453 | 144.1157 | 72.0094 | 143.8621 | 50.6333 | 50.6692 | 50.5055 | 50.5414
1840.8906 | 122.8317 | -72.0245 | 50.6607 | 4.8834 | 4.6757 | 4.8459 | 5.1578 | 5.2094 | 4.9387 | 4.9092 | 50.6265 | 0.23032 | 50.5171 | -0.03768 | 0.020767 | 72.1323 | -0.001436 | 71.865 | 76.9079 | 76.7002 | 76.8704 | 77.1824 | 77.2339 | 76.9632 | 76.9337 | 122.6511 | 72.2549 | 122.5416 | 71.9869 | 72.0453 | 144.1569 | 72.0231 | 143.8895 | 50.6058 | 50.628 | 50.4963 | 50.5185
1841.8906 | 122.8043 | -72.0108 | 50.6836 | 6.1058 | 5.8982 | 6.0684 | 6.3849 | 6.4363 | 6.1611 | 6.1224 | 50.6357 | 0.2349 | 50.5217 | -0.033101 | 0.029923 | 72.1094 | -0.001436 | 71.8467 | 78.1166 | 77.909 | 78.0792 | 78.3957 | 78.4471 | 78.1719 | 78.1332 | 122.6465 | 72.2457 | 122.5325 | 71.9777 | 72.0407 | 144.1202 | 72.0094 | 143.8575 | 50.6058 | 50.6371 | 50.4918 | 50.5231
1842.8906 | 122.7905 | -72.0154 | 50.6653 | 7.5526 | 7.3543 | 7.5335 | 7.85 | 7.9241 | 7.6537 | 7.5783 | 50.6174 | 0.22574 | 50.4851 | -0.046838 | 0.029923 | 72.1094 | -0.001436 | 71.8284 | 79.568 | 79.3697 | 79.5489 | 79.8654 | 79.9395 | 79.669 | 79.5936 | 122.6328 | 72.2411 | 122.5004 | 71.9685 | 72.0453 | 144.1248 | 72.0139 | 143.8437 | 50.5875 | 50.6188 | 50.4551 | 50.4865
1843.8906 | 122.8271 | -72.0612 | 50.5692 | 7.1771 | 6.9788 | 7.1581 | 7.4746 | 7.5579 | 7.2828 | 7.2028 | 50.5624 | 0.23032 | 50.4393 | -0.046838 | 0.020767 | 72.1461 | 0.003143 | 71.8558 | 79.2383 | 79.04 | 79.2192 | 79.5357 | 79.619 | 79.344 | 79.264 | 122.6236 | 72.2915 | 122.5004 | 72.0143 | 72.0819 | 144.2072 | 72.0643 | 143.917 | 50.5417 | 50.5593 | 50.4185 | 50.4361
1844.8906 | 122.7173 | -72.0337 | 50.6058 | 7.049 | 6.8369 | 7.0299 | 7.3693 | 7.4297 | 7.1729 | 7.0609 | 50.567 | 0.2349 | 50.4301 | -0.042259 | 0.029923 | 72.1049 | 0.003143 | 71.8238 | 79.0826 | 78.8706 | 79.0636 | 79.4029 | 79.4634 | 79.2066 | 79.0946 | 122.6007 | 72.2686 | 122.4638 | 71.9914 | 72.0636 | 144.1386 | 72.0368 | 143.8575 | 50.5371 | 50.5639 | 50.4002 | 50.427
1845.8906 | 122.9462 | -71.965 | 50.647 | 8.0928 | 7.8579 | 8.0418 | 8.3857 | 8.4826 | 8.2397 | 8.0956 | 50.5899 | 0.23032 | 50.421 | -0.03768 | 0.025345 | 72.0728 | 0.007721 | 71.7643 | 80.0579 | 79.823 | 80.0068 | 80.3507 | 80.4476 | 80.2047 | 80.0606 | 122.5549 | 72.1953 | 122.386 | 71.9273 | 71.9904 | 144.0378 | 71.9727 | 143.7293 | 50.5646 | 50.5822 | 50.3956 | 50.4132
1846.8906 | 122.7905 | -71.6766 | 50.885 | 6.1653 | 5.9257 | 6.1279 | 6.481 | 6.5553 | 6.303 | 6.1453 | 50.7639 | 0.2349 | 50.6407 | -0.042259 | 0.029923 | 71.8989 | -0.001436 | 71.6086 | 77.842 | 77.6023 | 77.8045 | 78.1577 | 78.2319 | 77.9797 | 77.8219 | 122.4405 | 71.9115 | 122.3174 | 71.6344 | 71.7066 | 143.5755 | 71.6752 | 143.2853 | 50.734 | 50.7653 | 50.6108 | 50.6422
1847.8906 | 122.8409 | -71.7545 | 50.8209 | 4.2516 | 3.9934 | 4.2186 | 4.5672 | 4.6234 | 4.3389 | 4.1675 | 50.8234 | 0.22574 | 50.7048 | -0.042259 | 0.025345 | 71.8393 | -0.001436 | 71.5583 | 76.006 | 75.7479 | 75.9731 | 76.3217 | 76.3778 | 76.0934 | 75.922 | 122.5779 | 71.9802 | 122.4593 | 71.7122 | 71.7798 | 143.5938 | 71.753 | 143.3127 | 50.7981 | 50.8249 | 50.6795 | 50.7063
1848.8906 | 122.8226 | -71.7087 | 50.8072 | 6.0692 | 5.8066 | 6.0272 | 6.394 | 6.4683 | 6.1932 | 6.0034 | 50.8188 | 0.2349 | 50.6682 | -0.042259 | 0.029923 | 71.8165 | -0.006014 | 71.5262 | 77.7779 | 77.5153 | 77.7359 | 78.1027 | 78.177 | 77.9018 | 77.712 | 122.5275 | 71.9436 | 122.3769 | 71.6664 | 71.7386 | 143.5251 | 71.7027 | 143.2349 | 50.7889 | 50.8249 | 50.6383 | 50.6742
1849.8906 | 122.7722 | -71.8597 | 50.5646 | 12.8772 | 12.7206 | 12.8493 | 13.1702 | 13.2437 | 13.0928 | 13.0171 | 50.5808 | 0.23032 | 50.3614 | -0.046838 | 0.034501 | 71.9904 | -0.001436 | 71.6361 | 84.737 | 84.5804 | 84.709 | 85.0299 | 85.1034 | 84.9525 | 84.8769 | 122.4405 | 72.0901 | 122.2212 | 71.8129 | 71.8942 | 143.8502 | 71.8583 | 143.4958 | 50.5463 | 50.5822 | 50.3269 | 50.3629
1850.8906 | 122.6944 | -71.9604 | 50.4364 | 14.8047 | 14.6117 | 14.7448 | 15.0016 | 15.1252 | 14.9837 | 14.9537 | 50.4526 | 0.2349 | 50.2104 | -0.046838 | 0.029923 | 72.027 | 0.003143 | 71.6269 | 86.7652 | 86.5721 | 86.7053 | 86.9621 | 87.0857 | 86.9441 | 86.9141 | 122.413 | 72.1953 | 122.1708 | 71.9136 | 71.9904 | 143.9875 | 71.9636 | 143.5874 | 50.4226 | 50.4494 | 50.1804 | 50.2072
1851.8906 | 122.8043 | -72.1115 | 50.3677 | 18.4171 | 18.316 | 18.3528 | 18.614 | 18.7143 | 18.6693 | 18.7719 | 50.3839 | 0.2349 | 50.3065 | -0.042259 | 0.025345 | 72.2376 | -0.001436 | 72.0069 | 90.5286 | 90.4275 | 90.4643 | 90.7255 | 90.8258 | 90.7808 | 90.8834 | 122.4954 | 72.3464 | 122.418 | 72.0693 | 72.1369 | 144.3491 | 72.1101 | 144.1184 | 50.3585 | 50.3853 | 50.2812 | 50.3079
1852.8906 | 122.8638 | -72.2168 | 50.2716 | 19.5937 | 19.5065 | 19.6027 | 19.7999 | 19.8451 | 19.791 | 19.921 | 50.3518 | 0.22574 | 50.2653 | -0.042259 | 0.025345 | 72.3017 | -0.001436 | 72.0756 | 91.8105 | 91.7232 | 91.8195 | 92.0167 | 92.0619 | 92.0078 | 92.1378 | 122.5686 | 72.4425 | 122.4821 | 72.1745 | 72.2421 | 144.5185 | 72.2154 | 144.2924 | 50.3265 | 50.3533 | 50.24 | 50.2667
1853.8906 | 122.8317 | -72.258 | 50.2853 | 21.5441 | 21.4891 | 21.6173 | 21.7824 | 21.7541 | 21.6956 | 21.8347 | 50.3152 | 0.22574 | 50.2241 | -0.042259 | 0.025345 | 72.3567 | -0.001436 | 72.1259 | 93.8021 | 93.7471 | 93.8753 | 94.0404 | 94.0121 | 93.9536 | 94.0927 | 122.5732 | 72.4837 | 122.4821 | 72.2157 | 72.2833 | 144.6147 | 72.2566 | 144.3839 | 50.2899 | 50.3166 | 50.1988 | 50.2255
1854.8906 | 122.8226 | -72.2351 | 50.322 | 22.3682 | 22.3499 | 22.4552 | 22.6111 | 22.569 | 22.5517 | 22.6771 | 50.3335 | 0.23948 | 50.2516 | -0.042259 | 0.034501 | 72.3429 | 0.003143 | 72.1076 | 94.6033 | 94.585 | 94.6903 | 94.8462 | 94.8041 | 94.7868 | 94.9122 | 122.5686 | 72.4746 | 122.4867 | 72.1928 | 72.2696 | 144.578 | 72.2382 | 144.3427 | 50.299 | 50.3304 | 50.2171 | 50.2484
1855.8906 | 122.85 | -72.171 | 50.386 | 22.6887 | 22.6887 | 22.8306 | 22.9361 | 22.8665 | 22.8127 | 23.0021 | 50.4068 | 0.2349 | 50.3248 | -0.046838 | 0.029923 | 72.2834 | 0.007721 | 72.0527 | 94.8597 | 94.8597 | 95.0017 | 95.1072 | 95.0376 | 94.9837 | 95.1731 | 122.5778 | 72.4059 | 122.4958 | 72.1242 | 72.2009 | 144.4544 | 72.1787 | 144.2237 | 50.3769 | 50.3991 | 50.2949 | 50.3171
1856.8906 | 122.85 | -72.171 | 50.4044 | 22.9726 | 23.0092 | 23.1099 | 23.2292 | 23.1641 | 23.0966 | 23.2768 | 50.4205 | 0.23032 | 50.3294 | -0.042259 | 0.029923 | 72.2788 | -0.001436 | 72.0481 | 95.1436 | 95.1803 | 95.281 | 95.4002 | 95.3351 | 95.2676 | 95.4478 | 122.5915 | 72.4013 | 122.5004 | 72.1288 | 72.2009 | 144.4499 | 72.1696 | 144.2191 | 50.3906 | 50.4219 | 50.2995 | 50.3308
1857.8906 | 122.8592 | -72.1252 | 50.4639 | 23.229 | 23.2794 | 23.3663 | 23.4993 | 23.4342 | 23.3392 | 23.4966 | 50.448 | 0.22116 | 50.3523 | -0.03768 | 0.034501 | 72.2422 | 0.003143 | 72.0069 | 95.3542 | 95.4046 | 95.4916 | 95.6245 | 95.5595 | 95.4645 | 95.6218 | 122.5732 | 72.3464 | 122.4775 | 72.0876 | 72.1597 | 144.3675 | 72.1284 | 144.1322 | 50.4135 | 50.4448 | 50.3178 | 50.3491
1858.8906 | 122.8134 | -72.1527 | 50.4318 | 22.849 | 22.8948 | 23.0001 | 23.1193 | 23.0314 | 22.9409 | 23.1028 | 50.4526 | 0.2349 | 50.366 | -0.042259 | 0.029923 | 72.2376 | 0.003143 | 72.0115 | 95.0017 | 95.0475 | 95.1528 | 95.272 | 95.1841 | 95.0936 | 95.2555 | 122.6053 | 72.3876 | 122.5187 | 72.1105 | 72.1826 | 144.3903 | 72.1559 | 144.1642 | 50.4226 | 50.4494 | 50.3361 | 50.3629
1859.8906 | 122.8867 | -72.1756 | 50.4318 | 23.1054 | 23.1512 | 23.2565 | 23.3665 | 23.274 | 23.2064 | 23.3592 | 50.4251 | 0.23032 | 50.3569 | -0.046838 | 0.029923 | 72.2743 | 0.003143 | 72.0435 | 95.281 | 95.3268 | 95.4321 | 95.5421 | 95.4496 | 95.382 | 95.5348 | 122.6007 | 72.4059 | 122.5325 | 72.1288 | 72.2055 | 144.4499 | 72.1787 | 144.2191 | 50.3952 | 50.4219 | 50.3269 | 50.3537
1860.8906 | 122.8729 | -72.1481 | 50.4684 | 23.2381 | 23.3114 | 23.4076 | 23.4993 | 23.4022 | 23.3255 | 23.5057 | 50.4526 | 0.23032 | 50.3889 | -0.042259 | 0.025345 | 72.2514 | -0.001436 | 72.0206 | 95.3863 | 95.4596 | 95.5557 | 95.6474 | 95.5503 | 95.4736 | 95.6539 | 122.6007 | 72.3785 | 122.537 | 72.1059 | 72.1735 | 144.3995 | 72.1467 | 144.1688 | 50.4272 | 50.454 | 50.3636 | 50.3904
1861.8906 | 122.905 | -72.1344 | 50.4593 | 23.696 | 23.7968 | 23.8929 | 23.9892 | 23.8691 | 23.7742 | 23.959 | 50.448 | 0.2349 | 50.3569 | -0.03768 | 0.025345 | 72.2651 | -0.006014 | 72.039 | 95.8304 | 95.9312 | 96.0273 | 96.1236 | 96.0035 | 95.9086 | 96.0934 | 122.5824 | 72.3693 | 122.4913 | 72.0967 | 72.1597 | 144.3995 | 72.1284 | 144.1734 | 50.4226 | 50.454 | 50.3315 | 50.3629
1862.8906 | 122.9279 | -72.0932 | 50.4959 | 23.9981 | 24.0761 | 24.1905 | 24.2593 | 24.153 | 24.0718 | 24.252 | 50.4938 | 0.22574 | 50.4072 | -0.042259 | 0.034501 | 72.2102 | 0.007721 | 71.9886 | 96.0913 | 96.1693 | 96.2837 | 96.3525 | 96.2462 | 96.165 | 96.3452 | 122.587 | 72.3189 | 122.5004 | 72.0509 | 72.1277 | 144.3034 | 72.1009 | 144.0818 | 50.4593 | 50.486 | 50.3727 | 50.3995
1863.8906 | 122.9416 | -72.0474 | 50.5829 | 23.7097 | 23.7785 | 23.8975 | 23.9938 | 23.892 | 23.7879 | 23.9498 | 50.5487 | 0.23032 | 50.453 | -0.03768 | 0.029923 | 72.1735 | -0.001436 | 71.9474 | 95.7571 | 95.8259 | 95.9449 | 96.0412 | 95.9394 | 95.8353 | 95.9972 | 122.5961 | 72.2777 | 122.5004 | 72.0097 | 72.0773 | 144.221 | 72.046 | 143.9948 | 50.5188 | 50.5501 | 50.4231 | 50.4544
1864.8906 | 122.905 | -72.0291 | 50.5646 | 23.7005 | 23.7693 | 23.8975 | 24.0029 | 23.8829 | 23.7696 | 23.9223 | 50.567 | 0.2349 | 50.4759 | -0.042259 | 0.034501 | 72.1323 | 0.003143 | 71.9016 | 95.7297 | 95.7984 | 95.9266 | 96.032 | 95.912 | 95.7987 | 95.9514 | 122.5961 | 72.264 | 122.505 | 71.9869 | 72.0636 | 144.1615 | 72.0323 | 143.9307 | 50.5325 | 50.5639 | 50.4414 | 50.4728
1865.8906 | 122.9187 | -72.0154 | 50.5829 | 23.4808 | 23.5358 | 23.6548 | 23.774 | 23.6585 | 23.5636 | 23.7209 | 50.5762 | 0.23948 | 50.4988 | -0.051417 | 0.025345 | 72.1369 | 0.007721 | 71.9199 | 95.4962 | 95.5512 | 95.6702 | 95.7894 | 95.6739 | 95.5789 | 95.7363 | 122.5916 | 72.2549 | 122.5142 | 71.964 | 72.0407 | 144.1523 | 72.0231 | 143.9353 | 50.5508 | 50.5685 | 50.4734 | 50.4911
1866.8906 | 122.9416 | -72.0383 | 50.5692 | 23.2885 | 23.3618 | 23.4625 | 23.5725 | 23.4617 | 23.3758 | 23.5286 | 50.5624 | 0.2349 | 50.4805 | -0.042259 | 0.034501 | 72.1506 | 0.007721 | 71.9291 | 95.3268 | 95.4001 | 95.5008 | 95.6108 | 95.4999 | 95.4141 | 95.5669 | 122.6007 | 72.2732 | 122.5187 | 71.996 | 72.0728 | 144.1889 | 72.046 | 143.9674 | 50.5279 | 50.5547 | 50.446 | 50.4728
1867.8906 | 122.8958 | -72.0016 | 50.6195 | 23.4899 | 23.5587 | 23.6777 | 23.7557 | 23.6585 | 23.559 | 23.7209 | 50.6082 | 0.2349 | 50.5263 | -0.042259 | 0.029923 | 72.1186 | 0.003143 | 71.9016 | 95.4916 | 95.5604 | 95.6793 | 95.7573 | 95.6602 | 95.5606 | 95.7225 | 122.6099 | 72.2365 | 122.5279 | 71.9594 | 72.0316 | 144.1202 | 72.0048 | 143.9033 | 50.5783 | 50.6051 | 50.4963 | 50.5231
1868.8906 | 122.9004 | -71.9238 | 50.6927 | 23.4671 | 23.5358 | 23.6365 | 23.7374 | 23.6173 | 23.5452 | 23.6934 | 50.6906 | 0.2349 | 50.6224 | -0.046838 | 0.029923 | 72.0408 | 0.003143 | 71.8284 | 95.3909 | 95.4596 | 95.5603 | 95.6612 | 95.5412 | 95.4691 | 95.6173 | 122.6145 | 72.1587 | 122.5462 | 71.877 | 71.9538 | 143.9646 | 71.927 | 143.7522 | 50.6607 | 50.6875 | 50.5925 | 50.6193
1869.8906 | 122.8912 | -71.9193 | 50.7248 | 23.609 | 23.6869 | 23.8105 | 23.893 | 23.7638 | 23.6872 | 23.8399 | 50.7044 | 0.23032 | 50.6316 | -0.03768 | 0.034501 | 72.0316 | -0.001436 | 71.8009 | 95.5282 | 95.6062 | 95.7297 | 95.8123 | 95.6831 | 95.6064 | 95.7592 | 122.6236 | 72.1496 | 122.5508 | 71.8816 | 71.9538 | 143.9509 | 71.9178 | 143.7201 | 50.6699 | 50.7058 | 50.5971 | 50.633
1870.8906 | 122.8134 | -71.8964 | 50.8026 | 23.609 | 23.6823 | 23.7922 | 23.8976 | 23.773 | 23.6826 | 23.8353 | 50.741 | 0.2349 | 50.6682 | -0.03768 | 0.034501 | 71.9858 | 0.007721 | 71.7689 | 95.5053 | 95.5787 | 95.6885 | 95.794 | 95.6693 | 95.579 | 95.7317 | 122.6374 | 72.1313 | 122.5646 | 71.8587 | 71.9309 | 143.8822 | 71.9041 | 143.6652 | 50.7065 | 50.7333 | 50.6337 | 50.6605
1871.8906 | 122.818 | -71.8552 | 50.8575 | 23.7692 | 23.8472 | 23.957 | 24.0441 | 23.9241 | 23.8383 | 23.9956 | 50.7959 | 0.22574 | 50.7231 | -0.046838 | 0.029923 | 71.9309 | 0.003143 | 71.7093 | 95.6244 | 95.7023 | 95.8121 | 95.8993 | 95.7792 | 95.6934 | 95.8507 | 122.6511 | 72.0809 | 122.5783 | 71.8083 | 71.8851 | 143.7861 | 71.8583 | 143.5645 | 50.766 | 50.7928 | 50.6932 | 50.72
1872.8906 | 122.7997 | -71.8506 | 50.8621 | 23.6593 | 23.7464 | 23.8563 | 23.948 | 23.8188 | 23.7558 | 23.9086 | 50.7822 | 0.2349 | 50.7002 | -0.042259 | 0.034501 | 71.9446 | -0.001436 | 71.7185 | 95.5099 | 95.597 | 95.7068 | 95.7986 | 95.6693 | 95.6064 | 95.7592 | 122.6328 | 72.0855 | 122.5508 | 71.8083 | 71.8851 | 143.7952 | 71.8492 | 143.5691 | 50.7477 | 50.7837 | 50.6657 | 50.7017
1873.8906 | 122.8226 | -71.8094 | 50.885 | 23.5495 | 23.6274 | 23.7418 | 23.8152 | 23.6952 | 23.6322 | 23.7804 | 50.8372 | 0.22574 | 50.7369 | -0.03768 | 0.029923 | 71.908 | 0.003143 | 71.6727 | 95.3588 | 95.4368 | 95.5512 | 95.6246 | 95.5045 | 95.4416 | 95.5898 | 122.6465 | 72.0351 | 122.5463 | 71.7717 | 71.8393 | 143.7174 | 71.8125 | 143.4821 | 50.8072 | 50.834 | 50.7069 | 50.7337
1874.8906 | 122.8134 | -71.7911 | 50.9033 | 23.8242 | 23.9021 | 24.0119 | 24.0945 | 23.9744 | 23.9207 | 24.0597 | 50.8555 | 0.2349 | 50.7918 | -0.046838 | 0.034501 | 71.8668 | 0.003143 | 71.6407 | 95.6152 | 95.6932 | 95.803 | 95.8856 | 95.7655 | 95.7117 | 95.8508 | 122.6465 | 72.026 | 122.5829 | 71.7442 | 71.8256 | 143.6579 | 71.7942 | 143.4317 | 50.821 | 50.8523 | 50.7573 | 50.7887
1875.8906 | 122.7859 | -71.6995 | 50.9674 | 23.7692 | 23.8517 | 23.9478 | 24.0441 | 23.9103 | 23.8703 | 24.0047 | 50.9196 | 0.22574 | 50.8284 | -0.042259 | 0.034501 | 71.7981 | 0.007721 | 71.572 | 95.4687 | 95.5513 | 95.6474 | 95.7437 | 95.6098 | 95.5698 | 95.7043 | 122.6191 | 71.9253 | 122.528 | 71.6573 | 71.734 | 143.4977 | 71.7072 | 143.2715 | 50.8851 | 50.9118 | 50.7939 | 50.8207
1876.8906 | 122.8317 | -71.6217 | 51.0361 | 22.5056 | 22.3865 | 22.5422 | 22.6843 | 22.5736 | 22.4968 | 22.5489 | 50.9928 | 0.2349 | 50.9108 | -0.042259 | 0.029923 | 71.7386 | 0.003143 | 71.5033 | 94.1273 | 94.0082 | 94.1639 | 94.306 | 94.1953 | 94.1185 | 94.1706 | 122.6145 | 71.8566 | 122.5325 | 71.5794 | 71.6516 | 143.3603 | 71.6248 | 143.125 | 50.9629 | 50.9897 | 50.8809 | 50.9077
1877.8906 | 122.818 | -71.6263 | 50.9949 | 23.3251 | 23.1924 | 23.3572 | 23.4535 | 23.3472 | 23.2705 | 23.3409 | 50.9516 | 0.2349 | 50.8742 | -0.051417 | 0.025345 | 71.7524 | -0.001436 | 71.5262 | 94.9514 | 94.8187 | 94.9835 | 95.0798 | 94.9735 | 94.8968 | 94.9672 | 122.5779 | 71.8612 | 122.5005 | 71.5749 | 71.6516 | 143.3786 | 71.6248 | 143.1525 | 50.9263 | 50.9531 | 50.8489 | 50.8756
1878.8906 | 122.8363 | -71.6171 | 51.0361 | 23.5952 | 23.4854 | 23.6456 | 23.742 | 23.6082 | 23.5132 | 23.6202 | 50.9882 | 0.23032 | 50.8971 | -0.033101 | 0.029923 | 71.7203 | -0.001436 | 71.4804 | 95.2124 | 95.1026 | 95.2628 | 95.3591 | 95.2253 | 95.1303 | 95.2373 | 122.6054 | 71.8474 | 122.5142 | 71.584 | 71.647 | 143.3374 | 71.6157 | 143.0976 | 50.9583 | 50.9897 | 50.8672 | 50.8985
1879.8906 | 122.7859 | -71.5988 | 51.0452 | 23.9066 | 23.8105 | 23.9524 | 24.035 | 23.892 | 23.8154 | 23.9269 | 51.0111 | 0.23032 | 50.9108 | -0.03768 | 0.029923 | 71.6791 | 0.003143 | 71.4392 | 95.5054 | 95.4094 | 95.5512 | 95.6338 | 95.4908 | 95.4142 | 95.5257 | 122.61 | 71.8291 | 122.5097 | 71.5611 | 71.6287 | 143.2779 | 71.602 | 143.038 | 50.9812 | 51.008 | 50.8809 | 50.9077
1880.8906 | 122.8363 | -71.5622 | 51.0361 | 24.3415 | 24.2913 | 24.4332 | 24.5157 | 24.3864 | 24.3327 | 24.3802 | 50.9882 | 0.2349 | 50.8834 | -0.042259 | 0.034501 | 71.6837 | 0.007721 | 71.4346 | 95.9037 | 95.8535 | 95.9954 | 96.0779 | 95.9486 | 95.8949 | 95.9423 | 122.5504 | 71.7971 | 122.4456 | 71.5199 | 71.5967 | 143.2459 | 71.5699 | 142.9968 | 50.9537 | 50.9805 | 50.8489 | 50.8756
1881.8906 | 122.7814 | -71.5668 | 51.0361 | 24.6116 | 24.5386 | 24.6896 | 24.7446 | 24.6245 | 24.5525 | 24.6319 | 50.9745 | 0.2349 | 50.8559 | -0.042259 | 0.029923 | 71.6837 | 0.003143 | 71.4209 | 96.1784 | 96.1053 | 96.2563 | 96.3114 | 96.1913 | 96.1193 | 96.1987 | 122.5413 | 71.8017 | 122.4227 | 71.5245 | 71.5967 | 143.2505 | 71.5699 | 142.9877 | 50.9446 | 50.9714 | 50.826 | 50.8528
1882.8906 | 122.7493 | -71.5393 | 50.9995 | 24.5109 | 24.4562 | 24.6117 | 24.6805 | 24.5558 | 24.5159 | 24.5404 | 50.9791 | 0.23032 | 50.8467 | -0.03768 | 0.034501 | 71.6562 | 0.003143 | 71.3797 | 96.0502 | 95.9955 | 96.151 | 96.2198 | 96.0951 | 96.0552 | 96.0797 | 122.5184 | 71.7696 | 122.386 | 71.5016 | 71.5738 | 143.1955 | 71.5424 | 142.919 | 50.9446 | 50.9759 | 50.8122 | 50.8436
1883.8906 | 122.7631 | -71.4935 | 51.0406 | 24.1721 | 24.1036 | 24.2592 | 24.3463 | 24.2216 | 24.2 | 24.2016 | 50.9928 | 0.23032 | 50.8651 | -0.042259 | 0.034501 | 71.6287 | 0.003143 | 71.3614 | 95.6657 | 95.5971 | 95.7527 | 95.8398 | 95.7152 | 95.6935 | 95.6951 | 122.4864 | 71.7238 | 122.3586 | 71.4513 | 71.528 | 143.1223 | 71.4967 | 142.8549 | 50.9583 | 50.9897 | 50.8306 | 50.8619
1884.8906 | 122.6486 | -71.4203 | 51.123 | 23.5769 | 23.49 | 23.6273 | 23.7465 | 23.6768 | 23.6093 | 23.6019 | 51.0936 | 0.2349 | 50.9475 | -0.03768 | 0.025345 | 71.5051 | -0.006014 | 71.2149 | 94.9972 | 94.9103 | 95.0476 | 95.1668 | 95.0971 | 95.0296 | 95.0221 | 122.5138 | 71.6552 | 122.3678 | 71.3826 | 71.4456 | 142.9254 | 71.4143 | 142.6352 | 51.0682 | 51.0996 | 50.9221 | 50.9535
1885.8906 | 122.7036 | -71.4523 | 51.1414 | 23.7646 | 23.6686 | 23.8059 | 23.9068 | 23.86 | 23.7971 | 23.785 | 51.1164 | 0.23032 | 51.0345 | -0.042259 | 0.029923 | 71.5143 | 0.007721 | 71.2973 | 95.217 | 95.1209 | 95.2582 | 95.3591 | 95.3123 | 95.2494 | 95.2373 | 122.5688 | 71.6826 | 122.4868 | 71.4101 | 71.4823 | 142.9666 | 71.4601 | 142.7496 | 51.0865 | 51.1087 | 51.0045 | 51.0267
1886.8906 | 122.7493 | -71.3837 | 51.178 | 23.8837 | 23.7968 | 23.9249 | 24.035 | 23.9881 | 23.9252 | 23.904 | 51.1439 | 0.2349 | 51.0436 | -0.046838 | 0.029923 | 71.4868 | -0.001436 | 71.2424 | 95.2674 | 95.1805 | 95.3086 | 95.4186 | 95.3718 | 95.3089 | 95.2877 | 122.5276 | 71.6186 | 122.4273 | 71.3368 | 71.4136 | 142.8705 | 71.3822 | 142.626 | 51.114 | 51.1454 | 51.0137 | 51.045
1887.8906 | 122.7127 | -71.3608 | 51.2146 | 24.0485 | 23.98 | 24.1127 | 24.2135 | 24.153 | 24.1175 | 24.0871 | 51.1668 | 0.23948 | 51.0802 | -0.042259 | 0.029923 | 71.4502 | 0.003143 | 71.2149 | 95.4093 | 95.3407 | 95.4734 | 95.5743 | 95.5137 | 95.4783 | 95.4479 | 122.5276 | 71.6003 | 122.441 | 71.3185 | 71.3907 | 142.811 | 71.3639 | 142.5757 | 51.1369 | 51.1637 | 51.0503 | 51.0771
1888.8906 | 122.7036 | -71.2875 | 51.2421 | 23.9295 | 23.8472 | 23.989 | 24.0853 | 24.0431 | 23.9619 | 23.9635 | 51.2218 | 0.2349 | 51.0802 | -0.042259 | 0.029923 | 71.3724 | 0.003143 | 71.0821 | 95.217 | 95.1347 | 95.2766 | 95.3729 | 95.3306 | 95.2494 | 95.2511 | 122.5093 | 71.5224 | 122.3678 | 71.2453 | 71.3175 | 142.6599 | 71.2907 | 142.3697 | 51.1918 | 51.2186 | 51.0503 | 51.0771
1889.8906 | 122.5983 | -71.228 | 51.3016 | 24.3186 | 24.2272 | 24.3736 | 24.4745 | 24.4322 | 24.3739 | 24.3389 | 51.2721 | 0.23032 | 51.1123 | -0.046838 | 0.025345 | 71.2991 | -0.001436 | 71.0043 | 95.5467 | 95.4552 | 95.6017 | 95.7025 | 95.6602 | 95.602 | 95.567 | 122.5001 | 71.4583 | 122.3403 | 71.1812 | 71.2534 | 142.5272 | 71.2266 | 142.2323 | 51.2468 | 51.2736 | 51.0869 | 51.1137
1890.8906 | 122.7081 | -71.2967 | 51.2329 | 25.1153 | 25.0331 | 25.2253 | 25.3078 | 25.2562 | 25.1797 | 25.1264 | 51.2446 | 0.2349 | 51.1398 | -0.042259 | 0.029923 | 71.3449 | 0.003143 | 71.0913 | 96.412 | 96.3298 | 96.5219 | 96.6045 | 96.5529 | 96.4764 | 96.4231 | 122.5413 | 71.5316 | 122.4364 | 71.2544 | 71.3266 | 142.6416 | 71.2998 | 142.388 | 51.2147 | 51.2415 | 51.1098 | 51.1366
1891.8906 | 122.6944 | -71.3242 | 51.1917 | 25.1015 | 25.0422 | 25.2436 | 25.2941 | 25.2517 | 25.1614 | 25.1264 | 51.2172 | 0.23032 | 51.1169 | -0.046838 | 0.034501 | 71.3815 | -0.001436 | 71.1416 | 96.4257 | 96.3664 | 96.5677 | 96.6182 | 96.5758 | 96.4856 | 96.4505 | 122.5413 | 71.5545 | 122.441 | 71.2773 | 71.3587 | 142.7057 | 71.3227 | 142.4658 | 51.1827 | 51.2186 | 51.0824 | 51.1183
1892.8906 | 122.731 | -71.2601 | 51.2466 | 25.1153 | 25.0468 | 25.2344 | 25.3261 | 25.2608 | 25.2072 | 25.1447 | 51.2538 | 0.23948 | 51.1581 | -0.03768 | 0.025345 | 71.3449 | -0.006014 | 71.1142 | 96.3753 | 96.3069 | 96.4945 | 96.5862 | 96.5209 | 96.4673 | 96.4048 | 122.5139 | 71.4995 | 122.4181 | 71.2224 | 71.2854 | 142.605 | 71.2541 | 142.3742 | 51.2285 | 51.2598 | 51.1327 | 51.1641
1893.8906 | 122.7264 | -71.2463 | 51.3016 | 24.9596 | 24.914 | 25.1016 | 25.1842 | 25.1097 | 25.0286 | 24.989 | 51.263 | 0.23948 | 51.1581 | -0.046838 | 0.025345 | 71.3358 | 0.003143 | 71.1096 | 96.2059 | 96.1604 | 96.348 | 96.4305 | 96.3561 | 96.275 | 96.2354 | 122.5093 | 71.4858 | 122.4044 | 71.1995 | 71.2717 | 142.5821 | 71.2495 | 142.3559 | 51.2376 | 51.2598 | 51.1327 | 51.1549
1894.8906 | 122.7036 | -71.1823 | 51.3336 | 25.0054 | 24.9552 | 25.1612 | 25.2391 | 25.1784 | 25.1065 | 25.0257 | 51.3316 | 0.23032 | 51.2359 | -0.042259 | 0.029923 | 71.2808 | 0.003143 | 71.0409 | 96.1876 | 96.1375 | 96.3434 | 96.4214 | 96.3607 | 96.2887 | 96.2079 | 122.5139 | 71.4126 | 122.4181 | 71.14 | 71.2122 | 142.4631 | 71.1854 | 142.2232 | 51.3017 | 51.3285 | 51.206 | 51.2328
1895.8906 | 122.8134 | -71.0815 | 51.4069 | 24.8589 | 24.8362 | 25.033 | 25.0835 | 24.9953 | 24.9417 | 24.8883 | 51.4095 | 0.2349 | 51.3091 | -0.046838 | 0.025345 | 71.1938 | -0.006014 | 70.9631 | 95.9404 | 95.9177 | 96.1145 | 96.165 | 96.0768 | 96.0232 | 95.9699 | 122.491 | 71.3164 | 122.3907 | 71.0347 | 71.1069 | 142.2754 | 71.0755 | 142.0446 | 51.3841 | 51.4155 | 51.2838 | 51.3152
1896.8906 | 122.7676 | -71.0678 | 51.4206 | 24.9001 | 24.8591 | 25.0787 | 25.1338 | 25.0502 | 24.9874 | 24.9341 | 51.4324 | 0.2349 | 51.3412 | -0.042259 | 0.029923 | 71.1755 | -0.001436 | 70.931 | 95.9679 | 95.9269 | 96.1466 | 96.2016 | 96.118 | 96.0552 | 96.0019 | 122.5002 | 71.3027 | 122.409 | 71.0256 | 71.0977 | 142.2433 | 71.0664 | 141.9989 | 51.4024 | 51.4338 | 51.3113 | 51.3426
1897.8906 | 122.7539 | -71.0495 | 51.416 | 24.7765 | 24.7446 | 24.9368 | 25.0056 | 24.9266 | 24.8547 | 24.8242 | 51.4232 | 0.2349 | 51.3549 | -0.046838 | 0.034501 | 71.1938 | 0.003143 | 70.9722 | 95.826 | 95.7941 | 95.9863 | 96.0551 | 95.9761 | 95.9042 | 95.8737 | 122.4727 | 71.2844 | 122.4044 | 71.0027 | 71.084 | 142.2433 | 71.0526 | 142.0217 | 51.3887 | 51.4201 | 51.3204 | 51.3518
1898.8906 | 122.7173 | -70.99 | 51.4526 | 24.8223 | 24.7721 | 24.9734 | 24.9873 | 24.8992 | 24.7906 | 24.8517 | 51.4919 | 0.23032 | 51.4099 | -0.046838 | 0.029923 | 71.116 | 0.007721 | 70.8853 | 95.8122 | 95.7621 | 95.9634 | 95.9773 | 95.8891 | 95.7806 | 95.8417 | 122.4819 | 71.2203 | 122.3999 | 70.9432 | 71.0199 | 142.106 | 70.9977 | 141.8753 | 51.462 | 51.4842 | 51.3799 | 51.4022
1899.8906 | 122.7951 | -70.9122 | 51.5579 | 24.8268 | 24.7721 | 24.9368 | 24.9781 | 24.8625 | 24.7906 | 24.8563 | 51.5651 | 0.2349 | 51.4831 | -0.042259 | 0.029923 | 71.0428 | 0.007721 | 70.812 | 95.739 | 95.6843 | 95.849 | 95.8903 | 95.7747 | 95.7027 | 95.7685 | 122.4773 | 71.1471 | 122.3953 | 70.8699 | 70.9421 | 141.9549 | 70.9199 | 141.7242 | 51.5352 | 51.5574 | 51.4532 | 51.4754
1900.8906 | 122.8821 | -70.8755 | 51.6083 | 23.8699 | 23.8426 | 24.0211 | 24.0808 | 23.9561 | 23.8383 | 23.9086 | 51.6247 | 0.23948 | 51.5426 | -0.046838 | 0.025345 | 70.997 | -0.001436 | 70.7708 | 94.7455 | 94.7181 | 94.8966 | 94.9563 | 94.8316 | 94.7138 | 94.7841 | 122.5002 | 71.115 | 122.4182 | 70.8287 | 70.9009 | 141.8725 | 70.8741 | 141.6464 | 51.5993 | 51.6261 | 51.5173 | 51.5441
1901.8906 | 122.7585 | -70.8206 | 51.6678 | 24.749 | 24.6759 | 24.8727 | 24.9049 | 24.8122 | 24.7082 | 24.7647 | 51.6796 | 0.2349 | 51.5472 | -0.042259 | 0.029923 | 70.9237 | 0.003143 | 70.6609 | 95.5696 | 95.4966 | 95.6933 | 95.7255 | 95.6328 | 95.5288 | 95.5853 | 122.5002 | 71.0555 | 122.3678 | 70.7784 | 70.8505 | 141.7443 | 70.8238 | 141.4815 | 51.6497 | 51.6765 | 51.5173 | 51.5441
1902.8906 | 122.7814 | -70.8984 | 51.6495 | 25.1611 | 25.1063 | 25.2894 | 25.3124 | 25.215 | 25.1294 | 25.1813 | 51.6338 | 0.23032 | 51.5472 | -0.046838 | 0.029923 | 70.9787 | 0.003143 | 70.7617 | 96.0595 | 96.0048 | 96.1878 | 96.2108 | 96.1135 | 96.0278 | 96.0798 | 122.5323 | 71.1288 | 122.4457 | 70.8516 | 70.9284 | 141.8771 | 70.9016 | 141.6601 | 51.6039 | 51.6307 | 51.5173 | 51.5441
1903.8906 | 122.7814 | -70.8389 | 51.6769 | 24.8818 | 24.8408 | 25.0192 | 25.0468 | 24.9358 | 24.8409 | 24.9112 | 51.675 | 0.2349 | 51.593 | -0.042259 | 0.029923 | 70.9512 | -0.001436 | 70.7113 | 95.7207 | 95.6797 | 95.8581 | 95.8858 | 95.7747 | 95.6799 | 95.7501 | 122.5139 | 71.0738 | 122.4319 | 70.7967 | 70.8689 | 141.7901 | 70.8375 | 141.5502 | 51.6451 | 51.6765 | 51.5631 | 51.5944
1904.8906 | 122.7539 | -70.8527 | 51.6815 | 25.0695 | 24.9965 | 25.1886 | 25.2208 | 25.1464 | 25.0378 | 25.1035 | 51.6888 | 0.2349 | 51.6113 | -0.042259 | 0.029923 | 70.9466 | 0.003143 | 70.7159 | 95.9221 | 95.8491 | 96.0413 | 96.0735 | 95.999 | 95.8905 | 95.9562 | 122.5414 | 71.0876 | 122.464 | 70.8104 | 70.8826 | 141.7993 | 70.8558 | 141.5685 | 51.6588 | 51.6856 | 51.5814 | 51.6082
1905.8906 | 122.8043 | -70.7199 | 51.8051 | 24.2637 | 24.186 | 24.3507 | 24.4013 | 24.3178 | 24.2274 | 24.2977 | 51.7757 | 0.2349 | 51.7029 | -0.03768 | 0.029923 | 70.8459 | -0.006014 | 70.6426 | 94.9836 | 94.9059 | 95.0707 | 95.1212 | 95.0377 | 94.9473 | 95.0177 | 122.4957 | 70.9548 | 122.4228 | 70.6822 | 70.7498 | 141.5658 | 70.7139 | 141.3625 | 51.7458 | 51.7818 | 51.673 | 51.7089
1906.8906 | 122.8088 | -70.7199 | 51.8326 | 24.2957 | 24.1997 | 24.3736 | 24.4104 | 24.3406 | 24.2549 | 24.3161 | 51.8078 | 0.2349 | 51.7304 | -0.03768 | 0.025345 | 70.823 | 0.003143 | 70.6014 | 95.0156 | 94.9196 | 95.0935 | 95.1303 | 95.0606 | 94.9748 | 95.036 | 122.5277 | 70.9548 | 122.4503 | 70.6822 | 70.7453 | 141.5429 | 70.7231 | 141.3213 | 51.7825 | 51.8047 | 51.705 | 51.7272
1907.8906 | 122.6624 | -70.6696 | 51.8692 | 24.3003 | 24.2043 | 24.3645 | 24.4241 | 24.3635 | 24.2686 | 24.3344 | 51.8765 | 0.2349 | 51.799 | -0.046838 | 0.029923 | 70.7498 | 0.003143 | 70.5373 | 94.9699 | 94.8739 | 95.034 | 95.0937 | 95.0331 | 94.9382 | 95.0039 | 122.546 | 70.9045 | 122.4686 | 70.6227 | 70.6995 | 141.4193 | 70.6727 | 141.2069 | 51.8466 | 51.8733 | 51.7691 | 51.7959
1908.8906 | 122.8821 | -70.6741 | 51.86 | 24.3095 | 24.2181 | 24.4011 | 24.4562 | 24.3727 | 24.2824 | 24.3573 | 51.8765 | 0.23948 | 51.8036 | -0.042259 | 0.020767 | 70.7543 | -0.001436 | 70.5419 | 94.9836 | 94.8922 | 95.0752 | 95.1303 | 95.0468 | 94.9565 | 95.0314 | 122.5506 | 70.9136 | 122.4777 | 70.6319 | 70.6949 | 141.4285 | 70.6727 | 141.216 | 51.8557 | 51.8779 | 51.7828 | 51.805
1909.8906 | 122.7859 | -70.6055 | 51.9104 | 24.7124 | 24.5981 | 24.7537 | 24.8179 | 24.771 | 24.6761 | 24.7464 | 51.9131 | 0.23948 | 51.8494 | -0.046838 | 0.034501 | 70.7223 | -0.001436 | 70.5099 | 95.3178 | 95.2036 | 95.3591 | 95.4234 | 95.3764 | 95.2816 | 95.3519 | 122.5186 | 70.8449 | 122.4549 | 70.5586 | 70.64 | 141.3278 | 70.604 | 141.1153 | 51.8786 | 51.9145 | 51.8149 | 51.8508
1910.8906 | 122.8729 | -70.5597 | 51.9379 | 24.6574 | 24.5431 | 24.7216 | 24.7767 | 24.7023 | 24.6212 | 24.696 | 51.9497 | 0.2349 | 51.854 | -0.03768 | 0.029923 | 70.6857 | 0.003143 | 70.4503 | 95.2171 | 95.1028 | 95.2813 | 95.3364 | 95.262 | 95.1809 | 95.2557 | 122.5094 | 70.7946 | 122.4137 | 70.522 | 70.5896 | 141.2454 | 70.5628 | 141.01 | 51.9198 | 51.9466 | 51.824 | 51.8508
1911.8906 | 122.7905 | -70.5414 | 51.9974 | 24.8451 | 24.7309 | 24.9002 | 24.9553 | 24.8854 | 24.8043 | 24.8746 | 51.9589 | 0.2349 | 51.8769 | -0.046838 | 0.029923 | 70.6536 | 0.007721 | 70.4366 | 95.3865 | 95.2723 | 95.4416 | 95.4966 | 95.4268 | 95.3457 | 95.416 | 122.5003 | 70.7763 | 122.4182 | 70.4945 | 70.5713 | 141.195 | 70.5491 | 140.978 | 51.929 | 51.9512 | 51.8469 | 51.8691
1912.8906 | 122.7585 | -70.5002 | 52.034 | 24.5155 | 24.392 | 24.5568 | 24.6073 | 24.5283 | 24.4838 | 24.545 | 52.023 | 0.2349 | 51.941 | -0.042259 | 0.039079 | 70.6078 | 0.003143 | 70.3908 | 95.0157 | 94.8922 | 95.057 | 95.1075 | 95.0285 | 94.984 | 95.0451 | 122.5232 | 70.7351 | 122.4411 | 70.4579 | 70.5393 | 141.108 | 70.5033 | 140.891 | 51.9839 | 52.0198 | 51.9019 | 51.9378
1913.8906 | 122.8043 | -70.4773 | 52.0889 | 24.8864 | 24.7675 | 24.9231 | 24.9553 | 24.8717 | 24.8455 | 24.9112 | 52.0505 | 0.23948 | 51.9547 | -0.042259 | 0.025345 | 70.5758 | -0.001436 | 70.3542 | 95.3636 | 95.2448 | 95.4004 | 95.4325 | 95.349 | 95.3228 | 95.3885 | 122.5278 | 70.7168 | 122.432 | 70.435 | 70.5026 | 141.0531 | 70.4759 | 140.8315 | 52.0251 | 52.0519 | 51.9293 | 51.9561
1914.8906 | 122.7585 | -70.3308 | 52.1805 | 23.2473 | 23.0871 | 23.3022 | 23.3207 | 23.2099 | 23.1698 | 23.2402 | 52.1649 | 0.23032 | 52.06 | -0.046838 | 0.034501 | 70.4476 | 0.003143 | 70.2031 | 93.5781 | 93.4179 | 93.6331 | 93.6515 | 93.5407 | 93.5006 | 93.571 | 122.4957 | 70.5611 | 122.3908 | 70.284 | 70.3653 | 140.7784 | 70.334 | 140.5339 | 52.1304 | 52.1618 | 52.0255 | 52.0568
1915.8906 | 122.6578 | -70.3171 | 52.2125 | 24.0897 | 23.98 | 24.1035 | 24.1357 | 24.0797 | 24.0534 | 24.1284 | 52.1741 | 0.2349 | 52.06 | -0.042259 | 0.025345 | 70.411 | -0.001436 | 70.139 | 94.4068 | 94.297 | 94.4206 | 94.4528 | 94.3968 | 94.3705 | 94.4454 | 122.4912 | 70.552 | 122.3771 | 70.2748 | 70.3424 | 140.7281 | 70.3156 | 140.4561 | 52.1487 | 52.1755 | 52.0346 | 52.0614
1916.8906 | 122.5891 | -70.2347 | 52.2858 | 23.2336 | 23.0917 | 23.261 | 23.2841 | 23.2419 | 23.1881 | 23.2493 | 52.2199 | 0.23032 | 52.0737 | -0.046838 | 0.039079 | 70.324 | 0.007721 | 70.0383 | 93.4682 | 93.3263 | 93.4957 | 93.5188 | 93.4766 | 93.4228 | 93.484 | 122.4545 | 70.465 | 122.3084 | 70.1878 | 70.2738 | 140.5587 | 70.2424 | 140.273 | 52.1808 | 52.2121 | 52.0346 | 52.066
1917.8906 | 122.6212 | -70.1889 | 52.3178 | 23.7784 | 23.6457 | 23.8013 | 23.8473 | 23.7776 | 23.733 | 23.7987 | 52.2382 | 0.22574 | 52.0966 | -0.042259 | 0.020767 | 70.3057 | -0.001436 | 70.02 | 93.9673 | 93.8346 | 93.9902 | 94.0362 | 93.9665 | 93.9219 | 93.9876 | 122.4271 | 70.4146 | 122.2855 | 70.1466 | 70.2097 | 140.4946 | 70.1875 | 140.2089 | 52.2174 | 52.2396 | 52.0758 | 52.098
1918.8906 | 122.5662 | -70.2393 | 52.2812 | 24.1355 | 24.0257 | 24.1493 | 24.1815 | 24.1392 | 24.1038 | 24.1741 | 52.229 | 0.2349 | 52.1149 | -0.046838 | 0.029923 | 70.3057 | -0.001436 | 70.0658 | 94.3748 | 94.265 | 94.3885 | 94.4207 | 94.3785 | 94.3431 | 94.4134 | 122.4683 | 70.4742 | 122.3542 | 70.1924 | 70.2692 | 140.5449 | 70.2378 | 140.305 | 52.1991 | 52.2305 | 52.085 | 52.1164
1919.8906 | 122.7081 | -70.1294 | 52.2858 | 23.6777 | 23.545 | 23.696 | 23.742 | 23.686 | 23.6277 | 23.6934 | 52.2565 | 0.23948 | 52.1103 | -0.042259 | 0.029923 | 70.2416 | -0.001436 | 69.9696 | 93.8071 | 93.6744 | 93.8254 | 93.8713 | 93.8154 | 93.757 | 93.8228 | 122.3859 | 70.3689 | 122.2397 | 70.0871 | 70.1593 | 140.371 | 70.128 | 140.099 | 52.2266 | 52.2579 | 52.0804 | 52.1118
1920.8906 | 122.6395 | -70.1248 | 52.3041 | 23.2702 | 23.1512 | 23.2519 | 23.2978 | 23.274 | 23.2248 | 23.2997 | 52.2656 | 0.2349 | 52.1241 | -0.046838 | 0.029923 | 70.2141 | -0.001436 | 69.9513 | 93.395 | 93.276 | 93.3767 | 93.4227 | 93.3988 | 93.3496 | 93.4245 | 122.3905 | 70.3597 | 122.2489 | 70.078 | 70.1547 | 140.3389 | 70.1234 | 140.0761 | 52.2357 | 52.2671 | 52.0942 | 52.1255
1921.8906 | 122.6852 | -70.1111 | 52.3499 | 23.0275 | 22.8994 | 22.9863 | 23.0598 | 23.0268 | 22.9867 | 23.0479 | 52.3297 | 0.23032 | 52.2202 | -0.042259 | 0.034501 | 70.1729 | 0.003143 | 69.933 | 93.1386 | 93.0104 | 93.0974 | 93.1708 | 93.1379 | 93.0978 | 93.159 | 122.4408 | 70.3414 | 122.3313 | 70.0688 | 70.1456 | 140.284 | 70.1142 | 140.0441 | 52.2952 | 52.3266 | 52.1857 | 52.2171
1922.8906 | 122.6761 | -70.0058 | 52.4002 | 23.1237 | 22.9909 | 23.0871 | 23.1422 | 23.1138 | 23.0782 | 23.1395 | 52.3343 | 0.22574 | 52.1928 | -0.046838 | 0.029923 | 70.1271 | 0.003143 | 69.8506 | 93.1295 | 92.9967 | 93.0928 | 93.148 | 93.1196 | 93.084 | 93.1453 | 122.3401 | 70.2315 | 122.1986 | 69.959 | 70.0357 | 140.1329 | 70.0089 | 139.8564 | 52.3044 | 52.3312 | 52.1628 | 52.1896
1923.8906 | 122.5845 | -69.96 | 52.478 | 23.3801 | 23.2657 | 23.3297 | 23.3848 | 23.3793 | 23.3438 | 23.4142 | 52.4305 | 0.2349 | 52.3347 | -0.03768 | 0.029923 | 70.0814 | 0.003143 | 69.8369 | 93.3401 | 93.2257 | 93.2897 | 93.3449 | 93.3393 | 93.3038 | 93.3742 | 122.3905 | 70.1949 | 122.2947 | 69.9223 | 69.9899 | 140.0414 | 69.9632 | 139.7969 | 52.4006 | 52.4273 | 52.3048 | 52.3315
1924.8906 | 122.6669 | -69.9371 | 52.4414 | 23.3389 | 23.2153 | 23.2702 | 23.339 | 23.3381 | 23.298 | 23.3638 | 52.4442 | 0.2349 | 52.3393 | -0.03768 | 0.029923 | 70.0447 | 0.007721 | 69.8002 | 93.276 | 93.1524 | 93.2073 | 93.2762 | 93.2752 | 93.2351 | 93.3009 | 122.3813 | 70.172 | 122.2764 | 69.8995 | 69.9671 | 139.9819 | 69.9449 | 139.7374 | 52.4143 | 52.4365 | 52.3093 | 52.3315
1925.8906 | 122.5845 | -69.8318 | 52.5879 | 22.8581 | 22.7391 | 22.8123 | 22.8675 | 22.862 | 22.8219 | 22.8922 | 52.5816 | 0.2349 | 52.4583 | -0.03768 | 0.025345 | 69.912 | -0.006014 | 69.6537 | 92.69 | 92.5709 | 92.6442 | 92.6993 | 92.6938 | 92.6537 | 92.7241 | 122.4134 | 70.0667 | 122.2901 | 69.7942 | 69.8572 | 139.7438 | 69.8258 | 139.4856 | 52.5562 | 52.5876 | 52.433 | 52.4643
1926.8906 | 122.5067 | -69.7403 | 52.6566 | 22.0294 | 21.8188 | 21.9882 | 22.0616 | 22.1295 | 21.9611 | 21.9858 | 52.6548 | 0.2349 | 52.4766 | -0.03768 | 0.025345 | 69.7517 | -0.001436 | 69.4157 | 91.7697 | 91.559 | 91.7285 | 91.8019 | 91.8698 | 91.7014 | 91.7261 | 122.3951 | 69.9752 | 122.2169 | 69.7026 | 69.7656 | 139.492 | 69.7389 | 139.156 | 52.6295 | 52.6563 | 52.4513 | 52.478
1927.8906 | 122.5433 | -69.7449 | 52.6611 | 22.2629 | 22.1438 | 22.2354 | 22.3501 | 22.3767 | 22.2267 | 22.2879 | 52.6411 | 0.2349 | 52.5407 | -0.042259 | 0.025345 | 69.8158 | -0.006014 | 69.553 | 92.0078 | 91.8887 | 91.9803 | 92.095 | 92.1216 | 91.9715 | 92.0328 | 122.386 | 69.9798 | 122.2856 | 69.7026 | 69.7702 | 139.5607 | 69.7389 | 139.2979 | 52.6157 | 52.6471 | 52.5154 | 52.5467
1928.8906 | 122.7173 | -69.6487 | 52.7893 | 22.1073 | 21.9927 | 22.1027 | 22.199 | 22.2165 | 22.0664 | 22.1414 | 52.7327 | 0.23948 | 52.6323 | -0.042259 | 0.025345 | 69.7563 | -0.001436 | 69.521 | 91.756 | 91.6415 | 91.7514 | 91.8477 | 91.8652 | 91.7152 | 91.7902 | 122.3814 | 69.8882 | 122.281 | 69.6065 | 69.6741 | 139.4051 | 69.6473 | 139.1697 | 52.7073 | 52.7341 | 52.6069 | 52.6337
1929.8906 | 122.6761 | -69.5984 | 52.7847 | 21.8784 | 21.7546 | 21.86 | 22.0204 | 21.9738 | 21.8375 | 21.9171 | 52.7968 | 0.23948 | 52.7147 | -0.051417 | 0.029923 | 69.6831 | 0.003143 | 69.4569 | 91.4767 | 91.353 | 91.4584 | 91.6188 | 91.5722 | 91.4359 | 91.5155 | 122.3951 | 69.8379 | 122.3131 | 69.547 | 69.6283 | 139.2815 | 69.6015 | 139.0553 | 52.7668 | 52.7936 | 52.6848 | 52.7115
1930.8906 | 122.4884 | -69.5755 | 52.7618 | 22.0294 | 21.9103 | 22.0294 | 22.1898 | 22.1432 | 21.9886 | 22.0682 | 52.7647 | 0.2349 | 52.5773 | -0.042259 | 0.034501 | 69.6098 | -0.006014 | 69.3562 | 91.6049 | 91.4858 | 91.6049 | 91.7653 | 91.7187 | 91.5641 | 91.6437 | 122.3402 | 69.8104 | 122.1528 | 69.5332 | 69.61 | 139.1853 | 69.5695 | 138.9317 | 52.7302 | 52.7707 | 52.5428 | 52.5833
1931.8906 | 122.5021 | -69.4977 | 52.858 | 21.567 | 21.457 | 21.567 | 21.6954 | 21.6625 | 21.5308 | 21.5966 | 52.8425 | 0.2349 | 52.7193 | -0.046838 | 0.034501 | 69.5961 | -0.001436 | 69.3195 | 91.0647 | 90.9547 | 91.0646 | 91.193 | 91.1602 | 91.0284 | 91.0943 | 122.3402 | 69.7326 | 122.2169 | 69.4508 | 69.5322 | 139.0938 | 69.4962 | 138.8172 | 52.808 | 52.844 | 52.6848 | 52.7207
1932.8906 | 122.612 | -69.3649 | 52.9541 | 21.0451 | 20.9305 | 21.0358 | 21.1322 | 21.1132 | 21.0042 | 21.0747 | 52.9616 | 0.22574 | 52.8246 | -0.03768 | 0.029923 | 69.4771 | 0.003143 | 69.2097 | 90.41 | 90.2954 | 90.4008 | 90.4971 | 90.4781 | 90.3692 | 90.4396 | 122.3265 | 69.5907 | 122.1895 | 69.3272 | 69.3949 | 138.842 | 69.3681 | 138.5746 | 52.9317 | 52.9584 | 52.7946 | 52.8214
1933.8906 | 122.644 | -69.3054 | 52.9816 | 21.2969 | 21.1777 | 21.2968 | 21.3932 | 21.3833 | 21.2652 | 21.3265 | 52.9936 | 0.2349 | 52.8291 | -0.042259 | 0.029923 | 69.413 | 0.003143 | 69.1135 | 90.6023 | 90.4831 | 90.6022 | 90.6986 | 90.6887 | 90.5706 | 90.6319 | 122.299 | 69.5403 | 122.1346 | 69.2632 | 69.3353 | 138.7184 | 69.3086 | 138.4189 | 52.9637 | 52.9905 | 52.7992 | 52.826
1934.8906 | 122.5891 | -69.3604 | 53.0411 | 21.8005 | 21.6768 | 21.7959 | 21.9151 | 21.8823 | 21.7551 | 21.821 | 52.9982 | 0.2349 | 52.8887 | -0.03768 | 0.034501 | 69.4267 | 0.003143 | 69.1684 | 91.1609 | 91.0372 | 91.1562 | 91.2755 | 91.2426 | 91.1154 | 91.1813 | 122.3586 | 69.5952 | 122.249 | 69.3227 | 69.3949 | 138.7871 | 69.3635 | 138.5288 | 52.9637 | 52.9951 | 52.8542 | 52.8855
1935.8906 | 122.6212 | -69.2825 | 53.064 | 20.7383 | 20.642 | 20.784 | 20.9033 | 20.8522 | 20.6975 | 20.7817 | 53.0531 | 0.2349 | 52.9665 | -0.042259 | 0.034501 | 69.4038 | 0.003143 | 69.1684 | 90.0209 | 89.9245 | 90.0665 | 90.1858 | 90.1348 | 89.98 | 90.0642 | 122.3357 | 69.5174 | 122.249 | 69.2403 | 69.317 | 138.6863 | 69.2857 | 138.451 | 53.0186 | 53.05 | 52.932 | 52.9633
1936.8906 | 122.6532 | -69.2551 | 53.1052 | 20.4957 | 20.381 | 20.4498 | 20.5919 | 20.5867 | 20.464 | 20.5299 | 53.0898 | 0.2349 | 52.9985 | -0.042259 | 0.039079 | 69.3626 | 0.003143 | 69.1318 | 89.7507 | 89.6361 | 89.7048 | 89.847 | 89.8418 | 89.7191 | 89.785 | 122.3448 | 69.49 | 122.2536 | 69.2128 | 69.2941 | 138.6177 | 69.2582 | 138.3869 | 53.0507 | 53.0866 | 52.9595 | 52.9954
1937.8906 | 122.6807 | -69.2322 | 53.1555 | 19.96 | 19.8544 | 19.9095 | 20.0242 | 20.0328 | 19.9283 | 19.9897 | 53.1493 | 0.2349 | 53.0809 | -0.042259 | 0.025345 | 69.3168 | -0.001436 | 69.1044 | 89.1922 | 89.0866 | 89.1417 | 89.2564 | 89.265 | 89.1605 | 89.2219 | 122.3815 | 69.4671 | 122.3131 | 69.1899 | 69.2575 | 138.549 | 69.2307 | 138.3365 | 53.124 | 53.1507 | 53.0556 | 53.0824
1938.8906 | 122.612 | -69.1864 | 53.1967 | 19.841 | 19.7445 | 19.8042 | 19.9647 | 19.9275 | 19.8093 | 19.8844 | 53.1813 | 0.2349 | 53.1084 | -0.046838 | 0.029923 | 69.2756 | -0.006014 | 69.054 | 89.0274 | 88.9309 | 88.9906 | 89.1511 | 89.1139 | 88.9957 | 89.0708 | 122.3677 | 69.4213 | 122.2948 | 69.1396 | 69.2163 | 138.462 | 69.1804 | 138.2404 | 53.1514 | 53.1874 | 53.0785 | 53.1144
1939.8906 | 122.6349 | -69.1681 | 53.2059 | 19.2092 | 19.0989 | 19.1632 | 19.3237 | 19.2912 | 19.182 | 19.2389 | 53.2088 | 0.2349 | 53.0947 | -0.042259 | 0.029923 | 69.2298 | 0.007721 | 68.9853 | 88.3772 | 88.267 | 88.3313 | 88.4918 | 88.4592 | 88.3501 | 88.407 | 122.3769 | 69.403 | 122.2628 | 69.1258 | 69.198 | 138.3979 | 69.1758 | 138.1534 | 53.1789 | 53.2011 | 53.0648 | 53.087
1940.8906 | 122.6715 | -69.1086 | 53.2333 | 18.939 | 18.8242 | 18.8885 | 18.9941 | 18.9936 | 18.9028 | 18.9733 | 53.2271 | 0.23948 | 53.145 | -0.042259 | 0.034501 | 69.2436 | -0.001436 | 69.0174 | 88.0476 | 87.9328 | 87.9971 | 88.1026 | 88.1022 | 88.0113 | 88.0819 | 122.3357 | 69.3481 | 122.2536 | 69.0663 | 69.1431 | 138.3522 | 69.1071 | 138.1259 | 53.1926 | 53.2286 | 53.1105 | 53.1465
1941.8906 | 122.7173 | -69.0994 | 53.2562 | 19.0306 | 18.902 | 18.9846 | 19.0215 | 19.0577 | 18.9897 | 19.0557 | 53.2454 | 0.23948 | 53.1588 | -0.03768 | 0.029923 | 69.2207 | -0.001436 | 68.9991 | 88.13 | 88.0015 | 88.084 | 88.1209 | 88.1571 | 88.0892 | 88.1552 | 122.3449 | 69.3389 | 122.2582 | 69.0617 | 69.1293 | 138.3201 | 69.098 | 138.0985 | 53.2155 | 53.2469 | 53.1289 | 53.1602
1942.8906 | 122.6578 | -69.0033 | 53.302 | 19.612 | 19.4973 | 19.5615 | 19.5938 | 19.6391 | 19.5712 | 19.628 | 53.3187 | 0.2349 | 53.2274 | -0.046838 | 0.025345 | 69.1429 | 0.003143 | 68.8983 | 88.6153 | 88.5006 | 88.5648 | 88.5971 | 88.6424 | 88.5745 | 88.6313 | 122.322 | 69.2382 | 122.2307 | 68.9565 | 69.0286 | 138.1462 | 69.0064 | 137.9016 | 53.2934 | 53.3156 | 53.2021 | 53.2243
1943.8906 | 122.6807 | -68.9621 | 53.4027 | 19.2229 | 19.131 | 19.1769 | 19.223 | 19.25 | 19.2004 | 19.2709 | 53.3599 | 0.23948 | 53.2641 | -0.042259 | 0.034501 | 69.1108 | 0.003143 | 68.8709 | 88.185 | 88.0931 | 88.139 | 88.1851 | 88.2121 | 88.1624 | 88.233 | 122.322 | 69.2016 | 122.2262 | 68.9198 | 68.9966 | 138.0729 | 68.9652 | 137.833 | 53.3254 | 53.3568 | 53.2296 | 53.2609
1944.8906 | 122.6349 | -68.9575 | 53.4073 | 19.0535 | 18.9341 | 19.0029 | 19.0444 | 19.0897 | 19.0538 | 19.0878 | 53.3874 | 0.2349 | 53.2824 | -0.042259 | 0.034501 | 69.065 | 0.003143 | 68.8205 | 88.011 | 87.8916 | 87.9605 | 88.0019 | 88.0472 | 88.0114 | 88.0453 | 122.3449 | 69.1924 | 122.2399 | 68.9153 | 68.992 | 138.0226 | 68.9607 | 137.778 | 53.3529 | 53.3842 | 53.2479 | 53.2792
1945.8906 | 122.5983 | -68.9255 | 53.4439 | 19.0214 | 18.9066 | 18.9663 | 19.0078 | 19.0439 | 19.0126 | 19.0512 | 53.4286 | 0.2349 | 53.3511 | -0.03768 | 0.034501 | 69.033 | -0.001436 | 68.8159 | 87.9469 | 87.8321 | 87.8918 | 87.9333 | 87.9694 | 87.9381 | 87.9766 | 122.3541 | 69.1604 | 122.2765 | 68.8878 | 68.96 | 137.9585 | 68.924 | 137.7414 | 53.3941 | 53.43 | 53.3166 | 53.3525
1946.8906 | 122.5525 | -68.8522 | 53.5492 | 18.7513 | 18.6411 | 18.7007 | 18.7468 | 18.7784 | 18.7608 | 18.7856 | 53.4789 | 0.2349 | 53.3465 | -0.042259 | 0.029923 | 68.9552 | 0.007721 | 68.6969 | 87.6035 | 87.4933 | 87.553 | 87.599 | 87.6307 | 87.6131 | 87.6379 | 122.3312 | 69.0871 | 122.1987 | 68.81 | 68.8822 | 137.8074 | 68.86 | 137.5491 | 53.449 | 53.4712 | 53.3166 | 53.3388
1947.8906 | 122.4747 | -68.8293 | 53.5629 | 18.5819 | 18.4762 | 18.5405 | 18.5957 | 18.5907 | 18.5823 | 18.6254 | 53.4881 | 0.2349 | 53.3556 | -0.03768 | 0.029923 | 68.914 | 0.003143 | 68.6465 | 87.4113 | 87.3056 | 87.3698 | 87.4251 | 87.4201 | 87.4116 | 87.4547 | 122.3175 | 69.0642 | 122.185 | 68.7917 | 68.8593 | 137.7433 | 68.8325 | 137.4759 | 53.4582 | 53.485 | 53.3257 | 53.3525
1948.8906 | 122.406 | -68.7515 | 53.5767 | 18.8383 | 18.7281 | 18.7923 | 18.8246 | 18.8517 | 18.8066 | 18.868 | 53.5156 | 0.23032 | 53.3465 | -0.042259 | 0.039079 | 68.8453 | 0.003143 | 68.587 | 87.5898 | 87.4796 | 87.5438 | 87.5762 | 87.6032 | 87.5581 | 87.6196 | 122.2671 | 68.9818 | 122.098 | 68.7093 | 68.7906 | 137.5968 | 68.7547 | 137.3385 | 53.4765 | 53.5124 | 53.3074 | 53.3433
1949.8906 | 122.493 | -68.8889 | 53.5126 | 22.5331 | 22.4186 | 22.4918 | 22.5241 | 22.5369 | 22.5151 | 22.5626 | 53.4606 | 0.2349 | 53.3511 | -0.042259 | 0.034501 | 68.9414 | 0.003143 | 68.6969 | 91.4219 | 91.3074 | 91.3807 | 91.4129 | 91.4258 | 91.404 | 91.4515 | 122.3495 | 69.1238 | 122.2399 | 68.8466 | 68.9234 | 137.8303 | 68.892 | 137.5858 | 53.4261 | 53.4575 | 53.3166 | 53.3479
1950.8906 | 122.5113 | -68.9713 | 53.4348 | 23.989 | 23.8197 | 23.9249 | 23.948 | 23.9836 | 23.939 | 23.9864 | 53.3828 | 0.23948 | 53.2824 | -0.03768 | 0.029923 | 69.0284 | 0.007721 | 68.7976 | 92.9602 | 92.7909 | 92.8962 | 92.9192 | 92.9548 | 92.9102 | 92.9577 | 122.3541 | 69.2107 | 122.2536 | 68.9336 | 69.0012 | 137.9997 | 68.979 | 137.7689 | 53.3529 | 53.3751 | 53.2525 | 53.2747
1951.8906 | 122.4747 | -68.866 | 53.5309 | 24.5796 | 24.4653 | 24.543 | 24.5752 | 24.5833 | 24.5571 | 24.6182 | 53.4744 | 0.23032 | 53.3785 | -0.042259 | 0.034501 | 68.9368 | 0.003143 | 68.7061 | 93.4456 | 93.3313 | 93.409 | 93.4412 | 93.4492 | 93.423 | 93.4842 | 122.3403 | 69.0963 | 122.2445 | 68.8237 | 68.9005 | 137.8028 | 68.8691 | 137.572 | 53.4399 | 53.4712 | 53.344 | 53.3754
1952.8906 | 122.5159 | -68.8065 | 53.5767 | 24.8864 | 24.7767 | 24.8498 | 24.882 | 24.89 | 24.8638 | 24.9341 | 53.4973 | 0.2349 | 53.4106 | -0.046838 | 0.043657 | 68.8956 | -0.001436 | 68.642 | 93.6928 | 93.5831 | 93.6563 | 93.6885 | 93.6965 | 93.6703 | 93.7406 | 122.3037 | 69.0414 | 122.217 | 68.7596 | 68.8501 | 137.7021 | 68.805 | 137.4484 | 53.4536 | 53.4987 | 53.3669 | 53.412
1953.8906 | 122.5754 | -68.7424 | 53.6041 | 25.9165 | 25.8069 | 25.88 | 25.9259 | 25.9246 | 25.9031 | 25.9642 | 53.5339 | 0.2349 | 53.4152 | -0.042259 | 0.029923 | 68.8636 | 0.003143 | 68.6053 | 94.6589 | 94.5493 | 94.6224 | 94.6683 | 94.667 | 94.6455 | 94.7066 | 122.2763 | 68.9773 | 122.1575 | 68.7001 | 68.7723 | 137.606 | 68.7455 | 137.3477 | 53.504 | 53.5307 | 53.3852 | 53.412
1954.8906 | 122.493 | -68.8385 | 53.4988 | 26.2416 | 26.1091 | 26.1822 | 26.2235 | 26.2359 | 26.2144 | 26.2618 | 53.4744 | 0.2349 | 53.374 | -0.042259 | 0.029923 | 68.9231 | 0.003143 | 68.6786 | 95.0801 | 94.9476 | 95.0207 | 95.062 | 95.0744 | 95.0529 | 95.1003 | 122.3129 | 69.0734 | 122.2125 | 68.7962 | 68.8684 | 137.7616 | 68.8416 | 137.5171 | 53.4444 | 53.4712 | 53.344 | 53.3708
1955.8906 | 122.4564 | -68.8568 | 53.4988 | 27.2717 | 27.1485 | 27.2261 | 27.2537 | 27.2705 | 27.2308 | 27.2873 | 53.424 | 0.2349 | 53.3282 | -0.046838 | 0.034501 | 68.978 | 0.007721 | 68.7427 | 96.1285 | 96.0053 | 96.0829 | 96.1105 | 96.1274 | 96.0877 | 96.1441 | 122.2808 | 69.0917 | 122.185 | 68.81 | 68.8913 | 137.8349 | 68.8645 | 137.5995 | 53.3895 | 53.4163 | 53.2937 | 53.3205
1956.8906 | 122.493 | -68.8797 | 53.3844 | 28.1965 | 28.0643 | 28.1601 | 28.1831 | 28.2044 | 28.1557 | 28.2212 | 53.3462 | 0.2349 | 53.145 | -0.042259 | 0.034501 | 68.9552 | 0.003143 | 68.6603 | 97.0762 | 96.944 | 97.0398 | 97.0628 | 97.0841 | 97.0354 | 97.1009 | 122.2259 | 69.1146 | 122.0247 | 68.8374 | 68.9142 | 137.8349 | 68.8828 | 137.54 | 53.3117 | 53.343 | 53.1105 | 53.1419
1957.8906 | 122.4243 | -68.866 | 53.3295 | 29.6845 | 29.557 | 29.639 | 29.6574 | 29.6831 | 29.6437 | 29.7046 | 53.3187 | 0.2349 | 53.1221 | -0.051417 | 0.029923 | 68.9506 | 0.003143 | 68.6282 | 98.5505 | 98.4229 | 98.505 | 98.5233 | 98.5491 | 98.5096 | 98.5705 | 122.1847 | 69.1009 | 121.9881 | 68.8145 | 68.8959 | 137.8165 | 68.8691 | 137.4942 | 53.2888 | 53.3156 | 53.0922 | 53.119
1958.8906 | 122.3373 | -68.8156 | 53.3524 | 30.6597 | 30.5414 | 30.6234 | 30.6417 | 30.6491 | 30.6326 | 30.6889 | 53.305 | 0.23032 | 53.0809 | -0.042259 | 0.034501 | 68.9048 | 0.003143 | 68.5824 | 99.4753 | 99.357 | 99.439 | 99.4574 | 99.4647 | 99.4482 | 99.5045 | 122.1206 | 69.0459 | 121.8966 | 68.7734 | 68.8501 | 137.7204 | 68.8188 | 137.3981 | 53.2705 | 53.3018 | 53.0464 | 53.0778
1959.8906 | 122.2458 | -68.8339 | 53.3615 | 30.3942 | 30.285 | 30.3579 | 30.3945 | 30.3973 | 30.367 | 30.4279 | 53.3187 | 0.2349 | 53.0855 | -0.042259 | 0.029923 | 68.8544 | 0.003143 | 68.5229 | 99.2281 | 99.1189 | 99.1918 | 99.2284 | 99.2312 | 99.201 | 99.2618 | 122.1526 | 69.0688 | 121.9194 | 68.7917 | 68.8638 | 137.6884 | 68.8371 | 137.3568 | 53.2888 | 53.3156 | 53.0556 | 53.0824
1960.8906 | 122.3694 | -68.8522 | 53.3615 | 30.2843 | 30.1522 | 30.248 | 30.2617 | 30.2783 | 30.2388 | 30.3089 | 53.3141 | 0.2349 | 53.1496 | -0.046838 | 0.029923 | 68.8956 | -0.006014 | 68.6236 | 99.1365 | 99.0044 | 99.1002 | 99.114 | 99.1305 | 99.0911 | 99.1611 | 122.1664 | 69.0871 | 122.0019 | 68.8054 | 68.8822 | 137.7479 | 68.8462 | 137.4759 | 53.2842 | 53.3201 | 53.1197 | 53.1556
1961.8906 | 122.2778 | -68.8705 | 53.3844 | 30.298 | 30.1659 | 30.2571 | 30.2755 | 30.2966 | 30.2526 | 30.318 | 53.3553 | 0.23032 | 53.2229 | -0.046838 | 0.029923 | 68.9002 | 0.003143 | 68.6557 | 99.1685 | 99.0365 | 99.1277 | 99.146 | 99.1671 | 99.1231 | 99.1886 | 122.2259 | 69.1009 | 122.0934 | 68.8237 | 68.9005 | 137.7708 | 68.8737 | 137.5262 | 53.3254 | 53.3522 | 53.1929 | 53.2197
1962.8906 | 122.3419 | -68.8568 | 53.3798 | 30.5086 | 30.3766 | 30.4632 | 30.4907 | 30.5117 | 30.4723 | 30.5332 | 53.3507 | 0.2349 | 53.2183 | -0.046838 | 0.039079 | 68.9231 | -0.001436 | 68.6877 | 99.3654 | 99.2334 | 99.32 | 99.3475 | 99.3685 | 99.3292 | 99.39 | 122.2076 | 69.0917 | 122.0751 | 68.81 | 68.8959 | 137.7799 | 68.8554 | 137.5446 | 53.3117 | 53.3522 | 53.1792 | 53.2197
1963.8906 | 122.4197 | -68.8568 | 53.3981 | 30.4033 | 30.2758 | 30.3579 | 30.3808 | 30.3927 | 30.3579 | 30.4188 | 53.3462 | 0.23948 | 53.2046 | -0.03768 | 0.025345 | 68.9277 | -0.001436 | 68.6832 | 99.2601 | 99.1326 | 99.2147 | 99.2376 | 99.2495 | 99.2147 | 99.2756 | 122.203 | 69.0963 | 122.0614 | 68.8191 | 68.8822 | 137.7845 | 68.8554 | 137.54 | 53.3208 | 53.3476 | 53.1792 | 53.206
1964.8906 | 122.3648 | -68.8522 | 53.3798 | 30.0462 | 29.937 | 30.0145 | 30.0328 | 30.0448 | 30.0099 | 30.0754 | 53.3462 | 0.2349 | 53.2 | -0.046838 | 0.029923 | 68.9002 | -0.001436 | 68.6557 | 98.8984 | 98.7892 | 98.8667 | 98.885 | 98.897 | 98.8622 | 98.9276 | 122.1984 | 69.0871 | 122.0522 | 68.8054 | 68.8822 | 137.7525 | 68.8508 | 137.5079 | 53.3162 | 53.3476 | 53.1701 | 53.2014
1965.8906 | 122.3099 | -68.8522 | 53.4164 | 30.1194 | 29.9965 | 30.074 | 30.1061 | 30.1135 | 30.0786 | 30.1486 | 53.3782 | 0.23948 | 53.2824 | -0.042259 | 0.034501 | 68.8865 | 0.003143 | 68.6511 | 98.9717 | 98.8488 | 98.9262 | 98.9583 | 98.9657 | 98.9308 | 99.0009 | 122.2305 | 69.0917 | 122.1346 | 68.81 | 68.8867 | 137.7387 | 68.8554 | 137.5033 | 53.3437 | 53.3751 | 53.2479 | 53.2792
1966.8906 | 122.3465 | -68.7469 | 53.4714 | 29.7532 | 29.6485 | 29.7214 | 29.7489 | 29.7564 | 29.7306 | 29.7916 | 53.4377 | 0.23948 | 53.2824 | -0.046838 | 0.029923 | 68.7949 | -0.001436 | 68.5458 | 98.5001 | 98.3955 | 98.4684 | 98.4959 | 98.5033 | 98.4776 | 98.5385 | 122.1847 | 68.9864 | 122.0293 | 68.7001 | 68.7769 | 137.5419 | 68.7455 | 137.2928 | 53.4078 | 53.4392 | 53.2525 | 53.2838
1967.8906 | 122.4472 | -68.7424 | 53.4485 | 29.9409 | 29.8225 | 29.9137 | 29.9367 | 29.9395 | 29.9138 | 29.9747 | 53.4377 | 0.23032 | 53.287 | -0.042259 | 0.029923 | 68.7995 | -0.001436 | 68.5596 | 98.6833 | 98.5649 | 98.6561 | 98.679 | 98.6819 | 98.6562 | 98.717 | 122.1801 | 68.9727 | 122.0293 | 68.7001 | 68.7723 | 137.5419 | 68.7409 | 137.3019 | 53.4078 | 53.4392 | 53.257 | 53.2884
1968.8906 | 122.2321 | -68.6371 | 53.4302 | 29.2587 | 29.209 | 29.2453 | 29.3002 | 29.2528 | 29.2499 | 29.3475 | 53.4423 | 0.23948 | 53.2 | -0.042259 | 0.025345 | 68.7354 | 0.003143 | 68.4543 | 97.8958 | 97.846 | 97.8824 | 97.9373 | 97.8899 | 97.887 | 97.9846 | 122.0794 | 68.8766 | 121.8371 | 68.5948 | 68.6624 | 137.3725 | 68.6402 | 137.0913 | 53.417 | 53.4392 | 53.1746 | 53.1968
1969.8906 | 122.3373 | -68.6462 | 53.4851 | 30.3575 | 30.2392 | 30.3212 | 30.3441 | 30.3469 | 30.3167 | 30.3867 | 53.4744 | 0.2349 | 53.2595 | -0.03768 | 0.029923 | 68.7263 | -0.001436 | 68.3856 | 99.0038 | 98.8854 | 98.9675 | 98.9904 | 98.9932 | 98.9629 | 99.033 | 122.1206 | 68.8811 | 121.9057 | 68.6086 | 68.6762 | 137.3725 | 68.6448 | 137.0318 | 53.4444 | 53.4758 | 53.2296 | 53.2609
1970.8906 | 122.3465 | -68.7607 | 53.4668 | 30.7558 | 30.6376 | 30.7104 | 30.747 | 30.7452 | 30.715 | 30.7896 | 53.4606 | 0.23948 | 53.3648 | -0.042259 | 0.025345 | 68.8041 | -0.001436 | 68.5779 | 99.5165 | 99.3982 | 99.4711 | 99.5077 | 99.5059 | 99.4757 | 99.5503 | 122.2213 | 69.0002 | 122.1255 | 68.7184 | 68.786 | 137.5648 | 68.7592 | 137.3385 | 53.4353 | 53.4621 | 53.3395 | 53.3662
1971.8906 | 122.3145 | -68.5455 | 53.4805 | 28.9153 | 28.8106 | 28.879 | 28.9157 | 28.9049 | 28.8882 | 28.9583 | 53.4332 | 0.23948 | 53.1084 | -0.046838 | 0.029923 | 68.6439 | -0.006014 | 68.1887 | 97.4609 | 97.3561 | 97.4245 | 97.4612 | 97.4504 | 97.4338 | 97.5039 | 121.9787 | 68.785 | 121.6539 | 68.4987 | 68.5755 | 137.1894 | 68.5395 | 136.7342 | 53.4032 | 53.4392 | 53.0785 | 53.1144
1972.8906 | 122.2412 | -68.486 | 53.4348 | 28.398 | 28.284 | 28.3616 | 28.3937 | 28.3921 | 28.3709 | 28.4364 | 53.4744 | 0.24405 | 53.1679 | -0.046838 | 0.039079 | 68.5981 | 0.003143 | 68.1429 | 96.884 | 96.7701 | 96.8476 | 96.8797 | 96.8782 | 96.8569 | 96.9224 | 121.9604 | 68.7301 | 121.654 | 68.4392 | 68.5251 | 137.0841 | 68.4892 | 136.629 | 53.4353 | 53.4712 | 53.1289 | 53.1648
1973.8906 | 122.1817 | -68.4448 | 53.4073 | 28.3751 | 28.2291 | 28.325 | 28.3433 | 28.3693 | 28.3251 | 28.3815 | 53.424 | 0.2349 | 53.0168 | -0.046838 | 0.029923 | 68.5477 | 0.003143 | 68.0056 | 96.8199 | 96.6739 | 96.7698 | 96.7882 | 96.8141 | 96.7699 | 96.8263 | 121.8688 | 68.6797 | 121.4617 | 68.398 | 68.4747 | 136.9925 | 68.448 | 136.4504 | 53.3941 | 53.4209 | 52.9869 | 53.0137
1974.8906 | 122.1313 | -68.4174 | 53.4576 | 26.8413 | 26.7685 | 26.814 | 26.8736 | 26.8265 | 26.8051 | 26.9027 | 53.5339 | 0.2349 | 53.2229 | -0.042259 | 0.029923 | 68.4287 | -0.001436 | 67.9781 | 95.2587 | 95.1858 | 95.2314 | 95.291 | 95.2438 | 95.2224 | 95.3201 | 121.9512 | 68.6523 | 121.6402 | 68.3751 | 68.4473 | 136.846 | 68.4159 | 136.3955 | 53.504 | 53.5353 | 53.1929 | 53.2243
1975.8906 | 122.3053 | -68.2755 | 53.6957 | 23.7875 | 23.7144 | 23.7555 | 23.8152 | 23.7776 | 23.7513 | 23.8582 | 53.685 | 0.2349 | 53.5205 | -0.042259 | 0.034501 | 68.3829 | 0.003143 | 68.0926 | 92.063 | 91.9898 | 92.031 | 92.0907 | 92.053 | 92.0267 | 92.1337 | 121.9604 | 68.5103 | 121.7959 | 68.2332 | 68.31 | 136.6584 | 68.2786 | 136.368 | 53.6505 | 53.6818 | 53.486 | 53.5173
1976.8906 | 122.2687 | -68.1839 | 53.7781 | 21.0497 | 21.0037 | 21.0313 | 21.0864 | 21.0491 | 21.0271 | 21.1434 | 53.804 | 0.2349 | 53.6166 | -0.046838 | 0.034501 | 68.273 | 0.003143 | 67.9735 | 89.2336 | 89.1876 | 89.2152 | 89.2703 | 89.233 | 89.211 | 89.3273 | 121.9879 | 68.4188 | 121.8005 | 68.1371 | 68.2184 | 136.4569 | 68.187 | 136.1574 | 53.7695 | 53.8009 | 53.5821 | 53.6135
1977.8906 | 122.2549 | -68.4952 | 53.4531 | 32.2347 | 32.0661 | 32.1756 | 32.1847 | 32.2376 | 32.1847 | 32.2226 | 53.4652 | 0.23032 | 53.2137 | -0.03768 | 0.029923 | 68.5523 | 0.003143 | 68.1933 | 100.7298 | 100.5613 | 100.6708 | 100.6799 | 100.7328 | 100.6798 | 100.7177 | 121.9604 | 68.7255 | 121.7089 | 68.4575 | 68.5251 | 137.0475 | 68.4983 | 136.6885 | 53.4353 | 53.4621 | 53.1838 | 53.2106
1978.8906 | 122.0764 | -68.2068 | 53.5767 | 25.9577 | 26.219 | 26.0448 | 26.2327 | 25.9521 | 26.045 | 26.2938 | 53.6163 | 0.2349 | 53.1954 | -0.042259 | 0.034501 | 68.2868 | 0.003143 | 67.8637 | 94.1645 | 94.4258 | 94.2516 | 94.4394 | 94.1589 | 94.2518 | 94.5006 | 121.8231 | 68.4417 | 121.4022 | 68.1645 | 68.2413 | 136.4935 | 68.2099 | 136.0705 | 53.5818 | 53.6132 | 53.1609 | 53.1923
1979.8906 | 122.1039 | -68.2892 | 53.5629 | 27.2808 | 27.0936 | 27.2124 | 27.1941 | 27.2751 | 27.1759 | 27.2598 | 53.6026 | 0.2349 | 53.2641 | -0.046838 | 0.029923 | 68.3509 | 0.003143 | 67.8545 | 95.57 | 95.3827 | 95.5016 | 95.4833 | 95.5643 | 95.4651 | 95.549 | 121.8918 | 68.5241 | 121.5533 | 68.2423 | 68.3191 | 136.64 | 68.2923 | 136.1437 | 53.5726 | 53.5994 | 53.2342 | 53.2609
1980.8906 | 122.1176 | -68.3853 | 53.4439 | 30.797 | 30.6192 | 30.7425 | 30.747 | 30.7956 | 30.747 | 30.7804 | 53.4515 | 0.2349 | 53.0947 | -0.042259 | 0.029923 | 68.4516 | 0.003143 | 67.9323 | 99.1824 | 99.0046 | 99.1278 | 99.1324 | 99.1809 | 99.1324 | 99.1658 | 121.8368 | 68.6202 | 121.48 | 68.3431 | 68.4152 | 136.8369 | 68.3885 | 136.3177 | 53.4216 | 53.4483 | 53.0648 | 53.0915
1981.8906 | 122.113 | -68.0191 | 53.8696 | 25.802 | 25.8344 | 25.8067 | 25.8984 | 25.7919 | 25.807 | 25.9459 | 53.7582 | 0.23948 | 53.5433 | -0.042259 | 0.029923 | 68.2227 | 0.003143 | 67.8591 | 93.8211 | 93.8535 | 93.8258 | 93.9175 | 93.811 | 93.8261 | 93.965 | 121.7773 | 68.2586 | 121.5625 | 67.9768 | 68.049 | 136.2418 | 68.0222 | 135.8782 | 53.7283 | 53.7551 | 53.5134 | 53.5402
1982.8906 | 122.2137 | -68.0603 | 53.8788 | 27.0565 | 26.9837 | 27.0338 | 27.0705 | 27.0508 | 27.0294 | 27.1179 | 53.7079 | 0.2349 | 53.5296 | -0.03768 | 0.039079 | 68.3005 | 0.003143 | 67.9827 | 95.1168 | 95.044 | 95.0941 | 95.1308 | 95.1111 | 95.0897 | 95.1782 | 121.7682 | 68.2952 | 121.5899 | 68.0226 | 68.0994 | 136.3608 | 68.0634 | 136.043 | 53.6688 | 53.7047 | 53.4905 | 53.5265
1983.8906 | 122.2183 | -68.4952 | 53.4851 | 32.4544 | 32.3409 | 32.4228 | 32.4365 | 32.4482 | 32.4182 | 32.4927 | 53.5522 | 0.24405 | 53.3923 | -0.03768 | 0.025345 | 68.4745 | 0.003143 | 68.1521 | 100.9496 | 100.8361 | 100.918 | 100.9317 | 100.9434 | 100.9133 | 100.9878 | 122.0474 | 68.7392 | 121.8874 | 68.4575 | 68.5205 | 136.9696 | 68.4983 | 136.6473 | 53.5269 | 53.5491 | 53.3669 | 53.3891
1984.8906 | 122.2092 | -68.4082 | 53.5492 | 35.641 | 35.4545 | 35.5958 | 35.5682 | 35.6299 | 35.5589 | 35.6104 | 53.5659 | 0.2349 | 53.406 | -0.046838 | 0.029923 | 68.4607 | -0.001436 | 68.1475 | 104.0492 | 103.8627 | 104.004 | 103.9764 | 104.0381 | 103.9671 | 104.0186 | 121.9741 | 68.6431 | 121.8142 | 68.3614 | 68.4381 | 136.8689 | 68.4068 | 136.5557 | 53.536 | 53.5674 | 53.3761 | 53.4074
1985.8906 | 122.2321 | -68.4723 | 53.54 | 36.3461 | 36.2054 | 36.3009 | 36.3008 | 36.3441 | 36.2777 | 36.3292 | 53.5293 | 0.2349 | 53.3694 | -0.03768 | 0.029923 | 68.5065 | 0.003143 | 68.1979 | 104.8183 | 104.6777 | 104.7732 | 104.7731 | 104.8163 | 104.75 | 104.8015 | 122.0016 | 68.7072 | 121.8417 | 68.4346 | 68.5022 | 136.9788 | 68.4754 | 136.6702 | 53.4994 | 53.5262 | 53.3395 | 53.3662
1986.8906 | 121.9482 | -67.7353 | 53.9886 | 21.448 | 21.3792 | 21.425 | 21.4619 | 21.4474 | 21.4209 | 21.5188 | 53.9185 | 0.23948 | 53.4152 | -0.046838 | 0.025345 | 67.8793 | 0.003143 | 67.2227 | 89.1833 | 89.1145 | 89.1603 | 89.1972 | 89.1827 | 89.1562 | 89.2541 | 121.6538 | 67.9748 | 121.1504 | 67.6885 | 67.7606 | 135.6146 | 67.7384 | 134.958 | 53.8931 | 53.9153 | 53.3898 | 53.412
1987.8906 | 122.1313 | -67.836 | 53.9429 | 20.34 | 20.2391 | 20.2941 | 20.331 | 20.3349 | 20.2992 | 20.3834 | 53.9643 | 0.2349 | 53.6899 | -0.03768 | 0.029923 | 67.9251 | -0.001436 | 67.5111 | 88.176 | 88.0751 | 88.1301 | 88.167 | 88.1709 | 88.1352 | 88.2194 | 121.8003 | 68.0709 | 121.5259 | 67.7983 | 67.8659 | 135.7611 | 67.8346 | 135.3471 | 53.9343 | 53.9657 | 53.6599 | 53.6913
1988.8906 | 122.1268 | -68.2709 | 53.5675 | 34.1576 | 34.0121 | 34.1535 | 34.1306 | 34.1512 | 34.1122 | 34.1774 | 53.5659 | 0.23948 | 53.3694 | -0.042259 | 0.029923 | 68.36 | 0.003143 | 68.0147 | 102.4285 | 102.283 | 102.4244 | 102.4014 | 102.4221 | 102.383 | 102.4483 | 121.8368 | 68.5104 | 121.6402 | 68.2286 | 68.3008 | 136.6309 | 68.274 | 136.2856 | 53.536 | 53.5628 | 53.3395 | 53.3662
1989.8906 | 122.1451 | -68.3853 | 53.4897 | 34.5193 | 34.3281 | 34.4557 | 34.4419 | 34.5083 | 34.4601 | 34.4979 | 53.5339 | 0.23948 | 53.4243 | -0.042259 | 0.034501 | 68.4561 | 0.003143 | 68.1841 | 102.9046 | 102.7134 | 102.841 | 102.8272 | 102.8936 | 102.8454 | 102.8832 | 121.9192 | 68.6248 | 121.8096 | 68.3431 | 68.4198 | 136.8415 | 68.3885 | 136.5695 | 53.4994 | 53.5307 | 53.3898 | 53.4212
1990.8906 | 122.1497 | -68.7424 | 53.1189 | 48.1171 | 47.9958 | 48.1 | 48.1133 | 48.1094 | 48.0854 | 48.15 | 53.1447 | 0.23948 | 52.9207 | -0.03768 | 0.029923 | 68.7949 | -0.001436 | 68.4451 | 116.8595 | 116.7382 | 116.8423 | 116.8557 | 116.8518 | 116.8278 | 116.8924 | 121.8871 | 68.9818 | 121.6631 | 68.7047 | 68.7723 | 137.5373 | 68.7409 | 137.1875 | 53.1148 | 53.1462 | 52.8908 | 52.9221
1991.8906 | 122.1176 | -68.8431 | 53.064 | 50.5574 | 50.4226 | 50.5175 | 50.5445 | 50.554 | 50.5394 | 50.5719 | 53.0669 | 0.24405 | 52.9665 | -0.042259 | 0.034501 | 68.8911 | 0.007721 | 68.6511 | 119.4005 | 119.2657 | 119.3605 | 119.3875 | 119.3971 | 119.3825 | 119.415 | 121.91 | 69.0871 | 121.8096 | 68.8008 | 68.8776 | 137.7341 | 68.8508 | 137.4942 | 53.0324 | 53.0592 | 52.932 | 52.9588
1992.8906 | 122.1817 | -68.8797 | 53.0502 | 50.2781 | 50.1433 | 50.2519 | 50.2652 | 50.2702 | 50.2556 | 50.2926 | 53.0531 | 0.23948 | 52.9436 | -0.033101 | 0.029923 | 68.946 | -0.001436 | 68.6877 | 119.1578 | 119.023 | 119.1316 | 119.1449 | 119.1499 | 119.1353 | 119.1723 | 121.9328 | 69.1192 | 121.8233 | 68.8466 | 68.9096 | 137.8257 | 68.8783 | 137.5674 | 53.0232 | 53.0546 | 52.9137 | 52.945
1993.8906 | 122.2458 | -68.8797 | 53.0594 | 50.6306 | 50.5096 | 50.6182 | 50.636 | 50.6227 | 50.6081 | 50.6634 | 53.0165 | 0.2349 | 52.8978 | -0.03768 | 0.034501 | 68.9918 | 0.003143 | 68.7335 | 119.5103 | 119.3893 | 119.4979 | 119.5157 | 119.5024 | 119.4878 | 119.5431 | 121.8962 | 69.1146 | 121.7775 | 68.842 | 68.9142 | 137.8715 | 68.8828 | 137.6132 | 52.982 | 53.0134 | 52.8633 | 52.8947
1994.8906 | 122.2687 | -68.8522 | 53.0731 | 50.3925 | 50.2624 | 50.3709 | 50.3796 | 50.3847 | 50.3609 | 50.4162 | 53.044 | 0.23948 | 52.9436 | -0.042259 | 0.029923 | 68.9597 | -0.006014 | 68.7198 | 119.2448 | 119.1146 | 119.2232 | 119.2319 | 119.2369 | 119.2131 | 119.2685 | 121.8962 | 69.0917 | 121.7958 | 68.81 | 68.8822 | 137.812 | 68.8462 | 137.572 | 53.0141 | 53.05 | 52.9137 | 52.9496
1995.8906 | 122.2183 | -68.811 | 53.1006 | 50.4979 | 50.3723 | 50.4763 | 50.4941 | 50.4945 | 50.4707 | 50.5215 | 53.0898 | 0.2349 | 52.9619 | -0.042259 | 0.029923 | 68.9185 | 0.007721 | 68.6557 | 119.3089 | 119.1833 | 119.2873 | 119.3051 | 119.3056 | 119.2818 | 119.3326 | 121.9008 | 69.0459 | 121.7729 | 68.7688 | 68.841 | 137.7296 | 68.8188 | 137.4667 | 53.0599 | 53.0821 | 52.932 | 52.9542
1996.8906 | 122.2778 | -68.7607 | 53.1372 | 50.7405 | 50.6149 | 50.7235 | 50.7276 | 50.7463 | 50.718 | 50.7642 | 53.131 | 0.23948 | 53.0214 | -0.033101 | 0.029923 | 68.8911 | 0.007721 | 68.6511 | 119.5012 | 119.3756 | 119.4842 | 119.4883 | 119.507 | 119.4787 | 119.5248 | 121.8917 | 69.0002 | 121.7821 | 68.7276 | 68.7906 | 137.6517 | 68.7684 | 137.4118 | 53.1011 | 53.1233 | 52.9915 | 53.0137
1997.8906 | 122.2092 | -68.7286 | 53.2013 | 50.4292 | 50.3036 | 50.4167 | 50.4346 | 50.4213 | 50.4158 | 50.4574 | 53.1859 | 0.2349 | 53.0535 | -0.03768 | 0.034501 | 68.8316 | 0.007721 | 68.5733 | 119.1578 | 119.0322 | 119.1454 | 119.1632 | 119.1499 | 119.1444 | 119.1861 | 121.9146 | 68.9635 | 121.7821 | 68.691 | 68.7631 | 137.5602 | 68.7364 | 137.3019 | 53.1514 | 53.1782 | 53.019 | 53.0458
1998.8906 | 122.1039 | -68.7424 | 53.1509 | 50.626 | 50.4913 | 50.6045 | 50.6086 | 50.6227 | 50.5944 | 50.6406 | 53.1401 | 0.2349 | 53.0123 | -0.046838 | 0.039079 | 68.8636 | 0.003143 | 68.6008 | 119.3684 | 119.2337 | 119.3468 | 119.3509 | 119.3651 | 119.3367 | 119.3829 | 121.8825 | 68.9773 | 121.7546 | 68.6955 | 68.7815 | 137.606 | 68.7455 | 137.3431 | 53.1011 | 53.137 | 52.9732 | 53.0091
1999.8906 | 122.3923 | -68.7607 | 53.1464 | 50.4338 | 50.3082 | 50.4121 | 50.4163 | 50.4304 | 50.4112 | 50.4574 | 53.1447 | 0.23948 | 53.0077 | -0.03768 | 0.039079 | 68.8544 | -0.006014 | 68.587 | 119.1944 | 119.0688 | 119.1728 | 119.1769 | 119.1911 | 119.1719 | 119.2181 | 121.9054 | 69.0002 | 121.7684 | 68.723 | 68.7998 | 137.6151 | 68.7547 | 137.3477 | 53.1056 | 53.1507 | 52.9686 | 53.0137
2000.8906 | 122.1268 | -68.6691 | 53.1647 | 50.1728 | 50.0426 | 50.1557 | 50.1644 | 50.1741 | 50.1503 | 50.201 | 53.163 | 0.23032 | 52.8978 | -0.042259 | 0.034501 | 68.7629 | -0.001436 | 68.3718 | 118.8419 | 118.7117 | 118.8249 | 118.8336 | 118.8432 | 118.8194 | 118.8702 | 121.8322 | 68.8994 | 121.5669 | 68.6269 | 68.7036 | 137.432 | 68.6677 | 137.041 | 53.1285 | 53.1645 | 52.8633 | 52.8992
2001.8906 | 121.9208 | -68.5684 | 53.1509 | 49.834 | 49.6992 | 49.8124 | 49.8165 | 49.8353 | 49.8023 | 49.8531 | 53.1356 | 0.23948 | 52.7879 | -0.051417 | 0.029923 | 68.6622 | 0.012299 | 68.175 | 118.4024 | 118.2676 | 118.3808 | 118.3849 | 118.4037 | 118.3707 | 118.4215 | 121.704 | 68.8079 | 121.3564 | 68.517 | 68.5983 | 137.2306 | 68.5807 | 136.7434 | 53.1056 | 53.1233 | 52.758 | 52.7756
2002.8906 | 121.9757 | -68.573 | 53.2425 | 50.2872 | 50.1433 | 50.2611 | 50.2652 | 50.2839 | 50.2556 | 50.288 | 53.1676 | 0.2349 | 52.9344 | -0.046838 | 0.039079 | 68.6484 | 0.007721 | 68.2894 | 118.8602 | 118.7163 | 118.8341 | 118.8382 | 118.8569 | 118.8286 | 118.861 | 121.7406 | 68.8079 | 121.5074 | 68.5262 | 68.6121 | 137.2214 | 68.5807 | 136.8624 | 53.1285 | 53.1599 | 52.8954 | 52.9267
2003.8906 | 122.0032 | -68.4265 | 53.3249 | 46.5055 | 46.4665 | 46.5112 | 46.5429 | 46.5071 | 46.5104 | 46.598 | 53.2821 | 0.2349 | 52.9756 | -0.03768 | 0.029923 | 68.5248 | 0.003143 | 68.0972 | 114.932 | 114.893 | 114.9377 | 114.9694 | 114.9336 | 114.9369 | 115.0245 | 121.7086 | 68.6614 | 121.4022 | 68.3888 | 68.4564 | 136.9513 | 68.4297 | 136.5237 | 53.2522 | 53.2789 | 52.9457 | 52.9725
2004.8906 | 122.0123 | -68.541 | 53.2104 | 50.5803 | 50.4455 | 50.5724 | 50.5628 | 50.5769 | 50.5577 | 50.5948 | 53.1539 | 0.23948 | 52.8978 | -0.033101 | 0.034501 | 68.6301 | 0.003143 | 68.2391 | 119.1212 | 118.9865 | 119.1134 | 119.1037 | 119.1179 | 119.0987 | 119.1357 | 121.6948 | 68.7804 | 121.4388 | 68.5079 | 68.5755 | 137.1711 | 68.5441 | 136.78 | 53.1194 | 53.1507 | 52.8633 | 52.8947
2005.8906 | 121.9391 | -68.5959 | 53.2104 | 50.3651 | 50.2395 | 50.3343 | 50.3522 | 50.3526 | 50.338 | 50.3842 | 53.1447 | 0.24863 | 52.9299 | -0.042259 | 0.039079 | 68.6484 | 0.003143 | 68.2849 | 118.961 | 118.8354 | 118.9302 | 118.9481 | 118.9485 | 118.9339 | 118.9801 | 121.7406 | 68.8445 | 121.5257 | 68.5536 | 68.635 | 137.2443 | 68.599 | 136.8807 | 53.1056 | 53.1416 | 52.8908 | 52.9267
2006.8906 | 121.8933 | -67.8818 | 53.9246 | 29.2633 | 29.328 | 29.3048 | 29.3918 | 29.2574 | 29.3003 | 29.4528 | 53.8498 | 0.23948 | 53.612 | -0.042259 | 0.029923 | 67.9571 | 0.003143 | 67.589 | 97.1451 | 97.2098 | 97.1866 | 97.2736 | 97.1392 | 97.1821 | 97.3345 | 121.7316 | 68.1213 | 121.4938 | 67.8395 | 67.9117 | 135.8389 | 67.8849 | 135.4708 | 53.8199 | 53.8467 | 53.5821 | 53.6089
2007.8906 | 121.9391 | -67.7902 | 54.0115 | 25.4358 | 25.3307 | 25.3947 | 25.4223 | 25.4302 | 25.4041 | 25.4789 | 53.9276 | 0.24863 | 53.6715 | -0.042259 | 0.039079 | 67.8381 | 0.003143 | 67.4471 | 93.226 | 93.1209 | 93.1849 | 93.2125 | 93.2204 | 93.1943 | 93.2691 | 121.7179 | 68.0389 | 121.4618 | 67.748 | 67.8293 | 135.6283 | 67.7934 | 135.2373 | 53.8886 | 53.9245 | 53.6325 | 53.6684
2008.8906 | 121.8979 | -67.3004 | 54.5013 | 15.5831 | 15.6648 | 15.6239 | 15.725 | 15.5967 | 15.6201 | 15.7732 | 54.2664 | 0.23032 | 54.0561 | -0.03768 | 0.029923 | 67.536 | 0.003143 | 67.1998 | 82.8835 | 82.9652 | 82.9243 | 83.0254 | 82.8972 | 82.9205 | 83.0736 | 121.5669 | 67.5307 | 121.3565 | 67.2627 | 67.3303 | 134.8364 | 67.3036 | 134.5002 | 54.2365 | 54.2633 | 54.0262 | 54.053
2009.8906 | 121.8201 | -68.4586 | 53.183 | 48.7626 | 48.5682 | 48.6998 | 48.6993 | 48.7503 | 48.7081 | 48.7315 | 53.2042 | 0.2349 | 52.82 | -0.03768 | 0.034501 | 68.4836 | 0.007721 | 67.9964 | 117.2212 | 117.0268 | 117.1583 | 117.1579 | 117.2089 | 117.1666 | 117.19 | 121.6628 | 68.6935 | 121.2785 | 68.4209 | 68.4931 | 136.9422 | 68.4663 | 136.455 | 53.1697 | 53.1965 | 52.7855 | 52.8123
2010.8906 | 121.9391 | -67.2867 | 54.3915 | 9.2649 | 9.0759 | 9.2047 | 9.1961 | 9.2929 | 9.224 | 9.2493 | 54.5045 | 0.24405 | 54.2621 | -0.033101 | 0.034501 | 67.2109 | -0.001436 | 66.8153 | 76.5516 | 76.3626 | 76.4914 | 76.4828 | 76.5796 | 76.5107 | 76.536 | 121.7912 | 67.5307 | 121.5488 | 67.2536 | 67.3212 | 134.4976 | 67.2852 | 134.1019 | 54.47 | 54.506 | 54.2276 | 54.2636
2011.8906 | 121.9254 | -67.186 | 54.6204 | 16.0638 | 16.6767 | 16.3153 | 16.6178 | 16.0774 | 16.2748 | 16.6888 | 54.326 | 0.24405 | 54.1339 | -0.03768 | 0.029923 | 67.4902 | 0.007721 | 67.1861 | 83.2498 | 83.8627 | 83.5013 | 83.8038 | 83.2634 | 83.4607 | 83.8748 | 121.5119 | 67.43 | 121.3199 | 67.1483 | 67.2159 | 134.6762 | 67.1937 | 134.3721 | 54.296 | 54.3182 | 54.104 | 54.1262
2012.8906 | 121.9345 | -67.0532 | 54.6844 | 10.1989 | 10.2298 | 10.2029 | 10.2903 | 10.2131 | 10.2176 | 10.3435 | 54.5549 | 0.23948 | 54.3995 | -0.033101 | 0.029923 | 67.2613 | -0.001436 | 66.9755 | 77.2521 | 77.283 | 77.2561 | 77.3436 | 77.2663 | 77.2708 | 77.3967 | 121.6081 | 67.2927 | 121.4527 | 67.0201 | 67.0831 | 134.3145 | 67.0518 | 134.0287 | 54.525 | 54.5563 | 54.3696 | 54.4009
2013.8906 | 121.9894 | -68.248 | 53.5538 | 34.414 | 33.481 | 34.0162 | 33.7551 | 34.4167 | 34.0847 | 33.7791 | 53.7537 | 0.22574 | 53.6074 | -0.033101 | 0.029923 | 68.0579 | 0.003143 | 67.7767 | 102.662 | 101.729 | 102.2642 | 102.0031 | 102.6647 | 102.3327 | 102.0271 | 122.0016 | 68.4737 | 121.8554 | 68.2149 | 68.2779 | 136.3058 | 68.2511 | 136.0247 | 53.7237 | 53.7505 | 53.5775 | 53.6043
2014.8906 | 121.9528 | -67.7444 | 54.0344 | 27.3083 | 27.0936 | 27.2215 | 27.2079 | 27.3026 | 27.2125 | 27.2644 | 53.9734 | 0.23948 | 53.7814 | -0.042259 | 0.029923 | 67.8244 | 0.007721 | 67.4928 | 95.0528 | 94.838 | 94.966 | 94.9523 | 95.047 | 94.957 | 95.0088 | 121.7179 | 67.9839 | 121.5259 | 67.7022 | 67.7744 | 135.5688 | 67.7522 | 135.2373 | 53.9435 | 53.9657 | 53.7515 | 53.7737
2015.8906 | 121.9803 | -67.6437 | 54.0665 | 25.9302 | 25.7932 | 25.88 | 25.903 | 25.9292 | 25.8711 | 25.9505 | 54.0421 | 0.2349 | 53.8684 | -0.042259 | 0.020767 | 67.7557 | 0.003143 | 67.4699 | 93.574 | 93.4369 | 93.5237 | 93.5467 | 93.5729 | 93.5148 | 93.5942 | 121.6858 | 67.8786 | 121.5121 | 67.6015 | 67.6645 | 135.3994 | 67.6469 | 135.1137 | 54.0213 | 54.039 | 53.8476 | 53.8653
2016.8906 | 121.8979 | -67.3325 | 54.3823 | 17.6296 | 17.533 | 17.6019 | 17.6663 | 17.6385 | 17.6849 | 17.7876 | 54.3443 | 0.24405 | 54.1294 | -0.03768 | 0.034501 | 67.4169 | 0.003143 | 67.0533 | 84.9621 | 84.8654 | 84.9343 | 84.9987 | 84.971 | 85.0174 | 85.12 | 121.6767 | 67.5765 | 121.4618 | 67.2948 | 67.367 | 134.7494 | 67.3356 | 134.3858 | 54.3098 | 54.3411 | 54.0949 | 54.1262
2017.8906 | 121.8338 | -67.4561 | 54.2816 | 20.5735 | 20.3032 | 20.4864 | 20.4637 | 20.573 | 20.551 | 20.5803 | 54.239 | 0.2349 | 53.9691 | -0.042259 | 0.029923 | 67.4948 | -0.001436 | 67.0762 | 88.0296 | 87.7592 | 87.9425 | 87.9198 | 88.029 | 88.007 | 88.0363 | 121.695 | 67.691 | 121.4252 | 67.4138 | 67.486 | 134.9508 | 67.4546 | 134.5323 | 54.2091 | 54.2404 | 53.9392 | 53.9706
2018.8906 | 121.7148 | -67.2272 | 54.4418 | 14.1775 | 13.9981 | 14.1313 | 14.15 | 14.1684 | 14.2145 | 14.299 | 54.3901 | 0.2349 | 54.0836 | -0.042259 | 0.029923 | 67.2979 | 0.003143 | 66.8748 | 81.4047 | 81.2253 | 81.3585 | 81.3772 | 81.3956 | 81.4417 | 81.5262 | 121.6172 | 67.4621 | 121.3108 | 67.1849 | 67.2571 | 134.5251 | 67.2303 | 134.102 | 54.3601 | 54.3869 | 54.0537 | 54.0804
2019.8906 | 121.7148 | -67.2089 | 54.4373 | 14.7361 | 14.4789 | 14.6624 | 14.6903 | 14.7452 | 16.8379 | 16.9223 | 54.3901 | 0.2349 | 54.1065 | -0.042259 | 0.034501 | 67.2613 | 0.007721 | 66.829 | 81.9449 | 81.6878 | 81.8713 | 81.8991 | 81.9541 | 84.0468 | 84.1312 | 121.5989 | 67.4438 | 121.3153 | 67.1666 | 67.2434 | 134.4701 | 67.2166 | 134.0379 | 54.3556 | 54.3823 | 54.072 | 54.0988
2020.8906 | 121.6873 | -66.9159 | 54.6204 | 7.6533 | 7.4367 | 7.6114 | 7.6577 | 7.6677 | 10.2588 | 10.3435 | 54.5686 | 0.23948 | 54.2209 | -0.03768 | 0.039079 | 67.0324 | 0.003143 | 66.5406 | 74.5692 | 74.3526 | 74.5273 | 74.5736 | 74.5836 | 77.1747 | 77.2594 | 121.4845 | 67.1554 | 121.1368 | 66.8782 | 66.955 | 133.9483 | 66.919 | 133.4565 | 54.5296 | 54.5655 | 54.1819 | 54.2178
2021.8906 | 121.7285 | -66.9113 | 54.5609 | 7.58 | 7.3314 | 7.5061 | 7.4883 | 7.5762 | 8.2809 | 8.2924 | 54.5732 | 0.23948 | 54.2072 | -0.051417 | 0.034501 | 67.0003 | 0.003143 | 66.4765 | 74.4914 | 74.2427 | 74.4174 | 74.3996 | 74.4875 | 75.1922 | 75.2038 | 121.4845 | 67.1508 | 121.1185 | 66.8599 | 66.9458 | 133.9116 | 66.9145 | 133.3878 | 54.5387 | 54.5701 | 54.1727 | 54.2041
2022.8906 | 121.7514 | -67.3691 | 54.0527 | 21.7776 | 21.2235 | 21.6127 | 21.558 | 21.7861 | 23.7009 | 23.6568 | 54.1154 | 0.24405 | 53.7219 | -0.03768 | 0.034501 | 67.4124 | -0.001436 | 66.8702 | 89.1467 | 88.5926 | 88.9818 | 88.9271 | 89.1552 | 91.07 | 91.0259 | 121.4844 | 67.6131 | 121.091 | 67.3314 | 67.4036 | 134.7814 | 67.3676 | 134.2393 | 54.0809 | 54.1168 | 53.6874 | 53.7233
2023.8906 | 121.8338 | -67.5385 | 53.9703 | 29.6753 | 29.4791 | 29.6482 | 29.694 | 29.6694 | 30.4952 | 30.5744 | 53.9322 | 0.23948 | 53.6807 | -0.046838 | 0.029923 | 67.6641 | 0.003143 | 67.2777 | 97.2138 | 97.0176 | 97.1866 | 97.2324 | 97.2078 | 98.0337 | 98.1129 | 121.4707 | 67.7779 | 121.2192 | 67.4916 | 67.5684 | 135.2026 | 67.5416 | 134.8161 | 53.9023 | 53.9291 | 53.6508 | 53.6776
2024.8906 | 121.8246 | -67.4469 | 54.0985 | 25.6693 | 25.4543 | 25.6328 | 25.6603 | 25.6683 | 26.2648 | 26.3488 | 54.0742 | 0.23032 | 53.8547 | -0.046838 | 0.025345 | 67.5588 | -0.006014 | 67.2044 | 93.1162 | 92.9012 | 93.0797 | 93.1072 | 93.1152 | 93.7117 | 93.7957 | 121.5211 | 67.6772 | 121.3016 | 67.4001 | 67.4722 | 135.0057 | 67.4409 | 134.6513 | 54.0488 | 54.0802 | 53.8293 | 53.8607
2025.8906 | 121.8613 | -67.5751 | 53.952 | 28.0134 | 27.5285 | 27.9358 | 27.9038 | 28.0167 | 28.9386 | 28.9492 | 53.9643 | 0.24405 | 53.7219 | -0.042259 | 0.025345 | 67.6596 | -0.006014 | 67.2685 | 95.5885 | 95.1036 | 95.5109 | 95.4789 | 95.5918 | 96.5137 | 96.5242 | 121.5393 | 67.8191 | 121.297 | 67.5328 | 67.6004 | 135.2346 | 67.5691 | 134.8436 | 53.9389 | 53.9703 | 53.6966 | 53.7279
2026.8906 | 121.8567 | -67.6712 | 53.8422 | 33.5349 | 33.1742 | 33.4988 | 33.5216 | 33.5423 | 34.4739 | 34.53 | 53.8223 | 0.2349 | 53.58 | -0.042259 | 0.034501 | 67.7832 | -0.001436 | 67.3875 | 101.2061 | 100.8454 | 101.17 | 101.1928 | 101.2135 | 102.1451 | 102.2012 | 121.4935 | 67.9061 | 121.2512 | 67.6289 | 67.7057 | 135.4544 | 67.6698 | 135.0587 | 53.7878 | 53.8238 | 53.5455 | 53.5814
2027.8906 | 121.8201 | -68.2068 | 53.3798 | 48.4147 | 48.179 | 48.3884 | 48.3971 | 48.407 | 48.8454 | 48.9008 | 53.3507 | 0.2349 | 53.1221 | -0.03768 | 0.025345 | 68.273 | -0.001436 | 67.9415 | 116.6215 | 116.3858 | 116.5952 | 116.6039 | 116.6138 | 117.0522 | 117.1076 | 121.5575 | 68.4417 | 121.3289 | 68.1691 | 68.2321 | 136.4798 | 68.2054 | 136.1483 | 53.3254 | 53.3522 | 53.0968 | 53.1236
2028.8906 | 121.8521 | -68.1519 | 53.421 | 49.2296 | 48.9803 | 49.2126 | 49.235 | 49.231 | 49.729 | 49.7753 | 53.4011 | 0.24405 | 53.2183 | -0.042259 | 0.029923 | 68.241 | 0.007721 | 67.9278 | 117.3815 | 117.1322 | 117.3644 | 117.3869 | 117.3829 | 117.8809 | 117.9271 | 121.553 | 68.3959 | 121.3701 | 68.1096 | 68.1818 | 136.3928 | 68.1596 | 136.0796 | 53.3712 | 53.3934 | 53.1884 | 53.2106
2029.8906 | 121.8475 | -68.1747 | 53.3936 | 48.6253 | 48.3896 | 48.6128 | 48.6169 | 48.6221 | 49.0926 | 49.1435 | 53.3782 | 0.23948 | 53.1817 | -0.042259 | 0.034501 | 68.241 | 0.007721 | 67.9095 | 116.8 | 116.5644 | 116.7875 | 116.7917 | 116.7969 | 117.2674 | 117.3182 | 121.553 | 68.4142 | 121.3564 | 68.1325 | 68.2092 | 136.4157 | 68.1825 | 136.0842 | 53.3437 | 53.3705 | 53.1472 | 53.1739
2030.8906 | 121.8384 | -68.1244 | 53.4119 | 49.5959 | 49.4153 | 49.5834 | 49.615 | 49.5927 | 49.9076 | 49.9767 | 53.4011 | 0.24405 | 53.2091 | -0.042259 | 0.034501 | 68.2318 | 0.003143 | 67.8957 | 117.7203 | 117.5397 | 117.7078 | 117.7394 | 117.7171 | 118.032 | 118.1011 | 121.5255 | 68.3684 | 121.3335 | 68.0821 | 68.1589 | 136.3562 | 68.1275 | 136.0201 | 53.3666 | 53.398 | 53.1746 | 53.206
2031.8906 | 121.9391 | -68.1061 | 53.4393 | 49.0694 | 48.7834 | 49.0523 | 49.061 | 49.0662 | 49.7611 | 49.8027 | 53.4286 | 0.2349 | 53.2687 | -0.042259 | 0.039079 | 68.2181 | -0.001436 | 67.9369 | 117.1755 | 116.8895 | 117.1584 | 117.1671 | 117.1723 | 117.8672 | 117.9088 | 121.5347 | 68.341 | 121.3747 | 68.0638 | 68.1452 | 136.3242 | 68.1046 | 136.043 | 53.3895 | 53.43 | 53.2296 | 53.2701
2032.8906 | 121.9025 | -68.129 | 53.4393 | 49.4586 | 49.2688 | 49.4461 | 49.4594 | 49.4507 | 49.8618 | 49.9172 | 53.4011 | 0.23032 | 53.2458 | -0.03768 | 0.029923 | 68.2456 | 0.003143 | 67.9552 | 117.5875 | 117.3977 | 117.575 | 117.5883 | 117.5797 | 117.9908 | 118.0462 | 121.5301 | 68.3593 | 121.3747 | 68.0913 | 68.1589 | 136.3745 | 68.1321 | 136.0842 | 53.3712 | 53.398 | 53.2158 | 53.2426
2033.8906 | 121.875 | -68.0191 | 53.5355 | 45.164 | 44.7998 | 45.1559 | 45.151 | 45.1612 | 46.515 | 46.5751 | 53.5018 | 0.23948 | 53.2915 | -0.046838 | 0.029923 | 68.0899 | 0.007721 | 67.7446 | 113.1831 | 112.8189 | 113.175 | 113.1701 | 113.1803 | 114.5341 | 114.5942 | 121.5209 | 68.2586 | 121.3106 | 67.9723 | 68.049 | 136.109 | 68.0268 | 135.7637 | 53.4719 | 53.4941 | 53.2616 | 53.2838
2034.8906 | 121.7972 | -68.1198 | 53.476 | 47.9156 | 47.6936 | 47.8939 | 47.8935 | 47.9034 | 48.7905 | 48.8413 | 53.4332 | 0.24405 | 53.2412 | -0.03768 | 0.029923 | 68.186 | -0.001436 | 67.8728 | 116.0355 | 115.8135 | 116.0137 | 116.0133 | 116.0232 | 116.9103 | 116.9611 | 121.553 | 68.3639 | 121.361 | 68.0821 | 68.1497 | 136.3059 | 68.1184 | 135.9926 | 53.4032 | 53.4346 | 53.2113 | 53.2426
2035.8906 | 121.6644 | -68.1335 | 53.4714 | 47.3617 | 47.1442 | 47.3353 | 47.3349 | 47.3632 | 48.1587 | 48.205 | 53.424 | 0.2349 | 53.2549 | -0.042259 | 0.034501 | 68.1906 | -0.001436 | 67.8774 | 115.4952 | 115.2777 | 115.4689 | 115.4685 | 115.4967 | 116.2922 | 116.3385 | 121.5576 | 68.3684 | 121.3885 | 68.0913 | 68.168 | 136.3242 | 68.1321 | 136.0109 | 53.3895 | 53.4254 | 53.2204 | 53.2564
2036.8906 | 121.4722 | -67.598 | 53.7323 | 34.24 | 34.438 | 34.3138 | 34.4144 | 34.2473 | 32.5921 | 32.7765 | 53.7125 | 0.23948 | 53.2412 | -0.03768 | 0.039079 | 67.7374 | -0.001436 | 67.1541 | 101.838 | 102.0359 | 101.9117 | 102.0124 | 101.8453 | 100.1901 | 100.3745 | 121.3104 | 67.8374 | 120.8391 | 67.5603 | 67.637 | 135.3354 | 67.5965 | 134.752 | 53.6734 | 53.7139 | 53.2021 | 53.2426
2037.8906 | 121.6599 | -65.7303 | 55.8105 | -12.7892 | -12.8612 | -12.7314 | -12.7715 | -12.6996 | -12.6378 | -12.5566 | 55.7087 | 0.24405 | -8.3458 | -0.042259 | 0.034501 | 65.6361 | 0.003143 | 34.7955 | 52.9411 | 52.8691 | 52.9989 | 52.9587 | 53.0307 | 53.0925 | 53.1737 | 121.439 | 65.9743 | 57.3844 | 65.688 | 65.7648 | 131.3663 | 65.7334 | 100.5258 | 55.6742 | 55.7055 | -8.3803 | -8.349
2038.8906 | 121.6599 | -67.1677 | 54.3182 | 8.7384 | 8.5677 | 8.6782 | 8.7245 | 8.7664 | 9.1004 | 9.144 | 54.2756 | 0.24405 | 13.4651 | -0.042259 | 0.034501 | 66.9179 | -0.001436 | 21.5142 | 75.906 | 75.7353 | 75.8459 | 75.8922 | 75.9341 | 76.2681 | 76.3117 | 121.4433 | 67.4117 | 80.6327 | 67.1254 | 67.2022 | 134.0856 | 67.1662 | 88.6819 | 54.2411 | 54.277 | 13.4306 | 13.4665
2039.8906 | 121.7743 | -67.5018 | 53.9932 | 13.0741 | 13.0503 | 13.0736 | 13.1519 | 13.0926 | 13.4133 | 13.5528 | 53.891 | 0.2349 | 17.407 | -0.03768 | 0.034501 | 67.2796 | 0.007721 | 11.1264 | 80.5759 | 80.5521 | 80.5755 | 80.6537 | 80.5944 | 80.9151 | 81.0546 | 121.3928 | 67.7367 | 84.9088 | 67.4642 | 67.5363 | 134.7814 | 67.5096 | 78.6282 | 53.8565 | 53.8833 | 17.3725 | 17.3993
2040.8906 | 121.7422 | -67.2089 | 54.3457 | 10.263 | 10.358 | 10.3127 | 10.4185 | 10.2726 | 10.4739 | 10.6365 | 54.0101 | 0.24405 | 13.0256 | -0.046838 | 0.034501 | 67.3574 | 0.003143 | 4.5933 | 77.4718 | 77.5668 | 77.5216 | 77.6274 | 77.4814 | 77.6828 | 77.8453 | 121.2189 | 67.4529 | 80.2344 | 67.162 | 67.2434 | 134.5663 | 67.212 | 71.8022 | 53.9756 | 54.0069 | 12.9911 | 13.0224
2041.8906 | 121.5866 | -66.9022 | 54.5654 | 3.4412 | 3.302 | 3.3899 | 3.4226 | 3.4652 | 3.5514 | 3.6044 | 54.2848 | 0.23948 | 7.7834 | -0.042259 | 0.034501 | 66.6844 | -0.001436 | 25.012 | 70.3433 | 70.2042 | 70.2921 | 70.3248 | 70.3673 | 70.4536 | 70.5066 | 121.1869 | 67.1416 | 74.6856 | 66.8599 | 66.9367 | 133.5866 | 66.9007 | 91.9141 | 54.2503 | 54.2862 | 7.7489 | 7.7849
2042.8906 | 121.6049 | -67.2226 | 54.2587 | 5.3962 | 5.2938 | 5.3633 | 5.4051 | 5.4291 | 5.4743 | 5.541 | 54.1108 | 0.24405 | 8.3603 | -0.046838 | 0.034501 | 67.0095 | 0.003143 | 12.628 | 72.6187 | 72.5164 | 72.5859 | 72.6277 | 72.6517 | 72.6969 | 72.7636 | 121.3334 | 67.4667 | 75.5829 | 67.1758 | 67.2571 | 134.2321 | 67.2257 | 79.8506 | 54.0763 | 54.1076 | 8.3258 | 8.3572
2043.8906 | 121.6095 | -67.63 | 53.8467 | 12.2317 | 12.0384 | 12.1533 | 12.1767 | 12.2548 | 12.3053 | 12.3579 | 53.6987 | 0.24405 | 15.8458 | -0.042259 | 0.034501 | 67.3437 | 0.003143 | 7.0976 | 79.8617 | 79.6684 | 79.7834 | 79.8067 | 79.8848 | 79.9353 | 79.9879 | 121.3287 | 67.8741 | 83.4758 | 67.5877 | 67.6645 | 134.9737 | 67.6331 | 74.7276 | 53.6642 | 53.6956 | 15.8113 | 15.8426
2044.8906 | 121.6324 | -67.662 | 53.8376 | 12.7399 | 12.8168 | 12.7852 | 12.8955 | 12.7493 | 12.8501 | 12.9942 | 53.5659 | 0.2349 | 14.9896 | -0.042259 | 0.029923 | 67.7008 | -0.001436 | -2.5853 | 80.4019 | 80.4788 | 80.4472 | 80.5575 | 80.4113 | 80.5122 | 80.6563 | 121.228 | 67.8969 | 82.6517 | 67.6198 | 67.692 | 135.3628 | 67.6606 | 65.0768 | 53.536 | 53.5674 | 14.9597 | 14.9911
2045.8906 | 121.6141 | -66.7099 | 54.7714 | 1.8342 | 1.8322 | 1.824 | 1.9163 | 1.8491 | 1.9856 | 2.1577 | 54.326 | 0.23948 | 6.355 | -0.033101 | 0.029923 | 66.7668 | -0.001436 | 13.182 | 68.5441 | 68.5421 | 68.5339 | 68.6262 | 68.559 | 68.6955 | 68.8676 | 121.0359 | 66.9494 | 73.0649 | 66.6768 | 66.7398 | 133.4767 | 66.7085 | 79.8919 | 54.296 | 54.3274 | 6.3251 | 6.3564
2046.8906 | 121.4722 | -66.7465 | 54.6295 | 3.6106 | 3.4669 | 3.5685 | 3.6149 | 3.6345 | 3.7895 | 3.8654 | 54.2115 | 0.2349 | 9.5415 | -0.042259 | 0.034501 | 66.5242 | -0.006014 | 16.7163 | 70.3571 | 70.2134 | 70.315 | 70.3614 | 70.3811 | 70.536 | 70.6119 | 120.958 | 66.9814 | 76.288 | 66.7043 | 66.781 | 133.2707 | 66.7405 | 83.4628 | 54.177 | 54.2175 | 9.507 | 9.5475
2047.8906 | 121.463 | -67.2592 | 54.0207 | 9.503 | 9.2224 | 9.4382 | 9.4296 | 9.5172 | 9.6361 | 9.6659 | 53.6896 | 0.2349 | 15.0675 | -0.042259 | 0.029923 | 66.9225 | 0.007721 | 9.8079 | 76.7622 | 76.4816 | 76.6975 | 76.6888 | 76.7764 | 76.8953 | 76.9251 | 120.9488 | 67.4941 | 82.3267 | 67.217 | 67.2891 | 134.1817 | 67.2669 | 77.0671 | 53.6596 | 53.6818 | 15.0376 | 15.0598
2048.8906 | 121.4172 | -66.6412 | 54.6021 | -0.62443 | -0.79603 | -0.66674 | -0.64311 | -0.59549 | -0.39973 | -0.3603 | 54.3489 | 0.23948 | 5.1784 | -0.042259 | 0.029923 | 66.1534 | -0.001436 | 19.6738 | 66.0168 | 65.8452 | 65.9745 | 65.9981 | 66.0457 | 66.2415 | 66.2809 | 120.9901 | 66.8807 | 71.8196 | 66.599 | 66.6712 | 132.7946 | 66.6398 | 86.3151 | 54.3189 | 54.3503 | 5.1485 | 5.1798
2049.8906 | 121.3898 | -66.8152 | 54.3823 | 0.75367 | 0.65088 | 0.73431 | 0.78538 | 0.78705 | 0.87764 | 0.98111 | 54.2436 | 0.23032 | 6.8678 | -0.042259 | 0.025345 | 66.0756 | -0.001436 | 18.3828 | 67.5689 | 67.4661 | 67.5495 | 67.6006 | 67.6022 | 67.6928 | 67.7963 | 121.0587 | 67.0455 | 73.683 | 66.7729 | 66.8405 | 132.8907 | 66.8137 | 85.198 | 54.2182 | 54.245 | 6.8424 | 6.8692
2050.8906 | 121.2067 | -66.2933 | 54.8584 | 0.63005 | 0.52725 | 0.57864 | 0.60224 | 0.65429 | 0.62125 | 0.65606 | 54.1886 | 0.2349 | 7.5225 | -0.042259 | 0.034501 | 65.9199 | 0.003143 | 19.2755 | 66.9234 | 66.8206 | 66.872 | 66.8956 | 66.9476 | 66.9146 | 66.9494 | 120.4819 | 66.5282 | 73.8158 | 66.2511 | 66.3278 | 132.2132 | 66.2965 | 85.5689 | 54.1541 | 54.1855 | 7.488 | 7.5193
2051.8906 | 121.1014 | -66.7145 | 54.2221 | 6.5041 | 6.3149 | 6.4255 | 6.4032 | 6.5232 | 6.4404 | 6.4474 | 53.6438 | 0.24405 | 16.6882 | -0.03768 | 0.025345 | 65.7276 | 0.007721 | 24.6594 | 73.2186 | 73.0294 | 73.14 | 73.1177 | 73.2377 | 73.1549 | 73.1619 | 120.3583 | 66.9585 | 83.4027 | 66.6768 | 66.7398 | 132.4421 | 66.7222 | 91.3739 | 53.6184 | 53.6361 | 16.6628 | 16.6805
2052.8906 | 121.2204 | -66.2155 | 54.7943 | 3.4366 | 3.3661 | 3.3853 | 3.4455 | 3.4468 | 3.3912 | 3.5083 | 54.1703 | 0.23948 | 14.3578 | -0.042259 | 0.034501 | 65.7185 | 0.007721 | 35.2671 | 69.6521 | 69.5816 | 69.6008 | 69.661 | 69.6624 | 69.6067 | 69.7238 | 120.3858 | 66.455 | 80.5734 | 66.1733 | 66.25 | 131.934 | 66.2232 | 101.4826 | 54.1358 | 54.1626 | 14.3233 | 14.3501
2053.8906 | 121.1838 | -66.5268 | 54.4327 | 4.0776 | 3.9522 | 4.0309 | 4.0407 | 4.1015 | 4.0505 | 4.1034 | 53.9414 | 0.23948 | 15.301 | -0.042259 | 0.029923 | 65.9062 | -0.006014 | 29.4116 | 70.6044 | 70.479 | 70.5577 | 70.5675 | 70.6283 | 70.5773 | 70.6302 | 120.4682 | 66.7663 | 81.8278 | 66.4845 | 66.5567 | 132.433 | 66.5208 | 95.9384 | 53.9115 | 53.9474 | 15.2711 | 15.307
2054.8906 | 121.0419 | -66.2796 | 54.6204 | 1.4175 | 1.3331 | 1.3799 | 1.4035 | 1.4417 | 1.3767 | 1.4481 | 53.7811 | 0.2349 | 14.248 | -0.042259 | 0.039079 | 65.7414 | 0.003143 | 33.9028 | 67.6971 | 67.6127 | 67.6595 | 67.6831 | 67.7213 | 67.6563 | 67.7277 | 120.0607 | 66.5145 | 80.5276 | 66.2373 | 66.3187 | 132.021 | 66.2827 | 100.1824 | 53.742 | 53.778 | 14.2089 | 14.2448
2055.9062 | 120.9503 | -65.6754 | 55.1514 | -9.3554 | -9.363 | -9.389 | -9.3194 | -9.2845 | -9.41 | -9.2465 | 54.3489 | 0.23948 | 6.6526 | -0.03768 | 0.034501 | 64.9906 | 0.012299 | 39.3691 | 56.3199 | 56.3124 | 56.2864 | 56.356 | 56.3909 | 56.2654 | 56.4288 | 120.0242 | 65.9148 | 72.328 | 65.6377 | 65.7099 | 130.6659 | 65.6877 | 105.0445 | 54.3144 | 54.3366 | 6.6181 | 6.6403
2056.8906 | 120.9732 | -66.687 | 54.0115 | 7.7632 | 7.6015 | 7.7075 | 7.731 | 7.7867 | 7.7315 | 7.766 | 53.1539 | 0.2349 | 24.7322 | -0.042259 | 0.034501 | 65.9428 | 0.007721 | 23.5103 | 74.4502 | 74.2885 | 74.3945 | 74.418 | 74.4738 | 74.4185 | 74.453 | 119.8409 | 66.9219 | 91.4192 | 66.6448 | 66.7215 | 132.6298 | 66.6947 | 90.1973 | 53.1194 | 53.1462 | 24.6977 | 24.7245
2057.8906 | 120.9412 | -66.3528 | 54.4464 | -3.7103 | -7.9115 | -3.7252 | -3.6878 | -3.6536 | -3.5085 | -3.4002 | 53.6896 | 0.23948 | 23.5602 | -0.042259 | 0.029923 | 65.7002 | -0.006014 | 24.4305 | 62.6426 | 58.4413 | 62.6276 | 62.665 | 62.6993 | 62.8444 | 62.9526 | 120.0424 | 66.5923 | 89.913 | 66.3106 | 66.3828 | 132.053 | 66.3468 | 90.7834 | 53.6596 | 53.6956 | 23.5303 | 23.5662
2058.8906 | 120.9457 | -66.1285 | 54.6616 | -11.5118 | -11.5425 | -11.4768 | -11.4896 | -11.4178 | -11.5344 | -11.4303 | 53.9872 | 0.24863 | 24.5949 | -0.03768 | 0.034501 | 65.5628 | -0.001436 | 23.1761 | 54.6167 | 54.586 | 54.6517 | 54.639 | 54.7108 | 54.5942 | 54.6982 | 120.1157 | 66.3772 | 90.7234 | 66.0909 | 66.163 | 131.6914 | 66.1271 | 89.3047 | 53.9527 | 53.9886 | 24.5604 | 24.5963
2059.8906 | 120.8542 | -65.6845 | 55.0598 | -17.0975 | -17.179 | -17.0627 | -17.1074 | -17.0304 | -17.1292 | -17.0569 | 54.3763 | 0.2349 | 19.7465 | -0.03768 | 0.029923 | 65.0455 | 0.003143 | 28.9767 | 48.587 | 48.5055 | 48.6218 | 48.5771 | 48.6541 | 48.5554 | 48.6276 | 120.0608 | 65.9194 | 85.431 | 65.6468 | 65.7144 | 130.73 | 65.6877 | 94.6612 | 54.3464 | 54.3732 | 19.7166 | 19.7433
2060.9062 | 120.9595 | -65.8951 | 54.7623 | -23.2417 | -23.3284 | -23.2438 | -23.2655 | -23.1923 | -23.2734 | -23.2054 | 54.152 | 0.23948 | 20.2547 | -0.042259 | 0.029923 | 65.3202 | 0.003143 | 31.9113 | 42.6534 | 42.5667 | 42.6513 | 42.6296 | 42.7028 | 42.6217 | 42.6897 | 120.0471 | 66.1346 | 86.1498 | 65.8528 | 65.925 | 131.2153 | 65.8982 | 97.8064 | 54.1221 | 54.1488 | 20.2247 | 20.2515
2061.8906 | 120.9641 | -65.6891 | 55.0186 | -23.6629 | -23.768 | -23.6559 | -23.6821 | -23.618 | -23.6808 | -23.6266 | 54.3031 | 0.23948 | 19.838 | -0.046838 | 0.029923 | 65.1233 | -0.001436 | 33.0833 | 42.0262 | 41.9211 | 42.0332 | 42.007 | 42.071 | 42.0083 | 42.0625 | 119.9922 | 65.9286 | 85.5271 | 65.6422 | 65.719 | 130.8124 | 65.6877 | 98.7724 | 54.2732 | 54.3045 | 19.8081 | 19.8395
2062.8906 | 120.9366 | -66.1697 | 54.4235 | -14.4878 | -14.7477 | -14.3247 | -14.6029 | -14.4072 | -14.4645 | -14.5481 | 53.9963 | 0.23948 | 16.7294 | -0.046838 | 0.020767 | 65.311 | -0.006014 | 29.5215 | 51.682 | 51.4221 | 51.845 | 51.5668 | 51.7625 | 51.7052 | 51.6217 | 120.1661 | 66.4092 | 82.8991 | 66.1229 | 66.1905 | 131.4808 | 66.1637 | 95.6912 | 53.9756 | 54.0023 | 16.7086 | 16.7354
2063.8906 | 120.8908 | -65.4648 | 55.1056 | -21.9414 | -22.0097 | -21.9435 | -21.9469 | -21.883 | -21.9594 | -21.8914 | 54.413 | 0.24405 | 14.6875 | -0.042259 | 0.029923 | 64.8853 | 0.003143 | 31.3573 | 43.5234 | 43.4551 | 43.5213 | 43.5179 | 43.5818 | 43.5054 | 43.5733 | 119.8777 | 65.7088 | 80.1523 | 65.4225 | 65.4947 | 130.35 | 65.4679 | 96.8221 | 54.383 | 54.4098 | 14.6576 | 14.6843
2064.8906 | 120.8725 | -65.8127 | 54.7485 | -18.1642 | -18.2688 | -18.1158 | -18.1604 | -18.0925 | -18.1776 | -18.1236 | 54.1749 | 0.23948 | 16.3906 | -0.046838 | 0.025345 | 65.2057 | 0.007721 | 24.6915 | 47.6485 | 47.5439 | 47.6969 | 47.6522 | 47.7202 | 47.6351 | 47.6891 | 119.9876 | 66.0522 | 82.2033 | 65.7658 | 65.838 | 131.0184 | 65.8204 | 90.5042 | 54.1495 | 54.1672 | 16.3653 | 16.3829
2065.9062 | 120.8313 | -65.2405 | 55.2704 | -27.7926 | -27.811 | -27.8774 | -27.7799 | -27.7703 | -27.8426 | -27.7149 | 54.6236 | 0.24405 | 13.9321 | -0.042259 | 0.029923 | 64.7159 | 0.003143 | 35.0977 | 37.4479 | 37.4294 | 37.3631 | 37.4606 | 37.4702 | 37.3979 | 37.5256 | 119.8641 | 65.4845 | 79.1725 | 65.1982 | 65.2704 | 129.9563 | 65.2436 | 100.3382 | 54.5936 | 54.6204 | 13.9021 | 13.9289
2066.8906 | 120.9045 | -65.0894 | 55.4764 | -26.3641 | -26.3458 | -26.4214 | -26.3376 | -26.3236 | -26.3821 | -26.2728 | 54.6602 | 0.23032 | 14.9713 | -0.042259 | 0.029923 | 64.725 | -0.001436 | 36.5764 | 38.7253 | 38.7436 | 38.668 | 38.7518 | 38.7658 | 38.7073 | 38.8167 | 119.7496 | 65.3197 | 80.0608 | 65.0472 | 65.1193 | 129.8144 | 65.088 | 101.6658 | 54.6303 | 54.6616 | 14.9414 | 14.9728
2067.8906 | 120.8221 | -65.5151 | 55.0369 | -16.9555 | -16.9821 | -16.9345 | -16.9471 | -16.8793 | -16.9781 | -16.8875 | 54.4496 | 0.2349 | 16.8072 | -0.046838 | 0.034501 | 65.0272 | 0.003143 | 25.4927 | 48.5596 | 48.533 | 48.5806 | 48.568 | 48.6358 | 48.5371 | 48.6276 | 119.9647 | 65.75 | 82.3224 | 65.4683 | 65.5496 | 130.5423 | 65.5183 | 91.0078 | 54.4151 | 54.4464 | 16.7727 | 16.8041
2068.8906 | 120.6299 | -66.037 | 54.2908 | -1.6408 | -1.6202 | -1.674 | -1.6046 | -1.5935 | -1.6176 | -1.546 | 53.5568 | 0.24405 | 17.5352 | -0.042259 | 0.034501 | 65.0775 | 0.003143 | 22.5901 | 64.3962 | 64.4168 | 64.363 | 64.4324 | 64.4435 | 64.4194 | 64.4909 | 119.5938 | 66.281 | 83.5722 | 65.9947 | 66.0715 | 131.1145 | 66.0401 | 88.6271 | 53.5223 | 53.5536 | 17.5007 | 17.532
2069.8906 | 120.3369 | -65.7532 | 54.3961 | 4.7231 | 4.6894 | 4.6719 | 4.7183 | 4.7378 | 4.6869 | 4.7718 | 53.0669 | 0.23948 | 16.1113 | -0.042259 | 0.034501 | 64.5968 | 0.003143 | 24.1421 | 70.4763 | 70.4426 | 70.4251 | 70.4715 | 70.491 | 70.44 | 70.525 | 118.8201 | 65.9926 | 81.8645 | 65.7109 | 65.7877 | 130.35 | 65.7563 | 89.8953 | 53.0324 | 53.0637 | 16.0768 | 16.1082
2070.9062 | 120.5521 | -64.92 | 55.3848 | -7.405 | -4.4545 | -10.7122 | -7.488 | -7.3388 | -7.3772 | -5.0071 | 54.2024 | 0.23948 | 0.46734 | -0.042259 | 0.029923 | 64.2947 | -0.001436 | 26.8615 | 57.515 | 60.4655 | 54.2079 | 57.4321 | 57.5812 | 57.5429 | 59.9129 | 119.1224 | 65.1595 | 65.3874 | 64.8778 | 64.95 | 129.2147 | 64.9186 | 91.7816 | 54.1724 | 54.2038 | 0.43742 | 0.46878
2071.8906 | 120.4422 | -65.2313 | 54.9774 | -4.6259 | -1.7805 | -7.1729 | -4.8233 | -4.5737 | -4.589 | -2.2831 | 53.9322 | 0.2349 | 3.7912 | -0.046838 | 0.034501 | 64.3267 | -0.001436 | 24.9296 | 60.6054 | 63.4509 | 58.0584 | 60.408 | 60.6576 | 60.6424 | 62.9482 | 119.1635 | 65.4662 | 69.0225 | 65.1845 | 65.2658 | 129.5581 | 65.2299 | 90.1609 | 53.8977 | 53.9337 | 3.7567 | 3.7926
2072.8906 | 120.3232 | -65.7394 | 54.3823 | 2.4614 | 3.9568 | 1.476 | 2.3466 | 2.5038 | 2.5167 | 3.7784 | 53.2042 | 0.24405 | 12.0641 | -0.03768 | 0.029923 | 64.5739 | 0.003143 | 18.424 | 68.2008 | 69.6962 | 67.2155 | 68.0861 | 68.2432 | 68.2561 | 69.5178 | 118.9437 | 65.9835 | 77.8036 | 65.7018 | 65.7694 | 130.3134 | 65.7426 | 84.1634 | 53.1743 | 53.2011 | 12.0342 | 12.061
2073.8906 | 120.2728 | -64.7552 | 55.1743 | 0.4286 | 2.1069 | -0.53396 | 0.36416 | 0.45744 | 0.41065 | 1.9288 | 53.4881 | 0.24405 | 11.7345 | -0.03768 | 0.034501 | 63.5897 | 0.012299 | 23.1761 | 65.1839 | 66.8622 | 64.2213 | 65.1194 | 65.2127 | 65.1659 | 66.684 | 118.2434 | 64.9993 | 76.4897 | 64.7176 | 64.7898 | 128.3449 | 64.7675 | 87.9314 | 53.4536 | 53.4758 | 11.7 | 11.7222
2074.8906 | 120.3186 | -64.5493 | 55.4672 | -8.1925 | -6.9316 | -8.8853 | -8.1976 | -8.1171 | -8.2196 | -6.9437 | 54.4084 | 0.23948 | 0.5406 | -0.042259 | 0.034501 | 63.4477 | 0.003143 | 26.2435 | 56.3568 | 57.6176 | 55.6639 | 56.3516 | 56.4322 | 56.3296 | 57.6055 | 118.9576 | 64.7887 | 65.0899 | 64.507 | 64.5838 | 127.997 | 64.5524 | 90.7927 | 54.3739 | 54.4052 | 0.50609 | 0.53745
2075.8906 | 120.2042 | -65.007 | 54.8813 | 2.9559 | 4.1583 | 2.2178 | 2.9464 | 2.9753 | 2.9425 | 4.1767 | 53.4103 | 0.23948 | 11.9405 | -0.042259 | 0.034501 | 63.9742 | 0.003143 | 15.0544 | 67.9629 | 69.1653 | 67.2248 | 67.9534 | 67.9823 | 67.9495 | 69.1837 | 118.4173 | 65.2465 | 76.9475 | 64.9648 | 65.0415 | 128.9812 | 65.0102 | 80.0615 | 53.3758 | 53.4071 | 11.906 | 11.9374
2076.8906 | 120.369 | -63.9404 | 56.0165 | -12.2169 | -10.9427 | -12.9191 | -12.1855 | -12.1411 | -12.2669 | -10.9496 | 54.6098 | 0.2349 | -2.9984 | -0.046838 | 0.025345 | 62.7565 | -0.001436 | 29.5627 | 51.7235 | 52.9977 | 51.0213 | 51.7549 | 51.7993 | 51.6735 | 52.9908 | 118.5503 | 64.1753 | 60.942 | 63.8936 | 63.9658 | 126.6969 | 63.939 | 93.5031 | 54.5845 | 54.6113 | -3.0238 | -2.997
2077.8906 | 120.5063 | -64.0503 | 56.1081 | -15.4492 | -14.9034 | -15.7349 | -15.4729 | -15.364 | -15.4397 | -14.8182 | 55.2417 | 0.24405 | -7.9155 | -0.046838 | 0.029923 | 63.2326 | 0.007721 | 23.9544 | 48.601 | 49.1469 | 48.3154 | 48.5774 | 48.6863 | 48.6106 | 49.2321 | 119.292 | 64.2943 | 56.1348 | 64.0035 | 64.0802 | 127.2829 | 64.058 | 88.0047 | 55.2117 | 55.2339 | -7.9454 | -7.9232
2078.8906 | 120.1401 | -64.4577 | 55.4535 | -3.93 | -2.6047 | -4.6501 | -3.8755 | -3.8642 | -3.9617 | -2.599 | 53.9551 | 0.24405 | 4.0888 | -0.042259 | 0.029923 | 63.5073 | -0.001436 | 16.6156 | 60.5277 | 61.853 | 59.8076 | 60.5822 | 60.5935 | 60.496 | 61.8587 | 118.4128 | 64.7018 | 68.5465 | 64.4154 | 64.4876 | 127.965 | 64.4563 | 81.0733 | 53.9252 | 53.9565 | 4.0588 | 4.0902
2079.8906 | 120.2271 | -64.3021 | 55.632 | -11.2829 | -10.2513 | -11.8706 | -11.2515 | -11.2164 | -11.3283 | -10.2079 | 54.5091 | 0.23948 | -4.4726 | -0.042259 | 0.029923 | 63.5256 | -0.006014 | 21.6516 | 53.0192 | 54.0508 | 52.4315 | 53.0506 | 53.0857 | 52.9737 | 54.0941 | 118.8112 | 64.5415 | 59.8294 | 64.2598 | 64.332 | 127.8276 | 64.296 | 85.9537 | 54.4792 | 54.5151 | -4.5025 | -4.4666
2080.8906 | 119.9249 | -64.3707 | 55.4077 | -9.3646 | -8.0855 | -10.0803 | -9.3102 | -9.2936 | -9.41 | -8.0471 | 53.9917 | 0.24405 | -1.0389 | -0.042259 | 0.034501 | 63.1227 | -0.006014 | 22.7046 | 55.0062 | 56.2852 | 54.2904 | 55.0605 | 55.0771 | 54.9607 | 56.3237 | 118.3625 | 64.6148 | 63.3318 | 64.3285 | 64.4052 | 127.4934 | 64.3647 | 87.0753 | 53.9572 | 53.9978 | -1.0734 | -1.0329
2081.8906 | 119.8013 | -64.8514 | 54.6112 | 4.0547 | 6.0814 | 2.9458 | 4.0315 | 4.0878 | 4.0505 | 6.1544 | 52.5907 | 0.23948 | 16.1663 | -0.03768 | 0.034501 | 63.0678 | 0.003143 | 24.2154 | 68.9061 | 70.9327 | 67.7972 | 68.8829 | 68.9391 | 68.9018 | 71.0058 | 117.4421 | 65.0909 | 81.0176 | 64.8137 | 64.8859 | 127.9191 | 64.8545 | 89.0667 | 52.5562 | 52.5876 | 16.1318 | 16.1631
2082.8906 | 120.4056 | -64.1418 | 55.8746 | -13.3615 | -12.7238 | -13.7158 | -13.3027 | -13.2948 | -13.4115 | -12.6802 | 54.8433 | 0.25321 | -7.0136 | -0.042259 | 0.029923 | 63.8231 | -0.001436 | 20.7543 | 50.7803 | 51.418 | 50.4261 | 50.8392 | 50.8471 | 50.7303 | 51.4617 | 118.9852 | 64.3951 | 57.1283 | 64.0996 | 64.1718 | 127.965 | 64.1404 | 84.8961 | 54.8134 | 54.8448 | -7.0435 | -7.0121
2083.8906 | 120.3186 | -64.5538 | 55.4901 | -11.521 | -11.1396 | -11.8248 | -11.5033 | -11.4407 | -11.5481 | -11.0641 | 54.7792 | 0.2349 | -6.9266 | -0.042259 | 0.029923 | 64.0108 | 0.003143 | 18.4148 | 53.0328 | 53.4143 | 52.729 | 53.0505 | 53.1132 | 53.0057 | 53.4898 | 119.3331 | 64.7887 | 57.6273 | 64.5116 | 64.5838 | 128.5647 | 64.557 | 82.9687 | 54.7493 | 54.7761 | -6.9565 | -6.9297
2084.8906 | 120.1584 | -65.4099 | 54.6249 | -4.603 | -4.2668 | -4.9432 | -4.6127 | -4.528 | -4.5569 | -4.1602 | 54.0375 | 0.2349 | -0.10494 | -0.03768 | 0.034501 | 64.5419 | -0.001436 | 12.4449 | 60.8068 | 61.1431 | 60.4667 | 60.7972 | 60.8819 | 60.8529 | 61.2497 | 119.4474 | 65.6447 | 65.3049 | 65.3722 | 65.4444 | 129.9518 | 65.4084 | 77.8547 | 54.003 | 54.039 | -0.13944 | -0.10351
2085.8906 | 120.0851 | -65.8768 | 54.0848 | -1.2517 | -0.69071 | -1.6649 | -1.2795 | -1.2135 | -1.2055 | -0.59379 | 53.1493 | 0.23948 | 4.1391 | -0.042259 | 0.034501 | 64.9906 | 0.003143 | 10.8196 | 64.6251 | 65.1861 | 64.2119 | 64.5972 | 64.6633 | 64.6712 | 65.283 | 119.0261 | 66.1162 | 70.0159 | 65.8345 | 65.9113 | 130.8673 | 65.8799 | 76.6964 | 53.1148 | 53.1462 | 4.1046 | 4.136
2086.8906 | 120.1401 | -65.799 | 54.1901 | 4.453 | 4.7443 | 4.1179 | 4.4711 | 4.4723 | 4.4259 | 4.8359 | 53.4835 | 0.23948 | 8.2046 | -0.03768 | 0.029923 | 65.1554 | -0.006014 | 2.2951 | 70.252 | 70.5433 | 69.9169 | 70.27 | 70.2713 | 70.2248 | 70.6349 | 119.2825 | 66.0384 | 74.0036 | 65.7613 | 65.8289 | 130.9543 | 65.7929 | 68.094 | 53.4536 | 53.4895 | 8.1747 | 8.2107
2087.8906 | 120.1675 | -65.1443 | 54.744 | -1.4531 | -1.1074 | -1.8618 | -1.4535 | -1.4104 | -1.4711 | -1.0379 | 53.7033 | 0.24405 | 3.2967 | -0.042259 | 0.039079 | 64.5556 | -0.001436 | 10.1512 | 63.6912 | 64.037 | 63.2826 | 63.6908 | 63.734 | 63.6733 | 64.1065 | 118.8476 | 65.3884 | 68.4411 | 65.1021 | 65.1834 | 129.7 | 65.1429 | 75.2956 | 53.6642 | 53.7047 | 3.2576 | 3.2982
2088.8906 | 119.989 | -64.888 | 54.8309 | -7.5332 | -6.7622 | -8.0383 | -7.4971 | -7.4579 | -7.5695 | -6.6965 | 53.772 | 0.24405 | -0.73674 | -0.033101 | 0.029923 | 63.4203 | 0.007721 | 19.715 | 57.3548 | 58.1258 | 56.8497 | 57.3909 | 57.4301 | 57.3185 | 58.1915 | 118.66 | 65.1321 | 64.1513 | 64.8549 | 64.9179 | 128.3083 | 64.8957 | 84.603 | 53.742 | 53.7643 | -0.76667 | -0.74446
2089.8906 | 119.8105 | -64.5218 | 55.1376 | -8.6778 | -8.113 | -9.1692 | -8.6646 | -8.5978 | -8.7141 | -8.0379 | 53.7537 | 0.2349 | -2.4582 | -0.046838 | 0.034501 | 62.3627 | -0.006014 | 17.6365 | 55.844 | 56.4088 | 55.3526 | 55.8572 | 55.924 | 55.8077 | 56.4839 | 118.2754 | 64.7567 | 62.0636 | 64.475 | 64.5563 | 126.8845 | 64.5158 | 82.1583 | 53.7192 | 53.7597 | -2.4927 | -2.4522
2090.8906 | 120.4468 | -25.5798 | 94.6976 | -25.508 | -25.5262 | -25.5514 | -25.5181 | -25.463 | -25.5351 | -25.4487 | -8.1705 | 0.2349 | -8.4008 | -0.046838 | 0.029923 | 25.9534 | -0.006014 | 25.5568 | 0.07187 | 0.053617 | 0.02839 | 0.061756 | 0.11687 | 0.044758 | 0.13115 | 17.4093 | 25.8147 | 17.179 | 25.533 | 25.6098 | 51.5332 | 25.5738 | 51.1366 | -8.2004 | -8.1645 | -8.4307 | -8.3948
2091.8906 | 120.5521 | -25.5066 | 94.9631 | -25.595 | -25.6453 | -25.6064 | -25.6188 | -25.5408 | -25.6083 | -25.554 | -8.7199 | 0.2349 | -8.4832 | -0.03768 | 0.034501 | 25.578 | -0.001436 | 25.3004 | -0.088362 | -0.13867 | -0.099796 | -0.11221 | -0.034198 | -0.10174 | -0.047394 | 16.7867 | 25.7415 | 17.0234 | 25.4689 | 25.5411 | 51.0846 | 25.5052 | 50.807 | -8.7544 | -8.7185 | -8.5177 | -8.4818
2092.8906 | 120.6619 | -25.5203 | 94.9905 | -25.6316 | -25.6727 | -25.6339 | -25.6509 | -25.582 | -25.6404 | -25.5998 | -8.7336 | 0.24405 | -8.4832 | -0.033101 | 0.039079 | 25.6009 | 0.007721 | 25.3324 | -0.11126 | -0.15241 | -0.11353 | -0.13053 | -0.061667 | -0.12005 | -0.079443 | 16.7867 | 25.7644 | 17.0371 | 25.4872 | 25.5594 | 51.1212 | 25.528 | 50.8528 | -8.7727 | -8.7414 | -8.5223 | -8.4909
2093.8906 | 120.6894 | -25.5112 | 95.0592 | -25.6316 | -25.6636 | -25.6339 | -25.6371 | -25.582 | -25.6312 | -25.5815 | -8.7382 | 0.23948 | -8.4786 | -0.046838 | 0.029923 | 25.5963 | 0.003143 | 25.3279 | -0.12041 | -0.15241 | -0.12269 | -0.12595 | -0.070823 | -0.12005 | -0.070286 | 16.7729 | 25.7506 | 17.0326 | 25.4643 | 25.5411 | 51.1075 | 25.5143 | 50.839 | -8.7681 | -8.7414 | -8.5085 | -8.4818
2094.8906 | 120.7031 | -25.4654 | 95.1416 | -25.5446 | -25.5995 | -25.556 | -25.573 | -25.5042 | -25.5534 | -25.5082 | -8.7382 | 0.23948 | -8.4695 | -0.051417 | 0.025345 | 25.5093 | -0.001436 | 25.25 | -0.079198 | -0.13409 | -0.09063 | -0.10763 | -0.038773 | -0.087996 | -0.042811 | 16.7272 | 25.7049 | 16.9959 | 25.414 | 25.4907 | 50.9747 | 25.464 | 50.7154 | -8.7636 | -8.7368 | -8.4948 | -8.468
2095.8906 | 120.8176 | -25.4471 | 95.137 | -25.5675 | -25.5995 | -25.5743 | -25.5913 | -25.5133 | -25.5717 | -25.5219 | -8.7382 | 0.2349 | -8.4695 | -0.042259 | 0.029923 | 25.523 | -0.001436 | 25.2638 | -0.1204 | -0.1524 | -0.12725 | -0.14425 | -0.066239 | -0.12462 | -0.074856 | 16.7089 | 25.682 | 16.9776 | 25.4048 | 25.477 | 50.9701 | 25.4456 | 50.7108 | -8.7681 | -8.7368 | -8.4994 | -8.468
2096.8906 | 120.8679 | -25.3372 | 95.2835 | -25.4805 | -25.5262 | -25.4965 | -25.5089 | -25.4447 | -25.503 | -25.4395 | -8.7382 | 0.23948 | -8.4924 | -0.046838 | 0.039079 | 25.4452 | 0.007721 | 25.1905 | -0.14327 | -0.189 | -0.15928 | -0.1717 | -0.10743 | -0.16581 | -0.10231 | 16.599 | 25.5767 | 16.8449 | 25.2904 | 25.3763 | 50.7824 | 25.3449 | 50.5277 | -8.7773 | -8.7459 | -8.5314 | -8.5001
2097.8906 | 120.8267 | -25.3647 | 95.3064 | -25.4942 | -25.5354 | -25.4965 | -25.5135 | -25.4492 | -25.503 | -25.4487 | -8.7382 | 0.23032 | -8.4832 | -0.046838 | 0.029923 | 25.4498 | -0.001436 | 25.1951 | -0.12954 | -0.17069 | -0.13182 | -0.14881 | -0.084546 | -0.13834 | -0.084003 | 16.6265 | 25.595 | 16.8815 | 25.3178 | 25.3946 | 50.8145 | 25.3632 | 50.5598 | -8.7681 | -8.7368 | -8.5131 | -8.4818
2098.8906 | 120.7901 | -25.3098 | 95.4254 | -25.3889 | -25.4392 | -25.4049 | -25.4174 | -25.3531 | -25.4115 | -25.3571 | -8.7382 | 0.2349 | -8.4878 | -0.046838 | 0.034501 | 25.3628 | -0.006014 | 25.0898 | -0.079173 | -0.12947 | -0.095176 | -0.1076 | -0.043341 | -0.10171 | -0.047371 | 16.5715 | 25.5447 | 16.822 | 25.2629 | 25.3443 | 50.6726 | 25.3037 | 50.3995 | -8.7727 | -8.7322 | -8.5223 | -8.4818
2099.8906 | 120.8359 | -25.2914 | 95.4254 | -25.4027 | -25.4438 | -25.4004 | -25.4265 | -25.3485 | -25.4115 | -25.3525 | -8.7382 | 0.24405 | -8.4878 | -0.042259 | 0.029923 | 25.3582 | 0.007721 | 25.0944 | -0.11122 | -0.15236 | -0.10891 | -0.13506 | -0.057073 | -0.12002 | -0.061103 | 16.5532 | 25.5355 | 16.8037 | 25.2492 | 25.3214 | 50.6497 | 25.2992 | 50.3858 | -8.7681 | -8.7459 | -8.5177 | -8.4955
2100.9062 | 120.9686 | -25.209 | 95.4987 | -25.3294 | -25.366 | -25.3317 | -25.3441 | -25.2798 | -25.3382 | -25.2793 | -8.7474 | 0.24405 | -8.4924 | -0.03768 | 0.034501 | 25.2941 | 0.003143 | 25.0211 | -0.12036 | -0.15691 | -0.12263 | -0.13505 | -0.070801 | -0.12916 | -0.07025 | 16.4617 | 25.4531 | 16.7167 | 25.1714 | 25.2435 | 50.5032 | 25.2122 | 50.2302 | -8.7819 | -8.7505 | -8.5269 | -8.4955
2101.8906 | 121.0144 | -25.1083 | 95.6177 | -25.2104 | -25.2698 | -25.2218 | -25.2342 | -25.17 | -25.2329 | -25.174 | -8.7382 | 0.24405 | -8.4878 | -0.046838 | 0.020767 | 25.1797 | 0.003143 | 24.9158 | -0.10203 | -0.16147 | -0.11345 | -0.12587 | -0.061638 | -0.12457 | -0.06566 | 16.3701 | 25.3524 | 16.6206 | 25.0615 | 25.1291 | 50.288 | 25.1115 | 50.0242 | -8.759 | -8.7414 | -8.5085 | -8.4909
2102.8906 | 120.8771 | -24.9985 | 95.7596 | -25.128 | -25.1736 | -25.1348 | -25.1426 | -25.083 | -25.1368 | -25.0824 | -8.7428 | 0.2349 | -8.4878 | -0.042259 | 0.029923 | 25.0881 | -0.001436 | 24.8334 | -0.12948 | -0.17517 | -0.13632 | -0.14417 | -0.08452 | -0.13828 | -0.08396 | 16.2557 | 25.2334 | 16.5107 | 24.9562 | 25.0284 | 50.0866 | 24.997 | 49.8319 | -8.7727 | -8.7414 | -8.5177 | -8.4863
2103.8906 | 120.9274 | -25.1221 | 95.6635 | -25.1921 | -25.2332 | -25.2035 | -25.2067 | -25.1334 | -25.2009 | -25.142 | -8.7474 | 0.2349 | -8.4924 | -0.033101 | 0.034501 | 25.1522 | 0.003143 | 24.8884 | -0.069985 | -0.1111 | -0.081401 | -0.08467 | -0.011282 | -0.078783 | -0.01988 | 16.3747 | 25.357 | 16.6297 | 25.089 | 25.1566 | 50.2743 | 25.1252 | 50.0104 | -8.7819 | -8.7505 | -8.5269 | -8.4955
2104.8906 | 120.9274 | -25.0076 | 95.8008 | -25.16 | -25.2057 | -25.1714 | -25.1838 | -25.1105 | -25.1688 | -25.1191 | -8.752 | 0.23948 | -8.4878 | -0.03768 | 0.034501 | 25.1202 | 0.003143 | 24.8563 | -0.15238 | -0.19807 | -0.16379 | -0.17622 | -0.10283 | -0.16118 | -0.11143 | 16.2557 | 25.2471 | 16.5199 | 24.9699 | 25.0421 | 50.1278 | 25.0108 | 49.8639 | -8.7865 | -8.7551 | -8.5223 | -8.4909
2105.8906 | 121.0785 | -25.0076 | 95.7687 | -25.1142 | -25.1553 | -25.1165 | -25.1335 | -25.0647 | -25.1184 | -25.0733 | -8.7474 | 0.24405 | -8.4878 | -0.046838 | 0.025345 | 25.0836 | -0.001436 | 24.8105 | -0.10659 | -0.1477 | -0.10885 | -0.12586 | -0.057053 | -0.11081 | -0.065649 | 16.2602 | 25.2517 | 16.5199 | 24.9608 | 25.033 | 50.0912 | 25.0062 | 49.8182 | -8.7727 | -8.7459 | -8.5131 | -8.4863
2106.8906 | 120.9961 | -24.9893 | 95.8374 | -25.0822 | -25.1141 | -25.0798 | -25.0877 | -25.0326 | -25.0818 | -25.0275 | -8.7474 | 0.23032 | -8.4878 | -0.042259 | 0.029923 | 25.0423 | -0.001436 | 24.7739 | -0.092855 | -0.12481 | -0.090529 | -0.098381 | -0.043318 | -0.092496 | -0.038177 | 16.2419 | 25.2196 | 16.5015 | 24.9471 | 25.0192 | 50.0317 | 24.9879 | 49.7632 | -8.7773 | -8.7459 | -8.5177 | -8.4863
2107.8906 | 120.9503 | -24.9481 | 95.9473 | -25.0089 | -25.0546 | -25.0112 | -25.0282 | -24.964 | -25.0223 | -24.9634 | -8.7474 | 0.2349 | -8.4878 | -0.042259 | 0.039079 | 24.9783 | -0.001436 | 24.7052 | -0.0608 | -0.10648 | -0.063049 | -0.080059 | -0.015847 | -0.074176 | -0.015281 | 16.2007 | 25.183 | 16.4603 | 24.9059 | 24.9872 | 49.9264 | 24.9467 | 49.6533 | -8.7865 | -8.7459 | -8.5269 | -8.4863
2108.8906 | 120.9824 | -24.8566 | 96.0388 | -24.9448 | -24.9905 | -24.9516 | -24.9687 | -24.8999 | -24.9536 | -24.8947 | -8.7474 | 0.25321 | -8.4969 | -0.042259 | 0.029923 | 24.9187 | 0.007721 | 24.6503 | -0.088255 | -0.13393 | -0.095081 | -0.11209 | -0.043309 | -0.097053 | -0.038162 | 16.1092 | 25.1098 | 16.3596 | 24.8143 | 24.8865 | 49.7753 | 24.8643 | 49.5069 | -8.7773 | -8.7551 | -8.5269 | -8.5047
2109.8906 | 120.9778 | -24.8978 | 96.0434 | -24.954 | -24.9951 | -24.9608 | -24.9732 | -24.909 | -24.9628 | -24.9085 | -8.752 | 0.24863 | -8.4878 | -0.033101 | 0.029923 | 24.9325 | 0.003143 | 24.6549 | -0.056213 | -0.097308 | -0.063039 | -0.075471 | -0.011266 | -0.065011 | -0.010697 | 16.1458 | 25.1464 | 16.41 | 24.8647 | 24.9277 | 49.8302 | 24.9009 | 49.5526 | -8.7819 | -8.7551 | -8.5177 | -8.4909
2110.8906 | 120.9915 | -24.8016 | 96.1441 | -24.9082 | -24.9539 | -24.9059 | -24.9275 | -24.8587 | -24.917 | -24.8581 | -8.752 | 0.23948 | -8.4924 | -0.033101 | 0.034501 | 24.8684 | 0.003143 | 24.6137 | -0.10656 | -0.15223 | -0.10423 | -0.12582 | -0.057038 | -0.11536 | -0.056467 | 16.0497 | 25.0411 | 16.3093 | 24.7685 | 24.8361 | 49.67 | 24.8048 | 49.4153 | -8.7865 | -8.7551 | -8.5269 | -8.4955
2111.8906 | 121.1243 | -24.7467 | 96.1395 | -24.8349 | -24.8806 | -24.8326 | -24.8542 | -24.7854 | -24.8529 | -24.794 | -8.7565 | 0.23948 | -8.4878 | -0.046838 | 0.029923 | 24.8226 | 0.003143 | 24.5313 | -0.088237 | -0.1339 | -0.0859 | -0.10749 | -0.038723 | -0.10619 | -0.047305 | 15.9902 | 24.9862 | 16.2589 | 24.6999 | 24.7766 | 49.5693 | 24.7498 | 49.278 | -8.7865 | -8.7597 | -8.5177 | -8.4909
2112.8906 | 121.0648 | -24.6918 | 96.2036 | -24.8029 | -24.844 | -24.8143 | -24.8221 | -24.7534 | -24.8163 | -24.7574 | -8.752 | 0.2349 | -8.4878 | -0.042259 | 0.034501 | 24.7768 | -0.001436 | 24.4946 | -0.11112 | -0.1522 | -0.12252 | -0.13038 | -0.061609 | -0.1245 | -0.065612 | 15.9398 | 24.9267 | 16.204 | 24.6495 | 24.7263 | 49.4686 | 24.6903 | 49.1864 | -8.7865 | -8.7505 | -8.5223 | -8.4863
2113.8906 | 121.0373 | -24.6963 | 96.2814 | -24.7296 | -24.7753 | -24.741 | -24.7443 | -24.671 | -24.743 | -24.6841 | -8.7565 | 0.2349 | -8.4969 | -0.046838 | 0.034501 | 24.7127 | -0.006014 | 24.426 | -0.033288 | -0.078941 | -0.044682 | -0.047962 | 0.025372 | -0.046664 | 0.012217 | 15.9398 | 24.9312 | 16.1994 | 24.6495 | 24.7309 | 49.4091 | 24.6903 | 49.1223 | -8.791 | -8.7505 | -8.5314 | -8.4909
2114.8906 | 121.17 | -24.6552 | 96.2677 | -24.7251 | -24.7707 | -24.7319 | -24.7443 | -24.6801 | -24.7384 | -24.6796 | -8.7611 | 0.24405 | -8.4924 | -0.042259 | 0.034501 | 24.7173 | -0.001436 | 24.4122 | -0.069909 | -0.11556 | -0.076724 | -0.089161 | -0.024983 | -0.083285 | -0.024404 | 15.894 | 24.8992 | 16.1628 | 24.6129 | 24.6897 | 49.3725 | 24.6537 | 49.0674 | -8.7956 | -8.7597 | -8.5269 | -8.4909
2115.8906 | 121.1426 | -24.6368 | 96.2997 | -24.7205 | -24.7661 | -24.7319 | -24.7397 | -24.6756 | -24.7384 | -24.675 | -8.7565 | 0.23948 | -8.4924 | -0.042259 | 0.034501 | 24.7036 | -0.001436 | 24.4214 | -0.08364 | -0.12929 | -0.095034 | -0.10289 | -0.038715 | -0.10159 | -0.038136 | 15.8803 | 24.8763 | 16.1445 | 24.5946 | 24.6713 | 49.3404 | 24.6354 | 49.0582 | -8.791 | -8.7551 | -8.5269 | -8.4909
2116.8906 | 121.1609 | -24.6414 | 96.3043 | -24.7251 | -24.7707 | -24.7273 | -24.7352 | -24.671 | -24.7293 | -24.675 | -8.752 | 0.24405 | -8.5015 | -0.042259 | 0.039079 | 24.7036 | 0.003143 | 24.4214 | -0.083642 | -0.12929 | -0.085878 | -0.093737 | -0.02956 | -0.087861 | -0.033559 | 15.8895 | 24.8855 | 16.1399 | 24.5992 | 24.6805 | 49.345 | 24.6446 | 49.0628 | -8.791 | -8.7551 | -8.5406 | -8.5047
2117.8906 | 121.1655 | -24.5499 | 96.4142 | -24.6426 | -24.6837 | -24.6403 | -24.6527 | -24.5886 | -24.6423 | -24.588 | -8.7565 | 0.24405 | -8.4878 | -0.042259 | 0.034501 | 24.6257 | -0.001436 | 24.3344 | -0.092783 | -0.13385 | -0.090437 | -0.10288 | -0.038709 | -0.092424 | -0.038125 | 15.7933 | 24.7939 | 16.0621 | 24.5076 | 24.5844 | 49.1756 | 24.5484 | 48.8843 | -8.791 | -8.7551 | -8.5223 | -8.4863
2118.8906 | 121.2387 | -24.4583 | 96.492 | -24.5557 | -24.6013 | -24.5716 | -24.5703 | -24.5153 | -24.5782 | -24.5102 | -8.7565 | 0.24405 | -8.4969 | -0.042259 | 0.029923 | 24.5479 | 0.003143 | 24.2611 | -0.097347 | -0.14298 | -0.11331 | -0.11202 | -0.057014 | -0.11988 | -0.051849 | 15.7018 | 24.7024 | 15.9614 | 24.4161 | 24.4882 | 49.0062 | 24.4615 | 48.7195 | -8.7865 | -8.7597 | -8.5269 | -8.5001
2119.8906 | 121.1746 | -24.4675 | 96.5332 | -24.519 | -24.5601 | -24.5213 | -24.5383 | -24.465 | -24.5324 | -24.4781 | -8.7565 | 0.24405 | -8.4878 | -0.03768 | 0.039079 | 24.5067 | -0.010593 | 24.2245 | -0.051564 | -0.092619 | -0.053791 | -0.070812 | 0.002498 | -0.064941 | -0.010647 | 15.7109 | 24.7115 | 15.9797 | 24.4298 | 24.5065 | 48.9742 | 24.4569 | 48.692 | -8.7956 | -8.7459 | -8.5269 | -8.4772
2120.8906 | 121.1288 | -24.5087 | 96.5881 | -24.5511 | -24.583 | -24.5487 | -24.5566 | -24.5016 | -24.5553 | -24.4964 | -8.752 | 0.23948 | -8.4969 | -0.03768 | 0.039079 | 24.5388 | 0.003143 | 24.2428 | -0.042414 | -0.074314 | -0.040063 | -0.047927 | 0.007074 | -0.046634 | 0.012239 | 15.7567 | 24.7481 | 16.0117 | 24.471 | 24.5477 | 49.0474 | 24.5118 | 48.7515 | -8.791 | -8.7551 | -8.536 | -8.5001
2121.8906 | 121.2433 | -24.3988 | 96.6156 | -24.4778 | -24.5189 | -24.4846 | -24.4971 | -24.4329 | -24.4912 | -24.4323 | -8.7565 | 0.24405 | -8.4878 | -0.042259 | 0.029923 | 24.4701 | -0.006014 | 24.1787 | -0.079023 | -0.12007 | -0.085826 | -0.09827 | -0.03412 | -0.092399 | -0.033529 | 15.6423 | 24.6429 | 15.911 | 24.3565 | 24.4287 | 48.8689 | 24.3928 | 48.5775 | -8.7865 | -8.7505 | -8.5177 | -8.4818
2122.8906 | 121.2524 | -24.3759 | 96.611 | -24.4549 | -24.5097 | -24.4663 | -24.4788 | -24.4055 | -24.4729 | -24.414 | -8.752 | 0.23948 | -8.4878 | -0.03768 | 0.029923 | 24.4518 | 0.003143 | 24.1604 | -0.079019 | -0.1338 | -0.0904 | -0.10284 | -0.02954 | -0.096974 | -0.038105 | 15.624 | 24.6154 | 15.8881 | 24.3382 | 24.4058 | 48.8277 | 24.3791 | 48.5363 | -8.7819 | -8.7551 | -8.5177 | -8.4909
2123.8906 | 121.1746 | -24.3668 | 96.698 | -24.4137 | -24.4548 | -24.4205 | -24.4284 | -24.3688 | -24.4271 | -24.3774 | -8.752 | 0.24405 | -8.4924 | -0.046838 | 0.029923 | 24.3968 | -0.001436 | 24.1101 | -0.046969 | -0.088014 | -0.05377 | -0.061636 | -0.002073 | -0.060346 | -0.010635 | 15.6148 | 24.6108 | 15.8744 | 24.3199 | 24.3967 | 48.7636 | 24.3653 | 48.4768 | -8.7819 | -8.7505 | -8.5223 | -8.4909
2124.8906 | 121.2662 | -24.3301 | 96.7072 | -24.4046 | -24.4456 | -24.4114 | -24.4192 | -24.3551 | -24.4179 | -24.3591 | -8.7474 | 0.2349 | -8.4969 | -0.042259 | 0.025345 | 24.3923 | -0.006014 | 24.1055 | -0.074434 | -0.11548 | -0.081233 | -0.0891 | -0.02496 | -0.08781 | -0.028944 | 15.5828 | 24.565 | 15.8332 | 24.2879 | 24.3555 | 48.7224 | 24.3241 | 48.4356 | -8.7727 | -8.7414 | -8.5223 | -8.4909
2125.8906 | 121.2753 | -24.2889 | 96.698 | -24.4046 | -24.4502 | -24.416 | -24.4238 | -24.3643 | -24.4179 | -24.3637 | -8.7565 | 0.23948 | -8.5015 | -0.046838 | 0.034501 | 24.4014 | 0.003143 | 24.1055 | -0.11563 | -0.16126 | -0.12701 | -0.13488 | -0.075315 | -0.12901 | -0.074721 | 15.5324 | 24.5284 | 15.7874 | 24.2421 | 24.3234 | 48.6904 | 24.2921 | 48.3944 | -8.791 | -8.7597 | -8.536 | -8.5047
2126.8906 | 121.2616 | -24.2523 | 96.8124 | -24.3176 | -24.3586 | -24.3198 | -24.3277 | -24.2635 | -24.3264 | -24.2675 | -8.752 | 0.24863 | -8.4878 | -0.042259 | 0.029923 | 24.3007 | -0.001436 | 24.0139 | -0.065264 | -0.1063 | -0.067481 | -0.07535 | -0.011221 | -0.074062 | -0.0152 | 15.5004 | 24.501 | 15.7645 | 24.2101 | 24.2822 | 48.553 | 24.2509 | 48.2662 | -8.7819 | -8.7505 | -8.5177 | -8.4863
2127.8906 | 121.2891 | -24.2752 | 96.7896 | -24.3405 | -24.3769 | -24.3473 | -24.3506 | -24.2864 | -24.3539 | -24.295 | -8.7565 | 0.2349 | -8.4924 | -0.03768 | 0.029923 | 24.3282 | 0.007721 | 24.046 | -0.065267 | -0.10173 | -0.072064 | -0.075354 | -0.011221 | -0.078644 | -0.01978 | 15.5187 | 24.5101 | 15.7829 | 24.2375 | 24.3051 | 48.6034 | 24.2829 | 48.3212 | -8.7865 | -8.7643 | -8.5223 | -8.5001
2128.8906 | 121.2616 | -24.2386 | 96.8216 | -24.3222 | -24.3586 | -24.3198 | -24.346 | -24.2773 | -24.331 | -24.2767 | -8.752 | 0.25321 | -8.4924 | -0.042259 | 0.029923 | 24.3236 | -0.001436 | 24.0185 | -0.083576 | -0.12003 | -0.081214 | -0.1074 | -0.038687 | -0.092374 | -0.038089 | 15.4866 | 24.4918 | 15.7462 | 24.1963 | 24.2685 | 48.5622 | 24.2371 | 48.2571 | -8.7819 | -8.7505 | -8.5223 | -8.4909
2129.8906 | 121.3257 | -24.1379 | 96.8903 | -24.2306 | -24.2808 | -24.2374 | -24.2544 | -24.1857 | -24.244 | -24.1805 | -8.7611 | 0.23948 | -8.4924 | -0.042259 | 0.029923 | 24.2229 | 0.003143 | 23.9315 | -0.092716 | -0.1429 | -0.099508 | -0.11653 | -0.047836 | -0.10609 | -0.042656 | 15.3768 | 24.3774 | 15.6455 | 24.0956 | 24.1678 | 48.3608 | 24.141 | 48.0694 | -8.791 | -8.7643 | -8.5223 | -8.4955
2130.8906 | 121.3394 | -24.1241 | 96.9543 | -24.1894 | -24.2258 | -24.2008 | -24.204 | -24.1445 | -24.2028 | -24.1439 | -8.7565 | 0.24405 | -8.4969 | -0.046838 | 0.034501 | 24.1908 | 0.007721 | 23.8949 | -0.065242 | -0.10169 | -0.076611 | -0.079904 | -0.020367 | -0.078619 | -0.019762 | 15.3676 | 24.3682 | 15.6272 | 24.0773 | 24.1586 | 48.315 | 24.1319 | 48.019 | -8.791 | -8.7643 | -8.5314 | -8.5047
2131.8906 | 121.3074 | -24.0784 | 97.0184 | -24.139 | -24.1755 | -24.1367 | -24.1537 | -24.0758 | -24.1478 | -24.0752 | -8.752 | 0.24863 | -8.4924 | -0.046838 | 0.029923 | 24.1405 | -0.001436 | 23.8354 | -0.060657 | -0.097097 | -0.058287 | -0.075318 | 0.002526 | -0.069455 | 0.003133 | 15.3264 | 24.327 | 15.586 | 24.0315 | 24.1083 | 48.2188 | 24.0769 | 47.9137 | -8.7819 | -8.7505 | -8.5223 | -8.4909
2132.8906 | 121.2845 | -24.0417 | 97.0688 | -24.1207 | -24.1526 | -24.1183 | -24.1262 | -24.0621 | -24.1249 | -24.0661 | -8.7565 | 0.24405 | -8.4924 | -0.042259 | 0.025345 | 24.1222 | 0.007721 | 23.8079 | -0.078965 | -0.11082 | -0.076594 | -0.084468 | -0.020361 | -0.083184 | -0.024332 | 15.2852 | 24.2858 | 15.5494 | 23.9995 | 24.0671 | 48.1639 | 24.0495 | 47.8497 | -8.7819 | -8.7643 | -8.5177 | -8.5001
2133.8906 | 121.3394 | -24.0738 | 97.0413 | -24.1299 | -24.1709 | -24.1458 | -24.1537 | -24.0804 | -24.1432 | -24.0752 | -8.7565 | 0.23948 | -8.5015 | -0.03768 | 0.034501 | 24.1405 | 0.007721 | 23.8354 | -0.056077 | -0.097095 | -0.072021 | -0.079895 | -0.006629 | -0.069454 | -0.001444 | 15.3173 | 24.3133 | 15.5723 | 24.0361 | 24.1083 | 48.2143 | 24.0815 | 47.9092 | -8.791 | -8.7643 | -8.536 | -8.5092
2134.8906 | 121.3943 | -23.9822 | 97.1191 | -24.0566 | -24.0976 | -24.068 | -24.0667 | -24.0072 | -24.0746 | -24.0066 | -8.7657 | 0.2349 | -8.5015 | -0.033101 | 0.029923 | 24.0626 | 0.003143 | 23.7575 | -0.074376 | -0.11539 | -0.085738 | -0.084456 | -0.024935 | -0.092331 | -0.024324 | 15.2165 | 24.2171 | 15.4807 | 23.9491 | 24.0122 | 48.0449 | 23.9854 | 47.7398 | -8.7956 | -8.7688 | -8.5314 | -8.5047
2135.8906 | 121.2708 | -24.0509 | 97.1603 | -24.0932 | -24.1297 | -24.1 | -24.1033 | -24.0392 | -24.1066 | -24.0432 | -8.752 | 0.23948 | -8.4969 | -0.033101 | 0.034501 | 24.0993 | 0.007721 | 23.7942 | -0.042339 | -0.078775 | -0.049124 | -0.05242 | 0.011683 | -0.055716 | 0.007714 | 15.2989 | 24.2904 | 15.554 | 24.0178 | 24.0854 | 48.1502 | 24.0586 | 47.8451 | -8.7865 | -8.7597 | -8.5314 | -8.5047
2136.8906 | 121.4355 | -24.0829 | 97.0871 | -24.0887 | -24.1343 | -24.1046 | -24.1079 | -24.0392 | -24.1066 | -24.0523 | -8.7611 | 0.24405 | -8.5061 | -0.03768 | 0.034501 | 24.113 | 0.003143 | 23.7942 | -0.005717 | -0.05131 | -0.021659 | -0.024955 | 0.043727 | -0.023672 | 0.030602 | 15.3218 | 24.327 | 15.5769 | 24.0453 | 24.1174 | 48.1959 | 24.0861 | 47.8771 | -8.7956 | -8.7643 | -8.5406 | -8.5092
2137.8906 | 121.3715 | -23.9777 | 97.1787 | -24.02 | -24.0564 | -24.0222 | -24.0346 | -23.9614 | -24.0242 | -23.9654 | -8.7565 | 0.23948 | -8.4924 | -0.042259 | 0.039079 | 24.0352 | -0.001436 | 23.7072 | -0.042327 | -0.078756 | -0.04453 | -0.056985 | 0.016267 | -0.046547 | 0.012301 | 15.2211 | 24.2171 | 15.4853 | 23.9354 | 24.0167 | 48.0128 | 23.9762 | 47.6848 | -8.7956 | -8.7551 | -8.5314 | -8.4909
2138.8906 | 121.2296 | -23.9456 | 97.3389 | -23.965 | -24.0152 | -23.981 | -23.9889 | -23.9202 | -23.9876 | -23.9196 | -8.7611 | 0.24405 | -8.5015 | -0.033101 | 0.034501 | 23.9894 | 0.007721 | 23.6797 | -0.019429 | -0.06959 | -0.035366 | -0.043243 | 0.025425 | -0.041962 | 0.02604 | 15.1845 | 24.1897 | 15.4441 | 23.9125 | 23.9801 | 47.935 | 23.9533 | 47.6253 | -8.7956 | -8.7688 | -8.536 | -8.5092
2139.8906 | 121.376 | -23.8632 | 97.261 | -23.9467 | -23.9877 | -23.9444 | -23.9568 | -23.8881 | -23.9555 | -23.8967 | -8.7611 | 0.2349 | -8.4969 | -0.03768 | 0.029923 | 23.9665 | 0.007721 | 23.6431 | -0.083514 | -0.12452 | -0.081135 | -0.093591 | -0.024927 | -0.092312 | -0.033467 | 15.1021 | 24.0981 | 15.3663 | 23.8255 | 23.8931 | 47.8297 | 23.8709 | 47.5063 | -8.791 | -8.7688 | -8.5269 | -8.5047
2140.8906 | 121.344 | -23.8907 | 97.3343 | -23.9193 | -23.9511 | -23.926 | -23.9248 | -23.8698 | -23.9235 | -23.8601 | -8.7611 | 0.2349 | -8.5061 | -0.03768 | 0.034501 | 23.9345 | 0.003143 | 23.6156 | -0.028578 | -0.060418 | -0.035355 | -0.034076 | 0.020851 | -0.032797 | 0.030624 | 15.1296 | 24.1256 | 15.3846 | 23.853 | 23.9252 | 47.8251 | 23.8938 | 47.5063 | -8.7956 | -8.7643 | -8.5406 | -8.5092
2141.8906 | 121.3394 | -23.8907 | 97.3434 | -23.9055 | -23.9511 | -23.9077 | -23.9202 | -23.8653 | -23.9281 | -23.8601 | -8.7657 | 0.23948 | -8.5061 | -0.033101 | 0.029923 | 23.9253 | 0.007721 | 23.611 | -0.014842 | -0.060418 | -0.01704 | -0.029497 | 0.025429 | -0.037375 | 0.030624 | 15.125 | 24.1302 | 15.3846 | 23.8576 | 23.9206 | 47.816 | 23.8984 | 47.5017 | -8.7956 | -8.7734 | -8.536 | -8.5138
2142.8906 | 121.3348 | -23.8129 | 97.3938 | -23.8506 | -23.8962 | -23.8574 | -23.8698 | -23.8012 | -23.8685 | -23.8005 | -8.7611 | 0.2349 | -8.4969 | -0.042259 | 0.029923 | 23.8749 | 0.003143 | 23.5515 | -0.037722 | -0.083292 | -0.044496 | -0.056954 | 0.0117 | -0.055676 | 0.012321 | 15.0518 | 24.0478 | 15.3159 | 23.7706 | 23.8428 | 47.6878 | 23.816 | 47.3644 | -8.791 | -8.7643 | -8.5269 | -8.5001
2143.8906 | 121.3165 | -23.7625 | 97.4899 | -23.7728 | -23.8137 | -23.7795 | -23.792 | -23.7233 | -23.7907 | -23.7273 | -8.7657 | 0.24405 | -8.4969 | -0.042259 | 0.034501 | 23.7925 | 0.007721 | 23.4874 | -0.010243 | -0.051228 | -0.017013 | -0.029473 | 0.039172 | -0.028198 | 0.035217 | 14.9968 | 24.0066 | 15.2656 | 23.7203 | 23.797 | 47.5551 | 23.7702 | 47.2499 | -8.8002 | -8.7734 | -8.5314 | -8.5047
2144.8906 | 121.3211 | -23.7717 | 97.5128 | -23.7773 | -23.8275 | -23.7978 | -23.8011 | -23.7325 | -23.7953 | -23.7365 | -8.7657 | 0.24405 | -8.5015 | -0.03768 | 0.039079 | 23.8017 | 0.007721 | 23.492 | -0.005667 | -0.055809 | -0.026173 | -0.029475 | 0.039171 | -0.023621 | 0.035216 | 15.006 | 24.0157 | 15.2702 | 23.734 | 23.8107 | 47.5734 | 23.7794 | 47.2637 | -8.8048 | -8.7734 | -8.5406 | -8.5092
2145.8906 | 121.3806 | -23.7717 | 97.4854 | -23.8094 | -23.8412 | -23.807 | -23.8195 | -23.7554 | -23.8182 | -23.7731 | -8.7657 | 0.24405 | -8.5015 | -0.042259 | 0.034501 | 23.8337 | -0.001436 | 23.5057 | -0.037715 | -0.069545 | -0.03533 | -0.047789 | 0.016281 | -0.046513 | -0.001409 | 15.006 | 24.0157 | 15.2702 | 23.7294 | 23.8062 | 47.6054 | 23.7702 | 47.2774 | -8.8002 | -8.7643 | -8.536 | -8.5001
2146.8906 | 121.3531 | -23.7259 | 97.5311 | -23.7636 | -23.8092 | -23.7658 | -23.7737 | -23.7096 | -23.7724 | -23.7136 | -8.7657 | 0.23948 | -8.5015 | -0.042259 | 0.029923 | 23.7834 | 0.003143 | 23.46 | -0.037707 | -0.08327 | -0.039898 | -0.04778 | 0.016284 | -0.046505 | 0.012331 | 14.9602 | 23.9654 | 15.2244 | 23.6836 | 23.7558 | 47.5093 | 23.729 | 47.1859 | -8.7956 | -8.7688 | -8.5314 | -8.5047
2147.8906 | 121.3852 | -23.671 | 97.6089 | -23.7087 | -23.7451 | -23.7063 | -23.7187 | -23.6638 | -23.7175 | -23.654 | -8.7611 | 0.24863 | -8.5015 | -0.046838 | 0.039079 | 23.7239 | 0.007721 | 23.4004 | -0.037699 | -0.074098 | -0.035309 | -0.04777 | 0.007132 | -0.046497 | 0.016915 | 14.9098 | 23.9196 | 15.1695 | 23.6241 | 23.71 | 47.3948 | 23.6787 | 47.0714 | -8.8002 | -8.7688 | -8.5406 | -8.5092
2148.8906 | 121.4035 | -23.616 | 97.673 | -23.6583 | -23.7038 | -23.6605 | -23.6729 | -23.6089 | -23.6762 | -23.6083 | -8.7565 | 0.24863 | -8.5015 | -0.046838 | 0.029923 | 23.6918 | 0.003143 | 23.3638 | -0.042268 | -0.08782 | -0.044454 | -0.056917 | 0.007137 | -0.060222 | 0.007766 | 14.8595 | 23.8647 | 15.1145 | 23.5692 | 23.646 | 47.3078 | 23.6192 | 46.9799 | -8.7865 | -8.7597 | -8.5314 | -8.5047
2149.8906 | 121.3852 | -23.6069 | 97.6639 | -23.6308 | -23.6764 | -23.633 | -23.6592 | -23.5814 | -23.6488 | -23.59 | -8.7611 | 0.23948 | -8.5061 | -0.03768 | 0.039079 | 23.6598 | -0.001436 | 23.3364 | -0.023952 | -0.069502 | -0.026137 | -0.052336 | 0.025449 | -0.041907 | 0.016923 | 14.8458 | 23.8463 | 15.1008 | 23.5692 | 23.646 | 47.2666 | 23.6054 | 46.9432 | -8.8002 | -8.7597 | -8.5452 | -8.5046
2150.8906 | 121.376 | -23.6801 | 97.641 | -23.672 | -23.7038 | -23.6651 | -23.6729 | -23.6135 | -23.6762 | -23.6037 | -8.7611 | 0.24405 | -8.4969 | -0.033101 | 0.039079 | 23.6918 | 0.003143 | 23.3638 | 0.008084 | -0.023733 | 0.015055 | 0.00717 | 0.066646 | 0.003865 | 0.076431 | 14.919 | 23.9242 | 15.1832 | 23.647 | 23.7192 | 47.3719 | 23.6833 | 47.0439 | -8.8002 | -8.7643 | -8.536 | -8.5001
2151.8906 | 121.3852 | -23.6115 | 97.673 | -23.6354 | -23.6718 | -23.6376 | -23.6546 | -23.5768 | -23.6488 | -23.5854 | -8.7703 | 0.24405 | -8.4969 | -0.042259 | 0.029923 | 23.6506 | 0.003143 | 23.3318 | -0.023954 | -0.060346 | -0.026139 | -0.043181 | 0.034604 | -0.03733 | 0.026079 | 14.8412 | 23.8555 | 15.1145 | 23.5692 | 23.6414 | 47.2621 | 23.6146 | 46.9432 | -8.8002 | -8.7734 | -8.5269 | -8.5001
2152.8906 | 121.3943 | -23.6206 | 97.7005 | -23.6354 | -23.681 | -23.6422 | -23.6546 | -23.586 | -23.6534 | -23.59 | -8.7657 | 0.23948 | -8.4924 | -0.042259 | 0.025345 | 23.6689 | -0.001436 | 23.3455 | -0.014799 | -0.060349 | -0.021562 | -0.034026 | 0.034603 | -0.032753 | 0.030655 | 14.8549 | 23.8601 | 15.1283 | 23.5783 | 23.646 | 47.2895 | 23.6192 | 46.9661 | -8.791 | -8.7643 | -8.5177 | -8.4909
2153.8906 | 121.431 | -23.5703 | 97.7554 | -23.5805 | -23.6214 | -23.5964 | -23.6043 | -23.5402 | -23.6076 | -23.5442 | -8.7657 | 0.24405 | -8.4969 | -0.046838 | 0.039079 | 23.6186 | 0.007721 | 23.2952 | -0.010212 | -0.051178 | -0.02613 | -0.034016 | 0.030029 | -0.037323 | 0.026083 | 14.8046 | 23.8143 | 15.0733 | 23.5234 | 23.6093 | 47.1888 | 23.578 | 46.8654 | -8.8048 | -8.7734 | -8.536 | -8.5047
2154.8906 | 121.3806 | -23.5245 | 97.8149 | -23.5347 | -23.5665 | -23.5414 | -23.5447 | -23.4807 | -23.5435 | -23.4801 | -8.7703 | 0.24405 | -8.4969 | -0.042259 | 0.034501 | 23.5591 | 0.003143 | 23.2311 | -0.010204 | -0.042008 | -0.016963 | -0.020272 | 0.043766 | -0.019002 | 0.044402 | 14.7542 | 23.7685 | 15.0275 | 23.4822 | 23.559 | 47.0835 | 23.5276 | 46.7555 | -8.8048 | -8.7734 | -8.5314 | -8.5001
2155.8906 | 121.4081 | -23.4924 | 97.847 | -23.4981 | -23.5299 | -23.4957 | -23.5173 | -23.4487 | -23.5069 | -23.4389 | -8.7657 | 0.24405 | -8.4924 | -0.042259 | 0.029923 | 23.5179 | 0.003143 | 23.1899 | -0.00562 | -0.037421 | -0.00322 | -0.024844 | 0.043769 | -0.014418 | 0.053562 | 14.7267 | 23.7365 | 15.0001 | 23.4502 | 23.5224 | 47.0103 | 23.4956 | 46.6823 | -8.7956 | -8.7688 | -8.5223 | -8.4955
2156.8906 | 121.4493 | -23.465 | 97.8973 | -23.4706 | -23.5115 | -23.4682 | -23.4852 | -23.4212 | -23.4748 | -23.4251 | -8.7657 | 0.23948 | -8.5061 | -0.046838 | 0.034501 | 23.4904 | -0.001436 | 23.1715 | -0.005616 | -0.046572 | -0.003214 | -0.02026 | 0.043771 | -0.009835 | 0.039831 | 14.6993 | 23.7044 | 14.9589 | 23.4181 | 23.4995 | 46.9554 | 23.4635 | 46.6365 | -8.8002 | -8.7643 | -8.5406 | -8.5046
2157.8906 | 121.4172 | -23.4467 | 97.8973 | -23.466 | -23.507 | -23.4682 | -23.4806 | -23.4166 | -23.4794 | -23.416 | -8.7703 | 0.23948 | -8.5015 | -0.033101 | 0.025345 | 23.4812 | -0.001436 | 23.1624 | -0.019348 | -0.060304 | -0.021525 | -0.033993 | 0.030038 | -0.032724 | 0.030676 | 14.6764 | 23.6861 | 14.9451 | 23.4136 | 23.472 | 46.9279 | 23.4452 | 46.609 | -8.7956 | -8.7688 | -8.5269 | -8.5001
2158.8906 | 121.55 | -23.4283 | 97.8424 | -23.4843 | -23.5115 | -23.4865 | -23.4898 | -23.4349 | -23.4931 | -23.4251 | -8.7657 | 0.23948 | -8.4969 | -0.03768 | 0.034501 | 23.4812 | 0.007721 | 23.1761 | -0.055972 | -0.083193 | -0.05815 | -0.06146 | -0.006584 | -0.06477 | 0.00321 | 14.6627 | 23.6678 | 14.9314 | 23.3907 | 23.4628 | 46.9096 | 23.4361 | 46.6045 | -8.8002 | -8.7734 | -8.5314 | -8.5047
2159.8906 | 121.5042 | -23.4741 | 97.7875 | -23.5118 | -23.5482 | -23.514 | -23.5264 | -23.4624 | -23.5206 | -23.4618 | -8.7657 | 0.24405 | -8.5015 | -0.042259 | 0.029923 | 23.5133 | -0.001436 | 23.2127 | -0.037666 | -0.074047 | -0.039845 | -0.052312 | 0.011724 | -0.046464 | 0.01236 | 14.7084 | 23.7182 | 14.9726 | 23.4319 | 23.504 | 46.9874 | 23.4727 | 46.6869 | -8.7956 | -8.7643 | -8.5314 | -8.5001
2160.8906 | 121.5042 | -23.5107 | 97.7966 | -23.5576 | -23.594 | -23.5598 | -23.5676 | -23.5036 | -23.5664 | -23.5167 | -8.7611 | 0.23948 | -8.5015 | -0.046838 | 0.029923 | 23.5545 | 0.003143 | 23.2631 | -0.046829 | -0.083214 | -0.04901 | -0.056897 | 0.007144 | -0.055627 | -0.005957 | 14.7496 | 23.7502 | 15.0092 | 23.4639 | 23.5407 | 47.0652 | 23.5139 | 46.7738 | -8.791 | -8.7643 | -8.5314 | -8.5047
2161.8906 | 121.5591 | -23.497 | 97.8195 | -23.5621 | -23.5985 | -23.5643 | -23.5722 | -23.5128 | -23.5755 | -23.503 | -8.7611 | 0.23948 | -8.4969 | -0.042259 | 0.034501 | 23.5636 | 0.003143 | 23.2677 | -0.06514 | -0.10153 | -0.067322 | -0.075209 | -0.015745 | -0.078517 | -0.005955 | 14.7359 | 23.7365 | 15.0001 | 23.4547 | 23.5315 | 47.0606 | 23.5002 | 46.7647 | -8.7956 | -8.7643 | -8.5314 | -8.5001
2162.8906 | 121.5363 | -23.465 | 97.8699 | -23.5072 | -23.5573 | -23.5094 | -23.5264 | -23.4578 | -23.5252 | -23.4663 | -8.7657 | 0.24405 | -8.5015 | -0.042259 | 0.020767 | 23.5087 | 0.007721 | 23.2173 | -0.042243 | -0.09236 | -0.044422 | -0.061467 | 0.007147 | -0.060197 | -0.001373 | 14.6993 | 23.709 | 14.9635 | 23.4227 | 23.4857 | 46.9737 | 23.4727 | 46.6823 | -8.7865 | -8.7734 | -8.5223 | -8.5092
2163.8906 | 121.5637 | -23.3871 | 97.9431 | -23.4706 | -23.507 | -23.4728 | -23.4852 | -23.4212 | -23.4885 | -23.416 | -8.7657 | 0.24405 | -8.5061 | -0.046838 | 0.034501 | 23.4767 | 0.007721 | 23.167 | -0.083436 | -0.11981 | -0.085613 | -0.09808 | -0.034049 | -0.10139 | -0.028833 | 14.6215 | 23.6312 | 14.8811 | 23.3403 | 23.4216 | 46.8638 | 23.3949 | 46.5541 | -8.8002 | -8.7734 | -8.5406 | -8.5138
2164.8906 | 121.5775 | -23.4238 | 97.8882 | -23.4889 | -23.5344 | -23.4911 | -23.5081 | -23.4395 | -23.5023 | -23.4434 | -8.7703 | 0.23948 | -8.4924 | -0.042259 | 0.020767 | 23.4995 | 0.003143 | 23.1899 | -0.065128 | -0.11066 | -0.067306 | -0.084352 | -0.01574 | -0.078504 | -0.019681 | 14.6535 | 23.6632 | 14.9314 | 23.3815 | 23.4445 | 46.9233 | 23.4269 | 46.6136 | -8.791 | -8.7734 | -8.5131 | -8.4955
2165.8906 | 121.582 | -23.3139 | 98.0072 | -23.379 | -23.4062 | -23.3766 | -23.3937 | -23.3342 | -23.397 | -23.3381 | -8.7657 | 0.23948 | -8.4969 | -0.03768 | 0.029923 | 23.3942 | -0.006014 | 23.0891 | -0.06511 | -0.092321 | -0.062704 | -0.079752 | -0.02031 | -0.083064 | -0.024246 | 14.5482 | 23.5534 | 14.817 | 23.2762 | 23.3438 | 46.7082 | 23.3079 | 46.403 | -8.7956 | -8.7597 | -8.5269 | -8.4909
2166.8906 | 121.5729 | -23.3139 | 98.0118 | -23.3973 | -23.4383 | -23.4041 | -23.4165 | -23.3479 | -23.4153 | -23.3565 | -8.7703 | 0.24405 | -8.4969 | -0.042259 | 0.029923 | 23.4126 | 0.007721 | 23.112 | -0.083423 | -0.12437 | -0.090176 | -0.10264 | -0.034044 | -0.10138 | -0.042559 | 14.5436 | 23.558 | 14.817 | 23.2716 | 23.3438 | 46.7265 | 23.3216 | 46.4259 | -8.8002 | -8.778 | -8.5269 | -8.5047
2167.8906 | 121.55 | -23.2635 | 98.1171 | -23.3195 | -23.3604 | -23.3217 | -23.3387 | -23.2655 | -23.3329 | -23.2649 | -8.7657 | 0.23948 | -8.5107 | -0.042259 | 0.025345 | 23.3302 | -0.001436 | 23.0205 | -0.055945 | -0.096887 | -0.058115 | -0.075164 | -0.001995 | -0.069321 | -0.001349 | 14.4979 | 23.503 | 14.7529 | 23.2213 | 23.2889 | 46.5937 | 23.2621 | 46.284 | -8.791 | -8.7643 | -8.536 | -8.5092
2168.8906 | 121.6278 | -23.1674 | 98.1628 | -23.2325 | -23.2734 | -23.2255 | -23.2471 | -23.1786 | -23.2459 | -23.1733 | -8.7565 | 0.23948 | -8.5061 | -0.03768 | 0.039079 | 23.2477 | 0.007721 | 22.9335 | -0.065086 | -0.10602 | -0.058095 | -0.079725 | -0.011144 | -0.078463 | -0.005917 | 14.4109 | 23.4069 | 14.6613 | 23.1297 | 23.2065 | 46.4152 | 23.1751 | 46.1009 | -8.7956 | -8.7643 | -8.5452 | -8.5138
2169.8906 | 121.5591 | -23.204 | 98.1857 | -23.2188 | -23.2505 | -23.2255 | -23.238 | -23.1694 | -23.2367 | -23.1688 | -8.7703 | 0.23948 | -8.5061 | -0.046838 | 0.034501 | 23.2432 | 0.003143 | 22.9335 | -0.014729 | -0.046504 | -0.021473 | -0.033946 | 0.034634 | -0.032684 | 0.035283 | 14.4338 | 23.4435 | 14.698 | 23.1572 | 23.2385 | 46.4472 | 23.2072 | 46.1375 | -8.8048 | -8.7734 | -8.5406 | -8.5092
2170.8906 | 121.6049 | -23.204 | 98.172 | -23.2829 | -23.3101 | -23.2805 | -23.2975 | -23.2335 | -23.2917 | -23.2283 | -8.7703 | 0.24405 | -8.5061 | -0.042259 | 0.025345 | 23.2935 | 0.003143 | 22.9838 | -0.078827 | -0.10603 | -0.076417 | -0.093467 | -0.029458 | -0.087625 | -0.024233 | 14.4338 | 23.4481 | 14.698 | 23.1618 | 23.2294 | 46.4976 | 23.2072 | 46.1879 | -8.7956 | -8.7734 | -8.5314 | -8.5092
2171.8906 | 121.5958 | -23.2132 | 98.1583 | -23.2691 | -23.3009 | -23.2759 | -23.2838 | -23.2198 | -23.2871 | -23.2283 | -8.7657 | 0.23948 | -8.4969 | -0.042259 | 0.034501 | 23.2844 | -0.001436 | 22.9701 | -0.055937 | -0.087716 | -0.062683 | -0.070576 | -0.006569 | -0.073891 | -0.015078 | 14.4475 | 23.4527 | 14.7163 | 23.1709 | 23.2477 | 46.4976 | 23.2118 | 46.1833 | -8.8002 | -8.7643 | -8.5314 | -8.4955
2172.8906 | 121.5042 | -23.2132 | 98.2269 | -23.2508 | -23.2826 | -23.2484 | -23.2609 | -23.1923 | -23.2596 | -23.2008 | -8.7749 | 0.24863 | -8.4924 | -0.03768 | 0.039079 | 23.2615 | -0.001436 | 22.9518 | -0.037623 | -0.069401 | -0.035211 | -0.047684 | 0.020899 | -0.046421 | 0.012391 | 14.4383 | 23.4618 | 14.7208 | 23.1755 | 23.2523 | 46.4747 | 23.2118 | 46.165 | -8.8139 | -8.7734 | -8.5314 | -8.4909
2173.8906 | 121.5912 | -23.1583 | 98.2132 | -23.2096 | -23.2414 | -23.2118 | -23.2243 | -23.1603 | -23.223 | -23.155 | -8.7703 | 0.23948 | -8.4969 | -0.03768 | 0.029923 | 23.2249 | 0.007721 | 22.9152 | -0.051349 | -0.083123 | -0.053515 | -0.065988 | -0.001988 | -0.064726 | 0.003241 | 14.388 | 23.3977 | 14.6613 | 23.1206 | 23.1882 | 46.3831 | 23.166 | 46.0734 | -8.8002 | -8.778 | -8.5269 | -8.5047
2174.8906 | 121.6324 | -23.0942 | 98.3002 | -23.1684 | -23.2048 | -23.1614 | -23.1739 | -23.1145 | -23.1772 | -23.1092 | -8.7703 | 0.24405 | -8.5061 | -0.042259 | 0.043657 | 23.1837 | 0.007721 | 22.8648 | -0.074231 | -0.11058 | -0.067237 | -0.079712 | -0.020295 | -0.083029 | -0.015064 | 14.3239 | 23.3382 | 14.5881 | 23.0519 | 23.1378 | 46.2778 | 23.1019 | 45.959 | -8.8139 | -8.778 | -8.5497 | -8.5138
2175.8906 | 121.5134 | -23.0804 | 98.378 | -23.1318 | -23.1727 | -23.1385 | -23.1464 | -23.0824 | -23.1497 | -23.0818 | -8.7703 | 0.23948 | -8.5061 | -0.042259 | 0.029923 | 23.147 | -0.006014 | 22.8373 | -0.051337 | -0.092261 | -0.058077 | -0.065974 | -0.001982 | -0.069292 | -0.001328 | 14.3102 | 23.3199 | 14.5744 | 23.0382 | 23.1104 | 46.2275 | 23.0744 | 45.9178 | -8.8002 | -8.7643 | -8.536 | -8.5001
2176.8906 | 121.5271 | -23.1308 | 98.3459 | -23.1593 | -23.1864 | -23.1477 | -23.1647 | -23.1053 | -23.168 | -23.0955 | -8.7703 | 0.24405 | -8.4969 | -0.03768 | 0.025345 | 23.1653 | 0.007721 | 22.8556 | -0.028453 | -0.055644 | -0.01688 | -0.033934 | 0.025482 | -0.037251 | 0.035291 | 14.3605 | 23.3749 | 14.6339 | 23.0931 | 23.1561 | 46.2961 | 23.1385 | 45.9864 | -8.7956 | -8.778 | -8.5223 | -8.5047
2177.8906 | 121.582 | -23.0896 | 98.3871 | -23.118 | -23.1544 | -23.1202 | -23.1327 | -23.0687 | -23.1314 | -23.0772 | -8.7749 | 0.23032 | -8.5061 | -0.03768 | 0.029923 | 23.1287 | -0.006014 | 22.8236 | -0.028446 | -0.06479 | -0.030607 | -0.043082 | 0.020908 | -0.041822 | 0.012406 | 14.3147 | 23.3199 | 14.5835 | 23.0519 | 23.1195 | 46.2183 | 23.0836 | 45.9132 | -8.8048 | -8.7688 | -8.536 | -8.5001
2178.8906 | 121.6553 | -23.0026 | 98.3917 | -23.0814 | -23.1132 | -23.0882 | -23.0915 | -23.0321 | -23.0948 | -23.0314 | -8.7749 | 0.24405 | -8.5107 | -0.046838 | 0.029923 | 23.0921 | 0.003143 | 22.7778 | -0.078794 | -0.11056 | -0.085531 | -0.088851 | -0.029444 | -0.09217 | -0.028787 | 14.2278 | 23.2467 | 14.492 | 22.9558 | 23.0325 | 46.0947 | 23.0058 | 45.7804 | -8.8048 | -8.778 | -8.5406 | -8.5138
2179.8906 | 121.6919 | -22.9752 | 98.4375 | -23.0539 | -23.0857 | -23.0469 | -23.0594 | -22.9954 | -23.0719 | -22.9994 | -8.7657 | 0.24405 | -8.5061 | -0.046838 | 0.034501 | 23.0509 | 0.007721 | 22.7458 | -0.078789 | -0.11055 | -0.07179 | -0.084267 | -0.020286 | -0.096744 | -0.024206 | 14.2095 | 23.2192 | 14.4691 | 22.9283 | 23.0097 | 46.026 | 22.9829 | 45.7209 | -8.8002 | -8.7734 | -8.5406 | -8.5138
2180.8906 | 121.5912 | -22.9706 | 98.5107 | -23.0265 | -23.0582 | -23.0286 | -23.0365 | -22.9726 | -23.0399 | -22.9719 | -8.7794 | 0.2349 | -8.5061 | -0.042259 | 0.034501 | 23.0326 | -0.006014 | 22.7229 | -0.055897 | -0.087654 | -0.058053 | -0.065953 | -0.001974 | -0.069273 | -0.001315 | 14.1912 | 23.2055 | 14.4645 | 22.9283 | 23.0051 | 46.0032 | 22.9646 | 45.6935 | -8.8139 | -8.7734 | -8.5406 | -8.5001
2181.8906 | 121.7056 | -22.8973 | 98.5474 | -22.9578 | -22.9804 | -22.96 | -22.9633 | -22.8993 | -22.9758 | -22.8986 | -8.7749 | 0.2349 | -8.5061 | -0.03768 | 0.034501 | 22.9593 | -0.001436 | 22.6542 | -0.060463 | -0.083056 | -0.062616 | -0.065939 | -0.001969 | -0.078418 | -0.001306 | 14.1225 | 23.1322 | 14.3913 | 22.8597 | 22.9318 | 45.8567 | 22.8959 | 45.5515 | -8.8094 | -8.7734 | -8.5406 | -8.5046
2182.9062 | 121.5637 | -22.9568 | 98.5336 | -22.9853 | -23.0216 | -22.992 | -22.9999 | -22.9314 | -22.9986 | -22.9353 | -8.7703 | 0.23948 | -8.4969 | -0.033101 | 0.039079 | 22.9914 | 0.007721 | 22.6817 | -0.028424 | -0.064756 | -0.035158 | -0.043058 | 0.025494 | -0.041801 | 0.021577 | 14.1866 | 23.1963 | 14.4599 | 22.9237 | 22.9959 | 45.9482 | 22.9646 | 45.6385 | -8.8094 | -8.778 | -8.536 | -8.5047
2183.8906 | 121.5729 | -22.9752 | 98.5382 | -22.9944 | -23.0353 | -22.9966 | -23.0091 | -22.9451 | -23.0078 | -22.9444 | -8.7703 | 0.23948 | -8.5107 | -0.042259 | 0.039079 | 23.0097 | 0.003143 | 22.7046 | -0.01927 | -0.060182 | -0.021425 | -0.033904 | 0.030072 | -0.032646 | 0.030732 | 14.2049 | 23.2146 | 14.4645 | 22.9329 | 23.0142 | 45.9848 | 22.9783 | 45.6797 | -8.8094 | -8.7734 | -8.5497 | -8.5138
2184.8906 | 121.6553 | -22.9797 | 98.5153 | -23.0173 | -23.0445 | -23.0057 | -23.0136 | -22.9542 | -23.0261 | -22.9582 | -8.7749 | 0.24863 | -8.5061 | -0.03768 | 0.034501 | 23.0188 | 0.007721 | 22.7137 | -0.037585 | -0.064762 | -0.026005 | -0.033905 | 0.025493 | -0.046383 | 0.021574 | 14.2049 | 23.2284 | 14.4736 | 22.9421 | 23.0142 | 45.9986 | 22.9875 | 45.6935 | -8.8094 | -8.7826 | -8.5406 | -8.5138
2185.8906 | 121.5683 | -22.9202 | 98.5977 | -22.9532 | -22.9896 | -22.96 | -22.9724 | -22.913 | -22.9666 | -22.8986 | -8.7749 | 0.2349 | -8.5061 | -0.03768 | 0.039079 | 22.9593 | 0.003143 | 22.6634 | -0.032997 | -0.069325 | -0.039728 | -0.052208 | 0.007185 | -0.046373 | 0.021582 | 14.1454 | 23.1551 | 14.4141 | 22.8825 | 22.9593 | 45.8796 | 22.9234 | 45.5836 | -8.8139 | -8.778 | -8.5452 | -8.5092
2186.8906 | 121.5683 | -22.9202 | 98.616 | -22.9395 | -22.9758 | -22.9416 | -22.945 | -22.8902 | -22.9529 | -22.8803 | -8.7794 | 0.23948 | -8.5061 | -0.042259 | 0.034501 | 22.9456 | -0.001436 | 22.6405 | -0.019262 | -0.055589 | -0.021414 | -0.024737 | 0.030075 | -0.032638 | 0.039894 | 14.1408 | 23.1597 | 14.4141 | 22.878 | 22.9547 | 45.8658 | 22.9188 | 45.5607 | -8.8139 | -8.778 | -8.5406 | -8.5046
2187.8906 | 121.6278 | -22.8653 | 98.6893 | -22.912 | -22.9483 | -22.9142 | -22.9266 | -22.8718 | -22.9391 | -22.8666 | -8.7749 | 0.24405 | -8.5061 | -0.03768 | 0.039079 | 22.9273 | 0.007721 | 22.6176 | -0.046723 | -0.083048 | -0.048874 | -0.061355 | -0.006545 | -0.073835 | -0.001303 | 14.0904 | 23.1093 | 14.3592 | 22.8276 | 22.9044 | 45.7926 | 22.873 | 45.4829 | -8.8139 | -8.7826 | -8.5452 | -8.5138
2188.8906 | 121.6415 | -22.8516 | 98.6618 | -22.8937 | -22.9346 | -22.8959 | -22.9083 | -22.8444 | -22.9117 | -22.8437 | -8.7749 | 0.2349 | -8.5107 | -0.042259 | 0.034501 | 22.9044 | -0.001436 | 22.5993 | -0.042143 | -0.083045 | -0.044293 | -0.056774 | 0.00719 | -0.060097 | 0.007855 | 14.0767 | 23.0865 | 14.3409 | 22.8093 | 22.8861 | 45.756 | 22.8501 | 45.4508 | -8.8094 | -8.7734 | -8.5452 | -8.5092
2189.8906 | 121.6141 | -22.8516 | 98.7259 | -22.8708 | -22.898 | -22.8684 | -22.8763 | -22.8169 | -22.875 | -22.8117 | -8.7703 | 0.23948 | -8.5152 | -0.03768 | 0.039079 | 22.8723 | -0.001436 | 22.5672 | -0.019251 | -0.046414 | -0.016821 | -0.024724 | 0.034657 | -0.02347 | 0.039902 | 14.0813 | 23.091 | 14.3363 | 22.8139 | 22.8906 | 45.7239 | 22.8501 | 45.4188 | -8.8094 | -8.7688 | -8.5543 | -8.5138
2190.8906 | 121.6324 | -22.8195 | 98.7167 | -22.8571 | -22.8934 | -22.8546 | -22.8671 | -22.8077 | -22.8613 | -22.7979 | -8.7749 | 0.24863 | -8.5015 | -0.042259 | 0.029923 | 22.8632 | 0.003143 | 22.5626 | -0.037559 | -0.073878 | -0.035129 | -0.04761 | 0.01177 | -0.041778 | 0.021593 | 14.0447 | 23.0682 | 14.318 | 22.7773 | 22.8494 | 45.6827 | 22.8227 | 45.3822 | -8.8048 | -8.778 | -8.5314 | -8.5047
2191.8906 | 121.6553 | -22.8241 | 98.703 | -22.8662 | -22.9026 | -22.8592 | -22.8717 | -22.8169 | -22.8842 | -22.8117 | -8.7749 | 0.23948 | -8.5015 | -0.03768 | 0.034501 | 22.8723 | 0.007721 | 22.5718 | -0.042137 | -0.078458 | -0.035129 | -0.047611 | 0.007192 | -0.060092 | 0.012437 | 14.0492 | 23.0636 | 14.3226 | 22.7864 | 22.8586 | 45.6964 | 22.8318 | 45.3959 | -8.8094 | -8.7826 | -8.536 | -8.5092
2192.8906 | 121.6187 | -22.8104 | 98.7167 | -22.8525 | -22.8888 | -22.8455 | -22.8626 | -22.7894 | -22.8567 | -22.7979 | -8.7703 | 0.23948 | -8.4969 | -0.03768 | 0.034501 | 22.8632 | 0.007721 | 22.5581 | -0.042135 | -0.078455 | -0.035126 | -0.052187 | 0.020927 | -0.046355 | 0.012438 | 14.0401 | 23.0498 | 14.3134 | 22.7727 | 22.8449 | 45.6736 | 22.8181 | 45.3684 | -8.8048 | -8.778 | -8.5314 | -8.5047
2193.8906 | 121.6507 | -22.7737 | 98.7534 | -22.8113 | -22.843 | -22.8043 | -22.8168 | -22.7574 | -22.8247 | -22.7567 | -8.7794 | 0.24405 | -8.5061 | -0.03768 | 0.029923 | 22.8174 | -0.001436 | 22.5077 | -0.037551 | -0.069287 | -0.03054 | -0.043023 | 0.016352 | -0.050927 | 0.017021 | 13.9943 | 23.0178 | 14.2677 | 22.7361 | 22.8037 | 45.5912 | 22.7723 | 45.2814 | -8.8094 | -8.778 | -8.536 | -8.5046
2194.8906 | 121.6187 | -22.8333 | 98.7213 | -22.8342 | -22.8705 | -22.8318 | -22.8488 | -22.7803 | -22.8476 | -22.775 | -8.7703 | 0.24405 | -8.4969 | -0.03768 | 0.020767 | 22.8495 | -0.001436 | 22.5443 | -0.000934 | -0.037251 | 0.001497 | -0.015563 | 0.052971 | -0.01431 | 0.058217 | 14.063 | 23.0773 | 14.3363 | 22.7956 | 22.854 | 45.6827 | 22.8318 | 45.3776 | -8.791 | -8.7688 | -8.5177 | -8.4955
2195.8906 | 121.6049 | -22.7737 | 98.7854 | -22.7701 | -22.8247 | -22.7814 | -22.7893 | -22.7299 | -22.7972 | -22.7247 | -8.7703 | 0.23948 | -8.5015 | -0.03768 | 0.034501 | 22.7854 | 0.003143 | 22.4848 | 0.003655 | -0.050972 | -0.007647 | -0.015552 | 0.04382 | -0.023457 | 0.049068 | 14.0035 | 23.0132 | 14.2722 | 22.7361 | 22.8082 | 45.5591 | 22.7769 | 45.2586 | -8.8048 | -8.7734 | -8.536 | -8.5047
2196.8906 | 121.669 | -22.7554 | 98.7808 | -22.7976 | -22.8293 | -22.7905 | -22.8076 | -22.7391 | -22.8018 | -22.7384 | -8.7794 | 0.24405 | -8.5015 | -0.03768 | 0.034501 | 22.7991 | 0.003143 | 22.4848 | -0.042127 | -0.073862 | -0.035115 | -0.052177 | 0.016353 | -0.046346 | 0.017023 | 13.976 | 22.9995 | 14.2539 | 22.7178 | 22.7899 | 45.5545 | 22.7586 | 45.2402 | -8.8139 | -8.7826 | -8.536 | -8.5047
2197.8906 | 121.6736 | -22.6776 | 98.8632 | -22.7335 | -22.7698 | -22.731 | -22.7298 | -22.675 | -22.7468 | -22.6789 | -8.7749 | 0.23948 | -8.5152 | -0.03768 | 0.039079 | 22.7396 | 0.007721 | 22.4253 | -0.055849 | -0.092157 | -0.053413 | -0.052163 | 0.002624 | -0.069225 | -0.001281 | 13.9028 | 22.9171 | 14.1624 | 22.6399 | 22.7167 | 45.4172 | 22.6853 | 45.1029 | -8.8139 | -8.7826 | -8.5543 | -8.523
2198.8906 | 121.6232 | -22.673 | 98.9273 | -22.6648 | -22.6965 | -22.6623 | -22.6703 | -22.6109 | -22.6736 | -22.6102 | -8.7703 | 0.24405 | -8.5061 | -0.046838 | 0.029923 | 22.6755 | -0.001436 | 22.3704 | 0.00825 | -0.023473 | 0.010689 | 0.002781 | 0.062139 | -0.000548 | 0.062815 | 13.9028 | 22.9171 | 14.1669 | 22.6262 | 22.703 | 45.3485 | 22.6716 | 45.0434 | -8.8002 | -8.7688 | -8.536 | -8.5046
2199.8906 | 121.701 | -22.5952 | 98.9777 | -22.6144 | -22.6553 | -22.6166 | -22.629 | -22.5697 | -22.6324 | -22.5644 | -8.7749 | 0.24863 | -8.5061 | -0.03768 | 0.029923 | 22.6251 | -0.001436 | 22.3246 | -0.019208 | -0.060084 | -0.021345 | -0.033833 | 0.02552 | -0.037163 | 0.030776 | 13.8204 | 22.8438 | 14.0891 | 22.5575 | 22.6251 | 45.2203 | 22.5938 | 44.9198 | -8.8048 | -8.7734 | -8.536 | -8.5046
2200.8906 | 121.756 | -22.6089 | 98.8998 | -22.6465 | -22.6874 | -22.6532 | -22.6565 | -22.6063 | -22.669 | -22.6011 | -8.7749 | 0.23948 | -8.5061 | -0.046838 | 0.029923 | 22.6618 | -0.006014 | 22.3566 | -0.037524 | -0.078403 | -0.044241 | -0.047571 | 0.002629 | -0.060057 | 0.007884 | 13.8341 | 22.8484 | 14.1029 | 22.5621 | 22.6389 | 45.2707 | 22.6029 | 44.9656 | -8.8048 | -8.7688 | -8.536 | -8.5001
|  |  |  | -22.6694 | -22.7011 | -22.6715 | -22.6703 | -22.6155 | -22.669 | -22.6056 | -8.7703 | 0.24405 | -8.5061 | -0.03768 | 0.029923 | 22.6663 | 0.003143 | 22.3658 | -0.01464 | -0.046363 | -0.016779 | -0.01553 | 0.03925 | -0.014281 | 0.049082 | 13.8845 | 22.8988 | 14.1486 | 22.617 | 22.6846 | 45.3211 | 22.6579 | 45.0205 | -8.8002 | -8.7734 | -8.536 | -8.5092
|  |  |  | -22.6694 | -22.7011 | -22.6578 | -22.6794 | -22.6155 | -22.6827 | -22.6102 | -8.7703 | 0.24863 | -8.5061 | -0.03768 | 0.034501 | 22.6663 | -0.001436 | 22.3704 | -0.042106 | -0.073829 | -0.03051 | -0.052153 | 0.011784 | -0.055482 | 0.017038 | 13.857 | 22.8759 | 14.1212 | 22.5896 | 22.6618 | 45.2936 | 22.6258 | 44.9976 | -8.8048 | -8.7688 | -8.5406 | -8.5046
|  |  |  | -22.6465 | -22.6828 | -22.644 | -22.6565 | -22.588 | -22.6644 | -22.5782 | -8.7703 | 0.24405 | -8.5061 | -0.042259 | 0.034501 | 22.648 | -0.001436 | 22.352 | -0.019214 | -0.055514 | -0.016774 | -0.029261 | 0.039251 | -0.037168 | 0.049085 | 13.857 | 22.8713 | 14.1212 | 22.585 | 22.6618 | 45.2753 | 22.6258 | 44.9793 | -8.8048 | -8.7688 | -8.5406 | -8.5046
|  |  |  | -22.5503 | -22.5775 | -22.5433 | -22.5512 | -22.4919 | -22.5683 | -22.4912 | -8.7749 | 0.24863 | -8.4969 | -0.046838 | 0.034501 | 22.5473 | 0.003143 | 22.2467 | -0.083285 | -0.11042 | -0.076262 | -0.084172 | -0.024829 | -0.10124 | -0.024147 | 13.6922 | 22.7157 | 13.9701 | 22.4202 | 22.5015 | 45.0143 | 22.4702 | 44.7138 | -8.8094 | -8.778 | -8.5314 | -8.5001
|  |  |  | -22.5366 | -22.5729 | -22.5433 | -22.5512 | -22.4736 | -22.55 | -22.4729 | -8.7749 | 0.24405 | -8.5061 | -0.03768 | 0.034501 | 22.5381 | 0.003143 | 22.2376 | -0.069549 | -0.10584 | -0.076262 | -0.084172 | -0.006517 | -0.082926 | -0.005834 | 13.6922 | 22.7111 | 13.961 | 22.4294 | 22.5015 | 45.0052 | 22.4702 | 44.7046 | -8.8094 | -8.778 | -8.5406 | -8.5092
|  |  |  | -22.5091 | -22.5454 | -22.5113 | -22.5146 | -22.4552 | -22.5271 | -22.4591 | -8.784 | 0.24863 | -8.4969 | -0.03768 | 0.025345 | 22.5061 | 0.003143 | 22.2101 | -0.032924 | -0.069211 | -0.035056 | -0.038389 | 0.02095 | -0.050879 | 0.017055 | 13.6922 | 22.7248 | 13.9793 | 22.4385 | 22.5015 | 44.9823 | 22.4793 | 44.6863 | -8.8094 | -8.7872 | -8.5223 | -8.5001
|  |  |  | -22.445 | -22.4813 | -22.4426 | -22.4596 | -22.3957 | -22.463 | -22.3859 | -8.7703 | 0.24863 | -8.5061 | -0.03768 | 0.020767 | 22.4512 | 0.003143 | 22.1506 | -0.019181 | -0.055462 | -0.016731 | -0.033801 | 0.03011 | -0.037135 | 0.039952 | 13.6556 | 22.6745 | 13.9198 | 22.3882 | 22.4466 | 44.877 | 22.429 | 44.5764 | -8.791 | -8.7734 | -8.5269 | -8.5092
|  |  |  | -22.4679 | -22.5042 | -22.4563 | -22.4734 | -22.414 | -22.4813 | -22.4088 | -8.7794 | 0.23948 | -8.5107 | -0.03768 | 0.034501 | 22.4741 | 0.003143 | 22.1643 | -0.064961 | -0.10124 | -0.053355 | -0.070425 | -0.01109 | -0.078337 | -0.005827 | 13.6235 | 22.6424 | 13.8923 | 22.3653 | 22.4375 | 44.877 | 22.4061 | 44.5673 | -8.8139 | -8.7826 | -8.5452 | -8.5138
|  |  |  | -22.4679 | -22.5134 | -22.4655 | -22.4825 | -22.4232 | -22.4904 | -22.4179 | -8.7703 | 0.24863 | -8.5107 | -0.042259 | 0.034501 | 22.4786 | 0.003143 | 22.1689 | -0.010029 | -0.055469 | -0.00758 | -0.02465 | 0.034686 | -0.032562 | 0.039949 | 13.6876 | 22.7065 | 13.9472 | 22.4156 | 22.4924 | 44.9365 | 22.461 | 44.6268 | -8.8048 | -8.7734 | -8.5452 | -8.5138
|  |  |  | -22.4771 | -22.5179 | -22.4792 | -22.478 | -22.4186 | -22.4813 | -22.4134 | -8.784 | 0.23948 | -8.5015 | -0.042259 | 0.039079 | 22.4786 | 0.003143 | 22.1735 | -0.051229 | -0.092092 | -0.05336 | -0.052115 | 0.00722 | -0.055449 | 0.012483 | 13.6418 | 22.6653 | 13.9243 | 22.3836 | 22.4649 | 44.9045 | 22.429 | 44.5993 | -8.8231 | -8.7872 | -8.5406 | -8.5047
|  |  |  | -22.4542 | -22.5042 | -22.4563 | -22.478 | -22.4049 | -22.4813 | -22.4042 | -8.7749 | 0.24405 | -8.5061 | -0.03768 | 0.029923 | 22.4603 | -0.001436 | 22.1643 | -0.010026 | -0.060045 | -0.012156 | -0.033804 | 0.039265 | -0.037138 | 0.03995 | 13.6693 | 22.6882 | 13.9381 | 22.4065 | 22.4741 | 44.9045 | 22.4427 | 44.6085 | -8.8048 | -8.7734 | -8.536 | -8.5046
|  |  |  | -22.4679 | -22.5042 | -22.4655 | -22.478 | -22.4186 | -22.4904 | -22.4179 | -8.784 | 0.25321 | -8.5107 | -0.03768 | 0.039079 | 22.4786 | -0.006014 | 22.1781 | -0.069539 | -0.10582 | -0.06709 | -0.079581 | -0.020246 | -0.092072 | -0.019561 | 13.6144 | 22.6516 | 13.8877 | 22.3607 | 22.4375 | 44.877 | 22.3924 | 44.5765 | -8.8231 | -8.778 | -8.5497 | -8.5047
|  |  |  | -22.4679 | -22.5088 | -22.47 | -22.4734 | -22.414 | -22.4859 | -22.4179 | -8.7794 | 0.24405 | -8.5061 | -0.042259 | 0.029923 | 22.4695 | -0.006014 | 22.1735 | -0.032917 | -0.073779 | -0.035047 | -0.038381 | 0.020954 | -0.050871 | 0.017061 | 13.6556 | 22.6791 | 13.9289 | 22.3927 | 22.4649 | 44.9045 | 22.429 | 44.6085 | -8.8094 | -8.7734 | -8.536 | -8.5001
|  |  |  | -22.445 | -22.4859 | -22.4472 | -22.4596 | -22.3912 | -22.4676 | -22.395 | -8.7749 | 0.24405 | -8.5061 | -0.042259 | 0.034501 | 22.4512 | -0.006014 | 22.1506 | -0.060379 | -0.10124 | -0.062508 | -0.074999 | -0.00651 | -0.082912 | -0.010402 | 13.6098 | 22.6287 | 13.8786 | 22.3424 | 22.4191 | 44.8358 | 22.3786 | 44.5353 | -8.8094 | -8.7688 | -8.5406 | -8.5001
|  |  |  | -22.413 | -22.4493 | -22.4105 | -22.4139 | -22.3637 | -22.4218 | -22.3538 | -8.7794 | 0.23948 | -8.5061 | -0.046838 | 0.029923 | 22.41 | -0.001436 | 22.1186 | -0.042063 | -0.078341 | -0.039612 | -0.042947 | 0.007224 | -0.050861 | 0.017068 | 13.5915 | 22.6104 | 13.8648 | 22.3241 | 22.4008 | 44.7809 | 22.3695 | 44.4895 | -8.8094 | -8.778 | -8.536 | -8.5046
|  |  |  | -22.3489 | -22.3897 | -22.351 | -22.3589 | -22.295 | -22.3668 | -22.2943 | -8.7794 | 0.24405 | -8.4969 | -0.033101 | 0.034501 | 22.3596 | 0.007721 | 22.059 | -0.01001 | -0.05086 | -0.012134 | -0.020049 | 0.04385 | -0.027964 | 0.044541 | 13.5594 | 22.5829 | 13.8419 | 22.3058 | 22.3734 | 44.6985 | 22.3466 | 44.3979 | -8.8139 | -8.7872 | -8.5314 | -8.5047
|  |  |  | -22.3306 | -22.376 | -22.3327 | -22.3452 | -22.2859 | -22.3577 | -22.2806 | -8.7886 | 0.24405 | -8.5061 | -0.033101 | 0.034501 | 22.3413 | 0.012299 | 22.0407 | -0.019162 | -0.06459 | -0.021286 | -0.03378 | 0.02554 | -0.046273 | 0.030809 | 13.5228 | 22.5555 | 13.8053 | 22.2783 | 22.3459 | 44.6527 | 22.3237 | 44.3521 | -8.8231 | -8.8009 | -8.5406 | -8.5184
|  |  |  | -22.3489 | -22.3851 | -22.3464 | -22.3589 | -22.2859 | -22.3668 | -22.2852 | -8.7794 | 0.24405 | -8.5107 | -0.046838 | 0.029923 | 22.3504 | -0.001436 | 22.0499 | -0.060364 | -0.096636 | -0.05791 | -0.070403 | 0.002652 | -0.078318 | 0.003343 | 13.5091 | 22.5326 | 13.7778 | 22.2417 | 22.3184 | 44.639 | 22.2871 | 44.3384 | -8.8094 | -8.778 | -8.5406 | -8.5092
|  |  |  | -22.326 | -22.3623 | -22.319 | -22.336 | -22.2721 | -22.3439 | -22.2714 | -8.7703 | 0.25321 | -8.5015 | -0.03768 | 0.034501 | 22.3321 | -0.001436 | 22.027 | -0.078671 | -0.11494 | -0.071637 | -0.08871 | -0.024814 | -0.096625 | -0.024122 | 13.477 | 22.5005 | 13.7458 | 22.2096 | 22.2818 | 44.5794 | 22.2459 | 44.2743 | -8.8048 | -8.7688 | -8.536 | -8.5001
|  |  |  | -22.3306 | -22.376 | -22.3327 | -22.3314 | -22.2767 | -22.3394 | -22.276 | -8.7794 | 0.24405 | -8.5015 | -0.092628 | 0.034501 | 22.3367 | -0.001436 | 22.0224 | -0.087826 | -0.13325 | -0.08995 | -0.088708 | -0.033968 | -0.096624 | -0.033277 | 13.4633 | 22.4868 | 13.7412 | 22.1501 | 22.2772 | 44.5795 | 22.2413 | 44.2652 | -8.8139 | -8.778 | -8.536 | -8.5001

## Thermal Data
Fire Time | North 25 C | Cable 1 | Cable 2
-0.0427 | 21.051
0.9573 | 21.0528
1.9573 | 21.053
2.9573 | 21.0589
3.9573 | 21.2873
4.9573 | 22.2129
5.9573 | 23.966
6.9573 | 26.4445
7.9573 | 29.5161
8.9573 | 33.0612
9.9573 | 36.9983
10.9573 | 41.2081
11.9573 | 45.6893
12.9573 | 50.3787
13.9573 | 55.3338
14.9573 | 60.4748
15.9573 | 65.744
16.9573 | 71.1531
17.9573 | 76.6479
18.9573 | 82.2888
19.9573 | 87.9584
20.9573 | 93.7137
21.9573 | 99.5111
22.9573 | 105.348
23.9573 | 111.2489
24.9573 | 117.1499
25.9573 | 123.1279
26.9573 | 129.1677
27.9573 | 135.229
28.9573 | 141.2677
29.9573 | 147.2805
30.9573 | 153.2387
31.9573 | 159.3247
32.9573 | 165.2767
33.9573 | 171.1262
34.9573 | 177.0864
35.9573 | 183.0763
36.9573 | 189.046
37.9573 | 194.8984
38.9573 | 200.7267
39.9573 | 206.641
40.9573 | 212.552
41.9573 | 218.3913
42.9573 | 224.1998
43.9573 | 230.0625
44.9573 | 235.8638
45.9573 | 241.5887
46.9573 | 247.4309
47.9573 | 253.2285
48.9573 | 258.9524
49.9573 | 264.8149
50.9573 | 270.5584
51.9573 | 276.0801
52.9573 | 281.5875
53.9573 | 287.1993
54.9573 | 292.7179
55.9573 | 298.2281
56.9573 | 303.6154
57.9573 | 308.9562
58.9573 | 314.3144
59.9573 | 319.7513
60.9573 | 325.2642
61.9573 | 330.6961
62.9573 | 336.3062
63.9573 | 341.7191
64.9573 | 346.8978
65.9573 | 352.143
66.9573 | 357.2857
67.9573 | 362.4249
68.9573 | 367.6404
69.9573 | 372.7463
70.9573 | 377.7588
71.9573 | 382.705
72.9573 | 387.5389
73.9573 | 392.5473
74.9573 | 397.6345
75.9573 | 402.4504
76.9573 | 407.492
77.9573 | 412.1101
78.9573 | 416.2534
79.9573 | 419.9288
80.9573 | 423.2599
81.9573 | 426.334
82.9573 | 429.2724
83.9573 | 432.1611
84.9573 | 434.9051
85.9573 | 437.7521
86.9573 | 440.523
87.9573 | 443.3506
88.9573 | 445.8887
89.9573 | 448.0365
90.9573 | 449.9801
91.9573 | 451.6216
92.9573 | 453.2111
93.9573 | 454.5268
94.9573 | 455.4828
95.9573 | 456.2826
96.9573 | 457.0735
97.9573 | 457.5924
98.9573 | 457.742
99.9573 | 458.0148
100.9573 | 458.3375
101.9573 | 458.3993
102.9573 | 458.483
103.9573 | 458.5365
104.9573 | 458.5799
105.9573 | 458.6465
106.9573 | 458.662
107.9573 | 458.5511
108.9573 | 458.5993
109.9573 | 458.7745
110.9573 | 459.0343
111.9573 | 459.1176
112.9573 | 459.2355
113.9573 | 459.4883
114.9573 | 459.5362
115.9573 | 459.7199
116.9573 | 459.8417
117.9573 | 460.0012
118.9573 | 460.1578
119.9573 | 460.2428
120.9573 | 460.3932
121.9573 | 460.5883
122.9573 | 460.6376
123.9573 | 460.7077
124.9573 | 460.7278
125.9573 | 460.8556
126.9573 | 460.9818
127.9573 | 460.9441
128.9573 | 461.1083
129.9573 | 461.2925
130.9573 | 461.3386
131.9573 | 461.2745
132.9573 | 461.3041
133.9573 | 461.5055
134.9573 | 461.6453
135.9573 | 461.7404
136.9573 | 461.8518
137.9573 | 461.9911
138.9573 | 462.0872
139.9573 | 462.0617
140.9573 | 462.1002
141.9573 | 462.0393
142.9573 | 461.8959
143.9573 | 461.9058
144.9573 | 462.0606
145.9573 | 462.2021
146.9573 | 462.1386
147.9573 | 462.0918
148.9573 | 462.1467
149.9573 | 462.4103
150.9573 | 462.5997
151.9573 | 462.7423
152.9573 | 462.8774
153.9573 | 462.953
154.9573 | 463.1967
155.9573 | 463.289
156.9573 | 463.445
157.9573 | 463.7026
158.9573 | 463.9463
159.9573 | 464.033
160.9573 | 464.1478
161.9573 | 464.3167
162.9573 | 464.2411
163.9573 | 464.0804
164.9573 | 464.0378
165.9573 | 464.2865
166.9573 | 464.1679
167.9573 | 464.1341
168.9573 | 464.2646
169.9573 | 464.3221
170.9573 | 464.328
171.9573 | 464.35
172.9573 | 464.3512
173.9573 | 464.3696
174.9573 | 464.1365
175.9573 | 463.96
176.9573 | 463.8032
177.9573 | 463.792
178.9573 | 463.6537
179.9573 | 463.6485
180.9573 | 463.6517
181.9573 | 463.8352
182.9573 | 463.9328
183.9573 | 463.9038
184.9573 | 463.8524
185.9573 | 463.9319
186.9573 | 464.0932
187.9573 | 464.0399
188.9573 | 464.0498
189.9573 | 464.1757
190.9573 | 464.1771
191.9573 | 464.0576
192.9573 | 463.8641
193.9573 | 463.7904
194.9573 | 463.7738
195.9573 | 463.4674
196.9573 | 463.3922
197.9573 | 463.0885
198.9573 | 463.0126
199.9573 | 463.0984
200.9573 | 463.2151
201.9573 | 463.3479
202.9573 | 463.6411
203.9573 | 463.7305
204.9573 | 463.7171
205.9573 | 463.7694
206.9573 | 463.8484
207.9573 | 463.9805
208.9573 | 464.0775
209.9573 | 464.0495
210.9573 | 463.9472
211.9573 | 464.0873
212.9573 | 463.8513
213.9573 | 463.8913
214.9573 | 463.8737
215.9573 | 463.6698
216.9573 | 463.6195
217.9573 | 463.5781
218.9573 | 463.6452
219.9573 | 463.7532
220.9573 | 463.6351
221.9573 | 463.6739
222.9573 | 463.6356
223.9573 | 463.6741
224.9573 | 463.8845
225.9573 | 463.8732
226.9573 | 463.8647
227.9573 | 463.7638
228.9573 | 463.7098
229.9573 | 463.7523
230.9573 | 463.5897
231.9729 | 463.3505
232.9573 | 463.1064
233.9573 | 462.9489
234.9573 | 462.9045
235.9573 | 462.8282
236.9573 | 462.5341
237.9573 | 462.3306
238.9573 | 462.2127
239.9573 | 462.2318
240.9573 | 462.1855
241.9573 | 462.3482
242.9573 | 462.2965
243.9573 | 462.182
244.9573 | 462.0783
245.9573 | 461.969
246.9573 | 461.8865
247.9573 | 461.7926
248.9573 | 461.8245
249.9573 | 461.8796
250.9573 | 461.8339
251.9573 | 461.7588
252.9573 | 461.7856
253.9573 | 461.9082
254.9573 | 462.0446
255.9573 | 462.1194
256.9573 | 462.0797
257.9573 | 462.0584
258.9573 | 462.0707
259.9573 | 462.1344
260.9573 | 462.2694
261.9573 | 462.2301
262.9573 | 462.2741
263.9573 | 462.2266
264.9573 | 462.2099
265.9573 | 462.1466
266.9573 | 462.0746
267.9573 | 461.8995
268.9573 | 461.7747
269.9573 | 461.9197
270.9573 | 462.0636
271.9573 | 462.2332
272.9573 | 462.1479
273.9573 | 462.0404
274.9573 | 462.1161
275.9573 | 462.0849
276.9573 | 462.0542
277.9573 | 462.0796
278.9573 | 462.111
279.9573 | 462.021
280.9573 | 461.9291
281.9573 | 461.9925
282.9573 | 461.9366
283.9573 | 461.8653
284.9573 | 461.8384
285.9573 | 461.8538
286.9573 | 461.7821
287.9573 | 461.7306
288.9573 | 461.5614
289.9573 | 461.3525
290.9573 | 461.3192
291.9573 | 461.2006
292.9573 | 460.981
293.9573 | 460.8011
294.9573 | 460.6477
295.9573 | 460.5983
296.9573 | 460.6602
297.9573 | 460.8048
298.9573 | 460.8617
299.9573 | 460.7179
300.9573 | 460.5901
301.9573 | 460.6931
302.9573 | 460.6581
303.9573 | 460.7912
304.9573 | 460.8114
305.9573 | 460.9701
306.9573 | 461.1332
307.9573 | 461.1379
308.9573 | 461.0293
309.9573 | 461.1863
310.9573 | 461.2475
311.9573 | 461.2647
312.9573 | 461.1399
313.9573 | 461.0246
314.9573 | 461.0746
315.9573 | 461.0312
316.9573 | 460.76
317.9573 | 460.7519
318.9573 | 460.7382
319.9573 | 460.6877
320.9573 | 460.8401
321.9573 | 461.0358
322.9573 | 460.9666
323.9573 | 460.9604
324.9573 | 460.9066
325.9573 | 460.8168
326.9573 | 460.824
327.9573 | 460.7981
328.9573 | 460.7642
329.9573 | 460.5205
330.9573 | 460.3134
331.9573 | 460.2925
332.9573 | 460.454
333.9573 | 460.4469
334.9573 | 460.5225
335.9573 | 460.3579
336.9573 | 460.4423
337.9573 | 460.5161
338.9573 | 460.4371
339.9573 | 460.3817
340.9573 | 460.4117
341.9573 | 460.3886
342.9573 | 460.4514
343.9573 | 460.4779
344.9573 | 460.4502
345.9573 | 460.4729
346.9573 | 460.3888
347.9573 | 460.4404
348.9573 | 460.5058
349.9573 | 460.3783
350.9573 | 460.4628
351.9573 | 460.3579
352.9573 | 460.2505
353.9573 | 460.2482
354.9573 | 460.2802
355.9573 | 460.1364
356.9573 | 460.1046
357.9573 | 460.152
358.9573 | 460.0177
359.9573 | 460.0674
360.9573 | 460.0675
361.9573 | 459.9842
362.9573 | 459.8263
363.9573 | 459.704
364.9573 | 459.5331
365.9573 | 459.3125
366.9573 | 459.1884
367.9573 | 459.2232
368.9573 | 459.1076
369.9573 | 459.2279
370.9573 | 459.1914
371.9573 | 459.2118
372.9573 | 459.1071
373.9573 | 459.1459
374.9573 | 459.1986
375.9573 | 459.2724
376.9573 | 459.2365
377.9573 | 459.2718
378.9573 | 459.3491
379.9573 | 459.351
380.9573 | 459.3041
381.9573 | 459.0696
382.9573 | 458.974
383.9573 | 458.9228
384.9573 | 458.9832
385.9573 | 459.1148
386.9573 | 459.1658
387.9573 | 459.1611
388.9573 | 459.3617
389.9573 | 459.4292
390.9573 | 459.4701
391.9573 | 459.4738
392.9573 | 459.3068
393.9573 | 459.1023
394.9573 | 458.9485
395.9573 | 458.8579
396.9573 | 458.7806
397.9573 | 458.7575
398.9573 | 458.7292
399.9573 | 458.7538
400.9573 | 458.6278
401.9573 | 458.64
402.9573 | 458.5179
403.9573 | 458.4243
404.9573 | 458.4103
405.9573 | 458.4301
406.9573 | 458.5806
407.9573 | 458.5331
408.9573 | 458.6972
409.9573 | 458.6914
410.9573 | 458.8089
411.9573 | 458.6145
412.9573 | 458.5748
413.9573 | 458.6091
414.9573 | 458.5637
415.9573 | 458.4244
416.9573 | 458.4198
417.9573 | 458.4127
418.9573 | 458.2914
419.9573 | 458.1228
420.9573 | 458.0391
421.9573 | 458.0182
422.9573 | 457.8201
423.9573 | 457.7628
424.9573 | 457.7842
425.9573 | 457.9087
426.9573 | 457.9048
427.9573 | 458.016
428.9573 | 458.04
429.9573 | 458.098
430.9573 | 458.0505
431.9573 | 458.0461
432.9573 | 458.1884
433.9573 | 458.1052
434.9573 | 458.2525
435.9573 | 458.3882
436.9573 | 458.536
437.9573 | 458.6885
438.9573 | 458.6825
439.9573 | 458.6801
440.9573 | 458.6535
441.9573 | 458.7329
442.9573 | 458.6959
443.9573 | 458.5522
444.9573 | 458.5376
445.9573 | 458.437
446.9573 | 458.2424
447.9573 | 458.2141
448.9573 | 458.1295
449.9573 | 458.1518
450.9573 | 458.0238
451.9573 | 458.0309
452.9573 | 457.8829
453.9573 | 457.8608
454.9573 | 457.975
455.9573 | 458.1209
456.9573 | 458.1653
457.9573 | 458.2571
458.9573 | 458.4172
459.9573 | 458.4189
460.9573 | 458.327
461.9573 | 458.2228
462.9573 | 458.2106
463.9573 | 458.3764
464.9573 | 458.5235
465.9573 | 458.4929
466.9573 | 458.3822
467.9573 | 458.3972
468.9573 | 458.5153
469.9573 | 458.5017
470.9573 | 458.5622
471.9573 | 458.7019
472.9573 | 458.6347
473.9573 | 458.5471
474.9573 | 458.5129
475.9573 | 458.462
476.9573 | 458.335
477.9573 | 458.2862
478.9573 | 458.1831
479.9573 | 458.0487
480.9573 | 457.9853
481.9573 | 458.0022
482.9573 | 458.024
483.9573 | 457.9242
484.9573 | 457.9295
485.9573 | 457.8433
486.9573 | 457.9136
487.9573 | 458.0359
488.9573 | 458.1185
489.9573 | 458.1299
490.9573 | 458.0117
491.9573 | 457.9735
492.9573 | 457.831
493.9573 | 457.8532
494.9573 | 457.9471
495.9573 | 457.844
496.9573 | 457.7792
497.9573 | 457.6661
498.9573 | 457.6761
499.9573 | 457.4954
500.9573 | 457.4275
501.9573 | 457.4916
502.9573 | 457.4683
503.9573 | 457.2866
504.9573 | 457.3264
505.9573 | 457.3674
506.9573 | 457.3302
507.9573 | 457.4406
508.9573 | 457.4755
509.9573 | 457.5067
510.9573 | 457.5168
511.9573 | 457.3588
512.9573 | 457.2726
513.9573 | 457.2031
514.9573 | 457.1261
515.9573 | 457.2464
516.9573 | 457.3042
517.9573 | 457.4327
518.9573 | 457.5731
519.9573 | 457.7908
520.9573 | 457.9214
521.9573 | 458.0119
522.9573 | 458.0263
523.9573 | 458.0638
524.9573 | 458.0133
525.9573 | 457.8979
526.9573 | 457.8619
527.9573 | 457.8423
528.9573 | 457.7423
529.9573 | 457.6285
530.9573 | 457.5954
531.9573 | 457.4957
532.9573 | 457.5253
533.9573 | 457.6287
534.9573 | 457.7266
535.9573 | 457.7868
536.9573 | 457.6807
537.9573 | 457.7268
538.9573 | 457.7125
539.9573 | 457.6463
540.9573 | 457.4847
541.9573 | 457.4755
542.9573 | 457.3902
543.9573 | 457.3046
544.9573 | 457.3345
545.9573 | 457.6009
546.9573 | 457.848
547.9573 | 457.9812
548.9573 | 458.1815
549.9573 | 458.1998
550.9573 | 458.2118
551.9573 | 458.2584
552.9573 | 458.2364
553.9573 | 458.1503
554.9573 | 458.0429
555.9573 | 457.8516
556.9573 | 457.7514
557.9573 | 457.7106
558.9573 | 457.7781
559.9573 | 457.864
560.9573 | 457.7991
561.9573 | 457.7293
562.9573 | 457.5548
563.9573 | 457.3772
564.9573 | 457.2716
565.9573 | 457.1609
566.9573 | 457.1466
567.9573 | 457.2398
568.9573 | 457.1614
569.9573 | 457.1639
570.9573 | 457.2361
571.9573 | 457.204
572.9573 | 457.1841
573.9573 | 457.1346
574.9573 | 457.0677
575.9573 | 457.1391
576.9573 | 457.3258
577.9573 | 457.4313
578.9573 | 457.5022
579.9573 | 457.3696
580.9573 | 457.3506
581.9573 | 457.2339
582.9573 | 457.1128
583.9573 | 457.0718
584.9573 | 456.9051
585.9573 | 456.7798
586.9573 | 456.6644
587.9573 | 456.7935
588.9573 | 456.8251
589.9573 | 456.9015
590.9573 | 456.998
591.9573 | 456.8796
592.9573 | 456.8848
593.9573 | 456.894
594.9573 | 457.0284
595.9573 | 457.122
597.1604 | 457.1179
597.9729 | 457.1935
599.0979 | 457.2696
600.3635 | 457.0357
601.2698 | 456.9452
602.2229 | 457.0367
603.0198 | 457.1043
603.9573 | 457.1054
604.9573 | 456.9511
605.9573 | 456.7395
606.9573 | 456.7748
607.9573 | 456.7937
608.9573 | 456.873
609.9573 | 456.8951
610.9573 | 456.7254
611.9573 | 456.6458
612.9573 | 456.6163
613.9573 | 456.5473
614.9573 | 456.5106
615.9573 | 456.4491
616.9573 | 456.3962
617.9573 | 456.4961
618.9573 | 456.7561
619.9573 | 456.8232
620.9573 | 456.8408
621.9573 | 456.8359
622.9573 | 456.9505
623.9573 | 456.966
624.9573 | 456.8583
625.9573 | 456.7498
626.9573 | 456.5942
627.9573 | 456.4367
628.9573 | 456.382
629.9573 | 456.3027
630.9573 | 456.3442
631.9573 | 456.2146
632.9729 | 456.3894
633.9729 | 456.6124
635.0198 | 456.7442
635.9729 | 456.8153
636.9573 | 456.8875
637.9885 | 456.7976
638.9729 | 456.7371
639.9729 | 456.852
640.9573 | 456.9143
641.9573 | 457.0205
642.9573 | 456.9087
643.9573 | 456.7072
644.9573 | 456.7512
645.9573 | 456.6445
646.9573 | 456.5815
647.9573 | 456.49
648.9573 | 456.4328
649.9573 | 456.4326
650.9573 | 456.292
651.9573 | 456.1975
652.9573 | 456.1167
653.9573 | 456.1623
654.9573 | 456.1432
655.9573 | 456.1629
656.9573 | 456.1758
657.9573 | 456.0939
658.9573 | 456.0861
659.9573 | 456.0542
660.9573 | 456.0168
661.9573 | 456.0349
662.9573 | 456.019
663.9573 | 455.9193
664.9573 | 455.8411
665.9573 | 455.8458
666.9573 | 455.8809
667.9573 | 455.863
668.9573 | 455.7948
669.9573 | 455.6506
670.9573 | 455.6358
671.9573 | 455.6353
672.9573 | 455.7816
673.9573 | 456.039
674.9573 | 456.1041
675.9573 | 456.2903
676.9573 | 456.4687
677.9573 | 456.4277
678.9573 | 456.4624
679.9573 | 456.5851
680.9573 | 456.6771
681.9573 | 456.7004
682.9573 | 456.7535
683.9573 | 456.7555
684.9573 | 456.7933
685.9573 | 456.8572
686.9573 | 456.8555
687.9573 | 456.6561
688.9573 | 456.5556
689.9573 | 456.6464
690.9573 | 456.6247
691.9573 | 456.8163
692.9573 | 456.9795
693.9573 | 456.9925
694.9573 | 456.9509
695.9573 | 456.9364
696.9573 | 456.8327
697.9573 | 456.8595
698.9573 | 456.8107
699.9573 | 456.73
700.9573 | 456.5788
701.9573 | 456.5671
702.9573 | 456.6098
703.9573 | 456.4925
704.9573 | 456.4465
705.9573 | 456.5557
706.9573 | 456.5565
707.9573 | 456.5318
708.9573 | 456.6359
709.9573 | 456.5651
710.9573 | 456.4759
711.9573 | 456.4819
712.9573 | 456.411
713.9573 | 456.3456
714.9573 | 456.1743
715.9573 | 456.1389
716.9573 | 456.1649
717.9573 | 456.3095
718.9573 | 456.2325
719.9573 | 456.2604
720.9573 | 456.3402
721.9573 | 456.5317
722.9573 | 456.5541
723.9573 | 456.6079
724.9573 | 456.7296
725.9573 | 456.6869
726.9573 | 456.7653
727.9573 | 456.9994
728.9573 | 457.1257
729.9573 | 456.9844
730.9573 | 456.8695
731.9573 | 456.7717
732.9573 | 456.7104
733.9573 | 456.68
734.9573 | 456.6539
735.9573 | 456.6945
736.9573 | 456.7166
737.9573 | 456.6025
738.9573 | 456.5029
739.9573 | 456.5209
740.9573 | 456.5398
741.9573 | 456.4642
742.9573 | 456.2994
743.9573 | 456.4559
744.9573 | 456.2879
745.9573 | 456.1592
746.9573 | 456.2265
747.9573 | 456.2911
748.9573 | 456.4355
749.9573 | 456.4335
750.9573 | 456.3503
751.9573 | 456.352
752.9573 | 456.4055
753.9573 | 456.3999
754.9573 | 456.4237
755.9573 | 456.4366
756.9573 | 456.4671
757.9573 | 456.4282
758.9573 | 456.3665
759.9573 | 456.3782
760.9573 | 456.5628
761.9573 | 456.5925
762.9573 | 456.6939
763.9573 | 456.7884
764.9573 | 456.656
765.9573 | 456.5496
766.9573 | 456.555
767.9573 | 456.644
768.9573 | 456.754
769.9573 | 456.8706
770.9573 | 457.0356
771.9573 | 456.9679
772.9573 | 456.86
773.9573 | 456.999
774.9573 | 457.0899
775.9573 | 457.0778
776.9573 | 457.0529
777.9573 | 456.8624
778.9573 | 456.8375
779.9573 | 456.8827
780.9573 | 456.968
781.9573 | 456.8876
782.9573 | 456.8343
783.9573 | 456.6643
784.9573 | 456.7998
785.9573 | 456.9104
786.9573 | 456.9045
787.9573 | 456.8706
788.9573 | 456.8597
789.9573 | 456.9267
790.9573 | 456.8829
791.9573 | 456.7158
792.9573 | 456.7436
793.9573 | 456.8608
794.9573 | 457.1103
795.9573 | 457.1557
796.9573 | 457.0272
797.9573 | 457.0795
798.9573 | 457.1199
799.9573 | 457.1443
800.9573 | 457.1171
801.9573 | 457.0548
802.9573 | 457.1061
803.9573 | 457.0441
804.9573 | 456.9582
805.9573 | 456.8985
806.9573 | 456.8061
807.9573 | 456.6338
808.9573 | 456.5862
809.9573 | 456.539
810.9573 | 456.4202
811.9573 | 456.3806
812.9573 | 456.3719
813.9573 | 456.3855
814.9573 | 456.3634
815.9573 | 456.4606
816.9573 | 456.3969
817.9573 | 456.5006
818.9573 | 456.6007
819.9573 | 456.5933
820.9573 | 456.5905
821.9573 | 456.5161
822.9573 | 456.4921
823.9573 | 456.4748
824.9573 | 456.3799
825.9573 | 456.3603
826.9573 | 456.3514
827.9573 | 456.4206
828.9573 | 456.2811
829.9573 | 456.2269
830.9573 | 456.1083
831.9573 | 456.0331
832.9573 | 456.1484
833.9573 | 456.2454
834.9573 | 456.3916
835.9573 | 456.351
836.9573 | 456.3557
837.9573 | 456.4162
838.9573 | 456.4922
839.9573 | 456.5034
840.9573 | 456.4731
841.9573 | 456.5099
842.9573 | 456.5063
843.9573 | 456.5455
844.9573 | 456.5547
845.9573 | 456.5696
846.9573 | 456.6074
847.9573 | 456.6418
848.9573 | 456.6142
849.9573 | 456.6078
850.9573 | 456.6986
851.9573 | 456.7294
852.9573 | 456.8122
853.9573 | 456.7867
854.9573 | 456.7966
855.9573 | 456.8947
856.9573 | 456.9124
857.9573 | 456.6667
858.9573 | 456.7501
859.9573 | 456.9598
860.9573 | 457.2071
861.9573 | 457.4017
862.9573 | 457.5477
863.9573 | 457.3872
864.9573 | 457.4463
865.9573 | 457.6059
866.9573 | 457.8238
867.9573 | 457.863
868.9573 | 457.8409
869.9573 | 457.7429
870.9573 | 457.7489
871.9573 | 457.8304
872.9573 | 457.6961
873.9573 | 457.6214
874.9573 | 457.4551
875.9573 | 457.3524
876.9573 | 457.2819
877.9573 | 456.9792
878.9573 | 456.8318
879.9573 | 456.86
880.9573 | 456.9369
881.9573 | 456.8614
882.9573 | 456.6637
883.9573 | 456.5278
884.9573 | 456.5943
885.9573 | 456.567
886.9573 | 456.3396
887.9573 | 456.1364
888.9573 | 455.983
889.9573 | 455.9271
890.9573 | 456.0175
891.9573 | 456.0426
892.9573 | 455.951
893.9573 | 455.8515
894.9573 | 455.8528
895.9573 | 455.9177
896.9573 | 455.9847
897.9573 | 456.1648
898.9573 | 456.3108
899.9573 | 456.4212
900.9573 | 456.59
901.9573 | 456.454
902.9573 | 456.3823
903.9573 | 456.2124
904.9573 | 456.1132
905.9573 | 456.0787
906.9573 | 456.0563
907.9573 | 456.1232
908.9573 | 456.2144
909.9573 | 456.0824
910.9573 | 456.0516
911.9573 | 456.1307
912.9573 | 456.1581
913.9573 | 455.9573
914.9573 | 455.8802
915.9573 | 455.8334
916.9573 | 455.8642
917.9573 | 455.9239
918.9573 | 455.9142
919.9573 | 455.9352
920.9573 | 456.0014
921.9573 | 456.1485
922.9573 | 456.2203
923.9573 | 456.145
924.9573 | 456.0025
925.9573 | 455.8004
926.9573 | 455.7708
927.9573 | 455.7871
928.9573 | 455.78
929.9573 | 455.7576
930.9573 | 455.7747
931.9573 | 455.7798
932.9573 | 455.8848
933.9573 | 455.8675
934.9573 | 455.8766
935.9573 | 455.8576
936.9573 | 455.7142
937.9573 | 455.6625
938.9573 | 455.6521
939.9573 | 455.7794
940.9573 | 455.9166
941.9573 | 455.8332
942.9573 | 455.792
943.9573 | 455.9418
944.9573 | 456.0147
945.9573 | 456.1732
946.9573 | 456.2749
947.9573 | 456.2816
948.9573 | 456.219
949.9573 | 456.2543
950.9573 | 456.2971
951.9573 | 456.3281
952.9573 | 456.474
953.9573 | 456.5038
954.9573 | 456.2903
955.9573 | 456.0992
956.9573 | 455.9606
957.9573 | 455.9106
958.9573 | 455.7675
959.9573 | 455.7156
960.9573 | 455.6027
961.9573 | 455.4361
962.9573 | 455.4255
963.9573 | 455.3793
964.9573 | 455.2665
965.9573 | 455.225
966.9573 | 455.2032
967.9573 | 455.1641
968.9573 | 455.1906
969.9573 | 455.1007
970.9573 | 455.1548
971.9573 | 455.2214
972.9573 | 455.2736
973.9573 | 455.3502
974.9573 | 455.4101
975.9573 | 455.4905
976.9573 | 455.5437
977.9573 | 455.5168
978.9573 | 455.4082
979.9573 | 455.4744
980.9573 | 455.4957
981.9573 | 455.4367
982.9573 | 455.5322
983.9573 | 455.4536
984.9573 | 455.3655
985.9573 | 455.3222
986.9573 | 455.0536
987.9573 | 455.0673
988.9573 | 455.0614
989.9573 | 455.0805
990.9573 | 454.9596
991.9573 | 454.957
992.9573 | 454.9684
993.9573 | 454.9545
994.9573 | 454.9568
995.9573 | 454.9983
996.9573 | 455.0548
997.9573 | 455.0524
998.9573 | 455.0326
999.9573 | 455.2084
1000.9573 | 455.2719
1001.9573 | 455.3863
1002.9573 | 455.5243
1003.9573 | 455.5405
1004.9573 | 455.5026
1005.9573 | 455.3929
1006.9573 | 455.3779
1007.9573 | 455.3929
1008.9573 | 455.4926
1009.9573 | 455.5979
1010.9573 | 455.6932
1011.9573 | 455.8093
1012.9573 | 455.7447
1013.9573 | 455.8756
1014.9573 | 455.9061
1015.9573 | 455.8756
1016.9573 | 455.8825
1017.9573 | 455.7669
1018.9573 | 455.731
1019.9573 | 455.7931
1020.9573 | 455.8202
1021.9573 | 455.8175
1022.9573 | 455.766
1023.9573 | 455.6799
1024.9573 | 455.6586
1025.9573 | 455.7025
1026.9573 | 455.7356
1027.9573 | 455.6157
1028.9573 | 455.4358
1029.9573 | 455.4175
1030.9573 | 455.4803
1031.9573 | 455.4463
1032.9573 | 455.4166
1033.9573 | 455.4281
1034.9573 | 455.448
1035.9573 | 455.512
1036.9573 | 455.576
1037.9573 | 455.535
1038.9573 | 455.4525
1039.9573 | 455.382
1040.9573 | 455.2807
1041.9573 | 455.2062
1042.9573 | 455.2378
1043.9573 | 455.151
1044.9573 | 455.028
1045.9573 | 455.1295
1046.9573 | 455.2216
1047.9573 | 455.2854
1048.9573 | 455.2953
1049.9573 | 455.3477
1050.9573 | 455.4666
1051.9573 | 455.5499
1052.9573 | 455.5933
1053.9573 | 455.703
1054.9573 | 455.8256
1055.9573 | 455.9391
1056.9573 | 455.9789
1057.9573 | 455.9667
1058.9573 | 455.8797
1059.9573 | 455.9225
1060.9573 | 455.9479
1061.9573 | 455.7777
1062.9573 | 455.8074
1063.9573 | 455.8361
1064.9573 | 455.8335
1065.9573 | 455.7425
1066.9573 | 455.6312
1067.9573 | 455.6527
1068.9573 | 455.7319
1069.9573 | 455.753
1070.9573 | 455.6584
1071.9573 | 455.4794
1072.9573 | 455.3674
1073.9573 | 455.4544
1074.9573 | 455.41
1075.9573 | 455.4041
1076.9573 | 455.6212
1077.9573 | 455.7211
1078.9573 | 455.8616
1079.9573 | 455.9967
1080.9573 | 455.9285
1081.9573 | 455.7832
1082.9573 | 455.6213
1083.9573 | 455.5625
1084.9573 | 455.561
1085.9573 | 455.3884
1086.9573 | 455.2428
1087.9573 | 455.1706
1088.9573 | 455.0742
1089.9573 | 454.8928
1090.9573 | 454.8782
1091.9573 | 455.0255
1092.9573 | 455.0585
1093.9573 | 455.0643
1094.9573 | 455.0355
1095.9573 | 455.0588
1096.9573 | 454.991
1097.9573 | 454.9164
1098.9573 | 454.7265
1099.9573 | 454.7137
1100.9573 | 454.7695
1101.9573 | 454.8078
1102.9573 | 454.9879
1103.9573 | 455.109
1104.9573 | 455.3015
1105.9573 | 455.299
1106.9573 | 455.2642
1107.9573 | 455.2656
1108.9573 | 455.2415
1109.9573 | 455.2263
1110.9573 | 455.1825
1111.9573 | 455.0966
1112.9573 | 454.9604
1113.9573 | 454.9943
1114.9573 | 454.9009
1115.9573 | 454.9306
1116.9573 | 454.9356
1117.9573 | 455.0016
1118.9573 | 454.9897
1119.9573 | 455.1649
1120.9573 | 455.2628
1121.9573 | 455.3176
1122.9573 | 455.3391
1123.9573 | 455.3062
1124.9573 | 455.3019
1125.9573 | 455.4116
1126.9573 | 455.4469
1127.9573 | 455.4526
1128.9573 | 455.4923
1129.9573 | 455.5078
1130.9573 | 455.5609
1131.9573 | 455.653
1132.9573 | 455.6182
1133.9573 | 455.5863
1134.9573 | 455.4119
1135.9573 | 455.331
1136.9573 | 455.2566
1137.9573 | 455.3242
1138.9573 | 455.4921
1139.9573 | 455.6763
1140.9573 | 455.8082
1141.9573 | 455.7861
1142.9573 | 455.6636
1143.9573 | 455.5701
1144.9573 | 455.641
1145.9573 | 455.5788
1146.9573 | 455.4685
1147.9573 | 455.38
1148.9573 | 455.4418
1149.9573 | 455.3921
1150.9573 | 455.341
1151.9573 | 455.397
1152.9573 | 455.5536
1153.9573 | 455.6174
1154.9573 | 455.7334
1155.9573 | 455.8707
1156.9573 | 455.835
1157.9573 | 455.8609
1158.9573 | 455.8095
1159.9573 | 455.6806
1160.9573 | 455.653
1161.9573 | 455.6319
1162.9573 | 455.5856
1163.9573 | 455.5504
1164.9573 | 455.6698
1165.9573 | 455.7577
1166.9573 | 455.7277
1167.9573 | 455.7109
1168.9573 | 455.8225
1169.9573 | 455.8791
1170.9573 | 455.7207
1171.9573 | 455.5982
1172.9573 | 455.4606
1173.9573 | 455.3029
1174.9573 | 455.174
1175.9573 | 455.1088
1176.9573 | 455.0627
1177.9573 | 455.0486
1178.9573 | 455.0315
1179.9573 | 454.9431
1180.9573 | 454.8827
1181.9573 | 454.8607
1182.9573 | 454.8886
1183.9573 | 454.8369
1184.9573 | 454.7532
1185.9573 | 454.7495
1186.9573 | 454.8537
1187.9573 | 455.0151
1188.9573 | 454.9615
1189.9573 | 454.9702
1190.9573 | 454.985
1191.9573 | 454.7685
1192.9573 | 454.7302
1193.9573 | 454.7701
1194.9573 | 454.8043
1195.9573 | 454.7861
1196.9573 | 454.8135
1197.9573 | 454.9331
1198.9573 | 454.9935
1199.9573 | 455.1379
1200.9573 | 455.262
1201.9573 | 455.2761
1202.9573 | 455.2013
1203.9573 | 455.1211
1204.9573 | 455.3086
1205.9573 | 455.4698
1206.9573 | 455.6697
1207.9573 | 455.8048
1208.9573 | 456.041
1209.9573 | 456.1695
1210.9573 | 456.1774
1211.9573 | 456.2035
1212.9573 | 456.1384
1213.9573 | 456.1593
1214.9573 | 456.0856
1215.9573 | 456.0056
1216.9573 | 456.0305
1217.9573 | 456.0347
1218.9573 | 456.0202
1219.9573 | 456.0724
1220.9573 | 456.0005
1221.9573 | 455.8581
1222.9573 | 455.7608
1223.9573 | 455.6767
1224.9573 | 455.5701
1225.9573 | 455.5471
1226.9573 | 455.5958
1227.9573 | 455.3668
1228.9573 | 455.216
1229.9573 | 455.1962
1230.9573 | 455.2442
1231.9573 | 455.3257
1232.9573 | 455.3366
1233.9573 | 455.3056
1234.9573 | 455.2997
1235.9573 | 455.268
1236.9573 | 455.44
1237.9573 | 455.5053
1238.9573 | 455.5614
1239.9573 | 455.4416
1240.9573 | 455.3032
1241.9573 | 455.2661
1242.9573 | 455.2857
1243.9573 | 455.2545
1244.9573 | 455.3209
1245.9573 | 455.3973
1246.9573 | 455.516
1247.9573 | 455.5722
1248.9573 | 455.4232
1249.9573 | 455.3922
1250.9573 | 455.3847
1251.9573 | 455.4225
1252.9573 | 455.4503
1253.9573 | 455.4657
1254.9573 | 455.4292
1255.9573 | 455.4139
1256.9573 | 455.3312
1257.9573 | 455.3859
1258.9573 | 455.4876
1259.9573 | 455.4591
1260.9573 | 455.4401
1261.9573 | 455.4338
1262.9573 | 455.5486
1263.9573 | 455.5555
1264.9573 | 455.5663
1265.9573 | 455.5239
1266.9573 | 455.2636
1267.9573 | 455.1696
1268.9573 | 455.1398
1269.9573 | 455.159
1270.9573 | 455.2643
1271.9573 | 455.3626
1272.9573 | 455.4939
1273.9573 | 455.5043
1274.9573 | 455.5279
1275.9573 | 455.4757
1276.9573 | 455.3478
1277.9573 | 455.2271
1278.9573 | 455.1893
1279.9573 | 455.2811
1280.9573 | 455.375
1281.9573 | 455.3993
1282.9573 | 455.4359
1283.9573 | 455.417
1284.9573 | 455.426
1285.9573 | 455.4749
1286.9573 | 455.5569
1287.9573 | 455.6422
1288.9573 | 455.697
1289.9573 | 455.5929
1290.9573 | 455.5131
1291.9573 | 455.435
1292.9573 | 455.4418
1293.9573 | 455.4448
1294.9573 | 455.4054
1295.9573 | 455.4105
1296.9573 | 455.3714
1297.9573 | 455.3055
1298.9573 | 455.2637
1299.9573 | 455.2173
1300.9573 | 455.1455
1301.9573 | 455.0957
1302.9573 | 455.1418
1303.9573 | 455.1179
1304.9573 | 454.9434
1305.9573 | 455.0179
1306.9573 | 455.0681
1307.9573 | 455.0621
1308.9573 | 455.0829
1309.9573 | 455.1936
1310.9573 | 455.3291
1311.9573 | 455.2721
1312.9573 | 455.1299
1313.9573 | 455.0192
1314.9573 | 454.9899
1315.9573 | 454.9897
1316.9573 | 455.0168
1317.9573 | 454.8291
1318.9573 | 454.6676
1319.9573 | 454.5081
1320.9573 | 454.4591
1321.9573 | 454.5854
1322.9573 | 454.5611
1323.9573 | 454.5345
1324.9573 | 454.5593
1325.9573 | 454.4941
1326.9573 | 454.4273
1327.9573 | 454.4406
1328.9573 | 454.3378
1329.9573 | 454.2793
1330.9573 | 454.2353
1331.9573 | 454.2117
1332.9573 | 454.2482
1333.9573 | 454.2682
1334.9573 | 454.3332
1335.9573 | 454.3288
1336.9573 | 454.2608
1337.9573 | 454.1499
1338.9573 | 454.0281
1339.9573 | 453.9989
1340.9573 | 454.0087
1341.9573 | 453.97
1342.9573 | 453.9068
1343.9573 | 453.8645
1344.9573 | 453.7987
1345.9573 | 453.7871
1346.9573 | 453.8221
1347.9573 | 453.7677
1348.9573 | 453.5764
1349.9573 | 453.5252
1350.9573 | 453.3876
1351.9573 | 453.3154
1352.9573 | 453.3801
1353.9573 | 453.4386
1354.9573 | 453.415
1355.9573 | 453.5682
1356.9573 | 453.5878
1357.9573 | 453.6262
1358.9573 | 453.7536
1359.9573 | 453.9305
1360.9573 | 454.0762
1361.9573 | 454.1454
1362.9573 | 454.0495
1363.9573 | 454.0575
1364.9573 | 454.1163
1365.9573 | 454.0426
1366.9573 | 453.8158
1367.9573 | 453.6211
1368.9573 | 453.4395
1369.9573 | 453.5558
1370.9573 | 453.6705
1371.9573 | 453.6374
1372.9573 | 453.7135
1373.9573 | 453.8091
1374.9573 | 453.7292
1375.9573 | 453.6046
1376.9573 | 453.6691
1377.9573 | 453.6181
1378.9573 | 453.5192
1379.9573 | 453.614
1380.9573 | 453.7026
1381.9573 | 453.6548
1382.9573 | 453.5734
1383.9573 | 453.4107
1384.9573 | 453.2004
1385.9573 | 453.2201
1386.9573 | 453.1916
1387.9573 | 453.1246
1388.9573 | 453.1932
1389.9573 | 453.0655
1390.9573 | 452.9635
1391.9573 | 452.9667
1392.9573 | 452.9371
1393.9573 | 452.9174
1394.9573 | 452.8285
1395.9573 | 452.862
1396.9573 | 453.064
1397.9573 | 453.0967
1398.9573 | 453.0162
1399.9573 | 452.8768
1400.9573 | 452.7312
1401.9573 | 452.758
1402.9573 | 452.7139
1403.9573 | 452.6962
1404.9573 | 452.6473
1405.9573 | 452.4774
1406.9573 | 452.2374
1407.9573 | 452.1138
1408.9573 | 452.0468
1409.9573 | 452.0359
1410.9573 | 452.0839
1411.9573 | 452.0581
1412.9573 | 452.1336
1413.9573 | 452.1819
1414.9573 | 452.3386
1415.9573 | 452.3683
1416.9573 | 452.4221
1417.9573 | 452.4946
1418.9573 | 452.5006
1419.9573 | 452.5125
1420.9573 | 452.5888
1421.9573 | 452.6059
1422.9573 | 452.5624
1423.9573 | 452.4525
1424.9573 | 452.3957
1425.9573 | 452.3214
1426.9573 | 452.3212
1427.9573 | 452.2587
1428.9573 | 452.3322
1429.9573 | 452.4333
1430.9573 | 452.5586
1431.9573 | 452.4596
1432.9573 | 452.3037
1433.9573 | 452.2899
1434.9573 | 452.2933
1435.9573 | 452.3703
1436.9573 | 452.4718
1437.9573 | 452.5017
1438.9573 | 452.4178
1439.9573 | 452.3405
1440.9573 | 452.2977
1441.9573 | 452.3416
1442.9573 | 452.3811
1443.9573 | 452.3949
1444.9573 | 452.385
1445.9573 | 452.3289
1446.9573 | 452.3758
1447.9573 | 452.3796
1448.9573 | 452.4012
1449.9573 | 452.3287
1450.9573 | 452.2789
1451.9573 | 452.3061
1452.9573 | 452.2989
1453.9573 | 452.2892
1454.9573 | 452.2385
1455.9573 | 452.2534
1456.9573 | 452.2065
1457.9573 | 452.0904
1458.9573 | 452.1023
1459.9573 | 452.0927
1460.9573 | 452.1041
1461.9573 | 452.0491
1462.9573 | 452.087
1463.9573 | 452.1849
1464.9573 | 452.1969
1465.9573 | 452.1961
1466.9573 | 452.2896
1467.9573 | 452.2123
1468.9573 | 452.2296
1469.9573 | 452.1385
1470.9573 | 452.0524
1471.9573 | 452.1368
1472.9573 | 452.2629
1473.9573 | 452.3464
1474.9573 | 452.1816
1475.9573 | 452.2899
1476.9573 | 452.2942
1477.9573 | 452.2495
1478.9573 | 452.2641
1479.9573 | 452.209
1480.9573 | 452.0459
1481.9573 | 451.9534
1482.9573 | 452.0397
1483.9573 | 452.0302
1484.9573 | 452.0555
1485.9573 | 452.037
1486.9573 | 452.0074
1487.9573 | 451.9346
1488.9573 | 451.9206
1489.9573 | 451.9685
1490.9573 | 451.9103
1491.9573 | 451.7939
1492.9573 | 451.8499
1493.9573 | 451.9637
1494.9573 | 451.9984
1495.9573 | 451.9361
1496.9573 | 451.9577
1497.9573 | 452.099
1498.9573 | 452.2344
1499.9573 | 452.3509
1500.9573 | 452.3437
1501.9573 | 452.3557
1502.9573 | 452.3729
1503.9573 | 452.4318
1504.9573 | 452.4076
1505.9573 | 452.405
1506.9573 | 452.4181
1507.9573 | 452.4141
1508.9573 | 452.3315
1509.9573 | 452.3889
1510.9573 | 452.3373
1511.9573 | 452.3531
1512.9573 | 452.3726
1513.9573 | 452.1959
1514.9573 | 452.1217
1515.9573 | 452.0917
1516.9573 | 452.2059
1517.9573 | 452.3814
1518.9573 | 452.4433
1519.9573 | 452.5064
1520.9573 | 452.5151
1521.9573 | 452.5159
1522.9573 | 452.4042
1523.9573 | 452.3562
1524.9573 | 452.2096
1525.9573 | 452.1664
1526.9573 | 452.1537
1527.9573 | 452.075
1528.9573 | 451.9928
1529.9573 | 451.9918
1530.9573 | 451.9204
1531.9573 | 451.9042
1532.9573 | 451.8815
1533.9573 | 451.868
1534.9573 | 451.8161
1535.9573 | 451.6896
1536.9573 | 451.742
1537.9573 | 451.8217
1538.9573 | 451.9806
1539.9573 | 451.9951
1540.9573 | 451.9446
1541.9573 | 452.0147
1542.9573 | 452.114
1543.9573 | 452.2276
1544.9573 | 452.2938
1545.9573 | 452.3667
1546.9573 | 452.4445
1547.9573 | 452.4433
1548.9573 | 452.3748
1549.9573 | 452.4372
1550.9573 | 452.537
1551.9573 | 452.5571
1552.9573 | 452.4238
1553.9573 | 452.2984
1554.9573 | 452.1853
1555.9573 | 452.243
1556.9573 | 452.3346
1557.9573 | 452.498
1558.9573 | 452.5647
1559.9573 | 452.643
1560.9573 | 452.7474
1561.9573 | 452.6334
1562.9573 | 452.5235
1563.9729 | 452.6154
1564.9573 | 452.7415
1565.9573 | 452.9098
1566.9573 | 453.0414
1567.9573 | 453.0881
1568.9573 | 453.0915
1569.9573 | 453.0508
1570.9573 | 453.0865
1571.9573 | 453.1704
1572.9573 | 453.1491
1573.9573 | 452.9672
1574.9573 | 452.762
1575.9573 | 452.6757
1576.9573 | 452.719
1577.9573 | 452.6825
1578.9573 | 452.5779
1579.9573 | 452.597
1580.9573 | 452.6618
1581.9573 | 452.6747
1582.9573 | 452.6748
1583.9573 | 452.8167
1584.9573 | 452.8276
1585.9573 | 452.7315
1586.9573 | 452.6882
1587.9573 | 452.7179
1588.9573 | 452.7942
1589.9573 | 452.7575
1590.9573 | 452.8354
1591.9573 | 452.9478
1592.9573 | 452.87
1593.9573 | 452.8309
1594.9573 | 452.956
1595.9573 | 453.0857
1596.9573 | 453.1462
1597.9573 | 453.1533
1598.9573 | 453.0677
1599.9573 | 453.0292
1600.9573 | 453.1769
1601.9573 | 453.2611
1602.9573 | 453.1326
1603.9573 | 453.1637
1604.9573 | 453.0966
1605.9573 | 452.9981
1606.9573 | 453.0356
1607.9573 | 453.1436
1608.9573 | 453.2554
1609.9573 | 453.3556
1610.9573 | 453.2347
1611.9573 | 453.3115
1612.9573 | 453.4119
1613.9573 | 453.529
1614.9573 | 453.6117
1615.9573 | 453.6736
1616.9573 | 453.7398
1617.9573 | 453.8253
1618.9573 | 453.776
1619.9573 | 453.9261
1620.9573 | 453.9739
1621.9573 | 453.9933
1622.9573 | 453.9722
1623.9573 | 454.0013
1624.9573 | 454.0184
1625.9573 | 454.1227
1626.9573 | 454.1268
1627.9573 | 454.0835
1628.9573 | 454.0808
1629.9573 | 454.112
1630.9573 | 454.2414
1631.9573 | 454.2205
1632.9573 | 454.1698
1633.9573 | 454.1094
1634.9573 | 454.0128
1635.9573 | 453.9165
1636.9573 | 453.9368
1637.9573 | 453.933
1638.9573 | 453.8941
1639.9573 | 453.9708
1640.9573 | 453.9569
1641.9573 | 453.9957
1642.9573 | 454.0035
1643.9573 | 453.8899
1644.9573 | 453.8316
1645.9573 | 453.9291
1646.9573 | 454.0427
1647.9573 | 454.0361
1648.9573 | 454.0922
1649.9573 | 454.1086
1650.9573 | 454.1943
1651.9573 | 454.1998
1652.9573 | 454.2218
1653.9573 | 454.2356
1654.9573 | 454.2585
1655.9573 | 454.2192
1656.9573 | 454.2504
1657.9573 | 454.2675
1658.9573 | 454.3452
1659.9573 | 454.3008
1660.9573 | 454.3637
1661.9573 | 454.3392
1662.9573 | 454.1582
1663.9573 | 454.1079
1664.9573 | 454.0335
1665.9573 | 453.8619
1666.9573 | 453.7298
1667.9573 | 453.6967
1668.9573 | 453.6953
1669.9573 | 453.6861
1670.9573 | 453.7559
1671.9573 | 453.8105
1672.9573 | 453.9399
1673.9573 | 454.0412
1674.9573 | 454.0276
1675.9573 | 454.0471
1676.9573 | 454.0731
1677.9573 | 454.1155
1678.9573 | 453.9817
1679.9573 | 454.0058
1680.9573 | 454.0219
1681.9573 | 453.9827
1682.9573 | 453.875
1683.9573 | 453.8494
1684.9573 | 453.9278
1685.9573 | 453.9706
1686.9573 | 454.0422
1687.9573 | 454.0995
1688.9573 | 454.0786
1689.9573 | 453.9938
1690.9573 | 454.0228
1691.9573 | 454.0425
1692.9573 | 454.0412
1693.9573 | 454.051
1694.9573 | 454.0202
1695.9573 | 454.1035
1696.9573 | 453.9943
1697.9573 | 453.8982
1698.9573 | 453.7999
1699.9573 | 453.7049
1700.9573 | 453.6106
1701.9573 | 453.4955
1702.9573 | 453.4281
1703.9573 | 453.3633
1704.9573 | 453.3146
1705.9573 | 453.2978
1706.9573 | 453.3692
1707.9573 | 453.4718
1708.9573 | 453.5284
1709.9573 | 453.6003
1710.9573 | 453.6365
1711.9573 | 453.585
1712.9573 | 453.583
1713.9573 | 453.5831
1714.9573 | 453.7111
1715.9573 | 453.7554
1716.9573 | 453.7495
1717.9573 | 453.7527
1718.9573 | 453.7506
1719.9573 | 453.8594
1720.9573 | 453.9619
1721.9573 | 453.9782
1722.9573 | 453.9216
1723.9573 | 453.8401
1724.9573 | 453.7925
1725.9573 | 453.7661
1726.9573 | 453.7494
1727.9573 | 453.7642
1728.9573 | 453.7791
1729.9573 | 453.8039
1730.9573 | 453.835
1731.9573 | 453.8685
1732.9573 | 453.8916
1733.9573 | 454.0297
1734.9573 | 454.1456
1735.9573 | 454.084
1736.9573 | 454.0624
1737.9573 | 454.1144
1738.9573 | 454.3039
1739.9573 | 454.3561
1740.9573 | 454.31
1741.9573 | 454.4233
1742.9573 | 454.4993
1743.9573 | 454.478
1744.9573 | 454.5221
1745.9573 | 454.5773
1746.9573 | 454.5109
1747.9573 | 454.4862
1748.9573 | 454.4839
1749.9573 | 454.6263
1750.9573 | 454.6475
1751.9573 | 454.7779
1752.9573 | 454.7045
1753.9573 | 454.6303
1754.9573 | 454.7183
1755.9573 | 454.8186
1756.9573 | 454.7999
1757.9573 | 454.751
1758.9573 | 454.6872
1759.9573 | 454.8627
1760.9573 | 455.0438
1761.9573 | 455.1447
1762.9573 | 455.1535
1763.9573 | 455.2445
1764.9573 | 455.243
1765.9573 | 455.1035
1766.9573 | 454.9955
1767.9573 | 455.0666
1768.9573 | 455.0553
1769.9573 | 455.0155
1770.9573 | 454.9282
1771.9573 | 454.9195
1772.9573 | 454.8318
1773.9573 | 454.7958
1774.9573 | 454.793
1775.9573 | 454.7356
1776.9573 | 454.6914
1777.9573 | 454.636
1778.9573 | 454.6251
1779.9573 | 454.6875
1780.9573 | 454.697
1781.9573 | 454.7495
1782.9573 | 454.8294
1784.0042 | 454.89
1784.9573 | 455.0252
1785.9573 | 455.0712
1786.9573 | 455.0378
1787.9573 | 455.0355
1788.9573 | 455.0171
1789.9573 | 454.9638
1790.9573 | 454.9199
1791.9573 | 454.8556
1792.9573 | 454.914
1793.9573 | 454.9852
1794.9573 | 454.9368
1795.9573 | 454.916
1796.9573 | 454.9309
1797.9573 | 454.9318
1798.9573 | 454.9849
1799.9573 | 454.933
1800.9573 | 455.0117
1801.9573 | 455.0466
1802.9573 | 454.9602
1803.9573 | 454.9858
1804.9573 | 455.0278
1805.9573 | 455.2322
1806.9573 | 455.4025
1807.9573 | 455.4481
1808.9573 | 455.411
1809.9573 | 455.5258
1810.9573 | 455.6526
1811.9573 | 455.6131
1812.9573 | 455.5597
1813.9573 | 455.5709
1814.9573 | 455.5747
1815.9573 | 455.657
1816.9573 | 455.7109
1817.9573 | 455.7079
1818.9573 | 455.5869
1819.9573 | 455.5596
1820.9573 | 455.5872
1821.9573 | 455.6178
1822.9573 | 455.5859
1823.9573 | 455.4909
1824.9573 | 455.354
1825.9573 | 455.3205
1826.9573 | 455.2045
1827.9573 | 455.1912
1828.9573 | 455.122
1829.9573 | 455.1671
1830.9573 | 455.186
1831.9573 | 455.2138
1832.9573 | 455.2282
1833.9573 | 455.2177
1834.9573 | 455.216
1835.9573 | 455.134
1836.9573 | 455.0223
1837.9573 | 455.0098
1838.9573 | 455.0392
1839.9573 | 455.0232
1840.9573 | 455.0607
1841.9573 | 455.0101
1842.9573 | 455.0281
1843.9573 | 455.1017
1844.9573 | 455.1343
1845.9573 | 455.131
1846.9573 | 455.0788
1847.9573 | 455.0959
1848.9573 | 455.0778
1849.9573 | 455.1613
1850.9573 | 455.2013
1851.9573 | 455.2518
1852.9573 | 455.2639
1853.9573 | 455.4093
1854.9573 | 455.5502
1855.9573 | 455.6371
1856.9573 | 455.6662
1857.9573 | 455.6644
1858.9573 | 455.619
1859.9573 | 455.6226
1860.9573 | 455.7152
1861.9573 | 455.8607
1862.9573 | 455.8974
1863.9573 | 455.864
1864.9573 | 455.808
1865.9573 | 455.85
1866.9573 | 455.8971
1867.9573 | 455.9986
1868.9573 | 455.9509
1869.9573 | 455.9041
1870.9573 | 455.8982
1871.9573 | 455.8278
1872.9573 | 455.6707
1873.9573 | 455.5801
1874.9573 | 455.4625
1875.9573 | 455.4478
1876.9573 | 455.3778
1877.9573 | 455.2942
1878.9573 | 455.27
1879.9573 | 455.232
1880.9573 | 455.3274
1881.9573 | 455.426
1882.9573 | 455.4917
1883.9573 | 455.5798
1884.9573 | 455.6201
1885.9573 | 455.6394
1886.9573 | 455.5656
1887.9573 | 455.4561
1888.9573 | 455.4004
1889.9573 | 455.3425
1890.9573 | 455.2192
1891.9573 | 455.3102
1892.9573 | 455.2938
1893.9573 | 455.2979
1894.9573 | 455.4775
1895.9573 | 455.4649
1896.9573 | 455.4223
1897.9573 | 455.5187
1898.9573 | 455.4863
1899.9573 | 455.6021
1900.9573 | 455.6443
1901.9573 | 455.6646
1902.9573 | 455.5914
1903.9573 | 455.5512
1904.9573 | 455.4203
1905.9573 | 455.3821
1906.9573 | 455.4431
1907.9573 | 455.5699
1908.9573 | 455.6454
1909.9573 | 455.6041
1910.9573 | 455.6109
1911.9573 | 455.5821
1912.9573 | 455.5464
1913.9573 | 455.5042
1914.9573 | 455.3981
1915.9573 | 455.3227
1916.9573 | 455.3122
1917.9573 | 455.2434
1918.9573 | 455.2398
1919.9573 | 455.2818
1920.9573 | 455.3232
1921.9573 | 455.2855
1922.9573 | 455.1915
1923.9573 | 455.0938
1924.9573 | 455.2246
1925.9573 | 455.2737
1926.9573 | 455.2924
1927.9573 | 455.3735
1928.9573 | 455.4304
1929.9573 | 455.4562
1930.9573 | 455.4745
1931.9573 | 455.4442
1932.9573 | 455.4813
1933.9573 | 455.428
1934.9573 | 455.2981
1935.9573 | 455.3315
1936.9573 | 455.4133
1937.9573 | 455.4061
1938.9573 | 455.3892
1939.9573 | 455.3483
1940.9573 | 455.3681
1941.9573 | 455.3621
1942.9573 | 455.3537
1943.9573 | 455.3044
1944.9573 | 455.2869
1945.9573 | 455.2235
1946.9573 | 455.2921
1947.9573 | 455.3362
1948.9573 | 455.3334
1949.9573 | 455.3952
1950.9573 | 455.4444
1951.9573 | 455.3872
1952.9573 | 455.2813
1953.9573 | 455.2306
1954.9573 | 455.0535
1955.9573 | 455.1068
1956.9573 | 455.2015
1957.9573 | 455.2725
1958.9573 | 455.3411
1959.9573 | 455.4109
1960.9573 | 455.446
1961.9573 | 455.4496
1962.9573 | 455.4312
1963.9573 | 455.3791
1964.9573 | 455.349
1965.9573 | 455.1665
1966.9573 | 455.1582
1967.9573 | 455.1914
1968.9573 | 455.1805
1969.9573 | 455.1876
1970.9573 | 455.1898
1971.9573 | 455.1688
1972.9573 | 455.1723
1973.9573 | 455.1021
1974.9573 | 455.0449
1975.9573 | 454.9621
1976.9573 | 455.0203
1977.9573 | 455.0506
1978.9573 | 455.1017
1979.9573 | 455.1216
1980.9573 | 455.194
1981.9573 | 455.2109
1982.9573 | 455.2523
1983.9573 | 455.2248
1984.9573 | 455.0823
1985.9573 | 455.0736
1986.9573 | 455.21
1987.9573 | 455.2218
1988.9573 | 455.2916
1989.9573 | 455.3771
1990.9573 | 455.4686
1991.9573 | 455.5778
1992.9573 | 455.6413
1993.9573 | 455.609
1994.9573 | 455.5339
1995.9573 | 455.4854
1996.9573 | 455.4963
1997.9573 | 455.5278
1998.9573 | 455.4703
1999.9573 | 455.5361
2000.9573 | 455.5479
2001.9573 | 455.5424
2002.9573 | 455.4495
2003.9573 | 455.5046
2004.9573 | 455.5659
2005.9573 | 455.5766
2006.9573 | 455.5105
2007.9573 | 455.5955
2008.9573 | 455.6621
2009.9573 | 455.7287
2010.9573 | 455.7289
2011.9573 | 455.7266
2012.9573 | 455.7331
2013.9573 | 455.6777
2014.9573 | 455.7729
2015.9573 | 455.8179
2016.9573 | 455.7663
2017.9573 | 455.7578
2018.9573 | 455.7673
2019.9573 | 455.7429
2020.9573 | 455.7792
2021.9573 | 455.7612
2022.9573 | 455.8355
2023.9573 | 455.8361
2024.9573 | 455.9365
2025.9573 | 455.9875
2026.9573 | 455.9835
2027.9573 | 455.9301
2028.9573 | 455.8574
2029.9573 | 455.7678
2030.9573 | 455.5942
2031.9573 | 455.6563
2032.9573 | 455.6862
2033.9573 | 455.6451
2034.9573 | 455.4957
2035.9573 | 455.4525
2036.9573 | 455.452
2037.9573 | 455.5851
2038.9573 | 455.676
2039.9573 | 455.6784
2040.9573 | 455.5987
2041.9573 | 455.6997
2042.9573 | 455.7284
2043.9573 | 455.6803
2044.9573 | 455.7469
2045.9573 | 455.8601
2046.9573 | 455.9829
2047.9573 | 455.9598
2048.9573 | 455.8791
2049.9573 | 455.921
2050.9573 | 455.9193
2051.9573 | 455.8279
2052.9573 | 455.7127
2053.9573 | 455.7203
2054.9573 | 455.7871
2055.9573 | 455.8195
2056.9573 | 455.7678
2057.9573 | 455.7879
2058.9573 | 455.7465
2059.9573 | 455.6106
2060.9573 | 455.7092
2061.9573 | 455.7852
2062.9573 | 455.7493
2063.9573 | 455.7694
2064.9573 | 455.7857
2065.9573 | 455.8929
2066.9573 | 455.9181
2067.9573 | 455.8148
2068.9573 | 455.7204
2069.9573 | 455.7335
2070.9573 | 455.763
2071.9573 | 455.7522
2072.9573 | 455.7716
2073.9573 | 455.7421
2074.9573 | 455.7026
2075.9573 | 455.5909
2076.9573 | 455.7003
2077.9573 | 455.8292
2078.9573 | 455.9166
2079.9573 | 455.9418
2080.9573 | 456.0308
2081.9573 | 456.089
2082.9573 | 456.1725
2083.9573 | 456.2022
2084.9573 | 456.2209
2085.9573 | 456.2084
2086.9573 | 456.301
2087.9573 | 456.2106
2088.9573 | 456.1077
2089.9573 | 456.1211
2090.9573 | 456.1633
2091.9573 | 456.0969
2092.9573 | 455.9873
2093.9573 | 455.8631
2094.9573 | 455.8474
2095.9573 | 455.7398
2096.9573 | 455.6583
2097.9573 | 455.6921
2098.9573 | 455.7325
2099.9573 | 455.7522
2100.9573 | 455.7395
2101.9573 | 455.6838
2102.9573 | 455.772
2103.9573 | 455.8048
2104.9573 | 455.7646
2105.9573 | 455.7698
2106.9573 | 455.8225
2107.9573 | 455.8801
2108.9573 | 455.917
2109.9573 | 455.7554
2110.9573 | 455.7915
2111.9573 | 455.87
2112.9573 | 455.9095
2113.9573 | 456.0324
2114.9573 | 456.0619
2115.9573 | 456.0965
2116.9573 | 456.2205
2117.9573 | 456.2379
2118.9573 | 456.2097
2119.9573 | 456.1941
2120.9573 | 456.2245
2121.9573 | 456.2371
2122.9573 | 456.1313
2123.9573 | 455.9844
2124.9573 | 455.9399
2125.9573 | 455.961
2126.9573 | 455.8661
2127.9573 | 455.725
2128.9573 | 455.64
2129.9573 | 455.5282
2130.9573 | 455.548
2131.9573 | 455.6252
2132.9573 | 455.7785
2133.9573 | 455.8462
2134.9573 | 455.9104
2135.9573 | 455.8167
2136.9573 | 455.6131
2137.9573 | 455.5639
2138.9573 | 455.3979
2139.9573 | 455.3977
2140.9573 | 455.3173
2141.9573 | 455.3118
2142.9573 | 455.3789
2143.9573 | 455.4028
2144.9573 | 455.3788
2145.9573 | 455.4419
2146.9573 | 455.5067
2147.9573 | 455.4886
2148.9573 | 455.4976
2149.9573 | 455.4357
2150.9573 | 455.4931
2151.9573 | 455.5996
2152.9573 | 455.6651
2153.9573 | 455.7199
2154.9573 | 455.7262
2155.9573 | 455.6557
2156.9573 | 455.7383
2157.9573 | 455.8441
2158.9573 | 455.9335
2159.9573 | 455.9234
2160.9573 | 455.8354
2161.9573 | 455.805
2162.9573 | 455.7769
2163.9573 | 455.772
2164.9573 | 455.7209
2165.9573 | 455.7746
2166.9573 | 455.8966
2167.9573 | 455.8311
2168.9573 | 455.804
2169.9573 | 455.9243
2170.9573 | 455.8609
2171.9573 | 455.8576
2172.9573 | 455.9483
2173.9573 | 456.0215
2174.9573 | 455.9614
2175.9573 | 456.0854
2176.9573 | 456.0772
2177.9573 | 456.0966
2178.9573 | 456.1792
2179.9573 | 456.2534
2180.9573 | 456.3152
2181.9573 | 456.2679
2182.9573 | 456.241
2183.9573 | 456.1841
2184.9573 | 456.1081
2185.9573 | 456.1683
2186.9573 | 456.1171
2187.9573 | 456.0938
2188.9573 | 456.1021
2189.9573 | 456.1657
2190.9573 | 456.1211
2191.9573 | 456.1538
2192.9573 | 456.1199
2193.9573 | 456.0988
2194.9573 | 456.1154
2195.9573 | 456.1261
2196.9573 | 456.0658
2197.9573 | 455.8567
2198.9573 | 455.6633
2199.9573 | 455.5332
2200.9573 | 455.5941
2201.9573 | 455.6585
2202.9573 | 455.5971
2203.9573 | 455.6505
2204.9573 | 455.7211
2205.9573 | 455.6131
2206.9573 | 455.6834
2207.9573 | 455.8365
2208.9573 | 455.9239
2209.9573 | 456.0511
2210.9573 | 455.9979
2211.9573 | 456.0092
2212.9573 | 456.0172
2213.9573 | 455.9314
2214.9573 | 455.999
2215.9573 | 456.1284
2216.9573 | 456.1011
2217.9573 | 456.0509
2218.9573 | 455.9737
2219.9573 | 456.0028
2220.9573 | 456.0008