## HRR-Calculations
CHAPTER 3. ESTIMATING BURNING CHARACTERISTICS
|  |  | OF LIQUID POOL FIRE, HEAT RELEASE RATE, |  |  |  |  | Version 1805.1
|  |  | BURNING DURATION, AND FLAME HEIGHT |  |  |  |  | (English Units)
The following calculations estimate the hot gas layer temperature and smoke layer height in enclosure fire.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Fuel Spill Volume (V) |  |  |  | 5 | gallons | 0.018925 | m3
| Fuel Spill Area or Dike Area (Adike) |  |  |  | 9 | ft2 | 0.83613 | m2
| Mass Burning Rate of Fuel (m") |  |  |  | 0.078 | kg/m2-sec
| Effective Heat of Combustion of Fuel (DHc,eff) |  |  |  | 45700 | kJ/kg
| Fuel Density (r) |  |  |  | 573 | kg/m3
| Empirical Constant (kb) |  |  |  | 2.7 | m-1
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Gravitational Acceleration (g) |  |  |  | 9.81 | m/sec2
| Ambient Air Density (ra) |  |  |  | 1.1846 | kg/m3
Calculate
Note: Air density will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES DATA
BURNING RATE DATA FOR LIQUID HYDROCARBON FUELS
Fuel |  | Mass Burning Rate |  | Heat of Combustion |  | Density | Empirical Constant | Select Fuel Type
|  | m" (kg/m2-sec) |  | DHc,eff (kJ/kg) |  | r (kg/m3) | kb (m-1)
Methanol |  | 0.017 |  | 20000 |  | 796 | 100 | Scroll to desired fuel type
Ethanol |  | 0.015 |  | 26800 |  | 794 | 100 | Click on selection
Butane |  | 0.078 |  | 45700 |  | 573 | 2.7
Benzene |  | 0.085 |  | 40100 |  | 874 | 2.7
Hexane |  | 0.074 |  | 44700 |  | 650 | 1.9
Heptane |  | 0.101 |  | 44600 |  | 675 | 1.1
Xylene |  | 0.09 |  | 40800 |  | 870 | 1.4
Acetone |  | 0.041 |  | 25800 |  | 791 | 1.9
Dioxane |  | 0.018 |  | 26200 |  | 1035 | 5.4
Diethy Ether |  | 0.085 |  | 34200 |  | 714 | 0.7
Benzine |  | 0.048 |  | 44700 |  | 740 | 3.6
Gasoline |  | 0.055 |  | 43700 |  | 740 | 2.1
Kerosine |  | 0.039 |  | 43200 |  | 820 | 3.5
Diesel |  | 0.045 |  | 44400 |  | 918 | 2.1
JP-4 |  | 0.051 |  | 43500 |  | 760 | 3.6
JP-5 |  | 0.054 |  | 43000 |  | 810 | 1.6
Transformer Oil, Hydrocarbon |  | 0.039 |  | 46000 |  | 760 | 0.7
561 Silicon Transformer Fluid |  | 0.005 |  | 28100 |  | 960 | 100
Fuel Oil, Heavy |  | 0.035 |  | 39700 |  | 970 | 1.7
Crude Oil |  | 0.0335 |  | 42600 |  | 855 | 2.8
Lube Oil |  | 0.039 |  | 46000 |  | 760 | 0.7
User Specified Value |  | Enter Value |  | Enter Value |  | Enter Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-26.
ESTIMATING POOL FIRE HEAT RELEASE RATE
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-25.
Q = m"DHc,eff (1 - e-kb D) Adike
Where
| Q = | pool fire heat release rate (kW)
| m" = | mass burning rate of fuel per unit surface area (kg/m2-sec)
| DHc,eff = | effective heat of combustion of fuel (kJ/kg)
| Af = Adike = | surface area of pool fire (area involved in vaporization) (m2)
| kb = | empirical constant (m-1)
| D = | diameter of pool fire (diameter involved in vaporization, circular pool is assumed) (m)
Pool Fire Diameter Calculation
Adike = pD2/4
Where
|  | Adike = | surface area of pool fire (m2)
|  | D = | pool fire diameter (m)
D = √(4Adike/p)
|  | D = | 1.0318 | m
| Heat Release Rate Calculation |  |  | (Liquids with relatively high flash point, like transformer oil, require
localized heating to achieve ignition)
Q = m"DHc,eff (1-e-kb D) Adike
|  | Q = | 2650.7034 | Btu/sec |  | 2796.6317 | kW
ESTIMATING POOL FIRE BURNING DURATION
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 3-197.
tb = 4V / pD2n
Where
| tb = | burning duration of pool fire (sec)
| V = | volume of liquid (m3)
| D = | pool diameter (m)
| n = | regression rate (m/sec)
Calculation for Regression Rate
n = m"/r
Where
|  | n = | regression rate (m/sec)
|  | m" = | mass burning rate of fuel (kg/m2-sec)
|  | r = | liquid fuel density (kg/m3)
|  | n = | 0.00013613 | m/sec
Burning Duration Calculation
tb = 4V/pD2n
|  | tb = | 166.2737 | sec | 2.7712 | minutes
Note that a liquid pool fire with a given amount of fuel can burn for long periods of time over small area or for
short periods of time over a large area.
ESTIMATING POOL FIRE FLAME HEIGHT
METHOD OF HESKESTAD
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 2-10.
Hf = 0.235 Q2/5 - 1.02 D
Where
| Hf = | pool fire flame height (m)
| Q = | pool fire heat release rate (kW)
| D = | pool fire diameter (m)
Pool Fire Flame Height Calculation
Hf = 0.235 Q2/5 - 1.02 D
| Hf = | 14.9849 | ft | 4.5674 | m
METHOD OF THOMAS
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 3-204.
Hf = 42 D (m"/ra √(g D))0.61
Where
| Hf = | pool fire flame height (m)
| m" = | mass burning rate of fuel per unit surface area (kg/m2-sec)
| ra = | ambient air density (kg/m3)
| D = | pool fire diameter (m)
| g = | gravitational acceleration (m/sec2)
Pool Fire Flame Height Calculation
Hf = 42 D (m"/(ra √(g D)))0.61
| Hf = | 13.3514 | ft | 4.0695 | m
Summary of Results
Heat Release Rate Calculation |  |  |  | (Liquids with relatively high flash point, like transformer oil, require
localized heating to achieve ignition)
Q = m"DHc,eff (1-e-kb D) Adike
Answer | Q= | 2650.7034 |  | Btu/sec | 2796.6317 |  | kW
Burning Duration Calculation
tb = 4V/pD2n
Answer | tb= | 166.2737 | sec |  | 2.7712 | minutes
Flame Height Calculation
| Method of Heskestad |  |  |  | Method of Thomas
| Hf = 0.235 Q2/5 - 1.02 D |  |  |  | Hf = 42 D (m"/(ra √(g D)))0.61
Answer | METHOD OF HESKESTAD |  | 14.9849 | ft
| METHOD OF THOMAS |  | 13.3514 | ft
ESTIMATING POOL FIRE RESULTS FOR RANDOM SIZE SPILLS USING INPUT PARAMETERS
Area (ft2) | Area (m2) | Diameter (m) | Q (kW) | tb (sec) | Hf (ft) (Heskestad) | Hf (ft) (Thomas)
1 | 0.092903 | 0.34393 | 200.3193 | 1496.463 | 5.2721 | 6.222
2 | 0.18581 | 0.48639 | 484.1966 | 748.2315 | 7.5147 | 7.9166
3 | 0.27871 | 0.5957 | 794.5831 | 498.821 | 9.1522 | 9.1144
4 | 0.37161 | 0.68786 | 1117.8635 | 374.1157 | 10.4745 | 10.0727
5 | 0.46452 | 0.76905 | 1448.2117 | 299.2926 | 11.5969 | 10.8848
6 | 0.55742 | 0.84245 | 1782.6413 | 249.4105 | 12.5793 | 11.5968
7 | 0.65032 | 0.90995 | 2119.4653 | 213.7804 | 13.4571 | 12.2349
8 | 0.74322 | 0.97278 | 2457.6722 | 187.0579 | 14.2537 | 12.816
9 | 0.83613 | 1.0318 | 2796.6317 | 166.2737 | 14.9849 | 13.3514
10 | 0.92903 | 1.0876 | 3135.9411 | 149.6463 | 15.6623 | 13.8493
11 | 1.0219 | 1.1407 | 3475.3399 | 136.0421 | 16.2946 | 14.3157
12 | 1.1148 | 1.1914 | 3814.6584 | 124.7052 | 16.8884 | 14.7552
13 | 1.2077 | 1.2401 | 4153.7873 | 115.1125 | 17.4491 | 15.1714
14 | 1.3006 | 1.2869 | 4492.6575 | 106.8902 | 17.9807 | 15.5671
15 | 1.3935 | 1.332 | 4831.2273 | 99.7642 | 18.4868 | 15.9449
20 | 1.8581 | 1.5381 | 6519.1316 | 74.8231 | 20.7188 | 17.6213
25 | 2.3226 | 1.7196 | 8199.3417 | 59.8585 | 22.596 | 19.042
50 | 4.6452 | 2.432 | 16534.811 | 29.9293 | 29.3945 | 24.2282
75 | 6.9677 | 2.9785 | 24829.174 | 19.9528 | 34.1934 | 27.8941
100 | 9.2903 | 3.4393 | 33113.1477 | 14.9646 | 38.0416 | 30.8268
NOTE:
The above calculations are based on principles developed in the Structural Design for Fire Safety, 2001. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  |  | Organization:
Checked by: |  |  |  | Date: |  |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Corrected diameter reference in Q calculation column in table. Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  | March 2011
Note on F25: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Caution! The purpose of this random spill size chart is to aid the user in evaluating the hazard of random sized spills. Please note that the calculation does not take into account the viscosity or volatility of the liquid, or the absorptivity of the surface. The results generated for small volume spills over large areas should be used with extreme caution.