## Ignition_Time_Calculations1
CHAPTER 6
ESTIMATING THE IGNITION TIME
|  | OF A TARGET FUEL | [5 empty] | Version 1805.1
|  | EXPOSED TO A CONSTANT RADIATIVE HEAT FLUX | [5 empty] | (English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Material Ignition Temperature (Tig) |  |  |  | 412 | °C
| Material Thermal Inertia (krc) |  |  |  | 0.93 | (kW/m2-K)2-sec
| Material Critical Heat Flux for Ignition (q"critical) |  |  |  | 18 | kW/m2
| Flame Spread Parameter b |  |  |  | 0.05 | (s)-1/2
| Exposure or External Radiative Heat Flux (q"e) |  |  |  | 20 | kW/m2
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
| Heat Transfer Coefficient at Ignition (hig) |  |  |  | 0.0275 | kW/m2-K
Calculate
FLAME SPREAD PROPERTIES OF COMMON MATERIALS
| Materials | Ignition Temp. | Thermal Inertia | Critical Heat Flux for | Flame Spread | Select Material
|  | Tig (°C) | krc (kW/m2-K)2-sec | Ignition q"critical (kW/m2) | Parameter b (s)-1/2
| PMMA Polycast (1.59 mm) | 278 | 0.73 | 9 | 0.04 | Scroll to desired material then
| Hardboard (6.35 mm) | 298 | 1.87 | 10 | 0.03 | Click on selection
| Carpet (Acrylic) | 300 | 0.42 | 10 | 0.06
| Fiber Insulation Board | 355 | 0.46 | 14 | 0.07
| Hardboard (3.175 mm) | 365 | 0.88 | 14 | 0.05
| PMMA Type G (1.27 cm) | 378 | 1.02 | 15 | 0.05
| Asphalt Shingle | 378 | 0.7 | 15 | 0.06
| Douglas Fire Particle Board (1.27 cm) | 382 | 0.94 | 16 | 0.05
| Plywood Plain (1.27 cm) | 390 | 0.54 | 16 | 0.07
| Plywood Plain (0.635 cm) | 390 | 0.46 | 16 | 0.07
| Foam Flexible (2.54 cm) | 390 | 0.32 | 16 | 0.09
| GRP (2.24 mm) | 390 | 0.32 | 16 | 0.09
| Hardboard (Gloss Paint) (3.4 mm) | 400 | 1.22 | 17 | 0.05
| Hardboard Nitrocellulose Paint) | 400 | 0.79 | 17 | 0.06
| GRP (1.14 mm) | 400 | 0.72 | 17 | 0.06
| Particle Board (1.27 cm Stock) | 412 | 0.93 | 18 | 0.05
| Carpet (Nylon/Wool Blend) | 412 | 0.68 | 18 | 0.06
| Gypsum Board, Wallboard (S142M) | 412 | 0.57 | 18 | 0.07
| Carpet # 2 (Wool Untreated) | 435 | 0.25 | 20 | 0.11
| Foam Rigid (2.54 cm) | 435 | 0.03 | 20 | 0.32
| Fiberglass Shingle | 445 | 0.5 | 21 | 0.08
| Polyisoyanurate (5.08 cm) | 445 | 0.02 | 21 | 0.36
| Carpet # 2 (Wool Treated) | 455 | 0.24 | 22 | 0.12
| Carpet # 1 (Wool, Stock) | 465 | 0.11 | 23 | 0.18
| Aircraft Panel Expoxy Fiberite | 505 | 0.24 | 28 | 0.13
| Gypsum Board FR (1.27 cm) | 510 | 0.4 | 28 | 0.1
| Polycarbonate (1.52 mm) | 528 | 1.16 | 30 | 0.06
| Gypsum Board (Common) (1.27 mm) | 565 | 0.45 | 35 | 0.11
| Plywood FR (1.27 cm) | 620 | 0.76 | 44 | 0.1
| Polystyrene (5.08 cm) | 630 | 0.38 | 46 | 0.14
| User Specified Value | Enter Value | Enter Value | Enter Value | Enter Value
Reference: SFPE Engineering Guide, "Piloted Ignition of Solid Materials Under Radiant Exposure," 2002, Page 14.
METHOD OF MIKKOLA AND WICHMAN
THERMALLY THICK MATERIALS
| Reference: SFPE Engineering Guide, "Piloted Ignition of Solid Materials Under Radiant Exposure," 2002, Page 7. |  |  |  |  | STOP - DO NOT USE THIS WORKSHEET IF HOT
GAS LAYER TEMPERATURE EXCEED 1112 °F
tig = p/4 krc (Tig - Ta)2 / (qe" - qcritical")2
Where
| tig = | material ignition time (sec)
| krc = | material thermal inertia (kW/m2-K)2-sec
| Tig = | material ignition temperature (°C)
| Ta = | ambient air temperature (°C)
| qe" = | exposure or external radiative heat flux (kW/m2)
| q"critical = | material critical heat flux for ignition (kW/m2)
tig = p/4 krc (Tig - Ta)2 / (qe" - qcritical")2
Answer | tig = | 27348.5791 | sec | 455.8097 | minute
METHOD OF QUINTIERE AND HARKLEROAD
THERMALLY THICK MATERIALS
Reference: SFPE Engineering Guide, "Piloted Ignition of Solid Materials Under Radiant Exposure," 2002, Page 12.
tig = (qcritical" / b qe")2
Where
| tig = | material ignition time (sec)
| q"critical = | material critical heat flux for ignition (kW/m2)
| b = | flame spread parameter (s)-1/2
| qe" = | exposure or external radiative heat flux (kW/m2)
tig = (qcritical" / b qe")2
Answer | tig = | 324 | sec | 5.4 | minute
METHOD OF JANSSENS
THERMALLY THICK MATERIALS
Reference: SFPE Engineering Guide, "Piloted Ignition of Solid Materials Under Radiant Exposure," 2002, Page 15.
tig = 0.563 (krc / hig2) ((qe" / qcritical")-1)-1.83
Where
| tig = | material ignition time (sec)
| krc = | material thermal inertia (kW/m2-K)2-sec
| hig = | heat transfer coefficient at ignition (kW/m2-K)
| qe" = | exposure or external radiative heat flux (kW/m2)
| q"critical = | material critical heat flux for ignition (kW/m2)
tig = 0.563 (krc / hig2) ((qe" / qcritical")-1)-1.83
Answer | tig = | 38600.2172 | sec | 643.337 | minute
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print paginationand print layout. |  |  |  | March 2011
Note on F25: This default value (0.0275) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Ignition_Time_Calculations2
CHAPTER 6
ESTIMATING THE IGNITION TIME
|  | OF A TARGET FUEL |  |  |  |  | Version 1805.1
|  | EXPOSED TO A CONSTANT RADIATIVE HEAT FLUX |  |  |  |  | (English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Material Flux Time Product (FTP) |  |  |  | 9332 | (kW-sec/m2)n
| Material Critical Heat Flux for Ignition (q"critical) |  |  |  | 8.1 | kW/m2
| Flux Time Product Index (n) |  |  |  | 1.51
| Exposure or External Radiative Heat Flux (q"r) |  |  |  | 20 | kW/m2
Calculate
FLAME SPREAD PROPERTIES OF COMMON MATERIALS
| Materials | Flux Time Product (FTP) | Critical Heat Flux for Ignition | Flux Time Product | Select Material
|  | (kW-sec/m2)n | q"critical (kW/m2) | Index n
| Chipboard | 5370 | 6.4 | 1.49 | Scroll to desired material then
| Chipboard (Horizontal) (15 mm) | 9921 | 9 | 1.7 | Click on selection
| Chipboard (Vertical) (15 mm) | 11071 | 10 | 1.7
| Fiberboard | 3981 | 8.3 | 1.66
| Hardboard | 8127 | 8.1 | 1.49
| Hardboard (Painted Gloss) | 9332 | 8.1 | 1.51
| Hardwood | 2818 | 8.1 | 1.5
| Plywood | 6164 | 10.6 | 1.51
| Plywood (Horizontal) (12 mm) | 5409 | 8.5 | 1.5
| Plywood (Vertical) (12 mm) | 42025 | 10 | 2
| Plywood (Painted Gloss) | 6761 | 11.4 | 1.5
| PMMA (cast) (3 mm) | 3100 | 5 | 1.25
| PMMA (extruded) (2 mm) | 1290 | 9 | 1
| Polyethylene (2 mm) | 2220 | 12.5 | 1
| Polypropylene (3.3 mm) | 8110 | 6.5 | 1.5
| PVC (Extruded Gray) (3 mm) | 5130 | 15 | 1.5
| PVC (Pressed White) (3 mm) | 95000 | 8 | 2
| Softwood | 5130 | 13.7 | 1.53
| Softwood (Horizontal) (20 mm) | 44079 | 10 | 2.2
| Softwood (Vertical) (20 mm) | 16502 | 12 | 1.9
| Softwood Intumescent Paint | 4569 | 13 | 1.5
| User Specified Value | Enter Value | Enter Value | Enter Value
Reference: SFPE Engineering Guide, "Piloted Ignition of Solid Materials Under Radiant Exposure," 2002, Page 20.
METHOD OF TOAL, SILCOCK AND SHIELDS
THERMALLY THICK MATERIALS
Reference: SFPE Engineering Guide, "Piloted Ignition of Solid Materials Under Radiant Exposure," 2002, Page 17.
tig = FTPn / (qr" - q"critical)n
Where
| tig = | material ignition time (sec)
| FTPn = | flux time product (kW-sec/m2)n for the given index
| qr" = | exposure or external heat flux (kW/m2)
| q"critical = | material critical heat flux for ignition (kW/m2)
| n = | flux time product index (n ≥ 1)
tig = FTPn / (qr" - q"critical)n
Answer | tig = | 221.768 | sec | 3.6961 | minute
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print paginationand print layout. |  |  |  | March 2011

## Ignition_Time_Calculations3
CHAPTER 6
ESTIMATING THE IGNITION TIME
| OF A TARGET FUEL | [5 empty] | Version 1805.1
| EXPOSED TO A CONSTANT RADIATIVE HEAT FLUX | [5 empty] | (English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Exposure or External Radiative Heat Flux to Target Fuel (q"e) |  | 25 | kW/m2 |  | STOP - This value must be greater than CHF
| Target Critical Heat Flux for Ignition (CHF) |  | 19 | kW/m2
| Target Thermal Response Parameter (TRP) |  | 248.5 | kW-sec1/2/m2
Calculate
CRITICAL HEAT FLUX AND THERMAL RESPONSE PARAMETER FOR MATERIALS
| Materials | Critical Heat Flux for Ignition | Thermal Response Parameter (TRP)
|  | CHF (kW/m2) | (kW-sec1/2/m2)
| PVC/PVC | 19 | 248.5 | Select Material
| PE/PVC | 15 | 232.5
| PVC/PE | 15 | 263 | Scroll to desired material then
| Silicone/PVC | 19 | 212 | Click on selection
| Silicone/crosslinked polyolefin (XLPO) | 27.5 | 446
| EPR (ethylene-propylene rubber/EPR) | 21.5 | 517
| XLPE/XLPE | 22.5 | 329.5
| XLPE/EVA (ethyl-vinyl acetate) | 17 | 472.5
| XLPE/Neoprene | 15 | 291
| XLPO/XLPO | 20.5 | 498
| XLPO, PVF (polyvinylidine fluoride)/XLPO | 15.5 | 526
| EPR/Chlorosulfonated PE | 16.5 | 349.5
| EPR, FR | 21 | 368.5
| User Specified Value | Enter Value | Enter Value
Select Material
| PVC/PVC | 15 | 131
| PE/PVC | 20 | 183 | Scroll to desired material then
| XLPE/XLOP | 20 | 498 | Click on selection
| Si/XLOP | 20 | 457
| EPR-FR | 19 | 295
| Chlorinated PE | 12 | 217
| ETFE/EVA | 22 | 454
| PVC/PVF | 30 | 264
| FEP/FEP | 36 | 645
| User Specified Value | Enter Value | Enter Value
Select Material
| Polypropylene | 15 | 193
| Nylon | 15 | 270 | Scroll to desired material then
| Polymethylmethacrylate (PMMA) | 11 | 274 | Click on selection
| Polycarbonate | 15 | 331
| Polycarbonate panel | 16 | 420
| User Specified Value | Enter Value | Enter Value
Select Material
| Wood (red oak) | 10 | 134
| Wood (douglas fir) | 10 | 138 | Scroll to desired material then
| Wood (douglas fir/fire retardant, FR) | 10 | 251 | Click on selection
| Corrugated paper (light) | 10 | 152
| User Specified Value | Enter Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 3-58.
ESTIMATING IGNITION TIME FOR COMBUSTIBLES
METHOD OF TEWARSON
THERMALLY THICK MATERIALS
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-83.
√(1/tig) = (√(4/p) (q"e - CHF))/TRP
tig = (p/4) (TRP)2/(q"e - CHF)2
Where
| tig = | target ignition time (sec)
| q"e = | external radiative heat flux to target (kW/m2)
| CHF = | target critical heat flux for ignition (kW/m2)
| TRP = | thermal response parameter of target material (kW-sec2/m2)
tig = (p/4) (TRP)2/(q"e - CHF)2
Answer | tig = | 1347.2251 | sec | 22.4538 | minutes
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print paginationand print layout. |  |  |  | March 2011