## Cable HRR Calculations
CHAPTER 7
ESTIMATING THE FULL-SCALE
|  | HEAT RELEASE RATE OF A | [5 empty] | Version 1805.1
|  | CABLE TRAY FIRE | [5 empty] | (SI Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Cable Bench-Scale HRR (Qbs'') |  |  |  | 1071 | kW/m2
| Exposed Floor Area (Length x Width) of Burning Cable Tray (Af) |  |  |  | 1.951 | m2 |  | 1.951 | m2
Calculate
HEAT RELEASE RATE DATA FOR CABLE TRAY FIRE
BENCH-SCALE HRR OF CABLE TRAY FIRE
| Cable Type |  |  | Bench-Scale HRR per |  |  | Select Cable Type
Unit Floor Area (L x W)
|  |  |  | Q"bs (kW/m2) |  |  | Scroll to desired cable type then
| FRXPE/Cl.S.PE |  |  | 258 |  |  | Click on selection
| ld PE |  |  | 1071
| PE, Nylon/PVC, Nylon |  |  | 231
| PE, Nylon/PVC, Nylon |  |  | 218
| PE, PP/Cl.S.PE |  |  | 345
| PE, PP/Cl.S.PE |  |  | 299
| PE, PP/Cl.S.PE |  |  | 271
| PE, PP/Cl.S.PE |  |  | 177
| PE/PVC |  |  | 589
| PE/PVC |  |  | 395
| PE/PVC |  |  | 359
| PE/PVC |  |  | 312
| Silicone, glass braid |  |  | 128
| Silicone, glass braid, asbestos |  |  | 182
| Teflon |  |  | 98
| XPE/Cl.S.PE |  |  | 204
| XPE/FRXPE |  |  | 475
| XPE/Neoprene |  |  | 354
| XPE/Neoprene |  |  | 302
| XPE/XPE |  |  | 178
| User Specified Value |  |  | Enter Value
Reference: "Categorization of Cable Flammability, Part 1: Laboratory Evaluation of Cable Flammability Parameters," EPRI Research Project 1165-1, NP-1200, Part 1.
ESTIMATING FULL-SCALE CABLE TRAY HEAT RELEASE RATE
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition 2002, Page 3-16.
Qfs = |  | 0.45 Qbs'' Af
Where,
Qfs = |  | cable tray full-scale HRR (kW)
Qbs'' = |  | cable tray bench-scale HRR (kW/m2)
Af = |  | exposed floor area (length x width) of burning cable tray (m2)
Heat Release Rate Calculation
Qfs = |  | 0.45 Qbs Af
Answer | Qfs = | 940.2844 |  |  | kW | 891.2204 |  | Btu/sec
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  | Date: |  | Organization:
Checked by: |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011