## Smoke_Detector
CHAPTER 10
ESTIMATING SPRINKLER RESPONSE TIME
Version 1805.1
(English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Heat Release Rate of the Fire (Q) (Steady State) |  |  |  | 1000 | kW | 947.82 | Btu/sec
| Radial Distance to the Detector (r) **never more than 0.707 or 1/2√2 of the listed spacing** |  |  |  | 10 | ft | 3.048 | m
| Height of Ceiling above Top of Fuel (H) |  |  |  | 13 | ft | 3.9624 | m
| Activation Temperature of the Smoke Detector (Tactivation) |  |  |  | 86 | °F | 30 | °C
| Smoke Detector Response Time Index (RTI) |  |  |  | 5 | (m-sec)1/2
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Convective Heat Release Rate Fraction (cc) |  |  |  | 0.7
| Plume Leg Time Constant (Cpl) (Experimentally Determined) |  |  |  | 0.67
| Ceiling Jet Lag Time Constant (Ccj) (Experimentally Determined) |  |  |  | 1.2
| Temperature Rise of Gases Under the Ceiling (DTc) |  |  |  | 18 | °F | 10 | °C
for Smoke Detector to Activate
| r/H = | 0.76923
Calculate
ESTIMATING SMOKE DETECTOR RESPONSE TIME
METHOD OF ALPERT
Reference: NFPA Fire Protection Handbook, 19th Edition, 2003, Page 3-140.
tactivation = (RTI/(√ujet)) (ln ((Tjet - Ta)/(Tjet - Tactivation)))
This method assume smoke detector is a low RTI device with a fixed activation temperature
Where
|  | tactivation = | detector activation time (sec)
|  | RTI = | detector response time index (m-sec)1/2
|  | ujet = | ceiling jet velocity (m/sec)
|  | Tjet = | ceiling jet temperature (°C)
|  | Ta = | ambient air temperature (°C)
|  | Tactivation = | activation temperature of detector (°C)
Ceiling Jet Temperature Calculation
|  |  | Tjet - Ta = 16.9 (Q)2/3/H5/3 |  |  | for r/H ≤ 0.18
|  |  | Tjet - Ta = 5.38 (Q/r)2/3/H |  |  | for r/H > 0.18
Where
|  |  | Tjet = | ceiling jet temperature (°C)
|  |  | Ta = | ambient air temperature (°C)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | H = | height of ceiling above top of fuel (m)
|  |  | r = | radial distance from the plume centerline to the detector (m)
Convective Heat Release Rate Calculation
Qc = cc Q
Where
|  |  | Qc = | convective portion of the heat release rate (kW)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | cc = | convective heat release rate fraction
|  |  | Qc = | 700 | kW
Radial Distance to Ceiling Height Ratio Calculation
|  |  | r/H = | 0.76923 | r/H > 0.18
|  |  | >0.18 | 64.5873 | <0.18 | 170.3294
|  |  | Tjet - Ta = | 5.38 ((Q/r)^2/3)/H
|  |  | Tjet - Ta = | 64.5873
|  |  | Tjet = | 89.5873 | (°C)
Ceiling Jet Velocity Calculation
|  |  | ujet = 0.96 (Q/H)1/3 |  |  | for r/H ≤ 0.15
|  |  | ujet = (0.195 Q1/3 H1/2)/r5/6 |  |  | for r/H > 0.15
Where
|  |  | ujet = | ceiling jet velocity (m/sec)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | H = | height of ceiling above top of fuel (m)
|  |  | r = | radial distance from the plume centerline to the detector (m)
Radial Distance to Ceiling Height Ratio Calculation
|  |  | r/H = | 0.76923 | r/H > 0.15
|  |  | >0.15 | 1.5334 | <0.15 | 6.0667
|  |  | ujet = | (0.195 Q^1/3 H^1/2)/r^(5/6)
|  |  | ujet = | 1.5334 | m/sec
Smoke Detector Response Time Calculation
tactivation = (RTI/(√ujet)) (ln (Tjet - Ta)/(Tjet - Tactivation))
|  |  | tactivation = | 0.32534 | sec
NOTE: If tactivation = "NUM" Detector does not activate
METHOD OF MOWRER
References: Mowrer, F., "Lag Times Associated With Fire Detection and Suppression," Fire Technology, August 1990, p. 244.
tactivation = tpl + tcj
Where
|  | tactivation = | detector activation time (sec)
|  | tpl = | transport lag time of plume (sec)
|  | tcj = | transport lag time of ceiling jet (sec)
Transport Lag Time of Plume Calculation
tpl = Cpl (H)4/3/(Q)1/3
Where
|  |  | tpl = | tpl = transport lag time of plume (sec)
|  |  | Cpl = | Cpl = plume lag time constant
|  |  | H = | H = height of ceiling above top of fuel (m)
|  |  | Q = | Q = heat release rate of the fire (kW)
|  |  | tpl = | 0.4201 | sec
Transport Lag Time of Ceiling Jet Calculation
tcj = (r)11/6/(Ccj) (Q)1/3 (H)1/2
Where
|  |  | tcj = | tcj = transport lag time of ceiling jet (sec)
|  |  | Ccj = | Ccj = ceiling jet lag time constant
|  |  | r = | r = radial distance from the plume centerline to the detector (m)
|  |  | H = | H = height of ceiling above top of fuel (m)
|  |  | Q = | Q = heat release rate of the fire (kW)
|  |  | tcj = | 0.323 | sec
Smoke Detector Response Time Calculation
tactivation = tpl + tcj
|  |  | tactivation = | 0.7431 | sec
METHOD OF MILKE
References: Milke, J., "Smoke Management for Covered Malls and Atria," Fire Technology, August 1990, p. 223.
NFPA 92B, "Guide for Smoke Management Systems in Mall, Atria, and Large Areas," 2000 Edition, Section A.3.4.
tactivation = X H4/3/Q1/3
Where
|  | tactivation = | detector activation time (sec)
|  | X = | 4.6 10-4 Y2 + 2.7 10-15 Y6
|  | H = | height of ceiling above top of fuel (ft)
|  | Q = | heat release rate from steady fire (Btu/sec)
Where
|  | Y = | Y = DTc H5/3 / Q2/3
|  | DTc = | DTc = temperature rise of gases under the ceiling for smoke detector to activate (°F)
Before estimating smoke detector response time, stratification effects can be calculated.
NFPA 92B, 2000 Edition, Section A.3.4 provides following correlation to estimate smoke
stratification in a compartment.
Hmax = 74 Qc2/5 / DTf->c3/5
Where
|  |  | Hmax = | Hmax = the maximum ceiling clearance to which a plume can rise (ft)
|  |  | Qc = | Qc = convective portion of the heat release rate (Btu/sec)
|  |  | DTf->c = | DTf->c = difference in temperature due to fire between the fuel location and ceiling level (°F)
Convective Heat Release Rate Calculation
Qc = Q cc
Where
|  |  | Qc = | convective portion of the heat release rate (Btu/sec)
|  |  | Q = | heat release rate of the fire (Btu/sec)
|  |  | cc = | convective heat releas rate fraction
|  |  | Qc = | 663.474 | Btu/sec
Difference in Temperature Due to Fire Between the Fuel Location and Ceiling Level
DTf->c = 1300 Qc2/3 / H5/3
Where
|  |  | DTf->c = | difference in temperature due to fire between the fuel location and ceiling level (°F)
|  |  | Qc = | convective portion of the heat release rate (Btu/sec)
|  |  | H = | ceiling height above the fire source (ft)
|  |  | DTf->c = | 1375.9005 | °F
Smoke Stratification Effects
Hmax = 74 Qc2/5 / DTf->c3/5
|  |  | Hmax = | 13.0259 | ft
|  | In this case the highest point of smoke rise is estimated to be |  |  | 13.0259 | ft
Thus, the smoke would be expected to reach the ceiling mounted smoke detector.
Y = DTc H5/3 / Q2/3
|  | Y = | 13.4079
X = 4.6 10-4 Y2 + 2.7 10-15 Y6
|  | X = | 0.082695
Smoke Detector Response Time Calculation
tactivation = X H4/3/Q1/3
|  | tactivation = | 0.25733 | sec
| Calculation Method |  | Smoke Detector Response Time (sec)
Summary of Results | METHOD OF ALPERT |  | 0.32534
| METHOD OF MOWRER |  | 0.7431
| METHOD OF MILKE |  | 0.25733
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [5 empty] | Date
1805.0 | Original issue with final text. | [5 empty] | December 2004
1805.1 | Changed references from Qc to Q and 0.15 to 0.18 in cells B37, B38 B55, C41, C57, | [5 empty] | March 2011
D53, D55, E37, and E38, as appropriate and changed calculations in cells C55, C58,
and E 55. Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout.
Note on F23: This default value (86 °F) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F24: This default value (5.0) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F27: This default value (0.70) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F30: This default value (18 °F) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Sprinkler
CHAPTER 10
ESTIMATING SPRINKLER RESPONSE TIME
Version 1805.1
(English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Heat Release Rate of the Fire (Q) (Steady State) |  |  |  | 1000 | kW
| Sprinkler Response Time Index (RTI) |  |  |  | 130 | (m-sec)1/2
| Activation Temperature of the Sprinkler (Tactivation) |  |  |  | 550 | °F | 287.7778 | °C
| Height of Ceiling above Top of Fuel (H) |  |  |  | 9.8 | ft | 2.987 | m
| Radial Distance to the Detector (r) **never more than 0.707 or 1/2√2 of the listed spacing** |  |  |  | 9.8 | ft | 2.987 | m
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Convective Heat Release Rate Fraction (cc) |  |  |  | 0.7
| r/H = | 1 |  |  | Calculate
GENERIC SPRINKLER RESPONSE TIME INDEX (RTI)*
| Common Sprinkler Type |  | Generic Response | Select Type of Sprinkler
Time Index (RTI) (m-sec)1/2
| Standard response bulb |  | 235 | Scroll to desired sprinkler type then Click on selection
| Standard response link |  | 130
| Quick response bulb |  | 42
| Quick response link |  | 34
| User Specified Value |  | Enter Value
Reference: Madrzykowski, D., "Evaluation of Sprinkler Activation Prediction Methods"
ASIAFLAM'95, International Conference on Fire Science and Engineering, 1st Proceeding,
March 15-16, 1995, Kowloon, Hong Kong, pp. 211-218.
*Note: The actual RTI should be used when the value is available.
GENERIC SPRINKLER TEMPERATURE RATING (Tactivation)*
| Temperature Classification |  | Range of Temperature | Generic Temperature | Select Sprinkler Classification
|  |  | Ratings (°F) | Ratings (°F)
| Ordinary |  | 135 to 170 | 165 | Scroll to desired sprinkler class
| Intermediate |  | 175 to 225 | 212 | then Click on selection
| High |  | 250 to 300 | 275
| Extra high |  | 325 to 375 | 350
| Very extra high |  | 400 to 475 | 450
| Ultra high |  | 500 to 575 | 550
| Ultra high |  | 650 | 550
| User Specified Value |  | – | Enter Value
Reference: Automatic Sprinkler Systems Handbook, 6th Edition, National Fire Protection
Association, Quincy, Massachusetts, 1994, Page 67.
*Note: The actual temperature rating should be used when the value is available.
ESTIMATING SPRINKLER RESPONSE TIME
Reference: NFPA Fire Protection Handbook, 19th Edition, 2003, Page 3-140.
tactivation = (RTI/(√ujet)) (ln ((Tjet - Ta)/(Tjet - Tactivation)))
Where
|  | tactivation = | sprinkler activation response time (sec)
|  | RTI = | sprinkler response time index (m-sec)1/2
|  | ujet = | ceiling jet velocity (m/sec)
|  | Tjet = | ceiling jet temperature (°C)
|  | Ta = | ambient air temperature (°C)
|  | Tactivation = | activation temperature of sprinkler (°C)
Ceiling Jet Temperature Calculation
|  | Tjet - Ta = 16.9 (Q)2/3/H5/3 |  |  | for r/H ≤ 0.18
|  | Tjet - Ta = 5.38 (Q/r)2/3/H |  |  | for r/H > 0.18
Where
|  | Tjet = | ceiling jet temperature (°C)
|  | Ta = | ambient air temperature (°C)
|  | Q = | heat release rate of the fire (kW)
|  | H = | height of ceiling above top of fuel (m)
|  | r = | radial distance from the plume centerline to the sprinkler (m)
Convective Heat Release Rate Calculation
Qc = cc Q
Where
|  | Qc = | convective portion of the heat release rate (kW)
|  | Q = | heat release rate of the fire (kW)
|  | cc = | convective heat release rate fraction
|  | Qc = | 700 | kW
Radial Distance to Ceiling Height Ratio Calculation
|  | r/H = | 1 | r/H > 0.18
|  | >0.18 | 86.8388 | <0.18 | 272.7836
|  | Tjet - Ta = | {5.38 (Q/r)^2/3}/H
|  | Tjet - Ta = | 86.8388
|  | Tjet = | 111.8388 | (°C)
Ceiling Jet Velocity Calculation
|  | ujet = 0.96 (Q/H)1/3 |  |  | for r/H ≤ 0.15
|  | ujet = (0.195 Q1/3 H1/2)/r5/6 |  |  | for r/H > 0.15
Where
|  | ujet = | ceiling jet velocity (m/sec)
|  | Q = | heat release rate of the fire (kW)
|  | H = | height of ceiling above top of fuel (m)
|  | r = | radial distance from the plume centerline to the sprinkler (m)
Radial Distance to Ceiling Height Ratio Calculation
| r/H = | 1 | r/H > 0.15
| >0.15 | 1.354 | <0.15 | 6.6659
|  | ujet = | (0.195 Q^1/3 H^1/2)/r^5/6
|  | ujet = | 1.354 | m/sec
SPRINKLER ACTIVATION TIME CALCULATION
tactivation = (RTI/(√ujet)) (ln (Tjet - Ta)/(Tjet - Tactivation))
| tactivation = | #VALUE! | sec
Answer | The sprinkler will respond in approximately |  |  | #VALUE! | minutes
NOTE: If tactivation = "NUM" Sprinkler does not activate
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Changed references from Qc to Q and 0.15 to 0.18 in cells B58, B59, B76, C62, C78, |  |  |  | March 2011
D74, D76, E58, and E59, as appropriate and changed calculations in cells C76, C79,
and E 76. Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout.
Note on F27: This default value (0.70) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## FTHDetector
CHAPTER 10
ESTIMATING SPRINKLER RESPONSE TIME
Version 1805.1
(English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Heat Release Rate of the Fire (Q) (Steady State) |  |  |  | 1000 | kW
| Radial Distance to the Detector (r) **never more than 0.707 or 1/2√2 of the listed spacing** |  |  |  | 10 | ft | 3.048 | m
| Activation Temperature of the Fixed Temperature Heat Detector (Tactivation) |  |  |  | 135 | °F | 57.2222 | °C
| Detector Response Time Index (RTI) |  |  |  | 165 | (m-sec)1/2
| Height of Ceiling above Top of Fuel (H) |  |  |  | 12 | ft | 3.6576 | m
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F | 25 | °C
[7 empty] | 298 | K
| Convective Heat Release Fraction (cc) |  |  |  | 0.7
| r/H = | 0.83333 |  |  | Calculate
INPUT DATA FOR ESTIMATING HEAT DETECTOR RESPONSE TIME
Activation
Temperature Tactivation
|  | UL Listed Spacing | Response Time Index | Activation
|  | r (ft) | RTI (m-sec)1/2 | Temperature (°F) | Select Detector Spacing
|  | 10 | 490 | 128
|  | 15 | 306 | 128 | Scroll to desired spacing then
|  | 20 | 325 | 128 | Click on selection
|  | 25 | 152 | 128
|  | 30 | 116 | 128
|  | 40 | 87 | 128
|  | 50 | 72 | 128
|  | 70 | 44 | 128
|  | User Specified Value | Enter Value | Enter Value
|  | UL Listed Spacing | Response Time Index | Activation
|  | r (ft) | RTI (m-sec)1/2 | Temperature (°F) | Select Detector Spacing
|  | 10 | 404 | 135
|  | 15 | 233 | 135 | Scroll to desired spacing then
|  | 20 | 165 | 135 | Click on selection
|  | 25 | 123 | 135
|  | 30 | 98 | 135
|  | 40 | 70 | 135
|  | 50 | 54 | 135
|  | 70 | 20 | 135
|  | User Specified Value | Enter Value | Enter Value
|  | UL Listed Spacing | Response Time Index | Activation
|  | r (ft) | RTI (m-sec)1/2 | Temperature (°F) | Select Detector Spacing
|  | 10 | 321 | 145
|  | 15 | 191 | 145 | Scroll to desired spacing then
|  | 20 | 129 | 145 | Click on selection
|  | 25 | 96 | 145
|  | 30 | 75 | 145
|  | 40 | 50 | 145
|  | 50 | 37 | 145
|  | 70 | 11 | 145
|  | User Specified Value | Enter Value | Enter Value
|  | UL Listed Spacing | Response Time Index | Activation
|  | r (ft) | RTI (m-sec)1/2 | Temperature (°F) | Select Detector Spacing
|  | 10 | 239 | 160
|  | 15 | 135 | 160 | Scroll to desired spacing then
|  | 20 | 86 | 160 | Click on selection
|  | 25 | 59 | 160
|  | 30 | 44 | 160
|  | 40 | 22 | 160
|  | User Specified Value | Enter Value | Enter Value
|  | UL Listed Spacing | Response Time Index | Activation
|  | r (ft) | RTI (m-sec)1/2 | Temperature (°F) | Select Detector Spacing
|  | 10 | 196 | 170
|  | 15 | 109 | 170 | Scroll to desired spacing then
|  | 20 | 64 | 170 | Click on selection
|  | 25 | 39 | 170
|  | 30 | 27 | 170
|  | User Specified Value | Enter Value | Enter Value
|  | UL Listed Spacing | Response Time Index | Activation
|  | r (ft) | RTI (m-sec)1/2 | Temperature (°F) | Select Detector Spacing
|  | 10 | 119 | 196
|  | 15 | 55 | 196 | Scroll to desired spacing then
|  | 20 | 21 | 196
|  | User Specified Value | Enter Value | Enter Value | Click on selection
Reference: NFPA Standard 72, National Fire Alarm Code, Appendix B, Table B-3.2.5.1, 1999, Edition.
ESTIMATING FIXED TEMPERATURE HEAT DETECTOR RESPONSE TIME
Reference: NFPA Fire Protection Handbook, 19th Edition, 2003, Page 3-140.
tactivation = ( RTI/(√ujet)) (ln ((Tjet - Ta)/(Tjet - Tactivation)))
Where
| tactivation = | detector activation time (sec)
| RTI = | detector response time index (m-sec)1/2
| ujet = | ceiling jet velocity (m/sec)
| Tjet = | ceiling jet temperature (°C)
| Ta = | ambient air temperature (°C)
| Tactivation = | activation temperature of detector (°C)
Ceiling Jet Temperature Calculation
|  |  | Tjet - Ta = 16.9 (Q)2/3/H5/3 |  |  | for r/H ≤ 0.18
|  |  | Tjet - Ta = 5.38 (Q/r)2/3/H |  |  | for r/H > 0.18
Where
|  |  | Tjet = | ceiling jet temperature (°C)
|  |  | Ta = | ambient air temperature (°C)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | H = | height of ceiling above top of fuel (m)
|  |  | r = | radial distance from the plume centerline to the detector (m)
Convective Heat Release Rate Calculation
Qc = cc Q
Where
|  |  | Qc = | convective heat release rate (kW)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | cc = | convective heat release fraction
|  |  | Qc = | 700 | kW
Radial Distance to Ceiling Height Ratio Calculation
|  |  | r/H = | 0.83333 | r/H > 0.18
|  |  | >0.18 | 69.9696 | <0.18 | 194.6374
|  |  | Tjet - Ta = | 5.38 ((Q/r)^2/3)/H
|  |  | Tjet - Ta = | 69.9696
|  |  | Tjet = | 94.9696 | (°C)
Ceiling Jet Velocity Calculation
|  |  | ujet = 0.96 (Q/H)1/3 |  |  | for r/H ≤ 0.15
|  |  | ujet = (0.195 Q1/3 H1/2)/r5/6 |  |  | for r/H > 0.15
Where
|  |  | ujet = | ceiling jet velocity (m/sec)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | H = | height of ceiling above top of fuel (m)
|  |  | r = | radial distance from the plume centerline to the detector (m)
Radial Distance to Ceiling Height Ratio Calculation
|  |  | r/H = | 0.83333 | r/H > 0.15
|  |  | >0.15 | 1.4733 | <0.15 | 6.2307
|  |  | ujet = | (0.195 Q^1/3 H^1/2)/r^(5/6)
|  |  | ujet = | 1.4733 | m/sec
DETECTOR ACTIVATION TIME CALCULATION
tactivation = ( RTI/(√ujet)) (ln (Tjet - Ta)/(Tjet - Tactivation))
|  | tactivation = | 83.8934 | sec
Answer | The detector will respond in approximately |  |  | 1.3982 | minutes
NOTE: If tactivation = "NUM" Detector does not activate
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Changed references from Qc to Q and 0.15 to 0.18 in cells B98, B99, B116, C102, C118, |  |  |  | March 2011
D114, D116, E98, and E99, as appropriate and changed calculations in cells C116, C119,
and E 116. Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout.
Note on F27: This default value (0.70) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.