## Battery_Room_Hydrogen
CHAPTER 16
CALCULATING THE RATE OF HYDROGEN GAS
| GENERATION IN BATTERY ROOMS | [6 empty] | Version 1805.1
(English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
BATTERY INFORMATION
| Float Current (FC) |  |  |  | 15 | mA per 100 AH @ 8-hr. rate
| Ampere Hours (AH) |  |  |  | 3730 | Ampere hours
| Number of Cells (N) |  |  |  | 60
| Constant (K) |  |  |  | 0.000267 | ft3
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 26 | ft
| Compartment Length (lc) |  |  |  | 50 | ft
| Compartment Height (hc) |  |  |  | 12 | ft
FLAMMABLE GAS INFORMATION
Lower Flammability Limit of Hydrogen (FL) |  |  |  |  | 4 | % | 0.04
Calculate
Float Current Demand of Fully Charged Stationary Lead-Acid Cells
Reference: Yuasa, Inc., Safety Storage, Installation, Operation, and Maintenance Manual, Section 58.00,
Heritage Series, Flooded Lead-Acid Batteries, 2000.
FC*
| Charge Voltage | Antimony
| (VPC) | New |  | Select Charge Current Value
| 2.15 | 15
| 2.17 | 19 |  | Scroll to desired value then Click on selection
| 2.2 | 26
| 2.23 | 37
| 2.25 | 45
| 2.27 | 60
| 2.33 | 120
| 2.37 | 195
| 2.41 | 300
| User Specified Value | Enter Value | *(milliamperes per 100 AH @ 8-hr. rate)
FC*
| Charge Voltage | Antimony
| (VPC) | Old |  | Select Charge Current Value
| 2.15 | 60
| 2.17 | 80 |  | Scroll to desired value then Click on selection
| 2.2 | 105
| 2.23 | 150
| 2.25 | 185
| 2.27 | 230
| 2.33 | 450
| 2.37 | 700
| 2.41 | 1100
| User Specified Value | Enter Value | *(milliamperes per 100 AH @ 8-hr. rate)
FC*
| Charge Voltage | Antimony
| (VPC) | Calcium |  | Select Charge Current Value
2.15
| 2.17 | 4 |  | Scroll to desired value then Click on selection
| 2.2 | 6
| 2.23 | 8
| 2.25 | 11
| 2.27 | 12
| 2.33 | 24
| 2.37 | 38
| 2.41 | 58
| User Specified Value | Enter Value | *(milliamperes per 100 AH @ 8-hr. rate)
METHOD OF YUASA, INC.
Reference: Yuasa, Inc., Safety Storage, Installation, Operation, and Maintenance Manual, Section 58.00,
Heritage Series, Flooded Lead-Acid Batteries, 2000.
Estimating Hydrogen Gas Generation Rate
| H2(gen) = | FC/1000 x AH/100 x K x N
This equation is based on when electrolyte temperature is 77 °F (25 °C)
| Where |  |  | For every 15 °F (8 °C) electrolyte temperature rise the equation will multiply by 2
| H2(gen) = | hydrogen gas generation rate (ft3/min)
| FC= | float current (mA per 100 AH @ 8-hr. rate)
| AH = | ampere hours (normal 8 hour)
| K = | constant - 1 AH = 0.000267 ft3
| N = | number of cells
| H2(gen) = | FC/1000 x AH / 100 x K x N x 2 |  | Since electrolyte temperature is 92 °F (33 °C) the equation is multiplied by 2
| H2(gen) = | 0.017926 | ft3/min | 0.00050768 | m3/min
Estimating Hydrogen Gas in Compartment Based on Given Flammability Limit
|  | H2(comp) = | V x FL
Where
|  | H2(comp) = | hydrogen gas in compartment (ft3)
|  | V = | volume of compartment (ft3)
|  | FL = | hydrogen gas flammability limit
|  | H2(comp) = | 624 | ft3
Volume of Compartment
|  | V = | wc x lc x hc
Where
|  | V = | compartment volume (ft3)
|  | wc = | compartment width (ft)
|  | lc = | compartment length (ft)
|  | hc = | compartment height (ft)
|  | V = | 15600 | ft3
Estimating Time Required to Reach Hydrogen Concentration on Given Flammability Limit
| tH2 = | H2(comp) / H2(gen)
Where
| tH2 = | time require to reach on given flammability limit (min)
| H2(comp) = | hydrogen gas in compartment (ft3)
| H2(gen) = | hydrogen gas generation rate (ft3/min)
| tH2 = | 34809.0356 | min. or approx. | 580.1506 | hours
Summary of Results
ESTIMATING HYDROGEN GAS GENERATION RATE
| H2(gen) = | FC/1000 x AH / 100 x K x N x 2
Answer | H2(gen) = | 0.017926 | ft3/min | 0.00050768 | m3/min
ESTIMATING TIME REQUIRED TO REACH HYDROGEN CONCENTRATION ON GIVEN FLAMMABILITY LIMIT
| tH2 = | H2(comp) / H2(gen)
Answer | tH2= | 34809.0356 | min or approx. | 580.1506 | hours
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  | March 2011
Note on F25: This default value (0.000267) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F32: This default value (4 %) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Flammable_Gas_Buildup_Time
CHAPTER 16
CALCULATING THE RATE OF HYDROGEN GAS
|  |  | GENERATION IN BATTERY ROOMS |  |  |  |  | Version 1805.1
(English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION HYDROGEN LEAK INFORMATION
| Compartment Width (wc) |  |  |  | 29 | ft
| Compartment Length (lc) |  |  |  | 15 | ft
| Compartment Height (hc) |  |  |  | 12 | ft
| Leakage Rate |  |  |  | 50 | ft3/min
| Percent of Combustible Gas/Air Mixture |  |  |  | 5 | percent | 0.05
| Combustible Gas Concentration (C) |  |  |  | 2 | percent | 0.02
| Mixing Efficiency Factor (K) |  |  |  | 0.2
Calculate
Mixing Efficiency (K Values) for Various Ventilation Arrangements
Reference: NFPA 69, "Standard on Explosion Prevention Systems," 1997 Edition.
|  |  | K | Select Ventilation Arrangement
| Single Exhaust Opening |  | 0.2
| Multiple Exhaust Openings |  | 0.3 | Scroll to desired arrangement then Click on selection
|  |  | K | Select Ventilation Arrangement
| Single Exhaust Opening |  | 0.2
| Multiple Exhaust Openings |  | 0.4 | Scroll to desired arrangement then Click on selection
|  |  | K | Select Ventilation Arrangement
| Single Exhaust Opening |  | 0.3
| Multiple Exhaust Openings |  | 0.5 | Scroll to desired arrangement then Click on selection
|  |  | K | Select Ventilation Arrangement
| Single Exhaust Opening |  | 0.5
| Multiple Exhaust Openings |  | 0.7 | Scroll to desired arrangement then Click on selection
|  |  | K | Select Ventilation Arrangement
| Single Exhaust Opening |  | 0.8
| Multiple Exhaust Openings |  | 0.9 | Scroll to desired arrangement then Click on selection
|  |  | K | Select Ventilation Arrangement
| Single Exhaust Opening |  | Enter Value
| Multiple Exhaust Openings |  | Enter Value | Scroll to desired arrangement then Click on selection
METHOD OF NFPA 69, STANDARD ON EXPLOSION PREVENTION SYSTEMS
Reference: NFPA 69, "Standard on Explosion Prevention Systems, 1997 Edition, Appendix D.
Estimating Number of Theoretical Air Changes
ln [1 - (CQ / G)] = - K N
Where
|  | C = | combustible gas concentration
|  | Q = | air flow rate (fresh air) in enclosure (ft3/min)
|  | G = | combustible gas leakage rate (ft3/min)
|  | K = | mixing efficiency factor (constant)
|  | N = | number of theoretical air changes
Q = air flow rate (fresh air) in enclosure
|  | Q = | 47.5 | ft3/min
G = combustible gas leakage rate
|  | G = | 2.5 | (ft3/min)
N = number of theoretical air changes
ln [1 - (CQ / G)] = - K N
or
N = - [ln(1 - (CQ/G))]/ K
|  | N = | 2.3902
Estimating Combustible Gas Concentration Buildup Time
t = (V / leakage rate) * N
Where
|  | t = | buildup time (min)
|  | V = | compartment volume (ft3)
leakage rate (ft3/min)
|  | N = | number of theoretical air changes
Volume of Compartment
V = wc x lc x hc
Where
|  | V = | compartment volume (ft3)
|  | wc = | compartment width (ft)
|  | lc = | compartment length (ft)
|  | hc = | compartment height (ft)
|  | V = | 5220 | ft3
COMBUSTIBLE GAS CONCENTRATION BUILDUP TIME
t = (V / leakage rate) * N
Answer | t = | 249.5347 | minutes
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
| Revision Log | Description of Revision |  |  |  | Date
| 1805.0 | Original issue with final text. |  |  |  | December 2004
| 1805.1 | Corrected Filed D61 air flow rate (fresh air) in enclosure calculation. |  |  |  | March 2011
Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout.

## Flammable_Gas_Buildup
CHAPTER 16
CALCULATING THE RATE OF HYDROGEN GAS
|  | GENERATION IN BATTERY ROOMS | [5 empty] | Version 1805.1
(English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Lower Flammability Limit of Flammable Gas or Vapor (LFL) |  |  | 4 | % | 0.04 | 6.7
| Compartment Width (wc) |  |  | 50 | ft
| Compartment Length (lc) |  |  | 50 | ft
| Compartment Height (hc) |  |  | 12 | ft
Calculate
LOWER FLAMMABILITY DATA FOR GASES AND VAPORS
| Gases and | LFL | Select Gas or Vapor
| Vapors | Volume-Percent
Scroll to desired gas or vapor then Click on selection
| Hydrogen | 4
| Carbon Monoxide | 12.5
| Methane | 5
| Ethane | 3
| Propane | 2.1
| n-Butane | 1.8
| n-Pentane | 1.4
| n-Hexane | 1.2
| n-Heptane | 1.05
| n-Octane | 0.95
| n-Nonane | 0.85
| n-Decane | 0.75
| Ethene | 2.7
| Propane | 2.4
| Butene-1 | 1.7
| Acetylene | 2.5
| Methanol | 6.7
| Ethanol | 3.3
| n-Propanol | 2.2
| Acetone | 2.6
| Methyl Ethyl Ketone | 1.9
| Diethyl Ketone | 1.6
| Benzene | 1.3
| User Specified Value | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 2-175.
ESTIMATING FLAMMABLE CONCENTRATION OF GASES USING LIMITS OF FLAMMABILITY
Volume of Gas or Vapor for Deflagration = V x LFL
Where
| V = | volume of enclosure (ft3)
| LFL= | lower flammability of a gas or vapor (percent-volume)
Volume of Compartment
|  | V = | wc x lc x hc
Where
|  | V = | compartment volume (ft3)
|  | wc = | compartment width (ft)
|  | lc = | compartment length (ft)
|  | hc = | compartment height (ft)
|  | V = | 30000 | ft3
Volume of Gas or Vapor for Deflagration = V x LFL
Answer | Volume of Gas or Vapor for Deflagration = |  | 1200 | ft3 | 33.9802 | m3
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  | March 2011