## Beam
CHAPTER 17
ESTIMATING FIRE RESISTANCE TIME OF STEEL BEAMS
|  | PROTECTED BY FIRE PROTECTION INSULATION | [6 empty] | Version 1805.1
|  | (QUASI-STEADY-STATE APPROACH) | [6 empty] | (SI Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [6 empty] | 18.1664 | lb/ft2
| Thickness of Applied Protection on Steel Beam (h) |  |  |  |  | h ≥ 1/6 cm |  | 1.3 | cm | 0.042651 | ft
| Density of Applied Material (ri) | [6 empty] | 50 | lb/ft3
| Thermal Conductivity of Applied Material (ki) | [6 empty] | 0.1156 | Btu/ft-hr-°F | 3.2111e-05 | Btu/ft-sec-°F
| Specific Heat of Applied Material (ci) | [6 empty] | 0.4063 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [6 empty] | 25 | °C | 77
| Specific Heat of Steel (cs) | [6 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL BEAMS
| Structural Shape | W/D Ratio | [9 empty] | 33x221 | 23.3194
| W Shapes | (lb/ft2) | [9 empty] | 33x201 | 21.314
[12 empty] | 33x152 | 18.1664
| 36x300 | 29.6162 | [9 empty] | 33x141 | 16.9208
| 36x280 | 27.756 | [9 empty] | 33x130 | 15.6705
| 36x260 | 25.8943 | [9 empty] | 33x118 | 14.2944
| 36x245 | 24.4816 | [9 empty] | 30x211 | 23.9671
| 36x230 | 23.0596 | [9 empty] | 30x191 | 21.8161
| 36x210 | 23.2773 | [9 empty] | 30x173 | 19.8613
| 36x194 | 21.5965 | [9 empty] | 30x132 | 17.4018
| 36x182 | 20.3286 | [9 empty] | 30x124 | 16.403
| 36x170 | 19.053 | [9 empty] | 30x116 | 15.4025
| 36x160 | 17.991 | [9 empty] | 30x108 | 14.4008
| 36x150 | 16.9213 | [9 empty] | 30x99 | 13.2574
| 36x135 | 15.3191 | [9 empty] | 27x178 | 22.1519
| 33x241 | 25.3063 | [9 empty] | 27x161 | 20.1418
| 33x221 | 23.3194 | [9 empty] | 27x146 | 18.3561
| 33x201 | 21.314 | [9 empty] | 27x114 | 16.3539
| 33x152 | 18.1664 | [9 empty] | 27x102 | 14.7124
| 33x141 | 16.9208 | [9 empty] | 27x94 | 13.6183
| 33x130 | 15.6705 | [9 empty] | 27x84 | 12.236
| 33x118 | 14.2944 | [9 empty] | 24x162 | 22.2286
| 30x211 | 23.9671 | [9 empty] | 24x146 | 20.1657
| 30x191 | 21.8161 | [9 empty] | 24x131 | 18.2124
| 30x173 | 19.8613 | [9 empty] | 24x117 | 16.3598
| 30x132 | 17.4018 | [9 empty] | 24x104 | 14.6187
| 30x124 | 16.403 | [9 empty] | 24x94 | 15.0832
| 30x116 | 15.4025 | [9 empty] | 24x84 | 13.563
| 30x108 | 14.4008 | [9 empty] | 24x76 | 12.336
| 30x99 | 13.2574 | [9 empty] | 24x68 | 11.0983
| 27x178 | 22.1519 | [9 empty] | 24x62 | 10.9832
| 27x161 | 20.1418 | [9 empty] | 24x55 | 9.7974
| 27x146 | 18.3561 | [9 empty] | 21x147 | 21.9923
| 27x114 | 16.3539 | [9 empty] | 21x132 | 19.8795
| 27x102 | 14.7124 | [9 empty] | 21x122 | 18.4546
| 27x94 | 13.6183 | [9 empty] | 21x111 | 16.8736
| 27x84 | 12.236 | [9 empty] | 21x101 | 15.4218
| 24x162 | 22.2286 | [9 empty] | 21x93 | 16.5726
| 24x146 | 20.1657 | [9 empty] | 21x83 | 14.889
| 24x131 | 18.2124 | [9 empty] | 21x73 | 13.1819
| 24x117 | 16.3598 | [9 empty] | 21x68 | 12.3244
| 24x104 | 14.6187 | [9 empty] | 21x62 | 11.2898
| 24x94 | 15.0832 | [9 empty] | 21x57 | 11.2205
| 24x84 | 13.563 | [9 empty] | 21x50 | 9.919
| 24x76 | 12.336 | [9 empty] | 21x44 | 8.7824
| 24x68 | 11.0983 | [9 empty] | 18x119 | 20.2769
| 24x62 | 10.9832 | [9 empty] | 18x106 | 18.2026
| 24x55 | 9.7974 | [9 empty] | 18x97 | 16.7374
| 21x147 | 21.9923 | [9 empty] | 18x86 | 14.937
| 21x132 | 19.8795 | [9 empty] | 18x76 | 13.2799
| 21x122 | 18.4546 | [9 empty] | 18x71 | 14.4763
| 21x111 | 16.8736 | [9 empty] | 18x65 | 13.3174
| 21x101 | 15.4218 | [9 empty] | 18x60 | 12.3499
| 21x93 | 16.5726 | [9 empty] | 18x55 | 11.3734
| 21x83 | 14.889 | [9 empty] | 18x50 | 10.3887
| 21x73 | 13.1819 | [9 empty] | 18x46 | 10.3024
| 21x68 | 12.3244 | [9 empty] | 18x40 | 9.02
| 21x62 | 11.2898 | [9 empty] | 18x35 | 7.9545
| 21x57 | 11.2205 | [9 empty] | 16x100 | 18.7368
| 21x50 | 9.919 | [9 empty] | 16x89 | 16.807
| 21x44 | 8.7824 | [9 empty] | 16x77 | 14.6632
| 18x119 | 20.2769 | [9 empty] | 16x67 | 12.8486
| 18x106 | 18.2026 | [9 empty] | 16x57 | 12.8186
| 18x97 | 16.7374 | [9 empty] | 16x50 | 11.3272
| 18x86 | 14.937 | [9 empty] | 16x45 | 10.2515
| 18x76 | 13.2799 | [9 empty] | 16x40 | 9.1612
| 18x71 | 14.4763 | [9 empty] | 16x36 | 8.2941
| 18x65 | 13.3174 | [9 empty] | 16x31 | 7.7849
| 18x60 | 12.3499 | [9 empty] | 16x26 | 6.5851
| 18x55 | 11.3734 | [9 empty] | 14x730 | 94.836
| 18x50 | 10.3887 | [9 empty] | 14x665 | 88.1086
| 18x46 | 10.3024 | [9 empty] | 14x605 | 81.6694
| 18x40 | 9.02 | [9 empty] | 14x550 | 75.5841
| 18x35 | 7.9545 | [9 empty] | 14x500 | 69.8893
| 16x100 | 18.7368 | [9 empty] | 14x455 | 64.6039
| 16x89 | 16.807 | [9 empty] | 14x426 | 61.0935
| 16x77 | 14.6632 | [9 empty] | 14x398 | 57.6742
| 16x67 | 12.8486 | [9 empty] | 14x370 | 54.1761
| 16x57 | 12.8186 | [9 empty] | 14x342 | 50.7293
| 16x50 | 11.3272 | [9 empty] | 14x311 | 46.5859
| 16x45 | 10.2515 | [9 empty] | 14x283 | 42.8626
| 16x40 | 9.1612 | [9 empty] | 14x257 | 39.3392
| 16x36 | 8.2941 | [9 empty] | 14x233 | 36.0263
| 16x31 | 7.7849 | [9 empty] | 14x211 | 32.9344
| 16x26 | 6.5851 | [9 empty] | 14x193 | 30.3499
| 14x730 | 94.836 | [9 empty] | 14x176 | 27.8886
| 14x665 | 88.1086 | [9 empty] | 14x159 | 25.2923
| 14x605 | 81.6694 | [9 empty] | 14x145 | 23.2932
| 14x550 | 75.5841 | [9 empty] | 14x132 | 21.9375
| 14x500 | 69.8893 | [9 empty] | 14x120 | 20.0585
| 14x455 | 64.6039 | [9 empty] | 14x109 | 18.318
| 14x426 | 61.0935 | [9 empty] | 14x99 | 16.7218
| 14x398 | 57.6742 | [9 empty] | 14x90 | 15.2715
| 14x370 | 54.1761 | [9 empty] | 14x82 | 16.9684
| 14x342 | 50.7293 | [9 empty] | 14x74 | 15.4033
| 14x311 | 46.5859 | [9 empty] | 14x68 | 14.2272
| 14x283 | 42.8626 | [9 empty] | 14x61 | 12.8387
| 14x257 | 39.3392 | [9 empty] | 14x53 | 12.4025
| 14x233 | 36.0263 | [9 empty] | 14x48 | 11.2963
| 14x211 | 32.9344 | [9 empty] | 14x43 | 10.1785
| 14x193 | 30.3499 | [9 empty] | 14x38 | 9.5218
| 14x176 | 27.8886 | [9 empty] | 14x34 | 8.5669
| 14x159 | 25.2923 | [9 empty] | 14x30 | 7.6062
| 14x145 | 23.2932 | [9 empty] | 14x26 | 7.3611
| 14x132 | 21.9375 | [9 empty] | 14x22 | 6.2827
| 14x120 | 20.0585 | [9 empty] | 12x336 | 57.3991
| 14x109 | 18.318 | [9 empty] | 12x305 | 52.9705
| 14x99 | 16.7218 | [9 empty] | 12x279 | 49.1919
| 14x90 | 15.2715 | [9 empty] | 12x252 | 45.104
| 14x82 | 16.9684 | [9 empty] | 12x230 | 41.6824
| 14x74 | 15.4033 | [9 empty] | 12x210 | 38.5144
| 14x68 | 14.2272 | [9 empty] | 12x190 | 35.2668
| 14x61 | 12.8387 | [9 empty] | 12x170 | 31.9499
| 14x53 | 12.4025 | [9 empty] | 12x152 | 28.8973
| 14x48 | 11.2963 | [9 empty] | 12x136 | 26.1371
| 14x43 | 10.1785 | [9 empty] | 12x120 | 23.3085
| 14x38 | 9.5218 | [9 empty] | 12x106 | 20.7775
| 14x34 | 8.5669 | [9 empty] | 12x96 | 18.9474
| 14x30 | 7.6062 | [9 empty] | 12x87 | 17.2833
| 14x26 | 7.3611 | [9 empty] | 12x79 | 15.7842
| 14x22 | 6.2827 | [9 empty] | 12x72 | 14.4578
| 12x336 | 57.3991 | [9 empty] | 12x65 | 13.1181
| 12x305 | 52.9705 | [9 empty] | 12x58 | 12.9633
| 12x279 | 49.1919 | [9 empty] | 12x53 | 11.9068
| 12x252 | 45.104 | [9 empty] | 12x50 | 12.5313
| 12x230 | 41.6824 | [9 empty] | 12x45 | 11.3481
| 12x210 | 38.5144 | [9 empty] | 12x40 | 10.1469
| 12x190 | 35.2668 | [9 empty] | 12x35 | 9.5281
| 12x170 | 31.9499 | [9 empty] | 12x30 | 8.2342
| 12x152 | 28.8973 | [9 empty] | 12x26 | 7.1807
| 12x136 | 26.1371 | [9 empty] | 12x22 | 7.2948
| 12x120 | 23.3085 | [9 empty] | 12x19 | 6.3572
| 12x106 | 20.7775 | [9 empty] | 12x16 | 5.4069
| 12x96 | 18.9474 | [9 empty] | 12x14 | 4.7552
| 12x87 | 17.2833 | [9 empty] | 10x112 | 25.622
| 12x79 | 15.7842 | [9 empty] | 10x100 | 23.1392
| 12x72 | 14.4578 | [9 empty] | 10x88 | 20.5988
| 12x65 | 13.1181 | [9 empty] | 10x77 | 18.2213
| 12x58 | 12.9633 | [9 empty] | 10x68 | 16.2388
| 12x53 | 11.9068 | [9 empty] | 10x60 | 14.4462
| 12x50 | 12.5313 | [9 empty] | 10x54 | 13.083
| 12x45 | 11.3481 | [9 empty] | 10x49 | 11.9318
| 12x40 | 10.1469 | [9 empty] | 10x45 | 12.3967
| 12x35 | 9.5281 | [9 empty] | 10x39 | 10.8421
| 12x30 | 8.2342 | [9 empty] | 10x33 | 9.261
| 12x26 | 7.1807 | [9 empty] | 10x30 | 9.5314
| 12x22 | 7.2948 | [9 empty] | 10x26 | 8.3311
| 12x19 | 6.3572 | [9 empty] | 10x22 | 7.114
| 12x16 | 5.4069 | [9 empty] | 10x19 | 7.1161
| 12x14 | 4.7552 | [9 empty] | 10x17 | 6.4212
| 10x112 | 25.622 | [9 empty] | 10x15 | 5.7107
| 10x100 | 23.1392 | [9 empty] | 10x12 | 4.6095
| 10x88 | 20.5988 | [9 empty] | 8x67 | 19.2806
| 10x77 | 18.2213 | [9 empty] | 8x58 | 16.9178
| 10x68 | 16.2388 | [9 empty] | 8x48 | 14.2117
| 10x60 | 14.4462 | [9 empty] | 8x40 | 12.003
| 10x54 | 13.083 | [9 empty] | 8x35 | 10.5823
| 10x49 | 11.9318 | [9 empty] | 8x31 | 9.438
| 10x45 | 12.3967 | [9 empty] | 8x28 | 9.5577
| 10x39 | 10.8421 | [9 empty] | 8x24 | 8.2628
| 10x33 | 9.261 | [9 empty] | 8x21 | 7.9071
| 10x30 | 9.5314 | [9 empty] | 8x18 | 6.8419
| 10x26 | 8.3311 | [9 empty] | 8x15 | 6.4806
| 10x22 | 7.114 | [9 empty] | 8x13 | 5.6686
| 10x19 | 7.1161 | [9 empty] | 8x10 | 4.4021
| 10x17 | 6.4212 | [9 empty] | 6x25 | 9.8814
| 10x15 | 5.7107 | [9 empty] | 6x20 | 8.016
| 10x12 | 4.6095 | [9 empty] | 6x15 | 6.1038
| 8x67 | 19.2806 | [9 empty] | 6x16 | 7.9569
| 8x58 | 16.9178 | [9 empty] | 6x12 | 6.1017
| 8x48 | 14.2117 | [9 empty] | 6x9 | 4.6392
| 8x40 | 12.003 | [9 empty] | 5x19 | 9.1751
| 8x35 | 10.5823 | [9 empty] | 5x16 | 7.824
| 8x31 | 9.438 | [9 empty] | 4x13 | 7.8235
| 8x28 | 9.5577
| 8x24 | 8.2628
| 8x21 | 7.9071
| 8x18 | 6.8419
| 8x15 | 6.4806
| 8x13 | 5.6686
| 8x10 | 4.4021
| 6x25 | 9.8814
| 6x20 | 8.016
| 6x15 | 6.1038
| 6x16 | 7.9569
| 6x12 | 6.1017
| 6x9 | 4.6392
| 5x19 | 9.1751
| 5x16 | 7.824
| 4x13 | 7.82
| User Specified Value | Enter Value
Select Beam
Scroll to desired beam size then Click on selection,
THERMAL PROPERTIES OF BOARD TYPE INSULATION MATERIALS
Select Insulation Type
Insulation Material |  | Density | Thermal | Specific Heat
Board |  | ρi | Conductivity ki | ci |  | Scroll to desired material then Click on selection
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F)
Fiber-silicate, fiber-calcium silicate |  | 38 | 0.0867 | 0.2868
Gypsum plaster |  | 50 | 0.1156 | 0.4063
Mineral wool, fiber silicate |  | 10 | 0.1156 | 0.2868
Concrete |  | 150 | 0.9248 | 0.1793
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 182.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of FireProtection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Beam
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
Where
DTs = temperature rise in steel (°F)
ki = thermal conductivity of insulation material (Btu/ft-sec-°F)
ri = density of insulation material (lb/ft3)
ci = specific heat of insulation material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
Dt = 15.9 W/D
|  |  | Dt = | 288.8462 | sec
|  |  | Dt = | 4.8141 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
Tf = C1 LOG (0.133 t + 1) + Ta
Where
Tf = fire exposure temperature (°F)
C1 = constant = 620
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where |  |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | t1 = Dt/2 |  |  | carbon steel structural members begin to fail. Predicted
|  | Ts0 = initial steel temperature (°F) |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
Where
t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Answer
Time | Time | DTs | Ts |  |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°C) |  |  | (min) | (sec) | (°F) | (°C)
4.8141 | 288.8462 | 78.0886 | 68.3826 |  |  | 255.1475 | 15308.8472 | 174.6647 | 4528.0716 | Failure of Beam
9.6282 | 577.6923 | 97.0068 | 122.2752 |  |  | 259.9616 | 15597.6933 | 175.0861 | 4625.3416 | Failure of Beam
14.4423 | 866.5385 | 107.5933 | 182.0493 |  |  | 264.7757 | 15886.5395 | 175.4997 | 4722.8414 | Failure of Beam
19.2564 | 1155.3847 | 114.7745 | 245.8129 |  |  | 269.5898 | 16175.3857 | 175.9058 | 4820.5668 | Failure of Beam
24.0705 | 1444.2309 | 120.2177 | 312.6005 |  |  | 274.4039 | 16464.2319 | 176.3046 | 4918.5139 | Failure of Beam
28.8846 | 1733.077 | 124.5969 | 381.821 |  |  | 279.218 | 16753.078 | 176.6965 | 5016.6786 | Failure of Beam
33.6987 | 2021.9232 | 128.2598 | 453.0764 |  |  | 284.0321 | 17041.9242 | 177.0816 | 5115.0573 | Failure of Beam
38.5128 | 2310.7694 | 131.4077 | 526.0807 |  |  | 288.8462 | 17330.7704 | 177.4603 | 5213.6463 | Failure of Beam
43.3269 | 2599.6156 | 134.1674 | 600.6181 | Failure of Beam |  | 293.6603 | 17619.6165 | 177.8326 | 5312.4422 | Failure of Beam
48.141 | 2888.4617 | 136.6243 | 676.5205 | Failure of Beam |  | 298.4744 | 17908.4627 | 178.1988 | 5411.4416 | Failure of Beam
52.9551 | 3177.3079 | 138.8381 | 753.6528 | Failure of Beam |  | 303.2885 | 18197.3089 | 178.5592 | 5510.6411 | Failure of Beam
57.7692 | 3466.1541 | 140.8527 | 831.9043 | Failure of Beam |  | 308.1026 | 18486.1551 | 178.9138 | 5610.0376 | Failure of Beam
62.5833 | 3755.0002 | 142.7009 | 911.1826 | Failure of Beam |  | 312.9167 | 18775.0012 | 179.2629 | 5709.6281 | Failure of Beam
67.3974 | 4043.8464 | 144.4081 | 991.4093 | Failure of Beam |  | 317.7308 | 19063.8474 | 179.6066 | 5809.4096 | Failure of Beam
72.2115 | 4332.6926 | 145.9943 | 1072.5173 | Failure of Beam |  | 322.5449 | 19352.6936 | 179.9451 | 5909.3791 | Failure of Beam
77.0256 | 4621.5388 | 147.4756 | 1154.4482 | Failure of Beam |  | 327.359 | 19641.5398 | 180.2786 | 6009.5339 | Failure of Beam
81.8397 | 4910.3849 | 148.8649 | 1237.1509 | Failure of Beam |  | 332.1731 | 19930.3859 | 180.6072 | 6109.8712 | Failure of Beam
86.6539 | 5199.2311 | 150.173 | 1320.5803 | Failure of Beam |  | 336.9872 | 20219.2321 | 180.931 | 6210.3884 | Failure of Beam
91.468 | 5488.0773 | 151.4088 | 1404.6963 | Failure of Beam |  | 341.8013 | 20508.0783 | 181.2503 | 6311.083 | Failure of Beam
96.2821 | 5776.9235 | 152.58 | 1489.463 | Failure of Beam |  | 346.6154 | 20796.9245 | 181.565 | 6411.9525 | Failure of Beam
101.0962 | 6065.7696 | 153.6929 | 1574.8479 | Failure of Beam |  | 351.4295 | 21085.7706 | 181.8754 | 6512.9943 | Failure of Beam
105.9103 | 6354.6158 | 154.7531 | 1660.8219 | Failure of Beam |  | 356.2436 | 21374.6168 | 182.1815 | 6614.2063 | Failure of Beam
110.7244 | 6643.462 | 155.7654 | 1747.3582 | Failure of Beam |  | 361.0577 | 21663.463 | 182.4835 | 6715.586 | Failure of Beam
115.5385 | 6932.3082 | 156.7338 | 1834.4326 | Failure of Beam |  | 365.8718 | 21952.3091 | 182.7814 | 6817.1312 | Failure of Beam
120.3526 | 7221.1543 | 157.6621 | 1922.0226 | Failure of Beam |  | 370.6859 | 22241.1553 | 183.0755 | 6918.8398 | Failure of Beam
125.1667 | 7510.0005 | 158.5534 | 2010.1079 | Failure of Beam |  | 375.5 | 22530.0015 | 183.3657 | 7020.7096 | Failure of Beam
129.9808 | 7798.8467 | 159.4106 | 2098.6693 | Failure of Beam |  | 380.3141 | 22818.8477 | 183.6522 | 7122.7386 | Failure of Beam
134.7949 | 8087.6928 | 160.2362 | 2187.6894 | Failure of Beam |  | 385.1282 | 23107.6938 | 183.9351 | 7224.9248 | Failure of Beam
139.609 | 8376.539 | 161.0324 | 2277.1518 | Failure of Beam |  | 389.9423 | 23396.54 | 184.2145 | 7327.2662 | Failure of Beam
144.4231 | 8665.3852 | 161.8012 | 2367.0414 | Failure of Beam |  | 394.7564 | 23685.3862 | 184.4904 | 7429.7609 | Failure of Beam
149.2372 | 8954.2314 | 162.5445 | 2457.3439 | Failure of Beam |  | 399.5705 | 23974.2324 | 184.763 | 7532.407 | Failure of Beam
154.0513 | 9243.0775 | 163.2639 | 2548.046 | Failure of Beam |  | 404.3846 | 24263.0785 | 185.0323 | 7635.2027 | Failure of Beam
158.8654 | 9531.9237 | 163.9609 | 2639.1354 | Failure of Beam |  | 409.1987 | 24551.9247 | 185.2984 | 7738.1462 | Failure of Beam
163.6795 | 9820.7699 | 164.6368 | 2730.6003 | Failure of Beam |  | 414.0128 | 24840.7709 | 185.5613 | 7841.2359 | Failure of Beam
168.4936 | 10109.6161 | 165.293 | 2822.4298 | Failure of Beam |  | 418.827 | 25129.617 | 185.8212 | 7944.4699 | Failure of Beam
173.3077 | 10398.4622 | 165.9304 | 2914.6133 | Failure of Beam |  | 423.6411 | 25418.4632 | 186.0781 | 8047.8466 | Failure of Beam
178.1218 | 10687.3084 | 166.5502 | 3007.1412 | Failure of Beam |  | 428.4552 | 25707.3094 | 186.3321 | 8151.3645 | Failure of Beam
182.9359 | 10976.1546 | 167.1533 | 3100.0041 | Failure of Beam |  | 433.2693 | 25996.1556 | 186.5833 | 8255.0218 | Failure of Beam
187.75 | 11265.0007 | 167.7405 | 3193.1933 | Failure of Beam |  | 438.0834 | 26285.0017 | 186.8317 | 8358.8172 | Failure of Beam
192.5641 | 11553.8469 | 168.3128 | 3286.7005 | Failure of Beam |  | 442.8975 | 26573.8479 | 187.0773 | 8462.749 | Failure of Beam
197.3782 | 11842.6931 | 168.8708 | 3380.5175 | Failure of Beam |  | 447.7116 | 26862.6941 | 187.3203 | 8566.8158 | Failure of Beam
202.1923 | 12131.5393 | 169.4152 | 3474.6371 | Failure of Beam |  | 452.5257 | 27151.5403 | 187.5606 | 8671.0162 | Failure of Beam
207.0064 | 12420.3854 | 169.9467 | 3569.0519 | Failure of Beam |  | 457.3398 | 27440.3864 | 187.7984 | 8775.3487 | Failure of Beam
211.8205 | 12709.2316 | 170.4658 | 3663.7551 | Failure of Beam |  | 462.1539 | 27729.2326 | 188.0337 | 8879.8119 | Failure of Beam
216.6346 | 12998.0778 | 170.9732 | 3758.7402 | Failure of Beam |  | 466.968 | 28018.0788 | 188.2666 | 8984.4044 | Failure of Beam
221.4487 | 13286.924 | 171.4693 | 3854.0009 | Failure of Beam |  | 471.7821 | 28306.9249 | 188.4971 | 9089.125 | Failure of Beam
226.2628 | 13575.7701 | 171.9547 | 3949.5313 | Failure of Beam |  | 476.5962 | 28595.7711 | 188.7252 | 9193.9723 | Failure of Beam
231.0769 | 13864.6163 | 172.4297 | 4045.3256 | Failure of Beam |  | 481.4103 | 28884.6173 | 188.951 | 9298.9451 | Failure of Beam
235.891 | 14153.4625 | 172.8949 | 4141.3784 | Failure of Beam |  | 486.2244 | 29173.4635 | 189.1745 | 9404.0421 | Failure of Beam
240.7051 | 14442.3086 | 173.3507 | 4237.6843 | Failure of Beam |  | 491.0385 | 29462.3096 | 189.3959 | 9509.262 | Failure of Beam
245.5192 | 14731.1548 | 173.7973 | 4334.2383 | Failure of Beam |  | 495.8526 | 29751.1558 | 189.6151 | 9614.6037 | Failure of Beam
250.3333 | 15020.001 | 174.2352 | 4431.0357 | Failure of Beam |  | 500.6667 | 30040.002 | 189.8321 | 9720.066 | Failure of Beam
The Failure Temperature for Steel Beams is Assumed at 1000 °F (538 °C)
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | January 2005
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and |  |  |  |  | March 2011
print layout.

## Column
CHAPTER 17
ESTIMATING FIRE RESISTANCE TIME OF STEEL COLUMNS
|  | PROTECTED BY FIRE PROTECTION INSULATION | [6 empty] | Version 1805.1
|  | (QUASI-STEADY-STATE APPROACH) | [6 empty] | (SI Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [6 empty] | 12.0334 | lb/ft2
| Thickness of Applied Protection on Steel Column (h) |  |  |  |  | h ≥ 1/6 cm |  | 2.54 | cm |  | 0.083333 | ft
| Density of Applied Material (ri) | [6 empty] | 10 | lb/ft3
| Thermal Conductivity of Applied Material (ki) | [6 empty] | 0.1156 | Btu/ft-hr-°F |  | 3.2111e-05 | Btu/ft-sec-°F
| Specific Heat of Applied Material (ci) | [6 empty] | 0.2868 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [6 empty] | 25 | °C | 77
| Specific Heat of Steel (cs) | [6 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL COLUMNS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 26.0473
| 36x280 | 24.4097
| 36x260 | 22.7671
| 36x245 | 21.5227
| 36x230 | 20.2703
| 36x210 | 20.9233
| 36x194 | 19.4146
| 36x182 | 18.2746
| 36x170 | 17.1285
| 36x160 | 16.1725
| 36x150 | 15.2091
| 36x135 | 13.7638
| 33x241 | 22.2222
| 33x221 | 20.474
| 33x201 | 18.7107
| 33x152 | 16.2901
| 33x141 | 15.1708
| 33x130 | 14.0465
| 33x118 | 12.8098
| 30x211 | 20.9689
| 30x191 | 19.0841
| 30x173 | 17.3709
| 30x132 | 15.5952
| 30x124 | 14.6992
| 30x116 | 13.7999
| 30x108 | 12.8994
| 30x99 | 11.8729
| 27x178 | 19.3286
| 27x161 | 17.5732
| 27x146 | 16.0132
| 27x114 | 14.5967
| 27x102 | 13.1316
| 27x94 | 12.1526
| 27x84 | 10.9162
| 24x162 | 19.3606
| 24x146 | 17.5586
| 24x131 | 15.8516
| 24x117 | 14.2365
| 24x104 | 12.7191
| 24x94 | 13.4526
| 24x84 | 12.095
| 24x76 | 10.9986
| 24x68 | 9.8921
| 24x62 | 9.9492
| 24x55 | 8.8745
| 21x147 | 19.025
| 21x132 | 17.195
| 21x122 | 15.9616
| 21x111 | 14.5925
| 21x101 | 13.3363
| 21x93 | 14.7307
| 21x83 | 13.2359
| 21x73 | 11.7191
| 21x68 | 10.956
| 21x62 | 10.0351
| 21x57 | 10.1318
| 21x50 | 8.9526
| 21x44 | 7.9255
| 18x119 | 17.4807
| 18x106 | 15.6882
| 18x97 | 14.4256
| 18x86 | 12.871
| 18x76 | 11.4415
| 18x71 | 12.814
| 18x65 | 11.7896
| 18x60 | 10.9339
| 18x55 | 10.0671
| 18x50 | 9.1954
| 18x46 | 9.2555
| 18x40 | 8.104
| 18x35 | 7.1429
| 16x100 | 16.1139
| 16x89 | 14.45
| 16x77 | 12.604
| 16x67 | 11.0424
| 16x57 | 11.3095
| 16x50 | 9.9933
| 16x45 | 9.0437
| 16x40 | 8.0822
| 16x36 | 7.3134
| 16x31 | 6.9781
| 16x26 | 5.9002
| 14x730 | 79.4486
| 14x665 | 73.7387
| 14x605 | 68.2908
| 14x550 | 63.1458
| 14x500 | 58.3317
| 14x455 | 53.8727
| 14x426 | 50.9316
| 14x398 | 48.0483
| 14x370 | 45.1082
| 14x342 | 42.1962
| 14x311 | 38.7378
| 14x283 | 35.6199
| 14x257 | 32.673
| 14x233 | 29.9037
| 14x211 | 27.3198
| 14x193 | 25.1684
| 14x176 | 23.1123
| 14x159 | 20.9454
| 14x145 | 19.2905
| 14x132 | 18.2216
| 14x120 | 16.6551
| 14x109 | 15.2075
| 14x99 | 13.8769
| 14x90 | 12.6701
| 14x82 | 14.4451
| 14x74 | 13.1128
| 14x68 | 12.1086
| 14x61 | 10.9237
| 14x53 | 10.7179
| 14x48 | 9.7594
| 14x43 | 8.792
| 14x38 | 8.3425
| 14x34 | 7.5041
| 14x30 | 6.6593
| 14x26 | 6.5809
| 14x22 | 5.6146
| 12x336 | 48.2124
| 12x305 | 44.4552
| 12x279 | 41.2315
| 12x252 | 37.7764
| 12x230 | 34.8881
| 12x210 | 32.2168
| 12x190 | 29.4878
| 12x170 | 26.6946
| 12x152 | 24.127
| 12x136 | 21.8065
| 12x120 | 19.4332
| 12x106 | 17.3203
| 12x96 | 15.7895
| 12x87 | 14.394
| 12x79 | 13.1411
| 12x72 | 12.0334
| 12x65 | 10.9152
| 12x58 | 10.9262
| 12x53 | 10.03
| 12x50 | 10.7219
| 12x45 | 9.707
| 12x40 | 8.6784
| 12x35 | 8.2938
| 12x30 | 7.1656
| 12x26 | 6.2475
| 12x22 | 6.5639
| 12x19 | 5.7186
| 12x16 | 4.8608
| 12x14 | 4.2748
| 10x112 | 21.3774
| 10x100 | 19.2926
| 10x88 | 17.1624
| 10x77 | 15.1724
| 10x68 | 13.5144
| 10x60 | 12.016
| 10x54 | 10.8798
| 10x49 | 9.919
| 10x45 | 10.4692
| 10x39 | 9.1496
| 10x33 | 7.8076
| 10x30 | 8.2607
| 10x26 | 7.2189
| 10x22 | 6.1596
| 10x19 | 6.3228
| 10x17 | 5.7015
| 10x15 | 5.0676
| 10x12 | 4.0909
| 8x67 | 16.0864
| 8x58 | 14.1005
| 8x48 | 11.8421
| 8x40 | 9.9875
| 8x35 | 8.8028
| 8x31 | 7.8464
| 8x28 | 8.0595
| 8x24 | 6.9649
| 8x21 | 6.7851
| 8x18 | 5.8664
| 8x15 | 5.6622
| 8x13 | 4.9492
| 8x10 | 3.8462
| 6x25 | 8.2327
| 6x20 | 6.6741
| 6x15 | 5.0733
| 6x16 | 6.8182
| 6x12 | 5.2174
| 6x9 | 3.9677
| 5x19 | 7.6305
| 5x16 | 6.4997
| 4x13 | 6.5
| User Specified Value | Enter Value
Select Column
Scroll to desired column size then Click on selection,
THERMAL PROPERTIES OF BOARD TYPE INSULATION MATERIALS
Select Insulation Type
Insulation Material |  | Density | Thermal | Specific Heat
Board |  | ρi | Conductivity ki | ci |  | Scroll to desired material then Click on selection
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F)
Fiber-silicate, fiber-calcium silicate |  | 38 | 0.0867 | 0.2868
Gypsum plaster |  | 50 | 0.1156 | 0.4063
Mineral wool, fiber silicate |  | 10 | 0.1156 | 0.2868
Concrete |  | 150 | 0.9248 | 0.1793
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 182.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of FireProtection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Beam
DTs = (ki /(cs h W/D+1/2cirih2)) (Tf - Ts) Dt
Where
DTs = temperature rise in steel (°F)
ki = thermal conductivity of insulation material (Btu/ft-sec-°F)
ri = density of insulation material (lb/ft3)
ci = specific heat of insulation material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
The Maximum Allowable Time Step
Dt = 15.9 W/D
|  |  | Dt = | 191.3315 | sec
|  |  | Dt = | 3.1889 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
Tf = C1 LOG (0.133 t + 1) + Ta
Where
Tf = fire exposure temperature (°F)
C1 = constant = 620
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where |  |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | t1 = Dt/2 |  |  | carbon steel structural members begin to fail. Predicted
|  | Ts0 = initial steel temperature (°F) |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
Where
t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Answer
Time | Time | DTs | Ts |  |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°C) |  |  | (min) | (sec) | (°F) | (°C)
3.1889 | 191.3315 | 35.1164 | 44.5091 |  |  | 194.5203 | 11671.2201 | 89.9047 | 2676.1863 | Failure of Column
6.3777 | 382.663 | 46.5844 | 70.3893 |  |  | 197.7092 | 11862.5515 | 90.1 | 2726.2418 | Failure of Column
9.5666 | 573.9944 | 52.3031 | 99.4466 |  |  | 200.8981 | 12053.883 | 90.2923 | 2776.4042 | Failure of Column
12.7554 | 765.3259 | 56.1841 | 130.6599 |  |  | 204.0869 | 12245.2145 | 90.4814 | 2826.6717 | Failure of Column
15.9443 | 956.6574 | 59.1114 | 163.4996 |  |  | 207.2758 | 12436.546 | 90.6676 | 2877.0426 | Failure of Column
19.1331 | 1147.9889 | 61.4618 | 197.645 |  |  | 210.4646 | 12627.8774 | 90.851 | 2927.5154 | Failure of Column
22.322 | 1339.3203 | 63.4251 | 232.8812 |  |  | 213.6535 | 12819.2089 | 91.0316 | 2978.0885 | Failure of Column
25.5109 | 1530.6518 | 65.111 | 269.054 |  |  | 216.8423 | 13010.5404 | 91.2095 | 3028.7604 | Failure of Column
28.6997 | 1721.9833 | 66.588 | 306.0473 |  |  | 220.0312 | 13201.8719 | 91.3848 | 3079.5297 | Failure of Column
31.8886 | 1913.3148 | 67.9024 | 343.7709 |  |  | 223.2201 | 13393.2033 | 91.5575 | 3130.395 | Failure of Column
35.0774 | 2104.6462 | 69.0863 | 382.1521 |  |  | 226.4089 | 13584.5348 | 91.7278 | 3181.3549 | Failure of Column
38.2663 | 2295.9777 | 70.1633 | 421.1317 |  |  | 229.5978 | 13775.8663 | 91.8957 | 3232.408 | Failure of Column
41.4552 | 2487.3092 | 71.1511 | 460.6601 |  |  | 232.7866 | 13967.1978 | 92.0612 | 3283.5531 | Failure of Column
44.644 | 2678.6407 | 72.0634 | 500.6953 |  |  | 235.9755 | 14158.5292 | 92.2245 | 3334.789 | Failure of Column
47.8329 | 2869.9721 | 72.9109 | 541.2014 | Failure of Column |  | 239.1643 | 14349.8607 | 92.3856 | 3386.1143 | Failure of Column
51.0217 | 3061.3036 | 73.7022 | 582.1471 | Failure of Column |  | 242.3532 | 14541.1922 | 92.5445 | 3437.5279 | Failure of Column
54.2106 | 3252.6351 | 74.4443 | 623.505 | Failure of Column |  | 245.5421 | 14732.5237 | 92.7014 | 3489.0287 | Failure of Column
57.3994 | 3443.9666 | 75.1429 | 665.2511 | Failure of Column |  | 248.7309 | 14923.8552 | 92.8562 | 3540.6155 | Failure of Column
60.5883 | 3635.2981 | 75.8029 | 707.3638 | Failure of Column |  | 251.9198 | 15115.1866 | 93.009 | 3592.2872 | Failure of Column
63.7772 | 3826.6295 | 76.4283 | 749.824 | Failure of Column |  | 255.1086 | 15306.5181 | 93.1599 | 3644.0427 | Failure of Column
66.966 | 4017.961 | 77.0226 | 792.6143 | Failure of Column |  | 258.2975 | 15497.8496 | 93.3089 | 3695.881 | Failure of Column
70.1549 | 4209.2925 | 77.5886 | 835.7191 | Failure of Column |  | 261.4864 | 15689.1811 | 93.4561 | 3747.8011 | Failure of Column
73.3437 | 4400.624 | 78.129 | 879.1241 | Failure of Column |  | 264.6752 | 15880.5125 | 93.6015 | 3799.8019 | Failure of Column
76.5326 | 4591.9554 | 78.6461 | 922.8164 | Failure of Column |  | 267.8641 | 16071.844 | 93.7451 | 3851.8825 | Failure of Column
79.7214 | 4783.2869 | 79.1416 | 966.7839 | Failure of Column |  | 271.0529 | 16263.1755 | 93.8871 | 3904.042 | Failure of Column
82.9103 | 4974.6184 | 79.6174 | 1011.0158 | Failure of Column |  | 274.2418 | 16454.507 | 94.0273 | 3956.2794 | Failure of Column
86.0992 | 5165.9499 | 80.0749 | 1055.5019 | Failure of Column |  | 277.4306 | 16645.8384 | 94.166 | 4008.5938 | Failure of Column
89.288 | 5357.2813 | 80.5156 | 1100.2327 | Failure of Column |  | 280.6195 | 16837.1699 | 94.303 | 4060.9844 | Failure of Column
92.4769 | 5548.6128 | 80.9405 | 1145.1997 | Failure of Column |  | 283.8084 | 17028.5014 | 94.4385 | 4113.4502 | Failure of Column
95.6657 | 5739.9443 | 81.3509 | 1190.3946 | Failure of Column |  | 286.9972 | 17219.8329 | 94.5724 | 4165.9904 | Failure of Column
98.8546 | 5931.2758 | 81.7476 | 1235.8099 | Failure of Column |  | 290.1861 | 17411.1643 | 94.7049 | 4218.6043 | Failure of Column
102.0435 | 6122.6072 | 82.1315 | 1281.4385 | Failure of Column |  | 293.3749 | 17602.4958 | 94.8359 | 4271.2909 | Failure of Column
105.2323 | 6313.9387 | 82.5035 | 1327.2738 | Failure of Column |  | 296.5638 | 17793.8273 | 94.9655 | 4324.0495 | Failure of Column
108.4212 | 6505.2702 | 82.8642 | 1373.3094 | Failure of Column |  | 299.7526 | 17985.1588 | 95.0937 | 4376.8793 | Failure of Column
111.61 | 6696.6017 | 83.2143 | 1419.5396 | Failure of Column |  | 302.9415 | 18176.4903 | 95.2206 | 4429.7796 | Failure of Column
114.7989 | 6887.9331 | 83.5545 | 1465.9587 | Failure of Column |  | 306.1304 | 18367.8217 | 95.3461 | 4482.7497 | Failure of Column
117.9877 | 7079.2646 | 83.8852 | 1512.5616 | Failure of Column |  | 309.3192 | 18559.1532 | 95.4703 | 4535.7887 | Failure of Column
121.1766 | 7270.5961 | 84.207 | 1559.3433 | Failure of Column |  | 312.5081 | 18750.4847 | 95.5932 | 4588.896 | Failure of Column
124.3655 | 7461.9276 | 84.5204 | 1606.2991 | Failure of Column |  | 315.6969 | 18941.8162 | 95.7149 | 4642.071 | Failure of Column
127.5543 | 7653.2591 | 84.8257 | 1653.4245 | Failure of Column |  | 318.8858 | 19133.1476 | 95.8353 | 4695.3128 | Failure of Column
130.7432 | 7844.5905 | 85.1234 | 1700.7153 | Failure of Column |  | 322.0747 | 19324.4791 | 95.9545 | 4748.6209 | Failure of Column
133.932 | 8035.922 | 85.4139 | 1748.1675 | Failure of Column |  | 325.2635 | 19515.8106 | 96.0726 | 4801.9945 | Failure of Column
137.1209 | 8227.2535 | 85.6975 | 1795.7772 | Failure of Column |  | 328.4524 | 19707.1421 | 96.1895 | 4855.4331 | Failure of Column
140.3097 | 8418.585 | 85.9745 | 1843.5408 | Failure of Column |  | 331.6412 | 19898.4735 | 96.3053 | 4908.9361 | Failure of Column
143.4986 | 8609.9164 | 86.2452 | 1891.4548 | Failure of Column |  | 334.8301 | 20089.805 | 96.4199 | 4962.5027 | Failure of Column
146.6875 | 8801.2479 | 86.5099 | 1939.5158 | Failure of Column |  | 338.0189 | 20281.1365 | 96.5335 | 5016.1324 | Failure of Column
149.8763 | 8992.5794 | 86.7689 | 1987.7208 | Failure of Column |  | 341.2078 | 20472.468 | 96.646 | 5069.8246 | Failure of Column
153.0652 | 9183.9109 | 87.0223 | 2036.0665 | Failure of Column |  | 344.3967 | 20663.7994 | 96.7574 | 5123.5787 | Failure of Column
156.254 | 9375.2423 | 87.2705 | 2084.5501 | Failure of Column |  | 347.5855 | 20855.1309 | 96.8678 | 5177.3942 | Failure of Column
159.4429 | 9566.5738 | 87.5136 | 2133.1688 | Failure of Column |  | 350.7744 | 21046.4624 | 96.9772 | 5231.2704 | Failure of Column
162.6318 | 9757.9053 | 87.7519 | 2181.9199 | Failure of Column |  | 353.9632 | 21237.7939 | 97.0856 | 5285.2068 | Failure of Column
165.8206 | 9949.2368 | 87.9855 | 2230.8007 | Failure of Column |  | 357.1521 | 21429.1253 | 97.1931 | 5339.203 | Failure of Column
169.0095 | 10140.5682 | 88.2147 | 2279.8089 | Failure of Column |  | 360.3409 | 21620.4568 | 97.2995 | 5393.2583 | Failure of Column
172.1983 | 10331.8997 | 88.4395 | 2328.9419 | Failure of Column |  | 363.5298 | 21811.7883 | 97.4051 | 5447.3722 | Failure of Column
175.3872 | 10523.2312 | 88.6601 | 2378.1975 | Failure of Column |  | 366.7187 | 22003.1198 | 97.5097 | 5501.5442 | Failure of Column
178.576 | 10714.5627 | 88.8768 | 2427.5735 | Failure of Column |  | 369.9075 | 22194.4513 | 97.6134 | 5555.7739 | Failure of Column
181.7649 | 10905.8942 | 89.0896 | 2477.0677 | Failure of Column |  | 373.0964 | 22385.7827 | 97.7162 | 5610.0606 | Failure of Column
184.9538 | 11097.2256 | 89.2986 | 2526.678 | Failure of Column |  | 376.2852 | 22577.1142 | 97.8181 | 5664.404 | Failure of Column
188.1426 | 11288.5571 | 89.5041 | 2576.4025 | Failure of Column |  | 379.4741 | 22768.4457 | 97.9191 | 5718.8035 | Failure of Column
191.3315 | 11479.8886 | 89.706 | 2626.2392 | Failure of Column |  | 382.663 | 22959.7772 | 98.0194 | 5773.2587 | Failure of Column
The Failure Temperature for Steel Beams is Assumed at 1000 °F (538 °C)
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | January 2005
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and |  |  |  |  | March 2011
print layout.

## Data
SECTIONAL FACTORS FOR STEEL MEMBERS
| BEAMS |  | COLUMNS
| Structural Shape | W/D Ratio | Structural Shape | W/D Ratio
| W Shapes | (lb/ft2) | W Shapes | (lb/ft2)
| 36x300 | 29.6162 | 36x300 | 26.0473
| 36x280 | 27.756 | 36x280 | 24.4097
| 36x260 | 25.8943 | 36x260 | 22.7671
| 36x245 | 24.4816 | 36x245 | 21.5227
| 36x230 | 23.0596 | 36x230 | 20.2703
| 36x210 | 23.2773 | 36x210 | 20.9233
| 36x194 | 21.5965 | 36x194 | 19.4146
| 36x182 | 20.3286 | 36x182 | 18.2746
| 36x170 | 19.053 | 36x170 | 17.1285
| 36x160 | 17.991 | 36x160 | 16.1725
| 36x150 | 16.9213 | 36x150 | 15.2091
| 36x135 | 15.3191 | 36x135 | 13.7638
| 33x241 | 25.3063 | 33x241 | 22.2222
| 33x221 | 23.3194 | 33x221 | 20.474
| 33x201 | 21.314 | 33x201 | 18.7107
| 33x152 | 18.1664 | 33x152 | 16.2901
| 33x141 | 16.9208 | 33x141 | 15.1708
| 33x130 | 15.6705 | 33x130 | 14.0465
| 33x118 | 14.2944 | 33x118 | 12.8098
| 30x211 | 23.9671 | 30x211 | 20.9689
| 30x191 | 21.8161 | 30x191 | 19.0841
| 30x173 | 19.8613 | 30x173 | 17.3709
| 30x132 | 17.4018 | 30x132 | 15.5952
| 30x124 | 16.403 | 30x124 | 14.6992
| 30x116 | 15.4025 | 30x116 | 13.7999
| 30x108 | 14.4008 | 30x108 | 12.8994
| 30x99 | 13.2574 | 30x99 | 11.8729
| 27x178 | 22.1519 | 27x178 | 19.3286
| 27x161 | 20.1418 | 27x161 | 17.5732
| 27x146 | 18.3561 | 27x146 | 16.0132
| 27x114 | 16.3539 | 27x114 | 14.5967
| 27x102 | 14.7124 | 27x102 | 13.1316
| 27x94 | 13.6183 | 27x94 | 12.1526
| 27x84 | 12.236 | 27x84 | 10.9162
| 24x162 | 22.2286 | 24x162 | 19.3606
| 24x146 | 20.1657 | 24x146 | 17.5586
| 24x131 | 18.2124 | 24x131 | 15.8516
| 24x117 | 16.3598 | 24x117 | 14.2365
| 24x104 | 14.6187 | 24x104 | 12.7191
| 24x94 | 15.0832 | 24x94 | 13.4526
| 24x84 | 13.563 | 24x84 | 12.095
| 24x76 | 12.336 | 24x76 | 10.9986
| 24x68 | 11.0983 | 24x68 | 9.8921
| 24x62 | 10.9832 | 24x62 | 9.9492
| 24x55 | 9.7974 | 24x55 | 8.8745
| 21x147 | 21.9923 | 21x147 | 19.025
| 21x132 | 19.8795 | 21x132 | 17.195
| 21x122 | 18.4546 | 21x122 | 15.9616
| 21x111 | 16.8736 | 21x111 | 14.5925
| 21x101 | 15.4218 | 21x101 | 13.3363
| 21x93 | 16.5726 | 21x93 | 14.7307
| 21x83 | 14.889 | 21x83 | 13.2359
| 21x73 | 13.1819 | 21x73 | 11.7191
| 21x68 | 12.3244 | 21x68 | 10.956
| 21x62 | 11.2898 | 21x62 | 10.0351
| 21x57 | 11.2205 | 21x57 | 10.1318
| 21x50 | 9.919 | 21x50 | 8.9526
| 21x44 | 8.7824 | 21x44 | 7.9255
| 18x119 | 20.2769 | 18x119 | 17.4807
| 18x106 | 18.2026 | 18x106 | 15.6882
| 18x97 | 16.7374 | 18x97 | 14.4256
| 18x86 | 14.937 | 18x86 | 12.871
| 18x76 | 13.2799 | 18x76 | 11.4415
| 18x71 | 14.4763 | 18x71 | 12.814
| 18x65 | 13.3174 | 18x65 | 11.7896
| 18x60 | 12.3499 | 18x60 | 10.9339
| 18x55 | 11.3734 | 18x55 | 10.0671
| 18x50 | 10.3887 | 18x50 | 9.1954
| 18x46 | 10.3024 | 18x46 | 9.2555
| 18x40 | 9.02 | 18x40 | 8.104
| 18x35 | 7.9545 | 18x35 | 7.1429
| 16x100 | 18.7368 | 16x100 | 16.1139
| 16x89 | 16.807 | 16x89 | 14.45
| 16x77 | 14.6632 | 16x77 | 12.604
| 16x67 | 12.8486 | 16x67 | 11.0424
| 16x57 | 12.8186 | 16x57 | 11.3095
| 16x50 | 11.3272 | 16x50 | 9.9933
| 16x45 | 10.2515 | 16x45 | 9.0437
| 16x40 | 9.1612 | 16x40 | 8.0822
| 16x36 | 8.2941 | 16x36 | 7.3134
| 16x31 | 7.7849 | 16x31 | 6.9781
| 16x26 | 6.5851 | 16x26 | 5.9002
| 14x730 | 94.836 | 14x730 | 79.4486
| 14x665 | 88.1086 | 14x665 | 73.7387
| 14x605 | 81.6694 | 14x605 | 68.2908
| 14x550 | 75.5841 | 14x550 | 63.1458
| 14x500 | 69.8893 | 14x500 | 58.3317
| 14x455 | 64.6039 | 14x455 | 53.8727
| 14x426 | 61.0935 | 14x426 | 50.9316
| 14x398 | 57.6742 | 14x398 | 48.0483
| 14x370 | 54.1761 | 14x370 | 45.1082
| 14x342 | 50.7293 | 14x342 | 42.1962
| 14x311 | 46.5859 | 14x311 | 38.7378
| 14x283 | 42.8626 | 14x283 | 35.6199
| 14x257 | 39.3392 | 14x257 | 32.673
| 14x233 | 36.0263 | 14x233 | 29.9037
| 14x211 | 32.9344 | 14x211 | 27.3198
| 14x193 | 30.3499 | 14x193 | 25.1684
| 14x176 | 27.8886 | 14x176 | 23.1123
| 14x159 | 25.2923 | 14x159 | 20.9454
| 14x145 | 23.2932 | 14x145 | 19.2905
| 14x132 | 21.9375 | 14x132 | 18.2216
| 14x120 | 20.0585 | 14x120 | 16.6551
| 14x109 | 18.318 | 14x109 | 15.2075
| 14x99 | 16.7218 | 14x99 | 13.8769
| 14x90 | 15.2715 | 14x90 | 12.6701
| 14x82 | 16.9684 | 14x82 | 14.4451
| 14x74 | 15.4033 | 14x74 | 13.1128
| 14x68 | 14.2272 | 14x68 | 12.1086
| 14x61 | 12.8387 | 14x61 | 10.9237
| 14x53 | 12.4025 | 14x53 | 10.7179
| 14x48 | 11.2963 | 14x48 | 9.7594
| 14x43 | 10.1785 | 14x43 | 8.792
| 14x38 | 9.5218 | 14x38 | 8.3425
| 14x34 | 8.5669 | 14x34 | 7.5041
| 14x30 | 7.6062 | 14x30 | 6.6593
| 14x26 | 7.3611 | 14x26 | 6.5809
| 14x22 | 6.2827 | 14x22 | 5.6146
| 12x336 | 57.3991 | 12x336 | 48.2124
| 12x305 | 52.9705 | 12x305 | 44.4552
| 12x279 | 49.1919 | 12x279 | 41.2315
| 12x252 | 45.104 | 12x252 | 37.7764
| 12x230 | 41.6824 | 12x230 | 34.8881
| 12x210 | 38.5144 | 12x210 | 32.2168
| 12x190 | 35.2668 | 12x190 | 29.4878
| 12x170 | 31.9499 | 12x170 | 26.6946
| 12x152 | 28.8973 | 12x152 | 24.127
| 12x136 | 26.1371 | 12x136 | 21.8065
| 12x120 | 23.3085 | 12x120 | 19.4332
| 12x106 | 20.7775 | 12x106 | 17.3203
| 12x96 | 18.9474 | 12x96 | 15.7895
| 12x87 | 17.2833 | 12x87 | 14.394
| 12x79 | 15.7842 | 12x79 | 13.1411
| 12x72 | 14.4578 | 12x72 | 12.0334
| 12x65 | 13.1181 | 12x65 | 10.9152
| 12x58 | 12.9633 | 12x58 | 10.9262
| 12x53 | 11.9068 | 12x53 | 10.03
| 12x50 | 12.5313 | 12x50 | 10.7219
| 12x45 | 11.3481 | 12x45 | 9.707
| 12x40 | 10.1469 | 12x40 | 8.6784
| 12x35 | 9.5281 | 12x35 | 8.2938
| 12x30 | 8.2342 | 12x30 | 7.1656
| 12x26 | 7.1807 | 12x26 | 6.2475
| 12x22 | 7.2948 | 12x22 | 6.5639
| 12x19 | 6.3572 | 12x19 | 5.7186
| 12x16 | 5.4069 | 12x16 | 4.8608
| 12x14 | 4.7552 | 12x14 | 4.2748
| 10x112 | 25.622 | 10x112 | 21.3774
| 10x100 | 23.1392 | 10x100 | 19.2926
| 10x88 | 20.5988 | 10x88 | 17.1624
| 10x77 | 18.2213 | 10x77 | 15.1724
| 10x68 | 16.2388 | 10x68 | 13.5144
| 10x60 | 14.4462 | 10x60 | 12.016
| 10x54 | 13.083 | 10x54 | 10.8798
| 10x49 | 11.9318 | 10x49 | 9.919
| 10x45 | 12.3967 | 10x45 | 10.4692
| 10x39 | 10.8421 | 10x39 | 9.1496
| 10x33 | 9.261 | 10x33 | 7.8076
| 10x30 | 9.5314 | 10x30 | 8.2607
| 10x26 | 8.3311 | 10x26 | 7.2189
| 10x22 | 7.114 | 10x22 | 6.1596
| 10x19 | 7.1161 | 10x19 | 6.3228
| 10x17 | 6.4212 | 10x17 | 5.7015
| 10x15 | 5.7107 | 10x15 | 5.0676
| 10x12 | 4.6095 | 10x12 | 4.0909
| 8x67 | 19.2806 | 8x67 | 16.0864
| 8x58 | 16.9178 | 8x58 | 14.1005
| 8x48 | 14.2117 | 8x48 | 11.8421
| 8x40 | 12.003 | 8x40 | 9.9875
| 8x35 | 10.5823 | 8x35 | 8.8028
| 8x31 | 9.438 | 8x31 | 7.8464
| 8x28 | 9.5577 | 8x28 | 8.0595
| 8x24 | 8.2628 | 8x24 | 6.9649
| 8x21 | 7.9071 | 8x21 | 6.7851
| 8x18 | 6.8419 | 8x18 | 5.8664
| 8x15 | 6.4806 | 8x15 | 5.6622
| 8x13 | 5.6686 | 8x13 | 4.9492
| 8x10 | 4.4021 | 8x10 | 3.8462
| 6x25 | 9.8814 | 6x25 | 8.2327
| 6x20 | 8.016 | 6x20 | 6.6741
| 6x15 | 6.1038 | 6x15 | 5.0733
| 6x16 | 7.9569 | 6x16 | 6.8182
| 6x12 | 6.1017 | 6x12 | 5.2174
| 6x9 | 4.6392 | 6x9 | 3.9677
| 5x19 | 9.1751 | 5x19 | 7.6305
| 5x16 | 7.824 | 5x16 | 6.4997
| 4x13 | 7.82 | 4x13 | 6.5
| User Specified Value | Enter Value | User Specified Value | Enter Value