## Smoke_Visibility
CHAPTER 18
|  | ESTIMATING VISIBILITY THROUGH SMOKE | [5 empty] | Version 1805.1
(English Units)
The following calculations estimate the smoke obscuration during a fire.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from each DROP DOWN MENU for the Situation, Mode of Combustion and Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 30 | ft |  | 9.144 | m
| Compartment Length (lc) |  |  |  | 20 | ft |  | 6.096 | m
| Compartment Height (hc) |  |  |  | 15 | ft |  | 4.572 | m
| Mass of Fuel Burn (Mf) |  |  |  | 1 | lb |  | 0.45359 | kg
| Situation / Proportionality Constant for Visibility (K) |  |  |  | 8
| Mode of Combustion / Specific Extinction Coefficient (am) |  |  |  | 37000 | ft2/lb |  | 7.5782 | m2/g
| Material / Particulate Yield (yp) |  |  |  | 0.018
Calculate
RECOMMENDED SITUATION / PROPORTIONALITY CONSTANTS FOR VISIBILITY
Situation |  |  | Proportionality Constant |  | Select Situation / Proportionality Constant for Visibility (K)
K
Building Components in Reflected Light |  |  | 3 |  | Scroll to desired Situation then
Illuminated Signs |  |  | 8 |  | Click on selection
Reflecting Signs |  |  | 3
User Specified Value |  |  | Enter Value
Reference: John H. Klote & James A. Milke, Principles of Smoke
Management, 2002, Page 31.
MODE OF COMBUSTION / SPECIFIC EXTINCTION COEFFICIENT
Mode of Combustion |  | Specific Extinction Coefficient |  |  | Select Mode of Combustion / Specific Extinction Coefficient (am)
am (ft2/lb)
Flaming Combustion |  | 37000 |  |  | Scroll to desired Mode of Combustion then
Smoldering Combustion |  | 21000 |  |  | Click on selection
User Specified Value |  | Enter Value
Reference: John H. Klote & James A. Milke, Principles of Smoke
Management, 2002, Page 32.
MATERIAL / PARTICULATE YIELD OF SOLID FUELS (WELL-VENTILATED FIRES)
Material |  |  |  | Particulate Yield | Select Material / Particulate Yield (yp)
( yp )
Acrylonitrile-Butadiene-Styrene (ABS) |  |  |  | 0.105 | Scroll to desired Material then
Ethylenetetrafluoroethylene (ETFE; TefzelTM) |  |  |  | 0.042 | Click on selection
Fiberboard |  |  |  | 0.008
Fluorinated Polyethylene-Polypropylene (FEP; TeflonTM) |  |  |  | 0.003
Nylon |  |  |  | 0.075
Perfluoroalkoxy (PFA; TeflonTM) |  |  |  | 0.002
Phenolic Foam |  |  |  | 0.002
Polyester |  |  |  | 0.09
Polyethylene (PE) |  |  |  | 0.06
Polyethylene Foam |  |  |  | 0.076
Polymethylemethacrylate (PMMA; PlexiglasTM) |  |  |  | 0.022
Polypropylene |  |  |  | 0.059
Polystyrene |  |  |  | 0.164
Polystyrene Foam |  |  |  | 0.194
Polyurethane Foam (Flexible) |  |  |  | 0.188
Polyurethane Foam (Rigid) |  |  |  | 0.118
Polyvinylchloride (PVC) |  |  |  | 0.172
Silicone |  |  |  | 0.065
Silicone Rubber |  |  |  | 0.078
Tetrafluoroethylene (TFE; TeflonTM) |  |  |  | 0.003
Wood (Douglas Fir) |  |  |  | 0.018
Wood (Hemlock) |  |  |  | 0.015
Wood (Red Oak) |  |  |  | 0.015
Wool 100% |  |  |  | 0.008
User Specified Value |  |  |  | Enter Value
Reference: John H. Klote & James A. Milke, Principles of Smoke
Management, 2002, Page 35.
ESTIMATING VISIBILITY THROUGH SMOKE
METHOD OF JIN
Reference: John H. Klote & James A. Milke, Principles of Smoke Management, 2002, Page 32.
S = |  | K / am mp
Where,
S = |  | visibility through smoke (ft)
K = |  | proportionality constant
am = |  | specific extinction coefficient (ft2/lb)
mp = |  | mass concentration of particulate (lb/ft3)
Compartment Volume Calculation
V = |  |  |  | wc x lc x hc
Where,
V = |  |  |  | volume of the compartment (ft3)
wc = |  |  |  | compartment width (ft)
lc = |  |  |  | compartment length (ft)
hc = |  |  |  | compartment height (ft)
V = |  |  |  | 9000 |  | ft3
Mass of Particulates Produced (airborne particulate)
Mp = |  |  |  | yp Mf
Where,
Mp = |  |  |  | mass of particulates produced (lb)
yp = |  |  |  | particulates yield
Mf = |  |  |  | mass of fuel consumed (lb)
Mp = |  |  |  | 0.018 |  | lb
Mass Concentration of the Particulates Calculation
mp = |  |  |  | Mp / V
Where,
mp = |  |  |  | mass concentration of the particulates (lb/ft3)
Mp = |  |  |  | mass of particulates produced (lb)
V = |  |  |  | volume of the compartment (m3)
mp = |  |  |  | 2e-06 |  | lb/ft3
Summary of Results
Visibility Through Smoke Calculation
S = |  | K / am mp
Answer | S = | 108.1081 |  |  | ft | 32.9514 |  | m
Visibility in smoke is defined in terms of
the furthest distance at which an object can be perceived.
NOTE:
The above calculations are based on principles developed in the Principles of Smoke Management by Klote and Milke 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [5 empty] | Date
1805.0 | Original issue with final text. | [5 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [5 empty] | March 2011