## THIEF
CHAPTER 19. ESTIMATING THE THERMALLY-INDUCED
|  | ELECTRICAL FAILURE (THIEF) |  |  |  | Version 1805.1
|  | OF CABLES |  |  |  | (English Units)
The following calculations estimate the time to failure of cables exposed to a specified hot gas layer.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU or SELECT CABLE BUTTON.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
Cable Diameter |  |  | 0.66 | in |  |  | 0.008382 | m
Cable Mass per Unit Length |  |  | 0.365 | lb/ft | Do Not Enter Any |  | 0.54318 | kg/m
Cable Jacket Thickness |  |  | 0.06 | in | Values in the |  | 0.001524 | m
Ambient Air Temperature |  |  | 70 | oF | Green Boxes! |  | 294.2611 | K
Failure Temperature |  |  | 392 | oF |  |  | 473.15 | K
Maximum Time |  |  | 4000 | s | They are entered
Conduit Thickness |  |  | 0 | in | automatically |  | 0 | m
Conduit Outside Diameter |  |  | 0 | in | based on the |  | 0 | m
Cable Density |  |  | 2460.9379 | kg/m3 | cable selection.
Cable Insulation Type (Thermoplastic or Thermoset) |  |  | Thermoplastic
Cable Function (Control, Instrumentation or Power) |  |  | Control
Wire Gauge (AWG) |  |  | 10
Number of Conductors |  |  | 7
Cable Location |  |  | Cable Tray
Click to Select Source for Exposure Gas Temperature Profile:
Warning: You MUST Click the Calculate Button Below when Finished Entering or Changing Data!
EXPOSURE GAS TEMPERATURE PROFILE
|  | Time (s) | Gas Temperature (ºF) | Gas Temperature (ºK)
|  | 0 | 77 | 298.15
|  | 60 | 199.8518 | 366.401
|  | 120 | 214.8965 | 374.7591
|  | 180 | 224.5372 | 380.1151
|  | 240 | 263.349 | 401.6772
|  | 300 | 263.349 | 401.6772
|  | 600 | 263.349 | 401.6772
|  | 900 | 263.349 | 401.6772
|  | 1200 | 263.349 | 401.6772
|  | 1500 | 263.349 | 401.6772
|  | 1800 | 263.349 | 401.6772
|  | 2100 | 263.349 | 401.6772
|  | 2400 | 263.349 | 401.6772
|  | 2700 | 263.349 | 401.6772
|  | 3000 | 263.349 | 401.6772
|  | 3300 | 263.349 | 401.6772
|  | 3600 | 263.349 | 401.6772
Answer: |  | Cable does not reach failure temperature in 4000.1 seconds
ESTIMATING THERMALLY-INDUCED ELECTRICAL FAILURE OF CABLES
Reference: NUREG/CR-6931, Vol. 3, Cable Response to Live Fire (CAROLFIRE) Volume 3: Thermally-Induced Electrical Failure (THIEF) Model
ρscs (∂Ts/∂t) = |  | (1/r) (∂/∂r) ksr (∂Ts/∂r)
where,
| ρs = | effective density of solid (kg/m3)
| cs = | specific heat of cable solid (J/kg/K)
| ks = | thermal conductivity of solid (W/m/K)
| r = | radius of conductor (m)
| Ts = | temperature of conductor (oC)
| t = | time (s)
Boundary Condition
| q" = | ks(Ts/r)(R,t)
where,
| R = | radius of cable at boundary (m)
| q" = | axially-symmetric heat flux to the exterior surface of the cable (W/m2)
Solution Scheme (Finite Difference)
Time Step Constraint
| dt= | csρsdr2/(2ks)
| Tin+1 = | Tin + (dt a/(ravg dr))*((ri(Tni+1 - Tin)/dr) - (ri-1(Tni - Tni-1)/dr)
where,
| ri = | radial distance from center for ith element (m)
| ri-1 = | radial distance from center for ith - 1 element (m)
| ravg = | ½ (ri + ri-1)
| Tni = | temperature at ith radial distance from center for time n (K)
| Tni-1 = | temperature at ith-1 radial distance from center for time n (K)
| Tni+1 = | temperature at ith+1 radial distance from center for time n (K)
| Tin+1 = | temperature at ith radial distance from center for time n+1 (K)
| a = | thermal diffusivity of the cable material (m2/s)
| dt = | time step (s)
| dr = | distance between points on radius from center of cable where temperatures are calculated (m)
NOTE:
The above calculations are based on principles developed in the NUREG/CR-6931, Vol. 3, "Cable Response to Live Fire (CAROLFIRE) Volume 3: Thermally-Induced Electrical Failure (THIEF) Model." Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation, and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov, Gabriel.Taylor@nrc.gov, Naeem.Iqbal@nrc.gov, or MarkHenry.Salley@nrc.gov.
Prepared by: |  |  | Date: | Organization:
Checked by: |  |  | Date: | Organization:
Additional Information:
Revision Log | Description of Revision | [5 empty] | Date
1805.1 | Original issue with final text. | [5 empty] | March 2013

## THIEF Results
CHAPTER 19.
ESTIMATING THE THERMALLY-INDUCED
ELECTRICAL FAILURE (THIEF) |  |  |  | Version 1805.1
OF CABLES |  |  |  | (English Units)
RESULTS
| Exposing | Cable | Conduit
Time(s) | Temp(°F) | Temp(°F) | Temp(°F)
5 | 87.5 | 70 | 70
10 | 98.1 | 70 | 70
15 | 107.9 | 70.2 | 70
20 | 118.4 | 70.3 | 70
25 | 128.9 | 70.6 | 70
30 | 138.7 | 70.9 | 70
35 | 149.2 | 71.3 | 70
40 | 159 | 71.8 | 70
45 | 169.6 | 72.3 | 70
50 | 180.1 | 73 | 70
55 | 189.9 | 73.7 | 70
60 | 199.9 | 74.5 | 70
65 | 201.1 | 75.3 | 70
70 | 202.4 | 76.2 | 70
75 | 203.7 | 77.2 | 70
80 | 204.9 | 78.1 | 70
85 | 206.2 | 79 | 70
90 | 207.4 | 79.9 | 70
95 | 208.7 | 80.9 | 70
100 | 210 | 81.8 | 70
105 | 211.2 | 82.7 | 70
110 | 212.5 | 83.6 | 70
115 | 213.7 | 84.4 | 70
120 | 214.9 | 85.3 | 70
125 | 215.8 | 86.2 | 70
130 | 216.5 | 87.1 | 70
135 | 217.3 | 88 | 70
140 | 218.1 | 88.8 | 70
145 | 218.9 | 89.6 | 70
150 | 219.8 | 90.5 | 70
155 | 220.5 | 91.3 | 70
160 | 221.4 | 92.2 | 70
165 | 222.1 | 92.9 | 70
170 | 223 | 93.8 | 70
175 | 223.8 | 94.6 | 70
180 | 224.6 | 95.4 | 70
185 | 227.9 | 96.2 | 70
190 | 231 | 97 | 70
195 | 234.4 | 97.8 | 70
200 | 237.7 | 98.7 | 70
205 | 240.8 | 99.5 | 70
210 | 244.1 | 100.4 | 70
215 | 247.2 | 101.2 | 70
220 | 250.5 | 102.2 | 70
225 | 253.8 | 103.2 | 70
230 | 256.9 | 104.1 | 70
235 | 260.3 | 105.1 | 70
240 | 263.3 | 106 | 70
245 | 263.3 | 107.1 | 70
250 | 263.3 | 108.2 | 70
255 | 263.3 | 109.1 | 70
260 | 263.3 | 110.2 | 70
265 | 263.3 | 111.2 | 70
270 | 263.3 | 112.2 | 70
275 | 263.3 | 113.2 | 70
280 | 263.3 | 114.1 | 70
285 | 263.3 | 115.1 | 70
290 | 263.3 | 116 | 70
295 | 263.3 | 117 | 70
300 | 263.3 | 117.9 | 70
305 | 263.3 | 118.8 | 70
310 | 263.3 | 119.7 | 70
315 | 263.3 | 120.6 | 70
320 | 263.3 | 121.4 | 70
325 | 263.3 | 122.3 | 70
330 | 263.3 | 123.1 | 70
335 | 263.3 | 124 | 70
340 | 263.3 | 124.9 | 70
345 | 263.3 | 125.7 | 70
350 | 263.3 | 126.5 | 70
355 | 263.3 | 127.3 | 70
360 | 263.3 | 128.1 | 70
365 | 263.3 | 129 | 70
370 | 263.3 | 129.7 | 70
375 | 263.3 | 130.5 | 70
380 | 263.3 | 131.3 | 70
385 | 263.3 | 132.1 | 70
390 | 263.3 | 132.9 | 70
395 | 263.3 | 133.6 | 70
400 | 263.3 | 134.4 | 70
405 | 263.3 | 135.1 | 70
410 | 263.3 | 135.8 | 70
415 | 263.3 | 136.6 | 70
420 | 263.3 | 137.3 | 70
425 | 263.3 | 138.1 | 70
430 | 263.3 | 138.7 | 70
435 | 263.3 | 139.5 | 70
440 | 263.3 | 140.2 | 70
445 | 263.3 | 140.9 | 70
450 | 263.3 | 141.6 | 70
455 | 263.3 | 142.3 | 70
460 | 263.3 | 143 | 70
465 | 263.3 | 143.7 | 70
470 | 263.3 | 144.4 | 70
475 | 263.3 | 145.1 | 70
480 | 263.3 | 145.7 | 70
485 | 263.3 | 146.4 | 70
490 | 263.3 | 147.1 | 70
495 | 263.3 | 147.7 | 70
500 | 263.3 | 148.4 | 70
505 | 263.3 | 149.1 | 70
510 | 263.3 | 149.7 | 70
515 | 263.3 | 150.4 | 70
520 | 263.3 | 151 | 70
525 | 263.3 | 151.7 | 70
530 | 263.3 | 152.3 | 70
535 | 263.3 | 152.9 | 70
540 | 263.3 | 153.6 | 70
545 | 263.3 | 154.2 | 70
550 | 263.3 | 154.8 | 70
555 | 263.3 | 155.4 | 70
560 | 263.3 | 156.1 | 70
565 | 263.3 | 156.7 | 70
570 | 263.3 | 157.3 | 70
575 | 263.3 | 157.9 | 70
580 | 263.3 | 158.5 | 70
585 | 263.3 | 159.1 | 70
590 | 263.3 | 159.7 | 70
595 | 263.3 | 160.3 | 70
600 | 263.3 | 160.9 | 70
605 | 263.3 | 161.4 | 70
610 | 263.3 | 162 | 70
615 | 263.3 | 162.6 | 70
620 | 263.3 | 163.2 | 70
625 | 263.3 | 163.8 | 70
630 | 263.3 | 164.4 | 70
635 | 263.3 | 164.9 | 70
640 | 263.3 | 165.5 | 70
645 | 263.3 | 166 | 70
650 | 263.3 | 166.6 | 70
655 | 263.3 | 167.2 | 70
660 | 263.3 | 167.7 | 70
665 | 263.3 | 168.3 | 70
670 | 263.3 | 168.8 | 70
675 | 263.3 | 169.3 | 70
680 | 263.3 | 169.9 | 70
685 | 263.3 | 170.4 | 70
690 | 263.3 | 171 | 70
695 | 263.3 | 171.5 | 70
700 | 263.3 | 172 | 70
705 | 263.3 | 172.6 | 70
710 | 263.3 | 173.1 | 70
715 | 263.3 | 173.6 | 70
720 | 263.3 | 174.1 | 70
725 | 263.3 | 174.6 | 70
730 | 263.3 | 175.1 | 70
735 | 263.3 | 175.6 | 70
740 | 263.3 | 176.2 | 70
745 | 263.3 | 176.6 | 70
750 | 263.3 | 177.1 | 70
755 | 263.3 | 177.7 | 70
760 | 263.3 | 178.1 | 70
765 | 263.3 | 178.6 | 70
770 | 263.3 | 179.1 | 70
775 | 263.3 | 179.6 | 70
780 | 263.3 | 180.1 | 70
785 | 263.3 | 180.6 | 70
790 | 263.3 | 181.1 | 70
795 | 263.3 | 181.5 | 70
800 | 263.3 | 182 | 70
805 | 263.3 | 182.5 | 70
810 | 263.3 | 182.9 | 70
815 | 263.3 | 183.4 | 70
820 | 263.3 | 183.9 | 70
825 | 263.3 | 184.3 | 70
830 | 263.3 | 184.8 | 70
835 | 263.3 | 185.2 | 70
840 | 263.3 | 185.7 | 70
845 | 263.3 | 186.1 | 70
850 | 263.3 | 186.6 | 70
855 | 263.3 | 187.1 | 70
860 | 263.3 | 187.5 | 70
865 | 263.3 | 187.9 | 70
870 | 263.3 | 188.4 | 70
875 | 263.3 | 188.8 | 70
880 | 263.3 | 189.3 | 70
885 | 263.3 | 189.7 | 70
890 | 263.3 | 190.1 | 70
895 | 263.3 | 190.5 | 70
900 | 263.3 | 190.9 | 70
905 | 263.3 | 191.4 | 70
910 | 263.3 | 191.8 | 70
915 | 263.3 | 192.2 | 70
920 | 263.3 | 192.6 | 70
925 | 263.3 | 193 | 70
930 | 263.3 | 193.5 | 70
935 | 263.3 | 193.8 | 70
940 | 263.3 | 194.3 | 70
945 | 263.3 | 194.7 | 70
950 | 263.3 | 195.1 | 70
955 | 263.3 | 195.5 | 70
960 | 263.3 | 195.9 | 70
965 | 263.3 | 196.3 | 70
970 | 263.3 | 196.7 | 70
975 | 263.3 | 197 | 70
980 | 263.3 | 197.4 | 70
985 | 263.3 | 197.8 | 70
990 | 263.3 | 198.2 | 70
995 | 263.3 | 198.6 | 70
1000 | 263.3 | 199 | 70
1005 | 263.3 | 199.3 | 70
1010 | 263.3 | 199.7 | 70
1015 | 263.3 | 200.1 | 70
1020 | 263.3 | 200.5 | 70
1025 | 263.3 | 200.8 | 70
1030 | 263.3 | 201.2 | 70
1035 | 263.3 | 201.5 | 70
1040 | 263.3 | 201.9 | 70
1045 | 263.3 | 202.3 | 70
1050 | 263.3 | 202.6 | 70
1055 | 263.3 | 203 | 70
1060 | 263.3 | 203.3 | 70
1065 | 263.3 | 203.7 | 70
1070 | 263.3 | 204.1 | 70
1075 | 263.3 | 204.4 | 70
1080 | 263.3 | 204.8 | 70
1085 | 263.3 | 205.1 | 70
1090 | 263.3 | 205.4 | 70
1095 | 263.3 | 205.8 | 70
1100 | 263.3 | 206.1 | 70
1105 | 263.3 | 206.5 | 70
1110 | 263.3 | 206.8 | 70
1115 | 263.3 | 207.1 | 70
1120 | 263.3 | 207.5 | 70
1125 | 263.3 | 207.8 | 70
1130 | 263.3 | 208.1 | 70
1135 | 263.3 | 208.4 | 70
1140 | 263.3 | 208.8 | 70
1145 | 263.3 | 209.1 | 70
1150 | 263.3 | 209.4 | 70
1155 | 263.3 | 209.7 | 70
1160 | 263.3 | 210 | 70
1165 | 263.3 | 210.4 | 70
1170 | 263.3 | 210.7 | 70
1175 | 263.3 | 211 | 70
1180 | 263.3 | 211.3 | 70
1185 | 263.3 | 211.6 | 70
1190 | 263.3 | 211.9 | 70
1195 | 263.3 | 212.2 | 70
1200 | 263.3 | 212.5 | 70
1205 | 263.3 | 212.8 | 70
1210 | 263.3 | 213.1 | 70
1215 | 263.3 | 213.4 | 70
1220 | 263.3 | 213.7 | 70
1225 | 263.3 | 214 | 70
1230 | 263.3 | 214.3 | 70
1235 | 263.3 | 214.6 | 70
1240 | 263.3 | 214.9 | 70
1245 | 263.3 | 215.2 | 70
1250 | 263.3 | 215.4 | 70
1255 | 263.3 | 215.7 | 70
1260 | 263.3 | 216 | 70
1265 | 263.3 | 216.3 | 70
1270 | 263.3 | 216.6 | 70
1275 | 263.3 | 216.8 | 70
1280 | 263.3 | 217.1 | 70
1285 | 263.3 | 217.4 | 70
1290 | 263.3 | 217.7 | 70
1295 | 263.3 | 218 | 70
1300 | 263.3 | 218.2 | 70
1305 | 263.3 | 218.5 | 70
1310 | 263.3 | 218.8 | 70
1315 | 263.3 | 219 | 70
1320 | 263.3 | 219.3 | 70
1325 | 263.3 | 219.5 | 70
1330 | 263.3 | 219.8 | 70
1335 | 263.3 | 220.1 | 70
1340 | 263.3 | 220.3 | 70
1345 | 263.3 | 220.6 | 70
1350 | 263.3 | 220.8 | 70
1355 | 263.3 | 221.1 | 70
1360 | 263.3 | 221.3 | 70
1365 | 263.3 | 221.6 | 70
1370 | 263.3 | 221.8 | 70
1375 | 263.3 | 222.1 | 70
1380 | 263.3 | 222.3 | 70
1385 | 263.3 | 222.6 | 70
1390 | 263.3 | 222.8 | 70
1395 | 263.3 | 223.1 | 70
1400 | 263.3 | 223.3 | 70
1405 | 263.3 | 223.5 | 70
1410 | 263.3 | 223.8 | 70
1415 | 263.3 | 224 | 70
1420 | 263.3 | 224.3 | 70
1425 | 263.3 | 224.5 | 70
1430 | 263.3 | 224.7 | 70
1435 | 263.3 | 224.9 | 70
1440 | 263.3 | 225.2 | 70
1445 | 263.3 | 225.4 | 70
1450 | 263.3 | 225.6 | 70
1455 | 263.3 | 225.9 | 70
1460 | 263.3 | 226.1 | 70
1465 | 263.3 | 226.3 | 70
1470 | 263.3 | 226.5 | 70
1475 | 263.3 | 226.7 | 70
1480 | 263.3 | 227 | 70
1485 | 263.3 | 227.2 | 70
1490 | 263.3 | 227.4 | 70
1495 | 263.3 | 227.6 | 70
1500 | 263.3 | 227.8 | 70
1505 | 263.3 | 228 | 70
1510 | 263.3 | 228.3 | 70
1515 | 263.3 | 228.5 | 70
1520 | 263.3 | 228.7 | 70
1525 | 263.3 | 228.9 | 70
1530 | 263.3 | 229.1 | 70
1535 | 263.3 | 229.3 | 70
1540 | 263.3 | 229.5 | 70
1545 | 263.3 | 229.7 | 70
1550 | 263.3 | 229.9 | 70
1555 | 263.3 | 230.1 | 70
1560 | 263.3 | 230.3 | 70
1565 | 263.3 | 230.5 | 70
1570 | 263.3 | 230.7 | 70
1575 | 263.3 | 230.9 | 70
1580 | 263.3 | 231.1 | 70
1585 | 263.3 | 231.3 | 70
1590 | 263.3 | 231.5 | 70
1595 | 263.3 | 231.7 | 70
1600 | 263.3 | 231.9 | 70
1605 | 263.3 | 232 | 70
1610 | 263.3 | 232.2 | 70
1615 | 263.3 | 232.4 | 70
1620 | 263.3 | 232.6 | 70
1625 | 263.3 | 232.8 | 70
1630 | 263.3 | 233 | 70
1635 | 263.3 | 233.2 | 70
1640 | 263.3 | 233.3 | 70
1645 | 263.3 | 233.5 | 70
1650 | 263.3 | 233.7 | 70
1655 | 263.3 | 233.9 | 70
1660 | 263.3 | 234 | 70
1665 | 263.3 | 234.2 | 70
1670 | 263.3 | 234.4 | 70
1675 | 263.3 | 234.6 | 70
1680 | 263.3 | 234.7 | 70
1685 | 263.3 | 234.9 | 70
1690 | 263.3 | 235.1 | 70
1695 | 263.3 | 235.3 | 70
1700 | 263.3 | 235.4 | 70
1705 | 263.3 | 235.6 | 70
1710 | 263.3 | 235.8 | 70
1715 | 263.3 | 235.9 | 70
1720 | 263.3 | 236.1 | 70
1725 | 263.3 | 236.3 | 70
1730 | 263.3 | 236.4 | 70
1735 | 263.3 | 236.6 | 70
1740 | 263.3 | 236.7 | 70
1745 | 263.3 | 236.9 | 70
1750 | 263.3 | 237.1 | 70
1755 | 263.3 | 237.2 | 70
1760 | 263.3 | 237.4 | 70
1765 | 263.3 | 237.5 | 70
1770 | 263.3 | 237.7 | 70
1775 | 263.3 | 237.8 | 70
1780 | 263.3 | 238 | 70
1785 | 263.3 | 238.2 | 70
1790 | 263.3 | 238.3 | 70
1795 | 263.3 | 238.5 | 70
1800 | 263.3 | 238.6 | 70
1805 | 263.3 | 238.8 | 70
1810 | 263.3 | 238.9 | 70
1815 | 263.3 | 239 | 70
1820 | 263.3 | 239.2 | 70
1825 | 263.3 | 239.3 | 70
1830 | 263.3 | 239.5 | 70
1835 | 263.3 | 239.6 | 70
1840 | 263.3 | 239.8 | 70
1845 | 263.3 | 239.9 | 70
1850 | 263.3 | 240.1 | 70
1855 | 263.3 | 240.2 | 70
1860 | 263.3 | 240.3 | 70
1865 | 263.3 | 240.5 | 70
1870 | 263.3 | 240.6 | 70
1875 | 263.3 | 240.8 | 70
1880 | 263.3 | 240.9 | 70
1885 | 263.3 | 241 | 70
1890 | 263.3 | 241.2 | 70
1895 | 263.3 | 241.3 | 70
1900 | 263.3 | 241.4 | 70
1905 | 263.3 | 241.6 | 70
1910 | 263.3 | 241.7 | 70
1915 | 263.3 | 241.8 | 70
1920 | 263.3 | 242 | 70
1925 | 263.3 | 242.1 | 70
1930 | 263.3 | 242.2 | 70
1935 | 263.3 | 242.3 | 70
1940 | 263.3 | 242.5 | 70
1945 | 263.3 | 242.6 | 70
1950 | 263.3 | 242.7 | 70
1955 | 263.3 | 242.8 | 70
1960 | 263.3 | 243 | 70
1965 | 263.3 | 243.1 | 70
1970 | 263.3 | 243.2 | 70
1975 | 263.3 | 243.3 | 70
1980 | 263.3 | 243.5 | 70
1985 | 263.3 | 243.6 | 70
1990 | 263.3 | 243.7 | 70
1995 | 263.3 | 243.8 | 70
2000 | 263.3 | 243.9 | 70
2005 | 263.3 | 244 | 70
2010 | 263.3 | 244.2 | 70
2015 | 263.3 | 244.3 | 70
2020 | 263.3 | 244.4 | 70
2025 | 263.3 | 244.5 | 70
2030 | 263.3 | 244.6 | 70
2035 | 263.3 | 244.7 | 70
2040 | 263.3 | 244.9 | 70
2045 | 263.3 | 245 | 70
2050 | 263.3 | 245.1 | 70
2055 | 263.3 | 245.2 | 70
2060 | 263.3 | 245.3 | 70
2065 | 263.3 | 245.4 | 70
2070 | 263.3 | 245.5 | 70
2075 | 263.3 | 245.6 | 70
2080 | 263.3 | 245.7 | 70
2085 | 263.3 | 245.8 | 70
2090 | 263.3 | 245.9 | 70
2095 | 263.3 | 246 | 70
2100 | 263.3 | 246.2 | 70
2105 | 263.3 | 246.3 | 70
2110 | 263.3 | 246.4 | 70
2115 | 263.3 | 246.5 | 70
2120 | 263.3 | 246.6 | 70
2125 | 263.3 | 246.7 | 70
2130 | 263.3 | 246.8 | 70
2135 | 263.3 | 246.9 | 70
2140 | 263.3 | 247 | 70
2145 | 263.3 | 247.1 | 70
2150 | 263.3 | 247.2 | 70
2155 | 263.3 | 247.3 | 70
2160 | 263.3 | 247.4 | 70
2165 | 263.3 | 247.5 | 70
2170 | 263.3 | 247.6 | 70
2175 | 263.3 | 247.7 | 70
2180 | 263.3 | 247.8 | 70
2185 | 263.3 | 247.8 | 70
2190 | 263.3 | 247.9 | 70
2195 | 263.3 | 248 | 70
2200 | 263.3 | 248.1 | 70
2205 | 263.3 | 248.2 | 70
2210 | 263.3 | 248.3 | 70
2215 | 263.3 | 248.4 | 70
2220 | 263.3 | 248.5 | 70
2225 | 263.3 | 248.6 | 70
2230 | 263.3 | 248.7 | 70
2235 | 263.3 | 248.8 | 70
2240 | 263.3 | 248.9 | 70
2245 | 263.3 | 248.9 | 70
2250 | 263.3 | 249 | 70
2255 | 263.3 | 249.1 | 70
2260 | 263.3 | 249.2 | 70
2265 | 263.3 | 249.3 | 70
2270 | 263.3 | 249.4 | 70
2275 | 263.3 | 249.5 | 70
2280 | 263.3 | 249.5 | 70
2285 | 263.3 | 249.6 | 70
2290 | 263.3 | 249.7 | 70
2295 | 263.3 | 249.8 | 70
2300 | 263.3 | 249.9 | 70
2305 | 263.3 | 250 | 70
2310 | 263.3 | 250 | 70
2315 | 263.3 | 250.1 | 70
2320 | 263.3 | 250.2 | 70
2325 | 263.3 | 250.3 | 70
2330 | 263.3 | 250.4 | 70
2335 | 263.3 | 250.4 | 70
2340 | 263.3 | 250.5 | 70
2345 | 263.3 | 250.6 | 70
2350 | 263.3 | 250.7 | 70
2355 | 263.3 | 250.8 | 70
2360 | 263.3 | 250.8 | 70
2365 | 263.3 | 250.9 | 70
2370 | 263.3 | 251 | 70
2375 | 263.3 | 251.1 | 70
2380 | 263.3 | 251.1 | 70
2385 | 263.3 | 251.2 | 70
2390 | 263.3 | 251.3 | 70
2395 | 263.3 | 251.3 | 70
2400 | 263.3 | 251.4 | 70
2405 | 263.3 | 251.5 | 70
2410 | 263.3 | 251.6 | 70
2415 | 263.3 | 251.6 | 70
2420 | 263.3 | 251.7 | 70
2425 | 263.3 | 251.8 | 70
2430 | 263.3 | 251.9 | 70
2435 | 263.3 | 251.9 | 70
2440 | 263.3 | 252 | 70
2445 | 263.3 | 252.1 | 70
2450 | 263.3 | 252.1 | 70
2455 | 263.3 | 252.2 | 70
2460 | 263.3 | 252.3 | 70
2465 | 263.3 | 252.3 | 70
2470 | 263.3 | 252.4 | 70
2475 | 263.3 | 252.5 | 70
2480 | 263.3 | 252.5 | 70
2485 | 263.3 | 252.6 | 70
2490 | 263.3 | 252.7 | 70
2495 | 263.3 | 252.7 | 70
2500 | 263.3 | 252.8 | 70
2505 | 263.3 | 252.9 | 70
2510 | 263.3 | 252.9 | 70
2515 | 263.3 | 253 | 70
2520 | 263.3 | 253.1 | 70
2525 | 263.3 | 253.1 | 70
2530 | 263.3 | 253.2 | 70
2535 | 263.3 | 253.2 | 70
2540 | 263.3 | 253.3 | 70
2545 | 263.3 | 253.4 | 70
2550 | 263.3 | 253.4 | 70
2555 | 263.3 | 253.5 | 70
2560 | 263.3 | 253.5 | 70
2565 | 263.3 | 253.6 | 70
2570 | 263.3 | 253.7 | 70
2575 | 263.3 | 253.7 | 70
2580 | 263.3 | 253.8 | 70
2585 | 263.3 | 253.8 | 70
2590 | 263.3 | 253.9 | 70
2595 | 263.3 | 254 | 70
2600 | 263.3 | 254 | 70
2605 | 263.3 | 254.1 | 70
2610 | 263.3 | 254.1 | 70
2615 | 263.3 | 254.2 | 70
2620 | 263.3 | 254.2 | 70
2625 | 263.3 | 254.3 | 70
2630 | 263.3 | 254.3 | 70
2635 | 263.3 | 254.4 | 70
2640 | 263.3 | 254.5 | 70
2645 | 263.3 | 254.5 | 70
2650 | 263.3 | 254.6 | 70
2655 | 263.3 | 254.6 | 70
2660 | 263.3 | 254.7 | 70
2665 | 263.3 | 254.7 | 70
2670 | 263.3 | 254.8 | 70
2675 | 263.3 | 254.8 | 70
2680 | 263.3 | 254.9 | 70
2685 | 263.3 | 254.9 | 70
2690 | 263.3 | 255 | 70
2695 | 263.3 | 255 | 70
2700 | 263.3 | 255.1 | 70
2705 | 263.3 | 255.1 | 70
2710 | 263.3 | 255.2 | 70
2715 | 263.3 | 255.2 | 70
2720 | 263.3 | 255.3 | 70
2725 | 263.3 | 255.3 | 70
2730 | 263.3 | 255.4 | 70
2735 | 263.3 | 255.4 | 70
2740 | 263.3 | 255.5 | 70
2745 | 263.3 | 255.5 | 70
2750 | 263.3 | 255.6 | 70
2755 | 263.3 | 255.6 | 70
2760 | 263.3 | 255.7 | 70
2765 | 263.3 | 255.7 | 70
2770 | 263.3 | 255.8 | 70
2775 | 263.3 | 255.8 | 70
2780 | 263.3 | 255.9 | 70
2785 | 263.3 | 255.9 | 70
2790 | 263.3 | 255.9 | 70
2795 | 263.3 | 256 | 70
2800 | 263.3 | 256 | 70
2805 | 263.3 | 256.1 | 70
2810 | 263.3 | 256.1 | 70
2815 | 263.3 | 256.2 | 70
2820 | 263.3 | 256.2 | 70
2825 | 263.3 | 256.3 | 70
2830 | 263.3 | 256.3 | 70
2835 | 263.3 | 256.3 | 70
2840 | 263.3 | 256.4 | 70
2845 | 263.3 | 256.4 | 70
2850 | 263.3 | 256.5 | 70
2855 | 263.3 | 256.5 | 70
2860 | 263.3 | 256.6 | 70
2865 | 263.3 | 256.6 | 70
2870 | 263.3 | 256.6 | 70
2875 | 263.3 | 256.7 | 70
2880 | 263.3 | 256.7 | 70
2885 | 263.3 | 256.8 | 70
2890 | 263.3 | 256.8 | 70
2895 | 263.3 | 256.8 | 70
2900 | 263.3 | 256.9 | 70
2905 | 263.3 | 256.9 | 70
2910 | 263.3 | 257 | 70
2915 | 263.3 | 257 | 70
2920 | 263.3 | 257 | 70
2925 | 263.3 | 257.1 | 70
2930 | 263.3 | 257.1 | 70
2935 | 263.3 | 257.2 | 70
2940 | 263.3 | 257.2 | 70
2945 | 263.3 | 257.2 | 70
2950 | 263.3 | 257.3 | 70
2955 | 263.3 | 257.3 | 70
2960 | 263.3 | 257.3 | 70
2965 | 263.3 | 257.4 | 70
2970 | 263.3 | 257.4 | 70
2975 | 263.3 | 257.4 | 70
2980 | 263.3 | 257.5 | 70
2985 | 263.3 | 257.5 | 70
2990 | 263.3 | 257.6 | 70
2995 | 263.3 | 257.6 | 70
3000 | 263.3 | 257.6 | 70
3005 | 263.3 | 257.7 | 70
3010 | 263.3 | 257.7 | 70
3015 | 263.3 | 257.7 | 70
3020 | 263.3 | 257.8 | 70
3025 | 263.3 | 257.8 | 70
3030 | 263.3 | 257.8 | 70
3035 | 263.3 | 257.9 | 70
3040 | 263.3 | 257.9 | 70
3045 | 263.3 | 257.9 | 70
3050 | 263.3 | 258 | 70
3055 | 263.3 | 258 | 70
3060 | 263.3 | 258 | 70
3065 | 263.3 | 258.1 | 70
3070 | 263.3 | 258.1 | 70
3075 | 263.3 | 258.1 | 70
3080 | 263.3 | 258.2 | 70
3085 | 263.3 | 258.2 | 70
3090 | 263.3 | 258.2 | 70
3095 | 263.3 | 258.3 | 70
3100 | 263.3 | 258.3 | 70
3105 | 263.3 | 258.3 | 70
3110 | 263.3 | 258.3 | 70
3115 | 263.3 | 258.4 | 70
3120 | 263.3 | 258.4 | 70
3125 | 263.3 | 258.4 | 70
3130 | 263.3 | 258.5 | 70
3135 | 263.3 | 258.5 | 70
3140 | 263.3 | 258.5 | 70
3145 | 263.3 | 258.6 | 70
3150 | 263.3 | 258.6 | 70
3155 | 263.3 | 258.6 | 70
3160 | 263.3 | 258.6 | 70
3165 | 263.3 | 258.7 | 70
3170 | 263.3 | 258.7 | 70
3175 | 263.3 | 258.7 | 70
3180 | 263.3 | 258.8 | 70
3185 | 263.3 | 258.8 | 70
3190 | 263.3 | 258.8 | 70
3195 | 263.3 | 258.8 | 70
3200 | 263.3 | 258.9 | 70
3205 | 263.3 | 258.9 | 70
3210 | 263.3 | 258.9 | 70
3215 | 263.3 | 259 | 70
3220 | 263.3 | 259 | 70
3225 | 263.3 | 259 | 70
3230 | 263.3 | 259 | 70
3235 | 263.3 | 259.1 | 70
3240 | 263.3 | 259.1 | 70
3245 | 263.3 | 259.1 | 70
3250 | 263.3 | 259.1 | 70
3255 | 263.3 | 259.2 | 70
3260 | 263.3 | 259.2 | 70
3265 | 263.3 | 259.2 | 70
3270 | 263.3 | 259.2 | 70
3275 | 263.3 | 259.3 | 70
3280 | 263.3 | 259.3 | 70
3285 | 263.3 | 259.3 | 70
3290 | 263.3 | 259.3 | 70
3295 | 263.3 | 259.4 | 70
3300 | 263.3 | 259.4 | 70
3305 | 263.3 | 259.4 | 70
3310 | 263.3 | 259.4 | 70
3315 | 263.3 | 259.5 | 70
3320 | 263.3 | 259.5 | 70
3325 | 263.3 | 259.5 | 70
3330 | 263.3 | 259.5 | 70
3335 | 263.3 | 259.6 | 70
3340 | 263.3 | 259.6 | 70
3345 | 263.3 | 259.6 | 70
3350 | 263.3 | 259.6 | 70
3355 | 263.3 | 259.6 | 70
3360 | 263.3 | 259.7 | 70
3365 | 263.3 | 259.7 | 70
3370 | 263.3 | 259.7 | 70
3375 | 263.3 | 259.7 | 70
3380 | 263.3 | 259.8 | 70
3385 | 263.3 | 259.8 | 70
3390 | 263.3 | 259.8 | 70
3395 | 263.3 | 259.8 | 70
3400 | 263.3 | 259.8 | 70
3405 | 263.3 | 259.9 | 70
3410 | 263.3 | 259.9 | 70
3415 | 263.3 | 259.9 | 70
3420 | 263.3 | 259.9 | 70
3425 | 263.3 | 260 | 70
3430 | 263.3 | 260 | 70
3435 | 263.3 | 260 | 70
3440 | 263.3 | 260 | 70
3445 | 263.3 | 260 | 70
3450 | 263.3 | 260.1 | 70
3455 | 263.3 | 260.1 | 70
3460 | 263.3 | 260.1 | 70
3465 | 263.3 | 260.1 | 70
3470 | 263.3 | 260.1 | 70
3475 | 263.3 | 260.2 | 70
3480 | 263.3 | 260.2 | 70
3485 | 263.3 | 260.2 | 70
3490 | 263.3 | 260.2 | 70
3495 | 263.3 | 260.2 | 70
3500 | 263.3 | 260.3 | 70
3505 | 263.3 | 260.3 | 70
3510 | 263.3 | 260.3 | 70
3515 | 263.3 | 260.3 | 70
3520 | 263.3 | 260.3 | 70
3525 | 263.3 | 260.3 | 70
3530 | 263.3 | 260.4 | 70
3535 | 263.3 | 260.4 | 70
3540 | 263.3 | 260.4 | 70
3545 | 263.3 | 260.4 | 70
3550 | 263.3 | 260.4 | 70
3555 | 263.3 | 260.5 | 70
3560 | 263.3 | 260.5 | 70
3565 | 263.3 | 260.5 | 70
3570 | 263.3 | 260.5 | 70
3575 | 263.3 | 260.5 | 70
3580 | 263.3 | 260.5 | 70
3585 | 263.3 | 260.6 | 70
3590 | 263.3 | 260.6 | 70
3595 | 263.3 | 260.6 | 70
3600 | 263.3 | 260.6 | 70
3605 | 263.3 | 260.6 | 70
3610 | 263.3 | 260.6 | 70
3615 | 263.3 | 260.7 | 70
3620 | 263.3 | 260.7 | 70
3625 | 263.3 | 260.7 | 70
3630 | 263.3 | 260.7 | 70
3635 | 263.3 | 260.7 | 70
3640 | 263.3 | 260.7 | 70
3645 | 263.3 | 260.8 | 70
3650 | 263.3 | 260.8 | 70
3655 | 263.3 | 260.8 | 70
3660 | 263.3 | 260.8 | 70
3665 | 263.3 | 260.8 | 70
3670 | 263.3 | 260.8 | 70
3675 | 263.3 | 260.8 | 70
3680 | 263.3 | 260.9 | 70
3685 | 263.3 | 260.9 | 70
3690 | 263.3 | 260.9 | 70
3695 | 263.3 | 260.9 | 70
3700 | 263.3 | 260.9 | 70
3705 | 263.3 | 260.9 | 70
3710 | 263.3 | 261 | 70
3715 | 263.3 | 261 | 70
3720 | 263.3 | 261 | 70
3725 | 263.3 | 261 | 70
3730 | 263.3 | 261 | 70
3735 | 263.3 | 261 | 70
3740 | 263.3 | 261 | 70
3745 | 263.3 | 261.1 | 70
3750 | 263.3 | 261.1 | 70
3755 | 263.3 | 261.1 | 70
3760 | 263.3 | 261.1 | 70
3765 | 263.3 | 261.1 | 70
3770 | 263.3 | 261.1 | 70
3775 | 263.3 | 261.1 | 70
3780 | 263.3 | 261.2 | 70
3785 | 263.3 | 261.2 | 70
3790 | 263.3 | 261.2 | 70
3795 | 263.3 | 261.2 | 70
3800 | 263.3 | 261.2 | 70
3805 | 263.3 | 261.2 | 70
3810 | 263.3 | 261.2 | 70
3815 | 263.3 | 261.2 | 70
3820 | 263.3 | 261.3 | 70
3825 | 263.3 | 261.3 | 70
3830 | 263.3 | 261.3 | 70
3835 | 263.3 | 261.3 | 70
3840 | 263.3 | 261.3 | 70
3845 | 263.3 | 261.3 | 70
3850 | 263.3 | 261.3 | 70
3855 | 263.3 | 261.3 | 70
3860 | 263.3 | 261.4 | 70
3865 | 263.3 | 261.4 | 70
3870 | 263.3 | 261.4 | 70
3875 | 263.3 | 261.4 | 70
3880 | 263.3 | 261.4 | 70
3885 | 263.3 | 261.4 | 70
3890 | 263.3 | 261.4 | 70
3895 | 263.3 | 261.4 | 70
3900 | 263.3 | 261.5 | 70
3905 | 263.3 | 261.5 | 70
3910 | 263.3 | 261.5 | 70
3915 | 263.3 | 261.5 | 70
3920 | 263.3 | 261.5 | 70
3925 | 263.3 | 261.5 | 70
3930 | 263.3 | 261.5 | 70
3935 | 263.3 | 261.5 | 70
3940 | 263.3 | 261.5 | 70
3945 | 263.3 | 261.6 | 70
3950 | 263.3 | 261.6 | 70
3955 | 263.3 | 261.6 | 70
3960 | 263.3 | 261.6 | 70
3965 | 263.3 | 261.6 | 70
3970 | 263.3 | 261.6 | 70
3975 | 263.3 | 261.6 | 70
3980 | 263.3 | 261.6 | 70
3985 | 263.3 | 261.6 | 70
3990 | 263.3 | 261.7 | 70
3995 | 263.3 | 261.7 | 70
4000 | 263.3 | 261.7 | 70

## Temperature-NV
CHAPTER 2. PREDICTING HOT GAS LAYER TEMPERATURE
|  | AND SMOKE LAYER HEIGHT IN A ROOM FIRE | [6 empty] | Version 1805.1
|  | WITH NATURAL VENTILATION | [6 empty] | (English Units)
COMPARTMENT WITH THERMALLY THICK/THIN BOUNDARIES
The following calculations estimate the hot gas layer temperature and smoke layer height in enclosure fire.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
|  | Compartment Width (wc) |  |  | 15 | ft |  |  | 4.572 | m
|  | Compartment Length (lc) |  |  | 15 | ft |  |  | 4.572 | m
|  | Compartment Height (hc) |  |  | 10 | ft |  |  | 3.048 | m
|  | Vent Width (wv) |  |  | 4 | ft |  |  | 1.2192 | m
|  | Vent Height (hv) |  |  | 6 | ft |  |  | 1.8288 | m
|  | Top of Vent from Floor (VT) |  |  | 6 | ft |  |  | 1.8288 | m
|  | Interior Lining Thickness (d) |  |  | 1 | in |  |  | 0.0254 | m
AMBIENT CONDITIONS
|  | Ambient Air Temperature (Ta) |  |  | 70 | °F |  |  | 21.1111 | °C
[9 empty] | 294.1111 | °K
|  | Specific Heat of Air (cp) |  |  | 1 | kJ/kg-K
|  | Ambient Air Density (ra) |  |  | 1.2002 | kg/m3
Note: Ambient Air Density (ra) will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES OF COMPARTMENT ENCLOSING SURFACES FOR
|  | Interior Lining Thermal Inertia (krc) |  |  | 2.9 | (kW/m2-K)2-sec
|  | Interior Lining Thermal Conductivity (k) |  |  | 0.0016 | kW/m-K
|  | Interior Lining Specific Heat (c) |  |  | 0.75 | kJ/kg-K
|  | Interior Lining Density (r) |  |  | 2400 | kg/m3
THERMAL PROPERTIES FOR COMMON INTERIOR LINING MATERIALS
|  | Material |  | krc | k | c | r | Select Material
|  |  |  | (kW/m2-K)2-sec | (kW/m-K) | (kJ/kg-K) | (kg/m3)
|  | Aluminum (pure) |  | 500 | 0.206 | 0.895 | 2710 | Scroll to desired material
|  | Steel (0.5% Carbon) |  | 197 | 0.054 | 0.465 | 7850 | Click the selection
|  | Concrete |  | 2.9 | 0.0016 | 0.75 | 2400
|  | Brick |  | 1.7 | 0.0008 | 0.8 | 2600
|  | Glass, Plate |  | 1.6 | 0.00076 | 0.8 | 2710
|  | Brick/Concrete Block |  | 1.2 | 0.00073 | 0.84 | 1900
|  | Gypsum Board |  | 0.18 | 0.00017 | 1.1 | 960
|  | Plywood |  | 0.16 | 0.00012 | 2.5 | 540
|  | Fiber Insulation Board |  | 0.16 | 0.00053 | 1.25 | 240
|  | Chipboard |  | 0.15 | 0.00015 | 1.25 | 800
|  | Aerated Concrete |  | 0.12 | 0.00026 | 0.96 | 500
|  | Plasterboard |  | 0.12 | 0.00016 | 0.84 | 950
|  | Calcium Silicate Board |  | 0.098 | 0.00013 | 1.12 | 700
|  | Alumina Silicate Block |  | 0.036 | 0.00014 | 1 | 260
|  | Glass Fiber Insulation |  | 0.0018 | 3.7e-05 | 0.8 | 60
|  | Expanded Polystyrene |  | 0.001 | 3.4e-05 | 1.5 | 20
|  | User Specified Value |  | Enter Value | Enter Value | Enter Value | Enter Value
Reference: Klote, J., J. Milke, Principles of Smoke Management, 2002, Page 270.
FIRE SPECIFICATIONS
|  | Fire Heat Release Rate (Q) |  |  | 250 | kW
METHOD OF McCAFFREY, QUINTIERE, AND HARKLEROAD (MQH)
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-175.
DTg = 6.85 [Q2/(Av(hv)1/2) (AThk)]1/3
Where,
|  | DTg = | Tg - Ta = upper layer gas temperature rise above ambient (°K)
|  | Q = | heat release rate of the fire (kW)
|  | Av = | area of ventilation opening (m2)
|  | hv = | height of ventilation opening (m)
|  | hk = | convective heat transfer coefficient (kW/m2-K)
|  | AT = | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
Area of Ventilation Opening Calculation
Av = (wv) (hv)
Where,
|  | Av = | area of ventilation opening (m2)
|  | wv = | vent width (m)
|  | hv = | vent height (m)
|  | Av = | 2.2297 |  | m2
Thermal Penetration Time Calculation
tp = (rcp/k) (d/2)2
Where,
|  | tp = | thermal penetration time (sec)
|  | r = | interior construction density (kg/m3)
|  | cp = | interior construction heat capacity (kJ/kg-K)
|  | k = | interior construction thermal conductivity (kW/m-K)
|  | d = | interior construction thickness (m)
|  | tp = | 181.4512 |  | sec
Heat Transfer Coefficient Calculation
hk = √(krc/t) for t < tp or (k/d) for t > tp
Where,
|  | hk = | heat transfer coefficient (kW/m2-K)
|  | krc = | interior construction thermal inertia (kW/m2-K)2-sec
(a thermal property of material responsible for the rate of temperature rise)
|  | t = | time after ignition (sec)
See table below for results
Area of Compartment Enclosing Surface Boundaries
AT = [2(wc x lc) + 2(hc x wc) + 2(hc x lc)] - Av
Where,
|  | AT = | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
|  | wc = | compartment width (m)
|  | lc = | compartment length (m)
|  | hc = | compartment height (m)
|  | Av = | area of ventilation opening (m2)
|  | AT = | 95.3185 |  | m2
Compartment Hot Gas Layer Temperature With Natural Ventilation
DTg = 6.85 [Q2/(Av(hv)1/2) (AThk)]1/3
|  | DTg = |  | Tg - Ta
|  | Tg = |  | DTg + Ta
Results |  | Time After Ignition (t) |  | hk | DTg | Tg | Tg | Tg
|  | (min) | (sec) | (kW/m2-K) | (°K) | (°K) | (°C) | (°F)
|  | 0 | 0 | - | - | 294.1111 | 21.1111 | 70
|  | 1 | 60 | 0.21985 | 68.251 | 362.3621 | 89.3621 | 192.8518
|  | 2 | 120 | 0.15546 | 76.6091 | 370.7203 | 97.7203 | 207.8965
|  | 3 | 180 | 0.12693 | 81.9651 | 376.0762 | 103.0762 | 217.5372
|  | 4 | 240 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 5 | 300 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 10 | 600 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 15 | 900 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 20 | 1200 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 25 | 1500 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 30 | 1800 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 35 | 2100 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 40 | 2400 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 45 | 2700 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 50 | 3000 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 55 | 3300 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
|  | 60 | 3600 | 0.062992 | 103.5272 | 397.6384 | 124.6384 | 256.349
ESTIMATING SMOKE LAYER HEIGHT
METHOD OF YAMANA AND TANAKA
z = ((2kQ1/3t/3Ac) + (1/hc(2/3)))-3/2
Where,
|  |  | z = | smoke layer height (m)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | t = | time after ignition (sec)
|  |  | hc = | compartment height (m)
|  |  | Ac = | compartment floor area (m2)
|  |  | k = | k = a constant given by k = 0.076/rg
|  |  | rg = | hot gas layer density (kg/m3)
rg is given by rg = 353/Tg
|  |  | Tg = | hot gas layer temperature (°K)
Compartment Area Calculation
Ac = (wc) (lc)
Where,
|  |  | Ac = | compartment floor area (m2)
|  |  | wc = | compartment width (m)
|  |  | lc = | compartment length (m)
|  |  | Ac = | 20.9032 |  | m2
Hot Gas Layer Density Calculation
|  |  | rg = | 353/Tg
Calculation for Constant K
|  |  | k = | 0.076/rg
Smoke Gas Layer Height With Natural Ventilation
|  |  | z = | [(2kQ1/3t/3Ac] + (1/hc2/3))-3/2
Results | Caution! The smoke layer height is a conservative estimate and is only intended to provide an indication where the hot gas layer is located. Calculated smoke layer height below the vent height are not creditable since the calculation is not accounting for the smoke exiting the vent.
|  | Time | rg | Constant (k) | Smoke Layer Height | Smoke Layer Height
|  | (min) | (kg/m3) | (kW/m-K) | z (m) | z (ft)
|  | 0 | 1.2002 | 0.063321 | 3.048 | 10
|  | 1 | 0.97416 | 0.078016 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 2 | 0.9522 | 0.079815 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 3 | 0.93864 | 0.080968 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 4 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 5 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 10 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 15 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 20 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 25 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 30 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 35 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 40 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 45 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 50 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 55 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
|  | 60 | 0.88774 | 0.085611 | 1.8288 | 6 | CAUTION: SMOKE IS EXITING OUT VENT
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov and Naeem.Iqbal@nrc.gov or MarkHenry.Salley@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011
Note on F38: This default value (1.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Click Here to Calculate this Sheet and Return to THIEF

## Temperature-FV
CHAPTER 2. PREDICTING HOT GAS LAYER TEMPERATURE
|  | IN A ROOM FIRE | [6 empty] | Version 1805.1
|  | WITH FORCED VENTILATION | [6 empty] | (English Units)
COMPARTMENT WITH THERMALLY THICK/THIN BOUNDARIES
The following calculations estimate the hot gas layer temperature and smoke layer height in enclosure fire.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
|  | Compartment Width (wc) |  |  | 16 | ft |  |  | 4.8768 | m
|  | Compartment Length (lc) |  |  | 16 | ft |  |  | 4.8768 | m
|  | Compartment Height (hc) |  |  | 12 | ft |  |  | 3.6576 | m
|  | Interior Lining Thickness (d) |  |  | 12 | in |  |  | 0.3048 | m
AMBIENT CONDITIONS
|  | Ambient Air Temperature (Ta) |  |  | 70 | °F |  |  | 21.1111 | °C
[9 empty] | 294.1111 | K
|  | Specific Heat of Air (cp) |  |  | 1 | kJ/kg-K
|  | Ambient Air Density (ra) |  |  | 1.2002 | kg/m3
Note: Ambient Air Density (ra) will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES OF COMPARTMENT ENCLOSING SURFACES FOR
|  | Interior Lining Thermal Inertia (krc) |  |  | 2.9 | (kW/m2-K)2-sec
|  | Interior Lining Thermal Conductivity (k) |  |  | 0.0016 | kW/m-K
|  | Interior Lining Specific Heat (c) |  |  | 0.75 | kJ/kg-K
|  | Interior Lining Density (r) |  |  | 2400 | kg/m3
THERMAL PROPERTIES FOR COMMON INTERIOR LINING MATERIALS
|  | Material |  | krc | k | c | r | Select Material
|  |  |  | (kW/m2-K)2-sec | (kW/m-K) | (kJ/kg-K) | (kg/m3)
|  | Aluminum (pure) |  | 500 | 0.206 | 0.895 | 2710 | Scroll to desired material
|  | Steel (0.5% Carbon) |  | 197 | 0.054 | 0.465 | 7850 | Click on selection
|  | Concrete |  | 2.9 | 0.0016 | 0.75 | 2400
|  | Brick |  | 1.7 | 0.0008 | 0.8 | 2600
|  | Glass, Plate |  | 1.6 | 0.00076 | 0.8 | 2710
|  | Brick/Concrete Block |  | 1.2 | 0.00073 | 0.84 | 1900
|  | Gypsum Board |  | 0.18 | 0.00017 | 1.1 | 960
|  | Plywood |  | 0.16 | 0.00012 | 2.5 | 540
|  | Fiber Insulation Board |  | 0.16 | 0.00053 | 1.25 | 240
|  | Chipboard |  | 0.15 | 0.00015 | 1.25 | 800
|  | Aerated Concrete |  | 0.12 | 0.00026 | 0.96 | 500
|  | Plasterboard |  | 0.12 | 0.00016 | 0.84 | 950
|  | Calcium Silicate Board |  | 0.098 | 0.00013 | 1.12 | 700
|  | Alumina Silicate Block |  | 0.036 | 0.00014 | 1 | 260
|  | Glass Fiber Insulation |  | 0.0018 | 3.7e-05 | 0.8 | 60
|  | Expanded Polystyrene |  | 0.001 | 3.4e-05 | 1.5 | 20
|  | User Specified Value |  | Enter Value | Enter Value | Enter Value | Enter Value
Reference: Klote, J., J. Milke, Principles of Smoke Management, 2002 Page 270.
COMPARTMENT MASS VENTILATION FLOW RATE
|  | Forced Ventilation Flow Rate (m) |  |  | 500 | cfm |  |  | 0.23597 | m3/sec
[9 empty] | 0.28322 | kg/sec
FIRE SPECIFICATIONS
|  | Fire Heat Release Rate (Q) |  |  | 250 | kW
METHOD OF FOOTE, PAGNI, AND ALVARES (FPA)
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-177.
DTg/Ta = 0.63(Q/mcpTa)0.72(hkAT/mcp)-0.36
Where,
|  | DTg = | Tg - Ta = upper layer gas temperature rise above ambient (°K)
|  | Ta = | ambient air temperature (°K)
|  | Q = | heat release rate of the fire (kW)
|  | m = | compartment mass ventilation flow rate (kg/sec)
|  | cp = | specific heat of air (kJ/kg-K)
|  | hk = | convective heat transfer coefficient (kW/m2-K)
|  | AT = | total area of the compartment enclosing surface boundaries (m2)
Thermal Penetration Time Calculation
tp = (rcp/k)(δ/2)2
Where,
|  | tp = | thermal penetration time (sec)
|  | r = | interior construction density (kg/m3)
|  | cp = | interior construction heat capacity (kJ/kg-K)
|  | k = | interior construction thermal conductivity (kW/m-K)
|  | d = | interior construction thickness (m)
|  | tp = | 26128.98 |  | sec
Heat Transfer Coefficient Calculation
hk = √(krc/t) for t < tp or (k/δ) for t > tp
Where,
|  | hk = | heat transfer coefficient (kW/m2-K)
|  | krc = | interior construction thermal inertia (kW/m2-K)2-sec
(a thermal property of material responsible for the rate of temperature rise)
|  | t = | time after ignition (sec)
See table below for results
Area of Compartment Enclosing Surface Boundaries
AT = 2 (wc x lc) + 2 (hc x wc) + 2 (hc x lc)
Where,
|  | AT = | total area of the compartment enclosing surface boundaries (m2)
|  | wc = | compartment width (m)
|  | lc = | compartment length (m)
|  | hc = | compartment height (m)
|  | AT = | 118.9159 |  | m2
Compartment Hot Gas Layer Temperature With Forced Ventilation
DTg/Ta = 0.63(Q/mcpTa)0.72(hkAT/mcp)-0.36
|  | DTg = |  | Tg - Ta
|  | Tg = |  | DTg + Ta
| Results | Time After Ignition (t) |  | hk | DTg/Ta | DTg | Tg | Tg | Tg
|  | (min) | (sec) | (kW/m2-K) |  | (°K) | (°K) | (°C) | (°F)
|  | 0 | 0 | - | - | - | 294.1111 | 21.1111 | 70
|  | 1 | 60 | 0.21985 | 0.27259 | 80.1722 | 374.2834 | 101.2834 | 214.31
|  | 2 | 120 | 0.15546 | 0.30881 | 90.8258 | 384.937 | 111.937 | 233.4865
|  | 3 | 180 | 0.12693 | 0.3322 | 97.7025 | 391.8137 | 118.8137 | 245.8646
|  | 4 | 240 | 0.10992 | 0.34985 | 102.8951 | 397.0063 | 124.0063 | 255.2113
|  | 5 | 300 | 0.098319 | 0.36419 | 107.1121 | 401.2232 | 128.2232 | 262.8018
|  | 10 | 600 | 0.069522 | 0.41258 | 121.3456 | 415.4567 | 142.4567 | 288.4221
|  | 15 | 900 | 0.056765 | 0.44382 | 130.5331 | 424.6442 | 151.6442 | 304.9595
|  | 20 | 1200 | 0.04916 | 0.46741 | 137.4705 | 431.5816 | 158.5816 | 317.4469
|  | 25 | 1500 | 0.04397 | 0.48657 | 143.1045 | 437.2156 | 164.2156 | 327.5881
|  | 30 | 1800 | 0.040139 | 0.5028 | 147.8788 | 441.9899 | 168.9899 | 336.1818
|  | 35 | 2100 | 0.037161 | 0.51695 | 152.0395 | 446.1506 | 173.1506 | 343.671
|  | 40 | 2400 | 0.034761 | 0.52952 | 155.7381 | 449.8492 | 176.8492 | 350.3286
|  | 45 | 2700 | 0.032773 | 0.54087 | 159.0751 | 453.1863 | 180.1863 | 356.3353
|  | 50 | 3000 | 0.031091 | 0.55122 | 162.1208 | 456.2319 | 183.2319 | 361.8174
|  | 55 | 3300 | 0.029644 | 0.56076 | 164.9261 | 459.0372 | 186.0372 | 366.867
|  | 60 | 3600 | 0.028382 | 0.56961 | 167.5295 | 461.6406 | 188.6406 | 371.5531
METHOD OF DEAL AND BEYLER
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-178.
Thermal Penetration Time Calculation
tp = (rcp/k) (d)2
Where,
|  | tp = | thermal penetration time (sec)
|  | r = | interior construction density (kg/m3)
|  | cp = | interior construction heat capacity (kJ/kg-K)
|  | k = | interior construction thermal conductivity (kW/m-K)
|  | d = | interior construction thickness (m)
|  | tp = | 104515.92 |  | sec
Heat Transfer Coefficient Calculation
hk = 0.4 √(krc / t) for t < tp or .4(kδ) for t > tp
Where,
|  | hk = | heat transfer coefficient (kW/m2-K)
|  | krc = | interior construction thermal inertia (kW/m2-K)2-sec
(a thermal property of material responsible for the rate of temperature rise)
|  | d = | thickness of interior lining (m)
See table below for results
Area of Compartment Enclosing Surface Boundaries
AT = 2(wc x lc) + 2(hc x wc) + 2(hc x lc)
|  | AT = | 118.9159 |  | m2
Compartment Hot Gas Layer Temperature With Forced Ventilation
DTg = Q / (mcp + hk AT)
Where,
|  | DTg = | Tg - Ta = upper layer gas temperature rise above ambient (°K)
|  | Ta = | ambient air temperature (°K)
|  | Q = | heat release rate of the fire (kW)
|  | m = | compartment mass ventilation flow rate (kg/sec)
|  | cp = | specific heat of air (kJ/Kg-K)
|  | hk = | convective heat transfer coefficient (kW/m2-K)
|  | AT = | total area of the compartment enclosing surface boundaries (m2)
| Results | Time After Ignition (t) |  | hk | DTg | Tg | Tg | Tg
|  | (min) | (sec) | (kW/m2-K) | (°K) | (°K) | (°C) | (°F)
|  | 0 | 0 | - | - | 294.1111 | 21.1111 | 70
|  | 1 | 60 | 0.087939 | 23.2761 | 317.3873 | 44.3873 | 111.8971
|  | 2 | 120 | 0.062183 | 32.5618 | 326.6729 | 53.6729 | 128.6112
|  | 3 | 180 | 0.050772 | 39.552 | 333.6631 | 60.6631 | 141.1935
|  | 4 | 240 | 0.04397 | 45.3563 | 339.4674 | 66.4674 | 151.6413
|  | 5 | 300 | 0.039328 | 50.4042 | 344.5153 | 71.5153 | 160.7275
|  | 10 | 600 | 0.027809 | 69.6352 | 363.7463 | 90.7463 | 195.3433
|  | 15 | 900 | 0.022706 | 83.7996 | 377.9107 | 104.9107 | 220.8393
|  | 20 | 1200 | 0.019664 | 95.3629 | 389.474 | 116.474 | 241.6532
|  | 25 | 1500 | 0.017588 | 105.2765 | 399.3876 | 126.3876 | 259.4976
|  | 30 | 1800 | 0.016055 | 114.0266 | 408.1377 | 135.1377 | 275.2478
|  | 35 | 2100 | 0.014864 | 121.9011 | 416.0122 | 143.0122 | 289.4219
|  | 40 | 2400 | 0.013904 | 129.0869 | 423.198 | 150.198 | 302.3564
|  | 45 | 2700 | 0.013109 | 135.7134 | 429.8245 | 156.8245 | 314.2841
|  | 50 | 3000 | 0.012437 | 141.8746 | 435.9857 | 162.9857 | 325.3742
|  | 55 | 3300 | 0.011858 | 147.641 | 441.7522 | 168.7522 | 335.7539
|  | 60 | 3600 | 0.011353 | 153.0676 | 447.1787 | 174.1787 | 345.5217
Summary of Results
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation, and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov and Naeem.Iqbal@nrc.gov or MarkHenry.Salley@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [8 empty] | Date
1805.0 | Original issue with final text. | [8 empty] | December 2004
1805.1 | Deleted extraneous variable in Cell C94. Under Deal & Beyler Method, added tp calculation in Cells starting B148, added hk formula for t > tp in Cell E158 and changed equation for results table for hk in Cells starting D184. Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [8 empty] | March 2011
Note on F35: This default value (1.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Click Here to Calculate this Sheet and Return to THIEF

## Gas_Temperature-Door_Closed
CHAPTER 2. PREDICTING HOT GAS LAYER TEMPERATURE
|  | IN A ROOM FIRE WITH | [6 empty] | Version 1805.1
|  | DOOR CLOSED | [6 empty] | (English Units)
The following calculations estimate the hot gas layer temperature in enclosure fire with door closed. This method assume that compartment has sufficient leaks to prevent pressure buildup, but the leakages are ignored.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 15 | ft |  |  | 4.572 | m
| Compartment Length (lc) |  |  |  | 15 | ft |  |  | 4.572 | m
| Compartment Height (hc) |  |  |  | 10 | ft |  |  | 3.048 | m
| Interior Lining Thickness (d) |  |  |  | 12 | in |  |  | 0.3048 | m
| Ambient Air Temperature (Ta) |  |  |  | 70 | °F |  |  | 21.1111 | °C
[9 empty] | 294.1111 | °K
AMBIENT CONDITIONS
| Specific Heat of Air (cp) |  |  |  | 1 | kJ/kg-K
| Ambient Air Density (ra) |  |  |  | 1.2002 | kg/m3
| Volume of the Compartment (V) |  |  |  | 2250 | ft3 |  |  | 63.7129 | m3
| Mass of the Gas in the Compartment (m = V x ra) |  |  |  | 76.4699 | kg
Note: Ambient Air Density (ra) will automatically correct with Ambient Air Temperature (Ta) Input
THERMAL PROPERTIES OF COMPARTMENT ENCLOSING SURFACES
| Interior Lining Thermal Inertia (krc) |  |  |  | 2.9 | (kW/m2-K)2-sec
| Interior Lining Thermal Conductivity (k) |  |  |  | 0.0016 | kW/m-K
| Interior Lining Specific Heat (c) |  |  |  | 0.75 | kJ/kg-K
| Interior Lining Density (r) |  |  |  | 2400 | kg/m3
THERMAL PROPERTIES FOR COMMON INTERIOR LINING MATERIALS
|  | Material |  | krc | k | c | r | Select Material
|  |  |  | (kW/m2-K)2-sec | (kW/m-K) | (kJ/kg-K) | (kg/m3)
|  | Aluminum (pure) |  | 500 | 0.206 | 0.895 | 2710 | Scroll to desired material
|  | Steel (0.5% Carbon) |  | 197 | 0.054 | 0.465 | 7850 | Click on selection
|  | Concrete |  | 2.9 | 0.0016 | 0.75 | 2400
|  | Brick |  | 1.7 | 0.0008 | 0.8 | 2600
|  | Glass, Plate |  | 1.6 | 0.00076 | 0.8 | 2710
|  | Brick/Concrete Block |  | 1.2 | 0.00073 | 0.84 | 1900
|  | Gypsum Board |  | 0.18 | 0.00017 | 1.1 | 960
|  | Plywood |  | 0.16 | 0.00012 | 2.5 | 540
|  | Fiber Insulation Board |  | 0.16 | 0.00053 | 1.25 | 240
|  | Chipboard |  | 0.15 | 0.00015 | 1.25 | 800
|  | Aerated Concrete |  | 0.12 | 0.00026 | 0.96 | 500
|  | Plasterboard |  | 0.12 | 0.00016 | 0.84 | 950
|  | Calcium Silicate Board |  | 0.098 | 0.00013 | 1.12 | 700
|  | Alumina Silicate Block |  | 0.036 | 0.00014 | 1 | 260
|  | Glass Fiber Insulation |  | 0.0018 | 3.7e-05 | 0.8 | 60
|  | Expanded Polystyrene |  | 0.001 | 3.4e-05 | 1.5 | 20
|  | User Specified Value |  | Enter Value | Enter Value | Enter Value | Enter Value
Reference: Klote, J., J. Milke, Principles of Smoke Management, 2002, Page 270.
FIRE SPECIFICATIONS
| Fire Heat Release Rate (Q) |  |  |  | 500 | kW
| Time after Ignition |  |  |  | 120 | sec
METHOD OF BEYLER
Reference: SFPE Handbook of Fire Protection Engineering, 3nd Edition, 2002, Page 3-180.
DTg = (2 K2 / K12) (K1 √t-1+e(- K1 √t))
Where,
|  | DTg = | Tg - Ta = upper layer gas temperature rise above ambient (K)
|  | Ta = | ambient air temperature (K)
Parameter K1 = |  |  | 2 (0.4√krc) AT / mcp
Parameter K2 = |  |  | Q / m cp
|  | krc = | interior construction thermal inertia (kW/m2-K)2-sec
|  | m = | mass of gas in the compartment (kg)
|  | cp = | specific heat of air (kJ/kg-K)
|  | AT = | total area of the compartment enclosing surface boundaries (m2)
|  | Q = | heat release rate of the fire (kW)
|  | t = | exposure time (sec)
Calculation for Parameter K1
K1 = 2 (0.4√krc) AT / mcp
Where,
|  | krc = | interior construction thermal inertia (kW/m2-K)2-sec
|  | AT = | total area of the compartment enclosing surface boundaries (m2)
|  | m = | mass of gas in the compartment (kg)
Area of Compartment Enclosing Surface Boundaries
AT = [2(wc x lc) + 2(hc x wc) + 2(hc x lc)]
Where,
|  | AT = | total area of the compartment enclosing surface boundaries (m2)
|  | wc = | compartment width (m)
|  | lc = | compartment length (m)
|  | hc = | compartment height (m)
|  |  | AT = | 97.5482 |  | m2
|  |  | K1 = | 1.7379 |  | sec -1/2
Calculation for Parameter K2
K2 = Q / m cp
Where,
|  | Q = | heat release rate of the fire (kW)
|  | m = | mass of gas in the compartment (kg)
|  | cp = | specific heat of air (kJ/kg-K)
|  |  | K2 = | 6.5385 |  | K / sec
Compartment Hot Gas Layer Temperature, Compartment Door Closed
DTg = (2 K2 / K12) (K1 √t-1+e(- K1 √t))
|  | DTg = Tg - Ta = |  | 78.0996 |  | °K
|  |  | Tg = | 372.2107 |  | °K
Answer | Tg = |  | 99.2107 |  | °C |  | 210.5793 |  | °F
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov and Naeem.Iqbal@nrc.gov or MarkHenry.Salley@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Corrected calculation for Parameter K1. Added area of compartment enclosing surface boundaries (AT) in Parameter K1. Corrected subscripts, revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011
Note on F34: This default value (1.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F36: Compartment Volume automatically calculated from the Compartment Information entered (i.e., V = wc x lc x hc).
Note on F37: Mass of Gas automatically calculated from Input Parameters previously entered (i.e., m = V x ra).
Click Here to Calculate this Sheet and Return to THIEF

## Plume-Calculations
CHAPTER 9. ESTIMATING CENTERLINE TEMPERATURE
|  | OF A | [5 empty] | Version 1805.1
|  | BUOYANT FIRE PLUME | [5 empty] | (English Units)
The following calculations estimate the centerline plume temperature in a compartment fire.
Parameters should be specified ONLY IN THE YELLOW INPUT PARAMETER BOXES.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Heat Release Rate of the Fire (Q) |  |  |  | 5000 | kW
| Elevation Above the Fire Source (z) |  |  |  | 25 | ft |  | 7.62 | m
| Area of Combustible Fuel (Ac) |  |  |  | 34.5 | ft2 |  | 3.2052 | m2
| Ambient Air Temperature (Ta) |  |  |  | 70 | °F |  | 21.1111 | °C
[8 empty] | 294.1111 | °K
AMBIENT CONDITIONS
| Specific Heat of Air (cp) |  |  |  | 1 | kJ/kg-K
| Ambient Air Density (ra) |  |  |  | 1.2002 | kg/m3
| Acceleration of Gravity (g) |  |  |  | 9.81 | m/sec2
| Convective Heat Release Fraction (cc) |  |  |  | 0.7
NOTE: Ambient Air Density (ra) will automatically correct with Ambient Air Temperature (Ta) Input
ESTIMATING PLUME CENTERLINE TEMPERATURE
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 2-6.
Tp(centerline) - Ta = 9.1 (Ta/g cp2 ra2)1/3 Qc2/3 (z - z0)-5/3
Where,
|  |  | Tp(centerline) = | plume centerline temperature (°C)
|  |  | Qc = | convective portion of the heat release rate (kW)
|  |  | Ta = | ambient air temperature (K)
|  |  | g = | acceleration of gravity (m/sec2)
|  |  | cp = | specific heat of air (kJ/kg-K)
|  |  | ra = | ambient air density (kg/m3)
|  |  | z = | distance from the top of the fuel package to the ceiling (m)
|  |  | z0 = | hypothetical virtual origin of the fire (m)
Convective Heat Release Rate Calculation
Qc = cc Q
Where,
|  |  | Qc = | convective portion of the heat release rate (kW)
|  |  | Q = | heat release rate of the fire (kW)
|  |  | cc = | convective heat release fraction
|  |  | Qc = | 3500 |  | kW
Fire Diameter Calculation
Ac = pD2/4
D = √(4 Ac/p)
Where,
|  |  | Ac = | area of combustible fuel (m2)
|  |  | D = | fire diameter (m)
|  |  | D = | 2.0201 |  | m
Hypothetical Virtual Origin Calculation
z0/D = -1.02 + 0.083 (Q2/5)/D
Where,
|  |  | z0 = | virtual origin of the fire (m)
|  |  | Q = | heat release rate of fire (kW)
|  |  | D = | fire diameter (m)
|  |  | z0/D = | 0.21961
|  |  | z0 = | 0.44365 |  | m
Mean Flame Height Calculation
|  |  | L = | -1.02D + 0.235 (Q2/5)
Where,
|  |  | L = | mean flame height (m)
|  |  | Q = | heat release rate of fire (kW)
|  |  | D = | fire diameter (m)
|  |  | L = | 5.03 |  | m
Centerline Plume Temperature Calculation
|  | Tp(centerline) - Ta = |  | 9.1 (Ta/g cp2 ra2)1/3 Qc2/3 (z - z0)-5/3
|  | Tp(centerline) - Ta = |  | 216.1155 |  | °K
|  | Tp(centerline) = |  | 510.2266 |  | °K
Answer | Tp(centerline) = |  | 237.2266 |  | °C |  | 459.0079 | °F
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation, and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns, and suggestions, or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov and Naeem.Iqbal@nrc.gov or MarkHenry.Salley@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Corrected subscripts, revised e-mail addresses, corrected editorial errors, added flame height calculation, revised print pagination and print layout. | [7 empty] | March 2011
Note on F35: This default value (1.00) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F37: This default value (9.81) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Note on F38: This default value (0.70) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.
Click Here to Calculate this Sheet and Return to THIEF

## Control (hidden)
Manufacturer | Cable Model | insul | jacket | AWG | #/C | Insulation Type | Jacket Type | OD mm | kg/m | Jkt (mm) | Grade | Comments | Part # | Item #
GENERIC | GENERIC | TP | TP | 2 | 7 | TP | TP | 25.527 | 1.4614 | 2.032 | Industrial Grade | 8 Pwr & 4 or 6 Control (14 AWG), 600V, 90°C dry 75°C wet | 22136 | 1433 | AWG | #/C | AWG | 2 | 4 | 6 | 8 | 9 | 10 | 12 | 14 | 16
GENERIC | GENERIC | TP | TP | 4 | 7 | TP | TP | 22.352 | 1.0447 | 2.032 | Industrial Grade | 7 Pwr & 4 or 6 Control (14 AWG), 600V, 90°C dry 75°C wet | 22135 | 1432 | 2 | 1 |  | 7 | 7 | 7 | 7 | 2 | 1 | 1 | 1 | 2
GENERIC | GENERIC | TP | TP | 6 | 7 | TP | TP | 18.161 | 0.68158 | 1.524 | Industrial Grade | 6 Pwr & 4 or 6 Control (14 AWG), 600V, 90°C dry 75°C wet | 22134 | 1101 | 4 | 2 | [5 empty] | 3 | 2 | 2 | 2 | 3
GENERIC | GENERIC | TP | TP | 8 | 7 | TP | TP | 16.51 | 0.52979 | 1.524 | Industrial Grade | 5 Pwr & 4 or 6 Control (14 AWG), 600V, 90°C dry 75°C wet | 22133 | 1100 | 6 | 3 | [5 empty] | 4 | 3 | 3 | 3 | 4
GENERIC | GENERIC | TP | TP | 9 | 2 | TP | TP | 10.16 | 0.21727 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3652 | 21 | 8 | 4 | [5 empty] | 5 | 4 | 4 | 4 | 5
GENERIC | GENERIC | TS | TS | 9 | 2 | TS | TS | 14.986 | 0.3899 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2652 | 852 | 9 | 5 | [5 empty] | 7 | 5 | 5 | 5 | 6
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 2 | TS | TS | 12.446 | 0.28573 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2652 | 318 | 10 | 6 | [5 empty] | 9 | 6 | 6 | 6 | 7
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 9 | 2 | TS | TS | 18.288 | 0.4524 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6652 | 827 | 12 | 7 | [5 empty] | 12 | 7 | 7 | 7 | 8
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 2 | TS | TS | 14.986 | 0.3899 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2652 | 852 | 14 | 8 | [5 empty] | 15 | 8 | 8 | 8 | 9
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 9 | 2 | TS | TS | 17.018 | 0.42978 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6652 | 879 | 16 | 9 | [5 empty] | 25 | 9 | 9 | 9 | 10
Okonite | FRM-N® Okolon® | EPR | CSPE | 9 | 2 | TS | TS | 14.732 | 0.32144 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2652 | 915 |  | 10 | [5 empty] | 30 | 10 | 10 | 10 | 11
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 9 | 2 | TS | TS | 16.256 | 0.37502 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2652 | 933 |  | 11 | [5 empty] | 37 | 11 | 11 | 11 | 12
GENERIC | GENERIC | TP | TP | 9 | 3 | TP | TP | 13.462 | 0.29019 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2653 | 406 |  | 12 | [6 empty] | 12 | 12 | 12 | 13
GENERIC | GENERIC | TS | TS | 9 | 3 | TS | TS | 15.748 | 0.44347 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2653 | 853 |  | 13 | [6 empty] | 13 | 13 | 13 | 14
Draka | 20-10 Control Cable | PE | PVC | 9 | 3 | TP | TP | 13.208 | 0.27977 | 1.143 | Industrial Grade | Unshielded, 1000V, 75°C | 75030 | 170 |  | 14 | [6 empty] | 14 | 14 | 14 | 15
Draka | 20-10 Control Cable Shielded | PE | PVC | 9 | 3 | TP | TP | 15.748 | 0.38395 | 1.524 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 75031 | 700 |  | 15 | [6 empty] | 15 | 15 | 15 | 16
Okonite | Okozel® | ETFE | ETFE | 9 | 3 | TP | TP | 10.922 | 0.29019 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3653 | 22 |  | 16 | [6 empty] | 16 | 16 | 16 | 17
Okonite | P-30 | PE | PVC | 9 | 3 | TP | TP | 13.462 | 0.29019 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2653 | 406 |  | 17 | [6 empty] | 17 | 17 | 17 | 18
Okonite | P-45 | PE | PVC | 9 | 3 | TP | TP | 16.002 | 0.35121 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3653 | 1010 |  | 18 | [6 empty] | 18 | 18 | 18 | 19
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 3 | TS | TS | 13.462 | 0.35567 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2653 | 319 |  | 19 | [6 empty] | 19 | 19 | 19 | 20
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 9 | 3 | TS | TS | 19.05 | 0.55509 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6653 | 828 |  | 20 | [6 empty] | 20 | 20 | 20 | 21
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 3 | TS | TS | 15.748 | 0.44347 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2653 | 853 |  | 21 | [6 empty] | 23 | 21 | 21 | 22
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 9 | 3 | TS | TS | 17.526 | 0.49556 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6653 | 880 |  | 22 | [6 empty] | 24 | 22 | 22 | 23
Okonite | FRM-N® Okolon® | EPR | CSPE | 9 | 3 | TS | TS | 15.494 | 0.40925 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2653 | 916 |  | 23 | [6 empty] | 25 | 23 | 23 | 24
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 9 | 3 | TS | TS | 17.272 | 0.45687 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2653 | 934 |  | 24 | [6 empty] | 30 | 24 | 24 | 25
GENERIC | GENERIC | TP | TP | 9 | 4 | TP | TP | 15.494 | 0.40478 | 1.524 | [5 empty] | 25 | [6 empty] | 37 | 25 | 25 | 26
GENERIC | GENERIC | TS | TS | 9 | 4 | TS | TS | 17.272 | 0.54913 | 1.524 | [5 empty] | 26 | [6 empty] | 3+G | 26 | 26 | 27
Draka | 20-10 Control Cable | PE | PVC | 9 | 4 | TP | TP | 15.24 | 0.38395 | 1.524 | Industrial Grade | Unshielded, 1000V, 75°C | 75040 | 693 |  | 27 | [7 empty] | 27 | 27 | 28
Draka | 20-10 Control Cable Shielded | PE | PVC | 9 | 4 | TP | TP | 17.018 | 0.47324 | 1.524 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 75041 | 701 |  | 28 | [7 empty] | 28 | 28 | 29
Okonite | Okozel® | ETFE | ETFE | 9 | 4 | TP | TP | 12.446 | 0.38692 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3654 | 32 |  | 29 | [7 empty] | 29 | 29 | 30
Okonite | P-30 | PE | PVC | 9 | 4 | TP | TP | 15.494 | 0.40478 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2654 | 1002 |  | 30 | [7 empty] | 30 | 30 | 31
Okonite | P-45 | PE | PVC | 9 | 4 | TP | TP | 17.526 | 0.4524 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3654 | 1011 |  | 31 | [7 empty] | 31 | 31 | 32
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 9 | 4 | TS | TS | 20.574 | 0.67265 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6654 | 829 |  | 32 | [7 empty] | 32 | 32 | 33
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 4 | TS | TS | 17.272 | 0.54913 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2654 | 854 |  | 33 | [7 empty] | 33 | 33 | 34
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 4 | TS | TS | 15.494 | 0.4777 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2654 | 855 |  | 34 | [7 empty] | 34 | 34 | 35
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 9 | 4 | TS | TS | 18.796 | 0.60122 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6654 | 881 |  | 35 | [7 empty] | 35 | 35 | 36
Okonite | FRM-N® Okolon® | EPR | CSPE | 9 | 4 | TS | TS | 16.764 | 0.49556 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2654 | 917 |  | 36 | [7 empty] | 36 | 36 | 37
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 9 | 4 | TS | TS | 18.796 | 0.5789 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2654 | 935 |  | 37 | [7 empty] | 37 | 37 | 41
GENERIC | GENERIC | TP | TP | 9 | 5 | TP | TP | 16.764 | 0.49258 | 1.524 | [5 empty] | 41 | [7 empty] | 3+G |  | 60
GENERIC | GENERIC | TS | TS | 9 | 5 | TS | TS | 18.796 | 0.67265 | [6 empty] | 60
Draka | 20-10 Control Cable | PE | PVC | 9 | 5 | TP | TP | 16.764 | 0.4658 | 1.524 | Industrial Grade | Unshielded, 1000V, 75°C | 75050 | 694 |  | 3+G
Draka | 20-10 Control Cable Shielded | PE | PVC | 9 | 5 | TP | TP | 18.415 | 0.56104 | 1.524 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 75051 | 702
Okonite | Okozel® | ETFE | ETFE | 9 | 5 | TP | TP | 13.716 | 0.47621 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3655 | 33
Okonite | P-30 | PE | PVC | 9 | 5 | TP | TP | 16.764 | 0.49258 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2655 | 1003
Okonite | P-45 | PE | PVC | 9 | 5 | TP | TP | 19.05 | 0.55211 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3655 | 1012
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 9 | 5 | TS | TS | 23.114 | 0.85123 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6655 | 830
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 5 | TS | TS | 18.796 | 0.67265 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2655 | 856
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 5 | TS | TS | 16.764 | 0.55657 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2655 | 857
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 9 | 5 | TS | TS | 20.066 | 0.7039 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6655 | 882
Okonite | FRM-N® Okolon® | EPR | CSPE | 9 | 5 | TS | TS | 18.034 | 0.61164 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2655 | 918
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 9 | 5 | TS | TS | 20.32 | 0.69051 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2655 | 936
GENERIC | GENERIC | TP | TP | 9 | 7 | TP | TP | 18.288 | 0.64586 | 1.524
GENERIC | GENERIC | TS | TS | 9 | 7 | TS | TS | 20.574 | 0.82891 | 1.524
Draka | 20-10 Control Cable | PE | PVC | 9 | 7 | TP | TP | 18.288 | 0.62205 | 1.524 | Industrial Grade | Unshielded, 1000V, 75°C | 75070 | 695
Okonite | Okozel® | ETFE | ETFE | 9 | 7 | TP | TP | 14.986 | 0.62949 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3657 | 34
Okonite | P-30 | PE | PVC | 9 | 7 | TP | TP | 18.288 | 0.64586 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2657 | 1004
Okonite | P-45 | PE | PVC | 9 | 7 | TP | TP | 20.828 | 0.72027 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3657 | 1013
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 7 | TS | TS | 20.574 | 0.82891 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2657 | 858
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 7 | TS | TS | 18.288 | 0.7292 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2657 | 859
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 9 | 7 | TS | TS | 22.606 | 0.94201 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6657 | 883
Okonite | FRM-N® Okolon® | EPR | CSPE | 9 | 7 | TS | TS | 19.558 | 0.77087 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2657 | 919
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 9 | 7 | TS | TS | 24.892 | 1.0521 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6657 | 1283
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 9 | 7 | TS | TS | 23.114 | 0.92415 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2657 | 1342
GENERIC | GENERIC | TP | TP | 9 | 9 | TP | TP | 21.336 | 0.83188 | 1.524
GENERIC | GENERIC | TS | TS | 9 | 9 | TS | TS | 25.146 | 1.1861 | 2.032
Draka | 20-10 Control Cable | PE | PVC | 9 | 9 | TP | TP | 21.463 | 0.78873 | 1.524 | Industrial Grade | Unshielded, 1000V, 75°C | 75090 | 696
Okonite | Okozel® | ETFE | ETFE | 9 | 9 | TP | TP | 18.034 | 0.76492 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3659 | 35
Okonite | P-30 | PE | PVC | 9 | 9 | TP | TP | 21.336 | 0.83188 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2659 | 1005
Okonite | P-45 | PE | PVC | 9 | 9 | TP | TP | 25.4 | 0.98814 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3659 | 1378
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 9 | TS | TS | 21.336 | 1.0015 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2659 | 860
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 9 | 9 | TS | TS | 28.448 | 1.3155 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6659 | 1284
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 9 | TS | TS | 25.146 | 1.1861 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2659 | 1298
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 9 | 9 | TS | TS | 25.654 | 1.1712 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6659 | 1308
Okonite | FRM-N® Okolon® | EPR | CSPE | 9 | 9 | TS | TS | 23.622 | 1.0864 | 2.032 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2659 | 1331
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 9 | 9 | TS | TS | 26.67 | 1.2307 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2659 | 1343
GENERIC | GENERIC | TP | TP | 9 | 12 | TP | TP | 25.146 | 1.1251 | 2.032
GENERIC | GENERIC | TS | TS | 9 | 12 | TS | TS | 28.194 | 1.4599 | 2.032
Draka | 20-10 Control Cable | PE | PVC | 9 | 12 | TP | TP | 25.019 | 1.0878 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 75120 | 1219
Okonite | Okozel® | ETFE | ETFE | 9 | 12 | TP | TP | 20.828 | 1.0566 | 0.635 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3662 | 38
Okonite | P-30 | PE | PVC | 9 | 12 | TP | TP | 25.146 | 1.1251 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2662 | 1376
Okonite | P-45 | PE | PVC | 9 | 12 | TP | TP | 28.702 | 1.253 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3662 | 1379
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 9 | 12 | TS | TS | 31.496 | 1.6385 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6662 | 1285
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 12 | TS | TS | 28.194 | 1.3989 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2662 | 1299
Okonite | FMR® Okolon® | EPR | CSPE | 9 | 12 | TS | TS | 25.146 | 1.2917 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2662 | 1300
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 9 | 12 | TS | TS | 28.194 | 1.4599 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6662 | 1309
Okonite | FRM-N® Okolon® | EPR | CSPE | 9 | 12 | TS | TS | 26.162 | 1.3111 | 2.032 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2662 | 1332
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 9 | 12 | TS | TS | 29.718 | 1.4673 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2662 | 1344
GENERIC | GENERIC | TP | TP | 9 | 15 | TP | TP | 27.813 | 1.3334 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 75150 | 1220
GENERIC | GENERIC | TP | TP | 9 | 19 | TP | TP | 29.21 | 1.637 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 75190 | 1221
GENERIC | GENERIC | TP | TP | 9 | 25 | TP | TP | 35.052 | 2.1325 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 75250 | 1222
GENERIC | GENERIC | TP | TP | 9 | 30 | TP | TP | 36.322 | 2.512 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 75300 | 1223
GENERIC | GENERIC | TP | TP | 9 | 37 | TP | TP | 39.243 | 3.0507 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 75370 | 1224
GENERIC | GENERIC | TS |  | 10 | 1 | TS | None | 4.6482 | 0.061015 | 0.762 | Industrial Grade | Single Conductor, 600V, 90°C |  | 62
Continental | SIS Switchboard Wire | XLPE |  | 10 | 1 | TS | None | 4.6482 | 0.061015 | 0.762 | Industrial Grade | Single Conductor, 600V, 90°C |  | 62
Continental | XHHW CONTROL WIRE | XLPO |  | 10 | 1 | TS | None | 4.6482 | 0.061015 | 0.762 | Industrial Grade | Single Conductor, 600V, 90°C |  | 65
GENERIC | GENERIC | TP | TP | 10 | 2 | TP | TP | 9.9568 | 0.18007 | 1.143
GENERIC | GENERIC | TS | TS | 10 | 2 | TS | TP | 13.589 | 0.26638 | 1.143
Cable USA | ETFE TYPE TC | ETFE | ETFE | 10 | 2 | TP | TP | 9.2456 | 0.15179 | 0.762 | Industrial Grade | Unshielded, 600V | 181002C6 | 45
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 10 | 2 | TP | TP | 7.9756 | 0.1384 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 262
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 10 | 2 | TP | TP | 9.9568 | 0.18007 | 1.143 | Industrial Grade | Unshielded, 600V | 181002C6 | 277
Dekoron | 1C99 | PVC | PVC | 10 | 2 | TP | TP | 11.2522 | 0.19197 | 1.143 | Industrial Grade | 600V |  | 144
General Cable | 20/10 | PE | PVC | 10 | 2 | TP | TP | 11.43 | 0.19346 | 1.143 | Industrial Grade | Unshielded, 600V | 257780 | 159
General Cable | VNTC® | PVC | PVC | 10 | 2 | TP | TP | 10.668 | 0.17114 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 243630 | 541
General Cable | VNTC® | PVC | PVC | 10 | 2 | TP | TP | 10.922 | 0.17709 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243770 | 542
Okonite | Okozel® | ETFE | ETFE | 10 | 2 | TP | TP | 9.144 | 0.17114 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3552 | 17
Okonite | P-30 | PE | PVC | 10 | 2 | TP | TP | 11.684 | 0.19346 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2452 | 404
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 2 | TS | TS | 11.684 | 0.22322 | 1.143 | Industrial Grade | Unshielded, 600V | 29515 | 562
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 10 | 2 | TS | TS | 11.938 | 0.19644 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 810-02 | 213
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 2 | TS | TP | 13.589 | 0.26638 | 1.143 | Industrial Grade | Shielded, 600V, 90°C | 258020 | 394
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 2 | TS | TP | 13.589 | 0.26638 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 158023 | 469
General Cable | CHTC® | XLPE | CSPE | 10 | 2 | TS | TS | 11.557 | 0.18751 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 355210 | 198
General Cable | CVTC® | XLPE | PVC | 10 | 2 | TS | TP | 11.557 | 0.19346 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 346930 | 226
General Cable | EHTC® | EPR | CSPE | 10 | 2 | TS | TS | 11.557 | 0.19941 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 343800 | 242
General Cable | FREP® | EPR | CPE | 10 | 2 | TS | TP | 11.684 | 0.19495 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 311900 | 341
General Cable | FREP® | EPR | CPE | 10 | 2 | TS | TP | 11.557 | 0.19048 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 305340 | 342
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 2 | TS | TS | 11.2522 | 0.20834 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378650 | 508
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 2 | TS | TS | 13.462 | 0.30954 | 1.143 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2452 | 315
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 2 | TS | TS | 11.938 | 0.24704 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2452 | 316
Okonite | FRM-N® Okolon® | EPR | CSPE | 10 | 2 | TS | TS | 12.192 | 0.24257 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2452 | 354
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 10 | 2 | TS | TP | 17.526 | 0.30061 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3162 | 607
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 10 | 2 | TS | TP | 17.526 | 0.37651 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3502 | 625
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 10 | 2 | Sil | TP | 19.812 | 0.4152 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3652 | 644
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 10 | 2 | TS | TS | 17.526 | 0.41371 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6452 | 823
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 10 | 2 | TS | TS | 17.018 | 0.41669 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6452 | 874
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 10 | 2 | TS | TS | 15.748 | 0.3393 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2452 | 928
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 2 | TS | TS | 10.668 | 0.18602 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C17-0020 | 76
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 2 | TS | TS | 9.906 | 0.15626 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0020 | 90
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 2 | Sil | Fiber | 13.716 | 0.20834 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2020 | 115
GENERIC | GENERIC | TP | TP | 10 | 3 | TP | TP | 11.938 | 0.24406 | 1.143
GENERIC | GENERIC | TS | TS | 10 | 3 | TS | TS | 14.351 | 0.35269 | 1.524
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 10 | 3 | TP | TP | 11.3284 | 0.24852 | 1.143 | Industrial Grade | Unshielded, 600V | 68142 | 497
Cable USA | ETFE TYPE TC | ETFE | ETFE | 10 | 3 | TP | TP | 9.8552 | 0.21281 | 0.762 | Industrial Grade | Unshielded, 600V | 181003C6 | 46
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 10 | 3 | TP | TP | 8.509 | 0.19793 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 263
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 10 | 3 | TP | TP | 10.5664 | 0.24108 | 1.143 | Industrial Grade | Unshielded, 600V | 181003C6 | 278
Dekoron | 1735 | PE | PVC | 10 | 3 | TP | TP | 11.8364 | 0.1756 | 1.143 | Industrial Grade | 600V |  | 129
Dekoron | 1C99 | PVC | PVC | 10 | 3 | TP | TP | 12.1412 | 0.25596 | 1.143 | Industrial Grade | 600V |  | 145
Draka | 20-10 Control Cable | PE | PVC | 10 | 3 | TP | TP | 12.573 | 0.25299 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 74030 | 169
Draka | Power & Control 3 THHN/THWN | PVC | PVC | 10 | 3 | TP | TP | 12.7 | 0.31103 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 8047 | 410
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 3 | TP | TP | 11.938 | 0.24406 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8033 | 438
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 10 | 3 | TP | TP | 13.716 | 0.31549 | 1.143 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 9603 | 455
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 10 | 3 | TP | TP | 13.716 | 0.28573 | 1.143 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 9803 | 456
Draka | 20-10 Control Cable Shielded | PE | PVC | 10 | 3 | TP | TP | 15.24 | 0.34674 | 1.524 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 74031 | 697
General Cable | 20/10 | PE | PVC | 10 | 3 | TP | TP | 12.192 | 0.25299 | 1.143 | Industrial Grade | Unshielded, 600V | 267840 | 160
General Cable | VNTC® | PVC | PVC | 10 | 3 | TP | TP | 11.43 | 0.23364 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236310 | 543
General Cable | VNTC® | PVC | PVC | 10 | 3 | TP | TP | 11.684 | 0.24108 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243820 | 544
General Cable | VNTC® | PVC | PVC | 10 | 3 | TP | TP | 12.827 | 0.2009 | 1.143 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 234260 | 545
Okonite | Okozel® | ETFE | ETFE | 10 | 3 | TP | TP | 9.652 | 0.22918 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3553 | 18
Okonite | P-30 | PE | PVC | 10 | 3 | TP | TP | 12.446 | 0.24406 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2453 | 405
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 10 | 3 | TS | TP | 11.938 | 0.22918 | 1.143 | Industrial Grade | Unshielded, 600V | 40939 | 485
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 3 | TS | TS | 12.7 | 0.27531 | 1.143 | Industrial Grade | Unshielded, 600V | 19895 | 563
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 10 | 3 | TS | TP | 12.065 | 0.22471 | 1.143 | Industrial Grade | Unshielded, 600V | 40821 | 586
Dekoron | 2X35 | XLPE | PVC | 10 | 3 | TS | TP | 12.8016 | 0.26936 | 1.143 | Industrial Grade | 600V | 2X35-B1260 | 176
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 10 | 3 | TS | TS | 12.7 | 0.26638 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 810-03 | 214
Draka | General Purpose Control XLPE | XLPE | CPE | 10 | 3 | TS | TP | 12.7 | 0.27531 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 228030 | 393
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 3 | TS | TP | 12.7 | 0.27531 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 208030 | 395
Draka | Power & Control Type TC 3 XHHW-2 1 bare | XLPE | PVC | 10 | 3 | TS | TP | 12.7 | 0.31103 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 8047 | 423
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 3 | TS | TP | 12.7 | 0.27531 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 108033 | 470
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 3 | TS | TP | 15.113 | 0.34823 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 258030 | 981
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 10 | 3 | TS | TP | 15.621 | 0.41669 | 1.524 | Industrial Grade | Shielded (Copper), 600V, 90°C | 158047 | 1035
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 3 | TS | TP | 15.113 | 0.34823 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 158033 | 1092
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 10 | 3 | TS | TS | 17.653 | 0.42264 | 2.413 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13385 | 1504
General Cable | CHTC® | XLPE | CSPE | 10 | 3 | TS | TS | 12.319 | 0.26192 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 224100 | 199
General Cable | CVTC® | XLPE | PVC | 10 | 3 | TS | TP | 12.319 | 0.25745 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770600 | 227
General Cable | CVTC® | XLPE | PVC | 10 | 3 | TS | TP | 13.081 | 0.35121 | 1.143 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 383880 | 228
General Cable | EHTC® | EPR | CSPE | 10 | 3 | TS | TS | 12.319 | 0.26489 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 343810 | 243
General Cable | FREP® | EPR | CPE | 10 | 3 | TS | TP | 12.446 | 0.26043 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367230 | 344
General Cable | FREP® | EPR | CPE | 10 | 3 | TS | TP | 12.319 | 0.25596 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280410 | 345
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 3 | TS | TS | 11.938 | 0.25299 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378660 | 509
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 10 | 3 | TS | TS | 13.3604 | 0.19941 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282570 | 753
General Cable | EHTC® | EPR | CSPE | 10 | 3 | TS | TS | 14.351 | 0.35269 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 383850 | 779
General Cable | EHTC® | EPR | CSPE | 10 | 3 | TS | TS | 13.3604 | 0.19941 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 383820 | 780
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 3 | TS | TS | 12.7 | 0.30507 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2453 | 317
Okonite | FRM-N® Okolon® | EPR | CSPE | 10 | 3 | TS | TS | 12.7 | 0.30507 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2453 | 355
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 10 | 3 | TS | TP | 17.526 | 0.35418 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3163 | 608
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 10 | 3 | Sil | TP | 20.828 | 0.49556 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3653 | 645
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 10 | 3 | TS | TS | 18.288 | 0.49853 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6453 | 824
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 3 | TS | TS | 15.24 | 0.38692 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2453 | 844
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 10 | 3 | TS | TS | 17.018 | 0.46133 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6453 | 875
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 10 | 3 | TS | TS | 16.51 | 0.40776 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2453 | 929
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 3 | TS | TS | 11.176 | 0.23811 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C17-0030 | 77
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 3 | TS | TS | 10.668 | 0.21578 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0030 | 91
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 3 | Sil | Fiber | 14.732 | 0.29763 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2030 | 116
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 3 | TS | TS | 12.192 | 0.29019 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-0030 | 291
GENERIC | GENERIC | TP | TP | 10 | 4 | TP | TP | 13.081 | 0.31251 | 1.143
GENERIC | GENERIC | TS | TS | 10 | 4 | TS | TS | 14.732 | 0.41073 | 1.524
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 10 | 4 | TP | TP | 12.446 | 0.31549 | 1.143 | Industrial Grade | Unshielded, 600V | 68143 | 498
Cable USA | ETFE TYPE TC | ETFE | ETFE | 10 | 4 | TP | TP | 10.8204 | 0.27531 | 0.762 | Industrial Grade | Unshielded, 600V | 181004C6 | 47
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 10 | 4 | TP | TP | 9.3726 | 0.25448 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 264
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 10 | 4 | TP | TP | 11.5062 | 0.3021 | 1.143 | Industrial Grade | Unshielded, 600V | 181004C6 | 279
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 4 | TP | TP | 13.081 | 0.31251 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8043 | 439
Draka | 20-10 Control Cable | PE | PVC | 10 | 4 | TP | TP | 14.732 | 0.34972 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 74040 | 689
Draka | 20-10 Control Cable Shielded | PE | PVC | 10 | 4 | TP | TP | 16.256 | 0.42413 | 1.524 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 74041 | 698
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 10 | 4 | TP | TP | 15.621 | 0.41073 | 1.524 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 9604 | 1074
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 10 | 4 | TP | TP | 15.621 | 0.38246 | 1.524 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 9804 | 1075
General Cable | VNTC® | PVC | PVC | 10 | 4 | TP | TP | 12.7 | 0.30507 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243690 | 546
General Cable | VNTC® | PVC | PVC | 10 | 4 | TP | TP | 12.827 | 0.31103 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236320 | 547
General Cable | 20/10 | PE | PVC | 10 | 4 | TP | TP | 13.208 | 0.34972 | 1.524 | Industrial Grade | Unshielded, 600V | 257740 | 676
Okonite | Okozel® | ETFE | ETFE | 10 | 4 | TP | TP | 10.668 | 0.29763 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3554 | 19
Okonite | P-30 | PE | PVC | 10 | 4 | TP | TP | 14.478 | 0.34079 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2454 | 997
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 10 | 4 | TS | TP | 13.208 | 0.31549 | 1.143 | Industrial Grade | Unshielded, 600V | 40940 | 486
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 4 | TS | TS | 14.732 | 0.36609 | 1.524 | Industrial Grade | Unshielded, 600V | 19896 | 1169
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 10 | 4 | TS | TP | 13.97 | 0.30954 | 1.524 | Industrial Grade | Unshielded, 600V | 40822 | 1182
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 4 | TS | TP | 14.605 | 0.38246 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 208040 | 396
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 10 | 4 | TS | TS | 14.732 | 0.36758 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 810-04 | 761
Draka | General Purpose Control XLPE | XLPE | CPE | 10 | 4 | TS | TP | 14.605 | 0.38246 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 228040 | 977
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 4 | TS | TP | 16.256 | 0.43008 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 258040 | 982
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 4 | TS | TP | 14.605 | 0.38246 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 108043 | 1093
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 4 | TS | TP | 16.256 | 0.43008 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 158043 | 1094
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 10 | 4 | TS | TS | 19.05 | 0.51788 | 2.413 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13386 | 1505
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 4 | TS | TS | 13.081 | 0.37353 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378670 | 510
General Cable | CHTC® | XLPE | CSPE | 10 | 4 | TS | TS | 14.224 | 0.35716 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 224110 | 749
General Cable | CVTC® | XLPE | PVC | 10 | 4 | TS | TP | 13.081 | 0.35121 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770370 | 768
General Cable | EHTC® | EPR | CSPE | 10 | 4 | TS | TS | 14.224 | 0.36162 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 264990 | 781
General Cable | FREP® | EPR | CPE | 10 | 4 | TS | TP | 14.351 | 0.35269 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 311910 | 896
General Cable | FREP® | EPR | CPE | 10 | 4 | TS | TP | 14.224 | 0.34823 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279900 | 897
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 10 | 4 | TS | TP | 19.812 | 0.44198 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3164 | 609
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 10 | 4 | Sil | TP | 23.114 | 0.60866 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3654 | 646
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 10 | 4 | TS | TS | 19.812 | 0.59824 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6454 | 825
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 4 | TS | TS | 16.51 | 0.47919 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2454 | 845
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 4 | TS | TS | 14.732 | 0.41073 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2454 | 846
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 10 | 4 | TS | TS | 17.78 | 0.52979 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6454 | 876
Okonite | FRM-N® Okolon® | EPR | CSPE | 10 | 4 | TS | TS | 14.732 | 0.41669 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2454 | 911
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 10 | 4 | TS | TS | 18.034 | 0.49407 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2454 | 930
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 4 | TS | TS | 12.192 | 0.31251 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C17-0040 | 78
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 4 | TS | TS | 11.684 | 0.28275 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0040 | 92
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 4 | Sil | Fiber | 16.51 | 0.38692 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2040 | 117
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 4 | TS | TS | 14.224 | 0.38692 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-0040 | 292
GENERIC | GENERIC | TP | TP | 10 | 5 | TP | TP | 14.478 | 0.39883 | 1.524
GENERIC | GENERIC | TS | TS | 10 | 5 | TS | TS | 17.272 | 0.5283 | 1.524
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 10 | 5 | TP | TP | 14.3764 | 0.40032 | 1.524 | Industrial Grade | Unshielded, 600V | 68144 | 1119
Cable USA | ETFE TYPE TC | ETFE | ETFE | 10 | 5 | TP | TP | 11.938 | 0.33781 | 0.762 | Industrial Grade | Unshielded, 600V | 181005C6 | 48
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 10 | 5 | TP | TP | 10.3632 | 0.31251 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 265
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 10 | 5 | TP | TP | 12.5984 | 0.3646 | 1.143 | Industrial Grade | Unshielded, 600V | 181005C6 | 280
Dekoron | 1735 | PE | PVC | 10 | 5 | TP | TP | 16.3068 | 0.024257 | 1.524 | Industrial Grade | 600V |  | 657
Dekoron | 1C99 | PVC | PVC | 10 | 5 | TP | TP | 15.4686 | 0.42115 | 1.524 | Industrial Grade | 600V |  | 668
Draka | 20-10 Control Cable | PE | PVC | 10 | 5 | TP | TP | 15.875 | 0.40776 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 74050 | 690
Draka | 20-10 Control Cable Shielded | PE | PVC | 10 | 5 | TP | TP | 17.653 | 0.49556 | 1.524 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 74051 | 699
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 5 | TP | TP | 15.113 | 0.40627 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8053 | 1066
General Cable | 20/10 | PE | PVC | 10 | 5 | TP | TP | 15.24 | 0.42561 | 1.524 | Industrial Grade | Unshielded, 600V | 257790 | 677
General Cable | VNTC® | PVC | PVC | 10 | 5 | TP | TP | 14.478 | 0.39883 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236330 | 1148
Okonite | Okozel® | ETFE | ETFE | 10 | 5 | TP | TP | 11.938 | 0.3646 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3555 | 20
Okonite | P-30 | PE | PVC | 10 | 5 | TP | TP | 15.748 | 0.4152 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2455 | 998
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 5 | TS | TS | 15.621 | 0.45984 | 1.524 | Industrial Grade | Unshielded, 600V | 19897 | 1170
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 10 | 5 | TS | TP | 15.367 | 0.37799 | 1.524 | Industrial Grade | Unshielded, 600V | 40967 | 1183
Dekoron | 2X35 | XLPE | PVC | 10 | 5 | TS | TP | 16.3068 | 0.44347 | 1.524 | Industrial Grade | 600V | 2X35-B1260 | 708
Draka | General Purpose Control XLPE | XLPE | CPE | 10 | 5 | TS | TP | 16.002 | 0.45835 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 228050 | 978
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 5 | TS | TP | 16.002 | 0.45835 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 208050 | 983
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 5 | TS | TP | 17.653 | 0.50598 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 258050 | 984
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 5 | TS | TP | 16.002 | 0.45835 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 108053 | 1095
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 5 | TS | TP | 17.653 | 0.50598 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 158053 | 1096
General Cable | CHTC® | XLPE | CSPE | 10 | 5 | TS | TS | 15.621 | 0.43306 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 224120 | 750
General Cable | CVTC® | XLPE | PVC | 10 | 5 | TS | TP | 15.621 | 0.4271 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770380 | 769
General Cable | EHTC® | EPR | CSPE | 10 | 5 | TS | TS | 15.621 | 0.43901 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343820 | 782
General Cable | FREP® | EPR | CPE | 10 | 5 | TS | TP | 15.748 | 0.4271 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367240 | 898
General Cable | FREP® | EPR | CPE | 10 | 5 | TS | TP | 15.621 | 0.42264 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279620 | 899
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 5 | TS | TS | 15.113 | 0.45984 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378680 | 1129
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 10 | 5 | TS | TP | 20.828 | 0.51788 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3165 | 610
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 10 | 5 | Sil | TP | 24.13 | 0.70241 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3655 | 647
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 10 | 5 | TS | TS | 21.336 | 0.69944 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6455 | 826
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 5 | TS | TS | 18.034 | 0.57741 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2455 | 847
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 5 | TS | TS | 16.002 | 0.49705 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2455 | 848
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 10 | 5 | TS | TS | 19.05 | 0.61908 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6455 | 877
Okonite | FRM-N® Okolon® | EPR | CSPE | 10 | 5 | TS | TS | 17.272 | 0.5283 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2455 | 912
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 10 | 5 | TS | TS | 19.304 | 0.60271 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2455 | 931
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 5 | TS | TS | 12.7 | 0.34972 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0050 | 93
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 5 | Sil | Fiber | 17.78 | 0.55062 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2050 | 118
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 5 | TS | TS | 13.97 | 0.4018 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C17-0050 | 298
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 5 | TS | TS | 15.748 | 0.49109 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-0050 | 808
GENERIC | GENERIC | TP | TP | 10 | 6 | TP | TP | 16.51 | 0.47621 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8063 | 1067
GENERIC | GENERIC | TS | TS | 10 | 6 | TS | TS | 23.876 | 0.78575 | 3.175 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13387 | 1536
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 10 | 6 | TS | TS | 23.876 | 0.78575 | 3.175 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13387 | 1536
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 10 | 6 | TS | TP | 21.844 | 0.67116 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3506 | 626
GENERIC | GENERIC | TP | TP | 10 | 7 | TP | TP | 15.6464 | 0.52383 | 1.524
GENERIC | GENERIC | TS | TS | 10 | 7 | TS | TS | 18.542 | 0.66521 | 1.524
American Insulated Wire | Type Tc - Composite (Power and Control) | PVC | PVC | 10 | 7 | TP | TP | 13.081 | 0.39436 | 1.143 | Industrial Grade | 4 Pwr & 4 or 6 Control (14 AWG), 600V, 90°C dry 75°C wet | 22132 | 477
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 10 | 7 | TP | TP | 15.6464 | 0.52383 | 1.524 | Industrial Grade | Unshielded, 600V | 68145 | 1120
Dekoron | 1735 | PE | PVC | 10 | 7 | TP | TP | 17.6784 | 0.48871 | 1.524 | Industrial Grade | 600V |  | 658
Dekoron | 1C99 | PVC | PVC | 10 | 7 | TP | TP | 16.764 | 0.54913 | 1.524 | Industrial Grade | 600V |  | 669
Draka | 20-10 Control Cable | PE | PVC | 10 | 7 | TP | TP | 17.272 | 0.54169 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 74070 | 691
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 7 | TP | TP | 16.51 | 0.53872 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8073 | 1068
General Cable | 20/10 | PE | PVC | 10 | 7 | TP | TP | 16.764 | 0.54318 | 1.524 | Industrial Grade | Unshielded, 600V | 257800 | 678
General Cable | VNTC® | PVC | PVC | 10 | 7 | TP | TP | 15.748 | 0.52086 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236340 | 1149
Okonite | Okozel® | ETFE | ETFE | 10 | 7 | TP | TP | 13.462 | 0.47175 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3557 | 29
Okonite | P-30 | PE | PVC | 10 | 7 | TP | TP | 17.272 | 0.5402 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2457 | 999
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 10 | 7 | TS | TP | 16.637 | 0.51044 | 1.524 | Industrial Grade | Unshielded, 600V | 40941 | 1110
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 7 | TS | TS | 17.018 | 0.53872 | 1.524 | Industrial Grade | Unshielded, 600V | 19898 | 1171
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 10 | 7 | TS | TP | 16.637 | 0.50002 | 1.524 | Industrial Grade | Unshielded, 600V | 40968 | 1184
Dekoron | 2X35 | XLPE | PVC | 10 | 7 | TS | TP | 17.6784 | 0.57741 | 1.524 | Industrial Grade | 600V | 2X35-B1260 | 709
Draka | General Purpose Control XLPE | XLPE | CPE | 10 | 7 | TS | TP | 17.526 | 0.59229 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 228070 | 979
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 7 | TS | TP | 17.526 | 0.5908 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 208070 | 985
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 7 | TS | TP | 19.05 | 0.65777 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 258070 | 986
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 7 | TS | TP | 17.526 | 0.5908 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 108073 | 1097
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 7 | TS | TP | 19.05 | 0.65777 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 158073 | 1098
General Cable | CHTC® | XLPE | CSPE | 10 | 7 | TS | TS | 17.018 | 0.55955 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 224130 | 751
General Cable | CVTC® | XLPE | PVC | 10 | 7 | TS | TP | 17.018 | 0.55211 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770900 | 770
General Cable | EHTC® | EPR | CSPE | 10 | 7 | TS | TS | 17.018 | 0.56848 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343830 | 783
General Cable | FREP® | EPR | CPE | 10 | 7 | TS | TP | 17.145 | 0.57145 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367250 | 900
General Cable | FREP® | EPR | CPE | 10 | 7 | TS | TP | 17.018 | 0.56699 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279630 | 901
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 7 | TS | TS | 16.4592 | 0.55657 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378690 | 1130
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 10 | 7 | TS | TP | 21.844 | 0.64884 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3167 | 611
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 10 | 7 | Sil | TP | 26.416 | 0.87802 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3657 | 648
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 7 | TS | TS | 19.558 | 0.71134 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2457 | 849
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 7 | TS | TS | 17.272 | 0.61759 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2457 | 850
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 10 | 7 | TS | TS | 20.574 | 0.77087 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6457 | 878
Okonite | FRM-N® Okolon® | EPR | CSPE | 10 | 7 | TS | TS | 18.542 | 0.66521 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2457 | 913
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 10 | 7 | TS | TS | 21.082 | 0.7545 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2457 | 932
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 10 | 7 | TS | TS | 23.876 | 0.93159 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6457 | 1280
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 7 | Sil | Fiber | 20.066 | 0.59527 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2070 | 119
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 7 | TS | TS | 15.24 | 0.50598 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C17-0070 | 299
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 7 | TS | TS | 14.478 | 0.47621 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0070 | 577
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 7 | TS | TS | 16.764 | 0.5655 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-0070 | 809
GENERIC | GENERIC | TP | TP | 10 | 8 | TP | TP | 18.034 | 0.61461 | 1.524
GENERIC | GENERIC | TS | TS | 10 | 8 | TS | TS | 27.432 | 1.1102 | 2.794
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 8 | TP | TP | 18.034 | 0.61461 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8083 | 1069
Okonite | P-30 | PE | PVC | 10 | 8 | TP | TP | 18.542 | 0.61164 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2458 | 1000
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 10 | 8 | TS | TS | 27.432 | 1.1102 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7456 | 1530
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 10 | 8 | TS | TS | 28.194 | 1.1087 | 3.556 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13388 | 1552
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 10 | 8 | TS | TP | 25.4 | 0.84528 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3508 | 627
GENERIC | GENERIC | TP | TP | 10 | 9 | TP | TP | 19.304 | 0.68604 | 1.524
GENERIC | GENERIC | TS | TS | 10 | 9 | TS | TS | 21.336 | 0.85272 | 1.524
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 10 | 9 | TP | TP | 18.1864 | 0.66223 | 1.524 | Industrial Grade | Unshielded, 600V | 68146 | 1121
Dekoron | 1735 | PE | PVC | 10 | 9 | TP | TP | 20.4724 | 0.59998 | 1.524 | Industrial Grade | 600V |  | 659
Dekoron | 1C99 | PVC | PVC | 10 | 9 | TP | TP | 19.3548 | 0.68902 | 1.524 | Industrial Grade | 600V |  | 670
Draka | 20-10 Control Cable | PE | PVC | 10 | 9 | TP | TP | 20.447 | 0.68753 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 74090 | 692
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 9 | TP | TP | 19.304 | 0.68604 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8093 | 1070
General Cable | 20/10 | PE | PVC | 10 | 9 | TP | TP | 19.304 | 0.69348 | 1.524 | Industrial Grade | Unshielded, 600V | 261690 | 679
General Cable | VNTC® | PVC | PVC | 10 | 9 | TP | TP | 18.415 | 0.65479 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 243620 | 1150
Okonite | Okozel® | ETFE | ETFE | 10 | 9 | TP | TP | 15.748 | 0.60271 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3559 | 30
Okonite | P-30 | PE | PVC | 10 | 9 | TP | TP | 20.066 | 0.69348 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2459 | 1001
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 9 | TS | TS | 19.812 | 0.74259 | 1.524 | Industrial Grade | Unshielded, 600V | 29709 | 1172
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 10 | 9 | TS | TP | 19.431 | 0.64289 | 1.524 | Industrial Grade | Unshielded, 600V | 40969 | 1185
Dekoron | 2X35 | XLPE | PVC | 10 | 9 | TS | TP | 20.4724 | 0.72325 | 1.524 | Industrial Grade | 600V | 2X35-B0960 | 710
Draka | General Purpose Control XLPE | XLPE | CPE | 10 | 9 | TS | TP | 20.447 | 0.73813 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 228090 | 980
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 9 | TS | TP | 20.447 | 0.73813 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 208090 | 987
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 9 | TS | TP | 20.447 | 0.73813 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 108093 | 1099
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 9 | TS | TP | 23.114 | 0.87802 | 2.032 | Industrial Grade | Shielded, 600V, 90°C | 258090 | 1370
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 9 | TS | TP | 23.114 | 0.87802 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 158093 | 1429
General Cable | CHTC® | XLPE | CSPE | 10 | 9 | TS | TS | 19.431 | 0.6786 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 347060 | 752
General Cable | CVTC® | XLPE | PVC | 10 | 9 | TS | TP | 19.939 | 0.71283 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770390 | 771
General Cable | EHTC® | EPR | CSPE | 10 | 9 | TS | TS | 19.431 | 0.73218 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343840 | 784
General Cable | FREP® | EPR | CPE | 10 | 9 | TS | TP | 19.431 | 0.69497 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367260 | 902
General Cable | FREP® | EPR | CPE | 10 | 9 | TS | TP | 19.304 | 0.69051 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279640 | 903
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 9 | TS | TS | 19.1516 | 0.77831 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378700 | 1131
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 10 | 9 | TS | TP | 25.4 | 0.80956 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3169 | 606
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 10 | 9 | Sil | TP | 29.718 | 1.0462 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3659 | 649
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 9 | TS | TS | 20.066 | 0.87355 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2459 | 851
Okonite | FRM-N® Okolon® | EPR | CSPE | 10 | 9 | TS | TS | 21.336 | 0.85272 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2459 | 914
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 10 | 9 | TS | TS | 27.178 | 1.1563 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6459 | 1281
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 9 | TS | TS | 23.876 | 0.95391 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2459 | 1295
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 10 | 9 | TS | TS | 24.384 | 1.0179 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6459 | 1306
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 10 | 9 | TS | TS | 25.4 | 1.0789 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2459 | 1340
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 9 | Sil | Fiber | 23.114 | 0.84825 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2090 | 120
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 9 | TS | TS | 18.034 | 0.65479 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C17-0090 | 300
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 9 | TS | TS | 17.018 | 0.63991 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0090 | 578
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 9 | TS | TS | 19.812 | 0.75152 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-0090 | 810
GENERIC | GENERIC | TP | TP | 10 | 10 | TP | TP | 20.828 | 0.76343 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8103 | 1071
GENERIC | GENERIC | TS | TS | 10 | 10 | TS | TS | 20.701 | 0.80212 | 1.524 | Industrial Grade | Unshielded, 600V | 31290 | 1173
GENERIC | GENERIC | TP | TP | 10 | 11 | TP | TP | 21.59 | 0.83188 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8113 | 1072
GENERIC | GENERIC | TS | TS | 10 | 11 | TS | TP | 27.432 | 1.0477 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3511 | 624
GENERIC | GENERIC | TP | TP | 10 | 12 | TP | TP | 21.717 | 0.88397 | 1.524
GENERIC | GENERIC | TS | TS | 10 | 12 | TS | TS | 24.892 | 1.0938 | 2.032
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 10 | 12 | TP | TP | 20.6248 | 0.86165 | 1.524 | Industrial Grade | Unshielded, 600V | 68147 | 1122
Dekoron | 1C99 | PVC | PVC | 10 | 12 | TP | TP | 21.717 | 0.88397 | 1.524 | Industrial Grade | 600V |  | 671
Dekoron | 1735 | PE | PVC | 10 | 12 | TP | TP | 24.003 | 0.035716 | 2.032 | Industrial Grade | 600V |  | 1201
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 12 | TP | TP | 21.59 | 0.85272 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8123 | 1073
Draka | 20-10 Control Cable | PE | PVC | 10 | 12 | TP | TP | 23.749 | 0.94945 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 74120 | 1213
General Cable | 20/10 | PE | PVC | 10 | 12 | TP | TP | 22.86 | 0.93159 | 1.524 | Industrial Grade | Unshielded, 600V | 257810 | 680
General Cable | VNTC® | PVC | PVC | 10 | 12 | TP | TP | 20.701 | 0.86909 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236350 | 1151
Okonite | Okozel® | ETFE | ETFE | 10 | 12 | TP | TP | 18.034 | 0.81849 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3562 | 31
Okonite | P-30 | PE | PVC | 10 | 12 | TP | TP | 23.622 | 0.94052 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2462 | 1375
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 12 | TS | TS | 22.86 | 1.0015 | 2.032 | Industrial Grade | Unshielded, 600V | 27443 | 1487
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 10 | 12 | TS | TP | 22.352 | 0.86462 | 2.032 | Industrial Grade | Unshielded, 600V | 40970 | 1500
Dekoron | 2X35 | XLPE | PVC | 10 | 12 | TS | TP | 24.003 | 0.98219 | 2.032 | Industrial Grade | 600V | 2X35-B1260 | 1225
Draka | General Purpose Control XLPE | XLPE | CPE | 10 | 12 | TS | TP | 23.749 | 0.98368 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 228120 | 1369
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 12 | TS | TP | 23.749 | 0.98368 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 208120 | 1371
Draka | General Purpose Control XLPE | XLPE | PVC | 10 | 12 | TS | TP | 25.654 | 1.1131 | 2.032 | Industrial Grade | Shielded, 600V, 90°C | 258120 | 1372
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 12 | TS | TP | 23.749 | 0.98368 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 108123 | 1430
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 10 | 12 | TS | TP | 25.654 | 1.1131 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 158123 | 1431
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 10 | 12 | TS | TS | 30.48 | 1.3542 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 22752 | 1531
General Cable | CHTC® | XLPE | CSPE | 10 | 12 | TS | TS | 22.987 | 0.94647 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 347070 | 1244
General Cable | CVTC® | XLPE | PVC | 10 | 12 | TS | TP | 22.733 | 0.95838 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770400 | 1253
General Cable | EHTC® | EPR | CSPE | 10 | 12 | TS | TS | 22.987 | 0.98516 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 343860 | 1261
General Cable | FREP® | EPR | CPE | 10 | 12 | TS | TP | 23.114 | 0.97326 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367270 | 1324
General Cable | FREP® | EPR | CPE | 10 | 12 | TS | TP | 22.987 | 0.96879 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279650 | 1325
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 12 | TS | TS | 22.606 | 0.97921 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378710 | 1451
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 10 | 12 | TS | TP | 27.432 | 1.0179 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3172 | 605
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 10 | 12 | Sil | TP | 34.29 | 1.381 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3662 | 650
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 10 | 12 | TS | TS | 30.226 | 1.4331 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6462 | 1282
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 12 | TS | TS | 26.924 | 1.1905 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2462 | 1296
Okonite | FMR® Okolon® | EPR | CSPE | 10 | 12 | TS | TS | 23.876 | 1.0878 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2462 | 1297
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 10 | 12 | TS | TS | 26.924 | 1.2664 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6462 | 1307
Okonite | FRM-N® Okolon® | EPR | CSPE | 10 | 12 | TS | TS | 24.892 | 1.0938 | 2.032 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2462 | 1330
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 10 | 12 | TS | TS | 28.194 | 1.2798 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2462 | 1341
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 12 | Sil | Fiber | 26.162 | 1.0268 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2120 | 121
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 12 | TS | TS | 19.304 | 0.81105 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0120 | 579
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 12 | TS | TS | 21.336 | 0.8929 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C17-0120 | 1191
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 12 | TS | TS | 23.114 | 0.98963 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-0120 | 1269
GENERIC | GENERIC | TP | TP | 10 | 13 | TP | TP | 23.749 | 1.0194 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8133 | 1412
GENERIC | GENERIC | TP | TP | 10 | 14 | TP | TP | 23.749 | 1.0804 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8143 | 1413
GENERIC | GENERIC | TP | TP | 10 | 15 | TP | TP | 25.019 | 1.1563 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8153 | 1414
GENERIC | GENERIC | TS | TS | 10 | 15 | TS | TS | 25.146 | 1.1742 | 2.032 | Industrial Grade | Unshielded, 600V | 31291 | 1488
Draka | 20-10 Control Cable | PE | PVC | 10 | 15 | TP | TP | 26.289 | 1.1608 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 74150 | 1214
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 15 | TP | TP | 25.019 | 1.1563 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8153 | 1414
GENERIC | GENERIC | TP | TP | 10 | 16 | TP | TP | 25.019 | 1.2203 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8163 | 1415
GENERIC | GENERIC | TS | TS | 10 | 16 | TS | TS | 34.29 | 1.7665 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | 23658 | 1545
GENERIC | GENERIC | TP | TP | 10 | 17 | TP | TP | 26.162 | 1.3334 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8173 | 1416
GENERIC | GENERIC | TP | TP | 10 | 18 | TP | TP | 26.162 | 1.3989 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8183 | 1417
GENERIC | GENERIC | TP | TP | 10 | 19 | TP | TP | 26.67 | 1.384 | 1.524
GENERIC | GENERIC | TS | TS | 10 | 19 | TS | TS | 26.3652 | 1.4524 | 2.032
Dekoron | 1C99 | PVC | PVC | 10 | 19 | TP | TP | 26.3144 | 1.381 | 1.524 | Industrial Grade | 600V |  | 672
Draka | 20-10 Control Cable | PE | PVC | 10 | 19 | TP | TP | 27.686 | 1.4257 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 74190 | 1215
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 10 | 19 | TP | TP | 26.162 | 1.4614 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 8193 | 1418
General Cable | 20/10 | PE | PVC | 10 | 19 | TP | TP | 26.67 | 1.384 | 1.524 | Industrial Grade | Unshielded, 600V | 271740 | 681
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 19 | TS | TS | 27.178 | 1.4182 | 2.032 | Industrial Grade | Unshielded, 600V | 31292 | 1489
General Cable | Ultrol® 275 | XLPE | CSPE | 10 | 19 | TS | TS | 26.3652 | 1.4524 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378720 | 1452
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 19 | Sil | Fiber | 30.988 | 1.6221 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2190 | 122
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 19 | TS | TS | 24.638 | 1.3393 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C17-0190 | 1192
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 19 | TS | TS | 23.368 | 1.2724 | 1.651 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0190 | 1198
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 19 | TS | TS | 27.178 | 1.4584 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-1190 | 1270
GENERIC | GENERIC | TS | TS | 10 | 20 | TS | TS | 38.1 | 2.1206 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | 12920 | 1546
GENERIC | GENERIC | TS | TS | 10 | 23 | TS | TS | 29.972 | 1.6906 | 2.032 | Industrial Grade | Unshielded, 600V | 31923 | 1490
GENERIC | GENERIC | TS | TS | 10 | 24 | TS | TS | 30.48 | 1.8111 | 2.032 | Industrial Grade | Unshielded, 600V | 31924 | 1491
GENERIC | GENERIC | TP | TP | 10 | 25 | TP | TP | 33.02 | 1.8528 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 74250 | 1216
GENERIC | GENERIC | TS | TS | 10 | 25 | TS | TS | 28.702 | 1.756 | 1.651
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 25 | TS | TS | 28.702 | 1.756 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C17-0250 | 1193
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 25 | TS | TS | 27.432 | 1.6742 | 1.651 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0250 | 1199
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 25 | TS | TS | 31.496 | 1.89 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-3570 | 1271
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 25 | Sil | Fiber | 36.322 | 2.2174 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2250 | 123
GENERIC | GENERIC | TP | TP | 10 | 30 | TP | TP | 34.29 | 2.1787 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 74300 | 1217
GENERIC | GENERIC | TS | TS | 10 | 30 | TS | TS | 33.655 | 2.2695 | 2.032 | Industrial Grade | Unshielded, 600V | 31295 | 1492
GENERIC | GENERIC | TP | TP | 10 | 37 | TP | TP | 37.084 | 2.646 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 74370 | 1218
GENERIC | GENERIC | TS | TS | 10 | 37 | TS | TS | 33.274 | 2.5001 | 1.651
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 10 | 37 | TS | TP | 31.369 | 1.6965 | 2.032 | Industrial Grade | Unshielded, 600V | 40937 | 1438
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 10 | 37 | TS | TS | 36.449 | 2.8275 | 2.032 | Industrial Grade | Unshielded, 600V | 31296 | 1493
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 10 | 37 | TS | TS | 33.274 | 2.5001 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C17-0370 | 1194
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 10 | 37 | TS | TS | 31.75 | 2.4108 | 1.651 | Industrial Grade | Unshielded, 600V, UL Type TC | C10-0370 | 1200
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 10 | 37 | TS | TS | 35.56 | 2.6936 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C51-3571 | 1272
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 10 | 37 | Sil | Fiber | 42.418 | 3.0731 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-2370 | 124
GENERIC | GENERIC | TS | TP | 10 | 3+G | TS | TP | 12.319 | 0.33484 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279680 | 343
GENERIC | GENERIC | TS | N/A | 12 | 1 | TS | None | 4.0386 | 0.041669 | 0.762 | Industrial Grade | Single Conductor, 600V, 90°C |  | 61
GENERIC | GENERIC | TP | TP | 12 | 2 | TP | TP | 9.017 | 0.12649 | 1.143
GENERIC | GENERIC | TS | TS | 12 | 2 | TS | TS | 12.192 | 0.24257 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 12 | 2 | TP | TS | 9.144 | 0.16221 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38809 | 184
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 2 | TP | TP | 7.5692 | 0.1012 | 0.762 | Industrial Grade | Unshielded, 600V | 181202C6 | 40
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 2 | TP | TP | 6.9596 | 0.10268 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 257
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 2 | TP | TP | 8.7376 | 0.13691 | 1.143 | Industrial Grade | Unshielded, 600V | 181202C6 | 272
Dekoron | 1C99 | PVC | PVC | 12 | 2 | TP | TP | 9.5758 | 0.1384 | 1.143 | Industrial Grade | 600V |  | 140
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 12 | 2 | TP | TP | 9.525 | 0.15179 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 7702 | 450
General Cable | 20/10 | PE | PVC | 12 | 2 | TP | TP | 10.16 | 0.12947 | 1.143 | Industrial Grade | Unshielded, 600V | 257770 | 151
General Cable | VNTC® | PVC | PVC | 12 | 2 | TP | TP | 9.017 | 0.12649 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 260150 | 532
General Cable | VNTC® | PVC | PVC | 12 | 2 | TP | TP | 9.398 | 0.12352 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243670 | 533
Okonite | Okozel® | ETFE | ETFE | 12 | 2 | TP | TP | 7.112 | 0.11012 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3452 | 12
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 2 | TS | TS | 10.414 | 0.16667 | 1.143 | Industrial Grade | Unshielded, 600V | 19885 | 559
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 12 | 2 | TS | TS | 10.541 | 0.17858 | 1.143 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 23098 | 569
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 2 | TS | TS | 8.763 | 0.1131 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 212-02 | 55
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 12 | 2 | TS | TS | 10.668 | 0.14733 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 812-02 | 210
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 2 | TS | TP | 12.319 | 0.20388 | 1.143 | Industrial Grade | Shielded, 600V, 90°C | 256020 | 388
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 2 | TS | TP | 12.319 | 0.20388 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 156023 | 464
General Cable | CHTC® | XLPE | CSPE | 12 | 2 | TS | TS | 10.414 | 0.14584 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 272260 | 194
General Cable | CVTC® | XLPE | PVC | 12 | 2 | TS | TP | 10.414 | 0.14286 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 346920 | 221
General Cable | EHTC® | EPR | CSPE | 12 | 2 | TS | TS | 10.414 | 1.3676 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 343670 | 236
General Cable | FREP® | EPR | CPE | 12 | 2 | TS | TP | 10.541 | 0.14435 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367160 | 332
General Cable | FREP® | EPR | CPE | 12 | 2 | TS | TP | 10.414 | 0.13989 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 307690 | 333
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 2 | TS | TS | 10.0838 | 0.15775 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378510 | 504
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 2 | TS | TS | 11.2522 | 0.24555 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378970 | 518
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 2 | TS | TS | 12.192 | 0.24257 | 1.143 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2302 | 309
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 2 | TS | TS | 10.668 | 0.18453 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2302 | 310
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 2 | TS | TS | 10.922 | 0.19197 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2302 | 351
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 2 | TS | TS | 13.462 | 0.23662 | 1.143 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2302 | 358
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 2 | TS | TP | 16.256 | 0.24406 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3082 | 596
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 12 | 2 | TS | TP | 16.256 | 0.29763 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3452 | 618
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 2 | Sil | TP | 18.542 | 0.34823 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3552 | 636
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 2 | TS | TS | 17.018 | 0.38097 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6302 | 818
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 2 | TS | TS | 17.018 | 0.40032 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6302 | 868
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 2 | TS | TS | 9.398 | 0.13393 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C16-0020 | 71
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 2 | TS | TS | 8.89 | 0.11161 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0020 | 85
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 2 | Sil | Fiber | 12.954 | 0.17858 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1020 | 105
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 2 | TS | TS | 10.414 | 0.1637 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0020 | 286
GENERIC | GENERIC | TP | TP | 12 | 3 | TP | TP | 10.033 | 0.1637 | 1.143
GENERIC | GENERIC | TS | TS | 12 | 3 | TS | TS | 12.192 | 0.23811 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 12 | 3 | TP | TS | 9.652 | 0.17114 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38515 | 185
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 3 | TP | TP | 9.9822 | 0.16816 | 1.143 | Industrial Grade | Unshielded, 600V | 68128 | 492
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 3 | TP | TP | 8.0518 | 0.1384 | 0.762 | Industrial Grade | Unshielded, 600V | 181203C6 | 41
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 3 | TP | TP | 7.4168 | 0.14584 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 258
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 3 | TP | TP | 9.2456 | 0.18304 | 1.143 | Industrial Grade | Unshielded, 600V | 181203C6 | 273
Dekoron | 1735 | PE | PVC | 12 | 3 | TP | TP | 11.4808 | 0.017114 | 1.143 | Industrial Grade | 600V |  | 128
Dekoron | 1C99 | PVC | PVC | 12 | 3 | TP | TP | 10.287 | 0.18007 | 1.143 | Industrial Grade | 600V |  | 141
Draka | 20-10 Control Cable | PE | PVC | 12 | 3 | TP | TP | 11.303 | 0.18751 | 1.143 | Industrial Grade | Unshielded, 1000V, 75°C | 73030 | 166
Draka | Power & Control 3 THHN/THWN | PVC | PVC | 12 | 3 | TP | TP | 10.795 | 0.20983 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 6047 | 409
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 3 | TP | TP | 10.033 | 0.1637 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6033 | 433
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 12 | 3 | TP | TP | 10.033 | 0.19346 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 7703 | 451
General Cable | 20/10 | PE | PVC | 12 | 3 | TP | TP | 10.922 | 0.17263 | 1.143 | Industrial Grade | Unshielded, 600V | 267830 | 152
General Cable | VNTC® | PVC | PVC | 12 | 3 | TP | TP | 9.779 | 0.1637 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 234590 | 534
General Cable | VNTC® | PVC | PVC | 12 | 3 | TP | TP | 9.906 | 0.16519 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243810 | 535
General Cable | VNTC® | PVC | PVC | 12 | 3 | TP | TP | 10.668 | 0.12798 | 1.143 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 234250 | 536
Okonite | Okozel® | ETFE | ETFE | 12 | 3 | TP | TP | 7.62 | 0.14584 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3453 | 13
Okonite | P-30 | PE | PVC | 12 | 3 | TP | TP | 11.176 | 0.17709 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2303 | 401
Okonite | P-45 | PE | PVC | 12 | 3 | TP | TP | 12.954 | 0.20537 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3330 | 407
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 3 | TS | TP | 10.668 | 0.1637 | 1.143 | Industrial Grade | Unshielded, 600V | 40928 | 482
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 3 | TS | TS | 11.43 | 0.2143 | 1.143 | Industrial Grade | Unshielded, 600V | 19886 | 560
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 12 | 3 | TS | TS | 11.049 | 0.2262 | 1.143 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 24902 | 570
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 3 | TS | TP | 10.795 | 0.16072 | 1.143 | Industrial Grade | Unshielded, 600V | 40817 | 583
Dekoron | 2X35 | XLPE | PVC | 12 | 3 | TS | TP | 11.4808 | 0.2009 | 1.143 | Industrial Grade | 600V | 2X35-41260 | 174
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 3 | TS | TS | 9.398 | 0.15328 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 212-03 | 56
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 12 | 3 | TS | TS | 11.303 | 0.19346 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 812-03 | 211
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 3 | TS | TP | 11.176 | 0.19495 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 226030 | 384
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 3 | TS | TP | 11.176 | 0.19495 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 206030 | 389
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 3 | TS | TP | 12.954 | 0.24257 | 1.143 | Industrial Grade | Shielded, 600V, 90°C | 256030 | 390
Draka | Power & Control Type TC 3 XHHW-2 1 bare | XLPE | PVC | 12 | 3 | TS | TP | 10.795 | 0.20983 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 6047 | 422
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 12 | 3 | TS | TP | 13.081 | 0.28573 | 1.143 | Industrial Grade | Shielded (Copper), 600V, 90°C | 156047 | 425
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 3 | TS | TP | 11.176 | 0.19495 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 106033 | 465
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 3 | TS | TP | 12.954 | 0.24257 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 156033 | 466
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 3 | TS | TS | 16.256 | 0.34228 | 2.413 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13393 | 1502
General Cable | CHTC® | XLPE | CSPE | 12 | 3 | TS | TS | 11.049 | 0.189 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 223910 | 195
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 12 | 3 | TS | TS | 12.065 | 0.12649 | 1.143 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 309340 | 201
General Cable | CVTC® | XLPE | PVC | 12 | 3 | TS | TP | 11.049 | 0.18602 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770570 | 222
General Cable | CVTC® | XLPE | PVC | 12 | 3 | TS | TP | 12.065 | 0.23364 | 1.143 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 383870 | 223
General Cable | EHTC® | EPR | CSPE | 12 | 3 | TS | TS | 12.192 | 0.23811 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 383840 | 237
General Cable | EHTC® | EPR | CSPE | 12 | 3 | TS | TS | 12.065 | 0.12649 | 1.143 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 383810 | 238
General Cable | EHTC® | EPR | CSPE | 12 | 3 | TS | TS | 11.049 | 0.19197 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 343680 | 239
General Cable | FREP® | EPR | CPE | 12 | 3 | TS | TP | 11.176 | 0.189 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367170 | 335
General Cable | FREP® | EPR | CPE | 12 | 3 | TS | TP | 11.049 | 0.18453 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280300 | 336
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 3 | TS | TS | 10.668 | 0.18304 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378520 | 505
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 3 | TS | TS | 11.938 | 0.29019 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378980 | 519
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 3 | TS | TS | 12.954 | 0.27085 | 1.143 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2303 | 311
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 3 | TS | TS | 11.43 | 0.22471 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2303 | 312
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 3 | TS | TS | 11.43 | 0.23364 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2303 | 352
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 3 | TS | TP | 16.256 | 0.28126 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3083 | 597
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 3 | Sil | TP | 19.812 | 0.40776 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3553 | 637
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 3 | TS | TS | 17.018 | 0.41222 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6303 | 819
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 3 | TS | TS | 17.018 | 0.42859 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6303 | 869
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 3 | TS | TS | 15.24 | 0.32888 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2303 | 924
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 3 | TS | TS | 9.906 | 0.17858 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C16-0030 | 72
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 3 | TS | TS | 9.398 | 0.15626 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0030 | 86
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 3 | Sil | Fiber | 13.97 | 0.22322 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1030 | 106
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 3 | TS | TS | 10.922 | 0.20834 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0030 | 287
GENERIC | GENERIC | TP | TP | 12 | 4 | TP | TP | 10.668 | 0.20685 | 1.143
GENERIC | GENERIC | TS | TS | 12 | 4 | TS | TS | 12.446 | 0.29466 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 12 | 4 | TP | TS | 10.541 | 0.21727 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38516 | 186
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 4 | TP | TP | 10.3124 | 0.21578 | 1.143 | Industrial Grade | Unshielded, 600V | 68130 | 493
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 4 | TP | TP | 8.8138 | 0.17858 | 0.762 | Industrial Grade | Unshielded, 600V | 181204C6 | 42
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 4 | TP | TP | 8.1534 | 0.18751 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 259
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 4 | TP | TP | 10.033 | 0.2262 | 1.143 | Industrial Grade | Unshielded, 600V | 181204C6 | 274
Draka | 20-10 Control Cable | PE | PVC | 12 | 4 | TP | TP | 12.319 | 0.23513 | 1.143 | Industrial Grade | Unshielded, 1000V, 75°C | 73040 | 167
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 4 | TP | TP | 10.922 | 0.20685 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6043 | 434
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 12 | 4 | TP | TP | 10.922 | 0.23811 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 7704 | 452
General Cable | 20/10 | PE | PVC | 12 | 4 | TP | TP | 11.938 | 0.21876 | 1.143 | Industrial Grade | Unshielded, 600V | 257730 | 153
General Cable | VNTC® | PVC | PVC | 12 | 4 | TP | TP | 10.668 | 0.20537 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 234600 | 537
General Cable | VNTC® | PVC | PVC | 12 | 4 | TP | TP | 10.668 | 0.20685 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243840 | 538
Okonite | Okozel® | ETFE | ETFE | 12 | 4 | TP | TP | 8.636 | 0.18751 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3454 | 14
Okonite | P-30 | PE | PVC | 12 | 4 | TP | TP | 12.192 | 0.22322 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2304 | 402
Okonite | P-45 | PE | PVC | 12 | 4 | TP | TP | 14.986 | 0.28573 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-4330 | 1006
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 4 | TS | TP | 11.684 | 0.20834 | 1.143 | Industrial Grade | Unshielded, 600V | 40929 | 483
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 4 | TS | TS | 12.446 | 0.27382 | 1.143 | Industrial Grade | Unshielded, 600V | 19887 | 561
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 4 | TS | TP | 11.811 | 0.20388 | 1.143 | Industrial Grade | Unshielded, 600V | 40818 | 584
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 4 | TS | TS | 10.287 | 0.19644 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 212-04 | 57
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 12 | 4 | TS | TS | 12.446 | 0.24406 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 812-04 | 212
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 4 | TS | TP | 12.319 | 0.24406 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 226040 | 385
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 4 | TS | TP | 12.319 | 0.24406 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 206040 | 391
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 4 | TS | TP | 12.319 | 0.24406 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 106043 | 467
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 4 | TS | TP | 14.859 | 0.33484 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 256040 | 970
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 4 | TS | TP | 14.859 | 0.33484 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 156043 | 1084
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 4 | TS | TS | 17.526 | 0.4018 | 2.413 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13394 | 1503
General Cable | CHTC® | XLPE | CSPE | 12 | 4 | TS | TS | 12.065 | 0.23811 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 223930 | 196
General Cable | CVTC® | XLPE | PVC | 12 | 4 | TS | TP | 12.065 | 0.23364 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770490 | 224
General Cable | EHTC® | EPR | CSPE | 12 | 4 | TS | TS | 12.065 | 0.24257 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 343690 | 240
General Cable | FREP® | EPR | CPE | 12 | 4 | TS | TP | 12.192 | 0.23811 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 326650 | 337
General Cable | FREP® | EPR | CPE | 12 | 4 | TS | TP | 12.065 | 0.23364 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280310 | 338
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 4 | TS | TS | 11.684 | 0.25596 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378530 | 506
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 4 | TS | TS | 13.081 | 0.41073 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378990 | 520
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 4 | TS | TS | 12.446 | 0.27977 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2304 | 313
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 4 | TS | TS | 12.446 | 0.29466 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2304 | 353
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 4 | TS | TP | 17.526 | 0.33633 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3084 | 598
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 4 | Sil | TP | 20.828 | 0.48365 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3554 | 638
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 4 | TS | TS | 18.288 | 0.48217 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6304 | 820
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 4 | TS | TS | 14.986 | 0.36311 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2304 | 837
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 4 | TS | TS | 17.018 | 0.45091 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6304 | 870
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 4 | TS | TS | 16.51 | 0.38841 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2304 | 925
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 4 | TS | TS | 10.922 | 0.21578 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C16-0040 | 73
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 4 | TS | TS | 10.16 | 0.19346 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0040 | 87
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 4 | Sil | Fiber | 15.494 | 0.31996 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1040 | 107
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 4 | TS | TS | 11.938 | 0.26043 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0040 | 288
GENERIC | GENERIC | TP | TP | 12 | 5 | TP | TP | 12.1158 | 0.26638 | 1.143
GENERIC | GENERIC | TS | TS | 12 | 5 | TS | TS | 14.478 | 0.37502 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 12 | 5 | TP | TS | 11.43 | 0.26341 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38517 | 187
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 5 | TP | TP | 11.2776 | 0.26043 | 1.143 | Industrial Grade | Unshielded, 600V | 68131 | 494
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 5 | TP | TP | 9.6774 | 0.21876 | 0.762 | Industrial Grade | Unshielded, 600V | 181205C6 | 43
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 5 | TP | TP | 8.9916 | 0.22918 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 260
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 5 | TP | TP | 10.9474 | 0.27085 | 1.143 | Industrial Grade | Unshielded, 600V | 181205C6 | 275
Dekoron | 1C99 | PVC | PVC | 12 | 5 | TP | TP | 12.1158 | 0.26638 | 1.143 | Industrial Grade | 600V |  | 142
Dekoron | 1735 | PE | PVC | 12 | 5 | TP | TP | 13.6398 | 0.020239 | 1.524 | Industrial Grade | 600V |  | 653
Draka | 20-10 Control Cable | PE | PVC | 12 | 5 | TP | TP | 14.224 | 0.29763 | 1.143 | Industrial Grade | Unshielded, 1000V, 75°C | 73050 | 168
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 5 | TP | TP | 11.938 | 0.2515 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6053 | 435
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 12 | 5 | TP | TP | 11.938 | 0.27382 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 7705 | 453
General Cable | 20/10 | PE | PVC | 12 | 5 | TP | TP | 13.208 | 0.26787 | 1.143 | Industrial Grade | Unshielded, 600V | 270720 | 154
General Cable | VNTC® | PVC | PVC | 12 | 5 | TP | TP | 11.303 | 0.24555 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 226420 | 539
Okonite | Okozel® | ETFE | ETFE | 12 | 5 | TP | TP | 9.398 | 0.22918 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3455 | 15
Okonite | P-30 | PE | PVC | 12 | 5 | TP | TP | 13.208 | 0.27531 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2305 | 403
Okonite | P-45 | PE | PVC | 12 | 5 | TP | TP | 16.256 | 0.35121 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3305 | 1007
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 5 | TS | TP | 12.827 | 0.25596 | 1.143 | Industrial Grade | Unshielded, 600V | 40930 | 484
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 5 | TS | TP | 12.954 | 0.2515 | 1.143 | Industrial Grade | Unshielded, 600V | 40960 | 585
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 5 | TS | TS | 13.97 | 0.34674 | 1.524 | Industrial Grade | Unshielded, 600V | 19888 | 1162
Dekoron | 2X35 | XLPE | PVC | 12 | 5 | TS | TP | 13.6398 | 0.29763 | 1.143 | Industrial Grade | 600V | 2X35-60 | 175
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 5 | TS | TS | 11.303 | 0.23959 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 212-05 | 58
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 5 | TS | TP | 13.462 | 0.30061 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 226050 | 386
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 5 | TS | TP | 13.462 | 0.30061 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 206050 | 392
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 5 | TS | TP | 13.462 | 0.30061 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 106053 | 468
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 5 | TS | TP | 16.002 | 0.38543 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 256050 | 971
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 5 | TS | TP | 16.002 | 0.38543 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 156053 | 1085
General Cable | CHTC® | XLPE | CSPE | 12 | 5 | TS | TS | 13.208 | 0.2887 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 223920 | 197
General Cable | CVTC® | XLPE | PVC | 12 | 5 | TS | TP | 13.081 | 0.28424 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770410 | 225
General Cable | EHTC® | EPR | CSPE | 12 | 5 | TS | TS | 13.208 | 0.29466 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 262200 | 241
General Cable | FREP® | EPR | CPE | 12 | 5 | TS | TP | 13.335 | 0.2887 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367180 | 339
General Cable | FREP® | EPR | CPE | 12 | 5 | TS | TP | 13.208 | 0.28424 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280320 | 340
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 5 | TS | TS | 12.9286 | 0.30507 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378540 | 507
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 5 | TS | TS | 17.4752 | 0.49705 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 379000 | 1139
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 5 | TS | TS | 13.462 | 0.34228 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2305 | 314
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 5 | TS | TP | 18.542 | 0.3899 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3085 | 599
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 5 | Sil | TP | 23.114 | 0.56848 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3555 | 639
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 5 | TS | TS | 19.558 | 0.56253 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6305 | 821
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 5 | TS | TS | 16.256 | 0.44347 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2305 | 838
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 5 | TS | TS | 17.018 | 0.48514 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6305 | 871
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 5 | TS | TS | 14.478 | 0.37502 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2305 | 907
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 5 | TS | TS | 17.78 | 0.4777 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2305 | 926
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 5 | TS | TS | 12.192 | 0.26787 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C16-0050 | 74
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 5 | TS | TS | 11.176 | 0.23811 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0050 | 88
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 5 | Sil | Fiber | 17.018 | 0.39436 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1050 | 108
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 5 | TS | TS | 12.954 | 0.31996 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0050 | 289
GENERIC | GENERIC | TP | TP | 12 | 6 | TP | TS | 12.446 | 0.31103 | 1.143
GENERIC | GENERIC | TS | TS | 12 | 6 | TS | TP | 19.812 | 0.503 | 1.27
American Insulated Wire | American SDN® | PVC | CP | 12 | 6 | TP | TS | 12.446 | 0.31103 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38518 | 188
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 6 | TP | TP | 11.6332 | 0.29614 | 1.143 | Industrial Grade | Unshielded, 600V | 68132 | 495
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 6 | TP | TP | 12.954 | 0.29614 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6063 | 436
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 6 | TS | TS | 15.24 | 0.38543 | 1.524 | Industrial Grade | Unshielded, 600V | 26154 | 1163
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 6 | TS | TS | 21.209 | 0.61015 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N5231 | 1514
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 6 | TS | TS | 21.209 | 0.59229 | 2.794 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13395 | 1518
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 12 | 6 | TS | TP | 19.812 | 0.503 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3456 | 619
GENERIC | GENERIC | TP | TP | 12 | 7 | TP | TP | 13.1572 | 0.34674 | 1.143
GENERIC | GENERIC | TS | TS | 12 | 7 | TS | TP | 15.8496 | 0.42264 | 1.524
American Insulated Wire | Type Tc - Composite (Power and Control) | PVC | PVC | 12 | 7 | TP | TP | 11.938 | 0.28573 | 1.143 | Industrial Grade | 3 Pwr & 4 or 6 Control (14 AWG), 600V, 90°C dry 75°C wet | 22131 | 476
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 7 | TP | TP | 12.319 | 0.33186 | 1.143 | Industrial Grade | Unshielded, 600V | 68133 | 496
American Insulated Wire | American SDN® | PVC | CP | 12 | 7 | TP | TS | 14.478 | 0.34228 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38810 | 728
Cable USA | CAROLFIRE | ETFE | ETFE | 12 | 7 | TP | TP | 10.16 | 0.29168 | 0.508 |  |  | Special Order | 23
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 7 | TP | TP | 10.5918 | 0.29466 | 0.762 | Industrial Grade | Unshielded, 600V | 181207C6 | 44
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 7 | TP | TP | 9.8552 | 0.30805 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 261
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 7 | TP | TP | 11.8872 | 0.35269 | 1.143 | Industrial Grade | Unshielded, 600V | 181207C6 | 276
Dekoron | 1C99 | PVC | PVC | 12 | 7 | TP | TP | 13.1572 | 0.34674 | 1.143 | Industrial Grade | 600V |  | 143
Dekoron | 1735 | PE | PVC | 12 | 7 | TP | TP | 15.8496 | 0.023513 | 1.524 | Industrial Grade | 600V |  | 654
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 7 | TP | TP | 12.954 | 0.33484 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6073 | 437
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 12 | 7 | TP | TP | 12.954 | 0.35269 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 7707 | 454
Draka | 20-10 Control Cable | PE | PVC | 12 | 7 | TP | TP | 15.494 | 0.38543 | 1.524 | Industrial Grade | Unshielded, 1000V, 75°C | 73070 | 686
General Cable | 20/10 | PE | PVC | 12 | 7 | TP | TP | 14.986 | 0.37948 | 1.143 | Industrial Grade | Unshielded, 600V | 256750 | 155
General Cable | 20/10 CAROLFIRE | PE | PVC | 12 | 7 | TP | TP | 14.986 | 0.37948 | 1.143 | Industrial Grade | Unshielded, 600V | 256750 | 161
General Cable | VNTC® | PVC | PVC | 12 | 7 | TP | TP | 12.446 | 0.32293 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 234620 | 540
General Cable | VNTC® CAROLFIRE | PVC | PVC | 12 | 7 | TP | TP | 12.446 | 0.32293 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 234620 | 548
Okonite | Okozel® | ETFE | ETFE | 12 | 7 | TP | TP | 10.414 | 0.30656 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3457 | 16
Okonite | P-30 | PE | PVC | 12 | 7 | TP | TP | 15.24 | 0.38543 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2307 | 993
Okonite | P-45 | PE | PVC | 12 | 7 | TP | TP | 17.78 | 0.44943 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3307 | 1008
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 7 | TS | TP | 14.859 | 0.3646 | 1.524 | Industrial Grade | Unshielded, 600V | 40931 | 1106
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 7 | TS | TS | 15.24 | 0.42561 | 1.524 | Industrial Grade | Unshielded, 600V | 19889 | 1164
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 7 | TS | TP | 14.859 | 0.35716 | 1.524 | Industrial Grade | Unshielded, 600V | 40819 | 1178
Dekoron | 2X35 | XLPE | PVC | 12 | 7 | TS | TP | 15.8496 | 0.42264 | 1.524 | Industrial Grade | 600V | 2X35-B1260 | 705
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 7 | TS | TS | 12.319 | 0.32144 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 212-07 | 59
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 7 | TS | TP | 15.494 | 0.42115 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 226070 | 387
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 7 | TS | TP | 15.494 | 0.42115 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 206070 | 972
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 7 | TS | TP | 17.145 | 0.47919 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 256070 | 973
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 7 | TS | TP | 15.494 | 0.42115 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 106073 | 1086
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 7 | TS | TP | 17.145 | 0.47919 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 156073 | 1087
First Capital | CAROLFIRE | SR | Aramid Braid | 12 | 7 | Sil | Fiber | 14.478 | 0.35716 | 0 |  |  | SRG-K | 1561
General Cable | CHTC® | XLPE | CSPE | 12 | 7 | TS | TS | 15.113 | 0.39288 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 224080 | 746
General Cable | CVTC® | XLPE | PVC | 12 | 7 | TS | TP | 15.113 | 0.38692 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770950 | 765
General Cable | CVTC® CAROLFIRE | XLPE | PVC | 12 | 7 | TS | TP | 15.113 | 0.38692 | 1.524 | Industrial Grade | Unshileded, 600V, UL Type TC-ER | 770950 | 772
General Cable | EHTC® | EPR | CSPE | 12 | 7 | TS | TS | 15.113 | 0.40032 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343700 | 776
General Cable | FREP® | EPR | CPE | 12 | 7 | TS | TP | 15.24 | 0.40329 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 326660 | 890
General Cable | FREP® | EPR | CPE | 12 | 7 | TS | TP | 15.113 | 0.39883 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279890 | 891
General Cable | FREP® CAROLFIRE | EPR | CPE | 12 | 7 | TS | TP | 15.113 | 0.39883 | 1.524 | Industrial Grade | Unshileded, 600V, UL Type TC-ER | 279890 | 904
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 7 | TS | TS | 14.7066 | 0.41073 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378550 | 1126
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 7 | TS | TS | 18.796 | 0.59675 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 379010 | 1140
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 7 | TS | TP | 19.812 | 0.48217 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3087 | 600
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 7 | Sil | TP | 24.13 | 0.68753 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3557 | 640
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 7 | TS | TS | 21.082 | 0.68307 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6307 | 822
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 7 | TS | TS | 17.78 | 0.53127 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2307 | 839
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 7 | TS | TS | 15.494 | 0.44645 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2307 | 840
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 7 | TS | TS | 18.796 | 0.58931 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6307 | 872
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 7 | TS | TS | 15.494 | 0.46133 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2307 | 908
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 7 | TS | TS | 19.304 | 0.58187 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2307 | 927
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 7 | TS | TS | 12.954 | 0.34228 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C16-0070 | 75
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 7 | TS | TS | 12.192 | 0.31996 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0070 | 89
Rockbestus-Sup | X-Link® TC CAROLFIRE | XLPO | XLPO | 12 | 7 | TS | TS | 12.192 | 0.31996 | 0.889 | Industrial Grade | Unshileded, 600V, UL Type TC, 90°C | C12-0070 | 94
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 7 | Sil | Fiber | 18.542 | 0.49853 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1070 | 109
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 7 | TS | TS | 14.986 | 0.40925 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0070 | 805
Rockbestus-Sup | Firewall® III CAROLFIRE | XLPE | CSPE | 12 | 7 | TS | TS | 14.986 | 0.58485 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0070 | 811
GENERIC | GENERIC | TP | TP | 12 | 8 | TP | TP | 14.986 | 0.40478 | 1.524
GENERIC | GENERIC | TS | TS | 12 | 8 | TS | TP | 23.114 | 0.63396 | 1.27
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 8 | TP | TP | 14.986 | 0.40478 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6083 | 1054
Okonite | P-30 | PE | PVC | 12 | 8 | TP | TP | 16.51 | 0.43454 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2308 | 994
American Insulated Wire | American SDN® | PVC | CP | 12 | 8 | TP | TS | 15.367 | 0.43752 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38519 | 729
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 8 | TS | TS | 25.146 | 0.8795 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7280 | 1525
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 8 | TS | TS | 25.019 | 0.82891 | 3.175 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13397 | 1535
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 12 | 8 | TS | TP | 23.114 | 0.63396 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3458 | 620
GENERIC | GENERIC | TP | TP | 12 | 9 | TP | TP | 16.002 | 0.4524 | 1.524
GENERIC | GENERIC | TS | TS | 12 | 9 | TS | TP | 19.685 | 0.60866 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 12 | 9 | TP | TS | 16.51 | 0.48365 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38811 | 730
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 9 | TP | TP | 15.0622 | 0.4524 | 1.524 | Industrial Grade | Unshielded, 600V | 68134 | 1115
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 9 | TP | TP | 13.3096 | 0.40329 | 1.143 | Industrial Grade | Unshielded, 600V | 181209C6 | 247
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 9 | TP | TP | 11.6586 | 0.39139 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 790
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 9 | TP | TP | 14.605 | 0.48068 | 1.524 | Industrial Grade | Unshielded, 600V | 181209C6 | 798
Dekoron | 1735 | PE | PVC | 12 | 9 | TP | TP | 18.2626 | 0.027233 | 1.524 | Industrial Grade | 600V |  | 655
Dekoron | 1C99 | PVC | PVC | 12 | 9 | TP | TP | 16.2306 | 0.46877 | 1.524 | Industrial Grade | 600V |  | 665
Draka | 20-10 Control Cable | PE | PVC | 12 | 9 | TP | TP | 18.161 | 0.48812 | 1.524 | Industrial Grade | Unshielded, 1000V, 75°C | 73090 | 687
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 9 | TP | TP | 16.002 | 0.4524 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6093 | 1055
General Cable | 20/10 | PE | PVC | 12 | 9 | TP | TP | 17.272 | 0.4777 | 1.143 | Industrial Grade | Unshielded, 600V | 270730 | 156
General Cable | VNTC® | PVC | PVC | 12 | 9 | TP | TP | 15.367 | 0.44198 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 226500 | 1145
Okonite | Okozel® | ETFE | ETFE | 12 | 9 | TP | TP | 12.446 | 0.38246 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3459 | 26
Okonite | P-30 | PE | PVC | 12 | 9 | TP | TP | 17.78 | 0.49258 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2309 | 995
Okonite | P-45 | PE | PVC | 12 | 9 | TP | TP | 20.574 | 0.57741 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3309 | 1009
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 9 | TS | TP | 17.145 | 0.45984 | 1.524 | Industrial Grade | Unshielded, 600V | 40932 | 1107
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 9 | TS | TS | 17.653 | 0.49853 | 1.524 | Industrial Grade | Unshielded, 600V | 19890 | 1165
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 9 | TS | TP | 17.145 | 0.45091 | 1.524 | Industrial Grade | Unshielded, 600V | 40961 | 1179
Dekoron | 2X35 | XLPE | PVC | 12 | 9 | TS | TP | 18.2626 | 0.52532 | 1.524 | Industrial Grade | 600V | 2X35-B1260 | 706
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 9 | TS | TS | 15.367 | 0.43901 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 212-09 | 473
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 9 | TS | TP | 18.161 | 0.53127 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 226090 | 967
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 9 | TS | TP | 18.161 | 0.53127 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 206090 | 974
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 9 | TS | TP | 19.685 | 0.60866 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 256090 | 975
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 9 | TS | TP | 18.161 | 0.53127 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 106093 | 1088
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 9 | TS | TP | 19.685 | 0.60866 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 156093 | 1089
General Cable | CHTC® | XLPE | CSPE | 12 | 9 | TS | TS | 17.653 | 0.51342 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 224070 | 747
General Cable | CVTC® | XLPE | PVC | 12 | 9 | TS | TP | 17.653 | 0.50598 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770580 | 766
General Cable | EHTC® | EPR | CSPE | 12 | 9 | TS | TS | 17.653 | 0.52235 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343710 | 777
General Cable | FREP® | EPR | CPE | 12 | 9 | TS | TP | 17.78 | 0.50598 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367190 | 892
General Cable | FREP® | EPR | CPE | 12 | 9 | TS | TP | 17.653 | 0.50151 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280330 | 893
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 9 | TS | TS | 17.0434 | 0.53574 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378560 | 1127
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 9 | TS | TS | 22.5298 | 0.817 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 379020 | 1461
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 9 | TS | TP | 23.114 | 0.60271 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3089 | 601
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 9 | Sil | TP | 27.432 | 0.80063 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3559 | 641
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 9 | TS | TS | 20.574 | 0.66521 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2309 | 841
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 9 | TS | TS | 18.034 | 0.60568 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2309 | 842
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 9 | TS | TS | 21.082 | 0.72474 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6309 | 873
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 9 | TS | TS | 19.05 | 0.63098 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2309 | 909
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 9 | TS | TS | 24.892 | 0.90927 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6309 | 1276
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 9 | TS | TS | 23.114 | 0.80807 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2309 | 1336
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 9 | Sil | Fiber | 21.844 | 0.63247 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1090 | 110
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 9 | TS | TS | 16.002 | 0.47621 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C16-0090 | 296
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 9 | TS | TS | 14.732 | 0.42413 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0090 | 574
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 9 | TS | TS | 17.272 | 0.5283 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0090 | 806
GENERIC | GENERIC | TP | TP | 12 | 10 | TP | TS | 16.637 | 0.52086 | 1.524
GENERIC | GENERIC | TS | TS | 12 | 10 | TS | TS | 27.178 | 0.95987 | 2.794
American Insulated Wire | American SDN® | PVC | CP | 12 | 10 | TP | TS | 16.637 | 0.52086 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38641 | 731
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 10 | TP | TP | 17.272 | 0.50151 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6103 | 1056
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 10 | TS | TS | 18.415 | 0.5402 | 1.524 | Industrial Grade | Unshielded, 600V | 25202 | 1166
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 10 | TS | TS | 27.178 | 0.95987 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7513 | 1526
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 10 | TS | TS | 27.686 | 0.94796 | 3.556 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13398 | 1550
GENERIC | GENERIC | TP | TP | 12 | 11 | TP | TS | 17.145 | 0.55806 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38812 | 732
GENERIC | GENERIC | TS | TS | 12 | 11 | TS | TP | 25.4 | 0.77236 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3461 | 621
American Insulated Wire | American SDN® | PVC | CP | 12 | 11 | TP | TS | 17.145 | 0.55806 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38812 | 732
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 11 | TP | TP | 17.78 | 0.54467 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6113 | 1057
GENERIC | GENERIC | TP | TP | 12 | 12 | TP | TP | 17.78 | 0.58485 | 1.524
GENERIC | GENERIC | TS | TS | 12 | 12 | TS | TS | 20.066 | 0.76045 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 12 | 12 | TP | TS | 17.145 | 0.58782 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38642 | 733
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 12 | TP | TP | 17.018 | 0.57741 | 1.524 | Industrial Grade | Unshielded, 600V | 68135 | 1116
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 12 | TP | TP | 14.9352 | 0.52383 | 1.143 | Industrial Grade | Unshielded, 600V | 181212C6 | 248
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 12 | TP | TP | 13.208 | 0.51193 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 791
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 12 | TP | TP | 16.3068 | 0.61015 | 1.524 | Industrial Grade | Unshielded, 600V | 181212C6 | 799
Dekoron | 1735 | PE | PVC | 12 | 12 | TP | TP | 20.447 | 0.030359 | 1.524 | Industrial Grade | 600V |  | 656
Dekoron | 1C99 | PVC | PVC | 12 | 12 | TP | TP | 18.1102 | 0.59527 | 1.524 | Industrial Grade | 600V |  | 666
Draka | 20-10 Control Cable | PE | PVC | 12 | 12 | TP | TP | 20.193 | 0.62949 | 1.524 | Industrial Grade | Unshielded, 1000V, 75°C | 73120 | 688
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 12 | TP | TP | 17.78 | 0.58485 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6123 | 1058
General Cable | 20/10 | PE | PVC | 12 | 12 | TP | TP | 19.558 | 0.61312 | 1.143 | Industrial Grade | Unshielded, 600V | 267860 | 157
General Cable | VNTC® | PVC | PVC | 12 | 12 | TP | TP | 17.145 | 0.56104 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 234640 | 1146
Okonite | Okozel® | ETFE | ETFE | 12 | 12 | TP | TP | 14.224 | 0.51639 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3462 | 27
Okonite | P-30 | PE | PVC | 12 | 12 | TP | TP | 19.812 | 0.62503 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2312 | 996
Okonite | P-45 | PE | PVC | 12 | 12 | TP | TP | 24.384 | 0.78426 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-3312 | 1377
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 12 | TS | TP | 18.796 | 0.5908 | 1.524 | Industrial Grade | Unshielded, 600V | 40933 | 1108
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 12 | TS | TS | 19.304 | 0.66372 | 1.524 | Industrial Grade | Unshielded, 600V | 19891 | 1167
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 12 | TS | TP | 18.923 | 0.5789 | 1.524 | Industrial Grade | Unshielded, 600V | 40962 | 1180
Dekoron | 2X35 | XLPE | PVC | 12 | 12 | TS | TP | 20.447 | 0.66819 | 1.524 | Industrial Grade | 600V | 2X35-B1260 | 707
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 12 | TS | TS | 17.272 | 0.57294 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 212-12 | 474
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 12 | TS | TP | 20.193 | 0.68753 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 226120 | 968
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 12 | TS | TP | 20.193 | 0.68753 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 206120 | 976
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 12 | TS | TP | 20.193 | 0.68753 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 106123 | 1090
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 12 | TS | TP | 22.987 | 0.82147 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 156123 | 1091
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 12 | TS | TP | 22.987 | 0.82147 | 2.032 | Industrial Grade | Shielded, 600V, 90°C | 256120 | 1362
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 12 | TS | TS | 27.94 | 1.0536 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N5771 | 1527
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 12 | TS | TS | 28.448 | 1.0655 | 3.556 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13399 | 1551
General Cable | CHTC® | XLPE | CSPE | 12 | 12 | TS | TS | 19.812 | 0.64735 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 224090 | 748
General Cable | CVTC® | XLPE | PVC | 12 | 12 | TS | TP | 19.812 | 0.63842 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770520 | 767
General Cable | EHTC® | EPR | CSPE | 12 | 12 | TS | TS | 19.812 | 0.65926 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343730 | 778
General Cable | FREP® | EPR | CPE | 12 | 12 | TS | TP | 19.558 | 0.6414 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 326640 | 894
General Cable | FREP® | EPR | CPE | 12 | 12 | TS | TP | 19.431 | 0.63693 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280340 | 895
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 12 | TS | TS | 19.1516 | 0.6786 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378570 | 1128
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 12 | TS | TS | 24.9428 | 1.0179 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 379030 | 1462
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 12 | TS | TP | 25.4 | 0.74855 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3092 | 602
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 12 | Sil | TP | 30.988 | 1.0655 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3562 | 642
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 12 | TS | TS | 20.066 | 0.74111 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2312 | 843
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 12 | TS | TS | 20.066 | 0.76045 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2312 | 910
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 12 | TS | TS | 27.686 | 1.1191 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6312 | 1277
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 12 | TS | TS | 24.384 | 0.89885 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2312 | 1290
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 12 | TS | TS | 24.384 | 0.9554 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6312 | 1303
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 12 | TS | TS | 25.654 | 0.94945 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2312 | 1337
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 12 | Sil | Fiber | 24.892 | 0.7664 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1120 | 111
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 12 | TS | TS | 18.034 | 0.59527 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C16-0120 | 297
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 12 | TS | TS | 16.51 | 0.54318 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0120 | 575
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 12 | TS | TS | 19.304 | 0.66223 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-0120 | 807
GENERIC | GENERIC | TP | TP | 12 | 13 | TP | TS | 17.78 | 0.63991 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38813 | 734
GENERIC | GENERIC | TS | TS | 12 | 13 | TS | TS | 20.066 | 0.75003 | 1.524 | Industrial Grade | Unshielded, 600V | 29513 | 1168
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 13 | TP | TP | 18.669 | 0.62949 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6133 | 1059
GENERIC | GENERIC | TP | TP | 12 | 14 | TP | TP | 18.669 | 0.66967 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6143 | 1060
GENERIC | GENERIC | TS | TS | 12 | 14 | TS | TS | 29.337 | 1.1995 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7881 | 1528
American Insulated Wire | American SDN® | PVC | CP | 12 | 14 | TP | TS | 18.288 | 0.67711 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38814 | 735
GENERIC | GENERIC | TP | TP | 12 | 15 | TP | TP | 19.685 | 0.71581 | 1.524
GENERIC | GENERIC | TS | TS | 12 | 15 | TS | TP | 20.828 | 0.71283 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 12 | 15 | TP | TS | 18.542 | 0.71432 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38643 | 736
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 15 | TP | TP | 18.796 | 0.69348 | 1.524 | Industrial Grade | Unshielded, 600V | 68136 | 1117
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 15 | TP | TP | 19.685 | 0.71581 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6153 | 1061
Draka | 20-10 Control Cable | PE | PVC | 12 | 15 | TP | TP | 23.368 | 0.82444 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 73150 | 1208
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 15 | TS | TP | 20.828 | 0.72771 | 1.524 | Industrial Grade | Unshielded, 600V | 40934 | 1109
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 15 | TS | TP | 20.828 | 0.71283 | 1.524 | Industrial Grade | Unshielded, 600V | 40963 | 1181
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 15 | TS | TS | 22.352 | 0.83784 | 2.032 | Industrial Grade | Unshielded, 600V | 19892 | 1478
GENERIC | GENERIC | TP | TP | 12 | 16 | TP | TP | 16.5608 | 0.68009 | 1.143
GENERIC | GENERIC | TS | TS | 12 | 16 | TS | TP | 23.622 | 0.92266 | 2.032
American Insulated Wire | American SDN® | PVC | CP | 12 | 16 | TP | TS | 19.177 | 0.75152 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38815 | 737
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 16 | TP | TP | 16.5608 | 0.68009 | 1.143 | Industrial Grade | Unshielded, 600V | 181216C6 | 249
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 16 | TP | TP | 14.7828 | 0.66967 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 792
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 16 | TP | TP | 18.0086 | 0.77682 | 1.524 | Industrial Grade | Unshielded, 600V | 181216C6 | 800
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 16 | TP | TP | 19.685 | 0.7545 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6163 | 1062
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 16 | TS | TS | 22.987 | 0.94796 | 2.032 | Industrial Grade | Unshielded, 600V | 27602 | 1479
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 16 | TS | TP | 23.622 | 0.92266 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 226160 | 969
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 16 | TS | TP | 23.622 | 0.92266 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 206160 | 1363
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 16 | TS | TP | 23.622 | 0.92266 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 106163 | 1423
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 16 | TS | TS | 30.861 | 1.3379 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7042 | 1529
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 16 | TS | TS | 32.004 | 1.3721 | 3.937 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13401 | 1555
GENERIC | GENERIC | TP | TP | 12 | 17 | TP | TS | 20.32 | 0.78873 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38816 | 738
American Insulated Wire | American SDN® | PVC | CP | 12 | 17 | TP | TS | 20.32 | 0.78873 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38816 | 738
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 17 | TP | TP | 20.701 | 0.80361 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6173 | 1063
GENERIC | GENERIC | TP | TP | 12 | 18 | TP | TS | 20.32 | 0.82593 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38817 | 739
GENERIC | GENERIC | TS | TS | 12 | 18 | TS | TP | 28.702 | 1.0998 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3468 | 622
American Insulated Wire | American SDN® | PVC | CP | 12 | 18 | TP | TS | 20.32 | 0.82593 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38817 | 739
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 18 | TP | TP | 20.701 | 0.8423 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6183 | 1064
GENERIC | GENERIC | TP | TP | 12 | 19 | TP | TP | 20.701 | 0.88099 | 1.524
GENERIC | GENERIC | TS | TS | 12 | 19 | TS | TP | 24.765 | 1.0566 | 2.032
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 19 | TP | TP | 19.812 | 0.86462 | 1.524 | Industrial Grade | Unshielded, 600V | 68137 | 1118
American Insulated Wire | American SDN® | PVC | CP | 12 | 19 | TP | TS | 20.32 | 0.90034 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38818 | 1231
Cable USA | ETFE TYPE TC | ETFE | ETFE | 12 | 19 | TP | TP | 17.4752 | 0.79468 | 1.143 | Industrial Grade | Unshielded, 600V | 181219C6 | 250
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 12 | 19 | TP | TP | 15.6464 | 0.78575 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 793
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 12 | 19 | TP | TP | 18.9484 | 0.89736 | 1.524 | Industrial Grade | Unshielded, 600V | 181219C6 | 801
Dekoron | 1C99 | PVC | PVC | 12 | 19 | TP | TP | 20.9804 | 0.8795 | 1.524 | Industrial Grade | 600V |  | 667
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 19 | TP | TP | 20.701 | 0.88099 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6193 | 1065
Draka | 20-10 Control Cable | PE | PVC | 12 | 19 | TP | TP | 24.638 | 1.0045 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 73190 | 1209
General Cable | 20/10 | PE | PVC | 12 | 19 | TP | TP | 23.876 | 0.97326 | 1.143 | Industrial Grade | Unshielded, 600V | 647650 | 158
General Cable | VNTC® | PVC | PVC | 12 | 19 | TP | TP | 19.939 | 0.84528 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 243600 | 1147
Okonite | Okozel® | ETFE | ETFE | 12 | 19 | TP | TP | 16.51 | 0.7664 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3469 | 28
Okonite | P-30 | PE | PVC | 12 | 19 | TP | TP | 24.384 | 0.99261 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2319 | 1374
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 19 | TS | TP | 24.257 | 0.91969 | 2.032 | Industrial Grade | Unshielded, 600V | 40935 | 1436
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 19 | TS | TS | 24.13 | 1.0938 | 2.032 | Industrial Grade | Unshielded, 600V | 19893 | 1480
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 19 | TS | TP | 23.622 | 0.90183 | 2.032 | Industrial Grade | Unshielded, 600V | 40964 | 1497
Draka | Reduced Diameter Control | XLPE | XLPO | 12 | 19 | TS | TS | 20.574 | 0.87802 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 212-19 | 475
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 19 | TS | TP | 24.765 | 1.0566 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 226190 | 1357
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 19 | TS | TP | 24.765 | 1.0566 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 206190 | 1364
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 19 | TS | TP | 24.765 | 1.0566 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 106193 | 1424
General Cable | CHTC® | XLPE | CSPE | 12 | 19 | TS | TS | 24.257 | 1.0268 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 265940 | 1242
General Cable | CVTC® | XLPE | PVC | 12 | 19 | TS | TP | 23.622 | 1.0134 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770700 | 1249
General Cable | EHTC® | EPR | CSPE | 12 | 19 | TS | TS | 24.257 | 1.0462 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 343750 | 1257
General Cable | FREP® | EPR | CPE | 12 | 19 | TS | TP | 24.003 | 1.0283 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 326670 | 1316
General Cable | FREP® | EPR | CPE | 12 | 19 | TS | TP | 23.876 | 1.0239 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279610 | 1317
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 19 | TS | TS | 23.4442 | 1.0492 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378580 | 1447
General Cable | Ultrol® 300 | XLPE | CSPE | 12 | 19 | TS | TS | 28.702 | 1.4897 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 379040 | 1463
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 19 | TS | TP | 28.702 | 1.073 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3099 | 603
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 19 | Sil | TP | 35.56 | 1.4807 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3569 | 643
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 19 | TS | TS | 31.496 | 1.5462 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6319 | 1278
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 19 | TS | TS | 28.448 | 1.2724 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2319 | 1291
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 19 | TS | TS | 24.638 | 1.134 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2319 | 1292
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 19 | TS | TS | 27.686 | 1.3274 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6319 | 1304
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 19 | TS | TS | 25.908 | 1.1444 | 2.032 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2319 | 1328
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 19 | TS | TS | 29.718 | 1.3527 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2319 | 1338
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 19 | Sil | Fiber | 29.464 | 1.1459 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1190 | 112
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 19 | TS | TS | 19.304 | 0.82593 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0190 | 576
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 19 | TS | TS | 21.844 | 0.92266 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C16-0190 | 1188
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 19 | TS | TS | 23.622 | 1.0268 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-1190 | 1266
GENERIC | GENERIC | TP | TP | 12 | 20 | TP | TP | 23.114 | 0.97475 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6203 | 1394
GENERIC | GENERIC | TS | TS | 12 | 20 | TS | TP | 26.162 | 1.1087 | 2.032
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 20 | TS | TP | 26.162 | 1.1087 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 226200 | 1358
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 20 | TS | TP | 26.162 | 1.1087 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 206200 | 1365
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 20 | TS | TP | 26.162 | 1.1087 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 106203 | 1425
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 20 | TS | TS | 34.798 | 1.7025 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N5692 | 1542
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 20 | TS | TS | 35.687 | 1.7292 | 4.318 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13402 | 1559
GENERIC | GENERIC | TP | TP | 12 | 21 | TP | TS | 22.352 | 1.012 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38819 | 1232
American Insulated Wire | American SDN® | PVC | CP | 12 | 21 | TP | TS | 22.352 | 1.012 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38819 | 1232
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 21 | TP | TP | 23.114 | 1.012 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6213 | 1395
GENERIC | GENERIC | TP | TP | 12 | 22 | TP | TP | 24.13 | 1.067 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6223 | 1396
GENERIC | GENERIC | TS | TS | 12 | 22 | TS | TS | 26.162 | 1.2367 | 2.032 | Industrial Grade | Unshielded, 600V | 29514 | 1481
GENERIC | GENERIC | TP | TP | 12 | 23 | TP | TP | 24.13 | 1.1176 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6233 | 1397
GENERIC | GENERIC | TS | TS | 12 | 23 | TS | TS | 26.543 | 1.2813 | 2.032 | Industrial Grade | Unshielded, 600V | 31244 | 1482
GENERIC | GENERIC | TP | TP | 12 | 24 | TP | TS | 24.257 | 1.1504 | 2.032
GENERIC | GENERIC | TS | TS | 12 | 24 | TS | TS | 37.973 | 2.0507 | 3.175
American Insulated Wire | American SDN® | PVC | CP | 12 | 24 | TP | TS | 24.257 | 1.1504 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38644 | 1233
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 24 | TP | TP | 25.273 | 1.1578 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6243 | 1398
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 24 | TS | TS | 27.051 | 1.326 | 2.032 | Industrial Grade | Unshielded, 600V | 31245 | 1483
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 24 | TS | TS | 37.973 | 2.0507 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N5772 | 1543
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 12 | 24 | TS | TS | 39.116 | 2.0968 | 4.318 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13403 | 1560
GENERIC | GENERIC | TP | TP | 12 | 25 | TP | TP | 25.781 | 1.2009 | 2.032
GENERIC | GENERIC | TS | TS | 12 | 25 | TS | TS | 28.321 | 1.3021 | 2.032
American Insulated Wire | American SDN® | PVC | CP | 12 | 25 | TP | TS | 24.638 | 1.1637 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38820 | 1234
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 25 | TP | TP | 24.13 | 1.1846 | 2.032 | Industrial Grade | Unshielded, 600V | 68138 | 1441
Draka | 20-10 Control Cable | PE | PVC | 12 | 25 | TP | TP | 29.21 | 1.2873 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 73250 | 1210
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 25 | TP | TP | 25.781 | 1.2009 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6253 | 1399
General Cable | VNTC® | PVC | PVC | 12 | 25 | TP | TP | 23.876 | 1.1533 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 243610 | 1466
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 12 | 25 | TS | TP | 26.67 | 1.1876 | 2.032 | Industrial Grade | Unshielded, 600V | 40936 | 1437
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 25 | TS | TS | 27.432 | 1.3706 | 2.032 | Industrial Grade | Unshielded, 600V | 36259 | 1484
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 25 | TS | TP | 26.67 | 1.1637 | 2.032 | Industrial Grade | Unshielded, 600V | 40965 | 1498
General Cable | CVTC® | XLPE | PVC | 12 | 25 | TS | TP | 27.813 | 1.317 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 347110 | 1250
General Cable | EHTC® | EPR | CSPE | 12 | 25 | TS | TS | 28.321 | 1.3021 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 343760 | 1258
General Cable | FREP® | EPR | CPE | 12 | 25 | TS | TP | 27.94 | 1.2754 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367200 | 1318
General Cable | FREP® | EPR | CPE | 12 | 25 | TS | TP | 49.53 | 1.2709 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 295400 | 1319
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 25 | TS | TS | 27.1018 | 1.3021 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378590 | 1448
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 25 | Sil | Fiber | 34.544 | 1.637 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1250 | 113
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 25 | TS | TS | 25.146 | 1.1905 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C16-0250 | 1189
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 25 | TS | TS | 24.638 | 1.1533 | 1.651 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0250 | 1196
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 25 | TS | TS | 27.178 | 1.3319 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-3637 | 1267
GENERIC | GENERIC | TS | TS | 12 | 26 | TS | TP | 29.464 | 1.4138 | 2.032
GENERIC | GENERIC | TP | TP | 12 | 26 | TP | TP | 25.781 | 1.2426 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6263 | 1400
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 26 | TS | TP | 29.464 | 1.4138 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 226260 | 1359
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 26 | TS | TP | 29.464 | 1.4138 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 206260 | 1366
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 26 | TS | TP | 29.464 | 1.4138 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 106263 | 1426
GENERIC | GENERIC | TP | TP | 12 | 27 | TP | TP | 25.781 | 1.2813 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6273 | 1401
GENERIC | GENERIC | TP | TP | 12 | 28 | TP | TP | 26.67 | 1.326 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6283 | 1402
GENERIC | GENERIC | TP | TP | 12 | 29 | TP | TP | 26.67 | 1.3661 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6293 | 1403
GENERIC | GENERIC | TP | TP | 12 | 30 | TP | TP | 26.67 | 1.4063 | 2.032
GENERIC | GENERIC | TS | TS | 12 | 30 | TS | TP | 29.337 | 1.4956 | 2.032
American Insulated Wire | American SDN® | PVC | CP | 12 | 30 | TP | TS | 25.654 | 1.5358 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38645 | 1235
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 30 | TP | TP | 25.4762 | 1.3959 | 2.032 | Industrial Grade | Unshielded, 600V | 68139 | 1442
Draka | 20-10 Control Cable | PE | PVC | 12 | 30 | TP | TP | 30.353 | 1.5179 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 73300 | 1211
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 30 | TP | TP | 26.67 | 1.4063 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6303 | 1404
General Cable | VNTC® | PVC | PVC | 12 | 30 | TP | TP | 26.162 | 1.3676 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 321720 | 1467
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 30 | TS | TS | 29.718 | 1.6072 | 2.032 | Industrial Grade | Unshielded, 600V | 31246 | 1485
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 30 | TS | TP | 30.48 | 1.5849 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 226300 | 1360
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 30 | TS | TP | 30.48 | 1.5849 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 206300 | 1367
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 30 | TS | TP | 30.48 | 1.5849 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 106303 | 1427
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 12 | 30 | TS | TS | 42.926 | 2.6727 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7281 | 1544
General Cable | CVTC® | XLPE | PVC | 12 | 30 | TS | TP | 29.21 | 1.4956 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 347120 | 1251
General Cable | EHTC® | EPR | CSPE | 12 | 30 | TS | TS | 29.21 | 1.5135 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 343770 | 1259
General Cable | FREP® | EPR | CPE | 12 | 30 | TS | TP | 29.337 | 1.4956 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367210 | 1320
General Cable | FREP® | EPR | CPE | 12 | 30 | TS | TP | 29.21 | 1.4911 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 347100 | 1321
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 30 | TS | TS | 28.9052 | 1.5105 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378600 | 1449
GENERIC | GENERIC | TP | TP | 12 | 31 | TP | TP | 27.686 | 1.4569 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6313 | 1405
GENERIC | GENERIC | TP | TP | 12 | 32 | TP | TP | 27.686 | 1.4941 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6323 | 1406
GENERIC | GENERIC | TP | TP | 12 | 33 | TP | TP | 27.686 | 1.5358 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6333 | 1407
GENERIC | GENERIC | TP | TP | 12 | 34 | TP | TP | 28.829 | 1.5834 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6343 | 1408
GENERIC | GENERIC | TP | TP | 12 | 35 | TP | TP | 28.829 | 1.6251 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6353 | 1409
GENERIC | GENERIC | TP | TP | 12 | 36 | TP | TP | 28.829 | 1.6638 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6363 | 1410
GENERIC | GENERIC | TS | TS | 12 | 36 | TS | TS | 49.276 | 3.5329 | 3.9624 | Industrial Grade | Unshielded, 600V, 90°C | N7282 | 1556
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 12 | 36 | TS | TP | 37.592 | 1.9376 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3486 | 623
GENERIC | GENERIC | TP | TP | 12 | 37 | TP | TP | 28.067 | 1.637 | 2.032
GENERIC | GENERIC | TS | TS | 12 | 37 | TS | TP | 33.02 | 1.9123 | 2.032
American Insulated Wire | American SDN® | PVC | CP | 12 | 37 | TP | TS | 29.083 | 1.6667 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38821 | 1236
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 12 | 37 | TP | TP | 27.432 | 1.6876 | 2.032 | Industrial Grade | Unshielded, 600V | 68140 | 1443
Draka | 20-10 Control Cable | PE | PVC | 12 | 37 | TP | TP | 32.766 | 1.8364 | 2.032 | Industrial Grade | Unshielded, 1000V, 75°C | 73370 | 1212
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 12 | 37 | TP | TP | 28.829 | 1.7054 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 6373 | 1411
General Cable | VNTC® | PVC | PVC | 12 | 37 | TP | TP | 28.067 | 1.637 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 234680 | 1468
Okonite | Okozel® | ETFE | ETFE | 12 | 37 | TP | TP | 23.368 | 1.509 | 0.635 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3487 | 37
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 12 | 37 | TS | TS | 32.131 | 1.9822 | 2.032 | Industrial Grade | Unshielded, 600V | 27241 | 1486
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 12 | 37 | TS | TP | 31.369 | 1.6638 | 2.032 | Industrial Grade | Unshielded, 600V | 40966 | 1499
Draka | General Purpose Control XLPE | XLPE | CPE | 12 | 37 | TS | TP | 33.02 | 1.9123 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 226370 | 1361
Draka | General Purpose Control XLPE | XLPE | PVC | 12 | 37 | TS | TP | 33.02 | 1.9123 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 206370 | 1368
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 12 | 37 | TS | TP | 33.02 | 1.9123 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 106373 | 1428
General Cable | CHTC® | XLPE | CSPE | 12 | 37 | TS | TS | 32.131 | 2.073 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 347050 | 1243
General Cable | CVTC® | XLPE | PVC | 12 | 37 | TS | TP | 31.496 | 1.7635 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 347130 | 1252
General Cable | EHTC® | EPR | CSPE | 12 | 37 | TS | TS | 31.496 | 2.1147 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 343480 | 1260
General Cable | FREP® | EPR | CPE | 12 | 37 | TS | TP | 31.623 | 1.8498 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367220 | 1322
General Cable | FREP® | EPR | CPE | 12 | 37 | TS | TP | 31.496 | 1.8453 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 301870 | 1323
General Cable | Ultrol® 275 | XLPE | CSPE | 12 | 37 | TS | TS | 31.1658 | 1.82 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378610 | 1450
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 12 | 37 | TS | TP | 37.592 | 1.9361 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3117 | 604
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 12 | 37 | Sil | TP | 48.514 | 2.7784 | 1.524 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3587 | 989
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 12 | 37 | TS | TS | 41.91 | 2.7338 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6337 | 1279
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 37 | TS | TS | 38.1 | 2.2888 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2337 | 1293
Okonite | FMR® Okolon® | EPR | CSPE | 12 | 37 | TS | TS | 32.766 | 2.0313 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2337 | 1294
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 12 | 37 | TS | TS | 36.322 | 2.332 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6337 | 1305
Okonite | FRM-N® Okolon® | EPR | CSPE | 12 | 37 | TS | TS | 33.782 | 2.0284 | 2.032 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2337 | 1329
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 12 | 37 | TS | TS | 39.116 | 2.3885 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2337 | 1339
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 12 | 37 | Sil | Fiber | 40.132 | 2.1578 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-1370 | 114
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 12 | 37 | TS | TS | 28.956 | 1.7114 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C16-0370 | 1190
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 12 | 37 | TS | TS | 27.432 | 1.637 | 1.651 | Industrial Grade | Unshielded, 600V, UL Type TC | C12-0370 | 1197
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 12 | 37 | TS | TS | 31.496 | 1.8974 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C52-3406 | 1268
GENERIC | GENERIC | TS | TS | 12 | 3+G | TS | TP | 10.414 | 0.22025 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280170 | 334
GENERIC | GENERIC | TS |  | 14 | 1 | TS | None | 3.556 | 0.028275 | 0.762 | Industrial Grade | Single Conductor, 600V, 90°C |  | 60
GENERIC | GENERIC | TP | TP | 14 | 2 | TP | TP | 8.128 | 0.095242 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 2 | TS | TP | 11.303 | 0.16221 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 14 | 2 | TP | TS | 8.128 | 0.11608 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38799 | 177
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 2 | TP | TP | 5.9944 | 0.07292 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 251
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 2 | TP | TP | 8.128 | 0.11161 | 1.143 | Industrial Grade | Unshielded, 600V | 181402C6 | 266
Dekoron | 1C99 | PVC | PVC | 14 | 2 | TP | TP | 8.636 | 0.1384 | 1.143 | Industrial Grade | 600V | 1C99-4020L | 135
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 14 | 2 | TP | TP | 8.382 | 0.11161 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 5702 | 445
General Cable | 20/10 | PE | PVC | 14 | 2 | TP | TP | 9.398 | 0.098219 | 1.143 | Industrial Grade | Unshielded, 600V | 647560 | 146
General Cable | VNTC® | PVC | PVC | 14 | 2 | TP | TP | 8.128 | 0.095242 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 245590 | 521
General Cable | VNTC® | PVC | PVC | 14 | 2 | TP | TP | 8.382 | 0.099707 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243660 | 522
Okonite | Okozel® | ETFE | ETFE | 14 | 2 | TP | TP | 6.35 | 0.078873 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3352 | 6
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 2 | TS | TS | 9.525 | 0.13245 | 1.143 | Industrial Grade | Unshielded, 600V | 19872 | 553
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 14 | 2 | TS | TS | 9.652 | 0.14435 | 1.143 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 30561 | 567
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 2 | TS | TS | 7.874 | 0.083337 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 214-02 | 49
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 2 | TS | TS | 9.779 | 0.11459 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 814-02 | 206
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 2 | TS | TP | 11.303 | 0.16221 | 1.143 | Industrial Grade | Shielded, 600V, 90°C | 254020 | 377
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 2 | TS | TP | 11.303 | 0.16221 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 154023 | 457
General Cable | CHTC® | XLPE | CSPE | 14 | 2 | TS | TS | 9.398 | 0.11161 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 272270 | 189
General Cable | CVTC® | XLPE | PVC | 14 | 2 | TS | TP | 9.271 | 0.10864 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 771080 | 215
General Cable | EHTC® | EPR | CSPE | 14 | 2 | TS | TS | 9.398 | 0.1012 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 343590 | 229
General Cable | FREP® | EPR | CPE | 14 | 2 | TS | TP | 9.525 | 0.11012 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 280980 | 322
General Cable | FREP® | EPR | CPE | 14 | 2 | TS | TP | 9.398 | 0.10566 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 305320 | 323
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 2 | TS | TS | 0.91186 | 0.12203 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378370 | 499
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 2 | TS | TS | 10.0838 | 0.18156 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378860 | 515
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 2 | TS | TS | 11.43 | 0.14733 | 1.143 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2152 | 301
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 2 | TS | TS | 8.382 | 0.14435 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2152 | 302
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 2 | TS | TS | 9.906 | 0.15626 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2152 | 346
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 2 | TS | TS | 12.7 | 0.189 | 1.143 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2152 | 356
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 2 | TS | TP | 15.24 | 0.21132 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3002 | 589
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 14 | 2 | TS | TP | 15.24 | 0.24257 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3402 | 612
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 2 | Sil | TP | 17.526 | 0.29614 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3452 | 628
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 2 | TS | TS | 17.018 | 0.37353 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6152 | 812
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 2 | TS | TS | 17.018 | 0.3899 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6152 | 861
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 2 | TS | TS | 8.382 | 0.096731 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C15-0020 | 66
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 2 | TS | TS | 7.874 | 0.081849 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0020 | 79
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 2 | Sil | Fiber | 11.684 | 0.13393 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0020 | 95
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 2 | TS | TS | 9.398 | 0.12649 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0020 | 281
GENERIC | GENERIC | TP | TP | 14 | 3 | TP | TP | 8.89 | 0.11756 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 3 | TS | TS | 10.922 | 0.1756 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 14 | 3 | TP | TS | 8.636 | 0.12501 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38509 | 178
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 3 | TP | TP | 8.4836 | 0.12947 | 1.143 | Industrial Grade | Unshielded, 600V | 68116 | 487
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 3 | TP | TP | 7.1628 | 0.098219 | 0.381 | Industrial Grade | Unshielded, 600V | 181403C6 | 1
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 3 | TP | TP | 6.3754 | 0.10417 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 252
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 3 | TP | TP | 8.5852 | 0.14733 | 1.143 | Industrial Grade | Unshielded, 600V | 181403C6 | 267
Dekoron | 1735 | PE | PVC | 14 | 3 | TP | TP | 10.4394 | 0.14733 | 1.143 | Industrial Grade | 600V |  | 125
Dekoron | 1C99 | PVC | PVC | 14 | 3 | TP | TP | 9.144 | 0.13691 | 1.143 | Industrial Grade | 600V | 1C99-4030L | 136
Draka | 20-10 Control Cable | PE | PVC | 14 | 3 | TP | TP | 10.16 | 0.14138 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 72030 | 162
Draka | Power & Control 3 THHN/THWN | PVC | PVC | 14 | 3 | TP | TP | 9.652 | 0.15328 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 4047 | 408
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 3 | TP | TP | 8.89 | 0.11756 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4033 | 426
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 14 | 3 | TP | TP | 8.89 | 0.13989 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 5703 | 446
General Cable | 20/10 | PE | PVC | 14 | 3 | TP | TP | 9.906 | 0.12947 | 1.143 | Industrial Grade | Unshielded, 600V | 365410 | 147
General Cable | VNTC® | PVC | PVC | 14 | 3 | TP | TP | 8.763 | 0.11905 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235050 | 523
General Cable | VNTC® | PVC | PVC | 14 | 3 | TP | TP | 8.89 | 0.12501 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243720 | 524
General Cable | VNTC® | PVC | PVC | 14 | 3 | TP | TP | 9.271 | 0.077385 | 1.143 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 383890 | 525
Okonite | Okozel® | ETFE | ETFE | 14 | 3 | TP | TP | 6.858 | 0.1012 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3353 | 7
Okonite | P-30 | PE | PVC | 14 | 3 | TP | TP | 10.16 | 0.13245 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2153 | 397
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 3 | TS | TP | 9.7282 | 0.12054 | 1.143 | Industrial Grade | Unshielded, 600V | 40917 | 478
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 3 | TS | TS | 10.287 | 0.16221 | 1.143 | Industrial Grade | Unshielded, 600V | 19873 | 554
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 14 | 3 | TS | TS | 10.414 | 0.17412 | 1.143 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 24713 | 568
Dekoron | 2X35 | XLPE | PVC | 14 | 3 | TS | TP | 10.4394 | 0.15626 | 1.143 | Industrial Grade | 600V | 2X35-40360 | 171
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 3 | TS | TS | 8.382 | 0.11012 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 214-03 | 50
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 3 | TS | TP | 10.16 | 0.15179 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 224030 | 373
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 3 | TS | TP | 10.16 | 0.15179 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 204030 | 378
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 3 | TS | TP | 11.938 | 0.19644 | 1.143 | Industrial Grade | Shielded, 600V, 90°C | 254030 | 379
Draka | Power & Control Type TC 3 XHHW-2 1 bare | XLPE | PVC | 14 | 3 | TS | TP | 9.652 | 0.15328 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 4047 | 421
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 14 | 3 | TS | TP | 11.938 | 0.22025 | 1.143 | Industrial Grade | Shielded (Copper), 600V, 90°C | 154047 | 424
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 3 | TS | TP | 10.16 | 0.15179 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 104033 | 458
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 3 | TS | TP | 11.938 | 0.19644 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 154033 | 459
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 3 | TS | TS | 14.351 | 0.2515 | 2.032 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13407 | 1226
General Cable | CHTC® | XLPE | CSPE | 14 | 3 | TS | TS | 9.906 | 0.14138 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 223790 | 190
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 14 | 3 | TS | TS | 10.795 | 0.078873 | 1.143 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 383790 | 200
General Cable | CVTC® | XLPE | PVC | 14 | 3 | TS | TP | 9.906 | 0.1384 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770530 | 216
General Cable | CVTC® | XLPE | PVC | 14 | 3 | TS | TP | 10.795 | 0.17263 | 1.143 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 383860 | 217
General Cable | EHTC® | EPR | CSPE | 14 | 3 | TS | TS | 10.922 | 0.1756 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 383830 | 230
General Cable | EHTC® | EPR | CSPE | 14 | 3 | TS | TS | 10.795 | 0.078873 | 1.143 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 383800 | 231
General Cable | EHTC® | EPR | CSPE | 14 | 3 | TS | TS | 9.906 | 0.1131 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 262140 | 232
General Cable | FREP® | EPR | CPE | 14 | 3 | TS | TP | 10.033 | 0.14138 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 354800 | 324
General Cable | FREP® | EPR | CPE | 14 | 3 | TS | TP | 9.906 | 0.13691 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280180 | 325
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 3 | TS | TS | 9.6266 | 0.1384 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378380 | 500
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 3 | TS | TS | 10.668 | 0.20685 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378870 | 516
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 3 | TS | TS | 11.938 | 0.17858 | 1.143 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2153 | 303
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 3 | TS | TS | 10.414 | 0.16965 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2153 | 304
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 3 | TS | TS | 10.414 | 0.18602 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2153 | 347
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 3 | TS | TS | 13.208 | 0.23067 | 1.143 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2153 | 357
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 3 | TS | TP | 15.24 | 0.22769 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3003 | 587
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 3 | Sil | TP | 18.542 | 0.34228 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3553 | 629
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 3 | TS | TS | 17.018 | 0.39288 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6153 | 813
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 3 | TS | TS | 17.018 | 0.40925 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6153 | 862
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 3 | TS | TS | 8.89 | 0.12649 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C15-0030 | 67
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 3 | TS | TS | 8.382 | 0.11161 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0030 | 80
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 3 | Sil | Fiber | 12.446 | 0.1637 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0030 | 96
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 3 | TS | TS | 9.906 | 0.1637 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0030 | 282
GENERIC | GENERIC | TP | TP | 14 | 4 | TP | TS | 9.398 | 0.15477 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 4 | TS | TS | 11.43 | 0.21578 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 14 | 4 | TP | TS | 9.398 | 0.15477 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38510 | 179
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 4 | TP | TP | 9.2202 | 0.15923 | 1.143 | Industrial Grade | Unshielded, 600V | 68117 | 488
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 4 | TP | TP | 7.8232 | 0.12501 | 0.381 | Industrial Grade | Unshielded, 600V | 181404C6 | 2
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 4 | TP | TP | 6.985 | 0.13245 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 253
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 4 | TP | TP | 9.2964 | 0.18007 | 1.143 | Industrial Grade | Unshielded, 600V | 181404C6 | 268
Draka | 20-10 Control Cable | PE | PVC | 14 | 4 | TP | TP | 11.049 | 0.17412 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 72040 | 163
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 4 | TP | TP | 9.652 | 0.14733 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4043 | 427
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 14 | 4 | TP | TP | 9.652 | 0.17114 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 5704 | 447
General Cable | 20/10 | PE | PVC | 14 | 4 | TP | TP | 10.668 | 0.16072 | 1.143 | Industrial Grade | Unshielded, 600V | 267950 | 148
General Cable | VNTC® | PVC | PVC | 14 | 4 | TP | TP | 9.271 | 0.14882 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235060 | 526
General Cable | VNTC® | PVC | PVC | 14 | 4 | TP | TP | 9.652 | 0.15477 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243650 | 527
Okonite | Okozel® | ETFE | ETFE | 14 | 4 | TP | TP | 7.366 | 0.12947 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3354 | 8
Okonite | P-30 | PE | PVC | 14 | 4 | TP | TP | 11.176 | 0.16519 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2154 | 398
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 4 | TS | TP | 10.5664 | 0.15179 | 1.143 | Industrial Grade | Unshielded, 600V | 40918 | 479
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 4 | TS | TS | 11.303 | 0.18304 | 1.143 | Industrial Grade | Unshielded, 600V | 19874 | 555
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 4 | TS | TP | 10.668 | 0.14882 | 1.143 | Industrial Grade | Unshielded, 600V | 40951 | 580
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 4 | TS | TS | 9.144 | 0.13989 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 214-04 | 51
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 4 | TS | TS | 11.303 | 0.18304 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 814-04 | 207
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 4 | TS | TP | 11.049 | 0.18751 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 224040 | 374
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 4 | TS | TP | 11.049 | 0.18751 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 204040 | 380
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 4 | TS | TP | 12.827 | 0.23067 | 1.143 | Industrial Grade | Shielded, 600V, 90°C | 254040 | 381
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 4 | TS | TP | 11.049 | 0.18751 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 104043 | 460
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 4 | TS | TP | 12.827 | 0.23067 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 154043 | 461
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 4 | TS | TS | 15.494 | 0.31251 | 2.032 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13408 | 1227
General Cable | CHTC® | XLPE | CSPE | 14 | 4 | TS | TS | 10.795 | 0.1756 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 223780 | 191
General Cable | CVTC® | XLPE | PVC | 14 | 4 | TS | TP | 10.795 | 0.17263 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770610 | 218
General Cable | EHTC® | EPR | CSPE | 14 | 4 | TS | TS | 10.795 | 0.14435 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 248240 | 233
General Cable | FREP® | EPR | CPE | 14 | 4 | TS | TP | 10.922 | 0.1756 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 305330 | 326
General Cable | FREP® | EPR | CPE | 14 | 4 | TS | TP | 10.795 | 0.17114 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280190 | 327
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 4 | TS | TS | 3.556 | 0.17263 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378390 | 501
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 4 | TS | TS | 11.684 | 0.27977 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378880 | 517
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 4 | TS | TS | 13.208 | 0.26341 | 1.143 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2154 | 305
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 4 | TS | TS | 11.176 | 0.20983 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2154 | 306
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 4 | TS | TS | 11.43 | 0.21578 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2154 | 348
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 4 | TS | TP | 16.256 | 0.26936 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3004 | 590
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 4 | Sil | TP | 19.812 | 0.40329 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3454 | 630
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 4 | TS | TS | 17.272 | 0.40627 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6154 | 814
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 4 | TS | TS | 17.018 | 0.42115 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6154 | 863
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 4 | TS | TS | 15.24 | 0.31251 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2154 | 920
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 4 | TS | TS | 9.906 | 0.15626 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C15-0040 | 68
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 4 | TS | TS | 9.144 | 0.14138 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0040 | 81
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 4 | Sil | Fiber | 13.716 | 0.22322 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0040 | 97
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 4 | TS | TS | 10.668 | 0.19346 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0040 | 283
GENERIC | GENERIC | TP | TP | 14 | 5 | TP | TP | 10.414 | 0.1756 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 5 | TS | TS | 12.446 | 0.26489 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 14 | 5 | TP | TS | 10.16 | 0.189 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38511 | 180
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 5 | TP | TP | 10.033 | 0.19197 | 1.143 | Industrial Grade | Unshielded, 600V | 68118 | 489
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 5 | TP | TP | 8.5852 | 0.15328 | 0.381 | Industrial Grade | Unshielded, 600V | 181405C6 | 3
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 5 | TP | TP | 7.6962 | 0.15923 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 254
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 5 | TP | TP | 10.1092 | 0.21281 | 1.143 | Industrial Grade | Unshielded, 600V | 181405C6 | 269
Dekoron | 1735 | PE | PVC | 14 | 5 | TP | TP | 12.065 | 0.20983 | 1.143 | Industrial Grade | 600V |  | 126
Dekoron | 1C99 | PVC | PVC | 14 | 5 | TP | TP | 10.8204 | 0.19644 | 1.143 | Industrial Grade | 600V | 1C99-4050L | 137
Draka | 20-10 Control Cable | PE | PVC | 14 | 5 | TP | TP | 12.065 | 0.19644 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 72050 | 164
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 5 | TP | TP | 10.541 | 0.17709 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4053 | 428
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 14 | 5 | TP | TP | 10.541 | 0.19346 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 5705 | 448
General Cable | 20/10 | PE | PVC | 14 | 5 | TP | TP | 11.684 | 0.19346 | 1.143 | Industrial Grade | Unshielded, 600V | 286130 | 149
General Cable | VNTC® | PVC | PVC | 14 | 5 | TP | TP | 10.16 | 0.18304 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243570 | 528
General Cable | VNTC® | PVC | PVC | 14 | 5 | TP | TP | 10.414 | 0.1756 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235070 | 529
Okonite | Okozel® | ETFE | ETFE | 14 | 5 | TP | TP | 8.128 | 0.15775 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3355 | 9
Okonite | P-30 | PE | PVC | 14 | 5 | TP | TP | 12.192 | 0.20239 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2155 | 399
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 5 | TS | TP | 11.557 | 0.18453 | 1.143 | Industrial Grade | Unshielded, 600V | 40919 | 480
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 5 | TS | TS | 11.938 | 0.23513 | 1.143 | Industrial Grade | Unshielded, 600V | 19875 | 556
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 5 | TS | TP | 11.684 | 0.18156 | 1.143 | Industrial Grade | Unshielded, 600V | 40952 | 581
Dekoron | 2X35 | XLPE | PVC | 14 | 5 | TS | TP | 12.319 | 0.22471 | 1.143 | Industrial Grade | 600V | 2X35-40560 | 172
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 5 | TS | TS | 10.033 | 0.16965 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 214-05 | 52
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 5 | TS | TP | 12.065 | 0.22322 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 224050 | 375
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 5 | TS | TP | 12.065 | 0.22322 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 204050 | 382
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 5 | TS | TP | 12.065 | 0.22322 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 104053 | 462
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 5 | TS | TP | 14.732 | 0.30805 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 254050 | 959
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 5 | TS | TP | 14.732 | 0.30805 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 154053 | 1076
General Cable | CHTC® | XLPE | CSPE | 14 | 5 | TS | TS | 11.811 | 0.21281 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 223770 | 192
General Cable | CVTC® | XLPE | PVC | 14 | 5 | TS | TP | 11.811 | 0.20834 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770420 | 219
General Cable | EHTC® | EPR | CSPE | 14 | 5 | TS | TS | 11.811 | 0.17858 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 262150 | 234
General Cable | FREP® | EPR | CPE | 14 | 5 | TS | TP | 11.938 | 0.21132 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 354810 | 328
General Cable | FREP® | EPR | CPE | 14 | 5 | TS | TP | 11.811 | 0.20685 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279870 | 329
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 5 | TS | TS | 11.4808 | 0.2009 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378400 | 502
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 5 | TS | TS | 15.4178 | 0.32888 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378890 | 1135
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 5 | TS | TS | 12.192 | 0.25448 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2155 | 307
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 5 | TS | TS | 12.446 | 0.26489 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2155 | 349
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 5 | TS | TP | 17.526 | 0.31251 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3005 | 591
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 5 | Sil | TP | 21.844 | 0.47175 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3455 | 631
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 5 | TS | TS | 18.288 | 0.4658 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6155 | 815
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 5 | TS | TS | 15.24 | 0.31103 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2155 | 831
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 5 | TS | TS | 17.018 | 0.43008 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6155 | 864
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 5 | TS | TS | 16.51 | 0.38692 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2155 | 921
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 5 | TS | TS | 10.668 | 0.18602 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C15-0050 | 69
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 5 | TS | TS | 9.906 | 0.17114 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0050 | 82
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 5 | Sil | Fiber | 14.986 | 0.26787 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0050 | 98
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 5 | TS | TS | 11.684 | 0.23811 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0050 | 284
GENERIC | GENERIC | TP | TP | 14 | 6 | TP | TS | 11.049 | 0.21876 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 6 | TS | TP | 18.542 | 0.39734 | 1.27
American Insulated Wire | American SDN® | PVC | CP | 14 | 6 | TP | TS | 11.049 | 0.21876 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38512 | 181
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 6 | TP | TP | 11.43 | 0.20834 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4063 | 429
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 6 | TS | TS | 12.954 | 0.26192 | 1.143 | Industrial Grade | Unshielded, 600V | 26153 | 557
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 6 | TS | TS | 13.335 | 0.25596 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 814-06 | 208
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 6 | TS | TS | 19.685 | 0.48812 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N7511 | 1512
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 6 | TS | TS | 19.685 | 0.47621 | 2.794 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13409 | 1517
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 14 | 6 | TS | TP | 18.542 | 0.39734 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3406 | 613
GENERIC | GENERIC | TP | TP | 14 | 7 | TP | TP | 11.43 | 0.24852 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 7 | TS | TS | 13.462 | 0.30656 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 14 | 7 | TP | TS | 11.938 | 0.24555 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38800 | 182
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 7 | TP | TP | 10.8966 | 0.24108 | 1.143 | Industrial Grade | Unshielded, 600V | 68119 | 490
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 7 | TP | TP | 9.3726 | 0.20388 | 0.381 | Industrial Grade | Unshielded, 600V | 181407C6 | 4
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 7 | TP | TP | 8.4074 | 0.21281 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 255
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 7 | TP | TP | 10.9728 | 0.27382 | 1.143 | Industrial Grade | Unshielded, 600V | 181407C6 | 270
Dekoron | 1735 | PE | PVC | 14 | 7 | TP | TP | 13.3858 | 0.26787 | 1.143 | Industrial Grade | 600V |  | 127
Dekoron | 1C99 | PVC | PVC | 14 | 7 | TP | TP | 11.7094 | 0.2515 | 1.143 | Industrial Grade | 600V | 1C99-4070L | 138
Draka | 20-10 Control Cable | PE | PVC | 14 | 7 | TP | TP | 13.081 | 0.25894 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 72070 | 165
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 7 | TP | TP | 11.43 | 0.21876 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4073 | 430
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 14 | 7 | TP | TP | 11.43 | 0.24852 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 5707 | 449
General Cable | 20/10 | PE | PVC | 14 | 7 | TP | TP | 12.7 | 0.25745 | 1.143 | Industrial Grade | Unshielded, 600V | 365240 | 150
General Cable | VNTC® | PVC | PVC | 14 | 7 | TP | TP | 11.176 | 0.23959 | 1.143 | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243580 | 530
General Cable | VNTC® | PVC | PVC | 14 | 7 | TP | TP | 11.303 | 0.22769 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235080 | 531
Okonite | Okozel® | ETFE | ETFE | 14 | 7 | TP | TP | 8.89 | 0.20834 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3357 | 10
Okonite | P-30 | PE | PVC | 14 | 7 | TP | TP | 13.208 | 0.26043 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2157 | 400
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 7 | TS | TP | 12.7 | 0.24108 | 1.143 | Industrial Grade | Unshielded, 600V | 40920 | 481
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 7 | TS | TS | 12.954 | 0.28126 | 1.143 | Industrial Grade | Unshielded, 600V | 19876 | 558
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 7 | TS | TP | 12.7 | 0.23662 | 1.143 | Industrial Grade | Unshielded, 600V | 40816 | 582
Dekoron | 2X35 | XLPE | PVC | 14 | 7 | TS | TP | 13.3858 | 0.2887 | 1.143 | Industrial Grade | 600V | 2X35-40760 | 173
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 7 | TS | TS | 10.922 | 0.2262 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 214-07 | 53
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 7 | TS | TS | 13.335 | 0.28573 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 814-07 | 209
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 7 | TS | TP | 13.208 | 0.28424 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 224070 | 376
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 7 | TS | TP | 13.208 | 0.28424 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 204070 | 383
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 7 | TS | TP | 13.208 | 0.28424 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 104073 | 463
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 7 | TS | TP | 15.748 | 0.36609 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 254070 | 960
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 7 | TS | TP | 15.748 | 0.36609 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 154073 | 1077
General Cable | CHTC® | XLPE | CSPE | 14 | 7 | TS | TS | 12.827 | 0.26638 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 223750 | 193
General Cable | CVTC® | XLPE | PVC | 14 | 7 | TS | TP | 14.986 | 0.26192 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770560 | 220
General Cable | EHTC® | EPR | CSPE | 14 | 7 | TS | TS | 12.827 | 0.21578 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | 262160 | 235
General Cable | FREP® | EPR | CPE | 14 | 7 | TS | TP | 12.954 | 0.26192 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 354820 | 330
General Cable | FREP® | EPR | CPE | 14 | 7 | TS | TP | 12.827 | 0.25745 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280200 | 331
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 7 | TS | TS | 12.4968 | 0.28275 | 1.143 | Class 1E Nuclear | Unshielded, 600V | 378410 | 503
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 7 | TS | TS | 16.5862 | 0.43454 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378900 | 1136
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 7 | TS | TS | 13.208 | 0.30805 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2157 | 308
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 7 | TS | TS | 13.462 | 0.30656 | 1.143 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2157 | 350
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 7 | TS | TP | 18.542 | 0.37799 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3007 | 592
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 7 | Sil | TP | 23.114 | 0.56253 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3457 | 632
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 7 | TS | TS | 19.812 | 0.5655 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6157 | 816
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 7 | TS | TS | 16.51 | 0.41222 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2157 | 832
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 7 | TS | TS | 17.272 | 0.46877 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6157 | 865
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 7 | TS | TS | 17.78 | 0.44198 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2157 | 922
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 7 | TS | TS | 11.43 | 0.23811 | 0.889 | Class 1E Nuclear | Unshielded, 600V | C15-0070 | 70
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 7 | TS | TS | 10.668 | 0.22322 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0070 | 83
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 7 | Sil | Fiber | 16.256 | 0.3274 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0070 | 99
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 7 | TS | TS | 12.7 | 0.27531 | 1.143 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0070 | 285
Rockbestus-Sup | Vita-Link CAROLFIRE | SR | SR | 14 | 7 | Sil | TS | 19.558 | 0.49853 | 0 |  |  |  | 1562
GENERIC | GENERIC | TP | TP | 14 | 8 | TP | TP | 12.446 | 0.26638 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 8 | TS | TP | 20.828 | 0.4777 | 1.27
American Insulated Wire | American SDN® | PVC | CP | 14 | 8 | TP | TS | 12.827 | 0.29763 | 1.143 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38634 | 183
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 8 | TP | TP | 12.446 | 0.26638 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4083 | 431
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 8 | TS | TS | 14.859 | 0.34228 | 1.524 | Industrial Grade | Unshielded, 600V | 25203 | 1154
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 8 | TS | TS | 22.606 | 0.66521 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N7512 | 1513
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 8 | TS | TS | 23.114 | 0.66372 | 3.175 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13410 | 1533
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 14 | 8 | TS | TP | 20.828 | 0.4777 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3408 | 614
GENERIC | GENERIC | TP | TP | 14 | 9 | TP | TP | 13.4874 | 0.31103 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 9 | TS | TP | 16.51 | 0.40776 | 1.524
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 9 | TP | TP | 12.7762 | 0.32888 | 1.143 | Industrial Grade | Unshielded, 600V | 68120 | 491
American Insulated Wire | American SDN® | PVC | CP | 14 | 9 | TP | TS | 14.478 | 0.34972 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38801 | 715
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 9 | TP | TP | 11.0744 | 0.26043 | 0.381 | Industrial Grade | Unshielded, 600V | 181409C6 | 5
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 9 | TP | TP | 9.906 | 0.26936 | 1.143 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 256
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 9 | TP | TP | 12.7254 | 0.34228 | 1.143 | Industrial Grade | Unshielded, 600V | 181409C6 | 271
Dekoron | 1C99 | PVC | PVC | 14 | 9 | TP | TP | 13.4874 | 0.31103 | 1.143 | Industrial Grade | 600V | 1C99-4090L | 139
Dekoron | 1735 | PE | PVC | 14 | 9 | TP | TP | 16.51 | 0.36906 | 1.524 | Industrial Grade | 600V |  | 651
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 9 | TP | TP | 13.335 | 0.29614 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4093 | 432
Draka | 20-10 Control Cable | PE | PVC | 14 | 9 | TP | TP | 16.256 | 0.35418 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 72090 | 682
General Cable | 20/10 | PE | PVC | 14 | 9 | TP | TP | 15.748 | 0.35121 | 1.524 | Industrial Grade | Unshielded, 600V | 365430 | 673
General Cable | VNTC® | PVC | PVC | 14 | 9 | TP | TP | 12.827 | 0.31698 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235090 | 1141
Okonite | Okozel® | ETFE | ETFE | 14 | 9 | TP | TP | 10.668 | 0.25299 | 0.381 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3359 | 11
Okonite | P-30 | PE | PVC | 14 | 9 | TP | TP | 16.002 | 0.36311 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2159 | 990
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 9 | TS | TP | 15.4178 | 0.33633 | 1.524 | Industrial Grade | Unshielded, 600V | 40921 | 1102
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 9 | TS | TS | 15.875 | 0.38246 | 1.524 | Industrial Grade | Unshielded, 600V | 19877 | 1155
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 9 | TS | TP | 15.494 | 0.33037 | 1.524 | Industrial Grade | Unshielded, 600V | 40953 | 1174
Dekoron | 2X35 | XLPE | PVC | 14 | 9 | TS | TP | 16.51 | 0.39436 | 1.524 | Industrial Grade | 600V | 2X35-40960 | 703
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 9 | TS | TS | 12.827 | 0.28573 | 0.762 | Industrial Grade | Unshielded, 600V, 90°C | 214-09 | 54
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 9 | TS | TS | 16.383 | 0.39139 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 814-09 | 758
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 9 | TS | TP | 16.51 | 0.40776 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 224090 | 955
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 9 | TS | TP | 16.51 | 0.40776 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 204090 | 961
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 9 | TS | TP | 17.907 | 0.46282 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 254090 | 962
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 9 | TS | TP | 16.51 | 0.40776 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 104093 | 1078
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 9 | TS | TP | 17.907 | 0.46282 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 154093 | 1079
General Cable | CHTC® | XLPE | CSPE | 14 | 9 | TS | TS | 15.748 | 0.37055 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 223760 | 743
General Cable | CVTC® | XLPE | PVC | 14 | 9 | TS | TP | 15.748 | 0.3646 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770540 | 762
General Cable | EHTC® | EPR | CSPE | 14 | 9 | TS | TS | 15.748 | 0.27233 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343600 | 773
General Cable | FREP® | EPR | CPE | 14 | 9 | TS | TP | 15.875 | 0.36162 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367120 | 884
General Cable | FREP® | EPR | CPE | 14 | 9 | TS | TP | 15.748 | 0.35716 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 280210 | 885
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 9 | TS | TS | 15.3162 | 0.3899 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378420 | 1123
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 9 | TS | TS | 18.923 | 0.55955 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378910 | 1137
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 9 | TS | TP | 20.828 | 0.45835 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3009 | 593
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 9 | Sil | TP | 26.416 | 0.65182 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3459 | 633
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 9 | TS | TS | 23.368 | 0.74706 | 1.524 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6159 | 817
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 9 | TS | TS | 19.05 | 0.51193 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2159 | 833
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 9 | TS | TS | 16.256 | 0.42859 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2159 | 834
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 9 | TS | TS | 19.558 | 0.57592 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6159 | 866
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 9 | TS | TS | 17.526 | 0.45538 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2159 | 905
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 9 | TS | TS | 20.32 | 0.59378 | 1.524 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2159 | 923
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 9 | TS | TS | 12.446 | 0.29019 | 0.889 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0090 | 84
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 9 | Sil | Fiber | 19.304 | 0.43901 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0090 | 100
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 9 | TS | TS | 14.224 | 0.33484 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C15-0090 | 293
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 9 | TS | TS | 15.748 | 0.38692 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0090 | 802
GENERIC | GENERIC | TP | TP | 14 | 10 | TP | TS | 14.732 | 0.36609 | 1.524
GENERIC | GENERIC | TS | TS | 14 | 10 | TS | TS | 24.892 | 0.7173 | 3.175
American Insulated Wire | American SDN® | PVC | CP | 14 | 10 | TP | TS | 14.732 | 0.36609 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38513 | 716
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 10 | TP | TP | 15.24 | 0.35418 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4103 | 1036
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 10 | TS | TS | 16.51 | 0.4152 | 1.524 | Industrial Grade | Unshielded, 600V | 31111 | 1156
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 10 | TS | TS | 25.146 | 0.74408 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7548 | 1521
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 10 | TS | TS | 24.892 | 0.7173 | 3.175 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13411 | 1534
GENERIC | GENERIC | TP | TP | 14 | 11 | TP | TP | 15.621 | 0.38395 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4113 | 1037
GENERIC | GENERIC | TS | TS | 14 | 11 | TS | TP | 23.114 | 0.58782 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3411 | 615
American Insulated Wire | American SDN® | PVC | CP | 14 | 11 | TP | TS | 15.113 | 0.4018 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38802 | 717
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 11 | TP | TP | 15.621 | 0.38395 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4113 | 1037
GENERIC | GENERIC | TP | TP | 14 | 12 | TP | TP | 15.621 | 0.40925 | 1.524
GENERIC | GENERIC | TS | TS | 14 | 12 | TS | TP | 19.939 | 0.58485 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 14 | 12 | TP | TS | 15.113 | 0.43157 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38635 | 718
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 12 | TP | TP | 15.0876 | 0.41817 | 1.524 | Industrial Grade | Unshielded, 600V | 68121 | 1111
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 12 | TP | TP | 13.2334 | 0.36609 | 1.143 | Industrial Grade | Unshielded, 600V | 181412C6 | 244
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 12 | TP | TP | 11.2014 | 0.35121 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 786
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 12 | TP | TP | 15.0368 | 0.47324 | 1.524 | Industrial Grade | Unshielded, 600V | 181412C6 | 794
Dekoron | 1735 | PE | PVC | 14 | 12 | TP | TP | 18.4404 | 0.46282 | 1.524 | Industrial Grade | 600V |  | 652
Dekoron | 1C99 | PVC | PVC | 14 | 12 | TP | TP | 16.1036 | 0.43157 | 1.524 | Industrial Grade | 600V | 1C99-4120L | 663
Draka | 20-10 Control Cable | PE | PVC | 14 | 12 | TP | TP | 18.034 | 0.45389 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 72120 | 683
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 12 | TP | TP | 15.621 | 0.40925 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4123 | 1038
General Cable | 20/10 | PE | PVC | 14 | 12 | TP | TP | 17.526 | 0.44645 | 1.524 | Industrial Grade | Unshielded, 600V | 647590 | 674
General Cable | VNTC® | PVC | PVC | 14 | 12 | TP | TP | 15.113 | 0.39734 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235110 | 1142
Okonite | Okozel® | ETFE | ETFE | 14 | 12 | TP | TP | 12.192 | 0.35121 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3362 | 24
Okonite | P-30 | PE | PVC | 14 | 12 | TP | TP | 18.034 | 0.45538 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2162 | 991
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 12 | TS | TP | 16.9164 | 0.41966 | 1.524 | Industrial Grade | Unshielded, 600V | 40922 | 1103
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 12 | TS | TS | 17.399 | 0.47324 | 1.524 | Industrial Grade | Unshielded, 600V | 19878 | 1157
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 12 | TS | TP | 17.018 | 0.41073 | 1.524 | Industrial Grade | Unshielded, 600V | 40954 | 1175
Dekoron | 2X35 | XLPE | PVC | 14 | 12 | TS | TP | 18.4404 | 0.49705 | 1.524 | Industrial Grade | 600V | 2X35-40960 | 704
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 12 | TS | TS | 15.24 | 0.40478 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 214-12 | 471
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 12 | TS | TS | 18.288 | 0.50151 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 814-12 | 759
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 12 | TS | TP | 20.066 | 0.64438 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 224120 | 956
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 12 | TS | TP | 18.034 | 0.50598 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 204120 | 963
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 12 | TS | TP | 19.939 | 0.58485 | 1.524 | Industrial Grade | Shielded, 600V, 90°C | 254120 | 964
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 12 | TS | TP | 18.034 | 0.50598 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 104123 | 1080
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 12 | TS | TP | 19.939 | 0.58485 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 154123 | 1081
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 12 | TS | TS | 25.908 | 0.84528 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7517 | 1522
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 12 | TS | TS | 26.416 | 0.84528 | 3.556 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13412 | 1548
General Cable | CHTC® | XLPE | CSPE | 14 | 12 | TS | TS | 17.78 | 0.47175 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 223640 | 744
General Cable | CVTC® | XLPE | PVC | 14 | 12 | TS | TP | 17.272 | 0.44943 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770470 | 763
General Cable | EHTC® | EPR | CSPE | 14 | 12 | TS | TS | 17.78 | 0.37799 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 248290 | 774
General Cable | FREP® | EPR | CPE | 14 | 12 | TS | TP | 17.907 | 0.4524 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 354830 | 886
General Cable | FREP® | EPR | CPE | 14 | 12 | TS | TP | 17.78 | 0.44794 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279880 | 887
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 12 | TS | TS | 17.145 | 0.47919 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378430 | 1124
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 12 | TS | TS | 21.0312 | 0.71581 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378920 | 1138
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 12 | TS | TP | 23.114 | 0.56699 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3012 | 594
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 12 | Sil | TP | 28.702 | 0.83188 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3462 | 634
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 12 | TS | TS | 21.336 | 0.63396 | 1.524 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2162 | 835
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 12 | TS | TS | 18.288 | 0.55657 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2162 | 836
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 12 | TS | TS | 21.336 | 0.69646 | 1.524 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6162 | 867
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 12 | TS | TS | 18.288 | 0.56997 | 1.524 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2162 | 906
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 12 | TS | TS | 25.654 | 0.9048 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6162 | 1273
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 12 | TS | TS | 23.876 | 0.75599 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2162 | 1333
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 12 | Sil | Fiber | 21.844 | 0.54318 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0120 | 101
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 12 | TS | TS | 16.002 | 0.40925 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C15-0120 | 294
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 12 | TS | TS | 14.732 | 0.37948 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0120 | 571
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 12 | TS | TS | 17.526 | 0.48365 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0120 | 803
GENERIC | GENERIC | TP | TS | 14 | 13 | TP | TS | 15.875 | 0.45389 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38803 | 719
American Insulated Wire | American SDN® | PVC | CP | 14 | 13 | TP | TS | 15.875 | 0.45389 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38803 | 719
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 13 | TP | TP | 16.383 | 0.4405 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4133 | 1039
GENERIC | GENERIC | TP | TP | 14 | 14 | TP | TS | 15.875 | 0.48365 | 1.524
GENERIC | GENERIC | TS | TS | 14 | 14 | TS | TS | 18.669 | 0.55062 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 14 | 14 | TP | TS | 15.875 | 0.48365 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38636 | 720
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 14 | TP | TP | 16.383 | 0.46728 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4143 | 1040
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 14 | TS | TS | 18.669 | 0.55062 | 1.524 | Industrial Grade | Unshielded, 600V | 19879 | 1158
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 14 | TS | TS | 27.051 | 0.93754 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7910 | 1523
GENERIC | GENERIC | TP | TP | 14 | 15 | TP | TP | 17.272 | 0.49853 | 1.524
GENERIC | GENERIC | TS | TS | 14 | 15 | TS | TP | 18.796 | 0.49705 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 14 | 15 | TP | TS | 16.637 | 0.50598 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38804 | 721
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 15 | TP | TP | 16.2306 | 0.50598 | 1.524 | Industrial Grade | Unshielded, 600V | 68122 | 1112
Draka | 20-10 Control Cable | PE | PVC | 14 | 15 | TP | TP | 19.939 | 0.55062 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 72150 | 684
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 15 | TP | TP | 17.272 | 0.49853 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4153 | 1041
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 15 | TS | TP | 18.669 | 0.50746 | 1.524 | Industrial Grade | Unshielded, 600V | 40923 | 1104
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 15 | TS | TS | 19.177 | 0.61759 | 1.524 | Industrial Grade | Unshielded, 600V | 19880 | 1159
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 15 | TS | TP | 18.796 | 0.49705 | 1.524 | Industrial Grade | Unshielded, 600V | 40955 | 1176
GENERIC | GENERIC | TP | TP | 14 | 16 | TP | TP | 14.6558 | 0.47026 | 1.143
GENERIC | GENERIC | TS | TS | 14 | 16 | TS | TP | 20.066 | 0.64438 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 14 | 16 | TP | TS | 16.637 | 0.52681 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38514 | 722
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 16 | TP | TP | 14.6558 | 0.47026 | 1.143 | Industrial Grade | Unshielded, 600V | 181416C6 | 245
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 16 | TP | TP | 12.5222 | 0.45687 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 787
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 16 | TP | TP | 16.5608 | 0.59675 | 1.524 | Industrial Grade | Unshielded, 600V | 181416C6 | 795
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 16 | TP | TP | 17.272 | 0.52532 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4163 | 1042
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 16 | TS | TS | 19.685 | 0.6533 | 1.524 | Industrial Grade | Unshielded, 600V | 27601 | 1160
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 16 | TS | TP | 20.066 | 0.64438 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 224160 | 957
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 16 | TS | TP | 20.066 | 0.64438 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 204160 | 965
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 16 | TS | TP | 20.066 | 0.64438 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 104163 | 1082
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 16 | TS | TS | 28.448 | 1.0625 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7549 | 1524
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 16 | TS | TS | 28.702 | 1.0164 | 3.556 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13414 | 1549
GENERIC | GENERIC | TP | TS | 14 | 17 | TP | TS | 18.415 | 0.59527 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38805 | 723
American Insulated Wire | American SDN® | PVC | CP | 14 | 17 | TP | TS | 18.415 | 0.59527 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38805 | 723
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 17 | TP | TP | 18.161 | 0.55657 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4173 | 1043
GENERIC | GENERIC | TP | TP | 14 | 18 | TP | TS | 18.415 | 0.61015 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38806 | 724
GENERIC | GENERIC | TS | TP | 14 | 18 | TS | TP | 26.416 | 0.82444 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3418 | 616
American Insulated Wire | American SDN® | PVC | CP | 14 | 18 | TP | TS | 18.415 | 0.61015 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38806 | 724
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 18 | TP | TP | 18.161 | 0.58187 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4183 | 1044
GENERIC | GENERIC | TP | TP | 14 | 19 | TP | TP | 17.653 | 0.58931 | 1.524
GENERIC | GENERIC | TS | TS | 14 | 19 | TS | TP | 21.209 | 0.73813 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 14 | 19 | TP | TS | 18.415 | 0.63991 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38637 | 725
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 19 | TP | TP | 17.526 | 0.60717 | 1.524 | Industrial Grade | Unshielded, 600V | 68123 | 1113
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 19 | TP | TP | 15.4432 | 0.54764 | 1.143 | Industrial Grade | Unshielded, 600V | 181419C6 | 246
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 19 | TP | TP | 13.2334 | 0.53276 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 788
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 19 | TP | TP | 17.4244 | 0.68456 | 1.524 | Industrial Grade | Unshielded, 600V | 181419C6 | 796
Dekoron | 1C99 | PVC | PVC | 14 | 19 | TP | TP | 18.5674 | 0.62503 | 1.524 | Industrial Grade | 600V | 1C99-4190L | 664
Draka | 20-10 Control Cable | PE | PVC | 14 | 19 | TP | TP | 20.955 | 0.67414 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 72190 | 685
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 19 | TP | TP | 18.161 | 0.60866 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4193 | 1045
General Cable | 20/10 | PE | PVC | 14 | 19 | TP | TP | 20.32 | 0.65926 | 1.524 | Industrial Grade | Unshielded, 600V | 647600 | 675
General Cable | VNTC® | PVC | PVC | 14 | 19 | TP | TP | 17.653 | 0.58931 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235130 | 1143
Okonite | Okozel® | ETFE | ETFE | 14 | 19 | TP | TP | 14.478 | 0.52681 | 0.508 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3369 | 25
Okonite | P-30 | PE | PVC | 14 | 19 | TP | TP | 21.082 | 0.67414 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2169 | 992
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 19 | TS | TP | 20.193 | 0.61759 | 1.524 | Industrial Grade | Unshielded, 600V | 40924 | 1105
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 19 | TS | TS | 20.701 | 0.67563 | 1.524 | Industrial Grade | Unshielded, 600V | 19881 | 1161
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 19 | TS | TP | 20.32 | 0.60568 | 1.524 | Industrial Grade | Unshielded, 600V | 40956 | 1177
Draka | Reduced Diameter Control | XLPE | XLPO | 14 | 19 | TS | TS | 18.161 | 0.61461 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 214-19 | 472
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 19 | TS | TS | 21.336 | 0.73664 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 814-19 | 760
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 19 | TS | TP | 21.209 | 0.73813 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 224190 | 958
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 19 | TS | TP | 21.209 | 0.73813 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 204190 | 966
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 19 | TS | TP | 21.209 | 0.73813 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 104193 | 1083
General Cable | CHTC® | XLPE | CSPE | 14 | 19 | TS | TS | 20.701 | 0.69497 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 223670 | 745
General Cable | CVTC® | XLPE | PVC | 14 | 19 | TS | TP | 20.32 | 0.68456 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770550 | 764
General Cable | EHTC® | EPR | CSPE | 14 | 19 | TS | TS | 20.701 | 0.48068 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC | 343630 | 775
General Cable | FREP® | EPR | CPE | 14 | 19 | TS | TP | 20.828 | 0.70093 | 1.524 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 305360 | 888
General Cable | FREP® | EPR | CPE | 14 | 19 | TS | TP | 20.701 | 0.69646 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279580 | 889
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 19 | TS | TS | 19.939 | 0.75152 | 1.524 | Class 1E Nuclear | Unshielded, 600V | 378440 | 1125
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 19 | TS | TS | 25.3238 | 1.073 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378930 | 1457
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 19 | TS | TP | 26.416 | 0.79914 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3019 | 595
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 19 | Sil | TP | 33.02 | 1.1637 | 1.27 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3469 | 635
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 19 | TS | TS | 29.21 | 1.2307 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6169 | 1274
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 19 | TS | TS | 26.162 | 0.97772 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2169 | 1286
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 19 | TS | TS | 22.352 | 0.84677 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2169 | 1287
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 19 | TS | TS | 25.4 | 1.0224 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6169 | 1301
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 19 | TS | TS | 23.622 | 0.85421 | 2.032 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2169 | 1326
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 19 | TS | TS | 27.432 | 1.0462 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2169 | 1334
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 19 | Sil | Fiber | 25.654 | 0.87058 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0190 | 102
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 19 | TS | TS | 18.288 | 0.61015 | 1.143 | Class 1E Nuclear | Unshielded, 600V | C15-0190 | 295
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 19 | TS | TS | 17.018 | 0.57294 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0190 | 572
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 19 | TS | TS | 20.32 | 0.69944 | 1.524 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-0190 | 804
GENERIC | GENERIC | TP | TP | 14 | 20 | TS | TP | 23.495 | 0.81849 | 2.032
GENERIC | GENERIC | TS | TS | 14 | 20 | TS | TS | 32.131 | 1.3349 | 3.175
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 20 | TP | TP | 19.939 | 0.65479 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4203 | 1046
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 20 | TS | TP | 23.495 | 0.81849 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 224200 | 1349
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 20 | TS | TP | 23.495 | 0.81849 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 404200 | 1353
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 20 | TS | TP | 23.495 | 0.81849 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 104203 | 1419
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 14 | 20 | TS | TS | 23.495 | 0.83932 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 814-20 | 1245
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 20 | TS | TS | 32.131 | 1.3349 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7462 | 1538
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 20 | TS | TS | 32.258 | 1.314 | 3.937 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13415 | 1554
GENERIC | GENERIC | TP | TS | 14 | 21 | TP | TS | 18.796 | 0.69944 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38807 | 726
American Insulated Wire | American SDN® | PVC | CP | 14 | 21 | TP | TS | 18.796 | 0.69944 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38807 | 726
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 21 | TP | TP | 19.939 | 0.67414 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4213 | 1047
GENERIC | GENERIC | TP | TP | 14 | 22 | TP | TP | 20.32 | 0.70241 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4223 | 1048
GENERIC | GENERIC | TP | TP | 14 | 23 | TP | TP | 20.32 | 0.73664 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4233 | 1049
GENERIC | GENERIC | TS | TS | 14 | 23 | TS | TS | 23.876 | 0.95838 | 2.032 | Industrial Grade | Unshielded, 600V | 31112 | 1473
GENERIC | GENERIC | TP | TP | 14 | 24 | TP | TS | 20.447 | 0.75896 | 1.524
GENERIC | GENERIC | TS | TS | 14 | 24 | TS | TS | 34.925 | 1.6132 | 3.175
American Insulated Wire | American SDN® | PVC | CP | 14 | 24 | TP | TS | 20.447 | 0.75896 | 1.524 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38638 | 727
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 24 | TP | TP | 21.209 | 0.76045 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4243 | 1050
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 24 | TS | TS | 24.257 | 0.99409 | 2.032 | Industrial Grade | Unshielded, 600V | 31113 | 1474
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 24 | TS | TS | 34.925 | 1.6132 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7621 | 1539
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 14 | 24 | TS | TS | 36.068 | 1.6459 | 4.318 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13416 | 1558
GENERIC | GENERIC | TP | TP | 14 | 25 | TP | TP | 20.3708 | 0.78277 | 1.524
GENERIC | GENERIC | TS | TS | 14 | 25 | TS | TS | 24.1554 | 0.93754 | 2.032
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 25 | TP | TP | 20.3708 | 0.78277 | 1.524 | Industrial Grade | Unshielded, 600V | 68124 | 1114
American Insulated Wire | American SDN® | PVC | CP | 14 | 25 | TP | TS | 22.225 | 0.77385 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38808 | 1228
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 25 | TP | TP | 17.8562 | 0.70837 | 1.524 | Industrial Grade | Unshielded, 600V | 181423C6 | 785
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 25 | TP | TP | 15.4432 | 0.69348 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 789
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 25 | TP | TP | 20.0406 | 0.87504 | 1.524 | Industrial Grade | Unshielded, 600V | 181423C6 | 797
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 25 | TP | TP | 21.59 | 0.78873 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4253 | 1051
Draka | 20-10 Control Cable | PE | PVC | 14 | 25 | TP | TP | 26.162 | 0.92861 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 72250 | 1205
General Cable | VNTC® | PVC | PVC | 14 | 25 | TP | TP | 19.939 | 0.7545 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235150 | 1144
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 25 | TS | TP | 24.003 | 0.8795 | 2.032 | Industrial Grade | Unshielded, 600V | 40925 | 1434
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 25 | TS | TS | 24.638 | 1.0283 | 2.032 | Industrial Grade | Unshielded, 600V | 19882 | 1475
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 25 | TS | TP | 24.13 | 0.86165 | 2.032 | Industrial Grade | Unshielded, 600V | 40957 | 1495
General Cable | CVTC® | XLPE | PVC | 14 | 25 | TS | TP | 25.019 | 0.95391 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770450 | 1246
General Cable | EHTC® | EPR | CSPE | 14 | 25 | TS | TS | 25.4 | 0.70985 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 262190 | 1254
General Cable | FREP® | EPR | CPE | 14 | 25 | TS | TP | 23.876 | 0.93308 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367130 | 1310
General Cable | FREP® | EPR | CPE | 14 | 25 | TS | TP | 23.749 | 0.92861 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279590 | 1311
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 25 | TS | TS | 24.1554 | 0.93754 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378450 | 1444
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 25 | TS | TS | 28.9814 | 1.3274 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378940 | 1458
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 25 | Sil | Fiber | 30.226 | 1.2129 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0250 | 103
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 25 | TS | TS | 19.812 | 0.78129 | 1.143 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0250 | 573
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 25 | TS | TS | 22.352 | 0.84825 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C15-0250 | 1186
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 25 | TS | TS | 24.638 | 0.97475 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-3499 | 1264
GENERIC | GENERIC | TP | TP | 14 | 26 | TP | TP | 21.59 | 0.81403 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4263 | 1052
GENERIC | GENERIC | TS | TS | 14 | 26 | TS | TP | 26.416 | 1.0194 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 224260 | 1350
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 26 | TS | TP | 26.416 | 1.0194 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 204260 | 1354
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 26 | TS | TP | 26.416 | 1.0194 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 104263 | 1420
GENERIC | GENERIC | TP | TP | 14 | 27 | TP | TP | 21.59 | 0.84081 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4273 | 1053
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 27 | TP | TP | 21.59 | 0.84081 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4273 | 1053
Okonite | P-30 | PE | PVC | 14 | 27 | TP | TP | 26.162 | 0.98814 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2177 | 1373
GENERIC | GENERIC | TP | TP | 14 | 28 | TP | TP | 23.495 | 0.92266 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4283 | 1384
GENERIC | GENERIC | TP | TP | 14 | 29 | TP | TP | 23.495 | 0.94945 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4293 | 1385
GENERIC | GENERIC | TP | TP | 14 | 30 | TP | TP | 23.495 | 0.97624 | 2.032
GENERIC | GENERIC | TS | TS | 14 | 30 | TS | TP | 27.305 | 1.134 | 2.032
American Insulated Wire | American SDN® | PVC | CP | 14 | 30 | TP | TS | 22.606 | 0.98219 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38639 | 1229
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 30 | TP | TP | 22.5552 | 0.99112 | 2.032 | Industrial Grade | Unshielded, 600V | 68125 | 1439
Draka | 20-10 Control Cable | PE | PVC | 14 | 30 | TP | TP | 27.051 | 1.0313 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 72300 | 1206
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 30 | TP | TP | 23.495 | 0.97624 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4303 | 1386
General Cable | VNTC® | PVC | PVC | 14 | 30 | TP | TP | 22.733 | 0.94796 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235160 | 1464
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 30 | TS | TS | 26.67 | 1.192 | 2.032 | Industrial Grade | Unshielded, 600V | 31114 | 1476
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 30 | TS | TP | 27.305 | 1.134 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 224300 | 1351
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 30 | TS | TP | 27.305 | 1.134 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 204300 | 1355
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 30 | TS | TP | 27.305 | 1.134 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 104303 | 1421
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 30 | TS | TS | 39.37 | 2.0879 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7536 | 1540
General Cable | CVTC® | XLPE | PVC | 14 | 30 | TS | TP | 26.67 | 1.1012 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 295320 | 1247
General Cable | EHTC® | EPR | CSPE | 14 | 30 | TS | TS | 26.67 | 0.95987 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 343640 | 1255
General Cable | FREP® | EPR | CPE | 14 | 30 | TS | TP | 26.289 | 1.1161 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367140 | 1312
General Cable | FREP® | EPR | CPE | 14 | 30 | TS | TP | 26.162 | 1.1117 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 347080 | 1313
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 30 | TS | TS | 25.7302 | 1.1756 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378460 | 1445
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 30 | TS | TS | 30.7594 | 1.5358 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378950 | 1459
GENERIC | GENERIC | TP | TP | 14 | 31 | TP | TP | 24.384 | 1.0105 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4313 | 1387
GENERIC | GENERIC | TP | TP | 14 | 32 | TP | TP | 24.384 | 1.0358 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4323 | 1388
GENERIC | GENERIC | TP | TP | 14 | 33 | TP | TP | 24.384 | 1.0625 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4333 | 1389
GENERIC | GENERIC | TP | TP | 14 | 34 | TP | TP | 25.273 | 1.0968 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4343 | 1390
GENERIC | GENERIC | TP | TP | 14 | 35 | TP | TP | 25.273 | 1.1236 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4353 | 1391
GENERIC | GENERIC | TP | TP | 14 | 36 | TP | TP | 25.273 | 1.1489 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4363 | 1392
GENERIC | GENERIC | TS | TS | 14 | 36 | TS | TS | 43.815 | 2.6013 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7622 | 1541
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 14 | 36 | TS | TS | 43.815 | 2.6013 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7622 | 1541
Okonite | C-L-X® Type MC-HL (XHHW-2) | XLPE | PVC | 14 | 36 | TS | TP | 34.29 | 1.4108 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3436 | 617
GENERIC | GENERIC | TP | TP | 14 | 37 | TP | TP | 24.257 | 1.1816 | 2.032
GENERIC | GENERIC | TS | TS | 14 | 37 | TS | TS | 29.464 | 1.4852 | 2.032
American Insulated Wire | American SDN® | PVC | CP | 14 | 37 | TP | TS | 25.146 | 1.1682 | 2.032 | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38640 | 1230
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 14 | 37 | TP | TP | 24.257 | 1.1816 | 2.032 | Industrial Grade | Unshielded, 600V | 68126 | 1440
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 37 | TP | TP | 21.4376 | 1.0581 | 0.762 | Industrial Grade | Unshielded, 600V | 181437C6 | 39
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 14 | 37 | TP | TP | 18.0594 | 1.009 | 2.032 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 1262
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 14 | 37 | TP | TP | 24.13 | 1.3126 | 2.032 | Industrial Grade | Unshielded, 600V | 181437C6 | 1263
Draka | 20-10 Control Cable | PE | PVC | 14 | 37 | TP | TP | 29.21 | 1.2382 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 72370 | 1207
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 14 | 37 | TP | TP | 25.273 | 1.1756 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 4373 | 1393
General Cable | VNTC® | PVC | PVC | 14 | 37 | TP | TP | 24.638 | 1.1399 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 235170 | 1465
Okonite | Okozel® | ETFE | ETFE | 14 | 37 | TP | TP | 20.066 | 1.0164 | 0.635 | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3387 | 36
American Insulated Wire | TYPE TC Control/Instrument | XLPE | PVC | 14 | 37 | TS | TP | 28.067 | 1.2545 | 2.032 | Industrial Grade | Unshielded, 600V | 40926 | 1435
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 14 | 37 | TS | TS | 28.829 | 1.3989 | 2.032 | Industrial Grade | Unshielded, 600V | 19883 | 1477
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 14 | 37 | TS | TS | 28.829 | 1.4108 | 2.032 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 31359 | 1494
American Insulated Wire | XLPE-CPE TYPE TC Power/Control | XLPE | CPE | 14 | 37 | TS | TP | 28.194 | 1.1727 | 2.032 | Industrial Grade | Unshielded, 600V | 40958 | 1496
Draka | General Purpose Control XLPE | XLPE | CPE | 14 | 37 | TS | TP | 29.337 | 1.3617 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 224370 | 1352
Draka | General Purpose Control XLPE | XLPE | PVC | 14 | 37 | TS | TP | 29.337 | 1.3617 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 204370 | 1356
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 14 | 37 | TS | TP | 29.337 | 1.3617 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 104373 | 1422
General Cable | CHTC® | XLPE | CSPE | 14 | 37 | TS | TS | 28.702 | 1.3379 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 232850 | 1241
General Cable | CVTC® | XLPE | PVC | 14 | 37 | TS | TP | 28.702 | 1.3215 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 770430 | 1248
General Cable | EHTC® | EPR | CSPE | 14 | 37 | TS | TS | 28.702 | 1.1102 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC | 343650 | 1256
General Cable | FREP® | EPR | CPE | 14 | 37 | TS | TP | 28.321 | 1.3066 | 2.032 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 367150 | 1314
General Cable | FREP® | EPR | CPE | 14 | 37 | TS | TP | 28.194 | 1.3021 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279600 | 1315
General Cable | Ultrol® 275 | XLPE | CSPE | 14 | 37 | TS | TS | 27.7114 | 1.3096 | 2.032 | Class 1E Nuclear | Unshielded, 600V | 378470 | 1446
Okonite | C-L-X® Type MC (XHHW-2) | XLPE | PVC | 14 | 37 | TS | TP | 34.29 | 1.4078 | 1.27 | Industrial Grade | Cont. Corrugated Alum. Sheath w/jacket, 600V, 90°C | 546-31-3037 | 588
Okonite | Okotherm® CIC Fire Resistant Cable | SR | PVC | 14 | 37 | Sil | TP | 43.942 | 2.1504 | 1.524 | Industrial Grade | Cont. Corr. Alum C-L-X Sheath, 600V, 90°, fiberglass braid over silicone | 546-15-3487 | 988
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 14 | 37 | TS | TS | 38.608 | 2.1311 | 2.032 | Nuclear Tracability | 2000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6187 | 1275
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 37 | TS | TS | 34.798 | 1.7278 | 2.032 | Nuclear Qualified 383 | Unshielded, 2000V, 90° | 202-14-2187 | 1288
Okonite | FMR® Okolon® | EPR | CSPE | 14 | 37 | TS | TS | 29.464 | 1.4852 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2187 | 1289
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 14 | 37 | TS | TS | 32.512 | 1.7099 | 2.032 | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6187 | 1302
Okonite | FRM-N® Okolon® | EPR | CSPE | 14 | 37 | TS | TS | 30.48 | 1.4807 | 2.032 | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2187 | 1327
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 14 | 37 | TS | TS | 36.068 | 1.8111 | 2.032 | Nuclear Qualified | Unshielded, 2000V, 90°C | 202-18-2187 | 1335
Rockbestus-Sup | Firewall® SR | SR | Aramid Braid | 14 | 37 | Sil | Fiber | 35.306 | 1.6593 | 1.016 | Class 1E Nuclear | Unshielded, 600V, 125°C | C64-0370 | 104
Rockbestus-Sup | Firewall® XLR | XLPE | XLPE | 14 | 37 | TS | TS | 25.654 | 1.1905 | 1.651 | Class 1E Nuclear | Unshielded, 600V | C15-0370 | 1187
Rockbestus-Sup | X-Link® TC | XLPO | XLPO | 14 | 37 | TS | TS | 23.622 | 1.1087 | 1.651 | Industrial Grade | Unshielded, 600V, UL Type TC | C14-0370 | 1195
Rockbestus-Sup | Firewall® III | XLPE | CSPE | 14 | 37 | TS | TS | 28.194 | 1.3542 | 2.032 | Class 1E Nuclear | Unshielded, 600V, UL Type TC | C53-3501 | 1265
General Cable | Ultrol® 300 | XLPE | CSPE | 14 | 37 | TS | TS | 33.0454 | 1.8453 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378960 | 1460
GENERIC | GENERIC | TP | TP | 16 | 2 | TP | TP | 7.874 | 0.086314 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 3702 | 440
GENERIC | GENERIC | TS | TS | 16 | 2 | TS | TS | 9.017 | 0.10715 | 1.143
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 16 | 2 | TS | TS | 9.017 | 0.10715 | 1.143 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 19869 | 564
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 2 | TS | TS | 9.144 | 0.093754 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 816-02 | 202
General Cable | FREP® | EPR | CPE | 16 | 2 | TS | TP | 8.128 | 0.077385 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 280470 | 320
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 2 | TS | TS | 9.1186 | 0.13691 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378750 | 511
GENERIC | GENERIC | TP | TP | 16 | 3 | TP | TP | 8.255 | 0.10864 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 3 | TS | TS | 9.525 | 0.12501 | 1.143
Draka | 15-10 Control Cable | PE | PVC | 16 | 3 | TP | TP | 8.763 | 0.10417 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 71030 | 130
Draka | Power & Control TFN | PVC | PVC | 16 | 3 | TP | TP | 8.001 | 0.099707 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2033 | 411
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 16 | 3 | TP | TP | 8.255 | 0.10864 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 3703 | 441
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 3 | TS | TS | 9.144 | 0.11756 | 1.143 | Industrial Grade | Unshielded, 600V | 19921 | 549
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 16 | 3 | TS | TS | 9.525 | 0.12501 | 1.143 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 19870 | 565
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 3 | TS | TP | 8.763 | 0.11012 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 222030 | 359
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 3 | TS | TP | 8.763 | 0.11012 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202030 | 366
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 3 | TS | TS | 10.541 | 0.13989 | 1.524 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13420 | 711
General Cable | FREP® | EPR | CPE | 16 | 3 | TS | TP | 8.509 | 0.098219 | 1.143 | Industrial Grade | Overall shielded, 600V, UL Type TC-ER | 280490 | 321
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 3 | TS | TS | 9.6266 | 0.15328 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378760 | 512
GENERIC | GENERIC | TP | TP | 16 | 4 | TP | TP | 8.89 | 0.12947 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 4 | TS | TS | 10.033 | 0.1503 | 1.143
Draka | 15-10 Control Cable | PE | PVC | 16 | 4 | TP | TP | 9.5758 | 0.12649 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 71040 | 131
Draka | Power & Control TFN | PVC | PVC | 16 | 4 | TP | TP | 8.636 | 0.12203 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2043 | 412
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 16 | 4 | TP | TP | 8.89 | 0.12947 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 3704 | 442
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 4 | TS | TS | 10.033 | 0.1503 | 1.143 | Industrial Grade | Unshielded, 600V | 19922 | 550
American Insulated Wire | XL-40™ Shielded Control | XLPO | CSPE | 16 | 4 | TS | TS | 9.906 | 0.15775 | 1.143 | Industrial Grade | Shielded, Overall Shield Alum. Polyester Tape, 600V | 24201 | 566
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 4 | TS | TS | 10.414 | 0.14584 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 816-04 | 203
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 4 | TS | TP | 9.652 | 0.13691 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 222040 | 360
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 4 | TS | TP | 9.652 | 0.13691 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202040 | 367
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 4 | TS | TS | 11.303 | 0.16965 | 1.524 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13421 | 712
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 4 | TS | TS | 10.5156 | 0.189 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378770 | 513
GENERIC | GENERIC | TP | TP | 16 | 5 | TP | TP | 9.652 | 0.12798 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 5 | TS | TS | 10.922 | 0.17263 | 1.143
Draka | 15-10 Control Cable | PE | PVC | 16 | 5 | TP | TP | 10.287 | 0.14138 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 71050 | 132
Draka | Power & Control TFN | PVC | PVC | 16 | 5 | TP | TP | 9.398 | 0.14435 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2053 | 413
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 16 | 5 | TP | TP | 9.652 | 0.12798 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 3705 | 443
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 5 | TS | TS | 10.922 | 0.17263 | 1.143 | Industrial Grade | Unshielded, 600V | 19923 | 551
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 5 | TS | TP | 10.287 | 0.16072 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 222050 | 361
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 5 | TS | TP | 10.287 | 0.16072 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202050 | 368
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 5 | TS | TS | 13.0048 | 0.21727 | 1.143 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378780 | 514
GENERIC | GENERIC | TP | TP | 16 | 6 | TP | TP | 10.16 | 0.16816 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2063 | 414
GENERIC | GENERIC | TS | TS | 16 | 6 | TS | TS | 12.446 | 0.2009 | 1.143
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 6 | TS | TS | 12.446 | 0.2009 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 816-06 | 204
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 6 | TS | TP | 11.303 | 0.18156 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 222060 | 362
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 6 | TS | TP | 11.303 | 0.18156 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202060 | 369
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 6 | TS | TS | 14.224 | 0.26787 | 1.524 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13422 | 713
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 6 | TS | TS | 14.986 | 0.29912 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | N7012 | 1240
GENERIC | GENERIC | TP | TP | 16 | 7 | TP | TP | 10.541 | 0.18156 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 7 | TS | TS | 12.446 | 0.22174 | 1.143
Draka | 15-10 Control Cable | PE | PVC | 16 | 7 | TP | TP | 11.176 | 0.18156 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 71070 | 133
Draka | Power & Control TFN | PVC | PVC | 16 | 7 | TP | TP | 10.16 | 0.18007 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2073 | 415
Draka | Power & Control Type TC THHN or THWN (or TFN) | PVC | PVC | 16 | 7 | TP | TP | 10.541 | 0.18156 | 1.143 | Industrial Grade | Shielded (Alum Foil), 600V, 90°C dry, 75° wet | 3707 | 444
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 7 | TS | TS | 11.811 | 0.21876 | 1.143 | Industrial Grade | Unshielded, 600V | 19924 | 552
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 7 | TS | TS | 12.446 | 0.22174 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 816-07 | 205
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 7 | TS | TP | 11.303 | 0.2009 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 222070 | 363
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 7 | TS | TP | 11.303 | 0.2009 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202070 | 370
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 7 | TS | TS | 14.7828 | 0.30061 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378790 | 1132
GENERIC | GENERIC | TP | TP | 16 | 8 | TP | TP | 11.049 | 0.20388 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2083 | 416
GENERIC | GENERIC | TS | TS | 16 | 8 | TS | TP | 12.319 | 0.22769 | 1.143
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 8 | TS | TP | 12.319 | 0.22769 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 222080 | 364
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 8 | TS | TP | 12.319 | 0.22769 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202080 | 371
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 8 | TS | TS | 16.891 | 0.37204 | 1.524 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13423 | 714
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 8 | TS | TS | 17.78 | 0.41371 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N7013 | 1506
GENERIC | GENERIC | TP | TP | 16 | 9 | TP | TP | 11.938 | 0.22769 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 9 | TS | TS | 15.24 | 0.30954 | 1.524
Draka | 15-10 Control Cable | PE | PVC | 16 | 9 | TP | TP | 13.081 | 0.22769 | 1.143 | Industrial Grade | Unshielded, 600V, 75°C | 71090 | 134
Draka | Power & Control TFN | PVC | PVC | 16 | 9 | TP | TP | 11.938 | 0.22769 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2093 | 417
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 9 | TS | TP | 15.875 | 0.25596 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 222090 | 365
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 9 | TS | TP | 13.335 | 0.25596 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 202090 | 372
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 9 | TS | TS | 15.24 | 0.30954 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 816-09 | 754
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 9 | TS | TS | 16.8402 | 0.40776 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378800 | 1133
GENERIC | GENERIC | TP | TP | 16 | 10 | TP | TP | 12.827 | 0.25001 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2103 | 418
GENERIC | GENERIC | TS | TS | 16 | 10 | TS | TP | 15.113 | 0.31251 | 1.524
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 10 | TS | TP | 15.113 | 0.31251 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222100 | 937
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 10 | TS | TP | 15.113 | 0.31251 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202100 | 946
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 10 | TS | TS | 18.034 | 0.4018 | 2.413 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13425 | 1501
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 10 | TS | TS | 19.177 | 0.44496 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N7015 | 1507
GENERIC | GENERIC | TP | TP | 16 | 11 | TP | TP | 13.208 | 0.27233 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2113 | 419
GENERIC | GENERIC | TP | TP | 16 | 12 | TP | TP | 13.208 | 0.2887 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 12 | TS | TS | 17.018 | 0.39139 | 1.524
Draka | Power & Control TFN | PVC | PVC | 16 | 12 | TP | TP | 13.208 | 0.2887 | 1.143 | Industrial Grade | Unshielded, 600V, 90°C | 2123 | 420
Draka | 15-10 Control Cable | PE | PVC | 16 | 12 | TP | TP | 15.24 | 0.31847 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 71120 | 660
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 12 | TS | TS | 15.875 | 0.36162 | 1.524 | Industrial Grade | Unshielded, 600V | 19925 | 1152
Draka | AUTO-FLEX® CF Type TC cont. flex control | XLPO | PVC | 16 | 12 | TS | TP | 15.113 | 0.33335 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 25957 | 740
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 12 | TS | TS | 17.018 | 0.39139 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 816-12 | 755
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 12 | TS | TP | 15.494 | 0.36311 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222120 | 938
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 12 | TS | TP | 15.494 | 0.36311 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202120 | 947
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 12 | TS | TS | 19.685 | 0.50895 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N7016 | 1508
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 12 | TS | TS | 19.304 | 0.47324 | 2.794 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13426 | 1515
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 12 | TS | TS | 18.6944 | 0.49853 | 1.524 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378810 | 1134
GENERIC | GENERIC | TP | TP | 16 | 13 | TP | TP | 14.732 | 0.34674 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2133 | 1014
GENERIC | GENERIC | TP | TP | 16 | 14 | TP | TP | 14.732 | 0.36311 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2143 | 1015
GENERIC | GENERIC | TS | TS | 16 | 14 | TS | TS | 20.574 | 0.56848 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N7918 | 1509
GENERIC | GENERIC | TP | TP | 16 | 15 | TP | TP | 15.494 | 0.39139 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 15 | TS | TP | 17.145 | 0.43454 | 1.524
Draka | 15-10 Control Cable | PE | PVC | 16 | 15 | TP | TP | 16.891 | 0.38395 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 71150 | 661
Draka | Power & Control TFN | PVC | PVC | 16 | 15 | TP | TP | 15.494 | 0.39139 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2153 | 1016
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 15 | TS | TP | 17.145 | 0.43454 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222150 | 939
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 15 | TS | TP | 17.145 | 0.43454 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202150 | 948
GENERIC | GENERIC | TP | TP | 16 | 16 | TP | TP | 15.494 | 0.40627 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 16 | TS | TP | 17.145 | 0.45091 | 1.524
Draka | AUTO-FLEX® CF Type TC cont. flex control | XLPO | PVC | 16 | 16 | TS | TP | 16.637 | 0.41966 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 25958 | 741
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 16 | TS | TP | 17.145 | 0.45091 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222160 | 940
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 16 | TS | TP | 17.145 | 0.45091 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202160 | 949
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 16 | TS | TS | 21.463 | 0.61908 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N5134 | 1510
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 16 | TS | TS | 21.082 | 0.59527 | 2.794 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13428 | 1516
GENERIC | GENERIC | TP | TP | 16 | 17 | TP | TP | 16.256 | 0.42859 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2173 | 1018
GENERIC | GENERIC | TP | TP | 16 | 18 | TP | TP | 16.256 | 0.44645 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2183 | 1019
GENERIC | GENERIC | TP | TP | 16 | 19 | TP | TP | 16.256 | 0.46282
GENERIC | GENERIC | TS | TS | 16 | 19 | TS | TS | 18.796 | 0.53127 | 1.524
Draka | 15-10 Control Cable | PE | PVC | 16 | 19 | TP | TP | 17.78 | 0.46133 | 1.524 | Industrial Grade | Unshielded, 600V, 75°C | 71190 | 662
Draka | Power & Control TFN | PVC | PVC | 16 | 19 | TP | TP | 16.256 | 0.46282 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2193 | 1020
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 19 | TS | TS | 18.796 | 0.53127 | 1.524 | Industrial Grade | Unshielded, 600V | 19926 | 1153
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 19 | TS | TS | 19.812 | 0.56699 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 816-19 | 756
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 19 | TS | TP | 18.034 | 0.50895 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222190 | 941
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 19 | TS | TP | 18.034 | 0.50895 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202190 | 950
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 19 | TS | TS | 22.5552 | 0.77236 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378820 | 1453
GENERIC | GENERIC | TP | TP | 16 | 20 | TP | TP | 17.145 | 0.4658 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 20 | TS | TS | 20.701 | 0.59675 | 1.524
Draka | Control Cable Multiconductor XLPE ins | XLPE | XLPO | 16 | 20 | TS | TS | 20.701 | 0.59675 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 816-20 | 757
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 20 | TS | TP | 19.05 | 0.52383 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222200 | 942
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 20 | TS | TP | 19.05 | 0.52383 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202200 | 951
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 20 | TS | TS | 23.495 | 0.75301 | 2.413 | Industrial Grade | Unshielded, 600V, 90°C | N7017 | 1511
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 20 | TS | TS | 23.622 | 0.74408 | 3.175 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13429 | 1532
GENERIC | GENERIC | TP | TP | 16 | 21 | TP | TP | 17.145 | 0.48217 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2213 | 1022
GENERIC | GENERIC | TP | TP | 16 | 22 | TP | TP | 18.034 | 0.49853 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2223 | 1023
GENERIC | GENERIC | TS | TP | 16 | 22 | TS | TP | 19.05 | 0.56104 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 25959 | 742
GENERIC | GENERIC | TP | TP | 16 | 23 | TP | TP | 18.034 | 0.51788 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2233 | 1024
GENERIC | GENERIC | TP | TP | 16 | 24 | TP | TP | 18.796 | 0.54616 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2243 | 1025
GENERIC | GENERIC | TS | TS | 16 | 24 | TS | TS | 22.098 | 0.68456 | 2.032
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 24 | TS | TS | 22.098 | 0.68456 | 2.032 | Industrial Grade | Unshielded, 600V | 25791 | 1469
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 24 | TS | TP | 20.955 | 0.6161 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222240 | 943
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 24 | TS | TP | 20.955 | 0.6161 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202240 | 952
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 24 | TS | TS | 26.416 | 0.95242 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7018 | 1519
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 24 | TS | TS | 26.67 | 0.94796 | 3.556 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13430 | 1547
GENERIC | GENERIC | TP | TP | 16 | 25 | TP | TP | 19.05 | 0.56253 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2253 | 1026
GENERIC | GENERIC | TS | TS | 16 | 25 | TS | TS | 25.7556 | 0.95838 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378830 | 1454
Draka | Power & Control TFN | PVC | PVC | 16 | 25 | TP | TP | 19.05 | 0.56253 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2253 | 1026
Draka | 15-10 Control Cable | PE | PVC | 16 | 25 | TP | TP | 22.352 | 0.59378 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 71250 | 1202
GENERIC | GENERIC | TP | TP | 16 | 26 | TP | TP | 19.05 | 0.58634 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2263 | 1027
GENERIC | GENERIC | TS | TP | 16 | 26 | TS | TP | 21.59 | 0.65777 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222260 | 944
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 26 | TS | TP | 21.59 | 0.65777 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222260 | 944
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 26 | TS | TP | 21.59 | 0.65777 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202260 | 953
GENERIC | GENERIC | TP | TP | 16 | 27 | TP | TP | 19.05 | 0.60122 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2273 | 1028
GENERIC | GENERIC | TS | TP | 16 | 27 | TS | TP | 21.59 | 0.67414 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222270 | 945
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 27 | TS | TS | 22.987 | 0.77533 | 2.032 | Industrial Grade | Unshielded, 600V | 28763 | 1470
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 27 | TS | TP | 21.59 | 0.67414 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 222270 | 945
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 27 | TS | TP | 21.59 | 0.67414 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 202270 | 954
GENERIC | GENERIC | TP | TP | 16 | 28 | TP | TP | 19.939 | 0.62503 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2283 | 1029
GENERIC | GENERIC | TP | TP | 16 | 29 | TP | TP | 19.939 | 0.64289 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2293 | 1030
GENERIC | GENERIC | TP | TP | 16 | 30 | TP | TP | 19.939 | 0.65777 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 30 | TS | TS | 27.3304 | 1.1995 | 2.032
Draka | Power & Control TFN | PVC | PVC | 16 | 30 | TP | TP | 19.939 | 0.65777 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2303 | 1031
Draka | 15-10 Control Cable | PE | PVC | 16 | 30 | TP | TP | 23.241 | 0.72027 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 71300 | 1203
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 30 | TS | TP | 23.368 | 0.79319 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 222300 | 1345
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 30 | TS | TP | 23.368 | 0.79319 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202300 | 1347
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 30 | TS | TS | 29.591 | 1.2248 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | N7019 | 1520
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 30 | TS | TS | 30.48 | 1.2054 | 3.937 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | A13431 | 1553
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 30 | TS | TS | 27.3304 | 1.1995 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378840 | 1455
GENERIC | GENERIC | TP | TP | 16 | 31 | TP | TP | 21.082 | 0.68456 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2313 | 1032
GENERIC | GENERIC | TS | TP | 16 | 31 | TS | TP | 23.114 | 0.86314 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 25960 | 1237
GENERIC | GENERIC | TP | TP | 16 | 32 | TP | TP | 21.082 | 0.69944 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2323 | 1033
GENERIC | GENERIC | TS | TS | 16 | 32 | TS | TS | 24.638 | 0.89141 | 2.032 | Industrial Grade | Unshielded, 600V | 25792 | 1471
Draka | Power & Control TFN | PVC | PVC | 16 | 32 | TP | TP | 21.082 | 0.69944 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2323 | 1033
GENERIC | GENERIC | TP | TP | 16 | 33 | TP | TP | 21.082 | 0.71878 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 2333 | 1034
GENERIC | GENERIC | TP | TP | 16 | 34 | TP | TP | 21.463 | 0.74111 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 2343 | 1380
GENERIC | GENERIC | TP | TP | 16 | 35 | TP | TP | 21.463 | 0.75748 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 2353 | 1381
GENERIC | GENERIC | TP | TP | 16 | 36 | TP | TP | 21.463 | 0.77385 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 2363 | 1382
GENERIC | GENERIC | TS | TS | 16 | 36 | TS | TS | 33.528 | 1.5596 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7020 | 1537
Draka | BOSTFLEX™ pendant & reel control | TS | TS | 16 | 36 | TS | TS | 33.528 | 1.5596 | 3.175 | Industrial Grade | Unshielded, 600V, 90°C | N7020 | 1537
Draka | ALL-TEMP INDUSTRITE® Type SOW Control | EPDM | EPDM | 16 | 36 | TS | TS | 34.671 | 1.5968 | 4.318 | Industrial Grade | Unshielded, 600V, +105°C to -55°C | 24908 | 1557
GENERIC | GENERIC | TP | TP | 16 | 37 | TP | TP | 21.463 | 0.79022 | 2.032
GENERIC | GENERIC | TS | TS | 16 | 37 | TS | TS | 26.416 | 0.99856 | 2.032
Draka | 15-10 Control Cable | PE | PVC | 16 | 37 | TP | TP | 24.892 | 0.88546 | 2.032 | Industrial Grade | Unshielded, 600V, 75°C | 71370 | 1204
Draka | Power & Control TFN | PVC | PVC | 16 | 37 | TP | TP | 21.463 | 0.79022 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 2373 | 1383
American Insulated Wire | XL-40™ Control | XLPO | CSPE | 16 | 37 | TS | TS | 26.416 | 0.99856 | 2.032 | Industrial Grade | Unshielded, 600V | 30350 | 1472
Draka | General Purpose Control XLPE | XLPE | CPE | 16 | 37 | TS | TP | 24.892 | 0.93457 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 222370 | 1346
Draka | General Purpose Control XLPE | XLPE | PVC | 16 | 37 | TS | TP | 24.892 | 0.93457 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 202370 | 1348
General Cable | Ultrol® 300 | XLPE | CSPE | 16 | 37 | TS | TS | 29.3116 | 1.4792 | 2.032 | Class 1E Nuclear | Overall Shield, 600V, Drain, 90°C | 378850 | 1456
GENERIC | GENERIC | TS | TP | 16 | 41 | TS | TP | 25.527 | 1.012 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 25961 | 1238
GENERIC | GENERIC | TS | TP | 16 | 60 | TS | TP | 29.337 | 1.4063 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 25962 | 1239

## Instrumentation (hidden)
Manufacturer | Cable Model | insul | jacket | AWG | #/C | Insulation Type | Jacket Type | OD mm | Kg/m | Jkt (mm) | # PAIR | # TRIAD | Grade | Comments | Part # | Item #
GENERIC | GENERIC | TP | TP | 10 | 2 | TP | TP | 10.922 | 0.21132 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 28091 | 431 | AWG | #/C | AWG | 10 | 12 | 14 | 16 | 18 | 20 | 22
GENERIC | GENERIC | TP | TP | 10 | 3 | TP | TP | 11.557 | 0.27085 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 28092 | 432 | 10 | 2 |  | 2 | 2 | 2 | 2 | 2 | 2 | 2
GENERIC | GENERIC | TP | TP | 10 | 4 | TP | TP | 12.7 | 0.33781 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 27923 | 433 | 12 | 3 |  | 3 | 3 | 3 | 3 | 3 | 3 | 3
GENERIC | GENERIC | TP | TP | 10 | 5 | TP | TP | 16.129 | 0.42264 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31325 | 699 | 14 | 4 |  | 4 | 4 | 4 | 4 | 4 | 4 | 4
GENERIC | GENERIC | TP | TP | 10 | 6 | TP | TP | 17.399 | 0.49407 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 36849 | 700 | 16 | 5 |  | 5 | 5 | 5 | 5 | 5 | 5 | 5
GENERIC | GENERIC | TP | TP | 10 | 15 | TP | TP | 25.019 | 1.1608 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31326 | 701 | 18 | 6 |  | 6 | 7 | 6 | 6 | 6 | 6 | 6
GENERIC | GENERIC | TP | TP | 10 | 30 | TP | TP | 32.766 | 2.1861 | 2.032 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31327 | 846 | 20 | 7 |  | 15 | 13 | 7 | 7 | 7 | 7 | 7
GENERIC | GENERIC | TP | TP | 12 | 2 | TP | TP | 9.271 | 0.15923 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18494 | 434 | 22 | 8 |  | 30 | 15 | 12 | 8 | 8 | 8 | 9
GENERIC | GENERIC | TP | TP | 12 | 3 | TP | TP | 9.779 | 0.19048 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31089 | 435 |  | 9 |  |  | 30 | 13 | 9 | 9 | 9 | 12
GENERIC | GENERIC | TP | TP | 12 | 4 | TP | TP | 10.668 | 0.23811 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18499 | 436 |  | 10 |  |  |  | 15 | 10 | 10 | 12 | 16
GENERIC | GENERIC | TP | TP | 12 | 5 | TP | TP | 13.208 | 0.29019 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 24683 | 437 |  | 11 |  |  |  | 24 | 11 | 11 | 16 | 19
GENERIC | GENERIC | TP | TP | 12 | 7 | TP | TP | 14.986 | 0.36162 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18502 | 702 |  | 12 |  |  |  | 30 | 12 | 12 | 19 | 25
GENERIC | GENERIC | TP | TP | 12 | 13 | TP | TP | 19.177 | 0.64438 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 36848 | 703 |  | 13 |  |  |  | 35 | 13 | 13 | 24 | 37
GENERIC | GENERIC | TP | TP | 12 | 15 | TP | TP | 20.32 | 0.72325 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31271 | 704 |  | 14 |  |  |  |  | 14 | 14 | 25 | 40
GENERIC | GENERIC | TP | TP | 12 | 30 | TP | TP | 27.432 | 1.4405 | 2.032 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31272 | 847 |  | 15 |  |  |  |  | 15 | 15 | 32 | 50
GENERIC | GENERIC | TP | TP | 14 | 2 | TP | TP | 6.7564 | 0.07292 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181402C6 | 70 |  | 16 |  |  |  |  | 16 | 16 | 36
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 14 | 2 | TP | TP | 8.255 | 0.12649 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18248 | 438 |  | 17 |  |  |  |  | 17 | 17 | 40
Cable USA | ETFE TYPE TC | ETFE | ETFE | 14 | 2 | TP | TP | 6.7564 | 0.07292 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181402C6 | 70 |  | 18 |  |  |  |  | 18 | 18 | 48
GENERIC | GENERIC | TP | TP | 14 | 3 | TP | TP | 8.636 | 0.15179 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18250 | 439 |  | 19 |  |  |  |  | 19 | 19 | 60
GENERIC | GENERIC | TP | TP | 14 | 4 | TP | TP | 9.398 | 0.18156 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18253 | 440 |  | 21 |  |  |  |  | 21 | 21 | 72
GENERIC | GENERIC | TP | TP | 14 | 5 | TP | TP | 11.811 | 0.2143 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31124 | 441 |  | 24 |  |  |  |  | 24 | 24 | 100
GENERIC | GENERIC | TP | TP | 14 | 6 | TP | TP | 12.7 | 0.24108 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 35910 | 442 |  | 25 |  |  |  |  | 25 | 25 | 108
GENERIC | GENERIC | TP | TP | 14 | 7 | TP | TP | 12.7 | 0.026787 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18256 | 443 |  | 27 |  |  |  |  | 27 | 27
GENERIC | GENERIC | TP | TP | 14 | 12 | TP | TP | 16.51 | 0.43306 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 23168 | 705 |  | 30 |  |  |  |  | 30 | 30
GENERIC | GENERIC | TP | TP | 14 | 13 | TP | TP | 16.891 | 0.4658 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 36847 | 706 |  | 32 |  |  |  |  | 32 | 32
GENERIC | GENERIC | TP | TP | 14 | 15 | TP | TP | 18.034 | 0.53574 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31125 | 707 |  | 35 |  |  |  |  | 36 | 36
GENERIC | GENERIC | TP | TP | 14 | 24 | TP | TP | 22.225 | 0.80063 | 2.032 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 32248 | 848 |  | 36 |  |  |  |  | 37 | 37
GENERIC | GENERIC | TP | TP | 14 | 30 | TP | TP | 24.257 | 1.0358 | 2.032 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 31126 | 849 |  | 37 |  |  |  |  | 38 | 38
GENERIC | GENERIC | TP | TP | 14 | 35 | TP | TP | 25.527 | 1.1697 | 2.032 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 29558 | 850 |  | 38 |  |  |  |  | 40 | 40
GENERIC | GENERIC | TP | TP | 16 | 2 | TP | TS | 7.366 | 0.075896 | 1.143 | [7 empty] | 40 |  |  |  |  | 48 | 48
GENERIC | GENERIC | TS | TS | 16 | 2 | Sil | Fiber | 9.398 | 0.074408 | 1.016 | [7 empty] | 48 |  |  |  |  | 60 | 60
American Insulated Wire | American SDN® | PVC | CP | 16 | 2 | TP | TS | 7.366 | 0.075896 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38486 | 289 |  | 50 |  |  |  |  | 72 | 72
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 2 | TP | TP | 7.62 | 0.092266 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18114 | 444 |  | 60 |  |  |  |  | 74 | 74
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 2 | TP | TP | 5.9944 | 0.053574 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181602C6 | 71 |  | 72 |  |  |  |  | 100 | 100
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 2 | TP | TP | 7.4168 | 0.092266 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181602C6 | 346 |  | 74 |  |  |  |  | 108 | 108
General Cable | 20/10 | PE | PVC | 16 | 2 | TP | TP | 8.128 | 0.07292 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365360 | 276 |  | 100
General Cable | VNTC® | PVC | PVC | 16 | 2 | TP | TP | 7.62 | 0.074408 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 245580 | 477 |  | 108
General Cable | VNTC® | PVC | PVC | 16 | 2 | TP | TP | 7.62 | 0.077385 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 247620 | 478
General Cable | VNTC® CAROLFIRE | PVC | PVC | 16 | 2 | TP | TP | 7.62 | 0.075896 | 1.143 |  |  | Industrial Grade | Shielded, 600V, UL Type TC, Overall Shielded Pairs/Triads | 230830 | 506
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 2 | TP | TP | 6.9342 | 0.066967 | 1.016 | 1 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325770 | 257
Okonite | Okozel® | ETFE | ETFE | 16 | 2 | TP | TP | 5.588 | 0.055062 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3252 | 52
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 2 | TS | TS | 7.112 | 0.063991 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-02 | 88
General Cable | CHTC® | XLPE | CSPE | 16 | 2 | TS | TS | 8.636 | 0.090778 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 241420 | 317
General Cable | EHTC® | EPR | CSPE | 16 | 2 | TS | TS | 8.128 | 0.081849 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343460 | 327
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 2 | TS | TS | 7.8486 | 0.080361 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377680 | 464
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 2 | TS | TS | 8.763 | 0.090778 | 1.143 | 1 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 240990 | 322
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 2 | TS | TP | 8.128 | 0.077385 | 1.143 | 1 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 314960 | 408
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 2 | TS | TS | 8.382 | 0.10417 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2032 | 398
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 2 | TS | TS | 10.668 | 0.12501 | 1.143 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2052 | 399
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 2 | TS | TS | 9.144 | 0.11459 | 1.143 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2032 | 415
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 2 | TS | TS | 11.938 | 0.19048 | 1.143 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2052 | 420
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 2 | TS | TS | 17.018 | 0.36906 | 1.524 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6052 | 643
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 2 | TS | TS | 17.018 | 0.3899 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6052 | 654
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 2 | TS | TS | 6.858 | 0.059527 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0020 | 101
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 2 | TS | TS | 6.858 | 0.066967 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0021 | 102
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 2 | Sil | Fiber | 9.144 | 0.074408 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3301 | 148
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 2 | Sil | Fiber | 9.398 | 0.074408 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3327 | 149
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 2 | TS | TS | 7.874 | 0.096731 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0020 | 361
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 2 | TS | TS | 7.874 | 0.096731 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-0021 | 362
Rockbestus-Sup | CAROLFIRE | XLPE | CSPE | 16 | 2 | TS | TS | 7.874 | 0.096731 | 1.143 |  |  |  |  | I46-0021 | 315
GENERIC | GENERIC | TP | TP | 16 | 3 | TP | TS | 7.747 | 0.092266 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 3 | TS | TS | 9.144 | 0.10864 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 16 | 3 | TP | TS | 7.747 | 0.092266 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38487 | 290
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 3 | TP | TP | 8.001 | 0.11905 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18118 | 445
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 3 | TP | TP | 7.874 | 0.098219 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 68104 | 458
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 3 | TP | TP | 6.35 | 0.071432 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181603C6 | 72
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 3 | TP | TP | 7.8232 | 0.12054 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181603C6 | 347
Dekoron | 1735 | PE | PVC | 16 | 3 | TP | TP | 8.9408 | 0.096731 | 1.143 |  |  | Industrial Grade | 600V |  | 272
General Cable | 20/10 | PE | PVC | 16 | 3 | TP | TP | 8.636 | 0.092266 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365370 | 277
General Cable | VNTC® | PVC | PVC | 16 | 3 | TP | TP | 8.001 | 0.08929 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236170 | 479
General Cable | VNTC® | PVC | PVC | 16 | 3 | TP | TP | 8.128 | 0.093754 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 261160 | 480
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 3 | TP | TP | 7.5438 | 0.086314 | 1.0668 |  | 1 | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325780 | 268
Okonite | Okozel® | ETFE | ETFE | 16 | 3 | TP | TP | 6.096 | 0.071432 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3253 | 53
Okonite | P-30 | PE | PVC | 16 | 3 | TP | TP | 8.636 | 0.095242 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2053 | 423
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 3 | TS | TS | 7.62 | 0.083337 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-03 | 89
General Cable | CHTC® | XLPE | CSPE | 16 | 3 | TS | TS | 9.144 | 0.10864 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 312500 | 318
General Cable | EHTC® | EPR | CSPE | 16 | 3 | TS | TS | 8.636 | 0.10268 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343470 | 328
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 3 | TS | TS | 8.255 | 0.098219 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377690 | 465
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 3 | TS | TS | 9.144 | 0.12649 | 1.143 |  | 1 | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 241510 | 323
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 3 | TS | TP | 8.509 | 0.098219 | 1.143 |  | 1 | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 279690 | 409
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 3 | TS | TS | 8.89 | 0.12203 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2033 | 400
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 3 | TS | TS | 11.176 | 0.14733 | 1.143 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2053 | 401
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 3 | TS | TS | 10.16 | 0.14584 | 1.143 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2033 | 416
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 3 | TS | TS | 12.446 | 0.19644 | 1.143 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2053 | 421
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 3 | TS | TS | 17.018 | 0.38246 | 1.524 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6053 | 644
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 3 | TS | TS | 17.018 | 0.4018 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6053 | 655
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 3 | TS | TS | 7.366 | 0.081849 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0030 | 103
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 3 | TS | TS | 7.366 | 0.08929 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0031 | 104
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 3 | Sil | Fiber | 9.652 | 0.096731 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3302 | 150
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 3 | Sil | Fiber | 9.906 | 0.096731 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3328 | 151
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 3 | TS | TS | 8.382 | 0.11905 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0030 | 363
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 3 | TS | TS | 8.382 | 0.12054 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-0031 | 364
GENERIC | GENERIC | TP | TP | 16 | 4 | TP | TS | 8.382 | 0.11459 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 4 | TS | TS | 11.176 | 0.13393 | 0.889 | 2
American Insulated Wire | American SDN® | PVC | CP | 16 | 4 | TP | TS | 8.382 | 0.11459 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38488 | 291
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 4 | TP | TP | 8.636 | 0.13989 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18121 | 446
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 4 | TP | TP | 8.509 | 0.11756 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 68105 | 459
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 4 | TP | TP | 6.9088 | 0.08929 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181604C6 | 73
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 4 | TP | TP | 8.4328 | 0.14733 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181604C6 | 348
General Cable | 20/10 | PE | PVC | 16 | 4 | TP | TP | 9.398 | 0.11459 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 647530 | 278
General Cable | VNTC® | PVC | PVC | 16 | 4 | TP | TP | 8.636 | 0.11012 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236180 | 481
General Cable | VNTC® | PVC | PVC | 16 | 4 | TP | TP | 8.89 | 0.11459 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243710 | 482
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 4 | TP | TP | 8.7884 | 0.11905 | 1.0668 | 2 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 325800 | 263
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 4 | TP | TP | 8.7376 | 0.11012 | 1.0668 | 2 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325790 | 267
Okonite | Okozel® | ETFE | ETFE | 16 | 4 | TP | TP | 6.604 | 0.090778 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3254 | 54
Okonite | P-30 | PE | PVC | 16 | 4 | TP | TP | 9.398 | 0.11756 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2054 | 424
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 4 | TS | TS | 8.255 | 0.10566 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-04 | 90
General Cable | CHTC® | XLPE | CSPE | 16 | 4 | TS | TS | 9.906 | 0.13542 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 312510 | 319
General Cable | EHTC® | EPR | CSPE | 16 | 4 | TS | TS | 9.271 | 0.12649 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343480 | 329
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 4 | TS | TS | 8.9662 | 0.12054 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377700 | 466
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 4 | TS | TP | 11.557 | 0.14286 | 0.381 | 2 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343240 | 34
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 4 | TS | TP | 11.684 | 0.14138 | 1.143 | 2 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 283170 | 410
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 4 | TS | TS | 14.859 | 0.19346 | 1.524 | 2 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 241010 | 583
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 4 | TS | TS | 9.652 | 0.14584 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2034 | 402
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 4 | TS | TS | 12.192 | 0.18602 | 1.143 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2054 | 403
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 4 | TS | TS | 10.922 | 0.16221 | 1.143 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2034 | 417
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 4 | TS | TS | 13.462 | 0.24406 | 1.143 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2054 | 422
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 4 | TS | TS | 17.018 | 0.38841 | 1.524 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6054 | 645
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 4 | TS | TS | 17.018 | 0.40925 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6054 | 656
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 4 | TS | TS | 7.874 | 0.096731 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0040 | 105
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 4 | TS | TS | 7.874 | 0.10417 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0041 | 106
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 4 | Sil | Fiber | 10.668 | 0.12649 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3303 | 152
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 4 | Sil | Fiber | 10.922 | 0.13393 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3329 | 153
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 4 | TS | TS | 9.144 | 0.14138 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0040 | 365
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 4 | TS | TS | 9.144 | 0.14882 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I463433 | 366
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 4 | TS | TS | 10.414 | 0.11161 | 0.889 | 2 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0025 | 115
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 4 | TS | TS | 11.176 | 0.13393 | 0.889 | 2 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0026 | 118
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 4 | TS | TS | 11.43 | 0.14138 | 0.889 | 2 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0024 | 120
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 4 | Sil | Fiber | 14.224 | 0.15626 | 1.016 | 2 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3351 | 170
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 4 | Sil | Fiber | 15.494 | 0.17858 | 1.016 | 2 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3371 | 180
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 4 | Sil | Fiber | 15.494 | 0.18602 | 1.016 | 2 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3266 | 190
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 4 | TS | TS | 11.938 | 0.2009 | 1.143 | 2 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-0041 | 373
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 4 | TS | TS | 12.954 | 0.23811 | 1.143 | 2 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-0042 | 375
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 4 | TS | TS | 12.954 | 0.24555 | 1.143 | 2 |  | Class 1E Nuclear | Multi-Shielded Pairs w Overall Shield, 90°C, 600V, UL Type TC | I46-5700 | 376
GENERIC | GENERIC | TP | TP | 16 | 5 | TP | TP | 9.271 | 0.13989 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 5 | TS | TS | 10.668 | 0.1637 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 16 | 5 | TP | TS | 9.144 | 0.13691 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38489 | 292
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 5 | TP | TP | 10.541 | 0.16221 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18123 | 447
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 5 | TP | TP | 9.271 | 0.13989 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 68106 | 460
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 5 | TP | TP | 7.5692 | 0.10864 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181605C6 | 74
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 5 | TP | TP | 9.1694 | 0.17263 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181605C6 | 349
Dekoron | 1735 | PE | PVC | 16 | 5 | TP | TP | 10.4902 | 0.1384 | 1.143 |  |  | Industrial Grade | 600V |  | 273
General Cable | 20/10 | PE | PVC | 16 | 5 | TP | TP | 10.16 | 0.13691 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 283540 | 279
General Cable | VNTC® | PVC | PVC | 16 | 5 | TP | TP | 9.398 | 0.13542 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 266580 | 483
General Cable | VNTC® | PVC | PVC | 16 | 5 | TP | TP | 9.398 | 0.14435 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236190 | 484
Okonite | Okozel® | ETFE | ETFE | 16 | 5 | TP | TP | 7.112 | 0.11012 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3255 | 55
Okonite | P-30 | PE | PVC | 16 | 5 | TP | TP | 10.414 | 0.14286 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2055 | 425
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 5 | TS | TS | 9.144 | 0.12649 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-05 | 91
General Cable | CHTC® | XLPE | CSPE | 16 | 5 | TS | TS | 10.668 | 0.1637 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 312520 | 320
General Cable | EHTC® | EPR | CSPE | 16 | 5 | TS | TS | 10.16 | 0.15179 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343490 | 330
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 5 | TS | TS | 9.7536 | 0.14435 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377710 | 467
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 5 | TS | TS | 10.414 | 0.16965 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2035 | 404
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 5 | TS | TS | 13.462 | 0.23067 | 1.143 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2055 | 405
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 5 | TS | TS | 11.684 | 0.189 | 1.143 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2035 | 418
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 5 | TS | TS | 17.526 | 0.40478 | 1.524 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6055 | 646
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 5 | TS | TS | 17.018 | 0.4152 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6055 | 657
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 5 | TS | TS | 15.494 | 0.31251 | 1.524 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2055 | 669
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 5 | TS | TS | 8.636 | 0.11905 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0050 | 107
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 5 | TS | TS | 9.398 | 0.14138 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0051 | 108
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 5 | Sil | Fiber | 11.684 | 0.15626 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3304 | 154
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 5 | Sil | Fiber | 12.446 | 0.1637 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3330 | 155
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 5 | TS | TS | 9.906 | 0.17114 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0050 | 367
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 5 | TS | TS | 10.668 | 0.2009 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-3444 | 368
GENERIC | GENERIC | TP | TP | 16 | 6 | TP | TS | 9.906 | 0.15923 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 6 | TS | TS | 12.7 | 0.24555 | 1.143 | 3
American Insulated Wire | American SDN® | PVC | CP | 16 | 6 | TP | TS | 9.906 | 0.15923 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38490 | 293
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 6 | TP | TP | 11.303 | 0.18453 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 24656 | 448
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 6 | TP | TP | 9.3218 | 0.15477 | 1.016 |  | 2 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340020 | 252
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 6 | TS | TS | 11.176 | 0.14882 | 0.889 | 3 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0035 | 116
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 6 | TS | TS | 11.938 | 0.17858 | 0.889 | 3 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0036 | 119
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 6 | TS | TS | 12.192 | 0.18602 | 0.889 | 3 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0034 | 121
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 6 | Sil | Fiber | 15.24 | 0.2009 | 1.016 | 3 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3352 | 171
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 6 | Sil | Fiber | 16.51 | 0.23811 | 1.016 | 3 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3372 | 181
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 6 | Sil | Fiber | 16.51 | 0.24555 | 1.016 | 3 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3267 | 191
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 6 | TS | TS | 12.7 | 0.24555 | 1.143 | 3 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3462 | 374
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 6 | TS | TS | 14.478 | 0.31996 | 1.524 | 3 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-3485 | 615
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 6 | TS | TS | 14.478 | 0.3274 | 1.524 | 3 |  | Class 1E Nuclear | Multi-Shielded Pairs w Overall Shield, 90°C, 600V, UL Type TC | I46-5701 | 619
GENERIC | GENERIC | TP | TP | 16 | 7 | TP | TP | 10.16 | 0.16519 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 7 | TS | TS | 11.684 | 0.20983 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 16 | 7 | TP | TS | 10.668 | 0.18304 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38491 | 294
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 7 | TP | TP | 11.303 | 0.19644 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 27339 | 449
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 7 | TP | TP | 10.033 | 0.1756 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 68107 | 461
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 7 | TP | TP | 8.2296 | 0.14286 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181607C6 | 75
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 7 | TP | TP | 9.906 | 0.22025 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181607C6 | 350
Dekoron | 1735 | PE | PVC | 16 | 7 | TP | TP | 11.3538 | 0.17709 | 1.143 |  |  | Industrial Grade | 600V |  | 274
General Cable | 20/10 | PE | PVC | 16 | 7 | TP | TP | 10.922 | 0.1756 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365380 | 280
General Cable | VNTC® | PVC | PVC | 16 | 7 | TP | TP | 10.16 | 0.16519 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236210 | 485
General Cable | VNTC® | PVC | PVC | 16 | 7 | TP | TP | 10.414 | 0.17709 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243740 | 486
Okonite | Okozel® | ETFE | ETFE | 16 | 7 | TP | TP | 7.874 | 0.14435 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3257 | 56
Okonite | P-30 | PE | PVC | 16 | 7 | TP | TP | 11.176 | 0.18156 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2057 | 426
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 7 | TS | TS | 9.906 | 0.16667 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-07 | 92
General Cable | CHTC® | XLPE | CSPE | 16 | 7 | TS | TS | 11.684 | 0.20983 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 241430 | 321
General Cable | EHTC® | EPR | CSPE | 16 | 7 | TS | TS | 10.922 | 0.189 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343500 | 331
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 7 | TS | TS | 10.5156 | 0.18453 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377720 | 468
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 7 | TS | TS | 11.43 | 0.2143 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2037 | 406
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 7 | TS | TS | 12.7 | 0.2262 | 1.143 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2037 | 419
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 7 | TS | TS | 18.542 | 0.47621 | 1.524 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6057 | 647
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 7 | TS | TS | 15.24 | 0.33186 | 1.524 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2057 | 649
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 7 | TS | TS | 17.018 | 0.43454 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6057 | 658
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 7 | TS | TS | 16.764 | 0.36906 | 1.524 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2057 | 670
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 7 | TS | TS | 9.398 | 0.15626 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0070 | 109
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 7 | TS | TS | 10.16 | 0.17858 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0071 | 110
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 7 | Sil | Fiber | 12.7 | 0.19346 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3306 | 156
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 7 | Sil | Fiber | 13.462 | 0.20834 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3332 | 157
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 7 | TS | TS | 10.668 | 0.19346 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0070 | 369
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 7 | TS | TS | 11.43 | 0.21578 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-3425 | 370
GENERIC | GENERIC | TP | TP | 16 | 8 | TP | TP | 12.192 | 0.22025 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 8 | TS | TS | 14.478 | 0.28275 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 16 | 8 | TP | TS | 11.43 | 0.20388 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38492 | 295
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 8 | TP | TP | 12.192 | 0.22025 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 27884 | 450
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 8 | TP | TP | 12.8524 | 0.22471 | 1.3462 | 4 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 325820 | 558
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 8 | TP | TP | 12.2174 | 0.19644 | 1.3462 | 4 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325810 | 559
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 8 | TS | TP | 13.462 | 0.23811 | 0.381 | 4 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343250 | 35
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 8 | TS | TS | 17.145 | 0.30359 | 1.524 | 4 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 232560 | 584
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 8 | TS | TP | 14.224 | 0.25448 | 1.524 | 4 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 283180 | 662
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 8 | TS | TS | 12.954 | 0.21578 | 0.889 | 4 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0045 | 117
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 8 | Sil | Fiber | 17.526 | 0.26787 | 1.016 | 4 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3353 | 172
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 8 | Sil | Fiber | 18.288 | 0.30507 | 1.016 | 4 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3373 | 182
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 8 | Sil | Fiber | 18.796 | 0.31996 | 1.016 | 4 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3268 | 192
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 8 | TS | TS | 13.716 | 0.24555 | 1.143 | 4 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0046 | 520
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 8 | TS | TS | 14.478 | 0.28275 | 1.143 | 4 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0044 | 525
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 8 | TS | TS | 15.24 | 0.35716 | 1.524 | 4 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3463 | 611
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 8 | TS | TS | 15.748 | 0.38692 | 1.524 | 4 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-0082 | 616
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 8 | TS | TS | 16.51 | 0.42413 | 1.524 | 4 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5844 | 620
GENERIC | GENERIC | TP | TP | 16 | 9 | TP | TP | 11.684 | 0.21876 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 9 | TS | TS | 14.351 | 0.29614 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 16 | 9 | TP | TS | 12.065 | 0.24555 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38631 | 296
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 9 | TP | TP | 12.954 | 0.24108 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18124 | 451
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 9 | TP | TP | 11.684 | 0.21876 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 68108 | 462
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 9 | TP | TP | 9.7028 | 0.18304 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181609C6 | 76
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 9 | TP | TP | 11.4554 | 0.27382 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181609C6 | 351
Dekoron | 1735 | PE | PVC | 16 | 9 | TP | TP | 13.081 | 0.22025 | 1.143 |  |  | Industrial Grade | 600V |  | 275
General Cable | 20/10 | PE | PVC | 16 | 9 | TP | TP | 12.7 | 0.22025 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365390 | 281
General Cable | VNTC® | PVC | PVC | 16 | 9 | TP | TP | 11.684 | 0.20983 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 243640 | 487
General Cable | VNTC® | PVC | PVC | 16 | 9 | TP | TP | 11.938 | 0.22322 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 243560 | 488
Okonite | Okozel® | ETFE | ETFE | 16 | 9 | TP | TP | 9.398 | 0.17412 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3259 | 57
Okonite | P-30 | PE | PVC | 16 | 9 | TP | TP | 12.954 | 0.23215 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2059 | 427
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 9 | TS | TS | 11.557 | 0.20983 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-09 | 93
General Cable | EHTC® | EPR | CSPE | 16 | 9 | TS | TS | 12.7 | 0.24108 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343510 | 332
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 9 | TS | TS | 12.2682 | 0.23215 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377730 | 469
General Cable | CHTC® | XLPE | CSPE | 16 | 9 | TS | TS | 14.351 | 0.29614 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 241440 | 582
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 9 | TS | TS | 13.208 | 0.2768 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2039 | 407
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 9 | TS | TS | 21.082 | 0.5789 | 1.524 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6059 | 648
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 9 | TS | TS | 17.78 | 0.41371 | 1.524 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2059 | 650
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 9 | TS | TS | 17.018 | 0.43752 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6059 | 659
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 9 | TS | TS | 15.24 | 0.32442 | 1.524 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2039 | 666
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 9 | TS | TS | 19.05 | 0.49109 | 1.524 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2059 | 671
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 9 | TS | TS | 10.922 | 0.19346 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0090 | 111
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 9 | TS | TS | 11.684 | 0.22322 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0091 | 112
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 9 | Sil | Fiber | 14.986 | 0.26043 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3308 | 158
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 9 | Sil | Fiber | 15.748 | 0.27531 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3334 | 159
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 9 | TS | TS | 12.446 | 0.23811 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0090 | 371
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 9 | TS | TS | 13.208 | 0.26787 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-3447 | 372
GENERIC | GENERIC | TP | TP | 16 | 10 | TP | TS | 12.319 | 0.24555 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 10 | TS | TS | 15.748 | 0.33484 | 1.143 | 5
American Insulated Wire | American SDN® | PVC | CP | 16 | 10 | TP | TS | 12.319 | 0.24555 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38484 | 297
General Cable | VNTC® | PVC | PVC | 16 | 10 | TP | TP | 12.573 | 0.22918 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236230 | 489
General Cable | EHTC® | EPR | CSPE | 16 | 10 | TS | TS | 14.351 | 0.29317 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343520 | 586
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 10 | Sil | Fiber | 19.05 | 0.3274 | 1.016 | 5 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3354 | 173
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 10 | Sil | Fiber | 20.066 | 0.37948 | 1.016 | 5 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3374 | 183
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 10 | Sil | Fiber | 20.828 | 0.4018 | 1.016 | 5 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3269 | 193
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 10 | TS | TS | 14.478 | 0.27531 | 1.143 | 5 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0055 | 516
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 10 | TS | TS | 14.986 | 0.29763 | 1.143 | 5 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0056 | 521
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 10 | TS | TS | 15.748 | 0.33484 | 1.143 | 5 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0054 | 526
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 10 | TS | TS | 16.51 | 0.42413 | 1.524 | 5 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3465 | 612
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 10 | TS | TS | 17.272 | 0.46133 | 1.524 | 5 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-3486 | 617
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 10 | TS | TS | 18.034 | 0.50598 | 1.524 | 5 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5985 | 621
GENERIC | GENERIC | TP | TP | 16 | 11 | TP | TS | 12.7 | 0.26787 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38792 | 298
GENERIC | GENERIC | TP | TP | 16 | 12 | TP | TP | 12.827 | 0.30061 | 1.143
GENERIC | GENERIC | TS | TS | 16 | 12 | TS | TS | 15.494 | 0.37055 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 16 | 12 | TP | TS | 12.7 | 0.27977 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38493 | 299
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 12 | TP | TP | 12.827 | 0.30061 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 68109 | 463
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 12 | TP | TP | 14.859 | 0.3274 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18126 | 708
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 12 | TP | TP | 10.8966 | 0.23662 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181612C6 | 77
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 12 | TP | TP | 12.8016 | 0.34674 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181612C6 | 352
Dekoron | 1735 | PE | PVC | 16 | 12 | TP | TP | 15.6718 | 0.314 | 1.524 |  |  | Industrial Grade | 600V |  | 560
General Cable | VNTC® | PVC | PVC | 16 | 12 | TP | TP | 12.827 | 0.26489 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236240 | 490
General Cable | VNTC® | PVC | PVC | 16 | 12 | TP | TP | 12.954 | 0.27531 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 229600 | 491
General Cable | 20/10 | PE | PVC | 16 | 12 | TP | TP | 14.986 | 0.31103 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 647550 | 561
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 12 | TP | TP | 12.7508 | 0.29019 | 1.27 |  | 4 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340030 | 551
Okonite | Okozel® | ETFE | ETFE | 16 | 12 | TP | TP | 10.668 | 0.23513 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3262 | 58
Okonite | P-30 | PE | PVC | 16 | 12 | TP | TP | 15.494 | 0.31698 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2062 | 673
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 12 | TS | TS | 13.843 | 0.30061 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-12 | 428
General Cable | EHTC® | EPR | CSPE | 16 | 12 | TS | TS | 14.986 | 0.32888 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343530 | 587
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 12 | TS | TS | 14.5034 | 0.32293 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377740 | 717
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 12 | TS | TS | 15.494 | 0.37055 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2042 | 651
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 12 | TS | TS | 19.812 | 0.50895 | 1.524 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2062 | 652
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 12 | TS | TS | 18.796 | 0.52979 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6062 | 660
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 12 | TS | TS | 16.764 | 0.39288 | 1.524 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2042 | 667
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 12 | TS | TS | 21.336 | 0.56699 | 1.524 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2062 | 672
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 12 | TS | TS | 24.13 | 0.76045 | 2.032 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6062 | 819
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 12 | TS | TS | 12.192 | 0.25299 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0120 | 113
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 12 | TS | TS | 12.954 | 0.28275 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0121 | 114
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 12 | Sil | Fiber | 16.764 | 0.3274 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3309 | 160
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 12 | Sil | Fiber | 17.526 | 0.34228 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3335 | 161
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 12 | TS | TS | 14.732 | 0.33484 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0120 | 603
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 12 | TS | TS | 15.494 | 0.37204 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-3449 | 604
GENERIC | GENERIC | TP | TS | 16 | 13 | TP | TS | 13.97 | 0.33484 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38793 | 564
American Insulated Wire | American SDN® | PVC | CP | 16 | 13 | TP | TS | 13.97 | 0.33484 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38793 | 564
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 13 | TP | TP | 15.24 | 0.35121 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18128 | 709
GENERIC | GENERIC | TP | TP | 16 | 14 | TP | TS | 13.97 | 0.35716 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 14 | TS | TS | 17.272 | 0.43157 | 1.143 | 7
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 14 | Sil | Fiber | 20.828 | 0.43157 | 1.016 | 7 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3355 | 174
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 14 | Sil | Fiber | 22.098 | 0.49853 | 1.016 | 7 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3375 | 184
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 14 | Sil | Fiber | 22.606 | 0.52086 | 1.016 | 7 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3270 | 194
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 14 | TS | TS | 15.748 | 0.34972 | 1.143 | 7 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0075 | 517
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 14 | TS | TS | 16.51 | 0.39436 | 1.143 | 7 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0076 | 522
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 14 | TS | TS | 17.272 | 0.43157 | 1.143 | 7 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0074 | 527
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 14 | TS | TS | 18.034 | 0.46133 | 1.524 | 7 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3466 | 613
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 14 | TS | TS | 18.796 | 0.51342 | 1.524 | 7 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-3232 | 618
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 14 | TS | TS | 19.558 | 0.55806 | 1.524 | 7 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5702 | 622
GENERIC | GENERIC | TP | TP | 16 | 15 | TP | TP | 14.859 | 0.36162 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 15 | TS | TS | 16.256 | 0.4018 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 16 | 15 | TP | TS | 14.859 | 0.37948 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38794 | 566
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 15 | TP | TP | 14.859 | 0.36162 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 68110 | 713
General Cable | VNTC® | PVC | PVC | 16 | 15 | TP | TP | 15.367 | 0.35567 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 244650 | 726
General Cable | EHTC® | EPR | CSPE | 16 | 15 | TS | TS | 16.256 | 0.4018 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343540 | 588
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 15 | Sil | Fiber | 18.796 | 0.40925 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3310 | 162
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 15 | Sil | Fiber | 19.558 | 0.43157 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3336 | 163
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 15 | TS | TS | 14.224 | 0.3274 | 1.143 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0150 | 508
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 15 | TS | TS | 14.986 | 0.35716 | 1.143 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0151 | 509
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 15 | TS | TS | 16.256 | 0.4018 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-3023 | 605
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 15 | TS | TS | 16.764 | 0.43901 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-3450 | 606
GENERIC | GENERIC | TP | TP | 16 | 16 | TP | TS | 14.859 | 0.38395 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 16 | TS | TP | 18.796 | 0.43752 | 1.524 | 8
American Insulated Wire | American SDN® | PVC | CP | 16 | 16 | TP | TS | 14.859 | 0.38395 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38494 | 567
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 16 | TP | TP | 12.1158 | 0.30507 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181616C6 | 78
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 16 | TP | TP | 14.9098 | 0.4777 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 181616C6 | 596
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 16 | TP | TP | 16.891 | 0.42859 | 1.524 | 8 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 298880 | 675
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 16 | TP | TP | 18.4404 | 0.38543 | 1.524 | 8 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339700 | 690
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 16 | TS | TP | 18.034 | 0.43603 | 0.381 | 8 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343260 | 36
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 16 | TS | TP | 18.796 | 0.43752 | 1.524 | 8 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337090 | 663
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 16 | TS | TS | 23.241 | 0.58634 | 2.032 | 8 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 241000 | 780
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 16 | TS | TS | 17.018 | 0.39436 | 1.143 | 8 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0085 | 518
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 16 | TS | TS | 17.78 | 0.44645 | 1.143 | 8 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0086 | 523
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 16 | TS | TS | 18.542 | 0.49109 | 1.143 | 8 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0084 | 528
GENERIC | GENERIC | TP | TS | 16 | 17 | TP | TS | 16.129 | 0.43157 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38795 | 568
GENERIC | GENERIC | TP | TS | 16 | 18 | TP | TS | 16.129 | 0.43157 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38796 | 569
GENERIC | GENERIC | TS | TS | 16 | 18 | Sil | Fiber | 24.638 | 0.55062 | 1.016 | 9
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 18 | Sil | Fiber | 24.638 | 0.55062 | 1.016 | 9 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3356 | 175
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 18 | Sil | Fiber | 26.162 | 0.67711 | 1.016 | 9 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3376 | 185
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 18 | Sil | Fiber | 26.924 | 0.692 | 1.016 | 9 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3271 | 195
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 18 | TS | TS | 18.542 | 0.43901 | 1.143 | 9 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0095 | 519
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 18 | TS | TS | 19.304 | 0.49853 | 1.143 | 9 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0096 | 524
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 18 | TS | TS | 20.066 | 0.54318 | 1.143 | 9 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0094 | 529
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 18 | TS | TS | 20.828 | 0.58038 | 1.524 | 9 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3468 | 614
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 18 | TS | TS | 23.114 | 0.71432 | 2.032 | 9 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-3487 | 798
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 18 | TS | TS | 23.876 | 0.7664 | 2.032 | 9 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5988 | 803
GENERIC | GENERIC | TP | TP | 16 | 19 | TP | TS | 16.129 | 0.4405 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 19 | TS | TS | 18.034 | 0.55211 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 16 | 19 | TP | TS | 16.129 | 0.4405 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38495 | 570
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 19 | TP | TP | 17.272 | 0.47026 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 23828 | 710
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 19 | TP | TP | 16.129 | 0.4405 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 68111 | 714
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 19 | TP | TP | 13.5382 | 0.38395 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181619C6 | 341
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 19 | TP | TP | 15.6464 | 0.54318 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 181619C6 | 597
General Cable | 20/10 | PE | PVC | 16 | 19 | TP | TP | 17.526 | 0.4524 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 365400 | 562
General Cable | VNTC® | PVC | PVC | 16 | 19 | TP | TP | 16.129 | 0.42264 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236260 | 727
Okonite | Okozel® | ETFE | ETFE | 16 | 19 | TP | TP | 12.7 | 0.36162 | 0.508 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3269 | 67
Okonite | P-30 | PE | PVC | 16 | 19 | TP | TP | 17.78 | 0.46282 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, 75°C | 203-84-2069 | 674
Draka | Reduced Diameter Control | XLPE | XLPO | 16 | 19 | TS | TS | 16.51 | 0.45389 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 216-19 | 429
General Cable | EHTC® | EPR | CSPE | 16 | 19 | TS | TS | 17.526 | 0.48663 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343550 | 589
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 19 | TS | TS | 16.8402 | 0.4658 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377750 | 718
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 19 | TS | TS | 18.034 | 0.55211 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2049 | 653
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 19 | TS | TS | 21.082 | 0.70837 | 1.524 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6069 | 661
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 19 | TS | TS | 19.304 | 0.55509 | 1.524 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2049 | 668
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 19 | TS | TS | 27.432 | 1.0149 | 2.032 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6069 | 820
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 19 | TS | TS | 24.384 | 0.78277 | 2.032 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2069 | 822
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 19 | TS | TS | 25.654 | 0.83635 | 2.032 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2069 | 838
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 19 | Sil | Fiber | 19.812 | 0.50598 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3311 | 164
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 19 | Sil | Fiber | 20.574 | 0.52086 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3337 | 165
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 19 | TS | TS | 14.986 | 0.4018 | 1.143 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0190 | 510
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 19 | TS | TS | 15.494 | 0.43157 | 1.143 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0191 | 511
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 19 | TS | TS | 17.018 | 0.47621 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0190 | 607
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 19 | TS | TS | 17.78 | 0.51342 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-3451 | 608
GENERIC | GENERIC | TP | TS | 16 | 21 | TP | TS | 16.51 | 0.50598 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38797 | 571
GENERIC | GENERIC | TP | TP | 16 | 24 | TP | TP | 19.9644 | 0.55806 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 24 | TS | TS | 22.86 | 0.70688 | 1.651 | 12
American Insulated Wire | American SDN® | PVC | CP | 16 | 24 | TP | TS | 19.05 | 0.54616 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38485 | 572
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 24 | TP | TP | 21.717 | 0.64735 | 1.524 | 12 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 298890 | 676
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 24 | TP | TP | 19.9644 | 0.55806 | 1.524 |  | 8 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340040 | 677
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 24 | TP | TP | 19.177 | 0.60717 | 1.524 | 12 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 298830 | 691
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 24 | TS | TP | 21.717 | 0.63247 | 0.381 | 12 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343270 | 37
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 24 | TS | TS | 28.194 | 0.81551 | 2.032 | 12 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 252370 | 781
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 24 | TS | TP | 22.86 | 0.65182 | 2.032 | 12 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 283190 | 826
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 24 | Sil | Fiber | 27.94 | 0.68456 | 1.016 | 12 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3357 | 176
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 24 | Sil | Fiber | 29.718 | 0.80361 | 1.016 | 12 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3377 | 186
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 24 | Sil | Fiber | 30.48 | 0.82593 | 1.016 | 12 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3272 | 196
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 24 | TS | TS | 21.844 | 0.61015 | 1.651 | 12 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0125 | 734
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 24 | TS | TS | 22.86 | 0.70688 | 1.651 | 12 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0126 | 738
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 24 | TS | TS | 23.622 | 0.75152 | 1.651 | 12 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0124 | 742
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 24 | TS | TS | 24.384 | 0.79617 | 2.032 | 12 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3470 | 794
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 24 | TS | TS | 25.908 | 0.90778 | 2.032 | 12 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-3029 | 799
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 24 | TS | TS | 26.67 | 0.96731 | 2.032 | 12 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5703 | 804
GENERIC | GENERIC | TP | TP | 16 | 25 | TP | TP | 17.907 | 0.54169 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 25 | TS | TS | 19.431 | 0.59675 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 16 | 25 | TP | TS | 18.542 | 0.5655 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38798 | 573
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 25 | TP | TP | 19.304 | 0.60122 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 18129 | 711
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 25 | TP | TP | 18.288 | 0.56401 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 68112 | 715
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 25 | TP | TP | 15.5956 | 0.49258 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181625C6 | 342
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 25 | TP | TP | 17.9324 | 0.692 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 181625C6 | 598
General Cable | VNTC® | PVC | PVC | 16 | 25 | TP | TP | 17.907 | 0.54169 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236280 | 728
General Cable | EHTC® | EPR | CSPE | 16 | 25 | TS | TS | 20.193 | 0.63098 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343560 | 590
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 25 | TS | TS | 19.431 | 0.59675 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377760 | 719
GENERIC | GENERIC | TS | TS | 16 | 27 | TS | TS | 20.066 | 0.64735 | 1.524
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 27 | Sil | Fiber | 23.876 | 0.71432 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3312 | 166
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 27 | Sil | Fiber | 24.638 | 0.7292 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3338 | 167
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 27 | TS | TS | 17.78 | 0.55062 | 1.143 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0270 | 512
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 27 | TS | TS | 18.542 | 0.58782 | 1.143 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0271 | 513
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 27 | TS | TS | 20.066 | 0.64735 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0270 | 609
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 27 | TS | TS | 20.828 | 0.692 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-5979 | 610
GENERIC | GENERIC | TP | TP | 16 | 30 | TP | TP | 19.304 | 0.63396 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 30 | TS | TS | 25.4 | 0.85569 | 1.651 | 15
American Insulated Wire | American SDN® | PVC | CP | 16 | 30 | TP | TS | 19.05 | 0.64289 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38496 | 574
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 30 | TP | TP | 19.812 | 0.6786 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 68113 | 716
General Cable | VNTC® | PVC | PVC | 16 | 30 | TP | TP | 19.304 | 0.63396 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 244670 | 729
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 30 | TS | TS | 20.701 | 0.7545 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377770 | 720
General Cable | EHTC® | EPR | CSPE | 16 | 30 | TS | TS | 22.606 | 0.75599 | 2.032 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343570 | 790
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 30 | Sil | Fiber | 31.242 | 0.85569 | 1.016 | 15 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3358 | 177
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 30 | Sil | Fiber | 33.274 | 1.0194 | 1.016 | 15 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3378 | 187
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 30 | Sil | Fiber | 34.036 | 1.0417 | 1.016 | 15 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3273 | 197
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 30 | TS | TS | 24.13 | 0.73664 | 1.651 | 15 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0155 | 735
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 30 | TS | TS | 25.4 | 0.85569 | 1.651 | 15 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0156 | 739
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 30 | TS | TS | 26.162 | 0.90778 | 1.651 | 15 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0154 | 743
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 30 | TS | TS | 26.924 | 0.92266 | 2.032 | 15 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3471 | 795
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 30 | TS | TS | 28.702 | 1.064 | 2.032 | 15 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-3489 | 800
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 30 | TS | TS | 29.464 | 1.1236 | 2.032 | 15 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5989 | 805
GENERIC | GENERIC | TP | TP | 16 | 32 | TP | TP | 21.463 | 0.78277 | 1.778
GENERIC | GENERIC | TS | TS | 16 | 32 | TS | TP | 25.781 | 0.83337 | 2.032 | 16
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 32 | TP | TP | 22.225 | 0.79914 | 2.032 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 27885 | 851
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 32 | TP | TP | 24.638 | 0.85569 | 1.778 | 16 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 759770 | 754
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 32 | TP | TP | 21.463 | 0.78277 | 1.778 | 16 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 760530 | 770
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 32 | TS | TP | 24.257 | 0.83784 | 0.381 | 16 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343280 | 38
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 32 | TS | TS | 34.29 | 1.0611 | 2.032 | 16 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337720 | 782
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 32 | TS | TP | 25.781 | 0.83337 | 2.032 | 16 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337100 | 827
GENERIC | GENERIC | TP | TP | 16 | 36 | TP | TP | 24.638 | 0.88843 | 1.778 |  | 12 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340050 | 757
GENERIC | GENERIC | TP | TP | 16 | 37 | TP | TP | 20.6248 | 0.96731 | 1.524
GENERIC | GENERIC | TS | TS | 16 | 37 | TS | TS | 25.4 | 1.0239 | 2.032
American Insulated Wire | American SDN® | PVC | CP | 16 | 37 | TP | TS | 22.098 | 0.82742 | 2.032 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38497 | 778
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 16 | 37 | TP | TP | 23.368 | 0.90778 | 2.032 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 27886 | 852
American Insulated Wire | TYPE TC-ER Control/Instrument | PVC | PVC | 16 | 37 | TP | TP | 22.352 | 0.86314 | 2.032 |  |  | Industrial Grade | Unshielded, 600V | 68114 | 853
Cable USA | ETFE TYPE TC | ETFE | ETFE | 16 | 37 | TP | TP | 18.0086 | 0.70093 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181637C6 | 343
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 16 | 37 | TP | TP | 20.6248 | 0.96731 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 181637C6 | 599
General Cable | VNTC® | PVC | PVC | 16 | 37 | TP | TP | 22.352 | 0.82147 | 2.032 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236290 | 854
Okonite | Okozel® | ETFE | ETFE | 16 | 37 | TP | TP | 17.272 | 0.68307 | 0.508 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3287 | 68
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 16 | 37 | TS | TS | 23.3426 | 0.89736 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377780 | 721
General Cable | EHTC® | EPR | CSPE | 16 | 37 | TS | TS | 24.257 | 0.90629 | 2.032 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343580 | 791
Okonite | FMR® - LCS® Okolon® | EPR | CSPE | 16 | 37 | TS | TS | 36.068 | 1.7307 | 2.032 |  |  | Nuclear Tracability | 1000V, 90°, Corrugated Copper Shield w/ Jacket | 202-14-6087 | 821
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 37 | TS | TS | 24.892 | 1.6682 | 2.032 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 202-10-2067 | 823
Okonite | FMR® Okolon® | EPR | CSPE | 16 | 37 | TS | TS | 32.258 | 1.3542 | 2.032 |  |  | Nuclear Qualified 383 | Unshielded, 1000V, 90° | 202-14-2087 | 824
Okonite | FMR-LCS® Okolon® | EPR | CSPE | 16 | 37 | TS | TS | 28.702 | 1.2768 | 2.032 |  |  | Nuclear Tracability | Corrugated Copper Shield, 600V, 90°C | 202-10-6087 | 825
Okonite | FRM-N® Okolon® | EPR | CSPE | 16 | 37 | TS | TS | 25.4 | 1.0239 | 2.032 |  |  | Nuclear Qualified | Unshielded, 600V, 90°C | 202-16-2067 | 837
Okonite | FRM-N® Okolon® 1000/2000V | EPR | CSPE | 16 | 37 | TS | TS | 33.528 | 1.4257 | 2.032 |  |  | Nuclear Qualified | Unshielded, 1000V, 90°C | 202-18-2087 | 839
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 37 | Sil | Fiber | 26.924 | 0.96731 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3313 | 168
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 37 | Sil | Fiber | 27.686 | 0.98963 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3339 | 169
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 37 | TS | TS | 19.812 | 0.7292 | 1.143 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I83-0370 | 514
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 37 | TS | TS | 20.574 | 0.77385 | 1.143 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I83-0371 | 515
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 37 | TS | TS | 23.622 | 0.90778 | 2.032 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I45-0370 | 792
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 37 | TS | TS | 24.13 | 0.96731 | 2.032 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I46-5980 | 793
GENERIC | GENERIC | TS | TS | 16 | 38 | TS | TS | 28.448 | 1.0715 | 2.032 | 19
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 38 | Sil | Fiber | 33.02 | 1.0492 | 1.016 | 19 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3359 | 178
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 38 | Sil | Fiber | 35.306 | 1.2575 | 1.016 | 19 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3379 | 188
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 38 | Sil | Fiber | 35.814 | 1.2798 | 1.016 | 19 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3274 | 198
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 38 | TS | TS | 25.4 | 0.88546 | 1.651 | 19 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0195 | 736
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 38 | TS | TS | 26.67 | 1.0492 | 1.651 | 19 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0196 | 740
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 38 | TS | TS | 27.432 | 1.1012 | 1.651 | 19 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0194 | 744
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 38 | TS | TS | 28.448 | 1.0715 | 2.032 | 19 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-3472 | 796
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 38 | TS | TS | 30.226 | 1.2501 | 2.032 | 19 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-3490 | 801
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 38 | TS | TS | 30.988 | 1.3096 | 2.032 | 19 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5990 | 806
GENERIC | GENERIC | TP | TP | 16 | 40 | TP | TP | 22.987 | 0.97475 | 1.778 | 20
GENERIC | GENERIC | TS | TS | 16 | 40 | TS | TP | 28.702 | 1.012 | 2.032 | 20
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 40 | TP | TP | 27.432 | 1.0492 | 1.778 | 20 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339840 | 755
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 40 | TP | TP | 22.987 | 0.97475 | 1.778 | 20 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339710 | 771
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 40 | TS | TP | 26.797 | 0.98814 | 0.381 | 20 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343290 | 39
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 40 | TS | TS | 34.671 | 1.2649 | 2.032 | 20 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337730 | 783
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 40 | TS | TP | 28.702 | 1.012 | 2.032 | 20 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337110 | 828
GENERIC | GENERIC | TP | TP | 16 | 48 | TP | TP | 27.305 | 1.1384 | 1.778 |  | 16
GENERIC | GENERIC | TS | TS | 16 | 48 | TS | TP | 30.861 | 1.2009 | 2.032 | 24
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 48 | TP | TP | 29.591 | 1.2322 | 1.778 | 24 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 759780 | 756
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 48 | TP | TP | 27.305 | 1.1384 | 1.778 |  | 16 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340060 | 758
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 48 | TP | TP | 26.162 | 1.195 | 1.778 | 24 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339720 | 772
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 48 | TS | TP | 29.464 | 1.1608 | 0.381 | 24 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343300 | 40
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 48 | TS | TS | 39.878 | 1.4897 | 2.032 | 24 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337740 | 784
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 48 | TS | TP | 30.861 | 1.2009 | 2.032 | 24 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337120 | 829
GENERIC | GENERIC | TP | TS | 16 | 60 | TP | TS | 26.543 | 1.4182 | 2.032 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38633 | 779
American Insulated Wire | American SDN® | PVC | CP | 16 | 60 | TP | TS | 26.543 | 1.4182 | 2.032 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38633 | 779
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 60 | TP | TP | 30.353 | 1.3885 | 1.778 |  | 20 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340070 | 759
GENERIC | GENERIC | TP | TP | 16 | 72 | TP | TP | 33.274 | 1.6742 | 2.032 |  | 24
GENERIC | GENERIC | TS | TS | 16 | 72 | TS | TP | 38.227 | 1.7263 | 2.032 | 36
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 72 | TP | TP | 29.591 | 1.6697 | 1.778 | 36 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339730 | 773
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 72 | TP | TP | 35.306 | 1.8081 | 2.032 | 36 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339850 | 840
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 72 | TP | TP | 33.274 | 1.6742 | 2.032 |  | 24 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340080 | 841
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 72 | TS | TP | 35.052 | 1.692 | 0.381 | 36 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343310 | 41
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 72 | TS | TP | 38.227 | 1.7263 | 2.032 | 36 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337130 | 830
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 72 | TS | TS | 50.292 | 2.3037 | 2.794 | 36 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337750 | 856
GENERIC | GENERIC | TS | TS | 16 | 74 | TS | TS | 37.592 | 1.89 | 2.032 | 37
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 74 | Sil | Fiber | 44.958 | 1.9048 | 1.016 | 37 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3360 | 179
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 74 | Sil | Fiber | 50.292 | 2.3364 | 1.016 | 37 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3380 | 189
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 16 | 74 | Sil | Fiber | 51.562 | 2.4852 | 1.016 | 37 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3276 | 199
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 74 | TS | TS | 33.782 | 1.5849 | 1.651 | 37 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I83-0375 | 737
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 74 | TS | TS | 36.068 | 1.9272 | 1.651 | 37 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I83-0376 | 741
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 16 | 74 | TS | TS | 36.83 | 1.9941 | 1.651 | 37 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I83-0374 | 745
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 74 | TS | TS | 37.592 | 1.89 | 2.032 | 37 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5982 | 797
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 74 | TS | TS | 40.64 | 2.2546 | 2.032 | 37 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I46-5984 | 802
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 16 | 74 | TS | TS | 41.402 | 2.3364 | 2.032 | 37 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I46-5992 | 807
GENERIC | GENERIC | TP | TP | 16 | 100 | TP | TP | 34.417 | 2.2977 | 2.032 | 50
GENERIC | GENERIC | TS | TS | 16 | 100 | TS | TP | 53.213 | 2.5329 | 2.032 | 50
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 16 | 100 | TP | TP | 34.417 | 2.2977 | 2.032 | 50 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339740 | 845
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 16 | 100 | TP | TP | 42.037 | 2.4852 | 2.286 | 50 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339860 | 855
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 16 | 100 | TS | TP | 40.132 | 2.259 | 0.381 | 50 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343320 | 42
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 16 | 100 | TS | TP | 53.213 | 2.5329 | 2.032 | 50 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337140 | 831
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 16 | 100 | TS | TS | 54.991 | 3.0061 | 2.794 | 50 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337760 | 857
GENERIC | GENERIC | TP | TP | 16 | 108 | TP | TP | 39.116 | 2.4108 | 2.032 |  | 36 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340090 | 842
GENERIC | GENERIC | TP | TP | 18 | 2 | TP | TP | 6.096 | 0.052086 | 1.016 | 1
GENERIC | GENERIC | TS | TS | 18 | 2 | TS | TS | 7.493 | 0.066967 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 18 | 2 | TP | TS | 6.985 | 0.068456 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38780 | 300
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 18 | 2 | TP | TP | 6.985 | 0.080361 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 19617 | 452
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 2 | TP | TP | 3.8608 | 0.022322 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 191802C3.ART | 1
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 2 | TP | TP | 5.3848 | 0.04018 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181802C6 | 79
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 2 | TP | TP | 6.9088 | 0.077385 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181802C6 | 353
General Cable | 20/10 | PE | PVC | 18 | 2 | TP | TP | 7.62 | 0.061015 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365300 | 282
General Cable | VNTC® | PVC | PVC | 18 | 2 | TP | TP | 6.858 | 0.05655 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 318050 | 492
General Cable | VNTC® | PVC | PVC | 18 | 2 | TP | TP | 7.112 | 0.059527 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 261130 | 493
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 2 | TP | TP | 6.096 | 0.052086 | 1.016 | 1 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325830 | 258
Okonite | Okozel® | ETFE | ETFE | 18 | 2 | TP | TP | 5.08 | 0.041669 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3152 | 59
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 2 | TS | TS | 6.604 | 0.050598 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-02 | 94
General Cable | EHTC® | EPR | CSPE | 18 | 2 | TS | TS | 7.493 | 0.066967 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343330 | 333
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 2 | TS | TS | 7.3406 | 0.071432 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377560 | 470
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 2 | TS | TS | 8.001 | 0.07292 | 1.143 | 1 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 285150 | 324
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 2 | TS | TP | 7.62 | 0.062503 | 1.143 | 1 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 387650 | 411
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 2 | TS | TS | 6.35 | 0.044645 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0022 | 122
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 2 | TS | TS | 6.35 | 0.052086 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0021 | 123
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 2 | Sil | Fiber | 8.636 | 0.059527 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3288 | 200
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 2 | Sil | Fiber | 8.636 | 0.059527 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3314 | 201
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 2 | TS | TS | 7.366 | 0.074408 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0020 | 377
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 2 | TS | TS | 7.366 | 0.081849 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0021 | 378
GENERIC | GENERIC | TP | TP | 18 | 3 | TP | TP | 6.7056 | 0.065479 | 1.016 |  | 1
GENERIC | GENERIC | TS | TS | 18 | 3 | TS | TS | 7.7216 | 0.077385 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 18 | 3 | TP | TS | 7.239 | 0.074408 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38498 | 301
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 18 | 3 | TP | TP | 7.366 | 0.092266 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 25650 | 453
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 3 | TP | TP | 4.1402 | 0.03274 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 191803C3.ART | 2
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 3 | TP | TP | 5.6896 | 0.053574 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181803C6 | 80
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 3 | TP | TP | 7.2644 | 0.099707 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181803C6 | 354
General Cable | 20/10 | PE | PVC | 18 | 3 | TP | TP | 7.874 | 0.07292 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 363310 | 283
General Cable | VNTC® | PVC | PVC | 18 | 3 | TP | TP | 7.239 | 0.068456 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 245920 | 494
General Cable | VNTC® | PVC | PVC | 18 | 3 | TP | TP | 7.366 | 0.07292 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 261140 | 495
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 3 | TP | TP | 6.7056 | 0.065479 | 1.016 |  | 1 | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325840 | 259
Okonite | Okozel® | ETFE | ETFE | 18 | 3 | TP | TP | 5.334 | 0.052086 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3153 | 60
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 3 | TS | TS | 6.985 | 0.065479 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-03 | 95
General Cable | EHTC® | EPR | CSPE | 18 | 3 | TS | TS | 7.874 | 0.081849 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343340 | 334
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 3 | TS | TS | 7.7216 | 0.077385 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377570 | 471
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 3 | TS | TS | 8.509 | 0.095242 | 1.143 |  | 1 | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337620 | 325
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 3 | TS | TP | 8.001 | 0.078873 | 1.143 |  | 1 | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 325250 | 412
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 3 | TS | TS | 6.604 | 0.059527 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0032 | 124
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 3 | TS | TS | 6.604 | 0.066967 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0031 | 125
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 3 | Sil | Fiber | 9.144 | 0.074408 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3289 | 202
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 3 | Sil | Fiber | 9.144 | 0.081849 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3315 | 203
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 3 | TS | TS | 7.874 | 0.08929 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0030 | 379
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 3 | TS | TS | 7.874 | 0.096731 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0031 | 380
GENERIC | GENERIC | TP | TP | 18 | 4 | TP | TP | 7.874 | 0.086314 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 4 | Sil | Fiber | 9.906 | 0.096731 | 1.016
American Insulated Wire | American SDN® | PVC | CP | 18 | 4 | TP | TS | 8.001 | 0.08929 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38781 | 302
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 18 | 4 | TP | TP | 7.874 | 0.10715 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 19619 | 454
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 4 | TP | TP | 4.5466 | 0.041669 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 191804C3.ART | 3
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 4 | TP | TP | 6.1722 | 0.065479 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181804C6 | 81
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 4 | TP | TP | 7.8232 | 0.11905 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181804C6 | 355
General Cable | 20/10 | PE | PVC | 18 | 4 | TP | TP | 8.636 | 0.08929 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 543640 | 284
General Cable | VNTC® | PVC | PVC | 18 | 4 | TP | TP | 7.874 | 0.083337 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236100 | 496
General Cable | VNTC® | PVC | PVC | 18 | 4 | TP | TP | 7.874 | 0.086314 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 261150 | 497
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 4 | TP | TP | 7.5184 | 0.090778 | 1.0668 | 2 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 325860 | 264
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 4 | TP | TP | 8.255 | 0.081849 | 1.0668 | 2 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325850 | 269
Okonite | Okozel® | ETFE | ETFE | 18 | 4 | TP | TP | 5.842 | 0.066967 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3154 | 61
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 4 | TS | TS | 7.62 | 0.081849 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-04 | 96
General Cable | EHTC® | EPR | CSPE | 18 | 4 | TS | TS | 8.636 | 0.099707 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343350 | 335
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 4 | TS | TS | 8.3566 | 0.1012 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377580 | 472
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 4 | TS | TP | 10.414 | 0.10864 | 0.381 | 2 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343140 | 43
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 4 | TS | TS | 12.954 | 0.13691 | 1.143 | 2 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337630 | 326
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 4 | TS | TP | 10.668 | 0.11161 | 1.143 | 2 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337010 | 413
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 4 | TS | TS | 7.366 | 0.074408 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0042 | 126
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 4 | TS | TS | 7.366 | 0.081849 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0041 | 127
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 4 | Sil | Fiber | 9.906 | 0.096731 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3290 | 204
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 4 | Sil | Fiber | 10.16 | 0.10417 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3316 | 205
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 4 | TS | TS | 8.382 | 0.11161 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0040 | 381
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 4 | TS | TS | 8.382 | 0.11905 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0041 | 382
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 4 | TS | TS | 9.398 | 0.08929 | 0.889 | 2 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0025 | 138
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 4 | TS | TS | 10.16 | 0.10417 | 0.889 | 2 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0026 | 142
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 4 | TS | TS | 10.414 | 0.10417 | 0.889 | 2 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0024 | 145
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 4 | Sil | Fiber | 13.208 | 0.12649 | 1.016 | 2 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3361 | 222
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 4 | Sil | Fiber | 14.224 | 0.14138 | 1.016 | 2 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3381 | 232
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 4 | Sil | Fiber | 14.478 | 0.14882 | 1.016 | 2 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3277 | 242
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 4 | TS | TS | 10.922 | 0.1637 | 1.143 | 2 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0022 | 391
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 4 | TS | TS | 11.684 | 0.18602 | 1.143 | 2 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0023 | 394
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 4 | TS | TS | 11.938 | 0.19346 | 1.143 | 2 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0024 | 396
GENERIC | GENERIC | TP | TP | 18 | 5 | TP | TP | 8.509 | 0.096731 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 5 | TS | TS | 9.0678 | 0.11161 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 18 | 5 | TP | TS | 8.509 | 0.10566 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38499 | 303
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 5 | TP | TP | 5.0292 | 0.052086 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 191805C3.ART | 4
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 5 | TP | TP | 6.731 | 0.078873 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181805C6 | 82
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 5 | TP | TP | 8.4836 | 0.1384 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181805C6 | 356
General Cable | 20/10 | PE | PVC | 18 | 5 | TP | TP | 9.398 | 0.10566 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365320 | 285
General Cable | VNTC® | PVC | PVC | 18 | 5 | TP | TP | 8.509 | 0.096731 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 244680 | 498
General Cable | VNTC® | PVC | PVC | 18 | 5 | TP | TP | 8.636 | 0.10417 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 260000 | 499
Okonite | Okozel® | ETFE | ETFE | 18 | 5 | TP | TP | 6.35 | 0.078873 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3155 | 62
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 5 | TS | TS | 8.255 | 0.098219 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-05 | 97
General Cable | EHTC® | EPR | CSPE | 18 | 5 | TS | TS | 9.271 | 0.11756 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343360 | 336
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 5 | TS | TS | 9.0678 | 0.11161 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377590 | 473
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 5 | TS | TS | 7.874 | 0.08929 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0052 | 128
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 5 | TS | TS | 8.382 | 0.10417 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0051 | 129
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 5 | Sil | Fiber | 10.922 | 0.11905 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3291 | 206
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 5 | Sil | Fiber | 11.43 | 0.12649 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3317 | 207
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 5 | TS | TS | 9.144 | 0.13393 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0050 | 383
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 5 | TS | TS | 9.652 | 0.15626 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0051 | 384
GENERIC | GENERIC | TP | TP | 18 | 6 | TP | TS | 9.144 | 0.12352 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 6 | TS | TS | 10.922 | 0.14138 | 0.889 | 3
American Insulated Wire | American SDN® | PVC | CP | 18 | 6 | TP | TS | 9.144 | 0.12352 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38500 | 304
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 18 | 6 | TP | TP | 10.1854 | 0.14435 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 27883 | 455
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 6 | TP | TP | 8.1534 | 0.11459 | 1.016 |  | 2 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 325870 | 253
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 6 | TS | TS | 10.16 | 0.11161 | 0.889 | 3 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0035 | 139
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 6 | TS | TS | 10.922 | 0.13393 | 0.889 | 3 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0036 | 143
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 6 | TS | TS | 10.922 | 0.14138 | 0.889 | 3 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0034 | 146
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 6 | Sil | Fiber | 14.224 | 0.1637 | 1.016 | 3 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3362 | 223
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 6 | Sil | Fiber | 15.24 | 0.18602 | 1.016 | 3 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3382 | 233
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 6 | Sil | Fiber | 15.494 | 0.19346 | 1.016 | 3 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3278 | 243
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 6 | TS | TS | 11.684 | 0.19346 | 1.143 | 3 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0032 | 392
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 6 | TS | TS | 12.446 | 0.23067 | 1.143 | 3 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0033 | 395
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 6 | TS | TS | 12.7 | 0.23811 | 1.143 | 3 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0034 | 397
GENERIC | GENERIC | TP | TP | 18 | 7 | TP | TP | 9.144 | 0.17412 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 7 | TS | TS | 9.652 | 0.14882 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 18 | 7 | TP | TS | 9.652 | 0.15775 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38782 | 305
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 18 | 7 | TP | TP | 10.1854 | 0.1503 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 30845 | 456
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 7 | TP | TP | 5.5372 | 0.071432 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 191807C3.ART | 5
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 7 | TP | TP | 7.3152 | 0.10417 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181807C6 | 83
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 7 | TP | TP | 9.144 | 0.17412 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181807C6 | 357
General Cable | 20/10 | PE | PVC | 18 | 7 | TP | TP | 10.16 | 0.13393 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365330 | 286
General Cable | VNTC® | PVC | PVC | 18 | 7 | TP | TP | 9.144 | 0.12203 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 244660 | 500
General Cable | VNTC® | PVC | PVC | 18 | 7 | TP | TP | 9.398 | 0.13245 | 1.143 |  |  | Industrial Grade | Shielded, Overall Shield, 600V, UL Type TC-ER | 259980 | 501
Okonite | Okozel® | ETFE | ETFE | 18 | 7 | TP | TP | 6.858 | 0.10417 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3157 | 63
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 7 | TS | TS | 9.017 | 0.12649 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-07 | 98
General Cable | EHTC® | EPR | CSPE | 18 | 7 | TS | TS | 10.033 | 0.14435 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343370 | 337
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 7 | TS | TS | 9.8298 | 0.14138 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377600 | 474
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 7 | TS | TS | 8.636 | 0.11161 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0072 | 130
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 7 | TS | TS | 9.144 | 0.13393 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0071 | 131
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 7 | Sil | Fiber | 11.684 | 0.15626 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3293 | 208
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 7 | Sil | Fiber | 12.446 | 0.1637 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3319 | 209
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 7 | TS | TS | 9.652 | 0.14882 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0070 | 385
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 7 | TS | TS | 10.414 | 0.1637 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0071 | 386
GENERIC | GENERIC | TP | TP | 18 | 8 | TP | TP | 10.414 | 0.14882 | 1.0668 | 4
GENERIC | GENERIC | TS | TS | 18 | 8 | TS | TS | 13.208 | 0.25299 | 1.143 | 4
American Insulated Wire | American SDN® | PVC | CP | 18 | 8 | TP | TS | 10.668 | 0.16221 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38501 | 306
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 8 | TP | TP | 10.414 | 0.14882 | 1.0668 | 4 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 325890 | 265
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 8 | TP | TP | 9.0678 | 0.13393 | 1.0668 | 4 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325880 | 270
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 8 | TS | TP | 12.065 | 0.17412 | 0.381 | 4 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343150 | 44
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 8 | TS | TP | 12.446 | 0.17412 | 1.143 | 4 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337020 | 414
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 8 | TS | TS | 16.002 | 0.24852 | 1.524 | 4 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337640 | 585
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 8 | TS | TS | 11.684 | 0.1637 | 0.889 | 4 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0045 | 140
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 8 | TS | TS | 11.938 | 0.17114 | 0.889 | 4 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0046 | 144
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 8 | TS | TS | 12.446 | 0.19346 | 0.889 | 4 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0044 | 147
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 8 | Sil | Fiber | 16.002 | 0.20834 | 1.016 | 4 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3363 | 224
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 8 | Sil | Fiber | 16.764 | 0.23811 | 1.016 | 4 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3383 | 234
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 8 | Sil | Fiber | 17.526 | 0.25299 | 1.016 | 4 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3279 | 244
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 8 | TS | TS | 13.208 | 0.25299 | 1.143 | 4 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0042 | 393
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 8 | TS | TS | 14.478 | 0.30507 | 1.524 | 4 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0043 | 635
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 8 | TS | TS | 15.24 | 0.33484 | 1.524 | 4 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0044 | 639
GENERIC | GENERIC | TP | TP | 18 | 9 | TP | TP | 10.668 | 0.15626 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 9 | TS | TS | 11.176 | 0.17858 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 18 | 9 | TP | TS | 11.43 | 0.17858 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38783 | 307
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 9 | TP | TP | 6.6548 | 0.092266 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 191809C3.ART | 6
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 9 | TP | TP | 8.5852 | 0.13245 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181809C6 | 84
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 9 | TP | TP | 10.541 | 0.2143 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181809C6 | 358
General Cable | 20/10 | PE | PVC | 18 | 9 | TP | TP | 11.684 | 0.16816 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 365340 | 287
General Cable | VNTC® | PVC | PVC | 18 | 9 | TP | TP | 10.668 | 0.15626 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 264570 | 502
Okonite | Okozel® | ETFE | ETFE | 18 | 9 | TP | TP | 8.128 | 0.12352 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3159 | 64
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 9 | TS | TS | 10.414 | 0.15923 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-09 | 99
General Cable | EHTC® | EPR | CSPE | 18 | 9 | TS | TS | 11.557 | 0.18304 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343380 | 338
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 9 | TS | TS | 11.3284 | 0.1756 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377610 | 475
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 9 | TS | TS | 9.906 | 0.14138 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0092 | 132
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 9 | TS | TS | 10.414 | 0.1637 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0091 | 133
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 9 | Sil | Fiber | 13.97 | 0.20834 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3295 | 210
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 9 | Sil | Fiber | 14.478 | 0.21578 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3321 | 211
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 9 | TS | TS | 11.176 | 0.17858 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0090 | 387
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 9 | TS | TS | 11.938 | 0.20834 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0091 | 388
GENERIC | GENERIC | TP | TP | 18 | 10 | TP | TP | 12.065 | 0.20239 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 10 | TS | TS | 14.224 | 0.2515 | 1.143 | 5
American Insulated Wire | American SDN® | PVC | CP | 18 | 10 | TP | TS | 11.43 | 0.18751 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38502 | 308
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 18 | 10 | TP | TP | 12.065 | 0.20239 | 1.143 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 19620 | 457
General Cable | VNTC® | PVC | PVC | 18 | 10 | TP | TP | 10.795 | 0.16965 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 233270 | 503
General Cable | EHTC® | EPR | CSPE | 18 | 10 | TS | TS | 12.319 | 0.20388 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343390 | 339
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 10 | TS | TS | 12.7 | 0.18602 | 0.889 | 5 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0055 | 141
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 10 | Sil | Fiber | 17.526 | 0.26043 | 1.016 | 5 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3364 | 225
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 10 | Sil | Fiber | 18.542 | 0.29763 | 1.016 | 5 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3384 | 235
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 10 | Sil | Fiber | 19.304 | 0.31251 | 1.016 | 5 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3280 | 245
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 10 | TS | TS | 13.462 | 0.22322 | 1.143 | 5 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0056 | 541
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 10 | TS | TS | 14.224 | 0.2515 | 1.143 | 5 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0054 | 546
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 10 | TS | TS | 14.986 | 0.3274 | 1.524 | 5 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0052 | 631
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 10 | TS | TS | 15.748 | 0.3646 | 1.524 | 5 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0053 | 636
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 10 | TS | TS | 16.51 | 0.39436 | 1.524 | 5 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0054 | 640
GENERIC | GENERIC | TP | TS | 18 | 11 | TP | TS | 11.938 | 0.2009 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38784 | 309
GENERIC | GENERIC | TP | TP | 18 | 12 | TP | TP | 11.303 | 0.19495 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 12 | TS | TS | 12.7 | 0.22322 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 18 | 12 | TP | TS | 11.811 | 0.21132 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38503 | 310
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 12 | TP | TP | 7.6708 | 0.12352 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 191812C3.ART | 23
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 12 | TP | TP | 9.6266 | 0.16965 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181812C6 | 85
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 12 | TP | TP | 11.7348 | 0.26787 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181812C6 | 359
General Cable | 20/10 | PE | PVC | 18 | 12 | TP | TP | 12.954 | 0.21578 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 547230 | 288
General Cable | VNTC® | PVC | PVC | 18 | 12 | TP | TP | 11.303 | 0.19495 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236120 | 504
General Cable | VNTC® CAROLFIRE | PVC | PVC | 18 | 12 | TP | TP | 11.303 | 0.19495 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236120 | 507
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 12 | TP | TP | 11.176 | 0.21281 | 1.27 |  | 4 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339960 | 552
Okonite | Okozel® | ETFE | ETFE | 18 | 12 | TP | TP | 9.398 | 0.16667 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3162 | 65
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 12 | TS | TS | 11.811 | 0.20537 | 0.762 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-12 | 100
General Cable | EHTC® | EPR | CSPE | 18 | 12 | TS | TS | 12.954 | 0.22769 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343400 | 340
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 12 | TS | TS | 12.7 | 0.22322 | 1.143 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377620 | 476
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 12 | TS | TS | 10.922 | 0.18602 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0122 | 134
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 12 | TS | TS | 11.684 | 0.20834 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0121 | 135
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 12 | Sil | Fiber | 15.748 | 0.25299 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3296 | 212
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 12 | Sil | Fiber | 16.256 | 0.26787 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3322 | 213
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 12 | TS | TS | 12.7 | 0.23067 | 1.143 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0120 | 389
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 12 | TS | TS | 13.208 | 0.25299 | 1.143 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0121 | 390
Rockbestus-Sup | CAROLFIRE | XLPE | CSPE | 18 | 12 | TS | TS | 12.7 | 0.23067 | 1.143 |  |  |  |  | I57-0120 | 316
GENERIC | GENERIC | TP | TS | 18 | 13 | TP | TS | 12.446 | 0.22769 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38785 | 311
GENERIC | GENERIC | TP | TS | 18 | 14 | TP | TS | 12.319 | 0.24555 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38629 | 312
GENERIC | GENERIC | TS | TS | 18 | 14 | TS | TS | 16.256 | 0.35716 | 1.524 | 7
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 14 | Sil | Fiber | 19.304 | 0.33484 | 1.016 | 7 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3365 | 226
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 14 | Sil | Fiber | 20.32 | 0.38692 | 1.016 | 7 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3385 | 236
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 14 | Sil | Fiber | 21.082 | 0.4018 | 1.016 | 7 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3281 | 246
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 14 | TS | TS | 14.224 | 0.26043 | 1.143 | 7 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0075 | 536
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 14 | TS | TS | 14.732 | 0.29019 | 1.143 | 7 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0076 | 542
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 14 | TS | TS | 15.494 | 0.31996 | 1.143 | 7 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0074 | 547
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 14 | TS | TS | 16.256 | 0.35716 | 1.524 | 7 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0072 | 632
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 14 | TS | TS | 17.272 | 0.39436 | 1.524 | 7 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0073 | 637
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 14 | TS | TS | 17.78 | 0.43157 | 1.524 | 7 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0074 | 641
GENERIC | GENERIC | TP | TP | 18 | 15 | TP | TS | 13.081 | 0.25299 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 15 | TS | TS | 14.732 | 0.30061 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 18 | 15 | TP | TS | 13.081 | 0.25299 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38786 | 313
General Cable | VNTC® | PVC | PVC | 18 | 15 | TP | TP | 12.319 | 0.24108 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 244720 | 505
General Cable | EHTC® | EPR | CSPE | 18 | 15 | TS | TS | 14.732 | 0.30061 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343410 | 591
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 15 | TS | TS | 12.192 | 0.22322 | 0.889 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0152 | 136
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 15 | TS | TS | 12.954 | 0.24555 | 0.889 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0151 | 137
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 15 | Sil | Fiber | 17.272 | 0.31996 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3297 | 214
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 15 | Sil | Fiber | 18.034 | 0.33484 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3323 | 215
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 15 | TS | TS | 14.732 | 0.30507 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0150 | 623
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 15 | TS | TS | 15.494 | 0.33484 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0151 | 624
GENERIC | GENERIC | TP | TP | 18 | 16 | TP | TS | 12.954 | 0.26043 | 1.143
GENERIC | GENERIC | TS | TS | 18 | 16 | TS | TP | 17.145 | 0.33335 | 1.524 | 8
American Insulated Wire | American SDN® | PVC | CP | 18 | 16 | TP | TS | 12.954 | 0.26043 | 1.143 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38504 | 314
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 16 | TP | TP | 8.5598 | 0.16072 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 191816C3.ART | 24
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 16 | TP | TP | 10.668 | 0.21727 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181816C6 | 86
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 16 | TP | TP | 12.954 | 0.33633 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181816C6 | 360
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 16 | TP | TP | 12.319 | 0.31549 | 1.524 | 8 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 348060 | 678
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 16 | TP | TP | 16.4084 | 0.28573 | 1.524 | 8 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 348020 | 692
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 16 | TS | TP | 15.367 | 0.31996 | 0.381 | 8 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343160 | 45
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 16 | TS | TP | 17.145 | 0.33335 | 1.524 | 8 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337030 | 664
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 16 | TS | TS | 21.717 | 0.48514 | 2.032 | 8 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337650 | 785
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 16 | TS | TS | 15.24 | 0.29019 | 1.143 | 8 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0085 | 537
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 16 | TS | TS | 16.002 | 0.3274 | 1.143 | 8 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0086 | 543
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 16 | TS | TS | 16.764 | 0.35716 | 1.143 | 8 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0084 | 548
GENERIC | GENERIC | TP | TS | 18 | 17 | TP | TS | 14.986 | 0.34228 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38787 | 575
GENERIC | GENERIC | TP | TS | 18 | 18 | TP | TS | 14.986 | 0.34228 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38788 | 576
GENERIC | GENERIC | TS | TS | 18 | 18 | TS | TS | 18.034 | 0.39436 | 1.143 | 9
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 18 | Sil | Fiber | 22.606 | 0.43157 | 1.016 | 9 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3366 | 227
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 18 | Sil | Fiber | 24.13 | 0.50598 | 1.016 | 9 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3386 | 237
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 18 | Sil | Fiber | 24.892 | 0.52086 | 1.016 | 9 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3282 | 247
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 18 | TS | TS | 16.51 | 0.31996 | 1.143 | 9 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0095 | 538
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 18 | TS | TS | 17.272 | 0.3646 | 1.143 | 9 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0096 | 544
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 18 | TS | TS | 18.034 | 0.39436 | 1.143 | 9 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0094 | 549
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 18 | TS | TS | 19.05 | 0.44645 | 1.524 | 9 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0092 | 633
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 18 | TS | TS | 20.066 | 0.49853 | 1.524 | 9 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0093 | 638
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 18 | TS | TS | 20.574 | 0.53574 | 1.524 | 9 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0094 | 642
GENERIC | GENERIC | TP | TP | 18 | 19 | TP | TP | 14.478 | 0.31103 | 1.524
GENERIC | GENERIC | TS | TS | 18 | 19 | TS | TS | 15.113 | 0.34674 | 1.143
American Insulated Wire | American SDN® | PVC | CP | 18 | 19 | TP | TS | 14.986 | 0.35716 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38630 | 577
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 19 | TP | TP | 9.0678 | 0.19048 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 191819C3.ART | 25
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 19 | TP | TP | 11.2522 | 0.25299 | 0.762 |  |  | Industrial Grade | Unshielded, 600V | 181819C6 | 87
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 19 | TP | TP | 14.3764 | 0.41966 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 181819C6 | 600
General Cable | 20/10 | PE | PVC | 18 | 19 | TP | TP | 16.002 | 0.34079 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 365350 | 563
General Cable | VNTC® | PVC | PVC | 18 | 19 | TP | TP | 14.478 | 0.31103 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236130 | 730
Okonite | Okozel® | ETFE | ETFE | 18 | 19 | TP | TP | 10.922 | 0.24704 | 0.381 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3169 | 66
Draka | Reduced Diameter Control | XLPE | XLPO | 18 | 19 | TS | TS | 15.113 | 0.34674 | 1.143 |  |  | Industrial Grade | Unshielded, 600V, 90°C | 218-19 | 430
General Cable | EHTC® | EPR | CSPE | 18 | 19 | TS | TS | 15.875 | 0.36162 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343420 | 592
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 19 | TS | TS | 15.5702 | 0.35121 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377630 | 722
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 19 | Sil | Fiber | 18.288 | 0.39436 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3298 | 216
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 19 | Sil | Fiber | 19.05 | 0.4018 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3324 | 217
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 19 | TS | TS | 13.462 | 0.29019 | 1.143 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0192 | 530
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 19 | TS | TS | 13.97 | 0.31251 | 1.143 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0191 | 531
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 19 | TS | TS | 15.494 | 0.35716 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0190 | 625
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 19 | TS | TS | 16.002 | 0.38692 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0191 | 626
GENERIC | GENERIC | TP | TS | 18 | 21 | TP | TS | 15.367 | 0.4018 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38789 | 578
GENERIC | GENERIC | TP | TP | 18 | 24 | TP | TP | 17.5514 | 0.40925 | 1.524 |  | 8
GENERIC | GENERIC | TS | TS | 18 | 24 | TS | TS | 21.082 | 0.55806 | 1.524 | 12
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 24 | TP | TP | 19.304 | 0.46877 | 1.524 | 12 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 348070 | 679
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 24 | TP | TP | 17.5514 | 0.40925 | 1.524 |  | 8 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 348010 | 681
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 24 | TP | TP | 17.018 | 0.43603 | 1.524 | 12 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 348030 | 693
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 24 | TS | TP | 19.05 | 0.45835 | 0.381 | 12 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343170 | 46
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 24 | TS | TP | 19.685 | 0.45389 | 1.524 | 12 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337040 | 665
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 24 | TS | TS | 26.162 | 0.65628 | 2.032 | 12 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337660 | 786
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 24 | Sil | Fiber | 25.654 | 0.5283 | 1.016 | 12 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3367 | 228
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 24 | Sil | Fiber | 27.432 | 0.61759 | 1.016 | 12 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3387 | 238
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 24 | Sil | Fiber | 27.94 | 0.63247 | 1.016 | 12 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3283 | 248
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 24 | TS | TS | 18.542 | 0.40925 | 1.143 | 12 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0125 | 539
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 24 | TS | TS | 19.558 | 0.46877 | 1.143 | 12 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0126 | 545
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 24 | TS | TS | 20.32 | 0.50598 | 1.143 | 12 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0124 | 550
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 24 | TS | TS | 21.082 | 0.55806 | 1.524 | 12 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0122 | 634
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 24 | TS | TS | 23.622 | 0.69944 | 2.032 | 12 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0123 | 811
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 24 | TS | TS | 24.13 | 0.74408 | 2.032 | 12 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0124 | 815
GENERIC | GENERIC | TP | TP | 18 | 25 | TP | TP | 16.637 | 0.39585 | 1.524
GENERIC | GENERIC | TS | TS | 18 | 25 | TS | TS | 17.9324 | 0.44943 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 18 | 25 | TP | TS | 17.272 | 0.44645 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38790 | 579
American Insulated Wire | TYPE TC Control/Instrument | PVC | PVC | 18 | 25 | TP | TP | 17.399 | 0.44347 | 1.524 |  |  | Industrial Grade | Overall shield, 600V, Drain Wire | 26390 | 712
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 18 | 25 | TP | TP | 10.7696 | 0.25299 | 0.381 |  |  | Industrial Grade | Optional Shield & Drain | 191825C3.ART | 31
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 25 | TP | TP | 13.7922 | 0.35418 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181825C6 | 344
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 25 | TP | TP | 16.4338 | 0.52979 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 181825C6 | 601
General Cable | VNTC® | PVC | PVC | 18 | 25 | TP | TP | 16.637 | 0.39585 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236140 | 731
General Cable | EHTC® | EPR | CSPE | 18 | 25 | TS | TS | 18.288 | 0.44794 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343430 | 593
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 25 | TS | TS | 17.9324 | 0.44943 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377640 | 723
GENERIC | GENERIC | TS | TS | 18 | 27 | TS | TS | 16.51 | 0.42413 | 1.143
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 27 | Sil | Fiber | 22.098 | 0.55062 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3299 | 218
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 27 | Sil | Fiber | 22.606 | 0.5655 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3325 | 219
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 27 | TS | TS | 16.002 | 0.39436 | 1.143 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0272 | 532
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 27 | TS | TS | 16.51 | 0.42413 | 1.143 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0271 | 533
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 27 | TS | TS | 18.288 | 0.48365 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0270 | 627
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 27 | TS | TS | 19.05 | 0.52086 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0271 | 628
GENERIC | GENERIC | TP | TP | 18 | 30 | TP | TP | 17.653 | 0.46133 | 1.524
GENERIC | GENERIC | TS | TS | 18 | 30 | TS | TS | 22.86 | 0.63247 | 1.651 | 15
American Insulated Wire | American SDN® | PVC | CP | 18 | 30 | TP | TS | 17.653 | 0.49853 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38791 | 580
General Cable | VNTC® | PVC | PVC | 18 | 30 | TP | TP | 17.653 | 0.46133 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 347140 | 732
General Cable | EHTC® | EPR | CSPE | 18 | 30 | TS | TS | 19.558 | 0.51342 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343440 | 594
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 30 | TS | TS | 19.0754 | 0.51788 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377650 | 724
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 30 | Sil | Fiber | 28.702 | 0.66223 | 1.016 | 15 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3368 | 229
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 30 | Sil | Fiber | 30.734 | 0.78129 | 1.016 | 15 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3388 | 239
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 30 | Sil | Fiber | 31.242 | 0.79617 | 1.016 | 15 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3284 | 249
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 30 | TS | TS | 20.574 | 0.49109 | 1.143 | 15 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0155 | 540
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 30 | TS | TS | 22.86 | 0.63247 | 1.651 | 15 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0156 | 748
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 30 | TS | TS | 23.368 | 0.66967 | 1.651 | 15 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0154 | 751
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 30 | TS | TS | 24.384 | 0.70688 | 2.032 | 15 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0152 | 808
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 30 | TS | TS | 26.162 | 0.81105 | 2.032 | 15 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0153 | 812
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 30 | TS | TS | 26.67 | 0.85569 | 2.032 | 15 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0154 | 816
GENERIC | GENERIC | TP | TP | 18 | 32 | TS | TP | 21.082 | 0.58336 | 0.381 | 16
GENERIC | GENERIC | TS | TS | 18 | 32 | TS | TP | 23.495 | 0.63247 | 2.032 | 16
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 32 | TS | TP | 21.082 | 0.58336 | 0.381 | 16 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343180 | 47
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 32 | TP | TP | 21.463 | 0.59675 | 1.524 | 16 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 760420 | 680
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 32 | TP | TP | 19.05 | 0.55657 | 1.524 | 16 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 348040 | 694
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 32 | TS | TS | 28.956 | 0.82444 | 2.032 | 16 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337670 | 787
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 32 | TS | TP | 23.495 | 0.63247 | 2.032 | 16 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 294580 | 832
GENERIC | GENERIC | TP | TP | 18 | 36 | TP | TP | 21.336 | 0.61312 | 1.524 |  | 12 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 760300 | 682
GENERIC | GENERIC | TP | TP | 18 | 37 | TP | TP | 18.8468 | 0.73366 | 1.524
GENERIC | GENERIC | TS | TS | 18 | 37 | TS | TS | 20.32 | 0.63247 | 1.524
American Insulated Wire | American SDN® | PVC | CP | 18 | 37 | TP | TS | 19.685 | 0.57443 | 1.524 |  |  | Industrial Grade | Small Diameter Flexible Control, 600V, 90°C dry 75°C wet | 38506 | 581
Cable USA | ETFE TYPE TC | ETFE | ETFE | 18 | 37 | TP | TP | 15.875 | 0.49853 | 1.143 |  |  | Industrial Grade | Unshielded, 600V | 181837C6 | 345
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 18 | 37 | TP | TP | 18.8468 | 0.73366 | 1.524 |  |  | Industrial Grade | Unshielded, 600V | 181837C6 | 602
General Cable | VNTC® | PVC | PVC | 18 | 37 | TP | TP | 18.923 | 0.55211 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 236150 | 733
Okonite | Okozel® | ETFE | ETFE | 18 | 37 | TP | TP | 15.24 | 0.4777 | 0.508 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 203-76-3187 | 69
General Cable | EHTC® | EPR | CSPE | 18 | 37 | TS | TS | 21.082 | 0.6161 | 1.524 |  |  | Industrial Grade | Unshielded, 600V, UL Type TC | 343450 | 595
General Cable | Ultrol ® 200 Instrument Cable | XLPE | CSPE | 18 | 37 | TS | TS | 20.5486 | 0.62503 | 1.524 |  |  | Class 1E Nuclear | Unshielded, 600V, 90°C | 377660 | 725
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 37 | Sil | Fiber | 24.892 | 0.74408 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Unshielded, 600V, 125°C | I48-3300 | 220
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 37 | Sil | Fiber | 25.4 | 0.75896 | 1.016 |  |  | Class 1E Nuclear | Multi-conductor Shielded, 600V, 125°C | I48-3326 | 221
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 37 | TS | TS | 17.78 | 0.52086 | 1.143 |  |  | Industrial Grade | Multi-conductor Unshielded, 600V, 90°C, UL Type TC | I84-0372 | 534
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 37 | TS | TS | 18.288 | 0.55806 | 1.143 |  |  | Industrial Grade | Multi-conductor Shileded, 600V, 90°C, UL Type TC | I84-0371 | 535
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 37 | TS | TS | 20.32 | 0.63247 | 1.524 |  |  | Class 1E Nuclear | Unshielded, Multi-conductor, 90°C, 600V, UL Type TC | I57-0370 | 629
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 37 | TS | TS | 21.082 | 0.66967 | 1.524 |  |  | Class 1E Nuclear | Shielded, Multi-conductor, 90°C, 600V, UL Type Tc | I57-0371 | 630
GENERIC | GENERIC | TS | TS | 18 | 38 | TS | TS | 25.654 | 0.81105 | 2.032 | 19
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 38 | Sil | Fiber | 30.226 | 0.80361 | 1.016 | 19 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3369 | 230
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 38 | Sil | Fiber | 32.512 | 0.80361 | 1.016 | 19 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3389 | 240
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 38 | Sil | Fiber | 33.274 | 0.97475 | 1.016 | 19 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3285 | 250
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 38 | TS | TS | 22.606 | 0.64735 | 1.651 | 19 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0195 | 746
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 38 | TS | TS | 24.13 | 0.75896 | 1.651 | 19 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0196 | 749
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 38 | TS | TS | 24.638 | 0.80361 | 1.651 | 19 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0194 | 752
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 38 | TS | TS | 25.654 | 0.81105 | 2.032 | 19 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0192 | 809
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 38 | TS | TS | 27.432 | 0.93754 | 2.032 | 19 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0193 | 813
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 38 | TS | TS | 28.194 | 0.98963 | 2.032 | 19 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0194 | 817
GENERIC | GENERIC | TP | TP | 18 | 40 | TP | TP | 19.812 | 0.66819 | 1.524 | 20
GENERIC | GENERIC | TS | TS | 18 | 40 | TS | TP | 26.035 | 0.75896 | 2.032 | 20
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 40 | TP | TP | 19.812 | 0.66819 | 1.524 | 20 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339670 | 695
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 40 | TP | TP | 24.257 | 0.75152 | 1.778 | 20 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339800 | 760
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 40 | TS | TP | 24.257 | 0.73515 | 0.381 | 20 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343190 | 48
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 40 | TS | TS | 32.131 | 1.006 | 2.032 | 20 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337680 | 788
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 40 | TS | TP | 26.035 | 0.75896 | 2.032 | 20 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337050 | 833
GENERIC | GENERIC | TP | TP | 18 | 48 | TP | TP | 24.384 | 0.81849 | 1.778 |  | 16
GENERIC | GENERIC | TS | TS | 18 | 48 | TS | TP | 28.067 | 0.89885 | 2.032 | 24
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 48 | TP | TP | 26.416 | 0.88695 | 1.778 | 24 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339810 | 761
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 48 | TP | TP | 24.384 | 0.81849 | 1.778 |  | 16 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339980 | 763
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 48 | TP | TP | 23.241 | 0.83932 | 1.778 | 24 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339680 | 774
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 48 | TS | TP | 26.162 | 0.8676 | 0.381 | 24 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343200 | 49
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 48 | TS | TS | 36.83 | 1.1831 | 2.032 | 24 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337690 | 789
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 48 | TS | TP | 28.067 | 0.89885 | 2.032 | 24 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337060 | 834
GENERIC | GENERIC | TP | TP | 18 | 60 | TP | TP | 26.924 | 0.99409 | 1.778 |  | 20 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339990 | 764
GENERIC | GENERIC | TP | TP | 18 | 72 | TP | TP | 29.083 | 1.1682 | 1.778 |  | 24
GENERIC | GENERIC | TS | TS | 18 | 72 | TS | TP | 34.544 | 1.2873 | 2.032 | 36
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 72 | TP | TP | 30.861 | 1.259 | 1.778 | 36 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339820 | 762
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 72 | TP | TP | 29.083 | 1.1682 | 1.778 |  | 24 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340000 | 765
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 72 | TP | TP | 26.162 | 1.1712 | 1.778 | 36 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 791720 | 775
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 72 | TS | TP | 30.734 | 1.2352 | 0.381 | 36 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343210 | 50
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 72 | TS | TP | 34.544 | 1.2873 | 2.032 | 36 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337070 | 835
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 72 | TS | TS | 41.91 | 1.6638 | 2.794 | 36 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337700 | 858
GENERIC | GENERIC | TS | TS | 18 | 74 | TS | TS | 34.036 | 1.4063 | 2.032 | 37
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 74 | Sil | Fiber | 41.402 | 1.5254 | 1.016 | 37 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 125°C, 600V | I48-3370 | 231
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 74 | Sil | Fiber | 46.228 | 1.756 | 1.016 | 37 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/o Overall Shield, 125°C, 600V | I48-3390 | 241
Rockbestos-Surprenant | Firewall® III SR Instrument | SR | Rockhide | 18 | 74 | Sil | Fiber | 48.26 | 1.9346 | 1.016 | 37 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 125°C, 600V | I48-3287 | 251
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 74 | TS | TS | 30.226 | 1.1384 | 1.651 | 37 |  | Industrial Grade | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I84-0375 | 747
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 74 | TS | TS | 32.258 | 1.3766 | 1.651 | 37 |  | Industrial Grade | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I84-0376 | 750
Rockbestos-Surprenant | X-Link® TC Instrument | XLPO | XLPO | 18 | 74 | TS | TS | 33.02 | 1.4361 | 1.651 | 37 |  | Industrial Grade | Multi-Shielded Paris w/ Overall Shiled, 90°C, 600V, UL Type TC | I84-0374 | 753
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 74 | TS | TS | 34.036 | 1.4063 | 2.032 | 37 |  | Class 1E Nuclear | Multi-Unshielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57-0372 | 810
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 74 | TS | TS | 36.83 | 1.6742 | 2.032 | 37 |  | Class 1E Nuclear | Multi-Shielded Pairs w/o Overall Shield, 90°C, 600V, UL Type TC | I57-0373 | 814
Rockbestos-Surprenant | Firewall® III Instrument | XLPE | CSPE | 18 | 74 | TS | TS | 37.338 | 1.7412 | 2.032 | 37 |  | Class 1E Nuclear | Multi-Shielded Pairs w/ Overall Shield, 90°C, 600V, UL Type TC | I57- 0374 | 818
GENERIC | GENERIC | TP | TP | 18 | 100 | TP | TP | 29.972 | 1.576 | 1.778 | 50
GENERIC | GENERIC | TS | TS | 18 | 100 | TS | TP | 39.497 | 1.7025 | 2.032 | 50
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 18 | 100 | TP | TP | 29.972 | 1.576 | 1.778 | 50 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339690 | 776
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 18 | 100 | TP | TP | 36.83 | 1.7337 | 2.032 | 50 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339830 | 843
General Cable | CVTC® FR-XLP/PVC SHIELDED | XLPE | PVC | 18 | 100 | TS | TP | 36.195 | 1.7039 | 0.381 | 50 |  | Industrial Grade | Shielded UL Type PLTC 90°C SUN RES PLUS 300V | 343220 | 51
General Cable | FREP® EPR/CPE SHIELDED | EPR | CPE | 18 | 100 | TS | TP | 39.497 | 1.7025 | 2.032 | 50 |  | Industrial Grade | Shielded UL Type TC 90°C WET or DRY 600V DIR BUR SUN RES | 337080 | 836
General Cable | CHTC® XLPE/HYP INDIVIDUAL SHIELD | XLPE | CSPE | 18 | 100 | TS | TS | 52.959 | 2.4049 | 2.794 | 50 |  | Industrial Grade | Shielded (Individual & Overall) TL Type TC 600V 90°C WET or DRY SUN RES OIL RES I&II | 337710 | 859
GENERIC | GENERIC | TP | TP | 18 | 108 | TP | TP | 34.671 | 1.7129 | 2.032 |  | 36 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 340010 | 844
GENERIC | GENERIC | TP | TP | 20 | 2 | TP | TP | 3.3528 | 0.01637 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192002C3.ART | 7
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 20 | 2 | TP | TP | 3.3528 | 0.01637 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192002C3.ART | 7
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 2 | TP | TP | 5.588 | 0.041669 | 1.016 | 1 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325900 | 260
GENERIC | GENERIC | TP | TP | 20 | 3 | TP | TP | 3.5814 | 0.023811 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192003C3.ART | 8
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 20 | 3 | TP | TP | 3.5814 | 0.023811 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192003C3.ART | 8
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 3 | TP | TP | 6.1214 | 0.050598 | 1.016 |  | 1 | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325910 | 262
GENERIC | GENERIC | TP | TP | 20 | 4 | TP | TP | 6.477 | 0.061015 | 1.016 | 2 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325920 | 261
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 20 | 4 | TP | TP | 3.937 | 0.031251 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192004C3.ART | 9
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 4 | TP | TP | 8.0264 | 0.068456 | 1.016 | 2 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 325930 | 254
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 4 | TP | TP | 6.477 | 0.061015 | 1.016 | 2 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325920 | 261
GENERIC | GENERIC | TP | TP | 20 | 5 | TP | TP | 4.3434 | 0.038692 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192005C3.ART | 10
GENERIC | GENERIC | TP | TP | 20 | 6 | TP | TP | 8.636 | 0.087802 | 1.016 |  | 2 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339870 | 255
GENERIC | GENERIC | TP | TP | 20 | 7 | TP | TP | 4.7752 | 0.052086 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192007C3.ART | 11
GENERIC | GENERIC | TP | TP | 20 | 8 | TP | TP | 8.255 | 0.1131 | 1.0668 | 4 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 325950 | 266
GENERIC | GENERIC | TP | TP | 20 | 8 | TP | TP | 8.1534 | 0.096731 | 1.0668 | 4 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 325940 | 271
GENERIC | GENERIC | TP | TP | 20 | 9 | TP | TP | 5.7404 | 0.066967 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192009C3.ART | 12
GENERIC | GENERIC | TP | TP | 20 | 12 | TP | TP | 6.5024 | 0.087802 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192012C3.ART | 13
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 20 | 12 | TP | TP | 6.5024 | 0.087802 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192012C3.ART | 13
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 12 | TP | TP | 9.271 | 0.14435 | 1.016 |  | 4 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339880 | 256
GENERIC | GENERIC | TP | TP | 20 | 16 | TP | TP | 10.8204 | 0.22025 | 1.27 | 8 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339750 | 553
Cable USA | ARTICZEL PLTC Instruement Cable | ETFE | ETFE | 20 | 16 | TP | TP | 7.366 | 0.11756 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 192016C3.ART | 26
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 16 | TP | TP | 10.8204 | 0.22025 | 1.27 | 8 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339750 | 553
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 16 | TP | TP | 12.065 | 0.15477 | 1.27 | 8 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339620 | 555
GENERIC | GENERIC | TP | TP | 20 | 19 | TP | TP | 7.7978 | 0.1384 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 192019C3.ART | 27
GENERIC | GENERIC | TP | TP | 20 | 24 | TP | TP | 14.3764 | 0.27829 | 1.27 |  | 8 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339890 | 554
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 24 | TP | TP | 14.3764 | 0.27829 | 1.27 |  | 8 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339890 | 554
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 24 | TP | TP | 13.843 | 0.29019 | 1.27 | 12 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 348090 | 556
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 24 | TP | TP | 16.256 | 0.33186 | 1.524 | 12 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339760 | 683
GENERIC | GENERIC | TP | TP | 20 | 25 | TP | TP | 9.1186 | 0.18156 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 192025C3.ART | 28
GENERIC | GENERIC | TP | TP | 20 | 32 | TP | TP | 15.367 | 0.36906 | 1.27 | 16 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 334630 | 557
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 32 | TP | TP | 15.367 | 0.36906 | 1.27 | 16 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 334630 | 557
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 32 | TP | TP | 17.907 | 0.41669 | 1.524 | 16 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 348110 | 684
GENERIC | GENERIC | TP | TP | 20 | 36 | TP | TP | 17.907 | 0.4271 | 1.524 |  | 12 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339900 | 687
GENERIC | GENERIC | TP | TP | 20 | 40 | TP | TP | 16.51 | 0.45984 | 1.524 | 20 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 348100 | 696
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 40 | TP | TP | 19.812 | 0.50449 | 1.524 | 20 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339770 | 685
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 40 | TP | TP | 16.51 | 0.45984 | 1.524 | 20 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 348100 | 696
GENERIC | GENERIC | TP | TP | 20 | 48 | TP | TP | 19.812 | 0.54318 | 1.524 |  | 16 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339910 | 688
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 48 | TP | TP | 21.463 | 0.5908 | 1.524 | 24 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 339780 | 686
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 48 | TP | TP | 19.812 | 0.54318 | 1.524 |  | 16 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339910 | 688
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 48 | TP | TP | 18.796 | 0.55955 | 1.524 | 24 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 759610 | 697
GENERIC | GENERIC | TP | TP | 20 | 60 | TP | TP | 21.844 | 0.65479 | 1.524 |  | 20 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339920 | 689
GENERIC | GENERIC | TP | TP | 20 | 72 | TP | TP | 24.257 | 0.8051 | 1.778 |  | 24 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339930 | 768
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 72 | TP | TP | 21.59 | 0.78873 | 1.524 | 36 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339650 | 698
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 72 | TP | TP | 25.781 | 0.87206 | 1.778 | 36 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 348120 | 766
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 72 | TP | TP | 24.257 | 0.8051 | 1.778 |  | 24 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339930 | 768
GENERIC | GENERIC | TP | TP | 20 | 100 | TP | TP | 24.638 | 1.0611 | 1.778 | 50 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339660 | 777
General Cable | PVIC® PVC/PVC INDIVIDUAL SHIELD | PVC | PVC | 20 | 100 | TP | TP | 30.226 | 1.1697 | 1.778 | 50 |  | Industrial Grade | Shielded (Individual & Overall) UL Type PLTC or ITC 105°C SUN RES 300V | 341790 | 767
General Cable | PVIC® PVC/PVC SHIELDED | PVC | PVC | 20 | 100 | TP | TP | 24.638 | 1.0611 | 1.778 | 50 |  | Industrial Grade | Shielded UL Type PLTC or ITC 105°C SUN RES 300V | 339660 | 777
GENERIC | GENERIC | TP | TP | 20 | 108 | TP | TP | 28.321 | 1.1414 | 1.778 |  | 36 | Industrial Grade | Shielded (Individual & Overall) Triad UL Type PLTC or ITC 105°C SUN RES 300V | 339940 | 769
GENERIC | GENERIC | TP | TP | 22 | 2 | TP | TP | 2.9464 | 0.011905 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192202C3.ART | 14
GENERIC | GENERIC | TP | TP | 22 | 3 | TP | TP | 3.1496 | 0.01637 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192203C3.ART | 15
GENERIC | GENERIC | TP | TP | 22 | 4 | TP | TP | 3.4544 | 0.020834 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192204C3.ART | 16
GENERIC | GENERIC | TP | TP | 22 | 5 | TP | TP | 3.81 | 0.026787 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192205C3.ART | 17
GENERIC | GENERIC | TP | TP | 22 | 7 | TP | TP | 4.1656 | 0.035716 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192207C3.ART | 18
GENERIC | GENERIC | TP | TP | 22 | 9 | TP | TP | 5.0038 | 0.046133 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192209C3.ART | 19
GENERIC | GENERIC | TP | TP | 22 | 12 | TP | TP | 5.6642 | 0.061015 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192212C3.ART | 20
GENERIC | GENERIC | TP | TP | 22 | 16 | TP | TP | 6.3246 | 0.080361 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192216C3.ART | 21
GENERIC | GENERIC | TP | TP | 22 | 19 | TP | TP | 6.6802 | 0.093754 | 0.254 |  |  | Industrial Grade | Optional Shield & Drain | 192219C3.ART | 22
GENERIC | GENERIC | TP | TP | 22 | 25 | TP | TP | 7.8994 | 0.12352 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 192225C3.ART | 29
GENERIC | GENERIC | TP | TP | 22 | 37 | TP | TP | 9.2202 | 0.18007 | 0.3048 |  |  | Industrial Grade | Optional Shield & Drain | 192237C3.ART | 30
GENERIC | GENERIC | TP | TP | 22 | 40 | TP | TP | 9.7536 | 0.19793 | 0.381 |  |  | Industrial Grade | Optional Shield & Drain | 192240C3.ART | 32
GENERIC | GENERIC | TP | TP | 22 | 50 | TP | TP | 10.795 | 0.24406 | 0.381 |  |  | Industrial Grade | Optional Shield & Drain | 192250C3.ART | 33

## Power (hidden)
Manufacturer | Cable Model | insul | jacket | AWG | #/C | Insulation Type | Jacket Type | OD mm | Kg/m | Jkt (mm) | Grade | Comments | Part # | Item #
GENERIC | GENERIC | TS | TS | 1 | 1 | TS | TS | 13.462 | 0.52087 | 1.143 |  |  |  |  | AWG | #/C | AWG | 1 | 2 | 4 | 6 | 8 | 10 | 12 | 14 | 250 | 300 | 350 | 400 | 450 | 500 | 550 | 600 | 650 | 700 | 750 | 1000 | 1/0 | 2/0 | 3/0 | 4/0
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 1 | 1 | TS | N/A | 12.446 | 0.48367 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3560 | 2 | 1 | 1 |  | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 1 | 2 | 1 | 2 | 3 | 1 | 3 | 3 | 3 | 3 | 1 | 1 | 1 | 1 | 1 | 1
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 1 | 1 | TS | N/A | 11.176 | 0.4539 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3516 | 19 | 2 | 2 |  | 2 | 2 | 2 | 2 | 2 | 3 | 3 | 3 | 2 | 3 | 2 | 3 | 4 | 2 | 3+G | 3+G | 3+G | 3+G | 3 | 3+G | 2 | 2 | 2 | 2
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 1 | 1 | Sil | Fiber | 14.732 | 0.50599 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3017 | 65 | 4 | 3 |  | 3 | 3 | 3 | 3 | 3 | 4 | 4 | 4 | 3 | 4 | 3 | 4 | 3+G | 3 |  |  |  |  | 4 |  | 3 | 3 | 3 | 3
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 1 | 1 | TS | TS | 13.462 | 0.52087 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-9 | P68-0010 | 111 | 6 | 4 |  | 4 | 4 | 4 | 4 | 4 |  |  |  | 4 | 3+G | 4 | 3+G |  | 4 |  |  |  |  | 3+G |  | 4 | 4 | 4 | 4
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 1 | 1 | TS | TS | 13.462 | 0.52087 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-5091 | 116 | 8 | 5 |  | 3+G | 5 | 5 | 5 | 5 |  |  |  | 3+G |  | 3+G |  |  | 3+G | [6 empty] | 3+G | 3+G | 3+G | 3+G
GENERIC | GENERIC | TS | TP | 1 | 2 | TS | TP | 27.94 | 1.2203 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218120 | 392 | 10 | 6 |  |  | 3+G | 3+G | 3+G | 6
American Insulated Wire | TYPE TC Power | XLPE | PVC | 1 | 2 | TS | TP | 27.051 | 1.2054 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 488 | 12 | 7 | [5 empty] | 7
Draka | General Purpose Control XLPE | XLPE | PVC | 1 | 2 | TS | TP | 27.94 | 1.2203 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218120 | 392 | 14 | 3+G | [5 empty] | 3+G
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 1 | 2 | TS | TP | 31.242 | 1.8394 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 258120 | 413 | 250
GENERIC | GENERIC | TP | TP | 1 | 3 | TP | TP | 28.194 | 1.7903 | 2.032 |  |  |  |  | 300
GENERIC | GENERIC | TS | TS | 1 | 3 | TS | TP | 29.21 | 1.7129 | 2.032 |  |  |  |  | 350
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 1 | 3 | TP | TP | 28.194 | 1.7903 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68165 | 510 | 400
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 1 | 3 | TP | TP | 28.194 | 1.6698 | 2.032 | Industrial Grade | Unshielded, 600V | 17733 | 522 | 450
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 1 | 3 | TP | TP | 29.972 | 1.8216 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18131 | 432 | 500
American Insulated Wire | TYPE TC Power | XLPE | PVC | 1 | 3 | TS | TP | 28.702 | 1.5775 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 489 | 550
Draka | General Purpose Control XLPE | XLPE | PVC | 1 | 3 | TS | TP | 29.21 | 1.7129 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 213130 | 393 | 600
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 1 | 3 | TS | TP | 34.29 | 2.3275 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 258130 | 414 | 650
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 1 | 3 | TS | TP | 31.115 | 1.9719 | 2.032 | Industrial Grade | Shielded (Copper), 600V, 90°C | 158149 | 429 | 700
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 1 | 3 | TS | TP | 29.21 | 1.7129 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118130 | 461 | 750
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 1 | 3 | TS | TP | 31.242 | 1.8394 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 158130 | 462 | 1000
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 1 | 3 | TS | TS | 28.448 | 1.2977 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 366070 | 323 | 1/0
General Cable | CVTC® | XLPE | PVC | 1 | 3 | TS | TP | 28.448 | 1.7844 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 352150 | 336 | 2/0
General Cable | EHTC® | EPR | CSPE | 1 | 3 | TS | TS | 28.448 | 1.2977 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 366220 | 349 | 3/0
General Cable | EHTC® | EPR | CSPE | 1 | 3 | TS | TS | 28.448 | 1.5195 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 297730 | 350 | 4/0
General Cable | Ultrol® 325 | XLPE | CSPE | 1 | 3 | TS | TS | 26.8986 | 1.7963 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379130 | 534
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 1 | 3 | Sil | Fiber | 31.496 | 1.89 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3031 | 66
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 1 | 3 | TS | TS | 26.416 | 1.6742 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0013 | 293
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 1 | 3 | TS | TS | 28.194 | 1.9198 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-3119 | 377
GENERIC | GENERIC | TP | TP | 1 | 4 | TP | TP | 30.988 | 2.3246 | 2.032
GENERIC | GENERIC | TS | TS | 1 | 4 | TS | TS | 31.369 | 2.2636 | 2.032
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 1 | 4 | TP | TP | 30.988 | 2.3246 | 2.032 | Industrial Grade | Unshielded, 600V | 2601 | 523
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 1 | 4 | TP | TP | 33.02 | 2.2531 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18141 | 434
American Insulated Wire | TYPE TC Power | XLPE | PVC | 1 | 4 | TS | TP | 31.623 | 2.3067 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 490
Draka | General Purpose Control XLPE | XLPE | PVC | 1 | 4 | TS | TP | 32.258 | 2.1936 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218140 | 395
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 1 | 4 | TS | TP | 34.29 | 2.3275 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 158140 | 463
Draka | Power & Control Type TC XHHW-3 | XLPE | PVC | 1 | 4 | TS | TP | 32.258 | 2.1936 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118140 | 487
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 1 | 4 | TS | TS | 31.369 | 1.6906 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 366080 | 324
General Cable | CVTC® | XLPE | PVC | 1 | 4 | TS | TP | 31.369 | 2.5359 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 371250 | 337
General Cable | EHTC® | EPR | CSPE | 1 | 4 | TS | TS | 31.369 | 1.6906 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 366230 | 351
General Cable | EHTC® | EPR | CSPE | 1 | 4 | TS | TS | 31.369 | 2.2636 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 365740 | 352
General Cable | Ultrol® 325 | XLPE | CSPE | 1 | 4 | TS | TS | 29.6418 | 2.2814 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379140 | 535
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 1 | 4 | Sil | Fiber | 35.052 | 2.4481 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3043 | 67
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 1 | 4 | TS | TS | 29.21 | 2.1505 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0014 | 294
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 1 | 4 | TS | TS | 31.242 | 2.4109 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5039 | 378
GENERIC | GENERIC | TP | TP | 1 | 3+G | TP | TP | 29.21 | 1.823 | 2.032
GENERIC | GENERIC | TS | TS | 1 | 3+G | TS | TP | 31.115 | 1.9719 | 2.032
Draka | Power & Control Type TC 3 XHHW-2 1 bare | PVC | PVC | 1 | 3+G | TP | TP | 29.21 | 1.823 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118149 | 424
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 1 | 3+G | TP | TP | 29.972 | 1.9585 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18149 | 433
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 1 | 3+G | TS | TP | 32.004 | 2.3811 | 1.27 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295071 | 135
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 1 | 3+G | TS | TP | 32.004 | 1.9644 | 1.27 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295071 | 136
Draka | General Purpose Control 3 XLPE 1 Bare | XLPE | PVC | 1 | 3+G | TS | TP | 31.115 | 1.9719 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 258149 | 389
Draka | General Purpose Control XLPE | XLPE | PVC | 1 | 3+G | TS | TP | 29.21 | 1.823 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218149 | 394
GENERIC | GENERIC | TS | TS | 2 | 1 | TS | N/A | 10.414 | 0.37205 | 0
Continental | SIS Switchboard Wire | XLPE | N/A | 2 | 1 | TS | N/A | 9.8044 | 0.34526 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 35
Continental | SIS Switchboard Wire | XLPE | N/A | 2 | 1 | TS | N/A | 10.8966 | 0.35717 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 36
Continental | XHHW CONTROL WIRE | XLPO |  | 2 | 1 | TS | None | 9.8806 | 0.3527 | 1.143 | Industrial Grade | Single Conductor, 600V, 90°C |  | 126
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 2 | 1 | TS | N/A | 10.414 | 0.37205 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3559 | 3
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 2 | 1 | TS | N/A | 9.652 | 0.35717 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3515 | 20
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 2 | 1 | TS | TS | 11.176 | 0.38693 | 0.762 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-8 | P68-0020 | 51
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 2 | 1 | TS | TS | 11.176 | 0.39437 | 0.762 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3973 | 54
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 2 | 1 | Sil | Fiber | 12.446 | 0.38693 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3016 | 68
GENERIC | GENERIC | TP | TP | 2 | 2 | TP | TP | 25.019 | 0.99561 | 2.032
GENERIC | GENERIC | TS | TS | 2 | 2 | TS | TP | 24.765 | 1.0001 | 2.032
Draka | General Purpose Control XLPE | XLPE | PVC | 2 | 2 | TS | TP | 24.765 | 1.0001 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 215020 | 396
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 2 | 2 | TS | TP | 26.289 | 1.1281 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 255020 | 415
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2 | 2 | TS | TP | 24.765 | 1.0001 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 115020 | 464
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2 | 2 | TS | TP | 26.289 | 1.1281 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 155020 | 465
GENERIC | GENERIC | TP | TP | 2 | 3 | TP | TP | 28.321 | 1.4778 | 2.032
GENERIC | GENERIC | TS | TS | 2 | 3 | TS | TS | 25.654 | 1.457 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 2 | 3 | TP | TP | 25.019 | 1.5314 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68163 | 511
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 2 | 3 | TP | TP | 25.019 | 1.4108 | 2.032 | Industrial Grade | Unshielded, 600V | 68155 | 524
Draka | 20-10 Control Cable Shielded | PE | PVC | 2 | 3 | TP | TP | 31.115 | 1.6013 | 2.032 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76331 | 308
Draka | 20-10 Control Cable Shielded | PE | PVC | 2 | 3 | TP | TP | 32.258 | 1.637 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78331 | 309
Draka | Power & Control 3 THHN/THWN | PVC | PVC | 2 | 3 | TP | TP | 26.67 | 1.518 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 15047 | 422
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 2 | 3 | TP | TP | 26.67 | 1.3959 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 15033 | 436
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 2 | 3 | TP | TP | 28.321 | 1.5299 | 2.032 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 15603 | 453
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 2 | 3 | TP | TP | 28.321 | 1.4778 | 2.032 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 15803 | 454
General Cable | VNTC® | PVC | PVC | 2 | 3 | TP | TP | 25.4 | 1.0566 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 236420 | 547
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 2 | 3 | TS | TS | 25.654 | 1.6817 | 1.524 | Industrial Grade | with Ground, Unshielded, 600V | 31033 | 257
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 2 | 3 | TS | TP | 24.765 | 1.4376 | 1.524 | Industrial Grade | Unshielded, 600V | 40826 | 279
American Insulated Wire | TYPE TC Power | XLPE | PVC | 2 | 3 | TS | TP | 25.273 | 1.3319 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 491
Draka | General Purpose Control XLPE | XLPE | PVC | 2 | 3 | TS | TP | 26.289 | 1.3617 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 215030 | 397
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 2 | 3 | TS | TP | 27.94 | 1.4986 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 255030 | 416
Draka | Power & Control Type TC 3 XHHW-2 1 bare | XLPE | PVC | 2 | 3 | TS | TP | 26.67 | 1.518 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 15047 | 426
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 2 | 3 | TS | TP | 27.94 | 1.6281 | 2.032 | Industrial Grade | Shielded (Copper), 600V, 90°C | 155049 | 430
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2 | 3 | TS | TP | 26.289 | 1.3617 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 115030 | 466
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2 | 3 | TS | TP | 27.94 | 1.4986 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 155030 | 467
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 2 | 3 | TS | TS | 25.908 | 1.0656 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282640 | 325
General Cable | CVTC® | XLPE | PVC | 2 | 3 | TS | TP | 25.4 | 1.4346 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 325610 | 338
General Cable | EHTC® | EPR | CSPE | 2 | 3 | TS | TS | 25.654 | 1.457 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 293600 | 353
General Cable | EHTC® | EPR | CSPE | 2 | 3 | TS | TS | 25.908 | 1.0656 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338700 | 354
General Cable | Ultrol® 325 | XLPE | CSPE | 2 | 3 | TS | TS | 24.8158 | 1.4703 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379110 | 536
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 2 | 3 | Sil | Fiber | 25.654 | 1.3989 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3030 | 69
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 2 | 3 | TS | TS | 23.114 | 1.3617 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0023 | 295
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 2 | 3 | TS | TS | 25.146 | 1.5552 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0024 | 379
GENERIC | GENERIC | TP | TP | 2 | 4 | TP | TP | 35.433 | 2.0775 | 2.032
GENERIC | GENERIC | TS | TS | 2 | 4 | Sil | Fiber | 28.702 | 1.8082 | 1.016
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 2 | 4 | TP | TP | 27.559 | 1.9153 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68164 | 512
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 2 | 4 | TP | TP | 27.559 | 1.7948 | 2.032 | Industrial Grade | Unshielded, 600V | 68156 | 525
Draka | 20-10 Control Cable Shielded | PE | PVC | 2 | 4 | TP | TP | 34.163 | 2.0374 | 2.032 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76341 | 310
Draka | 20-10 Control Cable Shielded | PE | PVC | 2 | 4 | TP | TP | 35.433 | 2.0775 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78341 | 311
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 2 | 4 | TP | TP | 29.337 | 1.7873 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 15043 | 437
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 2 | 4 | TP | TP | 31.115 | 2.149 | 2.032 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 15604 | 455
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 2 | 4 | TP | TP | 31.115 | 2.0909 | 2.032 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 15804 | 456
General Cable | VNTC® | PVC | PVC | 2 | 4 | TP | TP | 27.94 | 1.3677 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 236430 | 548
American Insulated Wire | TYPE TC Power | XLPE | PVC | 2 | 4 | TS | TP | 27.813 | 1.7338 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 492
Draka | General Purpose Control XLPE | XLPE | PVC | 2 | 4 | TS | TP | 28.956 | 1.7486 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 215040 | 399
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 2 | 4 | TS | TP | 30.48 | 1.9168 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 255040 | 417
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2 | 4 | TS | TP | 28.956 | 1.7486 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 115040 | 468
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2 | 4 | TS | TP | 30.48 | 1.9168 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 154040 | 469
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 2 | 4 | TS | TS | 28.448 | 1.3677 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282650 | 326
General Cable | CVTC® | XLPE | PVC | 2 | 4 | TS | TP | 27.813 | 1.8067 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 329520 | 339
General Cable | EHTC® | EPR | CSPE | 2 | 4 | TS | TS | 27.686 | 1.8379 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 285890 | 355
General Cable | EHTC® | EPR | CSPE | 2 | 4 | TS | TS | 28.448 | 1.3677 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338710 | 356
General Cable | Ultrol® 325 | XLPE | CSPE | 2 | 4 | TS | TS | 27.305 | 1.8543 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379120 | 537
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 2 | 4 | Sil | Fiber | 28.702 | 1.8082 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3042 | 70
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 2 | 4 | TS | TS | 25.654 | 1.7412 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0024 | 296
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 2 | 4 | TS | TS | 27.686 | 1.957 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5124 | 380
GENERIC | GENERIC | TP | TP | 2 | 5 | TP | TP | 32.258 | 2.1966 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 15053 | 438
GENERIC | GENERIC | TP | TP | 2 | 3+G | TP | TP | 26.67 | 1.518 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 115049 | 425
GENERIC | GENERIC | TS | TS | 2 | 3+G | TS | TP | 27.94 | 1.6281 | 2.032
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 2 | 3+G | TS | TP | 28.702 | 1.9644 | 1.27 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295067 | 137
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 2 | 3+G | TS | TP | 28.702 | 1.6073 | 1.27 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295067 | 138
Draka | General Purpose Control 3 XLPE 1 Bare | XLPE | PVC | 2 | 3+G | TS | TP | 27.94 | 1.6281 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 256049 | 390
Draka | General Purpose Control XLPE | XLPE | PVC | 2 | 3+G | TS | TP | 26.289 | 1.4748 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 216049 | 398
GENERIC | GENERIC | TS | TS | 4 | 1 | TS | N/A | 9.144 | 0.22621 | 0
Continental | SIS Switchboard Wire | XLPE | N/A | 4 | 1 | TS | N/A | 8.2804 | 0.21728 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 37
Continental | SIS Switchboard Wire | XLPE | N/A | 4 | 1 | TS | N/A | 9.144 | 0.22621 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 38
Continental | XHHW CONTROL WIRE | XLPO |  | 4 | 1 | TS | None | 8.3566 | 0.23067 | 1.143 | Industrial Grade | Single Conductor, 600V, 90°C |  | 127
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 4 | 1 | TS | N/A | 8.89 | 0.25299 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3558 | 4
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 4 | 1 | TS | N/A | 8.128 | 0.23811 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3514 | 21
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 4 | 1 | TS | TS | 9.906 | 0.26788 | 0.762 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-7 | P68-0040 | 52
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 4 | 1 | TS | TS | 9.906 | 0.27532 | 0.762 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-5090 | 55
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 4 | 1 | Sil | Fiber | 11.176 | 0.26044 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3015 | 71
GENERIC | GENERIC | TP | TP | 4 | 2 | TP | TP | 20.701 | 0.65034 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 14023 | 214
GENERIC | GENERIC | TS | TS | 4 | 2 | TS | TP | 20.447 | 0.65034 | 1.524
Draka | General Purpose Control XLPE | XLPE | PVC | 4 | 2 | TS | TP | 20.447 | 0.65034 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 214020 | 189
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4 | 2 | TS | TP | 20.447 | 0.65034 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 114020 | 233
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 4 | 2 | TS | TP | 23.241 | 0.81851 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 254020 | 418
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4 | 2 | TS | TP | 23.241 | 0.81851 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 154020 | 470
GENERIC | GENERIC | TP | TP | 4 | 3 | TP | TP | 24.892 | 1.0373 | 2.032
GENERIC | GENERIC | TS | TS | 4 | 3 | TS | TP | 22.225 | 0.9718 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 4 | 3 | TP | TP | 20.828 | 1.0477 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68161 | 513
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 4 | 3 | TP | TP | 20.828 | 0.9718 | 2.032 | Industrial Grade | Unshielded, 600V | 68153 | 526
Draka | 20-10 Control Cable Shielded | PE | PVC | 4 | 3 | TP | TP | 27.686 | 1.1474 | 2.032 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76231 | 312
Draka | 20-10 Control Cable Shielded | PE | PVC | 4 | 3 | TP | TP | 28.702 | 1.2114 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78231 | 313
Draka | Power & Control 3 THHN/THWN | PVC | PVC | 4 | 3 | TP | TP | 23.114 | 1.0432 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 14047 | 423
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 4 | 3 | TP | TP | 23.114 | 0.96733 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 14033 | 439
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 4 | 3 | TP | TP | 24.892 | 1.0819 | 2.032 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 14603 | 457
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 4 | 3 | TP | TP | 24.892 | 1.0373 | 2.032 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 14803 | 458
General Cable | VNTC® | PVC | PVC | 4 | 3 | TP | TP | 22.225 | 0.66374 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 236400 | 549
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 4 | 3 | TS | TS | 22.352 | 1.1757 | 1.524 | Industrial Grade | with Ground, Unshielded, 600V | 31032 | 258
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 4 | 3 | TS | TP | 20.574 | 0.98221 | 1.524 | Industrial Grade | Unshielded, 600V | 40825 | 280
American Insulated Wire | TYPE TC Power | XLPE | PVC | 4 | 3 | TS | TP | 21.971 | 0.93459 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 493
Draka | General Purpose Control XLPE | XLPE | PVC | 4 | 3 | TS | TP | 21.844 | 0.88846 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 214030 | 190
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 4 | 3 | TS | TP | 24.511 | 1.0745 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 254030 | 419
Draka | Power & Control Type TC 3 XHHW-2 1 bare | XLPE | PVC | 4 | 3 | TS | TP | 23.114 | 1.0432 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 14047 | 428
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 4 | 3 | TS | TP | 24.511 | 1.134 | 2.032 | Industrial Grade | Shielded (Copper), 600V, 90°C | 154049 | 431
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4 | 3 | TS | TP | 23.114 | 0.94352 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 114030 | 471
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4 | 3 | TS | TP | 24.511 | 1.0745 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 154030 | 472
General Cable | Ultrol® 325 | XLPE | CSPE | 4 | 3 | TS | TS | 20.574 | 1.012 | 1.524 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379090 | 269
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 4 | 3 | TS | TS | 22.606 | 0.66672 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282620 | 327
General Cable | CVTC® | XLPE | PVC | 4 | 3 | TS | TP | 22.225 | 0.9718 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 325660 | 340
General Cable | EHTC® | EPR | CSPE | 4 | 3 | TS | TS | 22.352 | 0.95543 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 283200 | 357
General Cable | EHTC® | EPR | CSPE | 4 | 3 | TS | TS | 22.606 | 0.66672 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 261010 | 358
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 4 | 3 | Sil | Fiber | 22.606 | 0.94501 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3029 | 72
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 4 | 3 | TS | TS | 18.796 | 0.8706 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0043 | 130
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 4 | 3 | TS | TS | 20.828 | 1.0194 | 1.524 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0044 | 181
GENERIC | GENERIC | TP | TP | 4 | 4 | TP | TP | 27.051 | 1.2843 | 2.032
GENERIC | GENERIC | TS | TS | 4 | 4 | TS | TP | 24.13 | 1.2203 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 4 | 4 | TP | TP | 24.003 | 1.3081 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68162 | 514
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 4 | 4 | TP | TP | 24.003 | 1.2322 | 2.032 | Industrial Grade | Unshielded, 600V | 68154 | 527
Draka | 20-10 Control Cable Shielded | PE | PVC | 4 | 4 | TP | TP | 30.226 | 1.4614 | 2.032 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76241 | 314
Draka | 20-10 Control Cable Shielded | PE | PVC | 4 | 4 | TP | TP | 31.496 | 1.5061 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78241 | 315
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 4 | 4 | TP | TP | 25.4 | 1.2099 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 14043 | 440
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 4 | 4 | TP | TP | 27.051 | 1.3334 | 2.032 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 14604 | 459
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 4 | 4 | TP | TP | 27.051 | 1.2843 | 2.032 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 14804 | 460
General Cable | VNTC® | PVC | PVC | 4 | 4 | TP | TP | 24.638 | 0.86018 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 236410 | 550
American Insulated Wire | TYPE TC Power | XLPE | PVC | 4 | 4 | TS | TP | 24.13 | 1.1876 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 494
Draka | General Purpose Control XLPE | XLPE | PVC | 4 | 4 | TS | TP | 25.146 | 1.195 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 214040 | 192
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 4 | 4 | TS | TP | 26.797 | 1.3438 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 254040 | 420
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4 | 4 | TS | TP | 25.146 | 1.195 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 114040 | 473
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4 | 4 | TS | TP | 26.797 | 1.3438 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 154040 | 474
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 4 | 4 | TS | TS | 24.765 | 0.86018 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282630 | 328
General Cable | CVTC® | XLPE | PVC | 4 | 4 | TS | TP | 24.13 | 1.2203 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339500 | 341
General Cable | EHTC® | EPR | CSPE | 4 | 4 | TS | TS | 24.13 | 1.2233 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 295390 | 359
General Cable | EHTC® | EPR | CSPE | 4 | 4 | TS | TS | 24.765 | 0.86018 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338690 | 360
General Cable | Ultrol® 325 | XLPE | CSPE | 4 | 4 | TS | TS | 23.6728 | 1.2665 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379100 | 538
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 4 | 4 | Sil | Fiber | 24.892 | 1.2203 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3041 | 73
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 4 | 4 | TS | TS | 21.844 | 1.1682 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0044 | 297
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 4 | 4 | TS | TS | 23.876 | 1.3171 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5038 | 381
GENERIC | GENERIC | TP | TP | 4 | 5 | TP | TP | 27.94 | 1.4882 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 14053 | 441
GENERIC | GENERIC | TP | TP | 4 | 3+G | TP | TP | 23.114 | 1.0432 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 114049 | 427
GENERIC | GENERIC | TS | TS | 4 | 3+G | TS | TP | 24.511 | 1.134 | 2.032
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 4 | 3+G | TS | TP | 25.4 | 1.4436 | 1.27 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295063 | 139
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 4 | 3+G | TS | TP | 25.4 | 1.131 | 1.27 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295063 | 140
Draka | General Purpose Control XLPE | XLPE | PVC | 4 | 3+G | TS | TP | 21.844 | 0.95691 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 214049 | 191
Draka | General Purpose Control 3 XLPE 1 Bare | XLPE | PVC | 4 | 3+G | TS | TP | 24.511 | 1.134 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 254049 | 391
GENERIC | GENERIC | TS | TS | 6 | 1 | TS | N/A | 7.62 | 0.1637 | 0
Continental | SIS Switchboard Wire | XLPE | N/A | 6 | 1 | TS | N/A | 7.0612 | 0.15031 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 39
Continental | SIS Switchboard Wire | XLPE | N/A | 6 | 1 | TS | N/A | 7.7216 | 0.15626 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 40
Continental | XHHW CONTROL WIRE | XLPO |  | 6 | 1 | TS | None | 7.1374 | 0.15328 | 1.143 | Industrial Grade | Single Conductor, 600V, 90°C |  | 128
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 6 | 1 | TS | N/A | 7.62 | 0.1637 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3557 | 5
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 6 | 1 | TS | N/A | 6.858 | 0.15626 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3488 | 22
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 6 | 1 | TS | TS | 8.636 | 0.17858 | 0.762 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-6 | P68-0060 | 53
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 6 | 1 | TS | TS | 8.636 | 0.18603 | 0.762 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3847 | 56
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 6 | 1 | Sil | Fiber | 9.906 | 0.17858 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3014 | 74
GENERIC | GENERIC | TP | TP | 6 | 2 | TP | TP | 16.0528 | 0.43902 | 1.524
GENERIC | GENERIC | TS | TS | 6 | 2 | TS | TP | 17.907 | 0.45539 | 1.524
Cable USA | ETFE TYPE TC | ETFE | ETFE | 6 | 2 | TP | TP | 15.1892 | 0.38396 | 1.143 | Industrial Grade | Unshielded, 600V | 180602C6 | 104
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 6 | 2 | TP | TP | 16.0528 | 0.43902 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 167
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 6 | 2 | TP | TP | 16.8148 | 0.47176 | 1.524 | Industrial Grade | Unshielded, 600V | 180602C6 | 174
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 6 | 2 | TP | TP | 16.891 | 0.43456 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 13023 | 215
Draka | General Purpose Control XLPE | XLPE | PVC | 6 | 2 | TS | TP | 17.907 | 0.45539 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 213020 | 193
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 6 | 2 | TS | TP | 19.685 | 0.56254 | 1.524 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 253020 | 201
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 6 | 2 | TS | TP | 17.907 | 0.45539 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 113020 | 234
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 6 | 2 | TS | TP | 19.685 | 0.56254 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 153020 | 235
GENERIC | GENERIC | TP | TP | 6 | 3 | TP | TP | 19.685 | 0.65332 | 1.524
GENERIC | GENERIC | TS | TS | 6 | 3 | TS | TS | 18.796 | 0.67862 | 1.524
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 6 | 3 | TP | TP | 16.891 | 0.67118 | 1.524 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68159 | 261
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 6 | 3 | TP | TP | 16.891 | 0.59528 | 1.524 | Industrial Grade | Unshielded, 600V | 68151 | 265
Cable USA | ETFE TYPE TC | ETFE | ETFE | 6 | 3 | TP | TP | 16.2306 | 0.53873 | 1.143 | Industrial Grade | Unshielded, 600V | 180603C6 | 105
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 6 | 3 | TP | TP | 17.2466 | 0.63397 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 168
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 6 | 3 | TP | TP | 17.907 | 0.63993 | 1.524 | Industrial Grade | Unshielded, 600V | 180603C6 | 175
Draka | Power & Control 3 THHN/THWN | PVC | PVC | 6 | 3 | TP | TP | 18.669 | 0.79768 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 13047 | 206
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 6 | 3 | TP | TP | 18.034 | 0.59677 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 13033 | 216
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 6 | 3 | TP | TP | 19.685 | 0.68904 | 1.524 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 13603 | 225
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 6 | 3 | TP | TP | 19.685 | 0.65332 | 1.524 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 13803 | 226
Draka | 20-10 Control Cable Shielded | PE | PVC | 6 | 3 | TP | TP | 24.892 | 0.8706 | 2.032 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76131 | 316
Draka | 20-10 Control Cable Shielded | PE | PVC | 6 | 3 | TP | TP | 25.908 | 0.90483 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78131 | 317
General Cable | VNTC® | PVC | PVC | 6 | 3 | TP | TP | 17.526 | 0.44646 | 1.524 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 226410 | 274
American Insulated Wire | TYPE TC Power | XLPE | PVC | 6 | 3 | TS | TP | 18.415 | 0.61016 | 1.524 | Industrial Grade | Unshielded, 600V | ES08231 | 253
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 6 | 3 | TS | TS | 19.05 | 0.78875 | 1.524 | Industrial Grade | with Ground, Unshielded, 600V | 31031 | 259
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 6 | 3 | TS | TP | 18.034 | 0.67564 | 1.524 | Industrial Grade | Unshielded, 600V | 40824 | 281
Draka | General Purpose Control XLPE | XLPE | PVC | 6 | 3 | TS | TP | 19.05 | 0.61463 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 213030 | 194
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 6 | 3 | TS | TP | 20.828 | 0.73517 | 1.524 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 253030 | 202
Draka | Power & Control Type TC 3 XHHW-2 1 bare | XLPE | PVC | 6 | 3 | TS | TP | 18.669 | 0.79768 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 13047 | 209
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 6 | 3 | TS | TP | 20.955 | 0.79768 | 1.524 | Industrial Grade | Shielded (Copper), 600V, 90°C | 153049 | 212
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 6 | 3 | TS | TP | 19.05 | 0.61463 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 113030 | 236
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 6 | 3 | TS | TP | 20.828 | 0.73517 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 153030 | 237
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 6 | 3 | TS | TS | 18.923 | 0.44795 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282600 | 150
General Cable | CVTC® | XLPE | PVC | 6 | 3 | TS | TP | 18.288 | 0.66225 | 1.524 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339470 | 154
General Cable | EHTC® | EPR | CSPE | 6 | 3 | TS | TS | 18.796 | 0.67862 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 283210 | 158
General Cable | EHTC® | EPR | CSPE | 6 | 3 | TS | TS | 18.923 | 0.44795 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 366210 | 159
General Cable | Ultrol® 325 | XLPE | CSPE | 6 | 3 | TS | TS | 17.9832 | 0.68606 | 1.524 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379070 | 270
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 6 | 3 | Sil | Fiber | 19.812 | 0.68457 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3028 | 75
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 6 | 3 | TS | TS | 15.748 | 0.61016 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0063 | 131
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 6 | 3 | TS | TS | 18.288 | 0.75898 | 1.524 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0064 | 182
GENERIC | GENERIC | TP | TP | 6 | 4 | TP | TP | 21.463 | 0.81702 | 1.524
GENERIC | GENERIC | TS | TS | 6 | 4 | TS | TP | 20.066 | 0.83042 | 1.524
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 6 | 4 | TP | TP | 18.542 | 0.82893 | 1.524 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68160 | 262
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 6 | 4 | TP | TP | 18.542 | 0.75303 | 1.524 | Industrial Grade | Unshielded, 600V | 68152 | 266
Cable USA | ETFE TYPE TC | ETFE | ETFE | 6 | 4 | TP | TP | 17.8308 | 0.69797 | 1.143 | Industrial Grade | Unshielded, 600V | 180604C6 | 106
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 6 | 4 | TP | TP | 19.3548 | 0.84679 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 169
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 6 | 4 | TP | TP | 19.6088 | 0.81107 | 1.524 | Industrial Grade | Unshielded, 600V | 180604C6 | 176
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 6 | 4 | TP | TP | 19.812 | 0.75601 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 13043 | 217
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 6 | 4 | TP | TP | 21.463 | 0.85721 | 1.524 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 13604 | 227
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 6 | 4 | TP | TP | 21.463 | 0.81702 | 1.524 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 13804 | 228
Draka | 20-10 Control Cable Shielded | PE | PVC | 6 | 4 | TP | TP | 27.051 | 1.0745 | 2.032 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76141 | 318
Draka | 20-10 Control Cable Shielded | PE | PVC | 6 | 4 | TP | TP | 28.321 | 1.1162 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78141 | 319
General Cable | VNTC® | PVC | PVC | 6 | 4 | TP | TP | 19.304 | 0.56998 | 1.524 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 231980 | 275
American Insulated Wire | TYPE TC Power | XLPE | PVC | 6 | 4 | TS | TP | 20.193 | 0.78131 | 1.524 | Industrial Grade | Unshielded, 600V | ES08231 | 254
Draka | General Purpose Control XLPE | XLPE | PVC | 6 | 4 | TS | TP | 20.955 | 0.78577 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 213040 | 196
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 6 | 4 | TS | TP | 20.955 | 0.78577 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 113040 | 238
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 6 | 4 | TS | TP | 23.749 | 0.95989 | 2.032 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 253040 | 421
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 6 | 4 | TS | TP | 23.749 | 0.95989 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 153040 | 475
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 6 | 4 | TS | TS | 20.828 | 0.57147 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282610 | 151
General Cable | CVTC® | XLPE | PVC | 6 | 4 | TS | TP | 20.066 | 0.83042 | 1.524 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339480 | 155
General Cable | EHTC® | EPR | CSPE | 6 | 4 | TS | TS | 20.066 | 0.83488 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 300380 | 160
General Cable | EHTC® | EPR | CSPE | 6 | 4 | TS | TS | 20.828 | 0.57147 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338680 | 161
General Cable | Ultrol® 325 | XLPE | CSPE | 6 | 4 | TS | TS | 19.7866 | 0.85274 | 1.524 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379080 | 271
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 6 | 4 | Sil | Fiber | 22.098 | 0.8706 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3040 | 76
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 6 | 4 | TS | TS | 17.526 | 0.76642 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0064 | 132
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 6 | 4 | TS | TS | 20.066 | 0.9078 | 1.524 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5037 | 183
GENERIC | GENERIC | TP | TP | 6 | 5 | TP | TP | 21.5138 | 1.0447 | 2.032
Cable USA | ETFE TYPE TC | ETFE | ETFE | 6 | 5 | TP | TP | 19.7104 | 0.85721 | 1.524 | Industrial Grade | Unshielded, 600V | 180605C6 | 166
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 6 | 5 | TP | TP | 21.5138 | 1.0447 | 2.032 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 375
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 6 | 5 | TP | TP | 22.606 | 1.0611 | 2.032 | Industrial Grade | Unshielded, 600V | 180605C6 | 376
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 6 | 5 | TP | TP | 21.717 | 0.93162 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 13053 | 218
GENERIC | GENERIC | TP | TP | 6 | 3+G | TP | TP | 18.669 | 0.79768 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 113049 | 208
GENERIC | GENERIC | TS | TS | 6 | 3+G | TS | TP | 20.955 | 0.79768 | 1.524
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 6 | 3+G | TS | TP | 21.844 | 1.0566 | 1.27 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295059 | 141
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 6 | 3+G | TS | TP | 21.844 | 0.81851 | 1.27 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295059 | 142
Draka | General Purpose Control 3 XLPE 1 Bare | XLPE | PVC | 6 | 3+G | TS | TP | 20.955 | 0.79768 | 1.524 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 253049 | 187
Draka | General Purpose Control XLPE | XLPE | PVC | 6 | 3+G | TS | TP | 19.05 | 0.68309 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 213049 | 195
GENERIC | GENERIC | TS | TS | 8 | 1 | TS | N/A | 6.858 | 0.1131 | 0
Continental | SIS Switchboard Wire | XLPE | N/A | 8 | 1 | TS | N/A | 6.1722 | 0.10269 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 41
Continental | SIS Switchboard Wire | XLPE | N/A | 8 | 1 | TS | N/A | 6.7056 | 0.10715 | 0 | Industrial Grade | Single Conductor, 600V, 90°C |  | 42
Continental | XHHW CONTROL WIRE | XLPO |  | 8 | 1 | TS | None | 6.1722 | 0.10269 | 1.143 | Industrial Grade | Single Conductor, 600V, 90°C |  | 129
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 8 | 1 | TS | N/A | 6.858 | 0.1131 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3556 | 6
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 8 | 1 | TS | N/A | 6.096 | 0.10417 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3513 | 23
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 8 | 1 | TS | TS | 7.112 | 0.11906 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-5 | P68-0080 | 43
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 8 | 1 | TS | TS | 7.112 | 0.11906 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3848 | 47
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 8 | 1 | Sil | Fiber | 8.89 | 0.1265 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3013 | 77
GENERIC | GENERIC | TP | TP | 8 | 2 | TP | TP | 14.986 | 0.28574 | 1.524
GENERIC | GENERIC | TS | TS | 8 | 2 | TS | TP | 15.875 | 0.29615 | 1.524
Cable USA | ETFE TYPE TC | ETFE | ETFE | 8 | 2 | TP | TP | 12.2936 | 0.24258 | 1.143 | Industrial Grade | Unshielded, 600V | 180802C6 | 107
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 8 | 2 | TP | TP | 10.922 | 0.2396 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 170
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 8 | 2 | TP | TP | 14.6812 | 0.34824 | 1.524 | Industrial Grade | Unshielded, 600V | 180802C6 | 177
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 8 | 2 | TP | TP | 14.986 | 0.28574 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 12023 | 219
Draka | General Purpose Control XLPE | XLPE | PVC | 8 | 2 | TS | TP | 15.875 | 0.29615 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 212020 | 197
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 8 | 2 | TS | TP | 17.653 | 0.4286 | 1.524 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 252020 | 203
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 8 | 2 | TS | TP | 15.875 | 0.29615 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 112020 | 239
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 8 | 2 | TS | TP | 17.653 | 0.4286 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 152020 | 240
GENERIC | GENERIC | TP | TP | 8 | 3 | TP | TP | 15.5956 | 0.46283 | 1.524
GENERIC | GENERIC | TS | TS | 8 | 3 | TS | TS | 16.637 | 0.4673 | 1.524
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 8 | 3 | TP | TP | 15.113 | 0.46878 | 1.524 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68157 | 263
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 8 | 3 | TP | TP | 15.113 | 0.42116 | 1.524 | Industrial Grade | Unshielded, 600V | 68149 | 267
Cable USA | ETFE TYPE TC | ETFE | ETFE | 8 | 3 | TP | TP | 13.9192 | 0.37205 | 1.143 | Industrial Grade | Unshielded, 600V | 180803C6 | 108
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 8 | 3 | TP | TP | 11.7094 | 0.34377 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 171
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 8 | 3 | TP | TP | 15.5956 | 0.46283 | 1.524 | Industrial Grade | Unshielded, 600V | 180803C6 | 178
Draka | 20-10 Control Cable Shielded | PE | PVC | 8 | 3 | TP | TP | 20.447 | 0.58189 | 1.524 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76031 | 149
Draka | Power & Control 3 THHN/THWN | PVC | PVC | 8 | 3 | TP | TP | 16.51 | 0.48069 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 12047 | 207
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 8 | 3 | TP | TP | 15.875 | 0.42711 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 12033 | 220
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 8 | 3 | TP | TP | 17.653 | 0.51045 | 1.524 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 12603 | 229
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 8 | 3 | TP | TP | 17.653 | 0.4792 | 1.524 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 12803 | 230
Draka | 20-10 Control Cable Shielded | PE | PVC | 8 | 3 | TP | TP | 23.495 | 0.68457 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78031 | 320
General Cable | VNTC® | PVC | PVC | 8 | 3 | TP | TP | 15.24 | 0.28127 | 1.524 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 236370 | 276
General Cable | VNTC® CAROLFIRE | PVC | PVC | 8 | 3 | TP | TP | 15.24 | 0.45837 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, UL Type TC-ER | 236370 | 278
American Insulated Wire | TYPE TC Power | XLPE | PVC | 8 | 3 | TS | TP | 16.383 | 0.43902 | 1.524 | Industrial Grade | Unshielded, 600V | ES08231 | 255
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 8 | 3 | TS | TS | 16.637 | 0.5804 | 1.524 | Industrial Grade | with Ground, Unshielded, 600V | 31030 | 260
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 8 | 3 | TS | TP | 16.1544 | 0.47325 | 1.524 | Industrial Grade | Unshielded, 600V | 40823 | 282
Draka | General Purpose Control XLPE | XLPE | PVC | 8 | 3 | TS | TP | 16.891 | 0.44051 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 212030 | 198
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 8 | 3 | TS | TP | 18.669 | 0.54319 | 1.524 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 252030 | 204
Draka | Power & Control Type TC 3 XHHW-2 1 bare | XLPE | PVC | 8 | 3 | TS | TP | 16.51 | 0.48069 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 12047 | 211
Draka | Power & Control Type TC 3 XHHW-2 1 bare Shield | XLPE | PVC | 8 | 3 | TS | TP | 18.542 | 0.58338 | 1.524 | Industrial Grade | Shielded (Copper), 600V, 90°C | 152049 | 213
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 8 | 3 | TS | TP | 16.891 | 0.44051 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 112030 | 241
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 8 | 3 | TS | TP | 18.669 | 0.54319 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 152030 | 242
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 8 | 3 | TS | TS | 16.764 | 0.28276 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282580 | 152
General Cable | CVTC® | XLPE | PVC | 8 | 3 | TS | TP | 16.256 | 0.4673 | 1.524 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 783160 | 156
General Cable | EHTC® | EPR | CSPE | 8 | 3 | TS | TS | 16.637 | 0.4673 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279660 | 162
General Cable | EHTC® | EPR | CSPE | 8 | 3 | TS | TS | 16.764 | 0.28276 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 261000 | 163
General Cable | Ultrol® 325 | XLPE | CSPE | 8 | 3 | TS | TS | 15.9766 | 0.47027 | 1.524 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379050 | 272
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 8 | 3 | Sil | Fiber | 17.78 | 0.47623 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3027 | 78
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 8 | 3 | TS | TS | 13.716 | 0.40926 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0083 | 133
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 8 | 3 | TS | TS | 16.256 | 0.52831 | 1.524 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0084 | 184
Rockbestus-Sup | CAROLFIRE | XLPE | CSPE | 8 | 3 | TS | TS | 16.256 | 0.52831 | 0 |  |  | P62-0084 | 1
GENERIC | GENERIC | TP | TP | 8 | 4 | TP | TP | 19.177 | 0.58486 | 1.524
GENERIC | GENERIC | TS | TS | 8 | 4 | TS | TP | 18.542 | 0.56998 | 1.524
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 8 | 4 | TP | TP | 16.51 | 0.57147 | 1.524 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68158 | 264
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 8 | 4 | TP | TP | 16.51 | 0.52385 | 1.524 | Industrial Grade | Unshielded, 600V | 68150 | 268
Cable USA | ETFE TYPE TC | ETFE | ETFE | 8 | 4 | TP | TP | 15.2654 | 0.47771 | 1.143 | Industrial Grade | Unshielded, 600V | 180804C6 | 109
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 8 | 4 | TP | TP | 12.9286 | 0.44646 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 172
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 8 | 4 | TP | TP | 17.0434 | 0.5804 | 1.524 | Industrial Grade | Unshielded, 600V | 180804C6 | 179
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 8 | 4 | TP | TP | 16.891 | 0.53873 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 12043 | 221
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 8 | 4 | TP | TP | 19.177 | 0.62058 | 1.524 | Industrial Grade | Shielded Copper, 600V, 90°C dry, 75°C wet | 12604 | 231
Draka | Power & Control Type TC THHN OR THWN Shield | PVC | PVC | 8 | 4 | TP | TP | 19.177 | 0.58486 | 1.524 | Industrial Grade | Shielded Alum, 600V, 90°C dry, 75°C wet | 12804 | 232
Draka | 20-10 Control Cable Shielded | PE | PVC | 8 | 4 | TP | TP | 23.368 | 0.76047 | 2.032 | Industrial Grade | Shielded Corrugated Copper, 600V, 75°C | 76041 | 321
Draka | 20-10 Control Cable Shielded | PE | PVC | 8 | 4 | TP | TP | 25.654 | 0.80363 | 2.032 | Industrial Grade | Shielded, 1000V, 75°C | 78041 | 322
General Cable | VNTC® | PVC | PVC | 8 | 4 | TP | TP | 16.637 | 0.35866 | 1.524 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 236380 | 277
American Insulated Wire | TYPE TC Power | XLPE | PVC | 8 | 4 | TS | TP | 17.907 | 0.55212 | 1.524 | Industrial Grade | Unshielded, 600V | ES08231 | 256
Draka | General Purpose Control XLPE | XLPE | PVC | 8 | 4 | TS | TP | 18.542 | 0.56998 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 212040 | 200
Draka | General Purpose Control XLPE Shield | XLPE | PVC | 8 | 4 | TS | TP | 20.193 | 0.66076 | 1.524 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 202040 | 205
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 8 | 4 | TS | TP | 18.542 | 0.56998 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 112040 | 243
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 8 | 4 | TS | TP | 20.193 | 0.66076 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 152040 | 244
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 8 | 4 | TS | TS | 18.415 | 0.36015 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282590 | 153
General Cable | CVTC® | XLPE | PVC | 8 | 4 | TS | TP | 17.907 | 0.57296 | 1.524 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 783190 | 157
General Cable | EHTC® | EPR | CSPE | 8 | 4 | TS | TS | 18.288 | 0.58486 | 1.524 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 279670 | 164
General Cable | EHTC® | EPR | CSPE | 8 | 4 | TS | TS | 18.415 | 0.36015 | 1.524 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338670 | 165
General Cable | Ultrol® 325 | XLPE | CSPE | 8 | 4 | TS | TS | 17.526 | 0.58189 | 1.524 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379060 | 273
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 8 | 4 | Sil | Fiber | 19.812 | 0.61016 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3039 | 79
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 8 | 4 | TS | TS | 15.24 | 0.52087 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0084 | 134
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 8 | 4 | TS | TS | 17.78 | 0.63993 | 1.524 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5036 | 185
GENERIC | GENERIC | TP | TP | 8 | 5 | TP | TP | 16.8148 | 0.58635 | 1.143 | Industrial Grade | Unshielded, 600V | 180805C6 | 110
Cable USA | ETFE TYPE TC | ETFE | ETFE | 8 | 5 | TP | TP | 16.8148 | 0.58635 | 1.143 | Industrial Grade | Unshielded, 600V | 180805C6 | 110
Cable USA | FEP Insulated Instrument/Control Cable | FEP | FEP | 8 | 5 | TP | TP | 14.3256 | 0.55064 | 1.524 | Industrial Grade | Optional Shield & Drain, 600V, 300°C |  | 173
Cable USA | FEP(Teflon) TYPE TC | FEP | FEP | 8 | 5 | TP | TP | 18.6944 | 0.70094 | 1.524 | Industrial Grade | Unshielded, 600V | 180805C6 | 180
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 8 | 5 | TP | TP | 19.05 | 0.63546 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 12053 | 222
GENERIC | GENERIC | TP | TP | 8 | 6 | TP | TP | 20.701 | 0.75452 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 12063 | 223
GENERIC | GENERIC | TP | TP | 8 | 7 | TP | TP | 20.701 | 0.83935 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 12073 | 224
GENERIC | GENERIC | TP | TP | 8 | 3+G | TP | TP | 16.51 | 0.48069 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 112049 | 210
GENERIC | GENERIC | TS | TS | 8 | 3+G | TS | TP | 18.542 | 0.58338 | 1.524
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 8 | 3+G | TS | TP | 19.812 | 0.81851 | 1.27 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295055 | 143
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 8 | 3+G | TS | TP | 19.812 | 0.61016 | 1.27 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295055 | 144
Draka | General Purpose Control 3 XLPE 1 Bare | XLPE | PVC | 8 | 3+G | TS | TP | 18.542 | 0.58338 | 1.524 | Industrial Grade | Shielded (Copper Tape), 600V, 90° | 252049 | 188
Draka | General Purpose Control XLPE | XLPE | PVC | 8 | 3+G | TS | TP | 16.891 | 0.47771 | 1.524 | Industrial Grade | Unshielded, 600V, 90°C | 212049 | 199
GENERIC | GENERIC | TS | TS | 10 | 1 | TS | TS | 5.6388 | 0.07441 | 0.381
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 10 | 1 | TS | N/A | 5.334 | 0.069946 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3555 | 7
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 10 | 1 | TS | N/A | 4.572 | 0.059528 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3340 | 24
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 10 | 1 | TS | TS | 5.588 | 0.07441 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-4 | P68-0110 | 44
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 10 | 1 | TS | TS | 5.6388 | 0.07441 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3922 | 48
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 10 | 1 | Sil | Fiber | 7.366 | 0.081851 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3065 | 80
GENERIC | GENERIC | TS | TS | 10 | 3 | TS | TS | 10.414 | 0.27532 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0113 | 59
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 10 | 3 | TS | TS | 10.414 | 0.27532 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0113 | 59
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 10 | 3 | TS | TS | 11.938 | 0.34973 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0144 | 121
GENERIC | GENERIC | TS | TS | 10 | 4 | TS | TS | 11.43 | 0.3274 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0114 | 60
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 10 | 4 | TS | TS | 11.43 | 0.3274 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0114 | 60
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 10 | 4 | TS | TS | 13.97 | 0.44646 | 1.524 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0116 | 186
GENERIC | GENERIC | TS | TS | 12 | 1 | TS | TS | 5.08 | 0.052087 | 0.381
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 12 | 1 | TS | N/A | 4.572 | 0.049111 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3554 | 8
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 12 | 1 | TS | N/A | 3.81 | 0.04167 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3328 | 25
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 12 | 1 | TS | TS | 5.08 | 0.052087 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-3 | P68-0120 | 45
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 12 | 1 | TS | TS | 5.08 | 0.052087 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3835 | 49
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 12 | 1 | Sil | Fiber | 6.604 | 0.059528 | 0.889 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3064 | 57
GENERIC | GENERIC | TS | TS | 12 | 3 | TS | TS | 9.144 | 0.18603 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0123 | 61
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 12 | 3 | TS | TS | 9.144 | 0.18603 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0123 | 61
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 12 | 3 | TS | TS | 10.668 | 0.25299 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0124 | 122
GENERIC | GENERIC | TS | TS | 12 | 4 | TS | TS | 10.16 | 0.22323 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0124 | 62
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 12 | 4 | TS | TS | 10.16 | 0.22323 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0124 | 62
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 12 | 4 | TS | TS | 11.938 | 0.29764 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0126 | 123
GENERIC | GENERIC | TS | TS | 14 | 1 | TS | TS | 4.572 | 0.037205 | 0.381
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 14 | 1 | TS | N/A | 4.064 | 0.034229 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3553 | 9
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 14 | 1 | TS | N/A | 3.302 | 0.028276 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3350 | 26
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 14 | 1 | TS | TS | 4.572 | 0.037205 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-2 | P68-0140 | 46
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 14 | 1 | TS | TS | 4.572 | 0.037205 | 0.381 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3834 | 50
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 14 | 1 | Sil | Fiber | 6.096 | 0.044646 | 0.889 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3063 | 58
GENERIC | GENERIC | TS | TS | 14 | 3 | TS | TS | 8.128 | 0.1265 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0143 | 63
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 14 | 3 | TS | TS | 8.128 | 0.1265 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0143 | 63
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 14 | 3 | TS | TS | 9.652 | 0.18603 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0144 | 124
GENERIC | GENERIC | TS | TS | 14 | 4 | TS | TS | 8.89 | 0.15626 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0144 | 64
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 14 | 4 | TS | TS | 8.89 | 0.15626 | 0.889 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0144 | 64
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 14 | 4 | TS | TS | 10.668 | 0.22323 | 1.143 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0146 | 125
GENERIC | GENERIC | TS | TS | 250 | 1 | Sil | Fiber | 21.336 | 1.3691 | 1.016
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 250 | 1 | TS | N/A | 19.304 | 1.3394 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3565 | 10
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 250 | 1 | TS | N/A | 17.78 | 1.2799 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3521 | 27
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 250 | 1 | Sil | Fiber | 21.336 | 1.3691 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3022 | 81
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 250 | 1 | TS | TS | 21.082 | 1.4212 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-14 | P68-0250 | 283
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 250 | 1 | TS | TS | 21.082 | 1.4287 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3954 | 288
GENERIC | GENERIC | TS | TP | 250 | 2 | TS | TP | 40.513 | 3.4407 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 495
GENERIC | GENERIC | TP | TP | 250 | 3 | TP | TP | 44.196 | 3.7116 | 2.794
GENERIC | GENERIC | TS | TS | 250 | 3 | TS | TP | 44.831 | 4.7965 | 2.794
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 250 | 3 | TP | TP | 41.402 | 4.9393 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68173 | 515
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 250 | 3 | TP | TP | 41.402 | 4.7474 | 2.794 | Industrial Grade | Unshielded, 600V | 17748 | 663
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 250 | 3 | TP | TP | 46.736 | 4.8307 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18631 | 602
General Cable | VNTC® | PVC | PVC | 250 | 3 | TP | TP | 44.196 | 3.7116 | 2.794 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 222490 | 676
American Insulated Wire | TYPE TC Power | XLPE | PVC | 250 | 3 | TS | TP | 44.831 | 4.7965 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 639
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 250 | 3 | TS | TS | 45.593 | 5.3203 | 2.794 | Industrial Grade | with Ground, Unshielded, 600V | 32673 | 654
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 250 | 3 | TS | TP | 43.942 | 4.8709 | 2.794 | Industrial Grade | Unshielded, 600V | 40974 | 683
Draka | General Purpose Control XLPE | XLPE | PVC | 250 | 3 | TS | TP | 46.736 | 4.7176 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218630 | 400
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 250 | 3 | TS | TP | 46.736 | 4.7176 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 118630 | 629
General Cable | Ultrol® 325 | XLPE | CSPE | 250 | 3 | TS | TS | 42.1132 | 4.7533 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379230 | 539
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 250 | 3 | TS | TS | 44.577 | 3.7116 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 338890 | 559
General Cable | CVTC® | XLPE | PVC | 250 | 3 | TS | TP | 44.45 | 4.6759 | 2.794 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 328540 | 566
General Cable | EHTC® | EPR | CSPE | 250 | 3 | TS | TS | 44.577 | 3.7116 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338780 | 573
General Cable | EHTC® | EPR | CSPE | 250 | 3 | TS | TS | 44.704 | 4.7384 | 2.794 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 300780 | 574
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 250 | 3 | Sil | Fiber | 46.736 | 4.8218 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3036 | 82
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 250 | 3 | TS | TS | 44.196 | 5.0376 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-3422 | 586
GENERIC | GENERIC | TP | TP | 250 | 4 | TP | TP | 49.403 | 4.8828 | 2.794
GENERIC | GENERIC | TS | TS | 250 | 4 | TS | TS | 48.641 | 5.9811 | 2.794
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 250 | 4 | TP | TP | 47.371 | 6.3219 | 2.794 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68174 | 657
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 250 | 4 | TP | TP | 47.371 | 6.1299 | 2.794 | Industrial Grade | Unshielded, 600V | 23569 | 664
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 250 | 4 | TP | TP | 51.816 | 6.1269 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18641 | 604
General Cable | VNTC® | PVC | PVC | 250 | 4 | TP | TP | 49.403 | 4.8828 | 2.794 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 297050 | 677
American Insulated Wire | TYPE TC Power | XLPE | PVC | 250 | 4 | TS | TP | 49.403 | 6.0674 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 640
Draka | General Purpose Control XLPE | XLPE | PVC | 250 | 4 | TS | TP | 50.292 | 6.0213 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 218640 | 594
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 250 | 4 | TS | TP | 50.292 | 6.0213 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 118640 | 631
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 250 | 4 | TS | TS | 49.149 | 4.8843 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 338900 | 560
General Cable | CVTC® | XLPE | PVC | 250 | 4 | TS | TP | 49.022 | 6.0242 | 2.794 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339590 | 567
General Cable | EHTC® | EPR | CSPE | 250 | 4 | TS | TS | 48.641 | 5.9811 | 2.794 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 346990 | 575
General Cable | EHTC® | EPR | CSPE | 250 | 4 | TS | TS | 49.149 | 4.8843 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338790 | 576
General Cable | Ultrol® 325 | XLPE | CSPE | 250 | 4 | TS | TS | 48.2092 | 6.1031 | 2.794 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379240 | 669
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 250 | 4 | Sil | Fiber | 52.07 | 6.2505 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3048 | 83
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 250 | 4 | TS | TS | 48.768 | 6.2951 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5044 | 587
GENERIC | GENERIC | TP | TP | 250 | 3+G | TP | TP | 46.736 | 5.0525 | 2.794
GENERIC | GENERIC | TS | TS | 250 | 3+G | TS | TP | 48.006 | 5.0301 | 1.524
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 250 | 3+G | TS | TP | 48.006 | 5.6254 | 1.524 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295086 | 245
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 250 | 3+G | TS | TP | 48.006 | 5.0301 | 1.524 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295086 | 246
Draka | General Purpose Control XLPE | XLPE | PVC | 250 | 3+G | TS | TP | 46.736 | 4.9111 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218649 | 401
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 250 | 3+G | TS | TP | 46.736 | 4.9111 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 118649 | 630
GENERIC | GENERIC | TS | TP | 300 | 2 | TS | TP | 44.831 | 3.8812 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 641
GENERIC | GENERIC | TS | TP | 300 | 3 | TS | TP | 47.625 | 5.8367 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 642
American Insulated Wire | TYPE TC Power | XLPE | PVC | 300 | 3 | TS | TP | 47.625 | 5.8367 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 642
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 300 | 3 | TP | TP | 50.038 | 5.6611 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18731 | 605
GENERIC | GENERIC | TS | TP | 300 | 4 | TS | TP | 52.705 | 7.0853 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 643
GENERIC | GENERIC | TP | TP | 300 | 4 | TP | TP | 55.372 | 7.191 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18741 | 607
GENERIC | GENERIC | TP | TP | 300 | 3+G | TP | TP | 50.038 | 5.8814 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18749 | 606
GENERIC | GENERIC | TS | TS | 350 | 1 | TS | N/A | 21.844 | 1.8156 | 0
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 350 | 1 | TS | N/A | 21.844 | 1.8156 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3566 | 11
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 350 | 1 | TS | N/A | 20.32 | 1.7561 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3522 | 28
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 350 | 1 | Sil | Fiber | 24.13 | 1.8603 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3023 | 84
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 350 | 1 | TS | TS | 23.876 | 1.9198 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-15 | P68-0350 | 284
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 350 | 1 | TS | TS | 23.876 | 1.9347 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3846 | 289
GENERIC | GENERIC | TS | TP | 350 | 2 | TS | TP | 47.371 | 4.3694 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 644
GENERIC | GENERIC | TP | TP | 350 | 3 | TP | TP | 50.419 | 6.176 | 2.794
GENERIC | GENERIC | TS | TS | 350 | 3 | TS | TP | 51.562 | 6.3264 | 2.794
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 350 | 3 | TP | TP | 48.514 | 6.4216 | 2.794 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68175 | 658
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 350 | 3 | TP | TP | 50.419 | 6.176 | 2.794 | Industrial Grade | Unshielded, 600V | 17750 | 665
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 350 | 3 | TP | TP | 52.832 | 6.4915 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18831 | 608
General Cable | VNTC® | PVC | PVC | 350 | 3 | TP | TP | 50.546 | 5.17 | 2.794 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 226430 | 678
American Insulated Wire | TYPE TC Power | XLPE | PVC | 350 | 3 | TS | TP | 50.419 | 6.249 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 645
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 350 | 3 | TS | TS | 51.181 | 7.2327 | 2.794 | Industrial Grade | with Ground, Unshielded, 600V | 31999 | 655
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 350 | 3 | TS | TP | 49.657 | 6.5317 | 2.794 | Industrial Grade | Unshielded, 600V | 40975 | 684
Draka | General Purpose Control XLPE | XLPE | PVC | 350 | 3 | TS | TP | 51.562 | 6.3264 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 218830 | 595
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 350 | 3 | TS | TP | 58.42 | 6.3264 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 118840 | 632
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 350 | 3 | TS | TS | 51.054 | 5.1745 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282690 | 561
General Cable | CVTC® | XLPE | PVC | 350 | 3 | TS | TP | 50.038 | 6.2951 | 2.794 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 222570 | 568
General Cable | EHTC® | EPR | CSPE | 350 | 3 | TS | TS | 49.784 | 6.2311 | 2.794 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 325120 | 577
General Cable | EHTC® | EPR | CSPE | 350 | 3 | TS | TS | 51.054 | 5.1745 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338800 | 578
General Cable | Ultrol® 325 | XLPE | CSPE | 350 | 3 | TS | TS | 54.5084 | 6.429 | 2.794 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379250 | 670
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 350 | 3 | Sil | Fiber | 52.578 | 6.5481 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3037 | 85
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 350 | 3 | TS | TS | 49.784 | 6.6002 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0354 | 588
GENERIC | GENERIC | TP | TP | 350 | 4 | TP | TP | 55.626 | 6.8249 | 2.794
GENERIC | GENERIC | TS | TS | 350 | 4 | TS | TP | 55.753 | 8.1509 | 2.794
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 350 | 4 | TP | TP | 53.34 | 8.4753 | 2.794 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68176 | 659
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 350 | 4 | TP | TP | 58.674 | 8.258 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18841 | 610
General Cable | VNTC® | PVC | PVC | 350 | 4 | TP | TP | 55.626 | 6.8249 | 2.794 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 297060 | 679
American Insulated Wire | TYPE TC Power | XLPE | PVC | 350 | 4 | TS | TP | 55.753 | 8.1509 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 646
Draka | General Purpose Control XLPE | XLPE | PVC | 350 | 4 | TS | TP | 56.896 | 8.1926 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 218840 | 597
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 350 | 4 | TS | TP | 56.896 | 8.1926 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 118849 | 634
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 350 | 4 | TS | TS | 55.372 | 6.8115 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 338910 | 562
General Cable | CVTC® | XLPE | PVC | 350 | 4 | TS | TP | 55.372 | 8.1405 | 2.794 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339600 | 569
General Cable | EHTC® | EPR | CSPE | 350 | 4 | TS | TS | 54.991 | 8.0899 | 2.794 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 347000 | 579
General Cable | EHTC® | EPR | CSPE | 350 | 4 | TS | TS | 55.372 | 6.8115 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338810 | 580
General Cable | Ultrol® 325 | XLPE | CSPE | 350 | 4 | TS | TS | 49.276 | 8.3116 | 2.794 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379260 | 671
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 350 | 4 | Sil | Fiber | 59.944 | 7.2922 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3049 | 86
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 350 | 4 | TS | TS | 55.118 | 8.4828 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5045 | 589
GENERIC | GENERIC | TP | TP | 350 | 3+G | TP | TP | 52.832 | 6.7133 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18849 | 609
GENERIC | GENERIC | TS | TS | 350 | 3+G | TS | TP | 53.848 | 6.7118 | 1.524
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 350 | 3+G | TS | TP | 53.848 | 7.3964 | 1.524 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295092 | 247
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 350 | 3+G | TS | TP | 53.848 | 6.7118 | 1.524 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295092 | 248
Draka | General Purpose Control XLPE | XLPE | PVC | 350 | 3+G | TS | TP | 51.562 | 6.5258 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 218849 | 596
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 350 | 3+G | TS | TP | 58.42 | 6.5258 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 118830 | 633
GENERIC | GENERIC | TS | TP | 400 | 2 | TS | TP | 49.911 | 4.9557 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 647
GENERIC | GENERIC | TP | TP | 400 | 3 | TP | TP | 55.626 | 7.3234 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18931 | 611
GENERIC | GENERIC | TS | TP | 400 | 3 | TS | TP | 52.959 | 7.2952 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 648
American Insulated Wire | TYPE TC Power | XLPE | PVC | 400 | 3 | TS | TP | 52.959 | 7.2952 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 648
GENERIC | GENERIC | TS | TP | 400 | 4 | TS | TP | 58.674 | 9.3965 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 649
GENERIC | GENERIC | TP | TP | 400 | 4 | TP | TP | 61.722 | 9.3266 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18941 | 613
GENERIC | GENERIC | TP | TP | 400 | 3+G | TP | TP | 55.626 | 7.5437 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18949 | 612
GENERIC | GENERIC | TP | TP | 450 | 3 | TP | TP | 58.166 | 8.139 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19031 | 614
GENERIC | GENERIC | TP | TP | 450 | 4 | TP | TP | 64.516 | 10.3758 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19041 | 616
GENERIC | GENERIC | TP | TP | 450 | 3+G | TP | TP | 58.166 | 8.4917 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19049 | 615
GENERIC | GENERIC | TS | TS | 500 | 1 | TS | N/A | 25.146 | 2.5597 | 0
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 500 | 1 | TS | N/A | 25.146 | 2.5597 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3567 | 12
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 500 | 1 | TS | N/A | 23.622 | 2.4853 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3523 | 29
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 500 | 1 | Sil | Fiber | 27.432 | 2.5969 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3024 | 87
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 500 | 1 | TS | TS | 27.178 | 2.6639 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-16 | P68-0510 | 285
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 500 | 1 | TS | TS | 27.178 | 2.6788 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3806 | 290
GENERIC | GENERIC | TS | TP | 500 | 2 | TS | TP | 53.975 | 5.9885 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 650
GENERIC | GENERIC | TP | TP | 500 | 3 | TP | TP | 55.118 | 8.8995 | 2.794
GENERIC | GENERIC | TS | TS | 500 | 3 | TS | TS | 58.293 | 9.8519 | 2.794
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 500 | 3 | TP | TP | 51.054 | 7.3592 | 2.794 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68177 | 660
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 500 | 3 | TP | TP | 55.118 | 8.8995 | 2.794 | Industrial Grade | Unshielded, 600V | 23568 | 666
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 500 | 3 | TP | TP | 60.452 | 8.9396 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19131 | 617
General Cable | VNTC® | PVC | PVC | 500 | 3 | TP | TP | 57.658 | 7.3428 | 2.794 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 219630 | 680
American Insulated Wire | TYPE TC Power | XLPE | PVC | 500 | 3 | TS | TP | 57.531 | 8.9143 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 651
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 500 | 3 | TS | TS | 58.293 | 9.8519 | 2.794 | Industrial Grade | with Ground, Unshielded, 600V | 31468 | 656
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 500 | 3 | TS | TP | 56.134 | 9.0691 | 2.794 | Industrial Grade | Unshielded, 600V | 40976 | 685
Draka | General Purpose Control XLPE | XLPE | PVC | 500 | 3 | TS | TP | 58.928 | 8.7343 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 219130 | 598
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 500 | 3 | TS | TP | 58.928 | 8.7343 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 119130 | 635
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 500 | 3 | TS | TS | 58.547 | 7.3487 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282710 | 563
General Cable | CVTC® | XLPE | PVC | 500 | 3 | TS | TP | 57.15 | 8.6747 | 2.794 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 222710 | 570
General Cable | EHTC® | EPR | CSPE | 500 | 3 | TS | TS | 57.023 | 8.7015 | 2.794 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 298020 | 581
General Cable | EHTC® | EPR | CSPE | 500 | 3 | TS | TS | 58.547 | 7.3487 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338820 | 582
General Cable | Ultrol® 325 | XLPE | CSPE | 500 | 3 | TS | TS | 56.3372 | 8.7849 | 2.794 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379270 | 672
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 500 | 3 | Sil | Fiber | 66.294 | 8.3339 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3038 | 88
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 500 | 3 | TS | TS | 56.896 | 9.212 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0504 | 590
GENERIC | GENERIC | TP | TP | 500 | 4 | TP | TP | 63.627 | 9.6867 | 2.794
GENERIC | GENERIC | TS | TS | 500 | 4 | TS | TS | 64.897 | 9.6867 | 2.794
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 500 | 4 | TP | TP | 57.15 | 9.5885 | 2.794 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68178 | 661
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 500 | 4 | TP | TP | 61.214 | 11.4115 | 2.794 | Industrial Grade | Unshielded, 600V | 26012 | 667
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 500 | 4 | TP | TP | 67.056 | 11.4071 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19141 | 618
General Cable | VNTC® | PVC | PVC | 500 | 4 | TP | TP | 63.627 | 9.6867 | 2.794 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 222510 | 681
American Insulated Wire | TYPE TC Power | XLPE | PVC | 500 | 4 | TS | TP | 63.754 | 11.4383 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 652
Draka | General Purpose Control XLPE | XLPE | PVC | 500 | 4 | TS | TP | 69.596 | 11.4115 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 219140 | 600
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 500 | 4 | TS | TP | 69.596 | 11.4115 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 119140 | 637
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 500 | 4 | TS | TS | 64.897 | 9.6867 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 331150 | 564
General Cable | CVTC® | XLPE | PVC | 500 | 4 | TS | TP | 62.865 | 11.2791 | 2.794 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 6790.0865 | 571
General Cable | EHTC® | EPR | CSPE | 500 | 4 | TS | TS | 64.897 | 9.6867 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338830 | 583
General Cable | Ultrol® 325 | XLPE | CSPE | 500 | 4 | TS | TS | 62.4332 | 11.3788 | 2.794 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379280 | 673
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 500 | 4 | Sil | Fiber | 73.914 | 9.2269 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3050 | 89
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 500 | 4 | TS | TS | 62.992 | 11.6824 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5046 | 591
GENERIC | GENERIC | TP | TP | 500 | 3+G | TP | TP | 60.452 | 9.2923 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19149 | 619
GENERIC | GENERIC | TS | TS | 500 | 3+G | TS | TP | 61.976 | 9.2864 | 1.905
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 500 | 3+G | TS | TP | 61.976 | 10.0751 | 1.905 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295101 | 304
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 500 | 3+G | TS | TP | 61.976 | 9.2864 | 1.905 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295101 | 305
Draka | General Purpose Control XLPE | XLPE | PVC | 500 | 3+G | TS | TP | 58.928 | 9.0661 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 219149 | 599
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 500 | 3+G | TS | TP | 58.928 | 9.0661 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 119149 | 636
GENERIC | GENERIC | TS | TP | 500 | 3+G | TS | TP | 58.928 | 9.0661 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 119149 | 636
GENERIC | GENERIC | TP | TP | 550 | 3 | TP | TP | 62.738 | 9.8102 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19231 | 620
GENERIC | GENERIC | TP | TP | 550 | 3+G | TP | TP | 62.738 | 10.1317 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19249 | 621
GENERIC | GENERIC | TP | TP | 600 | 3 | TP | TP | 65.024 | 10.5796 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19331 | 622
GENERIC | GENERIC | TP | TP | 600 | 3+G | TP | TP | 65.024 | 10.8981 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19349 | 623
GENERIC | GENERIC | TP | TP | 650 | 3 | TP | TP | 67.056 | 11.4026 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19431 | 624
GENERIC | GENERIC | TP | TP | 650 | 3+G | TP | TP | 67.056 | 11.7136 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19449 | 625
GENERIC | GENERIC | TP | TP | 700 | 3 | TP | TP | 68.834 | 12.1958 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19531 | 626
GENERIC | GENERIC | TP | TP | 700 | 3+G | TP | TP | 68.834 | 12.5039 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19549 | 627
GENERIC | GENERIC | TS | TS | 750 | 1 | Sil | Fiber | 32.766 | 3.8619 | 1.016
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 750 | 1 | TS | N/A | 30.48 | 3.8172 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3568 | 13
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 750 | 1 | TS | N/A | 28.956 | 3.7279 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3524 | 30
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 750 | 1 | Sil | Fiber | 32.766 | 3.8619 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3025 | 90
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 750 | 1 | TS | TS | 32.512 | 3.9289 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-17 | P68-0750 | 286
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 750 | 1 | TS | TS | 32.512 | 3.9437 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-5094 | 291
GENERIC | GENERIC | TP | TP | 750 | 3 | TP | TP | 72.644 | 13.0277 | 3.556
GENERIC | GENERIC | TS | TS | 750 | 3 | TS | TS | 68.58 | 13.5873 | 2.794
Draka | General Purpose Control XLPE | XLPE | PVC | 750 | 3 | TS | TP | 72.644 | 12.992 | 3.556 | Industrial Grade | Unshielded, 600V, 90°C | 219649 | 688
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 750 | 3 | TS | TP | 72.644 | 12.992 | 3.556 | Industrial Grade | Unshielded, 600V, 90°C | 119630 | 692
General Cable | Ultrol® 325 | XLPE | CSPE | 750 | 3 | TS | TS | 67.818 | 13.1423 | 2.794 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379290 | 674
General Cable | CVTC® | XLPE | PVC | 750 | 3 | TS | TP | 71.374 | 13.5441 | 3.556 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 6790.077 | 686
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 750 | 3 | TS | TS | 68.58 | 13.5873 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-3423 | 592
GENERIC | GENERIC | TS | TP | 750 | 4 | TS | TP | 79.121 | 17.4804 | 3.556 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 6790.047 | 687
GENERIC | GENERIC | TS | TS | 750 | 4 | TS | TS | 76.835 | 17.0593 | 3.556 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379300 | 694
GENERIC | GENERIC | TP | TP | 750 | 3+G | TP | TP | 72.644 | 13.3269 | 3.556 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 19649 | 691
GENERIC | GENERIC | TS | TS | 750 | 3+G | TS | TP | 73.66 | 13.5278 | 1.905
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 750 | 3+G | TS | TP | 73.66 | 14.4802 | 1.905 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295112 | 306
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 750 | 3+G | TS | TP | 73.66 | 13.5278 | 1.905 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295112 | 307
Draka | General Purpose Control XLPE | XLPE | PVC | 750 | 3+G | TS | TP | 72.644 | 13.3581 | 3.556 | Industrial Grade | Unshielded, 600V, 90°C | 219630 | 689
Draka | Power & Control Type TC XHHW-3 | XLPE | PVC | 750 | 3+G | TS | TP | 72.644 | 13.3581 | 3.556 | Industrial Grade | Unshielded, 600V, 90°C | 119649 | 693
GENERIC | GENERIC | TS | TS | 1000 | 1 | TS | TS | 36.322 | 5.1715 | 1.651
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 1000 | 1 | TS | N/A | 34.29 | 5.0227 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3703 | 14
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 1000 | 1 | Sil | Fiber | 36.576 | 5.0673 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3026 | 91
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 1000 | 1 | TS | TS | 36.322 | 5.1715 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-18 | P68-1000 | 287
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 1000 | 1 | TS | TS | 36.322 | 5.1938 | 1.651 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-5580 | 292
GENERIC | GENERIC | TS | TS | 1/0 | 1 | TS | TS | 14.478 | 0.63249 | 1.143
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 1/0 | 1 | TS | N/A | 13.462 | 0.59528 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3561 | 15
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 1/0 | 1 | TS | N/A | 12.192 | 0.55808 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3517 | 31
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 1/0 | 1 | Sil | Fiber | 15.494 | 6.1165 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3018 | 92
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 1/0 | 1 | TS | TS | 14.478 | 0.63249 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-10 | P68-0100 | 112
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 1/0 | 1 | TS | TS | 14.478 | 0.63249 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3902 | 117
GENERIC | GENERIC | TS | TP | 1/0 | 2 | TS | TP | 29.083 | 1.4287 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 496
GENERIC | GENERIC | TP | TP | 1/0 | 3 | TP | TP | 31.115 | 1.6073 | 2.032
GENERIC | GENERIC | TS | TS | 1/0 | 3 | TS | TP | 30.988 | 2.0537 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 1/0 | 3 | TP | TP | 30.353 | 2.2576 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68166 | 516
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 1/0 | 3 | TP | TP | 30.353 | 2.1371 | 2.032 | Industrial Grade | Unshielded, 600V | 17736 | 528
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 1/0 | 3 | TP | TP | 32.258 | 2.1638 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18231 | 443
General Cable | VNTC® | PVC | PVC | 1/0 | 3 | TP | TP | 31.115 | 1.6073 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 236440 | 551
American Insulated Wire | TYPE TC Power | XLPE | PVC | 1/0 | 3 | TS | TP | 30.988 | 2.0537 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 497
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 1/0 | 3 | TS | TS | 30.988 | 2.4109 | 2.032 | Industrial Grade | with Ground, Unshielded, 600V | 31466 | 507
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 1/0 | 3 | TS | TP | 30.607 | 2.2368 | 2.032 | Industrial Grade | Unshielded, 600V | 40971 | 556
Draka | General Purpose Control XLPE | XLPE | PVC | 1/0 | 3 | TS | TP | 31.496 | 2.082 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218230 | 402
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 1/0 | 3 | TS | TP | 31.496 | 2.082 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118230 | 476
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 1/0 | 3 | TS | TS | 31.496 | 1.6087 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282660 | 329
General Cable | CVTC® | XLPE | PVC | 1/0 | 3 | TS | TP | 30.861 | 2.1043 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339530 | 342
General Cable | EHTC® | EPR | CSPE | 1/0 | 3 | TS | TS | 31.115 | 2.1415 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 283220 | 361
General Cable | EHTC® | EPR | CSPE | 1/0 | 3 | TS | TS | 31.496 | 1.6087 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338720 | 362
General Cable | Ultrol® 325 | XLPE | CSPE | 1/0 | 3 | TS | TS | 30.1244 | 2.1519 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379150 | 540
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 1/0 | 3 | Sil | Fiber | 33.782 | 2.2397 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3032 | 93
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 1/0 | 3 | TS | TS | 28.448 | 2.0165 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0103 | 298
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 1/0 | 3 | TS | TS | 30.48 | 2.2993 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0104 | 382
GENERIC | GENERIC | TP | TP | 1/0 | 4 | TP | TP | 34.544 | 2.1028 | 2.032
GENERIC | GENERIC | TS | TS | 1/0 | 4 | TS | TP | 34.163 | 2.6282 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 1/0 | 4 | TP | TP | 33.528 | 2.8737 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68167 | 517
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 1/0 | 4 | TP | TP | 33.528 | 2.7532 | 2.032 | Industrial Grade | Unshielded, 600V | 17738 | 529
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 1/0 | 4 | TP | TP | 35.814 | 2.7353 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18241 | 444
General Cable | VNTC® | PVC | PVC | 1/0 | 4 | TP | TP | 34.544 | 2.1028 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 219580 | 552
American Insulated Wire | TYPE TC Power | XLPE | PVC | 1/0 | 4 | TS | TP | 34.163 | 2.6282 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 498
Draka | General Purpose Control XLPE | XLPE | PVC | 1/0 | 4 | TS | TP | 34.798 | 2.6698 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218249 | 404
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 1/0 | 4 | TS | TP | 34.798 | 2.6698 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118240 | 478
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 1/0 | 4 | TS | TS | 33.782 | 2.1028 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 338860 | 330
General Cable | CVTC® | XLPE | PVC | 1/0 | 4 | TS | TP | 34.036 | 2.716 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339540 | 343
General Cable | EHTC® | EPR | CSPE | 1/0 | 4 | TS | TS | 33.782 | 2.1028 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338730 | 363
General Cable | EHTC® | EPR | CSPE | 1/0 | 4 | TS | TS | 33.782 | 2.7085 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 294530 | 364
General Cable | Ultrol® 325 | XLPE | CSPE | 1/0 | 4 | TS | TS | 33.2486 | 2.7487 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379160 | 541
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 1/0 | 4 | Sil | Fiber | 37.592 | 2.9243 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3044 | 94
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 1/0 | 4 | TS | TS | 31.496 | 2.5969 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0104 | 299
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 1/0 | 4 | TS | TS | 33.528 | 2.8574 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5040 | 383
GENERIC | GENERIC | TP | TP | 1/0 | 3+G | TP | TP | 32.258 | 2.2755 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18249 | 442
GENERIC | GENERIC | TS | TS | 1/0 | 3+G | TS | TP | 34.29 | 2.3365 | 1.27
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 1/0 | 3+G | TS | TP | 34.29 | 2.7829 | 1.27 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295074 | 145
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 1/0 | 3+G | TS | TP | 34.29 | 2.3365 | 1.27 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295074 | 146
Draka | General Purpose Control XLPE | XLPE | PVC | 1/0 | 3+G | TS | TP | 31.496 | 2.1891 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218240 | 403
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 1/0 | 3+G | TS | TP | 31.496 | 2.1891 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118249 | 477
GENERIC | GENERIC | TS | TS | 2/0 | 1 | TS | TS | 15.748 | 0.77387 | 1.143
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 2/0 | 1 | TS | N/A | 14.478 | 0.72922 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3562 | 16
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 2/0 | 1 | TS | N/A | 13.208 | 0.69946 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3518 | 32
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 2/0 | 1 | Sil | Fiber | 16.764 | 0.75154 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3019 | 95
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 2/0 | 1 | TS | TS | 15.748 | 0.77387 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-11 | P68-0200 | 113
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 2/0 | 1 | TS | TS | 15.748 | 0.77387 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-3901 | 118
GENERIC | GENERIC | TS | TP | 2/0 | 2 | TS | TP | 31.369 | 1.6966 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 499
GENERIC | GENERIC | TP | TP | 2/0 | 3 | TP | TP | 32.766 | 2.6044 | 2.032
GENERIC | GENERIC | TS | TS | 2/0 | 3 | TS | TP | 33.401 | 2.5002 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 2/0 | 3 | TP | TP | 32.766 | 2.7249 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68168 | 518
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 2/0 | 3 | TP | TP | 32.766 | 2.6044 | 2.032 | Industrial Grade | Unshielded, 600V | 17740 | 530
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 2/0 | 3 | TP | TP | 35.052 | 2.6282 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18331 | 445
General Cable | VNTC® | PVC | PVC | 2/0 | 3 | TP | TP | 33.528 | 1.9942 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 243760 | 553
American Insulated Wire | TYPE TC Power | XLPE | PVC | 2/0 | 3 | TS | TP | 33.401 | 2.5002 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 500
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 2/0 | 3 | TS | TS | 33.782 | 3.0136 | 2.032 | Industrial Grade | with Ground, Unshielded, 600V | 31746 | 508
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 2/0 | 3 | TS | TP | 32.893 | 2.6951 | 2.032 | Industrial Grade | Unshielded, 600V | 40972 | 557
Draka | General Purpose Control XLPE | XLPE | PVC | 2/0 | 3 | TS | TP | 34.036 | 2.5404 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218330 | 405
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2/0 | 3 | TS | TP | 34.036 | 2.5404 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118330 | 479
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 2/0 | 3 | TS | TS | 34.036 | 1.9957 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282670 | 331
General Cable | CVTC® | XLPE | PVC | 2/0 | 3 | TS | TP | 33.274 | 2.5389 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339550 | 344
General Cable | EHTC® | EPR | CSPE | 2/0 | 3 | TS | TS | 33.02 | 2.5597 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 284560 | 365
General Cable | EHTC® | EPR | CSPE | 2/0 | 3 | TS | TS | 34.036 | 1.9957 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338740 | 366
General Cable | Ultrol® 325 | XLPE | CSPE | 2/0 | 3 | TS | TS | 32.5882 | 2.6029 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379170 | 542
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 2/0 | 3 | Sil | Fiber | 36.068 | 2.6936 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3033 | 96
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 2/0 | 3 | TS | TS | 30.988 | 2.4258 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0203 | 300
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 2/0 | 3 | TS | TS | 32.766 | 2.7532 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0204 | 384
GENERIC | GENERIC | TP | TP | 2/0 | 4 | TP | TP | 36.068 | 3.4898 | 2.032
GENERIC | GENERIC | TS | TS | 2/0 | 4 | TS | TP | 37.592 | 3.2785 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 2/0 | 4 | TP | TP | 36.068 | 3.6104 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68169 | 519
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 2/0 | 4 | TP | TP | 36.068 | 3.4898 | 2.032 | Industrial Grade | Unshielded, 600V | 17742 | 531
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 2/0 | 4 | TP | TP | 38.608 | 3.3321 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18341 | 447
General Cable | VNTC® | PVC | PVC | 2/0 | 4 | TP | TP | 36.957 | 2.6192 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 219610 | 554
American Insulated Wire | TYPE TC Power | XLPE | PVC | 2/0 | 4 | TS | TP | 36.957 | 3.2294 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 501
Draka | General Purpose Control XLPE | XLPE | PVC | 2/0 | 4 | TS | TP | 37.592 | 3.2785 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218349 | 407
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2/0 | 4 | TS | TP | 37.592 | 3.2785 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118340 | 481
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 2/0 | 4 | TS | TS | 37.592 | 2.6192 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 292410 | 332
General Cable | CVTC® | XLPE | PVC | 2/0 | 4 | TS | TP | 36.83 | 3.3083 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339560 | 345
General Cable | EHTC® | EPR | CSPE | 2/0 | 4 | TS | TS | 36.576 | 3.286 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 295360 | 367
General Cable | EHTC® | EPR | CSPE | 2/0 | 4 | TS | TS | 37.592 | 2.6192 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338750 | 368
General Cable | Ultrol® 325 | XLPE | CSPE | 2/0 | 4 | TS | TS | 36.0172 | 3.3425 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379180 | 543
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 2/0 | 4 | Sil | Fiber | 40.386 | 3.5196 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3045 | 97
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 2/0 | 4 | TS | TS | 34.29 | 3.1624 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0204 | 301
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 2/0 | 4 | TS | TS | 36.322 | 3.4824 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5041 | 385
GENERIC | GENERIC | TP | TP | 2/0 | 3+G | TP | TP | 35.052 | 2.7398 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18349 | 446
GENERIC | GENERIC | TS | TS | 2/0 | 3+G | TS | TP | 36.576 | 2.7978 | 1.27
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 2/0 | 3+G | TS | TP | 36.576 | 3.2889 | 1.27 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295077 | 147
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 2/0 | 3+G | TS | TP | 36.576 | 2.7978 | 1.27 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295077 | 148
Draka | General Purpose Control XLPE | XLPE | PVC | 2/0 | 3+G | TS | TP | 34.036 | 2.646 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 218340 | 406
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 2/0 | 3+G | TS | TP | 34.036 | 2.646 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118349 | 480
GENERIC | GENERIC | TS | TS | 3/0 | 1 | TS | N/A | 15.748 | 0.9078 | 0
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 3/0 | 1 | TS | N/A | 15.748 | 0.9078 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3563 | 17
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 3/0 | 1 | TS | N/A | 14.478 | 0.8706 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3519 | 33
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 3/0 | 1 | Sil | Fiber | 18.034 | 0.93013 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3020 | 98
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 3/0 | 1 | TS | TS | 17.018 | 0.94501 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-12 | P68-0300 | 114
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 3/0 | 1 | TS | TS | 17.018 | 0.95245 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-5092 | 119
GENERIC | GENERIC | TS | TP | 3/0 | 2 | TS | TP | 33.909 | 2.1906 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 502
GENERIC | GENERIC | TP | TP | 3/0 | 3 | TP | TP | 35.179 | 3.155 | 2.032
GENERIC | GENERIC | TS | TS | 3/0 | 3 | TS | TP | 36.195 | 2.9585 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 3/0 | 3 | TP | TP | 35.179 | 3.347 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68170 | 520
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 3/0 | 3 | TP | TP | 35.179 | 3.155 | 2.032 | Industrial Grade | Unshielded, 600V | 26011 | 532
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 3/0 | 3 | TP | TP | 37.846 | 3.2175 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18431 | 448
American Insulated Wire | TYPE TC Power | XLPE | PVC | 3/0 | 3 | TS | TP | 36.195 | 2.9585 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 503
Draka | General Purpose Control XLPE | XLPE | PVC | 3/0 | 3 | TS | TP | 37.084 | 3.1133 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 219430 | 408
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 3/0 | 3 | TS | TP | 37.084 | 3.1133 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118430 | 482
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 3/0 | 3 | TS | TS | 36.068 | 2.5552 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 366090 | 333
General Cable | CVTC® | XLPE | PVC | 3/0 | 3 | TS | TP | 36.068 | 3.6268 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 371260 | 346
General Cable | EHTC® | EPR | CSPE | 3/0 | 3 | TS | TS | 36.068 | 2.5552 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 366240 | 369
General Cable | EHTC® | EPR | CSPE | 3/0 | 3 | TS | TS | 36.068 | 3.2383 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 325700 | 370
General Cable | Ultrol® 325 | XLPE | CSPE | 3/0 | 3 | TS | TS | 35.3314 | 3.219 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379190 | 544
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 3/0 | 3 | Sil | Fiber | 38.862 | 3.3336 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3034 | 99
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 3/0 | 3 | TS | TS | 33.782 | 3.0583 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0303 | 302
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 3/0 | 3 | TS | TS | 35.56 | 3.4377 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-3421 | 386
GENERIC | GENERIC | TP | TP | 3/0 | 4 | TP | TP | 41.91 | 4.0851 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18441 | 450
GENERIC | GENERIC | TS | TS | 3/0 | 4 | TS | TP | 40.005 | 3.9363 | 2.032
American Insulated Wire | TYPE TC Power | XLPE | PVC | 3/0 | 4 | TS | TP | 40.005 | 3.9363 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 504
Draka | General Purpose Control XLPE | XLPE | PVC | 3/0 | 4 | TS | TP | 40.894 | 4.0286 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 219440 | 410
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 3/0 | 4 | TS | TP | 40.894 | 4.0286 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118440 | 484
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 3/0 | 4 | TS | TS | 39.878 | 3.341 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 366100 | 334
General Cable | CVTC® | XLPE | PVC | 3/0 | 4 | TS | TP | 39.878 | 4.6477 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 371270 | 347
General Cable | EHTC® | EPR | CSPE | 3/0 | 4 | TS | TS | 39.878 | 3.341 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 366250 | 371
General Cable | EHTC® | EPR | CSPE | 3/0 | 4 | TS | TS | 39.878 | 4.1491 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 365750 | 372
General Cable | Ultrol® 325 | XLPE | CSPE | 3/0 | 4 | TS | TS | 39.0652 | 4.1342 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379200 | 545
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 3/0 | 4 | Sil | Fiber | 43.942 | 4.3456 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3046 | 100
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 3/0 | 4 | TS | TS | 39.37 | 4.2042 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5042 | 387
GENERIC | GENERIC | TP | TP | 3/0 | 3+G | TP | TP | 37.846 | 3.4377 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18449 | 449
GENERIC | GENERIC | TS | TS | 3/0 | 3+G | TS | TP | 41.402 | 3.6015 | 1.524
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 3/0 | 3+G | TS | TP | 41.402 | 4.0926 | 1.524 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295080 | 249
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 3/0 | 3+G | TS | TP | 41.402 | 3.6015 | 1.524 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295080 | 250
Draka | General Purpose Control XLPE | XLPE | PVC | 3/0 | 3+G | TS | TP | 37.084 | 3.3351 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 219449 | 409
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 3/0 | 3+G | TS | TP | 37.084 | 3.3351 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118449 | 483
GENERIC | GENERIC | TS | TS | 4/0 | 1 | TS | N/A | 17.272 | 1.1236 | 0
Rockbestos-Surprenant | Firewall® III - Unipass Power Cable | XLPE | N/A | 4/0 | 1 | TS | N/A | 17.272 | 1.1236 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V | P51-3564 | 18
Rockbestos-Surprenant | Firewall® III-XHHW Power Cable | XLPE | N/A | 4/0 | 1 | TS | N/A | 16.002 | 1.0789 | 0 | Class 1E Nuclear | Power Cable Single conductor, 90°C, 600V, NEC Type XHHW-2 / Type SIS | P51-3520 | 34
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 4/0 | 1 | Sil | Fiber | 19.558 | 1.1459 | 1.016 | Class 1E Nuclear | Power Cable Single Conductor, 125°C, 600V | P40-3021 | 101
Rockbestos-Surprenant | Firewall® EP Power Cable | EPR | CSPE | 4/0 | 1 | TS | TS | 18.288 | 1.1608 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V, NEC Type RHH or RHW-2 or USE-13 | P68-0400 | 115
Rockbestos-Surprenant | Firewall® III - J Power Cable | XLPE | CSPE | 4/0 | 1 | TS | TS | 18.288 | 1.1682 | 1.143 | Class 1E Nuclear | Power Cable Single Conductor, 90°C, 600V | P62-5093 | 120
GENERIC | GENERIC | TS | TP | 4/0 | 2 | TS | TP | 36.83 | 2.5895 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 505
GENERIC | GENERIC | TP | TP | 4/0 | 3 | TP | TP | 38.481 | 3.8842 | 2.794
GENERIC | GENERIC | TS | TS | 4/0 | 3 | TS | TP | 39.624 | 3.7637 | 2.032
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 4/0 | 3 | TP | TP | 38.481 | 4.0762 | 2.032 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68171 | 521
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 4/0 | 3 | TP | TP | 38.481 | 3.8842 | 2.794 | Industrial Grade | Unshielded, 600V | 17745 | 668
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 4/0 | 3 | TP | TP | 41.402 | 3.9437 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18531 | 451
General Cable | VNTC® | PVC | PVC | 4/0 | 3 | TP | TP | 39.243 | 3.1699 | 2.032 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 221560 | 555
American Insulated Wire | TYPE TC Power | XLPE | PVC | 4/0 | 3 | TS | TP | 39.624 | 3.7637 | 2.032 | Industrial Grade | Unshielded, 600V | ES08231 | 506
American Insulated Wire | TYPE TC Power w/Ground | EPR | CSPE | 4/0 | 3 | TS | TS | 39.624 | 4.4646 | 2.032 | Industrial Grade | with Ground, Unshielded, 600V | 31467 | 509
American Insulated Wire | XLPE-CPE TYPE TC Power/Control w/Ground | XLPE | CPE | 4/0 | 3 | TS | TP | 38.862 | 4.0256 | 2.032 | Industrial Grade | Unshielded, 600V | 40973 | 558
Draka | General Purpose Control XLPE | XLPE | PVC | 4/0 | 3 | TS | TP | 40.132 | 3.8366 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 219530 | 411
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4/0 | 3 | TS | TP | 40.132 | 3.8366 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118530 | 485
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 4/0 | 3 | TS | TS | 40.005 | 3.1728 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 282680 | 335
General Cable | CVTC® | XLPE | PVC | 4/0 | 3 | TS | TP | 39.116 | 3.8693 | 2.032 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 383230 | 348
General Cable | EHTC® | EPR | CSPE | 4/0 | 3 | TS | TS | 39.116 | 3.8902 | 2.032 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 325110 | 373
General Cable | EHTC® | EPR | CSPE | 4/0 | 3 | TS | TS | 40.005 | 3.1728 | 2.032 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 360990 | 374
General Cable | Ultrol® 325 Power Cable | XLPE | CSPE | 4/0 | 3 | TS | TS | 38.3794 | 3.9259 | 2.032 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379210 | 546
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 4/0 | 3 | Sil | Fiber | 41.91 | 4.0256 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3035 | 102
Rockbestos-Surprenant | X-Link® TC Power Cable | XLPO | XLPO | 4/0 | 3 | TS | TS | 36.83 | 3.6982 | 1.651 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, NEC Type TC | P92-0403 | 303
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 4/0 | 3 | TS | TS | 38.608 | 4.1446 | 2.032 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-0404 | 388
GENERIC | GENERIC | TP | TP | 4/0 | 4 | TP | TP | 44.069 | 5.1789 | 2.032
GENERIC | GENERIC | TS | TS | 4/0 | 4 | TS | TP | 45.466 | 5.0212 | 2.794
American Insulated Wire | TYPE TC-ER Power | PVC | PVC | 4/0 | 4 | TP | TP | 44.069 | 5.1789 | 2.032 | Industrial Grade | Unshielded, 600V | 23576 | 533
American Insulated Wire | Type TC-ER - Power Cable w/Ground | PVC | PVC | 4/0 | 4 | TP | TP | 44.069 | 5.3709 | 2.794 | Industrial Grade | Bare Ground, Unshielded, 600V, 90°C dry 75°C wet | 68172 | 662
Draka | Power & Control Type TC THHN or THWN | PVC | PVC | 4/0 | 4 | TP | TP | 47.244 | 5.1923 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18541 | 628
General Cable | VNTC® | PVC | PVC | 4/0 | 4 | TP | TP | 44.958 | 4.161 | 2.794 | Industrial Grade | Unshielded, Low-Voltage Power, 600V, UL Type TC-ER | 329240 | 682
American Insulated Wire | TYPE TC Power | XLPE | PVC | 4/0 | 4 | TS | TP | 45.466 | 5.0212 | 2.794 | Industrial Grade | Unshielded, 600V | ES08231 | 653
Draka | General Purpose Control XLPE | XLPE | PVC | 4/0 | 4 | TS | TP | 45.974 | 5.1417 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 219540 | 601
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4/0 | 4 | TS | TP | 45.974 | 5.1417 | 2.794 | Industrial Grade | Unshielded, 600V, 90°C | 118540 | 638
General Cable | CHTC® Type TC-ER | XLPE | CSPE | 4/0 | 4 | TS | TS | 44.831 | 4.161 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, 600V, 90°C | 338880 | 565
General Cable | CVTC® | XLPE | PVC | 4/0 | 4 | TS | TP | 44.831 | 5.1254 | 2.794 | Industrial Grade | Unshielded, Low-Voltage, 600V, UL Type TC-ER | 339570 | 572
General Cable | EHTC® | EPR | CSPE | 4/0 | 4 | TS | TS | 44.831 | 4.161 | 2.794 | Industrial Grade | Low-Voltage Power, Unshielded, Type TC-ER, 600V, 90°C | 338770 | 584
General Cable | EHTC® | EPR | CSPE | 4/0 | 4 | TS | TS | 45.466 | 5.2013 | 2.794 | Industrial Grade | Unshielded, 600V, UL Type TC-ER | 346980 | 585
General Cable | Ultrol® 325 | XLPE | CSPE | 4/0 | 4 | TS | TS | 44.0436 | 5.2266 | 2.794 | Class 1E Nuclear | with 3 insulated Ground, 600V, 90°C | 379220 | 675
Rockbestos-Surprenant | Firewall® SR Power Cable | SR | Rockhide | 4/0 | 4 | Sil | Fiber | 47.244 | 5.2682 | 1.016 | Class 1E Nuclear | Power Cable 3 bare grounds, 125°C, 600V | P40-3047 | 103
Rockbestos-Surprenant | Firewall® III Power Cable | XLPE | CSPE | 4/0 | 4 | TS | TS | 44.45 | 5.3873 | 2.794 | Class 1E Nuclear | Power Cable 3 bare grounds, 90°C, 600V, UL Type TC | P62-5043 | 593
GENERIC | GENERIC | TP | TP | 4/0 | 3+G | TP | TP | 41.402 | 4.1655 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C dry, 75°C wet | 18549 | 452
GENERIC | GENERIC | TS | TS | 4/0 | 3+G | TS | TP | 44.45 | 4.3307 | 1.524 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295083 | 252
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 4/0 | 3+G | TS | TP | 44.45 | 4.8664 | 1.524 | Industrial Grade | Interlocked Steel Armor, 600V, 90°C | 295083 | 251
Draka | Type MC Power Cable 3 XHHW-2 (1 bare or 3 bare) | XLPE | PVC | 4/0 | 3+G | TS | TP | 44.45 | 4.3307 | 1.524 | Industrial Grade | Interlocked Aluminum Armor, 600V, 90°C | 295083 | 252
Draka | General Purpose Control XLPE | XLPE | PVC | 4/0 | 3+G | TS | TP | 40.132 | 4.0687 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 219549 | 412
Draka | Power & Control Type TC XHHW-2 | XLPE | PVC | 4/0 | 3+G | TS | TP | 40.132 | 4.0687 | 2.032 | Industrial Grade | Unshielded, 600V, 90°C | 118549 | 486

## Misc (hidden)
Air Drop
Cable Tray
Conduit - Rigid
Conduit - EMT
User Specified
EMT
| Designation |  | Outside | Diameter | Wall | Thickness
Thermoplastic | English | Metric | in | mm | in | mm
Thermoset | 1/2 | 16 | 0.706 | 17.9 | 0.042 | 1.07
User Defined | 3/4 | 21 | 0.922 | 23.4 | 0.049 | 1.25
Natural Ventilation - Method of McCaffrey, Quintiere, Harkleroad (MQH) | 1 | 27 | 1.163 | 29.5 | 0.057 | 1.45
Forced Ventilation - Method of Foote, Pagni, and Alvares (FPA) | 1-1/4 | 35 | 1.51 | 38.4 | 0.065 | 1.65
Forced Ventilation - Method of Deal and Beyler | 1-1/2 | 41 | 1.74 | 44.2 | 0.065 | 1.65
Room Fire with Closed Door | 2 | 53 | 2.197 | 55.8 | 0.065 | 1.65
Within Fire Plume | 2-1/2 | 63 | 2.875 | 73 | 0.072 | 1.83
User Defined | 3 | 78 | 3.5 | 88.9 | 0.072 | 1.83
| 3-1/2 | 91 | 4 | 101.6 | 0.083 | 2.11
| 4 | 103 | 4.5 | 114.3 | 0.083 | 2.11
Rigid
| Designation |  | Outside | Diameter | Wall | Thickness
| English | Metric | in | mm | in | mm
| 1/2 | 16 | 0.84 | 21.3 | 0.104 | 2.6
| 3/4 | 21 | 1.05 | 26.7 | 0.107 | 2.7
| 1 | 27 | 1.315 | 33.4 | 0.126 | 3.2
| 1-1/4 | 35 | 1.66 | 42.2 | 0.133 | 3.4
| 1-1/2 | 41 | 1.9 | 48.3 | 0.138 | 3.5
| 2 | 53 | 2.375 | 60.3 | 0.146 | 3.7
| 2-1/2 | 63 | 2.875 | 73 | 0.193 | 4.9
| 3 | 78 | 3.5 | 88.9 | 0.205 | 5.2
| 3-1/2 | 91 | 4 | 101.6 | 0.215 | 5.5
| 4 | 103 | 4.5 | 114.3 | 0.225 | 5.7
| 5 | 129 | 5.563 | 141.3 | 0.245 | 6.2
| 6 | 155 | 6.625 | 168.3 | 0.266 | 6.8