## Burning Duration Solid (8.9-1)
CHAPTER 8
ESTIMATING BURNING DURATION
|  | OF | [6 empty] | Version 1805.1
|  | SOLID COMBUSTIBLES | [6 empty] | (English Units)
The following calculations provides an approximation of the burning duration of solid combustibles based on free burning rate with a given surface area.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Mass of Solid Fuel (msolid) |  |  |  |  | 10 | lb |  | 4.5359 | kg
| Exposed Floor Area (Length x Width) of Fuel (Afuel) |  |  |  |  | 1 | ft2 |  | 0.092903 | m2
| Heat Release Rate (HRR) per Unit Floor Area (Q") |  |  |  |  | 589 | kW/m2
| Effective Heat of Combustion (DHc,eff) |  |  |  |  | 24000 | kJ/kg
Calculate
THERMAL PROPERTIES OF SOLID COMBUSTIBLE MATERIALS
Material |  |  | HRR per Unit Floor Area |  |  | Heat of Combustion |  | Select Material
|  |  | Q" |  |  | DHc
|  |  | (kW/m2) |  |  | (kJ/kg)
Douglas Fir Plywood |  |  | 221 |  |  | 17600 |  | Scroll to desired material then
Empty Cartons 15 ft high |  |  | 1700 |  |  | 12700 |  | Click on selection
Ethylene Propylene Dien Rubber (EPDM) |  |  | 956 |  |  | 28800
Fire Retardant Treated Plywood |  |  | 81 |  |  | 13500
Nylon 6/6 |  |  | 1313 |  |  | 32000
Particle Board, 19 mm thick |  |  | 1900 |  |  | 17500
PE, Nylon/PVC, Nylon |  |  | 231 |  |  | 9200
PE/PVC |  |  | 589 |  |  | 24000
Polycarbonate |  |  | 420 |  |  | 24400
Polyethylene (PE) |  |  | 1408 |  |  | 46500
Polymethlmethacrylate (PMMA) |  |  | 665 |  |  | 26000
Polypropylene (PP) |  |  | 1509 |  |  | 43200
Polystyrene (PS) |  |  | 1101 |  |  | 42000
Polyurethane |  |  | 710 |  |  | 45000
Polyvinyl Chloride (PVC) Flexible |  |  | 237 |  |  | 15700
Strene-Butadiene Copolymers (SBR) |  |  | 163 |  |  | 44000
Teflon |  |  | 98 |  |  | 3200
Wood Pallets, stacked 1.5 ft high |  |  | 1420 |  |  | 14000
Wood Pallets, stacked 5 ft high |  |  | 3970 |  |  | 14000
Wood Pallets, stacked 10 ft high |  |  | 6800 |  |  | 14000
XPE/FRXPE |  |  | 475 |  |  | 28300
XPE/Neoprene |  |  | 354 |  |  | 10300
User Specified Value |  |  | Enter Value |  |  | Enter Value
References:
"Categorization of Cable Flammability, Part 1: Laboratory Evaluation of Cable Flammability Parameters," EPRI Research Project 1165-1, NP-1200, Part 1.
Karlsson and Quantiere, Enclosure Fire Dynamics, Chapter 3: Energy Release Rate," CRC Press, 1999.
Johnson, D. G., "Combustion Properties of Plastics," Journal of Applied Fire Science, Volume 4, No. 3, 1994-95, pp. 185-201.
Hirschler, M. M., "Heat Release from Plastic Materials," Heat Release in Fires, Babrauskas and Grayson, Editors, Elsevier Applied Science, 1992.
BURNING DURATION OF SOLID COMBUSTIBLES
Reference: Buchanan, A. H., "Structural Design for Fire Safety," 2001, Page 38.
The burning duration of a solid fuel can be calculated if the total energy contained in the fuel and HRR are known.
The burning duration is given by:
Q = E / tsolid |  | or tsolid = |  | (E) / (Q" AFuel)
Where,
tsolid = |  |  |  | burning duration of solid combustible (sec)
E = |  |  |  | mFuel DHc = total energy contained in the fuel (kJ)
Q = |  |  |  | heat release rate of fire (kW)
Q" = |  |  |  | heat release rate per unit floor area of fuel (kW/m2)
AFuel = |  |  |  | exposed floor area (length x width) of fuel (m2)
tsolid = |  |  |  | (mFuel DHc) / (Q" AFuel)
Where,
mFuel = |  |  |  | mass of solid fuel (kg)
DHc = |  |  |  | fuel effective heat of combustion (kJ/kg)
tsolid = |  |  |  | (msolid DHc) / (Q" Asolid)
Answer | tsolid = | 1989.4426 |  |  | sec |  | 33.1574 |  | min
NOTE:
The above calculations are based on principles developed in the Structural Design for Fire Safety, 2001. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  |  | Organization:
Checked by: |  |  |  | Date: |  |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Corrected subscripts, revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011