## Fire_Severity
CHAPTER 13
|  | FIRE SEVERITY CALCULATIONS |  |  |  |  | Version 1805.1
(SI Units)
The following calculations estimate the fire severity or equivalent fire duration based on available fuel in a compartment with at least one vent opening.
Parameters in YELLOW CELLS are Entered by the User.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT AND FIRE HAZARD INFORMATION
| Compartment Width (wc) |  |  | 6.1 | m |  |  | 6.1 | m
| Compartment Length (lc) |  |  | 7.62 | m |  |  | 7.62 | m
| Compartment Height (hc) |  |  | 3.66 | m |  |  | 3.66 | m
| Vent Width (wv) |  |  | 0.91 | m |  |  | 0.91 | m
| Vent Height (hv) |  |  | 2.44 | m |  |  | 2.44 | m
| Total Fire or Fuel Load in Compartment (L) |  |  | 680.39 | kg |  |  | 680.39 | kg
| Fuel Heat of Combustion (DHc) |  |  | 32564 | kJ/kg |  |  | 32564 | kJ/kg
Calculate
Properties of Wood
| Wood Heat of Combustion (DHc, wood) |  |  | 8000 | Btu/lb | 18608 | kJ/kg
| Correlational Constant (K) |  |  | 1 | min-m2/kg
METHOD OF MARGARET LAW
Reference: Simplified Fire Growth Calculation, NFPA Fire Protection Handbook, 19th Edition, 2003, p. 3-137.
tf = |  | K Leq / (Av AT)1/2 |  |  | (Law's Fire Severity Correlation)
Where,
tf = |  |  | fire severity or duration (min)
K = |  |  | correlational constant (min-m2/kg)
Leq = |  |  | total fire or fuel load in compartment equivalent of wood (kg)
Av = |  |  | area of ventilation opening (m2)
AT = |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
Total Fire or Fuel Load in Compartment Equivalent of Wood
Leq = |  |  | L x DHc / DHc, wood
Where,
Leq = |  |  | total fire or fuel load in equivalent of wood (kg)
L = |  |  | total fire or fuel load in compartment (kg)
DHc = |  |  | fuel heat of combustion (kJ/kg)
DHc, wood = |  |  | wood heat of combustion (kJ/kg)
Leq = |  |  | 1190.6825 |  | kg
Area of Ventilation Opening
Av = |  |  | (wv) (hv)
Where,
Av = |  |  | area of ventilation opening (m2)
wv = |  |  | vent width (m)
hv = |  |  | vent height (m)
Av = |  |  | 2.2204 |  | m2
Area of Compartment Enclosing Surface Boundaries
AT = |  |  | [2(wc x lc) + 2(hc x wc) + 2(hc x lc)] - Av
Where,
AT = |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
wc = |  |  | compartment width (m)
lc = |  |  | compartment length (m)
hc = |  |  | compartment height (m)
Av = |  |  | area of ventilation opening (m2)
AT = |  |  | 191.174 |  | m2
LAW'S FIRE SEVERITY CORRELATION
tf = |  | K Leq / (Av AT)1/2
Answer | tf = | 57.7918 |  | min |  | 0.9632 |  | Hours
NOTE:
The above calculations are based on principles developed in the NFPA Fire Protection Handbook, 19th Edition, 2003. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions, or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  | Date: |  | Organization:
Checked by: |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [6 empty] | Date
1805.0 | Original issue with final text. | [6 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [6 empty] | March 2011

## Post_Flashover_Temperature
CHAPTER 13
|  | PREDICTING COMPARTMENT |  |  |  |  | Version 1805.1
|  | POST-FLASHOVER TEMPERATURE |  |  |  |  | (SI Units)
The following calculations estimate the compartment post-flashover temperature.
Parameters in YELLOW CELLS are Entered by the User.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  | 6.096 | m |  |  | 6.096 | m
| Compartment Length (lc) |  |  | 7.62 | m |  |  | 7.62 | m
| Compartment Height (hc) |  |  | 3.6576 | m |  |  | 3.6576 | m
| Vent Width (wv) |  |  | 0.914 | m |  |  | 0.914 | m
| Vent Height (hv) |  |  | 2.438 | m |  |  | 2.438 | m
Calculate
METHOD OF MARGARET LAW
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-183.
TPFO (max) = |  | 6000 (1 - e-0.1W) / (√W)
Where,
TPFO (max) = |  |  | maximum compartment post-flashover temperature (°C)
W = |  |  | ventilation factor
Ventilation Factor
W = |  |  | (AT - Av) / Av (√hv)
Where,
AT = |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
Av = |  |  | area of ventilation opening (m2)
hv = |  |  | height of ventilation opening (m)
Area of Ventilation Opening Calculation
Av = |  |  | (wv) (hv)
Where,
Av = |  |  | area of ventilation opening (m2)
wv = |  |  | vent width (m)
hv = |  |  | vent height (m)
Av = |  |  | 2.2283 |  | m2
Area of Compartment Enclosing Surface Boundaries
AT = |  |  | [2(wc x lc) + 2(hc x wc) + 2(hc x lc)] - Av
Where,
AT = |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
wc = |  |  | compartment width (m)
lc = |  |  | compartment length (m)
hc = |  |  | compartment height (m)
Av = |  |  | area of ventilation opening (m2)
AT = |  |  | 191.01 |  | m2
Ventilation Factor Calculation
W = |  |  | (AT - Av) / Av (√hv)
Where,
W = |  |  | ventilation factor
AT = |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
Av = |  |  | area of ventilation opening (m2)
hv = |  |  | vent height (m)
W = |  |  | 54.2579 |  | m-1/2
COMPARTMENT POST-FLASHOVER TEMPERATURE CALCULATION
TPFO (max) = |  | 6000 (1 - e-0.1W) / (√W)
Answer | TPFO (max) = | 810.9684 |  | °C |  | 1491.7431 |  | °F
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions, or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  | Date: |  | Organization:
Checked by: |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [6 empty] | Date
1805.0 | Original issue with final text. | [6 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [6 empty] | March 2011

## Flashover_HRR
CHAPTER 13
|  | PREDICTING COMPARTMENT FLASHOVER | [6 empty] | Version 1805.1
|  |  |  | HEAT RELEASE RATE |  |  |  |  | (SI Units)
The following calculations estimate the minimum heat release rate required to compartment flashover.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Material Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
COMPARTMENT INFORMATION
| Compartment Width (wc) |  |  |  | 30.48 | m |  |  | 30.48 | m
| Compartment Length (lc) |  |  |  | 5.49 | m |  |  | 5.49 | m
| Compartment Height (hc) |  |  |  | 3.048 | m |  |  | 3.048 | m
| Vent Width (wv) |  |  |  | 0.914 | m |  |  | 0.914 | m
| Vent Height (hv) |  |  |  | 2.44 | m |  |  | 2.44 | m
| Interior Lining Thickness (d) |  |  |  | 15.24 | cm |  |  | 0.1524 | m
| Interior Lining Thermal Conductivity (k) |  |  |  | 0.0016 | kW/m-K
Calculate
THERMAL PROPERTIES DATA
MATERIAL |  |  |  | THERMAL CONDUCTIVITY |  |  |  | Select Material
k (kW/m-K)
Aerated Concrete |  |  |  | 0.00026 |  |  |  | Scroll to desired material
Alumina Silicate Block |  |  |  | 0.00014 |  |  |  | Click on selection
Aluminum (pure) |  |  |  | 0.206
Brick |  |  |  | 0.0008
Brick/Concrete Block |  |  |  | 0.00073
Calcium Silicate Board |  |  |  | 0.00013
Chipboard |  |  |  | 0.00015
Concrete |  |  |  | 0.0016
Expended Polystyrene |  |  |  | 3.4e-05
Fiber Insulation Board |  |  |  | 0.00053
Glass Fiber Insulation |  |  |  | 3.7e-05
Glass Plate |  |  |  | 0.00076
Gypsum Board |  |  |  | 0.00017
Plasterboard |  |  |  | 0.00016
Plywood |  |  |  | 0.00012
Steel (0.5% Carbon) |  |  |  | 0.054
User Specified Value |  |  |  | Enter Value
Reference: Klote, J., J. Milke, Principles of Smoke Management, 2002, Page 270.
PREDICTING FLASHOVER HEAT RELEASE RATE
METHOD OF McCAFFREY, QUINTIERE, AND HARKLEROAD (MQH)
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-184.
QFO = |  |  | 610 √(hk AT Av (√hv))
Where,
QFO = |  |  |  | heat release rate necessary for flashover (kW)
hk = |  |  |  | effective heat transfer coefficient (kW/m2-K)
AT = |  |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
Av = |  |  |  | area of ventilation opening (m2)
hv = |  |  |  | height of ventilation opening (m)
Heat Transfer Coefficient Calculation
hk = |  |  |  | k/d | Assuming that compartment has been heated thoroughly before flashover, i.e., t > tp.
Where,
hk = |  |  |  | effective heat transfer coefficient (kW/m2-K)
k = |  |  |  | interior lining thermal conductivity (kW/m-K)
d = |  |  |  | interior lining thickness (m)
hk = |  |  |  | 0.010499 |  |  | kW/m2-K
Area of Ventilation Opening Calculation
Av = |  |  |  | (wv) (hv)
Where,
Av = |  |  |  | area of ventilation opening (m2)
wv = |  |  |  | vent width (m)
hv = |  |  |  | vent height (m)
Av = |  |  |  | 2.2302 |  |  | m2
Area of Compartment Enclosing Surface Boundaries
AT = |  |  |  | [2(wc x lc) + 2(hc x wc) + 2(hc x lc)] - Av
Where,
AT = |  |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
wc = |  |  |  | compartment width (m)
lc = |  |  |  | compartment length (m)
hc = |  |  |  | compartment height (m)
Av = |  |  |  | area of ventilation opening (m2)
AT = |  |  |  | 551.7134 |  |  | m2
MINIMUM HEAT RELEASE RATE FOR FLASHOVER
QFO = |  |  | 610 √(hk AT Av (√hv))
| QFO = |  | 2740.1199 |  |  |  | kW
PREDICTING FLASHOVER HEAT RELEASE RATE
METHOD OF BABRAUSKAS
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-184.
QFO = |  |  | 750 Av (√hv)
Where,
QFO = |  |  |  | heat release rate necessary for flashover (kW)
Av = |  |  |  | area of ventilation opening (m2)
hv = |  |  |  | height of ventilation opening (m)
Minimum Heat Release Rate for Flashover
QFO = |  |  | 750 Av (√hv)
| QFO = |  | 2612.716 |  |  |  | kW
PREDICTING FLASHOVER HEAT RELEASE RATE
METHOD OF THOMAS
Reference: SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 3-184.
QFO = |  |  | 7.8 AT + 378 Av (√hv)
Where,
QFO = |  |  |  | heat release rate necessary for flashover (kW)
AT = |  |  |  | total area of the compartment enclosing surface boundaries excluding area of vent openings (m2)
Av = |  |  |  | area of ventilation opening (m2)
hv = |  |  |  | height of ventilation opening (m)
Minimum Heat Release Rate for Flashover
QFO = |  |  | 7.8 AT + 378 Av (√hv)
| QFO = |  | 5620.1731 |  |  |  | kW
Summary of Results
CALCULATION METHOD | [7 empty] | FLASHOVER HRR (kW)
METHOD OF McCAFFREY, QUINTIERE, AND HARKLEROAD (MQH) | [7 empty] | 2740.1199
METHOD OF BABRAUSKAS | [7 empty] | 2612.716
METHOD OF THOMAS | [7 empty] | 5620.1731
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions, or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [7 empty] | Date
1805.0 | Original issue with final text. | [7 empty] | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [7 empty] | March 2011
O