## Explosion-Calculation
CHAPTER 15
ESTIMATING PRESSURE INCREASE AND
|  | EXPLOSIVE ENERGY RELEASE ASSOCIATED | [5 empty] | Version 1805.1
|  | WITH EXPLOSIONS | [5 empty] | (English Units)
The following calculations estimate the pressure and energy due to an explosion in a confined space.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Fuel Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected and
secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
EXPLOSIVE FUEL INFORMATION
| Adiabatic Flame Temperature of the Fuel ((Tad) |  |  |  | 2586 | °F |  | 1418.8889 | °C
[8 empty] | 1691.8889 | °K
| Heat of Combustion of the Fuel (DHc) |  |  |  | 44560 | kJ/kg
| Yield (a) See Note |  |  |  | 100 | % |  | 1
| Mass of Flammable Vapor Release (mF) |  |  |  | 48 | lb |  | 21.8182 | kg
| Ambient Air Temperature (Ta) |  |  |  | 77 | °F |  | 25 | °C
[8 empty] | 298 | °K
| Initial Atmospheric Pressure (Pa) |  |  |  | 14.7 | psi |  | 101.3529 | kPa
Note: The fraction of available combustion is 1% for unconfined mass release and 100% for confined vapor release energy participating in blast wave generation. |  |  |  |  | Calculate
THERMAL PROPERTIES FOR FUEL
FUEL FLAMMABILITY DATA
Fuel |  |  | Adiabatic Flame Temperature |  | Heat of Combustion |  | Select Fuel Type
|  |  | Tad (°F) |  | DHc (kJ/kg)
Acetylene |  |  | 4779 |  | 48220 |  | Scroll to desired Fuel Type then
Carbon Monoxide |  |  | 4329 |  | 10100 |  | Click on selection
Ethane |  |  | 2244 |  | 47490
Ethylene |  |  | 4152 |  | 47170
Hydrogen |  |  | 4085 |  | 130800
Methane |  |  | 2143 |  | 50030
n-Butane |  |  | 2442 |  | 45720
n-Heptane |  |  | 2586 |  | 44560
n-Octane |  |  | 2478 |  | 44440
n-Pentane |  |  | 2356 |  | 44980
Propane |  |  | 2338 |  | 46360
Propylene |  |  | 4050 |  | 45790
User Specified Value |  |  | Enter Value |  | Enter Value
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 1-86.
METHOD OF ZALOSH
Reference: SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995, Page 3-312.
Pressure Rise from a Confined Explosion
(Pmax)/Pa = |  |  |  | (Tad/Ta)
Pmax = |  |  |  | (Tad/Ta) Pa
Where,
Pmax = |  |  |  | maximum pressure developed at completion of combustion (kPa)
Pa = |  |  |  | initial atmospheric pressure (kPa)
Tad = |  |  |  | adiabatic flame temperature (K)
Ta = |  |  |  | ambient temperature (K)
Pmax = |  |  |  | 575.4292 |  | kPa | 83.459 | psi
Blast Wave Energy Calculation
E = |  |  |  | a DHc mF
Where,
E = |  |  |  | blast wave energy (kJ) [E is the Trinitrotoluene (TNT) equivalent energy]
a = |  |  |  | yield (a is the fraction of available combustion energy participating in blast wave generation)
DHc = |  |  |  | heat of combustion (kJ/kg)
mF = |  |  |  | mass of flammable vapor release (kg)
E = |  |  |  | 972218.1818 |  | kJ | 920787.84 | Btu
TNT Mass Equivalent Calculation
WTNT = |  |  |  | E/4500
Where,
WTNT = |  |  |  | weight of TNT (kg)
E = |  |  |  | explosive energy release (kJ)
WTNT = |  |  |  | 216.0485 |  | kg | 476.3055 | lb
Summary of Results
Pressure Rise from a Confined Explosion
Pmax = |  |  | (Tad/Ta) Pa
Answer | Pmax = |  | 83.459 |  | psi |  | 575.4292 | kPa
Blast Wave Energy
E = |  |  | a DHc mF
Answer | E = |  | 920787.84 |  | Btu |  | 972218.1818 | kJ
TNT Mass Equivalent
WTNT = |  |  | E/4500
Answer | WTNT = |  | 476.3055 |  | lb |  | 216.0485 | kg
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 2nd Edition, 1995. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheet, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision | [6 empty] | Date
1805.0 | Original issue with final text. | [6 empty] | December 2004
1805.1 | Corrected revision date for Revision Log 1805.0, revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. | [6 empty] | March 2011
Note on F32: This default value (14.70) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.