## Beam
CHAPTER 17
ESTIMATING FIRE RESISTANCE TIME OF STEEL BEAMS
|  | PROTECTED BY FIRE PROTECTION INSULATION | [6 empty] | Version 1805.1
|  | (QUASI-STEADY-STATE APPROACH) | [6 empty] | (English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [5 empty] | 18.1664 | lb/ft2
| Thickness of Spray-Applied Protection on Steel Beam (h) |  |  |  |  | h ≥ 1/16 in | 0.5 | in | 0.041667 | ft
| Density of Spray-Applied Material (ri) | [5 empty] | 35 | lb/ft3
| Thermal Conductivity of Spray-Applied Material (ki) | [5 empty] | 0.06936 | Btu/ft-hr-°F | 1.9267e-05 | Btu/ft-sec-°F
| Specific Heat of Spray-Applied Material (ci) | [5 empty] | 0.2868 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [5 empty] | 77 | °F
| Specific Heat of Steel (cs) | [5 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL BEAMS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 29.6162
| 36x280 | 27.756
| 36x260 | 25.8943
| 36x245 | 24.4816
| 36x230 | 23.0596
| 36x210 | 23.2773
| 36x194 | 21.5965
| 36x182 | 20.3286
| 36x170 | 19.053
| 36x160 | 17.991
| 36x150 | 16.9213
| 36x135 | 15.3191
| 33x241 | 25.3063
| 33x221 | 23.3194
| 33x201 | 21.314
| 33x152 | 18.1664
| 33x141 | 16.9208
| 33x130 | 15.6705
| 33x118 | 14.2944
| 30x211 | 23.9671
| 30x191 | 21.8161
| 30x173 | 19.8613
| 30x132 | 17.4018
| 30x124 | 16.403
| 30x116 | 15.4025
| 30x108 | 14.4008
| 30x99 | 13.2574
| 27x178 | 22.1519
| 27x161 | 20.1418
| 27x146 | 18.3561
| 27x114 | 16.3539
| 27x102 | 14.7124
| 27x94 | 13.6183
| 27x84 | 12.236
| 24x162 | 22.2286
| 24x146 | 20.1657
| 24x131 | 18.2124
| 24x117 | 16.3598
| 24x104 | 14.6187
| 24x94 | 15.0832
| 24x84 | 13.563
| 24x76 | 12.336
| 24x68 | 11.0983
| 24x62 | 10.9832
| 24x55 | 9.7974
| 21x147 | 21.9923
| 21x132 | 19.8795
| 21x122 | 18.4546
| 21x111 | 16.8736
| 21x101 | 15.4218
| 21x93 | 16.5726
| 21x83 | 14.889
| 21x73 | 13.1819
| 21x68 | 12.3244
| 21x62 | 11.2898
| 21x57 | 11.2205
| 21x50 | 9.919
| 21x44 | 8.7824
| 18x119 | 20.2769
| 18x106 | 18.2026
| 18x97 | 16.7374
| 18x86 | 14.937
| 18x76 | 13.2799
| 18x71 | 14.4763
| 18x65 | 13.3174
| 18x60 | 12.3499
| 18x55 | 11.3734
| 18x50 | 10.3887
| 18x46 | 10.3024
| 18x40 | 9.02
| 18x35 | 7.9545
| 16x100 | 18.7368
| 16x89 | 16.807
| 16x77 | 14.6632
| 16x67 | 12.8486
| 16x57 | 12.8186
| 16x50 | 11.3272
| 16x45 | 10.2515
| 16x40 | 9.1612
| 16x36 | 8.2941
| 16x31 | 7.7849
| 16x26 | 6.5851
| 14x730 | 94.836
| 14x665 | 88.1086
| 14x605 | 81.6694
| 14x550 | 75.5841
| 14x500 | 69.8893
| 14x455 | 64.6039
| 14x426 | 61.0935
| 14x398 | 57.6742
| 14x370 | 54.1761
| 14x342 | 50.7293
| 14x311 | 46.5859
| 14x283 | 42.8626
| 14x257 | 39.3392
| 14x233 | 36.0263
| 14x211 | 32.9344
| 14x193 | 30.3499
| 14x176 | 27.8886
| 14x159 | 25.2923
| 14x145 | 23.2932
| 14x132 | 21.9375
| 14x120 | 20.0585
| 14x109 | 18.318
| 14x99 | 16.7218
| 14x90 | 15.2715
| 14x82 | 16.9684
| 14x74 | 15.4033
| 14x68 | 14.2272
| 14x61 | 12.8387
| 14x53 | 12.4025
| 14x48 | 11.2963
| 14x43 | 10.1785
| 14x38 | 9.5218
| 14x34 | 8.5669
| 14x30 | 7.6062
| 14x26 | 7.3611
| 14x22 | 6.2827
| 12x336 | 57.3991
| 12x305 | 52.9705
| 12x279 | 49.1919
| 12x252 | 45.104
| 12x230 | 41.6824
| 12x210 | 38.5144
| 12x190 | 35.2668
| 12x170 | 31.9499
| 12x152 | 28.8973
| 12x136 | 26.1371
| 12x120 | 23.3085
| 12x106 | 20.7775
| 12x96 | 18.9474
| 12x87 | 17.2833
| 12x79 | 15.7842
| 12x72 | 14.4578
| 12x65 | 13.1181
| 12x58 | 12.9633
| 12x53 | 11.9068
| 12x50 | 12.5313
| 12x45 | 11.3481
| 12x40 | 10.1469
| 12x35 | 9.5281
| 12x30 | 8.2342
| 12x26 | 7.1807
| 12x22 | 7.2948
| 12x19 | 6.3572
| 12x16 | 5.4069
| 12x14 | 4.7552
| 10x112 | 25.622
| 10x100 | 23.1392
| 10x88 | 20.5988
| 10x77 | 18.2213
| 10x68 | 16.2388
| 10x60 | 14.4462
| 10x54 | 13.083
| 10x49 | 11.9318
| 10x45 | 12.3967
| 10x39 | 10.8421
| 10x33 | 9.261
| 10x30 | 9.5314
| 10x26 | 8.3311
| 10x22 | 7.114
| 10x19 | 7.1161
| 10x17 | 6.4212
| 10x15 | 5.7107
| 10x12 | 4.6095
| 8x67 | 19.2806
| 8x58 | 16.9178
| 8x48 | 14.2117
| 8x40 | 12.003
| 8x35 | 10.5823
| 8x31 | 9.438
| 8x28 | 9.5577
| 8x24 | 8.2628
| 8x21 | 7.9071
| 8x18 | 6.8419
| 8x15 | 6.4806
| 8x13 | 5.6686
| 8x10 | 4.4021
| 6x25 | 9.8814
| 6x20 | 8.016
| 6x15 | 6.1038
| 6x16 | 7.9569
| 6x12 | 6.1017
| 6x9 | 4.6392
| 5x19 | 9.1751
| 5x16 | 7.824
| 4x13 | 7.82
| User Specified Value | Enter Value
Select Beam
Scroll to desired beam size then Click on selection
THERMAL PROPERTIES OF SPRAY-APPLIED INSULATION MATERIALS
Insulation Material |  | Density | Thermal | Specific Heat |  | Select Insulation Type
Spray-Applied |  | ρi | Conductivity ki | ci
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F) |  | Scroll to desired material then Click on selection
Sprayed mineral fiber |  | 19 | 0.06936 | 0.2868
Perlite or vermiculite |  | 22 | 0.06936 | 0.2868
High density perlite or vermiculite |  | 35 | 0.06936 | 0.2868
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 179.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Beam
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
Where
DTs = temperature rise in steel (°F)
ki = thermal conductivity of spray-applied material (Btu/ft-sec-°F)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
cs W/D > 2 ci ri h
Where
cs = specific heat of steel (Btu/lb-°F)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (BTU/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
|  |  | 2.398 | > | 0.8365
The Maximum Allowable Time Step
Dt = 15.9 W/D
|  |  | Dt = | 288.8462 | sec
|  |  | Dt = | 4.8141 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
Tf = C1 LOG (0.133 t + 1) + Ta
Where
Tf = fire exposure temperature (°F)
C1 = constant = 620
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
Where
|  | t1 = Dt/2 |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | Ts0 = initial steel temperature (°F) |  |  | carbon steel structural members begin to fail. Predicted
temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
Where
t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Answer
Time | Time | DTs | Ts |  |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°F) |  |  | (min) | (sec) | (°F) | (°F)
4.8141 | 288.8462 | 45.0837 | 122.0837 |  |  | 255.1475 | 15308.8472 | 108.1205 | 5073.249 | Failure of Beam
9.6282 | 577.6923 | 58.5459 | 180.6295 |  |  | 259.9616 | 15597.6933 | 108.3882 | 5181.6372 | Failure of Beam
14.4423 | 866.5385 | 65.3544 | 245.984 |  |  | 264.7757 | 15886.5395 | 108.6509 | 5290.288 | Failure of Beam
19.2564 | 1155.3847 | 69.9772 | 315.9612 |  |  | 269.5898 | 16175.3857 | 108.9088 | 5399.1968 | Failure of Beam
24.0705 | 1444.2309 | 73.4642 | 389.4253 |  |  | 274.4039 | 16464.2319 | 109.1621 | 5508.359 | Failure of Beam
28.8846 | 1733.077 | 76.2638 | 465.6891 |  |  | 279.218 | 16753.078 | 109.411 | 5617.77 | Failure of Beam
33.6987 | 2021.9232 | 78.6024 | 544.2915 |  |  | 284.0321 | 17041.9242 | 109.6556 | 5727.4256 | Failure of Beam
38.5128 | 2310.7694 | 80.6103 | 624.9018 |  |  | 288.8462 | 17330.7704 | 109.8961 | 5837.3217 | Failure of Beam
43.3269 | 2599.6156 | 82.3695 | 707.2713 |  |  | 293.6603 | 17619.6165 | 110.1325 | 5947.4542 | Failure of Beam
48.141 | 2888.4617 | 83.9348 | 791.2061 |  |  | 298.4744 | 17908.4627 | 110.3651 | 6057.8193 | Failure of Beam
52.9551 | 3177.3079 | 85.3447 | 876.5508 |  |  | 303.2885 | 18197.3089 | 110.594 | 6168.4133 | Failure of Beam
57.7692 | 3466.1541 | 86.6273 | 963.1781 |  |  | 308.1026 | 18486.1551 | 110.8192 | 6279.2325 | Failure of Beam
62.5833 | 3755.0002 | 87.8036 | 1050.9817 | Failure of Beam |  | 312.9167 | 18775.0012 | 111.0409 | 6390.2734 | Failure of Beam
67.3974 | 4043.8464 | 88.89 | 1139.8717 | Failure of Beam |  | 317.7308 | 19063.8474 | 111.2592 | 6501.5325 | Failure of Beam
72.2115 | 4332.6926 | 89.8992 | 1229.7709 | Failure of Beam |  | 322.5449 | 19352.6936 | 111.4742 | 6613.0067 | Failure of Beam
77.0256 | 4621.5388 | 90.8415 | 1320.6124 | Failure of Beam |  | 327.359 | 19641.5398 | 111.686 | 6724.6927 | Failure of Beam
81.8397 | 4910.3849 | 91.7251 | 1412.3375 | Failure of Beam |  | 332.1731 | 19930.3859 | 111.8946 | 6836.5873 | Failure of Beam
86.6539 | 5199.2311 | 92.557 | 1504.8946 | Failure of Beam |  | 336.9872 | 20219.2321 | 112.1003 | 6948.6876 | Failure of Beam
91.468 | 5488.0773 | 93.3429 | 1598.2374 | Failure of Beam |  | 341.8013 | 20508.0783 | 112.303 | 7060.9906 | Failure of Beam
96.2821 | 5776.9235 | 94.0875 | 1692.325 | Failure of Beam |  | 346.6154 | 20796.9245 | 112.5029 | 7173.4935 | Failure of Beam
101.0962 | 6065.7696 | 94.7951 | 1787.1201 | Failure of Beam |  | 351.4295 | 21085.7706 | 112.7 | 7286.1934 | Failure of Beam
105.9103 | 6354.6158 | 95.4691 | 1882.5892 | Failure of Beam |  | 356.2436 | 21374.6168 | 112.8944 | 7399.0878 | Failure of Beam
110.7244 | 6643.462 | 96.1126 | 1978.7018 | Failure of Beam |  | 361.0577 | 21663.463 | 113.0861 | 7512.1739 | Failure of Beam
115.5385 | 6932.3082 | 96.7282 | 2075.43 | Failure of Beam |  | 365.8718 | 21952.3091 | 113.2753 | 7625.4493 | Failure of Beam
120.3526 | 7221.1543 | 97.3182 | 2172.7482 | Failure of Beam |  | 370.6859 | 22241.1553 | 113.4621 | 7738.9113 | Failure of Beam
125.1667 | 7510.0005 | 97.8847 | 2270.6329 | Failure of Beam |  | 375.5 | 22530.0015 | 113.6464 | 7852.5577 | Failure of Beam
129.9808 | 7798.8467 | 98.4295 | 2369.0624 | Failure of Beam |  | 380.3141 | 22818.8477 | 113.8283 | 7966.3861 | Failure of Beam
134.7949 | 8087.6928 | 98.9541 | 2468.0165 | Failure of Beam |  | 385.1282 | 23107.6938 | 114.008 | 8080.394 | Failure of Beam
139.609 | 8376.539 | 99.4601 | 2567.4765 | Failure of Beam |  | 389.9423 | 23396.54 | 114.1854 | 8194.5794 | Failure of Beam
144.4231 | 8665.3852 | 99.9486 | 2667.4252 | Failure of Beam |  | 394.7564 | 23685.3862 | 114.3606 | 8308.94 | Failure of Beam
149.2372 | 8954.2314 | 100.4209 | 2767.8461 | Failure of Beam |  | 399.5705 | 23974.2324 | 114.5337 | 8423.4737 | Failure of Beam
154.0513 | 9243.0775 | 100.8781 | 2868.7242 | Failure of Beam |  | 404.3846 | 24263.0785 | 114.7047 | 8538.1784 | Failure of Beam
158.8654 | 9531.9237 | 101.3209 | 2970.0451 | Failure of Beam |  | 409.1987 | 24551.9247 | 114.8736 | 8653.052 | Failure of Beam
163.6795 | 9820.7699 | 101.7504 | 3071.7955 | Failure of Beam |  | 414.0128 | 24840.7709 | 115.0406 | 8768.0926 | Failure of Beam
168.4936 | 10109.6161 | 102.1673 | 3173.9628 | Failure of Beam |  | 418.827 | 25129.617 | 115.2057 | 8883.2983 | Failure of Beam
173.3077 | 10398.4622 | 102.5723 | 3276.5351 | Failure of Beam |  | 423.6411 | 25418.4632 | 115.3688 | 8998.6671 | Failure of Beam
178.1218 | 10687.3084 | 102.966 | 3379.5011 | Failure of Beam |  | 428.4552 | 25707.3094 | 115.5301 | 9114.1972 | Failure of Beam
182.9359 | 10976.1546 | 103.3492 | 3482.8503 | Failure of Beam |  | 433.2693 | 25996.1556 | 115.6896 | 9229.8868 | Failure of Beam
187.75 | 11265.0007 | 103.7223 | 3586.5725 | Failure of Beam |  | 438.0834 | 26285.0017 | 115.8473 | 9345.734 | Failure of Beam
192.5641 | 11553.8469 | 104.0858 | 3690.6583 | Failure of Beam |  | 442.8975 | 26573.8479 | 116.0033 | 9461.7373 | Failure of Beam
197.3782 | 11842.6931 | 104.4403 | 3795.0986 | Failure of Beam |  | 447.7116 | 26862.6941 | 116.1575 | 9577.8948 | Failure of Beam
202.1923 | 12131.5393 | 104.7861 | 3899.8846 | Failure of Beam |  | 452.5257 | 27151.5403 | 116.3102 | 9694.205 | Failure of Beam
207.0064 | 12420.3854 | 105.1237 | 4005.0083 | Failure of Beam |  | 457.3398 | 27440.3864 | 116.4612 | 9810.6662 | Failure of Beam
211.8205 | 12709.2316 | 105.4535 | 4110.4618 | Failure of Beam |  | 462.1539 | 27729.2326 | 116.6106 | 9927.2767 | Failure of Beam
216.6346 | 12998.0778 | 105.7758 | 4216.2376 | Failure of Beam |  | 466.968 | 28018.0788 | 116.7584 | 10044.0352 | Failure of Beam
221.4487 | 13286.924 | 106.0909 | 4322.3285 | Failure of Beam |  | 471.7821 | 28306.9249 | 116.9048 | 10160.94 | Failure of Beam
226.2628 | 13575.7701 | 106.3992 | 4428.7278 | Failure of Beam |  | 476.5962 | 28595.7711 | 117.0496 | 10277.9896 | Failure of Beam
231.0769 | 13864.6163 | 106.701 | 4535.4287 | Failure of Beam |  | 481.4103 | 28884.6173 | 117.193 | 10395.1826 | Failure of Beam
235.891 | 14153.4625 | 106.9965 | 4642.4252 | Failure of Beam |  | 486.2244 | 29173.4635 | 117.335 | 10512.5176 | Failure of Beam
240.7051 | 14442.3086 | 107.2859 | 4749.7111 | Failure of Beam |  | 491.0385 | 29462.3096 | 117.4755 | 10629.9931 | Failure of Beam
245.5192 | 14731.1548 | 107.5696 | 4857.2808 | Failure of Beam |  | 495.8526 | 29751.1558 | 117.6147 | 10747.6077 | Failure of Beam
250.3333 | 15020.001 | 107.8477 | 4965.1285 | Failure of Beam |  | 500.6667 | 30040.002 | 117.7525 | 10865.3602 | Failure of Beam
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  |  | March 2011

## Column
CHAPTER 17
ESTIMATING FIRE RESISTANCE TIME OF STEEL COLUMNS
| PROTECTED BY FIRE PROTECTION INSULATION | [7 empty] | Version 1805.1
| (QUASI-STEADY-STATE APPROACH) | [7 empty] | (English Units)
The following calculations estimate the full-scale cable tray heat release rate.
Parameters in YELLOW CELLS are Entered by the User.
Parameters in GREEN CELLS are Automatically Selected from the DROP DOWN MENU for the Cable Type Selected.
All subsequent output values are calculated by the spreadsheet and based on values specified in the input parameters. This spreadsheet is protected
and secure to avoid errors due to a wrong entry in a cell(s). The chapter in the NUREG should be read before an analysis is made.
Project / Inspection Title:
INPUT PARAMETERS
| Ratio of Weight of Steel Section per Linear Foot and Heated Perimeter (W/D) | [6 empty] | 16.1725 | lb/ft2
| Thickness of Spray-Applied Protection on Steel Column (h) |  |  |  |  | h ≥ 1/16 in |  | 0.5 | in | 0.041667 | ft
| Density of Spray-Applied Material (ri) | [6 empty] | 35 | lb/ft3
| Thermal Conductivity of Spray-Applied Material (ki) | [6 empty] | 0.06936 | Btu/ft-hr-°F | 1.9267e-05 | Btu/lb-sec-°F
| Specific Heat of Spray-Applied Material (ci) | [6 empty] | 0.2868 | Btu/lb-°F
| Ambient Air Temperature (Ta) | [6 empty] | 77 | °F
| Specific Heat of Steel (cs) | [6 empty] | 0.132 | Btu/lb-°F
Calculate
SECTIONAL FACTORS FOR STEEL COLUMNS
| Structural Shape | W/D Ratio
| W Shapes | (lb/ft2)
| 36x300 | 26.0473
| 36x280 | 24.4097
| 36x260 | 22.7671
| 36x245 | 21.5227
| 36x230 | 20.2703
| 36x210 | 20.9233
| 36x194 | 19.4146
| 36x182 | 18.2746
| 36x170 | 17.1285
| 36x160 | 16.1725
| 36x150 | 15.2091
| 36x135 | 13.7638
| 33x241 | 22.2222
| 33x221 | 20.474
| 33x201 | 18.7107
| 33x152 | 16.2901
| 33x141 | 15.1708
| 33x130 | 14.0465
| 33x118 | 12.8098
| 30x211 | 20.9689
| 30x191 | 19.0841
| 30x173 | 17.3709
| 30x132 | 15.5952
| 30x124 | 14.6992
| 30x116 | 13.7999
| 30x108 | 12.8994
| 30x99 | 11.8729
| 27x178 | 19.3286
| 27x161 | 17.5732
| 27x146 | 16.0132
| 27x114 | 14.5967
| 27x102 | 13.1316
| 27x94 | 12.1526
| 27x84 | 10.9162
| 24x162 | 19.3606
| 24x146 | 17.5586
| 24x131 | 15.8516
| 24x117 | 14.2365
| 24x104 | 12.7191
| 24x94 | 13.4526
| 24x84 | 12.095
| 24x76 | 10.9986
| 24x68 | 9.8921
| 24x62 | 9.9492
| 24x55 | 8.8745
| 21x147 | 19.025
| 21x132 | 17.195
| 21x122 | 15.9616
| 21x111 | 14.5925
| 21x101 | 13.3363
| 21x93 | 14.7307
| 21x83 | 13.2359
| 21x73 | 11.7191
| 21x68 | 10.956
| 21x62 | 10.0351
| 21x57 | 10.1318
| 21x50 | 8.9526
| 21x44 | 7.9255
| 18x119 | 17.4807
| 18x106 | 15.6882
| 18x97 | 14.4256
| 18x86 | 12.871
| 18x76 | 11.4415
| 18x71 | 12.814
| 18x65 | 11.7896
| 18x60 | 10.9339
| 18x55 | 10.0671
| 18x50 | 9.1954
| 18x46 | 9.2555
| 18x40 | 8.104
| 18x35 | 7.1429
| 16x100 | 16.1139
| 16x89 | 14.45
| 16x77 | 12.604
| 16x67 | 11.0424
| 16x57 | 11.3095
| 16x50 | 9.9933
| 16x45 | 9.0437
| 16x40 | 8.0822
| 16x36 | 7.3134
| 16x31 | 6.9781
| 16x26 | 5.9002
| 14x730 | 79.4486
| 14x665 | 73.7387
| 14x605 | 68.2908
| 14x550 | 63.1458
| 14x500 | 58.3317
| 14x455 | 53.8727
| 14x426 | 50.9316
| 14x398 | 48.0483
| 14x370 | 45.1082
| 14x342 | 42.1962
| 14x311 | 38.7378
| 14x283 | 35.6199
| 14x257 | 32.673
| 14x233 | 29.9037
| 14x211 | 27.3198
| 14x193 | 25.1684
| 14x176 | 23.1123
| 14x159 | 20.9454
| 14x145 | 19.2905
| 14x132 | 18.2216
| 14x120 | 16.6551
| 14x109 | 15.2075
| 14x99 | 13.8769
| 14x90 | 12.6701
| 14x82 | 14.4451
| 14x74 | 13.1128
| 14x68 | 12.1086
| 14x61 | 10.9237
| 14x53 | 10.7179
| 14x48 | 9.7594
| 14x43 | 8.792
| 14x38 | 8.3425
| 14x34 | 7.5041
| 14x30 | 6.6593
| 14x26 | 6.5809
| 14x22 | 5.6146
| 12x336 | 48.2124
| 12x305 | 44.4552
| 12x279 | 41.2315
| 12x252 | 37.7764
| 12x230 | 34.8881
| 12x210 | 32.2168
| 12x190 | 29.4878
| 12x170 | 26.6946
| 12x152 | 24.127
| 12x136 | 21.8065
| 12x120 | 19.4332
| 12x106 | 17.3203
| 12x96 | 15.7895
| 12x87 | 14.394
| 12x79 | 13.1411
| 12x72 | 12.0334
| 12x65 | 10.9152
| 12x58 | 10.9262
| 12x53 | 10.03
| 12x50 | 10.7219
| 12x45 | 9.707
| 12x40 | 8.6784
| 12x35 | 8.2938
| 12x30 | 7.1656
| 12x26 | 6.2475
| 12x22 | 6.5639
| 12x19 | 5.7186
| 12x16 | 4.8608
| 12x14 | 4.2748
| 10x112 | 21.3774
| 10x100 | 19.2926
| 10x88 | 17.1624
| 10x77 | 15.1724
| 10x68 | 13.5144
| 10x60 | 12.016
| 10x54 | 10.8798
| 10x49 | 9.919
| 10x45 | 10.4692
| 10x39 | 9.1496
| 10x33 | 7.8076
| 10x30 | 8.2607
| 10x26 | 7.2189
| 10x22 | 6.1596
| 10x19 | 6.3228
| 10x17 | 5.7015
| 10x15 | 5.0676
| 10x12 | 4.0909
| 8x67 | 16.0864
| 8x58 | 14.1005
| 8x48 | 11.8421
| 8x40 | 9.9875
| 8x35 | 8.8028
| 8x31 | 7.8464
| 8x28 | 8.0595
| 8x24 | 6.9649
| 8x21 | 6.7851
| 8x18 | 5.8664
| 8x15 | 5.6622
| 8x13 | 4.9492
| 8x10 | 3.8462
| 6x25 | 8.2327
| 6x20 | 6.6741
| 6x15 | 5.0733
| 6x16 | 6.8182
| 6x12 | 5.2174
| 6x9 | 3.9677
| 5x19 | 7.6305
| 5x16 | 6.4997
| 4x13 | 6.5
| User Specified Value | Enter Value
Select Column
Scroll to desired column size then Click on selection
THERMAL PROPERTIES OF SPRAY-APPLIED INSULATION MATERIALS
Insulation Material |  | Density | Thermal | Specific Heat |  | Select Insulation Type
Spray-Applied |  | ρi | Conductivity ki | ci
|  | (lb/ft3) | (Btu/ft-hr-°F) | (Btu/lb-°F) |  | Scroll to desired material then Click on selection
Sprayed mineral fiber |  | 19 | 0.06936 | 0.2868
Perlite or vermiculite |  | 22 | 0.06936 | 0.2868
High density perlite or vermiculite |  | 35 | 0.06936 | 0.2868
User Specified Value |  | Enter Value | Enter Value | Enter Value
Reference: Buchanan, A. H., Structural Design for Fire Safety, 2001, Page 182.
ESTIMATING FIRE RESISTANCE TIME USING QUASI-STEADY-STATE APPROACH
Reference: "Analytical Methods for Determining Fire Resistance of Steel Members,"
"SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002, Page 4-209.
Temperature Rise in Steel Column
DTs = (ki /(cs h W/D + 1/2 ci ri h2)) (Tf - Ts) Dt
Where
DTs = temperature rise in steel (°F)
ki = thermal conductivity of spray-applied material (Btu/ft-sec-°F)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (Btu/lb-°F)
cs = specific heat of steel (Btu/lb-°F)
h = thickness of spray-applied protection on steel beam (in)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
Tf = fire exposure temperature (°F)
Ts = steel temperature (°F)
Dt = time step (sec)
cs W/D > 2 ci ri h
Where
cs = specific heat of steel (Btu/lb-°F)
W/D = ratio of weight of steel section per linear foot and heated perimeter (lb/ft2)
ri = density of spray-applied material (lb/ft3)
ci = specific heat of spray-applied material (ci)
h = thickness of spray-applied protection on steel column (in)
|  |  | 2.1348 | > | 0.8365
The Maximum Allowable Time Step
Dt = 15.9 W/D
|  |  | Dt = | 257.1429 | sec
|  |  | Dt = | 4.2857 | minutes
For ASTM-E-119 exposure, Tf at any time, t, is given by the following expression
Tf = C1 LOG (0.133 t + 1) + T0
Where
Tf = fire exposure temperature (°F)
C1 = constant = 620
t = time step (sec)
Ta = ambient air temperature (°F)
DTs1 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t1 + 1)+Ta) - Ts0) Dt
| Where |  |  |  |  | Caution! This equation is only valid up to 1000 °F (538 °C) where
|  | t1 = Dt/2 |  |  |  | carbon steel structural members begin to fail. Predicted
|  | Ts0 = initial steel temperature (°F) |  |  |  | temperatures above 1000 °F (538 °C) are not accurate or valid.
DTs2 = (ki /(cs h W/D + 1/2 ci ri h2)) ((C1 LOG (0.133 t2 + 1)+Ta) - Ts) Dt
Where
t2 = t1 + Dt/2
Ts = Ts0 + DTs from previous row
Answer
Time | Time | DTs | Ts |  |  | Time | Time | DTs | Ts
(min) | (sec) | (°F) | (°F) |  |  | (min) | (sec) | (°F) | (°F)
4.2857 | 257.1429 | 43.4313 | 120.4313 |  |  | 261.4286 | 15685.7143 | 108.4816 | 5846.8877 | Failure of Column
8.5714 | 514.2857 | 56.9258 | 177.357 |  |  | 265.7143 | 15942.8571 | 108.7142 | 5955.602 | Failure of Column
12.8571 | 771.4286 | 63.7201 | 241.0771 |  |  | 270 | 16200 | 108.9431 | 6064.545 | Failure of Column
17.1429 | 1028.5714 | 68.3382 | 309.4153 |  |  | 274.2857 | 16457.1429 | 109.1683 | 6173.7133 | Failure of Column
21.4286 | 1285.7143 | 71.8225 | 381.2378 |  |  | 278.5714 | 16714.2857 | 109.3899 | 6283.1032 | Failure of Column
25.7143 | 1542.8571 | 74.6203 | 455.8581 |  |  | 282.8571 | 16971.4286 | 109.6082 | 6392.7115 | Failure of Column
30 | 1800 | 76.9577 | 532.8158 |  |  | 287.1429 | 17228.5714 | 109.8232 | 6502.5347 | Failure of Column
34.2857 | 2057.1429 | 78.9647 | 611.7804 |  |  | 291.4286 | 17485.7143 | 110.035 | 6612.5697 | Failure of Column
38.5714 | 2314.2857 | 80.7231 | 692.5036 |  |  | 295.7143 | 17742.8571 | 110.2436 | 6722.8133 | Failure of Column
42.8571 | 2571.4286 | 82.2879 | 774.7915 |  |  | 300 | 18000 | 110.4493 | 6833.2626 | Failure of Column
47.1429 | 2828.5714 | 83.6973 | 858.4888 |  |  | 304.2857 | 18257.1429 | 110.652 | 6943.9146 | Failure of Column
51.4286 | 3085.7143 | 84.9796 | 943.4684 |  |  | 308.5714 | 18514.2857 | 110.8519 | 7054.7665 | Failure of Column
55.7143 | 3342.8571 | 86.1556 | 1029.624 | Failure of Column |  | 312.8571 | 18771.4286 | 111.0489 | 7165.8154 | Failure of Column
60 | 3600 | 87.2417 | 1116.8657 | Failure of Column |  | 317.1429 | 19028.5714 | 111.2433 | 7277.0587 | Failure of Column
64.2857 | 3857.1429 | 88.2507 | 1205.1164 | Failure of Column |  | 321.4286 | 19285.7143 | 111.4351 | 7388.4938 | Failure of Column
68.5714 | 4114.2857 | 89.1928 | 1294.3092 | Failure of Column |  | 325.7143 | 19542.8571 | 111.6243 | 7500.1181 | Failure of Column
72.8571 | 4371.4286 | 90.0762 | 1384.3854 | Failure of Column |  | 330 | 19800 | 111.811 | 7611.9292 | Failure of Column
77.1429 | 4628.5714 | 90.908 | 1475.2934 | Failure of Column |  | 334.2857 | 20057.1429 | 111.9953 | 7723.9245 | Failure of Column
81.4286 | 4885.7143 | 91.6937 | 1566.9871 | Failure of Column |  | 338.5714 | 20314.2857 | 112.1773 | 7836.1018 | Failure of Column
85.7143 | 5142.8571 | 92.4382 | 1659.4253 | Failure of Column |  | 342.8571 | 20571.4286 | 112.3569 | 7948.4587 | Failure of Column
90 | 5400 | 93.1457 | 1752.571 | Failure of Column |  | 347.1429 | 20828.5714 | 112.5343 | 8060.993 | Failure of Column
94.2857 | 5657.1429 | 93.8196 | 1846.3906 | Failure of Column |  | 351.4286 | 21085.7143 | 112.7095 | 8173.7025 | Failure of Column
98.5714 | 5914.2857 | 94.463 | 1940.8535 | Failure of Column |  | 355.7143 | 21342.8571 | 112.8826 | 8286.5851 | Failure of Column
102.8571 | 6171.4286 | 95.0785 | 2035.932 | Failure of Column |  | 360 | 21600 | 113.0536 | 8399.6387 | Failure of Column
107.1429 | 6428.5714 | 95.6684 | 2131.6004 | Failure of Column |  | 364.2857 | 21857.1429 | 113.2225 | 8512.8612 | Failure of Column
111.4286 | 6685.7143 | 96.2348 | 2227.8353 | Failure of Column |  | 368.5714 | 22114.2857 | 113.3895 | 8626.2507 | Failure of Column
115.7143 | 6942.8571 | 96.7795 | 2324.6148 | Failure of Column |  | 372.8571 | 22371.4286 | 113.5545 | 8739.8052 | Failure of Column
120 | 7200 | 97.3041 | 2421.9189 | Failure of Column |  | 377.1429 | 22628.5714 | 113.7177 | 8853.5229 | Failure of Column
124.2857 | 7457.1429 | 97.81 | 2519.7289 | Failure of Column |  | 381.4286 | 22885.7143 | 113.879 | 8967.4019 | Failure of Column
128.5714 | 7714.2857 | 98.2985 | 2618.0274 | Failure of Column |  | 385.7143 | 23142.8571 | 114.0384 | 9081.4403 | Failure of Column
132.8571 | 7971.4286 | 98.7708 | 2716.7982 | Failure of Column |  | 390 | 23400 | 114.1961 | 9195.6364 | Failure of Column
137.1429 | 8228.5714 | 99.2279 | 2816.0261 | Failure of Column |  | 394.2857 | 23657.1429 | 114.3521 | 9309.9886 | Failure of Column
141.4286 | 8485.7143 | 99.6707 | 2915.6968 | Failure of Column |  | 398.5714 | 23914.2857 | 114.5064 | 9424.4949 | Failure of Column
145.7143 | 8742.8571 | 100.1001 | 3015.7969 | Failure of Column |  | 402.8571 | 24171.4286 | 114.659 | 9539.1539 | Failure of Column
150 | 9000 | 100.517 | 3116.3138 | Failure of Column |  | 407.1429 | 24428.5714 | 114.81 | 9653.9639 | Failure of Column
154.2857 | 9257.1429 | 100.9219 | 3217.2357 | Failure of Column |  | 411.4286 | 24685.7143 | 114.9594 | 9768.9234 | Failure of Column
158.5714 | 9514.2857 | 101.3156 | 3318.5514 | Failure of Column |  | 415.7143 | 24942.8571 | 115.1073 | 9884.0306 | Failure of Column
162.8571 | 9771.4286 | 101.6987 | 3420.2501 | Failure of Column |  | 420 | 25200 | 115.2536 | 9999.2842 | Failure of Column
167.1429 | 10028.5714 | 102.0718 | 3522.3219 | Failure of Column |  | 424.2857 | 25457.1429 | 115.3984 | 10114.6827 | Failure of Column
171.4286 | 10285.7143 | 102.4353 | 3624.7572 | Failure of Column |  | 428.5714 | 25714.2857 | 115.5418 | 10230.2245 | Failure of Column
175.7143 | 10542.8571 | 102.7897 | 3727.5469 | Failure of Column |  | 432.8571 | 25971.4286 | 115.6838 | 10345.9083 | Failure of Column
180 | 10800 | 103.1355 | 3830.6825 | Failure of Column |  | 437.1429 | 26228.5714 | 115.8243 | 10461.7326 | Failure of Column
184.2857 | 11057.1429 | 103.4731 | 3934.1556 | Failure of Column |  | 441.4286 | 26485.7143 | 115.9635 | 10577.6961 | Failure of Column
188.5714 | 11314.2857 | 103.8029 | 4037.9585 | Failure of Column |  | 445.7143 | 26742.8571 | 116.1013 | 10693.7973 | Failure of Column
192.8571 | 11571.4286 | 104.1252 | 4142.0836 | Failure of Column |  | 450 | 27000 | 116.2378 | 10810.0351 | Failure of Column
197.1429 | 11828.5714 | 104.4403 | 4246.5239 | Failure of Column |  | 454.2857 | 27257.1429 | 116.373 | 10926.4081 | Failure of Column
201.4286 | 12085.7143 | 104.7486 | 4351.2725 | Failure of Column |  | 458.5714 | 27514.2857 | 116.5069 | 11042.915 | Failure of Column
205.7143 | 12342.8571 | 105.0503 | 4456.3228 | Failure of Column |  | 462.8571 | 27771.4286 | 116.6396 | 11159.5545 | Failure of Column
210 | 12600 | 105.3458 | 4561.6685 | Failure of Column |  | 467.1429 | 28028.5714 | 116.771 | 11276.3255 | Failure of Column
214.2857 | 12857.1429 | 105.6352 | 4667.3037 | Failure of Column |  | 471.4286 | 28285.7143 | 116.9012 | 11393.2268 | Failure of Column
218.5714 | 13114.2857 | 105.9189 | 4773.2226 | Failure of Column |  | 475.7143 | 28542.8571 | 117.0303 | 11510.257 | Failure of Column
222.8571 | 13371.4286 | 106.197 | 4879.4196 | Failure of Column |  | 480 | 28800 | 117.1582 | 11627.4152 | Failure of Column
227.1429 | 13628.5714 | 106.4697 | 4985.8893 | Failure of Column |  | 484.2857 | 29057.1429 | 117.2849 | 11744.7001 | Failure of Column
231.4286 | 13885.7143 | 106.7374 | 5092.6267 | Failure of Column |  | 488.5714 | 29314.2857 | 117.4105 | 11862.1107 | Failure of Column
235.7143 | 14142.8571 | 107.0001 | 5199.6268 | Failure of Column |  | 492.8571 | 29571.4286 | 117.5351 | 11979.6457 | Failure of Column
240 | 14400 | 107.258 | 5306.8847 | Failure of Column |  | 497.1429 | 29828.5714 | 117.6585 | 12097.3043 | Failure of Column
244.2857 | 14657.1429 | 107.5113 | 5414.396 | Failure of Column |  | 501.4286 | 30085.7143 | 117.7809 | 12215.0852 | Failure of Column
248.5714 | 14914.2857 | 107.7602 | 5522.1562 | Failure of Column |  | 505.7143 | 30342.8571 | 117.9022 | 12332.9874 | Failure of Column
252.8571 | 15171.4286 | 108.0047 | 5630.1609 | Failure of Column |  | 510 | 30600 | 118.0225 | 12451.0099 | Failure of Column
257.1429 | 15428.5714 | 108.2452 | 5738.4061 | Failure of Column |  | 514.2857 | 30857.1429 | 118.1418 | 12569.1518 | Failure of Column
The Failure Temperature for Steel Columns is Assumed at 1000 °F (538 °C)
NOTE:
The above calculations are based on principles developed in the SFPE Handbook of Fire Protection Engineering, 3rd Edition, 2002. Calculations are based on certain assumptions and have inherent limitations. The results of such calculations may or may not have reasonable predictive capabilities for a given situation and should only be interpreted by an informed user. Although each calculation in the spreadsheet has been verified with the results of hand calculation, there is no absolute guarantee of the accuracy of these calculations. Any questions, comments, concerns and suggestions or to report an error(s) in the spreadsheets, please send an email to David.Stroup@nrc.gov or Naeem.Iqbal@nrc.gov.
Prepared by: |  |  |  | Date: |  | Organization:
Checked by: |  |  |  | Date: |  | Organization:
Additional Information:
Revision Log | Description of Revision |  |  |  |  | Date
1805.0 | Original issue with final text. |  |  |  |  | December 2004
1805.1 | Revised e-mail addresses, corrected editorial errors, revised print pagination and print layout. |  |  |  |  | March 2011
Note on I27: This default value (0.132) is the most appropriate value for the majority of analyses. You may change this value for your specific application. If you change this value please ensure that it is appropriate.

## Data
SECTIONAL FACTORS FOR STEEL MEMBERS
| BEAMS |  | COLUMNS
| Structural Shape | W/D Ratio | Structural Shape | W/D Ratio
| W Shapes | (lb/ft2) | W Shapes | (lb/ft2)
| 36x300 | 29.6162 | 36x300 | 26.0473
| 36x280 | 27.756 | 36x280 | 24.4097
| 36x260 | 25.8943 | 36x260 | 22.7671
| 36x245 | 24.4816 | 36x245 | 21.5227
| 36x230 | 23.0596 | 36x230 | 20.2703
| 36x210 | 23.2773 | 36x210 | 20.9233
| 36x194 | 21.5965 | 36x194 | 19.4146
| 36x182 | 20.3286 | 36x182 | 18.2746
| 36x170 | 19.053 | 36x170 | 17.1285
| 36x160 | 17.991 | 36x160 | 16.1725
| 36x150 | 16.9213 | 36x150 | 15.2091
| 36x135 | 15.3191 | 36x135 | 13.7638
| 33x241 | 25.3063 | 33x241 | 22.2222
| 33x221 | 23.3194 | 33x221 | 20.474
| 33x201 | 21.314 | 33x201 | 18.7107
| 33x152 | 18.1664 | 33x152 | 16.2901
| 33x141 | 16.9208 | 33x141 | 15.1708
| 33x130 | 15.6705 | 33x130 | 14.0465
| 33x118 | 14.2944 | 33x118 | 12.8098
| 30x211 | 23.9671 | 30x211 | 20.9689
| 30x191 | 21.8161 | 30x191 | 19.0841
| 30x173 | 19.8613 | 30x173 | 17.3709
| 30x132 | 17.4018 | 30x132 | 15.5952
| 30x124 | 16.403 | 30x124 | 14.6992
| 30x116 | 15.4025 | 30x116 | 13.7999
| 30x108 | 14.4008 | 30x108 | 12.8994
| 30x99 | 13.2574 | 30x99 | 11.8729
| 27x178 | 22.1519 | 27x178 | 19.3286
| 27x161 | 20.1418 | 27x161 | 17.5732
| 27x146 | 18.3561 | 27x146 | 16.0132
| 27x114 | 16.3539 | 27x114 | 14.5967
| 27x102 | 14.7124 | 27x102 | 13.1316
| 27x94 | 13.6183 | 27x94 | 12.1526
| 27x84 | 12.236 | 27x84 | 10.9162
| 24x162 | 22.2286 | 24x162 | 19.3606
| 24x146 | 20.1657 | 24x146 | 17.5586
| 24x131 | 18.2124 | 24x131 | 15.8516
| 24x117 | 16.3598 | 24x117 | 14.2365
| 24x104 | 14.6187 | 24x104 | 12.7191
| 24x94 | 15.0832 | 24x94 | 13.4526
| 24x84 | 13.563 | 24x84 | 12.095
| 24x76 | 12.336 | 24x76 | 10.9986
| 24x68 | 11.0983 | 24x68 | 9.8921
| 24x62 | 10.9832 | 24x62 | 9.9492
| 24x55 | 9.7974 | 24x55 | 8.8745
| 21x147 | 21.9923 | 21x147 | 19.025
| 21x132 | 19.8795 | 21x132 | 17.195
| 21x122 | 18.4546 | 21x122 | 15.9616
| 21x111 | 16.8736 | 21x111 | 14.5925
| 21x101 | 15.4218 | 21x101 | 13.3363
| 21x93 | 16.5726 | 21x93 | 14.7307
| 21x83 | 14.889 | 21x83 | 13.2359
| 21x73 | 13.1819 | 21x73 | 11.7191
| 21x68 | 12.3244 | 21x68 | 10.956
| 21x62 | 11.2898 | 21x62 | 10.0351
| 21x57 | 11.2205 | 21x57 | 10.1318
| 21x50 | 9.919 | 21x50 | 8.9526
| 21x44 | 8.7824 | 21x44 | 7.9255
| 18x119 | 20.2769 | 18x119 | 17.4807
| 18x106 | 18.2026 | 18x106 | 15.6882
| 18x97 | 16.7374 | 18x97 | 14.4256
| 18x86 | 14.937 | 18x86 | 12.871
| 18x76 | 13.2799 | 18x76 | 11.4415
| 18x71 | 14.4763 | 18x71 | 12.814
| 18x65 | 13.3174 | 18x65 | 11.7896
| 18x60 | 12.3499 | 18x60 | 10.9339
| 18x55 | 11.3734 | 18x55 | 10.0671
| 18x50 | 10.3887 | 18x50 | 9.1954
| 18x46 | 10.3024 | 18x46 | 9.2555
| 18x40 | 9.02 | 18x40 | 8.104
| 18x35 | 7.9545 | 18x35 | 7.1429
| 16x100 | 18.7368 | 16x100 | 16.1139
| 16x89 | 16.807 | 16x89 | 14.45
| 16x77 | 14.6632 | 16x77 | 12.604
| 16x67 | 12.8486 | 16x67 | 11.0424
| 16x57 | 12.8186 | 16x57 | 11.3095
| 16x50 | 11.3272 | 16x50 | 9.9933
| 16x45 | 10.2515 | 16x45 | 9.0437
| 16x40 | 9.1612 | 16x40 | 8.0822
| 16x36 | 8.2941 | 16x36 | 7.3134
| 16x31 | 7.7849 | 16x31 | 6.9781
| 16x26 | 6.5851 | 16x26 | 5.9002
| 14x730 | 94.836 | 14x730 | 79.4486
| 14x665 | 88.1086 | 14x665 | 73.7387
| 14x605 | 81.6694 | 14x605 | 68.2908
| 14x550 | 75.5841 | 14x550 | 63.1458
| 14x500 | 69.8893 | 14x500 | 58.3317
| 14x455 | 64.6039 | 14x455 | 53.8727
| 14x426 | 61.0935 | 14x426 | 50.9316
| 14x398 | 57.6742 | 14x398 | 48.0483
| 14x370 | 54.1761 | 14x370 | 45.1082
| 14x342 | 50.7293 | 14x342 | 42.1962
| 14x311 | 46.5859 | 14x311 | 38.7378
| 14x283 | 42.8626 | 14x283 | 35.6199
| 14x257 | 39.3392 | 14x257 | 32.673
| 14x233 | 36.0263 | 14x233 | 29.9037
| 14x211 | 32.9344 | 14x211 | 27.3198
| 14x193 | 30.3499 | 14x193 | 25.1684
| 14x176 | 27.8886 | 14x176 | 23.1123
| 14x159 | 25.2923 | 14x159 | 20.9454
| 14x145 | 23.2932 | 14x145 | 19.2905
| 14x132 | 21.9375 | 14x132 | 18.2216
| 14x120 | 20.0585 | 14x120 | 16.6551
| 14x109 | 18.318 | 14x109 | 15.2075
| 14x99 | 16.7218 | 14x99 | 13.8769
| 14x90 | 15.2715 | 14x90 | 12.6701
| 14x82 | 16.9684 | 14x82 | 14.4451
| 14x74 | 15.4033 | 14x74 | 13.1128
| 14x68 | 14.2272 | 14x68 | 12.1086
| 14x61 | 12.8387 | 14x61 | 10.9237
| 14x53 | 12.4025 | 14x53 | 10.7179
| 14x48 | 11.2963 | 14x48 | 9.7594
| 14x43 | 10.1785 | 14x43 | 8.792
| 14x38 | 9.5218 | 14x38 | 8.3425
| 14x34 | 8.5669 | 14x34 | 7.5041
| 14x30 | 7.6062 | 14x30 | 6.6593
| 14x26 | 7.3611 | 14x26 | 6.5809
| 14x22 | 6.2827 | 14x22 | 5.6146
| 12x336 | 57.3991 | 12x336 | 48.2124
| 12x305 | 52.9705 | 12x305 | 44.4552
| 12x279 | 49.1919 | 12x279 | 41.2315
| 12x252 | 45.104 | 12x252 | 37.7764
| 12x230 | 41.6824 | 12x230 | 34.8881
| 12x210 | 38.5144 | 12x210 | 32.2168
| 12x190 | 35.2668 | 12x190 | 29.4878
| 12x170 | 31.9499 | 12x170 | 26.6946
| 12x152 | 28.8973 | 12x152 | 24.127
| 12x136 | 26.1371 | 12x136 | 21.8065
| 12x120 | 23.3085 | 12x120 | 19.4332
| 12x106 | 20.7775 | 12x106 | 17.3203
| 12x96 | 18.9474 | 12x96 | 15.7895
| 12x87 | 17.2833 | 12x87 | 14.394
| 12x79 | 15.7842 | 12x79 | 13.1411
| 12x72 | 14.4578 | 12x72 | 12.0334
| 12x65 | 13.1181 | 12x65 | 10.9152
| 12x58 | 12.9633 | 12x58 | 10.9262
| 12x53 | 11.9068 | 12x53 | 10.03
| 12x50 | 12.5313 | 12x50 | 10.7219
| 12x45 | 11.3481 | 12x45 | 9.707
| 12x40 | 10.1469 | 12x40 | 8.6784
| 12x35 | 9.5281 | 12x35 | 8.2938
| 12x30 | 8.2342 | 12x30 | 7.1656
| 12x26 | 7.1807 | 12x26 | 6.2475
| 12x22 | 7.2948 | 12x22 | 6.5639
| 12x19 | 6.3572 | 12x19 | 5.7186
| 12x16 | 5.4069 | 12x16 | 4.8608
| 12x14 | 4.7552 | 12x14 | 4.2748
| 10x112 | 25.622 | 10x112 | 21.3774
| 10x100 | 23.1392 | 10x100 | 19.2926
| 10x88 | 20.5988 | 10x88 | 17.1624
| 10x77 | 18.2213 | 10x77 | 15.1724
| 10x68 | 16.2388 | 10x68 | 13.5144
| 10x60 | 14.4462 | 10x60 | 12.016
| 10x54 | 13.083 | 10x54 | 10.8798
| 10x49 | 11.9318 | 10x49 | 9.919
| 10x45 | 12.3967 | 10x45 | 10.4692
| 10x39 | 10.8421 | 10x39 | 9.1496
| 10x33 | 9.261 | 10x33 | 7.8076
| 10x30 | 9.5314 | 10x30 | 8.2607
| 10x26 | 8.3311 | 10x26 | 7.2189
| 10x22 | 7.114 | 10x22 | 6.1596
| 10x19 | 7.1161 | 10x19 | 6.3228
| 10x17 | 6.4212 | 10x17 | 5.7015
| 10x15 | 5.7107 | 10x15 | 5.0676
| 10x12 | 4.6095 | 10x12 | 4.0909
| 8x67 | 19.2806 | 8x67 | 16.0864
| 8x58 | 16.9178 | 8x58 | 14.1005
| 8x48 | 14.2117 | 8x48 | 11.8421
| 8x40 | 12.003 | 8x40 | 9.9875
| 8x35 | 10.5823 | 8x35 | 8.8028
| 8x31 | 9.438 | 8x31 | 7.8464
| 8x28 | 9.5577 | 8x28 | 8.0595
| 8x24 | 8.2628 | 8x24 | 6.9649
| 8x21 | 7.9071 | 8x21 | 6.7851
| 8x18 | 6.8419 | 8x18 | 5.8664
| 8x15 | 6.4806 | 8x15 | 5.6622
| 8x13 | 5.6686 | 8x13 | 4.9492
| 8x10 | 4.4021 | 8x10 | 3.8462
| 6x25 | 9.8814 | 6x25 | 8.2327
| 6x20 | 8.016 | 6x20 | 6.6741
| 6x15 | 6.1038 | 6x15 | 5.0733
| 6x16 | 7.9569 | 6x16 | 6.8182
| 6x12 | 6.1017 | 6x12 | 5.2174
| 6x9 | 4.6392 | 6x9 | 3.9677
| 5x19 | 9.1751 | 5x19 | 7.6305
| 5x16 | 7.824 | 5x16 | 6.4997
| 4x13 | 7.82 | 4x13 | 6.5
| User Specified Value | Enter Value | User Specified Value | Enter Value